## Test Conditions
DESIREE-FIRE Test Number 49 - Circuit Simulator Data Only
Test Date: | 2009-10-09
DCSim DAQ Start Time | 10:56
DCSim Time for Synchronization | 13:13
Heat Source Synchronization | 0:03 | minutes:seconds
Heat Source DAQ Start Time | 13:10
Fire Time | 13:18
Offset | 2:22 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 8520 | seconds
Heat Source Offset | 0:08 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 457 | seconds
Heat Source Stop Time | 14:44
Test Duration | 1:26 | minutes:seconds
| 5158 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | Kerite, 9c, 14AWG |  | Channel 3 represents the top of the thermocouple cable | Channel 4, TC25 in the Temperature Data File
MOV 2 | Kerite, 9c, 14AWG |  | Channel 3 represents the top of the thermocouple cable | Channel 4, TC25 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.82812 | 123.23 | -58.58 | 64.3478 | -0.11398 | 0.00083526 | 0.064375 | 0.065841 | 0.0010148 | -0.0010125 | -0.00034601 | -0.068481 | 0.00046135 | -0.00064077 | 0.0045458 | 0.0019119 | 0.0014697 | -0.0031787 | -0.10071 | 64.3112 | -58.7402 | 64.2746 | -58.4564 | -58.8455 | -58.7723 | -0.032043 | 64.325 | -58.6166 | -58.5388 | -58.548 | -58.6761 | -58.3603 | -0.16022 | -0.036621 | -0.073242 | 0.1236 | -0.19226 | -0.2655 | -0.032044 | -0.10529 | -0.036621 | -0.022888 | -122.8867 | 0.032043 | 0.21973 | -0.09613 | 0.25635 | -0.059509 | 0.28381 | 123.0148 | 0.068664 | 0.07782 | 123.0515 | 122.9416 | 122.8912 | 122.905 | -123.0881 | -122.9645 | 122.8546 | 0.041199 | 58.4793 | 58.548
0.17188 | 123.2162 | -58.5983 | 64.357 | -0.12924 | -0.0015145 | 0.066298 | 0.063491 | 0.003151 | 0.00026909 | -0.00098701 | -0.01355 | 0.0017431 | 0.00021363 | -0.007417 | -0.00065151 | -0.00045288 | 0.00088014 | -0.054932 | 64.3021 | -58.6945 | 64.2883 | -58.4015 | -58.8226 | -58.7494 | 0 | 64.3387 | -58.6395 | -58.5663 | -58.5663 | -58.6761 | -58.3832 | -0.09613 | -0.054932 | -0.068665 | 0.19684 | -0.15106 | -0.2243 | -0.054932 | -0.12817 | -0.041198 | -0.018311 | -122.9233 | 0.032044 | 0.21515 | -0.077819 | 0.25635 | -0.036621 | 0.29297 | 122.9828 | 0.073242 | 0.073242 | 122.9965 | 122.9782 | 122.9004 | 122.937 | -123.0515 | -122.9965 | 122.8867 | 0.032044 | 58.5434 | 58.5983
1.1719 | 123.2117 | -58.5754 | 64.3845 | -0.060578 | -0.00023294 | 0.065871 | 0.061996 | -0.0013352 | -0.0014399 | 0.00029479 | 0.001709 | 0.0015295 | 0.0014954 | -0.006349 | -0.00022431 | 0.00018792 | -0.0012561 | -0.073242 | 64.27 | -58.7357 | 64.2471 | -58.4473 | -58.8455 | -58.7723 | -0.036621 | 64.389 | -58.6258 | -58.5846 | -58.5754 | -58.6716 | -58.4152 | -0.16022 | -0.11444 | -0.13733 | 0.12817 | -0.19684 | -0.27008 | -0.036621 | -0.10986 | -0.050354 | 0.004578 | -122.9691 | 0 | 0.16022 | -0.096131 | 0.21057 | -0.045777 | 0.28839 | 122.9828 | 0.050354 | 0.041198 | 123.0057 | 123.0148 | 122.8455 | 122.9645 | -123.1201 | -123.0103 | 122.8226 | -0.009156 | 58.5022 | 58.5388
2.1719 | 123.2483 | -58.548 | 64.3799 | -0.060578 | -0.0015145 | 0.064375 | 0.063491 | -0.0024032 | 0.00026909 | 0.0028582 | 0.026123 | 3.4148e-05 | -0.00064077 | -0.0054944 | 0.00020289 | 0.00040152 | -0.0014697 | -0.022888 | 64.3295 | -58.7082 | 64.3066 | -58.3878 | -58.7494 | -58.7128 | 0.073242 | 64.3616 | -58.5754 | -58.5068 | -58.4793 | -58.5846 | -58.3374 | -0.16022 | -0.050354 | -0.073242 | 0.16022 | -0.16479 | -0.20142 | -0.004578 | -0.041199 | -0.027465 | -0.018311 | -122.8867 | 0.068665 | 0.21057 | -0.036621 | 0.23804 | -0.009156 | 0.32043 | 123.0148 | 0.09613 | 0.068664 | 123.0377 | 122.937 | 122.8775 | 122.9095 | -123.0881 | -122.9553 | 122.8546 | 0.041199 | 58.5251 | 58.6212
3.1719 | 123.1888 | -58.5983 | 64.3616 | -0.098725 | 0.0029715 | 0.06523 | 0.061568 | -0.00090783 | -0.0016535 | 0.002431 | -0.0074462 | -0.0012477 | 0.00021363 | 5.9824e-05 | 0.0021255 | -0.0021619 | -0.00082886 | -0.073242 | 64.2929 | -58.7357 | 64.2929 | -58.4106 | -58.8226 | -58.754 | -0.013733 | 64.357 | -58.6166 | -58.58 | -58.58 | -58.667 | -58.3923 | -0.13733 | -0.068664 | -0.068664 | 0.18768 | -0.15564 | -0.2243 | -0.01831 | -0.086975 | -0.01831 | -0.004577 | -122.9416 | 0.018311 | 0.20599 | -0.068664 | 0.2243 | -0.050354 | 0.32501 | 123.0286 | 0.036621 | 0.036621 | 123.0286 | 122.9736 | 122.8912 | 122.9553 | -123.0972 | -122.9782 | 122.8912 | 0.018311 | 58.5251 | 58.5846
4.1719 | 123.2025 | -58.5754 | 64.357 | -0.11398 | 0.0016899 | 0.064589 | 0.063277 | 0.00251 | -0.0025079 | -0.00077341 | -0.01355 | 3.4148e-05 | 0.00064083 | -0.0018628 | -0.00065151 | -0.00045288 | -0.0010425 | -0.068665 | 64.2746 | -58.7357 | 64.2883 | -58.4106 | -58.8226 | -58.7631 | 0 | 64.3433 | -58.6304 | -58.5434 | -58.5342 | -58.6624 | -58.3694 | -0.16022 | -0.082398 | -0.068665 | 0.16479 | -0.18768 | -0.24719 | -0.027466 | -0.086975 | -0.054932 | -0.013733 | -122.9004 | 0.041198 | 0.20599 | -0.086976 | 0.26092 | -0.032044 | 0.32501 | 123.024 | 0.09613 | 0.086975 | 123.0103 | 122.9736 | 122.85 | 122.9187 | -123.0927 | -122.9874 | 122.8638 | 0.032043 | 58.5068 | 58.5754
5.1719 | 123.2437 | -58.5754 | 64.3433 | -0.098725 | 0.0019035 | 0.06523 | 0.062209 | -5.343e-05 | 0.00048269 | -0.00098701 | -0.0074462 | -0.00060665 | 0.00021363 | 0.0019824 | 0.00020289 | 0.00082892 | -0.0023243 | -0.073242 | 64.2792 | -58.699 | 64.2929 | -58.4106 | -58.8181 | -58.7448 | -0.004578 | 64.3341 | -58.6075 | -58.5434 | -58.5342 | -58.6578 | -58.3649 | -0.1236 | -0.064087 | -0.050354 | 0.16479 | -0.16937 | -0.24261 | -0.045776 | -0.11902 | -0.032044 | -0.009156 | -122.8867 | 0.041198 | 0.21057 | -0.082398 | 0.24262 | -0.050354 | 0.28839 | 122.9919 | 0.073242 | 0.064087 | 122.9782 | 122.9416 | 122.8546 | 122.9095 | -123.0423 | -122.9507 | 122.8683 | 0.032043 | 58.5022 | 58.5709
6.1719 | 123.1659 | -58.6578 | 64.3616 | -0.068207 | 0.00019446 | 0.066512 | 0.067123 | 0.00037377 | 0.0015509 | 0.0028582 | -0.071533 | 0.0015295 | -0.00042717 | -0.00015378 | -0.0012925 | 0.00040152 | -0.0010425 | -0.11902 | 64.3295 | -58.7769 | 64.1876 | -58.5342 | -58.9371 | -58.8776 | -0.12817 | 64.3707 | -58.6349 | -58.6212 | -58.6349 | -58.7585 | -58.4518 | -0.11902 | -0.032043 | -0.17395 | 0.1236 | -0.21973 | -0.27924 | -0.10071 | -0.16022 | 0.022888 | 0.009156 | -122.9828 | 0.022888 | 0.20599 | -0.10071 | 0.18311 | -0.1236 | 0.24261 | 122.9645 | 0 | 0.013733 | 123.1064 | 123.0057 | 122.9874 | 123.0286 | -123.1384 | -122.9965 | 122.8455 | 0.036621 | 58.5388 | 58.5297
7.1719 | 123.1705 | -58.5983 | 64.3433 | -0.068207 | -0.00044654 | 0.06523 | 0.061782 | -0.0017624 | -0.00015811 | 0.00029479 | 0.016968 | -0.0014613 | 0.00021363 | -0.00079478 | -0.00043791 | 0.00082892 | 0.0025891 | -0.068665 | 64.3295 | -58.7082 | 64.2563 | -58.4656 | -58.8181 | -58.7769 | -0.041199 | 64.3707 | -58.6121 | -58.58 | -58.5526 | -58.6578 | -58.3969 | -0.10986 | -0.013733 | -0.086975 | 0.13275 | -0.17853 | -0.21973 | -0.068664 | -0.10986 | -0.013733 | 0.027466 | -122.9233 | 0.045777 | 0.20142 | -0.059509 | 0.21515 | -0.045776 | 0.24262 | 122.9645 | 0.05951 | 0.032044 | 123.0377 | 122.9828 | 122.9279 | 122.9691 | -123.0515 | -122.9553 | 122.8546 | 0.018311 | 58.5297 | 58.5571
8.1719 | 123.2071 | -58.5892 | 64.3478 | -0.12924 | 0.0014761 | 0.067152 | 0.063491 | 0.0020828 | 0.0011237 | -0.0029096 | -0.0043946 | 3.4148e-05 | 0.00064083 | -0.0035718 | -0.00086511 | -2.5678e-05 | 0.00088014 | -0.059509 | 64.2792 | -58.7311 | 64.2838 | -58.4244 | -58.8181 | -58.7631 | -0.013733 | 64.3478 | -58.6212 | -58.5526 | -58.5754 | -58.6533 | -58.374 | -0.14191 | -0.068664 | -0.064087 | 0.16479 | -0.17395 | -0.22888 | -0.032044 | -0.086975 | -0.032044 | 0 | -122.9004 | 0.013733 | 0.21515 | -0.064087 | 0.24719 | -0.032043 | 0.3067 | 123.0148 | 0.045777 | 0.068665 | 123.0103 | 122.9691 | 122.8683 | 122.937 | -123.0789 | -122.9691 | 122.8729 | 0.036621 | 58.5297 | 58.5754
9.1719 | 123.1613 | -58.6075 | 64.3707 | -0.083466 | -0.00023294 | 0.06523 | 0.064559 | 0.0012284 | 0.00026909 | -0.00077341 | 0.013916 | 0.00088875 | 0.0023498 | -0.0033582 | 0.00020289 | 0.00061532 | 0.00045294 | -0.07782 | 64.3112 | -58.7082 | 64.3112 | -58.3008 | -58.8913 | -58.8364 | -0.073242 | 64.3295 | -58.6441 | -58.5754 | -58.5983 | -58.667 | -58.3832 | -0.10071 | -0.05951 | -0.05951 | 0.3067 | -0.22888 | -0.28381 | -0.12817 | -0.1831 | -0.036621 | -0.041199 | -122.9462 | 0.009155 | 0.2243 | -0.059509 | 0.26093 | -0.022888 | 0.40741 | 123.0194 | 0.045776 | 0.068665 | 123.0194 | 122.9736 | 122.9187 | 122.937 | -123.0789 | -123.0148 | 122.9187 | 0.032044 | 58.5297 | 58.5342
10.1719 | 123.1934 | -58.58 | 64.3753 | -0.12161 | 0.0010489 | 0.063948 | 0.064132 | -0.00026703 | -0.0020807 | -0.00077341 | 0.0047608 | 0.00088875 | 0.00042723 | -0.0014356 | -0.00086511 | -0.0025891 | 0.0015209 | -0.091553 | 64.3158 | -58.6945 | 64.2517 | -58.461 | -58.8547 | -58.7677 | -0.054932 | 64.3707 | -58.6212 | -58.58 | -58.58 | -58.6807 | -58.3832 | -0.11444 | -0.059509 | -0.1236 | 0.11902 | -0.18768 | -0.27466 | -0.073242 | -0.16022 | -0.041199 | -0.004577 | -122.9553 | 0 | 0.19684 | -0.10071 | 0.23804 | -0.059509 | 0.23346 | 122.9462 | 0.041199 | 0.041199 | 123.0103 | 122.9919 | 122.8958 | 122.9507 | -123.0698 | -122.9965 | 122.8317 | 0 | 58.4885 | 58.5251
11.1719 | 123.1934 | -58.5754 | 64.3524 | -0.12161 | -0.0010873 | 0.064375 | 0.063705 | 0.001442 | 0.0019781 | 0.00050839 | -0.06543 | -0.00082025 | 0.0025634 | 0.0028368 | -0.0012925 | -2.5678e-05 | -0.0010425 | -0.086975 | 64.2975 | -58.7631 | 64.2654 | -58.4473 | -58.8272 | -58.7677 | -0.032043 | 64.3478 | -58.6121 | -58.5526 | -58.548 | -58.6716 | -58.3649 | -0.18768 | -0.054932 | -0.086975 | 0.12817 | -0.19226 | -0.25177 | -0.004577 | -0.064086 | -0.036622 | -0.004578 | -122.905 | 0.027465 | 0.21057 | -0.096131 | 0.24719 | -0.059509 | 0.31586 | 123.0286 | 0.064087 | 0.05951 | 123.0606 | 122.9599 | 122.8729 | 122.9233 | -123.1155 | -122.9645 | 122.8409 | 0.022888 | 58.4885 | 58.5434
12.1719 | 123.2117 | -58.5663 | 64.3433 | -0.13687 | 0.0012625 | 0.065871 | 0.064773 | -0.0011214 | 0.0017645 | -0.0014142 | -0.0013428 | 0.00046135 | -0.00064077 | -0.001222 | 0.00041649 | -0.0013073 | -0.0023243 | -0.07782 | 64.2838 | -58.7357 | 64.2838 | -58.4106 | -58.8318 | -58.7494 | -0.013733 | 64.3341 | -58.6349 | -58.5709 | -58.58 | -58.5846 | -58.2504 | -0.16937 | -0.05951 | -0.05951 | 0.15564 | -0.18311 | -0.2655 | -0.013733 | -0.09613 | -0.068665 | -0.009156 | -122.9141 | -0.013733 | 0.31586 | -0.018311 | 0.38452 | 0.050354 | 0.32501 | 123.0194 | 0.054932 | 0.064087 | 123.0194 | 122.9691 | 122.85 | 122.9004 | -123.0789 | -122.9782 | 122.85 | -0.004578 | 58.4885 | 58.5526
13.1719 | 123.23 | -58.58 | 64.3478 | -0.15213 | 0.0027579 | 0.062666 | 0.063918 | 0.00037377 | -0.00079891 | 0.00050839 | -0.028809 | 0.0019567 | -0.0021362 | -0.00058098 | -0.00065151 | -0.0015211 | -0.0021107 | -0.059509 | 64.2792 | -58.7448 | 64.2975 | -58.4381 | -58.8089 | -58.7723 | 0 | 64.3295 | -58.6395 | -58.548 | -58.5571 | -58.6487 | -58.374 | -0.1648 | -0.068664 | -0.050354 | 0.14191 | -0.19226 | -0.22888 | -0.027466 | -0.064087 | -0.059509 | -0.01831 | -122.8958 | 0.022888 | 0.20599 | -0.068665 | 0.2655 | -0.009156 | 0.3067 | 123.0423 | 0.082397 | 0.091552 | 123.024 | 122.9691 | 122.8592 | 122.9095 | -123.0927 | -122.9874 | 122.8775 | 0.032043 | 58.5205 | 58.58
14.1719 | 123.1842 | -58.5983 | 64.3753 | -0.10635 | 0.00040806 | 0.063948 | 0.064345 | -0.0026168 | 0.0017645 | -0.00013241 | 0.0078126 | 0.00067495 | 0.001068 | 0.0015552 | 0.00063009 | 0.00040152 | 0.0028027 | -0.018311 | 64.3387 | -58.7265 | 64.2609 | -58.4702 | -58.8593 | -58.7769 | -0.073242 | 64.3707 | -58.6304 | -58.5846 | -58.5846 | -58.6807 | -58.4015 | -0.12817 | -0.036621 | -0.11444 | 0.12817 | -0.17853 | -0.26093 | -0.050354 | -0.13275 | -0.032043 | -0.004577 | -122.9599 | 0.013733 | 0.19684 | -0.082397 | 0.22888 | -0.050354 | 0.25635 | 122.9874 | 0.045776 | 0.045776 | 123.0652 | 123.0011 | 122.937 | 122.9691 | -123.1018 | -123.0057 | 122.8592 | 0.013733 | 58.58 | 58.5251
15.1719 | 123.2574 | -58.5846 | 64.3524 | -0.091095 | -0.00023294 | 0.065443 | 0.063491 | 0.001442 | 5.5488e-05 | 0.0020038 | -0.03186 | 0.00067495 | -0.0012818 | 0.0041186 | -0.0019333 | -2.5678e-05 | -0.0044605 | -0.064087 | 64.2792 | -58.7357 | 64.2975 | -58.4427 | -58.8318 | -58.754 | -0.004578 | 64.3524 | -58.6121 | -58.5434 | -58.5342 | -58.667 | -58.374 | -0.15106 | -0.073242 | -0.054932 | 0.14191 | -0.16937 | -0.24719 | -0.01831 | -0.09613 | -0.027466 | 0 | -122.8958 | 0.050354 | 0.21057 | -0.082397 | 0.23804 | -0.054931 | 0.29297 | 123.0331 | 0.07782 | 0.068665 | 123.0148 | 122.9645 | 122.8638 | 122.937 | -123.0881 | -122.9645 | 122.8821 | 0.041199 | 58.5205 | 58.58
16.1719 | 123.2071 | -58.5754 | 64.3478 | -0.16739 | 0.00040806 | 0.066512 | 0.061141 | -0.0021896 | 0.00069649 | -0.00013241 | -0.0074462 | 0.00088875 | -0.0021362 | -0.001222 | -0.00022431 | -0.00066648 | -0.0021107 | -0.082397 | 64.3204 | -58.7128 | 64.2334 | -58.5205 | -58.8867 | -58.7952 | -0.041199 | 64.3524 | -58.6121 | -58.5892 | -58.5754 | -58.6716 | -58.3969 | -0.13733 | -0.027465 | -0.11444 | 0.054931 | -0.21973 | -0.31128 | -0.082397 | -0.17395 | -0.036622 | 0.004578 | -122.937 | 0 | 0.17853 | -0.096131 | 0.21515 | -0.059509 | 0.19226 | 122.9462 | 0.036622 | 0.022889 | 123.0331 | 122.9645 | 122.8958 | 122.9279 | -123.0606 | -122.9599 | 122.8088 | -0.013733 | 58.493 | 58.5342
17.1719 | 123.2437 | -58.58 | 64.4028 | -0.03006 | 0.00040806 | 0.063521 | 0.063064 | 0.00058737 | 0.00026909 | -0.00098701 | 0.032227 | -0.00060665 | 2.8e-08 | -0.00229 | 0.00041649 | -0.0010937 | -0.0042469 | -0.050354 | 64.3433 | -58.7173 | 64.27 | -58.4244 | -58.7997 | -58.7494 | 0.013733 | 64.3799 | -58.6075 | -58.5526 | -58.5205 | -58.6166 | -58.3694 | -0.13733 | -0.059509 | -0.13275 | 0.15564 | -0.16937 | -0.21973 | -0.032044 | -0.082398 | -0.027466 | -0.022888 | -122.9553 | 0.059509 | 0.21057 | -0.036621 | 0.23804 | -0.009155 | 0.29297 | 122.9874 | 0.086975 | 0.054932 | 123.0606 | 122.9874 | 122.9233 | 122.9599 | -123.1201 | -123.0103 | 122.85 | 0.027466 | 58.5297 | 58.5938
18.1719 | 123.2346 | -58.5663 | 64.3387 | -0.045319 | 0.00062166 | 0.063734 | 0.062209 | 0.0027238 | 0.00048269 | 0.0020038 | -0.025757 | 0.00088875 | -0.00064077 | 0.0036914 | -0.0027877 | 0.0010425 | -0.0023243 | -0.059509 | 64.2838 | -58.7128 | 64.27 | -58.429 | -58.8043 | -58.7585 | -0.009155 | 64.3295 | -58.6349 | -58.5571 | -58.548 | -58.667 | -58.3649 | -0.14648 | -0.054932 | -0.068664 | 0.13733 | -0.19226 | -0.23804 | -0.045776 | -0.091552 | -0.068665 | -0.009155 | -122.8958 | 0.01831 | 0.20142 | -0.10071 | 0.27008 | -0.032043 | 0.28381 | 122.9828 | 0.086975 | 0.07782 | 122.9965 | 122.9645 | 122.85 | 122.8958 | -123.0515 | -122.9736 | 122.8363 | 0.009155 | 58.5068 | 58.5571
19.1719 | 123.2346 | -58.6075 | 64.357 | -0.068207 | 0.0012625 | 0.064162 | 0.065414 | -0.0034714 | 0.00091009 | 0.0028582 | -0.047119 | 0.0019567 | -0.0029908 | 0.0086048 | -0.0012925 | -0.0010937 | 0.0028027 | -0.11444 | 64.3387 | -58.7631 | 64.2014 | -58.5159 | -58.8776 | -58.8318 | 0.009155 | 64.389 | -58.6121 | -58.5892 | -58.5663 | -58.6624 | -58.374 | -0.15564 | -0.018311 | -0.15564 | 0.091553 | -0.2243 | -0.27008 | -0.068664 | -0.11444 | -0.004578 | 0.032043 | -122.9462 | 0.041199 | 0.23346 | -0.054932 | 0.23804 | -0.050354 | 0.24719 | 122.9645 | 0.045777 | 0.022889 | 123.1018 | 123.0011 | 122.9462 | 122.9965 | -123.1201 | -122.9691 | 122.8088 | 0.018311 | 58.493 | 58.6166
20.1719 | 123.23 | -58.5892 | 64.3204 | -0.11398 | 0.00083526 | 0.064589 | 0.064132 | 0.0012284 | -0.00037171 | 0.001363 | -0.0043946 | 0.00088875 | 0.00064083 | -0.0010084 | -0.0012925 | 0.0016833 | -0.00040166 | -0.064087 | 64.2929 | -58.7128 | 64.2975 | -58.4244 | -58.8226 | -58.7814 | -0.018311 | 64.3433 | -58.6166 | -58.5434 | -58.548 | -58.667 | -58.3557 | -0.1236 | -0.027466 | -0.022889 | 0.16479 | -0.19226 | -0.23346 | -0.068664 | -0.10986 | -0.027466 | 0.022888 | -122.8638 | 0.041198 | 0.23346 | -0.07782 | 0.26093 | -0.050354 | 0.28839 | 123.0103 | 0.068664 | 0.073242 | 123.0057 | 122.9599 | 122.8821 | 122.9324 | -123.0331 | -122.937 | 122.8867 | 0.045776 | 58.5251 | 58.5709
21.1719 | 123.2208 | -58.5709 | 64.3662 | -0.098725 | -0.00023294 | 0.063521 | 0.063918 | -0.001976 | -0.0022943 | -0.0012006 | 0.010864 | -0.00082025 | 0.00085443 | -0.00015378 | 0.00020289 | 0.00040152 | 0.0013073 | -0.14648 | 64.3433 | -58.7265 | 64.2471 | -58.4793 | -58.8089 | -58.7723 | -0.041199 | 64.3478 | -58.6212 | -58.5938 | -58.5754 | -58.6853 | -58.4152 | -0.15564 | -0.022888 | -0.11902 | 0.091553 | -0.20142 | -0.23804 | -0.045777 | -0.082398 | -0.050354 | -0.018311 | -122.9599 | -0.004577 | 0.15564 | -0.11444 | 0.20599 | -0.064087 | 0.24719 | 122.9736 | 0.045777 | 0.027466 | 123.0698 | 122.9691 | 122.9141 | 122.9187 | -123.0927 | -122.9874 | 122.818 | -0.022888 | 58.4244 | 58.5297
22.1719 | 123.2162 | -58.5434 | 64.3936 | -0.068207 | 0.00062166 | 0.062666 | 0.06285 | 0.0018692 | -0.0010125 | -0.00077341 | 0.044434 | -0.00039305 | 0.0021362 | -0.0016492 | -1.0706e-05 | -0.00045288 | -0.0033923 | -0.059509 | 64.3387 | -58.7128 | 64.2838 | -58.4061 | -58.786 | -58.7265 | 0.027466 | 64.3662 | -58.6121 | -58.5342 | -58.5022 | -58.5892 | -58.3466 | -0.16937 | -0.054932 | -0.10986 | 0.13733 | -0.1831 | -0.24262 | -0.013732 | -0.073242 | -0.068665 | -0.027466 | -122.9279 | 0.041199 | 0.19684 | -0.045776 | 0.2655 | 0.022889 | 0.3067 | 122.9965 | 0.10986 | 0.07782 | 123.0515 | 122.9782 | 122.8821 | 122.9095 | -123.1064 | -123.0057 | 122.8271 | 0.009155 | 58.4839 | 58.5709
23.1719 | 123.2117 | -58.5892 | 64.357 | -0.18265 | 0.0021171 | 0.065443 | 0.063064 | -0.003685 | 0.0028327 | -0.002055 | -0.010498 | -0.00039305 | 0.00085443 | 0.0066822 | 0.00020289 | 0.00018792 | 0.0040845 | -0.054932 | 64.2792 | -58.7173 | 64.2746 | -58.429 | -58.8318 | -58.7494 | -0.004578 | 64.3341 | -58.6121 | -58.5709 | -58.5663 | -58.6624 | -58.3786 | -0.12817 | -0.07782 | -0.082398 | 0.16022 | -0.16022 | -0.24262 | -0.032044 | -0.11444 | -0.022889 | -0.022889 | -122.9279 | 0.022888 | 0.21057 | -0.073243 | 0.23346 | -0.050354 | 0.28839 | 122.9919 | 0.045777 | 0.041199 | 122.9965 | 122.9462 | 122.8683 | 122.9233 | -123.0743 | -122.9691 | 122.8638 | 0.01831 | 58.5342 | 58.5846
24.1719 | 123.2071 | -58.6075 | 64.4028 | -0.12924 | 0.00040806 | 0.065016 | 0.063705 | -0.0017624 | 0.0030463 | -0.0016278 | 0.013916 | 0.00046135 | 0.001068 | 0.0045458 | 0.00020289 | -0.00066648 | 0.00066654 | -0.10986 | 64.3021 | -58.7311 | 64.2471 | -58.461 | -58.8226 | -58.786 | -0.068665 | 64.3845 | -58.6441 | -58.5892 | -58.58 | -58.6853 | -58.4061 | -0.1236 | -0.10071 | -0.15564 | 0.14648 | -0.17853 | -0.21515 | -0.054932 | -0.091553 | -0.036621 | -0.018311 | -122.9919 | 0.027466 | 0.20142 | -0.07782 | 0.23804 | -0.041199 | 0.27008 | 122.9782 | 0.064087 | 0.054932 | 123.0331 | 123.0286 | 122.9095 | 122.9919 | -123.1338 | -123.0469 | 122.8546 | 0.018311 | 58.4976 | 58.5388
25.1719 | 123.143 | -58.58 | 64.3845 | -0.060578 | -0.00023294 | 0.063734 | 0.068191 | 0.0033646 | -0.0025079 | 0.00072199 | -0.062378 | 0.0030249 | -0.00042717 | 0.0045458 | 0.00041649 | 0.00082892 | -0.0029651 | -0.022888 | 64.3295 | -58.7311 | 64.2654 | -58.4656 | -58.8318 | -58.7997 | 0.018311 | 64.4119 | -58.6166 | -58.6075 | -58.5983 | -58.7128 | -58.4106 | -0.15106 | -0.054931 | -0.11902 | 0.11444 | -0.21973 | -0.25177 | -0.068665 | -0.10071 | -0.036621 | 0.027466 | -122.9919 | -0.018311 | 0.16937 | -0.13275 | 0.20599 | -0.096131 | 0.2655 | 122.9965 | 0.01831 | 0.009155 | 123.0606 | 123.0286 | 122.9095 | 122.9919 | -123.1155 | -123.0011 | 122.8455 | -0.027466 | 58.5571 | 58.5983
26.1719 | 123.2346 | -58.58 | 64.357 | -0.12924 | 0.0027579 | 0.064803 | 0.063277 | -0.00026703 | -0.00037171 | 0.0011494 | -0.0074462 | 0.00046135 | 0.00064083 | 0.00091422 | -0.00022431 | 0.0014697 | 0.00066654 | -0.064087 | 64.2792 | -58.7357 | 64.2929 | -58.4061 | -58.8181 | -58.7494 | 0.004578 | 64.325 | -58.6075 | -58.5571 | -58.5205 | -58.6624 | -58.3603 | -0.15564 | -0.07782 | -0.064087 | 0.17395 | -0.16937 | -0.23804 | -0.013733 | -0.082397 | -0.027466 | -0.032044 | -122.9141 | 0.059509 | 0.21973 | -0.082398 | 0.24719 | -0.054932 | 0.32959 | 123.0286 | 0.086975 | 0.050354 | 123.0148 | 122.9324 | 122.8592 | 122.905 | -123.0927 | -122.9645 | 122.8729 | 0.022888 | 58.5159 | 58.5846
27.1719 | 123.2895 | -58.5388 | 64.3478 | -0.083466 | -0.00066014 | 0.064589 | 0.064986 | 0.00058737 | -0.0016535 | -0.0031232 | 0.032227 | -0.00060665 | -0.0010682 | -0.006349 | -0.0010787 | 0.0010425 | 0.00023934 | -0.009155 | 64.3478 | -58.6945 | 64.3021 | -58.3694 | -58.7494 | -58.699 | 0.11444 | 64.3616 | -58.5846 | -58.5159 | -58.4656 | -58.5892 | -58.3237 | -0.15564 | 0 | -0.045776 | 0.16937 | -0.16022 | -0.21057 | -0.004578 | -0.054932 | -0.045777 | 0.013733 | -122.8638 | 0.073242 | 0.21515 | -0.050354 | 0.26093 | -0.004577 | 0.32501 | 122.9965 | 0.11902 | 0.068665 | 123.0423 | 122.9462 | 122.8867 | 122.9004 | -123.0423 | -122.9324 | 122.8409 | 0.022888 | 58.5297 | 58.6533
28.1719 | 123.1979 | -58.5709 | 64.389 | -0.098725 | 0.00083526 | 0.063521 | 0.062209 | 0.0010148 | -0.0010125 | -0.0012006 | 0.029175 | -0.0025293 | -0.00021357 | 5.9824e-05 | 0.0012711 | -0.0028027 | 0.0013073 | -0.068665 | 64.3021 | -58.7173 | 64.2426 | -58.4747 | -58.8226 | -58.7769 | -0.041199 | 64.3387 | -58.6166 | -58.6075 | -58.548 | -58.6395 | -58.3969 | -0.14648 | -0.086975 | -0.14648 | 0.096131 | -0.20599 | -0.25177 | -0.059509 | -0.10529 | -0.045776 | -0.050354 | -122.9965 | 0.022888 | 0.17395 | -0.068664 | 0.21973 | -0.022888 | 0.24262 | 122.9599 | 0.068664 | 0.009155 | 123.0194 | 122.9553 | 122.8729 | 122.9095 | -123.1064 | -123.0057 | 122.8134 | -0.036621 | 58.5022 | 58.5297
29.1719 | 123.2849 | -58.58 | 64.3799 | -0.091095 | 0.0019035 | 0.063307 | 0.063918 | 0.00037377 | -0.0014399 | 0.0011494 | 0.023071 | 0.00067495 | 2.8e-08 | 0.0051868 | -0.00086511 | -0.0010937 | -0.00061526 | -0.045776 | 64.3341 | -58.7036 | 64.2838 | -58.4152 | -58.7814 | -58.7265 | 0.018311 | 64.3433 | -58.6075 | -58.5617 | -58.5114 | -58.6258 | -58.3603 | -0.1236 | -0.045777 | -0.096131 | 0.16479 | -0.14648 | -0.20142 | -0.022888 | -0.07782 | -0.027466 | -0.036621 | -122.9416 | 0.068664 | 0.21973 | -0.045776 | 0.24719 | -0.01831 | 0.28839 | 122.9874 | 0.09613 | 0.045776 | 123.0377 | 122.9507 | 122.9141 | 122.9233 | -123.0835 | -122.9874 | 122.8638 | 0.01831 | 58.5342 | 58.5983
30.1719 | 123.1384 | -58.5938 | 64.4577 | -0.037689 | -0.0021555 | 0.063734 | 0.066695 | -0.00048063 | -0.00058531 | -0.003764 | -0.050171 | 0.0030249 | -0.00064077 | 0.0045458 | -0.00065151 | -0.00088008 | 0.0019483 | -0.027466 | 64.3845 | -58.7219 | 64.2197 | -58.4885 | -58.8364 | -58.8043 | -0.022888 | 64.4348 | -58.6075 | -58.6349 | -58.6166 | -58.7173 | -58.4381 | -0.12817 | -0.073243 | -0.23804 | 0.10529 | -0.21057 | -0.24262 | -0.082397 | -0.11444 | -0.013733 | -0.022889 | -123.0927 | -0.022888 | 0.15564 | -0.1236 | 0.16937 | -0.10986 | 0.23346 | 122.9416 | -0.009155 | -0.027466 | 123.1064 | 123.0423 | 122.9782 | 123.0286 | -123.1796 | -123.0652 | 122.8134 | -0.041199 | 58.5663 | 58.5709
31.1719 | 123.262 | -58.58 | 64.3753 | -0.052948 | -0.0015145 | 0.063948 | 0.06285 | 0.0018692 | -0.00058531 | -0.00013241 | 0.041382 | 0.0019567 | 0.0019226 | -0.0010084 | -0.00022431 | -0.0023755 | -0.00018806 | -0.041199 | 64.3387 | -58.6945 | 64.2929 | -58.4061 | -58.7677 | -58.7082 | 0.036621 | 64.357 | -58.6075 | -58.5342 | -58.4976 | -58.6487 | -58.3511 | -0.11444 | -0.036621 | -0.082397 | 0.17395 | -0.12817 | -0.18768 | -0.013733 | -0.073242 | -0.027466 | -0.01831 | -122.9095 | 0.082397 | 0.22888 | -0.068665 | 0.25635 | -0.041199 | 0.28839 | 122.9874 | 0.10986 | 0.073242 | 123.0331 | 122.9645 | 122.9187 | 122.937 | -123.0698 | -122.9828 | 122.8729 | 0.045776 | 58.5388 | 58.6166
32.1719 | 123.1476 | -58.5892 | 64.4485 | -0.0071715 | -0.00066014 | 0.063094 | 0.061996 | -0.0015488 | -0.00037171 | -0.0022686 | -0.025757 | 0.00046135 | 0.0012818 | 0.00027342 | -0.00022431 | -0.0015211 | -0.00018806 | -0.027466 | 64.3753 | -58.7036 | 64.2105 | -58.4747 | -58.8409 | -58.8043 | 0.004578 | 64.4257 | -58.5938 | -58.6349 | -58.5846 | -58.7173 | -58.4473 | -0.11444 | -0.073242 | -0.23804 | 0.11444 | -0.21515 | -0.25177 | -0.10071 | -0.13733 | -0.004578 | -0.022888 | -123.0835 | 0.004577 | 0.14191 | -0.12817 | 0.14648 | -0.1236 | 0.22888 | 122.9141 | 0.009155 | -0.041199 | 123.0789 | 123.0194 | 122.9645 | 123.0148 | -123.1522 | -123.0423 | 122.7997 | -0.045777 | 58.5617 | 58.5938
33.1719 | 123.2254 | -58.5754 | 64.3707 | -0.13687 | 0.0010489 | 0.062666 | 0.063918 | -0.00048063 | -0.00037171 | -0.0012006 | 0.035278 | 0.00088875 | 0.0025634 | 0.0026232 | 0.00020289 | 0.00061532 | -0.0029651 | -0.059509 | 64.3158 | -58.7402 | 64.2517 | -58.4518 | -58.8135 | -58.7631 | -0.009155 | 64.3707 | -58.6212 | -58.5846 | -58.548 | -58.6395 | -58.3786 | -0.16479 | -0.054932 | -0.11902 | 0.1236 | -0.18768 | -0.23804 | -0.022889 | -0.073243 | -0.045777 | 0 | -122.9553 | 0.027465 | 0.19684 | -0.064087 | 0.24261 | -0.01831 | 0.28839 | 122.9919 | 0.073242 | 0.036621 | 123.056 | 122.9919 | 122.8912 | 122.9462 | -123.111 | -122.9919 | 122.8271 | -0.009156 | 58.5159 | 58.5663
34.1719 | 123.1888 | -58.5892 | 64.3799 | -0.083466 | 0.00083526 | 0.065016 | 0.063064 | -5.343e-05 | 0.00048269 | 0.0017902 | 0.0078126 | -0.00039305 | -0.00021357 | 0.00070062 | 0.0010575 | 0.00040152 | -0.0033923 | -0.082397 | 64.3158 | -58.699 | 64.2563 | -58.4564 | -58.8318 | -58.7814 | -0.054932 | 64.3524 | -58.5983 | -58.5983 | -58.5754 | -58.6853 | -58.4198 | -0.10986 | -0.064087 | -0.1236 | 0.13275 | -0.19226 | -0.24262 | -0.082397 | -0.13275 | -0.009156 | -0.027466 | -122.9782 | 0.013733 | 0.16937 | -0.096131 | 0.17853 | -0.086975 | 0.24262 | 122.9553 | 0.022889 | 0 | 123.0148 | 122.9507 | 122.905 | 122.9416 | -123.0789 | -122.9782 | 122.8455 | -0.009156 | 58.5068 | 58.5342
35.1719 | 123.1384 | -58.5846 | 64.4119 | -0.0071715 | -0.0013009 | 0.065016 | 0.065627 | -0.0013352 | 0.0011237 | 0.00093559 | -0.053223 | 0.0011023 | 0.0012818 | 0.0034778 | -0.0015061 | 0.0012561 | 0.0023755 | -0.041199 | 64.3341 | -58.7265 | 64.2609 | -58.4518 | -58.8181 | -58.7997 | 0.032043 | 64.4211 | -58.6166 | -58.5846 | -58.5663 | -58.7036 | -58.4061 | -0.14191 | -0.07782 | -0.15106 | 0.13275 | -0.21515 | -0.23346 | -0.073243 | -0.091553 | -0.032043 | 0.009156 | -122.9965 | 0.018311 | 0.17853 | -0.11902 | 0.21057 | -0.086975 | 0.27466 | 122.9874 | 0.050354 | 0.032043 | 123.0606 | 123.0377 | 122.9187 | 123.0057 | -123.1384 | -123.0286 | 122.8455 | 0 | 58.5434 | 58.6166
36.1719 | 123.2437 | -58.5526 | 64.4073 | -0.045319 | -1.9142e-05 | 0.064803 | 0.063277 | -0.0032578 | -0.00058531 | -0.00077341 | 0.062744 | 0.0011023 | -0.0019226 | -0.005708 | -0.00022431 | 0.00040152 | 0.0025891 | 0.036621 | 64.3387 | -58.6807 | 64.3662 | -58.3282 | -58.7082 | -58.6533 | 0.11902 | 64.3936 | -58.5617 | -58.5114 | -58.4793 | -58.5663 | -58.3374 | -0.12817 | -0.068665 | -0.041199 | 0.2243 | -0.10071 | -0.15564 | 0.027466 | -0.027466 | -0.009156 | -0.013733 | -122.9187 | 0.073242 | 0.21515 | -0.013733 | 0.22431 | -0.004577 | 0.35248 | 123.0469 | 0.082398 | 0.050354 | 123.0194 | 122.9553 | 122.8912 | 122.9462 | -123.0881 | -122.9691 | 122.9187 | 0.041198 | 58.5892 | 58.6716
37.1719 | 123.111 | -58.6121 | 64.4302 | -0.052948 | 0.00040806 | 0.064803 | 0.064986 | -0.003685 | -0.0027215 | 0.00029479 | -0.0074462 | 0.00067495 | 0.0025634 | -0.0031446 | 0.00041649 | -0.00045288 | 2.554e-05 | -0.027466 | 64.4119 | -58.7036 | 64.2242 | -58.493 | -58.8364 | -58.8226 | 0.004578 | 64.4348 | -58.6075 | -58.6395 | -58.6029 | -58.7357 | -58.4335 | -0.091552 | -0.018311 | -0.20599 | 0.11902 | -0.21057 | -0.2243 | -0.11902 | -0.13275 | 0.004578 | 0.004577 | -123.0698 | 0.009156 | 0.17853 | -0.1236 | 0.17395 | -0.12817 | 0.21057 | 122.9279 | 0.004578 | -0.032043 | 123.1155 | 123.0423 | 123.024 | 123.0469 | -123.1338 | -123.0377 | 122.8363 | -0.027465 | 58.5846 | 58.6166
38.1719 | 123.2254 | -58.5617 | 64.4028 | -0.022431 | 0.0012625 | 0.063521 | 0.061996 | -0.00090783 | -0.00015811 | -0.0012006 | 0.02002 | -0.0012477 | 0.00064083 | 0.0013416 | 0.0010575 | -0.00045288 | 0.00066654 | 0.041199 | 64.3478 | -58.6761 | 64.325 | -58.3466 | -58.7311 | -58.6899 | 0.10986 | 64.3799 | -58.6121 | -58.5526 | -58.4976 | -58.6121 | -58.3603 | -0.11444 | -0.054932 | -0.07782 | 0.21515 | -0.12817 | -0.16937 | -0.013733 | -0.054932 | -0.050354 | -0.022888 | -122.9553 | 0.064087 | 0.20142 | -0.050354 | 0.25177 | 0 | 0.32959 | 123.0011 | 0.11444 | 0.05951 | 123.024 | 122.9919 | 122.9095 | 122.9416 | -123.0789 | -123.0148 | 122.8867 | 0.009156 | 58.6029 | 58.6716
39.1719 | 123.1064 | -58.5754 | 64.4577 | 0.015716 | 0.0014761 | 0.063307 | 0.063705 | -0.0030442 | -0.0018671 | 0.0011494 | -0.0074462 | -0.00017945 | -0.00085457 | 0.0019824 | 0.0010575 | -0.00066648 | 0.00023934 | -0.045776 | 64.4028 | -58.7219 | 64.2105 | -58.4976 | -58.8455 | -58.7952 | -0.009155 | 64.4028 | -58.6121 | -58.6304 | -58.6258 | -58.7219 | -58.4473 | -0.14648 | -0.054932 | -0.24719 | 0.077819 | -0.21973 | -0.27008 | -0.073242 | -0.1236 | -0.036622 | -0.054932 | -123.0881 | -0.050354 | 0.12817 | -0.14648 | 0.16479 | -0.10986 | 0.2243 | 122.9324 | -0.013732 | -0.01831 | 123.1247 | 123.0148 | 122.9782 | 122.9782 | -123.1796 | -123.0698 | 122.7859 | -0.054932 | 58.5297 | 58.5663
40.1719 | 123.2529 | -58.5754 | 64.3982 | -0.10635 | 0.0010489 | 0.062025 | 0.064345 | -0.0011214 | 0.00048269 | -0.0022686 | 0.044434 | -0.00082025 | 0.00021363 | -0.0059216 | 0.00063009 | -0.00023928 | 0.00045294 | -0.032043 | 64.3341 | -58.6945 | 64.2975 | -58.3923 | -58.754 | -58.7219 | 0.064087 | 64.3707 | -58.6075 | -58.548 | -58.4793 | -58.5892 | -58.3282 | -0.11902 | -0.064087 | -0.10071 | 0.18311 | -0.14648 | -0.17853 | -0.027466 | -0.059509 | -0.032044 | -0.027465 | -122.9462 | 0.09613 | 0.24719 | -0.013733 | 0.27924 | 0.018311 | 0.30212 | 122.9919 | 0.12817 | 0.059509 | 123.0286 | 122.9782 | 122.9095 | 122.9462 | -123.0927 | -123.0057 | 122.8729 | 0.027465 | 58.5434 | 58.6395
41.1719 | 123.1705 | -58.6029 | 64.4394 | -0.037689 | -0.00023294 | 0.061598 | 0.065414 | -0.0060348 | -0.0010125 | -0.00013241 | -0.037964 | 0.0017431 | 0.00021363 | 0.0047594 | -0.0023605 | -0.0013073 | -0.0038197 | -0.036621 | 64.4028 | -58.7219 | 64.2242 | -58.5114 | -58.8501 | -58.8226 | -0.018311 | 64.4257 | -58.6349 | -58.6166 | -58.5983 | -58.7036 | -58.4061 | -0.11902 | -0.036621 | -0.21515 | 0.091552 | -0.21973 | -0.24719 | -0.10071 | -0.12817 | -0.032044 | -0.013733 | -123.056 | 0.004577 | 0.19684 | -0.10071 | 0.22888 | -0.068664 | 0.21057 | 122.9462 | 0.036621 | 0.018311 | 123.1247 | 123.0606 | 123.0057 | 123.0286 | -123.1613 | -123.0743 | 122.8271 | -0.013733 | 58.5663 | 58.5846
42.1719 | 123.1338 | -58.5846 | 64.3982 | -0.083466 | 0.0033987 | 0.065657 | 0.064773 | -0.00026703 | -0.00037171 | -0.00077341 | -0.077637 | 0.00046135 | 0.002777 | -0.0031446 | -1.0706e-05 | -0.00023928 | 0.0015209 | 0.009155 | 64.3707 | -58.7128 | 64.2517 | -58.461 | -58.8409 | -58.7952 | 0.036621 | 64.3799 | -58.6029 | -58.5892 | -58.5938 | -58.699 | -58.4152 | -0.12817 | -0.027465 | -0.14648 | 0.1236 | -0.21057 | -0.25635 | -0.082397 | -0.12817 | -0.01831 | -0.01831 | -122.9874 | -0.009155 | 0.16937 | -0.11444 | 0.18768 | -0.096131 | 0.25177 | 122.9645 | 0.009155 | 0.013733 | 123.0835 | 122.9828 | 122.9553 | 122.9645 | -123.111 | -123.0011 | 122.8363 | -0.004577 | 58.5938 | 58.6212
43.1719 | 123.1064 | -58.6121 | 64.4257 | -0.03006 | 0.0014761 | 0.06523 | 0.062636 | -0.0024032 | -0.0012261 | -0.0016278 | 0.001709 | 0.0028113 | 0.0057678 | 0.0030506 | 0.0021255 | -0.0019483 | -0.0023243 | -0.027466 | 64.4211 | -58.7265 | 64.2197 | -58.4702 | -58.8455 | -58.7906 | 0.004578 | 64.4165 | -58.5938 | -58.6212 | -58.6075 | -58.7311 | -58.4427 | -0.11444 | -0.004577 | -0.20599 | 0.14191 | -0.17853 | -0.23346 | -0.064087 | -0.11902 | 0.018311 | -0.009155 | -123.0469 | 0.004578 | 0.16937 | -0.11902 | 0.15106 | -0.13733 | 0.25635 | 122.9462 | -0.013733 | -0.027466 | 123.1476 | 123.0103 | 123.0331 | 123.0286 | -123.1522 | -123.0194 | 122.8317 | -0.009155 | 58.5846 | 58.6166
44.1719 | 123.2071 | -58.5617 | 64.3982 | -0.037689 | 0.00083526 | 0.06288 | 0.060927 | 0.0029374 | 0.0015509 | -0.00013241 | 0.044434 | 3.4148e-05 | 0.00021363 | 0.00070062 | -0.00086511 | -0.00045288 | 0.0021619 | 0.036621 | 64.3707 | -58.6853 | 64.3158 | -58.3557 | -58.7265 | -58.6945 | 0.14191 | 64.3845 | -58.5846 | -58.5617 | -58.493 | -58.5846 | -58.3466 | -0.1236 | -0.027465 | -0.082397 | 0.20599 | -0.13275 | -0.16479 | -0.009155 | -0.041198 | -0.022888 | -0.013733 | -122.9599 | 0.068665 | 0.21515 | -0.022888 | 0.23804 | 0 | 0.32959 | 123.0011 | 0.091553 | 0.022888 | 123.056 | 122.9691 | 122.9324 | 122.9462 | -123.0835 | -122.9828 | 122.8775 | 0 | 58.5983 | 58.7036
45.1719 | 123.2391 | -58.5754 | 64.3936 | -0.11398 | -0.00066014 | 0.065443 | 0.063491 | -0.00026703 | 5.5488e-05 | -0.0024822 | 0.047485 | 0.00024775 | 0.00042723 | -0.00229 | -0.00086511 | 0.00040152 | -0.00061526 | 0.027466 | 64.3524 | -58.6853 | 64.3433 | -58.3374 | -58.7311 | -58.6807 | 0.12817 | 64.389 | -58.5892 | -58.5388 | -58.493 | -58.5754 | -58.3466 | -0.10986 | -0.041199 | -0.050354 | 0.23804 | -0.10529 | -0.15564 | 0.004578 | -0.045776 | -0.013733 | -0.004578 | -122.9324 | 0.082397 | 0.22888 | 0 | 0.24261 | 0.013733 | 0.3479 | 123.0286 | 0.09613 | 0.050354 | 123.0377 | 122.9782 | 122.9279 | 122.9645 | -123.0789 | -122.9828 | 122.9187 | 0.036621 | 58.6029 | 58.7036
46.1719 | 123.2391 | -58.5846 | 64.4211 | -0.12161 | 0.00083526 | 0.064803 | 0.061996 | 0.0027238 | -0.0016535 | -0.00055961 | 0.032227 | -0.0014613 | 0.0012818 | 0.002196 | 0.00084389 | 0.00082892 | 0.0017345 | 0.045776 | 64.3616 | -58.6761 | 64.3021 | -58.3969 | -58.7402 | -58.7265 | 0.091553 | 64.3845 | -58.5938 | -58.5297 | -58.6716 | -58.7448 | -58.4198 | -0.091552 | -0.05951 | -0.11902 | 0.18768 | -0.14191 | -0.15564 | -0.050354 | -0.064087 | -0.009155 | -0.036622 | -122.9507 | -0.086975 | 0.16479 | -0.16022 | 0.17395 | -0.15106 | 0.27923 | 122.9782 | -0.07782 | 0.064087 | 123.0377 | 122.9782 | 122.9462 | 122.9691 | -123.0972 | -123.0148 | 122.8867 | 0.054932 | 58.6304 | 58.6761
47.1719 | 123.1567 | -58.5434 | 64.4302 | -0.037689 | 0.0012625 | 0.065657 | 0.066268 | -0.00069423 | -0.0010125 | 8.1188e-05 | -0.028809 | 0.0017431 | 0.001068 | 0.00091422 | -0.00043791 | -0.00045288 | -0.00082886 | -0.009155 | 64.3845 | -58.7128 | 64.238 | -58.4885 | -58.8226 | -58.7997 | 0.018311 | 64.4348 | -58.6075 | -58.5617 | -58.5342 | -58.6853 | -58.4106 | -0.16937 | -0.045777 | -0.19226 | 0.054932 | -0.25635 | -0.27924 | -0.086975 | -0.10986 | -0.064087 | 0.004577 | -122.9919 | 0.009155 | 0.13275 | -0.14191 | 0.19684 | -0.07782 | 0.22431 | 122.9507 | 0.073242 | 0.045776 | 123.0972 | 123.0423 | 122.9279 | 122.9782 | -123.143 | -123.0377 | 122.7814 | -0.018311 | 58.5342 | 58.5617
48.1719 | 123.0927 | -58.5892 | 64.444 | -0.052948 | 0.00040806 | 0.065016 | 0.06285 | -0.00090783 | 5.5488e-05 | 0.00050839 | -0.0074462 | 0.00088875 | 0.0025634 | 5.9824e-05 | -0.00086511 | 0.00061532 | -0.00018806 | -0.032043 | 64.3936 | -58.7082 | 64.2014 | -58.4839 | -58.8547 | -58.8181 | -0.022888 | 64.4165 | -58.6166 | -58.6395 | -58.5983 | -58.7311 | -58.4518 | -0.11902 | -0.050354 | -0.24261 | 0.10528 | -0.22888 | -0.2655 | -0.10986 | -0.14648 | -0.027466 | -0.027466 | -123.0835 | -0.009156 | 0.13733 | -0.14191 | 0.1648 | -0.11444 | 0.2243 | 122.9095 | 0.01831 | -0.022888 | 123.1018 | 123.0331 | 122.9828 | 123.0057 | -123.1522 | -123.0606 | 122.7905 | -0.050354 | 58.5571 | 58.5663
49.1719 | 123.1796 | -58.6166 | 64.3845 | -0.091095 | -0.00087374 | 0.065016 | 0.066695 | 0.00016017 | -0.0018671 | 0.00093559 | -0.022705 | 0.0015295 | 0.001709 | 0.0041186 | -0.0010787 | -0.00045288 | 0.0023755 | 0.009155 | 64.3845 | -58.7082 | 64.2517 | -58.4518 | -58.8318 | -58.8043 | 0.045776 | 64.4073 | -58.6121 | -58.6075 | -58.5754 | -58.6945 | -58.4015 | -0.091553 | 0 | -0.13275 | 0.1648 | -0.18768 | -0.21515 | -0.09613 | -0.1236 | 0.004577 | 0.022889 | -122.9919 | 0.041199 | 0.21515 | -0.07782 | 0.21057 | -0.082397 | 0.25635 | 122.9599 | 0.036622 | 0.004578 | 123.0927 | 123.0194 | 123.0011 | 123.024 | -123.0927 | -122.9965 | 122.8683 | 0.009155 | 58.6258 | 58.6624
50.1719 | 123.111 | -58.5892 | 64.4302 | -0.091095 | 0.00062166 | 0.064589 | 0.06285 | -0.003685 | -0.0022943 | -0.00098701 | 0.016968 | 0.00088875 | 0.0021362 | -0.0020764 | 0.0019119 | 0.00040152 | 0.0019483 | 0.018311 | 64.3616 | -58.6761 | 64.3341 | -58.3923 | -58.8043 | -58.7311 | 0.022888 | 64.4302 | -58.5983 | -58.6349 | -58.5983 | -58.7036 | -58.429 | -0.086975 | -0.068665 | -0.096131 | 0.19684 | -0.14191 | -0.21515 | -0.054932 | -0.12817 | -0.009156 | 0 | -123.0652 | -0.009156 | 0.16022 | -0.11444 | 0.16937 | -0.10528 | 0.28381 | 123.0103 | 0 | -0.036621 | 123.0377 | 123.0286 | 122.9507 | 123.0194 | -123.1064 | -123.0286 | 122.9233 | -0.045777 | 58.6075 | 58.6121
51.1719 | 123.2346 | -58.548 | 64.3707 | -0.060578 | 0.0010489 | 0.064803 | 0.059646 | -0.0028304 | 0.0013373 | 0.0011494 | 0.026123 | -0.0027429 | -0.00021357 | 0.0045458 | 0.00020289 | -0.0017347 | 0.00088014 | 0.013733 | 64.3295 | -58.699 | 64.3341 | -58.3191 | -58.7036 | -58.6533 | 0.1236 | 64.389 | -58.5663 | -58.5388 | -58.4702 | -58.5663 | -58.3466 | -0.15106 | -0.041199 | -0.036622 | 0.22888 | -0.10528 | -0.15564 | 0.045777 | -0.004577 | -0.01831 | 0.01831 | -122.9095 | 0.07782 | 0.20142 | -0.01831 | 0.21973 | 0 | 0.37994 | 123.0331 | 0.09613 | 0.027466 | 123.0286 | 122.9553 | 122.8775 | 122.937 | -123.0698 | -122.937 | 122.8821 | 0.009156 | 58.5617 | 58.6716
52.1719 | 123.1567 | -58.5938 | 64.4257 | 0.00045798 | -0.0013009 | 0.063521 | 0.0652 | -0.001976 | 0.00026909 | 0.001363 | 0.010864 | 0.0023839 | 0.0021362 | -0.003999 | -1.0706e-05 | 0.00082892 | -0.00061526 | -0.027466 | 64.4028 | -58.699 | 64.2059 | -58.493 | -58.8409 | -58.7952 | 0.004578 | 64.4348 | -58.6212 | -58.6304 | -58.6166 | -58.7219 | -58.4518 | -0.10529 | -0.022888 | -0.21973 | 0.10071 | -0.20142 | -0.24719 | -0.09613 | -0.14191 | -0.027466 | 0.009155 | -123.056 | -0.022888 | 0.14191 | -0.12817 | 0.16937 | -0.10071 | 0.20599 | 122.905 | 0.004578 | -0.009155 | 123.1018 | 123.056 | 122.9965 | 123.0286 | -123.1247 | -123.0469 | 122.7997 | -0.036621 | 58.5663 | 58.5983
53.1719 | 123.1567 | -58.5892 | 64.4257 | 0.00045798 | 0.0031851 | 0.064375 | 0.06285 | -0.0051804 | -0.00037171 | -0.00055961 | 0.032227 | -0.00060665 | -0.00021357 | 5.9824e-05 | -0.00086511 | -0.0015211 | 0.0034435 | 0.027466 | 64.357 | -58.6899 | 64.2838 | -58.4015 | -58.754 | -58.7402 | 0.073242 | 64.389 | -58.6029 | -58.5617 | -58.6029 | -58.6349 | -58.3923 | -0.10071 | -0.068664 | -0.14191 | 0.18768 | -0.15106 | -0.1648 | -0.050354 | -0.064087 | -0.013733 | -0.036621 | -122.9874 | -0.013733 | 0.19684 | -0.045777 | 0.21057 | -0.032044 | 0.28839 | 122.9736 | 0 | 0.041198 | 123.0469 | 122.9919 | 122.9462 | 122.9782 | -123.1155 | -123.0286 | 122.8729 | 0.027465 | 58.6166 | 58.6624
54.1719 | 123.1613 | -58.5983 | 64.4348 | -0.022431 | 0.0014761 | 0.063094 | 0.064345 | -0.0013352 | -0.0014399 | -0.0018414 | -0.010498 | 0.00067495 | 0.002777 | 0.0017688 | -0.0012925 | 0.0010425 | -0.0040333 | -0.018311 | 64.389 | -58.7036 | 64.2197 | -58.4885 | -58.8501 | -58.7906 | 0.004578 | 64.4257 | -58.6121 | -58.6304 | -58.5983 | -58.7036 | -58.4427 | -0.10528 | -0.045776 | -0.21515 | 0.10986 | -0.19226 | -0.25177 | -0.086975 | -0.14649 | -0.013733 | -0.009155 | -123.0652 | 0 | 0.15564 | -0.10528 | 0.16937 | -0.091552 | 0.21515 | 122.9233 | 0.013733 | -0.01831 | 123.0927 | 123.0377 | 122.9874 | 123.024 | -123.1384 | -123.0469 | 122.818 | -0.032043 | 58.58 | 58.6029
55.1719 | 123.2346 | -58.5434 | 64.389 | -0.052948 | 0.0012625 | 0.063948 | 0.062209 | -0.0028304 | 5.5488e-05 | -0.0022686 | 0.047485 | 3.4148e-05 | 0.0012818 | 0.00048702 | -0.0017197 | -0.00066648 | 0.0013073 | 0.032043 | 64.3478 | -58.7082 | 64.3158 | -58.3969 | -58.7585 | -58.699 | 0.10071 | 64.389 | -58.5754 | -58.58 | -58.548 | -58.6304 | -58.374 | -0.16479 | -0.041199 | -0.073242 | 0.14648 | -0.15564 | -0.21515 | 0.009155 | -0.050354 | -0.032043 | 0 | -122.9691 | -0.004578 | 0.16937 | -0.086975 | 0.20142 | -0.054932 | 0.31128 | 123.024 | 0.027465 | -0.004578 | 123.056 | 122.9645 | 122.8912 | 122.9324 | -123.0972 | -122.9645 | 122.8592 | -0.036621 | 58.5754 | 58.6441
56.1719 | 123.1796 | -58.6075 | 64.444 | -0.014801 | 0.0027579 | 0.064375 | 0.065627 | 0.00251 | 0.0019781 | -0.0018414 | -0.025757 | 0.00088875 | 0.00085443 | -0.0010084 | -0.00065151 | 0.00040152 | 2.554e-05 | -0.009155 | 64.3845 | -58.7173 | 64.2105 | -58.4976 | -58.8318 | -58.8272 | -0.004578 | 64.4165 | -58.5983 | -58.6212 | -58.6395 | -58.8364 | -58.4976 | -0.10986 | -0.05951 | -0.23346 | 0.10986 | -0.21973 | -0.2243 | -0.10986 | -0.11444 | 0.009155 | -0.027466 | -123.0652 | -0.032043 | 0.10986 | -0.22888 | 0.10071 | -0.23804 | 0.21973 | 122.9279 | -0.041198 | -0.022888 | 123.1018 | 123.0148 | 122.9919 | 123.024 | -123.1613 | -123.0423 | 122.818 | -0.013733 | 58.5983 | 58.6029
57.1719 | 123.1155 | -58.6258 | 64.3799 | -0.10635 | 0.0016899 | 0.06523 | 0.066482 | 0.0035782 | 0.00069649 | -0.0018414 | -0.016602 | 0.00046135 | 0.0014954 | -0.00079478 | -0.00022431 | -0.00023928 | -0.00082886 | -0.11444 | 64.3707 | -58.786 | 64.151 | -58.5709 | -58.9417 | -58.8684 | -0.13733 | 64.389 | -58.6578 | -58.6395 | -58.6441 | -58.7769 | -58.4564 | -0.16022 | -0.009155 | -0.22888 | 0.054931 | -0.24262 | -0.31586 | -0.082397 | -0.15564 | -0.032044 | 0.009155 | -123.0194 | -0.018311 | 0.16937 | -0.15106 | 0.20142 | -0.11902 | 0.21515 | 122.937 | 0.013733 | 0.018311 | 123.1567 | 123.0469 | 122.9965 | 123.0148 | -123.1659 | -123.0377 | 122.7768 | -0.013733 | 58.5114 | 58.4885
58.1719 | 123.2025 | -58.5526 | 64.4028 | -0.083466 | 0.0010489 | 0.065016 | 0.062423 | -0.0013352 | 0.00026909 | -0.0014142 | 0.050537 | 0.00067495 | 0.0012818 | -0.0014356 | -1.0706e-05 | -0.0017347 | 0.00045294 | 0.036621 | 64.3707 | -58.6853 | 64.3295 | -58.3511 | -58.7402 | -58.6853 | 0.11902 | 64.3753 | -58.5938 | -58.5663 | -58.5068 | -58.6258 | -58.3466 | -0.13275 | -0.032043 | -0.073242 | 0.20142 | -0.13275 | -0.18768 | 0 | -0.054931 | -0.041199 | -0.027466 | -122.9691 | 0.045776 | 0.20599 | -0.073242 | 0.24719 | -0.032043 | 0.33417 | 123.0148 | 0.086975 | 0.027466 | 123.056 | 122.9691 | 122.9233 | 122.9279 | -123.0881 | -122.9965 | 122.8821 | -0.013733 | 58.5892 | 58.6716
59.1719 | 123.2391 | -58.548 | 64.3982 | -0.091095 | -0.0013009 | 0.064375 | 0.06285 | -0.003685 | 0.00048269 | -0.00077341 | 0.078003 | 0.00046135 | 0.00042723 | 0.00027342 | -0.0010787 | -0.0015211 | -0.0025379 | 0.013733 | 64.3341 | -58.6807 | 64.3341 | -58.342 | -58.7082 | -58.6624 | 0.14191 | 64.3799 | -58.6166 | -58.5297 | -58.4702 | -58.58 | -58.342 | -0.13275 | -0.064087 | -0.064087 | 0.20599 | -0.11444 | -0.16022 | 0.01831 | -0.027466 | -0.068664 | -0.01831 | -122.9279 | 0.07782 | 0.20599 | -0.032043 | 0.27466 | 0.036621 | 0.33875 | 123.0148 | 0.14648 | 0.086975 | 123.0148 | 122.9965 | 122.8821 | 122.9279 | -123.0789 | -123.0148 | 122.8821 | 0.018311 | 58.5617 | 58.6899
60.1719 | 123.2391 | -58.5205 | 64.3982 | -0.060578 | 0.0010489 | 0.064375 | 0.06285 | -0.00048063 | -0.0018671 | 0.00072199 | 0.047485 | 0.00088875 | 0.001068 | 0.0034778 | -0.0010787 | -0.00045288 | -0.0010425 | 0.004578 | 64.3112 | -58.6899 | 64.325 | -58.3374 | -58.7219 | -58.6624 | 0.15564 | 64.3753 | -58.58 | -58.5022 | -58.4747 | -58.5846 | -58.3237 | -0.16937 | -0.086975 | -0.073242 | 0.18311 | -0.14191 | -0.20142 | 0.027465 | -0.032044 | -0.059509 | -0.022888 | -122.9004 | 0.045777 | 0.19684 | -0.064087 | 0.25635 | -0.004578 | 0.35248 | 123.0148 | 0.10529 | 0.07782 | 123.0011 | 122.9553 | 122.8317 | 122.8958 | -123.0881 | -122.9782 | 122.8455 | 0.018311 | 58.5251 | 58.6761
61.1719 | 123.2574 | -58.5526 | 64.3662 | -0.060578 | -0.0010873 | 0.064375 | 0.062209 | 0.00037377 | -0.0012261 | -0.00098701 | 0.044434 | 0.0013159 | 0.0014954 | 0.00048702 | -0.00086511 | -0.00045288 | -0.0010425 | 0.009155 | 64.3387 | -58.6853 | 64.3204 | -58.3603 | -58.7173 | -58.6853 | 0.14191 | 64.357 | -58.5526 | -58.5205 | -58.4518 | -58.5754 | -58.3237 | -0.13275 | -0.027466 | -0.045776 | 0.19226 | -0.13275 | -0.16479 | 0 | -0.032043 | 0 | -0.009155 | -122.8867 | 0.10071 | 0.22888 | -0.022888 | 0.22888 | -0.022888 | 0.32501 | 123.0057 | 0.10071 | 0.032043 | 123.024 | 122.9095 | 122.8912 | 122.9095 | -123.0515 | -122.9187 | 122.8729 | 0.032043 | 58.5617 | 58.6945
62.1719 | 123.2117 | -58.6029 | 64.3707 | -0.037689 | 0.00083526 | 0.062453 | 0.065627 | -0.00090783 | -0.0010125 | 0.00029479 | -0.028809 | 0.00024775 | 2.8e-08 | 0.003905 | -0.0023605 | -0.0013073 | -0.0014697 | -0.032043 | 64.3845 | -58.7128 | 64.2197 | -58.5159 | -58.8501 | -58.8089 | -0.009155 | 64.4119 | -58.6349 | -58.6121 | -58.6029 | -58.7219 | -58.429 | -0.10986 | 0.013732 | -0.15106 | 0.086975 | -0.20599 | -0.24719 | -0.09613 | -0.13733 | -0.032044 | 0.041198 | -122.9828 | 0 | 0.17395 | -0.11902 | 0.20599 | -0.086975 | 0.19684 | 122.9324 | 0.032044 | 0.022888 | 123.0972 | 123.0469 | 122.9874 | 123.0148 | -123.0835 | -123.0057 | 122.8226 | -0.009156 | 58.5709 | 58.5938
63.1719 | 123.1384 | -58.6029 | 64.4302 | -0.075836 | 0.00019446 | 0.06523 | 0.064132 | -0.0011214 | -0.00015811 | -0.00034601 | -0.028809 | 0.0023839 | 0.0023498 | 0.00070062 | -0.0021469 | 0.0018969 | 0.00066654 | -0.018311 | 64.4073 | -58.7311 | 64.2105 | -58.5022 | -58.8409 | -58.8135 | -0.009155 | 64.444 | -58.6121 | -58.6212 | -58.6029 | -58.7173 | -58.4244 | -0.12817 | -0.022888 | -0.21973 | 0.10071 | -0.21057 | -0.23804 | -0.082398 | -0.10986 | -0.009156 | 0.013733 | -123.0515 | 0 | 0.17853 | -0.11444 | 0.18768 | -0.10529 | 0.22888 | 122.9416 | 0.009156 | -0.009155 | 123.1384 | 123.056 | 123.0103 | 123.0469 | -123.1613 | -123.0423 | 122.8134 | -0.018311 | 58.5846 | 58.5938
64.1719 | 123.1796 | -58.5663 | 64.4119 | -0.083466 | -0.00087374 | 0.063094 | 0.064345 | 0.0018692 | 0.00048269 | -0.00055961 | 0.047485 | -0.00039305 | 0.00085443 | -0.0042126 | -0.00022431 | -0.0025891 | 0.00045294 | 0.041199 | 64.3204 | -58.6624 | 64.3066 | -58.3786 | -58.7494 | -58.7036 | 0.09613 | 64.3982 | -58.5983 | -58.6258 | -58.5983 | -58.6029 | -58.3237 | -0.096131 | -0.091552 | -0.10528 | 0.18768 | -0.13733 | -0.18311 | -0.041198 | -0.086975 | -0.032044 | -0.013733 | -123.0377 | -0.032044 | 0.24262 | -0.036621 | 0.27466 | -0.004577 | 0.28381 | 122.9691 | 0 | -0.027465 | 122.9828 | 122.9965 | 122.8867 | 122.9645 | -123.0743 | -123.0103 | 122.8729 | -0.059509 | 58.6075 | 58.6624
65.1719 | 123.1064 | -58.5983 | 64.4119 | -0.083466 | 0.00040806 | 0.063521 | 0.061996 | 0.0012284 | 0.0015509 | 8.1188e-05 | 0.02002 | 3.4148e-05 | 0.0021362 | -0.00058098 | 0.0010575 | -0.00088008 | -0.0027515 | 0.004578 | 64.3753 | -58.7036 | 64.238 | -58.4564 | -58.8272 | -58.786 | 0.036621 | 64.4257 | -58.6121 | -58.6349 | -58.5892 | -58.7036 | -58.4335 | -0.10528 | -0.036621 | -0.17395 | 0.14191 | -0.18768 | -0.22888 | -0.082398 | -0.1236 | -0.013733 | 0.013733 | -123.0469 | 0.009156 | 0.1648 | -0.10528 | 0.17853 | -0.091552 | 0.24719 | 122.9416 | 0.022889 | -0.022888 | 123.0789 | 123.0377 | 122.9736 | 123.024 | -123.1155 | -123.024 | 122.8363 | -0.036621 | 58.6029 | 58.6349
66.1719 | 123.0972 | -58.6166 | 64.444 | -0.045319 | 0.0016899 | 0.064803 | 0.064986 | 0.0035782 | -0.00079891 | -0.002696 | 0.0047608 | 0.0013159 | -0.0019226 | 0.0043322 | 0.0010575 | -0.0017347 | -0.0016833 | 0.027466 | 64.3616 | -58.6945 | 64.2426 | -58.4473 | -58.7906 | -58.7631 | 0.027466 | 64.4165 | -58.6121 | -58.6258 | -58.5983 | -58.7036 | -58.4518 | -0.07782 | -0.082398 | -0.20142 | 0.16937 | -0.14648 | -0.17395 | -0.068665 | -0.09613 | 0.004577 | -0.027466 | -123.0698 | 0.01831 | 0.1648 | -0.086975 | 0.16022 | -0.091552 | 0.24719 | 122.937 | 0.013733 | -0.013732 | 123.056 | 123.0286 | 122.9782 | 123.0331 | -123.1384 | -123.056 | 122.8592 | -0.009155 | 58.6441 | 58.6441
67.1719 | 123.2346 | -58.5526 | 64.3982 | -0.052948 | -0.00023294 | 0.066298 | 0.063491 | -0.00069423 | 0.00069649 | -0.00077341 | 0.03833 | -0.0010339 | -0.00021357 | 5.9824e-05 | -0.00065151 | -0.0017347 | 0.00045294 | 0.013733 | 64.3341 | -58.6807 | 64.3616 | -58.3237 | -58.7036 | -58.6624 | 0.13733 | 64.3845 | -58.5938 | -58.5251 | -58.4747 | -58.5617 | -58.3282 | -0.12817 | -0.064087 | -0.036621 | 0.22888 | -0.10986 | -0.15106 | 0.01831 | -0.022888 | -0.041199 | -0.013733 | -122.9233 | 0.07782 | 0.2243 | -0.009156 | 0.2655 | 0.032043 | 0.35706 | 123.0423 | 0.11902 | 0.068665 | 123.0148 | 122.9782 | 122.8867 | 122.937 | -123.0789 | -122.9919 | 122.9141 | 0.027466 | 58.5663 | 58.6899
68.1719 | 123.2346 | -58.5617 | 64.3662 | -0.052948 | -0.00044654 | 0.063948 | 0.064345 | -0.00048063 | -0.00058531 | -0.0033368 | 0.02002 | 0.00046135 | 0.0012818 | 0.00091422 | -0.00065151 | -0.0013073 | -0.0018971 | -0.009155 | 64.3707 | -58.6624 | 64.2838 | -58.4839 | -58.7219 | -58.7128 | 0.068665 | 64.3707 | -58.5846 | -58.5388 | -58.4976 | -58.6166 | -58.3466 | -0.10071 | 0.004578 | -0.082398 | 0.07782 | -0.15106 | -0.16022 | -0.050354 | -0.059509 | -0.022888 | 0.004578 | -122.905 | 0.064087 | 0.21515 | -0.054931 | 0.23804 | -0.032043 | 0.17853 | 122.9462 | 0.086975 | 0.045777 | 123.0331 | 122.9553 | 122.9324 | 122.9324 | -123.0286 | -122.9507 | 122.8455 | 0.022889 | 58.5526 | 58.6304
69.1719 | 123.1201 | -58.548 | 64.4165 | -0.075836 | -1.9142e-05 | 0.06523 | 0.063064 | 0.0033646 | 0.0017645 | -0.0016278 | 0.035278 | 0.00046135 | -0.00021357 | -0.0044262 | -0.0023605 | 0.00082892 | -0.0038197 | 0.009155 | 64.3707 | -58.699 | 64.2929 | -58.4015 | -58.7631 | -58.7402 | 0.068665 | 64.4119 | -58.58 | -58.6075 | -58.58 | -58.6853 | -58.4198 | -0.15106 | -0.045776 | -0.1236 | 0.14649 | -0.19226 | -0.21515 | -0.041198 | -0.064087 | -0.032043 | -0.004578 | -123.024 | -0.032043 | 0.12817 | -0.13733 | 0.16022 | -0.10529 | 0.29755 | 122.9919 | 0 | -0.027466 | 123.0698 | 122.9919 | 122.9187 | 122.9599 | -123.1155 | -122.9965 | 122.8409 | -0.059509 | 58.5571 | 58.6166
70.1719 | 123.2117 | -58.5571 | 64.4028 | -0.045319 | -0.00023294 | 0.062453 | 0.060927 | -0.0030442 | 0.0030463 | -0.0022686 | 0.029175 | -0.00039305 | -0.0010682 | 0.00070062 | -0.0010787 | -0.0028027 | 0.00045294 | 0.032043 | 64.3341 | -58.6899 | 64.3387 | -58.342 | -58.7219 | -58.699 | 0.14191 | 64.3753 | -58.5846 | -58.5434 | -58.4839 | -58.5754 | -58.3282 | -0.13275 | -0.068665 | -0.064087 | 0.21515 | -0.14191 | -0.16479 | -0.009156 | -0.032044 | -0.027466 | -0.027466 | -122.9462 | 0.073242 | 0.22888 | -0.01831 | 0.25635 | 0.009156 | 0.3479 | 123.0286 | 0.10071 | 0.041199 | 123.024 | 122.9599 | 122.8912 | 122.9324 | -123.0927 | -122.9874 | 122.8958 | 0.013733 | 58.5892 | 58.699
71.1719 | 123.1384 | -58.5846 | 64.4669 | -0.11398 | -1.9142e-05 | 0.062239 | 0.063705 | 0.00037377 | -0.00037171 | 0.0011494 | 0.0078126 | 0.00067495 | -0.0010682 | -0.007417 | -0.00065151 | -0.00066648 | -0.0036059 | 0.036621 | 64.357 | -58.6624 | 64.3066 | -58.4061 | -58.7585 | -58.7036 | 0.082397 | 64.4028 | -58.58 | -58.5892 | -58.5388 | -58.6533 | -58.4015 | -0.07782 | -0.10986 | -0.16022 | 0.17853 | -0.11902 | -0.17395 | -0.041198 | -0.09613 | 0.004578 | -0.064087 | -123.056 | 0.045777 | 0.18311 | -0.068664 | 0.17853 | -0.073242 | 0.25635 | 122.9691 | 0.041199 | -0.009155 | 123.0194 | 122.9828 | 122.9416 | 122.9874 | -123.1293 | -123.0469 | 122.8912 | -0.004577 | 58.6212 | 58.667
72.1719 | 123.1842 | -58.5709 | 64.4119 | -0.022431 | 0.0023307 | 0.064162 | 0.062636 | -0.0028304 | 0.0015509 | -0.00034601 | 0.023071 | -0.00017945 | 0.0014954 | -0.0042126 | -0.0023605 | -0.0015211 | -0.0018971 | 0.041199 | 64.3478 | -58.699 | 64.325 | -58.3694 | -58.7357 | -58.7219 | 0.10071 | 64.389 | -58.5938 | -58.5846 | -58.5434 | -58.6258 | -58.3694 | -0.12817 | -0.064087 | -0.086975 | 0.20142 | -0.15106 | -0.1648 | -0.022888 | -0.036621 | -0.022888 | -0.022888 | -122.9965 | 0.027466 | 0.20142 | -0.054931 | 0.2243 | -0.032043 | 0.32959 | 123.024 | 0.050354 | 0.009155 | 123.0469 | 122.9828 | 122.9187 | 122.9599 | -123.111 | -123.0057 | 122.8958 | -0.013733 | 58.6121 | 58.6716
73.1719 | 123.2117 | -58.5571 | 64.389 | -0.037689 | 0.00083526 | 0.066084 | 0.063064 | 0.0012284 | -0.00037171 | 0.00050839 | 0.035278 | 0.00024775 | 2.8e-08 | -0.001222 | 0.00063009 | -0.00088008 | -0.0021107 | 0.045776 | 64.3433 | -58.667 | 64.3341 | -58.3649 | -58.754 | -58.7128 | 0.10986 | 64.3982 | -58.5754 | -58.5617 | -58.5297 | -58.6166 | -58.3603 | -0.10986 | -0.045776 | -0.054932 | 0.19226 | -0.15564 | -0.19684 | -0.045777 | -0.086975 | -0.01831 | 0.009155 | -122.9507 | 0.027466 | 0.19684 | -0.059509 | 0.21515 | -0.041199 | 0.30212 | 123.0011 | 0.045776 | 0.013732 | 123.0103 | 122.9736 | 122.9004 | 122.9553 | -123.056 | -122.9645 | 122.8912 | -0.004578 | 58.6029 | 58.667
74.1719 | 123.2071 | -58.5663 | 64.4073 | -0.075836 | 0.00019446 | 0.067152 | 0.063705 | 0.00037377 | 0.00069649 | -0.00077341 | 0.023071 | 3.4148e-05 | 0.00085443 | 0.0028368 | 0.00041649 | -0.0017347 | 0.0021619 | 0.027466 | 64.3433 | -58.6761 | 64.3158 | -58.374 | -58.7448 | -58.699 | 0.11444 | 64.4119 | -58.5754 | -58.5526 | -58.5159 | -58.6166 | -58.342 | -0.10986 | -0.064087 | -0.091553 | 0.19226 | -0.13275 | -0.17853 | -0.022889 | -0.068665 | -0.009155 | 0.004577 | -122.9599 | 0.050354 | 0.2243 | -0.050354 | 0.23346 | -0.041199 | 0.30212 | 122.9919 | 0.059509 | 0.022888 | 123.0194 | 122.9874 | 122.9095 | 122.9782 | -123.0835 | -122.9828 | 122.8821 | 0.013733 | 58.5938 | 58.6807
75.1719 | 123.23 | -58.5526 | 64.3707 | -0.068207 | -0.00023294 | 0.064589 | 0.062423 | 0.001442 | 0.0011237 | -0.005473 | 0.059692 | -0.0010339 | 0.00085443 | -0.00058098 | -0.00065151 | -0.00088008 | -0.0016833 | -0.004578 | 64.3433 | -58.699 | 64.3066 | -58.3786 | -58.7448 | -58.7082 | 0.10071 | 64.3707 | -58.5938 | -58.548 | -58.4839 | -58.5938 | -58.3191 | -0.14648 | -0.027466 | -0.064087 | 0.17395 | -0.15564 | -0.19226 | -0.009155 | -0.045776 | -0.041199 | 0 | -122.9187 | 0.068664 | 0.23346 | -0.041199 | 0.27466 | 0 | 0.32043 | 123.0057 | 0.10986 | 0.045776 | 123.0423 | 122.9645 | 122.8958 | 122.9233 | -123.0698 | -122.9645 | 122.8592 | 0.004577 | 58.548 | 58.6533
76.1719 | 123.1979 | -58.5342 | 64.4211 | -0.098725 | 0.0019035 | 0.066298 | 0.062209 | 0.0012284 | 0.00026909 | 0.0011494 | -0.0013428 | -0.00082025 | 2.8e-08 | -0.00079478 | -0.0015061 | -0.00023928 | -0.0042469 | 0.027466 | 64.3341 | -58.6853 | 64.3341 | -58.3603 | -58.7311 | -58.6807 | 0.12817 | 64.3845 | -58.5938 | -58.5388 | -58.4839 | -58.6121 | -58.3557 | -0.15106 | -0.086976 | -0.086976 | 0.17395 | -0.14648 | -0.19684 | 0.004578 | -0.045776 | -0.059509 | -0.036622 | -122.9599 | 0.050354 | 0.17853 | -0.07782 | 0.23804 | -0.018311 | 0.32501 | 123.0194 | 0.10986 | 0.054932 | 123.0194 | 122.9782 | 122.8683 | 122.9187 | -123.1064 | -123.0148 | 122.8683 | -0.004577 | 58.5617 | 58.6624
77.1719 | 123.1201 | -58.5892 | 64.4257 | -0.022431 | 0.0012625 | 0.063521 | 0.064773 | 0.0016556 | -0.00079891 | -0.00055961 | -0.0043946 | 0.00067495 | 0.001068 | 0.00070062 | 0.00084389 | -0.0015211 | -0.0012561 | 0.036621 | 64.3616 | -58.6945 | 64.2792 | -58.4061 | -58.7631 | -58.7448 | 0.073242 | 64.4211 | -58.6029 | -58.6212 | -58.5709 | -58.7082 | -58.4335 | -0.10529 | -0.064087 | -0.14648 | 0.1831 | -0.15564 | -0.17395 | -0.050354 | -0.068665 | -0.013733 | -0.004577 | -123.0469 | 0.01831 | 0.15564 | -0.11902 | 0.16937 | -0.10529 | 0.28839 | 122.9736 | 0.032043 | -0.018311 | 123.056 | 123.024 | 122.9507 | 123.0103 | -123.1201 | -123.0286 | 122.8683 | -0.032044 | 58.6258 | 58.6624
78.1719 | 123.1247 | -58.58 | 64.4348 | -0.083466 | 0.00062166 | 0.064803 | 0.063277 | 0.0029374 | 0.0011237 | -0.0033368 | -0.010498 | -0.00039305 | 0.001068 | -0.00058098 | 0.00020289 | -0.00066648 | 0.0015209 | 0.036621 | 64.3524 | -58.6945 | 64.3066 | -58.4106 | -58.7494 | -58.7311 | 0.068665 | 64.4119 | -58.6075 | -58.6075 | -58.5617 | -58.6716 | -58.4061 | -0.11444 | -0.082397 | -0.12817 | 0.16937 | -0.15106 | -0.16937 | -0.036621 | -0.054932 | -0.027466 | -0.022888 | -123.0423 | 0.01831 | 0.17395 | -0.091553 | 0.20142 | -0.064087 | 0.28381 | 123.0011 | 0.045776 | 0 | 123.0469 | 123.0194 | 122.9324 | 122.9919 | -123.1293 | -123.0423 | 122.8867 | -0.027466 | 58.6166 | 58.6487
79.1719 | 123.0743 | -58.6029 | 64.4211 | -0.052948 | 0.00062166 | 0.064375 | 0.063705 | -0.0038986 | 5.5488e-05 | -0.0014142 | -0.022705 | 3.4148e-05 | -0.0021362 | -0.0027174 | 0.00041649 | 0.00018792 | -0.0033923 | 0 | 64.3799 | -58.7311 | 64.2151 | -58.493 | -58.8501 | -58.8043 | 0.018311 | 64.4257 | -58.6121 | -58.6304 | -58.5938 | -58.7128 | -58.4427 | -0.12817 | -0.041199 | -0.20599 | 0.10986 | -0.20142 | -0.24719 | -0.073242 | -0.11902 | -0.009156 | 0.004577 | -123.0515 | 0.009155 | 0.16022 | -0.10986 | 0.16937 | -0.10071 | 0.23804 | 122.9462 | 0.018311 | -0.01831 | 123.111 | 123.0377 | 122.9828 | 123.0286 | -123.1522 | -123.0331 | 122.818 | -0.027466 | 58.6029 | 58.6212
80.1719 | 123.1338 | -58.5754 | 64.4165 | -0.060578 | 0.00019446 | 0.063734 | 0.063918 | -0.0011214 | -0.00079891 | -0.00077341 | 0.010864 | 0.0019567 | 0.001709 | -0.0027174 | 0.0012711 | -0.00023928 | -0.0027515 | 0.045776 | 64.3387 | -58.6853 | 64.3112 | -58.3786 | -58.7494 | -58.7219 | 0.10071 | 64.4028 | -58.5938 | -58.5617 | -58.5388 | -58.6533 | -58.3923 | -0.10986 | -0.07782 | -0.10529 | 0.19684 | -0.14648 | -0.17395 | -0.036621 | -0.064087 | -0.018311 | -0.013733 | -122.9782 | 0.036621 | 0.18311 | -0.07782 | 0.20142 | -0.059509 | 0.3067 | 122.9965 | 0.054932 | 0.032043 | 123.024 | 122.9965 | 122.9141 | 122.9782 | -123.1018 | -123.0103 | 122.8867 | 0.013732 | 58.6212 | 58.6761
81.1719 | 123.0972 | -58.5663 | 64.4348 | -0.052948 | 0.00040806 | 0.065443 | 0.06285 | 0.00016017 | -0.0018671 | -0.0016278 | -0.0043946 | 0.0011023 | -0.00085457 | -0.0018628 | 0.00084389 | -2.5678e-05 | -0.00061526 | -0.009155 | 64.3936 | -58.7036 | 64.2242 | -58.4793 | -58.8272 | -58.7769 | 0.018311 | 64.4394 | -58.6121 | -58.6349 | -58.5892 | -58.7036 | -58.461 | -0.13733 | -0.041198 | -0.21057 | 0.086975 | -0.21057 | -0.26093 | -0.073242 | -0.1236 | -0.045777 | 0.004578 | -123.0698 | -0.022888 | 0.10529 | -0.13733 | 0.15106 | -0.091552 | 0.2243 | 122.9279 | 0.022889 | -0.022888 | 123.0972 | 123.0515 | 122.9599 | 123.0057 | -123.1384 | -123.0469 | 122.7905 | -0.068665 | 58.5571 | 58.5846
82.1719 | 123.111 | -58.5983 | 64.4211 | -0.045319 | 0.0014761 | 0.061598 | 0.063491 | -5.343e-05 | -0.0033625 | -0.00013241 | -0.037964 | 0.00046135 | 0.0021362 | -0.0010084 | -0.0010787 | 0.0010425 | -0.00082886 | -0.022888 | 64.3982 | -58.6945 | 64.1373 | -58.6395 | -58.8318 | -58.8226 | -0.013733 | 64.4119 | -58.6121 | -58.6349 | -58.6075 | -58.7036 | -58.4427 | -0.09613 | -0.022889 | -0.28381 | -0.041198 | -0.2243 | -0.23346 | -0.12817 | -0.13733 | -0.013733 | -0.009156 | -123.056 | -0.009155 | 0.15564 | -0.10528 | 0.16937 | -0.091552 | 0.054932 | 122.8317 | 0.004578 | -0.022888 | 123.0927 | 123.024 | 122.9965 | 123.0103 | -123.1155 | -123.0331 | 122.7356 | -0.036621 | 58.5754 | 58.5846
83.1719 | 123.1247 | -58.6121 | 64.4348 | -0.052948 | 0.00083526 | 0.064803 | 0.065414 | -0.0017624 | 5.5488e-05 | -0.00013241 | -0.028809 | 0.0011023 | 0.00064083 | 0.00091422 | 0.00020289 | -0.00066648 | -0.0025379 | -0.041199 | 64.3707 | -58.7357 | 64.151 | -58.6395 | -58.8409 | -58.8181 | -0.027466 | 64.4257 | -58.6258 | -58.6166 | -58.5938 | -58.7036 | -58.4335 | -0.1236 | -0.064086 | -0.28381 | -0.027465 | -0.20599 | -0.22888 | -0.082397 | -0.10528 | -0.013732 | -0.009155 | -123.0515 | 0.018311 | 0.17853 | -0.091552 | 0.19226 | -0.07782 | 0.096131 | 122.8867 | 0.032043 | 0.009155 | 123.1064 | 123.0515 | 122.9828 | 123.0377 | -123.1705 | -123.0606 | 122.7631 | -0.004577 | 58.5709 | 58.5846
84.1719 | 123.1522 | -58.5571 | 64.4165 | -0.068207 | 0.00019446 | 0.06758 | 0.063064 | -0.0021896 | -0.0014399 | -0.0016278 | 0.026123 | 0.0013159 | -0.00064077 | -0.0035718 | 0.00063009 | -0.0013073 | 2.554e-05 | 0.004578 | 64.3524 | -58.699 | 64.3158 | -58.3832 | -58.754 | -58.7128 | 0.091553 | 64.389 | -58.5846 | -58.5754 | -58.5388 | -58.6533 | -58.3649 | -0.14191 | -0.064087 | -0.10071 | 0.17395 | -0.15564 | -0.19684 | -0.013733 | -0.054931 | -0.027466 | -0.027466 | -122.9919 | 0.018311 | 0.19226 | -0.09613 | 0.21973 | -0.068664 | 0.31586 | 123.0148 | 0.045777 | 0.009156 | 123.0515 | 122.9736 | 122.9095 | 122.9462 | -123.1155 | -123.0011 | 122.8729 | -0.01831 | 58.5617 | 58.6487
85.1719 | 123.1934 | -58.5938 | 64.3982 | -0.052948 | -0.0021555 | 0.064803 | 0.061782 | -0.0021896 | -0.00037171 | -0.00098701 | 0.035278 | -0.0018885 | -0.00021357 | 0.00048702 | -0.00065151 | -0.0015211 | -0.0053149 | 0.027466 | 64.3616 | -58.6716 | 64.3021 | -58.3832 | -58.7723 | -58.7128 | 0.086975 | 64.4211 | -58.5754 | -58.5892 | -58.548 | -58.6304 | -58.374 | -0.07782 | -0.036621 | -0.09613 | 0.21057 | -0.11902 | -0.17853 | -0.041199 | -0.10071 | 0.018311 | 0.022889 | -122.9874 | 0.045776 | 0.21973 | -0.036621 | 0.20142 | -0.054932 | 0.28839 | 122.9736 | 0.027465 | -0.013733 | 123.0331 | 122.9965 | 122.9553 | 123.0148 | -123.0698 | -122.9736 | 122.8958 | 0.004578 | 58.6212 | 58.6807
86.1719 | 123.1338 | -58.5892 | 64.444 | -0.11398 | 0.00019446 | 0.064375 | 0.063064 | -0.0011214 | 0.00069649 | 0.00093559 | 0.02002 | 0.0021703 | 0.00085443 | -0.0080578 | -0.0012925 | -0.0028027 | -0.0025379 | 0.041199 | 64.3524 | -58.699 | 64.2929 | -58.3786 | -58.7585 | -58.7128 | 0.07782 | 64.4165 | -58.5938 | -58.5983 | -58.548 | -58.667 | -58.3969 | -0.10986 | -0.091553 | -0.15106 | 0.21057 | -0.1236 | -0.16937 | -0.013733 | -0.059509 | -0.004578 | -0.027466 | -123.0423 | 0.041198 | 0.19226 | -0.07782 | 0.19684 | -0.073242 | 0.32043 | 122.9919 | 0.045776 | -0.004578 | 123.0515 | 123.0103 | 122.9416 | 123.0057 | -123.143 | -123.0377 | 122.8821 | -0.009156 | 58.6304 | 58.667
87.1719 | 123.1064 | -58.6075 | 64.4165 | -0.045319 | 0.00019446 | 0.062666 | 0.062423 | -0.0011214 | 0.00026909 | 0.00072199 | 0.0078126 | 0.00046135 | 2.8e-08 | -0.0010084 | -0.00086511 | -0.00088008 | 0.0017345 | -0.022888 | 64.389 | -58.7219 | 64.2242 | -58.4747 | -58.8318 | -58.7906 | 0.004578 | 64.4485 | -58.5892 | -58.6395 | -58.5983 | -58.6945 | -58.4381 | -0.11444 | -0.027466 | -0.19226 | 0.13275 | -0.1831 | -0.2243 | -0.068664 | -0.10986 | 0.018311 | 0.032043 | -123.056 | 0.009155 | 0.16937 | -0.086975 | 0.15106 | -0.10529 | 0.24719 | 122.9462 | -0.009156 | -0.050354 | 123.111 | 123.0377 | 122.9965 | 123.056 | -123.1384 | -123.0057 | 122.8317 | -0.032043 | 58.5846 | 58.6121
88.1719 | 123.2254 | -58.548 | 64.3707 | -0.022431 | 0.0016899 | 0.059462 | 0.063918 | -0.00090783 | -0.00015811 | -0.00055961 | 0.041382 | -0.00039305 | -0.00021357 | 0.0015552 | 0.00041649 | -0.0013073 | -0.0016833 | 0.09613 | 64.3845 | -58.6533 | 64.3112 | -58.4244 | -58.7036 | -58.6853 | 0.12817 | 64.389 | -58.5846 | -58.5342 | -58.4976 | -58.6075 | -58.342 | -0.10528 | 0.013732 | -0.05951 | 0.1236 | -0.13733 | -0.15564 | -0.032044 | -0.050354 | -0.036621 | 0.01831 | -122.905 | 0.050354 | 0.20599 | -0.059509 | 0.24262 | -0.022888 | 0.22888 | 122.9645 | 0.086975 | 0.050354 | 123.0377 | 122.9736 | 122.9324 | 122.937 | -123.024 | -122.9553 | 122.8592 | 0.013733 | 58.6441 | 58.6761
89.1719 | 123.2071 | -58.5571 | 64.4119 | 0.34378 | 0.00040806 | 0.064803 | 0.062423 | -0.0011214 | 0.0013373 | 0.00072199 | 0.050537 | -0.0012477 | -0.00085457 | -0.0048536 | -0.0012925 | -0.0017347 | -0.0025379 | 0.004578 | 64.3753 | -58.6761 | 64.3066 | -58.3694 | -58.7585 | -58.6945 | 0.10071 | 64.3662 | -58.5846 | -58.5342 | -58.5068 | -58.5938 | -58.3282 | -0.11902 | -0.036621 | -0.10528 | 0.18768 | -0.13733 | -0.20142 | -0.018311 | -0.082398 | -0.027466 | -0.045776 | -122.9462 | 0.050354 | 0.22888 | -0.036621 | 0.25635 | -0.009155 | 0.3067 | 122.9828 | 0.07782 | 0.050354 | 123.0515 | 122.9507 | 122.9324 | 122.9233 | -123.0881 | -122.9965 | 122.8638 | 0.022888 | 58.5617 | 58.6578
90.1719 | 123.0743 | -58.6075 | 64.4211 | -0.037689 | 0.0023307 | 0.065443 | 0.063064 | -0.00048063 | 0.00026909 | -0.00077341 | -0.01355 | 0.0017431 | 2.8e-08 | 0.003905 | -1.0706e-05 | -0.00088008 | 0.0038709 | -0.027466 | 64.3799 | -58.699 | 64.2105 | -58.493 | -58.8181 | -58.7997 | -0.009155 | 64.4485 | -58.6121 | -58.6533 | -58.3923 | -58.7036 | -58.4747 | -0.091553 | -0.041199 | -0.21057 | 0.11444 | -0.19226 | -0.21057 | -0.10071 | -0.11902 | -0.004578 | 0.027465 | -123.0743 | 0.21515 | 0.13275 | -0.09613 | 0.13733 | -0.091552 | 0.20599 | 122.9095 | 0.21973 | -0.041198 | 123.0789 | 123.0606 | 122.9874 | 123.056 | -123.1201 | -123.0331 | 122.818 | -0.045776 | 58.58 | 58.5983
91.1719 | 123.2025 | -58.5892 | 64.3662 | -0.052948 | -0.00023294 | 0.064803 | 0.065627 | 0.0027238 | -0.00037171 | -0.0022686 | 0.044434 | 3.4148e-05 | 0.003418 | -0.0014356 | 0.00020289 | -0.0010937 | 0.00088014 | -0.091553 | 64.3158 | -58.7265 | 64.2471 | -58.4518 | -58.8272 | -58.7631 | -0.050354 | 64.3753 | -58.6121 | -58.5983 | -58.5617 | -58.4427 | -58.2779 | -0.13733 | -0.050354 | -0.11902 | 0.13733 | -0.17395 | -0.23804 | -0.036622 | -0.10071 | -0.022889 | 0.009155 | -122.9645 | 0.027465 | 0.31128 | 0.14648 | 0.33417 | 0.16937 | 0.27466 | 122.9736 | 0.050354 | 0.013733 | 123.0423 | 122.9874 | 122.905 | 122.9645 | -123.0927 | -122.9782 | 122.8363 | -0.009156 | 58.4976 | 58.5388
92.1719 | 123.111 | -58.6075 | 64.4073 | -0.045319 | -0.0013009 | 0.063948 | 0.063918 | 0.0016556 | -0.0022943 | -0.00055961 | -0.010498 | 0.00046135 | 0.0012818 | -0.0035718 | -0.00086511 | -0.0021619 | -0.00040166 | -0.041199 | 64.389 | -58.7173 | 64.2105 | -58.4839 | -58.8455 | -58.7906 | -0.004578 | 64.4211 | -58.6075 | -58.5938 | -58.7448 | -58.8501 | -58.4518 | -0.10986 | -0.018311 | -0.19684 | 0.1236 | -0.1831 | -0.23804 | -0.073242 | -0.12817 | 0 | 0.013733 | -123.0011 | -0.13733 | 0.15564 | -0.24262 | 0.15564 | -0.24262 | 0.23346 | 122.9279 | -0.13733 | 0.013733 | 123.1064 | 123.0286 | 122.9965 | 123.0286 | -123.1247 | -123.0148 | 122.818 | 0.013733 | 58.5663 | 58.6029
93.1719 | 123.1567 | -58.5892 | 64.4028 | -0.022431 | 0.00083526 | 0.063734 | 0.065627 | -5.343e-05 | 5.5488e-05 | 0.00050839 | -0.016602 | 3.4148e-05 | 0.001068 | 0.0015552 | -0.00086511 | -0.0017347 | 0.0010937 | -0.032043 | 64.3753 | -58.7311 | 64.2151 | -58.493 | -58.8547 | -58.8181 | -0.018311 | 64.444 | -58.6304 | -58.6212 | -58.5846 | -58.6945 | -58.4244 | -0.14191 | -0.027466 | -0.18768 | 0.09613 | -0.22888 | -0.2655 | -0.086975 | -0.1236 | -0.041199 | 0.041199 | -123.024 | 0.004577 | 0.16479 | -0.10529 | 0.20599 | -0.064087 | 0.23804 | 122.9462 | 0.045776 | 0.009155 | 123.1064 | 123.0743 | 122.9645 | 123.0331 | -123.1338 | -123.0331 | 122.8043 | -0.032044 | 58.5571 | 58.5709
94.1719 | 123.1155 | -58.6121 | 64.4073 | 0.00045798 | 0.00083526 | 0.063734 | 0.06285 | 0.00016017 | -0.0022943 | 8.1188e-05 | -0.010498 | 0.0013159 | 0.0038452 | 0.0019824 | -0.00043791 | -0.0036573 | 0.0017345 | -0.036621 | 64.3936 | -58.7219 | 64.2014 | -58.4839 | -58.8364 | -58.7952 | -0.018311 | 64.4211 | -58.6258 | -58.5663 | -58.6945 | -58.9233 | -58.4976 | -0.10986 | -0.013733 | -0.20599 | 0.12817 | -0.18311 | -0.2243 | -0.073242 | -0.11444 | -0.013732 | 0.013733 | -122.9736 | -0.082397 | 0.11444 | -0.31128 | 0.12817 | -0.29755 | 0.23804 | 122.9233 | -0.068665 | 0.059509 | 123.1155 | 123.0469 | 123.0057 | 123.0331 | -123.1293 | -123.0331 | 122.8134 | 0.045777 | 58.5754 | 58.5938
95.1719 | 123.143 | -58.5709 | 64.4211 | 0.053863 | 0.0012625 | 0.063734 | 0.063705 | 0.00037377 | -0.00037171 | -0.00013241 | 0.035278 | 0.0023839 | 0.0036316 | -0.0014356 | -0.0012925 | -0.0021619 | -0.0025379 | 0.022888 | 64.3478 | -58.6899 | 64.2929 | -58.4061 | -58.754 | -58.7265 | 0.059509 | 64.4073 | -58.5754 | -58.5983 | -58.5709 | -58.6716 | -58.4152 | -0.11902 | -0.073243 | -0.12817 | 0.16479 | -0.15564 | -0.18311 | -0.036621 | -0.064087 | -0.004577 | -0.013733 | -123.0194 | 0 | 0.15564 | -0.10071 | 0.16022 | -0.096131 | 0.28381 | 122.9828 | 0.004577 | -0.022889 | 123.0377 | 122.9828 | 122.9187 | 122.9782 | -123.111 | -122.9965 | 122.8638 | -0.027466 | 58.5938 | 58.6304
96.1719 | 123.0972 | -58.6121 | 64.3982 | -0.091095 | -1.9142e-05 | 0.063948 | 0.065627 | 0.00486 | -0.0031489 | 0.0043536 | -0.028809 | 0.0034521 | -0.0014954 | 0.0054004 | 0.0010575 | 0.0010425 | -0.0025379 | -0.10529 | 64.3341 | -58.7631 | 64.0686 | -58.2825 | -58.7082 | -58.8547 | -0.11444 | 64.389 | -58.6487 | -58.6441 | -58.667 | -58.8043 | -58.4793 | -0.15106 | -0.064087 | -0.32959 | 0.32959 | -0.24261 | -0.09613 | -0.091552 | 0.054932 | -0.036621 | -0.009155 | -123.0423 | -0.054931 | 0.13275 | -0.19226 | 0.16937 | -0.15564 | 0.48065 | 122.8317 | -0.01831 | 0.004578 | 123.0972 | 123.0377 | 122.9462 | 123.0011 | -123.1613 | -123.0469 | 122.6807 | -0.032043 | 58.5068 | 58.4976
97.1719 | 123.1567 | -58.5892 | 64.4073 | -0.068207 | 0.00062166 | 0.064375 | 0.065841 | 0.00058737 | -0.0016535 | -0.00055961 | -0.053223 | 0.0019567 | 0.00042723 | -0.00015378 | -0.00065151 | 0.0010425 | -0.0012561 | -0.013733 | 64.3936 | -58.7173 | 64.2471 | -58.461 | -58.8043 | -58.786 | 0.032043 | 64.4211 | -58.6029 | -58.5846 | -58.58 | -58.699 | -58.3832 | -0.12817 | -0.013733 | -0.16022 | 0.12817 | -0.19684 | -0.21515 | -0.068665 | -0.086975 | -0.013733 | 0.013733 | -122.9919 | 0.009155 | 0.20599 | -0.10986 | 0.21973 | -0.096131 | 0.25635 | 122.9645 | 0.022888 | 0.01831 | 123.111 | 123.024 | 122.9828 | 123.0103 | -123.1247 | -123.0103 | 122.8363 | 0.004577 | 58.5754 | 58.6212
98.1719 | 123.1476 | -58.6029 | 64.4028 | -0.03006 | -0.00044654 | 0.062453 | 0.061996 | 0.001442 | -0.0010125 | 0.001363 | 0.001709 | 0.0017431 | 0.0019226 | -0.0016492 | -1.0706e-05 | -0.00023928 | -0.00018806 | -0.041199 | 64.4073 | -58.7173 | 64.2059 | -58.5022 | -58.8318 | -58.8135 | -0.018311 | 64.4257 | -58.6395 | -58.6349 | -58.6212 | -58.7082 | -58.4335 | -0.11444 | 0.004578 | -0.19684 | 0.10071 | -0.21057 | -0.22888 | -0.096131 | -0.11444 | -0.036621 | 0.022888 | -123.0377 | -0.018311 | 0.16937 | -0.10529 | 0.20599 | -0.068665 | 0.21515 | 122.9233 | 0.01831 | 0.004577 | 123.1247 | 123.0652 | 123.0103 | 123.0286 | -123.1201 | -123.0423 | 122.8088 | -0.032044 | 58.5617 | 58.5846
99.1719 | 123.1613 | -58.5892 | 64.3936 | -0.022431 | 0.0016899 | 0.064162 | 0.0652 | -0.00048063 | 5.5488e-05 | 0.0017902 | -0.022705 | 0.0015295 | 0.00064083 | 0.0062548 | 0.00041649 | -0.00045288 | -0.0027515 | -0.018311 | 64.3936 | -58.7219 | 64.238 | -58.4702 | -58.8135 | -58.7769 | 0.027466 | 64.4257 | -58.5983 | -58.6166 | -58.5709 | -58.6945 | -58.4061 | -0.13275 | 0 | -0.15564 | 0.11902 | -0.18768 | -0.22431 | -0.054931 | -0.091553 | -0.009156 | 0.032043 | -123.0103 | 0.01831 | 0.1831 | -0.10529 | 0.19226 | -0.09613 | 0.25177 | 122.9599 | 0.027466 | -0.01831 | 123.1155 | 123.024 | 122.9828 | 123.0148 | -123.1155 | -122.9919 | 122.8271 | -0.027466 | 58.5709 | 58.6166
100.1719 | 123.1384 | -58.5709 | 64.4257 | -0.037689 | -0.00044654 | 0.06288 | 0.06285 | -0.0011214 | 0.0021917 | -0.00034601 | -0.01355 | 0.00024775 | 0.0025634 | 0.0026232 | -0.00086511 | -0.0015211 | -0.00040166 | -0.022888 | 64.3845 | -58.7036 | 64.2242 | -58.4702 | -58.8135 | -58.7952 | 0.022888 | 64.4257 | -58.6075 | -58.6121 | -58.5709 | -58.6899 | -58.4061 | -0.13275 | -0.041199 | -0.20142 | 0.10071 | -0.2243 | -0.24262 | -0.091553 | -0.10986 | -0.036621 | 0 | -123.0377 | 0 | 0.16479 | -0.11902 | 0.20142 | -0.082397 | 0.23346 | 122.9279 | 0.036621 | -0.004578 | 123.0881 | 123.0331 | 122.9553 | 122.9965 | -123.1293 | -123.0331 | 122.7951 | -0.041199 | 58.548 | 58.5938
101.1719 | 123.1888 | -58.5938 | 64.3707 | -0.091095 | 0.00062166 | 0.065016 | 0.062209 | 0.00058737 | 0.00069649 | -0.0031232 | 0.062744 | 0.00046135 | -0.0010682 | -0.001222 | 0.0021255 | -0.0010937 | 0.00088014 | -0.10071 | 64.2975 | -58.7082 | 64.2334 | -58.4564 | -58.8364 | -58.7585 | -0.050354 | 64.3478 | -58.6121 | -58.5938 | -58.58 | -58.6716 | -58.3832 | -0.11444 | -0.073243 | -0.13733 | 0.13733 | -0.16479 | -0.24262 | -0.050354 | -0.12817 | -0.018311 | -0.022889 | -122.9645 | 0.013733 | 0.21057 | -0.07782 | 0.22888 | -0.059509 | 0.25177 | 122.9416 | 0.032044 | 0.018311 | 123.0057 | 122.9599 | 122.8912 | 122.9416 | -123.0789 | -122.9828 | 122.8271 | 0 | 58.493 | 58.5434
102.1719 | 123.0469 | -58.5892 | 64.444 | -0.068207 | 0.0012625 | 0.067152 | 0.063064 | -0.00048063 | -0.0040033 | 0.00029479 | 0.023071 | 0.00067495 | 0.00042723 | 5.9824e-05 | -0.00086511 | -0.00045288 | -0.0012561 | -0.022888 | 64.357 | -58.6945 | 64.2105 | -58.4839 | -58.8318 | -58.8043 | 0.004578 | 64.4257 | -58.6121 | -58.6487 | -58.5983 | -58.699 | -58.4381 | -0.10529 | -0.086975 | -0.23346 | 0.10528 | -0.21515 | -0.24262 | -0.10986 | -0.13733 | -0.022889 | -0.018311 | -123.0927 | -0.009156 | 0.15106 | -0.10986 | 0.17395 | -0.086975 | 0.21057 | 122.905 | 0.013733 | -0.036621 | 123.0515 | 123.0377 | 122.9462 | 123.0148 | -123.1384 | -123.056 | 122.7997 | -0.05951 | 58.5663 | 58.5938
103.1719 | 123.1018 | -58.6029 | 64.4119 | -0.014801 | 0.00019446 | 0.062666 | 0.063918 | 0.0018692 | -0.00058531 | -0.00013241 | 0.001709 | 0.00024775 | 0.0023498 | -0.0010084 | -0.0023605 | -0.00066648 | 0.0021619 | -0.027466 | 64.3936 | -58.7311 | 64.1968 | -58.4976 | -58.8455 | -58.8135 | -0.022888 | 64.4257 | -58.5892 | -58.6304 | -58.5938 | -58.7311 | -58.4335 | -0.12817 | -0.01831 | -0.21515 | 0.10529 | -0.21057 | -0.24262 | -0.082398 | -0.11444 | 0.013733 | 0.013733 | -123.0423 | 0.009155 | 0.16937 | -0.12817 | 0.15564 | -0.14191 | 0.23346 | 122.9279 | -0.004578 | -0.041199 | 123.1247 | 123.0148 | 122.9965 | 123.0286 | -123.143 | -123.0011 | 122.7997 | -0.027466 | 58.5754 | 58.58
104.1719 | 123.1567 | -58.5754 | 64.4073 | -0.075836 | -0.0017281 | 0.064803 | 0.061782 | 0.0029374 | 0.00069649 | 8.1188e-05 | -0.022705 | -0.0010339 | 0.002777 | -0.00036738 | -0.00065151 | -0.00045288 | 0.0019483 | -0.041199 | 64.3936 | -58.7173 | 64.2334 | -58.4839 | -58.8181 | -58.7906 | -0.009155 | 64.4394 | -58.6304 | -58.5983 | -58.5709 | -58.6945 | -58.4152 | -0.14191 | -0.013733 | -0.17395 | 0.091552 | -0.21515 | -0.24261 | -0.073242 | -0.10071 | -0.054932 | 0.032043 | -123.0057 | 0.004577 | 0.16022 | -0.11902 | 0.21515 | -0.064087 | 0.23346 | 122.9507 | 0.059509 | 0.032043 | 123.111 | 123.0698 | 122.9691 | 123.0148 | -123.1247 | -123.0377 | 122.8088 | -0.022889 | 58.5342 | 58.5663
105.1719 | 123.1613 | -58.5617 | 64.4257 | 0.008087 | 0.00019446 | 0.063307 | 0.06285 | -0.0021896 | 0.00048269 | -0.0018414 | -0.025757 | 0.0015295 | 0.0025634 | -0.00229 | -0.0015061 | 0.0012561 | 0.0010937 | -0.022888 | 64.3982 | -58.7036 | 64.2288 | -58.4885 | -58.8135 | -58.7814 | 0 | 64.4073 | -58.5938 | -58.5892 | -58.5754 | -58.6899 | -58.4015 | -0.14191 | -0.027466 | -0.19684 | 0.073243 | -0.21973 | -0.25177 | -0.07782 | -0.10986 | -0.032043 | -0.01831 | -123.0148 | -0.013732 | 0.16022 | -0.12817 | 0.19226 | -0.09613 | 0.21515 | 122.9324 | 0.018311 | 0.004578 | 123.1018 | 123.0011 | 122.9599 | 122.9691 | -123.1293 | -123.0194 | 122.7905 | -0.027465 | 58.5388 | 58.5617
106.1719 | 123.2117 | -58.5892 | 64.357 | -0.13687 | 0.00083526 | 0.06288 | 0.062423 | -0.001976 | -0.00037171 | -0.002696 | 0.035278 | 0.0013159 | 0.0014954 | -0.0025036 | 0.0010575 | -0.00088008 | -0.0016833 | -0.068665 | 64.3158 | -58.6899 | 64.2609 | -58.3969 | -58.8043 | -58.754 | -0.004578 | 64.325 | -58.6075 | -58.58 | -58.5571 | -58.6578 | -58.3603 | -0.10071 | -0.041199 | -0.096131 | 0.19226 | -0.1648 | -0.21515 | -0.064087 | -0.11444 | -0.018311 | -0.032044 | -122.937 | 0.032043 | 0.22888 | -0.068665 | 0.24719 | -0.050354 | 0.29297 | 122.9507 | 0.050354 | 0.027466 | 123.0057 | 122.9324 | 122.905 | 122.9141 | -123.0469 | -122.9645 | 122.85 | 0.009155 | 58.5205 | 58.5846
107.1719 | 123.1796 | -58.5846 | 64.4348 | -0.03006 | 0.00040806 | 0.064162 | 0.063918 | 0.0012284 | -0.0014399 | 0.00093559 | -0.016602 | -0.00039305 | 0.00021363 | 0.0045458 | -0.0017197 | -0.00023928 | -0.00082886 | -0.022888 | 64.3982 | -58.7128 | 64.2105 | -58.5022 | -58.8181 | -58.8043 | 0 | 64.444 | -58.6075 | -58.5983 | -58.5754 | -58.699 | -58.3878 | -0.12817 | -0.036621 | -0.2243 | 0.082398 | -0.21973 | -0.23346 | -0.091552 | -0.10528 | -0.022888 | 0.009156 | -123.0331 | 0.009156 | 0.19684 | -0.11444 | 0.21973 | -0.091553 | 0.21057 | 122.9233 | 0.032044 | 0.009155 | 123.111 | 123.0515 | 122.9828 | 123.0286 | -123.1476 | -123.0423 | 122.7951 | -0.013733 | 58.5617 | 58.5846
108.1719 | 123.143 | -58.5846 | 64.4119 | -0.083466 | 0.00083526 | 0.064375 | 0.063064 | -0.0028304 | -0.00015811 | -0.0012006 | -0.0043946 | 3.4148e-05 | 0.001068 | 0.00091422 | -0.0012925 | -2.5678e-05 | 0.0015209 | -0.018311 | 64.3662 | -58.7311 | 64.2151 | -58.5068 | -58.8181 | -58.7952 | 0 | 64.4165 | -58.6121 | -58.6121 | -58.5754 | -58.6807 | -58.3786 | -0.14648 | -0.045776 | -0.19684 | 0.07782 | -0.21057 | -0.23346 | -0.064087 | -0.086975 | -0.027466 | 0.004578 | -123.024 | 0.009156 | 0.20599 | -0.09613 | 0.23346 | -0.068664 | 0.2243 | 122.9462 | 0.036622 | 0 | 123.0972 | 123.0286 | 122.9507 | 123.0011 | -123.143 | -123.024 | 122.7997 | -0.027466 | 58.5663 | 58.5846
109.1719 | 123.1247 | -58.5938 | 64.4257 | -0.03006 | 0.00062166 | 0.063948 | 0.063064 | 0.0027238 | -0.00058531 | -0.0018414 | 0.029175 | 0.0025975 | 0.0021362 | -0.0078442 | 0.0025529 | -0.0028027 | -0.0036059 | 0.091553 | 64.4348 | -58.6853 | 64.1785 | -58.493 | -58.8409 | -58.7997 | -0.013733 | 64.4257 | -58.6075 | -58.6395 | -58.6075 | -58.7128 | -58.4244 | -0.091553 | 0.009155 | -0.24719 | 0.10071 | -0.20599 | -0.24719 | -0.11444 | -0.15564 | -0.013733 | 0 | -123.0652 | -0.013733 | 0.16937 | -0.11902 | 0.18311 | -0.10529 | 0.19226 | 122.8638 | 0 | -0.032043 | 123.1201 | 123.0331 | 123.0286 | 123.0194 | -123.111 | -123.0331 | 122.7722 | -0.045776 | 58.6853 | 58.58
110.1719 | 123.143 | -58.5663 | 64.4073 | -0.0071715 | -0.00023294 | 0.064803 | 0.063918 | -0.0015488 | 0.00048269 | -0.00034601 | 0.001709 | -0.00017945 | 0.001709 | -0.00015378 | -0.00022431 | -0.00045288 | -0.0010425 | -0.036621 | 64.4073 | -58.7082 | 64.2151 | -58.5159 | -58.8409 | -58.7906 | -0.009155 | 64.4302 | -58.6029 | -58.6258 | -58.58 | -58.6807 | -58.3969 | -0.14191 | 0 | -0.19226 | 0.050354 | -0.2243 | -0.27466 | -0.082397 | -0.13275 | -0.036621 | 0.022888 | -123.0331 | -0.013733 | 0.16937 | -0.11444 | 0.20599 | -0.07782 | 0.19226 | 122.9233 | 0.022888 | -0.022888 | 123.1155 | 123.0331 | 122.9736 | 122.9965 | -123.1155 | -123.0103 | 122.7814 | -0.059509 | 58.5297 | 58.5571
111.1719 | 123.2666 | -58.5846 | 64.3662 | -0.022431 | 0.00083526 | 0.064803 | 0.063705 | -0.0013352 | 5.5488e-05 | 0.00029479 | -0.034912 | 0.0034521 | -0.00042717 | 0.00027342 | -0.0010787 | -0.00066648 | 0.00023934 | -0.018311 | 64.3707 | -58.7219 | 64.2517 | -58.4427 | -58.8181 | -58.7952 | 0.027466 | 64.4028 | -58.6029 | -58.5938 | -58.5709 | -58.6807 | -58.3786 | -0.13733 | 0.004578 | -0.11444 | 0.14191 | -0.21057 | -0.23346 | -0.073242 | -0.09613 | -0.01831 | 0.036621 | -122.9599 | 0.013733 | 0.20599 | -0.09613 | 0.2243 | -0.07782 | 0.27924 | 122.9736 | 0.032043 | 0.009155 | 123.0927 | 123.0057 | 122.9553 | 122.9874 | -123.0881 | -122.9691 | 122.8363 | -0.009155 | 58.5663 | 58.6121
112.1719 | 123.0835 | -58.5846 | 64.389 | -0.045319 | 0.0010489 | 0.064375 | 0.063705 | -0.00026703 | 0.00026909 | -0.002055 | -0.0043946 | 0.0011023 | 0.0023498 | 5.9824e-05 | -0.00065151 | -0.00066648 | -0.0057423 | -0.009155 | 64.3799 | -58.7173 | 64.238 | -58.4381 | -58.8135 | -58.7814 | 0.036621 | 64.3936 | -58.5938 | -58.5892 | -58.5663 | -58.6853 | -58.2733 | -0.13275 | -0.009155 | -0.15106 | 0.14648 | -0.19684 | -0.22888 | -0.064087 | -0.096131 | -0.009155 | 0.004578 | -122.9782 | 0.018311 | 0.31128 | -0.10071 | 0.32044 | -0.091553 | 0.27924 | 122.9553 | 0.027466 | 0.004578 | 123.0972 | 122.9874 | 122.9645 | 122.9782 | -123.1064 | -122.9828 | 122.8226 | -0.004577 | 58.5754 | 58.6212
113.1719 | 123.2346 | -58.6075 | 64.3799 | -0.052948 | 0.0021171 | 0.063094 | 0.063491 | 0.00080117 | -0.00058531 | -0.00013241 | -0.010498 | -0.00017945 | 0.0019226 | -0.00015378 | -0.0017197 | -0.00088008 | 0.0019483 | 0 | 64.3707 | -58.7128 | 64.238 | -58.4427 | -58.8364 | -58.786 | 0.022888 | 64.4028 | -58.6349 | -58.58 | -58.58 | -58.6945 | -58.4106 | -0.10529 | -0.009155 | -0.14191 | 0.1648 | -0.17853 | -0.22888 | -0.073242 | -0.1236 | -0.027466 | 0.022888 | -122.9599 | 0.027466 | 0.19684 | -0.086975 | 0.2243 | -0.059509 | 0.27008 | 122.9507 | 0.054932 | 0.054932 | 123.0835 | 123.0377 | 122.9782 | 123.0103 | -123.0927 | -123.0148 | 122.8455 | 0.027466 | 58.6075 | 58.6304
114.1719 | 123.2574 | -58.5892 | 64.3616 | -0.060578 | 0.00062166 | 0.065443 | 0.063064 | -0.0011214 | 5.5488e-05 | -0.002696 | -0.019653 | 3.4148e-05 | 2.8e-08 | 0.0019824 | -0.0010787 | 0.00018792 | 0.0021619 | -0.013733 | 64.3662 | -58.7082 | 64.238 | -58.4473 | -58.8226 | -58.7814 | 0.036621 | 64.4119 | -58.6121 | -58.5754 | -58.5663 | -58.7082 | -58.3923 | -0.11902 | 0.004578 | -0.1236 | 0.14191 | -0.19226 | -0.23346 | -0.073242 | -0.11444 | -0.022889 | 0.050354 | -122.937 | 0.022888 | 0.19684 | -0.11902 | 0.21973 | -0.09613 | 0.26093 | 122.9462 | 0.045777 | 0.036622 | 123.0743 | 123.024 | 122.9553 | 123.0011 | -123.0698 | -122.9736 | 122.8271 | 0.013733 | 58.5754 | 58.6258
115.1719 | 123.1522 | -58.5754 | 64.3845 | -0.075836 | 0.0019035 | 0.063307 | 0.063705 | -0.0034714 | 0.00069649 | 0.00029479 | -0.0074462 | 0.0011023 | 0.00021363 | -0.0061352 | -0.00086511 | -0.00066648 | -0.0010425 | -0.022888 | 64.3662 | -58.7036 | 64.2288 | -58.461 | -58.8181 | -58.7906 | 0.018311 | 64.3936 | -58.6258 | -58.5938 | -58.5709 | -58.6899 | -58.3969 | -0.12817 | -0.01831 | -0.15564 | 0.11444 | -0.21515 | -0.24261 | -0.086975 | -0.11444 | -0.050354 | 0.009156 | -122.9782 | 0.004577 | 0.17853 | -0.11444 | 0.22888 | -0.064087 | 0.24261 | 122.9324 | 0.054931 | 0.032043 | 123.0698 | 123.0194 | 122.9416 | 122.9691 | -123.0881 | -123.0103 | 122.8043 | -0.018311 | 58.5526 | 58.5938
116.1719 | 123.1705 | -58.5709 | 64.4028 | 0.015716 | -0.0025827 | 0.063521 | 0.063277 | 0.0016556 | -0.00037171 | -0.0012006 | 0.013916 | -0.00039305 | 0.00042723 | -0.0014356 | 0.00041649 | -2.5678e-05 | 0.0021619 | -0.050354 | 64.3616 | -58.7219 | 64.2105 | -58.4885 | -58.8226 | -58.8043 | -0.041199 | 64.4165 | -58.6075 | -58.6121 | -58.5663 | -58.6853 | -58.4061 | -0.15106 | -0.041199 | -0.19226 | 0.082398 | -0.23346 | -0.25177 | -0.082397 | -0.10071 | -0.036621 | 0.013733 | -123.0148 | 0.004578 | 0.16479 | -0.11444 | 0.20142 | -0.07782 | 0.23346 | 122.9324 | 0.041199 | -0.004578 | 123.0835 | 123.024 | 122.9324 | 122.9874 | -123.1247 | -123.0103 | 122.7814 | -0.041199 | 58.5205 | 58.5297
117.1719 | 123.1476 | -58.5983 | 64.3936 | -0.037689 | 0.00019446 | 0.066298 | 0.062423 | -0.00026703 | -0.0018671 | -0.0022686 | -0.0043946 | 0.00067495 | -0.00021357 | 0.0041186 | -1.0706e-05 | -2.5678e-05 | -0.00061526 | -0.018311 | 64.3799 | -58.7173 | 64.2426 | -58.4427 | -58.8089 | -58.7906 | 0.032043 | 64.4073 | -58.6121 | -58.5938 | -58.5617 | -58.7036 | -58.4015 | -0.11902 | -0.013733 | -0.15106 | 0.15564 | -0.19226 | -0.21057 | -0.073242 | -0.091553 | -0.013733 | 0.013733 | -122.9874 | 0.036621 | 0.19684 | -0.10528 | 0.21057 | -0.091552 | 0.27466 | 122.9599 | 0.050354 | 0.018311 | 123.0972 | 123.0194 | 122.9782 | 123.0057 | -123.111 | -123.0057 | 122.8409 | 0.004578 | 58.58 | 58.6304
118.1719 | 123.1018 | -58.548 | 64.3982 | -0.22842 | 0.0025443 | 0.063734 | 0.065627 | -0.00048063 | 0.00069649 | -0.00077341 | -0.010498 | 0.0025975 | 0.001709 | 0.00027342 | -0.00086511 | -2.5678e-05 | 0.00023934 | -0.12817 | 64.3204 | -58.7494 | 64.2288 | -58.4381 | -58.8135 | -58.7997 | 0.004578 | 64.3936 | -58.6349 | -58.6121 | -58.5938 | -58.7173 | -58.4152 | -0.20142 | -0.077819 | -0.16937 | 0.10986 | -0.25177 | -0.2655 | -0.050354 | -0.064087 | -0.086975 | -0.004577 | -123.0103 | -0.045776 | 0.13275 | -0.16937 | 0.21973 | -0.082397 | 0.31128 | 122.9782 | 0.041199 | 0.022888 | 123.0698 | 123.0286 | 122.8683 | 122.9416 | -123.1476 | -123.0331 | 122.7768 | -0.064087 | 58.4198 | 58.5526
119.1719 | 123.1018 | -58.5983 | 64.3845 | -0.098725 | 0.00083526 | 0.064375 | 0.064559 | 0.0022964 | -0.00058531 | 8.1188e-05 | -0.019653 | 0.0032385 | 0.0019226 | 0.0030506 | -0.00022431 | -2.5678e-05 | 0.00045294 | -0.050354 | 64.3433 | -58.7265 | 64.1876 | -58.4885 | -58.8638 | -58.8364 | -0.073242 | 64.389 | -58.6075 | -58.6533 | -58.6441 | -58.7769 | -58.4427 | -0.12817 | -0.041198 | -0.19684 | 0.10986 | -0.23804 | -0.2655 | -0.10986 | -0.13733 | -0.009155 | 0.004578 | -123.0377 | -0.045776 | 0.15564 | -0.17853 | 0.1648 | -0.16937 | 0.23804 | 122.9141 | -0.036621 | -0.045776 | 123.0698 | 122.9965 | 122.9416 | 122.9874 | -123.111 | -122.9919 | 122.786 | -0.054931 | 58.548 | 58.5251
120.1719 | 123.1155 | -58.5846 | 64.4028 | -0.083466 | 0.0014761 | 0.065016 | 0.063277 | -0.0011214 | 0.0019781 | -0.00077341 | -0.0074462 | 0.0011023 | 0.0038452 | -0.0010084 | -1.0706e-05 | 0.00018792 | 0.0017345 | -0.022888 | 64.3616 | -58.7173 | 64.2197 | -58.4335 | -58.8364 | -58.8089 | -0.004578 | 64.3845 | -58.6304 | -58.5983 | -58.58 | -58.7036 | -58.3878 | -0.13275 | -0.041199 | -0.1831 | 0.15106 | -0.2243 | -0.25177 | -0.091553 | -0.11902 | -0.045776 | -0.018311 | -123.0011 | 0.004578 | 0.19684 | -0.11902 | 0.24261 | -0.073242 | 0.28381 | 122.937 | 0.050354 | 0.032043 | 123.0789 | 123.0148 | 122.9462 | 122.9691 | -123.1201 | -123.0331 | 122.8043 | -0.013733 | 58.5617 | 58.58
121.1719 | 123.1293 | -58.6075 | 64.4119 | -0.014801 | -0.00023294 | 0.064803 | 0.065841 | 0.0018692 | 0.00091009 | 0.0015766 | -0.01355 | 0.00046135 | 0.00085443 | 0.0032642 | -0.0012925 | -0.0023755 | 2.554e-05 | -0.054932 | 64.3524 | -58.7357 | 64.183 | -58.5022 | -58.8638 | -58.8364 | -0.068665 | 64.389 | -58.6258 | -58.6258 | -58.6349 | -58.7494 | -58.429 | -0.12817 | -0.059509 | -0.22888 | 0.10529 | -0.22888 | -0.25635 | -0.10071 | -0.12817 | -0.01831 | -0.022888 | -123.0377 | -0.027466 | 0.17853 | -0.14191 | 0.19684 | -0.1236 | 0.23346 | 122.9187 | -0.009156 | 0 | 123.0881 | 123.0148 | 122.9599 | 122.9965 | -123.1476 | -123.0377 | 122.7905 | -0.01831 | 58.5526 | 58.5388
122.1719 | 123.1293 | -58.5754 | 64.3936 | -0.03006 | 0.00062166 | 0.063307 | 0.064559 | -0.00090783 | 0.0034735 | 0.0020038 | -0.01355 | -0.0012477 | 0.00021363 | -0.003999 | -0.00065151 | -0.0015211 | 0.00088014 | -0.059509 | 64.3662 | -58.7265 | 64.1922 | -58.4839 | -58.873 | -58.8181 | -0.07782 | 64.389 | -58.6258 | -58.6395 | -58.6349 | -58.7402 | -58.4244 | -0.15106 | -0.027466 | -0.20142 | 0.091552 | -0.24261 | -0.29755 | -0.091553 | -0.14648 | -0.050354 | -0.004578 | -123.0331 | -0.05951 | 0.15106 | -0.16479 | 0.20142 | -0.11444 | 0.24261 | 122.9187 | -0.009156 | -0.013733 | 123.0927 | 123.0148 | 122.9416 | 122.9645 | -123.1201 | -123.0194 | 122.7676 | -0.064087 | 58.5159 | 58.4976
123.1719 | 123.1384 | -58.5892 | 64.3662 | -0.037689 | -0.00087374 | 0.065443 | 0.063277 | -0.00048063 | -0.00037171 | -0.00055961 | 0.044434 | 0.0011023 | -0.00042717 | 0.0013416 | -0.0023605 | -0.0010937 | 0.0032299 | -0.018311 | 64.3936 | -58.7082 | 64.238 | -58.4656 | -58.8089 | -58.7997 | -0.004578 | 64.3936 | -58.5846 | -58.6121 | -58.5892 | -58.7082 | -58.3923 | -0.11902 | 0.027466 | -0.12817 | 0.1236 | -0.21057 | -0.21973 | -0.091553 | -0.10071 | 0.004577 | 0.027466 | -122.9782 | 0 | 0.19684 | -0.11902 | 0.19226 | -0.1236 | 0.24262 | 122.9462 | -0.004577 | -0.027466 | 123.1018 | 122.9782 | 122.9828 | 122.9828 | -123.0743 | -122.9507 | 122.8271 | -0.022889 | 58.5709 | 58.5846
124.1719 | 123.143 | -58.5846 | 64.4119 | -0.03006 | -0.00023294 | 0.063948 | 0.064559 | 0.00037377 | -0.0018671 | -0.00055961 | 0.013916 | -0.00039305 | -0.0010682 | 0.0054004 | -0.00022431 | -0.0013073 | -0.0010425 | -0.041199 | 64.4028 | -58.6853 | 64.2197 | -58.4656 | -58.7997 | -58.7906 | 0.004578 | 64.4302 | -58.6166 | -58.5983 | -58.5526 | -58.6853 | -58.3878 | -0.10071 | -0.009155 | -0.19226 | 0.11902 | -0.20599 | -0.21515 | -0.10529 | -0.11444 | -0.032043 | 0.018311 | -123.0103 | 0.032044 | 0.19684 | -0.10071 | 0.22888 | -0.068665 | 0.21973 | 122.905 | 0.064087 | 0.01831 | 123.0881 | 123.0469 | 122.9874 | 123.0148 | -123.0972 | -123.0286 | 122.8043 | -0.013733 | 58.5434 | 58.5892
125.1719 | 123.1522 | -58.5983 | 64.4073 | -0.037689 | -0.00023294 | 0.065657 | 0.064559 | 0.0022964 | 5.5488e-05 | -0.00098701 | 0.0078126 | 0.00024775 | 0.0023498 | 0.00027342 | -0.0025741 | -2.5678e-05 | 0.0032299 | -0.041199 | 64.3387 | -58.7082 | 64.1968 | -58.4747 | -58.8455 | -58.8181 | -0.027466 | 64.3936 | -58.6212 | -58.6487 | -58.6212 | -58.7448 | -58.429 | -0.10986 | -0.068665 | -0.21057 | 0.1236 | -0.21973 | -0.24719 | -0.10986 | -0.13733 | -0.022888 | -0.013733 | -123.056 | -0.022888 | 0.16937 | -0.14648 | 0.19226 | -0.1236 | 0.23346 | 122.905 | 0 | -0.027466 | 123.0469 | 123.0148 | 122.937 | 122.9919 | -123.1155 | -123.0286 | 122.7951 | -0.050354 | 58.5571 | 58.5709
126.1719 | 123.1201 | -58.5938 | 64.3845 | -0.0071715 | 0.00040806 | 0.064589 | 0.063918 | 0.0012284 | -0.0029351 | 0.001363 | 0.001709 | 0.0017431 | 0.0014954 | -0.00015378 | -0.00086511 | -0.00088008 | 0.0023755 | -0.041199 | 64.3524 | -58.7219 | 64.2151 | -58.4702 | -58.8455 | -58.7997 | -0.032043 | 64.4028 | -58.6166 | -58.6212 | -58.6258 | -58.7311 | -58.4244 | -0.12817 | -0.032043 | -0.16937 | 0.1236 | -0.20599 | -0.25177 | -0.07782 | -0.1236 | -0.022888 | 0.018311 | -123.0057 | -0.032043 | 0.16937 | -0.13733 | 0.19226 | -0.11444 | 0.25177 | 122.937 | -0.009155 | -0.004578 | 123.0743 | 123.0194 | 122.9462 | 122.9965 | -123.1064 | -123.0011 | 122.8088 | -0.027466 | 58.5526 | 58.5617
127.1719 | 123.1247 | -58.5709 | 64.4119 | -0.052948 | -1.9142e-05 | 0.06523 | 0.063918 | -0.00069423 | 0.00026909 | 0.00050839 | -0.0013428 | 0.00024775 | 0.0021362 | 0.0034778 | -1.0706e-05 | -0.00066648 | 0.0032299 | -0.027466 | 64.3662 | -58.7173 | 64.2288 | -58.4702 | -58.8364 | -58.8043 | -0.027466 | 64.4302 | -58.6121 | -58.6212 | -58.6075 | -58.7173 | -58.429 | -0.14648 | -0.045776 | -0.1831 | 0.10071 | -0.23346 | -0.2655 | -0.086975 | -0.11902 | -0.041199 | 0.018311 | -123.0331 | -0.036621 | 0.14191 | -0.14648 | 0.18311 | -0.10529 | 0.24719 | 122.9462 | 0.004578 | -0.009155 | 123.0835 | 123.0423 | 122.937 | 123.0011 | -123.1293 | -123.024 | 122.7997 | -0.050354 | 58.5434 | 58.5434
128.1719 | 123.0835 | -58.6121 | 64.3982 | -0.022431 | 0.0012625 | 0.064375 | 0.064345 | 0.0012284 | -0.00037171 | 0.002431 | 0.0047608 | 0.00088875 | -0.00042717 | -0.00079478 | 0.00041649 | -0.0010937 | 0.00088014 | -0.082397 | 64.3295 | -58.7448 | 64.1785 | -58.5068 | -58.8913 | -58.8409 | -0.10071 | 64.3936 | -58.6395 | -58.6624 | -58.6624 | -58.7769 | -58.4518 | -0.13275 | -0.068664 | -0.21973 | 0.10529 | -0.22888 | -0.27923 | -0.09613 | -0.14648 | -0.027465 | -0.004577 | -123.0606 | -0.050354 | 0.16022 | -0.16479 | 0.18768 | -0.13733 | 0.23804 | 122.9233 | -0.022889 | -0.022889 | 123.0743 | 123.0331 | 122.9416 | 123.0057 | -123.143 | -123.0377 | 122.7905 | -0.050354 | 58.5297 | 58.5114
129.1719 | 123.0835 | -58.6029 | 64.3936 | -0.03006 | -0.00044654 | 0.066298 | 0.063705 | -0.00048063 | -0.0012261 | 0.00050839 | 0.001709 | 0.0015295 | 0.00042723 | 0.002196 | -0.0015061 | 0.0014697 | -0.0014697 | -0.073242 | 64.357 | -58.7311 | 64.183 | -58.4747 | -58.8684 | -58.8501 | -0.10529 | 64.4073 | -58.6304 | -58.6624 | -58.6624 | -58.7631 | -58.4564 | -0.12817 | -0.036621 | -0.21057 | 0.12817 | -0.24719 | -0.2655 | -0.11902 | -0.13733 | -0.027466 | 0.013733 | -123.056 | -0.05951 | 0.14648 | -0.16022 | 0.17395 | -0.13275 | 0.25635 | 122.9141 | -0.032044 | -0.032044 | 123.0881 | 123.0377 | 122.9599 | 123.0103 | -123.1247 | -123.024 | 122.7859 | -0.05951 | 58.5297 | 58.4976
130.1719 | 123.143 | -58.58 | 64.3982 | -0.083466 | 0.00019446 | 0.066084 | 0.065414 | 0.0016556 | -0.0012261 | 0.0015766 | 0.016968 | 0.0023839 | 0.001068 | 0.0036914 | -0.00022431 | -0.0013073 | -0.0036059 | -0.050354 | 64.3524 | -58.7402 | 64.2334 | -58.4427 | -58.8226 | -58.8089 | 0 | 64.3982 | -58.6212 | -58.6075 | -58.5983 | -58.699 | -58.4015 | -0.16022 | -0.045776 | -0.1648 | 0.13733 | -0.22888 | -0.24262 | -0.068665 | -0.082398 | -0.041199 | 0 | -123.0057 | -0.018311 | 0.17853 | -0.11902 | 0.21973 | -0.07782 | 0.29755 | 122.9736 | 0.022888 | 0.013733 | 123.0927 | 123.0194 | 122.9324 | 122.9782 | -123.1384 | -123.0194 | 122.8134 | -0.027466 | 58.5297 | 58.58
131.1719 | 123.111 | -58.5938 | 64.3936 | -0.045319 | -0.00044654 | 0.06523 | 0.063064 | -0.00090783 | 0.00069649 | 0.00072199 | -0.0043946 | 0.0015295 | 0.0019226 | 0.0017688 | -0.0010787 | -0.00066648 | 0.0051525 | -0.064087 | 64.3387 | -58.699 | 64.2151 | -58.4793 | -58.8547 | -58.8226 | -0.073242 | 64.4028 | -58.5892 | -58.6487 | -58.6349 | -58.7402 | -58.4381 | -0.10529 | -0.054932 | -0.17853 | 0.11444 | -0.22888 | -0.26093 | -0.1236 | -0.15564 | 0.004578 | 0.009155 | -123.0423 | -0.041199 | 0.15564 | -0.14648 | 0.15106 | -0.15106 | 0.21973 | 122.9141 | -0.045777 | -0.05951 | 123.0377 | 122.9919 | 122.9324 | 122.9965 | -123.0927 | -122.9828 | 122.8088 | -0.054932 | 58.5297 | 58.5205
132.1719 | 123.1293 | -58.6075 | 64.389 | -0.037689 | 0.0010489 | 0.064162 | 0.063918 | 0.00058737 | -0.00037171 | 0.0015766 | -0.010498 | 0.0015295 | 2.8e-08 | -0.0010084 | -0.00065151 | 0.00082892 | -0.0027515 | -0.054932 | 64.3478 | -58.7082 | 64.1968 | -58.4656 | -58.8501 | -58.7906 | -0.073242 | 64.4119 | -58.6029 | -58.6166 | -58.6349 | -58.7357 | -58.4244 | -0.10071 | -0.041199 | -0.19226 | 0.14191 | -0.1831 | -0.24262 | -0.082397 | -0.14191 | 0.004578 | 0.022888 | -123.0057 | -0.027466 | 0.18311 | -0.12817 | 0.17853 | -0.13275 | 0.24262 | 122.905 | -0.032044 | -0.013733 | 123.056 | 123.0148 | 122.9553 | 123.0194 | -123.0972 | -122.9919 | 122.8043 | -0.009155 | 58.5526 | 58.5342
133.1719 | 123.1201 | -58.5846 | 64.3753 | -0.12924 | 0.0019035 | 0.064162 | 0.063277 | -0.0041122 | -0.0010125 | -0.00077341 | 0.010864 | 0.00088875 | 0.001709 | 0.0024096 | -0.0015061 | 0.00040152 | -0.0025379 | -0.022888 | 64.3662 | -58.7036 | 64.2059 | -58.4518 | -58.8455 | -58.7997 | -0.045776 | 64.3753 | -58.6166 | -58.6212 | -58.6075 | -58.7219 | -58.4106 | -0.11902 | -0.009155 | -0.16937 | 0.13275 | -0.21515 | -0.26093 | -0.096131 | -0.14191 | -0.032043 | 0 | -122.9965 | -0.022888 | 0.17395 | -0.13733 | 0.20599 | -0.10529 | 0.25177 | 122.9095 | 0.009155 | -0.004578 | 123.0698 | 122.9919 | 122.9507 | 122.9599 | -123.0789 | -122.9919 | 122.7905 | -0.036621 | 58.5617 | 58.5388
134.1719 | 123.1018 | -58.5754 | 64.4165 | -0.03006 | 0.0012625 | 0.064162 | 0.06285 | 0.00058737 | -0.00037171 | -0.0014142 | 0.001709 | 0.00046135 | 0.001709 | 0.0026232 | -1.0706e-05 | 0.00061532 | -0.0012561 | -0.07782 | 64.357 | -58.7265 | 64.183 | -58.5022 | -58.8638 | -58.8364 | -0.09613 | 64.3936 | -58.6304 | -58.6578 | -58.6395 | -58.7723 | -58.4564 | -0.15106 | -0.059509 | -0.23346 | 0.073242 | -0.26093 | -0.28839 | -0.10986 | -0.13733 | -0.054932 | -0.022888 | -123.0743 | -0.064087 | 0.11902 | -0.19684 | 0.17395 | -0.14191 | 0.2243 | 122.9095 | -0.009155 | -0.027466 | 123.0835 | 123.024 | 122.9324 | 122.9691 | -123.143 | -123.0469 | 122.7585 | -0.082398 | 58.4976 | 58.4793
135.1719 | 123.1476 | -58.5938 | 64.3936 | -0.014801 | 0.0014761 | 0.064375 | 0.06285 | 0.0016556 | -0.00015811 | -0.00034601 | 0.016968 | 0.00046135 | 0.003418 | 0.0054004 | -0.00065151 | 0.00082892 | -0.0010425 | -0.032043 | 64.357 | -58.7311 | 64.2792 | -58.6395 | -58.9691 | -58.786 | 0.004578 | 64.4257 | -58.6166 | -58.5846 | -58.58 | -58.6853 | -58.3786 | -0.13733 | -0.036621 | -0.11444 | -0.045776 | -0.19226 | -0.37537 | -0.054932 | -0.23804 | -0.022888 | 0.032043 | -122.9782 | 0.013733 | 0.21515 | -0.091553 | 0.23804 | -0.068665 | 0.091553 | 123.0103 | 0.036621 | 0.032043 | 123.0881 | 123.0423 | 122.9507 | 123.0194 | -123.1247 | -123.0103 | 122.8729 | 0.009155 | 58.5617 | 58.5983
136.1719 | 123.1201 | -58.6029 | 64.4073 | -0.068207 | 0.00083526 | 0.064589 | 0.061568 | -0.00026703 | -0.00079891 | 0.0015766 | -0.0043946 | 0.00024775 | 0.00085443 | 0.00048702 | 0.00041649 | -0.00088008 | -0.0023243 | -0.050354 | 64.3433 | -58.7036 | 64.1922 | -58.4656 | -58.8226 | -58.8089 | -0.032043 | 64.4028 | -58.6029 | -58.6304 | -58.6121 | -58.7219 | -58.4335 | -0.10071 | -0.064087 | -0.21515 | 0.13733 | -0.20599 | -0.21973 | -0.10529 | -0.11902 | 0 | -0.004578 | -123.0377 | -0.009156 | 0.16937 | -0.11902 | 0.16937 | -0.11902 | 0.23804 | 122.8958 | -0.009156 | -0.027466 | 123.0469 | 123.0057 | 122.9462 | 123.0057 | -123.111 | -123.0103 | 122.7951 | -0.027466 | 58.5526 | 58.5709
137.1719 | 123.1384 | -58.5892 | 64.4073 | 0.00045798 | -0.00066014 | 0.064589 | 0.061568 | -0.0017624 | 0.0015509 | -0.0014142 | 0.02002 | -0.00017945 | 0.00042723 | 0.0024096 | -0.00022431 | -0.0023755 | -0.0021107 | -0.027466 | 64.3616 | -58.7082 | 64.238 | -58.461 | -58.8181 | -58.7997 | -0.018311 | 64.4028 | -58.5938 | -58.5892 | -58.5846 | -58.699 | -58.3923 | -0.11902 | -0.045777 | -0.16937 | 0.12817 | -0.21057 | -0.22888 | -0.091553 | -0.10986 | -0.004578 | -0.004578 | -122.9965 | 0.004577 | 0.19684 | -0.10986 | 0.20142 | -0.10529 | 0.24719 | 122.9462 | 0.009155 | 0.004578 | 123.0698 | 122.9965 | 122.9507 | 122.9919 | -123.1155 | -123.0011 | 122.8271 | 0 | 58.5617 | 58.5709
138.1719 | 123.1338 | -58.5938 | 64.4257 | 0.00045798 | -0.00066014 | 0.062666 | 0.064345 | -0.00090783 | 0.00048269 | -0.00055961 | 0.013916 | 0.00024775 | -0.00021357 | -0.001222 | -0.00022431 | 0.0010425 | -0.0016833 | -0.059509 | 64.3982 | -58.7265 | 64.1739 | -58.4976 | -58.8318 | -58.8135 | -0.064087 | 64.4302 | -58.5938 | -58.6349 | -58.58 | -58.699 | -58.4106 | -0.13275 | -0.027466 | -0.25177 | 0.09613 | -0.21973 | -0.23804 | -0.086976 | -0.10529 | 0 | 0.004578 | -123.0606 | 0.013733 | 0.1831 | -0.10529 | 0.1831 | -0.10529 | 0.22888 | 122.9004 | 0.013733 | -0.041199 | 123.1247 | 123.024 | 122.9919 | 123.024 | -123.1522 | -123.0194 | 122.7676 | -0.041199 | 58.5342 | 58.5297
139.1719 | 123.1384 | -58.5938 | 64.3707 | -0.052948 | 0.00040806 | 0.06523 | 0.064986 | 0.0020828 | -0.00015811 | 0.0011494 | 0.0047608 | 0.0015295 | 0.004486 | -0.00079478 | 0.00063009 | 0.00061532 | -0.0021107 | -0.036621 | 64.3616 | -58.699 | 64.2059 | -58.4656 | -58.8409 | -58.7906 | -0.050354 | 64.3936 | -58.6166 | -58.6349 | -58.6075 | -58.7311 | -58.429 | -0.10529 | -0.009156 | -0.16479 | 0.12817 | -0.19684 | -0.24719 | -0.091552 | -0.14191 | -0.022888 | 0.022888 | -123.0057 | -0.013733 | 0.16479 | -0.13733 | 0.18768 | -0.11444 | 0.23346 | 122.905 | 0.009155 | -0.018311 | 123.0606 | 123.0103 | 122.9553 | 122.9874 | -123.0698 | -122.9874 | 122.7997 | -0.041199 | 58.5571 | 58.5434
140.1719 | 123.1064 | -58.6029 | 64.3982 | -0.61752 | 0.0019035 | 0.063734 | 0.063277 | -0.001976 | -0.00015811 | 0.0034992 | -0.0043946 | -0.0010339 | 0.0014954 | 0.00091422 | -0.0025741 | 0.00018792 | 0.0023755 | -0.022888 | 64.3341 | -58.7265 | 64.238 | -58.4244 | -58.8089 | -58.786 | -0.027466 | 64.3982 | -58.6212 | -58.6029 | -58.5892 | -58.7173 | -58.4061 | -0.1236 | -0.064087 | -0.16022 | 0.17853 | -0.18311 | -0.20599 | -0.05951 | -0.082398 | -0.018311 | 0 | -123.0011 | 0.013733 | 0.19684 | -0.11444 | 0.21515 | -0.09613 | 0.30212 | 122.9645 | 0.032044 | 0.018311 | 123.0606 | 123.0194 | 122.937 | 123.0011 | -123.1247 | -123.0194 | 122.8409 | 0 | 58.58 | 58.5754
141.1719 | 123.1613 | -58.5663 | 64.389 | -0.03006 | 0.0019035 | 0.061812 | 0.065414 | -0.001976 | -0.00015811 | 0.0017902 | 0.026123 | 0.00088875 | 0.001709 | -0.00036738 | -0.00022431 | -0.0010937 | -0.00018806 | -0.032043 | 64.389 | -58.7128 | 64.2197 | -58.4702 | -58.7952 | -58.786 | -0.027466 | 64.4165 | -58.6121 | -58.6075 | -58.5754 | -58.6761 | -58.3786 | -0.14648 | 0 | -0.16937 | 0.09613 | -0.21973 | -0.22888 | -0.073242 | -0.082397 | -0.045777 | 0.027466 | -122.9965 | -0.009155 | 0.18768 | -0.10986 | 0.23346 | -0.064086 | 0.24262 | 122.9324 | 0.036622 | 0.004578 | 123.1018 | 123.0286 | 122.9553 | 122.9828 | -123.1018 | -123.0011 | 122.786 | -0.041199 | 58.5342 | 58.5388
142.1719 | 123.1659 | -58.5663 | 64.3936 | -0.060578 | -0.0015145 | 0.065657 | 0.064773 | 0.00037377 | -0.0016535 | -0.00034601 | 0.010864 | 0.00024775 | 0.0023498 | 0.0032642 | 0.00084389 | -0.0010937 | 0.00088014 | -0.045776 | 64.3799 | -58.7265 | 64.2151 | -58.4381 | -58.8226 | -58.7769 | -0.009155 | 64.4028 | -58.6029 | -58.5754 | -58.5526 | -58.6487 | -58.3832 | -0.16022 | -0.013733 | -0.17853 | 0.12817 | -0.21057 | -0.25635 | -0.050354 | -0.096131 | -0.036621 | 0.009155 | -122.9691 | 0.013733 | 0.18311 | -0.082398 | 0.21973 | -0.045777 | 0.28839 | 122.9416 | 0.050354 | 0.027466 | 123.1064 | 123.0057 | 122.9462 | 122.9691 | -123.1201 | -122.9965 | 122.7814 | -0.009155 | 58.5205 | 58.5571
143.1719 | 123.1522 | -58.5754 | 64.4211 | -0.022431 | -0.00087374 | 0.064803 | 0.063918 | 0.0016556 | 0.0028327 | -0.0016278 | 0.026123 | 0.0021703 | 0.00021363 | 0.0013416 | -0.0015061 | -0.0013073 | -0.0046741 | -0.064087 | 64.3662 | -58.7082 | 64.1968 | -58.4976 | -58.8318 | -58.7952 | -0.068665 | 64.4119 | -58.5983 | -58.6166 | -58.5846 | -58.7036 | -58.3923 | -0.13275 | -0.054932 | -0.22431 | 0.077819 | -0.21973 | -0.25635 | -0.086975 | -0.1236 | -0.022889 | -0.009156 | -123.0377 | -0.009156 | 0.18311 | -0.12817 | 0.20599 | -0.10528 | 0.21057 | 122.905 | 0.013733 | -0.01831 | 123.0743 | 123.0103 | 122.9416 | 122.9874 | -123.1293 | -123.0194 | 122.7722 | -0.041199 | 58.5114 | 58.5068
144.1719 | 123.1384 | -58.5754 | 64.4028 | -0.060578 | -0.00066014 | 0.064375 | 0.063277 | -0.00069423 | 0.0011237 | 0.0011494 | -0.0013428 | 0.0025975 | -0.00064077 | 0.0019824 | -0.0012925 | -0.00045288 | -0.0018971 | -0.032043 | 64.3616 | -58.7082 | 64.2151 | -58.4564 | -58.7952 | -58.7814 | 0 | 64.4073 | -58.5983 | -58.5892 | -58.58 | -58.7173 | -58.3786 | -0.13275 | -0.041199 | -0.18768 | 0.11902 | -0.20599 | -0.21973 | -0.073242 | -0.086975 | -0.022889 | 0.004578 | -122.9919 | -0.004578 | 0.19684 | -0.14191 | 0.21973 | -0.11902 | 0.25177 | 122.9233 | 0.018311 | 0.009156 | 123.0698 | 123.0057 | 122.937 | 122.9828 | -123.111 | -123.0011 | 122.7905 | -0.013733 | 58.5434 | 58.5754
145.1719 | 123.1018 | -58.5892 | 64.4119 | -0.037689 | 0.00019446 | 0.063734 | 0.063064 | 0.0020828 | 5.5488e-05 | -0.0014142 | 0.029175 | 0.00088875 | 2.8e-08 | -0.0016492 | -0.00065151 | -0.0010937 | 2.554e-05 | -0.064087 | 64.3707 | -58.7036 | 64.183 | -58.5022 | -58.8409 | -58.786 | -0.07782 | 64.4119 | -58.6075 | -58.6349 | -58.5983 | -58.7082 | -58.4015 | -0.11444 | -0.041198 | -0.22888 | 0.086975 | -0.19684 | -0.25177 | -0.082398 | -0.13733 | -0.018311 | 0 | -123.0469 | -0.009156 | 0.18768 | -0.11902 | 0.20599 | -0.10071 | 0.20142 | 122.8867 | 0.009155 | -0.027466 | 123.0743 | 123.0194 | 122.9599 | 123.0011 | -123.1155 | -123.0194 | 122.7722 | -0.045777 | 58.5251 | 58.5114
146.1719 | 123.1796 | -58.5754 | 64.3982 | -0.037689 | 0.0025443 | 0.065657 | 0.063277 | 0.0018692 | 0.0011237 | -0.00098701 | -0.025757 | 0.00046135 | 2.8e-08 | 0.003905 | -0.0010787 | 0.00061532 | -0.0012561 | -0.045776 | 64.3387 | -58.7128 | 64.2197 | -58.4427 | -58.8226 | -58.786 | -0.027466 | 64.3936 | -58.6166 | -58.5983 | -58.6533 | -58.8364 | -58.5068 | -0.13733 | -0.059509 | -0.17853 | 0.13275 | -0.21057 | -0.24719 | -0.073242 | -0.10986 | -0.041199 | -0.004577 | -122.9965 | -0.07782 | 0.068664 | -0.26093 | 0.10986 | -0.21973 | 0.27008 | 122.9324 | -0.036621 | 0.01831 | 123.0515 | 123.0103 | 122.9141 | 122.9691 | -123.111 | -123.0148 | 122.7951 | -0.022889 | 58.5297 | 58.548
147.1719 | 123.1293 | -58.5892 | 64.4165 | -0.068207 | 0.0029715 | 0.065657 | 0.063277 | -0.0032578 | -0.00037171 | 0.00093559 | 0.010864 | 0.00067495 | 2.8e-08 | 0.0049732 | -0.00022431 | 0.0012561 | 0.0040845 | -0.032043 | 64.389 | -58.7173 | 64.2242 | -58.4518 | -58.8181 | -58.7952 | -0.022888 | 64.3753 | -58.5709 | -58.5983 | -58.5709 | -58.6853 | -58.3832 | -0.12817 | -0.027466 | -0.19226 | 0.13733 | -0.20599 | -0.22888 | -0.07782 | -0.10071 | 0.01831 | -0.041199 | -123.0148 | 0.01831 | 0.20599 | -0.096131 | 0.18768 | -0.11444 | 0.2655 | 122.9416 | 0 | -0.027466 | 123.1064 | 122.9462 | 122.9782 | 122.9645 | -123.1338 | -122.9874 | 122.8134 | -0.009156 | 58.5571 | 58.5663
148.1719 | 123.1338 | -58.5983 | 64.4302 | -0.045319 | 0.0012625 | 0.064162 | 0.063491 | 0.00016017 | 5.5488e-05 | -0.00098701 | 0.029175 | 0.00088875 | 0.00042723 | -0.00015378 | -0.00022431 | -0.0013073 | -0.0031787 | -0.09613 | 64.389 | -58.7219 | 64.2059 | -58.5159 | -58.8272 | -58.7997 | -0.073242 | 64.4211 | -58.6075 | -58.6212 | -58.58 | -58.7036 | -58.4015 | -0.1236 | -0.041199 | -0.2243 | 0.082398 | -0.20142 | -0.22888 | -0.07782 | -0.10529 | -0.009155 | -0.009155 | -123.0515 | 0.018311 | 0.19684 | -0.10528 | 0.20599 | -0.09613 | 0.20599 | 122.9279 | 0.027466 | -0.013733 | 123.111 | 123.0286 | 122.9874 | 123.0194 | -123.1522 | -123.0377 | 122.8043 | -0.022888 | 58.5022 | 58.5251
149.1719 | 123.0972 | -58.6029 | 64.4348 | -0.03006 | 0.0025443 | 0.063094 | 0.063918 | 0.00058737 | 5.5488e-05 | 0.00050839 | 0.02002 | -0.00039305 | 0.0012818 | -0.0080578 | 0.00063009 | -0.0010937 | 0.0025891 | -0.059509 | 64.4119 | -58.7082 | 64.1922 | -58.4885 | -58.8455 | -58.8043 | -0.091553 | 64.4165 | -58.6075 | -58.6304 | -58.5938 | -58.7036 | -58.4152 | -0.10529 | -0.022888 | -0.24261 | 0.11444 | -0.20142 | -0.24262 | -0.09613 | -0.13733 | -0.004578 | -0.01831 | -123.0652 | 0.009155 | 0.18768 | -0.10071 | 0.19226 | -0.09613 | 0.21973 | 122.9004 | 0.013733 | -0.022888 | 123.1201 | 123.024 | 123.0148 | 123.0194 | -123.143 | -123.0423 | 122.7951 | -0.027466 | 58.5434 | 58.5114
150.1719 | 123.111 | -58.5892 | 64.4073 | -0.0071715 | -0.00066014 | 0.065657 | 0.065414 | 0.0012284 | 0.00069649 | -0.0029096 | 0.029175 | 0.00088875 | 0.0042724 | 0.00048702 | -0.0021469 | -0.00088008 | 0.00023934 | -0.09613 | 64.3845 | -58.7311 | 64.2014 | -58.4885 | -58.8318 | -58.8043 | -0.09613 | 64.4211 | -58.5846 | -58.6349 | -58.5983 | -58.7265 | -58.4244 | -0.14191 | -0.022889 | -0.20599 | 0.10071 | -0.21515 | -0.24262 | -0.073242 | -0.10071 | 0.004577 | 0.013733 | -123.0423 | -0.009156 | 0.16479 | -0.13733 | 0.16022 | -0.14191 | 0.24262 | 122.9324 | -0.013733 | -0.050354 | 123.1155 | 123.0057 | 122.9736 | 123.0103 | -123.1384 | -122.9919 | 122.7905 | -0.045777 | 58.493 | 58.493
151.1719 | 123.0972 | -58.5571 | 64.4302 | -0.068207 | 0.00083526 | 0.065871 | 0.062423 | 0.0010148 | -0.00015811 | 0.0015766 | 0.074951 | 0.0017431 | 0.0019226 | -0.002931 | 0.00041649 | -0.00066648 | 0.00045294 | -0.054932 | 64.3936 | -58.6761 | 64.1876 | -58.4793 | -58.8272 | -58.786 | -0.059509 | 64.4211 | -58.5892 | -58.6441 | -58.5938 | -58.7036 | -58.4335 | -0.11902 | -0.036621 | -0.24262 | 0.07782 | -0.22888 | -0.27008 | -0.10986 | -0.15106 | -0.032043 | -0.009155 | -123.0743 | -0.036621 | 0.1236 | -0.14648 | 0.15564 | -0.11444 | 0.19684 | 122.8638 | -0.004578 | -0.054932 | 123.0698 | 123.0103 | 122.9507 | 122.9782 | -123.1064 | -123.0194 | 122.7448 | -0.086975 | 58.5022 | 58.4976
152.1719 | 123.0881 | -58.5938 | 64.4531 | -0.03006 | -0.00066014 | 0.063094 | 0.061996 | -0.0021896 | -0.0016535 | -0.0014142 | 0.02002 | 0.0023839 | 0.002777 | 5.9824e-05 | -0.0012925 | -0.00023928 | -0.00061526 | -0.082397 | 64.3845 | -58.6899 | 64.1235 | -58.667 | -58.8043 | -58.8043 | -0.086975 | 64.4165 | -58.5983 | -58.6349 | -58.6121 | -58.7128 | -58.4335 | -0.09613 | -0.068665 | -0.32959 | -0.073242 | -0.21057 | -0.21057 | -0.11444 | -0.11444 | -0.004578 | -0.036621 | -123.0881 | -0.018311 | 0.16022 | -0.11902 | 0.1648 | -0.11444 | 0.022888 | 122.8134 | -0.013733 | -0.036621 | 123.0743 | 123.0148 | 122.9782 | 123.0103 | -123.143 | -123.0515 | 122.7173 | -0.041199 | 58.5114 | 58.5068
153.1719 | 123.1155 | -58.5938 | 64.4257 | -0.052948 | 0.00019446 | 0.060744 | 0.064345 | 0.0020828 | 0.0026191 | -0.00098701 | 0.02002 | 0.0017431 | 0.00021363 | 0.0043322 | -0.0012925 | 0.0010425 | -0.0038197 | -0.068665 | 64.3662 | -58.6945 | 64.2014 | -58.493 | -58.8364 | -58.786 | -0.07782 | 64.4119 | -58.6166 | -58.6166 | -58.5892 | -58.6899 | -58.4152 | -0.10071 | -0.059509 | -0.2243 | 0.10071 | -0.19226 | -0.24262 | -0.091553 | -0.14191 | -0.022888 | -0.013733 | -123.0423 | 0.004578 | 0.17853 | -0.09613 | 0.20142 | -0.073242 | 0.20142 | 122.8958 | 0.027466 | 0 | 123.0606 | 123.0286 | 122.9599 | 123.0057 | -123.1201 | -123.0423 | 122.7951 | -0.022888 | 58.5251 | 58.5159
154.1719 | 123.143 | -58.5983 | 64.444 | -0.022431 | 0.00040806 | 0.06288 | 0.062209 | 0.00016017 | -0.00058531 | 0.00072199 | 0.02002 | 0.0028113 | 0.001068 | 0.0036914 | -0.00043791 | -0.0028027 | -0.0010425 | -0.086975 | 64.3845 | -58.7219 | 64.1968 | -58.493 | -58.8364 | -58.8181 | -0.10529 | 64.4073 | -58.5892 | -58.6212 | -58.5983 | -58.7219 | -58.4061 | -0.1236 | -0.05951 | -0.24719 | 0.10529 | -0.21973 | -0.23804 | -0.09613 | -0.11444 | 0.009156 | -0.036621 | -123.0652 | 0 | 0.19226 | -0.1236 | 0.1831 | -0.13275 | 0.22888 | 122.9187 | -0.009156 | -0.032044 | 123.1064 | 122.9965 | 122.9828 | 123.0057 | -123.1659 | -123.0331 | 122.7951 | -0.022888 | 58.5114 | 58.493
155.1719 | 123.1384 | -58.5938 | 64.4073 | -0.060578 | -1.9142e-05 | 0.064162 | 0.0652 | 0.0040054 | 0.00026909 | 0.00072199 | 0.001709 | 0.0015295 | 0.0019226 | -0.0018628 | -0.0012925 | -0.00088008 | 0.0019483 | -0.059509 | 64.4119 | -58.6853 | 64.2517 | -58.4702 | -58.8181 | -58.7906 | -0.054932 | 64.4257 | -58.6075 | -58.5938 | -58.5754 | -58.6807 | -58.3786 | -0.091553 | 0.004577 | -0.15564 | 0.1236 | -0.19684 | -0.2243 | -0.10529 | -0.13275 | -0.013733 | 0.01831 | -123.0011 | 0.018311 | 0.21515 | -0.086975 | 0.22888 | -0.073242 | 0.21515 | 122.937 | 0.032044 | 0.013733 | 123.0972 | 123.0331 | 123.0057 | 123.0194 | -123.0927 | -123.0148 | 122.8455 | 0 | 58.5342 | 58.5388
156.1719 | 123.1567 | -58.5983 | 64.4119 | -0.037689 | 0.0019035 | 0.065016 | 0.063705 | 0.00058737 | 0.0024053 | -0.002055 | -0.0043946 | 0.0019567 | 0.00042723 | 0.0019824 | -0.00065151 | 0.00018792 | -0.0044605 | -0.068665 | 64.3707 | -58.7173 | 64.2059 | -58.4885 | -58.7997 | -58.7952 | -0.091553 | 64.4165 | -58.5983 | -58.5892 | -58.5571 | -58.699 | -58.3786 | -0.11902 | -0.041198 | -0.20599 | 0.10986 | -0.19684 | -0.20142 | -0.07782 | -0.082398 | 0 | 0.004578 | -123.0011 | 0.041199 | 0.21973 | -0.10071 | 0.21973 | -0.10071 | 0.22888 | 122.9233 | 0.041199 | 0.009156 | 123.0881 | 123.0148 | 122.9691 | 123.0148 | -123.1293 | -123.0103 | 122.8043 | 0.009156 | 58.5297 | 58.5068
157.1719 | 123.1338 | -58.5526 | 64.4073 | -0.052948 | 0.00062166 | 0.062025 | 0.063064 | 0.0018692 | -0.0020807 | -0.00098701 | -0.0043946 | 0.0015295 | -0.00042717 | -0.00229 | -0.00022431 | -0.00045288 | 0.0030163 | -0.07782 | 64.3799 | -58.7173 | 64.2059 | -58.4885 | -58.8272 | -58.786 | -0.09613 | 64.4257 | -58.6121 | -58.6212 | -58.58 | -58.6899 | -58.3786 | -0.16479 | -0.027466 | -0.20142 | 0.064087 | -0.23346 | -0.27466 | -0.068665 | -0.10986 | -0.05951 | 0.01831 | -123.0286 | -0.027466 | 0.17395 | -0.13733 | 0.23346 | -0.077819 | 0.22888 | 122.9233 | 0.032044 | -0.009155 | 123.0972 | 123.0377 | 122.9324 | 122.9782 | -123.1247 | -123.0194 | 122.7585 | -0.068665 | 58.4747 | 58.4564
158.1719 | 123.1018 | -58.5754 | 64.4577 | -0.083466 | 0.0010489 | 0.06288 | 0.060073 | -0.0026168 | -0.00058531 | -0.00077341 | 0.041382 | -0.00017945 | 0.0021362 | -0.0027174 | -0.00086511 | -0.00088008 | 0.00088014 | -0.045776 | 64.3753 | -58.6578 | 64.2563 | -58.4381 | -58.7814 | -58.7631 | -0.073242 | 64.3982 | -58.6029 | -58.6441 | -58.5892 | -58.6807 | -58.429 | -0.082398 | -0.082398 | -0.20142 | 0.13733 | -0.18768 | -0.20599 | -0.10529 | -0.1236 | -0.027466 | -0.05951 | -123.1018 | -0.013733 | 0.14648 | -0.10529 | 0.17395 | -0.07782 | 0.21973 | 122.9141 | 0.013733 | -0.041199 | 123.0331 | 123.0011 | 122.9507 | 122.9736 | -123.1155 | -123.0606 | 122.8317 | -0.068665 | 58.5297 | 58.5022
159.1719 | 123.0789 | -58.6075 | 64.4073 | -0.022431 | -0.0019417 | 0.061171 | 0.064773 | -0.0017624 | -0.0014399 | 0.00050839 | 0.026123 | 0.00088875 | 0.00085443 | -0.00015378 | -1.0706e-05 | -0.0023755 | 0.0021619 | -0.086975 | 64.4073 | -58.7219 | 64.1968 | -58.4793 | -58.8272 | -58.786 | 0.091553 | 64.4714 | -58.5663 | -58.6395 | -58.6258 | -58.6945 | -58.429 | -0.11444 | 0 | -0.21057 | 0.12817 | -0.17853 | -0.21973 | -0.064087 | -0.10529 | 0.041199 | 0.064087 | -123.0469 | -0.01831 | 0.17853 | -0.086975 | 0.13733 | -0.12817 | 0.24262 | 122.9187 | -0.059509 | -0.073242 | 123.1293 | 123.0377 | 123.0148 | 123.0789 | -123.1293 | -122.9736 | 122.8043 | -0.032043 | 58.5205 | 58.699
160.1719 | 123.1293 | -58.5938 | 64.4165 | 0.00045798 | 0.0010489 | 0.061812 | 0.061996 | -5.343e-05 | -0.0020807 | -0.0016278 | -0.0074462 | 0.0013159 | 0.00064083 | -0.0048536 | -0.0017197 | -0.00045288 | 0.0034435 | -0.086975 | 64.3936 | -58.7128 | 64.1876 | -58.4839 | -58.8455 | -58.8043 | -0.11902 | 64.4485 | -58.6029 | -58.6258 | -58.58 | -58.7082 | -58.4106 | -0.11902 | -0.022888 | -0.22888 | 0.10986 | -0.21057 | -0.25177 | -0.091552 | -0.13275 | -0.009155 | 0.032043 | -123.0423 | 0.013733 | 0.1831 | -0.11444 | 0.19226 | -0.10529 | 0.22888 | 122.9004 | 0.022888 | -0.022888 | 123.1064 | 123.0515 | 122.9874 | 123.0423 | -123.1293 | -123.0194 | 122.7814 | -0.032043 | 58.5068 | 58.4747
161.1719 | 123.111 | -58.5846 | 64.4211 | 0.030975 | 0.00062166 | 0.065443 | 0.06285 | -0.001976 | -0.0016535 | -0.0012006 | 0.0078126 | -0.00039305 | 0.0023498 | -0.00229 | -0.0010787 | 0.00040152 | 0.0021619 | -0.12817 | 64.3936 | -58.7219 | 64.2014 | -58.4885 | -58.8318 | -58.8089 | -0.11902 | 64.4073 | -58.6075 | -58.6533 | -58.58 | -58.699 | -58.4335 | -0.13733 | -0.027466 | -0.21973 | 0.096131 | -0.2243 | -0.24719 | -0.086975 | -0.10986 | -0.022888 | -0.013733 | -123.0743 | 0.004578 | 0.15106 | -0.11444 | 0.17395 | -0.091553 | 0.23346 | 122.9233 | 0.027466 | -0.045776 | 123.1155 | 123.0148 | 122.9782 | 122.9919 | -123.143 | -123.0286 | 122.786 | -0.068664 | 58.4564 | 58.4656
162.1719 | 123.1522 | -58.5571 | 64.4302 | -0.052948 | 0.00062166 | 0.061598 | 0.063064 | -0.00069423 | 5.5488e-05 | 0.001363 | -0.0013428 | -0.00039305 | 0.00085443 | -0.005708 | -0.0012925 | -2.5678e-05 | -0.0018971 | -0.086975 | 64.3799 | -58.6853 | 64.2151 | -58.4793 | -58.8043 | -58.7906 | -0.11902 | 64.4348 | -58.5983 | -58.5983 | -58.5709 | -58.6899 | -58.3923 | -0.12817 | -0.050354 | -0.21515 | 0.07782 | -0.23346 | -0.24719 | -0.10529 | -0.11902 | -0.041199 | 0.004577 | -123.0286 | -0.013733 | 0.1648 | -0.13275 | 0.20599 | -0.091552 | 0.20599 | 122.9004 | 0.027466 | 0 | 123.0652 | 123.0331 | 122.937 | 122.9919 | -123.1155 | -123.0286 | 122.7722 | -0.041199 | 58.4702 | 58.4381
163.1719 | 123.1384 | -58.58 | 64.4348 | -0.022431 | 0.0021171 | 0.066725 | 0.064773 | 0.00037377 | -0.00015811 | -0.00077341 | 0.013916 | 0.0013159 | 0.0023498 | -0.00058098 | -0.0012925 | -0.0010937 | 0.0042981 | -0.09613 | 64.3845 | -58.7082 | 64.2014 | -58.4839 | -58.8318 | -58.8043 | -0.13275 | 64.4165 | -58.6075 | -58.6212 | -58.5709 | -58.6945 | -58.4015 | -0.12817 | -0.050354 | -0.23346 | 0.09613 | -0.2243 | -0.25177 | -0.09613 | -0.1236 | -0.027466 | -0.01831 | -123.056 | 0.009155 | 0.17853 | -0.11444 | 0.20599 | -0.086975 | 0.2243 | 122.9095 | 0.036621 | -0.013733 | 123.0927 | 123.024 | 122.9645 | 122.9965 | -123.143 | -123.0423 | 122.7814 | -0.041199 | 58.4839 | 58.4473
164.1719 | 123.1018 | -58.5846 | 64.4028 | -0.037689 | -0.00066014 | 0.061598 | 0.063918 | -5.343e-05 | 0.0015509 | -0.00034601 | 0.10547 | -0.00060665 | 0.0012818 | -0.0042126 | 0.00063009 | -0.00045288 | 0.0015209 | -0.10986 | 64.4119 | -58.7128 | 64.1922 | -58.4839 | -58.8409 | -58.7906 | -0.21973 | 64.4348 | -58.6121 | -58.6624 | -58.5983 | -58.7265 | -58.4244 | -0.12817 | 0.009155 | -0.21057 | 0.10071 | -0.20599 | -0.25635 | -0.077819 | -0.12817 | -0.027466 | 0.032043 | -123.0652 | -0.013733 | 0.16022 | -0.14191 | 0.18768 | -0.11444 | 0.22888 | 122.905 | 0.013733 | -0.050354 | 123.1247 | 123.0469 | 122.9965 | 123.0194 | -123.1155 | -123.0148 | 122.7768 | -0.07782 | 58.4747 | 58.3649
165.1719 | 123.1018 | -58.5663 | 64.4302 | -0.083466 | 0.00062166 | 0.064589 | 0.064345 | -0.0011214 | 0.0011237 | 0.00093559 | 0.047485 | -0.0012477 | 0.001709 | -0.003999 | -0.00065151 | -0.0013073 | 0.0017345 | -0.064087 | 64.3662 | -58.6853 | 64.2746 | -58.4061 | -58.7677 | -58.7265 | -0.073242 | 64.4119 | -58.5892 | -58.6212 | -58.5663 | -58.6533 | -58.4198 | -0.11902 | -0.064087 | -0.15564 | 0.16022 | -0.16022 | -0.20142 | -0.041198 | -0.082397 | -0.022888 | -0.018311 | -123.0515 | 0 | 0.14648 | -0.086975 | 0.16937 | -0.064087 | 0.27924 | 122.9599 | 0.022888 | -0.032044 | 123.0515 | 123.0011 | 122.9324 | 122.9782 | -123.1155 | -123.0194 | 122.8409 | -0.054932 | 58.5022 | 58.493
166.1719 | 123.056 | -58.5571 | 64.4119 | -0.037689 | 0.00040806 | 0.062453 | 0.062423 | -0.00090783 | -0.00079891 | -0.0022686 | 0.013916 | 0.0015295 | 0.0014954 | -0.0018628 | -0.0012925 | -2.5678e-05 | 0.00066654 | -0.10986 | 64.3753 | -58.7082 | 64.1968 | -58.4702 | -58.8226 | -58.7906 | -0.13275 | 64.4211 | -58.6029 | -58.6349 | -58.5938 | -58.4427 | -58.3466 | -0.15106 | -0.036621 | -0.21515 | 0.086975 | -0.23346 | -0.2655 | -0.082397 | -0.11444 | -0.045776 | 0.009156 | -123.0469 | -0.036621 | 0.21057 | 0.11444 | 0.25635 | 0.16022 | 0.23804 | 122.905 | 0.009155 | -0.032044 | 123.0835 | 123.024 | 122.9324 | 122.9782 | -123.1201 | -123.0148 | 122.7539 | -0.07782 | 58.4473 | 58.4244
167.1719 | 123.111 | -58.5938 | 64.4028 | -0.098725 | 0.0042533 | 0.063948 | 0.065414 | 0.0020828 | 0.0019781 | -0.00034601 | -0.059326 | 0.00024775 | 0.00064083 | -0.0016492 | -0.00065151 | -2.5678e-05 | 0.0028027 | -0.21973 | 64.3341 | -58.754 | 64.1281 | -58.5754 | -58.9188 | -58.8821 | -0.23346 | 64.3707 | -58.667 | -58.699 | -58.6212 | -58.786 | -58.4793 | -0.16022 | -0.068665 | -0.27466 | 0.018311 | -0.28839 | -0.32501 | -0.12817 | -0.16479 | -0.073242 | -0.032043 | -123.1018 | -0.027466 | 0.11444 | -0.19226 | 0.18768 | -0.11902 | 0.17853 | 122.8821 | 0.045776 | -0.032044 | 123.0881 | 123.0377 | 122.9279 | 122.9645 | -123.1567 | -123.0698 | 122.7219 | -0.10529 | 58.374 | 58.3603
168.1719 | 123.1476 | -58.5846 | 64.4028 | -0.045319 | -0.00044654 | 0.064162 | 0.064986 | 0.003151 | 5.5488e-05 | 0.00029479 | -0.0013428 | 0.0015295 | 0.001068 | -0.002931 | -0.00065151 | -0.0013073 | -0.0021107 | -0.10986 | 64.3936 | -58.7219 | 64.2014 | -58.4839 | -58.8226 | -58.7952 | -0.16022 | 64.4165 | -58.6166 | -58.6029 | -58.5663 | -58.6853 | -58.3832 | -0.13733 | -0.009155 | -0.20142 | 0.10071 | -0.21057 | -0.23804 | -0.073242 | -0.10071 | -0.032043 | 0.013733 | -123.0057 | 0.018311 | 0.20142 | -0.10071 | 0.23346 | -0.068665 | 0.23804 | 122.9233 | 0.050354 | 0.013733 | 123.1155 | 123.0331 | 122.9782 | 123.0011 | -123.1247 | -123.0194 | 122.786 | -0.01831 | 58.4747 | 58.4244
169.1719 | 123.111 | -58.5938 | 64.4257 | -0.060578 | -0.00044654 | 0.065443 | 0.061996 | -0.0028304 | -0.00058531 | 8.1188e-05 | -0.047119 | 0.0036657 | 0.0021362 | 0.00027342 | -0.0012925 | -0.00045288 | -0.0014697 | -0.1236 | 64.3982 | -58.6899 | 64.1922 | -58.5159 | -58.5526 | -58.7265 | -0.16479 | 64.4073 | -58.6121 | -58.6349 | -58.58 | -58.7128 | -58.4152 | -0.09613 | -0.027466 | -0.23346 | 0.07782 | -0.13275 | 0.041199 | -0.036621 | 0.13733 | -0.018311 | -0.01831 | -123.0606 | 0.013733 | 0.17853 | -0.11902 | 0.19684 | -0.10071 | 0.17395 | 122.8821 | 0.032044 | -0.022888 | 123.0881 | 123.0194 | 122.9919 | 123.0011 | -123.1155 | -123.0377 | 122.7859 | -0.041199 | 58.4702 | 58.429
170.1719 | 123.1338 | -58.58 | 64.4348 | -0.098725 | 0.00062166 | 0.064162 | 0.063277 | -0.0032578 | -0.0014399 | -0.0012006 | -0.0043946 | 0.00046135 | 0.0019226 | -0.0037854 | 0.00084389 | -0.0017347 | 0.00066654 | -0.11444 | 64.3845 | -58.7082 | 64.1968 | -58.493 | -58.8226 | -58.8181 | -0.19226 | 64.4119 | -58.5938 | -58.6304 | -58.5663 | -58.7082 | -58.4106 | -0.12817 | -0.050354 | -0.23804 | 0.086975 | -0.23804 | -0.24262 | -0.10986 | -0.11444 | -0.013733 | -0.022888 | -123.0652 | 0.013733 | 0.16937 | -0.12817 | 0.1831 | -0.11444 | 0.21515 | 122.905 | 0.027466 | -0.036621 | 123.0927 | 123.0057 | 122.9645 | 122.9919 | -123.143 | -123.0286 | 122.7768 | -0.050354 | 58.4656 | 58.3878
171.1719 | 123.0423 | -58.5663 | 64.4119 | -0.037689 | 0.0012625 | 0.064803 | 0.063277 | -0.00090783 | 0.00091009 | -0.0018414 | -0.0074462 | 0.0015295 | 0.0042724 | 0.00027342 | -0.00086511 | -0.0013073 | -0.00040166 | -0.13275 | 64.3799 | -58.7265 | 64.1876 | -58.461 | -58.8181 | -58.7906 | -0.16022 | 64.4119 | -58.5983 | -58.7128 | -58.4427 | -58.5114 | -58.4427 | -0.16022 | -0.032043 | -0.2243 | 0.10529 | -0.2243 | -0.25177 | -0.064087 | -0.091553 | -0.032044 | 0 | -123.1247 | 0.1236 | 0.1236 | 0.054931 | 0.15564 | 0.086975 | 0.2655 | 122.9141 | 0.15564 | -0.11444 | 123.1064 | 123.0103 | 122.9462 | 122.9782 | -123.1384 | -123.0103 | 122.7539 | -0.14648 | 58.4335 | 58.4061
172.1719 | 123.2208 | -58.5846 | 64.3433 | -0.11398 | -0.00044654 | 0.065443 | 0.063491 | -0.00090783 | 5.5488e-05 | -0.00077341 | 0.0078126 | 3.4148e-05 | 0.00085443 | -0.0031446 | -0.0032151 | -0.0015211 | -0.0021107 | -0.18768 | 64.3295 | -58.7494 | 64.2151 | -58.4473 | -58.8181 | -58.7814 | -0.2243 | 64.3295 | -58.6395 | -58.5663 | -58.5388 | -58.667 | -58.342 | -0.16479 | -0.013733 | -0.12817 | 0.13733 | -0.19684 | -0.23346 | -0.032043 | -0.068664 | -0.054931 | -0.013733 | -122.9095 | 0.045777 | 0.24262 | -0.082397 | 0.29755 | -0.027466 | 0.30212 | 122.9645 | 0.10071 | 0.073242 | 123.0789 | 122.9691 | 122.9141 | 122.9141 | -123.0927 | -122.9828 | 122.7997 | 0.018311 | 58.3969 | 58.3603
173.1719 | 123.1155 | -58.58 | 64.4302 | -0.014801 | -0.00087374 | 0.062453 | 0.065627 | -0.0011214 | -0.00037171 | -0.00034601 | 0.0047608 | 0.0015295 | 0.00021363 | -0.0027174 | 0.0010575 | -0.0015211 | 0.0038709 | -0.19684 | 64.4028 | -58.699 | 64.2014 | -58.5159 | -58.8547 | -58.7997 | -0.20599 | 64.4485 | -58.6258 | -58.6258 | -58.5983 | -58.6945 | -58.429 | -0.11902 | -0.027466 | -0.22888 | 0.064087 | -0.21973 | -0.27466 | -0.10071 | -0.15564 | -0.045776 | 0.01831 | -123.056 | -0.018311 | 0.15106 | -0.11444 | 0.19684 | -0.068665 | 0.18311 | 122.9004 | 0.027465 | 0 | 123.1018 | 123.0743 | 122.9828 | 123.0286 | -123.1293 | -123.056 | 122.7814 | -0.045776 | 58.3832 | 58.374
174.1719 | 123.0881 | -58.58 | 64.4257 | -0.052948 | -0.0010873 | 0.065443 | 0.063277 | -0.00090783 | -0.00058531 | 0.0022174 | 0.026123 | -0.00060665 | 0.0019226 | -0.0033582 | -1.0706e-05 | -0.0013073 | -0.0042469 | -0.12817 | 64.3936 | -58.6853 | 64.3707 | -58.3878 | -59.0057 | -58.9554 | -0.21057 | 64.4119 | -58.5938 | -58.6395 | -58.6029 | -58.6899 | -58.3969 | -0.10529 | -0.032043 | -0.054931 | 0.19226 | -0.37537 | -0.42572 | -0.27008 | -0.32043 | -0.013733 | -0.013733 | -123.0652 | -0.022888 | 0.1831 | -0.10986 | 0.19684 | -0.09613 | 0.29755 | 123.056 | -0.009155 | -0.045776 | 123.0789 | 123.0057 | 122.9736 | 122.9919 | -123.111 | -123.0194 | 122.9507 | -0.059509 | 58.4518 | 58.3694
175.1719 | 123.1155 | -58.5663 | 64.4211 | -0.045319 | 0.0010489 | 0.063521 | 0.063918 | -0.0017624 | 5.5488e-05 | 0.0015766 | -0.0013428 | 0.0019567 | 0.0014954 | -0.001222 | -0.0023605 | -0.00088008 | -0.0027515 | -0.15106 | 64.389 | -58.7036 | 64.1968 | -58.4839 | -58.8593 | -58.7906 | -0.2243 | 64.4211 | -58.6075 | -58.5938 | -58.5617 | -58.6945 | -58.3923 | -0.13733 | -0.032044 | -0.22431 | 0.082397 | -0.2243 | -0.29297 | -0.086975 | -0.15564 | -0.041199 | 0 | -123.0148 | 0.004577 | 0.17395 | -0.12817 | 0.21515 | -0.086975 | 0.21973 | 122.9004 | 0.045776 | 0.013733 | 123.0927 | 123.0286 | 122.9553 | 122.9874 | -123.1247 | -123.0286 | 122.7631 | -0.027466 | 58.4152 | 58.342
176.1719 | 123.1018 | -58.5663 | 64.4119 | -0.03006 | 0.00040806 | 0.063948 | 0.063705 | 0.0029374 | -0.00015811 | 0.0011494 | 0.016968 | 3.4148e-05 | 0.00064083 | -0.00058098 | -0.00022431 | -0.0013073 | 0.0021619 | -0.14648 | 64.4073 | -58.7265 | 64.1968 | -58.4885 | -58.8364 | -58.8089 | -0.2243 | 64.444 | -58.5938 | -58.6258 | -58.5709 | -58.6945 | -58.4015 | -0.16022 | -0.004577 | -0.21515 | 0.07782 | -0.24261 | -0.27008 | -0.082398 | -0.10986 | -0.027466 | 0.032044 | -123.0377 | -0.004578 | 0.1648 | -0.12817 | 0.19226 | -0.10071 | 0.23804 | 122.9233 | 0.022888 | -0.032043 | 123.1338 | 123.0377 | 122.9736 | 123.0103 | -123.1384 | -123.0057 | 122.7631 | -0.059509 | 58.4198 | 58.342
177.1719 | 123.1018 | -58.6121 | 64.3662 | -0.037689 | -0.00023294 | 0.06523 | 0.065414 | -0.0021896 | 0.0017645 | 0.001363 | 0.001709 | -0.00060665 | 0.0012818 | -0.0020764 | -1.0706e-05 | 0.0018969 | 2.554e-05 | -0.24261 | 64.3341 | -58.7357 | 64.1373 | -58.255 | -58.7448 | -58.8684 | -0.34332 | 64.3982 | -58.6121 | -58.6578 | -58.6578 | -58.8043 | -58.461 | -0.1236 | -0.032044 | -0.22888 | 0.35706 | -0.25635 | -0.13275 | -0.13275 | -0.009155 | 0 | 0.032043 | -123.024 | -0.045776 | 0.15106 | -0.19226 | 0.15106 | -0.19226 | 0.48065 | 122.8729 | -0.045776 | -0.045776 | 123.0698 | 123.0103 | 122.9462 | 123.0103 | -123.1018 | -122.9782 | 122.7493 | -0.045776 | 58.3694 | 58.2687
178.1719 | 123.111 | -58.5938 | 64.4028 | -0.045319 | -0.0032235 | 0.063094 | 0.060927 | 0.0037918 | -0.00015811 | -0.0012006 | 0.013916 | 0.0013159 | 0.00021363 | 0.00027342 | 0.00063009 | 0.00018792 | 0.0019483 | -0.15564 | 64.3845 | -58.6945 | 64.2014 | -58.4839 | -58.8455 | -58.7997 | -0.2243 | 64.444 | -58.6029 | -58.6212 | -58.58 | -58.699 | -58.4152 | -0.10071 | -0.018311 | -0.20142 | 0.10986 | -0.20599 | -0.25177 | -0.10529 | -0.15106 | -0.009155 | 0.041199 | -123.024 | 0.013733 | 0.17853 | -0.10529 | 0.18768 | -0.096131 | 0.21057 | 122.8958 | 0.022888 | -0.018311 | 123.0789 | 123.0469 | 122.9782 | 123.0377 | -123.0972 | -123.0057 | 122.7951 | -0.027466 | 58.4381 | 58.3694
179.1719 | 123.1338 | -58.5754 | 64.3936 | 0.008087 | 0.0012625 | 0.065016 | 0.061996 | -5.343e-05 | 0.00026909 | 0.00093559 | 0.0078126 | 0.00046135 | 0.0019226 | 0.00070062 | 0.00041649 | 0.00061532 | -0.0018971 | -0.14648 | 64.3799 | -58.6945 | 64.2288 | -58.4518 | -58.7997 | -58.7952 | -0.21515 | 64.4211 | -58.5938 | -58.5938 | -58.5617 | -58.6716 | -58.4015 | -0.11902 | -0.013733 | -0.16479 | 0.1236 | -0.21973 | -0.2243 | -0.10071 | -0.10529 | -0.018311 | 0.027466 | -122.9874 | 0.013732 | 0.17395 | -0.096131 | 0.19226 | -0.07782 | 0.24262 | 122.9233 | 0.032043 | 0 | 123.0743 | 123.0148 | 122.9553 | 122.9965 | -123.0881 | -122.9874 | 122.8043 | -0.018311 | 58.429 | 58.3603
180.1719 | 123.0698 | -58.5846 | 64.4211 | -0.037689 | -1.9142e-05 | 0.064803 | 0.06285 | -0.0032578 | -0.0012261 | 0.00072199 | 0.047485 | -0.0012477 | -0.00042717 | 0.00048702 | -0.00022431 | -0.0034437 | 0.0010937 | -0.15564 | 64.3753 | -58.7128 | 64.2197 | -58.4473 | -58.8089 | -58.786 | -0.2243 | 64.4073 | -58.5983 | -58.6304 | -58.5892 | -58.6899 | -58.4335 | -0.12817 | -0.045777 | -0.20142 | 0.13733 | -0.20142 | -0.2243 | -0.073242 | -0.09613 | -0.013733 | -0.013733 | -123.0515 | -0.004577 | 0.15106 | -0.10529 | 0.1648 | -0.091552 | 0.2655 | 122.9324 | 0.009156 | -0.032043 | 123.0881 | 123.0057 | 122.9599 | 122.9919 | -123.1339 | -123.0194 | 122.8043 | -0.045776 | 58.429 | 58.3603
181.1719 | 123.0927 | -58.58 | 64.4302 | -0.045319 | -0.0025827 | 0.064162 | 0.063918 | 0.001442 | -0.0018671 | -0.0018414 | -0.0013428 | 0.0013159 | 0.0014954 | -0.00229 | -0.00086511 | -0.0023755 | -0.0021107 | -0.17853 | 64.389 | -58.7036 | 64.1739 | -58.6349 | -58.9828 | -58.7906 | -0.26093 | 64.4348 | -58.6304 | -58.6349 | -58.5983 | -58.699 | -58.4152 | -0.1236 | -0.041199 | -0.25635 | -0.054932 | -0.21057 | -0.40283 | -0.086975 | -0.27924 | -0.050354 | 0.004577 | -123.0652 | -0.018311 | 0.16479 | -0.11902 | 0.21515 | -0.068665 | 0.068664 | 122.8775 | 0.032043 | -0.004578 | 123.0927 | 123.0652 | 122.9691 | 123.0148 | -123.1338 | -123.0606 | 122.7539 | -0.054932 | 58.4015 | 58.3191
182.1719 | 123.1842 | -58.6075 | 64.3341 | -0.068207 | 0.0025443 | 0.065443 | 0.064773 | 0.0069962 | 0.0013373 | -0.0035504 | 0.010864 | 0.0013159 | 0.002777 | -0.0014356 | -0.00043791 | 0.00061532 | 0.0010937 | -0.21515 | 64.3021 | -58.7448 | 64.2517 | -58.4152 | -58.8043 | -58.7402 | -0.26093 | 64.3478 | -58.5983 | -58.548 | -58.5251 | -58.8181 | -58.5388 | -0.13733 | -0.032043 | -0.082397 | 0.19226 | -0.13275 | -0.19684 | 0.004578 | -0.059509 | 0.009155 | 0.013733 | -122.8821 | 0.082398 | 0.068665 | -0.21057 | 0.05951 | -0.21973 | 0.32959 | 122.9965 | 0.073243 | 0.050354 | 123.0469 | 122.9462 | 122.9095 | 122.9553 | -123.0789 | -122.9324 | 122.8592 | 0.059509 | 58.3923 | 58.3466
183.1719 | 123.1247 | -58.5846 | 64.444 | -0.068207 | 0.00062166 | 0.063307 | 0.063064 | -0.0028304 | -0.0014399 | -0.0012006 | -0.016602 | 0.0011023 | 0.0019226 | 0.0026232 | -0.0010787 | -0.0019483 | 0.00023934 | -0.17395 | 64.3936 | -58.7219 | 64.1922 | -58.4747 | -58.8364 | -58.7952 | -0.28381 | 64.4165 | -58.5938 | -58.6212 | -58.5754 | -58.699 | -58.4244 | -0.13733 | -0.050354 | -0.25177 | 0.10986 | -0.21057 | -0.25177 | -0.073242 | -0.11444 | -0.009155 | -0.027466 | -123.0652 | 0.009156 | 0.16022 | -0.11444 | 0.16937 | -0.10529 | 0.24719 | 122.9141 | 0.018311 | -0.027466 | 123.1155 | 123.0103 | 122.9782 | 123.0011 | -123.1659 | -123.0377 | 122.7768 | -0.036621 | 58.4106 | 58.3008
184.1719 | 123.0743 | -58.5892 | 64.4073 | -0.045319 | 0.00019446 | 0.063094 | 0.063491 | 0.00251 | -0.00015811 | -0.0018414 | -0.0013428 | 0.00088875 | 0.0025634 | -0.0010084 | -0.00022431 | 0.00061532 | -0.0038197 | -0.16937 | 64.3845 | -58.7219 | 64.1968 | -58.4839 | -58.8272 | -58.8089 | -0.29755 | 64.4257 | -58.5892 | -58.6395 | -58.5846 | -58.7082 | -58.4381 | -0.13275 | -0.022889 | -0.21057 | 0.10528 | -0.21973 | -0.23804 | -0.086975 | -0.10529 | 0 | 0.01831 | -123.0469 | 0.004577 | 0.15106 | -0.11902 | 0.15106 | -0.11902 | 0.23804 | 122.9187 | 0.004577 | -0.050354 | 123.1064 | 123.0148 | 122.9736 | 123.0148 | -123.1293 | -122.9965 | 122.7859 | -0.050354 | 58.4198 | 58.2916
185.1719 | 123.1247 | -58.5526 | 64.4119 | -0.037689 | 0.0014761 | 0.064803 | 0.064773 | 0.00037377 | -0.0016535 | 0.00093559 | -0.0013428 | 0.0013159 | 2.8e-08 | 0.0054004 | -0.0027877 | -0.0021619 | -0.00061526 | -0.20599 | 64.3936 | -58.699 | 64.2197 | -58.4793 | -58.8089 | -58.7952 | -0.3067 | 64.4028 | -58.5938 | -58.6121 | -58.5663 | -58.6761 | -58.3969 | -0.14648 | -0.01831 | -0.19226 | 0.073242 | -0.24262 | -0.25635 | -0.09613 | -0.10986 | -0.041199 | -0.009155 | -123.024 | -0.013733 | 0.15564 | -0.1236 | 0.19684 | -0.082397 | 0.21973 | 122.9187 | 0.027466 | -0.018311 | 123.0927 | 122.9965 | 122.9462 | 122.9553 | -123.111 | -123.0057 | 122.7722 | -0.05951 | 58.3466 | 58.2458
186.1719 | 123.0881 | -58.5892 | 64.4165 | -0.022431 | 0.00083526 | 0.062025 | 0.060927 | 0.00058737 | -0.00058531 | -0.0035504 | 0.047485 | -0.0025293 | 0.004486 | -0.00036738 | -0.0010787 | -0.0021619 | -0.0046741 | -0.15106 | 64.3662 | -58.7036 | 64.2609 | -58.4152 | -58.7677 | -58.7357 | -0.2655 | 64.4165 | -58.5938 | -58.6166 | -58.58 | -58.6807 | -58.4198 | -0.11444 | -0.050354 | -0.15564 | 0.17395 | -0.14649 | -0.17853 | -0.032044 | -0.064087 | -0.004578 | 0 | -123.0331 | 0.009155 | 0.16937 | -0.091553 | 0.17395 | -0.086975 | 0.28839 | 122.9645 | 0.013733 | -0.022888 | 123.0698 | 123.0103 | 122.9553 | 123.0057 | -123.1201 | -123.0103 | 122.85 | -0.027466 | 58.4381 | 58.3237
187.1719 | 123.1018 | -58.58 | 64.4257 | -0.037689 | 0.0010489 | 0.063521 | 0.061996 | -0.00090783 | -0.0010125 | -0.0033368 | 0.029175 | 0.00046135 | 0.0023498 | -0.0018628 | -0.00065151 | -0.00088008 | -0.0023243 | -0.20142 | 64.4119 | -58.7219 | 64.2151 | -58.4793 | -58.8272 | -58.7952 | -0.31128 | 64.4577 | -58.5892 | -58.5022 | -58.6075 | -58.8776 | -58.5892 | -0.14191 | -0.013733 | -0.21057 | 0.10071 | -0.21515 | -0.24719 | -0.073242 | -0.10529 | -0.009155 | 0.032044 | -122.9279 | -0.027466 | -0.009155 | -0.29755 | 0 | -0.28839 | 0.24262 | 122.937 | -0.018311 | 0.086975 | 123.1338 | 123.0469 | 122.9919 | 123.0377 | -123.1476 | -123.0148 | 122.7951 | 0.07782 | 58.3786 | 58.2687
188.1719 | 123.0927 | -58.5663 | 64.4028 | -0.045319 | 0.0014761 | 0.063307 | 0.063064 | 0.0037918 | 5.5488e-05 | -0.0061138 | 0.03833 | 0.0011023 | 0.0023498 | 0.00091422 | 0.00020289 | -0.0019483 | -0.00040166 | -0.20142 | 64.3799 | -58.6807 | 64.2105 | -58.4702 | -58.8089 | -58.7769 | -0.32959 | 64.4348 | -58.6029 | -58.6258 | -58.5846 | -58.6853 | -58.4244 | -0.11444 | -0.022888 | -0.19226 | 0.09613 | -0.21057 | -0.24261 | -0.09613 | -0.12817 | -0.036621 | 0.032043 | -123.0286 | -0.018311 | 0.14191 | -0.11902 | 0.17853 | -0.082398 | 0.21057 | 122.8912 | 0.01831 | -0.022888 | 123.0606 | 123.0377 | 122.9462 | 123.0011 | -123.0835 | -123.0057 | 122.7768 | -0.059509 | 58.3649 | 58.2367
189.1719 | 123.0927 | -58.5754 | 64.4348 | -0.022431 | -1.9142e-05 | 0.064162 | 0.06285 | 0.0020828 | -0.0014399 | -0.0016278 | 0.02002 | -0.00039305 | 0.0023498 | -0.0020764 | -0.0023605 | -0.0013073 | -0.0029651 | -0.16022 | 64.3799 | -58.6761 | 64.2197 | -58.4473 | -58.8181 | -58.7631 | -0.31586 | 64.4257 | -58.5892 | -58.6304 | -58.5892 | -58.6716 | -58.429 | -0.10071 | -0.054931 | -0.21515 | 0.12817 | -0.18768 | -0.24261 | -0.086976 | -0.14191 | -0.013733 | -0.009155 | -123.0652 | -0.013733 | 0.14648 | -0.096131 | 0.16022 | -0.082398 | 0.22888 | 122.8958 | 0 | -0.041199 | 123.056 | 123.0148 | 122.9553 | 123.0011 | -123.111 | -123.024 | 122.7951 | -0.054932 | 58.4152 | 58.2596
190.1719 | 123.1247 | -58.5663 | 64.4302 | -0.014801 | 0.00019446 | 0.064162 | 0.063705 | 0.001442 | -0.0020807 | -0.00055961 | 0.041382 | 0.00088875 | 0.0019226 | 0.0013416 | -0.0015061 | -0.0019483 | -0.0010425 | -0.17395 | 64.3616 | -58.6899 | 64.2517 | -58.4198 | -58.7631 | -58.7448 | -0.29297 | 64.4119 | -58.5754 | -58.6075 | -58.5846 | -58.6761 | -58.4198 | -0.1236 | -0.068665 | -0.17853 | 0.14648 | -0.17853 | -0.19684 | -0.054932 | -0.073243 | -0.009155 | -0.018311 | -123.0377 | -0.018311 | 0.14648 | -0.10986 | 0.15564 | -0.10071 | 0.27008 | 122.9416 | -0.009156 | -0.032044 | 123.0515 | 122.9874 | 122.9279 | 122.9782 | -123.1201 | -123.0057 | 122.818 | -0.041199 | 58.3923 | 58.2733
191.1719 | 123.0652 | -58.5754 | 64.4165 | -0.03006 | 0.00040806 | 0.064375 | 0.062209 | 0.00080117 | -0.00037171 | -0.00055961 | -0.01355 | 0.00088875 | -0.00021357 | 0.002196 | -0.0012925 | -0.0017347 | -0.0029651 | -0.23804 | 64.3707 | -58.7219 | 64.2014 | -58.4793 | -58.8043 | -58.7814 | -0.35248 | 64.4073 | -58.5983 | -58.699 | -58.4198 | -58.5342 | -58.4106 | -0.14648 | -0.045776 | -0.21515 | 0.09613 | -0.20599 | -0.22888 | -0.059509 | -0.082397 | -0.022889 | -0.009155 | -123.1155 | 0.15564 | 0.16479 | 0.041198 | 0.18768 | 0.064087 | 0.24262 | 122.9233 | 0.17853 | -0.10071 | 123.0927 | 123.0057 | 122.9462 | 122.9828 | -123.1384 | -123.0148 | 122.7768 | -0.1236 | 58.3374 | 58.223
192.1719 | 123.2346 | -58.5434 | 64.3799 | -0.083466 | -0.00066014 | 0.063948 | 0.059219 | -0.0017624 | -0.0050715 | 0.00072199 | 0.026123 | -0.0010339 | -0.0012818 | 0.0017688 | -0.00065151 | 0.00061532 | -0.0046741 | -0.17395 | 64.3524 | -58.6899 | 64.2426 | -58.6395 | -58.8455 | -58.6624 | -0.2243 | 64.357 | -58.5663 | -58.5297 | -58.4747 | -58.5617 | -58.2916 | -0.14648 | -0.027466 | -0.13733 | -0.09613 | -0.11902 | -0.30212 | 0.027465 | -0.15564 | -0.022888 | -0.022888 | -122.9095 | 0.068665 | 0.25177 | -0.018311 | 0.27466 | 0.004577 | 0.050354 | 122.9324 | 0.091553 | 0.036621 | 123.0423 | 122.9233 | 122.8958 | 122.9004 | -123.0698 | -122.9462 | 122.7859 | 0.013733 | 58.3694 | 58.3191
193.1719 | 123.0927 | -58.5846 | 64.4257 | -0.098725 | 0.0014761 | 0.064803 | 0.062636 | -0.00026703 | -0.00015811 | -0.0039776 | -0.0013428 | 3.4148e-05 | 0.0029906 | 5.9824e-05 | -0.0021469 | -0.0028027 | -0.0014697 | -0.21515 | 64.3662 | -58.6945 | 64.2288 | -58.4473 | -58.8181 | -58.7585 | -0.36621 | 64.4119 | -58.5846 | -58.6121 | -58.5754 | -58.7173 | -58.4244 | -0.10986 | -0.059509 | -0.19684 | 0.13733 | -0.17395 | -0.23346 | -0.064087 | -0.1236 | 0 | -0.013733 | -123.0377 | 0.009156 | 0.16022 | -0.13275 | 0.16022 | -0.13275 | 0.24719 | 122.9233 | 0.009156 | -0.027466 | 123.0606 | 122.9965 | 122.9507 | 122.9965 | -123.1201 | -123.0103 | 122.8134 | -0.027466 | 58.3694 | 58.2184
194.1719 | 123.0972 | -58.5754 | 64.4257 | -0.03006 | 0.00062166 | 0.064375 | 0.064559 | 0.0027238 | -0.0012261 | -0.0014142 | 0.032227 | -0.00039305 | 0.0014954 | 5.9824e-05 | -0.0012925 | -0.0017347 | -0.0010425 | -0.20599 | 64.357 | -58.6807 | 64.27 | -58.4015 | -58.7631 | -58.7448 | -0.33875 | 64.4119 | -58.5983 | -58.5846 | -58.5709 | -58.6945 | -58.4152 | -0.10529 | -0.068664 | -0.15564 | 0.17395 | -0.16937 | -0.18768 | -0.064087 | -0.082398 | -0.022889 | -0.013733 | -123.0103 | 0.004577 | 0.16022 | -0.11902 | 0.18311 | -0.09613 | 0.27924 | 122.9507 | 0.027466 | 0.013733 | 123.0377 | 123.0103 | 122.9324 | 122.9874 | -123.1064 | -123.024 | 122.8455 | -0.009156 | 58.3694 | 58.2367
195.1719 | 123.0331 | -58.58 | 64.4348 | -0.045319 | -0.0010873 | 0.063094 | 0.063064 | 0.003151 | -0.0020807 | 8.1188e-05 | 0.010864 | -0.00039305 | -0.00021357 | 0.0028368 | 0.00041649 | -0.0010937 | -0.00082886 | -0.2655 | 64.3845 | -58.7082 | 64.2059 | -58.4702 | -58.8272 | -58.7769 | -0.41199 | 64.4165 | -58.5754 | -58.6258 | -58.5526 | -58.4335 | -58.3603 | -0.12817 | -0.050354 | -0.22888 | 0.10986 | -0.19684 | -0.24719 | -0.068664 | -0.11902 | 0.004578 | -0.01831 | -123.0606 | 0.027466 | 0.21973 | 0.14648 | 0.21515 | 0.14191 | 0.23804 | 122.9141 | 0.022888 | -0.050354 | 123.0927 | 122.9919 | 122.9645 | 122.9965 | -123.143 | -123.0103 | 122.7859 | -0.045776 | 58.3145 | 58.168
196.1719 | 123.0789 | -58.5571 | 64.444 | -0.03006 | 0.0019035 | 0.063734 | 0.061355 | -0.0024032 | 0.0015509 | -0.00034601 | -0.0043946 | 0.0021703 | 0.0012818 | -0.001222 | 0.0023391 | -0.0023755 | 2.554e-05 | -0.26093 | 64.3936 | -58.6761 | 64.2105 | -58.4793 | -58.8089 | -58.7997 | -0.41199 | 64.4211 | -58.6258 | -58.6212 | -58.58 | -58.699 | -58.4335 | -0.11902 | -0.050354 | -0.23346 | 0.07782 | -0.24261 | -0.25177 | -0.1236 | -0.13275 | -0.068664 | -0.022888 | -123.0652 | -0.022888 | 0.1236 | -0.14191 | 0.19226 | -0.073243 | 0.19684 | 122.8867 | 0.045776 | 0.004577 | 123.0698 | 123.0469 | 122.9507 | 122.9782 | -123.1201 | -123.0698 | 122.7676 | -0.064087 | 58.2962 | 58.1451
197.1719 | 123.1201 | -58.5754 | 64.4302 | -0.022431 | 0.00083526 | 0.062239 | 0.06285 | 0.00016017 | -0.0020807 | -0.0016278 | 0.0078126 | 0.00067495 | 0.0040588 | -0.001222 | -0.00065151 | -0.0010937 | 0.00045294 | -0.23804 | 64.3799 | -58.6716 | 64.2426 | -58.429 | -58.8089 | -58.7494 | -0.40283 | 64.4348 | -58.5846 | -58.6121 | -58.5663 | -58.6945 | -58.4335 | -0.096131 | -0.050354 | -0.18768 | 0.14648 | -0.17395 | -0.23346 | -0.07782 | -0.13733 | -0.009156 | 0.004577 | -123.0423 | 0.009155 | 0.14191 | -0.11902 | 0.15106 | -0.10986 | 0.24262 | 122.9141 | 0.018311 | -0.027466 | 123.0515 | 123.0194 | 122.9553 | 123.0103 | -123.1018 | -123.0148 | 122.818 | -0.036622 | 58.3374 | 58.1726
198.1719 | 123.1934 | -58.5297 | 64.3982 | -0.052948 | -0.00044654 | 0.06288 | 0.059646 | 0.0012284 | -0.00037171 | -0.0016278 | 0.026123 | 0.00067495 | 0.0014954 | 0.00027342 | -0.0010787 | -0.0015211 | -0.0012561 | -0.23804 | 64.3524 | -58.6853 | 64.3295 | -58.342 | -58.7128 | -58.6716 | -0.3479 | 64.3982 | -58.5938 | -58.5297 | -58.4702 | -58.6029 | -58.3237 | -0.15564 | -0.045776 | -0.068664 | 0.18768 | -0.14191 | -0.18311 | 0.013733 | -0.027466 | -0.064087 | 0 | -122.9279 | 0.059509 | 0.20599 | -0.073242 | 0.27008 | -0.009155 | 0.34332 | 123.0148 | 0.1236 | 0.064087 | 123.0377 | 122.9919 | 122.8821 | 122.9279 | -123.0835 | -122.9919 | 122.8592 | 0 | 58.2916 | 58.1818
199.1719 | 123.23 | -58.5571 | 64.3707 | -0.068207 | -0.0032235 | 0.065016 | 0.061568 | -0.0024032 | 0.00091009 | 0.00072199 | 0.041382 | -0.0014613 | 0.00021363 | -0.0082716 | -0.0015061 | 0.00061532 | -0.0036059 | 0.009155 | 64.4028 | -58.6578 | 64.2929 | -58.3282 | -58.7128 | -58.6807 | -0.3479 | 64.3753 | -58.5663 | -58.5297 | -58.4702 | -58.5846 | -58.3191 | -0.10071 | 0.032043 | -0.07782 | 0.22888 | -0.1236 | -0.15564 | -0.022888 | -0.054932 | -0.009155 | 0.004577 | -122.9004 | 0.086975 | 0.23804 | -0.027466 | 0.24719 | -0.018311 | 0.32959 | 122.9507 | 0.09613 | 0.036621 | 123.0606 | 122.9416 | 122.9599 | 122.9324 | -123.0286 | -122.937 | 122.85 | 0.027466 | 58.5663 | 58.2092
200.1719 | 123.2208 | -58.5388 | 64.4073 | -0.014801 | 0.00019446 | 0.063948 | 0.06285 | -0.00026703 | -0.0010125 | -0.003764 | -0.022705 | 0.0017431 | 0.00064083 | 0.0019824 | -0.00065151 | -0.00066648 | -0.00018806 | -0.24719 | 64.3478 | -58.6624 | 64.2654 | -58.0307 | -58.4335 | -58.8638 | -0.26093 | 64.3662 | -58.5663 | -58.5022 | -58.4564 | -58.5983 | -58.3145 | -0.1236 | -0.05951 | -0.14191 | 0.50812 | -0.32501 | 0.10529 | -0.20142 | 0.22888 | -0.027466 | -0.041199 | -122.9095 | 0.082397 | 0.2243 | -0.05951 | 0.25177 | -0.032044 | 0.63171 | 122.9279 | 0.10986 | 0.064087 | 123.0103 | 122.9324 | 122.8867 | 122.905 | -123.0698 | -122.9736 | 122.8043 | 0.036621 | 58.2916 | 58.2779
201.1719 | 123.1705 | -58.5388 | 64.4073 | -0.045319 | 0.0019035 | 0.066298 | 0.062423 | -5.343e-05 | -0.0016535 | -0.0012006 | 0.02002 | -0.00039305 | -0.0012818 | 0.0019824 | -0.00065151 | -0.0025891 | -0.0033923 | -0.2655 | 64.3341 | -58.6533 | 64.3112 | -58.3557 | -58.7219 | -58.6853 | -0.38452 | 64.3662 | -58.548 | -58.5297 | -58.4839 | -58.58 | -58.3237 | -0.11444 | -0.073243 | -0.096131 | 0.1831 | -0.14648 | -0.18311 | -0.032044 | -0.068665 | -0.009156 | -0.041199 | -122.937 | 0.054931 | 0.21515 | -0.041199 | 0.22431 | -0.032043 | 0.29755 | 122.9645 | 0.064087 | 0.018311 | 122.9874 | 122.9141 | 122.8729 | 122.905 | -123.0606 | -122.9553 | 122.85 | 0.009155 | 58.2733 | 58.1543
202.1719 | 123.2162 | -58.5388 | 64.3936 | -0.098725 | -0.00044654 | 0.064803 | 0.062636 | 0.001442 | 0.00026909 | 0.00072199 | 0.047485 | -0.0016749 | 0.00042723 | -0.00036738 | -1.0706e-05 | -0.00023928 | -0.0014697 | -0.26093 | 64.3341 | -58.6853 | 64.3341 | -58.342 | -58.7128 | -58.6761 | -0.41199 | 64.3936 | -58.5434 | -58.5159 | -58.4747 | -58.5892 | -58.3145 | -0.14648 | -0.05951 | -0.05951 | 0.19684 | -0.13733 | -0.17395 | 0.009156 | -0.027466 | -0.004578 | 0 | -122.9095 | 0.064087 | 0.2243 | -0.050354 | 0.22888 | -0.045776 | 0.34332 | 123.0194 | 0.068665 | 0.027466 | 123.0194 | 122.937 | 122.8729 | 122.9324 | -123.0789 | -122.937 | 122.8729 | 0.022888 | 58.2779 | 58.1268
203.1719 | 123.1888 | -58.5434 | 64.389 | -0.060578 | 0.0023307 | 0.063734 | 0.064773 | 0.0037918 | 0.00048269 | 0.00029479 | 0.047485 | 0.00088875 | -0.0042724 | 0.0017688 | -1.0706e-05 | -0.0023755 | -0.0051013 | -0.28839 | 64.3524 | -58.6487 | 64.2609 | -58.2779 | -58.7677 | -58.699 | -0.44403 | 64.3753 | -58.58 | -58.5022 | -58.461 | -58.5663 | -58.3145 | -0.10529 | -0.036621 | -0.12817 | 0.2655 | -0.15564 | -0.2243 | -0.050354 | -0.11902 | -0.036621 | -0.013733 | -122.8912 | 0.082397 | 0.22888 | -0.022888 | 0.2655 | 0.013733 | 0.37079 | 122.9095 | 0.11902 | 0.07782 | 123.0011 | 122.9553 | 122.8958 | 122.9187 | -123.0377 | -122.9691 | 122.8043 | 0.041199 | 58.255 | 58.0994
204.1719 | 123.1888 | -58.5526 | 64.3982 | -0.045319 | -0.00023294 | 0.06523 | 0.062636 | -0.0013352 | -0.00079891 | -0.0012006 | 0.099365 | 0.0030249 | 0.001709 | -0.0016492 | -0.0015061 | -0.00045288 | -0.0023243 | -0.27924 | 64.3478 | -58.6807 | 64.3158 | -58.3099 | -58.7036 | -58.493 | -0.68665 | 64.3845 | -58.6121 | -58.5114 | -58.4702 | -58.5754 | -58.3145 | -0.12817 | -0.050354 | -0.082397 | 0.24261 | 0.059509 | -0.15106 | 0.18768 | -0.022888 | -0.05951 | -0.013733 | -122.9095 | 0.082397 | 0.23804 | -0.022888 | 0.29755 | 0.036622 | 0.37079 | 122.9965 | 0.14191 | 0.10071 | 123.0286 | 122.9965 | 122.9004 | 122.937 | -123.0789 | -123.0103 | 122.8683 | 0.041198 | 58.2733 | 57.8659
205.1719 | 123.2437 | -58.5617 | 64.389 | -0.11398 | 0.00040806 | 0.062239 | 0.064773 | 0.00016017 | 0.00069649 | 0.0022174 | 0.010864 | 0.00046135 | -0.00042717 | -0.0061352 | -0.0015061 | -0.0019483 | -0.0025379 | -0.29297 | 64.357 | -58.667 | 64.3524 | -58.3008 | -58.6899 | -58.6487 | -0.44403 | 64.3662 | -58.5663 | -58.2962 | -58.6578 | -58.8867 | -58.4747 | -0.10529 | -0.032043 | -0.036621 | 0.26093 | -0.086975 | -0.12817 | 0.01831 | -0.022888 | -0.004577 | -0.022888 | -122.6852 | -0.09613 | 0.086976 | -0.32501 | 0.091553 | -0.32043 | 0.36621 | 123.0194 | -0.091553 | 0.27008 | 123.024 | 122.9324 | 122.9187 | 122.9279 | -123.056 | -122.9553 | 122.9141 | 0.2655 | 58.2687 | 58.1177
206.1719 | 123.2025 | -58.548 | 64.3753 | -0.091095 | 0.00083526 | 0.063307 | 0.063491 | 0.0016556 | -0.0022943 | -0.00055961 | 0.032227 | 0.0011023 | 0.001709 | 0.00048702 | -0.0025741 | -0.00088008 | 0.00088014 | -0.37537 | 64.3204 | -58.6899 | 64.2792 | -58.3923 | -58.754 | -58.7036 | -0.54016 | 64.357 | -58.5892 | -58.5205 | -58.4839 | -58.5938 | -58.3237 | -0.14191 | -0.054931 | -0.09613 | 0.15564 | -0.15564 | -0.20599 | -0.013733 | -0.064087 | -0.041198 | -0.01831 | -122.8958 | 0.064087 | 0.22431 | -0.045776 | 0.2655 | -0.004578 | 0.29755 | 122.9691 | 0.10528 | 0.068664 | 123.0103 | 122.9462 | 122.8683 | 122.905 | -123.0652 | -122.9645 | 122.8271 | 0.027466 | 58.1726 | 58.0078
207.1719 | 123.2117 | -58.5251 | 64.3982 | -0.052948 | 0.0010489 | 0.064589 | 0.060927 | -0.0049668 | 0.0015509 | 0.00029479 | -0.0043946 | -0.00017945 | -0.001709 | -0.005708 | -0.0019333 | -0.0019483 | -0.0042469 | -0.31586 | 64.3478 | -58.6761 | 64.1693 | -58.3374 | -58.6716 | -58.7036 | -0.48981 | 64.3845 | -58.5617 | -58.493 | -58.4473 | -58.5617 | -58.3099 | -0.15106 | -0.050354 | -0.22888 | 0.18768 | -0.17853 | -0.14649 | -0.027466 | 0.004577 | -0.036622 | -0.013733 | -122.8912 | 0.077819 | 0.21515 | -0.036622 | 0.25177 | 0 | 0.33875 | 122.8455 | 0.11444 | 0.068665 | 123.024 | 122.9462 | 122.8729 | 122.9095 | -123.0743 | -122.9599 | 122.6944 | 0.032043 | 58.2092 | 58.0353
208.1719 | 123.1796 | -58.5526 | 64.4211 | -0.022431 | 0.0014761 | 0.066512 | 0.064559 | 0.0027238 | -0.0014399 | -0.0029096 | -0.010498 | 0.00067495 | -0.00021357 | -0.0052808 | 0.00063009 | -0.00045288 | -0.0027515 | -0.33417 | 64.3616 | -58.6945 | 64.3387 | -58.3511 | -58.7265 | -58.6899 | -0.51727 | 64.4165 | -58.5846 | -58.5388 | -58.4976 | -58.5983 | -58.3466 | -0.14191 | -0.05951 | -0.082398 | 0.20142 | -0.13733 | -0.17395 | 0.004578 | -0.032043 | -0.032044 | -0.004578 | -122.9599 | 0.054931 | 0.20599 | -0.045777 | 0.23804 | -0.013733 | 0.34332 | 123.0331 | 0.086975 | 0.045777 | 123.056 | 123.0011 | 122.9141 | 122.9691 | -123.1155 | -123.0057 | 122.8912 | 0.013733 | 58.2184 | 58.0353
209.1719 | 123.175 | -58.5434 | 64.4119 | -0.037689 | 0.00040806 | 0.06523 | 0.061355 | -0.0034714 | 0.00048269 | -0.0022686 | -0.0043946 | -0.00039305 | -0.0010682 | 0.0030506 | -0.00022431 | -0.0010937 | 0.00066654 | -0.32501 | 64.3662 | -58.667 | 64.3341 | -58.3649 | -58.7357 | -58.6853 | -0.53101 | 64.3662 | -58.5663 | -58.5159 | -58.4793 | -58.58 | -58.3282 | -0.1236 | -0.045776 | -0.07782 | 0.17853 | -0.14191 | -0.19226 | -0.018311 | -0.068665 | -0.022888 | -0.045776 | -122.9279 | 0.064087 | 0.21515 | -0.036621 | 0.23804 | -0.013733 | 0.30212 | 123.0011 | 0.086975 | 0.050354 | 123.0331 | 122.9324 | 122.9095 | 122.9095 | -123.0789 | -122.9782 | 122.8775 | 0.027466 | 58.2184 | 58.0124
210.1719 | 123.2208 | -58.5022 | 64.3936 | -0.083466 | -0.0010873 | 0.063307 | 0.060927 | 0.0018692 | 0.0011237 | -0.0022686 | 0.032227 | 0.00067495 | -0.0010682 | -0.0037854 | -0.0021469 | -0.0028027 | 0.0023755 | -0.34332 | 64.325 | -58.6578 | 64.3387 | -58.3008 | -58.7036 | -58.6533 | -0.50354 | 64.3707 | -58.58 | -58.5022 | -58.4427 | -58.5617 | -58.2962 | -0.15564 | -0.068665 | -0.054932 | 0.20142 | -0.15106 | -0.20142 | 0.004578 | -0.045776 | -0.07782 | -0.022888 | -122.8958 | 0.059509 | 0.20599 | -0.05951 | 0.28381 | 0.01831 | 0.35706 | 122.9965 | 0.13733 | 0.07782 | 122.9828 | 122.9507 | 122.8271 | 122.8729 | -123.0515 | -122.9736 | 122.8409 | 0 | 58.1589 | 57.9987
211.1719 | 123.2574 | -58.5251 | 64.3982 | -0.03006 | 0.0010489 | 0.063094 | 0.063491 | -0.00026703 | 0.00026909 | -0.002055 | 0.026123 | 0.00046135 | -0.00064077 | -0.0054944 | -0.0015061 | 0.0012561 | 0.0015209 | -0.37994 | 64.3433 | -58.6761 | 64.325 | -58.3328 | -58.699 | -58.6578 | -0.54932 | 64.389 | -58.5617 | -58.4839 | -58.4381 | -58.5526 | -58.2916 | -0.15106 | -0.054931 | -0.073242 | 0.19226 | -0.13275 | -0.17395 | 0.01831 | -0.022889 | -0.036622 | -0.009155 | -122.8821 | 0.086975 | 0.23346 | -0.027466 | 0.27008 | 0.009156 | 0.34332 | 123.0011 | 0.1236 | 0.07782 | 123.0194 | 122.9507 | 122.8683 | 122.9141 | -123.0743 | -122.9599 | 122.85 | 0.041198 | 58.1451 | 57.9758
212.1719 | 123.1842 | -58.5297 | 64.3982 | -0.098725 | -0.0010873 | 0.063948 | 0.06285 | -0.00026703 | -0.0012261 | 0.00050839 | 0.0047608 | -0.0018885 | -0.00021357 | -0.00036738 | -0.0032151 | -0.00066648 | -0.0014697 | -0.41199 | 64.3524 | -58.667 | 64.3066 | -58.3511 | -58.7357 | -58.6716 | -0.59052 | 64.3799 | -58.5663 | -58.493 | -58.4518 | -58.5571 | -58.287 | -0.13733 | -0.045776 | -0.091552 | 0.17853 | -0.14191 | -0.20599 | -0.004578 | -0.068665 | -0.036621 | -0.01831 | -122.8912 | 0.07782 | 0.24262 | -0.027466 | 0.27924 | 0.009155 | 0.31586 | 122.9736 | 0.11444 | 0.073242 | 123.0194 | 122.9462 | 122.8821 | 122.9095 | -123.0652 | -122.9645 | 122.8363 | 0.036621 | 58.1177 | 57.9391
213.1719 | 123.1842 | -58.5342 | 64.389 | -0.10635 | 0.00062166 | 0.06288 | 0.063491 | -0.0015488 | 0.00069649 | 0.00050839 | 0.02002 | 0.00046135 | -0.001709 | -0.0044262 | -0.0017197 | -0.00023928 | 0.00045294 | -0.48065 | 64.3341 | -58.7082 | 64.2471 | -58.4335 | -58.7952 | -58.7311 | -0.72327 | 64.3753 | -58.5983 | -58.5342 | -58.5114 | -58.6166 | -58.3374 | -0.17395 | -0.054932 | -0.14191 | 0.10071 | -0.19684 | -0.26093 | -0.022888 | -0.086975 | -0.064087 | -0.013733 | -122.9233 | 0.022888 | 0.19684 | -0.082397 | 0.26093 | -0.01831 | 0.27466 | 122.9553 | 0.086975 | 0.064087 | 123.0423 | 122.9736 | 122.8683 | 122.9095 | -123.0972 | -122.9874 | 122.7814 | 0 | 58.0536 | 57.811
214.1719 | 123.2391 | -58.5114 | 64.3845 | -0.052948 | 0.0010489 | 0.06288 | 0.061141 | 0.0018692 | -0.00058531 | 0.00072199 | -0.0013428 | 3.4148e-05 | -0.001709 | 0.00048702 | 0.00063009 | -2.5678e-05 | -0.00082886 | -0.39368 | 64.3387 | -58.6487 | 64.3478 | -58.3099 | -58.6899 | -58.6533 | -0.59052 | 64.3707 | -58.5663 | -58.5022 | -58.4335 | -58.5526 | -58.2916 | -0.13733 | -0.045776 | -0.036621 | 0.20142 | -0.14191 | -0.17853 | -0.004577 | -0.041198 | -0.054931 | -0.013732 | -122.8867 | 0.07782 | 0.21973 | -0.041198 | 0.27466 | 0.013733 | 0.33875 | 122.9965 | 0.13275 | 0.064087 | 122.9874 | 122.937 | 122.85 | 122.8821 | -123.0331 | -122.9507 | 122.8592 | 0.009156 | 58.1177 | 57.9208
215.1719 | 123.2117 | -58.5388 | 64.3982 | -0.083466 | -0.0013009 | 0.063521 | 0.063277 | -0.003685 | 0.0011237 | -0.00055961 | 0.032227 | 0.0015295 | -0.00064077 | 0.0017688 | -0.00043791 | -0.0015211 | -0.0021107 | -0.4303 | 64.3478 | -58.6945 | 64.3158 | -58.3099 | -58.6899 | -58.6624 | -0.63629 | 64.3799 | -58.5892 | -58.4793 | -58.4244 | -58.5297 | -58.287 | -0.15564 | -0.050354 | -0.082397 | 0.22888 | -0.1236 | -0.15106 | 0.032043 | 0.004578 | -0.050354 | -0.01831 | -122.8775 | 0.11444 | 0.25177 | 0.009155 | 0.30212 | 0.059509 | 0.38452 | 123.0103 | 0.16479 | 0.10986 | 123.0423 | 122.9691 | 122.8867 | 122.9187 | -123.0927 | -122.9874 | 122.8546 | 0.059509 | 58.1085 | 57.9025
216.1719 | 123.2483 | -58.5526 | 64.3845 | 0.00045798 | -0.0023691 | 0.066725 | 0.063491 | 0.00058737 | -0.0014399 | -0.0022686 | 0.0078126 | -0.0035975 | 0.0014954 | -0.0052808 | 0.0016983 | 0.00082892 | -0.0023243 | -0.40741 | 64.3387 | -58.6304 | 64.3433 | -58.3237 | -58.6945 | -58.6716 | -0.34332 | 64.4485 | -58.5251 | -58.5342 | -58.4518 | -58.5434 | -58.3282 | -0.07782 | -0.045776 | -0.041198 | 0.22888 | -0.11902 | -0.14191 | -0.041199 | -0.064087 | 0.027466 | 0.064087 | -122.9187 | 0.10071 | 0.2243 | 0.009155 | 0.19684 | -0.018311 | 0.3067 | 122.9736 | 0.073242 | -0.009156 | 122.9691 | 122.9736 | 122.8912 | 123.0011 | -123.0148 | -122.9095 | 122.8958 | 0.01831 | 58.1451 | 58.2092
217.1719 | 123.175 | -58.5297 | 64.3707 | -0.075836 | 0.0033987 | 0.063094 | 0.062636 | -0.0032578 | -0.0027215 | -0.00034601 | -0.0013428 | 0.0021703 | 0.00021363 | -0.0018628 | -0.0019333 | -0.0010937 | -0.010228 | -0.43488 | 64.3524 | -58.6533 | 64.3616 | -58.2962 | -58.667 | -58.6487 | -0.68207 | 64.3707 | -58.5617 | -58.5297 | -58.1451 | -58.5846 | -58.4473 | -0.1236 | -0.018311 | -0.009156 | 0.23346 | -0.11902 | -0.13733 | 0.004577 | -0.013733 | -0.032044 | 0 | -122.9004 | 0.38452 | 0.082397 | -0.054932 | 0.11444 | -0.022888 | 0.35705 | 123.0148 | 0.41656 | 0.032044 | 123.0057 | 122.9324 | 122.8821 | 122.9004 | -123.024 | -122.9324 | 122.8912 | 0 | 58.0948 | 57.8476
218.1719 | 123.2162 | -58.5526 | 64.3524 | -0.03006 | -0.00066014 | 0.063521 | 0.062423 | 0.00016017 | -0.00037171 | 0.00093559 | 0.032227 | -0.00060665 | 0.00064083 | -0.0018628 | 0.00020289 | -0.0032301 | -0.0029651 | -0.54474 | 64.3158 | -58.699 | 64.2929 | -58.3923 | -58.754 | -58.6899 | -0.80109 | 64.3845 | -58.58 | -58.5205 | -58.4747 | -58.5846 | -58.3099 | -0.14648 | -0.036621 | -0.059509 | 0.16022 | -0.13733 | -0.20142 | 0.009156 | -0.054931 | -0.027466 | 0.032043 | -122.8729 | 0.07782 | 0.24261 | -0.032044 | 0.27008 | -0.004578 | 0.3067 | 122.9919 | 0.10529 | 0.059509 | 123.0148 | 122.9645 | 122.8683 | 122.937 | -123.0515 | -122.9324 | 122.8455 | 0.032043 | 58.0078 | 57.7515
219.1719 | 123.2208 | -58.5068 | 64.3662 | -0.068207 | 0.00083526 | 0.063948 | 0.061782 | -0.0011214 | 0.00091009 | 0.00029479 | 0.001709 | -0.00017945 | -0.0019226 | -0.002931 | 0.00084389 | -0.0015211 | -0.0014697 | -0.49896 | 64.3295 | -58.6761 | 64.3158 | -58.3282 | -58.7173 | -58.6578 | -0.71869 | 64.3707 | -58.5709 | -58.4839 | -58.4335 | -58.5388 | -58.3008 | -0.16937 | -0.036621 | -0.050354 | 0.17853 | -0.15106 | -0.21057 | 0.01831 | -0.041199 | -0.064087 | 0.004578 | -122.85 | 0.073242 | 0.20599 | -0.032043 | 0.27008 | 0.032044 | 0.3479 | 122.9919 | 0.13733 | 0.086975 | 123.0057 | 122.9416 | 122.8363 | 122.8775 | -123.0423 | -122.937 | 122.8226 | 0.022888 | 58.0078 | 57.7881
220.1719 | 123.175 | -58.5709 | 64.3845 | -0.10635 | 0.0010489 | 0.065016 | 0.063918 | 0.00037377 | 0.00069649 | 0.00050839 | 0.023071 | 0.00024775 | 0.0025634 | 0.0030506 | -0.00086511 | -0.00066648 | -0.0021107 | -0.5722 | 64.357 | -58.6853 | 64.27 | -58.4061 | -58.7769 | -58.7173 | -0.90179 | 64.3799 | -58.5754 | -58.548 | -58.5114 | -58.6029 | -58.342 | -0.11444 | -0.027465 | -0.11444 | 0.16479 | -0.14648 | -0.20599 | -0.032043 | -0.091552 | -0.004577 | -0.004577 | -122.9324 | 0.059509 | 0.22888 | -0.032043 | 0.23346 | -0.027466 | 0.27924 | 122.9553 | 0.064086 | 0.027465 | 123.0423 | 122.9553 | 122.9279 | 122.9507 | -123.0698 | -122.9599 | 122.8409 | 0.022888 | 57.9987 | 57.6691
221.1719 | 123.1842 | -58.5342 | 64.3799 | -0.068207 | 0.0023307 | 0.063521 | 0.06285 | -0.001976 | -0.0010125 | 0.00093559 | -0.0043946 | -0.0010339 | 0.0014954 | -0.0052808 | -0.00022431 | -0.00045288 | 0.00045294 | -0.56305 | 64.357 | -58.6899 | 64.2334 | -58.429 | -58.786 | -58.7357 | -0.90637 | 64.3707 | -58.548 | -58.5388 | -58.5205 | -58.6349 | -58.3511 | -0.15564 | -0.022888 | -0.14649 | 0.10529 | -0.20142 | -0.25177 | -0.045777 | -0.096131 | -0.013733 | -0.009155 | -122.9187 | 0.013733 | 0.18311 | -0.10071 | 0.19684 | -0.086975 | 0.26093 | 122.9233 | 0.027466 | 0.009156 | 123.0469 | 122.9187 | 122.8912 | 122.905 | -123.0698 | -122.9279 | 122.7676 | -0.004577 | 57.9712 | 57.6279
222.1719 | 123.2208 | -58.5617 | 64.3799 | -0.12924 | -0.00023294 | 0.064375 | 0.061568 | -0.00090783 | -0.0010125 | -0.00013241 | -0.0013428 | 0.00046135 | 0.00064083 | -0.0010084 | -0.0012925 | -0.0021619 | 0.0013073 | -0.59052 | 64.3433 | -58.6945 | 64.2792 | -58.3969 | -58.7631 | -58.7128 | -0.89722 | 64.389 | -58.5938 | -58.5251 | -58.4885 | -58.5892 | -58.3145 | -0.13275 | -0.036621 | -0.10071 | 0.16479 | -0.15106 | -0.20142 | -0.018311 | -0.068665 | -0.032043 | 0.009155 | -122.905 | 0.073243 | 0.24719 | -0.027465 | 0.27924 | 0.004578 | 0.29755 | 122.9736 | 0.10529 | 0.068665 | 123.0377 | 122.9828 | 122.905 | 122.9507 | -123.0743 | -122.9736 | 122.8409 | 0.036622 | 57.9712 | 57.6645
223.1719 | 123.1842 | -58.5388 | 64.389 | -0.045319 | -0.00066014 | 0.064162 | 0.062636 | -0.0013352 | -0.00037171 | -0.00055961 | 0.0047608 | 0.00067495 | 0.0019226 | 0.0054004 | -0.0012925 | -0.00045288 | 0.0017345 | -0.62256 | 64.3387 | -58.7082 | 64.2654 | -58.4106 | -58.786 | -58.7082 | -0.9613 | 64.3662 | -58.5846 | -58.5388 | -58.5022 | -58.5846 | -58.3191 | -0.16937 | -0.050354 | -0.1236 | 0.12817 | -0.16937 | -0.24719 | 0 | -0.07782 | -0.045777 | -0.022888 | -122.9279 | 0.036621 | 0.21973 | -0.045777 | 0.2655 | 0 | 0.29755 | 122.9736 | 0.082398 | 0.045777 | 123.0469 | 122.9507 | 122.8775 | 122.905 | -123.0972 | -122.9736 | 122.8043 | 0 | 57.9163 | 57.5775
224.1719 | 123.2162 | -58.5388 | 64.3478 | -0.098725 | 0.00062166 | 0.063948 | 0.062209 | -0.0015488 | -0.00015811 | -0.0022686 | -0.0043946 | 0.00046135 | 2.8e-08 | 0.001128 | -0.00086511 | 0.00040152 | -0.0021107 | -0.65918 | 64.3295 | -58.6853 | 64.2471 | -58.4198 | -58.7997 | -58.7357 | -1.0071 | 64.3936 | -58.5983 | -58.5342 | -58.5022 | -58.6304 | -58.3511 | -0.14648 | -0.01831 | -0.10071 | 0.11902 | -0.19684 | -0.26093 | -0.050354 | -0.11444 | -0.05951 | 0.045777 | -122.8821 | 0.036621 | 0.18768 | -0.091553 | 0.24719 | -0.032043 | 0.2655 | 122.9324 | 0.096131 | 0.064087 | 123.0148 | 122.9919 | 122.8683 | 122.9324 | -123.0331 | -122.9462 | 122.7859 | 0.004577 | 57.8796 | 57.5317
225.1719 | 123.175 | -58.5571 | 64.3662 | -0.075836 | -1.9142e-05 | 0.064589 | 0.063064 | -0.00090783 | -0.0010125 | -0.00013241 | -0.0013428 | -0.00017945 | 0.00064083 | 0.002196 | -0.00022431 | -0.0015211 | 0.00023934 | -0.65918 | 64.325 | -58.699 | 64.2883 | -58.4976 | -58.8547 | -58.7677 | -1.03 | 64.3616 | -58.5709 | -58.5663 | -58.5251 | -58.6166 | -58.342 | -0.14191 | -0.041199 | -0.07782 | 0.059509 | -0.21057 | -0.29755 | -0.068664 | -0.15564 | -0.013733 | -0.004578 | -122.9324 | 0.032044 | 0.21515 | -0.059509 | 0.22888 | -0.045776 | 0.20142 | 122.9874 | 0.045777 | 0.004578 | 123.024 | 122.9324 | 122.8821 | 122.9187 | -123.0652 | -122.937 | 122.8455 | -0.009155 | 57.8979 | 57.5272
226.1719 | 123.1705 | -58.548 | 64.3433 | -0.083466 | -0.00044654 | 0.063734 | 0.065627 | -0.00069423 | 0.0013373 | 0.00093559 | -0.025757 | 0.0021703 | 0.0012818 | 5.9824e-05 | -0.0021469 | -0.0019483 | -0.00018806 | -0.68207 | 64.3295 | -58.6899 | 64.2517 | -58.4198 | -58.8043 | -58.7357 | -0.91553 | 64.4073 | -58.5892 | -58.5663 | -58.5068 | -58.6533 | -58.3694 | -0.14191 | -0.013733 | -0.091553 | 0.12817 | -0.18768 | -0.25635 | -0.045777 | -0.11444 | -0.041198 | 0.064087 | -122.9095 | 0.041199 | 0.17853 | -0.10528 | 0.21973 | -0.064087 | 0.27008 | 122.9416 | 0.082397 | 0.022888 | 123.0194 | 122.9965 | 122.8775 | 122.9553 | -123.0331 | -122.9324 | 122.7997 | -0.01831 | 57.8659 | 57.6324
227.1719 | 123.1613 | -58.5571 | 64.3662 | -0.03006 | -0.00044654 | 0.06523 | 0.063491 | 0.00080117 | -0.00079891 | -0.00098701 | -0.053223 | 0.00067495 | 0.00085443 | 0.00091422 | -0.00065151 | 0.00040152 | 0.0030163 | -0.6958 | 64.3112 | -58.6945 | 64.2746 | -58.3832 | -58.8043 | -58.7357 | -1.0803 | 64.3616 | -58.5983 | -58.5388 | -58.5434 | -58.6349 | -58.3694 | -0.13733 | -0.054932 | -0.091553 | 0.17395 | -0.17853 | -0.24719 | -0.041199 | -0.10986 | -0.041199 | -0.004578 | -122.905 | 0.013733 | 0.18768 | -0.07782 | 0.22888 | -0.036621 | 0.31128 | 122.9691 | 0.054932 | 0.05951 | 123.0057 | 122.9599 | 122.8683 | 122.9187 | -123.0606 | -122.9645 | 122.8317 | 0.018311 | 57.8613 | 57.4768
228.1719 | 123.1522 | -58.5754 | 64.3478 | -0.052948 | 0.0025443 | 0.066725 | 0.06285 | 0.0022964 | -0.00037171 | 0.0020038 | -0.016602 | 0.00088875 | -0.0025636 | 0.00091422 | 0.00084389 | -0.00045288 | 0.0030163 | -0.72327 | 64.3341 | -58.7036 | 64.2288 | -58.429 | -58.7906 | -58.7357 | -1.1353 | 64.3845 | -58.6121 | -58.5617 | -58.5251 | -58.6349 | -58.3603 | -0.12817 | -0.013733 | -0.11902 | 0.14648 | -0.16022 | -0.21515 | -0.032044 | -0.086975 | -0.036622 | 0.036621 | -122.9095 | 0.050354 | 0.21515 | -0.05951 | 0.25177 | -0.022888 | 0.27466 | 122.9324 | 0.086976 | 0.050354 | 123.0377 | 122.9965 | 122.9095 | 122.9599 | -123.0515 | -122.9599 | 122.8043 | 0.013732 | 57.8522 | 57.4402
229.1719 | 123.2071 | -58.5754 | 64.357 | -0.083466 | 0.0021171 | 0.064162 | 0.062209 | -0.0011214 | -0.0012261 | -0.00077341 | 0.001709 | 0.0013159 | -0.0012818 | -0.00079478 | -0.00086511 | -0.0025891 | 0.0040845 | -0.70953 | 64.3662 | -58.6899 | 64.2746 | -58.3969 | -58.7631 | -58.6853 | -1.0986 | 64.3936 | -58.5892 | -58.5114 | -58.4656 | -58.5754 | -58.3191 | -0.11444 | 0.009155 | -0.082398 | 0.17853 | -0.10986 | -0.18768 | 0.004577 | -0.073243 | -0.013733 | 0.036621 | -122.8683 | 0.10986 | 0.25635 | 0 | 0.27008 | 0.013733 | 0.29297 | 122.9645 | 0.1236 | 0.077819 | 123.056 | 122.9828 | 122.9416 | 122.9691 | -123.0469 | -122.9462 | 122.85 | 0.064086 | 57.8659 | 57.4768
230.1719 | 123.1476 | -58.5251 | 64.3662 | -0.11398 | 0.0010489 | 0.064375 | 0.060714 | -0.00026703 | 0.0013373 | -0.0014142 | -0.010498 | -0.0016749 | 0.00021363 | -0.0067762 | -0.0015061 | -0.00088008 | 0.00088014 | -0.76446 | 64.3295 | -58.6853 | 64.2471 | -58.429 | -58.7906 | -58.7494 | -1.1856 | 64.357 | -58.5938 | -58.4747 | -58.4061 | -58.7128 | -58.4106 | -0.16022 | -0.036621 | -0.11902 | 0.09613 | -0.22431 | -0.2655 | -0.064087 | -0.10529 | -0.068665 | -0.009155 | -122.8409 | 0.11902 | 0.11444 | -0.18768 | 0.1831 | -0.11902 | 0.25635 | 122.9324 | 0.18768 | 0.11902 | 123.0148 | 122.9507 | 122.8546 | 122.8821 | -123.0515 | -122.9599 | 122.7722 | 0.050354 | 57.7606 | 57.3395
231.1719 | 123.1476 | -58.5434 | 64.3707 | -0.12161 | 0.00019446 | 0.065443 | 0.063705 | -0.0030442 | 5.5488e-05 | 0.00050839 | -0.044067 | -0.00082025 | -0.0014954 | 0.003905 | -0.00022431 | 0.00018792 | -0.0018971 | -0.77362 | 64.3616 | -58.699 | 64.2426 | -58.4244 | -58.8043 | -58.7448 | -1.2085 | 64.3707 | -58.5846 | -58.5434 | -58.5251 | -58.6578 | -58.3649 | -0.15564 | -0.009156 | -0.12817 | 0.11902 | -0.20142 | -0.26093 | -0.045776 | -0.10529 | -0.041199 | 0 | -122.9141 | 0.018311 | 0.17853 | -0.11444 | 0.21973 | -0.073242 | 0.27466 | 122.9416 | 0.05951 | 0.041199 | 123.0606 | 122.9553 | 122.905 | 122.9141 | -123.0698 | -122.9553 | 122.7859 | 0 | 57.7698 | 57.3349
232.1719 | 123.1567 | -58.5709 | 64.3753 | -0.10635 | -0.00044654 | 0.063948 | 0.063705 | 0.00037377 | 0.00091009 | 8.1188e-05 | -0.016602 | -0.0010339 | -0.00021357 | -0.003999 | -0.0012925 | -0.00066648 | 0.0023755 | -0.78735 | 64.3341 | -58.699 | 64.2609 | -58.4198 | -58.8089 | -58.7402 | -1.236 | 64.3662 | -58.5983 | -58.5754 | -58.548 | -58.6258 | -58.3557 | -0.12817 | -0.041199 | -0.11444 | 0.15106 | -0.16937 | -0.23804 | -0.041198 | -0.10986 | -0.027466 | -0.009155 | -122.9507 | 0.022888 | 0.21515 | -0.054931 | 0.24262 | -0.027465 | 0.27924 | 122.9599 | 0.050354 | 0.022889 | 123.0331 | 122.9645 | 122.905 | 122.937 | -123.0743 | -122.9736 | 122.8317 | -0.004577 | 57.7835 | 57.3349
233.1719 | 123.2025 | -58.5114 | 64.389 | -0.12924 | -0.00023294 | 0.061598 | 0.06285 | -0.0062484 | 0.00026909 | -0.00055961 | -0.016602 | 0.00024775 | -0.00085457 | -0.00464 | 0.0010575 | -0.0030163 | -0.00018806 | -0.72784 | 64.3616 | -58.6761 | 64.3112 | -58.3511 | -58.7128 | -58.6716 | -1.1307 | 64.3799 | -58.5526 | -58.4793 | -58.429 | -58.5297 | -58.2825 | -0.16479 | -0.027466 | -0.07782 | 0.16022 | -0.16022 | -0.20142 | 0.004577 | -0.036622 | -0.041198 | -0.009155 | -122.8683 | 0.082398 | 0.22888 | -0.01831 | 0.27008 | 0.022888 | 0.32501 | 122.9874 | 0.1236 | 0.073242 | 123.0377 | 122.9324 | 122.8729 | 122.8912 | -123.0652 | -122.9416 | 122.8226 | 0.032044 | 57.7835 | 57.3807
234.1719 | 123.2025 | -58.548 | 64.3662 | -0.11398 | 0.00040806 | 0.065016 | 0.061782 | 0.00016017 | 0.00069649 | 0.00093559 | -0.03186 | -0.0014613 | -0.00042717 | 0.0028368 | -0.00022431 | 0.00018792 | 0.00066654 | -0.8194 | 64.2975 | -58.6761 | 64.2838 | -58.4015 | -58.7769 | -58.7265 | -1.268 | 64.3799 | -58.58 | -58.5251 | -58.5342 | -58.6441 | -58.3466 | -0.12817 | -0.068665 | -0.082398 | 0.14649 | -0.17853 | -0.22888 | -0.050354 | -0.10071 | -0.032043 | 0.013733 | -122.8912 | 0.013733 | 0.20142 | -0.09613 | 0.23346 | -0.064087 | 0.27466 | 122.9599 | 0.045776 | 0.054932 | 122.9736 | 122.9599 | 122.8455 | 122.9279 | -123.0423 | -122.9462 | 122.8317 | 0.022889 | 57.7286 | 57.28
235.1719 | 123.1613 | -58.5434 | 64.3982 | -0.083466 | 0.0012625 | 0.064803 | 0.063918 | -5.343e-05 | 0.0021917 | 8.1188e-05 | 0.11768 | -0.0014613 | -0.00064077 | 0.0030506 | -0.0017197 | 0.00018792 | -0.00061526 | -0.84228 | 64.325 | -58.6853 | 64.27 | -58.4244 | -58.786 | -58.7219 | -1.3687 | 64.3845 | -58.5617 | -58.5388 | -58.5434 | -58.6441 | -58.3557 | -0.14191 | -0.073242 | -0.12817 | 0.11902 | -0.17853 | -0.24262 | -0.036621 | -0.10071 | -0.018311 | -0.013733 | -122.937 | 0 | 0.18768 | -0.10071 | 0.20599 | -0.082397 | 0.26093 | 122.9553 | 0.018311 | 0.022889 | 123.0103 | 122.9462 | 122.8683 | 122.9279 | -123.0835 | -122.9599 | 122.8134 | 0.004578 | 57.7011 | 57.1747
236.1719 | 123.1705 | -58.58 | 64.3845 | -0.098725 | -0.00066014 | 0.065016 | 0.065414 | -0.0045394 | 0.0013373 | -0.0022686 | -0.034912 | -0.00060665 | -0.0012818 | -0.0018628 | -0.00022431 | -0.0015211 | -0.0023243 | -0.84228 | 64.3295 | -58.6853 | 64.2654 | -58.3923 | -58.8043 | -58.7357 | -1.3321 | 64.3433 | -58.5892 | -58.5388 | -58.5159 | -58.6349 | -58.3511 | -0.10529 | -0.054931 | -0.11902 | 0.18768 | -0.15564 | -0.2243 | -0.050354 | -0.11902 | -0.009155 | -0.041198 | -122.9233 | 0.064087 | 0.22888 | -0.054932 | 0.23804 | -0.045777 | 0.29297 | 122.9507 | 0.073242 | 0.050354 | 123.0148 | 122.9324 | 122.9095 | 122.9233 | -123.0698 | -122.9736 | 122.8455 | 0.041199 | 57.7377 | 57.2479
237.1719 | 123.143 | -58.58 | 64.3799 | -0.060578 | 0.00083526 | 0.066298 | 0.064559 | 0.00486 | -0.0014399 | -0.002055 | -0.03186 | 3.4148e-05 | 0.00021363 | -0.003999 | -0.0023605 | -0.0036573 | -0.0018971 | -0.88806 | 64.3204 | -58.699 | 64.2471 | -58.4198 | -58.8181 | -58.7448 | -1.3962 | 64.3936 | -58.58 | -58.5617 | -58.5297 | -58.6304 | -58.3649 | -0.11902 | -0.059509 | -0.13275 | 0.16022 | -0.1648 | -0.23804 | -0.045776 | -0.11902 | 0 | 0.013733 | -122.9416 | 0.050354 | 0.21515 | -0.050354 | 0.21515 | -0.050354 | 0.27924 | 122.9462 | 0.050354 | 0.01831 | 123.0194 | 122.9736 | 122.9004 | 122.9736 | -123.0789 | -122.9599 | 122.8271 | 0.01831 | 57.692 | 57.1838
238.1719 | 123.1567 | -58.5434 | 64.3799 | -0.014801 | 0.00083526 | 0.062666 | 0.064986 | -0.0028304 | 5.5488e-05 | 0.00050839 | -0.14478 | 0.00024775 | -0.0010682 | -0.00036738 | -0.0017197 | -0.0010937 | -0.00018806 | -0.78278 | 64.3341 | -58.667 | 64.3478 | -58.3557 | -58.287 | -58.4381 | -1.3184 | 64.3524 | -58.58 | -58.4885 | -58.4335 | -58.5754 | -58.2962 | -0.1236 | -0.045777 | -0.032044 | 0.18768 | 0.10529 | 0.25635 | 0.22888 | 0.37994 | -0.036621 | -0.027466 | -122.8683 | 0.10986 | 0.24719 | -0.032043 | 0.28381 | 0.004578 | 0.31128 | 123.0148 | 0.14648 | 0.091553 | 123.0011 | 122.9324 | 122.8775 | 122.8958 | -123.0469 | -122.9599 | 122.8912 | 0.054932 | 57.7606 | 57.225
239.1719 | 123.1659 | -58.5754 | 64.3662 | -0.10635 | 0.00062166 | 0.065443 | 0.064986 | -0.0011214 | -0.00058531 | 0.002431 | -0.028809 | 0.0021703 | 0.00085443 | -0.0018628 | 0.00084389 | 0.00040152 | -0.0027515 | -0.89264 | 64.3066 | -58.6853 | 64.2838 | -58.3878 | -58.7952 | -58.7265 | -1.387 | 64.3707 | -58.5892 | -58.5205 | -58.5388 | -58.6441 | -58.3603 | -0.10986 | -0.059509 | -0.082398 | 0.18768 | -0.15106 | -0.21973 | -0.041198 | -0.10986 | -0.013733 | 0.004578 | -122.8867 | 0.036621 | 0.21515 | -0.068665 | 0.22888 | -0.054932 | 0.29755 | 122.9691 | 0.050354 | 0.068664 | 122.9919 | 122.9599 | 122.8821 | 122.9462 | -123.0515 | -122.9553 | 122.8592 | 0.054931 | 57.6828 | 57.1884
240.1719 | 123.1888 | -58.5663 | 64.3707 | -0.12161 | -0.0015145 | 0.064375 | 0.063705 | 0.001442 | -0.00015811 | -0.0012006 | -0.03186 | 0.0013159 | -0.0014954 | 0.0036914 | 0.0012711 | -0.0023755 | 2.554e-05 | -0.90637 | 64.3021 | -58.7036 | 64.2929 | -58.3557 | -58.7631 | -58.7082 | -1.4236 | 64.357 | -58.5846 | -58.4885 | -58.5159 | -58.6441 | -58.3328 | -0.13733 | -0.068665 | -0.07782 | 0.21057 | -0.14191 | -0.19684 | -0.004578 | -0.05951 | -0.018311 | -0.013733 | -122.8592 | 0.050354 | 0.23346 | -0.07782 | 0.25177 | -0.059509 | 0.3479 | 122.9965 | 0.068665 | 0.096131 | 123.0057 | 122.9416 | 122.8683 | 122.9233 | -123.0743 | -122.9553 | 122.8592 | 0.07782 | 57.6599 | 57.1426
241.1719 | 123.1522 | -58.5709 | 64.4028 | -0.083466 | 0.00019446 | 0.065443 | 0.065627 | 0.0016556 | -0.00079891 | 0.001363 | -0.086792 | 0.00024775 | -0.00085457 | 0.0017688 | -0.0017197 | -0.00066648 | 0.00088014 | -0.97961 | 64.3204 | -58.7357 | 64.2059 | -58.4747 | -58.8821 | -58.8043 | -1.5427 | 64.3982 | -58.6121 | -58.5434 | -58.5571 | -58.6945 | -58.3603 | -0.1648 | -0.082397 | -0.19684 | 0.096131 | -0.23346 | -0.31128 | -0.068664 | -0.14648 | -0.041199 | -0.004578 | -122.9462 | 0.013733 | 0.21057 | -0.1236 | 0.25177 | -0.082397 | 0.26093 | 122.9416 | 0.054932 | 0.068665 | 123.056 | 123.0103 | 122.8912 | 122.9691 | -123.1384 | -123.0148 | 122.7768 | 0.027466 | 57.5912 | 57.0282
242.1719 | 123.2162 | -58.5434 | 64.3295 | -0.060578 | 0.0016899 | 0.065016 | 0.0652 | 0.00080117 | -0.00037171 | -0.0012006 | -0.044067 | 0.0011023 | 0.0012818 | 0.0024096 | 0.0014847 | 0.0012561 | 2.554e-05 | -0.98419 | 64.3387 | -58.699 | 64.2471 | -58.429 | -58.8043 | -58.7402 | -1.5381 | 64.389 | -58.5709 | -58.5022 | -58.5114 | -58.6258 | -58.3191 | -0.15564 | 0.009155 | -0.082398 | 0.11444 | -0.19684 | -0.26093 | -0.041198 | -0.10529 | -0.027466 | 0.059509 | -122.8317 | 0.032043 | 0.2243 | -0.082397 | 0.25177 | -0.054931 | 0.27008 | 122.9462 | 0.059509 | 0.068665 | 123.0377 | 122.9599 | 122.8821 | 122.9324 | -123.0286 | -122.9004 | 122.7905 | 0.041199 | 57.5592 | 57.0053
243.1719 | 123.2162 | -58.5068 | 64.389 | -0.052948 | -0.00023294 | 0.063734 | 0.060714 | -0.00069423 | -0.0029351 | -0.0014142 | 0.0078126 | -0.00039305 | -0.0014954 | -0.006349 | -0.00022431 | -0.0021619 | 0.0013073 | -0.87433 | 64.3387 | -58.6441 | 64.3158 | -58.5938 | -58.8547 | -58.6487 | -1.387 | 64.3845 | -58.5571 | -58.4885 | -58.429 | -58.5159 | -58.2733 | -0.13733 | -0.050354 | -0.073242 | -0.086975 | -0.14191 | -0.3479 | -0.004578 | -0.21057 | -0.050354 | -0.004578 | -122.8775 | 0.07782 | 0.23346 | -0.009155 | 0.28381 | 0.041199 | 0.050354 | 122.9599 | 0.12817 | 0.068665 | 122.9828 | 122.9416 | 122.8455 | 122.8912 | -123.0331 | -122.9462 | 122.8226 | 0.018311 | 57.6324 | 57.1198
244.1719 | 123.1934 | -58.5251 | 64.3616 | 0.015716 | 0.0021171 | 0.066939 | 0.06285 | -0.0011214 | -0.00015811 | -0.00098701 | -0.016602 | 0.0015295 | -0.00042717 | 0.0030506 | -0.0012925 | 0.00040152 | -0.0014697 | -0.93384 | 64.2929 | -58.7128 | 64.3021 | -58.3603 | -58.7585 | -58.7082 | -1.5289 | 64.3387 | -58.5709 | -58.5068 | -58.5251 | -58.5983 | -58.3282 | -0.18768 | -0.068664 | -0.059509 | 0.16479 | -0.18311 | -0.23346 | 0.004578 | -0.045776 | -0.045777 | -0.022888 | -122.8683 | 0 | 0.19684 | -0.073243 | 0.24262 | -0.027466 | 0.35248 | 123.0148 | 0.045777 | 0.064087 | 123.0057 | 122.9095 | 122.818 | 122.8638 | -123.0743 | -122.9324 | 122.8271 | 0.01831 | 57.5912 | 56.9962
245.1719 | 123.2437 | -58.5526 | 64.3707 | -0.13687 | 0.00040806 | 0.066298 | 0.066054 | 0.0035782 | 0.00069649 | 0.0011494 | -0.056274 | 0.00067495 | 0.00085443 | 0.0024096 | -0.00065151 | -0.00045288 | -0.0023243 | -1.0345 | 64.3158 | -58.7082 | 64.2609 | -58.4061 | -58.7997 | -58.7357 | -1.6067 | 64.3662 | -58.5663 | -58.5022 | -58.5114 | -58.6304 | -58.3099 | -0.15564 | -0.054932 | -0.10986 | 0.14648 | -0.18311 | -0.24719 | -0.027466 | -0.091553 | -0.013733 | -0.004578 | -122.8729 | 0.041198 | 0.24261 | -0.07782 | 0.25635 | -0.064087 | 0.30212 | 122.9691 | 0.054931 | 0.064087 | 123.024 | 122.9324 | 122.8683 | 122.9187 | -123.0789 | -122.937 | 122.8134 | 0.050354 | 57.518 | 56.9458
246.1719 | 123.1934 | -58.5434 | 64.3341 | -0.098725 | 0.0010489 | 0.066298 | 0.064345 | 0.0016556 | 0.00026909 | 0.00093559 | -0.050171 | 0.0040929 | 0.00042723 | -0.0031446 | -0.0012925 | -0.00023928 | -0.00082886 | -1.0757 | 64.357 | -58.7173 | 64.2334 | -58.4381 | -58.8409 | -58.7631 | -1.6525 | 64.4028 | -58.6166 | -58.5297 | -58.5251 | -58.6441 | -58.3099 | -0.17395 | 0.022889 | -0.10071 | 0.10529 | -0.21973 | -0.29755 | -0.045777 | -0.1236 | -0.073242 | 0.068665 | -122.8638 | 0.018311 | 0.23346 | -0.10071 | 0.3067 | -0.027466 | 0.27924 | 122.9507 | 0.091553 | 0.086975 | 123.0743 | 123.0194 | 122.9004 | 122.9462 | -123.0515 | -122.9507 | 122.7768 | 0.013733 | 57.4677 | 56.8909
247.1719 | 123.143 | -58.5617 | 64.2975 | -0.13687 | 0.0012625 | 0.063948 | 0.063918 | 0.0012284 | 0.0013373 | 0.00050839 | -0.044067 | -0.0025293 | -0.00021357 | 0.002196 | -0.00086511 | 0.00040152 | 0.0036571 | -1.0117 | 64.3158 | -58.6945 | 64.2838 | -58.3878 | -58.7677 | -58.7173 | -1.6251 | 64.3478 | -58.5892 | -58.4885 | -58.5022 | -58.6121 | -58.2138 | -0.13275 | 0.018311 | -0.013733 | 0.17395 | -0.15564 | -0.20599 | -0.022888 | -0.073242 | -0.027465 | 0.050354 | -122.7859 | 0.05951 | 0.3479 | -0.050354 | 0.37537 | -0.022889 | 0.3067 | 122.9782 | 0.086975 | 0.10071 | 123.0103 | 122.937 | 122.8775 | 122.9095 | -122.9919 | -122.8867 | 122.8455 | 0.073243 | 57.55 | 56.9366
248.1719 | 123.0972 | -58.5846 | 64.3936 | -0.052948 | 0.0019035 | 0.064162 | 0.065627 | 0.0018692 | 0.0019781 | -0.0012006 | -0.068481 | 0.00046135 | -0.00064077 | -0.00036738 | -0.00022431 | 0.00018792 | -0.0012561 | -1.1078 | 64.3616 | -58.7128 | 63.9862 | -58.7906 | -58.6578 | -58.5846 | -1.7853 | 64.4211 | -58.5983 | -58.6166 | -58.6075 | -58.754 | -58.4381 | -0.12817 | -0.032044 | -0.40741 | -0.20599 | 0 | -0.073242 | 0.12817 | 0.054932 | -0.013733 | 0.027466 | -123.0103 | -0.022888 | 0.14648 | -0.16937 | 0.16022 | -0.15564 | -0.077819 | 122.699 | -0.009155 | -0.01831 | 123.0743 | 123.0194 | 122.9462 | 123.0057 | -123.1064 | -122.9919 | 122.5708 | -0.032043 | 57.4768 | 56.7993
249.1719 | 123.1979 | -58.5388 | 64.3341 | -0.03006 | 0.0012625 | 0.063307 | 0.064773 | 0.0020828 | 0.0013373 | -0.0018414 | -0.03186 | -0.00039305 | -0.00042717 | 0.0058276 | -1.0706e-05 | -0.00023928 | -0.00082886 | -1.0986 | 64.3341 | -58.6899 | 64.2517 | -58.4198 | -58.786 | -58.7402 | -1.7349 | 64.3707 | -58.6075 | -58.5159 | -58.5159 | -58.6304 | -58.3145 | -0.15106 | 0 | -0.082397 | 0.11902 | -0.20142 | -0.24719 | -0.050354 | -0.096131 | -0.068665 | 0.036622 | -122.85 | 0.022888 | 0.2243 | -0.091553 | 0.29297 | -0.022888 | 0.27008 | 122.9416 | 0.091553 | 0.091553 | 123.024 | 122.9782 | 122.8729 | 122.9095 | -123.024 | -122.9416 | 122.7905 | 0.022888 | 57.4402 | 56.8039
250.1719 | 123.1934 | -58.5571 | 64.3662 | -0.10635 | 0.00083526 | 0.066725 | 0.064559 | -0.0038986 | -0.0018671 | -0.00055961 | -0.019653 | 0.00067495 | 0.001068 | 0.0045458 | 0.00084389 | 0.00061532 | 0.0013073 | -1.1536 | 64.3433 | -58.6899 | 64.2334 | -58.4335 | -58.8181 | -58.754 | -1.7715 | 64.3524 | -58.5892 | -58.5114 | -58.548 | -58.6349 | -58.2916 | -0.13275 | -0.022888 | -0.13275 | 0.1236 | -0.19684 | -0.26092 | -0.064087 | -0.12817 | -0.032043 | -0.013733 | -122.8775 | 0.009155 | 0.2655 | -0.07782 | 0.29755 | -0.045777 | 0.25635 | 122.9233 | 0.041198 | 0.077819 | 123.0331 | 122.9416 | 122.9004 | 122.9095 | -123.056 | -122.9553 | 122.7905 | 0.045776 | 57.4036 | 56.7856
251.1719 | 123.1979 | -58.5526 | 64.3707 | -0.083466 | 0.00019446 | 0.065443 | 0.063064 | -0.0015488 | 0.00026909 | 8.1188e-05 | 0.0047608 | 0.00046135 | 2.8e-08 | -0.0052808 | 0.00041649 | -0.0025891 | -0.0021107 | -1.1215 | 64.3295 | -58.6761 | 64.2838 | -58.3603 | -58.7677 | -58.699 | -1.7349 | 64.3478 | -58.5846 | -58.5114 | -58.5022 | -58.6121 | -58.3282 | -0.1236 | -0.041199 | -0.086976 | 0.19226 | -0.14648 | -0.21515 | -0.022889 | -0.091553 | -0.032044 | -0.022889 | -122.8821 | 0.050354 | 0.2243 | -0.05951 | 0.25635 | -0.027466 | 0.31586 | 122.9599 | 0.082398 | 0.073242 | 123.0057 | 122.9324 | 122.8821 | 122.9004 | -123.0469 | -122.9553 | 122.8363 | 0.041198 | 57.431 | 56.8176
252.1719 | 123.2208 | -58.5571 | 64.357 | -0.075836 | 0.0010489 | 0.066084 | 0.062636 | -0.0043258 | 0.0017645 | 0.0039264 | -0.022705 | 0.00046135 | 0.00064083 | -0.001222 | -0.00022431 | -2.5678e-05 | 0.00023934 | -1.1536 | 64.3204 | -58.7036 | 64.2654 | -58.3923 | -58.7677 | -58.7082 | -1.767 | 64.3478 | -58.58 | -58.5068 | -58.5068 | -58.5983 | -58.2962 | -0.14648 | -0.036621 | -0.091553 | 0.1648 | -0.15106 | -0.21057 | -0.004578 | -0.064087 | -0.022888 | -0.009156 | -122.8638 | 0.050354 | 0.26093 | -0.041199 | 0.28381 | -0.018311 | 0.31128 | 122.9691 | 0.073242 | 0.073242 | 123.024 | 122.9279 | 122.8775 | 122.905 | -123.0606 | -122.937 | 122.8226 | 0.050354 | 57.4036 | 56.7902
253.1719 | 123.1522 | -58.5754 | 64.357 | -0.15213 | 0.0023307 | 0.063521 | 0.063491 | 0.0012284 | 0.00069649 | -0.00077341 | -0.041016 | -0.00017945 | 0.00021363 | 0.0079638 | -1.0706e-05 | -0.00066648 | 0.0013073 | -1.2085 | 64.3478 | -58.7219 | 64.183 | -58.4793 | -58.8638 | -58.7952 | -1.8997 | 64.3936 | -58.5983 | -58.5754 | -58.5754 | -58.7082 | -58.3832 | -0.14648 | -0.009156 | -0.17395 | 0.09613 | -0.21973 | -0.28839 | -0.073242 | -0.14191 | -0.022889 | 0.036621 | -122.9324 | 0 | 0.19226 | -0.13275 | 0.21515 | -0.10986 | 0.24262 | 122.905 | 0.022889 | 0.022889 | 123.0698 | 122.9919 | 122.9233 | 122.9691 | -123.0789 | -122.9553 | 122.7585 | 0 | 57.3669 | 56.6757
254.1719 | 123.1384 | -58.5846 | 64.3845 | -0.091095 | 0.00019446 | 0.062666 | 0.063491 | 0.0027238 | 0.00091009 | 0.00093559 | -0.037964 | 0.0025975 | 0.00085443 | -0.0037854 | -0.00022431 | -0.0021619 | 0.0042981 | -1.236 | 64.3662 | -58.7082 | 64.183 | -58.4976 | -58.8455 | -58.8135 | -1.9501 | 64.3845 | -58.5983 | -58.58 | -58.6029 | -58.7082 | -58.3969 | -0.1236 | -0.01831 | -0.20142 | 0.086975 | -0.22888 | -0.26093 | -0.10529 | -0.13733 | -0.013733 | 0 | -122.9645 | -0.01831 | 0.18768 | -0.1236 | 0.20142 | -0.10986 | 0.21057 | 122.8912 | -0.004577 | 0.018311 | 123.0743 | 122.9828 | 122.9507 | 122.9691 | -123.0927 | -122.9828 | 122.7676 | 0.004578 | 57.3486 | 56.6345
255.1719 | 123.1247 | -58.5709 | 64.4165 | 0.015716 | -0.0010873 | 0.064589 | 0.066054 | -0.0030442 | 0.00069649 | 0.0011494 | -0.047119 | 0.0017431 | -0.00064077 | 0.0030506 | 0.0014847 | 0.0012561 | -0.00061526 | -1.2772 | 64.3845 | -58.6899 | 64.1693 | -58.5159 | -58.8821 | -58.8181 | -1.9684 | 64.3982 | -58.6212 | -58.5846 | -58.6075 | -58.7448 | -58.3969 | -0.11902 | -0.032044 | -0.24719 | 0.054932 | -0.24719 | -0.31128 | -0.12817 | -0.19226 | -0.050354 | -0.018311 | -123.0011 | -0.036621 | 0.17395 | -0.17395 | 0.2243 | -0.1236 | 0.17395 | 122.8592 | 0.013733 | 0.036621 | 123.0743 | 123.0194 | 122.9553 | 122.9691 | -123.1064 | -123.0377 | 122.7402 | -0.013733 | 57.2937 | 56.6025
256.1719 | 123.1659 | -58.5617 | 64.3478 | -0.083466 | 0.0012625 | 0.065443 | 0.065414 | 0.0020828 | 0.00091009 | -0.00013241 | -0.025757 | -0.00039305 | 0.00064083 | -0.002931 | -0.0017197 | -0.00023928 | -0.00018806 | -1.3046 | 64.3433 | -58.7173 | 64.1968 | -58.4473 | -58.8547 | -58.7906 | -1.9638 | 64.357 | -58.6029 | -58.5251 | -58.5342 | -58.6395 | -58.3099 | -0.15564 | -0.004577 | -0.15106 | 0.11444 | -0.22888 | -0.29297 | -0.073242 | -0.13733 | -0.041198 | 0.009156 | -122.8729 | 0.027466 | 0.25177 | -0.077819 | 0.29297 | -0.036621 | 0.27008 | 122.9141 | 0.068664 | 0.07782 | 123.0606 | 122.9599 | 122.905 | 122.9187 | -123.0652 | -122.9507 | 122.7585 | 0.036622 | 57.2571 | 56.5979
257.1719 | 123.1796 | -58.548 | 64.3707 | -0.068207 | -0.00087374 | 0.064803 | 0.063705 | -0.0017624 | -0.0012261 | -0.0014142 | -0.041016 | -0.00082025 | 2.8e-08 | 0.0026232 | -0.00086511 | -0.00066648 | 0.0015209 | -1.3138 | 64.3662 | -58.6945 | 64.1968 | -58.4793 | -58.8684 | -58.8089 | -2.005 | 64.3799 | -58.5938 | -58.5526 | -58.5709 | -58.6761 | -58.3603 | -0.14648 | -0.004578 | -0.17395 | 0.068665 | -0.26092 | -0.32043 | -0.11444 | -0.17395 | -0.045776 | 0.009155 | -122.9233 | -0.022888 | 0.18768 | -0.12817 | 0.23346 | -0.082397 | 0.21515 | 122.8912 | 0.022888 | 0.041199 | 123.0606 | 122.9736 | 122.9141 | 122.9279 | -123.0652 | -122.9645 | 122.7448 | -0.004577 | 57.2342 | 56.543
258.1719 | 123.1064 | -58.5663 | 64.3845 | -0.083466 | 0.00062166 | 0.063734 | 0.066054 | -0.00090783 | 5.5488e-05 | -0.00098701 | -0.01355 | 0.0013159 | 0.00085443 | -0.0035718 | 0.00041649 | 0.0016833 | 0.00023934 | -1.3229 | 64.389 | -58.7265 | 64.1785 | -58.4839 | -58.8684 | -58.7997 | -2.0142 | 64.4028 | -58.5846 | -58.58 | -58.5754 | -58.7036 | -58.3786 | -0.16022 | 0.004578 | -0.20599 | 0.082397 | -0.23346 | -0.30212 | -0.073243 | -0.14191 | -0.018311 | 0.018311 | -122.9645 | -0.009155 | 0.18768 | -0.13733 | 0.20599 | -0.11902 | 0.24261 | 122.905 | 0.009156 | 0.004578 | 123.1155 | 122.9874 | 122.9553 | 122.9691 | -123.111 | -122.9691 | 122.7448 | -0.013733 | 57.2433 | 56.5521
259.1719 | 123.2025 | -58.5571 | 64.3662 | -0.13687 | -1.9142e-05 | 0.064589 | 0.063491 | 0.00016017 | 0.00026909 | -0.0014142 | 0.087158 | -0.00082025 | 0.0014954 | -0.0054944 | -0.00065151 | 0.00018792 | -0.0029651 | -1.2955 | 64.3295 | -58.6624 | 64.2792 | -58.4106 | -59.0652 | -58.6761 | -1.9592 | 64.389 | -58.5617 | -58.5068 | -58.5114 | -58.5938 | -58.287 | -0.10529 | -0.036621 | -0.086975 | 0.14648 | -0.11902 | -0.50812 | -0.013732 | -0.40283 | -0.004578 | 0.022888 | -122.8729 | 0.045776 | 0.27008 | -0.036621 | 0.27466 | -0.032043 | 0.25177 | 122.9416 | 0.050354 | 0.054932 | 122.9919 | 122.9507 | 122.8867 | 122.9462 | -123.0286 | -122.9279 | 122.8363 | 0.050354 | 57.2617 | 56.5979
260.1719 | 123.0972 | -58.5754 | 64.389 | -0.091095 | -0.00066014 | 0.064162 | 0.063277 | -0.00026703 | 0.00026909 | 0.00050839 | -0.025757 | 0.00088875 | 0.0021362 | 0.0043322 | 0.00041649 | -0.00088008 | 0.00088014 | -1.3641 | 64.3707 | -58.7036 | 64.1647 | -58.5068 | -58.8776 | -58.7997 | -2.1011 | 64.4028 | -58.5846 | -58.5983 | -58.6212 | -58.7219 | -58.4106 | -0.12817 | -0.01831 | -0.2243 | 0.068664 | -0.2243 | -0.30212 | -0.096131 | -0.17395 | -0.009156 | 0.013733 | -122.9874 | -0.045777 | 0.16479 | -0.14648 | 0.17395 | -0.13733 | 0.19684 | 122.8683 | -0.036621 | -0.013733 | 123.0743 | 122.9874 | 122.9462 | 122.9782 | -123.0927 | -122.9736 | 122.7402 | -0.022889 | 57.2113 | 56.4743
261.1719 | 123.1064 | -58.5663 | 64.4165 | -0.068207 | -0.0032235 | 0.063094 | 0.066695 | -0.0017624 | -0.0022943 | -0.0024822 | -0.028809 | 0.00088875 | 0.00085443 | -0.00058098 | 0.0019119 | 0.0014697 | 0.0030163 | -1.2589 | 64.3936 | -58.6945 | 64.183 | -58.5114 | -58.8593 | -58.7952 | -2.1332 | 64.4257 | -58.6121 | -58.5892 | -58.6212 | -58.7448 | -58.4061 | -0.12817 | -0.022888 | -0.23346 | 0.054931 | -0.22888 | -0.29297 | -0.10071 | -0.1648 | -0.045777 | 0.009155 | -123.0057 | -0.054932 | 0.16022 | -0.17853 | 0.20599 | -0.13275 | 0.1831 | 122.8775 | -0.009155 | 0.022889 | 123.0881 | 123.0377 | 122.9599 | 122.9919 | -123.111 | -123.0286 | 122.7493 | -0.022888 | 57.3074 | 56.4331
262.1719 | 123.056 | -58.5938 | 64.4073 | -0.091095 | -0.00044654 | 0.063094 | 0.064986 | -0.00069423 | 0.0015509 | 0.0028582 | -0.059326 | 0.0017431 | -0.0014954 | -0.0052808 | -0.0012925 | -0.00088008 | -0.0014697 | -1.3779 | 64.3799 | -58.6899 | 64.1876 | -58.4885 | -58.873 | -58.8089 | -2.1652 | 64.4302 | -58.5983 | -58.6075 | -58.6304 | -58.7677 | -58.429 | -0.09613 | -0.027466 | -0.21973 | 0.10529 | -0.21515 | -0.27924 | -0.11902 | -0.18311 | -0.004578 | 0.022888 | -123.0148 | -0.036621 | 0.16479 | -0.17395 | 0.16937 | -0.16937 | 0.20142 | 122.8775 | -0.032043 | -0.009155 | 123.0698 | 123.0286 | 122.9736 | 123.024 | -123.0972 | -123.0057 | 122.7814 | -0.013733 | 57.2159 | 56.4285
263.1719 | 123.0789 | -58.5846 | 64.3982 | -0.091095 | -1.9142e-05 | 0.064162 | 0.065841 | -0.0021896 | 0.00048269 | 0.0015766 | -0.028809 | 0.0011023 | 0.00042723 | 0.0043322 | 0.00063009 | -0.0015211 | 0.0023755 | -1.4557 | 64.3845 | -58.7173 | 64.1327 | -58.5297 | -58.8913 | -58.8364 | -2.4536 | 64.3616 | -58.6487 | -58.5892 | -58.58 | -58.786 | -58.429 | -0.13275 | -0.013733 | -0.2655 | 0.054932 | -0.25177 | -0.3067 | -0.11902 | -0.17395 | -0.064087 | -0.036621 | -122.9874 | 0.004578 | 0.15564 | -0.20142 | 0.21973 | -0.13733 | 0.18768 | 122.85 | 0.068665 | 0.05951 | 123.1018 | 123.0103 | 122.9691 | 122.9462 | -123.1155 | -123.0469 | 122.7173 | -0.004577 | 57.1289 | 56.131
264.1719 | 123.1934 | -58.5571 | 64.389 | -0.10635 | -0.00023294 | 0.065016 | 0.066268 | -0.0024032 | 0.0017645 | -0.0016278 | 0.02002 | 0.0013159 | 0.00021363 | -0.00036738 | -0.00043791 | 0.00040152 | 0.0013073 | -1.4786 | 64.3387 | -58.7082 | 64.2288 | -58.429 | -58.8226 | -58.7769 | -2.1194 | 64.389 | -58.6029 | -58.5159 | -58.5297 | -58.6487 | -58.3145 | -0.15106 | -0.050354 | -0.16022 | 0.12817 | -0.21973 | -0.2655 | -0.068664 | -0.11444 | -0.045776 | 0 | -122.905 | 0.027466 | 0.24262 | -0.091553 | 0.28839 | -0.045777 | 0.27924 | 122.937 | 0.073242 | 0.086975 | 123.0469 | 122.9919 | 122.8958 | 122.9462 | -123.0972 | -122.9919 | 122.7859 | 0.041199 | 57.0786 | 56.4377
265.1719 | 123.1659 | -58.5342 | 64.3799 | -0.091095 | -0.0023691 | 0.064375 | 0.063705 | -0.00069423 | -0.0016535 | 8.1188e-05 | -0.025757 | 0.00024775 | 0.0021362 | -0.0020764 | -0.00065151 | 0.00018792 | -0.00040166 | -1.4923 | 64.3799 | -58.6853 | 64.183 | -58.4747 | -58.8501 | -58.8043 | -2.1652 | 64.3753 | -58.5846 | -58.5571 | -58.5434 | -58.6533 | -58.3466 | -0.15106 | 0 | -0.19684 | 0.05951 | -0.27008 | -0.31586 | -0.11902 | -0.1648 | -0.050354 | -0.004578 | -122.937 | -0.009155 | 0.18768 | -0.11902 | 0.23804 | -0.068664 | 0.21057 | 122.8683 | 0.041199 | 0.027466 | 123.0652 | 122.9599 | 122.9141 | 122.9095 | -123.0652 | -122.9645 | 122.7173 | -0.022888 | 57.0419 | 56.369
266.1719 | 123.0835 | -58.5617 | 64.3799 | -0.068207 | 0.0019035 | 0.064803 | 0.064773 | 0.0010148 | 0.00069649 | -0.00013241 | -0.047119 | 0.0023839 | -0.0014954 | 0.0041186 | -0.0012925 | 0.00018792 | 0.0030163 | -1.5244 | 64.3616 | -58.6945 | 64.1693 | -58.5205 | -58.8821 | -58.8409 | -2.5681 | 64.3387 | -58.6487 | -58.58 | -58.6304 | -58.7494 | -58.3832 | -0.13275 | -0.018311 | -0.21057 | 0.041199 | -0.27923 | -0.32043 | -0.14648 | -0.18768 | -0.086975 | -0.041199 | -122.9599 | -0.068664 | 0.17853 | -0.18768 | 0.2655 | -0.10071 | 0.17395 | 122.8638 | 0.018311 | 0.068665 | 123.056 | 122.9874 | 122.9233 | 122.9004 | -123.0743 | -123.0286 | 122.731 | -0.01831 | 57.0374 | 55.9937
267.1719 | 123.0423 | -58.6304 | 64.3433 | -0.15976 | 0.00040806 | 0.064803 | 0.064345 | 0.0010148 | -0.00015811 | 0.003072 | -0.034912 | 0.0011023 | 0.001709 | -0.0044262 | -0.0010787 | -0.0010937 | 0.00066654 | -1.5244 | 64.3936 | -58.699 | 64.151 | -58.5251 | -58.905 | -58.8364 | -2.2339 | 64.4073 | -58.6029 | -58.6258 | -58.6121 | -58.7585 | -58.6349 | -0.068665 | 0.050354 | -0.19226 | 0.10529 | -0.20599 | -0.27466 | -0.13733 | -0.20599 | 0.027466 | 0.064087 | -122.9691 | 0.01831 | -0.004578 | -0.12817 | -0.032044 | -0.15564 | 0.17395 | 122.85 | -0.009156 | -0.022888 | 123.0927 | 123.0103 | 123.024 | 123.0377 | -123.0423 | -122.9462 | 122.7814 | 0.004578 | 57.106 | 56.3965
268.1719 | 123.0606 | -58.5709 | 64.4028 | -0.037689 | 0.0021171 | 0.064375 | 0.063491 | -0.00090783 | -0.0010125 | -0.0016278 | -0.028809 | -0.00060665 | -0.00085457 | 0.0028368 | -0.00086511 | -0.00023928 | 0.00023934 | -1.5518 | 64.389 | -58.7082 | 64.1693 | -58.5114 | -58.873 | -58.8226 | -2.2568 | 64.4394 | -58.58 | -58.6304 | -58.6395 | -58.7769 | -58.4244 | -0.13733 | -0.013733 | -0.23346 | 0.059509 | -0.25177 | -0.30212 | -0.11444 | -0.16479 | -0.009155 | 0.036621 | -123.0331 | -0.068664 | 0.14648 | -0.20599 | 0.15564 | -0.19684 | 0.19684 | 122.8775 | -0.059509 | -0.050354 | 123.0972 | 123.0194 | 122.9599 | 123.0103 | -123.111 | -122.9828 | 122.7402 | -0.059509 | 57.019 | 56.3141
269.1719 | 123.0515 | -58.5709 | 64.4073 | -0.083466 | -0.00087374 | 0.063094 | 0.063918 | 0.0022964 | -0.00058531 | 0.0015766 | -0.010498 | 0.0013159 | -0.00042717 | 0.0024096 | 0.00041649 | -0.0019483 | -0.0033923 | -1.5518 | 64.3799 | -58.6899 | 64.1876 | -58.4702 | -58.8593 | -58.7997 | -2.2247 | 64.4348 | -58.5938 | -58.6212 | -58.6075 | -58.7402 | -58.3923 | -0.11902 | -0.027466 | -0.21973 | 0.10071 | -0.22888 | -0.28839 | -0.10986 | -0.16937 | -0.022888 | 0.027465 | -123.0286 | -0.036621 | 0.17853 | -0.16937 | 0.20142 | -0.14648 | 0.21973 | 122.8775 | -0.013733 | -0.027466 | 123.0698 | 123.0286 | 122.9507 | 123.0057 | -123.0972 | -123.0011 | 122.7585 | -0.050354 | 57.019 | 56.3461
270.1719 | 123.111 | -58.548 | 64.4348 | -0.060578 | -0.00044654 | 0.064162 | 0.061782 | 0.001442 | -0.00037171 | 0.0034992 | -0.022705 | 0.00024775 | 0.00021363 | -0.00058098 | -0.0010787 | -2.5678e-05 | 0.00023934 | -1.5518 | 64.3662 | -58.699 | 64.2151 | -58.4518 | -58.8272 | -58.7952 | -2.179 | 64.4302 | -58.5846 | -58.6212 | -58.6029 | -58.699 | -58.3969 | -0.15106 | -0.068664 | -0.21973 | 0.096131 | -0.24719 | -0.27923 | -0.09613 | -0.12817 | -0.036621 | -0.004577 | -123.056 | -0.054931 | 0.15106 | -0.15106 | 0.18768 | -0.11444 | 0.24719 | 122.9141 | -0.01831 | -0.036621 | 123.0652 | 123.0148 | 122.9141 | 122.9782 | -123.1338 | -123.0194 | 122.7631 | -0.073242 | 56.9962 | 56.369
271.1719 | 123.0698 | -58.5709 | 64.3982 | -0.068207 | -0.0010873 | 0.064375 | 0.0652 | 0.00080117 | -0.00079891 | 0.00072199 | -0.028809 | 0.0013159 | 0.00064083 | 5.9824e-05 | 0.00084389 | -2.5678e-05 | -0.0031787 | -1.6113 | 64.3936 | -58.6899 | 64.1785 | -58.5022 | -58.8501 | -58.8318 | -2.2751 | 64.4211 | -58.5846 | -58.6258 | -58.6441 | -58.7769 | -58.4152 | -0.11902 | -0.004577 | -0.21973 | 0.068665 | -0.26093 | -0.27924 | -0.14191 | -0.16022 | -0.013733 | 0.022889 | -123.024 | -0.073242 | 0.15564 | -0.20599 | 0.16937 | -0.19226 | 0.18768 | 122.8683 | -0.059509 | -0.041198 | 123.0835 | 123.0057 | 122.9645 | 122.9919 | -123.0881 | -122.9828 | 122.7493 | -0.054931 | 56.9595 | 56.2958
272.1719 | 123.1064 | -58.5709 | 64.4257 | -0.083466 | 0.0021171 | 0.064589 | 0.063705 | 0.0018692 | 0.00091009 | -0.00055961 | -0.0043946 | 0.0019567 | 0.0014954 | 0.0024096 | -0.00065151 | -0.0015211 | 0.0025891 | -1.6525 | 64.3936 | -58.7448 | 64.151 | -58.5526 | -58.8913 | -58.8318 | -2.2797 | 64.4073 | -58.6212 | -58.4747 | -58.493 | -58.786 | -58.4564 | -0.17395 | -0.032043 | -0.27466 | 0.018311 | -0.26093 | -0.32043 | -0.086975 | -0.14648 | -0.050354 | -0.01831 | -122.9004 | 0.07782 | 0.11444 | -0.21515 | 0.16479 | -0.1648 | 0.19226 | 122.8958 | 0.12817 | 0.14648 | 123.1384 | 123.0286 | 122.9645 | 122.9782 | -123.1705 | -123.0469 | 122.7219 | 0.096131 | 56.9183 | 56.2912
273.1719 | 123.0881 | -58.5846 | 64.4073 | -0.037689 | -0.00023294 | 0.063094 | 0.063277 | 0.0022964 | 0.0019781 | -0.00055961 | -0.016602 | 0.00046135 | 0.00064083 | -0.00036738 | -0.00065151 | 0.00040152 | 0.0021619 | -1.6479 | 64.3662 | -58.6853 | 64.1647 | -58.5159 | -58.873 | -58.8272 | -2.3163 | 64.4348 | -58.6029 | -58.6304 | -58.6212 | -58.7448 | -58.4061 | -0.10071 | -0.041199 | -0.24262 | 0.068665 | -0.24261 | -0.28839 | -0.14191 | -0.18768 | -0.01831 | 0.027465 | -123.0377 | -0.036621 | 0.17853 | -0.16022 | 0.19684 | -0.14191 | 0.16937 | 122.85 | -0.018311 | -0.027466 | 123.0515 | 123.0377 | 122.9507 | 123.0194 | -123.0927 | -123.0103 | 122.7493 | -0.045776 | 56.9366 | 56.2683
274.1719 | 123.0972 | -58.5526 | 64.444 | -0.03006 | 0.0019035 | 0.065443 | 0.063705 | -0.0032578 | 0.00091009 | 8.1188e-05 | -0.019653 | 0.0013159 | -0.0023498 | 0.00091422 | 0.00041649 | -0.0017347 | 0.0015209 | -1.6067 | 64.3799 | -58.6807 | 64.2288 | -58.4015 | -58.8135 | -58.754 | -2.179 | 64.4257 | -58.5617 | -58.5709 | -58.58 | -58.699 | -58.374 | -0.12817 | -0.064087 | -0.21515 | 0.15106 | -0.20142 | -0.26093 | -0.073242 | -0.13275 | -0.009156 | -0.018311 | -123.0148 | -0.027466 | 0.17853 | -0.14648 | 0.18768 | -0.13733 | 0.27924 | 122.9095 | -0.01831 | -0.009155 | 123.0606 | 122.9874 | 122.9324 | 122.9782 | -123.1247 | -123.0057 | 122.7814 | -0.018311 | 56.9458 | 56.3736
275.1719 | 123.0606 | -58.5251 | 64.4211 | -0.12924 | -0.0030099 | 0.064375 | 0.063277 | 0.0040054 | 0.0030463 | -0.00034601 | -0.0043946 | 0.0013159 | -0.00042717 | 0.00070062 | -0.0012925 | 0.00082892 | -0.00061526 | -1.712 | 64.4028 | -58.699 | 64.151 | -58.5205 | -58.8821 | -58.8501 | -2.298 | 64.4257 | -58.5892 | -58.7906 | -58.3374 | -58.5342 | -58.3557 | -0.17395 | -0.018311 | -0.27008 | 0.004577 | -0.32501 | -0.35706 | -0.15106 | -0.1831 | -0.064087 | 0.004577 | -123.2117 | 0.18768 | 0.16937 | -0.009156 | 0.23346 | 0.054931 | 0.17853 | 122.85 | 0.25177 | -0.20142 | 123.1018 | 123.0148 | 122.9279 | 122.9507 | -123.1201 | -123.0103 | 122.6761 | -0.2655 | 56.813 | 56.2271
276.1719 | 123.1201 | -58.5159 | 64.4257 | -0.03006 | -0.0019417 | 0.063948 | 0.061782 | -0.0030442 | -0.0010125 | 0.0011494 | 0.0078126 | 0.0017431 | -0.00085457 | -0.00015378 | -0.00022431 | 0.00018792 | 2.554e-05 | -1.6205 | 64.4302 | -58.6716 | 64.2609 | -58.3923 | -58.7585 | -58.7265 | -2.1332 | 64.4302 | -58.5617 | -58.5526 | -58.5297 | -58.6304 | -58.3374 | -0.15564 | 0.004578 | -0.16479 | 0.1236 | -0.21057 | -0.24262 | -0.054931 | -0.086975 | -0.045777 | 0.004578 | -122.9782 | -0.013733 | 0.17853 | -0.11444 | 0.22431 | -0.068664 | 0.27924 | 122.9324 | 0.032044 | 0.009156 | 123.1018 | 122.9919 | 122.9462 | 122.9462 | -123.0972 | -122.9874 | 122.7768 | -0.036621 | 56.8954 | 56.3828
277.1719 | 123.1384 | -58.5251 | 64.4348 | 0.00045798 | 0.0014761 | 0.064375 | 0.063918 | 0.0010148 | -0.00079891 | -0.00013241 | -0.016602 | 0.00024775 | -0.0010682 | 0.003905 | -0.00065151 | 0.00040152 | -0.0014697 | -1.6388 | 64.4028 | -58.667 | 64.2517 | -58.3923 | -58.7631 | -58.7402 | -2.1423 | 64.4531 | -58.5663 | -58.5068 | -58.4885 | -58.6349 | -58.3191 | -0.14191 | -0.032043 | -0.1831 | 0.13275 | -0.21515 | -0.23804 | -0.073242 | -0.096131 | -0.041199 | 0.018311 | -122.9416 | 0.036621 | 0.20599 | -0.10986 | 0.24719 | -0.068665 | 0.27466 | 122.9187 | 0.07782 | 0.059509 | 123.0698 | 123.0194 | 122.9279 | 122.9782 | -123.1018 | -123.0011 | 122.7768 | 0.01831 | 56.8863 | 56.3828
278.1719 | 123.143 | -58.5388 | 64.4348 | 0.00045798 | 0.0019035 | 0.063734 | 0.0652 | 0.0020828 | 0.00069649 | 8.1188e-05 | -0.0074462 | 0.00088875 | 0.00085443 | -0.001222 | -0.00022431 | -2.5678e-05 | -0.00018806 | -1.6708 | 64.4165 | -58.6624 | 64.2517 | -58.4015 | -58.7585 | -58.7448 | -2.1515 | 64.4577 | -58.5617 | -58.5526 | -58.5434 | -58.6624 | -58.3511 | -0.1236 | -0.01831 | -0.1831 | 0.13733 | -0.20599 | -0.21973 | -0.082397 | -0.09613 | -0.022889 | 0.022889 | -122.9874 | -0.004578 | 0.18768 | -0.1236 | 0.21057 | -0.10071 | 0.26093 | 122.9141 | 0.018311 | 0.009156 | 123.0789 | 123.0194 | 122.9553 | 122.9965 | -123.0972 | -122.9965 | 122.7905 | -0.013733 | 56.868 | 56.3873
279.1719 | 123.0927 | -58.5205 | 64.4211 | -0.060578 | -1.9142e-05 | 0.064589 | 0.063491 | -0.0011214 | 0.00091009 | 0.0017902 | -0.016602 | -0.00060665 | 0.0012818 | 0.00027342 | -0.0021469 | -0.00023928 | 0.0010937 | -1.7166 | 64.4073 | -58.6761 | 64.2105 | -58.4198 | -58.8043 | -58.7677 | -2.2064 | 64.4028 | -58.5709 | -58.5983 | -58.5846 | -58.699 | -58.3969 | -0.15564 | -0.013733 | -0.21057 | 0.10071 | -0.24719 | -0.28381 | -0.091553 | -0.12817 | -0.050354 | -0.018311 | -123.0194 | -0.064087 | 0.1236 | -0.17853 | 0.17395 | -0.12817 | 0.25635 | 122.8867 | -0.013733 | -0.027466 | 123.0835 | 122.9736 | 122.9279 | 122.9233 | -123.0972 | -122.9919 | 122.731 | -0.07782 | 56.8039 | 56.3141
280.1719 | 123.0881 | -58.5388 | 64.4165 | -0.12161 | -0.0030099 | 0.063948 | 0.064345 | 0.003151 | 0.00069649 | -0.002055 | -0.0013428 | -0.00017945 | 0.001709 | -0.003999 | -0.0019333 | -0.0023755 | 0.0017345 | -1.7212 | 64.4073 | -58.6533 | 64.2288 | -58.4061 | -58.7906 | -58.7631 | -2.1881 | 64.4394 | -58.5709 | -58.5709 | -58.5663 | -58.6899 | -58.3786 | -0.11444 | -0.009155 | -0.18768 | 0.13275 | -0.22431 | -0.25177 | -0.10986 | -0.13733 | -0.032044 | 0.022888 | -122.9874 | -0.027466 | 0.16022 | -0.15106 | 0.19226 | -0.11902 | 0.24719 | 122.8821 | 0.004578 | 0 | 123.0606 | 123.0103 | 122.9462 | 122.9782 | -123.0698 | -122.9874 | 122.7676 | -0.032044 | 56.8176 | 56.3507
281.1719 | 123.1064 | -58.5571 | 64.4073 | -0.12924 | -0.0017281 | 0.066084 | 0.064559 | 0.00080117 | -0.0020807 | 0.00050839 | 0.0047608 | 0.0013159 | -0.00042717 | 0.0092456 | 0.00041649 | 0.0010425 | 0.00088014 | -1.68 | 64.3982 | -58.6487 | 64.2654 | -58.4015 | -58.754 | -58.7448 | -2.179 | 64.3982 | -58.5663 | -58.5526 | -58.5434 | -58.6533 | -58.3328 | -0.091553 | -0.009156 | -0.14191 | 0.15564 | -0.18768 | -0.19684 | -0.09613 | -0.10529 | -0.009155 | -0.009156 | -122.9599 | 0.013733 | 0.2243 | -0.09613 | 0.23346 | -0.086975 | 0.24719 | 122.9141 | 0.022888 | 0.013733 | 123.0469 | 122.9645 | 122.9553 | 122.9553 | -123.056 | -122.9736 | 122.8226 | 0.004578 | 56.8771 | 56.3782
282.1719 | 123.1247 | -58.5159 | 64.4531 | -0.014801 | -0.0030099 | 0.066084 | 0.064559 | 0.00080117 | -0.0020807 | 0.002431 | 0.026123 | 0.00024775 | 0.00064083 | -0.00058098 | 0.00041649 | -2.5678e-05 | 0.0017345 | -1.7166 | 64.389 | -58.6716 | 64.2883 | -58.5663 | -58.8684 | -58.7036 | -2.1515 | 64.4531 | -58.5526 | -58.5342 | -58.5388 | -58.6441 | -58.3282 | -0.15564 | -0.064087 | -0.16479 | -0.050354 | -0.18768 | -0.35248 | -0.032043 | -0.19684 | -0.036621 | 0 | -122.9874 | -0.022888 | 0.18768 | -0.12817 | 0.2243 | -0.091553 | 0.10529 | 122.9599 | 0.013733 | 0.01831 | 123.0606 | 123.0057 | 122.905 | 122.9691 | -123.1247 | -123.0057 | 122.8043 | -0.018311 | 56.7993 | 56.3644
283.1719 | 123.0881 | -58.5297 | 64.4577 | -0.014801 | 0.00019446 | 0.065443 | 0.061782 | -0.00090783 | 0.0015509 | -0.00098701 | 0.047485 | -0.00060665 | 0.0014954 | 0.00091422 | -0.0012925 | -0.0028027 | 0.0015209 | -1.7899 | 64.4348 | -58.6578 | 64.2059 | -58.4518 | -58.7906 | -58.7448 | -2.243 | 64.4577 | -58.5526 | -58.5938 | -58.5434 | -58.6716 | -58.3557 | -0.12817 | -0.022889 | -0.25177 | 0.07782 | -0.21515 | -0.26093 | -0.086975 | -0.13275 | -0.022888 | 0 | -123.0515 | -0.013733 | 0.17395 | -0.14191 | 0.19684 | -0.11902 | 0.20599 | 122.8638 | 0.009155 | -0.041199 | 123.0927 | 123.0103 | 122.9645 | 122.9874 | -123.1155 | -123.0103 | 122.7356 | -0.064087 | 56.7398 | 56.2866
284.1719 | 123.1064 | -58.5251 | 64.4531 | -0.045319 | -0.00066014 | 0.064589 | 0.06285 | -0.00090783 | 0.00091009 | -0.00034601 | 0.02002 | 0.0017431 | 0.0036316 | 0.0036914 | -0.0012925 | -0.0013073 | -0.00018806 | -1.7853 | 64.4302 | -58.667 | 64.2334 | -58.4335 | -58.7677 | -58.7448 | -2.2018 | 64.4806 | -58.5297 | -58.5617 | -58.5114 | -58.6304 | -58.3237 | -0.14191 | -0.022888 | -0.21973 | 0.091552 | -0.21973 | -0.24262 | -0.07782 | -0.10071 | -0.004578 | 0.027466 | -123.0148 | 0.013732 | 0.20142 | -0.10529 | 0.20599 | -0.10071 | 0.23346 | 122.9004 | 0.01831 | -0.032044 | 123.0972 | 123.0103 | 122.9553 | 123.0057 | -123.1201 | -122.9828 | 122.7585 | -0.036622 | 56.7398 | 56.3232
285.1719 | 123.1293 | -58.5022 | 64.4257 | 0.00045798 | -0.00044654 | 0.064589 | 0.064132 | 0.004219 | -0.0020807 | -0.0014142 | 0.029175 | 0.0030249 | 0.00042723 | -0.0054944 | 0.00041649 | -0.00023928 | -0.0029651 | -1.7487 | 64.4257 | -58.6578 | 64.2517 | -58.4015 | -58.7631 | -58.7311 | -2.1835 | 64.4531 | -58.548 | -58.5434 | -58.4976 | -58.6395 | -58.3328 | -0.15564 | 0 | -0.17395 | 0.10071 | -0.22888 | -0.26093 | -0.073242 | -0.10529 | -0.045777 | 0.027466 | -122.9691 | 0.004577 | 0.16937 | -0.13733 | 0.21515 | -0.091552 | 0.25635 | 122.9095 | 0.050354 | 0.004578 | 123.0835 | 123.0011 | 122.9279 | 122.9553 | -123.0835 | -122.9736 | 122.7539 | -0.041199 | 56.7535 | 56.3187
286.1719 | 123.143 | -58.5205 | 64.4485 | -0.083466 | -0.00023294 | 0.064375 | 0.063491 | 0.00080117 | -0.0010125 | -0.0035504 | 0.0047608 | 0.00067495 | 0.00042723 | -0.003999 | -0.0017197 | -0.00066648 | -0.0021107 | -1.7761 | 64.4028 | -58.6578 | 64.2426 | -58.4015 | -58.7494 | -58.7357 | -2.1927 | 64.444 | -58.5251 | -58.548 | -58.5114 | -58.6533 | -58.3282 | -0.13733 | -0.045776 | -0.20599 | 0.11902 | -0.21515 | -0.22888 | -0.07782 | -0.091553 | -0.004577 | -0.004577 | -122.9965 | 0.009155 | 0.19226 | -0.13275 | 0.19684 | -0.12817 | 0.25635 | 122.9004 | 0.013732 | -0.022889 | 123.0606 | 122.9691 | 122.9233 | 122.9645 | -123.1064 | -122.9736 | 122.7631 | -0.027466 | 56.7444 | 56.3278
287.1719 | 123.1201 | -58.548 | 64.4531 | -0.0071715 | 0.00083526 | 0.064162 | 0.060927 | -5.343e-05 | 5.5488e-05 | 0.003072 | 0.013916 | 0.00067495 | 0.0019226 | -0.0067762 | -0.00022431 | -0.00023928 | 0.00045294 | -1.7944 | 64.3982 | -58.6624 | 64.2654 | -58.429 | -58.7402 | -58.7128 | -2.2247 | 64.4577 | -58.5434 | -58.5388 | -58.5114 | -58.6395 | -58.342 | -0.11444 | -0.054932 | -0.18768 | 0.11902 | -0.16479 | -0.19226 | -0.050354 | -0.077819 | 0.004578 | 0.004578 | -122.9919 | 0.036621 | 0.20599 | -0.091552 | 0.20142 | -0.09613 | 0.23346 | 122.9279 | 0.032043 | 0.004578 | 123.0606 | 123.0011 | 122.9462 | 123.0057 | -123.1155 | -122.9965 | 122.8134 | 0.009156 | 56.7535 | 56.3232
288.1719 | 123.111 | -58.5251 | 64.4531 | -0.03006 | 0.0010489 | 0.064803 | 0.064345 | 0.00058737 | -0.0016535 | 0.00072199 | 0.010864 | 0.0013159 | 0.0021362 | 0.0028368 | 0.00041649 | -2.5678e-05 | -0.0012561 | -1.8082 | 64.4211 | -58.6533 | 64.2334 | -58.4335 | -58.7631 | -58.754 | -2.2385 | 64.4897 | -58.5434 | -58.5571 | -58.5251 | -58.6533 | -58.3282 | -0.12817 | -0.032043 | -0.21973 | 0.091552 | -0.22888 | -0.23804 | -0.10071 | -0.10986 | -0.018311 | 0.036621 | -123.0103 | 0 | 0.19684 | -0.12817 | 0.21515 | -0.10986 | 0.21973 | 122.8867 | 0.018311 | -0.013733 | 123.0743 | 123.0331 | 122.9462 | 123.0148 | -123.1064 | -122.9965 | 122.7585 | -0.032044 | 56.7169 | 56.2866
289.1719 | 123.1201 | -58.5297 | 64.444 | -0.014801 | 0.0014761 | 0.063948 | 0.06755 | 0.00251 | 0.00091009 | -0.0012006 | 0.026123 | 3.4148e-05 | 0.0021362 | -0.003999 | -0.00065151 | 0.00061532 | 0.00066654 | -1.7944 | 64.4165 | -58.6578 | 64.2609 | -58.3878 | -58.754 | -58.7311 | -2.2247 | 64.4485 | -58.548 | -58.5251 | -58.5159 | -58.6258 | -58.3145 | -0.12817 | -0.027466 | -0.18311 | 0.14191 | -0.20142 | -0.2243 | -0.073242 | -0.09613 | -0.018311 | 0.004577 | -122.9691 | 0.013733 | 0.21515 | -0.09613 | 0.23346 | -0.077819 | 0.27008 | 122.9187 | 0.032044 | 0.022889 | 123.0743 | 122.9965 | 122.9462 | 122.9782 | -123.1018 | -122.9919 | 122.7905 | 0.004578 | 56.7352 | 56.3049
290.1719 | 123.1064 | -58.5434 | 64.476 | -0.022431 | -0.0017281 | 0.065871 | 0.065627 | -0.00026703 | -0.0029351 | -0.00077341 | 0.026123 | 0.0011023 | 0.0014954 | -0.0010084 | -0.00022431 | -0.00023928 | -0.00040166 | -1.8402 | 64.3982 | -58.6624 | 64.2242 | -58.4335 | -58.7997 | -58.7402 | -2.298 | 64.4485 | -58.5434 | -58.5709 | -58.548 | -58.6578 | -58.3466 | -0.11902 | -0.07782 | -0.25177 | 0.10986 | -0.19684 | -0.25635 | -0.077819 | -0.13733 | 0 | -0.027466 | -123.0469 | -0.004578 | 0.19684 | -0.11444 | 0.19684 | -0.11444 | 0.22888 | 122.8867 | -0.004578 | -0.027466 | 123.0606 | 122.9919 | 122.9416 | 122.9919 | -123.1384 | -123.0194 | 122.7676 | -0.027466 | 56.7032 | 56.2454
291.1719 | 123.1201 | -58.5205 | 64.4485 | -0.068207 | -0.00044654 | 0.063948 | 0.064559 | -0.00026703 | -0.00015811 | -0.0024822 | 0.026123 | 0.0017431 | 2.8e-08 | -0.0035718 | -0.0015061 | -0.00045288 | -0.0010425 | -1.8539 | 64.4348 | -58.6487 | 64.2197 | -58.4198 | -58.7402 | -58.7402 | -2.2705 | 64.4531 | -58.548 | -58.5342 | -58.5068 | -58.6166 | -58.3328 | -0.12817 | -0.013733 | -0.22888 | 0.10071 | -0.21973 | -0.21973 | -0.091552 | -0.091552 | -0.027466 | 0.004578 | -122.9828 | 0.013733 | 0.18768 | -0.09613 | 0.21515 | -0.068664 | 0.22888 | 122.8683 | 0.041199 | 0.013733 | 123.0835 | 123.0011 | 122.9553 | 122.9736 | -123.0972 | -122.9965 | 122.7402 | -0.013733 | 56.6666 | 56.25
292.1719 | 123.111 | -58.5205 | 64.476 | -0.014801 | 0.00019446 | 0.064375 | 0.06285 | 0.00016017 | -0.0016535 | -0.0012006 | 0.029175 | 0.0011023 | 0.0019226 | 0.00070062 | -0.0017197 | -0.00066648 | -0.0029651 | -1.8768 | 64.4257 | -58.6487 | 64.2426 | -58.4381 | -58.7631 | -58.7265 | -2.298 | 64.4623 | -58.5663 | -58.5663 | -58.5251 | -58.6395 | -58.342 | -0.12817 | -0.050354 | -0.23346 | 0.082398 | -0.20599 | -0.24262 | -0.077819 | -0.11444 | -0.045776 | -0.013733 | -123.0423 | -0.004577 | 0.17853 | -0.11902 | 0.2243 | -0.073242 | 0.21057 | 122.8912 | 0.041199 | 0 | 123.0743 | 123.0286 | 122.9462 | 122.9828 | -123.1247 | -123.0423 | 122.7631 | -0.045776 | 56.6437 | 56.2225
293.1719 | 123.1155 | -58.5159 | 64.476 | 0.008087 | 0.00083526 | 0.06523 | 0.063491 | -0.00069423 | -0.0014399 | 0.002431 | 0.032227 | 0.00067495 | 0.00064083 | -0.00015378 | -1.0706e-05 | -0.0028027 | 0.0017345 | -1.8951 | 64.4302 | -58.6441 | 64.2288 | -58.4198 | -58.7677 | -58.7494 | -2.3209 | 64.4577 | -58.5571 | -58.5571 | -58.4976 | -58.6487 | -58.342 | -0.12817 | -0.045776 | -0.24719 | 0.09613 | -0.23346 | -0.25177 | -0.10529 | -0.1236 | -0.041199 | -0.01831 | -123.0331 | 0.01831 | 0.17395 | -0.13275 | 0.21515 | -0.091553 | 0.2243 | 122.8729 | 0.059509 | 0 | 123.0743 | 123.0148 | 122.9462 | 122.9736 | -123.1201 | -123.0331 | 122.7448 | -0.041199 | 56.6208 | 56.1951
294.1719 | 123.1018 | -58.5205 | 64.4577 | 0.030975 | 0.0010489 | 0.064162 | 0.064559 | 0.0010148 | -0.0012261 | -0.0031232 | 0.023071 | 3.4148e-05 | 0.0014954 | -0.006349 | 0.00020289 | -0.00023928 | -0.0051013 | -1.9135 | 64.4348 | -58.6533 | 64.2151 | -58.4335 | -58.7769 | -58.7494 | -2.3346 | 64.4485 | -58.5342 | -58.548 | -58.5251 | -58.6441 | -58.3328 | -0.13275 | -0.022889 | -0.24262 | 0.086975 | -0.22888 | -0.25635 | -0.096131 | -0.1236 | -0.013733 | -0.009156 | -123.0057 | -0.004577 | 0.18768 | -0.1236 | 0.20142 | -0.10986 | 0.21973 | 122.8683 | 0.009156 | -0.013733 | 123.0881 | 122.9828 | 122.9553 | 122.9691 | -123.111 | -122.9919 | 122.7356 | -0.027466 | 56.6071 | 56.1859
295.1719 | 123.1476 | -58.5342 | 64.4394 | -0.014801 | -0.00023294 | 0.063734 | 0.063918 | 0.00080117 | 5.5488e-05 | -0.00013241 | -0.037964 | 3.4148e-05 | 0.00064083 | -0.0050672 | 0.0010575 | -0.00045288 | -0.0029651 | -1.9363 | 64.4119 | -58.6807 | 64.2609 | -58.3878 | -58.7723 | -58.8135 | -2.2614 | 64.4348 | -58.5617 | -58.5159 | -58.5205 | -58.6487 | -58.3191 | -0.14648 | -0.027466 | -0.17853 | 0.14648 | -0.27924 | -0.23804 | -0.13275 | -0.091553 | -0.027466 | -0.004578 | -122.9553 | 0.013733 | 0.21515 | -0.11444 | 0.24262 | -0.086975 | 0.29297 | 122.9416 | 0.041199 | 0.045777 | 123.0927 | 122.9965 | 122.9462 | 122.9691 | -123.1201 | -123.0011 | 122.7951 | 0.018311 | 56.5979 | 56.2729
296.1719 | 123.1064 | -58.5434 | 64.476 | 0.008087 | -0.00044654 | 0.062666 | 0.062423 | -0.0011214 | 5.5488e-05 | -0.003764 | 0.016968 | -0.00060665 | -0.0010682 | 0.003905 | -0.00065151 | -0.0017347 | 0.00088014 | -1.9913 | 64.4257 | -58.6807 | 64.2334 | -58.4427 | -58.7677 | -58.7585 | -2.3712 | 64.4531 | -58.5526 | -58.58 | -58.5526 | -58.6624 | -58.3557 | -0.13733 | -0.050354 | -0.24262 | 0.10071 | -0.21515 | -0.2243 | -0.07782 | -0.086975 | -0.009155 | -0.022888 | -123.056 | -0.009155 | 0.18768 | -0.11902 | 0.19684 | -0.10986 | 0.23804 | 122.9141 | 0 | -0.027466 | 123.1064 | 123.0057 | 122.9691 | 122.9965 | -123.1567 | -123.0286 | 122.7768 | -0.036621 | 56.5521 | 56.1722
297.1719 | 123.1064 | -58.548 | 64.4623 | -0.037689 | 0.00062166 | 0.062453 | 0.06285 | 0.0010148 | -0.00015811 | -0.0018414 | 0.023071 | 0.0013159 | 0.00021363 | -0.0018628 | 0.0010575 | -0.00023928 | 0.0015209 | -1.9043 | 64.476 | -58.6212 | 64.1968 | -58.429 | -58.7723 | -58.7448 | -2.3712 | 64.4485 | -58.5159 | -58.5663 | -58.5297 | -58.6533 | -58.3511 | -0.073242 | 0.013733 | -0.2655 | 0.11902 | -0.19684 | -0.2243 | -0.1236 | -0.15106 | 0.032044 | -0.013733 | -123.0286 | 0.018311 | 0.19684 | -0.10528 | 0.16479 | -0.13733 | 0.19226 | 122.818 | -0.013733 | -0.050354 | 123.0972 | 122.9645 | 123.024 | 122.9965 | -123.0835 | -122.9782 | 122.7448 | -0.01831 | 56.6437 | 56.1768
298.1719 | 123.1018 | -58.5434 | 64.476 | -0.014801 | 0.0010489 | 0.063948 | 0.06285 | 0.0020828 | -0.0018671 | -0.002055 | -0.0013428 | 0.0011023 | 0.00064083 | -0.0010084 | -0.00065151 | -0.00045288 | 0.0049389 | -2.005 | 64.4531 | -58.6624 | 64.0869 | -58.4152 | -58.754 | -58.7723 | -2.3941 | 64.4623 | -58.5709 | -58.5892 | -58.5526 | -58.6624 | -58.3694 | -0.11902 | -0.022888 | -0.3891 | 0.12817 | -0.22888 | -0.21057 | -0.10986 | -0.091552 | -0.027466 | -0.013733 | -123.0652 | -0.009155 | 0.17395 | -0.11902 | 0.20142 | -0.091553 | 0.24719 | 122.7493 | 0.018311 | -0.01831 | 123.1155 | 123.0331 | 122.9965 | 123.0057 | -123.1384 | -123.0469 | 122.6303 | -0.045776 | 56.5384 | 56.1493
299.1719 | 123.1201 | -58.5114 | 64.4577 | -0.014801 | 0.0014761 | 0.064589 | 0.063705 | 0.001442 | -0.00037171 | 0.00029479 | -0.019653 | 0.00067495 | -0.00042717 | 0.0017688 | -0.00043791 | -0.00045288 | 0.0021619 | -2.005 | 64.4348 | -58.6716 | 64.2654 | -58.3923 | -58.7677 | -58.7173 | -2.3483 | 64.4348 | -58.5297 | -58.5388 | -58.5159 | -58.6395 | -58.3328 | -0.16022 | -0.022889 | -0.19226 | 0.11902 | -0.20599 | -0.25635 | -0.045776 | -0.09613 | -0.01831 | -0.022889 | -122.9965 | -0.004577 | 0.17853 | -0.12817 | 0.19684 | -0.10986 | 0.27924 | 122.937 | 0.013733 | -0.009155 | 123.1064 | 122.9645 | 122.9462 | 122.9462 | -123.1293 | -122.9874 | 122.7768 | -0.027465 | 56.5063 | 56.163
300.1719 | 123.1018 | -58.5251 | 64.4348 | -0.014801 | 0.0016899 | 0.062666 | 0.064132 | 0.00080117 | 0.00026909 | 0.001363 | 0.001709 | 0.0013159 | 2.8e-08 | -0.0044262 | -0.0019333 | -2.5678e-05 | 0.0010937 | -2.0233 | 64.4073 | -58.6624 | 64.2746 | -58.3832 | -58.7585 | -58.7128 | -2.3254 | 64.4348 | -58.5205 | -58.5205 | -58.5205 | -58.6395 | -58.3328 | -0.13733 | -0.027465 | -0.16022 | 0.14191 | -0.18768 | -0.23346 | -0.050354 | -0.09613 | 0.004577 | 0 | -122.9553 | 0.004577 | 0.19226 | -0.11444 | 0.18768 | -0.11902 | 0.27924 | 122.937 | 0 | 0 | 123.0698 | 122.9553 | 122.9324 | 122.9599 | -123.0972 | -122.9553 | 122.7997 | 0.004577 | 56.5018 | 56.1996
301.1719 | 123.1659 | -58.5068 | 64.4485 | -0.022431 | -0.00066014 | 0.063521 | 0.064559 | -0.00026703 | -0.0018671 | 0.003072 | 0.016968 | -0.00017945 | 0.00064083 | -0.0035718 | 0.00020289 | -0.0017347 | -0.0016833 | -2.0508 | 64.4119 | -58.6899 | 64.2609 | -58.3923 | -58.754 | -58.7311 | -2.3438 | 64.4531 | -58.5205 | -58.548 | -58.5068 | -58.6258 | -58.3328 | -0.18311 | -0.036621 | -0.18768 | 0.11444 | -0.2243 | -0.24719 | -0.041199 | -0.064087 | -0.013733 | 0.004578 | -122.9965 | 0 | 0.17395 | -0.11902 | 0.18768 | -0.10529 | 0.29755 | 122.9507 | 0.013733 | -0.027466 | 123.1018 | 122.9736 | 122.9187 | 122.9599 | -123.1384 | -122.9691 | 122.7676 | -0.041199 | 56.456 | 56.163
302.1719 | 123.0789 | -58.5205 | 64.4714 | 0.00045798 | -0.00066014 | 0.063948 | 0.062209 | -0.0038986 | 0.00069649 | 0.00093559 | 0.03833 | 0.0011023 | 0.002777 | 0.0013416 | 0.0010575 | -0.0017347 | -0.0016833 | -2.1103 | 64.4394 | -58.6624 | 64.2151 | -58.4427 | -58.7585 | -58.7631 | -2.4033 | 64.4348 | -58.5022 | -58.5617 | -58.5434 | -58.6533 | -58.3511 | -0.14191 | -0.032044 | -0.25635 | 0.07782 | -0.24262 | -0.23804 | -0.10071 | -0.09613 | 0.018311 | -0.036622 | -123.0331 | -0.022888 | 0.16937 | -0.13275 | 0.15106 | -0.15106 | 0.21973 | 122.8775 | -0.041199 | -0.05951 | 123.1018 | 122.937 | 122.9599 | 122.9553 | -123.1339 | -122.9736 | 122.7356 | -0.041199 | 56.4102 | 56.1172
303.1719 | 123.1155 | -58.5297 | 64.4302 | 0.030975 | 0.0021171 | 0.064162 | 0.063705 | -0.0028304 | -0.00015811 | -0.0016278 | -0.0043946 | -0.00017945 | 0.0012818 | -0.00058098 | -0.0015061 | 0.00018792 | -0.0010425 | -2.124 | 64.444 | -58.667 | 64.2563 | -58.4015 | -58.7448 | -58.7219 | -2.3895 | 64.444 | -58.5526 | -58.548 | -58.5114 | -58.6166 | -58.3328 | -0.13733 | 0.013733 | -0.17395 | 0.12817 | -0.19226 | -0.21515 | -0.054932 | -0.07782 | -0.022888 | 0.013733 | -122.9782 | 0.01831 | 0.19684 | -0.086975 | 0.21973 | -0.064087 | 0.2655 | 122.9233 | 0.041198 | 0.004577 | 123.111 | 122.9965 | 122.9736 | 122.9736 | -123.0972 | -122.9828 | 122.7859 | -0.018311 | 56.4056 | 56.1401
304.1719 | 123.1384 | -58.5342 | 64.4028 | -0.10635 | 0.0019035 | 0.06523 | 0.061141 | -0.0032578 | -0.0012261 | -0.0018414 | 0.065796 | -0.0014613 | 0.00064083 | -0.007417 | -0.0019333 | -2.5678e-05 | 0.00066654 | -2.2202 | 64.3936 | -58.6578 | 64.3295 | -58.2779 | -58.6807 | -58.7677 | -2.4673 | 64.3799 | -58.548 | -58.5434 | -58.4885 | -58.6029 | -58.3054 | -0.1236 | -0.009155 | -0.073242 | 0.25635 | -0.23346 | -0.14648 | -0.10986 | -0.022888 | -0.013733 | -0.022888 | -122.9462 | 0.045777 | 0.22888 | -0.068664 | 0.24262 | -0.054931 | 0.37994 | 122.9874 | 0.05951 | 0.004578 | 123.0515 | 122.9279 | 122.9279 | 122.9141 | -123.0606 | -122.9507 | 122.8638 | -0.009155 | 56.3141 | 56.0669
305.1719 | 123.1201 | -58.5434 | 64.4623 | -0.037689 | -0.00066014 | 0.064162 | 0.064773 | -0.0026168 | 0.00048269 | -0.0016278 | -0.0013428 | 0.00088875 | 0.0023498 | 0.00091422 | -0.00086511 | -0.0017347 | -0.00061526 | -2.1927 | 64.4165 | -58.6487 | 64.2426 | -58.4244 | -58.7769 | -58.7494 | -2.4536 | 64.476 | -58.5342 | -58.5526 | -58.5068 | -58.6441 | -58.3374 | -0.10529 | -0.045776 | -0.21973 | 0.11902 | -0.20599 | -0.23346 | -0.10071 | -0.12817 | 0.009155 | 0.013733 | -123.0148 | 0.036621 | 0.20599 | -0.10071 | 0.19684 | -0.10986 | 0.22431 | 122.8912 | 0.027466 | -0.01831 | 123.0652 | 123.0103 | 122.9599 | 123.0194 | -123.111 | -122.9965 | 122.7859 | -0.009155 | 56.3507 | 56.0898
306.1719 | 123.1247 | -58.5251 | 64.4806 | 0.061493 | -1.9142e-05 | 0.063307 | 0.064559 | -0.001976 | -0.0016535 | -0.0018414 | -0.01355 | 0.00024775 | 0.001709 | 0.001128 | -0.00065151 | -0.0021619 | 0.0015209 | -2.2156 | 64.4531 | -58.6395 | 64.2288 | -58.4335 | -58.7952 | -58.7585 | -2.4811 | 64.4623 | -58.5434 | -58.5663 | -58.5114 | -58.6349 | -58.3466 | -0.11444 | -0.027466 | -0.25177 | 0.091552 | -0.23346 | -0.27008 | -0.11902 | -0.15564 | -0.018311 | -0.018311 | -123.0469 | 0.013732 | 0.17853 | -0.10986 | 0.19684 | -0.091553 | 0.20599 | 122.8683 | 0.032043 | -0.022888 | 123.0927 | 123.0057 | 122.9782 | 122.9874 | -123.1201 | -123.024 | 122.7539 | -0.041199 | 56.3095 | 56.044
307.1719 | 123.1201 | -58.5114 | 64.4669 | -0.045319 | 0.0010489 | 0.062239 | 0.062636 | -0.0015488 | -0.00058531 | 8.1188e-05 | -0.0043946 | 0.0015295 | 2.8e-08 | 0.0017688 | 0.00020289 | -0.0023755 | -0.00040166 | -2.2202 | 64.4257 | -58.6349 | 64.2654 | -58.4015 | -58.7448 | -58.7265 | -2.4445 | 64.4714 | -58.5205 | -58.5342 | -58.4885 | -58.6487 | -58.3328 | -0.1236 | -0.041199 | -0.20142 | 0.10986 | -0.21515 | -0.23346 | -0.091552 | -0.10986 | -0.009155 | 0.004578 | -123.0011 | 0.022889 | 0.17853 | -0.13733 | 0.18768 | -0.12817 | 0.23346 | 122.9004 | 0.032044 | -0.013733 | 123.0606 | 122.9919 | 122.937 | 122.9828 | -123.1018 | -122.9874 | 122.7768 | -0.022888 | 56.2912 | 56.0669
308.1719 | 123.0789 | -58.4976 | 64.4623 | -0.037689 | -0.00066014 | 0.061171 | 0.066054 | 0.0027238 | 5.5488e-05 | -0.0041912 | 0.0047608 | 0.00046135 | -0.0012818 | 0.0062548 | -1.0706e-05 | -0.0010937 | 0.00066654 | -2.1194 | 64.4806 | -58.6212 | 64.1922 | -58.4564 | -58.7585 | -58.7494 | -2.5085 | 64.4852 | -58.5571 | -58.58 | -58.5434 | -58.6578 | -58.3603 | -0.1236 | 0.018311 | -0.27008 | 0.041199 | -0.25177 | -0.26093 | -0.12817 | -0.13733 | -0.059509 | 0.022888 | -123.0423 | -0.045776 | 0.13733 | -0.16022 | 0.19684 | -0.10071 | 0.16479 | 122.8134 | 0.013733 | -0.022888 | 123.1018 | 123.0423 | 122.9782 | 122.9828 | -123.0835 | -123.0194 | 122.6898 | -0.082397 | 56.3782 | 55.9891
309.1719 | 123.2117 | -58.4976 | 64.389 | -0.10635 | 0.00019446 | 0.067366 | 0.064773 | 0.00058737 | 0.00026909 | -0.0016278 | 0.035278 | -0.0010339 | -0.00085457 | 0.0019824 | 0.00041649 | -0.0010937 | -0.00018806 | -2.3346 | 64.3433 | -58.6487 | 64.3066 | -58.3466 | -58.7448 | -58.6899 | -2.5085 | 64.3433 | -58.5617 | -58.5251 | -58.3054 | -58.548 | -58.287 | -0.15106 | -0.045776 | -0.082397 | 0.15106 | -0.19226 | -0.24719 | -0.041198 | -0.09613 | -0.064087 | -0.045776 | -122.9141 | 0.19226 | 0.21057 | -0.050354 | 0.27466 | 0.013733 | 0.30212 | 122.9553 | 0.25635 | 0.036622 | 122.9919 | 122.905 | 122.8409 | 122.8409 | -123.0377 | -122.9507 | 122.8043 | -0.027465 | 56.163 | 55.9891
310.1719 | 123.1018 | -58.5159 | 64.4669 | -0.03006 | -1.9142e-05 | 0.063094 | 0.06285 | 0.0012284 | -0.00079891 | -0.00013241 | 0.026123 | -0.00039305 | -0.0012818 | -0.00015378 | 0.00041649 | -0.0034437 | -0.0012561 | -2.2934 | 64.4211 | -58.6121 | 64.27 | -58.3466 | -58.7357 | -58.6761 | -2.4948 | 64.4577 | -58.5297 | -58.5571 | -58.5159 | -58.6304 | -58.342 | -0.096131 | -0.045776 | -0.19684 | 0.16937 | -0.16022 | -0.21973 | -0.064086 | -0.1236 | -0.013733 | -0.009155 | -123.024 | 0 | 0.17395 | -0.11444 | 0.18768 | -0.10071 | 0.2655 | 122.8821 | 0.013733 | -0.027466 | 123.0331 | 122.9874 | 122.937 | 122.9736 | -123.0789 | -122.9965 | 122.7859 | -0.041199 | 56.2225 | 56.0211
311.1719 | 123.0789 | -58.5526 | 64.4623 | -0.014801 | -0.00023294 | 0.063734 | 0.060073 | -0.0034714 | -0.0014399 | 8.1188e-05 | 0.023071 | 0.0017431 | 0.001068 | 0.0017688 | -0.00065151 | -0.0025891 | -0.0010425 | -2.4033 | 64.4394 | -58.6349 | 64.2426 | -58.429 | -58.7723 | -58.7448 | -2.5681 | 64.4897 | -58.5251 | -58.5297 | -58.6533 | -58.8226 | -58.374 | -0.082398 | -0.022888 | -0.21973 | 0.1236 | -0.19226 | -0.21973 | -0.10986 | -0.13733 | 0.027466 | 0.027466 | -122.9919 | -0.10071 | 0.17853 | -0.27008 | 0.15106 | -0.29755 | 0.20599 | 122.8775 | -0.12817 | -0.004578 | 123.0743 | 123.0148 | 122.9919 | 123.0423 | -123.0972 | -122.9874 | 122.7951 | 0.022888 | 56.1493 | 55.9845
312.1719 | 123.1018 | -58.4976 | 64.4943 | 0.030975 | -0.0015145 | 0.063734 | 0.063705 | -0.00069423 | -0.0020807 | 0.001363 | -0.0074462 | 0.00067495 | 0.0014954 | -0.00015378 | -0.00043791 | -0.0013073 | 0.00088014 | -2.4353 | 64.4165 | -58.6624 | 64.2197 | -58.429 | -58.7677 | -58.7402 | -2.6001 | 64.444 | -58.5571 | -58.5663 | -58.5251 | -58.6624 | -58.342 | -0.1648 | -0.07782 | -0.27466 | 0.068665 | -0.24261 | -0.27008 | -0.077819 | -0.10528 | -0.059509 | -0.050354 | -123.0606 | -0.027465 | 0.15564 | -0.1648 | 0.21515 | -0.10529 | 0.23346 | 122.8821 | 0.032044 | -0.009155 | 123.0789 | 123.0011 | 122.9141 | 122.9416 | -123.1567 | -123.0515 | 122.7173 | -0.068664 | 56.0623 | 55.8975
313.1719 | 123.1613 | -58.5068 | 64.4394 | -0.022431 | 0.0016899 | 0.062666 | 0.065414 | -0.00069423 | 0.0024053 | 0.0020038 | -0.01355 | 0.0013159 | -0.00085457 | -0.0018628 | -0.0010787 | -0.0017347 | -0.0014697 | -2.4399 | 64.4531 | -58.6395 | 64.2563 | -58.4106 | -58.7402 | -58.7173 | -2.5726 | 64.4623 | -58.5205 | -58.5342 | -58.5205 | -58.6212 | -58.3099 | -0.13275 | 0.013733 | -0.1831 | 0.09613 | -0.21057 | -0.23346 | -0.07782 | -0.10071 | -0.013733 | 0.022888 | -122.9736 | -0.013733 | 0.19684 | -0.11444 | 0.21057 | -0.10071 | 0.22888 | 122.8958 | 0 | -0.013733 | 123.0927 | 122.9828 | 122.9599 | 122.9691 | -123.0789 | -122.9599 | 122.7631 | -0.027466 | 56.0669 | 55.9341
314.1719 | 123.1659 | -58.5709 | 64.4302 | -0.068207 | 0.0014761 | 0.066298 | 0.064559 | 0.0052872 | -0.00015811 | 0.00029479 | -0.03186 | 0.00046135 | 0.0014954 | -0.00015378 | -0.0015061 | 0.00018792 | 0.00066654 | -2.5726 | 64.4211 | -58.699 | 64.1693 | -58.5251 | -58.873 | -58.8318 | -2.742 | 64.4302 | -58.5892 | -58.5892 | -58.5434 | -59.1202 | -58.6533 | -0.12817 | -0.009155 | -0.26093 | 0.045777 | -0.26093 | -0.30212 | -0.13275 | -0.17395 | -0.01831 | 0 | -123.0194 | 0.027466 | -0.082397 | -0.54932 | -0.064087 | -0.53101 | 0.17395 | 122.8683 | 0.045776 | 0 | 123.1201 | 123.0194 | 122.9919 | 123.0011 | -123.1293 | -123.0194 | 122.7402 | -0.01831 | 55.9982 | 55.8289
315.1719 | 123.1384 | -58.5022 | 64.4485 | -0.052948 | 0.00040806 | 0.063734 | 0.063491 | 0.00037377 | -0.0012261 | -0.0012006 | 0.032227 | 0.00024775 | 0.0025634 | -0.005708 | 0.00084389 | -0.00088008 | -0.00082886 | -2.5314 | 64.4302 | -58.6441 | 64.238 | -58.4198 | -58.7723 | -58.7448 | -2.6505 | 64.4714 | -58.5388 | -58.5388 | -58.4839 | -58.6212 | -58.3237 | -0.14191 | -0.01831 | -0.21057 | 0.082397 | -0.24262 | -0.27008 | -0.10071 | -0.12817 | -0.036621 | 0.022889 | -122.9874 | 0.01831 | 0.17853 | -0.11902 | 0.21515 | -0.082398 | 0.2243 | 122.8821 | 0.054931 | 0 | 123.0743 | 123.0103 | 122.9324 | 122.9736 | -123.0927 | -122.9874 | 122.7402 | -0.036621 | 55.9708 | 55.8517
316.1719 | 123.1201 | -58.5342 | 64.4577 | -0.052948 | 0.00019446 | 0.063094 | 0.063064 | -0.0017624 | -0.0012261 | -0.00077341 | 0.016968 | 0.0011023 | 0.00064083 | -0.005708 | 0.0014847 | 0.00040152 | 0.00066654 | -2.5772 | 64.4348 | -58.6304 | 64.2426 | -58.4198 | -58.7585 | -58.7173 | -2.6779 | 64.4669 | -58.5159 | -58.5709 | -58.5526 | -58.6533 | -58.3511 | -0.09613 | -0.022889 | -0.21515 | 0.11444 | -0.1831 | -0.2243 | -0.086975 | -0.12817 | 0.018311 | 0.009155 | -123.0286 | -0.01831 | 0.18311 | -0.11902 | 0.16479 | -0.13733 | 0.21057 | 122.8729 | -0.036621 | -0.054932 | 123.0652 | 122.9828 | 122.9691 | 123.0011 | -123.0881 | -122.9736 | 122.7768 | -0.036621 | 55.957 | 55.8563
317.1719 | 123.1018 | -58.5159 | 64.4577 | -0.0071715 | 0.00062166 | 0.063307 | 0.064559 | -0.00090783 | 0.00091009 | 0.0020038 | -0.010498 | 0.00088875 | 0.0019226 | 0.0036914 | -0.0021469 | -0.0019483 | 0.00023934 | -2.6184 | 64.4485 | -58.6853 | 64.2426 | -58.429 | -58.7677 | -58.7402 | -2.6917 | 64.4714 | -58.5526 | -58.5617 | -58.5388 | -58.6487 | -58.3328 | -0.16937 | -0.009156 | -0.21515 | 0.086975 | -0.2243 | -0.25177 | -0.054931 | -0.082397 | -0.036621 | 0.013733 | -123.0194 | -0.022888 | 0.1831 | -0.13275 | 0.21973 | -0.096131 | 0.25635 | 122.9279 | 0.013733 | -0.009156 | 123.1338 | 123.024 | 122.9645 | 122.9874 | -123.143 | -123.0103 | 122.7585 | -0.045777 | 55.8975 | 55.8243
318.1719 | 123.0789 | -58.5205 | 64.4806 | -0.052948 | -0.00044654 | 0.065016 | 0.063491 | -0.0017624 | -0.00058531 | -0.0039776 | 0.0078126 | 0.0025975 | -0.00064077 | -0.0025036 | -0.00043791 | -2.5678e-05 | -0.0016833 | -2.7832 | 64.4394 | -58.667 | 64.2242 | -58.429 | -58.7769 | -58.7494 | -2.7191 | 64.4943 | -58.5342 | -58.5617 | -58.5297 | -58.6349 | -58.3466 | -0.14648 | -0.041199 | -0.25635 | 0.091553 | -0.22888 | -0.25635 | -0.082398 | -0.10986 | -0.013733 | 0.013733 | -123.0423 | -0.009155 | 0.17395 | -0.11444 | 0.18768 | -0.10071 | 0.23804 | 122.8912 | 0.004578 | -0.027466 | 123.1064 | 123.0286 | 122.9599 | 123.0148 | -123.1476 | -123.0148 | 122.7448 | -0.041199 | 55.7373 | 55.8014
319.1719 | 123.0698 | -58.5159 | 64.4943 | -0.045319 | 0.00019446 | 0.065016 | 0.061782 | -0.0015488 | -0.0012261 | -0.002696 | -0.0074462 | 0.0015295 | 0.0021362 | -0.002931 | -0.00065151 | -0.00088008 | 0.0030163 | -2.6917 | 64.4623 | -58.6441 | 64.1693 | -58.5892 | -58.7448 | -58.7448 | -2.742 | 64.4623 | -58.5571 | -58.5663 | -58.5342 | -58.6395 | -58.3466 | -0.12817 | -0.032044 | -0.32501 | -0.073242 | -0.22888 | -0.22888 | -0.10071 | -0.10071 | -0.041199 | -0.032044 | -123.0606 | -0.018311 | 0.16937 | -0.1236 | 0.21057 | -0.082397 | 0.054932 | 122.8134 | 0.022888 | -0.009155 | 123.1064 | 123.0194 | 122.9782 | 122.9782 | -123.1384 | -123.0515 | 122.6852 | -0.050354 | 55.8243 | 55.7739
320.1719 | 123.0515 | -58.5159 | 64.476 | -0.022431 | 0.00040806 | 0.062666 | 0.064773 | 0.00016017 | 0.00026909 | 0.00050839 | 0.071899 | 0.0032385 | 0.0025634 | 0.0066822 | 0.0010575 | -0.00045288 | 0.0010937 | -2.7237 | 64.4577 | -58.6166 | 64.2334 | -58.4198 | -58.7631 | -58.7219 | -2.7603 | 64.5218 | -58.5251 | -58.5938 | -58.5297 | -58.6533 | -58.3694 | -0.10071 | -0.01831 | -0.24262 | 0.09613 | -0.20599 | -0.24719 | -0.10529 | -0.14648 | -0.009155 | 0.045777 | -123.0698 | -0.013733 | 0.14648 | -0.13733 | 0.15564 | -0.12817 | 0.19684 | 122.85 | -0.004578 | -0.068665 | 123.0743 | 123.0469 | 122.9736 | 123.0377 | -123.0927 | -123.0011 | 122.7493 | -0.07782 | 55.7922 | 55.7556
321.1719 | 123.0881 | -58.5388 | 64.4714 | 0.00045798 | 0.00083526 | 0.062025 | 0.06285 | -0.00026703 | -0.00079891 | -0.0012006 | 0.03833 | 0.0019567 | 0.0014954 | 0.00027342 | -0.00043791 | -0.0042981 | 0.00066654 | -2.774 | 64.4394 | -58.6395 | 64.2426 | -58.4015 | -58.7494 | -58.7173 | -2.7695 | 64.4623 | -58.5342 | -58.4198 | -58.5114 | -58.8364 | -58.5297 | -0.10071 | -0.032044 | -0.22888 | 0.13733 | -0.17853 | -0.21057 | -0.07782 | -0.10986 | 0.004577 | -0.009156 | -122.8912 | 0.027465 | 0.009155 | -0.29755 | 0.004578 | -0.30212 | 0.23804 | 122.8821 | 0.022888 | 0.11444 | 123.0789 | 122.9965 | 122.9782 | 123.0011 | -123.111 | -123.0057 | 122.7814 | 0.11902 | 55.7648 | 55.7693
322.1719 | 123.0972 | -58.5159 | 64.4852 | -0.014801 | 0.00019446 | 0.063094 | 0.063277 | -0.0013352 | -0.00058531 | 0.001363 | 0.032227 | 0.0019567 | 0.001068 | -0.0018628 | -0.00022431 | -0.0015211 | 0.00066654 | -2.7832 | 64.4623 | -58.6441 | 64.2563 | -58.3923 | -58.7631 | -58.7219 | -2.7924 | 64.4669 | -58.5251 | -58.5754 | -58.5297 | -58.6304 | -58.3511 | -0.12817 | -0.022888 | -0.22888 | 0.1236 | -0.20599 | -0.24719 | -0.07782 | -0.11902 | -0.009155 | -0.01831 | -123.0606 | -0.013733 | 0.16479 | -0.11444 | 0.17395 | -0.10529 | 0.25177 | 122.9004 | -0.004578 | -0.050354 | 123.1064 | 122.9919 | 122.9782 | 122.9828 | -123.1293 | -123.0103 | 122.7722 | -0.059509 | 55.7327 | 55.7236
323.1719 | 123.0835 | -58.5297 | 64.476 | 0.00045798 | -0.0015145 | 0.062453 | 0.06285 | 0.0027238 | -0.00079891 | -0.0033368 | 0.023071 | -0.00017945 | 0.0012818 | 0.00070062 | -0.0015061 | 0.00018792 | -0.0010425 | -2.8152 | 64.4485 | -58.6533 | 64.2746 | -58.5159 | -58.9828 | -58.7631 | -2.8427 | 64.4577 | -58.5297 | -58.5571 | -58.5342 | -58.6395 | -58.3557 | -0.1236 | -0.027466 | -0.20142 | 0.013733 | -0.23346 | -0.45319 | -0.10986 | -0.32959 | 0 | -0.01831 | -123.0331 | -0.004578 | 0.17395 | -0.10986 | 0.17395 | -0.10986 | 0.13733 | 122.9279 | -0.004578 | -0.027466 | 123.1018 | 122.9874 | 122.9782 | 122.9874 | -123.1293 | -123.0057 | 122.8043 | -0.027466 | 55.7144 | 55.687
324.1719 | 123.1155 | -58.5159 | 64.476 | -0.068207 | 0.0021171 | 0.060103 | 0.063064 | 0.001442 | -0.0012261 | -0.002696 | 0.026123 | 0.00024775 | 0.00042723 | -0.002931 | -0.00086511 | -0.0023755 | -0.0016833 | -2.8015 | 64.4165 | -58.6349 | 64.2975 | -58.3374 | -58.6945 | -58.667 | -2.7924 | 64.4943 | -58.5297 | -58.5571 | -58.493 | -58.5938 | -58.3374 | -0.11902 | -0.059509 | -0.17853 | 0.17853 | -0.15106 | -0.17853 | -0.032043 | -0.059509 | -0.013733 | 0.018311 | -123.0331 | 0.022888 | 0.17853 | -0.07782 | 0.19226 | -0.064087 | 0.29755 | 122.9324 | 0.036621 | -0.027466 | 123.0515 | 123.024 | 122.9324 | 123.0103 | -123.111 | -123.0057 | 122.8134 | -0.041199 | 55.7144 | 55.7236
325.1719 | 123.0286 | -58.5205 | 64.5081 | -0.12161 | 0.00019446 | 0.062025 | 0.063705 | -0.0028304 | 0.0015509 | 0.0011494 | 0.035278 | 0.00088875 | 0.00064083 | -0.00229 | -0.00043791 | 0.00061532 | 0.00023934 | -2.8748 | 64.4531 | -58.6349 | 64.2563 | -58.4061 | -58.754 | -58.7265 | -2.8748 | 64.4989 | -58.5251 | -58.5571 | -58.5159 | -58.6441 | -58.3694 | -0.11444 | -0.054932 | -0.25177 | 0.11444 | -0.20599 | -0.23346 | -0.091552 | -0.11902 | -0.004577 | -0.009156 | -123.0652 | 0.004578 | 0.15106 | -0.1236 | 0.15564 | -0.11902 | 0.22888 | 122.8912 | 0.009155 | -0.032044 | 123.0881 | 123.024 | 122.9736 | 123.0194 | -123.143 | -123.0331 | 122.7768 | -0.036621 | 55.6458 | 55.6458
326.1719 | 123.0652 | -58.4976 | 64.4623 | -0.060578 | 0.0014761 | 0.064803 | 0.063277 | 0.0018692 | -0.0025079 | 0.00072199 | 0.013916 | 3.4148e-05 | 0.001068 | 0.0028368 | -0.00022431 | -0.0015211 | -0.0025379 | -2.8976 | 64.4531 | -58.6258 | 64.2746 | -58.3832 | -58.7677 | -58.6807 | -2.8885 | 64.4852 | -58.5342 | -58.548 | -58.5159 | -58.6212 | -58.3511 | -0.12817 | -0.009155 | -0.18768 | 0.11444 | -0.18311 | -0.27008 | -0.054932 | -0.14191 | -0.036621 | 0.022888 | -123.0103 | -0.01831 | 0.14648 | -0.1236 | 0.18311 | -0.086975 | 0.24261 | 122.9004 | 0.018311 | -0.013733 | 123.0789 | 123.0194 | 122.9507 | 122.9828 | -123.0881 | -122.9965 | 122.7722 | -0.050354 | 55.6 | 55.6091
327.1719 | 123.0743 | -58.5297 | 64.4852 | -0.083466 | -0.00023294 | 0.064803 | 0.063918 | -0.0017624 | -0.0014399 | -0.00034601 | 0.02002 | 3.4148e-05 | -0.0012818 | 0.00048702 | -0.0010787 | -0.0017347 | -0.00040166 | -2.98 | 64.4348 | -58.6304 | 64.2426 | -58.4152 | -58.7631 | -58.7173 | -2.8976 | 64.5172 | -58.5022 | -58.5342 | -58.5663 | -58.6395 | -58.3511 | -0.10071 | -0.050354 | -0.24261 | 0.11444 | -0.18768 | -0.23346 | -0.086975 | -0.13275 | 0.027466 | 0.032044 | -123.0194 | -0.036621 | 0.17853 | -0.10986 | 0.15106 | -0.13733 | 0.21515 | 122.8729 | -0.064087 | -0.032044 | 123.0652 | 123.0194 | 122.9645 | 123.0469 | -123.1155 | -122.9874 | 122.7722 | -0.004578 | 55.5496 | 55.632
328.1719 | 123.1476 | -58.5068 | 64.476 | -0.083466 | 0.00062166 | 0.064162 | 0.061141 | -0.0011214 | -0.0016535 | -0.00034601 | 0.053589 | -0.00017945 | 0.0023498 | -0.0033582 | 0.00020289 | -0.0021619 | -0.0025379 | -2.9388 | 64.4165 | -58.6166 | 64.357 | -58.3054 | -58.6716 | -58.6258 | -2.8427 | 64.4485 | -58.5068 | -58.5159 | -58.4518 | -58.5754 | -58.3008 | -0.10986 | -0.059509 | -0.11902 | 0.20142 | -0.11902 | -0.1648 | -0.009155 | -0.054932 | 0 | -0.027466 | -122.9919 | 0.054932 | 0.20599 | -0.068664 | 0.20599 | -0.068664 | 0.31128 | 122.9736 | 0.054932 | -0.009155 | 123.0331 | 122.9553 | 122.9233 | 122.9553 | -123.0927 | -122.9828 | 122.8638 | -0.009155 | 55.5679 | 55.6641
329.1719 | 123.1155 | -58.5159 | 64.444 | 0.015716 | 0.00083526 | 0.064803 | 0.066482 | -5.343e-05 | -0.00015811 | -0.002696 | -0.022705 | 0.0019567 | 0.0012818 | -0.00015378 | -0.0012925 | -0.00023928 | -0.00018806 | -3.0029 | 64.4257 | -58.6487 | 64.2746 | -58.374 | -58.7402 | -58.7036 | -2.9205 | 64.4531 | -58.5114 | -58.5114 | -58.4976 | -58.6121 | -58.3191 | -0.13275 | -0.018311 | -0.16937 | 0.14191 | -0.18768 | -0.2243 | -0.054931 | -0.091552 | 0.004577 | 0.009155 | -122.9553 | 0.01831 | 0.19684 | -0.096131 | 0.19226 | -0.10071 | 0.27466 | 122.9233 | 0.013733 | 0 | 123.0743 | 122.9645 | 122.9416 | 122.9691 | -123.0927 | -122.9553 | 122.7905 | 0.004577 | 55.513 | 55.5954
330.1719 | 123.1659 | -58.4656 | 64.4302 | 0.25223 | -0.00087374 | 0.06523 | 0.060714 | 0.0012284 | -0.00037171 | 8.1188e-05 | 0.059692 | -0.0016749 | 0.00085443 | -0.00058098 | -1.0706e-05 | -0.0015211 | 0.00023934 | -3.1906 | 64.3982 | -58.6029 | 64.3524 | -58.2916 | -58.667 | -58.6075 | -2.8748 | 64.4211 | -58.5022 | -58.4564 | -58.3969 | -58.5114 | -58.2413 | -0.13733 | -0.032044 | -0.07782 | 0.17395 | -0.14191 | -0.20142 | -0.004578 | -0.064087 | -0.036621 | -0.009155 | -122.8867 | 0.068664 | 0.2243 | -0.045777 | 0.26093 | -0.009156 | 0.31128 | 122.9553 | 0.10529 | 0.045776 | 123.0011 | 122.9233 | 122.8638 | 122.8867 | -123.0331 | -122.9324 | 122.818 | 0.009155 | 55.275 | 55.5908
331.1719 | 123.1705 | -58.4656 | 64.4577 | -0.083466 | 0.0014761 | 0.064375 | 0.063491 | -0.0013352 | 0.00048269 | -0.00098701 | 0.041382 | -0.0012477 | 0.00042723 | -0.00058098 | -0.00043791 | -0.0023755 | -0.00040166 | -3.0624 | 64.4119 | -58.5892 | 64.357 | -58.2916 | -58.6533 | -58.6121 | -2.9068 | 64.4531 | -58.5068 | -58.4839 | -58.4335 | -58.548 | -58.2642 | -0.1236 | -0.045777 | -0.10071 | 0.17395 | -0.14648 | -0.18768 | -0.022889 | -0.064087 | -0.041199 | -0.004578 | -122.9416 | 0.032043 | 0.20142 | -0.082398 | 0.24262 | -0.041199 | 0.29755 | 122.9462 | 0.073242 | 0.022888 | 123.0011 | 122.9599 | 122.8775 | 122.9187 | -123.0469 | -122.9645 | 122.8226 | -0.018311 | 55.4031 | 55.5588
332.1719 | 123.2666 | -58.4244 | 64.4669 | -0.052948 | -0.00044654 | 0.063948 | 0.062636 | 0.001442 | 0.0019781 | -0.00077341 | 0.059692 | 0.00024775 | -0.00042717 | -0.0042126 | -0.0010787 | -0.00045288 | -0.00061526 | -3.1082 | 64.4028 | -58.5983 | 64.3799 | -58.2413 | -58.6349 | -58.5892 | -2.8976 | 64.4302 | -58.493 | -58.4473 | -58.3969 | -58.3694 | -57.9758 | -0.17395 | -0.064087 | -0.086975 | 0.1831 | -0.16479 | -0.21057 | 0.009156 | -0.036621 | -0.068665 | -0.036621 | -122.9141 | 0.027465 | 0.44861 | 0.054931 | 0.51727 | 0.1236 | 0.35706 | 122.9782 | 0.09613 | 0.045776 | 123.0011 | 122.9233 | 122.8271 | 122.8546 | -123.0652 | -122.9599 | 122.8043 | -0.022889 | 55.3162 | 55.5267
333.1719 | 123.0743 | -58.5114 | 64.5126 | -0.0071715 | -0.0015145 | 0.064162 | 0.064773 | 0.0050736 | 0.0015509 | -0.0012006 | -0.010498 | 0.00067495 | 0.00042723 | -0.0014356 | -0.0019333 | -0.0015211 | -0.00018806 | -3.186 | 64.4577 | -58.6441 | 64.2654 | -58.3878 | -58.7357 | -58.7036 | -3.0487 | 64.4989 | -58.5342 | -58.5342 | -58.5159 | -58.6212 | -58.3466 | -0.13275 | -0.054931 | -0.24719 | 0.1236 | -0.19226 | -0.2243 | -0.059509 | -0.091553 | -0.022888 | -0.013733 | -123.0469 | -0.004577 | 0.16479 | -0.10986 | 0.18768 | -0.086975 | 0.25635 | 122.9095 | 0.018311 | 0 | 123.1018 | 123.0331 | 122.9691 | 123.0103 | -123.1567 | -123.0469 | 122.7768 | -0.022888 | 55.3253 | 55.4626
334.1719 | 123.2208 | -58.4793 | 64.4394 | -0.03006 | -0.00087374 | 0.06523 | 0.061141 | 0.00058737 | 0.0032599 | 0.001363 | 0.044434 | -0.00060665 | -0.00021357 | 0.0034778 | 0.00063009 | -0.0025891 | 0.00023934 | -3.1494 | 64.4119 | -58.6075 | 64.3936 | -58.2321 | -58.6304 | -58.5983 | -2.948 | 64.4485 | -58.4839 | -58.4152 | -58.429 | -58.5159 | -58.2413 | -0.12817 | -0.027466 | -0.045776 | 0.24719 | -0.11902 | -0.15106 | 0.009155 | -0.022888 | -0.004578 | 0.009155 | -122.8546 | 0.050354 | 0.23804 | -0.036621 | 0.24262 | -0.032043 | 0.37537 | 123.0011 | 0.054932 | 0.068665 | 123.0194 | 122.9324 | 122.8912 | 122.9279 | -123.0469 | -122.9233 | 122.8729 | 0.064087 | 55.3299 | 55.5313
335.1719 | 123.1659 | -58.4793 | 64.444 | -0.037689 | 0.0010489 | 0.064375 | 0.061141 | -0.0041122 | 0.0028327 | -0.0016278 | 0.032227 | -0.0010339 | -0.0012818 | -0.0042126 | -0.0010787 | -0.0032301 | -0.0021107 | -3.2318 | 64.389 | -58.6212 | 64.3845 | -58.287 | -58.6487 | -58.6075 | -3.0121 | 64.4348 | -58.4885 | -58.461 | -58.4061 | -58.5114 | -58.2642 | -0.14191 | -0.054932 | -0.05951 | 0.19226 | -0.12817 | -0.16937 | 0.013733 | -0.027466 | -0.009155 | -0.009156 | -122.905 | 0.073242 | 0.21515 | -0.032044 | 0.2243 | -0.022889 | 0.33417 | 123.0057 | 0.082397 | 0.027465 | 123.0103 | 122.9233 | 122.8683 | 122.9141 | -123.0652 | -122.9324 | 122.8638 | 0.01831 | 55.2475 | 55.4672
336.1719 | 123.1842 | -58.4702 | 64.4485 | -0.037689 | 0.00040806 | 0.064589 | 0.061782 | -0.0015488 | 0.00048269 | 0.0039264 | 0.016968 | -0.0016749 | -0.00085457 | -0.002931 | -0.0023605 | -0.0015211 | -0.0012561 | -3.2227 | 64.4119 | -58.5938 | 64.2242 | -58.255 | -58.6029 | -58.6441 | -3.035 | 64.4348 | -58.5022 | -58.4473 | -58.3969 | -58.5022 | -58.255 | -0.1236 | -0.036621 | -0.2243 | 0.21515 | -0.17395 | -0.13275 | -0.050354 | -0.009155 | -0.032043 | -0.013733 | -122.8958 | 0.073242 | 0.21515 | -0.032043 | 0.24719 | 0 | 0.33875 | 122.818 | 0.10529 | 0.054931 | 123.0057 | 122.937 | 122.8821 | 122.905 | -123.0423 | -122.9507 | 122.6944 | 0.022888 | 55.2475 | 55.4352
337.1719 | 123.1979 | -58.4564 | 64.4302 | -0.075836 | 0.0021171 | 0.065657 | 0.064345 | -0.0017624 | -0.0035761 | 0.00050839 | 0.041382 | 0.00046135 | 0.00064083 | -0.0027174 | -0.0019333 | -0.00045288 | -0.0016833 | -3.3005 | 64.3982 | -58.6029 | 64.3478 | -58.2916 | -58.6487 | -58.6075 | -3.0716 | 64.4348 | -58.5022 | -58.4427 | -58.3878 | -58.4839 | -58.223 | -0.14648 | -0.032044 | -0.082398 | 0.16479 | -0.15106 | -0.19226 | -0.004578 | -0.045777 | -0.045776 | 0.004577 | -122.8729 | 0.068665 | 0.23346 | -0.027466 | 0.27924 | 0.01831 | 0.31128 | 122.9507 | 0.11444 | 0.059509 | 123.0011 | 122.937 | 122.8546 | 122.8912 | -123.0331 | -122.9324 | 122.8043 | 0.013733 | 55.1559 | 55.3848
338.1719 | 123.0972 | -58.4473 | 64.4211 | -0.060578 | 0.0027579 | 0.067152 | 0.062209 | 0.0010148 | -0.00079891 | 0.00072199 | 0.050537 | -0.00017945 | 0.0025634 | -0.001222 | -0.00022431 | -0.0013073 | -0.0018971 | -3.3051 | 64.3662 | -58.5938 | 64.389 | -58.223 | -58.6212 | -58.5709 | -3.0579 | 64.4485 | -58.4976 | -58.4473 | -58.2458 | -58.168 | -58.0307 | -0.14648 | -0.054932 | -0.032044 | 0.22431 | -0.1236 | -0.17395 | 0.022888 | -0.027466 | -0.050354 | 0.027465 | -122.8683 | 0.20142 | 0.41656 | 0.27924 | 0.46692 | 0.32959 | 0.37079 | 122.9828 | 0.25177 | 0.050354 | 122.9599 | 122.9462 | 122.8134 | 122.8958 | -123.0148 | -122.9187 | 122.8363 | 0 | 55.1422 | 55.3894
339.1719 | 123.1842 | -58.493 | 64.4302 | -0.037689 | -0.00087374 | 0.061171 | 0.066482 | 0.00058737 | 0.0013373 | -0.0029096 | 0.029175 | -0.00039305 | 0.00042723 | -0.007417 | -0.0012925 | -0.0021619 | 2.554e-05 | -3.392 | 64.3707 | -58.6121 | 64.3295 | -58.3145 | -58.6899 | -58.6533 | -3.1677 | 64.4394 | -58.5068 | -58.4518 | -58.4244 | -58.5251 | -58.2504 | -0.11902 | -0.059509 | -0.10071 | 0.17853 | -0.16022 | -0.19684 | -0.041198 | -0.077819 | -0.013733 | 0.009155 | -122.8821 | 0.068665 | 0.24262 | -0.032043 | 0.25635 | -0.01831 | 0.29755 | 122.9416 | 0.082398 | 0.054932 | 122.9828 | 122.9462 | 122.8638 | 122.9324 | -123.0423 | -122.937 | 122.8226 | 0.041199 | 55.101 | 55.3253
340.1719 | 123.1934 | -58.4518 | 64.4623 | -0.075836 | -0.0013009 | 0.062453 | 0.06285 | -0.001976 | -0.0020807 | -0.0018414 | -0.019653 | -0.00017945 | 0.00021363 | 0.002196 | -0.0027877 | -0.0010937 | 0.0013073 | -3.36 | 64.3982 | -58.5983 | 64.2105 | -58.5342 | -58.7036 | -58.5938 | -3.0991 | 64.4165 | -58.5068 | -58.4244 | -58.3878 | -58.5022 | -58.255 | -0.14649 | -0.064087 | -0.25177 | -0.082398 | -0.14191 | -0.25177 | 0.004578 | -0.10528 | -0.054932 | -0.045776 | -122.8867 | 0.064087 | 0.19684 | -0.050354 | 0.25177 | 0.004578 | 0.064087 | 122.8088 | 0.11902 | 0.082398 | 122.9965 | 122.9233 | 122.85 | 122.8683 | -123.0606 | -122.9691 | 122.6624 | 0.027466 | 55.0919 | 55.3528
341.1719 | 123.2162 | -58.4747 | 64.4485 | -0.060578 | 0.0021171 | 0.064589 | 0.063064 | 0.0022964 | -0.0012261 | -0.0018414 | 0.093262 | 3.4148e-05 | -0.00064077 | 0.0015552 | -0.0010787 | -0.0019483 | -0.0014697 | -3.4103 | 64.3982 | -58.5983 | 64.3707 | -58.2321 | -58.6304 | -58.5114 | -3.3646 | 64.4485 | -58.5068 | -58.4427 | -58.4198 | -58.5297 | -58.2504 | -0.1236 | -0.050354 | -0.077819 | 0.24261 | -0.036622 | -0.15564 | 0.086975 | -0.032043 | -0.032044 | 0 | -122.8912 | 0.054931 | 0.2243 | -0.054932 | 0.25635 | -0.022888 | 0.36621 | 122.9691 | 0.086975 | 0.064087 | 122.9965 | 122.9553 | 122.8729 | 122.9233 | -123.0469 | -122.9553 | 122.8455 | 0.032043 | 55.0644 | 55.1102
342.1719 | 123.2208 | -58.4747 | 64.4531 | -0.12161 | -0.0013009 | 0.063734 | 0.060927 | -0.00026703 | 0.00069649 | -0.00077341 | 0.010864 | -0.00017945 | 0.00064083 | -0.0010084 | -0.00043791 | -0.0019483 | -0.0042469 | -3.4836 | 64.389 | -58.6304 | 64.3478 | -58.2962 | -58.6487 | -58.6029 | -3.1815 | 64.444 | -58.5205 | -58.429 | -58.3878 | -58.5022 | -58.2321 | -0.15564 | -0.064087 | -0.10529 | 0.17853 | -0.12817 | -0.17395 | 0.027466 | -0.018311 | -0.045777 | -0.009155 | -122.8821 | 0.086975 | 0.24261 | -0.027466 | 0.28839 | 0.018311 | 0.33417 | 122.9782 | 0.13275 | 0.091553 | 123.0194 | 122.9645 | 122.8638 | 122.9187 | -123.0835 | -122.9736 | 122.8226 | 0.045776 | 54.9911 | 55.2933
343.1719 | 123.2391 | -58.461 | 64.444 | -0.037689 | -0.0010873 | 0.061812 | 0.06285 | 0.00016017 | 0.00026909 | -0.00013241 | 0.016968 | -0.00017945 | 0.001068 | 0.0024096 | -0.00043791 | -0.00023928 | 0.00066654 | -3.5202 | 64.4073 | -58.6258 | 64.3433 | -58.2962 | -58.6761 | -58.6258 | -3.2318 | 64.4394 | -58.5159 | -58.4335 | -58.3832 | -58.5251 | -58.2367 | -0.16479 | -0.036621 | -0.10071 | 0.16479 | -0.16479 | -0.21515 | 0 | -0.050354 | -0.054931 | -0.004578 | -122.8775 | 0.07782 | 0.22431 | -0.064086 | 0.27924 | -0.009155 | 0.32959 | 122.9691 | 0.13275 | 0.082397 | 123.0331 | 122.9553 | 122.8683 | 122.9004 | -123.0698 | -122.9599 | 122.8043 | 0.027466 | 54.9408 | 55.2292
344.1719 | 123.1705 | -58.4518 | 64.4394 | -0.11398 | 0.0025443 | 0.065443 | 0.06285 | 0.0016556 | 0.0019781 | -0.0012006 | 0.0047608 | -0.0010339 | -0.00042717 | 0.00027342 | 0.00084389 | -0.00023928 | 0.00066654 | -3.4561 | 64.3799 | -58.6121 | 64.3799 | -58.2458 | -58.6578 | -58.6349 | -3.1952 | 64.4531 | -58.5068 | -58.4473 | -58.3878 | -58.493 | -58.2275 | -0.16022 | -0.059509 | -0.059509 | 0.20599 | -0.18311 | -0.20599 | -0.022888 | -0.045776 | -0.054932 | 0.013733 | -122.8867 | 0.064087 | 0.2243 | -0.041199 | 0.27924 | 0.013733 | 0.36621 | 122.9919 | 0.11902 | 0.059509 | 122.9919 | 122.9599 | 122.8317 | 122.905 | -123.0515 | -122.9462 | 122.8317 | 0.004577 | 54.9957 | 55.2567
345.1719 | 123.1796 | -58.5022 | 64.4257 | -0.075836 | 0.0014761 | 0.063948 | 0.063277 | -0.0017624 | -0.0010125 | 0.00050839 | 0.0078126 | -0.0018885 | 0.00085443 | 0.0045458 | -0.00065151 | -0.0015211 | 0.0042981 | -3.6575 | 64.3616 | -58.6395 | 64.4119 | -58.2458 | -58.7402 | -58.7036 | -3.3875 | 64.4302 | -58.5205 | -58.4885 | -58.461 | -58.5938 | -58.3008 | -0.13733 | -0.064087 | -0.013733 | 0.25635 | -0.20142 | -0.23804 | -0.064087 | -0.10071 | -0.018311 | 0.004578 | -122.9141 | 0.041198 | 0.20142 | -0.091553 | 0.21973 | -0.073242 | 0.39368 | 123.0515 | 0.059509 | 0.032044 | 123.0011 | 122.9507 | 122.8638 | 122.9324 | -123.0652 | -122.9462 | 122.9141 | 0.013733 | 54.8447 | 55.1147
346.1719 | 123.23 | -58.4839 | 64.4394 | -0.083466 | 0.0014761 | 0.061385 | 0.064773 | -5.343e-05 | -0.00015811 | -0.0016278 | 0.0078126 | 0.00024775 | 0.00042723 | -0.0014356 | -0.0021469 | -0.0019483 | 0.0013073 | -3.6209 | 64.3982 | -58.6212 | 64.3662 | -58.2642 | -58.6166 | -58.5754 | -3.241 | 64.4485 | -58.5159 | -58.4106 | -58.3694 | -58.4702 | -58.2138 | -0.13733 | -0.041199 | -0.073242 | 0.21973 | -0.091552 | -0.13275 | 0.045777 | 0.004578 | -0.032043 | 0.009155 | -122.85 | 0.11444 | 0.27008 | 0.013733 | 0.30212 | 0.045776 | 0.35706 | 122.9874 | 0.14648 | 0.10528 | 123.0194 | 122.9645 | 122.8821 | 122.9324 | -123.0606 | -122.9553 | 122.85 | 0.073242 | 54.863 | 55.2429
347.1719 | 123.1934 | -58.4564 | 64.4257 | -0.068207 | 0.0016899 | 0.063307 | 0.064986 | 0.00058737 | 0.00048269 | -0.002696 | 0.013916 | 0.0011023 | 0.0021362 | 0.0017688 | -0.00086511 | -0.00045288 | 0.00045294 | -3.6713 | 64.4028 | -58.6212 | 64.3616 | -58.2687 | -58.6487 | -58.5892 | -3.2684 | 64.4394 | -58.493 | -58.4106 | -58.3786 | -58.4885 | -58.223 | -0.16479 | -0.022888 | -0.064087 | 0.18768 | -0.13275 | -0.19226 | 0.032044 | -0.027466 | -0.036621 | 0.013733 | -122.8363 | 0.07782 | 0.23346 | -0.032043 | 0.27008 | 0.004578 | 0.35248 | 122.9828 | 0.11444 | 0.082397 | 123.024 | 122.9324 | 122.8592 | 122.8958 | -123.0469 | -122.9187 | 122.818 | 0.045776 | 54.7852 | 55.188
348.1719 | 123.1979 | -58.461 | 64.4485 | -0.022431 | 0.00019446 | 0.063094 | 0.063918 | -0.0013352 | -0.0020807 | -0.0018414 | -0.010498 | 0.0011023 | -0.0021362 | 0.003905 | -0.00086511 | -0.0025891 | 0.0015209 | -3.6484 | 64.4028 | -58.6075 | 64.4211 | -58.2413 | -58.6258 | -58.5892 | -3.2593 | 64.444 | -58.4885 | -58.3969 | -58.3832 | -58.5068 | -58.2275 | -0.14648 | -0.045776 | -0.027465 | 0.21973 | -0.12817 | -0.16479 | 0.018311 | -0.01831 | -0.027465 | -0.004577 | -122.8455 | 0.07782 | 0.23346 | -0.045776 | 0.26093 | -0.018311 | 0.36621 | 123.0286 | 0.10529 | 0.091552 | 123.0103 | 122.9324 | 122.8638 | 122.905 | -123.056 | -122.937 | 122.8821 | 0.064087 | 54.8126 | 55.2017
349.1719 | 123.143 | -58.4473 | 64.4028 | -0.083466 | -0.00087374 | 0.06288 | 0.062423 | -0.00026703 | -0.0012261 | -0.003764 | 0.035278 | -0.00060665 | 0.00021363 | -0.0052808 | -0.0019333 | -0.0013073 | 2.554e-05 | -3.7033 | 64.4119 | -58.5938 | 64.3982 | -58.2184 | -58.5892 | -58.5617 | -3.2913 | 64.4257 | -58.4885 | -58.3832 | -58.0811 | -58.5526 | -58.4152 | -0.14648 | 0.009155 | -0.004578 | 0.22888 | -0.11444 | -0.14191 | 0.032043 | 0.004578 | -0.041198 | 0.022888 | -122.7859 | 0.36621 | 0.032044 | -0.10529 | 0.073242 | -0.064087 | 0.37537 | 122.9919 | 0.40741 | 0.10529 | 123.0057 | 122.9141 | 122.8592 | 122.8729 | -122.9965 | -122.8912 | 122.8455 | 0.064087 | 54.744 | 55.1559
350.1719 | 123.1979 | -58.4473 | 64.4485 | -0.052948 | 0.00083526 | 0.062666 | 0.063064 | -0.0017624 | 0.00069649 | -0.00055961 | 0.0078126 | -0.00017945 | 2.8e-08 | 0.0058276 | -1.0706e-05 | -0.00066648 | -0.0010425 | -3.7262 | 64.3936 | -58.6166 | 64.3845 | -58.2458 | -58.6212 | -58.58 | -3.3051 | 64.444 | -58.5022 | -58.4152 | -58.374 | -58.4885 | -58.2138 | -0.16937 | -0.054931 | -0.064087 | 0.20142 | -0.13275 | -0.17395 | 0.036621 | -0.004578 | -0.054931 | -0.004577 | -122.8638 | 0.073243 | 0.23346 | -0.041198 | 0.28839 | 0.013733 | 0.37079 | 123.0011 | 0.12817 | 0.086975 | 123.0103 | 122.9462 | 122.8409 | 122.8912 | -123.0652 | -122.9507 | 122.8317 | 0.032044 | 54.7211 | 55.1422
351.1719 | 123.1842 | -58.4839 | 64.4348 | -0.083466 | 0.00019446 | 0.064375 | 0.064132 | 0.00016017 | 0.00091009 | 8.1188e-05 | -0.010498 | 0.00046135 | -0.00064077 | -0.006349 | -0.00086511 | -0.0015211 | -0.00040166 | -3.8361 | 64.3845 | -58.6304 | 64.3158 | -58.3237 | -58.6807 | -58.6578 | -3.4424 | 64.4531 | -58.4976 | -58.4381 | -58.4061 | -58.5205 | -58.255 | -0.14648 | -0.050354 | -0.11902 | 0.16022 | -0.17395 | -0.19684 | -0.027466 | -0.050354 | -0.013733 | 0.018311 | -122.8729 | 0.07782 | 0.22888 | -0.036621 | 0.24262 | -0.022888 | 0.3067 | 122.9462 | 0.091553 | 0.05951 | 123.0148 | 122.9507 | 122.8683 | 122.937 | -123.0652 | -122.9324 | 122.7997 | 0.045777 | 54.6478 | 55.0415
352.1719 | 123.1384 | -58.5022 | 64.4073 | -0.083466 | 0.0016899 | 0.064589 | 0.063918 | -0.0026168 | -0.00079891 | -0.00034601 | -0.019653 | -0.0010339 | -0.00021357 | -0.003999 | 0.0010575 | -0.0034437 | -0.0014697 | -3.9093 | 64.3753 | -58.6395 | 64.2975 | -58.3649 | -58.7357 | -58.667 | -3.5431 | 64.4302 | -58.5251 | -58.493 | -58.4885 | -58.5754 | -58.2596 | -0.13733 | -0.032044 | -0.10986 | 0.13733 | -0.16479 | -0.23346 | -0.027466 | -0.096131 | -0.022888 | 0.022888 | -122.9004 | 0.013733 | 0.24261 | -0.073242 | 0.2655 | -0.050354 | 0.27466 | 122.937 | 0.036621 | 0.032043 | 123.0148 | 122.9553 | 122.8775 | 122.9324 | -123.0469 | -122.9324 | 122.7997 | 0.009155 | 54.5929 | 54.9591
353.1719 | 123.1842 | -58.4885 | 64.444 | -0.03006 | 0.0014761 | 0.063307 | 0.060073 | 0.0035782 | -0.00015811 | -0.0018414 | -0.0043946 | -0.0012477 | 0.00064083 | -0.00079478 | -0.00086511 | 0.00040152 | 0.0023755 | -3.9276 | 64.3982 | -58.6304 | 64.3021 | -58.3374 | -58.7173 | -58.6441 | -3.5202 | 64.4257 | -58.5022 | -58.4656 | -58.4198 | -58.5388 | -58.2596 | -0.14191 | -0.045777 | -0.14191 | 0.15106 | -0.15564 | -0.22888 | -0.013733 | -0.086975 | -0.013733 | -0.018311 | -122.9095 | 0.068664 | 0.22888 | -0.050354 | 0.24261 | -0.036621 | 0.29297 | 122.9324 | 0.082397 | 0.036621 | 123.0286 | 122.9279 | 122.8867 | 122.9141 | -123.0743 | -122.9462 | 122.7905 | 0.022888 | 54.5609 | 54.9683
354.1719 | 123.1796 | -58.4656 | 64.4531 | -0.091095 | 0.00040806 | 0.064375 | 0.06285 | 0.0027238 | 0.00026909 | -0.00055961 | -0.0013428 | -0.00039305 | -0.00085457 | 0.0036914 | -0.0017197 | -0.0010937 | -0.0016833 | -3.9185 | 64.4165 | -58.6258 | 64.3524 | -58.2962 | -58.6487 | -58.6166 | -3.4653 | 64.4485 | -58.5297 | -58.4152 | -58.3878 | -58.4976 | -58.2275 | -0.16022 | -0.036621 | -0.10071 | 0.16937 | -0.15106 | -0.18311 | 0.009155 | -0.022889 | -0.064087 | -0.004578 | -122.8683 | 0.07782 | 0.23804 | -0.032044 | 0.30212 | 0.032043 | 0.32959 | 122.9782 | 0.14191 | 0.11444 | 123.0423 | 122.9782 | 122.8821 | 122.9141 | -123.0789 | -122.9828 | 122.818 | 0.050354 | 54.5471 | 55.0003
355.1719 | 123.1979 | -58.4747 | 64.4485 | -0.098725 | -0.0015145 | 0.064162 | 0.063918 | -0.0013352 | 0.00048269 | 0.00029479 | -0.0074462 | 0.0017431 | 0.00042723 | -0.00079478 | -0.0023605 | -0.0010937 | -0.0012561 | -3.9597 | 64.4073 | -58.6258 | 64.3387 | -58.2962 | -58.6807 | -58.6166 | -3.5019 | 64.4394 | -58.4976 | -58.4335 | -58.3969 | -58.5251 | -58.2321 | -0.15106 | -0.041198 | -0.10986 | 0.17853 | -0.14191 | -0.20599 | 0.009155 | -0.054932 | -0.022889 | -0.009155 | -122.8821 | 0.077819 | 0.24261 | -0.050354 | 0.2655 | -0.027465 | 0.32959 | 122.9645 | 0.10071 | 0.064087 | 123.0331 | 122.937 | 122.8821 | 122.9141 | -123.0743 | -122.9462 | 122.8134 | 0.041198 | 54.5151 | 54.9728
356.1719 | 123.2254 | -58.4656 | 64.444 | -0.091095 | 0.00040806 | 0.063307 | 0.061782 | 0.00251 | -0.0031489 | 0.00093559 | 0.023071 | 0.0011023 | 0.0014954 | 0.00070062 | -0.0015061 | -0.0028027 | -0.0018971 | -3.9597 | 64.4028 | -58.5983 | 64.3799 | -58.2367 | -58.6395 | -58.6029 | -3.4241 | 64.4257 | -58.4839 | -58.3923 | -58.3603 | -58.4656 | -58.2092 | -0.13275 | -0.041199 | -0.064087 | 0.22888 | -0.13733 | -0.17395 | -0.004577 | -0.041198 | -0.018311 | -0.018311 | -122.8363 | 0.10529 | 0.25635 | 0 | 0.27466 | 0.018311 | 0.36163 | 122.9782 | 0.1236 | 0.091553 | 123.0011 | 122.9095 | 122.8683 | 122.8912 | -123.0423 | -122.9279 | 122.8455 | 0.073242 | 54.5059 | 55.0415
357.1719 | 123.1659 | -58.4793 | 64.444 | -0.068207 | 0.0010489 | 0.064375 | 0.06285 | 0.0012284 | -0.0025079 | 0.00093559 | 0.0047608 | 3.4148e-05 | -0.0014954 | 0.0041186 | -0.0015061 | -0.0010937 | -0.0040333 | -4.0558 | 64.4119 | -58.6487 | 64.3204 | -58.3328 | -58.6899 | -58.6441 | -3.5614 | 64.4348 | -58.5205 | -58.4473 | -58.4198 | -58.5159 | -58.255 | -0.16937 | -0.032044 | -0.1236 | 0.14648 | -0.16479 | -0.21057 | 0.004578 | -0.041198 | -0.041199 | -0.009156 | -122.8912 | 0.059509 | 0.2243 | -0.036621 | 0.2655 | 0.004578 | 0.31586 | 122.9691 | 0.10071 | 0.073242 | 123.0606 | 122.9553 | 122.8912 | 122.9141 | -123.0927 | -122.9645 | 122.7997 | 0.032043 | 54.4235 | 54.9179
358.1719 | 123.175 | -58.4564 | 64.4302 | -0.10635 | 0.0014761 | 0.063521 | 0.062636 | -0.0011214 | -0.0018671 | -0.00098701 | -0.0013428 | 0.0015295 | 0.0014954 | 0.002196 | 0.00020289 | -0.0021619 | -0.00018806 | -4.1016 | 64.389 | -58.6304 | 64.3387 | -58.342 | -58.699 | -58.6578 | -3.5706 | 64.4348 | -58.5297 | -58.4518 | -58.4152 | -58.5297 | -58.2504 | -0.17395 | -0.041199 | -0.091553 | 0.11444 | -0.20142 | -0.24262 | -0.027466 | -0.068665 | -0.073242 | 0.004577 | -122.8821 | 0.041199 | 0.20599 | -0.073242 | 0.27924 | 0 | 0.28839 | 122.9691 | 0.11444 | 0.07782 | 123.0194 | 122.9645 | 122.8455 | 122.8912 | -123.0606 | -122.9599 | 122.7951 | 0.004578 | 54.3549 | 54.8859
359.1719 | 123.1979 | -58.4518 | 64.4302 | -0.068207 | -0.0015145 | 0.061812 | 0.062423 | -0.0043258 | 0.0021917 | -0.0016278 | 0.0047608 | -0.00060665 | 0.00021363 | 0.0030506 | -0.0012925 | -0.00023928 | -0.0023243 | -4.0878 | 64.3982 | -58.6212 | 64.3616 | -58.3008 | -58.6624 | -58.6166 | -3.5156 | 64.4302 | -58.5022 | -58.4106 | -58.3786 | -58.5114 | -58.223 | -0.16937 | -0.032044 | -0.068665 | 0.15106 | -0.1648 | -0.21057 | 0.004578 | -0.041199 | -0.050354 | 0 | -122.8409 | 0.073242 | 0.22888 | -0.05951 | 0.27924 | -0.009156 | 0.32043 | 122.9828 | 0.1236 | 0.091552 | 123.0194 | 122.9324 | 122.85 | 122.8821 | -123.0515 | -122.9324 | 122.8134 | 0.041198 | 54.364 | 54.9362
360.1719 | 123.1842 | -58.4793 | 64.4257 | -0.11398 | -0.00087374 | 0.064375 | 0.061568 | 0.00251 | -0.00037171 | 8.1188e-05 | -0.0043946 | -0.00039305 | 0.00021363 | -0.0033582 | -0.00086511 | -0.0017347 | -0.0040333 | -4.1519 | 64.4119 | -58.6304 | 64.2471 | -58.3603 | -58.754 | -58.6807 | -3.6392 | 64.444 | -58.5159 | -58.461 | -58.4473 | -58.5754 | -58.2642 | -0.15106 | -0.013733 | -0.17853 | 0.11902 | -0.20142 | -0.27466 | -0.050354 | -0.1236 | -0.036621 | 0.018311 | -122.8867 | 0.032043 | 0.21515 | -0.09613 | 0.25177 | -0.059509 | 0.27008 | 122.8775 | 0.068664 | 0.054931 | 123.0423 | 122.9599 | 122.8912 | 122.9233 | -123.056 | -122.9416 | 122.7264 | 0.01831 | 54.3274 | 54.8401
361.1719 | 123.1934 | -58.4518 | 64.4485 | -0.075836 | 0.00083526 | 0.064589 | 0.062209 | -0.0028304 | -0.0022943 | -0.0033368 | -0.056274 | 0.00024775 | 0.00021363 | -0.0025036 | -0.00065151 | -0.00023928 | -0.0042469 | -4.0924 | 64.4302 | -58.6212 | 64.4531 | -58.5297 | -58.8501 | -58.5983 | -3.4973 | 64.4485 | -58.5068 | -58.4198 | -58.374 | -58.461 | -58.2001 | -0.16937 | -0.01831 | 0.004578 | -0.07782 | -0.14649 | -0.39826 | 0.022888 | -0.22888 | -0.054932 | 0 | -122.8683 | 0.07782 | 0.25177 | -0.009156 | 0.3067 | 0.045776 | 0.091553 | 123.0743 | 0.13275 | 0.086975 | 123.0515 | 122.9553 | 122.8821 | 122.9004 | -123.0698 | -122.9553 | 122.905 | 0.032043 | 54.3594 | 54.9545
362.1719 | 123.2254 | -58.4427 | 64.444 | -0.12161 | -0.00066014 | 0.063094 | 0.062209 | -0.00026703 | 0.00069649 | 8.1188e-05 | -0.0074462 | -0.00017945 | 0.00021363 | 0.0028368 | -0.0017197 | -0.00066648 | -0.00018806 | -4.1702 | 64.4028 | -58.6166 | 64.3662 | -58.255 | -58.6349 | -58.6166 | -3.5385 | 64.4531 | -58.4976 | -58.429 | -58.3603 | -58.4793 | -58.2092 | -0.17395 | -0.041199 | -0.07782 | 0.18768 | -0.17395 | -0.19226 | 0 | -0.018311 | -0.054932 | 0.009155 | -122.8729 | 0.082397 | 0.23346 | -0.036621 | 0.28839 | 0.018311 | 0.36163 | 122.9828 | 0.13733 | 0.068665 | 123.0194 | 122.9507 | 122.8455 | 122.8958 | -123.0606 | -122.9416 | 122.8088 | 0.013733 | 54.2725 | 54.9042
363.1719 | 123.1796 | -58.4747 | 64.4485 | -0.060578 | -0.0030099 | 0.066512 | 0.061996 | 0.0016556 | 0.0017645 | -0.0018414 | 0.032227 | 0.00024775 | -0.00021357 | 0.0015552 | -0.0023605 | -0.0015211 | -0.0025379 | -4.2023 | 64.4211 | -58.6304 | 64.3616 | -58.2916 | -58.667 | -58.6075 | -3.5751 | 64.4257 | -58.5022 | -58.4244 | -58.374 | -58.4885 | -58.2092 | -0.15564 | -0.027465 | -0.086975 | 0.1831 | -0.13275 | -0.19226 | 0.022888 | -0.036621 | -0.027466 | -0.022888 | -122.8729 | 0.10071 | 0.2655 | -0.013733 | 0.29297 | 0.013733 | 0.33874 | 122.9919 | 0.12817 | 0.07782 | 123.0515 | 122.9279 | 122.8958 | 122.9004 | -123.0789 | -122.9507 | 122.8363 | 0.050354 | 54.2725 | 54.8996
364.1719 | 123.2025 | -58.4747 | 64.4394 | -0.11398 | 0.00040806 | 0.063734 | 0.061996 | -0.00026703 | -0.00058531 | -0.0014142 | 0.0047608 | 0.0030249 | 0.00064083 | 0.00070062 | -0.00022431 | -0.0013073 | -0.0029651 | -4.2755 | 64.4028 | -58.6075 | 64.3524 | -58.3145 | -58.6578 | -58.6121 | -3.6255 | 64.4531 | -58.5114 | -58.4244 | -58.3923 | -58.5022 | -58.2275 | -0.13275 | -0.036621 | -0.086975 | 0.16022 | -0.13733 | -0.18311 | -0.004578 | -0.050354 | -0.036622 | 0.013733 | -122.8638 | 0.082397 | 0.24719 | -0.027466 | 0.28381 | 0.009156 | 0.29297 | 122.9599 | 0.11902 | 0.086976 | 123.0103 | 122.9645 | 122.8775 | 122.9279 | -123.0469 | -122.9507 | 122.8271 | 0.050354 | 54.1992 | 54.8492
365.1719 | 123.1888 | -58.4427 | 64.4485 | -0.068207 | 0.0014761 | 0.062666 | 0.061355 | -0.00048063 | -0.00058531 | -0.0014142 | -0.025757 | -0.00060665 | -0.00021357 | -0.0033582 | -0.0017197 | 0.00018792 | -0.0036059 | -4.2389 | 64.4119 | -58.5892 | 64.3433 | -57.9208 | -58.3969 | -58.7906 | -3.5065 | 64.4394 | -58.4976 | -58.4015 | -58.3649 | -58.5068 | -58.2321 | -0.14648 | -0.036621 | -0.10529 | 0.52185 | -0.3479 | 0.045776 | -0.20142 | 0.19226 | -0.054932 | -0.009155 | -122.85 | 0.07782 | 0.21057 | -0.064087 | 0.2655 | -0.009155 | 0.66833 | 122.9324 | 0.13275 | 0.096131 | 123.0011 | 122.937 | 122.8546 | 122.8821 | -123.0377 | -122.9462 | 122.7859 | 0.041199 | 54.2038 | 54.9362
366.1719 | 123.2025 | -58.4656 | 64.4257 | -0.098725 | -0.0010873 | 0.063734 | 0.062209 | -0.0015488 | -0.0016535 | -0.0016278 | -0.010498 | -0.00039305 | -0.0019226 | -0.00036738 | -0.00086511 | -0.0025891 | -0.0031787 | -4.3625 | 64.3936 | -58.6258 | 64.3112 | -58.3511 | -58.7173 | -58.6578 | -3.7262 | 64.4714 | -58.5297 | -58.4793 | -58.429 | -58.6395 | -58.1543 | -0.16022 | -0.032043 | -0.11444 | 0.11444 | -0.19226 | -0.25177 | -0.032044 | -0.091553 | -0.064087 | 0.045777 | -122.905 | 0.036621 | 0.31128 | -0.17395 | 0.37537 | -0.10986 | 0.27466 | 122.937 | 0.10071 | 0.050354 | 123.0194 | 123.0011 | 122.8592 | 122.937 | -123.0515 | -122.9553 | 122.7768 | -0.013733 | 54.1031 | 54.7394
367.1719 | 123.1293 | -58.4656 | 64.4394 | -0.091095 | 0.00083526 | 0.063734 | 0.063064 | 0.00037377 | 0.0011237 | -0.00055961 | -0.016602 | 0.00024775 | 0.00021363 | 0.0028368 | -0.00043791 | -0.0028027 | -0.00061526 | -4.3945 | 64.4119 | -58.6349 | 64.3112 | -58.3466 | -58.7128 | -58.6533 | -3.7674 | 64.4577 | -58.5159 | -58.4702 | -58.4473 | -58.58 | -58.2779 | -0.16937 | -0.027466 | -0.12817 | 0.11902 | -0.18768 | -0.24719 | -0.01831 | -0.07782 | -0.050354 | 0.018311 | -122.9095 | 0.01831 | 0.18768 | -0.11444 | 0.23804 | -0.064087 | 0.28839 | 122.9462 | 0.068664 | 0.045776 | 123.0469 | 122.9736 | 122.8775 | 122.9233 | -123.0743 | -122.9553 | 122.7768 | -0.004578 | 54.071 | 54.6982
368.1719 | 123.1247 | -58.493 | 64.444 | -0.03006 | 0.00019446 | 0.064589 | 0.063705 | -0.0013352 | -0.00015811 | -0.0012006 | 0.023071 | 0.00024775 | -0.00042717 | 0.0015552 | -0.00022431 | -0.0028027 | 0.0042981 | -4.3991 | 64.3936 | -58.6258 | 64.2746 | -58.3694 | -58.7585 | -58.6807 | -3.7765 | 64.4348 | -58.5205 | -58.4518 | -58.4335 | -58.548 | -58.2596 | -0.13275 | -0.050354 | -0.16937 | 0.1236 | -0.18768 | -0.2655 | -0.054932 | -0.13275 | -0.027466 | -0.009156 | -122.8958 | 0.059509 | 0.23346 | -0.054932 | 0.26093 | -0.027466 | 0.25635 | 122.9004 | 0.086975 | 0.068665 | 123.0194 | 122.9553 | 122.8867 | 122.9279 | -123.0698 | -122.9645 | 122.7676 | 0.041199 | 54.0939 | 54.7165
369.1719 | 123.1522 | -58.5205 | 64.4485 | -0.052948 | 0.00062166 | 0.06523 | 0.063277 | 0.0016556 | 0.0011237 | 8.1188e-05 | -0.0074462 | -0.0029567 | 0.0014954 | 0.0017688 | 0.00041649 | -0.0010937 | -0.0048877 | -4.4403 | 64.389 | -58.6166 | 64.3295 | -58.3466 | -58.7082 | -58.6578 | -3.653 | 64.4669 | -58.5114 | -58.4473 | -58.4473 | -58.5754 | -58.287 | -0.09613 | -0.059509 | -0.11902 | 0.17395 | -0.13733 | -0.18768 | -0.041199 | -0.091553 | 0.009155 | 0.018311 | -122.8958 | 0.073242 | 0.23346 | -0.054931 | 0.22431 | -0.064086 | 0.27008 | 122.9462 | 0.064087 | 0.064087 | 123.0057 | 122.9782 | 122.9095 | 122.9874 | -123.0652 | -122.9599 | 122.85 | 0.073242 | 54.0802 | 54.8676
370.1719 | 123.1842 | -58.4976 | 64.4348 | -0.060578 | 0.0012625 | 0.063307 | 0.062636 | 0.003151 | 5.5488e-05 | -0.002055 | -0.034912 | -0.00060665 | 0.0012818 | -0.00036738 | -0.0017197 | -0.00023928 | -0.0025379 | -4.4678 | 64.4119 | -58.6075 | 64.3066 | -58.3466 | -58.7311 | -58.6624 | -3.7949 | 64.4577 | -58.5205 | -58.4747 | -58.4564 | -58.6029 | -58.2825 | -0.10986 | -0.022888 | -0.12817 | 0.15106 | -0.1648 | -0.23346 | -0.054932 | -0.1236 | -0.022888 | 0.022889 | -122.9095 | 0.041199 | 0.21515 | -0.10529 | 0.23804 | -0.082397 | 0.26093 | 122.9141 | 0.064087 | 0.045777 | 123.0194 | 122.9782 | 122.9095 | 122.9553 | -123.0423 | -122.9553 | 122.8043 | 0.022889 | 54.0298 | 54.7028
371.1719 | 123.1522 | -58.4793 | 64.4119 | -0.11398 | -0.0015145 | 0.06523 | 0.064132 | 0.00016017 | 5.5488e-05 | -0.00098701 | -0.0013428 | -0.00082025 | 0.0012818 | 0.00070062 | 0.0014847 | -0.00088008 | -0.0023243 | -4.5044 | 64.3982 | -58.5983 | 64.3021 | -58.3374 | -58.7173 | -58.6716 | -3.7765 | 64.4485 | -58.5068 | -58.4656 | -58.3282 | -58.4885 | -58.3008 | -0.11902 | -0.013733 | -0.10986 | 0.14191 | -0.19226 | -0.23804 | -0.073242 | -0.11902 | -0.027466 | 0.036621 | -122.8775 | 0.15106 | 0.17853 | -0.009155 | 0.20599 | 0.018311 | 0.26093 | 122.9004 | 0.17853 | 0.041199 | 122.9965 | 122.9553 | 122.8775 | 122.9279 | -123.0103 | -122.9187 | 122.7814 | 0.013733 | 53.9749 | 54.7028
372.1719 | 123.1384 | -58.4518 | 64.476 | -0.12161 | 0.00019446 | 0.06288 | 0.063705 | -0.0026168 | -0.0022943 | 0.0045672 | -0.016602 | 0.00067495 | -0.0019226 | -0.0033582 | -0.00086511 | -0.00066648 | 0.0030163 | -4.541 | 64.3982 | -58.6166 | 64.3112 | -58.3466 | -58.7219 | -58.6578 | -3.7994 | 64.4485 | -58.5159 | -58.493 | -58.4518 | -58.5709 | -58.3054 | -0.1648 | -0.07782 | -0.16479 | 0.10528 | -0.20599 | -0.27008 | -0.041199 | -0.10529 | -0.064087 | -0.027466 | -122.9691 | 0 | 0.14648 | -0.11902 | 0.21057 | -0.054932 | 0.27008 | 122.9279 | 0.064087 | 0.022888 | 123.0148 | 122.9645 | 122.85 | 122.9004 | -123.0927 | -122.9919 | 122.7631 | -0.041199 | 53.9108 | 54.6524
373.1719 | 123.175 | -58.4381 | 64.4257 | -0.15976 | -0.0010873 | 0.064803 | 0.061355 | 0.0040054 | 0.00048269 | 0.00050839 | -0.0043946 | 0.00067495 | 0.00064083 | -0.0027174 | 0.0012711 | -0.0030163 | 0.0010937 | -4.5547 | 64.4257 | -58.6075 | 64.2975 | -58.3237 | -58.7173 | -58.6395 | -3.7765 | 64.4302 | -58.4885 | -58.4564 | -58.4244 | -58.5388 | -58.255 | -0.16937 | 0 | -0.12817 | 0.11444 | -0.20142 | -0.27924 | -0.032043 | -0.10986 | -0.050354 | 0.004578 | -122.8821 | 0.013733 | 0.18311 | -0.10071 | 0.23346 | -0.050354 | 0.28381 | 122.905 | 0.064087 | 0.032043 | 123.0331 | 122.9187 | 122.8638 | 122.8683 | -123.0331 | -122.9141 | 122.7356 | -0.018311 | 53.8834 | 54.6616
374.1719 | 123.1705 | -58.5022 | 64.444 | -0.060578 | 0.0014761 | 0.06288 | 0.064559 | 0.00058737 | 0.00069649 | -0.0024822 | -0.01355 | 0.0021703 | -0.0012818 | -0.00058098 | 0.00084389 | 0.0021105 | -0.00040166 | -4.5822 | 64.389 | -58.6075 | 64.3066 | -58.3557 | -58.7036 | -58.6624 | -3.8589 | 64.4623 | -58.5297 | -58.461 | -58.4473 | -58.5617 | -58.2733 | -0.10529 | -0.054932 | -0.13733 | 0.14648 | -0.16022 | -0.20142 | -0.054932 | -0.09613 | -0.027466 | 0.01831 | -122.905 | 0.054931 | 0.22888 | -0.05951 | 0.25635 | -0.032044 | 0.25177 | 122.9141 | 0.082397 | 0.068664 | 122.9965 | 122.9919 | 122.8912 | 122.9645 | -123.0515 | -122.9736 | 122.8088 | 0.041198 | 53.92 | 54.6432
375.1719 | 123.1979 | -58.4518 | 64.4485 | -0.03006 | 0.0012625 | 0.062453 | 0.063064 | -0.0034714 | -0.0014399 | -0.0012006 | -0.010498 | 3.4148e-05 | 0.0012818 | -0.0031446 | -0.0010787 | -0.0013073 | -0.0012561 | -4.5456 | 64.4028 | -58.6075 | 64.3616 | -58.287 | -58.6578 | -58.6075 | -3.7857 | 64.4669 | -58.5068 | -58.4198 | -58.374 | -58.5068 | -58.223 | -0.15564 | -0.045776 | -0.086975 | 0.16479 | -0.15564 | -0.20599 | 0 | -0.050354 | -0.054932 | 0.018311 | -122.8683 | 0.07782 | 0.22888 | -0.054932 | 0.28381 | 0 | 0.32044 | 122.9691 | 0.13275 | 0.086975 | 123.0103 | 122.9736 | 122.8546 | 122.9187 | -123.056 | -122.9553 | 122.8134 | 0.032043 | 53.9062 | 54.6661
376.1719 | 123.175 | -58.4702 | 64.4577 | -0.098725 | 0.00062166 | 0.064589 | 0.06285 | 0.00016017 | -0.0012261 | -0.0050458 | 0.016968 | -0.00017945 | 0.0021362 | -0.0033582 | 0.0019119 | -0.0021619 | -0.0040333 | -4.5868 | 64.4119 | -58.6029 | 64.3662 | -58.2916 | -58.6624 | -58.6121 | -3.804 | 64.444 | -58.4976 | -58.429 | -58.3694 | -58.4976 | -58.2275 | -0.13275 | -0.045777 | -0.091553 | 0.17853 | -0.14191 | -0.19226 | -0.009156 | -0.05951 | -0.027466 | -0.013733 | -122.8867 | 0.10071 | 0.24262 | -0.027466 | 0.27008 | 0 | 0.31128 | 122.9691 | 0.12817 | 0.068665 | 123.0148 | 122.9416 | 122.8821 | 122.9141 | -123.0606 | -122.9553 | 122.8363 | 0.041199 | 53.8834 | 54.6661
377.1719 | 123.1934 | -58.4427 | 64.4623 | -0.060578 | -0.0010873 | 0.062025 | 0.062209 | -0.0024032 | 0.00026909 | -0.00013241 | 0.013916 | -0.00039305 | 0.00042723 | 5.9824e-05 | -0.00043791 | -0.00023928 | -0.0018971 | -4.6143 | 64.3982 | -58.6029 | 64.3616 | -58.2825 | -58.6578 | -58.6166 | -3.8361 | 64.4531 | -58.5022 | -58.4152 | -58.3786 | -58.4885 | -58.223 | -0.16022 | -0.064087 | -0.10071 | 0.16022 | -0.17395 | -0.21515 | -0.013733 | -0.054932 | -0.059509 | -0.009155 | -122.8775 | 0.064087 | 0.21973 | -0.045776 | 0.27924 | 0.013733 | 0.32043 | 122.9645 | 0.1236 | 0.086975 | 123.0011 | 122.9553 | 122.8409 | 122.8958 | -123.0652 | -122.9645 | 122.8043 | 0.027466 | 53.8284 | 54.6066
378.1719 | 123.1384 | -58.5022 | 64.4485 | -0.075836 | 0.00062166 | 0.064375 | 0.06285 | 0.0018692 | 0.00048269 | -0.00055961 | -0.050171 | -0.00017945 | -0.0010682 | -0.003999 | -0.0010787 | -0.00088008 | -0.00018806 | -4.6509 | 64.3982 | -58.6212 | 64.325 | -58.3511 | -58.4793 | -58.5892 | -3.9551 | 64.4394 | -58.5068 | -58.4656 | -58.4473 | -58.5571 | -58.2733 | -0.11902 | -0.050354 | -0.1236 | 0.15106 | -0.086975 | 0.022888 | 0.032044 | 0.14191 | -0.004578 | -0.009155 | -122.9141 | 0.054931 | 0.22888 | -0.054932 | 0.23346 | -0.050354 | 0.27008 | 122.9462 | 0.059509 | 0.041199 | 123.0194 | 122.9462 | 122.9004 | 122.9416 | -123.0698 | -122.9553 | 122.8271 | 0.036621 | 53.8513 | 54.5471
379.1719 | 123.1384 | -58.4747 | 64.4577 | -0.10635 | -0.00087374 | 0.065657 | 0.063491 | -5.343e-05 | 5.5488e-05 | -0.0018414 | -0.0013428 | 0.0017431 | -0.0014954 | -0.0050672 | -0.00065151 | -0.00066648 | -0.0010425 | -4.6875 | 64.4257 | -58.6075 | 64.325 | -58.3511 | -58.7036 | -58.5709 | -3.9917 | 64.444 | -58.461 | -58.493 | -58.4427 | -58.5434 | -58.2733 | -0.13275 | -0.032044 | -0.13275 | 0.1236 | -0.096131 | -0.22888 | 0.036621 | -0.09613 | 0.013732 | -0.013733 | -122.9507 | 0.032043 | 0.20142 | -0.068665 | 0.18768 | -0.082397 | 0.25635 | 122.9324 | 0.018311 | -0.032043 | 123.0331 | 122.905 | 122.9004 | 122.9187 | -123.0652 | -122.9187 | 122.7997 | -0.018311 | 53.7872 | 54.483
380.1719 | 123.0652 | -58.493 | 64.4669 | -0.045319 | 0.0031851 | 0.06523 | 0.065414 | 0.00058737 | -0.0010125 | 8.1188e-05 | -0.089844 | -0.00039305 | 0.00042723 | 0.0062548 | 0.00041649 | -2.5678e-05 | 0.00066654 | -4.6326 | 64.4485 | -58.6441 | 64.2929 | -58.3466 | -58.7402 | -58.6945 | -3.9917 | 64.4989 | -58.5342 | -58.4885 | -58.5068 | -58.6304 | -58.3054 | -0.15106 | -0.018311 | -0.17395 | 0.14648 | -0.20142 | -0.24719 | -0.050354 | -0.09613 | -0.041199 | 0.032043 | -122.9553 | -0.013733 | 0.18768 | -0.13733 | 0.22888 | -0.09613 | 0.29755 | 122.937 | 0.027466 | 0.045777 | 123.0927 | 123.0331 | 122.9416 | 122.9919 | -123.111 | -123.0011 | 122.7859 | 0.004578 | 53.8605 | 54.5013
381.1719 | 123.1293 | -58.4702 | 64.4302 | -0.083466 | -0.00066014 | 0.063307 | 0.06285 | -5.343e-05 | -0.0014399 | 0.0022174 | 0.0078126 | 3.4148e-05 | -0.0010682 | 0.002196 | 0.0021255 | -0.00088008 | 0.0010937 | -4.6875 | 64.4073 | -58.6166 | 64.3204 | -58.342 | -58.7036 | -58.6487 | -4.0512 | 64.4623 | -58.5068 | -58.461 | -58.429 | -58.5434 | -58.2687 | -0.14648 | -0.022888 | -0.10986 | 0.12817 | -0.17853 | -0.23346 | -0.032044 | -0.086975 | -0.036621 | 0.032043 | -122.8912 | 0.041199 | 0.20142 | -0.073242 | 0.23804 | -0.036621 | 0.27466 | 122.937 | 0.07782 | 0.045776 | 123.024 | 122.9691 | 122.8775 | 122.9324 | -123.0469 | -122.937 | 122.7905 | 0.009155 | 53.7827 | 54.4189
382.1719 | 123.2025 | -58.4518 | 64.4302 | -0.075836 | 0.00083526 | 0.062666 | 0.063705 | 0.00058737 | -0.00058531 | -0.00013241 | 0.032227 | 0.00046135 | 0.0023498 | -0.0033582 | -0.00043791 | -2.5678e-05 | -0.00018806 | -4.6463 | 64.4211 | -58.5892 | 64.3753 | -58.2504 | -58.6304 | -58.5709 | -3.9139 | 64.4714 | -58.4564 | -58.3923 | -58.3466 | -58.4656 | -58.1909 | -0.13733 | -0.009155 | -0.054932 | 0.20142 | -0.11902 | -0.17853 | 0.01831 | -0.041199 | -0.004578 | 0.041199 | -122.8226 | 0.10528 | 0.26092 | -0.013733 | 0.2655 | -0.009155 | 0.33874 | 122.9645 | 0.10986 | 0.064087 | 123.0103 | 122.9279 | 122.8729 | 122.9233 | -123.0194 | -122.8867 | 122.8271 | 0.059509 | 53.8055 | 54.538
383.1719 | 123.2162 | -58.4427 | 64.444 | -0.083466 | -0.0013009 | 0.064162 | 0.063918 | -5.343e-05 | 0.0019781 | 0.00093559 | 0.035278 | 0.0011023 | 0.002777 | -0.0025036 | -0.0010787 | -0.0045117 | 0.00023934 | -4.6555 | 64.4119 | -58.5663 | 64.3845 | -58.2642 | -58.6258 | -58.5617 | -3.978 | 64.4669 | -58.4976 | -58.3878 | -58.3466 | -58.4473 | -58.1818 | -0.1236 | -0.032044 | -0.05951 | 0.17853 | -0.11902 | -0.18311 | 0.004577 | -0.059509 | -0.054932 | 0.022888 | -122.8317 | 0.09613 | 0.26093 | -0.004578 | 0.31586 | 0.050354 | 0.30212 | 122.9507 | 0.15106 | 0.10986 | 122.9782 | 122.9645 | 122.8546 | 122.9095 | -123.0103 | -122.9416 | 122.8271 | 0.054932 | 53.7872 | 54.4647
384.1719 | 123.1659 | -58.4702 | 64.4531 | -0.091095 | -0.0017281 | 0.064162 | 0.061996 | 0.00080117 | 0.00048269 | -0.0016278 | -0.0043946 | 0.00046135 | 0.0023498 | 0.0051868 | -0.00022431 | -0.00045288 | -0.0010425 | -4.6783 | 64.444 | -58.6166 | 64.3204 | -58.3237 | -58.6761 | -58.6258 | -4.1016 | 64.4531 | -58.5022 | -58.429 | -58.4106 | -58.5251 | -58.2504 | -0.14648 | -0.009155 | -0.13275 | 0.14648 | -0.15564 | -0.20599 | -0.009155 | -0.059509 | -0.032043 | 0 | -122.8821 | 0.059509 | 0.21973 | -0.054931 | 0.25177 | -0.022888 | 0.29297 | 122.937 | 0.091552 | 0.073242 | 123.0606 | 122.9553 | 122.9141 | 122.9233 | -123.0698 | -122.9553 | 122.7905 | 0.041199 | 53.7918 | 54.3686
385.1719 | 123.0789 | -58.4793 | 64.4852 | -0.083466 | -1.9142e-05 | 0.065016 | 0.066909 | 0.0022964 | -0.00015811 | 0.00072199 | -0.10815 | 0.0015295 | -0.0012818 | 0.0019824 | -0.0012925 | 0.0023241 | -0.0016833 | -4.6967 | 64.4257 | -58.6578 | 64.2838 | -58.3649 | -58.7494 | -58.7128 | -4.1794 | 64.476 | -58.5251 | -58.5114 | -58.5114 | -58.6578 | -58.3282 | -0.17853 | -0.059509 | -0.20142 | 0.11444 | -0.23346 | -0.27008 | -0.054932 | -0.091553 | -0.045776 | -0.009155 | -122.9965 | -0.032044 | 0.15106 | -0.17853 | 0.19684 | -0.13275 | 0.29297 | 122.9416 | 0.013732 | 0.013732 | 123.0835 | 123.0011 | 122.905 | 122.9553 | -123.143 | -123.0103 | 122.7631 | -0.032044 | 53.7827 | 54.2999
386.1719 | 123.1522 | -58.4702 | 64.4577 | -0.068207 | -0.00023294 | 0.059462 | 0.061355 | -0.0034714 | 5.5488e-05 | -0.002055 | -0.0013428 | 0.00067495 | -0.0012818 | -0.0042126 | 0.00020289 | 0.00018792 | -0.00018806 | -4.6326 | 64.4577 | -58.5846 | 64.3112 | -58.3054 | -58.7173 | -58.6441 | -4.1794 | 64.444 | -58.5205 | -58.4473 | -58.4106 | -58.5434 | -58.2596 | -0.11444 | 0 | -0.14648 | 0.16479 | -0.17395 | -0.24719 | -0.059509 | -0.13275 | -0.050354 | -0.013733 | -122.905 | 0.059509 | 0.21057 | -0.073242 | 0.26093 | -0.022888 | 0.27924 | 122.8958 | 0.10986 | 0.073242 | 123.0423 | 122.9645 | 122.9279 | 122.9141 | -123.0423 | -122.9782 | 122.7814 | 0.022888 | 53.8376 | 54.2908
387.1719 | 123.1796 | -58.4656 | 64.4348 | -0.075836 | 0.0016899 | 0.064803 | 0.062423 | 0.00080117 | 0.00048269 | -0.00077341 | 0.023071 | 0.00046135 | 0.00042723 | -0.0037854 | -0.00086511 | -0.00066648 | -0.00018806 | -4.7104 | 64.4394 | -58.5983 | 64.357 | -58.2733 | -58.6578 | -58.6075 | -4.1153 | 64.4531 | -58.5022 | -58.4198 | -58.3832 | -58.4839 | -58.2092 | -0.13275 | 0.004578 | -0.077819 | 0.19226 | -0.14191 | -0.19226 | -0.009155 | -0.059509 | -0.036621 | 0.018311 | -122.8546 | 0.082397 | 0.25635 | -0.018311 | 0.29297 | 0.01831 | 0.32501 | 122.9553 | 0.11902 | 0.082397 | 123.0377 | 122.9553 | 122.905 | 122.9187 | -123.0331 | -122.937 | 122.8226 | 0.045776 | 53.7552 | 54.3503
388.1719 | 123.1567 | -58.4702 | 64.444 | -0.083466 | 0.00062166 | 0.063948 | 0.0652 | -0.0030442 | -0.00015811 | 0.0015766 | 0.0047608 | 0.0023839 | 0.00021363 | 0.0013416 | -0.00022431 | -0.00066648 | -0.00018806 | -4.7653 | 64.4119 | -58.6121 | 64.3066 | -58.3374 | -58.6945 | -58.5159 | -4.2618 | 64.4531 | -58.5068 | -58.4656 | -58.4381 | -58.5709 | -58.2733 | -0.14191 | -0.032044 | -0.13733 | 0.13275 | -0.045776 | -0.2243 | 0.096131 | -0.082397 | -0.036621 | 0.009155 | -122.9095 | 0.032044 | 0.19684 | -0.10071 | 0.23346 | -0.064087 | 0.27466 | 122.9187 | 0.068665 | 0.041199 | 123.024 | 122.9599 | 122.8821 | 122.9233 | -123.056 | -122.9507 | 122.7768 | 0.004578 | 53.7048 | 54.2084
389.1719 | 123.1247 | -58.4747 | 64.5172 | 0.030975 | 0.00019446 | 0.063307 | 0.064345 | -0.00090783 | -0.0010125 | 0.00093559 | -0.059326 | 0.0015295 | 0.001068 | 0.0043322 | -0.0010787 | -0.0017347 | 0.0015209 | -4.7424 | 64.4623 | -58.6121 | 64.2929 | -58.3649 | -58.699 | -58.6716 | -4.2389 | 64.5035 | -58.4885 | -58.4702 | -58.4473 | -58.58 | -58.2779 | -0.13733 | -0.054932 | -0.2243 | 0.10986 | -0.19684 | -0.22431 | -0.059509 | -0.086975 | -0.013733 | -0.013733 | -122.9874 | 0.027465 | 0.19684 | -0.10529 | 0.21057 | -0.091553 | 0.24719 | 122.905 | 0.041198 | 0.01831 | 123.0743 | 122.9919 | 122.937 | 122.9782 | -123.1293 | -123.0057 | 122.7676 | 0.004577 | 53.7323 | 54.2358
390.1719 | 123.1018 | -58.5068 | 64.4943 | -0.10635 | -1.9142e-05 | 0.062239 | 0.065627 | 0.00251 | 5.5488e-05 | 0.0020038 | -0.077637 | 0.0019567 | 0.001068 | 0.0043322 | 0.00020289 | 0.0014697 | 0.0019483 | -4.7974 | 64.4211 | -58.6716 | 64.325 | -58.3466 | -58.7219 | -58.667 | -4.2435 | 64.4989 | -58.5205 | -58.4793 | -58.4702 | -58.6029 | -58.287 | -0.1648 | -0.073242 | -0.16937 | 0.16022 | -0.16022 | -0.21515 | 0.004578 | -0.050354 | -0.013733 | 0.004577 | -122.9736 | 0.036621 | 0.21973 | -0.09613 | 0.23346 | -0.082397 | 0.32501 | 122.9965 | 0.050354 | 0.041199 | 123.0927 | 123.0194 | 122.9279 | 123.0057 | -123.1659 | -123.0148 | 122.8317 | 0.027466 | 53.7094 | 54.2633
391.1719 | 123.1842 | -58.4702 | 64.4257 | -0.13687 | -0.00044654 | 0.062453 | 0.062423 | -0.0049668 | -0.00058531 | 0.00029479 | 0.016968 | 0.0013159 | 2.8e-08 | -0.00229 | 0.00041649 | -0.0030163 | 0.0010937 | -4.8523 | 64.4394 | -58.5938 | 64.3158 | -58.3191 | -58.7173 | -58.6441 | -4.2664 | 64.4485 | -58.4976 | -58.4427 | -58.4152 | -58.5251 | -58.2367 | -0.1236 | 0.013733 | -0.10986 | 0.15106 | -0.17395 | -0.24719 | -0.050354 | -0.1236 | -0.027466 | 0.022888 | -122.8683 | 0.054932 | 0.23346 | -0.054931 | 0.26093 | -0.027465 | 0.27466 | 122.9095 | 0.082398 | 0.054932 | 123.0331 | 122.9462 | 122.9095 | 122.9187 | -123.0194 | -122.9233 | 122.786 | 0.027466 | 53.6179 | 54.2038
392.1719 | 123.1888 | -58.4656 | 64.4577 | -0.098725 | 0.0014761 | 0.064162 | 0.062423 | -0.001976 | -0.00037171 | -0.0022686 | 0.029175 | 3.4148e-05 | -0.0019226 | -0.0020764 | 0.0014847 | -0.00088008 | -0.0029651 | -4.7928 | 64.4394 | -58.5617 | 64.3158 | -58.3145 | -58.6807 | -58.6578 | -4.3259 | 64.444 | -58.5251 | -58.4564 | -58.4198 | -58.5388 | -58.2413 | -0.096131 | -0.018311 | -0.14191 | 0.15106 | -0.19226 | -0.21515 | -0.09613 | -0.11902 | -0.059509 | -0.013733 | -122.9141 | 0.045776 | 0.2243 | -0.073242 | 0.28381 | -0.013733 | 0.24719 | 122.8775 | 0.10528 | 0.068664 | 123.0011 | 122.9691 | 122.905 | 122.9095 | -123.0194 | -122.9828 | 122.7814 | 0.009155 | 53.6728 | 54.1397
393.1719 | 123.2025 | -58.4518 | 64.4531 | -0.022431 | -1.9142e-05 | 0.062666 | 0.06285 | -0.00069423 | 0.00048269 | -0.00034601 | 0.016968 | 0.0017431 | 0.0019226 | -0.0018628 | -1.0706e-05 | -0.0028027 | -0.0016833 | -4.8157 | 64.4302 | -58.5571 | 64.3936 | -58.2138 | -58.5983 | -58.5571 | -4.1428 | 64.4531 | -58.4518 | -58.3694 | -58.3237 | -58.429 | -58.1818 | -0.10529 | -0.022888 | -0.059509 | 0.23804 | -0.10529 | -0.14649 | 0 | -0.041199 | 0 | 0 | -122.8226 | 0.12817 | 0.27008 | 0.022888 | 0.27008 | 0.022888 | 0.34332 | 122.9507 | 0.12817 | 0.082397 | 122.9874 | 122.905 | 122.8821 | 122.905 | -123.0103 | -122.905 | 122.8455 | 0.082397 | 53.6362 | 54.3091
394.1719 | 123.1567 | -58.4702 | 64.4531 | -0.11398 | -0.0015145 | 0.062239 | 0.061782 | -0.001976 | -0.0014399 | -0.0014142 | 0.044434 | 0.00088875 | -0.00064077 | -0.00015378 | -1.0706e-05 | -0.00023928 | 0.0028027 | -4.9026 | 64.4073 | -58.6029 | 64.3158 | -58.3191 | -58.699 | -58.6578 | -4.4083 | 64.4669 | -58.5114 | -58.4747 | -58.4564 | -58.5617 | -58.2596 | -0.13275 | -0.045776 | -0.13733 | 0.15106 | -0.18768 | -0.22888 | -0.054932 | -0.096131 | -0.041199 | 0.013733 | -122.9279 | 0.013733 | 0.21057 | -0.091553 | 0.25177 | -0.050354 | 0.28381 | 122.9187 | 0.054932 | 0.036622 | 123.0103 | 122.9782 | 122.8775 | 122.937 | -123.056 | -122.9645 | 122.786 | -0.004577 | 53.5675 | 54.0619
395.1719 | 123.1201 | -58.4427 | 64.5035 | -0.03006 | -0.00066014 | 0.064375 | 0.064345 | -0.0038986 | -0.0033625 | 0.0015766 | -0.037964 | 0.0017431 | 0.00042723 | 0.0068958 | -0.0012925 | -0.0013073 | -0.0010425 | -4.8889 | 64.4714 | -58.6166 | 64.2883 | -58.374 | -58.6945 | -58.6807 | -4.3304 | 64.5172 | -58.5068 | -58.4427 | -58.4427 | -58.5846 | -58.2596 | -0.17395 | -0.032043 | -0.21515 | 0.068665 | -0.23804 | -0.25177 | -0.064087 | -0.07782 | -0.064087 | 0.013733 | -122.9462 | 0 | 0.1831 | -0.14191 | 0.24719 | -0.07782 | 0.24262 | 122.905 | 0.064087 | 0.064087 | 123.0881 | 123.024 | 122.9141 | 122.9599 | -123.1201 | -123.0103 | 122.731 | 0 | 53.5538 | 54.1122
396.1719 | 123.2254 | -58.429 | 64.4485 | -0.068207 | -0.00087374 | 0.064375 | 0.063277 | -0.0032578 | 0.00069649 | 8.1188e-05 | 0.047485 | -0.00017945 | -0.00085457 | -0.0025036 | 0.00084389 | -0.0010937 | -0.0018971 | -4.8843 | 64.4394 | -58.5709 | 64.3799 | -58.2687 | -58.6349 | -58.5846 | -4.2526 | 64.4485 | -58.4656 | -58.3786 | -58.3466 | -58.461 | -58.2001 | -0.14191 | -0.009155 | -0.068664 | 0.16022 | -0.15564 | -0.20599 | -0.013733 | -0.064087 | -0.036621 | 0 | -122.8271 | 0.082397 | 0.22888 | -0.032044 | 0.2655 | 0.004577 | 0.30212 | 122.9507 | 0.11902 | 0.086975 | 123.0103 | 122.9141 | 122.8683 | 122.8775 | -123.0194 | -122.9141 | 122.8088 | 0.050354 | 53.5446 | 54.1763
397.1719 | 123.1796 | -58.4518 | 64.4669 | -0.037689 | 0.00040806 | 0.064375 | 0.063277 | -5.343e-05 | -0.00058531 | 0.001363 | 0.023071 | -0.0016749 | 0.0012818 | -0.0054944 | -0.0010787 | -0.00088008 | -0.00040166 | -4.8843 | 64.4165 | -58.5938 | 64.3524 | -58.2779 | -58.6349 | -58.5846 | -4.3304 | 64.4531 | -58.4885 | -58.3923 | -58.3694 | -58.4747 | -58.2047 | -0.14191 | -0.050354 | -0.11444 | 0.17395 | -0.13275 | -0.18311 | 0.009155 | -0.041199 | -0.036621 | -0.013733 | -122.8592 | 0.082397 | 0.24719 | -0.022888 | 0.28381 | 0.013733 | 0.31586 | 122.9462 | 0.11902 | 0.09613 | 123.0103 | 122.9416 | 122.8683 | 122.905 | -123.0606 | -122.9553 | 122.8043 | 0.059509 | 53.5675 | 54.1214
398.1719 | 123.1705 | -58.4381 | 64.4669 | -0.052948 | 0.0016899 | 0.065016 | 0.063705 | 0.0016556 | -0.0012261 | 0.0011494 | 0.016968 | -0.00082025 | 0.0021362 | -0.00036738 | 0.00084389 | -0.00066648 | 0.00088014 | -4.9438 | 64.4028 | -58.5846 | 64.3066 | -58.3466 | -58.6761 | -58.6029 | -4.454 | 64.4669 | -58.493 | -58.4564 | -58.4152 | -58.5297 | -58.2596 | -0.14648 | -0.064087 | -0.16022 | 0.091552 | -0.16479 | -0.23804 | -0.01831 | -0.091552 | -0.054932 | 0 | -122.9233 | 0.022888 | 0.17853 | -0.091553 | 0.23346 | -0.036621 | 0.23804 | 122.8912 | 0.07782 | 0.036621 | 122.9874 | 122.9599 | 122.8409 | 122.905 | -123.0515 | -122.9599 | 122.7448 | -0.018311 | 53.4943 | 53.9841
399.1719 | 123.2025 | -58.4702 | 64.4669 | -0.014801 | -0.0015145 | 0.063094 | 0.057937 | 0.00058737 | -0.00079891 | -0.0024822 | 0.013916 | 0.0023839 | 0.00064083 | -0.0016492 | -0.00086511 | -0.0021619 | -0.0023243 | -4.9393 | 64.4348 | -58.5938 | 64.357 | -58.3054 | -58.6487 | -58.6121 | -4.4174 | 64.4531 | -58.4793 | -58.429 | -58.3878 | -58.4885 | -58.2047 | -0.1236 | -0.032044 | -0.10986 | 0.16479 | -0.14191 | -0.17853 | -0.018311 | -0.054932 | -0.009155 | -0.013733 | -122.8958 | 0.082398 | 0.2655 | -0.01831 | 0.27466 | -0.009155 | 0.28839 | 122.9507 | 0.091553 | 0.050354 | 123.0286 | 122.9324 | 122.905 | 122.9233 | -123.0606 | -122.9462 | 122.8271 | 0.041199 | 53.5309 | 54.0527
400.1719 | 123.0789 | -58.4702 | 64.5035 | -0.060578 | 0.00062166 | 0.064162 | 0.065627 | 0.0033646 | 5.5488e-05 | -0.0018414 | -0.03186 | 0.00088875 | 0.00085443 | 0.0028368 | 0.00020289 | -0.0010937 | -0.0029651 | -4.8798 | 64.4577 | -58.6029 | 64.3112 | -58.3603 | -58.6899 | -58.6716 | -4.4952 | 64.5218 | -58.4839 | -58.4702 | -58.4473 | -58.5617 | -58.2596 | -0.13275 | -0.045776 | -0.19226 | 0.10986 | -0.20142 | -0.21973 | -0.068665 | -0.086975 | -0.013733 | 0.018311 | -122.9736 | 0.022888 | 0.21057 | -0.091553 | 0.2243 | -0.07782 | 0.24261 | 122.9141 | 0.036621 | 0.013733 | 123.0606 | 123.0057 | 122.9279 | 122.9919 | -123.1064 | -122.9874 | 122.7814 | 0 | 53.5904 | 53.9749
401.1719 | 123.1338 | -58.4564 | 64.4669 | -0.098725 | 0.0014761 | 0.063307 | 0.062636 | -0.00090783 | 0.0024053 | -0.00098701 | 0.016968 | 0.0025975 | -0.00085457 | -0.0016492 | -0.00043791 | -0.0013073 | 0.0038709 | -4.9438 | 64.4073 | -58.58 | 64.3066 | -58.3282 | -58.7082 | -58.6487 | -4.5776 | 64.4394 | -58.461 | -58.4473 | -58.3328 | -58.4106 | -58.1268 | -0.1236 | -0.059509 | -0.16022 | 0.12817 | -0.19226 | -0.25177 | -0.068665 | -0.12817 | -0.004578 | -0.027466 | -122.9141 | 0.1236 | 0.32959 | 0.045776 | 0.33417 | 0.050354 | 0.25177 | 122.8867 | 0.12817 | 0.013733 | 122.9874 | 122.9004 | 122.8638 | 122.8958 | -123.0469 | -122.9279 | 122.7631 | 0.009155 | 53.5126 | 53.8788
402.1719 | 123.1522 | -58.4702 | 64.4531 | -0.060578 | -0.0010873 | 0.066725 | 0.061782 | 0.003151 | 0.00069649 | 0.001363 | 0.035278 | 0.0015295 | -0.0010682 | 0.00027342 | 0.0010575 | -0.0023755 | 0.0015209 | -4.9576 | 64.4119 | -58.6075 | 64.325 | -58.3145 | -58.7036 | -58.6441 | -4.6005 | 64.4669 | -58.5159 | -58.4564 | -58.4427 | -58.548 | -58.2596 | -0.13733 | -0.041199 | -0.12817 | 0.15564 | -0.17395 | -0.23346 | -0.036621 | -0.09613 | -0.045776 | 0.013733 | -122.9095 | 0.027466 | 0.21057 | -0.07782 | 0.25635 | -0.032044 | 0.29297 | 122.9324 | 0.073242 | 0.059509 | 123.0194 | 122.9828 | 122.8821 | 122.937 | -123.0606 | -122.9691 | 122.7951 | 0.013733 | 53.5126 | 53.8696
403.1719 | 123.175 | -58.4702 | 64.4577 | -0.12161 | 0.00083526 | 0.065443 | 0.063491 | -0.003685 | -0.00079891 | -0.00034601 | 0.029175 | 3.4148e-05 | 0.00064083 | 0.00048702 | 0.00020289 | -0.00045288 | -0.0025379 | -4.9484 | 64.4073 | -58.5846 | 64.3524 | -58.2825 | -58.6578 | -58.5938 | -4.5502 | 64.4531 | -58.493 | -58.4198 | -58.3694 | -58.4976 | -58.2138 | -0.11444 | -0.050354 | -0.10529 | 0.18768 | -0.1236 | -0.18768 | -0.009155 | -0.073242 | -0.022888 | -0.004578 | -122.8775 | 0.10071 | 0.25635 | -0.027466 | 0.27924 | -0.004578 | 0.30212 | 122.937 | 0.1236 | 0.073242 | 122.9919 | 122.9462 | 122.8775 | 122.9233 | -123.0423 | -122.9507 | 122.8226 | 0.050354 | 53.5217 | 53.92
404.1719 | 123.1476 | -58.4747 | 64.476 | -0.060578 | -0.0015145 | 0.063948 | 0.061996 | -0.0013352 | -0.00015811 | 0.00072199 | 0.010864 | -0.00039305 | 0.00085443 | -0.0059216 | -0.0023605 | -0.0015211 | 2.554e-05 | -4.9896 | 64.4073 | -58.6075 | 64.3158 | -58.3282 | -58.699 | -58.6533 | -4.7012 | 64.4485 | -58.493 | -58.4839 | -58.4564 | -58.5663 | -58.2779 | -0.13275 | -0.068664 | -0.16022 | 0.14648 | -0.17853 | -0.22431 | -0.045776 | -0.091553 | -0.018311 | -0.027466 | -122.9599 | 0.01831 | 0.19684 | -0.091553 | 0.21515 | -0.073242 | 0.27924 | 122.9233 | 0.036621 | 0.009155 | 123.0148 | 122.9416 | 122.8821 | 122.9233 | -123.0835 | -122.9691 | 122.7905 | -0.009156 | 53.4851 | 53.7735
405.1719 | 123.175 | -58.4518 | 64.4669 | -0.10635 | 0.0016899 | 0.062453 | 0.06285 | -0.0011214 | -0.00058531 | 0.00029479 | 0.0047608 | -0.0012477 | -0.0012818 | -0.0010084 | -0.00022431 | -0.00088008 | 0.0013073 | -5.0034 | 64.4302 | -58.6029 | 64.325 | -58.3237 | -58.7036 | -58.6349 | -4.6692 | 64.4577 | -58.4793 | -58.4381 | -58.4061 | -58.5159 | -58.2458 | -0.15106 | -0.036621 | -0.14191 | 0.12817 | -0.18311 | -0.25177 | -0.032044 | -0.10071 | -0.027466 | -0.009155 | -122.905 | 0.045776 | 0.20599 | -0.064087 | 0.23346 | -0.036621 | 0.27924 | 122.9279 | 0.073242 | 0.041199 | 123.0331 | 122.937 | 122.8821 | 122.9095 | -123.0698 | -122.9462 | 122.7768 | 0.013733 | 53.4485 | 53.7827
406.1719 | 123.1247 | -58.461 | 64.4531 | -0.11398 | 0.0031851 | 0.064162 | 0.063277 | -0.0013352 | -0.0016535 | 0.0011494 | -0.03186 | -0.00060665 | 0.0019226 | 0.00070062 | -0.0015061 | 0.00082892 | 0.0028027 | -5.0308 | 64.4028 | -58.5983 | 64.3204 | -58.3191 | -58.7128 | -58.6441 | -4.7516 | 64.444 | -58.5205 | -58.4518 | -58.429 | -58.5526 | -58.2687 | -0.13733 | -0.050354 | -0.13275 | 0.14191 | -0.1831 | -0.25177 | -0.045776 | -0.11444 | -0.059509 | -0.009155 | -122.905 | 0.032044 | 0.19226 | -0.091552 | 0.25177 | -0.032043 | 0.27924 | 122.9187 | 0.091553 | 0.068665 | 123.0011 | 122.9645 | 122.8638 | 122.905 | -123.0515 | -122.9736 | 122.7814 | 0.009156 | 53.4302 | 53.7094
407.1719 | 123.1613 | -58.461 | 64.4394 | -0.075836 | -0.00044654 | 0.064589 | 0.064132 | -0.00069423 | -0.0027215 | -0.00034601 | -0.019653 | -0.00017945 | -0.00042717 | -0.0020764 | -0.0049241 | -0.00023928 | 0.0017345 | -5.0308 | 64.4211 | -58.5938 | 64.325 | -58.3282 | -58.7128 | -58.6349 | -4.7882 | 64.4577 | -58.4976 | -58.4106 | -58.4885 | -58.5892 | -58.2642 | -0.13275 | -0.01831 | -0.11444 | 0.13275 | -0.17395 | -0.25177 | -0.041199 | -0.11902 | -0.036621 | 0.018311 | -122.85 | -0.027465 | 0.19684 | -0.12817 | 0.23346 | -0.091552 | 0.2655 | 122.9187 | 0.009156 | 0.086975 | 123.0148 | 122.9553 | 122.8821 | 122.9187 | -123.0331 | -122.937 | 122.7859 | 0.050354 | 53.4302 | 53.6728
408.1719 | 123.1522 | -58.461 | 64.4073 | -0.075836 | 0.0016899 | 0.064162 | 0.064345 | -0.0017624 | -0.0010125 | -0.00055961 | -0.016602 | -0.00060665 | -0.0025636 | 0.001128 | -0.0012925 | 0.00061532 | 0.0023755 | -5.0308 | 64.3936 | -58.5983 | 64.3433 | -58.2825 | -58.7173 | -58.6166 | -4.7882 | 64.4211 | -58.4976 | -58.4473 | -58.4518 | -58.548 | -58.2642 | -0.13733 | -0.013733 | -0.064087 | 0.17853 | -0.15564 | -0.25635 | -0.01831 | -0.11902 | -0.036621 | 0.013733 | -122.8546 | 0.009156 | 0.19684 | -0.086975 | 0.23346 | -0.050354 | 0.31586 | 122.9416 | 0.045777 | 0.050354 | 122.9919 | 122.9187 | 122.8546 | 122.8821 | -123.0057 | -122.905 | 122.8043 | 0.013733 | 53.4302 | 53.6728
409.1719 | 123.1613 | -58.4473 | 64.4073 | -0.091095 | -0.00087374 | 0.064589 | 0.063705 | 0.0018692 | 0.00091009 | -0.0018414 | -0.016602 | -0.0014613 | 0.00042723 | -0.0037854 | 0.00020289 | 0.0012561 | -0.0012561 | -5.0537 | 64.3845 | -58.5983 | 64.3616 | -58.2733 | -58.6716 | -58.6075 | -4.8065 | 64.444 | -58.493 | -58.4244 | -58.4244 | -58.5297 | -58.2321 | -0.15106 | -0.022889 | -0.045777 | 0.17395 | -0.16022 | -0.2243 | -0.009155 | -0.073242 | -0.045776 | 0.036621 | -122.8317 | 0.022889 | 0.21515 | -0.082397 | 0.26093 | -0.036621 | 0.32501 | 122.9599 | 0.068665 | 0.068665 | 122.9828 | 122.937 | 122.8317 | 122.8912 | -123.0057 | -122.9004 | 122.8088 | 0.022889 | 53.3936 | 53.6407
410.1719 | 123.1293 | -58.4656 | 64.4257 | -0.060578 | 0.0016899 | 0.063521 | 0.063277 | 0.0012284 | 0.00069649 | -0.0029096 | -0.0013428 | -0.00060665 | 0.0014954 | -0.0014356 | 0.00020289 | -0.00088008 | -0.0021107 | -5.0903 | 64.4073 | -58.6166 | 64.3158 | -58.3282 | -58.699 | -58.6395 | -4.9118 | 64.4302 | -58.5114 | -58.4656 | -58.3054 | -58.4152 | -58.2367 | -0.15106 | -0.01831 | -0.10986 | 0.13733 | -0.17395 | -0.23346 | -0.022888 | -0.082398 | -0.045777 | 0.004578 | -122.8912 | 0.16022 | 0.22888 | 0.050354 | 0.27466 | 0.096131 | 0.28839 | 122.9324 | 0.20599 | 0.045777 | 123.024 | 122.9416 | 122.8729 | 122.8958 | -123.0423 | -122.937 | 122.7814 | 0 | 53.3752 | 53.5538
411.1719 | 123.1659 | -58.4518 | 64.4394 | -0.098725 | 0.0021171 | 0.065871 | 0.065627 | 0.00251 | -0.00058531 | 0.00072199 | -0.037964 | -0.0021021 | -0.00085457 | 0.001128 | -0.0023605 | 0.00040152 | 2.554e-05 | -5.1041 | 64.3753 | -58.5846 | 64.3524 | -58.2642 | -58.6624 | -58.6258 | -4.8889 | 64.4257 | -58.493 | -58.4198 | -58.4244 | -58.5434 | -58.2321 | -0.13275 | -0.064087 | -0.086975 | 0.18768 | -0.17395 | -0.21057 | -0.041198 | -0.07782 | -0.041199 | -0.013733 | -122.8592 | 0.027466 | 0.21973 | -0.091553 | 0.26093 | -0.050354 | 0.32044 | 122.937 | 0.068665 | 0.073242 | 122.9599 | 122.9187 | 122.8271 | 122.8775 | -123.024 | -122.9324 | 122.8043 | 0.032043 | 53.3478 | 53.5629
412.1719 | 123.1659 | -58.461 | 64.4302 | -0.12161 | 0.00083526 | 0.065657 | 0.063705 | -0.00069423 | -0.00037171 | 0.0015766 | -0.016602 | 0.0019567 | -0.0014954 | 0.0013416 | -0.0017197 | 0.00040152 | -0.0031787 | -5.1041 | 64.3845 | -58.6029 | 64.3707 | -58.2779 | -58.6899 | -58.6029 | -4.9393 | 64.4348 | -58.4793 | -58.4152 | -58.429 | -58.5342 | -58.2092 | -0.14191 | -0.045777 | -0.059509 | 0.18311 | -0.14191 | -0.22888 | 0 | -0.086975 | -0.01831 | 0.004577 | -122.8455 | 0.032044 | 0.25177 | -0.073242 | 0.27008 | -0.054932 | 0.32501 | 122.9736 | 0.050354 | 0.064087 | 122.9874 | 122.9141 | 122.8455 | 122.8958 | -123.0331 | -122.9095 | 122.8317 | 0.045777 | 53.3569 | 53.5217
413.1719 | 123.1659 | -58.4427 | 64.4348 | -0.18265 | 0.0016899 | 0.062666 | 0.063277 | 0.00080117 | -0.00037171 | -0.0022686 | -0.037964 | 0.0013159 | -0.00021357 | 0.001128 | -0.0025741 | -0.0015211 | -0.0016833 | -5.072 | 64.3936 | -58.6487 | 64.3478 | -58.2367 | -58.6349 | -58.6349 | -4.9713 | 64.4119 | -58.4702 | -58.4106 | -58.3878 | -58.5068 | -58.2321 | -0.20599 | -0.041198 | -0.086975 | 0.20599 | -0.19226 | -0.19226 | 0.013733 | 0.013733 | -0.027466 | -0.022888 | -122.8455 | 0.054932 | 0.21057 | -0.064087 | 0.23804 | -0.036621 | 0.41199 | 122.9965 | 0.082398 | 0.059509 | 123.0423 | 122.8821 | 122.8363 | 122.8546 | -123.0835 | -122.905 | 122.7905 | 0.032043 | 53.3707 | 53.4714
414.1719 | 123.2117 | -58.461 | 64.444 | -0.052948 | 0.0016899 | 0.065443 | 0.062423 | -0.0015488 | -0.00037171 | -0.002055 | -0.050171 | -0.0010339 | -0.0019226 | 0.001128 | 0.00020289 | 0.0012561 | 0.0019483 | -5.1636 | 64.3982 | -58.5983 | 64.357 | -58.2779 | -58.6853 | -58.6075 | -5.0217 | 64.4302 | -58.5388 | -58.4244 | -58.3328 | -58.5388 | -58.2321 | -0.13733 | -0.045777 | -0.086975 | 0.18311 | -0.14648 | -0.2243 | -0.009155 | -0.086975 | -0.077819 | -0.013733 | -122.8683 | 0.12817 | 0.22888 | -0.077819 | 0.3067 | 0 | 0.32044 | 122.9553 | 0.20599 | 0.11444 | 122.9965 | 122.9691 | 122.8592 | 122.8912 | -123.0423 | -122.9828 | 122.818 | 0.036622 | 53.2974 | 53.4393
415.1719 | 123.1659 | -58.4702 | 64.4348 | -0.098725 | 0.0014761 | 0.065016 | 0.063705 | 0.004219 | 0.00091009 | 0.00093559 | -0.0013428 | 0.0015295 | 0.00064083 | 0.0030506 | -1.0706e-05 | 0.00061532 | 0.00023934 | -5.191 | 64.4073 | -58.5892 | 64.357 | -58.2687 | -58.6807 | -58.5938 | -5.0262 | 64.4302 | -58.4839 | -58.4152 | -58.4061 | -58.5068 | -58.2138 | -0.11902 | -0.027465 | -0.077819 | 0.20142 | -0.1236 | -0.21057 | -0.004578 | -0.091553 | -0.013733 | -0.004577 | -122.85 | 0.064087 | 0.25635 | -0.036621 | 0.27008 | -0.022888 | 0.32043 | 122.9462 | 0.07782 | 0.068665 | 122.9965 | 122.9141 | 122.8775 | 122.9004 | -123.024 | -122.9187 | 122.8271 | 0.054932 | 53.2791 | 53.4439
416.1719 | 123.1888 | -58.429 | 64.4531 | -0.11398 | 0.00019446 | 0.06523 | 0.06755 | 0.00058737 | -0.0027215 | 0.002431 | -0.022705 | -0.00082025 | 0.0014954 | 0.0043322 | -0.00065151 | 0.00082892 | 0.00066654 | -5.2094 | 64.3799 | -58.6121 | 64.4989 | -58.2458 | -58.6945 | -58.5754 | -5.0674 | 64.4348 | -58.4839 | -58.4061 | -58.3878 | -58.5251 | -58.223 | -0.18311 | -0.073242 | 0.045776 | 0.18311 | -0.14648 | -0.2655 | 0.036622 | -0.082397 | -0.054932 | -0.018311 | -122.8592 | 0.041199 | 0.20599 | -0.09613 | 0.26093 | -0.041198 | 0.36621 | 123.111 | 0.096131 | 0.07782 | 122.9919 | 122.9187 | 122.8088 | 122.8638 | -123.0652 | -122.937 | 122.9279 | 0.022888 | 53.2196 | 53.3615
417.1719 | 123.1888 | -58.4335 | 64.4302 | -0.068207 | 0.0016899 | 0.064589 | 0.065414 | -0.0013352 | -0.0010125 | -0.0014142 | -0.056274 | 0.00067495 | -0.00064077 | -0.00464 | -0.0027877 | 0.00061532 | -0.00040166 | -5.2185 | 64.389 | -58.5938 | 64.3662 | -58.2825 | -58.6761 | -58.6304 | -5.0766 | 64.4257 | -58.5159 | -58.4198 | -58.3694 | -58.5068 | -58.2184 | -0.16022 | -0.041199 | -0.064087 | 0.15106 | -0.19684 | -0.24261 | -0.036621 | -0.082397 | -0.082397 | -0.004578 | -122.85 | 0.064087 | 0.21515 | -0.073242 | 0.29755 | 0.009155 | 0.31128 | 122.9599 | 0.14648 | 0.09613 | 122.9828 | 122.9416 | 122.8226 | 122.8592 | -123.024 | -122.9462 | 122.7997 | 0.013733 | 53.215 | 53.3569
418.1719 | 123.2025 | -58.4427 | 64.4073 | -0.083466 | 0.0014761 | 0.065443 | 0.063277 | 0.0012284 | -0.0010125 | 0.00050839 | -0.041016 | 0.00024775 | -0.0032044 | 0.0051868 | -0.00043791 | 0.00040152 | -0.0021107 | -5.2689 | 64.389 | -58.5983 | 64.357 | -58.2779 | -58.6807 | -58.6349 | -5.1727 | 64.4394 | -58.493 | -58.3969 | -58.3969 | -58.5114 | -58.1909 | -0.15564 | -0.018311 | -0.050354 | 0.16479 | -0.19226 | -0.23804 | -0.036621 | -0.082397 | -0.050354 | 0.032043 | -122.8043 | 0.045776 | 0.25177 | -0.068665 | 0.30212 | -0.018311 | 0.32044 | 122.9553 | 0.09613 | 0.09613 | 122.9874 | 122.9324 | 122.8317 | 122.8821 | -123.0057 | -122.9004 | 122.7997 | 0.045776 | 53.1738 | 53.27
419.1719 | 123.2025 | -58.4427 | 64.4577 | -0.11398 | 0.0021171 | 0.065016 | 0.062636 | 0.00016017 | 0.00026909 | -0.0012006 | -0.06543 | -0.0010339 | -0.00042717 | -0.00036738 | -0.0010787 | 0.0010425 | 0.0030163 | -5.2689 | 64.357 | -58.6212 | 64.1876 | -58.3832 | -58.4839 | -58.4793 | -5.1773 | 64.444 | -58.493 | -58.4015 | -58.4106 | -58.5342 | -58.223 | -0.17853 | -0.10071 | -0.27008 | 0.059509 | -0.036621 | -0.041199 | 0.14191 | 0.13733 | -0.050354 | -0.013733 | -122.8592 | 0.032043 | 0.21973 | -0.091553 | 0.27008 | -0.041199 | 0.23804 | 122.8088 | 0.082397 | 0.091553 | 122.9782 | 122.937 | 122.7997 | 122.8867 | -123.0789 | -122.9507 | 122.6303 | 0.041199 | 53.1738 | 53.2654
420.1719 | 123.1705 | -58.4335 | 64.4485 | -0.12161 | 0.0042533 | 0.065016 | 0.063491 | -5.343e-05 | 0.0026191 | -0.0029096 | -0.037964 | -0.00039305 | 0.00064083 | 0.0034778 | -0.0025741 | -0.0010937 | -0.0038197 | -5.2185 | 64.389 | -58.6029 | 64.3616 | -58.287 | -58.6945 | -58.6258 | -5.2505 | 64.4394 | -58.4885 | -58.5251 | -58.3694 | -58.3191 | -58.0536 | -0.16937 | -0.059509 | -0.086975 | 0.14648 | -0.19226 | -0.26093 | -0.022888 | -0.091553 | -0.054931 | -0.009155 | -122.9736 | 0.064087 | 0.37994 | 0.11444 | 0.43487 | 0.16937 | 0.31586 | 122.9645 | 0.11902 | -0.036621 | 122.9919 | 122.9279 | 122.8226 | 122.8729 | -123.0515 | -122.937 | 122.7951 | -0.091552 | 53.215 | 53.183
421.1719 | 123.0789 | -58.4747 | 64.4623 | -0.060578 | -0.00066014 | 0.063734 | 0.064986 | 0.0087052 | -0.00015811 | 0.0022174 | -0.016602 | 0.0017431 | 0.001068 | 0.0064684 | -0.0012925 | 0.0023241 | -0.0033923 | -5.3101 | 64.4348 | -58.6212 | 64.3066 | -58.1451 | -58.6624 | -58.7357 | -5.4153 | 64.4943 | -58.5251 | -58.5022 | -58.5342 | -58.6578 | -58.3145 | -0.14648 | -0.027466 | -0.15564 | 0.32959 | -0.26093 | -0.18768 | -0.11444 | -0.041199 | -0.050354 | 0.032044 | -122.9645 | -0.05951 | 0.16022 | -0.18311 | 0.21057 | -0.13275 | 0.47607 | 122.9279 | -0.009156 | 0.022888 | 123.056 | 123.0194 | 122.9095 | 122.9691 | -123.0835 | -122.9874 | 122.7814 | -0.027466 | 53.1647 | 53.0594
422.1719 | 123.1155 | -58.4702 | 64.4623 | -0.052948 | 0.0027579 | 0.064375 | 0.064132 | 0.001442 | -0.00079891 | -0.0016278 | -0.062378 | 3.4148e-05 | -0.00042717 | 0.0051868 | -0.00022431 | -0.0013073 | -0.0016833 | -5.3467 | 64.4623 | -58.6029 | 64.2654 | -58.374 | -58.7677 | -58.7173 | -5.4337 | 64.4714 | -58.5159 | -58.4702 | -58.4793 | -58.6121 | -58.2916 | -0.13275 | 0 | -0.19684 | 0.096131 | -0.24719 | -0.29755 | -0.11444 | -0.16479 | -0.045776 | 0.009156 | -122.9324 | -0.009155 | 0.17853 | -0.14191 | 0.2243 | -0.096131 | 0.22888 | 122.8683 | 0.036621 | 0.045776 | 123.0652 | 122.9874 | 122.9324 | 122.9416 | -123.0652 | -122.9782 | 122.7356 | 0 | 53.1235 | 53.0365
423.1719 | 123.1476 | -58.4702 | 64.4485 | -0.075836 | 0.0014761 | 0.063734 | 0.06285 | 0.0029374 | 0.00048269 | 0.001363 | -0.047119 | -0.0016749 | 0.0025634 | -0.0035718 | -0.00022431 | 0.00061532 | -0.00061526 | -5.3696 | 64.4394 | -58.6212 | 64.2929 | -58.3649 | -58.7448 | -58.6807 | -5.4474 | 64.4669 | -58.4839 | -58.4152 | -58.4106 | -58.5663 | -58.2413 | -0.15106 | -0.009155 | -0.15564 | 0.10529 | -0.21057 | -0.27466 | -0.059509 | -0.1236 | -0.013733 | 0.018311 | -122.8638 | 0.059509 | 0.22888 | -0.09613 | 0.24262 | -0.082397 | 0.25635 | 122.9141 | 0.073242 | 0.068665 | 123.0606 | 122.9507 | 122.9095 | 122.937 | -123.0698 | -122.9324 | 122.7631 | 0.054932 | 53.1006 | 53.0228
424.1719 | 123.1384 | -58.4885 | 64.4531 | -0.083466 | 0.00040806 | 0.063094 | 0.065841 | 0.003151 | -0.00015811 | 0.00093559 | -0.053223 | 0.00046135 | 0.001709 | 0.0081774 | -0.0015061 | 0.0012561 | 0.0015209 | -5.397 | 64.4531 | -58.6487 | 64.2609 | -58.3786 | -58.7723 | -58.6945 | -5.5069 | 64.4714 | -58.5114 | -58.4427 | -58.4702 | -58.5754 | -58.2687 | -0.16022 | 0 | -0.19226 | 0.10986 | -0.20599 | -0.28381 | -0.045776 | -0.1236 | -0.022889 | 0.018311 | -122.8958 | 0.01831 | 0.21973 | -0.086975 | 0.24262 | -0.064086 | 0.27008 | 122.9095 | 0.041199 | 0.068665 | 123.1018 | 122.9828 | 122.9416 | 122.9599 | -123.1018 | -122.9645 | 122.7493 | 0.045776 | 53.0914 | 52.9816
425.1719 | 123.1064 | -58.4793 | 64.4577 | -0.083466 | 0.0023307 | 0.065016 | 0.064986 | 0.00016017 | -0.00037171 | 8.1188e-05 | -0.03186 | 0.0011023 | 0.00042723 | 0.0017688 | -0.00043791 | -0.00066648 | -0.00018806 | -5.4291 | 64.4531 | -58.6212 | 64.2609 | -58.3786 | -58.7677 | -58.7219 | -5.5664 | 64.4669 | -58.5159 | -58.4839 | -58.4885 | -58.6212 | -58.2733 | -0.14191 | -0.004578 | -0.19684 | 0.10071 | -0.24262 | -0.28839 | -0.10071 | -0.14648 | -0.036621 | 0.009155 | -122.9416 | -0.009155 | 0.20599 | -0.14191 | 0.24262 | -0.10529 | 0.24261 | 122.8821 | 0.027466 | 0.032043 | 123.0743 | 122.9828 | 122.9324 | 122.9462 | -123.0789 | -122.9736 | 122.7402 | -0.004578 | 53.0502 | 52.9129
426.1719 | 123.1888 | -58.4198 | 64.444 | -0.10635 | -0.00023294 | 0.063307 | 0.065414 | -0.0028304 | 0.0011237 | 0.00093559 | -0.034912 | 0.0011023 | 0.0014954 | -0.00229 | 0.0016983 | -0.0017347 | 0.00045294 | -5.4886 | 64.4119 | -58.6166 | 64.2929 | -58.3466 | -58.754 | -58.6807 | -5.5481 | 64.4485 | -58.5022 | -58.4015 | -58.4152 | -58.5663 | -58.2367 | -0.19684 | -0.032044 | -0.15106 | 0.073242 | -0.26093 | -0.33417 | -0.064087 | -0.13733 | -0.082397 | 0.004577 | -122.8455 | 0.004578 | 0.18311 | -0.14648 | 0.2655 | -0.064087 | 0.27008 | 122.9095 | 0.086975 | 0.10071 | 123.0286 | 122.9507 | 122.8317 | 122.8683 | -123.0606 | -122.9462 | 122.7127 | 0.018311 | 52.9312 | 52.8717
427.1719 | 123.0743 | -58.4885 | 64.4806 | -0.052948 | 0.0012625 | 0.064162 | 0.065841 | 0.0035782 | -0.00037171 | 0.001363 | -0.028809 | 0.0019567 | 0.0019226 | 0.002196 | -0.0012925 | -0.00066648 | 0.0036571 | -5.4977 | 64.4669 | -58.6304 | 64.4485 | -58.2642 | -58.8272 | -58.7265 | -5.8273 | 64.4806 | -58.5022 | -58.5114 | -58.5205 | -58.6624 | -58.3054 | -0.14191 | -0.013733 | -0.032044 | 0.2243 | -0.23804 | -0.33875 | -0.09613 | -0.19684 | -0.013733 | 0 | -122.9919 | -0.032044 | 0.1831 | -0.17395 | 0.19684 | -0.16022 | 0.36621 | 123.0789 | -0.018311 | -0.009156 | 123.0972 | 122.9828 | 122.9553 | 122.9691 | -123.111 | -122.9828 | 122.937 | -0.022889 | 52.9907 | 52.6611
428.1719 | 123.0423 | -58.4793 | 64.4897 | -0.060578 | 0.00019446 | 0.064589 | 0.066482 | -0.0021896 | -0.00079891 | 0.00050839 | -0.044067 | 0.0015295 | -0.00021357 | -0.0014356 | 0.00041649 | 0.00040152 | 0.0025891 | -5.4932 | 64.476 | -58.5754 | 64.2563 | -58.3832 | -58.754 | -58.7036 | -6.9397 | 64.4897 | -58.4976 | -58.5022 | -58.5159 | -58.6395 | -58.3145 | -0.09613 | -0.013733 | -0.23346 | 0.09613 | -0.2243 | -0.27466 | -0.12817 | -0.17853 | -0.018311 | 0 | -122.9919 | -0.036621 | 0.16479 | -0.16022 | 0.18311 | -0.14191 | 0.19226 | 122.8317 | -0.01831 | -0.004577 | 123.0515 | 122.9874 | 122.9553 | 122.9691 | -123.0652 | -122.9874 | 122.7356 | -0.022888 | 52.9861 | 51.5396
429.1719 | 123.1018 | -58.4518 | 64.4531 | -0.11398 | 0.0010489 | 0.06523 | 0.065627 | 0.00016017 | 0.0015509 | -0.0018414 | -0.016602 | 0.0015295 | 0.0014954 | 0.0030506 | -0.00022431 | -0.00066648 | -0.0031787 | -5.5664 | 64.4669 | -58.6258 | 64.2654 | -58.3832 | -58.7448 | -58.6853 | -7.0312 | 64.5172 | -58.4885 | -58.4747 | -58.4885 | -58.6121 | -58.2825 | -0.17395 | 0.013733 | -0.18768 | 0.068664 | -0.23346 | -0.29297 | -0.05951 | -0.11902 | -0.036621 | 0.064087 | -122.9279 | -0.036621 | 0.16937 | -0.16022 | 0.20599 | -0.1236 | 0.24261 | 122.8912 | 0 | 0.013733 | 123.0927 | 123.0057 | 122.9187 | 122.9691 | -123.0789 | -122.9416 | 122.7173 | -0.022888 | 52.8854 | 51.4206
430.1719 | 123.0927 | -58.4656 | 64.4897 | 0.12253 | -0.0023691 | 0.064589 | 0.066054 | -0.0015488 | 0.00048269 | -0.0014142 | -0.016602 | 0.00088875 | -0.00021357 | 0.0026232 | -0.00022431 | -0.00088008 | 0.0040845 | -5.603 | 64.4623 | -58.6029 | 64.27 | -58.3969 | -58.7494 | -58.6899 | -7.1182 | 64.4989 | -58.5068 | -58.4885 | -58.4976 | -58.6121 | -58.2825 | -0.13733 | -0.027466 | -0.21973 | 0.068664 | -0.2243 | -0.28381 | -0.086975 | -0.14648 | -0.041199 | 0.009155 | -122.9782 | -0.032044 | 0.1831 | -0.14648 | 0.2243 | -0.10529 | 0.20599 | 122.8729 | 0.009155 | 0.018311 | 123.0652 | 123.0057 | 122.9279 | 122.9645 | -123.0927 | -122.9965 | 122.7356 | -0.022888 | 52.8625 | 51.3474
431.1719 | 123.0743 | -58.4702 | 64.476 | -0.045319 | 0.00062166 | 0.06288 | 0.064773 | -0.0026168 | -0.0014399 | 0.00050839 | -0.037964 | 0.0015295 | 0.00042723 | 0.00027342 | 0.00020289 | 0.00082892 | 0.0038709 | -5.6168 | 64.4623 | -58.6258 | 64.2517 | -58.4564 | -58.7128 | -58.6899 | -7.1823 | 64.5035 | -58.4885 | -58.493 | -58.4976 | -58.6166 | -58.2825 | -0.15564 | -0.013733 | -0.2243 | 0.013733 | -0.21973 | -0.24262 | -0.064087 | -0.086976 | -0.01831 | 0.027466 | -122.9691 | -0.027466 | 0.18768 | -0.14648 | 0.20599 | -0.12817 | 0.16937 | 122.8775 | -0.009156 | -0.004578 | 123.0881 | 122.9919 | 122.9324 | 122.9736 | -123.1018 | -122.9645 | 122.7219 | -0.022888 | 52.8534 | 51.2878
432.1719 | 123.056 | -58.4702 | 64.4897 | -0.037689 | 0.00062166 | 0.064375 | 0.063918 | 0.00486 | 0.00048269 | 0.0015766 | 0.09021 | 0.00024775 | 0.0014954 | -0.0018628 | -0.0012925 | -0.0013073 | 0.0019483 | -5.6534 | 64.476 | -58.6075 | 64.2471 | -58.3923 | -59.2346 | -58.9005 | -7.3334 | 64.5493 | -58.4839 | -58.5159 | -58.5205 | -58.6075 | -58.2962 | -0.13733 | -0.013733 | -0.24262 | 0.07782 | -0.4303 | -0.76447 | -0.29297 | -0.62714 | -0.013733 | 0.059509 | -123.0057 | -0.050354 | 0.17395 | -0.13733 | 0.18768 | -0.1236 | 0.21515 | 122.8546 | -0.036621 | -0.032043 | 123.0835 | 123.0331 | 122.9462 | 123.0194 | -123.0972 | -122.9736 | 122.7173 | -0.045776 | 52.8168 | 51.1368
433.1719 | 123.0927 | -58.4885 | 64.4669 | -0.045319 | -0.00066014 | 0.064589 | 0.066054 | 0.0027238 | -0.00058531 | -0.00034601 | -0.016602 | -0.00060665 | 0.00085443 | -0.0010084 | 0.0025529 | 0.00018792 | 0.0034435 | -5.69 | 64.4669 | -58.5892 | 64.2654 | -58.3878 | -58.7723 | -58.6899 | -7.3746 | 64.476 | -58.4793 | -58.4885 | -58.4793 | -58.5846 | -58.2687 | -0.10071 | 0 | -0.20142 | 0.10071 | -0.20142 | -0.28381 | -0.10071 | -0.18311 | 0.009155 | 0.009155 | -122.9553 | 0.009155 | 0.21973 | -0.096131 | 0.21057 | -0.10529 | 0.20142 | 122.8546 | 0 | -0.009155 | 123.056 | 122.9553 | 122.9553 | 122.9645 | -123.056 | -122.9462 | 122.7539 | 0 | 52.7985 | 51.1139
434.1719 | 123.0331 | -58.5159 | 64.4714 | -0.060578 | 0.0010489 | 0.063307 | 0.064345 | 0.0018692 | -0.0020807 | -0.00013241 | -0.050171 | 0.0011023 | 0.00042723 | 0.0094592 | -1.0706e-05 | -0.0013073 | -0.0025379 | -5.6946 | 64.4714 | -58.6166 | 64.238 | -58.4244 | -58.7906 | -58.7311 | -7.4982 | 64.4989 | -58.5251 | -58.4885 | -58.5297 | -58.873 | -58.5297 | -0.10071 | 0 | -0.23346 | 0.091553 | -0.21515 | -0.27466 | -0.11444 | -0.17395 | -0.009155 | 0.027465 | -122.9599 | -0.013733 | -0.013733 | -0.35706 | -0.004578 | -0.3479 | 0.19226 | 122.8546 | -0.004578 | 0.036621 | 123.0881 | 123.024 | 122.9874 | 123.0148 | -123.0881 | -122.9965 | 122.7539 | 0.027466 | 52.8213 | 51.0178
435.1719 | 123.0927 | -58.4564 | 64.4897 | -0.28946 | -0.0030099 | 0.061598 | 0.064345 | 0.00058737 | 0.0013373 | 0.00093559 | -0.0074462 | 0.0028113 | 0.00064083 | 0.00091422 | -1.0706e-05 | -0.0010937 | 0.0036571 | -5.5023 | 64.4623 | -58.5938 | 64.2654 | -58.3694 | -58.7448 | -58.7082 | -7.5577 | 64.5126 | -58.4885 | -58.493 | -58.4976 | -58.6349 | -58.3008 | -0.13733 | -0.027466 | -0.2243 | 0.086975 | -0.25177 | -0.28839 | -0.11444 | -0.15106 | -0.032043 | 0.022888 | -122.9828 | -0.041199 | 0.15564 | -0.17853 | 0.18768 | -0.14648 | 0.2243 | 122.8592 | -0.009156 | -0.004578 | 123.056 | 123.0011 | 122.9187 | 122.9691 | -123.0835 | -122.9782 | 122.7219 | -0.036621 | 52.9541 | 50.8987
436.1719 | 123.0286 | -58.4473 | 64.4989 | -0.075836 | 0.00062166 | 0.063734 | 0.06285 | 0.0027238 | 0.00069649 | -0.00055961 | -0.010498 | 0.0017431 | 0.0032044 | 0.00091422 | -0.00065151 | -2.5678e-05 | 0.0025891 | -5.7037 | 64.4852 | -58.5892 | 64.27 | -58.3694 | -58.7631 | -58.7173 | -7.6584 | 64.5035 | -58.5068 | -58.5022 | -58.5159 | -58.6441 | -58.3008 | -0.14191 | -0.013733 | -0.22888 | 0.07782 | -0.27008 | -0.31586 | -0.12817 | -0.17395 | -0.059509 | 0.004578 | -123.0011 | -0.068664 | 0.14648 | -0.19684 | 0.20599 | -0.13733 | 0.21973 | 122.8592 | -0.009155 | 0.004578 | 123.0743 | 123.0103 | 122.9324 | 122.9507 | -123.0881 | -123.0057 | 122.7173 | -0.054931 | 52.7435 | 50.7889
437.1719 | 123.0835 | -58.4564 | 64.4669 | -0.083466 | 0.0025443 | 0.063094 | 0.063705 | -0.00069423 | 5.5488e-05 | -0.00098701 | -0.010498 | 0.00046135 | 0.0012818 | -0.0061352 | -0.00022431 | -0.0015211 | 0.00066654 | -5.7449 | 64.476 | -58.6029 | 64.2471 | -58.374 | -58.7631 | -58.7082 | -7.7042 | 64.4989 | -58.4702 | -58.4656 | -58.4747 | -58.58 | -58.2642 | -0.14648 | 0.009155 | -0.21973 | 0.082398 | -0.25177 | -0.3067 | -0.10529 | -0.16022 | -0.013733 | 0.032043 | -122.9324 | -0.01831 | 0.19226 | -0.1236 | 0.20599 | -0.10986 | 0.22888 | 122.85 | -0.004577 | 0.004578 | 123.0789 | 122.9691 | 122.9324 | 122.9553 | -123.0698 | -122.937 | 122.7036 | -0.009155 | 52.7115 | 50.7523
438.1719 | 123.0011 | -58.5159 | 64.4485 | -0.1445 | 0.00062166 | 0.063307 | 0.065841 | 0.0029374 | 0.0017645 | -0.0016278 | -0.025757 | 0.00088875 | 0.002777 | -0.0020764 | 0.00041649 | -0.0010937 | 0.0064343 | -5.7587 | 64.4897 | -58.5983 | 64.2563 | -58.4198 | -58.786 | -58.7357 | -7.8278 | 64.5172 | -58.4839 | -58.4976 | -58.5114 | -58.7128 | -58.4427 | -0.082398 | 0.041199 | -0.19226 | 0.09613 | -0.21973 | -0.27008 | -0.13733 | -0.18768 | 0.032043 | 0.068665 | -122.9462 | 0.004577 | 0.073242 | -0.19684 | 0.041199 | -0.22888 | 0.17853 | 122.8546 | -0.027466 | -0.013733 | 123.0881 | 123.0011 | 123.0057 | 123.0331 | -123.0469 | -122.9324 | 122.7722 | 0.01831 | 52.7573 | 50.6882
439.1719 | 123.024 | -58.4656 | 64.5081 | 0.00045798 | 0.0021171 | 0.064162 | 0.063491 | -5.343e-05 | 0.00091009 | -0.002055 | -0.01355 | 3.4148e-05 | 0.0014954 | 0.0032642 | -0.00043791 | -0.0010937 | 0.0034435 | -5.7449 | 64.476 | -58.6075 | 64.2746 | -58.3832 | -58.7631 | -58.7219 | -7.901 | 64.5401 | -58.4656 | -58.5159 | -58.548 | -58.6578 | -58.2962 | -0.14191 | -0.032044 | -0.23346 | 0.082397 | -0.25635 | -0.29755 | -0.11444 | -0.15564 | 0 | 0.032043 | -123.024 | -0.082398 | 0.16937 | -0.19226 | 0.16937 | -0.19226 | 0.2243 | 122.8821 | -0.082398 | -0.050354 | 123.0835 | 123.0057 | 122.9416 | 123.0057 | -123.1155 | -122.9736 | 122.7402 | -0.050354 | 52.7206 | 50.5646
440.1719 | 123.0377 | -58.4518 | 64.5447 | -0.045319 | -0.0015145 | 0.064589 | 0.065627 | -0.0013352 | -0.0016535 | -0.0018414 | -0.044067 | 0.00046135 | 0.0038452 | 0.0045458 | 0.0010575 | -0.0013073 | -0.0010425 | -5.722 | 64.5081 | -58.5709 | 64.2883 | -58.3511 | -58.7494 | -58.6853 | -7.9468 | 64.5172 | -58.4656 | -58.5068 | -58.5022 | -58.6304 | -58.2916 | -0.11902 | -0.036621 | -0.25635 | 0.10071 | -0.23346 | -0.29755 | -0.11444 | -0.17853 | -0.013733 | -0.027466 | -123.0515 | -0.050354 | 0.16022 | -0.17853 | 0.17395 | -0.16479 | 0.21973 | 122.8592 | -0.036621 | -0.041199 | 123.0789 | 122.9828 | 122.9599 | 122.9691 | -123.1155 | -123.0103 | 122.7402 | -0.054932 | 52.7298 | 50.5051
441.1719 | 123.0789 | -58.4656 | 64.5035 | -0.068207 | 0.00019446 | 0.06523 | 0.064132 | 0.0016556 | -0.00015811 | 0.00029479 | -0.019653 | 3.4148e-05 | 0.00021363 | 0.0068958 | -0.00022431 | -0.0013073 | -0.00082886 | -5.7083 | 64.476 | -58.5571 | 64.2746 | -58.3328 | -58.7219 | -58.6761 | -7.9926 | 64.5126 | -58.4885 | -58.4793 | -58.4885 | -58.6029 | -58.2733 | -0.091553 | -0.027466 | -0.22888 | 0.13275 | -0.21057 | -0.25635 | -0.11902 | -0.16479 | -0.022888 | 0.009155 | -122.9828 | -0.022888 | 0.19226 | -0.13733 | 0.21515 | -0.11444 | 0.2243 | 122.8317 | 0 | 0.009155 | 123.0331 | 123.0011 | 122.9416 | 122.9782 | -123.0606 | -122.9919 | 122.7402 | -0.013733 | 52.7573 | 50.473
442.1719 | 123.0927 | -58.4564 | 64.5264 | -0.13687 | 0.0010489 | 0.060744 | 0.064345 | 0.0067826 | 0.00091009 | 0.003072 | -0.0013428 | 0.00067495 | -0.0010682 | -0.0050672 | 0.0012711 | -0.0017347 | 0.0021619 | -5.7129 | 64.4897 | -58.5709 | 64.3158 | -58.3145 | -58.6899 | -58.6578 | -8.0475 | 64.5401 | -58.461 | -58.4564 | -58.4702 | -58.5892 | -58.2733 | -0.11444 | -0.036621 | -0.21057 | 0.14191 | -0.20142 | -0.23346 | -0.086975 | -0.11902 | -0.004578 | 0.013733 | -122.9828 | -0.013733 | 0.18311 | -0.13275 | 0.18768 | -0.12817 | 0.25635 | 122.8867 | -0.009155 | 0.004578 | 123.0606 | 123.0011 | 122.9462 | 122.9965 | -123.0972 | -122.9874 | 122.7722 | 0 | 52.7435 | 50.4089
443.1719 | 123.0743 | -58.4381 | 64.4989 | -0.022431 | 0.0016899 | 0.062239 | 0.063277 | 0.0016556 | -0.0010125 | 0.001363 | -0.016602 | 0.0030249 | -0.0010682 | 0.0019824 | 0.00063009 | 0.00061532 | -0.0014697 | -5.7266 | 64.4943 | -58.5663 | 64.325 | -58.3054 | -58.6624 | -58.6349 | -8.1116 | 64.5401 | -58.4473 | -58.461 | -58.4473 | -58.5846 | -58.2596 | -0.12817 | -0.004577 | -0.17395 | 0.13275 | -0.19684 | -0.22431 | -0.068665 | -0.096131 | -0.009156 | 0.041199 | -122.9599 | -0.009156 | 0.17853 | -0.14648 | 0.18768 | -0.13733 | 0.26093 | 122.8912 | 0 | -0.013733 | 123.0606 | 122.9874 | 122.9324 | 122.9782 | -123.0652 | -122.9462 | 122.7631 | -0.022889 | 52.7115 | 50.3265
444.1719 | 122.9965 | -58.5205 | 64.476 | -0.068207 | 0.0014761 | 0.063521 | 0.064773 | 0.0012284 | 0.00048269 | -0.002055 | -0.028809 | 0.0013159 | -0.00042717 | 0.001128 | 0.00063009 | -0.0010937 | 0.0032299 | -5.7953 | 64.4806 | -58.5938 | 64.2426 | -58.4106 | -58.786 | -58.7357 | -8.3313 | 64.5218 | -58.4839 | -58.4976 | -58.5114 | -58.5892 | -58.5114 | -0.073242 | 0.004578 | -0.23346 | 0.10986 | -0.21515 | -0.2655 | -0.14191 | -0.19226 | 0.036621 | 0.045777 | -122.9736 | 0.009155 | 0.009155 | -0.068664 | -0.027466 | -0.10528 | 0.1831 | 122.8363 | -0.027466 | -0.013733 | 123.0743 | 123.0057 | 123.0011 | 123.0423 | -123.0698 | -122.9599 | 122.7631 | 0.022888 | 52.7252 | 50.1892
445.1719 | 123.0194 | -58.4564 | 64.5126 | -0.045319 | -0.00044654 | 0.065871 | 0.065841 | 0.0010148 | -0.00015811 | -0.0016278 | 0.001709 | 0.0017431 | 2.8e-08 | 0.00091422 | -0.00086511 | -2.5678e-05 | -0.00040166 | -5.809 | 64.4623 | -58.5571 | 64.2838 | -58.4061 | -58.7723 | -58.7173 | -8.4183 | 64.5447 | -58.493 | -58.5205 | -58.5159 | -58.6624 | -58.2825 | -0.10071 | -0.050354 | -0.22888 | 0.050354 | -0.26093 | -0.31586 | -0.16022 | -0.21515 | -0.036621 | 0.032044 | -123.0331 | -0.059509 | 0.17395 | -0.20599 | 0.21057 | -0.16937 | 0.15106 | 122.8409 | -0.022888 | -0.027466 | 123.0194 | 123.0377 | 122.9187 | 123.0011 | -123.0698 | -123.0057 | 122.7402 | -0.064087 | 52.6474 | 50.0381
446.1719 | 123.0515 | -58.461 | 64.4989 | -0.075836 | -0.00023294 | 0.064803 | 0.063064 | 0.00080117 | 5.5488e-05 | 0.00029479 | -0.0043946 | 0.0055883 | 0.0036316 | -0.0018628 | 0.00041649 | -0.0015211 | -0.0014697 | -5.8685 | 64.4623 | -58.5938 | 64.2609 | -58.4015 | -58.7631 | -58.6945 | -8.7845 | 64.4485 | -58.5022 | -58.4702 | -58.493 | -58.6441 | -58.2825 | -0.13275 | -0.036621 | -0.23804 | 0.05951 | -0.23346 | -0.30212 | -0.10071 | -0.16937 | -0.041198 | -0.050354 | -122.9691 | -0.032043 | 0.17853 | -0.1831 | 0.21973 | -0.14191 | 0.19226 | 122.8546 | 0.009155 | 0.032043 | 123.056 | 122.9507 | 122.9233 | 122.9095 | -123.0927 | -123.0011 | 122.7219 | -0.009155 | 52.5925 | 49.6765
447.1719 | 123.0698 | -58.4473 | 64.5401 | -0.075836 | -1.9142e-05 | 0.063948 | 0.063277 | 0.00016017 | 0.0013373 | 0.00050839 | -0.01355 | 0.0019567 | 0.0012818 | -0.0018628 | 0.0014847 | -0.0019483 | 0.00045294 | -5.8456 | 64.4943 | -58.6029 | 64.2975 | -58.342 | -58.7219 | -58.6624 | -8.4778 | 64.5447 | -58.4564 | -58.4702 | -58.4702 | -58.6029 | -58.2779 | -0.15564 | -0.045776 | -0.24262 | 0.10529 | -0.21515 | -0.27466 | -0.05951 | -0.11902 | -0.009155 | 0.004578 | -123.0103 | -0.022888 | 0.16937 | -0.15564 | 0.17853 | -0.14648 | 0.26093 | 122.9004 | -0.013733 | -0.013733 | 123.0972 | 123.0011 | 122.9416 | 122.9919 | -123.143 | -122.9965 | 122.7448 | -0.022888 | 52.6016 | 49.9695
448.1719 | 123.1338 | -58.4244 | 64.5309 | -0.060578 | 0.00083526 | 0.066084 | 0.065414 | 0.00058737 | -0.0033625 | 0.00050839 | -0.056274 | 0.00088875 | 0.00042723 | 0.00070062 | -0.0015061 | -0.00023928 | -0.00040166 | -5.8319 | 64.4897 | -58.5388 | 64.3524 | -58.2733 | -58.6578 | -58.6258 | -8.4045 | 64.5218 | -58.4656 | -58.4152 | -58.4061 | -58.5159 | -58.1955 | -0.11444 | -0.041199 | -0.17853 | 0.15106 | -0.20142 | -0.23346 | -0.086975 | -0.11902 | -0.041199 | -0.009155 | -122.9462 | 0.01831 | 0.22888 | -0.091553 | 0.27008 | -0.050354 | 0.2655 | 122.8912 | 0.059509 | 0.050354 | 123.0286 | 122.9874 | 122.9141 | 122.9462 | -123.0698 | -122.9965 | 122.7768 | 0.009155 | 52.5925 | 50.0198
449.1719 | 123.1522 | -58.4015 | 64.4806 | -0.13687 | 0.0010489 | 0.063734 | 0.060714 | 0.0012284 | -0.00037171 | 0.00093559 | 0.02002 | 0.00088875 | -0.00042717 | -0.00015378 | -0.00043791 | -0.00045288 | 0.0049389 | -5.9372 | 64.4623 | -58.5617 | 64.3341 | -58.2962 | -58.6807 | -58.6075 | -8.5968 | 64.4623 | -58.4473 | -58.4015 | -58.3878 | -58.4885 | -58.1635 | -0.16022 | -0.018311 | -0.14648 | 0.10528 | -0.20599 | -0.27924 | -0.045776 | -0.11902 | -0.045777 | -0.018311 | -122.8821 | 0.013733 | 0.23804 | -0.086975 | 0.28381 | -0.041198 | 0.2655 | 122.8958 | 0.05951 | 0.045777 | 123.024 | 122.9095 | 122.8638 | 122.8638 | -123.0423 | -122.9279 | 122.7356 | 0 | 52.4643 | 49.8047
450.1719 | 123.0789 | -58.4244 | 64.5355 | -0.037689 | -0.0019417 | 0.064375 | 0.063918 | 0.0020828 | -0.0018671 | 0.0026446 | -0.0074462 | 0.0013159 | 0.0023498 | -0.00079478 | -0.0036423 | -0.0023755 | 0.00088014 | -6.0287 | 64.4852 | -58.5617 | 64.3524 | -58.3099 | -58.6533 | -58.6029 | -8.6426 | 64.5355 | -58.4518 | -58.4244 | -58.429 | -58.5342 | -58.223 | -0.13733 | -0.050354 | -0.1831 | 0.11444 | -0.17853 | -0.22888 | -0.041198 | -0.091552 | -0.027466 | 0 | -122.9599 | -0.004578 | 0.20142 | -0.10986 | 0.22888 | -0.082398 | 0.25177 | 122.9141 | 0.022888 | 0.027466 | 123.0469 | 122.9874 | 122.9095 | 122.9599 | -123.0972 | -122.9874 | 122.7768 | 0 | 52.3956 | 49.7818
451.1719 | 123.1018 | -58.4198 | 64.5172 | -0.052948 | 0.00019446 | 0.064375 | 0.063918 | -0.0028304 | 0.00069649 | 0.00072199 | -0.06543 | 3.4148e-05 | 0.001068 | 0.0017688 | -0.0025741 | -0.0015211 | -0.0016833 | -5.9189 | 64.5126 | -58.5297 | 64.3387 | -58.2687 | -58.6533 | -58.6075 | -8.6197 | 64.5081 | -58.4702 | -58.4152 | -58.3923 | -58.5388 | -58.223 | -0.10986 | -0.004578 | -0.17853 | 0.15106 | -0.18768 | -0.23346 | -0.07782 | -0.1236 | -0.050354 | -0.009155 | -122.9324 | 0.027466 | 0.19684 | -0.11902 | 0.24719 | -0.068664 | 0.26093 | 122.8683 | 0.07782 | 0.054932 | 123.0423 | 122.9782 | 122.9324 | 122.9279 | -123.0469 | -122.9874 | 122.7585 | 0.004578 | 52.5009 | 49.8001
452.1719 | 123.1155 | -58.4061 | 64.5309 | -0.03006 | -0.0015145 | 0.063734 | 0.063918 | 0.0016556 | 0.00026909 | -0.0018414 | 0.0047608 | -0.0014613 | 0.0025634 | 0.010741 | 0.00041649 | -2.5678e-05 | -0.0031787 | -5.9189 | 64.4806 | -58.5617 | 64.3478 | -58.255 | -58.6533 | -58.6075 | -8.7708 | 64.5538 | -58.4152 | -58.4061 | -58.5205 | -58.5938 | -58.1635 | -0.15564 | -0.050354 | -0.18311 | 0.15106 | -0.20142 | -0.24719 | -0.045776 | -0.091552 | -0.009155 | 0.022888 | -122.937 | -0.11444 | 0.24262 | -0.18768 | 0.25177 | -0.17853 | 0.3067 | 122.9095 | -0.10529 | 0.009155 | 123.0423 | 122.9691 | 122.8867 | 122.9599 | -123.0927 | -122.9462 | 122.7539 | 0 | 52.4872 | 49.6353
453.1719 | 123.0881 | -58.4244 | 64.5309 | -0.12161 | -0.0019417 | 0.065871 | 0.063491 | 0.0012284 | -0.00058531 | -0.00098701 | -0.022705 | 0.0023839 | 0.0021362 | 0.0015552 | -0.00086511 | 0.00061532 | -0.00018806 | -5.9418 | 64.4897 | -58.5617 | 64.3707 | -58.2642 | -58.6487 | -58.6166 | -8.8577 | 64.5035 | -58.429 | -58.4473 | -58.429 | -58.5434 | -58.2367 | -0.13733 | -0.041199 | -0.16022 | 0.16022 | -0.19226 | -0.22431 | -0.054931 | -0.086975 | -0.004578 | -0.027466 | -122.9782 | -0.004578 | 0.18768 | -0.11902 | 0.19226 | -0.11444 | 0.29755 | 122.9324 | 0 | -0.018311 | 123.0515 | 122.9324 | 122.9141 | 122.9279 | -123.0927 | -122.9599 | 122.7951 | -0.022889 | 52.4826 | 49.5666
454.1719 | 123.1247 | -58.4106 | 64.5309 | -0.045319 | 0.0021171 | 0.061598 | 0.06285 | 0.001442 | 0.00048269 | -0.0012006 | 0.010864 | 0.00024775 | 0.0019226 | 0.0028368 | -0.00022431 | -0.0015211 | -0.0027515 | -5.9738 | 64.5218 | -58.548 | 64.3524 | -58.2687 | -58.6395 | -58.6121 | -8.8486 | 64.5355 | -58.429 | -58.429 | -58.4015 | -58.5251 | -58.223 | -0.13733 | -0.009155 | -0.17853 | 0.14191 | -0.20142 | -0.22888 | -0.064087 | -0.091552 | -0.01831 | 0.004577 | -122.9599 | 0.009156 | 0.18768 | -0.11444 | 0.20599 | -0.09613 | 0.27924 | 122.9004 | 0.027466 | 0 | 123.0698 | 122.9645 | 122.9324 | 122.9462 | -123.0789 | -122.9599 | 122.7631 | -0.01831 | 52.4368 | 49.5621
455.1719 | 123.1155 | -58.4106 | 64.5676 | -0.03006 | 0.00083526 | 0.062239 | 0.062423 | -0.00026703 | -0.00079891 | 8.1188e-05 | 0.016968 | -0.00060665 | -0.0014954 | -0.00079478 | -0.0019333 | -0.0015211 | 0.00045294 | -6.0196 | 64.5401 | -58.548 | 64.3662 | -58.2504 | -58.6304 | -58.6029 | -8.9447 | 64.5309 | -58.4244 | -58.4198 | -58.3923 | -58.5159 | -58.2001 | -0.13733 | -0.027466 | -0.20142 | 0.16022 | -0.19226 | -0.21973 | -0.054931 | -0.082397 | -0.013732 | -0.036621 | -122.9874 | 0.018311 | 0.21057 | -0.10528 | 0.2243 | -0.091553 | 0.29755 | 122.9141 | 0.032043 | 0.004577 | 123.0881 | 122.9553 | 122.9507 | 122.9416 | -123.1155 | -122.9919 | 122.7768 | -0.009155 | 52.3911 | 49.4659
456.1719 | 123.1018 | -58.4198 | 64.5676 | -0.037689 | 0.00019446 | 0.062666 | 0.062423 | -0.00048063 | -0.0016535 | 0.0011494 | 0.032227 | 0.00024775 | 0.0014954 | 0.0030506 | 0.00041649 | -0.0017347 | -0.00061526 | -6.0699 | 64.5264 | -58.5617 | 64.3021 | -58.3145 | -58.6624 | -58.6212 | -9.0729 | 64.5859 | -58.4427 | -58.4564 | -58.4198 | -58.5342 | -58.2367 | -0.14191 | -0.041199 | -0.2655 | 0.10529 | -0.20142 | -0.24262 | -0.059509 | -0.10071 | -0.022888 | 0.01831 | -123.024 | 0 | 0.18311 | -0.11444 | 0.20599 | -0.091553 | 0.24719 | 122.8638 | 0.022888 | -0.013733 | 123.0881 | 123.0286 | 122.9462 | 123.0057 | -123.1293 | -123.0103 | 122.7219 | -0.036621 | 52.3499 | 49.3469
457.1719 | 123.1018 | -58.3878 | 64.5309 | 0.023346 | 0.0010489 | 0.064375 | 0.064345 | -0.00026703 | -0.0010125 | -0.002696 | 0.02002 | -0.0016749 | 0.0012818 | 0.0034778 | -0.0012925 | -0.0013073 | -0.00082886 | -6.0928 | 64.5401 | -58.5342 | 64.3341 | -58.2779 | -58.6395 | -58.5983 | -9.1187 | 64.5493 | -58.4518 | -58.4244 | -58.3786 | -58.5114 | -58.2275 | -0.14648 | 0.009155 | -0.19684 | 0.10986 | -0.21057 | -0.25177 | -0.064087 | -0.10528 | -0.064087 | 0.01831 | -122.9553 | 0.009155 | 0.16022 | -0.1236 | 0.2243 | -0.05951 | 0.25635 | 122.8683 | 0.073242 | 0.027466 | 123.0743 | 123.0011 | 122.9279 | 122.937 | -123.0652 | -122.9828 | 122.7219 | -0.036621 | 52.2949 | 49.2691
458.1719 | 123.1567 | -58.4015 | 64.5172 | -0.10635 | -0.00044654 | 0.063734 | 0.062209 | 0.001442 | 0.00026909 | -0.0014142 | 0.016968 | 0.00024775 | 0.001068 | 0.0030506 | -1.0706e-05 | 0.00040152 | 2.554e-05 | -6.0974 | 64.5218 | -58.5434 | 64.3387 | -58.2687 | -58.6212 | -58.6029 | -9.1644 | 64.5493 | -58.4427 | -58.4152 | -58.4015 | -58.5068 | -58.2184 | -0.14191 | 0.004578 | -0.17853 | 0.13275 | -0.20142 | -0.21973 | -0.059509 | -0.07782 | -0.041199 | 0.032043 | -122.9324 | 0 | 0.1831 | -0.10529 | 0.2243 | -0.064087 | 0.27466 | 122.8821 | 0.041199 | 0.027466 | 123.0652 | 122.9919 | 122.9233 | 122.9507 | -123.0606 | -122.9599 | 122.7402 | -0.013733 | 52.3041 | 49.2371
459.1719 | 123.1018 | -58.4106 | 64.5447 | -0.60989 | -0.0010873 | 0.065016 | 0.065841 | 0.0035782 | 5.5488e-05 | 0.00093559 | -0.0013428 | 0.00046135 | 2.8e-08 | -0.0014356 | -0.0023605 | 0.00018792 | -0.00040166 | -6.1295 | 64.5035 | -58.5571 | 64.3662 | -58.2504 | -58.6349 | -58.6258 | -9.256 | 64.5538 | -58.4198 | -58.429 | -58.4244 | -58.5388 | -58.223 | -0.14648 | -0.041199 | -0.17853 | 0.16022 | -0.21515 | -0.2243 | -0.068664 | -0.07782 | -0.009155 | 0.009155 | -122.9736 | -0.013732 | 0.18768 | -0.12817 | 0.19684 | -0.11902 | 0.3067 | 122.9233 | -0.004577 | -0.009155 | 123.0606 | 122.9736 | 122.9141 | 122.9645 | -123.1018 | -122.9645 | 122.7768 | -0.01831 | 52.2812 | 49.1547
460.1719 | 123.1018 | -58.4061 | 64.5493 | -0.060578 | -0.00066014 | 0.06523 | 0.062423 | 0.00058737 | -0.0014399 | -0.0012006 | 0.001709 | 0.0025975 | 0.00021363 | -0.00015378 | 0.0010575 | -0.00066648 | -0.0021107 | -6.1432 | 64.5264 | -58.5251 | 64.3616 | -58.2596 | -58.6441 | -58.5983 | -9.3292 | 64.5721 | -58.4152 | -58.4152 | -58.3832 | -58.5114 | -58.2138 | -0.11902 | -0.022888 | -0.18768 | 0.14648 | -0.19226 | -0.23804 | -0.073243 | -0.11902 | -0.009155 | 0.022889 | -122.9645 | 0.022888 | 0.19226 | -0.10529 | 0.20142 | -0.096131 | 0.2655 | 122.8867 | 0.032043 | 0 | 123.0515 | 122.9874 | 122.9324 | 122.9782 | -123.0743 | -122.9645 | 122.7676 | -0.009155 | 52.2629 | 49.0768
461.1719 | 123.1293 | -58.4381 | 64.4989 | -0.11398 | -0.00066014 | 0.065443 | 0.063277 | -0.00026703 | -0.00015811 | -0.00077341 | 0.029175 | 3.4148e-05 | 0.001068 | 0.00027342 | -0.00022431 | -0.0021619 | -0.0025379 | -6.3126 | 64.4806 | -58.5663 | 64.2883 | -58.3466 | -58.7082 | -58.6624 | -9.5261 | 64.5218 | -58.461 | -58.4198 | -58.429 | -58.5297 | -58.2047 | -0.12817 | -0.01831 | -0.21057 | 0.091552 | -0.22431 | -0.27008 | -0.096131 | -0.14191 | -0.022889 | 0.022889 | -122.9187 | 0.009155 | 0.23346 | -0.091553 | 0.25635 | -0.068664 | 0.21973 | 122.8546 | 0.032044 | 0.041199 | 123.0469 | 122.9828 | 122.9187 | 122.9599 | -123.0652 | -122.9599 | 122.7264 | 0.01831 | 52.1255 | 48.912
462.1719 | 123.1338 | -58.3878 | 64.5355 | 0.023346 | -0.00044654 | 0.065871 | 0.063705 | 0.0012284 | -0.0018671 | -0.00077341 | 0.016968 | 0.0023839 | 0.0036316 | 0.0036914 | -0.00065151 | 0.00040152 | 0.0023755 | -6.2256 | 64.5538 | -58.5434 | 64.3478 | -58.287 | -58.6349 | -58.6075 | -9.4894 | 64.5676 | -58.429 | -58.4015 | -58.3786 | -58.4976 | -58.1909 | -0.15564 | 0.018311 | -0.18768 | 0.10071 | -0.21973 | -0.24719 | -0.064087 | -0.091553 | -0.041199 | 0.032044 | -122.937 | 0.009155 | 0.19684 | -0.10986 | 0.23804 | -0.068665 | 0.25635 | 122.8912 | 0.050354 | 0.027466 | 123.0972 | 122.9965 | 122.9416 | 122.9553 | -123.0789 | -122.9645 | 122.7356 | -0.013733 | 52.1622 | 48.8983
463.1719 | 123.111 | -58.4015 | 64.5538 | -0.060578 | -1.9142e-05 | 0.063734 | 0.063064 | 0.00080117 | 0.0011237 | 0.0011494 | 0.0078126 | 0.0013159 | 0.0019226 | 5.9824e-05 | -0.0017197 | -0.00066648 | 0.00088014 | -6.2622 | 64.5172 | -58.5205 | 64.3295 | -58.2916 | -58.6349 | -58.6121 | -9.5993 | 64.5676 | -58.4335 | -58.429 | -58.3832 | -58.5159 | -58.2047 | -0.11902 | -0.036621 | -0.2243 | 0.10986 | -0.21057 | -0.23346 | -0.091553 | -0.11444 | -0.032044 | 0.013733 | -122.9828 | 0.01831 | 0.19684 | -0.11444 | 0.22888 | -0.082397 | 0.22888 | 122.85 | 0.050354 | 0.004578 | 123.0377 | 123.0011 | 122.9187 | 122.9691 | -123.0743 | -122.9874 | 122.731 | -0.027466 | 52.1393 | 48.8022
464.1719 | 123.0972 | -58.3923 | 64.5676 | -0.075836 | -0.0025827 | 0.064375 | 0.064773 | 0.0016556 | -0.0010125 | 0.00093559 | -0.019653 | 0.0021703 | -0.00042717 | 0.00070062 | -0.0023605 | -0.0015211 | -0.00082886 | -6.2576 | 64.5264 | -58.5342 | 64.357 | -58.2596 | -58.6304 | -58.6075 | -9.6451 | 64.5401 | -58.4335 | -58.4015 | -58.4061 | -58.5022 | -58.2047 | -0.14191 | -0.041199 | -0.21057 | 0.13275 | -0.21515 | -0.23804 | -0.073242 | -0.09613 | -0.041199 | -0.027466 | -122.9691 | -0.013733 | 0.18768 | -0.10986 | 0.22888 | -0.068664 | 0.27466 | 122.8912 | 0.027466 | 0.032044 | 123.0606 | 122.9736 | 122.9187 | 122.9324 | -123.1018 | -123.0011 | 122.7493 | -0.009155 | 52.1347 | 48.7473
465.1719 | 123.1155 | -58.374 | 64.5355 | -0.060578 | -0.00087374 | 0.063094 | 0.063918 | -0.0013352 | -0.0033625 | 0.002431 | 0.0078126 | 0.00046135 | 0.0014954 | -0.0020764 | -0.0015061 | -0.0017347 | -0.0055287 | -6.2622 | 64.5081 | -58.5251 | 64.3524 | -58.2596 | -58.6212 | -58.6166 | -9.6909 | 64.5493 | -58.4198 | -58.3969 | -58.3786 | -58.5022 | -58.1955 | -0.15106 | -0.027465 | -0.1831 | 0.11444 | -0.24262 | -0.24719 | -0.091553 | -0.096131 | -0.045777 | 0.013733 | -122.9324 | -0.004578 | 0.17853 | -0.12817 | 0.2243 | -0.082397 | 0.2655 | 122.8775 | 0.041199 | 0.022888 | 123.0331 | 122.9691 | 122.8821 | 122.9233 | -123.0606 | -122.9553 | 122.7264 | -0.022889 | 52.1118 | 48.6832
466.1719 | 123.1567 | -58.3923 | 64.4897 | -0.060578 | 0.00040806 | 0.065443 | 0.064559 | -0.0011214 | 0.00069649 | 0.0011494 | 0.02002 | -0.0014613 | 0.00021363 | -0.0025036 | -0.00043791 | -0.00066648 | -0.00061526 | -6.3629 | 64.4623 | -58.5342 | 64.3662 | -58.2596 | -58.6258 | -58.5938 | -9.8419 | 64.4669 | -58.4564 | -58.3649 | -58.3694 | -58.461 | -58.1451 | -0.14191 | -0.027466 | -0.1236 | 0.13275 | -0.20142 | -0.23346 | -0.059509 | -0.091552 | -0.064087 | -0.022888 | -122.8546 | 0.022888 | 0.24719 | -0.068665 | 0.31128 | -0.004578 | 0.27466 | 122.9004 | 0.086975 | 0.091553 | 122.9965 | 122.9233 | 122.8546 | 122.8592 | -123.024 | -122.9462 | 122.7585 | 0.027466 | 52.0294 | 48.5504
467.1719 | 123.0927 | -58.4106 | 64.5401 | -0.068207 | 0.0010489 | 0.062453 | 0.064986 | -0.0017624 | -0.00079891 | 8.1188e-05 | -0.025757 | 0.00088875 | 0.00042723 | 0.00027342 | 0.0014847 | 0.00018792 | 0.00066654 | -6.3034 | 64.5309 | -58.548 | 64.3662 | -58.255 | -58.6304 | -58.6075 | -9.8923 | 64.5447 | -58.429 | -58.4747 | -58.5114 | -58.5342 | -58.1223 | -0.13733 | -0.009155 | -0.17395 | 0.15564 | -0.19684 | -0.21973 | -0.059509 | -0.082397 | -0.01831 | 0.004578 | -123.0148 | -0.10071 | 0.28839 | -0.1236 | 0.3067 | -0.10529 | 0.29297 | 122.9141 | -0.082398 | -0.045776 | 123.0789 | 122.9736 | 122.9416 | 122.9553 | -123.0881 | -122.9691 | 122.7768 | -0.064086 | 52.1072 | 48.5184
468.1719 | 123.1155 | -58.3923 | 64.5584 | 0.00045798 | -0.00044654 | 0.064162 | 0.063064 | -0.00026703 | -0.0012261 | -0.00077341 | 0.013916 | 0.0013159 | -0.00021357 | -0.001222 | -0.0027877 | -0.00045288 | 0.00066654 | -6.308 | 64.5401 | -58.5297 | 64.3616 | -58.255 | -58.6212 | -58.5938 | -9.9243 | 64.5538 | -58.4061 | -58.4106 | -58.4015 | -58.5022 | -58.1772 | -0.13733 | -0.018311 | -0.19684 | 0.13733 | -0.20142 | -0.22888 | -0.064087 | -0.091553 | -0.013733 | -0.004578 | -122.9691 | -0.009155 | 0.21515 | -0.10986 | 0.22888 | -0.09613 | 0.27466 | 122.8912 | 0.004578 | -0.004578 | 123.0698 | 122.9599 | 122.9324 | 122.9462 | -123.0881 | -122.9645 | 122.7539 | -0.018311 | 52.0844 | 48.468
469.1719 | 123.0743 | -58.3969 | 64.5493 | -0.083466 | -0.00023294 | 0.063521 | 0.063705 | -0.00090783 | -0.0010125 | -0.002055 | 0.026123 | 0.00088875 | 0.00021363 | 0.0019824 | -0.0023605 | 0.00082892 | 0.00088014 | -6.3858 | 64.563 | -58.5205 | 64.3295 | -58.2962 | -58.6487 | -58.6121 | -10.0571 | 64.5676 | -58.4106 | -58.4061 | -58.3694 | -58.5068 | -58.2138 | -0.1236 | 0.013733 | -0.21973 | 0.10071 | -0.21515 | -0.25177 | -0.091553 | -0.12817 | -0.013733 | 0.018311 | -122.9553 | 0.027466 | 0.18311 | -0.10986 | 0.19684 | -0.09613 | 0.2243 | 122.85 | 0.041199 | 0.004578 | 123.0835 | 122.9782 | 122.9599 | 122.9645 | -123.0698 | -122.9599 | 122.7264 | -0.009155 | 52.0111 | 48.3398
470.1719 | 123.0835 | -58.374 | 64.5813 | -0.0071715 | 0.00062166 | 0.063948 | 0.062209 | 0.0018692 | 0.0013373 | 8.1188e-05 | 0.041382 | 0.00046135 | 0.00085443 | -0.00079478 | -0.0019333 | -0.0021619 | 0.00066654 | -6.427 | 64.5355 | -58.5251 | 64.3295 | -58.3008 | -58.6533 | -58.6166 | -10.1624 | 64.563 | -58.4198 | -58.4518 | -58.3969 | -58.5068 | -58.2138 | -0.15106 | -0.045777 | -0.25177 | 0.073242 | -0.24262 | -0.27924 | -0.091553 | -0.12817 | -0.045777 | -0.018311 | -123.0331 | -0.022889 | 0.16022 | -0.13275 | 0.20599 | -0.086975 | 0.2243 | 122.8546 | 0.022888 | -0.032043 | 123.0606 | 122.9828 | 122.9095 | 122.937 | -123.1064 | -123.0011 | 122.7036 | -0.07782 | 51.947 | 48.2117
471.1719 | 123.2162 | -58.3878 | 64.5218 | -0.068207 | 0.0014761 | 0.066084 | 0.063277 | 0.0052872 | -0.0016535 | -0.0012006 | 0.0078126 | 0.0011023 | -0.0021362 | -0.003999 | -0.00022431 | -0.0010937 | 0.0015209 | -6.514 | 64.4897 | -58.5388 | 64.3845 | -58.2687 | -58.6533 | -58.5892 | -10.2814 | 64.476 | -58.4473 | -58.3694 | -58.3649 | -58.4747 | -58.1497 | -0.15106 | -0.032044 | -0.13733 | 0.11902 | -0.20142 | -0.2655 | -0.050354 | -0.11444 | -0.05951 | -0.045777 | -122.8912 | 0.022888 | 0.23804 | -0.086975 | 0.29755 | -0.027465 | 0.27008 | 122.9233 | 0.082398 | 0.07782 | 123.0286 | 122.9233 | 122.8775 | 122.8638 | -123.0606 | -122.9691 | 122.7722 | 0.01831 | 51.8738 | 48.1064
472.1719 | 123.1064 | -58.3786 | 64.563 | -0.052948 | -1.9142e-05 | 0.062453 | 0.062209 | 0.0022964 | 0.0028327 | 0.002431 | -0.010498 | 0.0013159 | 0.00021363 | -0.0033582 | -0.0025741 | -0.0019483 | -0.00082886 | -6.5048 | 64.5309 | -58.5388 | 64.357 | -58.2916 | -58.6212 | -58.6075 | -10.3546 | 64.5493 | -58.4244 | -58.4015 | -58.3832 | -58.5022 | -58.2047 | -0.16022 | -0.032043 | -0.20599 | 0.086975 | -0.22888 | -0.24261 | -0.068665 | -0.082398 | -0.045776 | -0.013733 | -122.9645 | -0.004578 | 0.17395 | -0.1236 | 0.21973 | -0.07782 | 0.24719 | 122.8958 | 0.041198 | 0.022888 | 123.0698 | 122.9736 | 122.9095 | 122.9279 | -123.1018 | -122.9874 | 122.7356 | -0.022888 | 51.8738 | 48.024
473.1719 | 123.1018 | -58.3923 | 64.5584 | -0.068207 | -0.0010873 | 0.065657 | 0.063491 | 0.00251 | -0.0020807 | 8.1188e-05 | -0.0074462 | -0.00039305 | 0.00042723 | -0.00015378 | 0.00041649 | 0.0021105 | -0.0021107 | -6.5094 | 64.5493 | -58.5251 | 64.3753 | -58.2458 | -58.6166 | -58.5892 | -10.4233 | 64.5447 | -58.3969 | -58.4061 | -58.3786 | -58.5114 | -58.1772 | -0.13275 | -0.009156 | -0.18311 | 0.14648 | -0.19684 | -0.2243 | -0.064087 | -0.091553 | -0.004578 | -0.013733 | -122.9645 | 0.013733 | 0.21515 | -0.11902 | 0.21973 | -0.11444 | 0.27923 | 122.9004 | 0.018311 | -0.009155 | 123.0743 | 122.9416 | 122.9416 | 122.937 | -123.0835 | -122.9553 | 122.7676 | -0.013733 | 51.8829 | 47.9691
474.1719 | 123.1201 | -58.4106 | 64.5859 | -0.052948 | -0.00066014 | 0.063948 | 0.063491 | -0.0015488 | -0.00058531 | -0.00013241 | 0.010864 | 0.00088875 | 0.002777 | 0.0015552 | -0.00086511 | -0.0036573 | -0.00040166 | -6.5689 | 64.5401 | -58.5159 | 64.3295 | -58.3008 | -58.6349 | -58.6121 | -10.5423 | 64.5905 | -58.4335 | -58.4152 | -58.374 | -58.5251 | -58.2047 | -0.10528 | -0.045776 | -0.25635 | 0.10986 | -0.20142 | -0.2243 | -0.096131 | -0.11902 | -0.022888 | 0.004578 | -123.0011 | 0.036622 | 0.20599 | -0.11444 | 0.22888 | -0.091552 | 0.21515 | 122.8455 | 0.05951 | 0.018311 | 123.056 | 123.024 | 122.9507 | 123.0011 | -123.1018 | -123.0194 | 122.7402 | -0.004577 | 51.8417 | 47.8683
475.1719 | 123.0927 | -58.4106 | 64.5676 | -0.083466 | 0.00083526 | 0.065016 | 0.06285 | -0.00026703 | -0.0042169 | -0.0012006 | 0.016968 | 0.0013159 | 0.0025634 | -0.00015378 | -0.0021469 | 0.00082892 | 0.0013073 | -6.5964 | 64.5493 | -58.5571 | 64.3387 | -58.3008 | -58.6349 | -58.6166 | -10.6293 | 64.5813 | -58.4335 | -58.4335 | -58.3878 | -58.5068 | -58.2184 | -0.14648 | -0.018311 | -0.22888 | 0.10986 | -0.20599 | -0.2243 | -0.059509 | -0.07782 | -0.022888 | 0.013733 | -123.0011 | 0.022889 | 0.19226 | -0.09613 | 0.21515 | -0.073242 | 0.25635 | 122.8958 | 0.045777 | 0 | 123.1064 | 123.0148 | 122.9599 | 122.9919 | -123.1247 | -123.0011 | 122.7493 | -0.022888 | 51.8143 | 47.7814
476.1719 | 123.0927 | -58.3969 | 64.5813 | -0.022431 | 0.0012625 | 0.063521 | 0.061782 | 0.0012284 | 5.5488e-05 | -0.00077341 | -0.0013428 | 0.0013159 | 0.0029906 | -0.00229 | -0.0032151 | -0.00045288 | -0.0010425 | -6.6193 | 64.5721 | -58.5297 | 64.3707 | -58.2642 | -58.6029 | -58.58 | -10.6979 | 64.5584 | -58.3969 | -58.3969 | -58.3649 | -58.4885 | -58.2001 | -0.13275 | -0.009155 | -0.21057 | 0.13275 | -0.1831 | -0.20599 | -0.050354 | -0.073242 | 0 | -0.022888 | -122.9782 | 0.032044 | 0.19684 | -0.091552 | 0.19684 | -0.091552 | 0.2655 | 122.9004 | 0.032044 | 0 | 123.1018 | 122.9553 | 122.9691 | 122.9553 | -123.111 | -122.9782 | 122.7676 | 0 | 51.7776 | 47.699
477.1719 | 123.0789 | -58.3923 | 64.5767 | -0.052948 | -0.00066014 | 0.065443 | 0.064345 | 0.00080117 | 0.0013373 | 0.00072199 | 0.047485 | -0.00017945 | 0.00085443 | 0.001128 | -0.0012925 | -0.0013073 | 0.0032299 | -6.7749 | 64.5584 | -58.5297 | 64.3204 | -58.3008 | -58.6487 | -58.6166 | -10.8215 | 64.5767 | -58.4061 | -58.429 | -58.4106 | -58.5068 | -58.2184 | -0.13733 | -0.01831 | -0.25635 | 0.091553 | -0.2243 | -0.25635 | -0.086975 | -0.11902 | -0.013733 | 0 | -123.0057 | -0.018311 | 0.17395 | -0.11444 | 0.18768 | -0.10071 | 0.22888 | 122.85 | -0.004578 | -0.022888 | 123.0881 | 122.9828 | 122.9507 | 122.9691 | -123.1064 | -122.9828 | 122.7127 | -0.036621 | 51.6174 | 47.5708
478.1719 | 123.0972 | -58.3786 | 64.5859 | -0.052948 | -1.9142e-05 | 0.063948 | 0.064132 | 0.0029374 | -0.0010125 | -0.00034601 | 0.0078126 | -0.00039305 | -0.00085457 | 0.0015552 | -0.0032151 | -0.0010937 | 2.554e-05 | -6.7062 | 64.5447 | -58.5205 | 64.3524 | -58.2779 | -58.6212 | -58.58 | -10.8673 | 64.595 | -58.4061 | -58.3923 | -58.3832 | -58.5068 | -58.1772 | -0.14191 | -0.041198 | -0.23346 | 0.10071 | -0.20142 | -0.24261 | -0.059509 | -0.10071 | -0.027466 | 0.009156 | -122.9782 | -0.004578 | 0.20142 | -0.12817 | 0.22888 | -0.10071 | 0.24262 | 122.8729 | 0.022888 | 0.013733 | 123.0652 | 123.0011 | 122.9233 | 122.9736 | -123.1064 | -122.9919 | 122.731 | -0.013733 | 51.6724 | 47.5113
479.1719 | 123.0835 | -58.3511 | 64.5676 | -0.068207 | -0.00023294 | 0.063094 | 0.064986 | -0.0021896 | -0.00037171 | 8.1188e-05 | 0.02002 | -0.0025293 | 0.00021363 | -0.00015378 | -0.0021469 | -0.00088008 | -0.0023243 | -6.72 | 64.5493 | -58.5159 | 64.3616 | -58.3054 | -58.6395 | -58.6075 | -10.936 | 64.5905 | -58.4244 | -58.4015 | -58.3649 | -58.4885 | -58.1955 | -0.16479 | -0.018311 | -0.20599 | 0.045776 | -0.25635 | -0.28839 | -0.091553 | -0.1236 | -0.073242 | 0.022888 | -122.9691 | -0.013733 | 0.15564 | -0.13733 | 0.22888 | -0.064087 | 0.21057 | 122.8775 | 0.059509 | 0.022888 | 123.0652 | 123.0148 | 122.9004 | 122.9416 | -123.0835 | -122.9919 | 122.7127 | -0.050354 | 51.6312 | 47.4152
480.1719 | 123.1155 | -58.374 | 64.5676 | 0.046234 | 0.0012625 | 0.064162 | 0.063918 | 0.00080117 | -0.00079891 | -0.00077341 | -0.0013428 | 0.00067495 | 0.0029906 | -0.00058098 | -0.0015061 | -2.5678e-05 | -0.00018806 | -6.7474 | 64.5493 | -58.5297 | 64.3662 | -58.2687 | -58.6029 | -58.58 | -10.9543 | 64.5859 | -58.3878 | -58.3923 | -58.342 | -58.4976 | -58.2001 | -0.15564 | -0.018311 | -0.20142 | 0.10529 | -0.20599 | -0.22888 | -0.050354 | -0.073242 | -0.013733 | 0.01831 | -122.9599 | 0.032043 | 0.17395 | -0.1236 | 0.18768 | -0.10986 | 0.26093 | 122.8958 | 0.045776 | -0.004578 | 123.0789 | 122.9736 | 122.9233 | 122.9599 | -123.0972 | -122.9553 | 122.7402 | -0.018311 | 51.6266 | 47.4197
481.1719 | 123.1064 | -58.374 | 64.5767 | -0.014801 | 0.00040806 | 0.066084 | 0.064345 | -0.00048063 | -0.00058531 | 0.002431 | 0.035278 | 0.0017431 | -0.0012818 | -0.003999 | -0.00086511 | -0.0030163 | 2.554e-05 | -6.7886 | 64.563 | -58.5251 | 64.3478 | -58.2596 | -58.6075 | -58.5846 | -11.0641 | 64.5676 | -58.4244 | -58.374 | -58.3786 | -58.4793 | -58.1589 | -0.15106 | -0.013733 | -0.22888 | 0.11444 | -0.21057 | -0.23346 | -0.05951 | -0.082398 | -0.050354 | -0.009155 | -122.9507 | -0.004578 | 0.21515 | -0.10529 | 0.2655 | -0.054932 | 0.2655 | 122.8729 | 0.045776 | 0.050354 | 123.0881 | 122.9919 | 122.937 | 122.9416 | -123.1018 | -123.0011 | 122.7219 | 0 | 51.5854 | 47.3099
482.1719 | 123.056 | -58.3694 | 64.5996 | 0.00045798 | -0.00087374 | 0.065016 | 0.062423 | -0.00026703 | -0.0014399 | -0.0022686 | 0.035278 | 0.0028113 | 0.0021362 | 0.00027342 | -1.0706e-05 | -0.0034437 | -0.00082886 | -7.7545 | 64.6088 | -58.461 | 64.357 | -58.3328 | -58.6212 | -58.5663 | -11.1511 | 64.6179 | -58.3878 | -58.4244 | -58.3786 | -58.5159 | -58.1955 | -0.091553 | 0.009156 | -0.24261 | 0.036621 | -0.19684 | -0.25177 | -0.10529 | -0.16022 | -0.01831 | 0.018311 | -123.024 | -0.009155 | 0.17395 | -0.14648 | 0.19226 | -0.12817 | 0.12817 | 122.818 | 0.009155 | -0.036621 | 123.0698 | 123.0057 | 122.9782 | 122.9874 | -123.0606 | -122.9874 | 122.7264 | -0.054931 | 50.6149 | 47.2183
483.1719 | 123.0652 | -58.3832 | 64.5996 | -0.060578 | 0.00040806 | 0.063948 | 0.064345 | -0.0043258 | 5.5488e-05 | -0.00077341 | 0.059692 | 0.00088875 | 0.002777 | -0.00229 | -0.00043791 | -0.0015211 | -0.0018971 | -7.8278 | 64.5859 | -58.493 | 64.4852 | -58.0719 | -58.7585 | -58.7173 | -11.2473 | 64.595 | -58.4061 | -58.4015 | -58.3694 | -58.4747 | -58.1955 | -0.10986 | -0.013733 | -0.11444 | 0.31128 | -0.33417 | -0.37537 | -0.2243 | -0.2655 | -0.022888 | -0.004577 | -123.0011 | 0.013733 | 0.18768 | -0.091552 | 0.21057 | -0.068664 | 0.42114 | 122.9782 | 0.036621 | 0.004578 | 123.0789 | 123.0011 | 122.9691 | 122.9782 | -123.0927 | -123.0057 | 122.8683 | -0.01831 | 50.5554 | 47.1359
484.1719 | 123.0835 | -58.3878 | 64.595 | -0.022431 | -0.0019417 | 0.062453 | 0.064559 | -0.004753 | -0.0018671 | -0.0022686 | 0.032227 | -0.00039305 | -0.0012818 | -0.0037854 | -0.0023605 | -0.00045288 | 0.0047253 | -7.8735 | 64.5905 | -58.4885 | 64.357 | -58.2596 | -58.6075 | -58.5754 | -11.1969 | 64.6317 | -58.3649 | -58.4244 | -58.4106 | -58.4564 | -58.1955 | -0.10071 | -0.004578 | -0.23804 | 0.12817 | -0.18768 | -0.21973 | -0.086975 | -0.11902 | 0.022888 | 0.036621 | -123.0194 | -0.022889 | 0.19226 | -0.068665 | 0.16937 | -0.091553 | 0.22888 | 122.8455 | -0.045777 | -0.059509 | 123.0789 | 122.9965 | 122.9782 | 123.0194 | -123.0835 | -122.9599 | 122.7448 | -0.036621 | 50.5142 | 47.1909
485.1719 | 123.0423 | -58.3511 | 64.6133 | -0.052948 | -0.00066014 | 0.062453 | 0.063705 | 0.001442 | 0.00048269 | 0.00029479 | 0.023071 | 0.00067495 | 2.8e-08 | 0.00027342 | -0.0025741 | -0.0013073 | -0.0025379 | -7.9193 | 64.5905 | -58.5114 | 64.357 | -58.2504 | -58.6121 | -58.5892 | -11.3754 | 64.6225 | -58.3832 | -58.4061 | -58.1589 | -58.5938 | -58.2962 | -0.16022 | -0.022888 | -0.25635 | 0.10071 | -0.23804 | -0.26093 | -0.077819 | -0.10071 | -0.032044 | 0.009156 | -123.0194 | 0.19226 | 0.054931 | -0.24262 | 0.086975 | -0.21057 | 0.26093 | 122.8683 | 0.2243 | -0.022888 | 123.1018 | 123.0057 | 122.9416 | 122.9736 | -123.1247 | -122.9965 | 122.7081 | -0.054932 | 50.4318 | 46.9757
486.1719 | 123.0606 | -58.3374 | 64.6362 | -0.15213 | -0.00087374 | 0.06288 | 0.063705 | 0.00080117 | 0.0011237 | 8.1188e-05 | 0.001709 | 0.0023839 | 0.0014954 | 0.0028368 | -0.0017197 | -0.00023928 | 0.0021619 | -7.9559 | 64.5767 | -58.5022 | 64.3753 | -58.255 | -58.6166 | -58.5846 | -11.4807 | 64.595 | -58.3832 | -58.4106 | -58.3786 | -58.4885 | -58.1955 | -0.1648 | -0.059509 | -0.26093 | 0.082397 | -0.24719 | -0.27924 | -0.082398 | -0.11444 | -0.045777 | -0.041198 | -123.0469 | -0.041199 | 0.14191 | -0.15106 | 0.18768 | -0.10529 | 0.24719 | 122.8775 | 0.004578 | -0.027466 | 123.0789 | 122.9782 | 122.9141 | 122.9324 | -123.1384 | -123.0194 | 122.7127 | -0.073243 | 50.3815 | 46.8567
487.1719 | 123.0835 | -58.3603 | 64.595 | -0.014801 | -0.0013009 | 0.06288 | 0.064132 | 0.0010148 | 0.00069649 | 0.0017902 | 0.035278 | 0.00088875 | 0.002777 | -0.00058098 | -0.0012925 | -0.0019483 | 2.554e-05 | -8.0338 | 64.595 | -58.5114 | 64.357 | -58.2458 | -58.6441 | -58.5983 | -11.5402 | 64.5905 | -58.3923 | -58.4106 | -58.3923 | -58.4747 | -58.2047 | -0.15106 | 0 | -0.23804 | 0.11444 | -0.23804 | -0.28381 | -0.086975 | -0.13275 | -0.032043 | -0.004578 | -123.0057 | -0.032043 | 0.15564 | -0.11444 | 0.18768 | -0.082397 | 0.2655 | 122.8683 | 0 | -0.018311 | 123.1064 | 122.9828 | 122.9553 | 122.9507 | -123.1064 | -122.9874 | 122.7173 | -0.050354 | 50.3265 | 46.8201
488.1719 | 123.0652 | -58.3694 | 64.6179 | -0.052948 | -0.00044654 | 0.063094 | 0.062636 | -0.0011214 | -0.00079891 | -0.0018414 | -0.034912 | 0.0011023 | 0.00042723 | 0.003905 | -0.0025741 | 0.00018792 | 0.00066654 | -8.1161 | 64.5996 | -58.5022 | 64.3707 | -58.2596 | -58.3145 | -58.5663 | -11.586 | 64.5813 | -58.4015 | -58.4106 | -58.3694 | -58.4885 | -58.1863 | -0.13275 | -0.018311 | -0.24719 | 0.10986 | -0.19684 | 0.054932 | -0.064087 | 0.18768 | -0.032043 | -0.036621 | -123.0286 | 0 | 0.18311 | -0.11902 | 0.21515 | -0.086975 | 0.24261 | 122.8729 | 0.032043 | -0.009156 | 123.1018 | 122.9828 | 122.9691 | 122.9507 | -123.1201 | -123.0194 | 122.7402 | -0.041199 | 50.2533 | 46.7834
489.1719 | 123.0423 | -58.3832 | 64.5905 | -0.014801 | -0.00023294 | 0.064589 | 0.063064 | 0.0029374 | 0.00091009 | 8.1188e-05 | 0.035278 | 0.0015295 | -0.00042717 | -0.002931 | -1.0706e-05 | -0.0034437 | 0.0051525 | -8.1894 | 64.6042 | -58.493 | 64.3753 | -58.255 | -58.6075 | -58.5663 | -11.6959 | 64.6317 | -58.3603 | -58.3969 | -58.4152 | -58.493 | -58.1863 | -0.10986 | 0.013733 | -0.21515 | 0.12817 | -0.18311 | -0.2243 | -0.073242 | -0.11444 | 0.022888 | 0.041199 | -122.9874 | -0.032043 | 0.19684 | -0.10986 | 0.17395 | -0.13275 | 0.23804 | 122.8683 | -0.054931 | -0.036621 | 123.0972 | 122.9919 | 122.9874 | 123.0148 | -123.0835 | -122.9507 | 122.7585 | -0.013733 | 50.1938 | 46.6873
490.1719 | 123.0057 | -58.3603 | 64.6179 | -0.060578 | 0.00040806 | 0.061812 | 0.061782 | -5.343e-05 | 5.5488e-05 | 0.0015766 | 0.035278 | 0.0019567 | 0.002777 | 0.0077502 | 0.00063009 | -0.0021619 | -0.0053149 | -8.2397 | 64.5721 | -58.5068 | 64.3707 | -58.2367 | -58.6029 | -58.5526 | -11.7188 | 64.6179 | -58.3832 | -58.4885 | -58.1589 | -58.4015 | -58.2138 | -0.14648 | -0.045776 | -0.24719 | 0.1236 | -0.19226 | -0.24261 | -0.045776 | -0.09613 | -0.022888 | 0 | -123.1064 | 0.20142 | 0.14648 | -0.041198 | 0.16937 | -0.01831 | 0.27008 | 122.8775 | 0.2243 | -0.10529 | 123.0789 | 123.0011 | 122.9324 | 122.9782 | -123.1247 | -123.0011 | 122.731 | -0.12817 | 50.1205 | 46.6415
491.1719 | 123.0377 | -58.3786 | 64.6133 | -0.060578 | -0.00066014 | 0.06288 | 0.064345 | -0.00069423 | -0.0010125 | -0.00034601 | 0.023071 | 0.00067495 | 0.00021363 | -0.0018628 | 0.00063009 | -0.0019483 | 0.00045294 | -8.2901 | 64.5676 | -58.4793 | 64.3707 | -58.2275 | -58.5938 | -58.5663 | -11.7966 | 64.6317 | -58.3878 | -58.3969 | -58.3649 | -58.4793 | -58.2184 | -0.10071 | -0.045776 | -0.24261 | 0.15106 | -0.18768 | -0.21515 | -0.086975 | -0.11444 | -0.009155 | 0.018311 | -123.0103 | 0.013733 | 0.16022 | -0.10071 | 0.16937 | -0.091553 | 0.25177 | 122.85 | 0.022888 | -0.009156 | 123.0469 | 123.0194 | 122.9462 | 123.0103 | -123.0927 | -123.0011 | 122.7493 | -0.018311 | 50.0885 | 46.582
492.1719 | 123.056 | -58.3603 | 64.6362 | 0.00045798 | 0.0012625 | 0.06523 | 0.06285 | -0.0011214 | -0.0018671 | -0.0014142 | 0.026123 | 0.0013159 | 0.0025634 | -0.0010084 | -0.0017197 | -0.00045288 | 0.0038709 | -8.3405 | 64.5721 | -58.4793 | 64.4073 | -58.2184 | -58.5983 | -58.548 | -11.8561 | 64.5905 | -58.3649 | -58.4061 | -58.3557 | -58.4702 | -58.1955 | -0.11902 | -0.064086 | -0.22888 | 0.14191 | -0.18768 | -0.23804 | -0.068665 | -0.11902 | -0.004577 | -0.045776 | -123.0423 | 0.004578 | 0.16479 | -0.10986 | 0.16937 | -0.10529 | 0.26093 | 122.8867 | 0.009155 | -0.041199 | 123.0515 | 122.9553 | 122.9324 | 122.9507 | -123.1155 | -123.0011 | 122.7676 | -0.045776 | 50.0198 | 46.5042
493.1719 | 123.0698 | -58.3282 | 64.6362 | 0.023346 | 0.0014761 | 0.064162 | 0.06285 | 0.0020828 | -0.0031489 | -0.002055 | 0.044434 | 0.00088875 | -0.00064077 | 5.9824e-05 | -0.00043791 | -0.0019483 | -0.0025379 | -8.4412 | 64.6179 | -58.4747 | 64.3707 | -58.255 | -58.5892 | -58.4473 | -12.1353 | 64.6271 | -58.4106 | -58.3969 | -58.3603 | -58.5068 | -58.1955 | -0.14648 | -0.01831 | -0.2655 | 0.073242 | -0.11902 | -0.26093 | 0.027465 | -0.11444 | -0.082398 | -0.009155 | -123.0331 | -0.032044 | 0.13275 | -0.17853 | 0.21515 | -0.09613 | 0.21973 | 122.8455 | 0.050354 | 0.013733 | 123.0927 | 123.0377 | 122.9462 | 122.9553 | -123.111 | -123.0469 | 122.699 | -0.068665 | 49.8871 | 46.1929
494.1719 | 123.1201 | -58.374 | 64.6133 | -0.045319 | -0.00044654 | 0.063948 | 0.063918 | 0.0035782 | -0.0010125 | 8.1188e-05 | -0.01355 | 0.00088875 | 0.0023498 | 0.00027342 | -0.0017197 | -0.0030163 | -0.0025379 | -8.4732 | 64.5859 | -58.493 | 64.3845 | -58.2642 | -58.6029 | -58.5571 | -12.0346 | 64.6179 | -58.3603 | -58.3832 | -58.3557 | -58.4656 | -58.168 | -0.11902 | -0.027466 | -0.22888 | 0.10986 | -0.18311 | -0.22888 | -0.064087 | -0.10986 | 0.013732 | 0.004578 | -122.9965 | 0.01831 | 0.20599 | -0.091553 | 0.19226 | -0.10529 | 0.22888 | 122.8775 | 0.004578 | -0.022888 | 123.0789 | 122.9782 | 122.9599 | 122.9919 | -123.1064 | -122.9736 | 122.7585 | -0.009156 | 49.9008 | 46.3394
495.1719 | 123.1384 | -58.3008 | 64.6591 | -0.083466 | -0.0010873 | 0.06288 | 0.063064 | 0.003151 | -0.00037171 | -0.0014142 | 0.016968 | 0.0013159 | -0.00085457 | -0.0037854 | 0.00020289 | -0.0034437 | -0.0040333 | -8.5464 | 64.5996 | -58.493 | 64.3707 | -58.2458 | -58.5938 | -58.5617 | -12.0987 | 64.6362 | -58.3649 | -58.3923 | -58.3557 | -58.4473 | -58.1039 | -0.19226 | -0.05951 | -0.28839 | 0.054931 | -0.26093 | -0.29297 | -0.068665 | -0.10071 | -0.064087 | -0.022889 | -123.0515 | -0.054932 | 0.19684 | -0.14648 | 0.26093 | -0.082398 | 0.24719 | 122.8638 | 0.009155 | -0.027466 | 123.0927 | 123.0011 | 122.9004 | 122.937 | -123.1522 | -123.024 | 122.6715 | -0.091553 | 49.7543 | 46.2021
496.1719 | 123.0972 | -58.3328 | 64.6317 | -0.037689 | 0.0012625 | 0.064803 | 0.064559 | -0.0017624 | 0.0011237 | -0.00055961 | -0.01355 | -0.00017945 | -0.0029908 | -0.0018628 | -0.0015061 | -0.0015211 | -0.0010425 | -8.7524 | 64.5905 | -58.4976 | 64.3799 | -58.2458 | -58.6121 | -58.5617 | -12.1902 | 64.5905 | -58.3786 | -58.4061 | -58.3466 | -58.4518 | -58.1772 | -0.16479 | -0.041199 | -0.25177 | 0.086975 | -0.22888 | -0.27924 | -0.064087 | -0.11444 | -0.045776 | -0.041199 | -123.0377 | -0.013733 | 0.15564 | -0.11902 | 0.20142 | -0.073242 | 0.25177 | 122.8775 | 0.032043 | -0.027466 | 123.0881 | 122.9691 | 122.9233 | 122.9233 | -123.1293 | -123.0103 | 122.7127 | -0.073242 | 49.5804 | 46.1426
497.1719 | 123.0652 | -58.3466 | 64.6271 | -0.014801 | 0.0023307 | 0.063734 | 0.061782 | -0.004753 | -0.0027215 | 0.00072199 | 0.035278 | -0.00060665 | 0.002777 | -0.0018628 | 0.00063009 | -0.0028027 | -0.0010425 | -8.6838 | 64.5996 | -58.4793 | 64.4028 | -58.2092 | -58.5617 | -58.5342 | -12.2269 | 64.6179 | -58.3649 | -58.3878 | -58.3511 | -58.4656 | -58.1863 | -0.13275 | -0.027466 | -0.2243 | 0.13733 | -0.18768 | -0.21515 | -0.054932 | -0.082398 | -0.01831 | -0.009155 | -123.0148 | -0.004577 | 0.16022 | -0.11902 | 0.17853 | -0.10071 | 0.27008 | 122.8821 | 0.013733 | -0.022888 | 123.0789 | 122.9828 | 122.9462 | 122.9645 | -123.1064 | -122.9919 | 122.7493 | -0.041198 | 49.6628 | 46.1197
498.1719 | 123.0789 | -58.3466 | 64.6225 | -0.060578 | -0.00023294 | 0.063734 | 0.061782 | 0.0020828 | 0.00026909 | -0.00055961 | 0.010864 | 0.0015295 | 0.0012818 | -0.0025036 | -0.00043791 | -0.0019483 | -0.0018971 | -8.7158 | 64.5676 | -58.4702 | 64.4257 | -58.1863 | -58.5709 | -58.5342 | -12.2864 | 64.6179 | -58.3649 | -58.3878 | -58.3466 | -58.4564 | -58.1772 | -0.1236 | -0.054932 | -0.19684 | 0.16022 | -0.18768 | -0.2243 | -0.064087 | -0.10071 | -0.01831 | -0.004578 | -123.0103 | 0 | 0.16937 | -0.10986 | 0.18768 | -0.091553 | 0.28381 | 122.8958 | 0.01831 | -0.022888 | 123.0377 | 122.9828 | 122.9141 | 122.9645 | -123.0927 | -122.9874 | 122.7722 | -0.041198 | 49.6307 | 46.0602
499.1719 | 123.0515 | -58.3694 | 64.6179 | -0.022431 | -0.00023294 | 0.061598 | 0.062636 | -0.00026703 | 0.0026191 | -0.003764 | 0.026123 | -0.00060665 | 0.0019226 | 0.0068958 | -0.0019333 | -0.0015211 | -0.0014697 | -8.844 | 64.5813 | -58.4976 | 64.3936 | -58.2367 | -58.5938 | -58.5663 | -12.4329 | 64.6454 | -58.3374 | -58.374 | -58.4244 | -58.4747 | -58.1818 | -0.12817 | -0.036621 | -0.2243 | 0.13275 | -0.19684 | -0.2243 | -0.068664 | -0.09613 | 0.032044 | 0.027466 | -122.9919 | -0.054931 | 0.18768 | -0.10528 | 0.15564 | -0.13733 | 0.26093 | 122.8912 | -0.086975 | -0.036621 | 123.0789 | 122.9828 | 122.9507 | 123.0148 | -123.1155 | -122.9553 | 122.7631 | -0.004577 | 49.5255 | 45.9366
500.1719 | 122.9828 | -58.3054 | 64.6179 | -0.014801 | 0.00040806 | 0.065016 | 0.063064 | -0.00069423 | 0.00026909 | -0.0016278 | 0.026123 | 0.00046135 | 0.00042723 | 0.00027342 | -0.0017197 | -0.0025891 | -0.0031787 | -8.8898 | 64.6042 | -58.4656 | 64.4073 | -58.2321 | -58.5938 | -58.5388 | -12.4512 | 64.6225 | -58.3603 | -58.3969 | -58.2825 | -58.1955 | -58.1223 | -0.16022 | -0.013733 | -0.21057 | 0.073242 | -0.23346 | -0.28839 | -0.073242 | -0.12817 | -0.054932 | 0.004578 | -123.0148 | 0.022888 | 0.18311 | 0.10986 | 0.23804 | 0.16479 | 0.23346 | 122.8729 | 0.07782 | -0.036621 | 123.0698 | 122.9828 | 122.9095 | 122.9279 | -123.0835 | -122.9782 | 122.7127 | -0.091553 | 49.4156 | 45.8542
501.1719 | 123.0606 | -58.3328 | 64.6225 | 0.00045798 | 0.00062166 | 0.066939 | 0.064559 | -0.0026168 | 0.0017645 | 0.00029479 | -0.0043946 | 0.0011023 | -0.00042717 | 0.00027342 | -0.00043791 | -0.0015211 | 0.0017345 | -9.0775 | 64.595 | -58.5114 | 64.3753 | -58.2367 | -58.58 | -58.5709 | -12.5153 | 64.65 | -58.3786 | -58.3786 | -58.342 | -58.4656 | -58.1589 | -0.17853 | -0.027466 | -0.24719 | 0.096131 | -0.23804 | -0.24719 | -0.059509 | -0.068664 | -0.045776 | 0.027465 | -123.0011 | -0.009155 | 0.17395 | -0.13275 | 0.21973 | -0.086975 | 0.27466 | 122.8867 | 0.036621 | 0 | 123.1064 | 123.0286 | 122.9279 | 122.9828 | -123.1339 | -123.0011 | 122.7081 | -0.045776 | 49.2554 | 45.8176
502.1719 | 123.056 | -58.3511 | 64.6362 | -0.098725 | -0.00023294 | 0.065443 | 0.063705 | 0.0027238 | -0.00037171 | -0.0014142 | 0.03833 | -0.00039305 | 0.0046996 | -0.0035718 | -0.00086511 | -0.0013073 | -0.00018806 | -8.9676 | 64.5584 | -58.4839 | 64.4073 | -58.1909 | -58.548 | -58.5205 | -12.5656 | 64.6362 | -58.3557 | -58.3878 | -58.3511 | -58.4793 | -58.1818 | -0.13275 | -0.077819 | -0.22888 | 0.16022 | -0.16937 | -0.19684 | -0.036621 | -0.064087 | -0.004578 | 0 | -123.024 | 0 | 0.16937 | -0.12817 | 0.17395 | -0.1236 | 0.29297 | 122.8912 | 0.004578 | -0.032043 | 123.0423 | 122.9919 | 122.9095 | 122.9874 | -123.1201 | -122.9919 | 122.7585 | -0.036621 | 49.3835 | 45.7855
503.1719 | 123.0423 | -58.3511 | 64.65 | -0.060578 | -0.0013009 | 0.061598 | 0.062423 | -0.0028304 | -0.0025079 | -0.0018414 | -0.01355 | 0.0019567 | 0.0014954 | 0.0054004 | -0.0012925 | -0.0015211 | -0.0023243 | -9.0775 | 64.6179 | -58.4793 | 64.3845 | -58.2184 | -58.5846 | -58.5571 | -12.5153 | 64.6591 | -58.3374 | -58.4198 | -58.342 | -58.461 | -58.1863 | -0.12817 | -0.032043 | -0.2655 | 0.13275 | -0.20599 | -0.23346 | -0.07782 | -0.10529 | 0.013733 | 0.009156 | -123.0698 | 0.009155 | 0.16479 | -0.10986 | 0.15106 | -0.1236 | 0.26093 | 122.8638 | -0.004578 | -0.082398 | 123.0972 | 122.9965 | 122.9691 | 123.0103 | -123.1293 | -122.9874 | 122.7356 | -0.068665 | 49.2737 | 45.8359
504.1719 | 123.0652 | -58.3328 | 64.6042 | -0.060578 | 0.00040806 | 0.063521 | 0.061996 | -0.0032578 | 0.0015509 | -0.00013241 | 0.013916 | -0.00039305 | 0.0021362 | 0.0013416 | -1.0706e-05 | -0.0015211 | 0.00088014 | -9.05 | 64.5767 | -58.461 | 64.4806 | -58.1314 | -58.5205 | -58.4793 | -12.6297 | 64.6133 | -58.3557 | -58.3374 | -58.3191 | -58.4381 | -58.1635 | -0.12817 | -0.027466 | -0.1236 | 0.20142 | -0.14648 | -0.18768 | -0.01831 | -0.059509 | -0.022888 | 0.009155 | -122.9416 | 0.013733 | 0.16937 | -0.10529 | 0.19226 | -0.082397 | 0.32959 | 122.9416 | 0.036621 | 0.018311 | 123.0377 | 122.9691 | 122.9095 | 122.9462 | -123.0652 | -122.9599 | 122.8134 | -0.004577 | 49.2828 | 45.7031
505.1719 | 123.0881 | -58.3191 | 64.6133 | -0.091095 | -0.0013009 | 0.063094 | 0.06285 | 0.0012284 | -0.0016535 | -0.002055 | 0.053589 | -0.00082025 | 0.00085443 | 0.0015552 | -0.00022431 | -0.0021619 | 0.0013073 | -9.1187 | 64.5813 | -58.461 | 64.4806 | -58.1085 | -58.5022 | -58.4564 | -12.6617 | 64.6088 | -58.342 | -58.3237 | -58.2825 | -58.3969 | -58.1131 | -0.14191 | -0.032043 | -0.13275 | 0.21057 | -0.13733 | -0.18311 | 0.004578 | -0.041198 | -0.022888 | -0.004577 | -122.937 | 0.036621 | 0.20599 | -0.07782 | 0.22888 | -0.054932 | 0.35248 | 122.9416 | 0.059509 | 0.018311 | 123.0423 | 122.9507 | 122.9004 | 122.9279 | -123.0743 | -122.9553 | 122.7997 | -0.004577 | 49.2004 | 45.6573
506.1719 | 123.1476 | -58.2687 | 64.6088 | -0.014801 | 0.0012625 | 0.063948 | 0.064345 | 0.0012284 | -0.00079891 | 0.00093559 | 0.03833 | -0.00017945 | 0.00064083 | 0.0034778 | -0.00086511 | -0.0025891 | -0.00082886 | -9.1644 | 64.5447 | -58.429 | 64.5081 | -58.1039 | -58.4839 | -58.429 | -12.7121 | 64.5859 | -58.3237 | -58.3054 | -58.255 | -58.3694 | -58.0811 | -0.16022 | -0.064087 | -0.10071 | 0.16479 | -0.16022 | -0.21515 | 0 | -0.054932 | -0.054931 | -0.022889 | -122.9141 | 0.013733 | 0.18768 | -0.10071 | 0.24261 | -0.045777 | 0.32501 | 122.937 | 0.068664 | 0.01831 | 122.9736 | 122.9095 | 122.8134 | 122.8546 | -123.0377 | -122.9324 | 122.7768 | -0.036621 | 49.1043 | 45.5566
507.1719 | 123.0606 | -58.3191 | 64.6454 | -0.068207 | 0.0016899 | 0.06288 | 0.0652 | 0.00058737 | -0.0016535 | -0.0029096 | 0.001709 | 0.0019567 | -0.0032044 | -0.0031446 | -0.00086511 | -0.0032301 | 0.00023934 | -9.3155 | 64.6088 | -58.4747 | 64.4073 | -58.2275 | -58.5846 | -58.5617 | -12.6526 | 64.6957 | -58.3191 | -58.3832 | -58.3603 | -58.4518 | -58.1772 | -0.15564 | -0.036621 | -0.23804 | 0.091553 | -0.24262 | -0.2655 | -0.086976 | -0.10986 | 0 | 0.050354 | -123.0286 | -0.041199 | 0.14191 | -0.13275 | 0.14191 | -0.13275 | 0.24719 | 122.8821 | -0.041199 | -0.064087 | 123.0835 | 123.0148 | 122.9279 | 123.0148 | -123.1201 | -122.9645 | 122.7264 | -0.064087 | 49.0036 | 45.6665
508.1719 | 123.0652 | -58.3282 | 64.6271 | -0.037689 | 0.0012625 | 0.063948 | 0.063277 | -0.0034714 | 0.00091009 | -0.002696 | 0.02002 | 0.00024775 | -0.0010682 | 0.0062548 | -0.0021469 | -0.0017347 | 0.0010937 | -9.2926 | 64.5996 | -58.4427 | 64.4806 | -58.1223 | -58.5022 | -58.461 | -12.8677 | 64.6225 | -58.3466 | -58.3466 | -58.2825 | -58.4015 | -58.1589 | -0.11444 | -0.027466 | -0.14648 | 0.20599 | -0.13275 | -0.17395 | -0.018311 | -0.059509 | -0.018311 | -0.004577 | -122.9736 | 0.045776 | 0.16937 | -0.073242 | 0.18768 | -0.054931 | 0.32043 | 122.9233 | 0.064087 | 0 | 123.0423 | 122.9691 | 122.9279 | 122.9507 | -123.0698 | -122.9736 | 122.8088 | -0.018311 | 49.0356 | 45.4605
509.1719 | 123.1338 | -58.3054 | 64.6042 | -0.12161 | 0.00083526 | 0.065016 | 0.061782 | -0.0017624 | 0.00069649 | -0.002696 | 0.041382 | -0.0014613 | 0.0012818 | -0.0033582 | -1.0706e-05 | -0.0032301 | 0.0023755 | -9.3292 | 64.5721 | -58.429 | 64.4989 | -58.0994 | -58.4839 | -58.4518 | -12.9272 | 64.5996 | -58.3466 | -58.3054 | -58.2916 | -58.4015 | -58.1131 | -0.1236 | -0.032043 | -0.10529 | 0.20599 | -0.14648 | -0.17853 | -0.022888 | -0.054932 | -0.041199 | -0.004578 | -122.9095 | 0.013733 | 0.19226 | -0.09613 | 0.23346 | -0.054931 | 0.32959 | 122.9279 | 0.054932 | 0.041199 | 123.0011 | 122.9462 | 122.8775 | 122.905 | -123.0331 | -122.9507 | 122.8043 | 0 | 48.9761 | 45.3781
510.1719 | 123.0652 | -58.3191 | 64.6271 | -0.045319 | -0.00066014 | 0.063094 | 0.063491 | -0.00026703 | -0.00058531 | -0.0022686 | 0.016968 | 0.00088875 | -0.00085457 | -0.002931 | -0.0015061 | -0.00088008 | 0.0010937 | -9.4345 | 64.6133 | -58.4106 | 64.4257 | -58.1726 | -58.5892 | -58.5205 | -13.0417 | 64.6317 | -58.3374 | -58.3603 | -58.3374 | -58.4518 | -58.168 | -0.091553 | -0.013733 | -0.20142 | 0.14648 | -0.20142 | -0.27008 | -0.10986 | -0.17853 | -0.01831 | 0.004578 | -122.9874 | -0.01831 | 0.15106 | -0.13275 | 0.16937 | -0.11444 | 0.23804 | 122.8363 | 0 | -0.022889 | 123.024 | 122.9691 | 122.9324 | 122.9507 | -123.0377 | -122.9645 | 122.7448 | -0.041199 | 48.8846 | 45.2774
511.1719 | 123.0789 | -58.3099 | 64.6454 | -0.060578 | 0.00040806 | 0.06288 | 0.06285 | 0.00037377 | -0.0027215 | -0.00055961 | 0.02002 | 0.00046135 | 0.001709 | 0.0054004 | 0.00084389 | -0.0049389 | -0.00061526 | -9.4894 | 64.6088 | -58.4473 | 64.4577 | -58.1497 | -58.5205 | -58.493 | -13.1058 | 64.6545 | -58.3649 | -58.3374 | -58.3237 | -58.4473 | -58.168 | -0.13733 | -0.036621 | -0.18768 | 0.16022 | -0.18311 | -0.21057 | -0.045776 | -0.073242 | -0.054931 | 0.009155 | -122.9828 | -0.013732 | 0.14191 | -0.13733 | 0.19684 | -0.082398 | 0.29755 | 122.905 | 0.041199 | 0.027466 | 123.056 | 123.0194 | 122.9187 | 122.9645 | -123.0927 | -123.0103 | 122.7676 | -0.027465 | 48.8205 | 45.2042
512.1719 | 123.1064 | -58.3374 | 64.6271 | -0.022431 | 0.0016899 | 0.065016 | 0.061141 | -0.00090783 | 0.00026909 | -0.0012006 | 0.035278 | 0.0015295 | 0.00064083 | -0.0037854 | 0.00020289 | -0.0021619 | -0.00082886 | -9.5306 | 64.5676 | -58.4381 | 64.4852 | -58.136 | -58.4885 | -58.461 | -13.1149 | 64.6408 | -58.342 | -58.3237 | -58.3008 | -58.4335 | -58.1223 | -0.10071 | -0.059509 | -0.14191 | 0.20142 | -0.1236 | -0.15106 | -0.022889 | -0.050354 | -0.004578 | 0.013733 | -122.9507 | 0.036621 | 0.21515 | -0.096131 | 0.21973 | -0.091553 | 0.30212 | 122.9233 | 0.041199 | 0.018311 | 123.0057 | 122.9828 | 122.905 | 122.9782 | -123.0652 | -122.9691 | 122.8226 | 0.013733 | 48.8068 | 45.2225
513.1719 | 123.1842 | -58.2825 | 64.6088 | -0.037689 | 0.0012625 | 0.062239 | 0.061782 | 0.0018692 | -0.0031489 | -0.00055961 | 0.044434 | 0.0030249 | 0.0012818 | -0.0037854 | -0.00043791 | -0.0017347 | -0.0010425 | -9.5718 | 64.5905 | -58.4381 | 64.682 | -58.3191 | -58.7814 | -58.4656 | -13.1653 | 64.5859 | -58.3374 | -58.2596 | -58.2047 | -58.2916 | -58.0353 | -0.15564 | -0.018311 | 0.073242 | -0.036621 | -0.1831 | -0.49896 | -0.027466 | -0.34332 | -0.054931 | -0.022889 | -122.8683 | 0.07782 | 0.24719 | -0.009155 | 0.30212 | 0.045776 | 0.11902 | 123.1201 | 0.13275 | 0.077819 | 123.0286 | 122.9233 | 122.8729 | 122.8683 | -123.0469 | -122.9462 | 122.9645 | 0.022888 | 48.7106 | 45.1172
514.1719 | 123.0789 | -58.3099 | 64.6545 | 0.023346 | -0.00087374 | 0.062239 | 0.063064 | 0.0022964 | 0.00091009 | -0.0022686 | 0.013916 | -0.00017945 | 0.0025634 | -0.0014356 | 0.00084389 | -0.0036573 | -0.00040166 | -9.6405 | 64.5996 | -58.4335 | 64.4394 | -58.1772 | -58.5434 | -58.493 | -13.3163 | 64.65 | -58.3466 | -58.3603 | -58.3191 | -58.4381 | -58.1497 | -0.1236 | -0.054932 | -0.21515 | 0.13275 | -0.18311 | -0.23346 | -0.059509 | -0.10986 | -0.036621 | -0.004578 | -123.0148 | -0.009155 | 0.16022 | -0.12817 | 0.19684 | -0.091552 | 0.25635 | 122.8729 | 0.027466 | -0.013733 | 123.0331 | 122.9965 | 122.9095 | 122.9599 | -123.0881 | -123.0011 | 122.7493 | -0.050354 | 48.6694 | 44.9936
515.1719 | 123.0606 | -58.3099 | 64.65 | -0.098725 | 0.0021171 | 0.063521 | 0.06285 | -0.003685 | -0.0014399 | 0.0015766 | 0.010864 | 3.4148e-05 | 0.00042723 | -0.0010084 | -0.0010787 | -0.0017347 | -0.0031787 | -9.6725 | 64.6179 | -58.4381 | 64.476 | -58.1635 | -58.5114 | -58.4885 | -13.353 | 64.65 | -58.3557 | -58.342 | -58.3237 | -58.429 | -58.1589 | -0.12817 | -0.032043 | -0.17395 | 0.14648 | -0.17853 | -0.20142 | -0.050354 | -0.073243 | -0.045776 | 0 | -122.9919 | -0.013732 | 0.15106 | -0.11902 | 0.19684 | -0.073242 | 0.27466 | 122.9141 | 0.032044 | 0.013733 | 123.056 | 123.0057 | 122.9279 | 122.9599 | -123.0881 | -123.0057 | 122.7859 | -0.032043 | 48.6374 | 44.957
516.1719 | 123.056 | -58.3054 | 64.6408 | -0.037689 | 0.00019446 | 0.065016 | 0.063277 | -0.0015488 | -0.00058531 | -0.00034601 | 0.029175 | 0.00088875 | 0.001068 | -0.00058098 | -0.0023605 | -0.00088008 | -0.0016833 | -9.7183 | 64.6133 | -58.4152 | 64.5126 | -58.1314 | -58.493 | -58.4381 | -13.3759 | 64.6454 | -58.342 | -58.3282 | -58.2962 | -58.3969 | -58.1177 | -0.10986 | -0.027466 | -0.12817 | 0.17395 | -0.13275 | -0.18768 | -0.022888 | -0.07782 | -0.036621 | 0.004578 | -122.9691 | 0.009155 | 0.18768 | -0.091553 | 0.2243 | -0.054932 | 0.28381 | 122.9279 | 0.045776 | 0.013733 | 123.0286 | 122.9874 | 122.9187 | 122.9507 | -123.056 | -122.9828 | 122.818 | -0.022888 | 48.587 | 44.9295
517.1719 | 123.1567 | -58.287 | 64.6133 | -0.014801 | 0.0019035 | 0.063307 | 0.062209 | -0.0011214 | 0.0015509 | -0.00077341 | 0.068848 | -0.00060665 | 0.0021362 | -0.00036738 | -0.00086511 | -0.0030163 | -0.00061526 | -9.7687 | 64.5538 | -58.4198 | 64.7278 | -57.811 | -58.7814 | -58.6395 | -13.3804 | 64.6042 | -58.3191 | -58.2321 | -58.2138 | -58.2962 | -58.0215 | -0.13275 | -0.059509 | 0.11444 | 0.47607 | -0.35248 | -0.49439 | -0.21973 | -0.36163 | -0.032044 | -0.009155 | -122.8455 | 0.073242 | 0.2655 | -0.009156 | 0.29755 | 0.022888 | 0.60883 | 123.1476 | 0.10529 | 0.086975 | 122.9736 | 122.9233 | 122.8409 | 122.8912 | -123.0331 | -122.9324 | 123.0148 | 0.054931 | 48.5184 | 44.9066
518.1719 | 123.175 | -58.2642 | 64.5767 | -0.0071715 | 0.00062166 | 0.063307 | 0.061141 | -0.00026703 | -0.00015811 | -0.00055961 | 0.056641 | 0.00046135 | 0.0023498 | 0.0028368 | 0.00041649 | -0.00045288 | -0.0033923 | -9.819 | 64.5859 | -58.4152 | 64.5355 | -58.0536 | -58.429 | -58.4061 | -13.4354 | 64.6271 | -58.2825 | -58.2047 | -58.2321 | -58.3374 | -58.017 | -0.15106 | 0.009155 | -0.041199 | 0.21057 | -0.14191 | -0.1648 | 0.009155 | -0.013733 | -0.018311 | 0.050354 | -122.7814 | 0.032043 | 0.24719 | -0.073242 | 0.2655 | -0.054931 | 0.36163 | 122.9507 | 0.050354 | 0.07782 | 123.0011 | 122.9095 | 122.85 | 122.8912 | -122.9919 | -122.8592 | 122.7997 | 0.059509 | 48.4451 | 44.8288
519.1719 | 123.0881 | -58.2642 | 64.6225 | -0.037689 | 0.0012625 | 0.06288 | 0.062636 | -0.001976 | 0.00069649 | 0.0015766 | 0.059692 | 0.0011023 | 0.0019226 | -0.0014356 | -0.0017197 | -0.0013073 | 0.00023934 | -9.8557 | 64.5676 | -58.3832 | 64.5538 | -58.0307 | -58.4427 | -58.3786 | -13.4354 | 64.6088 | -58.3054 | -58.2413 | -58.1085 | -57.9666 | -57.7835 | -0.11902 | -0.054932 | -0.068665 | 0.23346 | -0.11444 | -0.17853 | 0.004578 | -0.059509 | -0.041199 | -0.013733 | -122.8638 | 0.15564 | 0.48065 | 0.29755 | 0.52185 | 0.33875 | 0.35248 | 122.937 | 0.19684 | 0.064087 | 122.9507 | 122.9141 | 122.8317 | 122.8729 | -123.0057 | -122.9279 | 122.818 | 0.022888 | 48.4085 | 44.8288
520.1719 | 123.1567 | -58.2825 | 64.6133 | -0.03006 | 0.0016899 | 0.063948 | 0.062209 | 0.00016017 | 0.00026909 | -0.0031232 | 0.047485 | -0.0018885 | 0.00085443 | -0.0082716 | -0.00065151 | -0.00088008 | -0.0029651 | -9.9152 | 64.5584 | -58.4198 | 64.5355 | -58.0536 | -58.4381 | -58.3832 | -13.5086 | 64.6271 | -58.3145 | -58.223 | -58.1955 | -58.2825 | -58.0353 | -0.13733 | -0.054931 | -0.07782 | 0.22888 | -0.10071 | -0.15564 | 0.036621 | -0.01831 | -0.032043 | 0.013733 | -122.8363 | 0.086975 | 0.24719 | 0 | 0.27924 | 0.032043 | 0.36621 | 122.9553 | 0.11902 | 0.091553 | 122.9782 | 122.9416 | 122.8409 | 122.9095 | -123.0331 | -122.9279 | 122.818 | 0.05951 | 48.3673 | 44.7739
521.1719 | 123.1064 | -58.2916 | 64.6362 | -0.052948 | 0.00062166 | 0.06523 | 0.061355 | 0.0027238 | 0.00026909 | -0.0014142 | 0.016968 | 0.00024775 | 2.8e-08 | -0.0010084 | -0.0021469 | -0.0015211 | -0.0023243 | -9.9472 | 64.6042 | -58.4152 | 64.5218 | -58.0948 | -58.461 | -58.4244 | -13.6368 | 64.6408 | -58.3191 | -58.2962 | -58.2642 | -58.3603 | -58.0856 | -0.1236 | -0.032043 | -0.11444 | 0.19684 | -0.13275 | -0.16937 | -0.009155 | -0.045777 | -0.027466 | 0.004578 | -122.9324 | 0.027466 | 0.20599 | -0.068665 | 0.23346 | -0.041199 | 0.32043 | 122.937 | 0.054932 | 0.022888 | 123.0194 | 122.9599 | 122.8958 | 122.9324 | -123.0515 | -122.9553 | 122.8134 | -0.004578 | 48.3444 | 44.6548
522.1719 | 123.1888 | -58.2779 | 64.6042 | -0.098725 | 0.00062166 | 0.064803 | 0.061355 | 0.003151 | -0.0016535 | -0.0012006 | 0.013916 | -0.00060665 | 0.0012818 | 0.00070062 | -0.00043791 | -0.0023755 | -0.0023243 | -10.0113 | 64.5721 | -58.3832 | 64.5493 | -58.0444 | -58.429 | -58.3969 | -13.3575 | 64.7141 | -58.2642 | -58.2779 | -58.2001 | -58.2916 | -58.049 | -0.10529 | -0.032043 | -0.054932 | 0.23346 | -0.11902 | -0.15106 | -0.013733 | -0.045776 | 0.013733 | 0.10986 | -122.8821 | 0.07782 | 0.22888 | -0.013733 | 0.21515 | -0.027466 | 0.33874 | 122.9324 | 0.064087 | -0.013733 | 122.9553 | 122.9782 | 122.85 | 122.9919 | -122.9874 | -122.8683 | 122.8271 | 0 | 48.2666 | 44.9203
523.1719 | 123.1476 | -58.2825 | 64.5813 | -0.037689 | -0.00087374 | 0.06288 | 0.063277 | 0.0010148 | -0.0010125 | -0.0018414 | 0.03833 | 0.0015295 | 0.00042723 | -0.00015378 | -0.0030013 | -0.0021619 | -0.0055287 | -10.0342 | 64.5905 | -58.4198 | 64.563 | -58.0215 | -58.4106 | -58.3969 | -13.678 | 64.6179 | -58.2962 | -58.1863 | -57.9025 | -58.4564 | -58.2504 | -0.13733 | 0.009155 | -0.018311 | 0.26093 | -0.11444 | -0.12817 | 0.022888 | 0.009155 | -0.013733 | 0.036621 | -122.7676 | 0.37994 | 0.032044 | -0.17395 | 0.045777 | -0.16022 | 0.39825 | 122.9828 | 0.39368 | 0.10986 | 123.0103 | 122.9141 | 122.8729 | 122.9004 | -123.0011 | -122.8775 | 122.8455 | 0.096131 | 48.2483 | 44.6045
524.1719 | 123.2208 | -58.287 | 64.6317 | -0.052948 | 0.0019035 | 0.06053 | 0.062209 | 0.001442 | 0.00091009 | -0.0024822 | 0.023071 | 3.4148e-05 | 0.0019226 | -0.0044262 | 0.00041649 | -0.00088008 | -0.0012561 | -10.0754 | 64.5767 | -58.4106 | 64.5355 | -58.017 | -58.4244 | -58.3786 | -13.7146 | 64.6317 | -58.2916 | -58.223 | -58.1772 | -58.2825 | -58.0307 | -0.1236 | -0.054932 | -0.096131 | 0.27008 | -0.091553 | -0.13733 | 0.032044 | -0.013732 | -0.004578 | 0 | -122.8546 | 0.10986 | 0.25635 | 0.004577 | 0.26093 | 0.009155 | 0.39368 | 122.9462 | 0.11444 | 0.068665 | 122.9874 | 122.9233 | 122.8638 | 122.9187 | -123.0423 | -122.9233 | 122.8226 | 0.064087 | 48.2117 | 44.5724
525.1719 | 123.1888 | -58.2962 | 64.65 | -0.10635 | -1.9142e-05 | 0.063094 | 0.063705 | -0.00069423 | -0.0040033 | -0.002696 | 0.03833 | 0.00088875 | 0.00064083 | -0.0025036 | -0.0019333 | -0.0013073 | -0.00018806 | -10.144 | 64.6088 | -58.429 | 64.7507 | -58.1223 | -58.8455 | -58.493 | -13.8611 | 64.6179 | -58.3145 | -58.2275 | -58.1909 | -58.287 | -58.0261 | -0.13275 | -0.041198 | 0.10071 | 0.17395 | -0.19684 | -0.54932 | -0.064087 | -0.41656 | -0.01831 | -0.032043 | -122.8775 | 0.10529 | 0.27008 | 0.009156 | 0.28839 | 0.027466 | 0.3067 | 123.1796 | 0.1236 | 0.086975 | 123.0377 | 122.9324 | 122.905 | 122.9141 | -123.0789 | -122.9645 | 123.0469 | 0.068665 | 48.1522 | 44.4351
526.1719 | 123.1888 | -58.2733 | 64.6088 | -0.037689 | -0.0023691 | 0.06523 | 0.062636 | 0.001442 | -0.0016535 | -0.00098701 | 0.016968 | 0.00046135 | 0.00085443 | 0.0032642 | 0.00041649 | 0.00061532 | -0.0031787 | -10.1761 | 64.5859 | -58.4152 | 64.5584 | -58.0536 | -58.4335 | -58.3923 | -13.8474 | 64.6317 | -58.2962 | -58.2413 | -58.1131 | -58.3191 | -58.049 | -0.14191 | -0.022889 | -0.050354 | 0.21973 | -0.11902 | -0.16022 | 0.022888 | -0.018311 | -0.022889 | 0.022888 | -122.85 | 0.16022 | 0.2243 | -0.045777 | 0.24719 | -0.022888 | 0.36163 | 122.9736 | 0.18311 | 0.054932 | 123.0011 | 122.9279 | 122.8592 | 122.905 | -123.024 | -122.905 | 122.8317 | 0.032043 | 48.0972 | 44.426
527.1719 | 123.056 | -58.3191 | 64.6317 | -0.098725 | 0.00062166 | 0.063521 | 0.065414 | 0.0012284 | 0.00048269 | -0.00098701 | -0.077637 | 0.0030249 | -0.0012818 | 0.0013416 | -0.00022431 | -2.5678e-05 | -0.0029651 | -10.2951 | 64.5996 | -58.4335 | 64.4394 | -58.1818 | -58.5846 | -58.5297 | -14.0854 | 64.6637 | -58.3374 | -58.3099 | -58.3374 | -58.4656 | -58.1543 | -0.11444 | -0.032044 | -0.19226 | 0.13733 | -0.21057 | -0.2655 | -0.09613 | -0.15106 | -0.01831 | 0.032043 | -122.9416 | -0.01831 | 0.16479 | -0.14648 | 0.1831 | -0.12817 | 0.25177 | 122.8729 | 0 | 0.027465 | 123.0331 | 123.0011 | 122.9187 | 122.9828 | -123.0652 | -122.9691 | 122.7585 | 0.009155 | 48.024 | 44.2337
528.1719 | 123.1888 | -58.2504 | 64.6133 | -0.045319 | -0.0015145 | 0.064162 | 0.063918 | -0.0032578 | 0.0019781 | -0.0016278 | 0.032227 | -0.0014613 | 0.0023498 | -0.0048536 | -0.00043791 | -0.00088008 | 0.00088014 | -10.318 | 64.5676 | -58.3923 | 64.5493 | -58.0307 | -58.4427 | -58.374 | -13.9618 | 64.6225 | -58.3099 | -58.2092 | -58.1314 | -58.255 | -58.0032 | -0.14191 | -0.045776 | -0.064087 | 0.21973 | -0.1236 | -0.19226 | 0.018311 | -0.050354 | -0.05951 | 0.009156 | -122.8226 | 0.11902 | 0.24719 | -0.004578 | 0.3067 | 0.054932 | 0.36163 | 122.9416 | 0.17853 | 0.10071 | 122.9599 | 122.9324 | 122.818 | 122.8729 | -123.0057 | -122.9233 | 122.7997 | 0.041198 | 47.9324 | 44.2886
529.1719 | 123.2071 | -58.255 | 64.6362 | -0.091095 | -0.0019417 | 0.06523 | 0.061568 | -0.0021896 | 0.00048269 | 0.0020038 | 0.029175 | 0.00024775 | -0.0010682 | -0.00015378 | -0.00065151 | -0.0028027 | -0.0070239 | -10.3729 | 64.5859 | -58.429 | 64.5447 | -58.0627 | -58.429 | -58.3923 | -14.0305 | 64.6362 | -58.3008 | -58.2047 | -58.1726 | -58.2779 | -58.0078 | -0.17395 | -0.050354 | -0.091552 | 0.19226 | -0.13733 | -0.17395 | 0.036621 | 0 | -0.045776 | 0 | -122.8409 | 0.082398 | 0.24719 | -0.022888 | 0.29297 | 0.022888 | 0.36621 | 122.9736 | 0.12817 | 0.09613 | 123.0148 | 122.937 | 122.8409 | 122.8912 | -123.0652 | -122.937 | 122.7997 | 0.050354 | 47.8821 | 44.2245
530.1719 | 123.175 | -58.2687 | 64.6133 | -0.060578 | 0.00062166 | 0.064375 | 0.064773 | 0.0010148 | -0.0014399 | 0.00050839 | 0.053589 | 0.00046135 | 0.0021362 | -0.0014356 | -0.0015061 | -0.0038709 | -0.0048877 | -10.3592 | 64.595 | -58.4106 | 64.5813 | -58.0124 | -58.3832 | -58.3832 | -14.0625 | 64.6225 | -58.2916 | -58.0582 | -58.2001 | -58.6212 | -58.2458 | -0.14191 | -0.01831 | -0.032043 | 0.25635 | -0.11444 | -0.11444 | 0.027466 | 0.027466 | -0.022888 | 0.009156 | -122.6715 | 0.068665 | 0.022888 | -0.35248 | 0.045776 | -0.32959 | 0.39825 | 122.9919 | 0.091553 | 0.23346 | 123.0057 | 122.9141 | 122.8638 | 122.8912 | -123.024 | -122.905 | 122.85 | 0.21057 | 47.9095 | 44.2062
531.1719 | 123.1613 | -58.2642 | 64.6362 | -0.091095 | 0.0023307 | 0.062239 | 0.061355 | 0.003151 | -0.00015811 | 0.00050839 | 0.026123 | -0.0010339 | 0.00064083 | 0.00027342 | -0.0012925 | -0.0017347 | -0.0014697 | -10.405 | 64.6042 | -58.3878 | 64.5767 | -58.0078 | -58.4244 | -58.3786 | -14.0945 | 64.6271 | -58.2825 | -58.2138 | -58.1726 | -58.2687 | -58.0124 | -0.1236 | -0.032043 | -0.059509 | 0.25635 | -0.11444 | -0.16022 | 0.009155 | -0.036621 | -0.018311 | -0.009155 | -122.85 | 0.091553 | 0.25177 | -0.004578 | 0.27008 | 0.013733 | 0.37994 | 122.9645 | 0.10986 | 0.068665 | 122.9919 | 122.9095 | 122.8683 | 122.8912 | -123.024 | -122.9187 | 122.8409 | 0.050354 | 47.8592 | 44.1696
532.1719 | 123.056 | -58.2779 | 64.6866 | -0.052948 | -0.0023691 | 0.061598 | 0.064773 | -0.00069423 | -0.00015811 | 0.003072 | -0.016602 | -0.0010339 | -0.00085457 | -0.0025036 | -0.0012925 | -0.0028027 | 0.0017345 | -10.524 | 64.6362 | -58.4335 | 64.4485 | -58.1635 | -58.5205 | -58.493 | -14.3372 | 64.7141 | -58.3099 | -58.3054 | -58.2825 | -58.4061 | -58.1314 | -0.15564 | -0.050354 | -0.23804 | 0.11444 | -0.21515 | -0.24262 | -0.059509 | -0.086975 | -0.032044 | 0.027466 | -122.9919 | -0.004578 | 0.14648 | -0.12817 | 0.17853 | -0.09613 | 0.27008 | 122.8821 | 0.027466 | 0.004578 | 123.0698 | 123.024 | 122.9141 | 122.9919 | -123.1201 | -122.9965 | 122.7264 | -0.027466 | 47.7539 | 43.9407
533.1719 | 123.1384 | -58.2642 | 64.5996 | -0.068207 | -1.9142e-05 | 0.062666 | 0.063064 | 0.0012284 | 0.0017645 | 0.0015766 | 0.044434 | 0.00067495 | -0.0010682 | -0.0016492 | -0.0010787 | -0.0030163 | 2.554e-05 | -10.5972 | 64.5767 | -58.4198 | 64.4897 | -58.1268 | -58.5114 | -58.4427 | -14.3692 | 64.6454 | -58.3191 | -58.2458 | -58.2001 | -58.3145 | -58.049 | -0.15564 | -0.022888 | -0.10986 | 0.13733 | -0.17853 | -0.24719 | -0.022888 | -0.091553 | -0.054932 | 0.045777 | -122.8455 | 0.064087 | 0.21515 | -0.050354 | 0.27008 | 0.004578 | 0.29297 | 122.9095 | 0.11902 | 0.073242 | 122.9965 | 122.9645 | 122.8409 | 122.9095 | -123.0194 | -122.9187 | 122.7539 | 0.01831 | 47.6669 | 43.895
534.1719 | 123.1384 | -58.2916 | 64.6042 | -0.052948 | 0.00083526 | 0.065016 | 0.062209 | -0.0011214 | 0.00026909 | 0.00029479 | -0.0013428 | -0.00060665 | 0.00085443 | -0.00036738 | -0.0021469 | -0.0019483 | -0.0018971 | -10.6522 | 64.595 | -58.4152 | 64.476 | -58.1039 | -58.5251 | -58.4473 | -14.4424 | 64.6179 | -58.3237 | -58.255 | -58.2047 | -58.3374 | -58.0582 | -0.1236 | -0.009155 | -0.12817 | 0.18768 | -0.15564 | -0.23346 | -0.032044 | -0.10986 | -0.032043 | 0.013733 | -122.8592 | 0.086975 | 0.23346 | -0.045776 | 0.2655 | -0.013733 | 0.31128 | 122.8912 | 0.11902 | 0.068664 | 123.0103 | 122.9416 | 122.8867 | 122.9095 | -123.0194 | -122.9279 | 122.7676 | 0.036621 | 47.6395 | 43.8492
535.1719 | 123.1979 | -58.2596 | 64.6133 | -0.060578 | 0.0014761 | 0.06288 | 0.063918 | -0.00090783 | -0.0012261 | -0.00034601 | 0.03833 | 0.00024775 | -0.0010682 | -0.0014356 | -0.0010787 | -0.00045288 | 0.00045294 | -10.6705 | 64.5813 | -58.3969 | 64.5309 | -58.0902 | -58.4656 | -58.3969 | -14.4333 | 64.6225 | -58.3054 | -58.2138 | -58.1863 | -58.2962 | -58.0215 | -0.13733 | -0.032043 | -0.082397 | 0.16937 | -0.13733 | -0.20599 | 0 | -0.068664 | -0.045776 | 0.009156 | -122.8271 | 0.073243 | 0.23804 | -0.036621 | 0.28381 | 0.009155 | 0.3067 | 122.9279 | 0.11902 | 0.091553 | 122.9782 | 122.9279 | 122.8409 | 122.8821 | -123.0103 | -122.9187 | 122.7905 | 0.045777 | 47.5891 | 43.8263
536.1719 | 123.1934 | -58.2092 | 64.6362 | -0.083466 | 0.00040806 | 0.064375 | 0.062209 | -0.0013352 | -0.00037171 | 0.00093559 | 0.023071 | -0.0014613 | 0.0014954 | -0.0086988 | -0.0019333 | -0.0023755 | -0.0025379 | -10.6842 | 64.5996 | -58.3923 | 64.5721 | -58.017 | -58.429 | -58.3923 | -14.415 | 64.6362 | -58.2642 | -58.1772 | -58.1406 | -58.2504 | -58.0032 | -0.1831 | -0.036621 | -0.064086 | 0.19226 | -0.1831 | -0.21973 | 0 | -0.036621 | -0.054931 | 0 | -122.8134 | 0.068665 | 0.20599 | -0.041198 | 0.26093 | 0.013733 | 0.37537 | 122.9645 | 0.1236 | 0.086975 | 122.9919 | 122.9004 | 122.8088 | 122.8455 | -123.0286 | -122.9004 | 122.7814 | 0.032044 | 47.525 | 43.7943
537.1719 | 123.1888 | -58.2596 | 64.6362 | -0.083466 | 0.0027579 | 0.065016 | 0.064559 | -0.0011214 | -0.0016535 | -0.002696 | 0.016968 | 0.00067495 | -0.00042717 | -0.00229 | -0.0023605 | -0.0017347 | -0.0027515 | -10.7666 | 64.595 | -58.4152 | 64.5035 | -58.1131 | -58.4793 | -58.4152 | -14.5706 | 64.6454 | -58.2962 | -58.2092 | -58.1909 | -58.3145 | -58.0444 | -0.15564 | -0.041198 | -0.13275 | 0.14648 | -0.15564 | -0.21973 | 0 | -0.064087 | -0.036621 | 0.009156 | -122.8455 | 0.068665 | 0.21515 | -0.054931 | 0.25177 | -0.01831 | 0.30212 | 122.9187 | 0.10529 | 0.086975 | 123.0103 | 122.9416 | 122.8546 | 122.905 | -123.0515 | -122.9324 | 122.7631 | 0.050354 | 47.493 | 43.689
538.1719 | 123.2025 | -58.255 | 64.6133 | -0.0071715 | 0.0014761 | 0.063521 | 0.062209 | 0.0037918 | -0.0018671 | -0.0022686 | 0.032227 | -0.0016749 | 0.00042723 | 0.00091422 | -0.0015061 | -0.0017347 | -0.0018971 | -10.7895 | 64.595 | -58.3832 | 64.5493 | -58.0536 | -58.4381 | -58.3694 | -14.5615 | 64.6454 | -58.2916 | -58.1772 | -58.1497 | -58.2825 | -57.9941 | -0.12817 | -0.01831 | -0.064087 | 0.20142 | -0.11444 | -0.18311 | 0.013733 | -0.054931 | -0.036621 | 0.032044 | -122.7905 | 0.10529 | 0.26093 | -0.027466 | 0.29755 | 0.009155 | 0.32959 | 122.9324 | 0.14191 | 0.11444 | 122.9782 | 122.937 | 122.85 | 122.9004 | -122.9965 | -122.905 | 122.8043 | 0.07782 | 47.4655 | 43.6935
539.1719 | 123.143 | -58.2687 | 64.6362 | -0.12161 | 0.00083526 | 0.064162 | 0.063064 | -0.0032578 | 0.00026909 | -0.00055961 | -0.0074462 | 0.00088875 | 0.0014954 | 0.0015552 | -0.0025741 | -0.00066648 | -0.0027515 | -10.8948 | 64.5996 | -58.4061 | 64.4897 | -58.1223 | -58.5022 | -58.4656 | -14.7354 | 64.6454 | -58.3237 | -58.2596 | -58.255 | -58.2184 | -57.9208 | -0.13733 | -0.036621 | -0.14648 | 0.14648 | -0.19684 | -0.23346 | -0.059509 | -0.09613 | -0.054931 | 0.009156 | -122.8958 | 0.013733 | 0.3479 | 0.050354 | 0.40283 | 0.10529 | 0.28381 | 122.8958 | 0.068664 | 0.064086 | 123.0057 | 122.9691 | 122.8683 | 122.9141 | -123.0423 | -122.9599 | 122.7585 | 0.009155 | 47.374 | 43.5333
540.1719 | 123.1613 | -58.255 | 64.6408 | -0.12161 | -0.00023294 | 0.065657 | 0.063491 | -0.0013352 | -0.0025079 | 0.00072199 | -0.0043946 | 0.00046135 | -0.00042717 | 0.0030506 | -1.0706e-05 | -0.0013073 | -0.0027515 | -10.9222 | 64.595 | -58.4061 | 64.5035 | -58.1131 | -58.493 | -58.429 | -14.7675 | 64.6408 | -58.3099 | -58.2413 | -58.2138 | -58.3328 | -58.049 | -0.15106 | -0.045776 | -0.13733 | 0.14191 | -0.17395 | -0.23804 | -0.022888 | -0.086975 | -0.054932 | 0 | -122.8821 | 0.041199 | 0.20599 | -0.07782 | 0.26093 | -0.022888 | 0.29297 | 122.9095 | 0.096131 | 0.068665 | 123.0011 | 122.9507 | 122.85 | 122.8958 | -123.0469 | -122.9507 | 122.7585 | 0.013733 | 47.3328 | 43.4875
541.1719 | 123.2346 | -58.2047 | 64.6683 | 0.008087 | 0.00062166 | 0.064803 | 0.061568 | -0.0015488 | -0.0016535 | -0.002696 | 0.0047608 | 3.4148e-05 | -0.00064077 | -0.001222 | -0.0017197 | -0.00023928 | -0.0025379 | -10.8948 | 64.6042 | -58.3649 | 64.5813 | -57.9895 | -58.374 | -58.3374 | -14.6667 | 64.6408 | -58.2779 | -58.1909 | -58.1406 | -58.0261 | -57.7744 | -0.16022 | -0.064087 | -0.086975 | 0.21515 | -0.13275 | -0.16937 | 0.027466 | -0.009155 | -0.073242 | -0.027466 | -122.8592 | 0.064087 | 0.4303 | 0.17853 | 0.50354 | 0.25177 | 0.37537 | 122.9462 | 0.13733 | 0.086975 | 122.9691 | 122.9187 | 122.8088 | 122.8455 | -123.0331 | -122.9462 | 122.7859 | 0.013733 | 47.3099 | 43.5379
542.1719 | 123.1659 | -58.2642 | 64.6362 | -0.060578 | -0.0010873 | 0.064803 | 0.061355 | -0.0024032 | 0.0019781 | -0.0052594 | -0.01355 | -0.0023157 | 0.00085443 | 0.0017688 | -0.00065151 | -0.0021619 | 0.0019483 | -10.9726 | 64.6179 | -58.3923 | 64.5447 | -58.0811 | -58.4427 | -58.4015 | -14.8178 | 64.6408 | -58.3054 | -58.2001 | -58.168 | -58.2733 | -58.0124 | -0.12817 | -0.01831 | -0.091552 | 0.1831 | -0.13733 | -0.17853 | -0.009155 | -0.050354 | -0.041199 | 0.004578 | -122.8363 | 0.09613 | 0.25177 | -0.009155 | 0.29297 | 0.032044 | 0.31128 | 122.937 | 0.13733 | 0.10529 | 123.0103 | 122.9462 | 122.8821 | 122.905 | -123.0286 | -122.9416 | 122.8088 | 0.064087 | 47.2916 | 43.4463
543.1719 | 123.1705 | -58.2367 | 64.6271 | -0.10635 | 0.00062166 | 0.063094 | 0.062636 | 0.0027238 | -0.00015811 | -0.00098701 | 0.010864 | 0.00067495 | -0.00021357 | 0.00027342 | -0.0027877 | -0.0013073 | -0.00018806 | -11.0229 | 64.6225 | -58.3969 | 64.5401 | -58.0673 | -58.4747 | -58.3969 | -14.8727 | 64.6545 | -58.2916 | -58.1909 | -58.1772 | -58.2916 | -58.017 | -0.16022 | -0.004577 | -0.086975 | 0.16937 | -0.16022 | -0.23804 | 0 | -0.077819 | -0.054932 | 0.027466 | -122.818 | 0.059509 | 0.21973 | -0.054932 | 0.27466 | 0 | 0.32959 | 122.937 | 0.11444 | 0.10071 | 123.0194 | 122.9462 | 122.8592 | 122.8912 | -123.024 | -122.9187 | 122.7768 | 0.045776 | 47.2137 | 43.364
544.1719 | 123.1613 | -58.2367 | 64.6454 | -0.1445 | -0.00044654 | 0.064589 | 0.061355 | 0.0033646 | -0.00079891 | -0.0012006 | 0.02002 | 0.00067495 | 0.001068 | 0.0054004 | -0.0010787 | -0.0032301 | -0.00018806 | -11.087 | 64.6179 | -58.3969 | 64.5264 | -58.0765 | -58.4656 | -58.4061 | -14.9231 | 64.6545 | -58.2962 | -58.1909 | -58.1818 | -58.2962 | -58.0124 | -0.16022 | -0.027466 | -0.11902 | 0.16022 | -0.16937 | -0.22888 | -0.009155 | -0.068664 | -0.05951 | 0.009155 | -122.8363 | 0.054931 | 0.2243 | -0.05951 | 0.28381 | 0 | 0.32044 | 122.9233 | 0.11444 | 0.10529 | 123.0148 | 122.9507 | 122.8546 | 122.8912 | -123.0423 | -122.9416 | 122.7631 | 0.045776 | 47.1497 | 43.3136
545.1719 | 123.1705 | -58.2642 | 64.6408 | -0.083466 | 0.00019446 | 0.064803 | 0.063064 | -0.001976 | 5.5488e-05 | -0.0012006 | 0.010864 | 0.00046135 | 0.001068 | -0.0080578 | 0.00084389 | -0.0028027 | 0.0030163 | -11.1237 | 64.6042 | -58.3969 | 64.5264 | -58.0811 | -58.4518 | -58.4061 | -14.9689 | 64.65 | -58.2779 | -58.1955 | -58.168 | -58.3008 | -58.0215 | -0.13275 | -0.036621 | -0.11444 | 0.1831 | -0.14191 | -0.18768 | -0.009155 | -0.054931 | -0.013733 | 0.009155 | -122.8363 | 0.09613 | 0.24261 | -0.036621 | 0.25635 | -0.022888 | 0.31586 | 122.9233 | 0.10986 | 0.082397 | 123.0011 | 122.9279 | 122.8683 | 122.9141 | -123.0377 | -122.9187 | 122.7905 | 0.068664 | 47.1405 | 43.2953
546.1719 | 123.1155 | -58.255 | 64.595 | -0.12924 | 0.0014761 | 0.064375 | 0.062209 | 0.00058737 | 5.5488e-05 | -0.0031232 | -0.028809 | -0.00060665 | -0.00021357 | 0.0030506 | -0.0017197 | -0.0017347 | -0.0012561 | -11.1969 | 64.5905 | -58.3969 | 64.4989 | -58.1131 | -58.5022 | -58.4427 | -15.0833 | 64.6545 | -58.3008 | -58.2504 | -58.223 | -58.3511 | -58.0627 | -0.14191 | -0.004578 | -0.096131 | 0.14191 | -0.18768 | -0.24719 | -0.045776 | -0.10529 | -0.045776 | 0.059509 | -122.8455 | 0.032044 | 0.19226 | -0.09613 | 0.23804 | -0.050354 | 0.28381 | 122.8958 | 0.07782 | 0.050354 | 122.9874 | 122.9553 | 122.8455 | 122.9095 | -122.9919 | -122.8958 | 122.7539 | 0.004578 | 47.0581 | 43.1717
547.1719 | 123.1888 | -58.2001 | 64.6317 | -0.037689 | 0.00040806 | 0.063094 | 0.065414 | 0.00037377 | -0.00058531 | -0.002055 | 0.010864 | -0.0010339 | -0.0021362 | -0.00036738 | 0.0012711 | -0.0015211 | -0.0033923 | -11.1923 | 64.6179 | -58.374 | 64.5584 | -58.0444 | -58.4015 | -58.3649 | -15.0101 | 64.6637 | -58.2596 | -58.168 | -58.136 | -58.2642 | -57.9849 | -0.17395 | -0.013733 | -0.073242 | 0.15564 | -0.16479 | -0.20142 | 0.009155 | -0.027466 | -0.05951 | 0.032043 | -122.7997 | 0.064087 | 0.21515 | -0.064087 | 0.27466 | -0.004577 | 0.32959 | 122.9324 | 0.1236 | 0.091553 | 122.9919 | 122.9233 | 122.818 | 122.8638 | -123.0057 | -122.8912 | 122.7585 | 0.032043 | 47.0078 | 43.19
548.1719 | 123.1934 | -58.2504 | 64.6317 | -0.052948 | 0.00062166 | 0.064803 | 0.06285 | -0.00026703 | -0.0018671 | -0.00055961 | 0.016968 | -0.00017945 | 0.00042723 | 0.0043322 | -0.0034287 | 0.00040152 | -0.0010425 | -11.2289 | 64.6271 | -58.3694 | 64.5538 | -58.0261 | -58.4152 | -58.3878 | -15.0742 | 64.6591 | -58.2642 | -58.1772 | -58.1497 | -58.2458 | -57.9666 | -0.11902 | -0.004578 | -0.07782 | 0.2243 | -0.13733 | -0.16479 | -0.01831 | -0.045776 | -0.013733 | 0.027466 | -122.8088 | 0.10071 | 0.28381 | 0.004577 | 0.29755 | 0.01831 | 0.34332 | 122.9233 | 0.11444 | 0.086975 | 122.9965 | 122.9233 | 122.8775 | 122.9095 | -123.0011 | -122.8958 | 122.8043 | 0.073242 | 47.0215 | 43.1763
549.1719 | 123.0469 | -58.223 | 64.6683 | -0.045319 | 0.0012625 | 0.063094 | 0.063064 | 0.0016556 | -0.00079891 | -0.0016278 | 0.02002 | 0.0013159 | -0.0010682 | -0.0059216 | -0.0025741 | -0.0010937 | -0.0023243 | -11.2381 | 64.6179 | -58.3878 | 64.5996 | -57.9758 | -58.3649 | -58.3328 | -15.0833 | 64.6774 | -58.2687 | -58.2413 | -57.8522 | -57.9575 | -57.9254 | -0.1648 | -0.050354 | -0.068665 | 0.24719 | -0.10986 | -0.14191 | 0.054931 | 0.022888 | -0.045777 | 0.009155 | -122.9095 | 0.37079 | 0.29755 | 0.2655 | 0.34332 | 0.31128 | 0.41199 | 122.9874 | 0.41656 | 0.027466 | 123.0057 | 122.9462 | 122.8409 | 122.9004 | -123.056 | -122.937 | 122.8226 | -0.018311 | 46.9849 | 43.1396
550.1719 | 123.1888 | -58.255 | 64.65 | -0.15213 | -0.00066014 | 0.06523 | 0.064132 | 0.0010148 | -0.00015811 | -0.00055961 | -0.01355 | -0.00060665 | 2.8e-08 | 0.0017688 | -0.00022431 | -0.00023928 | 0.0036571 | -11.3388 | 64.6225 | -58.4015 | 64.5538 | -58.0444 | -58.4335 | -58.3649 | -15.2069 | 64.6591 | -58.3054 | -58.2047 | -58.168 | -58.2733 | -57.9941 | -0.14648 | -0.027465 | -0.09613 | 0.21057 | -0.10986 | -0.17853 | 0.036621 | -0.032044 | -0.050354 | 0.009156 | -122.8546 | 0.086975 | 0.26093 | -0.01831 | 0.31128 | 0.032044 | 0.35705 | 122.9553 | 0.13733 | 0.10071 | 123.024 | 122.9645 | 122.8775 | 122.9141 | -123.0515 | -122.9553 | 122.8088 | 0.050354 | 46.9162 | 43.0481
551.1719 | 123.175 | -58.2275 | 64.6362 | -0.060578 | 0.00062166 | 0.063948 | 0.063064 | 0.0046464 | 5.5488e-05 | -0.0014142 | -0.0074462 | 0.00067495 | 2.8e-08 | 0.00048702 | 0.00020289 | -0.0025891 | -0.0031787 | -11.3846 | 64.6454 | -58.3832 | 64.5447 | -58.0582 | -58.4244 | -58.3878 | -15.2573 | 64.6774 | -58.2962 | -58.1955 | -58.1451 | -58.2642 | -58.0078 | -0.15564 | 0.009156 | -0.091552 | 0.16937 | -0.16022 | -0.19684 | -0.004577 | -0.041198 | -0.068665 | 0.041199 | -122.8317 | 0.082397 | 0.21973 | -0.036621 | 0.28839 | 0.032044 | 0.32501 | 122.9279 | 0.15106 | 0.10071 | 123.0286 | 122.9736 | 122.8729 | 122.905 | -123.0194 | -122.9324 | 122.7722 | 0.032043 | 46.843 | 42.9703
552.1719 | 123.1613 | -58.2596 | 64.6545 | -0.083466 | 0.0021171 | 0.061598 | 0.064986 | -5.343e-05 | 0.0015509 | -0.0014142 | 0.023071 | 3.4148e-05 | -0.00064077 | 0.002196 | 0.00020289 | -0.00088008 | -0.00082886 | -11.4441 | 64.6454 | -58.3694 | 64.5493 | -58.0627 | -58.4335 | -58.3786 | -15.3214 | 64.6591 | -58.2825 | -58.1955 | -58.1543 | -58.287 | -58.0124 | -0.10986 | -0.009155 | -0.10529 | 0.19684 | -0.11902 | -0.17395 | -0.009155 | -0.064087 | -0.022888 | 0.004578 | -122.85 | 0.10529 | 0.24719 | -0.027465 | 0.27008 | -0.004577 | 0.3067 | 122.9187 | 0.12817 | 0.086975 | 123.0148 | 122.9416 | 122.905 | 122.9187 | -123.024 | -122.937 | 122.8088 | 0.064087 | 46.8155 | 42.9382
553.1719 | 123.2025 | -58.2047 | 64.6591 | -0.052948 | -0.0010873 | 0.063094 | 0.062423 | -0.0034714 | -0.0035761 | 0.00050839 | 0.0078126 | 0.00024775 | 2.8e-08 | -0.0031446 | -0.00086511 | -0.00066648 | -0.0033923 | -11.4487 | 64.6317 | -58.3603 | 64.5905 | -57.9987 | -58.4015 | -58.3466 | -15.303 | 64.6408 | -58.255 | -58.1451 | -58.0994 | -58.223 | -57.9575 | -0.15564 | -0.027466 | -0.068665 | 0.20599 | -0.14191 | -0.19684 | 0.013733 | -0.041198 | -0.050354 | -0.018311 | -122.8043 | 0.10529 | 0.24719 | -0.01831 | 0.29755 | 0.032044 | 0.36163 | 122.9507 | 0.15564 | 0.10986 | 122.9919 | 122.8958 | 122.8363 | 122.8455 | -123.0194 | -122.9141 | 122.7951 | 0.059509 | 46.756 | 42.9016
554.1719 | 123.1659 | -58.2321 | 64.6317 | -0.075836 | -1.9142e-05 | 0.060744 | 0.061782 | -0.0017624 | 0.00026909 | 0.00029479 | 0.0078126 | -0.00082025 | -0.00021357 | 0.0034778 | -0.0010787 | -0.0010937 | 2.554e-05 | -11.5448 | 64.6225 | -58.3786 | 64.5355 | -58.0673 | -58.4473 | -58.3923 | -15.4678 | 64.682 | -58.255 | -58.1909 | -58.1589 | -58.2642 | -57.9895 | -0.14648 | -0.009155 | -0.096131 | 0.1648 | -0.16022 | -0.21515 | -0.013733 | -0.068665 | -0.022888 | 0.050354 | -122.8226 | 0.073242 | 0.24262 | -0.032043 | 0.2655 | -0.009155 | 0.31128 | 122.9141 | 0.09613 | 0.064087 | 123.0011 | 122.937 | 122.8546 | 122.9141 | -123.0103 | -122.8867 | 122.7676 | 0.041199 | 46.6873 | 42.7643
555.1719 | 123.1934 | -58.2047 | 64.6637 | -0.11398 | -0.0013009 | 0.062239 | 0.062423 | -0.0015488 | 0.00069649 | 0.0015766 | 0.0047608 | 0.0013159 | -0.00042717 | 0.0032642 | -0.0025741 | -0.0021619 | -0.00082886 | -11.5494 | 64.6408 | -58.374 | 64.5813 | -58.0307 | -58.4106 | -58.3649 | -15.4312 | 64.6729 | -58.2596 | -58.1543 | -58.1268 | -58.2367 | -57.9712 | -0.16937 | -0.022888 | -0.082397 | 0.17395 | -0.16022 | -0.20599 | 0.009155 | -0.036622 | -0.054932 | 0.009156 | -122.818 | 0.07782 | 0.23346 | -0.032043 | 0.28839 | 0.022889 | 0.34332 | 122.9553 | 0.13275 | 0.10529 | 123.0148 | 122.9324 | 122.8455 | 122.8775 | -123.0377 | -122.9233 | 122.7859 | 0.050354 | 46.6553 | 42.7734
556.1719 | 123.2025 | -58.2138 | 64.65 | -0.083466 | 0.0010489 | 0.061385 | 0.060927 | 0.0027238 | -0.00037171 | -0.00034601 | 0.010864 | 0.00067495 | 0.0012818 | -0.0059216 | -0.00086511 | -0.00088008 | -0.0023243 | -11.6089 | 64.65 | -58.3603 | 64.5767 | -58.0215 | -58.3969 | -58.3603 | -15.4953 | 64.6729 | -58.2504 | -58.168 | -58.1177 | -58.2275 | -57.9529 | -0.14648 | 0 | -0.073242 | 0.19226 | -0.14648 | -0.18311 | 0 | -0.036621 | -0.036621 | 0.022889 | -122.818 | 0.09613 | 0.26093 | -0.013733 | 0.29755 | 0.022888 | 0.33875 | 122.937 | 0.13275 | 0.082397 | 123.0103 | 122.9233 | 122.8638 | 122.8867 | -123.0103 | -122.9004 | 122.7905 | 0.045776 | 46.6049 | 42.7185
557.1719 | 123.1796 | -58.2138 | 64.65 | -0.091095 | -0.0010873 | 0.062666 | 0.06285 | 0.0035782 | -0.0020807 | 0.00093559 | -0.0074462 | 3.4148e-05 | -0.0010682 | 0.00091422 | 0.00020289 | -0.00066648 | -0.0012561 | -11.6638 | 64.6362 | -58.3694 | 64.5721 | -58.0444 | -58.4015 | -58.3603 | -15.564 | 64.6729 | -58.255 | -58.1589 | -58.136 | -58.2413 | -57.9803 | -0.15564 | -0.013733 | -0.077819 | 0.16937 | -0.14648 | -0.18768 | 0.009155 | -0.032043 | -0.041199 | 0.022889 | -122.8088 | 0.07782 | 0.23346 | -0.027466 | 0.27466 | 0.013733 | 0.32501 | 122.9416 | 0.11902 | 0.09613 | 123.0057 | 122.9279 | 122.85 | 122.8867 | -123.0194 | -122.905 | 122.7859 | 0.054931 | 46.55 | 42.6498
558.1719 | 123.1705 | -58.2138 | 64.6545 | -0.091095 | -0.0017281 | 0.063307 | 0.062423 | -0.00069423 | -0.0012261 | -0.0014142 | 0.0047608 | -0.00060665 | -0.001709 | -0.001222 | -0.00065151 | -0.0025891 | 0.0023755 | -11.7233 | 64.6408 | -58.3511 | 64.5676 | -58.0399 | -58.4106 | -58.3603 | -15.6418 | 64.6729 | -58.2504 | -58.1589 | -58.1406 | -58.2413 | -57.9666 | -0.13733 | -0.013733 | -0.086975 | 0.17395 | -0.14648 | -0.19684 | -0.009156 | -0.05951 | -0.036621 | 0.018311 | -122.8134 | 0.073242 | 0.24719 | -0.027466 | 0.28381 | 0.009155 | 0.31128 | 122.9187 | 0.10986 | 0.091552 | 122.9919 | 122.9233 | 122.8546 | 122.8867 | -123.0057 | -122.905 | 122.7814 | 0.054931 | 46.4905 | 42.572
559.1719 | 123.1796 | -58.223 | 64.6774 | -0.083466 | -0.00087374 | 0.063948 | 0.063491 | -0.0024032 | -0.00058531 | 0.0022174 | 0.026123 | 0.00067495 | 0.00064083 | -0.0020764 | -0.00043791 | -0.0019483 | -0.0010425 | -11.7828 | 64.6317 | -58.374 | 64.5493 | -58.0399 | -58.4335 | -58.3786 | -15.7104 | 64.7049 | -58.255 | -58.1726 | -58.1543 | -58.2458 | -57.9758 | -0.15106 | -0.045776 | -0.12817 | 0.1831 | -0.15564 | -0.21057 | -0.004578 | -0.05951 | -0.032044 | 0.027466 | -122.85 | 0.068664 | 0.24719 | -0.022889 | 0.27924 | 0.009155 | 0.33417 | 122.9233 | 0.10071 | 0.082398 | 123.0057 | 122.9599 | 122.8546 | 122.9279 | -123.0515 | -122.9324 | 122.7722 | 0.050354 | 46.4401 | 42.5125
560.1719 | 123.1613 | -58.2504 | 64.6545 | -0.045319 | 0.00040806 | 0.063094 | 0.062636 | 0.00251 | 5.5488e-05 | -0.0018414 | 0.001709 | -0.0010339 | 0.0021362 | 0.0075366 | -0.00022431 | -2.5678e-05 | -0.0018971 | -11.8332 | 64.6408 | -58.3694 | 64.5447 | -58.049 | -58.4473 | -58.3878 | -15.7837 | 64.6957 | -58.2642 | -58.168 | -58.1406 | -58.2642 | -57.9895 | -0.11902 | -0.013733 | -0.10986 | 0.20142 | -0.13733 | -0.19684 | -0.01831 | -0.07782 | -0.013733 | 0.041199 | -122.8226 | 0.10986 | 0.26093 | -0.013733 | 0.27466 | 0 | 0.32044 | 122.9141 | 0.1236 | 0.09613 | 123.0103 | 122.9599 | 122.8912 | 122.9462 | -123.024 | -122.9187 | 122.7951 | 0.082397 | 46.4172 | 42.4667
561.1719 | 123.2025 | -58.2138 | 64.6545 | -0.075836 | 0.00019446 | 0.064162 | 0.064132 | -0.00090783 | -0.0012261 | -0.002055 | -0.0013428 | -0.0014613 | -0.00042717 | -0.00015378 | -0.0017197 | -0.00088008 | -0.0014697 | -11.8561 | 64.65 | -58.3603 | 64.595 | -58.0078 | -58.3878 | -58.3374 | -15.7379 | 64.6729 | -58.2687 | -58.1406 | -58.0948 | -58.2184 | -57.9391 | -0.14648 | -0.004578 | -0.059509 | 0.20599 | -0.1236 | -0.17395 | 0.022889 | -0.027465 | -0.054932 | 0.018311 | -122.7951 | 0.11902 | 0.27466 | -0.004578 | 0.32959 | 0.050354 | 0.35248 | 122.9553 | 0.17395 | 0.12817 | 123.0103 | 122.9416 | 122.8638 | 122.8867 | -123.0148 | -122.9233 | 122.8088 | 0.073242 | 46.3577 | 42.4759
562.1719 | 123.1796 | -58.1955 | 64.6683 | -0.037689 | -0.00066014 | 0.06523 | 0.063705 | -0.0038986 | 0.00026909 | -0.0022686 | -0.0043946 | 0.00088875 | 2.8e-08 | 0.003905 | 0.0014847 | -0.0025891 | -0.0046741 | -11.9019 | 64.6454 | -58.3374 | 64.5813 | -57.9895 | -58.3923 | -58.3466 | -15.8295 | 64.7003 | -58.2504 | -58.1223 | -58.1039 | -58.223 | -57.93 | -0.14191 | -0.022888 | -0.086975 | 0.20599 | -0.15106 | -0.19684 | -0.009156 | -0.054932 | -0.054931 | 0.032043 | -122.7905 | 0.091553 | 0.2655 | -0.027465 | 0.32043 | 0.027466 | 0.3479 | 122.9187 | 0.14648 | 0.12817 | 122.9828 | 122.9507 | 122.8409 | 122.8958 | -123.0057 | -122.9187 | 122.7768 | 0.073243 | 46.2936 | 42.366
563.1719 | 123.2941 | -58.1635 | 64.7461 | -0.052948 | 0.0010489 | 0.063521 | 0.061996 | 0.00080117 | -0.00058531 | -0.0014142 | -0.0043946 | 0.0013159 | -0.0032044 | 0.00027342 | -0.0021469 | -0.0013073 | -0.0012561 | -11.9247 | 64.6362 | -58.3145 | 64.6408 | -57.9529 | -58.3191 | -58.2962 | -15.8478 | 64.7003 | -58.2367 | -58.1406 | -58.0856 | -58.2184 | -58.0399 | -0.15106 | -0.10986 | -0.10529 | 0.21057 | -0.13275 | -0.15564 | 0.01831 | -0.004578 | -0.073242 | -0.045777 | -122.8867 | 0.07782 | 0.1236 | -0.054932 | 0.19684 | 0.01831 | 0.36163 | 122.9553 | 0.15106 | 0.09613 | 122.9507 | 122.937 | 122.7997 | 122.8638 | -123.0606 | -122.9828 | 122.8043 | 0.022888 | 46.2387 | 42.3157
564.1719 | 123.1613 | -58.1955 | 64.6683 | -0.083466 | 0.0014761 | 0.063734 | 0.064773 | -0.0013352 | 5.5488e-05 | 8.1188e-05 | 0.0078126 | 0.00024775 | 0.001068 | -0.0027174 | -0.00022431 | -0.0017347 | -0.0025379 | -12.0163 | 64.6408 | -58.3466 | 64.5859 | -58.0124 | -58.3969 | -58.3282 | -15.9714 | 64.682 | -58.255 | -58.1497 | -58.1085 | -58.2367 | -57.962 | -0.15106 | -0.027466 | -0.082398 | 0.18311 | -0.13275 | -0.20142 | 0.018311 | -0.050354 | -0.059509 | 0.013733 | -122.818 | 0.086975 | 0.23346 | -0.041198 | 0.29297 | 0.018311 | 0.33417 | 122.9324 | 0.14648 | 0.10529 | 122.9874 | 122.937 | 122.8363 | 122.8775 | -123.0148 | -122.9233 | 122.7814 | 0.045777 | 46.1792 | 42.2241
565.1719 | 123.1705 | -58.1909 | 64.682 | -0.075836 | 0.0027579 | 0.064162 | 0.063064 | 0.001442 | 0.0021917 | -0.0016278 | 0.0047608 | 0.00067495 | 0.0023498 | -0.0061352 | -0.0019333 | -0.00088008 | -0.00082886 | -12.0621 | 64.6454 | -58.3511 | 64.5676 | -58.017 | -58.4061 | -58.3557 | -16.008 | 64.682 | -58.2687 | -58.1543 | -58.1223 | -58.2413 | -57.9849 | -0.16022 | -0.036621 | -0.11444 | 0.17395 | -0.16479 | -0.21515 | -0.004578 | -0.054932 | -0.07782 | 0 | -122.8363 | 0.068665 | 0.20599 | -0.050354 | 0.28381 | 0.027466 | 0.33417 | 122.9187 | 0.14648 | 0.11444 | 122.9965 | 122.9507 | 122.8363 | 122.8729 | -123.0331 | -122.9507 | 122.7585 | 0.036621 | 46.1288 | 42.1829
566.1719 | 123.1842 | -58.1955 | 64.6729 | -0.12161 | 0.0012625 | 0.064803 | 0.063064 | -0.001976 | 0.00069649 | -0.00077341 | 0.001709 | 0.0017431 | 0.00085443 | 0.0019824 | -0.0019333 | -0.0023755 | -0.0025379 | -12.1307 | 64.6591 | -58.3557 | 64.5905 | -58.0215 | -58.4152 | -58.3511 | -16.0721 | 64.7003 | -58.2321 | -58.1589 | -58.1177 | -58.2504 | -57.9529 | -0.16022 | -0.013733 | -0.082398 | 0.17395 | -0.15564 | -0.21973 | 0.004578 | -0.059509 | -0.036621 | 0.027465 | -122.8317 | 0.07782 | 0.24262 | -0.054931 | 0.27924 | -0.01831 | 0.33417 | 122.9462 | 0.11444 | 0.073242 | 123.0148 | 122.9324 | 122.8546 | 122.8958 | -123.0286 | -122.905 | 122.7859 | 0.036621 | 46.0648 | 42.1234
567.1719 | 123.1201 | -58.2184 | 64.7049 | -0.098725 | -0.00044654 | 0.063094 | 0.062636 | -0.0030442 | 0.00048269 | 0.003072 | 0.065796 | 0.0011023 | 0.0014954 | -0.00058098 | -0.00086511 | -0.0025891 | -0.0029651 | -12.1994 | 64.65 | -58.3557 | 64.5447 | -58.0444 | -58.4473 | -58.3969 | -16.1133 | 64.7049 | -58.2596 | -58.1772 | -58.1726 | -58.3145 | -58.0215 | -0.13733 | -0.054932 | -0.16022 | 0.17395 | -0.17853 | -0.22888 | -0.041199 | -0.091553 | -0.041199 | 0 | -122.8821 | 0.045777 | 0.19684 | -0.09613 | 0.23804 | -0.054931 | 0.31128 | 122.9004 | 0.086976 | 0.082398 | 123.0057 | 122.9645 | 122.8683 | 122.9233 | -123.0606 | -122.9645 | 122.7631 | 0.041199 | 46.019 | 42.1051
568.1719 | 123.1659 | -58.1818 | 64.7049 | -0.10635 | -0.0010873 | 0.064162 | 0.063277 | -0.0051804 | 0.00091009 | -0.0022686 | -0.025757 | -0.0021021 | -0.0019226 | 0.001128 | -0.00022431 | -0.0019483 | -0.0021107 | -12.2406 | 64.682 | -58.3603 | 64.5676 | -58.0261 | -58.4061 | -58.3511 | -16.1911 | 64.7186 | -58.255 | -58.1451 | -58.1223 | -58.2458 | -57.9712 | -0.17853 | -0.022888 | -0.13733 | 0.15564 | -0.16937 | -0.2243 | 0.009156 | -0.045776 | -0.073242 | 0.013733 | -122.85 | 0.05951 | 0.21057 | -0.064087 | 0.28381 | 0.009155 | 0.33417 | 122.9279 | 0.13275 | 0.10986 | 123.0423 | 122.9736 | 122.8638 | 122.9004 | -123.0652 | -122.9599 | 122.7493 | 0.036621 | 45.9412 | 41.9907
569.1719 | 123.2025 | -58.1818 | 64.6866 | -0.075836 | -0.0013009 | 0.062239 | 0.063705 | 0.00080117 | -0.00015811 | -0.00077341 | 0.0047608 | 3.4148e-05 | 0.00021363 | -0.0025036 | 0.00063009 | -0.00045288 | 0.0021619 | -12.2498 | 64.6637 | -58.3328 | 64.6225 | -57.9666 | -58.3649 | -58.3099 | -16.1545 | 64.7049 | -58.2047 | -58.1039 | -58.0765 | -58.1863 | -57.9208 | -0.15106 | -0.022888 | -0.064086 | 0.21515 | -0.12817 | -0.18311 | 0.022888 | -0.032043 | -0.022888 | 0.018311 | -122.7905 | 0.10529 | 0.26093 | -0.004577 | 0.28381 | 0.018311 | 0.36621 | 122.9553 | 0.12817 | 0.10071 | 122.9965 | 122.9095 | 122.8455 | 122.8867 | -123.0194 | -122.8912 | 122.8043 | 0.07782 | 45.932 | 42.0273
570.1719 | 123.1705 | -58.1635 | 64.682 | 0.00045798 | -1.9142e-05 | 0.064375 | 0.061141 | -0.0026168 | -0.00015811 | -0.00055961 | 0.056641 | 0.0011023 | 0.00021363 | 0.003905 | -0.0030013 | -0.0025891 | 0.0019483 | -12.2864 | 64.6912 | -58.3099 | 64.6454 | -57.9346 | -58.3466 | -58.1131 | -16.4932 | 64.7141 | -58.2367 | -58.1314 | -58.0994 | -58.2413 | -57.9529 | -0.14648 | 0.009155 | -0.036621 | 0.22888 | 0.050354 | -0.18311 | 0.19684 | -0.036621 | -0.073242 | 0.032043 | -122.8134 | 0.064087 | 0.21057 | -0.07782 | 0.28381 | -0.004578 | 0.37537 | 122.9553 | 0.13733 | 0.10529 | 123.0011 | 122.9507 | 122.8546 | 122.8775 | -122.9919 | -122.9187 | 122.8088 | 0.032043 | 45.8771 | 41.6702
571.1719 | 123.1613 | -58.1818 | 64.7186 | -0.068207 | -1.9142e-05 | 0.062666 | 0.061996 | -0.0011214 | -0.00015811 | 0.0020038 | 0.013916 | -0.0014613 | 0.00085443 | 0.0017688 | -0.0019333 | -0.0028027 | 0.0036571 | -12.3642 | 64.6591 | -58.3099 | 64.6179 | -57.9483 | -58.374 | -58.3191 | -16.2598 | 64.7186 | -58.2092 | -58.1039 | -58.0765 | -58.1863 | -57.93 | -0.12817 | -0.059509 | -0.10071 | 0.23346 | -0.13733 | -0.19226 | -0.009155 | -0.064086 | -0.027466 | 0 | -122.8226 | 0.10529 | 0.25177 | -0.004577 | 0.27924 | 0.022889 | 0.36163 | 122.9279 | 0.13275 | 0.10529 | 122.9691 | 122.9279 | 122.8409 | 122.9004 | -123.0286 | -122.9279 | 122.7997 | 0.07782 | 45.8176 | 41.922
572.1719 | 123.1659 | -58.1863 | 64.6729 | -0.13687 | 0.0014761 | 0.065443 | 0.0652 | 0.0020828 | -0.0012261 | -0.00055961 | 0.02002 | -0.0016749 | 0.0019226 | 0.001128 | -0.00065151 | -0.0028027 | -0.0021107 | -12.4237 | 64.682 | -58.3466 | 64.6133 | -57.9849 | -58.3603 | -58.3054 | -16.3422 | 64.7049 | -58.223 | -58.1177 | -58.0765 | -58.1955 | -57.93 | -0.16022 | 0.009155 | -0.05951 | 0.20142 | -0.11902 | -0.17395 | 0.041199 | -0.013733 | -0.036621 | 0.032043 | -122.7905 | 0.10986 | 0.25635 | -0.009156 | 0.29297 | 0.027465 | 0.36163 | 122.9599 | 0.14648 | 0.10528 | 123.0286 | 122.9279 | 122.8683 | 122.8912 | -123.0194 | -122.8958 | 122.7997 | 0.068664 | 45.7626 | 41.8442
573.1719 | 123.1842 | -58.1726 | 64.6912 | -0.045319 | 0.00083526 | 0.063307 | 0.063491 | -0.00026703 | -0.00037171 | -0.0012006 | -0.0074462 | 0.00067495 | 0.0029906 | -0.0037854 | 0.00020289 | -0.0015211 | 0.00088014 | -12.4603 | 64.6683 | -58.342 | 64.6179 | -57.9712 | -58.3649 | -58.3145 | -16.3651 | 64.7186 | -58.2047 | -58.1085 | -58.0673 | -58.1909 | -57.9346 | -0.16937 | -0.022888 | -0.073242 | 0.20142 | -0.14191 | -0.19226 | 0.027466 | -0.022888 | -0.032044 | 0.027466 | -122.7997 | 0.10529 | 0.23804 | -0.018311 | 0.27008 | 0.013733 | 0.37079 | 122.9599 | 0.13733 | 0.09613 | 123.0103 | 122.9233 | 122.8409 | 122.8912 | -123.0331 | -122.8958 | 122.7905 | 0.064086 | 45.7123 | 41.8076
574.1719 | 123.1888 | -58.1726 | 64.7186 | -0.045319 | -0.0027963 | 0.065016 | 0.063491 | 0.0010148 | -0.0018671 | 0.00093559 | -0.016602 | 0.0019567 | 0.001709 | 0.0024096 | 0.0012711 | -0.0030163 | -0.0010425 | -12.5153 | 64.682 | -58.3145 | 64.6088 | -57.9895 | -58.3649 | -58.3054 | -16.452 | 64.7186 | -58.2047 | -58.1085 | -58.0856 | -58.1863 | -57.9254 | -0.14191 | -0.036621 | -0.10986 | 0.1831 | -0.13275 | -0.19226 | 0.009155 | -0.050354 | -0.032044 | 0 | -122.8271 | 0.086975 | 0.24719 | -0.013733 | 0.27924 | 0.018311 | 0.32501 | 122.9233 | 0.11902 | 0.09613 | 122.9965 | 122.9233 | 122.8546 | 122.8912 | -123.0331 | -122.9233 | 122.7814 | 0.064086 | 45.6573 | 41.7206
575.1719 | 123.1476 | -58.1818 | 64.7095 | -0.060578 | 0.0029715 | 0.062453 | 0.063277 | 0.0010148 | -0.0022943 | -0.0016278 | -0.0013428 | -0.0016749 | 0.00021363 | -0.0048536 | -0.00022431 | -0.0010937 | -0.0029651 | -12.5748 | 64.6683 | -58.3237 | 64.6225 | -57.9849 | -58.3557 | -58.2962 | -16.507 | 64.6957 | -58.2275 | -58.1223 | -58.0765 | -58.2138 | -57.93 | -0.14191 | -0.041199 | -0.086975 | 0.19684 | -0.11444 | -0.17395 | 0.027465 | -0.032044 | -0.045776 | -0.013733 | -122.8317 | 0.10529 | 0.25177 | -0.032043 | 0.29755 | 0.013733 | 0.33875 | 122.9462 | 0.15106 | 0.10529 | 122.9919 | 122.9233 | 122.85 | 122.8775 | -123.0331 | -122.937 | 122.8043 | 0.05951 | 45.607 | 41.6748
576.1719 | 123.1613 | -58.168 | 64.7369 | -0.091095 | 0.00040806 | 0.064375 | 0.063491 | -0.00026703 | -0.0029351 | -0.00098701 | -0.016602 | 0.00024775 | 0.0025634 | -0.00229 | -0.0019333 | -0.00023928 | -0.0025379 | -12.5977 | 64.7003 | -58.3282 | 64.6408 | -57.9254 | -58.3145 | -58.287 | -16.5436 | 64.7232 | -58.2047 | -58.1131 | -58.0994 | -58.2047 | -57.9346 | -0.16022 | -0.036621 | -0.09613 | 0.24262 | -0.11902 | -0.14648 | 0.041199 | 0.013733 | -0.036621 | -0.013732 | -122.85 | 0.068665 | 0.23346 | -0.036621 | 0.27008 | 0 | 0.40283 | 122.9691 | 0.10529 | 0.091553 | 123.0286 | 122.9279 | 122.8683 | 122.8912 | -123.0652 | -122.9416 | 122.8088 | 0.054932 | 45.5704 | 41.6245
577.1719 | 123.1705 | -58.1635 | 64.7095 | -0.22842 | 0.0014761 | 0.063948 | 0.062423 | 0.00080117 | -0.0018671 | 0.0022174 | -0.01355 | 0.00067495 | 0.0025634 | 0.00027342 | 0.00041649 | -0.0023755 | -0.0038197 | -12.5702 | 64.6729 | -58.3282 | 64.6454 | -57.9163 | -58.3328 | -58.3145 | -16.5619 | 64.7141 | -58.1909 | -58.1131 | -58.0856 | -58.1863 | -57.9208 | -0.16479 | -0.036621 | -0.064087 | 0.24719 | -0.15106 | -0.16937 | 0.013733 | -0.004578 | -0.027466 | 0.004577 | -122.8226 | 0.07782 | 0.24262 | -0.022888 | 0.27008 | 0.004578 | 0.41199 | 122.9736 | 0.10529 | 0.07782 | 123.0011 | 122.905 | 122.8363 | 122.8775 | -123.0377 | -122.9004 | 122.8088 | 0.050354 | 45.5933 | 41.6016
578.1719 | 123.23 | -58.1726 | 64.7141 | -0.037689 | 0.00040806 | 0.063094 | 0.063064 | -0.0030442 | -0.0012261 | 0.0022174 | 0.02002 | 0.0021703 | -0.0023498 | -0.0033582 | -0.00022431 | -0.0021619 | 0.00088014 | -12.6938 | 64.6729 | -58.2962 | 64.65 | -57.9254 | -58.342 | -58.2733 | -16.5894 | 64.7186 | -58.1863 | -58.0811 | -58.0444 | -58.1635 | -57.8979 | -0.1236 | -0.041198 | -0.064087 | 0.24719 | -0.10071 | -0.16937 | 0.022889 | -0.045776 | -0.013733 | 0.004578 | -122.7951 | 0.12817 | 0.27466 | 0.009155 | 0.28839 | 0.022888 | 0.37079 | 122.9462 | 0.14191 | 0.10529 | 122.9691 | 122.905 | 122.8455 | 122.8912 | -123.0103 | -122.9004 | 122.8226 | 0.091552 | 45.4788 | 41.5833
579.1719 | 123.1567 | -58.1451 | 64.7232 | -0.060578 | 0.00083526 | 0.065016 | 0.064559 | -0.00048063 | -0.0014399 | -0.0014142 | -0.0074462 | 0.0017431 | -0.0027772 | -0.0018628 | -0.0017197 | -0.00023928 | -0.0014697 | -12.7304 | 64.7003 | -58.2687 | 64.6912 | -57.9163 | -58.4061 | -58.2916 | -16.6809 | 64.7232 | -58.2047 | -58.1039 | -58.0902 | -58.1863 | -57.9254 | -0.1236 | -0.022889 | -0.032044 | 0.22888 | -0.14648 | -0.26093 | -0.022888 | -0.13733 | -0.059509 | 0 | -122.8271 | 0.054932 | 0.21973 | -0.041198 | 0.27924 | 0.018311 | 0.35248 | 122.9599 | 0.11444 | 0.10071 | 122.9691 | 122.9279 | 122.8455 | 122.8683 | -122.9919 | -122.9279 | 122.8363 | 0.041199 | 45.4147 | 41.4642
580.1719 | 123.23 | -58.1497 | 64.7415 | -0.052948 | -0.00087374 | 0.061812 | 0.063064 | 0.001442 | -0.0022943 | 0.0011494 | 0.0078126 | -0.00060665 | 0.001068 | -0.003999 | -0.00065151 | -0.0019483 | 0.00023934 | -12.8265 | 64.7049 | -58.3054 | 64.6362 | -57.9254 | -58.3191 | -58.255 | -16.7038 | 64.7232 | -58.2047 | -58.0856 | -58.0444 | -58.168 | -57.9025 | -0.15564 | -0.036621 | -0.10529 | 0.2243 | -0.10529 | -0.16937 | 0.050354 | -0.013733 | -0.054932 | -0.01831 | -122.8271 | 0.10528 | 0.24719 | -0.018311 | 0.30212 | 0.036621 | 0.37994 | 122.9416 | 0.16022 | 0.11902 | 123.0103 | 122.9279 | 122.8546 | 122.8729 | -123.0469 | -122.9462 | 122.7859 | 0.064087 | 45.3232 | 41.4459
581.1719 | 123.175 | -58.1635 | 64.7049 | -0.022431 | -0.00044654 | 0.064589 | 0.063277 | 0.001442 | 0.0017645 | 0.001363 | 0.001709 | -0.00039305 | 2.8e-08 | 0.0032642 | -1.0706e-05 | -0.0021619 | -0.00082886 | -12.8448 | 64.7141 | -58.3008 | 64.6591 | -57.9117 | -58.3054 | -58.2733 | -16.4841 | 64.8148 | -58.1497 | -58.1223 | -58.0353 | -58.1635 | -57.93 | -0.13733 | 0.009155 | -0.045776 | 0.25177 | -0.10986 | -0.14191 | 0.027466 | -0.004578 | 0.013733 | 0.10986 | -122.8271 | 0.12817 | 0.23346 | 0 | 0.21973 | -0.013733 | 0.3891 | 122.9599 | 0.11444 | 0.027466 | 123.0148 | 122.9645 | 122.8775 | 122.9782 | -123.0057 | -122.8546 | 122.8226 | 0.041199 | 45.3186 | 41.6794
582.1719 | 123.1796 | -58.1406 | 64.7415 | -0.11398 | -0.00044654 | 0.063948 | 0.063491 | -0.00048063 | -0.0016535 | 0.0020038 | 0.010864 | 0.0013159 | 0.001709 | -0.00079478 | 0.0010575 | -2.5678e-05 | -0.0021107 | -12.9318 | 64.6912 | -58.3099 | 64.6317 | -57.9575 | -58.3374 | -58.2962 | -16.8732 | 64.7232 | -58.2092 | -58.0719 | -58.0627 | -58.1818 | -57.8888 | -0.16937 | -0.050354 | -0.10986 | 0.18311 | -0.15564 | -0.19684 | 0.013733 | -0.027465 | -0.068665 | -0.01831 | -122.8134 | 0.07782 | 0.25177 | -0.041199 | 0.32044 | 0.027466 | 0.35248 | 122.9416 | 0.14648 | 0.13733 | 123.0011 | 122.9324 | 122.8317 | 122.8638 | -123.0515 | -122.9507 | 122.7722 | 0.068665 | 45.2087 | 41.2674
583.1719 | 123.1979 | -58.1131 | 64.7598 | -0.052948 | -0.00023294 | 0.063521 | 0.063705 | -0.0013352 | -0.0016535 | -0.0014142 | 0.0078126 | 0.00046135 | 0.00085443 | -0.002931 | -0.00022431 | -0.00066648 | -0.0012561 | -12.9501 | 64.7186 | -58.2916 | 64.6866 | -57.8934 | -58.2962 | -58.2504 | -16.8777 | 64.7507 | -58.1818 | -58.0719 | -58.049 | -58.1451 | -57.9071 | -0.17853 | -0.041199 | -0.073243 | 0.21973 | -0.13733 | -0.18311 | 0.041199 | -0.004578 | -0.068665 | -0.009156 | -122.8317 | 0.064087 | 0.20599 | -0.032044 | 0.27466 | 0.036621 | 0.39825 | 122.9782 | 0.13275 | 0.10986 | 123.0103 | 122.9324 | 122.8317 | 122.8638 | -123.0515 | -122.9416 | 122.7997 | 0.041199 | 45.163 | 41.2354
584.1719 | 123.1705 | -58.1406 | 64.7415 | -0.11398 | -0.00023294 | 0.062666 | 0.061141 | 0.0020828 | 0.00069649 | -0.00034601 | 0.010864 | -0.00017945 | -0.0019226 | 0.00027342 | -0.0017197 | -0.0010937 | 0.0015209 | -13.0188 | 64.7095 | -58.2825 | 64.6591 | -57.8979 | -58.3099 | -58.287 | -16.9235 | 64.7461 | -58.1589 | -58.0673 | -58.0353 | -58.136 | -57.8842 | -0.14191 | -0.032043 | -0.082397 | 0.24262 | -0.14648 | -0.16937 | -0.004577 | -0.027466 | -0.018311 | 0.004578 | -122.8088 | 0.10529 | 0.25635 | 0.004578 | 0.27466 | 0.022889 | 0.38452 | 122.9416 | 0.1236 | 0.091553 | 122.9919 | 122.905 | 122.85 | 122.8867 | -123.024 | -122.9004 | 122.7997 | 0.073242 | 45.1218 | 41.217
585.1719 | 123.1567 | -58.1497 | 64.7507 | -0.091095 | -1.9142e-05 | 0.06523 | 0.063277 | -0.00090783 | -0.0010125 | -0.0012006 | -0.080688 | 0.0015295 | -0.0027772 | -0.0016492 | -0.00086511 | -0.0025891 | -0.0042469 | -13.0737 | 64.7003 | -58.2962 | 64.6729 | -57.8934 | -58.1177 | -57.9987 | -17.1432 | 64.7141 | -58.1955 | -58.1085 | -58.0536 | -58.1726 | -57.9025 | -0.14649 | -0.050354 | -0.077819 | 0.25635 | 0.15106 | 0.032043 | 0.29755 | 0.17853 | -0.045777 | -0.036621 | -122.8592 | 0.09613 | 0.24719 | -0.022888 | 0.29297 | 0.022889 | 0.40283 | 122.9691 | 0.14191 | 0.086975 | 122.9965 | 122.9095 | 122.85 | 122.8638 | -123.0469 | -122.9462 | 122.8226 | 0.041198 | 45.076 | 41.0065
586.1719 | 123.1705 | -58.1314 | 64.7278 | -0.037689 | -0.00044654 | 0.063307 | 0.063705 | -5.343e-05 | -0.0022943 | -0.0014142 | 0.013916 | -0.00017945 | -0.0010682 | -0.0065626 | -1.0706e-05 | -0.0028027 | -0.0021107 | -13.1516 | 64.7003 | -58.3191 | 64.6591 | -57.9346 | -58.3237 | -58.2916 | -17.07 | 64.7461 | -58.1955 | -58.0673 | -58.049 | -58.1818 | -57.8751 | -0.18768 | -0.027466 | -0.068664 | 0.19684 | -0.16022 | -0.19226 | 0.027466 | -0.004577 | -0.064087 | 0.018311 | -122.7951 | 0.082398 | 0.25635 | -0.050354 | 0.32043 | 0.013733 | 0.38452 | 122.9782 | 0.14648 | 0.12817 | 123.0194 | 122.9416 | 122.8317 | 122.8775 | -123.0469 | -122.9233 | 122.7905 | 0.064087 | 44.9799 | 41.0614
587.1719 | 123.2758 | -58.136 | 64.8239 | -0.052948 | 0.0010489 | 0.062239 | 0.063277 | 0.0012284 | -0.0016535 | 0.00029479 | -0.0043946 | -0.00039305 | 0.00042723 | -0.0018628 | -0.0025741 | -0.0021619 | 0.0038709 | -13.1561 | 64.7049 | -58.2596 | 64.6866 | -57.8796 | -58.2779 | -58.2413 | -17.1112 | 64.7644 | -58.1451 | -58.0811 | -58.0215 | -58.1451 | -58.0261 | -0.1236 | -0.11902 | -0.13733 | 0.25635 | -0.10529 | -0.14191 | 0.018311 | -0.01831 | -0.009156 | -0.05951 | -122.905 | 0.11444 | 0.10986 | -0.009156 | 0.11902 | 0 | 0.37994 | 122.9462 | 0.1236 | 0.064087 | 122.9645 | 122.9095 | 122.8409 | 122.9004 | -123.0835 | -122.9691 | 122.8226 | 0.054931 | 44.9799 | 41.0248
588.1719 | 123.1522 | -58.1406 | 64.7507 | -0.11398 | 0.0010489 | 0.064589 | 0.065414 | -0.00090783 | -0.00015811 | 0.0017902 | 0.023071 | 0.0011023 | 0.001709 | -0.00079478 | 0.0010575 | -0.0021619 | -0.00018806 | -13.2935 | 64.7141 | -58.3099 | 64.6317 | -57.9712 | -58.3466 | -58.3054 | -17.2348 | 64.7369 | -58.1909 | -58.0948 | -58.0582 | -58.1863 | -57.9071 | -0.16937 | -0.036621 | -0.11902 | 0.16937 | -0.1648 | -0.20599 | 0.004578 | -0.036621 | -0.050354 | -0.013733 | -122.8455 | 0.082397 | 0.23346 | -0.045776 | 0.28381 | 0.004578 | 0.33875 | 122.9416 | 0.13275 | 0.09613 | 123.024 | 122.9279 | 122.8546 | 122.8775 | -123.0606 | -122.9416 | 122.7722 | 0.045776 | 44.8471 | 40.9058
589.1719 | 123.1979 | -58.136 | 64.7507 | -0.075836 | 0.0025443 | 0.062025 | 0.064345 | -0.00069423 | -0.0025079 | 0.00050839 | 0.013916 | 0.0015295 | 0.00085443 | 0.0058276 | 0.0012711 | -0.0030163 | -0.0010425 | -13.3255 | 64.6866 | -58.2733 | 64.6683 | -57.93 | -58.3099 | -58.2687 | -17.2211 | 64.7507 | -58.1589 | -58.0582 | -58.0261 | -58.1451 | -57.8751 | -0.13733 | -0.064087 | -0.082397 | 0.20599 | -0.13275 | -0.17395 | 0.004577 | -0.036622 | -0.022889 | 0 | -122.8088 | 0.10986 | 0.26093 | -0.009156 | 0.28381 | 0.013733 | 0.34332 | 122.9416 | 0.13275 | 0.10071 | 122.9599 | 122.9095 | 122.8226 | 122.8867 | -123.024 | -122.9095 | 122.8043 | 0.077819 | 44.8105 | 40.9149
590.1719 | 123.2208 | -58.1314 | 64.7095 | -0.10635 | 0.0016899 | 0.063307 | 0.061355 | -0.004753 | 0.0021917 | -0.0012006 | -0.0013428 | -0.00060665 | -0.0010682 | 0.00027342 | -0.00086511 | -0.0040845 | -0.00018806 | -13.4079 | 64.6866 | -58.2733 | 64.6545 | -57.9391 | -58.3099 | -58.2642 | -17.3126 | 64.7369 | -58.168 | -58.0948 | -58.0215 | -58.1406 | -57.8796 | -0.14191 | -0.022889 | -0.054932 | 0.19226 | -0.13275 | -0.17853 | 0.009155 | -0.036622 | -0.036621 | 0.027465 | -122.8043 | 0.10986 | 0.25177 | -0.009155 | 0.28839 | 0.027466 | 0.33417 | 122.9279 | 0.14648 | 0.073242 | 122.9599 | 122.905 | 122.818 | 122.8683 | -122.9828 | -122.8775 | 122.7859 | 0.036621 | 44.7235 | 40.8188
591.1719 | 123.1522 | -58.1268 | 64.7598 | -0.11398 | -0.00044654 | 0.064162 | 0.062636 | -0.00026703 | 0.0011237 | 0.003072 | 0.010864 | 0.0021703 | -0.00085457 | -0.0025036 | -0.0017197 | -0.0023755 | 0.0021619 | -13.4583 | 64.7095 | -58.2962 | 64.6408 | -57.9346 | -58.3237 | -58.287 | -17.4042 | 64.7507 | -58.1772 | -58.0765 | -58.0399 | -58.1726 | -57.8888 | -0.16937 | -0.050354 | -0.11902 | 0.19226 | -0.16022 | -0.19684 | 0.009156 | -0.027465 | -0.050354 | -0.009156 | -122.8363 | 0.086975 | 0.23804 | -0.045776 | 0.28839 | 0.004578 | 0.36163 | 122.937 | 0.13733 | 0.10071 | 123.0057 | 122.9279 | 122.8363 | 122.8775 | -123.056 | -122.937 | 122.7676 | 0.050354 | 44.6686 | 40.7227
592.1719 | 123.1842 | -58.1223 | 64.7552 | -0.13687 | 0.00083526 | 0.063734 | 0.061568 | 0.0010148 | 0.00048269 | -0.0012006 | 0.013916 | 0.00046135 | 0.00064083 | -0.00036738 | 0.0019119 | -0.0030163 | -0.0023243 | -13.472 | 64.7324 | -58.2687 | 64.682 | -57.8979 | -58.2779 | -58.2458 | -17.3721 | 64.7415 | -58.1497 | -58.0353 | -58.0078 | -58.1268 | -57.8522 | -0.14648 | -0.022888 | -0.073242 | 0.2243 | -0.1236 | -0.15564 | 0.022888 | -0.009155 | -0.027466 | -0.013733 | -122.7905 | 0.11444 | 0.27008 | -0.004578 | 0.29755 | 0.022888 | 0.37079 | 122.9507 | 0.14191 | 0.11444 | 123.0011 | 122.8912 | 122.8546 | 122.8638 | -123.024 | -122.905 | 122.8043 | 0.086975 | 44.6503 | 40.7501
593.1719 | 123.1705 | -58.1635 | 64.7552 | -0.037689 | 0.00083526 | 0.062666 | 0.063918 | -0.0028304 | 5.5488e-05 | 8.1188e-05 | -0.016602 | 0.0025975 | 2.8e-08 | 0.0019824 | -0.00043791 | -0.0013073 | 0.00045294 | -13.5727 | 64.7186 | -58.3054 | 64.6133 | -57.9758 | -58.3511 | -58.2962 | -17.5598 | 64.7598 | -58.1772 | -58.1039 | -58.0673 | -58.1909 | -57.9071 | -0.14191 | -0.036621 | -0.14191 | 0.18768 | -0.13275 | -0.18768 | 0.009155 | -0.045776 | -0.013733 | 0.004578 | -122.8592 | 0.09613 | 0.25635 | -0.027466 | 0.27008 | -0.013733 | 0.32959 | 122.9187 | 0.10986 | 0.073242 | 123.024 | 122.937 | 122.8821 | 122.9233 | -123.0606 | -122.9324 | 122.7768 | 0.059509 | 44.5908 | 40.6036
594.1719 | 123.1384 | -58.1451 | 64.7461 | -0.11398 | 0.0012625 | 0.064375 | 0.064559 | -0.0021896 | 0.00091009 | -0.003764 | 0.001709 | 0.00024775 | 0.0019226 | 0.003905 | -0.00043791 | -0.0034437 | -0.0048877 | -13.591 | 64.7369 | -58.2825 | 64.6637 | -57.9254 | -58.3237 | -58.2733 | -17.5461 | 64.7507 | -58.168 | -58.049 | -58.0124 | -58.1589 | -57.8842 | -0.13733 | -0.009156 | -0.082398 | 0.21973 | -0.12817 | -0.17853 | 0.009156 | -0.041198 | -0.022888 | 0.004577 | -122.7951 | 0.13275 | 0.26093 | -0.013733 | 0.28381 | 0.009155 | 0.35706 | 122.9462 | 0.15564 | 0.11902 | 123.0194 | 122.9187 | 122.8821 | 122.8958 | -123.0286 | -122.9141 | 122.8088 | 0.096131 | 44.5541 | 40.5991
595.1719 | 123.1705 | -58.1497 | 64.7552 | 0.13016 | 0.0016899 | 0.064803 | 0.063491 | 0.0010148 | -0.00058531 | -0.0014142 | 0.0047608 | -0.0010339 | 0.0019226 | 0.0015552 | -0.00065151 | -0.0013073 | -0.0036059 | -13.6917 | 64.7003 | -58.2825 | 64.5996 | -58.0032 | -58.3832 | -58.3191 | -17.7109 | 64.7736 | -58.1955 | -58.0948 | -58.0948 | -58.2138 | -57.9208 | -0.13275 | -0.054932 | -0.15564 | 0.14648 | -0.16937 | -0.23346 | -0.036621 | -0.10071 | -0.045777 | 0.018311 | -122.85 | 0.054931 | 0.22888 | -0.064087 | 0.27466 | -0.01831 | 0.27924 | 122.8821 | 0.10071 | 0.10071 | 122.9828 | 122.9691 | 122.85 | 122.9233 | -123.0377 | -122.9507 | 122.7493 | 0.054931 | 44.458 | 40.4388
596.1719 | 123.1384 | -58.1543 | 64.7507 | -0.068207 | 0.0016899 | 0.061598 | 0.064132 | 0.0010148 | -0.0012261 | -0.00098701 | 0.001709 | 0.00046135 | 0.00085443 | 0.0064684 | 0.0010575 | -0.00023928 | 0.0010937 | -13.7421 | 64.7232 | -58.3145 | 64.5767 | -58.017 | -58.4061 | -58.3466 | -17.8116 | 64.7736 | -58.1863 | -58.1223 | -58.0948 | -58.2047 | -57.9391 | -0.16022 | -0.027465 | -0.17395 | 0.13733 | -0.19226 | -0.25177 | -0.032044 | -0.091553 | -0.032043 | 0.022889 | -122.8729 | 0.059509 | 0.21515 | -0.050354 | 0.24719 | -0.018311 | 0.29755 | 122.8912 | 0.091552 | 0.064087 | 123.0377 | 122.9599 | 122.8775 | 122.9279 | -123.0652 | -122.937 | 122.731 | 0.032044 | 44.4122 | 40.3427
597.1719 | 123.1522 | -58.1085 | 64.769 | -0.15213 | -0.0021555 | 0.064589 | 0.063918 | -0.001976 | 5.5488e-05 | -0.00077341 | 0.016968 | 0.0017431 | 2.8e-08 | 0.00070062 | -0.00043791 | -0.0013073 | -0.0046741 | -13.7421 | 64.7369 | -58.287 | 64.6408 | -57.962 | -58.3237 | -58.2825 | -17.8207 | 64.7736 | -58.1772 | -58.0811 | -58.0536 | -58.1772 | -57.8796 | -0.17853 | -0.032044 | -0.12817 | 0.14649 | -0.17395 | -0.21515 | 0.004577 | -0.036621 | -0.068664 | 0.004578 | -122.85 | 0.054932 | 0.22888 | -0.068664 | 0.29755 | 0 | 0.32501 | 122.9279 | 0.1236 | 0.09613 | 123.024 | 122.9507 | 122.8455 | 122.8821 | -123.056 | -122.9462 | 122.7493 | 0.027466 | 44.3665 | 40.2878
598.1719 | 123.1476 | -58.1543 | 64.7552 | -0.091095 | -0.00087374 | 0.062239 | 0.062636 | 0.00058737 | -0.00079891 | -0.0014142 | 0.013916 | 0.00046135 | -0.0023498 | -0.0033582 | -0.0015061 | -0.0021619 | 0.0010937 | -13.7924 | 64.7415 | -58.2596 | 64.6317 | -57.962 | -58.3649 | -58.2962 | -17.9123 | 64.7827 | -58.1589 | -58.1039 | -58.049 | -58.1726 | -57.8934 | -0.10529 | -0.013733 | -0.1236 | 0.19226 | -0.14191 | -0.21057 | -0.036621 | -0.10529 | -0.004578 | 0.027466 | -122.8592 | 0.10529 | 0.26093 | -0.01831 | 0.2655 | -0.013732 | 0.29755 | 122.8912 | 0.10986 | 0.054932 | 123.0011 | 122.9416 | 122.8958 | 122.937 | -123.0148 | -122.9141 | 122.7859 | 0.050354 | 44.3619 | 40.242
599.1719 | 123.1338 | -58.1497 | 64.7507 | -0.052948 | 0.00019446 | 0.064803 | 0.063277 | -0.001976 | -0.00058531 | 8.1188e-05 | -0.01355 | 0.00046135 | 0.00085443 | -0.00229 | -0.00065151 | -0.00088008 | -0.0025379 | -13.8519 | 64.7186 | -58.2779 | 64.6271 | -57.9849 | -58.3649 | -58.3145 | -17.9718 | 64.7644 | -58.168 | -58.0902 | -58.0627 | -58.1772 | -57.9025 | -0.12817 | -0.032043 | -0.1236 | 0.16479 | -0.1648 | -0.21515 | -0.036621 | -0.086975 | -0.018311 | 0.013733 | -122.8409 | 0.086975 | 0.24719 | -0.027466 | 0.2655 | -0.009155 | 0.29297 | 122.905 | 0.10529 | 0.07782 | 122.9965 | 122.9324 | 122.8683 | 122.9141 | -123.0286 | -122.9187 | 122.7768 | 0.059509 | 44.2978 | 40.1779
600.1719 | 123.1338 | -58.1406 | 64.7552 | -0.075836 | -0.0015145 | 0.065657 | 0.062636 | 0.0010148 | -0.0012261 | -0.00034601 | 0.026123 | 0.00046135 | 0.001068 | -0.00058098 | -0.00065151 | -0.0019483 | 0.0034435 | -13.884 | 64.7415 | -58.2733 | 64.5996 | -57.9712 | -58.3282 | -58.3008 | -18.0725 | 64.7598 | -58.1818 | -58.1039 | -58.0719 | -58.2092 | -57.9071 | -0.13275 | -0.013733 | -0.15564 | 0.16937 | -0.16022 | -0.18768 | -0.027466 | -0.054932 | -0.041199 | 0.004578 | -122.8592 | 0.068665 | 0.23346 | -0.068665 | 0.27466 | -0.027466 | 0.30212 | 122.8729 | 0.10986 | 0.07782 | 123.0148 | 122.9416 | 122.8821 | 122.9004 | -123.0286 | -122.937 | 122.7402 | 0.036621 | 44.2566 | 40.0681
601.1719 | 123.1842 | -58.1177 | 64.7507 | -0.060578 | -0.00044654 | 0.06288 | 0.063918 | 0.0035782 | -0.00079891 | -0.00077341 | 0.029175 | 3.4148e-05 | 0.0021362 | 0.00048702 | -0.00022431 | -0.0015211 | -0.0044605 | -13.9481 | 64.7278 | -58.2596 | 64.6454 | -57.9483 | -58.3237 | -58.2504 | -18.1412 | 64.7827 | -58.1772 | -58.0765 | -58.0353 | -58.1406 | -57.8888 | -0.14191 | -0.022888 | -0.10528 | 0.16937 | -0.13275 | -0.20599 | 0.009156 | -0.064086 | -0.059509 | 0.032044 | -122.8271 | 0.082398 | 0.22888 | -0.022888 | 0.28839 | 0.036621 | 0.31128 | 122.905 | 0.14191 | 0.10071 | 122.9874 | 122.9599 | 122.8455 | 122.9004 | -123.0103 | -122.9279 | 122.7631 | 0.041199 | 44.1696 | 39.9765
602.1719 | 123.1384 | -58.1223 | 64.769 | -0.052948 | 0.00019446 | 0.062453 | 0.06285 | -0.001976 | -0.0014399 | 0.0015766 | -0.0043946 | -0.00060665 | -0.00085457 | 0.003905 | -1.0706e-05 | -0.00045288 | 2.554e-05 | -14.0121 | 64.7186 | -58.2779 | 64.6454 | -57.9529 | -58.3282 | -58.2779 | -18.2419 | 64.7827 | -58.1726 | -58.0627 | -58.0353 | -58.168 | -57.8796 | -0.15564 | -0.050354 | -0.1236 | 0.16937 | -0.15564 | -0.20599 | 0 | -0.050354 | -0.050354 | 0.013733 | -122.8317 | 0.086975 | 0.24261 | -0.045777 | 0.29297 | 0.004577 | 0.32501 | 122.9233 | 0.13733 | 0.10986 | 122.9965 | 122.9553 | 122.8409 | 122.905 | -123.0469 | -122.9416 | 122.7676 | 0.059509 | 44.1101 | 39.8804
603.1719 | 123.1018 | -58.1314 | 64.801 | -0.068207 | -0.00044654 | 0.063307 | 0.066695 | -0.0021896 | 0.0013373 | 0.002431 | -0.041016 | 0.0021703 | -0.00021357 | 0.0017688 | -0.0027877 | -0.0028027 | -0.00018806 | -14.035 | 64.7919 | -58.2687 | 64.6042 | -57.9941 | -58.3649 | -58.3237 | -18.338 | 64.8239 | -58.1543 | -58.1085 | -58.0994 | -58.2458 | -57.9391 | -0.13733 | -0.009155 | -0.19684 | 0.13733 | -0.19226 | -0.23346 | -0.054931 | -0.09613 | -0.022888 | 0.022889 | -122.9095 | 0.032044 | 0.19226 | -0.11444 | 0.21515 | -0.091553 | 0.27466 | 122.8729 | 0.054932 | 0.045776 | 123.0606 | 122.9782 | 122.9233 | 122.9553 | -123.0698 | -122.9553 | 122.7356 | 0.022888 | 44.0964 | 39.7934
604.1719 | 123.1476 | -58.0948 | 64.7507 | -0.060578 | -1.9142e-05 | 0.064803 | 0.063705 | 0.00037377 | 0.00091009 | -0.0029096 | 0.0078126 | 0.0030249 | 0.001068 | 0.0015552 | -0.00022431 | -0.0025891 | -0.0018971 | -14.0671 | 64.7415 | -58.2642 | 64.6912 | -57.9071 | -58.2825 | -58.2413 | -18.2785 | 64.7873 | -58.1497 | -58.0353 | -57.9987 | -58.1314 | -57.8705 | -0.16937 | -0.009155 | -0.059509 | 0.18768 | -0.14648 | -0.18768 | 0.022888 | -0.018311 | -0.054931 | 0.036621 | -122.7859 | 0.096131 | 0.22431 | -0.036621 | 0.27924 | 0.01831 | 0.35706 | 122.9553 | 0.15106 | 0.11444 | 123.0057 | 122.937 | 122.8363 | 122.8821 | -123.0148 | -122.9004 | 122.786 | 0.05951 | 44.0277 | 39.8163
605.1719 | 123.1384 | -58.1039 | 64.7644 | -0.083466 | 0.0010489 | 0.064375 | 0.061996 | -0.00069423 | 5.5488e-05 | 0.0011494 | -0.0074462 | -0.0016749 | 0.00042723 | 0.001128 | -1.0706e-05 | -0.0015211 | -0.0033923 | -14.1861 | 64.7461 | -58.255 | 64.6179 | -57.9529 | -58.342 | -58.2916 | -18.4525 | 64.7781 | -58.1497 | -58.0948 | -58.0444 | -58.1909 | -57.8934 | -0.15106 | -0.01831 | -0.14648 | 0.15106 | -0.18768 | -0.23804 | -0.036621 | -0.086975 | -0.045776 | 0.013733 | -122.8592 | 0.059509 | 0.21057 | -0.086975 | 0.25635 | -0.041199 | 0.30212 | 122.8729 | 0.10528 | 0.054931 | 123.0011 | 122.9279 | 122.85 | 122.8821 | -123.0194 | -122.9141 | 122.7219 | 0.009155 | 43.9178 | 39.6515
606.1719 | 123.1338 | -58.1177 | 64.7827 | -0.1445 | 0.0014761 | 0.064589 | 0.061141 | 0.0012284 | 0.00048269 | -0.00098701 | -0.0043946 | -0.0012477 | 0.001709 | -0.0027174 | -0.00043791 | -0.0025891 | -0.00082886 | -14.2456 | 64.7461 | -58.2275 | 64.6179 | -57.962 | -58.3145 | -58.2962 | -18.5532 | 64.7736 | -58.168 | -58.0719 | -58.0399 | -58.1772 | -57.8979 | -0.10986 | -0.036621 | -0.16479 | 0.15564 | -0.17853 | -0.19684 | -0.068665 | -0.086975 | -0.050354 | -0.009155 | -122.8546 | 0.07782 | 0.21973 | -0.059509 | 0.27008 | -0.009155 | 0.2655 | 122.8455 | 0.12817 | 0.096131 | 122.9736 | 122.9416 | 122.8638 | 122.8912 | -123.0103 | -122.9507 | 122.7356 | 0.045777 | 43.8721 | 39.5645
607.1719 | 123.1567 | -58.0811 | 64.7964 | -0.091095 | -0.00023294 | 0.063734 | 0.062636 | -0.0028304 | -0.0018671 | -0.00013241 | 0.041382 | -0.00082025 | 0.0023498 | -0.0037854 | -0.00065151 | -0.0013073 | 0.0019483 | -14.2593 | 64.7186 | -58.2321 | 64.682 | -57.9025 | -58.3008 | -58.2458 | -18.5715 | 64.7919 | -58.1589 | -58.0353 | -58.0078 | -58.1223 | -57.8476 | -0.15106 | -0.07782 | -0.11444 | 0.17853 | -0.16479 | -0.21973 | -0.013733 | -0.068664 | -0.07782 | -0.004578 | -122.8317 | 0.073243 | 0.23346 | -0.041198 | 0.31128 | 0.036622 | 0.32959 | 122.9141 | 0.15106 | 0.1236 | 122.9507 | 122.9507 | 122.7997 | 122.8729 | -123.0286 | -122.9553 | 122.7631 | 0.045777 | 43.8217 | 39.5096
608.1719 | 123.056 | -58.1177 | 64.8148 | -0.045319 | 0.00040806 | 0.06288 | 0.064559 | 0.0018692 | -0.00015811 | 0.00050839 | -0.092895 | 0.00067495 | 0.00021363 | 0.0081774 | -0.0017197 | -0.00023928 | -0.0023243 | -14.3143 | 64.769 | -58.2916 | 64.6317 | -57.9803 | -58.3786 | -58.3603 | -18.7683 | 64.8285 | -58.1497 | -58.1406 | -58.1543 | -58.2596 | -57.93 | -0.17395 | -0.045776 | -0.1831 | 0.13733 | -0.24261 | -0.26093 | -0.068665 | -0.086975 | -0.032043 | 0.013733 | -122.9553 | -0.036621 | 0.18768 | -0.14191 | 0.21973 | -0.10986 | 0.31128 | 122.9233 | -0.004578 | 0.009155 | 123.0606 | 122.9782 | 122.8867 | 122.9462 | -123.1064 | -122.9645 | 122.7493 | -0.022888 | 43.8034 | 39.3494
609.1719 | 123.1796 | -58.1039 | 64.7736 | -0.068207 | -0.0019417 | 0.063521 | 0.063705 | 0.001442 | -0.0010125 | -0.00098701 | 0.03833 | 0.00067495 | 0.0025634 | 0.0032642 | -0.00043791 | -0.0017347 | -0.0055287 | -14.3417 | 64.7644 | -58.2367 | 64.6774 | -57.9117 | -58.3008 | -58.2504 | -18.8049 | 64.7827 | -58.1314 | -58.049 | -58.017 | -58.1406 | -57.8476 | -0.13275 | -0.009156 | -0.096131 | 0.19226 | -0.14648 | -0.19684 | -0.013733 | -0.064087 | -0.027466 | 0.009155 | -122.8226 | 0.086975 | 0.25635 | -0.036621 | 0.28381 | -0.009155 | 0.32501 | 122.9141 | 0.11444 | 0.082398 | 123.0011 | 122.9141 | 122.8683 | 122.8867 | -123.0103 | -122.905 | 122.7814 | 0.054932 | 43.7622 | 39.299
610.1719 | 123.1476 | -58.0994 | 64.7827 | -0.075836 | 0.00040806 | 0.063948 | 0.063277 | -5.343e-05 | -0.0014399 | -0.00077341 | 0.0078126 | -0.0012477 | 2.8e-08 | 0.0015552 | -0.00086511 | -0.0028027 | -0.00018806 | -14.3921 | 64.7507 | -58.2321 | 64.6729 | -57.9163 | -58.3145 | -58.2367 | -18.8736 | 64.7964 | -58.1131 | -58.0444 | -58.0124 | -58.1543 | -57.8476 | -0.13275 | -0.032044 | -0.10986 | 0.1831 | -0.13733 | -0.21515 | -0.004577 | -0.082397 | -0.013733 | 0.013733 | -122.8271 | 0.086975 | 0.25177 | -0.054932 | 0.2655 | -0.041199 | 0.31586 | 122.905 | 0.10071 | 0.068664 | 122.9828 | 122.9095 | 122.85 | 122.8958 | -123.0148 | -122.8958 | 122.7722 | 0.054931 | 43.7073 | 39.2258
611.1719 | 123.1796 | -58.0994 | 64.7964 | -0.052948 | 0.0010489 | 0.062666 | 0.061141 | -0.001976 | -0.00058531 | 0.0015766 | 0.0078126 | 3.4148e-05 | 0.00064083 | 0.002196 | -0.0010787 | -0.0017347 | -0.0033923 | -14.4608 | 64.7644 | -58.2504 | 64.6637 | -57.9254 | -58.3099 | -58.2596 | -18.9789 | 64.7827 | -58.1406 | -58.049 | -58.0078 | -58.1314 | -57.8796 | -0.15106 | -0.032044 | -0.13275 | 0.17395 | -0.16022 | -0.21057 | -0.009156 | -0.05951 | -0.041199 | -0.013733 | -122.8455 | 0.091553 | 0.21973 | -0.032044 | 0.26093 | 0.009155 | 0.32501 | 122.9141 | 0.13275 | 0.091553 | 123.0148 | 122.9233 | 122.8638 | 122.8821 | -123.0469 | -122.937 | 122.7631 | 0.050354 | 43.6386 | 39.1205
612.1719 | 123.1384 | -58.0902 | 64.801 | -0.075836 | -0.00023294 | 0.064589 | 0.061996 | 0.00016017 | -0.00037171 | 0.00029479 | 0.023071 | 0.00067495 | 0.00064083 | -0.0067762 | -0.0019333 | -0.00088008 | 0.0015209 | -14.5248 | 64.769 | -58.223 | 64.6774 | -57.9117 | -58.3054 | -58.2596 | -19.0796 | 64.7873 | -58.1543 | -58.049 | -58.0261 | -58.1451 | -57.8567 | -0.13275 | -0.032043 | -0.1236 | 0.17853 | -0.16937 | -0.21515 | -0.036622 | -0.082398 | -0.064087 | -0.013733 | -122.85 | 0.064087 | 0.23346 | -0.054932 | 0.29755 | 0.009155 | 0.31128 | 122.9004 | 0.12817 | 0.10529 | 122.9919 | 122.9416 | 122.8592 | 122.8775 | -123.024 | -122.9553 | 122.7676 | 0.041199 | 43.5654 | 39.0106
613.1719 | 123.0698 | -58.0948 | 64.8193 | -0.48782 | 0.0023307 | 0.06288 | 0.066054 | -0.0015488 | -0.00015811 | -0.0039776 | -0.089844 | -0.00060665 | 0.00085443 | 0.0071094 | -0.0010787 | 0.0014697 | -0.0016833 | -14.5981 | 64.769 | -58.2596 | 64.6591 | -57.93 | -58.342 | -58.2962 | -19.2123 | 64.8331 | -58.1451 | -58.0811 | -58.1039 | -58.2275 | -57.9117 | -0.16479 | -0.050354 | -0.16022 | 0.16479 | -0.20142 | -0.24719 | -0.036621 | -0.082397 | -0.050354 | 0.013733 | -122.9004 | -0.009155 | 0.18311 | -0.13275 | 0.23346 | -0.082397 | 0.32959 | 122.9187 | 0.041199 | 0.064087 | 123.0286 | 122.9782 | 122.8638 | 122.9279 | -123.0789 | -122.9645 | 122.7539 | 0.013733 | 43.4967 | 38.8824
614.1719 | 123.143 | -58.0902 | 64.7827 | -0.083466 | -0.00087374 | 0.064803 | 0.061782 | -0.003685 | 0.0013373 | -0.002696 | 0.044434 | -0.00039305 | 0.00042723 | -0.00058098 | 0.0016983 | -0.00023928 | 0.00066654 | -14.621 | 64.7598 | -58.2321 | 64.6683 | -57.93 | -58.3282 | -58.2504 | -19.3497 | 64.7873 | -58.1223 | -58.0582 | -58.0215 | -58.1406 | -57.8659 | -0.14191 | -0.022888 | -0.11444 | 0.16022 | -0.16022 | -0.23804 | -0.01831 | -0.09613 | -0.032043 | 0.004577 | -122.8409 | 0.068665 | 0.2243 | -0.050354 | 0.25635 | -0.018311 | 0.30212 | 122.9004 | 0.10071 | 0.064086 | 122.9919 | 122.9095 | 122.85 | 122.8775 | -123.0148 | -122.905 | 122.7585 | 0.032043 | 43.4692 | 38.7405
615.1719 | 123.1659 | -58.0627 | 64.7964 | -0.12924 | -0.00087374 | 0.06523 | 0.063705 | 0.001442 | 0.00091009 | -0.0018414 | 0.029175 | 3.4148e-05 | 0.0012818 | 0.0028368 | -0.0015061 | -0.0023755 | 0.0013073 | -14.6439 | 64.7827 | -58.2275 | 64.6866 | -57.8705 | -58.2825 | -58.2367 | -19.3817 | 64.801 | -58.1223 | -58.0261 | -57.9941 | -58.1177 | -57.8384 | -0.16479 | -0.013733 | -0.10986 | 0.19226 | -0.17395 | -0.21973 | -0.009155 | -0.054932 | -0.059509 | 0.004577 | -122.8226 | 0.068664 | 0.2243 | -0.054932 | 0.28381 | 0.004577 | 0.35706 | 122.9141 | 0.12817 | 0.09613 | 123.0103 | 122.9233 | 122.8455 | 122.8638 | -123.024 | -122.9187 | 122.7493 | 0.036621 | 43.4189 | 38.681
616.1719 | 123.1476 | -58.1039 | 64.7964 | -0.075836 | 0.0019035 | 0.063734 | 0.06285 | 0.00037377 | -0.00058531 | 0.0020038 | 0.010864 | 0.00024775 | 2.8e-08 | -0.00464 | 0.00041649 | -0.0019483 | 0.0017345 | -14.7812 | 64.7781 | -58.223 | 64.6317 | -57.9391 | -58.3099 | -58.2825 | -19.6014 | 64.801 | -58.1451 | -58.0582 | -58.0353 | -58.1772 | -57.8659 | -0.11902 | -0.018311 | -0.16479 | 0.16479 | -0.17853 | -0.20599 | -0.05951 | -0.086976 | -0.041199 | 0.004577 | -122.8546 | 0.068665 | 0.23804 | -0.073242 | 0.27924 | -0.032043 | 0.28381 | 122.8546 | 0.10986 | 0.086975 | 123.0011 | 122.9462 | 122.8821 | 122.905 | -123.0194 | -122.9416 | 122.7356 | 0.045776 | 43.3228 | 38.5025
617.1719 | 123.1201 | -58.0994 | 64.8056 | -0.052948 | 0.0021171 | 0.063307 | 0.063491 | 0.0012284 | 0.0017645 | -0.0033368 | 0.0078126 | 0.0011023 | -0.00085457 | -0.0035718 | -0.0038559 | 0.00061532 | -0.0012561 | -14.8087 | 64.7552 | -58.2275 | 64.7369 | -57.8293 | -58.342 | -58.3328 | -19.7571 | 64.7919 | -58.1543 | -58.0719 | -58.0719 | -58.1772 | -57.9071 | -0.12817 | -0.050354 | -0.068665 | 0.27008 | -0.23346 | -0.24262 | -0.10529 | -0.11444 | -0.054932 | -0.013733 | -122.8775 | 0.027466 | 0.19226 | -0.07782 | 0.24719 | -0.022888 | 0.39825 | 122.9645 | 0.082398 | 0.082398 | 122.9828 | 122.9462 | 122.8546 | 122.8912 | -123.0331 | -122.9599 | 122.8363 | 0.027466 | 43.2907 | 38.3423
618.1719 | 123.0606 | -58.0948 | 64.8193 | -0.091095 | 0.00083526 | 0.065016 | 0.066268 | 0.00037377 | -0.0022943 | -0.0012006 | -0.08374 | 0.0038793 | 0.00021363 | 0.007323 | -0.00043791 | -0.0010937 | -0.0029651 | -14.8178 | 64.8102 | -58.2458 | 64.65 | -57.9391 | -58.3466 | -58.3145 | -19.812 | 64.8285 | -58.1406 | -58.0811 | -58.1177 | -58.2275 | -57.9208 | -0.15106 | -0.009155 | -0.16937 | 0.15564 | -0.21973 | -0.25177 | -0.068664 | -0.10071 | -0.045776 | 0.009155 | -122.9004 | -0.022888 | 0.17395 | -0.13275 | 0.21973 | -0.086975 | 0.3067 | 122.8958 | 0.022888 | 0.059509 | 123.056 | 122.9691 | 122.905 | 122.9233 | -123.0652 | -122.9599 | 122.7448 | 0.013733 | 43.277 | 38.2828
619.1719 | 123.1567 | -58.0765 | 64.8102 | -0.12924 | 0.0012625 | 0.064375 | 0.062636 | -0.0013352 | -0.00079891 | 8.1188e-05 | 0.029175 | 0.00024775 | -0.0010682 | -0.0082716 | -0.00022431 | -0.0015211 | -0.00040166 | -14.9185 | 64.7781 | -58.2092 | 64.6683 | -57.9208 | -58.3099 | -58.2367 | -19.8853 | 64.8376 | -58.136 | -58.0399 | -58.0032 | -58.1268 | -57.843 | -0.13275 | -0.032044 | -0.14191 | 0.15564 | -0.16022 | -0.23346 | -0.027465 | -0.10071 | -0.059509 | 0.027465 | -122.85 | 0.073242 | 0.23346 | -0.050354 | 0.29297 | 0.009155 | 0.28839 | 122.8775 | 0.13275 | 0.09613 | 122.9874 | 122.9736 | 122.8546 | 122.9141 | -123.0194 | -122.9462 | 122.7448 | 0.036621 | 43.158 | 38.1912
620.1719 | 123.1247 | -58.0856 | 64.7919 | -0.12924 | -0.00066014 | 0.064162 | 0.063277 | 0.00016017 | -0.0033625 | -0.002055 | 0.001709 | 0.00067495 | 0.003418 | -0.0018628 | -0.00043791 | -0.0013073 | -0.0012561 | -14.9734 | 64.7827 | -58.2321 | 64.6591 | -57.9117 | -58.3237 | -58.2367 | -19.9448 | 64.7964 | -58.136 | -58.0399 | -58.017 | -58.1451 | -57.8522 | -0.14649 | -0.009155 | -0.13275 | 0.17395 | -0.15106 | -0.23804 | -0.004577 | -0.091552 | -0.050354 | 0.004578 | -122.8317 | 0.068664 | 0.23346 | -0.05951 | 0.28381 | -0.009156 | 0.32044 | 122.8912 | 0.11902 | 0.09613 | 123.0148 | 122.9324 | 122.8683 | 122.8821 | -123.024 | -122.9279 | 122.7448 | 0.045776 | 43.1122 | 38.1409
621.1719 | 123.1293 | -58.1039 | 64.8239 | -0.10635 | -0.00044654 | 0.063094 | 0.064132 | 0.00016017 | 0.00048269 | 0.0015766 | 0.001709 | 0.00067495 | 0.0019226 | 0.0030506 | -0.0021469 | -0.00088008 | -0.0023243 | -15.0101 | 64.7736 | -58.2458 | 64.6362 | -57.93 | -58.3191 | -58.2504 | -20.0684 | 64.8193 | -58.1085 | -58.0353 | -58.0261 | -58.1451 | -57.8659 | -0.14191 | -0.050354 | -0.18768 | 0.17395 | -0.14648 | -0.21515 | -0.004577 | -0.073242 | -0.004578 | -0.004578 | -122.8592 | 0.07782 | 0.23804 | -0.041199 | 0.24262 | -0.036621 | 0.31586 | 122.8821 | 0.082398 | 0.073243 | 123.0194 | 122.9279 | 122.8775 | 122.9233 | -123.0698 | -122.9324 | 122.7402 | 0.068665 | 43.0939 | 38.0356
622.1719 | 123.1064 | -58.0765 | 64.8102 | -0.091095 | -0.0019417 | 0.064375 | 0.064773 | 0.0018692 | -0.00037171 | 0.0020038 | 0.035278 | 0.00046135 | 0.001709 | 0.0017688 | -0.00086511 | -0.0019483 | -0.00082886 | -15.065 | 64.8056 | -58.2367 | 64.6545 | -57.9208 | -58.3099 | -58.2092 | -20.2194 | 64.8285 | -58.1177 | -58.0719 | -58.0582 | -58.1772 | -57.8888 | -0.16022 | -0.004578 | -0.15564 | 0.15564 | -0.13275 | -0.23346 | 0.027465 | -0.073243 | -0.041199 | 0.01831 | -122.8821 | 0.01831 | 0.18768 | -0.10071 | 0.22888 | -0.059509 | 0.31586 | 122.8912 | 0.059509 | 0.045777 | 123.0423 | 122.9462 | 122.8821 | 122.905 | -123.0469 | -122.9279 | 122.731 | 0.004578 | 43.0115 | 37.8571
623.1719 | 123.111 | -58.0719 | 64.8331 | -0.098725 | 0.00062166 | 0.065016 | 0.063491 | -0.0028304 | -0.0014399 | -0.0012006 | -0.016602 | -0.0012477 | 0.00042723 | -0.0031446 | 0.0023391 | -0.0042981 | 0.0025891 | -15.1199 | 64.7598 | -58.2001 | 64.6729 | -57.9391 | -58.3191 | -58.255 | -20.2789 | 64.8239 | -58.1314 | -58.0582 | -58.0582 | -58.2047 | -57.8842 | -0.12817 | -0.073242 | -0.16022 | 0.13275 | -0.18311 | -0.24719 | -0.054932 | -0.11902 | -0.05951 | -0.009155 | -122.8912 | 0.013732 | 0.18768 | -0.13275 | 0.24719 | -0.073242 | 0.26093 | 122.8729 | 0.073242 | 0.073242 | 122.9599 | 122.9553 | 122.8317 | 122.8958 | -123.0331 | -122.9645 | 122.7448 | 0.013732 | 42.952 | 37.793
624.1719 | 123.1567 | -58.049 | 64.801 | -0.12924 | -0.00044654 | 0.064162 | 0.063277 | -0.0024032 | 0.0017645 | -0.00077341 | 0.010864 | 0.00046135 | 0.00021363 | -0.0020764 | -0.0030013 | -0.0030163 | -0.0010425 | -15.1474 | 64.8102 | -58.2275 | 64.6683 | -57.8934 | -58.3054 | -58.2321 | -20.3156 | 64.8285 | -58.1085 | -58.0261 | -58.0032 | -58.1406 | -57.8567 | -0.17853 | 0.009156 | -0.13275 | 0.15564 | -0.18311 | -0.25635 | -0.004578 | -0.07782 | -0.05951 | 0.027466 | -122.8271 | 0.045776 | 0.19226 | -0.091553 | 0.25177 | -0.032043 | 0.33417 | 122.8958 | 0.10529 | 0.082398 | 123.0377 | 122.937 | 122.8592 | 122.8775 | -123.0286 | -122.9095 | 122.7173 | 0.022888 | 42.9016 | 37.7335
625.1719 | 123.1613 | -58.0673 | 64.8148 | -0.098725 | 0.00019446 | 0.063307 | 0.061782 | -0.0028304 | -0.00015811 | 0.00029479 | 0.02002 | 0.00024775 | 0.00064083 | -0.0025036 | 0.00063009 | -0.00066648 | 0.00066654 | -15.1749 | 64.801 | -58.1818 | 64.7278 | -57.8613 | -58.2596 | -58.2047 | -20.3293 | 64.8193 | -58.0765 | -57.9987 | -57.9666 | -58.0948 | -57.811 | -0.11444 | -0.013733 | -0.086975 | 0.20599 | -0.13733 | -0.19226 | -0.022888 | -0.07782 | -0.009155 | 0.004578 | -122.8134 | 0.10071 | 0.25635 | -0.027466 | 0.2655 | -0.018311 | 0.32043 | 122.9095 | 0.10986 | 0.07782 | 122.9828 | 122.8958 | 122.8683 | 122.8867 | -122.9965 | -122.8912 | 122.7951 | 0.068665 | 42.8925 | 37.738
626.1719 | 123.1476 | -58.0673 | 64.8376 | -0.091095 | 0.0012625 | 0.063521 | 0.064132 | -0.0011214 | 0.00048269 | 0.001363 | 0.0078126 | 0.00046135 | 0.00085443 | -0.0067762 | -0.0017197 | -0.0030163 | -0.00040166 | -15.2893 | 64.8102 | -58.2001 | 64.6729 | -57.9117 | -58.2504 | -58.2275 | -20.4071 | 64.8285 | -58.1177 | -58.0261 | -57.9941 | -58.1451 | -57.8339 | -0.13275 | -0.027465 | -0.16479 | 0.15564 | -0.16022 | -0.18311 | -0.027466 | -0.050354 | -0.050354 | -0.009155 | -122.8638 | 0.073242 | 0.23346 | -0.07782 | 0.28381 | -0.027466 | 0.28839 | 122.8729 | 0.1236 | 0.091553 | 123.0103 | 122.9462 | 122.8775 | 122.8958 | -123.0377 | -122.9553 | 122.7402 | 0.041199 | 42.778 | 37.6602
627.1719 | 123.143 | -58.049 | 64.8697 | -0.083466 | -0.0010873 | 0.063521 | 0.064132 | 0.0018692 | -0.00015811 | 0.00072199 | 0.010864 | -0.00082025 | 0.0019226 | -0.00036738 | -0.00086511 | -0.0025891 | -0.0021107 | -15.2756 | 64.8056 | -58.2001 | 64.7369 | -57.8522 | -58.2413 | -58.168 | -20.4254 | 64.8422 | -58.0765 | -57.9895 | -57.9391 | -58.0811 | -57.8156 | -0.15106 | -0.064087 | -0.13275 | 0.19684 | -0.11902 | -0.19226 | 0.032043 | -0.041199 | -0.027466 | -0.027466 | -122.8592 | 0.10986 | 0.23346 | -0.032044 | 0.26093 | -0.004578 | 0.3479 | 122.937 | 0.13733 | 0.086975 | 123.0057 | 122.9187 | 122.8546 | 122.8912 | -123.0698 | -122.9462 | 122.7859 | 0.059509 | 42.7734 | 37.6236
628.1719 | 123.143 | -58.0627 | 64.8376 | -0.098725 | 0.0016899 | 0.063094 | 0.062423 | 0.0020828 | 5.5488e-05 | 0.001363 | -0.028809 | -0.00039305 | 0.0012818 | -0.0037854 | -0.0015061 | -0.0013073 | 0.0032299 | -15.3625 | 64.7919 | -58.1955 | 64.7644 | -57.756 | -58.2779 | -58.2825 | -20.5948 | 64.8285 | -58.0811 | -58.017 | -58.0124 | -58.1497 | -57.8384 | -0.13275 | -0.045776 | -0.073242 | 0.3067 | -0.21973 | -0.21515 | -0.086975 | -0.082397 | -0.018311 | -0.009155 | -122.8546 | 0.050354 | 0.2243 | -0.086975 | 0.24262 | -0.068664 | 0.43945 | 122.9599 | 0.068665 | 0.064087 | 122.9874 | 122.9095 | 122.8546 | 122.8912 | -123.0331 | -122.9187 | 122.8271 | 0.045776 | 42.7002 | 37.468
629.1719 | 123.1201 | -58.049 | 64.856 | -0.083466 | 0.00083526 | 0.061385 | 0.063064 | -0.001976 | -0.00015811 | 0.00050839 | -0.028809 | 0.0013159 | -0.0019226 | 0.0028368 | -0.0017197 | -0.0017347 | -0.0023243 | -15.4312 | 64.7873 | -58.1863 | 64.7095 | -57.8705 | -58.0811 | -58.1543 | -20.7092 | 64.8697 | -58.0948 | -58.0261 | -58.0078 | -58.136 | -57.8384 | -0.13733 | -0.068665 | -0.14648 | 0.17853 | -0.10529 | -0.032044 | 0.032043 | 0.10529 | -0.045777 | 0.013733 | -122.8821 | 0.041199 | 0.21057 | -0.086975 | 0.25635 | -0.041198 | 0.31586 | 122.8958 | 0.086976 | 0.068665 | 122.9736 | 122.9645 | 122.8363 | 122.9187 | -123.0423 | -122.9507 | 122.7585 | 0.022888 | 42.6178 | 37.3398
630.1719 | 123.1384 | -58.0353 | 64.8468 | -0.083466 | 0.0012625 | 0.06288 | 0.063277 | -0.00048063 | -0.00015811 | 8.1188e-05 | 0.016968 | -0.00017945 | -0.0010682 | 0.0015552 | -0.00086511 | -0.0015211 | -0.0012561 | -15.4907 | 64.8056 | -58.168 | 64.7186 | -57.8476 | -58.2504 | -58.168 | -20.7413 | 64.8376 | -58.0856 | -57.9895 | -57.962 | -58.0856 | -57.7927 | -0.13275 | -0.041199 | -0.12817 | 0.18768 | -0.13275 | -0.21515 | 0 | -0.082397 | -0.050354 | -0.009156 | -122.8363 | 0.073242 | 0.24261 | -0.050354 | 0.29297 | 0 | 0.32044 | 122.8867 | 0.1236 | 0.09613 | 122.9736 | 122.9233 | 122.8409 | 122.8729 | -123.0148 | -122.9324 | 122.7539 | 0.045776 | 42.5446 | 37.294
631.1719 | 123.1476 | -58.0307 | 64.8193 | -0.052948 | 0.0019035 | 0.064375 | 0.061996 | -0.0032578 | -0.0014399 | -0.0012006 | -0.0013428 | 0.0019567 | 0.001068 | -0.0042126 | -0.00065151 | -0.0034437 | -0.0016833 | -15.564 | 64.8193 | -58.1772 | 64.7141 | -57.8522 | -58.2596 | -58.2047 | -20.9015 | 64.8468 | -58.0627 | -57.9941 | -57.9666 | -58.0765 | -57.8018 | -0.14648 | 0 | -0.10529 | 0.17853 | -0.17395 | -0.22888 | -0.027466 | -0.082398 | -0.032043 | 0.027466 | -122.8134 | 0.064087 | 0.22888 | -0.045776 | 0.26093 | -0.013733 | 0.32501 | 122.8912 | 0.09613 | 0.068664 | 122.9965 | 122.9095 | 122.85 | 122.8775 | -122.9965 | -122.8821 | 122.7448 | 0.036621 | 42.4667 | 37.1292
632.1719 | 123.1476 | -58.0627 | 64.8468 | -0.13687 | -0.0023691 | 0.065016 | 0.062636 | 0.00058737 | -0.0010125 | -0.00013241 | 0.0078126 | 0.00024775 | -0.00085457 | 0.0030506 | 0.00041649 | -0.0019483 | 0.00066654 | -15.6418 | 64.801 | -58.1772 | 64.7232 | -57.8842 | -58.2458 | -58.2138 | -21.0388 | 64.8376 | -58.0765 | -57.9895 | -57.9666 | -58.0811 | -57.811 | -0.11444 | -0.045777 | -0.1236 | 0.17853 | -0.15106 | -0.18311 | -0.036621 | -0.068665 | -0.013733 | -0.009156 | -122.8363 | 0.09613 | 0.25177 | -0.018311 | 0.2655 | -0.004578 | 0.29297 | 122.9004 | 0.10986 | 0.086975 | 122.9782 | 122.9141 | 122.8638 | 122.9004 | -123.024 | -122.9233 | 122.786 | 0.073242 | 42.421 | 37.0239
633.1719 | 123.1476 | -58.0307 | 64.8697 | -0.15976 | 0.00062166 | 0.062453 | 0.062423 | -0.001976 | 5.5488e-05 | -0.00098701 | 0.010864 | -0.00060665 | -0.0025636 | 0.0026232 | 0.00063009 | -2.5678e-05 | 0.00066654 | -15.6738 | 64.8148 | -58.1955 | 64.7324 | -57.8659 | -58.2687 | -58.1818 | -21.1624 | 64.8468 | -58.0811 | -57.9849 | -57.9483 | -58.0673 | -57.7789 | -0.16479 | -0.054932 | -0.13733 | 0.16479 | -0.15106 | -0.23804 | 0.013733 | -0.073242 | -0.050354 | -0.022888 | -122.8546 | 0.082398 | 0.25177 | -0.036621 | 0.30212 | 0.013733 | 0.32959 | 122.9279 | 0.13275 | 0.096131 | 123.0103 | 122.9279 | 122.8455 | 122.8775 | -123.0652 | -122.9507 | 122.7631 | 0.045777 | 42.3569 | 36.8683
634.1719 | 123.1705 | -58.0353 | 64.8651 | -0.091095 | 0.00062166 | 0.062453 | 0.061568 | -0.003685 | -0.0016535 | 0.00029479 | -0.0043946 | -0.00017945 | -0.00021357 | 0.0045458 | -0.00065151 | -0.0013073 | -0.00018806 | -15.7059 | 64.8193 | -58.1589 | 64.7781 | -57.7972 | -58.2047 | -58.1543 | -21.1761 | 64.8376 | -58.0627 | -57.9346 | -57.9208 | -58.017 | -57.7744 | -0.1236 | -0.045776 | -0.086975 | 0.23804 | -0.11902 | -0.16937 | 0.004578 | -0.045776 | -0.027466 | -0.027466 | -122.7997 | 0.11444 | 0.26093 | 0.01831 | 0.28839 | 0.045776 | 0.36163 | 122.937 | 0.14191 | 0.12817 | 122.9782 | 122.9004 | 122.8546 | 122.8729 | -123.024 | -122.9279 | 122.8134 | 0.10071 | 42.3294 | 36.8591
635.1719 | 123.1293 | -58.017 | 64.8743 | -0.10635 | 0.0012625 | 0.059889 | 0.063277 | -0.00090783 | 0.00026909 | 0.00029479 | 0.0047608 | -0.0012477 | 0.00064083 | 0.001128 | 0.00063009 | -0.0025891 | 0.00088014 | -15.7654 | 64.8468 | -58.1772 | 64.7232 | -57.8476 | -58.2458 | -58.1909 | -21.3959 | 64.8788 | -58.0719 | -57.9712 | -57.962 | -58.0765 | -57.8018 | -0.16022 | -0.027466 | -0.15106 | 0.16937 | -0.17395 | -0.22888 | -0.013733 | -0.068665 | -0.054931 | 0.004577 | -122.8455 | 0.054932 | 0.21515 | -0.059509 | 0.27008 | -0.004578 | 0.32959 | 122.9004 | 0.10986 | 0.10071 | 123.024 | 122.9507 | 122.8638 | 122.8958 | -123.0515 | -122.9462 | 122.7402 | 0.045777 | 42.2516 | 36.6211
636.1719 | 123.143 | -58.0399 | 64.8468 | -0.10635 | 0.00062166 | 0.063094 | 0.063918 | 0.00037377 | -0.00079891 | 0.00029479 | 0.001709 | -0.0010339 | -0.00021357 | -0.0042126 | -0.0017197 | -0.0015211 | -0.0018971 | -15.8295 | 64.8239 | -58.1589 | 64.7186 | -57.8659 | -58.2687 | -58.1818 | -21.5424 | 64.8514 | -58.0948 | -57.9849 | -57.962 | -58.0902 | -57.8064 | -0.11902 | -0.022888 | -0.12817 | 0.17395 | -0.14191 | -0.22888 | -0.022888 | -0.10986 | -0.054932 | 0.004577 | -122.8317 | 0.07782 | 0.23346 | -0.050354 | 0.28839 | 0.004578 | 0.29297 | 122.8775 | 0.13275 | 0.10986 | 122.9828 | 122.9462 | 122.8638 | 122.8912 | -123.0057 | -122.9416 | 122.7585 | 0.054932 | 42.2104 | 36.4975
637.1719 | 123.1613 | -58.0124 | 64.8285 | -0.091095 | 0.00062166 | 0.063094 | 0.062636 | -0.00069423 | -0.0012261 | -0.00077341 | 0.026123 | -0.00039305 | 0.0012818 | 0.00048702 | -0.0027877 | -0.0032301 | -0.0036059 | -15.8386 | 64.8514 | -58.1497 | 64.7736 | -57.8064 | -58.223 | -58.1589 | -21.5927 | 64.8788 | -58.0536 | -57.9391 | -57.9117 | -58.0261 | -57.7606 | -0.13733 | 0.022888 | -0.054931 | 0.20599 | -0.14648 | -0.21057 | -0.009156 | -0.073242 | -0.041199 | 0.050354 | -122.7676 | 0.10071 | 0.25177 | -0.013733 | 0.29297 | 0.027466 | 0.34332 | 122.9233 | 0.14191 | 0.11444 | 123.0011 | 122.9324 | 122.8638 | 122.8912 | -122.9782 | -122.8821 | 122.786 | 0.073242 | 42.1738 | 36.4197
638.1719 | 123.1659 | -58.0627 | 64.8651 | 0.053863 | 0.00062166 | 0.064589 | 0.063277 | 0.00016017 | -0.0014399 | 0.0015766 | -0.0074462 | -0.00082025 | -0.0014954 | -0.00229 | 0.00084389 | -0.0028027 | -0.00061526 | -15.9439 | 64.8285 | -58.168 | 64.6866 | -57.8796 | -58.2733 | -58.2001 | -21.8079 | 64.8697 | -58.0902 | -58.0032 | -57.9666 | -58.0994 | -57.8018 | -0.10529 | -0.036621 | -0.17853 | 0.18311 | -0.13733 | -0.21057 | -0.032043 | -0.10528 | -0.027466 | 0.004578 | -122.8683 | 0.09613 | 0.26093 | -0.036621 | 0.28839 | -0.009155 | 0.28839 | 122.8546 | 0.1236 | 0.086975 | 122.9965 | 122.9599 | 122.8912 | 122.9324 | -123.0331 | -122.9553 | 122.7493 | 0.059509 | 42.1188 | 36.2549
639.1719 | 123.1659 | -58.0032 | 64.8605 | -0.068207 | 0.0014761 | 0.064375 | 0.064559 | -0.0041122 | -0.00058531 | -0.00034601 | -0.03186 | 0.0011023 | -0.0023498 | 0.0034778 | -1.0706e-05 | -0.0017347 | 0.0028027 | -16.0172 | 64.8331 | -58.1863 | 64.7644 | -57.8247 | -58.2092 | -58.1635 | -21.8536 | 64.8834 | -58.0536 | -57.9575 | -57.93 | -58.0399 | -57.7835 | -0.18311 | -0.027466 | -0.096131 | 0.17853 | -0.16022 | -0.20599 | 0.022888 | -0.022889 | -0.050354 | 0.022888 | -122.818 | 0.073242 | 0.21973 | -0.036621 | 0.27008 | 0.013733 | 0.36163 | 122.9507 | 0.1236 | 0.096131 | 123.0194 | 122.937 | 122.8363 | 122.8867 | -123.0469 | -122.9141 | 122.7676 | 0.045777 | 41.9861 | 36.1496
640.1719 | 123.1888 | -57.9987 | 64.8834 | -0.052948 | 0.0012625 | 0.063734 | 0.064132 | 0.0022964 | -0.0014399 | 0.00093559 | 0.001709 | 3.4148e-05 | 2.8e-08 | 0.0058276 | -0.00086511 | -0.0010937 | 0.0023755 | -16.04 | 64.8239 | -58.1177 | 64.801 | -57.7606 | -58.1818 | -58.1314 | -21.9131 | 64.856 | -58.0353 | -57.9163 | -57.8705 | -58.0124 | -57.7469 | -0.11902 | -0.059509 | -0.082398 | 0.23804 | -0.13275 | -0.18311 | -0.013733 | -0.064087 | -0.036621 | -0.027466 | -122.7997 | 0.12817 | 0.25177 | -0.013733 | 0.28839 | 0.022888 | 0.35706 | 122.9187 | 0.16479 | 0.11902 | 122.9416 | 122.8912 | 122.8226 | 122.8546 | -123.0011 | -122.9187 | 122.7997 | 0.082397 | 41.9586 | 36.0855
641.1719 | 123.1705 | -58.0307 | 64.8468 | -0.098725 | -0.00087374 | 0.063307 | 0.063064 | -0.0021896 | 0.00048269 | -0.0022686 | -0.010498 | 0.0017431 | 2.8e-08 | 0.0019824 | -0.00022431 | -0.0021619 | -0.0014697 | -16.0812 | 64.8743 | -58.1451 | 64.801 | -57.7744 | -58.1955 | -58.1085 | -22.0184 | 64.8697 | -58.0307 | -57.93 | -57.8934 | -58.0032 | -57.7377 | -0.11444 | 0.027466 | -0.045777 | 0.25635 | -0.07782 | -0.16479 | 0.036621 | -0.050354 | 0 | 0.022888 | -122.7768 | 0.13733 | 0.29297 | 0.027466 | 0.29297 | 0.027466 | 0.37079 | 122.9462 | 0.13733 | 0.10071 | 123.0194 | 122.9004 | 122.905 | 122.9004 | -122.9919 | -122.8775 | 122.8317 | 0.10071 | 41.9495 | 36.0123
642.1719 | 123.1247 | -58.0261 | 64.8926 | -0.098725 | 0.0027579 | 0.063734 | 0.063277 | -0.00090783 | -0.00015811 | -0.00055961 | -0.022705 | 0.0011023 | -0.00085457 | 0.00091422 | -1.0706e-05 | -0.00088008 | -0.0014697 | -16.214 | 64.8285 | -58.1635 | 64.7278 | -57.8476 | -58.2504 | -58.1863 | -22.2702 | 64.8788 | -58.0811 | -57.9575 | -57.9437 | -58.0627 | -57.7835 | -0.13733 | -0.064087 | -0.16479 | 0.17853 | -0.16022 | -0.2243 | -0.022888 | -0.086975 | -0.054932 | -0.013733 | -122.85 | 0.082397 | 0.24262 | -0.036621 | 0.29755 | 0.018311 | 0.31586 | 122.8912 | 0.13733 | 0.1236 | 122.9919 | 122.9599 | 122.8546 | 122.905 | -123.056 | -122.9736 | 122.7539 | 0.068665 | 41.8121 | 35.7559
643.1719 | 123.1705 | -57.9941 | 64.8788 | -0.098725 | -1.9142e-05 | 0.063948 | 0.06285 | 0.00058737 | 5.5488e-05 | -0.002696 | -0.01355 | 0.00046135 | 0.0032044 | 0.0024096 | -0.0021469 | -0.0017347 | -0.0016833 | -16.214 | 64.8285 | -58.1131 | 64.7919 | -57.7789 | -58.1772 | -58.1223 | -22.1283 | 64.8788 | -58.0307 | -57.93 | -57.8842 | -58.0124 | -57.7423 | -0.11902 | -0.050354 | -0.086975 | 0.21515 | -0.12817 | -0.18311 | -0.009155 | -0.064087 | -0.036621 | 0 | -122.8088 | 0.10986 | 0.25177 | -0.01831 | 0.28839 | 0.018311 | 0.33417 | 122.905 | 0.14648 | 0.10071 | 122.9416 | 122.9095 | 122.8226 | 122.8729 | -122.9919 | -122.9095 | 122.7859 | 0.064087 | 41.7801 | 35.8658
644.1719 | 123.1247 | -58.0078 | 64.8834 | -0.12161 | 0.0021171 | 0.065657 | 0.064773 | -0.0062484 | -0.0022943 | -0.0012006 | 0.0047608 | -0.00082025 | -0.00085457 | -0.002931 | -1.0706e-05 | -0.0015211 | 0.0010937 | -16.3422 | 64.8468 | -58.136 | 64.7415 | -57.8247 | -58.2367 | -58.1589 | -22.2931 | 64.8972 | -58.0444 | -57.9758 | -57.9529 | -58.0536 | -57.7927 | -0.12817 | -0.036621 | -0.14191 | 0.18311 | -0.15106 | -0.22888 | -0.022889 | -0.10071 | -0.036622 | 0.013733 | -122.8592 | 0.054931 | 0.21515 | -0.045777 | 0.25177 | -0.009155 | 0.31128 | 122.8775 | 0.091553 | 0.068665 | 122.9828 | 122.9416 | 122.8546 | 122.905 | -123.0194 | -122.9279 | 122.7493 | 0.032043 | 41.6656 | 35.7147
645.1719 | 123.1293 | -58.0032 | 64.8651 | -0.11398 | 0.0016899 | 0.067152 | 0.065627 | 0.00037377 | -0.0016535 | -0.0014142 | 0.001709 | 0.00088875 | -0.00064077 | -0.0035718 | -0.0017197 | -0.00088008 | -0.0038197 | -16.2415 | 64.888 | -58.1131 | 64.7507 | -57.8064 | -58.2321 | -58.1818 | -22.3984 | 64.8788 | -58.0399 | -57.9437 | -57.9666 | -58.0673 | -57.7835 | -0.10986 | 0.022888 | -0.11444 | 0.19684 | -0.17853 | -0.22888 | -0.068665 | -0.11902 | -0.036621 | 0.013733 | -122.8088 | 0.036621 | 0.21973 | -0.064087 | 0.25635 | -0.027466 | 0.3067 | 122.8638 | 0.073242 | 0.09613 | 123.0011 | 122.9187 | 122.8912 | 122.8821 | -122.9782 | -122.905 | 122.7539 | 0.059509 | 41.7618 | 35.6049
646.1719 | 123.1888 | -57.9712 | 64.8926 | -0.022431 | 0.0010489 | 0.064803 | 0.063705 | -0.0026168 | 0.0017645 | -0.00013241 | 0.0047608 | -0.0016749 | 2.8e-08 | 0.0030506 | -0.00065151 | -0.0021619 | -0.0027515 | -16.4017 | 64.8422 | -58.1039 | 64.8331 | -57.7194 | -58.136 | -58.0627 | -22.3434 | 64.9155 | -58.0032 | -57.8751 | -57.8796 | -57.9941 | -57.7148 | -0.13275 | -0.050354 | -0.059509 | 0.25177 | -0.091553 | -0.1648 | 0.041199 | -0.032043 | -0.032044 | 0.022888 | -122.7676 | 0.091552 | 0.25635 | -0.022889 | 0.28839 | 0.009155 | 0.38452 | 122.937 | 0.1236 | 0.12817 | 122.9462 | 122.9187 | 122.8134 | 122.8867 | -122.9965 | -122.8958 | 122.8043 | 0.09613 | 41.5695 | 35.6277
647.1719 | 123.1888 | -57.9941 | 64.9017 | -0.060578 | 0.00083526 | 0.062239 | 0.063705 | 0.0022964 | 0.00069649 | -0.0016278 | 0.0078126 | -0.00017945 | 0.003418 | -0.002931 | 0.00041649 | -0.0032301 | -0.0031787 | -16.4703 | 64.8834 | -58.1223 | 64.8514 | -57.7103 | -58.1406 | -58.0765 | -22.4442 | 64.9063 | -58.0078 | -57.8796 | -57.8476 | -57.9666 | -57.7103 | -0.12817 | -0.01831 | -0.050354 | 0.28381 | -0.082397 | -0.14648 | 0.045776 | -0.018311 | -0.013732 | 0.004578 | -122.7814 | 0.14648 | 0.28381 | 0.027466 | 0.29755 | 0.041198 | 0.41199 | 122.9736 | 0.16022 | 0.12817 | 123.0057 | 122.9141 | 122.8775 | 122.9004 | -123.024 | -122.9095 | 122.8455 | 0.11444 | 41.5237 | 35.5499
648.1719 | 123.1522 | -57.9895 | 64.9017 | -0.014801 | 0.0023307 | 0.065016 | 0.064132 | 0.0035782 | -0.00037171 | -0.0012006 | -0.0013428 | 0.0017431 | -0.00064077 | 0.00027342 | -0.00043791 | -0.0034437 | -0.00082886 | -16.5894 | 64.8697 | -58.1268 | 64.7873 | -57.7881 | -58.1909 | -58.1314 | -22.6364 | 64.9155 | -58.0444 | -57.93 | -57.9025 | -58.0215 | -57.7515 | -0.13733 | -0.032043 | -0.11444 | 0.20142 | -0.14191 | -0.20142 | -0.004578 | -0.064087 | -0.054932 | 0.013733 | -122.8317 | 0.086975 | 0.23804 | -0.032043 | 0.29297 | 0.022889 | 0.33875 | 122.9141 | 0.14191 | 0.11444 | 122.9965 | 122.9599 | 122.8592 | 122.905 | -123.0286 | -122.9462 | 122.7768 | 0.059509 | 41.4001 | 35.3531
649.1719 | 123.1476 | -57.9987 | 64.9155 | -0.060578 | -0.0013009 | 0.063094 | 0.061355 | -0.0017624 | -0.00058531 | -0.0016278 | -0.0074462 | 0.0021703 | 0.0012818 | 0.0062548 | -0.0010787 | -0.00088008 | -0.0048877 | -16.6809 | 64.8834 | -58.1314 | 64.7919 | -57.8018 | -58.2001 | -58.1497 | -22.7463 | 64.9017 | -58.0307 | -57.9254 | -57.8888 | -58.0353 | -57.756 | -0.13275 | -0.032043 | -0.1236 | 0.19684 | -0.15106 | -0.20142 | -0.01831 | -0.068664 | -0.032044 | -0.013733 | -122.8409 | 0.10986 | 0.24262 | -0.036621 | 0.27466 | -0.004577 | 0.32959 | 122.9233 | 0.14191 | 0.10529 | 123.0148 | 122.9324 | 122.8821 | 122.9004 | -123.0469 | -122.9462 | 122.7905 | 0.073242 | 41.3177 | 35.2524
650.1719 | 123.1567 | -57.9987 | 64.92 | -0.083466 | -1.9142e-05 | 0.065871 | 0.063064 | -0.0021896 | 0.00069649 | -0.00034601 | -0.010498 | 0.0017431 | 0.00085443 | 0.0034778 | -0.00043791 | -0.0019483 | 0.00045294 | -16.777 | 64.8651 | -58.1268 | 64.7873 | -57.8064 | -58.2047 | -58.1223 | -22.8333 | 64.8972 | -58.0032 | -57.9391 | -57.8979 | -58.0215 | -57.7423 | -0.12817 | -0.054932 | -0.13275 | 0.19226 | -0.1236 | -0.20599 | 0.004578 | -0.07782 | -0.004578 | -0.022888 | -122.8592 | 0.10071 | 0.25635 | -0.022888 | 0.26092 | -0.01831 | 0.32044 | 122.9141 | 0.10529 | 0.064087 | 122.9919 | 122.9004 | 122.8638 | 122.8958 | -123.0469 | -122.9233 | 122.7859 | 0.059509 | 41.2216 | 35.1654
651.1719 | 123.1155 | -57.9575 | 64.9109 | -0.10635 | 0.0014761 | 0.063307 | 0.065414 | -0.0013352 | 5.5488e-05 | 0.0015766 | 0.0047608 | -0.00039305 | -0.0014954 | 0.0051868 | 0.00020289 | -0.0019483 | 0.0010937 | -16.8365 | 64.9017 | -58.0994 | 64.7507 | -57.8064 | -58.2047 | -58.136 | -22.9752 | 64.92 | -58.017 | -57.9346 | -57.9208 | -58.0444 | -57.756 | -0.14191 | -0.009156 | -0.16022 | 0.15106 | -0.17853 | -0.24719 | -0.036621 | -0.10529 | -0.05951 | 0.009155 | -122.8455 | 0.036621 | 0.20142 | -0.086976 | 0.26093 | -0.027466 | 0.29297 | 122.85 | 0.096131 | 0.082398 | 123.0011 | 122.937 | 122.8592 | 122.8775 | -123.0103 | -122.9279 | 122.7081 | 0.022888 | 41.1209 | 34.9823
652.1719 | 123.1705 | -57.9712 | 64.9109 | -0.052948 | 0.00040806 | 0.063734 | 0.063705 | -0.0028304 | -0.0010125 | -0.00034601 | -0.016602 | 0.0017431 | 0.001068 | -0.00079478 | -0.0027877 | -0.0021619 | -0.0025379 | -16.8869 | 64.888 | -58.1177 | 64.8239 | -57.756 | -58.1726 | -58.0902 | -23.053 | 64.9292 | -58.0261 | -57.8842 | -57.8613 | -57.9941 | -57.7103 | -0.14649 | -0.022889 | -0.086975 | 0.21515 | -0.11902 | -0.20142 | 0.027466 | -0.054931 | -0.054932 | 0.01831 | -122.7951 | 0.10986 | 0.26093 | -0.022889 | 0.31586 | 0.032043 | 0.36163 | 122.9416 | 0.16479 | 0.14191 | 123.0057 | 122.9553 | 122.8592 | 122.9004 | -123.0286 | -122.937 | 122.7951 | 0.086975 | 41.0843 | 34.9182
653.1719 | 123.1979 | -57.9437 | 64.9063 | -0.075836 | -1.9142e-05 | 0.063948 | 0.062209 | -0.0015488 | -0.0018671 | -0.00034601 | 0.02002 | 3.4148e-05 | -0.0012818 | -0.0025036 | -0.0019333 | -0.0023755 | 0.0021619 | -16.9144 | 64.8697 | -58.0765 | 64.8743 | -57.6828 | -58.1085 | -58.0536 | -23.0804 | 64.9246 | -57.9666 | -57.843 | -57.8293 | -57.9666 | -57.6828 | -0.13275 | -0.036621 | -0.032043 | 0.26093 | -0.10986 | -0.1648 | 0.022888 | -0.032044 | -0.022888 | 0.018311 | -122.7493 | 0.11444 | 0.26093 | -0.022888 | 0.28381 | 0 | 0.39368 | 122.9507 | 0.13733 | 0.1236 | 122.9462 | 122.8912 | 122.8134 | 122.8683 | -122.9828 | -122.8729 | 122.818 | 0.10071 | 41.0294 | 34.8633
654.1719 | 123.1659 | -57.9483 | 64.9429 | -0.075836 | 0.00019446 | 0.064162 | 0.061568 | -0.0013352 | -0.0012261 | 0.002431 | 0.013916 | 0.00088875 | 0.0023498 | 0.0054004 | -0.0012925 | -0.0010937 | -0.0025379 | -17.038 | 64.8697 | -58.0765 | 64.8239 | -57.7652 | -58.1635 | -58.1039 | -23.2819 | 64.9521 | -58.0032 | -57.8796 | -57.8796 | -57.9987 | -57.7103 | -0.12817 | -0.073242 | -0.11902 | 0.18311 | -0.15564 | -0.21515 | -0.027466 | -0.086975 | -0.054932 | 0.009155 | -122.8226 | 0.068664 | 0.23804 | -0.050354 | 0.29297 | 0.004578 | 0.31128 | 122.9004 | 0.1236 | 0.1236 | 122.9462 | 122.9553 | 122.818 | 122.9004 | -123.0194 | -122.9462 | 122.7722 | 0.068664 | 40.9103 | 34.6664
655.1719 | 123.1522 | -57.9666 | 64.9475 | -0.15213 | -0.0013009 | 0.062453 | 0.062423 | 0.0010148 | -0.0010125 | -0.00055961 | 0.0078126 | 3.4148e-05 | 0.00021363 | -0.00229 | -1.0706e-05 | -0.00088008 | 0.00023934 | -17.1204 | 64.8926 | -58.0902 | 64.8056 | -57.7606 | -58.1635 | -58.1131 | -23.3917 | 64.9384 | -58.0032 | -57.8934 | -57.8705 | -57.9987 | -57.7286 | -0.1236 | -0.054932 | -0.14191 | 0.20599 | -0.14648 | -0.19684 | -0.022888 | -0.073242 | -0.036621 | -0.009156 | -122.8409 | 0.096131 | 0.23804 | -0.032043 | 0.27466 | 0.004578 | 0.32959 | 122.8958 | 0.13275 | 0.10986 | 122.9828 | 122.9416 | 122.8592 | 122.905 | -123.0377 | -122.9507 | 122.7722 | 0.073242 | 40.8463 | 34.5749
656.1719 | 123.1705 | -57.9163 | 64.9384 | -0.098725 | -0.00023294 | 0.064375 | 0.062636 | -0.001976 | -0.0014399 | 0.00093559 | -0.010498 | -0.00060665 | 0.0014954 | -0.005708 | -0.0017197 | -0.00045288 | 0.00045294 | -17.2073 | 64.9017 | -58.0948 | 64.8193 | -57.7744 | -58.1726 | -58.0994 | -23.5382 | 64.9292 | -57.9803 | -57.8979 | -57.8659 | -58.0032 | -57.7148 | -0.17853 | -0.036621 | -0.11902 | 0.14191 | -0.1831 | -0.25635 | -0.004577 | -0.077819 | -0.064087 | -0.009155 | -122.8363 | 0.050354 | 0.20142 | -0.086975 | 0.2655 | -0.022888 | 0.32044 | 122.9141 | 0.11444 | 0.082398 | 122.9965 | 122.9095 | 122.818 | 122.8455 | -123.0331 | -122.9187 | 122.7356 | 0.018311 | 40.7089 | 34.3781
657.1719 | 123.2117 | -57.9575 | 64.9521 | -0.12924 | 0.0023307 | 0.063948 | 0.063918 | -0.00090783 | 0.00069649 | 0.0011494 | -0.010498 | -0.0010339 | 0.0023498 | -0.007417 | 0.0010575 | -0.0034437 | 0.00045294 | -17.2989 | 64.8834 | -58.1039 | 64.7736 | -57.7881 | -58.1909 | -58.1268 | -23.7213 | 64.9338 | -58.0307 | -57.93 | -57.9071 | -58.0444 | -57.7972 | -0.14648 | -0.068664 | -0.17853 | 0.16937 | -0.16937 | -0.23346 | -0.022888 | -0.086975 | -0.073243 | -0.01831 | -122.8821 | 0.050354 | 0.16022 | -0.086976 | 0.23346 | -0.013733 | 0.31586 | 122.8775 | 0.1236 | 0.10071 | 122.9874 | 122.9645 | 122.8409 | 122.8912 | -123.056 | -122.9828 | 122.731 | 0.027465 | 40.6586 | 34.2361
658.1719 | 123.175 | -57.93 | 64.9384 | -0.060578 | 0.0023307 | 0.064803 | 0.06285 | -0.0017624 | -0.0020807 | -0.00034601 | -0.01355 | -0.0016749 | -0.0010682 | 0.00091422 | -0.0010787 | -0.0023755 | -0.0025379 | -17.3401 | 64.9063 | -58.0673 | 64.8514 | -57.7194 | -58.1223 | -58.0765 | -23.703 | 64.9384 | -57.9849 | -57.8476 | -57.843 | -57.9529 | -57.6782 | -0.13733 | -0.032043 | -0.086975 | 0.21057 | -0.14648 | -0.19226 | -0.009155 | -0.054931 | -0.054931 | 0 | -122.7859 | 0.086975 | 0.25177 | -0.022888 | 0.3067 | 0.032043 | 0.3479 | 122.9187 | 0.14191 | 0.13733 | 122.9736 | 122.9233 | 122.8363 | 122.8683 | -123.0057 | -122.9233 | 122.7814 | 0.082398 | 40.5899 | 34.227
659.1719 | 123.1155 | -57.9391 | 64.9429 | -0.10635 | -0.0010873 | 0.06288 | 0.063277 | -0.0045394 | 0.00048269 | -0.00055961 | -0.010498 | 3.4148e-05 | 0.00064083 | -0.0020764 | 0.00041649 | -0.0019483 | -0.0042469 | -17.4454 | 64.8926 | -58.0765 | 64.7919 | -57.7972 | -58.1772 | -58.1039 | -23.909 | 64.9384 | -58.0078 | -57.9071 | -57.8979 | -58.0078 | -57.7286 | -0.13733 | -0.050354 | -0.15106 | 0.14191 | -0.16479 | -0.23804 | -0.027466 | -0.10071 | -0.068664 | -0.004578 | -122.85 | 0.041199 | 0.21057 | -0.068664 | 0.27923 | 0 | 0.27924 | 122.8683 | 0.10986 | 0.10071 | 122.9691 | 122.9462 | 122.8317 | 122.8775 | -123.0194 | -122.9507 | 122.731 | 0.032044 | 40.4938 | 34.0302
660.1719 | 123.1567 | -57.9437 | 64.9384 | -0.12161 | 0.0010489 | 0.062239 | 0.064345 | -0.00048063 | -0.0012261 | -0.002055 | 0.0047608 | 0.0011023 | 2.8e-08 | -0.00079478 | 0.00020289 | -0.0025891 | 0.0010937 | -17.482 | 64.9109 | -58.0673 | 64.8285 | -57.7469 | -58.1268 | -58.0856 | -23.9365 | 64.9521 | -57.9803 | -57.9025 | -57.8339 | -57.9666 | -57.6965 | -0.1236 | -0.027465 | -0.10986 | 0.19684 | -0.14191 | -0.18311 | -0.01831 | -0.059509 | -0.036621 | 0.013733 | -122.8409 | 0.10986 | 0.24719 | -0.022888 | 0.28381 | 0.013733 | 0.32043 | 122.8958 | 0.14648 | 0.07782 | 122.9782 | 122.9324 | 122.8546 | 122.8958 | -123.0057 | -122.9187 | 122.7722 | 0.041199 | 40.4617 | 34.0073
661.1719 | 123.1522 | -57.9437 | 64.9841 | -0.075836 | -0.00023294 | 0.061385 | 0.063491 | -0.0028304 | -0.0012261 | -0.00055961 | -0.0074462 | 0.00088875 | -0.00085457 | 0.005614 | -1.0706e-05 | -0.00088008 | -0.00082886 | -17.5598 | 64.9017 | -58.0673 | 64.8239 | -57.756 | -58.1589 | -58.0856 | -24.1058 | 64.9429 | -57.9895 | -57.8842 | -57.8659 | -57.9758 | -57.7011 | -0.1236 | -0.082398 | -0.16022 | 0.18768 | -0.14191 | -0.21515 | -0.01831 | -0.091553 | -0.045776 | -0.041199 | -122.8683 | 0.07782 | 0.24262 | -0.032043 | 0.28839 | 0.013733 | 0.31128 | 122.8912 | 0.1236 | 0.10529 | 122.9691 | 122.9324 | 122.8455 | 122.8867 | -123.0515 | -122.9736 | 122.7676 | 0.05951 | 40.3839 | 33.8379
662.1719 | 123.1476 | -57.93 | 64.9292 | -0.098725 | 0.00040806 | 0.063307 | 0.06285 | 0.0020828 | -0.00079891 | 0.003072 | -0.01355 | -0.00039305 | -0.00064077 | 0.001128 | -0.0015061 | -0.0015211 | 0.0040845 | -17.6651 | 64.8972 | -58.0765 | 64.8193 | -57.7652 | -58.168 | -58.1085 | -24.202 | 64.9704 | -57.9758 | -57.8842 | -57.8476 | -57.9987 | -57.7194 | -0.14648 | -0.032043 | -0.10986 | 0.1648 | -0.17853 | -0.23804 | -0.032044 | -0.091553 | -0.045776 | 0.041199 | -122.8134 | 0.082398 | 0.21057 | -0.068664 | 0.25635 | -0.022888 | 0.31128 | 122.8958 | 0.12817 | 0.091553 | 122.9736 | 122.9462 | 122.8271 | 122.9004 | -123.0057 | -122.905 | 122.7493 | 0.045777 | 40.2649 | 33.728
663.1719 | 123.1201 | -57.9529 | 64.9475 | -0.083466 | 0.00019446 | 0.061812 | 0.063491 | -0.0032578 | 0.00069649 | -0.0024822 | -0.010498 | 0.0015295 | -0.00021357 | 0.0026232 | -0.0023605 | -0.0015211 | -0.0010425 | -17.7155 | 64.92 | -58.0811 | 64.92 | -57.7011 | -58.2367 | -58.1223 | -24.3439 | 64.9612 | -57.9849 | -57.8979 | -57.8705 | -58.0032 | -57.6965 | -0.12817 | -0.027466 | -0.027466 | 0.25177 | -0.16937 | -0.28381 | -0.041198 | -0.15564 | -0.032043 | 0.013733 | -122.8455 | 0.082398 | 0.25635 | -0.050354 | 0.28839 | -0.018311 | 0.37994 | 123.0011 | 0.11444 | 0.086975 | 123.0011 | 122.9462 | 122.8729 | 122.9141 | -123.0286 | -122.9324 | 122.8729 | 0.054932 | 40.2374 | 33.609
664.1719 | 123.0469 | -57.962 | 65.0024 | -0.052948 | 0.0010489 | 0.066298 | 0.065414 | 0.00486 | -0.0014399 | -0.0014142 | -0.11426 | 0.00046135 | -0.00021357 | 0.00091422 | -0.0012925 | 0.0027515 | 0.0019483 | -17.8116 | 64.9521 | -58.1177 | 64.7552 | -57.8293 | -58.2458 | -58.2047 | -24.4904 | 64.9841 | -57.9849 | -57.9803 | -57.9849 | -58.1406 | -57.8064 | -0.15564 | -0.050354 | -0.24719 | 0.13275 | -0.24262 | -0.28381 | -0.086975 | -0.12817 | -0.022888 | -0.01831 | -122.9828 | -0.022888 | 0.15564 | -0.17853 | 0.17853 | -0.15564 | 0.28839 | 122.8729 | 0 | 0.004577 | 123.0698 | 122.9691 | 122.9141 | 122.9462 | -123.1201 | -122.9874 | 122.7173 | -0.018311 | 40.1505 | 33.4717
665.1719 | 123.1705 | -57.9254 | 64.9475 | 0.16067 | -0.00066014 | 0.064375 | 0.061568 | -0.0032578 | -0.00037171 | -0.0016278 | 0.041382 | 3.4148e-05 | 0.00064083 | -0.00058098 | -0.00086511 | -0.0023755 | -0.0016833 | -17.8528 | 64.9292 | -58.0673 | 64.8239 | -57.7744 | -58.168 | -58.0994 | -24.5178 | 64.975 | -57.9803 | -57.8934 | -57.8384 | -57.9895 | -57.7057 | -0.14191 | -0.018311 | -0.1236 | 0.15106 | -0.17395 | -0.24262 | -0.032043 | -0.10071 | -0.054932 | 0.027466 | -122.8409 | 0.086975 | 0.21973 | -0.064087 | 0.27466 | -0.009155 | 0.29297 | 122.8912 | 0.14191 | 0.086975 | 122.9965 | 122.9553 | 122.8546 | 122.9004 | -123.0148 | -122.9279 | 122.7493 | 0.032043 | 40.0726 | 33.4076
666.1719 | 123.1293 | -57.9391 | 64.9246 | -0.075836 | -0.0015145 | 0.064589 | 0.063064 | 0.00016017 | 0.00026909 | 0.0026446 | 0.11157 | -0.0014613 | 0.0012818 | -0.0014356 | -0.0010787 | -0.00066648 | -0.0010425 | -17.9993 | 64.9567 | -58.0673 | 64.8056 | -57.7744 | -58.1497 | -58.0856 | -24.6963 | 64.9933 | -57.93 | -57.8934 | -57.8796 | -58.0032 | -57.724 | -0.12817 | 0.032043 | -0.11902 | 0.1648 | -0.14648 | -0.21057 | -0.01831 | -0.082397 | 0.009155 | 0.068664 | -122.818 | 0.059509 | 0.21515 | -0.064087 | 0.20599 | -0.073242 | 0.29297 | 122.8729 | 0.050354 | 0.036621 | 123.024 | 122.9233 | 122.8958 | 122.9324 | -122.9919 | -122.8546 | 122.7448 | 0.045776 | 39.9399 | 33.2428
667.1719 | 123.1522 | -57.9346 | 64.9933 | -0.068207 | 0.00062166 | 0.061171 | 0.064132 | 0.0012284 | 5.5488e-05 | -0.0014142 | 0.0047608 | 0.0015295 | -0.00021357 | -0.0014356 | -0.00086511 | -0.00045288 | 0.0023755 | -18.0771 | 64.9246 | -58.0627 | 64.8239 | -57.7606 | -58.1543 | -58.1131 | -24.7513 | 64.9567 | -57.9803 | -57.8934 | -57.8796 | -58.0811 | -57.5638 | -0.12817 | -0.068664 | -0.16937 | 0.17395 | -0.17853 | -0.21973 | -0.050354 | -0.091553 | -0.045777 | -0.036621 | -122.8867 | 0.054931 | 0.37079 | -0.14648 | 0.41656 | -0.10071 | 0.30212 | 122.8867 | 0.10071 | 0.086975 | 122.9874 | 122.937 | 122.8592 | 122.8912 | -123.056 | -122.9736 | 122.7585 | 0.041198 | 39.8575 | 33.1833
668.1719 | 123.1293 | -57.9117 | 64.9704 | -0.10635 | 0.00019446 | 0.063948 | 0.064132 | -0.0015488 | 0.00026909 | 0.001363 | 0.001709 | 0.0019567 | 0.001068 | -0.0078442 | -0.00043791 | -0.0019483 | -0.00040166 | -18.2098 | 64.9338 | -58.0811 | 64.8193 | -57.7469 | -58.168 | -58.1085 | -24.8749 | 64.9612 | -57.9803 | -57.9117 | -57.8934 | -58.0078 | -57.7286 | -0.16937 | -0.036621 | -0.15106 | 0.16479 | -0.19684 | -0.25635 | -0.027466 | -0.086975 | -0.068665 | -0.009155 | -122.8821 | 0.01831 | 0.1831 | -0.09613 | 0.25177 | -0.027465 | 0.33417 | 122.9004 | 0.086975 | 0.068665 | 123.0148 | 122.9416 | 122.8455 | 122.8729 | -123.0515 | -122.9507 | 122.731 | 0 | 39.7018 | 33.0368
669.1719 | 123.0194 | -57.9666 | 65.0208 | -0.045319 | -0.0010873 | 0.06523 | 0.062209 | 0.0012284 | -0.0012261 | 0.0022174 | -0.053223 | 3.4148e-05 | 0.001709 | 0.008391 | 0.0014847 | -0.0010937 | -0.0040333 | -18.2465 | 64.9933 | -58.049 | 64.6866 | -57.8659 | -58.1726 | -58.1589 | -25.0122 | 65.0253 | -57.9849 | -57.93 | -57.9163 | -58.0627 | -57.7515 | -0.082397 | -0.027466 | -0.33417 | 0.10071 | -0.19226 | -0.20599 | -0.10986 | -0.1236 | -0.01831 | 0.004578 | -122.9507 | 0.050354 | 0.21515 | -0.09613 | 0.23346 | -0.07782 | 0.1831 | 122.7356 | 0.068664 | 0.054931 | 123.0423 | 123.0103 | 122.9599 | 122.9919 | -123.0698 | -123.0057 | 122.6532 | 0.036621 | 39.7202 | 32.9544
670.1719 | 123.1338 | -57.9163 | 64.9612 | -0.091095 | -0.00023294 | 0.064162 | 0.064345 | -0.0017624 | 0.00091009 | 0.0015766 | -0.037964 | 0.0011023 | 0.0012818 | 0.0026232 | -0.00086511 | -0.00088008 | 0.00023934 | -18.3289 | 64.8972 | -58.0673 | 64.8514 | -57.692 | -58.1451 | -58.0902 | -24.9344 | 64.9567 | -57.9529 | -57.8888 | -57.8613 | -57.9987 | -57.7057 | -0.15106 | -0.064087 | -0.10986 | 0.2243 | -0.17395 | -0.22888 | -0.022888 | -0.07782 | -0.036621 | -0.004578 | -122.85 | 0.054932 | 0.21057 | -0.082397 | 0.24719 | -0.045776 | 0.37537 | 122.9187 | 0.091553 | 0.064087 | 122.9645 | 122.9095 | 122.8134 | 122.8729 | -123.0286 | -122.9141 | 122.7676 | 0.027466 | 39.5874 | 32.9819
671.1719 | 123.0972 | -57.9391 | 64.9612 | -0.11398 | 0.0010489 | 0.063094 | 0.061568 | -0.0024032 | 0.00091009 | 0.0022174 | 0.010864 | -0.0023157 | -0.0023498 | -0.002931 | -0.0010787 | -0.0019483 | 0.00023934 | -18.4433 | 64.9384 | -58.0353 | 64.8376 | -57.7194 | -58.1451 | -58.0902 | -25.058 | 64.9841 | -57.9575 | -57.8659 | -57.8751 | -57.9941 | -57.7011 | -0.09613 | -0.022889 | -0.1236 | 0.21973 | -0.15106 | -0.20599 | -0.054932 | -0.10986 | -0.01831 | 0.022888 | -122.8271 | 0.064087 | 0.23804 | -0.054932 | 0.25635 | -0.036622 | 0.31586 | 122.8729 | 0.082397 | 0.091552 | 122.9736 | 122.9416 | 122.8775 | 122.9233 | -122.9965 | -122.9187 | 122.7768 | 0.073242 | 39.4959 | 32.8812
672.1719 | 123.1476 | -57.9071 | 64.9475 | -0.083466 | 0.0021171 | 0.06523 | 0.064559 | -0.0017624 | -0.0012261 | 0.001363 | -0.025757 | 0.0011023 | -0.00064077 | 0.00048702 | -0.0019333 | -0.00023928 | 2.554e-05 | -18.5303 | 64.9017 | -58.0536 | 64.9017 | -57.6508 | -58.0948 | -58.0536 | -25.0809 | 64.9475 | -57.9529 | -57.8201 | -57.8293 | -57.9483 | -57.6645 | -0.14649 | -0.045777 | -0.045777 | 0.25635 | -0.14649 | -0.18768 | 0 | -0.041199 | -0.045777 | 0 | -122.7676 | 0.077819 | 0.24261 | -0.041199 | 0.28839 | 0.004578 | 0.40283 | 122.9553 | 0.1236 | 0.13275 | 122.9553 | 122.9004 | 122.8088 | 122.8546 | -123.0011 | -122.9004 | 122.8088 | 0.086975 | 39.3768 | 32.8262
673.1719 | 123.143 | -57.9163 | 64.9658 | -0.091095 | 0.0014761 | 0.06523 | 0.063491 | -0.0034714 | 0.0021917 | 0.00029479 | -0.016602 | -0.00060665 | 0.00064083 | -0.0014356 | 0.00020289 | -0.00066648 | -0.00040166 | -18.5211 | 64.9338 | -58.0215 | 64.8834 | -57.6782 | -58.1131 | -58.0536 | -25.177 | 64.975 | -57.9391 | -57.8339 | -57.8384 | -57.9803 | -57.692 | -0.10529 | -0.032043 | -0.082397 | 0.23804 | -0.13733 | -0.19684 | -0.032044 | -0.091553 | -0.022888 | 0.009156 | -122.7997 | 0.07782 | 0.2243 | -0.064087 | 0.24719 | -0.041199 | 0.34332 | 122.905 | 0.10071 | 0.10529 | 122.9553 | 122.9141 | 122.85 | 122.8912 | -122.9874 | -122.905 | 122.7997 | 0.082398 | 39.3951 | 32.7393
674.1719 | 123.0972 | -57.8751 | 65.0024 | -0.060578 | -0.00023294 | 0.062666 | 0.062636 | -0.0011214 | -0.00037171 | 0.00050839 | 0.0078126 | -0.00039305 | 0.001709 | -0.0052808 | 0.00020289 | -0.00088008 | 0.00045294 | -18.5165 | 64.9704 | -57.9941 | 64.9155 | -57.6508 | -58.0307 | -57.9941 | -25.2228 | 65.0528 | -57.8796 | -57.8476 | -57.8064 | -57.93 | -57.6645 | -0.11902 | -0.032043 | -0.086975 | 0.2243 | -0.11902 | -0.15564 | 0 | -0.036621 | -0.004578 | 0.050354 | -122.85 | 0.068665 | 0.21057 | -0.054932 | 0.21515 | -0.050354 | 0.34332 | 122.9095 | 0.073243 | 0.032044 | 122.9645 | 122.9324 | 122.8455 | 122.9279 | -122.9965 | -122.8821 | 122.7905 | 0.027466 | 39.3585 | 32.6523
675.1719 | 123.1567 | -57.8705 | 64.9658 | -0.091095 | -1.9142e-05 | 0.063521 | 0.064132 | 0.00080117 | 0.00048269 | -0.00055961 | -0.025757 | -0.0021021 | -0.00064077 | 0.00091422 | -0.0021469 | -0.0021619 | 0.0017345 | -18.6493 | 64.9292 | -58.0353 | 65.007 | -57.6691 | -58.1085 | -57.9987 | -25.3464 | 64.9704 | -57.9163 | -57.8064 | -57.8018 | -57.9437 | -57.6324 | -0.16479 | -0.036621 | 0.041199 | 0.20142 | -0.12817 | -0.23804 | 0.036621 | -0.073243 | -0.045777 | 0.004578 | -122.7722 | 0.068664 | 0.23804 | -0.073243 | 0.28381 | -0.027466 | 0.36621 | 123.0423 | 0.11444 | 0.10986 | 122.9645 | 122.8867 | 122.7997 | 122.8409 | -123.0011 | -122.8821 | 122.8775 | 0.064087 | 39.2212 | 32.5241
676.1719 | 123.175 | -57.8842 | 64.9704 | -0.13687 | 0.0012625 | 0.066725 | 0.064132 | 0.00080117 | 5.5488e-05 | -0.0012006 | -0.041016 | -0.0027429 | 0.00064083 | 0.0024096 | -0.0021469 | -0.0015211 | 0.0010937 | -18.7317 | 64.9612 | -58.0261 | 64.888 | -57.6736 | -58.0811 | -58.0444 | -25.4745 | 64.975 | -57.93 | -57.7423 | -57.8247 | -57.9437 | -57.6279 | -0.14191 | -0.009155 | -0.082398 | 0.21057 | -0.16022 | -0.19684 | -0.018311 | -0.054932 | -0.045777 | 0.004578 | -122.7127 | 0.059509 | 0.25635 | -0.05951 | 0.30212 | -0.013733 | 0.35248 | 122.9141 | 0.10529 | 0.18768 | 122.9874 | 122.905 | 122.8455 | 122.8592 | -122.9965 | -122.9004 | 122.7722 | 0.14191 | 39.1525 | 32.4097
677.1719 | 123.1659 | -57.8705 | 64.975 | -0.052948 | -0.0013009 | 0.065443 | 0.064345 | 0.0044328 | -0.0016535 | -0.00034601 | -0.037964 | 0.0013159 | 2.8e-08 | 0.0017688 | -0.0025741 | -2.5678e-05 | 0.0017345 | -18.8416 | 64.9475 | -58.0307 | 64.8834 | -57.6691 | -58.0902 | -58.049 | -25.6119 | 65.0024 | -57.93 | -57.811 | -57.8156 | -57.9483 | -57.6233 | -0.16022 | -0.027466 | -0.091553 | 0.20142 | -0.17853 | -0.21973 | -0.01831 | -0.059509 | -0.05951 | 0.027465 | -122.7859 | 0.054931 | 0.24719 | -0.07782 | 0.3067 | -0.01831 | 0.36163 | 122.9141 | 0.11444 | 0.11902 | 122.9782 | 122.9324 | 122.818 | 122.8729 | -123.0057 | -122.905 | 122.7539 | 0.059509 | 39.0289 | 32.2586
678.1719 | 123.1384 | -57.8751 | 64.9841 | -0.052948 | 0.0023307 | 0.063094 | 0.064986 | 0.0018692 | -0.00079891 | -0.00034601 | -0.034912 | 3.4148e-05 | -0.00042717 | 0.0026232 | -0.0012925 | -0.00088008 | 0.00023934 | -18.9514 | 64.9887 | -58.0444 | 64.8514 | -57.7103 | -58.1497 | -58.0719 | -25.7492 | 64.9887 | -57.9254 | -57.7927 | -57.8156 | -57.9483 | -57.6187 | -0.16937 | 0.004577 | -0.13275 | 0.1648 | -0.19684 | -0.27466 | -0.027465 | -0.10528 | -0.050354 | 0.004577 | -122.7768 | 0.059509 | 0.25635 | -0.073242 | 0.3067 | -0.022888 | 0.33417 | 122.8958 | 0.10986 | 0.13275 | 123.0331 | 122.9141 | 122.8638 | 122.8638 | -123.0286 | -122.9095 | 122.7264 | 0.082397 | 38.9236 | 32.1259
679.1719 | 123.0789 | -57.8796 | 65.094 | -0.045319 | -0.00044654 | 0.063521 | 0.063491 | -0.0024032 | 0.00091009 | -0.002055 | -0.0013428 | 3.4148e-05 | -0.00085457 | 0.001128 | -1.0706e-05 | -0.0017347 | -0.0023243 | -18.9789 | 65.0116 | -58.0078 | 64.8697 | -57.7057 | -58.1268 | -58.0719 | -25.882 | 65.0436 | -57.9071 | -57.8751 | -57.843 | -57.9987 | -57.7011 | -0.12817 | -0.082397 | -0.2243 | 0.17395 | -0.19226 | -0.24719 | -0.064087 | -0.11902 | -0.027465 | -0.050354 | -122.9691 | 0.036621 | 0.17853 | -0.11902 | 0.20599 | -0.091553 | 0.30212 | 122.8775 | 0.064086 | 0.032043 | 123.0194 | 122.9507 | 122.8912 | 122.9233 | -123.1018 | -123.0011 | 122.7493 | 0.004578 | 38.9008 | 31.9977
680.1719 | 123.175 | -57.8796 | 65.007 | -0.075836 | -0.00087374 | 0.064162 | 0.064559 | -0.0032578 | -0.0010125 | -0.00013241 | -0.01355 | -0.0012477 | 0.00064083 | -0.0050672 | 0.00020289 | 0.00018792 | 0.0017345 | -19.1116 | 64.9567 | -58.0124 | 64.8834 | -57.6782 | -58.1268 | -58.0444 | -25.8911 | 64.9979 | -57.9208 | -57.7972 | -57.811 | -57.9437 | -57.6096 | -0.13275 | -0.050354 | -0.1236 | 0.20142 | -0.1648 | -0.24719 | -0.032044 | -0.11444 | -0.041198 | -0.009155 | -122.8043 | 0.068665 | 0.27008 | -0.064087 | 0.31128 | -0.022889 | 0.33417 | 122.8958 | 0.10986 | 0.1236 | 122.9691 | 122.9187 | 122.8363 | 122.8775 | -123.0194 | -122.9279 | 122.7631 | 0.082398 | 38.768 | 31.9885
681.1719 | 123.1384 | -57.8796 | 64.9841 | -0.10635 | -0.00044654 | 0.064375 | 0.063064 | 0.00251 | -0.00058531 | -0.00055961 | -0.044067 | 3.4148e-05 | -0.0023498 | -0.00058098 | -0.0025741 | -0.0030163 | 0.0010937 | -19.2261 | 64.9796 | -58.0124 | 64.8422 | -57.7148 | -58.1406 | -58.0811 | -26.0376 | 65.0253 | -57.9208 | -57.8064 | -57.8247 | -57.9758 | -57.6279 | -0.13275 | -0.004578 | -0.14191 | 0.16479 | -0.20142 | -0.26093 | -0.068665 | -0.12817 | -0.041198 | 0.041199 | -122.7905 | 0.054932 | 0.25177 | -0.09613 | 0.29297 | -0.054932 | 0.29755 | 122.8546 | 0.09613 | 0.11444 | 122.9919 | 122.9462 | 122.8592 | 122.905 | -122.9965 | -122.905 | 122.7219 | 0.073243 | 38.6536 | 31.842
682.1719 | 123.0972 | -57.8796 | 65.0116 | -0.045319 | -0.0010873 | 0.06288 | 0.067336 | -0.00069423 | 5.5488e-05 | 0.003072 | -0.037964 | -0.00060665 | 0.001068 | -0.0031446 | -0.0030013 | -0.00088008 | -0.0021107 | -19.3451 | 65.0162 | -58.0444 | 64.8056 | -57.7469 | -58.1726 | -58.1039 | -26.1841 | 65.0482 | -57.93 | -57.843 | -57.8567 | -57.9849 | -57.6645 | -0.1648 | 0.004577 | -0.20599 | 0.13275 | -0.2243 | -0.29297 | -0.059509 | -0.12817 | -0.050354 | 0.036621 | -122.8546 | 0.022889 | 0.21515 | -0.10529 | 0.2655 | -0.054931 | 0.29755 | 122.85 | 0.073243 | 0.086975 | 123.0606 | 122.9782 | 122.8958 | 122.9279 | -123.056 | -122.9416 | 122.6852 | 0.036621 | 38.5345 | 31.6956
683.1719 | 123.1796 | -57.8613 | 65.0253 | -0.10635 | -0.0017281 | 0.063948 | 0.064132 | -5.343e-05 | 0.00048269 | 0.001363 | -0.025757 | 0.00067495 | 0.00021363 | -0.0010084 | -0.0021469 | -0.0015211 | -0.0012561 | -19.4229 | 65.0162 | -58.017 | 64.8651 | -57.6874 | -58.1177 | -58.0444 | -26.2299 | 65.0116 | -57.8888 | -57.7881 | -57.7972 | -57.9391 | -57.5912 | -0.15564 | -0.009156 | -0.16022 | 0.17395 | -0.18311 | -0.25635 | -0.027466 | -0.10071 | -0.027466 | -0.013733 | -122.8134 | 0.064087 | 0.27008 | -0.07782 | 0.29755 | -0.050354 | 0.32959 | 122.8821 | 0.091553 | 0.10071 | 123.0331 | 122.9004 | 122.8775 | 122.8729 | -123.0423 | -122.9141 | 122.7264 | 0.073242 | 38.4384 | 31.6315
684.1719 | 123.0698 | -57.8934 | 65.0482 | -0.29709 | -0.00066014 | 0.063094 | 0.063918 | 0.00080117 | -0.0027215 | -0.0016278 | -0.03186 | 0.0019567 | 0.00021363 | -0.00015378 | -0.00022431 | -0.0010937 | -0.0036059 | -19.3359 | 65.0208 | -57.9987 | 64.8285 | -57.756 | -58.1863 | -58.0994 | -26.4313 | 65.0894 | -57.9163 | -57.8705 | -57.8796 | -58.049 | -57.7057 | -0.10529 | -0.027466 | -0.21973 | 0.13733 | -0.20599 | -0.29297 | -0.10071 | -0.18768 | -0.022888 | 0.041199 | -122.9187 | 0.013733 | 0.18768 | -0.15564 | 0.21057 | -0.13275 | 0.24262 | 122.8271 | 0.036621 | 0.045777 | 123.0194 | 123.0057 | 122.9141 | 122.9828 | -123.0469 | -122.9645 | 122.7219 | 0.022889 | 38.5574 | 31.4621
685.1719 | 123.0423 | -57.8888 | 65.0665 | -0.045319 | -0.00087374 | 0.063948 | 0.062636 | 0.0029374 | 0.00048269 | -0.00055961 | 0.023071 | 0.00067495 | 0.0012818 | 0.0017688 | 0.00041649 | -0.00045288 | 0.00045294 | -19.6472 | 65.0436 | -58.0032 | 64.801 | -57.7698 | -58.3969 | -58.3878 | -26.4267 | 65.0803 | -57.9117 | -57.8613 | -57.9117 | -58.0353 | -57.7057 | -0.11444 | -0.022888 | -0.2655 | 0.11902 | -0.49896 | -0.50812 | -0.38452 | -0.39368 | -0.022888 | 0.013733 | -122.9279 | -0.022888 | 0.18311 | -0.14648 | 0.20599 | -0.1236 | 0.23346 | 122.8043 | 0 | 0.050354 | 123.0469 | 122.9919 | 122.9324 | 122.9691 | -123.0698 | -122.9782 | 122.6898 | 0.027466 | 38.2416 | 31.4621
686.1719 | 123.1293 | -57.9025 | 65.0803 | -0.083466 | -0.00066014 | 0.062239 | 0.063064 | -0.0017624 | 0.0011237 | -0.0018414 | -0.047119 | 0.0015295 | -0.00085457 | 0.00048702 | 0.0016983 | -0.00088008 | 0.00045294 | -19.7067 | 65.0391 | -58.0261 | 64.8102 | -57.7972 | -58.2047 | -58.1314 | -26.6281 | 65.0528 | -57.9163 | -57.756 | -58.136 | -58.3008 | -57.8156 | -0.1236 | -0.041199 | -0.27008 | 0.10529 | -0.22888 | -0.30212 | -0.10529 | -0.17853 | -0.013733 | -0.027466 | -122.8363 | -0.23346 | 0.086975 | -0.39825 | 0.10071 | -0.38452 | 0.22888 | 122.8363 | -0.21973 | 0.16022 | 123.0652 | 122.9691 | 122.9416 | 122.9553 | -123.1064 | -122.9965 | 122.7127 | 0.14648 | 38.1958 | 31.2744
687.1719 | 123.1201 | -57.8613 | 65.0345 | -0.12161 | -0.0013009 | 0.06288 | 0.066482 | 0.0012284 | -0.0012261 | -0.002696 | -0.01355 | 0.0013159 | -0.0012818 | -0.0050672 | -0.0017197 | 0.00040152 | -0.0023243 | -19.8029 | 65.0528 | -58.0032 | 64.8285 | -57.7148 | -58.1497 | -58.0902 | -26.6602 | 65.0528 | -57.9117 | -57.8201 | -57.811 | -57.93 | -57.6462 | -0.14191 | 0.01831 | -0.20599 | 0.14648 | -0.22888 | -0.28839 | -0.086975 | -0.14648 | -0.050354 | 0.01831 | -122.8546 | 0.050354 | 0.21515 | -0.068665 | 0.2655 | -0.018311 | 0.28839 | 122.8317 | 0.10071 | 0.091553 | 123.056 | 122.9645 | 122.9141 | 122.9141 | -123.0377 | -122.9462 | 122.6898 | 0.041199 | 38.0585 | 31.2012
688.1719 | 123.0469 | -57.8796 | 65.0803 | -0.052948 | -0.0013009 | 0.064803 | 0.064773 | 0.0018692 | -0.00015811 | 0.00093559 | -0.29431 | 3.4148e-05 | 0.00085443 | 0.0026232 | 0.00020289 | -0.0021619 | 0.0013073 | -19.9127 | 65.0482 | -57.9895 | 64.801 | -57.7515 | -58.1726 | -58.1131 | -26.7151 | 65.0574 | -57.9254 | -57.8613 | -57.8613 | -57.9987 | -57.6874 | -0.10986 | -0.032043 | -0.27924 | 0.12817 | -0.23346 | -0.29297 | -0.1236 | -0.1831 | -0.045776 | -0.022888 | -122.9416 | 0.018311 | 0.19226 | -0.11902 | 0.23804 | -0.073242 | 0.23804 | 122.7905 | 0.064087 | 0.064087 | 123.0377 | 122.9828 | 122.9279 | 122.937 | -123.0698 | -123.0057 | 122.6807 | 0.018311 | 37.9669 | 31.1646
689.1719 | 122.9965 | -57.9163 | 65.0299 | -0.052948 | 0.00019446 | 0.064162 | 0.063491 | -0.00090783 | 0.0013373 | 0.00029479 | -0.068481 | -0.0014613 | -0.00021357 | 0.0017688 | -0.0021469 | -0.00023928 | 0.0036571 | -19.9997 | 65.0299 | -57.9987 | 64.801 | -57.7789 | -58.1726 | -58.1268 | -26.9302 | 65.0848 | -57.8934 | -57.8613 | -57.8796 | -58.2642 | -57.9025 | -0.082397 | 0 | -0.22888 | 0.13733 | -0.21057 | -0.25635 | -0.12817 | -0.17395 | 0.022888 | 0.054932 | -122.8912 | 0.036621 | 0.013733 | -0.3479 | -0.009155 | -0.37079 | 0.21973 | 122.7997 | 0.013733 | 0.032044 | 123.0286 | 122.9782 | 122.9462 | 123.0011 | -123.0286 | -122.9233 | 122.7173 | 0.054932 | 37.9166 | 30.986
690.1719 | 123.0469 | -57.8613 | 65.062 | -0.11398 | -0.00087374 | 0.061385 | 0.064986 | 0.0018692 | -0.00058531 | -0.00013241 | -0.016602 | 0.0025975 | -0.00085457 | 0.00091422 | 0.00020289 | 0.00018792 | 0.0025891 | -20.3659 | 64.9887 | -58.0536 | 64.8514 | -57.7148 | -58.1497 | -58.0902 | -26.9989 | 65.0894 | -57.8934 | -57.8613 | -57.8476 | -57.9941 | -57.6736 | -0.19226 | -0.073243 | -0.21057 | 0.14648 | -0.22888 | -0.28839 | -0.036621 | -0.09613 | -0.032044 | 0.027466 | -122.9233 | 0.013733 | 0.18768 | -0.13275 | 0.21973 | -0.10071 | 0.33875 | 122.905 | 0.045777 | 0.032044 | 123.0423 | 122.9828 | 122.85 | 122.9507 | -123.1155 | -122.9553 | 122.7127 | 0 | 37.4954 | 30.8624
691.1719 | 123.0286 | -57.8476 | 65.0848 | -0.091095 | 0.00019446 | 0.063521 | 0.065841 | -0.00069423 | 0.0013373 | 0.00029479 | 0.062744 | -0.00060665 | 0.00042723 | 0.007323 | -0.0015061 | 0.00082892 | 0.0013073 | -20.1462 | 65.062 | -57.9987 | 64.9017 | -57.9849 | -58.4839 | -57.9803 | -27.1683 | 65.0894 | -57.8842 | -57.8659 | -57.8796 | -58.0032 | -57.6782 | -0.15106 | -0.022888 | -0.18311 | -0.13733 | -0.13275 | -0.63629 | 0.01831 | -0.48523 | -0.036621 | 0.004578 | -122.9507 | -0.032044 | 0.16937 | -0.15564 | 0.20599 | -0.11902 | 0.013733 | 122.9004 | 0.004577 | 0.01831 | 123.0606 | 122.9736 | 122.9095 | 122.937 | -123.0835 | -122.9691 | 122.7493 | -0.018311 | 37.7014 | 30.6793
692.1719 | 123.0469 | -57.8705 | 65.094 | -0.045319 | -0.0015145 | 0.064162 | 0.065627 | -0.00026703 | 0.00069649 | 0.002431 | -0.044067 | 0.0015295 | 0.001068 | -0.003999 | -0.0025741 | -0.0030163 | -0.0031787 | -20.2194 | 65.062 | -57.9803 | 64.8468 | -57.7148 | -58.1223 | -58.0811 | -27.1683 | 65.1352 | -57.8842 | -57.8751 | -57.8567 | -58.0215 | -57.6782 | -0.10986 | -0.032043 | -0.24719 | 0.15564 | -0.21057 | -0.25177 | -0.10071 | -0.14191 | -0.013733 | 0.041199 | -122.9691 | 0.013733 | 0.19226 | -0.15106 | 0.20599 | -0.13733 | 0.2655 | 122.8271 | 0.027466 | 0.009155 | 123.0423 | 123.0194 | 122.9324 | 123.0057 | -123.0743 | -122.9782 | 122.7173 | -0.004578 | 37.6511 | 30.7022
693.1719 | 123.0469 | -57.8156 | 65.0894 | -0.11398 | -1.9142e-05 | 0.063094 | 0.066054 | -0.0041122 | -0.00079891 | -0.00098701 | -0.03186 | 0.0025975 | 0.00021363 | 0.005614 | -0.00065151 | -0.0017347 | -0.0018971 | -20.2835 | 65.0711 | -57.9529 | 64.8743 | -57.692 | -58.1039 | -58.0582 | -27.2415 | 65.1077 | -57.8567 | -57.8567 | -57.843 | -57.9758 | -57.6874 | -0.13733 | -0.018311 | -0.21515 | 0.1236 | -0.24262 | -0.28839 | -0.10529 | -0.15106 | -0.041198 | 0.01831 | -122.9462 | -0.027466 | 0.12817 | -0.16022 | 0.16937 | -0.11902 | 0.26093 | 122.8271 | 0.013732 | 0 | 123.024 | 122.9645 | 122.8867 | 122.9233 | -123.0423 | -122.9462 | 122.6898 | -0.041198 | 37.532 | 30.574
694.1719 | 123.0469 | -57.843 | 65.0986 | -0.014801 | -0.0015145 | 0.06288 | 0.064132 | 0.001442 | -0.00037171 | -0.00055961 | -0.034912 | 0.0017431 | 0.0036316 | -0.0014356 | 0.0027665 | -0.0017347 | -0.00082886 | -20.4254 | 65.0848 | -57.9712 | 64.8285 | -57.7469 | -58.1543 | -58.0994 | -27.4109 | 65.1077 | -57.8842 | -57.8613 | -57.8705 | -58.0078 | -57.6828 | -0.12817 | -0.013733 | -0.27008 | 0.096131 | -0.25635 | -0.31128 | -0.12817 | -0.18311 | -0.041198 | 0.009155 | -122.9599 | -0.027465 | 0.16022 | -0.16479 | 0.20142 | -0.1236 | 0.2243 | 122.7997 | 0.013733 | 0.022888 | 123.056 | 122.9919 | 122.9279 | 122.9507 | -123.0698 | -122.9828 | 122.6715 | -0.01831 | 37.4176 | 30.4321
695.1719 | 123.0194 | -57.8567 | 65.094 | -0.060578 | -0.00044654 | 0.062025 | 0.064559 | -0.00069423 | -0.00058531 | -0.0014142 | -0.0043946 | 0.0025975 | 0.0014954 | -0.00079478 | -0.00065151 | 0.00082892 | 0.0015209 | -20.4803 | 65.0848 | -57.9575 | 64.8285 | -57.724 | -58.1543 | -58.0856 | -27.4979 | 65.1169 | -57.8613 | -57.8751 | -57.8796 | -58.0307 | -57.6965 | -0.10071 | -0.009155 | -0.2655 | 0.13275 | -0.22888 | -0.29755 | -0.12817 | -0.19684 | -0.004578 | 0.022888 | -122.9691 | -0.022889 | 0.16022 | -0.17395 | 0.16479 | -0.16937 | 0.23346 | 122.7859 | -0.018311 | -0.013733 | 123.0423 | 122.9782 | 122.9416 | 122.9736 | -123.0515 | -122.9553 | 122.6852 | -0.018311 | 37.3764 | 30.3589
696.1719 | 123.0331 | -57.8522 | 65.1169 | -0.12924 | -0.0021555 | 0.065443 | 0.065627 | -0.005394 | 0.0019781 | -0.00013241 | -0.022705 | 0.0023839 | 0.00085443 | 0.0049732 | -0.00086511 | -0.0030163 | 0.0015209 | -20.5627 | 65.0848 | -57.9575 | 64.8468 | -57.7148 | -58.1314 | -58.0673 | -27.5711 | 65.1123 | -57.8476 | -57.8705 | -57.8751 | -58.0261 | -57.6828 | -0.10529 | -0.032043 | -0.27008 | 0.13733 | -0.21515 | -0.27924 | -0.10986 | -0.17395 | 0.004578 | -0.004577 | -122.9874 | -0.022888 | 0.16937 | -0.17395 | 0.16479 | -0.17853 | 0.24261 | 122.8043 | -0.027466 | -0.022888 | 123.0423 | 122.9599 | 122.937 | 122.9645 | -123.0743 | -122.9645 | 122.699 | -0.01831 | 37.2894 | 30.2811
697.1719 | 123.0103 | -57.8384 | 65.1169 | -0.0071715 | 0.0019035 | 0.063734 | 0.06285 | 0.00080117 | 0.0017645 | 8.1188e-05 | -0.0043946 | -0.00017945 | 0.001709 | -0.0048536 | -0.00086511 | -0.0028027 | 0.0040845 | -20.6451 | 65.1077 | -57.962 | 64.856 | -57.7148 | -58.1085 | -58.0719 | -27.6489 | 65.1123 | -57.8613 | -57.8522 | -57.8613 | -58.0032 | -57.6736 | -0.1236 | -0.009155 | -0.26093 | 0.1236 | -0.23346 | -0.27008 | -0.10986 | -0.14649 | -0.022888 | -0.004577 | -122.9691 | -0.022888 | 0.16479 | -0.16479 | 0.18768 | -0.14191 | 0.24719 | 122.818 | 0 | 0.009155 | 123.0698 | 122.9736 | 122.9462 | 122.9507 | -123.0789 | -122.9782 | 122.6944 | -0.013733 | 37.1933 | 30.1895
698.1719 | 123.056 | -57.8293 | 65.1169 | -0.098725 | 0.0012625 | 0.064162 | 0.065414 | 0.0020828 | -0.0010125 | -0.0014142 | -0.0013428 | -0.00017945 | 0.0032044 | -0.00015378 | -0.00022431 | 0.00040152 | 0.00066654 | -20.7092 | 65.0848 | -57.93 | 64.8605 | -57.7057 | -58.1131 | -58.0627 | -27.7176 | 65.1306 | -57.843 | -57.8522 | -57.8522 | -57.9803 | -57.6599 | -0.10071 | -0.032043 | -0.25635 | 0.1236 | -0.23346 | -0.28381 | -0.13275 | -0.1831 | -0.013733 | 0.013733 | -122.9691 | -0.022888 | 0.16937 | -0.15106 | 0.18311 | -0.13733 | 0.22431 | 122.7905 | -0.009155 | -0.009155 | 123.0148 | 122.9736 | 122.9141 | 122.9599 | -123.0469 | -122.9599 | 122.6898 | -0.022888 | 37.1201 | 30.1117
699.1719 | 123.0194 | -57.8522 | 65.1123 | -0.037689 | -1.9142e-05 | 0.063948 | 0.064559 | 0.0012284 | 0.00048269 | -0.002696 | -0.016602 | 0.0017431 | 0.00021363 | 0.0051868 | -0.0012925 | -0.00088008 | 0.00088014 | -20.7916 | 65.0803 | -57.93 | 64.8743 | -57.6782 | -58.0856 | -58.0399 | -27.7725 | 65.1581 | -57.8476 | -57.8339 | -57.843 | -57.9849 | -57.6553 | -0.07782 | -0.032044 | -0.23804 | 0.17395 | -0.18768 | -0.23346 | -0.10986 | -0.15564 | 0.004578 | 0.045776 | -122.9462 | 0.009155 | 0.19684 | -0.13275 | 0.19226 | -0.13733 | 0.25177 | 122.8043 | 0.004577 | 0.013733 | 123.0103 | 123.0057 | 122.9324 | 123.0103 | -123.0423 | -122.9599 | 122.7264 | 0.018311 | 37.0605 | 30.0797
700.1719 | 123.1338 | -57.8567 | 65.0757 | -0.060578 | 0.0014761 | 0.063307 | 0.063491 | 0.003151 | -0.0012261 | -0.0018414 | -0.0074462 | 0.0025975 | -0.00064077 | -0.0086988 | 0.00063009 | -0.0010937 | -0.00082886 | -20.9106 | 65.094 | -57.93 | 64.8376 | -57.7286 | -58.1451 | -58.0994 | -27.8687 | 65.1123 | -57.8384 | -57.843 | -57.8476 | -57.9941 | -57.6599 | -0.073243 | 0.01831 | -0.23804 | 0.12817 | -0.24262 | -0.28839 | -0.16937 | -0.21515 | 0.01831 | 0.036621 | -122.9187 | 0.009155 | 0.19684 | -0.13733 | 0.17853 | -0.15564 | 0.20142 | 122.7676 | -0.009155 | -0.004578 | 123.024 | 122.9507 | 122.9507 | 122.9691 | -123.0057 | -122.9141 | 122.6944 | 0.013732 | 36.9461 | 29.9881
701.1719 | 123.0057 | -57.8476 | 65.1169 | -0.091095 | 0.00062166 | 0.064589 | 0.064986 | -5.343e-05 | 0.00026909 | 0.00029479 | -0.016602 | 0.0017431 | 0.00021363 | 5.9824e-05 | -0.0019333 | -0.00066648 | 0.0021619 | -20.9656 | 65.1215 | -57.9712 | 64.8514 | -57.724 | -58.1223 | -58.0765 | -27.9236 | 65.126 | -57.8659 | -57.8522 | -57.8293 | -57.9941 | -57.6599 | -0.1236 | 0.004578 | -0.2655 | 0.1236 | -0.22888 | -0.27466 | -0.10529 | -0.15106 | -0.018311 | 0.009156 | -122.9691 | 0.01831 | 0.18768 | -0.14648 | 0.20599 | -0.12817 | 0.24719 | 122.8226 | 0.036621 | 0.013733 | 123.0927 | 122.9919 | 122.9691 | 122.9736 | -123.0881 | -122.9828 | 122.699 | -0.004578 | 36.882 | 29.924
702.1719 | 123.0515 | -57.8201 | 65.1215 | -0.091095 | 0.00083526 | 0.06288 | 0.061568 | 0.0057144 | 0.0013373 | -0.00013241 | 0.016968 | 0.0028113 | 0.00085443 | 0.0030506 | -0.0019333 | 0.00040152 | 0.0015209 | -21.1029 | 65.0894 | -57.9529 | 65.0253 | -57.55 | -58.136 | -58.0444 | -27.9785 | 65.126 | -57.8476 | -57.8201 | -57.8293 | -57.9849 | -57.637 | -0.13275 | -0.032043 | -0.09613 | 0.27008 | -0.22431 | -0.31586 | -0.091553 | -0.18311 | -0.027466 | 0.004578 | -122.9416 | -0.009156 | 0.18311 | -0.16479 | 0.21057 | -0.13733 | 0.40283 | 122.9782 | 0.01831 | 0.027466 | 123.0423 | 122.9736 | 122.9095 | 122.9462 | -123.0743 | -122.9691 | 122.8455 | 0 | 36.7172 | 29.8416
703.1719 | 123.0515 | -57.8247 | 65.1215 | -0.11398 | 0.0014761 | 0.064162 | 0.063491 | 0.00251 | -0.00058531 | 0.0022174 | -0.034912 | 0.0015295 | 0.0014954 | -0.0027174 | -0.0019333 | 0.00061532 | -0.0012561 | -21.2448 | 65.0986 | -57.9437 | 64.856 | -57.7332 | -58.1406 | -58.3054 | -27.8366 | 65.1123 | -57.8293 | -57.8156 | -57.811 | -57.9849 | -57.6416 | -0.11902 | -0.022888 | -0.2655 | 0.091553 | -0.48065 | -0.31586 | -0.36163 | -0.19684 | -0.004578 | -0.009155 | -122.937 | 0.013733 | 0.1831 | -0.16022 | 0.18768 | -0.15564 | 0.21057 | 122.7997 | 0.018311 | 0.013733 | 123.0423 | 122.9416 | 122.9233 | 122.937 | -123.0652 | -122.9507 | 122.6807 | 0.009155 | 36.5799 | 29.9881
704.1719 | 123.0148 | -57.8156 | 65.1352 | -0.03006 | 0.00040806 | 0.064375 | 0.064345 | -0.004753 | 0.0015509 | -0.00013241 | -0.0043946 | 0.0013159 | 0.00021363 | -0.0048536 | -0.00022431 | -0.0013073 | 0.0010937 | -21.3501 | 65.0986 | -57.9483 | 64.8788 | -57.6782 | -58.0719 | -58.0399 | -28.1662 | 65.1306 | -57.8201 | -57.8201 | -57.8476 | -57.9941 | -57.6553 | -0.13275 | -0.036621 | -0.25635 | 0.13733 | -0.2243 | -0.25635 | -0.091553 | -0.1236 | -0.004577 | -0.004578 | -122.9553 | -0.032043 | 0.16022 | -0.17853 | 0.16479 | -0.17395 | 0.27008 | 122.8271 | -0.027466 | 0 | 123.0469 | 122.9507 | 122.9141 | 122.9462 | -123.0835 | -122.9553 | 122.6944 | -0.004577 | 36.4655 | 29.6494
705.1719 | 123.1247 | -57.8018 | 65.1489 | -0.052948 | -0.0010873 | 0.064162 | 0.063491 | -0.00069423 | -0.00015811 | -0.00098701 | -0.01355 | 0.00088875 | 0.00021363 | -0.0016492 | -1.0706e-05 | 0.0018969 | 0.00045294 | -21.4966 | 65.1031 | -57.9575 | 64.8331 | -57.724 | -58.1406 | -58.0673 | -28.2761 | 65.126 | -57.8659 | -57.7927 | -58.1177 | -58.0536 | -57.4997 | -0.15564 | -0.045777 | -0.31586 | 0.07782 | -0.2655 | -0.33874 | -0.10986 | -0.18311 | -0.064087 | -0.022888 | -122.9416 | -0.31586 | 0.30212 | -0.25177 | 0.36621 | -0.18768 | 0.23346 | 122.7905 | -0.25177 | 0.073242 | 123.0606 | 122.9919 | 122.905 | 122.9279 | -123.1064 | -123.0148 | 122.6349 | 0.009155 | 36.3052 | 29.5258
706.1719 | 123.0469 | -57.811 | 65.1581 | -0.091095 | -0.00044654 | 0.063521 | 0.063918 | 0.0010148 | 0.0017645 | -0.0033368 | -0.028809 | -0.0016749 | 0.0012818 | -0.0010084 | 0.0019119 | -2.5678e-05 | 0.0013073 | -21.3821 | 65.094 | -57.93 | 64.92 | -57.637 | -58.0536 | -58.0124 | -28.3081 | 65.1672 | -57.8064 | -57.7972 | -57.7927 | -57.9437 | -57.5912 | -0.11902 | -0.064087 | -0.23804 | 0.17395 | -0.20142 | -0.24262 | -0.082397 | -0.1236 | 0.004578 | 0.009155 | -122.9553 | 0.01831 | 0.21973 | -0.13275 | 0.21515 | -0.13733 | 0.29297 | 122.85 | 0.013732 | 0.009155 | 123.024 | 122.9736 | 122.905 | 122.9782 | -123.0881 | -122.9645 | 122.731 | 0.013733 | 36.4288 | 29.5029
707.1719 | 123.0606 | -57.8064 | 65.1581 | -0.037689 | 0.0010489 | 0.064375 | 0.063064 | -5.343e-05 | -0.00015811 | 0.0015766 | 0.010864 | 0.0015295 | 0.0014954 | 0.00091422 | -0.0015061 | -0.0028027 | 0.0032299 | -21.4691 | 65.1169 | -57.9071 | 64.92 | -57.6324 | -58.0627 | -57.9941 | -28.4134 | 65.1581 | -57.8156 | -57.8018 | -57.7927 | -57.9529 | -57.605 | -0.10071 | -0.041199 | -0.23804 | 0.17395 | -0.18768 | -0.25635 | -0.086976 | -0.15564 | -0.009156 | 0 | -122.9599 | 0.013732 | 0.20142 | -0.14648 | 0.21057 | -0.13733 | 0.27466 | 122.8271 | 0.022888 | 0.013733 | 123.024 | 122.9736 | 122.9233 | 122.9645 | -123.0652 | -122.9736 | 122.7264 | 0.004577 | 36.3373 | 29.393
708.1719 | 123.056 | -57.7972 | 65.1489 | -0.068207 | 0.0038261 | 0.066298 | 0.065841 | 0.003151 | -0.0020807 | -0.00098701 | 0.0047608 | -0.00017945 | 0.001709 | -0.0025036 | -0.0025741 | -0.0023755 | 0.00045294 | -21.8582 | 65.0528 | -57.9712 | 64.92 | -57.6691 | -58.0902 | -58.017 | -28.5736 | 65.1581 | -57.8156 | -57.7972 | -57.8018 | -57.9575 | -57.6141 | -0.17395 | -0.096131 | -0.22888 | 0.12817 | -0.21973 | -0.29297 | -0.045777 | -0.11902 | -0.018311 | 0.009155 | -122.9462 | -0.004578 | 0.1831 | -0.16022 | 0.20142 | -0.14191 | 0.30212 | 122.8912 | 0.013733 | 0.018311 | 123.024 | 122.9736 | 122.85 | 122.9553 | -123.1201 | -122.9645 | 122.7173 | 0 | 35.939 | 29.2236
709.1719 | 123.0286 | -57.7972 | 65.1398 | -0.10635 | -0.0010873 | 0.064803 | 0.064559 | -0.0015488 | 0.00048269 | -0.0012006 | 0.001709 | 0.0017431 | 2.8e-08 | -0.0014356 | -0.0015061 | -0.0017347 | -0.00061526 | -21.6888 | 65.1398 | -57.9117 | 64.8926 | -57.6874 | -58.0856 | -58.0399 | -28.7613 | 65.1764 | -57.8156 | -57.8247 | -57.8339 | -57.9895 | -57.6324 | -0.11444 | 0 | -0.24719 | 0.10986 | -0.24262 | -0.28839 | -0.12817 | -0.17395 | -0.018311 | 0.036621 | -122.9645 | -0.036621 | 0.16479 | -0.19226 | 0.18311 | -0.17395 | 0.2243 | 122.8043 | -0.01831 | -0.009155 | 123.0515 | 122.9919 | 122.937 | 122.9736 | -123.0515 | -122.9553 | 122.6898 | -0.027466 | 36.1084 | 29.0359
710.1719 | 122.9919 | -57.7927 | 65.1764 | -0.075836 | 0.0014761 | 0.064589 | 0.066482 | 0.0012284 | 5.5488e-05 | -0.00055961 | -0.016602 | 0.0013159 | 0.00021363 | -0.00015378 | -0.0010787 | -0.0025891 | -0.00082886 | -21.8033 | 65.1123 | -57.8888 | 64.9017 | -57.6645 | -58.0719 | -58.0261 | -28.7888 | 65.1718 | -57.8293 | -57.8201 | -57.811 | -57.9712 | -57.637 | -0.09613 | -0.064087 | -0.27466 | 0.12817 | -0.23346 | -0.27923 | -0.13733 | -0.18311 | -0.036621 | -0.004578 | -122.9965 | -0.01831 | 0.15564 | -0.17853 | 0.19226 | -0.14191 | 0.2243 | 122.7905 | 0.018311 | 0.009156 | 123.0011 | 123.0011 | 122.905 | 122.9645 | -123.0652 | -123.0057 | 122.6944 | -0.027465 | 35.9894 | 29.0039
711.1719 | 123.024 | -57.7835 | 65.1672 | -0.083466 | 0.0012625 | 0.064803 | 0.063705 | -0.0015488 | 0.0021917 | 0.00093559 | -0.0074462 | 0.0017431 | 0.0023498 | -0.0018628 | 0.00020289 | -0.0030163 | -0.0023243 | -21.8857 | 65.1215 | -57.8934 | 64.9246 | -57.6553 | -58.0673 | -58.0078 | -28.8666 | 65.1627 | -57.7927 | -57.7972 | -57.8201 | -57.9391 | -57.6141 | -0.10986 | -0.045776 | -0.24261 | 0.12817 | -0.2243 | -0.28381 | -0.11444 | -0.17395 | -0.009156 | -0.004577 | -122.9645 | -0.036621 | 0.16937 | -0.15564 | 0.17853 | -0.14648 | 0.23804 | 122.818 | -0.027465 | -0.004577 | 123.0148 | 122.9553 | 122.905 | 122.9462 | -123.0606 | -122.9599 | 122.7081 | -0.013733 | 35.8978 | 28.9169
712.1719 | 123.0469 | -57.7789 | 65.1855 | -0.10635 | 0.00040806 | 0.063094 | 0.063491 | -0.00048063 | -0.0014399 | 0.0015766 | 0.081055 | -0.00017945 | 0.0014954 | -0.00464 | -0.0017197 | -0.0021619 | 0.00023934 | -22.0276 | 65.1306 | -57.8842 | 64.9109 | -57.9575 | -58.3374 | -57.8293 | -28.9948 | 65.2039 | -57.8018 | -57.7881 | -57.7789 | -57.93 | -57.6004 | -0.10529 | -0.054932 | -0.27466 | -0.17853 | -0.050354 | -0.55847 | 0.054931 | -0.45319 | -0.022888 | 0.01831 | -122.9736 | 0 | 0.17853 | -0.15106 | 0.20142 | -0.12817 | -0.073242 | 122.7951 | 0.022888 | 0.013733 | 123.0148 | 123.0057 | 122.9095 | 122.9828 | -123.0698 | -122.9874 | 122.6898 | -0.009155 | 35.7513 | 28.7842
713.1719 | 123.0103 | -57.7881 | 65.1764 | -0.091095 | -0.00044654 | 0.065443 | 0.063705 | 0.0027238 | -0.0010125 | 0.0017902 | -0.028809 | 3.4148e-05 | 0.0014954 | 0.0062548 | -1.0706e-05 | -0.0013073 | -0.0023243 | -22.0871 | 65.126 | -57.8796 | 64.92 | -57.637 | -58.0399 | -58.0124 | -29.0588 | 65.1993 | -57.7744 | -57.7881 | -57.7881 | -57.93 | -57.605 | -0.091553 | -0.050354 | -0.25635 | 0.15106 | -0.2243 | -0.25177 | -0.13275 | -0.16022 | 0.013733 | 0.022888 | -122.9645 | 0 | 0.18311 | -0.14191 | 0.16937 | -0.15564 | 0.24262 | 122.7997 | -0.013733 | -0.013733 | 123.0057 | 122.9736 | 122.9141 | 122.9874 | -123.056 | -122.9507 | 122.7081 | 0 | 35.701 | 28.7292
714.1719 | 123.0057 | -57.7881 | 65.1764 | -0.068207 | -0.00066014 | 0.064375 | 0.064559 | -0.0021896 | 0.00048269 | -0.00055961 | 0.010864 | 0.0017431 | 0.00085443 | 0.0068958 | -0.0019333 | -0.0017347 | 0.0040845 | -22.2015 | 65.1398 | -57.9025 | 64.9292 | -57.6233 | -58.0399 | -57.9987 | -29.1458 | 65.1855 | -57.8018 | -57.7698 | -57.7972 | -57.9437 | -57.6004 | -0.11444 | -0.036621 | -0.24719 | 0.16479 | -0.21057 | -0.25177 | -0.09613 | -0.13733 | -0.013733 | 0.009155 | -122.9462 | -0.009155 | 0.18768 | -0.15564 | 0.20142 | -0.14191 | 0.27924 | 122.8317 | 0.004578 | 0.032044 | 123.0423 | 122.9874 | 122.9279 | 122.9736 | -123.0789 | -122.9782 | 122.7173 | 0.018311 | 35.5865 | 28.6423
715.1719 | 123.0423 | -57.756 | 65.1718 | -0.075836 | -0.00066014 | 0.065657 | 0.062209 | 0.00037377 | 0.00069649 | -0.0014142 | -0.022705 | 0.0015295 | 0.001068 | -0.0033582 | -0.0034287 | -0.00088008 | 0.0015209 | -22.3526 | 65.1489 | -57.8934 | 64.888 | -57.6736 | -58.0719 | -57.9987 | -29.2648 | 65.181 | -57.811 | -57.7927 | -57.7652 | -57.9071 | -57.5775 | -0.13733 | -0.022888 | -0.28381 | 0.082397 | -0.24262 | -0.31586 | -0.10529 | -0.17853 | -0.054932 | 0.009155 | -122.9645 | -0.009156 | 0.17853 | -0.15106 | 0.23346 | -0.09613 | 0.21973 | 122.7814 | 0.045776 | 0.01831 | 123.0423 | 122.9919 | 122.905 | 122.937 | -123.0652 | -122.9828 | 122.644 | -0.036622 | 35.4034 | 28.4912
716.1719 | 123.0652 | -57.7469 | 65.1901 | -0.091095 | 0.0010489 | 0.063734 | 0.063918 | 0.001442 | -0.0014399 | 0.0034992 | -0.025757 | 0.0017431 | 0.001709 | 0.0060412 | 0.0010575 | -0.0019483 | -0.0018971 | -22.4075 | 65.1443 | -57.8888 | 64.8972 | -57.6691 | -58.0811 | -58.0078 | -29.3747 | 65.1901 | -57.811 | -57.7057 | -57.5638 | -57.8979 | -57.6187 | -0.14191 | -0.045777 | -0.29297 | 0.07782 | -0.26093 | -0.33417 | -0.11902 | -0.19226 | -0.064087 | 0 | -122.8958 | 0.1831 | 0.12817 | -0.15106 | 0.19226 | -0.086975 | 0.21973 | 122.7859 | 0.24719 | 0.10529 | 123.0331 | 123.0011 | 122.8912 | 122.937 | -123.0789 | -123.0011 | 122.644 | 0.041199 | 35.3394 | 28.3722
717.1719 | 123.0789 | -57.7423 | 65.213 | -0.091095 | 0.00040806 | 0.061812 | 0.064559 | 0.001442 | 0.0015509 | 0.00050839 | -0.0013428 | -0.0014613 | 0.0012818 | 0.0075366 | 0.00063009 | 0.0010425 | 0.0038709 | -22.5128 | 65.1581 | -57.8659 | 64.92 | -57.6553 | -58.0673 | -57.9941 | -29.4708 | 65.213 | -57.7835 | -57.7652 | -58.0582 | -57.8476 | -57.4127 | -0.1236 | -0.054932 | -0.29297 | 0.086976 | -0.25177 | -0.32501 | -0.12817 | -0.20142 | -0.041198 | 0 | -122.9782 | -0.31586 | 0.32959 | -0.10528 | 0.37079 | -0.064087 | 0.21057 | 122.786 | -0.27466 | 0.01831 | 123.024 | 122.9965 | 122.9004 | 122.9553 | -123.0789 | -122.9965 | 122.6624 | -0.022888 | 35.2295 | 28.2715
718.1719 | 122.9736 | -57.7606 | 65.1215 | -0.068207 | -0.00023294 | 0.064375 | 0.064345 | 0.00016017 | 0.00069649 | 0.00050839 | -0.034912 | 0.00024775 | 0.00021363 | 0.0017688 | -0.0012925 | -0.00023928 | 0.00066654 | -22.6181 | 65.1718 | -57.8567 | 64.92 | -57.637 | -58.0536 | -57.9941 | -29.6219 | 65.2084 | -57.7789 | -57.7652 | -57.756 | -57.9117 | -57.4173 | -0.09613 | 0.050354 | -0.20142 | 0.1236 | -0.23346 | -0.29297 | -0.13733 | -0.19684 | -0.018311 | 0.086975 | -122.8867 | 0.004578 | 0.34332 | -0.15106 | 0.36163 | -0.13275 | 0.21973 | 122.7768 | 0.022889 | 0.013733 | 123.0286 | 122.9874 | 122.9324 | 122.9691 | -122.9782 | -122.9004 | 122.6807 | -0.004578 | 35.1425 | 28.1387
719.1719 | 123.0423 | -57.7652 | 65.1947 | -0.22842 | 0.0010489 | 0.061812 | 0.064559 | -0.0024032 | -0.0012261 | -0.00077341 | 0.0078126 | 0.0015295 | 0.00064083 | -0.001222 | 0.00020289 | 0.00018792 | 0.0021619 | -22.4899 | 65.126 | -57.843 | 64.9429 | -57.6096 | -58.0399 | -57.9758 | -29.6402 | 65.1718 | -57.7972 | -57.7469 | -57.756 | -57.8979 | -57.5592 | -0.07782 | -0.068664 | -0.25177 | 0.15564 | -0.21057 | -0.27466 | -0.13275 | -0.19684 | -0.032043 | -0.022888 | -122.9416 | 0.009156 | 0.20599 | -0.13275 | 0.23804 | -0.10071 | 0.23346 | 122.7859 | 0.041199 | 0.050354 | 122.9691 | 122.9691 | 122.8912 | 122.937 | -123.0377 | -122.9919 | 122.7081 | 0.018311 | 35.2753 | 28.125
720.1719 | 123.024 | -57.7332 | 65.2039 | -0.098725 | 0.00083526 | 0.063734 | 0.066909 | 0.00016017 | -0.0012261 | 0.00050839 | 0.001709 | 0.0019567 | -0.001709 | 0.003905 | -0.00086511 | -0.0019483 | -0.0040333 | -22.7966 | 65.1855 | -57.8567 | 64.9567 | -57.6279 | -58.0536 | -57.962 | -29.7455 | 65.2084 | -57.756 | -57.7744 | -57.7652 | -57.9346 | -57.5821 | -0.1236 | -0.01831 | -0.24719 | 0.10529 | -0.22888 | -0.32044 | -0.10529 | -0.19684 | -0.022888 | 0.004578 | -122.9782 | -0.032044 | 0.15106 | -0.20142 | 0.17395 | -0.17853 | 0.22888 | 122.8134 | -0.009156 | -0.018311 | 123.0423 | 122.9645 | 122.9187 | 122.9416 | -123.0606 | -122.9599 | 122.6898 | -0.041199 | 34.9365 | 27.9877
721.1719 | 123.0835 | -57.724 | 65.1672 | -0.083466 | 0.0016899 | 0.06523 | 0.061355 | 0.0010148 | -0.0012261 | 0.00072199 | -0.0013428 | 0.00088875 | 0.0023498 | 0.00048702 | -0.00065151 | -0.0013073 | -0.0014697 | -22.9156 | 65.1672 | -57.843 | 64.9612 | -57.5867 | -58.0124 | -57.9483 | -29.7913 | 65.1627 | -57.7744 | -57.7011 | -57.7011 | -57.8476 | -57.5272 | -0.11902 | 0 | -0.20599 | 0.13733 | -0.2243 | -0.28839 | -0.10529 | -0.16937 | -0.050354 | -0.004577 | -122.8683 | 0.022888 | 0.19684 | -0.1236 | 0.24719 | -0.073242 | 0.25635 | 122.8043 | 0.073242 | 0.073242 | 123.0103 | 122.937 | 122.8912 | 122.8867 | -123.0103 | -122.9416 | 122.6852 | 0.022888 | 34.8084 | 27.9327
722.1719 | 123.0103 | -57.7469 | 65.2267 | -0.12161 | -0.0017281 | 0.064589 | 0.063491 | 0.0016556 | 0.0013373 | 0.00050839 | -0.010498 | 0.0023839 | 0.0014954 | -0.005708 | -0.00065151 | 0.00018792 | 0.0019483 | -23.0164 | 65.1855 | -57.8522 | 64.92 | -57.6233 | -58.0353 | -57.962 | -29.8462 | 65.2176 | -57.7881 | -57.7652 | -57.7057 | -57.8796 | -57.5775 | -0.10529 | -0.041199 | -0.3067 | 0.1236 | -0.21515 | -0.28839 | -0.10986 | -0.1831 | -0.041199 | -0.009156 | -122.9919 | 0.041199 | 0.16937 | -0.13275 | 0.21057 | -0.091553 | 0.22888 | 122.7722 | 0.082398 | 0.022888 | 123.0377 | 123.0057 | 122.9324 | 122.9645 | -123.0789 | -123.0148 | 122.6669 | -0.018311 | 34.7305 | 27.9007
723.1719 | 123.1155 | -57.7148 | 65.2267 | -0.10635 | -0.0010873 | 0.065443 | 0.064345 | 0.0027238 | 0.0013373 | -0.00077341 | -0.025757 | 0.0017431 | 2.8e-08 | -0.0031446 | -0.00022431 | -0.0025891 | 0.0013073 | -23.1262 | 65.1947 | -57.8842 | 64.9429 | -57.6508 | -58.0399 | -57.9803 | -30.0247 | 65.2313 | -57.756 | -57.6416 | -58.0215 | -58.1497 | -57.5684 | -0.16937 | -0.032044 | -0.28381 | 0.064087 | -0.2655 | -0.32501 | -0.096131 | -0.15564 | -0.041198 | 0.004577 | -122.8683 | -0.3067 | 0.14648 | -0.43487 | 0.18768 | -0.39368 | 0.23346 | 122.8271 | -0.2655 | 0.11444 | 123.0789 | 122.9874 | 122.9095 | 122.9462 | -123.111 | -122.9828 | 122.6578 | 0.073242 | 34.5886 | 27.6901
724.1719 | 123.056 | -57.7469 | 65.1993 | -0.19791 | -0.00087374 | 0.062239 | 0.064132 | 0.0016556 | -0.0010125 | -0.00034601 | 0.001709 | 0.0015295 | 0.0019226 | 0.001128 | -0.00022431 | -0.0017347 | -0.00061526 | -22.9889 | 65.1947 | -57.843 | 64.9704 | -57.5821 | -58.017 | -57.9666 | -30.1071 | 65.213 | -57.7515 | -57.7194 | -57.7148 | -57.8934 | -57.5638 | -0.096131 | -0.004578 | -0.22888 | 0.16479 | -0.21973 | -0.27008 | -0.1236 | -0.17395 | -0.004578 | 0.013733 | -122.9187 | 0.032043 | 0.1831 | -0.14648 | 0.18768 | -0.14191 | 0.26093 | 122.8134 | 0.036621 | 0.032044 | 123.0377 | 122.9645 | 122.9416 | 122.9599 | -123.0423 | -122.9507 | 122.7173 | 0.027466 | 34.758 | 27.6398
725.1719 | 123.0331 | -57.724 | 65.2084 | -0.037689 | 0.00062166 | 0.062666 | 0.061355 | -0.00048063 | -0.00015811 | 0.0026446 | -0.053223 | -0.00017945 | -0.00064077 | 5.9824e-05 | 0.0010575 | -0.0013073 | 0.00088014 | -23.3139 | 65.2084 | -57.8613 | 64.9475 | -57.605 | -58.0124 | -57.962 | -30.2261 | 65.2176 | -57.7423 | -57.7515 | -57.7423 | -57.9025 | -57.5638 | -0.13733 | 0 | -0.26093 | 0.11902 | -0.23804 | -0.28839 | -0.10071 | -0.15106 | -0.018311 | 0.009155 | -122.9599 | -0.018311 | 0.16022 | -0.17853 | 0.17853 | -0.16022 | 0.25635 | 122.8088 | 0 | -0.009155 | 123.0698 | 122.9599 | 122.9324 | 122.9416 | -123.0698 | -122.9507 | 122.6715 | -0.027466 | 34.4101 | 27.4979
726.1719 | 123.0515 | -57.7103 | 65.2405 | -0.03006 | 0.00062166 | 0.062453 | 0.063705 | 0.004219 | 5.5488e-05 | -0.0018414 | -0.028809 | 0.0011023 | 0.00064083 | -0.0042126 | 0.0012711 | -0.0013073 | 0.0053661 | -23.4833 | 65.2039 | -57.8384 | 64.9521 | -57.605 | -58.0215 | -57.962 | -30.5969 | 65.1672 | -57.7927 | -57.6965 | -57.692 | -57.8796 | -57.5272 | -0.12817 | -0.036622 | -0.28839 | 0.10529 | -0.25177 | -0.31128 | -0.1236 | -0.18311 | -0.082398 | -0.073243 | -122.937 | 0.01831 | 0.1831 | -0.16937 | 0.2655 | -0.086975 | 0.23346 | 122.7905 | 0.10071 | 0.096131 | 123.0423 | 122.9599 | 122.9141 | 122.8775 | -123.0789 | -123.0331 | 122.6624 | 0.013733 | 34.227 | 27.1133
727.1719 | 123.1476 | -57.7286 | 65.2451 | -0.060578 | 0.0023307 | 0.065016 | 0.063491 | 0.001442 | -0.00058531 | 0.00029479 | -0.010498 | -0.00017945 | 0.0014954 | -0.00036738 | 0.00041649 | 0.00018792 | 0.0032299 | -23.5977 | 65.2084 | -57.8339 | 64.9475 | -57.6279 | -58.0399 | -57.9712 | -30.4367 | 65.2451 | -57.7606 | -57.6782 | -57.8796 | -58.1818 | -57.7057 | -0.10529 | -0.036621 | -0.29755 | 0.10071 | -0.24261 | -0.31128 | -0.13733 | -0.20599 | -0.032043 | 0 | -122.9233 | -0.15106 | 0.022889 | -0.45319 | 0.054932 | -0.42114 | 0.20599 | 122.7814 | -0.11902 | 0.082397 | 123.0423 | 123.0057 | 122.937 | 122.9736 | -123.0789 | -123.0057 | 122.6761 | 0.050354 | 34.1309 | 27.2919
728.1719 | 123.0331 | -57.6965 | 65.2176 | -0.068207 | -0.00044654 | 0.063094 | 0.064986 | 0.00058737 | 5.5488e-05 | -0.0012006 | -0.016602 | 0.00088875 | -0.00042717 | 0.0064684 | 0.00084389 | -0.00088008 | 0.00045294 | -23.6435 | 65.1993 | -57.8156 | 65.007 | -57.5226 | -57.962 | -57.9163 | -30.455 | 65.2496 | -57.7194 | -57.692 | -57.7057 | -57.8476 | -57.5272 | -0.11902 | -0.01831 | -0.21057 | 0.17395 | -0.21973 | -0.2655 | -0.10071 | -0.14648 | -0.022888 | 0.032044 | -122.9095 | -0.009155 | 0.16937 | -0.15106 | 0.19226 | -0.12817 | 0.29297 | 122.8226 | 0.013733 | 0.027465 | 123.0148 | 122.9691 | 122.8958 | 122.9462 | -123.0331 | -122.937 | 122.7036 | 0.004577 | 34.053 | 27.2415
729.1719 | 123.0423 | -57.7011 | 65.2405 | -0.037689 | -0.0010873 | 0.063307 | 0.064559 | 0.00037377 | 0.00069649 | -0.0018414 | -0.019653 | 0.00046135 | 0.00042723 | 0.0030506 | -1.0706e-05 | -0.0010937 | -0.00018806 | -23.79 | 65.1947 | -57.8247 | 64.9796 | -57.5684 | -57.9895 | -57.962 | -30.629 | 65.2359 | -57.7652 | -57.7286 | -57.7194 | -57.9025 | -57.5455 | -0.1236 | -0.045777 | -0.26093 | 0.13275 | -0.26093 | -0.28839 | -0.13733 | -0.1648 | -0.064087 | -0.004578 | -122.9691 | -0.01831 | 0.15564 | -0.20142 | 0.21973 | -0.13733 | 0.25635 | 122.8043 | 0.045777 | 0.036621 | 123.0194 | 123.0011 | 122.8958 | 122.937 | -123.0652 | -123.0057 | 122.6807 | -0.027466 | 33.9111 | 27.0721
730.1719 | 123.0698 | -57.6965 | 65.2542 | -0.10635 | 0.0010489 | 0.063734 | 0.066909 | -0.00090783 | -0.00058531 | 8.1188e-05 | -0.022705 | 0.0021703 | 0.002777 | 0.0066822 | 0.0019119 | -0.0036573 | -0.00018806 | -23.9319 | 65.1993 | -57.8201 | 64.9475 | -57.5867 | -58.0215 | -57.9575 | -30.7159 | 65.2313 | -57.7377 | -57.5684 | -57.7011 | -57.9025 | -57.5272 | -0.1236 | -0.054931 | -0.3067 | 0.10986 | -0.26093 | -0.32501 | -0.13733 | -0.20142 | -0.041199 | -0.022888 | -122.8226 | -0.004578 | 0.16937 | -0.20599 | 0.21057 | -0.16479 | 0.23346 | 122.7676 | 0.036621 | 0.16937 | 123.0194 | 122.9691 | 122.8958 | 122.9279 | -123.0743 | -122.9919 | 122.644 | 0.12817 | 33.7646 | 26.9806
731.1719 | 123.0423 | -57.724 | 65.2267 | -0.083466 | 0.0012625 | 0.066725 | 0.064559 | -0.0024032 | -0.0025079 | 0.0017902 | -0.0043946 | 0.00046135 | 0.00042723 | -0.002931 | -0.00065151 | -2.5678e-05 | 0.00066654 | -24.0372 | 65.2222 | -57.8247 | 64.9567 | -57.5912 | -58.0261 | -57.962 | -30.8166 | 65.2588 | -57.7332 | -57.7194 | -57.7194 | -57.8659 | -57.5272 | -0.10071 | -0.004578 | -0.27008 | 0.13275 | -0.23804 | -0.30212 | -0.13733 | -0.20142 | -0.009155 | 0.032043 | -122.9462 | 0.004578 | 0.19684 | -0.14191 | 0.20599 | -0.13275 | 0.23346 | 122.7814 | 0.013733 | 0.013733 | 123.0469 | 122.9919 | 122.9462 | 122.9828 | -123.0515 | -122.9599 | 122.6807 | 0.004578 | 33.6868 | 26.9073
732.1719 | 123.0606 | -57.6599 | 65.2679 | -0.083466 | 0.00083526 | 0.063521 | 0.066482 | -0.00090783 | 0.0013373 | -0.0012006 | -0.01355 | 0.0015295 | 0.0014954 | 0.0036914 | 0.0010575 | -2.5678e-05 | -0.0018971 | -24.1058 | 65.2084 | -57.7972 | 65.0299 | -57.5043 | -57.93 | -57.8842 | -30.835 | 65.2679 | -57.7011 | -57.6828 | -57.6828 | -57.8293 | -57.5043 | -0.13733 | -0.059509 | -0.23804 | 0.15564 | -0.2243 | -0.27008 | -0.086975 | -0.13275 | -0.041199 | 0 | -122.9507 | -0.022888 | 0.15564 | -0.16937 | 0.19684 | -0.12817 | 0.29297 | 122.8271 | 0.018311 | 0.018311 | 123.0057 | 122.9691 | 122.8683 | 122.9279 | -123.0652 | -122.9691 | 122.6898 | -0.022888 | 33.5541 | 26.825
733.1719 | 123.0331 | -57.692 | 65.2451 | -0.11398 | 0.0014761 | 0.063948 | 0.064559 | -0.0032578 | -0.00015811 | -0.00013241 | -0.01355 | 0.0011023 | 0.001709 | -0.0042126 | -0.00065151 | -0.0036573 | 0.0038709 | -24.2706 | 65.2267 | -57.8064 | 64.975 | -57.5821 | -57.9987 | -57.93 | -31.0226 | 65.213 | -57.756 | -57.7148 | -57.6508 | -57.8705 | -57.5134 | -0.11444 | -0.01831 | -0.27008 | 0.10986 | -0.23804 | -0.3067 | -0.1236 | -0.19226 | -0.064086 | -0.032043 | -122.9599 | 0.041199 | 0.17853 | -0.17853 | 0.24261 | -0.11444 | 0.2243 | 122.7814 | 0.10529 | 0.041198 | 123.0331 | 122.9691 | 122.9187 | 122.905 | -123.0515 | -123.0011 | 122.6669 | -0.022888 | 33.4213 | 26.6693
734.1719 | 123.0423 | -57.6736 | 65.2725 | -0.075836 | 0.00062166 | 0.064162 | 0.063064 | -0.0030442 | 0.0011237 | -0.00098701 | -0.016602 | -0.00017945 | 0.00021363 | 0.0019824 | -0.0015061 | 0.00040152 | 0.0017345 | -24.3301 | 65.2496 | -57.7789 | 65.007 | -57.5134 | -57.9163 | -57.8842 | -31.0501 | 65.2771 | -57.724 | -57.6828 | -57.6965 | -57.8384 | -57.4997 | -0.10529 | -0.022888 | -0.2655 | 0.16022 | -0.21057 | -0.24262 | -0.10529 | -0.13733 | -0.050354 | 0.004578 | -122.9553 | -0.022888 | 0.17395 | -0.16479 | 0.2243 | -0.11444 | 0.2655 | 122.7859 | 0.027466 | 0.041199 | 123.0286 | 123.0011 | 122.9233 | 122.9507 | -123.0515 | -122.9965 | 122.6807 | -0.009155 | 33.3435 | 26.6235
735.1719 | 123.1201 | -57.6691 | 65.2176 | -0.052948 | -0.00044654 | 0.063734 | 0.063277 | -0.001976 | 0.0013373 | -0.00013241 | 0.02002 | -0.00060665 | -0.0012818 | -0.0027174 | -1.0706e-05 | -0.0023755 | -0.00040166 | -24.4995 | 65.2176 | -57.7927 | 65.007 | -57.5317 | -57.962 | -57.8888 | -31.1325 | 65.2313 | -57.7148 | -57.6233 | -57.6324 | -57.7789 | -57.4539 | -0.1236 | 0 | -0.21057 | 0.13733 | -0.21973 | -0.29297 | -0.09613 | -0.16937 | -0.045777 | 0.013733 | -122.8409 | 0.036621 | 0.21515 | -0.10986 | 0.26093 | -0.064087 | 0.26093 | 122.7997 | 0.082398 | 0.091553 | 123.0103 | 122.9462 | 122.8867 | 122.9004 | -123.0103 | -122.9324 | 122.6761 | 0.045776 | 33.1696 | 26.5366
736.1719 | 123.0423 | -57.6874 | 65.2451 | -0.13687 | 0.00019446 | 0.063734 | 0.063277 | 0.0012284 | -0.00079891 | -0.0033368 | -0.034912 | 0.00067495 | -0.00064077 | 0.0060412 | -0.0021469 | -0.0023755 | 0.0021619 | -24.6414 | 65.213 | -57.8247 | 64.9796 | -57.5684 | -57.9803 | -57.9346 | -31.2744 | 65.2679 | -57.7286 | -57.5455 | -57.6462 | -57.8567 | -57.5317 | -0.13733 | -0.032043 | -0.2655 | 0.11902 | -0.24719 | -0.29297 | -0.10986 | -0.15564 | -0.041199 | 0.022888 | -122.7905 | 0.041199 | 0.15564 | -0.16937 | 0.19684 | -0.12817 | 0.25635 | 122.8043 | 0.082398 | 0.18311 | 123.0377 | 122.9965 | 122.9004 | 122.9553 | -123.0698 | -122.9736 | 122.6669 | 0.14191 | 33.046 | 26.413
737.1719 | 123.1064 | -57.6416 | 65.2725 | -0.098725 | -0.00087374 | 0.063094 | 0.063705 | 0.00037377 | -0.0018671 | -0.0018414 | -0.016602 | 0.0021703 | 0.0014954 | 0.00027342 | -0.0021469 | -0.0015211 | 0.0023755 | -24.678 | 65.2313 | -57.7744 | 65.0574 | -57.431 | -57.8659 | -57.8384 | -31.2103 | 65.2634 | -57.6965 | -57.6233 | -57.6324 | -57.7698 | -57.4493 | -0.13275 | -0.041199 | -0.21515 | 0.21057 | -0.19684 | -0.2243 | -0.064087 | -0.091553 | -0.054931 | -0.009155 | -122.8958 | 0.009156 | 0.19226 | -0.12817 | 0.24719 | -0.073242 | 0.34332 | 122.8317 | 0.064087 | 0.073242 | 123.0057 | 122.9599 | 122.8729 | 122.905 | -123.0469 | -122.9691 | 122.699 | 0.018311 | 32.9636 | 26.4313
738.1719 | 123.0927 | -57.6599 | 65.2588 | -0.083466 | 0.00062166 | 0.065016 | 0.063705 | 0.00058737 | 0.00048269 | -0.00013241 | 0.001709 | 0.0017431 | 0.00042723 | -0.00058098 | -0.0010787 | -0.0025891 | -0.0038197 | -24.8016 | 65.2817 | -57.7972 | 65.0757 | -57.4585 | -57.8659 | -57.8156 | -31.3019 | 65.2679 | -57.6782 | -57.5867 | -57.5958 | -57.756 | -57.4448 | -0.13733 | 0.022888 | -0.1831 | 0.20142 | -0.15564 | -0.20599 | -0.018311 | -0.068665 | -0.018311 | 0.009155 | -122.8455 | 0.064087 | 0.21515 | -0.09613 | 0.23346 | -0.077819 | 0.33875 | 122.8729 | 0.082398 | 0.091553 | 123.0789 | 122.9462 | 122.9416 | 122.9279 | -123.056 | -122.937 | 122.7356 | 0.073242 | 32.8583 | 26.358
739.1719 | 123.1064 | -57.7057 | 65.2908 | -0.091095 | -0.00023294 | 0.064375 | 0.064132 | -0.00026703 | 0.0021917 | -0.0022686 | -0.022705 | 0.0013159 | 0.0012818 | 0.0015552 | -0.00022431 | 0.00040152 | 0.0013073 | -24.9939 | 65.2451 | -57.8018 | 64.9841 | -57.5684 | -57.9895 | -57.93 | -31.5079 | 65.2634 | -57.7011 | -57.6782 | -57.7606 | -58.1497 | -57.7377 | -0.096131 | -0.045777 | -0.3067 | 0.13733 | -0.22431 | -0.28381 | -0.12817 | -0.18768 | 0.004577 | -0.027466 | -122.9691 | -0.054932 | -0.032044 | -0.44403 | -0.036621 | -0.44861 | 0.23346 | 122.786 | -0.059509 | 0.022888 | 123.0469 | 122.9645 | 122.9507 | 122.9691 | -123.0927 | -122.9919 | 122.6898 | 0.027465 | 32.7118 | 26.1978
740.1719 | 123.1293 | -57.6599 | 65.213 | 0.038605 | -0.00087374 | 0.064375 | 0.063491 | -0.0026168 | -0.00079891 | -0.00077341 | 0.065796 | 3.4148e-05 | 0.0014954 | -0.0020764 | -0.0010787 | -0.00066648 | 0.0010937 | -24.9527 | 65.2039 | -57.7515 | 65.1031 | -57.4036 | -57.8522 | -57.7789 | -31.4163 | 65.2313 | -57.6462 | -57.5729 | -57.5592 | -57.7148 | -57.3853 | -0.091553 | -0.009156 | -0.10986 | 0.25635 | -0.11902 | -0.19226 | -0.027466 | -0.10071 | 0.013733 | 0.01831 | -122.786 | 0.10071 | 0.27466 | -0.054932 | 0.26092 | -0.068665 | 0.3479 | 122.8546 | 0.086975 | 0.073242 | 122.9553 | 122.8775 | 122.8638 | 122.8912 | -122.9645 | -122.8592 | 122.7631 | 0.086975 | 32.7072 | 26.2436
741.1719 | 123.0881 | -57.6187 | 65.3 | -0.045319 | -0.0017281 | 0.063094 | 0.063705 | -0.0011214 | 0.00026909 | -0.00055961 | 0.0078126 | -0.00060665 | 0.001709 | -0.0054944 | -0.00065151 | -0.0023755 | -0.0012561 | -25.1266 | 65.2679 | -57.7377 | 65.0757 | -57.4585 | -57.8522 | -57.811 | -31.5308 | 65.3046 | -57.6462 | -57.6004 | -57.5867 | -57.7286 | -57.4265 | -0.11902 | -0.032044 | -0.2243 | 0.16022 | -0.19226 | -0.23346 | -0.073242 | -0.11444 | -0.027466 | 0.004577 | -122.9004 | 0.032043 | 0.19226 | -0.10986 | 0.21973 | -0.082398 | 0.27924 | 122.8134 | 0.059509 | 0.045776 | 123.0057 | 122.9507 | 122.8867 | 122.9233 | -123.0377 | -122.9462 | 122.6944 | 0.01831 | 32.4921 | 26.088
742.1719 | 123.0652 | -57.637 | 65.3275 | -0.075836 | 0.0016899 | 0.063307 | 0.064132 | 0.0027238 | -0.00079891 | 8.1188e-05 | 0.013916 | 0.00024775 | 2.8e-08 | -0.0010084 | 0.00041649 | -0.00045288 | -0.00061526 | -25.2457 | 65.2908 | -57.7423 | 65.0711 | -57.4768 | -57.8705 | -57.8384 | -31.6681 | 65.3091 | -57.6462 | -57.6187 | -57.5867 | -57.7469 | -57.431 | -0.10529 | -0.036621 | -0.25635 | 0.16022 | -0.20142 | -0.23346 | -0.09613 | -0.12817 | -0.009155 | -0.018311 | -122.9462 | 0.050354 | 0.20599 | -0.10986 | 0.21515 | -0.10071 | 0.2655 | 122.8134 | 0.059509 | 0.027466 | 123.0331 | 122.9553 | 122.9279 | 122.9462 | -123.0698 | -122.9736 | 122.7081 | 0.018311 | 32.3914 | 25.9689
743.1719 | 123.1064 | -57.6553 | 65.2954 | -0.075836 | -1.9142e-05 | 0.064589 | 0.063705 | 0.0020828 | -0.00079891 | 0.0015766 | 0.0047608 | 0.00046135 | 0.0014954 | 0.0017688 | 0.00063009 | -0.0017347 | -0.00082886 | -25.3372 | 65.2954 | -57.724 | 65.0803 | -57.4402 | -57.8339 | -57.8156 | -31.7184 | 65.3046 | -57.6691 | -57.5958 | -57.5775 | -57.7103 | -57.4356 | -0.068665 | 0 | -0.21515 | 0.21515 | -0.16022 | -0.17853 | -0.091553 | -0.10986 | -0.013733 | 0.009155 | -122.8912 | 0.077819 | 0.21973 | -0.054932 | 0.23346 | -0.041199 | 0.28381 | 122.8043 | 0.091552 | 0.073242 | 123.0194 | 122.9736 | 122.9507 | 122.9599 | -123.0194 | -122.9645 | 122.7356 | 0.059509 | 32.3181 | 25.9369
744.1719 | 123.0698 | -57.605 | 65.3091 | -0.045319 | -0.0017281 | 0.064803 | 0.064345 | -0.00069423 | 0.00091009 | 0.0011494 | -0.0074462 | 0.0021703 | 0.001709 | -0.0025036 | -0.0025741 | -0.0025891 | -0.00082886 | -25.4517 | 65.2771 | -57.7698 | 65.0848 | -57.4722 | -57.8567 | -57.8201 | -31.8649 | 65.3137 | -57.6599 | -57.6187 | -57.5775 | -57.7515 | -57.4265 | -0.1648 | -0.032043 | -0.2243 | 0.13275 | -0.21515 | -0.25177 | -0.050354 | -0.086975 | -0.054932 | 0.004578 | -122.9279 | 0.027465 | 0.17853 | -0.14649 | 0.23346 | -0.091553 | 0.29755 | 122.8546 | 0.082397 | 0.041199 | 123.0469 | 122.9736 | 122.8821 | 122.9187 | -123.0789 | -122.9691 | 122.6898 | -0.013733 | 32.1533 | 25.7401
745.1719 | 123.0743 | -57.6508 | 65.2634 | -0.052948 | 0.00083526 | 0.063734 | 0.064345 | 0.001442 | 0.00026909 | -0.0014142 | 0.001709 | 0.0021703 | 0.0014954 | -0.0027174 | -0.00065151 | -0.0017347 | 0.0015209 | -25.6714 | 65.2222 | -57.7789 | 65.0299 | -57.5043 | -57.9437 | -57.8842 | -32.0297 | 65.2771 | -57.6736 | -57.6279 | -57.6462 | -57.7835 | -57.4631 | -0.12817 | -0.041199 | -0.23346 | 0.14648 | -0.23346 | -0.29297 | -0.10529 | -0.16479 | -0.022888 | 0.013733 | -122.8912 | 0.004578 | 0.18768 | -0.13275 | 0.21057 | -0.10986 | 0.27466 | 122.8088 | 0.027466 | 0.045776 | 123.0011 | 122.9507 | 122.8729 | 122.9279 | -123.0423 | -122.937 | 122.6807 | 0.022888 | 31.9794 | 25.621
746.1719 | 123.0789 | -57.6324 | 65.3229 | -0.060578 | -0.0013009 | 0.063734 | 0.063491 | -0.0038986 | -0.0018671 | 0.0015766 | 0.001709 | 0.00024775 | 0.00042723 | -0.0037854 | -0.0032151 | -0.0019483 | 2.554e-05 | -25.6897 | 65.3 | -57.7423 | 65.0757 | -57.4539 | -57.8567 | -57.8293 | -32.0892 | 65.3549 | -57.6599 | -57.6004 | -57.5729 | -57.7423 | -57.431 | -0.10986 | -0.022888 | -0.24719 | 0.17853 | -0.19684 | -0.2243 | -0.086975 | -0.11444 | -0.027466 | 0.032043 | -122.9233 | 0.059509 | 0.20142 | -0.10986 | 0.22888 | -0.082398 | 0.28839 | 122.818 | 0.086975 | 0.059509 | 123.0423 | 123.0148 | 122.9324 | 122.9874 | -123.0652 | -122.9828 | 122.7081 | 0.032043 | 31.9427 | 25.5432
747.1719 | 123.056 | -57.6187 | 65.2908 | -0.03006 | 0.0012625 | 0.063734 | 0.062423 | 0.00037377 | 0.00026909 | -0.0012006 | 0.0047608 | 0.0011023 | 2.8e-08 | 0.00070062 | -0.00022431 | 0.00018792 | -0.00082886 | -25.8133 | 65.3 | -57.7332 | 65.0894 | -57.4402 | -57.8384 | -57.7972 | -32.2083 | 65.3412 | -57.6508 | -57.5912 | -57.5684 | -57.7103 | -57.431 | -0.11444 | 0.009155 | -0.20142 | 0.17853 | -0.17853 | -0.21973 | -0.064087 | -0.10529 | -0.032044 | 0.050354 | -122.8821 | 0.050354 | 0.18768 | -0.091553 | 0.21973 | -0.059509 | 0.29297 | 122.8226 | 0.082398 | 0.059509 | 123.0331 | 122.9919 | 122.9187 | 122.9599 | -123.024 | -122.9416 | 122.7081 | 0.027465 | 31.8054 | 25.4105
748.1719 | 123.0743 | -57.6141 | 65.3412 | -0.03006 | -0.0017281 | 0.063948 | 0.06285 | -0.0017624 | -0.00058531 | -0.0046186 | 0.047485 | -0.0023157 | 0.0019226 | -0.00229 | -0.0017197 | -0.0034437 | 0.0015209 | -25.8499 | 65.2634 | -57.7011 | 65.1352 | -57.3578 | -57.7789 | -57.7286 | -32.2723 | 65.2908 | -57.6233 | -57.5958 | -57.5638 | -57.7194 | -57.4402 | -0.086975 | -0.07782 | -0.20599 | 0.25635 | -0.11444 | -0.16479 | -0.027466 | -0.07782 | -0.009155 | -0.050354 | -122.937 | 0.050354 | 0.17395 | -0.10528 | 0.18311 | -0.09613 | 0.34332 | 122.8363 | 0.059509 | 0.027466 | 122.9645 | 122.9141 | 122.8775 | 122.905 | -123.0423 | -122.9645 | 122.7493 | 0.018311 | 31.7642 | 25.3418
749.1719 | 123.1201 | -57.5867 | 65.3275 | -0.03006 | -0.00066014 | 0.063734 | 0.060287 | -0.001976 | -0.00015811 | -0.00077341 | 0.053589 | -0.00039305 | -0.0012818 | 0.002196 | -0.0034287 | -0.0010937 | 0.0021619 | -25.9415 | 65.2405 | -57.6736 | 65.181 | -57.3441 | -57.7469 | -57.7057 | -32.3456 | 65.2954 | -57.637 | -57.5363 | -57.5089 | -57.637 | -57.3669 | -0.086975 | -0.086975 | -0.14648 | 0.24262 | -0.11902 | -0.16022 | -0.032043 | -0.073242 | -0.050354 | -0.032044 | -122.8638 | 0.07782 | 0.21973 | -0.050354 | 0.27008 | 0 | 0.32959 | 122.8546 | 0.12817 | 0.10071 | 122.9141 | 122.9324 | 122.8271 | 122.8821 | -123.0011 | -122.9645 | 122.7676 | 0.050354 | 31.6452 | 25.2411
750.1719 | 123.0927 | -57.6141 | 65.3183 | -0.037689 | -0.00066014 | 0.062453 | 0.064345 | 0.0018692 | -0.0016535 | -0.0024822 | -0.037964 | 0.0011023 | 0.00064083 | 0.0028368 | -0.0025741 | 0.00061532 | -0.0023243 | -25.9872 | 65.2679 | -57.7377 | 65.1215 | -57.4173 | -57.8567 | -57.8064 | -32.5333 | 65.3275 | -57.6233 | -57.5912 | -57.6004 | -57.7469 | -57.4265 | -0.1236 | -0.050354 | -0.19684 | 0.19684 | -0.19226 | -0.24261 | -0.068664 | -0.11902 | -0.009155 | 0.009156 | -122.9095 | 0.013733 | 0.18768 | -0.13275 | 0.19684 | -0.1236 | 0.32044 | 122.8592 | 0.022888 | 0.032043 | 123.0057 | 122.9507 | 122.8821 | 122.9416 | -123.056 | -122.9416 | 122.7356 | 0.022888 | 31.6269 | 25.0809
751.1719 | 123.1247 | -57.5729 | 65.3229 | -0.098725 | 0.00040806 | 0.064375 | 0.062209 | -0.0041122 | -0.0014399 | -0.0012006 | 0.071899 | 0.0013159 | 0.001709 | -0.0048536 | -0.0017197 | -0.0028027 | 0.0023755 | -26.033 | 65.2817 | -57.6874 | 65.1764 | -57.3029 | -57.724 | -57.6874 | -32.5424 | 65.2954 | -57.605 | -57.518 | -57.4768 | -57.6004 | -57.3395 | -0.11444 | -0.041199 | -0.14648 | 0.27008 | -0.11444 | -0.15106 | 0 | -0.036621 | -0.032043 | -0.027466 | -122.8409 | 0.09613 | 0.23346 | -0.027466 | 0.2655 | 0.004577 | 0.38452 | 122.8638 | 0.12817 | 0.086975 | 122.9691 | 122.9004 | 122.8546 | 122.8683 | -123.0103 | -122.9279 | 122.7493 | 0.054932 | 31.5399 | 25.0305
752.1719 | 123.1338 | -57.5912 | 65.3137 | -0.091095 | 0.00019446 | 0.062666 | 0.063277 | -0.0026168 | 0.0026191 | 0.001363 | 0.068848 | -0.0021021 | 0.0014954 | 0.0015552 | -0.0015061 | -0.0028027 | -0.0016833 | -26.1017 | 65.2908 | -57.7148 | 65.1993 | -57.2937 | -57.7057 | -57.6691 | -32.3959 | 65.3687 | -57.55 | -57.5043 | -57.486 | -57.5912 | -57.3532 | -0.1236 | -0.022888 | -0.11444 | 0.29755 | -0.077819 | -0.11444 | 0.045777 | 0.009156 | 0.041199 | 0.054931 | -122.818 | 0.10529 | 0.23804 | 0 | 0.19684 | -0.041199 | 0.42114 | 122.9141 | 0.064087 | 0.045777 | 123.0057 | 122.9187 | 122.8821 | 122.9599 | -123.0286 | -122.8638 | 122.7905 | 0.086976 | 31.4896 | 25.1953
753.1719 | 123.1247 | -57.5638 | 65.3229 | -0.060578 | -0.00023294 | 0.06288 | 0.061568 | -0.001976 | -0.0037897 | 0.00029479 | 0.02002 | -0.0012477 | -0.0010682 | -0.00079478 | -0.00043791 | -0.0032301 | -0.0025379 | -26.2207 | 65.2634 | -57.6691 | 65.1993 | -57.5684 | -57.843 | -57.6782 | -32.7255 | 65.2954 | -57.5958 | -57.5043 | -57.4448 | -57.5729 | -57.3074 | -0.10528 | -0.059509 | -0.1236 | -0.004577 | -0.11444 | -0.27924 | -0.009156 | -0.17395 | -0.032043 | -0.027466 | -122.8271 | 0.11902 | 0.25635 | -0.009155 | 0.28839 | 0.022888 | 0.10071 | 122.8683 | 0.15106 | 0.091553 | 122.9324 | 122.8912 | 122.8271 | 122.8592 | -122.9919 | -122.9187 | 122.7631 | 0.05951 | 31.3431 | 24.8383
754.1719 | 123.143 | -57.5592 | 65.2771 | -0.045319 | 0.0019035 | 0.061385 | 0.063491 | 0.0012284 | -0.0012261 | -0.00098701 | 0.065796 | 3.4148e-05 | -0.00021357 | 0.0030506 | -0.0017197 | -0.0013073 | -0.0014697 | -26.3168 | 65.2771 | -57.6553 | 65.213 | -57.2662 | -57.7103 | -57.6553 | -32.8125 | 65.3183 | -57.5912 | -57.4905 | -57.4539 | -57.5729 | -57.3074 | -0.09613 | 0 | -0.064087 | 0.29297 | -0.09613 | -0.15106 | 0 | -0.054932 | -0.032044 | 0.041198 | -122.7676 | 0.10529 | 0.25177 | -0.013733 | 0.28381 | 0.018311 | 0.3891 | 122.8683 | 0.13733 | 0.10071 | 122.9324 | 122.9095 | 122.8363 | 122.8775 | -122.9324 | -122.8683 | 122.7722 | 0.068664 | 31.2424 | 24.7467
755.1719 | 123.0423 | -57.6004 | 65.3641 | -0.052948 | 0.0012625 | 0.064162 | 0.065627 | 0.00080117 | -0.0020807 | -0.00055961 | 0.010864 | 3.4148e-05 | 0.00042723 | -0.00079478 | -0.0012925 | -0.0034437 | -0.0016833 | -26.4175 | 65.2954 | -57.6874 | 65.1535 | -57.3807 | -57.7744 | -57.7377 | -33.0597 | 65.3641 | -57.5958 | -57.5867 | -57.5592 | -57.6782 | -57.4127 | -0.086975 | -0.068665 | -0.21057 | 0.21973 | -0.13733 | -0.17395 | -0.050354 | -0.086975 | 0.004578 | 0 | -122.9507 | 0.041199 | 0.18768 | -0.07782 | 0.1831 | -0.082398 | 0.3067 | 122.8409 | 0.036621 | 0.009155 | 122.9828 | 122.9599 | 122.8958 | 122.9645 | -123.0515 | -122.9599 | 122.7539 | 0.013733 | 31.1829 | 24.5407
756.1719 | 123.1201 | -57.5867 | 65.332 | -0.075836 | 0.0023307 | 0.062239 | 0.063918 | -0.0021896 | -0.0014399 | -0.002696 | 0.035278 | 0.00046135 | 0.00064083 | -0.0014356 | -0.0021469 | -0.0015211 | -0.0012561 | -26.6235 | 65.2725 | -57.7057 | 65.1398 | -57.3853 | -57.8064 | -57.7515 | -33.1329 | 65.3137 | -57.6096 | -57.5363 | -57.5455 | -57.6874 | -57.3898 | -0.11902 | -0.059509 | -0.19226 | 0.20142 | -0.1648 | -0.21973 | -0.045777 | -0.10071 | -0.022888 | -0.01831 | -122.8683 | 0.041199 | 0.19684 | -0.10071 | 0.21973 | -0.07782 | 0.32043 | 122.8455 | 0.064087 | 0.073242 | 122.9782 | 122.9233 | 122.8592 | 122.9004 | -123.0377 | -122.9416 | 122.7264 | 0.050354 | 30.9631 | 24.4537
757.1719 | 123.1338 | -57.5775 | 65.3366 | -0.068207 | 0.00083526 | 0.061598 | 0.063918 | 0.0020828 | 5.5488e-05 | -0.0033368 | 0.016968 | 3.4148e-05 | 0.00085443 | -0.0033582 | -0.0021469 | -0.0023755 | -0.0029651 | -26.7059 | 65.2634 | -57.7148 | 65.1718 | -57.2205 | -57.7332 | -57.7606 | -33.2474 | 65.2908 | -57.6141 | -57.5409 | -57.4951 | -57.6599 | -57.3532 | -0.13733 | -0.073242 | -0.16479 | 0.35706 | -0.18311 | -0.15564 | -0.045776 | -0.01831 | -0.036621 | -0.045776 | -122.8775 | 0.082398 | 0.22431 | -0.082397 | 0.26093 | -0.045776 | 0.49439 | 122.8867 | 0.11902 | 0.073242 | 122.9782 | 122.905 | 122.8409 | 122.8683 | -123.0515 | -122.9507 | 122.7493 | 0.036621 | 30.8716 | 24.3301
758.1719 | 123.1064 | -57.5775 | 65.3 | -0.1445 | 0.0014761 | 0.064375 | 0.061782 | 0.0012284 | 5.5488e-05 | 0.0022174 | 0.016968 | -0.00060665 | -0.00021357 | 0.001128 | -0.0023605 | -0.0010937 | 0.00023934 | -26.8341 | 65.2588 | -57.6828 | 65.1398 | -57.3853 | -57.8064 | -57.7423 | -33.3023 | 65.3091 | -57.637 | -57.5134 | -57.518 | -57.6508 | -57.3761 | -0.10529 | -0.041199 | -0.16022 | 0.19226 | -0.1648 | -0.22888 | -0.05951 | -0.1236 | -0.059509 | 0.009155 | -122.8134 | 0.05951 | 0.20142 | -0.073242 | 0.26092 | -0.013733 | 0.29755 | 122.8226 | 0.11902 | 0.1236 | 122.9416 | 122.9462 | 122.8363 | 122.8867 | -122.9828 | -122.937 | 122.7173 | 0.064087 | 30.7434 | 24.2752
759.1719 | 123.1247 | -57.5821 | 65.2954 | -0.12161 | 0.0012625 | 0.066084 | 0.063705 | 0.00251 | -0.00058531 | 0.00050839 | 0.001709 | 0.00046135 | 0.001709 | -0.0033582 | -0.0017197 | -0.0019483 | -0.0036059 | -26.8845 | 65.2496 | -57.7011 | 65.1489 | -57.3532 | -57.8064 | -57.7194 | -33.3801 | 65.2863 | -57.6233 | -57.518 | -57.5226 | -57.6645 | -57.3807 | -0.11902 | -0.045776 | -0.14648 | 0.22888 | -0.13733 | -0.2243 | -0.01831 | -0.10529 | -0.041199 | -0.009155 | -122.8134 | 0.059509 | 0.20142 | -0.082398 | 0.24262 | -0.041199 | 0.3479 | 122.85 | 0.10071 | 0.10529 | 122.9507 | 122.9095 | 122.8317 | 122.8683 | -122.9965 | -122.9187 | 122.731 | 0.064087 | 30.6976 | 24.202
760.1719 | 123.0103 | -57.5867 | 65.3824 | -0.0071715 | 0.0021171 | 0.062239 | 0.064132 | -0.0013352 | -0.00015811 | 0.0017902 | -0.0043946 | 0.00024775 | -0.0010682 | 0.00027342 | -0.00065151 | -0.0015211 | -0.0021107 | -26.9714 | 65.332 | -57.6828 | 65.126 | -57.399 | -57.7972 | -57.7515 | -33.5175 | 65.3824 | -57.6096 | -57.5546 | -57.5409 | -57.6736 | -57.4219 | -0.09613 | -0.050354 | -0.25635 | 0.18768 | -0.1648 | -0.21057 | -0.068665 | -0.11444 | -0.022888 | 0 | -122.937 | 0.045776 | 0.16479 | -0.086975 | 0.18768 | -0.064087 | 0.28381 | 122.8088 | 0.068664 | 0.054932 | 123.0148 | 122.9919 | 122.9187 | 122.9691 | -123.0652 | -122.9919 | 122.7127 | 0.032044 | 30.6152 | 24.0692
761.1719 | 123.111 | -57.5867 | 65.3 | -0.083466 | -0.00087374 | 0.064162 | 0.0652 | -0.0021896 | 0.0011237 | -0.00055961 | -0.0074462 | 0.0013159 | 0.00042723 | 0.0013416 | -0.0010787 | -0.0017347 | -0.0023243 | -27.1088 | 65.2725 | -57.6965 | 65.1535 | -57.3715 | -57.8018 | -57.7332 | -33.5861 | 65.3229 | -57.6096 | -57.5363 | -57.518 | -57.6462 | -57.3578 | -0.10986 | -0.027466 | -0.14648 | 0.21515 | -0.14648 | -0.21515 | -0.036621 | -0.10529 | -0.022888 | 0.022888 | -122.8363 | 0.068665 | 0.22888 | -0.059509 | 0.25177 | -0.036621 | 0.32501 | 122.85 | 0.091553 | 0.073242 | 122.9691 | 122.9324 | 122.8592 | 122.9095 | -122.9965 | -122.9095 | 122.7402 | 0.050354 | 30.4779 | 24.0005
762.1719 | 123.1613 | -57.5592 | 65.2451 | -0.060578 | -1.9142e-05 | 0.06523 | 0.063918 | 0.00016017 | -0.00058531 | 0.00050839 | -0.050171 | 0.0011023 | -0.00064077 | 0.0049732 | -0.0010787 | -0.0013073 | -0.00018806 | -27.2095 | 65.2634 | -57.7103 | 65.1718 | -57.3257 | -57.7744 | -57.7423 | -33.6456 | 65.2908 | -57.6096 | -57.4722 | -57.4814 | -57.6462 | -57.3212 | -0.15106 | 0.018311 | -0.073242 | 0.23346 | -0.18311 | -0.21515 | -0.032044 | -0.064087 | -0.050354 | 0.045777 | -122.7173 | 0.07782 | 0.23804 | -0.086975 | 0.28839 | -0.036621 | 0.38452 | 122.8821 | 0.12817 | 0.13733 | 122.9736 | 122.9004 | 122.8226 | 122.85 | -122.9553 | -122.8546 | 122.731 | 0.086975 | 30.3497 | 23.9136
763.1719 | 123.1796 | -57.5729 | 65.2863 | -0.13687 | 0.0019035 | 0.064375 | 0.063705 | -5.343e-05 | -0.00079891 | 0.00093559 | -0.047119 | 0.00067495 | 0.0012818 | -0.0016492 | -0.00065151 | -0.0019483 | -0.0018971 | -27.2827 | 65.2725 | -57.6874 | 65.2084 | -57.3257 | -57.7789 | -57.7194 | -33.9661 | 65.2679 | -57.6462 | -57.4722 | -57.4722 | -57.637 | -57.3074 | -0.11444 | -0.013733 | -0.07782 | 0.24719 | -0.14648 | -0.20599 | -0.032043 | -0.091553 | -0.073242 | -0.018311 | -122.7585 | 0.10071 | 0.2655 | -0.064087 | 0.33874 | 0.009155 | 0.36163 | 122.8958 | 0.17395 | 0.17395 | 122.9599 | 122.9141 | 122.8455 | 122.8409 | -122.9736 | -122.9324 | 122.7814 | 0.10071 | 30.2902 | 23.6069
764.1719 | 123.1567 | -57.5592 | 65.2908 | -0.15976 | -0.0021555 | 0.065871 | 0.063064 | -0.0011214 | 0.0036871 | -0.00013241 | -0.044067 | 0.00088875 | 0.00021363 | -0.0048536 | -0.0019333 | -0.0036573 | -0.0012561 | -27.4338 | 65.2634 | -57.692 | 65.1764 | -57.3486 | -57.7789 | -57.7332 | -33.8699 | 65.3 | -57.6324 | -57.4539 | -57.4631 | -57.6462 | -57.3212 | -0.13275 | -0.027466 | -0.11444 | 0.21057 | -0.17395 | -0.21973 | -0.041198 | -0.086975 | -0.073242 | 0.009155 | -122.7448 | 0.09613 | 0.23804 | -0.086975 | 0.31128 | -0.013733 | 0.34332 | 122.8683 | 0.16937 | 0.17853 | 122.9553 | 122.9324 | 122.8226 | 122.8592 | -122.9828 | -122.9233 | 122.7356 | 0.10529 | 30.1254 | 23.6893
765.1719 | 123.111 | -57.5729 | 65.3687 | -0.060578 | 0.0014761 | 0.063948 | 0.063705 | 0.0012284 | 0.00026909 | 0.0049946 | -0.06543 | -0.0010339 | 0.0012818 | 0.0034778 | -0.0015061 | -0.0023755 | 0.00088014 | -27.5253 | 65.3549 | -57.6782 | 65.181 | -57.3349 | -57.7881 | -57.7377 | -33.9615 | 65.3641 | -57.5821 | -57.5272 | -57.6187 | -57.7423 | -57.3212 | -0.10529 | -0.013733 | -0.18768 | 0.23804 | -0.16479 | -0.21515 | -0.059509 | -0.10986 | -0.009155 | -0.004577 | -122.8958 | -0.045776 | 0.25177 | -0.16937 | 0.26093 | -0.16022 | 0.34332 | 122.8592 | -0.036621 | 0.054931 | 123.0331 | 122.9462 | 122.9279 | 122.937 | -123.0469 | -122.9507 | 122.7539 | 0.045776 | 30.0476 | 23.6115
766.1719 | 123.1613 | -57.5592 | 65.2771 | -0.083466 | 0.0010489 | 0.065443 | 0.063277 | 0.001442 | 0.00069649 | 8.1188e-05 | -0.03186 | 0.00067495 | -0.00042717 | 0.0043322 | -0.0023605 | -0.0021619 | -0.0025379 | -27.7084 | 65.2817 | -57.6828 | 65.181 | -57.3578 | -57.8201 | -57.7423 | -34.0942 | 65.3091 | -57.6233 | -57.4722 | -57.4814 | -57.637 | -57.3029 | -0.1236 | 0.004577 | -0.096131 | 0.20142 | -0.18311 | -0.26093 | -0.05951 | -0.13733 | -0.064087 | 0.032043 | -122.7493 | 0.07782 | 0.25635 | -0.07782 | 0.32044 | -0.013733 | 0.32501 | 122.8638 | 0.14191 | 0.15106 | 122.9645 | 122.9324 | 122.8409 | 122.8683 | -122.9599 | -122.9004 | 122.7402 | 0.086975 | 29.8508 | 23.465
767.1719 | 123.0927 | -57.5684 | 65.3046 | -0.075836 | -0.00044654 | 0.060316 | 0.064132 | -0.0034714 | 0.0011237 | -0.00013241 | -0.044067 | -0.00039305 | 2.8e-08 | 0.00048702 | -0.00065151 | -0.00066648 | -0.0033923 | -27.8687 | 65.3046 | -57.7103 | 65.1443 | -57.399 | -57.8339 | -57.7927 | -34.2545 | 65.3137 | -57.6187 | -57.5089 | -57.5134 | -57.6462 | -57.3212 | -0.14191 | 0 | -0.16022 | 0.16937 | -0.22431 | -0.2655 | -0.082398 | -0.1236 | -0.050354 | 0.009156 | -122.8134 | 0.054931 | 0.24719 | -0.07782 | 0.29755 | -0.027466 | 0.31128 | 122.8546 | 0.10529 | 0.10986 | 123.0148 | 122.9324 | 122.8729 | 122.8821 | -123.0148 | -122.9233 | 122.7127 | 0.059509 | 29.6997 | 23.3139
768.1719 | 123.0835 | -57.5867 | 65.3183 | -0.098725 | -0.0013009 | 0.063734 | 0.063918 | 0.0012284 | 0.0015509 | 0.0017902 | -0.041016 | 0.0017431 | 0.00021363 | -0.0035718 | -0.0010787 | -0.00066648 | 2.554e-05 | -27.9877 | 65.3 | -57.692 | 65.0894 | -57.4127 | -57.8613 | -57.7835 | -34.4101 | 65.3412 | -57.6233 | -57.5317 | -57.5455 | -57.7011 | -57.3944 | -0.10529 | -0.01831 | -0.22888 | 0.17395 | -0.19684 | -0.27466 | -0.091552 | -0.16937 | -0.036621 | 0.022889 | -122.85 | 0.041199 | 0.19226 | -0.11444 | 0.22888 | -0.07782 | 0.27924 | 122.7814 | 0.07782 | 0.091553 | 122.9919 | 122.9645 | 122.8867 | 122.9279 | -123.0103 | -122.9416 | 122.6761 | 0.054932 | 29.599 | 23.1766
769.1719 | 123.0606 | -57.5638 | 65.2817 | -0.11398 | 0.0014761 | 0.064589 | 0.064559 | 0.00251 | 0.0013373 | -0.00098701 | -0.041016 | 0.0023839 | 0.00085443 | 0.0019824 | -0.0019333 | -0.00023928 | -0.00040166 | -28.0975 | 65.3 | -57.7011 | 65.126 | -57.3807 | -57.8201 | -57.7606 | -34.4467 | 65.3458 | -57.6279 | -57.5089 | -57.4905 | -57.6324 | -57.3166 | -0.13733 | 0.018311 | -0.15564 | 0.18311 | -0.19684 | -0.25635 | -0.059509 | -0.11902 | -0.064087 | 0.064087 | -122.7905 | 0.073242 | 0.24719 | -0.068664 | 0.31128 | -0.004577 | 0.32043 | 122.8271 | 0.13733 | 0.11902 | 123.0011 | 122.9736 | 122.8638 | 122.9095 | -122.9828 | -122.9095 | 122.6898 | 0.054932 | 29.4662 | 23.1171
770.1875 | 123.024 | -57.5821 | 65.3641 | -0.060578 | 0.0016899 | 0.066939 | 0.063277 | -0.0013352 | 5.5488e-05 | -0.00013241 | -0.037964 | 0.00067495 | 0.00085443 | -0.00079478 | -0.0015061 | 0.00082892 | 2.554e-05 | -28.1525 | 65.3091 | -57.7148 | 65.1123 | -57.4448 | -57.8796 | -57.8156 | -34.6344 | 65.3961 | -57.6096 | -57.5867 | -57.6141 | -57.7698 | -57.4493 | -0.13275 | -0.054932 | -0.25177 | 0.13733 | -0.23346 | -0.29755 | -0.10071 | -0.16479 | -0.027466 | 0.032043 | -122.9507 | -0.032044 | 0.13275 | -0.18768 | 0.16022 | -0.16022 | 0.27008 | 122.8271 | -0.004578 | 0.022888 | 123.024 | 123.0057 | 122.8912 | 122.9782 | -123.0789 | -122.9736 | 122.6944 | -0.004578 | 29.4296 | 22.9477
771.1719 | 123.0423 | -57.5729 | 65.3366 | -0.075836 | -0.00087374 | 0.064162 | 0.064345 | -5.343e-05 | -0.0012261 | 0.00093559 | -0.050171 | 0.0019567 | 0.0019226 | -0.0033582 | -0.00065151 | -0.00066648 | -0.0029651 | -28.3539 | 65.3503 | -57.7103 | 65.0986 | -57.4356 | -57.8705 | -57.7881 | -34.6664 | 65.3595 | -57.6004 | -57.5455 | -57.5638 | -57.7057 | -57.3898 | -0.13733 | 0.013733 | -0.23804 | 0.13733 | -0.21515 | -0.29755 | -0.07782 | -0.16022 | -0.027466 | 0.022888 | -122.8821 | 0.009155 | 0.18311 | -0.13275 | 0.21057 | -0.10529 | 0.27466 | 122.8088 | 0.036621 | 0.054932 | 123.0606 | 122.9599 | 122.9233 | 122.9324 | -123.0469 | -122.937 | 122.6715 | 0.027466 | 29.2191 | 22.9065
772.1719 | 123.0057 | -57.5958 | 65.3595 | -0.11398 | 0.00019446 | 0.064162 | 0.06755 | 0.001442 | 0.0026191 | 0.002431 | -0.050171 | -0.00017945 | -0.00021357 | -0.0025036 | -0.0010787 | -0.00066648 | -0.00082886 | -28.5233 | 65.3137 | -57.6782 | 65.1031 | -57.4173 | -57.8567 | -57.8156 | -34.8129 | 65.3687 | -57.6141 | -57.5592 | -57.5958 | -57.7652 | -57.4219 | -0.082398 | -0.045776 | -0.25635 | 0.17853 | -0.21973 | -0.26093 | -0.13733 | -0.17853 | -0.018311 | 0.009155 | -122.9187 | 0 | 0.17395 | -0.16937 | 0.19226 | -0.15106 | 0.26093 | 122.7814 | 0.018311 | 0.054932 | 122.9919 | 122.9828 | 122.9095 | 122.9645 | -123.0377 | -122.9736 | 122.699 | 0.036621 | 29.0726 | 22.7829
773.1719 | 123.0194 | -57.5455 | 65.3824 | -0.11398 | -0.00044654 | 0.06288 | 0.064345 | 0.0012284 | 0.0013373 | -0.00055961 | -0.028809 | -0.00017945 | 0.00064083 | 0.0034778 | -0.0015061 | -0.0040845 | 0.0017345 | -28.688 | 65.3229 | -57.6874 | 65.0711 | -57.4677 | -57.8659 | -57.8018 | -34.9045 | 65.3824 | -57.6141 | -57.4448 | -57.6096 | -57.7332 | -57.3853 | -0.14191 | -0.059509 | -0.31128 | 0.07782 | -0.25635 | -0.32044 | -0.11444 | -0.17853 | -0.068665 | 0 | -122.8271 | -0.064087 | 0.16022 | -0.18768 | 0.22888 | -0.11902 | 0.21973 | 122.7585 | 0.004578 | 0.16937 | 123.0103 | 122.9965 | 122.8683 | 122.9279 | -123.0698 | -122.9965 | 122.6166 | 0.10071 | 28.8574 | 22.641
774.1719 | 123.0515 | -57.5775 | 65.3412 | 0.023346 | -1.9142e-05 | 0.063948 | 0.065627 | 0.0022964 | 0.00069649 | 8.1188e-05 | -0.010498 | 0.00024775 | 0.00042723 | -0.0018628 | -0.00022431 | -0.0025891 | 0.0015209 | -28.6926 | 65.332 | -57.6828 | 65.1031 | -57.4265 | -57.8567 | -57.7789 | -35.0098 | 65.3595 | -57.6004 | -57.5455 | -57.5684 | -57.724 | -57.399 | -0.10529 | -0.009156 | -0.23804 | 0.15106 | -0.20142 | -0.27923 | -0.096131 | -0.17395 | -0.022888 | 0.01831 | -122.8867 | 0.009156 | 0.17853 | -0.14648 | 0.20142 | -0.1236 | 0.25635 | 122.7859 | 0.032044 | 0.054932 | 123.0148 | 122.9599 | 122.9095 | 122.937 | -123.024 | -122.9416 | 122.6807 | 0.032044 | 28.8849 | 22.5677
775.1875 | 123.0194 | -57.5455 | 65.3549 | -0.11398 | -1.9142e-05 | 0.06288 | 0.063918 | 0.0016556 | -0.00015811 | 8.1188e-05 | -0.025757 | 0.0017431 | 2.8e-08 | 0.00070062 | -0.0012925 | 0.00061532 | -0.00018806 | -28.775 | 65.3824 | -57.6508 | 65.1306 | -57.399 | -57.8522 | -57.756 | -35.0372 | 65.3824 | -57.5867 | -57.5317 | -57.5363 | -57.7103 | -57.3853 | -0.10529 | 0.027466 | -0.2243 | 0.14648 | -0.21057 | -0.3067 | -0.10529 | -0.20142 | -0.041199 | 0.027466 | -122.8867 | 0.009155 | 0.16022 | -0.16479 | 0.20142 | -0.1236 | 0.25177 | 122.7814 | 0.050354 | 0.054932 | 123.0331 | 122.9691 | 122.9279 | 122.9279 | -123.0057 | -122.9416 | 122.6761 | 0.013733 | 28.7704 | 22.5082
776.1719 | 123.0515 | -57.5455 | 65.3915 | -0.091095 | -1.9142e-05 | 0.063734 | 0.064773 | 0.003151 | -0.00015811 | -0.00034601 | -0.068481 | 0.0019567 | 2.8e-08 | 0.0026232 | 0.0019119 | -0.00045288 | 0.0028027 | -29.0039 | 65.3595 | -57.6599 | 65.1077 | -57.4539 | -57.8567 | -57.7835 | -35.1654 | 65.3778 | -57.5775 | -57.4905 | -57.312 | -57.6599 | -57.399 | -0.11444 | -0.032044 | -0.28381 | 0.091553 | -0.23804 | -0.31128 | -0.1236 | -0.19684 | -0.032044 | -0.013733 | -122.8821 | 0.23346 | 0.14648 | -0.11444 | 0.17853 | -0.082397 | 0.20599 | 122.7676 | 0.2655 | 0.086975 | 123.0194 | 122.9553 | 122.905 | 122.9233 | -123.0515 | -122.9691 | 122.6532 | 0.054931 | 28.5416 | 22.3801
777.1719 | 123.0515 | -57.5409 | 65.3824 | -0.091095 | -0.0019417 | 0.06288 | 0.064559 | 0.00037377 | 5.5488e-05 | 8.1188e-05 | -0.022705 | 0.0017431 | 0.00021363 | -0.002931 | -0.00086511 | -0.0021619 | 0.00023934 | -28.9627 | 65.3687 | -57.6508 | 65.1398 | -57.3761 | -57.8293 | -57.7515 | -35.2478 | 65.4099 | -57.5775 | -57.5043 | -57.5409 | -57.692 | -57.3395 | -0.10986 | -0.013733 | -0.24261 | 0.16479 | -0.21057 | -0.28839 | -0.10071 | -0.17853 | -0.036621 | 0.027466 | -122.8867 | 0 | 0.20142 | -0.15106 | 0.23804 | -0.11444 | 0.27466 | 122.7905 | 0.036621 | 0.073243 | 123.0194 | 122.9874 | 122.9095 | 122.9507 | -123.0331 | -122.9599 | 122.6807 | 0.036622 | 28.5782 | 22.2931
778.1719 | 123.0469 | -57.5409 | 65.4053 | -0.091095 | -0.00023294 | 0.066512 | 0.061782 | 0.005928 | 0.00091009 | 0.00093559 | -0.01355 | -0.00039305 | 0.00021363 | -0.0033582 | -0.00086511 | -0.00045288 | 0.00023934 | -29.1824 | 65.387 | -57.6233 | 65.1855 | -57.3257 | -57.7469 | -57.7057 | -35.289 | 65.4099 | -57.55 | -57.4905 | -57.5089 | -57.6416 | -57.3441 | -0.082397 | -0.01831 | -0.21973 | 0.21515 | -0.16479 | -0.20599 | -0.082397 | -0.1236 | -0.009155 | 0.004578 | -122.8958 | 0.032044 | 0.19684 | -0.10071 | 0.20599 | -0.091553 | 0.29755 | 122.8088 | 0.041199 | 0.059509 | 123.0103 | 122.9599 | 122.9279 | 122.9507 | -123.0286 | -122.9553 | 122.7264 | 0.050354 | 28.3585 | 22.2519
779.1719 | 123.024 | -57.5546 | 65.3961 | -0.060578 | -0.00087374 | 0.063521 | 0.063064 | 0.00016017 | -0.0018671 | -0.00055961 | -0.053223 | 0.0015295 | 0.00085443 | 0.0054004 | 0.00020289 | -0.00023928 | 0.00066654 | -29.3243 | 65.3778 | -57.6233 | 65.1535 | -57.3395 | -57.7927 | -57.7332 | -35.4309 | 65.419 | -57.5592 | -57.518 | -57.5272 | -57.6691 | -57.3532 | -0.068665 | -0.01831 | -0.24262 | 0.21515 | -0.17853 | -0.23804 | -0.10986 | -0.16937 | -0.004578 | 0.022888 | -122.9141 | 0.027465 | 0.20142 | -0.11444 | 0.20599 | -0.10986 | 0.28381 | 122.7768 | 0.032043 | 0.041199 | 123.0011 | 122.9782 | 122.9324 | 122.9736 | -123.0194 | -122.9553 | 122.7081 | 0.036621 | 28.2303 | 22.1237
780.1875 | 123.0057 | -57.5317 | 65.4144 | -0.091095 | -0.00087374 | 0.064162 | 0.0652 | -0.00090783 | -0.0010125 | -0.00098701 | -0.028809 | -0.00039305 | 0.001068 | -0.0018628 | -1.0706e-05 | -0.0019483 | 0.0021619 | -29.4708 | 65.3549 | -57.6187 | 65.1718 | -57.3303 | -57.7744 | -57.7148 | -35.5453 | 65.4282 | -57.5684 | -57.4997 | -57.5226 | -57.6691 | -57.3486 | -0.086975 | -0.05951 | -0.24262 | 0.20142 | -0.18311 | -0.24262 | -0.096131 | -0.15564 | -0.036621 | 0.013733 | -122.9141 | 0.009155 | 0.1831 | -0.13733 | 0.21973 | -0.10071 | 0.28839 | 122.7905 | 0.045776 | 0.068664 | 122.9736 | 122.9965 | 122.8867 | 122.9599 | -123.0331 | -122.9828 | 122.7036 | 0.032043 | 28.0609 | 21.9864
781.1719 | 123.0469 | -57.5317 | 65.4144 | -0.098725 | -0.0013009 | 0.064162 | 0.063705 | 0.0016556 | -0.0010125 | -0.00098701 | -0.019653 | 0.0015295 | 0.0012818 | -0.0016492 | -0.0019333 | -2.5678e-05 | 0.0025891 | -29.6402 | 65.3595 | -57.6691 | 65.1123 | -57.3898 | -57.8156 | -57.756 | -35.6232 | 65.4144 | -57.5821 | -57.5409 | -57.4814 | -57.692 | -57.3715 | -0.13733 | -0.054932 | -0.30212 | 0.14191 | -0.2243 | -0.28381 | -0.086975 | -0.14648 | -0.050354 | 0 | -122.9553 | 0.050354 | 0.16022 | -0.16022 | 0.21057 | -0.10986 | 0.27923 | 122.7814 | 0.10071 | 0.041198 | 123.0286 | 122.9965 | 122.8912 | 122.9462 | -123.0835 | -122.9965 | 122.644 | -0.009156 | 27.8915 | 21.9086
782.1719 | 123.0515 | -57.5134 | 65.3595 | -0.11398 | -0.0015145 | 0.062239 | 0.064559 | 0.0044328 | -0.0010125 | -0.00098701 | 0.001709 | 0.0013159 | 0.003418 | -0.0014356 | -0.00043791 | -0.0028027 | -0.00061526 | -29.5212 | 65.3778 | -57.6141 | 65.1581 | -57.3761 | -57.8201 | -57.7377 | -35.8704 | 65.4007 | -57.5821 | -57.4905 | -57.518 | -57.6828 | -57.3441 | -0.10071 | 0.018311 | -0.20142 | 0.13733 | -0.2243 | -0.3067 | -0.1236 | -0.20599 | -0.068664 | 0.041199 | -122.85 | -0.004577 | 0.16937 | -0.16937 | 0.23804 | -0.10071 | 0.23804 | 122.7722 | 0.064087 | 0.091552 | 122.9919 | 122.9828 | 122.8912 | 122.9141 | -122.9736 | -122.9416 | 122.6715 | 0.022888 | 27.9922 | 21.6431
783.1719 | 123.0469 | -57.5089 | 65.419 | -0.060578 | 0.0021171 | 0.063948 | 0.063918 | 0.00037377 | 0.00048269 | -0.0018414 | -0.0074462 | 0.00046135 | 0.001068 | 0.0015552 | -0.0019333 | -0.0021619 | 0.0045117 | -29.7409 | 65.3687 | -57.6141 | 65.1993 | -57.3074 | -57.7469 | -57.6965 | -35.9161 | 65.4144 | -57.5363 | -57.4631 | -57.4905 | -57.6508 | -57.3212 | -0.10529 | -0.050354 | -0.21973 | 0.20142 | -0.18768 | -0.23804 | -0.082397 | -0.13275 | -0.027466 | -0.004577 | -122.8821 | 0.01831 | 0.18768 | -0.14191 | 0.21515 | -0.11444 | 0.3067 | 122.8134 | 0.045776 | 0.073242 | 122.9828 | 122.9507 | 122.8775 | 122.9233 | -123.0331 | -122.9553 | 122.7081 | 0.045776 | 27.7679 | 21.5927
784.1719 | 123.0286 | -57.5272 | 65.4099 | -0.052948 | 0.00062166 | 0.063094 | 0.064986 | -0.0017624 | 5.5488e-05 | 0.001363 | -0.028809 | 0.0021703 | -0.00021357 | 0.00091422 | -0.00065151 | -0.00088008 | -0.00061526 | -29.8828 | 65.387 | -57.6279 | 65.1901 | -57.3303 | -57.7698 | -57.7103 | -36.0947 | 65.4327 | -57.5592 | -57.4997 | -57.5134 | -57.6782 | -57.3532 | -0.10071 | -0.022888 | -0.21973 | 0.19684 | -0.1831 | -0.24261 | -0.082397 | -0.14191 | -0.032043 | 0.022888 | -122.9095 | 0.013733 | 0.17395 | -0.15106 | 0.20599 | -0.11902 | 0.29755 | 122.818 | 0.045776 | 0.059509 | 123.0148 | 122.9919 | 122.9141 | 122.9599 | -123.0377 | -122.9691 | 122.7173 | 0.027466 | 27.6443 | 21.4325
785.1875 | 123.0469 | -57.518 | 65.419 | -0.068207 | -0.0015145 | 0.063734 | 0.063277 | -0.001976 | -0.0018671 | -0.0024822 | 0.053589 | 0.00088875 | 0.0021362 | -0.0037854 | -0.00065151 | -0.0023755 | 0.0019483 | -29.9973 | 65.4327 | -57.5867 | 65.3549 | -57.3074 | -57.9163 | -57.7881 | -36.2823 | 65.4327 | -57.5409 | -57.4722 | -57.4585 | -57.6187 | -57.3166 | -0.068665 | 0.013733 | -0.064087 | 0.21057 | -0.27008 | -0.39825 | -0.20142 | -0.32959 | -0.022889 | 0.013733 | -122.8912 | 0.059509 | 0.20142 | -0.10071 | 0.22431 | -0.077819 | 0.27924 | 122.9416 | 0.082398 | 0.068665 | 123.0194 | 122.9736 | 122.9507 | 122.9507 | -123.0057 | -122.9599 | 122.8729 | 0.045776 | 27.5208 | 21.2357
786.1719 | 123.0835 | -57.5272 | 65.4373 | -0.098725 | -0.0010873 | 0.063094 | 0.062423 | 0.0018692 | 0.0015509 | -0.00098701 | -0.022705 | 0.00046135 | 0.00085443 | -0.0067762 | -0.00065151 | -0.0015211 | 0.00066654 | -30.1025 | 65.4099 | -57.6096 | 65.2359 | -57.2571 | -57.7148 | -57.6691 | -36.4655 | 65.4373 | -57.5043 | -57.431 | -57.5684 | -57.6828 | -57.2754 | -0.082397 | -0.027466 | -0.20142 | 0.27008 | -0.14191 | -0.18768 | -0.059509 | -0.10529 | 0.022889 | 0 | -122.8683 | -0.041198 | 0.25177 | -0.15564 | 0.22888 | -0.17853 | 0.35248 | 122.8455 | -0.064087 | 0.073242 | 123.0194 | 122.9416 | 122.937 | 122.9645 | -123.0469 | -122.9416 | 122.7631 | 0.096131 | 27.4246 | 21.0617
787.1719 | 123.0469 | -57.5043 | 65.4007 | -0.052948 | -0.00023294 | 0.065016 | 0.064345 | 0.00058737 | 0.00048269 | -0.00055961 | -0.03186 | -0.00017945 | 0.001068 | 0.002196 | -0.00086511 | -2.5678e-05 | 0.0051525 | -30.3131 | 65.387 | -57.6508 | 65.1443 | -57.3944 | -57.8293 | -57.7469 | -36.8088 | 65.4144 | -57.55 | -57.486 | -57.5134 | -57.6828 | -57.3624 | -0.14648 | -0.013733 | -0.25635 | 0.10986 | -0.24262 | -0.32501 | -0.09613 | -0.17853 | -0.045777 | 0.013733 | -122.8867 | -0.009156 | 0.14191 | -0.17853 | 0.18768 | -0.13275 | 0.25635 | 122.7951 | 0.036621 | 0.064087 | 123.0377 | 122.9645 | 122.8912 | 122.9187 | -123.0515 | -122.9507 | 122.6486 | 0.01831 | 27.1912 | 20.6955
788.1719 | 123.1018 | -57.4951 | 65.3961 | -0.075836 | 0.00019446 | 0.064589 | 0.064559 | -0.0017624 | -0.0010125 | 0.0026446 | 0.013916 | 0.00088875 | -0.0012818 | 0.00027342 | -0.00022431 | -0.0010937 | 0.0015209 | -30.4321 | 65.4007 | -57.6324 | 65.1993 | -57.3257 | -57.7652 | -57.692 | -36.9049 | 65.4007 | -57.5455 | -57.4265 | -57.4402 | -57.6187 | -57.28 | -0.13733 | 0.004578 | -0.19684 | 0.16937 | -0.19684 | -0.27008 | -0.05951 | -0.13275 | -0.050354 | 0.004578 | -122.8226 | 0.054931 | 0.21515 | -0.1236 | 0.2655 | -0.073242 | 0.3067 | 122.8317 | 0.10529 | 0.11902 | 123.0331 | 122.9462 | 122.8958 | 122.8958 | -123.0286 | -122.9416 | 122.6944 | 0.068664 | 27.063 | 20.5902
789.1719 | 123.0423 | -57.5134 | 65.4282 | -0.068207 | -0.0017281 | 0.065657 | 0.064773 | -0.00069423 | 0.00069649 | -0.00034601 | -0.016602 | 0.00046135 | 0.0025634 | -0.00058098 | -0.00086511 | 0.00040152 | 0.0013073 | -30.5832 | 65.3915 | -57.637 | 65.1764 | -57.3761 | -57.7972 | -57.7194 | -37.0422 | 65.4099 | -57.55 | -57.4997 | -57.4677 | -57.6599 | -57.3303 | -0.1236 | -0.036621 | -0.25177 | 0.13733 | -0.20599 | -0.28381 | -0.082397 | -0.16022 | -0.036621 | -0.018311 | -122.9279 | 0.045777 | 0.18311 | -0.14648 | 0.21973 | -0.10986 | 0.26092 | 122.8134 | 0.082398 | 0.050354 | 123.0286 | 122.9599 | 122.905 | 122.9233 | -123.0652 | -122.9782 | 122.6898 | 0.013733 | 26.9302 | 20.4712
790.1875 | 123.1064 | -57.4677 | 65.4465 | -0.098725 | 0.00040806 | 0.064375 | 0.064986 | 0.0037918 | 0.0013373 | 0.00072199 | 0.001709 | -0.0010339 | 0.0012818 | 5.9824e-05 | -0.00043791 | 0.0014697 | -0.0027515 | -30.6107 | 65.4007 | -57.5821 | 65.2496 | -57.2571 | -57.6874 | -57.637 | -37.1384 | 65.451 | -57.5134 | -57.4677 | -57.4493 | -57.5455 | -57.2662 | -0.11444 | -0.045776 | -0.19684 | 0.21057 | -0.16937 | -0.21973 | -0.054932 | -0.10529 | -0.045777 | 0.004578 | -122.9141 | 0.01831 | 0.20142 | -0.07782 | 0.24719 | -0.032043 | 0.32501 | 122.8317 | 0.064087 | 0.045777 | 122.9828 | 122.9645 | 122.8683 | 122.9187 | -123.0286 | -122.9599 | 122.7173 | 0 | 26.857 | 20.3293
791.1719 | 123.0743 | -57.486 | 65.419 | -0.045319 | -0.0010873 | 0.063948 | 0.062423 | 0.00058737 | 0.00026909 | -0.0014142 | 0.010864 | 0.0013159 | 0.0012818 | 0.00027342 | 0.0014847 | -0.00045288 | -0.00018806 | -30.7297 | 65.4282 | -57.5867 | 65.2542 | -57.2433 | -57.6874 | -57.637 | -37.2528 | 65.4465 | -57.486 | -57.4127 | -57.4265 | -57.5821 | -57.2662 | -0.10071 | 0.009156 | -0.16479 | 0.24262 | -0.15106 | -0.20142 | -0.050354 | -0.10071 | 0 | 0.027466 | -122.8317 | 0.059509 | 0.21973 | -0.09613 | 0.21973 | -0.09613 | 0.34332 | 122.8409 | 0.059509 | 0.073242 | 123.0148 | 122.9324 | 122.9141 | 122.9324 | -123.0057 | -122.905 | 122.7402 | 0.073242 | 26.7563 | 20.2332
792.1719 | 123.0789 | -57.4585 | 65.4556 | -0.045319 | 0.00083526 | 0.064589 | 0.063705 | 0.001442 | -0.00015811 | 0.00414 | 0.0047608 | 0.0015295 | 0.0025634 | 0.0045458 | -0.00065151 | 0.00018792 | -0.0014697 | -30.9036 | 65.4099 | -57.5775 | 65.1855 | -57.3395 | -57.6187 | -57.637 | -37.3947 | 65.4419 | -57.5043 | -57.4127 | -57.431 | -57.5821 | -57.2754 | -0.11902 | -0.045776 | -0.27008 | 0.11902 | -0.17853 | -0.16022 | -0.059509 | -0.041198 | -0.045776 | -0.013732 | -122.8683 | 0.027466 | 0.1831 | -0.1236 | 0.22888 | -0.07782 | 0.23804 | 122.7631 | 0.073242 | 0.091552 | 122.9874 | 122.9462 | 122.8683 | 122.9004 | -123.0331 | -122.9599 | 122.644 | 0.045776 | 26.5549 | 20.0638
793.1719 | 123.0377 | -57.5043 | 65.451 | -0.075836 | -0.0010873 | 0.064375 | 0.063918 | 0.00058737 | -0.00058531 | -0.0031232 | -0.0013428 | 0.0011023 | 0.0014954 | 0.0045458 | 0.00084389 | -0.00088008 | -0.00018806 | -31.073 | 65.4419 | -57.605 | 65.181 | -57.3715 | -57.7881 | -57.724 | -37.6648 | 65.4373 | -57.5317 | -57.4997 | -57.5134 | -57.6736 | -57.3349 | -0.10071 | -0.009155 | -0.27008 | 0.13275 | -0.21973 | -0.28381 | -0.11902 | -0.18311 | -0.027466 | -0.013733 | -122.9507 | -0.009156 | 0.16937 | -0.16937 | 0.19684 | -0.14191 | 0.23346 | 122.7859 | 0.01831 | 0.032043 | 123.0469 | 122.9691 | 122.9462 | 122.9416 | -123.056 | -122.9828 | 122.6852 | 0.004577 | 26.4313 | 19.8395
794.1719 | 123.0652 | -57.4631 | 65.4602 | -0.075836 | 0.0016899 | 0.063094 | 0.06285 | 0.00080117 | -0.0016535 | -0.0018414 | 0.047485 | 0.00024775 | 0.00085443 | -0.0016492 | -0.0015061 | -0.0019483 | 0.00045294 | -31.16 | 65.4144 | -57.5821 | 65.2496 | -57.2342 | -57.8613 | -57.692 | -37.6373 | 65.4739 | -57.486 | -57.3898 | -57.4127 | -57.5684 | -57.2662 | -0.11902 | -0.045776 | -0.21057 | 0.22888 | -0.22888 | -0.39825 | -0.10986 | -0.27924 | -0.022888 | 0.013733 | -122.85 | 0.050354 | 0.19684 | -0.10529 | 0.21973 | -0.082397 | 0.3479 | 122.8317 | 0.073242 | 0.09613 | 122.9965 | 122.9599 | 122.8775 | 122.937 | -123.0423 | -122.9462 | 122.7127 | 0.073242 | 26.3031 | 19.8257
795.1719 | 123.0652 | -57.486 | 65.4282 | -0.037689 | -0.0013009 | 0.061385 | 0.061996 | 0.0018692 | -0.0020807 | -0.0016278 | -0.016602 | 0.0011023 | 0.0029906 | -0.0035718 | -0.0012925 | -0.00023928 | -0.0021107 | -31.398 | 65.4053 | -57.6004 | 65.2771 | -57.3715 | -57.7606 | -57.6553 | -37.9578 | 65.4465 | -57.5089 | -57.4631 | -57.4768 | -57.637 | -57.3212 | -0.11444 | -0.022889 | -0.15106 | 0.11444 | -0.16937 | -0.27466 | -0.054931 | -0.16022 | -0.022888 | 0.01831 | -122.8912 | 0.009155 | 0.16479 | -0.15106 | 0.18768 | -0.12817 | 0.22888 | 122.8775 | 0.032043 | 0.045776 | 123.0057 | 122.9553 | 122.8912 | 122.9324 | -123.0286 | -122.937 | 122.7631 | 0.022888 | 26.088 | 19.5282
796.1719 | 123.0743 | -57.4448 | 65.4602 | -0.052948 | 0.0010489 | 0.062453 | 0.063705 | 0.0012284 | -0.00037171 | 0.00029479 | -0.016602 | 0.00046135 | 0.001709 | -0.002931 | 0.0014847 | 0.00061532 | 0.0010937 | -31.4575 | 65.4327 | -57.5684 | 65.2542 | -57.3166 | -57.7744 | -57.6645 | -37.9852 | 65.4648 | -57.5043 | -57.399 | -57.4127 | -57.5684 | -57.2617 | -0.1236 | -0.027466 | -0.20599 | 0.12817 | -0.21973 | -0.32959 | -0.096131 | -0.20599 | -0.059509 | 0.004578 | -122.8592 | 0.032043 | 0.18311 | -0.1236 | 0.24261 | -0.064087 | 0.25177 | 122.8226 | 0.091552 | 0.10529 | 123.0011 | 122.9691 | 122.8775 | 122.9095 | -123.0286 | -122.9645 | 122.699 | 0.045776 | 25.9872 | 19.4595
797.1719 | 123.0515 | -57.4493 | 65.451 | -0.045319 | -0.00023294 | 0.064162 | 0.064773 | 0.0010148 | -0.00015811 | 0.0043536 | -0.01355 | -0.00082025 | 0.00042723 | -0.00079478 | -0.0010787 | -0.0013073 | 0.0042981 | -31.6498 | 65.4556 | -57.5821 | 65.1947 | -57.312 | -57.605 | -57.6141 | -38.1729 | 65.4419 | -57.4768 | -57.3944 | -57.4127 | -57.5729 | -57.2617 | -0.13275 | 0.004577 | -0.25635 | 0.13733 | -0.1648 | -0.15564 | -0.032044 | -0.022888 | -0.027466 | -0.009155 | -122.8455 | 0.036621 | 0.18768 | -0.1236 | 0.21515 | -0.09613 | 0.27008 | 122.7768 | 0.064087 | 0.082398 | 123.0377 | 122.9187 | 122.905 | 122.8912 | -123.0331 | -122.9279 | 122.644 | 0.054932 | 25.7996 | 19.2764
798.1719 | 123.1064 | -57.4493 | 65.4694 | -0.03006 | -1.9142e-05 | 0.063734 | 0.062423 | -0.0026168 | 0.0017645 | 0.00029479 | 0.0047608 | -0.00060665 | 0.0019226 | -0.0050672 | 0.0010575 | -0.00066648 | -0.00082886 | -31.8146 | 65.4282 | -57.5638 | 65.2817 | -57.225 | -57.6462 | -57.6096 | -38.2919 | 65.4877 | -57.4677 | -57.4036 | -57.4127 | -57.5592 | -57.2479 | -0.11444 | -0.041198 | -0.18768 | 0.2243 | -0.16022 | -0.19684 | -0.045776 | -0.082397 | -0.01831 | 0.018311 | -122.8729 | 0.036621 | 0.20142 | -0.10986 | 0.21973 | -0.091553 | 0.33875 | 122.8455 | 0.054931 | 0.064087 | 122.9919 | 122.9553 | 122.8775 | 122.937 | -123.0331 | -122.937 | 122.731 | 0.045777 | 25.6348 | 19.1574
799.1719 | 123.0835 | -57.4585 | 65.4419 | -0.060578 | 0.00062166 | 0.063094 | 0.0652 | -0.0024032 | -0.00058531 | -0.0022686 | 0.013916 | 0.00046135 | 0.004486 | -0.00229 | -0.0023605 | -2.5678e-05 | 0.00045294 | -32.0068 | 65.4556 | -57.5684 | 65.2908 | -57.2113 | -57.6691 | -57.6324 | -38.4384 | 65.4877 | -57.4768 | -57.399 | -57.4173 | -57.5409 | -57.2662 | -0.10986 | 0.013732 | -0.15106 | 0.24719 | -0.17395 | -0.21057 | -0.064087 | -0.10071 | -0.018311 | 0.045776 | -122.8409 | 0.041199 | 0.19226 | -0.082398 | 0.21057 | -0.064087 | 0.35706 | 122.8592 | 0.05951 | 0.07782 | 123.024 | 122.9645 | 122.9141 | 122.9462 | -123.0103 | -122.9187 | 122.7493 | 0.059509 | 25.4517 | 19.0201
800.1719 | 123.1659 | -57.4265 | 65.4282 | -0.098725 | 0.00083526 | 0.065443 | 0.061782 | 0.003151 | 5.5488e-05 | -0.00055961 | 0.035278 | 0.00088875 | 0.00042723 | 0.00091422 | -0.0012925 | -0.0034437 | -0.00040166 | -32.1442 | 65.4007 | -57.5455 | 65.2908 | -57.1884 | -57.6416 | -57.5775 | -38.5345 | 65.4236 | -57.4814 | -57.3166 | -57.2708 | -57.4951 | -57.1976 | -0.11902 | -0.027466 | -0.13733 | 0.23804 | -0.15106 | -0.21515 | -0.032044 | -0.096131 | -0.054931 | -0.004578 | -122.7448 | 0.15564 | 0.22888 | -0.068664 | 0.28381 | -0.013733 | 0.35706 | 122.8363 | 0.21057 | 0.16479 | 122.9462 | 122.905 | 122.8271 | 122.85 | -122.9736 | -122.9095 | 122.7173 | 0.10986 | 25.2823 | 18.8919
801.1719 | 123.0057 | -57.4539 | 65.4648 | -0.022431 | -0.00023294 | 0.065016 | 0.0652 | 0.00037377 | 0.00048269 | -0.00055961 | -0.019653 | 0.0011023 | 2.8e-08 | 0.0034778 | -0.0017197 | 0.00040152 | 0.0047253 | -32.309 | 65.4327 | -57.5729 | 65.2405 | -57.2662 | -57.7103 | -57.6553 | -38.768 | 65.4968 | -57.4768 | -57.4448 | -57.4768 | -57.6096 | -57.2937 | -0.11902 | -0.032044 | -0.2243 | 0.18768 | -0.20142 | -0.25635 | -0.082397 | -0.13733 | -0.022889 | 0.032043 | -122.9095 | -0.022889 | 0.16022 | -0.15564 | 0.18311 | -0.13275 | 0.3067 | 122.8134 | 0 | 0.032044 | 123.0057 | 122.9736 | 122.8867 | 122.9507 | -123.0377 | -122.9416 | 122.6944 | 0.009155 | 25.145 | 18.6859
802.1719 | 123.0606 | -57.4951 | 65.4602 | -0.10635 | -0.0021555 | 0.063521 | 0.062423 | -0.00026703 | 0.00026909 | -0.0012006 | 0.0047608 | 0.00088875 | 0.001068 | 0.0030506 | -0.00022431 | -0.0025891 | -0.00018806 | -32.5104 | 65.451 | -57.5592 | 65.2176 | -57.3074 | -57.7194 | -57.6599 | -38.9328 | 65.4694 | -57.4997 | -57.4219 | -57.4402 | -57.6141 | -57.2845 | -0.064087 | -0.009155 | -0.24262 | 0.18768 | -0.16479 | -0.2243 | -0.10071 | -0.16022 | -0.004578 | 0.009155 | -122.8821 | 0.054931 | 0.21057 | -0.11902 | 0.21515 | -0.11444 | 0.25177 | 122.7768 | 0.059509 | 0.07782 | 123.0103 | 122.9691 | 122.9462 | 122.9645 | -123.0194 | -122.9599 | 122.7127 | 0.073242 | 24.9847 | 18.5623
803.1719 | 123.0515 | -57.4677 | 65.4465 | -0.10635 | -0.00023294 | 0.063734 | 0.064773 | -0.00069423 | -0.0022943 | -0.00055961 | -0.01355 | -0.00017945 | -0.00085457 | 0.00091422 | -0.0010787 | -0.0015211 | -0.0018971 | -32.6157 | 65.4327 | -57.5729 | 65.2222 | -57.2891 | -57.7469 | -57.6645 | -39.0564 | 65.4739 | -57.4814 | -57.4127 | -57.4402 | -57.6096 | -57.28 | -0.10529 | -0.013733 | -0.2243 | 0.17853 | -0.19684 | -0.27924 | -0.091553 | -0.17395 | -0.013733 | 0.027466 | -122.8592 | 0.027465 | 0.18768 | -0.14191 | 0.20142 | -0.12817 | 0.28381 | 122.7951 | 0.041198 | 0.068664 | 123.0057 | 122.9553 | 122.9004 | 122.9416 | -123.0194 | -122.9279 | 122.6898 | 0.054931 | 24.852 | 18.4113
804.1719 | 123.0606 | -57.4356 | 65.4785 | -0.060578 | 0.00040806 | 0.062239 | 0.067763 | 0.0016556 | 0.0026191 | 0.001363 | -0.022705 | 0.0017431 | 0.0021362 | -0.007417 | -0.0023605 | -0.0021619 | -0.0018971 | -32.5333 | 65.4694 | -57.5455 | 65.2863 | -57.225 | -57.6599 | -57.6096 | -39.1159 | 65.4968 | -57.4585 | -57.3761 | -57.4173 | -57.5592 | -57.2388 | -0.10986 | -0.009156 | -0.19226 | 0.21057 | -0.17395 | -0.2243 | -0.064087 | -0.11444 | -0.022888 | 0.01831 | -122.8546 | 0.018311 | 0.19684 | -0.1236 | 0.21973 | -0.10071 | 0.32043 | 122.8317 | 0.041199 | 0.082397 | 123.0148 | 122.9553 | 122.905 | 122.9324 | -123.024 | -122.937 | 122.7219 | 0.059509 | 24.9023 | 18.3197
805.1719 | 123.1476 | -57.4265 | 65.4236 | -0.083466 | 0.00062166 | 0.063094 | 0.063064 | -0.0034714 | -0.00015811 | -0.002696 | 0.029175 | -0.00017945 | 2.8e-08 | 0.0047594 | -0.0030013 | 0.00061532 | -0.0025379 | -32.7072 | 65.4236 | -57.5363 | 65.2725 | -57.2296 | -57.6782 | -57.6096 | -39.2349 | 65.4373 | -57.4493 | -57.3349 | -57.3486 | -57.518 | -57.1701 | -0.10986 | 0 | -0.15106 | 0.19684 | -0.1831 | -0.25177 | -0.073242 | -0.14191 | -0.022888 | 0.013733 | -122.7585 | 0.07782 | 0.25635 | -0.091552 | 0.27924 | -0.068664 | 0.3067 | 122.8088 | 0.10071 | 0.11444 | 122.9599 | 122.8867 | 122.85 | 122.8638 | -122.9599 | -122.8729 | 122.699 | 0.091553 | 24.7192 | 18.1915
806.1719 | 123.0331 | -57.431 | 65.4739 | -0.13687 | -1.9142e-05 | 0.062666 | 0.063277 | -5.343e-05 | 0.00091009 | 0.0015766 | -0.034912 | 0.0023839 | 0.0023498 | -0.0025036 | -0.0023605 | -0.0015211 | 0.0032299 | -32.7988 | 65.4602 | -57.5592 | 65.2267 | -57.2891 | -57.7011 | -57.6416 | -39.4272 | 65.5014 | -57.5089 | -57.399 | -57.4356 | -57.5912 | -57.2571 | -0.12817 | -0.013733 | -0.24719 | 0.14191 | -0.21057 | -0.27008 | -0.082398 | -0.14191 | -0.07782 | 0.027466 | -122.8729 | -0.004578 | 0.17395 | -0.16022 | 0.25177 | -0.082398 | 0.27008 | 122.786 | 0.073242 | 0.10986 | 123.0194 | 123.0103 | 122.8912 | 122.9324 | -123.0331 | -122.9828 | 122.6578 | 0.032043 | 24.6323 | 18.0038
807.1719 | 123.0377 | -57.4402 | 65.5014 | -0.075836 | 0.0023307 | 0.063094 | 0.063918 | 0.0027238 | -0.00058531 | 0.00050839 | -0.03186 | 0.00046135 | 0.0014954 | 0.002196 | 0.00041649 | -0.0015211 | -0.0025379 | -33.0734 | 65.4556 | -57.5272 | 65.2542 | -57.2479 | -57.6874 | -57.6462 | -39.5187 | 65.506 | -57.4722 | -57.4127 | -57.431 | -57.6141 | -57.2708 | -0.086975 | -0.045777 | -0.24719 | 0.19226 | -0.20599 | -0.24719 | -0.11902 | -0.16022 | -0.032043 | 0.004577 | -122.9141 | 0.009156 | 0.16937 | -0.17395 | 0.20142 | -0.14191 | 0.27924 | 122.7814 | 0.041199 | 0.059509 | 122.9828 | 122.9782 | 122.8958 | 122.9462 | -123.0286 | -122.9736 | 122.6944 | 0.027466 | 24.3668 | 17.9214
808.1719 | 123.0331 | -57.4493 | 65.4785 | -0.068207 | 0.0014761 | 0.06523 | 0.065414 | 0.0018692 | 0.00026909 | -0.0029096 | -0.0074462 | 0.0011023 | 0.00085443 | -0.00015378 | -0.00065151 | -0.00045288 | 0.00045294 | -33.1787 | 65.4785 | -57.55 | 65.2451 | -57.2388 | -57.7011 | -57.6324 | -39.6286 | 65.506 | -57.4677 | -57.4127 | -57.4356 | -57.6187 | -57.2708 | -0.10071 | 0 | -0.23346 | 0.21057 | -0.18311 | -0.25177 | -0.082397 | -0.15106 | -0.01831 | 0.027465 | -122.8912 | 0.013733 | 0.17853 | -0.16937 | 0.19684 | -0.15106 | 0.31128 | 122.7951 | 0.032043 | 0.054931 | 123.0286 | 122.9736 | 122.9279 | 122.9553 | -123.0286 | -122.9462 | 122.6944 | 0.036621 | 24.2706 | 17.8207
809.1719 | 123.0423 | -57.4356 | 65.5106 | -0.083466 | 0.0012625 | 0.064162 | 0.063277 | -0.0028304 | 0.0015509 | 0.0011494 | -0.028809 | -0.0012477 | 0.0012818 | 0.0047594 | -0.0021469 | -0.0028027 | -0.0018971 | -33.3481 | 65.4694 | -57.5638 | 65.2039 | -57.3257 | -57.7515 | -57.6599 | -39.7888 | 65.4922 | -57.4768 | -57.2708 | -57.4722 | -57.6141 | -57.2662 | -0.12817 | -0.041199 | -0.3067 | 0.10986 | -0.2243 | -0.31586 | -0.09613 | -0.18768 | -0.041199 | -0.01831 | -122.7814 | -0.036621 | 0.16937 | -0.17853 | 0.21057 | -0.13733 | 0.23804 | 122.7676 | 0.004578 | 0.20599 | 123.0331 | 122.9691 | 122.905 | 122.9279 | -123.0743 | -122.9874 | 122.6395 | 0.1648 | 24.0875 | 17.6468
810.1719 | 123.1705 | -57.3807 | 65.4556 | -0.068207 | -0.0030099 | 0.062239 | 0.059859 | -0.00069423 | -0.00079891 | -0.0035504 | 0.093262 | -0.0012477 | 0.00085443 | -0.0016492 | 0.00020289 | -0.0019483 | 0.0021619 | -33.3939 | 65.4556 | -57.4722 | 65.3503 | -57.1289 | -57.5684 | -57.4951 | -39.7202 | 65.4877 | -57.4173 | -57.2937 | -57.2617 | -57.4173 | -57.1426 | -0.091553 | 0 | -0.10529 | 0.25177 | -0.11444 | -0.18768 | -0.022888 | -0.09613 | -0.036621 | 0.032044 | -122.7493 | 0.11902 | 0.23804 | -0.036621 | 0.27466 | 0 | 0.34332 | 122.8226 | 0.15564 | 0.1236 | 122.9279 | 122.905 | 122.8363 | 122.8683 | -122.9279 | -122.8729 | 122.731 | 0.086975 | 23.9868 | 17.6605
811.1719 | 123.0835 | -57.3715 | 65.4968 | -0.091095 | 0.00019446 | 0.064162 | 0.059859 | 0.0016556 | 0.00048269 | 8.1188e-05 | 0.074951 | 0.0019567 | 0.001709 | -0.00036738 | -0.0019333 | -0.0019483 | -0.0010425 | -33.5358 | 65.4602 | -57.4905 | 65.3 | -57.1884 | -57.6141 | -57.5134 | -39.8987 | 65.4877 | -57.4448 | -57.3212 | -57.3166 | -57.4631 | -57.1793 | -0.11902 | -0.036621 | -0.19684 | 0.18311 | -0.14191 | -0.24262 | -0.022888 | -0.1236 | -0.073242 | -0.009155 | -122.818 | 0.054932 | 0.19226 | -0.091553 | 0.2655 | -0.018311 | 0.30212 | 122.7905 | 0.12817 | 0.1236 | 122.9507 | 122.9324 | 122.8317 | 122.8592 | -122.9874 | -122.9416 | 122.6715 | 0.050354 | 23.8358 | 17.4728
812.1719 | 123.0698 | -57.4173 | 65.5243 | -0.068207 | -1.9142e-05 | 0.063734 | 0.065627 | 0.0040054 | -0.00015811 | 0.0015766 | -0.056274 | 0.0011023 | 2.8e-08 | 0.0036914 | -0.0027877 | -0.0038709 | -0.00082886 | -33.7097 | 65.4694 | -57.5455 | 65.2222 | -57.3074 | -57.7286 | -57.6324 | -40.1001 | 65.5151 | -57.4768 | -57.2708 | -57.4539 | -57.6141 | -57.2571 | -0.12817 | -0.054932 | -0.30212 | 0.10986 | -0.21515 | -0.31128 | -0.086975 | -0.18311 | -0.05951 | -0.009155 | -122.7951 | -0.036621 | 0.16022 | -0.19684 | 0.21973 | -0.13733 | 0.23804 | 122.7676 | 0.022889 | 0.20599 | 123.0148 | 122.9919 | 122.8867 | 122.9324 | -123.0698 | -123.0011 | 122.6395 | 0.14648 | 23.7076 | 17.3172
813.1719 | 123.1064 | -57.3853 | 65.4556 | -0.11398 | -0.0023691 | 0.064162 | 0.065841 | 0.0016556 | 0.00026909 | -0.0039776 | 0.0047608 | 0.0011023 | 0.001068 | 5.9824e-05 | -0.0021469 | -0.0042981 | 0.0017345 | -33.8242 | 65.4602 | -57.5226 | 65.3183 | -57.1793 | -57.637 | -57.55 | -40.1138 | 65.4739 | -57.4448 | -57.2937 | -57.3074 | -57.4631 | -57.1381 | -0.13733 | 0.004578 | -0.13733 | 0.20599 | -0.16479 | -0.25177 | -0.027466 | -0.11444 | -0.059509 | 0.018311 | -122.7493 | 0.07782 | 0.24719 | -0.07782 | 0.3067 | -0.018311 | 0.34332 | 122.8409 | 0.13733 | 0.15106 | 122.9828 | 122.9187 | 122.8455 | 122.8592 | -122.9782 | -122.9004 | 122.7036 | 0.091553 | 23.5611 | 17.2714
814.1719 | 123.0286 | -57.4219 | 65.5243 | -0.068207 | -0.00023294 | 0.065016 | 0.066695 | 0.00058737 | -0.00037171 | -0.00055961 | -0.059326 | 3.4148e-05 | -0.00042717 | -0.00079478 | -0.0025741 | -0.0023755 | 0.0062207 | -33.9661 | 65.4785 | -57.5363 | 65.2451 | -57.2845 | -57.7103 | -57.637 | -40.3427 | 65.5014 | -57.4677 | -57.3944 | -57.4173 | -57.5684 | -57.2479 | -0.11444 | -0.045776 | -0.27924 | 0.13733 | -0.21515 | -0.28839 | -0.10071 | -0.17395 | -0.045776 | -0.022888 | -122.9187 | 0.004578 | 0.17395 | -0.14648 | 0.21973 | -0.10071 | 0.25177 | 122.7814 | 0.050354 | 0.073242 | 123.0148 | 122.9691 | 122.9004 | 122.9233 | -123.0606 | -122.9919 | 122.6669 | 0.027466 | 23.4558 | 17.0792
815.1719 | 123.1247 | -57.4036 | 65.5106 | -0.098725 | -0.00066014 | 0.063094 | 0.061141 | -0.00090783 | 0.0019781 | -0.0016278 | 0.078003 | 0.0019567 | -0.00064077 | -0.0014356 | -1.0706e-05 | -0.0030163 | 0.0028027 | -33.9523 | 65.5106 | -57.4722 | 65.3458 | -57.1381 | -57.5729 | -57.5226 | -40.3381 | 65.4968 | -57.4356 | -57.3029 | -57.2845 | -57.4493 | -57.1793 | -0.068665 | 0 | -0.16479 | 0.2655 | -0.11902 | -0.16937 | -0.050354 | -0.10071 | -0.032044 | -0.013733 | -122.8134 | 0.11902 | 0.2243 | -0.045777 | 0.25635 | -0.013733 | 0.33417 | 122.818 | 0.15106 | 0.13275 | 122.9828 | 122.9324 | 122.9141 | 122.9004 | -122.9828 | -122.9462 | 122.7493 | 0.10071 | 23.4512 | 17.0654
816.1719 | 123.1384 | -57.3669 | 65.506 | -0.098725 | 0.00019446 | 0.064375 | 0.061782 | -0.0038986 | -0.0010125 | 0.00029479 | 0.053589 | -0.00039305 | 0.0019226 | -0.00229 | -0.00043791 | -0.0032301 | 0.00088014 | -34.1492 | 65.4877 | -57.4722 | 65.3824 | -57.1198 | -57.5317 | -57.4722 | -40.3976 | 65.5106 | -57.3761 | -57.2479 | -57.2433 | -57.3944 | -57.1243 | -0.10529 | -0.01831 | -0.1236 | 0.24719 | -0.10529 | -0.16479 | 0 | -0.059509 | -0.009156 | 0.004578 | -122.7539 | 0.1236 | 0.24261 | -0.027466 | 0.25177 | -0.01831 | 0.35248 | 122.8546 | 0.13275 | 0.12817 | 122.9599 | 122.8867 | 122.8546 | 122.8775 | -122.9782 | -122.8821 | 122.7493 | 0.11902 | 23.2178 | 16.9693
817.1719 | 123.1155 | -57.3853 | 65.4831 | -0.1445 | -0.00023294 | 0.062025 | 0.061996 | 0.0022964 | 0.00048269 | -0.00077341 | -0.03186 | 0.0017431 | 0.00064083 | 0.0026232 | -0.0015061 | -0.00066648 | -0.00040166 | -34.3369 | 65.451 | -57.5134 | 65.3366 | -57.1564 | -57.6279 | -57.5775 | -40.5579 | 65.4968 | -57.431 | -57.2708 | -57.312 | -57.4631 | -57.1381 | -0.12817 | -0.032043 | -0.14648 | 0.22888 | -0.19226 | -0.24261 | -0.064087 | -0.11444 | -0.045776 | 0.013733 | -122.7539 | 0.073242 | 0.24719 | -0.07782 | 0.29297 | -0.032044 | 0.35706 | 122.85 | 0.11902 | 0.16022 | 122.9645 | 122.9279 | 122.8363 | 122.8821 | -122.9965 | -122.9141 | 122.7219 | 0.11444 | 23.0484 | 16.8274
818.1719 | 123.1064 | -57.3853 | 65.4694 | -0.045319 | -1.9142e-05 | 0.065871 | 0.065627 | -0.0028304 | -0.00079891 | -0.00013241 | -0.019653 | 3.4148e-05 | -0.0010682 | 0.0013416 | -0.0032151 | -0.0019483 | -0.0025379 | -34.4696 | 65.4602 | -57.5043 | 65.3366 | -57.1564 | -57.6233 | -57.55 | -40.686 | 65.4785 | -57.4219 | -57.2662 | -57.2937 | -57.4677 | -57.1243 | -0.11902 | -0.009155 | -0.13275 | 0.22888 | -0.16479 | -0.23804 | -0.045777 | -0.11902 | -0.036621 | 0.009156 | -122.7356 | 0.091553 | 0.26093 | -0.082397 | 0.29755 | -0.045776 | 0.3479 | 122.8409 | 0.12817 | 0.15564 | 122.9645 | 122.9004 | 122.8455 | 122.8638 | -122.9736 | -122.8912 | 122.7219 | 0.11902 | 22.9157 | 16.6992
819.1719 | 123.1476 | -57.3578 | 65.4465 | -0.11398 | 0.0016899 | 0.063521 | 0.06285 | -0.00048063 | 0.00026909 | 0.001363 | -0.022705 | -0.00082025 | 0.00042723 | 0.001128 | -1.0706e-05 | -0.0019483 | 0.0025891 | -34.5978 | 65.4648 | -57.486 | 65.3503 | -57.1518 | -57.605 | -57.518 | -40.8051 | 65.5106 | -57.4127 | -57.2662 | -57.28 | -57.4585 | -57.1335 | -0.12817 | 0.018311 | -0.09613 | 0.20599 | -0.16022 | -0.24719 | -0.032043 | -0.11902 | -0.054932 | 0.064087 | -122.7127 | 0.07782 | 0.2243 | -0.10071 | 0.27924 | -0.045776 | 0.33417 | 122.8363 | 0.13275 | 0.14648 | 122.9507 | 122.9233 | 122.8226 | 122.8683 | -122.9324 | -122.8592 | 122.7081 | 0.091553 | 22.76 | 16.5527
820.1719 | 123.1064 | -57.3578 | 65.4877 | -0.11398 | 0.00062166 | 0.066725 | 0.061141 | -0.00069423 | -0.0014399 | -0.0024822 | 0.053589 | -0.0010339 | 2.8e-08 | -0.0052808 | -0.0012925 | -0.0015211 | 0.0021619 | -34.7443 | 65.4785 | -57.4631 | 65.3595 | -57.1289 | -57.5958 | -57.5089 | -40.9286 | 65.506 | -57.399 | -57.2845 | -57.28 | -57.4265 | -57.1564 | -0.10529 | -0.009155 | -0.12817 | 0.22888 | -0.15106 | -0.23804 | -0.045776 | -0.13275 | -0.041199 | 0.01831 | -122.7722 | 0.07782 | 0.20142 | -0.068665 | 0.24262 | -0.027466 | 0.33417 | 122.8226 | 0.11902 | 0.11444 | 122.9416 | 122.905 | 122.8363 | 122.8638 | -122.9507 | -122.8867 | 122.7173 | 0.073242 | 22.6135 | 16.4291
821.1719 | 123.0194 | -57.3578 | 65.5975 | -0.060578 | -0.0036507 | 0.06288 | 0.063918 | 0.0027238 | -0.0010125 | -0.0018414 | -0.01355 | -0.00060665 | 0.00042723 | 0.0049732 | -0.0025741 | -0.0030163 | -0.00082886 | -34.8541 | 65.5655 | -57.4402 | 65.332 | -57.1518 | -57.5729 | -57.5272 | -41.0522 | 65.5884 | -57.3898 | -57.3074 | -57.3853 | -57.28 | -57.0328 | -0.082398 | -0.032043 | -0.2655 | 0.20599 | -0.16937 | -0.21515 | -0.086975 | -0.13275 | -0.032044 | -0.009155 | -122.905 | -0.027466 | 0.32501 | 0.07782 | 0.35706 | 0.10986 | 0.28839 | 122.7722 | 0.004578 | 0.082398 | 123.0057 | 122.9782 | 122.9233 | 122.9462 | -123.0377 | -122.9874 | 122.6898 | 0.050354 | 22.5037 | 16.3055
822.1719 | 123.0698 | -57.3853 | 65.5701 | -0.075836 | -0.00066014 | 0.065657 | 0.064986 | 0.0027238 | -0.0018671 | -0.00055961 | -0.050171 | 0.0015295 | 0.00064083 | -0.002931 | -1.0706e-05 | -0.00066648 | -0.0040333 | -35.0189 | 65.5197 | -57.5134 | 65.2771 | -57.2708 | -57.7011 | -57.6096 | -41.2674 | 65.5609 | -57.4402 | -57.2754 | -57.2205 | -57.55 | -57.2571 | -0.12817 | -0.050354 | -0.29297 | 0.11444 | -0.2243 | -0.31586 | -0.09613 | -0.18768 | -0.054932 | -0.009155 | -122.8455 | 0.1648 | 0.12817 | -0.16479 | 0.18311 | -0.10986 | 0.24262 | 122.7905 | 0.21973 | 0.16479 | 123.0331 | 123.0011 | 122.905 | 122.9462 | -123.0835 | -123.0103 | 122.6624 | 0.10986 | 22.3663 | 16.1179
823.1719 | 123.0927 | -57.3349 | 65.5151 | -0.16739 | 0.00062166 | 0.063521 | 0.063064 | 0.00016017 | -0.00037171 | -0.0022686 | 0.013916 | -0.0014613 | 0.00021363 | -0.0059216 | -1.0706e-05 | -0.0030163 | 0.0015209 | -35.083 | 65.4694 | -57.4585 | 65.4007 | -57.0648 | -57.55 | -57.4814 | -41.2216 | 65.5151 | -57.4036 | -57.2433 | -57.2754 | -57.431 | -57.1381 | -0.1236 | -0.045777 | -0.11444 | 0.27008 | -0.14648 | -0.21515 | -0.022888 | -0.091553 | -0.068664 | 0 | -122.7585 | 0.059509 | 0.19684 | -0.09613 | 0.2655 | -0.027466 | 0.39368 | 122.8592 | 0.12817 | 0.16022 | 122.9279 | 122.9187 | 122.8043 | 122.85 | -122.9736 | -122.9187 | 122.7356 | 0.091553 | 22.2519 | 16.1133
824.1719 | 123.0789 | -57.3944 | 65.5151 | -0.083466 | 0.00040806 | 0.063948 | 0.065627 | -5.343e-05 | -0.00015811 | -0.00034601 | -0.059326 | -0.0014613 | 0.00021363 | -0.00229 | -0.00043791 | -0.0015211 | -0.0014697 | -35.257 | 65.5014 | -57.4905 | 65.2908 | -57.2021 | -57.6508 | -57.5729 | -41.4642 | 65.5746 | -57.4219 | -57.2983 | -57.3441 | -57.5089 | -57.2021 | -0.096131 | -0.013733 | -0.2243 | 0.19226 | -0.17853 | -0.25635 | -0.082397 | -0.16022 | -0.027466 | 0.059509 | -122.8134 | 0.050354 | 0.19226 | -0.11444 | 0.21973 | -0.086975 | 0.28839 | 122.7814 | 0.07782 | 0.1236 | 122.9919 | 122.9965 | 122.8958 | 122.9691 | -123.0057 | -122.937 | 122.6852 | 0.09613 | 22.1375 | 15.9302
825.1719 | 123.1018 | -57.3395 | 65.5197 | -0.12161 | 0.00019446 | 0.063307 | 0.059432 | 0.0029374 | 0.00026909 | -0.00034601 | 0.044434 | -0.00082025 | 0.00021363 | -0.0016492 | 0.00041649 | -0.0028027 | -0.0031787 | -35.3531 | 65.5334 | -57.4356 | 65.3778 | -57.1381 | -57.5363 | -57.486 | -41.5283 | 65.5838 | -57.3944 | -57.2479 | -57.2525 | -57.4127 | -57.1198 | -0.09613 | 0.013733 | -0.14191 | 0.20142 | -0.14648 | -0.19684 | -0.050354 | -0.10071 | -0.054931 | 0.064087 | -122.7676 | 0.086976 | 0.21973 | -0.073242 | 0.27466 | -0.018311 | 0.29755 | 122.8134 | 0.14191 | 0.14648 | 122.9691 | 122.9782 | 122.8729 | 122.9233 | -122.9553 | -122.9141 | 122.7173 | 0.091553 | 21.9864 | 15.8112
826.1719 | 122.9553 | -57.312 | 65.6113 | -0.075836 | -0.0036507 | 0.063307 | 0.064559 | -0.00048063 | -0.00058531 | -0.00034601 | 0.001709 | 0.00088875 | -0.001709 | 0.0047594 | -1.0706e-05 | -0.0036573 | 0.0025891 | -35.4767 | 65.5655 | -57.4493 | 65.3549 | -57.1335 | -57.5684 | -57.4997 | -41.6245 | 65.6113 | -57.3441 | -57.2937 | -57.2296 | -57.2067 | -57.1289 | -0.13733 | -0.045776 | -0.25635 | 0.17853 | -0.18768 | -0.25635 | -0.050354 | -0.11902 | -0.032043 | 0 | -122.905 | 0.082398 | 0.18311 | 0.10529 | 0.21515 | 0.13733 | 0.31586 | 122.8043 | 0.11444 | 0.050354 | 123.0148 | 122.9553 | 122.8775 | 122.9233 | -123.0606 | -122.9553 | 122.6669 | 0.018311 | 21.8353 | 15.6876
827.1719 | 123.1476 | -57.3441 | 65.5151 | -0.11398 | 0.0014761 | 0.063307 | 0.064559 | 0.00251 | 5.5488e-05 | 0.00029479 | -0.034912 | 0.00046135 | 0.0021362 | 0.003905 | -0.00065151 | -2.5678e-05 | 0.0013073 | -35.5774 | 65.5106 | -57.4631 | 65.3778 | -57.1243 | -57.5775 | -57.5134 | -41.7114 | 65.5334 | -57.3853 | -57.2067 | -57.2525 | -57.431 | -57.0969 | -0.11902 | -0.004578 | -0.13733 | 0.21973 | -0.16937 | -0.23346 | -0.050354 | -0.11444 | -0.041199 | 0.01831 | -122.7219 | 0.091553 | 0.24719 | -0.086975 | 0.28839 | -0.045776 | 0.33874 | 122.8409 | 0.13275 | 0.17853 | 122.9736 | 122.9187 | 122.8546 | 122.8775 | -122.9782 | -122.9004 | 122.7219 | 0.13733 | 21.7667 | 15.6326
828.1719 | 123.143 | -57.3349 | 65.5243 | -0.052948 | 0.0016899 | 0.064589 | 0.063918 | 0.00058737 | 0.00069649 | 0.0020038 | -0.028809 | -0.00017945 | 0.00085443 | -0.0072034 | -0.00043791 | -0.00066648 | 0.0023755 | -35.6918 | 65.5243 | -57.4585 | 65.3687 | -57.1289 | -57.5958 | -57.4951 | -41.8488 | 65.5426 | -57.3761 | -57.2113 | -57.2571 | -57.4036 | -57.0969 | -0.1236 | 0 | -0.15564 | 0.20599 | -0.16022 | -0.26093 | -0.036621 | -0.13733 | -0.041199 | 0.018311 | -122.7356 | 0.07782 | 0.23804 | -0.068664 | 0.27924 | -0.027465 | 0.32959 | 122.8271 | 0.11902 | 0.1648 | 122.9828 | 122.9187 | 122.8592 | 122.8775 | -122.9828 | -122.9004 | 122.7036 | 0.1236 | 21.6431 | 15.4861
829.1719 | 123.1476 | -57.2983 | 65.5014 | -0.083466 | -0.00044654 | 0.065016 | 0.060714 | -0.0024032 | 0.00026909 | 0.002431 | -0.022705 | 0.00088875 | -0.0027772 | -0.0014356 | -0.0012925 | -0.00066648 | -0.00040166 | -35.733 | 65.4877 | -57.4493 | 65.419 | -57.0602 | -57.5317 | -57.4585 | -41.8762 | 65.5518 | -57.3944 | -57.225 | -57.1289 | -57.2388 | -57.0419 | -0.15106 | -0.013733 | -0.082398 | 0.23804 | -0.16022 | -0.23346 | -0.009155 | -0.082397 | -0.09613 | 0.050354 | -122.7264 | 0.16937 | 0.25635 | 0.059509 | 0.35248 | 0.15564 | 0.3891 | 122.8683 | 0.2655 | 0.16937 | 122.937 | 122.9462 | 122.786 | 122.85 | -122.9507 | -122.8958 | 122.7173 | 0.073242 | 21.5652 | 15.4221
830.1719 | 123.1338 | -57.3074 | 65.5746 | -0.075836 | -1.9142e-05 | 0.063521 | 0.063918 | 0.0037918 | -0.00058531 | -0.00013241 | -0.053223 | -0.0014613 | -0.00064077 | -0.0069898 | -0.00065151 | -0.0028027 | -0.0023243 | -35.8292 | 65.5518 | -57.4036 | 65.4831 | -57.0374 | -57.0007 | -57.2433 | -41.9083 | 65.5701 | -57.3349 | -57.1655 | -57.1426 | -57.3074 | -57.0557 | -0.09613 | -0.022888 | -0.091553 | 0.27008 | 0.064087 | 0.3067 | 0.16022 | 0.40283 | -0.027466 | -0.004578 | -122.7402 | 0.16479 | 0.25177 | 0 | 0.27924 | 0.027466 | 0.36621 | 122.8867 | 0.19226 | 0.16937 | 122.9553 | 122.905 | 122.8592 | 122.8775 | -122.9782 | -122.9095 | 122.7905 | 0.14191 | 21.4783 | 15.3992
831.1719 | 123.0927 | -57.28 | 65.5975 | -0.091095 | -0.00066014 | 0.06288 | 0.061996 | 0.0012284 | -0.0010125 | 0.00029479 | 0.02002 | 0.00067495 | -0.0010682 | 0.0036914 | -0.0040695 | -2.5678e-05 | -0.0033923 | -35.939 | 65.5518 | -57.4127 | 65.4602 | -57.0053 | -57.431 | -57.3715 | -42.0593 | 65.5884 | -57.3257 | -57.1976 | -57.1884 | -57.3395 | -57.1014 | -0.13275 | -0.045776 | -0.13733 | 0.27466 | -0.091553 | -0.15106 | 0.041199 | -0.01831 | -0.045777 | -0.009155 | -122.7951 | 0.091552 | 0.17853 | -0.05951 | 0.22431 | -0.013733 | 0.40741 | 122.8729 | 0.13733 | 0.12817 | 122.9645 | 122.9141 | 122.8317 | 122.8683 | -123.0103 | -122.9233 | 122.7402 | 0.082397 | 21.3409 | 15.2206
832.1719 | 123.0927 | -57.3257 | 65.5838 | -0.045319 | 0.00040806 | 0.063734 | 0.064773 | 0.00251 | -0.00015811 | -0.00077341 | -0.056274 | 0.0013159 | -0.001709 | -0.0020764 | -0.0021469 | -0.00023928 | -0.0016833 | -36.1359 | 65.5289 | -57.4768 | 65.3458 | -57.1518 | -57.6279 | -57.518 | -42.3019 | 65.5655 | -57.3578 | -57.2479 | -57.2754 | -57.4356 | -57.1381 | -0.15106 | -0.054931 | -0.23804 | 0.17395 | -0.19226 | -0.30212 | -0.041198 | -0.15106 | -0.032043 | -0.01831 | -122.8317 | 0.050354 | 0.18768 | -0.10986 | 0.21973 | -0.07782 | 0.32501 | 122.8226 | 0.082397 | 0.10986 | 123.0057 | 122.9233 | 122.8546 | 122.8912 | -123.0606 | -122.9416 | 122.6715 | 0.07782 | 21.1899 | 15.0238
833.1719 | 123.1384 | -57.312 | 65.5151 | -0.098725 | 0.0014761 | 0.063948 | 0.064345 | -0.00026703 | 0.00026909 | -0.0014142 | -0.028809 | 0.0013159 | 0.00042723 | -0.006349 | -0.00065151 | -0.0010937 | -0.0025379 | -36.2137 | 65.5289 | -57.431 | 65.4053 | -57.0831 | -57.5409 | -57.4539 | -42.3111 | 65.5609 | -57.3578 | -57.1793 | -57.2113 | -57.3715 | -57.0511 | -0.11902 | 0.013733 | -0.10986 | 0.22888 | -0.14191 | -0.22888 | -0.022888 | -0.10986 | -0.045776 | 0.045776 | -122.6944 | 0.10071 | 0.26093 | -0.059509 | 0.3067 | -0.013733 | 0.3479 | 122.8363 | 0.14648 | 0.17853 | 122.9599 | 122.9187 | 122.8409 | 122.8729 | -122.9462 | -122.8729 | 122.7173 | 0.13275 | 21.0983 | 15.0009
834.1719 | 123.1522 | -57.312 | 65.5243 | -0.10635 | 0.0014761 | 0.064803 | 0.061568 | 0.0018692 | 0.0011237 | -0.0014142 | 0.035278 | 0.0017431 | 0.0019226 | 0.0047594 | -0.0032151 | -0.0021619 | -0.0021107 | -36.2778 | 65.5151 | -57.4356 | 65.4785 | -57.1243 | -57.7423 | -57.3624 | -42.4026 | 65.5472 | -57.3532 | -57.1747 | -57.2021 | -57.3624 | -57.0602 | -0.1236 | -0.009155 | -0.045776 | 0.18768 | -0.050354 | -0.4303 | 0.073242 | -0.3067 | -0.041198 | 0.022888 | -122.699 | 0.10986 | 0.25177 | -0.050354 | 0.29297 | -0.009156 | 0.31128 | 122.9141 | 0.15106 | 0.17853 | 122.9507 | 122.9004 | 122.8271 | 122.8592 | -122.9599 | -122.8775 | 122.7905 | 0.13733 | 21.0342 | 14.9094
835.1719 | 123.143 | -57.2983 | 65.5518 | -0.12924 | -0.0025827 | 0.06523 | 0.066054 | -0.00026703 | 0.0013373 | 0.00029479 | -0.022705 | -0.00060665 | 0.00021363 | -0.00015378 | -0.0012925 | 0.00018792 | -0.0029651 | -36.438 | 65.5334 | -57.4356 | 65.4007 | -57.0648 | -57.5363 | -57.4493 | -42.5446 | 65.5609 | -57.3578 | -57.1609 | -57.2067 | -57.3807 | -57.0465 | -0.13733 | -0.018311 | -0.15106 | 0.23346 | -0.15106 | -0.23804 | -0.013733 | -0.10071 | -0.059509 | 0.009155 | -122.7127 | 0.091553 | 0.25177 | -0.082397 | 0.31128 | -0.022888 | 0.37079 | 122.8363 | 0.15106 | 0.19684 | 122.9691 | 122.9187 | 122.8317 | 122.8592 | -122.9874 | -122.9095 | 122.699 | 0.13733 | 20.8603 | 14.7537
836.1719 | 123.1247 | -57.2937 | 65.5426 | -0.098725 | 0.00040806 | 0.062666 | 0.061996 | -0.0041122 | -0.00037171 | 8.1188e-05 | 0.013916 | 0.00046135 | -0.00064077 | -0.00058098 | -0.00022431 | -0.0025891 | -0.0018971 | -36.5021 | 65.5197 | -57.3898 | 65.4282 | -57.0236 | -57.5089 | -57.4081 | -42.6224 | 65.5609 | -57.3486 | -57.193 | -57.2296 | -57.3669 | -57.074 | -0.096131 | -0.022889 | -0.11444 | 0.27008 | -0.11444 | -0.21515 | -0.01831 | -0.11902 | -0.054932 | 0.01831 | -122.7356 | 0.064087 | 0.21973 | -0.073242 | 0.27466 | -0.01831 | 0.36621 | 122.818 | 0.11902 | 0.15564 | 122.9095 | 122.9095 | 122.8134 | 122.8546 | -122.9324 | -122.8912 | 122.7219 | 0.10071 | 20.7916 | 14.6713
837.1719 | 123.1522 | -57.2983 | 65.5563 | -0.12161 | 0.00040806 | 0.06288 | 0.064132 | -0.0013352 | -0.0018671 | -0.00013241 | -0.044067 | -0.00060665 | -0.0025636 | 0.00048702 | -0.0044967 | 0.0014697 | -0.00018806 | -36.5799 | 65.4968 | -57.3944 | 65.4419 | -57.0419 | -57.5043 | -57.4173 | -42.7277 | 65.5563 | -57.3349 | -57.1793 | -57.0465 | -57.3029 | -57.0465 | -0.09613 | -0.059509 | -0.11444 | 0.25635 | -0.11902 | -0.20599 | -0.022888 | -0.10986 | -0.036621 | 0 | -122.7356 | 0.25177 | 0.25177 | -0.004577 | 0.28839 | 0.032044 | 0.35248 | 122.8363 | 0.28839 | 0.15564 | 122.8912 | 122.8912 | 122.7951 | 122.8546 | -122.9507 | -122.8912 | 122.7402 | 0.11902 | 20.7184 | 14.5706
838.1719 | 123.2025 | -57.3029 | 65.5563 | -0.13687 | 0.0031851 | 0.064589 | 0.063918 | 0.0022964 | 5.5488e-05 | -0.00098701 | -0.01355 | -0.00060665 | -0.0029908 | 0.0026232 | -0.0036423 | -0.0015211 | -0.0010425 | -36.6898 | 65.5106 | -57.4127 | 65.451 | -57.0145 | -57.4951 | -57.4219 | -42.8284 | 65.5518 | -57.3395 | -57.1609 | -57.1564 | -57.5867 | -57.1381 | -0.10986 | -0.045776 | -0.10529 | 0.28839 | -0.11902 | -0.19226 | -0.009155 | -0.082397 | -0.036622 | -0.004577 | -122.7173 | 0.14648 | 0.16479 | -0.28381 | 0.20142 | -0.24719 | 0.39825 | 122.8638 | 0.18311 | 0.17853 | 122.9233 | 122.8912 | 122.8134 | 122.8546 | -122.9691 | -122.8958 | 122.7539 | 0.14191 | 20.6131 | 14.4745
839.1719 | 123.0057 | -57.3578 | 65.5792 | -0.068207 | 0.00040806 | 0.067366 | 0.063705 | 0.0033646 | -0.0016535 | -0.002055 | -0.050171 | 0.0017431 | 0.0012818 | 0.0051868 | -0.0015061 | -0.00023928 | -0.00040166 | -36.9598 | 65.538 | -57.4631 | 65.3687 | -57.1014 | -57.605 | -57.5363 | -43.0756 | 65.6113 | -57.3669 | -57.2479 | -57.2937 | -57.4722 | -57.1381 | -0.10529 | -0.041199 | -0.21057 | 0.25635 | -0.17853 | -0.24719 | -0.073242 | -0.14191 | -0.009155 | 0.032043 | -122.8271 | 0.064087 | 0.21973 | -0.11444 | 0.22888 | -0.10529 | 0.36163 | 122.8317 | 0.073242 | 0.11902 | 123.0011 | 122.9782 | 122.8958 | 122.9691 | -123.0423 | -122.9462 | 122.7264 | 0.10986 | 20.3979 | 14.2822
840.1719 | 123.1338 | -57.3029 | 65.5426 | 0.008087 | 0.0012625 | 0.063307 | 0.062423 | -0.0024032 | 0.00091009 | 0.002431 | 0.0047608 | 0.00088875 | 0.0012818 | -0.00079478 | -0.0010787 | -0.0015211 | -0.0038197 | -36.7538 | 65.538 | -57.3944 | 65.4556 | -57.0007 | -57.4951 | -57.399 | -42.9977 | 65.5701 | -57.3303 | -57.1381 | -57.1976 | -57.3395 | -57.0511 | -0.091553 | -0.004578 | -0.086976 | 0.30212 | -0.096131 | -0.19226 | -0.004578 | -0.10071 | -0.027466 | 0.027465 | -122.6807 | 0.10528 | 0.25177 | -0.036622 | 0.27924 | -0.009156 | 0.39368 | 122.85 | 0.13275 | 0.19226 | 122.9324 | 122.9004 | 122.8409 | 122.8729 | -122.937 | -122.8729 | 122.7585 | 0.16479 | 20.549 | 14.3051
841.1719 | 123.1384 | -57.2937 | 65.5426 | -0.098725 | 0.00019446 | 0.064803 | 0.062636 | -0.0011214 | 5.5488e-05 | 8.1188e-05 | -0.0013428 | -0.0016749 | -0.0044862 | 0.00048702 | -0.0019333 | -0.0017347 | 0.0021619 | -36.7767 | 65.5151 | -57.4219 | 65.4694 | -56.9641 | -57.4631 | -57.4081 | -43.1305 | 65.5609 | -57.3166 | -57.1472 | -57.1976 | -57.3441 | -57.0602 | -0.12817 | -0.027466 | -0.073243 | 0.32959 | -0.11444 | -0.16937 | 0.013733 | -0.041199 | -0.022888 | 0.01831 | -122.6898 | 0.09613 | 0.23346 | -0.050354 | 0.25635 | -0.027466 | 0.45776 | 122.8912 | 0.11902 | 0.16937 | 122.937 | 122.8775 | 122.8088 | 122.8546 | -122.9645 | -122.8592 | 122.7631 | 0.14648 | 20.517 | 14.1632
842.1719 | 123.1476 | -57.2571 | 65.5701 | -0.091095 | -0.00044654 | 0.065016 | 0.064132 | -0.0013352 | -0.00058531 | 0.0028582 | -0.0043946 | -0.00082025 | 0.00021363 | 0.0043322 | 0.00041649 | 0.00082892 | -0.0046741 | -37.0605 | 65.4922 | -57.3944 | 65.3 | -57.0007 | -57.2754 | -57.28 | -43.2175 | 65.5701 | -57.3257 | -57.1381 | -57.2021 | -57.3441 | -57.0374 | -0.13733 | -0.077819 | -0.27008 | 0.25635 | -0.022888 | -0.018311 | 0.11444 | 0.11902 | -0.068665 | 0 | -122.7081 | 0.054932 | 0.21973 | -0.086975 | 0.28839 | -0.01831 | 0.39368 | 122.6944 | 0.1236 | 0.18768 | 122.8867 | 122.8958 | 122.7493 | 122.8271 | -122.9645 | -122.8958 | 122.5571 | 0.11902 | 20.1965 | 14.0396
843.1719 | 123.0743 | -57.3257 | 65.6113 | -0.045319 | 0.0014761 | 0.063948 | 0.066482 | 0.00058737 | -0.00058531 | 0.00414 | -0.077637 | 0.00067495 | -0.00021357 | 0.0019824 | -0.0015061 | 0.00040152 | -0.00061526 | -37.2299 | 65.593 | -57.4127 | 65.3641 | -57.1106 | -57.5729 | -57.4905 | -43.4555 | 65.6021 | -57.3486 | -57.2296 | -57.2891 | -57.4402 | -57.1243 | -0.086975 | -0.01831 | -0.24719 | 0.21515 | -0.1648 | -0.24719 | -0.07782 | -0.16022 | -0.022888 | -0.009155 | -122.8409 | 0.036621 | 0.20142 | -0.11444 | 0.2243 | -0.091553 | 0.30212 | 122.7768 | 0.059509 | 0.11902 | 123.0057 | 122.9507 | 122.9187 | 122.9279 | -123.024 | -122.9599 | 122.6898 | 0.096131 | 20.0958 | 13.8702
844.1719 | 123.143 | -57.2845 | 65.5609 | -0.075836 | 0.0010489 | 0.065016 | 0.063491 | -0.00048063 | -0.00015811 | 0.001363 | -0.034912 | -0.00017945 | 0.00085443 | -0.0018628 | -0.0017197 | -0.00088008 | -0.00082886 | -37.2208 | 65.5655 | -57.4356 | 65.4099 | -57.0465 | -57.5455 | -57.4448 | -43.4967 | 65.593 | -57.3303 | -57.1609 | -57.2113 | -57.3578 | -57.0328 | -0.15106 | 0.004578 | -0.15106 | 0.23804 | -0.16022 | -0.26093 | -0.009155 | -0.10986 | -0.045776 | 0.032044 | -122.7219 | 0.073242 | 0.25177 | -0.073242 | 0.29755 | -0.027466 | 0.3891 | 122.8455 | 0.11902 | 0.16937 | 123.0011 | 122.9233 | 122.85 | 122.8775 | -122.9965 | -122.8912 | 122.6944 | 0.1236 | 20.0638 | 13.7878
845.1719 | 123.143 | -57.2617 | 65.6113 | -0.060578 | 0.00040806 | 0.061385 | 0.0605 | -0.0049668 | -0.00015811 | 8.1188e-05 | 0.062744 | 0.0019567 | 0.0012818 | -0.0078442 | -0.00065151 | -0.0010937 | -0.0023243 | -37.1567 | 65.5975 | -57.3715 | 65.5243 | -56.9138 | -57.3944 | -57.3212 | -43.2175 | 65.6754 | -57.2525 | -57.1426 | -57.106 | -57.2937 | -57.019 | -0.10986 | -0.013733 | -0.086975 | 0.3479 | -0.059509 | -0.13275 | 0.050354 | -0.022888 | 0.009156 | 0.064087 | -122.7539 | 0.15564 | 0.24261 | -0.032043 | 0.23346 | -0.041199 | 0.45776 | 122.8958 | 0.14648 | 0.10986 | 122.9691 | 122.9279 | 122.8592 | 122.937 | -122.9828 | -122.8638 | 122.7859 | 0.11902 | 20.105 | 14.0442
846.1719 | 123.0743 | -57.28 | 65.5884 | -0.083466 | 0.00019446 | 0.064375 | 0.063918 | -0.0017624 | 0.0017645 | 0.0015766 | -0.056274 | 0.0013159 | -0.0010682 | -0.0035718 | -0.00086511 | 0.00018792 | -0.00018806 | -37.4634 | 65.6021 | -57.4127 | 65.3824 | -57.0969 | -57.5684 | -57.4768 | -43.7347 | 65.6204 | -57.3303 | -57.193 | -57.2617 | -57.4036 | -57.106 | -0.13275 | 0.013733 | -0.20599 | 0.1831 | -0.19684 | -0.28839 | -0.064087 | -0.15564 | -0.050354 | 0.032043 | -122.7814 | 0.01831 | 0.17395 | -0.1236 | 0.2243 | -0.073242 | 0.31586 | 122.7951 | 0.068664 | 0.13733 | 123.0148 | 122.9507 | 122.8821 | 122.9004 | -123.0011 | -122.9187 | 122.6624 | 0.086975 | 19.8166 | 13.5452
847.1719 | 123.0881 | -57.2937 | 65.6296 | -0.098725 | -0.00066014 | 0.062025 | 0.061996 | 0.0020828 | -0.00058531 | -0.0014142 | 0.016968 | 0.00046135 | 0.00064083 | -0.001222 | 0.0010575 | -0.0013073 | -0.0042469 | -37.5412 | 65.5518 | -57.3624 | 65.4419 | -57.0328 | -57.4722 | -57.3807 | -43.7714 | 65.625 | -57.3166 | -57.1655 | -57.1976 | -57.3441 | -57.0786 | -0.068665 | -0.07782 | -0.18768 | 0.26093 | -0.086975 | -0.17853 | -0.01831 | -0.10986 | -0.022888 | -0.004578 | -122.7951 | 0.09613 | 0.21515 | -0.050354 | 0.23804 | -0.027466 | 0.32959 | 122.8043 | 0.11902 | 0.15106 | 122.9141 | 122.9416 | 122.8455 | 122.9187 | -122.9919 | -122.9462 | 122.7356 | 0.12817 | 19.7525 | 13.5223
848.1719 | 123.1613 | -57.2433 | 65.5838 | -0.12161 | 0.00040806 | 0.061812 | 0.064559 | -0.0011214 | 0.0015509 | 0.00029479 | -0.0043946 | 3.4148e-05 | 0.00042723 | 0.00070062 | -0.0010787 | 0.0012561 | -0.00061526 | -37.619 | 65.5426 | -57.3898 | 65.5014 | -56.9733 | -57.4768 | -57.3898 | -43.8263 | 65.5838 | -57.2983 | -57.0877 | -57.0786 | -57.312 | -57.0328 | -0.14648 | -0.041198 | -0.082397 | 0.27008 | -0.14648 | -0.23346 | 0 | -0.086975 | -0.054932 | 0 | -122.6715 | 0.16479 | 0.21057 | -0.068665 | 0.2655 | -0.013733 | 0.41656 | 122.8912 | 0.21973 | 0.21057 | 122.9324 | 122.8821 | 122.7859 | 122.8271 | -122.9736 | -122.8821 | 122.7448 | 0.15564 | 19.6243 | 13.4171
849.1719 | 123.1705 | -57.2617 | 65.5792 | -0.091095 | 0.0012625 | 0.064589 | 0.063918 | 0.0010148 | 0.00091009 | -0.00013241 | -0.01355 | 0.0011023 | 0.00064083 | -0.00036738 | -0.0017197 | -0.00023928 | -0.0029651 | -37.7106 | 65.5197 | -57.3624 | 65.4831 | -56.9824 | -57.4677 | -57.3807 | -43.8995 | 65.5746 | -57.3166 | -57.106 | -57.1747 | -57.3303 | -57.0099 | -0.10071 | -0.05951 | -0.096131 | 0.27924 | -0.11902 | -0.20599 | -0.01831 | -0.10528 | -0.054931 | -0.004578 | -122.6852 | 0.086975 | 0.25177 | -0.068664 | 0.3067 | -0.013733 | 0.37994 | 122.8455 | 0.14191 | 0.21057 | 122.8821 | 122.8912 | 122.7814 | 122.8363 | -122.9416 | -122.8958 | 122.7448 | 0.15564 | 19.5511 | 13.3621
850.1719 | 123.1567 | -57.2433 | 65.6021 | -0.075836 | 0.00040806 | 0.061385 | 0.062423 | 0.0020828 | 0.0026191 | 0.0015766 | 0.044434 | -0.00017945 | -0.00064077 | -0.00229 | -0.0015061 | -0.0030163 | 0.0040845 | -37.7426 | 65.5746 | -57.3257 | 65.5106 | -56.9504 | -57.4127 | -57.3349 | -43.9499 | 65.6113 | -57.28 | -57.0877 | -57.0969 | -57.2479 | -56.9962 | -0.082398 | -0.027466 | -0.091553 | 0.29297 | -0.091553 | -0.16937 | -0.009155 | -0.086975 | -0.036621 | 0.009155 | -122.6898 | 0.14648 | 0.24719 | -0.004578 | 0.28381 | 0.032043 | 0.37537 | 122.8363 | 0.1831 | 0.19226 | 122.9004 | 122.8912 | 122.818 | 122.8546 | -122.9279 | -122.8821 | 122.7539 | 0.15564 | 19.5007 | 13.2935
851.1719 | 123.0652 | -57.2525 | 65.6067 | -0.060578 | 0.0014761 | 0.062453 | 0.063705 | 0.0010148 | 0.00091009 | 0.00072199 | -0.010498 | 3.4148e-05 | 0.0025634 | -0.0020764 | -0.00043791 | -0.0021619 | -0.0063831 | -37.8708 | 65.5518 | -57.3761 | 65.5014 | -56.9504 | -57.4768 | -57.3807 | -44.0781 | 65.6113 | -57.3029 | -57.1426 | -57.193 | -57.3349 | -57.0602 | -0.1236 | -0.054931 | -0.10529 | 0.30212 | -0.12817 | -0.22431 | -0.004577 | -0.10071 | -0.050354 | 0.004578 | -122.7493 | 0.059509 | 0.19226 | -0.082398 | 0.24261 | -0.032044 | 0.42572 | 122.8775 | 0.10986 | 0.16022 | 122.9279 | 122.9141 | 122.8043 | 122.8638 | -122.9828 | -122.9095 | 122.7539 | 0.10986 | 19.3817 | 13.1744
852.1719 | 123.1018 | -57.2617 | 65.593 | -0.15976 | 0.0010489 | 0.064803 | 0.061782 | -0.0032578 | -0.00037171 | -0.00055961 | -0.0013428 | -0.0014613 | 2.8e-08 | 0.0017688 | -0.00065151 | -0.0023755 | -0.0033923 | -37.9623 | 65.5518 | -57.3486 | 65.5014 | -56.9458 | -57.4585 | -57.3578 | -44.1742 | 65.6067 | -57.3074 | -57.1106 | -57.1793 | -57.3441 | -57.0328 | -0.086975 | -0.041199 | -0.091553 | 0.31586 | -0.09613 | -0.19684 | -0.009155 | -0.10986 | -0.045776 | 0.013732 | -122.7036 | 0.082398 | 0.22888 | -0.082397 | 0.27466 | -0.036621 | 0.40283 | 122.85 | 0.12817 | 0.19684 | 122.9004 | 122.9141 | 122.8134 | 122.8683 | -122.9416 | -122.9004 | 122.7631 | 0.15106 | 19.2993 | 13.0875
853.1719 | 123.0606 | -57.2891 | 65.6296 | -0.11398 | -0.0013009 | 0.066512 | 0.064986 | 0.00037377 | 0.00048269 | 0.00072199 | -0.059326 | 0.0015295 | -0.00021357 | 0.0094592 | -0.0023605 | 0.0010425 | -0.0025379 | -38.1088 | 65.625 | -57.4219 | 65.3915 | -57.0557 | -57.5409 | -57.4539 | -44.3939 | 65.657 | -57.3349 | -57.193 | -57.2571 | -57.4036 | -57.0969 | -0.13275 | -0.004578 | -0.23804 | 0.23346 | -0.16479 | -0.25177 | -0.032043 | -0.11902 | -0.045776 | 0.027465 | -122.8226 | 0.032044 | 0.19226 | -0.11444 | 0.23804 | -0.068664 | 0.36621 | 122.8134 | 0.07782 | 0.14191 | 123.0469 | 122.9919 | 122.9141 | 122.9462 | -123.0515 | -122.9645 | 122.6807 | 0.096131 | 19.1803 | 12.8952
854.1719 | 123.0698 | -57.2662 | 65.6021 | -0.091095 | 0.00062166 | 0.061598 | 0.065627 | -0.0013352 | -0.0012261 | 0.00093559 | -0.050171 | 0.0023839 | 0.003418 | -0.001222 | 0.0012711 | 0.0010425 | 0.00066654 | -38.2141 | 65.6158 | -57.3944 | 65.4053 | -57.0877 | -57.55 | -57.4585 | -44.4534 | 65.6296 | -57.3029 | -57.1655 | -57.2342 | -57.3898 | -57.0694 | -0.12817 | 0.013733 | -0.19684 | 0.17853 | -0.19226 | -0.28381 | -0.064087 | -0.15564 | -0.036621 | 0.027466 | -122.7676 | 0.032043 | 0.19684 | -0.1236 | 0.23346 | -0.086976 | 0.3067 | 122.7997 | 0.068664 | 0.13733 | 123.0103 | 122.9324 | 122.8821 | 122.8958 | -122.9965 | -122.905 | 122.6715 | 0.10071 | 19.0521 | 12.8128
855.1719 | 123.1155 | -57.2159 | 65.6342 | -0.060578 | 0.0012625 | 0.062666 | 0.064986 | -0.001976 | 0.0021917 | 0.00093559 | 0.035278 | -0.0012477 | 0.00021363 | -0.00079478 | -0.0017197 | -0.0023755 | -0.0023243 | -38.2736 | 65.6479 | -57.2754 | 65.5609 | -56.9275 | -57.3761 | -57.2754 | -44.3527 | 65.6387 | -57.2479 | -57.0602 | -57.106 | -57.2525 | -56.9824 | -0.05951 | 0.013733 | -0.073242 | 0.28839 | -0.05951 | -0.16022 | 0 | -0.10071 | -0.032044 | 0.004578 | -122.6944 | 0.10986 | 0.23346 | -0.036621 | 0.2655 | -0.004577 | 0.3479 | 122.8363 | 0.14191 | 0.18768 | 122.9233 | 122.8867 | 122.8638 | 122.8546 | -122.9095 | -122.8821 | 122.7768 | 0.15564 | 18.9423 | 12.8632
856.1719 | 123.0148 | -57.2845 | 65.6479 | -0.060578 | -0.0023691 | 0.062239 | 0.0652 | -0.00026703 | 5.5488e-05 | 0.00072199 | -0.086792 | 0.0023839 | -0.00021357 | 0.002196 | -0.00022431 | -0.0013073 | 0.00066654 | -38.4018 | 65.6113 | -57.3853 | 65.4099 | -57.0923 | -57.5546 | -57.4768 | -44.6503 | 65.6845 | -57.3257 | -57.2159 | -57.28 | -57.4768 | -57.1152 | -0.10071 | -0.036621 | -0.23804 | 0.19226 | -0.19226 | -0.27008 | -0.091553 | -0.16937 | -0.041199 | 0.036621 | -122.8638 | 0.004578 | 0.16937 | -0.19226 | 0.21057 | -0.15106 | 0.29297 | 122.7951 | 0.045777 | 0.10986 | 122.9965 | 123.0103 | 122.8958 | 122.9691 | -123.0331 | -122.9736 | 122.6944 | 0.068665 | 18.8828 | 12.6343
857.1719 | 123.0377 | -57.2571 | 65.6479 | -0.091095 | 0.00040806 | 0.064375 | 0.064345 | -0.00090783 | 0.0011237 | -0.00077341 | -0.080688 | 0.0032385 | 0.0019226 | 0.0026232 | -0.00065151 | 0.00018792 | 2.554e-05 | -38.5208 | 65.6204 | -57.3898 | 65.3961 | -57.0831 | -57.5546 | -57.4677 | -45.0348 | 65.625 | -57.3532 | -57.1609 | -57.225 | -57.4356 | -57.0923 | -0.13275 | -0.027466 | -0.25177 | 0.17395 | -0.21057 | -0.29755 | -0.077819 | -0.16479 | -0.09613 | -0.022888 | -122.8088 | 0.032043 | 0.1648 | -0.17853 | 0.26093 | -0.082398 | 0.3067 | 122.7859 | 0.12817 | 0.19226 | 123.0103 | 122.9782 | 122.8775 | 122.8821 | -123.0377 | -123.0011 | 122.6532 | 0.09613 | 18.7363 | 12.2223
858.1719 | 123.0515 | -57.2891 | 65.6525 | -0.075836 | -0.0013009 | 0.065657 | 0.065841 | -0.0032578 | 0.00091009 | -0.00034601 | -0.068481 | 0.0013159 | -0.00042717 | -0.0052808 | -0.00022431 | -0.0017347 | 0.0013073 | -38.5712 | 65.6113 | -57.3624 | 65.4007 | -57.0465 | -57.55 | -57.4539 | -44.7922 | 65.6387 | -57.3212 | -57.1701 | -57.2525 | -57.399 | -57.0786 | -0.073242 | -0.041199 | -0.25177 | 0.24262 | -0.16479 | -0.26093 | -0.091552 | -0.18768 | -0.032043 | -0.013733 | -122.8226 | 0.036622 | 0.21057 | -0.10986 | 0.24262 | -0.07782 | 0.31586 | 122.7631 | 0.068665 | 0.15106 | 122.9736 | 122.9599 | 122.9004 | 122.9279 | -123.0148 | -122.9736 | 122.6898 | 0.11902 | 18.718 | 12.4969
859.1719 | 123.0881 | -57.2525 | 65.6204 | -0.098725 | 0.00040806 | 0.065016 | 0.0652 | -0.00048063 | 0.00048269 | 0.001363 | -0.044067 | 0.00088875 | -0.00021357 | 5.9824e-05 | 0.0019119 | -0.0028027 | 0.0019483 | -38.681 | 65.6479 | -57.3532 | 65.4327 | -57.019 | -57.5089 | -57.4219 | -44.8792 | 65.657 | -57.2937 | -57.1152 | -57.1793 | -57.3441 | -57.0328 | -0.10071 | 0.027466 | -0.18768 | 0.23346 | -0.16937 | -0.25635 | -0.068665 | -0.15564 | -0.041199 | 0.036621 | -122.7356 | 0.073242 | 0.21973 | -0.091553 | 0.26093 | -0.050354 | 0.33417 | 122.7859 | 0.11444 | 0.17853 | 123.0011 | 122.9507 | 122.9004 | 122.9095 | -122.9736 | -122.9141 | 122.6852 | 0.13733 | 18.5715 | 12.3734
860.1719 | 123.1293 | -57.2296 | 65.6158 | -0.15976 | 0.0016899 | 0.063307 | 0.063918 | 0.00016017 | 0.0019781 | 0.0015766 | 0.013916 | -0.00060665 | 0.00042723 | -0.0035718 | -0.00043791 | -0.0013073 | -0.0014697 | -38.6948 | 65.5838 | -57.3257 | 65.5792 | -56.7719 | -57.4081 | -57.312 | -44.8563 | 65.6296 | -57.2388 | -57.0694 | -57.1014 | -57.2708 | -56.9778 | -0.096131 | -0.032044 | -0.036621 | 0.45776 | -0.082398 | -0.17853 | 0.013733 | -0.082397 | -0.009156 | 0.013733 | -122.6852 | 0.12817 | 0.25177 | -0.041199 | 0.26093 | -0.032043 | 0.55389 | 122.905 | 0.13733 | 0.16937 | 122.9095 | 122.8683 | 122.8134 | 122.8592 | -122.9416 | -122.8546 | 122.8088 | 0.16022 | 18.5349 | 12.3734
861.1719 | 123.0011 | -57.2525 | 65.6845 | -0.11398 | 0.00040806 | 0.064589 | 0.062636 | 0.00037377 | -0.0012261 | -0.002055 | -0.056274 | 0.0025975 | 0.00064083 | -0.0027174 | -0.0010787 | 0.0012561 | -0.00040166 | -38.8504 | 65.6342 | -57.3578 | 65.3961 | -57.0831 | -57.5546 | -57.4585 | -45.1035 | 65.6937 | -57.2845 | -57.3715 | -57.0419 | -57.1609 | -56.9733 | -0.10529 | -0.050354 | -0.28839 | 0.16937 | -0.20599 | -0.30212 | -0.10071 | -0.19684 | -0.032044 | 0.009156 | -123.056 | 0.21057 | 0.27923 | 0.091552 | 0.31128 | 0.1236 | 0.27466 | 122.7539 | 0.24262 | -0.086975 | 122.9919 | 122.9782 | 122.8867 | 122.9462 | -123.0423 | -122.9691 | 122.6486 | -0.11902 | 18.4021 | 12.149
862.1719 | 123.056 | -57.2571 | 65.6479 | -0.15213 | -0.00087374 | 0.061598 | 0.063491 | 0.0016556 | -0.00037171 | 0.00029479 | -0.050171 | 0.0025975 | 0.001709 | -0.00036738 | -0.00022431 | -0.0021619 | 0.00066654 | -38.7634 | 65.6433 | -57.3349 | 65.4236 | -57.0511 | -57.5409 | -57.4402 | -45.1721 | 65.6754 | -57.3029 | -57.1609 | -57.2205 | -57.3898 | -57.0923 | -0.07782 | -0.004577 | -0.2243 | 0.20599 | -0.18311 | -0.28381 | -0.10529 | -0.20599 | -0.045776 | 0.027466 | -122.8088 | 0.036621 | 0.1648 | -0.13275 | 0.21057 | -0.086976 | 0.28381 | 122.7585 | 0.082397 | 0.14191 | 122.9782 | 122.9782 | 122.9004 | 122.9324 | -122.9828 | -122.9507 | 122.6807 | 0.09613 | 18.4937 | 12.085
863.1719 | 123.1522 | -57.2159 | 65.625 | -0.098725 | -0.0010873 | 0.06523 | 0.0652 | -0.00090783 | 0.0013373 | 0.00029479 | -0.016602 | 0.0011023 | 0.00021363 | -0.00036738 | 0.00020289 | -0.0017347 | -0.0021107 | -38.8916 | 65.5975 | -57.3395 | 65.506 | -56.9321 | -57.4173 | -57.3532 | -45.1218 | 65.6204 | -57.2662 | -57.0602 | -57.1472 | -57.2845 | -56.9778 | -0.1236 | -0.027466 | -0.11902 | 0.28381 | -0.13733 | -0.20142 | -0.013732 | -0.077819 | -0.050354 | -0.004578 | -122.6852 | 0.068664 | 0.23804 | -0.068665 | 0.28839 | -0.018311 | 0.40741 | 122.8455 | 0.11902 | 0.20599 | 122.937 | 122.8867 | 122.8134 | 122.8363 | -122.9645 | -122.8912 | 122.7219 | 0.15564 | 18.3243 | 12.0941
864.1719 | 123.0103 | -57.2388 | 65.6891 | -0.03006 | -1.9142e-05 | 0.063521 | 0.063705 | -0.0021896 | 0.0024053 | -0.0018414 | -0.068481 | 0.0011023 | 0.00042723 | -0.0027174 | -0.00065151 | -0.0013073 | 0.0017345 | -38.9603 | 65.6479 | -57.3441 | 65.4373 | -57.0007 | -57.4997 | -57.4265 | -45.3186 | 65.712 | -57.2754 | -57.1701 | -57.2342 | -57.4173 | -57.0831 | -0.10528 | -0.041199 | -0.25177 | 0.23804 | -0.18768 | -0.26093 | -0.082398 | -0.15564 | -0.036621 | 0.022888 | -122.8592 | 0.004578 | 0.15564 | -0.17853 | 0.19226 | -0.14191 | 0.34332 | 122.7814 | 0.041199 | 0.10529 | 122.9919 | 122.9874 | 122.8867 | 122.9507 | -123.0331 | -122.9645 | 122.6761 | 0.068665 | 18.2785 | 11.9202
865.1719 | 122.9324 | -57.2937 | 65.5884 | -0.037689 | 0.00019446 | 0.063948 | 0.066054 | 0.0029374 | 0.00091009 | 0.00029479 | -0.053223 | 0.00046135 | 0.0014954 | 0.0034778 | 0.0016983 | -0.0028027 | -0.0018971 | -39.0884 | 65.6342 | -57.3441 | 65.3824 | -57.074 | -57.5363 | -57.4722 | -45.4697 | 65.6891 | -57.2754 | -57.1701 | -57.2388 | -57.431 | -57.019 | -0.050354 | 0.045776 | -0.20599 | 0.21973 | -0.17853 | -0.24262 | -0.12817 | -0.19226 | 0.01831 | 0.10071 | -122.7585 | 0.054931 | 0.27466 | -0.13733 | 0.25635 | -0.15564 | 0.27008 | 122.7264 | 0.036621 | 0.10529 | 122.9782 | 122.9645 | 122.9279 | 122.9828 | -122.9324 | -122.8638 | 122.6761 | 0.1236 | 18.2053 | 11.824
866.1719 | 123.0194 | -57.2388 | 65.6845 | -0.045319 | -0.0019417 | 0.063094 | 0.065627 | 0.001442 | 0.00069649 | 0.0011494 | -0.041016 | 0.0021703 | 0.0021362 | 0.0034778 | -0.0015061 | -0.0019483 | 2.554e-05 | -39.1113 | 65.6296 | -57.3486 | 65.4556 | -56.9641 | -57.4585 | -57.399 | -45.4514 | 65.7028 | -57.2754 | -57.1426 | -57.2067 | -57.4036 | -57.0511 | -0.10986 | -0.054931 | -0.22888 | 0.27466 | -0.16022 | -0.21973 | -0.050354 | -0.10986 | -0.036621 | 0.018311 | -122.8271 | 0.032044 | 0.18768 | -0.16479 | 0.22431 | -0.12817 | 0.38452 | 122.8043 | 0.068665 | 0.13275 | 122.9782 | 122.9782 | 122.8683 | 122.9416 | -123.0331 | -122.9599 | 122.6944 | 0.096131 | 18.1274 | 11.7874
867.1719 | 123.0515 | -57.2571 | 65.6616 | -0.091095 | -0.00044654 | 0.063094 | 0.066909 | -5.343e-05 | -0.00037171 | 0.00093559 | -0.028809 | 0.0011023 | 0.0053406 | -0.00036738 | -0.0015061 | -0.0021619 | 0.00045294 | -39.2395 | 65.6708 | -57.3578 | 65.3961 | -57.0694 | -57.5134 | -57.4402 | -45.7306 | 65.657 | -57.3486 | -57.2021 | -57.2021 | -57.4219 | -57.0969 | -0.10071 | 0.009155 | -0.2655 | 0.18768 | -0.18311 | -0.25635 | -0.082398 | -0.15564 | -0.091553 | -0.004578 | -122.8638 | 0.054932 | 0.16022 | -0.16479 | 0.25177 | -0.073242 | 0.28839 | 122.7539 | 0.14648 | 0.14648 | 123.0286 | 123.0057 | 122.9279 | 122.9141 | -123.0194 | -123.0103 | 122.6532 | 0.054932 | 18.0176 | 11.5265
868.1719 | 123.024 | -57.2708 | 65.6708 | -0.068207 | -0.00066014 | 0.063948 | 0.064132 | 0.001442 | -0.00015811 | -0.00034601 | -0.0043946 | 0.00046135 | 0.001709 | 0.003905 | -0.0010787 | 0.00040152 | 0.0021619 | -39.299 | 65.6799 | -57.3257 | 65.4373 | -56.987 | -57.4722 | -57.4081 | -45.6253 | 65.6845 | -57.2754 | -57.1518 | -57.225 | -57.3807 | -57.074 | -0.054932 | 0.009156 | -0.23346 | 0.28381 | -0.13733 | -0.20142 | -0.082397 | -0.14648 | -0.004578 | 0.013733 | -122.8226 | 0.045776 | 0.19684 | -0.10986 | 0.20142 | -0.10529 | 0.33874 | 122.7631 | 0.050354 | 0.1236 | 123.0057 | 122.9599 | 122.9507 | 122.9553 | -122.9965 | -122.9462 | 122.7081 | 0.11902 | 17.9718 | 11.6455
869.1719 | 123.0286 | -57.225 | 65.7028 | -0.083466 | -0.00066014 | 0.06288 | 0.063491 | 0.0037918 | -0.0020807 | 0.0020038 | -0.047119 | 0.0023839 | 0.0019226 | -0.0054944 | -0.00022431 | -0.00045288 | -0.0018971 | -39.3723 | 65.6616 | -57.312 | 65.4694 | -56.9641 | -57.4539 | -57.3807 | -45.6802 | 65.712 | -57.2571 | -57.1609 | -57.2067 | -57.3761 | -57.0465 | -0.086975 | -0.041199 | -0.23346 | 0.26093 | -0.15564 | -0.22888 | -0.068664 | -0.14191 | -0.032043 | 0.009155 | -122.8638 | 0.018311 | 0.17853 | -0.15106 | 0.21057 | -0.11902 | 0.3479 | 122.7814 | 0.050354 | 0.09613 | 122.9736 | 122.9691 | 122.8867 | 122.937 | -123.0148 | -122.9599 | 122.6944 | 0.064087 | 17.8528 | 11.5448
870.1719 | 123.0789 | -57.2113 | 65.6204 | -0.13687 | 0.0021171 | 0.065657 | 0.061355 | 0.0010148 | 0.00026909 | -0.002696 | 0.035278 | -0.00039305 | 2.8e-08 | -0.0035718 | -1.0706e-05 | -0.0013073 | 0.00088014 | -39.4135 | 65.6158 | -57.2845 | 65.5014 | -56.8863 | -57.3807 | -57.312 | -45.6848 | 65.6525 | -57.2662 | -57.0877 | -57.1472 | -57.2845 | -56.987 | -0.073242 | -0.004577 | -0.11902 | 0.32501 | -0.10071 | -0.16937 | -0.027466 | -0.09613 | -0.054931 | 0.032044 | -122.7081 | 0.064087 | 0.2243 | -0.073242 | 0.27923 | -0.018311 | 0.39825 | 122.7859 | 0.11902 | 0.17853 | 122.9004 | 122.9187 | 122.8271 | 122.8638 | -122.905 | -122.8867 | 122.7127 | 0.1236 | 17.7979 | 11.5265
871.1719 | 123.0881 | -57.2113 | 65.6982 | -0.075836 | -0.00087374 | 0.065016 | 0.064559 | 0.0012284 | 0.00091009 | 0.003072 | -0.016602 | -0.00082025 | 0.0019226 | 0.001128 | -0.0010787 | 0.00082892 | -0.00018806 | -39.4638 | 65.6845 | -57.3029 | 65.5014 | -56.9275 | -57.3944 | -57.3532 | -45.7809 | 65.7028 | -57.2433 | -57.0969 | -57.1564 | -57.3074 | -57.0145 | -0.091552 | -0.013733 | -0.19684 | 0.28381 | -0.14191 | -0.18311 | -0.050354 | -0.091553 | -0.032043 | 0.004578 | -122.7951 | 0.054932 | 0.19684 | -0.09613 | 0.22888 | -0.064087 | 0.37537 | 122.8043 | 0.086975 | 0.14648 | 122.9874 | 122.9462 | 122.8958 | 122.9141 | -123.0011 | -122.9416 | 122.7127 | 0.11444 | 17.7475 | 11.4304
872.1719 | 123.056 | -57.2342 | 65.7074 | -0.037689 | 0.00062166 | 0.063734 | 0.063705 | 0.0012284 | 0.0011237 | -0.00034601 | -0.0013428 | 0.0030249 | 0.0032044 | 0.0017688 | -0.0023605 | -0.0013073 | -0.00061526 | -39.537 | 65.657 | -57.3349 | 65.4922 | -56.9321 | -57.4219 | -57.3532 | -45.845 | 65.7028 | -57.2525 | -57.0923 | -57.1381 | -57.2937 | -57.0053 | -0.10071 | -0.050354 | -0.21515 | 0.30212 | -0.11902 | -0.18768 | -0.01831 | -0.086975 | -0.01831 | -0.004577 | -122.7997 | 0.09613 | 0.22888 | -0.059509 | 0.24719 | -0.041199 | 0.40283 | 122.8271 | 0.11444 | 0.16022 | 122.9919 | 122.9553 | 122.8912 | 122.937 | -123.0423 | -122.9599 | 122.7264 | 0.14191 | 17.6971 | 11.3892
873.1719 | 123.0835 | -57.225 | 65.6891 | -0.091095 | 0.00019446 | 0.065871 | 0.064773 | -5.343e-05 | 5.5488e-05 | -0.0031232 | 0.010864 | 0.0015295 | 0.00085443 | -0.00058098 | -0.0015061 | -0.0010937 | -0.0031787 | -39.6057 | 65.6479 | -57.312 | 65.4968 | -56.9366 | -57.4081 | -57.3669 | -45.9229 | 65.6937 | -57.2525 | -57.1014 | -57.1381 | -57.3257 | -56.9916 | -0.086975 | -0.041199 | -0.19226 | 0.28839 | -0.14191 | -0.1831 | -0.054931 | -0.09613 | -0.027465 | 0.004578 | -122.7905 | 0.086975 | 0.23346 | -0.10071 | 0.26093 | -0.073243 | 0.37537 | 122.8088 | 0.11444 | 0.15106 | 122.9599 | 122.9462 | 122.8729 | 122.9187 | -123.0011 | -122.9416 | 122.7219 | 0.1236 | 17.6193 | 11.3022
874.1719 | 123.0652 | -57.225 | 65.6982 | -0.052948 | 0.0019035 | 0.062666 | 0.063064 | 0.0029374 | 0.00026909 | -0.0029096 | -0.0043946 | -0.00039305 | 0.00085443 | -0.002931 | -0.0025741 | -0.0023755 | 0.00023934 | -39.6698 | 65.6845 | -57.3166 | 65.4922 | -56.9412 | -57.4173 | -57.3578 | -46.019 | 65.7166 | -57.2479 | -57.1198 | -57.1381 | -57.3029 | -57.0236 | -0.091552 | -0.013733 | -0.20599 | 0.28381 | -0.13275 | -0.19226 | -0.041199 | -0.10071 | -0.022888 | 0.018311 | -122.818 | 0.086975 | 0.20142 | -0.077819 | 0.2243 | -0.054931 | 0.37537 | 122.8088 | 0.10986 | 0.12817 | 123.0011 | 122.9645 | 122.9095 | 122.9416 | -123.0148 | -122.9462 | 122.7173 | 0.10529 | 17.5552 | 11.2061
875.1719 | 123.1155 | -57.225 | 65.625 | -0.12161 | 0.0012625 | 0.063521 | 0.06285 | 0.00016017 | 0.00091009 | -0.00077341 | 0.056641 | 0.0013159 | -0.0010682 | -0.0067762 | 0.0010575 | -0.0036573 | 0.0036571 | -39.8026 | 65.5975 | -57.312 | 65.5014 | -56.9183 | -57.4127 | -57.3166 | -46.0648 | 65.625 | -57.2479 | -57.0969 | -57.1381 | -57.2983 | -56.9824 | -0.086975 | -0.027466 | -0.1236 | 0.3067 | -0.091552 | -0.18768 | -0.004577 | -0.10071 | -0.022888 | 0 | -122.7219 | 0.086975 | 0.24262 | -0.073242 | 0.2655 | -0.050354 | 0.39368 | 122.8134 | 0.10986 | 0.15106 | 122.9095 | 122.8729 | 122.8226 | 122.85 | -122.937 | -122.8729 | 122.7264 | 0.12817 | 17.4225 | 11.1603
876.1719 | 123.0469 | -57.225 | 65.6754 | -0.03006 | 0.00062166 | 0.062453 | 0.065414 | 0.0020828 | 0.0021917 | 0.0026446 | 0.023071 | 0.0017431 | -0.00085457 | -0.005708 | -0.0019333 | -0.00066648 | -0.0023243 | -39.8849 | 65.6891 | -57.3212 | 65.4602 | -56.9962 | -57.4356 | -57.3715 | -46.2387 | 65.7303 | -57.2479 | -57.1243 | -57.1518 | -57.3303 | -57.0236 | -0.09613 | 0.013733 | -0.21515 | 0.22888 | -0.14648 | -0.21057 | -0.050354 | -0.11444 | -0.022888 | 0.054932 | -122.7997 | 0.073243 | 0.20142 | -0.10529 | 0.2243 | -0.082397 | 0.32501 | 122.7814 | 0.096131 | 0.1236 | 123.0103 | 122.9782 | 122.9141 | 122.9553 | -122.9965 | -122.9233 | 122.6852 | 0.10071 | 17.3401 | 10.9863
877.1719 | 123.0972 | -57.2205 | 65.6342 | -0.13687 | 0.00062166 | 0.063734 | 0.061141 | -0.00090783 | 0.00026909 | 0.002431 | 0.029175 | -0.0012477 | 0.001709 | -0.0061352 | -0.00065151 | -0.0021619 | 0.00045294 | -39.949 | 65.5838 | -57.3166 | 65.506 | -56.9046 | -57.4356 | -57.3166 | -46.2433 | 65.6158 | -57.2708 | -57.1106 | -57.1564 | -57.2937 | -57.0007 | -0.09613 | -0.050354 | -0.12817 | 0.31586 | -0.09613 | -0.21515 | 0 | -0.11902 | -0.050354 | -0.01831 | -122.7448 | 0.064087 | 0.21973 | -0.073242 | 0.27008 | -0.022888 | 0.41199 | 122.8226 | 0.11444 | 0.16022 | 122.9004 | 122.8867 | 122.8043 | 122.8363 | -122.9507 | -122.905 | 122.7264 | 0.10986 | 17.2714 | 10.9772
878.1719 | 123.0881 | -57.2342 | 65.6616 | -0.052948 | -1.9142e-05 | 0.06523 | 0.065841 | 0.0016556 | 5.5488e-05 | 0.00093559 | -0.0013428 | 0.0015295 | 0.00085443 | 0.0030506 | -0.0021469 | -0.0023755 | -0.0025379 | -39.9948 | 65.6708 | -57.3029 | 65.4968 | -56.9366 | -57.4265 | -57.3624 | -46.3165 | 65.6891 | -57.2708 | -57.1106 | -57.1518 | -57.3257 | -57.0099 | -0.068664 | 0.009155 | -0.16479 | 0.29755 | -0.12817 | -0.19226 | -0.05951 | -0.1236 | -0.036621 | 0.027466 | -122.7722 | 0.082398 | 0.2243 | -0.091553 | 0.26093 | -0.054932 | 0.36621 | 122.7997 | 0.11902 | 0.16022 | 122.9736 | 122.9599 | 122.905 | 122.9233 | -122.9645 | -122.9324 | 122.731 | 0.1236 | 17.2394 | 10.9177
879.1719 | 123.0698 | -57.2296 | 65.6845 | -0.060578 | 0.00083526 | 0.063307 | 0.0652 | -0.0021896 | -0.0018671 | -0.0016278 | 0.013916 | 0.0025975 | -0.00064077 | -0.00015378 | -0.0012925 | -0.0010937 | -0.0021107 | -40.0955 | 65.657 | -57.3166 | 65.5334 | -56.9458 | -57.3944 | -57.3441 | -46.3852 | 65.6982 | -57.28 | -57.1289 | -57.1655 | -57.3441 | -57.0282 | -0.086975 | -0.027466 | -0.15106 | 0.28381 | -0.11444 | -0.1648 | -0.027466 | -0.07782 | -0.050354 | 0.013733 | -122.8134 | 0.064087 | 0.20142 | -0.11444 | 0.25177 | -0.064087 | 0.37079 | 122.85 | 0.11444 | 0.15106 | 122.9736 | 122.9782 | 122.8867 | 122.9279 | -123.0011 | -122.9645 | 122.7631 | 0.10071 | 17.1341 | 10.8444
880.1719 | 123.1567 | -57.2388 | 65.625 | -0.060578 | -0.00023294 | 0.064162 | 0.062423 | -5.343e-05 | 0.00026909 | -0.002055 | -0.0074462 | 0.0023839 | -0.0014954 | -0.00036738 | -0.00065151 | -0.00045288 | 0.0019483 | -40.21 | 65.6113 | -57.3441 | 65.4968 | -56.955 | -57.431 | -57.3257 | -46.4676 | 65.625 | -57.2617 | -57.074 | -57.1335 | -57.2754 | -56.9733 | -0.10528 | -0.013733 | -0.12817 | 0.28381 | -0.086975 | -0.19226 | 0.01831 | -0.086975 | -0.022888 | 0 | -122.699 | 0.10529 | 0.2655 | -0.036621 | 0.28839 | -0.013733 | 0.3891 | 122.8409 | 0.12817 | 0.18768 | 122.9553 | 122.8867 | 122.85 | 122.8638 | -122.9691 | -122.8867 | 122.7356 | 0.1648 | 17.0288 | 10.7712
881.1719 | 123.0423 | -57.2205 | 65.6937 | -0.03006 | -0.00066014 | 0.061598 | 0.062636 | -0.0032578 | -0.0012261 | -0.00013241 | 0.013916 | 0.0011023 | 0.00021363 | 0.0019824 | -0.0030013 | -0.0015211 | 0.0042981 | -40.2557 | 65.7028 | -57.3074 | 65.3915 | -56.9733 | -57.4677 | -57.399 | -46.6232 | 65.7211 | -57.2662 | -57.1609 | -57.1884 | -57.3303 | -57.0557 | -0.086975 | 0.009155 | -0.30212 | 0.24719 | -0.17853 | -0.24719 | -0.091553 | -0.16022 | -0.045776 | 0.027465 | -122.8546 | 0.032043 | 0.16479 | -0.10986 | 0.21057 | -0.064087 | 0.33417 | 122.699 | 0.077819 | 0.10529 | 123.0103 | 122.9874 | 122.9233 | 122.9416 | -123.0011 | -122.9599 | 122.612 | 0.059509 | 16.9647 | 10.5972
882.1719 | 123.1384 | -57.225 | 65.6342 | -0.12924 | 0.0010489 | 0.062239 | 0.064773 | 0.0010148 | 0.00026909 | -0.00034601 | -0.0013428 | 3.4148e-05 | 0.0019226 | -0.0016492 | -0.00086511 | -0.00088008 | -0.0012561 | -40.3656 | 65.6067 | -57.3303 | 65.5014 | -56.9183 | -57.3944 | -57.3257 | -46.6003 | 65.6433 | -57.28 | -57.0786 | -57.1243 | -57.2754 | -56.9641 | -0.10529 | -0.027466 | -0.13275 | 0.3067 | -0.10071 | -0.16937 | 0.004577 | -0.064087 | -0.054931 | 0.009156 | -122.7127 | 0.10071 | 0.26093 | -0.050354 | 0.31586 | 0.004577 | 0.41199 | 122.8317 | 0.15564 | 0.20142 | 122.937 | 122.9233 | 122.8317 | 122.8683 | -122.9645 | -122.9141 | 122.7264 | 0.14648 | 16.8594 | 10.6247
883.1719 | 123.0606 | -57.2159 | 65.6891 | 0.015716 | 0.0010489 | 0.064803 | 0.064559 | -0.0034714 | -0.00015811 | -0.00055961 | -0.025757 | 0.0013159 | 0.00064083 | 0.0024096 | -0.0015061 | -0.0015211 | -0.00018806 | -40.4068 | 65.6891 | -57.3303 | 65.4877 | -56.955 | -57.4081 | -57.3486 | -46.756 | 65.7303 | -57.2617 | -57.1152 | -57.1426 | -57.3257 | -57.0053 | -0.11444 | 0 | -0.20142 | 0.26093 | -0.13275 | -0.19226 | -0.018311 | -0.07782 | -0.045777 | 0.041199 | -122.8043 | 0.073242 | 0.21057 | -0.10986 | 0.25635 | -0.064087 | 0.37537 | 122.818 | 0.11902 | 0.14648 | 123.0194 | 122.9919 | 122.905 | 122.9462 | -123.0194 | -122.9507 | 122.7036 | 0.10071 | 16.8091 | 10.4599
884.1719 | 123.0331 | -57.2205 | 65.7074 | -0.098725 | 0.00083526 | 0.06288 | 0.063277 | -0.001976 | 0.00069649 | 0.003072 | 0.044434 | 0.0017431 | 0.00064083 | -0.0016492 | 0.0014847 | -0.0038709 | -0.0021107 | -40.4297 | 65.6479 | -57.2662 | 65.4785 | -56.9229 | -57.4036 | -57.3486 | -46.7926 | 65.7211 | -57.2388 | -57.1564 | -57.1472 | -57.3303 | -57.0511 | -0.045776 | -0.059509 | -0.22888 | 0.29755 | -0.12817 | -0.18311 | -0.082398 | -0.13733 | -0.018311 | 0.013733 | -122.8638 | 0.073242 | 0.16937 | -0.10986 | 0.18768 | -0.091552 | 0.34332 | 122.7448 | 0.091553 | 0.082398 | 122.9141 | 122.9599 | 122.8683 | 122.9416 | -122.9736 | -122.9462 | 122.699 | 0.064087 | 16.7908 | 10.4279
885.1719 | 123.0469 | -57.2296 | 65.7303 | -0.0071715 | -0.0010873 | 0.062666 | 0.061996 | -0.0062484 | -0.0016535 | -0.00077341 | 0.02002 | 0.00024775 | 0.0025634 | 5.9824e-05 | 0.00020289 | -0.0021619 | -0.00040166 | -40.4663 | 65.657 | -57.2891 | 65.5151 | -56.8863 | -57.3669 | -57.2983 | -46.8704 | 65.7074 | -57.2479 | -57.1198 | -57.1381 | -57.3029 | -57.0511 | -0.05951 | -0.073243 | -0.21515 | 0.34332 | -0.068665 | -0.13733 | -0.009155 | -0.077819 | -0.018311 | -0.022889 | -122.85 | 0.091552 | 0.17853 | -0.073242 | 0.19684 | -0.054931 | 0.40283 | 122.8043 | 0.10986 | 0.12817 | 122.9462 | 122.9553 | 122.8867 | 122.937 | -123.0194 | -122.9782 | 122.7448 | 0.10986 | 16.7633 | 10.3592
886.1719 | 123.0606 | -57.2205 | 65.7257 | -0.014801 | 0.0025443 | 0.061812 | 0.065841 | 0.0010148 | -0.00037171 | 0.0015766 | -0.010498 | 0.00088875 | 0.00085443 | -0.0014356 | -0.00043791 | -0.0021619 | -0.0018971 | -40.4434 | 65.7532 | -57.2662 | 65.4648 | -56.9778 | -57.4081 | -57.3578 | -46.9803 | 65.7257 | -57.2342 | -57.1289 | -57.1426 | -57.3257 | -57.0145 | -0.045776 | 0.027466 | -0.26093 | 0.24262 | -0.13733 | -0.18768 | -0.091553 | -0.14191 | -0.013733 | 0 | -122.8546 | 0.07782 | 0.20599 | -0.10529 | 0.21973 | -0.091553 | 0.28839 | 122.731 | 0.091553 | 0.10529 | 123.0194 | 122.9599 | 122.9736 | 122.9462 | -122.9919 | -122.9599 | 122.6852 | 0.091553 | 16.777 | 10.2402
887.1719 | 123.1247 | -57.193 | 65.6799 | -0.052948 | -1.9142e-05 | 0.062239 | 0.063705 | -0.0011214 | -0.00058531 | 0.0022174 | -0.0043946 | 3.4148e-05 | 0.0019226 | -0.0010084 | -1.0706e-05 | -0.00045288 | 0.00088014 | -40.7639 | 65.6525 | -57.3349 | 65.4694 | -56.955 | -57.4539 | -57.3441 | -47.0535 | 65.6754 | -57.2571 | -57.0648 | -57.1198 | -57.312 | -56.9641 | -0.14191 | -0.027466 | -0.21057 | 0.23804 | -0.15106 | -0.26093 | -0.009155 | -0.11902 | -0.064087 | -0.004578 | -122.7448 | 0.073242 | 0.22888 | -0.11902 | 0.29297 | -0.054932 | 0.37994 | 122.8043 | 0.13733 | 0.19226 | 122.9874 | 122.9324 | 122.8455 | 122.8683 | -123.0148 | -122.937 | 122.6624 | 0.12817 | 16.4291 | 10.1395
888.1719 | 123.1293 | -57.1793 | 65.7074 | -0.022431 | 0.0016899 | 0.061385 | 0.062636 | -0.00090783 | 0.0015509 | 0.0015766 | 0.071899 | -0.0010339 | 0.00042723 | -0.0052808 | -0.00043791 | -0.0025891 | -0.00061526 | -40.5029 | 65.7303 | -57.225 | 65.5746 | -56.7902 | -57.2983 | -57.2342 | -46.9482 | 65.7257 | -57.193 | -57.019 | -57.0282 | -57.2021 | -56.9321 | -0.045777 | 0.022889 | -0.13275 | 0.3891 | -0.054932 | -0.11902 | -0.009155 | -0.073242 | -0.013733 | 0.018311 | -122.7264 | 0.15106 | 0.24719 | -0.022888 | 0.26093 | -0.009155 | 0.43488 | 122.7997 | 0.16479 | 0.17395 | 122.9553 | 122.9187 | 122.9095 | 122.905 | -122.9324 | -122.9004 | 122.7539 | 0.16022 | 16.6763 | 10.231
889.1719 | 123.0423 | -57.1976 | 65.7623 | -0.068207 | 0.0016899 | 0.064162 | 0.064132 | -0.0015488 | -0.0012261 | -0.0039776 | 0.029175 | -0.00017945 | 0.003418 | -0.00058098 | -0.0021469 | -0.0010937 | 0.0010937 | -40.8325 | 65.7349 | -57.28 | 65.5106 | -56.9183 | -57.3944 | -57.3029 | -47.1634 | 65.7486 | -57.1976 | -57.1152 | -57.1152 | -57.2891 | -57.0099 | -0.082397 | -0.027466 | -0.25177 | 0.27924 | -0.10528 | -0.19684 | -0.022888 | -0.11444 | 0 | -0.013733 | -122.8775 | 0.082398 | 0.18768 | -0.091553 | 0.18768 | -0.091553 | 0.36163 | 122.7905 | 0.082398 | 0.082398 | 123.0148 | 122.9462 | 122.9324 | 122.9462 | -123.0423 | -122.9599 | 122.7081 | 0.082398 | 16.3651 | 10.0342
890.1719 | 123.0194 | -57.193 | 65.7074 | -0.068207 | -0.00044654 | 0.064803 | 0.065414 | 0.0037918 | -0.00058531 | 0.00050839 | -0.044067 | 0.0013159 | 0.001068 | 0.0043322 | -0.0010787 | -0.00023928 | 0.00088014 | -40.9927 | 65.6708 | -57.3486 | 65.4465 | -57.019 | -57.4768 | -57.399 | -47.3328 | 65.7394 | -57.2479 | -57.1381 | -57.1793 | -57.3715 | -57.0465 | -0.15564 | -0.036621 | -0.26093 | 0.17395 | -0.20599 | -0.28381 | -0.050354 | -0.12817 | -0.054932 | 0.032044 | -122.8455 | 0.013733 | 0.14648 | -0.17853 | 0.20142 | -0.1236 | 0.32959 | 122.7951 | 0.068665 | 0.10986 | 123.0194 | 122.9874 | 122.8638 | 122.9324 | -123.056 | -122.9553 | 122.6395 | 0.054931 | 16.2003 | 9.8602
891.1719 | 123.0011 | -57.1701 | 65.7623 | -0.014801 | 0.00040806 | 0.061598 | 0.061782 | -0.0032578 | 0.0011237 | 0.00072199 | 0.010864 | 0.00067495 | 0.001709 | -0.00058098 | 0.00020289 | -0.0036573 | -0.0018971 | -41.0477 | 65.744 | -57.2891 | 65.5014 | -56.9092 | -57.3898 | -57.3303 | -47.3007 | 65.7715 | -57.2159 | -57.106 | -57.1564 | -57.0328 | -56.8954 | -0.11902 | -0.01831 | -0.26093 | 0.26093 | -0.16022 | -0.21973 | -0.041198 | -0.10071 | -0.045776 | 0.009155 | -122.8683 | 0.013733 | 0.27466 | 0.13733 | 0.32043 | 0.18311 | 0.37994 | 122.7905 | 0.059509 | 0.10986 | 123.0331 | 122.9874 | 122.9141 | 122.9416 | -123.0515 | -122.9782 | 122.6715 | 0.064087 | 16.1224 | 9.8694
892.1719 | 122.9919 | -57.2067 | 65.7303 | -0.12161 | -1.9142e-05 | 0.06288 | 0.06755 | 0.0027238 | -0.0010125 | 0.00050839 | -0.044067 | 0.0011023 | 0.001068 | -0.0020764 | 0.0019119 | 0.00018792 | -0.0012561 | -41.1804 | 65.6982 | -57.3074 | 65.4373 | -57.0099 | -57.4905 | -57.3715 | -47.438 | 65.7394 | -57.2479 | -57.3074 | -56.9 | -57.1472 | -56.955 | -0.10071 | -0.032044 | -0.29297 | 0.19684 | -0.16479 | -0.28381 | -0.064087 | -0.18311 | -0.041199 | 0.009155 | -123.0377 | 0.3067 | 0.25177 | 0.059509 | 0.29297 | 0.10071 | 0.29755 | 122.7448 | 0.3479 | -0.059509 | 123.0057 | 122.9874 | 122.905 | 122.9462 | -123.0377 | -122.9782 | 122.644 | -0.10071 | 16.0263 | 9.7687
893.1719 | 123.1293 | -57.1701 | 65.7486 | -0.045319 | 0.0010489 | 0.064162 | 0.062636 | 0.00080117 | -0.0018671 | 0.00093559 | 0.032227 | -0.00017945 | 0.0012818 | -0.0020764 | 0.0016983 | -0.0032301 | -0.0021107 | -41.1209 | 65.6937 | -57.225 | 65.5975 | -56.7902 | -57.2937 | -57.2113 | -47.3007 | 65.7303 | -57.2067 | -57.0007 | -57.019 | -57.193 | -56.9229 | -0.054932 | -0.054931 | -0.15106 | 0.37994 | -0.041199 | -0.1236 | 0.013733 | -0.068664 | -0.036621 | -0.01831 | -122.7493 | 0.15106 | 0.24719 | -0.022888 | 0.28381 | 0.013733 | 0.43488 | 122.8226 | 0.18768 | 0.20599 | 122.9187 | 122.937 | 122.8638 | 122.9004 | -122.9736 | -122.9553 | 122.7676 | 0.16937 | 16.0492 | 9.8694
894.1719 | 123.1613 | -57.1335 | 65.7394 | -0.060578 | 0.00019446 | 0.064375 | 0.062209 | -0.00069423 | 0.00026909 | -0.0012006 | 0.081055 | -0.0010339 | 2.8e-08 | 0.0017688 | -0.0023605 | -0.0023755 | -0.0036059 | -41.2079 | 65.6845 | -57.2479 | 65.6296 | -56.7535 | -57.2708 | -57.1701 | -47.3053 | 65.6845 | -57.1609 | -56.9641 | -56.9824 | -57.1564 | -56.8909 | -0.11444 | -0.054932 | -0.10986 | 0.37994 | -0.036621 | -0.13733 | 0.07782 | -0.022888 | -0.027466 | -0.054932 | -122.7036 | 0.15106 | 0.24262 | -0.022888 | 0.27008 | 0.004578 | 0.49439 | 122.8775 | 0.17853 | 0.19684 | 122.9324 | 122.8455 | 122.818 | 122.818 | -122.9874 | -122.9004 | 122.7631 | 0.16937 | 15.9256 | 9.8282
895.1719 | 123.0743 | -57.1701 | 65.7669 | -0.31235 | 0.00019446 | 0.062453 | 0.068832 | 0.00080117 | 0.0013373 | -0.00055961 | -0.041016 | 3.4148e-05 | -0.001709 | -0.0010084 | -0.0023605 | -0.00023928 | -0.0023243 | -41.2766 | 65.7074 | -57.28 | 65.5609 | -56.8634 | -57.3715 | -57.2983 | -47.493 | 65.744 | -57.2067 | -57.0602 | -57.1014 | -57.3029 | -56.987 | -0.10986 | -0.05951 | -0.20599 | 0.3067 | -0.12817 | -0.20142 | -0.018311 | -0.091553 | -0.036621 | -0.022888 | -122.8271 | 0.068665 | 0.1831 | -0.13275 | 0.21973 | -0.09613 | 0.41656 | 122.8409 | 0.10529 | 0.14648 | 122.9874 | 122.9507 | 122.8775 | 122.9141 | -123.0469 | -122.9736 | 122.731 | 0.10986 | 15.8936 | 9.6771
896.1719 | 123.0286 | -57.1655 | 65.7623 | -0.045319 | -1.9142e-05 | 0.062666 | 0.064559 | 0.0010148 | 0.0026191 | -0.00098701 | 0.032227 | 0.00024775 | 0.0012818 | -0.00079478 | 0.00020289 | -0.0042981 | 0.0013073 | -41.3544 | 65.7166 | -57.2342 | 65.5609 | -56.8359 | -57.3212 | -57.2525 | -47.5388 | 65.7532 | -57.1793 | -57.0694 | -57.1014 | -57.2617 | -56.9824 | -0.068665 | -0.045776 | -0.20142 | 0.32959 | -0.086975 | -0.15564 | -0.01831 | -0.086975 | -0.013733 | -0.009155 | -122.8317 | 0.064087 | 0.1831 | -0.096131 | 0.19684 | -0.082398 | 0.39825 | 122.7951 | 0.07782 | 0.10986 | 122.9507 | 122.9324 | 122.8821 | 122.9187 | -122.9965 | -122.9416 | 122.7264 | 0.09613 | 15.8112 | 9.6268
897.1719 | 123.1064 | -57.1884 | 65.7578 | -0.060578 | 0.0048941 | 0.063094 | 0.064345 | 0.0044328 | 0.00026909 | 8.1188e-05 | -0.016602 | 0.00067495 | -0.00064077 | 0.0024096 | -0.0012925 | -0.0023755 | -0.0038197 | -41.4368 | 65.7166 | -57.2662 | 65.5426 | -56.8726 | -57.3669 | -57.2937 | -47.5937 | 65.7532 | -57.2205 | -57.1289 | -57.1701 | -57.2388 | -56.9504 | -0.077819 | -0.041198 | -0.21515 | 0.31586 | -0.10529 | -0.17853 | -0.027466 | -0.10071 | -0.032043 | -0.004577 | -122.8867 | 0.018311 | 0.23804 | -0.050354 | 0.27008 | -0.018311 | 0.39368 | 122.8088 | 0.050354 | 0.091553 | 122.9828 | 122.9736 | 122.905 | 122.9416 | -123.024 | -122.9782 | 122.731 | 0.05951 | 15.7516 | 9.5947
898.1719 | 123.1705 | -57.1564 | 65.7074 | -0.052948 | 0.0021171 | 0.063734 | 0.062423 | -0.0032578 | -0.00079891 | 0.00050839 | 0.078003 | 0.00088875 | 0.0021362 | -0.00079478 | 0.00020289 | -0.0025891 | 0.00045294 | -41.4825 | 65.6708 | -57.2433 | 65.6158 | -56.7581 | -57.2708 | -57.1838 | -47.5662 | 65.6982 | -57.1609 | -56.987 | -56.9962 | -57.2021 | -56.9412 | -0.086975 | -0.036621 | -0.091552 | 0.39825 | -0.027466 | -0.11444 | 0.059509 | -0.027466 | -0.004578 | -0.009155 | -122.6944 | 0.16022 | 0.21515 | -0.045776 | 0.21973 | -0.041198 | 0.48523 | 122.8592 | 0.16479 | 0.17395 | 122.9141 | 122.8592 | 122.8271 | 122.8546 | -122.9507 | -122.8683 | 122.7722 | 0.16937 | 15.6738 | 9.5901
899.1719 | 123.1201 | -57.1381 | 65.7257 | -0.2742 | 0.0019035 | 0.062453 | 0.061141 | 0.0035782 | 0.00026909 | -0.00055961 | 0.047485 | -0.00017945 | 0.002777 | -0.0035718 | -0.0012925 | -0.00023928 | -0.0010425 | -41.5329 | 65.6754 | -57.2342 | 65.5975 | -56.7673 | -57.28 | -57.1976 | -47.6578 | 65.7257 | -57.1793 | -57.0099 | -57.0053 | -57.1793 | -56.9229 | -0.09613 | -0.050354 | -0.12817 | 0.37079 | -0.059509 | -0.14191 | 0.036621 | -0.045776 | -0.041198 | 0 | -122.7356 | 0.13275 | 0.21515 | -0.041198 | 0.25635 | 0 | 0.46692 | 122.8317 | 0.17395 | 0.16937 | 122.9095 | 122.905 | 122.8134 | 122.8638 | -122.9599 | -122.905 | 122.7356 | 0.12817 | 15.6052 | 9.4803
900.1719 | 123.0652 | -57.1655 | 65.7578 | -0.052948 | 0.00062166 | 0.063307 | 0.064132 | 0.0016556 | -0.0016535 | 0.00072199 | -0.028809 | 0.0011023 | 0.00085443 | -0.00229 | -0.0038559 | -0.00088008 | 0.00088014 | -41.7023 | 65.7257 | -57.2891 | 65.5243 | -56.8863 | -57.3624 | -57.3029 | -47.8043 | 65.744 | -57.2205 | -57.0694 | -57.0786 | -57.2708 | -56.9687 | -0.1236 | -0.032043 | -0.23346 | 0.27923 | -0.13733 | -0.19684 | -0.013732 | -0.073242 | -0.054932 | -0.013732 | -122.8271 | 0.086975 | 0.19684 | -0.10529 | 0.25177 | -0.050354 | 0.40283 | 122.8134 | 0.14191 | 0.15106 | 123.0148 | 122.9645 | 122.8912 | 122.9095 | -123.0469 | -122.9782 | 122.6898 | 0.09613 | 15.4633 | 9.3613
901.1719 | 123.1476 | -57.1518 | 65.7074 | -0.11398 | -0.00087374 | 0.064162 | 0.060927 | 0.0018692 | 0.00069649 | 0.0011494 | 0.078003 | 3.4148e-05 | 0.00064083 | -0.0031446 | 0.00084389 | -0.0040845 | 0.00088014 | -41.6519 | 65.6799 | -57.2617 | 65.5655 | -56.7993 | -57.312 | -57.1976 | -47.7814 | 65.7257 | -57.193 | -56.9916 | -56.9962 | -57.1243 | -56.9046 | -0.10986 | -0.027465 | -0.14191 | 0.35248 | -0.045777 | -0.16022 | 0.064087 | -0.050354 | -0.041199 | 0.018311 | -122.699 | 0.15564 | 0.24719 | 0.027465 | 0.28839 | 0.068664 | 0.46234 | 122.8271 | 0.19684 | 0.20142 | 122.9416 | 122.9187 | 122.8317 | 122.8775 | -122.9691 | -122.9004 | 122.7173 | 0.16022 | 15.4999 | 9.3704
902.1719 | 123.1522 | -57.1793 | 65.7257 | -0.098725 | -0.00044654 | 0.063307 | 0.061782 | -0.00026703 | 0.00026909 | -0.00098701 | 0.068848 | 0.00024775 | 0.00064083 | -0.0042126 | -0.0012925 | -0.0025891 | -0.00018806 | -41.7389 | 65.6799 | -57.2433 | 65.5792 | -56.8451 | -57.3166 | -57.2342 | -47.8912 | 65.6937 | -57.1884 | -57.0145 | -57.0328 | -57.2159 | -56.9138 | -0.064087 | -0.045776 | -0.14648 | 0.33417 | -0.054932 | -0.13733 | 0.009155 | -0.073242 | -0.009156 | -0.032043 | -122.7402 | 0.14648 | 0.2655 | -0.036621 | 0.27466 | -0.027465 | 0.39825 | 122.8226 | 0.15564 | 0.17395 | 122.9233 | 122.8821 | 122.8592 | 122.8729 | -122.9691 | -122.9141 | 122.7585 | 0.16479 | 15.4404 | 9.288
903.1719 | 123.1201 | -57.1564 | 65.7028 | -0.037689 | -0.00066014 | 0.063094 | 0.061568 | -5.343e-05 | 5.5488e-05 | 0.003072 | 0.03833 | -0.00017945 | -0.00064077 | 0.00070062 | -0.0030013 | -0.0030163 | -0.00040166 | -41.7801 | 65.7028 | -57.2479 | 65.6158 | -56.7673 | -57.2617 | -57.1976 | -47.8821 | 65.7349 | -57.1655 | -56.955 | -57.0282 | -57.2067 | -56.9321 | -0.091553 | 0 | -0.086975 | 0.3891 | -0.041199 | -0.10529 | 0.050354 | -0.013733 | -0.009155 | 0.032043 | -122.6578 | 0.12817 | 0.2243 | -0.050354 | 0.23346 | -0.041199 | 0.48065 | 122.8638 | 0.13733 | 0.21057 | 122.9507 | 122.9004 | 122.8592 | 122.8912 | -122.9507 | -122.8683 | 122.7722 | 0.20142 | 15.3763 | 9.2743
904.1719 | 123.1201 | -57.1793 | 65.6937 | -0.10635 | -0.0013009 | 0.063307 | 0.064986 | -0.0041122 | 0.00026909 | -0.0033368 | 0.029175 | -0.00017945 | -0.0014954 | -0.007417 | -0.0023605 | -0.0019483 | 0.00023934 | -41.9357 | 65.6616 | -57.28 | 65.5151 | -56.9046 | -57.3898 | -57.2662 | -48.0789 | 65.7166 | -57.2433 | -57.0374 | -57.0602 | -57.2342 | -56.9595 | -0.10071 | -0.032044 | -0.17853 | 0.27466 | -0.086975 | -0.21057 | 0.013733 | -0.10986 | -0.064087 | 0.022888 | -122.731 | 0.11902 | 0.21973 | -0.054932 | 0.28381 | 0.009155 | 0.37537 | 122.7951 | 0.1831 | 0.20599 | 122.9416 | 122.9599 | 122.8409 | 122.8958 | -122.9736 | -122.937 | 122.6944 | 0.14191 | 15.2435 | 9.1003
905.1719 | 123.111 | -57.1564 | 65.7257 | -0.075836 | 0.0025443 | 0.063307 | 0.061782 | -0.0013352 | -0.0027215 | -0.0022686 | 0.0047608 | -0.00017945 | 0.0014954 | 0.0013416 | -0.0034287 | -0.00045288 | -0.0025379 | -41.9357 | 65.6433 | -57.2754 | 65.6021 | -56.8085 | -57.2983 | -57.2113 | -48.0331 | 65.7623 | -57.1884 | -57.0236 | -57.0419 | -57.2113 | -56.9412 | -0.11902 | -0.082397 | -0.1236 | 0.3479 | -0.054932 | -0.14191 | 0.064087 | -0.022888 | -0.032044 | 0.036621 | -122.7493 | 0.11444 | 0.21515 | -0.054932 | 0.24719 | -0.022888 | 0.46692 | 122.8775 | 0.14648 | 0.16479 | 122.9187 | 122.9507 | 122.7997 | 122.9187 | -123.0011 | -122.9141 | 122.7585 | 0.13275 | 15.2206 | 9.1232
906.1719 | 123.1064 | -57.1701 | 65.7074 | -0.075836 | -0.00044654 | 0.062453 | 0.062209 | 0.0016556 | 0.00069649 | 0.00072199 | 0.001709 | 0.00067495 | 0.00064083 | 0.0028368 | -0.0012925 | -0.0030163 | 0.0036571 | -41.9586 | 65.6708 | -57.2754 | 65.5243 | -56.8863 | -57.3441 | -57.2708 | -48.1613 | 65.712 | -57.2067 | -57.0419 | -57.0557 | -57.2342 | -56.9641 | -0.10529 | -0.036621 | -0.1831 | 0.28381 | -0.10071 | -0.17395 | 0.004578 | -0.068664 | -0.036621 | 0.004578 | -122.7493 | 0.11444 | 0.20599 | -0.064087 | 0.24262 | -0.027466 | 0.3891 | 122.7997 | 0.15106 | 0.1648 | 122.9462 | 122.9187 | 122.8409 | 122.8821 | -122.9828 | -122.9141 | 122.6944 | 0.12817 | 15.2115 | 9.0088
907.1719 | 123.111 | -57.1655 | 65.7211 | -0.12924 | -1.9142e-05 | 0.063307 | 0.062423 | -0.001976 | 0.00026909 | -0.0016278 | 0.03833 | -0.00017945 | -0.00064077 | -0.0016492 | -0.0023605 | -0.0021619 | -0.0042469 | -41.9998 | 65.6662 | -57.28 | 65.5563 | -56.8542 | -57.3212 | -57.2205 | -48.1888 | 65.6982 | -57.2021 | -57.0236 | -57.0099 | -57.2021 | -56.9321 | -0.11444 | -0.054931 | -0.16479 | 0.31128 | -0.054932 | -0.15564 | 0.059509 | -0.041199 | -0.036621 | -0.022888 | -122.7448 | 0.15564 | 0.23346 | -0.036621 | 0.27008 | 0 | 0.42572 | 122.8363 | 0.19226 | 0.17853 | 122.9462 | 122.9004 | 122.8317 | 122.8638 | -123.0011 | -122.9233 | 122.7219 | 0.14191 | 15.1657 | 8.9767
908.1719 | 123.111 | -57.1381 | 65.7211 | -0.13687 | -0.00023294 | 0.064589 | 0.064559 | -0.0032578 | -0.0010125 | 0.00414 | 0.03833 | 0.00067495 | -0.00021357 | -0.00058098 | -0.0017197 | -0.0021619 | 0.00066654 | -42.1143 | 65.6616 | -57.2708 | 65.5609 | -56.868 | -57.3578 | -57.2479 | -48.2758 | 65.712 | -57.1793 | -57.019 | -57.0328 | -57.2205 | -56.9458 | -0.13275 | -0.059509 | -0.16022 | 0.27008 | -0.10986 | -0.21973 | 0.022888 | -0.086975 | -0.041198 | -0.009155 | -122.7402 | 0.10529 | 0.19226 | -0.082397 | 0.23346 | -0.041199 | 0.40283 | 122.8317 | 0.14648 | 0.16022 | 122.9324 | 122.8912 | 122.7997 | 122.85 | -122.9919 | -122.9004 | 122.699 | 0.11902 | 15.0238 | 8.8623
909.1719 | 123.1934 | -57.1381 | 65.7257 | -0.037689 | -1.9142e-05 | 0.062453 | 0.062209 | -0.00090783 | 0.00026909 | -0.00013241 | 0.013916 | 0.00024775 | -0.0019226 | 0.0017688 | -0.00086511 | -0.0017347 | -0.0012561 | -42.1509 | 65.6937 | -57.2388 | 65.6433 | -56.7535 | -57.2662 | -57.1609 | -48.2254 | 65.7028 | -57.1564 | -56.9458 | -56.955 | -57.1472 | -56.868 | -0.10071 | -0.032043 | -0.082397 | 0.38452 | -0.022888 | -0.12817 | 0.07782 | -0.027465 | -0.01831 | -0.022888 | -122.6715 | 0.18311 | 0.27008 | -0.009155 | 0.28839 | 0.009155 | 0.48523 | 122.8821 | 0.20142 | 0.21057 | 122.9324 | 122.8592 | 122.8317 | 122.8409 | -122.9645 | -122.8821 | 122.7814 | 0.19226 | 14.9872 | 8.9127
910.1719 | 123.1201 | -57.1243 | 65.7532 | -0.060578 | 0.00040806 | 0.063307 | 0.065414 | 0.0035782 | 0.00091009 | -0.00055961 | 0.010864 | 0.00046135 | 0.00042723 | 0.0064684 | -0.0010787 | 0.00018792 | 2.554e-05 | -42.247 | 65.6982 | -57.2388 | 65.6204 | -56.781 | -57.2845 | -57.1655 | -48.3444 | 65.7578 | -57.193 | -56.9962 | -56.9916 | -57.193 | -56.9138 | -0.11444 | -0.054932 | -0.13275 | 0.34332 | -0.041198 | -0.16022 | 0.073243 | -0.045776 | -0.068664 | 0.004577 | -122.7493 | 0.13275 | 0.21057 | -0.068664 | 0.27924 | 0 | 0.45776 | 122.8592 | 0.20142 | 0.19684 | 122.937 | 122.9507 | 122.8226 | 122.8821 | -122.9919 | -122.9462 | 122.7448 | 0.12817 | 14.8773 | 8.7799
911.1719 | 123.1338 | -57.1655 | 65.7166 | -0.068207 | 0.0010489 | 0.062025 | 0.0652 | 0.0012284 | 0.0024053 | -0.00098701 | 0.001709 | -0.0014613 | -0.001709 | -0.0027174 | -0.00043791 | -0.0038709 | -0.0014697 | -42.3752 | 65.712 | -57.2525 | 65.5609 | -56.8588 | -57.3761 | -57.2525 | -48.5046 | 65.7074 | -57.1976 | -57.0145 | -57.0099 | -57.2205 | -56.9458 | -0.086975 | -0.004578 | -0.15564 | 0.3067 | -0.086975 | -0.21057 | 0 | -0.1236 | -0.032044 | -0.009156 | -122.731 | 0.15564 | 0.21973 | -0.054932 | 0.25177 | -0.022888 | 0.39368 | 122.8134 | 0.18768 | 0.18311 | 122.9645 | 122.905 | 122.8775 | 122.8729 | -122.9691 | -122.9141 | 122.7264 | 0.15106 | 14.7903 | 8.6609
912.1719 | 123.111 | -57.1518 | 65.6982 | -0.19028 | 0.00040806 | 0.063734 | 0.063918 | 0.0022964 | -0.0016535 | 0.001363 | -0.028809 | 0.00046135 | -0.0038452 | -0.0016492 | -0.0021469 | -0.0017347 | 0.00045294 | -42.4301 | 65.6662 | -57.2479 | 65.5838 | -56.8039 | -57.3303 | -57.2205 | -48.4817 | 65.6891 | -57.1976 | -56.987 | -57.0374 | -57.2067 | -56.9229 | -0.096131 | -0.032043 | -0.11444 | 0.3479 | -0.068665 | -0.17853 | 0.027466 | -0.082397 | -0.045777 | -0.009155 | -122.6852 | 0.11444 | 0.22888 | -0.054932 | 0.27466 | -0.009155 | 0.44403 | 122.8317 | 0.16022 | 0.21057 | 122.9141 | 122.8867 | 122.818 | 122.8409 | -122.9462 | -122.8958 | 122.7356 | 0.16479 | 14.7217 | 8.67
913.1719 | 123.1064 | -57.1564 | 65.7028 | -0.12924 | 0.0014761 | 0.062453 | 0.062423 | 0.0022964 | 0.0028327 | 0.00050839 | -0.0074462 | -0.00060665 | 0.00042723 | -0.0069898 | -0.0017197 | -0.0032301 | -0.0014697 | -42.5995 | 65.6479 | -57.2479 | 65.5792 | -56.8085 | -57.3395 | -57.2296 | -48.5641 | 65.7028 | -57.1747 | -57.019 | -57.0602 | -57.2205 | -56.9458 | -0.091553 | -0.054932 | -0.1236 | 0.3479 | -0.073242 | -0.18311 | 0.018311 | -0.091553 | -0.018311 | 0 | -122.7219 | 0.09613 | 0.21057 | -0.064087 | 0.22888 | -0.045776 | 0.43945 | 122.8271 | 0.11444 | 0.15564 | 122.8958 | 122.8775 | 122.8043 | 122.8592 | -122.9507 | -122.8775 | 122.7356 | 0.13733 | 14.5569 | 8.5922
914.1719 | 123.1064 | -57.1747 | 65.6525 | -0.10635 | 0.00019446 | 0.063307 | 0.064559 | -0.00090783 | -0.00037171 | -0.0016278 | -0.041016 | 0.0011023 | -0.0027772 | -0.00079478 | -0.0038559 | -0.00066648 | -0.0025379 | -42.6636 | 65.6342 | -57.2617 | 65.5838 | -56.8039 | -57.3257 | -57.2113 | -48.6237 | 65.7211 | -57.2021 | -56.9778 | -57.0328 | -57.2205 | -56.9275 | -0.086975 | -0.018311 | -0.068665 | 0.37079 | -0.036621 | -0.15106 | 0.050354 | -0.064087 | -0.027465 | 0.068664 | -122.6303 | 0.14191 | 0.24719 | -0.045776 | 0.27466 | -0.018311 | 0.45776 | 122.8455 | 0.16937 | 0.2243 | 122.8958 | 122.9233 | 122.8088 | 122.8958 | -122.9141 | -122.8546 | 122.7585 | 0.19684 | 14.5111 | 8.551
915.1719 | 123.1705 | -57.1243 | 65.7166 | -0.075836 | 0.00040806 | 0.066084 | 0.064345 | -0.001976 | -0.0010125 | -0.00098701 | -0.0013428 | -0.00017945 | 0.00085443 | -0.0010084 | -0.00022431 | -0.0036573 | 0.0017345 | -42.6453 | 65.7028 | -57.225 | 65.5975 | -56.7856 | -57.2617 | -57.193 | -48.6603 | 65.712 | -57.1655 | -56.9504 | -56.955 | -57.1335 | -56.868 | -0.10071 | -0.013733 | -0.11902 | 0.33875 | -0.068664 | -0.13733 | 0.032044 | -0.036621 | -0.041198 | -0.004578 | -122.6669 | 0.16937 | 0.25635 | -0.009155 | 0.29755 | 0.032043 | 0.43945 | 122.8226 | 0.21057 | 0.21515 | 122.9279 | 122.8775 | 122.8271 | 122.8363 | -122.9416 | -122.8821 | 122.7219 | 0.17395 | 14.4791 | 8.4641
916.1719 | 123.0881 | -57.1747 | 65.7211 | -0.098725 | 0.0021171 | 0.064375 | 0.062636 | 0.0012284 | 0.0019781 | 0.00029479 | 0.001709 | 0.0013159 | -0.0012818 | 0.0034778 | -0.00086511 | -0.0030163 | 0.00045294 | -42.7551 | 65.6708 | -57.2479 | 65.5655 | -56.8542 | -57.3624 | -57.2433 | -48.8159 | 65.7074 | -57.2067 | -57.0007 | -57.0374 | -57.2388 | -56.9321 | -0.073242 | -0.050354 | -0.15564 | 0.32044 | -0.068664 | -0.18768 | 0.004578 | -0.11444 | -0.032043 | -0.013733 | -122.7219 | 0.13733 | 0.24262 | -0.064087 | 0.27466 | -0.032044 | 0.39368 | 122.8134 | 0.16937 | 0.20599 | 122.9187 | 122.9141 | 122.8455 | 122.8821 | -122.9691 | -122.9279 | 122.7402 | 0.17395 | 14.4196 | 8.3588
917.1719 | 123.111 | -57.1381 | 65.7211 | -0.068207 | -0.0017281 | 0.061171 | 0.063491 | -5.343e-05 | 0.00048269 | -0.00098701 | 0.0078126 | -0.00039305 | 0.0021362 | -0.00464 | 0.0012711 | -0.0019483 | 0.0015209 | -42.7368 | 65.6845 | -57.2479 | 65.5838 | -56.8268 | -57.3029 | -57.1976 | -48.8754 | 65.7486 | -57.1701 | -56.987 | -57.0007 | -57.1884 | -56.9 | -0.10986 | -0.036621 | -0.13733 | 0.31128 | -0.059509 | -0.16479 | 0.050354 | -0.054931 | -0.032043 | 0.027466 | -122.7081 | 0.13733 | 0.23804 | -0.050354 | 0.27008 | -0.018311 | 0.42114 | 122.8317 | 0.16937 | 0.1831 | 122.9324 | 122.9187 | 122.8226 | 122.8867 | -122.9691 | -122.8912 | 122.7219 | 0.15106 | 14.4012 | 8.2626
918.1719 | 123.1476 | -57.1335 | 65.6982 | -0.12924 | -0.0017281 | 0.066725 | 0.063918 | 0.003151 | 0.00069649 | 0.00093559 | -0.059326 | 0.00024775 | 0.00021363 | -0.0054944 | -0.0025741 | -0.00066648 | -0.0057423 | -42.8741 | 65.6158 | -57.2617 | 65.6342 | -56.7993 | -57.3257 | -57.2205 | -48.9029 | 65.7074 | -57.1976 | -56.955 | -57.0236 | -57.1976 | -56.9138 | -0.12817 | -0.082397 | -0.064087 | 0.33417 | -0.086975 | -0.19226 | 0.041199 | -0.064087 | -0.064087 | 0.009155 | -122.6532 | 0.10986 | 0.21973 | -0.064087 | 0.28381 | 0 | 0.46234 | 122.8958 | 0.17395 | 0.24262 | 122.8775 | 122.905 | 122.7493 | 122.8409 | -122.9599 | -122.8958 | 122.7676 | 0.17853 | 14.2593 | 8.2306
919.1719 | 123.1064 | -57.1472 | 65.6982 | -0.075836 | 0.0012625 | 0.064162 | 0.063918 | 0.0022964 | -0.00079891 | 0.0015766 | -0.037964 | 3.4148e-05 | 0.0014954 | -0.0042126 | -0.0010787 | -0.0032301 | -0.00040166 | -42.8925 | 65.6616 | -57.2571 | 65.5975 | -56.781 | -57.3303 | -57.2113 | -48.9853 | 65.7166 | -57.2021 | -56.9824 | -57.0374 | -57.2205 | -56.9275 | -0.10986 | -0.036621 | -0.10071 | 0.36621 | -0.064087 | -0.18311 | 0.045776 | -0.073242 | -0.054931 | 0.018311 | -122.6807 | 0.10986 | 0.21973 | -0.073242 | 0.27466 | -0.018311 | 0.47607 | 122.8546 | 0.16479 | 0.21973 | 122.9187 | 122.9187 | 122.8088 | 122.8638 | -122.9553 | -122.9004 | 122.7448 | 0.16479 | 14.2548 | 8.1619
920.1719 | 123.0835 | -57.1518 | 65.7166 | -0.083466 | 0.00019446 | 0.064375 | 0.063064 | 0.0016556 | -0.00037171 | 8.1188e-05 | -0.019653 | 0.00067495 | 0.0014954 | 0.0013416 | 0.00020289 | -0.0017347 | 0.00023934 | -43.0161 | 65.6799 | -57.2617 | 65.5518 | -56.8268 | -57.3624 | -57.2205 | -49.0906 | 65.7257 | -57.2067 | -57.0053 | -57.0465 | -57.2433 | -56.9366 | -0.10986 | -0.036621 | -0.16479 | 0.32501 | -0.068665 | -0.21057 | 0.041199 | -0.10071 | -0.054932 | 0.009155 | -122.7219 | 0.10529 | 0.21515 | -0.091553 | 0.27008 | -0.036621 | 0.43488 | 122.8134 | 0.16022 | 0.20142 | 122.9416 | 122.9324 | 122.8317 | 122.8775 | -122.9782 | -122.9233 | 122.7036 | 0.14648 | 14.1357 | 8.0612
921.1719 | 123.1064 | -57.1426 | 65.7074 | -0.068207 | 0.00083526 | 0.063307 | 0.06285 | 0.00080117 | 0.00048269 | 0.0020038 | 0.010864 | -0.0010339 | -0.00021357 | -0.0020764 | -0.0023605 | -0.0017347 | -0.0040333 | -43.2083 | 65.6891 | -57.2388 | 65.5884 | -56.8268 | -57.3303 | -57.2205 | -49.1684 | 65.744 | -57.1976 | -57.0465 | -56.9138 | -57.1976 | -56.9824 | -0.096131 | -0.01831 | -0.11902 | 0.31586 | -0.07782 | -0.18768 | 0.018311 | -0.091552 | -0.054932 | 0.036622 | -122.7539 | 0.22888 | 0.16022 | -0.054932 | 0.21515 | 0 | 0.41199 | 122.8271 | 0.28381 | 0.15106 | 122.9279 | 122.9416 | 122.8317 | 122.8867 | -122.9462 | -122.905 | 122.731 | 0.09613 | 13.9343 | 7.9742
922.1719 | 123.1338 | -57.1564 | 65.6799 | -0.075836 | -0.00066014 | 0.064162 | 0.064773 | 0.00037377 | 0.00091009 | 0.00050839 | -0.086792 | -0.00039305 | -0.0012818 | 0.0098864 | -0.00065151 | 0.00018792 | -0.0025379 | -43.2861 | 65.6754 | -57.2662 | 65.5655 | -56.8085 | -57.3303 | -57.225 | -49.1959 | 65.7349 | -57.2067 | -56.9641 | -57.0145 | -57.225 | -56.8909 | -0.10986 | -0.004578 | -0.11444 | 0.3479 | -0.068665 | -0.17395 | 0.041198 | -0.064087 | -0.050354 | 0.054931 | -122.644 | 0.14191 | 0.2655 | -0.068665 | 0.31586 | -0.018311 | 0.45776 | 122.8317 | 0.19226 | 0.24262 | 122.9416 | 122.9416 | 122.8317 | 122.8912 | -122.9462 | -122.8867 | 122.7219 | 0.19226 | 13.8702 | 7.9605
923.1719 | 123.1567 | -57.1518 | 65.6982 | -0.091095 | -0.0013009 | 0.065016 | 0.064559 | -0.00090783 | 0.0017645 | -0.00013241 | -0.03186 | 0.0019567 | 2.8e-08 | 0.0071094 | -0.0023605 | -0.0040845 | -0.0025379 | -43.3868 | 65.6525 | -57.225 | 65.6113 | -56.7947 | -57.3212 | -57.2113 | -49.2508 | 65.712 | -57.1701 | -56.8634 | -56.9824 | -57.2342 | -56.9046 | -0.073243 | -0.045776 | -0.086975 | 0.35706 | -0.05951 | -0.16937 | 0.013733 | -0.09613 | -0.018311 | 0.013733 | -122.5616 | 0.16937 | 0.24719 | -0.082398 | 0.2655 | -0.064087 | 0.4303 | 122.8363 | 0.18768 | 0.3067 | 122.8775 | 122.8821 | 122.8043 | 122.8638 | -122.9233 | -122.8683 | 122.7631 | 0.28839 | 13.765 | 7.901
924.1719 | 123.1338 | -57.1426 | 65.6845 | -0.03006 | -0.00044654 | 0.063734 | 0.0652 | 0.0010148 | -0.00037171 | 0.00072199 | -0.056274 | 0.00088875 | -0.0012818 | 0.0051868 | -0.0017197 | 0.00082892 | 0.0021619 | -43.4875 | 65.7028 | -57.2525 | 65.5746 | -56.8039 | -57.3212 | -57.2159 | -49.3332 | 65.6982 | -57.1747 | -56.9641 | -57.0145 | -57.2067 | -56.8863 | -0.10986 | 0.018311 | -0.10986 | 0.33875 | -0.073242 | -0.17853 | 0.036621 | -0.068665 | -0.032044 | 0.013733 | -122.6486 | 0.12817 | 0.25635 | -0.064087 | 0.28839 | -0.032043 | 0.44861 | 122.8271 | 0.16022 | 0.21057 | 122.9553 | 122.8729 | 122.8455 | 122.8409 | -122.937 | -122.8592 | 122.7173 | 0.17853 | 13.6551 | 7.8094
925.1719 | 123.0789 | -57.1335 | 65.712 | -0.1445 | 0.00062166 | 0.061171 | 0.063918 | -0.00026703 | 0.00091009 | 8.1188e-05 | 0.0047608 | 0.00067495 | -0.001709 | 0.0017688 | -0.0017197 | -0.0013073 | -0.0018971 | -43.5471 | 65.6982 | -57.2525 | 65.5655 | -56.8222 | -57.3532 | -57.2113 | -49.4522 | 65.7349 | -57.1701 | -56.9824 | -57.0282 | -57.2205 | -56.9229 | -0.11902 | -0.013733 | -0.14648 | 0.31128 | -0.07782 | -0.21973 | 0.041198 | -0.10071 | -0.036621 | 0.022888 | -122.6944 | 0.10529 | 0.21057 | -0.086975 | 0.24719 | -0.050354 | 0.4303 | 122.818 | 0.14191 | 0.18768 | 122.9507 | 122.905 | 122.8317 | 122.8683 | -122.9645 | -122.8821 | 122.699 | 0.15106 | 13.5864 | 7.6813
926.1719 | 123.0377 | -57.1976 | 65.7486 | -0.0071715 | 0.0021171 | 0.063948 | 0.065414 | -0.003685 | 0.00069649 | 0.001363 | -0.080688 | 0.00088875 | 0.0012818 | 0.001128 | -0.00022431 | -0.0017347 | 0.00088014 | -43.5928 | 65.7028 | -57.2891 | 65.506 | -56.9183 | -57.4265 | -57.312 | -49.5712 | 65.7486 | -57.2067 | -57.0465 | -57.1106 | -57.3212 | -56.9916 | -0.091553 | -0.045776 | -0.24262 | 0.27924 | -0.11444 | -0.22888 | -0.022888 | -0.13733 | -0.009155 | 0 | -122.7951 | 0.086975 | 0.20599 | -0.1236 | 0.21515 | -0.11444 | 0.37079 | 122.7951 | 0.09613 | 0.16022 | 122.9919 | 122.9553 | 122.9004 | 122.9462 | -123.0377 | -122.9553 | 122.7036 | 0.15106 | 13.6047 | 7.6263
927.1719 | 123.1201 | -57.1335 | 65.6845 | -0.03006 | -0.00087374 | 0.064803 | 0.063064 | -0.0026168 | -0.0022943 | -0.00013241 | -0.034912 | 0.00024775 | -0.00021357 | -0.0033582 | -0.0023605 | -0.0019483 | -0.00082886 | -43.6111 | 65.6845 | -57.225 | 65.6067 | -56.7764 | -57.3212 | -57.1838 | -49.5117 | 65.7257 | -57.1609 | -56.9595 | -57.0145 | -57.193 | -56.8954 | -0.091553 | 0 | -0.07782 | 0.35706 | -0.050354 | -0.18768 | 0.041199 | -0.09613 | -0.027466 | 0.041199 | -122.644 | 0.11902 | 0.23804 | -0.059509 | 0.2655 | -0.032043 | 0.44861 | 122.8317 | 0.14648 | 0.20142 | 122.9095 | 122.8867 | 122.818 | 122.8592 | -122.9095 | -122.8455 | 122.7402 | 0.17395 | 13.5223 | 7.6218
928.1719 | 123.1247 | -57.1609 | 65.6891 | -0.12161 | 0.00040806 | 0.064375 | 0.0652 | 0.00080117 | -0.00058531 | 0.00072199 | -0.053223 | 0.00024775 | 0.00042723 | 0.0017688 | -0.0021469 | -0.00023928 | 0.00023934 | -43.6798 | 65.6708 | -57.2937 | 65.5746 | -56.8176 | -57.3486 | -57.2342 | -49.6124 | 65.7166 | -57.1747 | -56.955 | -57.0236 | -57.2067 | -56.8909 | -0.13275 | -0.018311 | -0.11444 | 0.34332 | -0.073242 | -0.18768 | 0.059509 | -0.054932 | -0.013733 | 0.027466 | -122.644 | 0.13733 | 0.27008 | -0.045776 | 0.28381 | -0.032043 | 0.47607 | 122.8683 | 0.15106 | 0.21973 | 122.9645 | 122.8912 | 122.8317 | 122.8775 | -122.9828 | -122.8638 | 122.7356 | 0.20599 | 13.4811 | 7.5485
929.1719 | 123.0057 | -57.1335 | 65.7761 | -0.022431 | 0.00019446 | 0.063307 | 0.063918 | -0.0038986 | -0.0014399 | -0.00013241 | -0.022705 | 0.0032385 | 0.00042723 | -0.002931 | -0.00086511 | 0.00018792 | 2.554e-05 | -43.7027 | 65.7623 | -57.2342 | 65.538 | -56.8405 | -57.3349 | -57.2433 | -49.7498 | 65.7898 | -57.1793 | -57.0282 | -57.0419 | -57.2617 | -56.9595 | -0.10071 | -0.013733 | -0.23804 | 0.29297 | -0.10986 | -0.20142 | -0.009155 | -0.10071 | -0.045776 | 0.013733 | -122.8043 | 0.091553 | 0.17395 | -0.12817 | 0.21973 | -0.082398 | 0.39368 | 122.7722 | 0.13733 | 0.15106 | 122.9965 | 122.9691 | 122.8958 | 122.9233 | -123.0103 | -122.9553 | 122.6715 | 0.10529 | 13.4308 | 7.3837
930.1719 | 123.0835 | -57.1793 | 65.7028 | -0.083466 | -0.00044654 | 0.064803 | 0.065841 | 0.0016556 | 0.00091009 | 0.0037128 | -0.062378 | 0.00088875 | -0.00085457 | -0.00036738 | 0.00020289 | -0.0019483 | 0.00088014 | -43.7668 | 65.6937 | -57.2708 | 65.5243 | -56.8726 | -57.3944 | -57.2754 | -49.823 | 65.7211 | -57.2021 | -57.0007 | -57.0602 | -57.2433 | -56.9504 | -0.091553 | -0.009155 | -0.17853 | 0.3067 | -0.096131 | -0.21515 | -0.004578 | -0.1236 | -0.022888 | 0.01831 | -122.7036 | 0.11902 | 0.22888 | -0.064087 | 0.25177 | -0.041199 | 0.39825 | 122.7951 | 0.14191 | 0.20142 | 122.9645 | 122.9233 | 122.8729 | 122.9004 | -122.9736 | -122.905 | 122.7036 | 0.17853 | 13.4125 | 7.3563
931.1719 | 123.056 | -57.1564 | 65.7211 | -0.091095 | 0.0012625 | 0.063948 | 0.063918 | -0.00026703 | 5.5488e-05 | -0.00013241 | -0.047119 | 0.0011023 | 0.00021363 | -0.0025036 | 0.00020289 | -0.00088008 | -0.0018971 | -43.8721 | 65.7303 | -57.2708 | 65.5106 | -56.8817 | -57.4127 | -57.2891 | -49.8962 | 65.7486 | -57.2021 | -57.0236 | -57.0831 | -57.28 | -56.9504 | -0.11444 | 0.009156 | -0.21057 | 0.27466 | -0.13275 | -0.25635 | -0.018311 | -0.14191 | -0.045776 | 0.027466 | -122.7448 | 0.073242 | 0.20599 | -0.1236 | 0.25177 | -0.07782 | 0.3891 | 122.7814 | 0.11902 | 0.17853 | 123.0011 | 122.9507 | 122.8867 | 122.905 | -122.9919 | -122.9233 | 122.6669 | 0.13275 | 13.2843 | 7.2601
932.1719 | 123.143 | -57.1472 | 65.7028 | -0.075836 | -0.0010873 | 0.065016 | 0.064345 | -0.004753 | -0.00079891 | 0.001363 | -0.019653 | 0.0011023 | 0.0012818 | 0.0034778 | -0.0027877 | -0.00088008 | 0.00088014 | -43.9087 | 65.6799 | -57.2617 | 65.5518 | -56.8176 | -57.3532 | -57.2296 | -49.8825 | 65.7211 | -57.1793 | -56.955 | -57.0099 | -57.1976 | -56.8634 | -0.11444 | -0.022888 | -0.15106 | 0.32959 | -0.082397 | -0.20599 | 0.032044 | -0.091552 | -0.032043 | 0.01831 | -122.6578 | 0.13733 | 0.28381 | -0.050354 | 0.31586 | -0.018311 | 0.44403 | 122.8134 | 0.16937 | 0.2243 | 122.9416 | 122.9004 | 122.8271 | 122.8683 | -122.9645 | -122.8821 | 122.699 | 0.19226 | 13.2385 | 7.2647
933.1719 | 123.1201 | -57.1152 | 65.7211 | -0.11398 | 0.00083526 | 0.065871 | 0.061568 | -5.343e-05 | 5.5488e-05 | 0.0022174 | 0.016968 | -0.0010339 | -0.00021357 | 0.0075366 | -0.0019333 | -0.00088008 | 0.0019483 | -43.9224 | 65.6799 | -57.2433 | 65.5975 | -56.7719 | -57.3029 | -57.1747 | -49.9237 | 65.7166 | -57.1609 | -57.0877 | -57.019 | -57.0419 | -56.7169 | -0.12817 | -0.041198 | -0.1236 | 0.34332 | -0.05951 | -0.18768 | 0.068664 | -0.059509 | -0.045777 | -0.004577 | -122.8088 | 0.09613 | 0.39825 | 0.073242 | 0.44403 | 0.11902 | 0.4715 | 122.8409 | 0.14191 | 0.073242 | 122.9233 | 122.8775 | 122.7951 | 122.8317 | -122.9645 | -122.8821 | 122.7127 | 0.027465 | 13.1927 | 7.1915
934.1719 | 123.1018 | -57.1381 | 65.7303 | -0.0071715 | 0.00083526 | 0.06288 | 0.064986 | 0.0022964 | -0.00015811 | 0.00050839 | 0.016968 | 0.00024775 | 0.001068 | -0.0059216 | -0.0012925 | -0.00023928 | 0.00088014 | -43.9728 | 65.6799 | -57.225 | 65.5975 | -56.7673 | -57.2983 | -57.1884 | -49.9741 | 65.7028 | -57.1884 | -56.9504 | -56.9962 | -57.1838 | -56.8863 | -0.086975 | -0.050354 | -0.13275 | 0.37079 | -0.050354 | -0.16022 | 0.036621 | -0.073242 | -0.050354 | -0.027466 | -122.6807 | 0.14191 | 0.25177 | -0.045776 | 0.30212 | 0.004578 | 0.45776 | 122.8226 | 0.19226 | 0.23804 | 122.905 | 122.8912 | 122.818 | 122.8409 | -122.9553 | -122.9187 | 122.7356 | 0.18768 | 13.1653 | 7.164
935.1719 | 123.0927 | -57.1335 | 65.712 | -0.12924 | -0.00023294 | 0.063307 | 0.065627 | -0.0030442 | 0.0011237 | -0.00034601 | -0.0013428 | 0.0015295 | 0.00042723 | -0.00464 | -1.0706e-05 | -0.00045288 | -0.0016833 | -44.0689 | 65.6799 | -57.2296 | 65.593 | -56.7581 | -57.3029 | -57.1884 | -50.0793 | 65.7349 | -57.1564 | -57.0007 | -57.0465 | -57.2021 | -56.9092 | -0.09613 | -0.032043 | -0.11902 | 0.37537 | -0.054932 | -0.16937 | 0.041198 | -0.073242 | -0.022888 | 0.022888 | -122.7127 | 0.086975 | 0.2243 | -0.068664 | 0.24719 | -0.045776 | 0.4715 | 122.8226 | 0.10986 | 0.15564 | 122.9095 | 122.8912 | 122.8134 | 122.8683 | -122.9416 | -122.8683 | 122.7264 | 0.13275 | 13.0646 | 7.0541
936.1719 | 123.0423 | -57.1564 | 65.744 | -0.083466 | 0.0027579 | 0.067366 | 0.066482 | -0.0026168 | -0.00058531 | 0.0020038 | -0.062378 | 0.0019567 | -0.00042717 | -0.0035718 | -0.0015061 | -0.0013073 | 0.00045294 | -44.2108 | 65.7166 | -57.2662 | 65.4922 | -56.9138 | -57.4173 | -57.2983 | -50.1892 | 65.7669 | -57.225 | -57.1014 | -57.074 | -57.2617 | -56.9687 | -0.10986 | -0.027466 | -0.25177 | 0.24262 | -0.14191 | -0.26093 | -0.032044 | -0.15106 | -0.068665 | 0.022888 | -122.8455 | 0.082397 | 0.18768 | -0.10529 | 0.25635 | -0.036621 | 0.35248 | 122.7585 | 0.15106 | 0.1236 | 122.9828 | 122.9919 | 122.8729 | 122.9233 | -123.0103 | -122.9691 | 122.6486 | 0.054932 | 12.9456 | 6.9672
937.1719 | 123.1155 | -57.1701 | 65.7806 | -0.098725 | -0.0017281 | 0.063948 | 0.0652 | 0.00080117 | 0.00048269 | -0.0014142 | -0.06543 | 0.0023839 | 0.00021363 | -0.00036738 | -0.00022431 | -0.00023928 | -0.00061526 | -44.2657 | 65.7303 | -57.2617 | 65.4968 | -56.9275 | -57.4356 | -57.3303 | -50.3586 | 65.7806 | -57.2113 | -56.9046 | -57.4356 | -57.5043 | -56.9321 | -0.091553 | -0.050354 | -0.28381 | 0.24262 | -0.16022 | -0.2655 | -0.068664 | -0.17395 | -0.041199 | 0 | -122.6852 | -0.2655 | 0.23804 | -0.33417 | 0.27924 | -0.29297 | 0.33417 | 122.7585 | -0.2243 | 0.3067 | 122.9919 | 122.9919 | 122.9004 | 122.9507 | -123.0423 | -122.9919 | 122.6669 | 0.2655 | 12.9044 | 6.8115
938.1719 | 123.024 | -57.1747 | 65.7349 | -0.068207 | 0.00062166 | 0.062666 | 0.066695 | -0.00090783 | -0.00015811 | 0.0017902 | -0.068481 | 0.00067495 | 0.0019226 | 0.0036914 | -0.0017197 | -0.0021619 | 0.0021619 | -44.3298 | 65.7166 | -57.2479 | 65.4922 | -56.8954 | -57.4127 | -57.2983 | -50.4547 | 65.7669 | -57.2205 | -57.0236 | -57.1243 | -57.3257 | -56.9733 | -0.073242 | -0.01831 | -0.24261 | 0.27924 | -0.1236 | -0.23804 | -0.050354 | -0.16479 | -0.045776 | 0.032044 | -122.7585 | 0.050354 | 0.20142 | -0.15106 | 0.24719 | -0.10529 | 0.35248 | 122.7402 | 0.09613 | 0.19684 | 122.9645 | 122.9874 | 122.8912 | 122.9416 | -122.9828 | -122.9553 | 122.6669 | 0.15106 | 12.8448 | 6.72
939.1719 | 123.0423 | -57.1609 | 65.7303 | -0.052948 | -0.00023294 | 0.065443 | 0.065841 | 0.0010148 | 0.0013373 | 8.1188e-05 | -0.03186 | -0.00039305 | -0.0012818 | -0.00079478 | 0.00041649 | -2.5678e-05 | 0.0025891 | -44.6732 | 65.6754 | -57.3029 | 65.538 | -56.8176 | -57.4127 | -57.2662 | -50.4684 | 65.7852 | -57.1838 | -57.0328 | -57.0602 | -57.2937 | -56.9595 | -0.14191 | -0.054932 | -0.19226 | 0.34332 | -0.10529 | -0.25177 | 0.036621 | -0.10986 | -0.022888 | 0.054931 | -122.7631 | 0.10071 | 0.20142 | -0.13275 | 0.2243 | -0.10986 | 0.48523 | 122.8409 | 0.1236 | 0.15106 | 122.9782 | 122.9691 | 122.8363 | 122.9462 | -123.0331 | -122.9141 | 122.699 | 0.12817 | 12.4878 | 6.6925
940.1719 | 123.1201 | -57.1518 | 65.7394 | -0.068207 | -0.00023294 | 0.063948 | 0.064559 | 0.00037377 | -0.0016535 | 0.0015766 | -0.016602 | 0.0021703 | 0.0019226 | 0.0047594 | -0.00043791 | -0.0025891 | 0.00023934 | -44.4626 | 65.7303 | -57.2296 | 65.5197 | -56.8451 | -57.3807 | -57.2571 | -50.4868 | 65.7486 | -57.193 | -56.987 | -57.0511 | -57.2433 | -56.9183 | -0.07782 | -0.009155 | -0.21973 | 0.3067 | -0.10529 | -0.22888 | -0.027466 | -0.15106 | -0.041199 | 0.009155 | -122.7264 | 0.10071 | 0.23346 | -0.091553 | 0.27466 | -0.050354 | 0.38452 | 122.7493 | 0.14191 | 0.20599 | 122.9599 | 122.9416 | 122.8821 | 122.9004 | -122.9691 | -122.9324 | 122.6715 | 0.16479 | 12.6892 | 6.665
941.1719 | 123.111 | -57.1106 | 65.7257 | -0.091095 | -0.0010873 | 0.064589 | 0.062636 | -0.0043258 | -0.00079891 | 0.00050839 | 0.0078126 | 0.00067495 | 0.00064083 | -0.0052808 | -0.0017197 | -0.00066648 | 0.0013073 | -44.5129 | 65.7074 | -57.2113 | 65.593 | -56.749 | -57.2891 | -57.1655 | -50.4913 | 65.7257 | -57.1518 | -56.9229 | -56.9916 | -57.1838 | -56.8451 | -0.10071 | -0.018311 | -0.13275 | 0.36163 | -0.054931 | -0.17853 | 0.045777 | -0.07782 | -0.041198 | 0 | -122.6486 | 0.11902 | 0.2655 | -0.073242 | 0.3067 | -0.032044 | 0.46234 | 122.8043 | 0.16022 | 0.22888 | 122.9187 | 122.8775 | 122.818 | 122.8363 | -122.937 | -122.8775 | 122.7036 | 0.18768 | 12.5977 | 6.6193
942.1719 | 123.024 | -57.1655 | 65.7806 | -0.037689 | 0.00062166 | 0.064589 | 0.066054 | 0.0020828 | 0.0015509 | -0.00055961 | -0.06543 | 0.0017431 | 0.00064083 | 0.001128 | 0.0012711 | -0.0010937 | 0.0023755 | -44.6365 | 65.7715 | -57.2479 | 65.538 | -56.8405 | -57.3669 | -57.2708 | -50.6836 | 65.8035 | -57.1609 | -57.0328 | -57.1243 | -57.2937 | -56.9641 | -0.082398 | -0.009156 | -0.24262 | 0.32501 | -0.10529 | -0.20142 | -0.022888 | -0.11902 | 0.004577 | 0.022888 | -122.8134 | 0.041198 | 0.20142 | -0.12817 | 0.19684 | -0.13275 | 0.40741 | 122.786 | 0.036621 | 0.12817 | 123.0194 | 122.9645 | 122.937 | 122.9691 | -123.0286 | -122.9416 | 122.7036 | 0.13275 | 12.529 | 6.4819
943.1719 | 122.9919 | -57.1518 | 65.7806 | -0.13687 | 0.00062166 | 0.063734 | 0.066268 | -0.0011214 | 0.0019781 | -0.00098701 | -0.01355 | 0.0028113 | 0.0012818 | 0.0049732 | 0.0019119 | 0.0018969 | -0.0016833 | -44.7739 | 65.7394 | -57.2708 | 65.4831 | -56.9138 | -57.4219 | -57.2708 | -50.766 | 65.7761 | -57.1976 | -56.9962 | -56.8359 | -57.2983 | -57.0236 | -0.11902 | -0.041199 | -0.29755 | 0.23804 | -0.11902 | -0.27008 | 0 | -0.15106 | -0.045777 | -0.004578 | -122.7768 | 0.31586 | 0.12817 | -0.14648 | 0.17395 | -0.10071 | 0.35706 | 122.7539 | 0.36163 | 0.20142 | 123.0103 | 122.9736 | 122.8912 | 122.9279 | -123.0515 | -122.9782 | 122.6349 | 0.15564 | 12.3779 | 6.3858
944.1719 | 123.0606 | -57.1655 | 65.7486 | 0.00045798 | -0.0017281 | 0.063094 | 0.066695 | 0.00251 | 0.00026909 | 0.0026446 | -0.0013428 | 0.0021703 | 0.001068 | -0.0014356 | 0.00063009 | -0.0010937 | -0.0040333 | -44.8975 | 65.7806 | -57.2067 | 65.5106 | -56.8542 | -57.399 | -57.2571 | -50.7889 | 65.7669 | -57.1884 | -57.019 | -57.1014 | -57.2754 | -56.9641 | -0.041199 | 0.032044 | -0.23804 | 0.31128 | -0.091553 | -0.23346 | -0.050354 | -0.19226 | -0.022889 | 0.018311 | -122.7676 | 0.064087 | 0.20142 | -0.10986 | 0.2243 | -0.086975 | 0.35248 | 122.7173 | 0.086976 | 0.16937 | 122.9874 | 122.9553 | 122.9462 | 122.9324 | -122.9553 | -122.937 | 122.6761 | 0.14648 | 12.2681 | 6.3766
945.1719 | 123.0698 | -57.1335 | 65.7623 | -0.10635 | 0.00083526 | 0.064375 | 0.063064 | 0.0022964 | 0.0021917 | -0.00034601 | 0.026123 | 0.0011023 | 0.0019226 | -0.0052808 | 0.0021255 | -0.0034437 | -0.0021107 | -45.0394 | 65.7257 | -57.2067 | 65.5746 | -56.7535 | -57.2983 | -57.1609 | -50.7889 | 65.7394 | -57.1518 | -56.9595 | -56.9962 | -57.1884 | -56.9138 | -0.073242 | -0.036621 | -0.18768 | 0.37994 | -0.027466 | -0.16479 | 0.045776 | -0.091553 | -0.01831 | -0.022888 | -122.7219 | 0.13733 | 0.21973 | -0.054932 | 0.23804 | -0.036622 | 0.45319 | 122.7814 | 0.15564 | 0.19226 | 122.9324 | 122.8912 | 122.8592 | 122.8729 | -122.9691 | -122.9141 | 122.7081 | 0.17395 | 12.0941 | 6.3446
946.1719 | 123.0423 | -57.1655 | 65.7623 | -0.068207 | 0.00083526 | 0.06288 | 0.066268 | -0.00048063 | -0.0016535 | 0.0028582 | -0.01355 | -0.0010339 | -0.0010682 | 0.002196 | -0.0012925 | -0.0013073 | 0.0023755 | -45.2179 | 65.7303 | -57.2845 | 65.4602 | -56.8817 | -57.3029 | -57.225 | -50.9491 | 65.7761 | -57.1793 | -57.0145 | -57.0923 | -57.2845 | -56.955 | -0.11902 | -0.032043 | -0.30212 | 0.28381 | -0.05951 | -0.13733 | 0.059509 | -0.01831 | -0.013733 | 0.013733 | -122.7768 | 0.073242 | 0.21057 | -0.11902 | 0.2243 | -0.10529 | 0.40283 | 122.7448 | 0.086975 | 0.16479 | 123.0148 | 122.9553 | 122.8958 | 122.9416 | -123.0469 | -122.9416 | 122.6257 | 0.15106 | 11.9476 | 6.2164
947.1719 | 123.0606 | -57.1564 | 65.7623 | -0.075836 | 0.0010489 | 0.063307 | 0.064559 | -0.0011214 | 5.5488e-05 | 0.00072199 | 0.062744 | 0.0028113 | 2.8e-08 | -0.00015378 | -0.0012925 | 0.00040152 | 0.0023755 | -45.2545 | 65.7349 | -57.2617 | 65.5701 | -57.1198 | -57.6828 | -57.0923 | -51.091 | 65.7898 | -57.1747 | -57.0328 | -57.1014 | -57.2845 | -56.9504 | -0.10529 | -0.027466 | -0.19226 | 0.036621 | 0.064087 | -0.52643 | 0.16937 | -0.42114 | -0.018311 | 0.027466 | -122.7951 | 0.054932 | 0.20599 | -0.12817 | 0.22431 | -0.10986 | 0.14191 | 122.8317 | 0.073243 | 0.14191 | 122.9965 | 122.9645 | 122.8912 | 122.9462 | -123.024 | -122.937 | 122.7264 | 0.1236 | 11.9019 | 6.0654
948.1719 | 123.111 | -57.0831 | 65.7806 | -0.0071715 | 0.0012625 | 0.065657 | 0.062209 | 0.00058737 | -0.0016535 | -0.0029096 | 0.068848 | -0.0016749 | -0.00085457 | 0.001128 | -0.00043791 | -0.0040845 | 0.0040845 | -45.2271 | 65.7532 | -57.193 | 65.6754 | -56.6574 | -57.2067 | -57.0786 | -50.9125 | 65.7852 | -57.1243 | -56.9138 | -56.9458 | -57.1106 | -56.8359 | -0.10986 | -0.027466 | -0.10529 | 0.42572 | 0.004578 | -0.1236 | 0.11444 | -0.013733 | -0.041199 | 0.004577 | -122.6944 | 0.13733 | 0.24719 | -0.027466 | 0.28839 | 0.013733 | 0.53558 | 122.8683 | 0.17853 | 0.21057 | 122.9462 | 122.9095 | 122.8363 | 122.8683 | -122.9736 | -122.905 | 122.7585 | 0.16937 | 11.8561 | 6.1707
949.1719 | 123.1338 | -57.1381 | 65.7532 | -0.1445 | -0.00044654 | 0.065016 | 0.0652 | 0.004219 | -0.0010125 | 0.00093559 | -0.016602 | 0.0019567 | -0.00021357 | 0.0015552 | -0.0012925 | -0.00066648 | -0.0014697 | -45.3461 | 65.7303 | -57.2388 | 65.5746 | -56.7535 | -57.312 | -57.1838 | -51.0635 | 65.744 | -57.1747 | -56.9366 | -57.0099 | -57.2021 | -56.8588 | -0.10071 | -0.022888 | -0.17853 | 0.38452 | -0.045776 | -0.17395 | 0.054932 | -0.073242 | -0.036621 | -0.009155 | -122.6898 | 0.12817 | 0.27924 | -0.064086 | 0.31586 | -0.027465 | 0.48523 | 122.8134 | 0.1648 | 0.23804 | 122.9691 | 122.9187 | 122.8683 | 122.8821 | -122.9919 | -122.9279 | 122.7127 | 0.20142 | 11.792 | 6.0745
950.1719 | 123.056 | -57.1564 | 65.7578 | -0.15976 | -1.9142e-05 | 0.062453 | 0.064559 | 0.003151 | 5.5488e-05 | 0.002431 | -0.028809 | 0.0015295 | 0.0023498 | 0.0026232 | -1.0706e-05 | -0.0040845 | 0.0013073 | -45.3918 | 65.7486 | -57.2342 | 65.5197 | -56.8176 | -57.3898 | -57.2433 | -51.2054 | 65.7944 | -57.1793 | -57.0099 | -57.0923 | -57.2983 | -56.9778 | -0.07782 | -0.009155 | -0.23804 | 0.33874 | -0.086975 | -0.23346 | -0.009155 | -0.15564 | -0.022888 | 0.036622 | -122.7676 | 0.064087 | 0.17853 | -0.14191 | 0.20142 | -0.11902 | 0.41656 | 122.7539 | 0.086975 | 0.16937 | 122.9828 | 122.9736 | 122.905 | 122.9507 | -122.9919 | -122.937 | 122.6761 | 0.14648 | 11.7645 | 5.9509
951.1719 | 123.0286 | -57.1243 | 65.7623 | -0.39627 | 0.0031851 | 0.06053 | 0.0652 | -0.00048063 | 0.0011237 | -0.00055961 | -0.028809 | 0.0019567 | 0.00042723 | -0.0048536 | 0.00041649 | -2.5678e-05 | -0.00018806 | -45.3186 | 65.7303 | -57.2388 | 65.5106 | -56.813 | -57.3807 | -57.2525 | -51.2878 | 65.7944 | -57.1609 | -57.0145 | -57.0969 | -57.3029 | -56.955 | -0.11444 | -0.032043 | -0.25177 | 0.31128 | -0.12817 | -0.25635 | -0.013732 | -0.14191 | -0.036621 | 0.032044 | -122.7768 | 0.027466 | 0.16937 | -0.17853 | 0.20599 | -0.14191 | 0.42572 | 122.7493 | 0.064087 | 0.14648 | 122.9691 | 122.9553 | 122.8546 | 122.9187 | -123.0011 | -122.9233 | 122.6349 | 0.10986 | 11.8057 | 5.8365
952.1719 | 123.1338 | -57.1335 | 65.7074 | -0.083466 | 0.00019446 | 0.065871 | 0.066054 | 0.0016556 | 0.00026909 | 0.003072 | 0.001709 | 0.0023839 | -0.00085457 | -0.0010084 | -0.00022431 | 0.00082892 | 0.00023934 | -45.5475 | 65.7486 | -57.2617 | 65.538 | -56.7947 | -57.3532 | -57.2205 | -51.3016 | 65.7578 | -57.1747 | -56.9687 | -57.019 | -57.2113 | -56.8863 | -0.12817 | 0.041199 | -0.16937 | 0.33875 | -0.086975 | -0.21973 | 0.041199 | -0.091552 | -0.041199 | 0.050354 | -122.6761 | 0.11444 | 0.24719 | -0.07782 | 0.28839 | -0.036621 | 0.46692 | 122.7997 | 0.15564 | 0.20599 | 123.0103 | 122.9324 | 122.8821 | 122.8912 | -122.9691 | -122.8821 | 122.6715 | 0.1648 | 11.586 | 5.8319
953.1719 | 123.0698 | -57.1289 | 65.7532 | -0.075836 | 0.00040806 | 0.063521 | 0.060714 | -0.0024032 | -0.0010125 | 0.0028582 | 0.056641 | 0.0023839 | 0.00021363 | -0.0052808 | -1.0706e-05 | -0.0036573 | -0.00061526 | -45.5154 | 65.712 | -57.1747 | 65.5838 | -56.7398 | -57.2754 | -57.1609 | -51.3519 | 65.7578 | -57.1609 | -56.9687 | -56.9366 | -57.0602 | -56.8039 | -0.045777 | -0.041199 | -0.16937 | 0.3891 | -0.032044 | -0.14648 | 0.013733 | -0.10071 | -0.032044 | 0.004577 | -122.7219 | 0.19226 | 0.32501 | 0.068664 | 0.35706 | 0.10071 | 0.43488 | 122.7585 | 0.2243 | 0.19226 | 122.8867 | 122.9187 | 122.8409 | 122.8867 | -122.9279 | -122.9141 | 122.7127 | 0.16022 | 11.6135 | 5.777
954.1719 | 123.1522 | -57.1243 | 65.7028 | -0.083466 | 0.0014761 | 0.063094 | 0.064559 | 0.0018692 | -0.00037171 | 0.0022174 | 0.016968 | -0.00082025 | -0.00021357 | 0.0096728 | -0.00043791 | 0.0010425 | -0.0033923 | -45.5246 | 65.712 | -57.2205 | 65.6204 | -56.7032 | -57.2845 | -57.1472 | -51.3702 | 65.7166 | -57.1564 | -56.9275 | -56.9641 | -57.1747 | -56.8817 | -0.09613 | 0.009155 | -0.082398 | 0.42114 | -0.022888 | -0.16022 | 0.073242 | -0.064087 | -0.032043 | 0.013733 | -122.6303 | 0.16022 | 0.24262 | -0.050354 | 0.27466 | -0.018311 | 0.51727 | 122.8409 | 0.19226 | 0.22888 | 122.9324 | 122.8729 | 122.8363 | 122.8409 | -122.9233 | -122.8592 | 122.7448 | 0.19684 | 11.5997 | 5.7541
955.1719 | 123.143 | -57.0969 | 65.7257 | -0.15976 | -0.0017281 | 0.065016 | 0.064773 | -0.00026703 | 0.0015509 | -0.0018414 | 0.03833 | -0.00060665 | 2.8e-08 | -0.0033582 | -0.0023605 | -0.0013073 | -0.0016833 | -45.6161 | 65.6937 | -57.2113 | 65.6937 | -56.5247 | -57.2983 | -57.1289 | -51.4206 | 65.744 | -57.1426 | -56.9321 | -56.9687 | -57.1655 | -56.8634 | -0.11444 | -0.032043 | -0.032043 | 0.5722 | -0.032043 | -0.20142 | 0.082398 | -0.086975 | -0.045776 | 0.018311 | -122.6578 | 0.12817 | 0.23346 | -0.068664 | 0.27924 | -0.022888 | 0.68665 | 122.905 | 0.17395 | 0.21057 | 122.905 | 122.8867 | 122.7905 | 122.8409 | -122.937 | -122.8683 | 122.7905 | 0.16479 | 11.4807 | 5.6763
956.1719 | 123.0148 | -57.1426 | 65.7715 | -0.083466 | 0.0016899 | 0.063094 | 0.0652 | -0.0017624 | 0.00048269 | 0.0039264 | -0.053223 | 0.00088875 | 2.8e-08 | -0.001222 | -0.00086511 | -0.0017347 | -0.00040166 | -45.7901 | 65.7349 | -57.2571 | 65.5197 | -56.8359 | -57.4036 | -57.2433 | -51.5488 | 65.7669 | -57.2113 | -57.0648 | -57.0465 | -57.2754 | -56.955 | -0.11444 | -0.036621 | -0.25177 | 0.3067 | -0.10071 | -0.26093 | 0.013733 | -0.14648 | -0.068665 | -0.004577 | -122.8363 | 0.09613 | 0.18768 | -0.13275 | 0.25635 | -0.064087 | 0.42114 | 122.7768 | 0.16479 | 0.14648 | 122.9919 | 122.9782 | 122.8775 | 122.9095 | -123.0286 | -122.9828 | 122.6624 | 0.07782 | 11.3525 | 5.5939
957.1719 | 123.0743 | -57.1564 | 65.7486 | -0.075836 | 0.0025443 | 0.064375 | 0.064986 | 0.00016017 | 0.00069649 | -0.00055961 | -0.01355 | 0.0013159 | 2.8e-08 | -0.00058098 | -0.00065151 | -0.0013073 | 0.0021619 | -45.8588 | 65.7578 | -57.2342 | 65.5334 | -56.7856 | -57.3669 | -57.2205 | -51.6907 | 65.7944 | -57.1838 | -57.0007 | -57.074 | -57.2617 | -56.9412 | -0.07782 | 0.009155 | -0.21515 | 0.37079 | -0.064087 | -0.21057 | 0.013733 | -0.13275 | -0.027466 | 0.045777 | -122.7493 | 0.082397 | 0.21515 | -0.10529 | 0.24262 | -0.07782 | 0.44861 | 122.7676 | 0.10986 | 0.18311 | 122.9919 | 122.9782 | 122.9141 | 122.9507 | -122.9828 | -122.9324 | 122.6898 | 0.15564 | 11.2976 | 5.4657
958.1719 | 123.1018 | -57.1289 | 65.7532 | -0.075836 | 0.0023307 | 0.062025 | 0.06285 | -0.0032578 | 0.0013373 | -0.002055 | 0.081055 | -0.00039305 | -0.00064077 | -0.007417 | 0.00020289 | -0.0028027 | 0.0040845 | -45.8908 | 65.7349 | -57.1976 | 65.6616 | -56.6025 | -57.2983 | -57.1701 | -51.6953 | 65.7532 | -57.1564 | -56.955 | -56.9962 | -57.1793 | -56.9 | -0.068665 | -0.018311 | -0.091553 | 0.52643 | -0.041199 | -0.16937 | 0.027466 | -0.10071 | -0.027466 | 0 | -122.7081 | 0.13275 | 0.22888 | -0.050354 | 0.25635 | -0.022888 | 0.59509 | 122.8592 | 0.16022 | 0.20142 | 122.9324 | 122.9095 | 122.8638 | 122.8821 | -122.9507 | -122.9095 | 122.7905 | 0.17395 | 11.2381 | 5.4337
959.1719 | 123.056 | -57.1426 | 65.7303 | -0.13687 | 0.0019035 | 0.06288 | 0.065841 | 0.0040054 | 5.5488e-05 | -0.00055961 | -0.041016 | 0.0019567 | 0.0023498 | 0.001128 | -0.0019333 | -0.00023928 | 2.554e-05 | -46.0144 | 65.7623 | -57.2571 | 65.506 | -56.7856 | -57.3624 | -57.2296 | -51.8143 | 65.8081 | -57.1884 | -57.0053 | -57.0877 | -57.2891 | -56.9504 | -0.11444 | 0.032043 | -0.22431 | 0.35706 | -0.086975 | -0.21973 | 0.027466 | -0.10529 | -0.045777 | 0.077819 | -122.7356 | 0.054931 | 0.19226 | -0.14648 | 0.23804 | -0.10071 | 0.4715 | 122.7631 | 0.10071 | 0.18311 | 123.0194 | 122.9965 | 122.905 | 122.9507 | -122.9874 | -122.9187 | 122.6486 | 0.13733 | 11.1282 | 5.3284
960.1719 | 123.1018 | -57.1106 | 65.7257 | -0.083466 | -0.0010873 | 0.063734 | 0.065414 | -0.00090783 | 0.00091009 | -0.00034601 | -0.03186 | 0.0013159 | 0.00021363 | -0.0010084 | 0.00063009 | -0.0010937 | -0.0051013 | -46.1472 | 65.7028 | -57.2388 | 65.5518 | -56.7352 | -57.3395 | -57.1793 | -51.8188 | 65.744 | -57.1747 | -56.955 | -56.9962 | -57.2159 | -56.8909 | -0.12817 | -0.022888 | -0.17395 | 0.37537 | -0.068664 | -0.22888 | 0.05951 | -0.10071 | -0.064087 | 0.018311 | -122.6807 | 0.11444 | 0.21973 | -0.10529 | 0.28381 | -0.041198 | 0.50354 | 122.7905 | 0.17853 | 0.21973 | 122.9416 | 122.9187 | 122.8134 | 122.8546 | -122.9645 | -122.9004 | 122.6624 | 0.15564 | 10.9634 | 5.2917
961.1719 | 123.0286 | -57.1747 | 65.744 | -0.068207 | 0.0010489 | 0.066512 | 0.066695 | -0.00026703 | -0.0014399 | 0.0022174 | -0.041016 | 0.0019567 | 0.00064083 | 0.0017688 | -0.0010787 | -0.00023928 | -0.0016833 | -46.5134 | 65.6937 | -57.2937 | 65.5609 | -56.7444 | -57.4036 | -57.2159 | -51.9882 | 65.8081 | -57.193 | -57.0145 | -57.0786 | -57.2983 | -56.9641 | -0.11902 | -0.050354 | -0.18311 | 0.4303 | -0.041198 | -0.22888 | 0.07782 | -0.10986 | -0.01831 | 0.064086 | -122.7585 | 0.096131 | 0.21057 | -0.1236 | 0.22888 | -0.10529 | 0.54932 | 122.8546 | 0.11444 | 0.17853 | 122.9874 | 123.0011 | 122.8683 | 122.9828 | -123.0377 | -122.937 | 122.7356 | 0.16022 | 10.6613 | 5.1865
962.1719 | 123.0927 | -57.1381 | 65.744 | -0.10635 | -1.9142e-05 | 0.065871 | 0.064559 | 0.0022964 | 0.0034735 | 0.0022174 | -0.01355 | 0.0019567 | 0.0023498 | -0.003999 | 0.00063009 | -0.00066648 | 0.00023934 | -46.3898 | 65.744 | -57.2433 | 65.5334 | -56.749 | -57.3486 | -57.2021 | -51.9974 | 65.744 | -57.1793 | -56.9687 | -57.0374 | -57.2021 | -56.9138 | -0.10529 | 0 | -0.21057 | 0.3891 | -0.064086 | -0.21057 | 0.041199 | -0.10529 | -0.041198 | 0 | -122.7127 | 0.10071 | 0.22431 | -0.064086 | 0.2655 | -0.022888 | 0.49439 | 122.7768 | 0.14191 | 0.21057 | 122.9874 | 122.9233 | 122.8821 | 122.8821 | -122.9874 | -122.9233 | 122.6715 | 0.16937 | 10.7483 | 5.1407
963.1719 | 123.1064 | -57.0877 | 65.7578 | -0.0071715 | 0.0012625 | 0.064162 | 0.063064 | -0.0017624 | -0.00058531 | 8.1188e-05 | 0.03833 | -0.0010339 | 0.0014954 | -0.007417 | -0.0032151 | -0.0053663 | 0.0025891 | -46.376 | 65.7394 | -57.1701 | 65.6982 | -56.5384 | -57.1747 | -57.0419 | -51.8967 | 65.7623 | -57.1152 | -56.9321 | -57.1884 | -57.1198 | -56.7627 | -0.082397 | -0.01831 | -0.059509 | 0.54932 | 0.045777 | -0.086975 | 0.12817 | -0.004578 | -0.027465 | 0.004578 | -122.6898 | -0.10071 | 0.32501 | -0.032043 | 0.35248 | -0.004578 | 0.63171 | 122.8683 | -0.073243 | 0.1831 | 122.9095 | 122.8775 | 122.8271 | 122.85 | -122.9279 | -122.8729 | 122.7859 | 0.15564 | 10.7117 | 5.191
964.1719 | 123.0103 | -57.1335 | 65.7715 | -0.060578 | 0.00040806 | 0.062025 | 0.066482 | -0.0013352 | -0.00037171 | 8.1188e-05 | -0.20581 | 0.0030249 | 0.00085443 | 0.0032642 | -0.00022431 | -0.0013073 | -0.0014697 | -46.6095 | 65.7669 | -57.2388 | 65.4968 | -56.7947 | -57.3853 | -57.2159 | -52.2629 | 65.7028 | -57.2205 | -56.9962 | -57.1289 | -57.2937 | -56.955 | -0.10529 | -0.004577 | -0.27466 | 0.33875 | -0.082397 | -0.25177 | 0.022889 | -0.14648 | -0.086975 | -0.068664 | -122.7676 | 0.004578 | 0.17853 | -0.16022 | 0.2655 | -0.073242 | 0.44403 | 122.7356 | 0.091553 | 0.2243 | 123.0057 | 122.9233 | 122.9004 | 122.8363 | -123.0103 | -122.9919 | 122.6303 | 0.13733 | 10.524 | 4.8706
965.1719 | 123.1384 | -57.1472 | 65.7394 | -0.091095 | -1.9142e-05 | 0.065443 | 0.064559 | -0.0024032 | -0.00079891 | 0.0015766 | 0.026123 | -0.00060665 | 0.00042723 | -0.0025036 | -0.00086511 | -0.0010937 | -0.0014697 | -46.6232 | 65.7074 | -57.2067 | 65.6158 | -56.6437 | -57.2662 | -57.2662 | -51.9333 | 65.7211 | -57.1335 | -56.9046 | -56.9778 | -57.1747 | -56.8726 | -0.059509 | -0.032044 | -0.1236 | 0.50354 | -0.11902 | -0.11902 | -0.059509 | -0.059509 | 0.013733 | -0.018311 | -122.644 | 0.16937 | 0.27466 | -0.027466 | 0.26093 | -0.041199 | 0.56305 | 122.8226 | 0.15564 | 0.22888 | 122.9141 | 122.8546 | 122.8546 | 122.8683 | -122.9462 | -122.8729 | 122.7631 | 0.24262 | 10.524 | 5.2139
966.1719 | 123.0698 | -57.1564 | 65.7074 | -0.13687 | -0.00023294 | 0.062453 | 0.063705 | 0.00058737 | 0.0011237 | 0.00050839 | 0.013916 | 0.0017431 | -0.00042717 | -0.00015378 | -0.00065151 | -0.00088008 | 0.0025891 | -46.7239 | 65.6891 | -57.1976 | 65.6113 | -56.6391 | -57.2617 | -57.1014 | -52.1439 | 65.7349 | -57.1518 | -56.9275 | -56.9962 | -57.1838 | -56.8863 | -0.041199 | -0.01831 | -0.09613 | 0.51727 | 0.054932 | -0.10529 | 0.096131 | -0.064087 | 0.004578 | 0.027466 | -122.6349 | 0.16022 | 0.27008 | -0.027466 | 0.2655 | -0.032044 | 0.55847 | 122.8088 | 0.15564 | 0.2243 | 122.8867 | 122.8867 | 122.8455 | 122.8912 | -122.905 | -122.8592 | 122.7676 | 0.22888 | 10.4324 | 5.0125
967.1719 | 123.0331 | -57.1472 | 65.7578 | 0.1149 | -0.0013009 | 0.061385 | 0.065841 | -0.0030442 | -0.00058531 | 0.001363 | -0.047119 | 0.0015295 | 0.00085443 | 0.0045458 | -0.0012925 | -0.0013073 | 0.0023755 | -46.8979 | 65.7349 | -57.2571 | 65.5197 | -56.7719 | -57.3898 | -57.2205 | -52.3636 | 65.7394 | -57.2159 | -57.0099 | -57.106 | -57.3029 | -56.9733 | -0.10986 | -0.022888 | -0.23804 | 0.37537 | -0.073242 | -0.24262 | 0.036621 | -0.13275 | -0.068664 | -0.01831 | -122.7676 | 0.041199 | 0.17395 | -0.15564 | 0.24261 | -0.086975 | 0.48523 | 122.7768 | 0.10986 | 0.20599 | 122.9919 | 122.9553 | 122.8821 | 122.8867 | -123.0148 | -122.9736 | 122.6669 | 0.13733 | 10.2493 | 4.7836
968.1719 | 123.0743 | -57.1289 | 65.7486 | -0.10635 | -0.00023294 | 0.061598 | 0.061996 | -0.0015488 | 5.5488e-05 | -0.00034601 | 0.035278 | 0.00046135 | -0.00085457 | -0.0054944 | -0.0017197 | -0.0032301 | -0.0038197 | -47.0032 | 65.7211 | -57.2159 | 65.5746 | -56.6666 | -57.2754 | -57.1152 | -52.3727 | 65.7578 | -57.1381 | -56.9275 | -56.9275 | -57.2525 | -56.9138 | -0.086975 | -0.027466 | -0.17395 | 0.46234 | 0.013733 | -0.14648 | 0.10071 | -0.05951 | -0.009156 | 0.009155 | -122.6761 | 0.20142 | 0.21515 | -0.1236 | 0.22431 | -0.11444 | 0.54932 | 122.7905 | 0.21057 | 0.21057 | 122.937 | 122.8958 | 122.85 | 122.8867 | -122.9645 | -122.8867 | 122.7036 | 0.20142 | 10.1257 | 4.7562
969.1719 | 123.1338 | -57.1152 | 65.7166 | -0.091095 | -0.00044654 | 0.061385 | 0.063491 | -0.00048063 | -0.00015811 | 0.00050839 | -0.010498 | 0.0017431 | -0.0010682 | 0.0032642 | -0.0017197 | -0.0021619 | 0.0017345 | -47.1313 | 65.6845 | -57.2296 | 65.5792 | -56.6528 | -57.2525 | -57.1243 | -52.359 | 65.744 | -57.1518 | -56.9229 | -57.0053 | -57.193 | -56.8542 | -0.11444 | -0.032044 | -0.13733 | 0.46234 | -0.009156 | -0.13733 | 0.10528 | -0.022888 | -0.036621 | 0.027466 | -122.6395 | 0.10986 | 0.26093 | -0.07782 | 0.29755 | -0.041199 | 0.57678 | 122.8088 | 0.14648 | 0.22888 | 122.9141 | 122.8958 | 122.7997 | 122.8592 | -122.9462 | -122.8683 | 122.6944 | 0.19226 | 9.9838 | 4.7562
970.1719 | 123.0835 | -57.1243 | 65.7257 | -0.13687 | -1.9142e-05 | 0.066084 | 0.066268 | -0.00069423 | -0.00079891 | 0.0020038 | 0.02002 | 0.0019567 | 0.00021363 | -0.001222 | -0.00022431 | -0.0017347 | -0.0046741 | -47.2046 | 65.6662 | -57.2113 | 65.6113 | -56.6162 | -57.2662 | -57.0877 | -52.4231 | 65.712 | -57.1472 | -56.9458 | -57.0145 | -57.2159 | -56.8954 | -0.086975 | -0.059509 | -0.11444 | 0.50812 | 0.036621 | -0.14191 | 0.1236 | -0.054931 | -0.022888 | -0.013733 | -122.6715 | 0.10986 | 0.22888 | -0.091552 | 0.25177 | -0.068664 | 0.59509 | 122.8226 | 0.13275 | 0.20142 | 122.8775 | 122.8592 | 122.7905 | 122.8363 | -122.937 | -122.8729 | 122.7356 | 0.17853 | 9.9197 | 4.7012
971.1719 | 123.0469 | -57.1472 | 65.7669 | -0.060578 | 0.00083526 | 0.064589 | 0.067336 | 0.0010148 | 0.00048269 | 0.00029479 | -0.086792 | 0.0023839 | 0.00085443 | 0.00027342 | -0.0012925 | -0.0013073 | 0.0023755 | -47.319 | 65.7257 | -57.2205 | 65.5197 | -56.7169 | -57.3395 | -57.1884 | -52.5833 | 65.7761 | -57.1701 | -57.0282 | -57.1106 | -57.3029 | -56.9733 | -0.073242 | -0.041199 | -0.24719 | 0.4303 | -0.041199 | -0.19226 | 0.032043 | -0.11902 | -0.022888 | 0.009155 | -122.7951 | 0.036621 | 0.17395 | -0.15564 | 0.19684 | -0.13275 | 0.50354 | 122.7402 | 0.059509 | 0.14191 | 122.9462 | 122.9462 | 122.8729 | 122.9233 | -122.9874 | -122.937 | 122.6669 | 0.11902 | 9.8282 | 4.5639
972.1719 | 123.0835 | -57.1518 | 65.7303 | -0.098725 | -1.9142e-05 | 0.062453 | 0.066054 | 0.00037377 | 0.00091009 | 0.001363 | -0.050171 | 0.0019567 | 0.0012818 | -0.0025036 | -0.00065151 | -0.0023755 | -0.0023243 | -47.4701 | 65.7028 | -57.2479 | 65.5289 | -56.7215 | -57.3441 | -57.1884 | -52.6016 | 65.7394 | -57.193 | -56.9687 | -57.0419 | -57.2342 | -56.9229 | -0.096131 | -0.027466 | -0.20142 | 0.4303 | -0.036622 | -0.19226 | 0.059509 | -0.09613 | -0.041199 | 0.009155 | -122.699 | 0.10986 | 0.22888 | -0.082398 | 0.27008 | -0.041199 | 0.52643 | 122.7768 | 0.15106 | 0.2243 | 122.9507 | 122.9324 | 122.8546 | 122.8912 | -122.9782 | -122.9233 | 122.6807 | 0.18311 | 9.6817 | 4.5502
973.1719 | 123.1201 | -57.1289 | 65.6982 | -0.12924 | -0.00044654 | 0.063521 | 0.064773 | 0.0022964 | -0.00015811 | 0.0022174 | 0.001709 | -0.00039305 | 0.00021363 | -0.00229 | -0.0036423 | -0.0034437 | -0.0012561 | -47.5388 | 65.6616 | -57.2342 | 65.5792 | -56.6254 | -57.2525 | -57.1106 | -52.6199 | 65.7074 | -57.1747 | -56.9229 | -57.019 | -57.1976 | -56.8863 | -0.10529 | -0.036621 | -0.11902 | 0.50354 | 0.01831 | -0.1236 | 0.1236 | -0.01831 | -0.045777 | 0.009155 | -122.6212 | 0.10986 | 0.24261 | -0.068665 | 0.28839 | -0.022888 | 0.60883 | 122.8134 | 0.15564 | 0.25177 | 122.8958 | 122.8821 | 122.7905 | 122.8363 | -122.9324 | -122.8729 | 122.7081 | 0.20599 | 9.5901 | 4.509
974.1719 | 123.0515 | -57.1747 | 65.7623 | -0.098725 | 0.00019446 | 0.064375 | 0.066909 | 0.0029374 | 0.0017645 | 0.0037128 | -0.077637 | 0.00067495 | 0.0029906 | 0.0036914 | -0.0025741 | -0.0013073 | 0.00045294 | -47.6624 | 65.7349 | -57.2754 | 65.4831 | -56.7856 | -57.4081 | -57.2159 | -52.8076 | 65.7623 | -57.2205 | -56.9412 | -57.2159 | -57.2937 | -56.9366 | -0.10071 | -0.027466 | -0.27924 | 0.3891 | -0.041198 | -0.23346 | 0.05951 | -0.13275 | -0.045776 | 0 | -122.7036 | -0.041198 | 0.23804 | -0.11902 | 0.28381 | -0.073242 | 0.48981 | 122.7585 | 0.004578 | 0.27924 | 123.0103 | 122.9828 | 122.9095 | 122.937 | -123.0377 | -122.9828 | 122.6578 | 0.23346 | 9.5123 | 4.3671
975.1719 | 123.1522 | -57.106 | 65.7166 | -0.12924 | -0.0019417 | 0.067152 | 0.064345 | 0.00016017 | 0.0013373 | 0.00093559 | -0.016602 | -0.00039305 | -0.00064077 | -0.00079478 | -0.00086511 | -0.0019483 | 0.00045294 | -47.6349 | 65.6433 | -57.2388 | 65.6021 | -56.6116 | -57.2571 | -57.0969 | -52.7206 | 65.6891 | -57.193 | -56.9641 | -56.8863 | -57.0328 | -56.8634 | -0.13275 | -0.073242 | -0.11444 | 0.49439 | 0.009155 | -0.15106 | 0.14191 | -0.01831 | -0.086975 | -0.027466 | -122.6807 | 0.21973 | 0.24262 | 0.073242 | 0.32959 | 0.16022 | 0.62714 | 122.8409 | 0.3067 | 0.22888 | 122.8821 | 122.8821 | 122.7493 | 122.7951 | -122.9553 | -122.9095 | 122.7081 | 0.14191 | 9.4711 | 4.3854
976.1719 | 123.024 | -57.1609 | 65.7486 | -0.068207 | -1.9142e-05 | 0.063307 | 0.064986 | -0.0032578 | -0.00037171 | 0.00050839 | -0.010498 | 0.0025975 | -0.00042717 | -0.00058098 | -0.00065151 | -0.0017347 | 0.0017345 | -47.7722 | 65.7257 | -57.2754 | 65.6799 | -56.5613 | -57.4402 | -57.2113 | -52.9221 | 65.8035 | -57.1838 | -57.0282 | -57.1381 | -57.3212 | -56.9778 | -0.11444 | -0.022888 | -0.068664 | 0.59967 | -0.050354 | -0.27924 | 0.064087 | -0.16479 | -0.022888 | 0.054932 | -122.7768 | 0.022888 | 0.18311 | -0.16022 | 0.20599 | -0.13733 | 0.71411 | 122.9553 | 0.045776 | 0.15564 | 123.0011 | 122.9874 | 122.8867 | 122.9645 | -123.024 | -122.9324 | 122.8409 | 0.13275 | 9.3887 | 4.2389
977.1719 | 123.024 | -57.1518 | 65.7303 | -0.083466 | 0.00083526 | 0.065016 | 0.066909 | 0.00037377 | 0.0024053 | 0.0015766 | -0.050171 | 0.0043065 | 0.0032044 | 0.0019824 | -0.00086511 | -0.0017347 | 0.00066654 | -47.9141 | 65.744 | -57.2388 | 65.4877 | -56.7719 | -57.3898 | -57.2159 | -53.2928 | 65.6937 | -57.2342 | -57.0236 | -57.0648 | -57.3441 | -56.9778 | -0.086976 | 0.013733 | -0.24262 | 0.37994 | -0.064087 | -0.23804 | 0.022889 | -0.15106 | -0.082398 | -0.036621 | -122.7539 | 0.086975 | 0.17395 | -0.19226 | 0.25635 | -0.10986 | 0.46692 | 122.7264 | 0.16937 | 0.21057 | 122.9828 | 122.9279 | 122.8958 | 122.8455 | -122.9691 | -122.9645 | 122.6395 | 0.12817 | 9.2377 | 3.8589
978.1719 | 123.0515 | -57.1747 | 65.7486 | -0.068207 | 0.0027579 | 0.064375 | 0.0652 | 0.00058737 | 0.00069649 | 0.0026446 | -0.010498 | 0.0013159 | -0.00021357 | -0.001222 | -0.00022431 | -0.0030163 | 0.0019483 | -47.9645 | 65.7486 | -57.2662 | 65.4785 | -56.7261 | -57.3669 | -57.1884 | -53.0411 | 65.7532 | -57.1976 | -57.0145 | -57.1106 | -57.2983 | -56.9733 | -0.091552 | 0 | -0.27008 | 0.44861 | -0.013733 | -0.19226 | 0.077819 | -0.10071 | -0.022888 | 0.004578 | -122.7631 | 0.064087 | 0.20142 | -0.1236 | 0.2243 | -0.10071 | 0.54016 | 122.7448 | 0.086975 | 0.18311 | 123.0148 | 122.9507 | 122.9233 | 122.9279 | -123.0148 | -122.9462 | 122.6532 | 0.16022 | 9.2102 | 4.1336
979.1719 | 123.0331 | -57.1472 | 65.7715 | -0.060578 | -0.00023294 | 0.06523 | 0.066909 | 0.0027238 | 0.0011237 | -0.0018414 | -0.041016 | 0.00024775 | 0.00085443 | -0.0033582 | -0.00043791 | -0.0013073 | 0.0013073 | -48.0194 | 65.7623 | -57.2296 | 65.5426 | -56.6574 | -57.3166 | -57.1518 | -53.0319 | 65.7623 | -57.1472 | -57.019 | -57.106 | -57.2891 | -56.9595 | -0.082397 | -0.009155 | -0.22888 | 0.48981 | -0.004577 | -0.16937 | 0.07782 | -0.086975 | 0 | -0.009155 | -122.7905 | 0.041199 | 0.18768 | -0.14191 | 0.18768 | -0.14191 | 0.5722 | 122.7722 | 0.041199 | 0.12817 | 122.9919 | 122.9095 | 122.9095 | 122.9095 | -123.0011 | -122.9187 | 122.6898 | 0.12817 | 9.1278 | 4.1153
980.1719 | 123.1064 | -57.1198 | 65.6937 | -0.12924 | -0.0013009 | 0.064375 | 0.06285 | -5.343e-05 | 0.00048269 | 0.00029479 | 0.010864 | -0.00060665 | 2.8e-08 | 0.0026232 | -0.0010787 | -0.0021619 | 0.0053661 | -48.0835 | 65.6754 | -57.2571 | 65.5838 | -56.5475 | -57.225 | -57.0648 | -53.0136 | 65.7257 | -57.1793 | -56.9275 | -57.0053 | -57.1884 | -56.8634 | -0.13733 | -0.018311 | -0.10986 | 0.57221 | 0.054932 | -0.10529 | 0.19226 | 0.032043 | -0.059509 | 0.032043 | -122.6212 | 0.11444 | 0.25635 | -0.068665 | 0.31586 | -0.009156 | 0.70953 | 122.8409 | 0.17395 | 0.25177 | 122.9324 | 122.905 | 122.7951 | 122.8455 | -122.9507 | -122.8729 | 122.7036 | 0.19226 | 9.0363 | 4.1061
981.1719 | 123.0423 | -57.1701 | 65.7852 | -0.098725 | 0.0016899 | 0.063948 | 0.068832 | 0.0010148 | 0.00026909 | -0.00034601 | -0.047119 | 0.00067495 | 0.00085443 | 0.0017688 | 0.0016983 | -0.0013073 | 0.0013073 | -48.262 | 65.7486 | -57.2662 | 65.4739 | -56.749 | -57.4081 | -57.1838 | -53.2059 | 65.744 | -57.2067 | -56.9733 | -56.9458 | -57.3669 | -57.0465 | -0.09613 | -0.036621 | -0.31128 | 0.42114 | -0.013733 | -0.23804 | 0.082397 | -0.14191 | -0.036621 | -0.041198 | -122.7585 | 0.2243 | 0.1236 | -0.19684 | 0.16022 | -0.16022 | 0.51727 | 122.7402 | 0.26093 | 0.23346 | 123.0148 | 122.9507 | 122.9187 | 122.9141 | -123.0515 | -122.9919 | 122.644 | 0.19684 | 8.9081 | 3.9642
982.1719 | 123.056 | -57.1609 | 65.7623 | -0.16739 | -1.9142e-05 | 0.061385 | 0.066695 | 0.00037377 | 0.0015509 | -0.00013241 | -0.044067 | -0.0012477 | 0.0023498 | 0.0032642 | -0.00086511 | -0.0025891 | 2.554e-05 | -48.2803 | 65.7349 | -57.2433 | 65.4739 | -56.7078 | -57.3441 | -57.1747 | -53.2379 | 65.7669 | -57.2021 | -57.0374 | -57.106 | -57.2937 | -56.9595 | -0.082397 | -0.027466 | -0.28839 | 0.45319 | -0.013733 | -0.1831 | 0.068664 | -0.10071 | -0.041198 | 0.004578 | -122.7997 | 0.054932 | 0.20142 | -0.13275 | 0.24261 | -0.091553 | 0.53558 | 122.7173 | 0.09613 | 0.16479 | 122.9782 | 122.9691 | 122.8958 | 122.9279 | -123.0057 | -122.9645 | 122.6349 | 0.1236 | 8.8806 | 3.923
983.1719 | 123.1247 | -57.1335 | 65.6754 | -0.10635 | 0.0012625 | 0.063094 | 0.063918 | 0.0016556 | 0.00048269 | 0.0015766 | -0.0043946 | -0.0010339 | 2.8e-08 | -0.0044262 | -0.0025741 | -2.5678e-05 | -0.0014697 | -48.3398 | 65.6799 | -57.2342 | 65.593 | -56.575 | -57.2388 | -57.0602 | -53.1784 | 65.7349 | -57.1609 | -56.9412 | -57.019 | -57.1884 | -56.868 | -0.10071 | 0.004578 | -0.082397 | 0.55847 | 0.073242 | -0.10529 | 0.17395 | -0.004578 | -0.027466 | 0.059509 | -122.6166 | 0.11444 | 0.2655 | -0.054932 | 0.29297 | -0.027466 | 0.65918 | 122.8271 | 0.14191 | 0.21973 | 122.9141 | 122.8958 | 122.8134 | 122.8683 | -122.9095 | -122.8363 | 122.7264 | 0.19226 | 8.7936 | 3.9551
984.1719 | 123.0469 | -57.1243 | 65.799 | -0.037689 | -1.9142e-05 | 0.063948 | 0.067123 | 0.0044328 | 0.00048269 | -0.00098701 | -0.053223 | 0.0013159 | 0.0014954 | 0.00027342 | -1.0706e-05 | -0.0023755 | -0.0012561 | -48.4131 | 65.744 | -57.2342 | 65.5838 | -56.6254 | -57.2571 | -57.1014 | -53.2516 | 65.7898 | -57.1518 | -57.0007 | -57.0877 | -57.2571 | -56.9321 | -0.10986 | -0.054931 | -0.21515 | 0.49896 | 0.022889 | -0.13275 | 0.13275 | -0.022888 | -0.027465 | -0.009155 | -122.7997 | 0.036621 | 0.19226 | -0.13275 | 0.21973 | -0.10529 | 0.60883 | 122.818 | 0.064086 | 0.15106 | 122.9782 | 122.9416 | 122.8683 | 122.9141 | -123.0331 | -122.9507 | 122.7081 | 0.1236 | 8.7112 | 3.8727
985.1719 | 123.1293 | -57.0969 | 65.7349 | -0.11398 | 0.00083526 | 0.065016 | 0.064773 | 0.0020828 | 0.00091009 | 0.001363 | 0.0078126 | -0.00060665 | 0.0019226 | -0.00229 | -0.00086511 | -0.00066648 | 0.00066654 | -48.5138 | 65.7074 | -57.2205 | 65.5792 | -56.575 | -57.2479 | -57.0511 | -53.2608 | 65.7578 | -57.1518 | -56.9458 | -56.9916 | -57.1472 | -56.8405 | -0.1236 | -0.027466 | -0.15564 | 0.52185 | 0.045777 | -0.15106 | 0.16937 | -0.027466 | -0.054931 | 0.022888 | -122.6807 | 0.10529 | 0.25635 | -0.050354 | 0.31128 | 0.004577 | 0.64545 | 122.7997 | 0.16022 | 0.20599 | 122.9279 | 122.9095 | 122.8043 | 122.8546 | -122.9553 | -122.8867 | 122.6761 | 0.15106 | 8.5831 | 3.8361
986.1719 | 123.0469 | -57.1426 | 65.744 | -0.052948 | 0.0019035 | 0.063948 | 0.066482 | -0.00069423 | -0.0014399 | 0.0026446 | 0.0078126 | 0.0017431 | 0.0012818 | -0.001222 | -0.00043791 | -0.0021619 | 0.0017345 | -48.6877 | 65.7486 | -57.2159 | 65.5289 | -56.6711 | -57.3441 | -57.1243 | -53.4256 | 65.7806 | -57.1747 | -57.019 | -57.0831 | -57.2845 | -56.9366 | -0.073242 | 0.004577 | -0.21515 | 0.4715 | 0.01831 | -0.20142 | 0.091552 | -0.12817 | -0.032044 | 0.036621 | -122.7631 | 0.059509 | 0.20599 | -0.14191 | 0.23804 | -0.10986 | 0.54474 | 122.7448 | 0.091553 | 0.15564 | 122.9645 | 122.9553 | 122.8912 | 122.9233 | -122.9599 | -122.9187 | 122.6715 | 0.1236 | 8.4549 | 3.717
987.1719 | 123.0194 | -57.1426 | 65.7898 | -0.045319 | -1.9142e-05 | 0.064803 | 0.066482 | 0.001442 | -0.0012261 | 0.0028582 | -0.041016 | 0.0021703 | 0.0029906 | 0.0062548 | -0.0015061 | -0.0010937 | -0.0012561 | -48.7198 | 65.7761 | -57.2296 | 65.5563 | -56.6116 | -57.312 | -57.0831 | -53.4256 | 65.7898 | -57.1564 | -57.0053 | -57.0877 | -57.2662 | -56.9366 | -0.086975 | -0.013733 | -0.23346 | 0.53101 | 0.059509 | -0.16937 | 0.14648 | -0.082398 | -0.013733 | 0 | -122.7951 | 0.054931 | 0.20599 | -0.1236 | 0.21973 | -0.10986 | 0.61798 | 122.7859 | 0.068664 | 0.15106 | 123.0057 | 122.9462 | 122.9187 | 122.9324 | -123.0194 | -122.9462 | 122.699 | 0.13733 | 8.4229 | 3.717
988.1719 | 122.9691 | -57.1335 | 65.7852 | -0.052948 | 0.0025443 | 0.065016 | 0.067763 | -0.0011214 | 5.5488e-05 | -0.00055961 | -0.016602 | -0.00017945 | 0.004486 | -0.00015378 | -0.00065151 | -0.00088008 | 0.00045294 | -48.8434 | 65.7806 | -57.2205 | 65.4968 | -56.6711 | -57.3395 | -57.1518 | -53.5446 | 65.8035 | -57.1701 | -57.0419 | -57.106 | -57.2891 | -56.955 | -0.086975 | -0.004577 | -0.28839 | 0.46234 | -0.01831 | -0.20599 | 0.068665 | -0.11902 | -0.036621 | 0.018311 | -122.8271 | 0.027466 | 0.17853 | -0.15564 | 0.21515 | -0.11902 | 0.54932 | 122.7173 | 0.064087 | 0.12817 | 123.0011 | 122.9736 | 122.9141 | 122.937 | -123.0057 | -122.9553 | 122.6303 | 0.091553 | 8.2901 | 3.5889
989.1719 | 123.0011 | -57.1198 | 65.7806 | -0.098725 | 0.00083526 | 0.065443 | 0.064986 | 0.0018692 | -0.00058531 | 0.0028582 | -0.019653 | 0.00024775 | 0.002777 | 5.9824e-05 | -0.0012925 | -0.0013073 | 0.0034435 | -48.912 | 65.7486 | -57.2067 | 65.5289 | -56.6574 | -57.3303 | -57.1152 | -53.5538 | 65.8127 | -57.1884 | -57.0328 | -57.1152 | -57.2983 | -56.9595 | -0.086975 | -0.032044 | -0.25177 | 0.46234 | 0.004578 | -0.21057 | 0.091553 | -0.1236 | -0.068665 | 0.032043 | -122.8134 | 0.004578 | 0.16022 | -0.17853 | 0.22888 | -0.10986 | 0.54932 | 122.7356 | 0.073243 | 0.15564 | 122.9553 | 123.0011 | 122.8683 | 122.9324 | -122.9874 | -122.9691 | 122.6486 | 0.086975 | 8.2077 | 3.566
990.1719 | 123.0789 | -57.1106 | 65.7532 | -0.083466 | 0.0019035 | 0.063734 | 0.064773 | -0.00090783 | -0.00015811 | 0.001363 | 0.035278 | 0.00088875 | 0.001709 | 0.00091422 | 0.00020289 | -0.00066648 | -0.00061526 | -48.9578 | 65.7303 | -57.1701 | 65.6158 | -56.5109 | -57.2113 | -57.0053 | -53.4576 | 65.7715 | -57.1243 | -56.9504 | -56.9916 | -57.1609 | -56.8497 | -0.059509 | -0.022888 | -0.13733 | 0.59967 | 0.10529 | -0.10071 | 0.16479 | -0.041199 | -0.013733 | 0.01831 | -122.7036 | 0.11902 | 0.26093 | -0.050354 | 0.27466 | -0.036621 | 0.65918 | 122.7859 | 0.13275 | 0.17395 | 122.9004 | 122.8958 | 122.8409 | 122.8821 | -122.9233 | -122.8775 | 122.7264 | 0.16022 | 8.1528 | 3.653
991.1719 | 123.0423 | -57.0923 | 65.8081 | -0.075836 | -0.0019417 | 0.064589 | 0.06755 | -0.00048063 | 0.00048269 | 0.0026446 | -0.019653 | 0.00088875 | -0.00042717 | -0.0010084 | -0.0017197 | 0.0021105 | -0.00018806 | -48.9944 | 65.7898 | -57.1838 | 65.6158 | -56.5201 | -57.2067 | -57.019 | -53.4988 | 65.8264 | -57.0923 | -57.0511 | -56.9595 | -57.1609 | -56.8588 | -0.091553 | -0.01831 | -0.19226 | 0.5722 | 0.073242 | -0.11444 | 0.16479 | -0.022888 | 0 | 0.018311 | -122.8592 | 0.13275 | 0.23346 | -0.068665 | 0.23346 | -0.068665 | 0.66376 | 122.7997 | 0.13275 | 0.041199 | 122.9736 | 122.9187 | 122.8821 | 122.9187 | -122.9919 | -122.9004 | 122.7081 | 0.041199 | 8.0978 | 3.5934
992.1719 | 123.056 | -57.0831 | 65.8218 | -0.045319 | 0.0010489 | 0.064375 | 0.065414 | 0.0018692 | 0.00026909 | 0.0028582 | -0.037964 | -0.00082025 | -0.0014954 | 0.0015552 | -1.0706e-05 | -0.0013073 | 0.0010937 | -49.0906 | 65.8035 | -57.1609 | 65.625 | -56.5155 | -57.193 | -57.0145 | -53.5355 | 65.8127 | -57.1014 | -56.9321 | -57.0282 | -57.312 | -57.0007 | -0.07782 | -0.01831 | -0.19684 | 0.56763 | 0.068665 | -0.10986 | 0.14648 | -0.032043 | -0.01831 | -0.009155 | -122.7539 | 0.054932 | 0.082398 | -0.22888 | 0.10071 | -0.21057 | 0.64545 | 122.7859 | 0.073242 | 0.16937 | 122.9645 | 122.9141 | 122.8867 | 122.8958 | -122.9828 | -122.9233 | 122.7081 | 0.15106 | 7.9926 | 3.5477
993.1719 | 123.0057 | -57.0969 | 65.799 | -0.098725 | -0.0019417 | 0.063307 | 0.065841 | 0.00058737 | 0.00026909 | 0.00029479 | -0.044067 | -0.00082025 | 0.00064083 | 0.003905 | 0.0010575 | 0.0010425 | 0.0023755 | -49.1776 | 65.7761 | -57.2021 | 65.4968 | -56.662 | -57.3212 | -57.1014 | -53.6957 | 65.8264 | -57.1564 | -57.074 | -56.7947 | -57.1976 | -56.9595 | -0.10529 | -0.022888 | -0.30212 | 0.43488 | -0.004577 | -0.2243 | 0.10071 | -0.11902 | -0.059509 | 0.027466 | -122.8729 | 0.30212 | 0.13733 | -0.10071 | 0.19684 | -0.041199 | 0.54016 | 122.699 | 0.36163 | 0.082397 | 122.9782 | 122.9828 | 122.8729 | 122.9233 | -123.0011 | -122.9553 | 122.5937 | 0.022888 | 7.9193 | 3.4012
994.1719 | 123.111 | -57.0969 | 65.831 | -0.060578 | -0.00023294 | 0.063521 | 0.065627 | -0.0030442 | -0.00015811 | 0.0022174 | -0.019653 | 0.0011023 | 0.001709 | 0.0013416 | -0.00022431 | -0.0025891 | 0.00088014 | -49.4156 | 65.7761 | -57.225 | 65.5243 | -56.6483 | -57.3212 | -57.1014 | -53.7231 | 65.7944 | -57.1518 | -56.9046 | -57.2937 | -57.55 | -57.0602 | -0.12817 | -0.054932 | -0.3067 | 0.44861 | -0.004577 | -0.2243 | 0.1236 | -0.09613 | -0.054931 | -0.036621 | -122.7356 | -0.19684 | 0.036621 | -0.45319 | 0.091552 | -0.39825 | 0.57678 | 122.7493 | -0.14191 | 0.24719 | 123.0011 | 122.9462 | 122.8729 | 122.8912 | -123.056 | -122.9828 | 122.6212 | 0.19226 | 7.6813 | 3.3737
995.1719 | 123.1338 | -57.0328 | 65.7715 | -0.12161 | -0.0013009 | 0.065443 | 0.062423 | -0.00069423 | 0.0015509 | 0.001363 | 0.013916 | 0.00088875 | -0.00042717 | -0.0010084 | -0.0010787 | -0.0038709 | -0.0014697 | -49.4064 | 65.7211 | -57.1609 | 65.6433 | -56.4789 | -57.1655 | -56.955 | -53.6224 | 65.7623 | -57.1198 | -56.8085 | -57.0007 | -57.1335 | -56.813 | -0.12817 | -0.050354 | -0.12817 | 0.55389 | 0.07782 | -0.13275 | 0.20599 | -0.004577 | -0.086975 | -0.009155 | -122.58 | 0.032044 | 0.21973 | -0.10071 | 0.3067 | -0.013733 | 0.68207 | 122.8043 | 0.11902 | 0.31128 | 122.8821 | 122.8821 | 122.7539 | 122.7951 | -122.9324 | -122.8912 | 122.6761 | 0.2243 | 7.6263 | 3.4103
996.1719 | 123.0469 | -57.1289 | 65.7669 | -0.1445 | 0.00062166 | 0.065871 | 0.067763 | -0.0011214 | -0.0014399 | 0.0037128 | -0.044067 | 0.0015295 | 0.0040588 | -0.001222 | 0.0010575 | -0.00045288 | 0.0010937 | -49.5712 | 65.7761 | -57.2113 | 65.5151 | -56.6391 | -57.3074 | -57.0877 | -53.8284 | 65.8081 | -57.1335 | -57.0282 | -57.0923 | -57.2754 | -56.9321 | -0.082398 | 0.009155 | -0.25177 | 0.48981 | 0.041198 | -0.17853 | 0.1236 | -0.09613 | -0.004578 | 0.041198 | -122.7951 | 0.036621 | 0.19684 | -0.14648 | 0.20142 | -0.14191 | 0.5722 | 122.7264 | 0.041199 | 0.10529 | 122.9874 | 122.9416 | 122.905 | 122.937 | -122.9782 | -122.9004 | 122.644 | 0.10071 | 7.5577 | 3.3005
997.1719 | 123.0652 | -57.106 | 65.7944 | 0.030975 | -0.0010873 | 0.060744 | 0.065627 | -0.001976 | -0.0012261 | 0.0020038 | -0.025757 | -0.0010339 | 0.001068 | -0.0037854 | -0.00065151 | -0.0030163 | 0.0025891 | -49.704 | 65.7669 | -57.1838 | 65.5334 | -56.6162 | -57.2708 | -57.0602 | -53.8376 | 65.8218 | -57.1426 | -57.0099 | -57.0694 | -57.2571 | -56.9275 | -0.07782 | -0.027466 | -0.26093 | 0.48981 | 0.045776 | -0.16479 | 0.1236 | -0.086975 | -0.036621 | 0.027465 | -122.8043 | 0.036621 | 0.17853 | -0.15106 | 0.21515 | -0.11444 | 0.56763 | 122.7173 | 0.073242 | 0.13275 | 122.9507 | 122.9645 | 122.8729 | 122.9279 | -122.9782 | -122.937 | 122.6395 | 0.09613 | 7.402 | 3.2684
998.1719 | 123.024 | -57.0969 | 65.799 | 0.17593 | 0.0010489 | 0.065657 | 0.063918 | 0.00080117 | 0.0019781 | 0.0020038 | -0.01355 | 0.00067495 | 0.0014954 | 0.002196 | -0.0015061 | -0.0023755 | -0.0014697 | -49.7955 | 65.7898 | -57.1793 | 65.5334 | -56.5979 | -57.2983 | -57.0236 | -53.8467 | 65.8173 | -57.1655 | -57.0007 | -57.0831 | -57.2571 | -56.9138 | -0.082397 | -0.009155 | -0.2655 | 0.49896 | 0.073242 | -0.20142 | 0.15564 | -0.11902 | -0.068664 | 0.018311 | -122.7997 | 0.013733 | 0.18311 | -0.16022 | 0.25177 | -0.091553 | 0.58136 | 122.7127 | 0.082397 | 0.16479 | 122.9691 | 122.9828 | 122.8867 | 122.9141 | -122.9782 | -122.9645 | 122.6303 | 0.096131 | 7.3013 | 3.2501
999.1719 | 123.0194 | -57.106 | 65.8035 | -0.052948 | 0.00083526 | 0.064375 | 0.066268 | 0.0027238 | -0.0016535 | 0.0011494 | -0.019653 | 0.00067495 | 0.0021362 | 0.0036914 | -0.0019333 | -0.0015211 | 0.00023934 | -49.7955 | 65.799 | -57.1518 | 65.5746 | -56.5292 | -57.2525 | -57.0282 | -53.8513 | 65.831 | -57.1335 | -56.9916 | -57.0648 | -57.2388 | -56.9 | -0.045776 | -0.004578 | -0.22888 | 0.57678 | 0.07782 | -0.14648 | 0.1236 | -0.10071 | -0.027466 | 0.027466 | -122.7951 | 0.041199 | 0.20599 | -0.13275 | 0.23346 | -0.10529 | 0.62256 | 122.7264 | 0.068665 | 0.14191 | 122.9507 | 122.9645 | 122.905 | 122.937 | -122.9553 | -122.937 | 122.6807 | 0.11444 | 7.3105 | 3.2547
1000.1719 | 123.1247 | -57.0694 | 65.7578 | -0.060578 | -1.9142e-05 | 0.065016 | 0.063491 | -0.0011214 | 0.0021917 | 0.0034992 | 0.053589 | -0.00017945 | 0.001068 | -0.0037854 | -0.00065151 | -0.0017347 | -0.0029651 | -49.8459 | 65.712 | -57.1518 | 65.6479 | -56.4331 | -57.1609 | -56.9275 | -53.7918 | 65.7532 | -57.106 | -56.9138 | -56.9687 | -57.1243 | -56.8222 | -0.082397 | -0.045776 | -0.10986 | 0.63629 | 0.14191 | -0.091553 | 0.2243 | -0.009156 | -0.036621 | -0.004577 | -122.6715 | 0.10071 | 0.24719 | -0.054932 | 0.28381 | -0.018311 | 0.71869 | 122.7997 | 0.13733 | 0.19226 | 122.8638 | 122.8592 | 122.7814 | 122.8226 | -122.9095 | -122.8638 | 122.7173 | 0.15564 | 7.2235 | 3.2776
1001.1719 | 123.0377 | -57.1289 | 65.8173 | -0.11398 | -0.0017281 | 0.065657 | 0.065414 | -0.0015488 | 0.0011237 | 0.00072199 | -0.010498 | 0.0011023 | 2.8e-08 | 0.002196 | -0.00043791 | -0.0013073 | -0.0040333 | -50.2487 | 65.7257 | -57.2571 | 65.5884 | -56.5109 | -57.2891 | -57.019 | -53.9658 | 65.7852 | -57.1198 | -57.0099 | -57.074 | -57.2433 | -56.9229 | -0.12817 | -0.091553 | -0.22888 | 0.61798 | 0.10986 | -0.16022 | 0.23804 | -0.032044 | 0.009155 | -0.032044 | -122.8271 | 0.054931 | 0.20599 | -0.11444 | 0.19684 | -0.1236 | 0.74616 | 122.8455 | 0.045776 | 0.10986 | 122.9828 | 122.905 | 122.8546 | 122.9141 | -123.0743 | -122.937 | 122.7173 | 0.11902 | 6.8802 | 3.1631
1002.1719 | 123.1293 | -57.074 | 65.8035 | -0.1445 | -0.00023294 | 0.063094 | 0.063705 | -5.343e-05 | 0.00069649 | 0.0022174 | 0.001709 | -0.00082025 | 0.0012818 | 0.0013416 | -0.0042831 | -0.00088008 | -0.0042469 | -50.0061 | 65.7303 | -57.1564 | 65.6433 | -56.4423 | -57.1793 | -56.9138 | -53.8742 | 65.7486 | -57.1152 | -56.9092 | -56.9778 | -57.1289 | -56.813 | -0.082397 | -0.073242 | -0.16022 | 0.63171 | 0.16022 | -0.10529 | 0.24262 | -0.022888 | -0.041198 | -0.054932 | -122.7127 | 0.096131 | 0.26093 | -0.054931 | 0.30212 | -0.013733 | 0.71411 | 122.7997 | 0.13733 | 0.20599 | 122.8867 | 122.8638 | 122.8043 | 122.8226 | -122.9599 | -122.9187 | 122.7173 | 0.16479 | 7.0679 | 3.1998
1003.1719 | 123.1247 | -57.0923 | 65.7623 | -0.12161 | -0.0010873 | 0.063948 | 0.065841 | -0.00048063 | 0.0019781 | 0.0022174 | 0.001709 | 0.00088875 | 0.00085443 | -0.0048536 | -0.00065151 | -0.0032301 | 0.0013073 | -50.0931 | 65.7349 | -57.1472 | 65.6433 | -56.4331 | -57.1655 | -56.9 | -53.9108 | 65.7486 | -57.0831 | -56.9092 | -56.9595 | -57.1426 | -56.7993 | -0.054932 | -0.027466 | -0.11902 | 0.65918 | 0.19226 | -0.073242 | 0.24719 | -0.01831 | 0.009155 | -0.013733 | -122.6715 | 0.13275 | 0.29297 | -0.050354 | 0.28381 | -0.059509 | 0.71411 | 122.7905 | 0.1236 | 0.17395 | 122.8821 | 122.8317 | 122.8271 | 122.8409 | -122.9095 | -122.8455 | 122.7356 | 0.1831 | 6.9992 | 3.1815
1004.1719 | 123.0103 | -57.1152 | 65.8173 | -0.060578 | -1.9142e-05 | 0.063307 | 0.071181 | 0.001442 | 0.0021917 | -0.00013241 | -0.019653 | 0.0019567 | 0.001709 | -0.0016492 | 0.00020289 | -0.0025891 | 0.0017345 | -50.1389 | 65.7852 | -57.1838 | 65.7349 | -56.3599 | -57.3303 | -57.019 | -54.1031 | 65.831 | -57.1289 | -57.019 | -57.0923 | -57.2617 | -56.9183 | -0.068665 | -0.032044 | -0.082398 | 0.75531 | 0.09613 | -0.21515 | 0.16479 | -0.14648 | -0.013733 | 0.013733 | -122.8363 | 0.022888 | 0.19684 | -0.14648 | 0.21057 | -0.13275 | 0.82398 | 122.9187 | 0.036621 | 0.10986 | 122.9691 | 122.9599 | 122.9004 | 122.9462 | -123.0011 | -122.9462 | 122.85 | 0.09613 | 6.9763 | 3.0121
1005.1719 | 123.1155 | -57.0694 | 65.7578 | -0.098725 | 0.00019446 | 0.063521 | 0.066054 | -0.001976 | 0.00026909 | 0.0043536 | 0.02002 | -0.0021021 | 0.00021363 | -0.00464 | -0.0017197 | -0.0032301 | -0.0010425 | -50.2075 | 65.7623 | -57.1472 | 65.657 | -56.4239 | -57.1472 | -56.9092 | -53.9658 | 65.7898 | -57.1335 | -56.9 | -56.9504 | -57.1426 | -56.8085 | -0.07782 | 0.004578 | -0.10071 | 0.64545 | 0.16022 | -0.07782 | 0.23804 | 0 | -0.064087 | 0.032044 | -122.6578 | 0.11902 | 0.26093 | -0.073242 | 0.32501 | -0.009155 | 0.72327 | 122.8043 | 0.18311 | 0.23346 | 122.9095 | 122.9233 | 122.8317 | 122.8592 | -122.905 | -122.8912 | 122.7264 | 0.16937 | 6.8619 | 3.1036
1006.1719 | 123.0011 | -57.0923 | 65.8218 | -0.045319 | -1.9142e-05 | 0.064589 | 0.06755 | -0.0021896 | 0.0011237 | 0.00414 | -0.01355 | 0.0017431 | 0.0019226 | -0.0027174 | -0.0012925 | -0.00023928 | -0.0010425 | -50.3494 | 65.7898 | -57.1564 | 65.5472 | -56.5887 | -57.3532 | -57.2662 | -53.9703 | 65.8356 | -57.106 | -56.9916 | -57.0648 | -57.2754 | -56.9138 | -0.064087 | -0.032043 | -0.27466 | 0.50354 | -0.17395 | -0.26093 | -0.10986 | -0.19684 | -0.013733 | 0.013733 | -122.8134 | 0.027466 | 0.17853 | -0.18311 | 0.19226 | -0.16937 | 0.56763 | 122.7036 | 0.041199 | 0.11444 | 122.9462 | 122.9416 | 122.8821 | 122.9279 | -122.9782 | -122.9279 | 122.6395 | 0.10071 | 6.7429 | 3.1219
1007.1719 | 123.1201 | -57.0557 | 65.7532 | -0.075836 | -1.9142e-05 | 0.065657 | 0.06755 | 0.00037377 | 0.0013373 | 0.00093559 | -0.0043946 | -0.00039305 | 0.0025634 | 5.9824e-05 | -0.0030013 | -2.5678e-05 | 0.0038709 | -50.3632 | 65.7532 | -57.1747 | 65.6525 | -56.4377 | -57.2021 | -56.9 | -54.0298 | 65.799 | -57.0923 | -56.9046 | -56.9641 | -57.1426 | -56.813 | -0.11902 | 0 | -0.10071 | 0.61798 | 0.15564 | -0.14648 | 0.27466 | -0.027465 | -0.036621 | 0.045776 | -122.6578 | 0.091553 | 0.24262 | -0.086975 | 0.27924 | -0.050354 | 0.737 | 122.8271 | 0.12817 | 0.18768 | 122.9279 | 122.8912 | 122.8088 | 122.8546 | -122.9279 | -122.8455 | 122.7081 | 0.15106 | 6.6925 | 3.0258
1008.1719 | 122.9919 | -57.0969 | 65.8447 | -0.068207 | 0.0014761 | 0.066939 | 0.066909 | 0.00016017 | 0.00026909 | 0.0011494 | -0.068481 | -0.00017945 | 0.0012818 | -0.001222 | -1.0706e-05 | -0.0013073 | 0.0019483 | -50.4547 | 65.7898 | -57.1747 | 65.5609 | -56.5201 | -57.2388 | -56.9504 | -54.2084 | 65.8356 | -57.106 | -57.0282 | -57.0694 | -57.2617 | -56.9138 | -0.07782 | -0.054932 | -0.28381 | 0.57678 | 0.14648 | -0.14191 | 0.22431 | -0.064087 | -0.009155 | -0.009156 | -122.8729 | 0.027466 | 0.18311 | -0.16479 | 0.19226 | -0.15564 | 0.6546 | 122.7356 | 0.036621 | 0.07782 | 122.9645 | 122.9416 | 122.8867 | 122.9324 | -123.0194 | -122.9507 | 122.6578 | 0.068665 | 6.6422 | 2.8885
1009.1719 | 123.0606 | -57.074 | 65.7944 | -0.045319 | -0.00044654 | 0.06288 | 0.066909 | 0.0018692 | 0.00069649 | 0.0026446 | -0.0043946 | 0.0030249 | 2.8e-08 | 0.0034778 | -0.00043791 | -0.0019483 | -0.0023243 | -50.5646 | 65.7715 | -57.1747 | 65.5655 | -56.5201 | -57.2571 | -56.9412 | -54.2038 | 65.8127 | -57.1243 | -56.9778 | -57.0465 | -57.2205 | -56.8909 | -0.10071 | -0.022889 | -0.22888 | 0.55389 | 0.13275 | -0.18311 | 0.23346 | -0.082397 | -0.050354 | 0.01831 | -122.7722 | 0.027466 | 0.18311 | -0.14648 | 0.23346 | -0.09613 | 0.6546 | 122.7402 | 0.07782 | 0.14649 | 122.9462 | 122.937 | 122.8455 | 122.8867 | -122.9691 | -122.9187 | 122.6395 | 0.096131 | 6.5094 | 2.8702
1010.1719 | 123.1338 | -57.0511 | 65.7898 | -0.091095 | -0.00044654 | 0.064375 | 0.066909 | 0.0016556 | 0.0011237 | 0.0034992 | 0.016968 | 0.0028113 | 0.0012818 | -0.00015378 | -0.0019333 | -0.0017347 | -0.0023243 | -50.5783 | 65.7486 | -57.1609 | 65.6067 | -56.4514 | -57.1747 | -56.8863 | -54.1718 | 65.7761 | -57.1014 | -56.9046 | -56.9504 | -57.1518 | -56.7993 | -0.10986 | -0.041199 | -0.18311 | 0.59967 | 0.16479 | -0.1236 | 0.27466 | -0.013733 | -0.050354 | -0.013733 | -122.6944 | 0.10071 | 0.25177 | -0.10071 | 0.30212 | -0.050354 | 0.70953 | 122.7676 | 0.15106 | 0.19684 | 122.9095 | 122.8775 | 122.7997 | 122.8271 | -122.9507 | -122.8912 | 122.6578 | 0.14648 | 6.4728 | 2.8793
1011.1719 | 122.9919 | -57.0786 | 65.8585 | -0.12924 | 0.00019446 | 0.06288 | 0.067977 | 0.00037377 | 0.0015509 | 0.001363 | -0.047119 | -0.00039305 | 0.0023498 | 0.001128 | -0.0025741 | -0.0021619 | -0.00061526 | -50.6744 | 65.8081 | -57.1609 | 65.538 | -56.575 | -57.2662 | -56.9595 | -54.3045 | 65.8493 | -57.1198 | -57.1472 | -57.106 | -56.9138 | -56.7307 | -0.082398 | -0.050354 | -0.32043 | 0.50354 | 0.11902 | -0.18768 | 0.20142 | -0.10529 | -0.041199 | -0.009155 | -123.0057 | -0.027466 | 0.3479 | 0.1648 | 0.3891 | 0.20599 | 0.58594 | 122.699 | 0.013733 | -0.027466 | 122.9691 | 122.9691 | 122.8867 | 122.9279 | -123.0194 | -122.9782 | 122.6166 | -0.068665 | 6.4041 | 2.774
1012.1719 | 122.9324 | -57.1289 | 65.7806 | -0.060578 | 0.00019446 | 0.063307 | 0.065841 | -0.0017624 | 5.5488e-05 | 0.0032856 | -0.059326 | 3.4148e-05 | -0.00085457 | -0.0033582 | -0.00065151 | -0.0010937 | 0.00023934 | -50.7431 | 65.8218 | -57.1335 | 65.5701 | -56.5384 | -57.2571 | -56.9504 | -54.3777 | 65.831 | -57.1152 | -57.0007 | -57.0557 | -57.2296 | -57.0465 | -0.004578 | 0.041198 | -0.21057 | 0.59052 | 0.17853 | -0.12817 | 0.18311 | -0.1236 | 0.013733 | 0.050354 | -122.7814 | 0.073242 | 0.082397 | -0.10071 | 0.068664 | -0.11444 | 0.59509 | 122.7036 | 0.059509 | 0.11444 | 122.9553 | 122.9462 | 122.9507 | 122.9599 | -122.9141 | -122.8958 | 122.699 | 0.12817 | 6.3858 | 2.7512
1013.1719 | 123.0148 | -57.074 | 65.8264 | -0.23605 | -0.0030099 | 0.062453 | 0.067336 | -0.0026168 | 0.00048269 | 0.0039264 | -0.0074462 | -0.0010339 | 0.00085443 | -0.001222 | 0.00041649 | -0.0023755 | 0.0045117 | -50.6058 | 65.8081 | -57.1289 | 65.5838 | -56.5063 | -57.2342 | -56.9138 | -54.3686 | 65.8447 | -57.1106 | -56.9916 | -57.0374 | -57.2159 | -56.8954 | -0.054931 | -0.018311 | -0.24262 | 0.56763 | 0.16022 | -0.16022 | 0.21515 | -0.10529 | -0.036621 | 0.018311 | -122.818 | 0.036621 | 0.17853 | -0.14191 | 0.21515 | -0.10529 | 0.62256 | 122.7127 | 0.073242 | 0.11902 | 122.937 | 122.9553 | 122.8821 | 122.9187 | -122.9553 | -122.937 | 122.6578 | 0.082398 | 6.4682 | 2.7054
1014.1719 | 123.0972 | -57.0511 | 65.8264 | -0.083466 | 0.0014761 | 0.066084 | 0.067336 | 0.0018692 | 0.0019781 | 0.0011494 | -0.010498 | 3.4148e-05 | 0.00021363 | 0.0036914 | -0.0015061 | -0.0017347 | -0.0016833 | -50.8804 | 65.799 | -57.1564 | 65.5975 | -56.4743 | -57.1976 | -56.8451 | -54.3503 | 65.8264 | -57.074 | -56.9412 | -56.9962 | -57.1701 | -56.8359 | -0.10529 | -0.027466 | -0.22888 | 0.57678 | 0.20599 | -0.14649 | 0.31128 | -0.041199 | -0.022889 | 0 | -122.7676 | 0.054931 | 0.21515 | -0.11902 | 0.23804 | -0.09613 | 0.68207 | 122.7539 | 0.07782 | 0.13275 | 122.9553 | 122.9004 | 122.85 | 122.8775 | -122.9828 | -122.9004 | 122.6486 | 0.10986 | 6.1707 | 2.7008
1015.1719 | 123.0057 | -57.0831 | 65.8447 | -0.052948 | 0.0014761 | 0.064589 | 0.066695 | 0.00037377 | 0.0017645 | 0.0022174 | -0.053223 | -0.0012477 | 0.0032044 | 0.00091422 | -0.0027877 | -0.00023928 | -0.00061526 | -50.9216 | 65.8035 | -57.1564 | 65.5975 | -56.5018 | -57.2021 | -56.8726 | -54.4098 | 65.8813 | -57.1014 | -57.0099 | -57.0648 | -57.2433 | -56.8863 | -0.073242 | -0.041199 | -0.24719 | 0.58136 | 0.21057 | -0.11902 | 0.28381 | -0.045776 | -0.01831 | 0.036621 | -122.8546 | 0.018311 | 0.19684 | -0.16022 | 0.21515 | -0.14191 | 0.6546 | 122.7539 | 0.036621 | 0.091552 | 122.9599 | 122.9828 | 122.8867 | 122.9645 | -123.0011 | -122.9462 | 122.6807 | 0.073242 | 6.1615 | 2.6733
1016.1719 | 122.9874 | -57.0831 | 65.8539 | -0.060578 | 0.00040806 | 0.065871 | 0.068191 | -0.0015488 | 0.0026191 | 0.0034992 | -0.037964 | 0.00067495 | 0.0012818 | -0.00015378 | 0.00084389 | -0.0023755 | 0.0032299 | -50.9857 | 65.8173 | -57.1472 | 65.5838 | -56.5063 | -57.1884 | -56.8497 | -54.4373 | 65.8722 | -57.1014 | -57.0007 | -57.0465 | -57.2433 | -56.8954 | -0.064087 | -0.036621 | -0.27008 | 0.57678 | 0.23346 | -0.10529 | 0.29755 | -0.041199 | -0.01831 | 0.01831 | -122.8546 | 0.036621 | 0.18768 | -0.16022 | 0.20599 | -0.14191 | 0.64087 | 122.731 | 0.054931 | 0.10071 | 122.9645 | 122.9736 | 122.9004 | 122.9553 | -123.0011 | -122.9553 | 122.6669 | 0.082398 | 6.0974 | 2.6459
1017.1719 | 123.0606 | -57.0557 | 65.8173 | -0.068207 | 0.00083526 | 0.063734 | 0.068832 | -0.001976 | 0.0017645 | 0.0032856 | -0.016602 | 0.0013159 | 0.0012818 | -0.0014356 | -0.00086511 | -0.0017347 | 0.0019483 | -51.0818 | 65.8356 | -57.1518 | 65.5792 | -56.488 | -57.2113 | -56.8405 | -54.4464 | 65.8676 | -57.0877 | -56.9504 | -57.0099 | -57.1838 | -56.8634 | -0.09613 | 0.01831 | -0.23804 | 0.56763 | 0.21515 | -0.15564 | 0.31128 | -0.05951 | -0.032044 | 0.050354 | -122.7676 | 0.045776 | 0.19226 | -0.12817 | 0.22431 | -0.09613 | 0.66376 | 122.731 | 0.07782 | 0.13733 | 122.9874 | 122.9553 | 122.8912 | 122.9233 | -122.9691 | -122.905 | 122.6349 | 0.10529 | 5.9738 | 2.6093
1018.1719 | 123.0194 | -57.0923 | 65.8356 | -0.045319 | -0.0015145 | 0.06288 | 0.069259 | -0.0024032 | -0.00015811 | 0.0034992 | -0.037964 | 0.0013159 | 2.8e-08 | -0.0031446 | 0.00041649 | -0.0023755 | -0.0010425 | -51.1642 | 65.8081 | -57.1518 | 65.5655 | -56.5384 | -57.2205 | -56.868 | -54.5334 | 65.8813 | -57.0831 | -56.9733 | -56.9504 | -57.5729 | -57.0923 | -0.059509 | -0.027466 | -0.27008 | 0.55389 | 0.2243 | -0.12817 | 0.28381 | -0.068665 | 0.009155 | 0.045777 | -122.8088 | 0.14191 | 0 | -0.48065 | -0.009155 | -0.48981 | 0.6134 | 122.7173 | 0.13275 | 0.10986 | 122.9599 | 122.9645 | 122.9004 | 122.9736 | -122.9874 | -122.9187 | 122.6578 | 0.11902 | 5.928 | 2.5589
1019.1719 | 123.0148 | -57.0511 | 65.8676 | -0.075836 | 0.00019446 | 0.064589 | 0.067336 | 0.0018692 | 0.00069649 | 0.0022174 | -0.025757 | 0.0019567 | 0.0023498 | -0.0010084 | -0.00086511 | -0.0021619 | -0.0040333 | -51.1826 | 65.8585 | -57.1106 | 65.6204 | -56.4331 | -57.1518 | -56.8039 | -54.4647 | 65.8722 | -57.0786 | -56.9595 | -57.0236 | -57.2159 | -56.8726 | -0.05951 | -0.009156 | -0.24719 | 0.61798 | 0.24719 | -0.10071 | 0.3067 | -0.041198 | -0.027466 | 0.004577 | -122.8271 | 0.027465 | 0.17853 | -0.1648 | 0.20599 | -0.13733 | 0.67749 | 122.731 | 0.054931 | 0.11902 | 122.9691 | 122.9507 | 122.9095 | 122.9233 | -122.9782 | -122.9462 | 122.6715 | 0.091552 | 5.8685 | 2.5864
1020.1719 | 122.9645 | -57.0786 | 65.8447 | -0.083466 | 0.00062166 | 0.064589 | 0.066054 | -0.0011214 | 0.0017645 | 0.00072199 | -0.025757 | 0.0019567 | 0.00064083 | 0.0019824 | -0.0010787 | -0.0036573 | 0.0015209 | -51.2878 | 65.8218 | -57.1472 | 65.5884 | -56.5155 | -57.1976 | -56.8222 | -54.5792 | 65.8905 | -57.0877 | -57.0099 | -57.0511 | -57.2388 | -56.8954 | -0.068665 | -0.022889 | -0.25635 | 0.56305 | 0.25635 | -0.11902 | 0.32501 | -0.050354 | -0.009156 | 0.045776 | -122.8546 | 0.027466 | 0.18311 | -0.16022 | 0.19226 | -0.15106 | 0.63171 | 122.7356 | 0.036622 | 0.07782 | 122.9691 | 122.9782 | 122.9004 | 122.9691 | -122.9919 | -122.9324 | 122.6669 | 0.068664 | 5.7907 | 2.4994
1021.1719 | 123.0103 | -57.0557 | 65.8218 | -0.098725 | -0.00023294 | 0.064803 | 0.066054 | 0.003151 | 0.0015509 | 0.009267 | -0.019653 | 0.0019567 | 0.00042723 | 0.0034778 | -0.00086511 | -0.0021619 | 0.0019483 | -51.3977 | 65.8218 | -57.1426 | 65.3961 | -56.7581 | -56.8771 | -56.5842 | -54.5471 | 65.8813 | -57.074 | -57.0007 | -57.0145 | -57.2205 | -56.8817 | -0.086975 | 0 | -0.42572 | 0.29755 | 0.4715 | 0.17853 | 0.55847 | 0.2655 | -0.018311 | 0.05951 | -122.8226 | 0.041199 | 0.17395 | -0.16479 | 0.19226 | -0.14648 | 0.38452 | 122.5388 | 0.05951 | 0.073243 | 122.9645 | 122.9553 | 122.8775 | 122.937 | -122.9645 | -122.8958 | 122.4518 | 0.054932 | 5.658 | 2.5085
1022.1719 | 122.9782 | -57.0557 | 65.8539 | -0.060578 | 0.0016899 | 0.065871 | 0.069472 | 0.00080117 | 0.00069649 | 0.0043536 | -0.022705 | 0.0025975 | -0.00085457 | 0.0024096 | -0.0010787 | -0.0013073 | 0.0023755 | -51.4114 | 65.8401 | -57.0969 | 65.6067 | -56.4789 | -57.1793 | -56.7947 | -54.6021 | 65.863 | -57.0786 | -56.987 | -57.0374 | -57.2113 | -56.8817 | -0.041199 | -0.013733 | -0.24719 | 0.57678 | 0.26093 | -0.1236 | 0.30212 | -0.082397 | -0.022888 | 0.009155 | -122.8409 | 0.01831 | 0.17395 | -0.15564 | 0.19684 | -0.13275 | 0.61798 | 122.7036 | 0.041198 | 0.091552 | 122.937 | 122.9416 | 122.8958 | 122.9187 | -122.9507 | -122.9324 | 122.6624 | 0.068664 | 5.6442 | 2.4536
1023.1719 | 123.0103 | -57.0557 | 65.8401 | -0.11398 | -0.00044654 | 0.06288 | 0.068618 | -0.0030442 | 0.0028327 | 0.0049946 | -0.01355 | 0.00067495 | 0.0021362 | 0.0079638 | -0.0021469 | -0.0036573 | -0.0016833 | -51.5442 | 65.8173 | -57.1472 | 65.5701 | -56.5109 | -57.1838 | -56.7993 | -54.6478 | 65.8539 | -57.1198 | -56.8634 | -57.1152 | -57.2021 | -56.8268 | -0.091553 | -0.022888 | -0.27008 | 0.54474 | 0.25635 | -0.12817 | 0.3479 | -0.036621 | -0.064087 | 0.013733 | -122.7036 | -0.059509 | 0.22888 | -0.14648 | 0.29297 | -0.082397 | 0.63629 | 122.7173 | 0.004578 | 0.25635 | 122.9645 | 122.9736 | 122.8729 | 122.9095 | -122.9874 | -122.9599 | 122.6257 | 0.19226 | 5.5115 | 2.4078
1024.1719 | 123.0331 | -57.0145 | 65.8722 | -0.022431 | 0.0010489 | 0.063307 | 0.067977 | -0.0021896 | -0.00015811 | 0.0032856 | 0.02002 | 0.00046135 | 0.0023498 | 0.002196 | -0.0012925 | -0.0028027 | 0.00045294 | -51.5488 | 65.8951 | -57.1014 | 65.6296 | -56.4423 | -57.106 | -56.7352 | -54.6021 | 65.9042 | -57.0557 | -56.9504 | -56.9733 | -57.1518 | -56.8405 | -0.086975 | 0.022889 | -0.24261 | 0.5722 | 0.27924 | -0.091553 | 0.36621 | -0.004578 | -0.041199 | 0.032044 | -122.8226 | 0.041198 | 0.17395 | -0.13733 | 0.21515 | -0.09613 | 0.65918 | 122.731 | 0.082397 | 0.10529 | 122.9965 | 122.9599 | 122.9095 | 122.9187 | -122.9736 | -122.9279 | 122.644 | 0.064087 | 5.4657 | 2.4124
1025.1719 | 122.9645 | -57.1014 | 65.8585 | -0.075836 | 0.00040806 | 0.064375 | 0.068618 | 0.001442 | 0.0026191 | 0.0032856 | -0.037964 | 0.00088875 | -0.00021357 | 0.00091422 | -1.0706e-05 | -0.0015211 | 0.0010937 | -51.6632 | 65.8264 | -57.1793 | 65.5609 | -56.5338 | -57.2113 | -56.813 | -54.7028 | 65.8768 | -57.0831 | -56.955 | -57.0511 | -57.4219 | -57.0877 | -0.07782 | -0.032043 | -0.29755 | 0.56763 | 0.28839 | -0.10986 | 0.36621 | -0.032044 | 0.01831 | 0.018311 | -122.8134 | 0.050354 | 0.013732 | -0.32044 | -0.004578 | -0.33875 | 0.64545 | 122.7402 | 0.032044 | 0.12817 | 123.0057 | 122.9599 | 122.9279 | 122.9782 | -123.0377 | -122.9416 | 122.6624 | 0.14648 | 5.4382 | 2.3987
1026.1719 | 122.9736 | -57.0602 | 65.8447 | -0.10635 | 0.0027579 | 0.064803 | 0.067336 | 0.0040054 | 0.00048269 | 0.0034992 | -0.019653 | 0.0036657 | 0.003418 | -0.0016492 | -0.0017197 | -0.0023755 | 0.0017345 | -51.7319 | 65.8539 | -57.1335 | 65.5655 | -56.5292 | -57.1976 | -56.7902 | -54.744 | 65.8951 | -57.0694 | -56.9916 | -57.0419 | -57.2342 | -56.8634 | -0.073242 | 0.009155 | -0.27924 | 0.53101 | 0.27008 | -0.13733 | 0.34332 | -0.064087 | -0.009155 | 0.050354 | -122.8363 | 0.018311 | 0.19684 | -0.17395 | 0.20599 | -0.16479 | 0.60425 | 122.699 | 0.027466 | 0.07782 | 122.9874 | 122.9645 | 122.9141 | 122.9553 | -122.9782 | -122.9141 | 122.6257 | 0.068665 | 5.3284 | 2.3163
1027.1719 | 123.0515 | -57.0694 | 65.831 | 0.076752 | -1.9142e-05 | 0.063948 | 0.06755 | -0.0024032 | -0.0012261 | 0.0034992 | 0.001709 | 0.0021703 | 0.003418 | 0.0026232 | -0.0017197 | -0.0017347 | -0.0016833 | -51.8097 | 65.8401 | -57.1381 | 65.5838 | -56.5063 | -57.1793 | -56.749 | -54.7302 | 65.8585 | -57.0694 | -56.955 | -57.0328 | -57.1838 | -56.8497 | -0.068665 | 0.009155 | -0.24719 | 0.56305 | 0.32044 | -0.10986 | 0.3891 | -0.041198 | 0 | 0.027465 | -122.786 | 0.036621 | 0.21973 | -0.11444 | 0.21973 | -0.11444 | 0.63171 | 122.7219 | 0.036621 | 0.11444 | 122.9782 | 122.9279 | 122.9095 | 122.9279 | -122.9691 | -122.9004 | 122.6532 | 0.11444 | 5.2597 | 2.3392
1028.1719 | 123.0011 | -57.0602 | 65.8493 | -0.045319 | -0.0010873 | 0.064162 | 0.066909 | 0.0029374 | 0.0017645 | 0.00072199 | -0.028809 | -0.0012477 | 0.0025634 | -0.0018628 | -1.0706e-05 | -0.00023928 | -0.0010425 | -51.8417 | 65.8447 | -57.1106 | 65.593 | -56.5201 | -57.1609 | -56.7398 | -54.8126 | 65.8859 | -57.0969 | -56.9916 | -57.019 | -57.2205 | -56.8771 | -0.050354 | -0.004577 | -0.25635 | 0.54016 | 0.32044 | -0.10071 | 0.37079 | -0.050354 | -0.036621 | 0.036621 | -122.8409 | 0.041199 | 0.18311 | -0.16022 | 0.21973 | -0.1236 | 0.59052 | 122.7036 | 0.07782 | 0.10529 | 122.9553 | 122.9828 | 122.905 | 122.9462 | -122.9599 | -122.9462 | 122.6532 | 0.068665 | 5.2185 | 2.2476
1029.1719 | 123.1522 | -56.9824 | 65.8676 | -0.075836 | 0.0019035 | 0.063307 | 0.065841 | -0.004753 | 0.0011237 | 0.00029479 | 0.096313 | 0.00088875 | -0.00021357 | -0.0078442 | -0.00022431 | -0.0030163 | 0.0017345 | -51.8372 | 65.8264 | -57.0557 | 65.7394 | -56.3049 | -56.9733 | -56.5384 | -54.5883 | 65.8585 | -57.0053 | -56.8314 | -56.8405 | -56.9916 | -56.7123 | -0.073242 | -0.041199 | -0.12817 | 0.67749 | 0.44403 | 0.009155 | 0.51727 | 0.082397 | -0.022888 | -0.009156 | -122.699 | 0.14191 | 0.27008 | -0.009155 | 0.29297 | 0.013733 | 0.75073 | 122.7951 | 0.16479 | 0.17395 | 122.8821 | 122.8638 | 122.8088 | 122.8409 | -122.9233 | -122.8729 | 122.7219 | 0.15106 | 5.1453 | 2.3941
1030.1719 | 123.0789 | -56.9916 | 65.8401 | -0.083466 | -0.00023294 | 0.06288 | 0.064773 | -0.001976 | -0.0012261 | 0.0045672 | 0.029175 | -0.00039305 | 0.0032044 | -0.0010084 | -0.00065151 | -0.0038709 | -0.00040166 | -51.9379 | 65.7715 | -57.0786 | 65.6799 | -56.3828 | -57.0648 | -56.6299 | -54.7028 | 65.8401 | -57.0465 | -56.8771 | -56.9366 | -57.1014 | -56.7856 | -0.086975 | -0.068665 | -0.16022 | 0.60883 | 0.36163 | -0.073242 | 0.44861 | 0.013733 | -0.054932 | 0 | -122.7173 | 0.054931 | 0.20599 | -0.10986 | 0.26093 | -0.054931 | 0.6958 | 122.7585 | 0.10986 | 0.16937 | 122.85 | 122.8867 | 122.7631 | 122.8317 | -122.9187 | -122.8867 | 122.6715 | 0.11444 | 5.0537 | 2.2888
1031.1719 | 123.1247 | -57.0007 | 65.8401 | -0.098725 | -0.0010873 | 0.065657 | 0.067336 | -0.0015488 | 5.5488e-05 | 0.0011494 | 0.029175 | -0.0010339 | 0.00042723 | 0.0028368 | -0.0021469 | -0.0032301 | -0.00082886 | -51.9928 | 65.7898 | -57.0557 | 65.7257 | -56.3416 | -57.0328 | -56.5704 | -54.6661 | 65.8081 | -57.0374 | -56.8909 | -56.9 | -57.0602 | -56.7444 | -0.054932 | -0.050354 | -0.11444 | 0.65918 | 0.4303 | -0.032044 | 0.48523 | 0.022888 | -0.036622 | -0.032044 | -122.731 | 0.10071 | 0.25635 | -0.05951 | 0.29297 | -0.022888 | 0.71411 | 122.7814 | 0.13733 | 0.14648 | 122.8455 | 122.8455 | 122.7905 | 122.8088 | -122.8958 | -122.8775 | 122.7264 | 0.10986 | 5.0079 | 2.3346
1032.1719 | 123.0698 | -57.0145 | 65.8401 | -0.098725 | 0.00040806 | 0.063307 | 0.068191 | -0.0045394 | -0.0010125 | 0.003072 | 0.047485 | -0.00060665 | -0.00021357 | -0.0037854 | -0.0019333 | -0.0013073 | -0.00040166 | -52.0844 | 65.7806 | -57.0557 | 65.6845 | -56.3553 | -57.0602 | -56.6071 | -54.7348 | 65.8401 | -57.0328 | -56.8863 | -56.9183 | -57.0786 | -56.781 | -0.041199 | -0.059509 | -0.15564 | 0.65918 | 0.40741 | -0.045777 | 0.44861 | -0.004578 | -0.018311 | 0 | -122.7264 | 0.09613 | 0.23346 | -0.064087 | 0.25177 | -0.045776 | 0.70038 | 122.7402 | 0.11444 | 0.14648 | 122.8363 | 122.8729 | 122.7951 | 122.8546 | -122.8958 | -122.8729 | 122.699 | 0.12817 | 4.9301 | 2.2797
1033.1719 | 123.0148 | -57.0236 | 65.8997 | -0.091095 | 0.00040806 | 0.063948 | 0.069259 | -0.0015488 | -0.0012261 | 0.0047808 | -0.028809 | 0.0017431 | 0.00064083 | 0.00048702 | -0.0019333 | -0.0023755 | -0.0025379 | -52.153 | 65.8585 | -57.1106 | 65.6113 | -56.5018 | -57.1381 | -56.6666 | -54.8859 | 65.9271 | -57.0557 | -56.9687 | -57.0236 | -57.2205 | -56.868 | -0.086975 | -0.041199 | -0.28839 | 0.52185 | 0.35706 | -0.11444 | 0.44403 | -0.027466 | -0.032043 | 0.027466 | -122.8683 | 0 | 0.15564 | -0.19684 | 0.18768 | -0.16479 | 0.60883 | 122.7219 | 0.032043 | 0.086975 | 122.9691 | 122.9828 | 122.8821 | 122.9507 | -123.0103 | -122.9553 | 122.6349 | 0.054932 | 4.8706 | 2.1378
1034.1719 | 123.0835 | -56.9824 | 65.8676 | -0.068207 | -0.00023294 | 0.06288 | 0.066909 | -0.0017624 | 0.0017645 | 0.003072 | 0.065796 | 0.00067495 | -0.00042717 | -0.005708 | -0.0010787 | -0.0038709 | -0.0027515 | -52.1667 | 65.8264 | -57.0374 | 65.7028 | -56.3599 | -57.0145 | -56.5521 | -54.7531 | 65.8813 | -57.0145 | -56.8588 | -56.8542 | -57.0145 | -56.7352 | -0.054932 | -0.041199 | -0.16479 | 0.62256 | 0.4303 | -0.032043 | 0.48523 | 0.022889 | -0.032043 | 0.013733 | -122.7264 | 0.12817 | 0.24719 | -0.032043 | 0.27924 | 0 | 0.67749 | 122.7402 | 0.16022 | 0.15564 | 122.8638 | 122.8958 | 122.8088 | 122.8638 | -122.905 | -122.8821 | 122.6852 | 0.1236 | 4.8157 | 2.2293
1035.1719 | 123.024 | -57.019 | 65.863 | -0.060578 | -0.0021555 | 0.064162 | 0.070541 | 0.0029374 | 0.0015509 | 0.00093559 | -0.034912 | 0.0028113 | 0.00085443 | -0.0031446 | -0.00065151 | -0.00066648 | 0.00066654 | -52.2675 | 65.8539 | -57.1289 | 65.8539 | -56.3828 | -57.2067 | -56.6299 | -54.9133 | 65.8951 | -57.0648 | -56.9458 | -57.0007 | -57.1701 | -56.8314 | -0.10986 | -0.009155 | -0.009155 | 0.63629 | 0.3891 | -0.18768 | 0.49896 | -0.07782 | -0.045776 | 0.032044 | -122.8088 | 0.018311 | 0.18768 | -0.15106 | 0.23346 | -0.10529 | 0.74616 | 122.9828 | 0.064087 | 0.11902 | 122.9828 | 122.9599 | 122.8729 | 122.9141 | -122.9919 | -122.9279 | 122.8729 | 0.073242 | 4.7516 | 2.1057
1036.1719 | 123.0148 | -57.0374 | 65.8768 | -0.098725 | -0.0010873 | 0.063307 | 0.070541 | -5.343e-05 | 0.00069649 | 0.002431 | -0.034912 | 3.4148e-05 | 2.8e-08 | -0.0042126 | -0.0023605 | -0.0010937 | -0.0038197 | -52.327 | 65.863 | -57.106 | 65.831 | -56.3965 | -57.2067 | -56.6025 | -54.9133 | 65.918 | -57.0465 | -56.9412 | -57.0007 | -57.1838 | -56.8268 | -0.068664 | -0.013733 | -0.045776 | 0.64087 | 0.43488 | -0.16937 | 0.50354 | -0.10071 | -0.009155 | 0.041199 | -122.818 | 0.036622 | 0.21057 | -0.14648 | 0.21973 | -0.13733 | 0.70953 | 122.937 | 0.045777 | 0.10529 | 122.9691 | 122.9645 | 122.9004 | 122.9553 | -122.9828 | -122.9233 | 122.8683 | 0.096131 | 4.7104 | 2.124
1037.1719 | 123.0469 | -57.0328 | 65.831 | -0.052948 | -0.0010873 | 0.06053 | 0.070327 | 0.0027238 | 0.0019781 | 0.0056354 | -0.016602 | 0.0028113 | 0.0023498 | -0.0018628 | -0.00065151 | -0.0013073 | -0.0014697 | -52.3315 | 65.8447 | -57.0694 | 65.6479 | -56.4194 | -57.0923 | -56.6025 | -54.8721 | 65.8768 | -57.0465 | -56.8817 | -56.9046 | -57.106 | -56.7947 | -0.036621 | 0.013733 | -0.18311 | 0.6134 | 0.4303 | -0.059509 | 0.46692 | -0.022888 | -0.013733 | 0.045776 | -122.7127 | 0.12817 | 0.23804 | -0.073242 | 0.25177 | -0.059509 | 0.65002 | 122.7173 | 0.14191 | 0.16479 | 122.9141 | 122.9233 | 122.8775 | 122.9095 | -122.9004 | -122.8775 | 122.6807 | 0.15106 | 4.7012 | 2.1606
1038.1719 | 123.1247 | -57.0007 | 65.831 | -0.11398 | -1.9142e-05 | 0.063521 | 0.070327 | -0.00090783 | -0.0027215 | 0.0047808 | -0.0074462 | 0.00067495 | 0.001709 | -0.0078442 | -0.0023605 | -0.0034437 | 0.0030163 | -52.3224 | 65.8081 | -57.0694 | 65.7166 | -56.3278 | -56.987 | -56.5201 | -54.8172 | 65.8539 | -57.0465 | -56.8359 | -56.8588 | -57.0465 | -56.7307 | -0.068665 | -0.022889 | -0.11444 | 0.67291 | 0.48065 | 0.013732 | 0.54932 | 0.082397 | -0.045777 | 0.022888 | -122.6669 | 0.14191 | 0.27008 | -0.045777 | 0.31586 | 0 | 0.74158 | 122.786 | 0.18768 | 0.21057 | 122.8775 | 122.9004 | 122.8088 | 122.8546 | -122.9004 | -122.8775 | 122.7173 | 0.16479 | 4.6783 | 2.1835
1039.1719 | 123.1293 | -56.9458 | 65.8676 | -0.11398 | 0.0012625 | 0.062239 | 0.067123 | -0.0045394 | 0.0015509 | 0.001363 | 0.068848 | 3.4148e-05 | -0.00042717 | -0.002931 | -0.00065151 | -0.0015211 | -0.00018806 | -52.3544 | 65.8585 | -57.0145 | 65.7623 | -56.2592 | -56.9138 | -56.4377 | -54.7943 | 65.8859 | -57.0053 | -56.7993 | -56.7902 | -56.955 | -56.7032 | -0.068664 | -0.009156 | -0.10529 | 0.68665 | 0.50812 | 0.032044 | 0.57678 | 0.10071 | -0.059509 | 0.01831 | -122.6669 | 0.15564 | 0.24262 | -0.009155 | 0.30212 | 0.050354 | 0.75531 | 122.7768 | 0.21515 | 0.20599 | 122.8729 | 122.8912 | 122.8043 | 122.8317 | -122.8821 | -122.8729 | 122.7081 | 0.14649 | 4.5914 | 2.1515
1040.1719 | 123.0469 | -57.0007 | 65.918 | -0.075836 | -0.00023294 | 0.064589 | 0.071609 | 0.00251 | 0.0011237 | 0.0020038 | -0.034912 | 0.0013159 | 2.8e-08 | -0.0016492 | -0.00022431 | 0.00082892 | -0.0029651 | -52.4551 | 65.8447 | -57.1198 | 65.831 | -56.3644 | -57.1884 | -56.5567 | -54.982 | 65.918 | -57.0511 | -56.9275 | -56.9733 | -57.1884 | -56.8359 | -0.11902 | -0.073242 | -0.086975 | 0.63629 | 0.44403 | -0.18768 | 0.56305 | -0.068665 | -0.050354 | 0 | -122.8455 | 0.027465 | 0.16479 | -0.18768 | 0.21515 | -0.13733 | 0.75531 | 122.9507 | 0.077819 | 0.1236 | 122.9645 | 122.9691 | 122.8455 | 122.9187 | -123.0377 | -122.9691 | 122.8317 | 0.073242 | 4.5456 | 2.0187
1041.1719 | 123.111 | -57.0053 | 65.8356 | -0.075836 | -0.0013009 | 0.064589 | 0.068404 | 0.0022964 | 0.00048269 | 0.0045672 | 0.0078126 | 0.0013159 | -0.00042717 | -0.0027174 | -0.00086511 | -0.0019483 | -0.00040166 | -52.4414 | 65.7898 | -57.0602 | 65.7532 | -56.3004 | -56.9824 | -56.4789 | -54.8721 | 65.8813 | -57.0282 | -56.8359 | -56.8542 | -57.0465 | -56.7123 | -0.054932 | -0.045776 | -0.082397 | 0.70496 | 0.52643 | 0.022888 | 0.58136 | 0.07782 | -0.022888 | 0.045777 | -122.6715 | 0.15106 | 0.29297 | -0.041199 | 0.31586 | -0.018311 | 0.75989 | 122.8134 | 0.17395 | 0.19226 | 122.85 | 122.9095 | 122.7951 | 122.8867 | -122.8958 | -122.8638 | 122.7585 | 0.16937 | 4.5639 | 2.1332
1042.1719 | 123.0835 | -57.0236 | 65.8722 | -0.10635 | -0.0010873 | 0.062666 | 0.071822 | -0.0038986 | 0.00091009 | 0.0011494 | -0.034912 | 0.0015295 | 2.8e-08 | -0.00229 | -0.0021469 | -0.0025891 | 2.554e-05 | -52.597 | 65.8539 | -57.1014 | 65.657 | -56.3736 | -57.0694 | -56.5475 | -54.9957 | 65.863 | -57.0557 | -56.868 | -56.9092 | -57.1014 | -56.7673 | -0.077819 | -0.01831 | -0.21515 | 0.65002 | 0.47608 | -0.045776 | 0.55389 | 0.032043 | -0.032043 | -0.009155 | -122.7402 | 0.11444 | 0.25635 | -0.077819 | 0.28839 | -0.045776 | 0.72784 | 122.7585 | 0.14648 | 0.18768 | 122.9553 | 122.9187 | 122.8775 | 122.8867 | -122.9736 | -122.9279 | 122.6807 | 0.15564 | 4.4266 | 2.0279
1043.1719 | 123.1155 | -57.0145 | 65.8356 | -0.15213 | 0.0014761 | 0.065657 | 0.070327 | 0.003151 | 0.0039007 | 0.00414 | -0.016602 | 0.0011023 | 0.00064083 | -0.0067762 | -0.00065151 | -0.0028027 | -0.0033923 | -52.6337 | 65.8218 | -57.0602 | 65.7303 | -56.2775 | -56.9778 | -56.4835 | -54.9179 | 65.8539 | -57.0328 | -56.8451 | -56.8451 | -57.0465 | -56.7307 | -0.045777 | -0.013733 | -0.10528 | 0.737 | 0.53101 | 0.036621 | 0.57678 | 0.082398 | -0.018311 | 0.018311 | -122.6807 | 0.16937 | 0.28381 | -0.032044 | 0.30212 | -0.013733 | 0.78278 | 122.7905 | 0.18768 | 0.18768 | 122.8821 | 122.8867 | 122.8363 | 122.8683 | -122.8958 | -122.8683 | 122.7448 | 0.16937 | 4.3808 | 2.0966
1044.1719 | 123.1064 | -56.955 | 65.8722 | -0.03006 | -0.0010873 | 0.064162 | 0.068832 | -0.0013352 | 0.00048269 | 0.0045672 | 0.059692 | 0.0013159 | 2.8e-08 | -0.0018628 | -0.0023605 | -0.0028027 | 0.0047253 | -52.684 | 65.8356 | -57.0511 | 65.7532 | -56.25 | -56.9 | -56.3873 | -54.8721 | 65.8997 | -57.0099 | -56.7993 | -56.7764 | -56.9733 | -56.7078 | -0.09613 | -0.036621 | -0.11902 | 0.70496 | 0.56763 | 0.054932 | 0.66376 | 0.15106 | -0.054932 | 0.027466 | -122.6715 | 0.17853 | 0.24719 | -0.018311 | 0.30212 | 0.036621 | 0.80109 | 122.8043 | 0.23346 | 0.21057 | 122.8867 | 122.9095 | 122.7905 | 122.8546 | -122.9233 | -122.8821 | 122.7081 | 0.15564 | 4.2709 | 2.0828
1045.1719 | 123.1155 | -57.0053 | 65.8356 | -0.15213 | 0.00019446 | 0.065871 | 0.070327 | 0.004219 | 0.00069649 | 0.0047808 | -0.022705 | 3.4148e-05 | 0.00021363 | 0.00027342 | -0.0019333 | -0.00066648 | -0.00082886 | -52.7481 | 65.8173 | -57.0648 | 65.7486 | -56.282 | -56.9733 | -56.4468 | -54.9408 | 65.8585 | -57.0282 | -56.8268 | -56.8451 | -57.0374 | -56.7215 | -0.059509 | -0.01831 | -0.086975 | 0.72327 | 0.55847 | 0.032043 | 0.61798 | 0.091552 | -0.022888 | 0.022888 | -122.6624 | 0.16022 | 0.28381 | -0.032044 | 0.3067 | -0.009156 | 0.78278 | 122.8134 | 0.18311 | 0.20142 | 122.8821 | 122.8867 | 122.8226 | 122.8638 | -122.9004 | -122.8638 | 122.7539 | 0.17853 | 4.2572 | 2.0645
1046.1719 | 123.1384 | -56.9824 | 65.8447 | -0.11398 | 0.00040806 | 0.064803 | 0.067977 | -0.0041122 | -0.00015811 | 0.0037128 | 0.02002 | -0.00017945 | -0.0010682 | -0.0016492 | -0.0012925 | -0.00088008 | -0.00040166 | -52.7115 | 65.8081 | -57.0602 | 65.7257 | -56.2408 | -56.9138 | -56.4331 | -54.95 | 65.8676 | -57.0374 | -56.8085 | -56.8405 | -57.0282 | -56.7352 | -0.07782 | -0.036622 | -0.11902 | 0.74158 | 0.54932 | 0.068665 | 0.62714 | 0.14649 | -0.054932 | 0.022888 | -122.6532 | 0.14191 | 0.24719 | -0.045776 | 0.30213 | 0.009156 | 0.8194 | 122.7859 | 0.19684 | 0.22888 | 122.8683 | 122.905 | 122.7905 | 122.85 | -122.905 | -122.8821 | 122.7081 | 0.17395 | 4.2709 | 2.0325
1047.1719 | 123.0652 | -57.0099 | 65.8768 | -0.060578 | 0.0016899 | 0.065016 | 0.072036 | 0.0016556 | 0.0021917 | 0.0052082 | -0.056274 | 0.0017431 | 0.003418 | 0.0049732 | -0.0015061 | -0.0017347 | 0.00045294 | -52.9037 | 65.863 | -57.0786 | 65.6479 | -56.369 | -57.0419 | -56.5063 | -55.0598 | 65.8813 | -57.0419 | -56.8771 | -56.9138 | -57.1198 | -56.7856 | -0.068664 | -0.013733 | -0.22888 | 0.64087 | 0.50354 | -0.032043 | 0.5722 | 0.036621 | -0.032043 | 0.004578 | -122.7539 | 0.096131 | 0.2243 | -0.10986 | 0.25635 | -0.07782 | 0.70953 | 122.7264 | 0.12817 | 0.16479 | 122.9416 | 122.9233 | 122.8729 | 122.8912 | -122.9553 | -122.9187 | 122.6578 | 0.13275 | 4.1061 | 1.9501
1048.1719 | 123.1155 | -56.9824 | 65.8493 | -0.075836 | 0.0012625 | 0.065016 | 0.070327 | -0.0021896 | 0.0036871 | 0.0067036 | -0.034912 | 0.00088875 | 0.0014954 | 0.0024096 | -0.0019333 | -0.0010937 | -0.00040166 | -52.9312 | 65.8173 | -57.0511 | 65.7211 | -56.3049 | -56.9824 | -56.4239 | -54.9774 | 65.8722 | -57.0465 | -56.813 | -56.8268 | -57.0419 | -56.7307 | -0.068664 | -0.032043 | -0.12817 | 0.67749 | 0.55847 | 0 | 0.62714 | 0.068664 | -0.064087 | 0.022888 | -122.6624 | 0.15564 | 0.25177 | -0.059509 | 0.31586 | 0.004578 | 0.74615 | 122.7722 | 0.21973 | 0.23346 | 122.8683 | 122.9187 | 122.7997 | 122.8546 | -122.9004 | -122.8958 | 122.7036 | 0.16937 | 4.0512 | 2.005
1049.1719 | 123.1293 | -56.9687 | 65.8539 | -0.083466 | -0.00087374 | 0.06523 | 0.068618 | 0.00251 | 0.0011237 | 0.0017902 | 0.0047608 | 0.0013159 | 0.001709 | -0.0059216 | -0.0015061 | -0.0019483 | 0.0023755 | -52.9266 | 65.8173 | -57.0374 | 65.7257 | -56.4468 | -56.9229 | -56.2912 | -54.9774 | 65.8539 | -57.0282 | -56.8268 | -56.8268 | -57.0374 | -56.7261 | -0.068665 | -0.036621 | -0.12817 | 0.52185 | 0.67749 | 0.045776 | 0.74616 | 0.11444 | -0.059509 | 0 | -122.6807 | 0.14191 | 0.24262 | -0.068665 | 0.30212 | -0.009156 | 0.59052 | 122.7631 | 0.20142 | 0.20142 | 122.8546 | 122.8821 | 122.7859 | 122.8226 | -122.8912 | -122.8821 | 122.6944 | 0.14191 | 4.0421 | 1.9913
1050.1719 | 123.111 | -57.0099 | 65.8722 | -0.13687 | -0.00044654 | 0.064162 | 0.068832 | 0.00080117 | 0.0011237 | 0.0047808 | -0.037964 | -0.00017945 | 0.0014954 | 0.0064684 | -0.00086511 | -0.0030163 | -0.0018971 | -53.0228 | 65.8447 | -57.0831 | 65.6982 | -56.2958 | -56.9687 | -56.4468 | -55.0278 | 65.8722 | -57.019 | -56.8085 | -56.8405 | -57.0602 | -56.7215 | -0.073242 | -0.027465 | -0.17395 | 0.71411 | 0.56305 | 0.041199 | 0.63629 | 0.11444 | -0.009155 | 0 | -122.6807 | 0.16937 | 0.28839 | -0.050354 | 0.29755 | -0.041199 | 0.78735 | 122.7814 | 0.17853 | 0.21057 | 122.9279 | 122.8912 | 122.8546 | 122.8821 | -122.9553 | -122.8912 | 122.7081 | 0.20142 | 3.9871 | 1.9821
1051.1719 | 123.1293 | -56.9916 | 65.8768 | -0.091095 | -0.0023691 | 0.063307 | 0.071181 | -0.00090783 | -0.0010125 | 0.005849 | -0.034912 | 0.00046135 | 0.001709 | -0.0020764 | -0.0025741 | -0.0017347 | 0.0021619 | -53.0869 | 65.8401 | -57.074 | 65.7028 | -56.3095 | -56.9916 | -56.4331 | -55.0644 | 65.8722 | -57.0145 | -56.8405 | -56.8588 | -57.0236 | -56.7261 | -0.082398 | -0.036621 | -0.17395 | 0.68207 | 0.55847 | 0 | 0.64087 | 0.082398 | -0.022888 | -0.004578 | -122.7173 | 0.13275 | 0.2655 | -0.032044 | 0.28839 | -0.009156 | 0.76447 | 122.7768 | 0.15564 | 0.17395 | 122.9141 | 122.8867 | 122.8317 | 122.8638 | -122.9507 | -122.8912 | 122.6944 | 0.15106 | 3.9047 | 1.9272
1052.1719 | 123.1293 | -56.9687 | 65.8401 | -0.10635 | 0.00040806 | 0.063948 | 0.069259 | -0.00090783 | 0.00069649 | 0.0047808 | -0.019653 | 0.00088875 | -0.00042717 | 0.0017688 | 0.0010575 | -0.0010937 | 0.0023755 | -53.0594 | 65.8264 | -57.0282 | 65.744 | -56.2134 | -56.9275 | -56.3736 | -55.0186 | 65.863 | -57.0374 | -56.8954 | -56.7535 | -56.8588 | -56.6437 | -0.059509 | -0.013733 | -0.09613 | 0.75531 | 0.59509 | 0.041199 | 0.6546 | 0.10071 | -0.068665 | 0.022888 | -122.7356 | 0.21515 | 0.32501 | 0.10986 | 0.39368 | 0.17853 | 0.81482 | 122.7722 | 0.28381 | 0.14191 | 122.8546 | 122.9004 | 122.7951 | 122.8317 | -122.8683 | -122.8775 | 122.7127 | 0.073242 | 3.9093 | 1.9501
1053.1719 | 123.0927 | -56.9733 | 65.863 | -0.068207 | -0.00087374 | 0.06523 | 0.072463 | 0.0010148 | 0.0032599 | 0.0060626 | -0.053223 | 0.00088875 | 0.001068 | 0.0032642 | -0.0015061 | -0.0023755 | 0.00088014 | -53.1692 | 65.863 | -57.0831 | 65.6616 | -56.3141 | -56.9962 | -56.4331 | -55.0964 | 65.8859 | -57.0282 | -56.8222 | -56.8634 | -57.0786 | -56.7444 | -0.10986 | 0 | -0.20142 | 0.65918 | 0.54016 | -0.022888 | 0.65002 | 0.086975 | -0.054931 | 0.022888 | -122.6852 | 0.10986 | 0.22888 | -0.10529 | 0.28381 | -0.050354 | 0.76904 | 122.7448 | 0.1648 | 0.20599 | 122.9462 | 122.9141 | 122.8363 | 122.8592 | -122.9462 | -122.8912 | 122.6349 | 0.15106 | 3.804 | 1.8768
1054.1719 | 123.0881 | -56.9824 | 65.863 | -0.075836 | 0.00040806 | 0.06523 | 0.070113 | -0.0041122 | 0.0019781 | 0.0039264 | -0.06543 | 0.0028113 | -0.0014954 | 0.0013416 | -0.0034287 | -0.00066648 | 0.00023934 | -53.2242 | 65.8401 | -57.0694 | 65.6616 | -56.3187 | -57.0053 | -56.4468 | -55.1331 | 65.8813 | -57.0282 | -56.8542 | -56.8954 | -57.106 | -56.7673 | -0.086975 | -0.022888 | -0.20142 | 0.66376 | 0.53558 | -0.022888 | 0.62256 | 0.064087 | -0.045776 | 0.018311 | -122.7173 | 0.086975 | 0.21515 | -0.1236 | 0.26093 | -0.07782 | 0.75073 | 122.731 | 0.13275 | 0.17395 | 122.9095 | 122.9095 | 122.8226 | 122.8638 | -122.9324 | -122.8912 | 122.644 | 0.12817 | 3.7582 | 1.8494
1055.1719 | 123.1476 | -56.9824 | 65.8539 | -0.083466 | -1.9142e-05 | 0.063734 | 0.069472 | 0.001442 | 0.0013373 | 0.0037128 | -0.028809 | 0.00067495 | -0.0012818 | -0.00058098 | -0.00065151 | -0.00066648 | -0.00018806 | -53.1967 | 65.8173 | -57.0648 | 65.7303 | -56.2546 | -56.9778 | -56.3828 | -55.0598 | 65.8493 | -57.0053 | -56.8039 | -56.8176 | -57.0374 | -56.7078 | -0.082397 | -0.036621 | -0.1236 | 0.72784 | 0.59967 | 0.004578 | 0.68207 | 0.086975 | -0.022888 | -0.004578 | -122.6578 | 0.16479 | 0.27466 | -0.054932 | 0.29755 | -0.032044 | 0.81024 | 122.7951 | 0.18768 | 0.20142 | 122.8821 | 122.8546 | 122.7997 | 122.8317 | -122.9187 | -122.8592 | 122.7127 | 0.17853 | 3.7857 | 1.9226
1056.1719 | 123.1247 | -56.9733 | 65.863 | -0.098725 | -0.0015145 | 0.063948 | 0.07289 | -0.00026703 | 0.0028327 | 0.0043536 | -0.034912 | 0.0015295 | 0.0014954 | -0.00464 | -0.0012925 | -0.0023755 | -0.00018806 | -53.27 | 65.8356 | -57.0602 | 65.6982 | -56.25 | -56.9504 | -56.4102 | -55.0873 | 65.8493 | -57.0145 | -56.813 | -56.8359 | -57.0328 | -56.7169 | -0.086975 | -0.027466 | -0.1648 | 0.72327 | 0.56305 | 0.022889 | 0.65002 | 0.10986 | -0.041198 | -0.013733 | -122.6761 | 0.13733 | 0.25635 | -0.059509 | 0.29755 | -0.018311 | 0.81024 | 122.7585 | 0.17853 | 0.20142 | 122.8958 | 122.8638 | 122.8088 | 122.8226 | -122.9233 | -122.8775 | 122.6715 | 0.16022 | 3.7033 | 1.886
1057.1719 | 123.175 | -56.9687 | 65.8493 | -0.11398 | 0.0029715 | 0.064162 | 0.0699 | 0.00016017 | 0.0017645 | 0.0060626 | -0.0074462 | 0.0013159 | 0.00085443 | 0.001128 | 0.00020289 | -0.0023755 | 0.00023934 | -53.2516 | 65.799 | -57.0511 | 65.7532 | -56.1859 | -56.9046 | -56.3416 | -55.0598 | 65.8585 | -57.019 | -56.6803 | -56.8222 | -57.0374 | -56.7123 | -0.082397 | -0.050354 | -0.09613 | 0.78278 | 0.62714 | 0.064087 | 0.70953 | 0.14648 | -0.050354 | 0.009155 | -122.5296 | 0.14648 | 0.25635 | -0.068665 | 0.3067 | -0.018311 | 0.86517 | 122.8043 | 0.19684 | 0.33875 | 122.85 | 122.8775 | 122.7676 | 122.8271 | -122.9004 | -122.8683 | 122.7219 | 0.28839 | 3.717 | 1.9089
1058.1719 | 123.0423 | -57.019 | 65.8264 | -0.075836 | 0.0023307 | 0.065443 | 0.070968 | 0.0035782 | 0.0028327 | 0.0032856 | -0.019653 | 0.0015295 | 2.8e-08 | -0.00036738 | -0.0027877 | -0.00045288 | -0.0051013 | -53.302 | 65.8173 | -57.0328 | 65.7578 | -56.1951 | -56.8954 | -56.3187 | -55.069 | 65.8493 | -56.9916 | -56.781 | -56.8268 | -57.0145 | -56.6849 | -0.013733 | -0.009155 | -0.068665 | 0.82398 | 0.70038 | 0.1236 | 0.71411 | 0.13733 | 0.027466 | 0.022888 | -122.6074 | 0.19226 | 0.33417 | 0.004578 | 0.3067 | -0.022888 | 0.83771 | 122.7905 | 0.16479 | 0.21057 | 122.85 | 122.8409 | 122.8363 | 122.8683 | -122.8592 | -122.818 | 122.7768 | 0.23804 | 3.717 | 1.9501
1059.1719 | 123.0835 | -56.9733 | 65.8447 | -0.12924 | 0.0031851 | 0.062239 | 0.070754 | -0.00069423 | 0.00091009 | 0.0039264 | 0.001709 | 0.00024775 | 0.00042723 | -0.003999 | -0.00086511 | -0.0021619 | 0.0017345 | -53.2883 | 65.799 | -57.0328 | 65.7715 | -56.1676 | -56.8863 | -56.3095 | -55.0827 | 65.863 | -57.0007 | -56.8039 | -56.8085 | -57.0145 | -56.7169 | -0.059509 | -0.045777 | -0.073243 | 0.80566 | 0.66376 | 0.086975 | 0.72327 | 0.14648 | -0.027465 | 0.01831 | -122.6486 | 0.16479 | 0.25635 | -0.041198 | 0.28381 | -0.013733 | 0.86517 | 122.8043 | 0.19226 | 0.19684 | 122.8317 | 122.8638 | 122.7722 | 122.8363 | -122.8775 | -122.8455 | 122.7448 | 0.16937 | 3.685 | 1.8906
1060.1719 | 123.0515 | -56.987 | 65.8859 | -0.091095 | 0.0012625 | 0.065443 | 0.073104 | 0.00251 | 0.0043281 | 0.0052082 | -0.050171 | 0.0028113 | 0.001068 | -0.0018628 | -0.00065151 | -2.5678e-05 | 0.0021619 | -53.3844 | 65.8951 | -57.0694 | 65.657 | -56.2866 | -56.9916 | -56.4239 | -55.2017 | 65.918 | -57.0465 | -56.8726 | -56.8863 | -57.106 | -56.7856 | -0.082397 | 0.009156 | -0.22888 | 0.70038 | 0.56305 | -0.004577 | 0.64545 | 0.07782 | -0.059509 | 0.032044 | -122.7585 | 0.10071 | 0.20142 | -0.11902 | 0.26093 | -0.059509 | 0.78278 | 122.7264 | 0.16022 | 0.17395 | 122.9645 | 122.9645 | 122.8821 | 122.905 | -122.9553 | -122.9324 | 122.644 | 0.11444 | 3.6026 | 1.7853
1061.1719 | 123.0423 | -56.9916 | 65.8905 | -0.11398 | 0.00083526 | 0.06288 | 0.072463 | -0.0015488 | 0.0021917 | 0.00414 | -0.034912 | 0.00046135 | 0.0014954 | 0.0015552 | -0.0017197 | -0.0023755 | 0.0013073 | -53.421 | 65.8859 | -57.0602 | 65.6479 | -56.282 | -56.987 | -56.3873 | -55.2109 | 65.918 | -57.0236 | -56.8726 | -56.9 | -57.1152 | -56.8085 | -0.068665 | -0.004578 | -0.24262 | 0.70953 | 0.60425 | 0.004577 | 0.67291 | 0.073242 | -0.032044 | 0.027466 | -122.7631 | 0.091553 | 0.1831 | -0.1236 | 0.21515 | -0.091552 | 0.7782 | 122.7081 | 0.1236 | 0.15106 | 122.9462 | 122.9416 | 122.8775 | 122.9095 | -122.9507 | -122.9141 | 122.6395 | 0.11902 | 3.5706 | 1.7807
1062.1719 | 123.1476 | -56.9595 | 65.8722 | -0.098725 | -0.00087374 | 0.065443 | 0.070113 | 0.0029374 | 0.0030463 | 0.0062762 | 0.0078126 | 0.00046135 | -0.0021362 | -0.0031446 | -0.0017197 | -0.0019483 | -0.0012561 | -53.3752 | 65.8035 | -57.0374 | 65.744 | -56.1676 | -56.8863 | -56.3049 | -55.0964 | 65.8813 | -57.0007 | -56.7581 | -56.8405 | -56.9733 | -56.6666 | -0.07782 | -0.068664 | -0.12817 | 0.79193 | 0.6546 | 0.073242 | 0.73242 | 0.15106 | -0.041198 | 0.009156 | -122.6303 | 0.11902 | 0.29297 | -0.013733 | 0.33417 | 0.027465 | 0.86975 | 122.7814 | 0.16022 | 0.24261 | 122.8409 | 122.8821 | 122.7631 | 122.8409 | -122.9095 | -122.8729 | 122.7036 | 0.20142 | 3.5843 | 1.8631
1063.1719 | 123.1567 | -56.9687 | 65.8722 | -0.10635 | -1.9142e-05 | 0.06523 | 0.069259 | 0.00080117 | 0.00026909 | 0.0056354 | -0.010498 | -0.00082025 | 0.00064083 | -0.0014356 | 0.00084389 | -0.00088008 | 0.0028027 | -53.421 | 65.8081 | -57.019 | 65.7578 | -56.163 | -56.8726 | -56.2912 | -55.101 | 65.8905 | -57.0099 | -56.694 | -57.0282 | -57.0969 | -56.6895 | -0.050354 | -0.064087 | -0.11444 | 0.80566 | 0.67749 | 0.09613 | 0.72784 | 0.14648 | -0.041199 | 0.018311 | -122.5662 | -0.059509 | 0.27924 | -0.12817 | 0.32043 | -0.086975 | 0.85602 | 122.7768 | -0.01831 | 0.31586 | 122.8271 | 122.9004 | 122.7768 | 122.8592 | -122.8912 | -122.8821 | 122.7264 | 0.27466 | 3.5477 | 1.8677
1064.1719 | 123.1293 | -56.9733 | 65.8539 | -0.12924 | 0.00040806 | 0.063094 | 0.07289 | -5.343e-05 | 0.0036871 | 0.0062762 | 0.013916 | 0.00024775 | 0.00085443 | 0.0030506 | -0.0027877 | 0.00082892 | 0.00045294 | -53.4531 | 65.8356 | -57.0419 | 65.7578 | -56.1676 | -56.8726 | -56.2729 | -55.1147 | 65.8951 | -57.0282 | -56.7764 | -56.8222 | -57.019 | -56.7032 | -0.068664 | -0.018311 | -0.096131 | 0.80566 | 0.70038 | 0.10071 | 0.76904 | 0.16937 | -0.054931 | 0.041199 | -122.6303 | 0.15106 | 0.27008 | -0.045776 | 0.32501 | 0.009155 | 0.87433 | 122.7997 | 0.20599 | 0.25177 | 122.8775 | 122.9233 | 122.8088 | 122.8683 | -122.8958 | -122.8821 | 122.731 | 0.19684 | 3.5202 | 1.8585
1065.1719 | 123.0515 | -56.9824 | 65.9088 | -0.022431 | -0.00044654 | 0.065016 | 0.071181 | 0.0027238 | 0.0032599 | 0.0071308 | -0.056274 | 0.0019567 | -0.0014954 | 0.0034778 | -0.0019333 | -0.0021619 | -0.00040166 | -53.5309 | 65.863 | -57.0602 | 65.6616 | -56.2637 | -56.9687 | -56.3919 | -55.2246 | 65.8997 | -57.0374 | -56.8405 | -56.868 | -57.0877 | -56.7673 | -0.07782 | -0.045776 | -0.24719 | 0.71869 | 0.59051 | 0.013733 | 0.66833 | 0.091553 | -0.054932 | -0.009155 | -122.7493 | 0.11444 | 0.21515 | -0.10529 | 0.27008 | -0.050354 | 0.79651 | 122.7219 | 0.16937 | 0.19684 | 122.9233 | 122.937 | 122.8455 | 122.8821 | -122.9691 | -122.9462 | 122.644 | 0.14191 | 3.4515 | 1.7578
1066.1719 | 123.1201 | -56.9504 | 65.8539 | -0.098725 | 0.0014761 | 0.063307 | 0.066054 | -5.343e-05 | 0.0049689 | 0.0045672 | 0.044434 | -0.00082025 | -0.00042717 | 0.0032642 | -0.0010787 | -0.0034437 | -0.0040333 | -53.4988 | 65.8401 | -57.0374 | 65.7166 | -56.0257 | -56.6711 | -56.2958 | -55.0873 | 65.8859 | -56.9962 | -56.781 | -56.7902 | -56.9916 | -56.7032 | -0.086976 | -0.013733 | -0.13733 | 0.92468 | 0.6546 | 0.27923 | 0.74158 | 0.36621 | -0.045777 | 0.032043 | -122.6349 | 0.16022 | 0.24719 | -0.041199 | 0.29297 | 0.004578 | 1.0117 | 122.7539 | 0.20599 | 0.21515 | 122.8775 | 122.8821 | 122.7905 | 122.8363 | -122.8912 | -122.85 | 122.6669 | 0.16937 | 3.4515 | 1.8631
1067.1719 | 123.1018 | -56.9733 | 65.8585 | -0.10635 | -0.00023294 | 0.064803 | 0.070327 | 0.0010148 | 0.0024053 | 0.0056354 | -0.03186 | 0.00046135 | 0.001068 | 0.0028368 | -0.0032151 | 0.00082892 | -0.00061526 | -53.5812 | 65.8447 | -57.0328 | 65.7211 | -56.2317 | -56.8954 | -56.3416 | -55.1559 | 65.8722 | -57.0099 | -56.7902 | -56.8268 | -57.0236 | -56.6849 | -0.059509 | -0.013732 | -0.13733 | 0.74158 | 0.63171 | 0.07782 | 0.69122 | 0.13733 | -0.036621 | 0.013733 | -122.6486 | 0.14648 | 0.28839 | -0.050354 | 0.32501 | -0.013733 | 0.80109 | 122.7539 | 0.18311 | 0.21973 | 122.8775 | 122.8821 | 122.818 | 122.8455 | -122.8912 | -122.8683 | 122.6944 | 0.18311 | 3.392 | 1.8173
1068.1719 | 123.0331 | -57.0145 | 65.8813 | -0.045319 | -1.9142e-05 | 0.063734 | 0.071181 | -5.343e-05 | 0.0019781 | 0.0067036 | -0.041016 | 0.0028113 | 2.8e-08 | 5.9824e-05 | -1.0706e-05 | -0.0017347 | 0.0013073 | -53.6453 | 65.8997 | -57.0374 | 65.6616 | -56.2958 | -56.987 | -56.4011 | -55.2612 | 65.9225 | -57.0557 | -56.8588 | -56.8954 | -57.1289 | -56.7902 | -0.022889 | 0.01831 | -0.21973 | 0.71869 | 0.6134 | 0.027465 | 0.63629 | 0.050354 | -0.041199 | 0.041198 | -122.7402 | 0.11902 | 0.2243 | -0.11444 | 0.2655 | -0.073242 | 0.74158 | 122.699 | 0.16022 | 0.19684 | 122.937 | 122.9782 | 122.9141 | 122.937 | -122.9187 | -122.937 | 122.6761 | 0.15564 | 3.3691 | 1.7532
1069.1719 | 123.1888 | -56.955 | 65.8585 | -0.15976 | -1.9142e-05 | 0.062239 | 0.070541 | -0.001976 | 0.0030463 | 0.0060626 | -0.025757 | -0.0016749 | 0.001709 | -0.0018628 | -0.0032151 | -0.0017347 | -0.0012561 | -53.5812 | 65.8447 | -57.0145 | 65.7578 | -56.1859 | -56.8497 | -56.3095 | -55.1147 | 65.8768 | -56.9916 | -56.7947 | -56.8588 | -57.2571 | -56.7444 | -0.059509 | -0.013732 | -0.10071 | 0.76904 | 0.64545 | 0.10529 | 0.70496 | 0.16479 | -0.036621 | 0.018311 | -122.6532 | 0.09613 | 0.21057 | -0.30212 | 0.24719 | -0.2655 | 0.82855 | 122.7722 | 0.13275 | 0.19684 | 122.8592 | 122.8683 | 122.7997 | 122.8317 | -122.8729 | -122.85 | 122.7127 | 0.16022 | 3.3737 | 1.8402
1070.1719 | 123.1064 | -56.9778 | 65.8585 | -0.16739 | 0.00062166 | 0.063094 | 0.070754 | -0.001976 | 0.0030463 | 0.0054218 | -0.019653 | 3.4148e-05 | 0.00021363 | -0.00229 | -0.00086511 | -0.0015211 | 0.0015209 | -53.627 | 65.8218 | -57.0328 | 65.744 | -56.1951 | -56.8359 | -56.2958 | -55.1376 | 65.8539 | -57.019 | -56.7719 | -56.8039 | -57.019 | -56.6895 | -0.054932 | -0.036621 | -0.11444 | 0.78278 | 0.68207 | 0.14191 | 0.737 | 0.19684 | -0.041199 | -0.004577 | -122.6303 | 0.17395 | 0.28839 | -0.041199 | 0.32959 | 0 | 0.83771 | 122.7768 | 0.21515 | 0.24719 | 122.8546 | 122.8729 | 122.7997 | 122.8317 | -122.8912 | -122.8775 | 122.7219 | 0.20599 | 3.3508 | 1.8402
1071.1719 | 123.0698 | -56.9962 | 65.8905 | -0.083466 | 0.0021171 | 0.064162 | 0.070754 | -0.0015488 | -0.0010125 | 0.0039264 | -0.041016 | 0.00088875 | 0.0014954 | -0.0037854 | -0.00043791 | -2.5678e-05 | 0.0010937 | -53.7094 | 65.863 | -57.0648 | 65.6754 | -56.2866 | -56.9458 | -56.3828 | -55.2292 | 65.8997 | -57.019 | -56.8451 | -56.8726 | -57.0877 | -56.7535 | -0.068664 | -0.027466 | -0.21515 | 0.70953 | 0.6134 | 0.050354 | 0.68207 | 0.11902 | -0.022888 | 0.009155 | -122.7356 | 0.1236 | 0.24262 | -0.091553 | 0.2655 | -0.068665 | 0.7782 | 122.7402 | 0.14648 | 0.17395 | 122.9279 | 122.9187 | 122.8592 | 122.8958 | -122.9553 | -122.9095 | 122.6715 | 0.15106 | 3.2867 | 1.767
1072.1719 | 123.1018 | -56.955 | 65.8676 | -0.10635 | -0.0030099 | 0.064803 | 0.070327 | -0.0011214 | 0.0026191 | 0.0073444 | -0.025757 | -0.0016749 | -0.00085457 | 0.0015552 | -0.0015061 | -0.00045288 | -0.00061526 | -53.7094 | 65.8356 | -57.0419 | 65.7257 | -56.2088 | -56.8771 | -56.3416 | -55.1422 | 65.8722 | -56.9916 | -56.781 | -56.8176 | -57.0236 | -56.6986 | -0.086975 | -0.032044 | -0.14191 | 0.74616 | 0.6134 | 0.07782 | 0.70038 | 0.16479 | -0.036621 | 0.004577 | -122.6486 | 0.13733 | 0.25635 | -0.068665 | 0.29297 | -0.032044 | 0.83313 | 122.7676 | 0.17395 | 0.21057 | 122.8775 | 122.8638 | 122.7905 | 122.8271 | -122.9095 | -122.8592 | 122.6807 | 0.17395 | 3.2455 | 1.8127
1073.1719 | 123.1155 | -56.9458 | 65.8859 | -0.12161 | 0.00062166 | 0.064162 | 0.071609 | 0.0022964 | 0.0028327 | 0.0052082 | 0.0047608 | 0.00067495 | -0.00021357 | 0.00091422 | -0.0012925 | -0.00066648 | 2.554e-05 | -53.6911 | 65.8218 | -57.0236 | 65.7623 | -56.1722 | -56.8542 | -56.2683 | -55.0552 | 65.8539 | -57.019 | -56.7856 | -56.781 | -56.9687 | -56.6803 | -0.07782 | -0.064087 | -0.1236 | 0.77362 | 0.67749 | 0.091553 | 0.75531 | 0.16937 | -0.073242 | -0.032043 | -122.6715 | 0.1648 | 0.2655 | -0.022888 | 0.33875 | 0.050354 | 0.85144 | 122.7859 | 0.23804 | 0.23346 | 122.8455 | 122.8729 | 122.7676 | 122.7997 | -122.9095 | -122.905 | 122.7081 | 0.16022 | 3.2547 | 1.8906
1074.1719 | 123.0103 | -57.0053 | 65.8859 | -0.045319 | -0.00087374 | 0.062666 | 0.072036 | -0.00048063 | 0.0015509 | 0.0077716 | -0.056274 | 0.0021703 | 0.001709 | 0.0049732 | -0.0017197 | -0.00088008 | -0.00082886 | -53.6453 | 65.9042 | -57.0282 | 65.6845 | -56.2592 | -56.987 | -56.3873 | -55.2704 | 65.918 | -57.0511 | -56.868 | -56.9046 | -57.1335 | -56.7947 | -0.022888 | 0.018311 | -0.20142 | 0.74616 | 0.61798 | 0.01831 | 0.64087 | 0.041198 | -0.045776 | 0.032044 | -122.7539 | 0.10071 | 0.21057 | -0.12817 | 0.25635 | -0.082398 | 0.76904 | 122.7127 | 0.14648 | 0.1831 | 122.9324 | 122.9691 | 122.9095 | 122.9233 | -122.9141 | -122.937 | 122.6898 | 0.13733 | 3.36 | 1.7349
1075.1719 | 123.0377 | -56.987 | 65.9088 | -0.098725 | -0.0019417 | 0.064589 | 0.071395 | -0.0017624 | 0.0013373 | 0.0073444 | -0.059326 | 0.00024775 | 0.00042723 | -0.0010084 | -0.0017197 | -0.0017347 | 0.0045117 | -53.8055 | 65.863 | -57.0511 | 65.6982 | -56.4102 | -56.8863 | -56.2958 | -55.2658 | 65.95 | -57.0236 | -56.8771 | -56.9138 | -57.1152 | -56.781 | -0.064086 | -0.045776 | -0.21057 | 0.57678 | 0.69122 | 0.10071 | 0.75531 | 0.16479 | -0.036621 | 0.041199 | -122.7859 | 0.073243 | 0.20599 | -0.12817 | 0.24262 | -0.091552 | 0.64087 | 122.7493 | 0.10986 | 0.14648 | 122.9141 | 122.9736 | 122.85 | 122.937 | -122.9599 | -122.9324 | 122.6852 | 0.10986 | 3.1815 | 1.7212
1076.1719 | 123.1247 | -56.9458 | 65.8493 | -0.060578 | 0.00062166 | 0.065871 | 0.066909 | -0.0021896 | 0.0015509 | 0.0049946 | 0.02002 | 0.00088875 | 0.00021363 | 0.00091422 | 0.0021255 | -0.0021619 | -0.0018971 | -53.7781 | 65.8218 | -57.0053 | 65.7394 | -56.1722 | -56.7673 | -56.2225 | -55.1147 | 65.8813 | -56.9962 | -56.7673 | -56.7993 | -57.0053 | -56.6895 | -0.059509 | -0.027466 | -0.10986 | 0.77362 | 0.72327 | 0.17853 | 0.78278 | 0.23804 | -0.050354 | 0.032044 | -122.6166 | 0.14649 | 0.25635 | -0.059509 | 0.3067 | -0.009155 | 0.83313 | 122.7448 | 0.19684 | 0.22888 | 122.8271 | 122.8775 | 122.7676 | 122.8271 | -122.8546 | -122.8455 | 122.6852 | 0.17853 | 3.1677 | 1.8311
1077.1719 | 123.1201 | -56.9641 | 65.8722 | -0.068207 | -0.0010873 | 0.063948 | 0.070113 | -0.00090783 | 0.0032599 | 0.0039264 | -0.022705 | 0.0023839 | -0.0014954 | 0.0026232 | -0.0030013 | -0.00023928 | 0.00023934 | -53.8055 | 65.8356 | -57.0465 | 65.7349 | -56.1996 | -56.8771 | -56.2683 | -55.1559 | 65.8813 | -57.0053 | -56.7947 | -56.7993 | -57.0374 | -56.6986 | -0.082398 | -0.036621 | -0.13733 | 0.76447 | 0.6958 | 0.086975 | 0.7782 | 0.16937 | -0.041199 | 0.009156 | -122.6669 | 0.1648 | 0.2655 | -0.073243 | 0.3067 | -0.032044 | 0.84686 | 122.7814 | 0.20599 | 0.21057 | 122.8821 | 122.8867 | 122.7997 | 122.8455 | -122.9187 | -122.8775 | 122.699 | 0.16937 | 3.1586 | 1.8082
1078.1719 | 122.9965 | -57.0053 | 65.8813 | -0.16739 | 0.0016899 | 0.062666 | 0.070327 | 0.0027238 | 0.0032599 | 0.0049946 | -0.077637 | -0.00017945 | 0.0012818 | -0.0025036 | -0.0010787 | -0.0013073 | 0.00088014 | -53.7918 | 65.9134 | -57.0419 | 65.6479 | -56.2683 | -56.955 | -56.3644 | -55.2521 | 65.9225 | -57.0007 | -56.8726 | -56.8954 | -57.1243 | -56.7902 | -0.036621 | 0.032043 | -0.23346 | 0.737 | 0.64087 | 0.050354 | 0.67749 | 0.086975 | 0.004578 | 0.041198 | -122.7539 | 0.10986 | 0.21515 | -0.11902 | 0.21057 | -0.1236 | 0.77362 | 122.6898 | 0.10529 | 0.12817 | 122.9553 | 122.9233 | 122.9187 | 122.9279 | -122.9233 | -122.8821 | 122.6532 | 0.13275 | 3.2135 | 1.7532
1079.1719 | 123.0789 | -56.9778 | 65.8722 | -0.12161 | -0.0010873 | 0.063734 | 0.071609 | 0.0018692 | 0.0017645 | 0.0052082 | -0.016602 | 0.0028113 | 0.0023498 | 0.0026232 | -0.0012925 | -0.00066648 | 0.0051525 | -53.8742 | 65.8676 | -57.0236 | 65.6662 | -56.25 | -56.9183 | -56.3232 | -55.2292 | 65.8997 | -57.0099 | -56.8176 | -56.8451 | -57.0511 | -56.7352 | -0.045777 | -0.004577 | -0.20599 | 0.72784 | 0.6546 | 0.059509 | 0.70038 | 0.10529 | -0.032044 | 0.027466 | -122.6898 | 0.13275 | 0.24262 | -0.073242 | 0.27466 | -0.041198 | 0.77362 | 122.6898 | 0.16479 | 0.19226 | 122.8912 | 122.9095 | 122.8455 | 122.8775 | -122.8958 | -122.8821 | 122.644 | 0.16022 | 3.1036 | 1.7487
1080.1719 | 123.1384 | -56.9595 | 65.8356 | -0.13687 | -0.00087374 | 0.065657 | 0.070113 | 0.0020828 | 0.0011237 | 0.0062762 | 0.0047608 | 0.00024775 | 0.00064083 | 0.0028368 | 0.00041649 | -0.0017347 | -0.0023243 | -53.8513 | 65.863 | -57.0419 | 65.7257 | -56.1676 | -56.8451 | -56.2546 | -55.1559 | 65.8539 | -57.0053 | -56.7719 | -56.7993 | -57.0236 | -56.6803 | -0.082397 | 0.027466 | -0.10986 | 0.79193 | 0.70496 | 0.11444 | 0.78735 | 0.19684 | -0.045776 | 0.018311 | -122.6074 | 0.16022 | 0.27924 | -0.064087 | 0.32501 | -0.018311 | 0.87433 | 122.7676 | 0.20599 | 0.23346 | 122.905 | 122.8592 | 122.8226 | 122.8134 | -122.8775 | -122.8409 | 122.6852 | 0.18768 | 3.1082 | 1.8036
1081.1719 | 122.9874 | -56.987 | 65.9454 | -0.083466 | 0.00083526 | 0.063521 | 0.073531 | 0.00016017 | -0.00058531 | 0.0064898 | -0.059326 | 0.0028113 | -0.0010682 | -0.0014356 | -0.0017197 | -0.0017347 | 0.0036571 | -53.9246 | 65.863 | -57.0465 | 65.6204 | -56.2912 | -56.955 | -56.3461 | -55.2887 | 65.918 | -57.0465 | -56.8863 | -56.9366 | -57.0511 | -56.7398 | -0.059509 | -0.082398 | -0.32501 | 0.6958 | 0.64087 | 0.032044 | 0.70038 | 0.091553 | -0.059509 | -0.027466 | -122.8317 | 0.050354 | 0.24719 | -0.064086 | 0.3067 | -0.004577 | 0.75531 | 122.6669 | 0.10986 | 0.16022 | 122.9095 | 122.9645 | 122.85 | 122.905 | -122.9919 | -122.9919 | 122.6074 | 0.10071 | 3.0624 | 1.6983
1082.1719 | 122.9279 | -57.0236 | 65.8951 | -0.075836 | -0.0015145 | 0.063094 | 0.071609 | 0.0022964 | 0.0028327 | 0.0045672 | -0.053223 | 0.0013159 | 0.0032044 | 0.0030506 | 0.0016983 | -0.0045117 | 0.00088014 | -53.92 | 65.8859 | -57.0419 | 65.6296 | -56.3141 | -56.9504 | -56.369 | -55.3345 | 65.9225 | -57.019 | -56.8726 | -56.9321 | -57.3486 | -57.0145 | -0.01831 | -0.009156 | -0.2655 | 0.70953 | 0.6546 | 0.073243 | 0.67291 | 0.091553 | 0.004578 | 0.027465 | -122.7676 | 0.091553 | 0.009156 | -0.32501 | 0.004578 | -0.32959 | 0.72784 | 122.6715 | 0.086975 | 0.14648 | 122.9279 | 122.9416 | 122.9095 | 122.9462 | -122.937 | -122.9141 | 122.6532 | 0.15106 | 3.1036 | 1.6891
1083.1719 | 123.0927 | -56.9687 | 65.863 | -0.098725 | 0.00062166 | 0.066512 | 0.072036 | -0.0011214 | -0.00015811 | 0.0067036 | -0.03186 | 0.0011023 | -0.00064077 | -0.00079478 | -0.0017197 | -0.0021619 | 0.0013073 | -53.9429 | 65.8722 | -57.0511 | 65.6708 | -56.2317 | -56.8954 | -56.3141 | -55.22 | 65.8905 | -57.0007 | -56.8222 | -56.8314 | -57.0694 | -56.7444 | -0.082397 | 0.009155 | -0.19226 | 0.737 | 0.6546 | 0.073242 | 0.737 | 0.15564 | -0.032043 | 0.027466 | -122.6852 | 0.13733 | 0.2243 | -0.10071 | 0.25635 | -0.068665 | 0.8194 | 122.7219 | 0.16937 | 0.17853 | 122.9233 | 122.8912 | 122.8409 | 122.8592 | -122.9141 | -122.8638 | 122.6395 | 0.14648 | 3.0258 | 1.7487
1084.1719 | 122.9874 | -56.9916 | 65.8859 | -0.091095 | 0.0023307 | 0.06288 | 0.074813 | -0.00026703 | 0.0015509 | 0.007558 | -0.059326 | 0.0021703 | -0.00042717 | -0.0065626 | -0.0015061 | -0.0015211 | 0.00088014 | -53.952 | 65.8539 | -57.0465 | 65.4465 | -56.543 | -56.5979 | -56.1035 | -55.2521 | 65.9271 | -57.0282 | -56.8771 | -56.9 | -57.1243 | -56.7947 | -0.054932 | -0.032043 | -0.43945 | 0.44861 | 0.88806 | 0.39368 | 0.94299 | 0.44861 | -0.036621 | 0.041199 | -122.7631 | 0.091553 | 0.19684 | -0.13275 | 0.23346 | -0.096131 | 0.50354 | 122.493 | 0.12817 | 0.15106 | 122.9004 | 122.9553 | 122.8455 | 122.9187 | -122.9324 | -122.9141 | 122.438 | 0.11444 | 3.0396 | 1.7395
1085.1719 | 123.0377 | -56.9824 | 65.8768 | -0.083466 | 0.0012625 | 0.061812 | 0.071395 | 0.00080117 | 0.0039007 | 0.0060626 | -0.019653 | 0.0034521 | 0.00042723 | -0.002931 | 0.00084389 | -0.00088008 | 0.0030163 | -53.9932 | 65.8951 | -57.0648 | 65.6525 | -56.2454 | -56.9229 | -56.3095 | -55.2795 | 65.9134 | -57.0419 | -56.8497 | -56.8863 | -57.0877 | -56.7719 | -0.082397 | 0.018311 | -0.2243 | 0.737 | 0.67291 | 0.059509 | 0.75531 | 0.14191 | -0.059509 | 0.036621 | -122.7264 | 0.09613 | 0.21057 | -0.10529 | 0.27008 | -0.045777 | 0.8194 | 122.7173 | 0.15564 | 0.19226 | 122.9599 | 122.9553 | 122.8775 | 122.8958 | -122.9416 | -122.9187 | 122.6349 | 0.13275 | 2.9892 | 1.7029
1086.1719 | 123.0377 | -56.9962 | 65.8859 | -0.1445 | 0.00083526 | 0.063094 | 0.071609 | 0.0022964 | 0.0030463 | 0.0067036 | -0.022705 | 0.0028113 | 0.0025634 | -0.0010084 | -0.0012925 | -0.0013073 | 0.0021619 | -53.9429 | 65.9042 | -57.0465 | 65.6433 | -56.2592 | -56.9092 | -56.3004 | -55.2979 | 65.918 | -57.0236 | -56.8726 | -56.8863 | -57.1243 | -56.7764 | -0.050354 | 0.018311 | -0.24261 | 0.737 | 0.6958 | 0.086975 | 0.74616 | 0.13733 | -0.027466 | 0.032044 | -122.7585 | 0.10986 | 0.21973 | -0.12817 | 0.24719 | -0.10071 | 0.78735 | 122.6898 | 0.13733 | 0.15106 | 122.9507 | 122.9416 | 122.9004 | 122.9141 | -122.9324 | -122.9095 | 122.6395 | 0.1236 | 3.0533 | 1.6983
1087.1719 | 123.0103 | -56.987 | 65.8768 | 0.1149 | -0.0013009 | 0.064589 | 0.072036 | 0.00058737 | 0.0013373 | 0.0047808 | -0.0074462 | -0.0010339 | 0.0038452 | -0.0042126 | -1.0706e-05 | -0.0015211 | -0.0014697 | -54.0756 | 65.8905 | -57.0465 | 65.6662 | -56.2546 | -56.9504 | -56.2912 | -55.3116 | 65.918 | -57.019 | -56.868 | -56.9092 | -57.1335 | -56.7856 | -0.059509 | 0.013733 | -0.21057 | 0.73242 | 0.6958 | 0.036622 | 0.75531 | 0.096131 | -0.032043 | 0.041199 | -122.7448 | 0.07782 | 0.20142 | -0.14648 | 0.23346 | -0.11444 | 0.79193 | 122.7127 | 0.10986 | 0.15106 | 122.937 | 122.937 | 122.8775 | 122.905 | -122.9233 | -122.8958 | 122.6532 | 0.11902 | 2.9114 | 1.6754
1088.1719 | 122.9828 | -57.0145 | 65.8813 | -0.12924 | 0.0019035 | 0.064375 | 0.073318 | 0.00058737 | 0.0026191 | 0.0071308 | -0.010498 | 0.00046135 | -0.00042717 | 0.0026232 | -0.0012925 | -0.0025891 | -0.0010425 | -54.0161 | 65.8768 | -57.0145 | 65.6433 | -56.2454 | -56.9183 | -56.3232 | -55.3299 | 65.9363 | -57.0236 | -56.9046 | -56.9412 | -57.1747 | -56.8314 | 0 | -0.004578 | -0.23804 | 0.76904 | 0.69122 | 0.09613 | 0.69122 | 0.09613 | -0.009156 | 0.054931 | -122.7859 | 0.073242 | 0.18311 | -0.16022 | 0.19226 | -0.15106 | 0.76904 | 122.6578 | 0.082398 | 0.11902 | 122.8912 | 122.9599 | 122.8912 | 122.9507 | -122.8958 | -122.905 | 122.6578 | 0.10986 | 2.9984 | 1.6846
1089.1719 | 122.9691 | -56.9962 | 65.8859 | -0.10635 | 0.0014761 | 0.063734 | 0.073531 | -0.0049668 | 0.0017645 | 0.0064898 | -0.025757 | 0.0028113 | 0.0021362 | 0.0017688 | -0.0012925 | -0.00045288 | -0.0042469 | -54.0115 | 65.9088 | -57.0511 | 65.6433 | -56.2271 | -56.9 | -56.3049 | -55.3345 | 65.918 | -57.0099 | -56.8771 | -56.9275 | -57.1518 | -56.8222 | -0.054931 | 0.022888 | -0.24261 | 0.76904 | 0.69122 | 0.096131 | 0.74615 | 0.15106 | -0.013733 | 0.032044 | -122.7631 | 0.068665 | 0.17395 | -0.15564 | 0.18768 | -0.14191 | 0.82397 | 122.6944 | 0.082398 | 0.13275 | 122.9599 | 122.9279 | 122.905 | 122.9141 | -122.937 | -122.8958 | 122.6395 | 0.11902 | 2.9846 | 1.6617
1090.1719 | 123.0423 | -56.9687 | 65.8813 | -0.083466 | 0.00019446 | 0.064162 | 0.070968 | 0.0016556 | 0.0021917 | 0.0052082 | -0.01355 | 0.0017431 | 0.0012818 | 0.0036914 | -0.00022431 | -0.0030163 | -0.0016833 | -54.0253 | 65.8676 | -57.0648 | 65.6433 | -56.2088 | -56.8909 | -56.282 | -55.2933 | 65.9088 | -57.0374 | -56.8359 | -56.8909 | -57.0877 | -56.7764 | -0.09613 | -0.013733 | -0.23804 | 0.75989 | 0.68665 | 0.07782 | 0.78278 | 0.17395 | -0.068665 | 0.027465 | -122.7173 | 0.07782 | 0.19226 | -0.11902 | 0.26093 | -0.050354 | 0.85602 | 122.7081 | 0.14648 | 0.20142 | 122.9324 | 122.9462 | 122.8363 | 122.8775 | -122.9462 | -122.9187 | 122.612 | 0.13275 | 2.9434 | 1.6754
1091.1719 | 123.0377 | -57.0099 | 65.9042 | -0.15976 | -0.0019417 | 0.061171 | 0.07225 | 0.0022964 | 0.0041143 | 0.0054218 | -0.047119 | 0.0034521 | 0.001709 | 0.0045458 | -0.0010787 | -0.0019483 | -0.0029651 | -54.039 | 65.8859 | -57.0557 | 65.6525 | -56.2088 | -56.9046 | -56.2958 | -55.275 | 65.9088 | -57.019 | -56.8451 | -56.8863 | -57.1106 | -56.7764 | -0.045776 | -0.018311 | -0.25177 | 0.80109 | 0.71411 | 0.10529 | 0.75989 | 0.15106 | -0.009155 | 0.004577 | -122.7493 | 0.1236 | 0.23346 | -0.10071 | 0.24262 | -0.091553 | 0.84686 | 122.7081 | 0.13275 | 0.17395 | 122.9416 | 122.9279 | 122.8958 | 122.9187 | -122.9599 | -122.9233 | 122.6624 | 0.16479 | 2.9709 | 1.7349
1092.1719 | 123.0881 | -57.0236 | 65.9409 | -0.10635 | -0.00066014 | 0.063948 | 0.071395 | 0.0033646 | -0.00015811 | 0.0045672 | -0.050171 | 0.0023839 | 2.8e-08 | 0.00091422 | -1.0706e-05 | -0.00066648 | 0.0017345 | -54.0482 | 65.8951 | -57.0694 | 65.6204 | -56.25 | -56.9504 | -56.3049 | -55.3482 | 65.9225 | -56.9962 | -56.8634 | -56.8634 | -57.5089 | -57.0419 | -0.045776 | -0.045776 | -0.32043 | 0.77362 | 0.71869 | 0.073243 | 0.76447 | 0.11902 | 0.027466 | -0.018311 | -122.8043 | 0.16022 | -0.01831 | -0.48523 | -0.045776 | -0.5127 | 0.8194 | 122.6898 | 0.13275 | 0.13275 | 122.9645 | 122.9187 | 122.9187 | 122.9462 | -123.0103 | -122.937 | 122.644 | 0.16022 | 2.9755 | 1.6754
1093.1719 | 123.1155 | -56.9458 | 65.8813 | -0.075836 | 0.00019446 | 0.064162 | 0.069686 | -5.343e-05 | 0.0028327 | 0.005849 | 0.0078126 | 0.00088875 | 0.00064083 | -0.005708 | 0.0012711 | -0.0023755 | 0.0025891 | -54.0573 | 65.8676 | -57.0465 | 65.6754 | -56.1768 | -56.8588 | -56.2592 | -55.2429 | 65.8859 | -57.0099 | -56.7947 | -56.813 | -57.0374 | -56.7032 | -0.10071 | -0.013733 | -0.20599 | 0.76904 | 0.68665 | 0.086975 | 0.78735 | 0.18768 | -0.064087 | 0.004577 | -122.6761 | 0.13275 | 0.24262 | -0.091553 | 0.3067 | -0.027466 | 0.86975 | 122.7219 | 0.19684 | 0.21515 | 122.9141 | 122.8958 | 122.8134 | 122.8317 | -122.9279 | -122.8912 | 122.6212 | 0.15106 | 2.8885 | 1.7029
1094.1719 | 123.1659 | -56.955 | 65.831 | -0.10635 | 0.0021171 | 0.063948 | 0.071181 | -0.00048063 | 0.0060369 | 0.0047808 | 0.02002 | 0.00088875 | 0.0025634 | 0.00070062 | -0.00022431 | -0.0036573 | -0.00040166 | -53.9932 | 65.8264 | -57.0099 | 65.744 | -56.1035 | -56.7902 | -56.1722 | -55.1788 | 65.8813 | -57.0328 | -56.7719 | -56.7856 | -56.9916 | -56.694 | -0.054932 | -0.004578 | -0.086975 | 0.85144 | 0.78278 | 0.1648 | 0.83771 | 0.21973 | -0.07782 | 0.050354 | -122.6028 | 0.16937 | 0.26093 | -0.036621 | 0.33874 | 0.041199 | 0.90637 | 122.7539 | 0.24719 | 0.26093 | 122.8363 | 122.9141 | 122.7814 | 122.8363 | -122.8409 | -122.8638 | 122.699 | 0.18311 | 2.9617 | 1.7761
1095.1719 | 123.0057 | -57.0053 | 65.9363 | -0.052948 | -0.00066014 | 0.064375 | 0.07225 | -0.00090783 | 0.00091009 | 0.0054218 | -0.037964 | 0.00046135 | 0.0019226 | -0.0035718 | -0.00043791 | -0.00066648 | -0.0057423 | -54.0619 | 65.8722 | -57.0282 | 65.6479 | -56.1951 | -56.9046 | -56.2866 | -55.3436 | 65.9317 | -57.0236 | -56.8726 | -56.9458 | -57.1472 | -56.813 | -0.022888 | -0.064087 | -0.28839 | 0.81024 | 0.71869 | 0.10071 | 0.74158 | 0.1236 | -0.018311 | -0.004577 | -122.8088 | 0.059509 | 0.19226 | -0.14191 | 0.21057 | -0.1236 | 0.83313 | 122.6761 | 0.07782 | 0.15106 | 122.9004 | 122.9553 | 122.8775 | 122.937 | -122.9645 | -122.9599 | 122.6532 | 0.13275 | 2.9434 | 1.6617
1096.1719 | 122.9874 | -56.987 | 65.9317 | -0.022431 | 0.0025443 | 0.063094 | 0.072463 | 0.00058737 | 0.0021917 | 0.0067036 | -0.034912 | 0.0019567 | -0.00042717 | -0.0020764 | -0.00086511 | -0.0023755 | -0.0010425 | -54.0665 | 65.8905 | -57.0282 | 65.6433 | -56.1859 | -56.8954 | -56.282 | -55.3162 | 65.9225 | -57.0236 | -56.8771 | -56.9138 | -57.1381 | -56.8039 | -0.041198 | -0.041199 | -0.28839 | 0.80109 | 0.70496 | 0.091553 | 0.74616 | 0.13275 | -0.036621 | -0.009156 | -122.8088 | 0.073243 | 0.18311 | -0.15106 | 0.21973 | -0.11444 | 0.84229 | 122.6715 | 0.10986 | 0.14648 | 122.9187 | 122.9462 | 122.8775 | 122.9095 | -122.9599 | -122.9553 | 122.6303 | 0.10986 | 2.9205 | 1.6708
1097.1719 | 123.0331 | -56.9778 | 65.8768 | -0.12161 | -0.00023294 | 0.065657 | 0.072463 | -0.0030442 | 0.0030463 | 0.0034992 | -0.03186 | 0.00067495 | 0.00021363 | 0.0028368 | 0.00020289 | -0.00088008 | 0.0032299 | -54.0756 | 65.8813 | -57.0648 | 65.6525 | -56.1676 | -56.8817 | -56.2592 | -55.3162 | 65.9088 | -57.0282 | -56.8405 | -56.8909 | -57.1106 | -56.7993 | -0.086975 | 0.004578 | -0.2243 | 0.81024 | 0.71869 | 0.09613 | 0.80566 | 0.1831 | -0.050354 | 0.032043 | -122.7173 | 0.086975 | 0.17853 | -0.13275 | 0.22888 | -0.082398 | 0.89722 | 122.7173 | 0.13733 | 0.18768 | 122.9462 | 122.937 | 122.8592 | 122.8867 | -122.9416 | -122.905 | 122.6303 | 0.13733 | 2.9022 | 1.6617
1098.1719 | 123.0927 | -56.9962 | 65.9363 | -0.075836 | 0.0014761 | 0.064803 | 0.07225 | -0.0011214 | 0.0017645 | 0.005849 | -0.03186 | 0.0019567 | -0.00042717 | -0.0010084 | -1.0706e-05 | -0.0017347 | 0.00045294 | -54.1077 | 65.8905 | -57.0602 | 65.6204 | -56.2317 | -56.9229 | -56.2958 | -55.3436 | 65.9363 | -57.0511 | -56.8039 | -57.2067 | -57.1838 | -56.6711 | -0.064087 | -0.045776 | -0.31586 | 0.76447 | 0.70038 | 0.073242 | 0.76447 | 0.13733 | -0.054931 | 0 | -122.7402 | -0.21057 | 0.32501 | -0.18768 | 0.37994 | -0.13275 | 0.82855 | 122.6807 | -0.15564 | 0.24719 | 122.9507 | 122.9874 | 122.8867 | 122.9324 | -122.9965 | -122.9874 | 122.6166 | 0.19226 | 2.8885 | 1.6525
1099.1719 | 123.0148 | -56.9916 | 65.8905 | -0.11398 | -0.00023294 | 0.064803 | 0.07289 | 0.00016017 | 0.0032599 | 0.0073444 | -0.016602 | 0.00067495 | -0.00042717 | -0.006349 | -0.0025741 | -0.0015211 | 0.0019483 | -54.071 | 65.8905 | -57.0328 | 65.6204 | -56.1813 | -56.8817 | -56.2637 | -55.3024 | 65.9271 | -57.0328 | -56.8451 | -56.9 | -57.1335 | -56.7856 | -0.041199 | 0 | -0.27008 | 0.81024 | 0.72784 | 0.10986 | 0.76904 | 0.15106 | -0.041199 | 0.036621 | -122.7356 | 0.091553 | 0.20599 | -0.14191 | 0.24719 | -0.10071 | 0.85144 | 122.6532 | 0.13275 | 0.18768 | 122.9233 | 122.9599 | 122.8821 | 122.9187 | -122.9233 | -122.9233 | 122.612 | 0.14648 | 2.9205 | 1.6891
1100.1719 | 123.0103 | -56.9916 | 65.8951 | -0.075836 | -0.0013009 | 0.064375 | 0.071609 | -5.343e-05 | 0.0026191 | 0.0054218 | -0.025757 | 0.00067495 | 0.00064083 | 0.00048702 | -0.0019333 | -0.00088008 | -0.0040333 | -54.1077 | 65.8813 | -57.019 | 65.6387 | -56.1996 | -56.9046 | -56.2775 | -55.3711 | 65.9134 | -57.0099 | -56.8954 | -56.9229 | -57.1426 | -56.8039 | -0.027466 | -0.013733 | -0.25635 | 0.79193 | 0.71411 | 0.086975 | 0.74158 | 0.11444 | -0.018311 | 0.01831 | -122.7905 | 0.068664 | 0.18768 | -0.15106 | 0.20599 | -0.13275 | 0.8194 | 122.6578 | 0.086975 | 0.11444 | 122.9004 | 122.9233 | 122.8729 | 122.905 | -122.9141 | -122.905 | 122.6303 | 0.09613 | 2.8839 | 1.6205
1101.1719 | 123.0743 | -56.9733 | 65.8813 | -0.1445 | 0.0027579 | 0.063521 | 0.073318 | -0.00090783 | 0.0056097 | 0.0062762 | -0.01355 | 0.0011023 | -0.00085457 | 0.0028368 | -1.0706e-05 | -0.0025891 | 0.0017345 | -54.1168 | 65.8585 | -57.0511 | 65.6616 | -56.1584 | -56.8863 | -56.2317 | -55.2979 | 65.8722 | -56.9916 | -56.8039 | -56.8542 | -57.074 | -56.7398 | -0.077819 | -0.022889 | -0.21973 | 0.81482 | 0.74158 | 0.086975 | 0.8194 | 0.16479 | -0.01831 | -0.009156 | -122.6852 | 0.11902 | 0.23346 | -0.10071 | 0.25177 | -0.082398 | 0.89264 | 122.7127 | 0.13733 | 0.18768 | 122.9095 | 122.8638 | 122.8317 | 122.8455 | -122.9324 | -122.8729 | 122.6349 | 0.16937 | 2.8564 | 1.6754
1102.1719 | 123.0148 | -56.987 | 65.918 | -0.075836 | -0.0019417 | 0.065016 | 0.075667 | 0.00251 | 0.0028327 | 0.0071308 | -0.034912 | 3.4148e-05 | 0.0019226 | -0.0025036 | -0.0017197 | -0.0010937 | 0.0038709 | -54.0527 | 65.9042 | -57.0236 | 65.657 | -56.1676 | -56.9 | -56.25 | -55.3482 | 65.9271 | -57.0145 | -56.8726 | -56.9366 | -57.1518 | -56.8039 | -0.036621 | -0.013733 | -0.26093 | 0.8194 | 0.737 | 0.086976 | 0.77362 | 0.1236 | -0.027465 | 0.009155 | -122.7905 | 0.050354 | 0.18311 | -0.16479 | 0.21057 | -0.13733 | 0.85602 | 122.6807 | 0.077819 | 0.14191 | 122.9279 | 122.9416 | 122.8912 | 122.9141 | -122.9416 | -122.9324 | 122.644 | 0.11444 | 2.9343 | 1.6388
1103.1719 | 123.0057 | -57.0007 | 65.9134 | -0.052948 | 0.0012625 | 0.065657 | 0.073318 | 0.0012284 | 0.0030463 | 0.0047808 | -0.028809 | 0.0019567 | 0.001709 | 0.002196 | -0.0012925 | -0.0034437 | 0.00045294 | -53.92 | 65.8813 | -57.0236 | 65.6525 | -56.1493 | -56.9046 | -56.2592 | -55.3619 | 65.9454 | -57.0328 | -56.868 | -56.9046 | -57.1426 | -56.8039 | -0.022889 | -0.032043 | -0.26093 | 0.85144 | 0.74158 | 0.09613 | 0.76447 | 0.11902 | -0.032044 | 0.032044 | -122.7814 | 0.09613 | 0.19684 | -0.14191 | 0.22888 | -0.10986 | 0.87433 | 122.6761 | 0.12817 | 0.16479 | 122.905 | 122.9782 | 122.8821 | 122.9462 | -122.937 | -122.9462 | 122.6532 | 0.13275 | 3.0807 | 1.6388
1104.1719 | 123.0286 | -57.0053 | 65.9088 | -0.045319 | -0.00023294 | 0.063094 | 0.07225 | -0.0038986 | 0.0030463 | 0.0073444 | -0.01355 | 0.0032385 | 0.0021362 | 0.002196 | -0.0017197 | -0.0013073 | 0.00066654 | -53.9108 | 65.9042 | -57.0511 | 65.657 | -56.1447 | -56.8954 | -56.2454 | -55.3391 | 65.9088 | -57.0236 | -56.8314 | -56.8726 | -57.1014 | -56.7764 | -0.045776 | -0.004577 | -0.25177 | 0.8606 | 0.75989 | 0.10986 | 0.80566 | 0.15564 | -0.018311 | 0 | -122.7402 | 0.13275 | 0.22888 | -0.09613 | 0.24719 | -0.077819 | 0.90637 | 122.7081 | 0.15106 | 0.19226 | 122.9553 | 122.9324 | 122.9095 | 122.9141 | -122.9599 | -122.9324 | 122.6624 | 0.17395 | 3.0945 | 1.6663
1105.1719 | 123.0835 | -56.9595 | 65.8905 | -0.075836 | -0.00044654 | 0.062453 | 0.070327 | 0.001442 | 0.0030463 | 0.0043536 | 0.13293 | 0.0011023 | 0.00042723 | 0.00091422 | -0.00043791 | -0.0038709 | -0.00061526 | -53.8376 | 65.8585 | -57.0099 | 65.712 | -56.0761 | -56.7947 | -56.1447 | -55.2292 | 65.9134 | -57.0099 | -56.7902 | -56.8085 | -57.0145 | -56.7307 | -0.050354 | -0.032044 | -0.17853 | 0.88348 | 0.81482 | 0.16479 | 0.86517 | 0.21515 | -0.050354 | 0.022888 | -122.6807 | 0.15106 | 0.22888 | -0.054931 | 0.27924 | -0.004577 | 0.93384 | 122.7219 | 0.20142 | 0.21973 | 122.8683 | 122.9233 | 122.818 | 122.8729 | -122.9004 | -122.9004 | 122.6715 | 0.16937 | 3.1219 | 1.7303
1106.1719 | 122.9645 | -57.0007 | 65.9225 | -0.045319 | 0.00083526 | 0.063521 | 0.072677 | -0.0015488 | 0.0047553 | 0.0056354 | -0.03186 | -0.00082025 | 0.0025634 | 0.0043322 | -0.0021469 | -0.0013073 | 2.554e-05 | -53.8742 | 65.9088 | -57.0511 | 65.6479 | -56.1722 | -56.9183 | -56.2775 | -55.3757 | 65.95 | -57.0282 | -56.8726 | -56.9504 | -57.1655 | -56.8268 | -0.050354 | -0.013733 | -0.27466 | 0.82855 | 0.72327 | 0.082397 | 0.77362 | 0.13275 | -0.027466 | 0.027466 | -122.7951 | 0.050354 | 0.17395 | -0.16479 | 0.20142 | -0.13733 | 0.87891 | 122.699 | 0.07782 | 0.15564 | 122.9599 | 122.9782 | 122.9095 | 122.9507 | -122.9736 | -122.9507 | 122.6486 | 0.12817 | 3.1265 | 1.6251
1107.1719 | 123.0515 | -56.9916 | 65.8859 | -0.12161 | 0.00062166 | 0.063948 | 0.073104 | 0.00016017 | 0.0017645 | 0.0060626 | 0.001709 | 0.00067495 | 0.003418 | 5.9824e-05 | -0.0021469 | -0.0010937 | 0.0038709 | -53.8925 | 65.8585 | -57.0419 | 65.6708 | -56.1356 | -56.8771 | -56.2363 | -55.3207 | 65.9225 | -57.0099 | -56.813 | -56.8588 | -57.074 | -56.749 | -0.050354 | -0.027466 | -0.21515 | 0.85602 | 0.75531 | 0.11444 | 0.80566 | 0.16479 | -0.018311 | 0.036621 | -122.699 | 0.13275 | 0.24262 | -0.082398 | 0.26093 | -0.064087 | 0.90637 | 122.7127 | 0.15106 | 0.19684 | 122.9004 | 122.9324 | 122.85 | 122.9141 | -122.9279 | -122.8958 | 122.6624 | 0.17853 | 3.0991 | 1.6708
1108.1719 | 123.056 | -56.987 | 65.8676 | -0.075836 | -0.00044654 | 0.06288 | 0.072463 | -5.343e-05 | 0.00091009 | 0.0060626 | -0.037964 | 0.0015295 | 0.0012818 | 0.0024096 | -0.0027877 | -0.0021619 | 0.0013073 | -53.9062 | 65.8722 | -57.0465 | 65.6387 | -56.1493 | -56.9092 | -56.2408 | -55.3253 | 65.9134 | -57.0282 | -56.8268 | -56.8817 | -57.1106 | -56.7719 | -0.059509 | 0.004577 | -0.22888 | 0.83771 | 0.74616 | 0.07782 | 0.80566 | 0.13733 | -0.041198 | 0.045776 | -122.6944 | 0.10529 | 0.21515 | -0.1236 | 0.25635 | -0.082398 | 0.89722 | 122.6852 | 0.14648 | 0.20142 | 122.9187 | 122.9416 | 122.8592 | 122.9004 | -122.9141 | -122.8958 | 122.6257 | 0.16022 | 3.0808 | 1.6617
1109.1719 | 123.0011 | -56.9824 | 65.918 | -0.083466 | -0.00044654 | 0.06523 | 0.07289 | 0.00037377 | 0.0013373 | 0.0039264 | -0.037964 | 0.00088875 | 0.0019226 | 0.0032642 | 0.0019119 | -0.00066648 | 0.00045294 | -53.8788 | 65.8722 | -57.0282 | 65.6799 | -56.1218 | -56.8542 | -56.2134 | -55.3253 | 65.9225 | -57.0236 | -56.8268 | -56.9 | -57.1106 | -56.7902 | -0.045776 | -0.045777 | -0.23804 | 0.8606 | 0.76904 | 0.12817 | 0.81482 | 0.17395 | -0.041199 | 0.004577 | -122.7448 | 0.082398 | 0.19226 | -0.12817 | 0.23346 | -0.086975 | 0.90637 | 122.7081 | 0.1236 | 0.19684 | 122.9004 | 122.9462 | 122.8546 | 122.905 | -122.9462 | -122.9416 | 122.6624 | 0.15564 | 3.1036 | 1.6571
1110.1719 | 123.1201 | -56.9687 | 65.8539 | -0.17502 | 0.0012625 | 0.064803 | 0.070541 | -0.001976 | 0.0028327 | 0.0069172 | 0.026123 | 0.00067495 | 0.0021362 | -0.0067762 | -0.00065151 | -0.00066648 | -0.00040166 | -53.8193 | 65.8447 | -56.987 | 65.7349 | -56.012 | -56.7627 | -56.1172 | -55.2155 | 65.8539 | -57.0145 | -56.7673 | -56.8085 | -56.9962 | -56.7123 | -0.018311 | -0.009155 | -0.11902 | 0.95673 | 0.85144 | 0.20599 | 0.86975 | 0.22431 | -0.045776 | 0 | -122.6212 | 0.16022 | 0.25635 | -0.027466 | 0.30212 | 0.01831 | 0.97504 | 122.7219 | 0.20599 | 0.24719 | 122.8317 | 122.8683 | 122.8134 | 122.8226 | -122.8409 | -122.8683 | 122.7036 | 0.20142 | 3.1494 | 1.7532
1111.1719 | 122.9782 | -56.9824 | 65.9317 | -0.068207 | 0.00040806 | 0.065657 | 0.071395 | -0.0011214 | 0.0017645 | 0.0067036 | -0.044067 | 0.0019567 | 0.00085443 | -0.00015378 | -0.00043791 | -0.00045288 | 0.0010937 | -53.8879 | 65.8813 | -57.0282 | 65.6479 | -56.131 | -56.868 | -56.2408 | -55.3711 | 65.9363 | -57.0053 | -56.8771 | -56.9275 | -57.1518 | -56.8222 | -0.045776 | -0.050354 | -0.28381 | 0.85144 | 0.74158 | 0.11444 | 0.78735 | 0.16022 | -0.022888 | 0.004577 | -122.8088 | 0.054932 | 0.16022 | -0.16937 | 0.18311 | -0.14648 | 0.89722 | 122.6761 | 0.07782 | 0.12817 | 122.9095 | 122.9416 | 122.8638 | 122.9187 | -122.9599 | -122.937 | 122.6303 | 0.10529 | 3.0945 | 1.6113
1112.1719 | 123.0148 | -56.9733 | 65.9088 | -0.10635 | 0.0012625 | 0.06288 | 0.071609 | 0.00037377 | 0.0019781 | 0.0071308 | -0.041016 | 0.0011023 | 0.001709 | 0.00070062 | -1.0706e-05 | 0.00040152 | 2.554e-05 | -53.8651 | 65.8905 | -57.0282 | 65.6662 | -56.1081 | -56.8726 | -56.2225 | -55.3482 | 65.918 | -57.0236 | -56.8497 | -56.9092 | -57.1198 | -56.8039 | -0.054931 | -0.01831 | -0.24261 | 0.86517 | 0.75073 | 0.10071 | 0.80566 | 0.15564 | -0.050354 | 0.009156 | -122.7585 | 0.064087 | 0.16937 | -0.14648 | 0.21973 | -0.09613 | 0.92011 | 122.6944 | 0.11444 | 0.17395 | 122.9187 | 122.9416 | 122.8638 | 122.8912 | -122.937 | -122.9324 | 122.6395 | 0.1236 | 3.1082 | 1.6251
1113.1719 | 122.9965 | -56.987 | 65.8905 | -0.11398 | -0.00023294 | 0.06288 | 0.072036 | 0.0035782 | 0.0026191 | 0.00414 | 0.0047608 | -0.00060665 | 0.0019226 | 0.00091422 | -0.0017197 | -0.0015211 | 0.0013073 | -53.7872 | 65.8905 | -57.0236 | 65.6662 | -56.1356 | -56.9275 | -56.25 | -55.394 | 65.918 | -57.0282 | -56.8542 | -56.9046 | -57.1381 | -56.7947 | -0.036621 | 0 | -0.2243 | 0.85144 | 0.737 | 0.05951 | 0.77362 | 0.096131 | -0.041198 | 0.027466 | -122.7448 | 0.082398 | 0.19226 | -0.15106 | 0.23346 | -0.10986 | 0.88806 | 122.6898 | 0.1236 | 0.17395 | 122.9141 | 122.9462 | 122.8775 | 122.905 | -122.9141 | -122.9187 | 122.6532 | 0.13275 | 3.1998 | 1.593
1114.1719 | 122.9691 | -56.9824 | 65.8905 | -0.068207 | -0.0023691 | 0.062666 | 0.07289 | 0.0033646 | -0.00037171 | 0.0060626 | 0.010864 | 0.0028113 | 0.00021363 | 5.9824e-05 | -0.0012925 | -0.0019483 | -0.0010425 | -53.9154 | 65.8768 | -57.0694 | 65.7806 | -55.8655 | -56.9412 | -56.2958 | -55.4214 | 65.9225 | -57.0236 | -56.8726 | -56.9229 | -57.1472 | -56.8314 | -0.086975 | -0.013733 | -0.10986 | 1.1169 | 0.68665 | 0.041199 | 0.77362 | 0.12817 | -0.041199 | 0.032043 | -122.7631 | 0.059509 | 0.15106 | -0.16479 | 0.19226 | -0.1236 | 1.2039 | 122.85 | 0.10071 | 0.15106 | 122.9462 | 122.9462 | 122.8592 | 122.905 | -122.9599 | -122.9141 | 122.7631 | 0.10986 | 3.067 | 1.561
1115.1719 | 123.0927 | -56.9641 | 65.8813 | -0.11398 | 0.00040806 | 0.062239 | 0.070541 | -0.003685 | 0.00091009 | 0.009267 | 0.059692 | -0.00039305 | 2.8e-08 | 0.00070062 | -1.0706e-05 | -0.0021619 | -0.0029651 | -53.8971 | 65.863 | -57.019 | 65.6982 | -56.0761 | -56.7993 | -56.1447 | -55.3116 | 65.8676 | -57.019 | -56.8222 | -56.8314 | -57.0328 | -56.7352 | -0.054932 | -0.018311 | -0.18311 | 0.88806 | 0.8194 | 0.1648 | 0.87433 | 0.21973 | -0.054932 | -0.013733 | -122.7036 | 0.13275 | 0.22888 | -0.068665 | 0.28381 | -0.013733 | 0.94299 | 122.7173 | 0.18768 | 0.19684 | 122.8821 | 122.8867 | 122.8271 | 122.8317 | -122.9004 | -122.9004 | 122.6624 | 0.14191 | 3.067 | 1.6525
1116.1719 | 122.9828 | -57.0145 | 65.8997 | -0.12924 | 0.0010489 | 0.064589 | 0.075667 | 0.0016556 | 0.0024053 | 0.0067036 | -0.022705 | 0.0011023 | -0.00042717 | 0.0034778 | -0.0012925 | -0.0015211 | 0.00023934 | -53.8788 | 65.8768 | -57.0145 | 65.6754 | -56.131 | -56.868 | -56.218 | -55.3665 | 65.9271 | -57.0007 | -56.8542 | -56.9229 | -57.1564 | -56.8268 | 0 | -0.022888 | -0.2243 | 0.88348 | 0.79651 | 0.14648 | 0.79651 | 0.14648 | 0.013733 | 0.027466 | -122.7539 | 0.091552 | 0.18768 | -0.14191 | 0.17395 | -0.15564 | 0.88348 | 122.6898 | 0.077819 | 0.14648 | 122.8912 | 122.9279 | 122.8912 | 122.9416 | -122.9141 | -122.9004 | 122.6898 | 0.16022 | 3.1357 | 1.6479
1117.1719 | 123.0377 | -56.9962 | 65.9088 | -0.11398 | 0.00062166 | 0.065657 | 0.07289 | 0.0020828 | 0.0013373 | 0.0079852 | -0.0043946 | 0.0017431 | -0.0012818 | 0.0015552 | -0.0021469 | -0.0023755 | 0.0015209 | -53.9017 | 65.863 | -57.0053 | 65.6982 | -56.0577 | -56.7993 | -56.1722 | -55.3253 | 65.8813 | -57.0099 | -56.8085 | -56.8634 | -57.0786 | -56.7673 | -0.009155 | -0.045776 | -0.21057 | 0.93842 | 0.82398 | 0.19684 | 0.83313 | 0.20599 | -0.013733 | -0.027465 | -122.7173 | 0.13275 | 0.22888 | -0.082397 | 0.24261 | -0.068664 | 0.94757 | 122.7036 | 0.14648 | 0.20142 | 122.8683 | 122.8912 | 122.8592 | 122.8775 | -122.9141 | -122.9187 | 122.6944 | 0.18768 | 3.0945 | 1.6708
1118.1719 | 122.9691 | -56.9962 | 65.9042 | -0.060578 | 0.0029715 | 0.06288 | 0.071395 | 0.0016556 | 0.0013373 | 0.0056354 | -0.025757 | 0.00067495 | 0.00064083 | -0.0014356 | 0.00063009 | -0.0010937 | 0.0021619 | -53.9337 | 65.8768 | -57.0419 | 65.6113 | -56.1813 | -56.9138 | -56.25 | -55.4626 | 65.9225 | -57.0557 | -56.868 | -56.9412 | -57.1381 | -56.8222 | -0.045776 | -0.027466 | -0.29297 | 0.81482 | 0.74616 | 0.082398 | 0.79193 | 0.12817 | -0.059509 | 0.01831 | -122.7722 | 0.054932 | 0.17395 | -0.14191 | 0.23346 | -0.082398 | 0.8606 | 122.6532 | 0.11444 | 0.18768 | 122.9187 | 122.9782 | 122.8729 | 122.9187 | -122.9462 | -122.9599 | 122.6074 | 0.12817 | 3.0624 | 1.5335
1119.1719 | 122.9736 | -57.0053 | 65.8768 | -0.052948 | 0.00040806 | 0.064375 | 0.073318 | -0.0028304 | 0.0021917 | 0.005849 | -0.034912 | 0.0021703 | -0.0019226 | 0.001128 | 0.00063009 | -0.00023928 | 0.0019483 | -53.9383 | 65.8859 | -57.0511 | 65.6158 | -56.163 | -56.9046 | -56.25 | -55.4489 | 65.9042 | -57.0419 | -56.8954 | -56.9504 | -57.1701 | -56.8268 | -0.045776 | 0.009155 | -0.26093 | 0.84229 | 0.75531 | 0.10071 | 0.80109 | 0.14648 | -0.036621 | 0.027466 | -122.7722 | 0.054932 | 0.17853 | -0.16479 | 0.21515 | -0.12817 | 0.88806 | 122.6669 | 0.091553 | 0.14648 | 122.937 | 122.9462 | 122.8912 | 122.9095 | -122.9279 | -122.9187 | 122.6212 | 0.10986 | 3.067 | 1.5564
1120.1719 | 123.0331 | -56.9733 | 65.8768 | -0.11398 | 0.00083526 | 0.064375 | 0.069045 | 0.00080117 | 0.0039007 | 0.005849 | 0.078003 | 0.0015295 | 0.001709 | -0.0061352 | -0.00065151 | -0.0038709 | -0.0023243 | -53.9017 | 65.8585 | -56.987 | 65.6937 | -56.0349 | -56.8039 | -56.131 | -55.3391 | 65.8676 | -57.019 | -56.8588 | -56.8588 | -57.0282 | -56.7444 | -0.013733 | -0.018311 | -0.1831 | 0.93842 | 0.84229 | 0.16937 | 0.85602 | 0.18311 | -0.045776 | -0.009155 | -122.7356 | 0.11444 | 0.22888 | -0.054931 | 0.27466 | -0.009155 | 0.95215 | 122.6807 | 0.16022 | 0.16022 | 122.8455 | 122.8867 | 122.8317 | 122.8409 | -122.8638 | -122.8958 | 122.6669 | 0.11444 | 3.0716 | 1.6342
1121.1719 | 122.9965 | -57.0053 | 65.918 | -0.052948 | -0.00066014 | 0.06822 | 0.07225 | 0.0033646 | 0.0036871 | 0.0062762 | -0.0043946 | 0.0015295 | 0.001709 | 0.0013416 | -0.0010787 | -0.0017347 | -0.0021107 | -54.0939 | 65.8401 | -57.074 | 65.6387 | -56.0486 | -56.8954 | -56.2454 | -55.4398 | 65.9042 | -57.0282 | -56.8817 | -56.9275 | -57.1335 | -56.8039 | -0.068665 | -0.07782 | -0.27924 | 0.95673 | 0.75989 | 0.10986 | 0.82855 | 0.17853 | -0.022888 | -0.013733 | -122.7997 | 0.07782 | 0.20142 | -0.12817 | 0.2243 | -0.10529 | 1.0254 | 122.7127 | 0.10071 | 0.14648 | 122.9141 | 122.9324 | 122.8455 | 122.9095 | -122.9919 | -122.9462 | 122.644 | 0.1236 | 2.9114 | 1.5656
1122.1719 | 122.9691 | -56.987 | 65.8813 | -0.075836 | -1.9142e-05 | 0.064589 | 0.073104 | 0.0018692 | 0.0041143 | 0.005849 | -0.022705 | 0.0025975 | 0.001068 | 0.0026232 | -0.0012925 | -0.0010937 | -0.0023243 | -53.9474 | 65.8722 | -57.0282 | 65.6204 | -56.1356 | -56.9 | -56.25 | -55.4535 | 65.9134 | -57.0465 | -56.9 | -56.9687 | -57.1793 | -56.8405 | -0.041198 | -0.009156 | -0.26093 | 0.85144 | 0.737 | 0.086976 | 0.7782 | 0.12817 | -0.059509 | 0.032043 | -122.7814 | 0.018311 | 0.14648 | -0.19226 | 0.20599 | -0.13275 | 0.89264 | 122.6486 | 0.07782 | 0.14648 | 122.9004 | 122.9599 | 122.8592 | 122.9004 | -122.9095 | -122.9279 | 122.6074 | 0.086976 | 3.0396 | 1.5335
1123.1719 | 122.9462 | -57.0099 | 65.8997 | -0.037689 | -0.00023294 | 0.06523 | 0.073745 | -5.343e-05 | 0.0036871 | 0.005849 | -0.044067 | 0.0028113 | 0.001709 | -0.0014356 | -0.0015061 | -0.0030163 | 0.00023934 | -53.952 | 65.8585 | -57.0465 | 65.6204 | -56.1584 | -56.9092 | -56.2317 | -55.5176 | 65.9042 | -57.0374 | -56.8863 | -56.9778 | -57.1747 | -56.8542 | -0.036621 | -0.041199 | -0.27924 | 0.85144 | 0.7782 | 0.10071 | 0.81482 | 0.13733 | -0.027466 | 0.004578 | -122.7859 | 0.032044 | 0.15564 | -0.1648 | 0.18311 | -0.13733 | 0.88806 | 122.6669 | 0.05951 | 0.15106 | 122.905 | 122.9416 | 122.8683 | 122.9141 | -122.9462 | -122.937 | 122.6303 | 0.1236 | 3.0579 | 1.4923
1124.1719 | 123.0148 | -56.9824 | 65.8997 | -0.10635 | -0.00023294 | 0.064375 | 0.073104 | -0.0030442 | 0.0013373 | 0.0069172 | -0.016602 | 0.00067495 | 0.0012818 | -0.0016492 | -0.0019333 | -0.0015211 | -0.00061526 | -53.9337 | 65.8722 | -57.0282 | 65.6662 | -56.0852 | -56.8405 | -56.1859 | -55.426 | 65.8768 | -57.0282 | -56.8588 | -56.9366 | -57.1243 | -56.8085 | -0.045776 | -0.027466 | -0.23346 | 0.89722 | 0.79651 | 0.14191 | 0.84229 | 0.18768 | -0.045776 | -0.022888 | -122.7585 | 0.045776 | 0.17395 | -0.14191 | 0.21973 | -0.096131 | 0.94299 | 122.6944 | 0.091552 | 0.16937 | 122.9004 | 122.905 | 122.8546 | 122.8592 | -122.9279 | -122.9279 | 122.6486 | 0.1236 | 3.0487 | 1.5564
1125.1719 | 123.0835 | -56.9641 | 65.8813 | -0.068207 | -0.0023691 | 0.061812 | 0.070968 | -0.0024032 | 0.0013373 | 0.0060626 | 0.09021 | 3.4148e-05 | 2.8e-08 | 0.0034778 | -0.00043791 | -0.0042981 | -0.0031787 | -53.9337 | 65.8218 | -57.0007 | 65.7211 | -56.0028 | -56.7444 | -56.0761 | -55.3482 | 65.8859 | -56.9916 | -56.781 | -56.7993 | -56.9824 | -56.7123 | -0.036621 | -0.05951 | -0.16022 | 0.9613 | 0.88806 | 0.21973 | 0.92468 | 0.25635 | -0.027466 | 0.004577 | -122.6624 | 0.1648 | 0.25177 | -0.018311 | 0.27924 | 0.009155 | 0.99792 | 122.7219 | 0.19226 | 0.21057 | 122.8226 | 122.8775 | 122.7859 | 122.85 | -122.8821 | -122.8729 | 122.6852 | 0.18311 | 3.0304 | 1.6159
1126.1719 | 123.0331 | -57.0007 | 65.8859 | -0.075836 | -1.9142e-05 | 0.063734 | 0.074599 | 0.0037918 | 0.0024053 | 0.0064898 | -0.022705 | 0.0015295 | 0.0012818 | 0.0024096 | -0.0027877 | -0.0019483 | -0.00040166 | -53.9749 | 65.8447 | -57.0465 | 65.625 | -56.1218 | -56.8542 | -56.2088 | -55.4581 | 65.8951 | -57.0374 | -56.8634 | -56.9321 | -57.1289 | -56.7993 | -0.045777 | -0.041198 | -0.26093 | 0.87891 | 0.79193 | 0.14648 | 0.83771 | 0.19226 | -0.036622 | 0.009156 | -122.7493 | 0.068664 | 0.20142 | -0.12817 | 0.23804 | -0.091552 | 0.92468 | 122.6715 | 0.10529 | 0.17395 | 122.8912 | 122.9324 | 122.8455 | 122.8958 | -122.9324 | -122.9233 | 122.6257 | 0.13733 | 3.0258 | 1.5427
1127.1719 | 123.024 | -57.0236 | 65.8768 | -0.11398 | 0.00019446 | 0.063521 | 0.074172 | 0.00080117 | 0.0034735 | 0.0043536 | -0.028809 | 0.0015295 | -0.00064077 | 0.00027342 | -0.0012925 | -0.00088008 | -0.0033923 | -53.9886 | 65.8493 | -57.0145 | 65.6296 | -56.1127 | -56.8817 | -56.2134 | -55.4535 | 65.918 | -57.0557 | -56.8634 | -56.9138 | -57.1243 | -56.8039 | 0.009156 | -0.027466 | -0.24719 | 0.91095 | 0.81024 | 0.14191 | 0.80109 | 0.13275 | -0.032043 | 0.041199 | -122.7402 | 0.10986 | 0.21973 | -0.10071 | 0.25177 | -0.068665 | 0.90179 | 122.644 | 0.14191 | 0.19226 | 122.8638 | 122.9736 | 122.8729 | 122.9416 | -122.8912 | -122.9324 | 122.6532 | 0.16022 | 3.035 | 1.5701
1128.1719 | 123.0469 | -56.9962 | 65.863 | -0.045319 | -0.00066014 | 0.064162 | 0.07225 | 0.00251 | 0.0034735 | 0.0054218 | 0.001709 | 0.0040929 | 0.001068 | 0.0047594 | -0.0010787 | -0.0015211 | -0.0010425 | -54.007 | 65.8539 | -57.0374 | 65.6433 | -56.1035 | -56.8817 | -56.2088 | -55.4672 | 65.8859 | -57.0511 | -56.8405 | -56.9183 | -57.1106 | -56.781 | -0.041199 | -0.009155 | -0.21973 | 0.89264 | 0.78735 | 0.11444 | 0.82855 | 0.15564 | -0.054931 | 0.022888 | -122.7036 | 0.07782 | 0.21515 | -0.11444 | 0.27008 | -0.05951 | 0.93384 | 122.6807 | 0.13275 | 0.21057 | 122.8912 | 122.937 | 122.85 | 122.8821 | -122.9004 | -122.9141 | 122.6395 | 0.15564 | 2.9892 | 1.5289
1129.1719 | 123.143 | -56.9733 | 65.8401 | -0.075836 | 0.0023307 | 0.065871 | 0.071609 | 0.0022964 | 0.0026191 | 0.0088398 | 0.0047608 | -0.00017945 | -0.0010682 | -0.0033582 | -0.0012925 | -0.0019483 | 0.0049389 | -53.9886 | 65.8218 | -57.0007 | 65.7303 | -56.012 | -56.7673 | -56.1035 | -55.3802 | 65.831 | -57.0282 | -56.7673 | -56.8359 | -57.0282 | -56.7123 | -0.027465 | -0.018311 | -0.10986 | 0.9613 | 0.86975 | 0.20599 | 0.89722 | 0.23346 | -0.054931 | -0.009155 | -122.6074 | 0.13733 | 0.26093 | -0.054931 | 0.31586 | 0 | 0.98877 | 122.731 | 0.19226 | 0.26093 | 122.8226 | 122.8592 | 122.7951 | 122.8043 | -122.8409 | -122.8683 | 122.7036 | 0.20599 | 2.9846 | 1.593
1130.1719 | 123.0743 | -56.987 | 65.8722 | -0.098725 | -0.0019417 | 0.063521 | 0.073958 | -0.0013352 | 0.00069649 | 0.0047808 | -0.025757 | -0.00017945 | 0.00021363 | -0.00229 | -0.00022431 | -0.0030163 | 0.0025891 | -54.0298 | 65.8768 | -57.0465 | 65.6525 | -56.0715 | -56.8405 | -56.1722 | -55.4581 | 65.8768 | -57.0557 | -56.8222 | -56.8726 | -57.0694 | -56.749 | -0.059509 | 0.004578 | -0.21973 | 0.91553 | 0.81482 | 0.14648 | 0.87433 | 0.20599 | -0.068664 | 0.004578 | -122.6944 | 0.11444 | 0.23804 | -0.082397 | 0.3067 | -0.013733 | 0.97504 | 122.699 | 0.1831 | 0.23346 | 122.9233 | 122.9324 | 122.8638 | 122.8638 | -122.9187 | -122.9279 | 122.6395 | 0.1648 | 2.9572 | 1.5289
1131.1719 | 123.1018 | -56.987 | 65.8447 | -0.060578 | -0.0032235 | 0.065443 | 0.072463 | 0.00037377 | 0.0026191 | 0.0064898 | -0.016602 | 0.00067495 | 0.0029906 | 5.9824e-05 | -0.0012925 | -0.0021619 | 0.00088014 | -54.0344 | 65.8401 | -57.0419 | 65.6479 | -56.0577 | -56.8314 | -56.163 | -55.4443 | 65.8722 | -57.0374 | -56.813 | -56.8542 | -57.0648 | -56.749 | -0.054931 | -0.004578 | -0.19684 | 0.92926 | 0.82398 | 0.15564 | 0.87891 | 0.21057 | -0.050354 | 0.027465 | -122.6578 | 0.13275 | 0.23804 | -0.077819 | 0.28839 | -0.027465 | 0.98419 | 122.6898 | 0.18311 | 0.22431 | 122.8821 | 122.9095 | 122.8271 | 122.8592 | -122.8867 | -122.8821 | 122.6349 | 0.17395 | 2.9526 | 1.5427
1132.1719 | 123.1064 | -56.9687 | 65.8218 | -0.11398 | 0.0027579 | 0.064803 | 0.072463 | 0.0018692 | 0.0039007 | 0.0056354 | -0.01355 | 0.00046135 | -0.0010682 | -0.0018628 | -0.0012925 | -0.0013073 | 0.00045294 | -53.9658 | 65.8173 | -57.019 | 65.7211 | -55.9662 | -56.7627 | -56.0852 | -55.3757 | 65.831 | -57.0282 | -56.7947 | -56.8222 | -56.9824 | -56.7032 | -0.050354 | -0.004577 | -0.10071 | 1.0025 | 0.88348 | 0.20599 | 0.93384 | 0.25635 | -0.059509 | 0.009156 | -122.6166 | 0.14648 | 0.2655 | -0.013733 | 0.32501 | 0.045776 | 1.0529 | 122.7402 | 0.20599 | 0.23346 | 122.8363 | 122.8592 | 122.7859 | 122.7997 | -122.8409 | -122.85 | 122.6898 | 0.17395 | 3.0029 | 1.593
1133.1719 | 123.111 | -56.9916 | 65.8264 | -0.11398 | -0.0013009 | 0.062666 | 0.073958 | 0.0040054 | 0.0015509 | 0.0073444 | -0.0074462 | 0.0013159 | 0.001068 | 0.0034778 | -0.0010787 | -0.0030163 | 2.554e-05 | -54.0115 | 65.831 | -57.0419 | 65.6937 | -56.0394 | -56.8085 | -56.1127 | -55.426 | 65.8493 | -57.0282 | -56.7902 | -56.8542 | -57.0419 | -56.7169 | -0.050354 | 0.004578 | -0.13275 | 0.95215 | 0.87891 | 0.1831 | 0.92926 | 0.23346 | -0.036621 | 0.022888 | -122.6166 | 0.13733 | 0.27466 | -0.050354 | 0.31128 | -0.013733 | 1.0025 | 122.7356 | 0.17395 | 0.23804 | 122.8729 | 122.8775 | 122.8226 | 122.8409 | -122.8683 | -122.8546 | 122.6852 | 0.20142 | 2.98 | 1.5656
1134.1719 | 123.1018 | -56.9778 | 65.8585 | -0.11398 | 0.0029715 | 0.064375 | 0.071822 | 0.0012284 | 0.0032599 | 0.0062762 | 0.041382 | -0.00039305 | 0.00021363 | -0.0025036 | -0.0030013 | -0.0021619 | -0.00061526 | -53.9841 | 65.8035 | -57.0099 | 65.7898 | -55.7922 | -56.7993 | -56.0944 | -55.4031 | 65.8218 | -57.0236 | -56.7902 | -56.8359 | -57.0282 | -56.7261 | -0.032044 | -0.054931 | -0.068664 | 1.1856 | 0.88348 | 0.17853 | 0.91553 | 0.21057 | -0.045777 | -0.036621 | -122.6486 | 0.14191 | 0.25177 | -0.050354 | 0.29755 | -0.004577 | 1.2177 | 122.7997 | 0.18768 | 0.23346 | 122.8134 | 122.8455 | 122.7814 | 122.7997 | -122.8683 | -122.8821 | 122.7676 | 0.18768 | 2.9938 | 1.5747
1135.1719 | 123.1064 | -56.9687 | 65.8081 | -0.12161 | 0.00083526 | 0.067366 | 0.07225 | 0.003151 | 0.0071051 | 0.00414 | 0.029175 | 0.0015295 | 0.002777 | 0.0026232 | -0.0015061 | -0.0023755 | -0.0042469 | -54.0802 | 65.7898 | -57.0648 | 65.7486 | -55.9158 | -56.7947 | -56.0715 | -55.4123 | 65.8356 | -57.0328 | -56.7764 | -56.8542 | -57.0145 | -56.7307 | -0.09613 | -0.01831 | -0.059509 | 1.0529 | 0.89722 | 0.17395 | 0.99335 | 0.27008 | -0.064087 | 0.027466 | -122.5845 | 0.11444 | 0.23804 | -0.045776 | 0.30212 | 0.018311 | 1.149 | 122.8134 | 0.17853 | 0.25635 | 122.8546 | 122.8683 | 122.7585 | 122.8043 | -122.8729 | -122.8409 | 122.7173 | 0.19226 | 2.8885 | 1.5564
1136.1719 | 123.0743 | -56.9733 | 65.8493 | -0.15213 | 0.00083526 | 0.063948 | 0.073531 | -0.0045394 | 0.0039007 | 0.0047808 | 0.02002 | 0.00024775 | 0.001068 | -0.0069898 | -0.00022431 | -0.0032301 | -0.0012561 | -54.007 | 65.8081 | -57.0099 | 65.6982 | -55.9799 | -56.7856 | -56.0806 | -55.4306 | 65.8356 | -57.0236 | -56.8359 | -56.8909 | -57.0602 | -56.7627 | -0.036621 | -0.041199 | -0.15106 | 0.99335 | 0.89264 | 0.18768 | 0.92926 | 0.2243 | -0.050354 | -0.013733 | -122.6852 | 0.082398 | 0.21057 | -0.086975 | 0.26093 | -0.036621 | 1.03 | 122.7081 | 0.13275 | 0.18768 | 122.818 | 122.8592 | 122.7814 | 122.8088 | -122.8592 | -122.8729 | 122.6715 | 0.13733 | 2.9663 | 1.5427
1137.1719 | 123.1064 | -56.9916 | 65.8264 | -0.075836 | 0.0012625 | 0.066084 | 0.072677 | 0.0044328 | 0.0030463 | 0.007558 | -0.010498 | 3.4148e-05 | -0.0027772 | -0.0027174 | -0.0023605 | -0.0013073 | 0.00023934 | -53.9886 | 65.7898 | -57.0374 | 65.7166 | -55.9799 | -56.7764 | -56.0989 | -55.4031 | 65.8539 | -57.0465 | -56.7856 | -56.8634 | -57.0511 | -56.7398 | -0.045777 | -0.036621 | -0.10986 | 1.0117 | 0.89264 | 0.21515 | 0.93842 | 0.26093 | -0.054932 | 0.027466 | -122.612 | 0.12817 | 0.25177 | -0.059509 | 0.3067 | -0.004577 | 1.0574 | 122.7539 | 0.18311 | 0.26093 | 122.8271 | 122.9004 | 122.7814 | 122.8455 | -122.8638 | -122.8729 | 122.7081 | 0.20599 | 3.0029 | 1.5884
1138.1719 | 123.0743 | -57.0053 | 65.8493 | -0.15213 | 0.00083526 | 0.063521 | 0.07225 | -5.343e-05 | 0.0034735 | 0.0073444 | 0.013916 | 0.0013159 | 2.8e-08 | -0.00079478 | -0.0025741 | -0.0015211 | 0.00066654 | -54.0024 | 65.7852 | -57.0053 | 65.6937 | -55.9891 | -56.7993 | -56.1035 | -55.481 | 65.8493 | -57.0602 | -56.8451 | -56.8954 | -57.0648 | -56.7673 | 0 | -0.064087 | -0.15564 | 1.0162 | 0.90179 | 0.20599 | 0.90179 | 0.20599 | -0.054932 | 0 | -122.6944 | 0.10986 | 0.23804 | -0.059509 | 0.29297 | -0.004577 | 1.0162 | 122.699 | 0.1648 | 0.21515 | 122.7905 | 122.9095 | 122.7905 | 122.8546 | -122.8546 | -122.9095 | 122.699 | 0.16022 | 3.0029 | 1.5244
1139.1719 | 123.111 | -56.987 | 65.8768 | -0.098725 | -0.0013009 | 0.063734 | 0.073531 | -0.0026168 | 0.0011237 | 0.0064898 | -0.01355 | 0.00046135 | -0.0014954 | 0.0024096 | -0.0025741 | -0.0038709 | 0.00066654 | -53.9932 | 65.7944 | -57.0236 | 65.7257 | -55.9387 | -56.7627 | -56.0806 | -55.4352 | 65.8585 | -57.0328 | -56.8085 | -56.8726 | -57.0511 | -56.7444 | -0.036621 | -0.082397 | -0.15106 | 1.0483 | 0.90637 | 0.22431 | 0.94299 | 0.26093 | -0.045776 | -0.018311 | -122.6852 | 0.11444 | 0.24262 | -0.064086 | 0.28839 | -0.01831 | 1.0849 | 122.7493 | 0.16022 | 0.2243 | 122.818 | 122.8912 | 122.7814 | 122.8455 | -122.9004 | -122.9095 | 122.7127 | 0.17853 | 2.9938 | 1.5518
1140.1719 | 123.0881 | -56.9916 | 65.8539 | -0.091095 | 0.0021171 | 0.065443 | 0.073104 | 0.0044328 | 0.0045417 | 0.002431 | 0.02002 | 0.0013159 | 0.002777 | -0.002931 | -0.00065151 | -0.0036573 | 0.0010937 | -54.0298 | 65.8127 | -56.9962 | 65.712 | -55.9845 | -56.8085 | -56.0898 | -55.4901 | 65.8676 | -57.0374 | -56.8314 | -56.8863 | -57.0602 | -56.7581 | -0.004578 | -0.041199 | -0.14191 | 1.0071 | 0.90179 | 0.1831 | 0.90637 | 0.18768 | -0.045777 | 0.013733 | -122.6852 | 0.10529 | 0.23346 | -0.068665 | 0.27924 | -0.022888 | 1.0117 | 122.7081 | 0.15106 | 0.20599 | 122.8088 | 122.905 | 122.8043 | 122.8592 | -122.85 | -122.8912 | 122.7036 | 0.16022 | 2.9617 | 1.5015
1141.1719 | 123.056 | -57.0053 | 65.8539 | -0.083466 | 0.00040806 | 0.065443 | 0.07289 | -0.0013352 | 0.0021917 | 0.0056354 | 0.02002 | -0.0025293 | -0.0046998 | -0.006349 | -0.0012925 | -0.0013073 | -0.0016833 | -53.9749 | 65.8356 | -57.0374 | 65.6799 | -55.9937 | -56.7764 | -56.0989 | -55.3574 | 65.8768 | -57.0511 | -56.8588 | -56.8451 | -57.0602 | -56.7719 | -0.032044 | -0.018311 | -0.17395 | 1.0117 | 0.90637 | 0.22888 | 0.93842 | 0.26093 | -0.045776 | 0.022888 | -122.7127 | 0.16022 | 0.23346 | -0.054932 | 0.27923 | -0.009156 | 1.0437 | 122.7173 | 0.20599 | 0.19226 | 122.8729 | 122.9279 | 122.8409 | 122.8821 | -122.8912 | -122.905 | 122.6852 | 0.14648 | 3.0304 | 1.6479
1142.1719 | 123.0652 | -57.0007 | 65.8585 | -0.12161 | 0.0019035 | 0.06523 | 0.070968 | -0.0013352 | 0.0021917 | 0.0060626 | -0.025757 | -0.00039305 | 0.00042723 | -0.006349 | -0.00065151 | -0.0028027 | -0.0023243 | -53.9841 | 65.8035 | -57.0328 | 65.6845 | -55.9937 | -56.8039 | -56.0898 | -55.481 | 65.831 | -57.0602 | -56.8451 | -56.8771 | -57.0511 | -56.7856 | -0.032044 | -0.054931 | -0.17395 | 1.0071 | 0.91095 | 0.19684 | 0.94299 | 0.22888 | -0.05951 | -0.027465 | -122.7036 | 0.1236 | 0.21515 | -0.050354 | 0.27466 | 0.009156 | 1.0391 | 122.7173 | 0.18311 | 0.21515 | 122.8363 | 122.8912 | 122.8043 | 122.8317 | -122.8912 | -122.9187 | 122.6852 | 0.15564 | 3.0167 | 1.5198
1143.1719 | 123.0789 | -57.0099 | 65.8356 | -0.15976 | -0.0010873 | 0.061598 | 0.070541 | -0.003685 | 0.0011237 | 0.0047808 | 0.026123 | 0.00088875 | 0.001068 | -0.0027174 | -0.0012925 | -0.0021619 | 0.00045294 | -53.9658 | 65.8081 | -57.019 | 65.6845 | -56.0165 | -56.7764 | -56.0852 | -55.4855 | 65.863 | -57.019 | -56.8268 | -56.8726 | -57.0831 | -56.7535 | -0.009155 | -0.027466 | -0.15106 | 0.99335 | 0.92468 | 0.23346 | 0.93384 | 0.24262 | -0.009155 | 0.027466 | -122.6624 | 0.13733 | 0.25635 | -0.073242 | 0.2655 | -0.064087 | 1.0025 | 122.7036 | 0.14648 | 0.19226 | 122.8271 | 122.8821 | 122.818 | 122.8729 | -122.8546 | -122.8546 | 122.6944 | 0.18311 | 3.0441 | 1.5244
1144.1719 | 123.0698 | -56.9962 | 65.8218 | -0.12924 | 0.00083526 | 0.064589 | 0.071395 | 0.0010148 | 0.0015509 | 0.0064898 | -0.0013428 | 0.00067495 | -0.00064077 | -0.0059216 | -0.0012925 | -0.0019483 | 0.00088014 | -53.8559 | 65.7806 | -57.0053 | 65.6982 | -55.9937 | -56.7856 | -56.0852 | -55.4901 | 65.863 | -57.0557 | -56.8085 | -56.8817 | -57.0786 | -56.7764 | -0.009155 | -0.041198 | -0.1236 | 1.0025 | 0.91095 | 0.21057 | 0.9201 | 0.21973 | -0.059509 | 0.041199 | -122.6303 | 0.11444 | 0.21973 | -0.082397 | 0.27924 | -0.022888 | 1.0117 | 122.7036 | 0.17395 | 0.24719 | 122.786 | 122.9187 | 122.7768 | 122.8592 | -122.8271 | -122.8775 | 122.6944 | 0.18768 | 3.1403 | 1.506
1145.1719 | 123.0423 | -56.987 | 65.8447 | -0.075836 | 0.0010489 | 0.062239 | 0.074172 | 0.00016017 | 0.0039007 | 0.0062762 | -0.044067 | 0.00067495 | 0.00064083 | 0.00091422 | -0.0038559 | -0.0017347 | -0.0016833 | -53.9246 | 65.8081 | -57.0465 | 65.6937 | -55.9845 | -56.7856 | -56.0623 | -55.5038 | 65.8401 | -57.0328 | -56.8176 | -56.8954 | -57.074 | -56.7856 | -0.059509 | -0.036622 | -0.15106 | 1.0025 | 0.92468 | 0.20142 | 0.98419 | 0.26093 | -0.045776 | -0.004578 | -122.6624 | 0.091553 | 0.20142 | -0.086975 | 0.24719 | -0.041199 | 1.062 | 122.7402 | 0.13733 | 0.21515 | 122.8546 | 122.8729 | 122.7951 | 122.8271 | -122.8912 | -122.8775 | 122.6807 | 0.16937 | 3.0624 | 1.4832
1146.1719 | 123.0698 | -57.0145 | 65.8264 | -0.083466 | 0.00019446 | 0.06288 | 0.073531 | -0.001976 | 0.00091009 | 0.007558 | -0.03186 | 0.0017431 | 0.00021363 | -0.00229 | -0.0027877 | -0.0015211 | -0.0012561 | -53.9154 | 65.799 | -57.019 | 65.6937 | -55.9662 | -56.7902 | -56.0715 | -55.4855 | 65.8356 | -57.0465 | -56.8085 | -56.8863 | -57.0602 | -56.7673 | -0.004578 | -0.027466 | -0.13275 | 1.0483 | 0.94299 | 0.2243 | 0.94757 | 0.22888 | -0.032044 | 0.009155 | -122.6349 | 0.12817 | 0.24719 | -0.045777 | 0.27924 | -0.013733 | 1.0529 | 122.7127 | 0.16022 | 0.23804 | 122.818 | 122.8821 | 122.8134 | 122.85 | -122.8455 | -122.8729 | 122.7081 | 0.20599 | 3.0991 | 1.5289
1147.1719 | 123.0331 | -57.0236 | 65.8356 | -0.091095 | 0.00062166 | 0.063521 | 0.072463 | -0.001976 | 5.5488e-05 | 0.0071308 | -0.010498 | 0.0011023 | 2.8e-08 | 0.0032642 | -0.0012925 | -0.0030163 | 0.00045294 | -53.9337 | 65.8173 | -57.0419 | 65.6754 | -55.9891 | -56.7856 | -56.0761 | -55.5222 | 65.8447 | -57.0511 | -56.813 | -56.8863 | -57.0694 | -56.7764 | -0.01831 | -0.01831 | -0.16022 | 1.0345 | 0.94757 | 0.23804 | 0.96588 | 0.25635 | -0.027465 | 0.009156 | -122.6486 | 0.13733 | 0.24719 | -0.045776 | 0.27466 | -0.018311 | 1.0529 | 122.7173 | 0.16479 | 0.23804 | 122.8592 | 122.8958 | 122.8409 | 122.8683 | -122.8775 | -122.8867 | 122.699 | 0.21057 | 3.0899 | 1.5015
1148.1719 | 123.0789 | -57.0007 | 65.831 | -0.15976 | -0.00023294 | 0.062025 | 0.074599 | -0.001976 | 0.0019781 | 0.0056354 | -0.0074462 | 0.00046135 | 0.0025634 | 0.0019824 | -0.0021469 | -0.0042981 | -0.00040166 | -53.8742 | 65.7669 | -57.0557 | 65.7166 | -55.9433 | -56.7764 | -56.0715 | -55.4901 | 65.8173 | -57.0602 | -56.8039 | -56.8817 | -57.0648 | -56.7673 | -0.054932 | -0.064087 | -0.11444 | 1.0574 | 0.92926 | 0.2243 | 0.98419 | 0.27924 | -0.05951 | -0.013733 | -122.6349 | 0.11902 | 0.23346 | -0.064087 | 0.29297 | -0.004577 | 1.1124 | 122.7722 | 0.17853 | 0.25635 | 122.8226 | 122.8775 | 122.7676 | 122.818 | -122.8867 | -122.8912 | 122.7173 | 0.19684 | 3.1265 | 1.5106
1149.1719 | 123.0881 | -57.0099 | 65.8447 | -0.075836 | 0.00062166 | 0.064375 | 0.073104 | -5.343e-05 | 0.0045417 | 0.0054218 | 0.059692 | 0.0017431 | 0.00064083 | 0.00048702 | -0.0015061 | -0.0025891 | 0.0013073 | -53.9062 | 65.8127 | -57.0145 | 65.6616 | -55.9799 | -56.781 | -56.0028 | -55.5908 | 65.8447 | -57.019 | -56.8176 | -56.8817 | -57.0465 | -56.7856 | -0.004577 | -0.032044 | -0.18311 | 1.03 | 1.0071 | 0.22888 | 1.0117 | 0.23346 | -0.009155 | 0 | -122.6624 | 0.12817 | 0.2243 | -0.036621 | 0.23346 | -0.027466 | 1.0345 | 122.6761 | 0.13733 | 0.20142 | 122.8271 | 122.8638 | 122.8226 | 122.8546 | -122.8592 | -122.8638 | 122.6715 | 0.19226 | 3.1036 | 1.4191
1150.1719 | 123.0515 | -56.9962 | 65.8218 | -0.12924 | -0.0013009 | 0.062239 | 0.073318 | 0.0035782 | 0.0017645 | 0.0073444 | -0.010498 | 0.0017431 | -0.00064077 | -0.00079478 | -0.0023605 | -0.0023755 | -0.00061526 | -53.8788 | 65.7852 | -57.0419 | 65.6891 | -55.9708 | -56.7947 | -56.0623 | -55.5267 | 65.8493 | -57.0465 | -56.8222 | -56.9 | -57.074 | -56.781 | -0.045776 | -0.036621 | -0.13275 | 1.0254 | 0.93384 | 0.20142 | 0.97961 | 0.24719 | -0.050354 | 0.027466 | -122.644 | 0.096131 | 0.21515 | -0.07782 | 0.2655 | -0.027466 | 1.0712 | 122.731 | 0.14648 | 0.2243 | 122.8271 | 122.8958 | 122.7814 | 122.8455 | -122.8638 | -122.8683 | 122.6852 | 0.17395 | 3.1174 | 1.4694
1151.1719 | 123.0789 | -57.0099 | 65.8081 | -0.15213 | 0.0025443 | 0.061598 | 0.073958 | -0.0017624 | -0.00058531 | 0.0073444 | -0.050171 | 0.0017431 | 0.00064083 | 0.0054004 | -0.0015061 | -0.00045288 | -0.0021107 | -53.8651 | 65.7944 | -57.0328 | 65.7257 | -55.9937 | -56.7398 | -56.0211 | -55.4718 | 65.8356 | -57.0557 | -56.7947 | -56.868 | -57.0465 | -56.7535 | -0.022888 | -0.013732 | -0.082397 | 1.0162 | 0.98877 | 0.27008 | 1.0117 | 0.29297 | -0.045776 | 0.027466 | -122.6028 | 0.14191 | 0.25635 | -0.036621 | 0.30212 | 0.009155 | 1.0391 | 122.7585 | 0.18768 | 0.26093 | 122.8271 | 122.8912 | 122.8043 | 122.8455 | -122.8409 | -122.8638 | 122.7356 | 0.21515 | 3.1448 | 1.5381
1152.1719 | 123.0606 | -57.019 | 65.799 | -0.15213 | -0.00044654 | 0.064589 | 0.07289 | -0.0024032 | 0.0026191 | 0.0071308 | -0.028809 | 0.0013159 | 0.0014954 | -0.001222 | 0.0012711 | -0.0040845 | -0.0012561 | -53.9337 | 65.7944 | -57.0419 | 65.7028 | -55.9479 | -56.7627 | -56.044 | -55.4947 | 65.8173 | -57.0557 | -56.8268 | -56.8863 | -57.0557 | -56.7673 | -0.022888 | -0.004577 | -0.09613 | 1.0712 | 0.97504 | 0.25635 | 0.99792 | 0.27924 | -0.036621 | 0.018311 | -122.6257 | 0.13275 | 0.25177 | -0.036621 | 0.28839 | 0 | 1.0941 | 122.7448 | 0.16937 | 0.22888 | 122.8363 | 122.8729 | 122.8134 | 122.8363 | -122.8409 | -122.8546 | 122.7219 | 0.19226 | 3.0853 | 1.5244
1153.1719 | 123.0972 | -57.0099 | 65.8081 | -0.10635 | 0.0016899 | 0.063948 | 0.073318 | 0.00016017 | 0.00026909 | 0.005849 | -0.034912 | 0.0015295 | 0.00021363 | -0.0031446 | -0.0021469 | -0.00066648 | -0.0025379 | -53.8651 | 65.7898 | -57.0465 | 65.7211 | -55.925 | -56.7444 | -56.0165 | -55.4947 | 65.8447 | -57.0602 | -56.8268 | -56.8771 | -57.0602 | -56.7444 | -0.036621 | -0.01831 | -0.086975 | 1.0849 | 0.99335 | 0.2655 | 1.03 | 0.30212 | -0.050354 | 0.036622 | -122.6349 | 0.13275 | 0.2655 | -0.050354 | 0.31586 | 0 | 1.1215 | 122.7676 | 0.18311 | 0.23346 | 122.8363 | 122.905 | 122.7997 | 122.8546 | -122.8546 | -122.8683 | 122.731 | 0.18311 | 3.1448 | 1.5152
1154.1719 | 123.0743 | -57.0053 | 65.7944 | -0.13687 | 0.0023307 | 0.067152 | 0.070968 | 0.0018692 | 0.0043281 | 0.0060626 | -0.01355 | 3.4148e-05 | 0.00021363 | -0.0031446 | -0.00065151 | -0.0015211 | 0.0019483 | -53.9383 | 65.7486 | -57.074 | 65.7303 | -55.8884 | -56.7764 | -56.0303 | -55.5267 | 65.8264 | -57.0648 | -56.7993 | -56.868 | -57.0419 | -56.7627 | -0.068665 | -0.045777 | -0.064087 | 1.1169 | 0.97504 | 0.22888 | 1.0437 | 0.29755 | -0.059509 | 0.032043 | -122.5937 | 0.13733 | 0.24262 | -0.036621 | 0.30212 | 0.022888 | 1.1856 | 122.8043 | 0.19684 | 0.2655 | 122.8226 | 122.8912 | 122.7539 | 122.8317 | -122.8683 | -122.8592 | 122.7356 | 0.20599 | 3.067 | 1.4786
1155.1719 | 123.0743 | -56.9916 | 65.8035 | -0.091095 | -1.9142e-05 | 0.064375 | 0.071822 | 0.0012284 | 0.0024053 | 0.0069172 | -0.016602 | 0.0023839 | 0.0014954 | -0.00464 | -0.0027877 | -0.0021619 | 0.00066654 | -53.8513 | 65.8081 | -57.019 | 65.6891 | -55.9158 | -56.7764 | -56.0532 | -55.5222 | 65.8081 | -57.0465 | -56.8314 | -56.8954 | -57.0648 | -56.781 | -0.027466 | 0.004577 | -0.11444 | 1.0757 | 0.93841 | 0.21515 | 0.96588 | 0.24262 | -0.054932 | 0.004577 | -122.6349 | 0.09613 | 0.21057 | -0.073242 | 0.2655 | -0.01831 | 1.1032 | 122.7081 | 0.15106 | 0.21515 | 122.8271 | 122.8546 | 122.7997 | 122.7997 | -122.8226 | -122.85 | 122.6807 | 0.16022 | 3.1403 | 1.4694
1156.1719 | 123.1064 | -57.0007 | 65.7852 | -0.15976 | 0.00062166 | 0.063948 | 0.07289 | 0.003151 | 0.0024053 | 0.0081988 | -0.025757 | 3.4148e-05 | 0.00064083 | 0.0017688 | -0.0021469 | -0.00045288 | -0.0038197 | -53.8239 | 65.7852 | -57.0145 | 65.7028 | -55.9296 | -56.7535 | -56.0211 | -55.5084 | 65.8264 | -57.0648 | -56.8222 | -56.8726 | -57.0648 | -56.7535 | -0.013733 | 0 | -0.082397 | 1.0712 | 0.97961 | 0.24719 | 0.99335 | 0.26093 | -0.064087 | 0.041199 | -122.6074 | 0.12817 | 0.24719 | -0.064087 | 0.31128 | 0 | 1.0849 | 122.7173 | 0.19226 | 0.24261 | 122.7997 | 122.8912 | 122.7859 | 122.8271 | -122.7997 | -122.85 | 122.7036 | 0.17853 | 3.1769 | 1.4923
1157.1719 | 123.1064 | -57.0099 | 65.8081 | -0.060578 | 0.0012625 | 0.06523 | 0.073958 | 0.0020828 | 0.0032599 | 0.0081988 | -0.06543 | -0.00060665 | -0.0014954 | 0.0032642 | -0.0025741 | -0.0019483 | -0.0031787 | -53.8284 | 65.7806 | -57.0511 | 65.6891 | -55.957 | -56.7627 | -56.044 | -55.5313 | 65.8356 | -57.074 | -56.813 | -56.8817 | -57.0648 | -56.7398 | -0.041198 | -0.027465 | -0.11902 | 1.0529 | 0.96588 | 0.24719 | 1.0071 | 0.28839 | -0.064087 | 0.027466 | -122.6212 | 0.12817 | 0.27008 | -0.054931 | 0.33417 | 0.009156 | 1.0941 | 122.7402 | 0.19226 | 0.26093 | 122.8317 | 122.9095 | 122.7905 | 122.8455 | -122.8592 | -122.8821 | 122.699 | 0.19684 | 3.1815 | 1.4786
1158.1719 | 123.1064 | -57.0007 | 65.8264 | -0.12924 | 0.0019035 | 0.064803 | 0.072036 | -0.00048063 | 0.0030463 | 0.0062762 | -0.037964 | -0.00060665 | 0.00085443 | 0.00091422 | -0.0017197 | -0.0015211 | 0.00066654 | -53.7964 | 65.7852 | -57.0419 | 65.744 | -56.1539 | -56.8497 | -55.9158 | -55.5496 | 65.8173 | -57.0511 | -56.813 | -56.8954 | -57.0419 | -56.7398 | -0.041199 | -0.041199 | -0.082397 | 0.84686 | 1.0849 | 0.15106 | 1.1261 | 0.19226 | -0.050354 | -0.009155 | -122.6395 | 0.10529 | 0.26093 | -0.041199 | 0.31128 | 0.009155 | 0.88806 | 122.7859 | 0.15564 | 0.23804 | 122.8271 | 122.8683 | 122.7859 | 122.818 | -122.8683 | -122.8775 | 122.7448 | 0.18768 | 3.2043 | 1.4511
1159.1719 | 123.1567 | -57.0053 | 65.8173 | -0.16739 | 0.00062166 | 0.065443 | 0.072677 | 0.00058737 | 0.0028327 | 0.007558 | -0.034912 | -0.00082025 | -0.00085457 | 0.0047594 | -0.00043791 | -0.0019483 | -0.0014697 | -53.7918 | 65.7532 | -57.0374 | 65.6799 | -55.9387 | -56.7581 | -56.0486 | -55.5313 | 65.799 | -57.0831 | -56.7764 | -56.7581 | -57.106 | -56.7856 | -0.032044 | -0.064087 | -0.13733 | 1.0666 | 0.95673 | 0.24719 | 0.98877 | 0.27924 | -0.07782 | -0.018311 | -122.5937 | 0.24719 | 0.21973 | -0.10071 | 0.29755 | -0.022888 | 1.0986 | 122.7173 | 0.32501 | 0.3067 | 122.7905 | 122.8821 | 122.7585 | 122.8043 | -122.8546 | -122.9004 | 122.6852 | 0.22888 | 3.2135 | 1.474
1160.1719 | 123.111 | -57.0053 | 65.7852 | -0.10635 | 0.00062166 | 0.065657 | 0.073958 | -0.0017624 | 0.0026191 | 0.0067036 | -0.062378 | 0.0019567 | 0.001068 | 0.0058276 | -0.0019333 | 0.00082892 | 0.0038709 | -53.746 | 65.7669 | -57.0328 | 65.7028 | -55.9387 | -56.7581 | -56.0669 | -55.545 | 65.8218 | -57.0465 | -56.8176 | -56.8863 | -57.0557 | -56.749 | -0.027466 | -0.01831 | -0.082397 | 1.0666 | 0.93841 | 0.24719 | 0.96588 | 0.27466 | -0.041199 | 0.036621 | -122.6028 | 0.11902 | 0.25635 | -0.050354 | 0.29755 | -0.009155 | 1.0941 | 122.7356 | 0.16022 | 0.22888 | 122.7997 | 122.8683 | 122.7722 | 122.8271 | -122.818 | -122.8317 | 122.7081 | 0.18768 | 3.2593 | 1.4603
1161.1719 | 123.1064 | -57.019 | 65.7944 | -0.11398 | 0.00040806 | 0.06523 | 0.075667 | -0.0026168 | 0.0013373 | 0.0096942 | -0.047119 | -0.00060665 | 0.00064083 | -0.0033582 | -0.0025741 | -0.0021619 | -0.0025379 | -53.7552 | 65.7349 | -57.074 | 65.7349 | -55.9845 | -56.7215 | -55.9845 | -55.5313 | 65.799 | -57.0694 | -56.8176 | -56.8771 | -57.0465 | -56.7627 | -0.054932 | -0.05951 | -0.05951 | 1.0345 | 1.0345 | 0.29755 | 1.0895 | 0.35248 | -0.050354 | 0.004577 | -122.612 | 0.14191 | 0.25635 | -0.027466 | 0.3067 | 0.022888 | 1.0895 | 122.8088 | 0.19226 | 0.25177 | 122.8088 | 122.8683 | 122.7539 | 122.818 | -122.8683 | -122.8638 | 122.7539 | 0.20142 | 3.2639 | 1.4877
1162.1719 | 123.0881 | -57.0099 | 65.7898 | -0.13687 | 0.0031851 | 0.063094 | 0.072036 | 0.003151 | 0.0039007 | 0.00414 | -0.053223 | -0.0023157 | 2.8e-08 | 0.0030506 | 0.00020289 | -0.0025891 | 0.0023755 | -53.7506 | 65.7669 | -57.0511 | 65.6891 | -55.9341 | -56.7535 | -56.0989 | -55.4031 | 65.7944 | -57.0511 | -56.813 | -56.8771 | -57.074 | -56.7627 | -0.041198 | -0.022888 | -0.10071 | 1.0757 | 0.91095 | 0.25635 | 0.95215 | 0.29755 | -0.041198 | 0.004578 | -122.6028 | 0.13275 | 0.24719 | -0.064087 | 0.28839 | -0.022889 | 1.1169 | 122.7402 | 0.17395 | 0.23804 | 122.818 | 122.8455 | 122.7768 | 122.8043 | -122.8409 | -122.8409 | 122.699 | 0.19684 | 3.2593 | 1.6068
1163.1719 | 123.0652 | -57.0145 | 65.7944 | -0.11398 | -1.9142e-05 | 0.066084 | 0.073318 | -0.0017624 | 0.0053961 | 0.0090534 | -0.010498 | 3.4148e-05 | 0.001068 | -0.0054944 | -0.0015061 | -0.0021619 | -0.0010425 | -53.7781 | 65.7715 | -57.0465 | 65.6799 | -55.925 | -56.7673 | -56.0303 | -55.5496 | 65.7944 | -57.0648 | -56.8405 | -56.9092 | -57.0831 | -56.7902 | -0.032044 | -0.022889 | -0.11444 | 1.0895 | 0.98419 | 0.24719 | 1.0162 | 0.27924 | -0.050354 | 0 | -122.6349 | 0.10529 | 0.2243 | -0.068665 | 0.27466 | -0.018311 | 1.1215 | 122.7264 | 0.15564 | 0.2243 | 122.818 | 122.8592 | 122.7859 | 122.8088 | -122.8409 | -122.8592 | 122.6944 | 0.17395 | 3.2364 | 1.4648
1164.1719 | 123.0881 | -57.0465 | 65.7898 | -0.12161 | 0.0019035 | 0.065016 | 0.07524 | 0.00037377 | 0.0015509 | 0.0064898 | -0.047119 | 0.0017431 | 2.8e-08 | 0.0081774 | -1.0706e-05 | -0.00088008 | 0.0015209 | -53.8193 | 65.7944 | -57.0923 | 65.6204 | -56.0349 | -56.8359 | -56.1081 | -55.6274 | 65.8447 | -57.0923 | -56.8771 | -56.9092 | -57.106 | -56.7673 | -0.045776 | 0.004578 | -0.16937 | 1.0117 | 0.93842 | 0.21057 | 0.98419 | 0.25635 | -0.045776 | 0.054932 | -122.6669 | 0.13733 | 0.27924 | -0.059509 | 0.32501 | -0.013733 | 1.0574 | 122.7127 | 0.1831 | 0.21515 | 122.8867 | 122.937 | 122.8409 | 122.8912 | -122.8821 | -122.8821 | 122.6669 | 0.16937 | 3.2272 | 1.4191
1165.1719 | 123.0927 | -57.0419 | 65.7715 | -0.12924 | 0.0021171 | 0.063948 | 0.073104 | -0.001976 | 0.0032599 | 0.0049946 | -0.028809 | 0.00046135 | 0.0019226 | -0.001222 | -0.00043791 | 0.00018792 | -0.0018971 | -53.746 | 65.7852 | -57.0557 | 65.6754 | -55.9479 | -56.7535 | -56.0303 | -55.5679 | 65.8127 | -57.0786 | -56.8359 | -56.8863 | -57.0923 | -56.7627 | -0.013733 | 0.013733 | -0.09613 | 1.0941 | 1.0117 | 0.28839 | 1.0254 | 0.30212 | -0.036621 | 0.041199 | -122.6074 | 0.15564 | 0.27924 | -0.050354 | 0.31586 | -0.013733 | 1.1078 | 122.731 | 0.19226 | 0.24262 | 122.8409 | 122.8912 | 122.8271 | 122.8546 | -122.8271 | -122.85 | 122.7173 | 0.20599 | 3.2959 | 1.474
1166.1719 | 123.0972 | -57.0236 | 65.7761 | -0.11398 | 0.0012625 | 0.062666 | 0.073958 | 0.0027238 | 0.0026191 | 0.0084124 | -0.010498 | 0.0013159 | 2.8e-08 | 0.0017688 | -0.0027877 | -0.0017347 | -0.0036059 | -53.7735 | 65.7761 | -57.0602 | 65.6799 | -55.9616 | -56.781 | -56.0623 | -55.6 | 65.8173 | -57.0557 | -56.8359 | -56.9092 | -57.0786 | -56.749 | -0.036621 | 0 | -0.09613 | 1.062 | 0.9613 | 0.24262 | 0.99793 | 0.27924 | -0.032043 | 0.041199 | -122.612 | 0.11444 | 0.27466 | -0.054931 | 0.3067 | -0.022888 | 1.0986 | 122.7402 | 0.14648 | 0.21973 | 122.8363 | 122.8729 | 122.7997 | 122.8409 | -122.8363 | -122.8317 | 122.7036 | 0.18768 | 3.2501 | 1.4236
1167.1719 | 123.1018 | -57.0053 | 65.7852 | -0.083466 | 0.00019446 | 0.06523 | 0.073531 | -0.0041122 | 0.0011237 | 0.0039264 | -0.041016 | 0.0021703 | 0.00085443 | 0.00027342 | -0.0027877 | -0.0010937 | 0.00023934 | -53.7872 | 65.7806 | -57.074 | 65.6342 | -55.9845 | -56.8039 | -56.0852 | -55.6137 | 65.8127 | -57.0648 | -56.8359 | -56.9046 | -57.0877 | -56.7764 | -0.068665 | -0.004577 | -0.15106 | 1.0208 | 0.9201 | 0.20142 | 0.98877 | 0.27008 | -0.059509 | 0.027466 | -122.6212 | 0.10071 | 0.22888 | -0.082398 | 0.28839 | -0.022889 | 1.0895 | 122.7081 | 0.16022 | 0.22888 | 122.8546 | 122.8775 | 122.786 | 122.818 | -122.8592 | -122.85 | 122.6395 | 0.16937 | 3.2181 | 1.3916
1168.1719 | 123.1384 | -57.019 | 65.7852 | -0.1445 | 0.0019035 | 0.065657 | 0.073104 | 0.00058737 | 0.0039007 | 0.0096942 | -0.028809 | 0.0011023 | 0.00064083 | -0.00058098 | -0.0017197 | -0.00045288 | -0.0068103 | -53.7415 | 65.7669 | -57.074 | 65.6937 | -55.9341 | -56.7535 | -56.044 | -55.5862 | 65.7898 | -57.0969 | -56.8726 | -57.0648 | -56.9687 | -56.6757 | -0.054932 | -0.01831 | -0.091552 | 1.0849 | 0.97504 | 0.2655 | 1.03 | 0.32043 | -0.07782 | 0.004578 | -122.6578 | -0.045776 | 0.34332 | 0.050354 | 0.42114 | 0.12817 | 1.1398 | 122.7676 | 0.032044 | 0.2243 | 122.8409 | 122.8867 | 122.786 | 122.8088 | -122.8592 | -122.8821 | 122.7127 | 0.14648 | 3.2776 | 1.4328
1169.1719 | 123.0515 | -57.0511 | 65.8035 | -0.068207 | 0.0038261 | 0.063094 | 0.074599 | -0.00090783 | 0.0015509 | 0.0062762 | -0.028809 | -0.00060665 | 0.00021363 | 0.0024096 | -0.0010787 | -0.0023755 | 0.0013073 | -53.7781 | 65.8173 | -57.074 | 65.5838 | -56.0165 | -56.8405 | -56.0989 | -55.6732 | 65.8447 | -57.0923 | -56.8771 | -56.9366 | -57.1152 | -56.8085 | -0.022889 | 0.013733 | -0.21973 | 1.0345 | 0.95215 | 0.21057 | 0.97504 | 0.23346 | -0.041199 | 0.041199 | -122.6807 | 0.11444 | 0.24261 | -0.064087 | 0.28381 | -0.022888 | 1.0574 | 122.6578 | 0.15564 | 0.21515 | 122.8912 | 122.937 | 122.8683 | 122.8958 | -122.8775 | -122.8958 | 122.6349 | 0.17395 | 3.273 | 1.3779
1170.1719 | 123.0927 | -57.0511 | 65.7761 | -0.068207 | 0.00083526 | 0.062453 | 0.073745 | -0.00069423 | 0.0015509 | 0.0047808 | 0.001709 | 0.00088875 | -0.00021357 | -0.00058098 | -0.00086511 | -0.0013073 | 2.554e-05 | -53.6545 | 65.7623 | -57.0374 | 65.6799 | -55.9021 | -56.7856 | -56.0303 | -55.5679 | 65.799 | -57.074 | -56.8726 | -56.9 | -57.0831 | -56.7764 | 0.013732 | -0.013733 | -0.09613 | 1.149 | 1.0208 | 0.2655 | 1.0071 | 0.25177 | -0.022889 | 0.022888 | -122.6486 | 0.15106 | 0.27466 | -0.032044 | 0.29755 | -0.009155 | 1.1353 | 122.7173 | 0.17395 | 0.20142 | 122.7997 | 122.8729 | 122.8134 | 122.85 | -122.8134 | -122.85 | 122.731 | 0.17853 | 3.3966 | 1.4832
1171.1719 | 123.0606 | -57.0328 | 65.7944 | -0.13687 | 0.00062166 | 0.063948 | 0.072463 | 0.00037377 | 0.0030463 | 0.0086262 | 0.001709 | 0.0015295 | 0.0012818 | -0.0042126 | 0.00020289 | -0.0017347 | 0.0017345 | -53.7506 | 65.7578 | -57.0419 | 65.657 | -55.9341 | -56.781 | -56.0211 | -55.6183 | 65.7806 | -57.106 | -56.868 | -56.9321 | -57.0877 | -56.7993 | -0.009155 | -0.036622 | -0.13733 | 1.0986 | 1.0117 | 0.25177 | 1.0208 | 0.26093 | -0.073242 | -0.013733 | -122.6624 | 0.10071 | 0.23346 | -0.054932 | 0.3067 | 0.01831 | 1.1078 | 122.699 | 0.17395 | 0.23804 | 122.7997 | 122.8867 | 122.7905 | 122.8134 | -122.8363 | -122.9004 | 122.6898 | 0.16479 | 3.2822 | 1.4145
1172.1719 | 123.0377 | -57.0557 | 65.8035 | -0.098725 | 0.0014761 | 0.064803 | 0.074386 | 0.0018692 | 0.0028327 | 0.0062762 | -0.041016 | 0.0015295 | 0.0029906 | 0.0064684 | -0.0017197 | -0.0023755 | 0.0034435 | -53.8147 | 65.8218 | -57.0831 | 65.5609 | -56.044 | -56.8542 | -56.1172 | -55.7053 | 65.8218 | -57.1152 | -56.9183 | -56.9916 | -57.1609 | -56.8497 | -0.027466 | 0.01831 | -0.24262 | 1.0117 | 0.93841 | 0.20142 | 0.96588 | 0.22888 | -0.059509 | 0.01831 | -122.7219 | 0.064087 | 0.20599 | -0.10529 | 0.2655 | -0.045777 | 1.0391 | 122.644 | 0.1236 | 0.19684 | 122.905 | 122.937 | 122.8775 | 122.8775 | -122.8867 | -122.9187 | 122.6166 | 0.13733 | 3.241 | 1.3504
1173.1719 | 123.1247 | -57.0557 | 65.7898 | -0.12161 | 0.0014761 | 0.065016 | 0.073745 | 0.00251 | 0.0015509 | 0.010121 | 0.026123 | 0.0011023 | 0.001709 | 0.0030506 | -0.0010787 | 0.00018792 | -0.00061526 | -53.7689 | 65.7623 | -57.0557 | 65.7349 | -56.0715 | -56.9092 | -55.9341 | -55.6229 | 65.7852 | -57.0694 | -56.8451 | -56.9046 | -57.074 | -56.7719 | 0 | -0.027466 | -0.054932 | 0.98419 | 1.1215 | 0.14648 | 1.1215 | 0.14648 | -0.013733 | -0.004578 | -122.6349 | 0.15106 | 0.28381 | -0.018311 | 0.29755 | -0.004578 | 0.98419 | 122.7905 | 0.1648 | 0.2243 | 122.818 | 122.8546 | 122.818 | 122.8409 | -122.8455 | -122.8592 | 122.7905 | 0.21057 | 3.2867 | 1.4328
1174.1719 | 123.1201 | -57.0282 | 65.7578 | -0.098725 | 0.00062166 | 0.066939 | 0.074172 | -0.0024032 | 0.0026191 | 0.0071308 | -0.053223 | 0.00088875 | 0.00021363 | 0.00091422 | -0.0023605 | -0.0030163 | 0.0023755 | -53.7552 | 65.7532 | -57.0419 | 65.6708 | -55.9296 | -56.7627 | -56.0074 | -55.6 | 65.7486 | -57.0831 | -56.8314 | -56.9092 | -57.0831 | -56.7627 | -0.013733 | -0.004577 | -0.086975 | 1.0986 | 1.0208 | 0.2655 | 1.0345 | 0.27924 | -0.054932 | -0.009155 | -122.5891 | 0.11902 | 0.2655 | -0.054932 | 0.32043 | 0 | 1.1124 | 122.7127 | 0.17395 | 0.25177 | 122.7951 | 122.8317 | 122.7814 | 122.7768 | -122.7997 | -122.8409 | 122.699 | 0.19684 | 3.273 | 1.4282
1175.1719 | 123.1247 | -57.0374 | 65.7623 | -0.068207 | 0.0010489 | 0.063734 | 0.072463 | 0.001442 | 0.0028327 | 0.010549 | -0.022705 | -0.00017945 | -0.00042717 | -0.00058098 | -0.0042831 | -0.0032301 | -0.0021107 | -53.7598 | 65.7486 | -57.0282 | 65.6754 | -55.9204 | -56.7535 | -56.012 | -55.6046 | 65.8127 | -57.0831 | -56.8222 | -56.9183 | -57.0511 | -56.7398 | 0.009156 | -0.013733 | -0.086975 | 1.1169 | 1.0254 | 0.28381 | 1.0162 | 0.27466 | -0.045776 | 0.050354 | -122.5845 | 0.11902 | 0.29755 | -0.013732 | 0.34332 | 0.032044 | 1.1078 | 122.7036 | 0.16479 | 0.26093 | 122.7768 | 122.8958 | 122.786 | 122.85 | -122.7905 | -122.8455 | 122.7127 | 0.21515 | 3.2776 | 1.4328
1176.1719 | 122.9691 | -57.0419 | 65.863 | -0.11398 | -0.00023294 | 0.064375 | 0.073958 | 0.00080117 | 0.0036871 | 0.0062762 | 0.0047608 | 0.0019567 | -0.0014954 | -0.0044262 | -0.0012925 | -0.0017347 | 0.00088014 | -53.801 | 65.8493 | -57.0282 | 65.6158 | -55.9937 | -56.7673 | -56.0303 | -55.7007 | 65.8722 | -57.0694 | -56.9366 | -56.955 | -57.1243 | -56.8405 | 0.013733 | -0.013733 | -0.24719 | 1.0483 | 1.0117 | 0.27466 | 0.99793 | 0.26093 | -0.027466 | 0.009155 | -122.7997 | 0.086975 | 0.20142 | -0.082398 | 0.22888 | -0.054932 | 1.0345 | 122.644 | 0.11444 | 0.13275 | 122.8775 | 122.9416 | 122.8912 | 122.9141 | -122.8912 | -122.9324 | 122.6578 | 0.10528 | 3.241 | 1.3412
1177.1719 | 123.0377 | -57.0877 | 65.7303 | -0.18265 | 0.0014761 | 0.064803 | 0.075881 | 0.00016017 | 0.0053961 | 0.0099078 | -0.037964 | 0.00024775 | -0.00021357 | 0.001128 | -0.0021469 | -0.0015211 | 0.0038709 | -53.7643 | 65.7623 | -57.0557 | 65.6754 | -55.9341 | -56.7581 | -56.0074 | -55.6274 | 65.7761 | -57.0969 | -56.8497 | -56.9 | -57.0831 | -56.6574 | 0.032044 | 0.032043 | -0.054932 | 1.1536 | 1.0803 | 0.32959 | 1.0483 | 0.29755 | -0.009155 | 0.045776 | -122.58 | 0.18768 | 0.4303 | 0.004578 | 0.43945 | 0.013733 | 1.1215 | 122.731 | 0.19684 | 0.24719 | 122.818 | 122.8729 | 122.85 | 122.8638 | -122.786 | -122.8271 | 122.7631 | 0.23804 | 3.3234 | 1.4603
1178.1719 | 123.1201 | -57.0374 | 65.7852 | -0.098725 | 0.0023307 | 0.066084 | 0.076736 | 0.0033646 | 0.0041143 | 0.011403 | -0.0074462 | -0.00017945 | -0.00085457 | -0.001222 | -0.00022431 | -0.0030163 | -0.0023243 | -53.8147 | 65.7532 | -57.0511 | 65.657 | -55.9433 | -56.7673 | -56.0211 | -55.6229 | 65.799 | -57.106 | -56.8451 | -56.9046 | -57.0923 | -56.7673 | -0.013732 | -0.032043 | -0.12817 | 1.0941 | 1.0162 | 0.27008 | 1.03 | 0.28381 | -0.068664 | 0.013733 | -122.6303 | 0.13275 | 0.27008 | -0.054931 | 0.33874 | 0.013733 | 1.1078 | 122.7081 | 0.20142 | 0.26093 | 122.8043 | 122.905 | 122.7905 | 122.8363 | -122.8363 | -122.8912 | 122.6944 | 0.19226 | 3.2227 | 1.4145
1179.1719 | 123.1384 | -57.0602 | 65.7715 | -0.16739 | 0.0021171 | 0.063734 | 0.07225 | 0.0029374 | 0.0039007 | 0.0086262 | -0.01355 | 0.00067495 | -0.0021362 | -0.0014356 | -0.0019333 | -0.0017347 | 2.554e-05 | -53.833 | 65.7486 | -57.0602 | 65.6433 | -55.9479 | -56.7993 | -56.0257 | -55.6503 | 65.7806 | -57.0877 | -56.8634 | -56.9275 | -57.106 | -56.781 | 0 | -0.022888 | -0.12817 | 1.1124 | 1.0345 | 0.26093 | 1.0345 | 0.26093 | -0.027466 | 0.009156 | -122.6349 | 0.13275 | 0.27924 | -0.045776 | 0.3067 | -0.01831 | 1.1124 | 122.7036 | 0.16022 | 0.22431 | 122.8088 | 122.8683 | 122.8088 | 122.8409 | -122.8317 | -122.8592 | 122.7036 | 0.19684 | 3.2272 | 1.4099
1180.1719 | 123.0789 | -57.0694 | 65.7532 | -0.10635 | -0.00044654 | 0.063948 | 0.074813 | 0.0020828 | 0.0043281 | 0.0086262 | -0.016602 | -0.0014613 | 0.001709 | 0.002196 | -0.0032151 | -0.0013073 | 0.0017345 | -53.8559 | 65.7669 | -57.074 | 65.6433 | -55.9525 | -56.7719 | -56.0486 | -55.687 | 65.7944 | -57.0786 | -56.8588 | -56.9229 | -57.1243 | -56.781 | -0.004578 | 0.013733 | -0.10986 | 1.1169 | 1.0208 | 0.29755 | 1.0254 | 0.30212 | -0.009155 | 0.041199 | -122.612 | 0.14648 | 0.28839 | -0.054932 | 0.29755 | -0.045777 | 1.1215 | 122.7173 | 0.15564 | 0.21973 | 122.8409 | 122.8729 | 122.8363 | 122.8638 | -122.8271 | -122.8317 | 122.7127 | 0.21057 | 3.2135 | 1.3824
1181.1719 | 123.1018 | -57.019 | 65.7944 | -0.12924 | -0.00023294 | 0.064803 | 0.072677 | -0.001976 | 0.0034735 | 0.0088398 | 0.03833 | -0.00039305 | 0.0019226 | -0.0025036 | 0.00063009 | -0.0030163 | 0.0019483 | -53.8193 | 65.8127 | -57.0236 | 65.6662 | -55.9113 | -56.7261 | -55.9662 | -55.632 | 65.799 | -57.074 | -56.8497 | -56.8771 | -57.0419 | -56.7627 | -0.004578 | 0.01831 | -0.12817 | 1.1078 | 1.0529 | 0.29297 | 1.0574 | 0.29755 | -0.054932 | 0.004577 | -122.644 | 0.14191 | 0.25635 | -0.022888 | 0.31128 | 0.032044 | 1.1124 | 122.6898 | 0.19684 | 0.2243 | 122.8363 | 122.8729 | 122.8317 | 122.818 | -122.818 | -122.8683 | 122.6852 | 0.16937 | 3.1998 | 1.387
1182.1719 | 123.1064 | -57.0328 | 65.8127 | -0.13687 | -0.0013009 | 0.064589 | 0.073745 | 0.00037377 | 0.0034735 | 0.0084124 | -0.037964 | 0.00088875 | 0.00042723 | -0.0010084 | -0.0021469 | -0.0057935 | 2.554e-05 | -53.8055 | 65.7623 | -57.0648 | 65.6662 | -55.9158 | -56.7719 | -55.9982 | -55.632 | 65.7761 | -57.0877 | -56.7947 | -56.9412 | -57.0602 | -56.7581 | -0.032043 | -0.050354 | -0.14648 | 1.1169 | 1.0345 | 0.26093 | 1.0666 | 0.29297 | -0.054932 | -0.036621 | -122.6074 | 0.091553 | 0.27466 | -0.027466 | 0.32959 | 0.027466 | 1.149 | 122.731 | 0.14648 | 0.29297 | 122.8271 | 122.8638 | 122.7951 | 122.8088 | -122.8775 | -122.9004 | 122.699 | 0.23804 | 3.2272 | 1.4008
1183.1719 | 123.0789 | -57.0511 | 65.7532 | -0.11398 | -0.00066014 | 0.064162 | 0.074172 | -0.0017624 | 0.0036871 | 0.0084124 | -0.041016 | 0.0043065 | 0.00064083 | 0.003905 | -0.0021469 | -0.0025891 | -0.00061526 | -53.8834 | 65.7852 | -57.0831 | 65.6021 | -56.012 | -56.8268 | -56.0761 | -55.7144 | 65.7852 | -57.1014 | -56.9046 | -56.955 | -57.1381 | -56.8085 | -0.032044 | 0.032043 | -0.15106 | 1.0391 | 0.97504 | 0.2243 | 1.0071 | 0.25635 | -0.050354 | 0.032043 | -122.6578 | 0.09613 | 0.24261 | -0.086976 | 0.29297 | -0.036622 | 1.0712 | 122.6852 | 0.14648 | 0.19684 | 122.8683 | 122.8867 | 122.8363 | 122.8363 | -122.8363 | -122.8546 | 122.6532 | 0.14648 | 3.1677 | 1.3367
1184.1719 | 123.1338 | -57.0557 | 65.7166 | -0.12924 | 0.0010489 | 0.064589 | 0.075667 | 0.00058737 | 0.0024053 | 0.0086262 | -0.037964 | 0.00088875 | 0.00042723 | 0.0015552 | -0.0030013 | -0.0019483 | 0.0021619 | -53.8376 | 65.7303 | -57.0602 | 65.6525 | -55.925 | -56.7581 | -55.9982 | -55.6686 | 65.7806 | -57.074 | -56.8542 | -56.9183 | -57.0877 | -56.7719 | -0.004578 | 0.013733 | -0.064087 | 1.1307 | 1.0574 | 0.29755 | 1.062 | 0.30212 | -0.018311 | 0.064087 | -122.5708 | 0.13733 | 0.28381 | -0.032044 | 0.30212 | -0.013733 | 1.1353 | 122.7127 | 0.15564 | 0.21973 | 122.7905 | 122.8546 | 122.786 | 122.8363 | -122.7768 | -122.7905 | 122.7081 | 0.20142 | 3.2181 | 1.387
1185.1719 | 123.0423 | -57.0831 | 65.7944 | -0.037689 | 0.00062166 | 0.06288 | 0.076736 | -0.0013352 | 0.0034735 | 0.0062762 | -0.034912 | 0.0017431 | 0.0019226 | 0.00048702 | -0.0015061 | -0.0021619 | -0.0012561 | -53.9017 | 65.8127 | -57.0648 | 65.5701 | -56.0257 | -56.8588 | -56.0761 | -55.7693 | 65.799 | -57.1106 | -56.9229 | -56.9733 | -57.1564 | -56.8451 | 0.018311 | 0.01831 | -0.2243 | 1.0574 | 1.0071 | 0.2243 | 0.98877 | 0.20599 | -0.027466 | 0.004577 | -122.7173 | 0.10986 | 0.23804 | -0.073242 | 0.2655 | -0.045776 | 1.0391 | 122.6349 | 0.13733 | 0.18768 | 122.8775 | 122.9095 | 122.8958 | 122.8821 | -122.8592 | -122.905 | 122.6532 | 0.16022 | 3.1815 | 1.3138
1186.1719 | 123.1064 | -57.0374 | 65.7944 | 0.084381 | 0.0016899 | 0.066725 | 0.072463 | 0.00016017 | 0.0024053 | 0.0062762 | 0.02002 | 0.0011023 | 0.0019226 | -0.0035718 | -1.0706e-05 | -0.0013073 | 0.0017345 | -53.8971 | 65.7761 | -57.0419 | 65.6158 | -55.957 | -56.7581 | -56.012 | -55.6915 | 65.8081 | -57.0557 | -56.9046 | -56.9183 | -57.0831 | -56.781 | -0.004577 | -0.018311 | -0.17853 | 1.0803 | 1.0254 | 0.27924 | 1.03 | 0.28381 | -0.01831 | 0.013732 | -122.699 | 0.11902 | 0.25635 | -0.045776 | 0.27466 | -0.027466 | 1.0849 | 122.6578 | 0.13733 | 0.15106 | 122.818 | 122.8638 | 122.8134 | 122.8455 | -122.8363 | -122.85 | 122.6532 | 0.13275 | 3.1403 | 1.3458
1187.1719 | 123.1018 | -57.0557 | 65.7806 | -0.091095 | 0.00083526 | 0.064589 | 0.073318 | -0.0021896 | 0.0036871 | 0.0086262 | -0.037964 | -0.0018885 | -0.00021357 | 0.0058276 | -0.0027877 | -0.0015211 | -0.0063831 | -53.8651 | 65.7303 | -57.0511 | 65.6708 | -55.925 | -56.7719 | -56.0852 | -55.4855 | 65.7806 | -57.0831 | -56.868 | -56.9138 | -57.0969 | -56.781 | 0.004578 | -0.050354 | -0.10986 | 1.1307 | 0.97046 | 0.28381 | 0.96588 | 0.27923 | -0.027466 | 0 | -122.6486 | 0.14191 | 0.27466 | -0.041199 | 0.30212 | -0.013733 | 1.1261 | 122.7219 | 0.16937 | 0.21515 | 122.7814 | 122.8638 | 122.786 | 122.8363 | -122.8317 | -122.8638 | 122.7264 | 0.18768 | 3.1906 | 1.5701
1188.1719 | 123.0972 | -57.0282 | 65.7669 | -0.083466 | 0.0016899 | 0.065443 | 0.074599 | 0.00080117 | 0.0024053 | 0.0062762 | -0.034912 | 0.0023839 | -0.0032044 | 0.0034778 | -0.0030013 | -0.00045288 | 2.554e-05 | -53.9291 | 65.7486 | -57.0831 | 65.593 | -55.9937 | -56.8085 | -56.0349 | -55.7007 | 65.799 | -57.0923 | -56.8863 | -56.9183 | -57.1152 | -56.7856 | -0.054932 | -0.018311 | -0.17395 | 1.0345 | 0.99335 | 0.21973 | 1.0483 | 0.27466 | -0.064087 | 0.032043 | -122.6532 | 0.10986 | 0.24262 | -0.086975 | 0.3067 | -0.022888 | 1.0895 | 122.6761 | 0.17395 | 0.20599 | 122.8317 | 122.8912 | 122.7768 | 122.8271 | -122.85 | -122.8592 | 122.6212 | 0.14191 | 3.0991 | 1.3275
1189.1719 | 123.0972 | -57.0236 | 65.7944 | -0.075836 | -0.0015145 | 0.065016 | 0.074172 | -0.00090783 | 0.0034735 | 0.0081988 | -0.022705 | 0.0013159 | 0.001068 | -0.0014356 | -0.0012925 | 0.0016833 | -0.0053149 | -53.8788 | 65.7303 | -57.0602 | 65.6662 | -55.9387 | -56.749 | -55.9891 | -55.6595 | 65.7715 | -57.0969 | -56.9321 | -56.8314 | -56.9229 | -56.7398 | -0.036621 | -0.064087 | -0.12817 | 1.0849 | 1.0345 | 0.27466 | 1.0712 | 0.31128 | -0.073242 | -0.022889 | -122.7264 | 0.19226 | 0.28381 | 0.10071 | 0.35706 | 0.17395 | 1.1215 | 122.7264 | 0.2655 | 0.16479 | 122.7905 | 122.8683 | 122.7539 | 122.7951 | -122.8546 | -122.8912 | 122.6898 | 0.091553 | 3.1448 | 1.3641
1190.1719 | 123.0835 | -57.0557 | 65.7669 | -0.12924 | 0.0016899 | 0.065657 | 0.073958 | -0.00090783 | 0.0013373 | 0.0088398 | -0.047119 | -0.00017945 | 0.0012818 | -0.0016492 | -0.00043791 | 0.0010425 | -0.00061526 | -53.9932 | 65.7715 | -57.1014 | 65.5838 | -56.012 | -56.8451 | -56.0532 | -55.7465 | 65.8081 | -57.1014 | -56.9 | -56.9641 | -57.1426 | -56.813 | -0.045776 | 0.004577 | -0.18311 | 1.0437 | 1.0025 | 0.21057 | 1.0483 | 0.25635 | -0.045776 | 0.041198 | -122.6669 | 0.091553 | 0.24262 | -0.086975 | 0.28839 | -0.041199 | 1.0895 | 122.6852 | 0.13733 | 0.20142 | 122.8729 | 122.9095 | 122.8271 | 122.8638 | -122.8683 | -122.8683 | 122.6395 | 0.15564 | 3.0624 | 1.3092
1191.1719 | 123.1155 | -57.019 | 65.7532 | -0.1445 | -0.00023294 | 0.064375 | 0.071822 | 0.001442 | 0.00069649 | 0.0084124 | -0.028809 | 0.00046135 | 0.002777 | -0.0025036 | -0.00065151 | -0.0010937 | 2.554e-05 | -53.9566 | 65.7715 | -57.0694 | 65.6433 | -55.9204 | -56.749 | -56.0028 | -55.6778 | 65.7944 | -57.0831 | -56.8817 | -56.9183 | -57.0923 | -56.7856 | -0.050354 | 0.01831 | -0.10986 | 1.0986 | 1.0162 | 0.27008 | 1.0666 | 0.32044 | -0.064087 | 0.041199 | -122.6349 | 0.10071 | 0.23346 | -0.073242 | 0.29755 | -0.009155 | 1.149 | 122.7127 | 0.16479 | 0.20142 | 122.8409 | 122.8775 | 122.7905 | 122.8134 | -122.8226 | -122.8363 | 122.6624 | 0.13733 | 3.0624 | 1.3412
1192.1719 | 123.1201 | -57.0602 | 65.7578 | -0.060578 | 0.0014761 | 0.063521 | 0.075027 | 0.0033646 | 0.0051825 | 0.007558 | -0.028809 | -0.0016749 | -0.00021357 | 0.0015552 | -0.0032151 | -0.0019483 | 0.00066654 | -53.952 | 65.7394 | -57.0511 | 65.625 | -55.9296 | -56.7581 | -55.9845 | -55.687 | 65.7852 | -57.0786 | -56.8817 | -56.9366 | -57.106 | -56.7719 | 0.009156 | -0.01831 | -0.13275 | 1.1307 | 1.0757 | 0.30212 | 1.0666 | 0.29297 | -0.01831 | 0.027466 | -122.6395 | 0.1236 | 0.28839 | -0.045776 | 0.3067 | -0.027466 | 1.1215 | 122.6761 | 0.14191 | 0.19684 | 122.7905 | 122.8638 | 122.7997 | 122.8455 | -122.8088 | -122.8363 | 122.6852 | 0.17853 | 3.1082 | 1.3733
1193.1719 | 123.0377 | -57.0786 | 65.7761 | -0.11398 | 0.0012625 | 0.064589 | 0.074813 | 0.0010148 | 0.0028327 | 0.0094806 | -0.047119 | 0.0023839 | 0.001709 | 0.0049732 | -0.00086511 | -0.0017347 | 0.00045294 | -53.9978 | 65.7944 | -57.0831 | 65.5472 | -56.0303 | -56.868 | -56.0898 | -55.7739 | 65.8173 | -57.1152 | -56.955 | -57.0053 | -57.193 | -56.868 | -0.004578 | 0.018311 | -0.22888 | 1.0483 | 0.98877 | 0.21057 | 0.99335 | 0.21515 | -0.036621 | 0.041199 | -122.731 | 0.073242 | 0.21057 | -0.11444 | 0.24719 | -0.07782 | 1.0529 | 122.6303 | 0.10986 | 0.16022 | 122.8775 | 122.9324 | 122.8729 | 122.8958 | -122.8592 | -122.8912 | 122.6257 | 0.1236 | 3.0807 | 1.3046
1194.1719 | 123.0835 | -57.0465 | 65.7761 | -0.060578 | 0.0016899 | 0.064375 | 0.07225 | 0.00058737 | 0.0030463 | 0.009267 | -0.016602 | 3.4148e-05 | -0.0010682 | -0.00229 | -0.0027877 | -0.00023928 | -0.00018806 | -53.9062 | 65.7257 | -57.0511 | 65.657 | -55.9067 | -56.749 | -55.9708 | -55.6824 | 65.7532 | -57.1152 | -56.8863 | -56.9366 | -57.0511 | -56.7535 | -0.004577 | -0.050354 | -0.11902 | 1.1398 | 1.0757 | 0.29755 | 1.0803 | 0.30212 | -0.068664 | -0.022888 | -122.6624 | 0.10986 | 0.29297 | -0.004577 | 0.36163 | 0.064087 | 1.1444 | 122.7081 | 0.17853 | 0.22888 | 122.7768 | 122.8683 | 122.7722 | 122.7997 | -122.8271 | -122.8912 | 122.7036 | 0.16022 | 3.1403 | 1.3641
1195.1719 | 123.1659 | -57.0648 | 65.7623 | -0.098725 | 0.0016899 | 0.065871 | 0.073104 | 0.0016556 | 0.0034735 | 0.0064898 | -0.016602 | 0.0015295 | -0.0014954 | 0.002196 | -0.0010787 | -0.0021619 | 0.0021619 | -53.8834 | 65.7394 | -57.0602 | 65.6479 | -55.9021 | -56.7627 | -55.9891 | -55.687 | 65.7715 | -57.0969 | -56.8634 | -56.987 | -57.3029 | -56.8314 | 0.004577 | -0.022888 | -0.11444 | 1.1627 | 1.0757 | 0.30212 | 1.0712 | 0.29755 | -0.032044 | 0.009155 | -122.6257 | 0.077819 | 0.23346 | -0.23804 | 0.2655 | -0.20599 | 1.1581 | 122.7081 | 0.10986 | 0.23346 | 122.7997 | 122.8683 | 122.8043 | 122.8363 | -122.8226 | -122.8592 | 122.7127 | 0.20142 | 3.1815 | 1.3779
1196.1719 | 123.0698 | -57.0694 | 65.7623 | -0.091095 | -0.00087374 | 0.065443 | 0.074172 | 0.0012284 | 0.0030463 | 0.0077716 | -0.025757 | 0.0025975 | 0.00085443 | 0.0041186 | -0.0023605 | -0.0013073 | 0.0034435 | -53.9749 | 65.7486 | -57.106 | 65.5655 | -56.012 | -56.8314 | -56.0532 | -55.7785 | 65.7761 | -57.1014 | -56.9275 | -56.9778 | -57.1472 | -56.8222 | -0.036621 | -0.013733 | -0.19684 | 1.0574 | 1.0162 | 0.23804 | 1.0529 | 0.27466 | -0.032043 | 0.013733 | -122.6898 | 0.091553 | 0.24719 | -0.07782 | 0.27923 | -0.045777 | 1.0941 | 122.6715 | 0.1236 | 0.17395 | 122.8546 | 122.8775 | 122.818 | 122.8455 | -122.8683 | -122.8638 | 122.6349 | 0.14191 | 3.0945 | 1.2909
1197.1719 | 123.1064 | -57.0602 | 65.7761 | -0.16739 | -0.00087374 | 0.065443 | 0.073531 | 0.0012284 | 0.0039007 | 0.0079852 | -0.0074462 | 0.0032385 | -0.0019226 | -0.00058098 | -0.0012925 | -0.0013073 | 0.0042981 | -53.9383 | 65.7349 | -57.0786 | 65.6342 | -55.9433 | -56.7627 | -55.9845 | -55.7098 | 65.7623 | -57.0831 | -56.8817 | -56.9504 | -57.1106 | -56.7902 | -0.01831 | -0.041199 | -0.14191 | 1.1169 | 1.0757 | 0.29755 | 1.0941 | 0.31586 | -0.022888 | -0.013733 | -122.6578 | 0.10986 | 0.27008 | -0.050354 | 0.29297 | -0.027466 | 1.1353 | 122.7127 | 0.13275 | 0.20142 | 122.8134 | 122.8455 | 122.7951 | 122.8226 | -122.8546 | -122.8592 | 122.6944 | 0.17853 | 3.1219 | 1.3504
1198.1719 | 123.1064 | -57.0374 | 65.7761 | -0.15213 | 0.0023307 | 0.064589 | 0.07289 | -0.00069423 | 0.0032599 | 0.0073444 | 0.013916 | 0.00088875 | -0.00021357 | 0.0024096 | -0.0019333 | -0.00088008 | -0.00082886 | -53.9474 | 65.7349 | -57.0465 | 65.744 | -55.7785 | -56.8039 | -55.9479 | -55.6915 | 65.7578 | -57.1106 | -56.8863 | -56.9412 | -57.0969 | -56.8039 | -0.009155 | -0.041199 | -0.032043 | 1.2589 | 1.0895 | 0.23346 | 1.0986 | 0.24262 | -0.073242 | -0.018311 | -122.6624 | 0.096131 | 0.23346 | -0.059509 | 0.3067 | 0.013733 | 1.268 | 122.7905 | 0.16937 | 0.2243 | 122.7814 | 122.8683 | 122.7722 | 122.7951 | -122.8226 | -122.8867 | 122.7814 | 0.15106 | 3.0899 | 1.3458
1199.1719 | 123.0377 | -57.0648 | 65.7623 | -0.10635 | 0.00019446 | 0.065443 | 0.075667 | 0.00037377 | 0.0039007 | 0.0062762 | -0.068481 | 0.0017431 | 0.00064083 | -0.0010084 | -1.0706e-05 | -0.0034437 | 0.0021619 | -54.0253 | 65.7806 | -57.1014 | 65.5518 | -56.044 | -56.8542 | -56.0898 | -55.8197 | 65.8173 | -57.1198 | -56.9778 | -57.0282 | -57.2113 | -56.8817 | -0.036621 | 0.018311 | -0.21057 | 1.0208 | 0.97504 | 0.21057 | 1.0117 | 0.24719 | -0.054932 | 0.054932 | -122.7402 | 0.036621 | 0.1831 | -0.14648 | 0.23804 | -0.091553 | 1.0574 | 122.6532 | 0.091553 | 0.14191 | 122.8821 | 122.937 | 122.8455 | 122.8821 | -122.8638 | -122.8821 | 122.6166 | 0.086975 | 3.0395 | 1.2451
1200.1719 | 123.111 | -57.0511 | 65.7303 | -0.12161 | 0.00083526 | 0.064803 | 0.075667 | -0.00069423 | 0.0034735 | 0.0054218 | -0.028809 | -0.0021021 | -0.0019226 | 0.0024096 | 0.0010575 | -0.0028027 | -0.0012561 | -54.0253 | 65.7578 | -57.0831 | 65.6067 | -55.9479 | -56.7947 | -56.0165 | -55.7236 | 65.7623 | -57.1106 | -56.9092 | -56.9733 | -57.1243 | -56.7902 | -0.032044 | 0.027465 | -0.1236 | 1.1032 | 1.0345 | 0.25635 | 1.0666 | 0.28839 | -0.05951 | 0.032043 | -122.6395 | 0.077819 | 0.26093 | -0.073243 | 0.32044 | -0.013733 | 1.1353 | 122.6898 | 0.13733 | 0.20142 | 122.8409 | 122.8729 | 122.8088 | 122.8134 | -122.8134 | -122.8409 | 122.6578 | 0.14191 | 3.0258 | 1.3275
1201.1719 | 123.0927 | -57.0694 | 65.7578 | -0.1445 | 0.0016899 | 0.064589 | 0.07524 | -0.00026703 | 0.0028327 | 0.0060626 | -0.03186 | -0.00060665 | 0.00064083 | 0.001128 | -0.00065151 | 0.00061532 | -0.00082886 | -54.0436 | 65.7486 | -57.1106 | 65.5838 | -55.9799 | -56.8085 | -56.0165 | -55.7877 | 65.7806 | -57.1106 | -56.9183 | -56.987 | -57.1335 | -56.813 | -0.041199 | -0.009155 | -0.17395 | 1.0895 | 1.0529 | 0.26093 | 1.0941 | 0.30212 | -0.041199 | 0.022889 | -122.6761 | 0.082397 | 0.25635 | -0.064087 | 0.29755 | -0.022888 | 1.1307 | 122.6944 | 0.1236 | 0.19226 | 122.8592 | 122.8912 | 122.818 | 122.85 | -122.8683 | -122.8683 | 122.6532 | 0.15106 | 3.0258 | 1.2817
1202.1719 | 123.0606 | -57.0831 | 65.744 | -0.083466 | 0.0012625 | 0.063734 | 0.074813 | 0.0022964 | 0.0041143 | 0.0077716 | -0.016602 | 0.0019567 | -0.00085457 | -0.0016492 | -0.00086511 | -0.0017347 | 0.0015209 | -54.0573 | 65.744 | -57.1014 | 65.5609 | -55.9891 | -56.8405 | -56.0303 | -55.7877 | 65.799 | -57.1152 | -56.9321 | -56.9778 | -57.1472 | -56.813 | -0.01831 | 0 | -0.18311 | 1.0941 | 1.0529 | 0.24261 | 1.0712 | 0.26092 | -0.032043 | 0.054931 | -122.6761 | 0.10529 | 0.27008 | -0.064087 | 0.30212 | -0.032044 | 1.1124 | 122.6624 | 0.13733 | 0.1831 | 122.8455 | 122.9141 | 122.8271 | 122.8821 | -122.8455 | -122.8592 | 122.644 | 0.15106 | 3.0258 | 1.2955
1203.1719 | 123.0789 | -57.0648 | 65.7669 | -0.098725 | 0.00019446 | 0.064375 | 0.074172 | -0.005394 | 0.00091009 | 0.0052082 | -0.025757 | -0.00017945 | 0.0012818 | 0.0043322 | -1.0706e-05 | -0.00066648 | 0.0028027 | -54.0756 | 65.7578 | -57.0648 | 65.5472 | -56.0211 | -56.8497 | -56.0532 | -55.7877 | 65.7944 | -57.1381 | -56.9641 | -56.9962 | -57.1884 | -56.8405 | 0 | -0.009156 | -0.21973 | 1.0437 | 1.0117 | 0.21515 | 1.0117 | 0.21515 | -0.073243 | 0.027466 | -122.731 | 0.068664 | 0.2243 | -0.1236 | 0.29755 | -0.050354 | 1.0437 | 122.612 | 0.14191 | 0.17395 | 122.8226 | 122.9324 | 122.8226 | 122.8592 | -122.8317 | -122.905 | 122.612 | 0.10071 | 2.9892 | 1.2772
1204.1719 | 123.111 | -57.0786 | 65.7303 | -0.13687 | 0.00019446 | 0.066084 | 0.073104 | -0.00048063 | 0.0011237 | 0.0088398 | -0.01355 | 0.00067495 | 0.00021363 | 0.00070062 | -0.0012925 | -0.0019483 | 0.0025891 | -54.0253 | 65.7394 | -57.0786 | 65.6387 | -55.9204 | -56.7581 | -55.9891 | -55.719 | 65.7623 | -57.106 | -56.9138 | -56.9504 | -57.1106 | -56.7902 | 0 | 0.009155 | -0.091553 | 1.1581 | 1.0895 | 0.32043 | 1.0895 | 0.32043 | -0.027466 | 0.032043 | -122.644 | 0.12817 | 0.28839 | -0.032044 | 0.31586 | -0.004578 | 1.1581 | 122.7173 | 0.15564 | 0.19226 | 122.818 | 122.8683 | 122.818 | 122.8409 | -122.8088 | -122.8363 | 122.7173 | 0.1648 | 3.0533 | 1.3596
1205.1719 | 123.1201 | -57.0557 | 65.744 | -0.15976 | 0.00040806 | 0.062453 | 0.073745 | -0.0026168 | 0.0024053 | 0.0062762 | -0.01355 | 3.4148e-05 | 0.0038452 | -0.00229 | -0.0021469 | -0.0034437 | -0.0014697 | -54.0207 | 65.744 | -57.0602 | 65.4694 | -55.9845 | -56.5796 | -55.838 | -55.6549 | 65.744 | -57.0877 | -56.9138 | -56.955 | -57.106 | -56.813 | -0.004578 | 0 | -0.27466 | 1.0712 | 1.2177 | 0.47607 | 1.2222 | 0.48065 | -0.032044 | 0 | -122.6578 | 0.10071 | 0.24262 | -0.050354 | 0.27466 | -0.01831 | 1.0757 | 122.5296 | 0.13275 | 0.17395 | 122.8043 | 122.8317 | 122.7997 | 122.7997 | -122.8043 | -122.8317 | 122.525 | 0.14191 | 3.035 | 1.4008
1206.1719 | 123.1155 | -57.0557 | 65.744 | -0.075836 | 0.00040806 | 0.064375 | 0.074599 | 0.00016017 | 0.0053961 | 0.0081988 | -0.022705 | 0.0017431 | -0.00021357 | 0.005614 | -0.00022431 | -0.0015211 | -0.0014697 | -54.0756 | 65.7394 | -57.0557 | 65.6067 | -55.9616 | -56.7902 | -55.9982 | -55.7648 | 65.7486 | -57.106 | -56.9275 | -56.9504 | -57.1106 | -56.7993 | 0 | -0.004578 | -0.13733 | 1.0941 | 1.0574 | 0.2655 | 1.0574 | 0.2655 | -0.050354 | 0.004577 | -122.6715 | 0.10529 | 0.25635 | -0.054932 | 0.3067 | -0.004578 | 1.0941 | 122.6624 | 0.15564 | 0.17853 | 122.7951 | 122.8546 | 122.7951 | 122.8043 | -122.7997 | -122.85 | 122.6624 | 0.12817 | 2.98 | 1.2909
1207.1719 | 122.9919 | -57.1014 | 65.7715 | -0.060578 | 0.00040806 | 0.063307 | 0.07524 | 0.001442 | 0.0030463 | 0.0073444 | -0.047119 | 0.0013159 | 0.00064083 | 0.0019824 | -0.00065151 | -0.0032301 | -0.00018806 | -54.1077 | 65.7578 | -57.0831 | 65.5289 | -56.0303 | -56.8542 | -56.0669 | -55.8472 | 65.7944 | -57.1198 | -56.9824 | -57.0511 | -57.2342 | -56.8954 | 0.01831 | -0.013733 | -0.24261 | 1.0712 | 1.0345 | 0.24719 | 1.0162 | 0.22888 | -0.018311 | 0.022889 | -122.7539 | 0.050354 | 0.20599 | -0.13275 | 0.2243 | -0.11444 | 1.0529 | 122.612 | 0.068665 | 0.13733 | 122.8409 | 122.9141 | 122.8592 | 122.8958 | -122.8546 | -122.8912 | 122.6303 | 0.11902 | 2.9938 | 1.2543
1208.1719 | 123.0927 | -57.074 | 65.744 | -0.098725 | 0.0016899 | 0.064589 | 0.076522 | 0.0022964 | 0.0045417 | 0.0084124 | -0.050171 | 0.00088875 | 0.00085443 | 0.0032642 | -0.0030013 | -0.0032301 | 0.0019483 | -54.0985 | 65.744 | -57.106 | 65.5701 | -55.9753 | -56.8176 | -56.0257 | -55.7877 | 65.7578 | -57.1106 | -56.9504 | -56.987 | -57.1793 | -56.8497 | -0.032043 | 0 | -0.17395 | 1.0986 | 1.0483 | 0.25635 | 1.0803 | 0.28839 | -0.036621 | 0.013732 | -122.6944 | 0.086975 | 0.2243 | -0.10529 | 0.26093 | -0.068664 | 1.1307 | 122.6761 | 0.1236 | 0.16022 | 122.85 | 122.8683 | 122.818 | 122.8317 | -122.85 | -122.8546 | 122.644 | 0.1236 | 2.9755 | 1.2863
1209.1719 | 123.0835 | -57.0969 | 65.7349 | -0.13687 | 0.0016899 | 0.06523 | 0.074599 | -0.00069423 | 0.0013373 | 0.0073444 | -0.019653 | 0.0011023 | -0.00021357 | 0.002196 | -0.0015061 | -0.0019483 | -0.00018806 | -54.1077 | 65.7394 | -57.0877 | 65.5655 | -55.9845 | -56.8314 | -56.0349 | -55.8014 | 65.7715 | -57.1289 | -56.955 | -56.9778 | -57.1518 | -56.8405 | 0.009155 | 0.004578 | -0.16937 | 1.1124 | 1.062 | 0.2655 | 1.0529 | 0.25635 | -0.032043 | 0.036621 | -122.6898 | 0.11902 | 0.25635 | -0.054931 | 0.28839 | -0.022888 | 1.1032 | 122.6532 | 0.15106 | 0.17395 | 122.8271 | 122.9004 | 122.8363 | 122.8683 | -122.8226 | -122.8638 | 122.6624 | 0.14191 | 2.9892 | 1.2955
1210.1719 | 123.0698 | -57.0831 | 65.7532 | -0.12161 | -0.00023294 | 0.066512 | 0.075454 | 0.003151 | 0.0032599 | 0.0079852 | -0.025757 | -0.00017945 | 0.0012818 | -0.0020764 | -0.0017197 | -0.0019483 | 0.0015209 | -54.1168 | 65.7532 | -57.1014 | 65.5472 | -56.012 | -56.8359 | -56.0394 | -55.8151 | 65.7715 | -57.1426 | -56.955 | -57.0007 | -57.1518 | -56.8451 | -0.01831 | 0 | -0.20599 | 1.0712 | 1.0437 | 0.24719 | 1.062 | 0.2655 | -0.059509 | 0.01831 | -122.7081 | 0.082398 | 0.23804 | -0.068664 | 0.29755 | -0.009155 | 1.0895 | 122.6486 | 0.14191 | 0.18768 | 122.8546 | 122.9141 | 122.8363 | 122.8546 | -122.8546 | -122.8958 | 122.6303 | 0.12817 | 2.9663 | 1.268
1211.1719 | 123.1018 | -57.0648 | 65.7303 | -0.1445 | -1.9142e-05 | 0.064589 | 0.073104 | -5.343e-05 | 0.0017645 | 0.0071308 | -0.0013428 | 0.00088875 | 2.8e-08 | 0.0049732 | -0.00043791 | -0.0017347 | 0.0021619 | -54.071 | 65.7028 | -57.0557 | 65.6342 | -55.9204 | -56.7627 | -55.9662 | -55.7373 | 65.7578 | -57.1106 | -56.9229 | -56.955 | -57.1335 | -56.7993 | 0.009155 | -0.027466 | -0.096131 | 1.1444 | 1.0986 | 0.30212 | 1.0895 | 0.29297 | -0.045777 | 0.027465 | -122.6532 | 0.10986 | 0.2655 | -0.068665 | 0.31128 | -0.022888 | 1.1353 | 122.6898 | 0.15564 | 0.18768 | 122.7585 | 122.8683 | 122.7676 | 122.8226 | -122.786 | -122.8409 | 122.699 | 0.14191 | 2.9938 | 1.3275
1212.1719 | 123.0972 | -57.0557 | 65.7257 | -0.15976 | 0.0012625 | 0.064803 | 0.076308 | -0.0013352 | 0.0060369 | 0.0088398 | -0.010498 | -0.00039305 | -0.00064077 | 0.0013416 | 0.00020289 | -0.0013073 | -0.0040333 | -54.0573 | 65.7074 | -57.074 | 65.5884 | -55.9296 | -56.7627 | -55.957 | -55.7693 | 65.7394 | -57.106 | -56.9229 | -56.9778 | -57.1381 | -56.813 | -0.018311 | -0.018311 | -0.13733 | 1.1261 | 1.0986 | 0.29297 | 1.1169 | 0.31128 | -0.050354 | 0.013733 | -122.6486 | 0.07782 | 0.24262 | -0.082398 | 0.29297 | -0.032044 | 1.1444 | 122.6624 | 0.12817 | 0.1831 | 122.7814 | 122.8455 | 122.7631 | 122.7951 | -122.7997 | -122.8317 | 122.644 | 0.13275 | 2.9984 | 1.2863
1213.1719 | 123.0652 | -57.0923 | 65.7806 | -0.075836 | -0.00087374 | 0.063948 | 0.076308 | 0.0018692 | 0.0021917 | 0.0054218 | -0.041016 | 0.00024775 | 0.0014954 | 0.002196 | -0.0027877 | -0.0015211 | 0.0038709 | -54.126 | 65.7303 | -57.0969 | 65.5563 | -56.0211 | -56.8497 | -56.0532 | -55.8334 | 65.7623 | -57.1152 | -56.9778 | -57.0328 | -57.2021 | -56.8634 | -0.004578 | -0.050354 | -0.22431 | 1.0712 | 1.0391 | 0.24261 | 1.0437 | 0.24719 | -0.022888 | -0.018311 | -122.7585 | 0.059509 | 0.22888 | -0.10986 | 0.25177 | -0.086975 | 1.0757 | 122.6532 | 0.082397 | 0.13733 | 122.8271 | 122.8775 | 122.8226 | 122.8546 | -122.8775 | -122.8958 | 122.6486 | 0.11444 | 2.9663 | 1.2588
1214.1719 | 123.0469 | -57.0831 | 65.7349 | -0.083466 | 0.00040806 | 0.063094 | 0.07524 | 0.00037377 | 0.0043281 | 0.0047808 | -0.034912 | 0.00067495 | 0.001068 | -0.0010084 | -0.0015061 | -0.0019483 | 0.0021619 | -54.126 | 65.7669 | -57.0923 | 65.5426 | -56.0257 | -56.8451 | -56.044 | -55.8655 | 65.7715 | -57.1472 | -56.9824 | -57.0145 | -57.2113 | -56.8863 | -0.009155 | 0.032044 | -0.19226 | 1.0574 | 1.0391 | 0.23804 | 1.0483 | 0.24719 | -0.064087 | 0.036621 | -122.7173 | 0.068665 | 0.19684 | -0.12817 | 0.26093 | -0.064087 | 1.0666 | 122.6349 | 0.13275 | 0.16479 | 122.8592 | 122.9187 | 122.85 | 122.8546 | -122.8271 | -122.8821 | 122.6257 | 0.10071 | 2.9572 | 1.2177
1215.1719 | 123.1018 | -57.0419 | 65.7257 | -0.12161 | 0.0029715 | 0.064375 | 0.072463 | -5.343e-05 | 0.0024053 | 0.0064898 | -0.0013428 | -0.00039305 | -0.0012818 | -0.003999 | -1.0706e-05 | -0.0023755 | 0.0017345 | -54.0756 | 65.6845 | -57.0602 | 65.6525 | -55.9204 | -56.7032 | -55.9204 | -55.751 | 65.7349 | -57.1381 | -56.9229 | -56.9412 | -57.1381 | -56.813 | -0.018311 | -0.041199 | -0.073242 | 1.1215 | 1.1215 | 0.33874 | 1.1398 | 0.35706 | -0.096131 | 0.009155 | -122.6486 | 0.10071 | 0.22888 | -0.096131 | 0.32501 | 0 | 1.1398 | 122.7127 | 0.19684 | 0.21515 | 122.7448 | 122.8729 | 122.7264 | 122.7768 | -122.7859 | -122.8638 | 122.6944 | 0.11902 | 2.9663 | 1.2909
1216.1719 | 123.056 | -57.0557 | 65.7715 | -0.10635 | 0.0038261 | 0.06523 | 0.073104 | -5.343e-05 | 0.0030463 | 0.0077716 | 0.068848 | -0.0012477 | 0.0021362 | -0.009126 | 0.00020289 | -0.00045288 | -0.0010425 | -54.1122 | 65.7394 | -57.0465 | 65.5884 | -55.9387 | -56.7581 | -55.9387 | -55.7922 | 65.7715 | -57.0969 | -56.9504 | -56.9366 | -57.1198 | -56.8359 | 0.009155 | -0.032043 | -0.1831 | 1.1169 | 1.1169 | 0.29755 | 1.1078 | 0.28839 | -0.041199 | 0 | -122.7219 | 0.11902 | 0.21973 | -0.064087 | 0.26093 | -0.022888 | 1.1078 | 122.6349 | 0.16022 | 0.14648 | 122.7859 | 122.8683 | 122.7951 | 122.8271 | -122.818 | -122.8683 | 122.644 | 0.10529 | 2.9434 | 1.2634
1217.1719 | 123.0743 | -57.0786 | 65.7166 | -0.13687 | 0.00019446 | 0.064375 | 0.075027 | 0.0022964 | 0.0047553 | 0.0094806 | 0.0078126 | -0.00017945 | 2.8e-08 | 0.0019824 | -0.0010787 | -0.0030163 | -0.0014697 | -54.1122 | 65.7257 | -57.0602 | 65.6204 | -55.9158 | -56.7764 | -55.9387 | -55.7739 | 65.7486 | -57.1243 | -56.9641 | -56.9962 | -57.1381 | -56.8451 | 0.01831 | 0.009155 | -0.096131 | 1.1627 | 1.1398 | 0.30212 | 1.1215 | 0.28381 | -0.045777 | 0.032043 | -122.6807 | 0.082397 | 0.23346 | -0.05951 | 0.27924 | -0.013733 | 1.1444 | 122.6807 | 0.12817 | 0.16022 | 122.7859 | 122.8729 | 122.8043 | 122.8271 | -122.7768 | -122.8409 | 122.699 | 0.11444 | 2.9663 | 1.3046
1218.1719 | 123.1018 | -57.0877 | 65.7303 | -0.18265 | 0.00040806 | 0.064803 | 0.076095 | 0.0018692 | 0.0043281 | 0.0084124 | -0.0013428 | -0.00082025 | 0.0012818 | -0.0010084 | -0.00086511 | -0.0032301 | -0.0033923 | -54.0985 | 65.6799 | -57.0419 | 65.6296 | -55.7968 | -56.5979 | -55.9525 | -55.7144 | 65.7486 | -57.1106 | -56.9321 | -56.9641 | -57.106 | -56.7993 | 0.045777 | -0.050354 | -0.10071 | 1.2909 | 1.1353 | 0.48981 | 1.0895 | 0.44403 | -0.022888 | 0.01831 | -122.6624 | 0.1236 | 0.28839 | -0.01831 | 0.31128 | 0.004578 | 1.2451 | 122.6715 | 0.14648 | 0.17853 | 122.7219 | 122.8592 | 122.7676 | 122.8363 | -122.7722 | -122.8409 | 122.7173 | 0.15564 | 2.9892 | 1.3733
1219.1719 | 123.0881 | -57.0648 | 65.744 | -0.10635 | -0.0019417 | 0.063307 | 0.075027 | 0.0027238 | 0.0019781 | 0.0081988 | -0.053223 | -0.00039305 | -0.00085457 | -0.00229 | -0.0015061 | -0.00088008 | -0.0021107 | -54.1214 | 65.7074 | -57.0786 | 65.4648 | -55.9937 | -56.575 | -55.8334 | -55.7236 | 65.7669 | -57.0923 | -56.9458 | -56.9595 | -57.1335 | -56.8085 | -0.013733 | -0.036622 | -0.27924 | 1.0712 | 1.2314 | 0.48981 | 1.2451 | 0.50354 | -0.027466 | 0.022888 | -122.6898 | 0.10529 | 0.25635 | -0.068665 | 0.28381 | -0.041199 | 1.0849 | 122.5433 | 0.13275 | 0.14648 | 122.7859 | 122.8592 | 122.7722 | 122.8317 | -122.8226 | -122.8363 | 122.5296 | 0.11902 | 2.9434 | 1.3412
1220.1719 | 123.0972 | -57.0694 | 65.7349 | -0.075836 | 0.0021171 | 0.064375 | 0.075667 | -0.0011214 | 0.0034735 | 0.010762 | -0.050171 | 0.0021703 | 0.001709 | 0.0066822 | -0.0023605 | -0.0017347 | -0.00040166 | -54.1534 | 65.7166 | -57.0969 | 65.5975 | -55.9433 | -56.781 | -55.9799 | -55.7922 | 65.7578 | -57.1243 | -56.9458 | -56.9687 | -57.1472 | -56.8222 | -0.027466 | -0.01831 | -0.13733 | 1.1261 | 1.0895 | 0.28839 | 1.1169 | 0.31586 | -0.054932 | 0.022888 | -122.6807 | 0.10071 | 0.24719 | -0.07782 | 0.30212 | -0.022888 | 1.1536 | 122.6944 | 0.15564 | 0.17853 | 122.8134 | 122.8821 | 122.786 | 122.8271 | -122.8317 | -122.8592 | 122.6669 | 0.1236 | 2.916 | 1.2772
1221.1719 | 123.1064 | -57.0694 | 65.7303 | -0.091095 | -0.0015145 | 0.064803 | 0.077163 | -0.00090783 | 0.0028327 | 0.0099078 | -0.028809 | 0.0013159 | 0.0019226 | 0.0041186 | -0.0012925 | -0.0030163 | -0.00082886 | -54.158 | 65.7257 | -57.0602 | 65.5975 | -55.9525 | -56.7902 | -55.9708 | -55.7877 | 65.744 | -57.1014 | -56.9366 | -56.9824 | -57.1335 | -56.8176 | 0.009155 | -0.004578 | -0.13275 | 1.1169 | 1.0986 | 0.27924 | 1.0895 | 0.27008 | -0.032043 | 0.013733 | -122.6669 | 0.086975 | 0.25177 | -0.064087 | 0.28381 | -0.032044 | 1.1078 | 122.6578 | 0.11902 | 0.16479 | 122.7859 | 122.8455 | 122.7951 | 122.8134 | -122.7905 | -122.8317 | 122.6669 | 0.13275 | 2.9114 | 1.2817
1222.1719 | 123.0835 | -57.0648 | 65.7578 | -0.068207 | -0.00066014 | 0.063307 | 0.074172 | 0.00016017 | 0.0049689 | 0.0096942 | 0.0078126 | -0.00060665 | 0.0019226 | 5.9824e-05 | -0.0010787 | -0.0023755 | -0.0016833 | -54.1443 | 65.7166 | -57.0465 | 65.6113 | -55.9113 | -56.7581 | -55.9341 | -55.7785 | 65.7623 | -57.1106 | -56.9595 | -56.9916 | -57.1381 | -56.8451 | 0.01831 | -0.041198 | -0.14648 | 1.1536 | 1.1307 | 0.3067 | 1.1124 | 0.28839 | -0.045777 | 0.004578 | -122.7173 | 0.073242 | 0.21973 | -0.073243 | 0.2655 | -0.027466 | 1.1353 | 122.6578 | 0.11902 | 0.15106 | 122.7631 | 122.8729 | 122.7814 | 122.8271 | -122.8043 | -122.8683 | 122.6761 | 0.10529 | 2.9205 | 1.2863
1223.1719 | 123.1018 | -57.0602 | 65.744 | -0.098725 | -0.0010873 | 0.065016 | 0.073958 | 0.00016017 | 0.0051825 | 0.0049946 | 0.050537 | 3.4148e-05 | -0.0019226 | -0.0014356 | 0.00063009 | -0.0040845 | -0.0027515 | -54.1397 | 65.6937 | -57.0786 | 65.6433 | -55.9753 | -57.0145 | -55.8609 | -55.7556 | 65.7349 | -57.1152 | -56.9321 | -56.9824 | -57.1381 | -56.8222 | -0.01831 | -0.050354 | -0.10071 | 1.0849 | 1.1993 | 0.045777 | 1.2177 | 0.064087 | -0.054931 | -0.009156 | -122.6761 | 0.07782 | 0.23804 | -0.07782 | 0.29297 | -0.022889 | 1.1032 | 122.7219 | 0.13275 | 0.1831 | 122.7722 | 122.85 | 122.7539 | 122.7951 | -122.8226 | -122.8592 | 122.7036 | 0.12817 | 2.9205 | 1.3046
1224.1719 | 123.0927 | -57.0877 | 65.7211 | -0.15213 | 0.0014761 | 0.065657 | 0.073745 | 0.00251 | 0.0039007 | 0.0088398 | -0.022705 | 0.00024775 | -0.001709 | 0.0030506 | -0.00043791 | -0.00045288 | -0.00018806 | -54.1443 | 65.6845 | -57.0831 | 65.625 | -55.9204 | -56.749 | -56.0806 | -55.6229 | 65.7486 | -57.1289 | -56.9412 | -56.9687 | -57.1609 | -56.8451 | 0.004578 | -0.036621 | -0.09613 | 1.1673 | 1.0071 | 0.33875 | 1.0025 | 0.33417 | -0.041198 | 0.027466 | -122.6624 | 0.11902 | 0.24262 | -0.073242 | 0.28381 | -0.032044 | 1.1627 | 122.7081 | 0.16022 | 0.18768 | 122.7676 | 122.8775 | 122.7722 | 122.8363 | -122.8043 | -122.85 | 122.7127 | 0.14648 | 2.9434 | 1.4648
1225.1719 | 123.1064 | -57.0786 | 65.712 | -0.12924 | -0.00044654 | 0.063521 | 0.075667 | -0.0028304 | 0.0026191 | 0.009267 | -0.13867 | 0.00046135 | -0.0019226 | 0.002196 | -0.0019333 | -0.0023755 | 2.554e-05 | -54.1443 | 65.6754 | -57.0557 | 65.6204 | -55.9204 | -56.7535 | -55.9387 | -55.7053 | 65.7166 | -57.1289 | -56.9275 | -56.9641 | -57.1289 | -56.8176 | 0.022888 | -0.036621 | -0.091553 | 1.1581 | 1.1398 | 0.32501 | 1.1169 | 0.30212 | -0.050354 | 0.004578 | -122.6395 | 0.11444 | 0.26093 | -0.050354 | 0.31128 | 0 | 1.1353 | 122.6761 | 0.16479 | 0.20142 | 122.731 | 122.8455 | 122.7539 | 122.7951 | -122.7676 | -122.8409 | 122.699 | 0.15106 | 2.9343 | 1.3733
1226.1719 | 123.056 | -57.074 | 65.7257 | -0.15213 | 0.0014761 | 0.065657 | 0.07524 | 0.0037918 | -0.00015811 | 0.010335 | -0.0074462 | 0.00088875 | -0.001709 | 0.00070062 | -0.00065151 | -0.0025891 | -0.00061526 | -54.1809 | 65.7074 | -57.0557 | 65.625 | -55.9204 | -56.7627 | -55.9341 | -55.7693 | 65.7349 | -57.1106 | -56.9412 | -56.987 | -57.1655 | -56.8588 | 0.018311 | -0.018311 | -0.10071 | 1.1536 | 1.1398 | 0.31128 | 1.1215 | 0.29297 | -0.036621 | 0.009155 | -122.6669 | 0.086975 | 0.21515 | -0.091552 | 0.25177 | -0.054931 | 1.1353 | 122.6807 | 0.1236 | 0.16937 | 122.7631 | 122.8455 | 122.7814 | 122.8088 | -122.7814 | -122.8363 | 122.699 | 0.13275 | 2.8931 | 1.3046
1227.1719 | 123.1064 | -57.106 | 65.7257 | -0.12161 | 0.0021171 | 0.065871 | 0.075027 | 0.00037377 | 0.0015509 | 0.0094806 | -0.041016 | 0.0013159 | -0.00021357 | 0.007323 | -1.0706e-05 | -0.0021619 | 0.00045294 | -54.1672 | 65.6982 | -57.0694 | 65.6296 | -55.925 | -56.749 | -55.9479 | -55.7831 | 65.7257 | -57.1335 | -56.9458 | -56.9229 | -57.3349 | -56.955 | 0.036621 | -0.027466 | -0.09613 | 1.181 | 1.1581 | 0.35706 | 1.1215 | 0.32044 | -0.027466 | 0 | -122.6715 | 0.1831 | 0.15106 | -0.22888 | 0.17853 | -0.20142 | 1.1444 | 122.699 | 0.21057 | 0.18768 | 122.7676 | 122.8592 | 122.8043 | 122.8317 | -122.7951 | -122.8592 | 122.7356 | 0.16022 | 2.9388 | 1.3229
1228.1719 | 123.0652 | -57.0831 | 65.7394 | -0.075836 | 0.00019446 | 0.063521 | 0.073745 | -0.00026703 | 0.0045417 | 0.0077716 | 0.0047608 | -0.00060665 | -0.0014954 | 0.0030506 | -0.0019333 | -0.0025891 | -0.0012561 | -54.0985 | 65.712 | -57.0648 | 65.625 | -55.9204 | -56.7719 | -55.9387 | -55.7648 | 65.7394 | -57.0923 | -56.9458 | -56.9641 | -57.1106 | -56.8268 | 0.018311 | -0.027466 | -0.11444 | 1.1627 | 1.1444 | 0.31128 | 1.1261 | 0.29297 | -0.009155 | 0 | -122.6852 | 0.11902 | 0.25635 | -0.027466 | 0.2655 | -0.018311 | 1.1444 | 122.6898 | 0.12817 | 0.14648 | 122.7768 | 122.8317 | 122.7951 | 122.8226 | -122.8043 | -122.8317 | 122.7081 | 0.13733 | 2.9846 | 1.3184
1229.1719 | 123.0789 | -57.0923 | 65.7349 | -0.091095 | 0.00019446 | 0.066084 | 0.075454 | -0.00069423 | 0.0028327 | 0.0071308 | -0.0043946 | 0.0017431 | 0.0014954 | -0.0033582 | 0.00084389 | -0.0021619 | -0.0016833 | -54.1946 | 65.6982 | -57.0557 | 65.6021 | -55.9204 | -56.7673 | -55.9341 | -55.806 | 65.7486 | -57.1106 | -56.9778 | -57.0053 | -57.1472 | -56.8405 | 0.036621 | -0.036621 | -0.13275 | 1.1719 | 1.1581 | 0.32501 | 1.1215 | 0.28839 | -0.018311 | 0.013733 | -122.7127 | 0.086975 | 0.25177 | -0.054932 | 0.27008 | -0.036621 | 1.1353 | 122.6578 | 0.10529 | 0.13275 | 122.7539 | 122.8592 | 122.7905 | 122.8409 | -122.7905 | -122.8455 | 122.6944 | 0.11444 | 2.8976 | 1.2863
1230.1719 | 123.0789 | -57.0831 | 65.7074 | -0.1445 | 0.0025443 | 0.065443 | 0.073104 | 0.001442 | 0.0041143 | 0.0049946 | 0.041382 | 0.00067495 | -0.00021357 | -0.00079478 | -0.0017197 | -0.0025891 | 0.0030163 | -54.1901 | 65.6708 | -57.0831 | 65.6158 | -55.9662 | -57.0419 | -55.8975 | -55.7968 | 65.744 | -57.1106 | -56.9366 | -56.9962 | -57.1518 | -56.8176 | 0 | -0.036621 | -0.091552 | 1.1169 | 1.1856 | 0.041199 | 1.1856 | 0.041199 | -0.027466 | 0.036622 | -122.644 | 0.086975 | 0.2655 | -0.068664 | 0.29297 | -0.041198 | 1.1169 | 122.699 | 0.11444 | 0.17395 | 122.7539 | 122.8546 | 122.7539 | 122.8271 | -122.7905 | -122.818 | 122.699 | 0.14648 | 2.8931 | 1.2863
1231.1719 | 123.1018 | -57.0969 | 65.7303 | -0.13687 | -0.00044654 | 0.062666 | 0.074172 | -5.343e-05 | 0.0030463 | 0.007558 | 0.010864 | 0.00067495 | 0.00042723 | -0.00036738 | -0.00086511 | -0.0013073 | 0.0017345 | -54.2175 | 65.6799 | -57.0648 | 65.6113 | -55.9113 | -56.7719 | -55.9341 | -55.7785 | 65.7257 | -57.1289 | -56.9641 | -56.9733 | -57.1472 | -56.8405 | 0.032044 | -0.050354 | -0.11902 | 1.1856 | 1.1627 | 0.32501 | 1.1307 | 0.29297 | -0.032043 | -0.004578 | -122.6944 | 0.1236 | 0.25635 | -0.050354 | 0.28839 | -0.018311 | 1.1536 | 122.6761 | 0.15564 | 0.16479 | 122.7448 | 122.8546 | 122.7768 | 122.8226 | -122.7951 | -122.8592 | 122.7081 | 0.13275 | 2.8793 | 1.3184
1232.1719 | 123.0743 | -57.0648 | 65.7303 | -0.15213 | 0.0012625 | 0.064162 | 0.073958 | -0.00069423 | 0.0051825 | 0.005849 | -0.0013428 | 0.00024775 | 0.0012818 | 0.00027342 | -0.0017197 | -0.00066648 | -0.0010425 | -54.2084 | 65.6891 | -57.0557 | 65.6296 | -55.9067 | -56.7581 | -55.9204 | -55.7831 | 65.7394 | -57.1106 | -56.9595 | -56.9962 | -57.1289 | -56.8451 | 0.009155 | -0.041199 | -0.10071 | 1.1581 | 1.1444 | 0.3067 | 1.1353 | 0.29755 | -0.045777 | 0.009155 | -122.6898 | 0.068664 | 0.21973 | -0.064087 | 0.2655 | -0.01831 | 1.149 | 122.6852 | 0.11444 | 0.15106 | 122.7448 | 122.85 | 122.7539 | 122.8043 | -122.786 | -122.8409 | 122.6944 | 0.10529 | 2.8564 | 1.2817
1233.1719 | 123.056 | -57.0969 | 65.7303 | -0.12924 | 0.00019446 | 0.063094 | 0.073531 | -0.0017624 | 0.0017645 | 0.010976 | -0.022705 | -0.00039305 | 0.00042723 | 0.001128 | 0.00084389 | -0.0021619 | 0.00045294 | -54.2542 | 65.7074 | -57.074 | 65.5884 | -55.9204 | -56.7947 | -55.9296 | -55.8472 | 65.7394 | -57.1243 | -56.9824 | -57.0053 | -57.1564 | -56.8542 | 0.022888 | -0.022889 | -0.14191 | 1.1765 | 1.1673 | 0.30212 | 1.1444 | 0.27924 | -0.027466 | 0.009155 | -122.7127 | 0.091553 | 0.24262 | -0.059509 | 0.27008 | -0.032043 | 1.1536 | 122.6624 | 0.11902 | 0.14191 | 122.7814 | 122.8638 | 122.8043 | 122.8363 | -122.8043 | -122.8546 | 122.6852 | 0.11444 | 2.8427 | 1.2497
1234.1719 | 123.1293 | -57.0786 | 65.7257 | -0.13687 | 0.0029715 | 0.062239 | 0.07524 | 0.00037377 | 0.0047553 | 0.0084124 | -0.0043946 | -0.0010339 | -0.00021357 | -0.00058098 | -0.0017197 | -0.00088008 | 0.00023934 | -54.213 | 65.6754 | -57.0602 | 65.7349 | -55.9387 | -56.7535 | -55.8884 | -55.7831 | 65.7257 | -57.1198 | -56.9412 | -56.955 | -57.1381 | -56.8222 | 0.01831 | -0.050354 | 0.009155 | 1.1398 | 1.1902 | 0.32501 | 1.1719 | 0.3067 | -0.041199 | 0 | -122.6669 | 0.1236 | 0.25635 | -0.05951 | 0.29755 | -0.018311 | 1.1215 | 122.7951 | 0.16479 | 0.17853 | 122.7356 | 122.8455 | 122.7539 | 122.8043 | -122.7859 | -122.8455 | 122.8134 | 0.13733 | 2.8656 | 1.2955
1235.1719 | 123.0927 | -57.0831 | 65.7303 | -0.083466 | 0.0014761 | 0.062239 | 0.075667 | -0.00090783 | 0.0030463 | 0.0073444 | -0.056274 | 0.0015295 | 0.00064083 | 0.001128 | -0.0021469 | -0.00045288 | -0.0021107 | -54.2816 | 65.712 | -57.1014 | 65.5884 | -55.9708 | -56.8085 | -55.9616 | -55.8563 | 65.7578 | -57.1609 | -56.955 | -57.0007 | -57.1243 | -56.8314 | -0.01831 | -0.018311 | -0.14191 | 1.1124 | 1.1215 | 0.27466 | 1.1398 | 0.29297 | -0.07782 | 0.027465 | -122.6852 | 0.082398 | 0.25177 | -0.041199 | 0.32959 | 0.036621 | 1.1307 | 122.6898 | 0.16022 | 0.20599 | 122.8134 | 122.9187 | 122.7951 | 122.8409 | -122.8317 | -122.8912 | 122.6715 | 0.12817 | 2.8015 | 1.2268
1236.1719 | 123.1338 | -57.074 | 65.7211 | -0.091095 | 0.0021171 | 0.065443 | 0.073104 | -0.0011214 | 0.0039007 | 0.0077716 | -0.016602 | -0.00039305 | -0.0014954 | 0.0036914 | -0.0027877 | -0.0015211 | 2.554e-05 | -54.2542 | 65.7074 | -57.0923 | 65.6067 | -55.9204 | -56.7673 | -55.9341 | -55.7968 | 65.7166 | -57.1381 | -56.9504 | -57.0007 | -57.0923 | -56.7764 | -0.01831 | -0.013733 | -0.11444 | 1.1536 | 1.1398 | 0.3067 | 1.1581 | 0.32501 | -0.064087 | -0.004577 | -122.6715 | 0.073243 | 0.29755 | -0.01831 | 0.36163 | 0.045777 | 1.1719 | 122.699 | 0.13733 | 0.18768 | 122.7997 | 122.8546 | 122.7814 | 122.7905 | -122.8134 | -122.8592 | 122.6807 | 0.1236 | 2.8198 | 1.2772
1237.1719 | 122.9919 | -57.1106 | 65.8218 | -0.045319 | 0.00019446 | 0.05818 | 0.074599 | -0.00069423 | 0.0021917 | 0.0090534 | -0.025757 | 0.0011023 | 0.0014954 | -0.0025036 | -0.0017197 | -0.00066648 | -0.00018806 | -54.0802 | 65.799 | -57.0282 | 65.5151 | -56.0303 | -56.7993 | -55.9891 | -55.8975 | 65.8356 | -57.1426 | -57.0374 | -57.0374 | -57.1884 | -56.8954 | 0.082398 | -0.022888 | -0.3067 | 1.0803 | 1.1215 | 0.31128 | 1.0391 | 0.22888 | -0.032043 | 0.013733 | -122.8592 | 0.073242 | 0.21515 | -0.07782 | 0.24719 | -0.045777 | 0.99793 | 122.5433 | 0.10529 | 0.10529 | 122.8271 | 122.9782 | 122.9095 | 122.9462 | -122.85 | -122.9645 | 122.6257 | 0.073242 | 3.0304 | 1.2131
1238.1719 | 123.1201 | -57.0923 | 65.7257 | -0.10635 | -1.9142e-05 | 0.064803 | 0.075454 | 0.0010148 | 0.0024053 | 0.0073444 | -0.037964 | 0.00088875 | -0.0019226 | -0.0027174 | -0.0025741 | -0.0021619 | 0.00045294 | -54.245 | 65.6891 | -57.0877 | 65.593 | -55.925 | -56.7719 | -55.925 | -55.7968 | 65.7211 | -57.1335 | -56.9504 | -56.987 | -57.1335 | -56.8268 | 0.004577 | -0.036621 | -0.13275 | 1.1673 | 1.1673 | 0.32043 | 1.1627 | 0.31586 | -0.041199 | -0.004578 | -122.6761 | 0.10528 | 0.2655 | -0.041199 | 0.3067 | 0 | 1.1627 | 122.6807 | 0.14648 | 0.18311 | 122.7768 | 122.8546 | 122.7814 | 122.8134 | -122.8134 | -122.8592 | 122.6852 | 0.14191 | 2.8473 | 1.2955
1239.1719 | 123.0606 | -57.0969 | 65.7532 | -0.083466 | -0.0015145 | 0.064375 | 0.075667 | 0.001442 | 0.0047553 | 0.0088398 | -0.025757 | 0.00046135 | 0.00064083 | -0.002931 | -0.0010787 | -0.0021619 | -0.0012561 | -54.2953 | 65.7028 | -57.0831 | 65.5792 | -55.9296 | -56.7947 | -55.9341 | -55.8334 | 65.7303 | -57.1472 | -56.9962 | -57.0282 | -57.1701 | -56.8634 | 0.013733 | -0.050354 | -0.17395 | 1.1673 | 1.1627 | 0.30212 | 1.149 | 0.28839 | -0.050354 | -0.022888 | -122.7493 | 0.068665 | 0.23346 | -0.073242 | 0.28381 | -0.022888 | 1.1536 | 122.6624 | 0.11902 | 0.15106 | 122.7859 | 122.8775 | 122.7997 | 122.8271 | -122.8363 | -122.9004 | 122.6761 | 0.10071 | 2.8015 | 1.2634
1240.1719 | 123.0469 | -57.1106 | 65.7257 | -0.098725 | -0.00087374 | 0.062666 | 0.073531 | 0.0033646 | 0.0047553 | 0.0084124 | -0.0013428 | 0.0017431 | 0.0025634 | -0.0042126 | -0.00086511 | -0.00066648 | 0.0019483 | -54.2908 | 65.6708 | -57.074 | 65.593 | -55.9296 | -56.7856 | -55.9341 | -55.8105 | 65.744 | -57.1518 | -56.987 | -57.0099 | -57.1701 | -56.868 | 0.036621 | -0.054932 | -0.13275 | 1.181 | 1.1765 | 0.32501 | 1.1398 | 0.28839 | -0.041198 | 0.018311 | -122.7127 | 0.10071 | 0.24262 | -0.059509 | 0.28381 | -0.018311 | 1.1444 | 122.6669 | 0.14191 | 0.16479 | 122.7448 | 122.8958 | 122.7814 | 122.8546 | -122.7997 | -122.8775 | 122.7036 | 0.1236 | 2.8198 | 1.3
1241.1719 | 123.1155 | -57.0786 | 65.7257 | -0.11398 | -0.0010873 | 0.062666 | 0.076522 | 0.0027238 | 0.0032599 | 0.009267 | -0.053223 | -0.0016749 | 2.8e-08 | 0.0024096 | -0.00086511 | -0.00066648 | -0.0042469 | -54.332 | 65.7028 | -57.1106 | 65.5518 | -55.9616 | -56.8176 | -55.957 | -55.838 | 65.712 | -57.1289 | -56.9733 | -56.9962 | -57.1472 | -56.8359 | -0.032044 | -0.022888 | -0.17395 | 1.1169 | 1.1215 | 0.26093 | 1.1536 | 0.29297 | -0.050354 | -0.013733 | -122.699 | 0.082397 | 0.24262 | -0.068665 | 0.29297 | -0.018311 | 1.149 | 122.6624 | 0.13275 | 0.15564 | 122.8134 | 122.8409 | 122.7814 | 122.7905 | -122.8363 | -122.8546 | 122.6303 | 0.10529 | 2.7466 | 1.2405
1242.1719 | 123.1018 | -57.0465 | 65.7761 | -0.060578 | -0.00023294 | 0.064589 | 0.07524 | 0.0010148 | 0.0028327 | 0.010121 | 0.0078126 | -0.00017945 | 0.00021363 | -0.00036738 | -0.00043791 | -0.0032301 | -0.00082886 | -54.2496 | 65.7486 | -57.0053 | 65.6937 | -55.8655 | -56.7627 | -55.8746 | -55.7785 | 65.7578 | -57.1014 | -56.955 | -56.9412 | -57.074 | -56.8176 | 0.041199 | -0.027466 | -0.082397 | 1.181 | 1.1719 | 0.28381 | 1.1307 | 0.24262 | -0.054931 | -0.018311 | -122.731 | 0.10529 | 0.22888 | -0.027466 | 0.28381 | 0.027465 | 1.1398 | 122.699 | 0.16022 | 0.14648 | 122.7539 | 122.8592 | 122.7951 | 122.8043 | -122.7814 | -122.8775 | 122.7402 | 0.091553 | 2.7969 | 1.268
1243.1719 | 123.111 | -57.0923 | 65.712 | -0.12161 | 0.0021171 | 0.064589 | 0.075667 | -0.0026168 | 0.0051825 | 0.0071308 | -0.053223 | 0.00067495 | -0.0019226 | 0.0041186 | -0.0023605 | -0.00045288 | -0.0068103 | -54.2908 | 65.6799 | -57.0831 | 65.6067 | -55.9296 | -56.7764 | -55.9341 | -55.8105 | 65.7166 | -57.1289 | -57.0007 | -57.1793 | -57.0419 | -56.7673 | 0.009155 | -0.032043 | -0.10529 | 1.1627 | 1.1581 | 0.31586 | 1.149 | 0.3067 | -0.036621 | 0.004578 | -122.7127 | -0.086975 | 0.32501 | 0.050354 | 0.36163 | 0.086975 | 1.1536 | 122.6898 | -0.050354 | 0.12817 | 122.7631 | 122.8455 | 122.7722 | 122.8088 | -122.7951 | -122.8409 | 122.699 | 0.091553 | 2.8015 | 1.2817
1244.1719 | 123.1384 | -57.1152 | 65.6982 | -0.098725 | 0.0027579 | 0.065871 | 0.074813 | 0.00080117 | 0.0034735 | 0.009267 | -0.03186 | 0.00067495 | -0.0019226 | -0.007417 | -0.0021469 | -0.00088008 | 0.00023934 | -54.3045 | 65.6754 | -57.0877 | 65.5975 | -55.9158 | -56.7673 | -55.9204 | -55.8151 | 65.7211 | -57.1198 | -56.9641 | -57.0099 | -57.1472 | -56.8359 | 0.027465 | -0.022888 | -0.10071 | 1.1993 | 1.1948 | 0.3479 | 1.1673 | 0.32043 | -0.004578 | 0.022888 | -122.6624 | 0.10529 | 0.27924 | -0.032044 | 0.28381 | -0.027466 | 1.1719 | 122.6852 | 0.10986 | 0.15564 | 122.7631 | 122.8409 | 122.7905 | 122.8363 | -122.7859 | -122.818 | 122.7127 | 0.15106 | 2.8107 | 1.3
1245.1719 | 123.0835 | -57.0877 | 65.6937 | -0.10635 | -1.9142e-05 | 0.065657 | 0.074386 | 0.00037377 | 0.0032599 | 0.010976 | -0.0074462 | -0.0021021 | -0.0025636 | 0.0034778 | -0.0017197 | -0.0015211 | -0.0053149 | -54.3915 | 65.6342 | -57.0831 | 65.6296 | -55.9296 | -56.7627 | -55.9067 | -55.8151 | 65.7394 | -57.1289 | -56.9595 | -57.0053 | -57.1335 | -56.8451 | 0.004578 | -0.05951 | -0.064087 | 1.1581 | 1.181 | 0.32501 | 1.1765 | 0.32043 | -0.041198 | 0.045776 | -122.6532 | 0.082398 | 0.24262 | -0.045776 | 0.28381 | -0.004578 | 1.1536 | 122.7127 | 0.1236 | 0.16937 | 122.7173 | 122.8683 | 122.7219 | 122.8271 | -122.7768 | -122.8226 | 122.7173 | 0.12817 | 2.6962 | 1.2726
1246.1719 | 123.0927 | -57.0877 | 65.712 | -0.16739 | 0.0010489 | 0.063307 | 0.074813 | 0.001442 | 0.0051825 | 0.010976 | -0.010498 | 0.00024775 | 0.00064083 | -0.0037854 | -0.0034287 | -0.0030163 | -0.0033923 | -54.3228 | 65.6845 | -57.0648 | 65.593 | -55.7877 | -56.6208 | -55.9296 | -55.7922 | 65.712 | -57.1335 | -56.9687 | -57.0053 | -57.1335 | -56.8222 | 0.022889 | -0.027466 | -0.11902 | 1.3 | 1.1581 | 0.46692 | 1.1353 | 0.44403 | -0.045776 | 0 | -122.6807 | 0.082398 | 0.2655 | -0.045776 | 0.31128 | 0 | 1.2772 | 122.6578 | 0.12817 | 0.1648 | 122.7493 | 122.8455 | 122.7722 | 122.7997 | -122.7768 | -122.8455 | 122.6807 | 0.11902 | 2.7649 | 1.2955
1247.1719 | 123.0103 | -57.1014 | 65.799 | -0.068207 | 0.0012625 | 0.064803 | 0.074172 | -0.00069423 | 0.0043281 | 0.010335 | 0.0078126 | -0.00017945 | 0.0014954 | 0.002196 | -0.0010787 | -0.0025891 | 0.0025891 | -54.2908 | 65.7349 | -57.0557 | 65.6296 | -55.8884 | -56.7123 | -55.8975 | -55.838 | 65.799 | -57.1014 | -57.019 | -57.0099 | -57.1381 | -56.8771 | 0.045776 | -0.064087 | -0.16937 | 1.2131 | 1.2039 | 0.3891 | 1.1581 | 0.34332 | 0 | 0 | -122.818 | 0.091552 | 0.2243 | -0.036622 | 0.2243 | -0.036622 | 1.1673 | 122.6852 | 0.091552 | 0.082397 | 122.7905 | 122.9004 | 122.8363 | 122.9004 | -122.8546 | -122.9004 | 122.731 | 0.082397 | 2.8107 | 1.2634
1248.1719 | 123.0881 | -57.106 | 65.712 | -0.03006 | 0.0025443 | 0.062025 | 0.076308 | 0.0020828 | 0.0064643 | 0.0090534 | -0.044067 | -0.00039305 | -0.00042717 | 0.0017688 | -0.0010787 | -0.00045288 | -0.0027515 | -54.3915 | 65.7211 | -57.1426 | 65.5243 | -55.9937 | -56.8405 | -55.9937 | -55.8975 | 65.7623 | -57.1518 | -56.9916 | -57.0236 | -57.193 | -56.8634 | -0.036621 | 0.009155 | -0.18768 | 1.1124 | 1.1124 | 0.2655 | 1.149 | 0.30212 | -0.045776 | 0.050354 | -122.7036 | 0.082397 | 0.24262 | -0.086975 | 0.28839 | -0.041199 | 1.149 | 122.6669 | 0.12817 | 0.16022 | 122.8638 | 122.9141 | 122.8271 | 122.8683 | -122.8546 | -122.8638 | 122.6303 | 0.11444 | 2.7145 | 1.2085
1249.1719 | 123.1018 | -57.0969 | 65.6937 | -0.10635 | 0.00019446 | 0.065016 | 0.076522 | 0.0027238 | 0.0032599 | 0.0081988 | -0.03186 | 0.0015295 | -0.0027772 | 0.00048702 | -0.0010787 | -0.0021619 | 0.00023934 | -54.3365 | 65.7028 | -57.0831 | 65.593 | -55.9479 | -56.7673 | -55.9296 | -55.8197 | 65.7257 | -57.1381 | -56.9641 | -57.0007 | -57.1426 | -56.8222 | 0.013733 | 0.009155 | -0.10071 | 1.149 | 1.1673 | 0.32959 | 1.1536 | 0.31586 | -0.041199 | 0.032043 | -122.6578 | 0.096131 | 0.27466 | -0.045776 | 0.31586 | -0.004577 | 1.1353 | 122.6761 | 0.13733 | 0.17395 | 122.7859 | 122.8638 | 122.7997 | 122.8226 | -122.7768 | -122.8317 | 122.6898 | 0.13275 | 2.7603 | 1.2772
1250.1719 | 123.0972 | -57.0877 | 65.7349 | -0.098725 | 0.0042533 | 0.064589 | 0.076522 | 0.0020828 | 0.0034735 | 0.0062762 | -0.06543 | 3.4148e-05 | 2.8e-08 | 0.00091422 | -0.00086511 | -0.0036573 | -0.0018971 | -54.3732 | 65.6891 | -57.1198 | 65.5746 | -55.957 | -56.7673 | -55.9433 | -55.8334 | 65.712 | -57.1518 | -56.9778 | -56.9962 | -57.1609 | -56.8405 | -0.032043 | -0.045776 | -0.16022 | 1.1307 | 1.1444 | 0.32043 | 1.1765 | 0.35248 | -0.064086 | -0.022888 | -122.7127 | 0.091553 | 0.24719 | -0.073242 | 0.31128 | -0.009156 | 1.1627 | 122.6944 | 0.15564 | 0.17395 | 122.8088 | 122.8638 | 122.7768 | 122.7997 | -122.8546 | -122.8867 | 122.6624 | 0.10986 | 2.7145 | 1.2543
1251.1719 | 123.0927 | -57.106 | 65.7166 | -0.11398 | 0.00083526 | 0.064162 | 0.075881 | 0.0016556 | 0.0058233 | 0.0073444 | -0.0074462 | 0.0013159 | -0.00021357 | 0.0043322 | -0.0030013 | -0.0010937 | -0.0029651 | -54.3549 | 65.6754 | -57.1014 | 65.6113 | -55.925 | -56.7535 | -55.9204 | -56.0211 | 65.6982 | -57.1838 | -56.9687 | -56.987 | -57.1701 | -56.8405 | 0.004578 | -0.041199 | -0.10529 | 1.181 | 1.1856 | 0.35248 | 1.181 | 0.3479 | -0.07782 | -0.018311 | -122.6852 | 0.11902 | 0.2655 | -0.064087 | 0.34332 | 0.013733 | 1.1765 | 122.7127 | 0.19684 | 0.21515 | 122.7768 | 122.8821 | 122.7814 | 122.8043 | -122.818 | -122.9004 | 122.7173 | 0.13733 | 2.7512 | 1.0849
1252.1719 | 123.1293 | -57.0557 | 65.7257 | -0.052948 | 0.0027579 | 0.064589 | 0.071395 | -0.00090783 | 0.0030463 | 0.0067036 | 0.050537 | -0.00017945 | -0.00042717 | -0.0027174 | 0.0016983 | -0.0021619 | -0.0021107 | -54.332 | 65.7166 | -57.0648 | 65.6342 | -55.8655 | -56.7123 | -55.8472 | -55.7648 | 65.7669 | -57.1106 | -56.9321 | -56.9321 | -57.0694 | -56.7947 | -0.009155 | -0.009155 | -0.091553 | 1.1902 | 1.2085 | 0.34332 | 1.2177 | 0.35248 | -0.054932 | 0.041199 | -122.6578 | 0.1236 | 0.26093 | -0.013733 | 0.31586 | 0.041199 | 1.1993 | 122.699 | 0.17853 | 0.17853 | 122.7814 | 122.8775 | 122.7722 | 122.8226 | -122.7905 | -122.8363 | 122.6898 | 0.1236 | 2.7237 | 1.2909
1253.1719 | 123.0377 | -57.1426 | 65.7349 | -0.060578 | 0.0010489 | 0.065016 | 0.075454 | -0.00069423 | 0.0030463 | 0.0094806 | -0.062378 | 0.0013159 | -0.0014954 | 0.0081774 | -0.00065151 | -0.0019483 | -0.0042469 | -54.4373 | 65.6891 | -57.1198 | 65.5151 | -56.0211 | -56.8634 | -55.9937 | -55.9296 | 65.7349 | -57.1609 | -57.0282 | -57.0602 | -57.2388 | -56.9138 | 0.022888 | -0.045776 | -0.21973 | 1.1215 | 1.149 | 0.27924 | 1.1261 | 0.25635 | -0.018311 | 0 | -122.7631 | 0.082397 | 0.22888 | -0.096131 | 0.24719 | -0.07782 | 1.0986 | 122.6349 | 0.10071 | 0.13275 | 122.8088 | 122.8958 | 122.8317 | 122.8775 | -122.8546 | -122.8958 | 122.6578 | 0.11444 | 2.7054 | 1.2131
1254.1719 | 123.1018 | -57.0877 | 65.7486 | -0.12924 | 0.0012625 | 0.064162 | 0.076736 | 0.00037377 | 0.0071051 | 0.0073444 | -0.0043946 | -0.00017945 | -0.00064077 | -0.00036738 | -0.0036423 | -0.0028027 | -0.0010425 | -54.3503 | 65.6891 | -57.0877 | 65.5746 | -55.806 | -56.5979 | -55.9021 | -55.806 | 65.712 | -57.1243 | -56.987 | -57.0099 | -57.1564 | -56.8314 | 0 | -0.059509 | -0.17395 | 1.2817 | 1.1856 | 0.48981 | 1.1856 | 0.48981 | -0.036621 | -0.036621 | -122.7356 | 0.07782 | 0.25635 | -0.068664 | 0.29297 | -0.032043 | 1.2817 | 122.6624 | 0.11444 | 0.13733 | 122.7768 | 122.8363 | 122.7768 | 122.7997 | -122.8363 | -122.8729 | 122.6624 | 0.10071 | 2.7374 | 1.2817
1255.1719 | 123.1018 | -57.0831 | 65.7349 | -0.15213 | 0.00040806 | 0.063948 | 0.074386 | -0.0024032 | 0.0041143 | 0.0079852 | -0.041016 | 0.00088875 | -0.00085457 | 0.0041186 | -0.00065151 | -0.00066648 | 0.0010937 | -54.4281 | 65.6982 | -57.1426 | 65.5518 | -55.9799 | -56.8268 | -55.9753 | -55.8975 | 65.7303 | -57.1747 | -57.0099 | -57.0145 | -57.1747 | -56.8451 | -0.059509 | -0.036621 | -0.1831 | 1.1032 | 1.1078 | 0.25635 | 1.1673 | 0.31586 | -0.091553 | -0.004577 | -122.7448 | 0.068665 | 0.23804 | -0.091553 | 0.32959 | 0 | 1.1627 | 122.6944 | 0.16022 | 0.1648 | 122.8409 | 122.905 | 122.7814 | 122.8134 | -122.8775 | -122.9095 | 122.6349 | 0.073242 | 2.655 | 1.1856
1256.1719 | 123.0698 | -57.1198 | 65.7074 | -0.060578 | -0.00066014 | 0.063521 | 0.076308 | 0.0027238 | 0.0019781 | 0.005849 | -0.041016 | 0.0025975 | 0.00064083 | -0.00079478 | -0.0015061 | -0.0017347 | -0.0014697 | -54.4601 | 65.7074 | -57.1609 | 65.5289 | -56.0349 | -56.8451 | -55.9937 | -55.925 | 65.744 | -57.1655 | -57.0145 | -57.0419 | -57.1701 | -56.8497 | -0.041199 | 0 | -0.17853 | 1.0849 | 1.1261 | 0.27466 | 1.1673 | 0.31586 | -0.045776 | 0.036622 | -122.7219 | 0.07782 | 0.27008 | -0.050354 | 0.31586 | -0.004578 | 1.1261 | 122.6898 | 0.1236 | 0.15106 | 122.8683 | 122.9095 | 122.8271 | 122.8638 | -122.8683 | -122.8729 | 122.6486 | 0.10529 | 2.6596 | 1.1948
1257.1719 | 123.111 | -57.0831 | 65.7166 | -0.075836 | 0.00062166 | 0.064375 | 0.073958 | -0.00026703 | 0.0036871 | 0.012258 | -0.025757 | -0.00017945 | 2.8e-08 | -0.00058098 | -0.0012925 | -0.0038709 | -0.0018971 | -54.4052 | 65.6845 | -57.1106 | 65.5792 | -55.9479 | -56.781 | -55.9204 | -55.8472 | 65.712 | -57.1564 | -56.9778 | -57.0374 | -57.1655 | -56.8268 | -0.027466 | -0.032044 | -0.13733 | 1.1353 | 1.1627 | 0.30212 | 1.1902 | 0.32959 | -0.073242 | -0.004578 | -122.6944 | 0.045776 | 0.25635 | -0.082397 | 0.32959 | -0.009155 | 1.1627 | 122.6898 | 0.11902 | 0.17853 | 122.7951 | 122.8683 | 122.7676 | 122.7951 | -122.8271 | -122.8729 | 122.6624 | 0.10529 | 2.6779 | 1.236
1258.1719 | 123.0423 | -57.1335 | 65.7349 | -0.098725 | -0.0017281 | 0.063094 | 0.078231 | 0.00016017 | 0.0021917 | 0.0084124 | -0.044067 | 0.00088875 | 0.001709 | 0.001128 | -0.0015061 | -0.00045288 | -0.00061526 | -54.4418 | 65.6891 | -57.1564 | 65.4922 | -56.0303 | -56.868 | -56.0028 | -55.9799 | 65.7578 | -57.1793 | -57.0602 | -57.1014 | -57.2342 | -56.9275 | -0.022888 | -0.045776 | -0.24261 | 1.1032 | 1.1307 | 0.2655 | 1.1536 | 0.28839 | -0.045776 | 0.022888 | -122.7951 | 0.032044 | 0.20599 | -0.10071 | 0.25177 | -0.054932 | 1.1261 | 122.6486 | 0.07782 | 0.11902 | 122.8455 | 122.937 | 122.8226 | 122.8912 | -122.8912 | -122.9141 | 122.6257 | 0.073242 | 2.6917 | 1.1536
1259.1719 | 123.1064 | -57.1152 | 65.7257 | -0.098725 | 0.0023307 | 0.064375 | 0.075454 | 0.0067826 | 0.0047553 | 0.009267 | 0.016968 | 3.4148e-05 | 0.00021363 | -0.002931 | -0.0025741 | -0.0032301 | 0.0010937 | -54.451 | 65.6708 | -57.1106 | 65.538 | -55.9753 | -56.8176 | -55.9525 | -55.8838 | 65.712 | -57.1609 | -56.9778 | -57.0328 | -57.1793 | -56.8542 | 0.004577 | -0.054932 | -0.18768 | 1.1398 | 1.1627 | 0.29755 | 1.1581 | 0.29297 | -0.045777 | -0.013733 | -122.7036 | 0.082397 | 0.26093 | -0.064087 | 0.3067 | -0.01831 | 1.1353 | 122.6486 | 0.12817 | 0.18311 | 122.7814 | 122.8729 | 122.7859 | 122.8271 | -122.8363 | -122.8867 | 122.6532 | 0.13733 | 2.6642 | 1.2314
1260.1719 | 123.1155 | -57.0923 | 65.7028 | -0.1445 | 0.0010489 | 0.063734 | 0.073318 | 0.0010148 | 0.0051825 | 0.0071308 | 0.001709 | -0.0012477 | -0.0019226 | 0.0051868 | -0.0032151 | -0.00066648 | 0.00023934 | -54.3915 | 65.6479 | -57.1014 | 65.6067 | -55.925 | -56.7581 | -55.9296 | -55.8563 | 65.7028 | -57.1472 | -56.9962 | -56.8542 | -57.1793 | -56.8634 | -0.009155 | -0.054932 | -0.096131 | 1.1673 | 1.1627 | 0.33417 | 1.1719 | 0.34332 | -0.054932 | 0 | -122.699 | 0.23804 | 0.22888 | -0.086975 | 0.28381 | -0.032043 | 1.1765 | 122.7081 | 0.29297 | 0.15106 | 122.7493 | 122.85 | 122.7402 | 122.7951 | -122.8043 | -122.85 | 122.699 | 0.09613 | 2.7008 | 1.236
1261.1719 | 123.0652 | -57.1335 | 65.712 | -0.10635 | 0.00019446 | 0.06288 | 0.075027 | -0.00090783 | 0.0036871 | 0.010335 | -0.050171 | 0.00067495 | 0.00064083 | 0.00091422 | -0.0012925 | -0.0025891 | -0.0012561 | -54.4739 | 65.712 | -57.1243 | 65.5106 | -56.0303 | -56.8588 | -55.9799 | -55.9479 | 65.7349 | -57.1747 | -57.019 | -57.074 | -57.2159 | -56.9 | 0.009155 | 0 | -0.20142 | 1.1032 | 1.1536 | 0.27466 | 1.1444 | 0.2655 | -0.041199 | 0.022888 | -122.731 | 0.059509 | 0.23346 | -0.082397 | 0.27466 | -0.041198 | 1.0941 | 122.6349 | 0.10071 | 0.15564 | 122.8363 | 122.9095 | 122.8455 | 122.8683 | -122.8363 | -122.8867 | 122.644 | 0.11444 | 2.6596 | 1.1856
1262.1719 | 123.0469 | -57.1106 | 65.7211 | -0.098725 | 0.00062166 | 0.062666 | 0.075667 | 0.0012284 | 0.0021917 | 0.0084124 | -0.050171 | 0.0034521 | 0.00042723 | -0.0042126 | -0.00065151 | -0.0028027 | 0.0023755 | -54.4968 | 65.712 | -57.1472 | 65.5014 | -56.044 | -56.8726 | -55.9799 | -55.957 | 65.7578 | -57.1838 | -57.0557 | -57.074 | -57.2525 | -56.9183 | -0.036621 | -0.009155 | -0.21973 | 1.0666 | 1.1307 | 0.23804 | 1.1673 | 0.27466 | -0.073242 | 0.036621 | -122.7768 | 0.036621 | 0.19226 | -0.14191 | 0.2655 | -0.068664 | 1.1032 | 122.6486 | 0.10986 | 0.12817 | 122.8592 | 122.9416 | 122.8226 | 122.8683 | -122.8683 | -122.905 | 122.612 | 0.054932 | 2.6138 | 1.1536
1263.1719 | 123.024 | -57.1426 | 65.712 | -0.098725 | 0.00062166 | 0.064162 | 0.074813 | -0.0021896 | 0.0028327 | 0.0084124 | -0.028809 | 0.0017431 | -0.0010682 | 0.0026232 | 0.00041649 | -0.0032301 | 0.00066654 | -54.4876 | 65.6891 | -57.1289 | 65.4831 | -56.0486 | -56.8588 | -56.0074 | -55.9845 | 65.7394 | -57.1747 | -57.0465 | -57.1014 | -57.2571 | -56.9321 | 0.013733 | -0.022888 | -0.22888 | 1.0941 | 1.1353 | 0.28381 | 1.1215 | 0.27008 | -0.032044 | 0.027466 | -122.7585 | 0.041199 | 0.21057 | -0.11444 | 0.24262 | -0.082397 | 1.0803 | 122.612 | 0.073243 | 0.12817 | 122.818 | 122.9141 | 122.8317 | 122.8821 | -122.8409 | -122.8867 | 122.6257 | 0.09613 | 2.655 | 1.1581
1264.1719 | 123.0743 | -57.1335 | 65.6982 | -0.068207 | 0.00040806 | 0.066084 | 0.075667 | -0.003685 | 0.0039007 | 0.0081988 | -0.010498 | 0.0021703 | -0.00085457 | 0.0024096 | -0.00086511 | -0.0021619 | -0.0040333 | -54.5013 | 65.6845 | -57.1335 | 65.5472 | -55.9937 | -56.8314 | -55.9525 | -55.8929 | 65.7028 | -57.1793 | -56.9733 | -57.0236 | -57.1884 | -56.8542 | 0 | -0.013733 | -0.15106 | 1.1398 | 1.181 | 0.30212 | 1.181 | 0.30212 | -0.045776 | 0.004578 | -122.6715 | 0.10986 | 0.27924 | -0.054932 | 0.32501 | -0.009156 | 1.1398 | 122.6807 | 0.15564 | 0.20599 | 122.818 | 122.8821 | 122.818 | 122.8363 | -122.8317 | -122.8775 | 122.6807 | 0.16022 | 2.6321 | 1.2405
1265.1719 | 123.0103 | -57.1609 | 65.7211 | -0.052948 | -0.00044654 | 0.064589 | 0.078231 | -0.0041122 | 0.0019781 | 0.0086262 | -0.03186 | 0.0028113 | 2.8e-08 | 0.003905 | -0.00065151 | -0.00066648 | 2.554e-05 | -54.5471 | 65.7166 | -57.1289 | 65.4465 | -56.0898 | -56.8726 | -56.0303 | -55.9982 | 65.7394 | -57.1884 | -57.0877 | -57.1243 | -57.28 | -56.9504 | 0.032044 | -0.004577 | -0.27466 | 1.0712 | 1.1307 | 0.28839 | 1.0986 | 0.25635 | -0.027466 | 0.018311 | -122.8088 | 0.036621 | 0.21057 | -0.11902 | 0.23804 | -0.091552 | 1.0391 | 122.5754 | 0.064087 | 0.10071 | 122.8455 | 122.9279 | 122.8775 | 122.9004 | -122.85 | -122.9095 | 122.6074 | 0.073242 | 2.6138 | 1.1627
1266.1719 | 123.0469 | -57.1426 | 65.6982 | -0.022431 | -0.00087374 | 0.061385 | 0.075454 | -0.00048063 | 0.0028327 | 0.012471 | -0.019653 | 0.0019567 | 0.001709 | 0.00091422 | -0.00086511 | -0.0019483 | 0.0028027 | -54.5197 | 65.7028 | -57.1198 | 65.5014 | -56.0394 | -56.868 | -56.0028 | -55.9525 | 65.7257 | -57.1747 | -57.0374 | -57.0831 | -57.225 | -56.8909 | 0.022888 | 0.004578 | -0.19684 | 1.1032 | 1.1398 | 0.27466 | 1.1169 | 0.25177 | -0.032044 | 0.027466 | -122.7356 | 0.059509 | 0.25177 | -0.082398 | 0.28381 | -0.050354 | 1.0803 | 122.6212 | 0.091553 | 0.13733 | 122.8226 | 122.9004 | 122.8455 | 122.8683 | -122.818 | -122.8729 | 122.644 | 0.10529 | 2.623 | 1.1902
1267.1719 | 123.0286 | -57.1198 | 65.6982 | -0.052948 | -0.00023294 | 0.063948 | 0.07524 | -0.0011214 | 0.0034735 | 0.0062762 | -0.03186 | 0.0019567 | 0.001068 | 0.0015552 | -0.00065151 | 0.0010425 | -0.0010425 | -54.5105 | 65.712 | -57.1106 | 65.4922 | -56.0623 | -56.868 | -55.9891 | -55.9799 | 65.7349 | -57.1747 | -57.0694 | -57.0877 | -57.2433 | -56.9092 | 0.009155 | 0.013733 | -0.20599 | 1.0574 | 1.1307 | 0.25177 | 1.1215 | 0.24262 | -0.054932 | 0.036621 | -122.7676 | 0.032043 | 0.21057 | -0.1236 | 0.2655 | -0.068664 | 1.0483 | 122.6028 | 0.086975 | 0.10529 | 122.8226 | 122.9095 | 122.8317 | 122.8546 | -122.8088 | -122.8729 | 122.612 | 0.050354 | 2.6093 | 1.1398
1268.1719 | 123.0057 | -57.1426 | 65.7211 | -0.13687 | 0.0019035 | 0.063948 | 0.074813 | 0.0010148 | 0.0028327 | 0.0094806 | -0.016602 | 0.0023839 | 0.003418 | -0.0010084 | -0.00086511 | -2.5678e-05 | 0.0010937 | -54.5242 | 65.7074 | -57.106 | 65.4694 | -56.0715 | -56.8817 | -56.0074 | -55.9891 | 65.744 | -57.1655 | -57.0831 | -57.106 | -57.2754 | -56.9504 | 0.036621 | -0.013733 | -0.25177 | 1.0712 | 1.1353 | 0.26093 | 1.0986 | 0.2243 | -0.022888 | 0.022889 | -122.8043 | 0.036621 | 0.19226 | -0.13275 | 0.21515 | -0.10986 | 1.0345 | 122.5754 | 0.059509 | 0.082397 | 122.8134 | 122.9095 | 122.85 | 122.8867 | -122.8271 | -122.8867 | 122.612 | 0.059509 | 2.6184 | 1.1536
1269.1719 | 122.937 | -57.1701 | 65.6891 | -0.091095 | -0.00087374 | 0.064589 | 0.074813 | 0.0040054 | 0.0034735 | 0.010121 | -0.03186 | 0.0017431 | 0.0014954 | 0.0062548 | -0.0012925 | -0.0019483 | 0.0017345 | -54.5013 | 65.7394 | -57.1152 | 65.4648 | -56.1035 | -56.9138 | -56.0486 | -56.0532 | 65.7532 | -57.193 | -57.0969 | -57.1518 | -57.2754 | -57.1014 | 0.054932 | 0.050354 | -0.2243 | 1.0666 | 1.1215 | 0.25635 | 1.0666 | 0.20142 | -0.022888 | 0.064087 | -122.7859 | 0.018311 | 0.068665 | -0.10529 | 0.091553 | -0.082398 | 1.0117 | 122.58 | 0.041199 | 0.09613 | 122.8546 | 122.9462 | 122.9095 | 122.9233 | -122.8043 | -122.8821 | 122.6349 | 0.073242 | 2.6688 | 1.1169
1270.1719 | 123.0194 | -57.1381 | 65.7349 | -0.23605 | -0.00066014 | 0.060744 | 0.076736 | 0.00016017 | 0.0045417 | 0.0073444 | -0.019653 | 0.00088875 | 0.0012818 | -0.00079478 | -0.0021469 | -0.0021619 | 0.00088014 | -54.2953 | 65.7074 | -57.1014 | 65.4556 | -56.0532 | -56.8909 | -56.0349 | -56.0257 | 65.744 | -57.1793 | -57.1014 | -57.1243 | -57.2937 | -56.9412 | 0.036622 | -0.027466 | -0.27924 | 1.0849 | 1.1032 | 0.24719 | 1.0666 | 0.21057 | -0.041198 | 0.009156 | -122.8363 | 0.013733 | 0.19684 | -0.15564 | 0.23804 | -0.11444 | 1.0483 | 122.5571 | 0.054931 | 0.07782 | 122.8088 | 122.9233 | 122.8455 | 122.8821 | -122.8363 | -122.9141 | 122.5937 | 0.036622 | 2.8427 | 1.1124
1271.1719 | 123.0377 | -57.1472 | 65.7211 | -0.091095 | 0.0016899 | 0.064162 | 0.073958 | -0.0028304 | 0.0028327 | 0.0088398 | -0.034912 | -0.00017945 | 0.0029906 | 0.0036914 | -0.0017197 | -0.0023755 | -0.00082886 | -54.5197 | 65.7028 | -57.1426 | 65.4922 | -56.0623 | -56.8771 | -55.9845 | -55.9891 | 65.7166 | -57.1701 | -57.0511 | -57.0786 | -57.2342 | -56.9 | 0.004578 | -0.01831 | -0.22888 | 1.0849 | 1.1627 | 0.27008 | 1.1581 | 0.2655 | -0.022888 | -0.004577 | -122.7722 | 0.068665 | 0.24719 | -0.086975 | 0.27008 | -0.064087 | 1.0803 | 122.6349 | 0.091553 | 0.11902 | 122.8455 | 122.8867 | 122.85 | 122.8638 | -122.8638 | -122.8912 | 122.6395 | 0.096131 | 2.6276 | 1.1581
1272.1719 | 123.0469 | -57.1472 | 65.6982 | -0.060578 | -0.0017281 | 0.06288 | 0.07524 | 0.0035782 | 0.0041143 | 0.0073444 | -0.034912 | 0.0019567 | -0.0021362 | 0.002196 | -0.00043791 | -0.0019483 | 0.0034435 | -54.5334 | 65.6891 | -57.1381 | 65.4694 | -56.0806 | -56.8771 | -56.0165 | -55.9845 | 65.7486 | -57.1884 | -57.0602 | -57.106 | -57.2433 | -56.9275 | 0.009155 | -0.009155 | -0.22888 | 1.0666 | 1.1307 | 0.27008 | 1.1215 | 0.26093 | -0.041199 | 0.050354 | -122.7585 | 0.041199 | 0.21973 | -0.09613 | 0.26093 | -0.054931 | 1.0574 | 122.6074 | 0.082398 | 0.12817 | 122.8271 | 122.937 | 122.8363 | 122.8958 | -122.8363 | -122.8867 | 122.6166 | 0.086975 | 2.6138 | 1.1627
1273.1719 | 123.1201 | -57.1152 | 65.7028 | -0.091095 | 0.00019446 | 0.063307 | 0.074599 | -0.0026168 | 0.0045417 | 0.0039264 | 0.0047608 | 0.0015295 | 0.00021363 | -0.0037854 | -0.00022431 | -0.0013073 | -0.0040333 | -54.5197 | 65.6708 | -57.1335 | 65.5426 | -56.012 | -56.8085 | -55.9296 | -55.925 | 65.6891 | -57.1838 | -57.0099 | -57.0374 | -57.1838 | -56.8359 | -0.018311 | -0.032044 | -0.16022 | 1.1032 | 1.1856 | 0.3067 | 1.2039 | 0.32501 | -0.068665 | -0.013733 | -122.7127 | 0.077819 | 0.27924 | -0.068665 | 0.3479 | 0 | 1.1215 | 122.6761 | 0.14648 | 0.17395 | 122.8043 | 122.8729 | 122.7859 | 122.8043 | -122.8363 | -122.8867 | 122.6578 | 0.10529 | 2.5955 | 1.1902
1274.1719 | 123.111 | -57.1335 | 65.712 | -0.16739 | -1.9142e-05 | 0.065016 | 0.078658 | -0.0011214 | 0.0039007 | 0.012899 | -0.0043946 | 0.0017431 | -0.00085457 | 0.00091422 | -0.0017197 | -0.00088008 | 0.0019483 | -54.5288 | 65.6754 | -57.1152 | 65.5289 | -55.9982 | -56.8359 | -55.9525 | -55.9204 | 65.7257 | -57.1609 | -56.9916 | -57.0511 | -57.2021 | -56.8634 | 0.018311 | -0.036621 | -0.1831 | 1.1353 | 1.181 | 0.29755 | 1.1627 | 0.27924 | -0.027466 | 0.013733 | -122.7036 | 0.082398 | 0.27008 | -0.068664 | 0.29755 | -0.041198 | 1.1169 | 122.644 | 0.10986 | 0.16937 | 122.7905 | 122.8867 | 122.8088 | 122.8592 | -122.8271 | -122.8729 | 122.6624 | 0.14191 | 2.6047 | 1.2131
1275.1719 | 123.0835 | -57.106 | 65.7074 | -0.11398 | 0.00083526 | 0.064589 | 0.076949 | 0.0016556 | 0.0030463 | 0.0064898 | -0.010498 | 0.0021703 | -0.00064077 | -0.0014356 | -0.0023605 | 0.00061532 | 0.0057935 | -54.5517 | 65.6982 | -57.2021 | 65.5151 | -56.0349 | -56.8451 | -55.9479 | -55.9341 | 65.712 | -57.1518 | -57.0374 | -57.0694 | -57.1793 | -56.8497 | -0.09613 | -0.009155 | -0.19226 | 1.0712 | 1.1581 | 0.26093 | 1.2543 | 0.35706 | -0.045776 | 0.004578 | -122.7448 | 0.036621 | 0.25635 | -0.073242 | 0.30212 | -0.027466 | 1.1673 | 122.7173 | 0.082397 | 0.11444 | 122.9004 | 122.8638 | 122.8043 | 122.818 | -122.9095 | -122.8592 | 122.6212 | 0.068664 | 2.5543 | 1.1719
1276.1719 | 122.9553 | -57.1381 | 65.7578 | -0.083466 | 0.0016899 | 0.061598 | 0.077163 | -0.00026703 | 0.0032599 | 0.009267 | -0.03186 | 0.0013159 | -0.0012818 | 0.002196 | -0.0019333 | -0.0028027 | -0.00082886 | -54.5654 | 65.7074 | -57.193 | 65.4602 | -56.1172 | -56.9046 | -56.0211 | -56.0623 | 65.7715 | -57.2021 | -57.106 | -57.1426 | -57.3074 | -56.955 | -0.054931 | -0.050354 | -0.29755 | 1.0208 | 1.1169 | 0.23346 | 1.1719 | 0.28839 | -0.064086 | 0.013733 | -122.8638 | -0.004577 | 0.18311 | -0.16937 | 0.24719 | -0.10529 | 1.0757 | 122.6532 | 0.059509 | 0.09613 | 122.9004 | 122.9736 | 122.8455 | 122.9095 | -122.9507 | -122.9599 | 122.5983 | 0.032044 | 2.5726 | 1.0757
1277.1719 | 123.0789 | -57.1564 | 65.7028 | -0.045319 | 0.00019446 | 0.064375 | 0.076308 | 0.0033646 | 0.0026191 | 0.0094806 | -0.010498 | -0.0016749 | 0.0014954 | -0.0020764 | -0.0015061 | -0.0030163 | 0.0025891 | -54.5654 | 65.712 | -57.1793 | 65.506 | -56.0532 | -56.8497 | -55.9845 | -55.9753 | 65.7303 | -57.1655 | -57.0419 | -57.074 | -57.2113 | -56.9046 | -0.022888 | 0.009155 | -0.19684 | 1.1032 | 1.1719 | 0.3067 | 1.1948 | 0.32959 | -0.009155 | 0.027466 | -122.7448 | 0.082397 | 0.25177 | -0.054932 | 0.26093 | -0.045777 | 1.1261 | 122.6852 | 0.091552 | 0.1236 | 122.8912 | 122.8958 | 122.8683 | 122.8867 | -122.8821 | -122.8683 | 122.6624 | 0.11444 | 2.5909 | 1.181
1278.1719 | 123.0194 | -57.1426 | 65.7257 | -0.075836 | -0.00066014 | 0.063948 | 0.078231 | 0.00037377 | 0.0030463 | 0.0090534 | -0.010498 | 0.00024775 | 0.001068 | 0.001128 | -0.0012925 | -0.00045288 | -0.00040166 | -54.5837 | 65.712 | -57.1884 | 65.6387 | -55.9021 | -56.9595 | -56.0165 | -56.044 | 65.7257 | -57.1793 | -57.0969 | -57.1793 | -57.3029 | -56.9687 | -0.045777 | -0.013733 | -0.086975 | 1.2405 | 1.1261 | 0.18311 | 1.1719 | 0.22888 | -0.036621 | 0 | -122.8226 | -0.036621 | 0.17395 | -0.16022 | 0.21057 | -0.1236 | 1.2863 | 122.8271 | 0 | 0.082397 | 122.9004 | 122.905 | 122.8546 | 122.8683 | -122.9141 | -122.905 | 122.7814 | 0.045776 | 2.5589 | 1.0986
1279.1719 | 122.9874 | -57.1564 | 65.7257 | -0.10635 | -0.0010873 | 0.062025 | 0.076308 | 0.00251 | 0.0053961 | 0.0079852 | -0.050171 | 0.0023839 | 2.8e-08 | 0.0101 | -0.0010787 | 0.00018792 | 0.0013073 | -54.5883 | 65.6845 | -57.1976 | 65.2496 | -56.3461 | -56.5201 | -55.8014 | -56.0074 | 65.7578 | -57.1976 | -57.1106 | -57.1518 | -57.3029 | -56.9641 | -0.041199 | -0.041199 | -0.47607 | 0.81024 | 1.355 | 0.63629 | 1.3962 | 0.67749 | -0.041199 | 0.032043 | -122.8363 | 0.004578 | 0.19226 | -0.14648 | 0.23346 | -0.10528 | 0.85144 | 122.4472 | 0.045777 | 0.086975 | 122.8821 | 122.9553 | 122.8409 | 122.9141 | -122.9233 | -122.9233 | 122.406 | 0.045776 | 2.5681 | 1.149
1280.1719 | 122.9782 | -57.1655 | 65.7394 | -0.060578 | -0.0013009 | 0.063521 | 0.078872 | 0.0012284 | 0.0032599 | 0.0071308 | -0.12036 | 0.0019567 | -0.00064077 | -0.0027174 | -0.0015061 | 0.00018792 | 0.0019483 | -54.5975 | 65.7074 | -57.1884 | 65.451 | -56.1218 | -56.9046 | -56.1264 | -55.7877 | 65.7486 | -57.1747 | -57.1106 | -57.1335 | -57.2983 | -56.9641 | -0.022889 | -0.032044 | -0.28839 | 1.0437 | 1.0391 | 0.26093 | 1.062 | 0.28381 | -0.009156 | 0.009155 | -122.85 | 0.032043 | 0.20142 | -0.13275 | 0.21057 | -0.1236 | 1.0666 | 122.6395 | 0.041199 | 0.064087 | 122.8958 | 122.9233 | 122.8729 | 122.9141 | -122.9279 | -122.9141 | 122.6166 | 0.054931 | 2.5681 | 1.3779
1281.1719 | 123.1338 | -57.0969 | 65.6662 | -0.037689 | -1.9142e-05 | 0.06523 | 0.074172 | -0.0021896 | 0.0051825 | 0.0049946 | -0.0013428 | 0.00067495 | 0.00021363 | 0.00048702 | -0.0021469 | -0.0019483 | -0.0010425 | -54.57 | 65.6799 | -57.1655 | 65.5289 | -55.9937 | -56.7947 | -55.9204 | -55.9204 | 65.6891 | -57.1747 | -57.0145 | -57.0374 | -57.1884 | -56.8497 | -0.068664 | 0.013733 | -0.13733 | 1.1032 | 1.1765 | 0.30212 | 1.2451 | 0.37079 | -0.07782 | 0.022888 | -122.6807 | 0.059509 | 0.24719 | -0.091553 | 0.32501 | -0.013733 | 1.1719 | 122.6944 | 0.13733 | 0.16022 | 122.8455 | 122.8638 | 122.7768 | 122.7859 | -122.8317 | -122.8409 | 122.6257 | 0.082398 | 2.5269 | 1.1765
1282.1719 | 122.9645 | -57.1564 | 65.7166 | -0.15213 | 0.0014761 | 0.06523 | 0.076949 | -0.00090783 | 0.0043281 | 0.0096942 | -0.044067 | 0.0017431 | -0.0023498 | 0.0049732 | -0.00043791 | 0.0023241 | -0.00040166 | -54.6021 | 65.7028 | -57.1884 | 65.4419 | -56.1493 | -56.9092 | -56.0165 | -56.0394 | 65.7303 | -57.1976 | -57.3349 | -56.9092 | -57.0877 | -56.8817 | -0.032044 | -0.013733 | -0.27466 | 1.0071 | 1.1398 | 0.24719 | 1.1719 | 0.27924 | -0.041199 | 0.013733 | -123.0515 | 0.24719 | 0.27466 | 0.068664 | 0.31586 | 0.10986 | 1.0391 | 122.6303 | 0.28839 | -0.13733 | 122.8912 | 122.9279 | 122.8592 | 122.8867 | -122.905 | -122.9141 | 122.5983 | -0.17853 | 2.5543 | 1.1169
1283.1719 | 123.0331 | -57.1518 | 65.7074 | -0.03006 | -0.0021555 | 0.064589 | 0.076522 | -0.0028304 | 0.0032599 | 0.009267 | -0.028809 | 0.0019567 | 0.00064083 | 0.0015552 | 0.0010575 | -0.0023755 | 0.0021619 | -54.6021 | 65.7074 | -57.1976 | 65.4556 | -56.1127 | -56.8817 | -55.9891 | -56.012 | 65.7486 | -57.1884 | -57.0969 | -57.1472 | -57.2937 | -56.9641 | -0.045777 | 0 | -0.25177 | 1.0391 | 1.1627 | 0.27008 | 1.2085 | 0.31586 | -0.036622 | 0.041199 | -122.8043 | 0.004577 | 0.18768 | -0.14191 | 0.2243 | -0.10529 | 1.0849 | 122.6532 | 0.041199 | 0.091553 | 122.905 | 122.937 | 122.8592 | 122.9004 | -122.905 | -122.8958 | 122.6074 | 0.054931 | 2.5497 | 1.1398
1284.1719 | 123.024 | -57.1564 | 65.712 | 0.1149 | -0.0015145 | 0.064589 | 0.076308 | -0.0034714 | 0.0043281 | 0.0084124 | -0.0013428 | 0.0017431 | 0.00042723 | 0.0047594 | -0.00022431 | -0.0028027 | 0.0010937 | -54.6433 | 65.7028 | -57.1838 | 65.4694 | -56.1081 | -56.9046 | -55.9937 | -56.0257 | 65.744 | -57.1655 | -57.1106 | -57.1426 | -57.2891 | -56.9687 | -0.027466 | -0.009155 | -0.24262 | 1.0483 | 1.1627 | 0.25177 | 1.1902 | 0.27924 | -0.009155 | 0.032044 | -122.8226 | 0.013733 | 0.18768 | -0.13275 | 0.19684 | -0.1236 | 1.0757 | 122.6532 | 0.022888 | 0.054931 | 122.8867 | 122.9095 | 122.8592 | 122.9004 | -122.8958 | -122.8775 | 122.6257 | 0.045776 | 2.5131 | 1.1307
1285.1719 | 123.0194 | -57.1564 | 65.7349 | -0.4039 | 0.0019035 | 0.065871 | 0.076522 | -0.0015488 | 0.0056097 | 0.0096942 | -0.041016 | 0.0019567 | 0.0012818 | -0.0076306 | -1.0706e-05 | -0.00045288 | -0.0033923 | -54.6524 | 65.657 | -57.225 | 65.4648 | -56.1172 | -56.8634 | -56.012 | -56.0394 | 65.7303 | -57.1884 | -57.106 | -57.1518 | -57.3074 | -56.955 | -0.068665 | -0.07782 | -0.27008 | 1.0391 | 1.1444 | 0.29297 | 1.2131 | 0.36163 | -0.032044 | -0.004577 | -122.8409 | 0.004578 | 0.20142 | -0.15106 | 0.23346 | -0.11902 | 1.1078 | 122.6898 | 0.036622 | 0.082398 | 122.8821 | 122.9187 | 122.8134 | 122.8867 | -122.9599 | -122.9233 | 122.6212 | 0.050354 | 2.504 | 1.1169
1286.1719 | 123.0972 | -57.1381 | 65.6616 | -0.11398 | 0.00019446 | 0.063307 | 0.075667 | -5.343e-05 | 0.0062507 | 0.0094806 | -0.01355 | 0.0011023 | -0.0010682 | -0.0050672 | -1.0706e-05 | -0.0023755 | 0.00045294 | -54.6112 | 65.6937 | -57.2113 | 65.4739 | -56.0761 | -56.868 | -55.9799 | -55.9891 | 65.7028 | -57.1747 | -57.0602 | -57.0786 | -57.2433 | -56.8954 | -0.073242 | 0.032044 | -0.18768 | 1.062 | 1.1581 | 0.27008 | 1.2314 | 0.34332 | -0.036621 | 0.041199 | -122.7219 | 0.05951 | 0.24262 | -0.10529 | 0.27924 | -0.068664 | 1.1353 | 122.6852 | 0.096131 | 0.11444 | 122.905 | 122.8775 | 122.8317 | 122.8409 | -122.8729 | -122.8363 | 122.612 | 0.07782 | 2.5269 | 1.149
1287.1719 | 123.0423 | -57.1609 | 65.7257 | -0.11398 | 0.00062166 | 0.063948 | 0.074813 | 0.0040054 | 0.0036871 | 0.0064898 | -0.019653 | 0.0015295 | 0.00085443 | -0.0052808 | -0.0015061 | 0.00018792 | -0.00061526 | -54.6158 | 65.6754 | -57.1793 | 65.4831 | -56.0898 | -56.8771 | -55.9799 | -56.0028 | 65.7303 | -57.1838 | -57.074 | -57.1152 | -57.2388 | -56.9366 | -0.01831 | -0.050354 | -0.24262 | 1.0712 | 1.181 | 0.28381 | 1.1993 | 0.30212 | -0.022888 | 0.004578 | -122.7997 | 0.045777 | 0.2243 | -0.07782 | 0.24719 | -0.054932 | 1.0895 | 122.6624 | 0.068665 | 0.10986 | 122.8546 | 122.9141 | 122.8363 | 122.8912 | -122.905 | -122.9095 | 122.644 | 0.086975 | 2.5452 | 1.1581
1288.1719 | 123.1018 | -57.1335 | 65.6845 | -0.10635 | -1.9142e-05 | 0.063734 | 0.076522 | 0.001442 | 0.0017645 | 0.0096942 | 0.013916 | -0.00017945 | 0.0014954 | 0.0049732 | -0.00065151 | -0.0019483 | -0.0025379 | -54.5746 | 65.6525 | -57.1609 | 65.5197 | -56.0349 | -56.781 | -55.8975 | -55.9296 | 65.6845 | -57.1564 | -57.0099 | -57.0465 | -57.193 | -56.8451 | -0.027466 | -0.032043 | -0.1648 | 1.0986 | 1.236 | 0.35248 | 1.2634 | 0.37994 | -0.022888 | 0 | -122.6944 | 0.086975 | 0.28839 | -0.059509 | 0.31128 | -0.036621 | 1.1261 | 122.6807 | 0.10986 | 0.14648 | 122.8134 | 122.8409 | 122.786 | 122.818 | -122.8455 | -122.8409 | 122.6532 | 0.1236 | 2.5589 | 1.2039
1289.1719 | 122.9782 | -57.1609 | 65.7211 | -0.11398 | 0.00083526 | 0.063307 | 0.076095 | -0.00090783 | 0.0017645 | 0.0073444 | -0.03186 | 0.0013159 | 0.003418 | 0.00048702 | -0.0010787 | -0.0015211 | 0.0010937 | -54.657 | 65.6891 | -57.2067 | 65.4556 | -56.1264 | -56.8954 | -56.0028 | -56.2592 | 65.6891 | -57.2525 | -57.1289 | -57.0923 | -57.2891 | -56.9733 | -0.045776 | -0.032043 | -0.2655 | 1.0345 | 1.1581 | 0.2655 | 1.2039 | 0.31128 | -0.091552 | -0.032043 | -122.85 | 0.068665 | 0.18768 | -0.12817 | 0.27923 | -0.036622 | 1.0803 | 122.6624 | 0.16022 | 0.1236 | 122.8958 | 122.9416 | 122.85 | 122.85 | -122.9279 | -122.9736 | 122.6166 | 0.032044 | 2.504 | 0.90179
1290.1719 | 122.9874 | -57.1243 | 65.7532 | -0.052948 | -0.00087374 | 0.063521 | 0.075454 | 0.0055008 | 0.0045417 | 0.010335 | -0.034912 | 0.0015295 | 0.001709 | -0.0018628 | -0.0019333 | 0.0025379 | -0.0036059 | -54.6433 | 65.7303 | -57.2021 | 65.4373 | -56.1493 | -56.9046 | -56.0257 | -56.0715 | 65.7578 | -57.1793 | -57.2662 | -57.2662 | -56.987 | -56.7673 | -0.077819 | -0.022888 | -0.31586 | 0.97504 | 1.0986 | 0.21973 | 1.1765 | 0.29755 | -0.054931 | 0.004577 | -123.0194 | -0.14191 | 0.35706 | 0.13733 | 0.41199 | 0.19226 | 1.0529 | 122.6395 | -0.086975 | -0.086975 | 122.9324 | 122.937 | 122.8546 | 122.8821 | -122.9553 | -122.9324 | 122.5616 | -0.14191 | 2.4811 | 1.0529
1291.1719 | 123.0148 | -57.1564 | 65.7074 | -0.12924 | -1.9142e-05 | 0.063307 | 0.076949 | 0.0012284 | 0.0053961 | 0.0096942 | 0.001709 | 0.0015295 | 0.001068 | 0.0024096 | -0.0017197 | -0.0032301 | -0.0012561 | -54.6249 | 65.6982 | -57.1655 | 65.451 | -56.1081 | -56.8909 | -56.0028 | -56.0486 | 65.712 | -57.193 | -57.1198 | -57.1609 | -57.2983 | -56.9778 | -0.009155 | -0.009155 | -0.25635 | 1.0483 | 1.1536 | 0.2655 | 1.1627 | 0.27466 | -0.036621 | 0.004578 | -122.8271 | -0.004578 | 0.17853 | -0.14191 | 0.21515 | -0.10529 | 1.0574 | 122.6166 | 0.032043 | 0.073242 | 122.8638 | 122.905 | 122.8546 | 122.8683 | -122.8729 | -122.9004 | 122.6074 | 0.036621 | 2.5314 | 1.1078
1292.1719 | 123.0423 | -57.1518 | 65.7074 | -0.083466 | 0.00019446 | 0.062453 | 0.075027 | -0.00026703 | 0.0047553 | 0.0099078 | -0.025757 | 0.00088875 | -0.0014954 | -0.00036738 | -0.0025741 | -0.0017347 | -0.00018806 | -54.6433 | 65.6616 | -57.1793 | 65.4922 | -56.0852 | -56.8771 | -55.9616 | -56.0074 | 65.6982 | -57.1793 | -57.0465 | -57.1014 | -57.2342 | -56.9138 | -0.027466 | -0.045776 | -0.21515 | 1.0666 | 1.1902 | 0.27466 | 1.2177 | 0.30212 | -0.027466 | -0.009155 | -122.7539 | 0.050354 | 0.23804 | -0.082398 | 0.2655 | -0.054932 | 1.0941 | 122.6715 | 0.07782 | 0.13275 | 122.8409 | 122.8775 | 122.8134 | 122.85 | -122.8867 | -122.8867 | 122.644 | 0.10529 | 2.5085 | 1.1444
1293.1719 | 123.0148 | -57.1609 | 65.7349 | -0.068207 | 0.00040806 | 0.06288 | 0.074599 | 0.0044328 | 0.0032599 | 0.0077716 | -0.037964 | 0.0017431 | -0.00042717 | 0.002196 | -0.0012925 | -0.0025891 | -0.0016833 | -54.6478 | 65.6708 | -57.2021 | 65.3183 | -55.8517 | -56.694 | -56.0257 | -56.0257 | 65.7532 | -57.1793 | -57.1289 | -57.1564 | -57.3029 | -56.987 | -0.041198 | -0.064087 | -0.41657 | 1.3092 | 1.1353 | 0.46692 | 1.1765 | 0.50812 | -0.01831 | 0.018311 | -122.8638 | 0.004578 | 0.17395 | -0.14191 | 0.19226 | -0.1236 | 1.3504 | 122.5204 | 0.022888 | 0.050354 | 122.8729 | 122.9324 | 122.8317 | 122.9141 | -122.937 | -122.9141 | 122.4792 | 0.032044 | 2.5131 | 1.1353
1294.1719 | 122.9965 | -57.1655 | 65.7211 | -0.068207 | 0.0016899 | 0.06523 | 0.075454 | 0.0016556 | 0.0026191 | 0.0056354 | -0.022705 | 0.0036657 | 0.001709 | 0.0034778 | 0.00041649 | -0.0017347 | -0.00061526 | -54.6844 | 65.6845 | -57.2021 | 65.4465 | -56.1356 | -56.9 | -56.0028 | -56.337 | 65.6662 | -57.2388 | -57.0831 | -57.1747 | -57.3074 | -56.9641 | -0.036621 | -0.036621 | -0.27466 | 1.03 | 1.1627 | 0.2655 | 1.1993 | 0.30212 | -0.073243 | -0.054931 | -122.8043 | -0.009156 | 0.20142 | -0.14191 | 0.27466 | -0.068664 | 1.0666 | 122.6486 | 0.064087 | 0.15564 | 122.8867 | 122.905 | 122.85 | 122.8317 | -122.9233 | -122.9599 | 122.612 | 0.082397 | 2.4811 | 0.82855
1295.1719 | 123.1018 | -57.1243 | 65.6616 | -0.11398 | -0.00066014 | 0.064375 | 0.075454 | 0.001442 | 0.0043281 | 0.0086262 | 0.016968 | 0.00067495 | 0.0012818 | 0.00048702 | -0.0030013 | -0.0015211 | 0.0023755 | -54.657 | 65.6799 | -57.1838 | 65.506 | -56.044 | -56.8405 | -55.9387 | -55.9525 | 65.6937 | -57.1701 | -57.0282 | -57.0648 | -57.225 | -56.868 | -0.059509 | 0.018311 | -0.15564 | 1.0803 | 1.1856 | 0.28381 | 1.2451 | 0.34332 | -0.045776 | 0.032044 | -122.6898 | 0.05951 | 0.25635 | -0.10071 | 0.30212 | -0.054932 | 1.1398 | 122.6898 | 0.10529 | 0.14191 | 122.8638 | 122.8638 | 122.8043 | 122.818 | -122.8455 | -122.8317 | 122.6303 | 0.096131 | 2.4673 | 1.1719
1296.1719 | 122.9965 | -57.1838 | 65.7074 | -0.11398 | 0.0012625 | 0.063521 | 0.075027 | 0.001442 | 0.0015509 | 0.0090534 | -0.028809 | 0.0013159 | 2.8e-08 | -0.00015378 | -0.00043791 | -0.0032301 | -0.0025379 | -54.6707 | 65.6845 | -57.2113 | 65.4556 | -56.1447 | -56.9 | -56.0257 | -56.1081 | 65.744 | -57.2067 | -57.1243 | -57.1793 | -57.3166 | -56.9778 | -0.027466 | -0.022888 | -0.25177 | 1.0391 | 1.1581 | 0.28381 | 1.1856 | 0.31128 | -0.022888 | 0.036622 | -122.8317 | 0.004578 | 0.20599 | -0.13275 | 0.22888 | -0.10986 | 1.0666 | 122.6669 | 0.027466 | 0.082397 | 122.8958 | 122.9507 | 122.8683 | 122.9279 | -122.9187 | -122.9141 | 122.6395 | 0.059509 | 2.5131 | 1.0757
1297.1719 | 123.0148 | -57.1609 | 65.7349 | -0.12924 | 0.0010489 | 0.063307 | 0.074599 | -0.0030442 | 0.0032599 | 0.007558 | -0.053223 | 0.0019567 | 0.001709 | 0.0077502 | -0.0012925 | -0.0028027 | -0.00040166 | -54.6707 | 65.6891 | -57.2159 | 65.2542 | -56.2546 | -56.5201 | -55.8701 | -56.012 | 65.7486 | -57.1747 | -57.1243 | -57.1564 | -57.3212 | -56.9733 | -0.054931 | -0.045776 | -0.48065 | 0.90637 | 1.2909 | 0.64087 | 1.3458 | 0.6958 | -0.013733 | 0.013733 | -122.8592 | 0.004578 | 0.18768 | -0.16022 | 0.20142 | -0.14648 | 0.9613 | 122.4701 | 0.018311 | 0.050354 | 122.905 | 122.9233 | 122.85 | 122.9095 | -122.9507 | -122.9095 | 122.4152 | 0.036621 | 2.4902 | 1.149
1298.1719 | 122.9965 | -57.1426 | 65.744 | -0.098725 | 0.00019446 | 0.062453 | 0.075881 | 0.0029374 | 0.0017645 | 0.0088398 | -0.028809 | 0.0019567 | 0.0021362 | 0.00091422 | -0.0015061 | -0.0025891 | -0.0016833 | -54.6844 | 65.6937 | -57.2205 | 65.4602 | -56.1356 | -56.9138 | -56.0074 | -55.9799 | 65.7166 | -57.2479 | -57.193 | -57.1106 | -57.2571 | -56.9824 | -0.07782 | -0.050354 | -0.28381 | 1.0071 | 1.1353 | 0.22888 | 1.2131 | 0.3067 | -0.10529 | -0.027466 | -122.937 | 0.032043 | 0.16022 | -0.11444 | 0.2655 | -0.009155 | 1.0849 | 122.6807 | 0.13733 | 0.054932 | 122.9141 | 122.9645 | 122.8363 | 122.8592 | -122.9645 | -122.9919 | 122.6028 | -0.050354 | 2.4582 | 1.1627
1299.1719 | 123.0103 | -57.1609 | 65.7074 | -0.068207 | 0.00019446 | 0.064803 | 0.074599 | -0.001976 | 0.0015509 | 0.010335 | -0.019653 | 0.00067495 | 0.00042723 | -0.0025036 | -0.0015061 | -0.0032301 | -0.0021107 | -54.6799 | 65.6937 | -57.2021 | 65.4373 | -56.1356 | -56.8909 | -56.0074 | -56.0394 | 65.7303 | -57.2205 | -57.1243 | -57.1518 | -57.2845 | -56.9595 | -0.041198 | -0.013732 | -0.27008 | 1.0254 | 1.1536 | 0.27008 | 1.1948 | 0.31128 | -0.059509 | 0.022889 | -122.8317 | 0.009156 | 0.20142 | -0.1236 | 0.26093 | -0.064087 | 1.0666 | 122.6395 | 0.068665 | 0.09613 | 122.8958 | 122.9507 | 122.8546 | 122.8912 | -122.9095 | -122.9279 | 122.5983 | 0.036621 | 2.4811 | 1.1215
1300.1719 | 123.0286 | -57.1747 | 65.6982 | -0.32761 | 0.0021171 | 0.062025 | 0.076308 | 0.0012284 | 0.0034735 | 0.0096942 | -0.034912 | 0.0019567 | 0.001709 | 0.0015552 | 0.00020289 | -0.0028027 | -0.0012561 | -54.4647 | 65.6754 | -57.2067 | 65.4419 | -56.1218 | -56.8771 | -56.0074 | -56.0806 | 65.7166 | -57.1701 | -57.1243 | -57.1609 | -57.2983 | -56.9687 | -0.032043 | -0.022888 | -0.25635 | 1.0529 | 1.1673 | 0.29755 | 1.1993 | 0.32959 | 0.004578 | 0.018311 | -122.8226 | 0.013733 | 0.20599 | -0.1236 | 0.20142 | -0.12817 | 1.0849 | 122.6486 | 0.009155 | 0.045776 | 122.8821 | 122.8867 | 122.85 | 122.8912 | -122.905 | -122.8683 | 122.6166 | 0.050354 | 2.71 | 1.0941
1301.1719 | 122.9782 | -57.1793 | 65.7257 | -0.083466 | 0.0010489 | 0.063734 | 0.077376 | 0.001442 | 0.0058233 | 0.0090534 | -0.025757 | 0.0023839 | 2.8e-08 | -0.00058098 | -0.00022431 | -0.0017347 | -0.0012561 | -54.6661 | 65.6937 | -57.2205 | 65.4602 | -56.1356 | -56.8954 | -56.0028 | -56.0944 | 65.7303 | -57.225 | -57.1564 | -57.2021 | -57.3486 | -56.9916 | -0.041199 | -0.032043 | -0.2655 | 1.0437 | 1.1765 | 0.28381 | 1.2177 | 0.32501 | -0.045777 | 0.004578 | -122.8821 | -0.022888 | 0.18768 | -0.16937 | 0.23346 | -0.1236 | 1.0849 | 122.6807 | 0.022889 | 0.068665 | 122.9141 | 122.9553 | 122.8729 | 122.9095 | -122.9462 | -122.9507 | 122.6395 | 0.022888 | 2.5131 | 1.0849
1302.1719 | 122.9782 | -57.1472 | 65.7303 | -0.098725 | -1.9142e-05 | 0.062666 | 0.075667 | 0.0037918 | 0.0047553 | 0.010976 | -0.050171 | 0.0019567 | 0.0014954 | -0.0093396 | -0.00086511 | -0.0030163 | 0.00066654 | -54.7119 | 65.6982 | -57.193 | 65.4236 | -56.1356 | -56.9183 | -55.9937 | -56.0532 | 65.7303 | -57.2159 | -57.1747 | -57.1243 | -57.2525 | -56.9641 | -0.045776 | -0.032044 | -0.3067 | 1.0117 | 1.1536 | 0.22888 | 1.1993 | 0.27466 | -0.068664 | 0 | -122.905 | 0.022888 | 0.18311 | -0.10529 | 0.25177 | -0.036621 | 1.0574 | 122.6166 | 0.091552 | 0.041198 | 122.8912 | 122.9462 | 122.8455 | 122.8775 | -122.9233 | -122.9462 | 122.5708 | -0.027466 | 2.4353 | 1.0941
1303.1719 | 122.9736 | -57.1564 | 65.7303 | -0.045319 | -0.00087374 | 0.062666 | 0.07524 | 0.00080117 | 0.0053961 | 0.0088398 | -0.037964 | 0.0017431 | 0.00042723 | 0.0017688 | -0.00086511 | -2.5678e-05 | 0.00045294 | -54.6707 | 65.6937 | -57.1838 | 65.4877 | -56.0852 | -56.8542 | -55.9799 | -56.0394 | 65.744 | -57.2021 | -57.1381 | -57.1655 | -57.312 | -56.9778 | -0.027466 | -0.036621 | -0.24262 | 1.0712 | 1.1765 | 0.30212 | 1.2039 | 0.32959 | -0.045776 | 0.013733 | -122.8683 | -0.009155 | 0.17853 | -0.15564 | 0.2243 | -0.10986 | 1.0986 | 122.6715 | 0.036621 | 0.064086 | 122.8775 | 122.9462 | 122.85 | 122.9004 | -122.9141 | -122.9324 | 122.644 | 0.01831 | 2.4857 | 1.1169
1304.1719 | 123.0057 | -57.1426 | 65.7257 | -0.083466 | -0.0015145 | 0.06523 | 0.07524 | 0.00037377 | 0.0028327 | 0.007558 | -0.019653 | 0.0013159 | 0.0042724 | -0.0035718 | -0.0021469 | -0.00088008 | -0.00082886 | -54.657 | 65.6937 | -57.1793 | 65.4785 | -56.0715 | -56.8405 | -55.957 | -56.0303 | 65.7303 | -57.1884 | -57.1198 | -57.1426 | -57.2754 | -56.9641 | -0.036621 | -0.032043 | -0.24719 | 1.0712 | 1.1856 | 0.30212 | 1.2222 | 0.33874 | -0.045777 | 0.004578 | -122.8455 | 0 | 0.17853 | -0.13275 | 0.2243 | -0.086975 | 1.1078 | 122.6578 | 0.045777 | 0.068665 | 122.8729 | 122.9187 | 122.8363 | 122.8729 | -122.905 | -122.9141 | 122.6212 | 0.022888 | 2.4857 | 1.1124
1305.1719 | 122.9599 | -57.1747 | 65.712 | -0.10635 | 0.0010489 | 0.061171 | 0.074386 | 0.0027238 | 0.0021917 | 0.0088398 | -0.01355 | 0.0043065 | 0.0012818 | -0.0016492 | -0.0019333 | -0.0030163 | -0.0016833 | -54.7211 | 65.6799 | -57.2205 | 65.2359 | -55.9387 | -56.5979 | -55.9616 | -56.0165 | 65.7578 | -57.2067 | -57.1335 | -57.1655 | -57.3303 | -56.987 | -0.045776 | -0.032043 | -0.47607 | 1.236 | 1.2131 | 0.57678 | 1.2588 | 0.62256 | -0.032043 | 0.045776 | -122.8455 | 0.009156 | 0.18768 | -0.15564 | 0.21973 | -0.1236 | 1.2817 | 122.4564 | 0.041199 | 0.073242 | 122.9004 | 122.9645 | 122.8546 | 122.9324 | -122.9324 | -122.9187 | 122.4106 | 0.041199 | 2.4536 | 1.1581
1306.1719 | 122.9645 | -57.1655 | 65.6982 | -0.1445 | 0.0021171 | 0.064375 | 0.076308 | -0.0021896 | 0.0032599 | 0.0079852 | -0.16003 | -0.00082025 | 0.00064083 | -0.0010084 | -0.0015061 | -0.00088008 | 0.00088014 | -54.7256 | 65.6891 | -57.2159 | 65.4419 | -56.1539 | -56.9 | -55.9937 | -55.8563 | 65.7074 | -57.193 | -57.1381 | -57.1655 | -57.2891 | -56.9733 | -0.050354 | -0.009155 | -0.25635 | 1.0117 | 1.1719 | 0.2655 | 1.2222 | 0.31586 | -0.027466 | 0.009155 | -122.8363 | 0 | 0.19226 | -0.1236 | 0.21973 | -0.096131 | 1.062 | 122.6578 | 0.027466 | 0.054931 | 122.905 | 122.9004 | 122.8546 | 122.8729 | -122.9141 | -122.8912 | 122.6074 | 0.027465 | 2.4399 | 1.3092
1307.1719 | 122.9874 | -57.1564 | 65.7166 | -0.037689 | -0.0010873 | 0.065016 | 0.077163 | -0.0017624 | 0.0045417 | 0.0084124 | -0.019653 | 0.0015295 | 2.8e-08 | -0.0044262 | -0.0010787 | -0.0028027 | 0.0023755 | -54.6936 | 65.6754 | -57.2113 | 65.4694 | -56.1035 | -56.8588 | -55.9799 | -56.0715 | 65.7394 | -57.1976 | -57.1472 | -57.1884 | -57.3074 | -56.9916 | -0.054932 | -0.041199 | -0.24719 | 1.0529 | 1.1765 | 0.29755 | 1.2314 | 0.35248 | -0.041199 | 0.022888 | -122.8638 | -0.032044 | 0.16479 | -0.15106 | 0.20599 | -0.10986 | 1.1078 | 122.6807 | 0.009155 | 0.050354 | 122.8867 | 122.937 | 122.8317 | 122.8958 | -122.9279 | -122.9141 | 122.6257 | 0.009155 | 2.4628 | 1.0849
1308.1719 | 123.0743 | -57.1609 | 65.6616 | -0.098725 | -0.0015145 | 0.065871 | 0.073958 | 0.0029374 | 0.0043281 | 0.0067036 | -0.025757 | 0.0023839 | 2.8e-08 | 0.00048702 | -0.00043791 | -0.00045288 | 0.00023934 | -54.7256 | 65.6937 | -57.2113 | 65.419 | -56.1539 | -56.9275 | -56.0211 | -56.1081 | 65.7303 | -57.2205 | -57.1655 | -57.2067 | -57.3349 | -56.987 | -0.050354 | 0.032044 | -0.24262 | 1.0071 | 1.1398 | 0.23346 | 1.1902 | 0.28381 | -0.059509 | 0.068665 | -122.8271 | -0.045776 | 0.17395 | -0.17395 | 0.23346 | -0.11444 | 1.0574 | 122.6303 | 0.013733 | 0.054932 | 122.905 | 122.9507 | 122.8546 | 122.8912 | -122.8729 | -122.8821 | 122.58 | -0.004577 | 2.4353 | 1.0529
1309.1719 | 122.9828 | -57.1655 | 65.7028 | -0.11398 | 0.00019446 | 0.064803 | 0.075881 | 0.00016017 | 0.0030463 | 0.0069172 | 0.029175 | 0.0023839 | 0.00021363 | 0.005614 | -0.0017197 | -0.0040845 | -0.0036059 | -54.8218 | 65.6525 | -57.2571 | 65.419 | -56.0715 | -56.9 | -55.9982 | -56.1081 | 65.7211 | -57.193 | -57.1381 | -57.1609 | -57.3029 | -56.9733 | -0.091553 | -0.050354 | -0.28381 | 1.0941 | 1.1673 | 0.2655 | 1.2589 | 0.35706 | -0.027466 | 0.01831 | -122.8409 | 0.004577 | 0.19226 | -0.13733 | 0.21973 | -0.10986 | 1.1856 | 122.6761 | 0.032043 | 0.054931 | 122.9095 | 122.9141 | 122.818 | 122.8867 | -122.9599 | -122.8958 | 122.5845 | 0.027465 | 2.3438 | 1.0574
1310.1719 | 122.9416 | -57.1793 | 65.6982 | -0.068207 | 0.0012625 | 0.063734 | 0.073958 | 0.0012284 | 0.0013373 | 0.0081988 | -0.025757 | -0.0014613 | 0.0023498 | -0.002931 | -0.0017197 | -0.00088008 | -0.0018971 | -54.7211 | 65.6891 | -57.2205 | 65.4556 | -56.1401 | -56.9046 | -55.9799 | -56.1172 | 65.7211 | -57.1976 | -57.1609 | -57.1976 | -57.3303 | -57.0007 | -0.041199 | -0.009155 | -0.24261 | 1.0391 | 1.1993 | 0.27466 | 1.2405 | 0.31586 | -0.018311 | 0.022888 | -122.8592 | -0.018311 | 0.17853 | -0.15106 | 0.19684 | -0.13275 | 1.0803 | 122.6761 | 0 | 0.036621 | 122.9095 | 122.9187 | 122.8683 | 122.9004 | -122.9187 | -122.8958 | 122.6349 | 0.01831 | 2.4582 | 1.062
1311.1719 | 123.0606 | -57.1335 | 65.6937 | -0.1445 | -0.00066014 | 0.06288 | 0.073958 | -0.0028304 | 0.0051825 | 0.0090534 | 0.093262 | -0.00060665 | 0.0021362 | -0.0048536 | -0.0012925 | -0.00088008 | -0.00040166 | -54.7211 | 65.6891 | -57.1793 | 65.5197 | -56.044 | -56.7535 | -55.8563 | -55.9982 | 65.6982 | -57.1701 | -57.0694 | -57.0602 | -57.1793 | -56.8817 | -0.045776 | -0.004578 | -0.17395 | 1.0895 | 1.2772 | 0.37994 | 1.3229 | 0.42572 | -0.036621 | 0.004577 | -122.7631 | 0.073242 | 0.25177 | -0.045776 | 0.28839 | -0.009155 | 1.1353 | 122.699 | 0.10986 | 0.10071 | 122.8683 | 122.8683 | 122.8226 | 122.8317 | -122.8729 | -122.8638 | 122.6532 | 0.064087 | 2.4124 | 1.1353
1312.75 | 123.0423 | -57.1747 | 65.7028 | -0.13687 | 0.00083526 | 0.065443 | 0.076308 | -0.00069423 | 0.0021917 | 0.0086262 | -0.01355 | 0.00067495 | 0.0019226 | 0.00091422 | -0.0015061 | -0.0015211 | -0.0014697 | -54.7302 | 65.6708 | -57.225 | 65.4648 | -56.1127 | -56.8771 | -55.9662 | -56.0349 | 65.6845 | -57.1609 | -57.0923 | -57.1198 | -57.2525 | -56.9412 | -0.050354 | -0.032044 | -0.23804 | 1.062 | 1.2085 | 0.29755 | 1.2589 | 0.3479 | 0.013733 | -0.018311 | -122.7951 | 0.054932 | 0.23346 | -0.077819 | 0.21973 | -0.091552 | 1.1124 | 122.6898 | 0.041199 | 0.068665 | 122.8958 | 122.8455 | 122.8455 | 122.8592 | -122.9279 | -122.8638 | 122.6395 | 0.082398 | 2.4445 | 1.1398
1313.5625 | 123.0835 | -57.1335 | 65.7349 | -0.052948 | 0.00019446 | 0.064589 | 0.075454 | 0.00037377 | 0.0021917 | 0.01119 | 0.047485 | -0.00060665 | 0.0012818 | 0.0043322 | -0.0012925 | -0.0038709 | -0.0033923 | -54.6524 | 65.6662 | -57.1838 | 65.593 | -55.9433 | -56.7215 | -55.838 | -55.8975 | 65.7257 | -57.1243 | -57.0374 | -57.0145 | -57.1335 | -56.8542 | -0.050354 | -0.068664 | -0.14191 | 1.1902 | 1.2955 | 0.41199 | 1.3458 | 0.46234 | 0.009155 | -0.009155 | -122.7722 | 0.11902 | 0.27924 | 0 | 0.27008 | -0.009155 | 1.2405 | 122.7768 | 0.10986 | 0.086975 | 122.85 | 122.85 | 122.7997 | 122.8592 | -122.9187 | -122.8592 | 122.7264 | 0.09613 | 2.4811 | 1.236
1314.9531 | 123.0057 | -57.1198 | 65.7303 | -0.052948 | 0.00019446 | 0.063521 | 0.076949 | -0.0011214 | 0.0013373 | 0.011617 | -0.037964 | -0.00017945 | -0.00064077 | 0.00048702 | -0.00065151 | -0.0015211 | 0.0021619 | -54.6616 | 65.7028 | -57.1884 | 65.5334 | -56.0486 | -56.8039 | -55.9067 | -55.957 | 65.744 | -57.1564 | -57.0877 | -57.1014 | -57.2113 | -56.9275 | -0.068665 | -0.027466 | -0.19684 | 1.0712 | 1.2131 | 0.31586 | 1.2817 | 0.38452 | -0.036621 | 0.013733 | -122.818 | 0.018311 | 0.19226 | -0.091553 | 0.22888 | -0.054932 | 1.1398 | 122.7219 | 0.054932 | 0.068664 | 122.8912 | 122.9004 | 122.8226 | 122.8638 | -122.9187 | -122.8867 | 122.6532 | 0.032043 | 2.4582 | 1.1627
1316 | 123.1018 | -57.1014 | 65.7074 | -0.045319 | 0.00062166 | 0.063734 | 0.07289 | -0.001976 | 0.0034735 | 0.0079852 | 0.081055 | 0.00024775 | 0.00064083 | -0.002931 | -0.0015061 | -0.0021619 | 0.0010937 | -54.7028 | 65.6754 | -57.193 | 65.5655 | -56.0074 | -56.7673 | -55.8472 | -55.9525 | 65.6982 | -57.1747 | -57.0328 | -57.0465 | -57.1472 | -56.8634 | -0.091553 | -0.032043 | -0.14191 | 1.0941 | 1.2543 | 0.33417 | 1.3458 | 0.42572 | -0.073243 | -0.009155 | -122.7402 | 0.054931 | 0.23804 | -0.045777 | 0.31128 | 0.027466 | 1.1856 | 122.7585 | 0.12817 | 0.14191 | 122.8683 | 122.8729 | 122.7768 | 122.7997 | -122.9004 | -122.8821 | 122.6669 | 0.068664 | 2.3987 | 1.149
1317.6562 | 123.0469 | -57.1518 | 65.6799 | -0.16739 | 0.00019446 | 0.062453 | 0.074172 | -0.0013352 | 0.0053961 | 0.0049946 | 0.044434 | 0.0013159 | 0.00021363 | 0.0032642 | -0.0034287 | -0.0021619 | 0.00088014 | -54.6982 | 65.6616 | -57.1976 | 65.538 | -55.9982 | -56.7947 | -55.9067 | -55.9433 | 65.657 | -57.1701 | -57.0602 | -57.0969 | -57.2159 | -56.9229 | -0.045777 | -0.018311 | -0.14191 | 1.1536 | 1.2451 | 0.35706 | 1.2909 | 0.40283 | -0.018311 | -0.022889 | -122.7402 | 0.054931 | 0.22888 | -0.064087 | 0.24719 | -0.045776 | 1.1993 | 122.7356 | 0.073242 | 0.10986 | 122.8592 | 122.8271 | 122.8134 | 122.8088 | -122.8775 | -122.85 | 122.6898 | 0.091552 | 2.4536 | 1.2085
1318.4062 | 122.9553 | -57.1701 | 65.7303 | -0.037689 | 0.00040806 | 0.063734 | 0.076949 | 0.0016556 | 0.0047553 | 0.01119 | -0.041016 | 0.0013159 | 0.00085443 | 0.0041186 | -0.0012925 | -0.0021619 | 0.00088014 | -54.7302 | 65.7074 | -57.2067 | 65.4694 | -56.131 | -56.8771 | -55.9662 | -56.0852 | 65.7486 | -57.1747 | -57.1381 | -57.193 | -57.3395 | -57.0007 | -0.036621 | -0.022889 | -0.26093 | 1.0391 | 1.2039 | 0.29297 | 1.2405 | 0.32959 | -0.004578 | 0.01831 | -122.8683 | -0.022888 | 0.16937 | -0.16937 | 0.17395 | -0.16479 | 1.0757 | 122.6761 | -0.01831 | 0.036621 | 122.9141 | 122.9233 | 122.8775 | 122.9187 | -122.937 | -122.905 | 122.6395 | 0.032043 | 2.4399 | 1.0849
1320.6094 | 122.9782 | -57.1793 | 65.6937 | -0.083466 | 0.0010489 | 0.063948 | 0.07759 | 0.0027238 | 0.0041143 | 0.0077716 | -0.041016 | 0.0015295 | -0.00064077 | 0.0049732 | -0.00022431 | -0.0030163 | 0.00066654 | -54.744 | 65.6754 | -57.2388 | 65.4694 | -56.1264 | -56.8771 | -55.9845 | -56.0944 | 65.744 | -57.2067 | -57.1472 | -57.1976 | -57.3349 | -56.987 | -0.05951 | -0.018311 | -0.22431 | 1.0529 | 1.1948 | 0.30212 | 1.2543 | 0.36163 | -0.027466 | 0.050354 | -122.8409 | -0.018311 | 0.19226 | -0.15564 | 0.21973 | -0.12817 | 1.1124 | 122.7081 | 0.009155 | 0.059509 | 122.9141 | 122.9507 | 122.8546 | 122.9233 | -122.9324 | -122.9004 | 122.6486 | 0.032043 | 2.4353 | 1.0849
1323.5781 | 123.143 | -57.1701 | 65.6937 | -0.098725 | -0.00044654 | 0.063734 | 0.073745 | 0.004219 | 0.0041143 | 0.0067036 | 0.010864 | -0.00082025 | 0.0012818 | 0.002196 | -0.0025741 | -0.0040845 | -0.0021107 | -54.6936 | 65.6342 | -57.2159 | 65.5426 | -56.0257 | -56.7902 | -55.8838 | -55.9525 | 65.6708 | -57.1609 | -57.0465 | -57.1381 | -57.4219 | -56.9092 | -0.045776 | -0.05951 | -0.15106 | 1.1444 | 1.2863 | 0.37994 | 1.3321 | 0.42572 | 0.009155 | -0.022889 | -122.7402 | 0.032043 | 0.26093 | -0.25177 | 0.25177 | -0.26093 | 1.1902 | 122.7585 | 0.022888 | 0.11444 | 122.85 | 122.8317 | 122.8043 | 122.8409 | -122.9095 | -122.8546 | 122.7127 | 0.1236 | 2.4765 | 1.2177
1324.1719 | 123.0011 | -57.1655 | 65.7303 | -0.091095 | -0.00087374 | 0.06288 | 0.076949 | -0.0043258 | 0.0026191 | 0.009267 | -0.056274 | -0.0023157 | 2.8e-08 | 0.0047594 | -0.0015061 | -0.0023755 | -0.0016833 | -54.7394 | 65.6799 | -57.2296 | 65.4785 | -56.0898 | -56.8451 | -55.9479 | -56.0303 | 65.7669 | -57.2021 | -57.1335 | -57.1655 | -57.3074 | -56.9641 | -0.064087 | -0.050354 | -0.25177 | 1.0757 | 1.2177 | 0.32043 | 1.2817 | 0.38452 | -0.036621 | 0.036621 | -122.8638 | 0 | 0.20142 | -0.14191 | 0.23804 | -0.10529 | 1.1398 | 122.7081 | 0.036621 | 0.068664 | 122.9095 | 122.9691 | 122.8455 | 122.9324 | -122.9599 | -122.9324 | 122.644 | 0.032043 | 2.4261 | 1.1353
1325.1719 | 123.0194 | -57.1335 | 65.7028 | -0.060578 | 0.0027579 | 0.063521 | 0.075027 | -5.343e-05 | 0.0015509 | 0.0086262 | -0.01355 | 3.4148e-05 | 0.001709 | -0.00058098 | -0.00065151 | -0.0036573 | 0.00088014 | -54.7165 | 65.6891 | -57.2342 | 65.5518 | -56.2363 | -56.8863 | -55.8838 | -55.9662 | 65.7303 | -57.1518 | -57.0969 | -57.1243 | -57.2525 | -56.9366 | -0.10071 | -0.013733 | -0.15106 | 0.89722 | 1.2497 | 0.24719 | 1.3504 | 0.3479 | -0.01831 | 0.027466 | -122.7997 | 0.009155 | 0.19684 | -0.11902 | 0.21515 | -0.10071 | 0.99793 | 122.786 | 0.027465 | 0.054931 | 122.9233 | 122.8821 | 122.8226 | 122.8638 | -122.937 | -122.8546 | 122.6852 | 0.036621 | 2.417 | 1.1673
1326.1719 | 122.9736 | -57.1426 | 65.7303 | -0.060578 | 0.00083526 | 0.064375 | 0.074813 | -0.0032578 | 0.0028327 | 0.010335 | -0.041016 | 0.00067495 | 0.001068 | 0.0030506 | -0.0015061 | -0.0019483 | 0.0042981 | -54.7256 | 65.6937 | -57.2205 | 65.4831 | -56.0669 | -56.8314 | -55.957 | -56.0257 | 65.7349 | -57.1884 | -57.1243 | -57.1472 | -57.2937 | -56.9641 | -0.07782 | -0.036621 | -0.24719 | 1.0757 | 1.1856 | 0.31128 | 1.2634 | 0.3891 | -0.045777 | 0.004577 | -122.8546 | -0.004578 | 0.17853 | -0.15106 | 0.2243 | -0.10529 | 1.1536 | 122.7036 | 0.041199 | 0.064087 | 122.9141 | 122.9233 | 122.8363 | 122.8775 | -122.9507 | -122.9187 | 122.6257 | 0.01831 | 2.417 | 1.1169
1327.1719 | 123.0103 | -57.1609 | 65.7028 | -0.060578 | -0.00023294 | 0.064375 | 0.078017 | -0.0030442 | 0.0021917 | 0.0077716 | -0.03186 | 0.0017431 | 0.003418 | 0.001128 | 0.00020289 | -0.00088008 | -0.0042469 | -54.7531 | 65.6845 | -57.2159 | 65.4922 | -56.0898 | -56.8405 | -55.9387 | -56.0165 | 65.7303 | -57.1976 | -57.1198 | -57.1701 | -57.2983 | -56.9595 | -0.054931 | -0.018311 | -0.21057 | 1.0712 | 1.2222 | 0.32043 | 1.2772 | 0.37537 | -0.036621 | 0.027466 | -122.8226 | -0.009155 | 0.20142 | -0.13733 | 0.23804 | -0.10071 | 1.1261 | 122.7081 | 0.027466 | 0.07782 | 122.9004 | 122.9279 | 122.8455 | 122.8912 | -122.9187 | -122.9004 | 122.6532 | 0.041199 | 2.4078 | 1.1444
1328.1719 | 122.9782 | -57.1655 | 65.6891 | 0.015716 | 0.00083526 | 0.063734 | 0.074599 | 0.0040054 | 0.0032599 | 0.0077716 | -0.041016 | 0.0013159 | 0.0025634 | 0.001128 | -0.00086511 | -0.0010937 | -0.00061526 | -54.7531 | 65.7074 | -57.2296 | 65.5014 | -56.0669 | -56.8314 | -55.9296 | -56.012 | 65.7028 | -57.1655 | -57.1243 | -57.1472 | -57.3029 | -56.9641 | -0.064087 | 0.01831 | -0.18768 | 1.0986 | 1.236 | 0.33417 | 1.3 | 0.39825 | 0 | 0.013733 | -122.8134 | 0.01831 | 0.20142 | -0.13733 | 0.20142 | -0.13733 | 1.1627 | 122.731 | 0.01831 | 0.041198 | 122.937 | 122.8683 | 122.8729 | 122.8683 | -122.9187 | -122.8546 | 122.6669 | 0.041198 | 2.4124 | 1.1536
1329.1719 | 122.9828 | -57.1747 | 65.7028 | -0.052948 | -0.0017281 | 0.063307 | 0.076095 | 0.001442 | 0.0028327 | 0.0086262 | -0.019653 | 0.0021703 | 0.0014954 | -0.00036738 | -0.00086511 | -0.0025891 | 0.0017345 | -54.7714 | 65.6845 | -57.2525 | 65.451 | -56.1264 | -56.8817 | -55.9616 | -56.0898 | 65.7303 | -57.2205 | -57.1609 | -57.1976 | -57.3257 | -56.9916 | -0.077819 | -0.018311 | -0.25177 | 1.0483 | 1.2131 | 0.29297 | 1.2909 | 0.37079 | -0.045776 | 0.027466 | -122.8638 | -0.022888 | 0.18311 | -0.15106 | 0.22888 | -0.10529 | 1.1261 | 122.7036 | 0.022888 | 0.059509 | 122.937 | 122.9507 | 122.8592 | 122.905 | -122.9553 | -122.9233 | 122.6257 | 0.013733 | 2.4033 | 1.0849
1330.1719 | 122.9553 | -57.1793 | 65.712 | -0.052948 | 0.0010489 | 0.064589 | 0.076522 | -0.0017624 | 0.0047553 | 0.009267 | -0.016602 | 0.0013159 | 0.001068 | -0.0020764 | -0.0012925 | -0.0038709 | -0.0044605 | -54.776 | 65.6937 | -57.2159 | 65.4648 | -56.0989 | -56.868 | -55.9616 | -56.0623 | 65.6937 | -57.1976 | -57.1609 | -57.1701 | -57.3257 | -56.9733 | -0.036621 | -0.01831 | -0.24719 | 1.0803 | 1.2177 | 0.31128 | 1.2543 | 0.3479 | -0.018311 | -0.01831 | -122.8729 | 0.009155 | 0.20599 | -0.14648 | 0.2243 | -0.12817 | 1.1169 | 122.6807 | 0.027466 | 0.036621 | 122.9095 | 122.8912 | 122.8729 | 122.8729 | -122.9279 | -122.9095 | 122.644 | 0.01831 | 2.4033 | 1.1169
1331.1719 | 123.0286 | -57.1609 | 65.7074 | -0.091095 | -0.00087374 | 0.065016 | 0.073531 | -0.0026168 | 0.0039007 | 0.0094806 | -0.037964 | -0.00082025 | 0.0025634 | 0.0068958 | -0.0019333 | -0.0021619 | 0.00023934 | -54.8218 | 65.6525 | -57.2525 | 65.4877 | -56.0669 | -56.7993 | -55.9067 | -55.9937 | 65.7303 | -57.1701 | -57.1106 | -57.1335 | -57.2525 | -56.9366 | -0.091552 | -0.054931 | -0.21973 | 1.0941 | 1.2543 | 0.36163 | 1.3458 | 0.45319 | -0.009155 | 0.022889 | -122.818 | 0.027466 | 0.2243 | -0.091552 | 0.23346 | -0.082397 | 1.1856 | 122.7402 | 0.036621 | 0.059509 | 122.905 | 122.9004 | 122.8134 | 122.8912 | -122.9599 | -122.8775 | 122.6486 | 0.050354 | 2.3392 | 1.1673
1332.1719 | 122.9828 | -57.1747 | 65.7166 | -0.075836 | 0.00040806 | 0.064162 | 0.075881 | 0.0012284 | 0.0049689 | 0.0071308 | -0.03186 | 0.00046135 | 0.0025634 | 0.0032642 | -0.00022431 | -0.0023755 | 0.0017345 | -54.7668 | 65.6845 | -57.2205 | 65.4739 | -56.0989 | -56.8588 | -55.9479 | -56.0486 | 65.7349 | -57.193 | -57.1518 | -57.1747 | -57.3074 | -56.9733 | -0.045776 | -0.032044 | -0.24262 | 1.0757 | 1.2268 | 0.31586 | 1.2726 | 0.36163 | -0.01831 | 0.01831 | -122.8683 | 0 | 0.20142 | -0.13275 | 0.21973 | -0.11444 | 1.1215 | 122.6944 | 0.01831 | 0.041199 | 122.905 | 122.9279 | 122.8592 | 122.9095 | -122.937 | -122.9095 | 122.6486 | 0.022889 | 2.4078 | 1.1261
1333.1719 | 122.9507 | -57.1838 | 65.712 | -0.091095 | 0.0016899 | 0.062453 | 0.073745 | 0.0035782 | 0.0021917 | 0.0073444 | -0.037964 | 0.00024775 | -0.00042717 | -0.0048536 | -0.0010787 | -0.0030163 | 0.0028027 | -54.7989 | 65.6799 | -57.2525 | 65.4282 | -56.1768 | -56.9366 | -55.9937 | -56.1172 | 65.7166 | -57.2296 | -57.1884 | -57.2159 | -57.3441 | -57.0099 | -0.068664 | -0.032043 | -0.28381 | 1.0071 | 1.1902 | 0.24719 | 1.2589 | 0.31586 | -0.045776 | 0.004578 | -122.9004 | -0.032043 | 0.17395 | -0.16022 | 0.21973 | -0.11444 | 1.0757 | 122.6807 | 0.013733 | 0.041198 | 122.9324 | 122.9462 | 122.8638 | 122.9004 | -122.9645 | -122.9416 | 122.612 | -0.004578 | 2.3849 | 1.0666
1334.1719 | 122.9782 | -57.2021 | 65.7074 | -0.045319 | -0.00087374 | 0.063948 | 0.07289 | 0.003151 | 0.0053961 | 0.0081988 | 0.0047608 | 0.0015295 | -0.00021357 | -0.0044262 | -0.0034287 | 0.00040152 | 0.0072887 | -54.7852 | 65.6845 | -57.2662 | 65.4465 | -56.1447 | -56.8909 | -55.9708 | -56.1127 | 65.712 | -57.2067 | -57.1564 | -57.2205 | -57.3578 | -57.0007 | -0.064087 | -0.022888 | -0.26093 | 1.0574 | 1.2314 | 0.31128 | 1.2955 | 0.37537 | -0.004578 | 0.004578 | -122.8638 | -0.018311 | 0.20142 | -0.15564 | 0.20599 | -0.15106 | 1.1215 | 122.7127 | -0.013733 | 0.050354 | 122.9507 | 122.9187 | 122.8867 | 122.9141 | -122.9736 | -122.9141 | 122.6486 | 0.045776 | 2.417 | 1.0895
1335.1719 | 122.9828 | -57.1472 | 65.7028 | -0.060578 | 0.0014761 | 0.064589 | 0.074599 | 0.0018692 | 0.0032599 | 0.0064898 | -0.0074462 | 0.0011023 | -0.00021357 | 0.0071094 | -0.00022431 | -0.0032301 | 0.0019483 | -54.7577 | 65.6662 | -57.2296 | 65.4831 | -56.0669 | -56.8314 | -55.9158 | -56.0028 | 65.7166 | -57.1976 | -57.1243 | -57.1564 | -57.2845 | -56.9733 | -0.082397 | -0.036621 | -0.21973 | 1.0803 | 1.2314 | 0.31586 | 1.3138 | 0.39825 | -0.050354 | 0.013733 | -122.8271 | -0.009155 | 0.17395 | -0.13733 | 0.2243 | -0.086975 | 1.1627 | 122.7127 | 0.041199 | 0.073242 | 122.8958 | 122.9141 | 122.8134 | 122.8638 | -122.9324 | -122.9004 | 122.6303 | 0.022888 | 2.3895 | 1.1444
1336.1719 | 122.9874 | -57.1609 | 65.7166 | -0.19791 | -0.00044654 | 0.064162 | 0.074386 | 0.00058737 | 0.0028327 | 0.007558 | -0.010498 | -0.00017945 | 0.001709 | -0.001222 | 0.00084389 | -0.0015211 | 0.00066654 | -54.689 | 65.6891 | -57.2342 | 65.4922 | -56.0669 | -56.8268 | -55.9433 | -56.0028 | 65.7303 | -57.1976 | -57.1243 | -57.1472 | -57.2708 | -56.9504 | -0.073242 | -0.027466 | -0.2243 | 1.0941 | 1.2177 | 0.33417 | 1.2909 | 0.40741 | -0.036621 | 0.013733 | -122.8409 | 0.013733 | 0.21057 | -0.10986 | 0.24719 | -0.073242 | 1.1673 | 122.7264 | 0.050354 | 0.073242 | 122.9233 | 122.9279 | 122.85 | 122.8912 | -122.9507 | -122.9141 | 122.6532 | 0.036621 | 2.4719 | 1.1581
1337.1719 | 122.9599 | -57.2113 | 65.712 | -0.10635 | 0.0021171 | 0.065016 | 0.076736 | 0.0016556 | 0.0049689 | 0.009267 | -0.0074462 | 0.0021703 | -0.00021357 | 0.003905 | -1.0706e-05 | -0.0021619 | 0.00045294 | -54.8172 | 65.6662 | -57.2479 | 65.4007 | -56.1951 | -56.9138 | -56.0074 | -56.1493 | 65.6799 | -57.2388 | -57.1701 | -57.2021 | -57.3532 | -57.0007 | -0.036621 | -0.045776 | -0.31128 | 1.0162 | 1.2039 | 0.29755 | 1.2405 | 0.33417 | -0.027466 | -0.032043 | -122.8821 | 0.009156 | 0.21057 | -0.14191 | 0.23804 | -0.11444 | 1.0529 | 122.6486 | 0.036622 | 0.068665 | 122.9141 | 122.9187 | 122.8775 | 122.8912 | -122.9599 | -122.9507 | 122.612 | 0.041199 | 2.3941 | 1.062
1338.1719 | 123.0331 | -57.1426 | 65.712 | -0.052948 | -0.00023294 | 0.061812 | 0.075881 | -0.0021896 | 0.0041143 | 0.0099078 | 0.029175 | 0.0013159 | 0.00085443 | 0.0024096 | -0.0030013 | -0.0017347 | 0.00088014 | -54.7577 | 65.7028 | -57.2159 | 65.5014 | -56.0486 | -57.0511 | -55.9616 | -55.9845 | 65.7303 | -57.2067 | -57.106 | -57.1426 | -57.2388 | -56.9366 | -0.073242 | -0.009155 | -0.21057 | 1.0941 | 1.181 | 0.091553 | 1.2543 | 0.1648 | -0.064087 | 0.018311 | -122.818 | 0 | 0.20599 | -0.096131 | 0.27008 | -0.032044 | 1.1673 | 122.7173 | 0.064087 | 0.10071 | 122.9187 | 122.937 | 122.8455 | 122.8729 | -122.9279 | -122.9187 | 122.644 | 0.036621 | 2.3849 | 1.1581
1339.1719 | 123.0011 | -57.1838 | 65.6937 | -0.11398 | 0.0029715 | 0.064589 | 0.074599 | 0.00037377 | 0.0015509 | 0.0099078 | -0.016602 | 0.0015295 | 0.00021363 | -0.0025036 | -0.00043791 | -0.0013073 | 0.00023934 | -54.7806 | 65.6799 | -57.2388 | 65.4922 | -56.0898 | -56.8451 | -55.9525 | -56.0394 | 65.7257 | -57.1793 | -57.1426 | -57.1701 | -57.2937 | -56.9687 | -0.054932 | -0.013733 | -0.20142 | 1.0941 | 1.2314 | 0.33875 | 1.2863 | 0.39368 | 0.004578 | 0.032043 | -122.8363 | 0.013733 | 0.21515 | -0.10986 | 0.21057 | -0.11444 | 1.149 | 122.731 | 0.009155 | 0.036621 | 122.9187 | 122.905 | 122.8638 | 122.9095 | -122.9324 | -122.8729 | 122.6761 | 0.041199 | 2.4033 | 1.1444
1340.1719 | 122.9553 | -57.1747 | 65.7074 | -0.075836 | 0.0010489 | 0.064589 | 0.076308 | 0.0016556 | 0.0034735 | 0.0084124 | -0.019653 | 0.0011023 | 0.0012818 | 0.0019824 | -0.00043791 | -0.00088008 | 0.0010937 | -54.8126 | 65.6799 | -57.2342 | 65.4236 | -56.1401 | -56.8863 | -55.9479 | -56.0898 | 65.7074 | -57.2067 | -57.1793 | -57.2159 | -57.3486 | -57.0099 | -0.059509 | -0.027465 | -0.28381 | 1.0345 | 1.2268 | 0.28839 | 1.2863 | 0.3479 | -0.032043 | 0 | -122.8867 | -0.041198 | 0.1648 | -0.17395 | 0.19684 | -0.14191 | 1.0941 | 122.6578 | -0.009155 | 0.027466 | 122.9141 | 122.9141 | 122.8546 | 122.8821 | -122.9416 | -122.9141 | 122.5983 | -0.004577 | 2.3621 | 1.0849
1341.1719 | 122.9782 | -57.1793 | 65.7028 | -0.060578 | 0.00019446 | 0.063948 | 0.076522 | 0.00016017 | 0.0032599 | 0.0073444 | -0.019653 | 0.0032385 | 0.0014954 | 0.0019824 | -0.0010787 | -0.0023755 | 2.554e-05 | -54.7897 | 65.6937 | -57.2296 | 65.4556 | -56.1218 | -56.868 | -55.9479 | -56.0761 | 65.7166 | -57.2067 | -57.1655 | -57.1976 | -57.3074 | -57.0007 | -0.050354 | -0.009155 | -0.24719 | 1.0574 | 1.2314 | 0.31128 | 1.2817 | 0.36163 | -0.027466 | 0.013733 | -122.8683 | -0.018311 | 0.17853 | -0.12817 | 0.20599 | -0.10071 | 1.1078 | 122.6852 | 0.009155 | 0.041199 | 122.9233 | 122.9233 | 122.8729 | 122.8958 | -122.9324 | -122.9095 | 122.6349 | 0.013733 | 2.3895 | 1.1032
1342.1719 | 122.9965 | -57.1564 | 65.712 | -0.075836 | 0.0010489 | 0.067366 | 0.075027 | -0.0013352 | 0.0051825 | 0.0086262 | 0.0078126 | 0.00067495 | 0.0025634 | 0.0062548 | -0.0015061 | -0.00045288 | 0.00088014 | -54.7485 | 65.6754 | -57.225 | 65.4419 | -56.1859 | -56.8359 | -55.8701 | -55.9937 | 65.7303 | -57.1884 | -57.0877 | -57.1335 | -57.2708 | -56.9412 | -0.068665 | -0.036621 | -0.27008 | 0.97046 | 1.2863 | 0.32043 | 1.355 | 0.3891 | -0.032044 | 0.018311 | -122.7997 | 0.022888 | 0.21515 | -0.11444 | 0.24719 | -0.082397 | 1.0391 | 122.6669 | 0.054932 | 0.10071 | 122.9004 | 122.9187 | 122.8317 | 122.8867 | -122.937 | -122.9004 | 122.5983 | 0.068664 | 2.4078 | 1.1627
1343.1719 | 123.056 | -57.1609 | 65.6937 | -0.060578 | 0.0010489 | 0.062453 | 0.077163 | 0.00058737 | 0.0021917 | 0.0088398 | 0.0047608 | 0.0011023 | -0.00064077 | -0.0037854 | 0.00063009 | -0.0049389 | 0.0025891 | -54.7668 | 65.6982 | -57.225 | 65.4922 | -56.0669 | -56.8176 | -55.9113 | -55.9982 | 65.6982 | -57.1838 | -57.0831 | -57.106 | -57.2296 | -56.9183 | -0.064087 | 0.004577 | -0.20142 | 1.0941 | 1.2497 | 0.34332 | 1.3138 | 0.40741 | -0.022888 | 0.004577 | -122.7768 | 0.054932 | 0.24262 | -0.068664 | 0.2655 | -0.045776 | 1.1581 | 122.7173 | 0.07782 | 0.10071 | 122.9233 | 122.8821 | 122.8592 | 122.8592 | -122.9187 | -122.8775 | 122.6532 | 0.07782 | 2.3941 | 1.1627
1344.1719 | 122.9965 | -57.1884 | 65.6891 | -0.098725 | 0.00083526 | 0.064589 | 0.076736 | 0.0022964 | 0.0049689 | 0.0071308 | -0.0013428 | 0.0030249 | 0.003418 | 0.0024096 | -0.0019333 | -0.0019483 | -0.00040166 | -54.8035 | 65.6799 | -57.2342 | 65.4465 | -56.1356 | -56.8634 | -55.9799 | -56.0898 | 65.7166 | -57.1976 | -57.1426 | -57.2159 | -57.3257 | -56.9916 | -0.045776 | -0.009155 | -0.24262 | 1.0529 | 1.2085 | 0.32501 | 1.2543 | 0.37079 | -0.009155 | 0.027466 | -122.8317 | -0.027465 | 0.19684 | -0.13733 | 0.20599 | -0.12817 | 1.0986 | 122.6807 | -0.01831 | 0.054932 | 122.9141 | 122.9141 | 122.8683 | 122.905 | -122.9233 | -122.8867 | 122.6349 | 0.045777 | 2.3849 | 1.0986
1345.1719 | 123.0148 | -57.1472 | 65.6845 | -0.052948 | -0.0010873 | 0.063094 | 0.074172 | -0.0021896 | 0.0030463 | 0.010121 | -0.019653 | 0.0015295 | 0.0019226 | 0.0017688 | -0.0010787 | -0.0030163 | -0.00061526 | -54.7668 | 65.6799 | -57.2205 | 65.5106 | -56.0669 | -56.8085 | -55.9021 | -56.012 | 65.712 | -57.193 | -57.1106 | -57.1289 | -57.2479 | -56.9412 | -0.073242 | -0.004577 | -0.17395 | 1.0803 | 1.2451 | 0.33874 | 1.3184 | 0.41199 | -0.045776 | 0.027466 | -122.7951 | 0.018311 | 0.20599 | -0.10071 | 0.25177 | -0.054932 | 1.1536 | 122.731 | 0.064087 | 0.082397 | 122.9004 | 122.905 | 122.8271 | 122.8592 | -122.905 | -122.8775 | 122.6578 | 0.036621 | 2.3804 | 1.1353
1346.1719 | 123.0377 | -57.1701 | 65.6982 | -0.12924 | -0.00044654 | 0.065016 | 0.077804 | 0.0022964 | 0.0039007 | 0.0094806 | 0.023071 | 0.0023839 | -0.00085457 | -0.0031446 | -0.0017197 | -0.0036573 | -0.0010425 | -54.7852 | 65.6662 | -57.225 | 65.4968 | -56.0577 | -56.8085 | -55.925 | -56.0165 | 65.7074 | -57.193 | -57.0923 | -57.1152 | -57.2388 | -56.955 | -0.054932 | -0.032043 | -0.20142 | 1.1124 | 1.2451 | 0.36163 | 1.3 | 0.41656 | -0.022888 | 0.009155 | -122.7905 | 0.054932 | 0.21515 | -0.068665 | 0.23804 | -0.045777 | 1.1673 | 122.7219 | 0.07782 | 0.10071 | 122.8912 | 122.9004 | 122.8363 | 122.8775 | -122.9233 | -122.8912 | 122.6669 | 0.07782 | 2.3849 | 1.1536
1347.1719 | 122.9828 | -57.1838 | 65.6708 | -0.091095 | 0.0012625 | 0.064375 | 0.076736 | 0.00016017 | 0.0034735 | 0.0099078 | -0.0074462 | 0.00088875 | 0.0014954 | -0.003999 | -0.0010787 | -0.0017347 | 0.00066654 | -54.808 | 65.6799 | -57.2571 | 65.4327 | -56.1401 | -56.8817 | -55.9799 | -56.0852 | 65.7211 | -57.2113 | -57.1747 | -57.193 | -57.3486 | -57.0007 | -0.073242 | 0.009156 | -0.23804 | 1.0437 | 1.2039 | 0.30212 | 1.2772 | 0.37537 | -0.027466 | 0.050354 | -122.8455 | -0.009155 | 0.18311 | -0.16479 | 0.21057 | -0.13733 | 1.1169 | 122.6898 | 0.018311 | 0.036621 | 122.937 | 122.9324 | 122.8638 | 122.905 | -122.9279 | -122.8821 | 122.6166 | 0.009155 | 2.3758 | 1.0986
1348.1719 | 123.0011 | -57.1655 | 65.7074 | -0.13687 | -0.00087374 | 0.06523 | 0.076308 | 0.0033646 | 0.0015509 | 0.01183 | 0.0078126 | 0.0015295 | 0.0021362 | 0.0045458 | -0.0015061 | -0.0013073 | 0.0013073 | -54.7623 | 65.6799 | -57.2205 | 65.4282 | -56.0028 | -56.7902 | -55.9158 | -56.0257 | 65.7028 | -57.193 | -57.1152 | -57.1655 | -57.2708 | -56.9595 | -0.054932 | -0.027465 | -0.27923 | 1.1627 | 1.2497 | 0.37537 | 1.3046 | 0.4303 | -0.027466 | -0.004577 | -122.8226 | 0 | 0.20599 | -0.10529 | 0.23346 | -0.07782 | 1.2177 | 122.6486 | 0.027466 | 0.07782 | 122.9004 | 122.8958 | 122.8455 | 122.8683 | -122.9279 | -122.9004 | 122.5937 | 0.050354 | 2.4033 | 1.1398
1349.1719 | 123.0103 | -57.1609 | 65.7303 | -0.091095 | 0.0019035 | 0.063948 | 0.076308 | -0.00048063 | 0.0045417 | 0.0081988 | -0.0013428 | 0.0021703 | 0.002777 | -0.003999 | -0.0023605 | -0.0017347 | 0.0021619 | -54.7714 | 65.7211 | -57.2205 | 65.4831 | -56.0806 | -56.8085 | -55.9067 | -56.0165 | 65.7257 | -57.1793 | -57.1014 | -57.1335 | -57.2617 | -56.9366 | -0.059509 | -0.009156 | -0.24719 | 1.0803 | 1.2543 | 0.35248 | 1.3138 | 0.41199 | -0.01831 | -0.004578 | -122.8317 | 0.027466 | 0.2243 | -0.10071 | 0.24261 | -0.082398 | 1.1398 | 122.7036 | 0.045776 | 0.07782 | 122.9416 | 122.905 | 122.8821 | 122.8867 | -122.9507 | -122.9095 | 122.644 | 0.05951 | 2.3895 | 1.1444
1350.1719 | 122.9462 | -57.2021 | 65.6937 | -0.060578 | -0.00087374 | 0.063521 | 0.076522 | 0.0016556 | 0.0030463 | 0.0081988 | 0.001709 | 0.0017431 | 0.0014954 | -0.0033582 | -0.0015061 | -0.0017347 | -0.00018806 | -54.7943 | 65.6662 | -57.2388 | 65.4465 | -56.1356 | -56.8817 | -55.9845 | -56.0623 | 65.712 | -57.225 | -57.1747 | -57.2021 | -57.3257 | -56.9962 | -0.036622 | -0.027466 | -0.24719 | 1.0666 | 1.2177 | 0.32043 | 1.2543 | 0.35706 | -0.022889 | 0.01831 | -122.8683 | 0 | 0.20599 | -0.1236 | 0.22888 | -0.10071 | 1.1032 | 122.6852 | 0.022889 | 0.050354 | 122.905 | 122.937 | 122.8683 | 122.9141 | -122.9324 | -122.9187 | 122.6486 | 0.027465 | 2.4078 | 1.1398
1351.1719 | 123.0286 | -57.1655 | 65.6937 | -0.045319 | -0.0021555 | 0.065657 | 0.074172 | 0.0035782 | 0.0024053 | 0.0071308 | 0.032227 | 0.0013159 | 0.001068 | 0.0028368 | -0.00022431 | -0.0034437 | -0.0010425 | -54.7577 | 65.7028 | -57.2296 | 65.4831 | -56.0806 | -56.8039 | -55.9067 | -55.9982 | 65.744 | -57.1884 | -57.1243 | -57.1152 | -57.2525 | -56.9229 | -0.064087 | 0.009155 | -0.21057 | 1.0849 | 1.2588 | 0.36163 | 1.3229 | 0.42572 | -0.022889 | 0.050354 | -122.818 | 0.050354 | 0.24261 | -0.086975 | 0.2655 | -0.064086 | 1.149 | 122.7127 | 0.073243 | 0.064087 | 122.9324 | 122.9324 | 122.8683 | 122.9095 | -122.9233 | -122.8821 | 122.6486 | 0.041198 | 2.4078 | 1.1673
1352.1719 | 122.9965 | -57.1472 | 65.7257 | 0.00045798 | 0.0010489 | 0.063094 | 0.076095 | -0.0015488 | 0.0049689 | 0.0073444 | 0.044434 | 0.0015295 | -0.00064077 | 0.0026232 | -1.0706e-05 | -0.0023755 | 0.00045294 | -54.8309 | 65.6754 | -57.2296 | 65.4648 | -56.1264 | -56.8268 | -55.9341 | -56.0669 | 65.7349 | -57.1838 | -57.1426 | -57.1609 | -57.2662 | -56.955 | -0.082397 | -0.050354 | -0.26093 | 1.0208 | 1.2131 | 0.32043 | 1.2955 | 0.40283 | -0.036621 | 0.009155 | -122.8683 | -0.013733 | 0.19226 | -0.11902 | 0.22888 | -0.082397 | 1.1032 | 122.6944 | 0.022888 | 0.041199 | 122.905 | 122.9187 | 122.8226 | 122.8821 | -122.9553 | -122.9095 | 122.612 | 0.004578 | 2.3163 | 1.0803
1353.1719 | 123.0194 | -57.1472 | 65.7349 | -0.014801 | -0.0013009 | 0.063307 | 0.078017 | 0.0018692 | 0.0024053 | 0.007558 | 0.029175 | 0.00067495 | 2.8e-08 | -0.00015378 | -0.0017197 | -0.0040845 | -0.0010425 | -54.7897 | 65.7074 | -57.225 | 65.4648 | -56.1127 | -56.8222 | -55.9204 | -56.0394 | 65.744 | -57.1976 | -57.1152 | -57.1106 | -57.2525 | -56.9412 | -0.07782 | -0.027466 | -0.27008 | 1.0345 | 1.2268 | 0.32501 | 1.3046 | 0.40283 | -0.050354 | 0.009156 | -122.85 | 0.036621 | 0.20599 | -0.10529 | 0.25635 | -0.054931 | 1.1124 | 122.6898 | 0.086975 | 0.082398 | 122.9324 | 122.9416 | 122.8546 | 122.8912 | -122.9599 | -122.9324 | 122.612 | 0.032044 | 2.3575 | 1.1078
1354.1719 | 123.0194 | -57.1655 | 65.7166 | -0.060578 | -1.9142e-05 | 0.063521 | 0.074599 | -5.343e-05 | 0.0043281 | 0.0099078 | 0.013916 | 0.0011023 | 0.0025634 | -0.0065626 | -0.00022431 | -0.0023755 | -0.00082886 | -54.8035 | 65.6937 | -57.2159 | 65.4465 | -56.1264 | -56.8359 | -55.9341 | -56.0715 | 65.7303 | -57.193 | -57.1198 | -57.1426 | -57.2617 | -56.9595 | -0.050354 | -0.022888 | -0.27008 | 1.0391 | 1.2314 | 0.32959 | 1.2817 | 0.37994 | -0.027466 | 0.013733 | -122.8363 | 0.022888 | 0.20599 | -0.096131 | 0.23346 | -0.068665 | 1.0895 | 122.6624 | 0.050354 | 0.073242 | 122.9095 | 122.9233 | 122.8592 | 122.8958 | -122.9324 | -122.9095 | 122.612 | 0.045776 | 2.3621 | 1.0941
1355.1719 | 122.9965 | -57.1472 | 65.7532 | -0.0071715 | -0.00044654 | 0.063948 | 0.076949 | 0.00058737 | 0.0028327 | 0.0077716 | 0.041382 | 0.0030249 | -0.00085457 | 0.003905 | -0.00022431 | -0.0028027 | 0.0019483 | -54.8447 | 65.6982 | -57.2205 | 65.4465 | -56.1401 | -56.8451 | -55.9433 | -56.0715 | 65.7394 | -57.2205 | -57.1472 | -57.1609 | -57.2845 | -56.9687 | -0.073242 | -0.054932 | -0.3067 | 1.0071 | 1.2039 | 0.30212 | 1.2772 | 0.37537 | -0.073242 | -0.013733 | -122.9004 | -0.013733 | 0.17853 | -0.13733 | 0.25177 | -0.064087 | 1.0803 | 122.6669 | 0.059509 | 0.073242 | 122.9187 | 122.9599 | 122.8455 | 122.8867 | -122.9736 | -122.9736 | 122.5937 | 0 | 2.3026 | 1.0757
1356.1719 | 122.9828 | -57.1701 | 65.744 | -0.045319 | 0.0014761 | 0.062666 | 0.075027 | 0.00080117 | 0.0043281 | 0.0096942 | 0.035278 | 0.0017431 | 0.0025634 | 0.0019824 | -0.0019333 | -0.0030163 | 0.00023934 | -54.8218 | 65.7211 | -57.2388 | 65.3641 | -56.0944 | -56.8588 | -55.9799 | -56.0669 | 65.7486 | -57.1838 | -57.1426 | -57.1564 | -57.2662 | -56.9687 | -0.068665 | -0.022889 | -0.37994 | 1.0757 | 1.1902 | 0.31128 | 1.2589 | 0.37994 | -0.013733 | 0.004577 | -122.8867 | 0.013733 | 0.20142 | -0.09613 | 0.21515 | -0.082397 | 1.1444 | 122.6028 | 0.027466 | 0.041199 | 122.9599 | 122.9324 | 122.8912 | 122.9187 | -122.9828 | -122.9279 | 122.5342 | 0.027466 | 2.3483 | 1.1032
1357.1719 | 123.024 | -57.1518 | 65.7028 | -0.12924 | -1.9142e-05 | 0.064375 | 0.075667 | 0.0022964 | 0.0024053 | 0.0096942 | 0.013916 | 0.0015295 | -0.0014954 | 0.002196 | -0.0015061 | -0.00088008 | -0.0053149 | -54.7668 | 65.7074 | -57.2021 | 65.4831 | -56.0806 | -56.8039 | -55.8884 | -56.0211 | 65.7211 | -57.1976 | -57.1243 | -57.1472 | -57.2845 | -56.9458 | -0.050354 | 0.004577 | -0.21973 | 1.0712 | 1.2634 | 0.3479 | 1.3138 | 0.39825 | -0.045777 | 0.01831 | -122.8271 | 0.004577 | 0.20599 | -0.13275 | 0.25177 | -0.086975 | 1.1215 | 122.6852 | 0.050354 | 0.073242 | 122.9095 | 122.9187 | 122.8592 | 122.8729 | -122.905 | -122.9004 | 122.6349 | 0.027465 | 2.3849 | 1.1307
1358.1719 | 123.0103 | -57.1701 | 65.7211 | -0.052948 | 0.0027579 | 0.064375 | 0.075454 | 0.00016017 | 0.0021917 | 0.0069172 | 0.013916 | -0.00082025 | -0.0021362 | -0.0086988 | 0.00041649 | -0.0017347 | 0.0034435 | -54.8492 | 65.6891 | -57.2525 | 65.451 | -56.1401 | -56.8497 | -55.9387 | -56.0532 | 65.7257 | -57.1884 | -57.1472 | -57.1426 | -57.28 | -56.9916 | -0.082397 | -0.032043 | -0.27008 | 1.03 | 1.2314 | 0.32043 | 1.3138 | 0.40283 | -0.018311 | 0.004578 | -122.8683 | 0.027466 | 0.17853 | -0.10986 | 0.19684 | -0.091552 | 1.1124 | 122.7036 | 0.045777 | 0.041199 | 122.9416 | 122.9141 | 122.8592 | 122.8958 | -122.9736 | -122.9095 | 122.6212 | 0.022888 | 2.3209 | 1.1169
1359.1719 | 122.9782 | -57.1564 | 65.7257 | -0.060578 | 0.0016899 | 0.063094 | 0.073745 | 0.00037377 | 0.0017645 | 0.010121 | 0.035278 | 0.00024775 | 0.001068 | 0.0045458 | -0.00022431 | -0.0038709 | -0.0023243 | -54.7852 | 65.7074 | -57.1976 | 65.4877 | -56.0852 | -56.8268 | -55.9296 | -56.0486 | 65.7303 | -57.193 | -57.1426 | -57.1609 | -57.2525 | -56.9733 | -0.041199 | -0.018311 | -0.23804 | 1.0712 | 1.2268 | 0.32959 | 1.268 | 0.37079 | -0.036621 | 0.004578 | -122.8683 | -0.004578 | 0.1831 | -0.09613 | 0.21973 | -0.059509 | 1.1124 | 122.6852 | 0.032043 | 0.050354 | 122.905 | 122.9233 | 122.8638 | 122.8867 | -122.9233 | -122.9187 | 122.644 | 0.013733 | 2.3712 | 1.1078
1360.1719 | 122.9828 | -57.1609 | 65.712 | -0.052948 | 0.00062166 | 0.061385 | 0.073531 | 0.003151 | 0.00091009 | 0.0090534 | 0.056641 | -0.00017945 | 0.0021362 | -0.0025036 | -0.0015061 | -0.0045117 | -0.0012561 | -54.7714 | 65.6708 | -57.2296 | 65.4968 | -56.0806 | -56.7902 | -55.8838 | -56.012 | 65.7166 | -57.1793 | -57.1701 | -57.1381 | -57.2296 | -56.9824 | -0.068664 | -0.041199 | -0.21515 | 1.0803 | 1.2772 | 0.37079 | 1.3458 | 0.43945 | -0.01831 | 0.004578 | -122.8821 | 0.022888 | 0.17853 | -0.068664 | 0.19684 | -0.050354 | 1.149 | 122.7264 | 0.041198 | 0.009155 | 122.9004 | 122.8958 | 122.8317 | 122.8775 | -122.9416 | -122.8912 | 122.6578 | -0.009155 | 2.3895 | 1.149
1361.1719 | 122.9233 | -57.1335 | 65.7166 | -0.045319 | 0.00083526 | 0.063948 | 0.076308 | 0.003151 | 0.0032599 | 0.0077716 | 0.041382 | 0.00046135 | -0.00085457 | -0.0061352 | 0.00020289 | -0.0023755 | 2.554e-05 | -54.8264 | 65.7166 | -57.2433 | 65.4694 | -56.1218 | -56.8314 | -55.9296 | -56.0486 | 65.7486 | -57.1884 | -57.1472 | -57.1014 | -57.0419 | -56.9595 | -0.10986 | 0 | -0.24719 | 1.0117 | 1.2039 | 0.30212 | 1.3138 | 0.41199 | -0.054932 | 0.032043 | -122.8638 | 0.032044 | 0.17395 | 0.091553 | 0.22888 | 0.14648 | 1.1215 | 122.7127 | 0.086976 | 0.041199 | 122.9599 | 122.937 | 122.85 | 122.8821 | -122.9599 | -122.905 | 122.6028 | -0.013733 | 2.3071 | 1.0849
1362.1719 | 122.9782 | -57.1701 | 65.7349 | -0.075836 | 0.0010489 | 0.064375 | 0.074386 | -0.00069423 | 0.0032599 | 0.0071308 | 0.010864 | 0.0030249 | -0.00064077 | 0.00027342 | -0.0015061 | -0.0028027 | 0.00045294 | -54.9591 | 65.6982 | -57.2617 | 65.4556 | -56.1356 | -56.8314 | -55.9296 | -56.0715 | 65.7211 | -57.2067 | -57.1518 | -57.1564 | -57.2708 | -56.9733 | -0.091553 | -0.036621 | -0.27924 | 1.0345 | 1.2405 | 0.33875 | 1.3321 | 0.4303 | -0.036621 | -0.013733 | -122.8867 | 0.013733 | 0.19684 | -0.10071 | 0.23346 | -0.064087 | 1.1261 | 122.7173 | 0.050354 | 0.054932 | 122.9599 | 122.9279 | 122.8683 | 122.8912 | -122.9965 | -122.9416 | 122.6257 | 0.018311 | 2.211 | 1.0986
1363.1719 | 123.0011 | -57.1838 | 65.6937 | -0.060578 | -1.9142e-05 | 0.063094 | 0.076095 | 0.00251 | 0.0032599 | 0.0081988 | 0.035278 | -0.00039305 | 0.00042723 | -0.0037854 | -0.0019333 | -0.0030163 | 0.00023934 | -54.7989 | 65.6616 | -57.2159 | 65.4877 | -56.0989 | -56.8039 | -55.8975 | -56.0486 | 65.7303 | -57.193 | -57.1564 | -57.1609 | -57.2708 | -56.9916 | -0.032043 | -0.032044 | -0.20599 | 1.0849 | 1.2863 | 0.37994 | 1.3184 | 0.41199 | -0.009155 | 0.036621 | -122.85 | 0.022888 | 0.19226 | -0.086975 | 0.20142 | -0.07782 | 1.1169 | 122.7036 | 0.032043 | 0.036621 | 122.8775 | 122.9233 | 122.8455 | 122.9141 | -122.9095 | -122.8867 | 122.6715 | 0.027466 | 2.3849 | 1.1353
1364.1719 | 122.9736 | -57.1793 | 65.6937 | -0.052948 | 0.00083526 | 0.063734 | 0.074813 | -0.003685 | 0.0030463 | 0.0081988 | 0.023071 | 0.00067495 | -0.00085457 | 0.005614 | -0.0034287 | -0.0021619 | -0.0021107 | -54.8172 | 65.6708 | -57.2342 | 65.4465 | -56.131 | -56.8542 | -55.9387 | -55.8472 | 65.7898 | -57.1426 | -57.1701 | -57.1976 | -57.2662 | -56.9962 | -0.054932 | -0.022889 | -0.24719 | 1.0483 | 1.2405 | 0.32501 | 1.2955 | 0.37994 | 0.036621 | 0.09613 | -122.8638 | -0.018311 | 0.1831 | -0.086975 | 0.14648 | -0.1236 | 1.1032 | 122.6807 | -0.054932 | -0.027466 | 122.905 | 122.9324 | 122.85 | 122.9691 | -122.9279 | -122.8363 | 122.6257 | 0.009155 | 2.3621 | 1.3321
1365.1719 | 123.0148 | -57.1747 | 65.7349 | -0.075836 | 0.0012625 | 0.06288 | 0.073958 | 0.001442 | 0.0017645 | 0.0088398 | 0.023071 | 0.0025975 | -0.00021357 | -0.0044262 | -0.00086511 | -0.0062207 | -0.00061526 | -54.8447 | 65.6982 | -57.2388 | 65.4556 | -56.1447 | -56.8497 | -55.9387 | -56.0669 | 65.7211 | -57.1793 | -57.0511 | -57.2159 | -57.4173 | -57.0969 | -0.064087 | -0.036621 | -0.27924 | 1.03 | 1.236 | 0.32501 | 1.3 | 0.3891 | -0.004577 | -0.013733 | -122.7859 | -0.041198 | 0.07782 | -0.24261 | 0.082397 | -0.23804 | 1.0941 | 122.6944 | -0.036621 | 0.12817 | 122.937 | 122.9004 | 122.8729 | 122.8958 | -122.9736 | -122.9141 | 122.6303 | 0.1236 | 2.33 | 1.1078
1366.1719 | 123.024 | -57.1472 | 65.7211 | -0.075836 | 0.0010489 | 0.064162 | 0.074813 | 0.00058737 | 0.0013373 | 0.010335 | 0.047485 | 0.00067495 | 0.0032044 | -0.0050672 | -0.0019333 | -0.0032301 | -0.0021107 | -54.776 | 65.6525 | -57.225 | 65.5426 | -56.044 | -56.749 | -55.838 | -55.957 | 65.7211 | -57.193 | -57.0969 | -57.1014 | -57.2159 | -56.9412 | -0.07782 | -0.068664 | -0.17853 | 1.1032 | 1.3092 | 0.39825 | 1.387 | 0.47608 | -0.045776 | 0 | -122.818 | 0.045777 | 0.20599 | -0.068664 | 0.25177 | -0.022888 | 1.181 | 122.7676 | 0.091553 | 0.09613 | 122.8775 | 122.9141 | 122.7997 | 122.8683 | -122.9462 | -122.9141 | 122.6898 | 0.050354 | 2.3712 | 1.1902
1367.1719 | 123.0698 | -57.1335 | 65.7166 | -0.098725 | 0.0029715 | 0.061598 | 0.076095 | 0.0040054 | 0.0019781 | 0.0064898 | 0.02002 | -0.0010339 | 0.0019226 | -0.00229 | -1.0706e-05 | -0.0030163 | 0.0010937 | -54.7714 | 65.6387 | -57.2159 | 65.5655 | -56.0303 | -56.7535 | -55.8334 | -55.9433 | 65.6982 | -57.1609 | -57.0877 | -57.0831 | -57.1793 | -56.9138 | -0.082397 | -0.07782 | -0.15106 | 1.1032 | 1.3 | 0.37994 | 1.3824 | 0.46234 | -0.027466 | -0.018311 | -122.8043 | 0.050354 | 0.21973 | -0.045776 | 0.24719 | -0.01831 | 1.1856 | 122.7814 | 0.07782 | 0.073242 | 122.8546 | 122.8592 | 122.7722 | 122.8317 | -122.9324 | -122.8775 | 122.699 | 0.045776 | 2.3621 | 1.1902
1368.1719 | 122.9553 | -57.1564 | 65.7303 | -0.091095 | -0.0019417 | 0.063094 | 0.075454 | 0.00016017 | 0.0019781 | 0.0084124 | 0.029175 | 0.0011023 | 2.8e-08 | 0.0047594 | -0.00022431 | -0.0047253 | 0.0017345 | -54.7989 | 65.6799 | -57.2342 | 65.5106 | -56.1172 | -56.8085 | -55.9067 | -56.0165 | 65.7303 | -57.1976 | -57.1655 | -57.1518 | -57.28 | -56.987 | -0.07782 | -0.050354 | -0.21973 | 1.0391 | 1.2497 | 0.3479 | 1.3275 | 0.42572 | -0.041199 | 0 | -122.8958 | 0.004578 | 0.16937 | -0.1236 | 0.21057 | -0.082397 | 1.1169 | 122.7448 | 0.045777 | 0.032044 | 122.9141 | 122.9279 | 122.8363 | 122.8867 | -122.9645 | -122.9279 | 122.6669 | -0.009155 | 2.3575 | 1.1398
1369.1719 | 123.0057 | -57.1426 | 65.7166 | -0.037689 | 0.0023307 | 0.062453 | 0.075667 | -0.0032578 | 0.0030463 | 0.0077716 | 0.044434 | 3.4148e-05 | 0.0023498 | -0.0052808 | -0.00043791 | -0.0025891 | 0.0025891 | -54.7897 | 65.6525 | -57.2113 | 65.5106 | -56.0715 | -56.7902 | -55.8975 | -56.012 | 65.7257 | -57.1884 | -57.1381 | -57.1426 | -57.2571 | -56.9733 | -0.068665 | -0.064087 | -0.20599 | 1.0712 | 1.2451 | 0.35248 | 1.3138 | 0.42114 | -0.045777 | 0.009155 | -122.8546 | 0 | 0.16937 | -0.11444 | 0.21515 | -0.068664 | 1.1398 | 122.7219 | 0.045777 | 0.050354 | 122.8638 | 122.9141 | 122.7951 | 122.8683 | -122.9279 | -122.905 | 122.6532 | 0.004577 | 2.3529 | 1.1307
1370.1719 | 122.9965 | -57.1472 | 65.7074 | -0.045319 | 0.0014761 | 0.065016 | 0.07289 | -0.00048063 | 0.0045417 | 0.0079852 | 0.02002 | 0.0025975 | 0.00085443 | -0.0052808 | -0.0025741 | -0.0025891 | -0.0031787 | -54.776 | 65.6479 | -57.2159 | 65.5334 | -56.0623 | -56.7535 | -55.8701 | -55.9982 | 65.7166 | -57.1793 | -57.1243 | -57.1289 | -57.2571 | -56.9733 | -0.068664 | -0.059509 | -0.17395 | 1.0849 | 1.2772 | 0.39368 | 1.3458 | 0.46234 | -0.032043 | 0.009156 | -122.8317 | 0.018311 | 0.17395 | -0.10986 | 0.20599 | -0.07782 | 1.1536 | 122.7493 | 0.050354 | 0.054931 | 122.8638 | 122.8958 | 122.7951 | 122.8638 | -122.9233 | -122.8867 | 122.6807 | 0.022888 | 2.3712 | 1.149
1371.1719 | 122.9736 | -57.1747 | 65.7211 | -0.11398 | 0.0014761 | 0.063734 | 0.074813 | 0.0018692 | 0.0021917 | 0.010549 | 0.001709 | 0.0013159 | 0.00021363 | 0.0045458 | -0.0017197 | -0.0030163 | 0.0038709 | -54.8172 | 65.657 | -57.2662 | 65.4556 | -56.1493 | -56.8314 | -55.9433 | -56.0577 | 65.7303 | -57.1884 | -57.1564 | -57.1609 | -57.2708 | -56.9733 | -0.091552 | -0.064087 | -0.2655 | 1.0254 | 1.2314 | 0.34332 | 1.3229 | 0.43488 | -0.013733 | 0.009156 | -122.8775 | 0.013733 | 0.20142 | -0.09613 | 0.21515 | -0.082397 | 1.1169 | 122.7219 | 0.027466 | 0.032044 | 122.9233 | 122.9187 | 122.8317 | 122.905 | -122.9874 | -122.9095 | 122.6303 | 0.018311 | 2.3575 | 1.1169
1372.1719 | 122.9782 | -57.1655 | 65.6891 | -0.083466 | -0.00087374 | 0.064162 | 0.075881 | -0.001976 | 0.0051825 | 0.0096942 | -0.010498 | 0.0025975 | 0.0012818 | 0.001128 | -0.00086511 | -0.0038709 | -0.0014697 | -54.8401 | 65.6891 | -57.225 | 65.4007 | -56.1172 | -56.8771 | -55.9662 | -56.0669 | 65.712 | -57.2159 | -57.1518 | -57.1609 | -57.2937 | -56.9824 | -0.05951 | 0 | -0.28839 | 1.0483 | 1.1993 | 0.28839 | 1.2589 | 0.3479 | -0.050354 | 0.022888 | -122.8409 | 0.004577 | 0.1831 | -0.12817 | 0.23346 | -0.07782 | 1.1078 | 122.6257 | 0.054931 | 0.064087 | 122.9141 | 122.9279 | 122.8546 | 122.8775 | -122.9141 | -122.905 | 122.5662 | 0.013733 | 2.3254 | 1.0986
1373.1719 | 123.0927 | -57.1426 | 65.6982 | -0.12161 | 0.0027579 | 0.063521 | 0.074386 | -0.0017624 | 0.0036871 | 0.010121 | 0.035278 | 0.00088875 | 2.8e-08 | -0.0033582 | 0.00020289 | -0.0042981 | -0.00040166 | -54.7714 | 65.6342 | -57.1976 | 65.5701 | -56.0394 | -56.749 | -55.8472 | -55.9387 | 65.6982 | -57.1564 | -57.0831 | -57.0694 | -57.1747 | -56.9046 | -0.054932 | -0.064087 | -0.12817 | 1.1032 | 1.2955 | 0.39368 | 1.3504 | 0.44861 | -0.013733 | 0 | -122.7814 | 0.073242 | 0.23804 | -0.032044 | 0.25177 | -0.018311 | 1.1581 | 122.7676 | 0.086975 | 0.073242 | 122.8317 | 122.8546 | 122.7768 | 122.8409 | -122.8958 | -122.8546 | 122.7127 | 0.059509 | 2.3712 | 1.2039
1374.1719 | 122.9965 | -57.1747 | 65.7349 | -0.052948 | 0.00083526 | 0.063094 | 0.074599 | -0.00026703 | 0.0032599 | 0.0084124 | 0.0078126 | -0.0014613 | -0.00021357 | 5.9824e-05 | -0.0019333 | -0.0036573 | 0.00023934 | -54.776 | 65.6845 | -57.2159 | 65.506 | -56.0852 | -56.7947 | -55.8746 | -56.0211 | 65.7074 | -57.1747 | -57.1198 | -57.1335 | -57.2891 | -56.9778 | -0.041198 | -0.050354 | -0.22888 | 1.0895 | 1.3 | 0.37994 | 1.3412 | 0.42114 | 0 | -0.027466 | -122.8546 | 0.041199 | 0.19684 | -0.11444 | 0.19684 | -0.11444 | 1.1307 | 122.7219 | 0.041199 | 0.054932 | 122.9004 | 122.8821 | 122.8592 | 122.8821 | -122.9507 | -122.9095 | 122.6807 | 0.054932 | 2.3987 | 1.1536
1375.1719 | 122.905 | -57.1426 | 65.7074 | -0.0071715 | 0.00040806 | 0.064803 | 0.075454 | 0.0027238 | 0.0026191 | 0.0094806 | 0.001709 | 0.0013159 | 0.0032044 | -0.001222 | -1.0706e-05 | -0.0010937 | 0.0021619 | -54.8355 | 65.7166 | -57.2525 | 65.451 | -56.1401 | -56.8268 | -55.925 | -56.0532 | 65.7532 | -57.1976 | -57.1472 | -57.2159 | -57.0465 | -56.8909 | -0.10986 | 0.009156 | -0.25635 | 1.0025 | 1.2177 | 0.31586 | 1.3275 | 0.42572 | -0.054932 | 0.045777 | -122.8546 | -0.073242 | 0.25177 | 0.09613 | 0.3067 | 0.15106 | 1.1124 | 122.7036 | -0.01831 | 0.050354 | 122.9691 | 122.9507 | 122.8592 | 122.8958 | -122.9599 | -122.905 | 122.5937 | -0.004578 | 2.3071 | 1.0895
1376.1719 | 122.9965 | -57.1793 | 65.7257 | -0.045319 | 0.0016899 | 0.063521 | 0.073745 | -0.00069423 | 0.00048269 | 0.007558 | -0.01355 | 0.0021703 | -0.00042717 | -0.00015378 | -0.0030013 | -0.0028027 | 0.0015209 | -54.8172 | 65.7074 | -57.2159 | 65.4694 | -56.1356 | -56.8726 | -55.9158 | -56.0486 | 65.7257 | -57.2021 | -57.1747 | -57.1518 | -57.2754 | -56.987 | -0.036621 | -0.018311 | -0.25635 | 1.0437 | 1.2634 | 0.3067 | 1.3 | 0.34332 | -0.022888 | 0 | -122.9004 | 0.027466 | 0.19226 | -0.096131 | 0.21515 | -0.073243 | 1.0803 | 122.6852 | 0.050354 | 0.027465 | 122.9233 | 122.9279 | 122.8867 | 122.905 | -122.9416 | -122.9279 | 122.6486 | 0.004577 | 2.3621 | 1.1307
1377.1719 | 123.024 | -57.1518 | 65.7211 | -0.068207 | 0.00062166 | 0.062666 | 0.073958 | -0.0015488 | 0.0024053 | 0.0073444 | 0.053589 | -0.00060665 | 0.001068 | 0.0026232 | -0.0030013 | -0.0034437 | -0.0044605 | -54.7852 | 65.657 | -57.2067 | 65.5609 | -56.0486 | -56.749 | -55.8563 | -55.9525 | 65.6754 | -57.1838 | -57.0877 | -57.0831 | -57.1747 | -56.9046 | -0.054932 | -0.064087 | -0.16022 | 1.1032 | 1.2955 | 0.40283 | 1.3504 | 0.45776 | -0.032044 | -0.045776 | -122.8088 | 0.068664 | 0.24719 | -0.022889 | 0.27924 | 0.009155 | 1.1581 | 122.7676 | 0.10071 | 0.09613 | 122.8638 | 122.8592 | 122.8088 | 122.8271 | -122.9279 | -122.905 | 122.7127 | 0.064086 | 2.3666 | 1.1993
1378.1719 | 123.0057 | -57.1701 | 65.7074 | -0.037689 | 0.00019446 | 0.062239 | 0.074599 | -0.0013352 | 0.0043281 | 0.0088398 | 0.010864 | 0.00024775 | 0.00085443 | -0.0086988 | -0.0021469 | -0.0021619 | 0.0025891 | -54.7943 | 65.6662 | -57.2205 | 65.4922 | -56.1172 | -56.8176 | -55.8975 | -56.0394 | 65.7028 | -57.2113 | -57.1381 | -57.1426 | -57.2662 | -56.9824 | -0.050354 | -0.041198 | -0.21515 | 1.0529 | 1.2726 | 0.35248 | 1.3229 | 0.40283 | -0.041199 | -0.004577 | -122.8455 | 0.027466 | 0.18768 | -0.09613 | 0.22888 | -0.054931 | 1.1032 | 122.7127 | 0.068665 | 0.073242 | 122.8867 | 122.9141 | 122.8363 | 122.8729 | -122.9279 | -122.9187 | 122.6624 | 0.032043 | 2.3758 | 1.1307
1379.1719 | 122.937 | -57.1884 | 65.712 | -0.075836 | 0.00040806 | 0.06288 | 0.074386 | -0.0011214 | 0.0047553 | 0.009267 | 0.0078126 | 0.00067495 | 0.00021363 | -0.0018628 | -0.0030013 | -0.0019483 | -0.0012561 | -54.8538 | 65.7074 | -57.2342 | 65.4648 | -56.1539 | -56.8405 | -55.9433 | -56.0715 | 65.7349 | -57.193 | -57.2845 | -57.1701 | -57.2708 | -57.0007 | -0.045776 | -0.004578 | -0.24719 | 1.0345 | 1.2451 | 0.3479 | 1.2909 | 0.39368 | -0.004577 | 0.022888 | -122.9965 | 0.018311 | 0.18768 | -0.082397 | 0.19226 | -0.07782 | 1.0803 | 122.699 | 0.022888 | -0.091553 | 122.9416 | 122.9279 | 122.8958 | 122.9233 | -122.9462 | -122.905 | 122.6532 | -0.09613 | 2.3346 | 1.1169
1380.1719 | 123.0103 | -57.1747 | 65.6525 | -0.12924 | 0.0012625 | 0.062239 | 0.075027 | 0.00486 | 0.0028327 | 0.010121 | -0.062378 | 0.0013159 | -0.00042717 | -0.003999 | 0.00084389 | -0.0023755 | -0.0010425 | -54.8767 | 65.6387 | -57.2891 | 65.419 | -56.2042 | -56.9183 | -55.9891 | -56.0852 | 65.6754 | -57.2433 | -57.1381 | -57.1884 | -57.3166 | -56.9824 | -0.11444 | -0.013733 | -0.23346 | 0.97046 | 1.1856 | 0.25635 | 1.3 | 0.37079 | -0.068664 | 0.022888 | -122.7905 | -0.013733 | 0.19226 | -0.14191 | 0.26093 | -0.073242 | 1.0849 | 122.7081 | 0.054931 | 0.10529 | 122.9279 | 122.9187 | 122.8134 | 122.85 | -122.9416 | -122.8958 | 122.5937 | 0.036621 | 2.298 | 1.0895
1381.1719 | 122.9553 | -57.1747 | 65.744 | -0.060578 | 0.00040806 | 0.06288 | 0.073745 | -0.0017624 | 0.0043281 | 0.011617 | 0.0078126 | 0.00067495 | -0.0010682 | 5.9824e-05 | -0.00022431 | -0.0040845 | -0.00082886 | -54.8492 | 65.6754 | -57.225 | 65.4648 | -56.1401 | -56.8451 | -55.9204 | -56.044 | 65.7211 | -57.1976 | -57.1609 | -57.1426 | -57.2754 | -56.9962 | -0.050354 | -0.068665 | -0.27924 | 1.0345 | 1.2543 | 0.32959 | 1.3046 | 0.37994 | -0.022888 | -0.022889 | -122.905 | 0.032044 | 0.17853 | -0.10071 | 0.20142 | -0.07782 | 1.0849 | 122.6898 | 0.054932 | 0.036621 | 122.9004 | 122.9187 | 122.85 | 122.8958 | -122.9691 | -122.9416 | 122.6395 | 0.013733 | 2.3254 | 1.1307
1382.1719 | 123.0652 | -57.1289 | 65.6799 | -0.10635 | 0.00019446 | 0.062453 | 0.074386 | -0.0024032 | 0.0053961 | 0.0073444 | 0.023071 | -0.00017945 | -0.0010682 | -0.0025036 | 0.00041649 | -0.0032301 | -0.0023243 | -54.8035 | 65.6387 | -57.1793 | 65.5426 | -56.044 | -56.749 | -55.8563 | -55.9616 | 65.6799 | -57.1747 | -57.0877 | -57.0786 | -57.193 | -56.9229 | -0.050354 | -0.041199 | -0.13733 | 1.0849 | 1.2726 | 0.37994 | 1.3229 | 0.4303 | -0.045777 | 0 | -122.7676 | 0.050354 | 0.20599 | -0.064087 | 0.25177 | -0.01831 | 1.1353 | 122.7219 | 0.096131 | 0.086975 | 122.818 | 122.8546 | 122.7676 | 122.8088 | -122.8592 | -122.8546 | 122.6715 | 0.041198 | 2.3254 | 1.1673
1383.1719 | 122.9828 | -57.1609 | 65.712 | -0.075836 | 0.0010489 | 0.064162 | 0.073958 | 0.001442 | 0.0026191 | 0.0069172 | 0.0078126 | 0.0021703 | 0.00064083 | -0.0033582 | -0.00022431 | -0.0036573 | -0.00040166 | -54.8172 | 65.6845 | -57.2113 | 65.506 | -56.1081 | -56.8085 | -55.8929 | -56.0303 | 65.7074 | -57.193 | -57.1472 | -57.1518 | -57.2479 | -57.0007 | -0.050354 | -0.027466 | -0.20599 | 1.0529 | 1.268 | 0.35248 | 1.3184 | 0.40283 | -0.032043 | -0.004578 | -122.8592 | 0.009156 | 0.16022 | -0.086975 | 0.19226 | -0.054932 | 1.1032 | 122.7173 | 0.041199 | 0.045776 | 122.8958 | 122.9004 | 122.8455 | 122.8683 | -122.9233 | -122.905 | 122.6669 | 0.013733 | 2.3438 | 1.1307
1384.1719 | 122.9645 | -57.1609 | 65.6982 | -0.10635 | 0.00040806 | 0.063307 | 0.07289 | 0.00058737 | 0.0056097 | 0.0062762 | 0.029175 | 0.0023839 | 0.001068 | -0.0035718 | -0.00086511 | -0.0049389 | 0.0017345 | -54.7989 | 65.6433 | -57.2205 | 65.5106 | -56.0989 | -56.7856 | -55.8838 | -56.0074 | 65.6982 | -57.1976 | -57.1564 | -57.1243 | -57.2433 | -56.9504 | -0.059509 | -0.054931 | -0.18768 | 1.062 | 1.2772 | 0.37537 | 1.3367 | 0.43488 | -0.036621 | 0 | -122.8546 | 0.036621 | 0.21057 | -0.082397 | 0.24719 | -0.045776 | 1.1215 | 122.731 | 0.073242 | 0.041199 | 122.8638 | 122.8958 | 122.8043 | 122.8592 | -122.9187 | -122.8958 | 122.6715 | 0.004578 | 2.3621 | 1.1536
1385.1719 | 122.9462 | -57.2113 | 65.6662 | -0.098725 | 0.0010489 | 0.064803 | 0.078017 | -0.0013352 | 0.0013373 | 0.0096942 | -0.089844 | 0.0015295 | -0.0021362 | -0.0018628 | -0.0017197 | -0.0019483 | 0.00023934 | -54.8767 | 65.6433 | -57.28 | 65.4144 | -56.2134 | -56.9092 | -55.9937 | -56.1356 | 65.6937 | -57.2479 | -57.1976 | -57.2388 | -57.3807 | -57.0465 | -0.068664 | -0.022888 | -0.25177 | 0.99792 | 1.2177 | 0.30212 | 1.2863 | 0.37079 | -0.036621 | 0.027466 | -122.8638 | -0.027466 | 0.16479 | -0.16937 | 0.20142 | -0.13275 | 1.0666 | 122.6944 | 0.009155 | 0.050354 | 122.9233 | 122.9416 | 122.8546 | 122.905 | -122.9462 | -122.9141 | 122.6257 | 0.013733 | 2.3346 | 1.0757
1386.1719 | 122.9324 | -57.1335 | 65.7303 | -0.091095 | -0.00066014 | 0.061598 | 0.074172 | -0.0017624 | 0.0036871 | 0.0077716 | 0.013916 | 0.0011023 | 0.0014954 | -0.0061352 | -0.00086511 | -0.0032301 | -0.0042469 | -54.8264 | 65.6891 | -57.2159 | 65.4465 | -56.1584 | -56.8497 | -55.925 | -56.0623 | 65.7349 | -57.2205 | -57.1518 | -57.1518 | -57.2983 | -57.0053 | -0.082397 | -0.041199 | -0.28381 | 0.97504 | 1.2085 | 0.28381 | 1.2909 | 0.36621 | -0.086975 | 0.004577 | -122.8821 | -0.01831 | 0.12817 | -0.16479 | 0.21515 | -0.07782 | 1.0574 | 122.6624 | 0.068665 | 0.068665 | 122.905 | 122.9553 | 122.8226 | 122.8683 | -122.9462 | -122.9507 | 122.58 | -0.01831 | 2.3071 | 1.0712
1387.1719 | 123.1018 | -57.1243 | 65.6708 | -0.083466 | -0.00044654 | 0.061812 | 0.073531 | 0.0020828 | 0.0013373 | 0.0052082 | 0.026123 | 0.0017431 | 0.00064083 | -0.001222 | 0.00084389 | -0.0032301 | -0.00018806 | -54.7943 | 65.6342 | -57.1976 | 65.6937 | -56.2866 | -56.9641 | -55.8243 | -55.9708 | 65.6662 | -57.1838 | -57.0602 | -57.0511 | -57.1518 | -56.8863 | -0.073242 | -0.036621 | 0.022889 | 0.83771 | 1.3 | 0.16022 | 1.3733 | 0.23346 | -0.059509 | -0.004577 | -122.731 | 0.073243 | 0.23804 | -0.027465 | 0.29755 | 0.032044 | 0.91095 | 122.8912 | 0.13275 | 0.1236 | 122.8317 | 122.85 | 122.7585 | 122.7905 | -122.8683 | -122.8546 | 122.818 | 0.064087 | 2.33 | 1.1536
1388.1719 | 122.9599 | -57.2021 | 65.7211 | -0.037689 | 0.0012625 | 0.063094 | 0.074172 | -0.00048063 | 0.0032599 | 0.0084124 | 0.016968 | 0.00067495 | 0.00085443 | 0.001128 | -0.0021469 | -0.0023755 | 0.0019483 | -54.8538 | 65.6891 | -57.2021 | 65.4785 | -56.1356 | -56.8359 | -55.9296 | -56.0349 | 65.7211 | -57.2067 | -57.1426 | -57.1564 | -57.2571 | -57.0053 | 0 | -0.032043 | -0.24261 | 1.0666 | 1.2726 | 0.36621 | 1.2726 | 0.36621 | -0.004578 | 0 | -122.8638 | 0.045776 | 0.19684 | -0.054932 | 0.20142 | -0.050354 | 1.0666 | 122.6807 | 0.050354 | 0.064087 | 122.8912 | 122.9279 | 122.8912 | 122.9233 | -122.9233 | -122.9279 | 122.6807 | 0.059509 | 2.3483 | 1.1673
1389.1719 | 123.0331 | -57.1564 | 65.6799 | -0.098725 | 0.0010489 | 0.062025 | 0.076308 | 0.0027238 | 0.0058233 | 0.005849 | 0.056641 | -0.0010339 | -0.00085457 | -0.0014356 | -0.0038559 | -0.0028027 | -0.0023243 | -54.7989 | 65.6616 | -57.1884 | 65.5563 | -56.0577 | -56.7307 | -55.8334 | -55.9662 | 65.6754 | -57.1701 | -57.0786 | -57.0923 | -57.2021 | -56.9229 | -0.032044 | -0.018311 | -0.1236 | 1.0986 | 1.3229 | 0.42572 | 1.355 | 0.45776 | -0.013733 | -0.004578 | -122.7585 | 0.064087 | 0.23346 | -0.045776 | 0.24719 | -0.032043 | 1.1307 | 122.7448 | 0.07782 | 0.091553 | 122.85 | 122.8455 | 122.818 | 122.8317 | -122.8683 | -122.85 | 122.7127 | 0.07782 | 2.3575 | 1.1902
1390.1719 | 122.9736 | -57.1793 | 65.6891 | -0.11398 | -0.00044654 | 0.061598 | 0.077376 | -0.00048063 | 0.0028327 | 0.010121 | -0.050171 | -0.00017945 | 0.0012818 | 0.0049732 | -0.0030013 | -0.00045288 | -0.0029651 | -54.8401 | 65.6708 | -57.2525 | 65.4419 | -56.1768 | -56.8817 | -55.9799 | -56.0486 | 65.6982 | -57.2296 | -57.1609 | -57.2113 | -57.3578 | -57.019 | -0.073242 | -0.018311 | -0.24719 | 1.0025 | 1.1993 | 0.29755 | 1.2726 | 0.37079 | -0.050354 | 0.009155 | -122.85 | -0.032044 | 0.16022 | -0.17853 | 0.21057 | -0.12817 | 1.0757 | 122.6944 | 0.01831 | 0.068664 | 122.9233 | 122.9279 | 122.85 | 122.8775 | -122.9416 | -122.9187 | 122.6212 | 0.01831 | 2.3392 | 1.1307
1391.1719 | 122.9553 | -57.1793 | 65.712 | -0.014801 | -0.0010873 | 0.061812 | 0.074386 | 0.0010148 | 0.0045417 | 0.0086262 | 0.026123 | -0.00039305 | 0.00042723 | 5.9824e-05 | -0.00086511 | -0.0028027 | -0.00040166 | -54.7943 | 65.6799 | -57.1838 | 65.4922 | -56.1172 | -56.8039 | -55.8884 | -56.0211 | 65.712 | -57.2021 | -57.1426 | -57.1564 | -57.2754 | -56.9778 | -0.004578 | -0.032043 | -0.21973 | 1.062 | 1.2909 | 0.37537 | 1.2955 | 0.37994 | -0.022888 | 0 | -122.8546 | 0.022888 | 0.20142 | -0.096131 | 0.2243 | -0.073243 | 1.0666 | 122.6761 | 0.045776 | 0.059509 | 122.8638 | 122.9141 | 122.8592 | 122.8912 | -122.8958 | -122.9141 | 122.6715 | 0.036621 | 2.3849 | 1.1581
1392.1719 | 122.9828 | -57.1564 | 65.712 | -0.03006 | -0.00066014 | 0.064803 | 0.073104 | -0.0011214 | 0.0039007 | 0.007558 | 0.016968 | 0.0015295 | 0.0014954 | 0.001128 | -0.00086511 | -0.0038709 | 0.00023934 | -54.8035 | 65.657 | -57.193 | 65.5014 | -56.0944 | -56.7993 | -55.8838 | -56.0074 | 65.6982 | -57.2021 | -57.1609 | -57.1289 | -57.2571 | -56.9824 | -0.036621 | -0.054932 | -0.21057 | 1.062 | 1.2726 | 0.35706 | 1.3092 | 0.39368 | -0.045776 | -0.013733 | -122.8729 | 0.027466 | 0.17395 | -0.10071 | 0.21973 | -0.054932 | 1.0986 | 122.6944 | 0.073242 | 0.041198 | 122.85 | 122.9004 | 122.8134 | 122.8546 | -122.905 | -122.9141 | 122.6578 | -0.004578 | 2.3529 | 1.149
1393.1719 | 123.0743 | -57.1609 | 65.6662 | -0.22842 | 0.00040806 | 0.062453 | 0.074599 | -0.0032578 | 0.0028327 | 0.009267 | 0.041382 | 0.00046135 | 0.00064083 | -0.0067762 | -0.00065151 | -0.0045117 | -0.0042469 | -54.7485 | 65.6158 | -57.225 | 65.5609 | -56.0532 | -56.7398 | -55.8517 | -55.9433 | 65.6845 | -57.1701 | -57.0602 | -57.0694 | -57.1701 | -56.8863 | -0.064087 | -0.050354 | -0.10529 | 1.1078 | 1.3092 | 0.42114 | 1.3733 | 0.48523 | -0.009155 | 0.01831 | -122.7264 | 0.091553 | 0.27466 | -0.009155 | 0.28381 | 0 | 1.1719 | 122.7859 | 0.10071 | 0.10986 | 122.8409 | 122.8546 | 122.7768 | 122.8455 | -122.8912 | -122.8363 | 122.7219 | 0.10071 | 2.4124 | 1.2177
1394.1719 | 122.9919 | -57.1838 | 65.7349 | -0.098725 | -0.00087374 | 0.062453 | 0.075667 | 0.00016017 | -0.00015811 | 0.0069172 | 0.0078126 | -0.00039305 | 0.0012818 | -0.00015378 | -0.00022431 | -0.0040845 | 0.0028027 | -54.8126 | 65.6479 | -57.2205 | 65.5151 | -56.0989 | -56.7764 | -55.8746 | -55.9708 | 65.712 | -57.1838 | -57.1426 | -57.1426 | -57.2571 | -56.9641 | -0.036621 | -0.086975 | -0.21973 | 1.0849 | 1.3092 | 0.40741 | 1.3458 | 0.44403 | 0 | -0.022888 | -122.8775 | 0.041199 | 0.21973 | -0.073242 | 0.21973 | -0.073242 | 1.1215 | 122.7356 | 0.041199 | 0.041199 | 122.8683 | 122.8958 | 122.8317 | 122.8958 | -122.9553 | -122.9187 | 122.699 | 0.041199 | 2.3712 | 1.2131
1395.1719 | 122.9828 | -57.193 | 65.7349 | -0.083466 | 0.00019446 | 0.063948 | 0.075454 | -0.0013352 | 0.0015509 | 0.0086262 | 0.044434 | 0.0019567 | 0.0012818 | 0.00091422 | -0.0017197 | -0.0036573 | 0.00045294 | -54.808 | 65.657 | -57.2021 | 65.506 | -56.1081 | -56.781 | -55.8792 | -55.9937 | 65.6982 | -57.1838 | -57.1335 | -57.1564 | -57.2617 | -56.9733 | -0.009155 | -0.07782 | -0.22888 | 1.0849 | 1.3138 | 0.41199 | 1.3229 | 0.42114 | 0.009155 | -0.036621 | -122.8683 | 0.036621 | 0.21973 | -0.068665 | 0.21057 | -0.07782 | 1.0941 | 122.7081 | 0.027466 | 0.050354 | 122.8592 | 122.8821 | 122.85 | 122.8912 | -122.937 | -122.9187 | 122.699 | 0.059509 | 2.3849 | 1.1993
1396.1719 | 123.0286 | -57.1793 | 65.7166 | -0.091095 | -0.00023294 | 0.063307 | 0.074386 | -0.00026703 | 0.0026191 | 0.010976 | -0.047119 | 0.00046135 | 0.0019226 | 0.00091422 | -0.0010787 | -0.00088008 | -0.0010425 | -54.8767 | 65.6754 | -57.2342 | 65.4465 | -56.1951 | -56.8542 | -55.957 | -56.0623 | 65.7211 | -57.2205 | -57.1564 | -57.1609 | -57.2891 | -56.9824 | -0.054932 | -0.041199 | -0.27008 | 0.98419 | 1.2222 | 0.32501 | 1.2772 | 0.37994 | -0.041199 | 0.004577 | -122.8729 | 0.01831 | 0.19684 | -0.10986 | 0.23804 | -0.068665 | 1.0391 | 122.6807 | 0.059509 | 0.064087 | 122.9095 | 122.9416 | 122.8546 | 122.9004 | -122.9507 | -122.937 | 122.6257 | 0.022888 | 2.3026 | 1.1169
1397.1719 | 122.9187 | -57.1884 | 65.7028 | -0.037689 | -0.00066014 | 0.062239 | 0.07524 | -0.00026703 | 0.0030463 | 0.0069172 | 0.016968 | 3.4148e-05 | 0.0029906 | -0.0014356 | -0.00043791 | -0.0032301 | -0.0010425 | -54.8904 | 65.6845 | -57.2342 | 65.4694 | -56.163 | -56.8497 | -55.9433 | -56.0577 | 65.7349 | -57.1884 | -57.2479 | -56.9412 | -57.2525 | -57.0236 | -0.045776 | -0.018311 | -0.23346 | 1.0254 | 1.2451 | 0.33875 | 1.2909 | 0.38452 | 0 | 0.032043 | -122.9507 | 0.24719 | 0.16479 | -0.064086 | 0.16479 | -0.064086 | 1.0712 | 122.7036 | 0.24719 | -0.059509 | 122.9187 | 122.9233 | 122.8729 | 122.9233 | -122.937 | -122.8912 | 122.6578 | -0.059509 | 2.298 | 1.1307
1398.1719 | 122.9095 | -57.1793 | 65.7211 | -0.052948 | 0.0014761 | 0.063307 | 0.075027 | 0.001442 | 0.0036871 | 0.0088398 | 0.0047608 | 0.0028113 | -0.00064077 | -0.0035718 | -0.00086511 | -0.0042981 | 2.554e-05 | -54.8996 | 65.7074 | -57.2479 | 65.4419 | -56.1768 | -56.8405 | -55.9479 | -56.0669 | 65.7211 | -57.2159 | -57.2113 | -56.9275 | -57.3441 | -57.0465 | -0.068665 | -0.013733 | -0.27923 | 1.0025 | 1.2314 | 0.33874 | 1.3 | 0.40741 | -0.036621 | 0 | -122.9324 | 0.25177 | 0.13275 | -0.16479 | 0.16937 | -0.12817 | 1.0712 | 122.6898 | 0.28839 | 0.004577 | 122.9553 | 122.937 | 122.8867 | 122.9004 | -122.9691 | -122.937 | 122.6212 | -0.032044 | 2.2797 | 1.1124
1399.1719 | 122.9233 | -57.1838 | 65.6937 | -0.052948 | 0.00040806 | 0.06288 | 0.07289 | 0.00037377 | 0.0026191 | 0.009267 | -0.0074462 | 0.00046135 | -0.00064077 | -0.0050672 | -0.0015061 | -0.0025891 | -0.0040333 | -54.8859 | 65.6845 | -57.2388 | 65.4419 | -56.1859 | -56.868 | -55.9341 | -56.0486 | 65.7028 | -57.2159 | -57.1976 | -56.955 | -57.3578 | -57.0419 | -0.054932 | -0.009156 | -0.25177 | 0.99793 | 1.2497 | 0.31586 | 1.3046 | 0.37079 | -0.032043 | 0.009155 | -122.8912 | 0.22888 | 0.14191 | -0.17395 | 0.17395 | -0.14191 | 1.0529 | 122.6807 | 0.26093 | 0.01831 | 122.9233 | 122.9187 | 122.8683 | 122.8867 | -122.9324 | -122.9095 | 122.6257 | -0.013733 | 2.298 | 1.1353
1400.1719 | 122.9141 | -57.1793 | 65.6891 | -0.075836 | -0.0013009 | 0.062666 | 0.076308 | 0.0018692 | 0.0028327 | 0.011617 | 0.001709 | 0.00088875 | 0.0025634 | -0.0010084 | -0.0010787 | -0.0023755 | -0.0031787 | -54.8859 | 65.6662 | -57.2342 | 65.451 | -56.1676 | -56.8359 | -55.9525 | -56.0577 | 65.7028 | -57.1884 | -57.2205 | -56.9366 | -57.3303 | -57.0145 | -0.054932 | -0.022888 | -0.23804 | 1.0117 | 1.2268 | 0.34332 | 1.2817 | 0.39825 | -0.009156 | 0.013733 | -122.9095 | 0.24261 | 0.16479 | -0.15106 | 0.17395 | -0.14191 | 1.0666 | 122.6852 | 0.25177 | -0.032043 | 122.9004 | 122.8912 | 122.8455 | 122.8821 | -122.9233 | -122.8775 | 122.6303 | -0.041199 | 2.2934 | 1.1215
1401.1719 | 122.9279 | -57.1609 | 65.7166 | -0.091095 | 0.0014761 | 0.061812 | 0.075454 | -0.0015488 | 0.0043281 | 0.0086262 | 0.023071 | 0.0021703 | 0.001709 | 0.0049732 | -0.0030013 | -0.0030163 | 0.0010937 | -54.9088 | 65.6708 | -57.2342 | 65.451 | -56.1859 | -56.8588 | -55.9525 | -56.0623 | 65.7257 | -57.2205 | -57.2342 | -57.0511 | -57.106 | -56.987 | -0.073242 | -0.045777 | -0.2655 | 0.97504 | 1.2085 | 0.30212 | 1.2817 | 0.37537 | -0.059509 | 0.009155 | -122.9507 | 0.10986 | 0.17395 | 0.054932 | 0.23346 | 0.11444 | 1.0483 | 122.6852 | 0.16937 | -0.013733 | 122.905 | 122.9462 | 122.8317 | 122.8867 | -122.9507 | -122.937 | 122.612 | -0.073242 | 2.2522 | 1.0986
1402.1719 | 122.9828 | -57.1518 | 65.6982 | -0.03006 | -0.00023294 | 0.062453 | 0.075454 | 0.0020828 | 0.0011237 | 0.0073444 | -0.01355 | 0.0025975 | -0.00064077 | 0.0032642 | 0.00020289 | -0.0053663 | -0.0040333 | -54.895 | 65.6754 | -57.2388 | 65.4419 | -56.1951 | -56.8588 | -55.9525 | -56.0806 | 65.7028 | -57.2021 | -57.1472 | -57.1701 | -57.2891 | -56.9962 | -0.086976 | -0.022888 | -0.25635 | 0.95673 | 1.1993 | 0.29297 | 1.2863 | 0.37994 | -0.050354 | 0.004578 | -122.8455 | -0.018311 | 0.15564 | -0.13733 | 0.20599 | -0.086976 | 1.0437 | 122.6807 | 0.032043 | 0.054931 | 122.9141 | 122.905 | 122.8271 | 122.8546 | -122.937 | -122.9004 | 122.5937 | 0.004577 | 2.2568 | 1.0712
1403.1719 | 123.024 | -57.1793 | 65.7028 | -0.060578 | -0.0010873 | 0.06288 | 0.076095 | -0.0015488 | 0.0024053 | 0.0090534 | -0.01355 | 3.4148e-05 | -0.00064077 | 0.008391 | 0.00041649 | -0.0030163 | 0.00023934 | -54.8859 | 65.657 | -57.2571 | 65.4327 | -56.2042 | -56.8634 | -55.9662 | -56.0715 | 65.712 | -57.2113 | -57.1701 | -57.1564 | -57.2662 | -56.987 | -0.07782 | -0.045777 | -0.27008 | 0.97504 | 1.2131 | 0.31586 | 1.2909 | 0.39368 | -0.032044 | 0.009155 | -122.8729 | 0.022888 | 0.19226 | -0.086975 | 0.2243 | -0.054931 | 1.0529 | 122.6898 | 0.054932 | 0.041199 | 122.9141 | 122.9233 | 122.8363 | 122.8912 | -122.9599 | -122.9141 | 122.612 | 0.009155 | 2.2934 | 1.1078
1404.1719 | 123.0148 | -57.1701 | 65.6891 | -0.098725 | -0.00066014 | 0.064589 | 0.073745 | 0.00251 | 0.0034735 | 0.009267 | -0.025757 | 0.0015295 | 2.8e-08 | 0.0041186 | -0.0019333 | -0.0013073 | 0.0021619 | -54.8538 | 65.6799 | -57.2525 | 65.4694 | -56.1447 | -56.8176 | -55.9479 | -56.0165 | 65.7166 | -57.2113 | -57.1289 | -57.1609 | -57.2754 | -56.9733 | -0.082397 | -0.009155 | -0.21973 | 1.0254 | 1.2222 | 0.35248 | 1.3046 | 0.43487 | -0.041199 | 0.027466 | -122.818 | 0.009155 | 0.19684 | -0.10529 | 0.23804 | -0.064087 | 1.1078 | 122.7219 | 0.050354 | 0.082398 | 122.9324 | 122.9279 | 122.85 | 122.8867 | -122.9416 | -122.9004 | 122.6395 | 0.041199 | 2.3163 | 1.1536
1405.1719 | 123.0011 | -57.193 | 65.7028 | -0.022431 | -0.0015145 | 0.062025 | 0.073958 | -0.00090783 | 0.0030463 | 0.0071308 | 0.029175 | 0.0011023 | 0.0012818 | -0.0037854 | 0.0016983 | -0.0028027 | -0.00040166 | -54.9042 | 65.6708 | -57.2388 | 65.4327 | -56.1905 | -56.8542 | -55.9433 | -56.0761 | 65.6937 | -57.225 | -57.0648 | -57.2433 | -57.4356 | -57.0694 | -0.045777 | -0.032044 | -0.27008 | 1.0025 | 1.2497 | 0.33875 | 1.2955 | 0.38452 | -0.032044 | -0.009155 | -122.7676 | -0.050354 | 0.1236 | -0.24262 | 0.15564 | -0.21057 | 1.0483 | 122.6715 | -0.01831 | 0.16022 | 122.9095 | 122.9187 | 122.8638 | 122.8867 | -122.9416 | -122.9279 | 122.6257 | 0.12817 | 2.2888 | 1.1169
1406.1719 | 123.0103 | -57.2021 | 65.6845 | 0.030975 | -0.0015145 | 0.06288 | 0.076308 | 0.00016017 | 0.0034735 | 0.010549 | -0.010498 | 0.0023839 | 0.001068 | 0.0013416 | -0.0030013 | -0.0010937 | 0.0013073 | -54.895 | 65.6754 | -57.2617 | 65.4373 | -56.2134 | -56.8771 | -55.9616 | -56.0852 | 65.6754 | -57.2433 | -57.1472 | -57.1472 | -57.2845 | -56.9733 | -0.05951 | -0.009155 | -0.24719 | 0.98877 | 1.2405 | 0.32501 | 1.3 | 0.38452 | -0.041199 | -0.009155 | -122.8317 | 0.054931 | 0.22888 | -0.082398 | 0.27008 | -0.041199 | 1.0483 | 122.699 | 0.09613 | 0.09613 | 122.937 | 122.9187 | 122.8775 | 122.8775 | -122.9462 | -122.9279 | 122.6395 | 0.054931 | 2.3071 | 1.1169
1407.1719 | 123.0057 | -57.1884 | 65.7211 | -0.03006 | -0.0015145 | 0.064375 | 0.075454 | -0.001976 | 0.0021917 | 0.009267 | 0.010864 | -0.00017945 | -0.00021357 | -0.0059216 | -0.00065151 | -0.0015211 | 0.0030163 | -54.8904 | 65.6891 | -57.2433 | 65.4419 | -56.1996 | -56.8588 | -55.9525 | -56.0898 | 65.712 | -57.2296 | -57.1564 | -57.1747 | -57.28 | -56.9687 | -0.054931 | -0.032043 | -0.27923 | 0.98877 | 1.236 | 0.32959 | 1.2909 | 0.38452 | -0.041198 | -0.009155 | -122.8775 | 0.013733 | 0.21973 | -0.091552 | 0.26093 | -0.050354 | 1.0437 | 122.6852 | 0.054931 | 0.073242 | 122.9324 | 122.9416 | 122.8775 | 122.9004 | -122.9645 | -122.9507 | 122.6303 | 0.032044 | 2.298 | 1.0986
1408.1719 | 122.9553 | -57.1747 | 65.6799 | -0.060578 | -1.9142e-05 | 0.059889 | 0.07225 | -0.0024032 | 0.0021917 | 0.0077716 | 0.013916 | 0.00024775 | 0.003418 | -0.0072034 | 0.00063009 | -0.0015211 | 0.0040845 | -54.9088 | 65.7166 | -57.2342 | 65.4282 | -56.1996 | -56.8634 | -55.9433 | -56.0806 | 65.6982 | -57.2159 | -57.2388 | -57.1426 | -57.3257 | -57.0419 | -0.059509 | 0.036621 | -0.25177 | 0.97504 | 1.2314 | 0.31128 | 1.2909 | 0.37079 | -0.041198 | 0.01831 | -122.9187 | 0.032044 | 0.13275 | -0.15106 | 0.17395 | -0.10986 | 1.0345 | 122.6624 | 0.073242 | -0.022889 | 122.9507 | 122.9141 | 122.8912 | 122.8729 | -122.9141 | -122.8958 | 122.6028 | -0.064087 | 2.2659 | 1.0941
1409.1719 | 123.024 | -57.1884 | 65.6662 | -0.083466 | 0.0027579 | 0.064375 | 0.075881 | 0.0016556 | 0.0028327 | 0.009267 | -0.010498 | 0.0019567 | -0.001709 | 0.002196 | -0.0034287 | -0.0028027 | 0.00045294 | -54.8538 | 65.6845 | -57.2342 | 65.4602 | -56.1722 | -56.8359 | -55.9433 | -55.9937 | 65.6937 | -57.2205 | -57.1243 | -57.1472 | -57.2571 | -56.955 | -0.045776 | 0.01831 | -0.20599 | 1.0162 | 1.2451 | 0.35248 | 1.2909 | 0.39825 | -0.032043 | 0.027466 | -122.7905 | 0.041199 | 0.23346 | -0.068664 | 0.2655 | -0.036621 | 1.062 | 122.6944 | 0.073242 | 0.09613 | 122.9187 | 122.9141 | 122.8729 | 122.8821 | -122.9004 | -122.8867 | 122.6486 | 0.064087 | 2.3346 | 1.1948
1410.1719 | 122.9736 | -57.1976 | 65.6616 | -0.083466 | 0.00040806 | 0.063521 | 0.074386 | 0.00251 | 0.0028327 | 0.0073444 | -0.037964 | 0.0013159 | 0.00064083 | 5.9824e-05 | -0.0017197 | -0.0019483 | -0.0010425 | -54.9133 | 65.6387 | -57.2754 | 65.4144 | -56.2134 | -56.8863 | -55.9982 | -56.0623 | 65.6799 | -57.2205 | -57.193 | -57.2067 | -57.3303 | -57.0145 | -0.07782 | -0.022888 | -0.24719 | 0.98419 | 1.1993 | 0.31128 | 1.2772 | 0.3891 | -0.022888 | 0.018311 | -122.8546 | -0.009155 | 0.18311 | -0.13275 | 0.20599 | -0.10986 | 1.062 | 122.6898 | 0.013733 | 0.027466 | 122.9141 | 122.9004 | 122.8363 | 122.8775 | -122.937 | -122.8821 | 122.612 | 0.004578 | 2.2842 | 1.1353
1411.1719 | 123.0057 | -57.2067 | 65.6754 | -0.052948 | -0.0021555 | 0.06288 | 0.07524 | 0.00058737 | 0.0011237 | 0.0084124 | 0.010864 | 0.0028113 | 0.0014954 | 0.00070062 | -0.00022431 | -0.0032301 | -0.00040166 | -54.8767 | 65.6845 | -57.2479 | 65.4602 | -56.1722 | -56.8359 | -55.9479 | -56.0257 | 65.6799 | -57.2205 | -57.1335 | -57.1426 | -57.2845 | -56.9641 | -0.041199 | 0.009155 | -0.21515 | 1.0345 | 1.2589 | 0.37079 | 1.3 | 0.41199 | -0.013733 | 0.004578 | -122.8088 | 0.064087 | 0.24262 | -0.07782 | 0.25635 | -0.064087 | 1.0757 | 122.7081 | 0.07782 | 0.086975 | 122.9324 | 122.9004 | 122.8912 | 122.8867 | -122.9233 | -122.8958 | 122.6669 | 0.073242 | 2.33 | 1.181
1412.1719 | 122.9919 | -57.1793 | 65.6708 | -0.068207 | 0.0025443 | 0.063307 | 0.075027 | 0.0010148 | 0.0028327 | 0.007558 | -0.044067 | 0.0015295 | 0.00042723 | 0.0030506 | 0.0014847 | -0.0032301 | 0.0042981 | -54.8859 | 65.657 | -57.2571 | 65.4648 | -56.1584 | -56.8497 | -55.9479 | -56.1127 | 65.6754 | -57.2342 | -57.1381 | -57.1655 | -57.2662 | -56.9641 | -0.07782 | -0.013733 | -0.20599 | 1.0208 | 1.2314 | 0.32959 | 1.3092 | 0.40741 | -0.054932 | 0.004578 | -122.8088 | 0.013733 | 0.21515 | -0.086975 | 0.27008 | -0.032043 | 1.0986 | 122.7219 | 0.068665 | 0.09613 | 122.9141 | 122.9095 | 122.8363 | 122.8546 | -122.9279 | -122.905 | 122.644 | 0.041198 | 2.2934 | 1.0666
1413.1719 | 122.9874 | -57.193 | 65.6708 | -0.083466 | 0.0023307 | 0.061812 | 0.075027 | -5.343e-05 | 0.0036871 | 0.010762 | 0.013916 | 0.00088875 | 0.00085443 | -0.006349 | -0.00065151 | -0.0045117 | 0.0025891 | -54.8859 | 65.6845 | -57.2433 | 65.4602 | -56.1859 | -56.8497 | -55.925 | -56.0165 | 65.6982 | -57.1976 | -57.1335 | -57.1518 | -57.2708 | -56.9733 | -0.050354 | 0.013733 | -0.21057 | 1.0071 | 1.268 | 0.34332 | 1.3184 | 0.39368 | -0.004578 | 0.027466 | -122.8043 | 0.041199 | 0.21973 | -0.07782 | 0.2243 | -0.073242 | 1.0574 | 122.7036 | 0.045777 | 0.064087 | 122.9279 | 122.8958 | 122.8775 | 122.8912 | -122.9141 | -122.8683 | 122.6532 | 0.059509 | 2.3071 | 1.1765
1414.1719 | 123.0194 | -57.1793 | 65.6342 | -0.083466 | -0.00023294 | 0.063521 | 0.073318 | 0.003151 | 0.0021917 | 0.0084124 | -0.0043946 | 0.0017431 | 0.0032044 | -0.001222 | 0.0019119 | -0.00088008 | 0.0017345 | -54.8813 | 65.6708 | -57.2388 | 65.4648 | -56.1813 | -56.8451 | -55.957 | -56.0257 | 65.7028 | -57.2479 | -57.1472 | -57.1518 | -57.2708 | -56.9595 | -0.05951 | 0.036621 | -0.16937 | 0.99793 | 1.2222 | 0.33417 | 1.2817 | 0.39368 | -0.068665 | 0.068665 | -122.7814 | 0.027466 | 0.21973 | -0.091553 | 0.28839 | -0.022888 | 1.0574 | 122.7036 | 0.096131 | 0.10071 | 122.9095 | 122.9507 | 122.85 | 122.8821 | -122.8729 | -122.8821 | 122.644 | 0.032043 | 2.298 | 1.1536
1415.1719 | 122.9645 | -57.193 | 65.6799 | -0.075836 | -0.0015145 | 0.060957 | 0.073104 | 0.0012284 | 0.0039007 | 0.010335 | 0.041382 | 0.0017431 | 0.0019226 | -0.0044262 | -0.0010787 | -0.0049389 | -0.0016833 | -54.95 | 65.7349 | -57.225 | 65.4053 | -56.2042 | -56.868 | -55.9662 | -56.1127 | 65.7166 | -57.2159 | -57.1747 | -57.1564 | -57.312 | -57.0007 | -0.032044 | 0.054931 | -0.27466 | 0.98877 | 1.2268 | 0.32501 | 1.2589 | 0.35706 | -0.022888 | 0.036621 | -122.8546 | 0.036621 | 0.19226 | -0.11902 | 0.21515 | -0.096131 | 1.0208 | 122.6303 | 0.059509 | 0.041198 | 122.9599 | 122.9324 | 122.9279 | 122.9095 | -122.905 | -122.8958 | 122.5983 | 0.01831 | 2.243 | 1.0803
1416.1719 | 122.9965 | -57.1793 | 65.6662 | -0.037689 | -0.00044654 | 0.064375 | 0.073958 | -0.0011214 | 0.0019781 | 0.0069172 | 0.0078126 | 0.00088875 | 0.00085443 | 5.9824e-05 | -0.0010787 | -0.00088008 | -0.0018971 | -54.8904 | 65.6708 | -57.2388 | 65.4465 | -56.1951 | -56.8588 | -55.9479 | -56.044 | 65.6937 | -57.2113 | -57.1426 | -57.1564 | -57.2708 | -56.9595 | -0.05951 | 0.004577 | -0.21973 | 0.98419 | 1.2314 | 0.32043 | 1.2909 | 0.37994 | -0.032044 | 0.027466 | -122.8088 | 0.022888 | 0.21973 | -0.091553 | 0.25177 | -0.059509 | 1.0437 | 122.6852 | 0.054932 | 0.068665 | 122.9095 | 122.905 | 122.85 | 122.8729 | -122.905 | -122.8775 | 122.6257 | 0.036621 | 2.2888 | 1.1353
1417.1719 | 123.0057 | -57.1609 | 65.6708 | -0.052948 | 0.0019035 | 0.064162 | 0.076949 | -0.0024032 | 0.0047553 | 0.010121 | -0.016602 | 0.0011023 | -0.00021357 | 0.001128 | -0.0010787 | -0.0045117 | -0.0025379 | -54.8721 | 65.6662 | -57.2388 | 65.451 | -56.1676 | -56.8497 | -55.9433 | -56.0349 | 65.6754 | -57.2205 | -57.1426 | -57.1564 | -57.2937 | -56.987 | -0.07782 | -0.004577 | -0.21973 | 0.99335 | 1.2177 | 0.31128 | 1.2955 | 0.3891 | -0.059509 | 0.004578 | -122.8134 | 0.004578 | 0.17395 | -0.13275 | 0.23346 | -0.073242 | 1.0712 | 122.6898 | 0.064087 | 0.07782 | 122.905 | 122.8958 | 122.8271 | 122.8363 | -122.9095 | -122.8912 | 122.612 | 0.018311 | 2.2888 | 1.1261
1418.1719 | 123.0057 | -57.1747 | 65.6662 | -0.083466 | 0.0021171 | 0.062025 | 0.075667 | 0.00251 | 0.0043281 | 0.0081988 | 0.0078126 | 0.0011023 | 0.003418 | 0.00070062 | -0.0019333 | -0.0034437 | 0.0010937 | -54.8813 | 65.6525 | -57.2342 | 65.4785 | -56.1539 | -56.8497 | -55.9296 | -56.0303 | 65.6845 | -57.2113 | -57.1381 | -57.1655 | -57.2662 | -56.955 | -0.059509 | -0.013733 | -0.18768 | 1.0208 | 1.2451 | 0.32501 | 1.3046 | 0.38452 | -0.036621 | 0.01831 | -122.8043 | 0.009156 | 0.21973 | -0.091552 | 0.25635 | -0.054931 | 1.0803 | 122.7127 | 0.045777 | 0.073242 | 122.8867 | 122.8958 | 122.8271 | 122.8592 | -122.9004 | -122.8775 | 122.6532 | 0.036621 | 2.2934 | 1.1444
1419.1719 | 123.0286 | -57.2067 | 65.6616 | -0.060578 | 0.00083526 | 0.065443 | 0.073958 | -0.0021896 | 0.0049689 | 0.0071308 | 0.001709 | 0.0025975 | 0.00085443 | -0.00058098 | -0.0012925 | -0.0019483 | 0.0015209 | -54.8859 | 65.6525 | -57.1884 | 65.3275 | -56.131 | -56.8039 | -55.9479 | -56.0394 | 65.6662 | -57.2159 | -57.1609 | -57.1701 | -57.3029 | -56.9916 | 0.01831 | -0.009155 | -0.33417 | 1.0757 | 1.2589 | 0.40283 | 1.2405 | 0.38452 | -0.009155 | 0.004578 | -122.8226 | 0.036621 | 0.21515 | -0.09613 | 0.2243 | -0.086975 | 1.0574 | 122.5159 | 0.045776 | 0.054931 | 122.8409 | 122.8821 | 122.8592 | 122.8729 | -122.85 | -122.8775 | 122.5342 | 0.045776 | 2.3209 | 1.1673
1420.1719 | 123.0103 | -57.2159 | 65.6525 | -0.052948 | 0.0010489 | 0.064375 | 0.074599 | 0.003151 | 0.0017645 | 0.0069172 | 0.023071 | -0.00060665 | 0.0023498 | 0.0013416 | -0.00065151 | -0.0032301 | 0.0028027 | -54.8813 | 65.6433 | -57.2159 | 65.4465 | -56.1813 | -57.0328 | -56.0486 | -56.0028 | 65.6799 | -57.225 | -57.1518 | -57.1793 | -57.2617 | -56.9687 | 0 | -0.009155 | -0.20599 | 1.0345 | 1.1673 | 0.18311 | 1.1673 | 0.18311 | -0.009156 | 0.027466 | -122.8043 | 0.036621 | 0.24719 | -0.045777 | 0.25635 | -0.036621 | 1.0345 | 122.6624 | 0.045777 | 0.073243 | 122.8592 | 122.905 | 122.8592 | 122.8958 | -122.8683 | -122.8775 | 122.6624 | 0.064087 | 2.3346 | 1.2131
1421.1719 | 123.0011 | -57.1976 | 65.6799 | -0.045319 | -0.00066014 | 0.062239 | 0.076095 | 0.0012284 | 0.0041143 | 0.0094806 | 0.03833 | 0.00046135 | 0.0036316 | 0.0045458 | -0.0010787 | -0.0028027 | 0.00023934 | -54.9271 | 65.6891 | -57.2433 | 65.4144 | -56.2317 | -56.8771 | -55.9708 | -56.1035 | 65.6845 | -57.2205 | -57.1747 | -57.1884 | -57.2891 | -56.9916 | -0.045776 | 0.009155 | -0.2655 | 0.96588 | 1.2268 | 0.32044 | 1.2726 | 0.36621 | -0.022888 | 0.004577 | -122.8546 | 0.009155 | 0.20599 | -0.091553 | 0.22888 | -0.068665 | 1.0117 | 122.6578 | 0.032043 | 0.045776 | 122.9324 | 122.905 | 122.8867 | 122.8821 | -122.9233 | -122.9004 | 122.612 | 0.022888 | 2.2705 | 1.0941
1422.1719 | 122.9507 | -57.1701 | 65.6982 | -0.083466 | -0.00023294 | 0.060744 | 0.074599 | 0.0027238 | 0.0021917 | 0.0086262 | 0.026123 | 0.00046135 | 0.0014954 | 0.0051868 | -0.0010787 | -0.0042981 | -0.00061526 | -54.8904 | 65.6616 | -57.2388 | 65.4007 | -56.218 | -56.868 | -55.9662 | -56.1035 | 65.6937 | -57.2067 | -57.1747 | -57.1976 | -57.2937 | -57.0099 | -0.068665 | -0.036621 | -0.29755 | 0.95215 | 1.2039 | 0.30212 | 1.2726 | 0.37079 | -0.036621 | -0.004577 | -122.8729 | -0.027466 | 0.16022 | -0.1236 | 0.19684 | -0.086975 | 1.0208 | 122.6395 | 0.009155 | 0.032043 | 122.9004 | 122.9004 | 122.8317 | 122.8638 | -122.937 | -122.905 | 122.5708 | -0.004578 | 2.2797 | 1.0666
1423.1719 | 123.0377 | -57.2067 | 65.6754 | -0.045319 | 0.0012625 | 0.062239 | 0.076522 | 0.0012284 | 0.0043281 | 0.0079852 | 0.026123 | 0.0011023 | 0.00064083 | -0.0016492 | -0.0023605 | -0.0019483 | -0.0012561 | -54.895 | 65.6616 | -57.2205 | 65.4236 | -56.2317 | -56.8634 | -55.9525 | -56.0623 | 65.6982 | -57.2159 | -57.1426 | -57.1564 | -57.2708 | -56.9687 | -0.013733 | -0.013733 | -0.25177 | 0.97504 | 1.2543 | 0.34332 | 1.268 | 0.35706 | -0.009155 | 0.022888 | -122.818 | 0.050354 | 0.23804 | -0.064087 | 0.24719 | -0.054932 | 0.98877 | 122.644 | 0.059509 | 0.073242 | 122.8821 | 122.9141 | 122.8683 | 122.905 | -122.8958 | -122.8912 | 122.6303 | 0.064087 | 2.3117 | 1.1444
1424.1719 | 122.9965 | -57.1976 | 65.6982 | -0.045319 | 0.00083526 | 0.064589 | 0.074813 | 0.00037377 | 0.0026191 | 0.010121 | 0.010864 | 0.00088875 | 0.0019226 | -0.00015378 | -0.0017197 | -0.0034437 | 0.00045294 | -54.8721 | 65.6754 | -57.2433 | 65.419 | -56.2363 | -56.868 | -55.9799 | -56.0715 | 65.6891 | -57.2021 | -57.1564 | -57.1564 | -57.2845 | -56.987 | -0.045776 | -0.022888 | -0.27924 | 0.9613 | 1.2177 | 0.32959 | 1.2634 | 0.37537 | -0.004577 | -0.009155 | -122.8546 | 0.041199 | 0.21057 | -0.086975 | 0.21515 | -0.082398 | 1.0071 | 122.6624 | 0.045776 | 0.045776 | 122.9187 | 122.8912 | 122.8729 | 122.8867 | -122.9416 | -122.9004 | 122.6166 | 0.041199 | 2.3254 | 1.1261
1425.1719 | 122.9828 | -57.1747 | 65.6891 | -0.052948 | -0.0013009 | 0.06288 | 0.073531 | -0.0026168 | 0.00048269 | 0.0094806 | 0.026123 | 0.0011023 | 0.0019226 | 0.0032642 | -0.0019333 | -0.0030163 | -0.00082886 | -54.9271 | 65.6845 | -57.225 | 65.419 | -56.2408 | -56.8634 | -55.9662 | -56.1035 | 65.6891 | -57.2433 | -57.193 | -57.1884 | -57.2891 | -56.9916 | -0.050354 | -0.004578 | -0.27008 | 0.93384 | 1.2085 | 0.31128 | 1.2589 | 0.36163 | -0.068664 | 0 | -122.8821 | -0.013733 | 0.18311 | -0.11444 | 0.25177 | -0.045777 | 0.98419 | 122.644 | 0.054931 | 0.050354 | 122.9095 | 122.9324 | 122.8592 | 122.8638 | -122.9141 | -122.9324 | 122.5937 | -0.01831 | 2.2476 | 1.0712
1426.1719 | 123.0148 | -57.1884 | 65.6799 | -0.022431 | 0.00040806 | 0.064375 | 0.076949 | -0.001976 | 0.0030463 | 0.0064898 | 0.029175 | 0.0017431 | 0.001068 | -0.0016492 | -0.0023605 | -0.0015211 | -0.0038197 | -54.9271 | 65.6845 | -57.2342 | 65.4419 | -56.2271 | -56.868 | -55.9662 | -56.0577 | 65.7211 | -57.2159 | -57.1655 | -57.193 | -57.2845 | -56.9687 | -0.045776 | 0.004577 | -0.23804 | 0.9613 | 1.2222 | 0.32043 | 1.268 | 0.36621 | -0.027465 | 0.041198 | -122.8455 | -0.004577 | 0.21973 | -0.09613 | 0.24719 | -0.068665 | 1.0071 | 122.6761 | 0.022888 | 0.050354 | 122.9187 | 122.937 | 122.8729 | 122.9095 | -122.9141 | -122.8958 | 122.6303 | 0.022889 | 2.2614 | 1.1307
1427.1719 | 123.0103 | -57.2021 | 65.6891 | -0.075836 | -0.00023294 | 0.064375 | 0.07524 | -0.0041122 | 0.0017645 | 0.0088398 | 0.029175 | 0.0017431 | 0.0029906 | -0.0052808 | -0.0019333 | -0.0028027 | -0.0023243 | -54.9179 | 65.6479 | -57.2205 | 65.4144 | -56.2271 | -56.868 | -55.9616 | -56.0852 | 65.6937 | -57.2205 | -57.1884 | -57.1747 | -57.2891 | -56.9778 | -0.018311 | -0.041199 | -0.27466 | 0.97504 | 1.2405 | 0.33417 | 1.2588 | 0.35248 | -0.018311 | 0.004578 | -122.8775 | 0.027465 | 0.2243 | -0.086976 | 0.24262 | -0.068665 | 0.99335 | 122.6349 | 0.045776 | 0.032043 | 122.8683 | 122.9141 | 122.85 | 122.8958 | -122.9095 | -122.9095 | 122.6166 | 0.013732 | 2.2842 | 1.1169
1428.1719 | 123.0103 | -57.1838 | 65.7257 | -0.091095 | -0.00023294 | 0.061385 | 0.074172 | 0.00037377 | 0.0032599 | 0.0077716 | 0.050537 | 0.0013159 | -0.0010682 | -0.010835 | 0.0010575 | -0.0036573 | -0.0014697 | -54.9225 | 65.657 | -57.225 | 65.4419 | -56.218 | -56.8726 | -55.957 | -56.1035 | 65.6799 | -57.2113 | -57.193 | -57.1884 | -57.2891 | -57.1106 | -0.041199 | -0.068665 | -0.28381 | 0.96588 | 1.2268 | 0.31128 | 1.268 | 0.35248 | -0.027466 | -0.045776 | -122.9187 | -0.004578 | 0.073242 | -0.10529 | 0.10071 | -0.07782 | 1.0071 | 122.6669 | 0.022888 | 0.018311 | 122.8821 | 122.8912 | 122.8409 | 122.8638 | -122.9507 | -122.937 | 122.6257 | -0.009155 | 2.2614 | 1.0803
1429.1719 | 122.9691 | -57.193 | 65.6891 | -0.075836 | -0.0017281 | 0.06288 | 0.071822 | 0.0012284 | -0.00015811 | 0.0071308 | 0.047485 | 3.4148e-05 | 0.003418 | -0.00015378 | -0.00086511 | -0.0021619 | 0.00066654 | -54.895 | 65.6525 | -57.2205 | 65.4419 | -56.1905 | -56.8542 | -55.9479 | -56.0394 | 65.6891 | -57.2113 | -57.1976 | -57.193 | -57.2937 | -57.0007 | -0.027466 | -0.036621 | -0.24719 | 1.0025 | 1.2451 | 0.33875 | 1.2726 | 0.36621 | -0.018311 | 0 | -122.8867 | 0 | 0.19226 | -0.10071 | 0.21057 | -0.082397 | 1.03 | 122.6624 | 0.018311 | 0.013733 | 122.8729 | 122.9004 | 122.8455 | 122.8821 | -122.9095 | -122.9004 | 122.6349 | -0.004578 | 2.298 | 1.1536
1430.1719 | 123.0286 | -57.1884 | 65.6799 | 0.008087 | -0.00087374 | 0.063948 | 0.075667 | 0.0010148 | 0.0026191 | 0.0090534 | 0.0047608 | 3.4148e-05 | 0.0032044 | 0.0036914 | -0.0023605 | -0.0021619 | -0.0012561 | -54.9133 | 65.6845 | -57.2296 | 65.419 | -56.2363 | -56.8634 | -55.9799 | -56.0806 | 65.6799 | -57.2205 | -57.1655 | -57.1747 | -57.2983 | -56.9962 | -0.041198 | 0.004577 | -0.26093 | 0.95215 | 1.2085 | 0.32501 | 1.2497 | 0.36621 | -0.032043 | 0 | -122.8455 | 0.013733 | 0.19226 | -0.10986 | 0.2243 | -0.07782 | 0.99335 | 122.6486 | 0.045776 | 0.054932 | 122.9141 | 122.9004 | 122.8729 | 122.8683 | -122.9095 | -122.9004 | 122.6074 | 0.022889 | 2.2751 | 1.1078
1431.1719 | 122.9736 | -57.1838 | 65.712 | -0.052948 | -0.00044654 | 0.061171 | 0.074172 | -0.00090783 | 0.0039007 | 0.0086262 | 0.035278 | 0.00088875 | 0.00085443 | -0.0014356 | -0.0027877 | -0.0036573 | -0.0025379 | -54.9133 | 65.6754 | -57.2388 | 65.4236 | -56.2225 | -56.8726 | -55.9708 | -56.0715 | 65.6891 | -57.225 | -57.193 | -57.1884 | -57.3029 | -57.0145 | -0.054932 | -0.036621 | -0.28839 | 0.9613 | 1.2131 | 0.31128 | 1.268 | 0.36621 | -0.041199 | -0.022888 | -122.905 | -0.004578 | 0.16937 | -0.11902 | 0.21057 | -0.077819 | 1.0162 | 122.6624 | 0.036621 | 0.032044 | 122.9141 | 122.9141 | 122.8592 | 122.8729 | -122.9507 | -122.937 | 122.6074 | -0.009155 | 2.2705 | 1.1124
1432.1719 | 122.9645 | -57.2067 | 65.6754 | -0.045319 | 0.0021171 | 0.063307 | 0.074386 | -0.0013352 | 0.0019781 | 0.010976 | 0.068848 | 0.0019567 | 0.00085443 | 0.0026232 | -0.0010787 | -0.0032301 | -0.0016833 | -54.8859 | 65.6342 | -57.225 | 65.4419 | -56.2088 | -56.8405 | -55.9296 | -56.0394 | 65.6982 | -57.2159 | -57.1976 | -57.1838 | -57.2937 | -57.0282 | -0.018311 | -0.041199 | -0.23346 | 0.99793 | 1.2772 | 0.36621 | 1.2955 | 0.38452 | -0.009155 | 0.022888 | -122.8729 | 0.022888 | 0.17853 | -0.086975 | 0.18768 | -0.07782 | 1.0162 | 122.6669 | 0.032043 | 0.01831 | 122.8592 | 122.9141 | 122.8409 | 122.905 | -122.9004 | -122.8912 | 122.6486 | 0.009155 | 2.3209 | 1.1673
1433.1719 | 122.9736 | -57.1884 | 65.6891 | -0.037689 | 0.00019446 | 0.064375 | 0.074599 | -0.00048063 | 0.0019781 | 0.0069172 | 0.016968 | 0.0013159 | 0.0021362 | -0.0037854 | -0.00043791 | -0.00045288 | 0.0015209 | -54.9362 | 65.6891 | -57.2342 | 65.4282 | -56.2225 | -56.8771 | -55.9662 | -56.0577 | 65.7257 | -57.2159 | -57.312 | -57.1747 | -57.312 | -57.0328 | -0.045776 | 0 | -0.26093 | 0.96588 | 1.2222 | 0.31128 | 1.268 | 0.35706 | -0.027465 | 0.036621 | -123.0011 | 0.013733 | 0.15564 | -0.1236 | 0.18311 | -0.096131 | 1.0117 | 122.6624 | 0.041198 | -0.096131 | 122.9233 | 122.9416 | 122.8775 | 122.9141 | -122.9233 | -122.905 | 122.6166 | -0.1236 | 2.2522 | 1.1307
1434.1719 | 122.9828 | -57.1793 | 65.7074 | -0.052948 | 0.0016899 | 0.061171 | 0.07524 | -0.0021896 | 0.0017645 | 0.0079852 | 0.032227 | 0.00088875 | -0.0010682 | -0.0037854 | -0.0019333 | -0.0053663 | 2.554e-05 | -54.9316 | 65.6708 | -57.2342 | 65.4465 | -56.2317 | -56.8771 | -55.9662 | -56.0715 | 65.6845 | -57.2205 | -57.193 | -57.1793 | -57.2983 | -57.019 | -0.054932 | -0.036621 | -0.26093 | 0.94757 | 1.2131 | 0.30212 | 1.268 | 0.35706 | -0.041199 | -0.022888 | -122.9004 | 0 | 0.16022 | -0.11902 | 0.20142 | -0.07782 | 1.0025 | 122.6807 | 0.041199 | 0.027466 | 122.905 | 122.905 | 122.85 | 122.8638 | -122.9416 | -122.9279 | 122.6257 | -0.013733 | 2.2476 | 1.1078
1435.1719 | 122.9507 | -57.193 | 65.6891 | -0.03006 | -1.9142e-05 | 0.063734 | 0.072677 | -0.00069423 | 0.00069649 | 0.0077716 | 0.029175 | 3.4148e-05 | 0.001068 | -0.0020764 | -0.0015061 | -0.0013073 | -0.0014697 | -54.8767 | 65.6296 | -57.225 | 65.4648 | -56.1996 | -56.8497 | -55.957 | -56.0257 | 65.6982 | -57.1884 | -57.1838 | -57.193 | -57.3029 | -57.0145 | -0.032044 | -0.059509 | -0.2243 | 0.99335 | 1.236 | 0.34332 | 1.268 | 0.37537 | 0.004577 | 0.009155 | -122.8729 | 0 | 0.17853 | -0.10986 | 0.17395 | -0.11444 | 1.0254 | 122.6898 | -0.004577 | 0.004578 | 122.8546 | 122.8867 | 122.8226 | 122.8912 | -122.9141 | -122.8775 | 122.6578 | 0.009155 | 2.3163 | 1.1673
1436.1719 | 123.0469 | -57.1701 | 65.6891 | -0.083466 | -0.00066014 | 0.062025 | 0.073958 | -0.0021896 | 0.0015509 | 0.0094806 | 0.050537 | 0.0023839 | -0.0012818 | 0.002196 | -0.0030013 | -0.0032301 | -0.0012561 | -54.9042 | 65.5838 | -57.2113 | 65.5472 | -56.1127 | -56.7627 | -55.8517 | -55.9387 | 65.6433 | -57.2021 | -57.1106 | -57.074 | -57.193 | -56.9183 | -0.041199 | -0.10529 | -0.14191 | 1.0574 | 1.3184 | 0.40741 | 1.3596 | 0.44861 | -0.032043 | -0.045776 | -122.7997 | 0.09613 | 0.25177 | -0.022888 | 0.28381 | 0.009155 | 1.0986 | 122.7585 | 0.12817 | 0.091552 | 122.7951 | 122.8455 | 122.7539 | 122.8134 | -122.9004 | -122.8912 | 122.7173 | 0.059509 | 2.2659 | 1.2314
1437.1719 | 122.9736 | -57.2021 | 65.7028 | -0.068207 | 0.0025443 | 0.063094 | 0.075667 | -0.0030442 | 0.0039007 | 0.010121 | 0.0047608 | -0.00082025 | 0.00085443 | -0.001222 | -0.00022431 | -0.0045117 | -0.0012561 | -54.9225 | 65.6708 | -57.225 | 65.4373 | -56.2225 | -56.8726 | -55.9525 | -56.0532 | 65.7166 | -57.2067 | -57.1976 | -57.1838 | -57.3074 | -57.0282 | -0.022889 | -0.032044 | -0.2655 | 0.97961 | 1.2497 | 0.32959 | 1.2726 | 0.35248 | -0.004578 | 0.013733 | -122.9004 | 0.01831 | 0.17395 | -0.10529 | 0.17853 | -0.10071 | 1.0025 | 122.6624 | 0.022888 | 0.009155 | 122.8958 | 122.9233 | 122.8729 | 122.9187 | -122.9279 | -122.9095 | 122.6395 | 0.004577 | 2.2797 | 1.149
1438.1719 | 123.0515 | -57.1655 | 65.6708 | -0.098725 | -0.00087374 | 0.063307 | 0.074172 | -0.0032578 | 0.0021917 | 0.0096942 | 0.035278 | -0.00060665 | -0.0012818 | 0.00070062 | -0.0010787 | -0.0045117 | -0.00040166 | -54.8721 | 65.6342 | -57.225 | 65.5151 | -56.1218 | -56.7902 | -55.8746 | -55.9433 | 65.6525 | -57.2113 | -57.1198 | -57.1106 | -57.2067 | -56.9412 | -0.05951 | -0.036621 | -0.15564 | 1.0437 | 1.2909 | 0.37537 | 1.3504 | 0.43488 | -0.045777 | -0.01831 | -122.7905 | 0.054931 | 0.2243 | -0.041199 | 0.27008 | 0.004578 | 1.1032 | 122.7402 | 0.10071 | 0.091553 | 122.8592 | 122.8638 | 122.7997 | 122.818 | -122.8958 | -122.8821 | 122.6807 | 0.045776 | 2.2934 | 1.2222
1439.1719 | 122.9965 | -57.1976 | 65.6616 | 0.00045798 | -0.0023691 | 0.060316 | 0.07524 | -0.00069423 | 0.0021917 | 0.0064898 | -0.0013428 | 0.0011023 | -0.0010682 | 0.0058276 | -0.0030013 | -0.0028027 | 0.00023934 | -54.9225 | 65.657 | -57.2479 | 65.419 | -56.2363 | -56.8726 | -55.9845 | -56.0486 | 65.7349 | -57.1976 | -57.1747 | -57.2479 | -57.3303 | -57.0328 | -0.050354 | -0.004578 | -0.24262 | 0.9613 | 1.2131 | 0.32501 | 1.2634 | 0.37537 | 0 | 0.073242 | -122.8363 | -0.050354 | 0.1648 | -0.13275 | 0.1648 | -0.13275 | 1.0117 | 122.6669 | -0.050354 | 0.022888 | 122.905 | 122.9324 | 122.8546 | 122.9324 | -122.9095 | -122.8592 | 122.6166 | 0.022888 | 2.2751 | 1.149
1440.1719 | 123.024 | -57.1747 | 65.6616 | -0.068207 | 0.00062166 | 0.063521 | 0.074813 | -0.00026703 | 5.5488e-05 | 0.0081988 | 0.016968 | 0.00067495 | -0.0012818 | 0.0049732 | -0.0012925 | -0.0025891 | 0.0010937 | -54.863 | 65.6296 | -57.2113 | 65.506 | -56.1539 | -56.813 | -55.8838 | -55.9891 | 65.6982 | -57.1976 | -57.1655 | -57.1426 | -57.2662 | -56.9733 | -0.036621 | -0.032043 | -0.15564 | 1.0208 | 1.2909 | 0.36163 | 1.3275 | 0.39825 | -0.022888 | 0.036621 | -122.8271 | 0.032044 | 0.20142 | -0.091552 | 0.2243 | -0.068664 | 1.0574 | 122.7173 | 0.054932 | 0.032044 | 122.8409 | 122.8958 | 122.8043 | 122.8729 | -122.8729 | -122.8592 | 122.6807 | 0.009156 | 2.3117 | 1.1856
1441.1719 | 123.0423 | -57.1793 | 65.6662 | -0.098725 | 0.00040806 | 0.064162 | 0.076308 | 0.00251 | 0.00091009 | 0.009267 | 0.026123 | 0.00067495 | 0.00021363 | -0.0076306 | -0.0027877 | -0.0038709 | 2.554e-05 | -54.8676 | 65.6158 | -57.2067 | 65.5197 | -56.1401 | -56.7902 | -55.8975 | -55.9845 | 65.6662 | -57.193 | -57.1152 | -57.1198 | -57.2342 | -56.9504 | -0.027466 | -0.050354 | -0.14649 | 1.0391 | 1.2817 | 0.3891 | 1.3092 | 0.41657 | -0.013733 | 0 | -122.7814 | 0.059509 | 0.22888 | -0.054932 | 0.24262 | -0.041199 | 1.0666 | 122.7264 | 0.073242 | 0.07782 | 122.8226 | 122.8592 | 122.7951 | 122.8455 | -122.8729 | -122.8592 | 122.699 | 0.064087 | 2.3117 | 1.1948
1442.1719 | 123.0789 | -57.1564 | 65.6387 | -0.037689 | -0.00044654 | 0.061385 | 0.074599 | -0.00026703 | 0.0053961 | 0.007558 | 0.03833 | -0.00060665 | 0.00064083 | -0.0027174 | -0.00065151 | -0.0034437 | 0.00023934 | -54.8538 | 65.6113 | -57.1884 | 65.5334 | -56.0898 | -56.781 | -55.8838 | -55.7098 | 65.6799 | -57.1472 | -57.0786 | -57.1472 | -57.1838 | -56.9092 | -0.032044 | -0.027466 | -0.10529 | 1.0666 | 1.2726 | 0.37537 | 1.3046 | 0.40741 | 0.009155 | 0.041199 | -122.7173 | 0.009155 | 0.24719 | -0.027466 | 0.23804 | -0.036621 | 1.0986 | 122.7219 | 0 | 0.068665 | 122.7997 | 122.8271 | 122.7676 | 122.8363 | -122.8271 | -122.7859 | 122.6898 | 0.07782 | 2.3026 | 1.4465
1443.1719 | 123.056 | -57.1564 | 65.6479 | -0.068207 | 0.0031851 | 0.06288 | 0.074813 | 0.0020828 | 0.0032599 | 0.011403 | 0.029175 | 0.00067495 | -0.0025636 | -0.001222 | -0.0023605 | -0.0028027 | -0.0023243 | -54.8721 | 65.6067 | -57.225 | 65.5243 | -56.1401 | -56.781 | -55.8975 | -55.9204 | 65.657 | -57.2067 | -57.1106 | -57.0969 | -57.1884 | -56.9229 | -0.068665 | -0.041199 | -0.1236 | 1.0162 | 1.2588 | 0.37537 | 1.3275 | 0.44403 | -0.050354 | 0.009155 | -122.7585 | 0.059509 | 0.23346 | -0.032044 | 0.28381 | 0.01831 | 1.0849 | 122.7493 | 0.10986 | 0.09613 | 122.8317 | 122.8638 | 122.7631 | 122.8134 | -122.8729 | -122.8546 | 122.6807 | 0.045776 | 2.2842 | 1.236
1444.1719 | 123.0743 | -57.1793 | 65.6479 | -0.18265 | -0.0017281 | 0.065657 | 0.075454 | 0.00058737 | 0.0032599 | 0.0086262 | 0.03833 | -0.00017945 | 0.001068 | 0.0045458 | -0.0032151 | -0.0028027 | 2.554e-05 | -54.8584 | 65.6067 | -57.2433 | 65.5563 | -56.1218 | -56.7673 | -55.8838 | -55.9204 | 65.6433 | -57.193 | -57.0969 | -57.0923 | -57.1838 | -56.9366 | -0.064087 | -0.041199 | -0.091553 | 1.0574 | 1.2955 | 0.41199 | 1.3596 | 0.47607 | -0.013733 | -0.004577 | -122.7448 | 0.086975 | 0.24261 | -0.004578 | 0.25635 | 0.009155 | 1.1215 | 122.7997 | 0.10071 | 0.09613 | 122.85 | 122.8363 | 122.7859 | 122.8226 | -122.8912 | -122.8409 | 122.7356 | 0.082397 | 2.3209 | 1.2589
1445.1719 | 123.0148 | -57.1976 | 65.6754 | -0.068207 | -0.0013009 | 0.063307 | 0.075454 | -0.00069423 | 0.0043281 | 0.0094806 | 0.013916 | 0.00088875 | 0.00042723 | 0.0017688 | -0.0036423 | -0.0021619 | -0.00018806 | -54.8813 | 65.6296 | -57.2205 | 65.5014 | -56.1493 | -56.8176 | -55.9067 | -55.9799 | 65.6891 | -57.1747 | -57.1564 | -57.1701 | -57.2433 | -56.9595 | -0.022888 | -0.045776 | -0.17395 | 1.0483 | 1.2909 | 0.37994 | 1.3138 | 0.40283 | 0.022888 | 0.013733 | -122.8317 | 0.027466 | 0.23804 | -0.045776 | 0.21515 | -0.068664 | 1.0712 | 122.7219 | 0.004578 | 0.018311 | 122.85 | 122.8638 | 122.8271 | 122.8867 | -122.8958 | -122.85 | 122.699 | 0.041199 | 2.3163 | 1.2177
1446.1719 | 122.9462 | -57.2571 | 65.6754 | -0.060578 | 0.00019446 | 0.065443 | 0.078231 | 0.00080117 | 0.0032599 | 0.0090534 | -0.08374 | 0.0019567 | -0.00042717 | -0.0050672 | -0.0034287 | -0.0023755 | -0.00082886 | -54.9545 | 65.6067 | -57.2845 | 65.387 | -56.2683 | -56.9366 | -56.0349 | -56.0898 | 65.6708 | -57.2754 | -57.2159 | -57.2617 | -57.3944 | -57.0374 | -0.027466 | -0.068665 | -0.28839 | 0.98877 | 1.2222 | 0.32043 | 1.2497 | 0.3479 | -0.018311 | -0.004578 | -122.8912 | -0.004578 | 0.21973 | -0.13733 | 0.23804 | -0.11902 | 1.0162 | 122.6715 | 0.013733 | 0.05951 | 122.8912 | 122.9462 | 122.8638 | 122.9279 | -122.9599 | -122.9507 | 122.644 | 0.041199 | 2.3026 | 1.1673
1447.1719 | 123.0835 | -57.1976 | 65.6525 | -0.083466 | 0.0012625 | 0.060957 | 0.073104 | -0.0021896 | 0.0030463 | 0.010335 | 0.02002 | 3.4148e-05 | -0.00021357 | -0.0033582 | -0.00086511 | -0.0028027 | -0.00040166 | -54.8859 | 65.6296 | -57.2159 | 65.5334 | -56.1356 | -56.8039 | -55.8929 | -55.9525 | 65.6799 | -57.2113 | -57.1152 | -57.1152 | -57.225 | -56.9366 | -0.01831 | -0.022888 | -0.11902 | 1.062 | 1.3046 | 0.39368 | 1.3229 | 0.41199 | -0.013733 | 0.027466 | -122.7676 | 0.082398 | 0.26093 | -0.027466 | 0.27466 | -0.013733 | 1.0803 | 122.7493 | 0.096131 | 0.096131 | 122.8455 | 122.8912 | 122.8271 | 122.8775 | -122.8683 | -122.8638 | 122.731 | 0.082398 | 2.3117 | 1.2451
1448.1719 | 122.9828 | -57.2067 | 65.6708 | -0.068207 | 0.00040806 | 0.063307 | 0.075667 | -0.0013352 | 0.0045417 | 0.0049946 | -0.016602 | 0.0021703 | 2.8e-08 | -0.0035718 | 0.00084389 | -0.0049389 | 0.0057935 | -54.895 | 65.6387 | -57.2067 | 65.4602 | -56.2042 | -56.8542 | -55.9753 | -56.0257 | 65.6799 | -57.225 | -57.2021 | -57.1976 | -57.3074 | -57.0236 | 0 | -0.032043 | -0.21057 | 1.0025 | 1.2314 | 0.35248 | 1.2314 | 0.35248 | -0.018311 | 0.009156 | -122.8729 | 0.009155 | 0.18311 | -0.10071 | 0.20142 | -0.082397 | 1.0025 | 122.6669 | 0.027466 | 0.022889 | 122.8455 | 122.905 | 122.8455 | 122.8867 | -122.8775 | -122.8958 | 122.6669 | 0.004578 | 2.3117 | 1.181
1449.1719 | 123.0057 | -57.1701 | 65.5975 | -0.075836 | 0.00062166 | 0.064162 | 0.07289 | -0.0013352 | 0.0028327 | 0.0094806 | 0.023071 | 0.0030249 | 0.00085443 | 0.0026232 | -0.0030013 | -0.0049389 | -0.0033923 | -54.8721 | 65.6113 | -57.225 | 65.538 | -56.0944 | -56.7627 | -55.8609 | -55.9021 | 65.6387 | -57.1976 | -57.2296 | -56.7719 | -57.0053 | -56.9366 | -0.054932 | 0.013733 | -0.059509 | 1.0757 | 1.3092 | 0.40741 | 1.3641 | 0.46234 | -0.027466 | 0.041199 | -122.8271 | 0.39825 | 0.23346 | 0.16479 | 0.26093 | 0.19226 | 1.1307 | 122.7631 | 0.42572 | -0.032043 | 122.8363 | 122.8363 | 122.7814 | 122.8088 | -122.8226 | -122.7951 | 122.7081 | -0.059509 | 2.298 | 1.268
1450.1719 | 123.1888 | -57.1655 | 65.7303 | -0.03006 | 0.0025443 | 0.062666 | 0.07524 | 0.00037377 | 0.0015509 | 0.0077716 | 0.03833 | 0.00088875 | 0.001709 | -0.0059216 | -0.0021469 | -0.0040845 | -0.0023243 | -54.895 | 65.5884 | -57.2113 | 65.5426 | -56.0989 | -56.7535 | -55.8517 | -55.8838 | 65.6433 | -57.2113 | -57.0923 | -57.0694 | -57.1564 | -57.0145 | -0.045777 | -0.14191 | -0.18768 | 1.0666 | 1.3138 | 0.41199 | 1.3596 | 0.45776 | -0.045777 | -0.086975 | -122.8226 | 0.09613 | 0.15106 | 0.009155 | 0.19684 | 0.054932 | 1.1124 | 122.7539 | 0.14191 | 0.11902 | 122.7997 | 122.8546 | 122.7539 | 122.8088 | -122.9416 | -122.9416 | 122.7081 | 0.073242 | 2.2705 | 1.2817
1451.1719 | 122.9279 | -57.2525 | 65.6433 | -0.16739 | 0.0014761 | 0.065443 | 0.077804 | 0.003151 | 0.0034735 | 0.010762 | -0.077637 | 0.00067495 | 0.001068 | -0.00058098 | -0.0032151 | -0.0017347 | -0.0016833 | -54.9683 | 65.6067 | -57.3074 | 65.3824 | -56.3049 | -56.987 | -56.0761 | -56.1172 | 65.6754 | -57.2479 | -57.2388 | -57.2937 | -57.4081 | -57.0648 | -0.054932 | -0.036622 | -0.26093 | 0.94757 | 1.1765 | 0.2655 | 1.2314 | 0.32043 | 0.004577 | 0.032043 | -122.8821 | -0.041199 | 0.18768 | -0.15564 | 0.18311 | -0.16022 | 1.0025 | 122.6898 | -0.045776 | 0.009155 | 122.9141 | 122.9233 | 122.8592 | 122.9279 | -122.9507 | -122.8912 | 122.6349 | 0.013732 | 2.2842 | 1.1353
1452.1719 | 122.9965 | -57.193 | 65.6662 | -0.037689 | 0.00019446 | 0.064589 | 0.073958 | -0.0021896 | 0.0028327 | 0.01119 | 0.013916 | 0.0013159 | -0.0012818 | 0.0028368 | -0.0012925 | -0.0049389 | -0.00061526 | -54.8904 | 65.6204 | -57.2159 | 65.4922 | -56.1722 | -56.8176 | -55.9204 | -55.9708 | 65.6891 | -57.2342 | -57.1655 | -57.1564 | -57.2571 | -56.9916 | -0.022888 | -0.045777 | -0.17395 | 1.0208 | 1.2726 | 0.37537 | 1.2955 | 0.39825 | -0.041199 | 0.022888 | -122.8317 | 0.036621 | 0.20142 | -0.064087 | 0.24262 | -0.022888 | 1.0437 | 122.7081 | 0.07782 | 0.068665 | 122.8363 | 122.9233 | 122.8134 | 122.8821 | -122.8821 | -122.9004 | 122.6852 | 0.027466 | 2.3026 | 1.2222
1453.1719 | 123.0423 | -57.1976 | 65.6708 | -0.037689 | 0.00083526 | 0.063094 | 0.074599 | -0.00026703 | 0.0030463 | 0.0079852 | 0.026123 | -0.0014613 | -0.0010682 | -0.00015378 | -0.00065151 | -0.0015211 | -0.0021107 | -54.8904 | 65.625 | -57.2296 | 65.5106 | -56.1676 | -56.7993 | -55.9204 | -55.9662 | 65.6525 | -57.2113 | -57.1426 | -57.1289 | -57.2433 | -56.955 | -0.032043 | -0.045776 | -0.16022 | 1.03 | 1.2772 | 0.39826 | 1.3092 | 0.4303 | -0.013733 | -0.01831 | -122.8134 | 0.068665 | 0.24262 | -0.045776 | 0.25635 | -0.032043 | 1.062 | 122.7402 | 0.082398 | 0.068665 | 122.8546 | 122.8638 | 122.8226 | 122.85 | -122.9004 | -122.8821 | 122.7081 | 0.054932 | 2.3071 | 1.2314
1454.1719 | 123.024 | -57.1793 | 65.6616 | -0.060578 | 0.0012625 | 0.062666 | 0.073531 | -0.0017624 | 0.0024053 | 0.009267 | 0.02002 | 0.00067495 | 0.00021363 | -0.0033582 | -0.0012925 | -0.0040845 | -0.0014697 | -54.8859 | 65.6067 | -57.1884 | 65.506 | -56.131 | -56.8085 | -55.8929 | -55.957 | 65.6479 | -57.2067 | -57.1335 | -57.1289 | -57.2388 | -56.9595 | -0.009156 | -0.054932 | -0.15564 | 1.0483 | 1.2863 | 0.37079 | 1.2955 | 0.37994 | -0.027466 | -0.013733 | -122.7951 | 0.050354 | 0.21973 | -0.05951 | 0.24719 | -0.032044 | 1.0574 | 122.6944 | 0.07782 | 0.073242 | 122.7951 | 122.8546 | 122.7859 | 122.8271 | -122.85 | -122.8683 | 122.6852 | 0.045776 | 2.2934 | 1.2222
1455.1719 | 122.9599 | -57.1976 | 65.6799 | -0.083466 | 0.00040806 | 0.06288 | 0.074172 | 0.0012284 | 0.0032599 | 0.0088398 | 0.0078126 | 0.00067495 | 0.00021363 | -0.0033582 | -0.0010787 | -0.0038709 | -0.0021107 | -54.9179 | 65.6342 | -57.2433 | 65.4327 | -56.2134 | -56.8542 | -55.9708 | -56.0257 | 65.6937 | -57.225 | -57.1884 | -57.2113 | -57.2983 | -57.0053 | -0.045776 | -0.045777 | -0.24719 | 0.98419 | 1.2268 | 0.34332 | 1.2726 | 0.3891 | -0.027466 | 0.013733 | -122.8683 | -0.013733 | 0.19226 | -0.10071 | 0.21973 | -0.073242 | 1.03 | 122.6761 | 0.013733 | 0.036621 | 122.8775 | 122.9187 | 122.8317 | 122.8912 | -122.9233 | -122.905 | 122.6303 | 0.009155 | 2.2797 | 1.1719
1456.1719 | 122.9736 | -57.2296 | 65.6479 | -0.12161 | 0.0014761 | 0.064589 | 0.077376 | 0.0018692 | 0.0026191 | 0.0088398 | -0.053223 | 0.0023839 | 0.0019226 | 0.0058276 | -0.0023605 | -0.0015211 | 0.0036571 | -54.9774 | 65.6158 | -57.2983 | 65.3595 | -56.3461 | -56.9916 | -56.0761 | -56.1584 | 65.6479 | -57.2891 | -57.2159 | -57.2662 | -57.3898 | -57.0602 | -0.068665 | -0.032043 | -0.28839 | 0.88348 | 1.1536 | 0.23804 | 1.2222 | 0.3067 | -0.05951 | 0 | -122.8638 | -0.036621 | 0.16937 | -0.16022 | 0.22888 | -0.10071 | 0.95215 | 122.6578 | 0.022889 | 0.073243 | 122.9141 | 122.937 | 122.8455 | 122.8775 | -122.9462 | -122.937 | 122.5891 | 0.013733 | 2.2522 | 1.0712
1457.1719 | 123.024 | -57.1747 | 65.6479 | -0.075836 | 0.0019035 | 0.064375 | 0.07225 | -0.0030442 | 0.0032599 | 0.0073444 | 0.035278 | 0.0013159 | -0.00021357 | 0.00027342 | -0.0012925 | -0.0028027 | -0.00040166 | -54.8904 | 65.6113 | -57.2205 | 65.5106 | -56.1584 | -56.7947 | -55.8975 | -55.9433 | 65.657 | -57.2067 | -57.1152 | -57.106 | -57.1976 | -56.9321 | -0.045776 | -0.036621 | -0.13733 | 1.0162 | 1.2772 | 0.37994 | 1.3229 | 0.42572 | -0.032043 | 0.009155 | -122.7631 | 0.068665 | 0.24262 | -0.022888 | 0.27466 | 0.009155 | 1.062 | 122.731 | 0.10071 | 0.091553 | 122.8317 | 122.8638 | 122.7859 | 122.8317 | -122.8683 | -122.8546 | 122.6852 | 0.05951 | 2.2842 | 1.2314
1458.1719 | 122.9691 | -57.193 | 65.6616 | -0.060578 | 0.0025443 | 0.063948 | 0.073531 | 0.001442 | 0.0032599 | 0.0096942 | 0.010864 | 0.00067495 | -0.00064077 | -0.0042126 | -0.00065151 | -0.0019483 | 0.0017345 | -54.895 | 65.6616 | -57.2205 | 65.4648 | -56.1905 | -56.8405 | -55.9296 | -56.0165 | 65.6754 | -57.2388 | -57.1793 | -57.1609 | -57.2937 | -57.0053 | -0.027466 | 0 | -0.19684 | 1.0025 | 1.2634 | 0.35248 | 1.2909 | 0.37994 | -0.045777 | 0.013733 | -122.8409 | 0.032043 | 0.18768 | -0.10071 | 0.23346 | -0.054931 | 1.03 | 122.6852 | 0.07782 | 0.05951 | 122.8821 | 122.9141 | 122.8546 | 122.8683 | -122.8821 | -122.9004 | 122.6578 | 0.013733 | 2.298 | 1.1765
1459.1719 | 122.9782 | -57.193 | 65.6479 | -0.10635 | 0.0014761 | 0.063094 | 0.073958 | 0.00058737 | 0.0024053 | 0.0060626 | 0.010864 | -0.00017945 | 0.0012818 | 5.9824e-05 | -0.00086511 | -0.0017347 | -0.0016833 | -54.8996 | 65.6158 | -57.225 | 65.4694 | -56.1813 | -56.8268 | -55.9341 | -55.9799 | 65.6662 | -57.2296 | -57.1609 | -57.1793 | -57.2845 | -57.0053 | -0.032044 | -0.032043 | -0.17853 | 1.0117 | 1.2589 | 0.36621 | 1.2909 | 0.39825 | -0.036621 | 0.018311 | -122.8088 | 0.013733 | 0.18768 | -0.091553 | 0.2243 | -0.054932 | 1.0437 | 122.6944 | 0.050354 | 0.068664 | 122.8409 | 122.8958 | 122.8088 | 122.8592 | -122.8729 | -122.8775 | 122.6624 | 0.032043 | 2.2934 | 1.2131
1460.1719 | 122.9507 | -57.2159 | 65.6845 | -0.068207 | -0.00044654 | 0.061598 | 0.074386 | 0.00058737 | 0.0011237 | 0.010762 | 0.0078126 | 0.0023839 | 0.00085443 | 0.002196 | -0.0019333 | -0.0030163 | 0.00066654 | -54.9362 | 65.6296 | -57.2388 | 65.419 | -56.2592 | -56.8909 | -55.9982 | -56.044 | 65.7074 | -57.2479 | -57.2067 | -57.2159 | -57.3212 | -57.019 | -0.022889 | -0.054931 | -0.2655 | 0.95673 | 1.2177 | 0.32501 | 1.2405 | 0.3479 | -0.032044 | 0.022888 | -122.8912 | 0 | 0.19684 | -0.10529 | 0.22888 | -0.073242 | 0.97962 | 122.6578 | 0.032044 | 0.041199 | 122.8683 | 122.9553 | 122.8455 | 122.9233 | -122.9233 | -122.9324 | 122.6349 | 0.009155 | 2.2797 | 1.1719
1461.1719 | 122.9691 | -57.2113 | 65.6937 | -0.052948 | 0.00083526 | 0.061812 | 0.073104 | -0.0024032 | 0.0017645 | 0.010549 | 0.0078126 | 0.0025975 | 0.00042723 | 0.00027342 | -0.00086511 | -0.0040845 | -0.00018806 | -54.9225 | 65.6616 | -57.2388 | 65.4282 | -56.2592 | -56.8817 | -55.9799 | -56.044 | 65.6754 | -57.2342 | -57.1838 | -57.193 | -57.2937 | -57.0282 | -0.027466 | -0.032044 | -0.2655 | 0.95215 | 1.2314 | 0.32959 | 1.2589 | 0.35706 | -0.022888 | -0.018311 | -122.8775 | 0.018311 | 0.18311 | -0.082397 | 0.20599 | -0.059509 | 0.97962 | 122.6669 | 0.041199 | 0.050354 | 122.9004 | 122.9095 | 122.8729 | 122.8867 | -122.9324 | -122.9279 | 122.6395 | 0.027466 | 2.2888 | 1.1673
1462.1719 | 123.0469 | -57.1655 | 65.6387 | -0.045319 | 0.0012625 | 0.062239 | 0.073531 | 0.00080117 | 0.0032599 | 0.0079852 | 0.02002 | 0.00024775 | 0.0012818 | -0.0020764 | -0.0012925 | -0.0025891 | -0.0012561 | -54.8996 | 65.6113 | -57.2205 | 65.506 | -56.1584 | -56.7902 | -55.9021 | -55.9479 | 65.6754 | -57.2296 | -57.1152 | -57.106 | -57.2159 | -56.9458 | -0.054932 | -0.027466 | -0.13275 | 1.0071 | 1.2634 | 0.37537 | 1.3184 | 0.4303 | -0.064087 | 0.036621 | -122.7539 | 0.059509 | 0.21973 | -0.050354 | 0.28381 | 0.013733 | 1.062 | 122.7264 | 0.1236 | 0.11444 | 122.8317 | 122.905 | 122.7768 | 122.8409 | -122.8592 | -122.8683 | 122.6715 | 0.050354 | 2.2659 | 1.2177
1463.1719 | 122.9599 | -57.1884 | 65.593 | -0.11398 | -1.9142e-05 | 0.064375 | 0.073958 | 0.00037377 | 0.0030463 | 0.0079852 | 0.059692 | 0.0019567 | 0.001068 | -0.0054944 | 0.00020289 | -0.0023755 | 0.00066654 | -54.8813 | 65.6296 | -57.2113 | 65.5472 | -56.1035 | -56.7627 | -55.8609 | -55.8975 | 65.6296 | -57.2296 | -57.2296 | -56.7947 | -56.955 | -56.9046 | -0.022888 | 0.036621 | -0.045777 | 1.0849 | 1.3275 | 0.42572 | 1.3504 | 0.44861 | -0.041198 | 0.036621 | -122.8226 | 0.39368 | 0.28381 | 0.23346 | 0.32501 | 0.27466 | 1.1078 | 122.7585 | 0.43487 | 0 | 122.8409 | 122.8592 | 122.818 | 122.818 | -122.8043 | -122.8226 | 122.7356 | -0.041198 | 2.3071 | 1.2909
1464.1719 | 123.1247 | -57.1655 | 65.657 | -0.10635 | 0.00040806 | 0.062453 | 0.071181 | 0.0012284 | 0.0030463 | 0.010335 | 0.056641 | 3.4148e-05 | -0.0012818 | -0.00036738 | -0.0025741 | -0.0036573 | 0.00088014 | -54.895 | 65.5746 | -57.2067 | 65.538 | -56.1127 | -56.7673 | -55.8517 | -55.8517 | 65.6387 | -57.2021 | -57.0923 | -57.0831 | -57.1793 | -56.9229 | -0.041199 | -0.082397 | -0.11902 | 1.0529 | 1.3138 | 0.39825 | 1.355 | 0.43945 | -0.036621 | -0.01831 | -122.7493 | 0.082397 | 0.24261 | -0.013733 | 0.27923 | 0.022888 | 1.0941 | 122.7448 | 0.11902 | 0.10986 | 122.7814 | 122.8409 | 122.7402 | 122.8043 | -122.8638 | -122.8592 | 122.7036 | 0.073242 | 2.2705 | 1.3138
1465.1719 | 123.0606 | -57.1838 | 65.6067 | 0.09964 | 0.0014761 | 0.066298 | 0.073958 | -0.0051804 | 0.0034735 | 0.0094806 | -0.0013428 | 0.00046135 | 0.001068 | 0.0019824 | -0.0023605 | -0.0034437 | 0.0010937 | -55.1056 | 65.6021 | -57.2021 | 65.5197 | -56.163 | -56.7993 | -55.8701 | -55.8929 | 65.657 | -57.2113 | -57.106 | -57.106 | -57.193 | -56.9229 | -0.01831 | -0.004577 | -0.086975 | 1.0208 | 1.3138 | 0.38452 | 1.3321 | 0.40283 | -0.027466 | 0.050354 | -122.7127 | 0.07782 | 0.26093 | -0.009155 | 0.28839 | 0.018311 | 1.0391 | 122.7219 | 0.10529 | 0.10529 | 122.8043 | 122.8683 | 122.786 | 122.8409 | -122.8088 | -122.818 | 122.7036 | 0.07782 | 2.0782 | 1.2909
1466.1719 | 123.0743 | -57.1701 | 65.625 | -0.037689 | -0.00066014 | 0.06288 | 0.074599 | 0.0057144 | 0.0024053 | 0.0081988 | 0.023071 | -0.00082025 | 0.00042723 | 0.00091422 | -0.0021469 | -0.0036573 | 0.00088014 | -54.9683 | 65.625 | -57.2021 | 65.5563 | -56.1905 | -56.8268 | -55.8975 | -55.8838 | 65.6342 | -57.2113 | -57.0969 | -57.106 | -57.2205 | -56.9321 | -0.032043 | 0 | -0.068665 | 0.97961 | 1.2726 | 0.34332 | 1.3046 | 0.37537 | -0.041199 | 0.009155 | -122.7219 | 0.064087 | 0.23804 | -0.050354 | 0.27924 | -0.009155 | 1.0117 | 122.7585 | 0.10529 | 0.11444 | 122.8271 | 122.8455 | 122.7951 | 122.8043 | -122.8271 | -122.8363 | 122.7264 | 0.073242 | 2.2018 | 1.2863
1467.1719 | 123.0103 | -57.1838 | 65.6433 | -0.12924 | 0.0014761 | 0.064375 | 0.073104 | -0.0013352 | 0.0039007 | 0.007558 | 0.010864 | -0.00060665 | 2.8e-08 | 0.0043322 | -0.00065151 | -0.00066648 | -0.0027515 | -54.8904 | 65.6067 | -57.1976 | 65.5106 | -56.1768 | -56.813 | -55.8929 | -55.9479 | 65.6799 | -57.2067 | -57.1335 | -57.1472 | -57.2525 | -56.987 | -0.013733 | -0.036622 | -0.13275 | 1.0071 | 1.2909 | 0.37079 | 1.3046 | 0.38452 | -0.022888 | 0.036621 | -122.7768 | 0.036621 | 0.19684 | -0.068664 | 0.21973 | -0.045776 | 1.0208 | 122.7081 | 0.059509 | 0.073242 | 122.8043 | 122.8867 | 122.7905 | 122.8638 | -122.8409 | -122.85 | 122.6944 | 0.050354 | 2.2934 | 1.236
1468.1719 | 123.0011 | -57.2067 | 65.6754 | -0.022431 | -0.00066014 | 0.062453 | 0.073958 | -0.00090783 | 0.0043281 | 0.0094806 | -0.01355 | 0.00088875 | -0.0012818 | -0.0052808 | -0.0021469 | -0.0038709 | -0.0010425 | -54.9408 | 65.6342 | -57.2479 | 65.4327 | -56.25 | -56.9 | -56.0028 | -56.0303 | 65.6799 | -57.2617 | -57.1838 | -57.2067 | -57.2937 | -57.0145 | -0.041199 | -0.041199 | -0.24262 | 0.95673 | 1.2039 | 0.3067 | 1.2451 | 0.3479 | -0.054932 | 0.004578 | -122.8592 | 0 | 0.19226 | -0.086975 | 0.24719 | -0.032043 | 0.99793 | 122.6807 | 0.054932 | 0.07782 | 122.8821 | 122.9416 | 122.8409 | 122.8867 | -122.9233 | -122.937 | 122.6395 | 0.022888 | 2.2659 | 1.1765
1469.1719 | 122.9782 | -57.2388 | 65.6662 | -0.060578 | 0.0014761 | 0.061598 | 0.074386 | -0.00026703 | 0.0051825 | 0.0094806 | -0.010498 | 0.0021703 | -0.00085457 | -0.00036738 | -0.0012925 | -0.0025891 | -0.0036059 | -54.9271 | 65.6387 | -57.2205 | 65.4419 | -56.2363 | -56.8909 | -56.0028 | -56.0257 | 65.6754 | -57.2433 | -57.1884 | -57.2021 | -57.3029 | -57.0328 | 0.018311 | -0.027466 | -0.2243 | 1.0025 | 1.236 | 0.3479 | 1.2177 | 0.32959 | -0.004577 | 0.009155 | -122.8546 | 0.036622 | 0.20599 | -0.064086 | 0.21057 | -0.059509 | 0.98419 | 122.6624 | 0.041199 | 0.054931 | 122.8592 | 122.9187 | 122.8775 | 122.9141 | -122.8867 | -122.9095 | 122.6807 | 0.050354 | 2.3117 | 1.2131
1470.1719 | 122.9828 | -57.1838 | 65.6754 | -0.014801 | -0.00023294 | 0.06288 | 0.074172 | 0.00058737 | 0.0013373 | 0.007558 | 0.013916 | 0.0021703 | -0.00085457 | -0.0037854 | -0.00022431 | -0.0028027 | 0.0025891 | -54.9408 | 65.625 | -57.2433 | 65.4419 | -56.2317 | -56.8588 | -56.0028 | -56.0165 | 65.6891 | -57.2433 | -57.2021 | -57.193 | -57.3074 | -57.0099 | -0.059509 | -0.050354 | -0.23346 | 0.95215 | 1.181 | 0.32501 | 1.2405 | 0.38452 | -0.059509 | 0.013733 | -122.8775 | -0.009155 | 0.17395 | -0.1236 | 0.23346 | -0.064087 | 1.0117 | 122.6852 | 0.050354 | 0.041199 | 122.8683 | 122.9324 | 122.8088 | 122.8729 | -122.9187 | -122.9187 | 122.6257 | -0.01831 | 2.243 | 1.1673
1471.1719 | 123.0835 | -57.1884 | 65.6021 | -0.037689 | 0.00083526 | 0.064803 | 0.074172 | -5.343e-05 | 0.0024053 | 0.0069172 | 0.03833 | -0.00017945 | -0.0019226 | -0.0018628 | -0.0032151 | -0.0040845 | 0.0030163 | -54.8721 | 65.5884 | -57.1976 | 65.5243 | -56.1401 | -56.7673 | -55.9067 | -55.6366 | 65.6754 | -57.1701 | -57.1198 | -57.1243 | -57.1884 | -56.9321 | -0.009155 | -0.013733 | -0.07782 | 1.0483 | 1.2817 | 0.42114 | 1.2909 | 0.4303 | 0.018311 | 0.073242 | -122.7219 | 0.064087 | 0.25635 | 0 | 0.23804 | -0.018311 | 1.0574 | 122.7219 | 0.045776 | 0.050354 | 122.786 | 122.8455 | 122.7768 | 122.8638 | -122.7997 | -122.7722 | 122.7127 | 0.068665 | 2.3163 | 1.5518
1472.1719 | 123.0652 | -57.1747 | 65.6113 | -0.068207 | 0.0029715 | 0.063521 | 0.07524 | -0.00026703 | 0.0032599 | 0.0081988 | 0.016968 | -0.00082025 | -0.00085457 | -0.0037854 | -0.0023605 | -0.0055799 | 2.554e-05 | -54.9042 | 65.6113 | -57.2296 | 65.506 | -56.1584 | -56.8039 | -55.8975 | -55.9296 | 65.6342 | -57.2205 | -57.1198 | -57.1198 | -57.2113 | -56.9458 | -0.054931 | 0 | -0.10529 | 1.0162 | 1.2772 | 0.37079 | 1.3321 | 0.42572 | -0.045776 | 0.022888 | -122.731 | 0.054932 | 0.22888 | -0.036621 | 0.27466 | 0.009155 | 1.0712 | 122.7356 | 0.10071 | 0.10071 | 122.8409 | 122.8546 | 122.7859 | 122.8088 | -122.8409 | -122.8317 | 122.6807 | 0.054932 | 2.2705 | 1.2451
1473.1719 | 123.0881 | -57.1701 | 65.625 | -0.022431 | -0.0015145 | 0.063307 | 0.073958 | 0.00251 | 0.0032599 | 0.0086262 | 0.029175 | 0.0017431 | -0.00085457 | -0.00015378 | -0.0021469 | -0.0019483 | 0.00066654 | -54.9042 | 65.5792 | -57.2296 | 65.5197 | -56.1539 | -56.8085 | -55.9158 | -55.9204 | 65.6342 | -57.2159 | -57.0969 | -57.1014 | -57.2159 | -56.9504 | -0.059509 | -0.045776 | -0.10529 | 1.0162 | 1.2543 | 0.36163 | 1.3138 | 0.42114 | -0.045776 | 0.009155 | -122.7219 | 0.068665 | 0.21973 | -0.045776 | 0.2655 | 0 | 1.0757 | 122.7493 | 0.11444 | 0.11902 | 122.8088 | 122.85 | 122.7493 | 122.8043 | -122.8546 | -122.8409 | 122.6898 | 0.073242 | 2.2659 | 1.2497
1474.1719 | 122.9736 | -57.193 | 65.6982 | -0.037689 | 0.0023307 | 0.064803 | 0.074813 | -0.0015488 | 0.0024053 | 0.0079852 | -0.0074462 | 0.00024775 | -0.0019226 | -0.0014356 | -0.00043791 | -0.0053663 | 0.0025891 | -54.8996 | 65.625 | -57.2159 | 65.4877 | -56.2088 | -56.8497 | -55.9479 | -55.9891 | 65.6845 | -57.2433 | -57.1838 | -57.1747 | -57.2983 | -57.0007 | -0.022888 | -0.073242 | -0.21057 | 0.98419 | 1.2451 | 0.34332 | 1.268 | 0.36621 | -0.050354 | -0.013733 | -122.8821 | 0.01831 | 0.19226 | -0.10529 | 0.24262 | -0.054932 | 1.0071 | 122.7036 | 0.068664 | 0.059509 | 122.8409 | 122.9279 | 122.818 | 122.8775 | -122.9141 | -122.9416 | 122.6807 | 0.009155 | 2.2934 | 1.2039
1475.1719 | 122.9965 | -57.2159 | 65.6479 | -0.060578 | 0.0029715 | 0.062239 | 0.074386 | -0.0017624 | 0.0030463 | 0.0086262 | -0.010498 | 0.0021703 | 0.00021363 | 0.0019824 | 0.00020289 | -0.0038709 | -0.0014697 | -54.8996 | 65.6433 | -57.2113 | 65.4877 | -56.1996 | -56.8314 | -55.9341 | -55.9525 | 65.6616 | -57.1976 | -57.1609 | -57.1747 | -57.2662 | -57.0053 | 0.004577 | -0.004577 | -0.16022 | 1.0162 | 1.2817 | 0.38452 | 1.2772 | 0.37994 | 0.01831 | 0.013733 | -122.8088 | 0.041198 | 0.21057 | -0.050354 | 0.19226 | -0.068664 | 1.0117 | 122.699 | 0.022888 | 0.036621 | 122.8546 | 122.8592 | 122.8592 | 122.8775 | -122.8592 | -122.8455 | 122.7036 | 0.054931 | 2.3163 | 1.2634
1476.1719 | 123.111 | -57.2021 | 65.593 | -0.13687 | 0.00062166 | 0.064375 | 0.076308 | 0.0010148 | 0.0028327 | 0.009267 | -0.022705 | 0.00088875 | -0.00021357 | 0.00048702 | -0.00022431 | -0.0013073 | -0.0012561 | -54.9774 | 65.5701 | -57.2662 | 65.4465 | -56.2363 | -56.8954 | -56.012 | -55.9662 | 65.625 | -57.2708 | -57.1106 | -57.1609 | -57.28 | -56.9412 | -0.064087 | -0.022889 | -0.14648 | 0.96588 | 1.1902 | 0.3067 | 1.2543 | 0.37079 | -0.068665 | 0.032043 | -122.7036 | 0.041198 | 0.26093 | -0.07782 | 0.32959 | -0.009155 | 1.03 | 122.7127 | 0.10986 | 0.16022 | 122.8363 | 122.8958 | 122.7722 | 122.8271 | -122.8592 | -122.8638 | 122.6486 | 0.091552 | 2.2247 | 1.236
1477.1719 | 123.0286 | -57.1838 | 65.6479 | -0.083466 | 0.00040806 | 0.06053 | 0.073958 | 0.00251 | 0.00069649 | 0.0086262 | -0.0043946 | -0.00017945 | 0.0014954 | -0.0033582 | -0.0015061 | -0.0030163 | 0.00023934 | -54.895 | 65.5792 | -57.2159 | 65.506 | -56.163 | -56.8176 | -55.9158 | -55.9433 | 65.6662 | -57.2205 | -57.1426 | -57.1243 | -57.2388 | -56.9778 | -0.032043 | -0.068664 | -0.14191 | 1.0208 | 1.268 | 0.36621 | 1.3 | 0.39825 | -0.036621 | 0.018311 | -122.7905 | 0.059509 | 0.20599 | -0.054932 | 0.24262 | -0.018311 | 1.0529 | 122.7219 | 0.09613 | 0.07782 | 122.7951 | 122.8867 | 122.7631 | 122.85 | -122.8638 | -122.8683 | 122.6898 | 0.041199 | 2.2888 | 1.2405
1478.1719 | 122.9507 | -57.2021 | 65.6708 | -0.052948 | 0.00062166 | 0.062025 | 0.074813 | -0.00026703 | 0.0021917 | 0.0088398 | -0.0074462 | 0.0028113 | -0.00085457 | -0.0010084 | -0.00043791 | -0.0023755 | -0.0018971 | -54.9042 | 65.6387 | -57.2296 | 65.4236 | -56.2637 | -56.868 | -55.9799 | -56.0394 | 65.6845 | -57.2525 | -57.2067 | -57.2159 | -57.3166 | -57.0374 | -0.027466 | -0.032043 | -0.24719 | 0.93841 | 1.2222 | 0.33417 | 1.2497 | 0.36163 | -0.050354 | 0.013733 | -122.8775 | -0.013733 | 0.16479 | -0.11444 | 0.21515 | -0.064087 | 0.96588 | 122.6532 | 0.036621 | 0.045776 | 122.8683 | 122.937 | 122.8409 | 122.8867 | -122.9004 | -122.9233 | 122.6257 | -0.004578 | 2.298 | 1.1627
1479.1719 | 122.9691 | -57.1884 | 65.6342 | -0.060578 | 0.00062166 | 0.063521 | 0.074599 | -0.00048063 | 0.0041143 | 0.0073444 | -0.01355 | 0.00024775 | 2.8e-08 | -0.00036738 | -0.0019333 | -0.0021619 | -0.0029651 | -54.9133 | 65.6342 | -57.2159 | 65.4465 | -56.2408 | -56.8542 | -55.9616 | -56.0028 | 65.6845 | -57.225 | -57.193 | -57.2067 | -57.2891 | -57.019 | -0.027465 | 0 | -0.18768 | 0.94757 | 1.2268 | 0.33417 | 1.2543 | 0.36163 | -0.036621 | 0.050354 | -122.8271 | -0.01831 | 0.16937 | -0.10071 | 0.20599 | -0.064087 | 0.97504 | 122.6624 | 0.018311 | 0.032044 | 122.85 | 122.9095 | 122.8226 | 122.8729 | -122.85 | -122.8592 | 122.6349 | -0.004577 | 2.2751 | 1.1856
1480.1719 | 122.9919 | -57.2113 | 65.6708 | -0.052948 | -0.00023294 | 0.061385 | 0.073318 | -0.0043258 | 0.0049689 | 0.007558 | 0.023071 | 0.00067495 | 0.001068 | 0.0030506 | -0.0030013 | -0.0055799 | -0.00018806 | -54.9042 | 65.6113 | -57.2205 | 65.4785 | -56.2088 | -56.8405 | -55.9616 | -55.9753 | 65.6708 | -57.2067 | -57.1838 | -57.2067 | -57.2754 | -56.9962 | -0.009155 | -0.059509 | -0.19226 | 1.0025 | 1.2497 | 0.37079 | 1.2588 | 0.37994 | 0.004578 | 0 | -122.8546 | 0.004578 | 0.21515 | -0.064087 | 0.21057 | -0.068665 | 1.0117 | 122.699 | 0 | 0.022888 | 122.8317 | 122.8775 | 122.8226 | 122.8821 | -122.8912 | -122.8775 | 122.6898 | 0.027466 | 2.3071 | 1.236
1481.1719 | 123.024 | -57.2021 | 65.6479 | -0.098725 | 0.00040806 | 0.063307 | 0.074386 | 0.00080117 | 0.00026909 | 0.0099078 | 0.0047608 | 0.0017431 | -0.0010682 | -0.0027174 | -0.0010787 | -0.0019483 | -0.00061526 | -54.9088 | 65.6158 | -57.2113 | 65.4922 | -56.1951 | -56.8176 | -55.9387 | -55.957 | 65.657 | -57.2479 | -57.1701 | -57.1518 | -57.2525 | -56.9641 | -0.009156 | -0.032043 | -0.15564 | 1.0071 | 1.2634 | 0.38452 | 1.2726 | 0.39368 | -0.045777 | 0.009155 | -122.818 | 0.050354 | 0.23804 | -0.050354 | 0.28381 | -0.004577 | 1.0162 | 122.7036 | 0.096131 | 0.07782 | 122.8271 | 122.905 | 122.818 | 122.8592 | -122.8592 | -122.8958 | 122.6944 | 0.032043 | 2.2934 | 1.2451
1482.1719 | 123.0331 | -57.2021 | 65.6387 | -0.075836 | 0.00040806 | 0.062025 | 0.073958 | 0.0010148 | 0.0041143 | 0.0090534 | 0.029175 | -0.00039305 | 0.00085443 | -0.00015378 | -0.0030013 | -0.0032301 | 0.0010937 | -54.9042 | 65.5701 | -57.2205 | 65.4922 | -56.1768 | -56.813 | -55.9296 | -55.9341 | 65.6296 | -57.225 | -57.1426 | -57.1381 | -57.2479 | -56.9641 | -0.018311 | -0.068665 | -0.14648 | 1.0254 | 1.2726 | 0.3891 | 1.2909 | 0.40741 | -0.022889 | -0.009155 | -122.7814 | 0.064086 | 0.23804 | -0.045777 | 0.26093 | -0.022888 | 1.0437 | 122.7127 | 0.086975 | 0.082398 | 122.7905 | 122.8546 | 122.7722 | 122.8317 | -122.8592 | -122.8638 | 122.6944 | 0.059509 | 2.298 | 1.268
1483.1719 | 122.9553 | -57.2205 | 65.6845 | -0.10635 | 0.0012625 | 0.062453 | 0.076736 | 0.00058737 | 0.0032599 | 0.0069172 | -0.019653 | 0.0013159 | -0.00064077 | -0.00015378 | 0.00063009 | -0.0040845 | -0.0025379 | -54.9362 | 65.625 | -57.2205 | 65.4465 | -56.2546 | -56.8726 | -55.9845 | -55.9982 | 65.6799 | -57.2388 | -57.2021 | -57.2113 | -57.3166 | -57.0328 | 0 | -0.059509 | -0.23804 | 0.96588 | 1.236 | 0.3479 | 1.236 | 0.3479 | -0.018311 | -0.004577 | -122.8867 | 0.009155 | 0.18768 | -0.09613 | 0.20599 | -0.077819 | 0.96588 | 122.6669 | 0.027466 | 0.036622 | 122.8455 | 122.9187 | 122.8455 | 122.9004 | -122.905 | -122.9233 | 122.6669 | 0.018311 | 2.2842 | 1.2222
1484.1719 | 123.056 | -57.1793 | 65.6067 | -0.075836 | 0.00019446 | 0.063521 | 0.07289 | 0.001442 | 0.0030463 | 0.0096942 | 0.0078126 | 0.00067495 | 0.00021363 | 0.0026232 | -0.0027877 | -0.0028027 | 0.0010937 | -54.9042 | 65.6067 | -57.2113 | 65.5106 | -56.1539 | -56.7993 | -55.9158 | -55.925 | 65.6479 | -57.2113 | -57.106 | -57.1152 | -57.225 | -56.9321 | -0.032044 | 0 | -0.09613 | 1.0254 | 1.2634 | 0.37994 | 1.2955 | 0.41199 | -0.032044 | 0.041199 | -122.7127 | 0.064087 | 0.24719 | -0.045777 | 0.27924 | -0.013733 | 1.0574 | 122.7219 | 0.096131 | 0.10529 | 122.818 | 122.8592 | 122.7859 | 122.8271 | -122.818 | -122.818 | 122.6898 | 0.073242 | 2.2751 | 1.2543
1485.1719 | 123.0698 | -57.1747 | 65.6296 | -0.083466 | 0.0031851 | 0.060316 | 0.076095 | -0.0021896 | 0.0045417 | 0.0099078 | 0.035278 | 0.00046135 | -0.00064077 | -0.0033582 | -0.00086511 | -0.00088008 | 0.0013073 | -54.6707 | 65.6662 | -57.1793 | 65.4694 | -56.1768 | -56.7993 | -55.9433 | -55.9067 | 65.6342 | -57.2205 | -57.0969 | -57.1198 | -57.2067 | -56.9412 | -0.004577 | 0.036621 | -0.16022 | 0.99793 | 1.2314 | 0.37537 | 1.236 | 0.37994 | -0.045776 | 0.004577 | -122.7264 | 0.054932 | 0.23346 | -0.032043 | 0.27924 | 0.013733 | 1.0025 | 122.6486 | 0.10071 | 0.1236 | 122.8455 | 122.8546 | 122.8409 | 122.8088 | -122.8088 | -122.85 | 122.644 | 0.07782 | 2.504 | 1.268
1486.1719 | 122.9782 | -57.2067 | 65.657 | -0.075836 | -0.00023294 | 0.065016 | 0.072463 | 0.0012284 | 0.0024053 | 0.0067036 | -0.0043946 | 0.0011023 | 0.003418 | 0.0015552 | -0.0032151 | -0.0036573 | 0.00066654 | -54.9637 | 65.6433 | -57.2342 | 65.4144 | -56.2775 | -56.9 | -56.0211 | -56.0349 | 65.6525 | -57.2479 | -57.2021 | -57.2205 | -57.312 | -57.019 | -0.027466 | -0.013732 | -0.24261 | 0.92926 | 1.1856 | 0.3067 | 1.2131 | 0.33417 | -0.041199 | -0.004577 | -122.8592 | -0.013733 | 0.18768 | -0.10529 | 0.22888 | -0.064087 | 0.95673 | 122.6486 | 0.027466 | 0.045777 | 122.8775 | 122.9004 | 122.85 | 122.8592 | -122.8912 | -122.905 | 122.6212 | 0.004578 | 2.243 | 1.1719
1487.1719 | 123.0377 | -57.1838 | 65.6433 | -0.03006 | -0.00087374 | 0.060957 | 0.073745 | -0.00048063 | 0.0032599 | 0.0073444 | 0.010864 | 0.0011023 | 0.00085443 | -0.0033582 | -0.00065151 | -0.0028027 | -0.00082886 | -54.9042 | 65.593 | -57.2571 | 65.506 | -56.1813 | -56.8085 | -55.9341 | -55.9433 | 65.6433 | -57.2388 | -57.1381 | -57.1243 | -57.2296 | -56.9595 | -0.073242 | -0.050354 | -0.13733 | 1.0025 | 1.2497 | 0.37537 | 1.3229 | 0.44861 | -0.054932 | 0 | -122.7814 | 0.059509 | 0.2243 | -0.045776 | 0.27924 | 0.009156 | 1.0757 | 122.7631 | 0.11444 | 0.10071 | 122.85 | 122.8821 | 122.7768 | 122.8271 | -122.9004 | -122.8821 | 122.6898 | 0.045776 | 2.2797 | 1.2405
1488.1719 | 123.0835 | -57.193 | 65.6525 | -0.068207 | 0.0010489 | 0.064162 | 0.074599 | -0.0013352 | 0.0013373 | 0.007558 | 0.013916 | 3.4148e-05 | -0.0012818 | -0.0025036 | -0.0012925 | -0.0036573 | -0.0014697 | -54.9042 | 65.6067 | -57.2342 | 65.5106 | -56.1859 | -56.8314 | -55.9341 | -55.925 | 65.6342 | -57.2342 | -57.1106 | -57.1335 | -57.2067 | -56.9504 | -0.041199 | -0.045777 | -0.14191 | 1.0071 | 1.2589 | 0.36163 | 1.3 | 0.40283 | -0.041199 | -0.018311 | -122.7631 | 0.059509 | 0.24262 | -0.013733 | 0.28381 | 0.027466 | 1.0483 | 122.7448 | 0.10071 | 0.1236 | 122.8409 | 122.8683 | 122.7997 | 122.8271 | -122.8867 | -122.8867 | 122.7036 | 0.082397 | 2.2888 | 1.268
1489.1719 | 122.9919 | -57.1747 | 65.6525 | -0.068207 | 0.00019446 | 0.063948 | 0.073958 | -0.00026703 | 0.0021917 | 0.0090534 | -0.0013428 | 0.00046135 | 0.0019226 | 0.00048702 | -0.00065151 | -0.0032301 | -0.0012561 | -54.9225 | 65.6204 | -57.2388 | 65.4831 | -56.2088 | -56.8359 | -55.9662 | -55.9616 | 65.6662 | -57.2159 | -57.1701 | -57.2021 | -57.2891 | -57.0145 | -0.064087 | -0.032044 | -0.16937 | 0.96588 | 1.2085 | 0.33875 | 1.2726 | 0.40283 | -0.041198 | 0.013733 | -122.8226 | -0.027465 | 0.16022 | -0.11444 | 0.20142 | -0.073243 | 1.03 | 122.7219 | 0.013733 | 0.045776 | 122.8592 | 122.8821 | 122.7951 | 122.8409 | -122.8912 | -122.8683 | 122.6578 | 0.004578 | 2.2522 | 1.2131
1490.1719 | 123.0331 | -57.193 | 65.625 | -0.098725 | 0.0019035 | 0.06288 | 0.075667 | 0.0018692 | 0.00069649 | 0.0064898 | 0.026123 | -0.0010339 | 0.00064083 | -0.00464 | -0.00065151 | -0.0040845 | 0.00045294 | -54.9271 | 65.6158 | -57.2479 | 65.4877 | -56.2042 | -56.8314 | -55.9341 | -55.9662 | 65.657 | -57.2342 | -57.1564 | -57.1564 | -57.2754 | -56.9641 | -0.054932 | -0.009155 | -0.13733 | 0.98877 | 1.2589 | 0.36163 | 1.3138 | 0.41657 | -0.041199 | 0.032043 | -122.7814 | 0.036621 | 0.22888 | -0.082398 | 0.27008 | -0.041199 | 1.0437 | 122.7356 | 0.07782 | 0.07782 | 122.8638 | 122.8912 | 122.8088 | 122.85 | -122.8729 | -122.8592 | 122.6807 | 0.036621 | 2.2659 | 1.2268
1491.1719 | 123.0972 | -57.1884 | 65.6342 | -0.098725 | 0.0012625 | 0.063521 | 0.074172 | 0.00016017 | 0.0028327 | 0.00414 | 0.035278 | 0.0013159 | -0.00085457 | -0.005708 | -0.0040695 | -0.0023755 | -0.00018806 | -54.9179 | 65.5884 | -57.2433 | 65.506 | -56.1813 | -56.8222 | -55.9021 | -55.8975 | 65.6067 | -57.2205 | -57.0877 | -57.0877 | -57.1793 | -56.9138 | -0.054931 | -0.045776 | -0.12817 | 1.0071 | 1.2863 | 0.36621 | 1.3412 | 0.42114 | -0.032043 | -0.027466 | -122.7219 | 0.10071 | 0.27466 | 0.009156 | 0.3067 | 0.041199 | 1.062 | 122.7493 | 0.13275 | 0.13275 | 122.8317 | 122.8271 | 122.7768 | 122.7951 | -122.8775 | -122.8546 | 122.6944 | 0.10071 | 2.2705 | 1.2909
1492.1719 | 123.0789 | -57.2067 | 65.6067 | -0.03006 | 0.00083526 | 0.06288 | 0.072677 | -0.0017624 | 0.0028327 | 0.009267 | 0.023071 | -0.0031703 | 0.00042723 | -0.0059216 | -0.00043791 | -0.0015211 | 0.0013073 | -54.8996 | 65.5838 | -57.2388 | 65.5243 | -56.1493 | -56.7856 | -55.9296 | -55.6778 | 65.6891 | -57.225 | -57.1335 | -57.0786 | -57.2067 | -56.9458 | -0.032044 | -0.022888 | -0.082397 | 1.0574 | 1.2772 | 0.42114 | 1.3092 | 0.45319 | -0.018311 | 0.082398 | -122.7402 | 0.12817 | 0.26093 | 0 | 0.27924 | 0.018311 | 1.0895 | 122.7631 | 0.14648 | 0.091553 | 122.8226 | 122.9141 | 122.7905 | 122.8958 | -122.8455 | -122.8317 | 122.731 | 0.073242 | 2.3071 | 1.5289
1493.1719 | 123.0469 | -57.193 | 65.625 | -0.045319 | 0.0029715 | 0.063094 | 0.072677 | 0.0037918 | 0.0043281 | 0.010121 | 0.0078126 | -0.00039305 | -0.00085457 | 0.0017688 | -0.0017197 | -2.5678e-05 | 0.00088014 | -54.9179 | 65.6067 | -57.2525 | 65.4968 | -56.1813 | -56.8039 | -55.925 | -55.9067 | 65.6204 | -57.2388 | -57.1289 | -57.1014 | -57.2296 | -56.9504 | -0.059509 | -0.018311 | -0.12817 | 1.0117 | 1.268 | 0.3891 | 1.3275 | 0.44861 | -0.045777 | -0.004578 | -122.7539 | 0.091553 | 0.24262 | -0.036621 | 0.28839 | 0.009156 | 1.0712 | 122.7493 | 0.13733 | 0.10986 | 122.8592 | 122.8592 | 122.7997 | 122.8134 | -122.8775 | -122.8638 | 122.6898 | 0.064087 | 2.2751 | 1.2863
1494.1719 | 122.9965 | -57.2205 | 65.6616 | -0.075836 | 0.0019035 | 0.062025 | 0.072677 | 0.0012284 | 0.0045417 | 0.009267 | 0.001709 | 3.4148e-05 | 0.00064083 | 0.0066822 | -0.0017197 | -0.0025891 | -0.0012561 | -54.9271 | 65.6067 | -57.2571 | 65.4648 | -56.2363 | -56.8497 | -55.9708 | -55.9845 | 65.6525 | -57.2479 | -57.193 | -57.1976 | -57.2479 | -56.9962 | -0.036621 | -0.054932 | -0.19684 | 0.98419 | 1.2497 | 0.37079 | 1.2863 | 0.40741 | -0.027466 | -0.009155 | -122.8546 | 0.022888 | 0.2243 | -0.027466 | 0.25177 | 0 | 1.0208 | 122.7219 | 0.050354 | 0.054932 | 122.8638 | 122.9004 | 122.8271 | 122.8729 | -122.9187 | -122.9095 | 122.6852 | 0.027466 | 2.2934 | 1.236
1495.1719 | 123.0743 | -57.225 | 65.6113 | 0.26749 | -0.0013009 | 0.062025 | 0.075454 | 0.00058737 | 0.0039007 | 0.0088398 | 0.013916 | -0.00017945 | -0.00064077 | -0.00058098 | -0.0023605 | -0.0023755 | -0.00061526 | -54.9225 | 65.625 | -57.2159 | 65.5106 | -56.1768 | -56.8542 | -55.925 | -55.9158 | 65.6204 | -57.2113 | -57.1014 | -57.1198 | -57.2113 | -56.9229 | 0.009156 | 0.013733 | -0.10071 | 1.0483 | 1.3 | 0.37079 | 1.2909 | 0.36163 | 0.013733 | 0.009155 | -122.7127 | 0.10529 | 0.30212 | 0.013733 | 0.28839 | 0 | 1.0391 | 122.7264 | 0.091553 | 0.10986 | 122.8409 | 122.8317 | 122.85 | 122.8455 | -122.8271 | -122.8226 | 122.7356 | 0.1236 | 2.3026 | 1.3092
1496.1719 | 123.1064 | -57.1976 | 65.625 | -0.11398 | 0.00040806 | 0.063094 | 0.073318 | -0.00026703 | 5.5488e-05 | 0.009267 | -0.0074462 | 0.0017431 | -0.00021357 | -0.00015378 | 0.0016983 | -0.0040845 | -0.0033923 | -54.9316 | 65.5792 | -57.225 | 65.3503 | -56.4239 | -56.7764 | -55.8746 | -55.8746 | 65.6067 | -57.225 | -57.1014 | -57.0786 | -57.193 | -56.9183 | -0.027466 | -0.045776 | -0.27466 | 0.77362 | 1.3229 | 0.42114 | 1.3504 | 0.44861 | -0.027466 | -0.018311 | -122.7264 | 0.11902 | 0.27924 | 0.004578 | 0.3067 | 0.032044 | 0.80109 | 122.5754 | 0.14648 | 0.1236 | 122.8043 | 122.8317 | 122.7768 | 122.8043 | -122.85 | -122.85 | 122.5479 | 0.096131 | 2.2659 | 1.3229
1497.1719 | 123.0743 | -57.193 | 65.5838 | -0.16739 | -0.00044654 | 0.06288 | 0.07524 | -0.0045394 | 0.0047553 | 0.010335 | 0.023071 | -0.00017945 | 0.0012818 | -0.0065626 | -0.0017197 | -0.0032301 | -0.00061526 | -54.9316 | 65.5792 | -57.2708 | 65.5014 | -56.1996 | -56.813 | -55.9296 | -55.9113 | 65.5792 | -57.2388 | -57.0923 | -57.0923 | -57.2021 | -56.9321 | -0.07782 | -0.004577 | -0.082397 | 0.99335 | 1.2634 | 0.37994 | 1.3412 | 0.45776 | -0.045777 | -0.004577 | -122.6761 | 0.10071 | 0.26093 | -0.009155 | 0.3067 | 0.036622 | 1.0712 | 122.7722 | 0.14649 | 0.14649 | 122.85 | 122.818 | 122.7722 | 122.7722 | -122.8546 | -122.8226 | 122.6944 | 0.10071 | 2.2614 | 1.2817
1498.1719 | 123.0972 | -57.193 | 65.6296 | -0.037689 | -0.00087374 | 0.062453 | 0.073958 | -0.0015488 | 0.0047553 | 0.010335 | 0.029175 | -0.00017945 | 0.0014954 | 0.00070062 | -0.0010787 | -0.0040845 | -0.00082886 | -54.9454 | 65.593 | -57.2708 | 65.4922 | -56.2088 | -56.8359 | -55.9479 | -55.9341 | 65.6204 | -57.2525 | -57.0969 | -57.1106 | -57.2159 | -56.9092 | -0.07782 | -0.036621 | -0.13733 | 0.98419 | 1.2451 | 0.35706 | 1.3229 | 0.43488 | -0.059509 | -0.009156 | -122.7264 | 0.082397 | 0.28381 | -0.022888 | 0.34332 | 0.036621 | 1.062 | 122.7631 | 0.14191 | 0.15564 | 122.8638 | 122.8729 | 122.7859 | 122.8134 | -122.9004 | -122.8821 | 122.6852 | 0.09613 | 2.2476 | 1.2589
1499.1719 | 123.0606 | -57.1838 | 65.625 | -0.1445 | 0.0025443 | 0.062453 | 0.074172 | -0.003685 | 0.0015509 | 0.0077716 | -0.01355 | 3.4148e-05 | -0.00085457 | 0.002196 | -0.0030013 | -0.0034437 | -0.0010425 | -54.9225 | 65.5838 | -57.2617 | 65.4968 | -56.1722 | -56.8039 | -55.9341 | -55.9204 | 65.6204 | -57.2159 | -57.0969 | -57.1152 | -57.2205 | -56.9458 | -0.07782 | -0.041199 | -0.12817 | 1.0117 | 1.2497 | 0.37994 | 1.3275 | 0.45776 | -0.032043 | -0.004578 | -122.7219 | 0.068665 | 0.23804 | -0.036621 | 0.27008 | -0.004578 | 1.0895 | 122.7585 | 0.10071 | 0.11902 | 122.8455 | 122.8363 | 122.7676 | 122.8043 | -122.8867 | -122.8409 | 122.6807 | 0.086975 | 2.2614 | 1.2634
1500.1719 | 122.9828 | -57.2021 | 65.625 | -0.083466 | 0.0016899 | 0.06288 | 0.074599 | -0.0017624 | 0.0041143 | 0.007558 | -0.010498 | 0.0015295 | 0.00085443 | 0.0028368 | -0.0021469 | -0.0045117 | -0.0038197 | -54.9179 | 65.593 | -57.2617 | 65.4922 | -56.2317 | -56.8405 | -55.9708 | -55.9616 | 65.657 | -57.2479 | -57.1655 | -57.1747 | -57.2937 | -56.9916 | -0.05951 | -0.032043 | -0.13275 | 0.97046 | 1.2314 | 0.36163 | 1.2909 | 0.42114 | -0.045777 | 0.032043 | -122.7905 | 0.027465 | 0.21057 | -0.091553 | 0.25635 | -0.045776 | 1.03 | 122.7539 | 0.073242 | 0.082398 | 122.8546 | 122.905 | 122.7951 | 122.8592 | -122.8867 | -122.8729 | 122.6944 | 0.036621 | 2.2842 | 1.2405
1501.1719 | 123.0698 | -57.1701 | 65.6021 | -0.11398 | 0.00019446 | 0.063307 | 0.074813 | 0.0037918 | 0.0039007 | 0.0062762 | 0.013916 | 0.00046135 | -0.00085457 | 0.0045458 | -0.00043791 | -0.0019483 | -0.0029651 | -54.9042 | 65.5975 | -57.2388 | 65.5197 | -56.1127 | -56.8954 | -55.957 | -55.925 | 65.6067 | -57.2159 | -57.1014 | -57.0877 | -57.2067 | -56.9458 | -0.068665 | -0.004578 | -0.082398 | 1.0574 | 1.2131 | 0.27466 | 1.2817 | 0.34332 | -0.045776 | 0.004577 | -122.7036 | 0.082397 | 0.2243 | -0.036621 | 0.27008 | 0.009155 | 1.1261 | 122.7585 | 0.12817 | 0.11444 | 122.8363 | 122.8226 | 122.7676 | 122.7768 | -122.8409 | -122.818 | 122.6898 | 0.068665 | 2.2659 | 1.2451
1502.1719 | 123.0194 | -57.1793 | 65.6433 | -0.098725 | 0.00062166 | 0.06523 | 0.072463 | 0.0020828 | 0.00091009 | 0.0077716 | 0.0047608 | -0.00039305 | 0.00042723 | -0.0042126 | -0.0015061 | -0.0030163 | 0.0025891 | -54.9133 | 65.5746 | -57.2617 | 65.4877 | -56.1951 | -56.8314 | -55.9479 | -55.9433 | 65.6113 | -57.2296 | -57.1335 | -57.1472 | -57.2754 | -56.9733 | -0.082398 | -0.068665 | -0.15564 | 0.98419 | 1.2314 | 0.3479 | 1.3138 | 0.4303 | -0.050354 | -0.032044 | -122.7768 | 0.032043 | 0.20599 | -0.096131 | 0.25635 | -0.045777 | 1.0666 | 122.7493 | 0.082397 | 0.09613 | 122.8363 | 122.8409 | 122.7539 | 122.7905 | -122.905 | -122.8729 | 122.6669 | 0.045776 | 2.2659 | 1.236
1503.1719 | 123.0698 | -57.1793 | 65.6067 | -0.052948 | 0.00040806 | 0.061812 | 0.075881 | 0.00037377 | 0.0021917 | 0.0071308 | 0.032227 | -0.0018885 | -0.00042717 | -0.003999 | -0.0015061 | -0.0013073 | -0.0025379 | -54.9042 | 65.5975 | -57.2479 | 65.5151 | -56.163 | -56.7993 | -55.9341 | -55.6183 | 65.7028 | -57.1747 | -57.1335 | -57.0648 | -57.2067 | -56.9458 | -0.068665 | -0.009155 | -0.091552 | 1.0162 | 1.2451 | 0.37994 | 1.3138 | 0.44861 | 0.004577 | 0.096131 | -122.7402 | 0.11444 | 0.23346 | -0.027466 | 0.22888 | -0.032043 | 1.0849 | 122.7631 | 0.10986 | 0.041199 | 122.8455 | 122.8775 | 122.7768 | 122.8821 | -122.8546 | -122.7814 | 122.6944 | 0.045776 | 2.2751 | 1.561
1504.1719 | 123.1064 | -57.1976 | 65.6158 | -0.068207 | 0.0010489 | 0.063948 | 0.072677 | -0.0021896 | 0.00091009 | 0.010335 | 0.016968 | 0.0025975 | -0.0019226 | -0.00036738 | -0.0015061 | -0.0051527 | 0.00045294 | -54.9454 | 65.5884 | -57.28 | 65.4922 | -56.2225 | -56.8405 | -55.9433 | -55.9158 | 65.625 | -57.2433 | -57.0923 | -57.0969 | -57.1838 | -56.9229 | -0.082397 | -0.027466 | -0.1236 | 0.97504 | 1.2543 | 0.35706 | 1.3367 | 0.43945 | -0.045776 | 0.009155 | -122.7081 | 0.10071 | 0.27466 | 0.013733 | 0.32043 | 0.059509 | 1.0574 | 122.7722 | 0.14648 | 0.15106 | 122.8683 | 122.8683 | 122.786 | 122.8226 | -122.8958 | -122.8592 | 122.6898 | 0.10529 | 2.2522 | 1.2817
1505.1719 | 123.0698 | -57.1747 | 65.6021 | -0.075836 | 0.0016899 | 0.061385 | 0.074386 | -0.00069423 | 0.0026191 | 0.0081988 | 0.013916 | -0.00082025 | -0.00042717 | 0.0041186 | -0.0012925 | -0.0034437 | -0.00061526 | -54.9454 | 65.5792 | -57.2571 | 65.4648 | -56.2363 | -56.8268 | -55.9662 | -55.9433 | 65.625 | -57.2479 | -57.1106 | -57.1014 | -57.2067 | -56.9412 | -0.082397 | -0.022888 | -0.13733 | 0.93842 | 1.2085 | 0.3479 | 1.2909 | 0.4303 | -0.073242 | 0.022888 | -122.7127 | 0.073243 | 0.23346 | -0.032043 | 0.3067 | 0.041199 | 1.0208 | 122.7219 | 0.14649 | 0.13733 | 122.8363 | 122.8729 | 122.7539 | 122.7997 | -122.8592 | -122.85 | 122.6395 | 0.064087 | 2.2293 | 1.2314
1506.1719 | 123.1476 | -57.1426 | 65.6616 | -0.091095 | 0.00040806 | 0.063521 | 0.07524 | -0.00069423 | 0.0017645 | 0.0079852 | 0.023071 | -0.00082025 | 0.00085443 | -0.0027174 | -0.0021469 | -0.0040845 | -0.00061526 | -54.9454 | 65.6021 | -57.2479 | 65.538 | -56.163 | -56.7947 | -55.9113 | -55.8792 | 65.6204 | -57.2113 | -57.1014 | -57.0969 | -57.1472 | -56.7902 | -0.10529 | -0.059509 | -0.1236 | 0.97961 | 1.2314 | 0.3479 | 1.3367 | 0.45319 | -0.068665 | -0.041199 | -122.7631 | 0.045776 | 0.35248 | -0.004578 | 0.42114 | 0.064087 | 1.0849 | 122.786 | 0.11444 | 0.10986 | 122.85 | 122.8317 | 122.7448 | 122.7631 | -122.9095 | -122.8729 | 122.6807 | 0.041199 | 2.1973 | 1.2634
1507.1719 | 123.0423 | -57.1655 | 65.6342 | -0.037689 | 0.0012625 | 0.06288 | 0.073745 | 0.00037377 | 0.0043281 | 0.0077716 | 0.001709 | 0.0025975 | 0.00021363 | 0.0030506 | -0.0017197 | -0.0021619 | -0.0038197 | -54.9683 | 65.5746 | -57.2708 | 65.5151 | -56.1859 | -56.813 | -55.9296 | -55.9158 | 65.6479 | -57.2388 | -57.1106 | -57.1198 | -57.2113 | -56.9321 | -0.10529 | -0.059509 | -0.11902 | 0.97961 | 1.236 | 0.35248 | 1.3412 | 0.45776 | -0.073243 | 0.013733 | -122.7448 | 0.045776 | 0.23346 | -0.045777 | 0.3067 | 0.027466 | 1.0849 | 122.7859 | 0.11902 | 0.12817 | 122.8455 | 122.8867 | 122.7402 | 122.8134 | -122.905 | -122.8729 | 122.6807 | 0.054931 | 2.1973 | 1.2497
1508.1719 | 122.9645 | -57.2159 | 65.6525 | -0.052948 | 0.0014761 | 0.062666 | 0.075881 | -0.0013352 | 0.0056097 | 0.0077716 | 0.001709 | -0.00060665 | 0.0014954 | 0.0013416 | -0.0019333 | -0.0047253 | -0.0014697 | -54.9271 | 65.6021 | -57.2433 | 65.4739 | -56.2408 | -56.8451 | -55.9799 | -55.9708 | 65.657 | -57.2433 | -57.1701 | -57.1609 | -57.2662 | -57.019 | -0.027466 | -0.050354 | -0.17853 | 0.97504 | 1.236 | 0.37079 | 1.2634 | 0.39825 | -0.027466 | 0.004577 | -122.8226 | 0.054931 | 0.19684 | -0.050354 | 0.2243 | -0.022888 | 1.0025 | 122.7173 | 0.082397 | 0.073242 | 122.8455 | 122.9004 | 122.818 | 122.8729 | -122.8958 | -122.8958 | 122.6898 | 0.045776 | 2.2888 | 1.2451
1509.1719 | 123.0377 | -57.2067 | 65.6387 | -0.12924 | -0.0010873 | 0.064375 | 0.072677 | -0.001976 | 0.0024053 | 0.0084124 | -0.019653 | 0.00046135 | 0.0019226 | 0.0015552 | -0.0023605 | -0.0025891 | -0.00082886 | -54.9408 | 65.6158 | -57.2525 | 65.4785 | -56.2363 | -56.8405 | -55.9753 | -55.9708 | 65.6616 | -57.2479 | -57.1564 | -57.1747 | -57.28 | -56.9916 | -0.045776 | -0.022888 | -0.16022 | 0.97046 | 1.2314 | 0.36621 | 1.2772 | 0.41199 | -0.041199 | 0.022888 | -122.7951 | 0.032043 | 0.21515 | -0.073242 | 0.25635 | -0.032043 | 1.0162 | 122.731 | 0.073242 | 0.091553 | 122.8683 | 122.9095 | 122.8226 | 122.8683 | -122.8912 | -122.8867 | 122.6852 | 0.050354 | 2.2659 | 1.236
1510.1719 | 123.0286 | -57.1976 | 65.625 | -0.060578 | 0.00083526 | 0.063734 | 0.07524 | 0.001442 | 0.0011237 | 0.0062762 | -0.01355 | -0.00060665 | 0.00021363 | -0.002931 | -0.0034287 | -0.0036573 | 0.0010937 | -54.9225 | 65.593 | -57.2571 | 65.4785 | -56.2271 | -56.8268 | -55.9708 | -55.9525 | 65.6342 | -57.2388 | -57.1609 | -57.1426 | -57.2662 | -56.9962 | -0.059509 | -0.032043 | -0.14648 | 0.97046 | 1.2268 | 0.37079 | 1.2863 | 0.4303 | -0.041199 | 0.009155 | -122.7859 | 0.054932 | 0.20142 | -0.068664 | 0.24262 | -0.027465 | 1.03 | 122.7356 | 0.096131 | 0.07782 | 122.85 | 122.8729 | 122.7905 | 122.8317 | -122.8821 | -122.8638 | 122.6761 | 0.036621 | 2.2751 | 1.2451
1511.1719 | 123.0331 | -57.2067 | 65.6433 | -0.13687 | 0.0014761 | 0.062453 | 0.075667 | 0.0018692 | 0.0026191 | 0.007558 | -0.01355 | -0.00082025 | 2.8e-08 | 0.001128 | 0.0010575 | -0.0042981 | -0.0065967 | -54.9271 | 65.5884 | -57.2708 | 65.4922 | -56.2225 | -56.8314 | -55.9662 | -55.9616 | 65.6662 | -57.2479 | -57.1472 | -57.1609 | -57.2617 | -56.9824 | -0.064087 | -0.054932 | -0.15106 | 0.98419 | 1.2405 | 0.37537 | 1.3046 | 0.43945 | -0.041199 | 0.022888 | -122.7905 | 0.045776 | 0.2243 | -0.054932 | 0.2655 | -0.013733 | 1.0483 | 122.7631 | 0.086975 | 0.10071 | 122.8592 | 122.9141 | 122.7951 | 122.8729 | -122.9141 | -122.8912 | 122.699 | 0.059509 | 2.2797 | 1.2451
1512.1719 | 123.0743 | -57.225 | 65.5838 | -0.098725 | -0.00087374 | 0.064162 | 0.076736 | 0.0052872 | 0.0028327 | 0.0073444 | -0.062378 | -0.00017945 | 0.0019226 | -0.00036738 | -0.0019333 | -0.00088008 | 0.0019483 | -55.0095 | 65.5518 | -57.3395 | 65.4282 | -56.3049 | -56.9321 | -56.0349 | -55.9982 | 65.5884 | -57.2525 | -57.1289 | -57.1793 | -57.2937 | -56.9458 | -0.11444 | -0.032043 | -0.15564 | 0.9201 | 1.1902 | 0.29297 | 1.3046 | 0.40741 | -0.027465 | 0.004578 | -122.7127 | 0.045777 | 0.27924 | -0.068664 | 0.3067 | -0.041199 | 1.0345 | 122.7676 | 0.073242 | 0.1236 | 122.8912 | 122.8409 | 122.7768 | 122.8134 | -122.9233 | -122.8363 | 122.6532 | 0.096131 | 2.2156 | 1.2268
1513.1719 | 123.056 | -57.2067 | 65.6296 | -0.075836 | 0.0029715 | 0.063094 | 0.072036 | -5.343e-05 | 0.0049689 | 0.010762 | 0.013916 | 3.4148e-05 | 0.00085443 | -0.00058098 | -0.0023605 | -0.0028027 | 0.00066654 | -54.9271 | 65.5792 | -57.2479 | 65.4877 | -56.218 | -56.8222 | -55.9662 | -55.9525 | 65.6525 | -57.2433 | -57.1381 | -57.1701 | -57.2525 | -56.9778 | -0.041199 | -0.050354 | -0.14191 | 0.98877 | 1.2405 | 0.38452 | 1.2817 | 0.42572 | -0.036621 | 0.022888 | -122.7676 | 0.036621 | 0.22888 | -0.045776 | 0.2655 | -0.009155 | 1.03 | 122.7356 | 0.073242 | 0.10529 | 122.8271 | 122.8958 | 122.7859 | 122.8592 | -122.8775 | -122.8729 | 122.6944 | 0.068664 | 2.2797 | 1.2543
1514.1719 | 123.0377 | -57.1884 | 65.6158 | -0.10635 | -1.9142e-05 | 0.063521 | 0.075027 | -0.00069423 | 0.0049689 | 0.0052082 | 0.001709 | 0.0013159 | 0.002777 | -0.0016492 | 0.00020289 | -0.0015211 | -0.0016833 | -54.9271 | 65.5792 | -57.2571 | 65.5106 | -56.2042 | -56.8405 | -55.9616 | -55.9479 | 65.6158 | -57.2479 | -57.1472 | -57.1472 | -57.2388 | -56.9733 | -0.068664 | -0.036621 | -0.10529 | 0.98419 | 1.2268 | 0.3479 | 1.2955 | 0.41656 | -0.059509 | 0 | -122.7631 | 0.041199 | 0.21515 | -0.050354 | 0.27466 | 0.009155 | 1.0529 | 122.7676 | 0.10071 | 0.10071 | 122.8363 | 122.8638 | 122.7676 | 122.8043 | -122.8729 | -122.8638 | 122.699 | 0.041199 | 2.2614 | 1.2405
1515.1719 | 123.0515 | -57.1976 | 65.6342 | -0.098725 | 0.0014761 | 0.064162 | 0.073318 | 0.003151 | 0.0021917 | 0.0064898 | 0.02002 | -0.00060665 | 0.00021363 | -0.0044262 | -0.0021469 | -0.0032301 | -0.0033923 | -54.9408 | 65.5884 | -57.2479 | 65.4877 | -56.2134 | -56.8268 | -55.957 | -55.9296 | 65.6433 | -57.2342 | -57.1518 | -57.1289 | -57.2433 | -56.9687 | -0.050354 | -0.045776 | -0.14648 | 0.98419 | 1.2405 | 0.37079 | 1.2909 | 0.42114 | -0.036621 | 0.009156 | -122.7859 | 0.068665 | 0.22888 | -0.045776 | 0.2655 | -0.009155 | 1.0345 | 122.7356 | 0.10529 | 0.082398 | 122.8363 | 122.8775 | 122.786 | 122.8409 | -122.8821 | -122.8683 | 122.6852 | 0.045777 | 2.2568 | 1.268
1516.1719 | 123.0377 | -57.1884 | 65.625 | -0.10635 | 0.00062166 | 0.062666 | 0.073318 | -0.00048063 | 0.0043281 | 0.0056354 | 0.001709 | -0.0016749 | 0.00042723 | -0.0027174 | -0.0040695 | -0.0032301 | -0.0021107 | -54.9362 | 65.5884 | -57.2617 | 65.4877 | -56.2225 | -56.8222 | -55.9662 | -55.9296 | 65.6387 | -57.2433 | -57.1381 | -57.1289 | -57.2296 | -56.955 | -0.073242 | -0.036621 | -0.13733 | 0.96588 | 1.2222 | 0.36621 | 1.2955 | 0.43945 | -0.054931 | 0.013733 | -122.7631 | 0.05951 | 0.23346 | -0.041198 | 0.28839 | 0.013733 | 1.0391 | 122.7493 | 0.11444 | 0.10529 | 122.85 | 122.8821 | 122.7768 | 122.8271 | -122.8867 | -122.8683 | 122.6761 | 0.050354 | 2.2522 | 1.2589
1517.1719 | 122.9645 | -57.2433 | 65.5975 | 0.053863 | -0.00066014 | 0.063948 | 0.077376 | 0.0010148 | 0.0034735 | 0.0099078 | -0.089844 | 0.0017431 | -0.0014954 | 0.0024096 | -0.00086511 | -0.0030163 | 0.0013073 | -55.0964 | 65.5746 | -57.3349 | 65.3549 | -56.4148 | -57.0099 | -56.1127 | -56.0761 | 65.6158 | -57.2937 | -57.2021 | -57.2617 | -57.4036 | -57.0511 | -0.091553 | -0.022888 | -0.24262 | 0.82855 | 1.1307 | 0.23346 | 1.2222 | 0.32501 | -0.050354 | 0.018311 | -122.7997 | -0.018311 | 0.19226 | -0.16022 | 0.24262 | -0.10986 | 0.9201 | 122.6898 | 0.032043 | 0.091553 | 122.9095 | 122.9095 | 122.818 | 122.8592 | -122.9324 | -122.8912 | 122.5983 | 0.041199 | 2.1469 | 1.1673
1518.1719 | 123.0698 | -57.1976 | 65.5609 | -0.075836 | 0.0014761 | 0.063094 | 0.071609 | -0.0030442 | 0.0028327 | 0.0086262 | 0.032227 | -0.00082025 | 0.0019226 | -0.003999 | -0.00065151 | -0.0051527 | -0.0014697 | -54.9179 | 65.5838 | -57.2617 | 65.5334 | -56.1722 | -56.7993 | -55.925 | -55.8975 | 65.6113 | -57.2296 | -57.1472 | -57.3441 | -57.1838 | -56.8771 | -0.064087 | 0.022888 | -0.027466 | 1.0254 | 1.2726 | 0.39826 | 1.3367 | 0.46234 | -0.032043 | 0.050354 | -122.7081 | -0.14648 | 0.32044 | 0.013733 | 0.35248 | 0.045776 | 1.0895 | 122.7951 | -0.11444 | 0.082397 | 122.8455 | 122.8409 | 122.7814 | 122.8088 | -122.8226 | -122.7905 | 122.731 | 0.050354 | 2.2797 | 1.3
1519.1719 | 123.0469 | -57.1838 | 65.6433 | -0.060578 | 0.0014761 | 0.063521 | 0.075027 | 0.00058737 | 0.0011237 | 0.0056354 | 0.029175 | 0.0025975 | -0.0010682 | 0.00070062 | -0.0017197 | -0.0042981 | 0.0010937 | -54.95 | 65.5746 | -57.2891 | 65.5014 | -56.2088 | -56.8405 | -55.9662 | -55.9113 | 65.6067 | -57.2296 | -57.1198 | -57.1289 | -57.2159 | -56.9412 | -0.10529 | -0.068665 | -0.14191 | 0.97504 | 1.2177 | 0.34332 | 1.3229 | 0.44861 | -0.045776 | -0.036622 | -122.7631 | 0.054932 | 0.24262 | -0.032043 | 0.28839 | 0.013733 | 1.0803 | 122.7905 | 0.10071 | 0.10986 | 122.8638 | 122.8363 | 122.7585 | 122.7905 | -122.9324 | -122.8729 | 122.6852 | 0.064087 | 2.2339 | 1.2726
1520.1719 | 123.0606 | -57.1747 | 65.6387 | -0.13687 | 0.0012625 | 0.062666 | 0.073958 | 0.00080117 | 0.0041143 | 0.007558 | 0.010864 | -0.0014613 | 0.00064083 | 0.0045458 | -0.0036423 | -0.0038709 | -0.0021107 | -54.9362 | 65.5609 | -57.2708 | 65.4694 | -56.2088 | -56.8176 | -55.9616 | -55.9021 | 65.6158 | -57.2296 | -57.1106 | -57.1289 | -57.2296 | -56.9641 | -0.09613 | -0.07782 | -0.16937 | 0.96588 | 1.2131 | 0.35706 | 1.3092 | 0.45319 | -0.054931 | -0.022888 | -122.7493 | 0.045777 | 0.21057 | -0.054931 | 0.2655 | 0 | 1.062 | 122.7402 | 0.10071 | 0.11902 | 122.8317 | 122.8455 | 122.7356 | 122.7905 | -122.9095 | -122.8683 | 122.644 | 0.064087 | 2.2385 | 1.2726
1521.1719 | 122.9874 | -57.2754 | 65.6708 | -0.03006 | 0.0012625 | 0.061171 | 0.076095 | -0.0015488 | 0.0034735 | 0.007558 | 0.001709 | 0.00067495 | 0.0029906 | -0.0050672 | -0.0051377 | -0.0060071 | 2.554e-05 | -55.0232 | 65.6296 | -57.2937 | 65.387 | -56.3278 | -56.9275 | -56.044 | -56.0394 | 65.6845 | -57.2479 | -57.1609 | -57.3807 | -57.3853 | -57.0236 | -0.01831 | -0.041198 | -0.28381 | 0.94757 | 1.2314 | 0.3479 | 1.2497 | 0.36621 | 0.027466 | 0.013733 | -122.8317 | -0.10529 | 0.25177 | -0.10986 | 0.2243 | -0.13733 | 0.96588 | 122.6807 | -0.13275 | 0.086975 | 122.9233 | 122.9324 | 122.905 | 122.9599 | -122.9645 | -122.9187 | 122.6624 | 0.11444 | 2.2522 | 1.236
1522.1719 | 122.937 | -57.2525 | 65.625 | -0.11398 | 0.00083526 | 0.065657 | 0.07524 | 0.00016017 | 0.0028327 | 0.010976 | -0.077637 | -0.00039305 | 0.00042723 | 0.007323 | -0.0032151 | -0.00066648 | 0.00023934 | -55.0278 | 65.5884 | -57.3441 | 65.3549 | -56.3873 | -57.0145 | -56.1264 | -56.1172 | 65.6433 | -57.2891 | -57.2479 | -57.312 | -57.4219 | -57.0786 | -0.091553 | -0.036621 | -0.27008 | 0.86517 | 1.1261 | 0.23804 | 1.2177 | 0.32959 | -0.036622 | 0.018311 | -122.8729 | -0.05951 | 0.17395 | -0.16937 | 0.21057 | -0.13275 | 0.95673 | 122.699 | -0.022888 | 0.041199 | 122.9324 | 122.9324 | 122.8409 | 122.8958 | -122.9691 | -122.9141 | 122.6074 | 0.004577 | 2.2247 | 1.1353
1523.1719 | 122.9874 | -57.2342 | 65.6479 | -0.014801 | 0.00083526 | 0.06288 | 0.075881 | 0.00037377 | 0.0026191 | 0.0084124 | 0.023071 | 0.00024775 | -0.0014954 | -0.00015378 | -0.00022431 | -0.0047253 | -0.0025379 | -55.014 | 65.6479 | -57.2662 | 65.3961 | -56.3461 | -56.9275 | -56.0623 | -56.0532 | 65.6616 | -57.2662 | -57.2021 | -57.2342 | -57.3349 | -57.0282 | -0.032043 | 0 | -0.25177 | 0.88806 | 1.1719 | 0.3067 | 1.2039 | 0.33875 | -0.032043 | 0.013733 | -122.85 | 0 | 0.20599 | -0.10071 | 0.23804 | -0.068665 | 0.9201 | 122.6624 | 0.032043 | 0.064087 | 122.9141 | 122.9279 | 122.8821 | 122.8958 | -122.9141 | -122.9141 | 122.6303 | 0.032044 | 2.2202 | 1.181
1524.1719 | 122.9507 | -57.2342 | 65.6525 | -0.060578 | -0.00023294 | 0.061598 | 0.073104 | -0.0038986 | 0.0028327 | 0.0060626 | 0.02002 | 0.0025975 | -0.00042717 | -0.0020764 | 0.00063009 | -0.0028027 | -0.0042469 | -55.0095 | 65.6158 | -57.2937 | 65.3824 | -56.3232 | -56.9138 | -56.0349 | -56.044 | 65.6525 | -57.2525 | -57.2159 | -57.225 | -57.3166 | -57.0374 | -0.059509 | -0.036621 | -0.27008 | 0.91095 | 1.1993 | 0.32044 | 1.2588 | 0.37994 | -0.01831 | 0 | -122.8683 | 0.009155 | 0.19684 | -0.082397 | 0.21515 | -0.064087 | 0.97046 | 122.6761 | 0.027465 | 0.036621 | 122.9095 | 122.905 | 122.85 | 122.8867 | -122.9462 | -122.905 | 122.6166 | 0.018311 | 2.2247 | 1.1902
1525.1719 | 123.0103 | -57.2021 | 65.6387 | -0.10635 | 0.00040806 | 0.062239 | 0.073318 | 0.0010148 | 0.0030463 | 0.0086262 | 0.03833 | 0.0017431 | 2.8e-08 | -0.002931 | -0.0015061 | -0.0023755 | -0.00040166 | -54.9591 | 65.5746 | -57.2708 | 65.4831 | -56.2225 | -56.8359 | -55.9799 | -55.9341 | 65.6479 | -57.2571 | -57.1426 | -57.1426 | -57.2342 | -56.9641 | -0.068665 | -0.064087 | -0.15564 | 0.97961 | 1.2222 | 0.36621 | 1.2909 | 0.43488 | -0.054932 | 0.009155 | -122.7814 | 0.059509 | 0.23804 | -0.032044 | 0.29297 | 0.022888 | 1.0483 | 122.7539 | 0.11444 | 0.11444 | 122.8455 | 122.905 | 122.7768 | 122.85 | -122.9095 | -122.8958 | 122.6852 | 0.059509 | 2.243 | 1.268
1526.1719 | 123.0606 | -57.193 | 65.593 | -0.083466 | 0.0014761 | 0.063307 | 0.074813 | 0.0029374 | 0.0036871 | 0.0073444 | 0.044434 | -0.00039305 | 0.00021363 | -0.0044262 | -0.0030013 | -0.0051527 | 0.00045294 | -54.9408 | 65.5792 | -57.2525 | 65.5289 | -56.1722 | -56.8039 | -55.9662 | -55.8929 | 65.5884 | -57.2021 | -57.1701 | -57.3212 | -57.1747 | -56.8771 | -0.059509 | -0.013733 | -0.064087 | 1.0208 | 1.2268 | 0.3891 | 1.2863 | 0.44861 | -0.009155 | -0.004578 | -122.7631 | -0.12817 | 0.31586 | 0.01831 | 0.32501 | 0.027465 | 1.0803 | 122.7814 | -0.11902 | 0.032043 | 122.8317 | 122.7905 | 122.7722 | 122.7814 | -122.8455 | -122.7951 | 122.7219 | 0.022888 | 2.2522 | 1.3
1527.1719 | 122.9416 | -57.28 | 65.6296 | -0.075836 | 0.0010489 | 0.063307 | 0.078658 | 0.00058737 | 0.0032599 | 0.010976 | -0.074585 | 0.00024775 | 0.0019226 | 5.9824e-05 | -0.0023605 | -0.0025891 | -0.0010425 | -55.0323 | 65.5884 | -57.3212 | 65.3412 | -56.4239 | -57.019 | -56.1401 | -56.131 | 65.6479 | -57.3074 | -57.2662 | -57.3212 | -57.4402 | -57.0923 | -0.041199 | -0.041199 | -0.28839 | 0.85602 | 1.1398 | 0.26092 | 1.181 | 0.30212 | -0.027466 | 0.01831 | -122.8958 | -0.041199 | 0.18768 | -0.16022 | 0.21515 | -0.13275 | 0.89722 | 122.6624 | -0.013733 | 0.041199 | 122.9095 | 122.9553 | 122.8683 | 122.9279 | -122.9507 | -122.937 | 122.6212 | 0.013733 | 2.2476 | 1.149
1528.1719 | 123.0148 | -57.2159 | 65.6479 | -0.098725 | 0.0010489 | 0.063094 | 0.071822 | 0.0012284 | 0.0043281 | 0.0049946 | 0.041382 | 0.0013159 | -0.0019226 | -0.0044262 | -0.0023605 | -0.0028027 | 0.0023755 | -54.9637 | 65.593 | -57.2662 | 65.4831 | -56.2546 | -56.8451 | -55.9891 | -55.9753 | 65.625 | -57.2525 | -57.1793 | -57.1793 | -57.2525 | -56.9778 | -0.050354 | -0.054931 | -0.16479 | 0.9613 | 1.2268 | 0.37079 | 1.2772 | 0.42114 | -0.036621 | -0.022888 | -122.8271 | 0.036621 | 0.23804 | -0.036621 | 0.27466 | 0 | 1.0117 | 122.7493 | 0.073242 | 0.073242 | 122.8592 | 122.8775 | 122.8088 | 122.8409 | -122.9141 | -122.9004 | 122.699 | 0.036621 | 2.2522 | 1.2405
1529.1719 | 123.0423 | -57.2113 | 65.6067 | -0.075836 | -0.00023294 | 0.062239 | 0.073745 | 0.00080117 | 0.0045417 | 0.0067036 | 0.029175 | 3.4148e-05 | -0.0010682 | 0.00091422 | -0.0015061 | -0.0036573 | 2.554e-05 | -54.9683 | 65.5792 | -57.2433 | 65.5014 | -56.2225 | -56.8314 | -55.9753 | -55.9433 | 65.6525 | -57.2342 | -57.1564 | -57.1518 | -57.2571 | -56.9733 | -0.032043 | -0.027465 | -0.10529 | 0.98877 | 1.236 | 0.37994 | 1.268 | 0.41199 | -0.022888 | 0.045777 | -122.7631 | 0.05951 | 0.23804 | -0.045776 | 0.26093 | -0.022888 | 1.0208 | 122.7448 | 0.082398 | 0.07782 | 122.8226 | 122.8867 | 122.7905 | 122.8638 | -122.85 | -122.8409 | 122.7127 | 0.054932 | 2.243 | 1.268
1530.1719 | 122.9553 | -57.2433 | 65.6479 | -0.037689 | 0.0014761 | 0.062453 | 0.072036 | -0.00026703 | 0.0026191 | 0.0064898 | 0.010864 | 0.0032385 | 2.8e-08 | -0.010194 | -0.00086511 | -0.0036573 | -0.0027515 | -54.9683 | 65.6158 | -57.2708 | 65.4282 | -56.2912 | -56.8863 | -56.0349 | -56.0028 | 65.6479 | -57.2571 | -57.1976 | -57.2159 | -57.3257 | -57.0236 | -0.027466 | -0.032043 | -0.21973 | 0.95215 | 1.2085 | 0.35706 | 1.236 | 0.38452 | -0.013733 | 0 | -122.8455 | 0.027466 | 0.21973 | -0.082398 | 0.23346 | -0.068665 | 0.97961 | 122.699 | 0.041199 | 0.059509 | 122.8867 | 122.905 | 122.8592 | 122.8912 | -122.9187 | -122.905 | 122.6715 | 0.045776 | 2.2751 | 1.2405
1531.1719 | 122.9782 | -57.2159 | 65.6616 | -0.091095 | 0.00019446 | 0.063307 | 0.073104 | 0.0022964 | 0.0015509 | 0.0062762 | 0.023071 | 0.00024775 | 0.0021362 | 0.0030506 | -0.0021469 | -0.0021619 | -0.0023243 | -54.9454 | 65.5975 | -57.2662 | 65.4419 | -56.2683 | -56.8634 | -56.0028 | -55.9937 | 65.6616 | -57.2479 | -57.193 | -57.2067 | -57.3166 | -57.0145 | -0.050354 | -0.064087 | -0.21973 | 0.94757 | 1.2131 | 0.35248 | 1.2634 | 0.40283 | -0.032044 | 0 | -122.8546 | 0.009155 | 0.20142 | -0.10071 | 0.23346 | -0.068664 | 0.99792 | 122.7081 | 0.041199 | 0.054932 | 122.8638 | 122.9095 | 122.8134 | 122.8775 | -122.9279 | -122.9095 | 122.6578 | 0.022888 | 2.2705 | 1.2222
1532.1719 | 123.1293 | -57.193 | 65.625 | -0.083466 | 0.0016899 | 0.063948 | 0.074172 | -0.0021896 | 0.00069649 | 0.0084124 | 0.044434 | 0.00046135 | 0.001068 | 0.001128 | -0.0025741 | -0.0040845 | -0.0018971 | -54.9591 | 65.5609 | -57.2662 | 65.5014 | -56.2042 | -56.8222 | -55.9479 | -55.9021 | 65.6067 | -57.2113 | -57.0969 | -57.1014 | -57.1793 | -56.9412 | -0.073242 | -0.064087 | -0.1236 | 0.98877 | 1.2451 | 0.37079 | 1.3184 | 0.44403 | -0.018311 | -0.018311 | -122.7219 | 0.091553 | 0.25177 | 0.013733 | 0.27008 | 0.032044 | 1.062 | 122.7676 | 0.10986 | 0.11444 | 122.8271 | 122.818 | 122.7539 | 122.7997 | -122.8912 | -122.8363 | 122.6944 | 0.09613 | 2.2339 | 1.2909
1533.1719 | 123.0927 | -57.1976 | 65.5746 | -0.098725 | 0.00062166 | 0.061598 | 0.07289 | 0.00058737 | 0.0019781 | 0.0094806 | 0.059692 | -0.00039305 | -0.00021357 | -0.0016492 | -0.0012925 | -0.0036573 | -0.00082886 | -54.9911 | 65.5746 | -57.2754 | 65.4877 | -56.2546 | -56.8634 | -55.9753 | -55.9296 | 65.5838 | -57.2205 | -57.0969 | -57.1106 | -57.1884 | -56.9504 | -0.07782 | 0 | -0.086975 | 0.94299 | 1.2222 | 0.33417 | 1.3 | 0.41199 | -0.022888 | 0.009155 | -122.6715 | 0.086975 | 0.24719 | 0.009155 | 0.27008 | 0.032043 | 1.0208 | 122.7631 | 0.10986 | 0.1236 | 122.85 | 122.8043 | 122.7722 | 122.7814 | -122.85 | -122.7951 | 122.6852 | 0.10071 | 2.2064 | 1.268
1534.1719 | 123.0972 | -57.1793 | 65.6204 | -0.060578 | 0.00019446 | 0.061171 | 0.075454 | -0.0013352 | 0.0024053 | 0.0049946 | 0.047485 | 3.4148e-05 | -0.00021357 | 0.003905 | -0.0023605 | -0.0055799 | -0.0033923 | -54.9454 | 65.5563 | -57.2479 | 65.5243 | -56.1905 | -56.813 | -55.9341 | -55.8701 | 65.6067 | -57.2205 | -57.1289 | -57.1106 | -57.2067 | -56.9275 | -0.068665 | -0.064087 | -0.09613 | 0.98877 | 1.2451 | 0.36621 | 1.3138 | 0.43488 | -0.041199 | -0.013733 | -122.7493 | 0.068664 | 0.25177 | -0.027466 | 0.29297 | 0.013733 | 1.0574 | 122.7722 | 0.10986 | 0.091553 | 122.8043 | 122.8271 | 122.7356 | 122.7859 | -122.8683 | -122.8409 | 122.7036 | 0.050354 | 2.2339 | 1.3092
1535.1719 | 123.0286 | -57.2067 | 65.6296 | -0.014801 | 0.0027579 | 0.064162 | 0.074813 | -0.00048063 | 0.0021917 | 0.0064898 | 0.0047608 | 0.0019567 | 0.00021363 | -0.00464 | -0.0023605 | -0.0036573 | -0.0031787 | -54.95 | 65.593 | -57.2754 | 65.4785 | -56.2546 | -56.8542 | -55.9708 | -55.9525 | 65.6616 | -57.2479 | -57.1518 | -57.1701 | -57.2708 | -56.9824 | -0.068665 | -0.036621 | -0.15106 | 0.95215 | 1.236 | 0.35248 | 1.3046 | 0.42114 | -0.041199 | 0.032043 | -122.7814 | 0.036621 | 0.2243 | -0.064087 | 0.2655 | -0.022888 | 1.0208 | 122.7539 | 0.07782 | 0.096131 | 122.8683 | 122.9095 | 122.7997 | 122.8683 | -122.905 | -122.8775 | 122.6852 | 0.054932 | 2.2568 | 1.2543
1536.1719 | 122.9828 | -57.2205 | 65.6158 | -0.12924 | 0.0021171 | 0.062453 | 0.071822 | -0.001976 | 0.0019781 | 0.0073444 | 0.0047608 | 0.0015295 | -0.00021357 | -0.0037854 | 0.00063009 | -0.0042981 | -0.0010425 | -54.9957 | 65.5975 | -57.2571 | 65.4282 | -56.3049 | -56.9138 | -56.0532 | -56.0028 | 65.657 | -57.2525 | -57.2067 | -57.225 | -57.3257 | -57.0465 | -0.036621 | -0.018311 | -0.18768 | 0.91553 | 1.1673 | 0.3067 | 1.2039 | 0.34332 | -0.032043 | 0.041198 | -122.8226 | -0.004578 | 0.17395 | -0.10529 | 0.20599 | -0.073243 | 0.95215 | 122.6852 | 0.027465 | 0.045776 | 122.8546 | 122.9095 | 122.818 | 122.8775 | -122.8729 | -122.8683 | 122.6486 | 0.013733 | 2.2247 | 1.2177
1537.1719 | 123.0835 | -57.2021 | 65.6067 | -0.10635 | 0.0012625 | 0.063521 | 0.075881 | -0.0024032 | 0.0030463 | 0.0096942 | 0.065796 | 0.00067495 | -0.0021362 | -0.0018628 | -0.0030013 | -0.0021619 | 0.0023755 | -54.9545 | 65.5609 | -57.2433 | 65.506 | -56.2134 | -56.8222 | -55.9479 | -55.8701 | 65.5975 | -57.2205 | -57.1106 | -57.1106 | -57.2021 | -56.955 | -0.041199 | -0.045776 | -0.10071 | 0.98877 | 1.2543 | 0.37994 | 1.2955 | 0.42114 | -0.018311 | -0.009155 | -122.7173 | 0.091552 | 0.24719 | 0 | 0.2655 | 0.018311 | 1.03 | 122.7493 | 0.10986 | 0.10986 | 122.8043 | 122.818 | 122.7631 | 122.7997 | -122.85 | -122.8271 | 122.7081 | 0.091552 | 2.2476 | 1.3321
1538.1719 | 123.111 | -57.1884 | 65.5884 | -0.052948 | -1.9142e-05 | 0.062239 | 0.075027 | -0.00090783 | 0.0045417 | 0.0060626 | 0.032227 | 0.0017431 | 0.0021362 | -0.00058098 | -0.0021469 | -0.0042981 | -0.0012561 | -54.9683 | 65.5746 | -57.2845 | 65.4785 | -56.2454 | -56.868 | -55.9708 | -55.8884 | 65.5975 | -57.2388 | -57.106 | -57.0969 | -57.2021 | -56.9229 | -0.09613 | -0.013733 | -0.10986 | 0.94299 | 1.2177 | 0.32043 | 1.3138 | 0.41656 | -0.050354 | 0.009155 | -122.6944 | 0.091553 | 0.2655 | -0.013732 | 0.31586 | 0.036622 | 1.0391 | 122.7631 | 0.14191 | 0.13275 | 122.8592 | 122.8363 | 122.7631 | 122.7859 | -122.8729 | -122.8271 | 122.6669 | 0.082398 | 2.2202 | 1.3
1539.1719 | 123.0927 | -57.1884 | 65.5838 | -0.052948 | 0.00019446 | 0.062453 | 0.071395 | 0.003151 | 0.0028327 | 0.0073444 | 0.023071 | 0.0011023 | -0.0010682 | 0.001128 | -0.0021469 | -0.0023755 | 0.00023934 | -54.9774 | 65.5472 | -57.2754 | 65.4648 | -56.2775 | -56.8817 | -55.9753 | -55.9296 | 65.5975 | -57.2571 | -57.1106 | -57.1198 | -57.2205 | -56.9321 | -0.086975 | -0.036621 | -0.11902 | 0.91095 | 1.2131 | 0.3067 | 1.3 | 0.39368 | -0.068664 | 0.013733 | -122.6944 | 0.068665 | 0.25635 | -0.032043 | 0.32501 | 0.036621 | 0.99793 | 122.7402 | 0.13733 | 0.14648 | 122.8226 | 122.8546 | 122.7356 | 122.7859 | -122.8592 | -122.8409 | 122.6532 | 0.07782 | 2.211 | 1.2589
1540.1719 | 123.0515 | -57.2433 | 65.5975 | -0.1445 | 0.00040806 | 0.061598 | 0.073104 | -0.001976 | 0.0034735 | 0.0096942 | 0.013916 | -0.00017945 | -0.00042717 | -0.0018628 | -0.00043791 | -0.0017347 | -0.0010425 | -55.0186 | 65.5563 | -57.2937 | 65.4556 | -56.2042 | -56.9275 | -56.0944 | -56.0303 | 65.6021 | -57.2571 | -57.1609 | -57.1747 | -57.2983 | -56.9824 | -0.050354 | -0.041199 | -0.14191 | 1.0391 | 1.149 | 0.31586 | 1.1993 | 0.36621 | -0.013733 | 0.004578 | -122.7585 | 0.068664 | 0.26093 | -0.054932 | 0.27466 | -0.041199 | 1.0895 | 122.7493 | 0.082397 | 0.09613 | 122.85 | 122.8592 | 122.7997 | 122.8455 | -122.8912 | -122.8546 | 122.699 | 0.082397 | 2.2247 | 1.2131
1541.1719 | 123.0927 | -57.2159 | 65.5746 | -0.075836 | -0.00044654 | 0.063948 | 0.072677 | -0.0017624 | 0.0024053 | 0.0096942 | 0.029175 | 0.00024775 | 0.0014954 | -0.001222 | -0.0032151 | -0.0025891 | 0.0025891 | -54.9683 | 65.5518 | -57.2845 | 65.4831 | -56.25 | -56.868 | -55.9753 | -55.9021 | 65.6113 | -57.225 | -57.0969 | -57.106 | -57.1976 | -56.9275 | -0.068665 | -0.022888 | -0.091553 | 0.96588 | 1.2405 | 0.3479 | 1.3092 | 0.41656 | -0.009156 | 0.036621 | -122.6715 | 0.10986 | 0.28839 | 0.01831 | 0.29755 | 0.027466 | 1.0345 | 122.7676 | 0.11902 | 0.12817 | 122.8363 | 122.8363 | 122.7676 | 122.8271 | -122.8592 | -122.7997 | 122.699 | 0.11902 | 2.2476 | 1.3138
1542.1719 | 122.9599 | -57.2021 | 65.5746 | -0.075836 | -0.00066014 | 0.063948 | 0.075027 | -0.00090783 | 0.0043281 | 0.0045672 | 0.010864 | -0.00017945 | 0.0025634 | -0.0014356 | -0.0025741 | -0.0017347 | -0.0012561 | -54.9362 | 65.5655 | -57.2571 | 65.5243 | -56.2042 | -56.813 | -55.925 | -55.9021 | 65.6342 | -57.2388 | -57.2388 | -56.8405 | -56.9824 | -56.9321 | -0.054932 | -0.009155 | -0.050354 | 0.99792 | 1.2772 | 0.3891 | 1.3321 | 0.44403 | -0.036622 | 0.059509 | -122.8134 | 0.36163 | 0.27008 | 0.21973 | 0.3067 | 0.25635 | 1.0529 | 122.7814 | 0.39825 | 0 | 122.8226 | 122.8729 | 122.7676 | 122.8363 | -122.8317 | -122.8134 | 122.7264 | -0.036622 | 2.2659 | 1.3
1543.1719 | 123.0972 | -57.2021 | 65.5884 | -0.052948 | -0.00066014 | 0.063094 | 0.073958 | -0.0024032 | 0.0045417 | 0.005849 | 0.03833 | 3.4148e-05 | 0.001068 | 0.0032642 | -0.0012925 | -0.0040845 | -0.00018806 | -54.9637 | 65.5518 | -57.2662 | 65.5106 | -56.2225 | -56.8268 | -55.9753 | -55.8609 | 65.6021 | -57.2433 | -57.0786 | -57.0877 | -57.1976 | -56.9321 | -0.064087 | -0.036621 | -0.07782 | 0.97961 | 1.2268 | 0.37537 | 1.2909 | 0.43945 | -0.041199 | 0.013733 | -122.6669 | 0.11444 | 0.27008 | 0.004577 | 0.31128 | 0.045776 | 1.0437 | 122.7768 | 0.15564 | 0.16479 | 122.818 | 122.8455 | 122.7539 | 122.8043 | -122.8546 | -122.8317 | 122.7127 | 0.1236 | 2.2385 | 1.3412
1544.1719 | 123.0606 | -57.2205 | 65.5792 | -0.068207 | 0.00083526 | 0.061812 | 0.075027 | 0.00251 | 0.0045417 | 0.0081988 | 0.013916 | 0.0017431 | 0.001709 | 0.0019824 | -0.0021469 | -0.0028027 | 0.00088014 | -55.0049 | 65.5563 | -57.28 | 65.4327 | -56.3278 | -56.9138 | -56.0303 | -55.9753 | 65.6067 | -57.2662 | -57.1381 | -57.1381 | -57.2479 | -56.9595 | -0.059509 | -0.022889 | -0.14648 | 0.89264 | 1.1902 | 0.3067 | 1.2497 | 0.36621 | -0.045776 | 0.027465 | -122.7173 | 0.082397 | 0.26093 | -0.027466 | 0.3067 | 0.01831 | 0.95215 | 122.7127 | 0.12817 | 0.12817 | 122.8363 | 122.8729 | 122.7768 | 122.8271 | -122.8592 | -122.8455 | 122.6532 | 0.082397 | 2.2156 | 1.2451
1545.1719 | 123.0972 | -57.193 | 65.593 | -0.083466 | -0.00087374 | 0.063307 | 0.074172 | -0.0021896 | 0.0047553 | 0.0079852 | 0.02002 | 0.00067495 | -0.00021357 | -0.001222 | -0.0017197 | -0.0015211 | -0.0025379 | -54.9911 | 65.5838 | -57.2891 | 65.4785 | -56.2637 | -56.8497 | -55.9845 | -55.9387 | 65.5746 | -57.2571 | -57.106 | -57.1106 | -57.1884 | -56.9458 | -0.096131 | -0.009156 | -0.11444 | 0.92926 | 1.2085 | 0.34332 | 1.3046 | 0.43945 | -0.064087 | -0.018311 | -122.699 | 0.082397 | 0.24719 | 0.004577 | 0.31128 | 0.068664 | 1.0254 | 122.7676 | 0.14648 | 0.15106 | 122.8729 | 122.8317 | 122.7768 | 122.7676 | -122.8821 | -122.85 | 122.6715 | 0.086975 | 2.2018 | 1.2543
1546.1719 | 123.0377 | -57.2296 | 65.5655 | -0.12924 | -0.00066014 | 0.062239 | 0.074386 | 0.003151 | 0.0041143 | 0.0067036 | -0.0013428 | -0.00039305 | -0.00021357 | -0.0018628 | -0.00022431 | -0.0025891 | -0.0012561 | -55.0278 | 65.5563 | -57.3212 | 65.4282 | -56.3416 | -56.9412 | -56.044 | -56.0211 | 65.5975 | -57.2845 | -57.1793 | -57.193 | -57.312 | -56.9916 | -0.091553 | -0.009156 | -0.13733 | 0.88806 | 1.1856 | 0.28839 | 1.2772 | 0.37994 | -0.054932 | 0.032043 | -122.7448 | 0.036621 | 0.23804 | -0.082398 | 0.29297 | -0.027466 | 0.97961 | 122.7493 | 0.091553 | 0.10529 | 122.8775 | 122.8821 | 122.7859 | 122.8271 | -122.8867 | -122.85 | 122.6578 | 0.050354 | 2.2018 | 1.2085
1547.1719 | 123.0377 | -57.2342 | 65.5655 | -0.11398 | 0.0010489 | 0.063734 | 0.074172 | -0.0017624 | 0.0034735 | 0.0081988 | 0.0078126 | -0.00017945 | -0.00064077 | 0.0043322 | -0.0012925 | -0.0045117 | -0.0027515 | -55.0186 | 65.5701 | -57.2891 | 65.4282 | -56.2592 | -56.7947 | -56.0303 | -56.0349 | 65.5792 | -57.2662 | -57.1793 | -57.1701 | -57.2891 | -56.987 | -0.054932 | 0.004577 | -0.13733 | 0.97504 | 1.2039 | 0.43945 | 1.2589 | 0.49439 | -0.032043 | 0.013733 | -122.7448 | 0.064087 | 0.24719 | -0.054932 | 0.27923 | -0.022889 | 1.03 | 122.7173 | 0.09613 | 0.086975 | 122.8592 | 122.8455 | 122.8043 | 122.8134 | -122.8546 | -122.8317 | 122.6624 | 0.054932 | 2.2156 | 1.1993
1548.1719 | 123.0606 | -57.2205 | 65.593 | -0.060578 | 0.00040806 | 0.063521 | 0.074813 | -0.0013352 | 0.0047553 | 0.0081988 | -0.0013428 | 0.00067495 | -0.0019226 | -0.00079478 | -0.0017197 | -0.0015211 | -0.0027515 | -55.0049 | 65.5472 | -57.3212 | 65.4373 | -56.3004 | -56.9138 | -56.0165 | -55.9753 | 65.593 | -57.2571 | -57.1381 | -57.1472 | -57.2433 | -56.9733 | -0.10071 | -0.045777 | -0.15564 | 0.9201 | 1.2039 | 0.3067 | 1.3046 | 0.40741 | -0.036621 | 0 | -122.731 | 0.073242 | 0.24719 | -0.022888 | 0.28381 | 0.013733 | 1.0208 | 122.7585 | 0.10986 | 0.11902 | 122.8683 | 122.85 | 122.7676 | 122.8134 | -122.9141 | -122.85 | 122.6578 | 0.082397 | 2.2156 | 1.2451
1549.1719 | 123.0743 | -57.2296 | 65.5838 | -0.098725 | -0.00066014 | 0.062453 | 0.073958 | 0.00037377 | 0.0017645 | 0.0079852 | 0.0047608 | 0.00067495 | 0.00042723 | -0.00036738 | -0.0019333 | -0.0047253 | 0.0017345 | -55.0323 | 65.5655 | -57.3166 | 65.4419 | -56.3324 | -56.9046 | -56.0211 | -55.9753 | 65.5884 | -57.2525 | -57.1426 | -57.1381 | -57.2525 | -56.9687 | -0.086975 | -0.01831 | -0.14191 | 0.89722 | 1.2085 | 0.32501 | 1.2955 | 0.41199 | -0.022888 | 0.004578 | -122.7264 | 0.091552 | 0.26093 | -0.022888 | 0.28381 | 0 | 0.98419 | 122.7585 | 0.11444 | 0.10986 | 122.8821 | 122.8409 | 122.7951 | 122.818 | -122.9004 | -122.8363 | 122.6715 | 0.086975 | 2.1973 | 1.2543
1550.1719 | 123.1293 | -57.1976 | 65.5746 | -0.091095 | 0.0016899 | 0.063734 | 0.074813 | -0.0021896 | 0.0021917 | 0.0081988 | 0.010864 | 0.0011023 | 0.001068 | 0.0066822 | -0.0017197 | -0.0047253 | 0.00066654 | -55.0095 | 65.5838 | -57.2891 | 65.4694 | -56.2866 | -56.868 | -55.9937 | -55.925 | 65.6021 | -57.2617 | -57.1106 | -57.1243 | -57.2067 | -56.9321 | -0.091553 | 0.009155 | -0.10529 | 0.91095 | 1.2039 | 0.32959 | 1.2955 | 0.42114 | -0.064087 | 0.027466 | -122.6852 | 0.073242 | 0.2655 | -0.009155 | 0.32959 | 0.054932 | 1.0025 | 122.7585 | 0.13733 | 0.15106 | 122.8729 | 122.8638 | 122.7814 | 122.7997 | -122.8638 | -122.8363 | 122.6669 | 0.086975 | 2.1881 | 1.2726
1551.1719 | 123.0972 | -57.2113 | 65.5746 | -0.045319 | 0.0012625 | 0.060103 | 0.074813 | -0.0041122 | 0.00069649 | 0.0069172 | -0.0043946 | -0.00017945 | 0.00042723 | -0.0014356 | -0.00065151 | -0.0010937 | 0.0023755 | -55.0095 | 65.5563 | -57.2708 | 65.4694 | -56.3095 | -56.8954 | -55.9845 | -55.957 | 65.625 | -57.2754 | -57.1014 | -57.1152 | -57.2296 | -56.9412 | -0.059509 | -0.018311 | -0.10529 | 0.90179 | 1.2268 | 0.31586 | 1.2863 | 0.37537 | -0.064087 | 0.050354 | -122.6761 | 0.096131 | 0.27008 | -0.01831 | 0.33417 | 0.045777 | 0.9613 | 122.7402 | 0.16022 | 0.17395 | 122.8271 | 122.9004 | 122.7676 | 122.8363 | -122.8455 | -122.85 | 122.6807 | 0.10986 | 2.2018 | 1.2543
1552.1719 | 123.1247 | -57.2021 | 65.5884 | -0.083466 | -0.00066014 | 0.061385 | 0.074599 | 0.00080117 | 0.0015509 | 0.0081988 | 0.010864 | -0.00039305 | -0.001709 | 0.0013416 | -0.0017197 | -0.0038709 | -0.0033923 | -54.9866 | 65.5746 | -57.2662 | 65.5197 | -56.2317 | -56.8359 | -55.9708 | -55.8884 | 65.5838 | -57.2342 | -57.0923 | -57.0877 | -57.193 | -56.9183 | -0.064087 | -0.013733 | -0.068665 | 0.97046 | 1.2314 | 0.36621 | 1.2955 | 0.4303 | -0.032044 | -0.004578 | -122.6807 | 0.11444 | 0.28381 | 0.009155 | 0.31586 | 0.041199 | 1.0345 | 122.7859 | 0.14648 | 0.14191 | 122.8409 | 122.818 | 122.7768 | 122.7859 | -122.8546 | -122.8226 | 122.7219 | 0.10986 | 2.2156 | 1.3138
1553.1719 | 123.024 | -57.2525 | 65.5472 | -0.10635 | 0.00062166 | 0.06288 | 0.074172 | -0.0024032 | 0.0021917 | 0.0079852 | 0.0078126 | -0.00060665 | -0.001709 | -0.0018628 | -0.0017197 | -0.0038709 | -0.0021107 | -55.0415 | 65.538 | -57.312 | 65.4144 | -56.337 | -56.9321 | -56.0532 | -55.9296 | 65.6296 | -57.2433 | -57.1472 | -57.193 | -57.3166 | -57.0007 | -0.05951 | -0.009155 | -0.13275 | 0.91553 | 1.1993 | 0.32043 | 1.2589 | 0.37994 | 0.009155 | 0.082398 | -122.6944 | 0.059509 | 0.25177 | -0.064087 | 0.24262 | -0.073242 | 0.97504 | 122.7264 | 0.050354 | 0.09613 | 122.85 | 122.8729 | 122.7905 | 122.8821 | -122.8592 | -122.7905 | 122.6669 | 0.10529 | 2.211 | 1.3229
1554.1719 | 123.0331 | -57.2296 | 65.5746 | -0.13687 | -0.00087374 | 0.061812 | 0.073958 | -0.0015488 | 0.0028327 | 0.009267 | -0.03186 | 0.00088875 | 0.00064083 | 0.002196 | -0.0023605 | -0.0028027 | 0.0021619 | -55.0232 | 65.4968 | -57.3029 | 65.4327 | -56.3278 | -56.9595 | -56.0669 | -56.0165 | 65.593 | -57.2662 | -57.1747 | -57.1884 | -57.3166 | -57.0099 | -0.073242 | -0.07782 | -0.14191 | 0.90179 | 1.1627 | 0.27008 | 1.236 | 0.34332 | -0.036621 | 0.018311 | -122.7493 | 0.041198 | 0.21973 | -0.086975 | 0.25635 | -0.050354 | 0.97504 | 122.7356 | 0.077819 | 0.091552 | 122.7997 | 122.8592 | 122.7264 | 122.8226 | -122.8775 | -122.8409 | 122.6624 | 0.054931 | 2.2064 | 1.2131
1555.1719 | 123.0743 | -57.2113 | 65.5884 | -0.15213 | -0.0015145 | 0.062025 | 0.075027 | -0.0026168 | 0.0017645 | 0.009267 | -0.0043946 | -0.0014613 | -0.0010682 | 0.0024096 | -0.0012925 | -0.0023755 | -0.00018806 | -55.0598 | 65.538 | -57.3074 | 65.4373 | -56.3278 | -56.9321 | -56.0257 | -55.9982 | 65.6204 | -57.2662 | -57.1564 | -57.1701 | -57.2662 | -56.987 | -0.09613 | -0.050354 | -0.15106 | 0.88348 | 1.1856 | 0.27924 | 1.2817 | 0.37537 | -0.054931 | 0.032043 | -122.7448 | 0.041199 | 0.2243 | -0.054931 | 0.27923 | 0 | 0.97961 | 122.7448 | 0.09613 | 0.10986 | 122.8455 | 122.8867 | 122.7493 | 122.8317 | -122.8958 | -122.8546 | 122.6486 | 0.054932 | 2.1515 | 1.2131
1556.1719 | 123.0469 | -57.2205 | 65.5792 | -0.068207 | -0.00066014 | 0.064375 | 0.074599 | -0.0026168 | 0.0041143 | 0.0073444 | -0.0043946 | 0.00024775 | -0.00064077 | 0.0019824 | -0.00022431 | -0.0034437 | -0.0021107 | -55.0461 | 65.5563 | -57.3166 | 65.4236 | -56.3416 | -56.9275 | -56.044 | -56.0165 | 65.5838 | -57.2708 | -57.1564 | -57.1564 | -57.2708 | -56.9824 | -0.09613 | -0.022889 | -0.15564 | 0.87891 | 1.1765 | 0.29297 | 1.2726 | 0.3891 | -0.050354 | 0.004577 | -122.7356 | 0.064087 | 0.23804 | -0.050354 | 0.28839 | 0 | 0.97504 | 122.7402 | 0.11444 | 0.11444 | 122.8729 | 122.8546 | 122.7768 | 122.8043 | -122.8958 | -122.85 | 122.644 | 0.064087 | 2.1744 | 1.2039
1557.1719 | 123.0377 | -57.2479 | 65.5563 | -0.13687 | 0.0010489 | 0.060957 | 0.074172 | -0.001976 | 0.0036871 | 0.009267 | -0.0074462 | 0.00046135 | -0.0014954 | -0.003999 | -0.00043791 | -0.0028027 | -0.0016833 | -54.9316 | 65.593 | -57.3074 | 65.4465 | -56.3461 | -56.9595 | -56.0486 | -56.0165 | 65.6067 | -57.2479 | -57.1609 | -57.1747 | -57.2708 | -56.9962 | -0.059509 | 0.036622 | -0.10986 | 0.90179 | 1.1993 | 0.28839 | 1.2589 | 0.3479 | 0 | 0.050354 | -122.7173 | 0.073242 | 0.25177 | -0.022888 | 0.25177 | -0.022888 | 0.9613 | 122.7539 | 0.073242 | 0.086975 | 122.9004 | 122.8546 | 122.8409 | 122.8546 | -122.8638 | -122.8043 | 122.6944 | 0.086975 | 2.3163 | 1.2314
1558.1719 | 123.1018 | -57.2159 | 65.5838 | -0.022431 | -0.00023294 | 0.063307 | 0.072677 | -0.00090783 | 0.0019781 | 0.0052082 | -0.01355 | -0.00082025 | -0.00042717 | 0.00048702 | -0.0040695 | -0.0047253 | 0.0010937 | -55.0323 | 65.5746 | -57.2891 | 65.4327 | -56.2958 | -56.9046 | -56.012 | -55.9525 | 65.625 | -57.2662 | -57.1289 | -57.1243 | -57.2296 | -56.9641 | -0.073243 | -0.009155 | -0.15106 | 0.92011 | 1.2039 | 0.31128 | 1.2772 | 0.38452 | -0.050354 | 0.041199 | -122.7127 | 0.091552 | 0.25177 | -0.013733 | 0.30212 | 0.036621 | 0.99335 | 122.7219 | 0.14191 | 0.13733 | 122.8638 | 122.8912 | 122.7905 | 122.8409 | -122.8729 | -122.85 | 122.6486 | 0.086975 | 2.1835 | 1.2634
1559.1719 | 123.0881 | -57.1793 | 65.5975 | -0.083466 | -0.00023294 | 0.063948 | 0.073958 | -0.00026703 | 0.0039007 | 0.0060626 | 0.016968 | 0.0032385 | -0.00042717 | -0.002931 | -0.0034287 | -0.0034437 | -0.0014697 | -55.0278 | 65.5609 | -57.3029 | 65.4327 | -56.3232 | -56.9 | -56.0257 | -55.9753 | 65.593 | -57.2662 | -57.1335 | -57.1381 | -57.2525 | -56.9733 | -0.1236 | -0.036621 | -0.16479 | 0.85602 | 1.1536 | 0.27924 | 1.2772 | 0.40283 | -0.086975 | -0.004577 | -122.731 | 0.041198 | 0.20599 | -0.073242 | 0.29297 | 0.013733 | 0.97961 | 122.7356 | 0.12817 | 0.13275 | 122.8638 | 122.8592 | 122.7402 | 122.7722 | -122.9004 | -122.8638 | 122.612 | 0.045776 | 2.1515 | 1.2039
1560.1719 | 123.0515 | -57.2433 | 65.6067 | -0.1445 | -0.00066014 | 0.063307 | 0.073104 | -0.004753 | 0.0051825 | 0.010121 | -0.0013428 | 0.00067495 | -0.001709 | 0.0013416 | -0.00043791 | -0.0038709 | 0.0019483 | -55.0415 | 65.5563 | -57.3074 | 65.4282 | -56.369 | -56.9595 | -56.0532 | -55.9067 | 65.6158 | -57.2708 | -57.193 | -57.1747 | -57.2937 | -57.0145 | -0.064087 | -0.050354 | -0.17853 | 0.87433 | 1.1902 | 0.28381 | 1.2543 | 0.3479 | -0.027466 | 0.009156 | -122.7997 | 0.068664 | 0.22888 | -0.050354 | 0.25635 | -0.022888 | 0.93841 | 122.7356 | 0.09613 | 0.07782 | 122.8638 | 122.8867 | 122.7997 | 122.8592 | -122.9141 | -122.8775 | 122.6715 | 0.050354 | 2.2018 | 1.3367
1561.1719 | 123.0331 | -57.2571 | 65.5655 | -0.1445 | -0.0013009 | 0.063094 | 0.07289 | -0.0021896 | 0.0056097 | 0.0064898 | -0.028809 | 0.00067495 | -0.00085457 | -0.0010084 | -0.0017197 | -0.0021619 | 2.554e-05 | -55.0369 | 65.5106 | -57.3257 | 65.4373 | -56.3461 | -56.955 | -56.0486 | -56.0028 | 65.5792 | -57.2891 | -57.1701 | -57.2113 | -57.3029 | -57.0099 | -0.068665 | -0.054932 | -0.12817 | 0.91095 | 1.2085 | 0.30212 | 1.2772 | 0.37079 | -0.032044 | 0.013733 | -122.7356 | 0.045776 | 0.24719 | -0.045776 | 0.27924 | -0.013732 | 0.97961 | 122.7631 | 0.07782 | 0.11902 | 122.8363 | 122.8683 | 122.7676 | 122.8363 | -122.8912 | -122.8546 | 122.6944 | 0.086975 | 2.2202 | 1.2543
1562.1719 | 123.0881 | -57.2433 | 65.5655 | -0.15213 | -0.00044654 | 0.065443 | 0.072677 | 0.0016556 | 0.0043281 | 0.0071308 | 0.0047608 | 0.00067495 | 0.0014954 | -0.00036738 | 0.00020289 | -0.0032301 | -0.00061526 | -55.069 | 65.5518 | -57.312 | 65.4419 | -56.3278 | -56.9183 | -56.044 | -55.9937 | 65.593 | -57.2479 | -57.1609 | -57.1564 | -57.2617 | -56.987 | -0.068665 | -0.013733 | -0.1236 | 0.91553 | 1.1993 | 0.32501 | 1.268 | 0.39368 | -0.004578 | 0.027466 | -122.7264 | 0.086975 | 0.25635 | -0.018311 | 0.26093 | -0.013733 | 0.98419 | 122.7539 | 0.091553 | 0.086975 | 122.8638 | 122.8409 | 122.7951 | 122.8363 | -122.8775 | -122.8134 | 122.6852 | 0.082397 | 2.1744 | 1.2497
1563.1719 | 123.0331 | -57.1976 | 65.5884 | -0.098725 | -0.00044654 | 0.062666 | 0.074813 | 0.00016017 | 0.0032599 | 0.007558 | -0.0074462 | -0.0010339 | 0.001709 | 0.0041186 | 0.00020289 | -0.0051527 | 0.0045117 | -55.0644 | 65.5472 | -57.3074 | 65.4236 | -56.337 | -56.9275 | -56.0303 | -56.0074 | 65.5975 | -57.2479 | -57.1609 | -57.1564 | -57.2708 | -56.9778 | -0.10986 | -0.041199 | -0.16479 | 0.8606 | 1.1673 | 0.27008 | 1.2772 | 0.37994 | -0.050354 | 0.009155 | -122.7493 | 0.041199 | 0.21973 | -0.073242 | 0.27008 | -0.022888 | 0.97046 | 122.731 | 0.091553 | 0.086975 | 122.8546 | 122.8455 | 122.7448 | 122.7951 | -122.8958 | -122.8363 | 122.6212 | 0.036621 | 2.1332 | 1.1902
1564.1719 | 123.0377 | -57.2113 | 65.5884 | -0.10635 | -0.00044654 | 0.061598 | 0.072463 | -0.0011214 | 0.0036871 | 0.0054218 | 0.0047608 | -0.00039305 | -0.0021362 | 0.00027342 | -0.00065151 | -0.0015211 | -0.0018971 | -54.9454 | 65.5655 | -57.2845 | 65.419 | -56.3324 | -56.9229 | -56.0532 | -55.9982 | 65.5884 | -57.2845 | -57.1701 | -57.1655 | -57.2754 | -56.9962 | -0.073242 | -0.022888 | -0.16937 | 0.87891 | 1.1581 | 0.28839 | 1.2314 | 0.36163 | -0.073242 | 0 | -122.7585 | 0.045777 | 0.21515 | -0.064087 | 0.28839 | 0.009155 | 0.95215 | 122.7036 | 0.11902 | 0.11444 | 122.85 | 122.8729 | 122.7768 | 122.7997 | -122.8729 | -122.8729 | 122.6303 | 0.041199 | 2.2659 | 1.2131
1565.1719 | 123.0652 | -57.193 | 65.5884 | -0.083466 | -0.0019417 | 0.062025 | 0.07289 | 0.00037377 | 0.0030463 | 0.010121 | -0.0013428 | -0.00039305 | 2.8e-08 | -0.0010084 | -0.0032151 | -0.0017347 | -0.0029651 | -55.0186 | 65.5655 | -57.2891 | 65.451 | -56.3187 | -56.8817 | -56.0165 | -55.9753 | 65.5884 | -57.28 | -57.1289 | -57.1426 | -57.2296 | -56.9595 | -0.096131 | -0.022888 | -0.13733 | 0.87433 | 1.1765 | 0.31128 | 1.2726 | 0.40741 | -0.086975 | 0 | -122.7173 | 0.050354 | 0.23346 | -0.036621 | 0.32043 | 0.050354 | 0.97046 | 122.7402 | 0.13733 | 0.15106 | 122.8546 | 122.8683 | 122.7585 | 122.7814 | -122.8775 | -122.8683 | 122.644 | 0.064087 | 2.1744 | 1.2177
1566.1719 | 123.056 | -57.2159 | 65.593 | -0.091095 | 0.00040806 | 0.062666 | 0.072677 | -0.0011214 | 0.0041143 | 0.010121 | -0.0013428 | -0.00060665 | 0.00021363 | 0.0015552 | -0.00043791 | -0.0040845 | 0.0015209 | -55.0415 | 65.5792 | -57.3212 | 65.4602 | -56.3416 | -56.8954 | -56.0165 | -55.9616 | 65.593 | -57.28 | -57.1198 | -57.1381 | -57.2342 | -56.9778 | -0.10529 | -0.013733 | -0.13275 | 0.87433 | 1.1993 | 0.32043 | 1.3046 | 0.42572 | -0.064087 | 0 | -122.7127 | 0.077819 | 0.23804 | -0.018311 | 0.30212 | 0.045776 | 0.97961 | 122.7814 | 0.14191 | 0.16022 | 122.9004 | 122.8729 | 122.7951 | 122.8088 | -122.9141 | -122.8729 | 122.6761 | 0.09613 | 2.1744 | 1.2543
1567.1719 | 123.056 | -57.2342 | 65.5563 | -0.13687 | 0.0014761 | 0.063094 | 0.074599 | -0.0015488 | 0.0026191 | 0.0073444 | -0.019653 | 0.00088875 | -0.0021362 | 0.001128 | 0.00041649 | -0.0036573 | -0.0018971 | -55.069 | 65.506 | -57.3212 | 65.419 | -56.3461 | -56.9641 | -56.0715 | -56.0028 | 65.5746 | -57.2662 | -57.1747 | -57.2021 | -57.2937 | -56.9916 | -0.086975 | -0.050354 | -0.13733 | 0.88806 | 1.1627 | 0.27008 | 1.2497 | 0.35706 | -0.032043 | 0.018311 | -122.731 | 0.032044 | 0.24262 | -0.059509 | 0.27466 | -0.027466 | 0.97504 | 122.7402 | 0.064087 | 0.091552 | 122.8271 | 122.8409 | 122.7402 | 122.8088 | -122.8775 | -122.8226 | 122.6532 | 0.059509 | 2.1652 | 1.2314
1568.1719 | 123.0515 | -57.2433 | 65.5472 | -0.19028 | -0.00087374 | 0.063948 | 0.073958 | 0.0012284 | 0.0049689 | 0.0081988 | -0.01355 | 0.0015295 | -0.0010682 | 0.003905 | 0.0012711 | -0.0023755 | -0.0023243 | -55.0461 | 65.5472 | -57.3303 | 65.4236 | -56.3416 | -56.9595 | -56.0532 | -56.0165 | 65.5609 | -57.28 | -57.1747 | -57.225 | -57.2891 | -57.0099 | -0.086975 | 0 | -0.1236 | 0.90179 | 1.1902 | 0.28381 | 1.2772 | 0.37079 | -0.036621 | 0.013733 | -122.7219 | 0.01831 | 0.23346 | -0.045777 | 0.27008 | -0.009156 | 0.98877 | 122.7539 | 0.054931 | 0.10528 | 122.8775 | 122.8409 | 122.7905 | 122.8043 | -122.8775 | -122.8271 | 122.6669 | 0.068664 | 2.1973 | 1.2268
1569.1719 | 123.0515 | -57.2159 | 65.5838 | -0.060578 | 0.0016899 | 0.062239 | 0.073958 | 0.0016556 | 0.0019781 | 0.0043536 | -0.0043946 | 0.00088875 | 0.00042723 | -0.002931 | -0.0036423 | -0.0032301 | 0.0015209 | -55.0598 | 65.5563 | -57.3212 | 65.4236 | -56.337 | -56.9183 | -56.0257 | -55.9845 | 65.5975 | -57.28 | -57.1655 | -57.1609 | -57.2662 | -56.9687 | -0.10529 | -0.027466 | -0.16022 | 0.87891 | 1.1902 | 0.29755 | 1.2955 | 0.40283 | -0.064087 | 0.013733 | -122.7493 | 0.054931 | 0.24719 | -0.050354 | 0.31128 | 0.013733 | 0.98419 | 122.7448 | 0.11902 | 0.11444 | 122.8775 | 122.8775 | 122.7722 | 122.8134 | -122.905 | -122.8638 | 122.6395 | 0.050354 | 2.1561 | 1.2314
1570.1719 | 123.0423 | -57.2113 | 65.5701 | -0.098725 | 0.0021171 | 0.063307 | 0.072677 | -5.343e-05 | 0.0034735 | 0.0077716 | 0.013916 | 0.0025975 | 2.8e-08 | -0.00079478 | -0.0019333 | -0.0023755 | -0.00061526 | -55.0415 | 65.538 | -57.3074 | 65.419 | -56.3644 | -56.9275 | -56.0394 | -56.0028 | 65.6067 | -57.2617 | -57.1655 | -57.1655 | -57.2708 | -57.0007 | -0.09613 | -0.032043 | -0.15106 | 0.84686 | 1.1719 | 0.28381 | 1.268 | 0.37994 | -0.050354 | 0.036621 | -122.7356 | 0.045777 | 0.21057 | -0.059509 | 0.26093 | -0.009155 | 0.94299 | 122.7264 | 0.096131 | 0.096131 | 122.8455 | 122.8683 | 122.7493 | 122.818 | -122.8775 | -122.8317 | 122.6303 | 0.045777 | 2.1698 | 1.2085
1571.1719 | 123.0789 | -57.2067 | 65.5838 | -0.060578 | -1.9142e-05 | 0.062666 | 0.073531 | -0.0011214 | 0.0017645 | 0.0069172 | 0.032227 | 0.0017431 | -0.00021357 | -0.0016492 | -0.00022431 | -0.0030163 | 0.0010937 | -55.0049 | 65.5426 | -57.2937 | 65.4694 | -56.3049 | -56.8863 | -56.012 | -55.9479 | 65.6021 | -57.2433 | -57.1243 | -57.1335 | -57.2113 | -56.9595 | -0.086975 | -0.041198 | -0.11444 | 0.90179 | 1.1948 | 0.32043 | 1.2817 | 0.40741 | -0.036621 | 0.018311 | -122.7081 | 0.073242 | 0.24719 | -0.004578 | 0.28381 | 0.032043 | 0.98877 | 122.7631 | 0.10986 | 0.11902 | 122.8363 | 122.8455 | 122.7493 | 122.8088 | -122.8775 | -122.8271 | 122.6761 | 0.082397 | 2.2018 | 1.2589
1572.1719 | 123.0789 | -57.225 | 65.5792 | -0.12161 | 0.00083526 | 0.063521 | 0.073745 | -0.0021896 | 0.0034735 | 0.010762 | 0.013916 | -0.00082025 | -0.00021357 | -0.0010084 | -0.00022431 | -0.0051527 | 0.0010937 | -55.0232 | 65.538 | -57.2845 | 65.4648 | -56.3187 | -56.9046 | -56.0303 | -55.9433 | 65.6021 | -57.28 | -57.1335 | -57.1335 | -57.2205 | -56.9504 | -0.059509 | -0.041199 | -0.11444 | 0.90637 | 1.1948 | 0.32044 | 1.2543 | 0.37994 | -0.054931 | 0.022888 | -122.7127 | 0.091553 | 0.27466 | 0.004578 | 0.32959 | 0.059509 | 0.96588 | 122.7493 | 0.14648 | 0.14648 | 122.8226 | 122.8821 | 122.7631 | 122.8271 | -122.8638 | -122.8592 | 122.6898 | 0.091553 | 2.2018 | 1.2817
1573.1719 | 123.0377 | -57.2388 | 65.5838 | -0.083466 | -0.0021555 | 0.061171 | 0.074172 | 0.00037377 | 0.0039007 | 0.0086262 | -0.0013428 | -0.00060665 | 0.00042723 | 0.0013416 | -0.0019333 | -0.0038709 | 0.00066654 | -55.0598 | 65.5426 | -57.3166 | 65.4419 | -56.2408 | -56.8542 | -56.0989 | -56.0074 | 65.5792 | -57.2662 | -57.1701 | -57.1884 | -57.3029 | -56.9778 | -0.077819 | -0.041198 | -0.14191 | 0.99793 | 1.1398 | 0.38452 | 1.2177 | 0.46234 | -0.027465 | -0.004577 | -122.7539 | 0.050354 | 0.26093 | -0.064086 | 0.28839 | -0.036621 | 1.0757 | 122.7585 | 0.077819 | 0.09613 | 122.8592 | 122.8455 | 122.7814 | 122.818 | -122.9004 | -122.85 | 122.6807 | 0.068665 | 2.179 | 1.2314
1574.1719 | 123.0423 | -57.2433 | 65.5563 | -0.052948 | 0.00040806 | 0.062239 | 0.075027 | -0.003685 | 0.0030463 | 0.005849 | -0.0013428 | -0.0033839 | 0.00064083 | -0.0031446 | -0.0025741 | -0.0034437 | 0.0010937 | -55.0552 | 65.5334 | -57.3212 | 65.419 | -56.369 | -56.9504 | -56.0669 | -55.8975 | 65.6204 | -57.2571 | -57.1564 | -57.193 | -57.3212 | -57.0282 | -0.07782 | -0.022888 | -0.13733 | 0.87433 | 1.1765 | 0.29297 | 1.2543 | 0.37079 | -0.013733 | 0.064087 | -122.7127 | 0.050354 | 0.21515 | -0.07782 | 0.22888 | -0.064087 | 0.95215 | 122.7402 | 0.064087 | 0.10071 | 122.8546 | 122.8775 | 122.7768 | 122.8638 | -122.8775 | -122.8134 | 122.6624 | 0.086975 | 2.1881 | 1.3458
1575.1719 | 123.0377 | -57.2433 | 65.5609 | -0.098725 | -0.00044654 | 0.063948 | 0.076308 | -0.0028304 | 0.0028327 | 0.0099078 | -0.034912 | 3.4148e-05 | -0.0019226 | -0.010194 | -0.0015061 | -0.0040845 | -0.0036059 | -55.0552 | 65.5151 | -57.3074 | 65.4053 | -56.3416 | -56.9687 | -56.0577 | -56.0028 | 65.5792 | -57.2479 | -57.1884 | -57.2113 | -57.2891 | -57.0053 | -0.064087 | -0.045776 | -0.15564 | 0.90179 | 1.1856 | 0.27466 | 1.2497 | 0.33875 | -0.004578 | 0.018311 | -122.7493 | 0.032043 | 0.23804 | -0.045777 | 0.24262 | -0.041199 | 0.96588 | 122.7127 | 0.036621 | 0.059509 | 122.8226 | 122.8271 | 122.7585 | 122.8226 | -122.8683 | -122.8088 | 122.6486 | 0.054931 | 2.1881 | 1.2405
1576.1719 | 123.0927 | -57.2113 | 65.5563 | -0.083466 | 0.0010489 | 0.063094 | 0.073531 | 0.0027238 | 0.00026909 | 0.0086262 | -0.010498 | 0.00067495 | 2.8e-08 | -0.001222 | -0.00043791 | -0.0025891 | -0.0033923 | -55.0095 | 65.5792 | -57.2891 | 65.4831 | -56.2637 | -56.868 | -56.0028 | -55.8929 | 65.5975 | -57.2388 | -57.1106 | -57.106 | -57.2021 | -56.9458 | -0.07782 | 0.022889 | -0.073242 | 0.94757 | 1.2085 | 0.34332 | 1.2863 | 0.42114 | -0.027466 | 0.041199 | -122.6669 | 0.10529 | 0.2655 | 0.009156 | 0.29297 | 0.036622 | 1.0254 | 122.7722 | 0.13275 | 0.12817 | 122.8683 | 122.8363 | 122.7905 | 122.8088 | -122.8455 | -122.7951 | 122.6944 | 0.10071 | 2.2018 | 1.3184
1577.1719 | 123.0789 | -57.2113 | 65.5792 | -0.12161 | 0.0021171 | 0.062025 | 0.074599 | -0.006462 | 0.0026191 | 0.010121 | 0.0047608 | -0.00039305 | 0.00021363 | -0.00036738 | 0.00041649 | -0.0036573 | -0.0014697 | -55.0095 | 65.5609 | -57.2845 | 65.4648 | -56.3095 | -56.8771 | -56.0165 | -55.9158 | 65.5975 | -57.2708 | -57.1106 | -57.1014 | -57.2067 | -56.9504 | -0.073242 | -0.018311 | -0.11444 | 0.90179 | 1.1948 | 0.33417 | 1.268 | 0.40741 | -0.059509 | 0.01831 | -122.6898 | 0.10986 | 0.26093 | 0.004578 | 0.32043 | 0.064087 | 0.97504 | 122.7493 | 0.16937 | 0.16022 | 122.8455 | 122.8683 | 122.7722 | 122.8088 | -122.8638 | -122.85 | 122.6761 | 0.10071 | 2.2018 | 1.2955
1578.1719 | 123.0835 | -57.1976 | 65.6616 | -0.10635 | 0.00040806 | 0.063948 | 0.073745 | -0.0013352 | 0.0013373 | 0.0084124 | 0.026123 | -0.0016749 | 0.00064083 | 0.0064684 | -0.0019333 | -0.0028027 | -0.0036059 | -54.9957 | 65.5884 | -57.2754 | 65.5197 | -56.25 | -56.8222 | -55.9708 | -55.8929 | 65.6387 | -57.2388 | -57.106 | -57.1106 | -57.2021 | -56.955 | -0.07782 | -0.073242 | -0.14191 | 0.94757 | 1.2268 | 0.37537 | 1.3046 | 0.45319 | -0.041199 | -0.022888 | -122.7676 | 0.086975 | 0.24262 | -0.004577 | 0.28381 | 0.036622 | 1.0254 | 122.7951 | 0.12817 | 0.13275 | 122.8638 | 122.8775 | 122.786 | 122.8363 | -122.937 | -122.9004 | 122.7173 | 0.091553 | 2.2018 | 1.3046
1579.1719 | 123.0194 | -57.2433 | 65.5746 | -0.052948 | 0.0014761 | 0.062453 | 0.074386 | -0.0017624 | 0.0060369 | 0.0088398 | -0.01355 | 3.4148e-05 | 0.0023498 | 0.00048702 | -0.00086511 | -0.0032301 | 0.0017345 | -55.0552 | 65.5563 | -57.3029 | 65.3915 | -56.369 | -56.9641 | -56.0623 | -56.0257 | 65.5975 | -57.2754 | -57.1518 | -57.1609 | -57.2983 | -57.0007 | -0.059509 | -0.018311 | -0.1831 | 0.87433 | 1.181 | 0.27924 | 1.2405 | 0.33874 | -0.032044 | 0.022888 | -122.7264 | 0.082397 | 0.24262 | -0.054932 | 0.27466 | -0.022888 | 0.93384 | 122.6944 | 0.11444 | 0.1236 | 122.8592 | 122.8729 | 122.7997 | 122.8409 | -122.8775 | -122.85 | 122.6349 | 0.091553 | 2.1881 | 1.2177
1580.1719 | 123.0606 | -57.225 | 65.5655 | -0.12924 | 0.0010489 | 0.064589 | 0.074813 | -5.343e-05 | 0.00091009 | 0.0045672 | -0.034912 | 0.0015295 | 0.00085443 | 0.0024096 | -0.0015061 | -0.0042981 | -0.0025379 | -55.069 | 65.5426 | -57.3074 | 65.4282 | -56.3782 | -56.8588 | -55.9708 | -56.0486 | 65.6158 | -57.2754 | -57.1838 | -57.1884 | -57.3029 | -56.9962 | -0.082397 | -0.022888 | -0.13733 | 0.84686 | 1.2543 | 0.36621 | 1.3367 | 0.44861 | -0.050354 | 0.050354 | -122.7493 | 0.036621 | 0.22888 | -0.077819 | 0.27924 | -0.027465 | 0.92926 | 122.7356 | 0.086975 | 0.091553 | 122.85 | 122.8912 | 122.7676 | 122.8409 | -122.8729 | -122.8409 | 122.6532 | 0.041199 | 2.1561 | 1.1765
1581.1719 | 123.0103 | -57.2617 | 65.5609 | -0.11398 | 0.0012625 | 0.062453 | 0.074599 | 0.00058737 | 0.0041143 | 0.0077716 | -0.037964 | 0.0013159 | -0.0010682 | 0.0077502 | -0.0019333 | -0.0025891 | 0.0030163 | -55.069 | 65.5151 | -57.3166 | 65.4144 | -56.3828 | -56.9687 | -56.0806 | -56.0028 | 65.5884 | -57.2845 | -57.1747 | -57.2067 | -57.312 | -57.0099 | -0.054931 | -0.045776 | -0.14648 | 0.87891 | 1.181 | 0.29297 | 1.236 | 0.3479 | -0.022888 | 0.027466 | -122.7356 | 0.054932 | 0.25177 | -0.050354 | 0.27466 | -0.027466 | 0.93384 | 122.731 | 0.07782 | 0.10986 | 122.8317 | 122.8729 | 122.7768 | 122.85 | -122.8775 | -122.8455 | 122.6761 | 0.086975 | 2.1927 | 1.2588
1582.1719 | 123.0698 | -57.2205 | 65.5701 | -0.10635 | 0.0016899 | 0.063734 | 0.074172 | -0.0032578 | 0.0032599 | 0.0084124 | 0.02002 | 0.0013159 | 0.00042723 | 0.0045458 | -0.0030013 | -0.0025891 | 0.0025891 | -55.0369 | 65.5609 | -57.3166 | 65.4099 | -56.3507 | -56.9275 | -56.0577 | -55.9845 | 65.5975 | -57.2662 | -57.1426 | -57.1518 | -57.2617 | -56.9916 | -0.09613 | -0.009155 | -0.16022 | 0.86975 | 1.1627 | 0.29297 | 1.2589 | 0.3891 | -0.045776 | 0.027466 | -122.7127 | 0.068665 | 0.22888 | -0.041199 | 0.27466 | 0.004577 | 0.96588 | 122.7264 | 0.11444 | 0.1236 | 122.8775 | 122.8638 | 122.7814 | 122.818 | -122.8867 | -122.8363 | 122.6303 | 0.07782 | 2.1835 | 1.236
1583.1719 | 123.0103 | -57.2205 | 65.6021 | -0.052948 | 0.0010489 | 0.064589 | 0.077804 | 0.0029374 | 0.0024053 | 0.0086262 | -0.095947 | 0.00046135 | 0.001068 | 0.003905 | -0.0017197 | -0.0019483 | 0.0021619 | -55.0186 | 65.5746 | -57.3486 | 65.4739 | -56.3461 | -56.9412 | -56.1081 | -55.9891 | 65.625 | -57.2845 | -57.1976 | -57.2342 | -57.3441 | -57.019 | -0.12817 | -0.027466 | -0.12817 | 0.87433 | 1.1124 | 0.27924 | 1.2405 | 0.40741 | -0.064087 | 0.022888 | -122.7997 | -0.013733 | 0.20142 | -0.1236 | 0.2655 | -0.059509 | 1.0025 | 122.8226 | 0.050354 | 0.086975 | 122.9233 | 122.9095 | 122.7951 | 122.8455 | -122.9507 | -122.8867 | 122.6944 | 0.022888 | 2.2018 | 1.2314
1584.1719 | 123.0835 | -57.225 | 65.5884 | -0.075836 | 0.00040806 | 0.063094 | 0.073104 | -0.0028304 | 0.0039007 | 0.0052082 | 0.001709 | 0.00024775 | 0.00021363 | -0.00036738 | -1.0706e-05 | -0.0034437 | 0.0023755 | -55.0095 | 65.5518 | -57.312 | 65.4556 | -56.3095 | -56.8817 | -56.0303 | -55.9479 | 65.593 | -57.2708 | -57.1335 | -57.1289 | -57.2342 | -56.9595 | -0.086975 | -0.036621 | -0.13275 | 0.91553 | 1.1948 | 0.34332 | 1.2817 | 0.4303 | -0.045776 | 0.004578 | -122.7219 | 0.096131 | 0.2655 | -0.009155 | 0.31128 | 0.036621 | 1.0025 | 122.7676 | 0.14191 | 0.13733 | 122.8638 | 122.8638 | 122.7768 | 122.818 | -122.9004 | -122.8592 | 122.6807 | 0.091553 | 2.2156 | 1.2772
1585.1719 | 123.0927 | -57.2342 | 65.6021 | -0.10635 | -0.00087374 | 0.06288 | 0.073531 | -0.00069423 | 0.0028327 | 0.0099078 | 0.0078126 | -0.00017945 | -0.00064077 | -0.00079478 | -0.00022431 | -0.0034437 | 0.0019483 | -55.0323 | 65.5472 | -57.3166 | 65.451 | -56.337 | -56.9092 | -56.0211 | -55.9616 | 65.5975 | -57.2617 | -57.1426 | -57.1335 | -57.2479 | -56.9595 | -0.082397 | -0.054932 | -0.15106 | 0.89722 | 1.2131 | 0.32501 | 1.2955 | 0.40741 | -0.027466 | -0.004578 | -122.7448 | 0.10071 | 0.27466 | -0.013733 | 0.30212 | 0.013733 | 0.97961 | 122.7676 | 0.12817 | 0.11902 | 122.8638 | 122.8592 | 122.7814 | 122.8317 | -122.9187 | -122.8638 | 122.6852 | 0.091553 | 2.2018 | 1.2726
1586.1719 | 123.0652 | -57.2296 | 65.5792 | -0.083466 | 0.0014761 | 0.061812 | 0.073958 | -0.0017624 | 0.0028327 | 0.0069172 | 0.03833 | -0.00082025 | 0.0019226 | 0.00027342 | -0.0017197 | -0.0021619 | 0.0019483 | -55.0415 | 65.5472 | -57.3303 | 65.4327 | -56.3461 | -56.9 | -56.0532 | -55.9662 | 65.5746 | -57.2479 | -57.1426 | -57.1609 | -57.2571 | -56.9595 | -0.10071 | -0.032044 | -0.14648 | 0.88348 | 1.1765 | 0.32959 | 1.2772 | 0.4303 | -0.018311 | -0.004578 | -122.7219 | 0.068664 | 0.27008 | -0.027466 | 0.28839 | -0.009155 | 0.98419 | 122.7631 | 0.086975 | 0.10529 | 122.8775 | 122.8226 | 122.7768 | 122.8043 | -122.9095 | -122.8271 | 122.6624 | 0.086975 | 2.1881 | 1.2634
1587.1719 | 123.0286 | -57.2708 | 65.5746 | -0.068207 | -0.0013009 | 0.063948 | 0.074599 | -0.0028304 | 0.0030463 | 0.0090534 | -0.022705 | -0.0016749 | 0.00042723 | 0.0054004 | -0.0017197 | -0.0025891 | 0.0017345 | -55.0415 | 65.5426 | -57.3212 | 65.4099 | -56.369 | -56.9641 | -56.0898 | -56.0165 | 65.6158 | -57.2845 | -57.2021 | -57.2113 | -57.312 | -57.0007 | -0.050354 | -0.032043 | -0.16479 | 0.90179 | 1.181 | 0.3067 | 1.2314 | 0.35706 | -0.013733 | 0.041199 | -122.7768 | 0.059509 | 0.27008 | -0.041199 | 0.28381 | -0.027466 | 0.95215 | 122.731 | 0.073242 | 0.082398 | 122.8638 | 122.9004 | 122.8134 | 122.8867 | -122.8958 | -122.8592 | 122.6807 | 0.068665 | 2.2293 | 1.2543
1588.1719 | 122.9507 | -57.2433 | 65.6342 | -0.10635 | -0.00023294 | 0.063521 | 0.074172 | 0.00058737 | 0.0028327 | 0.011403 | -0.025757 | 0.0019567 | 2.8e-08 | 0.00091422 | -0.0021469 | -0.0017347 | 0.00066654 | -55.014 | 65.6021 | -57.3029 | 65.4236 | -56.3736 | -56.9595 | -56.0806 | -56.0486 | 65.6525 | -57.2617 | -57.2159 | -57.2433 | -57.3486 | -57.0511 | -0.059509 | -0.032043 | -0.21057 | 0.86975 | 1.1627 | 0.28381 | 1.2222 | 0.34332 | -0.018311 | 0.018311 | -122.85 | 0 | 0.19226 | -0.10529 | 0.21057 | -0.086975 | 0.92926 | 122.7264 | 0.018311 | 0.045777 | 122.905 | 122.9141 | 122.8455 | 122.8958 | -122.937 | -122.8958 | 122.6669 | 0.027466 | 2.2293 | 1.1948
1589.1719 | 123.1064 | -57.2388 | 65.5609 | -0.083466 | 0.00083526 | 0.063734 | 0.072463 | -0.00026703 | 0.0047553 | 0.007558 | -0.0013428 | 3.4148e-05 | 0.0032044 | -0.0016492 | -0.0025741 | -0.0028027 | -0.0016833 | -55.0507 | 65.5334 | -57.3257 | 65.4236 | -56.3828 | -56.9504 | -56.0761 | -56.0257 | 65.6113 | -57.2937 | -57.1793 | -57.2021 | -57.2937 | -56.9916 | -0.086975 | -0.027466 | -0.13733 | 0.85602 | 1.1627 | 0.28839 | 1.2497 | 0.37537 | -0.054931 | 0.050354 | -122.7402 | 0.036622 | 0.24719 | -0.054931 | 0.30212 | 0 | 0.94299 | 122.7493 | 0.091553 | 0.11444 | 122.8592 | 122.905 | 122.7722 | 122.85 | -122.8867 | -122.8546 | 122.6624 | 0.05951 | 2.1881 | 1.2131
1590.1719 | 123.0469 | -57.225 | 65.5746 | -0.091095 | 0.0012625 | 0.063094 | 0.074599 | -0.00090783 | 0.0021917 | 0.0079852 | -0.0074462 | 0.00046135 | 0.00042723 | 0.00048702 | -0.0021469 | -0.0034437 | 0.00088014 | -55.0507 | 65.5243 | -57.3029 | 65.4236 | -56.3782 | -56.9412 | -56.0532 | -56.0165 | 65.5746 | -57.28 | -57.1747 | -57.1701 | -57.2754 | -56.9778 | -0.077819 | -0.050354 | -0.15106 | 0.84686 | 1.1719 | 0.28381 | 1.2497 | 0.36163 | -0.054931 | 0 | -122.7493 | 0.054932 | 0.24719 | -0.050354 | 0.30212 | 0.004577 | 0.92468 | 122.7264 | 0.10986 | 0.10528 | 122.8271 | 122.8546 | 122.7493 | 122.7997 | -122.8775 | -122.8546 | 122.6486 | 0.050354 | 2.1744 | 1.2085
1591.1719 | 123.0652 | -57.2159 | 65.5884 | -0.091095 | -0.0019417 | 0.06288 | 0.074599 | 0.0016556 | 0.0015509 | 0.0071308 | 0.023071 | 0.00046135 | 0.001709 | 0.002196 | -0.0030013 | -0.0028027 | -0.0016833 | -55.0186 | 65.5563 | -57.3029 | 65.4694 | -56.3187 | -56.9 | -56.0211 | -55.9341 | 65.5792 | -57.2662 | -57.1289 | -57.1381 | -57.2296 | -56.9641 | -0.086975 | -0.032044 | -0.11902 | 0.89722 | 1.1948 | 0.31586 | 1.2817 | 0.40283 | -0.050354 | -0.009155 | -122.7173 | 0.077819 | 0.25177 | -0.013733 | 0.30212 | 0.036621 | 0.98419 | 122.7722 | 0.12817 | 0.13733 | 122.8592 | 122.8455 | 122.7722 | 122.7951 | -122.8912 | -122.8546 | 122.6852 | 0.086975 | 2.1973 | 1.2817
1592.1719 | 123.1064 | -57.1701 | 65.5701 | -0.075836 | -0.0010873 | 0.065016 | 0.072677 | -0.0017624 | 0.0034735 | 0.0071308 | -0.0013428 | 0.00046135 | 0.00042723 | -0.00058098 | -0.00065151 | -0.0045117 | -0.0055287 | -55.0003 | 65.5655 | -57.2937 | 65.451 | -56.3232 | -56.8954 | -56.0257 | -55.9387 | 65.5975 | -57.2662 | -57.1152 | -57.1198 | -57.2296 | -56.955 | -0.1236 | -0.004577 | -0.11902 | 0.84686 | 1.1444 | 0.27466 | 1.268 | 0.39825 | -0.09613 | 0.027466 | -122.6852 | 0.050354 | 0.21515 | -0.059509 | 0.31128 | 0.036621 | 0.97046 | 122.7448 | 0.14648 | 0.15106 | 122.8592 | 122.8638 | 122.7356 | 122.7676 | -122.8638 | -122.8363 | 122.6212 | 0.054932 | 2.1698 | 1.2314
1593.1719 | 123.0148 | -57.2205 | 65.6433 | -0.03006 | 0.00040806 | 0.06053 | 0.075027 | 0.0020828 | 0.0017645 | 0.0054218 | -0.077637 | 0.00067495 | 0.001709 | 0.003905 | -0.0012925 | -0.0030163 | -0.0014697 | -55.0507 | 65.6158 | -57.3349 | 65.3915 | -56.4285 | -56.9687 | -56.131 | -56.0486 | 65.6708 | -57.2845 | -57.2113 | -57.2205 | -57.3349 | -57.0282 | -0.11444 | -0.027466 | -0.25177 | 0.79193 | 1.0895 | 0.25177 | 1.2039 | 0.36621 | -0.064087 | 0.027465 | -122.8546 | 0 | 0.19226 | -0.11444 | 0.25635 | -0.050354 | 0.90637 | 122.7264 | 0.064087 | 0.073242 | 122.9507 | 122.9553 | 122.8363 | 122.8912 | -122.9782 | -122.9279 | 122.612 | 0.009155 | 2.1698 | 1.1719
1594.1719 | 123.1064 | -57.225 | 65.5655 | -0.083466 | 0.00019446 | 0.060744 | 0.074172 | 0.0022964 | 0.0039007 | 0.0069172 | 0.026123 | 0.0021703 | 0.00085443 | -0.005708 | -0.0012925 | -0.0047253 | -0.0029651 | -55.014 | 65.5609 | -57.3166 | 65.4419 | -56.3324 | -56.9138 | -56.0349 | -55.9387 | 65.5792 | -57.2571 | -57.1243 | -57.1381 | -57.2296 | -56.955 | -0.091552 | -0.004578 | -0.1236 | 0.89264 | 1.1902 | 0.31128 | 1.2817 | 0.40283 | -0.032043 | 0.013733 | -122.6898 | 0.086975 | 0.27008 | -0.004577 | 0.30212 | 0.027466 | 0.98419 | 122.7585 | 0.11902 | 0.13275 | 122.8775 | 122.8363 | 122.7859 | 122.8043 | -122.8821 | -122.8226 | 122.6669 | 0.10071 | 2.211 | 1.2863
1595.1719 | 123.0606 | -57.225 | 65.5609 | 0.13779 | -0.0025827 | 0.063734 | 0.074813 | -0.0011214 | 0.0041143 | 0.0090534 | 0.0047608 | -0.00082025 | 0.00064083 | -0.0018628 | -0.0010787 | -0.0025891 | -0.0029651 | -55.1239 | 65.5609 | -57.2845 | 65.4144 | -56.3919 | -56.9504 | -56.0715 | -56.0074 | 65.5701 | -57.2662 | -57.1655 | -57.1838 | -57.28 | -56.9916 | -0.059509 | 0 | -0.14648 | 0.83313 | 1.1536 | 0.27466 | 1.2131 | 0.33417 | -0.041198 | 0.009155 | -122.7264 | 0.041199 | 0.23346 | -0.054931 | 0.27466 | -0.013733 | 0.89264 | 122.699 | 0.082397 | 0.10071 | 122.8455 | 122.8363 | 122.7859 | 122.7951 | -122.8455 | -122.8271 | 122.6395 | 0.05951 | 2.1011 | 1.2177
1596.1719 | 123.0789 | -57.2296 | 65.5746 | 0.084381 | -0.00087374 | 0.062025 | 0.075881 | -0.0017624 | 0.0039007 | 0.0084124 | 0.001709 | 0.0032385 | 0.0012818 | 0.00027342 | -0.0010787 | -0.0032301 | -0.0012561 | -55.0735 | 65.5701 | -57.312 | 65.4053 | -56.4011 | -56.9412 | -56.0715 | -55.9891 | 65.5884 | -57.2617 | -57.1838 | -57.1884 | -57.28 | -56.987 | -0.082398 | -0.004578 | -0.16937 | 0.82855 | 1.1581 | 0.28839 | 1.2405 | 0.37079 | -0.032044 | 0.013733 | -122.7585 | 0.041198 | 0.24261 | -0.050354 | 0.27466 | -0.01831 | 0.91095 | 122.7173 | 0.073242 | 0.07782 | 122.8821 | 122.85 | 122.7997 | 122.818 | -122.8867 | -122.8363 | 122.6349 | 0.045776 | 2.1561 | 1.2405
1597.1719 | 123.0835 | -57.225 | 65.5609 | -0.068207 | -0.0010873 | 0.063094 | 0.073958 | -0.0026168 | 0.0056097 | 0.0096942 | 0.013916 | 0.0015295 | 0.00021363 | -0.0065626 | -0.0015061 | -0.0045117 | 0.00088014 | -55.0278 | 65.538 | -57.3029 | 65.4648 | -56.3278 | -56.9138 | -56.0394 | -55.9387 | 65.6113 | -57.2617 | -57.1381 | -57.1243 | -57.2388 | -56.9595 | -0.077819 | -0.022888 | -0.09613 | 0.89722 | 1.1856 | 0.31128 | 1.2634 | 0.3891 | -0.036621 | 0.050354 | -122.699 | 0.10071 | 0.2655 | -0.013733 | 0.30212 | 0.022888 | 0.97504 | 122.7676 | 0.13733 | 0.1236 | 122.8409 | 122.8729 | 122.7631 | 122.8363 | -122.8638 | -122.8226 | 122.6898 | 0.086975 | 2.1973 | 1.2863
1598.1719 | 123.0057 | -57.2433 | 65.6296 | -0.03006 | -0.0015145 | 0.061171 | 0.07524 | 0.0012284 | 0.0039007 | 0.0090534 | -0.068481 | 0.0043065 | -0.00064077 | 0.0041186 | -0.0027877 | -0.0017347 | -0.0018971 | -55.0552 | 65.5838 | -57.3029 | 65.3824 | -56.4285 | -56.9641 | -56.1172 | -56.0532 | 65.6754 | -57.2845 | -57.1976 | -57.2296 | -57.3486 | -57.0419 | -0.059509 | -0.045777 | -0.24719 | 0.81482 | 1.1261 | 0.27924 | 1.1856 | 0.33874 | -0.041199 | 0.045776 | -122.8271 | 0.013733 | 0.20142 | -0.10529 | 0.24262 | -0.064087 | 0.87433 | 122.6852 | 0.054932 | 0.086975 | 122.8867 | 122.9599 | 122.8271 | 122.9187 | -122.9324 | -122.9141 | 122.6257 | 0.045776 | 2.1881 | 1.1902
1599.1719 | 123.0743 | -57.2205 | 65.5609 | -0.075836 | -0.0013009 | 0.061598 | 0.071395 | 0.003151 | 0.0066779 | 0.0067036 | 0.041382 | 3.4148e-05 | 0.001709 | -0.0014356 | -1.0706e-05 | -0.0017347 | 0.00023934 | -55.0278 | 65.5518 | -57.3029 | 65.4419 | -56.3324 | -56.9046 | -56.0303 | -55.9387 | 65.5838 | -57.2571 | -57.1335 | -57.1381 | -57.2388 | -56.9504 | -0.082397 | -0.009155 | -0.11902 | 0.88806 | 1.1902 | 0.31586 | 1.2726 | 0.39825 | -0.036621 | 0.022888 | -122.6944 | 0.082397 | 0.27008 | -0.018311 | 0.3067 | 0.01831 | 0.97046 | 122.7448 | 0.11902 | 0.1236 | 122.8546 | 122.8409 | 122.7722 | 122.8043 | -122.8638 | -122.818 | 122.6624 | 0.086975 | 2.1927 | 1.2817
1600.1719 | 123.1064 | -57.1701 | 65.6204 | -0.11398 | -0.00023294 | 0.061598 | 0.072677 | -0.001976 | 0.0032599 | 0.009267 | 0.035278 | 0.0013159 | -0.00085457 | 0.0034778 | -0.00043791 | -0.0021619 | 0.0013073 | -54.9911 | 65.5563 | -57.28 | 65.506 | -56.2592 | -56.8451 | -55.9845 | -55.8609 | 65.6113 | -57.2433 | -57.1152 | -57.1198 | -56.9778 | -56.7444 | -0.10986 | -0.064087 | -0.11444 | 0.91095 | 1.1856 | 0.32501 | 1.2955 | 0.43487 | -0.073242 | -0.009155 | -122.7356 | 0.050354 | 0.42572 | 0.19226 | 0.49896 | 0.2655 | 1.0208 | 122.7859 | 0.1236 | 0.12817 | 122.8363 | 122.8546 | 122.7264 | 122.7814 | -122.9004 | -122.8638 | 122.6761 | 0.054932 | 2.179 | 1.3092
1601.1719 | 123.0789 | -57.2205 | 65.6067 | -0.075836 | -0.00023294 | 0.061812 | 0.071609 | -0.0011214 | 0.0028327 | 0.01119 | 0.023071 | 3.4148e-05 | 0.0019226 | 0.0024096 | -0.00086511 | -0.0023755 | 2.554e-05 | -55.0278 | 65.5472 | -57.3029 | 65.451 | -56.3461 | -56.9046 | -56.0394 | -55.9525 | 65.5884 | -57.2662 | -57.1243 | -57.1381 | -57.225 | -56.955 | -0.082397 | -0.059509 | -0.15564 | 0.87433 | 1.181 | 0.31586 | 1.2634 | 0.39825 | -0.045776 | -0.01831 | -122.731 | 0.082397 | 0.2655 | -0.004578 | 0.31128 | 0.041198 | 0.95673 | 122.7539 | 0.12817 | 0.14191 | 122.85 | 122.8546 | 122.7676 | 122.8088 | -122.9095 | -122.8729 | 122.6715 | 0.09613 | 2.1927 | 1.268
1602.1719 | 123.0606 | -57.2479 | 65.5701 | -0.075836 | 0.0029715 | 0.06053 | 0.074599 | 0.0027238 | 0.0034735 | 0.011617 | 0.010864 | 0.0025975 | 0.0012818 | -0.0025036 | -0.00086511 | -0.0036573 | -0.00040166 | -54.9591 | 65.5746 | -57.3029 | 65.4282 | -56.3919 | -56.9778 | -56.0806 | -56.012 | 65.5792 | -57.2754 | -57.1701 | -57.1793 | -57.2891 | -56.9916 | -0.054931 | 0.004578 | -0.14191 | 0.85602 | 1.1673 | 0.27008 | 1.2222 | 0.32501 | -0.027466 | 0.009156 | -122.7402 | 0.068665 | 0.25635 | -0.041199 | 0.28381 | -0.013733 | 0.91095 | 122.731 | 0.096131 | 0.10529 | 122.8775 | 122.8546 | 122.8226 | 122.8271 | -122.8729 | -122.8455 | 122.6761 | 0.07782 | 2.2888 | 1.236
1603.1719 | 123.0835 | -57.2296 | 65.5655 | -0.10635 | -0.00044654 | 0.061812 | 0.07289 | -0.0011214 | 0.0041143 | 0.0060626 | 0.016968 | 0.00088875 | 2.8e-08 | 0.00091422 | -0.0010787 | -0.0028027 | -0.0012561 | -55.0232 | 65.5563 | -57.3074 | 65.4602 | -56.3278 | -56.8954 | -56.0394 | -55.9433 | 65.5838 | -57.2662 | -57.1243 | -57.1472 | -57.2342 | -56.9458 | -0.07782 | -0.009156 | -0.10529 | 0.90179 | 1.1902 | 0.33417 | 1.268 | 0.41199 | -0.036621 | 0.01831 | -122.6898 | 0.082397 | 0.28381 | -0.004578 | 0.32043 | 0.032043 | 0.97961 | 122.7676 | 0.11902 | 0.14191 | 122.8638 | 122.85 | 122.7859 | 122.8134 | -122.8729 | -122.8317 | 122.6898 | 0.10528 | 2.2064 | 1.2863
1604.1719 | 123.0698 | -57.2342 | 65.593 | -0.052948 | 0.0014761 | 0.064162 | 0.07225 | -0.001976 | 0.0043281 | 0.0081988 | 0.023071 | 0.00088875 | 0.001709 | 0.0034778 | -0.00086511 | -0.0021619 | -0.00040166 | -55.0232 | 65.5334 | -57.2983 | 65.4922 | -56.3141 | -56.8726 | -56.0074 | -55.9204 | 65.5792 | -57.2662 | -57.1335 | -57.1289 | -57.2342 | -56.955 | -0.064087 | -0.05951 | -0.10071 | 0.9201 | 1.2268 | 0.36163 | 1.2909 | 0.42572 | -0.032043 | -0.013733 | -122.7264 | 0.10529 | 0.27924 | 0 | 0.31128 | 0.032043 | 0.98419 | 122.7905 | 0.13733 | 0.13275 | 122.8317 | 122.8455 | 122.7676 | 122.8134 | -122.8912 | -122.8592 | 122.7264 | 0.10071 | 2.211 | 1.3138
1605.1719 | 123.1567 | -57.1884 | 65.6662 | -0.068207 | 0.00062166 | 0.063521 | 0.072463 | -0.0049668 | 0.0028327 | 0.0069172 | 0.016968 | 0.00046135 | 0.001068 | 5.9824e-05 | -0.00043791 | -0.0038709 | -0.00040166 | -54.9866 | 65.5563 | -57.2845 | 65.4968 | -56.2683 | -56.8542 | -55.9891 | -55.8609 | 65.593 | -57.2433 | -57.1289 | -57.1106 | -57.2113 | -57.1198 | -0.09613 | -0.10986 | -0.16937 | 0.9201 | 1.1993 | 0.33417 | 1.2955 | 0.4303 | -0.054931 | -0.073242 | -122.7951 | 0.07782 | 0.068665 | -0.022888 | 0.1236 | 0.032043 | 1.0162 | 122.7814 | 0.13275 | 0.11444 | 122.8409 | 122.8363 | 122.7448 | 122.7814 | -122.9507 | -122.9095 | 122.6852 | 0.05951 | 2.2018 | 1.3275
1606.1719 | 123.0377 | -57.2205 | 65.5701 | -0.098725 | 0.0025443 | 0.063307 | 0.076308 | -0.00090783 | 0.0028327 | 0.0064898 | -0.0013428 | -0.00039305 | 0.00042723 | 0.0045458 | -0.0012925 | -0.0036573 | -0.0018971 | -55.014 | 65.5563 | -57.2891 | 65.4877 | -56.2866 | -56.8588 | -56.0211 | -55.9204 | 65.593 | -57.2571 | -57.1335 | -57.1426 | -57.2342 | -56.955 | -0.068665 | -0.013733 | -0.082397 | 0.93384 | 1.1993 | 0.36163 | 1.268 | 0.4303 | -0.036621 | 0.022889 | -122.7036 | 0.07782 | 0.2655 | -0.013733 | 0.30212 | 0.022888 | 1.0025 | 122.7768 | 0.11444 | 0.1236 | 122.8455 | 122.85 | 122.7768 | 122.8134 | -122.8592 | -122.8271 | 122.7081 | 0.086975 | 2.2064 | 1.3
1607.1719 | 123.0286 | -57.193 | 65.5975 | -0.083466 | 0.0040397 | 0.062666 | 0.071822 | 0.0044328 | 0.0039007 | 0.0086262 | 0.010864 | 0.00024775 | 0.0019226 | 0.00070062 | -0.0030013 | -0.0028027 | 0.00066654 | -55.0323 | 65.5243 | -57.3166 | 65.4922 | -56.3049 | -56.8726 | -56.0028 | -55.9113 | 65.6204 | -57.2525 | -57.1243 | -57.1518 | -57.225 | -56.9595 | -0.1236 | -0.073242 | -0.10528 | 0.88806 | 1.1902 | 0.32043 | 1.3138 | 0.44403 | -0.059509 | 0.022888 | -122.7219 | 0.041199 | 0.23346 | -0.032044 | 0.29297 | 0.027465 | 1.0117 | 122.8088 | 0.10071 | 0.12817 | 122.8409 | 122.8729 | 122.7173 | 122.8134 | -122.9141 | -122.85 | 122.6852 | 0.068664 | 2.1606 | 1.2817
1608.1719 | 123.0652 | -57.1884 | 65.5975 | -0.068207 | 0.0021171 | 0.061812 | 0.073531 | -0.0026168 | 0.0043281 | 0.0081988 | 0.02002 | 0.00024775 | 0.001068 | 0.0015552 | -0.0023605 | -0.0036573 | -0.0033923 | -55.0003 | 65.5701 | -57.2891 | 65.4968 | -56.282 | -56.8863 | -56.0074 | -55.8838 | 65.5838 | -57.2479 | -57.1381 | -57.1518 | -57.2296 | -56.9504 | -0.10071 | -0.027466 | -0.10071 | 0.90637 | 1.181 | 0.30212 | 1.2817 | 0.40283 | -0.059509 | -0.013733 | -122.7356 | 0.036622 | 0.23804 | -0.041198 | 0.29755 | 0.018311 | 1.0071 | 122.7859 | 0.096131 | 0.10986 | 122.8592 | 122.8317 | 122.7585 | 122.7722 | -122.8867 | -122.8455 | 122.6852 | 0.050354 | 2.1881 | 1.3046
1609.1719 | 123.0927 | -57.2113 | 65.5746 | -0.098725 | 0.00040806 | 0.062025 | 0.073745 | -5.343e-05 | 0.0056097 | 0.0071308 | 0.010864 | 0.0015295 | -0.00021357 | -0.00015378 | -0.00086511 | -0.0030163 | -0.00040166 | -55.0415 | 65.5701 | -57.312 | 65.451 | -56.3324 | -56.9092 | -56.0486 | -55.9525 | 65.5609 | -57.2708 | -57.1381 | -57.1472 | -57.2479 | -56.9641 | -0.10071 | -0.004578 | -0.1236 | 0.87891 | 1.1627 | 0.30212 | 1.2634 | 0.40283 | -0.059509 | -0.013733 | -122.7127 | 0.064087 | 0.24719 | -0.036621 | 0.3067 | 0.022888 | 0.97962 | 122.7631 | 0.1236 | 0.13275 | 122.8821 | 122.8317 | 122.7814 | 122.7722 | -122.8867 | -122.8455 | 122.6624 | 0.073242 | 2.1698 | 1.2588
1610.1719 | 123.0698 | -57.2159 | 65.5472 | -0.075836 | 0.0021171 | 0.062453 | 0.074386 | 0.00251 | 0.0045417 | 0.0062762 | 0.0047608 | 0.00024775 | 0.0012818 | 0.0013416 | -0.0019333 | -0.0032301 | -0.00082886 | -54.9911 | 65.5609 | -57.3029 | 65.4968 | -56.2683 | -56.8359 | -55.9982 | -55.8426 | 65.5884 | -57.2708 | -57.1243 | -57.106 | -57.2159 | -56.9458 | -0.086975 | 0.013733 | -0.050354 | 0.94757 | 1.2177 | 0.37994 | 1.3046 | 0.46692 | -0.054932 | 0.041199 | -122.6715 | 0.10986 | 0.27008 | 0 | 0.32501 | 0.054932 | 1.0345 | 122.7997 | 0.16479 | 0.14648 | 122.8638 | 122.8592 | 122.7768 | 122.8043 | -122.85 | -122.818 | 122.7127 | 0.091552 | 2.2247 | 1.3733
1611.1719 | 123.0606 | -57.2159 | 65.5792 | 0.10727 | 0.0027579 | 0.063521 | 0.075027 | -0.0021896 | 0.0041143 | 0.009267 | 0.001709 | -0.0010339 | -0.0021362 | -0.0065626 | -0.00022431 | -0.0030163 | -0.0018971 | -55.1971 | 65.5609 | -57.2845 | 65.4831 | -56.3004 | -56.8817 | -56.0165 | -55.9021 | 65.625 | -57.2525 | -57.1426 | -57.1381 | -57.2296 | -56.9687 | -0.068665 | -0.018311 | -0.096131 | 0.91553 | 1.1993 | 0.33417 | 1.268 | 0.40283 | -0.036621 | 0.045776 | -122.7219 | 0.077819 | 0.24719 | -0.013733 | 0.28381 | 0.022888 | 0.98419 | 122.7676 | 0.11444 | 0.10986 | 122.8455 | 122.8775 | 122.7768 | 122.8409 | -122.8638 | -122.8317 | 122.699 | 0.073242 | 2.0187 | 1.3138
1612.1719 | 122.9919 | -57.2205 | 65.6067 | -0.10635 | 0.0016899 | 0.062025 | 0.073745 | -0.00048063 | 0.0043281 | 0.0090534 | 0.001709 | -0.00017945 | 0.00042723 | -0.0018628 | -0.00065151 | -0.0034437 | -0.0038197 | -54.9911 | 65.593 | -57.3029 | 65.4556 | -56.337 | -56.9 | -56.0486 | -55.957 | 65.6433 | -57.2342 | -57.1884 | -57.225 | -57.3212 | -57.0236 | -0.082397 | -0.013732 | -0.15106 | 0.88348 | 1.1719 | 0.32043 | 1.2543 | 0.40283 | -0.013733 | 0.036622 | -122.7951 | -0.004578 | 0.19684 | -0.10071 | 0.21057 | -0.086975 | 0.96588 | 122.7585 | 0.009155 | 0.045776 | 122.8958 | 122.8775 | 122.8134 | 122.8638 | -122.9095 | -122.8409 | 122.6761 | 0.032043 | 2.2293 | 1.2634
1613.1719 | 123.0331 | -57.2342 | 65.6158 | -0.12924 | 0.00083526 | 0.064162 | 0.073318 | 0.00058737 | 0.0017645 | 0.0056354 | 0.0078126 | 0.0015295 | 0.00064083 | -0.0037854 | -0.00065151 | -0.0038709 | -0.0033923 | -55.0049 | 65.5838 | -57.2937 | 65.451 | -56.3324 | -56.9 | -56.0394 | -55.9433 | 65.6021 | -57.2388 | -57.1884 | -57.2021 | -57.2983 | -57.0007 | -0.059509 | -0.032044 | -0.16479 | 0.90179 | 1.1948 | 0.33417 | 1.2543 | 0.39368 | -0.004578 | -0.013733 | -122.8043 | 0.032044 | 0.23346 | -0.064087 | 0.23804 | -0.059509 | 0.9613 | 122.7448 | 0.036622 | 0.050354 | 122.8775 | 122.8409 | 122.818 | 122.8363 | -122.9095 | -122.8546 | 122.6852 | 0.045776 | 2.2293 | 1.2909
1614.1719 | 123.0743 | -57.2021 | 65.593 | -0.098725 | 0.00062166 | 0.063094 | 0.073958 | -0.0038986 | 0.0021917 | 0.0094806 | -0.01355 | 0.0013159 | 0.001068 | 0.0051868 | -0.0017197 | -0.0032301 | -0.0023243 | -54.9911 | 65.5609 | -57.2754 | 65.3412 | -56.5933 | -56.8954 | -55.9708 | -55.8792 | 65.5792 | -57.2617 | -57.1243 | -57.1152 | -57.2159 | -56.9595 | -0.073243 | -0.032044 | -0.25177 | 0.60883 | 1.2314 | 0.3067 | 1.3046 | 0.37994 | -0.05951 | -0.013733 | -122.7173 | 0.086975 | 0.24261 | -0.013733 | 0.30212 | 0.045777 | 0.68207 | 122.6166 | 0.14648 | 0.13733 | 122.8363 | 122.8409 | 122.7631 | 122.7814 | -122.8683 | -122.8546 | 122.5433 | 0.077819 | 2.211 | 1.3229
1615.1719 | 123.0927 | -57.1976 | 65.5792 | -0.03006 | 0.0021171 | 0.061598 | 0.073104 | -0.0041122 | 0.0049689 | 0.0094806 | 0.016968 | -0.00060665 | 0.0014954 | 0.0062548 | -0.0025741 | -0.0036573 | 0.00045294 | -54.9957 | 65.5609 | -57.3029 | 65.4739 | -56.3095 | -56.8863 | -56.0303 | -55.8655 | 65.5838 | -57.2296 | -57.1243 | -57.1198 | -57.193 | -56.9366 | -0.10528 | -0.018311 | -0.10529 | 0.88806 | 1.1673 | 0.31128 | 1.2726 | 0.41656 | -0.032043 | 0.004577 | -122.7036 | 0.07782 | 0.26093 | 0.004578 | 0.29297 | 0.036621 | 0.99335 | 122.7768 | 0.10986 | 0.10528 | 122.8638 | 122.8134 | 122.7585 | 122.7814 | -122.8821 | -122.8088 | 122.6715 | 0.073242 | 2.2018 | 1.3321
1616.1719 | 123.0972 | -57.2205 | 65.5701 | -0.098725 | -0.00044654 | 0.063521 | 0.073318 | 0.006569 | 0.0026191 | 0.007558 | 0.010864 | 0.0025975 | 0.00021363 | -0.00079478 | -0.0010787 | -0.0034437 | -0.0016833 | -55.0232 | 65.538 | -57.2983 | 65.4694 | -56.3095 | -56.8817 | -56.0257 | -55.8884 | 65.5563 | -57.2754 | -57.1152 | -57.1152 | -57.2021 | -56.9458 | -0.07782 | -0.032043 | -0.10071 | 0.91095 | 1.1948 | 0.33874 | 1.2726 | 0.41656 | -0.054932 | -0.013733 | -122.6852 | 0.10529 | 0.27466 | 0.018311 | 0.32959 | 0.073243 | 0.98877 | 122.7676 | 0.16022 | 0.16022 | 122.8363 | 122.8317 | 122.7585 | 122.7768 | -122.8683 | -122.8455 | 122.6898 | 0.10529 | 2.1973 | 1.3321
1617.1719 | 123.0972 | -57.2388 | 65.5746 | -0.10635 | 0.0012625 | 0.062453 | 0.074599 | 0.00080117 | 0.0024053 | 0.0062762 | 0.02002 | 0.00067495 | 0.001709 | -0.00015378 | -0.0017197 | -0.0036573 | -0.0042469 | -54.9774 | 65.5792 | -57.2708 | 65.4739 | -56.2683 | -56.8542 | -56.0074 | -55.9799 | 65.5975 | -57.2342 | -57.0969 | -57.1838 | -57.2525 | -56.9504 | -0.032043 | 0.004578 | -0.10071 | 0.97046 | 1.2314 | 0.38452 | 1.2634 | 0.41656 | 0.004578 | 0.022888 | -122.6715 | 0.054932 | 0.28839 | -0.013732 | 0.28381 | -0.01831 | 1.0025 | 122.7448 | 0.050354 | 0.13733 | 122.85 | 122.8317 | 122.818 | 122.8363 | -122.8455 | -122.8088 | 122.7127 | 0.14191 | 2.2614 | 1.2589
1618.1719 | 122.9553 | -57.2342 | 65.6342 | -0.052948 | 0.0016899 | 0.064375 | 0.073531 | 0.0010148 | 0.0013373 | 0.0067036 | -0.019653 | 0.0021703 | -0.00064077 | 0.0034778 | -0.0015061 | -0.0015211 | -0.0036059 | -55.0049 | 65.5701 | -57.2937 | 65.4099 | -56.3828 | -56.9366 | -56.0898 | -56.012 | 65.6296 | -57.2662 | -57.2205 | -57.2159 | -57.3349 | -57.0694 | -0.059509 | -0.064087 | -0.2243 | 0.85144 | 1.1444 | 0.29755 | 1.2039 | 0.35705 | -0.032043 | -0.004577 | -122.8546 | 0.018311 | 0.16479 | -0.10071 | 0.19684 | -0.068665 | 0.91095 | 122.7036 | 0.050354 | 0.045776 | 122.8638 | 122.8958 | 122.8043 | 122.8638 | -122.9279 | -122.9004 | 122.644 | 0.013733 | 2.2293 | 1.2222
1619.1719 | 122.9782 | -57.2571 | 65.6204 | -0.10635 | 0.00062166 | 0.061171 | 0.075027 | 0.0020828 | 0.0021917 | 0.0096942 | -0.016602 | 0.0013159 | 0.00064083 | 0.0019824 | -0.00043791 | -0.0017347 | 0.00023934 | -55.0003 | 65.5746 | -57.312 | 65.4282 | -56.3507 | -56.9229 | -56.0898 | -55.9799 | 65.6204 | -57.2571 | -57.2159 | -57.2388 | -57.3257 | -57.0694 | -0.054932 | -0.045776 | -0.19226 | 0.90637 | 1.1673 | 0.33417 | 1.2222 | 0.3891 | 0 | 0 | -122.8363 | 0.01831 | 0.18768 | -0.068665 | 0.18768 | -0.068665 | 0.9613 | 122.7402 | 0.01831 | 0.041199 | 122.8867 | 122.8775 | 122.8317 | 122.8775 | -122.9324 | -122.8775 | 122.6852 | 0.041199 | 2.2568 | 1.2772
1620.1719 | 123.0331 | -57.2113 | 65.5975 | -0.13687 | 0.0023307 | 0.064803 | 0.072677 | -0.0015488 | 0.0026191 | 0.0090534 | 0.041382 | 0.0011023 | -0.00021357 | 0.001128 | -0.0023605 | -0.0017347 | -0.0021107 | -55.0095 | 65.5518 | -57.3166 | 65.4602 | -56.3049 | -56.8497 | -56.012 | -55.8884 | 65.6067 | -57.2525 | -57.1472 | -57.1198 | -57.2342 | -56.9595 | -0.10529 | -0.045776 | -0.13733 | 0.90637 | 1.1993 | 0.36163 | 1.3046 | 0.46692 | -0.041198 | 0.009155 | -122.7448 | 0.091553 | 0.25177 | -0.022888 | 0.29297 | 0.01831 | 1.0117 | 122.7768 | 0.13275 | 0.10529 | 122.8683 | 122.8592 | 122.7631 | 122.818 | -122.9141 | -122.85 | 122.6715 | 0.064087 | 2.2018 | 1.3229
1621.1719 | 123.0789 | -57.2159 | 65.6158 | -0.037689 | 0.0019035 | 0.063521 | 0.074172 | -0.00090783 | 0.0017645 | 0.0090534 | -0.016602 | -0.00017945 | -0.0019226 | 0.00091422 | -0.0021469 | -0.00045288 | 0.0013073 | -55.1102 | 65.5426 | -57.3029 | 65.4694 | -56.2912 | -56.8497 | -56.0165 | -55.8746 | 65.6204 | -57.2617 | -57.1335 | -57.1289 | -57.2433 | -56.9824 | -0.086975 | -0.073242 | -0.14648 | 0.92468 | 1.1993 | 0.36621 | 1.2863 | 0.45319 | -0.045777 | 0.004577 | -122.7493 | 0.086975 | 0.23346 | -0.027466 | 0.27924 | 0.018311 | 1.0117 | 122.7722 | 0.13275 | 0.12817 | 122.8455 | 122.8821 | 122.7585 | 122.8363 | -122.9187 | -122.8775 | 122.6852 | 0.082397 | 2.1057 | 1.3412
1622.1719 | 123.0789 | -57.225 | 65.5792 | -0.045319 | -0.00023294 | 0.062453 | 0.072036 | -0.0013352 | 0.0026191 | 0.0077716 | 0.032227 | -0.0010339 | 0.00064083 | 0.00048702 | 0.00020289 | -0.0034437 | -0.00061526 | -54.9774 | 65.5472 | -57.2845 | 65.4877 | -56.2775 | -56.868 | -56.0028 | -55.8563 | 65.5884 | -57.2479 | -57.1152 | -57.106 | -57.1838 | -56.9504 | -0.059509 | -0.032044 | -0.091553 | 0.94757 | 1.2222 | 0.35706 | 1.2817 | 0.41656 | -0.022888 | 0.009155 | -122.6944 | 0.11902 | 0.27466 | 0.041199 | 0.29755 | 0.064087 | 1.0071 | 122.7722 | 0.14191 | 0.13275 | 122.8317 | 122.8363 | 122.7722 | 122.8134 | -122.8638 | -122.8271 | 122.7127 | 0.10986 | 2.2476 | 1.3687
1623.1719 | 123.1155 | -57.2205 | 65.5792 | -0.1445 | -0.00044654 | 0.063094 | 0.073745 | 0.001442 | 0.0049689 | 0.0073444 | -0.0013428 | -0.00017945 | 0.0025634 | 0.00027342 | -0.00043791 | -0.0036573 | -0.0023243 | -55.0003 | 65.5563 | -57.2937 | 65.4922 | -56.2866 | -56.8771 | -56.0211 | -55.8472 | 65.5975 | -57.2296 | -57.1014 | -57.106 | -57.2113 | -56.9321 | -0.073242 | -0.022889 | -0.086975 | 0.93384 | 1.1993 | 0.34332 | 1.2726 | 0.41656 | -0.009155 | 0.01831 | -122.6807 | 0.11444 | 0.28839 | 0.009155 | 0.29755 | 0.01831 | 1.0071 | 122.7859 | 0.1236 | 0.12817 | 122.85 | 122.8271 | 122.7768 | 122.818 | -122.8729 | -122.8088 | 122.7127 | 0.11902 | 2.2202 | 1.3733
1624.1719 | 123.056 | -57.1976 | 65.5563 | -0.014801 | 0.0021171 | 0.061812 | 0.072036 | 0.00080117 | 0.0013373 | 0.0071308 | 0.041382 | -0.00039305 | 0.001709 | 0.00091422 | -0.0027877 | -0.0034437 | -0.0027515 | -54.982 | 65.5609 | -57.2891 | 65.5518 | -56.0028 | -56.8039 | -56.2683 | -55.8746 | 65.5975 | -57.2525 | -57.1289 | -57.1335 | -57.2433 | -56.9733 | -0.091553 | 0.004578 | -0.004577 | 1.1948 | 0.92926 | 0.39368 | 1.0208 | 0.48523 | -0.054931 | 0.041199 | -122.6852 | 0.064087 | 0.2243 | -0.045776 | 0.27923 | 0.009155 | 1.2863 | 122.8409 | 0.11902 | 0.1236 | 122.85 | 122.85 | 122.7585 | 122.7951 | -122.8455 | -122.8088 | 122.7493 | 0.068665 | 2.2156 | 1.3229
1625.1719 | 123.024 | -57.2296 | 65.6021 | -0.014801 | 0.00019446 | 0.062666 | 0.073104 | 0.0020828 | 0.0051825 | 0.0073444 | 0.023071 | 0.0015295 | 0.00085443 | 0.0041186 | 0.00041649 | -0.0038709 | -0.0016833 | -54.982 | 65.5655 | -57.2937 | 65.4739 | -56.3232 | -56.868 | -56.0486 | -55.9387 | 65.593 | -57.2525 | -57.1518 | -57.1609 | -57.2754 | -56.9916 | -0.064087 | -0.036621 | -0.12817 | 0.90637 | 1.181 | 0.36163 | 1.2451 | 0.42572 | -0.022888 | -0.009155 | -122.7539 | 0.068664 | 0.23804 | -0.045777 | 0.26093 | -0.022889 | 0.97046 | 122.7676 | 0.091552 | 0.10071 | 122.8592 | 122.8455 | 122.7951 | 122.8226 | -122.8958 | -122.8546 | 122.7036 | 0.07782 | 2.2476 | 1.2909
1626.1719 | 122.9965 | -57.2479 | 65.6616 | -0.10635 | 0.00019446 | 0.063734 | 0.073104 | 0.00037377 | 0.00069649 | 0.0081988 | 0.10547 | 0.00067495 | 0.0014954 | 0.005614 | -0.0012925 | -0.0034437 | 2.554e-05 | -55.0507 | 65.5975 | -57.3166 | 65.3641 | -56.4331 | -56.9778 | -56.1401 | -56.0623 | 65.6616 | -57.2617 | -57.2388 | -57.2525 | -57.3669 | -57.0511 | -0.068664 | -0.064087 | -0.29755 | 0.81482 | 1.1078 | 0.27008 | 1.1765 | 0.33875 | -0.013733 | 0 | -122.9004 | -0.004577 | 0.19684 | -0.11902 | 0.21057 | -0.10529 | 0.88348 | 122.6807 | 0.009156 | 0.022888 | 122.9141 | 122.9233 | 122.8455 | 122.9095 | -122.9782 | -122.9233 | 122.612 | 0.009155 | 2.1973 | 1.1856
1627.1719 | 122.937 | -57.2525 | 65.6342 | -0.045319 | 0.0019035 | 0.062239 | 0.072677 | -0.00048063 | 0.0030463 | 0.011617 | -0.0043946 | 0.0011023 | -0.00021357 | 0.0058276 | -0.0015061 | -0.0028027 | -0.0031787 | -54.9866 | 65.5884 | -57.3029 | 65.4236 | -56.3507 | -56.9229 | -56.0852 | -55.9708 | 65.6433 | -57.2479 | -57.2067 | -57.1793 | -57.3395 | -57.0648 | -0.050354 | -0.045776 | -0.21057 | 0.90179 | 1.1673 | 0.32959 | 1.2177 | 0.37994 | 0.004577 | 0.009156 | -122.8409 | 0.073242 | 0.18768 | -0.086976 | 0.18311 | -0.091553 | 0.95215 | 122.7264 | 0.068665 | 0.041199 | 122.8912 | 122.8912 | 122.8409 | 122.8958 | -122.937 | -122.8821 | 122.6761 | 0.045776 | 2.2659 | 1.2817
1628.1719 | 122.9782 | -57.2342 | 65.6021 | -0.091095 | 0.00083526 | 0.062025 | 0.07524 | 0.0010148 | 0.00026909 | 0.0079852 | -0.0013428 | 0.0019567 | 0.0040588 | -0.0010084 | -0.0023605 | -0.0040845 | 0.0062207 | -54.9866 | 65.5701 | -57.2845 | 65.451 | -56.3416 | -56.9092 | -56.0761 | -55.9433 | 65.6113 | -57.28 | -57.193 | -57.225 | -57.3349 | -57.0374 | -0.050354 | -0.032044 | -0.15106 | 0.89264 | 1.1581 | 0.32501 | 1.2085 | 0.37537 | -0.045776 | 0.009155 | -122.7951 | 0.009155 | 0.19684 | -0.10071 | 0.24261 | -0.054932 | 0.94299 | 122.7356 | 0.054931 | 0.086975 | 122.8546 | 122.8912 | 122.8043 | 122.8455 | -122.8867 | -122.8821 | 122.6852 | 0.041199 | 2.2476 | 1.2909
1629.1719 | 123.1018 | -57.2113 | 65.5701 | -0.068207 | 0.0012625 | 0.06053 | 0.075881 | 0.0020828 | 0.0017645 | 0.0096942 | 0.044434 | -0.0010339 | 0.00021363 | -0.00036738 | -0.0021469 | -0.0023755 | -0.00082886 | -55.0186 | 65.5518 | -57.2845 | 65.4602 | -56.3049 | -56.8771 | -56.012 | -55.8701 | 65.5884 | -57.2662 | -57.1014 | -57.1152 | -57.1884 | -56.9412 | -0.073242 | -0.01831 | -0.10986 | 0.90637 | 1.1993 | 0.33417 | 1.2726 | 0.40741 | -0.054931 | 0.018311 | -122.6715 | 0.096131 | 0.27008 | 0.022888 | 0.32501 | 0.077819 | 0.97961 | 122.7448 | 0.15106 | 0.1648 | 122.8363 | 122.8546 | 122.7631 | 122.7997 | -122.8546 | -122.8363 | 122.6715 | 0.10986 | 2.1927 | 1.3412
1630.1719 | 123.1064 | -57.2113 | 65.5472 | -0.11398 | 0.0012625 | 0.063521 | 0.073745 | 0.00058737 | 0.0041143 | 0.005849 | 0.035278 | -0.0014613 | -0.0021362 | -0.0031446 | -0.0021469 | -0.0047253 | -0.0014697 | -55.0186 | 65.5655 | -57.3074 | 65.4556 | -56.3278 | -56.9046 | -56.044 | -55.9067 | 65.5838 | -57.2433 | -57.1243 | -57.1014 | -57.225 | -56.9458 | -0.09613 | 0.018311 | -0.091553 | 0.88348 | 1.1673 | 0.3067 | 1.2634 | 0.40283 | -0.032043 | 0.036621 | -122.6715 | 0.10986 | 0.2655 | -0.013733 | 0.29755 | 0.01831 | 0.97961 | 122.7631 | 0.14191 | 0.11902 | 122.8729 | 122.8271 | 122.7768 | 122.7951 | -122.8546 | -122.7905 | 122.6669 | 0.086975 | 2.1927 | 1.3046
1631.1719 | 123.0515 | -57.2205 | 65.6158 | -0.13687 | -1.9142e-05 | 0.06288 | 0.074386 | -5.343e-05 | 0.0019781 | 0.0086262 | -0.0013428 | -0.00017945 | 0.00021363 | 0.0026232 | -0.0010787 | -0.0032301 | -0.00061526 | -54.9362 | 65.5426 | -57.3029 | 65.4877 | -56.2775 | -56.8817 | -56.0349 | -55.8884 | 65.5838 | -57.2662 | -57.1518 | -57.1518 | -57.2433 | -56.9504 | -0.082397 | -0.073242 | -0.12817 | 0.94299 | 1.1856 | 0.33874 | 1.268 | 0.42114 | -0.045776 | -0.032044 | -122.7676 | 0.068665 | 0.27008 | -0.022888 | 0.31586 | 0.022888 | 1.0254 | 122.7905 | 0.11444 | 0.11444 | 122.8455 | 122.85 | 122.7631 | 122.8043 | -122.9187 | -122.8821 | 122.7081 | 0.068665 | 2.2842 | 1.3321
1632.1719 | 122.9965 | -57.2342 | 65.6021 | -0.083466 | 0.00040806 | 0.062666 | 0.071395 | 0.00080117 | 0.0032599 | 0.0077716 | 0.0078126 | 0.00046135 | 0.00021363 | 0.0051868 | -0.0021469 | -0.0032301 | 0.0025891 | -54.9591 | 65.5746 | -57.2845 | 65.451 | -56.3278 | -56.9 | -56.0715 | -55.9296 | 65.6113 | -57.2662 | -57.1793 | -57.2113 | -57.2891 | -57.0053 | -0.050354 | -0.027466 | -0.15106 | 0.90637 | 1.1627 | 0.33417 | 1.2131 | 0.38452 | -0.032043 | 0.009155 | -122.7814 | 0.022888 | 0.22888 | -0.054932 | 0.26093 | -0.022889 | 0.95673 | 122.7356 | 0.054931 | 0.086975 | 122.8592 | 122.8775 | 122.8088 | 122.8455 | -122.8867 | -122.8683 | 122.6852 | 0.054932 | 2.2751 | 1.3046
1633.1719 | 123.1155 | -57.2205 | 65.5746 | -0.11398 | -0.00044654 | 0.062453 | 0.07289 | -0.00069423 | 0.0028327 | 0.0047808 | 0.032227 | 0.00088875 | 0.001709 | 0.005614 | -0.00022431 | -0.0032301 | -0.0029651 | -54.9683 | 65.5609 | -57.28 | 65.4785 | -56.282 | -56.8634 | -56.0349 | -55.9158 | 65.6067 | -57.225 | -57.0969 | -57.1976 | -57.2617 | -56.9412 | -0.059509 | -0.013733 | -0.09613 | 0.93842 | 1.1856 | 0.35706 | 1.2451 | 0.41656 | -0.004578 | 0.032043 | -122.6715 | 0.022888 | 0.27924 | -0.041199 | 0.28381 | -0.036621 | 0.99792 | 122.7585 | 0.027466 | 0.12817 | 122.8409 | 122.8317 | 122.7814 | 122.8271 | -122.8546 | -122.7997 | 122.699 | 0.1236 | 2.2522 | 1.3046
1634.1719 | 123.0698 | -57.1838 | 65.6021 | -0.075836 | 0.0014761 | 0.062025 | 0.074813 | -0.00090783 | 0.0017645 | 0.0073444 | 0.044434 | 0.0013159 | 0.001068 | 0.0013416 | -0.00065151 | -0.0025891 | -0.0014697 | -54.982 | 65.5609 | -57.2937 | 65.4831 | -56.2683 | -56.8588 | -56.0165 | -55.8517 | 65.593 | -57.2342 | -57.1381 | -57.1472 | -57.2205 | -56.9595 | -0.10986 | -0.041199 | -0.11902 | 0.91553 | 1.1673 | 0.32501 | 1.2772 | 0.43487 | -0.050354 | -0.009155 | -122.7402 | 0.036621 | 0.2243 | -0.036621 | 0.27466 | 0.013733 | 1.0254 | 122.7768 | 0.086975 | 0.09613 | 122.8546 | 122.8271 | 122.7448 | 122.7768 | -122.8958 | -122.8363 | 122.6669 | 0.045776 | 2.2018 | 1.3321
1635.1719 | 123.0743 | -57.2296 | 65.6067 | -0.098725 | 0.00040806 | 0.063307 | 0.073745 | -0.0041122 | 0.0026191 | 0.0090534 | -0.0013428 | 0.00046135 | 0.001068 | 0.00048702 | -0.0032151 | -0.0034437 | -0.00082886 | -54.982 | 65.5472 | -57.2983 | 65.2679 | -56.3873 | -56.7719 | -56.0623 | -55.8792 | 65.6158 | -57.2525 | -57.1243 | -57.1243 | -57.2342 | -56.9641 | -0.068665 | -0.059509 | -0.33875 | 0.84228 | 1.1673 | 0.45776 | 1.236 | 0.52643 | -0.022888 | 0.009156 | -122.731 | 0.10528 | 0.2655 | -0.004578 | 0.28839 | 0.01831 | 0.91095 | 122.5662 | 0.12817 | 0.12817 | 122.8455 | 122.8683 | 122.7768 | 122.8455 | -122.905 | -122.8592 | 122.4976 | 0.10528 | 2.2476 | 1.3504
1636.1719 | 123.0698 | -57.2433 | 65.5838 | -0.098725 | -0.00044654 | 0.062666 | 0.073958 | -0.00090783 | 0.0021917 | 0.007558 | 0.026123 | 0.0021703 | 0.0019226 | 0.00048702 | -0.0017197 | -0.0025891 | -0.0031787 | -55.0278 | 65.5472 | -57.3395 | 65.4099 | -56.3828 | -56.9458 | -56.1035 | -55.9616 | 65.5975 | -57.2845 | -57.1747 | -57.1655 | -57.2617 | -56.9778 | -0.096131 | -0.036621 | -0.17395 | 0.8606 | 1.1398 | 0.29755 | 1.236 | 0.39368 | -0.041199 | 0.013733 | -122.7585 | 0.07782 | 0.2655 | -0.018311 | 0.3067 | 0.022888 | 0.95673 | 122.7493 | 0.11902 | 0.10986 | 122.8867 | 122.8821 | 122.7905 | 122.8409 | -122.9233 | -122.8683 | 122.6532 | 0.068664 | 2.2156 | 1.2817
1637.1719 | 123.0377 | -57.225 | 65.5792 | -0.098725 | -1.9142e-05 | 0.064162 | 0.076095 | -0.0032578 | 0.0032599 | 0.0073444 | 0.032227 | 0.0013159 | -0.00085457 | -0.00229 | -1.0706e-05 | -0.0025891 | -0.0014697 | -54.9088 | 65.5746 | -57.312 | 65.4007 | -56.369 | -56.9778 | -56.1172 | -55.9799 | 65.5792 | -57.2754 | -57.1884 | -57.193 | -57.2891 | -56.9962 | -0.086975 | -0.004578 | -0.17853 | 0.85602 | 1.1078 | 0.24719 | 1.1948 | 0.33417 | -0.050354 | 0 | -122.7676 | 0.032044 | 0.22888 | -0.064087 | 0.27924 | -0.013733 | 0.94299 | 122.7127 | 0.082398 | 0.086975 | 122.8867 | 122.8546 | 122.7997 | 122.8043 | -122.8912 | -122.8546 | 122.6257 | 0.036621 | 2.3163 | 1.2451
1638.1719 | 123.0743 | -57.2067 | 65.5884 | -0.075836 | 0.00062166 | 0.060744 | 0.074386 | -0.0030442 | 0.0032599 | 0.0047808 | 0.010864 | 0.00067495 | 0.0023498 | -0.0016492 | -0.0012925 | -0.0032301 | -0.00082886 | -54.9774 | 65.5518 | -57.3029 | 65.4831 | -56.2866 | -56.8909 | -56.0211 | -55.8517 | 65.5838 | -57.2342 | -57.1152 | -57.1106 | -57.2159 | -56.9366 | -0.09613 | -0.036621 | -0.10529 | 0.92011 | 1.1856 | 0.31586 | 1.2817 | 0.41199 | -0.027466 | -0.004578 | -122.7036 | 0.09613 | 0.27008 | -0.009155 | 0.29755 | 0.018311 | 1.0162 | 122.7859 | 0.1236 | 0.11902 | 122.8546 | 122.818 | 122.7585 | 122.7905 | -122.8912 | -122.8226 | 122.6898 | 0.091553 | 2.2293 | 1.355
1639.1719 | 123.0789 | -57.2296 | 65.5701 | -0.052948 | -0.0023691 | 0.061598 | 0.072463 | 0.001442 | 0.0011237 | 0.0067036 | 0.023071 | -0.0012477 | -0.0025636 | 0.002196 | -0.0032151 | -0.0034437 | 0.0042981 | -54.9683 | 65.5609 | -57.2891 | 65.4877 | -56.2912 | -56.8726 | -56.0349 | -55.6458 | 65.6662 | -57.2021 | -57.1289 | -57.193 | -57.2205 | -56.9641 | -0.05951 | -0.009155 | -0.082397 | 0.93841 | 1.1948 | 0.35705 | 1.2543 | 0.41656 | 0.027466 | 0.096131 | -122.699 | 0.036621 | 0.2655 | 0.009155 | 0.23804 | -0.018311 | 0.99793 | 122.7768 | 0.009155 | 0.073242 | 122.85 | 122.8683 | 122.7905 | 122.8958 | -122.8592 | -122.7722 | 122.7173 | 0.10071 | 2.2614 | 1.5839
1640.1719 | 123.0331 | -57.1884 | 65.5563 | -0.12161 | -0.00023294 | 0.06288 | 0.073745 | -0.00069423 | 0.0036871 | 0.0062762 | 0.001709 | -0.00082025 | 0.00064083 | 0.00070062 | -0.0042831 | -0.0017347 | 0.0025891 | -54.982 | 65.5472 | -57.2983 | 65.5014 | -56.2775 | -56.8588 | -56.0257 | -55.8655 | 65.593 | -57.2571 | -57.1198 | -57.1747 | -56.868 | -56.7215 | -0.10986 | -0.009155 | -0.054931 | 0.91095 | 1.1627 | 0.32959 | 1.2726 | 0.43945 | -0.068664 | 0.036622 | -122.6761 | 0.013733 | 0.46692 | 0.32043 | 0.53558 | 0.3891 | 1.0208 | 122.7997 | 0.082397 | 0.13733 | 122.8455 | 122.85 | 122.7356 | 122.7814 | -122.8546 | -122.8134 | 122.6898 | 0.068665 | 2.2064 | 1.3229
1641.1719 | 123.0927 | -57.2067 | 65.593 | -0.045319 | 0.0012625 | 0.063307 | 0.072677 | 0.0018692 | 0.0013373 | 0.0069172 | 0.029175 | 0.00046135 | 0.001068 | -0.0025036 | -0.0010787 | -0.0038709 | 0.00045294 | -54.9866 | 65.5472 | -57.3257 | 65.4877 | -56.2912 | -56.8726 | -56.0211 | -55.8426 | 65.5701 | -57.2296 | -57.106 | -57.1335 | -57.2296 | -56.9595 | -0.11902 | -0.045777 | -0.10529 | 0.91553 | 1.1856 | 0.33417 | 1.3046 | 0.45319 | -0.022888 | -0.022889 | -122.699 | 0.073242 | 0.24719 | -0.022888 | 0.27008 | 0 | 1.0345 | 122.8134 | 0.09613 | 0.1236 | 122.8729 | 122.7997 | 122.7539 | 122.7768 | -122.9187 | -122.8226 | 122.6944 | 0.10071 | 2.2202 | 1.3641
1642.1719 | 123.0698 | -57.1976 | 65.6204 | -0.10635 | -0.00066014 | 0.061812 | 0.071822 | -0.0024032 | 0.0047553 | 0.010121 | 0.026123 | 0.00067495 | 0.00064083 | 0.0043322 | -0.0010787 | -0.0032301 | -0.0023243 | -54.9774 | 65.5563 | -57.2937 | 65.6433 | -56.0394 | -57.106 | -56.2912 | -55.8975 | 65.5884 | -57.2525 | -57.1381 | -57.1335 | -57.2433 | -56.955 | -0.09613 | -0.064087 | 0.022889 | 1.1581 | 0.90637 | 0.091553 | 1.0025 | 0.18768 | -0.054931 | -0.032043 | -122.7585 | 0.064087 | 0.24262 | -0.045776 | 0.29755 | 0.009155 | 1.2543 | 122.937 | 0.11902 | 0.11444 | 122.85 | 122.8409 | 122.7539 | 122.786 | -122.9141 | -122.8729 | 122.8409 | 0.059509 | 2.2202 | 1.3
1643.1719 | 123.0377 | -57.2433 | 65.5838 | -0.075836 | -1.9142e-05 | 0.061385 | 0.073318 | -5.343e-05 | 0.0019781 | 0.0060626 | 0.023071 | 0.0013159 | -0.0012818 | -0.00036738 | 0.00041649 | -0.0023755 | -0.00040166 | -55.0415 | 65.538 | -57.3303 | 65.419 | -56.3828 | -56.9504 | -56.1081 | -55.9662 | 65.5884 | -57.2891 | -57.1793 | -57.1609 | -57.2754 | -56.9916 | -0.086975 | -0.045776 | -0.16479 | 0.8606 | 1.1353 | 0.29297 | 1.2222 | 0.37994 | -0.045777 | 0.004578 | -122.7631 | 0.082397 | 0.25177 | -0.032044 | 0.29755 | 0.013733 | 0.94757 | 122.7493 | 0.12817 | 0.10986 | 122.8683 | 122.8775 | 122.7814 | 122.8317 | -122.9141 | -122.8729 | 122.6624 | 0.064087 | 2.2018 | 1.2772
1644.1719 | 123.024 | -57.2342 | 65.5609 | -0.12161 | -0.00044654 | 0.063094 | 0.074599 | -5.343e-05 | 0.0034735 | 0.005849 | 0.001709 | 0.0017431 | -0.00042717 | -0.0010084 | -0.00086511 | -0.0017347 | -0.0010425 | -55.0735 | 65.538 | -57.3395 | 65.4053 | -56.4011 | -56.9824 | -56.1264 | -55.9845 | 65.5838 | -57.2845 | -57.2021 | -57.1976 | -57.312 | -57.0236 | -0.10529 | -0.022888 | -0.15564 | 0.83313 | 1.1078 | 0.25177 | 1.2131 | 0.35706 | -0.050354 | 0.022888 | -122.7631 | 0.036621 | 0.21057 | -0.07782 | 0.26093 | -0.027466 | 0.93842 | 122.7448 | 0.086975 | 0.082398 | 122.8775 | 122.8683 | 122.7722 | 122.818 | -122.9004 | -122.8455 | 122.6395 | 0.032044 | 2.1606 | 1.2497
1645.1719 | 123.0743 | -57.2021 | 65.5655 | -0.083466 | 0.00040806 | 0.063734 | 0.073745 | 0.0010148 | 0.0011237 | 0.007558 | 0.029175 | 0.00067495 | 0.00064083 | -0.0020764 | -0.00043791 | -0.0025891 | -0.00018806 | -55.0186 | 65.5334 | -57.3212 | 65.4602 | -56.3644 | -56.9275 | -56.0761 | -55.925 | 65.5838 | -57.2571 | -57.1472 | -57.1335 | -57.225 | -56.9687 | -0.11902 | -0.032044 | -0.10529 | 0.83771 | 1.1261 | 0.27466 | 1.2451 | 0.39368 | -0.054932 | 0.01831 | -122.7127 | 0.068664 | 0.23346 | -0.022889 | 0.28839 | 0.032043 | 0.95673 | 122.7814 | 0.1236 | 0.10986 | 122.8546 | 122.8409 | 122.7356 | 122.7859 | -122.8867 | -122.8226 | 122.6624 | 0.054931 | 2.1835 | 1.2772
1646.1719 | 123.0835 | -57.2021 | 65.5518 | -0.098725 | -0.00087374 | 0.061385 | 0.074813 | 0.0020828 | 0.0034735 | 0.0073444 | 0.010864 | 0.00067495 | 0.00085443 | -0.00036738 | -0.0025741 | -0.0023755 | -0.0012561 | -54.9728 | 65.5609 | -57.2617 | 65.4831 | -56.2775 | -56.8726 | -56.0257 | -55.8517 | 65.5792 | -57.2479 | -57.1152 | -57.1381 | -57.2113 | -56.9595 | -0.05951 | 0.009155 | -0.068665 | 0.92468 | 1.1765 | 0.32959 | 1.236 | 0.3891 | -0.045777 | 0.027466 | -122.6669 | 0.064086 | 0.24261 | -0.009156 | 0.28839 | 0.036621 | 0.98419 | 122.7448 | 0.10986 | 0.13275 | 122.8226 | 122.8271 | 122.7631 | 122.7814 | -122.8134 | -122.7997 | 122.6852 | 0.086975 | 2.2293 | 1.3504
1647.1719 | 123.1018 | -57.2113 | 65.5746 | -0.12924 | 0.0010489 | 0.065016 | 0.073958 | -0.0013352 | 0.0019781 | 0.0077716 | 0.023071 | -0.00039305 | 0.001709 | -0.0042126 | -0.0023605 | -0.0025891 | -0.0040333 | -54.9774 | 65.5426 | -57.2891 | 65.4877 | -56.2912 | -56.8771 | -56.0394 | -55.8517 | 65.5746 | -57.2662 | -57.1152 | -57.1198 | -57.2433 | -56.9595 | -0.07782 | -0.032043 | -0.086975 | 0.9201 | 1.1719 | 0.33417 | 1.2497 | 0.41199 | -0.054931 | 0 | -122.6898 | 0.091553 | 0.25177 | -0.032043 | 0.3067 | 0.022888 | 0.99793 | 122.7768 | 0.14648 | 0.15106 | 122.8317 | 122.8409 | 122.7539 | 122.7859 | -122.8638 | -122.8409 | 122.699 | 0.096131 | 2.2339 | 1.3596
1648.1719 | 123.0881 | -57.2021 | 65.5792 | -0.10635 | -1.9142e-05 | 0.063948 | 0.074386 | -0.0015488 | 0.0021917 | 0.0096942 | 0.016968 | 0.00046135 | 0.0019226 | 0.0036914 | -0.0019333 | -0.0049389 | 0.0036571 | -54.9866 | 65.5243 | -57.3029 | 65.4922 | -56.2866 | -56.868 | -56.0349 | -55.8334 | 65.5884 | -57.2525 | -57.1152 | -57.1243 | -57.2205 | -56.9504 | -0.10071 | -0.054932 | -0.086975 | 0.91553 | 1.1673 | 0.33417 | 1.268 | 0.43487 | -0.050354 | 0.009155 | -122.6944 | 0.077819 | 0.25177 | -0.018311 | 0.30212 | 0.032043 | 1.0162 | 122.7951 | 0.12817 | 0.13733 | 122.8271 | 122.8409 | 122.7264 | 122.7905 | -122.8821 | -122.8317 | 122.6944 | 0.086975 | 2.2156 | 1.3687
1649.1719 | 123.1247 | -57.193 | 65.5792 | -0.083466 | 0.0021171 | 0.063521 | 0.071822 | -0.0017624 | 0.0034735 | 0.0086262 | 0.013916 | -0.00082025 | 0.00085443 | 0.00027342 | -0.0032151 | -0.0021619 | -0.0046741 | -54.9866 | 65.5334 | -57.2937 | 65.4739 | -56.2866 | -56.8726 | -56.0394 | -55.8289 | 65.5792 | -57.2296 | -57.106 | -57.1289 | -57.2296 | -56.9595 | -0.10071 | -0.045777 | -0.10529 | 0.90637 | 1.1536 | 0.32043 | 1.2543 | 0.42114 | -0.036621 | 0 | -122.6852 | 0.064087 | 0.23346 | -0.036621 | 0.27008 | 0 | 1.0071 | 122.7676 | 0.10071 | 0.1236 | 122.8271 | 122.8088 | 122.7264 | 122.7722 | -122.8729 | -122.8088 | 122.6669 | 0.086975 | 2.2064 | 1.3641
1650.1719 | 123.0743 | -57.2159 | 65.5746 | -0.091095 | -0.00044654 | 0.06288 | 0.073104 | -0.003685 | 0.0030463 | 0.0079852 | -0.0013428 | 0.0021703 | 0.00042723 | 0.0058276 | -0.0021469 | -0.00088008 | 0.0019483 | -54.9637 | 65.5472 | -57.2983 | 65.4922 | -56.2729 | -56.8634 | -56.044 | -55.838 | 65.593 | -57.2342 | -57.1106 | -57.1243 | -57.225 | -56.9595 | -0.082398 | -0.027466 | -0.082397 | 0.94299 | 1.1719 | 0.35248 | 1.2543 | 0.43488 | -0.018311 | 0.018311 | -122.6852 | 0.091552 | 0.25635 | -0.009156 | 0.27466 | 0.009155 | 1.0254 | 122.7905 | 0.10986 | 0.1236 | 122.8455 | 122.8271 | 122.7631 | 122.8088 | -122.8729 | -122.8088 | 122.7081 | 0.10529 | 2.2522 | 1.3779
1651.1719 | 123.0515 | -57.2296 | 65.5746 | -0.083466 | 0.00062166 | 0.062239 | 0.074386 | -5.343e-05 | 0.0041143 | 0.0086262 | 0.026123 | 0.0023839 | -0.00085457 | -0.0048536 | -0.00065151 | -0.0021619 | -0.0046741 | -55.0415 | 65.5472 | -57.3212 | 65.387 | -56.4239 | -56.955 | -56.1127 | -55.9662 | 65.5792 | -57.2617 | -57.1793 | -57.193 | -57.2891 | -57.0099 | -0.091553 | -0.027466 | -0.18768 | 0.80566 | 1.1169 | 0.27466 | 1.2085 | 0.36621 | -0.032044 | 0.004578 | -122.7539 | 0.036621 | 0.21973 | -0.05951 | 0.25177 | -0.027466 | 0.89722 | 122.7081 | 0.068665 | 0.082398 | 122.8683 | 122.8409 | 122.7768 | 122.8088 | -122.8958 | -122.8363 | 122.6166 | 0.050354 | 2.1881 | 1.2634
1652.1719 | 123.1888 | -57.1838 | 65.6158 | -0.075836 | -0.0015145 | 0.061598 | 0.073958 | -0.00069423 | 0.0015509 | 0.0052082 | -0.0074462 | 3.4148e-05 | 0.001709 | 0.002196 | -0.0017197 | -0.0034437 | 0.0015209 | -54.9683 | 65.5426 | -57.3029 | 65.5014 | -56.2775 | -56.8771 | -56.0303 | -55.8426 | 65.6113 | -57.2525 | -57.1335 | -57.1152 | -57.2296 | -57.106 | -0.11902 | -0.073242 | -0.11444 | 0.90637 | 1.1536 | 0.3067 | 1.2726 | 0.42572 | -0.068664 | -0.004578 | -122.7493 | 0.068665 | 0.07782 | -0.045776 | 0.14648 | 0.022888 | 1.0254 | 122.8043 | 0.13733 | 0.11902 | 122.8455 | 122.8638 | 122.7264 | 122.7951 | -122.9187 | -122.8683 | 122.6852 | 0.050354 | 2.2156 | 1.3412
1653.1719 | 122.9782 | -57.2388 | 65.5472 | -0.060578 | 0.00019446 | 0.063734 | 0.073318 | -0.0051804 | 0.00091009 | 0.007558 | 0.026123 | 3.4148e-05 | -0.0010682 | -0.0044262 | -0.0019333 | -0.0023755 | -0.0046741 | -54.9774 | 65.5609 | -57.312 | 65.4968 | -56.2683 | -56.8634 | -56.0349 | -55.8563 | 65.6158 | -57.2296 | -57.2296 | -56.8039 | -57.0648 | -57.0099 | -0.073242 | 0.013733 | -0.050354 | 0.97046 | 1.2039 | 0.37537 | 1.2772 | 0.44861 | 0.009156 | 0.068665 | -122.7768 | 0.43488 | 0.22888 | 0.17395 | 0.21973 | 0.16479 | 1.0437 | 122.8088 | 0.42572 | 0 | 122.8729 | 122.8455 | 122.7997 | 122.8546 | -122.8592 | -122.7768 | 122.7356 | 0.009156 | 2.2614 | 1.3824
1654.1719 | 123.0011 | -57.2525 | 65.5563 | -0.091095 | -1.9142e-05 | 0.061171 | 0.073104 | 0.0012284 | 0.0034735 | 0.0094806 | -0.089844 | 0.0013159 | -0.00085457 | -0.001222 | -0.0012925 | -0.0034437 | 2.554e-05 | -54.9271 | 65.5518 | -57.3807 | 65.3366 | -56.4926 | -57.1014 | -56.2408 | -56.0806 | 65.5838 | -57.3212 | -57.2571 | -57.2983 | -57.4173 | -57.0923 | -0.12817 | -0.004577 | -0.21973 | 0.75989 | 1.0117 | 0.15106 | 1.1398 | 0.27924 | -0.068665 | 0.027466 | -122.8134 | -0.045777 | 0.16022 | -0.16479 | 0.22888 | -0.09613 | 0.88806 | 122.7173 | 0.022888 | 0.064087 | 122.9324 | 122.905 | 122.8043 | 122.8363 | -122.937 | -122.8775 | 122.5891 | -0.004578 | 2.3254 | 1.1719
1655.1719 | 123.0148 | -57.2296 | 65.6021 | -0.083466 | 0.0025443 | 0.063734 | 0.072677 | 0.00058737 | 0.0032599 | 0.007558 | 0.013916 | 0.00088875 | -0.00085457 | -0.0010084 | 0.00063009 | -0.0025891 | -0.0010425 | -54.9774 | 65.5746 | -57.312 | 65.4739 | -56.3324 | -56.8954 | -56.0761 | -55.8884 | 65.6158 | -57.225 | -57.1655 | -57.1701 | -57.2571 | -56.9778 | -0.082398 | -0.027466 | -0.12817 | 0.89722 | 1.1536 | 0.33417 | 1.236 | 0.41657 | 0.004577 | 0.013733 | -122.7676 | 0.059509 | 0.25177 | -0.027466 | 0.24719 | -0.032043 | 0.97962 | 122.786 | 0.054932 | 0.05951 | 122.8867 | 122.8409 | 122.8043 | 122.8455 | -122.9141 | -122.8271 | 122.7036 | 0.064087 | 2.2522 | 1.3412
1656.1719 | 123.024 | -57.2205 | 65.6021 | -0.091095 | 0.0029715 | 0.063094 | 0.073745 | 0.0022964 | 0.00026909 | 0.0088398 | -0.0074462 | 0.00088875 | 0.002777 | 0.0030506 | -0.0017197 | -0.0025891 | -0.0025379 | -54.9866 | 65.5472 | -57.2845 | 65.4556 | -56.337 | -56.8771 | -56.0852 | -55.9067 | 65.6158 | -57.2342 | -57.1655 | -57.1838 | -57.2662 | -57.0053 | -0.064087 | -0.054932 | -0.14648 | 0.88348 | 1.1353 | 0.34332 | 1.1993 | 0.40741 | -0.013733 | 0.013733 | -122.7676 | 0.036621 | 0.21515 | -0.045776 | 0.22888 | -0.032043 | 0.94757 | 122.7402 | 0.050354 | 0.068665 | 122.8317 | 122.85 | 122.7676 | 122.8363 | -122.8867 | -122.8363 | 122.6761 | 0.054932 | 2.2339 | 1.3138
1657.1719 | 123.0881 | -57.2205 | 65.5701 | -0.091095 | 0.00040806 | 0.061171 | 0.072463 | -0.0024032 | 0.0032599 | 0.0094806 | 0.035278 | -0.00060665 | 0.001709 | -0.0052808 | -0.0012925 | -0.0032301 | 0.0025891 | -54.9911 | 65.5563 | -57.3166 | 65.4694 | -56.3095 | -56.8771 | -56.044 | -55.8746 | 65.5655 | -57.2571 | -57.106 | -57.1106 | -57.1976 | -56.9412 | -0.09613 | -0.013733 | -0.10071 | 0.91095 | 1.1765 | 0.34332 | 1.2726 | 0.43945 | -0.036621 | -0.004577 | -122.6761 | 0.10986 | 0.27924 | 0.022888 | 0.31586 | 0.059509 | 1.0071 | 122.7859 | 0.14648 | 0.15106 | 122.8729 | 122.8226 | 122.7768 | 122.7859 | -122.8867 | -122.8271 | 122.6898 | 0.11444 | 2.2293 | 1.3458
1658.1719 | 123.1155 | -57.2205 | 65.5838 | -0.11398 | -0.00023294 | 0.063734 | 0.072463 | 0.001442 | 0.0043281 | 0.005849 | 0.02002 | 0.00046135 | 0.0014954 | -0.00036738 | -0.0019333 | -0.0040845 | -0.0018971 | -54.9866 | 65.5472 | -57.3166 | 65.4694 | -56.3095 | -56.8954 | -56.0577 | -55.8609 | 65.593 | -57.2433 | -57.1014 | -57.1198 | -57.2067 | -56.9321 | -0.09613 | -0.036621 | -0.11444 | 0.91095 | 1.1627 | 0.32501 | 1.2589 | 0.42114 | -0.022888 | 0.009156 | -122.6852 | 0.10071 | 0.28839 | 0.013733 | 0.31128 | 0.036621 | 1.0071 | 122.7859 | 0.1236 | 0.14191 | 122.8638 | 122.8363 | 122.7676 | 122.8134 | -122.9004 | -122.8271 | 122.6898 | 0.11902 | 2.2339 | 1.3596
1659.1719 | 123.0011 | -57.2296 | 65.5838 | -0.045319 | -0.00087374 | 0.063094 | 0.07524 | 0.0035782 | 0.0030463 | 0.0069172 | -0.08374 | 0.0011023 | 0.00042723 | 0.0032642 | -0.0044967 | -0.0021619 | 0.00088014 | -55.0003 | 65.5472 | -57.3532 | 65.3961 | -56.4056 | -56.9962 | -56.1584 | -56.0898 | 65.5975 | -57.28 | -57.1884 | -57.2754 | -57.3349 | -57.019 | -0.1236 | -0.036621 | -0.18768 | 0.82397 | 1.0712 | 0.23346 | 1.1948 | 0.35705 | -0.050354 | 0.013733 | -122.7722 | -0.045777 | 0.21057 | -0.10529 | 0.26092 | -0.054932 | 0.94757 | 122.7493 | 0.004577 | 0.091552 | 122.9004 | 122.8775 | 122.7768 | 122.8271 | -122.937 | -122.8638 | 122.6257 | 0.041198 | 2.2293 | 1.1398
1660.1719 | 122.9965 | -57.2433 | 65.6113 | -0.022431 | -0.00023294 | 0.061171 | 0.074386 | 0.0022964 | 5.5488e-05 | 0.009267 | -0.03186 | 0.00088875 | -0.0014954 | 0.0051868 | -0.0012925 | -0.0030163 | -0.00082886 | -55.0323 | 65.5838 | -57.3257 | 65.3366 | -56.4606 | -57.0053 | -56.1859 | -56.0165 | 65.6387 | -57.2983 | -57.225 | -57.2433 | -57.3624 | -57.0602 | -0.082398 | -0.027466 | -0.27466 | 0.78278 | 1.0574 | 0.23804 | 1.1398 | 0.32043 | -0.054932 | 0.027466 | -122.8363 | 0 | 0.1831 | -0.11902 | 0.23804 | -0.064087 | 0.86517 | 122.6624 | 0.054932 | 0.073242 | 122.9095 | 122.937 | 122.8271 | 122.8821 | -122.937 | -122.9095 | 122.58 | 0.01831 | 2.211 | 1.2268
1661.1719 | 122.9416 | -57.2525 | 65.625 | -0.083466 | 0.0027579 | 0.063307 | 0.072677 | 0.0022964 | 0.00026909 | 0.0067036 | 0.0078126 | -0.00060665 | 0.00064083 | -0.0033582 | -0.0019333 | -0.0053663 | 0.0015209 | -54.9866 | 65.5655 | -57.2937 | 65.4144 | -56.3782 | -56.955 | -56.1264 | -55.9479 | 65.6296 | -57.2983 | -57.2113 | -57.225 | -57.3441 | -57.0511 | -0.041199 | -0.059509 | -0.21057 | 0.87433 | 1.1261 | 0.29755 | 1.1673 | 0.33874 | -0.045777 | 0.004578 | -122.8363 | 0.027465 | 0.20142 | -0.091553 | 0.24719 | -0.045776 | 0.91553 | 122.7081 | 0.073242 | 0.086975 | 122.8592 | 122.9279 | 122.818 | 122.8821 | -122.9187 | -122.9233 | 122.6669 | 0.041198 | 2.2659 | 1.3046
1662.1719 | 122.9462 | -57.2433 | 65.6113 | -0.052948 | -0.00066014 | 0.061812 | 0.073531 | -0.0011214 | 0.0024053 | 0.010549 | 0.065796 | 0.0025975 | 0.0029906 | -0.00079478 | -0.00065151 | 0.00061532 | -0.0029651 | -55.0598 | 65.6296 | -57.3257 | 65.3503 | -56.4423 | -56.9916 | -56.1813 | -56.0715 | 65.657 | -57.2617 | -57.2479 | -57.2525 | -57.3669 | -57.0694 | -0.082398 | 0.018311 | -0.26093 | 0.80109 | 1.062 | 0.25177 | 1.1444 | 0.33417 | -0.018311 | 0.045776 | -122.8592 | -0.009155 | 0.17395 | -0.1236 | 0.19226 | -0.10529 | 0.88348 | 122.6761 | 0.009156 | 0.013733 | 122.9553 | 122.9187 | 122.8729 | 122.9004 | -122.937 | -122.8729 | 122.5937 | -0.004578 | 2.1835 | 1.1719
1663.1719 | 122.9645 | -57.2342 | 65.6204 | -0.03006 | 0.0025443 | 0.06288 | 0.074599 | -0.0015488 | 0.0021917 | 0.0073444 | -0.056274 | 0.00067495 | -0.00042717 | 0.00048702 | 0.0010575 | -0.0019483 | -0.0021107 | -55.0598 | 65.6113 | -57.3166 | 65.3549 | -56.4102 | -56.7078 | -56.1951 | -56.012 | 65.6158 | -57.312 | -57.2296 | -57.2479 | -57.3395 | -57.0465 | -0.082397 | -0.009155 | -0.2655 | 0.82397 | 1.0391 | 0.52643 | 1.1215 | 0.60883 | -0.07782 | -0.004577 | -122.85 | -0.013733 | 0.18768 | -0.10529 | 0.2655 | -0.027466 | 0.90637 | 122.6715 | 0.064087 | 0.082398 | 122.9279 | 122.9279 | 122.8455 | 122.85 | -122.937 | -122.9324 | 122.5891 | 0.004578 | 2.1744 | 1.2222
1664.1719 | 123.0469 | -57.2754 | 65.5563 | -0.12161 | -1.9142e-05 | 0.062239 | 0.072677 | 0.0010148 | 0.0034735 | 0.0062762 | -0.041016 | 0.00067495 | 0.00085443 | -0.0052808 | -0.0034287 | -0.0021619 | 0.0023755 | -55.0827 | 65.5197 | -57.3807 | 65.3503 | -56.4468 | -57.0282 | -56.1905 | -55.9753 | 65.5518 | -57.2983 | -57.1838 | -57.2342 | -57.3212 | -56.9962 | -0.10529 | -0.036621 | -0.20599 | 0.82855 | 1.0849 | 0.24719 | 1.1902 | 0.35248 | -0.022888 | -0.004577 | -122.7402 | 0.041199 | 0.27924 | -0.045776 | 0.30212 | -0.022888 | 0.93384 | 122.731 | 0.064087 | 0.11444 | 122.9004 | 122.85 | 122.7951 | 122.8271 | -122.937 | -122.8546 | 122.6257 | 0.091553 | 2.1927 | 1.3
1665.1719 | 122.9645 | -57.2662 | 65.6204 | -0.068207 | -1.9142e-05 | 0.06288 | 0.07225 | -0.0032578 | 0.0017645 | 0.0079852 | 0.0078126 | -0.00017945 | -0.00021357 | 0.0026232 | 0.0014847 | -0.0028027 | -0.0012561 | -55.0186 | 65.5975 | -57.3349 | 65.3732 | -56.4056 | -56.955 | -56.1584 | -56.0074 | 65.6342 | -57.28 | -57.225 | -57.2342 | -57.3532 | -57.0557 | -0.068665 | -0.022888 | -0.24719 | 0.8606 | 1.1078 | 0.31128 | 1.1765 | 0.37994 | -0.013733 | 0.013733 | -122.8455 | 0.032043 | 0.21057 | -0.086975 | 0.2243 | -0.073242 | 0.92926 | 122.7081 | 0.045776 | 0.054931 | 122.9324 | 122.9141 | 122.8638 | 122.9004 | -122.9553 | -122.9004 | 122.6395 | 0.041198 | 2.2476 | 1.2589
1666.1719 | 122.9233 | -57.2205 | 65.6158 | -0.045319 | 0.00019446 | 0.061385 | 0.073318 | 0.00080117 | 0.0030463 | 0.0084124 | 0.001709 | 0.0013159 | 2.8e-08 | -0.0048536 | -0.00065151 | -0.0023755 | -0.00061526 | -55.0644 | 65.625 | -57.312 | 65.3778 | -56.4331 | -57.074 | -56.1905 | -56.0303 | 65.6113 | -57.2754 | -57.2525 | -57.2479 | -57.3578 | -57.0511 | -0.091553 | 0.009155 | -0.23804 | 0.78735 | 1.03 | 0.14648 | 1.1215 | 0.23804 | -0.054932 | -0.004578 | -122.8683 | -0.027466 | 0.16937 | -0.13733 | 0.22431 | -0.082397 | 0.87891 | 122.6898 | 0.027466 | 0.022889 | 122.937 | 122.8867 | 122.8455 | 122.8317 | -122.9279 | -122.8912 | 122.5983 | -0.032043 | 2.1561 | 1.1902
1667.1719 | 122.9782 | -57.2571 | 65.625 | -0.045319 | -0.0019417 | 0.06523 | 0.073745 | 0.0022964 | 0.0034735 | 0.0049946 | -0.010498 | 0.00088875 | 0.001068 | -0.001222 | -0.00086511 | -0.0021619 | 0.0015209 | -55.0369 | 65.6067 | -57.3441 | 65.3687 | -56.456 | -57.074 | -56.2088 | -56.0257 | 65.6158 | -57.28 | -57.2479 | -57.2571 | -57.3624 | -57.0511 | -0.086975 | -0.018311 | -0.25635 | 0.80109 | 1.0483 | 0.18311 | 1.1353 | 0.27008 | -0.022888 | -0.009155 | -122.8729 | 0 | 0.20599 | -0.10529 | 0.22888 | -0.082398 | 0.88806 | 122.7127 | 0.022888 | 0.032043 | 122.9507 | 122.8958 | 122.8638 | 122.8729 | -122.9691 | -122.905 | 122.6257 | 0.009155 | 2.2202 | 1.2314
1668.1719 | 122.9691 | -57.2662 | 65.625 | -0.060578 | -0.0021555 | 0.063307 | 0.074599 | 0.003151 | 0.0043281 | 0.0086262 | -0.010498 | 0.00088875 | 0.0014954 | 0.0034778 | -0.0021469 | -0.0028027 | -0.0029651 | -55.069 | 65.5975 | -57.312 | 65.2405 | -56.4651 | -56.9824 | -56.218 | -56.044 | 65.625 | -57.2754 | -57.2388 | -57.2662 | -57.3532 | -57.0465 | -0.045777 | -0.027466 | -0.38452 | 0.80109 | 1.0483 | 0.28381 | 1.0941 | 0.32959 | -0.009156 | 0 | -122.8638 | 0 | 0.21973 | -0.086975 | 0.22888 | -0.077819 | 0.84686 | 122.5525 | 0.009156 | 0.036621 | 122.9095 | 122.9004 | 122.8638 | 122.8912 | -122.937 | -122.9004 | 122.5067 | 0.027465 | 2.1973 | 1.2222
1669.1719 | 123.0194 | -57.2662 | 65.538 | -0.098725 | 0.0023307 | 0.063948 | 0.07225 | -0.00090783 | 0.0047553 | 0.0084124 | 0.023071 | 0.00067495 | 0.0025634 | -0.0082716 | -1.0706e-05 | -0.0030163 | -0.0021107 | -55.0323 | 65.506 | -57.3441 | 65.4099 | -56.3736 | -56.987 | -56.1127 | -55.9113 | 65.5518 | -57.2891 | -57.1793 | -57.2159 | -57.3212 | -57.0236 | -0.07782 | -0.032044 | -0.12817 | 0.89264 | 1.1536 | 0.27923 | 1.2314 | 0.35705 | -0.022889 | 0.013733 | -122.7173 | 0.050354 | 0.24261 | -0.054932 | 0.2655 | -0.032043 | 0.97046 | 122.7539 | 0.073243 | 0.10986 | 122.85 | 122.8409 | 122.7722 | 122.818 | -122.8821 | -122.8271 | 122.6761 | 0.086975 | 2.2339 | 1.355
1670.1719 | 122.9782 | -57.2617 | 65.6113 | -0.075836 | 0.0012625 | 0.060744 | 0.072463 | -0.001976 | 0.0036871 | 0.0086262 | -0.0074462 | 0.00046135 | 0.00064083 | 0.00048702 | -0.0027877 | -0.0017347 | -0.0014697 | -55.0781 | 65.6204 | -57.3349 | 65.2908 | -56.6208 | -56.9733 | -56.2088 | -56.0211 | 65.6204 | -57.3074 | -57.2433 | -57.2571 | -57.3669 | -57.0602 | -0.073242 | 0.009155 | -0.32043 | 0.64087 | 1.0529 | 0.28839 | 1.1261 | 0.36163 | -0.045776 | 0.009155 | -122.8546 | 0.004578 | 0.20142 | -0.10529 | 0.24719 | -0.059509 | 0.71411 | 122.6257 | 0.050354 | 0.064087 | 122.9553 | 122.9279 | 122.8821 | 122.8821 | -122.9462 | -122.9187 | 122.5525 | 0.018311 | 2.1835 | 1.2405
1671.1719 | 122.9599 | -57.2708 | 65.6067 | -0.068207 | -0.00044654 | 0.060957 | 0.074386 | -0.0015488 | -0.00015811 | 0.0060626 | 0.02002 | 0.00088875 | 0.0023498 | 0.0047594 | -0.0010787 | -0.0023755 | 0.00088014 | -55.0735 | 65.6021 | -57.2983 | 65.387 | -56.575 | -57.1793 | -56.1768 | -56.044 | 65.6204 | -57.2983 | -57.2388 | -57.2479 | -57.3486 | -57.074 | -0.027466 | -0.004577 | -0.21973 | 0.6958 | 1.0941 | 0.091553 | 1.1215 | 0.11902 | -0.027466 | 0.013733 | -122.8455 | 0.022888 | 0.19684 | -0.07782 | 0.2243 | -0.050354 | 0.72327 | 122.6852 | 0.050354 | 0.059509 | 122.9004 | 122.9187 | 122.8729 | 122.8912 | -122.905 | -122.905 | 122.6578 | 0.032043 | 2.1973 | 1.2268
1672.1719 | 122.9507 | -57.2571 | 65.6021 | -0.052948 | 0.00019446 | 0.06288 | 0.07289 | -0.001976 | 0.00026909 | 0.0054218 | 0.023071 | 0.00088875 | 0.00085443 | -0.00058098 | -0.0017197 | -0.0021619 | 0.0010937 | -55.0415 | 65.5838 | -57.312 | 65.3549 | -56.4194 | -56.9504 | -56.1584 | -56.0028 | 65.6113 | -57.28 | -57.2571 | -57.2525 | -57.3441 | -57.0786 | -0.054932 | -0.018311 | -0.24719 | 0.83771 | 1.0986 | 0.3067 | 1.1536 | 0.36163 | -0.022888 | 0.009155 | -122.8592 | 0.004578 | 0.17853 | -0.086975 | 0.20142 | -0.064087 | 0.89264 | 122.6669 | 0.027466 | 0.022888 | 122.8958 | 122.8912 | 122.8409 | 122.8683 | -122.9141 | -122.8821 | 122.612 | 0 | 2.2156 | 1.2543
1673.1719 | 123.0103 | -57.2479 | 65.6067 | -0.037689 | -0.00044654 | 0.062025 | 0.076522 | 0.0033646 | 0.0045417 | 0.0084124 | -0.028809 | 0.0017431 | 0.0019226 | 0.00070062 | -0.0025741 | -0.0025891 | 0.0025891 | -55.0507 | 65.6021 | -57.3349 | 65.387 | -56.4651 | -56.9916 | -56.1813 | -56.012 | 65.6342 | -57.28 | -57.2159 | -57.2296 | -57.3349 | -57.0328 | -0.086975 | -0.004577 | -0.21973 | 0.78278 | 1.0666 | 0.25635 | 1.1536 | 0.34332 | -0.032043 | 0.027466 | -122.8226 | 0.018311 | 0.21515 | -0.086975 | 0.24719 | -0.054932 | 0.86975 | 122.7219 | 0.050354 | 0.064087 | 122.937 | 122.9141 | 122.85 | 122.8821 | -122.9416 | -122.8867 | 122.6349 | 0.032044 | 2.1973 | 1.236
1674.1719 | 122.9828 | -57.2525 | 65.6158 | -0.045319 | -0.00023294 | 0.062666 | 0.075454 | 0.00080117 | 0.00091009 | 0.0049946 | -0.025757 | 0.0028113 | 0.00042723 | -0.00036738 | -0.0015061 | -0.0019483 | -0.0012561 | -55.0461 | 65.5838 | -57.3257 | 65.3595 | -56.456 | -56.987 | -56.1859 | -56.0211 | 65.6342 | -57.2983 | -57.2205 | -57.2205 | -57.3349 | -57.0328 | -0.073243 | -0.032044 | -0.25635 | 0.79651 | 1.0666 | 0.2655 | 1.1398 | 0.33874 | -0.045777 | 0.01831 | -122.8363 | 0.032043 | 0.21973 | -0.082398 | 0.2655 | -0.036621 | 0.86975 | 122.6852 | 0.07782 | 0.07782 | 122.9095 | 122.9324 | 122.8363 | 122.8867 | -122.9416 | -122.9141 | 122.612 | 0.032043 | 2.2064 | 1.2314
1675.1719 | 123.0331 | -57.2571 | 65.593 | -0.03006 | -0.00023294 | 0.064162 | 0.073958 | 0.00080117 | 0.0017645 | 0.0073444 | -0.041016 | -0.0010339 | 0.001068 | 0.0045458 | -0.00043791 | -0.0017347 | -0.0025379 | -55.0232 | 65.5563 | -57.3303 | 65.3915 | -56.4194 | -56.9962 | -56.1676 | -55.9891 | 65.6342 | -57.28 | -57.2113 | -57.2388 | -57.3532 | -57.0465 | -0.073242 | -0.036622 | -0.20142 | 0.83771 | 1.0895 | 0.26093 | 1.1627 | 0.33417 | -0.022888 | 0.041198 | -122.8043 | 0.01831 | 0.21057 | -0.09613 | 0.23346 | -0.073242 | 0.91095 | 122.7219 | 0.041198 | 0.068664 | 122.8867 | 122.9141 | 122.8134 | 122.8912 | -122.9233 | -122.8729 | 122.6486 | 0.045776 | 2.2339 | 1.268
1676.1719 | 122.9919 | -57.2479 | 65.5746 | -0.091095 | -0.0010873 | 0.064162 | 0.072463 | -0.00048063 | 0.0026191 | 0.0073444 | -0.03186 | -0.0012477 | -0.00085457 | 0.00027342 | -0.0010787 | -0.0025891 | -0.0018971 | -55.014 | 65.5884 | -57.312 | 65.3824 | -56.4148 | -56.987 | -56.1905 | -55.9799 | 65.6067 | -57.3029 | -57.2113 | -57.225 | -57.3441 | -57.0282 | -0.064087 | 0.013733 | -0.19226 | 0.83313 | 1.0574 | 0.26093 | 1.1215 | 0.32501 | -0.054931 | 0.032043 | -122.7859 | 0.022888 | 0.21973 | -0.09613 | 0.27466 | -0.041199 | 0.89722 | 122.6944 | 0.077819 | 0.091552 | 122.9004 | 122.9095 | 122.8363 | 122.8546 | -122.8867 | -122.8775 | 122.6303 | 0.036621 | 2.2339 | 1.268
1677.1719 | 123.024 | -57.2433 | 65.6113 | -0.052948 | 0.0019035 | 0.064162 | 0.073104 | -0.0026168 | 0.0051825 | 0.0069172 | 0.016968 | -0.00039305 | -0.00021357 | -0.00464 | -0.0030013 | -0.0030163 | -0.00082886 | -55.0369 | 65.6067 | -57.3441 | 65.3732 | -56.4423 | -56.9824 | -56.1905 | -56.0074 | 65.6433 | -57.2754 | -57.2205 | -57.2296 | -57.3441 | -57.0236 | -0.10071 | -0.004578 | -0.23804 | 0.80109 | 1.0529 | 0.26093 | 1.1536 | 0.36163 | -0.032044 | 0.032044 | -122.8317 | 0.013733 | 0.21973 | -0.10071 | 0.25177 | -0.068664 | 0.90179 | 122.7173 | 0.045777 | 0.054932 | 122.9507 | 122.9187 | 122.85 | 122.8867 | -122.9553 | -122.8867 | 122.6166 | 0.022888 | 2.2064 | 1.236
1678.1719 | 122.9828 | -57.2708 | 65.5975 | -0.037689 | 0.00083526 | 0.064162 | 0.072463 | -0.0030442 | 0.0039007 | 0.007558 | -0.0043946 | 0.0023839 | -0.00021357 | 0.00048702 | 0.00084389 | -0.0040845 | 2.554e-05 | -55.0735 | 65.6113 | -57.3029 | 65.3046 | -56.6299 | -57.0923 | -56.1813 | -56.044 | 65.6204 | -57.3074 | -57.2617 | -57.28 | -57.3578 | -57.0602 | -0.032043 | 0.013733 | -0.29297 | 0.64087 | 1.0895 | 0.17853 | 1.1215 | 0.21057 | -0.036621 | 0.022888 | -122.8592 | -0.009155 | 0.21057 | -0.086975 | 0.24719 | -0.050354 | 0.67291 | 122.6074 | 0.027466 | 0.045776 | 122.9141 | 122.9279 | 122.8821 | 122.8912 | -122.9004 | -122.905 | 122.5754 | 0.009155 | 2.1973 | 1.2268
1679.1719 | 123.0148 | -57.2388 | 65.5975 | 0.030975 | 0.0014761 | 0.06288 | 0.073318 | 0.0016556 | 0.0015509 | 0.0077716 | 0.013916 | 0.0028113 | 0.001709 | 0.002196 | -0.00043791 | -0.0010937 | 0.0013073 | -55.0507 | 65.5838 | -57.3441 | 65.3549 | -56.4743 | -57.0053 | -56.1859 | -56.0165 | 65.6387 | -57.2983 | -57.2342 | -57.2388 | -57.3486 | -57.0328 | -0.10528 | -0.013733 | -0.24262 | 0.76447 | 1.0529 | 0.23346 | 1.1581 | 0.33874 | -0.059509 | 0.041199 | -122.8317 | 0 | 0.20599 | -0.10986 | 0.2655 | -0.050354 | 0.86975 | 122.699 | 0.059509 | 0.064087 | 122.9279 | 122.937 | 122.8226 | 122.8775 | -122.9416 | -122.8958 | 122.5937 | 0.004578 | 2.1881 | 1.2222
1680.1719 | 122.9782 | -57.2525 | 65.5746 | -0.045319 | -1.9142e-05 | 0.06523 | 0.073531 | 0.0010148 | 0.0034735 | 0.0094806 | -0.016602 | 0.0032385 | 0.00064083 | 0.003905 | 0.0014847 | -0.0025891 | 0.0010937 | -55.1468 | 65.5151 | -57.3486 | 65.3641 | -56.4606 | -56.9916 | -56.1722 | -55.9891 | 65.6067 | -57.2845 | -57.2342 | -57.2571 | -57.3578 | -57.0374 | -0.096131 | -0.059509 | -0.21057 | 0.79193 | 1.0803 | 0.26093 | 1.1765 | 0.35706 | -0.032044 | 0.032043 | -122.8088 | -0.004578 | 0.21515 | -0.10529 | 0.24719 | -0.073242 | 0.88806 | 122.7127 | 0.027466 | 0.050354 | 122.8638 | 122.8912 | 122.7676 | 122.8592 | -122.9233 | -122.8592 | 122.6166 | 0.01831 | 2.1057 | 1.2634
1681.1719 | 122.9691 | -57.2571 | 65.5838 | -0.075836 | -1.9142e-05 | 0.069716 | 0.071822 | 0.0022964 | 0.0045417 | 0.0081988 | -0.022705 | 0.0025975 | 0.00042723 | -0.0042126 | 0.00020289 | -0.0034437 | -0.0016833 | -55.1331 | 65.538 | -57.3715 | 65.3824 | -56.4651 | -57.0145 | -56.2042 | -55.9937 | 65.6021 | -57.2845 | -57.2296 | -57.2617 | -57.3578 | -57.0465 | -0.11444 | -0.045776 | -0.20142 | 0.79193 | 1.0529 | 0.24262 | 1.1673 | 0.35706 | -0.027466 | 0.018311 | -122.8134 | -0.004578 | 0.21057 | -0.10071 | 0.23804 | -0.073242 | 0.90637 | 122.7539 | 0.022888 | 0.054932 | 122.9095 | 122.8867 | 122.7951 | 122.8592 | -122.9553 | -122.8683 | 122.6395 | 0.027466 | 2.124 | 1.2634
1682.1719 | 122.9553 | -57.2983 | 65.5746 | -0.10635 | -1.9142e-05 | 0.062025 | 0.07289 | -0.0011214 | 0.0028327 | 0.0062762 | -0.025757 | 0.0017431 | 0.001709 | 0.001128 | -0.0012925 | -0.0013073 | 0.0010937 | -55.0552 | 65.5518 | -57.3669 | 65.3229 | -56.488 | -57.0694 | -56.2408 | -56.044 | 65.5884 | -57.2662 | -57.2662 | -57.3029 | -57.4173 | -57.0923 | -0.068664 | -0.022888 | -0.25177 | 0.81024 | 1.0574 | 0.22888 | 1.1261 | 0.29755 | 0.032044 | 0.013733 | -122.8409 | -0.004577 | 0.20599 | -0.11902 | 0.17395 | -0.15106 | 0.87891 | 122.6898 | -0.036621 | 0 | 122.9187 | 122.8546 | 122.85 | 122.8867 | -122.9416 | -122.8409 | 122.6212 | 0.032044 | 2.243 | 1.2543
1683.1719 | 123.024 | -57.2479 | 65.5792 | -0.037689 | 0.00040806 | 0.06523 | 0.07225 | 0.00251 | 0.0026191 | 0.0088398 | 0.010864 | 0.0015295 | 2.8e-08 | -0.0016492 | 0.00041649 | -0.0032301 | 0.0051525 | -55.0232 | 65.5838 | -57.3486 | 65.3778 | -56.4377 | -56.9778 | -56.1813 | -55.9845 | 65.625 | -57.2891 | -57.225 | -57.2388 | -57.3441 | -57.0282 | -0.10071 | 0.004577 | -0.20142 | 0.81024 | 1.0666 | 0.27008 | 1.1673 | 0.37079 | -0.041199 | 0.045776 | -122.8043 | 0.009155 | 0.21973 | -0.09613 | 0.26093 | -0.054931 | 0.91095 | 122.7264 | 0.050354 | 0.064087 | 122.9324 | 122.9141 | 122.8317 | 122.8729 | -122.9279 | -122.8683 | 122.6257 | 0.022888 | 2.2247 | 1.2634
1684.1719 | 122.9553 | -57.2433 | 65.5792 | -0.10635 | -0.00066014 | 0.063307 | 0.073104 | 0.0044328 | 0.0028327 | 0.0062762 | 0.02002 | 0.0017431 | -0.00021357 | 0.0026232 | -0.0017197 | -0.00066648 | -0.0012561 | -55.0278 | 65.5838 | -57.3303 | 65.387 | -56.3873 | -56.987 | -56.1768 | -55.9799 | 65.593 | -57.2983 | -57.2342 | -57.2662 | -57.3441 | -57.0374 | -0.086975 | 0.004577 | -0.19226 | 0.85602 | 1.0666 | 0.25635 | 1.1536 | 0.34332 | -0.054932 | 0.013733 | -122.8134 | -0.022888 | 0.20599 | -0.10071 | 0.26093 | -0.045776 | 0.94299 | 122.7173 | 0.032044 | 0.064087 | 122.9141 | 122.8912 | 122.8271 | 122.8363 | -122.9095 | -122.8775 | 122.6303 | 0.009155 | 2.2156 | 1.2634
1685.1719 | 122.9965 | -57.2525 | 65.5884 | -0.060578 | 0.00083526 | 0.064375 | 0.072036 | 0.00486 | 0.0015509 | 0.0084124 | 0.013916 | 0.0013159 | 0.003418 | -0.00079478 | -0.0027877 | -0.0028027 | -0.00061526 | -55.0278 | 65.5655 | -57.3441 | 65.3 | -56.5704 | -57.0557 | -56.1264 | -55.9982 | 65.6067 | -57.2937 | -57.225 | -57.2708 | -57.3441 | -57.0511 | -0.091553 | -0.022888 | -0.28839 | 0.68207 | 1.1261 | 0.19684 | 1.2177 | 0.28839 | -0.041199 | 0.01831 | -122.8134 | -0.018311 | 0.20142 | -0.091553 | 0.24262 | -0.050354 | 0.77362 | 122.644 | 0.022888 | 0.068664 | 122.9095 | 122.9004 | 122.818 | 122.8592 | -122.9324 | -122.8821 | 122.5525 | 0.027465 | 2.2247 | 1.2543
1686.1719 | 122.9874 | -57.2296 | 65.5884 | -0.022431 | 0.0010489 | 0.060316 | 0.073318 | 0.0018692 | 0.00026909 | 0.005849 | 0.0047608 | 0.00067495 | 0.00064083 | -0.0031446 | 0.0010575 | -0.0021619 | 0.0036571 | -55.0369 | 65.5792 | -57.3303 | 65.3641 | -56.4377 | -56.9916 | -56.1813 | -56.0028 | 65.6204 | -57.2891 | -57.2159 | -57.2433 | -57.3486 | -57.0374 | -0.10071 | -0.009155 | -0.2243 | 0.79193 | 1.0483 | 0.23804 | 1.149 | 0.33875 | -0.05951 | 0.032043 | -122.8043 | -0.013733 | 0.19226 | -0.11902 | 0.25177 | -0.059509 | 0.89264 | 122.6944 | 0.045777 | 0.073243 | 122.9095 | 122.9095 | 122.8088 | 122.85 | -122.9187 | -122.8775 | 122.5937 | 0.013733 | 2.1927 | 1.2268
1687.1719 | 123.0011 | -57.2571 | 65.5792 | -0.098725 | -0.00066014 | 0.063094 | 0.071822 | 0.0020828 | 0.0024053 | 0.007558 | -0.028809 | 0.00024775 | 0.0019226 | -0.0050672 | -0.0034287 | -0.0032301 | 0.0025891 | -55.0278 | 65.5518 | -57.3212 | 65.3687 | -56.4514 | -56.987 | -56.1996 | -56.0349 | 65.5701 | -57.3257 | -57.2205 | -57.2571 | -57.3532 | -57.0374 | -0.064087 | -0.027466 | -0.21057 | 0.80566 | 1.0574 | 0.27008 | 1.1215 | 0.33417 | -0.068665 | -0.009156 | -122.7997 | 0 | 0.21973 | -0.09613 | 0.28839 | -0.027465 | 0.86975 | 122.6898 | 0.068665 | 0.10529 | 122.8729 | 122.8958 | 122.8088 | 122.8271 | -122.9004 | -122.905 | 122.6257 | 0.036621 | 2.2293 | 1.2222
1688.1719 | 122.9507 | -57.2662 | 65.5792 | -0.060578 | 0.0010489 | 0.064375 | 0.074172 | 0.00016017 | 0.0034735 | 0.0086262 | 0.0047608 | 0.00024775 | 0.0021362 | -0.0018628 | -0.0010787 | -0.0042981 | 2.554e-05 | -55.0415 | 65.5289 | -57.3624 | 65.3458 | -56.4743 | -57.0236 | -56.2225 | -56.0028 | 65.6204 | -57.28 | -57.2433 | -57.28 | -57.4081 | -57.0831 | -0.096131 | -0.050354 | -0.23346 | 0.79193 | 1.0437 | 0.24261 | 1.1398 | 0.33875 | -0.013733 | 0.041198 | -122.8226 | -0.013733 | 0.18311 | -0.14191 | 0.19684 | -0.12817 | 0.88806 | 122.7081 | 0 | 0.036621 | 122.8912 | 122.9004 | 122.7951 | 122.8867 | -122.9416 | -122.8592 | 122.612 | 0.022888 | 2.2247 | 1.2634
1689.1719 | 122.9416 | -57.28 | 65.5563 | -0.091095 | 0.00040806 | 0.061598 | 0.072677 | 0.0010148 | 0.0021917 | 0.0096942 | -0.0013428 | 0.0025975 | 0.001709 | 0.0013416 | -0.0025741 | -0.0015211 | 0.00023934 | -55.0095 | 65.593 | -57.3212 | 65.3687 | -56.4514 | -57.0007 | -56.1996 | -55.9799 | 65.6113 | -57.2937 | -57.2159 | -57.2571 | -57.2662 | -57.1472 | -0.041199 | 0.036622 | -0.18768 | 0.82855 | 1.0803 | 0.27924 | 1.1215 | 0.32044 | -0.013733 | 0.054932 | -122.7722 | 0.022888 | 0.13275 | 0.013733 | 0.14648 | 0.027466 | 0.86975 | 122.6898 | 0.036621 | 0.07782 | 122.9141 | 122.905 | 122.8729 | 122.8912 | -122.8775 | -122.85 | 122.6486 | 0.064087 | 2.2705 | 1.3
1690.1719 | 122.9965 | -57.2708 | 65.5701 | -0.11398 | -0.00044654 | 0.062239 | 0.074813 | 0.0012284 | 0.0041143 | 0.010335 | 0.0078126 | 0.00024775 | 0.0019226 | 0.0049732 | -0.0017197 | -0.0021619 | 0.0062207 | -55.1285 | 65.5609 | -57.4127 | 65.2771 | -56.5887 | -57.1335 | -56.2958 | -56.1127 | 65.5701 | -57.3303 | -57.3349 | -57.6004 | -57.2571 | -56.9183 | -0.14191 | -0.009155 | -0.29297 | 0.68207 | 0.97504 | 0.13733 | 1.1169 | 0.27924 | -0.059509 | 0 | -122.905 | -0.32959 | 0.35248 | 0.013733 | 0.41199 | 0.073242 | 0.82397 | 122.6898 | -0.27008 | -0.004578 | 122.9736 | 122.9004 | 122.8317 | 122.8409 | -122.9828 | -122.9004 | 122.5479 | -0.064087 | 2.1423 | 1.1581
1691.1719 | 123.0103 | -57.2708 | 65.5884 | -0.037689 | 0.0012625 | 0.064803 | 0.071181 | -0.0028304 | 0.00048269 | 0.0064898 | 0.016968 | 0.0015295 | 0.00064083 | 0.002196 | -0.0021469 | -0.0017347 | -0.0016833 | -55.0232 | 65.5884 | -57.3166 | 65.3595 | -56.4514 | -57.0053 | -56.1996 | -55.9753 | 65.593 | -57.28 | -57.2067 | -57.2159 | -57.3486 | -57.0282 | -0.045776 | 0 | -0.22888 | 0.8194 | 1.0712 | 0.2655 | 1.1169 | 0.31128 | -0.009155 | 0.004578 | -122.7951 | 0.054932 | 0.24261 | -0.07782 | 0.25177 | -0.068665 | 0.86517 | 122.6761 | 0.064087 | 0.073242 | 122.905 | 122.8729 | 122.8592 | 122.8638 | -122.905 | -122.8683 | 122.6303 | 0.064087 | 2.2476 | 1.2955
1692.1719 | 122.9828 | -57.2571 | 65.5884 | -0.10635 | -0.00044654 | 0.063734 | 0.07225 | -0.0032578 | 0.0030463 | 0.0064898 | 0.016968 | 0.0013159 | 0.0025634 | -0.00058098 | -0.0010787 | -0.0036573 | 0.00045294 | -55.0186 | 65.5838 | -57.3074 | 65.3732 | -56.4468 | -56.987 | -56.1996 | -55.9753 | 65.6113 | -57.28 | -57.2205 | -57.2479 | -57.3532 | -57.0328 | -0.050354 | -0.004578 | -0.21515 | 0.81024 | 1.0574 | 0.27008 | 1.1078 | 0.32043 | -0.022888 | 0.022888 | -122.8088 | 0.009155 | 0.2243 | -0.09613 | 0.24719 | -0.073242 | 0.8606 | 122.6807 | 0.032043 | 0.059509 | 122.8912 | 122.8912 | 122.8409 | 122.8683 | -122.8958 | -122.8683 | 122.6303 | 0.036621 | 2.2385 | 1.2817
1693.1719 | 123.0011 | -57.2617 | 65.5975 | -0.052948 | 0.00019446 | 0.064589 | 0.074599 | -0.0013352 | 0.0011237 | 0.009267 | 0.041382 | 0.0023839 | 0.0023498 | 0.001128 | -0.00043791 | -0.0030163 | 0.0032299 | -55.0323 | 65.5655 | -57.3395 | 65.3778 | -56.4651 | -57.0007 | -56.1996 | -55.9891 | 65.5792 | -57.2754 | -57.2296 | -57.2296 | -57.3486 | -57.0419 | -0.07782 | -0.032043 | -0.21973 | 0.79651 | 1.062 | 0.26093 | 1.1398 | 0.33875 | -0.013733 | -0.01831 | -122.8271 | 0.032044 | 0.21973 | -0.086975 | 0.23346 | -0.073242 | 0.87433 | 122.7173 | 0.045777 | 0.045777 | 122.905 | 122.8546 | 122.8271 | 122.8409 | -122.937 | -122.8729 | 122.6395 | 0.032044 | 2.2293 | 1.2726
1694.1719 | 122.9919 | -57.2571 | 65.5746 | -0.091095 | 0.0019035 | 0.063094 | 0.074172 | 0.0046464 | 0.0015509 | 0.0064898 | -0.010498 | -0.00082025 | 0.00085443 | 0.0013416 | -0.0019333 | -0.0028027 | -0.0014697 | -55.0323 | 65.5563 | -57.3303 | 65.3595 | -56.4423 | -57.0053 | -56.2042 | -56.0349 | 65.5838 | -57.2983 | -57.2342 | -57.2433 | -57.3441 | -57.0419 | -0.073242 | -0.018311 | -0.21515 | 0.81482 | 1.0529 | 0.25177 | 1.1261 | 0.32501 | -0.041199 | 0.009155 | -122.8088 | 0.013733 | 0.21515 | -0.086975 | 0.25635 | -0.045776 | 0.88806 | 122.6898 | 0.054932 | 0.064087 | 122.8867 | 122.8821 | 122.8134 | 122.8409 | -122.905 | -122.8729 | 122.6166 | 0.022888 | 2.2247 | 1.2222
1695.1719 | 123.024 | -57.2983 | 65.5518 | -0.052948 | -0.00044654 | 0.062666 | 0.0699 | 0.0010148 | 0.0032599 | 0.0071308 | -0.0013428 | 0.00067495 | 0.0012818 | 0.001128 | -0.00043791 | -0.0023755 | 0.00088014 | -55.1102 | 65.538 | -57.3624 | 65.3046 | -56.5384 | -57.1014 | -56.2592 | -56.0623 | 65.5609 | -57.3166 | -57.2571 | -57.2983 | -57.3898 | -57.0602 | -0.064087 | -0.013733 | -0.24719 | 0.75989 | 1.0391 | 0.19684 | 1.1032 | 0.26093 | -0.01831 | 0.009155 | -122.8088 | 0 | 0.23804 | -0.091553 | 0.25635 | -0.073243 | 0.82398 | 122.6669 | 0.01831 | 0.059509 | 122.9004 | 122.8775 | 122.8363 | 122.8592 | -122.9141 | -122.8683 | 122.6028 | 0.041199 | 2.1881 | 1.236
1696.1719 | 122.9874 | -57.2571 | 65.5746 | -0.060578 | 0.00019446 | 0.06288 | 0.072463 | 0.0010148 | 0.0015509 | 0.0062762 | 0.001709 | 3.4148e-05 | 0.00042723 | -0.0033582 | -0.0012925 | -0.0028027 | 0.0036571 | -55.0232 | 65.5655 | -57.3395 | 65.3549 | -56.4789 | -57.0419 | -56.2225 | -56.012 | 65.5884 | -57.2983 | -57.2571 | -57.28 | -57.3807 | -57.074 | -0.082398 | -0.009155 | -0.21973 | 0.7782 | 1.0345 | 0.21515 | 1.1169 | 0.29755 | -0.041199 | 0.013733 | -122.8317 | -0.022888 | 0.18311 | -0.1236 | 0.2243 | -0.082397 | 0.8606 | 122.6944 | 0.018311 | 0.041199 | 122.905 | 122.8867 | 122.8226 | 122.8455 | -122.9141 | -122.8729 | 122.612 | 0 | 2.2339 | 1.2451
1697.1719 | 122.9645 | -57.2662 | 65.5838 | -0.037689 | 0.0014761 | 0.063521 | 0.074386 | 0.0022964 | 0.0026191 | 0.0052082 | -0.0043946 | 0.0021703 | -0.0012818 | -0.0018628 | -0.0025741 | -0.0017347 | 0.0010937 | -55.0232 | 65.5838 | -57.3257 | 65.3687 | -56.4468 | -57.0282 | -56.2271 | -56.0165 | 65.6021 | -57.2662 | -57.2525 | -57.2708 | -57.3761 | -57.0374 | -0.05951 | 0 | -0.21515 | 0.8194 | 1.0391 | 0.23804 | 1.0986 | 0.29755 | 0 | 0.018311 | -122.8363 | -0.004578 | 0.22888 | -0.10986 | 0.22888 | -0.10986 | 0.87891 | 122.6944 | -0.004578 | 0.013733 | 122.9095 | 122.8683 | 122.85 | 122.8683 | -122.9095 | -122.85 | 122.6349 | 0.013733 | 2.243 | 1.2497
1698.1719 | 123.0789 | -57.2754 | 65.5197 | -0.13687 | 0.00083526 | 0.063948 | 0.073531 | -0.0021896 | 0.0028327 | 0.0067036 | 0.065796 | -0.00060665 | 0.0012818 | -0.001222 | 0.00020289 | -0.0036573 | 0.0023755 | -55.0461 | 65.4968 | -57.3166 | 65.3824 | -56.4056 | -57.0007 | -56.1584 | -55.9296 | 65.538 | -57.312 | -57.193 | -57.2067 | -57.2983 | -57.0007 | -0.041198 | -0.022888 | -0.13733 | 0.86975 | 1.1169 | 0.27466 | 1.1581 | 0.31586 | -0.036621 | 0.018311 | -122.7127 | 0.068665 | 0.27466 | -0.022888 | 0.31128 | 0.013733 | 0.91095 | 122.699 | 0.10529 | 0.11902 | 122.8134 | 122.85 | 122.7722 | 122.8134 | -122.8363 | -122.8317 | 122.6578 | 0.082398 | 2.2293 | 1.3458
1699.1719 | 122.9828 | -57.2617 | 65.5975 | -0.12924 | 0.0027579 | 0.063094 | 0.075027 | -0.0013352 | 0.0011237 | 0.010762 | 0.0047608 | -0.00017945 | -0.00064077 | 0.00027342 | -0.0032151 | -0.0030163 | 0.0017345 | -55.0278 | 65.5655 | -57.3303 | 65.3732 | -56.4423 | -57.0831 | -56.337 | -55.9708 | 65.6067 | -57.2845 | -57.2342 | -57.2525 | -57.3669 | -57.0419 | -0.068664 | -0.032043 | -0.2243 | 0.8194 | 0.92468 | 0.17853 | 0.99335 | 0.24719 | -0.022888 | 0.009155 | -122.8317 | 0.009156 | 0.21973 | -0.10529 | 0.24262 | -0.082397 | 0.88806 | 122.7036 | 0.032044 | 0.050354 | 122.8958 | 122.8912 | 122.8271 | 122.8683 | -122.9279 | -122.8821 | 122.6349 | 0.027466 | 2.2339 | 1.2909
1700.1719 | 123.0423 | -57.2571 | 65.5243 | -0.10635 | 0.0019035 | 0.062666 | 0.070968 | 0.003151 | 0.0024053 | 0.0084124 | 0.053589 | 0.00088875 | 0.00064083 | 0.0015552 | -0.0023605 | -0.0047253 | -0.0021107 | -55.0415 | 65.506 | -57.3395 | 65.3687 | -56.4377 | -57.0099 | -56.1768 | -55.9616 | 65.5197 | -57.2845 | -57.2067 | -57.2433 | -57.3349 | -57.0328 | -0.082398 | -0.018311 | -0.15564 | 0.8194 | 1.0803 | 0.24719 | 1.1627 | 0.32959 | -0.027466 | -0.004578 | -122.731 | 0.013733 | 0.2243 | -0.07782 | 0.25177 | -0.050354 | 0.90179 | 122.7081 | 0.041199 | 0.07782 | 122.8455 | 122.8043 | 122.7631 | 122.7768 | -122.8638 | -122.8088 | 122.6257 | 0.050354 | 2.2156 | 1.2955
1701.1719 | 122.9828 | -57.2571 | 65.5884 | -0.075836 | 0.00083526 | 0.064162 | 0.07289 | 0.0029374 | 0.0019781 | 0.0071308 | -0.022705 | 0.0011023 | 0.001068 | 0.0034778 | -0.0036423 | -0.0013073 | 0.00023934 | -55.0415 | 65.5563 | -57.3349 | 65.3595 | -56.4697 | -57.0282 | -56.2271 | -55.9937 | 65.5975 | -57.2983 | -57.2479 | -57.2845 | -57.3898 | -57.0602 | -0.07782 | -0.032044 | -0.22888 | 0.78735 | 1.03 | 0.22888 | 1.1078 | 0.3067 | -0.041199 | 0.009155 | -122.8363 | -0.027466 | 0.19684 | -0.13275 | 0.23804 | -0.091553 | 0.86517 | 122.6944 | 0.013733 | 0.050354 | 122.8912 | 122.8958 | 122.8134 | 122.8546 | -122.9233 | -122.8867 | 122.6166 | 0.009155 | 2.2156 | 1.2634
1702.1719 | 122.9965 | -57.2525 | 65.5746 | -0.075836 | -0.0015145 | 0.06288 | 0.074386 | -0.0026168 | 0.00026909 | 0.0086262 | -0.022705 | 0.0030249 | 0.00085443 | -0.00079478 | -0.0023605 | -0.0017347 | 0.0013073 | -55.0232 | 65.5792 | -57.3212 | 65.3732 | -56.456 | -57.0053 | -56.2134 | -56.0074 | 65.6204 | -57.2754 | -57.2159 | -57.2479 | -57.3624 | -57.0419 | -0.068665 | 0.004578 | -0.20142 | 0.79651 | 1.0391 | 0.24719 | 1.1078 | 0.31586 | -0.022889 | 0.045776 | -122.7905 | 0.004577 | 0.21057 | -0.10986 | 0.23346 | -0.086975 | 0.86517 | 122.6944 | 0.027466 | 0.05951 | 122.9004 | 122.8958 | 122.8317 | 122.8729 | -122.8958 | -122.85 | 122.6257 | 0.036621 | 2.2293 | 1.2451
1703.1719 | 123.0103 | -57.2708 | 65.5792 | -0.068207 | 0.0016899 | 0.063094 | 0.073745 | 0.00058737 | 0.0026191 | 0.0088398 | -0.0043946 | -0.00017945 | 0.00085443 | 0.0026232 | -0.00065151 | -0.0042981 | -0.00018806 | -55.0461 | 65.5701 | -57.3257 | 65.3595 | -56.456 | -57.0007 | -56.3553 | -55.9479 | 65.5975 | -57.28 | -57.2067 | -57.2662 | -57.3669 | -57.0374 | -0.054932 | -0.009156 | -0.21973 | 0.81482 | 0.91553 | 0.27008 | 0.97046 | 0.32501 | -0.009155 | 0.01831 | -122.7859 | 0.004578 | 0.23346 | -0.09613 | 0.24261 | -0.086975 | 0.86975 | 122.6852 | 0.013733 | 0.073242 | 122.8958 | 122.8775 | 122.8409 | 122.8683 | -122.905 | -122.8592 | 122.6303 | 0.064087 | 2.2247 | 1.3229
1704.1719 | 123.0011 | -57.2617 | 65.5884 | -0.060578 | -0.00066014 | 0.061812 | 0.074172 | -0.0030442 | 0.0024053 | 0.007558 | 0.010864 | -0.00039305 | -0.001709 | -0.001222 | -0.00022431 | -0.0034437 | 0.0019483 | -55.0461 | 65.5518 | -57.3441 | 65.3732 | -56.4514 | -57.0053 | -56.2088 | -55.9845 | 65.6067 | -57.2937 | -57.3257 | -57.1518 | -57.312 | -57.019 | -0.082397 | -0.036621 | -0.21515 | 0.81024 | 1.0529 | 0.25635 | 1.1353 | 0.33874 | -0.032043 | 0.01831 | -122.9141 | 0.10986 | 0.24261 | -0.050354 | 0.27466 | -0.018311 | 0.89264 | 122.7173 | 0.14191 | -0.032044 | 122.8958 | 122.9004 | 122.8134 | 122.8683 | -122.9324 | -122.8821 | 122.6349 | -0.064087 | 2.2156 | 1.2772
1705.1719 | 122.9416 | -57.2571 | 65.6113 | -0.014801 | 0.00062166 | 0.060957 | 0.07225 | -0.0026168 | 0.0060369 | 0.0086262 | 0.032227 | 0.0021703 | 0.00085443 | 0.00091422 | 0.0014847 | -0.0042981 | -0.00061526 | -55.0644 | 65.6204 | -57.3303 | 65.3 | -56.4743 | -57.0694 | -56.2637 | -56.0486 | 65.6158 | -57.28 | -57.2617 | -57.2662 | -57.3669 | -57.0786 | -0.073242 | 0.009155 | -0.31128 | 0.78278 | 0.99335 | 0.18768 | 1.0666 | 0.26093 | -0.022888 | 0.004578 | -122.8729 | -0.009155 | 0.17853 | -0.10986 | 0.20142 | -0.086975 | 0.85602 | 122.6303 | 0.013733 | 0.01831 | 122.9507 | 122.8958 | 122.8775 | 122.8729 | -122.9416 | -122.8912 | 122.5571 | -0.004578 | 2.1927 | 1.2085
1706.1719 | 122.9919 | -57.2388 | 65.6067 | -0.060578 | -0.0025827 | 0.064162 | 0.073745 | 0.0020828 | 0.0036871 | 0.005849 | -0.0013428 | 0.0011023 | 0.0021362 | -0.00058098 | -0.0023605 | -0.0036573 | -0.00082886 | -55.0415 | 65.5792 | -57.3349 | 65.3732 | -56.4651 | -56.9962 | -56.2225 | -55.9845 | 65.6204 | -57.2845 | -57.2205 | -57.2296 | -57.3395 | -57.0328 | -0.09613 | -0.027465 | -0.23346 | 0.77362 | 1.0162 | 0.24262 | 1.1124 | 0.33874 | -0.045776 | 0.013733 | -122.8271 | 0.009156 | 0.20599 | -0.10071 | 0.25177 | -0.054932 | 0.86975 | 122.7081 | 0.054932 | 0.064087 | 122.9141 | 122.905 | 122.818 | 122.8592 | -122.9416 | -122.8912 | 122.612 | 0.018311 | 2.1973 | 1.2543
1707.1719 | 122.9782 | -57.2342 | 65.6433 | 0.015716 | 0.00040806 | 0.061385 | 0.073104 | -0.001976 | 0.0034735 | 0.0069172 | 0.010864 | -0.00060665 | 0.0021362 | 0.00070062 | -0.0017197 | -0.0019483 | -0.00082886 | -55.069 | 65.593 | -57.3303 | 65.3412 | -56.4926 | -57.0236 | -56.218 | -56.0486 | 65.6296 | -57.2845 | -57.2617 | -57.2525 | -57.3624 | -57.0465 | -0.09613 | -0.050354 | -0.30212 | 0.74158 | 1.0162 | 0.21057 | 1.1124 | 0.3067 | -0.050354 | -0.013733 | -122.905 | -0.01831 | 0.18768 | -0.12817 | 0.23804 | -0.07782 | 0.83771 | 122.6715 | 0.032044 | 0.022888 | 122.9233 | 122.9141 | 122.8271 | 122.8638 | -122.9736 | -122.9279 | 122.5754 | -0.027466 | 2.1652 | 1.1856
1708.1719 | 122.9919 | -57.2617 | 65.6067 | -0.014801 | -0.0010873 | 0.06288 | 0.073531 | 0.00058737 | 0.0013373 | 0.0081988 | 0.016968 | 0.0023839 | 0.00042723 | -0.0084852 | -0.0010787 | -0.0040845 | -0.0018971 | -55.0415 | 65.593 | -57.3257 | 65.3641 | -56.4926 | -56.9962 | -56.2134 | -56.012 | 65.6113 | -57.2754 | -57.2205 | -57.2296 | -57.3486 | -57.0328 | -0.064087 | -0.013732 | -0.24261 | 0.76904 | 1.0483 | 0.2655 | 1.1124 | 0.32959 | -0.013733 | 0.004578 | -122.8271 | 0.032044 | 0.22888 | -0.086975 | 0.24262 | -0.073242 | 0.83313 | 122.6898 | 0.045777 | 0.054932 | 122.9187 | 122.8867 | 122.8546 | 122.8729 | -122.9324 | -122.8821 | 122.6257 | 0.041199 | 2.2202 | 1.2497
1709.1719 | 123.0057 | -57.2662 | 65.6067 | -0.03006 | -0.00023294 | 0.061812 | 0.071395 | 0.0016556 | 0.0015509 | 0.0069172 | 0.013916 | -0.00082025 | 0.00085443 | 0.00048702 | -0.0027877 | -0.0028027 | -0.0010425 | -55.0781 | 65.5975 | -57.3395 | 65.3366 | -56.5155 | -57.019 | -56.2317 | -56.0074 | 65.6433 | -57.28 | -57.2296 | -57.225 | -57.3532 | -57.0374 | -0.073243 | -0.009155 | -0.27008 | 0.75073 | 1.0345 | 0.24719 | 1.1078 | 0.32043 | -0.013733 | 0.036622 | -122.8363 | 0.041198 | 0.22888 | -0.086975 | 0.24261 | -0.073242 | 0.82397 | 122.6761 | 0.054931 | 0.050354 | 122.937 | 122.9233 | 122.8638 | 122.9095 | -122.9462 | -122.8867 | 122.6028 | 0.036621 | 2.1881 | 1.2589
1710.1875 | 123.0148 | -57.2525 | 65.6113 | -0.060578 | -0.0015145 | 0.062453 | 0.072036 | -0.0032578 | 0.0017645 | 0.0060626 | 0.010864 | 0.0019567 | -0.0010682 | -0.0031446 | -0.00065151 | -0.0042981 | -0.0012561 | -55.0735 | 65.5838 | -57.3349 | 65.3595 | -56.4972 | -56.9824 | -56.2225 | -56.0028 | 65.6204 | -57.2891 | -57.225 | -57.225 | -57.3486 | -57.0419 | -0.082398 | -0.027466 | -0.25177 | 0.75531 | 1.03 | 0.27008 | 1.1124 | 0.35248 | -0.036622 | 0.009155 | -122.8363 | 0.027465 | 0.21057 | -0.096131 | 0.24719 | -0.059509 | 0.83771 | 122.6944 | 0.064087 | 0.064087 | 122.9187 | 122.9095 | 122.8363 | 122.8729 | -122.9462 | -122.9004 | 122.612 | 0.027465 | 2.179 | 1.2497
1711.1719 | 122.9736 | -57.2479 | 65.5884 | -0.091095 | -0.00087374 | 0.063734 | 0.071822 | -0.00069423 | 0.0028327 | 0.010121 | 0.029175 | -0.0010339 | 0.00085443 | 0.0047594 | -0.0015061 | -0.0025891 | -0.0012561 | -55.0552 | 65.5609 | -57.3303 | 65.3732 | -56.4651 | -57.0007 | -56.218 | -55.9845 | 65.5792 | -57.2754 | -57.2342 | -57.2433 | -57.3349 | -57.0328 | -0.082397 | -0.027466 | -0.21515 | 0.78278 | 1.03 | 0.24719 | 1.1124 | 0.32959 | -0.027466 | -0.009155 | -122.8226 | 0.004578 | 0.21515 | -0.086975 | 0.24262 | -0.059509 | 0.86517 | 122.7036 | 0.032044 | 0.041199 | 122.8912 | 122.8546 | 122.8088 | 122.8271 | -122.9187 | -122.8638 | 122.6212 | 0.013733 | 2.1927 | 1.2634
1712.1719 | 123.0286 | -57.2388 | 65.5975 | -0.052948 | -0.00044654 | 0.064589 | 0.073318 | 0.0022964 | 0.0024053 | 0.010121 | -0.03186 | 0.00067495 | 0.0023498 | -0.00058098 | -0.0010787 | -0.0064343 | -0.0010425 | -55.0507 | 65.5701 | -57.3486 | 65.3732 | -56.456 | -57.0145 | -56.2271 | -55.9845 | 65.5975 | -57.3029 | -57.2159 | -57.2067 | -57.5546 | -57.1472 | -0.10986 | -0.027466 | -0.2243 | 0.78278 | 1.0117 | 0.22431 | 1.1215 | 0.33417 | -0.064086 | 0 | -122.8134 | 0.032044 | 0.091553 | -0.31586 | 0.15564 | -0.25177 | 0.89264 | 122.7219 | 0.09613 | 0.086975 | 122.9187 | 122.9004 | 122.8088 | 122.8363 | -122.9462 | -122.9004 | 122.612 | 0.022889 | 2.1881 | 1.2543
1713.1719 | 123.0103 | -57.2617 | 65.5884 | -0.052948 | -0.0015145 | 0.063307 | 0.073104 | 0.0010148 | 0.0030463 | 0.0086262 | 0.010864 | 0.0011023 | 0.00085443 | -0.00036738 | -0.0023605 | -0.0021619 | 0.0010937 | -55.0415 | 65.5518 | -57.3441 | 65.3595 | -56.4743 | -57.019 | -56.218 | -55.9982 | 65.5975 | -57.28 | -57.225 | -57.2433 | -57.3578 | -57.0419 | -0.082397 | -0.036621 | -0.22888 | 0.78735 | 1.0437 | 0.24261 | 1.1261 | 0.32501 | -0.01831 | 0.009155 | -122.8134 | 0.018311 | 0.21973 | -0.09613 | 0.23804 | -0.07782 | 0.86975 | 122.7036 | 0.036621 | 0.054931 | 122.8958 | 122.8775 | 122.8134 | 122.8592 | -122.9324 | -122.8683 | 122.6212 | 0.036621 | 2.2202 | 1.2634
1714.1719 | 123.024 | -57.2708 | 65.5746 | -0.11398 | 0.00083526 | 0.062453 | 0.07289 | 0.005928 | 0.0011237 | 0.0071308 | 0.001709 | 0.0017431 | 0.0019226 | 0.0034778 | 0.0021255 | -0.0034437 | 0.00088014 | -55.0507 | 65.5609 | -57.3349 | 65.4007 | -56.4102 | -57.0053 | -56.2225 | -56.0028 | 65.6158 | -57.312 | -57.2433 | -57.2662 | -57.3624 | -57.0511 | -0.064087 | -0.013733 | -0.17395 | 0.8606 | 1.0483 | 0.2655 | 1.1124 | 0.32959 | -0.041199 | 0.041199 | -122.818 | 0.004578 | 0.21973 | -0.091553 | 0.26093 | -0.050354 | 0.92468 | 122.7356 | 0.045777 | 0.068665 | 122.8958 | 122.9279 | 122.8317 | 122.8867 | -122.9095 | -122.8867 | 122.6715 | 0.027466 | 2.2202 | 1.268
1715.1875 | 122.9462 | -57.2708 | 65.5701 | -0.068207 | -0.0015145 | 0.064375 | 0.073531 | -0.0013352 | 0.0026191 | 0.010976 | 0.0047608 | 0.0019567 | 2.8e-08 | 0.00070062 | -0.0042831 | -0.0034437 | -0.00061526 | -55.0827 | 65.5243 | -57.3669 | 65.3137 | -56.5201 | -57.074 | -56.2637 | -56.0532 | 65.593 | -57.2983 | -57.2845 | -57.3074 | -57.431 | -57.074 | -0.09613 | -0.045776 | -0.25635 | 0.75073 | 1.0071 | 0.19684 | 1.1032 | 0.29297 | -0.027466 | 0.022889 | -122.8546 | -0.036621 | 0.19684 | -0.16022 | 0.2243 | -0.13275 | 0.84686 | 122.6807 | -0.009155 | 0.013733 | 122.8912 | 122.8912 | 122.7951 | 122.8638 | -122.937 | -122.8683 | 122.5845 | -0.013733 | 2.1881 | 1.2177
1716.1719 | 123.0194 | -57.2479 | 65.5884 | -0.052948 | -0.00023294 | 0.063521 | 0.072463 | -0.0030442 | 0.0043281 | 0.0094806 | 0.029175 | 0.0017431 | -0.00085457 | 0.0028368 | -0.00065151 | -0.0034437 | 0.0038709 | -55.0552 | 65.6067 | -57.3532 | 65.3549 | -56.5018 | -56.9962 | -56.2225 | -56.0074 | 65.6113 | -57.2617 | -57.225 | -57.2342 | -57.3441 | -57.019 | -0.10528 | 0.01831 | -0.23346 | 0.74616 | 1.0254 | 0.25177 | 1.1307 | 0.35705 | -0.013733 | 0.022888 | -122.8134 | 0.013733 | 0.22888 | -0.09613 | 0.24261 | -0.082397 | 0.85144 | 122.7081 | 0.027466 | 0.036621 | 122.9599 | 122.8729 | 122.8546 | 122.8592 | -122.9416 | -122.85 | 122.6028 | 0.022888 | 2.1927 | 1.2405
1717.1719 | 123.0194 | -57.2708 | 65.5655 | -0.022431 | 0.00040806 | 0.062666 | 0.071609 | 0.0010148 | 0.0019781 | 0.0067036 | 0.0047608 | 0.00088875 | 2.8e-08 | -0.00079478 | -0.0015061 | -0.00045288 | 0.0017345 | -55.0507 | 65.5792 | -57.3166 | 65.3595 | -56.456 | -57.0145 | -56.2225 | -55.9753 | 65.5884 | -57.3074 | -57.2342 | -57.2617 | -57.3441 | -57.0419 | -0.045776 | 0.013733 | -0.20599 | 0.81482 | 1.0483 | 0.25635 | 1.0941 | 0.30212 | -0.036621 | 0.022888 | -122.7997 | 0.009155 | 0.22888 | -0.073242 | 0.2655 | -0.036621 | 0.8606 | 122.6761 | 0.045776 | 0.073242 | 122.8958 | 122.8958 | 122.85 | 122.8592 | -122.8821 | -122.8729 | 122.6303 | 0.036621 | 2.2202 | 1.2955
1718.1719 | 122.9416 | -57.2617 | 65.6021 | 0.023346 | 0.00019446 | 0.061812 | 0.07225 | -0.0051804 | 0.0021917 | 0.005849 | -0.019653 | 0.0017431 | 0.00085443 | -0.0044262 | -0.0015061 | -0.0025891 | 0.00066654 | -55.101 | 65.6113 | -57.3349 | 65.2679 | -56.3644 | -56.8268 | -56.3187 | -56.0349 | 65.6158 | -57.3074 | -57.2708 | -57.2708 | -57.3624 | -57.0694 | -0.073242 | 0.009155 | -0.33417 | 0.89722 | 0.94299 | 0.43488 | 1.0162 | 0.50812 | -0.045776 | 0.013733 | -122.8729 | -0.009155 | 0.19226 | -0.10071 | 0.23804 | -0.054932 | 0.97046 | 122.6028 | 0.036621 | 0.036621 | 122.9462 | 122.9233 | 122.8729 | 122.8775 | -122.937 | -122.9095 | 122.5296 | -0.009155 | 2.1606 | 1.2268
1719.1719 | 123.024 | -57.2754 | 65.6021 | -0.03006 | 0.00019446 | 0.063307 | 0.073745 | 0.00037377 | 0.0021917 | 0.0054218 | 0.0078126 | -0.00017945 | 0.00042723 | -0.0025036 | -0.0012925 | -0.0040845 | 0.0013073 | -55.101 | 65.5975 | -57.3257 | 65.332 | -56.5338 | -57.0236 | -56.2408 | -56.0394 | 65.625 | -57.2708 | -57.2479 | -57.2479 | -57.3486 | -57.0374 | -0.050354 | -0.004578 | -0.27008 | 0.74158 | 1.0345 | 0.25177 | 1.0849 | 0.30212 | 0.004578 | 0.022888 | -122.85 | 0.027466 | 0.23804 | -0.073242 | 0.23346 | -0.07782 | 0.79193 | 122.6578 | 0.022888 | 0.022888 | 122.9233 | 122.8958 | 122.8729 | 122.9004 | -122.9279 | -122.8729 | 122.6074 | 0.027466 | 2.1744 | 1.236
1720.1875 | 122.9416 | -57.2662 | 65.6113 | -0.083466 | -0.00044654 | 0.062666 | 0.071395 | 0.00058737 | 0.0015509 | 0.0088398 | 0.10852 | 0.00067495 | 0.0029906 | 0.00091422 | -0.0025741 | -0.0047253 | 0.0025891 | -55.0873 | 65.593 | -57.3441 | 65.3229 | -56.5155 | -57.0328 | -56.2363 | -56.1264 | 65.625 | -57.3074 | -57.2845 | -57.2662 | -57.3761 | -57.0648 | -0.07782 | -0.01831 | -0.28839 | 0.75073 | 1.03 | 0.23346 | 1.1078 | 0.31128 | -0.041199 | 0.013733 | -122.8958 | 0 | 0.20142 | -0.10986 | 0.24262 | -0.068665 | 0.82855 | 122.6669 | 0.041199 | 0.022888 | 122.937 | 122.9324 | 122.8592 | 122.8912 | -122.9553 | -122.9187 | 122.5891 | -0.018311 | 2.179 | 1.1398
1721.1719 | 123.0103 | -57.2754 | 65.6021 | -0.03006 | -0.0042917 | 0.06288 | 0.072677 | 0.00058737 | 0.0030463 | 0.007558 | 0.010864 | 3.4148e-05 | -0.00042717 | 0.0013416 | -0.0010787 | -0.0021619 | 0.00023934 | -55.0507 | 65.5838 | -57.3395 | 65.3641 | -56.4835 | -57.0053 | -56.2225 | -55.9982 | 65.6067 | -57.28 | -57.2296 | -57.2433 | -57.3441 | -57.0419 | -0.064087 | -0.018311 | -0.23804 | 0.79193 | 1.0529 | 0.27008 | 1.1169 | 0.33417 | -0.004577 | 0.004577 | -122.8317 | 0.032044 | 0.23346 | -0.068664 | 0.23804 | -0.064087 | 0.85602 | 122.7036 | 0.036621 | 0.050354 | 122.9233 | 122.8867 | 122.8592 | 122.8821 | -122.9416 | -122.8821 | 122.6395 | 0.045777 | 2.2247 | 1.2772
1722.1719 | 122.9691 | -57.2617 | 65.5609 | -0.098725 | 0.0029715 | 0.060957 | 0.076095 | -0.0017624 | 0.0043281 | 0.0060626 | -0.010498 | 0.00067495 | -0.0012818 | 0.0017688 | -0.0032151 | -0.0032301 | 0.0015209 | -55.0827 | 65.5472 | -57.3441 | 65.3595 | -56.4835 | -57.0328 | -56.2546 | -55.9982 | 65.6021 | -57.2891 | -57.2388 | -57.2891 | -57.3669 | -57.0694 | -0.082397 | -0.013733 | -0.20142 | 0.7782 | 1.0071 | 0.22888 | 1.0895 | 0.31128 | -0.027466 | 0.041199 | -122.7997 | -0.027466 | 0.19226 | -0.10529 | 0.21973 | -0.077819 | 0.8606 | 122.7036 | 0 | 0.050354 | 122.8912 | 122.8912 | 122.8088 | 122.8638 | -122.905 | -122.85 | 122.6212 | 0.022888 | 2.179 | 1.2634
1723.1719 | 122.9965 | -57.2571 | 65.6021 | 0.00045798 | -0.00044654 | 0.063307 | 0.074386 | 0.0018692 | 0.0017645 | 0.0045672 | 0.026123 | 0.0017431 | 0.00064083 | 0.0036914 | -0.0015061 | -0.0040845 | -0.0029651 | -55.1102 | 65.593 | -57.3395 | 65.3275 | -56.5292 | -57.019 | -56.2363 | -56.0165 | 65.6113 | -57.2937 | -57.2433 | -57.2479 | -57.3441 | -57.0419 | -0.082398 | -0.009155 | -0.27466 | 0.72784 | 1.0208 | 0.23804 | 1.1032 | 0.32043 | -0.036621 | 0.009155 | -122.8455 | 0.009155 | 0.21515 | -0.086975 | 0.25177 | -0.050354 | 0.81024 | 122.6669 | 0.045776 | 0.050354 | 122.9324 | 122.905 | 122.85 | 122.8683 | -122.9416 | -122.8958 | 122.5845 | 0.013733 | 2.1469 | 1.2405
1724.1719 | 122.9919 | -57.2479 | 65.5655 | -0.060578 | 0.0012625 | 0.064803 | 0.07289 | 0.00080117 | 0.0015509 | 0.0062762 | -0.010498 | 0.00046135 | 0.0021362 | 0.00091422 | -0.00022431 | -0.0051527 | -0.00018806 | -55.0735 | 65.5746 | -57.3257 | 65.3687 | -56.4697 | -57.0007 | -56.2088 | -55.9662 | 65.6158 | -57.2708 | -57.2388 | -57.2433 | -57.3486 | -57.0282 | -0.07782 | 0.009155 | -0.19684 | 0.7782 | 1.0391 | 0.24719 | 1.1169 | 0.32501 | -0.022888 | 0.050354 | -122.8043 | 0.004578 | 0.21973 | -0.10071 | 0.24261 | -0.07782 | 0.85602 | 122.6944 | 0.027466 | 0.032043 | 122.9004 | 122.8867 | 122.8226 | 122.8638 | -122.8912 | -122.8363 | 122.6166 | 0.009155 | 2.1744 | 1.2817
1725.1875 | 123.024 | -57.2571 | 65.5151 | -0.1445 | -1.9142e-05 | 0.062453 | 0.071609 | -0.00048063 | 0.0019781 | 0.009267 | 0.081055 | -0.00039305 | 0.0029906 | -0.002931 | -0.0021469 | -0.0042981 | 0.0030163 | -55.1056 | 65.5151 | -57.3441 | 65.3549 | -56.4789 | -57.0328 | -56.2042 | -55.9937 | 65.5197 | -57.28 | -57.2296 | -57.2296 | -57.2983 | -57.019 | -0.086975 | 0 | -0.16022 | 0.7782 | 1.0529 | 0.2243 | 1.1398 | 0.31128 | -0.022888 | 0.004577 | -122.7448 | 0.027466 | 0.23804 | -0.041199 | 0.26092 | -0.018311 | 0.86517 | 122.699 | 0.050354 | 0.050354 | 122.8592 | 122.7997 | 122.7722 | 122.7768 | -122.8592 | -122.7951 | 122.612 | 0.027466 | 2.1515 | 1.2634
1726.1719 | 122.9462 | -57.2708 | 65.5609 | -0.10635 | 0.0025443 | 0.063734 | 0.075454 | 0.0010148 | 0.0041143 | 0.0084124 | -0.044067 | -0.00039305 | -0.00021357 | 0.00027342 | -0.00022431 | -0.0040845 | 0.00045294 | -55.0827 | 65.5151 | -57.3624 | 65.3595 | -56.5063 | -57.0374 | -56.2683 | -56.0074 | 65.6021 | -57.3166 | -57.2617 | -57.2891 | -57.4173 | -57.0602 | -0.091553 | -0.045776 | -0.20142 | 0.76446 | 1.0025 | 0.23346 | 1.0941 | 0.32501 | -0.045776 | 0.041199 | -122.8226 | -0.018311 | 0.21057 | -0.14648 | 0.25635 | -0.10071 | 0.85602 | 122.7219 | 0.027465 | 0.054931 | 122.8775 | 122.9187 | 122.7859 | 122.8729 | -122.9233 | -122.8775 | 122.6303 | 0.009155 | 2.1881 | 1.2634
1727.1719 | 122.9599 | -57.2617 | 65.6204 | -0.068207 | -1.9142e-05 | 0.062025 | 0.072463 | -0.0058212 | 0.0030463 | 0.0090534 | 0.053589 | 3.4148e-05 | -0.0014954 | 0.0019824 | 0.00041649 | -0.0040845 | -0.00018806 | -55.1193 | 65.5792 | -57.3532 | 65.332 | -56.5018 | -57.0282 | -56.2317 | -56.012 | 65.6158 | -57.28 | -57.2662 | -57.2617 | -57.3441 | -57.0786 | -0.091552 | -0.041198 | -0.28839 | 0.75989 | 1.03 | 0.23346 | 1.1215 | 0.32501 | -0.01831 | -0.004577 | -122.8867 | 0 | 0.18311 | -0.082397 | 0.20142 | -0.064087 | 0.85144 | 122.6852 | 0.01831 | 0.013733 | 122.9324 | 122.8958 | 122.8409 | 122.8775 | -122.9736 | -122.9004 | 122.5937 | -0.004577 | 2.1423 | 1.2497
1728.1719 | 122.9553 | -57.2571 | 65.6204 | -0.075836 | -0.0010873 | 0.062453 | 0.072036 | -0.0028304 | 0.0043281 | 0.0062762 | -0.0043946 | 0.0025975 | 0.0023498 | 0.0013416 | -0.00043791 | -0.0017347 | -0.0010425 | -55.1102 | 65.6067 | -57.3578 | 65.1993 | -56.5979 | -56.9962 | -56.2683 | -56.044 | 65.6067 | -57.2983 | -57.2525 | -57.2754 | -57.3669 | -57.0511 | -0.10071 | -0.013733 | -0.42114 | 0.65918 | 0.98877 | 0.26093 | 1.0895 | 0.36163 | -0.041199 | -0.013733 | -122.8729 | -0.018311 | 0.20599 | -0.10986 | 0.24719 | -0.068664 | 0.75989 | 122.5571 | 0.022888 | 0.045777 | 122.9645 | 122.905 | 122.8638 | 122.8638 | -122.9782 | -122.9187 | 122.4564 | 0.004578 | 2.1469 | 1.2131
1729.1719 | 123.0103 | -57.2525 | 65.5838 | -0.052948 | -0.00066014 | 0.062453 | 0.072677 | 0.0010148 | 0.0030463 | 0.0067036 | 0.001709 | 0.0021703 | 0.00042723 | 0.0049732 | -0.0034287 | -0.0045117 | -0.0031787 | -55.101 | 65.593 | -57.3303 | 65.3503 | -56.5201 | -57.0374 | -56.2683 | -56.0211 | 65.6433 | -57.28 | -57.2479 | -57.2296 | -57.3395 | -57.0465 | -0.07782 | 0.009156 | -0.23346 | 0.73242 | 0.98419 | 0.21515 | 1.062 | 0.29297 | -0.027466 | 0.05951 | -122.8317 | 0.022888 | 0.20599 | -0.086976 | 0.23346 | -0.05951 | 0.81024 | 122.6807 | 0.050354 | 0.032043 | 122.9233 | 122.9233 | 122.8455 | 122.8958 | -122.9141 | -122.8638 | 122.6028 | 0.004577 | 2.1515 | 1.2314
1730.1719 | 123.0148 | -57.2617 | 65.5655 | -0.045319 | 0.0012625 | 0.063094 | 0.071822 | -0.00026703 | 0.0049689 | 0.0069172 | 0.065796 | -0.0014613 | 0.0025634 | 0.00048702 | -0.0042831 | -0.0013073 | -0.0025379 | -55.1331 | 65.5472 | -57.312 | 65.3687 | -56.488 | -57.0282 | -56.2042 | -55.9982 | 65.5655 | -57.2983 | -57.1518 | -57.2021 | -57.4036 | -57.0465 | -0.050354 | -0.018311 | -0.19684 | 0.77362 | 1.0574 | 0.23346 | 1.1078 | 0.28381 | -0.036621 | 0 | -122.7173 | 0.05951 | 0.21515 | -0.14191 | 0.25177 | -0.10529 | 0.82398 | 122.6807 | 0.096131 | 0.14648 | 122.8592 | 122.8638 | 122.8088 | 122.8271 | -122.8775 | -122.8638 | 122.6303 | 0.10986 | 2.1286 | 1.2634
1731.1719 | 122.9279 | -57.2571 | 65.5792 | -0.075836 | -0.00066014 | 0.063307 | 0.07524 | -0.0015488 | 0.0017645 | 0.0079852 | -0.034912 | 0.0021703 | 0.001709 | 0.001128 | -0.0036423 | -0.0025891 | -0.00040166 | -55.101 | 65.5609 | -57.3532 | 65.3458 | -56.5018 | -57.0602 | -56.2592 | -56.0074 | 65.6021 | -57.3166 | -57.2571 | -57.2937 | -57.4036 | -57.0786 | -0.09613 | -0.018311 | -0.23346 | 0.75531 | 0.99793 | 0.19684 | 1.0941 | 0.29297 | -0.059509 | 0.022888 | -122.8363 | -0.036621 | 0.17853 | -0.14648 | 0.23804 | -0.086975 | 0.85144 | 122.699 | 0.022888 | 0.059509 | 122.9141 | 122.9187 | 122.818 | 122.8592 | -122.9324 | -122.8958 | 122.6028 | 0 | 2.1561 | 1.2497
1732.1719 | 123.0606 | -57.2708 | 65.5518 | 0.10727 | 0.00040806 | 0.062025 | 0.070327 | -0.0028304 | 0.0034735 | 0.007558 | 0.056641 | -0.0010339 | 0.0014954 | -0.0078442 | -0.0021469 | -0.0038709 | -0.00018806 | -55.1788 | 65.5334 | -57.3212 | 65.3595 | -56.4972 | -57.0282 | -56.1905 | -55.9891 | 65.5518 | -57.2754 | -57.2113 | -57.1838 | -57.3166 | -57.019 | -0.050354 | -0.018311 | -0.19226 | 0.77362 | 1.0803 | 0.24261 | 1.1307 | 0.29297 | -0.004578 | 0 | -122.7631 | 0.086975 | 0.25177 | -0.045776 | 0.25635 | -0.041198 | 0.82398 | 122.6807 | 0.091553 | 0.064087 | 122.8546 | 122.8271 | 122.8043 | 122.8226 | -122.8729 | -122.8271 | 122.6303 | 0.059509 | 2.092 | 1.2817
1733.1719 | 122.9919 | -57.2525 | 65.6021 | -0.083466 | -0.00044654 | 0.060103 | 0.073958 | -5.343e-05 | 0.0013373 | 0.0052082 | -0.010498 | 0.0015295 | 0.00042723 | -0.0031446 | -0.0019333 | -0.0036573 | 0.00088014 | -55.1102 | 65.5884 | -57.3349 | 65.3503 | -56.5018 | -57.0053 | -56.2454 | -56.0211 | 65.6113 | -57.2983 | -57.2342 | -57.2479 | -57.3624 | -57.0374 | -0.082398 | -0.013733 | -0.25177 | 0.75073 | 1.0071 | 0.24719 | 1.0895 | 0.32959 | -0.045777 | 0.009155 | -122.8363 | 0.004577 | 0.21515 | -0.10986 | 0.26093 | -0.064087 | 0.83313 | 122.6852 | 0.050354 | 0.064087 | 122.9233 | 122.9095 | 122.8409 | 122.8638 | -122.937 | -122.9004 | 122.6028 | 0.01831 | 2.1423 | 1.2314
1734.1719 | 122.9645 | -57.2525 | 65.5792 | -0.20554 | -0.00087374 | 0.062666 | 0.073958 | 0.0012284 | 0.0028327 | 0.007558 | -0.025757 | -0.0014613 | 2.8e-08 | -0.0035718 | 0.00041649 | -0.0030163 | -0.0025379 | -55.0415 | 65.5655 | -57.3395 | 65.3778 | -56.4835 | -57.0236 | -56.2454 | -55.9891 | 65.593 | -57.3166 | -57.2342 | -57.2708 | -57.3807 | -57.0602 | -0.086976 | -0.013733 | -0.20142 | 0.76904 | 1.0071 | 0.22888 | 1.0941 | 0.31586 | -0.064087 | 0.013733 | -122.8134 | -0.018311 | 0.19226 | -0.12817 | 0.25635 | -0.064087 | 0.85602 | 122.7173 | 0.045776 | 0.082397 | 122.905 | 122.9095 | 122.818 | 122.8455 | -122.9187 | -122.8958 | 122.6303 | 0.01831 | 2.211 | 1.2634
1735.1719 | 122.9965 | -57.2937 | 65.5518 | -0.11398 | 0.0014761 | 0.061812 | 0.073318 | 0.00080117 | 0.0051825 | 0.010335 | -0.034912 | 0.0015295 | 0.0021362 | 0.0013416 | -0.0017197 | -0.0021619 | 0.0047253 | -55.1285 | 65.5609 | -57.3669 | 65.2771 | -56.575 | -57.1243 | -56.3095 | -56.0623 | 65.6021 | -57.3486 | -57.28 | -57.3257 | -57.4219 | -57.0877 | -0.073242 | 0.009155 | -0.27466 | 0.71869 | 0.98419 | 0.16937 | 1.0574 | 0.24261 | -0.054932 | 0.050354 | -122.8317 | -0.032044 | 0.20599 | -0.12817 | 0.26093 | -0.073242 | 0.79193 | 122.644 | 0.022888 | 0.068665 | 122.9279 | 122.9507 | 122.8546 | 122.8958 | -122.9187 | -122.9004 | 122.5708 | 0.013733 | 2.1652 | 1.2314
1736.1719 | 122.9599 | -57.2662 | 65.5975 | -0.03006 | -0.00087374 | 0.060103 | 0.07225 | -0.0024032 | 0.0028327 | 0.0094806 | -0.0013428 | 0.0028113 | 0.00085443 | 0.0030506 | -0.00022431 | -0.0034437 | -0.0025379 | -55.1331 | 65.5975 | -57.3395 | 65.3458 | -56.5338 | -57.0465 | -56.2637 | -56.044 | 65.625 | -57.28 | -57.2388 | -57.2571 | -57.3578 | -57.0374 | -0.073243 | 0 | -0.25177 | 0.73242 | 1.0025 | 0.21973 | 1.0757 | 0.29297 | -0.013733 | 0.027466 | -122.8363 | 0.009155 | 0.22888 | -0.091553 | 0.24261 | -0.07782 | 0.80566 | 122.6852 | 0.022888 | 0.041198 | 122.937 | 122.905 | 122.8638 | 122.8912 | -122.937 | -122.8775 | 122.612 | 0.027465 | 2.1332 | 1.2222
1737.1719 | 122.9965 | -57.2617 | 65.5792 | -0.045319 | 0.00062166 | 0.062025 | 0.071822 | 0.0010148 | -0.00037171 | 0.0081988 | -0.0013428 | 0.0017431 | 2.8e-08 | -0.00036738 | -0.00086511 | -0.0034437 | -0.0010425 | -55.0873 | 65.5701 | -57.3441 | 65.3732 | -56.4743 | -57.0053 | -56.2271 | -55.9799 | 65.6067 | -57.2983 | -57.2296 | -57.2388 | -57.3669 | -57.0419 | -0.082397 | -0.009156 | -0.20599 | 0.78735 | 1.0345 | 0.25635 | 1.1169 | 0.33874 | -0.036621 | 0.027465 | -122.8088 | 0.022888 | 0.21973 | -0.10529 | 0.25635 | -0.068664 | 0.86975 | 122.7173 | 0.059509 | 0.068665 | 122.9141 | 122.905 | 122.8317 | 122.8683 | -122.9233 | -122.8775 | 122.6349 | 0.032044 | 2.1744 | 1.2817
1738.1719 | 122.9965 | -57.2617 | 65.5746 | -0.0071715 | -0.00023294 | 0.062025 | 0.073104 | 0.0040054 | 0.00026909 | 0.007558 | -0.044067 | 0.0011023 | 0.0012818 | 0.00048702 | 0.0016983 | -0.0036573 | 2.554e-05 | -55.0827 | 65.5655 | -57.3441 | 65.3503 | -56.4743 | -57.0236 | -56.2317 | -56.0989 | 65.5746 | -57.3212 | -57.2433 | -57.2296 | -57.3532 | -57.0419 | -0.082397 | -0.009155 | -0.2243 | 0.78735 | 1.03 | 0.23804 | 1.1124 | 0.32043 | -0.059509 | 0 | -122.818 | 0.032044 | 0.21973 | -0.091552 | 0.27924 | -0.032043 | 0.86975 | 122.6944 | 0.091553 | 0.07782 | 122.9095 | 122.8958 | 122.8271 | 122.8363 | -122.9187 | -122.8958 | 122.612 | 0.018311 | 2.179 | 1.1627
1739.1719 | 122.9691 | -57.2479 | 65.5884 | -0.083466 | 0.00040806 | 0.063307 | 0.074599 | 0.0010148 | 0.0026191 | 0.0047808 | -0.034912 | 0.0015295 | 0.001068 | -0.002931 | -0.0021469 | -0.0032301 | 0.0015209 | -55.1147 | 65.5701 | -57.3441 | 65.3366 | -56.488 | -57.0602 | -56.2683 | -56.012 | 65.5746 | -57.312 | -57.2708 | -57.2845 | -57.399 | -57.074 | -0.09613 | -0.018311 | -0.25177 | 0.75989 | 0.97961 | 0.18768 | 1.0757 | 0.28381 | -0.064087 | -0.013733 | -122.8592 | -0.036621 | 0.17395 | -0.15106 | 0.23804 | -0.086975 | 0.85602 | 122.6807 | 0.027466 | 0.041199 | 122.9141 | 122.8867 | 122.818 | 122.8226 | -122.9324 | -122.9004 | 122.5845 | -0.022888 | 2.1332 | 1.236
1740.1719 | 123.0194 | -57.2708 | 65.5151 | -0.075836 | -0.0015145 | 0.063307 | 0.070968 | -0.00026703 | 0.0019781 | 0.0077716 | 0.056641 | 0.00088875 | -0.0014954 | -0.0016492 | -0.00065151 | -0.0040845 | -0.00040166 | -55.1147 | 65.4648 | -57.3441 | 65.3595 | -56.4651 | -57.0328 | -56.2088 | -55.9525 | 65.5334 | -57.2983 | -57.2205 | -57.2205 | -57.3303 | -57.0236 | -0.073242 | -0.050354 | -0.15564 | 0.80566 | 1.062 | 0.23804 | 1.1353 | 0.31128 | -0.027466 | 0.01831 | -122.7356 | 0.050354 | 0.24719 | -0.059509 | 0.27466 | -0.032043 | 0.87891 | 122.7036 | 0.07782 | 0.07782 | 122.8088 | 122.8317 | 122.7356 | 122.8043 | -122.8592 | -122.8134 | 122.6303 | 0.050354 | 2.1561 | 1.3184
1741.1719 | 123.0057 | -57.2525 | 65.5884 | -0.098725 | -0.0015145 | 0.061171 | 0.072463 | 0.0018692 | 0.0036871 | 0.0064898 | -0.025757 | 0.0017431 | 0.00042723 | 0.0026232 | -0.0010787 | -0.0030163 | 0.0038709 | -55.0919 | 65.5701 | -57.3212 | 65.3641 | -56.488 | -57.0099 | -56.2454 | -55.9937 | 65.6067 | -57.2754 | -57.2159 | -57.2296 | -57.3624 | -57.0328 | -0.068665 | -0.018311 | -0.2243 | 0.76447 | 1.0071 | 0.24261 | 1.0757 | 0.31128 | -0.022889 | 0.01831 | -122.8043 | 0.022888 | 0.21973 | -0.10986 | 0.24262 | -0.086975 | 0.83313 | 122.6852 | 0.045777 | 0.05951 | 122.8912 | 122.8821 | 122.8226 | 122.8592 | -122.9095 | -122.8638 | 122.6166 | 0.036621 | 2.1606 | 1.2589
1742.1719 | 122.9782 | -57.2571 | 65.6296 | 0.030975 | -1.9142e-05 | 0.063307 | 0.073531 | -0.0021896 | 0.0021917 | 0.0039264 | 0.001709 | -0.00017945 | 0.001068 | -0.0059216 | -0.0015061 | -0.0010937 | 0.00023934 | -55.1651 | 65.5975 | -57.3395 | 65.332 | -56.5201 | -57.0648 | -56.2683 | -56.012 | 65.625 | -57.2891 | -57.2662 | -57.2708 | -57.3578 | -57.0465 | -0.082398 | -0.032044 | -0.29755 | 0.737 | 0.98877 | 0.19226 | 1.0712 | 0.27466 | -0.032044 | -0.004578 | -122.8958 | -0.013733 | 0.21057 | -0.10071 | 0.24262 | -0.068664 | 0.8194 | 122.6715 | 0.018311 | 0.022889 | 122.937 | 122.9141 | 122.8546 | 122.8821 | -122.9691 | -122.9187 | 122.5891 | -0.009155 | 2.092 | 1.2451
1743.1719 | 122.9828 | -57.2754 | 65.6296 | -0.091095 | 0.0010489 | 0.062453 | 0.072463 | 0.00016017 | 0.0028327 | 0.0039264 | 0.0078126 | 0.00067495 | 0.0014954 | -0.00015378 | -0.0019333 | -0.0036573 | -0.00040166 | -55.1285 | 65.625 | -57.3441 | 65.3366 | -56.5201 | -57.0282 | -56.25 | -56.0211 | 65.625 | -57.2983 | -57.2662 | -57.2662 | -57.3532 | -57.074 | -0.068664 | -0.004578 | -0.29297 | 0.75531 | 1.0254 | 0.24719 | 1.0941 | 0.31586 | -0.022888 | -0.004578 | -122.8958 | 0.009156 | 0.20142 | -0.077819 | 0.2243 | -0.054931 | 0.82397 | 122.6807 | 0.032044 | 0.032044 | 122.9691 | 122.9233 | 122.9004 | 122.9004 | -122.9736 | -122.9279 | 122.612 | 0.009156 | 2.1469 | 1.2543
1744.1719 | 123.0011 | -57.2754 | 65.6021 | -0.060578 | -0.00023294 | 0.066298 | 0.074172 | 0.0050736 | 0.0030463 | 0.0086262 | -0.01355 | 0.0017431 | -0.0010682 | 0.0032642 | -0.0025741 | -0.0038709 | 0.0019483 | -55.101 | 65.5975 | -57.3303 | 65.3595 | -56.4926 | -57.0145 | -56.25 | -55.9891 | 65.6021 | -57.2845 | -57.2205 | -57.2433 | -57.3578 | -57.0465 | -0.054931 | -0.004578 | -0.24262 | 0.78278 | 1.0254 | 0.26093 | 1.0803 | 0.31586 | -0.009155 | 0 | -122.8226 | 0.032044 | 0.22888 | -0.082397 | 0.23804 | -0.073242 | 0.83771 | 122.6898 | 0.041199 | 0.064087 | 122.9279 | 122.8867 | 122.8729 | 122.8775 | -122.9324 | -122.8867 | 122.6349 | 0.054932 | 2.1744 | 1.2863
1745.1719 | 122.9828 | -57.2571 | 65.5884 | -0.075836 | -1.9142e-05 | 0.063734 | 0.073318 | 0.0029374 | 0.0017645 | 0.0077716 | -0.019653 | -0.0023157 | 0.00042723 | 0.0051868 | -0.0010787 | -0.0019483 | -0.00061526 | -55.101 | 65.5563 | -57.3349 | 65.3458 | -56.5063 | -57.0557 | -56.2729 | -55.9982 | 65.6113 | -57.3074 | -57.2617 | -57.28 | -57.4081 | -57.0694 | -0.07782 | -0.032044 | -0.24262 | 0.75073 | 0.98419 | 0.20142 | 1.062 | 0.27924 | -0.050354 | 0.022888 | -122.85 | -0.022888 | 0.18768 | -0.15106 | 0.23804 | -0.10071 | 0.82855 | 122.6807 | 0.027466 | 0.045776 | 122.8912 | 122.9187 | 122.8134 | 122.8683 | -122.9233 | -122.8958 | 122.6028 | -0.004578 | 2.1561 | 1.2589
1746.1719 | 122.9736 | -57.2617 | 65.5746 | -0.052948 | 0.00019446 | 0.063734 | 0.072463 | 0.0033646 | 0.0034735 | 0.0071308 | -0.010498 | 0.0015295 | 0.0036316 | -0.00015378 | 0.0016983 | -0.0010937 | -0.0014697 | -55.1147 | 65.5609 | -57.3303 | 65.3687 | -56.4972 | -57.0374 | -56.2683 | -55.9891 | 65.593 | -57.2983 | -57.2525 | -57.2845 | -57.399 | -57.0648 | -0.068664 | -0.013733 | -0.20599 | 0.76447 | 0.99335 | 0.2243 | 1.062 | 0.29297 | -0.036621 | 0.018311 | -122.8271 | -0.022888 | 0.19684 | -0.13733 | 0.23346 | -0.10071 | 0.83313 | 122.699 | 0.013733 | 0.045777 | 122.8912 | 122.8912 | 122.8226 | 122.8546 | -122.905 | -122.8729 | 122.6303 | 0.009156 | 2.1469 | 1.2726
1747.1719 | 122.9645 | -57.28 | 65.5609 | -0.060578 | 0.0012625 | 0.064803 | 0.077376 | 0.0012284 | 0.0030463 | 0.0069172 | -0.010498 | -0.00060665 | 2.8e-08 | -0.0042126 | -0.00043791 | -0.0034437 | -0.0023243 | -55.1056 | 65.538 | -57.3257 | 65.3503 | -56.4835 | -57.0648 | -56.2546 | -56.0074 | 65.5838 | -57.2891 | -57.2388 | -57.2937 | -57.4036 | -57.0648 | -0.045777 | -0.022888 | -0.21057 | 0.79651 | 1.0254 | 0.21515 | 1.0712 | 0.26093 | -0.009156 | 0.022888 | -122.7997 | -0.013733 | 0.21515 | -0.1236 | 0.22431 | -0.11444 | 0.84229 | 122.6761 | -0.004577 | 0.050354 | 122.8638 | 122.8729 | 122.818 | 122.8638 | -122.8867 | -122.85 | 122.6303 | 0.041198 | 2.1744 | 1.2726
1748.1719 | 122.9599 | -57.2571 | 65.5746 | -0.1445 | -0.00044654 | 0.062666 | 0.072463 | -0.0021896 | 0.0015509 | 0.0069172 | 0.013916 | 0.00046135 | 0.001068 | 0.0019824 | -0.0019333 | -0.0053663 | -0.00018806 | -55.1102 | 65.593 | -57.3532 | 65.332 | -56.5201 | -57.0419 | -56.2683 | -56.0486 | 65.625 | -57.2937 | -57.2662 | -57.2525 | -57.3669 | -57.0602 | -0.09613 | 0.018311 | -0.24262 | 0.737 | 0.98877 | 0.21515 | 1.0849 | 0.31128 | -0.036621 | 0.050354 | -122.8409 | 0.004578 | 0.19684 | -0.10986 | 0.23346 | -0.073242 | 0.83313 | 122.6852 | 0.041199 | 0.027466 | 122.9462 | 122.9187 | 122.85 | 122.8821 | -122.9279 | -122.8683 | 122.5891 | -0.009155 | 2.1469 | 1.2085
1749.1719 | 123.0103 | -57.2479 | 65.5746 | -0.083466 | 0.00040806 | 0.061598 | 0.072036 | -0.0011214 | 0.0036871 | 0.0071308 | 0.0078126 | 0.0011023 | 2.8e-08 | -0.0054944 | 0.00084389 | 0.00040152 | 0.00066654 | -55.0919 | 65.5701 | -57.3166 | 65.3778 | -56.4743 | -57.0145 | -56.2592 | -55.957 | 65.593 | -57.2937 | -57.3395 | -57.2342 | -57.312 | -57.019 | -0.068664 | -0.004578 | -0.19684 | 0.77362 | 0.98877 | 0.23346 | 1.0574 | 0.30212 | -0.045776 | 0.018311 | -122.9141 | 0.013733 | 0.22888 | -0.064087 | 0.27466 | -0.018311 | 0.84229 | 122.6944 | 0.059509 | -0.045777 | 122.8867 | 122.8867 | 122.818 | 122.8409 | -122.8912 | -122.8683 | 122.6257 | -0.091553 | 2.1561 | 1.2909
1750.1719 | 123.0835 | -57.2479 | 65.5197 | -0.083466 | 0.0016899 | 0.063734 | 0.071822 | 0.0020828 | 0.0056097 | 0.0094806 | 0.013916 | 3.4148e-05 | 0.00042723 | -0.0027174 | -0.0017197 | -0.0060071 | 2.554e-05 | -55.1193 | 65.5151 | -57.3349 | 65.3641 | -56.4789 | -57.0465 | -56.2592 | -55.9387 | 65.5243 | -57.3029 | -57.1838 | -57.2021 | -57.3257 | -56.9962 | -0.086975 | -0.004577 | -0.15564 | 0.76904 | 0.98877 | 0.20142 | 1.0757 | 0.28839 | -0.054931 | 0.004578 | -122.7036 | 0.045777 | 0.25177 | -0.07782 | 0.3067 | -0.022889 | 0.85602 | 122.699 | 0.10071 | 0.11902 | 122.85 | 122.8271 | 122.7631 | 122.7722 | -122.8546 | -122.8226 | 122.612 | 0.064087 | 2.1286 | 1.3092
1751.1719 | 122.9187 | -57.3029 | 65.5746 | -0.068207 | -0.0010873 | 0.062239 | 0.072677 | -0.001976 | 0.0024053 | 0.0060626 | -0.041016 | 0.00067495 | 0.0014954 | 0.0030506 | -0.0025741 | -0.0045117 | 2.554e-05 | -55.1376 | 65.5563 | -57.3624 | 65.3137 | -56.5567 | -57.0969 | -56.3278 | -56.0898 | 65.593 | -57.3257 | -57.2983 | -57.3257 | -57.4493 | -57.1014 | -0.05951 | -0.018311 | -0.26093 | 0.74615 | 0.97504 | 0.20599 | 1.0345 | 0.2655 | -0.022889 | 0.018311 | -122.8729 | -0.022889 | 0.20142 | -0.14648 | 0.22431 | -0.1236 | 0.80566 | 122.6761 | 0 | 0.027466 | 122.9187 | 122.9187 | 122.8592 | 122.8958 | -122.937 | -122.9004 | 122.6166 | 0.004577 | 2.1652 | 1.2131
1752.1719 | 122.9965 | -57.2525 | 65.5655 | -0.098725 | -0.00023294 | 0.062239 | 0.072463 | 0.0010148 | 0.0032599 | 0.0067036 | -0.03186 | 3.4148e-05 | 0.0012818 | -0.0061352 | -0.0019333 | -0.0021619 | -0.0016833 | -55.0964 | 65.5426 | -57.3441 | 65.3687 | -56.4835 | -57.0328 | -56.2592 | -55.8884 | 65.5746 | -57.28 | -57.2113 | -57.2342 | -57.3761 | -57.0374 | -0.091553 | -0.022888 | -0.19684 | 0.76904 | 0.99335 | 0.21973 | 1.0849 | 0.31128 | -0.027466 | 0.009155 | -122.7768 | 0.01831 | 0.21515 | -0.1236 | 0.24261 | -0.096131 | 0.8606 | 122.7127 | 0.045776 | 0.068664 | 122.8867 | 122.8546 | 122.7951 | 122.8271 | -122.9095 | -122.8455 | 122.6212 | 0.041198 | 2.1561 | 1.3641
1753.1719 | 123.0057 | -57.2571 | 65.593 | -0.091095 | -0.00087374 | 0.061171 | 0.073745 | -0.0013352 | 0.0047553 | 0.0062762 | -0.03186 | -0.00017945 | 0.00085443 | 0.0013416 | -0.0032151 | -0.0030163 | 2.554e-05 | -55.0735 | 65.5746 | -57.3166 | 65.3595 | -56.488 | -57.0236 | -56.2637 | -56.1035 | 65.5884 | -57.3257 | -57.2021 | -57.28 | -57.3532 | -57.0145 | -0.059509 | -0.018311 | -0.23346 | 0.76904 | 0.99335 | 0.23346 | 1.0529 | 0.29297 | -0.068665 | -0.004578 | -122.7951 | -0.022888 | 0.24262 | -0.09613 | 0.31128 | -0.027465 | 0.82855 | 122.6761 | 0.045777 | 0.1236 | 122.8912 | 122.9141 | 122.8317 | 122.8455 | -122.9095 | -122.9187 | 122.6166 | 0.054932 | 2.1835 | 1.1536
1754.1719 | 122.9599 | -57.28 | 65.5518 | -0.068207 | 0.0014761 | 0.064162 | 0.073745 | 0.0057144 | 0.0043281 | 0.0060626 | -0.037964 | 0.0013159 | 0.0012818 | 5.9824e-05 | -0.0015061 | -0.0034437 | -0.0023243 | -55.1102 | 65.5197 | -57.3486 | 65.332 | -56.5384 | -57.0648 | -56.2912 | -55.9937 | 65.5975 | -57.2983 | -57.2754 | -57.2891 | -57.4219 | -57.0602 | -0.068665 | -0.032044 | -0.21973 | 0.74158 | 0.98877 | 0.21515 | 1.0574 | 0.28381 | -0.018311 | 0.045776 | -122.8271 | -0.009156 | 0.21973 | -0.14191 | 0.23804 | -0.1236 | 0.81024 | 122.6807 | 0.009155 | 0.022888 | 122.8683 | 122.8958 | 122.7997 | 122.8775 | -122.9004 | -122.85 | 122.612 | 0.004577 | 2.1698 | 1.2863
1755.1719 | 122.9141 | -57.2891 | 65.5609 | -0.052948 | 0.00019446 | 0.064803 | 0.073104 | 0.0018692 | 0.0058233 | 0.010121 | -0.022705 | 0.00024775 | -0.00085457 | 0.0030506 | -0.00086511 | -0.0032301 | -0.00061526 | -55.1239 | 65.5518 | -57.3578 | 65.2679 | -56.5887 | -57.1289 | -56.3507 | -56.0806 | 65.6067 | -57.312 | -57.3212 | -57.3532 | -57.4585 | -57.1106 | -0.068664 | -0.009155 | -0.29297 | 0.70038 | 0.93842 | 0.16022 | 1.0071 | 0.22888 | -0.022888 | 0.045776 | -122.8821 | -0.064086 | 0.17853 | -0.16937 | 0.20142 | -0.14648 | 0.76904 | 122.6257 | -0.041198 | -0.009155 | 122.9095 | 122.9187 | 122.8409 | 122.8958 | -122.9187 | -122.8729 | 122.5571 | -0.032043 | 2.1652 | 1.2085
1756.1719 | 122.9462 | -57.2708 | 65.5746 | -0.068207 | -0.00023294 | 0.063734 | 0.071395 | 0.00016017 | 0.0034735 | 0.007558 | 0.010864 | 0.0013159 | 2.8e-08 | -0.003999 | -0.0012925 | -0.0042981 | -0.0036059 | -55.101 | 65.5609 | -57.3578 | 65.3412 | -56.5292 | -57.0694 | -56.3095 | -56.0257 | 65.6113 | -57.3074 | -57.2617 | -57.3029 | -57.4173 | -57.0786 | -0.086975 | -0.013733 | -0.23346 | 0.74158 | 0.9613 | 0.20142 | 1.0483 | 0.28839 | -0.036621 | 0.036621 | -122.8363 | -0.032043 | 0.19226 | -0.14648 | 0.22888 | -0.10986 | 0.82855 | 122.699 | 0.004578 | 0.045776 | 122.9187 | 122.9187 | 122.8317 | 122.8821 | -122.9324 | -122.8821 | 122.612 | 0.009155 | 2.1698 | 1.2451
1757.1719 | 122.9782 | -57.2525 | 65.5792 | -0.098725 | -1.9142e-05 | 0.063307 | 0.072036 | 0.0055008 | 0.0041143 | 0.0064898 | 0.029175 | 0.0015295 | 0.003418 | -0.0020764 | -0.0021469 | -0.0036573 | -0.00018806 | -55.0919 | 65.5609 | -57.3395 | 65.3229 | -56.6254 | -57.1106 | -56.2317 | -55.9616 | 65.5838 | -57.2754 | -57.225 | -57.2708 | -57.3624 | -57.0374 | -0.086976 | -0.018311 | -0.25635 | 0.62714 | 1.0208 | 0.14191 | 1.1078 | 0.22888 | -0.022889 | 0.004577 | -122.8043 | -0.018311 | 0.21515 | -0.10986 | 0.23804 | -0.086975 | 0.71411 | 122.6624 | 0.004578 | 0.050354 | 122.9004 | 122.8592 | 122.8134 | 122.8363 | -122.9187 | -122.8546 | 122.5754 | 0.027465 | 2.1606 | 1.2909
1758.1719 | 122.9874 | -57.2708 | 65.5838 | -0.014801 | 0.0010489 | 0.064589 | 0.071181 | 0.00016017 | 0.0041143 | 0.0090534 | 0.013916 | 3.4148e-05 | 0.0021362 | -0.0014356 | -0.0017197 | -0.0025891 | 0.0013073 | -55.1102 | 65.5792 | -57.3669 | 65.3229 | -56.5292 | -57.0969 | -56.2912 | -56.0211 | 65.5975 | -57.312 | -57.2754 | -57.3029 | -57.4219 | -57.0831 | -0.09613 | -0.004577 | -0.26093 | 0.74158 | 0.97961 | 0.17395 | 1.0757 | 0.27008 | -0.041199 | 0.013733 | -122.8592 | -0.032043 | 0.18768 | -0.15106 | 0.22888 | -0.10986 | 0.83771 | 122.6898 | 0.009156 | 0.036621 | 122.9462 | 122.9095 | 122.85 | 122.8683 | -122.9507 | -122.8958 | 122.5937 | -0.004578 | 2.1606 | 1.2497
1759.1719 | 122.9141 | -57.2891 | 65.5609 | -0.075836 | 0.0019035 | 0.063307 | 0.073104 | 0.001442 | 0.0041143 | 0.005849 | -0.03186 | -0.00017945 | 0.0023498 | 0.0019824 | -0.0015061 | -0.0025891 | 0.0032299 | -55.1651 | 65.5289 | -57.3715 | 65.2771 | -56.6208 | -57.1289 | -56.3507 | -56.0989 | 65.5838 | -57.3349 | -57.312 | -57.3349 | -57.4631 | -57.106 | -0.082397 | -0.032043 | -0.28381 | 0.66833 | 0.93842 | 0.16022 | 1.0208 | 0.24262 | -0.045776 | 0.022888 | -122.8729 | -0.045776 | 0.18311 | -0.17395 | 0.22888 | -0.12817 | 0.75073 | 122.6486 | 0 | 0.022888 | 122.9004 | 122.9187 | 122.818 | 122.8729 | -122.9324 | -122.8958 | 122.5662 | -0.022888 | 2.124 | 1.1902
1760.1719 | 122.9324 | -57.312 | 65.5472 | -0.16739 | 0.00062166 | 0.061598 | 0.073958 | 0.0018692 | 0.0019781 | 0.0047808 | -0.0074462 | 0.0011023 | 0.00042723 | -0.0048536 | -0.0030013 | -0.0013073 | -0.00018806 | -54.9408 | 65.5563 | -57.3578 | 65.2954 | -56.575 | -57.1518 | -56.3416 | -56.0761 | 65.5518 | -57.3074 | -57.2845 | -57.3166 | -57.4402 | -57.0831 | -0.045776 | 0.009155 | -0.25177 | 0.737 | 0.97046 | 0.16022 | 1.0162 | 0.20599 | 0.004578 | 0.004578 | -122.8317 | -0.004577 | 0.22888 | -0.12817 | 0.2243 | -0.13275 | 0.78278 | 122.6532 | -0.009155 | 0.022888 | 122.9141 | 122.8592 | 122.8683 | 122.8638 | -122.905 | -122.8546 | 122.6074 | 0.027466 | 2.3712 | 1.236
1761.1719 | 122.9736 | -57.2525 | 65.5609 | -0.083466 | -0.00044654 | 0.063307 | 0.076736 | -0.0026168 | 0.0019781 | 0.0060626 | -0.019653 | 0.0019567 | 0.0021362 | 0.00070062 | -0.0015061 | -0.0045117 | -0.0018971 | -55.0827 | 65.5426 | -57.3486 | 65.3915 | -56.4697 | -57.0282 | -56.2592 | -55.9708 | 65.5838 | -57.2937 | -57.2479 | -57.2891 | -57.3715 | -57.0419 | -0.096131 | -0.01831 | -0.16937 | 0.78278 | 0.99335 | 0.2243 | 1.0895 | 0.32043 | -0.041199 | 0.022888 | -122.8088 | -0.036622 | 0.21057 | -0.11902 | 0.25177 | -0.07782 | 0.87891 | 122.7402 | 0.004577 | 0.045776 | 122.8912 | 122.8775 | 122.7951 | 122.8363 | -122.9095 | -122.8546 | 122.644 | 0.004577 | 2.1698 | 1.2817
1762.1719 | 122.9187 | -57.3029 | 65.5609 | -0.083466 | -0.0019417 | 0.064162 | 0.072036 | -0.00090783 | 0.0036871 | 0.0084124 | -0.041016 | 0.0021703 | 0.00064083 | 0.0024096 | -0.0010787 | -0.0036573 | 0.00045294 | -55.1651 | 65.5563 | -57.3669 | 65.2771 | -56.6345 | -57.1564 | -56.369 | -56.1127 | 65.5838 | -57.3257 | -57.2845 | -57.3441 | -57.4402 | -57.106 | -0.064087 | -0.004578 | -0.28381 | 0.66833 | 0.93384 | 0.14648 | 0.99792 | 0.21057 | -0.022889 | 0.022888 | -122.8455 | -0.041199 | 0.19684 | -0.13733 | 0.21973 | -0.11444 | 0.73242 | 122.644 | -0.01831 | 0.041199 | 122.9233 | 122.9095 | 122.8592 | 122.8867 | -122.9279 | -122.8867 | 122.58 | 0.01831 | 2.1378 | 1.1902
1763.1719 | 122.9828 | -57.2937 | 65.5289 | -0.36575 | 0.0025443 | 0.062239 | 0.073531 | -0.00026703 | 0.0026191 | 0.0086262 | -0.01355 | 0.0025975 | 0.00064083 | -0.00036738 | -0.0012925 | -0.0013073 | -0.0021107 | -54.95 | 65.5197 | -57.3441 | 65.2908 | -56.5842 | -57.1381 | -56.3553 | -56.0623 | 65.5838 | -57.312 | -57.2891 | -57.3029 | -57.4493 | -57.0786 | -0.050354 | -0.009156 | -0.23804 | 0.70953 | 0.93841 | 0.15564 | 0.98877 | 0.20599 | -0.018311 | 0.054931 | -122.818 | -0.009155 | 0.21515 | -0.15564 | 0.23346 | -0.13733 | 0.75989 | 122.6349 | 0.009156 | 0.022888 | 122.8638 | 122.8958 | 122.8134 | 122.8775 | -122.8729 | -122.8409 | 122.5845 | 0.004577 | 2.3438 | 1.2314
1764.1719 | 122.9233 | -57.2891 | 65.5746 | -0.098725 | -0.00066014 | 0.063734 | 0.073745 | -0.001976 | 0.0036871 | 0.0073444 | -0.022705 | 0.0036657 | 0.00085443 | 0.005614 | -0.0015061 | -0.0034437 | -0.00082886 | -55.1559 | 65.5563 | -57.3807 | 65.2863 | -56.6116 | -57.1381 | -56.3416 | -56.0989 | 65.5701 | -57.3212 | -57.3212 | -57.3715 | -57.4631 | -57.1335 | -0.091552 | -0.018311 | -0.28839 | 0.67749 | 0.94757 | 0.15106 | 1.0391 | 0.24261 | -0.032043 | -0.004578 | -122.8958 | -0.082397 | 0.15564 | -0.17395 | 0.18768 | -0.14191 | 0.76904 | 122.6669 | -0.050354 | 0 | 122.937 | 122.8912 | 122.8455 | 122.8592 | -122.9553 | -122.8958 | 122.5754 | -0.032043 | 2.1332 | 1.1902
1765.1719 | 123.0103 | -57.2617 | 65.5334 | -0.12924 | -0.0010873 | 0.062025 | 0.07225 | -0.00026703 | 0.0036871 | 0.0052082 | 0.053589 | -0.00017945 | 0.0025634 | -0.0052808 | -0.0023605 | -0.0034437 | 0.00023934 | -55.1285 | 65.5106 | -57.3441 | 65.3458 | -56.4789 | -57.0511 | -56.25 | -55.957 | 65.5197 | -57.312 | -57.225 | -57.2342 | -57.3212 | -57.0236 | -0.082397 | -0.022888 | -0.18768 | 0.78278 | 1.0117 | 0.21057 | 1.0941 | 0.29297 | -0.050354 | -0.013733 | -122.7585 | 0.027466 | 0.23804 | -0.059509 | 0.28839 | -0.009155 | 0.86517 | 122.6898 | 0.07782 | 0.086975 | 122.8546 | 122.8317 | 122.7722 | 122.7814 | -122.8775 | -122.8455 | 122.6074 | 0.036621 | 2.1332 | 1.3046
1766.1719 | 122.9141 | -57.2891 | 65.5563 | -0.083466 | 0.0010489 | 0.063948 | 0.075881 | -0.00090783 | 0.0019781 | 0.0071308 | -0.028809 | 0.00088875 | 2.8e-08 | 0.0077502 | -0.0023605 | -0.0023755 | 0.0019483 | -55.1697 | 65.5426 | -57.3807 | 65.3 | -56.6025 | -57.1198 | -56.3507 | -56.0852 | 65.5975 | -57.3074 | -57.3074 | -57.3486 | -57.4539 | -57.1106 | -0.091552 | -0.013732 | -0.25635 | 0.68665 | 0.93842 | 0.16937 | 1.03 | 0.26093 | -0.01831 | 0.041199 | -122.8638 | -0.059509 | 0.17853 | -0.16479 | 0.19684 | -0.14648 | 0.7782 | 122.6807 | -0.041199 | 0 | 122.9233 | 122.905 | 122.8317 | 122.8867 | -122.937 | -122.8638 | 122.5891 | -0.01831 | 2.1194 | 1.2039
1767.1719 | 122.9919 | -57.2891 | 65.5563 | -0.060578 | -1.9142e-05 | 0.06288 | 0.072677 | -0.0026168 | 0.0019781 | 0.0045672 | 0.001709 | 0.0019567 | 2.8e-08 | -0.00015378 | -0.0010787 | -0.0034437 | 0.0015209 | -55.1147 | 65.5609 | -57.3395 | 65.3366 | -56.5292 | -57.0557 | -56.2912 | -55.9799 | 65.593 | -57.2937 | -57.2617 | -57.2937 | -57.4081 | -57.0786 | -0.050354 | 0.004578 | -0.21973 | 0.75989 | 0.99793 | 0.23346 | 1.0483 | 0.28381 | -0.004577 | 0.036622 | -122.818 | -0.004577 | 0.21057 | -0.11902 | 0.21515 | -0.11444 | 0.81024 | 122.6761 | 0 | 0.032043 | 122.9004 | 122.8867 | 122.85 | 122.8821 | -122.8958 | -122.85 | 122.6257 | 0.027466 | 2.1744 | 1.3092
1768.1719 | 122.9919 | -57.2662 | 65.5655 | -0.045319 | 0.0014761 | 0.063734 | 0.076736 | 0.0020828 | 0.0019781 | 0.0079852 | 0.0078126 | 0.0015295 | 0.00064083 | 0.00048702 | -1.0706e-05 | -0.0032301 | 0.0010937 | -55.101 | 65.5655 | -57.3257 | 65.3595 | -56.4972 | -57.0236 | -56.282 | -55.9662 | 65.6067 | -57.28 | -57.2388 | -57.2479 | -57.3395 | -57.0374 | -0.05951 | 0 | -0.20599 | 0.76904 | 0.98419 | 0.24261 | 1.0437 | 0.30212 | -0.013733 | 0.041198 | -122.8043 | 0.01831 | 0.22888 | -0.073243 | 0.24261 | -0.05951 | 0.82855 | 122.6852 | 0.032043 | 0.041198 | 122.8912 | 122.8867 | 122.8317 | 122.8729 | -122.8912 | -122.8455 | 122.6257 | 0.027465 | 2.1652 | 1.3
1769.1719 | 122.9462 | -57.2937 | 65.5563 | -0.11398 | 0.0025443 | 0.062666 | 0.074172 | 0.00058737 | 0.0021917 | 0.0067036 | -0.037964 | 0.00067495 | -0.00021357 | -0.0014356 | -0.0019333 | -0.0040845 | 0.0036571 | -55.1468 | 65.5426 | -57.3532 | 65.3137 | -56.5521 | -57.0969 | -56.3141 | -56.0257 | 65.6067 | -57.2937 | -57.2662 | -57.3166 | -57.4219 | -57.0877 | -0.059509 | -0.013732 | -0.24261 | 0.74158 | 0.97961 | 0.19684 | 1.0391 | 0.25635 | 0 | 0.050354 | -122.8226 | -0.022888 | 0.20599 | -0.12817 | 0.20599 | -0.12817 | 0.80109 | 122.6669 | -0.022888 | 0.027466 | 122.8958 | 122.9004 | 122.8363 | 122.9004 | -122.9095 | -122.85 | 122.6074 | 0.027466 | 2.1469 | 1.268
1770.1719 | 123.0103 | -57.2433 | 65.5426 | -0.12924 | 0.00019446 | 0.062666 | 0.071609 | -0.001976 | 0.0047553 | 0.0054218 | 0.078003 | 0.00046135 | 0.0021362 | 0.00048702 | -0.00065151 | -0.0030163 | 0.00023934 | -55.1193 | 65.4877 | -57.3395 | 65.3687 | -56.4789 | -57.0374 | -56.2454 | -55.9616 | 65.5472 | -57.3166 | -57.225 | -57.2433 | -57.3257 | -57.0374 | -0.096131 | -0.054932 | -0.17395 | 0.76447 | 0.99793 | 0.20599 | 1.0941 | 0.30212 | -0.073242 | 0.004577 | -122.7676 | 0 | 0.20599 | -0.082398 | 0.27923 | -0.009156 | 0.8606 | 122.7081 | 0.073242 | 0.091552 | 122.8271 | 122.8638 | 122.731 | 122.7905 | -122.8821 | -122.8592 | 122.612 | 0.01831 | 2.124 | 1.2817
1771.1719 | 123.0057 | -57.2617 | 65.5701 | -0.091095 | 0.0012625 | 0.064803 | 0.074599 | -5.343e-05 | 0.0011237 | 0.0054218 | -0.010498 | 0.00024775 | 0.0025634 | -0.001222 | -0.0027877 | -0.0017347 | 0.0010937 | -55.1102 | 65.5472 | -57.3395 | 65.3687 | -56.5155 | -57.0374 | -56.2729 | -55.957 | 65.5975 | -57.2708 | -57.225 | -57.2571 | -57.3853 | -57.0602 | -0.07782 | -0.022888 | -0.20142 | 0.74615 | 0.98877 | 0.2243 | 1.0666 | 0.30212 | -0.009155 | 0.027466 | -122.7951 | 0.004578 | 0.20142 | -0.1236 | 0.21057 | -0.11444 | 0.82397 | 122.7081 | 0.013733 | 0.045776 | 122.8867 | 122.8683 | 122.8088 | 122.8592 | -122.9095 | -122.8409 | 122.6303 | 0.036621 | 2.1515 | 1.3046
1772.1719 | 122.9599 | -57.2891 | 65.5701 | -0.091095 | 0.0010489 | 0.063521 | 0.07524 | 0.0022964 | 0.0030463 | 0.0047808 | -0.0043946 | 0.0028113 | 0.00085443 | 0.00070062 | -0.0032151 | -0.0028027 | -0.00061526 | -55.1514 | 65.5472 | -57.3715 | 65.3 | -56.5704 | -57.0969 | -56.3232 | -56.0623 | 65.593 | -57.3074 | -57.2937 | -57.3303 | -57.4493 | -57.1152 | -0.082397 | -0.022888 | -0.27008 | 0.71869 | 0.96588 | 0.19226 | 1.0483 | 0.27466 | -0.01831 | 0.022889 | -122.8638 | -0.041198 | 0.17395 | -0.16022 | 0.19226 | -0.14191 | 0.80109 | 122.6715 | -0.022888 | 0.013733 | 122.9187 | 122.9004 | 122.8363 | 122.8821 | -122.9416 | -122.8775 | 122.5891 | -0.004577 | 2.1378 | 1.2268
1773.1719 | 122.9416 | -57.28 | 65.5472 | -0.060578 | 0.0010489 | 0.063734 | 0.072463 | -0.0017624 | 0.0034735 | 0.0045672 | -0.016602 | 0.0011023 | -0.00042717 | 0.0032642 | -0.0017197 | -0.0025891 | 0.00023934 | -55.1514 | 65.5426 | -57.3715 | 65.3229 | -56.5521 | -57.1014 | -56.3095 | -56.012 | 65.5792 | -57.2983 | -57.28 | -57.312 | -57.4219 | -57.0923 | -0.091553 | -0.004577 | -0.2243 | 0.72784 | 0.97046 | 0.17853 | 1.062 | 0.27008 | -0.018311 | 0.032044 | -122.8271 | -0.032044 | 0.18768 | -0.14191 | 0.20599 | -0.1236 | 0.8194 | 122.6944 | -0.013733 | 0.018311 | 122.9141 | 122.8775 | 122.8226 | 122.8592 | -122.9187 | -122.8455 | 122.6028 | 0 | 2.1286 | 1.268
1774.1719 | 122.9324 | -57.2937 | 65.5746 | -0.091095 | 0.0010489 | 0.06288 | 0.072463 | 0.0029374 | 0.0028327 | 0.0054218 | -0.016602 | -0.0016749 | 0.00064083 | -0.001222 | -0.0015061 | -0.0023755 | -0.00061526 | -55.1559 | 65.5563 | -57.3761 | 65.3 | -56.5979 | -57.1152 | -56.3416 | -56.0944 | 65.593 | -57.2983 | -57.312 | -57.3395 | -57.4677 | -57.1152 | -0.082398 | -0.018311 | -0.27466 | 0.6958 | 0.95215 | 0.17853 | 1.0345 | 0.26093 | -0.004578 | 0.018311 | -122.8867 | -0.045777 | 0.17853 | -0.17395 | 0.18311 | -0.16937 | 0.7782 | 122.6761 | -0.041199 | -0.013733 | 122.9324 | 122.8912 | 122.85 | 122.8867 | -122.9507 | -122.8729 | 122.5937 | -0.018311 | 2.1378 | 1.1993
1775.1719 | 122.9874 | -57.2525 | 65.5563 | -0.060578 | -0.00066014 | 0.062666 | 0.071822 | 0.00016017 | 0.0045417 | 0.0064898 | -0.0074462 | -0.00017945 | -0.0010682 | 0.00091422 | -0.0012925 | -0.0047253 | -0.0012561 | -55.1056 | 65.5609 | -57.3303 | 65.3687 | -56.5155 | -57.0511 | -56.282 | -55.9616 | 65.6067 | -57.3074 | -57.2296 | -57.2479 | -57.3532 | -57.0465 | -0.07782 | 0.004578 | -0.18768 | 0.737 | 0.97046 | 0.20142 | 1.0483 | 0.27924 | -0.054932 | 0.050354 | -122.7859 | 0.004577 | 0.20599 | -0.10071 | 0.26093 | -0.045776 | 0.81482 | 122.699 | 0.059509 | 0.07782 | 122.8912 | 122.9141 | 122.8134 | 122.8592 | -122.8867 | -122.8638 | 122.6212 | 0.022888 | 2.1469 | 1.2909
1776.1719 | 122.9919 | -57.2525 | 65.5746 | -0.083466 | -1.9142e-05 | 0.063948 | 0.07289 | 0.0016556 | 0.0013373 | 0.0054218 | 0.02002 | -0.00039305 | 0.0012818 | 0.00070062 | -0.0012925 | -0.0015211 | 0.0017345 | -55.1193 | 65.5701 | -57.3441 | 65.3458 | -56.5018 | -57.0328 | -56.2683 | -55.9433 | 65.6021 | -57.2937 | -57.2342 | -57.2388 | -57.3486 | -57.0328 | -0.091553 | -0.004578 | -0.22888 | 0.75073 | 0.98419 | 0.21973 | 1.0757 | 0.31128 | -0.041199 | 0.027466 | -122.8088 | 0.013732 | 0.21973 | -0.096131 | 0.26093 | -0.054932 | 0.84228 | 122.6898 | 0.054931 | 0.059509 | 122.9141 | 122.8958 | 122.8226 | 122.8546 | -122.9187 | -122.8683 | 122.5983 | 0.01831 | 2.1332 | 1.3092
1777.1719 | 122.9965 | -57.2525 | 65.5655 | -0.1445 | -0.00044654 | 0.061385 | 0.070754 | 0.0046464 | 0.0049689 | 0.0043536 | 0.001709 | 0.00067495 | 0.001709 | 0.0019824 | -0.0010787 | -0.0060071 | -0.00040166 | -55.1193 | 65.5426 | -57.3349 | 65.3458 | -56.5109 | -57.0374 | -56.2683 | -55.9387 | 65.6158 | -57.2983 | -57.312 | -57.2708 | -57.2708 | -57.019 | -0.082398 | -0.022888 | -0.21973 | 0.74158 | 0.98419 | 0.21515 | 1.0666 | 0.29755 | -0.045777 | 0.050354 | -122.8775 | -0.018311 | 0.23346 | -0.018311 | 0.27924 | 0.027466 | 0.82397 | 122.6807 | 0.027466 | -0.013733 | 122.8775 | 122.9141 | 122.7951 | 122.8683 | -122.9004 | -122.8638 | 122.5983 | -0.05951 | 2.1332 | 1.3138
1778.1719 | 122.9507 | -57.2754 | 65.5838 | -0.091095 | 0.0014761 | 0.063948 | 0.073958 | 0.001442 | 0.0045417 | 0.0069172 | -0.0013428 | 0.0028113 | 0.00021363 | 0.0054004 | -0.0015061 | -0.0030163 | -0.00082886 | -55.1559 | 65.5609 | -57.3532 | 65.3137 | -56.5704 | -57.0969 | -56.3324 | -56.0028 | 65.6204 | -57.3074 | -57.2983 | -57.3029 | -57.431 | -57.0923 | -0.077819 | -0.022888 | -0.27008 | 0.70496 | 0.94299 | 0.17853 | 1.0208 | 0.25635 | -0.032043 | 0.036621 | -122.8821 | -0.027465 | 0.18311 | -0.15564 | 0.21515 | -0.1236 | 0.78277 | 122.6669 | 0.004578 | 0.009155 | 122.9141 | 122.9279 | 122.8363 | 122.8958 | -122.937 | -122.8912 | 122.5891 | -0.022888 | 2.1194 | 1.2726
1779.1719 | 122.9233 | -57.2983 | 65.5518 | -0.03006 | 0.0012625 | 0.064162 | 0.070754 | 0.0012284 | 0.0034735 | 0.0081988 | -0.010498 | 0.0021703 | 0.0019226 | 0.00027342 | -0.0012925 | -0.0032301 | 0.00088014 | -55.1559 | 65.5334 | -57.3624 | 65.2771 | -56.6208 | -57.1381 | -56.3644 | -56.0806 | 65.5975 | -57.3349 | -57.312 | -57.3578 | -57.4677 | -57.1152 | -0.064087 | -0.018311 | -0.27466 | 0.67749 | 0.93384 | 0.16022 | 0.99793 | 0.2243 | -0.036621 | 0.045776 | -122.8638 | -0.059509 | 0.18311 | -0.16937 | 0.21973 | -0.13275 | 0.74158 | 122.6395 | -0.022888 | 0.022888 | 122.8958 | 122.9324 | 122.8317 | 122.8958 | -122.9141 | -122.8867 | 122.5754 | -0.013733 | 2.1423 | 1.2177
1780.1719 | 122.9965 | -57.2754 | 65.5426 | -0.060578 | -1.9142e-05 | 0.063307 | 0.074172 | 0.0035782 | 0.0011237 | 0.010762 | 0.0078126 | 0.0015295 | -0.00021357 | 0.00027342 | -0.0012925 | -0.0030163 | 0.0013073 | -55.1651 | 65.538 | -57.3715 | 65.3 | -56.5887 | -57.1381 | -56.3461 | -56.0532 | 65.5701 | -57.3303 | -57.28 | -57.312 | -57.4265 | -57.0831 | -0.09613 | -0.004578 | -0.24262 | 0.68665 | 0.92926 | 0.13733 | 1.0254 | 0.23346 | -0.054931 | 0.027465 | -122.8226 | -0.036621 | 0.19226 | -0.15106 | 0.24719 | -0.096131 | 0.78278 | 122.6715 | 0.01831 | 0.050354 | 122.9095 | 122.9004 | 122.8134 | 122.8455 | -122.9141 | -122.8729 | 122.5754 | -0.004577 | 2.1103 | 1.2222
1781.1719 | 122.9919 | -57.2342 | 65.5884 | -0.060578 | 0.0010489 | 0.062239 | 0.073318 | 0.0016556 | 0.0032599 | 0.0067036 | 0.001709 | 0.0017431 | 0.001709 | 0.0045458 | -0.0034287 | -0.0047253 | 0.0045117 | -55.1102 | 65.5701 | -57.3578 | 65.3595 | -56.5155 | -57.0099 | -56.2637 | -55.957 | 65.593 | -57.2662 | -57.2433 | -57.2342 | -57.3486 | -57.0145 | -0.1236 | -0.018311 | -0.22888 | 0.71869 | 0.97046 | 0.2243 | 1.0941 | 0.3479 | -0.032043 | 0.004578 | -122.8317 | 0 | 0.21973 | -0.11444 | 0.25177 | -0.082398 | 0.84228 | 122.7173 | 0.032043 | 0.022888 | 122.9279 | 122.8592 | 122.8043 | 122.8271 | -122.9462 | -122.8546 | 122.5937 | -0.009155 | 2.124 | 1.2772
1782.1719 | 122.9782 | -57.2525 | 65.5838 | -0.091095 | -0.0019417 | 0.063734 | 0.072036 | -0.0030442 | 0.0026191 | 0.0056354 | 0.001709 | 0.00067495 | 0.0025634 | -0.0042126 | -0.0032151 | -0.0038709 | 0.00066654 | -55.1239 | 65.6021 | -57.3441 | 65.3641 | -56.5155 | -57.0419 | -56.2729 | -55.9753 | 65.6067 | -57.3029 | -57.2296 | -57.2296 | -57.3486 | -57.0374 | -0.091553 | 0.018311 | -0.21973 | 0.737 | 0.97961 | 0.21057 | 1.0712 | 0.30212 | -0.050354 | 0.022888 | -122.8134 | 0.022888 | 0.21515 | -0.096131 | 0.2655 | -0.045777 | 0.82855 | 122.7081 | 0.073242 | 0.073242 | 122.9462 | 122.9095 | 122.8546 | 122.8592 | -122.9279 | -122.8867 | 122.6166 | 0.022888 | 2.1286 | 1.2772
1783.1719 | 122.9462 | -57.28 | 65.5884 | -0.083466 | 0.0010489 | 0.061385 | 0.071609 | -0.0026168 | 0.0017645 | 0.0062762 | 0.065796 | 0.00088875 | 0.0021362 | -0.0010084 | -1.0706e-05 | -0.0042981 | -0.00082886 | -55.1102 | 65.5563 | -57.3074 | 65.3458 | -56.5063 | -57.0145 | -56.2683 | -55.9937 | 65.6204 | -57.2891 | -57.2754 | -57.2617 | -57.3532 | -57.074 | -0.027466 | -0.032044 | -0.24262 | 0.77362 | 1.0117 | 0.2655 | 1.0391 | 0.29297 | -0.009156 | 0.032043 | -122.8638 | 0.01831 | 0.20599 | -0.073242 | 0.21515 | -0.064086 | 0.80109 | 122.6532 | 0.027466 | 0.013733 | 122.8638 | 122.9095 | 122.8363 | 122.9004 | -122.8958 | -122.8775 | 122.6257 | 0.004577 | 2.1698 | 1.2863
1784.1719 | 122.9874 | -57.2662 | 65.6021 | -0.03006 | 0.00040806 | 0.061385 | 0.072677 | -0.00090783 | 0.0049689 | 0.0086262 | -0.0013428 | 0.0013159 | 0.0019226 | 0.001128 | -0.0027877 | -0.0032301 | -0.00061526 | -55.1468 | 65.5975 | -57.3349 | 65.3412 | -56.5613 | -57.0419 | -56.3049 | -56.0211 | 65.6158 | -57.28 | -57.2571 | -57.2433 | -57.3669 | -57.0602 | -0.068665 | -0.004578 | -0.26093 | 0.70496 | 0.9613 | 0.2243 | 1.03 | 0.29297 | -0.013733 | 0.013733 | -122.8592 | 0.022888 | 0.20599 | -0.10071 | 0.21973 | -0.086975 | 0.77362 | 122.6761 | 0.036621 | 0.022888 | 122.9324 | 122.8958 | 122.8638 | 122.8821 | -122.937 | -122.8821 | 122.6074 | 0.009155 | 2.1194 | 1.2451
1785.1719 | 122.9462 | -57.2754 | 65.5655 | -0.014801 | -0.00023294 | 0.062239 | 0.073958 | -0.0017624 | 0.0034735 | 0.007558 | -0.016602 | 0.0011023 | -0.00042717 | 0.0047594 | -0.0012925 | -0.00045288 | -0.0012561 | -55.1834 | 65.5518 | -57.3761 | 65.2863 | -56.6162 | -57.1243 | -56.3507 | -56.0806 | 65.5792 | -57.312 | -57.3029 | -57.3395 | -57.4585 | -57.106 | -0.10071 | -0.013733 | -0.27924 | 0.65918 | 0.92468 | 0.15106 | 1.0254 | 0.25177 | -0.036621 | 0.013733 | -122.8683 | -0.064087 | 0.16937 | -0.1831 | 0.20599 | -0.14648 | 0.75989 | 122.6624 | -0.027466 | 0.009156 | 122.9279 | 122.8912 | 122.8271 | 122.8546 | -122.9416 | -122.8775 | 122.5616 | -0.027465 | 2.092 | 1.1948
1786.1719 | 123.0331 | -57.2708 | 65.5609 | -0.075836 | 0.0014761 | 0.060957 | 0.073104 | -0.0026168 | 0.0036871 | 0.0056354 | -0.010498 | 0.00024775 | 0.0019226 | 0.00070062 | -0.0019333 | -0.0042981 | 0.00023934 | -55.0873 | 65.5701 | -57.3395 | 65.3732 | -56.5201 | -57.0236 | -56.2958 | -55.957 | 65.593 | -57.2845 | -57.2342 | -57.2342 | -57.3624 | -57.0236 | -0.068665 | 0.009155 | -0.18768 | 0.75073 | 0.97504 | 0.24719 | 1.0437 | 0.31586 | -0.013733 | 0.032044 | -122.7951 | 0.036621 | 0.24719 | -0.091553 | 0.26093 | -0.07782 | 0.8194 | 122.7127 | 0.050354 | 0.050354 | 122.9095 | 122.8775 | 122.8409 | 122.8638 | -122.9004 | -122.8455 | 122.644 | 0.036621 | 2.1835 | 1.3138
1787.1719 | 122.9691 | -57.2708 | 65.5792 | -0.083466 | -0.00044654 | 0.062239 | 0.073745 | 0.0050736 | 0.0026191 | 0.0073444 | -0.028809 | 0.0015295 | -0.00064077 | 0.0043322 | 0.00063009 | -0.0042981 | 2.554e-05 | -55.1193 | 65.5792 | -57.3349 | 65.4236 | -56.4789 | -57.0328 | -56.2775 | -55.9616 | 65.5746 | -57.28 | -57.2433 | -57.2617 | -57.3669 | -57.0419 | -0.064087 | 0 | -0.15564 | 0.79193 | 0.99335 | 0.23804 | 1.0574 | 0.30212 | -0.009155 | -0.004578 | -122.8226 | 0.009155 | 0.22888 | -0.09613 | 0.23804 | -0.086975 | 0.85602 | 122.7585 | 0.01831 | 0.036621 | 122.9141 | 122.8546 | 122.85 | 122.8455 | -122.9141 | -122.8592 | 122.6944 | 0.027466 | 2.1515 | 1.3092
1788.1719 | 122.9691 | -57.2708 | 65.593 | -0.045319 | 0.00019446 | 0.06288 | 0.073745 | 0.00080117 | -0.0010125 | 0.0071308 | -0.016602 | 0.00088875 | -0.00042717 | 5.9824e-05 | -0.00065151 | -0.0030163 | 0.0032299 | -55.1376 | 65.5289 | -57.3578 | 65.332 | -56.5475 | -57.0923 | -56.3141 | -55.9845 | 65.5746 | -57.2937 | -57.28 | -57.3029 | -57.4127 | -57.0786 | -0.086975 | -0.064087 | -0.26093 | 0.72327 | 0.95673 | 0.17853 | 1.0437 | 0.2655 | -0.022888 | -0.018311 | -122.8729 | -0.032043 | 0.19226 | -0.14191 | 0.21515 | -0.11902 | 0.81024 | 122.6898 | -0.009155 | 0.013733 | 122.8867 | 122.8683 | 122.7997 | 122.8455 | -122.9507 | -122.8867 | 122.6028 | -0.009155 | 2.1332 | 1.2863
1789.1719 | 122.9553 | -57.2662 | 65.5975 | 0.00045798 | 0.00040806 | 0.062025 | 0.069045 | 0.00080117 | 0.00091009 | 0.0047808 | 0.056641 | -0.0010339 | 2.8e-08 | -0.0018628 | -0.00043791 | -0.0028027 | 0.0032299 | -55.1376 | 65.5746 | -57.3212 | 65.3412 | -56.5384 | -57.0374 | -56.2683 | -56.0211 | 65.593 | -57.3166 | -57.2662 | -57.2433 | -57.3624 | -57.0877 | -0.054932 | -0.022888 | -0.25635 | 0.72784 | 0.99792 | 0.22888 | 1.0529 | 0.28381 | -0.050354 | -0.004577 | -122.8638 | 0.022888 | 0.17853 | -0.096131 | 0.22888 | -0.045777 | 0.78278 | 122.6624 | 0.073242 | 0.050354 | 122.8958 | 122.9095 | 122.8409 | 122.8592 | -122.9187 | -122.9141 | 122.6074 | 0 | 2.1286 | 1.2451
1790.1719 | 122.9691 | -57.2617 | 65.625 | -0.045319 | 0.00019446 | 0.06288 | 0.070113 | -5.343e-05 | 0.0026191 | 0.0079852 | 0.081055 | 0.0028113 | 0.0012818 | -0.0035718 | -0.0027877 | -0.0049389 | -0.0014697 | -55.1651 | 65.593 | -57.3212 | 65.332 | -56.5521 | -57.0511 | -56.282 | -56.0623 | 65.657 | -57.3029 | -57.2708 | -57.2754 | -57.3807 | -57.0877 | -0.059509 | -0.032043 | -0.29297 | 0.70953 | 0.97961 | 0.21057 | 1.0391 | 0.27008 | -0.041198 | 0.032043 | -122.8958 | -0.013733 | 0.17395 | -0.11902 | 0.21515 | -0.07782 | 0.76904 | 122.6532 | 0.027465 | 0.032043 | 122.9141 | 122.9599 | 122.8546 | 122.9187 | -122.9462 | -122.9279 | 122.5937 | -0.009155 | 2.0966 | 1.1993
1791.1719 | 122.9691 | -57.2296 | 65.5975 | -0.045319 | -0.00087374 | 0.062453 | 0.071395 | 0.00016017 | 0.0021917 | 0.0037128 | 0.059692 | 3.4148e-05 | -0.00064077 | -0.0027174 | -0.0012925 | -0.0053663 | 0.00088014 | -55.0919 | 65.5609 | -57.2891 | 65.3961 | -56.4743 | -56.9824 | -56.2088 | -55.9296 | 65.6113 | -57.2845 | -57.2525 | -57.2388 | -57.3395 | -57.0465 | -0.05951 | -0.036621 | -0.20142 | 0.75531 | 1.0208 | 0.24719 | 1.0803 | 0.3067 | -0.054932 | 0.013733 | -122.85 | -0.009156 | 0.1831 | -0.10986 | 0.23804 | -0.054932 | 0.81482 | 122.6852 | 0.045776 | 0.032044 | 122.85 | 122.8958 | 122.7905 | 122.8409 | -122.8867 | -122.8821 | 122.6257 | -0.022888 | 2.1378 | 1.3
1792.1719 | 122.9736 | -57.2708 | 65.5792 | -0.083466 | 0.0016899 | 0.060316 | 0.07524 | 0.0012284 | 0.0011237 | 0.0094806 | -0.0074462 | 0.0019567 | -0.00021357 | 0.0101 | -0.0023605 | -0.0032301 | 0.0015209 | -55.1102 | 65.5655 | -57.3074 | 65.3687 | -56.5292 | -57.0465 | -56.2866 | -55.9296 | 65.5975 | -57.2983 | -57.2296 | -57.2571 | -57.3624 | -57.0374 | -0.036621 | -0.013733 | -0.21057 | 0.74158 | 0.98419 | 0.2243 | 1.0208 | 0.26093 | -0.027466 | 0.01831 | -122.8088 | 0.013733 | 0.23346 | -0.091553 | 0.26093 | -0.064087 | 0.7782 | 122.6761 | 0.041199 | 0.068665 | 122.8729 | 122.8958 | 122.8363 | 122.8683 | -122.8867 | -122.8775 | 122.6395 | 0.041199 | 2.1606 | 1.3412
1793.1719 | 122.9736 | -57.28 | 65.625 | -0.083466 | 0.00083526 | 0.062025 | 0.071181 | 0.0012284 | 0.0019781 | 0.0071308 | 0.09021 | 0.0015295 | 0.0055542 | -0.0014356 | 0.00041649 | -0.0023755 | -0.0048877 | -55.1376 | 65.6021 | -57.3257 | 65.332 | -56.5659 | -57.0557 | -56.3049 | -56.0532 | 65.6799 | -57.2754 | -57.28 | -57.2754 | -57.3853 | -57.0694 | -0.045777 | -0.022888 | -0.29297 | 0.71411 | 0.97504 | 0.2243 | 1.0208 | 0.27008 | 0.004577 | 0.054932 | -122.905 | 0.004577 | 0.21057 | -0.10529 | 0.20599 | -0.10986 | 0.75989 | 122.6578 | 0 | -0.004577 | 122.9279 | 122.9553 | 122.8821 | 122.9599 | -122.9507 | -122.9004 | 122.612 | 0 | 2.1423 | 1.2268
1794.1719 | 122.9782 | -57.28 | 65.6158 | -0.075836 | -0.0010873 | 0.06288 | 0.072036 | 0.0016556 | 0.0026191 | 0.0056354 | 0.02002 | 0.00024775 | 0.00085443 | 0.002196 | -0.0017197 | -0.0030163 | -0.00040166 | -55.1468 | 65.5792 | -57.3486 | 65.3458 | -56.5796 | -57.0648 | -56.3004 | -56.0257 | 65.6113 | -57.2708 | -57.2708 | -57.2708 | -57.3761 | -57.0602 | -0.068665 | -0.036621 | -0.27008 | 0.70038 | 0.97961 | 0.21515 | 1.0483 | 0.28381 | 0.009155 | -0.004578 | -122.8867 | 0.009155 | 0.21973 | -0.096131 | 0.21057 | -0.10529 | 0.76904 | 122.6944 | 0 | 0 | 122.9279 | 122.8821 | 122.8592 | 122.8912 | -122.9645 | -122.8867 | 122.6257 | 0.009155 | 2.1332 | 1.2543
1795.1719 | 122.9324 | -57.2845 | 65.5884 | -0.12924 | 0.0023307 | 0.061598 | 0.075027 | 0.00251 | 0.0041143 | 0.0073444 | -0.041016 | 0.00046135 | 0.0014954 | 0.00091422 | -0.0021469 | -0.0025891 | 0.0019483 | -55.1514 | 65.5609 | -57.3532 | 65.3137 | -56.5933 | -57.1289 | -56.3553 | -56.0532 | 65.5975 | -57.3166 | -57.2937 | -57.3441 | -57.4402 | -57.0969 | -0.068664 | -0.027466 | -0.27466 | 0.69122 | 0.92926 | 0.15564 | 0.99792 | 0.2243 | -0.032043 | 0.009155 | -122.8821 | -0.059509 | 0.18768 | -0.15564 | 0.21973 | -0.1236 | 0.75989 | 122.6669 | -0.027466 | 0.022888 | 122.9141 | 122.9141 | 122.8455 | 122.8821 | -122.9416 | -122.905 | 122.5983 | -0.009155 | 2.1332 | 1.2314
1796.1719 | 123.0743 | -57.225 | 65.5426 | -0.11398 | -0.00066014 | 0.064375 | 0.071395 | -0.00090783 | 5.5488e-05 | 0.0071308 | 0.09021 | 0.0013159 | 0.001068 | -0.006349 | -0.0015061 | -0.0072889 | 0.0017345 | -55.0827 | 65.5289 | -57.2983 | 65.4602 | -56.3965 | -56.9183 | -56.1859 | -55.8655 | 65.5609 | -57.2433 | -57.1381 | -57.4356 | -57.3029 | -56.9275 | -0.073242 | -0.013733 | -0.082398 | 0.82855 | 1.0391 | 0.3067 | 1.1124 | 0.37994 | -0.01831 | 0.01831 | -122.6807 | -0.21057 | 0.29755 | -0.077819 | 0.31586 | -0.059509 | 0.90179 | 122.7585 | -0.19226 | 0.10529 | 122.8271 | 122.8043 | 122.7539 | 122.7859 | -122.8409 | -122.7859 | 122.6852 | 0.086975 | 2.1423 | 1.3596
1797.1719 | 123.0789 | -57.2205 | 65.5701 | -0.22842 | 0.0014761 | 0.063307 | 0.070541 | -0.0030442 | 0.0028327 | 0.0052082 | 0.062744 | 0.00067495 | 0.00042723 | -0.0042126 | -0.0015061 | -0.0030163 | -0.0012561 | -55.0369 | 65.5014 | -57.3029 | 65.4373 | -56.4239 | -56.9504 | -56.1905 | -55.8746 | 65.5701 | -57.28 | -57.1793 | -57.1655 | -57.2708 | -56.9824 | -0.082397 | -0.068664 | -0.13275 | 0.79651 | 1.03 | 0.27008 | 1.1124 | 0.35248 | -0.059509 | 0 | -122.7493 | 0.054932 | 0.23804 | -0.050354 | 0.29755 | 0.009155 | 0.87891 | 122.7402 | 0.11444 | 0.10071 | 122.8043 | 122.85 | 122.7219 | 122.7905 | -122.8729 | -122.85 | 122.6578 | 0.041199 | 2.1835 | 1.3458
1798.1719 | 122.9691 | -57.2754 | 65.6296 | -0.052948 | -0.0017281 | 0.062666 | 0.071822 | 0.0020828 | 0.0021917 | 0.0077716 | 0.032227 | 0.0028113 | 0.0029906 | 0.0015552 | -0.0027877 | -0.0034437 | -0.0018971 | -55.1239 | 65.593 | -57.3212 | 65.3503 | -56.5475 | -57.0648 | -56.2912 | -55.9982 | 65.6113 | -57.2662 | -57.2754 | -57.2617 | -57.3715 | -57.0648 | -0.045776 | -0.036621 | -0.27924 | 0.72785 | 0.98419 | 0.21057 | 1.03 | 0.25635 | 0.009156 | -0.018311 | -122.905 | 0.013733 | 0.21057 | -0.09613 | 0.20142 | -0.10529 | 0.77362 | 122.6715 | 0.004577 | -0.009156 | 122.9141 | 122.8775 | 122.8683 | 122.8867 | -122.9507 | -122.8958 | 122.6257 | 0 | 2.1515 | 1.2772
1799.1719 | 122.9416 | -57.2662 | 65.5838 | -0.0071715 | 0.0010489 | 0.062666 | 0.073104 | 0.00080117 | 0.00026909 | 0.0043536 | 0.029175 | -0.00017945 | 0.0029906 | -0.0025036 | -0.00043791 | -0.0040845 | 0.00045294 | -55.1285 | 65.5975 | -57.3441 | 65.5106 | -56.5613 | -57.2525 | -56.4285 | -56.0623 | 65.6296 | -57.2937 | -57.2571 | -57.2617 | -57.3761 | -57.0923 | -0.07782 | 0.013733 | -0.073242 | 0.70496 | 0.83771 | 0.013733 | 0.91553 | 0.091553 | -0.027466 | 0.045777 | -122.8409 | 0.004577 | 0.17395 | -0.10986 | 0.20142 | -0.082398 | 0.78278 | 122.8546 | 0.032043 | 0.036621 | 122.9416 | 122.9233 | 122.8638 | 122.8958 | -122.9279 | -122.8775 | 122.7768 | 0.009155 | 2.1378 | 1.2039
1800.1719 | 122.937 | -57.2754 | 65.5701 | -0.11398 | 0.00040806 | 0.063734 | 0.072463 | 0.0046464 | 0.0039007 | 0.0086262 | -0.034912 | 0.00024775 | 0.0025634 | 0.008391 | -0.00022431 | -0.0042981 | 0.00066654 | -55.1559 | 65.5472 | -57.3715 | 65.2954 | -56.6345 | -57.1564 | -56.3782 | -56.0852 | 65.6067 | -57.3303 | -57.3212 | -57.3532 | -57.4677 | -57.1335 | -0.09613 | -0.022888 | -0.27466 | 0.64087 | 0.89722 | 0.11902 | 0.99335 | 0.21515 | -0.054931 | 0.036621 | -122.8912 | -0.077819 | 0.14191 | -0.19226 | 0.19684 | -0.13733 | 0.737 | 122.6669 | -0.022888 | 0.009155 | 122.9187 | 122.937 | 122.8226 | 122.8821 | -122.9416 | -122.9004 | 122.5708 | -0.045776 | 2.1194 | 1.1902
1801.1719 | 122.9919 | -57.2525 | 65.5609 | -0.03006 | -0.00066014 | 0.063521 | 0.072036 | -0.00026703 | 0.0053961 | 0.0084124 | -0.019653 | -0.00017945 | 0.0021362 | -0.0025036 | -0.0040695 | -0.0038709 | 0.00045294 | -55.1102 | 65.5472 | -57.3578 | 65.3595 | -56.5247 | -57.0465 | -56.2866 | -55.9616 | 65.6113 | -57.3212 | -57.2067 | -57.2433 | -57.3486 | -57.074 | -0.10529 | -0.013733 | -0.20142 | 0.72784 | 0.96588 | 0.20599 | 1.0712 | 0.31128 | -0.068665 | 0.050354 | -122.7676 | 0.009155 | 0.17853 | -0.096131 | 0.24719 | -0.027466 | 0.83313 | 122.7173 | 0.07782 | 0.11444 | 122.905 | 122.9324 | 122.7997 | 122.8638 | -122.9187 | -122.8821 | 122.612 | 0.045776 | 2.1423 | 1.2909
1802.1719 | 122.9507 | -57.2891 | 65.6113 | -0.075836 | 0.0014761 | 0.061171 | 0.072036 | -0.00090783 | 0.0013373 | 0.0039264 | 0.02002 | 0.0011023 | 0.0014954 | -0.00229 | -0.0019333 | -0.0025891 | 0.00066654 | -55.1422 | 65.5792 | -57.3074 | 65.3275 | -56.5475 | -57.0419 | -56.2912 | -56.0028 | 65.6204 | -57.2845 | -57.2662 | -57.2708 | -57.3669 | -57.0786 | -0.01831 | -0.032043 | -0.28381 | 0.74158 | 0.99793 | 0.24719 | 1.0162 | 0.2655 | 0.004578 | 0.009155 | -122.8775 | 0.018311 | 0.21057 | -0.077819 | 0.20599 | -0.082397 | 0.75989 | 122.6349 | 0.013733 | 0.018311 | 122.8867 | 122.905 | 122.8683 | 122.9095 | -122.9187 | -122.8958 | 122.6166 | 0.022889 | 2.1469 | 1.2863
1803.1719 | 122.9782 | -57.2754 | 65.6204 | -0.075836 | -1.9142e-05 | 0.063734 | 0.070541 | -0.0024032 | 0.0039007 | 0.0067036 | 0.032227 | 0.00024775 | 0.0021362 | -0.0035718 | -0.00065151 | -0.0034437 | -0.00061526 | -55.1102 | 65.6067 | -57.3441 | 65.3366 | -56.5155 | -57.0236 | -56.2912 | -55.9891 | 65.6158 | -57.2937 | -57.2662 | -57.2708 | -57.3761 | -57.0831 | -0.068664 | -0.013733 | -0.28381 | 0.75989 | 0.98419 | 0.25177 | 1.0529 | 0.32043 | -0.01831 | -0.004577 | -122.8867 | 0.004578 | 0.19226 | -0.10071 | 0.21057 | -0.082398 | 0.82855 | 122.6807 | 0.022888 | 0.027466 | 122.9507 | 122.9095 | 122.8821 | 122.8912 | -122.9645 | -122.9141 | 122.612 | 0.009156 | 2.1652 | 1.2863
1804.1719 | 123.0743 | -57.2571 | 65.5609 | -0.091095 | 0.00040806 | 0.061385 | 0.071609 | -0.00026703 | 0.0017645 | 0.0032856 | 0.056641 | 0.00046135 | -0.00021357 | -0.011476 | -0.0034287 | -0.0053663 | 0.0021619 | -55.101 | 65.5243 | -57.2937 | 65.4282 | -56.4697 | -56.9916 | -56.2088 | -55.8929 | 65.5472 | -57.2708 | -57.1701 | -57.1289 | -57.2342 | -56.9687 | -0.036621 | -0.036621 | -0.13275 | 0.78735 | 1.0483 | 0.2655 | 1.0849 | 0.30212 | -0.013733 | -0.013733 | -122.731 | 0.12817 | 0.28839 | 0.022888 | 0.30212 | 0.036621 | 0.82397 | 122.7219 | 0.14191 | 0.10071 | 122.818 | 122.818 | 122.7814 | 122.8043 | -122.8546 | -122.8317 | 122.6852 | 0.086975 | 2.1561 | 1.3641
1805.1719 | 123.0377 | -57.2342 | 65.593 | -0.12924 | 0.00019446 | 0.063307 | 0.07225 | 0.0029374 | 0.0036871 | 0.0073444 | 0.047485 | 0.0015295 | -0.0010682 | 0.003905 | -0.00086511 | -0.0042981 | 0.00045294 | -55.0369 | 65.5197 | -57.3166 | 65.451 | -56.4194 | -56.9504 | -56.2225 | -55.8701 | 65.5655 | -57.2845 | -57.1838 | -57.1655 | -57.2479 | -56.9916 | -0.082397 | -0.073243 | -0.14191 | 0.81482 | 1.0117 | 0.28381 | 1.0941 | 0.36621 | -0.050354 | -0.027466 | -122.7768 | 0.068665 | 0.24262 | -0.013733 | 0.29297 | 0.036621 | 0.89722 | 122.7676 | 0.11902 | 0.10071 | 122.8363 | 122.85 | 122.7539 | 122.7997 | -122.9095 | -122.8775 | 122.6852 | 0.050354 | 2.1973 | 1.3641
1806.1719 | 122.9919 | -57.2754 | 65.5563 | -0.075836 | 0.00062166 | 0.062453 | 0.073958 | 0.003151 | 5.5488e-05 | 0.0067036 | -0.056274 | 0.0021703 | 0.00085443 | 5.9824e-05 | -0.00043791 | -0.0028027 | -0.0012561 | -55.1285 | 65.5563 | -57.3486 | 65.3549 | -56.5567 | -57.0786 | -56.3324 | -55.9845 | 65.6021 | -57.3029 | -57.2571 | -57.3074 | -57.3898 | -57.0786 | -0.073242 | 0 | -0.20142 | 0.71869 | 0.94299 | 0.19684 | 1.0162 | 0.27008 | -0.027465 | 0.045777 | -122.8134 | -0.032043 | 0.19684 | -0.11444 | 0.2243 | -0.086976 | 0.79193 | 122.7036 | -0.004578 | 0.045776 | 122.905 | 122.905 | 122.8317 | 122.8775 | -122.905 | -122.8592 | 122.6303 | 0.018311 | 2.1469 | 1.2909
1807.1719 | 122.9462 | -57.2525 | 65.593 | -0.068207 | 0.00040806 | 0.063948 | 0.070754 | 0.0018692 | 0.00091009 | 0.007558 | 0.029175 | 0.0021703 | 0.00085443 | 0.0043322 | -0.00065151 | -0.0051527 | -0.0010425 | -55.1468 | 65.5792 | -57.3257 | 65.3549 | -56.5475 | -57.0648 | -56.3004 | -55.9937 | 65.6113 | -57.2891 | -57.2754 | -57.2662 | -57.3669 | -57.0831 | -0.073243 | -0.013733 | -0.23804 | 0.70496 | 0.95215 | 0.18768 | 1.0254 | 0.26093 | -0.036622 | 0.01831 | -122.8683 | -0.013733 | 0.16937 | -0.11444 | 0.20599 | -0.077819 | 0.7782 | 122.6807 | 0.022889 | 0.013733 | 122.905 | 122.9004 | 122.8317 | 122.8638 | -122.9187 | -122.8821 | 122.6074 | -0.022889 | 2.1057 | 1.2589
1808.1719 | 122.9462 | -57.2662 | 65.5884 | -0.10635 | -0.0013009 | 0.062239 | 0.071609 | -0.0015488 | 0.0030463 | 0.0028582 | 0.016968 | 0.0021703 | 0.0014954 | -0.0044262 | -0.0025741 | -0.0045117 | 0.0010937 | -55.1605 | 65.5838 | -57.3441 | 65.3503 | -56.694 | -57.2159 | -56.3004 | -56.0486 | 65.6158 | -57.3074 | -57.2525 | -57.2708 | -57.3898 | -57.074 | -0.07782 | -0.004578 | -0.23804 | 0.5722 | 0.96588 | 0.050354 | 1.0437 | 0.12817 | -0.041199 | 0.027466 | -122.8409 | -0.004578 | 0.19226 | -0.1236 | 0.23346 | -0.082398 | 0.65002 | 122.6944 | 0.036621 | 0.054932 | 122.9279 | 122.9233 | 122.85 | 122.8821 | -122.9324 | -122.8958 | 122.6166 | 0.013733 | 2.1057 | 1.2177
1809.1719 | 123.0789 | -57.2617 | 65.5334 | -0.075836 | 0.00040806 | 0.064589 | 0.068404 | 0.00080117 | 0.0015509 | 0.005849 | 0.068848 | 3.4148e-05 | 0.002777 | -0.001222 | -0.0010787 | -0.0083569 | 0.00066654 | -55.0781 | 65.5197 | -57.2983 | 65.4739 | -56.4011 | -56.9458 | -56.1905 | -55.8563 | 65.5838 | -57.2571 | -56.9321 | -57.4036 | -57.4493 | -57.0236 | -0.036621 | -0.013733 | -0.059509 | 0.8606 | 1.0712 | 0.31586 | 1.1078 | 0.35248 | 0.004578 | 0.050354 | -122.4655 | -0.14191 | 0.23804 | -0.18768 | 0.23346 | -0.19226 | 0.89722 | 122.7722 | -0.14648 | 0.32501 | 122.818 | 122.8409 | 122.7814 | 122.8455 | -122.8317 | -122.7905 | 122.7356 | 0.32959 | 2.1835 | 1.4053
1810.1719 | 123.0057 | -57.2525 | 65.5609 | -0.068207 | 0.0012625 | 0.060957 | 0.073958 | 0.001442 | 0.0017645 | 0.0086262 | -0.08374 | 3.4148e-05 | -0.0014954 | 0.00070062 | -0.0019333 | -0.0042981 | 0.0013073 | -55.1102 | 65.5609 | -57.3578 | 65.3595 | -56.5201 | -57.0511 | -56.3049 | -55.9433 | 65.5838 | -57.3074 | -57.2205 | -57.2205 | -57.3669 | -57.0236 | -0.10529 | 0 | -0.20142 | 0.73242 | 0.94757 | 0.20142 | 1.0529 | 0.3067 | -0.054932 | 0.022888 | -122.7814 | 0.032043 | 0.22888 | -0.11444 | 0.28381 | -0.059509 | 0.83771 | 122.7173 | 0.086975 | 0.086975 | 122.9187 | 122.8912 | 122.8134 | 122.8363 | -122.9187 | -122.8683 | 122.612 | 0.032043 | 2.1423 | 1.3092
1811.1719 | 122.9141 | -57.2891 | 65.5289 | -0.098725 | 0.0036125 | 0.063307 | 0.075027 | 0.0020828 | 0.0034735 | 0.00414 | -0.27295 | 0.0023839 | 0.001709 | 0.00027342 | -0.0010787 | -0.0038709 | 0.0021619 | -55.22 | 65.5334 | -57.3669 | 65.2771 | -56.6574 | -57.1426 | -56.3965 | -55.9387 | 65.5701 | -57.3212 | -57.2845 | -57.3257 | -57.431 | -57.0877 | -0.077819 | 0.004577 | -0.25177 | 0.63171 | 0.89264 | 0.14648 | 0.97046 | 0.2243 | -0.032043 | 0.041198 | -122.8134 | -0.036621 | 0.20142 | -0.14191 | 0.23346 | -0.10986 | 0.70953 | 122.644 | -0.004578 | 0.036621 | 122.9004 | 122.8912 | 122.8226 | 122.8592 | -122.8958 | -122.85 | 122.5662 | 0.004578 | 2.0691 | 1.3504
1812.1719 | 122.9462 | -57.2433 | 65.6021 | -0.045319 | 0.0021171 | 0.061812 | 0.071822 | 0.00058737 | 0.0013373 | 0.0060626 | -0.0074462 | 0.0015295 | 0.002777 | -0.00058098 | -0.0019333 | -0.0040845 | -0.0021107 | -55.1559 | 65.5838 | -57.3029 | 65.3412 | -56.5887 | -57.1106 | -56.3278 | -56.0349 | 65.6158 | -57.3029 | -57.2662 | -57.2617 | -57.3715 | -57.0786 | -0.059509 | -0.018311 | -0.26093 | 0.6546 | 0.91553 | 0.13275 | 0.97504 | 0.19226 | -0.059509 | 0.013733 | -122.8683 | -0.018311 | 0.16479 | -0.12817 | 0.2243 | -0.068665 | 0.71411 | 122.644 | 0.041198 | 0.036621 | 122.8867 | 122.9187 | 122.8271 | 122.8592 | -122.905 | -122.905 | 122.5845 | -0.022888 | 2.0874 | 1.2085
1813.1719 | 123.0515 | -57.2342 | 65.5106 | -0.075836 | 0.00083526 | 0.062453 | 0.068618 | -0.0015488 | 0.0024053 | 0.0071308 | 0.062744 | -0.00039305 | -0.0038452 | -0.011049 | -0.00022431 | -0.0013073 | -0.0027515 | -55.0735 | 65.5472 | -57.2708 | 65.4602 | -56.4056 | -56.9366 | -56.1905 | -55.8701 | 65.5792 | -57.28 | -57.3303 | -57.1701 | -57.1884 | -56.9458 | -0.036621 | 0.036621 | -0.050354 | 0.82855 | 1.0437 | 0.29755 | 1.0803 | 0.33417 | -0.045776 | 0.068665 | -122.8409 | 0.064087 | 0.28839 | 0.045776 | 0.33417 | 0.091552 | 0.86517 | 122.731 | 0.10986 | -0.050354 | 122.818 | 122.8592 | 122.7814 | 122.8134 | -122.7814 | -122.7905 | 122.6944 | -0.09613 | 2.1606 | 1.3641
1814.1719 | 123.0103 | -57.225 | 65.5655 | -0.13687 | 0.0010489 | 0.061812 | 0.067763 | -0.0041122 | 0.0041143 | 0.0056354 | 0.035278 | 3.4148e-05 | 0.0021362 | -0.0010084 | -0.0030013 | -0.0060071 | -0.0033923 | -55.0644 | 65.5426 | -57.2891 | 65.4327 | -56.4377 | -56.9504 | -56.2134 | -55.8929 | 65.5655 | -57.28 | -57.1701 | -57.1609 | -57.2662 | -56.9778 | -0.064087 | -0.022888 | -0.13275 | 0.78735 | 1.0117 | 0.27466 | 1.0757 | 0.33875 | -0.054931 | 0 | -122.7356 | 0.064087 | 0.24719 | -0.041198 | 0.30212 | 0.013733 | 0.85144 | 122.7219 | 0.11902 | 0.10986 | 122.8317 | 122.8455 | 122.7676 | 122.7905 | -122.8546 | -122.8455 | 122.6578 | 0.054932 | 2.1606 | 1.3321
1815.1719 | 122.9874 | -57.2937 | 65.5838 | -0.052948 | -0.00023294 | 0.062025 | 0.074172 | 0.00251 | 0.0019781 | 0.0084124 | -0.10205 | 0.00046135 | -0.00085457 | 0.0043322 | -0.0023605 | -0.0010937 | 0.00023934 | -55.1376 | 65.5289 | -57.3532 | 65.3458 | -56.5659 | -57.0877 | -56.337 | -55.9891 | 65.593 | -57.3166 | -57.2708 | -57.2891 | -57.4036 | -57.0831 | -0.059509 | -0.054931 | -0.23804 | 0.72784 | 0.95673 | 0.20599 | 1.0162 | 0.2655 | -0.022888 | 0.009156 | -122.8546 | 0.004577 | 0.21057 | -0.10986 | 0.23346 | -0.086975 | 0.78735 | 122.699 | 0.027465 | 0.045776 | 122.8821 | 122.9095 | 122.8226 | 122.8867 | -122.937 | -122.9004 | 122.6395 | 0.022888 | 2.1561 | 1.3046
1816.1719 | 123.0789 | -57.2617 | 65.5014 | -0.083466 | -0.0021555 | 0.06288 | 0.071395 | 0.00037377 | 0.0030463 | 0.0090534 | -0.01355 | 0.00046135 | 0.0014954 | -0.00079478 | -0.00065151 | -0.0042981 | 0.0010937 | -55.1559 | 65.5289 | -57.3486 | 65.3549 | -56.5247 | -57.0557 | -56.3278 | -55.925 | 65.5426 | -57.2937 | -57.1838 | -57.2113 | -57.3257 | -56.9916 | -0.086975 | 0.027466 | -0.14648 | 0.737 | 0.93384 | 0.20599 | 1.0208 | 0.29297 | -0.032043 | 0.041199 | -122.6852 | 0.050354 | 0.27008 | -0.064087 | 0.30212 | -0.032044 | 0.82397 | 122.7036 | 0.082397 | 0.10986 | 122.8775 | 122.8363 | 122.7905 | 122.8043 | -122.85 | -122.7951 | 122.6166 | 0.07782 | 2.1057 | 1.3367
1817.1719 | 123.0652 | -57.2159 | 65.5289 | -0.091095 | 0.00083526 | 0.063734 | 0.069259 | -0.0038986 | 0.0015509 | 0.0039264 | 0.065796 | 0.0015295 | 0.001709 | -0.00058098 | -0.0012925 | -0.0053663 | 0.00066654 | -55.1147 | 65.5243 | -57.3257 | 65.4236 | -56.456 | -56.9687 | -56.2225 | -55.8701 | 65.5655 | -57.2525 | -57.1609 | -57.1426 | -57.2342 | -56.955 | -0.10986 | -0.004578 | -0.10529 | 0.75989 | 0.99335 | 0.24719 | 1.1032 | 0.35706 | -0.036621 | 0.036621 | -122.6898 | 0.073242 | 0.26093 | -0.018311 | 0.29755 | 0.01831 | 0.86975 | 122.7493 | 0.10986 | 0.091552 | 122.85 | 122.818 | 122.7402 | 122.7814 | -122.8546 | -122.7814 | 122.6395 | 0.054931 | 2.1011 | 1.3458
1818.1719 | 123.0789 | -57.2525 | 65.5655 | -0.13687 | -0.0015145 | 0.063094 | 0.071181 | -0.0079574 | 0.00091009 | 0.0079852 | 0.029175 | -0.0016749 | -0.00021357 | 0.0036914 | -0.00065151 | -0.0047253 | 0.0038709 | -55.0827 | 65.5289 | -57.2845 | 65.4694 | -56.4011 | -56.9504 | -56.2042 | -55.8655 | 65.5884 | -57.2479 | -57.1152 | -57.1701 | -57.3074 | -56.9962 | -0.032044 | -0.036621 | -0.096131 | 0.85144 | 1.0483 | 0.30212 | 1.0803 | 0.33417 | 0.004577 | 0.022888 | -122.6807 | 0.082397 | 0.25635 | -0.054932 | 0.25177 | -0.059509 | 0.88348 | 122.7539 | 0.07782 | 0.13275 | 122.8134 | 122.8363 | 122.7814 | 122.8409 | -122.85 | -122.8134 | 122.7219 | 0.13733 | 2.1698 | 1.387
1819.1719 | 123.0698 | -57.2342 | 65.5792 | -0.060578 | 0.0014761 | 0.062239 | 0.070968 | -0.00069423 | 0.0024053 | 0.007558 | 0.016968 | 3.4148e-05 | -0.001709 | -0.0050672 | -0.0012925 | -0.0028027 | -0.0018971 | -55.0919 | 65.4968 | -57.3029 | 65.451 | -56.4468 | -56.955 | -56.2271 | -55.8929 | 65.5701 | -57.2617 | -57.1701 | -57.1747 | -57.2525 | -56.9824 | -0.068664 | -0.082398 | -0.12817 | 0.78735 | 1.0071 | 0.27924 | 1.0757 | 0.3479 | -0.027466 | -0.009156 | -122.7493 | 0.059509 | 0.25177 | -0.01831 | 0.27924 | 0.009156 | 0.85602 | 122.7539 | 0.086975 | 0.091553 | 122.7997 | 122.8317 | 122.731 | 122.8043 | -122.8821 | -122.8409 | 122.6852 | 0.064087 | 2.1423 | 1.3412
1820.1719 | 122.9004 | -57.2433 | 65.5975 | -0.045319 | -1.9142e-05 | 0.063521 | 0.071395 | -0.001976 | 0.00048269 | 0.007558 | -0.022705 | -0.00060665 | -0.0012818 | -0.00058098 | -0.0019333 | -0.0017347 | 0.0021619 | -55.1468 | 65.5884 | -57.3074 | 65.3366 | -56.5887 | -57.0557 | -56.3049 | -56.0165 | 65.6067 | -57.2937 | -57.3212 | -57.1106 | -57.2021 | -57.0602 | -0.064087 | -0.009155 | -0.26093 | 0.6546 | 0.93841 | 0.18768 | 1.0025 | 0.25177 | -0.050354 | 0.009155 | -122.9187 | 0.13275 | 0.1831 | 0.041199 | 0.23346 | 0.091553 | 0.71869 | 122.644 | 0.1831 | -0.027466 | 122.8958 | 122.9004 | 122.8317 | 122.85 | -122.905 | -122.8912 | 122.58 | -0.07782 | 2.0966 | 1.2268
1821.1719 | 123.0743 | -57.2388 | 65.5655 | -0.060578 | 0.00019446 | 0.062666 | 0.070754 | -0.0017624 | 0.00048269 | 0.0062762 | 0.044434 | -0.0021021 | -0.00021357 | -0.002931 | -0.0012925 | -0.0040845 | -0.0027515 | -55.0964 | 65.5334 | -57.3029 | 65.4419 | -56.4423 | -56.955 | -56.2042 | -55.8517 | 65.5701 | -57.2617 | -57.1289 | -57.1289 | -57.2388 | -56.955 | -0.064086 | -0.032044 | -0.1236 | 0.79651 | 1.0345 | 0.28381 | 1.0986 | 0.3479 | -0.022888 | 0.004577 | -122.6944 | 0.10986 | 0.28381 | 0 | 0.3067 | 0.022888 | 0.86059 | 122.7448 | 0.13275 | 0.13275 | 122.8363 | 122.8317 | 122.7722 | 122.8088 | -122.8683 | -122.8271 | 122.6807 | 0.10986 | 2.1423 | 1.387
1822.1719 | 123.0881 | -57.225 | 65.5609 | -0.10635 | 0.0010489 | 0.061812 | 0.071395 | 0.0018692 | 0.0013373 | 0.0084124 | -0.0013428 | -0.0025293 | 0.0012818 | -0.0067762 | -0.0012925 | -0.0042981 | -0.0010425 | -55.069 | 65.5609 | -57.2891 | 65.4602 | -56.4239 | -56.9412 | -56.2042 | -55.6961 | 65.625 | -57.2571 | -57.193 | -57.1289 | -57.2433 | -56.987 | -0.064087 | 0 | -0.10071 | 0.80109 | 1.0208 | 0.28381 | 1.0849 | 0.3479 | -0.032043 | 0.064087 | -122.7539 | 0.096131 | 0.23804 | -0.01831 | 0.27008 | 0.013733 | 0.86517 | 122.7493 | 0.12817 | 0.064087 | 122.85 | 122.8821 | 122.7859 | 122.85 | -122.85 | -122.818 | 122.6852 | 0.032044 | 2.1561 | 1.5289
1823.1719 | 123.0423 | -57.2296 | 65.5655 | -0.098725 | 0.0012625 | 0.061598 | 0.0699 | -0.003685 | 0.0024053 | 0.0096942 | 0.010864 | 0.00046135 | 0.00064083 | -0.00036738 | -0.0012925 | -0.0023755 | -0.0021107 | -55.0827 | 65.5106 | -57.2891 | 65.4327 | -56.4514 | -56.9733 | -56.218 | -55.8884 | 65.5701 | -57.2342 | -57.1701 | -57.1609 | -57.2708 | -56.9778 | -0.05951 | -0.054932 | -0.13275 | 0.7782 | 1.0117 | 0.25635 | 1.0712 | 0.31586 | -0.004578 | 0.004577 | -122.7356 | 0.068664 | 0.25177 | -0.041199 | 0.25635 | -0.036621 | 0.83771 | 122.7219 | 0.073242 | 0.064087 | 122.7997 | 122.8043 | 122.7402 | 122.7997 | -122.8546 | -122.7997 | 122.6624 | 0.059509 | 2.1469 | 1.3412
1824.1719 | 123.0377 | -57.2205 | 65.5518 | -0.13687 | -0.0015145 | 0.062239 | 0.071395 | -0.001976 | 0.0015509 | 0.0094806 | 0.016968 | -0.00082025 | -0.0010682 | -0.0065626 | -0.0021469 | -0.0034437 | -0.0014697 | -55.1239 | 65.5243 | -57.3349 | 65.4327 | -56.4972 | -57.0053 | -56.2363 | -55.9158 | 65.5609 | -57.2937 | -57.1609 | -57.1564 | -57.2571 | -56.9824 | -0.11444 | -0.027466 | -0.11902 | 0.72327 | 0.98419 | 0.21515 | 1.0986 | 0.32959 | -0.073242 | 0.009155 | -122.7127 | 0.064087 | 0.23804 | -0.036621 | 0.31128 | 0.036621 | 0.83771 | 122.7676 | 0.13733 | 0.13275 | 122.8592 | 122.8546 | 122.7448 | 122.7814 | -122.8867 | -122.8455 | 122.6532 | 0.059509 | 2.0966 | 1.3046
1825.1719 | 122.9599 | -57.2571 | 65.6158 | -0.052948 | -0.0027963 | 0.064162 | 0.070113 | 0.00058737 | 0.00048269 | 0.0067036 | -0.019653 | 0.0023839 | 0.0036316 | -0.00058098 | -0.0019333 | -0.0038709 | -0.0016833 | -55.1285 | 65.5701 | -57.3349 | 65.3458 | -56.5613 | -57.0511 | -56.3004 | -56.0074 | 65.625 | -57.2937 | -57.2479 | -57.2662 | -57.3486 | -57.0694 | -0.07782 | -0.045777 | -0.27008 | 0.6958 | 0.95673 | 0.20599 | 1.0345 | 0.28381 | -0.036621 | 0.009155 | -122.8638 | -0.009155 | 0.18768 | -0.091553 | 0.2243 | -0.054932 | 0.77362 | 122.6807 | 0.027466 | 0.045776 | 122.905 | 122.9187 | 122.8271 | 122.8821 | -122.9507 | -122.9095 | 122.6028 | 0.009155 | 2.1286 | 1.2497
1826.1719 | 123.0606 | -57.2479 | 65.5334 | -0.12161 | -0.0013009 | 0.062239 | 0.0699 | -0.0013352 | 0.0032599 | 0.0060626 | 0.013916 | 0.00046135 | 0.00042723 | -0.0059216 | 0.00084389 | -0.0021619 | -0.0018971 | -55.0644 | 65.5426 | -57.2983 | 65.4831 | -56.4102 | -56.9321 | -56.1996 | -55.8746 | 65.5701 | -57.2571 | -57.2662 | -57.0557 | -57.2708 | -57.0374 | -0.050354 | 0.009156 | -0.050354 | 0.83771 | 1.0483 | 0.31586 | 1.0986 | 0.36621 | -0.009155 | 0.036621 | -122.7997 | 0.19226 | 0.21057 | -0.022888 | 0.21973 | -0.013733 | 0.88806 | 122.7814 | 0.20142 | -0.009155 | 122.8409 | 122.8271 | 122.7905 | 122.818 | -122.8317 | -122.7905 | 122.731 | -0.01831 | 2.1835 | 1.3733
1827.1719 | 123.1064 | -57.2388 | 65.5426 | -0.091095 | 0.00062166 | 0.062239 | 0.070754 | -0.00090783 | 0.0030463 | 0.0086262 | 0.053589 | 0.0011023 | -0.0012818 | 0.00048702 | -0.0017197 | -0.0036573 | -0.0051013 | -55.069 | 65.5289 | -57.3029 | 65.4739 | -56.4239 | -56.9366 | -56.1859 | -55.838 | 65.5426 | -57.2571 | -57.1381 | -57.1426 | -57.2388 | -56.9595 | -0.064086 | -0.013733 | -0.068665 | 0.81482 | 1.0529 | 0.30212 | 1.1169 | 0.36621 | -0.01831 | 0 | -122.6807 | 0.096131 | 0.27924 | 0 | 0.29755 | 0.01831 | 0.87891 | 122.7768 | 0.11444 | 0.11902 | 122.8317 | 122.7997 | 122.7676 | 122.7814 | -122.8455 | -122.7997 | 122.7127 | 0.10071 | 2.1698 | 1.4008
1828.1719 | 123.0515 | -57.2433 | 65.5655 | -0.11398 | 0.00062166 | 0.063094 | 0.070754 | 0.0018692 | 5.5488e-05 | 0.0060626 | 0.065796 | 0.00067495 | 0.00064083 | 0.001128 | -0.0032151 | -0.0040845 | -0.0027515 | -55.0781 | 65.5472 | -57.2845 | 65.6525 | -56.3141 | -57.3669 | -56.3416 | -55.925 | 65.5655 | -57.28 | -57.1289 | -57.1518 | -57.2342 | -56.9733 | -0.041199 | -0.018311 | 0.086975 | 0.92926 | 0.90179 | -0.1236 | 0.94299 | -0.082397 | -0.036621 | 0 | -122.6944 | 0.091553 | 0.27008 | 0.009155 | 0.3067 | 0.045776 | 0.97046 | 122.937 | 0.12817 | 0.15106 | 122.8317 | 122.8455 | 122.7905 | 122.8088 | -122.85 | -122.8455 | 122.8958 | 0.11444 | 2.1652 | 1.3184
1829.1719 | 122.9553 | -57.2571 | 65.6113 | -0.014801 | 0.00040806 | 0.061598 | 0.071395 | -0.0030442 | -0.00037171 | 0.0049946 | -0.0074462 | 0.00088875 | -0.0010682 | -0.0010084 | -0.00043791 | -0.0045117 | 0.00088014 | -55.1056 | 65.5563 | -57.2937 | 65.387 | -56.5247 | -57.0099 | -56.2775 | -55.9708 | 65.6158 | -57.2662 | -57.2433 | -57.2571 | -57.3349 | -57.0465 | -0.036621 | -0.054932 | -0.2243 | 0.73242 | 0.97961 | 0.24719 | 1.0162 | 0.28381 | -0.009155 | 0.004578 | -122.8546 | 0 | 0.21057 | -0.07782 | 0.21973 | -0.068665 | 0.76904 | 122.6807 | 0.009155 | 0.022888 | 122.85 | 122.8821 | 122.8134 | 122.8729 | -122.905 | -122.8775 | 122.644 | 0.013733 | 2.1515 | 1.2863
1830.1719 | 123.024 | -57.2617 | 65.5975 | -0.03006 | 0.0025443 | 0.061812 | 0.074172 | 0.00037377 | 0.0032599 | 0.0067036 | -0.080688 | 3.4148e-05 | 0.00021363 | 0.0049732 | -0.0021469 | -0.0036573 | -0.0040333 | -55.1102 | 65.5655 | -57.3486 | 65.3824 | -56.5567 | -57.0557 | -56.2958 | -55.9479 | 65.6067 | -57.3029 | -57.1884 | -57.2205 | -57.3303 | -57.0374 | -0.086975 | -0.032043 | -0.21515 | 0.70496 | 0.96588 | 0.20599 | 1.0529 | 0.29297 | -0.041198 | 0.009155 | -122.7859 | 0.041199 | 0.2243 | -0.068664 | 0.2655 | -0.027466 | 0.79193 | 122.731 | 0.082397 | 0.11444 | 122.9141 | 122.9095 | 122.8271 | 122.8683 | -122.9462 | -122.9004 | 122.644 | 0.073242 | 2.1515 | 1.3138
1831.1719 | 123.0011 | -57.2617 | 65.5334 | -0.10635 | 0.00083526 | 0.062025 | 0.071609 | -0.00069423 | 0.0019781 | 0.0043536 | 0.029175 | 0.0011023 | 0.00064083 | -0.0020764 | -0.0010787 | -0.0019483 | -0.0012561 | -55.1605 | 65.5197 | -57.3395 | 65.3687 | -56.5384 | -57.0648 | -56.2866 | -55.9937 | 65.5518 | -57.3074 | -57.1106 | -57.2342 | -57.3761 | -57.0557 | -0.07782 | -0.013733 | -0.16479 | 0.72327 | 0.97504 | 0.19684 | 1.0529 | 0.27466 | -0.045776 | 0.018311 | -122.644 | 0.027466 | 0.20599 | -0.11444 | 0.25177 | -0.068665 | 0.80109 | 122.7081 | 0.073242 | 0.19684 | 122.8592 | 122.8592 | 122.7814 | 122.8134 | -122.8729 | -122.8409 | 122.6303 | 0.15106 | 2.1011 | 1.268
1832.1719 | 123.0286 | -57.2571 | 65.5289 | -0.11398 | 0.00083526 | 0.061385 | 0.07289 | 0.0029374 | 0.0032599 | 0.0071308 | 0.001709 | -0.00060665 | 0.001709 | 0.002196 | -0.0015061 | -0.0032301 | 0.00088014 | -55.1651 | 65.506 | -57.3257 | 65.3641 | -56.5475 | -57.0557 | -56.2958 | -55.9845 | 65.5609 | -57.2891 | -57.2067 | -57.2205 | -57.3212 | -57.0282 | -0.068665 | -0.022889 | -0.16479 | 0.70953 | 0.9613 | 0.20142 | 1.03 | 0.27008 | -0.032044 | 0.032043 | -122.7356 | 0.036621 | 0.22888 | -0.064087 | 0.26093 | -0.032043 | 0.7782 | 122.6898 | 0.068665 | 0.082398 | 122.8317 | 122.85 | 122.7631 | 122.818 | -122.8546 | -122.818 | 122.6212 | 0.050354 | 2.092 | 1.2726
1833.1719 | 123.0057 | -57.2571 | 65.5334 | -0.12161 | -1.9142e-05 | 0.062239 | 0.072463 | -0.00048063 | 0.0032599 | 0.0086262 | -0.0043946 | 0.00088875 | 0.0012818 | 0.00070062 | -0.0015061 | -0.0025891 | -0.00018806 | -55.1834 | 65.506 | -57.3349 | 65.3778 | -56.5384 | -57.0877 | -56.2958 | -55.9753 | 65.5472 | -57.2983 | -57.2205 | -57.2205 | -57.3303 | -57.0282 | -0.07782 | -0.027466 | -0.15564 | 0.71869 | 0.9613 | 0.16937 | 1.0391 | 0.24719 | -0.041199 | 0.013733 | -122.7539 | 0.036621 | 0.22888 | -0.073242 | 0.27008 | -0.032043 | 0.79651 | 122.7127 | 0.07782 | 0.07782 | 122.8409 | 122.8455 | 122.7631 | 122.8043 | -122.8683 | -122.8317 | 122.6349 | 0.036621 | 2.0737 | 1.2817
1834.1719 | 123.0423 | -57.2617 | 65.5334 | -0.10635 | -0.00044654 | 0.064589 | 0.070541 | -5.343e-05 | 0.0024053 | 0.0099078 | 0.026123 | -0.0023157 | -0.0023498 | 0.0013416 | -0.0032151 | -0.0040845 | -0.00018806 | -55.2017 | 65.5014 | -57.3257 | 65.3915 | -56.543 | -57.0419 | -56.2729 | -55.9708 | 65.5655 | -57.2891 | -57.1976 | -57.1976 | -57.2708 | -57.0145 | -0.064087 | -0.032043 | -0.14191 | 0.71869 | 0.98877 | 0.21973 | 1.0529 | 0.28381 | -0.027466 | 0.032044 | -122.731 | 0.064087 | 0.24719 | -0.009155 | 0.27466 | 0.018311 | 0.78278 | 122.7173 | 0.091553 | 0.091553 | 122.8271 | 122.8546 | 122.7631 | 122.8271 | -122.8592 | -122.8226 | 122.6532 | 0.064087 | 2.0599 | 1.2909
1835.1719 | 123.056 | -57.2159 | 65.5518 | -0.091095 | -0.0017281 | 0.06288 | 0.070754 | 0.004219 | 0.0039007 | 0.0056354 | 0.032227 | -0.00060665 | -0.00064077 | -0.00058098 | -0.0036423 | -0.0036573 | -0.0014697 | -55.1239 | 65.5334 | -57.28 | 65.4373 | -56.3644 | -57.0374 | -56.2637 | -55.8975 | 65.5609 | -57.2891 | -57.1609 | -57.1655 | -57.2433 | -56.9778 | -0.064087 | -0.018311 | -0.11444 | 0.85144 | 0.95215 | 0.17853 | 1.0162 | 0.24261 | -0.073243 | 0.009155 | -122.7127 | 0.050354 | 0.23804 | -0.027466 | 0.31128 | 0.045777 | 0.91553 | 122.7173 | 0.1236 | 0.12817 | 122.8134 | 122.85 | 122.7493 | 122.7768 | -122.8317 | -122.8409 | 122.6532 | 0.054931 | 2.092 | 1.3184
1836.1719 | 123.0835 | -57.2205 | 65.5563 | -0.10635 | -0.00087374 | 0.061598 | 0.073958 | -0.00069423 | 0.0015509 | 0.0043536 | 0.02002 | 0.0017431 | 0.00085443 | 0.0032642 | -0.0010787 | -0.0055799 | -0.0027515 | -55.1559 | 65.538 | -57.312 | 65.4419 | -56.4789 | -56.9687 | -56.2225 | -55.8792 | 65.5746 | -57.2708 | -57.1426 | -57.1472 | -57.2342 | -56.9412 | -0.091553 | -0.01831 | -0.11444 | 0.74158 | 0.99792 | 0.25177 | 1.0895 | 0.34332 | -0.050354 | 0.018311 | -122.699 | 0.073242 | 0.27924 | -0.013733 | 0.32959 | 0.036621 | 0.83313 | 122.7539 | 0.1236 | 0.12817 | 122.85 | 122.8455 | 122.7585 | 122.7951 | -122.8683 | -122.8271 | 122.6624 | 0.07782 | 2.0645 | 1.3412
1837.1719 | 123.0835 | -57.2571 | 65.5197 | -0.12161 | 0.0019035 | 0.063948 | 0.07289 | 0.0040054 | 0.0034735 | 0.0037128 | -0.016602 | 0.00088875 | 0.00064083 | 0.0049732 | -0.0019333 | -0.0023755 | -0.0031787 | -55.1697 | 65.4922 | -57.312 | 65.4556 | -56.7215 | -57.1198 | -56.1584 | -55.9479 | 65.5472 | -57.2845 | -57.1609 | -57.2067 | -57.3303 | -56.987 | -0.054932 | -0.027465 | -0.064087 | 0.53558 | 1.0986 | 0.13733 | 1.1536 | 0.19226 | -0.027466 | 0.027466 | -122.6807 | 0.050354 | 0.27008 | -0.073242 | 0.29755 | -0.045776 | 0.59052 | 122.7676 | 0.07782 | 0.1236 | 122.8043 | 122.8317 | 122.7493 | 122.8043 | -122.8317 | -122.8043 | 122.7127 | 0.09613 | 2.0874 | 1.3092
1838.1719 | 123.0423 | -57.2525 | 65.5334 | -0.11398 | 0.0027579 | 0.064375 | 0.07289 | 0.0033646 | 0.0024053 | 0.0081988 | -0.050171 | 0.0023839 | 0.00021363 | -0.0061352 | -0.0015061 | -0.00045288 | -0.00061526 | -55.1697 | 65.4922 | -57.3395 | 65.3915 | -56.5109 | -57.0557 | -56.282 | -55.9296 | 65.5472 | -57.2937 | -57.225 | -57.0648 | -57.1884 | -56.9962 | -0.086976 | -0.041198 | -0.14191 | 0.74158 | 0.97046 | 0.19684 | 1.0574 | 0.28381 | -0.041199 | 0.013733 | -122.7585 | 0.18768 | 0.25635 | 0.064086 | 0.29755 | 0.10529 | 0.82855 | 122.731 | 0.22888 | 0.068664 | 122.8317 | 122.8409 | 122.7448 | 122.7997 | -122.8729 | -122.8271 | 122.644 | 0.027465 | 2.0828 | 1.3229
1839.1719 | 123.0194 | -57.2433 | 65.5243 | -0.098725 | -0.0019417 | 0.063734 | 0.072677 | 0.001442 | 0.0019781 | 0.0086262 | 0.023071 | 0.00024775 | -0.0023498 | 5.9824e-05 | -0.00086511 | -0.0053663 | 0.0028027 | -55.2109 | 65.5197 | -57.3166 | 65.3778 | -56.5475 | -57.0694 | -56.2912 | -55.9891 | 65.5609 | -57.2845 | -57.1426 | -57.1243 | -57.3349 | -57.0831 | -0.073242 | -0.004578 | -0.14648 | 0.6958 | 0.95215 | 0.17395 | 1.0254 | 0.24719 | -0.041199 | 0.036621 | -122.6669 | 0.11902 | 0.16022 | -0.091553 | 0.20142 | -0.050354 | 0.76904 | 122.6944 | 0.16022 | 0.14191 | 122.8363 | 122.8455 | 122.7631 | 122.8043 | -122.8409 | -122.8088 | 122.6212 | 0.10071 | 2.0325 | 1.2543
1840.1719 | 123.0698 | -57.2296 | 65.5655 | -0.083466 | 0.00019446 | 0.063094 | 0.072463 | 0.0029374 | 0.0015509 | 0.0067036 | -0.0043946 | 0.0013159 | 0.00064083 | 0.0032642 | -0.0032151 | -0.0034437 | -0.0023243 | -55.1331 | 65.5426 | -57.3074 | 65.4602 | -56.4789 | -56.987 | -56.2408 | -55.9021 | 65.5655 | -57.28 | -57.1838 | -57.1609 | -57.2617 | -56.987 | -0.07782 | -0.022888 | -0.10529 | 0.75073 | 0.98877 | 0.24261 | 1.0666 | 0.32043 | -0.050354 | 0 | -122.7493 | 0.068664 | 0.24261 | -0.032044 | 0.29297 | 0.01831 | 0.82855 | 122.7676 | 0.11902 | 0.09613 | 122.85 | 122.8455 | 122.7722 | 122.7951 | -122.8729 | -122.8455 | 122.6898 | 0.045776 | 2.0966 | 1.3275
1841.1719 | 123.0103 | -57.28 | 65.4922 | -0.12161 | -1.9142e-05 | 0.063734 | 0.071395 | -0.0024032 | 0.0030463 | 0.0077716 | -0.025757 | 0.0011023 | 0.00085443 | 0.00091422 | -0.00065151 | -0.0060071 | 0.00066654 | -55.1788 | 65.4785 | -57.3395 | 65.4007 | -56.5063 | -57.0419 | -56.2729 | -55.9387 | 65.5014 | -57.3074 | -57.193 | -57.2205 | -57.3303 | -57.0282 | -0.05951 | -0.013733 | -0.091553 | 0.77362 | 1.0071 | 0.23804 | 1.0666 | 0.29755 | -0.027466 | 0.009155 | -122.6852 | 0.059509 | 0.25177 | -0.050354 | 0.27924 | -0.022888 | 0.83313 | 122.7402 | 0.086975 | 0.11444 | 122.818 | 122.8088 | 122.7585 | 122.7814 | -122.8317 | -122.7997 | 122.6807 | 0.086975 | 2.1011 | 1.3412
1842.1719 | 123.0286 | -57.2388 | 65.5243 | -0.037689 | 0.00040806 | 0.064375 | 0.071181 | 0.00016017 | 0.0011237 | 0.0073444 | -0.0074462 | 0.0013159 | 0.00021363 | -0.00464 | -0.00043791 | -0.0021619 | -0.00082886 | -55.2063 | 65.4877 | -57.3441 | 65.3641 | -56.5475 | -57.074 | -56.3049 | -56.0028 | 65.5518 | -57.312 | -57.1884 | -57.2296 | -57.3257 | -57.0419 | -0.10528 | -0.036621 | -0.16022 | 0.69122 | 0.93384 | 0.1648 | 1.0391 | 0.27008 | -0.073242 | 0.027466 | -122.7127 | 0.009156 | 0.19684 | -0.086975 | 0.27008 | -0.013733 | 0.79651 | 122.7081 | 0.082398 | 0.1236 | 122.8317 | 122.8638 | 122.7264 | 122.7905 | -122.8683 | -122.8363 | 122.6028 | 0.050354 | 2.0325 | 1.236
1843.1719 | 123.0148 | -57.2479 | 65.5289 | -0.11398 | -0.00066014 | 0.063521 | 0.072463 | -0.003685 | -0.0010125 | 0.0094806 | -0.0043946 | 0.0011023 | -0.00064077 | -0.007417 | -0.00065151 | -0.0034437 | 0.0038709 | -55.1926 | 65.5014 | -57.3166 | 65.3595 | -56.5567 | -57.0786 | -56.3049 | -55.9753 | 65.5334 | -57.3166 | -57.2113 | -57.2205 | -57.3303 | -57.0374 | -0.068664 | -0.027466 | -0.16937 | 0.69122 | 0.94299 | 0.16937 | 1.0117 | 0.23804 | -0.068664 | 0.004577 | -122.7402 | 0.027466 | 0.21057 | -0.082397 | 0.27923 | -0.013733 | 0.75989 | 122.6761 | 0.09613 | 0.10529 | 122.818 | 122.85 | 122.7493 | 122.7814 | -122.8455 | -122.8455 | 122.6074 | 0.036621 | 2.0554 | 1.2726
1844.1719 | 123.0331 | -57.2617 | 65.5289 | -0.12161 | 0.00083526 | 0.061171 | 0.071609 | -0.0032578 | 0.0039007 | 0.0071308 | -0.0013428 | -0.00060665 | 2.8e-08 | -0.0035718 | -0.0010787 | -0.0053663 | 0.0015209 | -55.2063 | 65.5014 | -57.3395 | 65.3687 | -56.5659 | -57.0786 | -56.2958 | -55.9753 | 65.5792 | -57.3029 | -57.2617 | -57.0969 | -57.2662 | -57.0465 | -0.07782 | -0.027466 | -0.16022 | 0.6958 | 0.96588 | 0.18311 | 1.0437 | 0.26093 | -0.041198 | 0.050354 | -122.7905 | 0.16479 | 0.21515 | -0.004577 | 0.25635 | 0.036621 | 0.77362 | 122.7081 | 0.20599 | 0.041198 | 122.8409 | 122.8821 | 122.7631 | 122.8409 | -122.8683 | -122.8317 | 122.6303 | 0 | 2.0554 | 1.2863
1845.1719 | 123.0469 | -57.2571 | 65.5563 | -0.12161 | 0.00019446 | 0.06288 | 0.072036 | 0.00037377 | 0.0030463 | 0.0056354 | -0.0043946 | -0.00017945 | 0.001068 | 0.0058276 | -0.0038559 | -0.0017347 | -0.0018971 | -55.1926 | 65.5197 | -57.3212 | 65.3641 | -56.5384 | -57.0557 | -56.3004 | -55.9799 | 65.5563 | -57.3349 | -57.2067 | -57.2159 | -57.3441 | -57.0465 | -0.064087 | -0.036621 | -0.19226 | 0.71869 | 0.95673 | 0.20142 | 1.0208 | 0.2655 | -0.07782 | 0 | -122.7631 | 0.041199 | 0.21057 | -0.086975 | 0.28839 | -0.009155 | 0.78278 | 122.6852 | 0.11902 | 0.12817 | 122.8409 | 122.8912 | 122.7768 | 122.8134 | -122.8775 | -122.8912 | 122.6212 | 0.050354 | 2.0645 | 1.2772
1846.1719 | 123.0652 | -57.2525 | 65.5334 | -0.1445 | 0.00062166 | 0.061812 | 0.071395 | 0.00016017 | 0.0041143 | 0.0047808 | -0.028809 | 0.0011023 | -0.0010682 | 0.00091422 | -0.0023605 | -0.0040845 | 0.00066654 | -55.1743 | 65.4877 | -57.3349 | 65.4099 | -56.5109 | -57.0511 | -56.2866 | -55.9387 | 65.5426 | -57.2983 | -57.1838 | -57.225 | -57.3303 | -57.019 | -0.082398 | -0.045776 | -0.1236 | 0.74158 | 0.96588 | 0.20142 | 1.0483 | 0.28381 | -0.045777 | 0.009156 | -122.7173 | 0.027465 | 0.23346 | -0.07782 | 0.27924 | -0.032043 | 0.82397 | 122.7448 | 0.073242 | 0.11444 | 122.8226 | 122.8409 | 122.7402 | 122.7951 | -122.8683 | -122.8317 | 122.6624 | 0.068664 | 2.0782 | 1.3138
1847.1719 | 123.024 | -57.2388 | 65.5243 | -0.18265 | 0.0027579 | 0.063307 | 0.072463 | 0.0010148 | 0.0021917 | 0.0060626 | -0.010498 | 0.00067495 | -0.00085457 | -0.001222 | 0.00041649 | -0.0038709 | -0.0014697 | -55.2109 | 65.4831 | -57.3441 | 65.3595 | -56.5521 | -57.0831 | -56.3004 | -55.9799 | 65.538 | -57.3029 | -57.225 | -57.2159 | -57.3212 | -57.0145 | -0.10528 | -0.041199 | -0.16479 | 0.68665 | 0.93842 | 0.15564 | 1.0437 | 0.26093 | -0.064086 | 0.013733 | -122.7493 | 0.022889 | 0.22431 | -0.082397 | 0.28839 | -0.018311 | 0.79193 | 122.7036 | 0.086975 | 0.077819 | 122.8271 | 122.8409 | 122.7219 | 122.7768 | -122.8683 | -122.8271 | 122.5983 | 0.013733 | 2.0279 | 1.2589
1848.1719 | 123.0148 | -57.2525 | 65.5151 | -0.12924 | 0.0010489 | 0.062239 | 0.073958 | 0.0018692 | 0.00091009 | 0.007558 | 0.013916 | 0.0019567 | -0.00021357 | 0.001128 | -0.00022431 | -0.0025891 | 0.00066654 | -55.2063 | 65.5334 | -57.3395 | 65.3687 | -56.5613 | -57.0694 | -56.3004 | -56.0394 | 65.5884 | -57.2845 | -57.2113 | -57.2021 | -57.3074 | -57.0236 | -0.086976 | 0.01831 | -0.14648 | 0.69122 | 0.95215 | 0.1831 | 1.0391 | 0.27008 | -0.032044 | 0.073242 | -122.7264 | 0.050354 | 0.22888 | -0.054932 | 0.26093 | -0.022888 | 0.7782 | 122.7081 | 0.082398 | 0.073242 | 122.8729 | 122.8729 | 122.7859 | 122.8409 | -122.8546 | -122.7997 | 122.6212 | 0.041198 | 2.0462 | 1.2131
1849.1719 | 123.0652 | -57.2845 | 65.5426 | -0.098725 | -0.00087374 | 0.060957 | 0.071822 | 0.00016017 | 0.0015509 | 0.0081988 | 0.0078126 | 0.0028113 | 0.001709 | 0.0028368 | -0.0017197 | -0.0028027 | -0.00040166 | -55.22 | 65.5151 | -57.3395 | 65.3915 | -56.5384 | -57.0465 | -56.282 | -55.9616 | 65.5518 | -57.2754 | -57.1747 | -57.1838 | -57.2845 | -56.9733 | -0.054932 | -0.027466 | -0.15106 | 0.74616 | 1.0025 | 0.23804 | 1.0574 | 0.29297 | 0.009155 | 0.009155 | -122.7173 | 0.10071 | 0.31128 | 0 | 0.30212 | -0.009155 | 0.80109 | 122.731 | 0.091553 | 0.10071 | 122.8546 | 122.8271 | 122.7997 | 122.8363 | -122.8821 | -122.818 | 122.6761 | 0.10986 | 2.0645 | 1.3229
1850.1719 | 123.0927 | -57.1655 | 65.5609 | -0.098725 | 0.0010489 | 0.061812 | 0.073318 | -0.0043258 | 0.00091009 | 0.0049946 | 0.010864 | -0.0023157 | -0.00085457 | -0.0014356 | -0.0023605 | -0.0023755 | -0.0012561 | -55.1147 | 65.5289 | -57.2937 | 65.4831 | -56.4148 | -56.9366 | -56.2042 | -55.8563 | 65.5746 | -57.2571 | -57.1335 | -57.1289 | -57.0419 | -56.7719 | -0.12817 | -0.032043 | -0.07782 | 0.75073 | 0.9613 | 0.22888 | 1.0895 | 0.35705 | -0.091553 | 0.013733 | -122.6944 | 0.036621 | 0.39368 | 0.1236 | 0.48523 | 0.21515 | 0.87891 | 122.7768 | 0.12817 | 0.1236 | 122.8226 | 122.8317 | 122.6944 | 122.7402 | -122.8546 | -122.818 | 122.6486 | 0.032043 | 2.0508 | 1.3092
1851.1719 | 123.0148 | -57.2617 | 65.5243 | -0.12924 | -0.00087374 | 0.060957 | 0.071181 | 0.00058737 | 0.0047553 | 0.0086262 | -0.028809 | -0.00060665 | -0.00085457 | -0.001222 | -0.0017197 | -0.0034437 | 0.0040845 | -55.1605 | 65.4968 | -57.312 | 65.3961 | -56.5201 | -57.0511 | -56.2866 | -55.9387 | 65.5334 | -57.2845 | -57.1793 | -57.2159 | -57.3303 | -57.0374 | -0.050354 | -0.027466 | -0.12817 | 0.74158 | 0.97504 | 0.21057 | 1.0254 | 0.26093 | -0.022888 | 0.009155 | -122.7036 | 0.045777 | 0.2243 | -0.068664 | 0.24719 | -0.045776 | 0.79193 | 122.7081 | 0.068665 | 0.10529 | 122.8088 | 122.818 | 122.7585 | 122.7951 | -122.8363 | -122.8088 | 122.6578 | 0.082398 | 2.1011 | 1.3229
1852.1719 | 123.0331 | -57.2662 | 65.4922 | -0.15976 | 0.0012625 | 0.064589 | 0.072463 | -0.0011214 | 0.0013373 | 0.0062762 | -0.028809 | 0.0032385 | -0.00064077 | -0.00079478 | -0.0036423 | -0.00088008 | 0.0015209 | -55.1468 | 65.5014 | -57.3257 | 65.4144 | -56.5155 | -57.019 | -56.2775 | -55.9341 | 65.5426 | -57.2937 | -57.1747 | -57.2067 | -57.3029 | -56.9916 | -0.05951 | 0.009155 | -0.07782 | 0.75073 | 0.98877 | 0.24719 | 1.0483 | 0.3067 | -0.027466 | 0.050354 | -122.6669 | 0.059509 | 0.27466 | -0.036621 | 0.30212 | -0.009155 | 0.81024 | 122.7402 | 0.086975 | 0.11902 | 122.8271 | 122.8363 | 122.7676 | 122.8088 | -122.818 | -122.7859 | 122.6807 | 0.091552 | 2.1194 | 1.3321
1853.1719 | 123.0103 | -57.2708 | 65.538 | -0.083466 | 0.00083526 | 0.062666 | 0.071822 | 0.0010148 | 0.0043281 | 0.0045672 | -0.019653 | -0.00017945 | 0.00042723 | 0.0017688 | -0.0012925 | -0.0034437 | -0.00061526 | -55.2155 | 65.4831 | -57.3166 | 65.3824 | -56.5567 | -57.0694 | -56.2912 | -55.9799 | 65.5518 | -57.28 | -57.1976 | -57.2296 | -57.3212 | -57.0145 | -0.045776 | -0.054932 | -0.15564 | 0.71411 | 0.97961 | 0.20142 | 1.0254 | 0.24719 | -0.009155 | 0.013733 | -122.7356 | 0.041199 | 0.25635 | -0.050354 | 0.2655 | -0.041199 | 0.75989 | 122.699 | 0.050354 | 0.082397 | 122.7997 | 122.8317 | 122.7539 | 122.8226 | -122.8546 | -122.818 | 122.6532 | 0.073242 | 2.0554 | 1.2909
1854.1719 | 123.0377 | -57.2525 | 65.4968 | -0.098725 | 0.00062166 | 0.063521 | 0.073104 | 0.0022964 | 0.00069649 | 0.0062762 | -0.037964 | -0.0035975 | -0.0012818 | 0.0026232 | -0.0034287 | -0.0047253 | 0.00066654 | -55.1651 | 65.4922 | -57.3212 | 65.4144 | -56.5247 | -57.0557 | -56.3004 | -55.9525 | 65.5014 | -57.3074 | -57.1564 | -57.1884 | -57.2891 | -56.9778 | -0.068665 | -0.004577 | -0.082397 | 0.72784 | 0.95215 | 0.19684 | 1.0208 | 0.2655 | -0.054932 | 0.004578 | -122.6532 | 0.064086 | 0.27466 | -0.036622 | 0.32959 | 0.01831 | 0.79651 | 122.7356 | 0.11902 | 0.15106 | 122.8134 | 122.8088 | 122.7448 | 122.7539 | -122.818 | -122.8043 | 122.6669 | 0.09613 | 2.0874 | 1.3
1855.1719 | 123.024 | -57.2571 | 65.5106 | -0.16739 | 0.0010489 | 0.063307 | 0.070754 | -0.0017624 | 5.5488e-05 | 0.0077716 | -0.037964 | 0.0013159 | -0.0012818 | 0.0019824 | -0.0012925 | -0.0034437 | -0.0014697 | -55.1605 | 65.4922 | -57.312 | 65.4099 | -56.4835 | -57.0374 | -56.2912 | -55.9341 | 65.5426 | -57.3029 | -57.1655 | -57.1976 | -57.2937 | -56.9916 | -0.054932 | -0.01831 | -0.10071 | 0.77362 | 0.96588 | 0.21973 | 1.0208 | 0.27466 | -0.045776 | 0.032044 | -122.6761 | 0.059509 | 0.2655 | -0.036621 | 0.31128 | 0.009155 | 0.82855 | 122.7219 | 0.10528 | 0.13733 | 122.8043 | 122.8455 | 122.7493 | 122.7997 | -122.8226 | -122.8134 | 122.6669 | 0.091553 | 2.0966 | 1.3229
1856.1719 | 123.0377 | -57.2662 | 65.506 | -0.11398 | 0.0014761 | 0.063734 | 0.071181 | -0.003685 | 0.0036871 | 0.005849 | -0.010498 | 0.00046135 | -0.00064077 | -0.0042126 | -0.0012925 | -0.0019483 | -0.0023243 | -55.22 | 65.4648 | -57.3486 | 65.4099 | -56.4697 | -57.0419 | -56.2912 | -55.9341 | 65.5243 | -57.312 | -57.1609 | -57.1838 | -57.3029 | -56.9916 | -0.082398 | -0.041198 | -0.09613 | 0.79651 | 0.97504 | 0.2243 | 1.0574 | 0.3067 | -0.045777 | 0.018311 | -122.6669 | 0.082397 | 0.27466 | -0.036621 | 0.32044 | 0.009156 | 0.87891 | 122.7585 | 0.12817 | 0.15106 | 122.8134 | 122.8363 | 122.731 | 122.7905 | -122.8546 | -122.818 | 122.6761 | 0.10529 | 2.0462 | 1.3321
1857.1719 | 123.0057 | -57.2479 | 65.5014 | -0.18265 | 0.0025443 | 0.062666 | 0.071822 | -0.0011214 | 0.0013373 | 0.0081988 | -0.028809 | 0.0025975 | -0.0027772 | 0.0024096 | -0.00043791 | -0.0030163 | 0.0010937 | -55.188 | 65.5014 | -57.3212 | 65.4053 | -56.5155 | -57.0419 | -56.282 | -55.925 | 65.5334 | -57.2754 | -57.1747 | -57.2296 | -57.3212 | -57.0145 | -0.073242 | 0 | -0.096131 | 0.73242 | 0.96588 | 0.20599 | 1.0391 | 0.27924 | -0.027466 | 0.032043 | -122.6761 | 0.018311 | 0.23346 | -0.073242 | 0.26093 | -0.045776 | 0.80566 | 122.7264 | 0.045777 | 0.10071 | 122.8226 | 122.8088 | 122.7493 | 122.7814 | -122.8226 | -122.7768 | 122.6532 | 0.073242 | 2.0599 | 1.3229
1858.1719 | 123.0515 | -57.2525 | 65.5151 | -0.13687 | -0.00087374 | 0.063307 | 0.07289 | 0.003151 | 0.0019781 | 0.007558 | -0.041016 | 0.0013159 | -0.00085457 | -0.001222 | -0.0032151 | -0.0023755 | -0.0012561 | -55.1743 | 65.4968 | -57.3395 | 65.4007 | -56.5475 | -57.0694 | -56.3049 | -55.9433 | 65.5518 | -57.2983 | -57.2708 | -57.1289 | -57.1426 | -56.9 | -0.086976 | -0.018311 | -0.11444 | 0.70496 | 0.94757 | 0.1831 | 1.0345 | 0.27008 | -0.045777 | 0.036621 | -122.7859 | 0.1236 | 0.35248 | 0.10986 | 0.39825 | 0.15564 | 0.79193 | 122.7402 | 0.16937 | 0.027466 | 122.8363 | 122.85 | 122.7493 | 122.8043 | -122.8546 | -122.8134 | 122.6532 | -0.018311 | 2.0782 | 1.3092
1859.1719 | 122.9691 | -57.2891 | 65.5518 | -0.091095 | 0.00062166 | 0.064803 | 0.072677 | -0.0024032 | 0.0034735 | 0.0096942 | -0.10205 | 0.00046135 | 0.00085443 | 0.0019824 | -0.00086511 | -0.0013073 | -0.0023243 | -55.2429 | 65.5426 | -57.3486 | 65.3687 | -56.7398 | -57.1152 | -56.369 | -56.0577 | 65.593 | -57.3486 | -57.2571 | -57.312 | -57.4356 | -57.0877 | -0.059509 | -0.009155 | -0.18311 | 0.54932 | 0.9201 | 0.17395 | 0.97961 | 0.23346 | -0.059509 | 0.041199 | -122.8088 | -0.022888 | 0.20142 | -0.14648 | 0.26093 | -0.086975 | 0.60883 | 122.7173 | 0.036621 | 0.091553 | 122.8912 | 122.9416 | 122.8317 | 122.8821 | -122.9004 | -122.9004 | 122.6578 | 0.032044 | 2.0462 | 1.2314
1860.1719 | 123.0377 | -57.2571 | 65.4785 | -0.12161 | 0.0016899 | 0.065657 | 0.071822 | 0.0033646 | 0.0036871 | 0.0054218 | -0.034912 | 3.4148e-05 | -0.0010682 | -0.0010084 | -0.0023605 | -0.0042981 | 0.00088014 | -55.1743 | 65.4877 | -57.3166 | 65.4968 | -56.3782 | -57.0877 | -56.2958 | -55.9341 | 65.538 | -57.2891 | -57.1518 | -57.193 | -57.2983 | -56.9916 | -0.059509 | 0.009155 | 0.01831 | 0.87891 | 0.9613 | 0.16937 | 1.0208 | 0.22888 | -0.032044 | 0.059509 | -122.6303 | 0.064087 | 0.2655 | -0.041199 | 0.29755 | -0.009155 | 0.93841 | 122.8134 | 0.096131 | 0.13733 | 122.8043 | 122.8271 | 122.7448 | 122.7951 | -122.7951 | -122.7676 | 122.7539 | 0.10529 | 2.0828 | 1.3229
1861.1719 | 123.0652 | -57.225 | 65.506 | -0.098725 | 0.0021171 | 0.061812 | 0.072463 | 0.0016556 | 0.0019781 | 0.0084124 | -0.022705 | 0.0013159 | -0.00085457 | -0.00079478 | -0.0030013 | -0.0025891 | -0.0018971 | -55.1743 | 65.4877 | -57.312 | 65.4007 | -56.5247 | -57.0511 | -56.282 | -56.0577 | 65.4877 | -57.3212 | -57.1426 | -57.193 | -57.2983 | -56.987 | -0.086975 | -0.01831 | -0.10529 | 0.70038 | 0.94299 | 0.17395 | 1.03 | 0.26093 | -0.09613 | -0.01831 | -122.6486 | 0.032044 | 0.23804 | -0.073242 | 0.33417 | 0.022888 | 0.78735 | 122.7127 | 0.12817 | 0.17853 | 122.7997 | 122.8088 | 122.7127 | 122.7127 | -122.818 | -122.8271 | 122.6257 | 0.082398 | 2.0508 | 1.1673
1862.1719 | 123.0331 | -57.2891 | 65.5106 | -0.091095 | -0.00044654 | 0.063521 | 0.07289 | 0.00016017 | 0.0034735 | 0.0060626 | -0.053223 | 0.0028113 | 0.00085443 | -0.0027174 | -0.0021469 | -0.0025891 | -0.0038197 | -55.2383 | 65.5289 | -57.3486 | 65.332 | -56.6116 | -57.1381 | -56.3736 | -55.9982 | 65.5518 | -57.3166 | -57.193 | -57.2479 | -57.3257 | -57.0007 | -0.059509 | 0.018311 | -0.17853 | 0.67749 | 0.91553 | 0.15106 | 0.97504 | 0.21057 | -0.027465 | 0.041199 | -122.7036 | 0.041199 | 0.28839 | -0.036621 | 0.31586 | -0.009156 | 0.737 | 122.6807 | 0.068664 | 0.1236 | 122.8775 | 122.8683 | 122.818 | 122.8409 | -122.8592 | -122.8271 | 122.6212 | 0.096131 | 2.0508 | 1.2909
1863.1719 | 123.0423 | -57.2662 | 65.4968 | -0.12924 | -0.00023294 | 0.063734 | 0.074172 | 0.0022964 | 0.0034735 | 0.0054218 | -0.044067 | 0.0015295 | 0.00064083 | 0.0043322 | -0.0027877 | -0.0034437 | -0.00061526 | -55.2429 | 65.5151 | -57.3669 | 65.3229 | -56.6391 | -57.1289 | -56.3965 | -56.0394 | 65.5518 | -57.3257 | -57.2205 | -57.2708 | -57.3441 | -57.0419 | -0.10071 | 0.018311 | -0.17395 | 0.62714 | 0.86975 | 0.13733 | 0.97046 | 0.23804 | -0.05951 | 0.054932 | -122.7173 | -0.004578 | 0.2243 | -0.07782 | 0.28381 | -0.01831 | 0.72784 | 122.6898 | 0.054932 | 0.10529 | 122.8821 | 122.8775 | 122.7814 | 122.818 | -122.8638 | -122.8226 | 122.5891 | 0.045776 | 2.0233 | 1.2268
1864.1719 | 123.0606 | -57.2525 | 65.4877 | -0.1445 | -0.00044654 | 0.065016 | 0.073531 | 0.0072098 | 0.0013373 | 0.0054218 | -0.016602 | 3.4148e-05 | -0.001709 | -0.0027174 | -0.0010787 | -0.0017347 | -0.0021107 | -55.1651 | 65.4877 | -57.3212 | 65.4556 | -56.337 | -57.0694 | -56.2912 | -55.9341 | 65.5426 | -57.2937 | -57.1518 | -57.1884 | -57.2891 | -56.9916 | -0.068665 | 0 | -0.032044 | 0.91553 | 0.9613 | 0.1831 | 1.03 | 0.25177 | -0.041199 | 0.054932 | -122.6395 | 0.064086 | 0.26093 | -0.036622 | 0.30212 | 0.004577 | 0.98419 | 122.7768 | 0.10529 | 0.14191 | 122.8088 | 122.8363 | 122.7402 | 122.7951 | -122.8088 | -122.7814 | 122.7081 | 0.10071 | 2.0874 | 1.3184
1865.1719 | 123.0194 | -57.2754 | 65.5197 | -0.16739 | -1.9142e-05 | 0.064803 | 0.071609 | 0.004219 | 0.00091009 | 0.0064898 | 0.0078126 | 0.0028113 | 0.002777 | -0.0065626 | -0.0010787 | -0.0019483 | -0.0012561 | -55.1788 | 65.4831 | -57.3074 | 65.3732 | -56.5155 | -57.0465 | -56.2912 | -55.9158 | 65.538 | -57.3074 | -57.1838 | -57.2296 | -57.3212 | -56.9916 | -0.032043 | -0.036621 | -0.14648 | 0.75989 | 0.98419 | 0.22888 | 1.0162 | 0.26093 | -0.032043 | 0.018311 | -122.7036 | 0.045777 | 0.28381 | -0.045776 | 0.31586 | -0.013733 | 0.79193 | 122.6807 | 0.07782 | 0.1236 | 122.7905 | 122.8455 | 122.7585 | 122.8134 | -122.8271 | -122.8271 | 122.6486 | 0.091553 | 2.0966 | 1.3596
1866.1719 | 122.9187 | -57.2983 | 65.5472 | -0.098725 | -0.0010873 | 0.062239 | 0.074172 | 0.0027238 | 0.0028327 | 0.0071308 | -0.068481 | 0.0021703 | 0.001709 | -0.0059216 | -0.0010787 | -0.0010937 | 0.00066654 | -55.2429 | 65.5426 | -57.3715 | 65.2908 | -56.6666 | -57.1701 | -56.4331 | -56.1127 | 65.5838 | -57.3395 | -57.2845 | -57.3166 | -57.4539 | -57.0969 | -0.073242 | -0.004577 | -0.25635 | 0.63171 | 0.86517 | 0.12817 | 0.93842 | 0.20142 | -0.041199 | 0.036621 | -122.8317 | -0.01831 | 0.20142 | -0.15564 | 0.24262 | -0.11444 | 0.70496 | 122.6624 | 0.022889 | 0.054932 | 122.9141 | 122.9233 | 122.8409 | 122.8821 | -122.9187 | -122.8867 | 122.5891 | 0.013733 | 2.0554 | 1.1856
1867.1719 | 123.0103 | -57.2571 | 65.5106 | -0.11398 | -0.0015145 | 0.063307 | 0.070327 | 0.0022964 | 0.0032599 | 0.007558 | -0.077637 | -0.0016749 | -0.00042717 | -0.003999 | -0.0019333 | -0.0042981 | -0.0038197 | -55.2155 | 65.5289 | -57.3578 | 65.3091 | -56.6071 | -57.1381 | -56.4011 | -56.044 | 65.5701 | -57.3349 | -57.2205 | -57.2662 | -57.3807 | -57.074 | -0.10071 | 0.018311 | -0.20142 | 0.65002 | 0.85602 | 0.11902 | 0.95673 | 0.21973 | -0.07782 | 0.059509 | -122.731 | -0.009155 | 0.18311 | -0.1236 | 0.26093 | -0.045776 | 0.75073 | 122.6669 | 0.068665 | 0.11444 | 122.8867 | 122.905 | 122.7859 | 122.8271 | -122.8683 | -122.8455 | 122.5662 | 0.036621 | 2.0416 | 1.2131
1868.1719 | 123.0148 | -57.2708 | 65.5243 | -0.098725 | -0.0010873 | 0.062025 | 0.072677 | -0.00048063 | 0.0036871 | 0.005849 | -0.050171 | 0.0021703 | -0.0025636 | -0.0025036 | 0.00041649 | -0.0023755 | -0.0016833 | -55.2429 | 65.5243 | -57.3441 | 65.2954 | -56.6574 | -57.1655 | -56.4011 | -56.0623 | 65.5563 | -57.3257 | -57.2433 | -57.2891 | -57.3944 | -57.0648 | -0.073242 | 0 | -0.22888 | 0.6134 | 0.86975 | 0.10529 | 0.94299 | 0.17853 | -0.054932 | 0.032043 | -122.7676 | -0.018311 | 0.20599 | -0.1236 | 0.26093 | -0.068664 | 0.68664 | 122.6395 | 0.036621 | 0.082398 | 122.8683 | 122.8821 | 122.7951 | 122.8271 | -122.8683 | -122.85 | 122.5662 | 0.027466 | 2.0279 | 1.2085
1869.1719 | 123.0469 | -57.2296 | 65.5472 | -0.1445 | 0.0014761 | 0.064162 | 0.070113 | -0.00048063 | 0.0030463 | 0.0084124 | -0.0074462 | 0.0011023 | -0.0038452 | 0.0030506 | -0.0027877 | -0.0032301 | -0.00018806 | -55.1651 | 65.4922 | -57.3441 | 65.3915 | -56.5247 | -57.0511 | -56.3095 | -55.925 | 65.5243 | -57.3074 | -57.1564 | -57.2205 | -57.2662 | -56.9687 | -0.11444 | -0.054931 | -0.15564 | 0.70496 | 0.9201 | 0.17853 | 1.0345 | 0.29297 | -0.07782 | -0.022888 | -122.7036 | 0.009155 | 0.26093 | -0.036621 | 0.33875 | 0.041199 | 0.8194 | 122.7356 | 0.086975 | 0.15106 | 122.8363 | 122.8317 | 122.7219 | 122.7539 | -122.8912 | -122.8546 | 122.6212 | 0.073242 | 2.0645 | 1.3046
1870.1719 | 123.0972 | -57.2159 | 65.5334 | -0.083466 | -0.00044654 | 0.061171 | 0.069472 | 0.00058737 | 0.0030463 | 0.0067036 | 0.056641 | -0.00017945 | 0.00042723 | -0.003999 | 0.00020289 | -0.0021619 | 0.0015209 | -55.1559 | 65.5518 | -57.3029 | 65.4373 | -56.488 | -56.987 | -56.2454 | -55.8884 | 65.5746 | -57.2845 | -57.1335 | -57.1335 | -57.2113 | -56.9412 | -0.086975 | 0.018311 | -0.09613 | 0.72784 | 0.97046 | 0.22888 | 1.0574 | 0.31586 | -0.068665 | 0.041199 | -122.6669 | 0.082397 | 0.27466 | 0.004577 | 0.34332 | 0.073242 | 0.81482 | 122.7402 | 0.15106 | 0.15106 | 122.8546 | 122.8592 | 122.7676 | 122.7905 | -122.8363 | -122.818 | 122.6532 | 0.082397 | 2.0599 | 1.3275
1871.1719 | 122.9507 | -57.2891 | 65.5472 | -0.098725 | 0.0016899 | 0.062453 | 0.074172 | -0.0013352 | 0.00048269 | 0.0088398 | 0.047485 | 0.00088875 | -0.00042717 | 0.00048702 | -0.0019333 | -0.0040845 | 0.0021619 | -55.2429 | 65.538 | -57.3578 | 65.2863 | -56.781 | -57.5592 | -56.4514 | -56.163 | 65.6158 | -57.312 | -57.2662 | -57.3486 | -57.4173 | -57.0831 | -0.068664 | -0.009155 | -0.26093 | 0.50812 | 0.83771 | -0.27008 | 0.90637 | -0.20142 | -0.022888 | 0.068665 | -122.8134 | -0.059509 | 0.20599 | -0.12817 | 0.22888 | -0.10528 | 0.57678 | 122.644 | -0.036621 | 0.045777 | 122.8958 | 122.9279 | 122.8271 | 122.905 | -122.905 | -122.8592 | 122.5754 | 0.022889 | 2.0462 | 1.1261
1872.1719 | 123.0469 | -57.2159 | 65.5563 | -0.060578 | 0.0019035 | 0.065016 | 0.070754 | 0.0029374 | 0.00026909 | 0.0060626 | 0.026123 | 0.00046135 | -0.0010682 | -0.0025036 | -0.0019333 | -0.0040845 | -0.0012561 | -55.307 | 65.5472 | -57.312 | 65.4282 | -56.4697 | -56.9641 | -56.25 | -55.8975 | 65.5701 | -57.2571 | -57.1609 | -57.1609 | -57.225 | -56.9595 | -0.096131 | -0.009155 | -0.12817 | 0.74615 | 0.96588 | 0.25177 | 1.062 | 0.3479 | -0.041199 | 0.013733 | -122.7173 | 0.054931 | 0.25635 | -0.009156 | 0.29755 | 0.032043 | 0.84229 | 122.7402 | 0.09613 | 0.09613 | 122.8592 | 122.8271 | 122.7631 | 122.7859 | -122.8683 | -122.8134 | 122.644 | 0.054931 | 1.9089 | 1.3184
1873.1719 | 122.9599 | -57.2845 | 65.5563 | 0.046234 | 0.0025443 | 0.063307 | 0.072036 | 0.0044328 | 0.0034735 | 0.007558 | -0.041016 | 0.0011023 | 2.8e-08 | 0.0030506 | -0.0023605 | -0.0032301 | -0.0016833 | -55.2887 | 65.5426 | -57.3853 | 65.2725 | -56.6803 | -57.1518 | -56.4148 | -56.0669 | 65.5746 | -57.3074 | -57.2662 | -57.3029 | -57.4356 | -57.0969 | -0.10071 | -0.013732 | -0.28381 | 0.60425 | 0.86975 | 0.13275 | 0.97046 | 0.23346 | -0.022888 | 0.018311 | -122.8226 | -0.01831 | 0.18768 | -0.15106 | 0.21057 | -0.12817 | 0.70496 | 122.6578 | 0.004578 | 0.041199 | 122.9279 | 122.8821 | 122.8271 | 122.8592 | -122.9416 | -122.8638 | 122.5571 | 0.018311 | 1.9958 | 1.2177
1874.1719 | 122.9736 | -57.2754 | 65.5609 | -0.098725 | -0.0015145 | 0.060744 | 0.073531 | -0.00069423 | 0.0013373 | 0.0084124 | -0.080688 | 0.00046135 | 2.8e-08 | 0.0028368 | -0.0030013 | -0.0025891 | 0.0017345 | -55.2429 | 65.5426 | -57.3715 | 65.3503 | -56.7261 | -57.1243 | -56.3736 | -56.0852 | 65.5884 | -57.3166 | -57.28 | -57.3212 | -57.431 | -57.0831 | -0.09613 | -0.01831 | -0.21057 | 0.54932 | 0.90179 | 0.15106 | 0.99793 | 0.24719 | -0.041198 | 0.027466 | -122.8409 | -0.045776 | 0.19226 | -0.15564 | 0.23346 | -0.11444 | 0.64545 | 122.7219 | -0.004578 | 0.036621 | 122.9141 | 122.905 | 122.818 | 122.8638 | -122.9324 | -122.8775 | 122.6257 | -0.004577 | 2.0325 | 1.1902
1875.1719 | 123.0148 | -57.2662 | 65.5243 | -0.12924 | -1.9142e-05 | 0.063948 | 0.069686 | -0.0015488 | 0.0030463 | 0.0043536 | 0.016968 | 0.00088875 | -0.0010682 | 0.0030506 | 0.0010575 | -0.0021619 | -0.00082886 | -55.188 | 65.4831 | -57.3212 | 65.3915 | -56.5201 | -57.0648 | -56.3141 | -55.9708 | 65.5289 | -57.3029 | -57.1976 | -57.2205 | -57.3212 | -57.0053 | -0.054932 | -0.041199 | -0.13275 | 0.74615 | 0.95215 | 0.20142 | 1.0071 | 0.25635 | -0.036621 | 0.004578 | -122.7219 | 0.045776 | 0.26093 | -0.054932 | 0.29755 | -0.018311 | 0.80109 | 122.7127 | 0.082397 | 0.10528 | 122.8043 | 122.8317 | 122.7493 | 122.7951 | -122.8455 | -122.8271 | 122.6578 | 0.068664 | 2.0782 | 1.2955
1876.1719 | 122.9599 | -57.2983 | 65.5655 | -0.060578 | -0.00023294 | 0.062239 | 0.074172 | -5.343e-05 | 0.0019781 | 0.0071308 | -0.053223 | 0.0019567 | 0.001068 | -0.0033582 | -0.0021469 | -0.0036573 | 0.0036571 | -55.22 | 65.5197 | -57.3578 | 65.2817 | -56.6666 | -57.1655 | -56.3965 | -56.0944 | 65.5884 | -57.3349 | -57.2617 | -57.3029 | -57.4173 | -57.074 | -0.059509 | -0.045777 | -0.28381 | 0.63171 | 0.90179 | 0.13275 | 0.9613 | 0.19226 | -0.036621 | 0.022888 | -122.8271 | -0.004577 | 0.2243 | -0.11902 | 0.26093 | -0.082397 | 0.69122 | 122.6395 | 0.032044 | 0.073242 | 122.8775 | 122.9233 | 122.818 | 122.8867 | -122.9233 | -122.9004 | 122.58 | 0.036621 | 2.0782 | 1.2039
1877.1719 | 123.0789 | -57.2708 | 65.5518 | -0.1445 | -0.00044654 | 0.060103 | 0.069045 | -0.0013352 | 0.0021917 | 0.0062762 | 0.059692 | 0.0017431 | 0.00064083 | -0.002931 | -0.00065151 | -0.0030163 | -0.00018806 | -55.1926 | 65.538 | -57.3349 | 65.387 | -56.5384 | -57.0511 | -56.2912 | -55.9799 | 65.5518 | -57.3166 | -57.1976 | -57.1655 | -57.2754 | -57.0053 | -0.064087 | -0.013733 | -0.1648 | 0.73242 | 0.97961 | 0.21973 | 1.0437 | 0.28381 | -0.045776 | 0 | -122.7493 | 0.10529 | 0.2655 | -0.004578 | 0.31128 | 0.041198 | 0.79651 | 122.7219 | 0.15106 | 0.11902 | 122.8729 | 122.8683 | 122.8088 | 122.8226 | -122.8867 | -122.8683 | 122.6578 | 0.073242 | 2.0782 | 1.2909
1878.1719 | 122.9416 | -57.2891 | 65.5746 | -0.075836 | -0.0010873 | 0.063307 | 0.074813 | 0.0029374 | 0.0026191 | 0.0056354 | -0.074585 | 0.00046135 | -0.00021357 | 0.001128 | -0.0019333 | -0.0040845 | 0.0028027 | -55.2017 | 65.5426 | -57.3532 | 65.3046 | -56.6528 | -57.1564 | -56.4102 | -56.0989 | 65.5792 | -57.3166 | -57.3029 | -57.3257 | -57.4585 | -57.0969 | -0.064086 | -0.032043 | -0.27008 | 0.63629 | 0.87891 | 0.13275 | 0.94299 | 0.19684 | -0.027465 | 0.004578 | -122.8775 | -0.036621 | 0.19226 | -0.16937 | 0.21973 | -0.14191 | 0.70038 | 122.6578 | -0.009156 | 0.013733 | 122.8958 | 122.8958 | 122.8317 | 122.8683 | -122.9279 | -122.8912 | 122.5937 | -0.013732 | 2.0874 | 1.1902
1879.1719 | 122.9782 | -57.2662 | 65.5563 | -0.060578 | -0.00066014 | 0.06288 | 0.071395 | 0.0012284 | 0.0032599 | 0.0062762 | -0.071533 | 0.00046135 | 0.0019226 | 0.0030506 | -0.0012925 | -0.0021619 | -0.0033923 | -55.1514 | 65.5518 | -57.3303 | 65.3595 | -56.5659 | -57.0786 | -56.3599 | -56.0028 | 65.5838 | -57.2891 | -57.2296 | -57.2845 | -57.3853 | -57.0557 | -0.064087 | -0.004577 | -0.19684 | 0.70038 | 0.90637 | 0.18768 | 0.97046 | 0.25177 | -0.022889 | 0.027466 | -122.7859 | -0.018311 | 0.21057 | -0.11902 | 0.23346 | -0.09613 | 0.76447 | 122.6898 | 0.004578 | 0.05951 | 122.8821 | 122.8729 | 122.818 | 122.85 | -122.8867 | -122.8455 | 122.6257 | 0.036621 | 2.1149 | 1.2634
1880.1719 | 122.9645 | -57.2845 | 65.5518 | -0.29709 | 0.0019035 | 0.062239 | 0.073318 | 0.00037377 | 0.0019781 | 0.0062762 | -0.025757 | 0.0015295 | 0.00042723 | -0.00058098 | -0.00043791 | -0.0036573 | -0.0023243 | -55.2063 | 65.4739 | -57.399 | 65.3046 | -56.6666 | -57.1335 | -56.4285 | -56.0852 | 65.5746 | -57.3257 | -57.2662 | -57.3029 | -57.431 | -57.0877 | -0.11444 | -0.07782 | -0.24719 | 0.61798 | 0.85602 | 0.15106 | 0.97046 | 0.2655 | -0.041199 | 0.022888 | -122.818 | -0.01831 | 0.19684 | -0.14648 | 0.23804 | -0.10529 | 0.73242 | 122.7036 | 0.022889 | 0.05951 | 122.8729 | 122.9004 | 122.7585 | 122.8592 | -122.9507 | -122.8775 | 122.5891 | 0.018311 | 2.0782 | 1.1993
1881.1719 | 122.9507 | -57.2937 | 65.5563 | -0.1445 | 0.00019446 | 0.062666 | 0.074172 | 0.00016017 | 0.0013373 | 0.009267 | -0.11121 | 0.0017431 | 2.8e-08 | 0.003905 | 0.0012711 | -0.0019483 | -0.00040166 | -55.2567 | 65.5655 | -57.3624 | 65.2771 | -56.662 | -57.1976 | -56.5384 | -55.838 | 65.5838 | -57.3029 | -57.2845 | -57.3029 | -57.4402 | -57.0877 | -0.068665 | 0.009156 | -0.27923 | 0.63171 | 0.75531 | 0.09613 | 0.82398 | 0.16479 | -0.009155 | 0.027466 | -122.8409 | -0.009155 | 0.20599 | -0.14648 | 0.21515 | -0.13733 | 0.70038 | 122.6395 | 0 | 0.01831 | 122.9279 | 122.8867 | 122.8592 | 122.8775 | -122.9187 | -122.8592 | 122.5708 | 0.009155 | 2.037 | 1.4557
1882.1719 | 123.0148 | -57.2479 | 65.538 | -0.091095 | 0.00040806 | 0.060957 | 0.069045 | -0.0015488 | 0.0047553 | 0.0032856 | 0.026123 | 3.4148e-05 | 0.00021363 | -0.00079478 | -0.0017197 | -0.0025891 | 0.00088014 | -55.188 | 65.5334 | -57.3212 | 65.3549 | -56.5659 | -56.987 | -56.2134 | -56.0394 | 65.5563 | -57.2983 | -57.2113 | -57.2159 | -57.3166 | -57.0282 | -0.073242 | -0.004578 | -0.18311 | 0.68207 | 1.0345 | 0.26093 | 1.1078 | 0.33417 | -0.050354 | 0.01831 | -122.7493 | 0.032044 | 0.21973 | -0.068664 | 0.27008 | -0.01831 | 0.75531 | 122.6761 | 0.082398 | 0.086975 | 122.8546 | 122.8546 | 122.7814 | 122.8043 | -122.8592 | -122.8363 | 122.6028 | 0.036621 | 2.0599 | 1.2085
1883.1719 | 122.937 | -57.2937 | 65.5792 | -0.098725 | -0.00066014 | 0.063734 | 0.075667 | -0.0011214 | 0.00069649 | 0.0049946 | -0.044067 | 0.0013159 | -0.0012818 | 0.0030506 | 0.0014847 | -0.0017347 | -0.0014697 | -55.1971 | 65.538 | -57.3441 | 65.2771 | -56.6711 | -57.1655 | -56.4331 | -56.1081 | 65.6021 | -57.3212 | -57.2983 | -57.3441 | -57.4585 | -57.1106 | -0.050354 | -0.041199 | -0.30212 | 0.62256 | 0.8606 | 0.12817 | 0.91095 | 0.17853 | -0.027466 | 0.022888 | -122.8775 | -0.050354 | 0.1831 | -0.16479 | 0.21057 | -0.13733 | 0.67291 | 122.6212 | -0.022888 | 0.022888 | 122.8821 | 122.9233 | 122.8317 | 122.8958 | -122.9233 | -122.9004 | 122.5708 | -0.004578 | 2.0966 | 1.1856
1884.1719 | 122.9507 | -57.2845 | 65.5563 | -0.075836 | 0.0027579 | 0.062453 | 0.071609 | -0.0021896 | 0.0034735 | 0.0032856 | -0.041016 | 0.0023839 | 0.00085443 | 0.0049732 | -0.0017197 | -0.0047253 | -0.0012561 | -55.2338 | 65.5151 | -57.3715 | 65.2634 | -56.6757 | -57.1655 | -56.4331 | -56.0989 | 65.5838 | -57.3395 | -57.1106 | -57.2891 | -57.5043 | -57.1106 | -0.086975 | -0.041198 | -0.29297 | 0.60883 | 0.85144 | 0.11902 | 0.93842 | 0.20599 | -0.054932 | 0.027466 | -122.6669 | -0.004578 | 0.17395 | -0.21973 | 0.22888 | -0.16479 | 0.6958 | 122.6349 | 0.050354 | 0.22888 | 122.8867 | 122.9233 | 122.7997 | 122.8683 | -122.9279 | -122.8958 | 122.5479 | 0.17395 | 2.0508 | 1.1856
1885.1719 | 123.0515 | -57.2708 | 65.5151 | -0.068207 | -0.0013009 | 0.063094 | 0.071822 | 0.0010148 | 0.0028327 | 0.0064898 | -0.022705 | 0.0013159 | 0.00064083 | 0.0026232 | -0.0015061 | -0.0030163 | 2.554e-05 | -55.2383 | 65.5289 | -57.3486 | 65.332 | -56.6025 | -57.1426 | -56.3782 | -56.0211 | 65.5197 | -57.312 | -57.2113 | -57.2433 | -57.3532 | -57.0236 | -0.07782 | 0.013733 | -0.18311 | 0.66833 | 0.89264 | 0.12817 | 0.97046 | 0.20599 | -0.041199 | 0.004577 | -122.7264 | 0.027466 | 0.24719 | -0.082397 | 0.28839 | -0.041198 | 0.74616 | 122.6807 | 0.068665 | 0.10071 | 122.8775 | 122.8317 | 122.7997 | 122.7905 | -122.8638 | -122.8271 | 122.6028 | 0.059509 | 2.0325 | 1.2497
1886.1719 | 122.9324 | -57.2662 | 65.5655 | -0.13687 | 0.00019446 | 0.063734 | 0.073104 | 0.00080117 | 0.0030463 | 0.0077716 | -0.050171 | 0.00067495 | -0.00021357 | 0.0051868 | -0.00065151 | -0.0045117 | -0.00061526 | -55.2475 | 65.5426 | -57.3349 | 65.2908 | -56.6757 | -57.1747 | -56.4285 | -56.2546 | 65.5243 | -57.3349 | -57.2433 | -57.3257 | -57.4219 | -57.074 | -0.068665 | -0.022888 | -0.27466 | 0.59052 | 0.83771 | 0.091552 | 0.90637 | 0.16022 | -0.068665 | -0.041199 | -122.8088 | -0.05951 | 0.19226 | -0.15564 | 0.26093 | -0.086975 | 0.65918 | 122.6257 | 0.009155 | 0.091553 | 122.8775 | 122.8592 | 122.8088 | 122.7905 | -122.9004 | -122.9004 | 122.5571 | 0.022888 | 2.0187 | 1.0117
1887.1719 | 123.0606 | -57.225 | 65.5472 | -0.098725 | -0.0021555 | 0.062453 | 0.068832 | -0.0028304 | 0.0011237 | 0.0039264 | 0.093262 | 0.00024775 | 0.00064083 | 0.0034778 | -0.00086511 | -0.0053663 | -0.00082886 | -55.1926 | 65.5334 | -57.312 | 65.3915 | -56.5384 | -57.0328 | -56.3049 | -55.9433 | 65.5563 | -57.2617 | -57.1884 | -57.1793 | -57.2662 | -56.9733 | -0.086975 | -0.013733 | -0.15564 | 0.68665 | 0.9201 | 0.19226 | 1.0071 | 0.27924 | -0.036621 | 0.009155 | -122.7356 | 0.045777 | 0.25177 | -0.041198 | 0.28839 | -0.004577 | 0.77362 | 122.7036 | 0.082398 | 0.073242 | 122.8455 | 122.818 | 122.7585 | 122.7814 | -122.8592 | -122.8088 | 122.6166 | 0.036621 | 2.0325 | 1.2817
1888.1719 | 122.9645 | -57.2525 | 65.5701 | -0.098725 | 0.00062166 | 0.062453 | 0.072463 | -5.343e-05 | 0.0019781 | 0.0067036 | -0.047119 | 0.0011023 | 0.0029906 | -0.0033582 | -0.0017197 | -0.0015211 | 0.0010937 | -55.1788 | 65.5472 | -57.3578 | 65.3641 | -56.575 | -57.1198 | -56.3919 | -56.0165 | 65.5975 | -57.2845 | -57.2433 | -57.3029 | -57.399 | -57.0602 | -0.10529 | -0.022888 | -0.20599 | 0.67749 | 0.86059 | 0.13275 | 0.96588 | 0.23804 | -0.032044 | 0.027466 | -122.8134 | -0.050354 | 0.19226 | -0.14648 | 0.2243 | -0.11444 | 0.78278 | 122.7219 | -0.01831 | 0.041199 | 122.905 | 122.8821 | 122.7997 | 122.85 | -122.9279 | -122.8546 | 122.6166 | 0.009155 | 2.0737 | 1.236
1889.1719 | 122.9187 | -57.2937 | 65.5563 | -0.052948 | 0.0021171 | 0.062666 | 0.072463 | 0.0029374 | 0.0026191 | 0.002431 | -0.028809 | 0.00067495 | -0.00042717 | -0.0010084 | -0.0023605 | -0.0028027 | 0.00045294 | -55.1971 | 65.5426 | -57.3303 | 65.3046 | -56.6071 | -57.1243 | -56.4148 | -56.0486 | 65.5655 | -57.312 | -57.28 | -57.2983 | -57.4173 | -57.0786 | -0.036621 | -0.013732 | -0.25177 | 0.68664 | 0.87891 | 0.16937 | 0.91553 | 0.20599 | -0.018311 | 0.009156 | -122.8363 | -0.004578 | 0.21515 | -0.1236 | 0.23346 | -0.10528 | 0.72327 | 122.6349 | 0.013733 | 0.032044 | 122.8729 | 122.8775 | 122.8363 | 122.8592 | -122.8867 | -122.8683 | 122.5983 | 0.013733 | 2.0966 | 1.2451
1890.1719 | 122.9782 | -57.2708 | 65.5701 | -0.091095 | -1.9142e-05 | 0.063734 | 0.071609 | 0.0022964 | 0.0028327 | 0.0052082 | -0.037964 | 0.00046135 | 0.0012818 | 0.0036914 | -0.0032151 | -0.0017347 | 0.0032299 | -55.1743 | 65.5472 | -57.3349 | 65.3458 | -56.5796 | -57.1014 | -56.3644 | -56.012 | 65.6067 | -57.3074 | -57.2617 | -57.2983 | -57.4081 | -57.0786 | -0.064087 | -0.022888 | -0.2243 | 0.69122 | 0.90637 | 0.16937 | 0.97046 | 0.23346 | -0.036621 | 0.036621 | -122.8317 | -0.027466 | 0.19226 | -0.13733 | 0.22888 | -0.10071 | 0.75531 | 122.6807 | 0.009155 | 0.045776 | 122.8821 | 122.9141 | 122.818 | 122.8775 | -122.905 | -122.8775 | 122.6166 | 0.009155 | 2.0966 | 1.2588
1891.1719 | 122.9691 | -57.2571 | 65.5792 | -0.12924 | -1.9142e-05 | 0.061812 | 0.071822 | -0.00026703 | 0.0015509 | 0.0071308 | -0.016602 | -0.00017945 | 2.8e-08 | 5.9824e-05 | -0.0027877 | -0.0036573 | 0.00045294 | -55.1514 | 65.5655 | -57.3395 | 65.3641 | -56.5475 | -57.0786 | -56.3599 | -55.9845 | 65.593 | -57.3074 | -57.2296 | -57.2433 | -57.3532 | -57.0282 | -0.082398 | -0.013733 | -0.21515 | 0.70953 | 0.89722 | 0.17853 | 0.97962 | 0.26093 | -0.050354 | 0.013733 | -122.8088 | 0.013733 | 0.22888 | -0.09613 | 0.27924 | -0.045776 | 0.79193 | 122.7036 | 0.064087 | 0.07782 | 122.905 | 122.9004 | 122.8226 | 122.85 | -122.9187 | -122.8867 | 122.6212 | 0.027466 | 2.1057 | 1.2726
1892.1719 | 122.9736 | -57.2662 | 65.5655 | -0.068207 | 0.00062166 | 0.063307 | 0.070327 | 0.0016556 | 0.0028327 | 0.0081988 | -0.041016 | 0.00088875 | 0.00064083 | -0.0052808 | -0.0015061 | -0.0015211 | 0.0015209 | -55.2017 | 65.5426 | -57.3486 | 65.332 | -56.5933 | -57.1198 | -56.3965 | -56.0211 | 65.5884 | -57.3029 | -57.2571 | -57.2937 | -57.3853 | -57.0694 | -0.082398 | -0.022888 | -0.23346 | 0.67291 | 0.86975 | 0.14648 | 0.95215 | 0.22888 | -0.036621 | 0.022888 | -122.8226 | -0.027466 | 0.19684 | -0.11902 | 0.23346 | -0.082398 | 0.75531 | 122.6807 | 0.009155 | 0.045776 | 122.8912 | 122.8912 | 122.8088 | 122.8546 | -122.9141 | -122.8683 | 122.5983 | 0.009155 | 2.0645 | 1.2451
1893.1719 | 122.9919 | -57.2388 | 65.5884 | -0.052948 | -0.00087374 | 0.062239 | 0.071181 | 0.0016556 | 0.0015509 | 0.0084124 | 0.02002 | 0.0025975 | 0.0023498 | 0.001128 | -0.0030013 | -0.0021619 | 0.0025891 | -55.1651 | 65.5746 | -57.312 | 65.3595 | -56.5842 | -57.0602 | -56.369 | -56.012 | 65.6021 | -57.2662 | -57.2159 | -57.2296 | -57.3349 | -57.0236 | -0.073242 | -0.013733 | -0.22888 | 0.6546 | 0.86975 | 0.17853 | 0.94299 | 0.25177 | -0.027465 | 0.013733 | -122.8043 | 0.009156 | 0.21515 | -0.09613 | 0.24261 | -0.068665 | 0.72785 | 122.6715 | 0.036621 | 0.050354 | 122.8867 | 122.8683 | 122.8134 | 122.8409 | -122.9004 | -122.8546 | 122.5983 | 0.022889 | 2.0737 | 1.2268
1894.1719 | 122.9645 | -57.2525 | 65.6296 | -0.03006 | -0.0017281 | 0.06288 | 0.070327 | -0.0034714 | -0.00015811 | 0.0062762 | 0.071899 | 0.0011023 | 0.0023498 | 0.0015552 | -0.00065151 | -0.0045117 | 0.0036571 | -55.1239 | 65.5609 | -57.312 | 65.3778 | -56.5292 | -57.0328 | -56.3141 | -55.9937 | 65.6204 | -57.2754 | -57.2525 | -57.225 | -57.3395 | -57.0602 | -0.05951 | -0.068665 | -0.25177 | 0.72327 | 0.93841 | 0.21973 | 0.99793 | 0.27924 | -0.022889 | -0.009156 | -122.8821 | 0.027465 | 0.19226 | -0.086976 | 0.21515 | -0.064087 | 0.78278 | 122.6898 | 0.050354 | 0.022889 | 122.8729 | 122.8958 | 122.8134 | 122.8729 | -122.9416 | -122.905 | 122.6303 | 0 | 2.1286 | 1.2589
1895.1719 | 122.9462 | -57.2479 | 65.5609 | -0.083466 | -0.0015145 | 0.061171 | 0.071181 | 0.0010148 | 0.0028327 | 0.0037128 | -0.0074462 | -0.00060665 | -0.00042717 | 0.00048702 | -0.00043791 | -0.0025891 | 0.00045294 | -55.1514 | 65.5518 | -57.3441 | 65.3458 | -56.575 | -57.0831 | -56.3828 | -55.9799 | 65.5838 | -57.3029 | -57.2296 | -57.28 | -57.4036 | -57.0694 | -0.09613 | -0.009155 | -0.21515 | 0.67291 | 0.86517 | 0.1648 | 0.9613 | 0.26093 | -0.054931 | 0.022888 | -122.7905 | -0.032043 | 0.17853 | -0.15564 | 0.23346 | -0.10071 | 0.76904 | 122.6898 | 0.022888 | 0.073242 | 122.8958 | 122.8867 | 122.7997 | 122.8317 | -122.905 | -122.8638 | 122.5937 | 0.018311 | 2.0966 | 1.268
1896.1719 | 122.9874 | -57.2479 | 65.6021 | -0.060578 | -0.00087374 | 0.062666 | 0.071181 | 0.0020828 | 0.0021917 | 0.00414 | 0.016968 | 0.0025975 | 0.003418 | -0.0035718 | -1.0706e-05 | -0.0019483 | -0.0044605 | -55.1605 | 65.5884 | -57.3166 | 65.3366 | -56.5979 | -57.0831 | -56.3873 | -56.0165 | 65.625 | -57.2891 | -57.2433 | -57.2571 | -57.3532 | -57.0374 | -0.068664 | -0.013733 | -0.2655 | 0.65002 | 0.8606 | 0.1648 | 0.92926 | 0.23346 | -0.041199 | 0.022888 | -122.8455 | -0.009155 | 0.21057 | -0.10528 | 0.25177 | -0.064086 | 0.71869 | 122.6532 | 0.032044 | 0.045777 | 122.905 | 122.9141 | 122.8363 | 122.8729 | -122.9187 | -122.8912 | 122.5845 | 0.004578 | 2.0874 | 1.2314
1897.1719 | 122.9965 | -57.2433 | 65.5975 | -0.075836 | 0.0012625 | 0.063734 | 0.069259 | 0.0016556 | 0.0039007 | 0.0077716 | 0.016968 | 0.0017431 | -0.00021357 | 0.001128 | -0.00065151 | -0.0028027 | 0.0023755 | -55.1605 | 65.5746 | -57.312 | 65.3687 | -56.5613 | -57.0602 | -56.3599 | -55.9937 | 65.6158 | -57.2891 | -57.225 | -57.2296 | -57.3578 | -57.0236 | -0.068665 | -0.022888 | -0.22888 | 0.68207 | 0.88348 | 0.1831 | 0.95215 | 0.25177 | -0.045777 | 0.018311 | -122.8226 | 0.013733 | 0.21973 | -0.11444 | 0.2655 | -0.068664 | 0.75073 | 122.6807 | 0.05951 | 0.064087 | 122.8867 | 122.905 | 122.818 | 122.8592 | -122.9095 | -122.8867 | 122.612 | 0.01831 | 2.0828 | 1.2497
1898.1719 | 122.9507 | -57.225 | 65.6021 | -0.052948 | 0.00062166 | 0.062666 | 0.069472 | -0.0021896 | 0.0017645 | 0.0015766 | 0.016968 | 0.0011023 | 0.0032044 | 0.00091422 | -0.0019333 | -0.0040845 | -0.00061526 | -55.1926 | 65.6158 | -57.3257 | 65.419 | -56.6803 | -57.2754 | -56.4056 | -56.0761 | 65.593 | -57.3074 | -57.2479 | -57.2617 | -57.3761 | -57.0465 | -0.10071 | 0.013733 | -0.18311 | 0.54474 | 0.8194 | -0.050354 | 0.9201 | 0.050354 | -0.082397 | -0.009155 | -122.85 | -0.036621 | 0.17853 | -0.15106 | 0.26093 | -0.068665 | 0.64545 | 122.7448 | 0.045776 | 0.059509 | 122.9416 | 122.9004 | 122.8409 | 122.818 | -122.9279 | -122.9095 | 122.644 | -0.022888 | 2.0325 | 1.149
1899.1719 | 122.9507 | -57.2754 | 65.6021 | -0.068207 | -1.9142e-05 | 0.061812 | 0.07225 | 0.00080117 | 0.0036871 | 0.0079852 | 0.029175 | 0.0015295 | -0.00064077 | -0.0044262 | -0.00043791 | -0.0068615 | 0.00045294 | -55.1834 | 65.5884 | -57.2983 | 65.3366 | -56.5842 | -57.074 | -56.3644 | -56.044 | 65.6296 | -57.2937 | -57.1793 | -57.3715 | -57.5455 | -57.1198 | -0.022888 | -0.013733 | -0.2655 | 0.69122 | 0.91095 | 0.20142 | 0.93384 | 0.2243 | -0.01831 | 0.027466 | -122.7814 | -0.09613 | 0.15564 | -0.27008 | 0.17395 | -0.25177 | 0.71411 | 122.6349 | -0.07782 | 0.11444 | 122.8867 | 122.9233 | 122.8638 | 122.905 | -122.9004 | -122.8958 | 122.612 | 0.096131 | 2.092 | 1.2314
1900.1719 | 122.9507 | -57.2617 | 65.6021 | -0.075836 | -0.00066014 | 0.062025 | 0.070754 | -0.0021896 | 0.0028327 | 0.0045672 | 0.03833 | -0.00039305 | 0.00085443 | -0.0018628 | -0.0019333 | -0.0038709 | -0.00061526 | -55.1651 | 65.5792 | -57.3074 | 65.3778 | -56.5796 | -57.106 | -56.3553 | -56.0303 | 65.6113 | -57.28 | -57.2571 | -57.2617 | -57.3532 | -57.074 | -0.045776 | -0.022888 | -0.2243 | 0.68207 | 0.90637 | 0.15564 | 0.95215 | 0.20142 | -0.01831 | 0.009155 | -122.8592 | 0 | 0.18768 | -0.091552 | 0.20599 | -0.073242 | 0.72784 | 122.6852 | 0.01831 | 0.022888 | 122.8867 | 122.8912 | 122.8409 | 122.8729 | -122.9095 | -122.8821 | 122.6395 | 0.004578 | 2.0966 | 1.2314
1901.1719 | 122.9874 | -57.2433 | 65.6021 | -0.045319 | 0.00062166 | 0.063094 | 0.071181 | 0.00080117 | 0.0028327 | 0.0060626 | 0.035278 | -0.00082025 | 0.0014954 | -0.00079478 | -0.00065151 | -0.0036573 | 0.0023755 | -55.1331 | 65.5655 | -57.2937 | 65.3961 | -56.5338 | -57.0282 | -56.3095 | -55.9891 | 65.6113 | -57.2662 | -57.2342 | -57.2159 | -57.3303 | -57.0648 | -0.050354 | -0.036621 | -0.20599 | 0.70953 | 0.93384 | 0.21515 | 0.98419 | 0.2655 | -0.022888 | 0.009155 | -122.8363 | 0.027466 | 0.17853 | -0.086975 | 0.20142 | -0.064087 | 0.75989 | 122.6898 | 0.050354 | 0.032043 | 122.8592 | 122.8775 | 122.8088 | 122.8546 | -122.8958 | -122.8683 | 122.6395 | 0.009155 | 2.1103 | 1.2543
1902.1719 | 123.0606 | -57.225 | 65.5655 | -0.075836 | -0.00044654 | 0.062025 | 0.070327 | 0.0012284 | -0.0016535 | 0.0017902 | 0.062744 | -0.0010339 | -0.00064077 | -0.0027174 | -0.0012925 | -0.0051527 | -0.0014697 | -55.1056 | 65.5472 | -57.2617 | 65.657 | -56.575 | -57.3257 | -56.3095 | -55.9433 | 65.5655 | -57.2754 | -57.1747 | -57.1564 | -57.2388 | -56.9687 | -0.036621 | -0.018311 | 0.091552 | 0.65002 | 0.91553 | -0.10071 | 0.95215 | -0.064087 | -0.050354 | 0 | -122.7402 | 0.068665 | 0.25635 | -0.013733 | 0.3067 | 0.036621 | 0.68665 | 122.9187 | 0.11902 | 0.10071 | 122.8088 | 122.8409 | 122.7722 | 122.7905 | -122.8271 | -122.8409 | 122.8821 | 0.050354 | 2.1194 | 1.2817
1903.1719 | 123.0469 | -57.2296 | 65.5792 | -0.13687 | 0.0010489 | 0.061598 | 0.069045 | -0.001976 | 0.0030463 | 0.0067036 | 0.044434 | 0.00046135 | -0.0019226 | -0.002931 | -0.0032151 | -0.0036573 | -0.0018971 | -55.1147 | 65.5472 | -57.3074 | 65.451 | -56.4835 | -56.9824 | -56.282 | -55.9067 | 65.5975 | -57.2617 | -57.1838 | -57.1747 | -57.2617 | -56.9962 | -0.07782 | -0.032044 | -0.12817 | 0.74615 | 0.94757 | 0.24719 | 1.0254 | 0.32501 | -0.032044 | 0.01831 | -122.7631 | 0.054931 | 0.23346 | -0.032044 | 0.2655 | 0 | 0.82397 | 122.7585 | 0.086975 | 0.07782 | 122.8546 | 122.8592 | 122.7768 | 122.8271 | -122.8867 | -122.8409 | 122.6807 | 0.045776 | 2.1149 | 1.3229
1904.1719 | 122.9828 | -57.2388 | 65.6067 | -0.17502 | 0.00040806 | 0.061598 | 0.070968 | -0.0015488 | 0.0030463 | 0.0064898 | 0.032227 | 0.00024775 | -0.0014954 | 5.9824e-05 | -0.0032151 | -0.0038709 | 0.0013073 | -55.1147 | 65.5701 | -57.2983 | 65.4327 | -56.5109 | -57.0007 | -56.2866 | -55.9479 | 65.5792 | -57.2525 | -57.2021 | -57.2205 | -57.3257 | -57.0282 | -0.059509 | -0.036621 | -0.17395 | 0.72785 | 0.95215 | 0.23804 | 1.0117 | 0.29755 | -0.013732 | -0.027465 | -122.8088 | 0.018311 | 0.21057 | -0.086975 | 0.2243 | -0.073243 | 0.78735 | 122.731 | 0.032043 | 0.050354 | 122.8683 | 122.8317 | 122.8088 | 122.818 | -122.905 | -122.8592 | 122.6715 | 0.036622 | 2.124 | 1.2909
1905.1719 | 122.9691 | -57.28 | 65.6067 | 0.008087 | -0.00066014 | 0.062666 | 0.070327 | 0.00037377 | 0.0017645 | 0.0056354 | 0.02002 | 0.00088875 | 0.001709 | 0.0066822 | -0.0012925 | -0.0032301 | -0.00040166 | -55.1743 | 65.6067 | -57.3166 | 65.3366 | -56.6025 | -57.1014 | -56.2454 | -56.1859 | 65.625 | -57.3166 | -57.2571 | -57.2617 | -57.3624 | -57.0602 | -0.036621 | 0 | -0.27008 | 0.67749 | 1.0345 | 0.17853 | 1.0712 | 0.21515 | -0.036621 | 0.018311 | -122.8638 | 0.01831 | 0.21973 | -0.082398 | 0.25635 | -0.045777 | 0.71411 | 122.6532 | 0.054931 | 0.059509 | 122.9233 | 122.9416 | 122.8867 | 122.905 | -122.9233 | -122.9233 | 122.6166 | 0.022888 | 2.1057 | 1.0941
1906.1719 | 123.0194 | -57.2159 | 65.5975 | -0.060578 | 0.0016899 | 0.06288 | 0.071395 | 0.00058737 | 0.0021917 | 0.005849 | 0.050537 | -0.00082025 | 0.0023498 | -0.0014356 | -0.0010787 | -0.0055799 | -0.0031787 | -55.1193 | 65.5563 | -57.2983 | 65.419 | -56.5155 | -57.0007 | -56.2866 | -55.9616 | 65.6067 | -57.2433 | -57.2159 | -57.2113 | -57.3074 | -57.019 | -0.082398 | -0.041199 | -0.17853 | 0.70038 | 0.92926 | 0.21515 | 1.0117 | 0.29755 | -0.027466 | 0.009155 | -122.8134 | 0.004577 | 0.19684 | -0.091553 | 0.2243 | -0.064087 | 0.78278 | 122.7173 | 0.032043 | 0.027466 | 122.8546 | 122.85 | 122.7722 | 122.8226 | -122.8958 | -122.8409 | 122.6349 | 0 | 2.0966 | 1.2543
1907.1719 | 123.0377 | -57.2571 | 65.5563 | -0.15213 | 0.00040806 | 0.061598 | 0.0699 | -0.0015488 | 0.0017645 | 0.0073444 | 0.03833 | -0.00017945 | 0.0014954 | 0.002196 | -0.0010787 | -0.0038709 | -0.00061526 | -55.1651 | 65.5289 | -57.3349 | 65.3824 | -56.5613 | -57.0602 | -56.3187 | -55.9753 | 65.5701 | -57.28 | -57.1838 | -57.1747 | -57.28 | -57.0007 | -0.07782 | -0.027465 | -0.17395 | 0.6958 | 0.93841 | 0.19684 | 1.0162 | 0.27466 | -0.022888 | 0.013733 | -122.7402 | 0.082397 | 0.25635 | -0.022888 | 0.27924 | 0 | 0.77362 | 122.7173 | 0.10528 | 0.09613 | 122.8638 | 122.85 | 122.7859 | 122.8271 | -122.8912 | -122.8363 | 122.6395 | 0.073242 | 2.092 | 1.2817
1908.1719 | 123.0743 | -57.2205 | 65.5655 | -0.091095 | -0.00023294 | 0.063307 | 0.070113 | -0.0030442 | 0.0041143 | 0.005849 | 0.03833 | 0.0017431 | 0.00021363 | 5.9824e-05 | -0.00065151 | -0.0042981 | -0.0031787 | -55.1468 | 65.5334 | -57.3166 | 65.4053 | -56.5018 | -57.0236 | -56.2866 | -55.9296 | 65.5609 | -57.2571 | -57.1655 | -57.1472 | -57.2388 | -56.9687 | -0.09613 | -0.032044 | -0.16022 | 0.71869 | 0.93384 | 0.19684 | 1.03 | 0.29297 | -0.036621 | -0.004578 | -122.731 | 0.073242 | 0.25177 | -0.018311 | 0.28839 | 0.01831 | 0.81482 | 122.7219 | 0.10986 | 0.091553 | 122.85 | 122.818 | 122.7539 | 122.7814 | -122.8821 | -122.8226 | 122.6257 | 0.054932 | 2.0737 | 1.2909
1909.1719 | 123.0743 | -57.2113 | 65.5746 | -0.045319 | 0.00019446 | 0.063307 | 0.066909 | -0.0060348 | 0.0045417 | 0.0049946 | 0.023071 | 0.00067495 | 0.00064083 | 0.0032642 | -0.0030013 | -0.0051527 | -0.0012561 | -55.1147 | 65.5334 | -57.2845 | 65.2451 | -56.5155 | -56.8863 | -56.3049 | -55.8929 | 65.5655 | -57.2754 | -57.1335 | -57.1472 | -57.2433 | -56.9778 | -0.073242 | -0.041199 | -0.32959 | 0.6958 | 0.90637 | 0.32501 | 0.97961 | 0.39825 | -0.064087 | -0.009155 | -122.7081 | 0.064087 | 0.23346 | -0.032043 | 0.29755 | 0.032044 | 0.76904 | 122.5296 | 0.12817 | 0.14191 | 122.818 | 122.8409 | 122.7448 | 122.7768 | -122.8592 | -122.85 | 122.4564 | 0.07782 | 2.0966 | 1.3184
1910.1719 | 122.9462 | -57.2525 | 65.6113 | -0.091095 | -0.0015145 | 0.061171 | 0.07289 | -0.0017624 | 0.0028327 | 0.0064898 | -0.062378 | -0.00017945 | 0.00064083 | 0.0019824 | -0.0030013 | -0.0040845 | -0.0016833 | -55.1743 | 65.6067 | -57.3212 | 65.3183 | -56.3782 | -57.0694 | -56.488 | -56.0303 | 65.6067 | -57.3074 | -57.2479 | -57.2479 | -57.3532 | -57.0786 | -0.068665 | -0.004578 | -0.29297 | 0.87433 | 0.76447 | 0.1831 | 0.83313 | 0.25177 | -0.054932 | -0.004578 | -122.8592 | 0.004577 | 0.17395 | -0.10071 | 0.22888 | -0.045776 | 0.94299 | 122.6395 | 0.059509 | 0.059509 | 122.9279 | 122.9141 | 122.8592 | 122.8592 | -122.9324 | -122.9187 | 122.5708 | 0.004577 | 2.0782 | 1.2222
1911.1719 | 123.0652 | -57.2433 | 65.5655 | -0.15976 | -0.00044654 | 0.062025 | 0.071395 | -0.0011214 | 0.0043281 | 0.0026446 | 0.035278 | 0.00088875 | 0.0012818 | -0.0052808 | -1.0706e-05 | -0.0025891 | -0.0012561 | -55.1422 | 65.5151 | -57.3074 | 65.4282 | -56.5247 | -57.0099 | -56.2866 | -55.9341 | 65.5975 | -57.2708 | -57.1609 | -57.1609 | -57.2479 | -56.9733 | -0.064087 | -0.050354 | -0.13733 | 0.71869 | 0.95673 | 0.23346 | 1.0208 | 0.29755 | -0.027466 | 0.032043 | -122.7264 | 0.082397 | 0.27008 | -0.004578 | 0.29755 | 0.022888 | 0.78278 | 122.7356 | 0.10986 | 0.10986 | 122.8226 | 122.8683 | 122.7585 | 122.8409 | -122.8729 | -122.8363 | 122.6715 | 0.082397 | 2.1011 | 1.3092
1912.1719 | 123.1018 | -57.2388 | 65.5472 | -0.12161 | 0.00062166 | 0.060103 | 0.069472 | 0.00058737 | 0.0024053 | 0.0069172 | 0.035278 | 3.4148e-05 | -0.00064077 | 0.0041186 | 0.00084389 | -0.0055799 | -0.0025379 | -55.1193 | 65.5334 | -57.2937 | 65.4648 | -56.4514 | -56.9916 | -56.2729 | -55.8838 | 65.5701 | -57.2845 | -57.1472 | -57.1198 | -57.193 | -56.9504 | -0.054931 | -0.013733 | -0.082397 | 0.78735 | 0.96588 | 0.24719 | 1.0208 | 0.30212 | -0.045776 | 0.022888 | -122.6944 | 0.11902 | 0.28839 | 0.045777 | 0.33417 | 0.091553 | 0.84228 | 122.7585 | 0.16479 | 0.13733 | 122.8271 | 122.8546 | 122.7722 | 122.8088 | -122.8409 | -122.8317 | 122.7036 | 0.091553 | 2.1194 | 1.355
1913.1719 | 122.9324 | -57.2617 | 65.625 | -0.045319 | 0.0019035 | 0.061385 | 0.073958 | -0.00048063 | -0.00079891 | 0.0073444 | 0.001709 | 0.0011023 | 0.00021363 | -0.0042126 | -0.0017197 | -0.0038709 | -0.0038197 | -55.1422 | 65.5701 | -57.2845 | 65.3778 | -56.5613 | -57.0831 | -56.3644 | -56.012 | 65.6204 | -57.28 | -57.2479 | -57.2525 | -57.3441 | -57.0831 | -0.022888 | -0.054932 | -0.24719 | 0.70038 | 0.89722 | 0.17853 | 0.9201 | 0.20142 | -0.01831 | -0.004578 | -122.8729 | 0.009156 | 0.17853 | -0.082397 | 0.19684 | -0.064087 | 0.72327 | 122.6624 | 0.027466 | 0.032043 | 122.8546 | 122.9004 | 122.8317 | 122.8821 | -122.9095 | -122.905 | 122.6395 | 0.013733 | 2.1194 | 1.2497
1914.1719 | 123.0835 | -57.2342 | 65.5243 | -0.15213 | -0.00044654 | 0.061812 | 0.070113 | 0.0040054 | 0.0026191 | 0.0062762 | 0.044434 | 0.00024775 | -0.00085457 | -0.0020764 | -0.00065151 | -0.0040845 | -0.0031787 | -55.1422 | 65.5563 | -57.3029 | 65.4465 | -56.4926 | -57.019 | -56.3004 | -55.9067 | 65.5563 | -57.2617 | -57.1472 | -57.1335 | -57.2296 | -56.9733 | -0.068664 | 0.032043 | -0.07782 | 0.74158 | 0.93384 | 0.21515 | 1.0025 | 0.28381 | -0.027466 | 0.032043 | -122.6715 | 0.10071 | 0.26093 | 0.004578 | 0.28839 | 0.032044 | 0.81024 | 122.7493 | 0.12817 | 0.11444 | 122.8592 | 122.818 | 122.7905 | 122.7905 | -122.8271 | -122.7859 | 122.6807 | 0.086975 | 2.092 | 1.3275
1915.1719 | 123.1613 | -57.2021 | 65.5655 | -0.083466 | 0.0014761 | 0.060744 | 0.070113 | -0.0015488 | 0.0045417 | 0.005849 | 0.053589 | 0.00046135 | -0.0010682 | -0.0033582 | -0.0012925 | -0.0064343 | -0.0038197 | -55.1056 | 65.5426 | -57.3029 | 65.4831 | -56.4514 | -56.9687 | -56.25 | -55.8701 | 65.5838 | -57.2525 | -57.1472 | -57.1289 | -57.1609 | -56.8405 | -0.10071 | -0.022888 | -0.082398 | 0.75073 | 0.95215 | 0.23346 | 1.0529 | 0.33417 | -0.050354 | 0.01831 | -122.7127 | 0.073242 | 0.36163 | 0.041198 | 0.41199 | 0.091552 | 0.85144 | 122.7859 | 0.1236 | 0.10529 | 122.8455 | 122.8363 | 122.7448 | 122.7859 | -122.8683 | -122.818 | 122.6852 | 0.054931 | 2.0966 | 1.3321
1916.1719 | 123.0789 | -57.2433 | 65.5334 | -0.083466 | -1.9142e-05 | 0.062239 | 0.071609 | 0.001442 | 0.0021917 | 0.0045672 | 0.041382 | 0.00067495 | 0.00021363 | 0.002196 | -0.0017197 | -0.0038709 | 0.0017345 | -55.1605 | 65.538 | -57.3166 | 65.4144 | -56.5292 | -57.019 | -56.2912 | -55.9479 | 65.5884 | -57.2617 | -57.1564 | -57.1609 | -57.2525 | -56.9778 | -0.073242 | 0.004578 | -0.11902 | 0.71411 | 0.95215 | 0.2243 | 1.0254 | 0.29755 | -0.018311 | 0.054932 | -122.6898 | 0.082397 | 0.2655 | -0.009155 | 0.28381 | 0.009156 | 0.78735 | 122.731 | 0.10071 | 0.10529 | 122.8546 | 122.85 | 122.7814 | 122.8317 | -122.85 | -122.7951 | 122.6578 | 0.086975 | 2.0828 | 1.2955
1917.1719 | 123.111 | -57.225 | 65.5518 | -0.068207 | -0.00066014 | 0.062666 | 0.069259 | -0.0045394 | 0.0034735 | 0.0052082 | 0.023071 | 0.0011023 | 0.00085443 | 0.0036914 | -0.0030013 | -0.0045117 | 0.0013073 | -55.1193 | 65.5289 | -57.3029 | 65.4602 | -56.4468 | -56.9733 | -56.2729 | -55.8701 | 65.5746 | -57.2845 | -57.1335 | -57.1243 | -57.2113 | -56.955 | -0.077819 | -0.022888 | -0.091553 | 0.7782 | 0.95215 | 0.25177 | 1.03 | 0.32959 | -0.059509 | 0.022888 | -122.6852 | 0.10071 | 0.27008 | 0.013733 | 0.32959 | 0.073242 | 0.85602 | 122.7631 | 0.16022 | 0.15106 | 122.8317 | 122.8592 | 122.7539 | 122.7997 | -122.8546 | -122.8363 | 122.6852 | 0.091553 | 2.1057 | 1.355
1918.1719 | 123.0789 | -57.2067 | 65.5655 | -0.075836 | 0.0012625 | 0.064589 | 0.070113 | -0.0056076 | 0.0019781 | 0.0056354 | -0.080688 | -0.00082025 | -0.001709 | 0.0017688 | -0.0019333 | -0.0057935 | -0.0036059 | -55.0964 | 65.5563 | -57.312 | 65.4648 | -56.3599 | -56.575 | -56.218 | -55.8289 | 65.5792 | -57.2708 | -57.1701 | -57.1152 | -57.2296 | -56.9641 | -0.10529 | -0.009156 | -0.10071 | 0.84686 | 0.98877 | 0.63171 | 1.0941 | 0.737 | -0.064087 | 0.013733 | -122.7356 | 0.091553 | 0.24262 | -0.022888 | 0.3067 | 0.041199 | 0.95215 | 122.7768 | 0.15564 | 0.10071 | 122.8683 | 122.85 | 122.7631 | 122.7859 | -122.8775 | -122.8363 | 122.6715 | 0.036621 | 2.1103 | 1.3779
1919.1719 | 123.0606 | -57.2113 | 65.5838 | -0.068207 | -0.00087374 | 0.061812 | 0.0699 | 0.00058737 | 0.0045417 | 0.0026446 | 0.0078126 | 0.0019567 | 0.00064083 | 0.0028368 | -0.0012925 | -0.0042981 | 0.00023934 | -55.1239 | 65.5334 | -57.2983 | 65.451 | -56.4972 | -57.0053 | -56.282 | -55.9341 | 65.5975 | -57.2662 | -57.1701 | -57.1655 | -57.2754 | -56.9778 | -0.086975 | -0.050354 | -0.13275 | 0.71411 | 0.92926 | 0.20599 | 1.0162 | 0.29297 | -0.054931 | 0.013733 | -122.7539 | 0.045777 | 0.23346 | -0.064087 | 0.28839 | -0.009156 | 0.80109 | 122.7493 | 0.10071 | 0.09613 | 122.8317 | 122.8638 | 122.7448 | 122.8088 | -122.8821 | -122.85 | 122.6624 | 0.041199 | 2.0874 | 1.2772
1920.1719 | 123.0423 | -57.2159 | 65.5838 | -0.091095 | -1.9142e-05 | 0.066725 | 0.070113 | -0.001976 | 0.0017645 | 0.0067036 | 0.013916 | 0.0011023 | -0.0019226 | 0.0071094 | -0.0030013 | -0.0036573 | -0.0021107 | -55.101 | 65.5518 | -57.2937 | 65.451 | -56.5063 | -57.0007 | -56.2775 | -55.9113 | 65.5792 | -57.2433 | -57.1609 | -57.1747 | -57.2571 | -56.9824 | -0.07782 | -0.032043 | -0.13275 | 0.70953 | 0.93842 | 0.21515 | 1.0162 | 0.29297 | -0.027466 | -0.004577 | -122.7448 | 0.041198 | 0.23346 | -0.041199 | 0.26093 | -0.013733 | 0.78735 | 122.7448 | 0.068664 | 0.082397 | 122.8455 | 122.8226 | 122.7676 | 122.7951 | -122.8775 | -122.8271 | 122.6669 | 0.054931 | 2.1149 | 1.3046
1921.1719 | 123.0743 | -57.2342 | 65.5563 | -0.075836 | -0.00023294 | 0.059676 | 0.07289 | 0.0016556 | 5.5488e-05 | 0.0064898 | 0.016968 | -0.0016749 | -0.001709 | -0.0059216 | -0.0012925 | -0.0034437 | -0.0012561 | -55.1376 | 65.5151 | -57.3166 | 65.4282 | -56.5201 | -57.0236 | -56.2958 | -55.9296 | 65.5518 | -57.2525 | -57.1381 | -57.1426 | -57.2479 | -56.9733 | -0.082397 | -0.041198 | -0.12817 | 0.71411 | 0.93842 | 0.21057 | 1.0208 | 0.29297 | -0.01831 | -0.004577 | -122.6944 | 0.091553 | 0.26093 | -0.013733 | 0.27923 | 0.004577 | 0.79651 | 122.7448 | 0.10986 | 0.11444 | 122.8317 | 122.8043 | 122.7493 | 122.786 | -122.8729 | -122.8088 | 122.6624 | 0.09613 | 2.0966 | 1.3046
1922.1719 | 123.0927 | -57.2205 | 65.5792 | -0.022431 | 0.00062166 | 0.060957 | 0.070754 | -0.0017624 | 0.00091009 | 0.0067036 | 0.016968 | 0.00024775 | -0.00064077 | 0.0079638 | -0.0017197 | -0.0023755 | 0.0023755 | -55.1102 | 65.5472 | -57.2937 | 65.4556 | -56.4423 | -56.9595 | -56.2546 | -55.8655 | 65.5746 | -57.2617 | -57.1426 | -57.1289 | -57.2342 | -56.9458 | -0.073242 | -0.032044 | -0.1236 | 0.7782 | 0.96588 | 0.26093 | 1.0391 | 0.33417 | -0.041199 | -0.004578 | -122.7219 | 0.091553 | 0.27466 | -0.013733 | 0.31586 | 0.027466 | 0.85144 | 122.7493 | 0.13275 | 0.11902 | 122.8409 | 122.8363 | 122.7676 | 122.7951 | -122.8729 | -122.8409 | 122.6761 | 0.07782 | 2.1103 | 1.355
1923.1719 | 123.111 | -57.2113 | 65.5289 | -0.075836 | 0.00040806 | 0.062025 | 0.070113 | 0.00016017 | 0.0028327 | 0.0039264 | 0.010864 | -0.0014613 | -0.00064077 | -0.0025036 | -0.0019333 | -0.0034437 | -0.00018806 | -55.1147 | 65.5243 | -57.3166 | 65.4556 | -56.4743 | -56.9916 | -56.2637 | -55.8609 | 65.5746 | -57.2571 | -57.1289 | -57.1014 | -57.2113 | -56.9458 | -0.10529 | -0.004578 | -0.073243 | 0.737 | 0.94757 | 0.21973 | 1.0529 | 0.32501 | -0.045776 | 0.045776 | -122.6578 | 0.10986 | 0.2655 | 0 | 0.31128 | 0.045776 | 0.84229 | 122.7722 | 0.15564 | 0.12817 | 122.8409 | 122.8317 | 122.7356 | 122.7859 | -122.8455 | -122.7859 | 122.6669 | 0.082398 | 2.0966 | 1.3504
1924.1719 | 123.0423 | -57.2296 | 65.5563 | -0.083466 | 0.0014761 | 0.063094 | 0.068832 | -0.0032578 | 0.0013373 | 0.0047808 | 0.013916 | 0.00088875 | -0.0012818 | -0.0050672 | -1.0706e-05 | -0.0064343 | -0.0036059 | -55.1422 | 65.5289 | -57.3074 | 65.4144 | -56.5384 | -57.0328 | -56.3004 | -55.9616 | 65.5655 | -57.2983 | -57.1609 | -57.1609 | -57.2662 | -56.9778 | -0.07782 | -0.027465 | -0.14191 | 0.69122 | 0.92926 | 0.19684 | 1.0071 | 0.27466 | -0.068665 | 0.009156 | -122.7173 | 0.068664 | 0.25177 | -0.036621 | 0.32044 | 0.032044 | 0.76904 | 122.7219 | 0.13733 | 0.13733 | 122.8363 | 122.8638 | 122.7585 | 122.7951 | -122.8638 | -122.8546 | 122.644 | 0.068664 | 2.0874 | 1.268
1925.1719 | 122.9553 | -57.2525 | 65.5975 | 0.038605 | -0.00044654 | 0.061812 | 0.074599 | 0.004219 | -0.00037171 | 0.00414 | -0.050171 | 0.0013159 | 0.00064083 | 0.0047594 | -0.0019333 | -0.0032301 | -0.0025379 | -55.2567 | 65.6204 | -57.3257 | 65.3458 | -56.6299 | -57.0923 | -56.3965 | -56.0532 | 65.6342 | -57.2891 | -57.2433 | -57.2479 | -57.3669 | -57.0511 | -0.073243 | 0.022888 | -0.25177 | 0.62256 | 0.85602 | 0.16022 | 0.92926 | 0.23346 | -0.036622 | 0.036621 | -122.8409 | 0.004577 | 0.20142 | -0.11444 | 0.23804 | -0.077819 | 0.6958 | 122.6715 | 0.041199 | 0.045777 | 122.9462 | 122.9233 | 122.8729 | 122.8867 | -122.9233 | -122.8867 | 122.5983 | 0.009155 | 1.9958 | 1.1993
1926.1719 | 123.0789 | -57.2296 | 65.5655 | -0.052948 | -0.00044654 | 0.062239 | 0.071609 | 0.00080117 | 0.0028327 | 0.0060626 | -0.016602 | 0.00046135 | 2.8e-08 | 0.0030506 | -0.0023605 | -0.0047253 | -0.0031787 | -55.1102 | 65.5563 | -57.2845 | 65.4327 | -56.1493 | -56.8176 | -56.4972 | -55.8655 | 65.5746 | -57.2754 | -57.1335 | -57.1243 | -57.2525 | -56.955 | -0.054932 | -0.009156 | -0.13275 | 1.0803 | 0.73242 | 0.41199 | 0.78735 | 0.46692 | -0.045777 | 0.009155 | -122.699 | 0.10528 | 0.27466 | -0.022888 | 0.32043 | 0.022889 | 1.1353 | 122.7173 | 0.15106 | 0.14191 | 122.8409 | 122.85 | 122.7859 | 122.8043 | -122.85 | -122.8409 | 122.6624 | 0.09613 | 2.1194 | 1.3641
1927.1719 | 123.0331 | -57.2342 | 65.5472 | -0.083466 | 0.0014761 | 0.061385 | 0.072036 | -0.00090783 | 0.0034735 | 0.0043536 | 0.010864 | 3.4148e-05 | 0.0019226 | -0.0042126 | -0.0017197 | -0.0047253 | 0.0028027 | -55.1651 | 65.5106 | -57.3303 | 65.4053 | -56.5567 | -57.0465 | -56.3187 | -55.9662 | 65.5701 | -57.2708 | -57.1701 | -57.1564 | -57.28 | -56.987 | -0.09613 | -0.036621 | -0.14191 | 0.67749 | 0.91553 | 0.18768 | 1.0117 | 0.28381 | -0.036621 | 0.022888 | -122.7173 | 0.07782 | 0.24719 | -0.045776 | 0.28381 | -0.009155 | 0.77362 | 122.7356 | 0.11444 | 0.10071 | 122.8409 | 122.8409 | 122.7448 | 122.8043 | -122.8775 | -122.818 | 122.6395 | 0.064087 | 2.0691 | 1.268
1928.1719 | 123.024 | -57.2342 | 65.5472 | -0.022431 | 0.0029715 | 0.061812 | 0.073531 | -5.343e-05 | 0.0017645 | 0.0060626 | 0.0047608 | 0.0015295 | -0.00042717 | -0.0044262 | -0.0021469 | -0.0038709 | -0.0021107 | -55.1788 | 65.5197 | -57.3074 | 65.3824 | -56.5613 | -57.0786 | -56.3553 | -56.0074 | 65.5655 | -57.2845 | -57.2067 | -57.2388 | -57.3212 | -57.0099 | -0.073242 | -0.027466 | -0.16479 | 0.67291 | 0.87891 | 0.15564 | 0.95215 | 0.22888 | -0.050354 | 0.018311 | -122.7539 | -0.004578 | 0.2243 | -0.086975 | 0.27466 | -0.036621 | 0.74616 | 122.6898 | 0.045776 | 0.07782 | 122.8271 | 122.85 | 122.7539 | 122.7997 | -122.8546 | -122.8317 | 122.6166 | 0.027466 | 2.0554 | 1.2268
1929.1719 | 123.0469 | -57.2342 | 65.5609 | -0.098725 | 0.0021171 | 0.061171 | 0.071181 | 0.00251 | 0.0015509 | 0.0067036 | -0.016602 | 0.0011023 | 0.00042723 | 0.00048702 | -0.0030013 | -0.0017347 | -0.00061526 | -55.1651 | 65.5197 | -57.3212 | 65.3915 | -56.543 | -57.0374 | -56.3324 | -55.9708 | 65.5792 | -57.2845 | -57.1655 | -57.1701 | -57.2754 | -56.987 | -0.086975 | -0.041199 | -0.16937 | 0.69122 | 0.90179 | 0.19684 | 0.98877 | 0.28381 | -0.050354 | 0.018311 | -122.7264 | 0.064087 | 0.24719 | -0.041199 | 0.29755 | 0.009155 | 0.7782 | 122.7127 | 0.11444 | 0.11902 | 122.8409 | 122.8638 | 122.7539 | 122.8134 | -122.8821 | -122.8455 | 122.6257 | 0.068665 | 2.0691 | 1.2634
1930.1719 | 122.9462 | -57.2571 | 65.6342 | -0.083466 | 0.00019446 | 0.062453 | 0.073104 | 0.0072098 | 0.0019781 | 0.005849 | -0.06543 | 0.00088875 | 0.00021363 | -0.00229 | -0.0010787 | -0.0045117 | 2.554e-05 | -55.1651 | 65.593 | -57.2983 | 65.3549 | -56.6208 | -57.1518 | -56.4056 | -56.044 | 65.6342 | -57.2845 | -57.2388 | -57.2617 | -57.3624 | -57.0557 | -0.041199 | -0.041198 | -0.27924 | 0.63629 | 0.85144 | 0.10529 | 0.89264 | 0.14648 | -0.027466 | 0 | -122.8729 | -0.004578 | 0.20142 | -0.10529 | 0.22888 | -0.07782 | 0.67749 | 122.6532 | 0.022888 | 0.045776 | 122.8912 | 122.9187 | 122.85 | 122.8912 | -122.9324 | -122.9187 | 122.612 | 0.01831 | 2.092 | 1.2131
1931.1719 | 122.937 | -57.2479 | 65.5975 | -0.060578 | -1.9142e-05 | 0.06288 | 0.072463 | 0.0022964 | 0.00069649 | 0.0056354 | -0.0013428 | 0.0011023 | 0.0019226 | 0.0030506 | -0.0030013 | -0.0032301 | 0.0025891 | -55.1559 | 65.5701 | -57.3303 | 65.3778 | -56.5979 | -57.0786 | -56.369 | -56.0394 | 65.625 | -57.2845 | -57.2433 | -57.2388 | -57.3624 | -57.0602 | -0.082397 | -0.027466 | -0.21973 | 0.65002 | 0.87891 | 0.16937 | 0.9613 | 0.25177 | -0.036621 | 0.027466 | -122.8409 | 0.009155 | 0.18768 | -0.11444 | 0.2243 | -0.07782 | 0.73242 | 122.7081 | 0.045776 | 0.041199 | 122.9004 | 122.9095 | 122.818 | 122.8729 | -122.9279 | -122.8821 | 122.6257 | 0.004578 | 2.092 | 1.2085
1932.1719 | 123.0606 | -57.2113 | 65.5701 | -0.068207 | 0.00062166 | 0.060744 | 0.073104 | -0.0030442 | 0.0041143 | 0.0022174 | 0.032227 | -0.00060665 | 0.00085443 | 0.00091422 | -0.0010787 | -0.0042981 | -0.0025379 | -55.1056 | 65.538 | -57.2754 | 65.3595 | -56.4056 | -57.0099 | -56.3278 | -55.925 | 65.5563 | -57.2525 | -57.1426 | -57.1289 | -57.2617 | -56.9595 | -0.064087 | -0.032043 | -0.21057 | 0.80566 | 0.88348 | 0.20142 | 0.94757 | 0.2655 | -0.041198 | -0.013733 | -122.7127 | 0.082398 | 0.25177 | -0.050354 | 0.29297 | -0.009156 | 0.86975 | 122.6349 | 0.1236 | 0.10986 | 122.8134 | 122.8088 | 122.7493 | 122.7676 | -122.8455 | -122.8226 | 122.5708 | 0.068665 | 2.1057 | 1.2863
1933.1719 | 123.056 | -57.2067 | 65.5792 | -0.098725 | -0.0015145 | 0.062666 | 0.070541 | 0.0010148 | 0.0026191 | 0.0073444 | 0.023071 | 0.00024775 | -0.00021357 | -0.0031446 | -0.0019333 | -0.0051527 | -0.00040166 | -54.9637 | 65.6021 | -57.2754 | 65.4236 | -56.4789 | -57.0145 | -56.2958 | -55.925 | 65.5792 | -57.2617 | -57.1381 | -57.1472 | -57.2433 | -56.9595 | -0.068665 | 0.022888 | -0.15564 | 0.72784 | 0.91095 | 0.19226 | 0.97962 | 0.26093 | -0.054932 | 0 | -122.7173 | 0.059509 | 0.24719 | -0.036621 | 0.30212 | 0.018311 | 0.79651 | 122.699 | 0.11444 | 0.1236 | 122.8775 | 122.8409 | 122.8088 | 122.7859 | -122.8546 | -122.8409 | 122.6303 | 0.068664 | 2.243 | 1.2817
1934.1719 | 122.9507 | -57.2388 | 65.6067 | -0.098725 | 0.0029715 | 0.062239 | 0.071822 | 0.0061416 | 0.0028327 | 0.0064898 | -0.016602 | 0.0015295 | 0.00085443 | 0.0019824 | -0.0017197 | -0.0034437 | 0.0021619 | -55.1147 | 65.5563 | -57.3074 | 65.4007 | -56.5338 | -57.0374 | -56.3232 | -55.9937 | 65.6113 | -57.2662 | -57.2296 | -57.2205 | -57.3166 | -57.0374 | -0.068664 | -0.050354 | -0.20599 | 0.70496 | 0.91553 | 0.20142 | 0.98419 | 0.27008 | -0.027465 | 0.004578 | -122.8363 | 0.018311 | 0.20142 | -0.077819 | 0.22888 | -0.050354 | 0.77362 | 122.7081 | 0.045776 | 0.036621 | 122.8638 | 122.8775 | 122.7951 | 122.85 | -122.9141 | -122.8729 | 122.6395 | 0.009156 | 2.124 | 1.2451
1935.1719 | 123.0011 | -57.2662 | 65.5746 | -0.10635 | 0.0027579 | 0.065871 | 0.074599 | 0.0072098 | 0.00048269 | 0.0067036 | -0.077637 | 0.00067495 | 0.001068 | -0.00036738 | -0.0010787 | -0.0023755 | -0.00040166 | -55.1376 | 65.5746 | -57.3257 | 65.4419 | -56.5338 | -57.074 | -56.3828 | -55.9799 | 65.6021 | -57.2845 | -57.2021 | -57.2388 | -57.3532 | -57.0374 | -0.05951 | 0 | -0.13275 | 0.73242 | 0.88348 | 0.19226 | 0.94299 | 0.25177 | -0.018311 | 0.027466 | -122.7768 | 0.027465 | 0.22888 | -0.086975 | 0.24719 | -0.068664 | 0.79193 | 122.7676 | 0.045776 | 0.082398 | 122.9004 | 122.8867 | 122.8409 | 122.8683 | -122.9004 | -122.8592 | 122.7081 | 0.064087 | 2.1286 | 1.2863
1936.1719 | 123.0194 | -57.2342 | 65.593 | -0.052948 | 0.00040806 | 0.06288 | 0.068832 | 0.0052872 | 0.00026909 | 0.0049946 | 0.02002 | 0.00024775 | 0.0021362 | -0.0014356 | 0.00063009 | -0.0042981 | -0.0023243 | -55.101 | 65.5701 | -57.3074 | 65.4419 | -56.488 | -57.0053 | -56.3095 | -55.9341 | 65.5975 | -57.2708 | -57.1838 | -57.1838 | -57.2525 | -56.9778 | -0.073242 | -0.022889 | -0.15106 | 0.74616 | 0.92468 | 0.22888 | 0.99793 | 0.30212 | -0.036621 | 0.004577 | -122.7768 | 0.050354 | 0.25635 | -0.01831 | 0.29297 | 0.018311 | 0.8194 | 122.7493 | 0.086975 | 0.086975 | 122.8775 | 122.8683 | 122.8043 | 122.8317 | -122.9004 | -122.8638 | 122.6761 | 0.050354 | 2.1332 | 1.3
1937.1719 | 122.9645 | -57.2525 | 65.5792 | -0.052948 | 0.0019035 | 0.06053 | 0.071395 | -0.00026703 | 0.0021917 | 0.007558 | -0.019653 | 0.0015295 | 0.001709 | 0.0060412 | -0.0021469 | -0.0049389 | 0.00045294 | -55.0095 | 65.6479 | -57.2754 | 65.3046 | -56.6345 | -57.1014 | -56.3919 | -56.0577 | 65.6158 | -57.2937 | -57.2388 | -57.2525 | -57.3624 | -57.0465 | -0.022889 | 0.068664 | -0.27466 | 0.61798 | 0.86059 | 0.15106 | 0.88348 | 0.17395 | -0.041199 | 0.036621 | -122.818 | 0 | 0.20599 | -0.10986 | 0.24719 | -0.068665 | 0.64087 | 122.58 | 0.041199 | 0.054931 | 122.9233 | 122.9095 | 122.9004 | 122.8683 | -122.8546 | -122.8729 | 122.5571 | 0.013732 | 2.243 | 1.1948
1938.1719 | 122.9645 | -57.2479 | 65.5792 | -0.037689 | 0.0010489 | 0.063521 | 0.072036 | 0.0018692 | 0.0030463 | 0.0064898 | -0.010498 | 0.0017431 | 0.0014954 | 0.0030506 | -0.0017197 | -0.0032301 | -0.0031787 | -55.1971 | 65.5884 | -57.3349 | 65.3549 | -56.6116 | -57.1106 | -56.4102 | -56.0394 | 65.6158 | -57.2891 | -57.2342 | -57.2479 | -57.3578 | -57.0511 | -0.086975 | 0.009155 | -0.22431 | 0.63629 | 0.83771 | 0.13733 | 0.92468 | 0.2243 | -0.041199 | 0.036621 | -122.8134 | 0 | 0.19684 | -0.10986 | 0.23804 | -0.068664 | 0.72327 | 122.6898 | 0.041199 | 0.054932 | 122.9233 | 122.905 | 122.8363 | 122.8638 | -122.9141 | -122.8683 | 122.6028 | 0.013733 | 2.0508 | 1.2085
1939.1719 | 122.9965 | -57.2708 | 65.5609 | -0.075836 | 0.0016899 | 0.062239 | 0.071822 | 0.0018692 | 0.0034735 | 0.005849 | -0.01355 | 0.0025975 | 0.00042723 | 0.0062548 | -0.0017197 | -0.0023755 | -0.0044605 | -55.1376 | 65.5655 | -57.3257 | 65.3778 | -56.5704 | -57.2296 | -56.488 | -55.9753 | 65.6021 | -57.2845 | -57.1976 | -57.2342 | -57.3486 | -57.0236 | -0.054932 | 0.004578 | -0.1831 | 0.70038 | 0.78278 | 0.041199 | 0.83771 | 0.096131 | -0.013733 | 0.041199 | -122.7585 | 0.036621 | 0.24719 | -0.07782 | 0.26093 | -0.064087 | 0.75531 | 122.7036 | 0.050354 | 0.086975 | 122.8912 | 122.8867 | 122.8363 | 122.8729 | -122.8867 | -122.8455 | 122.6486 | 0.073242 | 2.1332 | 1.2955
1940.1719 | 123.0057 | -57.2662 | 65.6021 | -0.098725 | 0.00062166 | 0.063521 | 0.070968 | -0.00026703 | 0.0041143 | 0.0064898 | -0.022705 | 0.00067495 | 0.0029906 | -0.0027174 | -0.00065151 | -0.0013073 | 0.00088014 | -55.1559 | 65.6021 | -57.3212 | 65.3549 | -56.6162 | -57.0831 | -56.3873 | -56.0303 | 65.6158 | -57.2937 | -57.2342 | -57.2296 | -57.3395 | -57.0328 | -0.054932 | 0 | -0.24719 | 0.65002 | 0.87891 | 0.18311 | 0.93384 | 0.23804 | -0.027466 | 0.013733 | -122.8363 | 0.036621 | 0.23346 | -0.073243 | 0.26093 | -0.045777 | 0.70496 | 122.6761 | 0.064087 | 0.059509 | 122.9233 | 122.9095 | 122.8683 | 122.8821 | -122.9233 | -122.8958 | 122.6212 | 0.032043 | 2.1103 | 1.236
1941.1719 | 122.9553 | -57.2571 | 65.5975 | -0.0071715 | -0.00066014 | 0.061598 | 0.070541 | -0.0038986 | 0.0028327 | 0.0073444 | -0.010498 | 3.4148e-05 | 0.001709 | -0.0014356 | -0.00065151 | -0.0055799 | 0.00023934 | -55.1697 | 65.6296 | -57.3074 | 65.2313 | -56.7444 | -57.0465 | -56.4239 | -56.0394 | 65.6479 | -57.2983 | -57.2662 | -57.2479 | -57.3578 | -57.0465 | -0.050354 | 0.032044 | -0.36621 | 0.5127 | 0.83313 | 0.21057 | 0.88348 | 0.26093 | -0.041199 | 0.050354 | -122.8638 | 0.009155 | 0.21057 | -0.10071 | 0.25177 | -0.059509 | 0.56305 | 122.5388 | 0.050354 | 0.032044 | 122.937 | 122.9462 | 122.8867 | 122.905 | -122.905 | -122.8958 | 122.4884 | -0.009155 | 2.0874 | 1.2177
1942.1719 | 122.9645 | -57.2479 | 65.5884 | -0.083466 | -0.00023294 | 0.060316 | 0.069686 | 0.00080117 | 0.00069649 | 0.007558 | 0.0078126 | 0.0023839 | 0.00042723 | -0.0016492 | -1.0706e-05 | -0.0038709 | -0.0025379 | -55.0827 | 65.6387 | -57.2845 | 65.2908 | -56.6208 | -57.0923 | -56.4011 | -56.0532 | 65.6204 | -57.2754 | -57.2296 | -57.2617 | -57.3669 | -57.0419 | -0.036621 | 0.050354 | -0.29755 | 0.62714 | 0.84686 | 0.15564 | 0.88348 | 0.19226 | -0.027466 | 0.032043 | -122.818 | -0.013733 | 0.20599 | -0.11902 | 0.23346 | -0.091552 | 0.66376 | 122.5754 | 0.013733 | 0.045777 | 122.9233 | 122.8958 | 122.8867 | 122.8683 | -122.8729 | -122.8638 | 122.5388 | 0.018311 | 2.1652 | 1.1948
1943.1719 | 122.9416 | -57.2433 | 65.5884 | -0.083466 | -0.00044654 | 0.062025 | 0.070541 | 0.0016556 | 0.0045417 | 0.0067036 | 0.013916 | 0.0011023 | 0.0012818 | 0.0026232 | -0.0021469 | -0.0045117 | -0.00040166 | -55.1788 | 65.6021 | -57.312 | 65.3503 | -56.6025 | -57.0877 | -56.3828 | -56.0486 | 65.6296 | -57.2937 | -57.2433 | -57.2479 | -57.3532 | -57.0602 | -0.068665 | 0.013733 | -0.23804 | 0.64087 | 0.8606 | 0.15564 | 0.92926 | 0.2243 | -0.050354 | 0.041199 | -122.8317 | -0.004578 | 0.1831 | -0.10986 | 0.23346 | -0.059509 | 0.70953 | 122.6624 | 0.045776 | 0.050354 | 122.9141 | 122.9233 | 122.8455 | 122.8729 | -122.9004 | -122.8821 | 122.5937 | 0 | 2.0645 | 1.1948
1944.1719 | 122.9691 | -57.2388 | 65.6067 | -0.075836 | 0.00040806 | 0.061598 | 0.070327 | 0.0018692 | 0.0032599 | 0.0049946 | -0.0074462 | 0.0015295 | 2.8e-08 | -0.0044262 | -0.00065151 | -0.0040845 | -0.0038197 | -55.1605 | 65.5838 | -57.3257 | 65.3366 | -56.6345 | -57.0923 | -56.3828 | -56.0623 | 65.625 | -57.2983 | -57.2342 | -57.2433 | -57.3624 | -57.0419 | -0.086975 | -0.022888 | -0.27008 | 0.60425 | 0.85602 | 0.14649 | 0.94299 | 0.23346 | -0.059509 | 0.018311 | -122.8409 | -0.004577 | 0.19684 | -0.1236 | 0.25635 | -0.064087 | 0.69122 | 122.6624 | 0.054932 | 0.064087 | 122.9095 | 122.9233 | 122.8226 | 122.8638 | -122.9324 | -122.905 | 122.5754 | 0.004578 | 2.0782 | 1.1765
1945.1719 | 122.9874 | -57.2571 | 65.593 | -0.022431 | 0.00019446 | 0.060957 | 0.071395 | 0.0016556 | 0.0021917 | 0.0090534 | -0.03186 | 0.0015295 | 0.0029906 | 0.009032 | -0.00065151 | -0.0019483 | -0.0018971 | -55.1285 | 65.6021 | -57.312 | 65.3641 | -56.5979 | -57.0557 | -56.3782 | -55.9982 | 65.6113 | -57.2891 | -57.2113 | -57.2342 | -57.3669 | -57.0236 | -0.054932 | 0.009155 | -0.22888 | 0.65918 | 0.87891 | 0.20142 | 0.93384 | 0.25635 | -0.032044 | 0.01831 | -122.8043 | 0.022888 | 0.23346 | -0.10986 | 0.2655 | -0.077819 | 0.71411 | 122.6761 | 0.054932 | 0.07782 | 122.9141 | 122.9004 | 122.8592 | 122.8683 | -122.905 | -122.8821 | 122.6212 | 0.045776 | 2.1286 | 1.2589
1946.1719 | 122.9874 | -57.2342 | 65.5609 | -0.068207 | 0.00040806 | 0.060957 | 0.072463 | 0.00486 | 0.0030463 | 0.0077716 | 0.001709 | 0.00088875 | 0.0025634 | -0.0027174 | 0.0010575 | -0.0032301 | 0.0015209 | -55.1285 | 65.5884 | -57.3349 | 65.3732 | -56.575 | -57.0648 | -56.3873 | -55.9708 | 65.6113 | -57.2708 | -57.2113 | -57.225 | -57.3532 | -57.0328 | -0.10071 | 0.027466 | -0.18768 | 0.65918 | 0.84686 | 0.16937 | 0.94757 | 0.27008 | -0.036621 | 0.050354 | -122.7722 | 0.009155 | 0.20142 | -0.11902 | 0.23804 | -0.082397 | 0.75989 | 122.7081 | 0.045776 | 0.059509 | 122.9233 | 122.8821 | 122.8226 | 122.8455 | -122.8958 | -122.8317 | 122.6074 | 0.022888 | 2.1057 | 1.2634
1947.1719 | 122.9416 | -57.2754 | 65.5701 | -0.10635 | 0.0025443 | 0.063521 | 0.07289 | 0.001442 | 0.0021917 | 0.0077716 | -0.01355 | 0.0030249 | 0.001709 | 0.00027342 | 0.0014847 | -0.0023755 | 0.0028027 | -55.1651 | 65.5746 | -57.3303 | 65.3275 | -56.6299 | -57.1289 | -56.4239 | -56.0623 | 65.5975 | -57.2983 | -57.2479 | -57.2891 | -57.4036 | -57.0786 | -0.054931 | 0.004578 | -0.24261 | 0.64545 | 0.85144 | 0.14648 | 0.90637 | 0.20142 | -0.022888 | 0.027466 | -122.818 | -0.013733 | 0.19684 | -0.12817 | 0.21973 | -0.10529 | 0.70038 | 122.6578 | 0.009155 | 0.050354 | 122.905 | 122.8958 | 122.85 | 122.8729 | -122.9004 | -122.8683 | 122.6028 | 0.027466 | 2.1103 | 1.2131
1948.1719 | 123.0377 | -57.2662 | 65.5289 | -0.15213 | 0.00019446 | 0.063307 | 0.068618 | 0.0012284 | 0.0015509 | 0.0034992 | 0.044434 | 0.00088875 | -0.00021357 | -0.0067762 | -0.00065151 | -0.0049389 | 0.00023934 | -55.1605 | 65.5014 | -57.312 | 65.3961 | -56.5292 | -57.0602 | -56.3324 | -55.9525 | 65.5426 | -57.2937 | -57.1838 | -57.193 | -57.2983 | -57.0007 | -0.045777 | -0.027466 | -0.13275 | 0.737 | 0.93384 | 0.20599 | 0.97962 | 0.25177 | -0.027466 | 0.013733 | -122.7127 | 0.073242 | 0.2655 | -0.032044 | 0.29297 | -0.004578 | 0.78278 | 122.7081 | 0.10071 | 0.10986 | 122.8134 | 122.8363 | 122.7676 | 122.8088 | -122.8409 | -122.8226 | 122.6624 | 0.082397 | 2.1057 | 1.3138
1949.1719 | 123.0057 | -57.2388 | 65.6067 | -0.091095 | 0.0016899 | 0.061598 | 0.073104 | 0.005928 | 0.0021917 | 0.0064898 | -0.025757 | 0.0015295 | 0.00064083 | 0.0060412 | -0.0025741 | -0.0021619 | -0.0048877 | -55.1239 | 65.5884 | -57.3441 | 65.3641 | -56.5704 | -57.0694 | -56.3919 | -55.9982 | 65.5884 | -57.2662 | -57.2159 | -57.2388 | -57.3349 | -57.019 | -0.10528 | -0.01831 | -0.24261 | 0.66833 | 0.84686 | 0.16937 | 0.95215 | 0.27466 | -0.027465 | -0.01831 | -122.8226 | 0 | 0.21973 | -0.09613 | 0.24719 | -0.068665 | 0.77362 | 122.7081 | 0.027465 | 0.050354 | 122.9324 | 122.8546 | 122.8271 | 122.8271 | -122.9507 | -122.8729 | 122.6028 | 0.022889 | 2.1149 | 1.2405
1950.1719 | 122.9416 | -57.28 | 65.5655 | -0.037689 | 0.0012625 | 0.063307 | 0.072677 | 0.0020828 | 0.0026191 | 0.0077716 | -0.022705 | 0.0017431 | 0.0012818 | 0.0045458 | 0.00020289 | -0.0040845 | 0.0030163 | -55.1743 | 65.5563 | -57.3441 | 65.3229 | -56.6345 | -57.1426 | -56.4331 | -56.0669 | 65.5655 | -57.28 | -57.2891 | -57.3166 | -57.4493 | -57.0831 | -0.064087 | -0.009156 | -0.24262 | 0.64545 | 0.84686 | 0.13733 | 0.91095 | 0.20142 | 0 | 0 | -122.8546 | -0.036621 | 0.19684 | -0.16937 | 0.19684 | -0.16937 | 0.70953 | 122.6669 | -0.036621 | -0.009156 | 122.9004 | 122.8455 | 122.8363 | 122.8455 | -122.9095 | -122.8455 | 122.6028 | -0.009156 | 2.1057 | 1.2131
1951.1719 | 123.024 | -57.3349 | 65.5655 | -0.1445 | 0.00040806 | 0.064162 | 0.071822 | 0.0010148 | 0.0013373 | 0.0071308 | -0.025757 | 0.0019567 | 0.00085443 | 0.003905 | -0.0019333 | -0.0032301 | 0.0021619 | -55.2017 | 65.538 | -57.3578 | 65.2725 | -56.7352 | -57.2067 | -56.4972 | -56.1127 | 65.5975 | -57.3395 | -57.2891 | -57.3669 | -57.7469 | -57.3303 | -0.022888 | -0.027466 | -0.29297 | 0.59967 | 0.83771 | 0.12817 | 0.8606 | 0.15106 | -0.004578 | 0.032043 | -122.8546 | -0.032043 | 0.004578 | -0.41199 | 0.009156 | -0.40741 | 0.62256 | 122.6303 | -0.027465 | 0.050354 | 122.8958 | 122.937 | 122.8729 | 122.9324 | -122.9233 | -122.905 | 122.6074 | 0.045776 | 2.1332 | 1.2222
1952.1719 | 122.9782 | -57.2662 | 65.5746 | -0.060578 | 0.0012625 | 0.061385 | 0.070327 | 0.0016556 | 0.0030463 | 0.0049946 | -0.0074462 | 0.00046135 | 0.001709 | -0.00015378 | -0.0015061 | -0.0036573 | -0.0012561 | -55.1147 | 65.5701 | -57.3395 | 65.3778 | -56.5704 | -57.0831 | -56.4011 | -55.9982 | 65.5792 | -57.312 | -57.1976 | -57.225 | -57.3532 | -57.019 | -0.073243 | -0.004578 | -0.19684 | 0.6958 | 0.86517 | 0.18311 | 0.93842 | 0.25635 | -0.045777 | 0.004578 | -122.7722 | 0.041198 | 0.24719 | -0.086975 | 0.29297 | -0.041198 | 0.76904 | 122.7173 | 0.086975 | 0.11444 | 122.9095 | 122.8912 | 122.8363 | 122.8455 | -122.9141 | -122.8867 | 122.644 | 0.068664 | 2.1515 | 1.268
1953.1719 | 123.0515 | -57.2525 | 65.5289 | -0.10635 | -0.00044654 | 0.062666 | 0.071822 | 0.0055008 | 0.0028327 | 0.0084124 | 0.03833 | 0.00046135 | -0.00085457 | -0.00079478 | -0.0015061 | -0.0032301 | -0.00018806 | -55.1239 | 65.4968 | -57.3074 | 65.4053 | -56.5659 | -57.0557 | -56.3553 | -55.8975 | 65.5106 | -57.3349 | -57.2021 | -57.1564 | -57.28 | -56.9733 | -0.054932 | -0.032044 | -0.1236 | 0.68664 | 0.89722 | 0.19684 | 0.95215 | 0.25177 | -0.082398 | -0.018311 | -122.731 | 0.09613 | 0.27923 | -0.027466 | 0.36163 | 0.054932 | 0.74158 | 122.7127 | 0.17853 | 0.13275 | 122.8043 | 122.8455 | 122.7493 | 122.7631 | -122.8363 | -122.8638 | 122.6578 | 0.050354 | 2.1286 | 1.355
1954.1719 | 123.0286 | -57.2845 | 65.5334 | -0.17502 | 0.00083526 | 0.063094 | 0.068832 | -0.001976 | 0.0021917 | 0.0045672 | 0.059692 | -0.0012477 | 0.0014954 | -0.0037854 | -0.0038559 | -0.0032301 | 0.00023934 | -55.1422 | 65.4831 | -57.3212 | 65.387 | -56.5475 | -57.0602 | -56.337 | -55.9845 | 65.5518 | -57.2983 | -57.1976 | -57.2159 | -57.3166 | -57.0145 | -0.036621 | -0.050354 | -0.14648 | 0.737 | 0.94757 | 0.2243 | 0.98419 | 0.26093 | -0.013733 | 0.018311 | -122.731 | 0.068665 | 0.27008 | -0.032043 | 0.28381 | -0.01831 | 0.77362 | 122.7081 | 0.082398 | 0.10071 | 122.8043 | 122.85 | 122.7676 | 122.8363 | -122.8546 | -122.8317 | 122.6715 | 0.086975 | 2.1423 | 1.3
1955.1719 | 122.9874 | -57.2296 | 65.6113 | -0.12924 | -0.0013009 | 0.063734 | 0.073531 | -0.0024032 | 0.0011237 | 0.0054218 | 0.026123 | 0.00067495 | 0.0029906 | -0.0072034 | -0.0038559 | -0.0042981 | -0.0014697 | -55.1514 | 65.5746 | -57.3212 | 65.3595 | -56.6391 | -57.0786 | -56.3965 | -56.0257 | 65.625 | -57.2708 | -57.225 | -57.2296 | -57.3349 | -57.0099 | -0.091553 | -0.036621 | -0.25177 | 0.59051 | 0.83313 | 0.15106 | 0.92468 | 0.24262 | -0.041199 | 0.013733 | -122.8363 | 0 | 0.21973 | -0.10529 | 0.26093 | -0.064087 | 0.68207 | 122.6807 | 0.041199 | 0.045776 | 122.8958 | 122.8958 | 122.8043 | 122.8546 | -122.9324 | -122.8821 | 122.5891 | 0.004577 | 2.0782 | 1.2039
1956.1719 | 122.9828 | -57.2662 | 65.593 | -0.045319 | -0.00087374 | 0.061812 | 0.073104 | 0.0020828 | 0.0013373 | 0.0067036 | -0.019653 | 0.0011023 | 0.00085443 | 0.00048702 | -0.00086511 | -0.0036573 | -0.00061526 | -55.1193 | 65.5746 | -57.3257 | 65.387 | -56.5933 | -57.0694 | -56.3919 | -55.9891 | 65.6113 | -57.28 | -57.2113 | -57.225 | -57.3395 | -57.0145 | -0.05951 | -0.018311 | -0.20599 | 0.67291 | 0.87433 | 0.19684 | 0.93384 | 0.25635 | -0.013733 | 0.01831 | -122.8043 | 0.041198 | 0.25177 | -0.073243 | 0.2655 | -0.05951 | 0.73242 | 122.7127 | 0.054931 | 0.068664 | 122.9004 | 122.8912 | 122.8409 | 122.8775 | -122.9187 | -122.8729 | 122.6532 | 0.054931 | 2.1469 | 1.2772
1957.1719 | 122.9462 | -57.2296 | 65.5472 | -0.10635 | 0.0010489 | 0.062666 | 0.072677 | -0.00048063 | 0.0017645 | 0.0088398 | -0.03186 | 0.0011023 | 0.001068 | 0.0015552 | -0.0032151 | -0.0025891 | -0.0010425 | -55.2292 | 65.5518 | -57.3257 | 65.3503 | -56.6116 | -57.0648 | -56.3828 | -56.0211 | 65.6158 | -57.2891 | -57.2296 | -57.2662 | -57.3761 | -57.0328 | -0.096131 | 0.004578 | -0.19684 | 0.61798 | 0.84686 | 0.16479 | 0.94299 | 0.26093 | -0.05951 | 0.068665 | -122.7768 | -0.036621 | 0.19684 | -0.14649 | 0.25635 | -0.086975 | 0.71411 | 122.6761 | 0.022889 | 0.05951 | 122.8775 | 122.905 | 122.7814 | 122.8455 | -122.8729 | -122.8363 | 122.58 | 0 | 2.0004 | 1.2085
1958.1719 | 123.0835 | -57.2525 | 65.5243 | -0.13687 | -0.0013009 | 0.063521 | 0.071609 | -0.005394 | 0.0041143 | 0.0049946 | 0.023071 | 0.00067495 | 0.00085443 | -0.0037854 | 0.00041649 | -0.0025891 | -0.0012561 | -55.1331 | 65.5243 | -57.3257 | 65.3915 | -56.5613 | -57.0786 | -56.3553 | -55.9753 | 65.5426 | -57.3166 | -57.2708 | -57.2983 | -57.1655 | -56.8497 | -0.073243 | 0 | -0.13275 | 0.69122 | 0.89722 | 0.17395 | 0.97046 | 0.24719 | -0.064087 | 0.018311 | -122.7951 | -0.045777 | 0.40283 | 0.086975 | 0.46692 | 0.15106 | 0.76447 | 122.7173 | 0.01831 | 0.045776 | 122.85 | 122.8592 | 122.7768 | 122.7951 | -122.85 | -122.8409 | 122.644 | -0.018311 | 2.1194 | 1.2772
1959.1719 | 122.9874 | -57.2662 | 65.5884 | -0.083466 | -0.00066014 | 0.062666 | 0.071822 | -0.0038986 | 0.0019781 | 0.007558 | -0.01355 | 0.0021703 | 0.0014954 | 0.00070062 | -0.0017197 | -0.0028027 | 0.0023755 | -55.1422 | 65.5472 | -57.3441 | 65.2817 | -56.6116 | -57.0007 | -56.3965 | -56.012 | 65.5975 | -57.2708 | -57.2021 | -57.2708 | -57.3624 | -57.019 | -0.07782 | -0.041199 | -0.3067 | 0.6546 | 0.86975 | 0.2655 | 0.94757 | 0.34332 | -0.004578 | 0.009155 | -122.7905 | -0.004578 | 0.24719 | -0.096131 | 0.25177 | -0.091553 | 0.73242 | 122.6257 | 0 | 0.068665 | 122.8912 | 122.8683 | 122.8134 | 122.8638 | -122.9324 | -122.8592 | 122.5479 | 0.064087 | 2.124 | 1.2543
1960.1719 | 122.9874 | -57.2388 | 65.5746 | -0.075836 | -1.9142e-05 | 0.063307 | 0.070327 | 0.0010148 | 0.0021917 | 0.0062762 | -0.1051 | 0.0023839 | 0.0019226 | 0.003905 | -0.0019333 | -0.0023755 | 0.00023934 | -55.1056 | 65.5609 | -57.3303 | 65.3687 | -56.5887 | -57.0786 | -56.3873 | -56.0532 | 65.5838 | -57.28 | -57.225 | -57.2342 | -57.3441 | -57.0282 | -0.091552 | -0.013733 | -0.20599 | 0.65002 | 0.85144 | 0.16022 | 0.94299 | 0.25177 | -0.041198 | 0.009155 | -122.7997 | 0.004578 | 0.21057 | -0.10528 | 0.25177 | -0.064087 | 0.74158 | 122.699 | 0.045776 | 0.054931 | 122.8912 | 122.8638 | 122.7997 | 122.8226 | -122.905 | -122.8546 | 122.6074 | 0.013733 | 2.1332 | 1.1856
1961.1719 | 122.9782 | -57.2754 | 65.5975 | -0.03006 | -0.0010873 | 0.059462 | 0.071822 | -0.001976 | 0.0030463 | 0.0064898 | -0.025757 | 0.0011023 | 0.001068 | -0.00058098 | 0.00063009 | -0.0038709 | -0.00040166 | -55.1193 | 65.5655 | -57.3257 | 65.3458 | -56.5933 | -57.0969 | -56.4194 | -56.0394 | 65.625 | -57.2845 | -57.2433 | -57.2845 | -57.4081 | -57.0511 | -0.050354 | -0.032043 | -0.25177 | 0.68207 | 0.85602 | 0.17853 | 0.90637 | 0.22888 | -0.009155 | 0.027466 | -122.8409 | -0.009155 | 0.22431 | -0.13275 | 0.23346 | -0.1236 | 0.73242 | 122.6715 | 0 | 0.041199 | 122.8912 | 122.9095 | 122.8409 | 122.9004 | -122.9233 | -122.8821 | 122.6212 | 0.032044 | 2.1561 | 1.236
1962.1719 | 122.9691 | -57.2479 | 65.5609 | -0.045319 | -0.00087374 | 0.062666 | 0.072036 | 0.00037377 | 0.0015509 | 0.0028582 | -0.03186 | 0.00067495 | -0.00064077 | 0.0017688 | -0.0027877 | -0.0032301 | 0.0013073 | -55.1147 | 65.5426 | -57.3212 | 65.3503 | -56.5979 | -57.0969 | -56.4011 | -56.012 | 65.6021 | -57.2983 | -57.2525 | -57.28 | -57.3761 | -57.0557 | -0.073242 | -0.01831 | -0.21057 | 0.65002 | 0.84686 | 0.15106 | 0.9201 | 0.2243 | -0.050354 | 0.041199 | -122.8134 | -0.032043 | 0.19226 | -0.12817 | 0.24262 | -0.07782 | 0.72327 | 122.6715 | 0.018311 | 0.045777 | 122.8638 | 122.9004 | 122.7905 | 122.85 | -122.8821 | -122.8592 | 122.5983 | -0.004577 | 2.1332 | 1.236
1963.1719 | 123.0423 | -57.2525 | 65.5334 | -0.060578 | -1.9142e-05 | 0.062453 | 0.068618 | -0.00069423 | 0.0034735 | 0.0067036 | 0.041382 | 0.00046135 | 0.0019226 | 0.00027342 | -0.00065151 | -0.0051527 | 2.554e-05 | -55.1422 | 65.5014 | -57.3212 | 65.3503 | -56.5933 | -57.0831 | -56.3782 | -56.0211 | 65.5563 | -57.2891 | -57.2159 | -57.225 | -57.3029 | -57.0099 | -0.068665 | -0.032043 | -0.1831 | 0.65918 | 0.87433 | 0.16937 | 0.94299 | 0.23804 | -0.036622 | 0.022888 | -122.7493 | 0.027465 | 0.24261 | -0.050354 | 0.27924 | -0.013732 | 0.72784 | 122.6715 | 0.064087 | 0.073243 | 122.8226 | 122.8455 | 122.7539 | 122.8088 | -122.8546 | -122.8226 | 122.6028 | 0.036621 | 2.1103 | 1.2314
1964.1719 | 122.9782 | -57.2342 | 65.5838 | -0.068207 | 0.00083526 | 0.062025 | 0.072036 | 0.00251 | 0.0011237 | 0.012685 | -0.041016 | 0.00067495 | 0.0021362 | 0.0013416 | -0.0025741 | -0.0021619 | -0.00018806 | -55.0873 | 65.5792 | -57.3486 | 65.2771 | -56.7261 | -56.9733 | -56.3599 | -55.9937 | 65.6021 | -57.2983 | -57.2159 | -57.2571 | -57.3441 | -57.0328 | -0.11444 | -0.004577 | -0.3067 | 0.50812 | 0.87433 | 0.26093 | 0.98877 | 0.37537 | -0.064087 | 0.018311 | -122.7997 | -0.022888 | 0.20142 | -0.10986 | 0.2655 | -0.045776 | 0.62256 | 122.6257 | 0.041199 | 0.082398 | 122.9279 | 122.9004 | 122.8134 | 122.8363 | -122.9324 | -122.8821 | 122.5113 | 0.018311 | 2.1469 | 1.2405
1965.1719 | 122.9828 | -57.2708 | 65.5701 | -0.052948 | 0.00062166 | 0.062453 | 0.071822 | 0.0035782 | 0.0015509 | 0.0043536 | -0.028809 | 0.0025975 | -0.001709 | 0.0030506 | -0.0017197 | -0.0038709 | -0.0010425 | -55.1102 | 65.5518 | -57.3212 | 65.3458 | -56.6162 | -57.1014 | -56.4102 | -56.044 | 65.593 | -57.3029 | -57.2433 | -57.2845 | -57.3944 | -57.0557 | -0.050354 | -0.01831 | -0.2243 | 0.6546 | 0.8606 | 0.16937 | 0.91095 | 0.21973 | -0.032043 | 0.022889 | -122.8134 | -0.013733 | 0.21515 | -0.1236 | 0.24719 | -0.091553 | 0.70496 | 122.6669 | 0.01831 | 0.059509 | 122.8729 | 122.8958 | 122.8226 | 122.8638 | -122.8912 | -122.8729 | 122.6166 | 0.027466 | 2.1606 | 1.2268
1966.1719 | 122.9782 | -57.2433 | 65.5609 | -0.083466 | 0.0012625 | 0.062453 | 0.07289 | 0.0035782 | 0.0021917 | 0.0064898 | -0.034912 | 0.0019567 | 0.00064083 | -0.00015378 | -0.0027877 | -0.0015211 | -0.0016833 | -55.0964 | 65.5701 | -57.312 | 65.3687 | -56.6025 | -57.1014 | -56.4102 | -56.0211 | 65.5975 | -57.2754 | -57.2296 | -57.2571 | -57.3807 | -57.0419 | -0.068665 | 0.009155 | -0.19226 | 0.64087 | 0.83313 | 0.14191 | 0.90179 | 0.21057 | -0.032044 | 0.036621 | -122.7905 | -0.013733 | 0.20142 | -0.13733 | 0.23346 | -0.10529 | 0.70953 | 122.6807 | 0.018311 | 0.045777 | 122.8821 | 122.8729 | 122.8134 | 122.8409 | -122.8729 | -122.8363 | 122.612 | 0.013733 | 2.1469 | 1.2222
1967.1719 | 122.937 | -57.2525 | 65.5746 | -0.083466 | 0.00019446 | 0.061812 | 0.073104 | 0.0033646 | 0.00026909 | 0.0047808 | -0.0043946 | 0.0025975 | 0.00085443 | -0.0025036 | -0.0025741 | -0.0028027 | 0.00045294 | -55.1056 | 65.5655 | -57.3349 | 65.3091 | -56.6299 | -57.1289 | -56.4377 | -56.0715 | 65.5838 | -57.3029 | -57.2754 | -57.2983 | -57.4173 | -57.0694 | -0.082398 | -0.009155 | -0.2655 | 0.62256 | 0.81482 | 0.1236 | 0.89722 | 0.20599 | -0.050354 | 0.009155 | -122.85 | -0.045777 | 0.1831 | -0.16479 | 0.23346 | -0.11444 | 0.70496 | 122.644 | 0.004577 | 0.027465 | 122.9004 | 122.8867 | 122.818 | 122.8363 | -122.9095 | -122.8775 | 122.5616 | -0.022889 | 2.1469 | 1.181
1968.1719 | 122.9782 | -57.2433 | 65.593 | -0.10635 | 0.0012625 | 0.063521 | 0.071395 | -0.00048063 | -0.00037171 | 0.0067036 | 0.0078126 | 0.0013159 | -0.00021357 | -0.0025036 | -0.0015061 | -0.0032301 | 0.00045294 | -55.0781 | 65.6021 | -57.2891 | 65.3595 | -56.6116 | -57.0648 | -56.3919 | -56.012 | 65.593 | -57.2708 | -57.2021 | -57.225 | -57.3532 | -57.0465 | -0.045777 | 0.009155 | -0.23346 | 0.63171 | 0.85144 | 0.17853 | 0.89722 | 0.22431 | -0.027466 | 0 | -122.7951 | 0.01831 | 0.19684 | -0.10986 | 0.2243 | -0.082397 | 0.67749 | 122.6486 | 0.045776 | 0.068665 | 122.8912 | 122.8638 | 122.8455 | 122.8363 | -122.8821 | -122.8638 | 122.6028 | 0.041199 | 2.1652 | 1.2314
1969.1719 | 122.9507 | -57.2433 | 65.5975 | 0.015716 | -0.00066014 | 0.061171 | 0.071822 | -0.0017624 | 0.0015509 | 0.0064898 | 0.029175 | 0.0015295 | 0.0012818 | 0.0026232 | -0.00043791 | -0.0045117 | 0.0017345 | -55.0781 | 65.6067 | -57.2754 | 65.3183 | -56.6895 | -57.1014 | -56.4194 | -56.044 | 65.6158 | -57.2571 | -57.2708 | -57.2525 | -57.3486 | -57.0557 | -0.032044 | 0.009155 | -0.27924 | 0.55389 | 0.82397 | 0.14191 | 0.85602 | 0.17395 | -0.013733 | 0.018311 | -122.8683 | -0.009155 | 0.18768 | -0.10529 | 0.20142 | -0.091553 | 0.58594 | 122.5937 | 0.004578 | -0.013733 | 122.8821 | 122.8729 | 122.85 | 122.8592 | -122.8729 | -122.8546 | 122.5616 | -0.027466 | 2.1652 | 1.1993
1970.1719 | 122.9828 | -57.225 | 65.6296 | -0.060578 | -0.00066014 | 0.062025 | 0.070968 | 0.00080117 | 0.00069649 | 0.0071308 | 0.023071 | 0.0017431 | 0.00064083 | 0.00027342 | -0.00043791 | -0.0051527 | -0.0031787 | -55.0964 | 65.5838 | -57.3074 | 65.332 | -56.6391 | -57.0831 | -56.4011 | -56.0669 | 65.6113 | -57.28 | -57.2388 | -57.2205 | -57.3486 | -57.0236 | -0.082397 | -0.045777 | -0.29755 | 0.58594 | 0.82397 | 0.14191 | 0.90637 | 0.2243 | -0.054931 | -0.018311 | -122.8683 | 0.004578 | 0.20142 | -0.1236 | 0.25635 | -0.068665 | 0.66833 | 122.6395 | 0.059509 | 0.041198 | 122.8912 | 122.8912 | 122.8088 | 122.8363 | -122.937 | -122.9095 | 122.5571 | -0.013733 | 2.1286 | 1.1581
1971.1719 | 123.0011 | -57.2479 | 65.5655 | -0.037689 | 0.00062166 | 0.060316 | 0.071181 | 0.0020828 | 0.0036871 | 0.0049946 | -0.0043946 | -0.0023157 | 0.0012818 | -0.0018628 | -0.00043791 | -0.0040845 | -0.0012561 | -55.0781 | 65.6021 | -57.3074 | 65.3595 | -56.5704 | -57.0694 | -56.3736 | -56.0211 | 65.6158 | -57.2937 | -57.2113 | -57.2388 | -57.3395 | -57.0374 | -0.059509 | 0.036621 | -0.20599 | 0.67749 | 0.87433 | 0.17853 | 0.93384 | 0.23804 | -0.045776 | 0.050354 | -122.7768 | 0.009155 | 0.21057 | -0.091553 | 0.25635 | -0.045777 | 0.737 | 122.6669 | 0.054931 | 0.082397 | 122.9095 | 122.9095 | 122.85 | 122.8638 | -122.8729 | -122.8592 | 122.6074 | 0.036621 | 2.1698 | 1.2268
1972.1719 | 123.0103 | -57.2205 | 65.6067 | -0.060578 | 0.00083526 | 0.063094 | 0.069259 | 0.00016017 | 0.00091009 | 0.0062762 | -0.0043946 | 0.0028113 | 2.8e-08 | -0.0033582 | -0.0023605 | -0.0040845 | 0.0023755 | -55.0781 | 65.5838 | -57.3212 | 65.3687 | -56.5979 | -57.0694 | -56.4011 | -56.0257 | 65.6158 | -57.2708 | -57.2067 | -57.2067 | -57.3303 | -57.0236 | -0.10071 | -0.022888 | -0.23804 | 0.62256 | 0.8194 | 0.15106 | 0.9201 | 0.25177 | -0.050354 | 0.009156 | -122.8134 | 0.013733 | 0.19684 | -0.10986 | 0.24719 | -0.059509 | 0.72327 | 122.6898 | 0.064087 | 0.064087 | 122.905 | 122.8867 | 122.8043 | 122.8363 | -122.9279 | -122.8775 | 122.5891 | 0.013733 | 2.1423 | 1.1948
1973.1719 | 122.9965 | -57.2296 | 65.5838 | -0.045319 | -1.9142e-05 | 0.062453 | 0.072036 | 0.0037918 | 0.0039007 | 0.0064898 | -0.0013428 | 0.0011023 | -0.00021357 | -0.0010084 | -0.0012925 | -0.0036573 | -0.0036059 | -55.069 | 65.5746 | -57.3303 | 65.3549 | -56.5887 | -57.0831 | -56.4011 | -55.9937 | 65.593 | -57.28 | -57.1976 | -57.225 | -57.3486 | -57.0236 | -0.10071 | -0.009155 | -0.22888 | 0.64087 | 0.82855 | 0.14648 | 0.92926 | 0.24719 | -0.050354 | 0.009156 | -122.7814 | 0.004577 | 0.20599 | -0.11902 | 0.25635 | -0.068665 | 0.74158 | 122.6852 | 0.054931 | 0.082397 | 122.905 | 122.8729 | 122.8043 | 122.8226 | -122.9141 | -122.8638 | 122.5845 | 0.032043 | 2.1606 | 1.236
1974.1719 | 122.9965 | -57.2433 | 65.5792 | -0.022431 | 0.0014761 | 0.060957 | 0.0699 | 0.0012284 | 0.0015509 | 0.0049946 | 0.013916 | 0.00088875 | 0.002777 | 0.00027342 | -0.00065151 | -0.0042981 | -0.0016833 | -55.069 | 65.6067 | -57.3074 | 65.3687 | -56.5887 | -57.0694 | -56.4056 | -56.0028 | 65.5746 | -57.2662 | -57.2113 | -57.2296 | -57.3578 | -57.0099 | -0.064087 | 0.027465 | -0.21057 | 0.6546 | 0.83771 | 0.17395 | 0.90179 | 0.23804 | -0.022888 | -0.004578 | -122.7905 | 0.013733 | 0.23346 | -0.11444 | 0.25635 | -0.091553 | 0.71869 | 122.6761 | 0.036621 | 0.054931 | 122.9141 | 122.8409 | 122.85 | 122.818 | -122.8867 | -122.8455 | 122.612 | 0.032043 | 2.1744 | 1.2405
1975.1719 | 122.9828 | -57.2433 | 65.6067 | -0.052948 | 0.0014761 | 0.061812 | 0.070327 | -0.003685 | 0.00069649 | 0.00414 | 0.02002 | 3.4148e-05 | 0.0023498 | -0.0018628 | -0.00086511 | -0.0032301 | -0.0029651 | -54.9637 | 65.657 | -57.2891 | 65.3137 | -56.662 | -57.0969 | -56.4514 | -56.0623 | 65.6433 | -57.2891 | -57.2525 | -57.2525 | -57.3578 | -57.0648 | -0.045777 | 0.050354 | -0.29297 | 0.58136 | 0.79193 | 0.14648 | 0.83771 | 0.19226 | -0.045777 | 0.036622 | -122.8592 | -0.009155 | 0.17853 | -0.11444 | 0.22431 | -0.068664 | 0.62714 | 122.6028 | 0.036622 | 0.036622 | 122.9462 | 122.9324 | 122.9004 | 122.8867 | -122.8958 | -122.8958 | 122.5571 | -0.009155 | 2.2797 | 1.181
1976.1719 | 122.9599 | -57.2479 | 65.6067 | -0.075836 | -0.0023691 | 0.059248 | 0.068618 | -0.0017624 | 0.0024053 | 0.0034992 | 0.071899 | 0.00024775 | 0.001709 | -0.005708 | -0.0023605 | -0.0047253 | 0.0017345 | -55.0507 | 65.5655 | -57.2983 | 65.3824 | -56.5704 | -57.0511 | -56.3507 | -56.0028 | 65.6158 | -57.2571 | -57.2342 | -57.2479 | -57.3441 | -57.0557 | -0.050354 | -0.041198 | -0.2243 | 0.67749 | 0.89722 | 0.19684 | 0.94757 | 0.24719 | -0.009155 | 0.009156 | -122.8409 | 0 | 0.19226 | -0.09613 | 0.20142 | -0.086975 | 0.72784 | 122.6807 | 0.009155 | 0.022888 | 122.8638 | 122.8729 | 122.8134 | 122.8638 | -122.905 | -122.8638 | 122.6303 | 0.013733 | 2.1973 | 1.2451
1977.1719 | 122.9919 | -57.2342 | 65.5884 | -0.083466 | 0.00019446 | 0.061385 | 0.0699 | -0.0024032 | 0.0058233 | 0.0043536 | 0.053589 | 0.00024775 | 0.0019226 | -0.0082716 | -0.00086511 | -0.0062207 | 0.0013073 | -55.0461 | 65.5609 | -57.2662 | 65.4236 | -56.5292 | -57.0053 | -56.337 | -55.9891 | 65.6067 | -57.2662 | -57.2159 | -57.2113 | -57.2937 | -57.0053 | -0.032043 | -0.027466 | -0.16479 | 0.70496 | 0.89722 | 0.22888 | 0.92926 | 0.26093 | -0.032043 | 0.01831 | -122.8043 | 0.022888 | 0.22888 | -0.059509 | 0.26093 | -0.027466 | 0.737 | 122.6898 | 0.054931 | 0.050354 | 122.8271 | 122.8729 | 122.7951 | 122.8409 | -122.8546 | -122.8546 | 122.6578 | 0.018311 | 2.1881 | 1.2451
1978.1719 | 122.9507 | -57.2525 | 65.6296 | -0.098725 | 0.0025443 | 0.062025 | 0.069686 | -0.0028304 | 0.00069649 | 0.005849 | 0.047485 | 0.00088875 | 0.0012818 | -0.0033582 | -0.0017197 | -0.0045117 | -0.0016833 | -55.0507 | 65.593 | -57.2983 | 65.3458 | -56.6162 | -57.1014 | -56.369 | -56.0577 | 65.6342 | -57.2754 | -57.2662 | -57.2479 | -57.3624 | -57.0786 | -0.045777 | -0.036621 | -0.28381 | 0.63629 | 0.88348 | 0.15106 | 0.92926 | 0.19684 | -0.022889 | 0.004577 | -122.8958 | 0.004577 | 0.17395 | -0.10986 | 0.19684 | -0.086975 | 0.68207 | 122.644 | 0.027466 | 0.009156 | 122.8912 | 122.9095 | 122.8455 | 122.8867 | -122.9279 | -122.905 | 122.5983 | -0.013733 | 2.2018 | 1.1948
1979.1719 | 122.9599 | -57.2479 | 65.5975 | -0.0071715 | 0.00019446 | 0.062453 | 0.071395 | 0.0037918 | 0.0032599 | 0.005849 | 0.02002 | -0.00017945 | 0.00021363 | -0.00229 | -0.0019333 | -0.00088008 | 0.0015209 | -55.0644 | 65.5975 | -57.312 | 65.3366 | -56.6666 | -57.0877 | -56.4194 | -56.0486 | 65.625 | -57.2845 | -57.2525 | -57.2388 | -57.3624 | -57.0465 | -0.064087 | 0 | -0.26093 | 0.58136 | 0.82855 | 0.16022 | 0.89264 | 0.2243 | -0.036621 | 0.027466 | -122.85 | 0.009155 | 0.20142 | -0.11444 | 0.23804 | -0.07782 | 0.64545 | 122.6486 | 0.045776 | 0.032044 | 122.9095 | 122.9095 | 122.8455 | 122.8729 | -122.9095 | -122.8821 | 122.5845 | -0.004577 | 2.1835 | 1.1993
1980.1719 | 122.9553 | -57.2479 | 65.6158 | -0.068207 | 0.00083526 | 0.062666 | 0.071822 | -0.0041122 | -0.00037171 | 0.00414 | 0.016968 | 0.0021703 | 0.00085443 | -0.0050672 | -0.0015061 | -0.0047253 | 0.0064343 | -55.0735 | 65.6067 | -57.2845 | 65.3503 | -56.6666 | -57.1472 | -56.4239 | -56.0394 | 65.6342 | -57.2662 | -57.2571 | -57.2525 | -57.3715 | -57.0511 | -0.036621 | -0.009156 | -0.2655 | 0.58136 | 0.82398 | 0.10071 | 0.8606 | 0.13733 | -0.01831 | 0.01831 | -122.8729 | -0.004577 | 0.19684 | -0.1236 | 0.21515 | -0.10529 | 0.61798 | 122.6349 | 0.013733 | 0.009155 | 122.8912 | 122.9004 | 122.8546 | 122.8821 | -122.9004 | -122.8821 | 122.5983 | -0.009155 | 2.1744 | 1.2085
1981.1719 | 122.9507 | -57.2433 | 65.6113 | -0.045319 | -0.00066014 | 0.06288 | 0.069045 | -0.00026703 | -0.00037171 | 0.0067036 | 0.029175 | -0.00017945 | 0.00021363 | -0.00464 | -0.0010787 | -0.0055799 | 0.00066654 | -55.014 | 65.5655 | -57.28 | 65.387 | -56.5659 | -57.0419 | -56.3782 | -56.012 | 65.6158 | -57.2708 | -57.225 | -57.2433 | -57.3303 | -57.0419 | -0.036621 | -0.045776 | -0.2243 | 0.67749 | 0.86517 | 0.20142 | 0.90179 | 0.23804 | -0.027466 | 0.004578 | -122.8363 | 0 | 0.20142 | -0.086975 | 0.22888 | -0.059509 | 0.71411 | 122.6669 | 0.027466 | 0.045776 | 122.8455 | 122.8867 | 122.8088 | 122.8592 | -122.8912 | -122.8821 | 122.6303 | 0.01831 | 2.2293 | 1.2314
1982.1719 | 122.9553 | -57.2525 | 65.6067 | -0.045319 | -0.00023294 | 0.06288 | 0.069045 | -0.0011214 | 0.0028327 | 0.007558 | 0.023071 | -0.00039305 | 0.00085443 | -0.0010084 | -0.0015061 | -0.0040845 | -0.0014697 | -55.0369 | 65.625 | -57.2845 | 65.3412 | -56.6437 | -57.074 | -56.4102 | -56.044 | 65.625 | -57.2754 | -57.2571 | -57.2342 | -57.3532 | -57.0465 | -0.032044 | 0.018311 | -0.2655 | 0.60883 | 0.84228 | 0.17853 | 0.87433 | 0.21057 | -0.022889 | 0.018311 | -122.8638 | 0.01831 | 0.20599 | -0.10071 | 0.22888 | -0.077819 | 0.64087 | 122.6257 | 0.041199 | 0.018311 | 122.9095 | 122.9004 | 122.8775 | 122.8775 | -122.8912 | -122.8821 | 122.5937 | -0.004578 | 2.2156 | 1.2085
1983.1719 | 123.024 | -57.2205 | 65.5655 | -0.091095 | -0.0019417 | 0.061171 | 0.069472 | -0.0028304 | 0.0039007 | 0.005849 | 0.062744 | 3.4148e-05 | 0.00064083 | 0.0036914 | -0.0027877 | -0.0049389 | 0.0010937 | -54.9911 | 65.538 | -57.2937 | 65.4419 | -56.5247 | -57.0007 | -56.3141 | -55.9204 | 65.593 | -57.2708 | -57.1701 | -57.1609 | -57.2708 | -56.987 | -0.073242 | -0.027466 | -0.1236 | 0.6958 | 0.90637 | 0.21973 | 0.97961 | 0.29297 | -0.050354 | 0.027466 | -122.7356 | 0.059509 | 0.23346 | -0.050354 | 0.28381 | 0 | 0.76904 | 122.7356 | 0.10986 | 0.10071 | 122.8317 | 122.8638 | 122.7585 | 122.8134 | -122.8592 | -122.8363 | 122.6624 | 0.050354 | 2.2293 | 1.3
1984.1719 | 123.0698 | -57.2067 | 65.5792 | -0.25131 | 0.0021171 | 0.059889 | 0.070541 | -0.00090783 | 0.0013373 | 0.0039264 | 0.047485 | -0.0016749 | 0.00021363 | 0.00091422 | -0.00043791 | -0.0040845 | -0.00040166 | -55.0049 | 65.5151 | -57.3074 | 65.4373 | -56.4972 | -56.9778 | -56.3187 | -55.8884 | 65.593 | -57.2662 | -57.1564 | -57.1426 | -57.2433 | -56.9504 | -0.10071 | -0.064087 | -0.14191 | 0.70953 | 0.88806 | 0.22888 | 0.98877 | 0.32959 | -0.059509 | 0.013733 | -122.7356 | 0.064087 | 0.25635 | -0.036621 | 0.31586 | 0.022888 | 0.81024 | 122.7448 | 0.1236 | 0.10986 | 122.8226 | 122.8592 | 122.7219 | 122.7997 | -122.8867 | -122.8455 | 122.644 | 0.050354 | 2.2018 | 1.3184
1985.1719 | 122.9919 | -57.2159 | 65.5884 | -0.10635 | -1.9142e-05 | 0.062453 | 0.071609 | 0.00058737 | 0.0034735 | 0.0081988 | 0.03833 | -0.00039305 | -0.00021357 | 0.003905 | -0.0012925 | -0.0055799 | -0.00061526 | -55.0003 | 65.5518 | -57.2845 | 65.4419 | -56.543 | -57.0007 | -56.3278 | -55.9479 | 65.6021 | -57.2662 | -57.1838 | -57.1838 | -57.2845 | -57.0053 | -0.068665 | -0.036621 | -0.14648 | 0.67291 | 0.88806 | 0.21515 | 0.95673 | 0.28381 | -0.050354 | 0.013733 | -122.7722 | 0.032043 | 0.21057 | -0.068665 | 0.26093 | -0.018311 | 0.74158 | 122.7264 | 0.082397 | 0.082397 | 122.8363 | 122.8683 | 122.7676 | 122.818 | -122.8729 | -122.8546 | 122.6578 | 0.032043 | 2.2156 | 1.268
1986.1719 | 123.0698 | -57.225 | 65.5655 | -0.03006 | 0.0010489 | 0.062666 | 0.0699 | -0.0015488 | 0.0021917 | 0.005849 | 0.023071 | -0.00039305 | 0.00085443 | -0.0031446 | -0.0027877 | -0.0047253 | -0.00082886 | -55.0095 | 65.5334 | -57.2937 | 65.4602 | -56.5292 | -57.0099 | -56.3095 | -55.9021 | 65.5975 | -57.2388 | -57.1609 | -57.1518 | -57.2433 | -56.9778 | -0.068664 | -0.032044 | -0.10529 | 0.6958 | 0.91553 | 0.21515 | 0.98419 | 0.28381 | -0.013733 | 0.032043 | -122.7264 | 0.073243 | 0.24719 | -0.01831 | 0.26093 | -0.004577 | 0.76447 | 122.7539 | 0.086976 | 0.07782 | 122.8271 | 122.8363 | 122.7585 | 122.8226 | -122.8592 | -122.8043 | 122.6852 | 0.064087 | 2.2156 | 1.3229
1987.1719 | 123.0331 | -57.2113 | 65.5792 | -0.098725 | 0.0019035 | 0.061385 | 0.069045 | -0.0038986 | 0.0034735 | 0.0081988 | 0.029175 | -0.00082025 | -0.001709 | -0.003999 | -0.00065151 | -0.0045117 | 0.0015209 | -54.9957 | 65.5609 | -57.2937 | 65.2451 | -56.5887 | -56.9 | -56.3232 | -55.9113 | 65.5563 | -57.2525 | -57.1335 | -57.1289 | -57.225 | -56.9641 | -0.082397 | -0.018311 | -0.33417 | 0.62256 | 0.88806 | 0.31128 | 0.97046 | 0.39368 | -0.041198 | -0.022889 | -122.7127 | 0.082398 | 0.24719 | -0.013733 | 0.28839 | 0.027465 | 0.70496 | 122.5388 | 0.1236 | 0.11902 | 122.8546 | 122.8088 | 122.7722 | 122.7676 | -122.8729 | -122.8317 | 122.4564 | 0.07782 | 2.2156 | 1.3
1988.1719 | 122.9736 | -57.2662 | 65.5472 | 0.076752 | -0.0019417 | 0.064375 | 0.074172 | 0.0027238 | 0.0039007 | 0.0062762 | -0.068481 | -0.00017945 | 0.00021363 | -0.0025036 | -0.0017197 | -0.0019483 | -0.0023243 | -55.0873 | 65.5609 | -57.3349 | 65.3229 | -56.694 | -57.2067 | -56.4789 | -56.1081 | 65.5792 | -57.2937 | -57.2571 | -57.312 | -57.4173 | -57.074 | -0.068665 | 0.013733 | -0.2243 | 0.5722 | 0.78735 | 0.059509 | 0.85602 | 0.12817 | -0.027466 | 0.032044 | -122.8043 | -0.045777 | 0.19226 | -0.15106 | 0.21973 | -0.1236 | 0.64087 | 122.6578 | -0.018311 | 0.036621 | 122.8958 | 122.8729 | 122.8271 | 122.8455 | -122.8821 | -122.8409 | 122.5891 | 0.009155 | 2.179 | 1.1581
1989.1719 | 123.0743 | -57.2159 | 65.5609 | -0.075836 | -0.00044654 | 0.061598 | 0.069259 | -0.001976 | 0.0019781 | 0.0034992 | 0.056641 | 0.00046135 | -0.00042717 | 0.0015552 | -0.00065151 | -0.0045117 | -0.0070239 | -55.0095 | 65.5655 | -57.2754 | 65.4556 | -56.488 | -56.9824 | -56.3004 | -55.8655 | 65.5701 | -57.2708 | -57.1152 | -57.1106 | -57.2159 | -56.9458 | -0.05951 | 0.004578 | -0.10529 | 0.72784 | 0.91553 | 0.23346 | 0.97504 | 0.29297 | -0.054932 | 0.009155 | -122.6761 | 0.10529 | 0.27008 | 0 | 0.32501 | 0.054932 | 0.78735 | 122.731 | 0.16022 | 0.15564 | 122.8409 | 122.8409 | 122.7814 | 122.7859 | -122.8363 | -122.8317 | 122.6715 | 0.10071 | 2.2064 | 1.3504
1990.1719 | 123.0652 | -57.225 | 65.5243 | -0.098725 | 0.0023307 | 0.062666 | 0.068832 | -0.003685 | 0.0036871 | 0.003072 | 0.013916 | 0.00024775 | 0.00021363 | -0.0044262 | -0.0017197 | -0.0032301 | -0.0053149 | -55.0186 | 65.5426 | -57.28 | 65.451 | -56.5201 | -57.0145 | -56.3187 | -55.9021 | 65.5609 | -57.2296 | -57.1289 | -57.1198 | -57.2296 | -56.9321 | -0.054931 | 0.018311 | -0.073242 | 0.70496 | 0.90637 | 0.21057 | 0.9613 | 0.2655 | -0.004577 | 0.036621 | -122.6532 | 0.10529 | 0.29297 | -0.004577 | 0.29755 | 0 | 0.75989 | 122.731 | 0.10986 | 0.10071 | 122.8226 | 122.7905 | 122.7676 | 122.7859 | -122.8043 | -122.7539 | 122.6761 | 0.096131 | 2.2064 | 1.3229
1991.1719 | 123.0194 | -57.2525 | 65.538 | -0.098725 | -0.00087374 | 0.060744 | 0.073531 | 0.00037377 | 0.0019781 | 0.0054218 | 0.016968 | 0.00067495 | 0.00042723 | 0.002196 | -0.0032151 | -0.0045117 | -0.0012561 | -55.0781 | 65.5289 | -57.312 | 65.3824 | -56.6025 | -57.074 | -56.369 | -55.9982 | 65.5838 | -57.2617 | -57.1793 | -57.1838 | -57.2891 | -56.9916 | -0.05951 | -0.009155 | -0.15564 | 0.65002 | 0.88348 | 0.17853 | 0.94299 | 0.23804 | -0.009156 | 0.045776 | -122.7173 | 0.068664 | 0.26093 | -0.036622 | 0.27008 | -0.027466 | 0.70953 | 122.6944 | 0.07782 | 0.082398 | 122.8409 | 122.8455 | 122.7814 | 122.8363 | -122.85 | -122.7997 | 122.6349 | 0.073242 | 2.1744 | 1.2543
1992.1719 | 123.0881 | -57.2296 | 65.5609 | -0.091095 | -0.0013009 | 0.060957 | 0.068832 | -0.00090783 | 0.0019781 | 0.0062762 | 0.026123 | 0.00088875 | -0.00042717 | 0.0017688 | -0.0030013 | -0.0034437 | 0.0025891 | -55.0369 | 65.5426 | -57.2845 | 65.4236 | -56.5613 | -57.0236 | -56.3416 | -55.9616 | 65.5701 | -57.2617 | -57.1381 | -57.1335 | -57.2342 | -56.9733 | -0.054932 | -0.01831 | -0.13733 | 0.66833 | 0.88806 | 0.20599 | 0.94299 | 0.26093 | -0.032044 | 0.009155 | -122.699 | 0.09613 | 0.25635 | -0.004578 | 0.28839 | 0.027466 | 0.72327 | 122.7081 | 0.12817 | 0.1236 | 122.8271 | 122.8317 | 122.7722 | 122.7997 | -122.8455 | -122.8226 | 122.6532 | 0.091552 | 2.1927 | 1.268
1993.1719 | 123.0927 | -57.2113 | 65.593 | -0.083466 | -0.00087374 | 0.063094 | 0.070541 | 0.00016017 | 0.0011237 | 0.0062762 | 0.023071 | 0.0023839 | 0.00042723 | 0.00027342 | -0.00022431 | -0.0062207 | 0.00045294 | -55.0232 | 65.5518 | -57.3074 | 65.451 | -56.5063 | -56.987 | -56.3049 | -55.8929 | 65.5746 | -57.2617 | -57.1152 | -57.1243 | -57.1976 | -56.9458 | -0.09613 | -0.041199 | -0.14191 | 0.70496 | 0.90637 | 0.2243 | 1.0025 | 0.32043 | -0.050354 | -0.018311 | -122.7081 | 0.086975 | 0.2655 | 0.013733 | 0.31586 | 0.064087 | 0.80109 | 122.7585 | 0.13733 | 0.14648 | 122.8592 | 122.8363 | 122.7631 | 122.7859 | -122.9004 | -122.8546 | 122.6624 | 0.096131 | 2.1881 | 1.3184
1994.1719 | 123.0972 | -57.2159 | 65.5701 | -0.037689 | -1.9142e-05 | 0.062666 | 0.067336 | 0.0018692 | -0.00079891 | 0.0069172 | 0.026123 | 0.00088875 | -0.00042717 | -0.0037854 | -0.0027877 | -0.0055799 | -0.0029651 | -55.0369 | 65.5518 | -57.3074 | 65.4373 | -56.5292 | -57.0236 | -56.3141 | -55.9341 | 65.5746 | -57.2617 | -57.1106 | -57.1198 | -57.2159 | -56.9504 | -0.091553 | -0.01831 | -0.13275 | 0.68665 | 0.90179 | 0.19226 | 0.99335 | 0.28381 | -0.045777 | 0.004578 | -122.6807 | 0.09613 | 0.2655 | 0 | 0.31128 | 0.045777 | 0.7782 | 122.7448 | 0.14191 | 0.15106 | 122.8592 | 122.8363 | 122.7676 | 122.7905 | -122.8775 | -122.8317 | 122.6532 | 0.10529 | 2.179 | 1.2817
1995.1719 | 123.0743 | -57.2205 | 65.5655 | -0.052948 | -0.00066014 | 0.064375 | 0.069686 | 0.00016017 | 0.00026909 | 0.0045672 | 0.035278 | 0.00024775 | 0.0014954 | -0.00036738 | -0.0034287 | -0.0047253 | 0.00088014 | -55.0415 | 65.5518 | -57.312 | 65.4236 | -56.5475 | -57.0419 | -56.337 | -55.957 | 65.5838 | -57.2754 | -57.1426 | -57.1564 | -57.2433 | -56.9595 | -0.091553 | -0.013733 | -0.14191 | 0.67291 | 0.88348 | 0.17853 | 0.97504 | 0.27008 | -0.054932 | 0.01831 | -122.7081 | 0.064087 | 0.26093 | -0.022888 | 0.31586 | 0.032044 | 0.76447 | 122.7356 | 0.11902 | 0.13275 | 122.8638 | 122.8592 | 122.7722 | 122.8043 | -122.8775 | -122.8409 | 122.644 | 0.07782 | 2.179 | 1.2634
1996.1719 | 123.0743 | -57.2159 | 65.5518 | -0.12924 | -0.00066014 | 0.060316 | 0.067763 | -0.0024032 | 0.0039007 | 0.0049946 | 0.0078126 | -0.00017945 | 0.00021363 | 0.0054004 | -0.0010787 | -0.0053663 | 0.0010937 | -55.0369 | 65.5563 | -57.312 | 65.4144 | -56.5567 | -57.0374 | -56.3507 | -55.9525 | 65.5563 | -57.28 | -57.1472 | -57.1426 | -57.2617 | -56.9595 | -0.096131 | 0.004577 | -0.13733 | 0.65918 | 0.86517 | 0.17853 | 0.9613 | 0.27466 | -0.064087 | 0.004577 | -122.699 | 0.073242 | 0.25635 | -0.045777 | 0.32043 | 0.01831 | 0.75531 | 122.7264 | 0.13733 | 0.13275 | 122.8683 | 122.8363 | 122.7722 | 122.7722 | -122.8638 | -122.8317 | 122.6303 | 0.068664 | 2.179 | 1.2634
1997.1719 | 123.0515 | -57.2388 | 65.5563 | -0.083466 | -0.00023294 | 0.06288 | 0.0699 | -0.00090783 | 0.0043281 | 0.0081988 | -0.0043946 | -0.00017945 | -0.001709 | 0.001128 | -0.0032151 | -0.0038709 | -0.0025379 | -55.0461 | 65.5609 | -57.312 | 65.4327 | -56.5796 | -57.0511 | -56.3553 | -55.9753 | 65.5746 | -57.2891 | -57.1472 | -57.1747 | -57.2662 | -56.9778 | -0.073242 | 0.004578 | -0.1236 | 0.65918 | 0.88348 | 0.18768 | 0.95673 | 0.26093 | -0.050354 | 0.018311 | -122.7036 | 0.064087 | 0.26093 | -0.027465 | 0.31128 | 0.022889 | 0.73242 | 122.7448 | 0.11444 | 0.14191 | 122.8729 | 122.8638 | 122.7997 | 122.8134 | -122.8683 | -122.8455 | 122.6715 | 0.091553 | 2.1927 | 1.2634
1998.1719 | 123.0103 | -57.2388 | 65.538 | -0.12924 | 0.00062166 | 0.060316 | 0.069686 | -0.0030442 | 0.00069649 | 0.0052082 | -0.019653 | 0.00088875 | -0.00021357 | -0.002931 | -0.0023605 | -0.0034437 | -0.0029651 | -55.0735 | 65.538 | -57.3166 | 65.3915 | -56.6116 | -57.0877 | -56.3782 | -56.0165 | 65.5838 | -57.2754 | -57.106 | -57.1014 | -57.3303 | -57.0694 | -0.077819 | 0 | -0.14648 | 0.62714 | 0.8606 | 0.15106 | 0.93841 | 0.22888 | -0.036621 | 0.045776 | -122.644 | 0.13733 | 0.16937 | -0.091552 | 0.20599 | -0.054931 | 0.70496 | 122.7081 | 0.17395 | 0.16937 | 122.8546 | 122.8592 | 122.7768 | 122.8226 | -122.8546 | -122.8134 | 122.6303 | 0.13275 | 2.1652 | 1.2222
1999.1719 | 123.0927 | -57.2159 | 65.5563 | -0.045319 | 0.0012625 | 0.062453 | 0.069472 | -0.0032578 | 0.0011237 | 0.00414 | 0.013916 | 0.00067495 | -0.00064077 | -0.0014356 | -0.0010787 | -0.0025891 | -0.0012561 | -54.9911 | 65.5289 | -57.28 | 65.4968 | -56.4789 | -56.9641 | -56.3049 | -55.8975 | 65.593 | -57.2388 | -56.9778 | -57.0969 | -57.5455 | -57.1243 | -0.064087 | -0.027465 | -0.059509 | 0.737 | 0.91095 | 0.25177 | 0.97504 | 0.31586 | -0.022889 | 0.036622 | -122.5342 | 0.11902 | 0.091552 | -0.32959 | 0.11444 | -0.3067 | 0.80109 | 122.7768 | 0.14191 | 0.26093 | 122.8088 | 122.8317 | 122.7448 | 122.8088 | -122.8363 | -122.7951 | 122.7127 | 0.23804 | 2.2247 | 1.3184
2000.1719 | 123.0423 | -57.225 | 65.5838 | -0.091095 | -0.00044654 | 0.06288 | 0.070541 | -0.0045394 | 0.0026191 | 0.0037128 | -0.0013428 | 0.0011023 | -0.0012818 | 0.0013416 | -0.0034287 | -0.0049389 | -0.0010425 | -55.0415 | 65.5426 | -57.312 | 65.4373 | -56.5521 | -57.0374 | -56.3461 | -55.9525 | 65.5518 | -57.2388 | -57.1518 | -57.1426 | -57.2388 | -56.9458 | -0.086975 | -0.041198 | -0.14648 | 0.67291 | 0.87891 | 0.18768 | 0.96588 | 0.27466 | -0.013733 | -0.032043 | -122.7356 | 0.082398 | 0.27924 | -0.013733 | 0.29297 | 0 | 0.75989 | 122.7493 | 0.096131 | 0.086976 | 122.8546 | 122.7905 | 122.7676 | 122.7768 | -122.8958 | -122.8226 | 122.6624 | 0.073243 | 2.1835 | 1.2726
2001.1719 | 123.0743 | -57.2067 | 65.5609 | -0.1445 | -0.00087374 | 0.063521 | 0.070327 | 0.0027238 | 0.0026191 | 0.0054218 | -0.0013428 | 0.0028113 | -0.00064077 | 0.001128 | -0.0030013 | -0.0013073 | 0.0028027 | -55.0323 | 65.5426 | -57.3257 | 65.419 | -56.5521 | -57.0374 | -56.337 | -55.9616 | 65.5975 | -57.2571 | -57.1381 | -57.1381 | -57.2433 | -56.9687 | -0.11902 | -0.01831 | -0.14191 | 0.6546 | 0.86975 | 0.16937 | 0.98877 | 0.28839 | -0.050354 | 0.036621 | -122.699 | 0.068664 | 0.23804 | -0.036621 | 0.28839 | 0.013733 | 0.77362 | 122.7448 | 0.11902 | 0.11902 | 122.8683 | 122.8546 | 122.7493 | 122.8043 | -122.8867 | -122.818 | 122.6257 | 0.068664 | 2.1744 | 1.2451
2002.1719 | 123.0469 | -57.2113 | 65.5472 | -0.19028 | 0.00062166 | 0.062025 | 0.0699 | 0.00037377 | 0.0049689 | 0.0088398 | 0.010864 | 0.0015295 | -0.00021357 | -0.005708 | -0.0021469 | -0.0028027 | -0.00082886 | -55.0369 | 65.5197 | -57.2983 | 65.4282 | -56.5613 | -57.0648 | -56.3599 | -55.9708 | 65.5884 | -57.2433 | -57.1381 | -57.1609 | -57.2617 | -56.9824 | -0.086975 | -0.027466 | -0.11902 | 0.65002 | 0.85144 | 0.14648 | 0.93842 | 0.23346 | -0.032043 | 0.041199 | -122.6852 | 0.050354 | 0.22888 | -0.050354 | 0.26093 | -0.018311 | 0.737 | 122.7264 | 0.082397 | 0.10529 | 122.818 | 122.8317 | 122.731 | 122.7997 | -122.8455 | -122.7905 | 122.6395 | 0.073242 | 2.1744 | 1.2405
2003.1719 | 123.0606 | -57.225 | 65.5975 | -0.12161 | -0.00087374 | 0.061598 | 0.071609 | 0.0029374 | 0.0021917 | 0.0043536 | -0.01355 | 0.00088875 | -0.00064077 | -0.0033582 | -0.0019333 | -0.0042981 | -0.0061695 | -55.0415 | 65.5426 | -57.2983 | 65.4144 | -56.5796 | -57.0465 | -56.3828 | -55.9753 | 65.5975 | -57.2983 | -57.1655 | -57.1472 | -57.2525 | -56.9778 | -0.073242 | -0.054931 | -0.1831 | 0.64545 | 0.84229 | 0.17853 | 0.91553 | 0.25177 | -0.073242 | 0 | -122.7631 | 0.07782 | 0.24719 | -0.027465 | 0.32044 | 0.045777 | 0.71869 | 122.7127 | 0.15106 | 0.13275 | 122.8409 | 122.8958 | 122.7676 | 122.8226 | -122.8958 | -122.8958 | 122.6395 | 0.05951 | 2.1835 | 1.2497
2004.1719 | 123.0103 | -57.2159 | 65.5472 | -0.052948 | 0.0016899 | 0.063521 | 0.068618 | -0.0021896 | 0.0034735 | 0.005849 | -0.019653 | 0.0017431 | -0.00085457 | -0.0016492 | -0.0019333 | -0.0055799 | -0.0033923 | -55.0644 | 65.5243 | -57.3166 | 65.3824 | -56.6162 | -57.0831 | -56.4011 | -56.0303 | 65.5792 | -57.2937 | -57.1243 | -57.0786 | -57.3898 | -57.0557 | -0.10071 | -0.022888 | -0.16479 | 0.59967 | 0.81482 | 0.13275 | 0.91553 | 0.23346 | -0.07782 | 0.032044 | -122.6715 | 0.13733 | 0.16022 | -0.17395 | 0.23804 | -0.096131 | 0.70038 | 122.699 | 0.21515 | 0.16937 | 122.8409 | 122.8729 | 122.7402 | 122.7951 | -122.8638 | -122.8409 | 122.5983 | 0.091552 | 2.1515 | 1.1856
2005.1719 | 123.0927 | -57.2296 | 65.5518 | -0.052948 | 0.00040806 | 0.063094 | 0.070327 | -5.343e-05 | 0.0019781 | 0.0071308 | -0.01355 | 0.0023839 | 0.001709 | 0.00027342 | -0.0025741 | -0.0028027 | 2.554e-05 | -55.069 | 65.5289 | -57.3212 | 65.4007 | -56.6071 | -57.0923 | -56.369 | -56.012 | 65.5792 | -57.2891 | -57.1793 | -57.2067 | -57.312 | -57.1198 | -0.091553 | -0.022888 | -0.15106 | 0.62256 | 0.86059 | 0.13733 | 0.95215 | 0.22888 | -0.05951 | 0.027466 | -122.731 | 0.022888 | 0.10986 | -0.082398 | 0.16937 | -0.022888 | 0.71411 | 122.7219 | 0.082398 | 0.10986 | 122.85 | 122.8683 | 122.7585 | 122.8088 | -122.8729 | -122.8409 | 122.6303 | 0.050354 | 2.1606 | 1.2177
2006.1719 | 123.0515 | -57.2067 | 65.5518 | -0.11398 | -0.00044654 | 0.060103 | 0.070327 | -0.00090783 | 0.00091009 | 0.00414 | -0.0074462 | 0.00067495 | -0.00042717 | -0.0052808 | -0.0015061 | -0.0049389 | -0.0012561 | -55.0003 | 65.538 | -57.2937 | 65.4465 | -56.5384 | -57.0145 | -56.3416 | -55.9341 | 65.5838 | -57.2617 | -57.1335 | -57.1289 | -57.2388 | -56.9412 | -0.086975 | -0.013733 | -0.10529 | 0.66834 | 0.86517 | 0.19226 | 0.95215 | 0.27924 | -0.054932 | 0.032043 | -122.6852 | 0.07782 | 0.2655 | -0.032044 | 0.32043 | 0.022888 | 0.75531 | 122.7402 | 0.13275 | 0.12817 | 122.8317 | 122.8455 | 122.7448 | 122.7905 | -122.8455 | -122.8134 | 122.6532 | 0.073242 | 2.2064 | 1.2726
2007.1719 | 123.0515 | -57.2205 | 65.5334 | -0.11398 | -0.0013009 | 0.063307 | 0.070968 | -0.0032578 | 0.00091009 | 0.0047808 | -0.019653 | 3.4148e-05 | -0.0010682 | 0.0026232 | -0.0015061 | -0.0055799 | -0.0010425 | -55.0186 | 65.5426 | -57.3212 | 65.451 | -56.543 | -57.0419 | -56.337 | -55.9296 | 65.5655 | -57.2617 | -57.1198 | -57.1289 | -57.2479 | -56.9595 | -0.10071 | 0.009156 | -0.082397 | 0.67749 | 0.88348 | 0.17853 | 0.98419 | 0.27924 | -0.041199 | 0.032044 | -122.6532 | 0.091553 | 0.26093 | -0.027466 | 0.30212 | 0.013733 | 0.7782 | 122.7722 | 0.13275 | 0.14191 | 122.8638 | 122.8271 | 122.7631 | 122.7859 | -122.8546 | -122.7951 | 122.6715 | 0.10071 | 2.2018 | 1.2909
2008.1719 | 123.0423 | -57.2159 | 65.5609 | -0.052948 | 0.00062166 | 0.060316 | 0.071181 | -0.0015488 | 0.00026909 | 0.0054218 | -0.0013428 | 0.00088875 | 0.0012818 | 0.002196 | -0.0025741 | -0.0040845 | 0.00088014 | -55.0186 | 65.538 | -57.3029 | 65.4236 | -56.5613 | -57.0419 | -56.3461 | -55.9662 | 65.6113 | -57.2937 | -57.1381 | -57.1381 | -57.2525 | -56.9595 | -0.086975 | -0.022888 | -0.13733 | 0.6546 | 0.86975 | 0.17395 | 0.95673 | 0.26093 | -0.07782 | 0.050354 | -122.699 | 0.077819 | 0.25635 | -0.036621 | 0.33417 | 0.041199 | 0.74158 | 122.7264 | 0.15564 | 0.15564 | 122.8409 | 122.905 | 122.7539 | 122.8271 | -122.8638 | -122.8546 | 122.6395 | 0.077819 | 2.1973 | 1.2497
2009.1719 | 123.0881 | -57.2113 | 65.5563 | -0.083466 | 0.00019446 | 0.061598 | 0.068404 | 0.0012284 | 0.0028327 | 0.0084124 | 0.001709 | 0.00067495 | -0.00085457 | 0.0017688 | -0.00065151 | -0.0028027 | 0.0047253 | -55.0232 | 65.538 | -57.312 | 65.4419 | -56.5567 | -57.0419 | -56.3416 | -55.9753 | 65.5792 | -57.28 | -57.1381 | -57.1426 | -57.2525 | -56.9687 | -0.10071 | -0.01831 | -0.11444 | 0.6546 | 0.86975 | 0.16937 | 0.97046 | 0.27008 | -0.068664 | 0.022889 | -122.6944 | 0.068665 | 0.24262 | -0.041198 | 0.31128 | 0.027466 | 0.75531 | 122.7539 | 0.13733 | 0.14191 | 122.85 | 122.8592 | 122.7493 | 122.7905 | -122.8683 | -122.8363 | 122.6532 | 0.073242 | 2.1881 | 1.236
2010.1719 | 123.1018 | -57.193 | 65.5563 | -0.12161 | -1.9142e-05 | 0.062239 | 0.069259 | -0.0011214 | 0.00048269 | 0.0064898 | 0.0047608 | 0.0013159 | 0.00042723 | 0.0043322 | -0.0019333 | -0.0047253 | 0.00045294 | -54.9911 | 65.5518 | -57.2708 | 65.4602 | -56.4972 | -56.9778 | -56.3049 | -55.8929 | 65.5746 | -57.2617 | -57.0877 | -57.0831 | -57.1976 | -56.9366 | -0.07782 | -0.004577 | -0.09613 | 0.6958 | 0.88806 | 0.21515 | 0.96588 | 0.29297 | -0.068665 | 0.018311 | -122.644 | 0.10986 | 0.25635 | -0.004578 | 0.32501 | 0.064087 | 0.77362 | 122.731 | 0.17853 | 0.17395 | 122.8226 | 122.8363 | 122.7448 | 122.7676 | -122.8271 | -122.818 | 122.6532 | 0.10529 | 2.2018 | 1.3
2011.1719 | 123.024 | -57.2388 | 65.5426 | -0.13687 | -0.00023294 | 0.060957 | 0.070541 | -0.001976 | 0.0013373 | 0.0054218 | -0.0043946 | -0.0010339 | -0.0010682 | -0.0014356 | -0.00022431 | -0.0036573 | -0.0023243 | -55.0507 | 65.538 | -57.3074 | 65.387 | -56.6208 | -57.0786 | -56.3965 | -55.9067 | 65.6021 | -57.225 | -57.1838 | -57.1655 | -57.3166 | -57.0236 | -0.068664 | -0.004578 | -0.15564 | 0.61798 | 0.84229 | 0.16022 | 0.91095 | 0.22888 | 0.013733 | 0.059509 | -122.7264 | 0.073243 | 0.21515 | -0.077819 | 0.20142 | -0.091552 | 0.68664 | 122.6944 | 0.05951 | 0.041199 | 122.8455 | 122.8271 | 122.7768 | 122.8409 | -122.85 | -122.7676 | 122.6257 | 0.054932 | 2.1881 | 1.3321
2012.1719 | 123.0286 | -57.225 | 65.538 | -0.091095 | 0.00083526 | 0.062666 | 0.069472 | -0.005394 | 0.0017645 | 0.0084124 | -0.03186 | -0.0014613 | 0.00085443 | -0.00058098 | -0.0010787 | -0.0036573 | -0.0016833 | -55.0461 | 65.538 | -57.3074 | 65.387 | -56.6071 | -57.0923 | -56.3873 | -56.0028 | 65.5884 | -57.2845 | -57.2067 | -57.2159 | -57.2983 | -57.0236 | -0.082397 | 0 | -0.15106 | 0.61798 | 0.83771 | 0.13275 | 0.9201 | 0.21515 | -0.059509 | 0.050354 | -122.7448 | 0.009156 | 0.20142 | -0.073242 | 0.26093 | -0.013733 | 0.70038 | 122.6944 | 0.068665 | 0.07782 | 122.8455 | 122.8729 | 122.7631 | 122.8134 | -122.8455 | -122.8226 | 122.612 | 0.018311 | 2.179 | 1.2222
2013.1719 | 123.0606 | -57.225 | 65.5472 | -0.068207 | -1.9142e-05 | 0.063734 | 0.070113 | 0.001442 | 0.0051825 | 0.0090534 | -0.0074462 | -0.00082025 | 0.001068 | 0.0013416 | -0.0027877 | -0.0032301 | 0.0010937 | -54.9545 | 65.5563 | -57.28 | 65.4785 | -56.4835 | -57.0007 | -56.3095 | -55.7144 | 65.625 | -57.2067 | -57.1014 | -57.2067 | -57.2113 | -56.9504 | -0.054931 | 0.009155 | -0.068664 | 0.74158 | 0.91553 | 0.22431 | 0.97046 | 0.27924 | 0.018311 | 0.07782 | -122.6486 | 0.018311 | 0.27466 | 0.013733 | 0.25635 | -0.004578 | 0.79651 | 122.7585 | 0 | 0.10529 | 122.8363 | 122.8317 | 122.7814 | 122.85 | -122.8271 | -122.7539 | 122.7036 | 0.1236 | 2.2705 | 1.5106
2014.1719 | 123.0789 | -57.225 | 65.5609 | -0.098725 | -0.00044654 | 0.060316 | 0.072036 | 0.00016017 | 0.0019781 | 0.0043536 | -0.016602 | 0.0011023 | -0.00042717 | -0.0042126 | -0.0015061 | -0.0019483 | -0.0012561 | -54.9866 | 65.538 | -57.2845 | 65.4419 | -56.5521 | -57.0145 | -56.3416 | -55.9387 | 65.5838 | -57.2571 | -57.1198 | -57.1106 | -57.2342 | -56.9366 | -0.059509 | -0.022888 | -0.11902 | 0.67291 | 0.88348 | 0.21057 | 0.94299 | 0.27008 | -0.032043 | 0.022888 | -122.6807 | 0.11444 | 0.28839 | -0.009155 | 0.32043 | 0.022888 | 0.73242 | 122.7264 | 0.14648 | 0.13733 | 122.8226 | 122.8409 | 122.7631 | 122.8088 | -122.8455 | -122.818 | 122.6669 | 0.10529 | 2.2385 | 1.2863
2015.1719 | 122.9645 | -57.2021 | 65.5426 | -0.083466 | -0.00066014 | 0.063948 | 0.071609 | -5.343e-05 | 0.0030463 | 0.0049946 | 0.0047608 | -0.00060665 | 0.0021362 | 0.00091422 | -0.0021469 | -0.0036573 | 0.0021619 | -54.9683 | 65.5518 | -57.2617 | 65.4831 | -56.4697 | -56.9595 | -56.2958 | -55.8884 | 65.5884 | -57.2479 | -57.1198 | -57.0145 | -56.8909 | -56.7215 | -0.05951 | 0.009155 | -0.05951 | 0.73242 | 0.90637 | 0.24261 | 0.96588 | 0.30212 | -0.045777 | 0.045776 | -122.6624 | 0.18768 | 0.48065 | 0.31128 | 0.52643 | 0.35706 | 0.79193 | 122.7448 | 0.23346 | 0.12817 | 122.8134 | 122.8363 | 122.7539 | 122.7905 | -122.8043 | -122.7905 | 122.6852 | 0.082397 | 2.2339 | 1.3138
2016.1719 | 123.0606 | -57.2159 | 65.5792 | -0.12161 | 0.00040806 | 0.061171 | 0.067336 | 0.00080117 | 0.0041143 | 0.0039264 | -0.0043946 | -0.00060665 | 0.0012818 | -0.00015378 | -0.0010787 | -0.0028027 | 0.00045294 | -55.0049 | 65.5334 | -57.312 | 65.4327 | -56.5567 | -57.0099 | -56.3507 | -55.9525 | 65.5792 | -57.2617 | -57.1335 | -57.1289 | -57.2296 | -56.955 | -0.096131 | -0.045777 | -0.14648 | 0.65918 | 0.86517 | 0.20599 | 0.9613 | 0.30212 | -0.045777 | 0 | -122.7127 | 0.086975 | 0.26093 | -0.013733 | 0.3067 | 0.032044 | 0.75531 | 122.7448 | 0.13275 | 0.12817 | 122.8455 | 122.8409 | 122.7493 | 122.7951 | -122.8912 | -122.8409 | 122.6486 | 0.082397 | 2.211 | 1.2634
2017.1719 | 123.0469 | -57.2388 | 65.5792 | -0.045319 | -0.0013009 | 0.063307 | 0.069686 | -0.0032578 | 0.0019781 | 0.0084124 | -0.0043946 | 0.0021703 | 0.00064083 | -0.0031446 | 0.00041649 | -0.0051527 | -0.0014697 | -55.0095 | 65.5334 | -57.2937 | 65.4373 | -56.5567 | -57.0328 | -56.3599 | -55.9616 | 65.5838 | -57.2708 | -57.1289 | -57.1243 | -57.2525 | -56.955 | -0.054931 | -0.045777 | -0.14191 | 0.68207 | 0.87891 | 0.20599 | 0.93384 | 0.26093 | -0.032043 | 0.004577 | -122.7081 | 0.11444 | 0.28381 | -0.013732 | 0.31586 | 0.018311 | 0.737 | 122.731 | 0.14648 | 0.14191 | 122.8271 | 122.8546 | 122.7722 | 122.8226 | -122.8729 | -122.85 | 122.6761 | 0.10986 | 2.2293 | 1.2772
2018.1719 | 123.0331 | -57.2342 | 65.5563 | -0.10635 | 0.0010489 | 0.062239 | 0.071822 | 0.0027238 | 0.0047553 | 0.0077716 | -0.050171 | 0.0011023 | -0.00064077 | 0.007323 | -0.0017197 | -0.0036573 | -0.0010425 | -55.0278 | 65.5197 | -57.312 | 65.3915 | -56.6071 | -57.0282 | -56.2775 | -56.0577 | 65.5792 | -57.28 | -57.2021 | -57.2021 | -57.3074 | -56.987 | -0.07782 | -0.036621 | -0.16479 | 0.62714 | 0.95673 | 0.20599 | 1.0345 | 0.28381 | -0.045776 | 0.022889 | -122.7585 | 0.032044 | 0.24719 | -0.073242 | 0.29297 | -0.027466 | 0.70496 | 122.7036 | 0.07782 | 0.07782 | 122.8317 | 122.8592 | 122.7539 | 122.8134 | -122.8683 | -122.8363 | 122.6257 | 0.032044 | 2.2064 | 1.1765
2019.1719 | 123.0011 | -57.2479 | 65.5701 | -0.045319 | -0.00087374 | 0.061598 | 0.071609 | 0.0016556 | 0.0015509 | 0.0086262 | -0.098999 | 0.0015295 | 0.00021363 | 0.005614 | -0.0027877 | -0.0030163 | 0.0021619 | -54.982 | 65.5655 | -57.3303 | 65.3915 | -56.5887 | -57.0786 | -56.4194 | -55.9937 | 65.6204 | -57.2937 | -57.193 | -57.225 | -57.3212 | -57.0145 | -0.082397 | -0.004577 | -0.17853 | 0.65918 | 0.82855 | 0.16937 | 0.91095 | 0.25177 | -0.045776 | 0.050354 | -122.7631 | 0.022888 | 0.23346 | -0.073242 | 0.27924 | -0.027466 | 0.74158 | 122.7219 | 0.068664 | 0.10071 | 122.8958 | 122.9141 | 122.8134 | 122.8683 | -122.9004 | -122.8638 | 122.6395 | 0.054932 | 2.2659 | 1.2543
2020.1719 | 123.0469 | -57.2205 | 65.5701 | -0.052948 | 0.00062166 | 0.063948 | 0.070541 | -0.00090783 | 0.00091009 | 0.0069172 | -0.0043946 | 0.0017431 | 2.8e-08 | -0.0044262 | -0.0010787 | -0.0038709 | -0.00082886 | -54.9774 | 65.538 | -57.2983 | 65.4556 | -56.5155 | -57.0053 | -56.3461 | -55.9113 | 65.5975 | -57.2662 | -57.1152 | -57.106 | -57.2021 | -56.9366 | -0.07782 | -0.032043 | -0.11444 | 0.70496 | 0.87433 | 0.21515 | 0.95215 | 0.29297 | -0.045776 | 0.027466 | -122.6852 | 0.11444 | 0.28381 | 0.018311 | 0.32959 | 0.064087 | 0.78278 | 122.7539 | 0.16022 | 0.15106 | 122.8363 | 122.8638 | 122.7585 | 122.818 | -122.8683 | -122.8363 | 122.6761 | 0.10529 | 2.243 | 1.3092
2021.1719 | 123.056 | -57.2296 | 65.5746 | -0.068207 | 0.00040806 | 0.062453 | 0.0699 | -0.00026703 | 0.0015509 | 0.0045672 | 0.02002 | -0.00082025 | 0.0025634 | 0.0013416 | -0.0032151 | -0.0028027 | 0.00045294 | -54.982 | 65.5334 | -57.2662 | 65.451 | -56.5384 | -57.0099 | -56.3278 | -55.9387 | 65.5975 | -57.2571 | -57.0923 | -57.1106 | -57.193 | -56.9504 | -0.036621 | -0.041199 | -0.1236 | 0.69122 | 0.90179 | 0.21973 | 0.93841 | 0.25635 | -0.027466 | 0.022888 | -122.6669 | 0.11902 | 0.27924 | 0.036621 | 0.3067 | 0.064087 | 0.72784 | 122.7173 | 0.14648 | 0.1648 | 122.7997 | 122.8546 | 122.7631 | 122.8271 | -122.8409 | -122.8317 | 122.6807 | 0.13733 | 2.2476 | 1.2909
2022.1719 | 123.0652 | -57.2021 | 65.5426 | -0.091095 | 0.0010489 | 0.062239 | 0.0699 | 0.0016556 | 0.0013373 | 0.0045672 | -0.0013428 | 0.00088875 | 0.00042723 | 0.0047594 | -0.0044967 | -0.0055799 | 0.00045294 | -54.9454 | 65.538 | -57.2754 | 65.4968 | -56.4926 | -56.9595 | -56.3278 | -55.9113 | 65.5884 | -57.2617 | -57.0419 | -57.4127 | -57.2891 | -56.9183 | -0.073243 | -0.004578 | -0.045777 | 0.70953 | 0.87433 | 0.24261 | 0.94757 | 0.31586 | -0.05951 | 0.045776 | -122.5845 | -0.21057 | 0.28381 | -0.086976 | 0.34332 | -0.027466 | 0.78278 | 122.7722 | -0.15106 | 0.21973 | 122.8134 | 122.85 | 122.7402 | 122.7905 | -122.818 | -122.8043 | 122.699 | 0.16022 | 2.2568 | 1.2909
2023.1719 | 123.1567 | -57.2067 | 65.6616 | -0.12161 | -0.0015145 | 0.061598 | 0.069259 | -0.0015488 | 0.0036871 | 0.007558 | 0.035278 | -0.00039305 | 0.0014954 | 0.0060412 | -0.0034287 | -0.0042981 | -0.0014697 | -54.9545 | 65.5655 | -57.3074 | 65.4785 | -56.488 | -56.9733 | -56.3004 | -55.8792 | 65.5838 | -57.2342 | -57.1198 | -57.106 | -57.1976 | -57.0053 | -0.10071 | -0.09613 | -0.1831 | 0.71869 | 0.90637 | 0.23346 | 1.0071 | 0.33417 | -0.027466 | -0.07782 | -122.7814 | 0.10071 | 0.20142 | 0.009155 | 0.22888 | 0.036621 | 0.8194 | 122.7859 | 0.12817 | 0.11444 | 122.8729 | 122.818 | 122.7722 | 122.7905 | -122.9691 | -122.8958 | 122.6852 | 0.086975 | 2.2522 | 1.3275
2024.1719 | 122.9416 | -57.2617 | 65.5746 | -0.052948 | 0.00083526 | 0.063948 | 0.073318 | 0.003151 | 0.0032599 | 0.0077716 | -0.11121 | 0.0028113 | -0.0012818 | -0.00229 | -0.00086511 | -0.00066648 | 0.0015209 | -55.0049 | 65.5655 | -57.3395 | 65.3641 | -56.6162 | -57.106 | -56.4606 | -56.0394 | 65.6296 | -57.2937 | -57.2159 | -57.2617 | -57.3761 | -57.0557 | -0.07782 | -0.009155 | -0.21057 | 0.64545 | 0.80109 | 0.15564 | 0.87891 | 0.23346 | -0.032043 | 0.054932 | -122.7905 | 0 | 0.20599 | -0.11444 | 0.23804 | -0.082398 | 0.72327 | 122.7036 | 0.032043 | 0.07782 | 122.905 | 122.9233 | 122.8271 | 122.8912 | -122.9141 | -122.8683 | 122.6257 | 0.045777 | 2.2568 | 1.2222
2025.1719 | 123.0331 | -57.2388 | 65.5426 | -0.11398 | -0.00023294 | 0.06053 | 0.068618 | 0.00037377 | 0.0049689 | 0.0032856 | 0.001709 | 0.00088875 | 0.001709 | -0.0016492 | -0.00022431 | -0.0038709 | -0.00018806 | -55.0552 | 65.5563 | -57.2891 | 65.4007 | -56.6071 | -56.987 | -56.2866 | -56.0532 | 65.5701 | -57.28 | -57.2113 | -57.1884 | -57.2983 | -56.987 | -0.050354 | 0.013732 | -0.14191 | 0.63171 | 0.95215 | 0.25177 | 1.0025 | 0.30212 | -0.041198 | 0.027465 | -122.7539 | 0.050354 | 0.25177 | -0.059509 | 0.29297 | -0.018311 | 0.68207 | 122.6898 | 0.091552 | 0.068664 | 122.8455 | 122.85 | 122.7951 | 122.8088 | -122.8317 | -122.8226 | 122.6395 | 0.027466 | 2.1835 | 1.1856
2026.1719 | 123.0194 | -57.2342 | 65.5289 | -0.075836 | 0.0021171 | 0.060957 | 0.070541 | -0.003685 | 0.0011237 | 0.0043536 | 0.001709 | 0.00067495 | -0.0012818 | -0.0042126 | -0.00022431 | -0.0034437 | 0.0021619 | -55.0323 | 65.5197 | -57.312 | 65.3732 | -56.6254 | -57.0923 | -56.4011 | -56.0211 | 65.5701 | -57.2708 | -57.1976 | -57.2159 | -57.2937 | -56.987 | -0.07782 | -0.009156 | -0.15564 | 0.60883 | 0.83313 | 0.14191 | 0.91095 | 0.21973 | -0.036621 | 0.041198 | -122.7264 | 0.018311 | 0.24719 | -0.059509 | 0.28381 | -0.022888 | 0.68665 | 122.6852 | 0.054932 | 0.073242 | 122.8317 | 122.8409 | 122.7539 | 122.8043 | -122.8409 | -122.7997 | 122.6074 | 0.036621 | 2.2018 | 1.2131
2027.1719 | 123.0698 | -57.2205 | 65.5655 | -0.091095 | -1.9142e-05 | 0.063521 | 0.070113 | -0.0013352 | 0.00091009 | 0.0034992 | -0.0013428 | 0.0017431 | -0.00042717 | 0.0030506 | -0.00086511 | -0.0021619 | -0.00061526 | -54.9316 | 65.5609 | -57.28 | 65.4648 | -56.4835 | -56.987 | -56.3232 | -55.9113 | 65.593 | -57.225 | -57.1243 | -57.0694 | -57.2708 | -56.9916 | -0.059509 | -0.004578 | -0.10071 | 0.737 | 0.89722 | 0.23346 | 0.95673 | 0.29297 | -0.004578 | 0.027466 | -122.6898 | 0.15106 | 0.22888 | -0.050354 | 0.23346 | -0.045776 | 0.79651 | 122.7448 | 0.15564 | 0.10071 | 122.8409 | 122.818 | 122.7814 | 122.8134 | -122.8455 | -122.7905 | 122.6852 | 0.09613 | 2.2888 | 1.3092
2028.1719 | 123.056 | -57.2021 | 65.5701 | -0.10635 | 0.0019035 | 0.062025 | 0.069686 | -0.00026703 | 0.0021917 | 0.007558 | 0.02002 | 0.00067495 | -0.00042717 | 0.00048702 | -0.0025741 | -0.0051527 | 0.0023755 | -54.9866 | 65.5472 | -57.2937 | 65.4373 | -56.543 | -57.0007 | -56.3507 | -55.9479 | 65.5975 | -57.2617 | -57.1198 | -57.1106 | -57.2113 | -56.9229 | -0.091553 | -0.022888 | -0.13275 | 0.65918 | 0.85144 | 0.20142 | 0.94299 | 0.29297 | -0.05951 | 0.027466 | -122.6898 | 0.091552 | 0.27923 | -0.009156 | 0.33874 | 0.050354 | 0.75073 | 122.731 | 0.15106 | 0.14191 | 122.8409 | 122.8592 | 122.7493 | 122.7997 | -122.8638 | -122.8317 | 122.6395 | 0.082397 | 2.2156 | 1.2543
2029.1719 | 122.937 | -57.2708 | 65.5838 | -0.075836 | -0.00066014 | 0.06288 | 0.071609 | 0.00251 | 0.0032599 | 0.0039264 | -0.095947 | 0.0019567 | -0.00085457 | 0.0051868 | -0.0032151 | -0.0032301 | 0.0017345 | -55.0095 | 65.538 | -57.3166 | 65.3549 | -56.6345 | -57.1472 | -56.488 | -56.0486 | 65.625 | -57.2891 | -57.2021 | -57.2708 | -57.399 | -57.0557 | -0.045776 | -0.045776 | -0.22888 | 0.63629 | 0.78278 | 0.1236 | 0.82855 | 0.16937 | -0.018311 | 0.041199 | -122.7859 | 0 | 0.21515 | -0.12817 | 0.23346 | -0.10986 | 0.68207 | 122.6715 | 0.018311 | 0.086976 | 122.8546 | 122.9141 | 122.8088 | 122.8958 | -122.9004 | -122.8729 | 122.6257 | 0.068665 | 2.2614 | 1.2222
2030.1719 | 123.0515 | -57.2067 | 65.5518 | -0.045319 | 0.0010489 | 0.060744 | 0.068832 | -0.004753 | 0.0024053 | 0.0043536 | 0.032227 | 0.0011023 | 2.8e-08 | -0.00464 | -0.0015061 | -0.0042981 | -0.0048877 | -54.9591 | 65.538 | -57.2937 | 65.4648 | -56.488 | -56.9595 | -56.2912 | -55.8838 | 65.5884 | -57.2205 | -57.1014 | -57.1152 | -57.2021 | -56.9458 | -0.086975 | -0.013733 | -0.086975 | 0.71869 | 0.91553 | 0.24719 | 1.0025 | 0.33417 | -0.013733 | 0.036621 | -122.6532 | 0.091553 | 0.26093 | 0.004578 | 0.27466 | 0.018311 | 0.80566 | 122.7585 | 0.10529 | 0.11902 | 122.8317 | 122.8088 | 122.7448 | 122.7951 | -122.8455 | -122.7722 | 122.6715 | 0.10529 | 2.2476 | 1.3229
2031.1719 | 123.0469 | -57.2021 | 65.5701 | -0.083466 | 0.00083526 | 0.061171 | 0.067977 | 0.0029374 | 0.0011237 | 0.0064898 | 0.016968 | 0.00067495 | 0.00064083 | 0.00027342 | -0.0012925 | -0.0028027 | -0.0012561 | -54.9911 | 65.5426 | -57.2754 | 65.4144 | -56.5796 | -57.0374 | -56.3736 | -55.9937 | 65.593 | -57.2571 | -57.1518 | -57.1472 | -57.2479 | -56.9595 | -0.073243 | -0.027465 | -0.15564 | 0.62256 | 0.82855 | 0.16479 | 0.90179 | 0.23804 | -0.054932 | 0.022889 | -122.7219 | 0.054931 | 0.24261 | -0.045777 | 0.29755 | 0.009155 | 0.6958 | 122.6898 | 0.10986 | 0.10529 | 122.818 | 122.85 | 122.7448 | 122.7951 | -122.8455 | -122.8271 | 122.6166 | 0.050354 | 2.211 | 1.2085
2032.1719 | 123.0515 | -57.2113 | 65.5472 | -0.12161 | 0.0031851 | 0.061171 | 0.0699 | -0.004753 | 0.0021917 | 0.0071308 | 0.023071 | -0.00017945 | -0.00085457 | -0.0048536 | -0.0012925 | -0.0047253 | 0.0017345 | -55.0186 | 65.5655 | -57.2983 | 65.4236 | -56.5887 | -57.0465 | -56.3736 | -55.9753 | 65.5609 | -57.2617 | -57.1426 | -57.1701 | -57.2479 | -56.9595 | -0.086975 | 0.018311 | -0.1236 | 0.62256 | 0.83771 | 0.16479 | 0.92468 | 0.25177 | -0.050354 | 0.013733 | -122.6898 | 0.041199 | 0.25177 | -0.036621 | 0.30212 | 0.013733 | 0.70953 | 122.7219 | 0.091553 | 0.11902 | 122.8638 | 122.8226 | 122.7768 | 122.7722 | -122.8455 | -122.8088 | 122.6349 | 0.068665 | 2.1927 | 1.236
2033.1719 | 123.0606 | -57.2159 | 65.5746 | -0.19028 | -0.00023294 | 0.063307 | 0.068832 | -0.00048063 | 0.0013373 | 0.007558 | 0.041382 | -0.0016749 | 0.00042723 | -0.0010084 | -0.0019333 | -0.0036573 | 0.00088014 | -55.0095 | 65.5426 | -57.3029 | 65.4099 | -56.5979 | -57.0694 | -56.3782 | -56.0074 | 65.593 | -57.2754 | -57.1564 | -57.1518 | -57.2708 | -56.9641 | -0.086975 | -0.032043 | -0.16479 | 0.61798 | 0.83771 | 0.14648 | 0.92468 | 0.23346 | -0.05951 | 0.018311 | -122.731 | 0.064087 | 0.25177 | -0.054932 | 0.31128 | 0.004578 | 0.70496 | 122.7127 | 0.1236 | 0.11902 | 122.8455 | 122.8683 | 122.7585 | 122.8088 | -122.8775 | -122.85 | 122.6257 | 0.059509 | 2.2064 | 1.2085
2034.1719 | 123.0789 | -57.2113 | 65.5701 | -0.083466 | -0.00023294 | 0.063094 | 0.066909 | 0.0022964 | 0.0034735 | 0.0049946 | 0.041382 | 0.0013159 | 2.8e-08 | -0.00079478 | -0.0015061 | -0.0038709 | 0.00023934 | -54.9637 | 65.5518 | -57.3029 | 65.4373 | -56.5384 | -57.0099 | -56.3232 | -55.9341 | 65.5563 | -57.2571 | -57.1152 | -57.1152 | -57.2067 | -56.9229 | -0.091552 | -0.01831 | -0.13275 | 0.67291 | 0.88806 | 0.20142 | 0.97961 | 0.29297 | -0.045776 | -0.013733 | -122.6852 | 0.096131 | 0.28839 | 0.004578 | 0.33417 | 0.050354 | 0.76447 | 122.7402 | 0.14191 | 0.14191 | 122.8546 | 122.8134 | 122.7631 | 122.7676 | -122.8729 | -122.8271 | 122.6486 | 0.096131 | 2.2476 | 1.2772
2035.1719 | 123.0881 | -57.2159 | 65.5609 | -0.068207 | -0.0017281 | 0.063521 | 0.072677 | -0.0017624 | 0.0026191 | 0.0064898 | 0.026123 | -0.00017945 | 0.001709 | -0.00036738 | -0.0059921 | -0.0047253 | -0.00018806 | -54.9774 | 65.5609 | -57.2891 | 65.4465 | -56.5475 | -57.0282 | -56.3461 | -55.9479 | 65.5746 | -57.2525 | -57.1243 | -57.1152 | -57.225 | -56.9183 | -0.073243 | 0 | -0.11444 | 0.66834 | 0.86975 | 0.18768 | 0.94299 | 0.26093 | -0.036621 | 0.013733 | -122.6852 | 0.10071 | 0.29755 | -0.009156 | 0.33417 | 0.027465 | 0.74158 | 122.7356 | 0.13733 | 0.12817 | 122.85 | 122.8271 | 122.7768 | 122.7905 | -122.85 | -122.8134 | 122.6624 | 0.091552 | 2.2385 | 1.268
2036.1719 | 123.0789 | -57.1976 | 65.5746 | -0.10635 | -0.00087374 | 0.06053 | 0.070327 | -0.0026168 | 0.0011237 | 0.0062762 | 0.026123 | -0.0010339 | 0.00042723 | -0.0048536 | -0.00065151 | -0.0040845 | -0.0023243 | -54.9728 | 65.5426 | -57.2891 | 65.4465 | -56.5475 | -57.019 | -56.3599 | -55.9616 | 65.5792 | -57.28 | -57.1243 | -57.1243 | -57.2296 | -56.955 | -0.091553 | -0.032043 | -0.12817 | 0.65003 | 0.83771 | 0.17853 | 0.92926 | 0.27008 | -0.082397 | 0.004578 | -122.699 | 0.073242 | 0.24262 | -0.032043 | 0.32501 | 0.050354 | 0.74158 | 122.7356 | 0.15564 | 0.15564 | 122.8317 | 122.8592 | 122.7402 | 122.7768 | -122.8638 | -122.8546 | 122.644 | 0.073242 | 2.2247 | 1.236
2037.1719 | 123.0469 | -57.2159 | 65.5426 | -0.075836 | 0.00019446 | 0.061812 | 0.068832 | -0.00026703 | 0.0028327 | 0.0069172 | 0.023071 | 0.0019567 | 0.00042723 | -0.0025036 | -0.0019333 | -0.0040845 | -0.0036059 | -54.9866 | 65.5472 | -57.312 | 65.4373 | -56.5659 | -57.0328 | -56.3599 | -55.9616 | 65.5746 | -57.2525 | -57.1198 | -57.1472 | -57.2479 | -56.9504 | -0.096131 | 0.004577 | -0.10529 | 0.65002 | 0.85602 | 0.18311 | 0.95215 | 0.27924 | -0.036621 | 0.032043 | -122.6624 | 0.068664 | 0.2655 | -0.032044 | 0.30212 | 0.004577 | 0.74616 | 122.7493 | 0.10529 | 0.13275 | 122.8592 | 122.8271 | 122.7631 | 122.7905 | -122.8546 | -122.7951 | 122.6532 | 0.09613 | 2.2293 | 1.2543
2038.1719 | 123.0835 | -57.2113 | 65.5701 | -0.10635 | -0.0019417 | 0.063521 | 0.069259 | -0.0038986 | 0.0021917 | 0.0022174 | 0.0047608 | 0.0021703 | 0.00042723 | -0.0048536 | -0.0025741 | -0.0013073 | -0.0014697 | -55.0049 | 65.5472 | -57.2937 | 65.4327 | -56.5796 | -57.0419 | -56.3553 | -55.9616 | 65.5975 | -57.2617 | -57.1381 | -57.1518 | -57.2571 | -56.9595 | -0.082397 | -0.022888 | -0.13733 | 0.63171 | 0.85602 | 0.16937 | 0.93841 | 0.25177 | -0.050354 | 0.027466 | -122.7081 | 0.05951 | 0.25177 | -0.045776 | 0.30212 | 0.004578 | 0.71411 | 122.7264 | 0.10986 | 0.1236 | 122.8409 | 122.8592 | 122.7585 | 122.8088 | -122.8638 | -122.8317 | 122.644 | 0.073242 | 2.2064 | 1.2497
2039.1719 | 123.0515 | -57.225 | 65.538 | -0.068207 | 0.0031851 | 0.06288 | 0.0699 | -0.0024032 | 0.0017645 | 0.0056354 | 0.013916 | -0.00017945 | -0.00042717 | -0.0031446 | -0.00065151 | -0.0013073 | -0.0033923 | -54.9683 | 65.5563 | -57.28 | 65.4236 | -56.5796 | -57.0374 | -56.3736 | -55.9845 | 65.5975 | -57.2662 | -57.1335 | -57.1701 | -57.2617 | -56.9733 | -0.054931 | 0.01831 | -0.11444 | 0.64545 | 0.85144 | 0.18768 | 0.90637 | 0.24261 | -0.041198 | 0.059509 | -122.6715 | 0.054932 | 0.25177 | -0.036621 | 0.29297 | 0.004577 | 0.70038 | 122.7036 | 0.09613 | 0.13275 | 122.8363 | 122.8638 | 122.7814 | 122.8226 | -122.818 | -122.8043 | 122.6486 | 0.091553 | 2.2568 | 1.2405
2040.1719 | 123.0423 | -57.2525 | 65.5655 | -0.052948 | -0.0013009 | 0.062453 | 0.070327 | -0.0011214 | 0.0034735 | 0.0062762 | -0.0043946 | 0.0013159 | -0.00085457 | 0.00091422 | -0.0015061 | -0.0034437 | 0.00045294 | -55.014 | 65.538 | -57.2845 | 65.3961 | -56.6071 | -57.0877 | -56.4056 | -56.0257 | 65.5609 | -57.2525 | -57.193 | -57.2021 | -57.3029 | -56.9962 | -0.032044 | -0.027466 | -0.16937 | 0.64545 | 0.84686 | 0.16479 | 0.87891 | 0.19684 | 0 | -0.004578 | -122.7585 | 0.050354 | 0.25635 | -0.050354 | 0.25635 | -0.050354 | 0.67749 | 122.6807 | 0.050354 | 0.059509 | 122.8226 | 122.8134 | 122.7905 | 122.8134 | -122.85 | -122.818 | 122.6486 | 0.059509 | 2.2385 | 1.2268
2041.1719 | 123.0423 | -57.2113 | 65.5975 | -0.10635 | 0.0016899 | 0.060316 | 0.069472 | -5.343e-05 | 0.0021917 | 0.0060626 | 0.23669 | 0.00046135 | 0.0021362 | 0.0028368 | -0.0027877 | -0.0030163 | -0.0053149 | -54.9179 | 65.5746 | -57.2891 | 65.4648 | -56.488 | -56.9687 | -56.3324 | -56.0577 | 65.6204 | -57.2662 | -57.1243 | -57.1381 | -57.225 | -56.9595 | -0.07782 | -0.022888 | -0.13275 | 0.72327 | 0.87891 | 0.24262 | 0.95673 | 0.32044 | -0.054931 | 0.022888 | -122.7219 | 0.073242 | 0.25177 | -0.013733 | 0.3067 | 0.041198 | 0.80109 | 122.7539 | 0.12817 | 0.14191 | 122.8638 | 122.8867 | 122.7859 | 122.8317 | -122.8867 | -122.8638 | 122.6761 | 0.086975 | 2.2934 | 1.1536
2042.1719 | 123.0743 | -57.1976 | 65.5701 | -0.13687 | 0.00019446 | 0.06053 | 0.069686 | -5.343e-05 | 0.00069649 | 0.0043536 | 0.013916 | 0.00024775 | -0.00021357 | -0.00229 | -0.0017197 | -0.0049389 | -0.0031787 | -54.9728 | 65.5518 | -57.2983 | 65.4419 | -56.5567 | -57.0099 | -56.3461 | -55.9387 | 65.5792 | -57.2525 | -57.0969 | -57.1014 | -57.2067 | -56.9366 | -0.10071 | -0.01831 | -0.12817 | 0.64087 | 0.85144 | 0.18768 | 0.95215 | 0.28839 | -0.054931 | 0.009156 | -122.6669 | 0.096131 | 0.26093 | -0.009155 | 0.31586 | 0.045776 | 0.74158 | 122.7402 | 0.15106 | 0.15564 | 122.85 | 122.8317 | 122.7493 | 122.7768 | -122.8683 | -122.8226 | 122.6395 | 0.10071 | 2.2247 | 1.2589
2043.1719 | 123.0652 | -57.1884 | 65.5792 | -0.11398 | -0.0013009 | 0.062025 | 0.070968 | -0.00026703 | 0.0019781 | 0.0081988 | -0.010498 | 0.0023839 | -0.00085457 | 0.0015552 | -0.0025741 | -0.0038709 | 0.0023755 | -54.9683 | 65.5472 | -57.2937 | 65.4419 | -56.5475 | -57.019 | -56.3507 | -55.9525 | 65.5655 | -57.2708 | -57.1152 | -57.1106 | -57.2205 | -56.9412 | -0.10529 | -0.032044 | -0.13733 | 0.64087 | 0.83771 | 0.16937 | 0.94299 | 0.27466 | -0.082397 | -0.013733 | -122.6944 | 0.07782 | 0.24719 | -0.032043 | 0.32959 | 0.050354 | 0.74616 | 122.7356 | 0.16022 | 0.15564 | 122.8409 | 122.8363 | 122.7356 | 122.7539 | -122.8729 | -122.85 | 122.6303 | 0.073243 | 2.2202 | 1.236
2044.1719 | 123.0881 | -57.2067 | 65.5701 | -0.1445 | 0.00019446 | 0.060316 | 0.070754 | 0.00037377 | 0.0036871 | 0.0049946 | -0.019653 | -0.00017945 | 0.0012818 | 0.00091422 | -0.0036423 | -0.0038709 | 0.0013073 | -54.9591 | 65.5609 | -57.28 | 65.4373 | -56.5613 | -57.0328 | -56.3644 | -55.957 | 65.5792 | -57.2571 | -57.1243 | -57.1381 | -57.2205 | -56.9504 | -0.073242 | -0.009155 | -0.13275 | 0.64545 | 0.84229 | 0.17395 | 0.91553 | 0.24719 | -0.050354 | 0.009156 | -122.6944 | 0.068664 | 0.25635 | -0.013733 | 0.3067 | 0.036621 | 0.71869 | 122.7173 | 0.11902 | 0.13275 | 122.8409 | 122.8363 | 122.7676 | 122.7859 | -122.85 | -122.8271 | 122.644 | 0.082397 | 2.2476 | 1.2497
2045.1719 | 123.0377 | -57.1976 | 65.5884 | -0.075836 | 0.0010489 | 0.063521 | 0.0699 | -0.0038986 | 0.00091009 | 0.003072 | 0.013916 | 0.0011023 | 0.00064083 | 0.00070062 | -0.0038559 | -0.0038709 | -0.0010425 | -54.9271 | 65.5563 | -57.2937 | 65.4785 | -56.4835 | -56.9733 | -56.3278 | -55.8792 | 65.5884 | -57.2433 | -57.1106 | -57.106 | -57.2113 | -56.9275 | -0.09613 | -0.032044 | -0.10986 | 0.71411 | 0.86975 | 0.2243 | 0.96588 | 0.32043 | -0.045776 | 0 | -122.699 | 0.091553 | 0.27008 | -0.013733 | 0.31586 | 0.032043 | 0.81024 | 122.7722 | 0.13733 | 0.13275 | 122.85 | 122.8317 | 122.7539 | 122.786 | -122.8821 | -122.8317 | 122.6761 | 0.086975 | 2.2705 | 1.3184
2046.1719 | 123.0377 | -57.2205 | 65.5701 | -0.12924 | 0.00040806 | 0.062666 | 0.068191 | -0.0013352 | 0.0019781 | 0.0049946 | 0.02002 | 0.0011023 | 0.00021363 | -0.0010084 | 0.00020289 | -0.0034437 | 0.00023934 | -54.9774 | 65.5472 | -57.2845 | 65.4327 | -56.5475 | -57.0328 | -56.3644 | -55.9662 | 65.6067 | -57.2617 | -57.1381 | -57.1335 | -57.2433 | -56.955 | -0.064087 | -0.022888 | -0.13733 | 0.67291 | 0.85602 | 0.18768 | 0.9201 | 0.25177 | -0.041199 | 0.036621 | -122.7081 | 0.086975 | 0.2655 | -0.022888 | 0.3067 | 0.018311 | 0.737 | 122.7173 | 0.12817 | 0.1236 | 122.8317 | 122.8683 | 122.7676 | 122.8271 | -122.8546 | -122.8317 | 122.6532 | 0.082397 | 2.243 | 1.2543
2047.1719 | 123.0789 | -57.1976 | 65.5563 | -0.12161 | -1.9142e-05 | 0.062025 | 0.067336 | -0.0026168 | 0.0013373 | 0.007558 | 0.010864 | 0.0013159 | 0.00085443 | -0.0025036 | -0.0021469 | -0.0038709 | 0.00088014 | -54.9728 | 65.5472 | -57.2891 | 65.4327 | -56.5659 | -57.0374 | -56.3553 | -55.9616 | 65.6067 | -57.2754 | -57.1289 | -57.1335 | -57.2388 | -56.9595 | -0.091553 | -0.009155 | -0.1236 | 0.63171 | 0.84229 | 0.16022 | 0.93384 | 0.25177 | -0.07782 | 0.050354 | -122.6852 | 0.064087 | 0.23804 | -0.041199 | 0.31586 | 0.036621 | 0.72327 | 122.7219 | 0.14191 | 0.14648 | 122.8363 | 122.8821 | 122.7448 | 122.8043 | -122.8455 | -122.8317 | 122.6303 | 0.068665 | 2.2247 | 1.236
2048.1719 | 123.0331 | -57.1976 | 65.5701 | -0.068207 | -1.9142e-05 | 0.058607 | 0.0699 | -0.0034714 | 0.0017645 | 0.0071308 | 0.0078126 | -0.0012477 | -0.0023498 | -0.0037854 | -0.0017197 | -0.0038709 | -0.0042469 | -54.6661 | 65.6067 | -57.2388 | 65.4282 | -56.5475 | -56.9824 | -56.3553 | -55.925 | 65.6158 | -57.2388 | -57.1289 | -57.1335 | -57.225 | -56.9595 | -0.041199 | 0.036621 | -0.14191 | 0.65003 | 0.84229 | 0.21515 | 0.88348 | 0.25635 | -0.041199 | 0.045777 | -122.699 | 0.064087 | 0.23804 | -0.027466 | 0.27924 | 0.013733 | 0.69122 | 122.6669 | 0.10529 | 0.10986 | 122.8455 | 122.8546 | 122.8043 | 122.8134 | -122.8088 | -122.8088 | 122.6257 | 0.068665 | 2.5314 | 1.2726
2049.1719 | 123.0927 | -57.1884 | 65.593 | -0.098725 | -1.9142e-05 | 0.060744 | 0.070541 | -0.00026703 | 0.0026191 | 0.0039264 | 0.016968 | 3.4148e-05 | 0.0021362 | -0.0025036 | -0.0023605 | -0.0030163 | -0.0021107 | -54.9362 | 65.5518 | -57.3029 | 65.4831 | -56.4972 | -56.9824 | -56.337 | -55.9021 | 65.5792 | -57.2205 | -57.0877 | -57.1014 | -57.1976 | -56.9138 | -0.11444 | -0.041199 | -0.10986 | 0.69122 | 0.85144 | 0.20599 | 0.96588 | 0.32043 | -0.032043 | -0.013733 | -122.6807 | 0.086976 | 0.27466 | -0.009155 | 0.3067 | 0.022888 | 0.80566 | 122.7859 | 0.11902 | 0.13275 | 122.8546 | 122.7997 | 122.7402 | 122.7676 | -122.8958 | -122.8134 | 122.6715 | 0.10071 | 2.2522 | 1.2863
2050.1719 | 123.0515 | -57.2296 | 65.5609 | -0.12924 | -0.0015145 | 0.061385 | 0.071609 | 0.0016556 | 0.0024053 | 0.0086262 | 0.001709 | 0.0019567 | -0.00042717 | -0.0020764 | 0.0023391 | -0.0047253 | 0.00023934 | -54.9225 | 65.5518 | -57.2708 | 65.4831 | -56.4972 | -56.9916 | -56.3095 | -55.9158 | 65.5975 | -57.2479 | -57.0969 | -57.0877 | -57.1838 | -56.9 | -0.041199 | -0.009155 | -0.07782 | 0.73242 | 0.9201 | 0.23804 | 0.9613 | 0.27924 | -0.018311 | 0.036621 | -122.6578 | 0.14191 | 0.32959 | 0.045776 | 0.3479 | 0.064087 | 0.77362 | 122.7539 | 0.16022 | 0.15106 | 122.8226 | 122.8455 | 122.7814 | 122.8271 | -122.8317 | -122.8088 | 122.7127 | 0.13275 | 2.3071 | 1.3138
2051.1719 | 123.111 | -57.2067 | 65.5563 | -0.091095 | 0.00083526 | 0.061598 | 0.069045 | 0.0027238 | 0.00091009 | 0.0069172 | -0.0043946 | 0.00024775 | 2.8e-08 | -0.0016492 | -0.0042831 | -0.0025891 | -0.0057423 | -54.9225 | 65.5426 | -57.2891 | 65.4922 | -56.4972 | -56.9824 | -56.3095 | -55.8929 | 65.5975 | -57.2525 | -57.0877 | -57.0923 | -57.193 | -56.9275 | -0.082398 | -0.013732 | -0.064086 | 0.70953 | 0.89722 | 0.2243 | 0.97962 | 0.3067 | -0.045776 | 0.041199 | -122.644 | 0.11444 | 0.27924 | 0.013733 | 0.32501 | 0.059509 | 0.79193 | 122.7814 | 0.16022 | 0.16479 | 122.8317 | 122.85 | 122.7493 | 122.8043 | -122.8455 | -122.8088 | 122.699 | 0.11902 | 2.2842 | 1.3138
2052.1719 | 123.056 | -57.2159 | 65.5884 | -0.045319 | -1.9142e-05 | 0.063734 | 0.071609 | 0.0057144 | 0.0015509 | 0.0054218 | -0.0013428 | 0.00046135 | -0.00042717 | -0.0054944 | -0.0030013 | -0.0047253 | -0.00061526 | -54.9042 | 65.5243 | -57.2754 | 65.4694 | -56.4331 | -57.0602 | -56.3873 | -55.9296 | 65.5975 | -57.2342 | -57.106 | -57.1198 | -57.2433 | -56.955 | -0.05951 | -0.064087 | -0.11902 | 0.78278 | 0.82855 | 0.15564 | 0.88806 | 0.21515 | -0.018311 | 0.009155 | -122.6944 | 0.09613 | 0.26093 | -0.027466 | 0.27924 | -0.009155 | 0.84229 | 122.7448 | 0.11444 | 0.12817 | 122.7997 | 122.8317 | 122.7402 | 122.8134 | -122.8638 | -122.8226 | 122.6852 | 0.10986 | 2.3117 | 1.2863
2053.1719 | 123.0927 | -57.193 | 65.5746 | -0.075836 | -0.00087374 | 0.060957 | 0.0699 | -0.0017624 | 0.0015509 | 0.0077716 | 0.0047608 | -0.0016749 | -0.0012818 | -0.0035718 | -0.0012925 | -0.0047253 | -0.0031787 | -54.895 | 65.5563 | -57.2983 | 65.4877 | -56.488 | -56.9778 | -56.3507 | -55.8792 | 65.593 | -57.2433 | -57.0877 | -57.106 | -57.2021 | -56.9229 | -0.10529 | -0.018311 | -0.086975 | 0.70496 | 0.84229 | 0.21515 | 0.94757 | 0.32044 | -0.050354 | 0.018311 | -122.6624 | 0.086975 | 0.27008 | -0.009155 | 0.32043 | 0.041199 | 0.81024 | 122.786 | 0.13733 | 0.15564 | 122.8546 | 122.8363 | 122.7493 | 122.7859 | -122.8729 | -122.818 | 122.6807 | 0.10529 | 2.298 | 1.3138
2054.1719 | 123.0881 | -57.193 | 65.5701 | -0.12161 | -0.0021555 | 0.063307 | 0.069686 | 0.001442 | 0.00026909 | 0.0086262 | 0.0047608 | 0.00046135 | 0.0023498 | -0.00229 | -0.0034287 | -0.0049389 | 0.0023755 | -54.9179 | 65.5518 | -57.2571 | 65.4694 | -56.4926 | -56.9824 | -56.3278 | -55.8792 | 65.593 | -57.2113 | -57.0969 | -57.0877 | -57.1838 | -56.9321 | -0.064087 | -0.01831 | -0.10071 | 0.70038 | 0.86517 | 0.21057 | 0.92926 | 0.27466 | -0.018311 | 0.022889 | -122.6669 | 0.10529 | 0.26093 | 0.009155 | 0.27924 | 0.027466 | 0.76447 | 122.7264 | 0.1236 | 0.11444 | 122.8088 | 122.8043 | 122.7448 | 122.7859 | -122.8271 | -122.7814 | 122.6624 | 0.09613 | 2.2751 | 1.3138
2055.1719 | 123.0469 | -57.1976 | 65.5655 | -0.014801 | -0.0010873 | 0.063307 | 0.071822 | 0.0040054 | 0.0028327 | 0.0069172 | 0.0047608 | 3.4148e-05 | 2.8e-08 | 5.9824e-05 | -0.0019333 | -0.0038709 | -0.0018971 | -54.6982 | 65.5975 | -57.225 | 65.4465 | -56.5796 | -56.987 | -56.3461 | -55.9067 | 65.6021 | -57.2433 | -57.1198 | -57.1198 | -57.2159 | -56.955 | -0.027466 | 0.032043 | -0.11902 | 0.61798 | 0.85144 | 0.21057 | 0.87891 | 0.23804 | -0.045776 | 0.036621 | -122.6852 | 0.07782 | 0.24262 | -0.01831 | 0.28839 | 0.027466 | 0.64545 | 122.6715 | 0.1236 | 0.1236 | 122.8226 | 122.8455 | 122.7951 | 122.7997 | -122.7905 | -122.8088 | 122.644 | 0.07782 | 2.4994 | 1.2909
2056.1719 | 123.0515 | -57.1976 | 65.5975 | -0.060578 | 0.0014761 | 0.06053 | 0.069686 | 0.00251 | 0.0043281 | 0.0067036 | -0.0013428 | -0.00060665 | 0.00021363 | 0.001128 | -0.0017197 | -0.0019483 | 0.00066654 | -54.8264 | 65.6296 | -57.225 | 65.451 | -56.488 | -57.0007 | -56.3416 | -55.9204 | 65.6158 | -57.2525 | -57.1289 | -57.1289 | -57.2205 | -56.9412 | -0.027466 | 0.032044 | -0.14648 | 0.70953 | 0.85602 | 0.19684 | 0.88348 | 0.22431 | -0.054931 | 0.018311 | -122.7264 | 0.068665 | 0.25635 | -0.022888 | 0.31128 | 0.032043 | 0.737 | 122.6761 | 0.1236 | 0.1236 | 122.8546 | 122.8683 | 122.8271 | 122.8134 | -122.8226 | -122.85 | 122.6486 | 0.068665 | 2.3712 | 1.2772
2057.1719 | 123.0469 | -57.1701 | 65.5884 | 0.00045798 | 0.0033987 | 0.066512 | 0.070541 | -0.0013352 | 0.0026191 | 0.0060626 | -0.01355 | 0.0015295 | -0.00085457 | -0.00058098 | -1.0706e-05 | -0.0036573 | 0.00045294 | -55.1285 | 65.5518 | -57.28 | 65.4648 | -56.5292 | -56.987 | -56.337 | -55.9067 | 65.5838 | -57.2571 | -57.1335 | -57.1243 | -57.2388 | -56.955 | -0.10986 | -0.036621 | -0.1236 | 0.64087 | 0.83313 | 0.1831 | 0.94299 | 0.29297 | -0.086975 | -0.004578 | -122.7219 | 0.045776 | 0.21515 | -0.068665 | 0.30212 | 0.01831 | 0.75073 | 122.7448 | 0.13275 | 0.1236 | 122.8317 | 122.8409 | 122.7219 | 122.7539 | -122.8683 | -122.8455 | 122.6349 | 0.036621 | 2.0416 | 1.2634
2058.1719 | 123.0743 | -57.2113 | 65.5792 | -0.22842 | -1.9142e-05 | 0.062666 | 0.068191 | -0.00048063 | 0.0015509 | 0.005849 | -0.0013428 | -0.0014613 | 0.00042723 | 0.00070062 | -0.0012925 | -0.0034437 | -0.00082886 | -54.8904 | 65.5197 | -57.2983 | 65.4648 | -56.5063 | -56.9733 | -56.3644 | -55.9204 | 65.6067 | -57.2479 | -57.1152 | -57.1243 | -57.225 | -56.9458 | -0.086975 | -0.05951 | -0.11444 | 0.70496 | 0.84686 | 0.23804 | 0.93384 | 0.32501 | -0.036621 | 0.027465 | -122.6944 | 0.086975 | 0.2655 | -0.013733 | 0.30212 | 0.022888 | 0.79193 | 122.7631 | 0.1236 | 0.13275 | 122.818 | 122.8546 | 122.731 | 122.818 | -122.8775 | -122.8271 | 122.6761 | 0.096131 | 2.3209 | 1.2909
2059.1719 | 122.9599 | -57.2159 | 65.593 | -0.060578 | -0.00023294 | 0.062453 | 0.070541 | -0.0017624 | 0.00048269 | 0.0069172 | -0.019653 | 0.0021703 | 0.00064083 | 0.001128 | -0.0012925 | -0.0034437 | -0.0025379 | -54.9225 | 65.5838 | -57.2845 | 65.4282 | -56.5521 | -57.0145 | -56.3919 | -56.0074 | 65.6387 | -57.2342 | -57.193 | -57.2296 | -57.2754 | -57.0053 | -0.068665 | -0.009156 | -0.16479 | 0.66376 | 0.82397 | 0.20142 | 0.89264 | 0.27008 | -0.018311 | 0.045776 | -122.7859 | -0.013733 | 0.21057 | -0.05951 | 0.22888 | -0.041199 | 0.73242 | 122.7127 | 0.004578 | 0.041199 | 122.8683 | 122.8729 | 122.7997 | 122.8546 | -122.8775 | -122.8271 | 122.644 | 0.022888 | 2.2934 | 1.2085
2060.1719 | 123.1522 | -57.1609 | 65.6525 | -0.075836 | 0.00019446 | 0.061598 | 0.069472 | 0.001442 | 0.00048269 | 0.0069172 | 0.010864 | 0.00024775 | -0.00064077 | -0.0059216 | -0.0025741 | -0.0053663 | -0.0018971 | -54.8996 | 65.5609 | -57.2754 | 65.4968 | -56.4697 | -56.955 | -56.3141 | -55.8884 | 65.5975 | -57.2388 | -57.1014 | -57.0969 | -57.1884 | -56.9641 | -0.11444 | -0.091553 | -0.15564 | 0.69122 | 0.84686 | 0.20599 | 0.9613 | 0.32043 | -0.07782 | -0.054932 | -122.7539 | 0.064087 | 0.19684 | -0.027466 | 0.27466 | 0.050354 | 0.80566 | 122.7722 | 0.14191 | 0.13733 | 122.8363 | 122.8363 | 122.7219 | 122.7585 | -122.9279 | -122.8912 | 122.6578 | 0.05951 | 2.2614 | 1.2726
2061.1719 | 122.9553 | -57.2113 | 65.6433 | -0.091095 | 0.00040806 | 0.062025 | 0.0699 | -0.0017624 | 0.0024053 | 0.00414 | 0.016968 | 0.0015295 | 0.0012818 | 0.0034778 | -1.0706e-05 | -0.0040845 | -0.0010425 | -54.9225 | 65.5701 | -57.3029 | 65.4282 | -56.5842 | -57.0374 | -56.4056 | -56.0074 | 65.6296 | -57.2708 | -57.1838 | -57.2296 | -57.3441 | -57.0328 | -0.091552 | -0.073243 | -0.21515 | 0.62714 | 0.80566 | 0.17395 | 0.89722 | 0.2655 | -0.059509 | -0.013733 | -122.8271 | -0.01831 | 0.17853 | -0.13275 | 0.23804 | -0.073242 | 0.71869 | 122.731 | 0.041199 | 0.086975 | 122.8729 | 122.9004 | 122.7814 | 122.8409 | -122.9462 | -122.9141 | 122.6395 | 0.027466 | 2.2888 | 1.2039
2062.1719 | 122.9736 | -57.2296 | 65.6204 | -0.091095 | 0.00062166 | 0.060103 | 0.069472 | -0.0015488 | 5.5488e-05 | 0.0047808 | 0.010864 | 0.0013159 | 0.00021363 | 0.0015552 | -0.0023605 | -0.0051527 | -0.0012561 | -54.9179 | 65.593 | -57.2754 | 65.4053 | -56.5842 | -57.0419 | -56.4148 | -56.012 | 65.6342 | -57.2845 | -57.2113 | -57.2342 | -57.3257 | -57.0328 | -0.045777 | -0.027465 | -0.21515 | 0.64545 | 0.81482 | 0.18768 | 0.8606 | 0.23346 | -0.054932 | 0.013733 | -122.8317 | -0.004578 | 0.19684 | -0.096131 | 0.25177 | -0.041199 | 0.69122 | 122.6807 | 0.050354 | 0.073242 | 122.8683 | 122.9187 | 122.8226 | 122.8638 | -122.8958 | -122.905 | 122.6349 | 0.01831 | 2.3117 | 1.2177
2063.1719 | 122.9645 | -57.2388 | 65.5975 | -0.0071715 | -0.0017281 | 0.061171 | 0.074172 | -5.343e-05 | 0.0013373 | 0.0032856 | -0.022705 | 0.0030249 | -0.00021357 | 0.003905 | -0.0010787 | -0.0025891 | 0.00045294 | -54.982 | 65.625 | -57.2983 | 65.3687 | -56.6437 | -57.0969 | -56.456 | -55.9799 | 65.6845 | -57.225 | -57.2433 | -57.225 | -57.3395 | -57.0374 | -0.059509 | 0.027466 | -0.22888 | 0.59509 | 0.78278 | 0.14191 | 0.84229 | 0.20142 | 0.013733 | 0.086975 | -122.8409 | 0.013733 | 0.20142 | -0.10071 | 0.18768 | -0.11444 | 0.6546 | 122.6669 | 0 | -0.01831 | 122.9233 | 122.9095 | 122.8638 | 122.9233 | -122.8958 | -122.8226 | 122.6074 | -0.004577 | 2.2568 | 1.2589
2064.1719 | 122.9324 | -57.2342 | 65.593 | -0.060578 | 0.00062166 | 0.062239 | 0.068618 | 0.0012284 | 0.0015509 | 0.00414 | 0.0078126 | 0.0019567 | 0.0019226 | 0.00048702 | -0.0017197 | -0.0040845 | -0.00040166 | -54.9225 | 65.5884 | -57.2891 | 65.3961 | -56.5613 | -57.0602 | -56.4011 | -56.0211 | 65.625 | -57.2433 | -57.2205 | -57.2159 | -57.3074 | -57.0282 | -0.054932 | -0.004578 | -0.19684 | 0.67291 | 0.83313 | 0.17395 | 0.88806 | 0.22888 | -0.009155 | 0.032043 | -122.8134 | 0.018311 | 0.20599 | -0.073242 | 0.21515 | -0.064087 | 0.72785 | 122.6852 | 0.027466 | 0.022888 | 122.8775 | 122.8683 | 122.8226 | 122.8592 | -122.8821 | -122.8363 | 122.6303 | 0.013733 | 2.3117 | 1.2131
2065.1719 | 122.9691 | -57.2342 | 65.6021 | -0.075836 | -0.00044654 | 0.06288 | 0.070113 | 0.0018692 | 0.0043281 | 0.002431 | 0.016968 | 0.0015295 | 0.001068 | -0.003999 | -0.0021469 | -0.0023755 | -0.0018971 | -54.9271 | 65.5975 | -57.28 | 65.4099 | -56.5933 | -57.0602 | -56.4056 | -56.0303 | 65.6387 | -57.2525 | -57.2159 | -57.225 | -57.3029 | -57.0282 | -0.045776 | -0.004578 | -0.19226 | 0.64087 | 0.82855 | 0.17395 | 0.87433 | 0.21973 | -0.01831 | 0.036621 | -122.818 | 0.009155 | 0.20599 | -0.068664 | 0.2243 | -0.050354 | 0.68664 | 122.6898 | 0.027465 | 0.036621 | 122.8775 | 122.8912 | 122.8317 | 122.8729 | -122.8821 | -122.8546 | 122.644 | 0.018311 | 2.3071 | 1.2039
2066.1719 | 123.0103 | -57.1976 | 65.6067 | -0.075836 | -1.9142e-05 | 0.062239 | 0.070113 | 0.0044328 | 0.0026191 | 0.0052082 | 0.02002 | -0.0014613 | 0.0014954 | -0.00079478 | -0.0015061 | -0.0045117 | -0.0025379 | -54.9408 | 65.5655 | -57.2479 | 65.4648 | -56.5247 | -56.9962 | -56.3599 | -55.9296 | 65.5884 | -57.2205 | -57.1289 | -57.1198 | -57.2296 | -56.9458 | -0.050354 | -0.041198 | -0.14191 | 0.67291 | 0.83771 | 0.20142 | 0.88806 | 0.25177 | -0.022888 | -0.01831 | -122.7356 | 0.07782 | 0.25177 | -0.032043 | 0.27466 | -0.009155 | 0.72327 | 122.7127 | 0.10071 | 0.091553 | 122.8134 | 122.8088 | 122.7631 | 122.786 | -122.8546 | -122.8271 | 122.6624 | 0.068665 | 2.2568 | 1.268
2067.1719 | 122.9553 | -57.2433 | 65.6067 | -0.045319 | 0.00040806 | 0.06053 | 0.068618 | 0.00016017 | 0.0017645 | 0.0043536 | -0.0043946 | -0.00039305 | -0.00021357 | 0.0024096 | 0.00020289 | -0.0021619 | -0.00018806 | -54.9271 | 65.5792 | -57.2891 | 65.4099 | -56.5704 | -57.0465 | -56.4011 | -56.0028 | 65.625 | -57.2525 | -57.1976 | -57.2205 | -57.3257 | -57.0328 | -0.045777 | -0.027465 | -0.19684 | 0.67291 | 0.84228 | 0.19684 | 0.88806 | 0.24262 | -0.009155 | 0.018311 | -122.8043 | 0.022888 | 0.21057 | -0.082398 | 0.21973 | -0.073243 | 0.71869 | 122.699 | 0.032043 | 0.054931 | 122.8683 | 122.8775 | 122.8226 | 122.8683 | -122.8958 | -122.8592 | 122.6532 | 0.045776 | 2.3163 | 1.2405
2068.1719 | 122.9095 | -57.2754 | 65.6113 | -0.098725 | 0.00083526 | 0.061812 | 0.070754 | -0.001976 | 0.0019781 | 0.0047808 | 0.001709 | 3.4148e-05 | -0.00064077 | -0.0016492 | -1.0706e-05 | -0.0025891 | -0.0014697 | -54.9774 | 65.6067 | -57.3029 | 65.3503 | -56.6437 | -57.1014 | -56.4514 | -56.0669 | 65.6479 | -57.2525 | -57.2479 | -57.3715 | -57.3029 | -57.0236 | -0.027465 | -0.004578 | -0.26093 | 0.63171 | 0.82397 | 0.17395 | 0.85144 | 0.20142 | 0.022889 | 0.036621 | -122.8592 | -0.09613 | 0.25177 | -0.027465 | 0.22888 | -0.050354 | 0.65918 | 122.6532 | -0.11902 | 0.004577 | 122.9095 | 122.9004 | 122.8821 | 122.9233 | -122.9141 | -122.8638 | 122.6257 | 0.027466 | 2.298 | 1.2085
2069.1719 | 122.9645 | -57.2525 | 65.6113 | -0.075836 | 0.0019035 | 0.060957 | 0.0699 | -0.0024032 | 0.0019781 | 0.003072 | -0.022705 | 0.0023839 | 0.001709 | -0.00079478 | -0.0030013 | -0.0049389 | 0.0013073 | -54.9683 | 65.6021 | -57.2983 | 65.3641 | -56.6254 | -57.1014 | -56.4377 | -56.0532 | 65.6525 | -57.2845 | -57.1655 | -57.3898 | -57.4219 | -57.0236 | -0.045777 | -0.009155 | -0.24719 | 0.62714 | 0.81482 | 0.15106 | 0.8606 | 0.19684 | -0.032044 | 0.041199 | -122.7768 | -0.13733 | 0.22888 | -0.16937 | 0.26093 | -0.13733 | 0.67291 | 122.6624 | -0.10529 | 0.11902 | 122.9004 | 122.937 | 122.8546 | 122.905 | -122.9095 | -122.8958 | 122.6166 | 0.086975 | 2.2842 | 1.1993
2070.1719 | 122.905 | -57.2342 | 65.6113 | -0.060578 | -0.00087374 | 0.060103 | 0.070968 | -0.0043258 | 0.0015509 | 0.0060626 | -0.010498 | 0.0017431 | -0.00021357 | 0.0028368 | -0.0032151 | -0.0030163 | -0.0018971 | -54.9545 | 65.6158 | -57.2983 | 65.3641 | -56.6254 | -57.0923 | -56.4423 | -56.0715 | 65.6342 | -57.2525 | -57.2891 | -56.9916 | -57.3761 | -57.0877 | -0.064087 | 0.004578 | -0.24719 | 0.60883 | 0.79193 | 0.14191 | 0.85602 | 0.20599 | -0.01831 | 0.022888 | -122.9004 | 0.24262 | 0.14648 | -0.14191 | 0.16479 | -0.1236 | 0.67291 | 122.6624 | 0.26093 | -0.036622 | 122.9141 | 122.8867 | 122.85 | 122.8683 | -122.9095 | -122.8638 | 122.5983 | -0.054932 | 2.2797 | 1.1627
2071.1719 | 122.9965 | -57.2021 | 65.6799 | 0.008087 | -0.0019417 | 0.063307 | 0.073318 | 0.00058737 | 0.00026909 | 0.0034992 | -0.0043946 | 0.0013159 | 0.00042723 | 0.00070062 | -0.00022431 | -0.0045117 | 0.00088014 | -54.9637 | 65.6342 | -57.2662 | 65.3595 | -56.6299 | -57.1106 | -56.4377 | -56.0623 | 65.6387 | -57.2479 | -57.2205 | -57.2433 | -57.3349 | -57.0648 | -0.064087 | -0.045777 | -0.32043 | 0.5722 | 0.76447 | 0.091552 | 0.82855 | 0.15564 | -0.045777 | -0.041199 | -122.9004 | -0.041199 | 0.13733 | -0.13275 | 0.18311 | -0.086975 | 0.63629 | 122.6257 | 0.004578 | 0.027466 | 122.9004 | 122.8867 | 122.8363 | 122.8409 | -122.9462 | -122.9279 | 122.5616 | -0.018311 | 2.2385 | 1.1398
2072.1719 | 122.9416 | -57.2342 | 65.625 | -0.060578 | 0.0021171 | 0.063948 | 0.070327 | -0.00048063 | 0.0026191 | 0.0043536 | 0.026123 | 0.0015295 | 0.00085443 | -0.002931 | -0.00086511 | -0.0025891 | 0.0034435 | -54.9637 | 65.6296 | -57.2754 | 65.3503 | -56.6345 | -57.0969 | -56.4377 | -56.044 | 65.6342 | -57.2479 | -57.2159 | -57.2296 | -57.3441 | -57.0236 | -0.041199 | 0.004578 | -0.27466 | 0.59967 | 0.79651 | 0.13733 | 0.83771 | 0.17853 | -0.013733 | 0.009155 | -122.8409 | 0.004578 | 0.21057 | -0.10986 | 0.2243 | -0.09613 | 0.64087 | 122.6257 | 0.018311 | 0.032044 | 122.905 | 122.8821 | 122.8638 | 122.8683 | -122.9004 | -122.8729 | 122.5845 | 0.018311 | 2.2705 | 1.1902
2073.1719 | 123.024 | -57.2021 | 65.5838 | -0.075836 | -0.00087374 | 0.062666 | 0.069045 | -0.006462 | 0.0030463 | 0.0064898 | 0.023071 | 0.0017431 | 0.00021363 | 0.00048702 | -1.0706e-05 | -0.0047253 | 0.00023934 | -54.9088 | 65.5746 | -57.2754 | 65.4556 | -56.5247 | -57.0053 | -56.3644 | -55.9753 | 65.6021 | -57.2296 | -57.1426 | -57.1609 | -57.2708 | -56.987 | -0.073243 | -0.009155 | -0.12817 | 0.67749 | 0.83771 | 0.19684 | 0.91095 | 0.27008 | -0.027466 | 0.018311 | -122.7264 | 0.041198 | 0.21515 | -0.068665 | 0.24261 | -0.041199 | 0.75073 | 122.731 | 0.068664 | 0.086975 | 122.85 | 122.8317 | 122.7768 | 122.8043 | -122.8592 | -122.8134 | 122.6578 | 0.059509 | 2.2934 | 1.2268
2074.1719 | 122.9828 | -57.2296 | 65.625 | -0.068207 | -0.00044654 | 0.061385 | 0.0699 | -0.00069423 | 0.00026909 | 0.0039264 | 0.032227 | 0.0015295 | 0.001709 | -0.00229 | -0.0030013 | -0.0045117 | 2.554e-05 | -54.9271 | 65.593 | -57.2662 | 65.3732 | -56.5933 | -57.0786 | -56.4148 | -56.0532 | 65.6616 | -57.2617 | -57.2113 | -57.2296 | -57.3303 | -57.0374 | -0.036621 | -0.032043 | -0.25177 | 0.63629 | 0.81482 | 0.15106 | 0.85144 | 0.18768 | -0.032044 | 0.036621 | -122.8363 | 0 | 0.19226 | -0.10071 | 0.2243 | -0.068664 | 0.67291 | 122.6395 | 0.032044 | 0.050354 | 122.8592 | 122.9233 | 122.8226 | 122.8912 | -122.8912 | -122.8867 | 122.6028 | 0.01831 | 2.3026 | 1.1765
2075.1719 | 122.9507 | -57.2388 | 65.625 | -0.060578 | -0.00023294 | 0.062025 | 0.070968 | 0.0022964 | 0.0030463 | 0.0056354 | -0.044067 | 0.00024775 | 0.0023498 | -0.0025036 | -0.0012925 | -0.0040845 | 0.0040845 | -54.9683 | 65.6204 | -57.3074 | 65.3687 | -56.6437 | -57.1014 | -56.4606 | -56.0257 | 65.7166 | -57.2479 | -57.2571 | -57.2342 | -57.3532 | -57.0419 | -0.068664 | -0.004578 | -0.25635 | 0.59509 | 0.7782 | 0.13733 | 0.84686 | 0.20599 | -0.009155 | 0.091553 | -122.8821 | 0.004578 | 0.19684 | -0.11444 | 0.20599 | -0.10528 | 0.66376 | 122.6761 | 0.013733 | -0.009155 | 122.9279 | 122.9645 | 122.8592 | 122.9553 | -122.9324 | -122.8729 | 122.6074 | -0.01831 | 2.2705 | 1.2131
2076.1719 | 122.9736 | -57.2342 | 65.625 | -0.060578 | -0.00066014 | 0.062453 | 0.072036 | 0.00016017 | 0.00048269 | 0.0043536 | -0.010498 | 0.0013159 | 0.00064083 | 0.0051868 | -0.0015061 | -0.0068615 | 0.0019483 | -54.9683 | 65.6067 | -57.2891 | 65.3641 | -56.6345 | -57.0923 | -56.4514 | -56.0486 | 65.6616 | -57.2662 | -57.1106 | -57.2983 | -57.4814 | -57.1518 | -0.054932 | -0.018311 | -0.26093 | 0.59967 | 0.78278 | 0.14191 | 0.83771 | 0.19684 | -0.032043 | 0.036621 | -122.7356 | -0.064087 | 0.082398 | -0.24719 | 0.11444 | -0.21515 | 0.6546 | 122.6532 | -0.032044 | 0.15564 | 122.8958 | 122.9279 | 122.8409 | 122.8958 | -122.9141 | -122.8912 | 122.5983 | 0.1236 | 2.2659 | 1.1856
2077.1719 | 122.9187 | -57.2388 | 65.6387 | -0.022431 | 0.00040806 | 0.062025 | 0.070541 | 0.00080117 | 0.0026191 | 0.005849 | 0.0047608 | 0.0021703 | 0.0025634 | -0.0010084 | -0.0015061 | -0.0051527 | 0.0015209 | -54.9728 | 65.6158 | -57.2937 | 65.3503 | -56.6254 | -57.106 | -56.4331 | -56.0715 | 65.6433 | -57.2525 | -57.2113 | -57.2388 | -57.3303 | -57.0465 | -0.054931 | -0.022888 | -0.28839 | 0.6134 | 0.80567 | 0.13275 | 0.8606 | 0.18768 | -0.013732 | 0.004578 | -122.85 | 0 | 0.19226 | -0.091552 | 0.20599 | -0.07782 | 0.66833 | 122.644 | 0.013732 | 0.041198 | 122.9095 | 122.8958 | 122.8546 | 122.8821 | -122.9324 | -122.8912 | 122.5891 | 0.027466 | 2.2659 | 1.1673
2078.1719 | 122.9553 | -57.225 | 65.625 | -0.037689 | 0.0021171 | 0.06288 | 0.070754 | 0.001442 | 0.00048269 | 0.0039264 | -0.0074462 | 0.0011023 | 0.00064083 | -0.0016492 | -0.0015061 | -0.0045117 | -0.0021107 | -55.0232 | 65.6296 | -57.2845 | 65.3687 | -56.6666 | -57.1609 | -56.456 | -56.0669 | 65.6433 | -57.2617 | -57.225 | -57.2479 | -57.3395 | -57.0419 | -0.059509 | 0.004578 | -0.25635 | 0.55847 | 0.76904 | 0.064087 | 0.82855 | 0.1236 | -0.036621 | 0.018311 | -122.85 | -0.022888 | 0.18311 | -0.11444 | 0.21973 | -0.07782 | 0.61798 | 122.6532 | 0.013733 | 0.036621 | 122.9141 | 122.905 | 122.8546 | 122.8683 | -122.9095 | -122.8867 | 122.5937 | 0 | 2.2018 | 1.1581
2079.1719 | 122.9462 | -57.225 | 65.6158 | -0.098725 | -1.9142e-05 | 0.062025 | 0.070113 | 0.0035782 | 0.0015509 | 0.0052082 | 0.026123 | -0.00017945 | 0.0014954 | -0.0027174 | -1.0706e-05 | -0.0038709 | -0.00018806 | -54.9225 | 65.6113 | -57.2708 | 65.4007 | -56.6025 | -57.0602 | -56.4377 | -56.0257 | 65.6158 | -57.2479 | -57.2205 | -57.2296 | -57.3303 | -57.0419 | -0.045776 | -0.004578 | -0.21515 | 0.62256 | 0.78735 | 0.16479 | 0.83313 | 0.21057 | -0.022888 | 0 | -122.8363 | -0.004577 | 0.18311 | -0.10529 | 0.20599 | -0.082397 | 0.66833 | 122.6715 | 0.018311 | 0.027466 | 122.8821 | 122.8638 | 122.8363 | 122.8409 | -122.8867 | -122.8638 | 122.6257 | 0.004578 | 2.3026 | 1.1993
2080.1719 | 123.024 | -57.1976 | 65.6113 | -0.098725 | -1.9142e-05 | 0.061598 | 0.070754 | 0.001442 | 0.0041143 | 0.0049946 | 0.044434 | 0.00046135 | 0.00064083 | -0.0018628 | -0.0012925 | -0.0025891 | 0.0015209 | -54.9271 | 65.5701 | -57.2845 | 65.4556 | -56.5018 | -56.9733 | -56.3599 | -55.9341 | 65.6113 | -57.2296 | -57.1335 | -57.1152 | -57.2388 | -56.9504 | -0.086975 | -0.041199 | -0.15564 | 0.6958 | 0.83771 | 0.2243 | 0.92468 | 0.31128 | -0.032043 | 0 | -122.7448 | 0.082398 | 0.24719 | -0.041199 | 0.27924 | -0.009156 | 0.78278 | 122.7402 | 0.11444 | 0.09613 | 122.8546 | 122.8409 | 122.7676 | 122.8088 | -122.8958 | -122.8409 | 122.6532 | 0.064087 | 2.2705 | 1.2634
2081.1719 | 123.0835 | -57.2021 | 65.5838 | -0.022431 | -0.0030099 | 0.059889 | 0.067763 | -0.00069423 | 0.0026191 | 0.0073444 | 0.047485 | 0.00024775 | 0.00064083 | 0.0026232 | -0.00065151 | -0.0045117 | 0.0013073 | -54.6478 | 65.6433 | -57.2388 | 65.4236 | -56.5247 | -56.9916 | -56.3782 | -55.925 | 65.6113 | -57.2113 | -57.1289 | -57.1381 | -57.2159 | -56.9504 | -0.036622 | 0.05951 | -0.16022 | 0.67749 | 0.82397 | 0.21057 | 0.8606 | 0.24719 | -0.009156 | 0.027466 | -122.7127 | 0.064086 | 0.25177 | -0.013733 | 0.26093 | -0.004577 | 0.71411 | 122.6624 | 0.073242 | 0.082398 | 122.8821 | 122.8226 | 122.8455 | 122.8134 | -122.8226 | -122.7951 | 122.6257 | 0.073242 | 2.5543 | 1.2772
2082.1719 | 122.937 | -57.225 | 65.6479 | -0.075836 | -1.9142e-05 | 0.060957 | 0.067977 | -0.0021896 | 0.0017645 | 0.0043536 | -0.0013428 | 0.0025975 | 0.0012818 | 0.0024096 | -0.0032151 | -0.0032301 | 0.0047253 | -54.9408 | 65.6067 | -57.2754 | 65.3641 | -56.6299 | -57.0831 | -56.4377 | -56.0577 | 65.6525 | -57.2525 | -57.2433 | -57.2433 | -57.3303 | -57.0374 | -0.050354 | -0.041199 | -0.28381 | 0.59509 | 0.78735 | 0.14191 | 0.83771 | 0.19226 | -0.027465 | 0.004578 | -122.8912 | -0.01831 | 0.18768 | -0.10529 | 0.21515 | -0.07782 | 0.64545 | 122.6395 | 0.009155 | 0.009155 | 122.8821 | 122.905 | 122.8317 | 122.8775 | -122.9233 | -122.9004 | 122.5891 | -0.01831 | 2.2842 | 1.1673
2083.1719 | 122.9324 | -57.225 | 65.6387 | -0.045319 | -0.0019417 | 0.062025 | 0.069259 | -0.0015488 | 0.0015509 | 0.0045672 | -0.028809 | -0.00082025 | 2.8e-08 | 0.0036914 | -0.00043791 | -0.0025891 | -0.0042469 | -54.9637 | 65.6296 | -57.2983 | 65.3046 | -56.4194 | -57.019 | -56.5659 | -56.0577 | 65.6204 | -57.28 | -57.2433 | -57.2205 | -57.3349 | -57.0282 | -0.073242 | -0.009155 | -0.33417 | 0.80566 | 0.65918 | 0.20599 | 0.73242 | 0.27924 | -0.054931 | -0.018311 | -122.8821 | 0.004578 | 0.19684 | -0.10986 | 0.25177 | -0.054932 | 0.87891 | 122.6028 | 0.059509 | 0.036621 | 122.9279 | 122.9004 | 122.8546 | 122.8455 | -122.937 | -122.9187 | 122.5296 | -0.01831 | 2.2614 | 1.1673
2084.1719 | 122.9828 | -57.225 | 65.6158 | -0.068207 | 0.0010489 | 0.063521 | 0.069259 | 0.0027238 | 0.0026191 | 0.0064898 | 0.010864 | 3.4148e-05 | 0.00085443 | 0.0019824 | -0.00043791 | -0.0049389 | -0.00018806 | -54.8996 | 65.5838 | -57.2617 | 65.4282 | -56.5704 | -57.0465 | -56.3919 | -55.9891 | 65.6204 | -57.2479 | -57.1976 | -57.2113 | -57.2937 | -56.9916 | -0.036621 | -0.032044 | -0.18768 | 0.6546 | 0.83313 | 0.17853 | 0.86975 | 0.21515 | -0.022888 | 0.004577 | -122.8134 | 0.013733 | 0.23346 | -0.068664 | 0.25635 | -0.045776 | 0.69122 | 122.6898 | 0.036621 | 0.050354 | 122.8455 | 122.8683 | 122.8088 | 122.8455 | -122.8775 | -122.8638 | 122.6532 | 0.027466 | 2.3254 | 1.236
2085.1719 | 122.9919 | -57.2159 | 65.6433 | -0.052948 | 0.0012625 | 0.064589 | 0.068191 | -0.00026703 | 0.0024053 | 0.0060626 | 0.03833 | -0.00039305 | 2.8e-08 | -0.0054944 | -0.0021469 | -0.0025891 | -0.0012561 | -54.8904 | 65.6021 | -57.2433 | 65.4419 | -56.5567 | -57.0053 | -56.3736 | -55.9708 | 65.6113 | -57.2479 | -57.1747 | -57.1838 | -57.2662 | -56.9824 | -0.027466 | -0.041199 | -0.20142 | 0.65918 | 0.84229 | 0.21057 | 0.86975 | 0.23804 | -0.032044 | -0.032044 | -122.818 | 0.032043 | 0.23346 | -0.050354 | 0.2655 | -0.01831 | 0.68664 | 122.6852 | 0.064087 | 0.073242 | 122.8455 | 122.8592 | 122.818 | 122.8271 | -122.8867 | -122.8912 | 122.6578 | 0.041198 | 2.3254 | 1.2451
2086.1719 | 123.0194 | -57.2296 | 65.6204 | -0.037689 | 0.0023307 | 0.061812 | 0.070113 | -0.0043258 | 0.0019781 | 0.0071308 | 0.032227 | 0.0015295 | -0.0010682 | 0.00027342 | -0.0015061 | -0.0036573 | -0.0029651 | -54.8904 | 65.5792 | -57.2845 | 65.4556 | -56.5338 | -57.0007 | -56.3599 | -55.9433 | 65.6204 | -57.2296 | -57.1564 | -57.1472 | -57.2617 | -56.955 | -0.054932 | -0.041198 | -0.16479 | 0.6958 | 0.86975 | 0.22888 | 0.92468 | 0.28381 | 0 | 0 | -122.7768 | 0.082397 | 0.27466 | -0.032044 | 0.27466 | -0.032044 | 0.75073 | 122.7402 | 0.082397 | 0.073242 | 122.8638 | 122.85 | 122.8088 | 122.85 | -122.905 | -122.85 | 122.6852 | 0.073242 | 2.3392 | 1.2863
2087.1719 | 123.0743 | -57.2159 | 65.5792 | -0.068207 | -0.00066014 | 0.060957 | 0.068832 | 0.005928 | 0.0039007 | 0.0052082 | 0.047485 | -0.00017945 | 0.0014954 | -0.010194 | 0.00041649 | -0.0045117 | -0.00018806 | -54.8721 | 65.5746 | -57.28 | 65.4785 | -56.4835 | -56.9824 | -56.3416 | -55.957 | 65.5975 | -57.2113 | -57.0831 | -57.1609 | -57.2571 | -56.9595 | -0.064087 | -0.004578 | -0.10071 | 0.73242 | 0.87433 | 0.23346 | 0.93841 | 0.29755 | 0.004577 | 0.01831 | -122.6624 | 0.054931 | 0.25635 | -0.041199 | 0.25177 | -0.045776 | 0.79651 | 122.7585 | 0.050354 | 0.12817 | 122.8546 | 122.8088 | 122.7905 | 122.8134 | -122.8592 | -122.7905 | 122.6944 | 0.13275 | 2.3438 | 1.2589
2088.1719 | 123.0377 | -57.2113 | 65.5838 | -0.12161 | 0.0038261 | 0.063094 | 0.069686 | -0.0011214 | -0.00058531 | 0.0056354 | 0.013916 | -0.00082025 | 0.00042723 | 0.00070062 | -0.0030013 | -0.0025891 | -0.0012561 | -54.863 | 65.5563 | -57.2708 | 65.4602 | -56.5201 | -56.9824 | -56.3644 | -55.925 | 65.6067 | -57.2479 | -57.1198 | -57.1426 | -57.2342 | -56.9595 | -0.059509 | -0.027466 | -0.1236 | 0.69122 | 0.84686 | 0.22888 | 0.90637 | 0.28839 | -0.036621 | 0.022888 | -122.7036 | 0.068665 | 0.25177 | -0.022888 | 0.28839 | 0.013733 | 0.75073 | 122.731 | 0.10529 | 0.12817 | 122.8271 | 122.8546 | 122.7676 | 122.818 | -122.8546 | -122.8317 | 122.6715 | 0.091553 | 2.3483 | 1.2863
2089.1719 | 122.9874 | -57.2113 | 65.6021 | -0.045319 | 0.0014761 | 0.064162 | 0.069259 | -0.0026168 | 0.0039007 | 0.0079852 | 0.03833 | 0.00024775 | -0.00021357 | -0.0016492 | -0.0021469 | -0.0049389 | -0.0016833 | -54.8859 | 65.5884 | -57.2662 | 65.4419 | -56.5613 | -57.0282 | -56.369 | -55.9845 | 65.6158 | -57.2662 | -57.1838 | -57.1793 | -57.2983 | -57.0145 | -0.054931 | -0.013733 | -0.16022 | 0.65002 | 0.84228 | 0.18311 | 0.89722 | 0.23804 | -0.054931 | 0.013733 | -122.786 | 0.032044 | 0.19684 | -0.086975 | 0.25177 | -0.032044 | 0.70496 | 122.7081 | 0.086975 | 0.082397 | 122.8546 | 122.8821 | 122.7997 | 122.8271 | -122.8683 | -122.8683 | 122.6532 | 0.027466 | 2.3254 | 1.2268
2090.1719 | 122.9782 | -57.2525 | 65.5792 | -0.12161 | -0.0010873 | 0.065657 | 0.072036 | 0.0055008 | 0.0019781 | 0.0067036 | -0.044067 | 0.0021703 | 0.0021362 | 0.0015552 | -0.0025741 | -0.0030163 | -0.00061526 | -54.9545 | 65.5518 | -57.3441 | 65.332 | -56.694 | -57.1701 | -56.5109 | -56.0761 | 65.6021 | -57.2937 | -57.2067 | -57.2708 | -57.3715 | -57.0374 | -0.091553 | -0.027466 | -0.24719 | 0.55847 | 0.74158 | 0.082397 | 0.83313 | 0.17395 | -0.041199 | 0.022888 | -122.7859 | -0.018311 | 0.21515 | -0.11902 | 0.25635 | -0.07782 | 0.65002 | 122.6761 | 0.022888 | 0.086975 | 122.8958 | 122.8958 | 122.8043 | 122.8546 | -122.9233 | -122.8729 | 122.5845 | 0.045776 | 2.298 | 1.1765
2091.1719 | 122.9279 | -57.225 | 65.625 | -0.052948 | -0.00044654 | 0.063094 | 0.070968 | 0.00016017 | -0.00015811 | 0.0011494 | 0.0047608 | 0.0036657 | 0.0023498 | 0.0081774 | -0.0015061 | -0.0032301 | 0.0015209 | -54.9042 | 65.5792 | -57.2845 | 65.3824 | -56.6254 | -57.0786 | -56.4606 | -56.0394 | 65.6479 | -57.2388 | -57.193 | -57.2159 | -57.3349 | -57.0465 | -0.059509 | -0.045776 | -0.24262 | 0.59967 | 0.76447 | 0.14648 | 0.82397 | 0.20599 | -0.013733 | 0.022888 | -122.818 | 0.009156 | 0.17853 | -0.10986 | 0.19226 | -0.09613 | 0.65918 | 122.6669 | 0.022889 | 0.045777 | 122.8638 | 122.8867 | 122.8043 | 122.8729 | -122.9095 | -122.8638 | 122.6074 | 0.032044 | 2.3209 | 1.1856
2092.1719 | 123.0194 | -57.2113 | 65.6342 | -0.091095 | -1.9142e-05 | 0.063094 | 0.070754 | 0.0022964 | 0.0017645 | 0.0069172 | 0.035278 | -0.00017945 | 0.00064083 | -0.0044262 | -0.0010787 | -0.0045117 | 0.0013073 | -54.863 | 65.5609 | -57.2525 | 65.451 | -56.5292 | -56.987 | -56.369 | -55.9433 | 65.6113 | -57.225 | -57.1518 | -57.1426 | -57.2479 | -56.9733 | -0.041198 | -0.073242 | -0.18311 | 0.68207 | 0.84228 | 0.2243 | 0.88348 | 0.2655 | -0.013733 | -0.022888 | -122.7859 | 0.068665 | 0.23804 | -0.036621 | 0.25177 | -0.022888 | 0.72327 | 122.7036 | 0.082398 | 0.073243 | 122.8134 | 122.8363 | 122.7722 | 122.8226 | -122.8867 | -122.8592 | 122.6624 | 0.05951 | 2.3483 | 1.268
2093.1719 | 123.0331 | -57.193 | 65.6158 | -0.098725 | 0.00040806 | 0.062025 | 0.069472 | 0.0022964 | 5.5488e-05 | 0.0052082 | -0.0013428 | 0.00067495 | -0.00021357 | 0.0017688 | -0.0017197 | -0.0053663 | -0.0044605 | -54.8584 | 65.5701 | -57.2708 | 65.4739 | -56.5338 | -56.9916 | -56.3599 | -55.957 | 65.6204 | -57.2205 | -57.1381 | -57.1426 | -57.2479 | -56.9687 | -0.07782 | -0.045777 | -0.14191 | 0.65918 | 0.83313 | 0.20142 | 0.91095 | 0.27924 | -0.027466 | 0.004577 | -122.7539 | 0.050354 | 0.2243 | -0.054932 | 0.25177 | -0.027466 | 0.737 | 122.7448 | 0.07782 | 0.082397 | 122.8409 | 122.8409 | 122.7631 | 122.8134 | -122.8867 | -122.8363 | 122.6669 | 0.054931 | 2.3346 | 1.236
2094.1719 | 123.0698 | -57.1793 | 65.5563 | -0.075836 | 0.00083526 | 0.06288 | 0.067977 | -0.0043258 | 0.0021917 | 0.0043536 | 0.032227 | 3.4148e-05 | -0.0014954 | -0.0018628 | -0.0049241 | -0.0072889 | 0.0023755 | -54.863 | 65.5426 | -57.2617 | 65.4922 | -56.4972 | -56.9641 | -56.337 | -55.8975 | 65.5975 | -57.2205 | -57.1701 | -57.3807 | -57.1976 | -56.868 | -0.082398 | -0.013732 | -0.064086 | 0.68207 | 0.84228 | 0.21515 | 0.92468 | 0.29755 | -0.041199 | 0.041199 | -122.7264 | -0.20142 | 0.31128 | -0.018311 | 0.35248 | 0.022888 | 0.76447 | 122.7539 | -0.16022 | 0.050354 | 122.8043 | 122.818 | 122.7219 | 122.7768 | -122.818 | -122.7768 | 122.6715 | 0.009155 | 2.3163 | 1.2817
2095.1719 | 122.937 | -57.225 | 65.593 | -0.075836 | 0.0014761 | 0.062025 | 0.072463 | 0.003151 | -0.00015811 | 0.0060626 | -0.080688 | 0.0025975 | 0.00064083 | 0.0054004 | -0.0021469 | -0.0030163 | 0.0017345 | -54.9179 | 65.5472 | -57.3257 | 65.3778 | -56.6483 | -57.1335 | -56.5063 | -56.0577 | 65.6204 | -57.2937 | -57.225 | -57.2754 | -57.3898 | -57.0465 | -0.10071 | -0.045777 | -0.21515 | 0.57678 | 0.71869 | 0.091553 | 0.8194 | 0.19226 | -0.068664 | 0.027465 | -122.818 | -0.050354 | 0.17853 | -0.16479 | 0.24719 | -0.096131 | 0.67749 | 122.7036 | 0.01831 | 0.068664 | 122.8729 | 122.9141 | 122.7722 | 122.8455 | -122.9187 | -122.8867 | 122.6028 | 0 | 2.3071 | 1.1673
2096.1719 | 122.9324 | -57.225 | 65.6158 | 0.015716 | -0.00066014 | 0.060103 | 0.071609 | -0.00048063 | 0.00091009 | 0.0071308 | 0.010864 | 0.0013159 | 0.0019226 | 0.00048702 | -1.0706e-05 | -0.0049389 | -0.00082886 | -54.9271 | 65.6342 | -57.3029 | 65.3458 | -56.6483 | -57.106 | -56.4651 | -56.0623 | 65.6479 | -57.2342 | -57.2113 | -57.2342 | -57.3715 | -57.0694 | -0.077819 | 0.01831 | -0.27008 | 0.57678 | 0.75989 | 0.11902 | 0.83771 | 0.19684 | -0.009155 | 0.032043 | -122.8271 | -0.009155 | 0.15564 | -0.14648 | 0.16479 | -0.13733 | 0.6546 | 122.6486 | 0 | 0.022888 | 122.937 | 122.8821 | 122.8592 | 122.8729 | -122.9187 | -122.85 | 122.5708 | 0.013733 | 2.298 | 1.1627
2097.1719 | 122.9599 | -57.2067 | 65.6158 | -0.052948 | -0.0010873 | 0.062239 | 0.068404 | -0.0013352 | 0.0039007 | 0.0056354 | 0.013916 | -0.0016749 | 0.00042723 | 0.0041186 | -0.0017197 | -0.0021619 | -0.0010425 | -54.8767 | 65.5884 | -57.2617 | 65.419 | -56.5796 | -57.0374 | -56.3919 | -56.0257 | 65.6433 | -57.28 | -57.2159 | -57.1701 | -57.2891 | -57.0145 | -0.054932 | -0.027466 | -0.19684 | 0.62714 | 0.81482 | 0.16937 | 0.86975 | 0.2243 | -0.073242 | 0.027466 | -122.8317 | 0.036621 | 0.19226 | -0.082398 | 0.2655 | -0.009156 | 0.68207 | 122.6807 | 0.10986 | 0.064087 | 122.85 | 122.9233 | 122.7951 | 122.85 | -122.8775 | -122.8958 | 122.6257 | -0.009155 | 2.33 | 1.181
2098.1719 | 122.937 | -57.2067 | 65.6387 | -0.068207 | 0.0014761 | 0.061598 | 0.06755 | 0.0018692 | 0.0013373 | 0.0060626 | 0.023071 | 0.0025975 | 0.001709 | 0.0013416 | -0.00086511 | -0.0057935 | -0.0014697 | -54.8767 | 65.5655 | -57.2754 | 65.4099 | -56.5796 | -57.0328 | -56.4011 | -56.0074 | 65.6158 | -57.2342 | -57.2113 | -57.193 | -57.2937 | -57.0053 | -0.068665 | -0.073242 | -0.22888 | 0.62714 | 0.80566 | 0.17395 | 0.87433 | 0.24262 | -0.027466 | -0.022888 | -122.85 | 0.013733 | 0.20142 | -0.086975 | 0.22888 | -0.059509 | 0.6958 | 122.6852 | 0.041199 | 0.022888 | 122.8409 | 122.85 | 122.7722 | 122.8226 | -122.9141 | -122.8729 | 122.6166 | -0.004578 | 2.33 | 1.1993
2099.1719 | 122.9645 | -57.2296 | 65.6204 | -0.098725 | 0.00062166 | 0.061598 | 0.068832 | 0.00016017 | 0.0019781 | 0.0062762 | 0.013916 | 0.00088875 | 0.0012818 | -0.0020764 | -0.0015061 | -0.0040845 | -0.0010425 | -54.8767 | 65.5838 | -57.2754 | 65.4327 | -56.5796 | -57.0374 | -56.4056 | -56.0028 | 65.6479 | -57.2479 | -57.2113 | -57.2159 | -57.2983 | -57.0099 | -0.045777 | -0.036621 | -0.18768 | 0.65002 | 0.82397 | 0.19226 | 0.86975 | 0.23804 | -0.018311 | 0.027466 | -122.8317 | 0.013733 | 0.21973 | -0.068665 | 0.23804 | -0.050354 | 0.6958 | 122.7081 | 0.032044 | 0.036621 | 122.8592 | 122.8958 | 122.8134 | 122.8775 | -122.8958 | -122.8683 | 122.6624 | 0.01831 | 2.3529 | 1.2268
2100.1719 | 123.0103 | -57.2479 | 65.5746 | -0.098725 | -0.00066014 | 0.062453 | 0.072036 | 0.0010148 | 0.00091009 | 0.0049946 | -0.041016 | 0.0013159 | -0.00021357 | 0.00070062 | -0.0019333 | -0.0036573 | -0.0021107 | -54.9591 | 65.538 | -57.3441 | 65.3275 | -56.6895 | -57.1747 | -56.5063 | -56.0715 | 65.593 | -57.3029 | -57.1838 | -57.2525 | -57.3532 | -57.0328 | -0.09613 | -0.036621 | -0.24719 | 0.55847 | 0.74158 | 0.073242 | 0.83771 | 0.16937 | -0.054931 | 0.018311 | -122.7585 | -0.004577 | 0.21515 | -0.10528 | 0.27008 | -0.050354 | 0.6546 | 122.6715 | 0.050354 | 0.11902 | 122.8821 | 122.8958 | 122.786 | 122.8409 | -122.9187 | -122.8775 | 122.5754 | 0.064087 | 2.2888 | 1.1765
2101.1719 | 122.9874 | -57.225 | 65.6158 | -0.037689 | 0.00040806 | 0.063307 | 0.0699 | 0.00016017 | 0.0021917 | 0.0049946 | 0.029175 | 3.4148e-05 | 0.00064083 | -0.0016492 | -0.0023605 | -0.0021619 | 0.00066654 | -54.8676 | 65.5701 | -57.2617 | 65.4282 | -56.5842 | -57.0328 | -56.4056 | -55.9937 | 65.6387 | -57.2388 | -57.1976 | -57.1976 | -57.2845 | -57.0053 | -0.036621 | -0.045777 | -0.18768 | 0.64087 | 0.8194 | 0.19226 | 0.85602 | 0.22888 | -0.013733 | 0.022888 | -122.8134 | 0.027466 | 0.21973 | -0.059509 | 0.23346 | -0.045776 | 0.67749 | 122.6898 | 0.041199 | 0.041199 | 122.8317 | 122.8775 | 122.7951 | 122.8638 | -122.8775 | -122.8546 | 122.6532 | 0.027466 | 2.3575 | 1.2314
2102.1719 | 123.0423 | -57.1793 | 65.6067 | -0.052948 | -0.00044654 | 0.063094 | 0.0699 | 0.0033646 | 0.0017645 | 0.0049946 | 0.068848 | 0.00088875 | 0.0014954 | -0.00058098 | 0.00041649 | -0.0045117 | -0.0029651 | -55.0827 | 65.5609 | -57.2845 | 65.4556 | -56.5292 | -56.987 | -56.3553 | -55.9113 | 65.5792 | -57.2159 | -57.1426 | -57.1152 | -57.2113 | -56.9366 | -0.10529 | -0.045776 | -0.15106 | 0.65002 | 0.82397 | 0.19226 | 0.92926 | 0.29755 | -0.036621 | -0.027465 | -122.7493 | 0.064087 | 0.24261 | -0.032044 | 0.27923 | 0.004577 | 0.75531 | 122.7402 | 0.10071 | 0.073242 | 122.8455 | 122.7951 | 122.7402 | 122.7585 | -122.8912 | -122.8226 | 122.6349 | 0.036621 | 2.0966 | 1.268
2103.1719 | 122.9645 | -57.1884 | 65.6799 | -0.060578 | -0.0010873 | 0.061812 | 0.0699 | -0.0056076 | 0.0026191 | 0.003072 | -0.03186 | 0.0015295 | 0.001709 | -0.0010084 | -0.00043791 | -0.0034437 | -0.0053149 | -54.9179 | 65.6113 | -57.2937 | 65.3595 | -56.6299 | -57.0877 | -56.4606 | -56.0532 | 65.657 | -57.2342 | -57.225 | -57.2388 | -57.28 | -56.9366 | -0.10529 | -0.068665 | -0.32043 | 0.55847 | 0.72784 | 0.10071 | 0.83313 | 0.20599 | -0.045776 | -0.022889 | -122.905 | -0.050354 | 0.25177 | -0.091552 | 0.29755 | -0.045776 | 0.66376 | 122.6532 | -0.004578 | 0.009155 | 122.905 | 122.8912 | 122.7997 | 122.8455 | -122.9736 | -122.9141 | 122.5479 | -0.036621 | 2.2705 | 1.1353
2104.1719 | 122.9691 | -57.2021 | 65.6845 | -0.045319 | -0.00023294 | 0.061171 | 0.070327 | -0.00090783 | 0.0019781 | 0.0049946 | 0.001709 | 0.00046135 | 0.00064083 | -0.005708 | -0.00065151 | -0.0047253 | 2.554e-05 | -54.9271 | 65.6433 | -57.28 | 65.3595 | -56.6391 | -57.0969 | -56.4606 | -56.0623 | 65.6616 | -57.2617 | -57.2159 | -57.2433 | -57.3395 | -57.106 | -0.07782 | -0.041198 | -0.32501 | 0.56305 | 0.74158 | 0.10529 | 0.8194 | 0.1831 | -0.05951 | -0.022888 | -122.9004 | -0.041199 | 0.09613 | -0.13733 | 0.15564 | -0.07782 | 0.64087 | 122.6395 | 0.018311 | 0.045777 | 122.9233 | 122.9233 | 122.8455 | 122.8638 | -122.9645 | -122.9462 | 122.5616 | -0.013733 | 2.2751 | 1.1398
2105.1719 | 122.9004 | -57.2571 | 65.5701 | -0.060578 | -1.9142e-05 | 0.062239 | 0.075881 | 0.00016017 | 0.0015509 | 0.0054218 | -0.08374 | 0.0015295 | 2.8e-08 | -0.00058098 | -0.0023605 | -0.0019483 | 0.0047253 | -54.9362 | 65.5838 | -57.312 | 65.3366 | -56.6986 | -57.1609 | -56.5201 | -56.1081 | 65.6296 | -57.28 | -57.2433 | -57.3029 | -57.4402 | -57.0694 | -0.054932 | 0.013733 | -0.23346 | 0.55847 | 0.737 | 0.09613 | 0.79193 | 0.15106 | -0.022888 | 0.05951 | -122.8134 | -0.045776 | 0.18768 | -0.18311 | 0.21057 | -0.16022 | 0.6134 | 122.6486 | -0.022888 | 0.036621 | 122.8958 | 122.9095 | 122.8409 | 122.8867 | -122.8821 | -122.85 | 122.5937 | 0.013733 | 2.3209 | 1.149
2106.1719 | 122.9645 | -57.2342 | 65.625 | -0.03006 | 0.00062166 | 0.06288 | 0.071395 | -0.00048063 | 0.0030463 | 0.0067036 | 0.0078126 | 0.0028113 | 0.0025634 | -0.0020764 | -0.00022431 | -0.0051527 | -0.0018971 | -55.0644 | 65.6113 | -57.2983 | 65.3549 | -56.6666 | -57.0923 | -56.4606 | -56.0852 | 65.6296 | -57.2845 | -57.1976 | -57.2342 | -57.3303 | -57.0282 | -0.064087 | -0.013733 | -0.27008 | 0.56763 | 0.77362 | 0.14191 | 0.83771 | 0.20599 | -0.050354 | 0.004578 | -122.8226 | 0 | 0.20599 | -0.09613 | 0.25635 | -0.045776 | 0.63171 | 122.6532 | 0.050354 | 0.086975 | 122.9095 | 122.9141 | 122.8455 | 122.8638 | -122.9233 | -122.9095 | 122.5891 | 0.036621 | 2.1698 | 1.149
2107.1719 | 122.9187 | -57.2296 | 65.6113 | -0.022431 | -0.00023294 | 0.062025 | 0.069472 | 0.00058737 | 0.0045417 | 0.0056354 | 0.032227 | 0.00067495 | 0.0014954 | 0.0015552 | 0.0010575 | -0.0032301 | -0.00040166 | -54.9225 | 65.625 | -57.2708 | 65.3732 | -56.6345 | -57.0923 | -56.4606 | -56.0486 | 65.657 | -57.2754 | -57.2296 | -57.225 | -57.3212 | -57.0419 | -0.041199 | 0.013733 | -0.23804 | 0.59509 | 0.76904 | 0.13733 | 0.81024 | 0.17853 | -0.045777 | 0.045776 | -122.8409 | 0.004577 | 0.18768 | -0.091553 | 0.23346 | -0.045776 | 0.63629 | 122.644 | 0.050354 | 0.045777 | 122.8958 | 122.9324 | 122.8546 | 122.8867 | -122.8821 | -122.8867 | 122.6028 | 0 | 2.3071 | 1.181
2108.1719 | 122.9965 | -57.2205 | 65.6067 | -0.098725 | -0.0013009 | 0.059889 | 0.069045 | -0.003685 | 0.0015509 | 0.0062762 | 0.035278 | 3.4148e-05 | 0.00064083 | -0.0042126 | -0.0010787 | -0.0049389 | 0.00023934 | -54.8767 | 65.5975 | -57.2662 | 65.4419 | -56.5384 | -56.9962 | -56.3828 | -55.9433 | 65.6067 | -57.2159 | -57.1518 | -57.1609 | -57.225 | -56.9687 | -0.045776 | -0.009155 | -0.16479 | 0.68207 | 0.83771 | 0.2243 | 0.88348 | 0.27008 | 0.004578 | 0 | -122.7585 | 0.059509 | 0.25177 | -0.004578 | 0.24719 | -0.009156 | 0.72784 | 122.7081 | 0.054931 | 0.064087 | 122.8638 | 122.8226 | 122.818 | 122.8271 | -122.8729 | -122.8226 | 122.6624 | 0.068665 | 2.3438 | 1.2772
2109.1719 | 122.9279 | -57.225 | 65.6479 | -0.03006 | 0.0027579 | 0.061385 | 0.069472 | -0.0017624 | 0.0024053 | 0.0034992 | 0.029175 | 0.0011023 | 0.0014954 | -0.00079478 | -0.00043791 | -0.0042981 | 0.0019483 | -54.895 | 65.5838 | -57.2845 | 65.3961 | -56.6345 | -57.0786 | -56.4331 | -56.0532 | 65.6433 | -57.2662 | -57.2113 | -57.2113 | -57.3166 | -57.0282 | -0.059509 | -0.064087 | -0.25177 | 0.59052 | 0.79193 | 0.14648 | 0.85144 | 0.20599 | -0.041198 | -0.004577 | -122.8592 | 0.013733 | 0.19684 | -0.091552 | 0.23804 | -0.050354 | 0.65002 | 122.6807 | 0.054931 | 0.054931 | 122.8683 | 122.9095 | 122.8088 | 122.8683 | -122.9324 | -122.9141 | 122.6212 | 0.013733 | 2.33 | 1.1719
2110.1719 | 122.937 | -57.2296 | 65.6387 | -0.03006 | -1.9142e-05 | 0.061598 | 0.071609 | -0.00069423 | 0.0021917 | 0.005849 | 0.02002 | 0.0040929 | -0.00042717 | 0.0028368 | -0.0017197 | -0.0021619 | -0.00082886 | -54.9225 | 65.5975 | -57.2891 | 65.3595 | -56.6666 | -57.0831 | -56.456 | -56.0394 | 65.6937 | -57.2296 | -57.2388 | -57.2296 | -57.3349 | -57.0419 | -0.05951 | -0.041199 | -0.27924 | 0.56305 | 0.77362 | 0.14648 | 0.83313 | 0.20599 | 0 | 0.054932 | -122.8775 | 0 | 0.18768 | -0.10529 | 0.18768 | -0.10529 | 0.62256 | 122.6486 | 0 | -0.009156 | 122.8867 | 122.9233 | 122.8271 | 122.9233 | -122.9279 | -122.8683 | 122.5891 | -0.009156 | 2.3071 | 1.1902
2111.1719 | 122.9691 | -57.2433 | 65.6479 | 0.023346 | 0.00040806 | 0.064803 | 0.070541 | 0.0012284 | 0.0015509 | 0.009267 | -0.022705 | -0.00082025 | 0.001709 | -0.00036738 | -0.0010787 | -0.0038709 | -0.0031787 | -54.9271 | 65.6387 | -57.28 | 65.3732 | -56.6666 | -57.0969 | -56.4789 | -56.0669 | 65.657 | -57.2433 | -57.1884 | -57.2067 | -57.3212 | -57.019 | -0.036621 | -0.009155 | -0.27466 | 0.57678 | 0.76447 | 0.14648 | 0.80109 | 0.1831 | 0 | 0.009155 | -122.8363 | 0.036621 | 0.2243 | -0.07782 | 0.2243 | -0.07782 | 0.6134 | 122.6532 | 0.036621 | 0.054931 | 122.9187 | 122.9004 | 122.8821 | 122.9004 | -122.9279 | -122.8912 | 122.6166 | 0.054931 | 2.3163 | 1.1765
2112.1719 | 122.9691 | -57.2113 | 65.6158 | -0.045319 | -0.0015145 | 0.062025 | 0.070541 | -0.001976 | 0.0028327 | 0.0052082 | -0.0074462 | 0.0011023 | 0.0014954 | 0.0036914 | -0.0017197 | -0.0038709 | -0.0014697 | -54.9271 | 65.6342 | -57.312 | 65.3549 | -56.6574 | -57.1243 | -56.488 | -56.0669 | 65.6616 | -57.2571 | -57.2113 | -57.2296 | -57.3395 | -57.019 | -0.10071 | 0.01831 | -0.26093 | 0.55389 | 0.72327 | 0.086975 | 0.82398 | 0.18768 | -0.045776 | 0.045776 | -122.8271 | -0.01831 | 0.19226 | -0.12817 | 0.23804 | -0.082398 | 0.6546 | 122.6669 | 0.027466 | 0.045776 | 122.9462 | 122.9187 | 122.8455 | 122.8729 | -122.9279 | -122.8729 | 122.5662 | 0 | 2.2842 | 1.1444
2113.1719 | 122.9462 | -57.2205 | 65.6296 | -0.052948 | 0.00019446 | 0.061385 | 0.07289 | -0.00048063 | 0.0026191 | 0.0064898 | -0.0013428 | 0.0019567 | 0.00042723 | -0.0059216 | -0.00086511 | -0.0032301 | 0.0023755 | -55.0461 | 65.6342 | -57.2754 | 65.3458 | -56.6803 | -57.0877 | -56.4606 | -56.0715 | 65.6433 | -57.2479 | -57.2159 | -57.2113 | -57.3349 | -57.0007 | -0.054932 | 0.004577 | -0.28381 | 0.54016 | 0.75989 | 0.13275 | 0.81482 | 0.18768 | -0.027466 | 0.013733 | -122.8455 | 0.009155 | 0.21973 | -0.11444 | 0.24719 | -0.086975 | 0.59509 | 122.6212 | 0.036621 | 0.032044 | 122.9095 | 122.8912 | 122.8546 | 122.8638 | -122.905 | -122.8775 | 122.5662 | 0.004578 | 2.1744 | 1.149
2114.1719 | 122.9828 | -57.2296 | 65.6113 | -0.052948 | -0.0017281 | 0.061385 | 0.069045 | 0.0012284 | 0.0024053 | 0.00414 | -0.0013428 | 0.0011023 | 0.0025634 | 0.008391 | -0.0017197 | -0.0034437 | 0.0015209 | -54.9225 | 65.6204 | -57.2708 | 65.3641 | -56.6666 | -57.1518 | -56.4789 | -56.0669 | 65.6525 | -57.2662 | -57.2021 | -57.2342 | -57.3303 | -57.0328 | -0.041199 | 0.009155 | -0.24719 | 0.56305 | 0.75073 | 0.07782 | 0.79193 | 0.11902 | -0.036621 | 0.041199 | -122.8134 | -0.004578 | 0.19684 | -0.10071 | 0.23346 | -0.064087 | 0.60425 | 122.6349 | 0.032043 | 0.064087 | 122.8912 | 122.9187 | 122.85 | 122.8821 | -122.8821 | -122.8775 | 122.5937 | 0.027466 | 2.3071 | 1.1627
2115.1719 | 123.0103 | -57.193 | 65.6067 | -0.098725 | 0.00019446 | 0.061171 | 0.067977 | -0.0021896 | 0.0030463 | 0.0045672 | 0.044434 | -0.00082025 | 0.0021362 | -0.0044262 | -0.0015061 | -0.0013073 | -0.0016833 | -54.8538 | 65.5975 | -57.2617 | 65.451 | -56.5292 | -56.9962 | -56.3644 | -55.9479 | 65.6021 | -57.2388 | -57.1518 | -57.1335 | -57.2342 | -56.955 | -0.068665 | -0.009155 | -0.15564 | 0.66376 | 0.82855 | 0.19684 | 0.89722 | 0.2655 | -0.045777 | -0.004577 | -122.7585 | 0.059509 | 0.23804 | -0.041199 | 0.28381 | 0.004578 | 0.73242 | 122.7127 | 0.10529 | 0.086976 | 122.8592 | 122.8409 | 122.7905 | 122.7951 | -122.8683 | -122.8455 | 122.644 | 0.041199 | 2.3392 | 1.2451
2116.1719 | 122.9507 | -57.2662 | 65.6021 | -0.060578 | -0.00044654 | 0.061385 | 0.070327 | -0.00026703 | 0.00069649 | 0.0060626 | 0.0078126 | 0.00067495 | 0.0019226 | -0.0018628 | -0.00022431 | -0.0036573 | -0.0018971 | -54.9225 | 65.6342 | -57.28 | 65.3687 | -56.6574 | -57.0969 | -56.4651 | -56.0715 | 65.6525 | -57.2571 | -57.2479 | -57.2205 | -57.3669 | -57.0602 | -0.013733 | 0.032043 | -0.23346 | 0.60883 | 0.80109 | 0.16937 | 0.81482 | 0.1831 | 0.009155 | 0.050354 | -122.85 | 0.045776 | 0.20599 | -0.10071 | 0.19684 | -0.10986 | 0.62256 | 122.6486 | 0.036621 | 0.009155 | 122.9141 | 122.9095 | 122.9004 | 122.9187 | -122.8821 | -122.8592 | 122.6349 | 0.01831 | 2.3438 | 1.1948
2117.1719 | 122.9462 | -57.2296 | 65.6342 | -0.083466 | 0.00040806 | 0.063734 | 0.071181 | -0.0024032 | 0.0039007 | 0.0022174 | -0.019653 | 0.00046135 | 0.003418 | -0.0016492 | -0.0030013 | -0.0021619 | 0.00066654 | -54.8996 | 65.6204 | -57.2937 | 65.3778 | -56.6803 | -57.0969 | -56.4697 | -56.0623 | 65.6525 | -57.2571 | -57.2067 | -57.2113 | -57.3349 | -57.0099 | -0.064087 | -0.013733 | -0.25635 | 0.54932 | 0.75989 | 0.13275 | 0.82397 | 0.19684 | -0.027466 | 0.018311 | -122.8409 | 0.01831 | 0.21973 | -0.10529 | 0.24719 | -0.07782 | 0.6134 | 122.6715 | 0.045776 | 0.050354 | 122.9141 | 122.9095 | 122.85 | 122.8821 | -122.9279 | -122.8912 | 122.6074 | 0.022888 | 2.33 | 1.1673
2118.1719 | 122.9462 | -57.2571 | 65.6616 | -0.045319 | 0.0012625 | 0.062666 | 0.070113 | 0.0012284 | 0.0028327 | 0.0064898 | 0.02002 | 0.00024775 | -0.0012818 | -0.0020764 | -0.0017197 | -0.0049389 | -0.0010425 | -54.9225 | 65.625 | -57.2891 | 65.3778 | -56.6483 | -57.0969 | -56.456 | -56.0577 | 65.6662 | -57.2525 | -57.2342 | -57.2388 | -57.3166 | -57.019 | -0.032044 | -0.036621 | -0.28381 | 0.60883 | 0.80109 | 0.16022 | 0.83313 | 0.19226 | 0.004578 | 0.004578 | -122.8958 | 0.01831 | 0.23804 | -0.059509 | 0.23346 | -0.064087 | 0.64087 | 122.6669 | 0.013732 | 0.01831 | 122.9141 | 122.9187 | 122.8821 | 122.9233 | -122.9507 | -122.9141 | 122.6349 | 0.022888 | 2.3346 | 1.1993
2119.1719 | 122.9324 | -57.2342 | 65.6387 | -0.052948 | 0.00062166 | 0.062025 | 0.07225 | 0.0010148 | 0.00091009 | 0.0043536 | 0.010864 | 0.0023839 | 0.0040588 | 0.0015552 | -0.0015061 | -0.0038709 | -0.0023243 | -54.9088 | 65.6113 | -57.2891 | 65.387 | -56.6437 | -57.1152 | -56.456 | -56.0349 | 65.6479 | -57.2525 | -57.225 | -57.2205 | -57.312 | -57.0282 | -0.054932 | -0.027466 | -0.25177 | 0.59052 | 0.7782 | 0.11902 | 0.83313 | 0.17395 | -0.01831 | 0.009155 | -122.8638 | 0.013733 | 0.20599 | -0.07782 | 0.2243 | -0.05951 | 0.64545 | 122.6761 | 0.032043 | 0.027465 | 122.9004 | 122.9004 | 122.8455 | 122.8821 | -122.9279 | -122.8912 | 122.6212 | 0.009155 | 2.3254 | 1.1993
2120.1719 | 122.9416 | -57.2342 | 65.6387 | -0.068207 | -0.00044654 | 0.059676 | 0.069686 | -0.0015488 | 0.0013373 | 0.0056354 | 0.03833 | -0.0010339 | 0.00042723 | 0.0013416 | -0.0012925 | -0.0053663 | 0.00066654 | -54.8721 | 65.6204 | -57.2708 | 65.387 | -56.6208 | -57.0831 | -56.4743 | -56.0257 | 65.6616 | -57.2525 | -57.225 | -57.2205 | -57.3074 | -57.019 | -0.036621 | -0.018311 | -0.25177 | 0.6134 | 0.75989 | 0.15106 | 0.79651 | 0.18768 | -0.01831 | 0.022888 | -122.8638 | 0.013733 | 0.21515 | -0.073242 | 0.23346 | -0.054932 | 0.65002 | 122.6578 | 0.032043 | 0.027465 | 122.8912 | 122.9141 | 122.8546 | 122.8958 | -122.9095 | -122.8912 | 122.6212 | 0.009155 | 2.3621 | 1.2085
2121.1719 | 122.9919 | -57.2388 | 65.6433 | -0.060578 | 0.00083526 | 0.062025 | 0.068404 | -0.0017624 | 0.0026191 | 0.0060626 | 0.050537 | 0.0017431 | 0.0014954 | -0.0067762 | -0.0019333 | -0.0042981 | -0.00018806 | -54.8721 | 65.6113 | -57.2662 | 65.3915 | -56.6299 | -57.0877 | -56.4423 | -56.0257 | 65.6616 | -57.2388 | -57.2067 | -57.2205 | -57.3212 | -57.019 | -0.027465 | -0.032044 | -0.25177 | 0.60883 | 0.79651 | 0.15106 | 0.82397 | 0.17853 | 0 | 0.01831 | -122.85 | 0.018311 | 0.21973 | -0.082397 | 0.21973 | -0.082397 | 0.63629 | 122.6578 | 0.018311 | 0.032044 | 122.8775 | 122.9004 | 122.85 | 122.9004 | -122.9095 | -122.8821 | 122.6303 | 0.032044 | 2.3666 | 1.2131
2122.1719 | 123.0194 | -57.1884 | 65.625 | -0.12161 | 0.0033987 | 0.062239 | 0.069472 | -0.0024032 | 0.0015509 | 0.0060626 | 0.056641 | 0.0011023 | -0.00064077 | -0.002931 | -0.00086511 | -0.0053663 | -0.0031787 | -54.8492 | 65.5518 | -57.28 | 65.4831 | -56.543 | -56.9916 | -56.3873 | -55.9433 | 65.6158 | -57.2525 | -57.1381 | -57.1335 | -57.2296 | -56.9458 | -0.091552 | -0.073242 | -0.14191 | 0.64545 | 0.80109 | 0.19684 | 0.89264 | 0.28839 | -0.064086 | -0.009155 | -122.7631 | 0.054932 | 0.24261 | -0.041198 | 0.3067 | 0.022888 | 0.737 | 122.7631 | 0.11902 | 0.11444 | 122.8317 | 122.8683 | 122.7402 | 122.8043 | -122.905 | -122.8775 | 122.6715 | 0.050354 | 2.3392 | 1.2451
2123.1719 | 122.9736 | -57.2296 | 65.6342 | -0.060578 | -0.0023691 | 0.06053 | 0.070113 | -0.0015488 | -0.0010125 | 0.0090534 | 0.0078126 | 3.4148e-05 | 0.001709 | 0.0028368 | -0.00086511 | -0.0049389 | 0.0042981 | -54.9225 | 65.625 | -57.2983 | 65.3732 | -56.6574 | -57.0923 | -56.4606 | -56.0715 | 65.6479 | -57.2617 | -57.0786 | -57.2296 | -57.4768 | -57.1564 | -0.068665 | -0.009155 | -0.26093 | 0.5722 | 0.76904 | 0.13733 | 0.83771 | 0.20599 | -0.032044 | 0.013733 | -122.7127 | 0 | 0.073242 | -0.24719 | 0.10529 | -0.21515 | 0.64087 | 122.6715 | 0.032044 | 0.18311 | 122.9233 | 122.9095 | 122.8546 | 122.8775 | -122.9324 | -122.8958 | 122.6028 | 0.15106 | 2.3071 | 1.1581
2124.1719 | 122.9004 | -57.2067 | 65.6616 | -0.083466 | 0.00083526 | 0.061171 | 0.067977 | -0.0011214 | -0.0010125 | 0.0071308 | 0.016968 | 0.0019567 | 0.0025634 | -0.0020764 | -0.0010787 | -0.0047253 | -0.00040166 | -54.9133 | 65.6204 | -57.2617 | 65.3687 | -56.6483 | -57.0969 | -56.4651 | -56.044 | 65.6525 | -57.2617 | -57.2067 | -57.2433 | -57.3349 | -57.0328 | -0.054932 | -0.041199 | -0.29297 | 0.55847 | 0.74158 | 0.10986 | 0.79651 | 0.16479 | -0.054932 | -0.009155 | -122.8683 | -0.036621 | 0.17395 | -0.12817 | 0.22888 | -0.073242 | 0.6134 | 122.6303 | 0.018311 | 0.054932 | 122.8821 | 122.9141 | 122.8271 | 122.8592 | -122.9233 | -122.9233 | 122.5754 | 0 | 2.2934 | 1.1627
2125.1719 | 122.9599 | -57.2021 | 65.6479 | -0.045319 | 0.00040806 | 0.062453 | 0.071395 | -0.0032578 | 0.0015509 | 0.0045672 | 0.016968 | 0.0023839 | 0.0025634 | 0.0047594 | -0.00065151 | -0.0040845 | 0.0015209 | -54.8676 | 65.6342 | -57.28 | 65.3732 | -56.6437 | -57.0969 | -56.4606 | -56.0577 | 65.657 | -57.2479 | -57.2296 | -57.2296 | -57.3257 | -57.0374 | -0.07782 | -0.013733 | -0.27466 | 0.55847 | 0.74158 | 0.10529 | 0.8194 | 0.1831 | -0.045777 | 0.009155 | -122.8775 | -0.027466 | 0.16479 | -0.1236 | 0.21057 | -0.07782 | 0.63629 | 122.6532 | 0.018311 | 0.018311 | 122.9141 | 122.905 | 122.8363 | 122.8592 | -122.9279 | -122.8958 | 122.5754 | -0.027466 | 2.3346 | 1.1444
2126.1719 | 122.9462 | -57.2113 | 65.625 | -0.060578 | -0.0010873 | 0.06288 | 0.07289 | 0.00037377 | 0.0026191 | 0.0064898 | -0.01355 | 0.00024775 | 0.00085443 | 5.9824e-05 | -0.0027877 | -0.0053663 | 0.0025891 | -54.8996 | 65.6158 | -57.28 | 65.2405 | -56.6711 | -57.0923 | -56.5247 | -56.0669 | 65.6296 | -57.2342 | -57.2296 | -57.2342 | -57.3349 | -57.019 | -0.068664 | -0.009155 | -0.38452 | 0.54016 | 0.68665 | 0.11902 | 0.75531 | 0.18768 | -0.022888 | 0.004578 | -122.8546 | -0.022888 | 0.19226 | -0.1236 | 0.21515 | -0.10071 | 0.60882 | 122.5204 | 0 | 0.004578 | 122.8958 | 122.8638 | 122.8271 | 122.8409 | -122.905 | -122.8592 | 122.4518 | -0.01831 | 2.3117 | 1.1444
2127.1719 | 122.9416 | -57.2205 | 65.6479 | -0.060578 | 0.0012625 | 0.062025 | 0.068618 | 0.0040054 | 0.00069649 | 0.0071308 | 0.026123 | 0.0019567 | 0.00042723 | -0.0025036 | -0.0017197 | -0.0055799 | 0.0038709 | -54.8676 | 65.5975 | -57.2479 | 65.387 | -56.6254 | -57.074 | -56.4331 | -56.044 | 65.6479 | -57.2296 | -57.2021 | -57.2113 | -57.3166 | -57.0236 | -0.027466 | -0.050354 | -0.26093 | 0.59509 | 0.78735 | 0.14648 | 0.81482 | 0.17395 | -0.009155 | 0 | -122.85 | 0.009155 | 0.19684 | -0.09613 | 0.20599 | -0.086975 | 0.62256 | 122.6349 | 0.01831 | 0.027466 | 122.8455 | 122.8775 | 122.818 | 122.8683 | -122.8958 | -122.8775 | 122.6074 | 0.018311 | 2.3529 | 1.1765
2128.1719 | 122.9599 | -57.2296 | 65.657 | -0.091095 | 0.00019446 | 0.063734 | 0.069259 | 0.0020828 | 0.0026191 | 0.0094806 | 0.029175 | 0.0019567 | 0.0012818 | 0.0013416 | 0.00041649 | -0.0055799 | 0.0025891 | -54.8538 | 65.593 | -57.2937 | 65.3961 | -56.6071 | -57.0602 | -56.4239 | -56.0074 | 65.6433 | -57.2433 | -57.193 | -57.2113 | -57.3303 | -57.0282 | -0.064087 | -0.064086 | -0.26093 | 0.62256 | 0.80566 | 0.16937 | 0.86975 | 0.23346 | -0.013733 | -0.013732 | -122.85 | 0.01831 | 0.20142 | -0.10071 | 0.21515 | -0.086975 | 0.68664 | 122.6898 | 0.032043 | 0.050354 | 122.8867 | 122.8867 | 122.8226 | 122.8729 | -122.9507 | -122.9004 | 122.6257 | 0.036621 | 2.3758 | 1.2222
2129.1719 | 123.024 | -57.1884 | 65.6067 | -0.12161 | -0.00066014 | 0.061171 | 0.069259 | 0.00058737 | 0.0011237 | 0.0081988 | 0.056641 | -0.00082025 | 0.0021362 | -0.0010084 | -0.0012925 | -0.0045117 | 0.00045294 | -54.8492 | 65.5838 | -57.2891 | 65.4739 | -56.5384 | -56.987 | -56.3736 | -55.9296 | 65.6204 | -57.2205 | -57.1289 | -57.1243 | -57.2342 | -56.9366 | -0.10071 | -0.022888 | -0.13275 | 0.65002 | 0.81482 | 0.20142 | 0.91553 | 0.30212 | -0.032043 | 0.013733 | -122.7356 | 0.064087 | 0.25177 | -0.045776 | 0.28381 | -0.013733 | 0.75073 | 122.7631 | 0.09613 | 0.091553 | 122.8729 | 122.8409 | 122.7722 | 122.8088 | -122.8958 | -122.8271 | 122.6624 | 0.05951 | 2.3392 | 1.2589
2130.1719 | 123.0469 | -57.1838 | 65.6067 | -0.037689 | 0.0016899 | 0.063307 | 0.068832 | 0.0044328 | 0.0013373 | 0.0011494 | 0.044434 | -0.00017945 | 0.0023498 | 5.9824e-05 | -0.0038559 | -0.0051527 | -0.0040333 | -54.895 | 65.5838 | -57.2479 | 65.4648 | -56.5292 | -56.987 | -56.3873 | -55.9479 | 65.625 | -57.2342 | -57.1243 | -57.1198 | -57.2205 | -56.9321 | -0.064087 | -0.022888 | -0.14191 | 0.6546 | 0.79651 | 0.19684 | 0.8606 | 0.26093 | -0.050354 | 0.018311 | -122.731 | 0.064087 | 0.25177 | -0.036621 | 0.30212 | 0.013733 | 0.71869 | 122.7127 | 0.11444 | 0.10986 | 122.8317 | 122.8592 | 122.7676 | 122.8088 | -122.8546 | -122.8409 | 122.6486 | 0.059509 | 2.2888 | 1.236
2131.1719 | 122.8867 | -57.225 | 65.6342 | 0.038605 | -0.00044654 | 0.061598 | 0.070327 | 0.0035782 | 0.0017645 | 0.0064898 | -0.0013428 | -0.00017945 | -0.00042717 | 0.001128 | -0.0015061 | -0.0045117 | -0.0044605 | -54.9088 | 65.6113 | -57.2845 | 65.3549 | -56.6437 | -57.1014 | -56.4697 | -56.0532 | 65.6754 | -57.2388 | -57.2021 | -57.0099 | -57.4173 | -57.1106 | -0.059509 | -0.022888 | -0.27924 | 0.58136 | 0.75531 | 0.1236 | 0.81482 | 0.18311 | -0.013733 | 0.041199 | -122.8363 | 0.21515 | 0.11444 | -0.19226 | 0.12817 | -0.17853 | 0.64087 | 122.6395 | 0.22888 | 0.036622 | 122.8958 | 122.9141 | 122.8363 | 122.9004 | -122.9187 | -122.8729 | 122.58 | 0.022889 | 2.3163 | 1.1719
2132.1719 | 122.937 | -57.193 | 65.6799 | -0.060578 | -0.0017281 | 0.062666 | 0.069472 | 0.0012284 | 0.0051825 | 0.0056354 | 0.001709 | 0.00088875 | 0.0019226 | -0.0016492 | -0.0019333 | -0.0038709 | 0.00088014 | -54.9179 | 65.6067 | -57.2937 | 65.3778 | -56.6574 | -57.0969 | -56.4651 | -56.044 | 65.6616 | -57.2525 | -57.2067 | -57.2205 | -57.2433 | -56.8588 | -0.10071 | -0.073243 | -0.30212 | 0.53558 | 0.72784 | 0.09613 | 0.82855 | 0.19684 | -0.059509 | -0.018311 | -122.8867 | -0.027466 | 0.33417 | -0.050354 | 0.39368 | 0.009155 | 0.63629 | 122.6715 | 0.032043 | 0.045776 | 122.9004 | 122.9141 | 122.7997 | 122.8546 | -122.9736 | -122.9324 | 122.5708 | -0.013733 | 2.2751 | 1.149
2133.1719 | 122.8775 | -57.2159 | 65.6708 | -0.014801 | -0.00066014 | 0.061171 | 0.0699 | -0.0013352 | 0.00091009 | 0.0045672 | 0.02002 | 0.0017431 | 0.0014954 | -0.0031446 | -0.00065151 | -0.0036573 | -0.00061526 | -54.8904 | 65.657 | -57.2754 | 65.3732 | -56.6574 | -57.0923 | -56.4743 | -56.0532 | 65.6433 | -57.2159 | -57.225 | -57.2067 | -57.312 | -57.0328 | -0.05951 | -0.013733 | -0.29755 | 0.55847 | 0.74158 | 0.1236 | 0.80109 | 0.18311 | 0 | -0.027465 | -122.8958 | 0.009155 | 0.18311 | -0.096131 | 0.18311 | -0.096131 | 0.61798 | 122.6486 | 0.009155 | -0.009156 | 122.9324 | 122.8592 | 122.8729 | 122.8592 | -122.9462 | -122.8867 | 122.5891 | -0.009156 | 2.3254 | 1.1627
2134.1719 | 122.9416 | -57.2296 | 65.6616 | -0.10635 | 0.00040806 | 0.060744 | 0.069472 | -5.343e-05 | 0.0024053 | 0.003072 | -0.025757 | 0.0013159 | 0.001709 | 0.0032642 | -0.00086511 | -0.0053663 | -0.0029651 | -54.9088 | 65.6113 | -57.2571 | 65.3824 | -56.6391 | -57.0969 | -56.456 | -56.0532 | 65.6479 | -57.2433 | -57.2067 | -57.2159 | -57.3212 | -57.0328 | -0.027466 | -0.050354 | -0.27924 | 0.59051 | 0.77362 | 0.13275 | 0.80109 | 0.16022 | -0.013733 | -0.013733 | -122.8683 | 0.013733 | 0.19684 | -0.091553 | 0.21057 | -0.07782 | 0.61798 | 122.6395 | 0.027466 | 0.036621 | 122.8683 | 122.8912 | 122.8409 | 122.8775 | -122.9187 | -122.905 | 122.612 | 0.022888 | 2.3209 | 1.1765
2135.1719 | 122.937 | -57.2342 | 65.6204 | 0.023346 | -0.0019417 | 0.063521 | 0.069045 | 0.00058737 | 0.0013373 | 0.0049946 | -0.019653 | 0.0015295 | 0.0012818 | -0.0025036 | -0.0015061 | -0.0034437 | -0.0010425 | -54.9911 | 65.6433 | -57.2937 | 65.3732 | -56.6711 | -57.0969 | -56.4743 | -56.0577 | 65.6616 | -57.2571 | -57.2113 | -57.2205 | -57.3349 | -57.0099 | -0.059509 | 0.022889 | -0.24719 | 0.56305 | 0.75989 | 0.13733 | 0.8194 | 0.19684 | -0.022888 | 0.041199 | -122.8317 | 0.013733 | 0.2243 | -0.10071 | 0.24719 | -0.07782 | 0.62256 | 122.6669 | 0.036621 | 0.045776 | 122.937 | 122.9187 | 122.8775 | 122.8958 | -122.9141 | -122.8775 | 122.6074 | 0.022888 | 2.243 | 1.1765
2136.1719 | 123.0194 | -57.1838 | 65.5975 | -0.091095 | -0.0010873 | 0.063734 | 0.067763 | 0.0020828 | 0.0017645 | 0.0064898 | 0.041382 | 0.0025975 | 0.0023498 | 0.00048702 | -0.0032151 | -0.0034437 | 0.0036571 | -54.8355 | 65.5701 | -57.2708 | 65.4602 | -56.543 | -56.9916 | -56.3919 | -55.9479 | 65.6296 | -57.2159 | -57.1472 | -57.1426 | -57.2479 | -56.955 | -0.086975 | -0.027466 | -0.13733 | 0.64087 | 0.79193 | 0.19226 | 0.87891 | 0.27924 | -0.032043 | 0.032044 | -122.7448 | 0.041199 | 0.22888 | -0.064087 | 0.26093 | -0.032044 | 0.72784 | 122.731 | 0.073242 | 0.068664 | 122.8409 | 122.8455 | 122.7539 | 122.8134 | -122.8683 | -122.8134 | 122.644 | 0.036621 | 2.3483 | 1.236
2137.1719 | 123.0011 | -57.193 | 65.6387 | -0.083466 | 0.0010489 | 0.062239 | 0.066909 | -0.0011214 | 0.0021917 | 0.0069172 | 0.035278 | 0.00024775 | 0.00064083 | 0.001128 | -0.0017197 | -0.0045117 | -0.0031787 | -54.8309 | 65.5838 | -57.2708 | 65.4602 | -56.5475 | -56.9824 | -56.3828 | -55.9708 | 65.6021 | -57.2296 | -57.1381 | -57.1381 | -57.225 | -56.955 | -0.07782 | -0.054932 | -0.17853 | 0.64545 | 0.81024 | 0.21057 | 0.88806 | 0.28839 | -0.036621 | -0.036621 | -122.7768 | 0.054931 | 0.23804 | -0.032044 | 0.27466 | 0.004577 | 0.72327 | 122.731 | 0.091552 | 0.091552 | 122.8546 | 122.8317 | 122.7768 | 122.7951 | -122.9095 | -122.8683 | 122.6532 | 0.054931 | 2.3621 | 1.2222
2138.1719 | 122.9233 | -57.225 | 65.6342 | -0.037689 | -0.00023294 | 0.062025 | 0.070541 | 0.0016556 | -0.00058531 | 0.0037128 | -0.062378 | 0.00024775 | 0.00021363 | 5.9824e-05 | -1.0706e-05 | -0.0036573 | -0.00040166 | -54.8859 | 65.625 | -57.2983 | 65.332 | -56.488 | -56.955 | -56.5704 | -56.0257 | 65.6479 | -57.2708 | -57.193 | -57.2067 | -57.3212 | -57.0099 | -0.073242 | -0.009155 | -0.30212 | 0.737 | 0.6546 | 0.27008 | 0.72784 | 0.34332 | -0.045776 | 0.013733 | -122.8271 | 0.018311 | 0.21515 | -0.09613 | 0.26093 | -0.050354 | 0.81024 | 122.6303 | 0.064087 | 0.07782 | 122.9233 | 122.9187 | 122.85 | 122.8729 | -122.9324 | -122.905 | 122.5571 | 0.032044 | 2.3392 | 1.1993
2139.1719 | 122.9645 | -57.2113 | 65.6204 | -0.083466 | 0.0014761 | 0.060744 | 0.069259 | 0.00080117 | 0.0024053 | 0.0037128 | 0.047485 | 0.0019567 | 0.0042724 | -0.0050672 | -0.0023605 | -0.0038709 | -0.0025379 | -54.9042 | 65.6296 | -57.312 | 65.3641 | -56.6574 | -57.0831 | -56.4697 | -56.1859 | 65.6845 | -57.2479 | -57.2113 | -57.2205 | -57.3349 | -57.0145 | -0.10071 | 0.009156 | -0.25635 | 0.55389 | 0.74158 | 0.12817 | 0.84229 | 0.22888 | -0.036621 | 0.064087 | -122.8317 | -0.009155 | 0.19684 | -0.1236 | 0.23346 | -0.086975 | 0.6546 | 122.6761 | 0.027466 | 0.036621 | 122.9416 | 122.9324 | 122.8409 | 122.8958 | -122.9324 | -122.8683 | 122.5754 | 0 | 2.3071 | 1.0254
2140.1719 | 122.9279 | -57.2342 | 65.6296 | -0.068207 | 0.00062166 | 0.060744 | 0.07289 | -0.00090783 | 0.0032599 | 0.005849 | -0.010498 | 0.0017431 | -0.00021357 | 0.00048702 | 0.0010575 | -0.0042981 | -0.00040166 | -54.8904 | 65.6067 | -57.2845 | 65.3824 | -56.6483 | -57.0969 | -56.456 | -56.0623 | 65.6662 | -57.2433 | -57.2891 | -57.1884 | -57.3532 | -57.0465 | -0.050354 | -0.022889 | -0.24719 | 0.58594 | 0.7782 | 0.13733 | 0.82855 | 0.18768 | -0.009155 | 0.036621 | -122.9187 | 0.045776 | 0.18768 | -0.11902 | 0.19684 | -0.10986 | 0.63629 | 122.6669 | 0.054931 | -0.045777 | 122.8912 | 122.9095 | 122.8409 | 122.9004 | -122.9141 | -122.8729 | 122.6166 | -0.054932 | 2.3438 | 1.1719
2141.1719 | 122.9416 | -57.193 | 65.6754 | -0.083466 | 0.0016899 | 0.060316 | 0.067763 | 0.0016556 | 0.0013373 | 0.0047808 | 0.016968 | 0.0015295 | 0.0023498 | -0.0035718 | -0.0010787 | -0.0032301 | 0.0023755 | -54.8721 | 65.6387 | -57.2708 | 65.3824 | -56.6574 | -57.1014 | -56.4743 | -56.0669 | 65.6342 | -57.2433 | -57.2159 | -57.2205 | -57.1884 | -56.8497 | -0.07782 | -0.036621 | -0.29297 | 0.53558 | 0.71869 | 0.091553 | 0.79651 | 0.16937 | -0.050354 | -0.041199 | -122.8912 | -0.027466 | 0.34332 | 0.004577 | 0.39368 | 0.054931 | 0.6134 | 122.6532 | 0.022888 | 0.027466 | 122.9095 | 122.8775 | 122.8317 | 122.8271 | -122.9462 | -122.9187 | 122.5754 | -0.022888 | 2.3209 | 1.1261
2142.1719 | 122.9416 | -57.2205 | 65.657 | -0.03006 | -0.0023691 | 0.062666 | 0.070113 | 0.0012284 | 0.0021917 | 0.0037128 | 0.02002 | 0.00088875 | 0.001709 | 0.00070062 | -0.0017197 | -0.0040845 | 0.0015209 | -54.8676 | 65.6113 | -57.2937 | 65.3824 | -56.6483 | -57.0831 | -56.4606 | -56.0577 | 65.6525 | -57.28 | -57.2159 | -57.1976 | -57.3257 | -57.0328 | -0.073242 | -0.045776 | -0.27466 | 0.5722 | 0.75989 | 0.13733 | 0.83313 | 0.21057 | -0.059509 | -0.004577 | -122.8729 | 0.022888 | 0.18768 | -0.10529 | 0.24719 | -0.045777 | 0.64545 | 122.6761 | 0.082397 | 0.064087 | 122.905 | 122.9324 | 122.8317 | 122.8729 | -122.9507 | -122.937 | 122.6028 | 0.004578 | 2.3529 | 1.1627
2143.1719 | 123.0103 | -57.1884 | 65.6113 | -0.045319 | -0.00023294 | 0.062025 | 0.068618 | 0.00037377 | 0.0011237 | 0.0045672 | 0.03833 | -0.00060665 | 0.0029906 | 0.00027342 | -0.0017197 | -0.0047253 | -0.0014697 | -54.8401 | 65.5838 | -57.2662 | 65.4602 | -56.5292 | -56.9916 | -56.3782 | -55.957 | 65.6342 | -57.2342 | -57.1426 | -57.1335 | -57.225 | -56.9595 | -0.077819 | -0.027466 | -0.15106 | 0.65918 | 0.81024 | 0.19684 | 0.88806 | 0.27466 | -0.045776 | 0.022888 | -122.7539 | 0.054932 | 0.22888 | -0.036621 | 0.27466 | 0.009155 | 0.737 | 122.7264 | 0.10071 | 0.091553 | 122.85 | 122.8683 | 122.7722 | 122.8226 | -122.8775 | -122.8455 | 122.6486 | 0.045777 | 2.3483 | 1.2314
2144.1719 | 123.0377 | -57.193 | 65.625 | -0.060578 | 0.00062166 | 0.063307 | 0.067763 | -0.001976 | 0.0036871 | 0.0056354 | 0.026123 | 0.0011023 | 2.8e-08 | -0.00229 | -0.0019333 | -0.0042981 | -0.0012561 | -54.8309 | 65.5609 | -57.2571 | 65.4465 | -56.5292 | -57.0053 | -56.3782 | -55.9204 | 65.6342 | -57.2296 | -57.1198 | -57.1198 | -57.225 | -56.9366 | -0.064087 | -0.064087 | -0.17853 | 0.66376 | 0.81482 | 0.18768 | 0.87891 | 0.25177 | -0.036621 | 0.009155 | -122.7448 | 0.073242 | 0.25635 | -0.032044 | 0.29297 | 0.004577 | 0.72784 | 122.7036 | 0.10986 | 0.10986 | 122.818 | 122.8638 | 122.7539 | 122.8271 | -122.8821 | -122.8546 | 122.6395 | 0.073242 | 2.3621 | 1.2726
2145.1719 | 122.9416 | -57.2159 | 65.6158 | -0.022431 | -0.00087374 | 0.063094 | 0.070968 | -0.0017624 | 0.0017645 | 0.0052082 | -0.03186 | 0.00088875 | 0.00021363 | 0.0045458 | -0.0030013 | -0.0045117 | 2.554e-05 | -54.9042 | 65.6067 | -57.3029 | 65.3641 | -56.6666 | -57.0923 | -56.488 | -56.0623 | 65.6891 | -57.2571 | -57.2021 | -57.2205 | -57.3257 | -57.0099 | -0.086975 | -0.009156 | -0.25177 | 0.54932 | 0.72784 | 0.1236 | 0.81482 | 0.21057 | -0.041199 | 0.073242 | -122.818 | -0.004578 | 0.20599 | -0.10986 | 0.24719 | -0.068665 | 0.63629 | 122.6669 | 0.036621 | 0.054932 | 122.9095 | 122.9462 | 122.8226 | 122.905 | -122.9187 | -122.8729 | 122.58 | 0.013733 | 2.3117 | 1.1536
2146.1719 | 122.9599 | -57.2113 | 65.6204 | 0.00045798 | -0.0025827 | 0.062025 | 0.071822 | -5.343e-05 | 0.0026191 | 0.0054218 | -0.0043946 | 3.4148e-05 | 0.0012818 | -0.0031446 | -0.0015061 | -0.0038709 | 0.00023934 | -55.0369 | 65.6387 | -57.2983 | 65.3687 | -56.6757 | -57.0969 | -56.4835 | -56.0623 | 65.6616 | -57.2479 | -57.2113 | -57.1976 | -57.3212 | -57.0145 | -0.086975 | 0.018311 | -0.25177 | 0.53558 | 0.72784 | 0.11444 | 0.81482 | 0.20142 | -0.036621 | 0.041199 | -122.8317 | 0.013733 | 0.19684 | -0.10986 | 0.23346 | -0.073242 | 0.62256 | 122.6669 | 0.050354 | 0.036621 | 122.937 | 122.9095 | 122.85 | 122.8729 | -122.9187 | -122.8683 | 122.58 | 0 | 2.1744 | 1.149
2147.1719 | 122.9462 | -57.2205 | 65.6204 | -0.052948 | 0.00019446 | 0.062025 | 0.068832 | 0.0016556 | -0.00037171 | 0.0032856 | -0.01355 | 0.0023839 | 0.0019226 | -0.0048536 | -0.00022431 | -0.0025891 | 0.0013073 | -54.9088 | 65.6342 | -57.2845 | 65.419 | -56.7581 | -57.28 | -56.4926 | -56.0898 | 65.657 | -57.2342 | -57.2205 | -57.2205 | -57.3395 | -57.019 | -0.064087 | 0.013733 | -0.20142 | 0.46234 | 0.72784 | -0.059509 | 0.79193 | 0.004578 | -0.013733 | 0.036621 | -122.8409 | 0 | 0.20142 | -0.11902 | 0.21515 | -0.10529 | 0.52643 | 122.7036 | 0.013733 | 0.013733 | 122.9187 | 122.8912 | 122.8546 | 122.8775 | -122.905 | -122.8546 | 122.6395 | 0 | 2.3117 | 1.1307
2148.1719 | 122.9507 | -57.2021 | 65.6433 | -0.091095 | -0.00044654 | 0.061812 | 0.068404 | -0.0021896 | 0.0021917 | 0.0045672 | 0.029175 | -0.00060665 | 0.0019226 | -0.0042126 | 0.00020289 | -0.0049389 | 0.00066654 | -54.8721 | 65.625 | -57.2617 | 65.419 | -56.5842 | -57.0465 | -56.4194 | -55.9891 | 65.6479 | -57.225 | -57.2067 | -57.2067 | -57.2937 | -56.9916 | -0.05951 | -0.018311 | -0.22431 | 0.61798 | 0.78278 | 0.15564 | 0.84228 | 0.21515 | -0.022889 | 0.004577 | -122.85 | -0.004578 | 0.21057 | -0.091553 | 0.23346 | -0.068664 | 0.67749 | 122.6807 | 0.018311 | 0.018311 | 122.8867 | 122.8729 | 122.8271 | 122.85 | -122.905 | -122.8683 | 122.6212 | -0.004578 | 2.33 | 1.2131
2149.1719 | 122.9736 | -57.2067 | 65.6296 | -0.075836 | -0.00023294 | 0.061598 | 0.069259 | -0.0017624 | 0.0011237 | 0.0077716 | 0.056641 | 0.00067495 | 0.00085443 | -0.0027174 | -0.0010787 | -0.0034437 | -0.0018971 | -54.8309 | 65.6067 | -57.2525 | 65.4419 | -56.5704 | -57.0099 | -56.4148 | -55.9708 | 65.6387 | -57.2433 | -57.1976 | -57.1793 | -57.2983 | -56.987 | -0.045776 | -0.022889 | -0.18768 | 0.63629 | 0.79193 | 0.19684 | 0.83771 | 0.24261 | -0.036621 | 0.009155 | -122.8271 | 0.027466 | 0.21973 | -0.091553 | 0.25635 | -0.054932 | 0.68207 | 122.6944 | 0.064087 | 0.045776 | 122.8592 | 122.8821 | 122.8134 | 122.8455 | -122.8821 | -122.8729 | 122.6486 | 0.009155 | 2.3758 | 1.236
2150.1719 | 123.0423 | -57.1838 | 65.6113 | -0.091095 | -1.9142e-05 | 0.060957 | 0.067123 | -0.0049668 | 0.0034735 | 0.005849 | 0.023071 | -0.00017945 | 0.001709 | -0.0014356 | -0.0027877 | -0.0066479 | 0.00023934 | -54.8355 | 65.5975 | -57.2388 | 65.3183 | -56.5201 | -56.9412 | -56.4148 | -55.9341 | 65.5975 | -57.2342 | -57.106 | -57.0923 | -57.193 | -56.9183 | -0.054932 | -0.013733 | -0.29297 | 0.66376 | 0.76904 | 0.24262 | 0.82398 | 0.29755 | -0.050354 | -0.013733 | -122.7173 | 0.091553 | 0.2655 | -0.009155 | 0.31586 | 0.041199 | 0.71869 | 122.5571 | 0.14191 | 0.12817 | 122.8363 | 122.8317 | 122.7814 | 122.7814 | -122.85 | -122.8455 | 122.5021 | 0.07782 | 2.3483 | 1.2497
2151.1719 | 122.9279 | -57.1976 | 65.6158 | -0.052948 | 0.00083526 | 0.061171 | 0.069472 | 0.0012284 | 0.0013373 | 0.003072 | -0.0013428 | 0.0021703 | 0.0019226 | 0.002196 | -0.0036423 | -0.0045117 | 0.0019483 | -54.9042 | 65.6296 | -57.28 | 65.3961 | -56.6437 | -57.1518 | -56.4972 | -56.0761 | 65.6708 | -57.2571 | -57.225 | -57.2342 | -57.3212 | -57.0099 | -0.082397 | 0.013733 | -0.21973 | 0.55389 | 0.70038 | 0.045777 | 0.78278 | 0.12817 | -0.059509 | 0.054931 | -122.8409 | -0.036621 | 0.18768 | -0.1236 | 0.24719 | -0.064087 | 0.63629 | 122.6761 | 0.022888 | 0.032043 | 122.9095 | 122.9279 | 122.8271 | 122.8683 | -122.8958 | -122.8729 | 122.5937 | -0.027466 | 2.2934 | 1.1215
2152.1719 | 122.9507 | -57.2205 | 65.6296 | -0.060578 | 0.0021171 | 0.060744 | 0.068618 | -0.001976 | 0.0019781 | 0.0034992 | 0.0047608 | -0.0016749 | -0.00021357 | -0.0025036 | -0.0023605 | -0.0051527 | 0.0032299 | -54.8538 | 65.6158 | -57.2662 | 65.4236 | -56.6071 | -57.0648 | -56.4285 | -56.0211 | 65.6479 | -57.225 | -57.1838 | -57.2021 | -57.312 | -57.0328 | -0.045776 | -0.013733 | -0.20599 | 0.6134 | 0.79193 | 0.15564 | 0.83771 | 0.20142 | -0.004578 | 0.01831 | -122.8134 | 0.018311 | 0.18768 | -0.091553 | 0.19226 | -0.086975 | 0.65918 | 122.6898 | 0.022889 | 0.041199 | 122.8821 | 122.8729 | 122.8363 | 122.8683 | -122.8958 | -122.8546 | 122.644 | 0.036621 | 2.3666 | 1.1993
2153.1719 | 122.9324 | -57.2021 | 65.6387 | -0.045319 | 0.0014761 | 0.062666 | 0.068618 | 0.00058737 | -0.00037171 | 0.0081988 | 0.029175 | -0.0010339 | 0.0019226 | 0.00048702 | -0.00065151 | -0.0030163 | -0.00082886 | -54.8492 | 65.6158 | -57.2571 | 65.4282 | -56.575 | -57.0557 | -56.4194 | -55.9937 | 65.6754 | -57.225 | -57.2113 | -57.1838 | -57.3074 | -57.0053 | -0.054932 | -0.022888 | -0.21057 | 0.62714 | 0.78278 | 0.14648 | 0.83771 | 0.20142 | -0.022889 | 0.036621 | -122.85 | 0.01831 | 0.19684 | -0.10529 | 0.21973 | -0.082397 | 0.68207 | 122.6852 | 0.041199 | 0.013733 | 122.8729 | 122.9004 | 122.818 | 122.8775 | -122.8958 | -122.8638 | 122.6303 | -0.009156 | 2.3529 | 1.2085
2154.1719 | 122.9553 | -57.2296 | 65.6296 | -0.060578 | 0.00019446 | 0.062025 | 0.069259 | -0.0011214 | 0.00026909 | 0.0022174 | 0.016968 | -0.00060665 | 0.00021363 | -0.0072034 | -0.0036423 | -0.0038709 | -0.0023243 | -54.8492 | 65.5792 | -57.2845 | 65.4327 | -56.5704 | -57.0282 | -56.4056 | -55.9845 | 65.625 | -57.2388 | -57.1793 | -57.1884 | -57.2845 | -57.0007 | -0.054932 | -0.050354 | -0.19684 | 0.65918 | 0.82397 | 0.20142 | 0.87891 | 0.25635 | -0.009156 | -0.004578 | -122.8088 | 0.041198 | 0.22888 | -0.054932 | 0.23804 | -0.045776 | 0.71411 | 122.7173 | 0.050354 | 0.05951 | 122.8638 | 122.8638 | 122.8088 | 122.8546 | -122.9141 | -122.8683 | 122.6624 | 0.050354 | 2.3804 | 1.2451
2155.1719 | 122.9599 | -57.2205 | 65.6021 | -0.091095 | 0.00062166 | 0.062239 | 0.068832 | 0.0010148 | 0.0015509 | 0.0049946 | 0.013916 | 0.0011023 | 0.0032044 | -0.0018628 | -0.0012925 | -0.0051527 | -0.0010425 | -54.8309 | 65.593 | -57.2479 | 65.4602 | -56.5521 | -57.0145 | -56.3873 | -55.9616 | 65.6342 | -57.2479 | -57.1655 | -57.1747 | -57.2662 | -56.9641 | -0.027466 | -0.009155 | -0.14191 | 0.66833 | 0.83313 | 0.20599 | 0.8606 | 0.23346 | -0.027466 | 0.032043 | -122.7676 | 0.045776 | 0.25635 | -0.045776 | 0.28381 | -0.01831 | 0.6958 | 122.7081 | 0.073242 | 0.082398 | 122.8409 | 122.8821 | 122.8134 | 122.8546 | -122.85 | -122.85 | 122.6807 | 0.054932 | 2.3895 | 1.2588
2156.1719 | 122.9416 | -57.2067 | 65.6479 | -0.068207 | 0.00019446 | 0.063094 | 0.068618 | 0.00080117 | 0.0017645 | 0.0049946 | 0.001709 | 0.0017431 | 0.0023498 | 0.0094592 | -0.0027877 | -0.0038709 | 0.0023755 | -54.8721 | 65.5975 | -57.2662 | 65.3961 | -56.6483 | -57.0877 | -56.4697 | -56.0577 | 65.657 | -57.2388 | -57.1884 | -57.2205 | -57.3074 | -57.0236 | -0.059509 | -0.050354 | -0.25177 | 0.55847 | 0.737 | 0.11902 | 0.79651 | 0.17853 | -0.032044 | 0.009155 | -122.8363 | -0.013733 | 0.18311 | -0.10071 | 0.21515 | -0.068664 | 0.61798 | 122.6624 | 0.018311 | 0.050354 | 122.8638 | 122.8958 | 122.8043 | 122.8638 | -122.9141 | -122.8867 | 122.6028 | 0.01831 | 2.3346 | 1.149
2157.1719 | 123.0331 | -57.1609 | 65.593 | -0.10635 | 0.0012625 | 0.060957 | 0.067763 | -0.001976 | 0.00069649 | 0.0045672 | 0.032227 | -0.0012477 | 0.0040588 | -0.0065626 | -0.0019333 | -0.0025891 | 0.0010937 | -54.8218 | 65.6067 | -57.2662 | 65.4877 | -56.4926 | -56.987 | -56.3461 | -55.6595 | 65.6799 | -57.1838 | -57.1426 | -57.0877 | -57.2159 | -56.9229 | -0.10529 | 0.013732 | -0.10529 | 0.66833 | 0.81482 | 0.17395 | 0.9201 | 0.27923 | -0.022888 | 0.086975 | -122.7356 | 0.073242 | 0.23804 | -0.054931 | 0.26093 | -0.032043 | 0.77362 | 122.7539 | 0.09613 | 0.041199 | 122.8729 | 122.8638 | 122.7676 | 122.8409 | -122.8592 | -122.7768 | 122.6486 | 0.018311 | 2.3392 | 1.5015
2158.1719 | 123.0148 | -57.1655 | 65.6113 | -0.083466 | 0.00040806 | 0.062239 | 0.069045 | 0.003151 | 5.5488e-05 | 0.0043536 | 0.035278 | 3.4148e-05 | 0.001068 | -0.0035718 | -0.0034287 | -0.0047253 | 0.0030163 | -54.8355 | 65.5884 | -57.2571 | 65.4739 | -56.5292 | -57.0053 | -56.3873 | -55.9296 | 65.625 | -57.225 | -57.1335 | -57.1472 | -57.2205 | -56.9321 | -0.091553 | -0.022888 | -0.13733 | 0.63629 | 0.7782 | 0.16022 | 0.86975 | 0.25177 | -0.05951 | 0.013733 | -122.7448 | 0.01831 | 0.23346 | -0.054932 | 0.29297 | 0.004578 | 0.72784 | 122.731 | 0.07782 | 0.091553 | 122.8455 | 122.85 | 122.7539 | 122.7905 | -122.8683 | -122.8363 | 122.6395 | 0.032043 | 2.33 | 1.236
2159.1719 | 122.9507 | -57.193 | 65.6296 | -0.068207 | 0.00083526 | 0.06288 | 0.068618 | -0.00090783 | 5.5488e-05 | 0.007558 | -0.0043946 | 0.00067495 | 0.001709 | 0.0019824 | -0.0017197 | -0.0040845 | 2.554e-05 | -54.8264 | 65.5975 | -57.2479 | 65.419 | -56.5613 | -57.0419 | -56.4194 | -56.0028 | 65.6616 | -57.2433 | -57.1747 | -57.1701 | -57.2983 | -57.0236 | -0.054932 | -0.032044 | -0.21057 | 0.63171 | 0.77362 | 0.15106 | 0.82855 | 0.20599 | -0.050354 | 0.032043 | -122.8043 | 0.022888 | 0.16937 | -0.10529 | 0.21973 | -0.054932 | 0.68665 | 122.6669 | 0.073242 | 0.068664 | 122.8455 | 122.905 | 122.7905 | 122.8546 | -122.8775 | -122.8729 | 122.612 | 0.01831 | 2.3666 | 1.1902
2160.1719 | 122.9691 | -57.1838 | 65.625 | -0.068207 | 0.0021171 | 0.06288 | 0.067336 | -0.0013352 | 0.0019781 | 0.0060626 | 0.02002 | -0.00060665 | 0.003418 | 0.0030506 | -0.0027877 | -0.0049389 | -0.0023243 | -54.8447 | 65.5884 | -57.2433 | 65.4465 | -56.5659 | -57.0282 | -56.4148 | -55.9708 | 65.6525 | -57.2342 | -57.1747 | -57.1747 | -57.2662 | -56.9778 | -0.059509 | -0.036621 | -0.17853 | 0.61798 | 0.76904 | 0.15564 | 0.82855 | 0.21515 | -0.050354 | 0.027466 | -122.7997 | 0.009155 | 0.20599 | -0.082397 | 0.25635 | -0.032043 | 0.67749 | 122.6898 | 0.059509 | 0.059509 | 122.8317 | 122.8867 | 122.7722 | 122.8363 | -122.8683 | -122.8592 | 122.6303 | 0.009155 | 2.3392 | 1.2131
2161.1719 | 122.9507 | -57.2571 | 65.6204 | -0.060578 | 0.0014761 | 0.060744 | 0.07289 | 0.0035782 | 0.0036871 | 0.003072 | -0.050171 | 0.00024775 | 0.00085443 | 0.0030506 | -0.0012925 | -0.0036573 | 0.0021619 | -54.9088 | 65.6067 | -57.3074 | 65.3503 | -56.694 | -57.1609 | -56.543 | -56.1035 | 65.6433 | -57.2662 | -57.2433 | -57.3029 | -57.4036 | -57.0511 | -0.050354 | -0.013733 | -0.27008 | 0.56305 | 0.71411 | 0.09613 | 0.76447 | 0.14648 | -0.009155 | 0.022889 | -122.8638 | -0.045776 | 0.20599 | -0.14648 | 0.21515 | -0.13733 | 0.6134 | 122.6578 | -0.036621 | 0.022888 | 122.9141 | 122.9095 | 122.8638 | 122.9004 | -122.9279 | -122.8867 | 122.6074 | 0.013733 | 2.3483 | 1.1536
2162.1719 | 122.9919 | -57.1747 | 65.6067 | -0.11398 | -0.00044654 | 0.06288 | 0.069686 | -0.0013352 | 0.00069649 | 0.0064898 | 0.056641 | 3.4148e-05 | 0.00064083 | -0.00229 | -0.0015061 | -0.0032301 | 0.0019483 | -54.8355 | 65.5792 | -57.2342 | 65.4648 | -56.5475 | -57.0145 | -56.3873 | -55.9616 | 65.6158 | -57.2067 | -57.1472 | -57.1472 | -57.2479 | -56.9504 | -0.059509 | -0.027465 | -0.14191 | 0.62714 | 0.78735 | 0.16022 | 0.84686 | 0.21973 | -0.032043 | 0.009156 | -122.7539 | 0.027466 | 0.22431 | -0.073242 | 0.25635 | -0.041199 | 0.68665 | 122.699 | 0.059509 | 0.059509 | 122.8134 | 122.8226 | 122.7539 | 122.7905 | -122.8409 | -122.8134 | 122.6395 | 0.027466 | 2.3392 | 1.2131
2163.1719 | 123.024 | -57.2021 | 65.6067 | -0.098725 | 0.0019035 | 0.06288 | 0.069045 | -0.0026168 | 0.0017645 | 0.0056354 | 0.013916 | 0.00067495 | 2.8e-08 | -0.0027174 | -0.00086511 | -0.0038709 | -0.00061526 | -54.8355 | 65.6021 | -57.2571 | 65.4785 | -56.5475 | -57.0053 | -56.3919 | -55.9525 | 65.6113 | -57.2388 | -57.1335 | -57.1243 | -57.2342 | -56.955 | -0.054932 | -0.004577 | -0.12817 | 0.6546 | 0.81024 | 0.19684 | 0.86517 | 0.25177 | -0.036622 | 0.004578 | -122.7402 | 0.077819 | 0.24719 | -0.032044 | 0.28381 | 0.004578 | 0.70953 | 122.7356 | 0.11444 | 0.10529 | 122.8592 | 122.85 | 122.8043 | 122.8134 | -122.8638 | -122.8455 | 122.6807 | 0.068664 | 2.3666 | 1.2497
2164.1719 | 123.0286 | -57.2159 | 65.5838 | -0.11398 | 0.0012625 | 0.061812 | 0.070327 | -0.0013352 | 0.0028327 | 0.0069172 | 0.013916 | 0.0013159 | -0.00021357 | -0.0014356 | -0.00022431 | -0.0010937 | -0.0021107 | -54.8172 | 65.5792 | -57.2388 | 65.4785 | -56.5063 | -56.9824 | -56.3644 | -55.8975 | 65.5975 | -57.2067 | -57.1564 | -57.0145 | -57.2571 | -56.9687 | -0.022889 | -0.004577 | -0.10528 | 0.70953 | 0.85144 | 0.23346 | 0.87433 | 0.25635 | 0.009155 | 0.013733 | -122.7402 | 0.20142 | 0.24719 | -0.041199 | 0.23804 | -0.050354 | 0.73242 | 122.7173 | 0.19226 | 0.050354 | 122.818 | 122.8043 | 122.7951 | 122.8134 | -122.8226 | -122.7905 | 122.6944 | 0.059509 | 2.3987 | 1.3184
2165.1719 | 122.9553 | -57.2067 | 65.6525 | -0.075836 | -0.00044654 | 0.061812 | 0.067977 | 0.0040054 | 0.00026909 | 0.0043536 | 0.023071 | 0.00046135 | 0.00064083 | 0.0013416 | -0.0015061 | -0.0040845 | -0.0014697 | -54.8401 | 65.5884 | -57.2525 | 65.4144 | -56.6254 | -57.0694 | -56.456 | -56.0074 | 65.6662 | -57.2342 | -57.193 | -57.2021 | -57.3074 | -57.0145 | -0.045776 | -0.064087 | -0.23804 | 0.58136 | 0.75073 | 0.13733 | 0.79651 | 0.1831 | -0.027466 | 0.013733 | -122.8455 | 0.004578 | 0.19226 | -0.10071 | 0.21973 | -0.073242 | 0.62714 | 122.6669 | 0.032044 | 0.041199 | 122.8409 | 122.9004 | 122.7951 | 122.8729 | -122.905 | -122.8867 | 122.6212 | 0.013733 | 2.3666 | 1.1993
2166.1719 | 122.9416 | -57.2388 | 65.5655 | -0.083466 | 0.00040806 | 0.061812 | 0.071609 | 0.0020828 | 0.0030463 | 0.0032856 | -0.06543 | 0.0011023 | 0.00085443 | -0.002931 | -0.0017197 | -0.0028027 | 0.0034435 | -54.9271 | 65.5838 | -57.2754 | 65.3275 | -56.7627 | -57.193 | -56.5659 | -56.1401 | 65.6433 | -57.2617 | -57.2205 | -57.2891 | -57.399 | -57.0511 | -0.036621 | 0.01831 | -0.23804 | 0.47608 | 0.67291 | 0.045777 | 0.70953 | 0.082398 | -0.022888 | 0.07782 | -122.7859 | -0.050354 | 0.18768 | -0.16022 | 0.21057 | -0.13733 | 0.5127 | 122.6028 | -0.027466 | 0.041199 | 122.8592 | 122.905 | 122.8226 | 122.8821 | -122.8409 | -122.8271 | 122.5662 | 0.018311 | 2.3117 | 1.0986
2167.1719 | 122.9553 | -57.2113 | 65.625 | -0.022431 | -0.0010873 | 0.060103 | 0.071822 | -0.00026703 | 0.0026191 | 0.0069172 | -0.074585 | 0.00088875 | -0.00021357 | 0.002196 | -0.0019333 | -0.0025891 | 0.0010937 | -54.8904 | 65.6433 | -57.2662 | 65.3687 | -56.662 | -56.9733 | -56.2912 | -56.1264 | 65.6479 | -57.2525 | -57.193 | -57.1976 | -57.312 | -57.0099 | -0.054931 | 0.018311 | -0.25635 | 0.54932 | 0.9201 | 0.23804 | 0.97504 | 0.29297 | -0.041198 | 0.022888 | -122.818 | 0.013733 | 0.20142 | -0.10071 | 0.24261 | -0.05951 | 0.60425 | 122.6349 | 0.054931 | 0.059509 | 122.9095 | 122.9004 | 122.8546 | 122.8592 | -122.8912 | -122.8775 | 122.58 | 0.018311 | 2.3209 | 1.0849
2168.1719 | 122.9645 | -57.2113 | 65.6479 | -0.068207 | -0.0015145 | 0.062239 | 0.068618 | -0.00048063 | 0.0015509 | 0.0067036 | 0.032227 | 0.00088875 | 0.0014954 | -0.0065626 | -0.00022431 | -0.0042981 | -0.00018806 | -54.8584 | 65.6067 | -57.2617 | 65.4099 | -56.6208 | -57.0786 | -56.4743 | -56.0303 | 65.6662 | -57.2617 | -57.193 | -57.2021 | -57.3074 | -57.0099 | -0.050354 | -0.041199 | -0.23804 | 0.59051 | 0.737 | 0.13275 | 0.78735 | 0.18311 | -0.050354 | 0.018311 | -122.8409 | 0.009156 | 0.20142 | -0.09613 | 0.25177 | -0.045776 | 0.64087 | 122.6715 | 0.05951 | 0.068665 | 122.8683 | 122.9279 | 122.818 | 122.8775 | -122.9095 | -122.9095 | 122.6212 | 0.018311 | 2.3529 | 1.181
2169.1719 | 122.9507 | -57.2113 | 65.6525 | -0.091095 | -0.0017281 | 0.061812 | 0.068191 | 0.0010148 | 0.0049689 | 0.0034992 | 0.029175 | 0.0021703 | 0.0012818 | -0.00079478 | -0.0012925 | -0.0019483 | 0.0019483 | -54.8492 | 65.625 | -57.2571 | 65.3915 | -56.6437 | -57.0923 | -56.4377 | -56.0349 | 65.6387 | -57.2571 | -57.1747 | -57.1976 | -57.3029 | -57.0099 | -0.045776 | -0.027466 | -0.26093 | 0.56763 | 0.77362 | 0.11902 | 0.8194 | 0.1648 | -0.045776 | -0.013733 | -122.8271 | 0.013733 | 0.20142 | -0.091552 | 0.24719 | -0.045776 | 0.6134 | 122.6486 | 0.059509 | 0.082397 | 122.8821 | 122.8958 | 122.8363 | 122.85 | -122.9095 | -122.9095 | 122.6028 | 0.036621 | 2.3621 | 1.1765
2170.1719 | 122.9736 | -57.1976 | 65.6067 | 0.030975 | -0.00023294 | 0.061171 | 0.069472 | -0.0026168 | 0.0011237 | 0.0077716 | -0.0043946 | 0.0023839 | 0.001709 | -0.0027174 | -0.0025741 | -0.0047253 | -0.0027515 | -54.8859 | 65.625 | -57.2891 | 65.3595 | -56.7902 | -57.2433 | -56.4743 | -56.0623 | 65.6662 | -57.2388 | -57.2067 | -57.2021 | -57.3257 | -57.019 | -0.091553 | 0.018311 | -0.24719 | 0.40741 | 0.72327 | -0.045776 | 0.81482 | 0.045777 | -0.041199 | 0.05951 | -122.8134 | -0.004577 | 0.17853 | -0.12817 | 0.21973 | -0.086975 | 0.49896 | 122.6486 | 0.036622 | 0.032044 | 122.9141 | 122.905 | 122.8226 | 122.8638 | -122.8958 | -122.8455 | 122.5571 | -0.009155 | 2.3117 | 1.1353
2171.1719 | 122.9004 | -57.2342 | 65.593 | -0.045319 | 0.0014761 | 0.063094 | 0.072677 | 0.0061416 | 0.00069649 | 0.0047808 | -0.068481 | 0.0011023 | 0.00021363 | -0.00015378 | -0.0021469 | -0.0036573 | 0.0028027 | -54.8996 | 65.6158 | -57.3074 | 65.3503 | -56.662 | -57.1335 | -56.5292 | -56.0852 | 65.625 | -57.2708 | -57.2021 | -57.2571 | -57.3944 | -57.0374 | -0.073242 | 0.022888 | -0.24262 | 0.5722 | 0.70496 | 0.10071 | 0.7782 | 0.17395 | -0.036621 | 0.032043 | -122.7951 | -0.022888 | 0.19684 | -0.16022 | 0.23346 | -0.1236 | 0.64545 | 122.6578 | 0.013733 | 0.068665 | 122.9233 | 122.8958 | 122.85 | 122.8592 | -122.9004 | -122.8638 | 122.5845 | 0.032044 | 2.3346 | 1.149
2172.1719 | 122.9507 | -57.2113 | 65.6479 | -0.11398 | 0.00019446 | 0.06288 | 0.068618 | -0.0051804 | 0.0039007 | 0.0056354 | 0.010864 | 0.0013159 | 0.002777 | -0.00229 | -0.00086511 | -0.0047253 | 0.0010937 | -54.8859 | 65.6067 | -57.2479 | 65.3778 | -56.6437 | -57.0877 | -56.4651 | -56.044 | 65.657 | -57.225 | -57.2205 | -57.1976 | -57.3074 | -57.0145 | -0.036621 | -0.041199 | -0.27008 | 0.56763 | 0.74616 | 0.1236 | 0.78278 | 0.16022 | -0.013733 | 0.009155 | -122.8683 | 0.013733 | 0.19684 | -0.09613 | 0.21057 | -0.082397 | 0.60425 | 122.6257 | 0.027466 | 0.004578 | 122.8546 | 122.8821 | 122.818 | 122.8683 | -122.8958 | -122.8729 | 122.5891 | -0.009155 | 2.3254 | 1.1673
2173.1719 | 122.9645 | -57.2021 | 65.625 | 0.046234 | -0.0025827 | 0.062025 | 0.068404 | -0.0032578 | 0.00026909 | 0.0032856 | 0.0047608 | 0.0015295 | 0.00021363 | -0.00464 | -0.00065151 | -0.0040845 | 0.00066654 | -54.9408 | 65.6616 | -57.28 | 65.3641 | -56.6666 | -57.1014 | -56.4835 | -56.0852 | 65.6525 | -57.2617 | -57.2021 | -57.2159 | -57.2983 | -57.0145 | -0.07782 | 0.036621 | -0.26093 | 0.53558 | 0.71869 | 0.10071 | 0.79651 | 0.17853 | -0.05951 | 0.027466 | -122.8271 | -0.013733 | 0.18768 | -0.096131 | 0.24719 | -0.036621 | 0.6134 | 122.644 | 0.045777 | 0.05951 | 122.9416 | 122.9141 | 122.8638 | 122.8546 | -122.905 | -122.8867 | 122.5662 | 0 | 2.2614 | 1.1169
2174.1719 | 122.9736 | -57.2342 | 65.625 | 0.008087 | -0.0010873 | 0.061598 | 0.069472 | -0.0013352 | 0.0030463 | 0.002431 | -0.019653 | 0.00088875 | 0.0012818 | -0.0016492 | -0.0012925 | -0.0021619 | -0.0031787 | -54.9042 | 65.6158 | -57.2708 | 65.387 | -56.6711 | -57.0877 | -56.4972 | -56.0577 | 65.657 | -57.225 | -57.2021 | -57.2113 | -57.3166 | -57.0053 | -0.036621 | -0.009155 | -0.23804 | 0.56305 | 0.737 | 0.14648 | 0.77362 | 0.1831 | 0.009155 | 0.032043 | -122.8271 | 0.022888 | 0.22888 | -0.082397 | 0.21973 | -0.091552 | 0.59967 | 122.6578 | 0.013733 | 0.022889 | 122.8867 | 122.8821 | 122.85 | 122.8912 | -122.8958 | -122.85 | 122.6212 | 0.032044 | 2.33 | 1.1765
2175.1719 | 122.9462 | -57.2342 | 65.6525 | -0.045319 | -0.00066014 | 0.062453 | 0.070754 | -0.0026168 | 0.0017645 | 0.007558 | -0.0043946 | 0.0025975 | 0.00021363 | 0.0028368 | -0.0010787 | -0.0045117 | -0.0021107 | -54.8767 | 65.6387 | -57.2845 | 65.3549 | -56.6803 | -57.1014 | -56.4789 | -56.0577 | 65.6479 | -57.2571 | -57.2021 | -57.2067 | -57.312 | -57.0007 | -0.050354 | -0.013733 | -0.29755 | 0.55389 | 0.75531 | 0.13275 | 0.80566 | 0.18311 | -0.022888 | -0.004578 | -122.8546 | 0.027466 | 0.23346 | -0.07782 | 0.25635 | -0.054932 | 0.60425 | 122.6395 | 0.050354 | 0.054932 | 122.9233 | 122.905 | 122.8729 | 122.8821 | -122.937 | -122.9095 | 122.5891 | 0.032044 | 2.3575 | 1.1765
2176.1719 | 122.9691 | -57.2067 | 65.6387 | -0.068207 | -0.0017281 | 0.059889 | 0.070541 | 0.00080117 | 0.0028327 | 0.0062762 | -0.0013428 | 0.0017431 | 0.001709 | -0.00058098 | -0.0012925 | -0.0015211 | -0.0021107 | -54.8813 | 65.6387 | -57.2662 | 65.3732 | -56.6711 | -57.0969 | -56.4926 | -56.0577 | 65.6433 | -57.2433 | -57.1838 | -57.2021 | -57.312 | -56.9916 | -0.059509 | 0 | -0.2655 | 0.53558 | 0.71411 | 0.10986 | 0.77362 | 0.16937 | -0.036621 | 0.004578 | -122.8226 | 0.004578 | 0.21515 | -0.10529 | 0.25177 | -0.068665 | 0.59509 | 122.6395 | 0.041199 | 0.059509 | 122.905 | 122.8867 | 122.8455 | 122.85 | -122.905 | -122.8821 | 122.58 | 0.022888 | 2.3254 | 1.149
2177.1719 | 122.9691 | -57.2021 | 65.6342 | -0.014801 | -1.9142e-05 | 0.061171 | 0.069259 | -0.001976 | 0.0024053 | 0.005849 | 0.013916 | 3.4148e-05 | 0.0029906 | -0.0016492 | -0.00086511 | -0.0025891 | -0.0018971 | -54.8904 | 65.6479 | -57.2662 | 65.3641 | -56.6528 | -57.0969 | -56.488 | -56.0898 | 65.6525 | -57.2113 | -57.2159 | -57.2067 | -57.3532 | -57.0419 | -0.064087 | 0.013733 | -0.27008 | 0.54932 | 0.71411 | 0.10529 | 0.7782 | 0.16937 | -0.009156 | 0.018311 | -122.85 | -0.004578 | 0.16022 | -0.15106 | 0.16937 | -0.14191 | 0.6134 | 122.6303 | 0.004578 | -0.004577 | 122.9141 | 122.8638 | 122.85 | 122.8546 | -122.9004 | -122.8455 | 122.5662 | -0.013733 | 2.3117 | 1.1124
2178.1719 | 122.9599 | -57.2205 | 65.6525 | -0.014801 | -0.00023294 | 0.060957 | 0.067763 | -0.00026703 | 0.0011237 | 0.0086262 | 0.10852 | 3.4148e-05 | 0.003418 | -0.0018628 | -1.0706e-05 | -0.0040845 | 2.554e-05 | -54.8859 | 65.625 | -57.2617 | 65.387 | -56.6574 | -57.0877 | -56.4789 | -56.1127 | 65.6891 | -57.2571 | -57.2205 | -57.2433 | -57.3257 | -57.0099 | -0.041199 | -0.027466 | -0.2655 | 0.56305 | 0.74158 | 0.13275 | 0.78278 | 0.17395 | -0.036621 | 0.036621 | -122.8729 | -0.022888 | 0.21057 | -0.10529 | 0.24719 | -0.068665 | 0.60425 | 122.6486 | 0.013733 | 0.036621 | 122.8867 | 122.9462 | 122.8455 | 122.9095 | -122.9141 | -122.9095 | 122.6074 | 0 | 2.3346 | 1.1078
2179.1719 | 122.9736 | -57.1976 | 65.6204 | -0.03006 | -0.0015145 | 0.060957 | 0.07289 | -0.0017624 | 0.00048269 | 0.0064898 | -0.010498 | 0.00088875 | -0.00021357 | 0.0032642 | -0.0012925 | -0.0036573 | 0.0015209 | -54.8355 | 65.6067 | -57.2754 | 65.4144 | -56.6254 | -57.0831 | -56.4835 | -56.0165 | 65.6525 | -57.2388 | -57.1701 | -57.1884 | -57.3074 | -56.9962 | -0.07782 | -0.013733 | -0.20599 | 0.57221 | 0.71411 | 0.11444 | 0.79193 | 0.19226 | -0.041199 | 0.032044 | -122.7905 | 0.009155 | 0.20142 | -0.10986 | 0.24262 | -0.068664 | 0.65002 | 122.6898 | 0.050354 | 0.068665 | 122.8821 | 122.8912 | 122.8043 | 122.85 | -122.8958 | -122.8592 | 122.612 | 0.027466 | 2.3621 | 1.181
2180.1719 | 122.9782 | -57.2296 | 65.6158 | -0.075836 | -0.00023294 | 0.063734 | 0.070113 | 0.0012284 | 0.0019781 | 0.0056354 | -0.022705 | -0.00039305 | 0.001709 | -0.001222 | -0.0017197 | -0.00066648 | -0.0010425 | -54.8492 | 65.5975 | -57.2754 | 65.4144 | -56.6345 | -57.074 | -56.4606 | -56.012 | 65.657 | -57.2296 | -57.1655 | -57.1976 | -57.312 | -56.9733 | -0.045777 | -0.018311 | -0.20142 | 0.59509 | 0.76904 | 0.15564 | 0.81482 | 0.20142 | 0 | 0.041198 | -122.7814 | 0.032043 | 0.25635 | -0.082398 | 0.25635 | -0.082398 | 0.64087 | 122.6898 | 0.032043 | 0.064087 | 122.8729 | 122.8867 | 122.8271 | 122.8867 | -122.8912 | -122.8455 | 122.644 | 0.064087 | 2.3804 | 1.2177
2181.1719 | 122.9416 | -57.2205 | 65.593 | -0.10635 | -0.0015145 | 0.064375 | 0.071181 | -0.00048063 | 0.0032599 | 0.0049946 | -0.022705 | 0.0013159 | 0.00085443 | -0.00229 | -0.0021469 | -0.0028027 | -0.0033923 | -54.8447 | 65.6021 | -57.28 | 65.4099 | -56.6345 | -57.1014 | -56.4835 | -56.0211 | 65.6204 | -57.2571 | -57.1793 | -57.225 | -57.3166 | -56.987 | -0.059509 | 0.009155 | -0.18311 | 0.58594 | 0.737 | 0.11902 | 0.79651 | 0.17853 | -0.036621 | 0.027465 | -122.7722 | -0.004578 | 0.23346 | -0.09613 | 0.27008 | -0.059509 | 0.64545 | 122.6898 | 0.032043 | 0.07782 | 122.8821 | 122.8775 | 122.8226 | 122.8409 | -122.8729 | -122.85 | 122.6303 | 0.041199 | 2.3758 | 1.1993
2182.1719 | 122.9874 | -57.2159 | 65.625 | -0.052948 | -0.00023294 | 0.063094 | 0.069472 | 0.0027238 | 0.0034735 | 0.0056354 | -0.016602 | 0.00046135 | 0.00085443 | -0.0033582 | -0.0017197 | -0.0030163 | -0.00018806 | -54.8401 | 65.5975 | -57.2845 | 65.4007 | -56.6437 | -57.0969 | -56.4743 | -55.9845 | 65.625 | -57.2433 | -57.1793 | -57.193 | -57.2845 | -56.9733 | -0.068665 | -0.027466 | -0.2243 | 0.5722 | 0.74158 | 0.11902 | 0.81024 | 0.18768 | -0.027466 | 0 | -122.8043 | 0.022888 | 0.24261 | -0.068665 | 0.27008 | -0.041199 | 0.64087 | 122.6852 | 0.050354 | 0.064087 | 122.8821 | 122.8683 | 122.8134 | 122.8409 | -122.9095 | -122.8683 | 122.6166 | 0.036621 | 2.3758 | 1.2314
2183.1719 | 122.8912 | -57.2021 | 65.593 | -0.13687 | -0.0015145 | 0.063948 | 0.070541 | 0.0018692 | 0.0026191 | 0.0047808 | -0.025757 | 0.00067495 | 0.0019226 | -0.00015378 | -0.00065151 | -0.0028027 | 0.0023755 | -54.8676 | 65.6158 | -57.2617 | 65.4144 | -56.6208 | -57.0831 | -56.4743 | -55.9982 | 65.6662 | -57.225 | -57.1655 | -57.1976 | -57.3029 | -56.8771 | -0.05951 | 0.022888 | -0.17853 | 0.58136 | 0.72784 | 0.11902 | 0.78735 | 0.17853 | -0.022889 | 0.073242 | -122.7585 | 0.004577 | 0.32501 | -0.10071 | 0.3479 | -0.077819 | 0.64087 | 122.6761 | 0.027466 | 0.05951 | 122.8775 | 122.8912 | 122.818 | 122.8683 | -122.8546 | -122.818 | 122.6166 | 0.036621 | 2.3346 | 1.2039
2184.1719 | 122.9736 | -57.2067 | 65.6296 | -0.091095 | 0.00062166 | 0.060957 | 0.069259 | -0.0013352 | 0.0013373 | 0.0020038 | 0.023071 | 0.00088875 | 2.8e-08 | 0.0019824 | -0.0017197 | -0.0032301 | 0.00045294 | -54.8584 | 65.6158 | -57.2708 | 65.3961 | -56.6483 | -57.0602 | -56.4743 | -56.0303 | 65.6479 | -57.2525 | -57.1564 | -57.1976 | -57.2937 | -56.987 | -0.064087 | -0.013733 | -0.23346 | 0.55847 | 0.73242 | 0.14648 | 0.79651 | 0.21057 | -0.045776 | 0.01831 | -122.7859 | 0.009155 | 0.21973 | -0.086975 | 0.2655 | -0.041199 | 0.62256 | 122.6669 | 0.054931 | 0.09613 | 122.8867 | 122.9004 | 122.8226 | 122.8546 | -122.9004 | -122.8821 | 122.6028 | 0.050354 | 2.3483 | 1.1765
2185.1719 | 122.9691 | -57.2159 | 65.6296 | 0.015716 | 0.00083526 | 0.060957 | 0.070113 | -0.00026703 | 0.0017645 | 0.0045672 | -0.0013428 | 0.00024775 | 0.0012818 | 0.0032642 | -0.0017197 | -0.0045117 | 0.0047253 | -54.8492 | 65.6342 | -57.2754 | 65.3824 | -56.6483 | -57.0694 | -56.4789 | -56.0257 | 65.6296 | -57.2388 | -57.1609 | -57.1976 | -57.2891 | -56.9733 | -0.05951 | 0.004577 | -0.24719 | 0.56763 | 0.737 | 0.14648 | 0.79651 | 0.20599 | -0.022889 | 0 | -122.7905 | 0.01831 | 0.24261 | -0.073243 | 0.2655 | -0.050354 | 0.62714 | 122.6578 | 0.041199 | 0.07782 | 122.9095 | 122.8683 | 122.85 | 122.8455 | -122.905 | -122.8683 | 122.5983 | 0.054931 | 2.3666 | 1.1902
2186.1719 | 122.9279 | -57.2296 | 65.5975 | -0.098725 | -0.0013009 | 0.061812 | 0.070754 | 0.0029374 | 0.0026191 | 0.0039264 | -0.028809 | 0.0011023 | 0.001709 | -0.0020764 | -0.0017197 | -0.0036573 | 0.0038709 | -54.9088 | 65.6158 | -57.3074 | 65.3229 | -56.7123 | -57.1655 | -56.5384 | -56.1356 | 65.6662 | -57.2708 | -57.2662 | -57.2891 | -57.3944 | -57.0602 | -0.07782 | 0.018311 | -0.27466 | 0.51727 | 0.69122 | 0.064087 | 0.76904 | 0.14191 | -0.041199 | 0.068665 | -122.8638 | -0.05951 | 0.16937 | -0.1648 | 0.21057 | -0.1236 | 0.59509 | 122.6303 | -0.018311 | 0.004578 | 122.9233 | 122.937 | 122.8455 | 122.8958 | -122.905 | -122.8683 | 122.5525 | -0.036621 | 2.3209 | 1.0941
2187.1719 | 122.9507 | -57.225 | 65.6021 | -0.083466 | 0.0021171 | 0.063094 | 0.0699 | 0.00251 | -0.00015811 | 0.0056354 | -0.016602 | 0.0019567 | 0.0014954 | -0.00058098 | -0.00086511 | -0.0045117 | -0.00040166 | -54.8492 | 65.6067 | -57.28 | 65.3915 | -56.662 | -57.1152 | -56.4972 | -56.0349 | 65.6525 | -57.2525 | -57.2021 | -57.2342 | -57.3441 | -57.019 | -0.054931 | 0.004577 | -0.21057 | 0.56305 | 0.72785 | 0.10986 | 0.78278 | 0.16479 | -0.027465 | 0.050354 | -122.8043 | -0.009155 | 0.20599 | -0.11902 | 0.23346 | -0.091553 | 0.61798 | 122.6715 | 0.01831 | 0.050354 | 122.8867 | 122.905 | 122.8317 | 122.8775 | -122.8821 | -122.8546 | 122.6166 | 0.022889 | 2.3758 | 1.1902
2188.1719 | 122.905 | -57.2067 | 65.6387 | -0.068207 | -0.0013009 | 0.06288 | 0.071395 | -0.00048063 | 0.0028327 | 0.0060626 | -0.028809 | 3.4148e-05 | 0.00085443 | 0.00048702 | -0.00086511 | -0.0038709 | -0.0016833 | -54.8996 | 65.593 | -57.2983 | 65.3366 | -56.7169 | -57.1655 | -56.543 | -56.1172 | 65.6387 | -57.2525 | -57.2525 | -57.28 | -57.399 | -57.0374 | -0.091553 | -0.045776 | -0.30212 | 0.48981 | 0.66376 | 0.041199 | 0.75531 | 0.13275 | -0.045776 | 0 | -122.8912 | -0.073242 | 0.16937 | -0.19226 | 0.21515 | -0.14648 | 0.58136 | 122.6349 | -0.027466 | 0 | 122.8912 | 122.8912 | 122.7997 | 122.8455 | -122.937 | -122.8912 | 122.5433 | -0.045776 | 2.3071 | 1.0895
2189.1719 | 122.9553 | -57.1976 | 65.6296 | -0.060578 | -0.00066014 | 0.063734 | 0.0699 | 0.0020828 | 0.0019781 | 0.0071308 | -0.010498 | 0.0032385 | 0.001709 | 0.00070062 | -0.0012925 | -0.0042981 | -0.0018971 | -54.8676 | 65.5975 | -57.2937 | 65.387 | -56.662 | -57.1014 | -56.4926 | -56.0394 | 65.6204 | -57.2479 | -57.1976 | -57.2433 | -57.3624 | -57.0099 | -0.09613 | -0.032044 | -0.24262 | 0.53558 | 0.70496 | 0.096131 | 0.80109 | 0.19226 | -0.050354 | -0.009156 | -122.8271 | -0.045776 | 0.18768 | -0.16479 | 0.23804 | -0.11444 | 0.63171 | 122.6807 | 0.004578 | 0.050354 | 122.8912 | 122.8683 | 122.7951 | 122.818 | -122.9233 | -122.8775 | 122.5845 | 0 | 2.33 | 1.1581
2190.1719 | 122.9507 | -57.2067 | 65.5975 | -0.060578 | -0.00066014 | 0.064803 | 0.069686 | 0.00058737 | 0.0013373 | 0.0049946 | -0.041016 | 0.0023839 | 0.00064083 | -0.0025036 | -0.0030013 | -0.0028027 | 0.00045294 | -54.8447 | 65.6067 | -57.2845 | 65.3778 | -56.6437 | -57.1014 | -56.488 | -56.0303 | 65.6387 | -57.2433 | -57.193 | -57.2342 | -57.3532 | -57.0099 | -0.07782 | 0.009155 | -0.21973 | 0.56305 | 0.71869 | 0.10529 | 0.79651 | 0.18311 | -0.036621 | 0.041199 | -122.7905 | -0.027466 | 0.19684 | -0.14648 | 0.23346 | -0.10986 | 0.64087 | 122.6624 | 0.009155 | 0.050354 | 122.8912 | 122.8821 | 122.8134 | 122.8455 | -122.8821 | -122.8409 | 122.5845 | 0.013733 | 2.3621 | 1.1765
2191.1719 | 122.9599 | -57.2021 | 65.6342 | -0.068207 | 0.0019035 | 0.062666 | 0.070327 | 0.00037377 | 0.00091009 | 0.0054218 | -0.016602 | 0.0017431 | -0.0010682 | 5.9824e-05 | -0.00086511 | -0.0038709 | 0.0013073 | -54.8584 | 65.5975 | -57.2708 | 65.3732 | -56.6437 | -57.1106 | -56.4972 | -56.0349 | 65.6296 | -57.2479 | -57.1838 | -57.2433 | -57.3257 | -57.0053 | -0.068665 | -0.036621 | -0.26093 | 0.55847 | 0.70496 | 0.091552 | 0.77362 | 0.16022 | -0.045777 | -0.004577 | -122.818 | -0.041199 | 0.19684 | -0.1236 | 0.24262 | -0.07782 | 0.62714 | 122.644 | 0.004578 | 0.064087 | 122.8683 | 122.8775 | 122.7997 | 122.8317 | -122.905 | -122.8821 | 122.5754 | 0.01831 | 2.3438 | 1.1673
2192.1719 | 122.9828 | -57.225 | 65.6067 | -0.075836 | -1.9142e-05 | 0.062453 | 0.066482 | 0.00058737 | 0.0015509 | 0.00414 | 0.0047608 | -0.00060665 | 0.0012818 | -0.00058098 | -0.0025741 | -0.0030163 | -0.00061526 | -54.8447 | 65.6067 | -57.2617 | 65.3824 | -56.6391 | -57.0648 | -56.4651 | -56.0028 | 65.6342 | -57.2159 | -57.1609 | -57.1976 | -57.2983 | -56.9733 | -0.036621 | 0 | -0.2243 | 0.58594 | 0.75989 | 0.16022 | 0.79651 | 0.19684 | 0.009156 | 0.027466 | -122.7676 | 0.027466 | 0.25177 | -0.073242 | 0.24261 | -0.082398 | 0.62256 | 122.644 | 0.01831 | 0.054931 | 122.8683 | 122.85 | 122.8317 | 122.8592 | -122.8683 | -122.8226 | 122.6074 | 0.064087 | 2.3804 | 1.2222
2193.1719 | 122.9233 | -57.2342 | 65.6204 | -0.083466 | 0.0016899 | 0.06288 | 0.071395 | 0.00058737 | 0.0039007 | 0.00414 | -0.0043946 | 0.0013159 | 0.0025634 | 0.0036914 | -0.00065151 | -0.0049389 | 0.0010937 | -54.8859 | 65.6021 | -57.2983 | 65.3458 | -56.7123 | -57.1472 | -56.543 | -56.0852 | 65.6204 | -57.2662 | -57.2433 | -57.2754 | -57.4036 | -57.0511 | -0.064087 | -0.01831 | -0.27466 | 0.52185 | 0.69122 | 0.086975 | 0.75531 | 0.15106 | -0.032043 | 0 | -122.8638 | -0.041199 | 0.18311 | -0.16937 | 0.21515 | -0.13733 | 0.58594 | 122.644 | -0.009156 | 0.022888 | 122.9004 | 122.8867 | 122.8363 | 122.8546 | -122.9187 | -122.8867 | 122.58 | -0.009155 | 2.3483 | 1.149
2194.1719 | 122.8821 | -57.2617 | 65.5563 | -0.075836 | -0.00087374 | 0.063307 | 0.071181 | -0.00048063 | 0.0019781 | 0.0054218 | -0.01355 | 0.0017431 | 0.0021362 | -0.0035718 | -0.0017197 | -0.0051527 | -0.0018971 | -54.9225 | 65.593 | -57.3029 | 65.2954 | -56.7764 | -57.2159 | -56.6071 | -56.1584 | 65.6296 | -57.2754 | -57.2296 | -57.2983 | -57.4631 | -57.1564 | -0.041198 | 0.036622 | -0.26093 | 0.48523 | 0.6546 | 0.045777 | 0.6958 | 0.086975 | -0.013733 | 0.073243 | -122.7859 | -0.036621 | 0.10529 | -0.20142 | 0.11902 | -0.18768 | 0.52643 | 122.5983 | -0.022888 | 0.045777 | 122.8958 | 122.905 | 122.8546 | 122.8912 | -122.8592 | -122.8317 | 122.5571 | 0.032044 | 2.3392 | 1.1032
2195.1719 | 122.937 | -57.2159 | 65.625 | -0.10635 | -0.0017281 | 0.063948 | 0.069472 | -0.00048063 | 0.0013373 | 0.0052082 | 0.001709 | 0.00088875 | 0.0021362 | 0.00091422 | -0.0027877 | -0.0038709 | 0.0021619 | -54.8767 | 65.6021 | -57.3074 | 65.3641 | -56.7032 | -57.1426 | -56.5292 | -56.0669 | 65.6479 | -57.2525 | -57.2021 | -57.2983 | -57.3715 | -57.0328 | -0.091553 | -0.022888 | -0.26093 | 0.5127 | 0.68665 | 0.073242 | 0.7782 | 0.16479 | -0.036621 | 0.022888 | -122.8271 | -0.082398 | 0.18311 | -0.15564 | 0.21973 | -0.11902 | 0.60425 | 122.6715 | -0.045777 | 0.050354 | 122.9095 | 122.9004 | 122.818 | 122.8638 | -122.9324 | -122.8775 | 122.58 | 0.013733 | 2.3392 | 1.149
2196.1719 | 122.937 | -57.2479 | 65.6433 | -0.060578 | 0.00083526 | 0.061812 | 0.070754 | -0.00026703 | 0.00069649 | 0.0073444 | 0.013916 | 0.0030249 | -0.0012818 | -0.00464 | -0.00065151 | -0.0055799 | 0.0017345 | -54.8813 | 65.5884 | -57.28 | 65.3595 | -56.6803 | -57.1198 | -56.5201 | -56.0806 | 65.6342 | -57.2662 | -57.2159 | -57.2479 | -57.3486 | -57.0465 | -0.032043 | -0.054932 | -0.28381 | 0.56763 | 0.72784 | 0.12817 | 0.75989 | 0.16022 | -0.01831 | -0.009156 | -122.8592 | 0 | 0.20142 | -0.10071 | 0.21973 | -0.082398 | 0.59967 | 122.6395 | 0.01831 | 0.050354 | 122.8683 | 122.9004 | 122.8363 | 122.8821 | -122.9233 | -122.9095 | 122.6074 | 0.032044 | 2.3666 | 1.1673
2197.1719 | 122.937 | -57.2159 | 65.6021 | 0.008087 | 0.0014761 | 0.062453 | 0.069045 | 0.0010148 | 0.0028327 | 0.0086262 | -0.010498 | 0.00067495 | 0.0025634 | -0.00079478 | -0.0012925 | -0.0028027 | 0.0023755 | -54.8584 | 65.5838 | -57.28 | 65.3641 | -56.6666 | -57.1472 | -56.5155 | -56.0623 | 65.6342 | -57.2433 | -57.2113 | -57.2525 | -57.3624 | -57.0145 | -0.064087 | -0.018311 | -0.23804 | 0.54932 | 0.70038 | 0.068664 | 0.76446 | 0.13275 | -0.027466 | 0.032043 | -122.8134 | -0.036621 | 0.20142 | -0.14648 | 0.22888 | -0.11902 | 0.6134 | 122.644 | -0.009155 | 0.032043 | 122.8638 | 122.8775 | 122.7997 | 122.85 | -122.8821 | -122.8455 | 122.58 | 0.004577 | 2.3575 | 1.1536
2198.1719 | 122.9691 | -57.2067 | 65.6021 | -0.068207 | -0.00087374 | 0.062453 | 0.069686 | 0.003151 | 0.0021917 | 0.0049946 | 0.013916 | 0.0013159 | 0.003418 | -0.00058098 | -0.0023605 | -0.0049389 | 0.00066654 | -54.8447 | 65.6067 | -57.2525 | 65.3824 | -56.6391 | -57.0831 | -56.488 | -56.1035 | 65.5975 | -57.2479 | -57.1564 | -57.2342 | -57.312 | -56.9824 | -0.045776 | 0.004577 | -0.21973 | 0.56763 | 0.71869 | 0.1236 | 0.76447 | 0.16937 | -0.041199 | -0.004578 | -122.7585 | -0.027466 | 0.2243 | -0.10529 | 0.2655 | -0.064087 | 0.6134 | 122.6349 | 0.013733 | 0.091553 | 122.8592 | 122.8455 | 122.8134 | 122.8043 | -122.8546 | -122.85 | 122.5891 | 0.050354 | 2.3621 | 1.1032
2199.1719 | 123.0011 | -57.2113 | 65.625 | -0.10635 | -0.0017281 | 0.060957 | 0.070113 | 0.00037377 | 0.0024053 | 0.0047808 | -0.010498 | 0.0019567 | 0.00085443 | 0.00070062 | -0.0017197 | -0.0064343 | 0.0025891 | -54.8492 | 65.6158 | -57.28 | 65.4053 | -56.6299 | -57.0786 | -56.4743 | -55.9982 | 65.6296 | -57.2342 | -57.2571 | -57.1289 | -57.2708 | -56.9595 | -0.068664 | -0.009155 | -0.21973 | 0.58136 | 0.737 | 0.13275 | 0.80566 | 0.20142 | -0.022888 | 0.004578 | -122.8821 | 0.082398 | 0.25177 | -0.059509 | 0.27466 | -0.036621 | 0.65002 | 122.6852 | 0.10529 | -0.022888 | 122.8958 | 122.8638 | 122.8271 | 122.8409 | -122.905 | -122.8592 | 122.6166 | -0.045776 | 2.3621 | 1.2131
2200.1719 | 122.9553 | -57.225 | 65.6342 | -0.052948 | -0.00066014 | 0.060316 | 0.070754 | -0.0026168 | 0.00048269 | 0.005849 | -0.028809 | -0.00039305 | 0.0032044 | -0.00015378 | -0.0017197 | -0.0051527 | 0.0015209 | -54.9362 | 65.5792 | -57.312 | 65.3 | -56.7764 | -57.1747 | -56.575 | -56.1447 | 65.6296 | -57.2891 | -57.0786 | -57.3303 | -57.4173 | -57.0236 | -0.086975 | -0.054931 | -0.33417 | 0.44861 | 0.65002 | 0.050354 | 0.737 | 0.13733 | -0.064087 | -0.004577 | -122.7127 | -0.10529 | 0.20142 | -0.19226 | 0.2655 | -0.12817 | 0.53558 | 122.612 | -0.041198 | 0.21057 | 122.8912 | 122.9187 | 122.8043 | 122.8546 | -122.9462 | -122.9233 | 122.525 | 0.14648 | 2.2888 | 1.0803
2201.1719 | 122.9187 | -57.2113 | 65.6204 | -0.083466 | -0.00023294 | 0.062239 | 0.0699 | -0.0030442 | 0.0039007 | 0.0064898 | -0.01355 | 0.00067495 | -0.0019226 | 0.0019824 | -0.0023605 | -0.0049389 | 0.0010937 | -54.8859 | 65.5975 | -57.2891 | 65.3549 | -56.7078 | -57.1518 | -56.5475 | -56.0989 | 65.6525 | -57.2662 | -57.2342 | -57.2617 | -57.3898 | -57.0374 | -0.07782 | -0.022888 | -0.2655 | 0.50354 | 0.66376 | 0.05951 | 0.74158 | 0.13733 | -0.054931 | 0.032044 | -122.8546 | -0.050354 | 0.17395 | -0.17853 | 0.22888 | -0.1236 | 0.58136 | 122.644 | 0.004577 | 0.032043 | 122.8867 | 122.9187 | 122.8088 | 122.8638 | -122.9095 | -122.8867 | 122.5662 | -0.022888 | 2.3254 | 1.1124
2202.1719 | 122.9599 | -57.2342 | 65.6204 | -0.037689 | -0.0015145 | 0.063094 | 0.070113 | 0.0010148 | 0.0013373 | 0.0064898 | -0.03186 | 0.00067495 | 0.003418 | -0.0010084 | -0.0019333 | -0.0025891 | -0.0012561 | -54.8676 | 65.6113 | -57.28 | 65.3503 | -56.7032 | -57.1426 | -56.5247 | -56.0715 | 65.6479 | -57.2342 | -57.2159 | -57.2662 | -57.3715 | -57.0236 | -0.045776 | -0.009155 | -0.27008 | 0.53101 | 0.70953 | 0.091553 | 0.75531 | 0.13733 | 0 | 0.027466 | -122.8363 | -0.032043 | 0.21057 | -0.13733 | 0.21057 | -0.13733 | 0.57678 | 122.6303 | -0.032043 | 0.018311 | 122.8912 | 122.8821 | 122.8455 | 122.8821 | -122.9004 | -122.8546 | 122.5845 | 0.018311 | 2.3666 | 1.1627
2203.1719 | 122.9279 | -57.2388 | 65.6204 | -0.091095 | 0.00019446 | 0.060316 | 0.070968 | 0.0020828 | 5.5488e-05 | 0.0073444 | -0.019653 | 0.00024775 | 0.003418 | 0.0051868 | -0.0040695 | -0.0036573 | 0.00023934 | -54.8584 | 65.5975 | -57.2754 | 65.3641 | -56.6757 | -57.1472 | -56.5155 | -56.0623 | 65.6387 | -57.2479 | -57.2113 | -57.2479 | -57.3853 | -57.019 | -0.036621 | -0.022888 | -0.25635 | 0.56305 | 0.72327 | 0.091553 | 0.75989 | 0.12817 | -0.009155 | 0.018311 | -122.8317 | -0.009155 | 0.21973 | -0.14648 | 0.22888 | -0.13733 | 0.59967 | 122.6395 | 0 | 0.036621 | 122.8729 | 122.8867 | 122.8363 | 122.8775 | -122.8958 | -122.8683 | 122.6028 | 0.027466 | 2.3804 | 1.1765
2204.1719 | 122.9599 | -57.2205 | 65.6021 | -0.068207 | -0.00066014 | 0.063948 | 0.070113 | -0.00048063 | 0.0011237 | 0.0049946 | -0.01355 | -0.00060665 | 0.002777 | 0.0071094 | -0.0015061 | -0.0036573 | 0.0010937 | -54.8492 | 65.6204 | -57.2983 | 65.3778 | -56.6711 | -57.1198 | -56.5247 | -56.0532 | 65.6204 | -57.2433 | -57.2067 | -57.2433 | -57.3532 | -57.0236 | -0.07782 | 0.01831 | -0.2243 | 0.54932 | 0.6958 | 0.10071 | 0.77362 | 0.17853 | -0.022888 | 0.01831 | -122.8088 | -0.022888 | 0.19684 | -0.13275 | 0.21973 | -0.10986 | 0.62714 | 122.6761 | 0 | 0.036621 | 122.9187 | 122.8638 | 122.8409 | 122.8409 | -122.9004 | -122.8455 | 122.5983 | 0.013733 | 2.3712 | 1.1673
2205.1719 | 122.9828 | -57.1976 | 65.625 | -0.037689 | 0.00019446 | 0.061598 | 0.0699 | -0.00026703 | 0.0021917 | 0.0060626 | -0.0074462 | -0.00017945 | 0.00042723 | 0.0024096 | -0.0017197 | -0.0040845 | -0.00040166 | -54.8264 | 65.6158 | -57.2708 | 65.3915 | -56.6254 | -57.0694 | -56.488 | -56.0165 | 65.6204 | -57.2617 | -57.1381 | -57.2021 | -57.28 | -56.9916 | -0.073242 | -0.009155 | -0.23346 | 0.57221 | 0.70953 | 0.12817 | 0.78278 | 0.20142 | -0.064087 | -0.004578 | -122.7631 | -0.004577 | 0.20599 | -0.082397 | 0.27008 | -0.01831 | 0.64545 | 122.6624 | 0.05951 | 0.1236 | 122.8867 | 122.8821 | 122.8134 | 122.818 | -122.8958 | -122.8867 | 122.5891 | 0.059509 | 2.3712 | 1.181
2206.1719 | 122.9507 | -57.1838 | 65.6296 | -0.052948 | 0.00062166 | 0.060957 | 0.069472 | 0.0010148 | 0.0019781 | 0.0069172 | -0.016602 | -0.0010339 | 0.0019226 | 0.0026232 | -0.00065151 | -0.0036573 | 0.0030163 | -54.8492 | 65.5792 | -57.2708 | 65.387 | -56.6574 | -57.106 | -56.5018 | -56.0303 | 65.6296 | -57.2479 | -57.193 | -57.225 | -57.3441 | -57.0236 | -0.086975 | -0.050354 | -0.24262 | 0.52643 | 0.68207 | 0.07782 | 0.76904 | 0.16479 | -0.064087 | 0 | -122.8226 | -0.041199 | 0.16022 | -0.16022 | 0.2243 | -0.09613 | 0.6134 | 122.6578 | 0.022888 | 0.054932 | 122.85 | 122.8775 | 122.7631 | 122.8134 | -122.9004 | -122.8775 | 122.5708 | -0.009155 | 2.3346 | 1.1536
2207.1719 | 122.9324 | -57.2113 | 65.6204 | -0.060578 | 0.00083526 | 0.065443 | 0.069686 | 0.0020828 | 0.0026191 | 0.0054218 | 0.010864 | 0.0030249 | 2.8e-08 | -0.00058098 | -0.0019333 | -0.0030163 | -0.0023243 | -54.8813 | 65.593 | -57.2983 | 65.3458 | -56.7123 | -57.1472 | -56.5475 | -56.0989 | 65.6158 | -57.2388 | -57.2067 | -57.2662 | -57.3853 | -57.0328 | -0.086975 | -0.027465 | -0.27466 | 0.49896 | 0.66376 | 0.064087 | 0.75073 | 0.15106 | -0.027466 | -0.004577 | -122.8271 | -0.054931 | 0.17853 | -0.17395 | 0.20599 | -0.14648 | 0.58594 | 122.644 | -0.027465 | 0.032044 | 122.8912 | 122.8546 | 122.8043 | 122.8271 | -122.9187 | -122.8592 | 122.5571 | 0.004578 | 2.33 | 1.1124
2208.1719 | 123.0698 | -57.2021 | 65.5701 | -0.068207 | 0.00040806 | 0.064162 | 0.068404 | -0.00090783 | 0.0013373 | 0.0073444 | 0.035278 | 0.0019567 | 0.00085443 | -0.0037854 | -0.0025741 | -0.0049389 | -0.00018806 | -54.895 | 65.5701 | -57.3029 | 65.3595 | -56.6895 | -57.1335 | -56.5155 | -56.0303 | 65.5975 | -57.2754 | -57.1381 | -57.2021 | -57.2891 | -56.9504 | -0.10071 | 0 | -0.21057 | 0.5127 | 0.68664 | 0.068664 | 0.78735 | 0.16937 | -0.073243 | 0.027466 | -122.7081 | 0 | 0.25177 | -0.086976 | 0.32501 | -0.013733 | 0.6134 | 122.6624 | 0.073243 | 0.13733 | 122.8729 | 122.8729 | 122.7722 | 122.7997 | -122.8729 | -122.8455 | 122.5616 | 0.064086 | 2.3071 | 1.1719
2209.1719 | 122.9599 | -57.2296 | 65.5975 | -0.014801 | 0.00019446 | 0.064589 | 0.070541 | 0.0012284 | 0.00091009 | 0.00414 | -0.022705 | 0.0011023 | -0.00021357 | 0.0017688 | -0.0034287 | -0.0030163 | 0.0030163 | -54.863 | 65.6204 | -57.2937 | 65.3503 | -56.694 | -57.1381 | -56.5247 | -56.0715 | 65.6113 | -57.28 | -57.225 | -57.2571 | -57.3624 | -57.0145 | -0.064087 | 0.022888 | -0.24719 | 0.53558 | 0.70496 | 0.091552 | 0.76904 | 0.15564 | -0.050354 | 0.013733 | -122.8226 | -0.027466 | 0.21515 | -0.13275 | 0.2655 | -0.082398 | 0.59967 | 122.644 | 0.022888 | 0.054931 | 122.9141 | 122.8912 | 122.85 | 122.8409 | -122.8912 | -122.8775 | 122.58 | 0.004577 | 2.3666 | 1.1581
2210.1719 | 122.9507 | -57.2205 | 65.6113 | -0.075836 | 0.00083526 | 0.062025 | 0.069472 | -0.0011214 | 0.0019781 | 0.0045672 | -0.0074462 | 0.00024775 | 0.001709 | 0.0015552 | -0.00043791 | -0.0049389 | 0.00088014 | -54.8447 | 65.6067 | -57.28 | 65.3687 | -56.6757 | -57.1289 | -56.5338 | -56.0486 | 65.6296 | -57.2388 | -57.2113 | -57.2388 | -57.3578 | -57.0236 | -0.059509 | -0.004578 | -0.24262 | 0.54474 | 0.68665 | 0.091553 | 0.74615 | 0.15106 | -0.018311 | 0.018311 | -122.8226 | -0.018311 | 0.19684 | -0.13733 | 0.21515 | -0.11902 | 0.60425 | 122.6486 | 0 | 0.027466 | 122.8867 | 122.8683 | 122.8271 | 122.85 | -122.8912 | -122.85 | 122.5891 | 0.009155 | 2.3758 | 1.1719
2211.1719 | 122.905 | -57.2479 | 65.6296 | -0.10635 | -0.00023294 | 0.06053 | 0.069259 | 0.0018692 | 0.0019781 | 0.0028582 | -0.0074462 | 0.0011023 | 0.0012818 | 0.00091422 | -0.0010787 | -0.0040845 | 0.0047253 | -54.8859 | 65.5838 | -57.2891 | 65.3366 | -56.7398 | -57.1838 | -56.5842 | -56.1356 | 65.6525 | -57.2617 | -57.2388 | -57.3074 | -57.3944 | -57.0557 | -0.041199 | -0.045777 | -0.29297 | 0.50812 | 0.66376 | 0.064087 | 0.70496 | 0.10529 | -0.013733 | 0.022888 | -122.8683 | -0.059509 | 0.19226 | -0.14648 | 0.20599 | -0.13275 | 0.54932 | 122.6257 | -0.045776 | 0.022888 | 122.8729 | 122.9141 | 122.8317 | 122.9004 | -122.9187 | -122.8912 | 122.5845 | 0.009155 | 2.3621 | 1.1124
2212.1719 | 122.9599 | -57.2205 | 65.6067 | -0.083466 | -1.9142e-05 | 0.062453 | 0.069045 | 0.00486 | 0.0011237 | 0.0086262 | -0.025757 | 0.00024775 | 0.001709 | -0.0027174 | -0.0010787 | -0.0040845 | 0.00045294 | -54.863 | 65.6021 | -57.2845 | 65.3915 | -56.6757 | -57.1014 | -56.5155 | -56.0577 | 65.625 | -57.2433 | -57.1976 | -57.2342 | -57.3441 | -57.0053 | -0.064087 | -0.004577 | -0.21515 | 0.54474 | 0.70496 | 0.11902 | 0.76904 | 0.18311 | -0.022888 | 0.018311 | -122.8043 | -0.013733 | 0.21515 | -0.1236 | 0.23804 | -0.10071 | 0.60883 | 122.6761 | 0.009155 | 0.045776 | 122.8867 | 122.8683 | 122.8226 | 122.8455 | -122.8912 | -122.85 | 122.612 | 0.022888 | 2.3575 | 1.1627
2213.1719 | 122.9416 | -57.2113 | 65.6433 | -0.022431 | -0.0013009 | 0.062666 | 0.071395 | -0.0024032 | 0.00069649 | 0.0073444 | -0.0013428 | 0.00024775 | -0.00042717 | -0.00229 | -0.00043791 | -0.0047253 | 2.554e-05 | -54.8492 | 65.6296 | -57.28 | 65.3732 | -56.662 | -57.1106 | -56.4972 | -56.0257 | 65.6387 | -57.2433 | -57.193 | -57.225 | -57.3303 | -56.9962 | -0.068664 | -0.013733 | -0.27008 | 0.54932 | 0.71411 | 0.10071 | 0.78278 | 0.16937 | -0.032043 | -0.004578 | -122.8363 | -0.013733 | 0.21515 | -0.11902 | 0.24719 | -0.086975 | 0.61798 | 122.6532 | 0.01831 | 0.050354 | 122.9095 | 122.8821 | 122.8409 | 122.85 | -122.9233 | -122.8867 | 122.5845 | 0.018311 | 2.3621 | 1.1856
2214.1719 | 122.9416 | -57.225 | 65.6204 | -0.045319 | -0.0010873 | 0.062239 | 0.069045 | 0.0012284 | 0.0032599 | 0.003072 | 0.001709 | 0.0015295 | 0.0014954 | 0.0013416 | -0.00086511 | -0.0042981 | 2.554e-05 | -54.863 | 65.593 | -57.2891 | 65.3458 | -56.7169 | -57.1609 | -56.5521 | -56.0944 | 65.6387 | -57.2571 | -57.2296 | -57.2754 | -57.4036 | -57.0465 | -0.064087 | -0.027465 | -0.27466 | 0.50812 | 0.67291 | 0.064087 | 0.737 | 0.12817 | -0.032043 | 0.018311 | -122.85 | -0.050354 | 0.17853 | -0.17853 | 0.21057 | -0.14648 | 0.57221 | 122.6349 | -0.018311 | 0.027466 | 122.8821 | 122.8958 | 122.818 | 122.8638 | -122.9095 | -122.8775 | 122.5708 | -0.004577 | 2.3621 | 1.1307
2215.1719 | 122.9691 | -57.2205 | 65.593 | -0.12924 | -0.00066014 | 0.062666 | 0.069472 | 0.0035782 | 0.0026191 | 0.0045672 | -0.025757 | 0.0019567 | 0.001068 | 0.00091422 | -0.0021469 | -0.0047253 | 0.0013073 | -54.9225 | 65.6204 | -57.3029 | 65.2863 | -56.7673 | -57.2021 | -56.5796 | -56.1264 | 65.6342 | -57.28 | -57.3578 | -57.5089 | -57.1014 | -56.813 | -0.082397 | 0.027465 | -0.3067 | 0.45319 | 0.64087 | 0.018311 | 0.72327 | 0.10071 | -0.059509 | 0.041198 | -122.9507 | -0.28839 | 0.40741 | 0.11902 | 0.46692 | 0.17853 | 0.53558 | 122.5891 | -0.22888 | -0.07782 | 122.9233 | 122.9141 | 122.8409 | 122.8546 | -122.8958 | -122.8729 | 122.5067 | -0.13733 | 2.298 | 1.0941
2216.1719 | 122.8821 | -57.225 | 65.625 | -0.075836 | 0.0010489 | 0.061385 | 0.0699 | 0.00251 | 0.0011237 | 0.0054218 | -0.0074462 | 0.0013159 | -0.00042717 | -0.0025036 | -0.0023605 | -0.0036573 | -0.0010425 | -54.8721 | 65.6021 | -57.28 | 65.3687 | -56.7032 | -57.1381 | -56.5338 | -56.0715 | 65.6387 | -57.2571 | -57.2113 | -57.2617 | -57.3624 | -57.0374 | -0.054931 | -0.022888 | -0.25635 | 0.52185 | 0.69122 | 0.086975 | 0.74615 | 0.14191 | -0.032043 | 0.013733 | -122.8363 | -0.036621 | 0.18768 | -0.13733 | 0.21973 | -0.10529 | 0.57678 | 122.6486 | -0.004578 | 0.045776 | 122.8821 | 122.8958 | 122.8271 | 122.8638 | -122.905 | -122.8821 | 122.5937 | 0.013733 | 2.3529 | 1.1536
2217.1719 | 122.9507 | -57.2113 | 65.625 | -0.091095 | -0.00023294 | 0.061812 | 0.070541 | -0.0017624 | 0.0026191 | 0.0071308 | -0.0074462 | -0.00017945 | 0.0014954 | 0.0060412 | -0.0025741 | -0.0032301 | 0.00066654 | -54.8676 | 65.6067 | -57.28 | 65.3549 | -56.6803 | -57.1243 | -56.5338 | -56.0623 | 65.6616 | -57.225 | -57.2113 | -57.2479 | -57.3532 | -57.0145 | -0.068664 | -0.018311 | -0.27008 | 0.53101 | 0.67749 | 0.086975 | 0.74615 | 0.15564 | -0.013733 | 0.036621 | -122.8363 | -0.036621 | 0.19684 | -0.14191 | 0.21057 | -0.12817 | 0.59967 | 122.6349 | -0.022888 | 0.013733 | 122.8867 | 122.8867 | 122.818 | 122.8729 | -122.905 | -122.85 | 122.5662 | 0 | 2.3438 | 1.149
2218.1719 | 122.9233 | -57.2159 | 65.625 | -0.068207 | 0.00040806 | 0.062666 | 0.070541 | 0.00080117 | 0.00069649 | 0.0081988 | -0.041016 | 0.0015295 | 0.0021362 | -0.0010084 | -0.0021469 | -0.0036573 | -0.0016833 | -54.8813 | 65.6021 | -57.2845 | 65.3091 | -56.7673 | -57.1838 | -56.5796 | -56.1401 | 65.657 | -57.2845 | -57.2479 | -57.2937 | -57.4127 | -57.0557 | -0.068665 | -0.022888 | -0.31586 | 0.44861 | 0.63629 | 0.032043 | 0.70496 | 0.10071 | -0.068665 | 0.032043 | -122.8729 | -0.07782 | 0.16022 | -0.19684 | 0.22888 | -0.12817 | 0.51727 | 122.5937 | -0.009155 | 0.036621 | 122.8867 | 122.9416 | 122.818 | 122.8729 | -122.9095 | -122.9095 | 122.525 | -0.032044 | 2.3346 | 1.0757
2219.1719 | 122.9691 | -57.225 | 65.625 | -0.037689 | -0.00066014 | 0.060957 | 0.069259 | 0.003151 | 0.0034735 | 0.005849 | 0.047485 | 0.0017431 | 0.0032044 | 0.0041186 | -0.0040695 | -0.0038709 | -0.00018806 | -54.8218 | 65.6113 | -57.2571 | 65.4099 | -56.5796 | -57.312 | -56.5613 | -56.0074 | 65.6662 | -57.2205 | -57.1472 | -57.1976 | -57.3074 | -56.9687 | -0.032043 | -0.013733 | -0.21515 | 0.64545 | 0.66376 | -0.086975 | 0.6958 | -0.054932 | 0.004578 | 0.041199 | -122.7722 | 0.027466 | 0.25635 | -0.082397 | 0.25177 | -0.086975 | 0.67749 | 122.6669 | 0.022888 | 0.073242 | 122.8683 | 122.8867 | 122.8363 | 122.8912 | -122.8821 | -122.8455 | 122.6349 | 0.07782 | 2.4033 | 1.2177
2220.1719 | 122.9919 | -57.1976 | 65.6387 | -0.068207 | -1.9142e-05 | 0.061598 | 0.068191 | 0.0037918 | 0.00091009 | 0.005849 | -0.13257 | 0.0015295 | -0.001709 | -0.00229 | -0.0021469 | -0.0040845 | -0.00018806 | -54.8309 | 65.6342 | -57.2662 | 65.4007 | -56.6483 | -57.0969 | -56.4972 | -55.957 | 65.6433 | -57.2571 | -57.1655 | -57.1838 | -57.3074 | -56.9687 | -0.068664 | -0.004578 | -0.23804 | 0.54932 | 0.70038 | 0.10071 | 0.76904 | 0.16937 | -0.059509 | 0.004578 | -122.8043 | 0.013733 | 0.22888 | -0.10986 | 0.28839 | -0.050354 | 0.61798 | 122.6669 | 0.073242 | 0.091553 | 122.9004 | 122.9004 | 122.8317 | 122.8409 | -122.905 | -122.8958 | 122.5983 | 0.032044 | 2.3666 | 1.2405
2221.1719 | 122.9004 | -57.2433 | 65.6204 | -0.060578 | -0.0013009 | 0.063521 | 0.070327 | -0.0026168 | 0.00091009 | 0.0045672 | -0.022705 | 0.00046135 | -0.0014954 | -0.00464 | -0.0030013 | -0.0047253 | -0.0023243 | -54.895 | 65.6021 | -57.2754 | 65.332 | -56.7261 | -57.1838 | -56.5659 | -56.1172 | 65.6387 | -57.2388 | -57.2433 | -57.2983 | -57.4127 | -57.0465 | -0.032044 | -0.01831 | -0.28839 | 0.51727 | 0.67749 | 0.059509 | 0.70953 | 0.091553 | 0.004577 | 0.018311 | -122.8638 | -0.054932 | 0.19684 | -0.16937 | 0.19226 | -0.17395 | 0.54932 | 122.6074 | -0.059509 | -0.004577 | 122.8775 | 122.8775 | 122.8455 | 122.8821 | -122.8958 | -122.8592 | 122.5754 | 0 | 2.3483 | 1.1261
2222.1719 | 122.9279 | -57.2159 | 65.6113 | -0.083466 | 0.00083526 | 0.061812 | 0.068618 | 0.004219 | 0.00048269 | 0.0062762 | -0.0074462 | 0.0017431 | 0.0025634 | -0.0014356 | -0.00086511 | -0.0021619 | -0.00082886 | -54.8767 | 65.6067 | -57.2891 | 65.3275 | -56.7444 | -57.1564 | -56.5704 | -56.1264 | 65.6387 | -57.2617 | -57.2525 | -57.3074 | -57.3944 | -57.0648 | -0.073243 | -0.004578 | -0.28381 | 0.4715 | 0.64545 | 0.059509 | 0.71869 | 0.13275 | -0.045777 | 0.027466 | -122.8638 | -0.091553 | 0.15106 | -0.17853 | 0.19684 | -0.13275 | 0.54474 | 122.6166 | -0.045776 | 0.009156 | 122.8958 | 122.9004 | 122.8226 | 122.8546 | -122.9004 | -122.8729 | 122.5433 | -0.036621 | 2.3392 | 1.0895
2223.1719 | 122.9782 | -57.2205 | 65.5975 | -0.10635 | 0.0012625 | 0.063307 | 0.070968 | -5.343e-05 | 0.0011237 | 0.0056354 | -0.01355 | 0.0015295 | -0.001709 | 0.001128 | 0.00063009 | -0.0023755 | -0.0012561 | -54.9042 | 65.5838 | -57.3029 | 65.181 | -57.0328 | -57.0328 | -56.3004 | -56.0944 | 65.6479 | -57.2571 | -57.2296 | -57.2571 | -57.3807 | -57.019 | -0.082397 | -0.013733 | -0.41656 | 0.18768 | 0.9201 | 0.18768 | 1.0025 | 0.27008 | -0.036621 | 0.050354 | -122.8271 | -0.036621 | 0.20142 | -0.16022 | 0.23804 | -0.1236 | 0.27008 | 122.4838 | 0 | 0.027466 | 122.8867 | 122.905 | 122.8043 | 122.8683 | -122.9004 | -122.8546 | 122.4014 | -0.009155 | 2.3163 | 1.1261
2224.1719 | 122.9187 | -57.2205 | 65.6067 | -0.10635 | -0.0010873 | 0.062453 | 0.067977 | -0.00048063 | -0.0012261 | 0.0032856 | -0.010498 | 0.0017431 | 0.0025634 | 0.002196 | -0.0030013 | -0.0036573 | -0.00040166 | -54.8767 | 65.5975 | -57.2983 | 65.3275 | -56.7398 | -57.1793 | -56.5704 | -56.131 | 65.6158 | -57.2845 | -57.2296 | -57.2891 | -57.4036 | -57.0419 | -0.07782 | -0.009155 | -0.27923 | 0.48065 | 0.65002 | 0.041199 | 0.72784 | 0.11902 | -0.064087 | 0.009156 | -122.8363 | -0.068665 | 0.17853 | -0.18311 | 0.24262 | -0.11902 | 0.55847 | 122.6257 | -0.004578 | 0.054932 | 122.8958 | 122.9004 | 122.818 | 122.8363 | -122.905 | -122.8912 | 122.5479 | -0.009155 | 2.3438 | 1.0895
2225.1719 | 122.937 | -57.2388 | 65.6387 | -0.075836 | -0.00044654 | 0.062025 | 0.069045 | 0.0010148 | 0.0024053 | 0.0067036 | -0.0074462 | 0.0017431 | 0.0012818 | 0.0041186 | -0.0012925 | -0.0040845 | -0.0014697 | -54.8676 | 65.5975 | -57.3029 | 65.3229 | -56.7352 | -57.1747 | -56.5613 | -56.1218 | 65.6387 | -57.2571 | -57.2388 | -57.28 | -57.3853 | -57.0465 | -0.064086 | -0.041199 | -0.31586 | 0.50354 | 0.67749 | 0.064087 | 0.74158 | 0.12817 | -0.01831 | 0 | -122.8775 | -0.041198 | 0.19226 | -0.14648 | 0.21057 | -0.12817 | 0.56763 | 122.6257 | -0.022888 | 0.01831 | 122.9004 | 122.8958 | 122.8363 | 122.8775 | -122.9416 | -122.8958 | 122.5616 | 0 | 2.3712 | 1.1169
2226.1719 | 122.9416 | -57.2067 | 65.6296 | -0.083466 | 0.00019446 | 0.062025 | 0.070113 | -0.0017624 | 0.00026909 | 0.0079852 | -0.0074462 | 0.0013159 | 0.0014954 | 0.0034778 | -0.00043791 | -0.0047253 | -0.0018971 | -54.8401 | 65.6067 | -57.2708 | 65.3915 | -56.662 | -57.1152 | -56.5109 | -56.0394 | 65.6387 | -57.2433 | -57.193 | -57.2296 | -57.3395 | -57.0099 | -0.064087 | -0.022889 | -0.23804 | 0.54474 | 0.6958 | 0.091553 | 0.75989 | 0.15564 | -0.036621 | 0.009155 | -122.8226 | -0.022888 | 0.19684 | -0.13275 | 0.23346 | -0.096131 | 0.60883 | 122.6624 | 0.013733 | 0.050354 | 122.8775 | 122.8821 | 122.8134 | 122.8455 | -122.9004 | -122.8729 | 122.5983 | 0.013733 | 2.3666 | 1.1673
2227.1719 | 123.0286 | -57.2159 | 65.6067 | -0.068207 | 0.00083526 | 0.06288 | 0.0699 | -0.0041122 | 0.0015509 | 0.0039264 | 0.074951 | -0.0029567 | 0.001709 | -0.0050672 | 0.00020289 | -0.0038709 | 2.554e-05 | -54.8676 | 65.5746 | -57.2525 | 65.3961 | -56.6437 | -57.0786 | -56.4606 | -56.0165 | 65.6113 | -57.225 | -57.1518 | -57.1609 | -57.2617 | -56.9687 | -0.036621 | -0.032043 | -0.21057 | 0.5722 | 0.75531 | 0.13733 | 0.79193 | 0.17395 | -0.009156 | 0.004578 | -122.7585 | 0.054931 | 0.24719 | -0.045777 | 0.25635 | -0.036621 | 0.60883 | 122.6486 | 0.064087 | 0.073243 | 122.8271 | 122.8363 | 122.7905 | 122.8271 | -122.8592 | -122.8317 | 122.612 | 0.064087 | 2.3483 | 1.1993
2228.1719 | 122.937 | -57.2205 | 65.6479 | -0.11398 | 0.0014761 | 0.060316 | 0.072036 | -5.343e-05 | 0.0013373 | 0.010762 | -0.03186 | 0.00088875 | -0.00021357 | 0.0017688 | -0.0023605 | -0.0023755 | -0.00018806 | -54.8996 | 65.6021 | -57.2937 | 65.1398 | -57.0282 | -56.8909 | -56.3416 | -56.0623 | 65.6342 | -57.2296 | -57.2388 | -57.2662 | -57.3853 | -57.0236 | -0.073242 | -0.045776 | -0.50812 | 0.19226 | 0.87891 | 0.32959 | 0.95215 | 0.40283 | -0.009155 | -0.013733 | -122.8867 | -0.045776 | 0.19684 | -0.1648 | 0.20599 | -0.15564 | 0.2655 | 122.4335 | -0.036621 | -0.009156 | 122.8958 | 122.8638 | 122.8226 | 122.8546 | -122.9416 | -122.8775 | 122.3602 | -0.018311 | 2.3209 | 1.1581
2229.1719 | 122.9553 | -57.2205 | 65.6067 | -0.098725 | 0.00062166 | 0.063734 | 0.069686 | 0.0018692 | 0.0060369 | 0.0077716 | -0.028809 | 0.0015295 | -0.00064077 | -0.0037854 | -0.0019333 | -0.0040845 | -0.00061526 | -54.8859 | 65.5884 | -57.2983 | 65.1215 | -56.6803 | -56.8085 | -56.4835 | -56.0486 | 65.657 | -57.2296 | -57.2205 | -57.2708 | -57.3807 | -57.0419 | -0.07782 | -0.01831 | -0.48523 | 0.54016 | 0.737 | 0.41199 | 0.81482 | 0.48981 | -0.009155 | 0.050354 | -122.8271 | -0.050354 | 0.17853 | -0.16022 | 0.18768 | -0.15106 | 0.61798 | 122.4197 | -0.041199 | 0.009155 | 122.8867 | 122.8867 | 122.8088 | 122.8775 | -122.905 | -122.8363 | 122.3419 | 0 | 2.3346 | 1.1719
2230.1719 | 122.9645 | -57.2342 | 65.5884 | -0.15213 | -0.00066014 | 0.061385 | 0.068618 | 0.0057144 | 0.0043281 | 0.0017902 | -0.0013428 | 0.00046135 | 0.001709 | 0.0032642 | -0.00086511 | -0.0025891 | 0.00045294 | -54.8996 | 65.5746 | -57.3303 | 65.5289 | -56.5704 | -57.2479 | -56.575 | -56.131 | 65.6799 | -57.2754 | -57.2342 | -57.2754 | -57.3807 | -57.0236 | -0.09613 | -0.013733 | -0.059509 | 0.66376 | 0.65918 | -0.013733 | 0.75531 | 0.082397 | -0.041199 | 0.091553 | -122.8226 | -0.041199 | 0.21057 | -0.14648 | 0.25177 | -0.10529 | 0.75989 | 122.8592 | 0 | 0.041199 | 122.905 | 122.9553 | 122.8088 | 122.9141 | -122.9187 | -122.8638 | 122.7631 | 0 | 2.3346 | 1.1032
2231.1719 | 122.9599 | -57.2433 | 65.5792 | -0.037689 | 0.0012625 | 0.06053 | 0.070541 | -0.0015488 | 0.0026191 | 0.0037128 | -0.028809 | 0.00088875 | -0.0012818 | -0.0097668 | -0.0017197 | -0.0051527 | 0.00088014 | -54.8996 | 65.5838 | -57.3166 | 65.419 | -56.8222 | -57.1472 | -56.5018 | -56.0944 | 65.6296 | -57.2754 | -57.2342 | -57.2571 | -57.3853 | -57.0099 | -0.073242 | 0.004577 | -0.16022 | 0.42114 | 0.74158 | 0.09613 | 0.81482 | 0.16937 | -0.032044 | 0.050354 | -122.8134 | -0.013733 | 0.23346 | -0.14191 | 0.2655 | -0.10986 | 0.49438 | 122.7356 | 0.018311 | 0.041199 | 122.9004 | 122.905 | 122.8271 | 122.8729 | -122.8958 | -122.8546 | 122.6624 | 0.009155 | 2.3438 | 1.149
2232.1719 | 123.0331 | -57.2113 | 65.5701 | -0.11398 | 0.00019446 | 0.062025 | 0.068618 | -0.0043258 | 0.0028327 | 0.0043536 | 0.062744 | 0.00046135 | -0.00042717 | -0.002931 | -0.0015061 | -0.0042981 | -0.00040166 | -54.8584 | 65.5884 | -57.2388 | 65.4007 | -56.6483 | -57.0923 | -56.4606 | -56.0394 | 65.6113 | -57.2113 | -57.0419 | -57.2617 | -57.3029 | -56.9778 | -0.027466 | 0.018311 | -0.16937 | 0.56305 | 0.75073 | 0.11902 | 0.7782 | 0.14649 | 0 | 0.041199 | -122.612 | -0.050354 | 0.23346 | -0.091552 | 0.23346 | -0.091552 | 0.59052 | 122.6395 | -0.050354 | 0.16937 | 122.8271 | 122.8226 | 122.7997 | 122.8226 | -122.8088 | -122.7814 | 122.612 | 0.16937 | 2.3529 | 1.1719
2233.1719 | 122.9507 | -57.2296 | 65.5701 | -0.13687 | 0.0010489 | 0.062025 | 0.068832 | -0.0015488 | 0.0032599 | 0.0054218 | -0.019653 | 0.0019567 | -0.0023498 | -0.0027174 | -0.0015061 | -0.0057935 | 0.00023934 | -54.9774 | 65.5746 | -57.3441 | 65.3229 | -56.694 | -57.1884 | -56.5613 | -56.1035 | 65.6525 | -57.2571 | -57.1976 | -57.2479 | -57.3486 | -57.019 | -0.11444 | 0.004578 | -0.24719 | 0.53558 | 0.66833 | 0.041198 | 0.78278 | 0.15564 | -0.027466 | 0.082398 | -122.7676 | -0.018311 | 0.21057 | -0.11902 | 0.23804 | -0.091553 | 0.65002 | 122.6669 | 0.009155 | 0.059509 | 122.9187 | 122.9095 | 122.8043 | 122.8821 | -122.9141 | -122.8271 | 122.5525 | 0.032043 | 2.2522 | 1.1261
2234.1719 | 122.9187 | -57.2617 | 65.625 | -0.098725 | 0.0012625 | 0.062453 | 0.070541 | 0.00058737 | -0.0010125 | 0.0045672 | -0.037964 | 0.0013159 | -0.00042717 | -0.00464 | -0.0012925 | -0.0017347 | 0.0015209 | -54.8767 | 65.5975 | -57.3166 | 65.3412 | -56.7627 | -57.2021 | -56.5796 | -56.1356 | 65.6342 | -57.2388 | -57.2388 | -57.2891 | -57.4127 | -57.0557 | -0.054931 | -0.027466 | -0.28381 | 0.49896 | 0.68207 | 0.05951 | 0.737 | 0.11444 | 0.022888 | 0.009155 | -122.8638 | -0.027466 | 0.20599 | -0.15106 | 0.18311 | -0.17395 | 0.55389 | 122.6578 | -0.050354 | 0 | 122.9141 | 122.8729 | 122.8592 | 122.8958 | -122.9416 | -122.8638 | 122.6028 | 0.022888 | 2.3849 | 1.1261
2235.1719 | 123.0972 | -57.2159 | 65.5655 | -0.098725 | -0.0013009 | 0.063307 | 0.0699 | 0.0037918 | 0.0011237 | 0.0071308 | -0.010498 | -0.0018885 | -0.00085457 | 0.0030506 | -0.0027877 | -0.0047253 | -0.00082886 | -54.8218 | 65.538 | -57.2571 | 65.4465 | -56.6208 | -57.0694 | -56.4514 | -55.9845 | 65.5701 | -57.2525 | -57.1106 | -57.1289 | -57.4539 | -57.0694 | -0.041199 | -0.027466 | -0.11902 | 0.59509 | 0.76447 | 0.14648 | 0.80566 | 0.18768 | -0.036621 | 0.004577 | -122.6761 | 0.086975 | 0.14648 | -0.23804 | 0.1831 | -0.20142 | 0.63629 | 122.7036 | 0.1236 | 0.14191 | 122.7951 | 122.8226 | 122.7539 | 122.7859 | -122.8226 | -122.818 | 122.6624 | 0.10529 | 2.3941 | 1.2314
2236.1719 | 123.0331 | -57.1655 | 65.5655 | -0.10635 | -0.00066014 | 0.062453 | 0.068404 | -0.0043258 | 0.0041143 | 0.0052082 | 0.0078126 | -0.00017945 | 0.0012818 | -0.0035718 | -0.0010787 | -0.0010937 | -0.00040166 | -54.8126 | 65.538 | -57.2708 | 65.4327 | -56.6116 | -57.0602 | -56.4697 | -55.9799 | 65.5701 | -57.2021 | -57.1426 | -56.9916 | -57.1609 | -56.9092 | -0.10529 | -0.027466 | -0.13275 | 0.55389 | 0.6958 | 0.10528 | 0.80109 | 0.21057 | -0.036621 | 0.004577 | -122.7081 | 0.17395 | 0.25635 | 0.004577 | 0.29297 | 0.041198 | 0.65918 | 122.7036 | 0.21057 | 0.059509 | 122.8088 | 122.7722 | 122.7036 | 122.7356 | -122.8363 | -122.7676 | 122.5983 | 0.022888 | 2.3529 | 1.1856
2237.1719 | 123.0286 | -57.1609 | 65.5792 | -0.091095 | 0.0016899 | 0.063094 | 0.070113 | 0.00016017 | 0.0015509 | 0.0071308 | 0.013916 | 0.00067495 | -0.00064077 | -0.0016492 | -0.0053513 | -0.0062207 | 0.0023755 | -54.8126 | 65.5563 | -57.2708 | 65.4556 | -56.6116 | -57.0786 | -56.4468 | -56.1539 | 65.5426 | -57.2479 | -57.0969 | -57.1335 | -57.2388 | -56.9275 | -0.10986 | -0.022889 | -0.1236 | 0.54932 | 0.71411 | 0.082398 | 0.82397 | 0.19226 | -0.086975 | -0.036621 | -122.6761 | 0.027466 | 0.23346 | -0.07782 | 0.32044 | 0.009155 | 0.65918 | 122.7264 | 0.11444 | 0.15106 | 122.8271 | 122.7905 | 122.7173 | 122.7036 | -122.85 | -122.8271 | 122.6166 | 0.064087 | 2.3483 | 1.0071
2238.1719 | 123.056 | -57.1747 | 65.5746 | -0.1445 | 0.00019446 | 0.062453 | 0.069686 | 0.00058737 | -0.0012261 | 0.0064898 | -0.01355 | 0.0011023 | 0.001709 | 0.0019824 | -0.0030013 | -0.0036573 | -0.0012561 | -54.8035 | 65.5426 | -57.2891 | 65.2725 | -56.6483 | -56.8542 | -56.3278 | -55.9158 | 65.593 | -57.2296 | -57.0969 | -57.1518 | -57.2433 | -56.9183 | -0.11444 | -0.032043 | -0.30212 | 0.52643 | 0.84686 | 0.32044 | 0.9613 | 0.43488 | -0.054931 | 0.018311 | -122.6715 | 0.022889 | 0.25635 | -0.068664 | 0.31128 | -0.013733 | 0.64087 | 122.5616 | 0.07782 | 0.13275 | 122.8317 | 122.8226 | 122.7173 | 122.7676 | -122.8638 | -122.8043 | 122.4472 | 0.07782 | 2.3712 | 1.2589
2239.1719 | 123.0606 | -57.1701 | 65.5746 | -0.12924 | -0.0013009 | 0.063094 | 0.069686 | 0.0035782 | 0.0013373 | 0.0054218 | -0.025757 | 0.0028113 | -0.0014954 | -0.0027174 | -0.0015061 | -0.0040845 | 2.554e-05 | -54.8126 | 65.5746 | -57.2937 | 65.4144 | -56.6483 | -57.074 | -56.456 | -55.9662 | 65.5792 | -57.2479 | -57.106 | -57.1381 | -57.2571 | -56.9275 | -0.1236 | 0 | -0.16022 | 0.52185 | 0.71411 | 0.09613 | 0.83771 | 0.21973 | -0.07782 | 0.004578 | -122.6807 | 0.032043 | 0.24262 | -0.086975 | 0.32044 | -0.009155 | 0.64545 | 122.7081 | 0.10986 | 0.14191 | 122.8683 | 122.8271 | 122.7448 | 122.7493 | -122.8683 | -122.8226 | 122.5845 | 0.064087 | 2.3575 | 1.2039
2240.1719 | 123.0148 | -57.2113 | 65.5655 | -0.098725 | -0.0010873 | 0.062025 | 0.069472 | 0.00251 | 0.0030463 | 0.0039264 | -0.041016 | -0.00017945 | -0.0023498 | -0.001222 | -0.0027877 | -0.0034437 | 0.00088014 | -54.863 | 65.5792 | -57.2845 | 65.3641 | -56.6986 | -57.1564 | -56.5292 | -56.044 | 65.5975 | -57.2479 | -57.1518 | -57.1747 | -57.2845 | -56.9321 | -0.073242 | 0.013733 | -0.20142 | 0.5127 | 0.68207 | 0.054932 | 0.75531 | 0.12817 | -0.036621 | 0.032043 | -122.7173 | 0.036621 | 0.27924 | -0.073242 | 0.31586 | -0.036621 | 0.58594 | 122.6486 | 0.073242 | 0.096131 | 122.8638 | 122.8455 | 122.7905 | 122.8088 | -122.85 | -122.8134 | 122.5754 | 0.05951 | 2.3483 | 1.1673
2241.1719 | 123.0331 | -57.1838 | 65.593 | -0.083466 | 0.00083526 | 0.063094 | 0.070327 | 0.0012284 | 0.0015509 | 0.0045672 | -0.022705 | -0.0010339 | -0.0012818 | -0.0031446 | -0.0027877 | -0.0040845 | 0.0013073 | -54.808 | 65.5472 | -57.312 | 65.4465 | -56.6162 | -57.0694 | -56.4514 | -56.0852 | 65.5472 | -57.2754 | -57.1106 | -57.106 | -57.2342 | -56.9183 | -0.12817 | -0.045777 | -0.14648 | 0.56763 | 0.73242 | 0.11444 | 0.8606 | 0.24262 | -0.091553 | -0.045777 | -122.7036 | 0.07782 | 0.2655 | -0.050354 | 0.35706 | 0.041199 | 0.6958 | 122.7585 | 0.16937 | 0.16479 | 122.8592 | 122.8226 | 122.731 | 122.731 | -122.905 | -122.8683 | 122.6303 | 0.073242 | 2.3758 | 1.0986
2242.1719 | 123.0194 | -57.2159 | 65.5701 | -0.12161 | 0.0023307 | 0.06053 | 0.0699 | -0.0034714 | 0.0017645 | 0.0054218 | 0.016968 | -0.00060665 | -0.0014954 | -0.0010084 | -0.0010787 | -0.0047253 | 0.0013073 | -54.8264 | 65.5472 | -57.2662 | 65.4373 | -56.5933 | -57.0694 | -56.4651 | -55.9891 | 65.5746 | -57.2296 | -57.1289 | -57.1747 | -57.2617 | -56.9641 | -0.050354 | -0.022888 | -0.13275 | 0.62256 | 0.75073 | 0.14648 | 0.80109 | 0.19684 | -0.013733 | 0.004578 | -122.699 | 0.041198 | 0.25177 | -0.045777 | 0.2655 | -0.032044 | 0.67291 | 122.7036 | 0.054931 | 0.10071 | 122.8134 | 122.8043 | 122.7631 | 122.7905 | -122.8363 | -122.7997 | 122.6532 | 0.086975 | 2.3895 | 1.2268
2243.1719 | 123.0194 | -57.1793 | 65.5975 | -0.068207 | 0.00040806 | 0.06053 | 0.067336 | -0.00090783 | 0.0021917 | 0.0049946 | 0.02002 | 0.00088875 | 0.0012818 | -0.0059216 | -0.00086511 | -0.0051527 | 0.0021619 | -54.8447 | 65.5655 | -57.2662 | 65.4053 | -56.6574 | -57.0786 | -56.4468 | -56.0074 | 65.6021 | -57.2479 | -57.1426 | -57.0236 | -57.1381 | -56.9504 | -0.086975 | -0.032043 | -0.19226 | 0.52185 | 0.73242 | 0.10071 | 0.8194 | 0.18768 | -0.068665 | 0.004578 | -122.7402 | 0.15564 | 0.22888 | 0.041198 | 0.29755 | 0.10986 | 0.60883 | 122.6715 | 0.2243 | 0.10529 | 122.8317 | 122.85 | 122.7448 | 122.7814 | -122.8638 | -122.8455 | 122.5845 | 0.036621 | 2.3346 | 1.1719
2244.1719 | 122.9874 | -57.1976 | 65.6296 | -0.068207 | -0.00023294 | 0.062025 | 0.070541 | 0.00037377 | 0.0017645 | 0.0052082 | -0.053223 | 0.00088875 | 0.00042723 | 0.001128 | 0.00020289 | -0.0038709 | -0.0016833 | -54.7989 | 65.6525 | -57.2708 | 65.419 | -56.6757 | -57.0648 | -56.4972 | -56.0211 | 65.657 | -57.2205 | -57.1381 | -57.1564 | -57.2983 | -56.9778 | -0.073242 | 0.022888 | -0.21057 | 0.52185 | 0.70038 | 0.13275 | 0.77362 | 0.20599 | -0.022888 | 0.027465 | -122.7676 | 0.041199 | 0.21973 | -0.10071 | 0.24262 | -0.07782 | 0.59509 | 122.6898 | 0.064087 | 0.082397 | 122.9233 | 122.8775 | 122.85 | 122.8546 | -122.9004 | -122.85 | 122.6166 | 0.059509 | 2.3987 | 1.1765
2245.1719 | 123.0148 | -57.1793 | 65.593 | -0.12161 | -0.0036507 | 0.062453 | 0.069472 | 0.0010148 | 0.0026191 | 0.0037128 | 0.02002 | 0.0011023 | 0.00064083 | 0.00027342 | -0.0023605 | -0.0057935 | 2.554e-05 | -54.8447 | 65.5792 | -57.2708 | 65.4053 | -56.6574 | -57.0969 | -56.4789 | -55.9982 | 65.5975 | -57.2433 | -57.1609 | -57.1564 | -57.2617 | -56.9458 | -0.091553 | -0.013733 | -0.18768 | 0.52185 | 0.70038 | 0.082397 | 0.79193 | 0.17395 | -0.064087 | 0.004577 | -122.7539 | 0.022888 | 0.23346 | -0.082398 | 0.29755 | -0.018311 | 0.6134 | 122.6761 | 0.086975 | 0.082397 | 122.85 | 122.8409 | 122.7585 | 122.7768 | -122.8638 | -122.8363 | 122.5845 | 0.01831 | 2.3346 | 1.181
2246.1719 | 123.0103 | -57.193 | 65.6158 | 0.053863 | 0.0021171 | 0.062666 | 0.066482 | -0.0024032 | 0.0026191 | 0.0032856 | 0.029175 | -0.00017945 | 0.00085443 | 0.0015552 | -0.0019333 | -0.0049389 | -0.00018806 | -54.9042 | 65.5838 | -57.2708 | 65.4144 | -56.662 | -57.0557 | -56.4697 | -55.9891 | 65.625 | -57.2296 | -57.1152 | -57.1381 | -57.2342 | -56.9504 | -0.07782 | -0.032044 | -0.20142 | 0.53101 | 0.72327 | 0.13733 | 0.80109 | 0.21515 | -0.036621 | 0.009155 | -122.731 | 0.054931 | 0.24262 | -0.041199 | 0.27924 | -0.004578 | 0.60883 | 122.6852 | 0.091552 | 0.11444 | 122.8546 | 122.8546 | 122.7768 | 122.818 | -122.8867 | -122.8455 | 122.6074 | 0.07782 | 2.2888 | 1.2039
2247.1719 | 123.0011 | -57.1564 | 65.6296 | -0.098725 | 0.00062166 | 0.061385 | 0.067123 | -0.00026703 | 0.0049689 | 0.003072 | 0.0078126 | 0.0011023 | -0.00064077 | 0.0032642 | -0.0027877 | -0.0038709 | -0.0025379 | -54.8309 | 65.5792 | -57.2617 | 65.4144 | -56.6483 | -57.0694 | -56.4423 | -56.012 | 65.5975 | -57.2296 | -57.1335 | -57.1152 | -57.1106 | -56.8268 | -0.10529 | -0.050354 | -0.21515 | 0.50812 | 0.71411 | 0.086975 | 0.8194 | 0.19226 | -0.073242 | -0.032044 | -122.7631 | 0.041199 | 0.32959 | 0.045776 | 0.40283 | 0.11902 | 0.6134 | 122.6761 | 0.11444 | 0.09613 | 122.8409 | 122.8271 | 122.7356 | 122.7539 | -122.8912 | -122.8592 | 122.5708 | 0.022888 | 2.3254 | 1.1444
2248.1719 | 123.0011 | -57.193 | 65.6021 | -0.13687 | -0.00087374 | 0.060744 | 0.068404 | -0.0013352 | 0.0043281 | 0.0047808 | -0.0074462 | -0.00017945 | -0.00042717 | -0.0016492 | -0.0017197 | -0.0038709 | -0.0016833 | -54.8355 | 65.593 | -57.2388 | 65.4099 | -56.6483 | -57.0786 | -56.4423 | -56.0074 | 65.6158 | -57.2205 | -57.1518 | -57.1472 | -57.2571 | -56.9321 | -0.045777 | -0.009155 | -0.19226 | 0.54474 | 0.75073 | 0.11444 | 0.79651 | 0.16022 | -0.027466 | 0.013733 | -122.7539 | 0.045776 | 0.26093 | -0.064087 | 0.28839 | -0.036621 | 0.59052 | 122.6486 | 0.073242 | 0.068665 | 122.8317 | 122.8363 | 122.7859 | 122.8088 | -122.8409 | -122.8226 | 122.6028 | 0.041199 | 2.3575 | 1.1856
2249.1719 | 123.0789 | -57.1518 | 65.6204 | -0.098725 | -0.0017281 | 0.060957 | 0.069686 | -0.0017624 | 0.0034735 | 0.0032856 | 0.035278 | 0.0011023 | 0.00042723 | -0.0031446 | -0.0021469 | -0.0055799 | -0.0014697 | -54.7806 | 65.6158 | -57.2525 | 65.5243 | -56.5338 | -56.987 | -56.3736 | -55.8838 | 65.6342 | -57.2067 | -57.0374 | -57.0602 | -57.1472 | -56.8817 | -0.10071 | -0.004577 | -0.09613 | 0.61798 | 0.7782 | 0.16479 | 0.87891 | 0.2655 | -0.054932 | 0.013733 | -122.6578 | 0.091552 | 0.27008 | 0.004577 | 0.32501 | 0.059509 | 0.71869 | 122.7768 | 0.14648 | 0.16937 | 122.8683 | 122.8409 | 122.7676 | 122.7859 | -122.8729 | -122.8271 | 122.6761 | 0.11444 | 2.3712 | 1.268
2250.1719 | 123.0789 | -57.1747 | 65.6113 | -0.068207 | -0.0013009 | 0.061171 | 0.070113 | -0.001976 | 0.0030463 | 0.0081988 | 0.02002 | -0.0010339 | -0.0021362 | -0.0035718 | -0.0023605 | -0.0042981 | -0.00061526 | -54.7989 | 65.5975 | -57.2433 | 65.4648 | -56.6071 | -57.0236 | -56.4056 | -55.957 | 65.6479 | -57.2205 | -57.0969 | -57.106 | -57.2021 | -56.8954 | -0.068664 | -0.013733 | -0.14648 | 0.56763 | 0.76904 | 0.15106 | 0.83771 | 0.21973 | -0.045776 | 0.036621 | -122.7081 | 0.068665 | 0.27924 | -0.027465 | 0.32501 | 0.018311 | 0.63629 | 122.7081 | 0.11444 | 0.1236 | 122.8409 | 122.8683 | 122.7722 | 122.8226 | -122.8546 | -122.8317 | 122.6395 | 0.07782 | 2.3758 | 1.2177
2251.1719 | 122.9416 | -57.1838 | 65.6113 | -0.03006 | 0.0027579 | 0.061385 | 0.0699 | 0.0018692 | 0.0024053 | 0.0045672 | -0.077637 | 0.00088875 | 0.00042723 | 0.0032642 | -0.0019333 | -0.0025891 | -0.0016833 | -54.7852 | 65.6067 | -57.2754 | 65.4373 | -56.6528 | -57.074 | -56.4835 | -55.9799 | 65.6891 | -57.2159 | -57.1335 | -57.1884 | -57.2891 | -56.9595 | -0.091553 | -0.004578 | -0.17395 | 0.53101 | 0.70038 | 0.10986 | 0.79193 | 0.20142 | -0.032043 | 0.07782 | -122.7448 | -0.004578 | 0.2243 | -0.10529 | 0.25635 | -0.073243 | 0.62256 | 122.7127 | 0.027465 | 0.082397 | 122.8821 | 122.905 | 122.7905 | 122.8729 | -122.8867 | -122.8271 | 122.6212 | 0.050354 | 2.3987 | 1.2039
2252.1719 | 123.0743 | -57.1472 | 65.6113 | -0.10635 | -0.00087374 | 0.063307 | 0.068404 | -0.00026703 | 0.0043281 | 0.0045672 | 0.03833 | 0.0011023 | -0.00021357 | -0.0061352 | 0.00020289 | -0.0064343 | -0.0029651 | -54.7806 | 65.593 | -57.2479 | 65.4739 | -56.5887 | -57.0328 | -56.4056 | -55.9433 | 65.6387 | -57.2159 | -57.074 | -57.0694 | -57.193 | -56.8954 | -0.10071 | -0.01831 | -0.13733 | 0.55847 | 0.74158 | 0.11444 | 0.84229 | 0.21515 | -0.068664 | 0.027466 | -122.6852 | 0.07782 | 0.25177 | -0.045776 | 0.32043 | 0.022888 | 0.65918 | 122.7219 | 0.14648 | 0.14191 | 122.8409 | 122.8546 | 122.7402 | 122.7859 | -122.8592 | -122.8271 | 122.6212 | 0.073242 | 2.3666 | 1.2039
2253.1719 | 123.0148 | -57.1701 | 65.6021 | -0.045319 | 0.0021171 | 0.061598 | 0.067977 | -0.0024032 | 0.0017645 | 0.0020038 | 0.016968 | -0.0010339 | 0.00042723 | -0.007417 | 0.0014847 | -0.0013073 | -0.0029651 | -54.7531 | 65.6113 | -57.2296 | 65.5334 | -56.5109 | -56.9687 | -56.3965 | -55.8929 | 65.6021 | -57.1976 | -57.2205 | -57.0053 | -57.1655 | -56.9138 | -0.059509 | 0.009155 | -0.068665 | 0.65918 | 0.77362 | 0.20142 | 0.83313 | 0.26093 | -0.027466 | 0 | -122.8226 | 0.16479 | 0.25635 | 0.004578 | 0.28381 | 0.032044 | 0.71869 | 122.7631 | 0.19226 | -0.022888 | 122.8409 | 122.7997 | 122.7814 | 122.7722 | -122.8317 | -122.7997 | 122.7036 | -0.050354 | 2.417 | 1.2772
2254.1719 | 123.0515 | -57.1747 | 65.5975 | -0.11398 | 0.00019446 | 0.062025 | 0.070113 | -0.00090783 | 0.0030463 | 0.0045672 | 0.001709 | 0.00088875 | -0.0021362 | -0.00058098 | -0.0015061 | -0.0038709 | -0.0027515 | -54.7943 | 65.5838 | -57.2662 | 65.4465 | -56.6345 | -57.074 | -56.4285 | -55.9799 | 65.6296 | -57.2205 | -57.1106 | -57.1198 | -57.2342 | -56.9366 | -0.091552 | -0.013733 | -0.15106 | 0.54016 | 0.74616 | 0.10071 | 0.83771 | 0.19226 | -0.045776 | 0.032044 | -122.7081 | 0.054932 | 0.23804 | -0.059509 | 0.28381 | -0.013733 | 0.63171 | 122.7127 | 0.10071 | 0.10986 | 122.85 | 122.85 | 122.7585 | 122.8043 | -122.8638 | -122.818 | 122.6212 | 0.064087 | 2.3804 | 1.1948
2255.1719 | 123.0515 | -57.1335 | 65.6158 | -0.091095 | -0.00087374 | 0.061812 | 0.067336 | 0.00037377 | 0.0021917 | 0.0067036 | 0.010864 | -0.0053065 | 0.0021362 | -0.003999 | -0.0015061 | -0.0045117 | -0.00018806 | -54.7394 | 65.5884 | -57.2205 | 65.5014 | -56.543 | -56.987 | -56.3828 | -55.6732 | 65.712 | -57.1701 | -57.1152 | -57.0648 | -57.193 | -56.9321 | -0.086975 | -0.027466 | -0.11444 | 0.59052 | 0.75073 | 0.14648 | 0.83771 | 0.23346 | -0.036621 | 0.09613 | -122.731 | 0.068665 | 0.20142 | -0.059509 | 0.23804 | -0.022888 | 0.67749 | 122.7219 | 0.10529 | 0.054932 | 122.8088 | 122.8821 | 122.7219 | 122.8455 | -122.8363 | -122.7859 | 122.6349 | 0.018311 | 2.3941 | 1.4603
2256.1719 | 123.0606 | -57.1564 | 65.6158 | -0.045319 | -0.00023294 | 0.062239 | 0.067977 | 0.0029374 | 0.0036871 | 0.0073444 | 0.14514 | -0.00082025 | 0.0019226 | 0.00027342 | -1.0706e-05 | -0.0042981 | -0.0074513 | -54.7302 | 65.5884 | -57.2113 | 65.5106 | -56.543 | -56.9641 | -56.369 | -56.1264 | 65.6616 | -57.2296 | -57.0602 | -57.0923 | -57.1793 | -56.9 | -0.054932 | -0.027466 | -0.10529 | 0.6134 | 0.78735 | 0.19226 | 0.84228 | 0.24719 | -0.073242 | 0.045776 | -122.6761 | 0.064087 | 0.25635 | -0.022888 | 0.32959 | 0.050354 | 0.66833 | 122.7219 | 0.13733 | 0.16937 | 122.7997 | 122.8912 | 122.7448 | 122.818 | -122.8271 | -122.8455 | 122.6669 | 0.09613 | 2.4261 | 1.03
2257.1719 | 123.0377 | -57.1564 | 65.6021 | -0.045319 | -0.00023294 | 0.061598 | 0.068832 | 0.0037918 | -0.0014399 | 0.0034992 | 0.096313 | 0.0032385 | 0.0019226 | 0.0051868 | -0.0025741 | -0.0049389 | -0.0033923 | -54.7256 | 65.6021 | -57.2296 | 65.5106 | -56.5247 | -56.9687 | -56.3919 | -55.9296 | 65.6708 | -57.1976 | -57.0877 | -57.0831 | -57.1976 | -56.9046 | -0.073242 | 0 | -0.091553 | 0.63171 | 0.76446 | 0.18768 | 0.83771 | 0.26093 | -0.041199 | 0.068664 | -122.6898 | 0.073242 | 0.25177 | -0.041199 | 0.29297 | 0 | 0.70496 | 122.7402 | 0.11444 | 0.10986 | 122.8317 | 122.8683 | 122.7585 | 122.8271 | -122.8317 | -122.7997 | 122.6669 | 0.068664 | 2.4307 | 1.2268
2258.1719 | 123.0423 | -57.1472 | 65.5975 | -0.10635 | 0.00019446 | 0.06053 | 0.069686 | 0.00037377 | 0.0028327 | 0.0037128 | 0.02002 | 0.00046135 | 0.0014954 | -0.002931 | -0.0023605 | -0.0051527 | -0.0016833 | -54.7211 | 65.625 | -57.2113 | 65.5014 | -56.5384 | -56.9824 | -56.3828 | -55.8884 | 65.6525 | -57.1518 | -57.0374 | -57.1564 | -57.1884 | -56.8817 | -0.064087 | 0.027466 | -0.09613 | 0.60883 | 0.76447 | 0.16479 | 0.82855 | 0.22888 | -0.004577 | 0.054932 | -122.6349 | -0.009155 | 0.2655 | -0.041199 | 0.27008 | -0.036622 | 0.67291 | 122.7127 | -0.004578 | 0.11444 | 122.8363 | 122.8043 | 122.7722 | 122.7997 | -122.8088 | -122.7493 | 122.6486 | 0.10986 | 2.4261 | 1.2588
2259.1719 | 123.0469 | -57.1747 | 65.5838 | -0.045319 | -1.9142e-05 | 0.062453 | 0.067763 | 0.00016017 | 0.0026191 | 0.0054218 | 0.013916 | -0.0010339 | -0.00021357 | -0.0078442 | -0.0015061 | -0.00045288 | 0.0036571 | -54.7256 | 65.593 | -57.2205 | 65.538 | -56.5063 | -56.9824 | -56.3828 | -55.8884 | 65.6342 | -57.1655 | -57.2388 | -57.0374 | -57.1243 | -56.8954 | -0.045776 | 0.009156 | -0.045776 | 0.66833 | 0.79193 | 0.19226 | 0.83771 | 0.23804 | 0.009156 | 0.050354 | -122.8226 | 0.13733 | 0.27924 | 0.050354 | 0.27008 | 0.041198 | 0.71411 | 122.7585 | 0.12817 | -0.073243 | 122.8134 | 122.7997 | 122.7676 | 122.8088 | -122.8043 | -122.7493 | 122.7127 | -0.064087 | 2.449 | 1.2863
2260.1719 | 123.1155 | -57.1655 | 65.6113 | -0.075836 | 0.0016899 | 0.062453 | 0.071609 | -0.0041122 | 0.0019781 | 0.0015766 | 0.016968 | 0.0013159 | 0.00085443 | -0.0010084 | -0.0012925 | -0.0057935 | -0.0018971 | -54.7348 | 65.5975 | -57.225 | 65.5289 | -56.5018 | -56.9641 | -56.3553 | -55.8884 | 65.6433 | -57.2021 | -56.8542 | -57.2845 | -57.4356 | -56.9778 | -0.05951 | -0.013733 | -0.082397 | 0.66376 | 0.81024 | 0.20142 | 0.86975 | 0.26093 | -0.036621 | 0.032044 | -122.4655 | -0.11902 | 0.18768 | -0.27008 | 0.2243 | -0.23346 | 0.72327 | 122.7539 | -0.082398 | 0.3479 | 122.8226 | 122.8455 | 122.7631 | 122.8088 | -122.8363 | -122.8134 | 122.6944 | 0.31128 | 2.4307 | 1.2772
2261.1719 | 123.0652 | -57.1701 | 65.5838 | -0.1445 | -0.00044654 | 0.063734 | 0.069259 | -0.0038986 | 0.0019781 | 0.0062762 | 0.02002 | 0.00024775 | 0.001068 | 0.002196 | -0.0036423 | -0.0038709 | -0.0025379 | -54.7714 | 65.5975 | -57.2388 | 65.4831 | -56.6025 | -57.0007 | -56.4102 | -55.9433 | 65.6342 | -57.2067 | -57.0831 | -57.0831 | -57.1838 | -56.8954 | -0.068665 | 0.013733 | -0.10071 | 0.56763 | 0.75989 | 0.16937 | 0.82855 | 0.23804 | -0.036621 | 0.050354 | -122.6669 | 0.086975 | 0.27466 | -0.013733 | 0.31128 | 0.022888 | 0.63629 | 122.7219 | 0.1236 | 0.1236 | 122.8363 | 122.8409 | 122.7676 | 122.8043 | -122.8226 | -122.7905 | 122.6532 | 0.086975 | 2.3987 | 1.2268
2262.1719 | 123.0606 | -57.1518 | 65.6158 | -0.068207 | 0.0021171 | 0.061812 | 0.068618 | -0.0041122 | 0.0013373 | 0.0032856 | 0.0078126 | -0.00060665 | 0.0019226 | -0.0037854 | -0.00086511 | -0.0040845 | -0.0016833 | -54.7394 | 65.5884 | -57.2388 | 65.5243 | -56.543 | -56.987 | -56.3873 | -55.8609 | 65.6433 | -57.1747 | -57.0328 | -57.074 | -57.1518 | -56.8863 | -0.086976 | -0.027466 | -0.091553 | 0.60883 | 0.76447 | 0.16479 | 0.85144 | 0.25177 | -0.022889 | 0.027466 | -122.6486 | 0.077819 | 0.2655 | 0 | 0.28839 | 0.022889 | 0.6958 | 122.7631 | 0.10071 | 0.14191 | 122.8271 | 122.818 | 122.7402 | 122.7951 | -122.8546 | -122.7905 | 122.6761 | 0.11902 | 2.4124 | 1.2909
2263.1719 | 122.9919 | -57.1747 | 65.6342 | -0.11398 | 0.0014761 | 0.062453 | 0.070541 | 0.00016017 | 0.0019781 | 0.00414 | 0.001709 | 0.00067495 | 0.00042723 | 0.001128 | -0.0012925 | -0.0032301 | -0.00018806 | -54.7348 | 65.6204 | -57.225 | 65.4877 | -56.5933 | -57.0145 | -56.4148 | -55.9525 | 65.6616 | -57.2159 | -57.1106 | -57.1289 | -57.2296 | -56.9366 | -0.050354 | -0.013733 | -0.14648 | 0.58136 | 0.75989 | 0.16022 | 0.81024 | 0.21057 | -0.041198 | 0.027466 | -122.7448 | 0.045777 | 0.23804 | -0.054931 | 0.27923 | -0.013733 | 0.63171 | 122.7127 | 0.086975 | 0.10529 | 122.8455 | 122.8775 | 122.7951 | 122.8363 | -122.8592 | -122.85 | 122.6624 | 0.064087 | 2.4399 | 1.2222
2264.1719 | 122.9782 | -57.1747 | 65.6158 | -0.075836 | 0.00019446 | 0.062239 | 0.067336 | -0.0017624 | 0.0019781 | 0.003072 | -0.0043946 | 0.0011023 | -0.0010682 | 0.0054004 | -0.0034287 | -0.0038709 | -0.0029651 | -54.7256 | 65.625 | -57.2525 | 65.4968 | -56.5567 | -57.0053 | -56.4148 | -55.9479 | 65.6525 | -57.1838 | -57.1243 | -57.1243 | -57.2113 | -56.9321 | -0.077819 | 0.009155 | -0.11902 | 0.61798 | 0.75989 | 0.16937 | 0.83771 | 0.24719 | -0.009155 | 0.036621 | -122.7402 | 0.050354 | 0.24262 | -0.036621 | 0.25177 | -0.027466 | 0.6958 | 122.7493 | 0.059509 | 0.059509 | 122.8775 | 122.8363 | 122.7997 | 122.8271 | -122.8683 | -122.7997 | 122.6715 | 0.050354 | 2.449 | 1.2268
2265.1719 | 122.9965 | -57.1335 | 65.6296 | -0.15976 | 0.0021171 | 0.061812 | 0.068832 | 0.00016017 | 0.0030463 | 0.005849 | 0.001709 | -0.00060665 | 0.0014954 | -0.0033582 | 0.00041649 | -0.0066479 | -0.0014697 | -54.7302 | 65.6158 | -57.2433 | 65.5106 | -56.5521 | -57.0053 | -56.4102 | -55.925 | 65.6799 | -57.1884 | -57.0923 | -57.0877 | -57.193 | -56.9183 | -0.10986 | -0.013733 | -0.11902 | 0.58136 | 0.72327 | 0.12817 | 0.83313 | 0.23804 | -0.054932 | 0.050354 | -122.7219 | 0.045776 | 0.21515 | -0.059509 | 0.27008 | -0.004577 | 0.69122 | 122.7539 | 0.10071 | 0.096131 | 122.8592 | 122.8683 | 122.7493 | 122.8134 | -122.8729 | -122.818 | 122.644 | 0.041199 | 2.4033 | 1.2085
2266.1719 | 123.0423 | -57.1564 | 65.6296 | -0.12161 | 0.00083526 | 0.061385 | 0.068618 | 0.0016556 | 0.0013373 | 0.0060626 | -0.0043946 | -0.00082025 | 0.001068 | 0.001128 | -0.00043791 | -0.0038709 | -0.0016833 | -54.7302 | 65.5746 | -57.2525 | 65.5106 | -56.5567 | -56.9778 | -56.4056 | -55.9113 | 65.6204 | -57.1838 | -57.0831 | -57.074 | -57.193 | -56.9046 | -0.09613 | -0.054932 | -0.11902 | 0.59967 | 0.75073 | 0.17853 | 0.84686 | 0.27466 | -0.027466 | -0.009156 | -122.7127 | 0.082397 | 0.25177 | -0.036621 | 0.27924 | -0.009155 | 0.6958 | 122.7631 | 0.10986 | 0.10071 | 122.8271 | 122.8043 | 122.731 | 122.7768 | -122.8821 | -122.8134 | 122.6669 | 0.073242 | 2.4261 | 1.2451
2267.1719 | 123.0469 | -57.1609 | 65.6296 | -0.052948 | 0.00083526 | 0.06053 | 0.067123 | -0.0015488 | 0.0032599 | 0.0043536 | 0.001709 | -0.0012477 | 0.00064083 | -0.0050672 | -0.0015061 | -0.0040845 | -0.0063831 | -54.483 | 65.6708 | -57.1838 | 65.4648 | -56.6116 | -56.9733 | -56.4148 | -55.8975 | 65.6525 | -57.1976 | -57.1014 | -57.0969 | -57.1747 | -56.9046 | -0.022888 | 0.041198 | -0.16479 | 0.54932 | 0.74616 | 0.18768 | 0.76904 | 0.21057 | -0.036621 | 0.022888 | -122.731 | 0.064087 | 0.25635 | -0.013733 | 0.29297 | 0.022888 | 0.57221 | 122.6486 | 0.10071 | 0.096131 | 122.8546 | 122.85 | 122.8317 | 122.8134 | -122.8134 | -122.8271 | 122.6257 | 0.05951 | 2.6779 | 1.2634
2268.1719 | 123.056 | -57.1472 | 65.6342 | -0.060578 | -0.0010873 | 0.061385 | 0.067977 | 0.0037918 | 0.0024053 | 0.002431 | 0.041382 | 0.0011023 | -0.00064077 | -0.0027174 | -0.0012925 | -0.0053663 | -0.00018806 | -54.7394 | 65.6021 | -57.2433 | 65.4922 | -56.575 | -56.9962 | -56.3965 | -55.8792 | 65.6433 | -57.2021 | -57.0465 | -57.0602 | -57.1426 | -56.8863 | -0.09613 | -0.032043 | -0.14191 | 0.5722 | 0.75073 | 0.15106 | 0.84686 | 0.24719 | -0.054931 | 0.009156 | -122.6807 | 0.086975 | 0.26093 | 0.004578 | 0.31586 | 0.059509 | 0.66833 | 122.7356 | 0.14191 | 0.15564 | 122.8455 | 122.8455 | 122.7493 | 122.7905 | -122.8775 | -122.8363 | 122.6395 | 0.10071 | 2.4078 | 1.268
2269.1719 | 123.056 | -57.1609 | 65.5975 | -0.091095 | 0.00040806 | 0.062025 | 0.067336 | 0.0010148 | 0.0021917 | 0.0062762 | 0.016968 | 0.0021703 | 0.00021363 | -0.0042126 | -0.0025741 | -0.0070753 | 0.0025891 | -54.7302 | 65.5792 | -57.2342 | 65.5334 | -56.5063 | -56.9733 | -56.3828 | -55.8929 | 65.6387 | -57.1747 | -57.1243 | -57.2983 | -57.1335 | -56.813 | -0.073242 | -0.01831 | -0.064087 | 0.6546 | 0.7782 | 0.18768 | 0.85144 | 0.26093 | -0.013733 | 0.041199 | -122.7219 | -0.13733 | 0.3479 | 0.027466 | 0.36163 | 0.041199 | 0.72784 | 122.7676 | -0.1236 | 0.050354 | 122.8134 | 122.8134 | 122.7402 | 122.7997 | -122.8317 | -122.7722 | 122.6944 | 0.036621 | 2.4307 | 1.268
2270.1719 | 123.0515 | -57.1289 | 65.6387 | -0.068207 | -0.00066014 | 0.062025 | 0.069045 | -0.00026703 | 0.0019781 | 0.00414 | 0.023071 | -0.0014613 | -0.0014954 | -0.0037854 | -0.00065151 | -0.0051527 | 0.00066654 | -54.7302 | 65.6021 | -57.1976 | 65.5289 | -56.5201 | -56.9687 | -56.3599 | -55.8655 | 65.657 | -57.2021 | -57.0465 | -57.0694 | -57.1701 | -56.8771 | -0.068665 | -0.036621 | -0.10986 | 0.60883 | 0.76904 | 0.16022 | 0.83771 | 0.22888 | -0.073242 | 0.01831 | -122.6852 | 0.059509 | 0.25177 | -0.041199 | 0.32501 | 0.032043 | 0.67749 | 122.7264 | 0.13275 | 0.15564 | 122.7997 | 122.8592 | 122.731 | 122.7859 | -122.8363 | -122.8409 | 122.6578 | 0.082397 | 2.3987 | 1.2634
2271.1719 | 123.0652 | -57.1472 | 65.6158 | -0.075836 | -0.00044654 | 0.062666 | 0.066909 | -0.0015488 | 0.0030463 | 0.0081988 | -0.0074462 | 0.00024775 | 0.00042723 | 0.0026232 | -0.0027877 | -0.0049389 | -0.0027515 | -54.7348 | 65.6021 | -57.193 | 65.3915 | -56.4972 | -56.9641 | -56.456 | -55.9067 | 65.6296 | -57.2021 | -57.0786 | -57.074 | -57.1838 | -56.9092 | -0.045776 | -0.013733 | -0.2243 | 0.65002 | 0.69122 | 0.18311 | 0.737 | 0.22888 | -0.054931 | 0.013733 | -122.6944 | 0.073242 | 0.23804 | -0.036621 | 0.29297 | 0.01831 | 0.6958 | 122.5845 | 0.12817 | 0.1236 | 122.7951 | 122.8317 | 122.7493 | 122.7768 | -122.8088 | -122.818 | 122.5388 | 0.068665 | 2.4124 | 1.2405
2272.1719 | 123.0698 | -57.1472 | 65.625 | -0.037689 | 0.0012625 | 0.059676 | 0.069686 | -0.0021896 | 0.0028327 | 0.0028582 | 0.047485 | 0.0011023 | 0.0012818 | -0.0020764 | -0.0010787 | -0.0038709 | 0.0045117 | -54.7165 | 65.6158 | -57.2342 | 65.5151 | -56.5475 | -56.9595 | -56.4056 | -55.7602 | 65.7349 | -57.1793 | -57.1014 | -57.0786 | -57.1884 | -56.9046 | -0.086975 | -0.009155 | -0.10986 | 0.59967 | 0.74158 | 0.18768 | 0.82855 | 0.27466 | -0.032043 | 0.10986 | -122.7264 | 0.068665 | 0.24262 | -0.041199 | 0.27466 | -0.009156 | 0.68665 | 122.7493 | 0.10071 | 0.07782 | 122.85 | 122.9141 | 122.7631 | 122.8821 | -122.8592 | -122.8043 | 122.6624 | 0.045777 | 2.4307 | 1.387
2273.1719 | 122.9828 | -57.1655 | 65.5792 | -0.098725 | -1.9142e-05 | 0.061598 | 0.068618 | -0.0015488 | 0.00048269 | 0.0047808 | 0.032227 | -0.0021021 | 0.0025634 | -0.0050672 | -0.00043791 | -0.0036573 | 0.0034435 | -54.7256 | 65.5792 | -57.2525 | 65.5426 | -56.5338 | -56.9595 | -56.3782 | -55.8929 | 65.625 | -57.193 | -57.1335 | -56.7947 | -57.1472 | -57.0328 | -0.086975 | 0 | -0.036621 | 0.63171 | 0.78735 | 0.20599 | 0.87433 | 0.29297 | -0.027466 | 0.045776 | -122.7127 | 0.37079 | 0.13275 | 0.01831 | 0.16022 | 0.045776 | 0.71869 | 122.7951 | 0.39825 | 0.059509 | 122.8317 | 122.818 | 122.7448 | 122.7905 | -122.8317 | -122.7722 | 122.7081 | 0.032043 | 2.4399 | 1.2726
2274.1719 | 123.0652 | -57.1381 | 65.6158 | -0.068207 | -0.00087374 | 0.062453 | 0.066268 | -0.001976 | 0.0017645 | 0.0037128 | 0.0047608 | -0.0014613 | 0.00085443 | 0.0032642 | -0.0012925 | -0.0042981 | 2.554e-05 | -54.7028 | 65.5838 | -57.2479 | 65.506 | -56.5292 | -56.955 | -56.3873 | -55.8563 | 65.6479 | -57.1884 | -57.0511 | -57.0694 | -57.1518 | -56.9 | -0.10986 | -0.032044 | -0.10986 | 0.60883 | 0.75073 | 0.18311 | 0.8606 | 0.29297 | -0.050354 | 0.032043 | -122.6669 | 0.068665 | 0.23804 | -0.013732 | 0.28839 | 0.036622 | 0.71869 | 122.7539 | 0.11902 | 0.13733 | 122.8317 | 122.8363 | 122.7219 | 122.7859 | -122.8638 | -122.8043 | 122.644 | 0.086976 | 2.4353 | 1.2817
2275.1719 | 123.0515 | -57.1564 | 65.6067 | -0.12161 | -0.00023294 | 0.062453 | 0.069472 | -0.0013352 | 0.0013373 | 0.0039264 | 0.023071 | 0.0013159 | -0.0029908 | 0.0028368 | -0.0019333 | -0.0042981 | -0.00061526 | -54.7852 | 65.5838 | -57.2708 | 65.4648 | -56.6116 | -57.0282 | -56.4285 | -55.957 | 65.6342 | -57.2067 | -57.0877 | -57.106 | -57.2113 | -56.9183 | -0.11444 | -0.022888 | -0.14191 | 0.54474 | 0.72784 | 0.12817 | 0.84228 | 0.24261 | -0.050354 | 0.027466 | -122.6944 | 0.050354 | 0.23804 | -0.054932 | 0.28839 | -0.004578 | 0.65918 | 122.7356 | 0.10071 | 0.11902 | 122.8546 | 122.8409 | 122.7402 | 122.7905 | -122.8775 | -122.8134 | 122.6212 | 0.068664 | 2.3712 | 1.1993
2276.1719 | 123.0743 | -57.1381 | 65.6113 | -0.068207 | -0.00023294 | 0.060957 | 0.070327 | 0.001442 | 0.0032599 | 0.0049946 | 0.0047608 | 0.0011023 | -0.001709 | 0.0026232 | -0.0025741 | -0.0062207 | 0.0013073 | -54.7394 | 65.6067 | -57.2571 | 65.5014 | -56.5704 | -56.9962 | -56.3828 | -55.8746 | 65.625 | -57.1976 | -57.0602 | -57.0602 | -57.1609 | -56.8863 | -0.11902 | -0.004578 | -0.10986 | 0.56763 | 0.75531 | 0.14191 | 0.87433 | 0.26093 | -0.059509 | 0.013733 | -122.6715 | 0.07782 | 0.25177 | -0.022888 | 0.31128 | 0.036621 | 0.68664 | 122.7585 | 0.13733 | 0.13733 | 122.8638 | 122.8226 | 122.7448 | 122.7631 | -122.8683 | -122.8088 | 122.6395 | 0.07782 | 2.3987 | 1.2634
2277.1719 | 123.0927 | -57.1335 | 65.6067 | -0.075836 | 0.00019446 | 0.06288 | 0.06755 | -0.00026703 | 0.0047553 | 0.0043536 | 0.0047608 | -0.00017945 | 0.00064083 | -0.0027174 | -0.00043791 | -0.0045117 | 0.0040845 | -54.7394 | 65.5975 | -57.2067 | 65.4922 | -56.5704 | -57.019 | -56.4011 | -55.8975 | 65.6158 | -57.1976 | -57.0511 | -57.0511 | -57.1793 | -56.8817 | -0.073242 | -0.009155 | -0.11444 | 0.56305 | 0.73242 | 0.11444 | 0.80566 | 0.18768 | -0.064087 | 0.009156 | -122.6578 | 0.082398 | 0.25177 | -0.045776 | 0.31586 | 0.018311 | 0.63629 | 122.699 | 0.14649 | 0.14649 | 122.8043 | 122.8134 | 122.731 | 122.7493 | -122.8134 | -122.8043 | 122.6257 | 0.082398 | 2.3941 | 1.236
2278.1719 | 123.1247 | -57.1198 | 65.6845 | -0.12161 | -0.0010873 | 0.06053 | 0.070113 | -0.0030442 | 0.0034735 | 0.0032856 | 0.02002 | 0.0013159 | 0.0014954 | 0.0058276 | -0.0047103 | -0.0042981 | -0.0023243 | -54.7165 | 65.5792 | -57.2205 | 65.5334 | -56.5292 | -56.9504 | -56.369 | -55.8563 | 65.6342 | -57.1701 | -57.0648 | -57.0648 | -57.1564 | -56.781 | -0.10071 | -0.10529 | -0.15106 | 0.59052 | 0.75073 | 0.16937 | 0.85144 | 0.27008 | -0.050354 | -0.050354 | -122.7493 | 0.054932 | 0.33875 | -0.036621 | 0.3891 | 0.013733 | 0.69122 | 122.7539 | 0.10529 | 0.10529 | 122.7997 | 122.8043 | 122.699 | 122.7539 | -122.905 | -122.8546 | 122.6532 | 0.054932 | 2.4033 | 1.2634
2279.1719 | 123.0789 | -57.1701 | 65.6158 | -0.10635 | -0.00066014 | 0.061812 | 0.067336 | -0.003685 | 0.0030463 | 0.0062762 | 0.02002 | 0.00024775 | 0.001709 | 0.00091422 | -0.0034287 | -0.0047253 | -0.0021107 | -54.7256 | 65.5701 | -57.2205 | 65.538 | -56.5338 | -56.9641 | -56.3828 | -55.8701 | 65.625 | -57.1747 | -57.0236 | -57.0786 | -57.1609 | -56.8771 | -0.050354 | -0.045777 | -0.07782 | 0.63629 | 0.78735 | 0.20599 | 0.83771 | 0.25635 | -0.004578 | 0.009155 | -122.6395 | 0.091553 | 0.29297 | 0.009155 | 0.29755 | 0.013733 | 0.68665 | 122.7585 | 0.096131 | 0.15106 | 122.7905 | 122.7997 | 122.7402 | 122.7951 | -122.8363 | -122.7905 | 122.7081 | 0.14648 | 2.4445 | 1.3
2280.1719 | 123.0881 | -57.1518 | 65.625 | -0.091095 | 0.0021171 | 0.061171 | 0.067336 | -0.0015488 | 0.0011237 | 0.002431 | -0.0043946 | -0.0018885 | -0.0012818 | 5.9824e-05 | -0.0023605 | -0.0049389 | -0.0029651 | -54.7394 | 65.6067 | -57.225 | 65.5014 | -56.5521 | -56.9595 | -56.3782 | -55.8838 | 65.6158 | -57.1976 | -57.0374 | -57.0465 | -57.1472 | -56.8817 | -0.073243 | -0.018311 | -0.1236 | 0.59967 | 0.77362 | 0.19226 | 0.84686 | 0.2655 | -0.045777 | -0.009155 | -122.6624 | 0.10529 | 0.27008 | 0.004577 | 0.31586 | 0.050354 | 0.67291 | 122.7264 | 0.15106 | 0.16022 | 122.8317 | 122.8134 | 122.7585 | 122.7676 | -122.85 | -122.8226 | 122.6532 | 0.11444 | 2.4124 | 1.268
2281.1719 | 123.0606 | -57.1564 | 65.6204 | -0.091095 | 0.00019446 | 0.061598 | 0.068832 | -5.343e-05 | 0.0017645 | 0.0039264 | -0.010498 | 0.00067495 | -0.0010682 | -0.00036738 | -0.0027877 | -0.0049389 | -0.0023243 | -54.744 | 65.5746 | -57.2571 | 65.5197 | -56.5659 | -56.9916 | -56.4011 | -55.8884 | 65.6387 | -57.2159 | -57.0419 | -57.0648 | -57.1518 | -56.8909 | -0.10071 | -0.045776 | -0.10071 | 0.59051 | 0.75531 | 0.16479 | 0.85602 | 0.2655 | -0.059509 | 0.018311 | -122.6624 | 0.091553 | 0.2655 | 0.004578 | 0.32501 | 0.064087 | 0.69122 | 122.7768 | 0.15106 | 0.17395 | 122.8317 | 122.8546 | 122.731 | 122.7951 | -122.8775 | -122.8363 | 122.6761 | 0.11444 | 2.4124 | 1.268
2282.1719 | 123.0103 | -57.1609 | 65.5975 | -0.091095 | 0.0019035 | 0.061598 | 0.070968 | 0.0016556 | 0.0015509 | 0.0043536 | -0.010498 | 0.0011023 | 0.00021363 | -0.00079478 | -0.0027877 | -0.0034437 | -0.0021107 | -54.7897 | 65.5792 | -57.2662 | 65.4373 | -56.6528 | -57.0786 | -56.488 | -56.0165 | 65.6342 | -57.2296 | -57.1289 | -57.1518 | -57.2433 | -56.9458 | -0.10529 | -0.01831 | -0.16022 | 0.50812 | 0.67291 | 0.082398 | 0.7782 | 0.18768 | -0.068664 | 0.036621 | -122.7264 | 0.009156 | 0.21515 | -0.082397 | 0.28381 | -0.013733 | 0.6134 | 122.7036 | 0.07782 | 0.10071 | 122.8455 | 122.8638 | 122.7402 | 122.7951 | -122.8638 | -122.8271 | 122.5983 | 0.032044 | 2.3712 | 1.1444
2283.1719 | 123.0286 | -57.1655 | 65.6387 | -0.11398 | -0.00023294 | 0.063307 | 0.070541 | -0.0015488 | 0.0026191 | 0.0028582 | -0.022705 | 0.0019567 | 2.8e-08 | -0.0048536 | -0.0027877 | -0.0055799 | -0.0025379 | -54.7897 | 65.6067 | -57.2342 | 65.4373 | -56.6528 | -57.0511 | -56.4697 | -55.9891 | 65.6204 | -57.2342 | -57.1243 | -57.1381 | -57.2296 | -56.9321 | -0.068665 | -0.032044 | -0.20142 | 0.5127 | 0.6958 | 0.11444 | 0.76447 | 0.18311 | -0.068665 | -0.018311 | -122.7631 | 0.027465 | 0.23346 | -0.064087 | 0.30212 | 0.004578 | 0.58136 | 122.6715 | 0.09613 | 0.10986 | 122.8409 | 122.8546 | 122.7722 | 122.7859 | -122.8729 | -122.8729 | 122.6028 | 0.041198 | 2.3758 | 1.1765
2284.1719 | 123.0652 | -57.1564 | 65.593 | -0.1445 | -0.00023294 | 0.060744 | 0.069259 | -0.0030442 | 0.0019781 | 0.0064898 | -0.01355 | -0.00017945 | 2.8e-08 | -0.0018628 | -0.0012925 | -0.0036573 | -0.0040333 | -54.7485 | 65.6113 | -57.2662 | 65.4785 | -56.6071 | -57.0282 | -56.4285 | -55.9525 | 65.6387 | -57.2021 | -57.0648 | -57.0877 | -57.1747 | -56.9138 | -0.10986 | 0.01831 | -0.11444 | 0.54932 | 0.72784 | 0.12817 | 0.83771 | 0.23804 | -0.045776 | 0.045776 | -122.6578 | 0.068664 | 0.24262 | -0.018311 | 0.28839 | 0.027465 | 0.65918 | 122.7448 | 0.11444 | 0.13733 | 122.8775 | 122.8409 | 122.7676 | 122.7951 | -122.8592 | -122.7951 | 122.6349 | 0.091553 | 2.4078 | 1.2039
2285.1719 | 123.0515 | -57.1655 | 65.6067 | -0.10635 | -0.00066014 | 0.061598 | 0.067123 | -0.0028304 | 0.0051825 | 0.00414 | 0.0078126 | 3.4148e-05 | 0.00085443 | 0.0041186 | -0.00065151 | -0.0036573 | 0.00023934 | -54.7623 | 65.6113 | -57.2479 | 65.4602 | -56.6391 | -57.0419 | -56.4423 | -55.9708 | 65.6525 | -57.2205 | -57.0831 | -57.1014 | -57.1976 | -56.9275 | -0.082398 | 0.004578 | -0.14648 | 0.52643 | 0.72327 | 0.1236 | 0.80566 | 0.20599 | -0.054932 | 0.045777 | -122.6898 | 0.064087 | 0.23804 | -0.032044 | 0.29297 | 0.022888 | 0.60883 | 122.7081 | 0.11902 | 0.13733 | 122.8592 | 122.8729 | 122.7768 | 122.818 | -122.8546 | -122.8271 | 122.6257 | 0.082397 | 2.4033 | 1.1948
2286.1719 | 123.0606 | -57.1747 | 65.6204 | -0.060578 | 0.0016899 | 0.063307 | 0.068618 | 0.0016556 | 0.0030463 | 0.0071308 | -0.0043946 | 0.0015295 | 2.8e-08 | -0.0010084 | -0.0027877 | -0.0045117 | -0.0014697 | -54.776 | 65.593 | -57.2617 | 65.4602 | -56.6437 | -57.0602 | -56.4606 | -55.9708 | 65.6342 | -57.2205 | -57.0831 | -57.0877 | -57.2021 | -56.9183 | -0.086975 | -0.027465 | -0.16022 | 0.53101 | 0.71411 | 0.11444 | 0.80109 | 0.20142 | -0.045776 | 0.013733 | -122.7036 | 0.086975 | 0.25635 | -0.027465 | 0.30212 | 0.018311 | 0.61798 | 122.7219 | 0.13275 | 0.13733 | 122.8546 | 122.8546 | 122.7676 | 122.8088 | -122.8821 | -122.8409 | 122.6349 | 0.091553 | 2.3987 | 1.2039
2287.1719 | 123.0377 | -57.1838 | 65.5975 | -0.091095 | -0.00044654 | 0.060744 | 0.069472 | 0.00037377 | 0.0026191 | 0.0026446 | -0.010498 | 0.00024775 | 0.00064083 | -0.0054944 | -0.0015061 | -0.0036573 | 0.00088014 | -54.7623 | 65.6021 | -57.2525 | 65.451 | -56.6345 | -57.0648 | -56.4423 | -55.9845 | 65.6296 | -57.2205 | -57.106 | -57.1243 | -57.2067 | -56.9138 | -0.068664 | 0.004578 | -0.14648 | 0.54932 | 0.74158 | 0.11902 | 0.81024 | 0.18768 | -0.036621 | 0.032044 | -122.7036 | 0.059509 | 0.27008 | -0.022888 | 0.3067 | 0.013733 | 0.61798 | 122.7036 | 0.09613 | 0.11444 | 122.8546 | 122.85 | 122.786 | 122.8134 | -122.85 | -122.818 | 122.6349 | 0.07782 | 2.4216 | 1.1993
2288.1719 | 123.056 | -57.1518 | 65.6113 | -0.091095 | -0.00044654 | 0.059889 | 0.068618 | 0.0018692 | 0.00026909 | 0.00414 | 0.0047608 | 0.0011023 | 0.0029906 | 0.00070062 | -0.0025741 | -0.0047253 | -0.0010425 | -54.7256 | 65.5884 | -57.2433 | 65.4922 | -56.6071 | -57.019 | -56.4102 | -55.9341 | 65.6296 | -57.2159 | -57.0694 | -57.0831 | -57.1747 | -56.8954 | -0.091553 | -0.022888 | -0.11902 | 0.54474 | 0.74158 | 0.13275 | 0.83313 | 0.2243 | -0.064087 | 0.018311 | -122.6807 | 0.068664 | 0.25635 | -0.022889 | 0.32043 | 0.041198 | 0.63629 | 122.7356 | 0.13275 | 0.14648 | 122.8317 | 122.8455 | 122.7402 | 122.7814 | -122.8546 | -122.8271 | 122.644 | 0.082397 | 2.4261 | 1.2177
2289.1719 | 123.0148 | -57.2113 | 65.6067 | -0.083466 | 0.0014761 | 0.060744 | 0.0699 | 0.001442 | 0.0017645 | 0.0077716 | -0.0074462 | 0.00024775 | 0.00042723 | 0.00048702 | -0.00065151 | -0.0032301 | 0.0019483 | -54.7989 | 65.5609 | -57.2571 | 65.4282 | -56.6483 | -57.0831 | -56.4835 | -56.0074 | 65.6433 | -57.2159 | -57.1152 | -57.1426 | -57.2388 | -56.9366 | -0.045776 | -0.045776 | -0.17853 | 0.56305 | 0.72784 | 0.12817 | 0.77362 | 0.17395 | -0.004577 | 0.036622 | -122.7219 | 0.068665 | 0.27466 | -0.027466 | 0.27923 | -0.022889 | 0.60883 | 122.6852 | 0.073242 | 0.10071 | 122.818 | 122.8592 | 122.7722 | 122.8546 | -122.8638 | -122.8226 | 122.6395 | 0.096131 | 2.4124 | 1.2039
2290.1719 | 123.0469 | -57.1518 | 65.625 | -0.052948 | -0.0017281 | 0.062666 | 0.067977 | -0.0017624 | 0.00069649 | 0.005849 | -0.0074462 | 0.0015295 | 0.0014954 | -0.0018628 | -0.0025741 | -0.0030163 | 0.00023934 | -54.7485 | 65.5975 | -57.2571 | 65.4694 | -56.6162 | -57.0328 | -56.4423 | -55.9662 | 65.6479 | -57.2113 | -57.0831 | -57.0923 | -57.1838 | -56.9046 | -0.10529 | -0.027466 | -0.15564 | 0.53558 | 0.70953 | 0.11902 | 0.81482 | 0.2243 | -0.05951 | 0.022888 | -122.7081 | 0.059509 | 0.24719 | -0.032044 | 0.3067 | 0.027466 | 0.64087 | 122.7264 | 0.11902 | 0.12817 | 122.8546 | 122.8592 | 122.7493 | 122.7997 | -122.8821 | -122.8363 | 122.6212 | 0.068664 | 2.4033 | 1.1856
2291.1719 | 123.0835 | -57.1518 | 65.6113 | -0.045319 | 0.00040806 | 0.060316 | 0.067763 | -0.0015488 | 0.0013373 | 0.0032856 | -0.019653 | 0.00024775 | -0.00042717 | -0.0018628 | -0.0015061 | -0.0055799 | 0.0019483 | -54.7211 | 65.6067 | -57.2525 | 65.5197 | -56.5475 | -56.9778 | -56.3965 | -55.8838 | 65.6342 | -57.193 | -57.0328 | -57.0419 | -57.1289 | -56.8726 | -0.10071 | -0.004578 | -0.091553 | 0.60425 | 0.75531 | 0.17395 | 0.85602 | 0.27466 | -0.041199 | 0.022888 | -122.644 | 0.10986 | 0.27923 | 0.022888 | 0.32043 | 0.064087 | 0.70496 | 122.7722 | 0.15106 | 0.16022 | 122.8592 | 122.8271 | 122.7585 | 122.7859 | -122.8638 | -122.8043 | 122.6715 | 0.11902 | 2.4307 | 1.268
2292.1719 | 123.0606 | -57.1472 | 65.6158 | -0.10635 | -0.0015145 | 0.061598 | 0.067977 | -0.0013352 | 0.0028327 | 0.0056354 | 0.0078126 | 0.0015295 | -0.00042717 | -0.0016492 | -0.0034287 | -0.0047253 | 0.0023755 | -54.7394 | 65.5975 | -57.2342 | 65.5197 | -56.5704 | -57.0053 | -56.4102 | -55.8792 | 65.6433 | -57.1884 | -57.0419 | -57.0557 | -57.1564 | -56.8771 | -0.086975 | -0.018311 | -0.096131 | 0.57678 | 0.737 | 0.14191 | 0.82397 | 0.22888 | -0.041199 | 0.027466 | -122.6578 | 0.091553 | 0.27008 | -0.009155 | 0.31128 | 0.032044 | 0.66376 | 122.7539 | 0.13275 | 0.14648 | 122.8317 | 122.8317 | 122.7448 | 122.7905 | -122.85 | -122.8043 | 122.6669 | 0.10529 | 2.4078 | 1.268
2293.1719 | 123.0835 | -57.1655 | 65.6204 | -0.083466 | 0.00083526 | 0.060744 | 0.068832 | 0.00058737 | 0.0013373 | 0.0017902 | 0.023071 | 0.00046135 | 0.0019226 | 0.0017688 | -0.0034287 | -0.0040845 | -0.00082886 | -54.7348 | 65.593 | -57.2021 | 65.5014 | -56.575 | -56.9962 | -56.3965 | -55.8838 | 65.6387 | -57.1747 | -57.0511 | -57.0602 | -57.1793 | -56.8863 | -0.036621 | -0.027465 | -0.11902 | 0.59051 | 0.76904 | 0.16937 | 0.80566 | 0.20599 | -0.009156 | 0.018311 | -122.6715 | 0.10528 | 0.27923 | -0.013733 | 0.28839 | -0.004577 | 0.62714 | 122.7036 | 0.11444 | 0.1236 | 122.7951 | 122.8134 | 122.7585 | 122.8043 | -122.8226 | -122.7951 | 122.6669 | 0.11444 | 2.4307 | 1.2817
2294.1719 | 123.0652 | -57.1564 | 65.625 | -0.12161 | 0.00062166 | 0.06053 | 0.070754 | -0.0011214 | -0.00015811 | 0.0054218 | -0.01355 | 0.00088875 | 0.001068 | -0.0035718 | -0.00065151 | -0.0042981 | 0.0017345 | -54.7256 | 65.6204 | -57.2159 | 65.5106 | -56.5659 | -57.0007 | -56.4056 | -55.9067 | 65.6158 | -57.193 | -57.0419 | -57.0694 | -57.1518 | -56.8909 | -0.059509 | -0.004578 | -0.11444 | 0.59051 | 0.75073 | 0.15564 | 0.81024 | 0.21515 | -0.036621 | -0.009155 | -122.6669 | 0.086975 | 0.2655 | 0.004578 | 0.30212 | 0.041199 | 0.65002 | 122.7264 | 0.1236 | 0.15106 | 122.8363 | 122.8088 | 122.7768 | 122.7722 | -122.8409 | -122.818 | 122.6669 | 0.11444 | 2.4307 | 1.2497
2295.1719 | 123.0835 | -57.1701 | 65.6204 | -0.098725 | -0.0017281 | 0.060744 | 0.068618 | -0.0030442 | 0.0026191 | 0.0043536 | 0.0078126 | 3.4148e-05 | 0.0012818 | -0.00058098 | -0.0017197 | -0.0036573 | -0.0021107 | -54.7394 | 65.5884 | -57.225 | 65.4877 | -56.6025 | -57.019 | -56.4285 | -55.9158 | 65.6387 | -57.2021 | -57.0602 | -57.0648 | -57.1381 | -56.8726 | -0.054932 | -0.032043 | -0.13275 | 0.56763 | 0.74158 | 0.15106 | 0.79651 | 0.20599 | -0.032043 | 0.018311 | -122.6807 | 0.10529 | 0.29755 | 0.032043 | 0.32959 | 0.064086 | 0.62256 | 122.7127 | 0.13733 | 0.14191 | 122.8134 | 122.8409 | 122.7585 | 122.8088 | -122.8455 | -122.8226 | 122.6578 | 0.10986 | 2.4307 | 1.2543
2296.1719 | 123.0011 | -57.1793 | 65.5975 | -0.098725 | 0.00019446 | 0.063521 | 0.069259 | 0.0012284 | 0.0036871 | 0.0032856 | -0.0074462 | 0.00024775 | 0.00064083 | 0.0017688 | -0.0015061 | -0.0028027 | 0.0017345 | -54.7668 | 65.5884 | -57.2433 | 65.451 | -56.662 | -57.0786 | -56.4697 | -56.0074 | 65.625 | -57.2159 | -57.1289 | -57.1564 | -57.2479 | -56.9504 | -0.064087 | -0.009155 | -0.14648 | 0.51727 | 0.70953 | 0.10071 | 0.77362 | 0.16479 | -0.036621 | 0.027466 | -122.7264 | 0.022888 | 0.22888 | -0.068665 | 0.2655 | -0.032044 | 0.58136 | 122.6944 | 0.059509 | 0.086975 | 122.8317 | 122.8409 | 122.7676 | 122.8043 | -122.8409 | -122.8134 | 122.6303 | 0.050354 | 2.4124 | 1.1719
2297.1719 | 123.0652 | -57.1655 | 65.6158 | -0.083466 | 0.0025443 | 0.060744 | 0.069472 | -0.00026703 | 0.0013373 | 0.002431 | 0.02002 | 0.00046135 | -0.00085457 | 0.0036914 | -0.00043791 | -0.0036573 | -0.00082886 | -54.7348 | 65.6158 | -57.2525 | 65.4922 | -56.6071 | -57.0328 | -56.4239 | -55.9341 | 65.6204 | -57.2067 | -57.0557 | -57.0694 | -57.1701 | -56.8771 | -0.086975 | 0 | -0.1236 | 0.55847 | 0.74158 | 0.13275 | 0.82855 | 0.21973 | -0.041199 | 0.004577 | -122.6715 | 0.09613 | 0.28839 | -0.004578 | 0.32959 | 0.036621 | 0.64545 | 122.7448 | 0.13733 | 0.15106 | 122.8683 | 122.8271 | 122.7814 | 122.7859 | -122.8683 | -122.8226 | 122.6578 | 0.10986 | 2.4307 | 1.2314
2298.1719 | 122.9782 | -57.1793 | 65.6433 | -0.045319 | 0.0021171 | 0.061812 | 0.070968 | 0.00016017 | 0.0017645 | 0.0052082 | -0.095947 | 0.0011023 | 0.0012818 | 0.0077502 | -0.0025741 | -0.0025891 | -0.0021107 | -54.7394 | 65.657 | -57.2433 | 65.4419 | -56.6391 | -57.0648 | -56.4926 | -55.9845 | 65.6845 | -57.2205 | -57.1152 | -57.1564 | -57.2617 | -56.9504 | -0.064087 | 0.013732 | -0.20142 | 0.54016 | 0.68664 | 0.11444 | 0.75073 | 0.17853 | -0.041199 | 0.041198 | -122.7585 | 0.022888 | 0.22888 | -0.082398 | 0.27008 | -0.041199 | 0.60425 | 122.6852 | 0.064087 | 0.10529 | 122.9004 | 122.905 | 122.8363 | 122.8638 | -122.8867 | -122.8638 | 122.6212 | 0.064087 | 2.4399 | 1.1948
2299.1719 | 123.0469 | -57.1518 | 65.6342 | -0.075836 | 0.00040806 | 0.062453 | 0.070754 | 0.00251 | 0.0015509 | 0.0067036 | -0.0013428 | -0.00039305 | -0.00085457 | 0.0032642 | -0.00043791 | -0.0066479 | -0.0010425 | -54.744 | 65.5975 | -57.2342 | 65.4739 | -56.6025 | -57.0282 | -56.4331 | -55.9158 | 65.625 | -57.1976 | -57.0511 | -57.0557 | -57.1609 | -56.8954 | -0.082398 | -0.036621 | -0.16022 | 0.54932 | 0.71869 | 0.1236 | 0.80109 | 0.20599 | -0.045777 | -0.009155 | -122.6852 | 0.09613 | 0.25635 | -0.009156 | 0.30212 | 0.036621 | 0.63171 | 122.7081 | 0.14191 | 0.14649 | 122.8317 | 122.8226 | 122.7493 | 122.7768 | -122.8683 | -122.8317 | 122.6257 | 0.10071 | 2.4078 | 1.236
2300.1719 | 123.0789 | -57.1518 | 65.6067 | -0.075836 | 0.00083526 | 0.06053 | 0.067763 | -0.00090783 | -0.00058531 | 0.005849 | 0.016968 | 0.00088875 | 0.00085443 | -0.0050672 | -0.0017197 | -0.0055799 | 0.0034435 | -54.7348 | 65.6158 | -57.2433 | 65.4877 | -56.5887 | -57.0282 | -56.4423 | -55.9387 | 65.6387 | -57.1884 | -57.0511 | -57.074 | -57.1655 | -56.9 | -0.091553 | 0.009156 | -0.11902 | 0.56305 | 0.70953 | 0.1236 | 0.80109 | 0.21515 | -0.036622 | 0.032044 | -122.6578 | 0.077819 | 0.25177 | -0.013733 | 0.28839 | 0.022889 | 0.6546 | 122.731 | 0.11444 | 0.13733 | 122.8592 | 122.8271 | 122.7676 | 122.7905 | -122.85 | -122.7951 | 122.6395 | 0.10071 | 2.417 | 1.2131
2301.1719 | 123.056 | -57.1609 | 65.5884 | -0.098725 | -0.0019417 | 0.059676 | 0.069686 | -0.00069423 | 0.0028327 | 0.00414 | 0.029175 | 0.0023839 | -0.0010682 | -0.0037854 | -0.0023605 | -0.0040845 | 0.0042981 | -54.7394 | 65.6067 | -57.2296 | 65.4877 | -56.6025 | -57.0282 | -56.4377 | -55.9387 | 65.6754 | -57.2159 | -57.0465 | -57.0786 | -57.1564 | -56.9092 | -0.068664 | 0.01831 | -0.10071 | 0.55847 | 0.72327 | 0.13275 | 0.79193 | 0.20142 | -0.054931 | 0.086975 | -122.6349 | 0.082398 | 0.25177 | 0.004578 | 0.3067 | 0.059509 | 0.62714 | 122.7173 | 0.13733 | 0.16937 | 122.8363 | 122.8912 | 122.7676 | 122.8363 | -122.818 | -122.8043 | 122.6486 | 0.11444 | 2.4216 | 1.2222
2302.1719 | 123.0148 | -57.1701 | 65.6158 | -0.068207 | -0.00087374 | 0.062453 | 0.069259 | -0.0038986 | -0.00015811 | 0.0054218 | -0.0013428 | 0.00088875 | 0.0021362 | -0.00036738 | 0.00041649 | -0.0038709 | 0.00066654 | -54.657 | 65.625 | -57.2205 | 65.4465 | -56.6345 | -57.0877 | -56.4651 | -55.9799 | 65.6479 | -57.1976 | -57.0969 | -57.1198 | -57.2296 | -56.9275 | -0.050354 | 0.009155 | -0.16937 | 0.53558 | 0.70496 | 0.082397 | 0.75531 | 0.13275 | -0.027466 | 0.032043 | -122.7127 | 0.050354 | 0.24262 | -0.059509 | 0.27008 | -0.032043 | 0.58594 | 122.6669 | 0.07782 | 0.10071 | 122.8455 | 122.8455 | 122.7951 | 122.818 | -122.8363 | -122.8134 | 122.6166 | 0.073242 | 2.5131 | 1.1902
2303.1719 | 122.9782 | -57.1838 | 65.6799 | -0.014801 | -0.0021555 | 0.060957 | 0.070327 | -0.001976 | 0.0028327 | 0.0049946 | -0.077637 | 0.00067495 | 0.0014954 | 0.0026232 | -0.00086511 | -0.0030163 | -0.0021107 | -54.7531 | 65.6525 | -57.2662 | 65.419 | -56.7032 | -57.0694 | -56.5247 | -56.044 | 65.6982 | -57.2021 | -57.1335 | -57.1518 | -57.28 | -56.955 | -0.082397 | -0.027466 | -0.26093 | 0.48065 | 0.65918 | 0.11444 | 0.74158 | 0.19684 | -0.01831 | 0.01831 | -122.8134 | 0.032044 | 0.22888 | -0.09613 | 0.24719 | -0.07782 | 0.56305 | 122.6852 | 0.050354 | 0.068664 | 122.9187 | 122.9004 | 122.8363 | 122.8821 | -122.9462 | -122.8821 | 122.6028 | 0.050354 | 2.4307 | 1.1398
2304.1719 | 123.0469 | -57.1198 | 65.6433 | -0.075836 | -0.00087374 | 0.061598 | 0.069686 | 0.00058737 | 0.0026191 | 0.0056354 | 0.023071 | 0.00088875 | 0.00064083 | -0.001222 | -0.0015061 | -0.0047253 | -0.00061526 | -54.6936 | 65.6113 | -57.2296 | 65.5334 | -56.5109 | -56.9458 | -56.369 | -55.8746 | 65.657 | -57.193 | -57.0419 | -57.074 | -56.8314 | -56.6574 | -0.10986 | -0.032044 | -0.10986 | 0.60883 | 0.75073 | 0.17395 | 0.86059 | 0.28381 | -0.073242 | 0.013732 | -122.6852 | 0.045776 | 0.46234 | 0.28839 | 0.53558 | 0.36163 | 0.71869 | 122.7631 | 0.11902 | 0.15106 | 122.8409 | 122.85 | 122.731 | 122.7768 | -122.8729 | -122.8363 | 122.6532 | 0.07782 | 2.4261 | 1.2451
2305.1719 | 122.9507 | -57.1426 | 65.6342 | -0.075836 | 0.00019446 | 0.062025 | 0.06755 | -0.0021896 | 5.5488e-05 | 0.0056354 | 0.013916 | -0.00082025 | 0.0019226 | -0.0061352 | -0.0012925 | -0.0028027 | -0.0031787 | -54.6844 | 65.6204 | -57.2113 | 65.5243 | -56.5109 | -56.9412 | -56.3782 | -55.8975 | 65.6525 | -57.1838 | -57.1106 | -56.7947 | -56.8954 | -56.7856 | -0.068665 | -0.013733 | -0.10986 | 0.63171 | 0.76447 | 0.20142 | 0.83313 | 0.27008 | -0.041199 | 0.018311 | -122.7448 | 0.3479 | 0.35706 | 0.24719 | 0.39825 | 0.28839 | 0.70038 | 122.7356 | 0.3891 | 0.073242 | 122.8317 | 122.8363 | 122.7631 | 122.7951 | -122.8455 | -122.818 | 122.6669 | 0.032043 | 2.4582 | 1.2451
2306.1719 | 123.0789 | -57.1472 | 65.6204 | -0.091095 | 0.00062166 | 0.061598 | 0.070327 | 0.0012284 | 0.0024053 | 0.0056354 | 0.0078126 | 0.00024775 | 0.00021363 | -0.003999 | -0.0025741 | -0.0075025 | 0.0051525 | -54.6982 | 65.5884 | -57.193 | 65.5518 | -56.5201 | -56.9504 | -56.3736 | -55.8655 | 65.6387 | -57.1655 | -56.9183 | -56.9458 | -57.4768 | -57.0786 | -0.045776 | -0.032043 | -0.068664 | 0.62714 | 0.77362 | 0.19684 | 0.8194 | 0.24262 | -0.01831 | 0.018311 | -122.5388 | 0.20142 | 0.068665 | -0.32959 | 0.086975 | -0.31128 | 0.67291 | 122.7448 | 0.21973 | 0.24719 | 122.7814 | 122.8043 | 122.7356 | 122.7859 | -122.8134 | -122.7859 | 122.699 | 0.22888 | 2.449 | 1.2817
2307.1719 | 123.0972 | -57.1564 | 65.6113 | -0.1445 | -1.9142e-05 | 0.062239 | 0.069045 | -0.001976 | 0.0017645 | 0.0043536 | 0.035278 | 0.0013159 | 0.0029906 | 0.0013416 | -0.0053513 | -0.0072889 | -0.0012561 | -54.6753 | 65.6158 | -57.225 | 65.538 | -56.5201 | -56.9595 | -56.3965 | -55.8884 | 65.6479 | -57.1655 | -56.955 | -57.3624 | -57.2433 | -56.8542 | -0.068665 | 0.004578 | -0.073242 | 0.63629 | 0.75989 | 0.19684 | 0.82855 | 0.2655 | -0.009155 | 0.036621 | -122.5662 | -0.20599 | 0.30212 | -0.086975 | 0.31128 | -0.07782 | 0.70496 | 122.7631 | -0.19684 | 0.21057 | 122.8409 | 122.8134 | 122.7722 | 122.8043 | -122.8363 | -122.7768 | 122.6944 | 0.20142 | 2.4811 | 1.268
2308.1719 | 122.9324 | -57.193 | 65.6387 | -0.037689 | 0.00040806 | 0.060957 | 0.072036 | -0.00090783 | -0.0018671 | 0.0060626 | -0.095947 | 3.4148e-05 | -0.00064077 | 0.0026232 | -0.0019333 | -0.0036573 | -0.00018806 | -54.7668 | 65.6296 | -57.28 | 65.4236 | -56.6986 | -57.1243 | -56.5475 | -56.0303 | 65.6662 | -57.2388 | -57.1701 | -57.2159 | -57.3395 | -57.0007 | -0.086975 | -0.009155 | -0.21515 | 0.49439 | 0.64545 | 0.068664 | 0.73242 | 0.15564 | -0.045777 | 0.027466 | -122.8088 | -0.022888 | 0.19226 | -0.14648 | 0.23804 | -0.10071 | 0.58136 | 122.7036 | 0.022889 | 0.068665 | 122.9095 | 122.905 | 122.8226 | 122.8592 | -122.9187 | -122.8775 | 122.6166 | 0.022888 | 2.4261 | 1.1627
2309.1719 | 123.0927 | -57.1472 | 65.6113 | -0.075836 | 0.00040806 | 0.062666 | 0.069259 | 0.001442 | 0.0041143 | -0.00034601 | 0.044434 | 0.00067495 | 0.00064083 | -0.00229 | -0.0010787 | -0.0034437 | -0.0053149 | -54.7256 | 65.6158 | -57.2205 | 65.4968 | -56.5887 | -56.9916 | -56.4102 | -55.9204 | 65.6433 | -57.1701 | -57.0374 | -57.0602 | -57.1564 | -56.868 | -0.073242 | 0.004578 | -0.11444 | 0.55847 | 0.737 | 0.15564 | 0.81024 | 0.22888 | -0.022888 | 0.032044 | -122.6486 | 0.086975 | 0.27924 | -0.009155 | 0.30212 | 0.013733 | 0.63171 | 122.7173 | 0.10986 | 0.13275 | 122.8363 | 122.8134 | 122.7631 | 122.7905 | -122.8317 | -122.7814 | 122.644 | 0.10986 | 2.4216 | 1.2268
2310.1719 | 123.0743 | -57.1701 | 65.6387 | -0.098725 | 0.00083526 | 0.062025 | 0.069472 | -0.00090783 | 0.0011237 | 0.0060626 | 0.013916 | 0.0013159 | -0.00021357 | 0.0013416 | -0.0019333 | -0.0042981 | -0.0010425 | -54.7302 | 65.625 | -57.2159 | 65.4922 | -56.5796 | -57.0053 | -56.4102 | -55.8792 | 65.6387 | -57.1976 | -57.0419 | -57.0465 | -57.1655 | -56.8817 | -0.045776 | -0.013733 | -0.14648 | 0.59051 | 0.75989 | 0.16479 | 0.80566 | 0.21057 | -0.027466 | 0 | -122.6807 | 0.1236 | 0.28839 | 0.004578 | 0.31586 | 0.032044 | 0.63629 | 122.7081 | 0.15106 | 0.15564 | 122.8409 | 122.8363 | 122.7951 | 122.8088 | -122.8546 | -122.8363 | 122.6624 | 0.12817 | 2.4399 | 1.2909
2311.1719 | 122.9828 | -57.1838 | 65.6433 | -0.26657 | -0.0019417 | 0.063094 | 0.070327 | 0.00080117 | 0.0026191 | 0.00414 | -0.10205 | 0.0013159 | -0.00021357 | -0.002931 | -0.0040695 | -0.0042981 | -0.0027515 | -54.6844 | 65.6158 | -57.2617 | 65.451 | -56.6345 | -57.0969 | -56.5155 | -55.9937 | 65.6616 | -57.2113 | -57.1243 | -57.1793 | -57.3074 | -56.9824 | -0.07782 | -0.027466 | -0.19226 | 0.54932 | 0.66833 | 0.086975 | 0.74615 | 0.16479 | -0.027466 | 0.01831 | -122.7676 | 0.004578 | 0.20142 | -0.1236 | 0.22888 | -0.09613 | 0.62714 | 122.7127 | 0.032044 | 0.086975 | 122.8775 | 122.8729 | 122.7997 | 122.8455 | -122.905 | -122.8546 | 122.6349 | 0.059509 | 2.4994 | 1.1902
2312.1719 | 122.9874 | -57.1609 | 65.6754 | -0.091095 | 0.0014761 | 0.061812 | 0.068832 | -0.00048063 | 0.0024053 | 0.0052082 | 0.013916 | -0.00017945 | 2.8e-08 | -0.0078442 | -0.0010787 | -0.0049389 | -0.0042469 | -54.6936 | 65.6204 | -57.2296 | 65.506 | -56.5796 | -56.9916 | -56.4148 | -55.9296 | 65.6754 | -57.1793 | -57.0831 | -57.1014 | -57.2113 | -56.9092 | -0.068664 | -0.054932 | -0.16937 | 0.58136 | 0.74616 | 0.16937 | 0.81482 | 0.23804 | -0.01831 | 0 | -122.7585 | 0.05951 | 0.25177 | -0.050354 | 0.27008 | -0.032044 | 0.65002 | 122.7356 | 0.07782 | 0.09613 | 122.85 | 122.8546 | 122.7814 | 122.8363 | -122.905 | -122.8546 | 122.6669 | 0.07782 | 2.4673 | 1.2314
2313.1719 | 123.0057 | -57.1518 | 65.657 | -0.098725 | 0.00062166 | 0.060316 | 0.06755 | -0.00069423 | 0.00048269 | 0.0049946 | 0.0047608 | 0.00024775 | -0.0027772 | -0.0031446 | -0.00043791 | -0.0032301 | -0.0016833 | -54.6936 | 65.6113 | -57.2479 | 65.5106 | -56.5842 | -56.9962 | -56.4148 | -55.9433 | 65.6708 | -57.1838 | -57.0969 | -57.1106 | -57.2067 | -56.9229 | -0.096131 | -0.045776 | -0.14648 | 0.56763 | 0.737 | 0.15564 | 0.83313 | 0.25177 | -0.032044 | 0.013733 | -122.7539 | 0.041198 | 0.22888 | -0.054932 | 0.26093 | -0.022888 | 0.66376 | 122.7585 | 0.073242 | 0.086975 | 122.8592 | 122.8546 | 122.7631 | 122.8226 | -122.905 | -122.8409 | 122.6624 | 0.054931 | 2.4582 | 1.2085
2314.1719 | 123.0011 | -57.1655 | 65.6387 | -0.11398 | -0.00087374 | 0.063307 | 0.067336 | -0.0030442 | 0.0011237 | 0.0054218 | 0.0047608 | 0.0011023 | 0.002777 | 0.0015552 | -0.0012925 | -0.0049389 | 0.00088014 | -54.689 | 65.6342 | -57.2205 | 65.4968 | -56.575 | -57.0099 | -56.4056 | -55.9387 | 65.6845 | -57.1655 | -57.1198 | -57.1198 | -57.1884 | -56.9046 | -0.054932 | -0.004578 | -0.14191 | 0.59051 | 0.75989 | 0.15564 | 0.81482 | 0.21057 | 0 | 0.045776 | -122.7585 | 0.045776 | 0.26093 | -0.022889 | 0.26093 | -0.022889 | 0.64545 | 122.7173 | 0.045776 | 0.045776 | 122.8546 | 122.85 | 122.7997 | 122.85 | -122.8592 | -122.8043 | 122.6624 | 0.045776 | 2.4765 | 1.2268
2315.1719 | 122.9782 | -57.1793 | 65.6616 | -0.091095 | 0.00062166 | 0.06288 | 0.070113 | -0.0015488 | 0.0026191 | 0.0052082 | 0.023071 | 0.0040929 | 2.8e-08 | 0.005614 | -0.00022431 | -0.0049389 | 0.00088014 | -54.7028 | 65.625 | -57.2113 | 65.506 | -56.575 | -57.0099 | -56.4285 | -55.925 | 65.6616 | -57.1701 | -57.0923 | -57.106 | -57.1838 | -56.9183 | -0.032044 | -0.036621 | -0.15564 | 0.60425 | 0.75073 | 0.16937 | 0.78278 | 0.20142 | 0.009155 | 0 | -122.7539 | 0.073242 | 0.26093 | -0.004578 | 0.25177 | -0.013733 | 0.63629 | 122.7173 | 0.064087 | 0.07782 | 122.8363 | 122.8317 | 122.8043 | 122.8409 | -122.8729 | -122.8317 | 122.6852 | 0.086975 | 2.4765 | 1.2543
2316.1719 | 122.9919 | -57.1518 | 65.6708 | -0.083466 | -0.0019417 | 0.060744 | 0.069686 | 0.001442 | -0.00058531 | 0.0017902 | 0.0078126 | 0.0011023 | 2.8e-08 | 5.9824e-05 | -0.00086511 | -0.0032301 | -0.0018971 | -54.6982 | 65.5838 | -57.2205 | 65.5106 | -56.5796 | -56.9962 | -56.4148 | -55.9296 | 65.6342 | -57.1838 | -57.0877 | -57.1106 | -57.2067 | -56.9046 | -0.068665 | -0.086975 | -0.16022 | 0.5722 | 0.737 | 0.15564 | 0.80566 | 0.2243 | -0.032044 | -0.036621 | -122.7585 | 0.041198 | 0.24719 | -0.054932 | 0.27924 | -0.022888 | 0.64087 | 122.731 | 0.073242 | 0.09613 | 122.8043 | 122.818 | 122.7356 | 122.7859 | -122.8912 | -122.8546 | 122.6624 | 0.064086 | 2.4536 | 1.2222
2317.1719 | 123.0103 | -57.1426 | 65.6708 | 0.00045798 | -0.0010873 | 0.062666 | 0.067336 | 0.0016556 | 0.0026191 | 0.0015766 | 0.032227 | 0.0013159 | -0.00021357 | 0.0024096 | -0.00086511 | -0.0036573 | 0.0017345 | -54.689 | 65.6021 | -57.2067 | 65.4877 | -56.5704 | -56.9824 | -56.4148 | -55.925 | 65.6525 | -57.2021 | -57.1014 | -57.0877 | -57.1884 | -56.9138 | -0.064087 | -0.068664 | -0.1831 | 0.5722 | 0.72784 | 0.16022 | 0.79193 | 0.2243 | -0.059509 | -0.01831 | -122.7722 | 0.054931 | 0.22888 | -0.045777 | 0.28839 | 0.013732 | 0.63629 | 122.6944 | 0.11444 | 0.10071 | 122.8088 | 122.8546 | 122.7448 | 122.7951 | -122.8775 | -122.8729 | 122.6303 | 0.041199 | 2.4536 | 1.2177
2318.1719 | 122.9416 | -57.1701 | 65.657 | -0.060578 | -0.0027963 | 0.061171 | 0.068404 | 0.003151 | 0.00091009 | 0.0026446 | -0.025757 | 0.0034521 | 0.002777 | 0.0017688 | -0.00086511 | -0.0042981 | -0.0016833 | -54.7577 | 65.6708 | -57.2479 | 65.538 | -56.5659 | -57.2525 | -56.6254 | -56.0623 | 65.6799 | -57.2021 | -57.1518 | -57.1655 | -57.2754 | -56.9733 | -0.07782 | 0.013733 | -0.11902 | 0.60425 | 0.54474 | -0.082397 | 0.62256 | -0.004577 | -0.032043 | 0.022889 | -122.8088 | 0.004578 | 0.19684 | -0.10529 | 0.22888 | -0.073243 | 0.68207 | 122.786 | 0.036621 | 0.050354 | 122.9187 | 122.8821 | 122.8409 | 122.85 | -122.905 | -122.8592 | 122.7081 | 0.018311 | 2.4124 | 1.1078
2319.1719 | 122.9507 | -57.1609 | 65.6799 | -0.045319 | 0.00062166 | 0.060316 | 0.070968 | -0.0011214 | 5.5488e-05 | 0.0060626 | -0.092895 | 0.0021703 | -0.00085457 | 0.0032642 | -0.0012925 | -0.0032301 | 0.00066654 | -54.7623 | 65.6662 | -57.225 | 65.3961 | -56.7032 | -56.9183 | -56.3278 | -56.0761 | 65.6891 | -57.2205 | -57.1655 | -57.1701 | -57.28 | -56.9687 | -0.064087 | -0.013733 | -0.28381 | 0.45776 | 0.83313 | 0.24262 | 0.89722 | 0.3067 | -0.059509 | 0.009155 | -122.8455 | -0.009155 | 0.19226 | -0.11902 | 0.25177 | -0.059509 | 0.52185 | 122.6212 | 0.050354 | 0.054932 | 122.8912 | 122.9095 | 122.8271 | 122.85 | -122.905 | -122.9004 | 122.5571 | -0.004577 | 2.3987 | 1.0849
2320.1719 | 122.9324 | -57.1701 | 65.6754 | -0.11398 | -0.0017281 | 0.062239 | 0.068191 | 0.0022964 | 0.00048269 | 0.0028582 | -0.03186 | 0.0021703 | 0.00021363 | 0.0032642 | -0.00065151 | -0.0030163 | -0.0031787 | -54.7577 | 65.6662 | -57.2479 | 65.4236 | -56.7032 | -57.0923 | -56.3644 | -56.1905 | 65.6845 | -57.2159 | -57.1609 | -57.193 | -57.2708 | -56.955 | -0.07782 | -0.009155 | -0.25177 | 0.46692 | 0.80566 | 0.07782 | 0.88348 | 0.15564 | -0.045776 | 0.009155 | -122.8363 | -0.022888 | 0.21515 | -0.10071 | 0.26093 | -0.054932 | 0.54474 | 122.6715 | 0.022888 | 0.054931 | 122.9141 | 122.9004 | 122.8363 | 122.8546 | -122.9233 | -122.8912 | 122.5937 | 0.009155 | 2.4124 | 0.97961
2321.1719 | 122.9324 | -57.1838 | 65.6754 | -0.037689 | -0.00066014 | 0.059676 | 0.069259 | 0.00037377 | 0.00048269 | 0.0062762 | -0.0043946 | 0.0028113 | 0.0012818 | -0.00229 | -0.00022431 | -0.0032301 | 0.00066654 | -54.776 | 65.657 | -57.2525 | 65.4053 | -56.6803 | -57.0877 | -56.5018 | -55.9387 | 65.7578 | -57.1793 | -57.1701 | -57.1747 | -57.2983 | -56.9824 | -0.068664 | -0.018311 | -0.27008 | 0.50354 | 0.68207 | 0.09613 | 0.75073 | 0.16479 | 0.004578 | 0.082397 | -122.8455 | 0.009155 | 0.20142 | -0.11444 | 0.19684 | -0.11902 | 0.5722 | 122.6578 | 0.004577 | 0.009155 | 122.9095 | 122.937 | 122.8409 | 122.9416 | -122.9279 | -122.8546 | 122.5891 | 0.013733 | 2.4078 | 1.2451
2322.1719 | 122.9462 | -57.1793 | 65.6708 | -0.083466 | -0.00044654 | 0.062025 | 0.071181 | -0.0011214 | 0.0039007 | 0.0043536 | 0.001709 | 0.0013159 | 0.00064083 | -0.0014356 | -0.0012925 | -0.0019483 | -0.0031787 | -54.7623 | 65.6525 | -57.2433 | 65.4007 | -56.6803 | -57.0831 | -56.5155 | -56.0349 | 65.712 | -57.1976 | -57.2296 | -57.1289 | -57.3166 | -57.0053 | -0.064087 | -0.01831 | -0.27008 | 0.49896 | 0.66376 | 0.09613 | 0.72784 | 0.16022 | -0.018311 | 0.041199 | -122.9004 | 0.050354 | 0.17395 | -0.13733 | 0.19226 | -0.11902 | 0.56305 | 122.644 | 0.068665 | -0.032043 | 122.8958 | 122.9095 | 122.8317 | 122.8912 | -122.9141 | -122.8683 | 122.58 | -0.050354 | 2.417 | 1.1444
2323.1719 | 122.9462 | -57.1518 | 65.6616 | -0.052948 | -0.00066014 | 0.060957 | 0.068404 | 0.0016556 | 0.0032599 | 0.0054218 | 0.001709 | 0.0023839 | 0.002777 | 5.9824e-05 | -0.00022431 | -0.0042981 | 0.0030163 | -54.7028 | 65.625 | -57.2388 | 65.4648 | -56.6208 | -57.0099 | -56.4514 | -55.9616 | 65.6616 | -57.1793 | -57.1426 | -57.1609 | -57.2525 | -56.9321 | -0.086976 | -0.036621 | -0.19684 | 0.53101 | 0.70038 | 0.14191 | 0.78735 | 0.22888 | -0.027466 | 0 | -122.8043 | -0.009156 | 0.21973 | -0.10071 | 0.24719 | -0.073242 | 0.61798 | 122.7036 | 0.01831 | 0.036621 | 122.8638 | 122.8409 | 122.7768 | 122.8134 | -122.9004 | -122.8409 | 122.6166 | 0.009155 | 2.449 | 1.1902
2324.1719 | 122.9279 | -57.1884 | 65.6754 | -0.052948 | 0.0016899 | 0.060957 | 0.069472 | 0.00080117 | 0.0043281 | 0.0045672 | 0.010864 | 0.0030249 | 0.0021362 | 0.0024096 | -0.0019333 | -0.0053663 | -0.0055287 | -54.7623 | 65.6616 | -57.225 | 65.4099 | -56.6895 | -57.0831 | -56.5109 | -56.0394 | 65.712 | -57.2021 | -57.0099 | -57.1472 | -57.4265 | -57.1426 | -0.036621 | -0.013733 | -0.2655 | 0.49896 | 0.67749 | 0.10529 | 0.71411 | 0.14191 | -0.013732 | 0.036621 | -122.6852 | 0.041199 | 0.045777 | -0.23804 | 0.059509 | -0.22431 | 0.53558 | 122.6349 | 0.054931 | 0.19226 | 122.8867 | 122.9141 | 122.85 | 122.9004 | -122.9004 | -122.8775 | 122.5983 | 0.17853 | 2.4261 | 1.149
2325.1719 | 122.9691 | -57.1701 | 65.6754 | -0.045319 | -0.0019417 | 0.060957 | 0.071395 | -0.0062484 | 0.0021917 | 0.00414 | -0.0043946 | 0.00046135 | 0.00064083 | 0.0049732 | -0.0012925 | -0.0036573 | -0.0025379 | -54.7623 | 65.6616 | -57.2571 | 65.4053 | -56.7123 | -57.0923 | -56.543 | -56.0303 | 65.6891 | -57.2067 | -57.1426 | -57.1701 | -57.2754 | -56.9778 | -0.086975 | -0.013733 | -0.27008 | 0.45776 | 0.62714 | 0.07782 | 0.71411 | 0.1648 | -0.036621 | 0.013733 | -122.818 | 0 | 0.19226 | -0.10529 | 0.22888 | -0.068665 | 0.54474 | 122.6624 | 0.036621 | 0.064087 | 122.9187 | 122.8958 | 122.8317 | 122.8592 | -122.9324 | -122.8821 | 122.5754 | 0.027466 | 2.4078 | 1.1398
2326.1719 | 122.9279 | -57.1747 | 65.6845 | 0.008087 | 0.00040806 | 0.060103 | 0.069472 | 0.0018692 | -0.00037171 | 0.0045672 | -0.025757 | 0.00024775 | 0.00085443 | -0.00079478 | 0.00041649 | -0.0023755 | -0.0023243 | -54.7806 | 65.6525 | -57.2617 | 65.4144 | -56.7032 | -57.1014 | -56.5201 | -56.0303 | 65.7074 | -57.225 | -57.1564 | -57.1747 | -57.28 | -56.9504 | -0.086975 | -0.032043 | -0.27008 | 0.4715 | 0.6546 | 0.073243 | 0.74158 | 0.16022 | -0.050354 | 0.022888 | -122.8409 | 0 | 0.22431 | -0.10528 | 0.27466 | -0.054931 | 0.55847 | 122.6761 | 0.050354 | 0.068665 | 122.9141 | 122.9324 | 122.8271 | 122.8821 | -122.9462 | -122.9095 | 122.5891 | 0.018311 | 2.3941 | 1.1444
2327.1719 | 122.9507 | -57.1701 | 65.6662 | -0.014801 | -1.9142e-05 | 0.063521 | 0.068404 | 0.0035782 | 0.00091009 | 0.0054218 | 0.029175 | 0.0013159 | -0.0010682 | -0.00015378 | -0.00065151 | -0.0025891 | 0.00023934 | -54.8538 | 65.7028 | -57.2205 | 65.4053 | -56.7078 | -57.0969 | -56.5109 | -56.044 | 65.6982 | -57.2205 | -57.1701 | -57.1747 | -57.2845 | -56.9733 | -0.050354 | 0.036621 | -0.26093 | 0.46234 | 0.65918 | 0.073242 | 0.70953 | 0.1236 | -0.050354 | 0.032043 | -122.8363 | -0.004578 | 0.19684 | -0.11444 | 0.24719 | -0.064087 | 0.5127 | 122.6257 | 0.045776 | 0.050354 | 122.9233 | 122.9187 | 122.8729 | 122.8683 | -122.8867 | -122.8867 | 122.5754 | 0 | 2.3163 | 1.1261
2328.1719 | 122.9324 | -57.1793 | 65.6708 | -0.060578 | -0.00066014 | 0.059462 | 0.069686 | 0.0033646 | 0.0034735 | 0.0064898 | 0.016968 | -0.0012477 | -0.0010682 | -0.00058098 | -0.00065151 | -0.0034437 | -0.0036059 | -54.7394 | 65.6662 | -57.2296 | 65.3778 | -56.6528 | -57.1289 | -56.5613 | -56.0349 | 65.6891 | -57.2067 | -57.1747 | -57.1655 | -57.2754 | -56.987 | -0.050354 | -0.004577 | -0.29297 | 0.52643 | 0.61798 | 0.050354 | 0.66833 | 0.10071 | -0.027466 | 0.018311 | -122.8455 | 0.013733 | 0.19226 | -0.096131 | 0.21973 | -0.068665 | 0.57678 | 122.6074 | 0.041199 | 0.032043 | 122.8958 | 122.8958 | 122.8455 | 122.8683 | -122.9004 | -122.8775 | 122.5571 | 0.004577 | 2.4399 | 1.1444
2329.1719 | 122.9553 | -57.1793 | 65.6662 | -0.10635 | 0.0010489 | 0.062666 | 0.069686 | -0.0030442 | 0.0013373 | 0.0071308 | 0.02002 | 0.0021703 | 0.0023498 | -0.00058098 | -0.0017197 | -0.0034437 | -0.0018971 | -54.7348 | 65.6799 | -57.2433 | 65.5197 | -56.488 | -57.2159 | -56.6345 | -56.044 | 65.6845 | -57.225 | -57.1655 | -57.1838 | -57.2845 | -56.9687 | -0.064087 | 0.013733 | -0.14649 | 0.69122 | 0.54474 | -0.036621 | 0.60883 | 0.027466 | -0.045777 | 0.01831 | -122.8317 | -0.004578 | 0.21057 | -0.10529 | 0.25635 | -0.059509 | 0.75531 | 122.7631 | 0.041199 | 0.05951 | 122.9233 | 122.9095 | 122.8592 | 122.8638 | -122.9095 | -122.8912 | 122.699 | 0.013733 | 2.4445 | 1.1353
2330.1719 | 122.9553 | -57.1655 | 65.6708 | -0.060578 | 0.00019446 | 0.060744 | 0.067763 | 0.0018692 | 0.0013373 | 0.005849 | 0.02002 | 0.0017431 | 0.0014954 | -0.00015378 | -0.0010787 | -0.0042981 | -0.0010425 | -54.7119 | 65.657 | -57.2113 | 65.4602 | -56.6208 | -57.0374 | -56.4606 | -55.9753 | 65.6754 | -57.1793 | -57.1426 | -57.193 | -57.28 | -56.9733 | -0.045777 | -0.013733 | -0.21057 | 0.54474 | 0.70496 | 0.12817 | 0.75073 | 0.17395 | -0.013733 | 0.004578 | -122.8134 | -0.027466 | 0.19226 | -0.11444 | 0.20599 | -0.10071 | 0.59051 | 122.6715 | -0.013733 | 0.036621 | 122.8683 | 122.8546 | 122.8226 | 122.8409 | -122.8821 | -122.85 | 122.6257 | 0.022888 | 2.4536 | 1.1902
2331.1719 | 122.9187 | -57.1884 | 65.6525 | -0.083466 | -0.00044654 | 0.060316 | 0.067763 | -0.005394 | 0.0028327 | 0.00414 | 0.0078126 | 0.00067495 | 0.00085443 | 0.0026232 | -0.00086511 | -0.0051527 | 0.0015209 | -54.7623 | 65.657 | -57.2571 | 65.4007 | -56.6895 | -57.0831 | -56.5063 | -56.0257 | 65.6891 | -57.1838 | -57.1243 | -57.0053 | -57.3624 | -57.0694 | -0.068664 | 0.004577 | -0.25177 | 0.49896 | 0.68207 | 0.10529 | 0.75073 | 0.17395 | 0.004578 | 0.036621 | -122.7768 | 0.18311 | 0.11902 | -0.17395 | 0.11444 | -0.17853 | 0.56763 | 122.6578 | 0.17853 | 0.059509 | 122.9141 | 122.8729 | 122.8455 | 122.8775 | -122.9095 | -122.8363 | 122.5891 | 0.064087 | 2.4261 | 1.1627
2332.1719 | 122.9462 | -57.1838 | 65.6982 | -0.083466 | 0.0027579 | 0.059676 | 0.068618 | 0.0012284 | 0.0030463 | 0.0049946 | -0.022705 | 0.0015295 | 0.0021362 | 0.00048702 | -0.0012925 | -0.0047253 | -0.0044605 | -54.7394 | 65.6754 | -57.2525 | 65.4099 | -56.6803 | -57.0786 | -56.5247 | -56.0303 | 65.7257 | -57.193 | -57.1518 | -57.193 | -57.2754 | -56.9504 | -0.068664 | -0.022888 | -0.28839 | 0.50354 | 0.65918 | 0.10529 | 0.72784 | 0.17395 | -0.009155 | 0.027466 | -122.85 | -0.009155 | 0.23346 | -0.091553 | 0.24262 | -0.082398 | 0.5722 | 122.6624 | 0 | 0.041199 | 122.9279 | 122.9187 | 122.8592 | 122.9095 | -122.9507 | -122.8912 | 122.5937 | 0.032044 | 2.4445 | 1.1536
2333.1719 | 122.9553 | -57.1701 | 65.6708 | 0.008087 | 0.00083526 | 0.056044 | 0.068191 | 0.0027238 | 5.5488e-05 | 0.0045672 | -0.010498 | 0.00088875 | 0.00064083 | -0.0033582 | -0.0015061 | -0.0045117 | -0.0025379 | -54.5746 | 65.6937 | -57.2159 | 65.387 | -56.7307 | -57.0786 | -56.5292 | -56.0211 | 65.6937 | -57.193 | -57.1609 | -57.1701 | -57.2754 | -56.9687 | -0.045776 | 0.022889 | -0.28381 | 0.43945 | 0.64087 | 0.091553 | 0.68665 | 0.13733 | -0.022888 | 0.022889 | -122.8317 | 0 | 0.20142 | -0.10529 | 0.2243 | -0.082398 | 0.48523 | 122.6028 | 0.022888 | 0.032043 | 122.9095 | 122.8867 | 122.8638 | 122.8638 | -122.8867 | -122.8638 | 122.5571 | 0.009155 | 2.5955 | 1.149
2334.1719 | 122.9416 | -57.1701 | 65.6754 | -0.068207 | 0.00083526 | 0.060744 | 0.068191 | -0.0038986 | 0.0026191 | 0.0032856 | 0.023071 | 0.00046135 | 0.0012818 | -0.003999 | -0.0023605 | -0.0036573 | -0.0059559 | -54.744 | 65.6891 | -57.2525 | 65.5884 | -56.6299 | -57.2708 | -56.6483 | -56.0669 | 65.6799 | -57.2159 | -57.1747 | -57.1655 | -57.2754 | -56.9824 | -0.082397 | 0.013733 | -0.086975 | 0.54016 | 0.52185 | -0.10071 | 0.60425 | -0.018311 | -0.045776 | 0.004578 | -122.85 | 0.004578 | 0.18768 | -0.10529 | 0.23346 | -0.05951 | 0.62256 | 122.8409 | 0.050354 | 0.041198 | 122.9416 | 122.8958 | 122.8592 | 122.85 | -122.9279 | -122.8912 | 122.7585 | -0.004578 | 2.4261 | 1.1032
2335.1719 | 122.9462 | -57.1976 | 65.6754 | -0.083466 | -0.00044654 | 0.061171 | 0.067336 | 0.00251 | 0.0024053 | 0.003072 | 0.010864 | -0.00060665 | 0.0025634 | -0.00229 | -0.00086511 | -0.0047253 | -0.0012561 | -54.7577 | 65.6799 | -57.225 | 65.4053 | -56.6757 | -57.0877 | -56.5109 | -55.838 | 65.7532 | -57.1655 | -57.1747 | -57.2159 | -57.2937 | -56.9778 | -0.027466 | 0.004578 | -0.27008 | 0.52185 | 0.68665 | 0.10986 | 0.71411 | 0.13733 | 0.032044 | 0.07782 | -122.85 | -0.01831 | 0.21973 | -0.09613 | 0.18768 | -0.12817 | 0.54932 | 122.6303 | -0.050354 | -0.009156 | 122.905 | 122.9187 | 122.8775 | 122.9507 | -122.9004 | -122.8409 | 122.6028 | 0.022888 | 2.4399 | 1.3596
2336.1719 | 122.9645 | -57.1793 | 65.6799 | -0.098725 | -0.00066014 | 0.060316 | 0.069259 | -0.0026168 | 0.0019781 | 0.0043536 | 0.03833 | 0.0019567 | 0.0032044 | -0.0037854 | -0.0010787 | -0.0049389 | 0.0025891 | -54.7531 | 65.6845 | -57.225 | 65.4144 | -56.6803 | -57.0831 | -56.5201 | -56.0303 | 65.7074 | -57.1884 | -57.0648 | -57.2479 | -57.4402 | -57.0694 | -0.045777 | 0.004577 | -0.2655 | 0.49896 | 0.65918 | 0.09613 | 0.70496 | 0.14191 | -0.009156 | 0.027465 | -122.7448 | -0.068665 | 0.10986 | -0.26093 | 0.11902 | -0.25177 | 0.54474 | 122.6395 | -0.059509 | 0.1236 | 122.9095 | 122.8958 | 122.8638 | 122.8867 | -122.905 | -122.8683 | 122.5937 | 0.11444 | 2.4261 | 1.149
2337.1719 | 122.9874 | -57.1472 | 65.657 | -0.045319 | -0.0013009 | 0.062025 | 0.068191 | -0.003685 | 0.0017645 | 0.0028582 | 0.053589 | -0.00017945 | 0.001068 | -0.0010084 | -0.0042831 | -0.0053663 | -0.0018971 | -54.6936 | 65.6479 | -57.2021 | 65.4694 | -56.5979 | -57.0053 | -56.4331 | -55.957 | 65.6891 | -57.1838 | -57.1381 | -57.1472 | -57.2296 | -56.9321 | -0.054931 | -0.009155 | -0.18768 | 0.54932 | 0.71411 | 0.14191 | 0.76904 | 0.19684 | -0.036621 | 0.032044 | -122.7951 | 0 | 0.21515 | -0.082397 | 0.25177 | -0.045776 | 0.60425 | 122.6715 | 0.036621 | 0.045776 | 122.85 | 122.8729 | 122.7951 | 122.8363 | -122.8592 | -122.8409 | 122.6166 | 0.009155 | 2.4536 | 1.1902
2338.1719 | 122.9416 | -57.2067 | 65.6982 | -0.083466 | -0.0015145 | 0.061598 | 0.069472 | -0.001976 | 5.5488e-05 | 0.0032856 | 0.0047608 | 0.0023839 | 0.0025634 | 0.00070062 | -0.0023605 | -0.0064343 | 2.554e-05 | -54.7485 | 65.6433 | -57.2342 | 65.419 | -56.6803 | -57.0877 | -56.5063 | -56.0211 | 65.6937 | -57.2067 | -57.1701 | -57.1701 | -57.2754 | -56.987 | -0.027466 | -0.054931 | -0.27924 | 0.52643 | 0.70038 | 0.11902 | 0.72784 | 0.14648 | 0 | -0.004577 | -122.8683 | 0.036621 | 0.21973 | -0.068665 | 0.21973 | -0.068665 | 0.55389 | 122.6532 | 0.036621 | 0.036621 | 122.8775 | 122.9004 | 122.85 | 122.9004 | -122.9324 | -122.905 | 122.6257 | 0.036621 | 2.4582 | 1.1856
2339.1719 | 122.9599 | -57.1747 | 65.6845 | -0.083466 | 0.00019446 | 0.059248 | 0.07289 | -0.0038986 | 0.0013373 | 0.005849 | -0.0043946 | 0.00024775 | 0.0040588 | -0.00036738 | -0.00065151 | -0.0055799 | -0.0016833 | -54.7668 | 65.6799 | -57.2296 | 65.2771 | -56.7535 | -57.0465 | -56.5475 | -56.0394 | 65.7166 | -57.2021 | -57.1793 | -57.1976 | -57.28 | -56.9733 | -0.054931 | -0.004577 | -0.40741 | 0.42114 | 0.62714 | 0.12817 | 0.68207 | 0.1831 | -0.027465 | 0.032044 | -122.8638 | -0.022888 | 0.20142 | -0.10528 | 0.22888 | -0.07782 | 0.47607 | 122.5067 | 0.004577 | 0.022888 | 122.9095 | 122.9187 | 122.8546 | 122.8912 | -122.9141 | -122.8867 | 122.4518 | -0.004577 | 2.4078 | 1.1353
2340.1719 | 122.9691 | -57.1701 | 65.6662 | -0.060578 | 0.00019446 | 0.060957 | 0.067336 | -5.343e-05 | 0.0024053 | 0.0054218 | -0.053223 | 0.0019567 | 0.00042723 | 0.0013416 | -0.00065151 | -0.0047253 | 0.00088014 | -54.7485 | 65.6891 | -57.2067 | 65.3961 | -56.6208 | -56.8222 | -56.5567 | -56.0165 | 65.712 | -57.2205 | -57.1701 | -57.1564 | -57.2662 | -56.9824 | -0.036621 | 0.022888 | -0.27008 | 0.54932 | 0.6134 | 0.3479 | 0.65002 | 0.38452 | -0.050354 | 0.045776 | -122.8363 | 0.013733 | 0.18768 | -0.09613 | 0.23804 | -0.045776 | 0.58594 | 122.6028 | 0.064087 | 0.050354 | 122.8958 | 122.9324 | 122.8592 | 122.8821 | -122.8729 | -122.8867 | 122.5662 | 0 | 2.4216 | 1.1536
2341.1719 | 122.9507 | -57.1655 | 65.6616 | -0.075836 | 0.0019035 | 0.060744 | 0.067336 | -0.0026168 | 0.00091009 | 0.0054218 | 0.02002 | 0.0011023 | 0.0038452 | -0.00079478 | -0.0030013 | -0.0036573 | 0.00023934 | -54.7485 | 65.6525 | -57.2342 | 65.419 | -56.694 | -57.0877 | -56.5109 | -55.838 | 65.7349 | -57.1655 | -57.1701 | -57.2021 | -57.2708 | -56.9824 | -0.068665 | -0.009155 | -0.24262 | 0.4715 | 0.6546 | 0.077819 | 0.72327 | 0.14648 | 0 | 0.073242 | -122.8317 | -0.036621 | 0.1831 | -0.10529 | 0.1831 | -0.10529 | 0.54016 | 122.6532 | -0.036621 | -0.004578 | 122.8867 | 122.9004 | 122.818 | 122.9004 | -122.8958 | -122.8271 | 122.5845 | -0.004578 | 2.417 | 1.3275
2342.1719 | 122.9324 | -57.1838 | 65.6799 | -0.03006 | -0.0019417 | 0.062666 | 0.069045 | -0.0032578 | 0.00026909 | 0.0052082 | 0.029175 | 0.00067495 | 0.0032044 | 0.00027342 | -0.0023605 | -0.0036573 | -0.00018806 | -54.7485 | 65.6662 | -57.2296 | 65.4144 | -56.694 | -57.0831 | -56.5063 | -56.0349 | 65.7257 | -57.2113 | -57.2296 | -57.28 | -57.2388 | -56.955 | -0.045776 | -0.013733 | -0.2655 | 0.48981 | 0.67749 | 0.10071 | 0.72327 | 0.14648 | -0.027466 | 0.045776 | -122.9095 | -0.09613 | 0.22888 | -0.054932 | 0.25635 | -0.027466 | 0.53558 | 122.644 | -0.068664 | -0.01831 | 122.8958 | 122.937 | 122.85 | 122.9095 | -122.9095 | -122.8912 | 122.5983 | -0.045776 | 2.4353 | 1.149
2343.1719 | 122.9828 | -57.1518 | 65.7028 | -0.091095 | -0.0013009 | 0.062239 | 0.07225 | -0.001976 | 0.0030463 | 0.0067036 | 0.026123 | 0.0017431 | 0.0014954 | -0.0020764 | -0.0034287 | -0.0051527 | 0.00045294 | -54.7394 | 65.6937 | -57.2342 | 65.4053 | -56.6711 | -57.1014 | -56.5109 | -56.0303 | 65.7303 | -57.1793 | -57.1564 | -57.1884 | -57.2983 | -56.8359 | -0.082398 | -0.009155 | -0.29755 | 0.48065 | 0.64087 | 0.050354 | 0.72327 | 0.13275 | -0.027466 | 0.027466 | -122.8592 | -0.036622 | 0.31586 | -0.14648 | 0.34332 | -0.11902 | 0.56305 | 122.6395 | -0.009156 | 0.022888 | 122.9279 | 122.9095 | 122.8455 | 122.8821 | -122.937 | -122.8821 | 122.5571 | -0.004578 | 2.4124 | 1.1215
2344.1719 | 123.0103 | -57.1472 | 65.6616 | -0.052948 | -0.00066014 | 0.061598 | 0.068618 | -0.00026703 | 0.0024053 | 0.002431 | 0.023071 | 0.0019567 | 0.001068 | 0.0013416 | -0.0040695 | -0.0034437 | 0.0038709 | -54.6844 | 65.6204 | -57.2021 | 65.5014 | -56.5887 | -57.0007 | -56.4331 | -55.9479 | 65.6708 | -57.1609 | -57.1335 | -57.1152 | -57.2067 | -56.9321 | -0.054931 | -0.041199 | -0.16022 | 0.55847 | 0.71411 | 0.14648 | 0.76904 | 0.20142 | -0.013733 | 0.009155 | -122.7951 | 0.032044 | 0.21515 | -0.059509 | 0.22888 | -0.045776 | 0.6134 | 122.7036 | 0.045777 | 0.027466 | 122.8226 | 122.8317 | 122.7676 | 122.818 | -122.8638 | -122.8226 | 122.6486 | 0.013733 | 2.4628 | 1.1993
2345.1719 | 122.9691 | -57.1564 | 65.6799 | -0.075836 | 0.0010489 | 0.061171 | 0.068832 | -0.0011214 | 0.00026909 | 0.00414 | 0.035278 | 0.00067495 | -0.00085457 | 0.0045458 | 0.00041649 | -0.0060071 | 2.554e-05 | -54.7348 | 65.6662 | -57.2342 | 65.4053 | -56.6803 | -57.0557 | -56.5063 | -56.0211 | 65.6891 | -57.1838 | -57.1609 | -57.1655 | -57.2617 | -56.9733 | -0.07782 | -0.013733 | -0.27466 | 0.47607 | 0.65002 | 0.10071 | 0.72784 | 0.17853 | -0.027466 | 0.009155 | -122.8409 | -0.009155 | 0.1831 | -0.10529 | 0.21057 | -0.07782 | 0.55389 | 122.6395 | 0.018311 | 0.022888 | 122.9004 | 122.8729 | 122.8226 | 122.8455 | -122.9141 | -122.8638 | 122.5616 | -0.004578 | 2.4216 | 1.1353
2346.1719 | 122.9736 | -57.1838 | 65.6891 | -0.03006 | 0.0014761 | 0.059035 | 0.068618 | -0.0021896 | 0.00026909 | 0.0043536 | -0.01355 | 0.0015295 | 0.0014954 | -0.00036738 | -0.00043791 | -0.0015211 | -0.00040166 | -54.7348 | 65.6525 | -57.2662 | 65.3503 | -56.8634 | -57.0648 | -56.5247 | -56.0211 | 65.7166 | -57.2067 | -57.1701 | -57.193 | -57.2983 | -56.9595 | -0.082397 | -0.036621 | -0.33875 | 0.32044 | 0.65918 | 0.11902 | 0.74158 | 0.20142 | -0.022888 | 0.027466 | -122.8592 | -0.009155 | 0.2243 | -0.11444 | 0.24719 | -0.091553 | 0.40283 | 122.6166 | 0.013733 | 0.036621 | 122.9187 | 122.9233 | 122.8363 | 122.9004 | -122.9553 | -122.8958 | 122.5342 | 0.013733 | 2.449 | 1.1627
2347.1719 | 122.9279 | -57.1701 | 65.6845 | -0.045319 | -0.00066014 | 0.064162 | 0.068832 | -0.0011214 | 0.0032599 | 0.0052082 | -0.022705 | 0.0021703 | 2.8e-08 | 0.0064684 | -0.0025741 | -0.0049389 | 0.00066654 | -54.744 | 65.6754 | -57.2479 | 65.4053 | -56.7169 | -56.8268 | -56.4331 | -56.0165 | 65.6982 | -57.2205 | -57.1701 | -57.1655 | -57.2662 | -56.9733 | -0.07782 | -0.009155 | -0.27924 | 0.45319 | 0.737 | 0.34332 | 0.81482 | 0.42114 | -0.050354 | 0.013733 | -122.8546 | 0.004578 | 0.19684 | -0.09613 | 0.24719 | -0.045776 | 0.53101 | 122.6532 | 0.054932 | 0.050354 | 122.9233 | 122.9187 | 122.8455 | 122.8683 | -122.9324 | -122.905 | 122.5754 | 0 | 2.4261 | 1.1536
2348.1719 | 122.9507 | -57.193 | 65.6982 | -0.014801 | -1.9142e-05 | 0.062239 | 0.068404 | -0.001976 | 0.0030463 | 0.0062762 | 0.0078126 | 0.0011023 | 0.0014954 | 0.0041186 | -0.0015061 | -0.0040845 | 0.00023934 | -54.7531 | 65.6845 | -57.2205 | 65.4099 | -56.6895 | -57.0877 | -56.5155 | -55.8334 | 65.7257 | -57.1564 | -57.1518 | -57.225 | -57.28 | -56.9916 | -0.027466 | -0.013733 | -0.28839 | 0.50354 | 0.67749 | 0.10529 | 0.70496 | 0.13275 | 0.036621 | 0.027466 | -122.85 | -0.032044 | 0.20142 | -0.086975 | 0.16479 | -0.1236 | 0.53101 | 122.6303 | -0.068665 | 0.004578 | 122.905 | 122.8821 | 122.8775 | 122.9187 | -122.9187 | -122.8546 | 122.6028 | 0.041199 | 2.4399 | 1.3596
2349.1719 | 122.9095 | -57.1747 | 65.6662 | -0.045319 | -0.00044654 | 0.059889 | 0.069686 | 0.0018692 | 0.0011237 | 0.0054218 | -0.0043946 | 0.00067495 | -0.00064077 | -0.0093396 | -0.0023605 | -0.0025891 | 0.0023755 | -54.7577 | 65.6708 | -57.2296 | 65.4236 | -56.694 | -57.0831 | -56.5247 | -56.0303 | 65.6891 | -57.2113 | -57.2708 | -57.2067 | -57.2571 | -56.9778 | -0.054931 | 0.004577 | -0.24262 | 0.48065 | 0.65002 | 0.091553 | 0.70496 | 0.14648 | -0.036621 | 0.022888 | -122.937 | -0.032043 | 0.19684 | -0.082397 | 0.23346 | -0.045776 | 0.53558 | 122.6532 | 0.004578 | -0.059509 | 122.9004 | 122.9004 | 122.8455 | 122.8638 | -122.8958 | -122.8775 | 122.5983 | -0.09613 | 2.417 | 1.1444
2350.1719 | 122.9416 | -57.1838 | 65.6845 | 0.00045798 | 0.0025443 | 0.060744 | 0.069045 | -0.00069423 | -0.0010125 | 0.0032856 | 0.0078126 | -0.0010339 | -0.001709 | -0.00079478 | -0.0010787 | -0.0066479 | -0.00040166 | -54.7394 | 65.6708 | -57.2433 | 65.4099 | -56.6757 | -57.0877 | -56.5201 | -56.0211 | 65.712 | -57.193 | -57.0648 | -57.2388 | -57.4448 | -57.0648 | -0.059509 | -0.013733 | -0.27466 | 0.50812 | 0.66376 | 0.09613 | 0.72327 | 0.15564 | -0.009155 | 0.027466 | -122.7493 | -0.054932 | 0.11902 | -0.26093 | 0.12817 | -0.25177 | 0.56763 | 122.6532 | -0.045777 | 0.12817 | 122.9141 | 122.905 | 122.8546 | 122.8958 | -122.9279 | -122.8775 | 122.5937 | 0.11902 | 2.4445 | 1.1627
2351.1719 | 122.9828 | -57.1793 | 65.6845 | -0.060578 | 0.0014761 | 0.062453 | 0.069045 | -0.00048063 | 0.0013373 | 0.0045672 | 0.03833 | 0.00024775 | 0.0012818 | -0.00079478 | -0.0021469 | -0.0047253 | 0.0034435 | -54.6982 | 65.625 | -57.2113 | 65.4694 | -56.6025 | -57.0053 | -56.4468 | -55.9616 | 65.6845 | -57.1701 | -57.1426 | -57.1472 | -57.2388 | -56.955 | -0.032044 | -0.059509 | -0.21515 | 0.57678 | 0.73242 | 0.17395 | 0.76447 | 0.20599 | 0.009155 | 0 | -122.8271 | 0.032043 | 0.2243 | -0.05951 | 0.21515 | -0.068665 | 0.60883 | 122.6807 | 0.022888 | 0.027466 | 122.8363 | 122.8546 | 122.8043 | 122.8638 | -122.8958 | -122.8546 | 122.6486 | 0.036621 | 2.4811 | 1.2177
2352.1719 | 122.9324 | -57.1976 | 65.6845 | -0.12161 | -0.0013009 | 0.06053 | 0.069472 | 0.0057144 | 0.00069649 | 0.0054218 | 0.0047608 | 0.0019567 | 0.0019226 | 0.0051868 | -0.00022431 | -0.0049389 | 0.0023755 | -54.744 | 65.6525 | -57.2479 | 65.4099 | -56.694 | -57.0786 | -56.5201 | -56.0394 | 65.6937 | -57.1976 | -57.1381 | -57.1793 | -57.2708 | -56.9641 | -0.050354 | -0.032043 | -0.27466 | 0.50354 | 0.67749 | 0.11902 | 0.72784 | 0.16937 | 0 | 0.009156 | -122.8226 | 0.018311 | 0.23346 | -0.073242 | 0.23346 | -0.073242 | 0.55389 | 122.6578 | 0.018311 | 0.059509 | 122.9004 | 122.8912 | 122.85 | 122.8912 | -122.9324 | -122.8821 | 122.6074 | 0.059509 | 2.4536 | 1.1581
2353.1719 | 122.9324 | -57.1793 | 65.6845 | -0.0071715 | -0.00087374 | 0.062025 | 0.068832 | -0.001976 | 0.0015509 | 0.00414 | -0.028809 | -0.00039305 | 0.00021363 | 0.0028368 | -0.0010787 | -0.0023755 | -0.00018806 | -54.7394 | 65.657 | -57.2433 | 65.4053 | -56.6986 | -57.1014 | -56.5384 | -56.0349 | 65.7211 | -57.2067 | -57.1564 | -57.1793 | -57.2617 | -56.9504 | -0.064087 | -0.027466 | -0.27924 | 0.48065 | 0.64087 | 0.07782 | 0.70496 | 0.14191 | -0.027466 | 0.036621 | -122.8409 | 0 | 0.22888 | -0.082398 | 0.25635 | -0.054932 | 0.54474 | 122.6486 | 0.027466 | 0.050354 | 122.9004 | 122.9279 | 122.8363 | 122.9004 | -122.9279 | -122.8912 | 122.5845 | 0.022888 | 2.4399 | 1.1444
2354.1719 | 122.9553 | -57.1701 | 65.6845 | -0.091095 | 0.00062166 | 0.062239 | 0.0699 | -5.343e-05 | 0.0015509 | 0.007558 | 0.0047608 | 0.00088875 | 0.0012818 | 0.0026232 | -0.0010787 | -0.0042981 | -0.0012561 | -54.7577 | 65.6754 | -57.2525 | 65.4144 | -56.7078 | -57.0969 | -56.5384 | -56.0394 | 65.7074 | -57.1793 | -57.1426 | -57.1793 | -57.2845 | -56.9687 | -0.082397 | -0.009155 | -0.27008 | 0.46234 | 0.63171 | 0.073242 | 0.71411 | 0.15564 | -0.009155 | 0.022888 | -122.8271 | -0.009155 | 0.20142 | -0.11444 | 0.21057 | -0.10529 | 0.54474 | 122.6669 | 0 | 0.036621 | 122.9279 | 122.8867 | 122.8455 | 122.8775 | -122.937 | -122.8638 | 122.5845 | 0.027466 | 2.4124 | 1.1307
2355.1719 | 122.9416 | -57.1518 | 65.6891 | -0.060578 | 0.0019035 | 0.06053 | 0.069259 | 0.001442 | -0.00058531 | 0.0064898 | -0.0013428 | 0.00088875 | 0.00085443 | 0.0043322 | -0.0021469 | -0.0025891 | -0.0027515 | -54.7668 | 65.6616 | -57.2525 | 65.3961 | -56.7078 | -57.1014 | -56.5475 | -56.0349 | 65.6937 | -57.1884 | -57.1381 | -57.1564 | -57.2937 | -56.9504 | -0.10071 | -0.027466 | -0.29297 | 0.44403 | 0.60425 | 0.050354 | 0.70496 | 0.15106 | -0.036622 | 0.004578 | -122.8271 | -0.004578 | 0.20142 | -0.14191 | 0.23804 | -0.10529 | 0.54474 | 122.6486 | 0.032044 | 0.050354 | 122.9141 | 122.8821 | 122.8134 | 122.8455 | -122.9416 | -122.8775 | 122.5479 | 0.013732 | 2.3849 | 1.1169
2356.1719 | 122.9279 | -57.1838 | 65.6937 | -0.045319 | -0.0010873 | 0.060957 | 0.068191 | -0.00069423 | 0.0017645 | 0.0056354 | 0.016968 | 0.0032385 | 0.001709 | -0.0010084 | -0.0023605 | -0.0060071 | 0.0051525 | -54.7577 | 65.6937 | -57.2571 | 65.4236 | -56.7032 | -57.0923 | -56.543 | -56.0303 | 65.6891 | -57.2021 | -57.1609 | -57.1701 | -57.2845 | -56.9595 | -0.073242 | 0 | -0.27008 | 0.48065 | 0.64087 | 0.091553 | 0.71411 | 0.1648 | -0.01831 | -0.004578 | -122.8546 | 0.013733 | 0.2243 | -0.10071 | 0.24261 | -0.082398 | 0.55389 | 122.6807 | 0.032043 | 0.041198 | 122.9507 | 122.8912 | 122.8775 | 122.8729 | -122.9507 | -122.8958 | 122.6074 | 0.022888 | 2.4261 | 1.1536
2357.1719 | 122.9233 | -57.1793 | 65.6799 | -0.11398 | 0.00040806 | 0.061812 | 0.068618 | -0.0011214 | 0.0034735 | 0.0054218 | -0.01355 | 0.0011023 | 0.001709 | -0.003999 | -0.0012925 | -0.0051527 | -0.00082886 | -54.7485 | 65.6754 | -57.2479 | 65.4053 | -56.7078 | -57.0831 | -56.5338 | -56.044 | 65.7074 | -57.2021 | -57.1655 | -57.1747 | -57.2845 | -56.9641 | -0.068665 | -0.004578 | -0.27466 | 0.4715 | 0.64545 | 0.09613 | 0.71411 | 0.1648 | -0.022888 | 0.027465 | -122.8455 | 0.004577 | 0.21515 | -0.10529 | 0.23804 | -0.082398 | 0.54016 | 122.6532 | 0.027465 | 0.036621 | 122.9233 | 122.9095 | 122.8546 | 122.8867 | -122.9279 | -122.8821 | 122.5845 | 0.013733 | 2.4307 | 1.1353
2358.1719 | 122.9553 | -57.1381 | 65.7074 | -0.052948 | -0.00066014 | 0.060957 | 0.067336 | -0.0038986 | 0.0041143 | 0.0032856 | 0.02002 | 0.00067495 | 0.0012818 | 0.0019824 | -0.0030013 | -0.0047253 | 0.0025891 | -54.7577 | 65.6479 | -57.1884 | 65.3961 | -56.6849 | -57.0786 | -56.5109 | -56.0211 | 65.712 | -57.2113 | -57.1655 | -57.2021 | -57.1838 | -56.7902 | -0.050354 | -0.059509 | -0.31128 | 0.45319 | 0.62714 | 0.05951 | 0.67749 | 0.10986 | -0.073242 | 0.004578 | -122.8729 | -0.064086 | 0.3479 | -0.045776 | 0.42114 | 0.027466 | 0.50354 | 122.5845 | 0.009156 | 0.045777 | 122.8363 | 122.9233 | 122.7859 | 122.85 | -122.8958 | -122.9187 | 122.5342 | -0.027465 | 2.3804 | 1.1169
2359.1719 | 122.9462 | -57.1747 | 65.6754 | -0.052948 | -1.9142e-05 | 0.061598 | 0.067763 | 0.00058737 | 0.0017645 | 0.001363 | -0.0074462 | -0.00060665 | 0.0014954 | 0.003905 | -0.00065151 | -0.0034437 | 0.0025891 | -54.7394 | 65.6799 | -57.2021 | 65.3915 | -56.7032 | -57.0969 | -56.5338 | -56.0532 | 65.6891 | -57.1838 | -57.1381 | -57.1793 | -57.28 | -56.9641 | -0.027465 | 0.004578 | -0.28381 | 0.4715 | 0.64087 | 0.07782 | 0.66833 | 0.10529 | -0.009155 | 0.013733 | -122.8134 | -0.004577 | 0.21057 | -0.10528 | 0.21973 | -0.09613 | 0.49896 | 122.5937 | 0.004578 | 0.045776 | 122.8821 | 122.8729 | 122.8546 | 122.8638 | -122.8775 | -122.8592 | 122.5662 | 0.036621 | 2.4353 | 1.1215
2360.1719 | 122.9874 | -57.1793 | 65.6479 | -0.075836 | 0.00083526 | 0.062453 | 0.0699 | 0.0010148 | -0.00058531 | 0.003072 | -0.01355 | -0.0021021 | 0.0012818 | 0.00048702 | -0.0025741 | -0.0051527 | -0.0010425 | -54.7119 | 65.6525 | -57.225 | 65.451 | -56.6666 | -57.0602 | -56.5063 | -55.9982 | 65.7028 | -57.1793 | -57.1152 | -57.1518 | -57.2617 | -56.9275 | -0.045777 | 0.004578 | -0.19684 | 0.5127 | 0.67291 | 0.11902 | 0.71869 | 0.16479 | 0 | 0.054932 | -122.7631 | 0.027466 | 0.25177 | -0.082398 | 0.25177 | -0.082398 | 0.55847 | 122.6761 | 0.027466 | 0.064087 | 122.8775 | 122.8821 | 122.8317 | 122.8821 | -122.8729 | -122.8271 | 122.6303 | 0.064087 | 2.4673 | 1.181
2361.1719 | 122.9782 | -57.1609 | 65.6479 | -0.037689 | 0.0014761 | 0.061171 | 0.0699 | 0.0010148 | 0.00069649 | 0.0062762 | 0.010864 | 0.0017431 | 0.00042723 | -0.00058098 | -0.0017197 | -0.0040845 | -0.00018806 | -54.7073 | 65.6799 | -57.2113 | 65.4282 | -56.6711 | -57.0694 | -56.5155 | -55.9891 | 65.6982 | -57.1884 | -57.1335 | -57.1243 | -57.2525 | -56.9458 | -0.050354 | 0.032044 | -0.21973 | 0.48981 | 0.64545 | 0.091553 | 0.6958 | 0.14191 | -0.027466 | 0.050354 | -122.7814 | 0.036621 | 0.21515 | -0.091552 | 0.24261 | -0.064086 | 0.54016 | 122.6395 | 0.064087 | 0.054932 | 122.8912 | 122.8867 | 122.8409 | 122.8592 | -122.8592 | -122.8363 | 122.5891 | 0.027466 | 2.4536 | 1.1719
2362.1719 | 122.9553 | -57.1518 | 65.6754 | -0.11398 | 0.0021171 | 0.061812 | 0.070113 | 0.0016556 | 0.0013373 | 0.002431 | 0.013916 | 0.00046135 | -0.00021357 | 0.003905 | -0.0012925 | -0.0051527 | 0.00023934 | -54.7119 | 65.6616 | -57.2159 | 65.4099 | -56.6849 | -57.0694 | -56.5247 | -56.0303 | 65.6891 | -57.1976 | -57.1747 | -57.1609 | -57.2754 | -56.955 | -0.064087 | -0.013733 | -0.2655 | 0.46692 | 0.62714 | 0.082397 | 0.69122 | 0.14648 | -0.045777 | 0.013733 | -122.85 | -0.009156 | 0.19684 | -0.1236 | 0.24262 | -0.07782 | 0.53101 | 122.6257 | 0.036621 | 0.022888 | 122.8775 | 122.8867 | 122.8134 | 122.8409 | -122.8912 | -122.8729 | 122.5616 | -0.022889 | 2.4399 | 1.1215
2363.1719 | 122.9828 | -57.1609 | 65.6662 | -0.045319 | 0.0014761 | 0.061171 | 0.067763 | 0.0044328 | 0.0032599 | 0.007558 | -0.01355 | 0.0011023 | 0.001068 | -0.00058098 | -0.00043791 | -0.0036573 | 0.0013073 | -54.7211 | 65.6799 | -57.2067 | 65.4373 | -56.6803 | -57.0511 | -56.5292 | -56.0028 | 65.6982 | -57.193 | -57.1289 | -57.1518 | -57.2525 | -56.9275 | -0.045776 | 0.013733 | -0.22888 | 0.48065 | 0.63171 | 0.10986 | 0.67749 | 0.15564 | -0.032043 | 0.032043 | -122.7951 | 0.009156 | 0.23346 | -0.091552 | 0.2655 | -0.059509 | 0.52643 | 122.644 | 0.041199 | 0.064087 | 122.8867 | 122.8912 | 122.8409 | 122.8592 | -122.8729 | -122.8592 | 122.5983 | 0.032044 | 2.4399 | 1.1581
2364.1719 | 122.9645 | -57.1747 | 65.6708 | -0.075836 | -0.0015145 | 0.062453 | 0.068832 | -0.0028304 | 0.0011237 | 0.00414 | 0.013916 | 0.00046135 | 0.001709 | -0.002931 | -0.0015061 | -0.0053663 | -0.00018806 | -54.5471 | 65.7303 | -57.1609 | 65.3915 | -56.7352 | -57.0831 | -56.5384 | -56.0257 | 65.712 | -57.1884 | -57.1564 | -57.1793 | -57.2662 | -56.955 | 0.013733 | 0.05951 | -0.27923 | 0.43945 | 0.63629 | 0.091553 | 0.62256 | 0.07782 | -0.013733 | 0.041199 | -122.8271 | -0.004577 | 0.21973 | -0.091552 | 0.23346 | -0.077819 | 0.42572 | 122.5525 | 0.009156 | 0.032044 | 122.8912 | 122.9004 | 122.905 | 122.8867 | -122.8317 | -122.8592 | 122.5662 | 0.018311 | 2.6276 | 1.149
2365.1719 | 122.9279 | -57.1884 | 65.6982 | -0.060578 | 0.00062166 | 0.062025 | 0.068832 | -0.00069423 | 0.00091009 | 0.0037128 | 0.041382 | 0.00024775 | 0.0023498 | -0.0010084 | -0.0034287 | -0.0057935 | 0.00023934 | -54.7211 | 65.6708 | -57.193 | 65.4419 | -56.6757 | -57.106 | -56.5109 | -56.0165 | 65.7074 | -57.1838 | -57.1701 | -57.1701 | -57.2342 | -56.9641 | -0.004577 | -0.027466 | -0.25635 | 0.5127 | 0.67749 | 0.082398 | 0.68207 | 0.086975 | 0.004578 | 0.009155 | -122.8683 | 0.018311 | 0.2243 | -0.045776 | 0.21973 | -0.050354 | 0.51727 | 122.6349 | 0.013733 | 0.013733 | 122.8638 | 122.8912 | 122.8592 | 122.8958 | -122.8912 | -122.8821 | 122.6303 | 0.018311 | 2.4673 | 1.1719
2366.1719 | 122.937 | -57.1381 | 65.6982 | -0.075836 | -0.0017281 | 0.059676 | 0.069045 | -0.0028304 | -0.0018671 | 0.0062762 | -0.0013428 | 0.0017431 | 0.00064083 | -0.00229 | -0.0019333 | -0.0034437 | 0.0030163 | -54.7348 | 65.6891 | -57.193 | 65.4327 | -56.7947 | -57.28 | -56.5338 | -56.0577 | 65.6937 | -57.2205 | -57.1564 | -57.1838 | -57.2891 | -56.9641 | -0.054931 | -0.009155 | -0.2655 | 0.34332 | 0.60425 | -0.14191 | 0.65918 | -0.086975 | -0.082397 | -0.004577 | -122.8546 | -0.045776 | 0.17395 | -0.15106 | 0.25635 | -0.068665 | 0.39825 | 122.6257 | 0.036621 | 0.064087 | 122.8821 | 122.9141 | 122.8271 | 122.8317 | -122.8912 | -122.9187 | 122.5708 | -0.01831 | 2.4033 | 1.0803
2367.1719 | 122.9736 | -57.1518 | 65.6845 | -0.045319 | -0.00087374 | 0.060103 | 0.069045 | -0.0024032 | 0.0015509 | 0.0049946 | 0.0047608 | 0.0015295 | 0.00085443 | 0.0054004 | -0.00086511 | -0.0051527 | 0.00088014 | -54.7348 | 65.657 | -57.1747 | 65.4144 | -56.7032 | -57.0923 | -56.5155 | -56.012 | 65.7074 | -57.1701 | -57.1335 | -57.1426 | -57.2525 | -56.9366 | -0.022889 | -0.027466 | -0.27008 | 0.44861 | 0.63629 | 0.059509 | 0.65918 | 0.082398 | -0.018311 | 0.022888 | -122.818 | 0.009155 | 0.21515 | -0.10071 | 0.23346 | -0.082397 | 0.4715 | 122.5891 | 0.027466 | 0.036621 | 122.8317 | 122.8775 | 122.8088 | 122.8592 | -122.8592 | -122.8546 | 122.5662 | 0.01831 | 2.417 | 1.1398
2368.1719 | 122.9828 | -57.1472 | 65.7028 | 0.038605 | 0.00062166 | 0.060744 | 0.070327 | 0.00037377 | 0.00026909 | 0.0047808 | -0.0013428 | 0.0017431 | 0.00085443 | -0.0020764 | -0.0034287 | -0.0042981 | 0.0010937 | -54.7256 | 65.6891 | -57.225 | 65.4053 | -56.694 | -57.074 | -56.5384 | -56.0394 | 65.6982 | -57.193 | -57.1381 | -57.1655 | -57.2571 | -56.9504 | -0.07782 | -0.013733 | -0.29755 | 0.45319 | 0.60883 | 0.073242 | 0.68665 | 0.15106 | -0.045776 | -0.004578 | -122.8409 | -0.01831 | 0.19684 | -0.10986 | 0.24262 | -0.064087 | 0.53101 | 122.6303 | 0.027466 | 0.054931 | 122.9141 | 122.8912 | 122.8363 | 122.8455 | -122.9279 | -122.8958 | 122.5525 | 0.009155 | 2.4216 | 1.1078
2369.1719 | 122.9233 | -57.1838 | 65.625 | 0.008087 | 0.00083526 | 0.064375 | 0.068618 | 0.00251 | 0.00026909 | 0.0022174 | -0.025757 | 0.0015295 | 0.001068 | 0.00091422 | -0.0017197 | -0.0042981 | 2.554e-05 | -54.7668 | 65.6296 | -57.2205 | 65.3687 | -56.781 | -57.1838 | -56.6071 | -56.0944 | 65.6708 | -57.2525 | -57.2021 | -57.2617 | -57.3624 | -57.019 | -0.036621 | 0.004578 | -0.25635 | 0.40283 | 0.57678 | 0 | 0.6134 | 0.036621 | -0.068664 | 0.045776 | -122.8271 | -0.07782 | 0.16479 | -0.17853 | 0.23346 | -0.10986 | 0.43945 | 122.5891 | -0.009156 | 0.050354 | 122.85 | 122.9233 | 122.8134 | 122.8546 | -122.8455 | -122.8775 | 122.5525 | -0.01831 | 2.417 | 1.0895
2370.1719 | 122.9645 | -57.1747 | 65.6616 | -0.037689 | 0.00019446 | 0.061598 | 0.070113 | 0.0022964 | 0.00048269 | 0.0045672 | 0.02002 | 0.0015295 | 0.00064083 | -0.0065626 | -0.0012925 | -0.0038709 | 0.0028027 | -54.7577 | 65.6891 | -57.2113 | 65.4053 | -56.6986 | -57.0923 | -56.543 | -56.0349 | 65.7303 | -57.2113 | -57.1655 | -57.193 | -57.2754 | -56.9641 | -0.036621 | 0.027466 | -0.25635 | 0.47608 | 0.63171 | 0.082398 | 0.66833 | 0.11902 | -0.036621 | 0.068665 | -122.8271 | -0.01831 | 0.21057 | -0.10071 | 0.24719 | -0.064087 | 0.5127 | 122.6166 | 0.018311 | 0.045777 | 122.9004 | 122.9416 | 122.8638 | 122.905 | -122.8729 | -122.8729 | 122.58 | 0.009156 | 2.417 | 1.1398
2371.1719 | 122.9004 | -57.1884 | 65.6342 | -0.098725 | 0.00062166 | 0.063948 | 0.069686 | 0.0061416 | 0.0021917 | 0.0071308 | -0.037964 | 0.00067495 | 0.00064083 | -0.001222 | -0.0025741 | -0.0055799 | 0.0013073 | -54.7897 | 65.625 | -57.2388 | 65.332 | -56.781 | -57.1884 | -56.5887 | -56.0944 | 65.6845 | -57.2342 | -57.0831 | -57.2983 | -57.312 | -56.9595 | -0.050354 | -0.009155 | -0.30212 | 0.40741 | 0.59967 | 0 | 0.65002 | 0.050354 | -0.045776 | 0.050354 | -122.7173 | -0.10986 | 0.22888 | -0.1236 | 0.27466 | -0.07782 | 0.45776 | 122.5708 | -0.064087 | 0.15106 | 122.8638 | 122.9187 | 122.8134 | 122.8729 | -122.8729 | -122.8683 | 122.5204 | 0.10529 | 2.3987 | 1.0941
2372.1719 | 122.9599 | -57.1838 | 65.6891 | -0.052948 | -0.00066014 | 0.061385 | 0.069045 | -0.001976 | 0.0017645 | 0.0086262 | -0.0043946 | 3.4148e-05 | 0.0029906 | 0.0024096 | 0.00020289 | -0.0032301 | 0.0013073 | -54.744 | 65.6982 | -57.1793 | 65.3275 | -56.8222 | -57.0557 | -56.5475 | -56.0532 | 65.6799 | -57.2021 | -57.1564 | -57.1747 | -57.2754 | -56.9687 | 0.004578 | 0.009155 | -0.36163 | 0.36163 | 0.63629 | 0.12817 | 0.63171 | 0.1236 | -0.01831 | -0.009155 | -122.8455 | 0.009155 | 0.21515 | -0.091553 | 0.23346 | -0.073243 | 0.35706 | 122.5067 | 0.027465 | 0.045776 | 122.8775 | 122.8821 | 122.8821 | 122.8638 | -122.8683 | -122.8912 | 122.5113 | 0.027466 | 2.4399 | 1.1307
2373.1719 | 122.9187 | -57.1655 | 65.7074 | -0.0071715 | -0.0019417 | 0.06053 | 0.067977 | -0.0011214 | 5.5488e-05 | 0.0028582 | -0.025757 | -0.00060665 | 0.0021362 | -0.0014356 | -0.0025741 | -0.0055799 | 2.554e-05 | -54.7348 | 65.6754 | -57.2113 | 65.4099 | -56.6895 | -57.0099 | -56.3416 | -56.131 | 65.6982 | -57.1976 | -57.1609 | -57.1701 | -57.2571 | -56.9504 | -0.045777 | -0.032043 | -0.29755 | 0.47607 | 0.82397 | 0.15564 | 0.86975 | 0.20142 | -0.032044 | -0.009155 | -122.8683 | -0.004578 | 0.21515 | -0.091553 | 0.24719 | -0.059509 | 0.52185 | 122.6212 | 0.027466 | 0.036621 | 122.8867 | 122.8958 | 122.8409 | 122.8638 | -122.9187 | -122.905 | 122.5754 | 0.004577 | 2.4307 | 1.0345
2374.1719 | 123.024 | -57.1793 | 65.5975 | -0.18265 | 0.0014761 | 0.063521 | 0.068618 | 0.003151 | 0.0021917 | 0.0028582 | 0.026123 | 0.00024775 | 0.0014954 | -0.0018628 | -0.0023605 | -0.0057935 | 0.0013073 | -54.7119 | 65.6021 | -57.2021 | 65.4648 | -56.5979 | -57.0465 | -56.4789 | -55.925 | 65.6067 | -57.1976 | -57.0786 | -57.1152 | -57.225 | -56.9 | -0.022888 | 0.004578 | -0.13275 | 0.58136 | 0.70038 | 0.13275 | 0.72327 | 0.15564 | -0.018311 | 0.009155 | -122.6761 | 0.064087 | 0.27924 | -0.045777 | 0.29755 | -0.027466 | 0.60425 | 122.6669 | 0.082398 | 0.11902 | 122.8043 | 122.8043 | 122.7814 | 122.7859 | -122.7997 | -122.7951 | 122.644 | 0.10071 | 2.4673 | 1.2543
2375.1719 | 122.9507 | -57.1518 | 65.7074 | -0.022431 | 0.00083526 | 0.060744 | 0.069045 | 0.0010148 | 0.0011237 | 0.0032856 | -0.0074462 | 0.0021703 | 0.0014954 | 0.0034778 | -0.0012925 | -0.0030163 | 0.0017345 | -54.7302 | 65.6845 | -57.1884 | 65.4053 | -56.7032 | -57.074 | -56.5292 | -56.0349 | 65.6937 | -57.1655 | -57.1564 | -57.1701 | -57.2662 | -56.955 | -0.036622 | -0.022888 | -0.30212 | 0.44861 | 0.62256 | 0.077819 | 0.65918 | 0.11444 | -0.013733 | -0.013732 | -122.8638 | -0.018311 | 0.19684 | -0.11444 | 0.21057 | -0.10071 | 0.48523 | 122.5937 | -0.004578 | 0.009155 | 122.8729 | 122.8592 | 122.8363 | 122.8455 | -122.8958 | -122.8729 | 122.5571 | -0.004578 | 2.4216 | 1.1169
2376.1719 | 122.9828 | -57.1838 | 65.7074 | -0.083466 | -0.00044654 | 0.061812 | 0.067977 | 0.0063554 | -0.00015811 | 0.0020038 | 0.0047608 | 0.0013159 | -0.00085457 | -0.006349 | -0.0032151 | -0.0023755 | 0.0010937 | -54.7211 | 65.6754 | -57.2113 | 65.4419 | -56.7032 | -57.0786 | -56.543 | -56.0211 | 65.7257 | -57.193 | -57.1472 | -57.1793 | -57.2662 | -56.9458 | -0.027466 | -0.032043 | -0.2655 | 0.48065 | 0.64087 | 0.10529 | 0.66833 | 0.13275 | -0.009155 | 0.018311 | -122.8546 | 0.004578 | 0.23804 | -0.082397 | 0.24719 | -0.073242 | 0.50812 | 122.6532 | 0.013733 | 0.045776 | 122.8867 | 122.9187 | 122.8592 | 122.9095 | -122.9187 | -122.9004 | 122.6257 | 0.036621 | 2.4628 | 1.1627
2377.1719 | 122.937 | -57.1701 | 65.6845 | -0.10635 | -0.0023691 | 0.061171 | 0.069045 | -0.001976 | -0.00015811 | 0.0032856 | 0.013916 | 0.0011023 | 0.0014954 | 0.0036914 | -0.0012925 | -0.0038709 | 0.0013073 | -54.6204 | 65.7074 | -57.1564 | 65.3824 | -56.7078 | -57.0877 | -56.5384 | -56.0349 | 65.6937 | -57.1793 | -57.1564 | -57.1564 | -57.2845 | -56.955 | 0.013733 | 0.022888 | -0.30212 | 0.46234 | 0.63171 | 0.082397 | 0.61798 | 0.068664 | -0.009155 | 0.009156 | -122.8409 | 0.013733 | 0.21515 | -0.11444 | 0.2243 | -0.10529 | 0.44861 | 122.5388 | 0.022888 | 0.022888 | 122.8638 | 122.8729 | 122.8775 | 122.8638 | -122.8409 | -122.8638 | 122.5525 | 0.013733 | 2.5497 | 1.1353
2378.1719 | 122.9462 | -57.1747 | 65.6799 | -0.083466 | -0.00087374 | 0.061598 | 0.067763 | 0.0027238 | 0.0015509 | 0.0062762 | -0.022705 | 0.0015295 | 0.001068 | -0.0052808 | -0.0027877 | -0.0042981 | 0.0010937 | -54.7394 | 65.6891 | -57.1793 | 65.3 | -56.7947 | -57.0511 | -56.5338 | -56.0394 | 65.7211 | -57.2067 | -57.1518 | -57.1747 | -57.2754 | -56.955 | -0.004577 | 0.009155 | -0.37994 | 0.37994 | 0.64087 | 0.1236 | 0.64545 | 0.12817 | -0.032043 | 0.041198 | -122.8317 | 0 | 0.21973 | -0.10071 | 0.25177 | -0.068665 | 0.38452 | 122.4792 | 0.032043 | 0.054932 | 122.8683 | 122.9279 | 122.8638 | 122.8958 | -122.8592 | -122.8867 | 122.4747 | 0.022889 | 2.4353 | 1.1353
2379.1719 | 122.9507 | -57.193 | 65.6296 | 0.084381 | 0.00083526 | 0.061812 | 0.069686 | 0.0012284 | 0.0028327 | 0.005849 | -0.034912 | -0.00060665 | 0.00085443 | 0.001128 | -0.0032151 | -0.0040845 | 0.00023934 | -54.8218 | 65.6433 | -57.2342 | 65.3595 | -56.7719 | -57.1564 | -56.6025 | -56.0486 | 65.657 | -57.2433 | -57.1747 | -57.1976 | -57.3578 | -56.9824 | -0.041199 | 0.013733 | -0.27008 | 0.42114 | 0.59052 | 0.036621 | 0.63171 | 0.07782 | -0.050354 | 0.027465 | -122.8043 | -0.004578 | 0.21057 | -0.16479 | 0.26093 | -0.11444 | 0.46234 | 122.5937 | 0.045776 | 0.068664 | 122.8775 | 122.9004 | 122.8363 | 122.85 | -122.8638 | -122.8729 | 122.5525 | 0.01831 | 2.3712 | 1.1444
2380.1719 | 122.9782 | -57.1747 | 65.6799 | -0.075836 | -0.0015145 | 0.061385 | 0.069045 | -0.0017624 | 0.0028327 | 0.0047808 | -0.0043946 | 0.0015295 | 0.00085443 | -0.0016492 | 0.00084389 | -0.0040845 | 0.00088014 | -54.7165 | 65.6799 | -57.2113 | 65.4327 | -56.7078 | -57.0694 | -56.543 | -56.0349 | 65.712 | -57.1976 | -57.1289 | -57.1609 | -57.2525 | -56.9366 | -0.036621 | 0 | -0.24719 | 0.46692 | 0.63171 | 0.10529 | 0.66833 | 0.14191 | -0.022888 | 0.032043 | -122.8088 | 0.013733 | 0.23804 | -0.077819 | 0.26093 | -0.054931 | 0.50354 | 122.644 | 0.036621 | 0.068665 | 122.8912 | 122.9095 | 122.8546 | 122.8867 | -122.8912 | -122.8775 | 122.6074 | 0.045777 | 2.4582 | 1.1398
2381.1719 | 122.9462 | -57.1518 | 65.6662 | -0.037689 | 0.0021171 | 0.063521 | 0.067977 | -0.00026703 | 0.0017645 | 0.0039264 | -0.0043946 | 0.0028113 | 0.001709 | 0.0015552 | -0.0044967 | -0.0042981 | -0.0016833 | -54.689 | 65.6708 | -57.2205 | 65.4373 | -56.6711 | -57.0648 | -56.5155 | -55.9753 | 65.6982 | -57.1609 | -57.106 | -57.1472 | -57.2479 | -56.9321 | -0.068665 | 0.004577 | -0.22888 | 0.48065 | 0.63629 | 0.086975 | 0.70496 | 0.15564 | -0.009156 | 0.032043 | -122.7722 | 0.004577 | 0.21973 | -0.096131 | 0.22888 | -0.086975 | 0.54932 | 122.6578 | 0.013733 | 0.054932 | 122.8912 | 122.8592 | 122.8226 | 122.85 | -122.8867 | -122.8271 | 122.5891 | 0.045776 | 2.4628 | 1.1765
2382.1719 | 122.9691 | -57.1518 | 65.6845 | -0.037689 | 0.0014761 | 0.060957 | 0.068191 | 0.0022964 | 0.0019781 | 0.0045672 | -0.01355 | 0.00024775 | 0.0014954 | 0.0028368 | -0.00086511 | -0.0042981 | 0.00088014 | -54.7028 | 65.6799 | -57.1838 | 65.4327 | -56.6711 | -57.0511 | -56.5155 | -55.9799 | 65.7257 | -57.1884 | -57.1014 | -57.1243 | -57.2479 | -56.9275 | -0.032044 | -0.004577 | -0.25177 | 0.48065 | 0.63629 | 0.10071 | 0.66833 | 0.13275 | -0.036622 | 0.041199 | -122.7859 | 0.027465 | 0.2243 | -0.096131 | 0.26093 | -0.059509 | 0.5127 | 122.6166 | 0.064087 | 0.086976 | 122.8638 | 122.9141 | 122.8317 | 122.8775 | -122.8683 | -122.8729 | 122.5845 | 0.050354 | 2.449 | 1.1719
2383.1719 | 122.9874 | -57.1472 | 65.6616 | -0.014801 | -0.0021555 | 0.061385 | 0.069045 | -0.0038986 | 0.0032599 | 0.0037128 | -0.0043946 | -0.00017945 | 0.0012818 | -0.0027174 | -0.0023605 | -0.0028027 | -0.0018971 | -54.7211 | 65.7074 | -57.1793 | 65.4373 | -56.6849 | -57.0557 | -56.5018 | -55.9845 | 65.6845 | -57.1609 | -57.1198 | -57.1381 | -57.2296 | -56.9183 | -0.032043 | 0.045776 | -0.2243 | 0.46234 | 0.64545 | 0.091553 | 0.67749 | 0.1236 | -0.013733 | 0.022888 | -122.7814 | 0.009155 | 0.22888 | -0.082397 | 0.24262 | -0.068664 | 0.49439 | 122.6166 | 0.022888 | 0.041199 | 122.8867 | 122.8455 | 122.8546 | 122.8317 | -122.8409 | -122.8226 | 122.5845 | 0.027466 | 2.4261 | 1.1627
2384.1719 | 122.9828 | -57.1747 | 65.6982 | -0.075836 | 0.0016899 | 0.061171 | 0.069045 | 0.0044328 | 0.0011237 | 0.0026446 | 0.001709 | 3.4148e-05 | -0.00042717 | 0.0041186 | -0.00022431 | -0.0036573 | 0.00023934 | -54.6844 | 65.6754 | -57.2113 | 65.4327 | -56.6574 | -57.0786 | -56.5201 | -55.9616 | 65.7028 | -57.2021 | -57.106 | -57.1472 | -57.2433 | -56.9321 | -0.036621 | -0.022888 | -0.2655 | 0.51727 | 0.6546 | 0.096131 | 0.69122 | 0.13275 | -0.027465 | 0.004578 | -122.8043 | 0.027466 | 0.24262 | -0.068664 | 0.27008 | -0.041199 | 0.55389 | 122.644 | 0.054931 | 0.09613 | 122.8867 | 122.905 | 122.85 | 122.8775 | -122.9095 | -122.9004 | 122.6074 | 0.068665 | 2.4902 | 1.2131
2385.1719 | 122.9553 | -57.1518 | 65.6479 | -0.068207 | 0.0010489 | 0.060744 | 0.069686 | 0.00058737 | 0.0013373 | 0.0037128 | 0.013916 | 0.0019567 | 0.00064083 | -0.0016492 | 0.00063009 | -0.0032301 | 0.0025891 | -54.6844 | 65.6799 | -57.1976 | 65.4602 | -56.6528 | -57.0694 | -56.5155 | -55.9845 | 65.6891 | -57.1701 | -57.1014 | -57.1564 | -57.2525 | -56.9229 | -0.045777 | 0.032044 | -0.18768 | 0.49896 | 0.63629 | 0.082397 | 0.68207 | 0.12817 | -0.018311 | 0.041199 | -122.7493 | -0.004578 | 0.22888 | -0.10071 | 0.24719 | -0.082397 | 0.54474 | 122.6578 | 0.013733 | 0.068665 | 122.8775 | 122.8592 | 122.8317 | 122.8409 | -122.8455 | -122.818 | 122.612 | 0.050354 | 2.4673 | 1.1673
2386.1719 | 122.9462 | -57.1701 | 65.6845 | -0.014801 | -0.00044654 | 0.060744 | 0.069045 | -0.0038986 | 0.0026191 | 0.0060626 | 0.023071 | 0.0013159 | 0.00021363 | 0.0015552 | -0.0017197 | -0.0081433 | 0.0019483 | -54.744 | 65.7028 | -57.1976 | 65.4144 | -56.6711 | -57.0648 | -56.5292 | -56.0349 | 65.7257 | -57.1976 | -57.1106 | -57.2845 | -57.3807 | -56.9824 | -0.027466 | 0.018311 | -0.27008 | 0.49896 | 0.64087 | 0.10529 | 0.66834 | 0.13275 | -0.027466 | 0.041199 | -122.7951 | -0.11444 | 0.18768 | -0.21057 | 0.21515 | -0.1831 | 0.52643 | 122.612 | -0.086975 | 0.086975 | 122.9004 | 122.9233 | 122.8729 | 122.8958 | -122.8821 | -122.8821 | 122.5845 | 0.059509 | 2.4261 | 1.1353
2387.1719 | 122.9691 | -57.1609 | 65.6662 | -0.045319 | -0.00023294 | 0.060744 | 0.068832 | 0.0044328 | 0.0011237 | 0.0032856 | -0.0074462 | 0.00024775 | -0.00085457 | 0.0041186 | -0.0034287 | -0.0042981 | 0.0017345 | -54.6753 | 65.7028 | -57.1793 | 65.451 | -56.6757 | -57.0511 | -56.5109 | -55.9891 | 65.6982 | -57.1701 | -57.106 | -57.1381 | -57.2617 | -56.9321 | -0.01831 | 0.036621 | -0.21515 | 0.48523 | 0.65002 | 0.10986 | 0.66833 | 0.12817 | -0.009155 | 0.032043 | -122.7722 | 0.022888 | 0.22888 | -0.10071 | 0.23804 | -0.091553 | 0.50354 | 122.6303 | 0.032043 | 0.064087 | 122.8821 | 122.8683 | 122.8638 | 122.8592 | -122.8455 | -122.8363 | 122.612 | 0.054932 | 2.4857 | 1.1719
2388.1719 | 122.9874 | -57.1655 | 65.6662 | -0.03006 | -0.00044654 | 0.062239 | 0.0699 | 0.00080117 | 0.0013373 | 0.0064898 | 0.023071 | 0.00067495 | 0.0012818 | -0.0025036 | -0.0032151 | -0.0025891 | 0.00045294 | -54.7119 | 65.6845 | -57.1976 | 65.4419 | -56.6666 | -57.0511 | -56.5247 | -55.9937 | 65.712 | -57.1747 | -57.1152 | -57.1289 | -57.2571 | -56.9321 | -0.032044 | 0.01831 | -0.2243 | 0.49896 | 0.64087 | 0.11444 | 0.67291 | 0.14649 | -0.009156 | 0.045776 | -122.7814 | 0.036621 | 0.23346 | -0.091553 | 0.24262 | -0.082397 | 0.53101 | 122.6395 | 0.045777 | 0.05951 | 122.8821 | 122.8867 | 122.85 | 122.8775 | -122.8638 | -122.8409 | 122.6074 | 0.050354 | 2.4536 | 1.1719
2389.1719 | 122.9691 | -57.1655 | 65.6891 | -0.091095 | -0.00023294 | 0.061598 | 0.068618 | 0.00080117 | -0.00015811 | 0.0049946 | -0.022705 | -0.00039305 | 0.0019226 | -0.0037854 | -0.00043791 | -0.0030163 | -0.0038197 | -54.689 | 65.657 | -57.193 | 65.451 | -56.6483 | -57.0648 | -56.5247 | -55.957 | 65.6937 | -57.1701 | -57.1243 | -57.1381 | -57.2525 | -56.9183 | -0.027466 | -0.032044 | -0.23804 | 0.51727 | 0.64087 | 0.10071 | 0.66833 | 0.12817 | -0.004578 | 0.004578 | -122.8134 | 0.027465 | 0.24719 | -0.086975 | 0.25177 | -0.082397 | 0.54474 | 122.644 | 0.032043 | 0.045776 | 122.85 | 122.8638 | 122.8226 | 122.8592 | -122.8821 | -122.8592 | 122.6166 | 0.041198 | 2.4765 | 1.2085
2390.1719 | 123.0011 | -57.1518 | 65.6662 | -0.083466 | 0.0029715 | 0.062025 | 0.068618 | -0.0028304 | 0.0026191 | 0.0020038 | -0.0074462 | 3.4148e-05 | 0.0025634 | -0.001222 | -0.0034287 | -0.0015211 | 0.0013073 | -54.6707 | 65.6616 | -57.1976 | 65.4327 | -56.6483 | -57.0602 | -56.5109 | -55.9616 | 65.6845 | -57.1838 | -57.0969 | -57.1472 | -57.2662 | -56.9183 | -0.045777 | -0.004578 | -0.23346 | 0.50354 | 0.64087 | 0.091552 | 0.68665 | 0.13733 | -0.032044 | 0.01831 | -122.7631 | 0.004577 | 0.23346 | -0.11444 | 0.2655 | -0.082397 | 0.54932 | 122.6303 | 0.036621 | 0.086975 | 122.8592 | 122.8683 | 122.8134 | 122.8363 | -122.8638 | -122.85 | 122.5845 | 0.054931 | 2.4811 | 1.1902
2391.1719 | 122.9691 | -57.1426 | 65.6662 | -0.014801 | 0.0016899 | 0.063521 | 0.069259 | -0.0034714 | 0.00069649 | 0.0054218 | 0.0047608 | 0.0017431 | -0.00064077 | -0.001222 | -0.0023605 | -0.0025891 | 0.00023934 | -54.6844 | 65.6891 | -57.193 | 65.4465 | -56.6483 | -57.0511 | -56.5018 | -55.9708 | 65.6891 | -57.1838 | -57.1152 | -57.1564 | -57.2708 | -56.9229 | -0.050354 | 0.022888 | -0.21973 | 0.49439 | 0.64087 | 0.091553 | 0.69122 | 0.14191 | -0.041199 | 0.022888 | -122.7814 | -0.013733 | 0.21973 | -0.12817 | 0.26093 | -0.086975 | 0.54474 | 122.6395 | 0.027466 | 0.068665 | 122.8821 | 122.8729 | 122.8317 | 122.8317 | -122.8592 | -122.85 | 122.5891 | 0.027466 | 2.4582 | 1.1719
2392.1719 | 122.9919 | -57.1655 | 65.6799 | -0.014801 | 0.0019035 | 0.063094 | 0.067336 | 0.0010148 | 0.0039007 | 0.0043536 | 0.013916 | 0.0011023 | 0.001709 | 0.002196 | -0.0023605 | -0.0047253 | -0.00040166 | -54.689 | 65.7028 | -57.2021 | 65.4373 | -56.6666 | -57.0374 | -56.5109 | -55.9662 | 65.712 | -57.1793 | -57.1106 | -57.1472 | -57.2342 | -56.9275 | -0.036621 | 0.022888 | -0.24262 | 0.49896 | 0.6546 | 0.12817 | 0.69122 | 0.16479 | -0.013733 | 0.032043 | -122.7905 | 0.01831 | 0.23804 | -0.068665 | 0.25177 | -0.054932 | 0.53558 | 122.6395 | 0.032043 | 0.068664 | 122.905 | 122.8912 | 122.8683 | 122.8775 | -122.8821 | -122.8592 | 122.6028 | 0.054931 | 2.4765 | 1.1993
2393.1719 | 122.9828 | -57.1381 | 65.7211 | -0.014801 | 0.00083526 | 0.060957 | 0.065627 | 0.0012284 | 0.00048269 | 0.00414 | 0.053589 | 0.00088875 | 0.003418 | 0.00070062 | -0.0012925 | -0.0028027 | 0.0034435 | -54.7348 | 65.6799 | -57.1609 | 65.4099 | -56.6849 | -57.0786 | -56.5018 | -56.0257 | 65.7074 | -57.1655 | -57.1472 | -57.1655 | -57.2571 | -56.9641 | -0.022888 | -0.041198 | -0.31128 | 0.45319 | 0.63629 | 0.05951 | 0.65918 | 0.082398 | -0.027465 | -0.013733 | -122.8683 | -0.027465 | 0.17395 | -0.11902 | 0.20142 | -0.091553 | 0.47608 | 122.5708 | 0 | 0.01831 | 122.8409 | 122.8729 | 122.818 | 122.8455 | -122.8821 | -122.8867 | 122.5479 | -0.009155 | 2.4033 | 1.1124
2394.1719 | 122.9965 | -57.1335 | 65.6525 | -0.052948 | -0.00044654 | 0.061171 | 0.068618 | -0.0030442 | 0.0026191 | 0.0011494 | 0.0078126 | 0.00046135 | 0.00042723 | -0.0084852 | -0.0017197 | -0.0049389 | -0.00040166 | -54.6844 | 65.712 | -57.1838 | 65.4602 | -56.6711 | -57.0374 | -56.5063 | -55.9799 | 65.7303 | -57.1747 | -57.1014 | -57.1289 | -57.2571 | -56.9229 | -0.050354 | 0.059509 | -0.19226 | 0.46234 | 0.62714 | 0.09613 | 0.67749 | 0.14648 | -0.041199 | 0.07782 | -122.7539 | 0.004578 | 0.21057 | -0.1236 | 0.25177 | -0.082397 | 0.5127 | 122.644 | 0.045777 | 0.073243 | 122.8958 | 122.905 | 122.8455 | 122.8638 | -122.8363 | -122.8271 | 122.5937 | 0.032044 | 2.449 | 1.1536
2395.1719 | 122.9828 | -57.1335 | 65.7028 | -0.083466 | -0.00023294 | 0.06288 | 0.069472 | -0.00069423 | 0.0026191 | 0.0071308 | 0.016968 | 0.0021703 | 0.00021363 | -0.00015378 | -0.0012925 | -0.0038709 | -0.00018806 | -54.6707 | 65.6937 | -57.193 | 65.4282 | -56.662 | -57.0511 | -56.5155 | -55.9799 | 65.6845 | -57.1564 | -57.1152 | -57.1426 | -57.2388 | -56.9229 | -0.059509 | -0.009155 | -0.27466 | 0.4715 | 0.61798 | 0.082398 | 0.67749 | 0.14191 | -0.022888 | -0.018311 | -122.818 | -0.009155 | 0.21057 | -0.10529 | 0.23346 | -0.082398 | 0.53101 | 122.6212 | 0.013733 | 0.041199 | 122.8867 | 122.8409 | 122.8271 | 122.818 | -122.8958 | -122.8592 | 122.5616 | 0.018311 | 2.4628 | 1.1536
2396.1719 | 123.0011 | -57.1564 | 65.657 | -0.068207 | -1.9142e-05 | 0.061812 | 0.069045 | -0.003685 | 0.0024053 | 0.0045672 | -0.0013428 | 0.0032385 | 0.00021363 | 0.00048702 | -0.0012925 | -0.0036573 | 0.00023934 | -54.7028 | 65.6662 | -57.2342 | 65.4465 | -56.662 | -57.0602 | -56.5292 | -55.9662 | 65.7028 | -57.1976 | -57.1106 | -57.0877 | -57.4127 | -57.019 | -0.07782 | 0.009156 | -0.21057 | 0.49438 | 0.62714 | 0.09613 | 0.70496 | 0.17395 | -0.041199 | 0.045777 | -122.7676 | 0.068664 | 0.13733 | -0.25635 | 0.17853 | -0.21515 | 0.5722 | 122.6807 | 0.10986 | 0.086975 | 122.9004 | 122.9004 | 122.8226 | 122.8592 | -122.8912 | -122.8546 | 122.6028 | 0.045776 | 2.4536 | 1.1902
2397.1719 | 122.9095 | -57.1793 | 65.6387 | -0.083466 | 0.0021171 | 0.063094 | 0.069045 | -0.0021896 | 0.0021917 | 0.0069172 | 0.0078126 | 0.0023839 | 0.00085443 | -0.0014356 | -0.0023605 | -0.0028027 | -0.0027515 | -54.6844 | 65.6708 | -57.2067 | 65.4465 | -56.6391 | -57.0557 | -56.5292 | -55.9479 | 65.6754 | -57.1793 | -57.1106 | -57.1701 | -57.2479 | -56.8954 | -0.027466 | 0.032043 | -0.19226 | 0.54016 | 0.65002 | 0.1236 | 0.67749 | 0.15106 | 0 | 0.036621 | -122.7493 | 0.009155 | 0.28381 | -0.068665 | 0.28381 | -0.068665 | 0.56763 | 122.6532 | 0.009155 | 0.068664 | 122.8775 | 122.8546 | 122.85 | 122.8546 | -122.8455 | -122.818 | 122.6257 | 0.068664 | 2.4948 | 1.2314
2398.1719 | 122.9782 | -57.1518 | 65.6708 | -0.068207 | 0.00019446 | 0.061171 | 0.068618 | 0.0016556 | 0.0019781 | 0.0052082 | 0.026123 | 0.00088875 | 0.00064083 | -0.0027174 | -0.0036423 | -0.0013073 | 2.554e-05 | -54.7028 | 65.6799 | -57.2021 | 65.4282 | -56.6711 | -57.0557 | -56.5109 | -55.9891 | 65.712 | -57.1609 | -57.1289 | -57.1426 | -57.2433 | -56.9321 | -0.050354 | 0.009156 | -0.24261 | 0.48065 | 0.64087 | 0.09613 | 0.69122 | 0.14648 | -0.009156 | 0.041199 | -122.7997 | 0.009155 | 0.21973 | -0.091553 | 0.22888 | -0.082397 | 0.53101 | 122.6303 | 0.018311 | 0.032044 | 122.8821 | 122.8729 | 122.8317 | 122.8638 | -122.8729 | -122.8317 | 122.58 | 0.022888 | 2.449 | 1.1627
2399.1719 | 122.9782 | -57.1518 | 65.6982 | -0.014801 | 0.0025443 | 0.062025 | 0.068191 | 0.0022964 | 0.0017645 | 0.0022174 | 0.010864 | 0.00046135 | 0.00042723 | -0.00079478 | -0.0019333 | -0.0025891 | 2.554e-05 | -54.6936 | 65.6754 | -57.2021 | 65.451 | -56.6895 | -57.0511 | -56.5063 | -55.9845 | 65.712 | -57.1976 | -57.1243 | -57.1335 | -57.2479 | -56.9275 | -0.050354 | -0.022888 | -0.24719 | 0.46234 | 0.64545 | 0.10071 | 0.6958 | 0.15106 | -0.045777 | 0.013733 | -122.8226 | 0.01831 | 0.2243 | -0.096131 | 0.27008 | -0.050354 | 0.5127 | 122.6532 | 0.064087 | 0.073242 | 122.8775 | 122.9095 | 122.8271 | 122.8638 | -122.9004 | -122.8958 | 122.6028 | 0.027465 | 2.4582 | 1.1673
2400.1719 | 122.9462 | -57.1655 | 65.6891 | -0.037689 | 0.0012625 | 0.061598 | 0.068618 | -0.0015488 | 0.00048269 | 0.0026446 | -0.14172 | 0.0025975 | -0.0025636 | 0.0047594 | 0.00041649 | -0.0042981 | 0.00045294 | -54.7211 | 65.6937 | -57.2021 | 65.4099 | -56.6986 | -57.0786 | -56.5384 | -55.7556 | 65.6799 | -57.1793 | -57.1426 | -57.1335 | -57.2891 | -56.9412 | -0.036621 | 0.004578 | -0.27924 | 0.46692 | 0.62714 | 0.086975 | 0.66376 | 0.1236 | -0.013733 | -0.009155 | -122.8317 | 0.032043 | 0.2243 | -0.1236 | 0.23804 | -0.10986 | 0.50354 | 122.612 | 0.045776 | 0.036621 | 122.8958 | 122.8592 | 122.8592 | 122.8455 | -122.8912 | -122.8683 | 122.5754 | 0.022888 | 2.4445 | 1.4099
2401.1719 | 122.9782 | -57.1747 | 65.7028 | -0.10635 | -0.00087374 | 0.061171 | 0.068191 | -0.00048063 | 0.0011237 | 0.0052082 | -0.010498 | 0.0015295 | -0.00021357 | 0.0047594 | -0.0010787 | -0.0047253 | -0.0021107 | -54.6936 | 65.6387 | -57.2342 | 65.4556 | -56.6437 | -57.074 | -56.5109 | -55.957 | 65.7074 | -57.1793 | -57.1335 | -57.1655 | -57.2479 | -56.9229 | -0.059509 | -0.064087 | -0.24719 | 0.53101 | 0.66376 | 0.10071 | 0.72327 | 0.16022 | -0.004577 | 0.004577 | -122.8363 | 0.009156 | 0.25177 | -0.073242 | 0.25635 | -0.068665 | 0.59052 | 122.6898 | 0.013733 | 0.045776 | 122.8729 | 122.8867 | 122.8134 | 122.8821 | -122.937 | -122.8821 | 122.6303 | 0.041199 | 2.4811 | 1.2177
2402.1719 | 122.9691 | -57.1472 | 65.657 | -0.068207 | 0.00062166 | 0.062239 | 0.068191 | 0.0033646 | 0.0017645 | 0.0073444 | 0.0047608 | -0.0016749 | 0.001709 | -0.002931 | -0.0019333 | -0.0036573 | -0.0018971 | -54.6799 | 65.6616 | -57.193 | 65.4556 | -56.6483 | -57.0648 | -56.5338 | -55.9616 | 65.6891 | -57.1884 | -57.1243 | -57.1472 | -57.2525 | -56.9321 | -0.045776 | 0.004578 | -0.20142 | 0.49896 | 0.6134 | 0.082398 | 0.65918 | 0.12817 | -0.041199 | 0.032044 | -122.7814 | 0 | 0.21515 | -0.10529 | 0.25635 | -0.064086 | 0.54474 | 122.6486 | 0.041199 | 0.064087 | 122.8546 | 122.8775 | 122.8088 | 122.8363 | -122.85 | -122.8455 | 122.6028 | 0.022888 | 2.4673 | 1.1856
2403.1719 | 122.9691 | -57.1518 | 65.6708 | -0.075836 | -0.00087374 | 0.060957 | 0.069686 | -0.00048063 | -0.0016535 | 0.0054218 | -0.025757 | 0.0019567 | -0.0010682 | 0.003905 | -0.0017197 | -0.0053663 | -0.0014697 | -54.6524 | 65.6754 | -57.193 | 65.4556 | -56.6574 | -57.0602 | -56.5292 | -55.9708 | 65.7166 | -57.1747 | -57.1152 | -57.1426 | -57.2479 | -56.9138 | -0.041199 | 0.004578 | -0.21515 | 0.49438 | 0.62256 | 0.091552 | 0.66376 | 0.13275 | -0.022889 | 0.045777 | -122.7859 | 0.009155 | 0.23804 | -0.096131 | 0.26093 | -0.073242 | 0.53558 | 122.6486 | 0.032044 | 0.05951 | 122.8683 | 122.8912 | 122.8271 | 122.8683 | -122.8638 | -122.8455 | 122.6074 | 0.036621 | 2.4994 | 1.181
2404.1719 | 122.9919 | -57.1701 | 65.6662 | 0.008087 | -1.9142e-05 | 0.061385 | 0.068618 | 0.0050736 | 0.00026909 | 0.0052082 | -0.0013428 | 0.00067495 | 0.0014954 | -0.0014356 | -0.0023605 | -0.0034437 | 0.00088014 | -54.689 | 65.657 | -57.1884 | 65.4556 | -56.662 | -57.074 | -56.5155 | -55.9616 | 65.6845 | -57.193 | -57.1014 | -57.1472 | -57.2342 | -56.9229 | -0.018311 | -0.009156 | -0.21057 | 0.50812 | 0.6546 | 0.09613 | 0.67291 | 0.11444 | -0.022888 | 0.01831 | -122.7676 | 0.022888 | 0.24719 | -0.064087 | 0.27008 | -0.041199 | 0.52643 | 122.644 | 0.045776 | 0.091553 | 122.8455 | 122.8775 | 122.8271 | 122.8546 | -122.8546 | -122.8592 | 122.6257 | 0.068665 | 2.4811 | 1.2085
2405.1719 | 122.9736 | -57.1564 | 65.6662 | -0.052948 | 0.00083526 | 0.059676 | 0.069686 | -5.343e-05 | 0.0019781 | 0.0037128 | -0.016602 | 0.00088875 | 2.8e-08 | 0.0026232 | -0.0017197 | -0.0038709 | 2.554e-05 | -54.6844 | 65.6799 | -57.1976 | 65.4373 | -56.6483 | -57.0786 | -56.5201 | -55.9616 | 65.7303 | -57.1747 | -57.1106 | -57.1472 | -57.2433 | -56.9138 | -0.041199 | 0.013733 | -0.22888 | 0.50812 | 0.63629 | 0.07782 | 0.67749 | 0.11902 | -0.018311 | 0.064087 | -122.7768 | 0.009155 | 0.24262 | -0.086975 | 0.26093 | -0.068664 | 0.54932 | 122.6349 | 0.027466 | 0.064087 | 122.8775 | 122.905 | 122.8363 | 122.8867 | -122.8638 | -122.8409 | 122.5937 | 0.045776 | 2.4719 | 1.1948
2406.1719 | 122.9874 | -57.1472 | 65.6387 | -0.022431 | 0.00062166 | 0.060744 | 0.068618 | 0.0010148 | -0.00015811 | 0.0054218 | -0.0013428 | 0.0030249 | 0.0019226 | -0.0035718 | -1.0706e-05 | -0.0045117 | -0.0012561 | -54.6066 | 65.657 | -57.1838 | 65.4602 | -56.6528 | -57.0694 | -56.5109 | -55.957 | 65.6799 | -57.1701 | -57.106 | -57.1609 | -57.2433 | -56.9183 | -0.036621 | 0.01831 | -0.17853 | 0.49439 | 0.63629 | 0.07782 | 0.67291 | 0.11444 | -0.022888 | 0.041199 | -122.7448 | -0.013733 | 0.22888 | -0.09613 | 0.25177 | -0.073242 | 0.53101 | 122.644 | 0.009155 | 0.064087 | 122.8409 | 122.85 | 122.8043 | 122.8271 | -122.8226 | -122.8088 | 122.6074 | 0.041199 | 2.5406 | 1.1902
2407.1719 | 122.9874 | -57.1655 | 65.6662 | -0.091095 | -0.0017281 | 0.06288 | 0.070541 | 0.0027238 | 0.00026909 | 0.0062762 | -0.019653 | 0.00046135 | 0.00064083 | -0.0044262 | -0.0015061 | -0.0036573 | -0.0016833 | -54.6707 | 65.657 | -57.1884 | 65.451 | -56.6483 | -57.0694 | -56.543 | -55.9341 | 65.6937 | -57.1838 | -57.1198 | -57.1243 | -57.2617 | -56.9275 | -0.022889 | -0.009156 | -0.21515 | 0.51727 | 0.62256 | 0.09613 | 0.64545 | 0.11902 | -0.018311 | 0.027466 | -122.786 | 0.041198 | 0.23804 | -0.096131 | 0.25635 | -0.07782 | 0.54016 | 122.6395 | 0.059509 | 0.064087 | 122.8455 | 122.8775 | 122.8226 | 122.8592 | -122.8546 | -122.85 | 122.6166 | 0.045776 | 2.4948 | 1.2314
2408.1719 | 122.9324 | -57.1793 | 65.6754 | 0.084381 | 0.00019446 | 0.062025 | 0.069472 | -5.343e-05 | 0.0039007 | 0.0043536 | -0.028809 | -0.00017945 | 0.0012818 | -0.001222 | -0.0027877 | -0.0064343 | 0.0025891 | -54.6936 | 65.6754 | -57.1884 | 65.419 | -56.7215 | -57.1152 | -56.5567 | -56.0349 | 65.7074 | -57.2021 | -57.1747 | -57.2067 | -57.3212 | -56.9641 | -0.009156 | 0 | -0.25635 | 0.45776 | 0.62256 | 0.064087 | 0.63171 | 0.073243 | -0.022888 | 0.032043 | -122.85 | -0.027466 | 0.21515 | -0.14191 | 0.23804 | -0.11902 | 0.46692 | 122.6074 | -0.004578 | 0.027465 | 122.8638 | 122.9095 | 122.8546 | 122.8867 | -122.8638 | -122.8775 | 122.5983 | 0.004577 | 2.4857 | 1.1444
2409.1719 | 122.9462 | -57.1793 | 65.6342 | -0.091095 | 0.0014761 | 0.062239 | 0.067763 | -0.0011214 | 0.00069649 | 0.0034992 | -0.010498 | 0.0013159 | 0.0029906 | -0.0020764 | -0.0015061 | -0.0047253 | -0.0016833 | -54.6204 | 65.657 | -57.2021 | 65.3778 | -56.6345 | -57.0923 | -56.5796 | -56.0761 | 65.6799 | -57.1976 | -57.1564 | -57.2021 | -57.3349 | -56.9824 | -0.022888 | 0.022888 | -0.25635 | 0.54474 | 0.59967 | 0.086975 | 0.62256 | 0.10986 | -0.018311 | 0.045777 | -122.7905 | -0.022888 | 0.19684 | -0.15564 | 0.21515 | -0.13733 | 0.56763 | 122.58 | -0.004577 | 0.041199 | 122.8592 | 122.8775 | 122.8363 | 122.8592 | -122.8363 | -122.8317 | 122.5571 | 0.022888 | 2.5589 | 1.1032
2410.1719 | 122.9324 | -57.1884 | 65.657 | -0.045319 | 0.00083526 | 0.06288 | 0.073958 | -0.00090783 | 0.0024053 | 0.001363 | 0.026123 | 0.0013159 | 0.0012818 | 0.0019824 | -0.00065151 | -0.0034437 | 0.0030163 | -54.7119 | 65.6754 | -57.225 | 65.5563 | -56.5155 | -57.2067 | -56.5842 | -56.0944 | 65.712 | -57.1884 | -57.1747 | -57.2296 | -57.3257 | -56.9733 | -0.036621 | 0.018311 | -0.10071 | 0.67291 | 0.60425 | -0.01831 | 0.64087 | 0.018311 | 0 | 0.054932 | -122.8317 | -0.041198 | 0.21515 | -0.13733 | 0.21515 | -0.13733 | 0.70953 | 122.7814 | -0.041198 | 0.013733 | 122.9004 | 122.9004 | 122.8638 | 122.9004 | -122.8821 | -122.8455 | 122.7448 | 0.013733 | 2.4765 | 1.0941
2411.1719 | 122.9187 | -57.1701 | 65.6387 | -0.060578 | -0.00087374 | 0.062239 | 0.070327 | 0.0078506 | -0.00015811 | 0.0037128 | 0.056641 | 0.00046135 | 0.003418 | -0.0037854 | -0.0021469 | -0.0042981 | -0.0014697 | -54.7165 | 65.6662 | -57.2159 | 65.3915 | -56.4331 | -57.0557 | -56.6299 | -56.1127 | 65.7211 | -57.193 | -57.1701 | -57.2205 | -57.3395 | -56.9687 | -0.045776 | 0.027466 | -0.24719 | 0.737 | 0.54016 | 0.11444 | 0.58594 | 0.16022 | -0.022888 | 0.082397 | -122.8088 | -0.050354 | 0.20142 | -0.16937 | 0.2243 | -0.14648 | 0.78278 | 122.6074 | -0.027466 | 0.022888 | 122.8821 | 122.9141 | 122.8363 | 122.8912 | -122.8546 | -122.8317 | 122.5616 | 0 | 2.4536 | 1.0574
2412.1719 | 122.9462 | -57.1655 | 65.6387 | -0.098725 | 0.00019446 | 0.064162 | 0.071181 | 0.0035782 | -0.0014399 | 0.0026446 | -0.0043946 | 0.0015295 | 0.0025634 | -0.0010084 | -0.0017197 | -0.0038709 | -0.00061526 | -54.7165 | 65.6662 | -57.225 | 65.625 | -56.6437 | -57.2205 | -56.5659 | -56.0715 | 65.7303 | -57.1976 | -57.1747 | -57.225 | -57.3303 | -56.9687 | -0.05951 | 0.027466 | -0.013733 | 0.52185 | 0.59967 | -0.054932 | 0.65918 | 0.004578 | -0.032044 | 0.091553 | -122.8134 | -0.05951 | 0.19684 | -0.1648 | 0.22888 | -0.13275 | 0.58136 | 122.85 | -0.027466 | 0.022888 | 122.8912 | 122.9279 | 122.8317 | 122.8958 | -122.8638 | -122.8363 | 122.7905 | -0.009156 | 2.449 | 1.0941
2413.1719 | 122.8867 | -57.1884 | 65.6845 | -0.11398 | 0.0012625 | 0.062666 | 0.06755 | -0.00026703 | 0.0021917 | 0.0056354 | -0.028809 | 3.4148e-05 | 0.001068 | -0.00015378 | -0.00086511 | -0.0049389 | 0.0032299 | -54.6707 | 65.6754 | -57.1884 | 65.3961 | -56.7215 | -57.1289 | -56.6025 | -56.0669 | 65.6891 | -57.2113 | -57.1609 | -57.2159 | -57.3486 | -56.9916 | 0 | -0.009155 | -0.28839 | 0.46692 | 0.58594 | 0.05951 | 0.58594 | 0.05951 | -0.022888 | 0.004578 | -122.8455 | -0.027465 | 0.19684 | -0.16022 | 0.21973 | -0.13733 | 0.46692 | 122.5845 | -0.004577 | 0.050354 | 122.8638 | 122.9004 | 122.8638 | 122.8775 | -122.8729 | -122.8958 | 122.5845 | 0.027466 | 2.5177 | 1.1215
2414.1719 | 122.9507 | -57.1609 | 65.657 | -0.56412 | 0.0019035 | 0.062453 | 0.068191 | 0.00080117 | 0.0036871 | 0.0043536 | 0.013916 | -0.00039305 | 0.0012818 | 0.0032642 | -0.00065151 | -0.0045117 | -0.0012561 | -54.5746 | 65.6204 | -57.2525 | 65.3732 | -56.749 | -57.1381 | -56.5796 | -56.0715 | 65.7166 | -57.2296 | -57.1472 | -57.2159 | -57.2937 | -56.9733 | -0.091552 | -0.036621 | -0.28381 | 0.41199 | 0.58136 | 0.022888 | 0.67291 | 0.11444 | -0.068664 | 0.05951 | -122.8043 | -0.054931 | 0.18768 | -0.13275 | 0.25635 | -0.064087 | 0.50354 | 122.6257 | 0.013733 | 0.082397 | 122.8729 | 122.9462 | 122.7814 | 122.8775 | -122.9095 | -122.8867 | 122.5342 | 0.013733 | 2.5864 | 1.0895
2415.1719 | 123.024 | -57.1472 | 65.6296 | -0.12161 | 0.0010489 | 0.060316 | 0.069472 | -0.0011214 | 0.0034735 | 0.0056354 | 0.02002 | 0.00088875 | 0.0019226 | -0.001222 | -0.0036423 | -0.0034437 | -0.00061526 | -54.7073 | 65.6525 | -57.2067 | 65.419 | -56.6757 | -57.0877 | -56.543 | -55.9799 | 65.6433 | -57.1701 | -57.0602 | -57.1243 | -57.2433 | -56.8817 | -0.059509 | 0.022888 | -0.21057 | 0.4715 | 0.60425 | 0.059509 | 0.66376 | 0.11902 | -0.022888 | 0.013733 | -122.6898 | 0.022888 | 0.2655 | -0.09613 | 0.28839 | -0.073242 | 0.53101 | 122.6257 | 0.045776 | 0.10986 | 122.8592 | 122.8134 | 122.7997 | 122.7905 | -122.8363 | -122.7997 | 122.5662 | 0.086975 | 2.4399 | 1.1673
2416.1719 | 123.0927 | -57.1243 | 65.6387 | -0.10635 | -1.9142e-05 | 0.062453 | 0.06755 | 0.001442 | 0.0024053 | 0.0049946 | 0.013916 | -0.00039305 | 2.8e-08 | 0.00027342 | -0.0044967 | -0.0021619 | 0.0013073 | -54.6661 | 65.6387 | -57.2021 | 65.4648 | -56.6391 | -57.0602 | -56.5063 | -55.9387 | 65.657 | -57.1793 | -57.0511 | -57.0923 | -57.2021 | -56.8542 | -0.077819 | 0 | -0.17395 | 0.48523 | 0.61798 | 0.064087 | 0.6958 | 0.14191 | -0.054931 | 0.01831 | -122.6898 | 0.032044 | 0.27008 | -0.077819 | 0.32501 | -0.022888 | 0.56305 | 122.6669 | 0.086975 | 0.12817 | 122.8409 | 122.8363 | 122.7631 | 122.7814 | -122.8409 | -122.818 | 122.5891 | 0.073243 | 2.4582 | 1.1856
2417.1719 | 123.0606 | -57.1152 | 65.6113 | -0.075836 | -0.00023294 | 0.06288 | 0.067123 | 0.0033646 | 0.00069649 | 0.0060626 | 0.02002 | 0.0011023 | -0.0010682 | -0.00464 | -0.0025741 | -0.0034437 | -0.0018971 | -54.6249 | 65.6113 | -57.1747 | 65.4831 | -56.6208 | -57.0419 | -56.4789 | -55.9067 | 65.6158 | -57.1793 | -57.0557 | -57.0831 | -57.1838 | -56.8497 | -0.05951 | 0 | -0.12817 | 0.49438 | 0.63629 | 0.073242 | 0.6958 | 0.13275 | -0.064087 | 0.004578 | -122.6669 | 0.032043 | 0.2655 | -0.068665 | 0.32959 | -0.004578 | 0.55389 | 122.6578 | 0.09613 | 0.1236 | 122.7859 | 122.7951 | 122.7264 | 122.731 | -122.7859 | -122.7905 | 122.5983 | 0.059509 | 2.4902 | 1.2085
2418.1719 | 123.0194 | -57.1381 | 65.6067 | -0.12161 | -0.0010873 | 0.062453 | 0.070968 | -0.0024032 | 0.0024053 | 0.0047808 | -0.019653 | -0.00060665 | 2.8e-08 | -0.0020764 | -0.0017197 | -0.0042981 | -0.0016833 | -54.6021 | 65.6067 | -57.1838 | 65.5014 | -56.6071 | -57.0328 | -56.4835 | -55.9113 | 65.657 | -57.1701 | -57.0374 | -57.0786 | -57.1701 | -56.9916 | -0.045776 | 0 | -0.10529 | 0.53101 | 0.6546 | 0.10529 | 0.70038 | 0.15106 | -0.032043 | 0.050354 | -122.644 | 0.05951 | 0.14648 | -0.032043 | 0.17853 | 0 | 0.57678 | 122.6852 | 0.091553 | 0.13275 | 122.7905 | 122.8271 | 122.7448 | 122.7951 | -122.7905 | -122.7768 | 122.6395 | 0.10071 | 2.536 | 1.2268
2419.1719 | 123.0652 | -57.1198 | 65.6204 | -0.12161 | 0.00083526 | 0.061812 | 0.067336 | -0.00069423 | 0.0013373 | 0.0032856 | 0.010864 | 0.00067495 | -0.00021357 | -0.0027174 | -0.0012925 | -0.0055799 | 0.0015209 | -54.6066 | 65.6204 | -57.1655 | 65.5151 | -56.6025 | -57.0419 | -56.4651 | -55.8517 | 65.6204 | -57.193 | -57.0694 | -57.0602 | -57.1518 | -56.8497 | -0.045776 | 0 | -0.10529 | 0.51727 | 0.6546 | 0.07782 | 0.70038 | 0.1236 | -0.073242 | 0 | -122.6898 | 0.059509 | 0.27008 | -0.032043 | 0.34332 | 0.041199 | 0.56305 | 122.6807 | 0.13275 | 0.1236 | 122.7859 | 122.8134 | 122.7402 | 122.7402 | -122.7859 | -122.8134 | 122.6349 | 0.050354 | 2.5131 | 1.268
2420.1719 | 123.024 | -57.1289 | 65.6433 | -0.1445 | 0.00062166 | 0.062453 | 0.070113 | -0.0013352 | 0.0015509 | 0.0069172 | -0.010498 | -0.00082025 | 0.001068 | 0.0088184 | -0.0015061 | -0.0034437 | -0.00018806 | -54.6204 | 65.6342 | -57.193 | 65.4739 | -56.6254 | -57.0236 | -56.4697 | -55.9067 | 65.6525 | -57.1793 | -57.0374 | -57.0923 | -57.193 | -56.8497 | -0.064087 | -0.009156 | -0.16937 | 0.50354 | 0.65918 | 0.10529 | 0.72327 | 0.16937 | -0.050354 | 0.009155 | -122.6807 | 0.036621 | 0.27924 | -0.064087 | 0.32959 | -0.013733 | 0.56763 | 122.6669 | 0.086975 | 0.14191 | 122.8271 | 122.8317 | 122.7631 | 122.7814 | -122.8363 | -122.8226 | 122.6028 | 0.091552 | 2.5085 | 1.2222
2421.1719 | 123.0377 | -57.1198 | 65.6296 | -0.075836 | -0.00023294 | 0.061598 | 0.067123 | -0.0041122 | 0.00069649 | 0.0043536 | 0.029175 | 0.00067495 | 0.0012818 | -0.00079478 | -0.0032151 | -0.0047253 | 0.00045294 | -54.5059 | 65.6342 | -57.1518 | 65.5243 | -56.5842 | -57.0328 | -56.4468 | -55.8929 | 65.6525 | -57.1381 | -57.0419 | -57.0877 | -57.1747 | -56.8588 | -0.032043 | 0.004577 | -0.10529 | 0.53558 | 0.67291 | 0.086975 | 0.70496 | 0.11902 | -0.018311 | 0.022888 | -122.6715 | 0.032043 | 0.26093 | -0.054932 | 0.27924 | -0.036621 | 0.56763 | 122.6761 | 0.050354 | 0.096131 | 122.7859 | 122.7905 | 122.7539 | 122.7722 | -122.7814 | -122.7676 | 122.644 | 0.07782 | 2.6138 | 1.2268
2422.1719 | 123.0331 | -57.1152 | 65.6708 | -0.11398 | -0.00044654 | 0.060957 | 0.067123 | -0.0021896 | 0.0017645 | 0.0043536 | 0.062744 | -0.0048793 | 0.00042723 | -0.0050672 | -0.0019333 | -0.0049389 | -0.0029651 | -54.6433 | 65.6662 | -57.1655 | 65.4877 | -56.6437 | -57.0374 | -56.456 | -55.8243 | 65.6799 | -57.1381 | -57.0465 | -57.106 | -57.2113 | -56.8954 | -0.050354 | -0.004577 | -0.1831 | 0.4715 | 0.65918 | 0.077819 | 0.70953 | 0.12817 | -0.022889 | 0.009156 | -122.7173 | 0.009155 | 0.21973 | -0.096131 | 0.24262 | -0.073242 | 0.52185 | 122.6532 | 0.032044 | 0.091553 | 122.8317 | 122.818 | 122.7814 | 122.7951 | -122.8363 | -122.8088 | 122.6028 | 0.068664 | 2.4719 | 1.2909
2423.1719 | 123.0331 | -57.1198 | 65.6799 | -0.091095 | -1.9142e-05 | 0.06053 | 0.067336 | -0.0026168 | -0.0012261 | 0.0049946 | 0.041382 | -0.00017945 | -0.001709 | -0.0033582 | -0.0032151 | -0.0047253 | -0.0021107 | -54.6112 | 65.6754 | -57.1472 | 65.506 | -56.6849 | -57.0786 | -56.4789 | -55.9479 | 65.6799 | -57.1655 | -57.0557 | -57.074 | -57.1747 | -56.868 | -0.027466 | -0.004578 | -0.17395 | 0.43488 | 0.64087 | 0.041199 | 0.66833 | 0.068665 | -0.045776 | 0 | -122.7356 | 0.045776 | 0.25177 | -0.054932 | 0.29755 | -0.009156 | 0.46234 | 122.6532 | 0.091552 | 0.10986 | 122.8226 | 122.8455 | 122.7951 | 122.7997 | -122.8271 | -122.8455 | 122.6257 | 0.064087 | 2.5085 | 1.1719
2424.1719 | 123.056 | -57.1152 | 65.6754 | 0.015716 | 0.00019446 | 0.063307 | 0.070113 | 0.00080117 | 0.0011237 | 0.0047808 | 0.023071 | 0.0011023 | -0.001709 | -0.0061352 | -0.0032151 | -0.0079297 | -0.0014697 | -54.6433 | 65.6937 | -57.1472 | 65.4785 | -56.6208 | -57.0282 | -56.4651 | -55.9433 | 65.7028 | -57.1426 | -57.0419 | -57.0648 | -57.1793 | -56.8726 | -0.032044 | 0.018311 | -0.19684 | 0.49438 | 0.65002 | 0.086975 | 0.68207 | 0.11902 | -0.027466 | 0.027466 | -122.7173 | 0.050354 | 0.24261 | -0.064087 | 0.27008 | -0.036621 | 0.52643 | 122.6257 | 0.07782 | 0.10071 | 122.8409 | 122.8455 | 122.8088 | 122.818 | -122.8226 | -122.818 | 122.5937 | 0.073242 | 2.4719 | 1.1719
2425.1719 | 123.024 | -57.0877 | 65.6799 | -0.091095 | 0.0023307 | 0.061385 | 0.069045 | -5.343e-05 | 0.0019781 | 0.0052082 | 0.023071 | -0.00039305 | 0.001709 | -0.0018628 | -0.0027877 | -0.0047253 | 2.554e-05 | -54.5975 | 65.6616 | -57.1609 | 65.5243 | -56.6254 | -57.0236 | -56.4377 | -55.925 | 65.7074 | -57.1335 | -57.0236 | -57.0602 | -57.1518 | -56.8497 | -0.073242 | -0.018311 | -0.15564 | 0.46234 | 0.65002 | 0.064087 | 0.72327 | 0.13733 | -0.045776 | 0.027465 | -122.7036 | 0.027466 | 0.23804 | -0.064086 | 0.28381 | -0.01831 | 0.53558 | 122.6852 | 0.073242 | 0.10986 | 122.8226 | 122.8409 | 122.7493 | 122.7951 | -122.8409 | -122.8134 | 122.612 | 0.064087 | 2.4902 | 1.1627
2426.1719 | 123.0423 | -57.1014 | 65.6754 | -0.10635 | -0.0019417 | 0.061385 | 0.069045 | 0.004219 | 0.00026909 | 0.0071308 | 0.029175 | 0.0017431 | 0.00021363 | -0.0078442 | -0.0019333 | -0.0068615 | -0.0033923 | -54.6021 | 65.6754 | -57.1655 | 65.5334 | -56.6071 | -56.9962 | -56.4423 | -55.9021 | 65.6937 | -57.1564 | -57.0328 | -57.0465 | -57.1426 | -56.8634 | -0.064087 | 0 | -0.14191 | 0.49438 | 0.65918 | 0.10528 | 0.72327 | 0.16937 | -0.054932 | 0.018311 | -122.7081 | 0.054931 | 0.23804 | -0.041199 | 0.29297 | 0.013733 | 0.55847 | 122.699 | 0.10986 | 0.1236 | 122.8409 | 122.85 | 122.7768 | 122.7951 | -122.8409 | -122.8317 | 122.6349 | 0.068664 | 2.4994 | 1.1993
2427.1719 | 123.0103 | -57.1106 | 65.6891 | -0.098725 | -0.00044654 | 0.062453 | 0.068618 | 0.00058737 | 5.5488e-05 | 0.002431 | -0.0043946 | -0.00082025 | -0.0010682 | -0.0027174 | -0.0034287 | -0.0040845 | -0.0012561 | -54.5883 | 65.6525 | -57.1472 | 65.5197 | -56.6299 | -57.0419 | -56.4651 | -55.8289 | 65.7211 | -57.1426 | -57.0557 | -57.0511 | -57.1976 | -56.8817 | -0.036621 | -0.036621 | -0.16937 | 0.48065 | 0.64545 | 0.068665 | 0.68207 | 0.10529 | -0.032043 | 0.032043 | -122.7448 | 0.05951 | 0.22888 | -0.086975 | 0.26093 | -0.054932 | 0.51727 | 122.6669 | 0.091553 | 0.086975 | 122.7997 | 122.8638 | 122.7631 | 122.8317 | -122.8363 | -122.8317 | 122.6303 | 0.054932 | 2.5223 | 1.2817
2428.1719 | 123.0652 | -57.106 | 65.7074 | -0.10635 | 0.00083526 | 0.059248 | 0.069686 | -0.0024032 | -0.00037171 | 0.0060626 | 0.010864 | -0.0014613 | -0.00064077 | 0.0036914 | -0.0030013 | -0.0036573 | -0.0012561 | -54.57 | 65.6845 | -57.1426 | 65.538 | -56.5887 | -56.9962 | -56.4194 | -55.8792 | 65.6937 | -57.1289 | -57.0053 | -57.0282 | -57.1381 | -56.8451 | -0.036621 | -0.022888 | -0.16937 | 0.51727 | 0.68664 | 0.10986 | 0.72327 | 0.14648 | -0.022888 | -0.013732 | -122.7127 | 0.07782 | 0.26093 | -0.032044 | 0.28381 | -0.009156 | 0.55389 | 122.6807 | 0.10071 | 0.1236 | 122.8271 | 122.8226 | 122.7905 | 122.7997 | -122.85 | -122.8363 | 122.644 | 0.10071 | 2.536 | 1.2268
2429.1719 | 123.0606 | -57.0786 | 65.7074 | -0.12161 | -0.00044654 | 0.062453 | 0.067123 | 0.0016556 | 0.0019781 | 0.0045672 | 0.026123 | 0.00024775 | 0.0014954 | -0.0014356 | -0.0019333 | -0.0045117 | 0.0013073 | -54.5334 | 65.6845 | -57.1564 | 65.5884 | -56.5155 | -56.9229 | -56.3782 | -55.8014 | 65.7303 | -57.0969 | -56.955 | -56.9733 | -57.0831 | -56.7764 | -0.07782 | -0.022888 | -0.11902 | 0.56305 | 0.70038 | 0.15564 | 0.7782 | 0.23346 | -0.018311 | 0.022889 | -122.6624 | 0.10529 | 0.30212 | -0.004578 | 0.32043 | 0.013733 | 0.64087 | 122.7448 | 0.1236 | 0.14191 | 122.8409 | 122.8271 | 122.7631 | 122.8088 | -122.8638 | -122.8043 | 122.6669 | 0.1236 | 2.5452 | 1.2772
2430.1719 | 123.0606 | -57.074 | 65.712 | -0.2742 | 0.00083526 | 0.060957 | 0.069259 | -0.00048063 | 0.00048269 | 0.0017902 | 0.013916 | -0.00039305 | -0.00021357 | 0.00070062 | -1.0706e-05 | -0.0032301 | 0.00045294 | -54.4739 | 65.6616 | -57.1243 | 65.5792 | -56.5063 | -56.9183 | -56.4011 | -55.8151 | 65.7394 | -57.106 | -56.987 | -57.0007 | -57.0877 | -56.8359 | -0.050354 | -0.050354 | -0.13275 | 0.56763 | 0.67291 | 0.15564 | 0.72327 | 0.20599 | -0.032043 | 0.027466 | -122.699 | 0.073243 | 0.23804 | -0.013733 | 0.27008 | 0.01831 | 0.61798 | 122.7036 | 0.10529 | 0.11902 | 122.7859 | 122.8455 | 122.7356 | 122.8134 | -122.8363 | -122.818 | 122.6532 | 0.086975 | 2.6001 | 1.2588
2431.1719 | 123.0606 | -57.0557 | 65.7669 | -0.075836 | -0.00023294 | 0.060103 | 0.067123 | -5.343e-05 | 0.0019781 | 0.0037128 | -0.0013428 | -0.00017945 | -0.00021357 | 0.003905 | -0.0017197 | -0.0040845 | -0.0010425 | -54.4968 | 65.7028 | -57.1014 | 65.593 | -56.4926 | -56.9183 | -56.3644 | -55.7877 | 65.712 | -57.0969 | -56.9504 | -56.9916 | -57.0923 | -56.813 | -0.045776 | -0.064087 | -0.17395 | 0.56305 | 0.69122 | 0.13733 | 0.737 | 0.1831 | -0.041199 | -0.054932 | -122.7173 | 0.064087 | 0.24262 | -0.036621 | 0.28381 | 0.004578 | 0.60882 | 122.6944 | 0.10529 | 0.14648 | 122.8043 | 122.8088 | 122.7585 | 122.7676 | -122.8683 | -122.8638 | 122.6486 | 0.10529 | 2.5589 | 1.268
2432.1719 | 123.024 | -57.0648 | 65.7715 | -0.075836 | -0.00023294 | 0.060957 | 0.066909 | -0.0017624 | 0.0026191 | 0.0045672 | 0.029175 | 0.00024775 | 0.00085443 | 0.0026232 | -0.0021469 | -0.0042981 | -0.0042469 | -54.4968 | 65.6891 | -57.1152 | 65.6021 | -56.4835 | -56.9092 | -56.3644 | -55.7831 | 65.712 | -57.1014 | -56.955 | -56.9778 | -57.0694 | -56.7856 | -0.050354 | -0.082397 | -0.16937 | 0.58136 | 0.70038 | 0.15564 | 0.75073 | 0.20599 | -0.036621 | -0.059509 | -122.7264 | 0.086975 | 0.27924 | -0.004578 | 0.31586 | 0.032043 | 0.63171 | 122.7173 | 0.1236 | 0.14648 | 122.8043 | 122.8134 | 122.7539 | 122.7768 | -122.8867 | -122.8729 | 122.6669 | 0.10986 | 2.5681 | 1.2817
2433.1719 | 123.0927 | -57.0602 | 65.6982 | -0.091095 | -0.00044654 | 0.060744 | 0.06755 | -0.0034714 | -0.00015811 | 0.0043536 | -0.0013428 | 0.0011023 | 0.00064083 | 0.0068958 | -0.0012925 | -0.0028027 | -0.0014697 | -54.5013 | 65.6662 | -57.1198 | 65.6067 | -56.4743 | -56.9321 | -56.3873 | -55.7785 | 65.7211 | -57.1106 | -56.9412 | -56.955 | -57.0465 | -56.7673 | -0.059509 | -0.032043 | -0.091553 | 0.58594 | 0.67291 | 0.12817 | 0.73242 | 0.18768 | -0.050354 | 0.022888 | -122.6395 | 0.10529 | 0.29297 | 0.013733 | 0.34332 | 0.064087 | 0.64545 | 122.7264 | 0.15564 | 0.16937 | 122.786 | 122.8317 | 122.7264 | 122.7814 | -122.818 | -122.8088 | 122.6669 | 0.11902 | 2.5589 | 1.2817
2434.1719 | 123.0331 | -57.074 | 65.6891 | -0.083466 | 0.0010489 | 0.062025 | 0.066268 | 0.00016017 | 0.0021917 | 0.0037128 | 0.013916 | -0.0010339 | 2.8e-08 | 0.002196 | -0.0012925 | -0.0040845 | 0.00088014 | -54.5288 | 65.6891 | -57.1472 | 65.538 | -56.5613 | -56.9778 | -56.4239 | -55.8884 | 65.7166 | -57.1335 | -56.9824 | -57.0099 | -57.106 | -56.813 | -0.073242 | 0 | -0.15106 | 0.5127 | 0.65002 | 0.096131 | 0.72327 | 0.16937 | -0.059509 | 0.027466 | -122.6715 | 0.064087 | 0.26093 | -0.032043 | 0.32044 | 0.027466 | 0.58594 | 122.6852 | 0.1236 | 0.15106 | 122.8363 | 122.85 | 122.7631 | 122.7905 | -122.8363 | -122.8226 | 122.612 | 0.091553 | 2.5452 | 1.1856
2435.1719 | 122.9141 | -57.1198 | 65.7303 | -0.12924 | 0.00062166 | 0.061385 | 0.068618 | 0.0050736 | 0.00048269 | 0.0067036 | -0.12341 | 0.00088875 | 0.00021363 | 0.010955 | -0.0015061 | -0.0015211 | 0.00066654 | -54.57 | 65.6754 | -57.1701 | 65.4602 | -56.6849 | -57.0923 | -56.5521 | -55.9891 | 65.7623 | -57.1564 | -57.1106 | -57.1747 | -57.28 | -56.9366 | -0.050354 | -0.054932 | -0.27008 | 0.43488 | 0.56763 | 0.027466 | 0.61798 | 0.07782 | -0.036621 | 0.032043 | -122.8409 | -0.054932 | 0.1831 | -0.16022 | 0.21973 | -0.1236 | 0.48523 | 122.6303 | -0.018311 | 0.045776 | 122.8455 | 122.9187 | 122.7951 | 122.8821 | -122.9004 | -122.8867 | 122.58 | 0.009155 | 2.5497 | 1.1307
2436.1719 | 123.0377 | -57.0602 | 65.7211 | 0.16067 | 0.0010489 | 0.063307 | 0.068404 | 0.0010148 | 0.0021917 | 0.0073444 | -0.016602 | -0.00017945 | -0.0014954 | -0.0048536 | -0.0023605 | -0.0040845 | -0.0018971 | -54.6982 | 65.7074 | -57.106 | 65.6067 | -56.5109 | -56.9092 | -56.3599 | -55.806 | 65.6982 | -57.0831 | -56.9733 | -56.987 | -57.0923 | -56.8176 | -0.045776 | -0.013733 | -0.11444 | 0.54932 | 0.70038 | 0.15106 | 0.74616 | 0.19684 | -0.022888 | -0.022888 | -122.6944 | 0.073242 | 0.24262 | -0.032043 | 0.2655 | -0.009155 | 0.59509 | 122.7127 | 0.09613 | 0.10986 | 122.8134 | 122.7814 | 122.7676 | 122.7585 | -122.8271 | -122.8043 | 122.6669 | 0.086975 | 2.3621 | 1.2543
2437.1719 | 123.0515 | -57.0694 | 65.7303 | -0.083466 | 0.00083526 | 0.060103 | 0.069045 | -0.0026168 | 0.0021917 | 0.0039264 | -0.0074462 | 0.00067495 | 0.001068 | -0.0010084 | -0.0012925 | -0.0047253 | -0.0010425 | -54.3686 | 65.7211 | -57.0557 | 65.6021 | -56.5613 | -56.9138 | -56.3873 | -55.7922 | 65.744 | -57.1014 | -56.9641 | -56.9641 | -57.0786 | -56.813 | 0.013733 | -0.009156 | -0.12817 | 0.50812 | 0.68207 | 0.15564 | 0.66833 | 0.14191 | -0.032043 | 0.013733 | -122.6944 | 0.10529 | 0.25635 | -0.009155 | 0.28839 | 0.022888 | 0.49439 | 122.6578 | 0.13733 | 0.13733 | 122.7768 | 122.8455 | 122.7905 | 122.8134 | -122.786 | -122.8317 | 122.6715 | 0.10529 | 2.7008 | 1.2772
2438.1719 | 123.0652 | -57.0694 | 65.7211 | -0.13687 | 0.00083526 | 0.061171 | 0.069259 | -0.0051804 | 0.0017645 | 0.0034992 | -0.044067 | 0.00046135 | 0.00085443 | -0.0044262 | -1.0706e-05 | -0.0038709 | -0.0023243 | -54.451 | 65.7028 | -57.0877 | 65.5014 | -56.7856 | -56.9824 | -56.3278 | -55.7785 | 65.7257 | -57.1106 | -56.9778 | -56.9733 | -57.0648 | -56.7947 | -0.018311 | -0.01831 | -0.21973 | 0.28381 | 0.74158 | 0.086975 | 0.75989 | 0.10529 | -0.041199 | 0.004578 | -122.699 | 0.09613 | 0.27466 | 0.004578 | 0.31586 | 0.045777 | 0.30212 | 122.5891 | 0.13733 | 0.13275 | 122.7905 | 122.8363 | 122.7722 | 122.7951 | -122.8088 | -122.8317 | 122.5708 | 0.091553 | 2.6184 | 1.2909
2439.1719 | 123.0789 | -57.0419 | 65.7166 | -0.068207 | 0.0012625 | 0.061812 | 0.066268 | -0.00090783 | 5.5488e-05 | 0.00072199 | -0.098999 | 0.0021703 | -0.0023498 | -0.00058098 | -0.0027877 | -0.0040845 | -0.0014697 | -54.4601 | 65.6754 | -57.0786 | 65.6342 | -56.456 | -56.5704 | -56.1127 | -55.8929 | 65.7028 | -57.1152 | -56.9733 | -56.9641 | -57.0465 | -56.7856 | -0.036621 | -0.041199 | -0.082398 | 0.58594 | 0.92926 | 0.4715 | 0.96588 | 0.50812 | -0.073242 | -0.013733 | -122.6898 | 0.07782 | 0.25635 | -0.004578 | 0.32959 | 0.068664 | 0.62256 | 122.7127 | 0.15106 | 0.14191 | 122.7539 | 122.818 | 122.7173 | 122.7448 | -122.7951 | -122.8317 | 122.6761 | 0.068664 | 2.5818 | 1.149
2440.1719 | 122.9645 | -57.0831 | 65.7211 | -0.091095 | 0.00040806 | 0.061598 | 0.070541 | 0.0016556 | 0.0030463 | 0.0077716 | -0.077637 | 0.00067495 | 2.8e-08 | 0.003905 | -0.0010787 | -0.0021619 | -0.0010425 | -54.4922 | 65.712 | -57.1747 | 65.5563 | -56.575 | -57.0236 | -56.4743 | -55.8975 | 65.7669 | -57.1198 | -57.0328 | -57.0877 | -57.2021 | -56.8726 | -0.091553 | -0.009155 | -0.16479 | 0.50812 | 0.60883 | 0.059509 | 0.70038 | 0.15106 | -0.036621 | 0.045777 | -122.7539 | -0.004578 | 0.21057 | -0.11902 | 0.24719 | -0.082397 | 0.59967 | 122.731 | 0.032043 | 0.086975 | 122.8867 | 122.8867 | 122.7951 | 122.85 | -122.8958 | -122.8409 | 122.6395 | 0.050354 | 2.5909 | 1.1856
2441.1719 | 123.0698 | -57.0557 | 65.6754 | -0.12161 | -0.0027963 | 0.06053 | 0.068618 | -0.00090783 | 0.0019781 | 0.007558 | 0.029175 | 0.0015295 | -0.001709 | -0.0010084 | 0.00041649 | -0.0038709 | -0.0025379 | -54.5013 | 65.6937 | -57.0969 | 65.5655 | -56.543 | -56.955 | -56.3919 | -55.8701 | 65.7303 | -57.1152 | -56.9778 | -56.987 | -57.0831 | -56.813 | -0.041199 | 0.018311 | -0.10986 | 0.5127 | 0.66376 | 0.10071 | 0.70496 | 0.14191 | -0.059509 | 0.054932 | -122.6532 | 0.068664 | 0.24262 | -0.027466 | 0.30212 | 0.032043 | 0.55389 | 122.6624 | 0.12817 | 0.13733 | 122.7905 | 122.8455 | 122.7493 | 122.786 | -122.7722 | -122.7905 | 122.6212 | 0.07782 | 2.5543 | 1.1856
2442.1719 | 123.0972 | -57.0786 | 65.712 | -0.068207 | -1.9142e-05 | 0.060316 | 0.067977 | -0.0034714 | 0.0043281 | 0.0037128 | 0.041382 | 0.0019567 | -0.00042717 | -0.00079478 | -0.0023605 | -0.0062207 | -0.0029651 | -54.483 | 65.7166 | -57.0923 | 65.5975 | -56.4835 | -56.9092 | -56.369 | -55.7739 | 65.7349 | -57.0648 | -56.9321 | -56.9458 | -57.0419 | -56.7719 | -0.013733 | 0.004578 | -0.11444 | 0.59509 | 0.70953 | 0.16937 | 0.72327 | 0.1831 | 0.013733 | 0.022888 | -122.644 | 0.13275 | 0.3067 | 0.036621 | 0.29297 | 0.022888 | 0.60883 | 122.6898 | 0.11902 | 0.13275 | 122.8088 | 122.7997 | 122.7951 | 122.8134 | -122.8043 | -122.7768 | 122.6761 | 0.14648 | 2.5955 | 1.3046
2443.1719 | 123.0789 | -57.0602 | 65.7166 | -0.060578 | -0.00066014 | 0.060957 | 0.067123 | 0.003151 | 0.0032599 | 0.0037128 | 0.016968 | -0.0016749 | -0.00021357 | -0.0031446 | -0.0015061 | -0.0053663 | -0.0029651 | -54.4418 | 65.7257 | -57.0786 | 65.5884 | -56.4285 | -56.9778 | -56.4239 | -55.8151 | 65.7303 | -57.0786 | -56.955 | -56.9733 | -57.0602 | -56.781 | -0.01831 | 0.009155 | -0.12817 | 0.63171 | 0.63629 | 0.082398 | 0.6546 | 0.10071 | -0.01831 | 0.013733 | -122.6715 | 0.086975 | 0.27924 | 0 | 0.29755 | 0.01831 | 0.65002 | 122.6669 | 0.10529 | 0.1236 | 122.8043 | 122.8088 | 122.7859 | 122.7905 | -122.7951 | -122.7951 | 122.6486 | 0.10529 | 2.6184 | 1.2451
2444.1719 | 123.0652 | -57.0557 | 65.7074 | -0.068207 | 0.00019446 | 0.059889 | 0.066054 | 0.00058737 | 0.0041143 | 0.0047808 | -0.13257 | 0.00067495 | 0.0019226 | -0.00079478 | -0.00086511 | -0.0034437 | -0.0036059 | -54.4418 | 65.6937 | -57.074 | 65.6296 | -56.4835 | -56.4102 | -56.163 | -55.7831 | 65.7257 | -57.0786 | -56.9641 | -56.9504 | -57.0419 | -56.781 | -0.018311 | -0.013732 | -0.077819 | 0.5722 | 0.89264 | 0.64545 | 0.91095 | 0.66376 | -0.022888 | 0.018311 | -122.6715 | 0.10529 | 0.27466 | 0.013733 | 0.29755 | 0.036621 | 0.59052 | 122.7036 | 0.12817 | 0.11444 | 122.7676 | 122.8043 | 122.7493 | 122.7814 | -122.7814 | -122.7859 | 122.6852 | 0.091553 | 2.6138 | 1.2726
2445.1719 | 123.0011 | -57.0694 | 65.7394 | -0.060578 | 0.00083526 | 0.061598 | 0.070113 | 0.0044328 | 0.0017645 | 0.0034992 | -0.059326 | 0.00024775 | 0.0019226 | 0.0041186 | -0.0017197 | -0.0017347 | 0.00066654 | -54.4327 | 65.7211 | -57.1335 | 65.5655 | -56.5613 | -57.0145 | -56.4651 | -55.8655 | 65.7715 | -57.1152 | -57.0236 | -57.074 | -57.1793 | -56.868 | -0.064087 | -0.018311 | -0.17395 | 0.50812 | 0.60425 | 0.054932 | 0.66834 | 0.11902 | -0.045776 | 0.032043 | -122.7631 | -0.004578 | 0.20142 | -0.10986 | 0.24719 | -0.064087 | 0.57221 | 122.699 | 0.041198 | 0.091552 | 122.8546 | 122.8867 | 122.7905 | 122.8409 | -122.8729 | -122.8546 | 122.6349 | 0.045776 | 2.6367 | 1.2039
2446.1719 | 123.0606 | -57.0786 | 65.712 | -0.12924 | 0.00019446 | 0.060957 | 0.067763 | 0.00058737 | 0.0030463 | 0.0028582 | 0.056641 | -0.00017945 | -0.0014954 | -0.002931 | -0.00043791 | -0.0038709 | -0.0046741 | -54.483 | 65.6982 | -57.0831 | 65.5655 | -56.5338 | -56.9412 | -56.3965 | -55.8655 | 65.7669 | -57.0969 | -56.9595 | -56.9778 | -57.0786 | -56.781 | -0.004578 | -0.013733 | -0.14648 | 0.54474 | 0.68207 | 0.13733 | 0.68665 | 0.14191 | -0.018311 | 0.054932 | -122.6715 | 0.10071 | 0.29755 | 0 | 0.31586 | 0.018311 | 0.54932 | 122.6486 | 0.11902 | 0.13733 | 122.7814 | 122.8638 | 122.7768 | 122.8455 | -122.7951 | -122.8088 | 122.644 | 0.11902 | 2.5955 | 1.2131
2447.1719 | 123.0377 | -57.074 | 65.7303 | -0.10635 | -0.00066014 | 0.062239 | 0.067977 | -0.0015488 | 0.0039007 | 0.00414 | 0.010864 | 0.0017431 | 0.00021363 | -0.0037854 | -0.0017197 | -0.0064343 | -0.0027515 | -54.483 | 65.6982 | -57.1014 | 65.5609 | -56.5659 | -56.955 | -56.3828 | -55.8517 | 65.7303 | -57.0923 | -56.9687 | -56.9824 | -57.074 | -56.8039 | -0.027465 | -0.032044 | -0.16937 | 0.50812 | 0.69122 | 0.11902 | 0.71869 | 0.14648 | -0.01831 | 0 | -122.699 | 0.091553 | 0.27008 | 0 | 0.28839 | 0.01831 | 0.53558 | 122.6624 | 0.10986 | 0.1236 | 122.7997 | 122.8226 | 122.7722 | 122.8043 | -122.8317 | -122.8226 | 122.6349 | 0.10529 | 2.5909 | 1.2222
2448.1719 | 123.0194 | -57.0648 | 65.7303 | -0.12161 | -1.9142e-05 | 0.061171 | 0.068832 | 0.00037377 | 0.0013373 | 0.0056354 | 0.14819 | 0.00024775 | 0.0012818 | -0.00058098 | -0.00086511 | -0.0038709 | -0.00040166 | -54.5059 | 65.6982 | -57.1198 | 65.5655 | -56.5842 | -56.987 | -56.4331 | -55.9616 | 65.7578 | -57.0969 | -57.0007 | -57.0694 | -57.1335 | -56.8405 | -0.054932 | -0.032044 | -0.1648 | 0.48065 | 0.63171 | 0.077819 | 0.68665 | 0.13275 | -0.032044 | 0.027465 | -122.731 | -0.004578 | 0.2243 | -0.068665 | 0.25635 | -0.036621 | 0.53558 | 122.6852 | 0.027466 | 0.096131 | 122.818 | 122.8546 | 122.7631 | 122.8226 | -122.85 | -122.8271 | 122.6303 | 0.064087 | 2.5589 | 1.1032
2449.1719 | 123.0103 | -57.0648 | 65.7028 | -0.052948 | -0.0013009 | 0.063521 | 0.069259 | -0.00069423 | 0.0013373 | 0.0028582 | -0.0043946 | 0.00046135 | 0.00021363 | -0.0031446 | -0.0015061 | -0.0060071 | 0.0019483 | -54.5059 | 65.7257 | -57.0831 | 65.5563 | -56.5567 | -56.9595 | -56.4148 | -55.8838 | 65.7394 | -57.074 | -56.9916 | -57.0099 | -57.106 | -56.8085 | -0.018311 | 0.022888 | -0.14648 | 0.50812 | 0.65002 | 0.10529 | 0.66833 | 0.1236 | -0.009156 | 0.036621 | -122.6944 | 0.054931 | 0.25635 | -0.041199 | 0.2655 | -0.032043 | 0.52643 | 122.6395 | 0.064087 | 0.082398 | 122.8088 | 122.8134 | 122.7905 | 122.8043 | -122.7859 | -122.7768 | 122.6212 | 0.073242 | 2.5589 | 1.181
2450.1719 | 123.0698 | -57.0648 | 65.7257 | -0.075836 | 0.0010489 | 0.060957 | 0.068404 | -0.00026703 | 0.0043281 | 0.0056354 | 0.023071 | 0.00088875 | -0.00064077 | -0.0033582 | -0.0044967 | -0.010279 | -0.0038197 | -54.4373 | 65.7211 | -57.0648 | 65.6296 | -56.4514 | -56.8954 | -56.3187 | -55.7602 | 65.7486 | -57.0694 | -56.7032 | -57.2021 | -57.2571 | -56.8405 | 0 | -0.004578 | -0.09613 | 0.6134 | 0.74615 | 0.16937 | 0.74615 | 0.16937 | -0.004578 | 0.022888 | -122.4289 | -0.13733 | 0.2243 | -0.19226 | 0.22888 | -0.18768 | 0.6134 | 122.6944 | -0.13275 | 0.36621 | 122.7859 | 122.818 | 122.7859 | 122.8134 | -122.7905 | -122.7951 | 122.6944 | 0.36163 | 2.6276 | 1.3046
2451.1719 | 123.0377 | -57.0419 | 65.7349 | -0.060578 | 0.00040806 | 0.063521 | 0.067336 | 0.00016017 | 0.0021917 | 0.0043536 | 0.001709 | 0.00024775 | -0.00064077 | -0.0050672 | -0.0012925 | -0.0053663 | -0.0038197 | -54.4693 | 65.7257 | -57.0831 | 65.593 | -56.5292 | -56.9275 | -56.3782 | -55.8472 | 65.7532 | -57.0786 | -56.9595 | -56.9962 | -57.0694 | -56.781 | -0.041199 | -0.009155 | -0.14191 | 0.5127 | 0.66376 | 0.11444 | 0.70496 | 0.15564 | -0.036621 | 0.018311 | -122.6944 | 0.045776 | 0.26093 | -0.027466 | 0.29755 | 0.009155 | 0.55389 | 122.6761 | 0.082397 | 0.11902 | 122.8088 | 122.8317 | 122.7676 | 122.7951 | -122.818 | -122.8134 | 122.6349 | 0.082397 | 2.5726 | 1.1948
2452.1719 | 123.0331 | -57.0511 | 65.7257 | -0.098725 | -0.0017281 | 0.062239 | 0.06755 | -0.0030442 | 0.00091009 | 0.0064898 | -0.0043946 | 0.00088875 | 0.00042723 | 0.0026232 | -0.0023605 | -0.0034437 | -0.0021107 | -54.4876 | 65.7211 | -57.0923 | 65.5701 | -56.5475 | -56.9504 | -56.3965 | -55.8609 | 65.7852 | -57.074 | -56.9641 | -56.9687 | -57.0831 | -56.7902 | -0.041199 | -0.004578 | -0.15564 | 0.50354 | 0.6546 | 0.10071 | 0.6958 | 0.14191 | -0.022889 | 0.059509 | -122.6898 | 0.082397 | 0.26093 | -0.032044 | 0.28381 | -0.009155 | 0.54474 | 122.6624 | 0.10529 | 0.10986 | 122.8134 | 122.8592 | 122.7722 | 122.8363 | -122.818 | -122.7997 | 122.6212 | 0.086975 | 2.5635 | 1.1902
2453.1719 | 123.024 | -57.0557 | 65.7532 | -0.098725 | 0.00040806 | 0.062239 | 0.067123 | -0.00069423 | -0.00079891 | 0.0054218 | 0.001709 | 0.00046135 | -0.0010682 | 0.0019824 | -0.0030013 | -0.0047253 | 0.0013073 | -54.4785 | 65.7028 | -57.0831 | 65.5792 | -56.5338 | -56.9504 | -56.4011 | -55.8609 | 65.7623 | -57.0923 | -56.9687 | -56.9824 | -57.0831 | -56.8039 | -0.027466 | -0.050354 | -0.17395 | 0.52185 | 0.6546 | 0.10529 | 0.68207 | 0.13275 | -0.036621 | 0.009155 | -122.7219 | 0.073242 | 0.25177 | -0.027466 | 0.28839 | 0.009155 | 0.54932 | 122.6624 | 0.10986 | 0.1236 | 122.7859 | 122.8546 | 122.7585 | 122.818 | -122.8363 | -122.8455 | 122.6349 | 0.086975 | 2.5772 | 1.1948
2454.1719 | 123.0194 | -57.0557 | 65.7486 | -0.10635 | -0.00023294 | 0.060103 | 0.068191 | -0.00090783 | 0.00091009 | 0.0032856 | -0.0074462 | 0.00046135 | 0.00021363 | -0.00036738 | -0.0027877 | -0.0051527 | -0.0040333 | -54.4968 | 65.712 | -57.0694 | 65.5701 | -56.5567 | -56.9641 | -56.4011 | -55.8884 | 65.7578 | -57.0831 | -56.9733 | -56.987 | -57.0969 | -56.7993 | -0.013733 | -0.036621 | -0.17853 | 0.49896 | 0.6546 | 0.091553 | 0.66833 | 0.10529 | -0.027466 | 0.009155 | -122.7219 | 0.068664 | 0.25635 | -0.041199 | 0.28381 | -0.013733 | 0.5127 | 122.6395 | 0.09613 | 0.10986 | 122.7814 | 122.8409 | 122.7676 | 122.8134 | -122.818 | -122.8317 | 122.6257 | 0.082397 | 2.5589 | 1.1673
2455.1719 | 123.1201 | -57.0374 | 65.7898 | -0.12161 | 0.0019035 | 0.063521 | 0.068191 | 0.0040054 | 0.0028327 | 0.00414 | -0.019653 | 0.0023839 | -0.0014954 | -0.0050672 | -0.00022431 | -0.0032301 | -0.0021107 | -54.4922 | 65.7257 | -57.0969 | 65.5609 | -56.5613 | -56.987 | -56.3919 | -55.8884 | 65.7623 | -57.0831 | -56.9824 | -57.0236 | -57.1335 | -56.8314 | -0.059509 | -0.064087 | -0.22888 | 0.47608 | 0.64545 | 0.050354 | 0.70496 | 0.10986 | -0.045776 | -0.027466 | -122.7722 | 0.013733 | 0.20599 | -0.09613 | 0.25177 | -0.050354 | 0.53558 | 122.6578 | 0.059509 | 0.10071 | 122.8226 | 122.8455 | 122.7631 | 122.7997 | -122.8867 | -122.8729 | 122.5983 | 0.054932 | 2.5452 | 1.149
2456.1719 | 123.0194 | -57.0465 | 65.7303 | 0.10727 | 0.00040806 | 0.061812 | 0.067763 | -0.00048063 | -0.00015811 | 0.0049946 | 0.016968 | 0.00024775 | 0.001068 | -0.0020764 | -0.0042831 | -0.0047253 | -0.0025379 | -54.5425 | 65.7349 | -57.074 | 65.5472 | -56.5842 | -56.955 | -56.4102 | -55.8792 | 65.7806 | -57.0648 | -56.987 | -57.0007 | -57.1014 | -56.7902 | -0.027466 | 0.004577 | -0.18311 | 0.46234 | 0.63629 | 0.091553 | 0.66376 | 0.11902 | -0.01831 | 0.050354 | -122.7173 | 0.045777 | 0.25635 | -0.054931 | 0.27466 | -0.036621 | 0.48981 | 122.6212 | 0.064087 | 0.077819 | 122.8088 | 122.8455 | 122.7814 | 122.8271 | -122.8043 | -122.7951 | 122.5937 | 0.059509 | 2.504 | 1.1673
2457.1719 | 123.0331 | -57.0465 | 65.744 | -0.045319 | -0.00087374 | 0.061598 | 0.067763 | 0.0022964 | 0.0011237 | 0.0032856 | 0.010864 | -0.00039305 | -0.00064077 | -0.0037854 | -0.0015061 | -0.0042981 | -0.0016833 | -54.451 | 65.7303 | -57.0786 | 65.593 | -56.5292 | -56.9412 | -56.369 | -55.8289 | 65.7486 | -57.0923 | -56.9504 | -56.955 | -57.0602 | -56.7673 | -0.032043 | -0.013733 | -0.15106 | 0.51727 | 0.67749 | 0.10529 | 0.70953 | 0.13733 | -0.045776 | 0.004577 | -122.6944 | 0.091553 | 0.27924 | -0.013733 | 0.32501 | 0.032043 | 0.54932 | 122.6715 | 0.13733 | 0.14191 | 122.8088 | 122.8409 | 122.7768 | 122.7951 | -122.8226 | -122.8363 | 122.6395 | 0.096131 | 2.5955 | 1.2177
2458.1719 | 123.0148 | -57.0419 | 65.7303 | -0.15213 | -0.0023691 | 0.061812 | 0.069686 | 0.00080117 | 0.0026191 | 0.0045672 | 0.02002 | -0.00017945 | 0.00042723 | -0.002931 | -0.0015061 | -0.0030163 | -0.00040166 | -54.4556 | 65.744 | -57.0694 | 65.5884 | -56.543 | -56.9229 | -56.3644 | -55.8426 | 65.7715 | -57.0694 | -56.9366 | -56.9733 | -57.0602 | -56.7764 | -0.027466 | 0.013733 | -0.14191 | 0.49896 | 0.67749 | 0.11902 | 0.70496 | 0.14648 | -0.027466 | 0.041198 | -122.6669 | 0.068664 | 0.2655 | -0.018311 | 0.29297 | 0.009155 | 0.52643 | 122.6578 | 0.09613 | 0.13275 | 122.8134 | 122.8409 | 122.7859 | 122.8134 | -122.7997 | -122.7997 | 122.6303 | 0.10528 | 2.5864 | 1.1993
2459.1719 | 123.0698 | -57.0236 | 65.7578 | -0.1445 | -0.0013009 | 0.060957 | 0.068404 | 0.00080117 | 0.0030463 | 0.0037128 | -0.0043946 | 0.0011023 | 0.00085443 | -0.0014356 | -0.0017197 | -0.0042981 | -0.0023243 | -54.4647 | 65.7257 | -57.0694 | 65.5838 | -56.5155 | -56.9275 | -56.3736 | -55.8517 | 65.7761 | -57.0831 | -56.9275 | -56.9687 | -57.0694 | -56.7719 | -0.045776 | -0.032043 | -0.17395 | 0.50812 | 0.65002 | 0.096131 | 0.6958 | 0.14191 | -0.059509 | 0.018311 | -122.6852 | 0.054932 | 0.25177 | -0.045776 | 0.31128 | 0.013733 | 0.55389 | 122.6532 | 0.11444 | 0.15564 | 122.7951 | 122.8592 | 122.7493 | 122.7997 | -122.8271 | -122.8409 | 122.6074 | 0.096131 | 2.5589 | 1.1719
2460.1719 | 123.0377 | -57.0511 | 65.7486 | -0.068207 | -0.0010873 | 0.060957 | 0.068191 | -0.00048063 | 0.0021917 | 0.002431 | 0.0078126 | 0.0011023 | -0.00021357 | 0.00027342 | -0.0030013 | -0.0032301 | 0.00023934 | -54.4464 | 65.7532 | -57.0602 | 65.593 | -56.5338 | -56.9458 | -56.3782 | -55.838 | 65.7715 | -57.0648 | -56.9458 | -56.9641 | -57.0694 | -56.781 | -0.009156 | 0.004578 | -0.15564 | 0.51727 | 0.67291 | 0.10528 | 0.68207 | 0.11444 | -0.013733 | 0.022888 | -122.6944 | 0.086975 | 0.27008 | -0.018311 | 0.28381 | -0.004578 | 0.52643 | 122.6532 | 0.10071 | 0.11902 | 122.8134 | 122.8363 | 122.8043 | 122.8226 | -122.8088 | -122.8134 | 122.644 | 0.10528 | 2.6047 | 1.2131
2461.1719 | 123.0743 | -57.0374 | 65.7394 | -0.068207 | 0.00019446 | 0.062453 | 0.068404 | -0.0032578 | 0.0017645 | 0.0043536 | 0.013916 | 0.0030249 | 0.0012818 | -0.0076306 | -0.0021469 | -0.0066479 | 0.0032299 | -54.4373 | 65.744 | -57.0511 | 65.6433 | -56.4789 | -56.8863 | -56.3416 | -55.7831 | 65.7761 | -57.0465 | -56.8954 | -56.9229 | -57.0145 | -56.7398 | -0.013732 | 0.004578 | -0.09613 | 0.55847 | 0.6958 | 0.15106 | 0.70953 | 0.16479 | -0.009155 | 0.036621 | -122.6349 | 0.11444 | 0.29755 | 0.022889 | 0.3067 | 0.032044 | 0.5722 | 122.6944 | 0.1236 | 0.15106 | 122.7951 | 122.8226 | 122.7814 | 122.8134 | -122.7905 | -122.7859 | 122.6807 | 0.14191 | 2.6001 | 1.2543
2462.1719 | 122.9691 | -57.0557 | 65.7486 | -0.11398 | 0.0010489 | 0.062025 | 0.068832 | -0.00048063 | 0.00069649 | 0.0043536 | 0.0047608 | 0.0023839 | -0.0021362 | 0.0017688 | -0.00043791 | -0.0023755 | 2.554e-05 | -54.4601 | 65.7211 | -57.074 | 65.5792 | -56.5567 | -56.955 | -56.3919 | -55.8792 | 65.7623 | -57.0969 | -56.9641 | -56.8314 | -56.987 | -56.7764 | -0.018311 | -0.027466 | -0.16937 | 0.49896 | 0.66376 | 0.10071 | 0.68207 | 0.11902 | -0.041199 | 0.013733 | -122.7127 | 0.2243 | 0.27924 | 0.068664 | 0.32043 | 0.10986 | 0.51727 | 122.6532 | 0.2655 | 0.13275 | 122.7951 | 122.8592 | 122.7768 | 122.818 | -122.8226 | -122.8455 | 122.6349 | 0.091553 | 2.5955 | 1.1765
2463.1719 | 123.056 | -57.0236 | 65.7349 | -0.13687 | 0.00062166 | 0.061385 | 0.069686 | 0.001442 | 0.0017645 | 0.001363 | -0.019653 | 3.4148e-05 | 0.001068 | -0.0067762 | -0.0027877 | -0.0042981 | -0.00082886 | -54.4418 | 65.7303 | -57.0786 | 65.5701 | -56.5521 | -56.955 | -56.3919 | -55.8609 | 65.7898 | -57.074 | -56.9595 | -56.9687 | -57.0877 | -56.7764 | -0.054931 | -0.004577 | -0.16479 | 0.4715 | 0.63171 | 0.068665 | 0.68664 | 0.1236 | -0.050354 | 0.054932 | -122.6944 | 0.054932 | 0.24719 | -0.064087 | 0.29755 | -0.013733 | 0.52643 | 122.6486 | 0.10529 | 0.11444 | 122.8088 | 122.8638 | 122.7539 | 122.8134 | -122.8134 | -122.8088 | 122.5937 | 0.064087 | 2.5818 | 1.1627
2464.1719 | 123.0469 | -57.0145 | 65.7761 | -0.083466 | -0.00044654 | 0.06288 | 0.066482 | -0.0021896 | 0.00091009 | 0.0062762 | 0.010864 | 0.0011023 | -0.00064077 | -0.00036738 | -0.0021469 | -0.0049389 | -0.0010425 | -54.4189 | 65.7669 | -57.0557 | 65.625 | -56.5109 | -56.9046 | -56.3553 | -55.8197 | 65.7761 | -57.0648 | -56.9229 | -56.9412 | -57.0419 | -56.7581 | -0.041199 | -0.009155 | -0.15106 | 0.50354 | 0.65918 | 0.10986 | 0.70038 | 0.15106 | -0.050354 | 0 | -122.699 | 0.073242 | 0.25635 | -0.027466 | 0.3067 | 0.022888 | 0.54474 | 122.6807 | 0.1236 | 0.14191 | 122.8226 | 122.8409 | 122.7814 | 122.7905 | -122.8317 | -122.8409 | 122.6395 | 0.091552 | 2.5955 | 1.1948
2465.1719 | 123.0789 | -56.9962 | 65.7669 | -0.083466 | -0.00066014 | 0.062453 | 0.067763 | -0.0011214 | 0.0032599 | 0.0032856 | -0.019653 | -0.00060665 | 0.00085443 | 0.0017688 | -0.00086511 | -0.0030163 | -0.00082886 | -54.3777 | 65.744 | -57.0328 | 65.6616 | -56.4514 | -56.8451 | -56.2866 | -55.7556 | 65.7532 | -57.0419 | -56.8771 | -56.8954 | -56.9962 | -56.7307 | -0.036621 | -0.022888 | -0.10529 | 0.54474 | 0.70953 | 0.15106 | 0.74616 | 0.18768 | -0.045776 | -0.013733 | -122.644 | 0.10071 | 0.2655 | 0 | 0.31128 | 0.045776 | 0.58136 | 122.6944 | 0.14648 | 0.16479 | 122.7768 | 122.7951 | 122.7402 | 122.7493 | -122.7997 | -122.8088 | 122.6578 | 0.11902 | 2.6184 | 1.2405
2466.1719 | 123.0743 | -57.0145 | 65.7486 | -0.091095 | -0.0010873 | 0.059889 | 0.069686 | -0.0015488 | 0.00026909 | 0.0071308 | 0.013916 | -0.00060665 | -0.00021357 | -0.0010084 | -0.0038559 | -0.0030163 | -0.0042469 | -54.3915 | 65.7806 | -57.0511 | 65.6662 | -56.456 | -56.8634 | -56.3095 | -55.7648 | 65.7761 | -57.0419 | -56.8909 | -56.9092 | -57.0099 | -56.7215 | -0.036621 | 0.032044 | -0.082397 | 0.55847 | 0.70496 | 0.15106 | 0.74158 | 0.18768 | -0.027466 | 0.027466 | -122.6395 | 0.10529 | 0.29297 | 0.004577 | 0.32043 | 0.032043 | 0.59509 | 122.7173 | 0.13275 | 0.15106 | 122.8317 | 122.818 | 122.7951 | 122.7905 | -122.7997 | -122.7905 | 122.6807 | 0.1236 | 2.623 | 1.2497
2467.1719 | 123.056 | -56.9824 | 65.7578 | -0.11398 | 0.00040806 | 0.060316 | 0.067763 | -0.00069423 | 0.00069649 | 0.0054218 | 0.0047608 | 0.00067495 | 0.00021363 | -0.002931 | -0.0023605 | -0.0032301 | -0.0021107 | -54.3961 | 65.7715 | -57.0099 | 65.6433 | -56.4697 | -56.8726 | -56.3141 | -55.7785 | 65.7944 | -57.0557 | -56.9 | -56.9 | -56.9962 | -56.7307 | -0.027466 | 0.013733 | -0.11444 | 0.5127 | 0.66833 | 0.10986 | 0.6958 | 0.13733 | -0.073242 | 0.036622 | -122.6578 | 0.082398 | 0.25177 | -0.013733 | 0.32501 | 0.059509 | 0.54016 | 122.6532 | 0.15564 | 0.15564 | 122.7814 | 122.85 | 122.7539 | 122.7768 | -122.7676 | -122.8134 | 122.6257 | 0.082398 | 2.5864 | 1.2039
2468.1719 | 123.0743 | -57.0099 | 65.7349 | -0.098725 | 0.0021171 | 0.061385 | 0.069259 | -0.0034714 | 0.0013373 | 0.0060626 | 0.02002 | -0.0014613 | 0.0023498 | -0.0037854 | -0.0034287 | -0.0025891 | -0.00082886 | -54.4006 | 65.7715 | -57.0053 | 65.6342 | -56.4651 | -56.8726 | -56.337 | -55.7877 | 65.7944 | -57.0374 | -56.9046 | -56.9229 | -57.0099 | -56.7352 | 0.004578 | 0.036621 | -0.10071 | 0.54474 | 0.67291 | 0.13733 | 0.66833 | 0.13275 | -0.027466 | 0.05951 | -122.6395 | 0.086975 | 0.27466 | 0 | 0.30213 | 0.027466 | 0.54016 | 122.6395 | 0.11444 | 0.13275 | 122.7768 | 122.8317 | 122.7814 | 122.8043 | -122.7402 | -122.7722 | 122.644 | 0.10529 | 2.6093 | 1.2222
2469.1719 | 123.0286 | -57.0236 | 65.7806 | -0.11398 | -0.00044654 | 0.061171 | 0.067123 | -0.0024032 | 0.0026191 | 0.0039264 | -0.0043946 | 0.0017431 | 0.001068 | 0.0028368 | -0.0027877 | -0.0040845 | -0.0029651 | -54.4464 | 65.744 | -57.0465 | 65.5838 | -56.5247 | -56.9412 | -56.3736 | -55.8609 | 65.7944 | -57.0602 | -56.9458 | -56.9595 | -57.074 | -56.781 | -0.022888 | -0.036621 | -0.19684 | 0.49896 | 0.65002 | 0.082398 | 0.67291 | 0.10529 | -0.036621 | 0.013733 | -122.7264 | 0.064087 | 0.24262 | -0.050354 | 0.27924 | -0.013733 | 0.52185 | 122.6303 | 0.10071 | 0.11444 | 122.7905 | 122.8546 | 122.7676 | 122.818 | -122.8271 | -122.8409 | 122.6074 | 0.07782 | 2.5772 | 1.1627
2470.1719 | 123.0331 | -57.0007 | 65.744 | -0.091095 | -0.00087374 | 0.062453 | 0.070754 | -0.00069423 | 0.0017645 | 0.00414 | 0.016968 | -0.00017945 | 0.0012818 | -0.001222 | -0.00065151 | -0.0060071 | -0.0027515 | -54.3961 | 65.7669 | -57.0099 | 65.6204 | -56.5063 | -56.8954 | -56.3278 | -55.8014 | 65.8035 | -57.0465 | -56.9183 | -56.9183 | -57.0236 | -56.749 | -0.009156 | 0.022888 | -0.1236 | 0.49438 | 0.67291 | 0.10529 | 0.68207 | 0.11444 | -0.045777 | 0.059509 | -122.6624 | 0.082397 | 0.25177 | -0.022889 | 0.29755 | 0.022888 | 0.50354 | 122.6303 | 0.12817 | 0.12817 | 122.7768 | 122.85 | 122.7676 | 122.8043 | -122.7539 | -122.7905 | 122.6212 | 0.082397 | 2.6047 | 1.1993
2471.1719 | 123.0743 | -56.9916 | 65.7578 | -0.037689 | -0.0010873 | 0.061812 | 0.069472 | -0.0015488 | 0.0017645 | 0.0037128 | -0.010498 | -0.00082025 | -0.00064077 | -0.00058098 | -0.00065151 | -0.0036573 | -0.0031787 | -54.3549 | 65.7532 | -57.0145 | 65.6616 | -56.4285 | -56.8268 | -56.282 | -55.7556 | 65.8127 | -57.0374 | -56.868 | -56.8771 | -56.9733 | -56.6849 | -0.022888 | -0.004577 | -0.09613 | 0.56305 | 0.70953 | 0.16479 | 0.73242 | 0.18768 | -0.045777 | 0.054932 | -122.6257 | 0.11444 | 0.3067 | 0.01831 | 0.35248 | 0.064087 | 0.58594 | 122.6761 | 0.16022 | 0.16937 | 122.7676 | 122.85 | 122.7448 | 122.8043 | -122.7722 | -122.7951 | 122.6532 | 0.1236 | 2.6367 | 1.236
2472.1719 | 123.0927 | -56.9595 | 65.7852 | -0.091095 | -0.00044654 | 0.062453 | 0.068832 | -0.00069423 | -0.00015811 | 0.0047808 | 0.0047608 | 0.0011023 | 0.00085443 | -0.0044262 | -0.0021469 | -0.0042981 | -0.0014697 | -54.3686 | 65.7623 | -57.0053 | 65.6479 | -56.4331 | -56.8451 | -56.2912 | -55.751 | 65.8035 | -57.0328 | -56.8634 | -56.8771 | -56.9916 | -56.7123 | -0.045776 | -0.022888 | -0.13733 | 0.52643 | 0.66833 | 0.11444 | 0.71411 | 0.16022 | -0.073242 | 0.018311 | -122.6486 | 0.082398 | 0.24719 | -0.032043 | 0.32043 | 0.041199 | 0.57221 | 122.6532 | 0.15564 | 0.16937 | 122.7676 | 122.8363 | 122.7219 | 122.7631 | -122.7905 | -122.818 | 122.6074 | 0.096131 | 2.5909 | 1.2085
2473.1719 | 123.0743 | -56.9916 | 65.7623 | -0.083466 | -0.0023691 | 0.061171 | 0.067977 | 0.00080117 | 0.0011237 | 0.0054218 | 0.010864 | 0.0015295 | 0.001068 | -0.0010084 | -0.0017197 | -0.0068615 | -0.0048877 | -54.3777 | 65.7852 | -57.019 | 65.6754 | -56.4468 | -56.8588 | -56.3095 | -55.7648 | 65.799 | -57.0374 | -56.8726 | -56.868 | -56.987 | -56.6895 | -0.027466 | 0.022888 | -0.086975 | 0.54474 | 0.68207 | 0.13275 | 0.70953 | 0.16022 | -0.045777 | 0.036621 | -122.6349 | 0.1236 | 0.30212 | 0.004577 | 0.3479 | 0.050354 | 0.57221 | 122.6944 | 0.16937 | 0.16479 | 122.8043 | 122.8363 | 122.7768 | 122.7905 | -122.7814 | -122.7997 | 122.6669 | 0.11902 | 2.6138 | 1.2268
2474.1719 | 123.0331 | -57.0145 | 65.7852 | -0.060578 | -0.00023294 | 0.060957 | 0.072463 | 0.0022964 | 0.0032599 | 0.0026446 | 0.016968 | 0.0025975 | 0.0021362 | 0.005614 | -0.00065151 | -0.0038709 | -0.0051013 | -54.3732 | 65.7669 | -56.987 | 65.6342 | -56.4697 | -56.8771 | -56.3187 | -55.7831 | 65.799 | -57.0419 | -56.8771 | -56.9046 | -57.0099 | -56.6986 | 0.027465 | -0.01831 | -0.15106 | 0.54474 | 0.6958 | 0.13733 | 0.66833 | 0.10986 | -0.027466 | 0.013733 | -122.6624 | 0.10986 | 0.31586 | 0.004577 | 0.34332 | 0.032043 | 0.51727 | 122.6212 | 0.13733 | 0.16479 | 122.7539 | 122.8409 | 122.7814 | 122.8134 | -122.7722 | -122.8271 | 122.6486 | 0.13733 | 2.6413 | 1.2314
2475.1719 | 123.0515 | -56.9962 | 65.7898 | -0.10635 | -0.00066014 | 0.062239 | 0.069686 | -0.00069423 | 0.0013373 | 0.0043536 | -0.0043946 | 0.00088875 | 0.001709 | -0.0031446 | -0.00065151 | -0.0049389 | -0.0016833 | -54.3869 | 65.7761 | -57.0099 | 65.6433 | -56.4743 | -56.8634 | -56.3232 | -55.8014 | 65.8173 | -57.0236 | -56.8771 | -56.8954 | -57.0007 | -56.7261 | -0.013733 | -0.013733 | -0.14648 | 0.52185 | 0.67291 | 0.13275 | 0.68665 | 0.14648 | -0.027466 | 0.027466 | -122.6669 | 0.10071 | 0.27008 | -0.004577 | 0.29755 | 0.022889 | 0.53558 | 122.6532 | 0.12817 | 0.14648 | 122.7859 | 122.8409 | 122.7722 | 122.8134 | -122.7997 | -122.8134 | 122.6395 | 0.11902 | 2.6093 | 1.1948
2476.1719 | 122.9965 | -57.0328 | 65.799 | -0.083466 | 0.00040806 | 0.060744 | 0.0699 | -0.0026168 | -0.00037171 | 0.0034992 | -0.010498 | 0.00088875 | 0.0025634 | 0.001128 | -0.0012925 | -0.0032301 | -0.00040166 | -54.3961 | 65.7623 | -57.0099 | 65.6937 | -56.6162 | -56.9504 | -56.3644 | -55.8517 | 65.7852 | -57.0374 | -56.9366 | -56.9504 | -57.0511 | -56.7627 | 0.022888 | -0.036621 | -0.10529 | 0.41656 | 0.66833 | 0.082398 | 0.64545 | 0.05951 | -0.004578 | -0.013733 | -122.7356 | 0.082398 | 0.27008 | -0.01831 | 0.27466 | -0.013732 | 0.39368 | 122.7036 | 0.086976 | 0.10071 | 122.7722 | 122.8226 | 122.7951 | 122.818 | -122.8088 | -122.8363 | 122.7264 | 0.09613 | 2.6367 | 1.181
2477.1719 | 123.0469 | -57.0007 | 65.7761 | -0.15976 | 0.0014761 | 0.060103 | 0.068404 | 0.00037377 | 0.0015509 | 0.0084124 | -0.028809 | 0.0013159 | -0.0027772 | -0.0025036 | 0.00084389 | -0.0047253 | 0.0023755 | -54.3777 | 65.7806 | -56.987 | 65.657 | -56.4789 | -56.8817 | -56.3187 | -55.8289 | 65.799 | -57.0465 | -56.9 | -56.9229 | -57.0236 | -56.7261 | 0.013732 | 0.004578 | -0.11902 | 0.52185 | 0.68207 | 0.11902 | 0.66833 | 0.10529 | -0.045777 | 0.022888 | -122.6761 | 0.077819 | 0.27466 | -0.022889 | 0.32044 | 0.022888 | 0.50812 | 122.644 | 0.1236 | 0.14648 | 122.7676 | 122.8455 | 122.7814 | 122.7997 | -122.7631 | -122.8226 | 122.6578 | 0.10071 | 2.623 | 1.1719
2478.1719 | 123.0606 | -56.9778 | 65.8081 | -0.014801 | 0.00019446 | 0.062239 | 0.068191 | -0.00069423 | 0.0021917 | 0.005849 | -0.01355 | 0.00088875 | 0.00085443 | 0.00048702 | -0.0017197 | -0.0034437 | -0.0023243 | -54.364 | 65.744 | -56.9641 | 65.6662 | -56.4148 | -56.8451 | -56.2729 | -55.7648 | 65.8173 | -57.0145 | -56.8451 | -56.8817 | -56.9824 | -56.6986 | 0.013733 | -0.064086 | -0.14191 | 0.56305 | 0.70496 | 0.13275 | 0.69122 | 0.11902 | -0.036621 | 0.009156 | -122.6532 | 0.09613 | 0.27924 | -0.004578 | 0.31586 | 0.032043 | 0.54932 | 122.6303 | 0.13275 | 0.16937 | 122.7081 | 122.8317 | 122.7219 | 122.7951 | -122.7722 | -122.8226 | 122.644 | 0.13275 | 2.6138 | 1.2131
2479.1719 | 123.0652 | -56.9778 | 65.7898 | -0.083466 | -0.00023294 | 0.060103 | 0.069259 | -0.00026703 | 0.0013373 | 0.0037128 | 0.001709 | 0.0017431 | 0.0019226 | 0.0026232 | -0.00065151 | -0.0036573 | -0.0033923 | -54.3365 | 65.7761 | -56.987 | 65.6754 | -56.4239 | -56.8634 | -56.2912 | -55.751 | 65.799 | -57.0099 | -56.8588 | -56.8817 | -56.9778 | -56.7078 | -0.009156 | -0.013733 | -0.11444 | 0.55389 | 0.68664 | 0.11444 | 0.6958 | 0.1236 | -0.032044 | 0.009155 | -122.6486 | 0.09613 | 0.27008 | 0 | 0.30212 | 0.032044 | 0.56305 | 122.6624 | 0.12817 | 0.15106 | 122.7631 | 122.8088 | 122.7539 | 122.7768 | -122.7768 | -122.7997 | 122.6532 | 0.11902 | 2.6413 | 1.2268
2480.1719 | 123.0743 | -56.9778 | 65.7806 | -0.083466 | -0.00087374 | 0.061385 | 0.0699 | -0.001976 | 0.0024053 | 0.003072 | 0.001709 | 0.00024775 | 0.0012818 | 0.0036914 | -0.0025741 | -0.0060071 | -0.00018806 | -54.3503 | 65.8035 | -56.9962 | 65.6616 | -56.4514 | -56.8588 | -56.2958 | -55.7785 | 65.831 | -57.0236 | -56.868 | -56.9 | -56.9824 | -56.7078 | -0.018311 | 0.022888 | -0.11902 | 0.52643 | 0.68207 | 0.11902 | 0.70038 | 0.13733 | -0.045777 | 0.050354 | -122.6486 | 0.07782 | 0.27008 | -0.004578 | 0.31586 | 0.041199 | 0.54474 | 122.6578 | 0.1236 | 0.15564 | 122.7997 | 122.8546 | 122.7814 | 122.8088 | -122.7768 | -122.8043 | 122.6395 | 0.10986 | 2.6276 | 1.1993
2481.1719 | 123.0652 | -56.9733 | 65.8035 | -0.083466 | -0.00044654 | 0.062453 | 0.068832 | 0.001442 | 0.0032599 | 0.0043536 | -0.0043946 | -0.0016749 | 0.001709 | 0.0064684 | -0.0034287 | -0.0030163 | 0.00045294 | -54.3457 | 65.799 | -57.0053 | 65.7257 | -56.3965 | -56.813 | -56.282 | -55.6961 | 65.8173 | -57.0007 | -56.8359 | -56.8497 | -56.955 | -56.6849 | -0.032043 | -0.004578 | -0.07782 | 0.57678 | 0.69122 | 0.16022 | 0.72327 | 0.19226 | -0.027465 | 0.013733 | -122.6395 | 0.1236 | 0.28839 | 0.018311 | 0.31586 | 0.045776 | 0.60883 | 122.731 | 0.15106 | 0.16479 | 122.8043 | 122.818 | 122.7722 | 122.7905 | -122.8088 | -122.8043 | 122.699 | 0.13733 | 2.6276 | 1.2772
2482.1719 | 123.0423 | -56.9641 | 65.799 | -0.12924 | -0.00087374 | 0.061171 | 0.068191 | -0.00069423 | 0.00069649 | 0.0049946 | 0.0047608 | 0.00046135 | 0.00021363 | 0.0015552 | -0.00022431 | -0.0055799 | -0.00040166 | -54.3686 | 65.7806 | -56.9778 | 65.657 | -56.4743 | -56.8726 | -56.3004 | -55.806 | 65.8264 | -57.0328 | -56.8863 | -56.8909 | -57.0099 | -56.7078 | -0.013733 | -0.01831 | -0.14191 | 0.48981 | 0.66376 | 0.091552 | 0.67749 | 0.10528 | -0.068665 | 0.027466 | -122.6852 | 0.073242 | 0.25635 | -0.045777 | 0.32501 | 0.022888 | 0.50354 | 122.6349 | 0.14191 | 0.14648 | 122.7585 | 122.8592 | 122.7448 | 122.7905 | -122.7768 | -122.8317 | 122.6212 | 0.077819 | 2.5955 | 1.1581
2483.1719 | 123.0194 | -56.9916 | 65.7898 | -0.075836 | 0.00062166 | 0.061812 | 0.068832 | 0.00016017 | 0.0021917 | 0.0043536 | 0.001709 | -0.0014613 | 0.0014954 | -0.0069898 | -0.0019333 | -0.0042981 | -0.0046741 | -54.3777 | 65.7761 | -56.9733 | 65.6479 | -56.5018 | -56.9092 | -56.337 | -55.7877 | 65.8539 | -57.0053 | -56.9183 | -56.9366 | -57.0419 | -56.7535 | 0.01831 | -0.013733 | -0.14191 | 0.48981 | 0.6546 | 0.082397 | 0.63629 | 0.064087 | -0.013733 | 0.064087 | -122.7081 | 0.054931 | 0.23804 | -0.050354 | 0.25177 | -0.036621 | 0.4715 | 122.6212 | 0.068664 | 0.086975 | 122.7493 | 122.8592 | 122.7676 | 122.8455 | -122.7631 | -122.7951 | 122.6395 | 0.073242 | 2.6138 | 1.2039
2484.1719 | 123.0286 | -56.9733 | 65.7806 | -0.11398 | -0.0010873 | 0.060316 | 0.068404 | 0.0022964 | 0.0011237 | 0.0045672 | -0.016602 | 0.00088875 | -0.0027772 | 0.0036914 | -0.0034287 | -0.0053663 | -0.0012561 | -54.3823 | 65.7669 | -56.9916 | 65.6433 | -56.4835 | -56.8634 | -56.3278 | -55.8105 | 65.8081 | -57.0282 | -56.8726 | -56.9183 | -57.019 | -56.7261 | -0.01831 | -0.013733 | -0.13733 | 0.48981 | 0.64545 | 0.10986 | 0.66376 | 0.12817 | -0.054931 | 0.027465 | -122.6532 | 0.054932 | 0.24719 | -0.045776 | 0.30212 | 0.009155 | 0.50812 | 122.6349 | 0.10986 | 0.15564 | 122.7585 | 122.8363 | 122.7402 | 122.7814 | -122.7722 | -122.8088 | 122.6166 | 0.10071 | 2.5909 | 1.1627
2485.1719 | 123.0835 | -56.9687 | 65.8035 | -0.098725 | -1.9142e-05 | 0.063948 | 0.069045 | -0.0017624 | 0.0030463 | 0.00093559 | -0.01355 | 0.0015295 | 0.0021362 | -0.00058098 | -0.0010787 | -0.0042981 | 0.00088014 | -54.3411 | 65.7944 | -56.9687 | 65.6937 | -56.4377 | -56.8405 | -56.2729 | -55.7556 | 65.8493 | -57.0099 | -56.8451 | -56.8771 | -56.9824 | -56.6803 | 0 | -0.009155 | -0.10986 | 0.53101 | 0.6958 | 0.12817 | 0.6958 | 0.12817 | -0.041199 | 0.045776 | -122.6486 | 0.091553 | 0.28839 | -0.013733 | 0.32959 | 0.027466 | 0.53101 | 122.6624 | 0.13275 | 0.16479 | 122.7631 | 122.8592 | 122.7631 | 122.818 | -122.7722 | -122.8134 | 122.6624 | 0.1236 | 2.6276 | 1.2131
2486.1719 | 123.0377 | -56.9778 | 65.7898 | -0.075836 | 0.00083526 | 0.062239 | 0.066909 | 0.001442 | 0.0017645 | 0.0037128 | -0.0074462 | -0.00017945 | -0.00042717 | -0.003999 | -0.0032151 | -0.0042981 | -0.0012561 | -54.3457 | 65.8035 | -56.9962 | 65.6754 | -56.4423 | -56.8497 | -56.2729 | -55.7693 | 65.8401 | -57.0145 | -56.8634 | -56.8771 | -56.9824 | -56.6849 | -0.018311 | 0.013733 | -0.11444 | 0.53558 | 0.70496 | 0.12817 | 0.72327 | 0.14648 | -0.036621 | 0.050354 | -122.6532 | 0.10071 | 0.29297 | -0.004578 | 0.32959 | 0.032043 | 0.55389 | 122.6715 | 0.13733 | 0.15106 | 122.7997 | 122.8546 | 122.7814 | 122.818 | -122.7859 | -122.8043 | 122.6532 | 0.11444 | 2.6321 | 1.2085
2487.1719 | 123.0331 | -56.9733 | 65.8127 | -0.12161 | 0.00062166 | 0.062453 | 0.069259 | -0.0041122 | 0.00026909 | 0.0062762 | 0.0047608 | 0.00067495 | 0.001068 | -0.00079478 | -0.0030013 | -0.0042981 | -0.0014697 | -54.3457 | 65.7898 | -56.9687 | 65.6662 | -56.4514 | -56.8405 | -56.2912 | -55.7831 | 65.8447 | -57.0145 | -56.8497 | -56.8909 | -56.9916 | -56.7078 | 0.004578 | -0.022888 | -0.14648 | 0.52185 | 0.68207 | 0.13275 | 0.67749 | 0.12817 | -0.041198 | 0.032044 | -122.6624 | 0.082398 | 0.2655 | -0.01831 | 0.3067 | 0.022888 | 0.51727 | 122.6349 | 0.1236 | 0.16479 | 122.7585 | 122.8592 | 122.7631 | 122.818 | -122.7814 | -122.8271 | 122.6395 | 0.1236 | 2.6276 | 1.1902
2488.1719 | 123.0377 | -56.9687 | 65.799 | -0.11398 | -0.00044654 | 0.063094 | 0.069686 | -0.001976 | 0.0028327 | 0.00414 | -0.010498 | 0.00067495 | 0.00085443 | 0.0028368 | -0.0010787 | -0.0053663 | -0.0021107 | -54.364 | 65.7898 | -56.987 | 65.6616 | -56.4606 | -56.8588 | -56.3049 | -55.8105 | 65.8401 | -57.0053 | -56.8634 | -56.8909 | -57.0007 | -56.7123 | -0.018311 | -0.009155 | -0.13733 | 0.50812 | 0.66376 | 0.10986 | 0.68207 | 0.12817 | -0.036621 | 0.041199 | -122.6624 | 0.07782 | 0.25635 | -0.032043 | 0.29297 | 0.004578 | 0.52643 | 122.6486 | 0.11444 | 0.14191 | 122.7768 | 122.8455 | 122.7585 | 122.8088 | -122.786 | -122.8043 | 122.6303 | 0.10529 | 2.6047 | 1.1581
2489.1719 | 123.0331 | -56.9687 | 65.831 | -0.10635 | 0.00019446 | 0.059462 | 0.068404 | 0.00080117 | 0.0017645 | 0.0047808 | -0.01355 | 0.0017431 | -0.0027772 | -0.00036738 | -0.0012925 | -0.0036573 | -0.0031787 | -54.364 | 65.7806 | -57.0099 | 65.6479 | -56.456 | -56.868 | -56.3004 | -55.8151 | 65.8264 | -56.9916 | -56.868 | -56.9046 | -57.0099 | -56.7032 | -0.041199 | -0.050354 | -0.18311 | 0.5127 | 0.66833 | 0.10071 | 0.70953 | 0.14191 | -0.022888 | -0.004578 | -122.699 | 0.064087 | 0.2655 | -0.041199 | 0.28839 | -0.018311 | 0.55389 | 122.6578 | 0.086975 | 0.1236 | 122.7905 | 122.818 | 122.7493 | 122.7951 | -122.8409 | -122.8226 | 122.6166 | 0.10071 | 2.6047 | 1.1536
2490.1719 | 123.0148 | -56.9916 | 65.8035 | -0.083466 | -0.0010873 | 0.060957 | 0.067977 | -0.0015488 | 0.0015509 | 0.005849 | -0.016602 | 0.0021703 | -0.0023498 | -0.0025036 | -0.00086511 | -0.0057935 | -0.0010425 | -54.3732 | 65.8081 | -56.9824 | 65.6433 | -56.4926 | -56.8954 | -56.3232 | -55.838 | 65.831 | -57.0099 | -56.8863 | -56.9412 | -57.0465 | -56.7352 | 0.009155 | 0.004577 | -0.16022 | 0.49896 | 0.66833 | 0.09613 | 0.65918 | 0.086975 | -0.018311 | 0.027466 | -122.6898 | 0.050354 | 0.25635 | -0.054932 | 0.27466 | -0.036621 | 0.48981 | 122.6257 | 0.068665 | 0.1236 | 122.7905 | 122.8409 | 122.7997 | 122.8226 | -122.7859 | -122.8134 | 122.6349 | 0.10529 | 2.6184 | 1.1536
2491.1719 | 123.0469 | -56.9641 | 65.8493 | -0.12161 | -0.00044654 | 0.063734 | 0.068404 | -0.0038986 | 0.0032599 | 0.002431 | -0.025757 | 0.00024775 | 0.0012818 | 0.00070062 | -0.0015061 | -0.0038709 | 0.0021619 | -54.3549 | 65.7944 | -56.9687 | 65.6158 | -56.337 | -56.7902 | -56.3141 | -55.8334 | 65.8356 | -57.0053 | -56.9 | -56.9092 | -57.0374 | -56.7307 | -0.004578 | -0.054931 | -0.23346 | 0.62714 | 0.65002 | 0.17395 | 0.6546 | 0.17853 | -0.041199 | -0.013733 | -122.7493 | 0.054931 | 0.23346 | -0.073243 | 0.27466 | -0.032044 | 0.63171 | 122.5845 | 0.09613 | 0.10529 | 122.7631 | 122.8409 | 122.7585 | 122.7997 | -122.818 | -122.8546 | 122.58 | 0.064087 | 2.6093 | 1.1307
2492.1719 | 123.0011 | -56.9641 | 65.8173 | -0.12161 | -0.0021555 | 0.062453 | 0.0699 | -0.0041122 | 0.0024053 | 0.005849 | -0.019653 | 0.0013159 | 0.00042723 | 0.0026232 | -0.0025741 | -0.0049389 | -0.0040333 | -54.3365 | 65.8218 | -56.9733 | 65.6662 | -56.4468 | -56.8542 | -56.3004 | -55.8105 | 65.8447 | -56.9733 | -56.8588 | -56.8863 | -56.9778 | -56.694 | -0.009156 | 0.004577 | -0.15106 | 0.51727 | 0.66376 | 0.10986 | 0.67291 | 0.11902 | -0.009156 | 0.027466 | -122.6761 | 0.077819 | 0.27008 | -0.013733 | 0.27924 | -0.004577 | 0.52643 | 122.6395 | 0.086975 | 0.11444 | 122.7951 | 122.818 | 122.7859 | 122.8088 | -122.7905 | -122.7905 | 122.6303 | 0.10529 | 2.6276 | 1.1536
2493.1719 | 123.0469 | -56.955 | 65.8264 | -0.060578 | -0.0017281 | 0.062025 | 0.067977 | -0.0011214 | 0.00026909 | 0.0054218 | -0.037964 | 3.4148e-05 | 0.001068 | -0.0080578 | -0.0017197 | -0.0025891 | 2.554e-05 | -54.3411 | 65.8081 | -56.9687 | 65.6616 | -56.4514 | -56.8542 | -56.2866 | -55.8014 | 65.8585 | -57.0053 | -56.8634 | -56.8909 | -57.0145 | -56.7215 | -0.013733 | -0.018311 | -0.16479 | 0.50354 | 0.66834 | 0.10071 | 0.68207 | 0.11444 | -0.050354 | 0.032043 | -122.6898 | 0.064087 | 0.23346 | -0.059509 | 0.28381 | -0.009155 | 0.51727 | 122.6303 | 0.11444 | 0.14191 | 122.7768 | 122.8638 | 122.7631 | 122.8134 | -122.7951 | -122.8317 | 122.6166 | 0.091553 | 2.6138 | 1.1536
2494.1719 | 122.9919 | -56.9504 | 65.831 | -0.11398 | 0.00019446 | 0.059248 | 0.064345 | -0.00048063 | 0.0028327 | 0.0037128 | -0.03186 | 3.4148e-05 | -0.00064077 | -0.0025036 | -0.0015061 | -0.0045117 | -0.0018971 | -54.3274 | 65.7898 | -56.9595 | 65.6296 | -56.4651 | -56.8359 | -56.2912 | -55.8334 | 65.8447 | -56.9962 | -56.8771 | -56.9046 | -57.0099 | -56.7032 | -0.009156 | -0.041199 | -0.20142 | 0.48523 | 0.65918 | 0.11444 | 0.66833 | 0.1236 | -0.045777 | 0.013733 | -122.7081 | 0.045776 | 0.24719 | -0.05951 | 0.29297 | -0.013733 | 0.49439 | 122.5891 | 0.091553 | 0.11902 | 122.7493 | 122.8409 | 122.7402 | 122.7951 | -122.7905 | -122.8271 | 122.58 | 0.073242 | 2.623 | 1.1169
2495.1719 | 123.024 | -56.9687 | 65.8356 | -0.11398 | 0.00019446 | 0.061812 | 0.068618 | -0.00048063 | 0.0039007 | 0.0054218 | 0.10547 | -0.00017945 | 0.001068 | -0.0037854 | -0.0038559 | -0.0034437 | -0.0018971 | -54.3365 | 65.8401 | -56.9687 | 65.6387 | -56.4651 | -56.8771 | -56.3004 | -55.9067 | 65.863 | -56.9962 | -56.8726 | -56.9366 | -57.0328 | -56.7215 | 0 | 0.004578 | -0.19684 | 0.50354 | 0.66833 | 0.091553 | 0.66833 | 0.091553 | -0.027466 | 0.027466 | -122.7081 | 0.032043 | 0.24719 | -0.064087 | 0.27466 | -0.036621 | 0.50354 | 122.6074 | 0.059509 | 0.1236 | 122.8088 | 122.8592 | 122.8088 | 122.8317 | -122.8043 | -122.8317 | 122.6074 | 0.09613 | 2.6321 | 1.062
2496.1719 | 123.0103 | -56.9641 | 65.8035 | -0.052948 | -0.00023294 | 0.060744 | 0.069259 | -0.0038986 | 0.0013373 | 0.0039264 | -0.01355 | 0.0011023 | 0.00042723 | 0.0068958 | -0.0019333 | -0.0051527 | 0.00023934 | -54.3503 | 65.8173 | -56.9687 | 65.6662 | -56.4606 | -56.8771 | -56.3004 | -55.8243 | 65.8539 | -56.9778 | -56.8039 | -56.9962 | -57.0648 | -56.7261 | -0.004578 | 0.013733 | -0.13733 | 0.50354 | 0.66376 | 0.086975 | 0.66833 | 0.091553 | -0.013733 | 0.050354 | -122.6074 | -0.032044 | 0.23804 | -0.10071 | 0.25177 | -0.086975 | 0.50812 | 122.6349 | -0.018311 | 0.17395 | 122.7859 | 122.8317 | 122.7814 | 122.818 | -122.7722 | -122.7814 | 122.6303 | 0.16022 | 2.6138 | 1.1398
2497.1719 | 123.0194 | -56.9412 | 65.8218 | -0.12924 | -0.0013009 | 0.063948 | 0.068618 | -0.00026703 | 0.0026191 | 0.0049946 | -0.028809 | -0.00017945 | 0.00064083 | -0.00036738 | -0.0010787 | -0.0042981 | -0.0016833 | -54.3182 | 65.7623 | -56.9504 | 65.6845 | -56.4148 | -56.8497 | -56.2775 | -55.7648 | 65.8356 | -57.0099 | -56.8588 | -56.9183 | -57.0236 | -56.7123 | -0.009155 | -0.059509 | -0.13733 | 0.52643 | 0.66376 | 0.091553 | 0.67291 | 0.10071 | -0.068665 | 0.013733 | -122.6807 | 0.022888 | 0.22888 | -0.082398 | 0.29755 | -0.013733 | 0.53558 | 122.6349 | 0.091553 | 0.15106 | 122.7127 | 122.8455 | 122.7036 | 122.7768 | -122.7722 | -122.8317 | 122.6257 | 0.082397 | 2.623 | 1.1765
2498.1719 | 123.0331 | -56.9412 | 65.8035 | -0.13687 | 0.00062166 | 0.060957 | 0.067123 | -0.0021896 | 0.0026191 | 0.0060626 | -0.047119 | 0.0011023 | -0.00021357 | -0.00015378 | -0.0044967 | -0.0032301 | 0.0010937 | -54.3045 | 65.8127 | -56.955 | 65.6937 | -56.3782 | -56.8405 | -56.282 | -55.751 | 65.863 | -56.9962 | -56.8314 | -56.9138 | -57.0053 | -56.6986 | -0.013733 | 0.009155 | -0.10986 | 0.56305 | 0.65918 | 0.10071 | 0.67291 | 0.11444 | -0.054932 | 0.059509 | -122.6349 | 0.027466 | 0.24262 | -0.064087 | 0.29755 | -0.009155 | 0.57678 | 122.6486 | 0.082398 | 0.1648 | 122.7676 | 122.8592 | 122.7539 | 122.8043 | -122.7585 | -122.7997 | 122.6349 | 0.10986 | 2.6367 | 1.1902
2499.1719 | 123.0057 | -56.9458 | 65.8173 | -0.10635 | 0.00040806 | 0.061171 | 0.068191 | 0.00016017 | 0.0068915 | 0.0056354 | 0.001709 | -0.00039305 | 0.001068 | -0.0020764 | -0.0034287 | -0.0045117 | 0.0015209 | -54.3411 | 65.831 | -56.9595 | 65.6616 | -56.4331 | -56.8542 | -56.2729 | -55.8243 | 65.8813 | -56.9595 | -56.8954 | -56.9138 | -56.9733 | -56.7169 | -0.013733 | 0.013733 | -0.15564 | 0.5127 | 0.67291 | 0.091553 | 0.68665 | 0.10529 | -0.013733 | 0.064087 | -122.7127 | 0.032044 | 0.22888 | -0.027466 | 0.24262 | -0.013733 | 0.52643 | 122.6212 | 0.045777 | 0.064087 | 122.7905 | 122.8409 | 122.7768 | 122.8271 | -122.7768 | -122.7768 | 122.6074 | 0.050354 | 2.6047 | 1.1215
2500.1719 | 122.9736 | -56.9595 | 65.863 | -0.075836 | -0.0013009 | 0.061598 | 0.071609 | 0.0020828 | -0.0022943 | 0.0034992 | -0.08374 | 0.00067495 | 0.0012818 | -0.00229 | -0.00043791 | -0.0040845 | -0.0018971 | -54.2953 | 65.8813 | -57.0099 | 65.6982 | -56.4239 | -56.8542 | -56.3095 | -55.7922 | 65.9363 | -57.0053 | -56.8588 | -56.955 | -57.0374 | -56.7307 | -0.050354 | 0.018311 | -0.1648 | 0.53558 | 0.65002 | 0.10529 | 0.70038 | 0.15564 | -0.045776 | 0.073242 | -122.7219 | 0.004578 | 0.22888 | -0.07782 | 0.27466 | -0.032044 | 0.58594 | 122.7081 | 0.050354 | 0.14648 | 122.8912 | 122.9416 | 122.8409 | 122.8958 | -122.8729 | -122.8683 | 122.6578 | 0.10071 | 2.6642 | 1.1673
2501.1719 | 122.9507 | -56.9275 | 65.9225 | -0.098725 | -0.00066014 | 0.061812 | 0.069045 | -0.00090783 | 0.0017645 | 0.0047808 | -0.044067 | 0.0021703 | -0.0014954 | 0.00091422 | -0.0021469 | -0.0028027 | -0.0016833 | -54.3228 | 65.8859 | -56.9641 | 65.6525 | -56.488 | -56.8588 | -56.337 | -55.8517 | 65.9409 | -56.9733 | -56.8817 | -56.9275 | -57.0374 | -56.7398 | -0.036621 | -0.036621 | -0.27008 | 0.43945 | 0.59051 | 0.068664 | 0.62714 | 0.10529 | -0.045777 | 0.018311 | -122.8043 | 0 | 0.18768 | -0.10986 | 0.23346 | -0.064087 | 0.47607 | 122.6166 | 0.045777 | 0.091553 | 122.85 | 122.9141 | 122.8134 | 122.8683 | -122.8867 | -122.8958 | 122.58 | 0.045776 | 2.6047 | 1.0757
2502.1719 | 123.0194 | -56.955 | 65.831 | -0.11398 | -0.00087374 | 0.060957 | 0.067336 | -0.00026703 | -0.00015811 | 0.0067036 | -0.028809 | -0.00060665 | 0.00021363 | 0.0071094 | -0.0012925 | -0.0032301 | 2.554e-05 | -54.3228 | 65.8218 | -56.9412 | 65.6708 | -56.4011 | -56.8497 | -56.2592 | -55.7968 | 65.8447 | -56.9778 | -56.8497 | -56.9 | -57.0099 | -56.7032 | 0.013733 | -0.009156 | -0.16022 | 0.55389 | 0.6958 | 0.10529 | 0.68207 | 0.091553 | -0.022888 | 0.013733 | -122.6807 | 0.054932 | 0.25177 | -0.054932 | 0.27466 | -0.032044 | 0.54016 | 122.612 | 0.07782 | 0.12817 | 122.7631 | 122.8226 | 122.7768 | 122.7997 | -122.7722 | -122.8088 | 122.6257 | 0.10529 | 2.6321 | 1.1581
2503.1719 | 122.9919 | -56.9504 | 65.8401 | -0.068207 | 0.0014761 | 0.062666 | 0.068832 | -0.00026703 | 0.0034735 | 0.0034992 | -0.0074462 | 0.0017431 | 2.8e-08 | 0.0019824 | -0.00043791 | -0.0040845 | 0.0013073 | -54.332 | 65.831 | -56.955 | 65.6616 | -56.4377 | -56.8451 | -56.2729 | -55.8243 | 65.8539 | -56.9916 | -56.8588 | -56.8909 | -57.0099 | -56.7078 | -0.004578 | -0.009155 | -0.17853 | 0.5127 | 0.67749 | 0.10529 | 0.68207 | 0.10986 | -0.041199 | 0.013733 | -122.699 | 0.059509 | 0.24261 | -0.05951 | 0.28381 | -0.018311 | 0.51727 | 122.6166 | 0.10071 | 0.13275 | 122.786 | 122.8455 | 122.7814 | 122.8043 | -122.7951 | -122.8317 | 122.612 | 0.091552 | 2.6184 | 1.1261
2504.1719 | 123.0148 | -56.9366 | 65.8447 | -0.075836 | -0.00066014 | 0.063094 | 0.067336 | 0.0010148 | 0.0019781 | 0.003072 | -0.022705 | 0.00067495 | -0.0014954 | -0.0016492 | -0.0021469 | -0.0032301 | 0.0040845 | -54.2908 | 65.8081 | -56.9412 | 65.7074 | -56.3873 | -56.8222 | -56.2363 | -55.7648 | 65.8585 | -56.9916 | -56.8176 | -56.8909 | -56.9824 | -56.6895 | -0.004577 | -0.036622 | -0.13733 | 0.54932 | 0.70038 | 0.11444 | 0.70496 | 0.11902 | -0.054931 | 0.013732 | -122.6624 | 0.045777 | 0.24719 | -0.045776 | 0.30212 | 0.009155 | 0.55389 | 122.6486 | 0.10071 | 0.17395 | 122.7493 | 122.85 | 122.7448 | 122.7951 | -122.786 | -122.8363 | 122.644 | 0.11902 | 2.6459 | 1.1719
2505.1719 | 123.0286 | -56.9229 | 65.8356 | -0.15976 | 0.0012625 | 0.063521 | 0.067763 | 0.0010148 | 0.0013373 | 0.00414 | -0.03186 | 0.00024775 | 0.001068 | -0.003999 | -0.0034287 | -0.0042981 | -0.0014697 | -54.2679 | 65.8356 | -56.9366 | 65.7074 | -56.3919 | -56.813 | -56.2637 | -55.7465 | 65.8539 | -56.955 | -56.8176 | -56.8726 | -56.9778 | -56.6666 | -0.013733 | 0 | -0.12817 | 0.53101 | 0.65918 | 0.10986 | 0.67291 | 0.1236 | -0.032043 | 0.018311 | -122.6532 | 0.050354 | 0.25635 | -0.054931 | 0.28839 | -0.022888 | 0.54474 | 122.644 | 0.082397 | 0.13733 | 122.7722 | 122.8088 | 122.7585 | 122.7768 | -122.7722 | -122.7905 | 122.6303 | 0.10529 | 2.655 | 1.1765
2506.1719 | 122.9233 | -56.9412 | 65.9225 | -0.052948 | -0.0015145 | 0.061385 | 0.068832 | -0.003685 | 0.0011237 | 0.0052082 | -0.022705 | 0.0017431 | -0.0019226 | -0.0010084 | -0.0021469 | -0.0047253 | -0.0021107 | -54.3457 | 65.9088 | -56.9275 | 65.6662 | -56.4514 | -56.8405 | -56.2958 | -55.6915 | 65.9866 | -56.9275 | -56.8909 | -56.955 | -57.0374 | -56.7398 | 0.013733 | -0.013733 | -0.25635 | 0.48981 | 0.64545 | 0.10071 | 0.63171 | 0.086975 | 0.013733 | 0.064087 | -122.8134 | -0.013733 | 0.20142 | -0.096131 | 0.18768 | -0.10986 | 0.47607 | 122.5937 | -0.027466 | 0.036621 | 122.8363 | 122.9141 | 122.85 | 122.9279 | -122.85 | -122.85 | 122.6074 | 0.050354 | 2.5955 | 1.2497
2507.1719 | 123.0103 | -56.9229 | 65.8356 | -0.10635 | 0.0014761 | 0.061385 | 0.0699 | 0.0012284 | 0.00069649 | 0.0069172 | -0.041016 | 0.0013159 | -0.0014954 | 0.00027342 | -0.00065151 | -0.0047253 | 0.0023755 | -54.2953 | 65.8218 | -56.9321 | 65.7028 | -56.3782 | -56.8268 | -56.2408 | -55.7556 | 65.8768 | -56.9641 | -56.8039 | -56.8817 | -56.9778 | -56.6803 | -0.009155 | -0.013733 | -0.13275 | 0.54474 | 0.68207 | 0.096131 | 0.69122 | 0.10529 | -0.041198 | 0.041199 | -122.6395 | 0.041199 | 0.24262 | -0.054931 | 0.28381 | -0.013733 | 0.55389 | 122.6349 | 0.082397 | 0.16022 | 122.7539 | 122.8409 | 122.7448 | 122.7997 | -122.7676 | -122.7997 | 122.6257 | 0.11902 | 2.6276 | 1.1673
2508.1719 | 123.0789 | -56.9321 | 65.8447 | -0.16739 | 0.00040806 | 0.063307 | 0.070113 | -5.343e-05 | 0.00048269 | 0.0039264 | -0.0043946 | 0.00088875 | -0.00021357 | 0.0030506 | -0.0012925 | -0.0042981 | -0.00040166 | -54.277 | 65.8035 | -56.9092 | 65.7028 | -56.3644 | -56.813 | -56.2546 | -55.7465 | 65.8676 | -56.9733 | -56.8039 | -56.8542 | -56.9733 | -56.6345 | 0.022888 | -0.041199 | -0.14191 | 0.56763 | 0.67749 | 0.11902 | 0.6546 | 0.096131 | -0.041199 | 0.022888 | -122.6486 | 0.07782 | 0.29755 | -0.041199 | 0.33875 | 0 | 0.54474 | 122.612 | 0.11902 | 0.16937 | 122.7127 | 122.8409 | 122.7356 | 122.7997 | -122.7539 | -122.818 | 122.6349 | 0.12817 | 2.655 | 1.1856
2509.1719 | 123.0515 | -56.9 | 65.831 | -0.12924 | -1.9142e-05 | 0.063307 | 0.070541 | 0.00037377 | 0.0028327 | 0.0090534 | -0.0043946 | -0.00039305 | 2.8e-08 | 0.0045458 | -0.0010787 | -0.0038709 | -0.0033923 | -54.2633 | 65.8081 | -56.9458 | 65.7349 | -56.218 | -56.6849 | -56.2729 | -55.7236 | 65.8768 | -56.9641 | -56.7947 | -56.868 | -56.9595 | -56.6437 | -0.045777 | -0.022889 | -0.096131 | 0.68207 | 0.62714 | 0.21515 | 0.67291 | 0.26093 | -0.064087 | 0.045776 | -122.6257 | 0.032043 | 0.25635 | -0.05951 | 0.32043 | 0.004577 | 0.72784 | 122.6807 | 0.09613 | 0.16937 | 122.7539 | 122.8409 | 122.7081 | 122.7768 | -122.7768 | -122.7951 | 122.6349 | 0.10529 | 2.6367 | 1.1765
2510.1719 | 122.9965 | -56.9046 | 65.863 | -0.12161 | 0.00040806 | 0.062239 | 0.070327 | -5.343e-05 | 0.0019781 | 0.0060626 | -0.010498 | 0.0013159 | 0.0021362 | -0.0072034 | -0.0019333 | -0.0040845 | -0.00082886 | -54.2862 | 65.8173 | -56.9412 | 65.7394 | -56.3782 | -56.8039 | -56.2317 | -55.7419 | 65.8859 | -56.9641 | -56.8222 | -56.8634 | -56.9778 | -56.6666 | -0.036621 | -0.045776 | -0.1236 | 0.52643 | 0.67291 | 0.10071 | 0.70953 | 0.13733 | -0.059509 | 0.022888 | -122.6852 | 0.041199 | 0.23804 | -0.073242 | 0.29755 | -0.013733 | 0.56305 | 122.6807 | 0.10071 | 0.14191 | 122.7585 | 122.85 | 122.7219 | 122.7905 | -122.8043 | -122.8271 | 122.644 | 0.082397 | 2.6184 | 1.1627
2511.1719 | 123.0148 | -56.9229 | 65.8676 | -0.12924 | -0.00066014 | 0.062453 | 0.06755 | 0.0010148 | 0.0019781 | 0.002431 | 0.032227 | -0.0012477 | -0.0010682 | 0.0013416 | -0.0012925 | -0.0025891 | -0.0042469 | -54.3091 | 65.8722 | -56.9275 | 65.7074 | -56.4056 | -56.7993 | -56.2225 | -55.7693 | 65.9088 | -56.9504 | -56.8314 | -56.8451 | -56.9412 | -56.6574 | -0.004577 | 0.004577 | -0.16022 | 0.51727 | 0.70038 | 0.1236 | 0.70496 | 0.12817 | -0.027465 | 0.041198 | -122.699 | 0.07782 | 0.2655 | -0.01831 | 0.29297 | 0.009155 | 0.52185 | 122.6349 | 0.10529 | 0.11902 | 122.7997 | 122.8592 | 122.7951 | 122.8317 | -122.7951 | -122.818 | 122.6303 | 0.091553 | 2.6138 | 1.1536
2512.1719 | 123.056 | -56.9138 | 65.8356 | -0.13687 | 0.00083526 | 0.060957 | 0.071822 | 0.00037377 | 0.0021917 | 0.0034992 | -0.044067 | 0.0017431 | -0.001709 | 0.003905 | -0.0030013 | -0.0019483 | -0.0016833 | -54.3182 | 65.8676 | -56.955 | 65.6891 | -56.4331 | -56.8588 | -56.2912 | -55.7785 | 65.8859 | -56.9412 | -56.8085 | -56.8771 | -56.9687 | -56.6391 | -0.041199 | 0.032044 | -0.14648 | 0.48065 | 0.62256 | 0.054931 | 0.66376 | 0.09613 | -0.027466 | 0.050354 | -122.644 | 0.036621 | 0.27466 | -0.054932 | 0.30212 | -0.027466 | 0.52185 | 122.644 | 0.064087 | 0.13275 | 122.8226 | 122.8271 | 122.7814 | 122.7997 | -122.7905 | -122.7768 | 122.6028 | 0.10528 | 2.5955 | 1.1353
2513.1719 | 123.0881 | -56.9046 | 65.8722 | -0.11398 | -0.00066014 | 0.061385 | 0.069686 | 0.0040054 | 0.0036871 | 0.005849 | -0.019653 | 0.0015295 | 0.00021363 | 0.0030506 | -0.00065151 | -0.0034437 | -0.0021107 | -54.277 | 65.8264 | -56.9321 | 65.7349 | -56.3782 | -56.7902 | -56.25 | -55.7648 | 65.8997 | -56.9641 | -56.8222 | -57.0282 | -56.8726 | -56.5567 | -0.027466 | -0.045776 | -0.13733 | 0.52643 | 0.6546 | 0.11444 | 0.68207 | 0.14191 | -0.059509 | 0.027466 | -122.6944 | -0.1236 | 0.3479 | 0.032043 | 0.40741 | 0.091552 | 0.55389 | 122.6669 | -0.064087 | 0.14191 | 122.7585 | 122.8638 | 122.731 | 122.8043 | -122.8043 | -122.8363 | 122.6395 | 0.082397 | 2.6276 | 1.1398
2514.1719 | 123.0743 | -56.9092 | 65.8493 | -0.16739 | 0.00062166 | 0.062666 | 0.068404 | 0.0022964 | 0.0021917 | 0.00414 | -0.044067 | 0.0013159 | -0.0019226 | -0.0025036 | -0.00043791 | -0.0023755 | -0.0016833 | -54.3137 | 65.8676 | -56.9778 | 65.7028 | -56.3782 | -56.8176 | -56.2775 | -55.751 | 65.8722 | -56.9458 | -56.7764 | -56.8588 | -56.9778 | -56.6299 | -0.068664 | 0.018311 | -0.14648 | 0.53101 | 0.63171 | 0.091553 | 0.70038 | 0.16022 | -0.036621 | 0.022888 | -122.6257 | 0.050354 | 0.27924 | -0.068664 | 0.31586 | -0.032043 | 0.59967 | 122.6807 | 0.086975 | 0.16937 | 122.8455 | 122.818 | 122.7768 | 122.7814 | -122.8271 | -122.7951 | 122.612 | 0.13275 | 2.5955 | 1.1581
2515.1719 | 123.0377 | -56.8863 | 65.8493 | -0.068207 | 0.0010489 | 0.06288 | 0.068618 | 0.0022964 | 0.0015509 | 0.003072 | -0.047119 | 0.0021703 | -0.0023498 | 0.0030506 | -0.00043791 | -0.0015211 | 2.554e-05 | -54.3228 | 65.8722 | -56.9412 | 65.657 | -56.4423 | -56.868 | -56.3095 | -55.8197 | 65.8997 | -56.9824 | -56.8222 | -56.8497 | -57.0007 | -56.6528 | -0.054931 | 0.022888 | -0.19226 | 0.44403 | 0.57678 | 0.018311 | 0.63171 | 0.073242 | -0.09613 | 0.050354 | -122.6715 | 0.036622 | 0.23346 | -0.11444 | 0.32959 | -0.01831 | 0.49896 | 122.5983 | 0.13275 | 0.16022 | 122.8134 | 122.8821 | 122.7585 | 122.7859 | -122.7905 | -122.8317 | 122.5433 | 0.064087 | 2.5635 | 1.0666
2516.1719 | 122.9965 | -56.8451 | 65.9042 | -0.060578 | -0.0021555 | 0.059462 | 0.068191 | 0.00016017 | 0.0017645 | 0.0047808 | 0.010864 | -0.00039305 | 0.003418 | 5.9824e-05 | -0.0021469 | -0.0034437 | 0.0038709 | -54.2221 | 65.8905 | -56.8771 | 65.7623 | -56.3049 | -56.7169 | -56.1722 | -55.719 | 65.9134 | -56.9046 | -56.7627 | -56.7993 | -56.9 | -56.6254 | -0.032043 | -0.013733 | -0.14191 | 0.54016 | 0.67291 | 0.12817 | 0.70496 | 0.16022 | -0.059509 | 0.009155 | -122.6669 | 0.045777 | 0.21973 | -0.054931 | 0.27924 | 0.004578 | 0.5722 | 122.6395 | 0.10529 | 0.14191 | 122.7676 | 122.818 | 122.7356 | 122.7585 | -122.7814 | -122.8088 | 122.6074 | 0.082398 | 2.623 | 1.1261
2517.1719 | 123.0423 | -56.9138 | 65.8813 | -0.11398 | -1.9142e-05 | 0.061812 | 0.069045 | 0.0040054 | 0.0017645 | 0.0054218 | -0.041016 | -0.00017945 | 0.00085443 | -0.0027174 | -0.0025741 | -0.0053663 | -0.00061526 | -54.332 | 65.8539 | -56.955 | 65.6982 | -56.4148 | -56.8405 | -56.2729 | -55.7968 | 65.8951 | -56.9641 | -56.7856 | -56.8634 | -56.9916 | -56.6391 | -0.041199 | -0.027466 | -0.18311 | 0.49896 | 0.64087 | 0.073242 | 0.68207 | 0.11444 | -0.050354 | 0.013733 | -122.6669 | 0.050354 | 0.27466 | -0.07782 | 0.32501 | -0.027466 | 0.54016 | 122.6532 | 0.10071 | 0.17853 | 122.8088 | 122.8592 | 122.7676 | 122.8088 | -122.8363 | -122.8455 | 122.612 | 0.12817 | 2.5818 | 1.1169
2518.1719 | 122.9691 | -56.9138 | 65.8768 | -0.091095 | 0.00062166 | 0.061385 | 0.067336 | 0.00080117 | 0.0049689 | 0.0045672 | -0.068481 | 0.0023839 | 2.8e-08 | 0.0019824 | -0.0012925 | -0.0034437 | -0.00040166 | -54.2404 | 65.8722 | -56.987 | 65.5884 | -56.4377 | -56.8359 | -56.337 | -55.9067 | 65.9271 | -56.9687 | -56.8863 | -56.9504 | -57.074 | -56.7261 | -0.073243 | -0.004578 | -0.28839 | 0.47607 | 0.57678 | 0.07782 | 0.65002 | 0.15106 | -0.054932 | 0.050354 | -122.7631 | -0.036621 | 0.18768 | -0.16022 | 0.24262 | -0.10529 | 0.54932 | 122.5754 | 0.018311 | 0.082397 | 122.8592 | 122.8958 | 122.7859 | 122.8409 | -122.8638 | -122.8455 | 122.5021 | 0.027465 | 2.6733 | 1.0071
2519.1719 | 122.9004 | -56.9138 | 65.9225 | -0.068207 | 0.00083526 | 0.060744 | 0.069259 | -0.0017624 | 0.0019781 | 0.0067036 | -0.071533 | 0.0015295 | 0.001068 | -0.00015378 | -0.0036423 | -0.0028027 | -0.0036059 | -54.332 | 65.9271 | -56.9321 | 65.6158 | -56.5247 | -56.9321 | -56.369 | -55.9021 | 65.9454 | -56.987 | -56.8771 | -56.9504 | -57.0282 | -56.6711 | -0.018311 | 0.004578 | -0.3067 | 0.3891 | 0.54474 | -0.018311 | 0.56305 | 0 | -0.073243 | 0.022889 | -122.7997 | -0.036621 | 0.24261 | -0.11444 | 0.31586 | -0.041198 | 0.40741 | 122.5479 | 0.036622 | 0.10986 | 122.8592 | 122.9324 | 122.8409 | 122.8592 | -122.8546 | -122.9095 | 122.5296 | 0.036621 | 2.5818 | 1.0117
2520.1719 | 122.9416 | -56.9458 | 65.9088 | -0.10635 | -0.0017281 | 0.060957 | 0.068404 | 0.003151 | 0.0015509 | 0.0028582 | -0.037964 | 0.0013159 | 0.0029906 | -0.0033582 | -1.0706e-05 | -0.0025891 | 0.00066654 | -54.1489 | 65.9225 | -56.9183 | 65.6296 | -56.4606 | -56.9275 | -56.3416 | -55.9021 | 65.9271 | -56.9595 | -56.868 | -56.9366 | -57.0694 | -56.7169 | 0.027466 | 0.013733 | -0.27923 | 0.48523 | 0.60425 | 0.018311 | 0.57678 | -0.009155 | -0.013733 | 0.018311 | -122.7768 | 0.009155 | 0.22888 | -0.1236 | 0.24262 | -0.10986 | 0.45776 | 122.5479 | 0.022888 | 0.091553 | 122.8409 | 122.8867 | 122.8683 | 122.8729 | -122.8271 | -122.8683 | 122.5754 | 0.07782 | 2.7969 | 1.0437
2521.1719 | 122.9279 | -56.9183 | 65.8951 | -0.060578 | 0.00040806 | 0.062025 | 0.071395 | 0.001442 | 0.0024053 | 0.0045672 | -0.23633 | 0.00088875 | -0.0014954 | -0.001222 | -0.0015061 | -0.0040845 | 0.00045294 | -54.3411 | 65.8951 | -56.955 | 65.6067 | -56.488 | -56.9046 | -56.3324 | -55.6824 | 65.918 | -56.9641 | -56.8909 | -56.9321 | -57.0465 | -56.7307 | -0.036621 | 0 | -0.28839 | 0.4303 | 0.58594 | 0.013733 | 0.62256 | 0.050354 | -0.045776 | 0.022888 | -122.786 | -0.013733 | 0.18768 | -0.12817 | 0.23346 | -0.082398 | 0.46692 | 122.5616 | 0.032043 | 0.073242 | 122.85 | 122.8821 | 122.8134 | 122.8363 | -122.85 | -122.8592 | 122.525 | 0.027466 | 2.5772 | 1.236
2522.1719 | 123.0194 | -56.9229 | 65.8722 | -0.083466 | -0.00044654 | 0.062025 | 0.070968 | -0.0015488 | 0.0015509 | 0.00414 | -0.019653 | 0.0015295 | 0.00064083 | 0.0032642 | -0.00065151 | -0.0028027 | 0.0028027 | -54.3137 | 65.9271 | -56.9366 | 65.6204 | -56.5018 | -56.8863 | -56.3278 | -55.9113 | 65.9592 | -56.9641 | -56.8863 | -56.9412 | -57.0602 | -56.7215 | -0.013733 | 0.054932 | -0.25177 | 0.42114 | 0.59509 | 0.036621 | 0.60883 | 0.050354 | -0.041198 | 0.086975 | -122.7585 | -0.01831 | 0.20142 | -0.13733 | 0.24261 | -0.096131 | 0.43488 | 122.5571 | 0.022888 | 0.077819 | 122.8638 | 122.9233 | 122.85 | 122.8821 | -122.8088 | -122.8363 | 122.5433 | 0.036621 | 2.6093 | 1.0117
2523.1719 | 122.9095 | -56.9138 | 65.9409 | -0.068207 | 0.0019035 | 0.06053 | 0.069259 | -0.00026703 | -0.00037171 | 0.0047808 | -0.03186 | 0.0021703 | -0.0010682 | -0.0010084 | -0.00086511 | -0.0030163 | -0.0010425 | -54.2953 | 65.9271 | -56.9229 | 65.6479 | -56.4651 | -56.8634 | -56.3049 | -55.8929 | 65.9409 | -56.9366 | -56.8909 | -56.9687 | -57.074 | -56.7261 | -0.009156 | -0.013733 | -0.29297 | 0.44861 | 0.60882 | 0.050354 | 0.61798 | 0.05951 | -0.022889 | 0 | -122.8317 | -0.054932 | 0.18768 | -0.16022 | 0.21057 | -0.13733 | 0.45776 | 122.5708 | -0.032043 | 0.045777 | 122.85 | 122.8775 | 122.8409 | 122.8546 | -122.8638 | -122.8775 | 122.5616 | 0.022888 | 2.6184 | 1.0208
2524.1719 | 122.9645 | -56.9183 | 65.9317 | -0.068207 | 0.0025443 | 0.059035 | 0.069045 | -0.0013352 | 0.0019781 | 0.0043536 | -0.041016 | 0.0013159 | 0.0021362 | -0.0014356 | -0.00086511 | -0.0028027 | 0.0013073 | -54.3137 | 65.9317 | -56.9275 | 65.6387 | -56.4926 | -56.8954 | -56.3324 | -55.9067 | 65.9592 | -56.9595 | -56.9962 | -57.2113 | -56.813 | -56.5018 | -0.009155 | 0 | -0.29297 | 0.42572 | 0.58594 | 0.022888 | 0.59509 | 0.032043 | -0.041199 | 0.027465 | -122.9279 | -0.29297 | 0.41656 | 0.10529 | 0.45776 | 0.14648 | 0.43487 | 122.5662 | -0.25177 | -0.036621 | 122.8592 | 122.9187 | 122.85 | 122.8775 | -122.8592 | -122.8912 | 122.5571 | -0.07782 | 2.6047 | 1.0117
2525.1719 | 122.9645 | -56.8954 | 65.9409 | -0.083466 | -0.0017281 | 0.064375 | 0.069045 | 0.00037377 | -0.00058531 | 0.0049946 | -0.025757 | 0.0019567 | 0.001709 | -0.002931 | -0.0015061 | -0.0038709 | -0.0012561 | -54.2496 | 65.9088 | -56.8817 | 65.6891 | -56.3828 | -56.8085 | -56.2637 | -55.8014 | 65.9912 | -56.9229 | -56.8314 | -56.9138 | -57.0236 | -56.6849 | 0.013733 | -0.032044 | -0.25177 | 0.5127 | 0.63171 | 0.086975 | 0.61798 | 0.073242 | -0.027466 | 0.050354 | -122.7722 | -0.01831 | 0.21057 | -0.12817 | 0.23804 | -0.10071 | 0.49896 | 122.5708 | 0.009156 | 0.091553 | 122.7905 | 122.9141 | 122.8043 | 122.8867 | -122.8226 | -122.8638 | 122.5845 | 0.064087 | 2.6459 | 1.0941
2526.1719 | 122.905 | -56.9046 | 65.9317 | -0.083466 | 0.00083526 | 0.061812 | 0.070113 | 0.00251 | 0.0028327 | 0.0028582 | -0.03186 | 0.0013159 | 0.0023498 | 0.0028368 | -0.0015061 | -0.0025891 | -0.0044605 | -54.2862 | 65.9317 | -56.8863 | 65.6799 | -56.4285 | -56.8451 | -56.282 | -55.838 | 65.9729 | -56.9229 | -56.8634 | -56.9412 | -57.0602 | -56.7032 | 0.01831 | 0 | -0.25177 | 0.47607 | 0.62256 | 0.059509 | 0.60425 | 0.041199 | -0.018311 | 0.041198 | -122.7951 | -0.036621 | 0.20142 | -0.15564 | 0.21973 | -0.13733 | 0.45776 | 122.5662 | -0.01831 | 0.05951 | 122.818 | 122.8958 | 122.8363 | 122.8775 | -122.818 | -122.8546 | 122.5845 | 0.041199 | 2.6184 | 1.0666
2527.1719 | 122.937 | -56.8817 | 65.9637 | -0.068207 | -0.00066014 | 0.062453 | 0.070113 | 0.0020828 | 0.0013373 | 0.0043536 | -0.044067 | 0.0028113 | -0.0012818 | 0.0034778 | -0.0015061 | -0.0047253 | -0.00061526 | -54.2679 | 65.9225 | -56.9138 | 65.6891 | -56.3919 | -56.8085 | -56.2683 | -55.8151 | 65.9775 | -56.9046 | -56.8542 | -56.9046 | -57.019 | -56.6849 | -0.032043 | -0.041199 | -0.27466 | 0.48981 | 0.6134 | 0.073242 | 0.64545 | 0.10528 | -0.022888 | 0.013733 | -122.818 | -0.022888 | 0.19684 | -0.13733 | 0.21973 | -0.11444 | 0.52185 | 122.6028 | 0 | 0.050354 | 122.8363 | 122.8821 | 122.8043 | 122.8592 | -122.8775 | -122.8683 | 122.5708 | 0.027466 | 2.6138 | 1.0666
2528.1719 | 122.9553 | -56.9046 | 65.9454 | -0.037689 | -0.00066014 | 0.062239 | 0.069045 | -0.0011214 | 0.0015509 | 0.0045672 | -0.025757 | 0.0015295 | -0.00021357 | 0.00027342 | -0.0017197 | -0.0045117 | -0.0046741 | -54.2496 | 65.95 | -56.8863 | 65.7074 | -56.3828 | -56.7856 | -56.25 | -55.7831 | 65.9683 | -56.9138 | -56.8314 | -56.9138 | -57.0007 | -56.6666 | 0.01831 | 0.004577 | -0.23804 | 0.52185 | 0.6546 | 0.11902 | 0.63629 | 0.10071 | -0.009155 | 0.022888 | -122.7768 | -0.009155 | 0.23804 | -0.09613 | 0.24719 | -0.086975 | 0.50354 | 122.5937 | 0 | 0.082397 | 122.8363 | 122.8821 | 122.8546 | 122.8729 | -122.8317 | -122.8592 | 122.612 | 0.073242 | 2.655 | 1.1215
2529.1719 | 122.9324 | -56.8771 | 65.9637 | -0.037689 | 0.00062166 | 0.060957 | 0.069259 | 0.0016556 | 0.0034735 | 0.0071308 | -0.016602 | 0.0019567 | -0.0012818 | -0.00229 | 0.00063009 | -0.0040845 | 0.0032299 | -54.2313 | 65.9546 | -56.8771 | 65.7349 | -56.3644 | -56.781 | -56.2134 | -55.7602 | 65.9683 | -56.9092 | -56.8222 | -56.8909 | -56.987 | -56.6483 | 0 | -0.009155 | -0.22888 | 0.5127 | 0.66376 | 0.09613 | 0.66376 | 0.09613 | -0.032044 | 0.004578 | -122.7859 | -0.013733 | 0.22888 | -0.10986 | 0.26093 | -0.07782 | 0.5127 | 122.612 | 0.018311 | 0.086975 | 122.8317 | 122.8775 | 122.8317 | 122.8455 | -122.8409 | -122.8729 | 122.612 | 0.054931 | 2.6459 | 1.1169
2530.1719 | 122.9965 | -56.8542 | 65.9592 | -0.10635 | 0.0019035 | 0.061598 | 0.06755 | 0.00058737 | 0.0021917 | 0.0043536 | 0.013916 | 0.0017431 | 0.0021362 | 0.0060412 | -0.0038559 | -0.0040845 | -0.0010425 | -54.2267 | 65.9546 | -56.8726 | 65.7394 | -56.3324 | -56.7856 | -56.2088 | -55.7602 | 66.0004 | -56.9092 | -56.7993 | -56.8817 | -56.9687 | -56.6299 | -0.018311 | -0.004577 | -0.21973 | 0.52185 | 0.64545 | 0.068665 | 0.66376 | 0.086976 | -0.054932 | 0.041199 | -122.7585 | -0.027466 | 0.2243 | -0.11444 | 0.27924 | -0.059509 | 0.54016 | 122.612 | 0.027466 | 0.10986 | 122.8271 | 122.9095 | 122.8088 | 122.8546 | -122.8317 | -122.8683 | 122.5937 | 0.054932 | 2.6276 | 1.0941
2531.1719 | 122.9324 | -56.8771 | 65.9592 | -0.037689 | 0.00062166 | 0.061171 | 0.069045 | 0.0022964 | 0.0043281 | 0.0062762 | -0.0013428 | 0.0013159 | -0.00064077 | 0.0015552 | -0.00086511 | -0.0028027 | -0.0012561 | -54.2358 | 65.9546 | -56.8771 | 65.7074 | -56.3828 | -56.7993 | -56.2454 | -55.7968 | 66.0004 | -56.8954 | -56.8314 | -56.8817 | -56.9962 | -56.6803 | 0 | -0.004577 | -0.25177 | 0.49439 | 0.63171 | 0.07782 | 0.63171 | 0.07782 | -0.018311 | 0.041199 | -122.7905 | -0.004578 | 0.19684 | -0.11902 | 0.21515 | -0.10071 | 0.49439 | 122.5845 | 0.013733 | 0.064087 | 122.8317 | 122.8958 | 122.8317 | 122.8775 | -122.8363 | -122.8546 | 122.5845 | 0.045776 | 2.6413 | 1.0803
2532.1719 | 122.9919 | -56.8634 | 66.0004 | -0.03006 | -0.00023294 | 0.062666 | 0.0699 | -0.0011214 | 0.0017645 | 0.0037128 | 0.032227 | 3.4148e-05 | 0.0029906 | 0.00048702 | -0.0017197 | -0.0042981 | 0.0013073 | -54.2313 | 65.9775 | -56.8497 | 65.7303 | -56.3507 | -56.7444 | -56.2042 | -55.7144 | 66.0004 | -56.8863 | -56.7627 | -56.8359 | -56.9504 | -56.6299 | 0.013733 | -0.022888 | -0.27008 | 0.5127 | 0.65918 | 0.11902 | 0.64545 | 0.10529 | -0.022889 | 0 | -122.7631 | 0.027466 | 0.23346 | -0.086975 | 0.25635 | -0.064086 | 0.49896 | 122.58 | 0.050355 | 0.1236 | 122.8271 | 122.8867 | 122.8409 | 122.8638 | -122.85 | -122.8867 | 122.5937 | 0.10071 | 2.6321 | 1.149
2533.1719 | 122.9279 | -56.9 | 65.9683 | -0.083466 | 0.00019446 | 0.062025 | 0.068191 | 0.0040054 | 0.00091009 | 0.0069172 | 0.010864 | 0.00024775 | 0.0021362 | -0.0018628 | -0.0015061 | -0.0030163 | -0.00018806 | -54.2267 | 65.9637 | -56.868 | 65.7166 | -56.3644 | -56.7673 | -56.218 | -55.7693 | 65.9775 | -56.8771 | -56.8039 | -56.8771 | -56.9778 | -56.6528 | 0.032043 | -0.004578 | -0.25177 | 0.53558 | 0.68207 | 0.13275 | 0.65002 | 0.10071 | 0.022888 | 0.009155 | -122.7722 | 0.022888 | 0.24719 | -0.07782 | 0.2243 | -0.10071 | 0.50354 | 122.5845 | 0 | 0.073242 | 122.8317 | 122.8546 | 122.8638 | 122.8775 | -122.8363 | -122.8455 | 122.6166 | 0.09613 | 2.6733 | 1.1307
2534.1719 | 122.9691 | -56.8588 | 65.9592 | -0.098725 | 0.0019035 | 0.06288 | 0.068404 | 0.0018692 | 0.0030463 | 0.0056354 | -0.0013428 | 0.0015295 | 0.00085443 | -0.00015378 | -0.0027877 | -0.0042981 | 0.0017345 | -54.2084 | 65.9409 | -56.8726 | 65.7349 | -56.3507 | -56.7673 | -56.218 | -55.7465 | 65.9683 | -56.9138 | -56.7993 | -56.8634 | -56.987 | -56.6391 | -0.013733 | -0.01831 | -0.2243 | 0.50812 | 0.64087 | 0.091553 | 0.6546 | 0.10529 | -0.054931 | 0.009156 | -122.7585 | -0.004577 | 0.21973 | -0.12817 | 0.27466 | -0.073243 | 0.52185 | 122.6074 | 0.050354 | 0.11444 | 122.8134 | 122.8821 | 122.7997 | 122.8271 | -122.8317 | -122.8729 | 122.5937 | 0.05951 | 2.6505 | 1.1124
2535.1719 | 122.9599 | -56.8497 | 65.9592 | -0.045319 | 0.00040806 | 0.059248 | 0.068832 | -5.343e-05 | 0.00069649 | 0.0045672 | -0.0013428 | 0.00046135 | 0.002777 | 0.0015552 | -0.0012925 | -0.0036573 | 0.0015209 | -54.2267 | 65.9912 | -56.868 | 65.744 | -56.3461 | -56.7581 | -56.2042 | -55.7465 | 65.9637 | -56.8542 | -56.7947 | -56.8588 | -56.9641 | -56.6299 | -0.018311 | 0.032044 | -0.21515 | 0.50354 | 0.64545 | 0.091552 | 0.66376 | 0.10986 | -0.004578 | 0.004578 | -122.7539 | -0.009156 | 0.21973 | -0.11444 | 0.2243 | -0.10986 | 0.52185 | 122.612 | -0.004578 | 0.059509 | 122.8592 | 122.818 | 122.8409 | 122.8134 | -122.8271 | -122.8134 | 122.5937 | 0.054931 | 2.623 | 1.1032
2536.1719 | 122.9919 | -56.8359 | 65.9775 | -0.10635 | 0.0016899 | 0.061598 | 0.069045 | 0.00251 | 0.00048269 | 0.0049946 | 0.0078126 | 0.0019567 | 0.0014954 | 5.9824e-05 | -0.00043791 | -0.0030163 | 0.0032299 | -54.1901 | 65.95 | -56.8771 | 65.7623 | -56.3416 | -56.749 | -56.1951 | -55.751 | 65.9912 | -56.8634 | -56.7764 | -56.8634 | -56.9641 | -56.6345 | -0.041199 | -0.027466 | -0.21515 | 0.49438 | 0.64087 | 0.086975 | 0.68207 | 0.12817 | -0.027466 | 0.013733 | -122.7539 | -0.027466 | 0.20142 | -0.12817 | 0.22888 | -0.10071 | 0.53558 | 122.6395 | 0 | 0.086975 | 122.8271 | 122.8546 | 122.7859 | 122.8271 | -122.8546 | -122.8409 | 122.5983 | 0.059509 | 2.6459 | 1.0849
2537.1719 | 122.9828 | -56.8542 | 65.9912 | -0.16739 | 0.00083526 | 0.060316 | 0.069686 | -0.00048063 | 0.0011237 | 0.0045672 | -0.01355 | 0.00088875 | -0.00021357 | -0.007417 | 0.0010575 | -0.0030163 | -0.00082886 | -54.2084 | 65.9729 | -56.8726 | 65.7669 | -56.3187 | -56.7444 | -56.1951 | -55.7236 | 66.0004 | -56.8497 | -56.7993 | -56.8359 | -56.9641 | -56.6299 | -0.018311 | -0.018311 | -0.2243 | 0.53558 | 0.65918 | 0.10986 | 0.67749 | 0.12817 | 0.004578 | 0.009155 | -122.7905 | 0.018311 | 0.2243 | -0.10986 | 0.21973 | -0.11444 | 0.55389 | 122.6395 | 0.013733 | 0.050354 | 122.8455 | 122.85 | 122.8271 | 122.8546 | -122.8638 | -122.8409 | 122.6212 | 0.054932 | 2.6459 | 1.1307
2538.1719 | 122.9691 | -56.8542 | 65.9958 | -0.10635 | -0.00044654 | 0.062025 | 0.069686 | 0.00037377 | 0.0019781 | 0.0047808 | 0.001709 | 0.0019567 | 0.0012818 | 0.0062548 | -0.00043791 | -0.0034437 | 0.0017345 | -54.2267 | 65.9546 | -56.8771 | 65.7028 | -56.3736 | -56.7947 | -56.2271 | -55.7877 | 66.0004 | -56.8863 | -56.8176 | -56.9 | -57.0007 | -56.6666 | -0.022888 | -0.041199 | -0.29297 | 0.48065 | 0.62714 | 0.059509 | 0.65002 | 0.082397 | -0.032044 | 0.004577 | -122.8134 | -0.045776 | 0.18768 | -0.14648 | 0.21973 | -0.11444 | 0.50354 | 122.58 | -0.013732 | 0.068665 | 122.8317 | 122.8867 | 122.8088 | 122.8546 | -122.8729 | -122.8821 | 122.5571 | 0.036621 | 2.6276 | 1.0666
2539.1719 | 122.9828 | -56.8359 | 65.9866 | -0.49545 | 0.0010489 | 0.059676 | 0.06755 | 0.00037377 | 0.0024053 | 0.003072 | -0.0043946 | 0.0011023 | 0.0029906 | -0.0010084 | -0.0030013 | -0.0023755 | 0.00088014 | -54.1534 | 65.9592 | -56.8588 | 65.7761 | -56.3004 | -56.7261 | -56.1951 | -55.7373 | 66.0004 | -56.8588 | -56.7764 | -56.8451 | -56.9412 | -56.6208 | -0.022889 | -0.027466 | -0.21057 | 0.53558 | 0.64087 | 0.10986 | 0.66376 | 0.13275 | -0.022889 | 0.013733 | -122.7631 | -0.009156 | 0.21515 | -0.10529 | 0.23804 | -0.082397 | 0.55847 | 122.6349 | 0.013733 | 0.082398 | 122.818 | 122.8592 | 122.7951 | 122.8363 | -122.8455 | -122.8455 | 122.612 | 0.059509 | 2.6825 | 1.0986
2540.1719 | 122.9691 | -56.8451 | 66.0049 | -0.11398 | 0.00040806 | 0.061385 | 0.068404 | 0.001442 | 0.0015509 | 0.0039264 | -0.01355 | 0.0011023 | 0.00085443 | 0.0024096 | -0.0017197 | -0.0023755 | -0.0033923 | -54.2267 | 65.9775 | -56.8634 | 65.7166 | -56.3736 | -56.7856 | -56.2317 | -55.7968 | 66.0278 | -56.8726 | -56.8222 | -56.8771 | -57.0007 | -56.6528 | -0.01831 | -0.027466 | -0.28839 | 0.4715 | 0.6134 | 0.05951 | 0.63171 | 0.07782 | -0.027466 | 0.022888 | -122.8271 | -0.032043 | 0.19226 | -0.15564 | 0.21973 | -0.12817 | 0.48981 | 122.58 | -0.004577 | 0.050354 | 122.8409 | 122.9004 | 122.8226 | 122.8729 | -122.8683 | -122.8775 | 122.5616 | 0.022888 | 2.6184 | 1.0483
2541.1719 | 122.937 | -56.8588 | 66.0004 | -0.075836 | -0.0013009 | 0.061812 | 0.070968 | 0.004219 | 0.0013373 | 0.0084124 | 0.0047608 | 0.00046135 | 0.001709 | 0.0013416 | -1.0706e-05 | -0.0036573 | -0.00082886 | -54.2267 | 65.9729 | -56.8588 | 65.712 | -56.3644 | -56.7947 | -56.2225 | -55.7968 | 66.0004 | -56.8909 | -56.7993 | -56.8817 | -57.0053 | -56.6711 | 0 | -0.027466 | -0.28839 | 0.49439 | 0.63629 | 0.064087 | 0.63629 | 0.064087 | -0.032043 | 0 | -122.7997 | -0.022888 | 0.18768 | -0.14648 | 0.21973 | -0.11444 | 0.49439 | 122.5708 | 0.009155 | 0.091553 | 122.8317 | 122.8912 | 122.8317 | 122.8592 | -122.8592 | -122.8912 | 122.5708 | 0.05951 | 2.6321 | 1.062
2542.1719 | 122.9599 | -56.8497 | 65.9866 | -0.091095 | -0.00023294 | 0.063521 | 0.0699 | 0.0016556 | 0.00026909 | 0.0060626 | 0.001709 | 0.00024775 | 0.0036316 | 0.001128 | -0.0010787 | -0.0042981 | -0.00018806 | -54.2267 | 65.9775 | -56.8497 | 65.7257 | -56.369 | -56.7856 | -56.218 | -55.7877 | 66.0095 | -56.8771 | -56.8039 | -56.9 | -56.9916 | -56.6391 | 0 | -0.009155 | -0.26093 | 0.48065 | 0.63171 | 0.064087 | 0.63171 | 0.064087 | -0.027466 | 0.022888 | -122.7905 | -0.050354 | 0.21057 | -0.14191 | 0.23804 | -0.11444 | 0.48065 | 122.5754 | -0.022888 | 0.073242 | 122.8271 | 122.8867 | 122.8271 | 122.8592 | -122.8363 | -122.8638 | 122.5754 | 0.045776 | 2.623 | 1.062
2543.1719 | 122.9507 | -56.8359 | 65.9821 | -0.03006 | 0.0014761 | 0.059676 | 0.069045 | -0.00048063 | -0.00058531 | 0.0043536 | -0.016602 | 0.0011023 | 0.00042723 | -0.00036738 | -0.00065151 | -0.0045117 | 0.0019483 | -54.2175 | 65.9821 | -56.8405 | 65.7257 | -56.3507 | -56.7581 | -56.218 | -55.7831 | 66.0095 | -56.8817 | -56.8268 | -56.8726 | -56.9733 | -56.6483 | -0.004578 | 0 | -0.25635 | 0.48523 | 0.61798 | 0.077819 | 0.62256 | 0.082397 | -0.045777 | 0.027465 | -122.8088 | -0.036622 | 0.18768 | -0.13733 | 0.23346 | -0.091553 | 0.48981 | 122.5662 | 0.009155 | 0.054932 | 122.8226 | 122.8912 | 122.818 | 122.8455 | -122.8226 | -122.8638 | 122.5616 | 0.009155 | 2.6184 | 1.0529
2544.1719 | 122.9553 | -56.8405 | 66.0141 | -0.060578 | 0.0023307 | 0.063307 | 0.069472 | -0.00048063 | 0.00048269 | 0.005849 | 0.013916 | 0.0013159 | -0.0012818 | -0.00229 | -0.0015061 | -0.0023755 | 0.0010937 | -54.2221 | 65.9866 | -56.8771 | 65.7349 | -56.3599 | -56.7627 | -56.2088 | -55.7877 | 66.037 | -56.8634 | -56.8085 | -56.8817 | -56.9916 | -56.6528 | -0.036621 | -0.027466 | -0.27924 | 0.48065 | 0.63171 | 0.07782 | 0.66833 | 0.11444 | -0.022888 | 0.022888 | -122.8226 | -0.041199 | 0.18768 | -0.15106 | 0.21057 | -0.12817 | 0.51727 | 122.612 | -0.018311 | 0.054931 | 122.8638 | 122.9004 | 122.8271 | 122.8775 | -122.8912 | -122.8775 | 122.5754 | 0.032043 | 2.6184 | 1.0529
2545.1719 | 122.9187 | -56.8542 | 66.0004 | -0.060578 | -1.9142e-05 | 0.062453 | 0.069686 | 0.00016017 | 0.0028327 | 0.0039264 | 0.010864 | 0.00046135 | -0.00021357 | -0.0020764 | -0.00065151 | -0.0019483 | 0.00045294 | -54.2175 | 65.9958 | -56.8359 | 65.7349 | -56.3644 | -56.7627 | -56.1951 | -55.7922 | 66.037 | -56.8588 | -56.7947 | -56.8771 | -56.9733 | -56.6483 | 0.018311 | -0.004577 | -0.2655 | 0.48981 | 0.65918 | 0.091553 | 0.64087 | 0.073242 | -0.004578 | 0.036621 | -122.7951 | -0.022888 | 0.20599 | -0.11902 | 0.21057 | -0.11444 | 0.4715 | 122.5708 | -0.01831 | 0.064087 | 122.8317 | 122.8958 | 122.85 | 122.8912 | -122.8363 | -122.8592 | 122.5891 | 0.059509 | 2.6367 | 1.062
2546.1719 | 122.9599 | -56.8268 | 66.0004 | -0.060578 | -0.00087374 | 0.062025 | 0.069045 | 0.0018692 | 0.0019781 | 0.0037128 | -0.01355 | 0.0025975 | 0.001709 | -0.00079478 | -0.0017197 | -0.0051527 | -0.00061526 | -54.213 | 65.9866 | -56.8497 | 65.7257 | -56.3599 | -56.7719 | -56.1859 | -55.7877 | 66.0187 | -56.8542 | -56.813 | -56.8771 | -56.9962 | -56.6437 | -0.022888 | -0.013733 | -0.27466 | 0.46692 | 0.64087 | 0.054931 | 0.66376 | 0.077819 | -0.027466 | 0.018311 | -122.8134 | -0.050354 | 0.18311 | -0.16937 | 0.21057 | -0.14191 | 0.48981 | 122.5754 | -0.022888 | 0.041199 | 122.8363 | 122.8729 | 122.8134 | 122.8455 | -122.85 | -122.8546 | 122.5525 | 0.013733 | 2.6138 | 1.0391
2547.1719 | 122.937 | -56.8314 | 66.0095 | -0.13687 | 0.0010489 | 0.065871 | 0.070113 | 0.00037377 | 0.0039007 | 0.0056354 | -0.019653 | 0.0011023 | 0.0025634 | 0.002196 | -0.0010787 | -0.0025891 | -0.0029651 | -54.2725 | 65.9821 | -56.8588 | 65.6937 | -56.4377 | -56.8359 | -56.25 | -55.838 | 66.0049 | -56.8863 | -56.8176 | -56.6208 | -56.9412 | -56.6757 | -0.027466 | -0.027465 | -0.31586 | 0.39368 | 0.58136 | -0.004577 | 0.60883 | 0.022889 | -0.054932 | -0.004577 | -122.8271 | 0.21057 | 0.15564 | -0.10986 | 0.21057 | -0.054931 | 0.42114 | 122.5525 | 0.2655 | 0.068665 | 122.8409 | 122.8912 | 122.8134 | 122.8363 | -122.8683 | -122.8958 | 122.525 | 0.013733 | 2.5589 | 0.99335
2548.1719 | 122.9599 | -56.8085 | 66.0233 | -0.11398 | 0.00083526 | 0.061598 | 0.070113 | 0.00058737 | 0.0024053 | 0.0045672 | -0.0043946 | 0.0011023 | -0.00021357 | 0.002196 | -0.0051377 | -0.0045117 | 0.0010937 | -54.2496 | 65.9958 | -56.8542 | 65.6799 | -56.4331 | -56.8497 | -56.2363 | -55.8334 | 66.0049 | -56.9092 | -56.8222 | -56.8451 | -56.9641 | -56.6391 | -0.045776 | -0.027465 | -0.34332 | 0.37537 | 0.57221 | -0.041198 | 0.61798 | 0.004578 | -0.10071 | -0.01831 | -122.8455 | -0.036621 | 0.16937 | -0.15564 | 0.27008 | -0.054931 | 0.42114 | 122.5342 | 0.064087 | 0.086975 | 122.85 | 122.9141 | 122.8043 | 122.8134 | -122.8775 | -122.9324 | 122.4884 | -0.013733 | 2.5589 | 0.97504
2549.1719 | 122.9553 | -56.8451 | 65.9866 | -0.098725 | 0.00019446 | 0.059035 | 0.070541 | 0.0022964 | 0.0039007 | 0.0045672 | -0.03186 | -0.0042383 | 0.0012818 | -0.002931 | -0.0040695 | -0.0023755 | 0.0040845 | -54.2542 | 66.0004 | -56.8588 | 65.6845 | -56.4377 | -56.8085 | -56.4194 | -55.5817 | 66.0141 | -56.8588 | -56.7902 | -56.8497 | -56.9916 | -56.6574 | -0.013733 | 0.013733 | -0.30212 | 0.40741 | 0.42572 | 0.036621 | 0.43945 | 0.050354 | -0.013733 | 0.027466 | -122.7768 | -0.004577 | 0.18768 | -0.14648 | 0.20142 | -0.13275 | 0.42114 | 122.5433 | 0.009156 | 0.068665 | 122.8592 | 122.8729 | 122.8455 | 122.8592 | -122.8455 | -122.8455 | 122.5296 | 0.054932 | 2.5909 | 1.2634
2550.1719 | 122.9553 | -56.8451 | 65.9866 | -0.098725 | 0.0025443 | 0.063307 | 0.070754 | -0.0017624 | 0.0024053 | 0.0039264 | -0.016602 | 0.00024775 | 0.00085443 | -0.00058098 | -0.0012925 | -0.0053663 | 0.0064343 | -54.245 | 65.9958 | -56.868 | 65.4648 | -56.6345 | -56.4514 | -56.0349 | -55.8105 | 66.0324 | -56.8542 | -56.8039 | -56.868 | -56.9824 | -56.6437 | -0.022888 | 0.009156 | -0.52185 | 0.21057 | 0.81024 | 0.39368 | 0.83313 | 0.41656 | -0.009155 | 0.045777 | -122.7905 | -0.022888 | 0.20142 | -0.13733 | 0.21057 | -0.12817 | 0.23346 | 122.3328 | -0.013733 | 0.050354 | 122.8638 | 122.8867 | 122.8409 | 122.8775 | -122.8546 | -122.8409 | 122.3099 | 0.041199 | 2.6001 | 1.0345
2551.1719 | 122.9874 | -56.8085 | 65.9821 | -0.091095 | -0.0013009 | 0.063948 | 0.0699 | 0.0057144 | 0.0041143 | 0.0032856 | 0.001709 | -0.00039305 | 0.00085443 | 0.0026232 | -0.0012925 | -0.0034437 | -0.0023243 | -54.2404 | 65.9958 | -56.8359 | 65.7211 | -56.3782 | -56.7673 | -56.1996 | -55.7785 | 65.9912 | -56.8451 | -56.7535 | -56.8222 | -56.9458 | -56.5887 | -0.027465 | 0.013733 | -0.26093 | 0.4303 | 0.60883 | 0.041199 | 0.63629 | 0.068664 | -0.036621 | 0.009155 | -122.7356 | -0.013733 | 0.21973 | -0.13733 | 0.25635 | -0.10071 | 0.45776 | 122.5571 | 0.022888 | 0.091553 | 122.8317 | 122.8363 | 122.8043 | 122.7997 | -122.818 | -122.8271 | 122.5296 | 0.054932 | 2.5681 | 1.03
2552.1719 | 122.9553 | -56.8222 | 66.0141 | -0.098725 | -0.00087374 | 0.061812 | 0.067977 | -0.0017624 | 0.0024053 | 0.0039264 | -0.0043946 | -0.00082025 | 0.0029906 | 0.0013416 | -0.0021469 | -0.0040845 | 0.0036571 | -54.2267 | 65.9866 | -56.8863 | 65.7074 | -56.3599 | -56.781 | -56.2088 | -55.8334 | 66.037 | -56.8588 | -56.7947 | -56.8634 | -56.9778 | -56.6208 | -0.064087 | -0.027466 | -0.3067 | 0.46234 | 0.6134 | 0.041199 | 0.67749 | 0.10529 | -0.036621 | 0.022888 | -122.8088 | -0.041198 | 0.20142 | -0.15564 | 0.23804 | -0.11902 | 0.52643 | 122.5937 | -0.004577 | 0.064087 | 122.8729 | 122.8958 | 122.8088 | 122.8592 | -122.9004 | -122.8729 | 122.5296 | 0.027466 | 2.5955 | 0.98877
2553.1719 | 122.9553 | -56.8268 | 65.9958 | -0.25131 | 0.00062166 | 0.059676 | 0.070541 | -0.0032578 | 0.0021917 | 0.00414 | -0.010498 | 0.0032385 | 0.0019226 | 0.0043322 | -0.0015061 | -0.0055799 | -0.0029651 | -54.0436 | 65.9729 | -56.8176 | 65.7211 | -56.369 | -56.7856 | -56.2225 | -55.8197 | 66.0278 | -56.8634 | -56.7993 | -56.8497 | -56.9778 | -56.6254 | 0.009155 | -0.022889 | -0.27466 | 0.45776 | 0.60425 | 0.041199 | 0.59509 | 0.032044 | -0.036621 | 0.032043 | -122.7951 | -0.022888 | 0.20142 | -0.15106 | 0.23804 | -0.11444 | 0.44861 | 122.5388 | 0.013733 | 0.064087 | 122.7905 | 122.8912 | 122.7997 | 122.8546 | -122.8134 | -122.8592 | 122.5479 | 0.027466 | 2.7832 | 1.0071
2554.1719 | 123.024 | -56.7993 | 65.9866 | -0.068207 | -0.0010873 | 0.059462 | 0.069472 | 0.00037377 | 0.00069649 | 0.0056354 | 0.016968 | 0.00088875 | 0.0023498 | 0.002196 | -0.00065151 | -0.0053663 | -0.0012561 | -54.213 | 66.0049 | -56.8176 | 65.744 | -56.3599 | -56.7673 | -56.1768 | -55.7785 | 66.0141 | -56.8497 | -56.7352 | -56.7902 | -56.9275 | -56.5796 | -0.018311 | 0.018311 | -0.24261 | 0.43945 | 0.62256 | 0.032043 | 0.64087 | 0.050354 | -0.050354 | 0.027466 | -122.7219 | 0.009155 | 0.21973 | -0.12817 | 0.27008 | -0.07782 | 0.45776 | 122.5616 | 0.059509 | 0.11444 | 122.8226 | 122.8638 | 122.8043 | 122.8134 | -122.8043 | -122.8363 | 122.5433 | 0.064087 | 2.5864 | 1.0208
2555.1719 | 123.0103 | -56.8268 | 65.9775 | -0.15213 | -0.0010873 | 0.063094 | 0.068618 | -0.0013352 | 0.0034735 | 0.0054218 | 0.001709 | 0.0011023 | 0.0019226 | -0.0078442 | -0.0030013 | -0.0055799 | 0.0019483 | -54.2221 | 65.9821 | -56.813 | 65.7578 | -56.3553 | -56.7535 | -56.1859 | -55.751 | 66.0141 | -56.8451 | -56.7215 | -56.7902 | -56.8863 | -56.5521 | 0.013733 | 0.004578 | -0.21973 | 0.4715 | 0.64087 | 0.073242 | 0.62714 | 0.059509 | -0.018311 | 0.036621 | -122.699 | 0.036621 | 0.27466 | -0.05951 | 0.29297 | -0.041199 | 0.45776 | 122.5708 | 0.054932 | 0.1236 | 122.7951 | 122.8592 | 122.8088 | 122.8409 | -122.7905 | -122.8226 | 122.5845 | 0.10529 | 2.6047 | 1.0757
2556.1719 | 123.0011 | -56.8085 | 65.9866 | -0.083466 | -0.0019417 | 0.062239 | 0.069045 | 0.00058737 | 0.0021917 | 0.0047808 | -0.0074462 | 0.0021703 | -0.00021357 | -0.00058098 | -0.0030013 | -0.0042981 | 0.0010937 | -54.2313 | 65.9866 | -56.8268 | 65.7578 | -56.3553 | -56.7581 | -56.1722 | -55.7556 | 66.0278 | -56.8405 | -56.7307 | -56.7673 | -56.9 | -56.5704 | -0.01831 | 0 | -0.22888 | 0.45319 | 0.63629 | 0.050354 | 0.6546 | 0.068664 | -0.032043 | 0.041199 | -122.7173 | 0.041199 | 0.23804 | -0.091552 | 0.27008 | -0.059509 | 0.4715 | 122.5845 | 0.073242 | 0.10986 | 122.8134 | 122.8683 | 122.7951 | 122.8363 | -122.8134 | -122.8271 | 122.5662 | 0.07782 | 2.5772 | 1.0529
2557.1719 | 123.0148 | -56.7993 | 65.9729 | -0.075836 | 0.00083526 | 0.06053 | 0.069472 | -0.00069423 | 0.0011237 | 0.0073444 | 0.02002 | 0.0017431 | 0.00021363 | -0.0061352 | -0.0012925 | -0.0045117 | 0.0028027 | -54.2221 | 65.9866 | -56.7947 | 65.7578 | -56.3553 | -56.749 | -56.163 | -55.7602 | 66.0278 | -56.8268 | -56.7215 | -56.781 | -56.9 | -56.5567 | 0.004577 | 0.013733 | -0.21515 | 0.44403 | 0.63629 | 0.050354 | 0.63171 | 0.045777 | -0.027466 | 0.054932 | -122.6944 | 0.01831 | 0.24261 | -0.10071 | 0.27008 | -0.073242 | 0.43945 | 122.5525 | 0.045776 | 0.10529 | 122.7814 | 122.8546 | 122.7859 | 122.8271 | -122.7676 | -122.7997 | 122.5571 | 0.077819 | 2.5772 | 1.0391
2558.1719 | 123.0286 | -56.7856 | 65.9866 | -0.083466 | -0.0023691 | 0.061598 | 0.06755 | -0.0026168 | 0.0011237 | 0.0056354 | -0.010498 | 0.00024775 | 0.0021362 | -0.0010084 | -0.0025741 | -0.0028027 | 0.00023934 | -54.2038 | 65.9866 | -56.8039 | 65.7532 | -56.3599 | -56.749 | -56.1813 | -55.7465 | 66.0278 | -56.8771 | -56.7307 | -56.7947 | -56.9138 | -56.5567 | -0.018311 | 0 | -0.23346 | 0.42572 | 0.60425 | 0.036621 | 0.62256 | 0.054932 | -0.091553 | 0.041199 | -122.7173 | -0.009156 | 0.22888 | -0.12817 | 0.32043 | -0.036621 | 0.44403 | 122.5571 | 0.082397 | 0.14648 | 122.7905 | 122.905 | 122.7722 | 122.8134 | -122.7905 | -122.8638 | 122.5388 | 0.054931 | 2.5818 | 1.0391
2559.1719 | 123.0057 | -56.7947 | 66.0004 | -0.045319 | 0.0012625 | 0.06053 | 0.071181 | 0.0016556 | 0.0015509 | 0.0052082 | -0.01355 | 0.0023839 | -0.00064077 | 0.00027342 | -0.0038559 | -0.0045117 | -0.00040166 | -54.2221 | 66.0049 | -56.7902 | 65.7761 | -56.3553 | -56.7627 | -56.1722 | -55.751 | 66.0324 | -56.8405 | -56.7261 | -56.7856 | -56.9092 | -56.5567 | 0.004578 | 0.004578 | -0.2243 | 0.43945 | 0.62256 | 0.032044 | 0.61798 | 0.027466 | -0.045776 | 0.032044 | -122.7264 | 0.009156 | 0.23804 | -0.11444 | 0.28381 | -0.068665 | 0.43487 | 122.5662 | 0.054932 | 0.11444 | 122.7951 | 122.8729 | 122.7997 | 122.8271 | -122.7905 | -122.8409 | 122.5708 | 0.068665 | 2.5726 | 1.0437
2560.1719 | 123.0148 | -56.8176 | 65.9912 | -0.13687 | -0.00023294 | 0.063734 | 0.069045 | 0.0029374 | 0.0019781 | 0.005849 | -0.010498 | 0.00067495 | 0.002777 | 0.00048702 | -0.0030013 | -0.0032301 | -0.00082886 | -54.213 | 66.0095 | -56.7993 | 65.7669 | -56.3507 | -56.749 | -56.1676 | -55.7373 | 66.0324 | -56.8314 | -56.7307 | -56.7856 | -56.9046 | -56.5659 | 0.018311 | 0.01831 | -0.2243 | 0.46692 | 0.65002 | 0.068665 | 0.63171 | 0.050354 | -0.013733 | 0.041199 | -122.7219 | 0.032044 | 0.25177 | -0.086975 | 0.2655 | -0.073242 | 0.44861 | 122.5662 | 0.045777 | 0.10071 | 122.8088 | 122.8638 | 122.8271 | 122.85 | -122.7905 | -122.8226 | 122.5845 | 0.086975 | 2.6047 | 1.0803
2561.1719 | 123.0515 | -56.7856 | 65.9729 | -0.12924 | -1.9142e-05 | 0.06288 | 0.071822 | -0.0011214 | 0.0039007 | 0.0067036 | -0.0043946 | 0.0011023 | 0.001068 | -0.003999 | -0.0025741 | -0.0055799 | -0.0027515 | -54.1855 | 66.0004 | -56.8039 | 65.8218 | -56.2683 | -56.6757 | -56.0944 | -55.6961 | 66.0187 | -56.7993 | -56.6574 | -56.7169 | -56.8268 | -56.5018 | -0.018311 | 0.027466 | -0.15106 | 0.51727 | 0.69122 | 0.10986 | 0.70953 | 0.12817 | -0.013733 | 0.045777 | -122.6303 | 0.068664 | 0.28381 | -0.041199 | 0.29755 | -0.027466 | 0.53558 | 122.6257 | 0.082397 | 0.14191 | 122.8043 | 122.818 | 122.7859 | 122.8043 | -122.7768 | -122.7722 | 122.6074 | 0.12817 | 2.6001 | 1.0895
2562.1719 | 123.0423 | -56.7627 | 66.0141 | -0.098725 | -0.0015145 | 0.06053 | 0.070968 | -0.0013352 | 0.0047553 | 0.002431 | -0.022705 | 0.0017431 | 0.00064083 | -0.00015378 | -0.0032151 | -0.0040845 | -0.0029651 | -54.1946 | 66.0004 | -56.8176 | 65.8218 | -56.2912 | -56.694 | -56.1264 | -55.687 | 66.0187 | -56.8085 | -56.6574 | -56.7261 | -56.8588 | -56.4972 | -0.054932 | -0.013733 | -0.19226 | 0.4715 | 0.63629 | 0.068664 | 0.69122 | 0.1236 | -0.045777 | 0.004578 | -122.6715 | 0.036621 | 0.2655 | -0.096131 | 0.31128 | -0.050354 | 0.52643 | 122.6395 | 0.082398 | 0.15106 | 122.818 | 122.8271 | 122.7631 | 122.7814 | -122.8317 | -122.8226 | 122.5845 | 0.10529 | 2.5681 | 1.0757
2563.1719 | 123.0606 | -56.7444 | 65.9958 | -0.10635 | 0.00019446 | 0.061385 | 0.071181 | 0.00080117 | 0.0030463 | 0.0079852 | -0.034912 | 0.0013159 | 0.00042723 | 0.0026232 | -0.00043791 | -0.0032301 | 0.0023755 | -54.1809 | 65.9912 | -56.7993 | 65.8081 | -56.3187 | -56.694 | -56.1081 | -55.6915 | 66.0324 | -56.8176 | -56.6574 | -56.7581 | -56.8634 | -56.5063 | -0.054931 | -0.004578 | -0.18768 | 0.42572 | 0.63629 | 0.050354 | 0.69122 | 0.10528 | -0.073242 | 0.036621 | -122.6532 | -0.013733 | 0.23804 | -0.11902 | 0.31128 | -0.045776 | 0.48065 | 122.6074 | 0.059509 | 0.16022 | 122.7905 | 122.85 | 122.7356 | 122.7768 | -122.7951 | -122.8134 | 122.5525 | 0.086975 | 2.5635 | 1.0529
2564.1719 | 123.0377 | -56.7352 | 66.0233 | -0.13687 | -0.0017281 | 0.060744 | 0.070541 | 0.00058737 | 0.00091009 | 0.00414 | -0.028809 | 0.0025975 | 0.00021363 | 0.0026232 | -0.0023605 | -0.0045117 | -0.0012561 | -54.2038 | 66.0278 | -56.8176 | 65.799 | -56.3095 | -56.7078 | -56.131 | -55.719 | 66.0461 | -56.8222 | -56.662 | -56.7535 | -56.8634 | -56.5018 | -0.082398 | 0.004578 | -0.2243 | 0.42572 | 0.60425 | 0.027465 | 0.68665 | 0.10986 | -0.086976 | 0.022889 | -122.6852 | -0.018311 | 0.23346 | -0.12817 | 0.32043 | -0.041198 | 0.50812 | 122.6166 | 0.068665 | 0.16022 | 122.8455 | 122.8683 | 122.7631 | 122.7814 | -122.8409 | -122.8455 | 122.5342 | 0.073242 | 2.5314 | 1.0162
2565.1719 | 123.0286 | -56.7764 | 66.0141 | -0.075836 | -0.0013009 | 0.061598 | 0.068618 | -0.0021896 | 0.0047553 | 0.0039264 | -0.01355 | -0.00039305 | -0.00021357 | -0.00015378 | -0.0030013 | -0.0032301 | 2.554e-05 | -54.1992 | 66.0095 | -56.8039 | 65.7715 | -56.3141 | -56.7123 | -56.1401 | -55.7236 | 66.037 | -56.8085 | -56.694 | -56.7398 | -56.8726 | -56.5338 | -0.027466 | -0.004578 | -0.24262 | 0.46234 | 0.63629 | 0.064087 | 0.66376 | 0.091553 | -0.032044 | 0.022888 | -122.7081 | 0.036621 | 0.24262 | -0.096131 | 0.27466 | -0.064087 | 0.48981 | 122.5754 | 0.068665 | 0.11444 | 122.8134 | 122.8455 | 122.7859 | 122.8134 | -122.818 | -122.8226 | 122.5479 | 0.082397 | 2.5772 | 1.0529
2566.1719 | 122.9874 | -56.8039 | 66.0095 | -0.045319 | 0.0010489 | 0.061812 | 0.069472 | 0.001442 | 0.0019781 | 0.003072 | -0.022705 | 0.0013159 | 0.0032044 | 0.0019824 | -0.00086511 | -0.0057935 | 0.00045294 | -54.1901 | 66.0187 | -56.7993 | 65.7898 | -56.3187 | -56.7352 | -56.1356 | -55.751 | 66.0507 | -56.8176 | -56.7169 | -56.7581 | -56.8909 | -56.5475 | 0.004578 | 0.009156 | -0.21973 | 0.48523 | 0.66833 | 0.068665 | 0.66376 | 0.064087 | -0.013733 | 0.041199 | -122.7264 | 0.045776 | 0.25635 | -0.086975 | 0.27008 | -0.073242 | 0.48065 | 122.5891 | 0.059509 | 0.10071 | 122.818 | 122.8683 | 122.8226 | 122.8546 | -122.8088 | -122.8271 | 122.5937 | 0.086975 | 2.6138 | 1.0529
2567.1719 | 122.9324 | -56.7352 | 66.0919 | -0.060578 | -0.00066014 | 0.061171 | 0.0652 | -5.343e-05 | 0.00091009 | 0.0049946 | -0.010498 | 0.0025975 | 0.00042723 | -0.0042126 | -0.0027877 | -0.0049389 | -0.0036059 | -54.0985 | 66.0828 | -56.7307 | 65.863 | -56.2225 | -56.6071 | -56.0303 | -55.6824 | 66.1057 | -56.7993 | -56.6986 | -56.7215 | -56.8405 | -56.5521 | 0.004577 | -0.009155 | -0.22888 | 0.51269 | 0.70496 | 0.12817 | 0.70038 | 0.1236 | -0.064087 | 0.013733 | -122.7905 | 0.013732 | 0.1831 | -0.10529 | 0.24719 | -0.041199 | 0.50812 | 122.5937 | 0.077819 | 0.10071 | 122.8134 | 122.905 | 122.818 | 122.8409 | -122.8226 | -122.8912 | 122.5983 | 0.036621 | 2.6367 | 1.0529
2568.1719 | 123.0743 | -56.7535 | 66.037 | -0.068207 | 0.0012625 | 0.062025 | 0.0699 | 0.0012284 | 0.0043281 | 0.002431 | -0.016602 | 0.0013159 | -0.001709 | -0.00036738 | -0.00065151 | -0.0034437 | 0.00088014 | -54.1855 | 66.0187 | -56.7993 | 65.8493 | -56.2546 | -56.6711 | -56.0806 | -55.6595 | 66.0507 | -56.7764 | -56.6391 | -56.7123 | -56.8222 | -56.4789 | -0.045776 | -0.01831 | -0.18768 | 0.49896 | 0.67291 | 0.082397 | 0.71869 | 0.12817 | -0.022888 | 0.013733 | -122.6761 | 0.041199 | 0.27466 | -0.068665 | 0.29755 | -0.045777 | 0.54474 | 122.6486 | 0.064087 | 0.13733 | 122.818 | 122.8271 | 122.7722 | 122.8043 | -122.8363 | -122.8134 | 122.6028 | 0.11444 | 2.5681 | 1.0941
2569.1719 | 123.0423 | -56.7627 | 66.0095 | -0.11398 | -0.0017281 | 0.062025 | 0.072036 | 0.0020828 | 0.0028327 | 0.0049946 | -0.025757 | 0.00024775 | -0.00021357 | 0.00048702 | -0.0015061 | -0.0055799 | 0.00023934 | -54.1901 | 66.0095 | -56.7856 | 65.8081 | -56.3049 | -56.6895 | -56.1081 | -55.687 | 66.0599 | -56.7947 | -56.6391 | -56.7123 | -56.8359 | -56.4743 | -0.022888 | 0 | -0.20142 | 0.45776 | 0.6546 | 0.073242 | 0.67749 | 0.09613 | -0.032044 | 0.050354 | -122.6486 | 0.050354 | 0.28839 | -0.073242 | 0.32044 | -0.041198 | 0.48065 | 122.5937 | 0.082398 | 0.15564 | 122.7951 | 122.8546 | 122.7722 | 122.8226 | -122.7951 | -122.8043 | 122.5708 | 0.1236 | 2.5726 | 1.0757
2570.1719 | 123.0194 | -56.749 | 66.0095 | -0.1445 | 0.00019446 | 0.061385 | 0.073318 | -0.00026703 | -0.00015811 | 0.0054218 | -0.019653 | 0.00067495 | 0.0012818 | -0.0048536 | -0.0023605 | -0.0047253 | 0.0015209 | -54.1901 | 66.0507 | -56.7764 | 65.8081 | -56.3049 | -56.7078 | -56.1218 | -55.7236 | 66.0461 | -56.8176 | -56.662 | -56.7398 | -56.8451 | -56.5201 | -0.027466 | 0.041199 | -0.20142 | 0.44403 | 0.62714 | 0.041198 | 0.6546 | 0.068664 | -0.068665 | 0.036622 | -122.6715 | 0.009155 | 0.22888 | -0.096131 | 0.29755 | -0.027466 | 0.4715 | 122.5845 | 0.07782 | 0.15564 | 122.8271 | 122.8638 | 122.7997 | 122.7951 | -122.7859 | -122.8271 | 122.5571 | 0.086975 | 2.5589 | 1.0254
2571.1719 | 122.9691 | -56.749 | 66.0461 | -0.13687 | -0.0030099 | 0.059676 | 0.070327 | 0.00251 | 0.0021917 | 0.0047808 | -0.034912 | 0.00067495 | -0.0012818 | -0.0014356 | -0.00065151 | -0.0023755 | 0.0010937 | -54.1809 | 66.0324 | -56.781 | 65.7898 | -56.3004 | -56.7261 | -56.1172 | -55.7419 | 66.0553 | -56.7856 | -56.6803 | -56.7673 | -56.8817 | -56.5384 | -0.032044 | -0.013733 | -0.25635 | 0.44861 | 0.63171 | 0.022888 | 0.66376 | 0.054932 | -0.036621 | 0.009155 | -122.7264 | -0.018311 | 0.21057 | -0.13275 | 0.24719 | -0.096131 | 0.48065 | 122.5708 | 0.01831 | 0.10529 | 122.8134 | 122.8409 | 122.7814 | 122.8043 | -122.8271 | -122.8317 | 122.5388 | 0.068664 | 2.5681 | 1.0071
2572.1719 | 122.9919 | -56.7307 | 66.0553 | -0.15213 | 0.00040806 | 0.062025 | 0.069259 | 0.0016556 | 0.0017645 | 0.0045672 | 0.056641 | 0.0011023 | 0.00021363 | -0.0050672 | -0.0010787 | -0.0066479 | 0.0023755 | -54.1626 | 66.0278 | -56.7673 | 65.863 | -56.2408 | -56.6483 | -56.0486 | -55.6732 | 66.0599 | -56.7719 | -56.6711 | -56.6895 | -56.8039 | -56.4926 | -0.036621 | -0.027466 | -0.19226 | 0.48981 | 0.68207 | 0.082398 | 0.71869 | 0.11902 | -0.041199 | 0.004577 | -122.7264 | 0.041199 | 0.23804 | -0.073242 | 0.27924 | -0.032043 | 0.52643 | 122.6303 | 0.082398 | 0.10071 | 122.7951 | 122.8317 | 122.7585 | 122.7905 | -122.8226 | -122.8271 | 122.5937 | 0.059509 | 2.5681 | 1.0574
2573.1719 | 122.9324 | -56.7764 | 66.0736 | -0.052948 | 0.0010489 | 0.060103 | 0.070754 | 0.00251 | 0.00026909 | 0.0073444 | -0.050171 | 0.0011023 | 0.00021363 | 0.0026232 | -0.0027877 | -0.0028027 | 0.0030163 | -54.1809 | 66.0873 | -56.749 | 65.8127 | -56.3416 | -56.7352 | -56.1447 | -55.7785 | 66.0919 | -56.8085 | -56.7078 | -56.7856 | -56.9092 | -56.5613 | 0.027466 | 0.013733 | -0.26092 | 0.43488 | 0.63171 | 0.041199 | 0.60425 | 0.013733 | -0.032044 | 0.018311 | -122.7814 | -0.009155 | 0.21515 | -0.13275 | 0.24719 | -0.10071 | 0.40741 | 122.5616 | 0.022889 | 0.10071 | 122.8363 | 122.9004 | 122.8638 | 122.8683 | -122.8226 | -122.8821 | 122.5891 | 0.068664 | 2.5955 | 0.99793
2574.1719 | 122.937 | -56.7581 | 66.0553 | -0.098725 | -0.00087374 | 0.062453 | 0.071822 | -0.0024032 | 0.0047553 | 0.0071308 | -0.041016 | 0.0023839 | 0.00021363 | -0.001222 | 0.0012711 | -0.0034437 | -0.0023243 | -54.1946 | 66.0919 | -56.7902 | 65.6067 | -56.1676 | -56.4148 | -56.0715 | -55.7556 | 66.1148 | -56.8039 | -56.7078 | -56.7856 | -56.9229 | -56.5659 | -0.032043 | 0.036621 | -0.44861 | 0.59052 | 0.68665 | 0.34332 | 0.71869 | 0.37537 | -0.045776 | 0.059509 | -122.7631 | -0.027465 | 0.19226 | -0.16479 | 0.23804 | -0.11902 | 0.62256 | 122.3969 | 0.018311 | 0.09613 | 122.8821 | 122.9187 | 122.85 | 122.8729 | -122.8455 | -122.8592 | 122.3648 | 0.050354 | 2.5635 | 1.0025
2575.1719 | 122.9416 | -56.7444 | 66.0599 | -0.10635 | -0.00023294 | 0.060957 | 0.070327 | 0.0035782 | 0.0021917 | 0.0060626 | -0.044067 | 0.0030249 | 0.003418 | -0.0050672 | -0.0010787 | -0.0034437 | -0.00082886 | -54.2038 | 66.0553 | -56.781 | 65.8218 | -56.3004 | -56.7032 | -56.1172 | -55.751 | 66.1057 | -56.8176 | -56.6666 | -56.7627 | -56.8863 | -56.5384 | -0.036621 | -0.004577 | -0.23804 | 0.44403 | 0.62714 | 0.041199 | 0.66376 | 0.07782 | -0.073242 | 0.045777 | -122.7264 | -0.01831 | 0.20599 | -0.14191 | 0.27924 | -0.068665 | 0.48065 | 122.6028 | 0.054932 | 0.15106 | 122.8363 | 122.9233 | 122.7997 | 122.85 | -122.8409 | -122.8775 | 122.5662 | 0.07782 | 2.5406 | 0.99335
2576.1719 | 122.9324 | -56.7444 | 66.0645 | -0.045319 | 0.0021171 | 0.061598 | 0.06755 | -0.0021896 | 0.0011237 | 0.0056354 | -0.041016 | 0.0011023 | 2.8e-08 | -0.0010084 | -0.00065151 | -0.0057935 | 0.0030163 | -54.1809 | 66.069 | -56.749 | 65.7898 | -56.3278 | -56.7032 | -56.1218 | -55.7465 | 66.1011 | -56.7719 | -56.694 | -56.7856 | -56.9092 | -56.5567 | -0.004577 | 0.004578 | -0.27466 | 0.41656 | 0.62256 | 0.041199 | 0.62714 | 0.045776 | -0.027466 | 0.036621 | -122.7585 | -0.041198 | 0.18768 | -0.16479 | 0.21515 | -0.13733 | 0.42114 | 122.5388 | -0.013732 | 0.07782 | 122.818 | 122.8729 | 122.8134 | 122.8455 | -122.8134 | -122.8363 | 122.5342 | 0.050354 | 2.5635 | 0.99793
2577.1719 | 123.0698 | -56.7078 | 66.0782 | -0.12924 | 0.00083526 | 0.061171 | 0.065841 | -0.0034714 | 0.0041143 | 0.0028582 | 0.047485 | -0.00060665 | 0.0014954 | -0.0035718 | -0.0017197 | -0.0053663 | 0.00045294 | -54.1077 | 66.0736 | -56.6895 | 65.918 | -56.1584 | -56.543 | -55.957 | -55.5771 | 66.069 | -56.7398 | -56.575 | -56.6208 | -56.6803 | -56.4285 | 0.018311 | -0.004578 | -0.16022 | 0.54932 | 0.75073 | 0.16479 | 0.73242 | 0.14648 | -0.032043 | -0.009155 | -122.6532 | 0.086975 | 0.27924 | 0.027466 | 0.31128 | 0.059509 | 0.53101 | 122.6074 | 0.11902 | 0.16479 | 122.7631 | 122.8088 | 122.7814 | 122.7768 | -122.7676 | -122.818 | 122.6257 | 0.13275 | 2.6001 | 1.1307
2578.1719 | 122.8867 | -56.7398 | 66.1011 | -0.083466 | -0.0021555 | 0.062239 | 0.069686 | -0.0024032 | 0.0011237 | 0.0090534 | -0.06543 | 0.00088875 | 0.0021362 | 0.0068958 | -0.00043791 | 0.00061532 | 0.00088014 | -54.1718 | 66.0873 | -56.7764 | 65.7761 | -56.3461 | -56.7215 | -56.1447 | -55.7556 | 66.124 | -56.7902 | -56.8954 | -56.6437 | -56.6574 | -56.4423 | -0.036621 | -0.013733 | -0.32501 | 0.39368 | 0.59509 | 0.01831 | 0.63171 | 0.054931 | -0.050354 | 0.022888 | -122.9965 | 0.09613 | 0.29755 | 0.082397 | 0.3479 | 0.13275 | 0.4303 | 122.5525 | 0.14648 | -0.10529 | 122.8638 | 122.9141 | 122.8271 | 122.8638 | -122.8775 | -122.8912 | 122.5159 | -0.15564 | 2.5681 | 0.98419
2579.1719 | 122.9599 | -56.7444 | 66.1011 | -0.11398 | 0.00019446 | 0.063948 | 0.071181 | 0.0022964 | 0.0019781 | 0.0056354 | -0.071533 | 0.0025975 | 0.00064083 | 0.00070062 | -0.0021469 | -0.0051527 | -0.0023243 | -54.4418 | 66.0095 | -56.7719 | 65.8493 | -56.3141 | -56.6849 | -56.0806 | -55.7693 | 66.1148 | -56.7856 | -56.6986 | -56.7719 | -56.8726 | -56.5384 | -0.027466 | -0.091553 | -0.25177 | 0.4303 | 0.66376 | 0.05951 | 0.69122 | 0.086976 | -0.041198 | 0.013733 | -122.7997 | -0.027466 | 0.20599 | -0.12817 | 0.24719 | -0.086976 | 0.45776 | 122.6212 | 0.013732 | 0.086975 | 122.7814 | 122.9004 | 122.7539 | 122.8592 | -122.8729 | -122.8867 | 122.5937 | 0.045777 | 2.3026 | 0.97504
2580.1719 | 122.9095 | -56.7398 | 66.0919 | -0.052948 | 0.00040806 | 0.062025 | 0.070327 | 0.0035782 | 0.0017645 | 0.0067036 | -0.047119 | -0.00017945 | 0.001068 | 0.002196 | -0.00086511 | -0.0034437 | 0.0036571 | -54.1351 | 66.0782 | -56.749 | 65.831 | -56.2637 | -56.6711 | -56.0944 | -55.7373 | 66.1469 | -56.7719 | -56.6711 | -56.7993 | -56.9 | -56.5475 | -0.009155 | -0.013733 | -0.26093 | 0.47607 | 0.64545 | 0.068664 | 0.6546 | 0.077819 | -0.032044 | 0.054932 | -122.7631 | -0.059509 | 0.19226 | -0.16022 | 0.22431 | -0.12817 | 0.48523 | 122.58 | -0.027465 | 0.10071 | 122.8271 | 122.9187 | 122.818 | 122.8867 | -122.8409 | -122.8638 | 122.5708 | 0.068664 | 2.6047 | 1.0025
2581.1719 | 122.937 | -56.7078 | 66.0965 | -0.014801 | 0.00040806 | 0.063521 | 0.069259 | -0.00090783 | 0.0019781 | 0.0043536 | -0.056274 | 3.4148e-05 | -0.0010682 | -0.00036738 | -0.0019333 | -0.0030163 | 0.0013073 | -54.1397 | 66.0919 | -56.7352 | 65.8676 | -56.25 | -56.6345 | -56.0761 | -55.7007 | 66.1194 | -56.7764 | -56.6666 | -56.7398 | -56.868 | -56.5201 | -0.027465 | -0.004578 | -0.22888 | 0.45776 | 0.63171 | 0.073243 | 0.65918 | 0.10071 | -0.068664 | 0.022888 | -122.7631 | -0.032043 | 0.18768 | -0.16022 | 0.25635 | -0.091553 | 0.48523 | 122.6028 | 0.036621 | 0.10986 | 122.8271 | 122.8958 | 122.7997 | 122.8271 | -122.8317 | -122.8729 | 122.5754 | 0.041199 | 2.5681 | 1.0071
2582.1719 | 123.0789 | -56.7123 | 66.0553 | -0.098725 | 0.0010489 | 0.061598 | 0.067336 | -0.0017624 | 0.0028327 | 0.0064898 | -0.0013428 | 0.00067495 | 2.8e-08 | -0.0031446 | -1.0706e-05 | -0.0032301 | -0.0021107 | -54.1489 | 66.0782 | -56.749 | 65.8905 | -56.2134 | -56.6162 | -56.0211 | -55.6458 | 66.069 | -56.7444 | -56.5796 | -56.6391 | -56.781 | -56.4148 | -0.036621 | 0.022888 | -0.16479 | 0.49896 | 0.69122 | 0.09613 | 0.72784 | 0.13275 | -0.032044 | 0.013733 | -122.6349 | 0.073242 | 0.29755 | -0.068665 | 0.32959 | -0.036621 | 0.53558 | 122.6395 | 0.10529 | 0.16479 | 122.8271 | 122.8134 | 122.7905 | 122.7814 | -122.8043 | -122.7997 | 122.6028 | 0.13275 | 2.5635 | 1.0666
2583.1719 | 122.9324 | -56.7261 | 66.1011 | -0.060578 | 0.0010489 | 0.064162 | 0.070327 | 0.0020828 | 0.00048269 | 0.003072 | -0.034912 | 0.00046135 | 0.0021362 | 0.0024096 | -0.0027877 | -0.0030163 | -0.00082886 | -54.1122 | 66.0873 | -56.7215 | 65.863 | -56.2363 | -56.6345 | -56.0577 | -55.6915 | 66.1194 | -56.7535 | -56.6711 | -56.7352 | -56.8405 | -56.5155 | 0.004577 | -0.013733 | -0.23804 | 0.48981 | 0.66833 | 0.091553 | 0.66376 | 0.086976 | -0.027466 | 0.018311 | -122.7722 | -0.009155 | 0.21057 | -0.11444 | 0.23804 | -0.086975 | 0.48523 | 122.5845 | 0.018311 | 0.082397 | 122.8088 | 122.8729 | 122.8134 | 122.8455 | -122.8226 | -122.8546 | 122.5891 | 0.054931 | 2.6138 | 1.0345
2584.1719 | 122.9233 | -56.7169 | 66.1194 | 0.00045798 | -0.0013009 | 0.063094 | 0.070541 | -0.0011214 | 0.0015509 | 0.0052082 | -0.034912 | 0.0028113 | 0.0023498 | 0.0032642 | -0.0021469 | -0.0038709 | 0.0025891 | -54.1077 | 66.1148 | -56.7169 | 65.8722 | -56.2134 | -56.6025 | -56.0394 | -55.6595 | 66.1285 | -56.7398 | -56.6528 | -56.7215 | -56.8268 | -56.5063 | 0 | -0.004578 | -0.24719 | 0.50354 | 0.67749 | 0.11444 | 0.67749 | 0.11444 | -0.022888 | 0.009155 | -122.7722 | -0.004578 | 0.21057 | -0.10986 | 0.23346 | -0.086975 | 0.50354 | 122.5891 | 0.01831 | 0.086975 | 122.8317 | 122.8683 | 122.8317 | 122.8455 | -122.8363 | -122.8592 | 122.5891 | 0.064087 | 2.6093 | 1.0574
2585.1719 | 122.9828 | -56.7032 | 66.1285 | -0.34287 | -0.00066014 | 0.062453 | 0.068618 | -0.0013352 | 0.0021917 | 0.0062762 | -0.025757 | 0.0019567 | -0.00064077 | -0.001222 | -0.0012925 | -0.0028027 | -0.0012561 | -54.0619 | 66.1102 | -56.7261 | 65.9042 | -56.163 | -56.5704 | -56.012 | -55.6366 | 66.1606 | -56.7398 | -56.6116 | -56.6757 | -56.7993 | -56.4972 | -0.022888 | -0.018311 | -0.2243 | 0.54016 | 0.69122 | 0.13275 | 0.71411 | 0.15564 | -0.036621 | 0.032043 | -122.7402 | 0.027466 | 0.20599 | -0.09613 | 0.24262 | -0.059509 | 0.56305 | 122.6303 | 0.064087 | 0.12817 | 122.8363 | 122.9004 | 122.8134 | 122.8638 | -122.8546 | -122.8683 | 122.6074 | 0.091553 | 2.6413 | 1.0666
2586.1719 | 122.9187 | -56.7123 | 66.124 | -0.060578 | 0.0021171 | 0.060744 | 0.069686 | 0.0016556 | 0.0034735 | 0.0032856 | -0.025757 | 0.0028113 | 0.00064083 | -0.0031446 | -0.00043791 | -0.0038709 | 0.0019483 | -54.1077 | 66.1148 | -56.6986 | 65.8676 | -56.2042 | -56.6071 | -56.0349 | -55.6641 | 66.1514 | -56.749 | -56.6574 | -56.7215 | -56.8359 | -56.4835 | 0.013733 | -0.009155 | -0.25635 | 0.50812 | 0.67749 | 0.10529 | 0.66376 | 0.091552 | -0.036621 | 0.027466 | -122.7814 | -0.009156 | 0.22888 | -0.1236 | 0.2655 | -0.086975 | 0.49438 | 122.5662 | 0.027465 | 0.091552 | 122.8134 | 122.9004 | 122.8271 | 122.8638 | -122.8226 | -122.8729 | 122.58 | 0.054931 | 2.6047 | 1.0483
2587.1719 | 122.9782 | -56.7032 | 66.124 | -0.083466 | 0.00040806 | 0.060103 | 0.067763 | -0.00048063 | 0.00091009 | 0.0056354 | 0.001709 | 0.0013159 | 0.0019226 | 0.00048702 | -0.0021469 | -0.0025891 | -0.0036059 | -54.0756 | 66.1194 | -56.6849 | 65.9042 | -56.1722 | -56.5842 | -56.012 | -55.6183 | 66.1469 | -56.7078 | -56.5979 | -56.6666 | -56.7719 | -56.4606 | 0.018311 | -0.004577 | -0.21973 | 0.53101 | 0.69122 | 0.11902 | 0.67291 | 0.10071 | -0.004578 | 0.022889 | -122.7219 | 0.036621 | 0.24262 | -0.068665 | 0.24719 | -0.064087 | 0.5127 | 122.5891 | 0.041199 | 0.10986 | 122.8043 | 122.8546 | 122.8226 | 122.85 | -122.8088 | -122.8317 | 122.6074 | 0.10529 | 2.6276 | 1.0849
2588.1719 | 122.9645 | -56.6986 | 66.1377 | -0.11398 | -1.9142e-05 | 0.062025 | 0.068618 | 0.00080117 | 0.00091009 | 0.0047808 | 0.026123 | 0.0017431 | 0.0029906 | 0.0019824 | -0.0021469 | -0.0032301 | 0.0038709 | -54.0939 | 66.1331 | -56.7032 | 65.9088 | -56.1813 | -56.543 | -56.0028 | -55.6229 | 66.1835 | -56.7078 | -56.6071 | -56.6711 | -56.781 | -56.4468 | -0.004578 | -0.004577 | -0.22888 | 0.51727 | 0.6958 | 0.15564 | 0.70038 | 0.16022 | -0.009156 | 0.045777 | -122.7448 | 0.027465 | 0.25177 | -0.082398 | 0.26093 | -0.073242 | 0.52185 | 122.612 | 0.036621 | 0.10071 | 122.8363 | 122.8912 | 122.8317 | 122.8821 | -122.8409 | -122.8455 | 122.6074 | 0.091552 | 2.6047 | 1.0757
2589.1719 | 122.9691 | -56.662 | 66.1102 | -0.052948 | 0.00019446 | 0.059889 | 0.069045 | 0.0010148 | 0.0011237 | 0.0034992 | 0.016968 | 0.0025975 | 0.0014954 | 0.00048702 | 0.0023391 | -0.0047253 | -0.0023243 | -54.0802 | 66.1285 | -56.6849 | 65.9134 | -56.1859 | -56.5567 | -56.0028 | -55.6091 | 66.156 | -56.7261 | -56.5887 | -56.6666 | -56.7307 | -56.4377 | -0.022888 | 0.018311 | -0.19684 | 0.47607 | 0.65918 | 0.10529 | 0.68207 | 0.12817 | -0.064087 | 0.045777 | -122.699 | -0.004578 | 0.2243 | -0.068665 | 0.28839 | -0.004578 | 0.49896 | 122.5983 | 0.059509 | 0.13733 | 122.8134 | 122.8821 | 122.7905 | 122.818 | -122.7951 | -122.8363 | 122.5754 | 0.073242 | 2.5818 | 1.0529
2590.1719 | 122.9782 | -56.694 | 66.1606 | -0.03006 | -1.9142e-05 | 0.061385 | 0.067763 | -0.0013352 | 0.0024053 | 0.0073444 | -0.0043946 | 0.0021703 | 0.0023498 | 0.00048702 | -0.0021469 | -0.0034437 | 0.0034435 | -54.0665 | 66.1331 | -56.6711 | 65.9363 | -56.1676 | -56.5567 | -55.9891 | -55.6183 | 66.1743 | -56.6986 | -56.5933 | -56.662 | -56.7719 | -56.4514 | 0.022888 | -0.027465 | -0.2243 | 0.52643 | 0.70496 | 0.13733 | 0.68207 | 0.11444 | -0.004577 | 0.013733 | -122.7539 | 0.032044 | 0.24262 | -0.07782 | 0.24719 | -0.073243 | 0.50354 | 122.6074 | 0.036621 | 0.10529 | 122.8043 | 122.8729 | 122.8271 | 122.8683 | -122.8317 | -122.8592 | 122.6303 | 0.10071 | 2.6276 | 1.0757
2591.1719 | 122.9736 | -56.6757 | 66.1331 | -0.068207 | 0.0016899 | 0.061385 | 0.067336 | -0.0011214 | -0.00037171 | 0.005849 | -0.0043946 | 0.00024775 | 0.00085443 | -0.001222 | -0.0021469 | -0.0038709 | 0.0017345 | -54.0894 | 66.156 | -56.6849 | 65.9134 | -56.163 | -56.5338 | -55.9799 | -55.6274 | 66.1743 | -56.7123 | -56.6025 | -56.6483 | -56.7581 | -56.4377 | -0.009155 | 0.022888 | -0.21973 | 0.5127 | 0.6958 | 0.14191 | 0.70496 | 0.15106 | -0.036621 | 0.041198 | -122.7356 | 0.027466 | 0.23804 | -0.082398 | 0.27466 | -0.045777 | 0.52185 | 122.5983 | 0.064087 | 0.10986 | 122.8409 | 122.8867 | 122.8317 | 122.85 | -122.818 | -122.8455 | 122.5891 | 0.073242 | 2.5864 | 1.0483
2592.1719 | 122.9691 | -56.6711 | 66.1514 | -0.03006 | -0.00066014 | 0.061598 | 0.06755 | -0.0011214 | 5.5488e-05 | 0.0047808 | 0.044434 | 0.0015295 | 0.0025634 | -0.0044262 | -0.0021469 | -0.0032301 | 0.0030163 | -54.0939 | 66.1606 | -56.662 | 65.95 | -56.1859 | -56.5384 | -55.9799 | -55.6137 | 66.1926 | -56.7078 | -56.6071 | -56.6391 | -56.749 | -56.4285 | 0.009156 | 0.009155 | -0.20142 | 0.48523 | 0.69122 | 0.13275 | 0.68207 | 0.1236 | -0.036621 | 0.041199 | -122.7585 | 0.032044 | 0.24262 | -0.077819 | 0.27924 | -0.041198 | 0.47607 | 122.612 | 0.068665 | 0.10071 | 122.8226 | 122.9004 | 122.8317 | 122.8638 | -122.8134 | -122.8592 | 122.6212 | 0.064087 | 2.5772 | 1.0574
2593.1719 | 122.9691 | -56.6666 | 66.1606 | -0.037689 | 0.0014761 | 0.06053 | 0.066909 | 0.0029374 | 0.00048269 | 0.0039264 | 0.035278 | 0.0028113 | 0.0023498 | 0.0030506 | -0.0032151 | -0.0034437 | -0.0012561 | -54.1031 | 66.1743 | -56.6574 | 65.8905 | -56.1859 | -56.5567 | -55.9799 | -55.6549 | 66.1972 | -56.7123 | -56.5979 | -56.6299 | -56.7581 | -56.4423 | 0.009155 | 0.013733 | -0.27008 | 0.48065 | 0.68665 | 0.10986 | 0.67749 | 0.10071 | -0.045776 | 0.036622 | -122.7585 | 0.036621 | 0.2243 | -0.091553 | 0.27008 | -0.045777 | 0.4715 | 122.5479 | 0.082397 | 0.11444 | 122.8317 | 122.9095 | 122.8409 | 122.8638 | -122.818 | -122.8729 | 122.5571 | 0.068665 | 2.5635 | 1.0117
2594.1719 | 122.9645 | -56.662 | 66.1835 | -0.060578 | -0.00023294 | 0.063094 | 0.069686 | -0.00090783 | -0.00037171 | 0.0052082 | 0.026123 | 0.0017431 | -0.0010682 | -0.0018628 | -0.0027877 | -0.0036573 | 0.00066654 | -54.0939 | 66.1514 | -56.6483 | 65.9042 | -56.1905 | -56.5704 | -55.9799 | -55.6595 | 66.2018 | -56.6986 | -56.6071 | -56.6345 | -56.7581 | -56.4423 | 0.013733 | -0.032044 | -0.27924 | 0.4715 | 0.68207 | 0.091552 | 0.66833 | 0.077819 | -0.036621 | 0.01831 | -122.7905 | 0.027466 | 0.21973 | -0.096131 | 0.25635 | -0.05951 | 0.45776 | 122.5525 | 0.064087 | 0.091552 | 122.7997 | 122.9004 | 122.8134 | 122.8638 | -122.8317 | -122.8821 | 122.5662 | 0.054931 | 2.5681 | 1.0025
2595.1719 | 122.9645 | -56.6483 | 66.156 | -0.075836 | -0.00066014 | 0.061812 | 0.070541 | -0.0038986 | -0.00037171 | 0.0049946 | 0.0078126 | 0.0021703 | 0.0032044 | -0.0052808 | -0.0032151 | -0.0053663 | -0.0016833 | -54.1122 | 66.1835 | -56.6437 | 65.9042 | -56.2088 | -56.5567 | -55.9799 | -55.6686 | 66.1743 | -56.6986 | -56.6254 | -56.6483 | -56.7673 | -56.4377 | 0.004577 | 0.027466 | -0.25177 | 0.43945 | 0.66833 | 0.091552 | 0.66376 | 0.086975 | -0.050354 | 0.01831 | -122.7814 | 0 | 0.21057 | -0.11902 | 0.26093 | -0.068665 | 0.43488 | 122.5479 | 0.050354 | 0.073242 | 122.8271 | 122.8729 | 122.8317 | 122.8226 | -122.7997 | -122.8546 | 122.5525 | 0.022888 | 2.536 | 0.97961
2596.1719 | 122.9919 | -56.6391 | 66.2064 | -0.052948 | -0.00087374 | 0.061171 | 0.0699 | -0.0011214 | 0.00026909 | 0.0060626 | 0.0047608 | 3.4148e-05 | 0.0014954 | -0.0025036 | -0.0012925 | -0.0040845 | 0.00066654 | -54.071 | 66.188 | -56.6345 | 65.9409 | -56.1813 | -56.5338 | -55.9708 | -55.6 | 66.2064 | -56.6986 | -56.5796 | -56.6345 | -56.749 | -56.4331 | 0.004578 | -0.018311 | -0.2655 | 0.45776 | 0.66833 | 0.10529 | 0.66376 | 0.10071 | -0.059509 | 0 | -122.786 | 0.004578 | 0.20599 | -0.10986 | 0.2655 | -0.050354 | 0.45319 | 122.5754 | 0.064087 | 0.11902 | 122.8226 | 122.905 | 122.8271 | 122.8455 | -122.8409 | -122.905 | 122.58 | 0.059509 | 2.5681 | 1.0391
2597.1719 | 122.9691 | -56.6666 | 66.1743 | -0.03006 | -0.00066014 | 0.060316 | 0.069045 | 0.0040054 | 0.0013373 | 0.0054218 | 0.013916 | -0.00039305 | 0.002777 | -0.0027174 | -0.0027877 | -0.0032301 | -0.0016833 | -54.0848 | 66.1652 | -56.6391 | 65.9271 | -56.1722 | -56.5338 | -55.957 | -55.6412 | 66.1789 | -56.7032 | -56.5887 | -56.6437 | -56.7352 | -56.4285 | 0.027466 | -0.009155 | -0.24719 | 0.49439 | 0.70953 | 0.13275 | 0.68207 | 0.10529 | -0.036621 | 0.004578 | -122.7631 | 0.022888 | 0.23804 | -0.068664 | 0.27466 | -0.032043 | 0.46692 | 122.5662 | 0.059509 | 0.11444 | 122.8043 | 122.8821 | 122.8317 | 122.8455 | -122.8134 | -122.8775 | 122.5937 | 0.07782 | 2.5818 | 1.0254
2598.1719 | 122.9645 | -56.662 | 66.1743 | 0.00045798 | -0.00023294 | 0.062239 | 0.069472 | -0.0021896 | 0.00069649 | 0.0043536 | 0.02002 | 0.00088875 | 0.0032044 | -0.0016492 | -0.0012925 | -0.0032301 | 0.00023934 | -54.0985 | 66.188 | -56.6208 | 65.9225 | -56.1768 | -56.5384 | -55.9753 | -55.6412 | 66.2018 | -56.6986 | -56.5842 | -56.6299 | -56.749 | -56.4148 | 0.041198 | 0.013733 | -0.25177 | 0.48523 | 0.68665 | 0.1236 | 0.64545 | 0.082398 | -0.036621 | 0.027466 | -122.7585 | 0.032043 | 0.24719 | -0.086975 | 0.28381 | -0.050354 | 0.44403 | 122.5433 | 0.068664 | 0.11444 | 122.8088 | 122.9004 | 122.85 | 122.8638 | -122.7951 | -122.8729 | 122.5845 | 0.07782 | 2.5635 | 1.0208
2599.1719 | 122.9507 | -56.6437 | 66.1835 | -0.10635 | 0.0010489 | 0.060744 | 0.069686 | -0.0021896 | 0.0021917 | 0.0062762 | 0.010864 | 0.0023839 | 0.002777 | -0.0048536 | -0.00022431 | -0.0036573 | -0.0027515 | -54.0939 | 66.2064 | -56.6208 | 65.918 | -56.1951 | -56.5475 | -55.9891 | -55.6503 | 66.2247 | -56.6849 | -56.6116 | -56.6391 | -56.7535 | -56.4377 | 0.022888 | 0.022888 | -0.2655 | 0.44861 | 0.6546 | 0.096131 | 0.63171 | 0.073243 | -0.041198 | 0.041198 | -122.7951 | 0.004578 | 0.20599 | -0.10986 | 0.24719 | -0.068665 | 0.42572 | 122.5388 | 0.045776 | 0.073242 | 122.8271 | 122.9095 | 122.85 | 122.8683 | -122.8043 | -122.8683 | 122.5616 | 0.032044 | 2.5497 | 0.99335
2600.1719 | 122.9416 | -56.6345 | 66.1972 | -0.068207 | -0.0032235 | 0.063094 | 0.0699 | 0.00080117 | -0.0014399 | 0.0049946 | 0.0047608 | -0.00060665 | 0.0012818 | 0.0079638 | -0.0023605 | -0.0038709 | 0.00045294 | -54.0894 | 66.2109 | -56.662 | 65.9088 | -56.1768 | -56.543 | -55.9708 | -55.6503 | 66.2247 | -56.6528 | -56.6071 | -56.6391 | -56.7581 | -56.4514 | -0.027466 | 0.013732 | -0.28839 | 0.45776 | 0.66376 | 0.091552 | 0.69122 | 0.11902 | -0.018311 | 0.027465 | -122.8043 | -0.004578 | 0.1831 | -0.1236 | 0.20142 | -0.10529 | 0.48523 | 122.5708 | 0.013733 | 0.045776 | 122.8729 | 122.8775 | 122.8455 | 122.8592 | -122.8592 | -122.85 | 122.5433 | 0.027465 | 2.5452 | 0.98419
2601.1719 | 122.9233 | -56.6666 | 66.2109 | -0.075836 | -0.00087374 | 0.058607 | 0.069259 | 0.0018692 | 0.0015509 | 0.0039264 | 0.03833 | 0.0013159 | 2.8e-08 | -0.009126 | -0.0019333 | -0.0036573 | 0.0015209 | -53.9429 | 66.2247 | -56.6162 | 65.9088 | -56.1768 | -56.5338 | -55.9799 | -55.6412 | 66.2521 | -56.6803 | -56.6025 | -56.6483 | -56.7398 | -56.4514 | 0.050354 | 0.013733 | -0.30212 | 0.48981 | 0.68665 | 0.13275 | 0.63629 | 0.082398 | -0.013733 | 0.041199 | -122.8134 | 0.018311 | 0.21515 | -0.073242 | 0.22888 | -0.059509 | 0.43945 | 122.525 | 0.032044 | 0.07782 | 122.8409 | 122.9324 | 122.8912 | 122.9187 | -122.8271 | -122.8912 | 122.5754 | 0.064087 | 2.7237 | 1.0254
2602.1719 | 122.9279 | -56.6254 | 66.2109 | -0.045319 | 0.00040806 | 0.058821 | 0.068191 | 0.0044328 | 0.0019781 | 0.0015766 | -0.037964 | 0.0019567 | -0.00042717 | -0.003999 | -0.0019333 | -0.0051527 | 0.0010937 | -54.0894 | 66.1926 | -56.6116 | 65.9454 | -56.1905 | -56.2592 | -55.8609 | -55.6366 | 66.2064 | -56.6803 | -56.5979 | -56.6254 | -56.7307 | -56.4285 | 0.013733 | -0.01831 | -0.2655 | 0.43487 | 0.76447 | 0.36621 | 0.75073 | 0.35248 | -0.054932 | -0.004577 | -122.8088 | 0 | 0.19684 | -0.10529 | 0.25177 | -0.050354 | 0.42114 | 122.5571 | 0.054932 | 0.082398 | 122.8043 | 122.8867 | 122.818 | 122.8317 | -122.8226 | -122.8912 | 122.5708 | 0.027466 | 2.536 | 0.98877
2603.1719 | 122.9599 | -56.6345 | 66.2064 | -0.022431 | -0.0010873 | 0.059889 | 0.072036 | 0.00251 | 0.0026191 | 0.0043536 | 0.013916 | 0.0011023 | 0.00085443 | 0.0043322 | -0.0015061 | -0.0040845 | -0.0031787 | -54.0848 | 66.1972 | -56.6116 | 65.9409 | -56.163 | -56.5247 | -55.9616 | -55.6458 | 66.2292 | -56.662 | -56.5887 | -56.6391 | -56.7352 | -56.4239 | 0.022888 | -0.009155 | -0.2655 | 0.4715 | 0.67291 | 0.10986 | 0.65002 | 0.086975 | -0.027466 | 0.022888 | -122.7951 | -0.004578 | 0.21057 | -0.10071 | 0.23804 | -0.073242 | 0.44861 | 122.5525 | 0.022888 | 0.073242 | 122.8088 | 122.8912 | 122.8317 | 122.8638 | -122.818 | -122.8683 | 122.5754 | 0.045776 | 2.5497 | 0.98877
2604.1719 | 122.9553 | -56.6666 | 66.2338 | -0.083466 | -0.0013009 | 0.058821 | 0.067763 | -0.0026168 | 0.0011237 | 0.0062762 | 0.03833 | 0.0019567 | 0.0023498 | -0.0031446 | -0.00043791 | -0.0040845 | -0.0010425 | -54.0756 | 66.2155 | -56.5979 | 65.9409 | -56.163 | -56.5292 | -55.957 | -55.6229 | 66.2247 | -56.6711 | -56.5887 | -56.6299 | -56.7535 | -56.4468 | 0.068665 | -0.018311 | -0.29297 | 0.50354 | 0.70953 | 0.13733 | 0.64087 | 0.068664 | -0.004578 | -0.009156 | -122.8226 | 0.036621 | 0.21973 | -0.086975 | 0.22431 | -0.082397 | 0.43488 | 122.5388 | 0.041199 | 0.082398 | 122.8134 | 122.8958 | 122.8821 | 122.8912 | -122.8317 | -122.905 | 122.6074 | 0.07782 | 2.5909 | 1.0437
2605.1719 | 122.9187 | -56.6391 | 66.2201 | -0.075836 | -0.0021555 | 0.059035 | 0.067336 | -0.0051804 | 0.0011237 | 0.0069172 | 0.0078126 | 0.0030249 | 0.00042723 | 0.0024096 | -0.0017197 | -0.0062207 | 0.00023934 | -54.0894 | 66.2338 | -56.6254 | 65.8676 | -56.3141 | -56.4972 | -55.9433 | -55.6274 | 66.2476 | -56.662 | -56.5887 | -56.6162 | -56.7398 | -56.4194 | 0.013733 | 0.013733 | -0.35248 | 0.32501 | 0.6958 | 0.14191 | 0.68207 | 0.12817 | -0.022888 | 0.027466 | -122.8088 | 0.022888 | 0.21973 | -0.10071 | 0.24261 | -0.07782 | 0.31128 | 122.493 | 0.045776 | 0.073242 | 122.8592 | 122.9095 | 122.8729 | 122.8867 | -122.8455 | -122.8821 | 122.5067 | 0.050354 | 2.5497 | 1.0117
2606.1719 | 122.937 | -56.6254 | 66.2018 | -0.045319 | -0.0010873 | 0.06288 | 0.070327 | 0.001442 | 0.00048269 | 0.0032856 | 0.023071 | 0.00088875 | 0.0014954 | 0.0064684 | -0.0010787 | -0.0045117 | 2.554e-05 | -54.0848 | 66.2384 | -56.6162 | 65.9454 | -56.1401 | -56.5155 | -55.925 | -55.687 | 66.243 | -56.6116 | -56.5659 | -56.6574 | -56.7581 | -56.4514 | 0.009155 | 0.036621 | -0.25635 | 0.48523 | 0.70038 | 0.10986 | 0.69122 | 0.10071 | 0.013733 | 0.041199 | -122.7676 | -0.032044 | 0.17395 | -0.13275 | 0.16022 | -0.14649 | 0.47607 | 122.5616 | -0.045777 | 0.045776 | 122.8546 | 122.8546 | 122.8638 | 122.8683 | -122.818 | -122.8134 | 122.5708 | 0.059509 | 2.5406 | 0.93841
2607.1719 | 122.9599 | -56.6254 | 66.2201 | -0.052948 | -0.00044654 | 0.058394 | 0.068832 | -0.0032578 | 0.0021917 | 0.00414 | 0.010864 | 0.0023839 | 0.0012818 | -0.0010084 | -0.00065151 | -0.0049389 | -0.0012561 | -54.0756 | 66.2384 | -56.6025 | 65.9363 | -56.163 | -56.5018 | -55.9433 | -55.6274 | 66.275 | -56.662 | -56.575 | -56.6162 | -56.7398 | -56.4194 | 0.022888 | 0.01831 | -0.28381 | 0.46234 | 0.68207 | 0.1236 | 0.65918 | 0.10071 | -0.036621 | 0.054931 | -122.7951 | 0.009155 | 0.20599 | -0.11444 | 0.24261 | -0.07782 | 0.43945 | 122.5388 | 0.045776 | 0.086975 | 122.8409 | 122.937 | 122.8638 | 122.9004 | -122.8226 | -122.8821 | 122.5616 | 0.050354 | 2.5497 | 0.99793
2608.1719 | 122.9324 | -56.6071 | 66.2292 | -0.12161 | -0.0015145 | 0.060957 | 0.066695 | 0.00016017 | 0.0011237 | 0.0032856 | 0.041382 | 0.00088875 | 0.0021362 | -0.0082716 | -0.0012925 | -0.0064343 | -0.00061526 | -54.0298 | 66.1926 | -56.5796 | 65.9637 | -56.1127 | -56.4835 | -55.8975 | -55.5817 | 66.2247 | -56.6437 | -56.5704 | -56.6162 | -56.7215 | -56.4285 | 0.027466 | -0.036621 | -0.2655 | 0.49439 | 0.70953 | 0.1236 | 0.68207 | 0.096131 | -0.036621 | -0.004578 | -122.7997 | -0.009155 | 0.17853 | -0.11444 | 0.21515 | -0.07782 | 0.46692 | 122.5433 | 0.027466 | 0.073242 | 122.7722 | 122.8683 | 122.7997 | 122.8317 | -122.8088 | -122.8729 | 122.5708 | 0.036621 | 2.5772 | 1.0254
2609.1719 | 122.9233 | -56.6162 | 66.2338 | -0.060578 | 0.0012625 | 0.063307 | 0.067123 | -0.00069423 | 0.00048269 | 0.0043536 | 0.056641 | 0.0019567 | 0.0014954 | -0.0014356 | -0.00065151 | -0.0040845 | -0.0029651 | -54.0115 | 66.2201 | -56.5842 | 66.0187 | -56.0715 | -56.456 | -55.8792 | -55.5817 | 66.2567 | -56.6254 | -56.5613 | -56.5979 | -56.6895 | -56.4148 | 0.032044 | -0.013733 | -0.21515 | 0.54474 | 0.737 | 0.16022 | 0.70496 | 0.12817 | -0.009155 | 0.022888 | -122.7951 | 0.018311 | 0.20142 | -0.073242 | 0.21057 | -0.064087 | 0.5127 | 122.6028 | 0.027466 | 0.064087 | 122.8043 | 122.8821 | 122.8363 | 122.8729 | -122.818 | -122.8592 | 122.6349 | 0.054932 | 2.6047 | 1.0345
2610.1719 | 122.9233 | -56.6116 | 66.2247 | -0.091095 | 0.0021171 | 0.060103 | 0.071822 | -0.0015488 | 0.00026909 | 0.0047808 | 0.02002 | 0.0019567 | 0.0029906 | 0.00091422 | -0.0034287 | -0.0055799 | -0.00061526 | -54.0619 | 66.2018 | -56.5979 | 65.9592 | -56.1264 | -56.5063 | -55.9067 | -55.5954 | 66.2659 | -56.6391 | -56.5521 | -56.7764 | -56.7215 | -56.4056 | 0.013733 | -0.022888 | -0.2655 | 0.48523 | 0.70496 | 0.10528 | 0.69122 | 0.091552 | -0.027466 | 0.041199 | -122.7768 | -0.1648 | 0.20599 | -0.10986 | 0.23346 | -0.082398 | 0.4715 | 122.5571 | -0.13733 | 0.086975 | 122.7997 | 122.905 | 122.8134 | 122.8775 | -122.8226 | -122.8638 | 122.5708 | 0.059509 | 2.5497 | 1.0162
2611.1719 | 122.9233 | -56.5933 | 66.2384 | -0.0071715 | -0.0013009 | 0.062666 | 0.069045 | 0.0012284 | 0.0017645 | 0.0064898 | 0.001709 | -0.00082025 | 0.0023498 | -0.00079478 | -0.00043791 | -0.0034437 | -0.0029651 | -54.0665 | 66.2292 | -56.6116 | 65.9729 | -56.1081 | -56.4835 | -55.925 | -55.5725 | 66.2476 | -56.6254 | -56.5521 | -56.5933 | -56.7078 | -56.4194 | -0.01831 | -0.009155 | -0.2655 | 0.48523 | 0.66833 | 0.10986 | 0.68664 | 0.12817 | -0.032043 | 0.009156 | -122.7905 | 0 | 0.17395 | -0.11444 | 0.20599 | -0.082398 | 0.50354 | 122.5845 | 0.032043 | 0.073242 | 122.8409 | 122.8729 | 122.8226 | 122.8409 | -122.85 | -122.8638 | 122.5662 | 0.041199 | 2.5269 | 1.0208
2612.1719 | 122.9416 | -56.5979 | 66.2292 | -0.083466 | -1.9142e-05 | 0.061171 | 0.069686 | -0.0028304 | -0.00058531 | 0.0056354 | 0.026123 | 0.00088875 | 0.00085443 | -0.006349 | -0.0019333 | -0.0040845 | 0.0015209 | -54.007 | 66.243 | -56.6162 | 65.9866 | -56.1081 | -56.4606 | -55.8655 | -55.5771 | 66.2613 | -56.6254 | -56.5567 | -56.5979 | -56.6986 | -56.4011 | -0.018311 | 0.013733 | -0.24262 | 0.48981 | 0.73242 | 0.13733 | 0.75073 | 0.15564 | -0.027466 | 0.032044 | -122.7859 | 0 | 0.19684 | -0.10071 | 0.2243 | -0.073242 | 0.50812 | 122.6028 | 0.027466 | 0.068664 | 122.8592 | 122.8867 | 122.8409 | 122.8592 | -122.8455 | -122.8546 | 122.5845 | 0.041198 | 2.5909 | 1.0208
2613.1719 | 122.9233 | -56.6116 | 66.2384 | -0.045319 | 0.00019446 | 0.062239 | 0.0699 | 0.00016017 | 0.00091009 | 0.0045672 | 0.02002 | -0.00039305 | 0.0036316 | -0.00229 | -0.0015061 | -0.0066479 | 0.00023934 | -54.0024 | 66.2338 | -56.5887 | 66.0278 | -56.0532 | -56.4331 | -55.8563 | -55.5359 | 66.275 | -56.6208 | -56.5475 | -56.5887 | -56.6895 | -56.4011 | 0.022888 | -0.004577 | -0.21057 | 0.55847 | 0.75531 | 0.17853 | 0.73242 | 0.15564 | -0.009156 | 0.036621 | -122.7859 | 0.022888 | 0.21057 | -0.07782 | 0.21973 | -0.068664 | 0.53558 | 122.6166 | 0.032044 | 0.073243 | 122.8226 | 122.8958 | 122.8455 | 122.8867 | -122.8271 | -122.8592 | 122.6395 | 0.064087 | 2.6093 | 1.0757
2614.1719 | 122.9462 | -56.6208 | 66.2659 | -0.03006 | 0.00040806 | 0.061385 | 0.069686 | 0.00016017 | 0.00048269 | 0.0064898 | 0.010864 | 3.4148e-05 | 0.0023498 | 0.002196 | -0.0012925 | -0.0085705 | -0.0016833 | -54.0344 | 66.2476 | -56.5979 | 65.9683 | -56.1127 | -56.4789 | -55.9113 | -55.6 | 66.2659 | -56.6208 | -56.4697 | -56.694 | -56.8588 | -56.4468 | 0.022889 | -0.01831 | -0.29755 | 0.50812 | 0.70953 | 0.14191 | 0.68665 | 0.11902 | 0 | 0 | -122.7356 | -0.073242 | 0.17395 | -0.23804 | 0.17395 | -0.23804 | 0.48523 | 122.5662 | -0.073242 | 0.15106 | 122.8455 | 122.8867 | 122.8683 | 122.8867 | -122.8638 | -122.8867 | 122.5891 | 0.15106 | 2.5864 | 1.0208
2615.1719 | 122.9782 | -56.5842 | 66.2155 | -0.083466 | 0.0016899 | 0.061598 | 0.068404 | -0.00069423 | 0.0032599 | 0.0064898 | 0.044434 | -0.00017945 | -0.0010682 | -0.00058098 | -0.0012925 | -0.0062207 | -0.0036059 | -53.9795 | 66.2109 | -56.5842 | 66.0782 | -56.0257 | -56.3965 | -55.8105 | -55.4993 | 66.2659 | -56.6162 | -56.5063 | -56.5338 | -56.6391 | -56.337 | 0 | -0.004578 | -0.13733 | 0.55847 | 0.77362 | 0.18768 | 0.77362 | 0.18768 | -0.032044 | 0.050354 | -122.7219 | 0.050354 | 0.24719 | -0.054932 | 0.27924 | -0.022888 | 0.55847 | 122.6624 | 0.082398 | 0.10986 | 122.7951 | 122.8821 | 122.7951 | 122.85 | -122.7997 | -122.8317 | 122.6624 | 0.077819 | 2.6047 | 1.0849
2616.1719 | 122.9828 | -56.5659 | 66.2567 | -0.098725 | 0.0014761 | 0.060316 | 0.069472 | -0.0028304 | -0.00037171 | 0.0015766 | 0.010864 | 0.0021703 | -0.0012818 | 0.0028368 | -0.0027877 | -0.0049389 | 0.00088014 | -53.9795 | 66.2201 | -56.5475 | 66.0782 | -55.9891 | -56.3782 | -55.806 | -55.4626 | 66.2796 | -56.5842 | -56.4697 | -56.4972 | -56.5933 | -56.3141 | 0.018311 | -0.036621 | -0.17853 | 0.57678 | 0.75989 | 0.18768 | 0.74158 | 0.16937 | -0.01831 | 0.022888 | -122.7264 | 0.068665 | 0.25177 | -0.027466 | 0.27008 | -0.009156 | 0.55847 | 122.6257 | 0.086975 | 0.11444 | 122.7676 | 122.8638 | 122.786 | 122.8455 | -122.8043 | -122.8409 | 122.644 | 0.09613 | 2.5864 | 1.1032
2617.1719 | 122.9462 | -56.5933 | 66.275 | -0.091095 | -0.00087374 | 0.058821 | 0.0699 | 0.00058737 | 0.00048269 | 0.0071308 | 0.029175 | 0.0013159 | -0.001709 | -0.00036738 | -0.00043791 | -0.0055799 | -0.0014697 | -53.9932 | 66.2247 | -56.5796 | 66.0461 | -56.0349 | -56.4331 | -55.8334 | -55.5084 | 66.2842 | -56.5979 | -56.543 | -56.543 | -56.6483 | -56.3828 | 0.013733 | -0.050354 | -0.22888 | 0.55847 | 0.75989 | 0.16022 | 0.74616 | 0.14649 | -0.004577 | 0.009156 | -122.818 | 0.050354 | 0.21057 | -0.054931 | 0.21515 | -0.050354 | 0.54474 | 122.6257 | 0.054931 | 0.054931 | 122.8043 | 122.8821 | 122.818 | 122.8775 | -122.8546 | -122.8729 | 122.6395 | 0.050354 | 2.6001 | 1.0849
2618.1719 | 122.9645 | -56.575 | 66.2384 | -0.060578 | 0.0014761 | 0.063094 | 0.069045 | -0.0026168 | 0.0017645 | 0.00414 | 0.02002 | 0.0017431 | 0.0029906 | -0.0054944 | -0.0025741 | -0.0032301 | -0.0012561 | -53.9703 | 66.2292 | -56.5521 | 66.0645 | -56.0303 | -56.3782 | -55.8151 | -55.4718 | 66.2521 | -56.6162 | -56.4926 | -56.5201 | -56.6299 | -56.3507 | 0.022888 | -0.009155 | -0.17395 | 0.54474 | 0.75989 | 0.19684 | 0.737 | 0.17395 | -0.041199 | 0.013733 | -122.731 | 0.054931 | 0.2243 | -0.054932 | 0.2655 | -0.013733 | 0.52185 | 122.6166 | 0.09613 | 0.1236 | 122.7814 | 122.8683 | 122.8043 | 122.8271 | -122.7905 | -122.8546 | 122.6395 | 0.082397 | 2.6047 | 1.1032
2619.1719 | 122.9874 | -56.5384 | 66.2476 | -0.098725 | 0.00040806 | 0.060103 | 0.067977 | -0.0034714 | 0.00069649 | 0.0062762 | 0.0078126 | 0.00024775 | 0.001709 | 0.0017688 | -0.0025741 | -0.0038709 | -0.0036059 | -53.9703 | 66.2292 | -56.575 | 66.0965 | -55.9937 | -56.3782 | -55.7877 | -55.4718 | 66.243 | -56.5659 | -56.4514 | -56.5018 | -56.6116 | -56.3141 | -0.036621 | -0.018311 | -0.15106 | 0.54474 | 0.75073 | 0.16022 | 0.78735 | 0.19684 | -0.027466 | -0.004578 | -122.699 | 0.036621 | 0.2243 | -0.073242 | 0.25177 | -0.045776 | 0.58136 | 122.6715 | 0.064087 | 0.11444 | 122.8043 | 122.8088 | 122.7676 | 122.7814 | -122.8226 | -122.8134 | 122.6349 | 0.086975 | 2.5681 | 1.0666
2620.1719 | 123.0103 | -56.5613 | 66.2567 | -0.075836 | -0.00087374 | 0.062239 | 0.067763 | 0.0022964 | 0.0017645 | 0.0049946 | 0.0078126 | 0.0013159 | -0.0012818 | 0.00091422 | -0.0038559 | -0.0062207 | 0.00023934 | -53.9795 | 66.2201 | -56.5521 | 66.0965 | -55.9799 | -56.3782 | -55.7922 | -55.4626 | 66.2659 | -56.5521 | -56.4423 | -56.4743 | -56.5842 | -56.2912 | 0.009155 | -0.036621 | -0.16022 | 0.58136 | 0.76904 | 0.1831 | 0.75989 | 0.17395 | 0.009155 | 0.009155 | -122.699 | 0.086975 | 0.27008 | -0.022888 | 0.26093 | -0.032043 | 0.5722 | 122.6486 | 0.07782 | 0.10986 | 122.7722 | 122.818 | 122.7814 | 122.8271 | -122.8088 | -122.8088 | 122.6578 | 0.11902 | 2.5818 | 1.0986
2621.1719 | 122.9553 | -56.5887 | 66.2613 | -0.068207 | -0.0013009 | 0.061812 | 0.070754 | -0.00026703 | 0.0028327 | 0.0056354 | 0.016968 | -0.0010339 | 0.001068 | -0.00464 | -0.0019333 | -0.0064343 | -0.0012561 | -53.9795 | 66.2292 | -56.5659 | 66.0782 | -56.0028 | -56.3873 | -55.8105 | -55.5038 | 66.2888 | -56.5933 | -56.4926 | -56.5247 | -56.6391 | -56.3507 | 0.022888 | -0.032044 | -0.18311 | 0.58594 | 0.7782 | 0.20142 | 0.75531 | 0.17853 | -0.004578 | 0.027465 | -122.7539 | 0.064087 | 0.23804 | -0.050354 | 0.24262 | -0.045776 | 0.56305 | 122.644 | 0.068665 | 0.10071 | 122.7951 | 122.8821 | 122.818 | 122.8775 | -122.8271 | -122.8546 | 122.6669 | 0.09613 | 2.6093 | 1.0849
2622.1719 | 123.024 | -56.5475 | 66.243 | -0.11398 | -0.00066014 | 0.060316 | 0.066268 | -0.0024032 | 0.0049689 | 0.005849 | 0.041382 | -0.00060665 | 0.0012818 | -0.001222 | -0.0017197 | -0.0032301 | 0.00045294 | -53.9566 | 66.2201 | -56.5247 | 66.0233 | -55.9296 | -56.369 | -55.806 | -55.4398 | 66.2064 | -56.575 | -56.4102 | -56.4239 | -56.5567 | -56.2958 | 0.022888 | -0.022888 | -0.21973 | 0.61798 | 0.74158 | 0.17853 | 0.71869 | 0.15564 | -0.027466 | -0.036621 | -122.6532 | 0.1236 | 0.25177 | -0.009156 | 0.27924 | 0.01831 | 0.59509 | 122.5479 | 0.15106 | 0.16479 | 122.7448 | 122.7814 | 122.7676 | 122.7539 | -122.7676 | -122.818 | 122.5708 | 0.13733 | 2.5909 | 1.1078
2623.1719 | 123.0606 | -56.5521 | 66.2247 | -0.098725 | 0.0021171 | 0.061598 | 0.066054 | 0.00080117 | 0.0017645 | 0.0043536 | 0.13904 | 0.0090063 | 0.0032044 | 0.0024096 | -0.0012925 | -0.0062207 | -0.0031787 | -53.9337 | 66.2201 | -56.543 | 66.1102 | -55.9525 | -56.3278 | -55.7007 | -55.632 | 66.2659 | -56.5796 | -56.4148 | -56.4651 | -56.5201 | -56.2729 | 0.009155 | -0.004577 | -0.11444 | 0.59967 | 0.85144 | 0.2243 | 0.84228 | 0.21515 | -0.027466 | 0.041199 | -122.6395 | 0.086975 | 0.27924 | 0.032043 | 0.3067 | 0.059509 | 0.59051 | 122.6532 | 0.11444 | 0.1648 | 122.7631 | 122.8455 | 122.7722 | 122.818 | -122.7676 | -122.8043 | 122.6624 | 0.13733 | 2.6184 | 0.9201
2624.1719 | 123.0194 | -56.5109 | 66.2704 | -0.060578 | 0.0012625 | 0.061812 | 0.067763 | 0.001442 | 0.0034735 | 0.0043536 | 0.013916 | -0.0010339 | 0.0021362 | -0.0027174 | -0.0030013 | -0.0053663 | -0.0012561 | -53.9612 | 66.2384 | -56.5338 | 66.1331 | -55.9662 | -56.3599 | -55.7739 | -55.4489 | 66.243 | -56.5796 | -56.4102 | -56.4468 | -56.5475 | -56.2775 | -0.022888 | -0.032044 | -0.13733 | 0.54474 | 0.737 | 0.15106 | 0.75989 | 0.17395 | -0.068665 | -0.027466 | -122.6807 | 0.064087 | 0.23346 | -0.036621 | 0.30212 | 0.032044 | 0.56763 | 122.6669 | 0.13275 | 0.16937 | 122.7722 | 122.8226 | 122.7493 | 122.7539 | -122.8043 | -122.85 | 122.644 | 0.10071 | 2.5497 | 1.062
2625.1719 | 123.0377 | -56.5292 | 66.2659 | -0.21317 | 0.0021171 | 0.061385 | 0.069259 | 0.00016017 | 0.0030463 | 0.0069172 | 0.050537 | 0.0017431 | -0.0014954 | 0.00091422 | -0.0019333 | -0.0034437 | -0.0018971 | -53.9429 | 66.2201 | -56.5567 | 66.1377 | -55.9479 | -56.3324 | -55.7556 | -55.4031 | 66.2933 | -56.5567 | -56.4011 | -56.4331 | -56.5292 | -56.2683 | -0.027466 | -0.045776 | -0.12817 | 0.58136 | 0.77362 | 0.19684 | 0.80109 | 0.22431 | -0.027466 | 0.027466 | -122.6669 | 0.096131 | 0.26093 | 0 | 0.28839 | 0.027466 | 0.60883 | 122.6944 | 0.1236 | 0.15564 | 122.7768 | 122.85 | 122.7493 | 122.8226 | -122.8226 | -122.8226 | 122.6669 | 0.12817 | 2.5864 | 1.1261
2626.1719 | 123.0515 | -56.4926 | 66.2476 | -0.037689 | -0.00087374 | 0.059462 | 0.067336 | 0.00016017 | 0.0011237 | 0.0069172 | 0.026123 | 0.00024775 | 0.00064083 | 0.0036914 | -0.0030013 | -0.0055799 | -0.0012561 | -53.9383 | 66.2292 | -56.4972 | 66.0233 | -55.9158 | -56.3461 | -55.7831 | -55.4306 | 66.2521 | -56.5613 | -56.3736 | -56.4194 | -56.5338 | -56.2592 | -0.004577 | -0.018311 | -0.22431 | 0.57678 | 0.70953 | 0.14648 | 0.71411 | 0.15106 | -0.068664 | 0.004577 | -122.6212 | 0.073242 | 0.23346 | -0.041198 | 0.30212 | 0.027466 | 0.58136 | 122.5204 | 0.14191 | 0.18768 | 122.7264 | 122.8134 | 122.7219 | 122.7448 | -122.7448 | -122.8088 | 122.5159 | 0.11902 | 2.5543 | 1.062
2627.1719 | 123.0652 | -56.5247 | 66.2384 | -0.03006 | 0.0012625 | 0.060957 | 0.067336 | -0.0056076 | 0.0026191 | 0.0020038 | 0.17566 | 0.0015295 | 0.00064083 | -0.0010084 | -0.0036423 | -0.0049389 | -0.0010425 | -53.9383 | 66.2292 | -56.5292 | 66.1652 | -55.9158 | -56.3187 | -55.7556 | -55.6 | 66.3025 | -56.5704 | -56.3919 | -56.4468 | -56.5292 | -56.2546 | -0.004578 | -0.009155 | -0.073242 | 0.60883 | 0.76904 | 0.20599 | 0.77362 | 0.21057 | -0.045777 | 0.064087 | -122.6303 | 0.07782 | 0.27008 | -0.004578 | 0.31586 | 0.041199 | 0.6134 | 122.6944 | 0.1236 | 0.17853 | 122.7585 | 122.8729 | 122.7539 | 122.8271 | -122.7676 | -122.8088 | 122.6898 | 0.13275 | 2.5864 | 0.92468
2628.1719 | 123.0515 | -56.5247 | 66.2521 | -0.091095 | -0.00087374 | 0.062666 | 0.068832 | -0.004753 | 0.0024053 | 0.0049946 | 0.026123 | 0.0011023 | -0.00064077 | -0.0035718 | -0.0025741 | -0.0051527 | -0.0021107 | -53.9337 | 66.2292 | -56.543 | 66.1469 | -55.9387 | -56.337 | -55.751 | -55.4169 | 66.2842 | -56.5613 | -56.3919 | -56.4377 | -56.5475 | -56.2546 | -0.018311 | -0.022888 | -0.10528 | 0.58594 | 0.77362 | 0.18768 | 0.79193 | 0.20599 | -0.036621 | 0.032044 | -122.644 | 0.086975 | 0.27008 | -0.022888 | 0.3067 | 0.013733 | 0.60425 | 122.6898 | 0.1236 | 0.16937 | 122.7722 | 122.8455 | 122.7539 | 122.8088 | -122.7951 | -122.8134 | 122.6715 | 0.13275 | 2.5909 | 1.1078
2629.1719 | 123.0606 | -56.5247 | 66.2659 | -0.10635 | 0.00083526 | 0.062453 | 0.067763 | 0.00016017 | 0.0024053 | 0.0052082 | 0.032227 | 0.0013159 | 0.00042723 | -0.00015378 | -0.0021469 | -0.0072889 | 0.0017345 | -53.952 | 66.2247 | -56.5338 | 66.1514 | -55.9158 | -56.3141 | -55.7281 | -55.3757 | 66.275 | -56.5475 | -56.3644 | -56.3828 | -56.5063 | -56.2271 | -0.009155 | -0.041199 | -0.11444 | 0.60883 | 0.79651 | 0.21057 | 0.80566 | 0.21973 | -0.022888 | 0.009155 | -122.6303 | 0.14191 | 0.29755 | 0.01831 | 0.32043 | 0.041198 | 0.61798 | 122.6852 | 0.16479 | 0.1831 | 122.7585 | 122.8226 | 122.7493 | 122.7997 | -122.7997 | -122.8134 | 122.6761 | 0.16022 | 2.5726 | 1.149
2630.1719 | 123.0743 | -56.5109 | 66.2521 | -0.10635 | 0.00040806 | 0.061812 | 0.069045 | -0.0038986 | 0.00069649 | 0.0069172 | 0.032227 | 0.00024775 | 0.00064083 | 0.00048702 | -0.0027877 | -0.0055799 | 2.554e-05 | -53.9383 | 66.2567 | -56.543 | 66.1331 | -55.9296 | -56.3232 | -55.7281 | -55.3986 | 66.2613 | -56.5292 | -56.3507 | -56.4148 | -56.4926 | -56.2454 | -0.032044 | 0.004578 | -0.11902 | 0.58136 | 0.78278 | 0.18768 | 0.81482 | 0.21973 | -0.018311 | 0.009156 | -122.6028 | 0.09613 | 0.2655 | 0.01831 | 0.28381 | 0.036621 | 0.6134 | 122.6761 | 0.11444 | 0.17853 | 122.7997 | 122.7905 | 122.7676 | 122.7722 | -122.7951 | -122.7814 | 122.644 | 0.16022 | 2.5726 | 1.1124
2631.1719 | 123.0789 | -56.5338 | 66.275 | -0.075836 | 0.0010489 | 0.059889 | 0.069045 | -0.0015488 | 0.0026191 | 0.0060626 | 0.14514 | 0.00067495 | 0.0025634 | 0.00027342 | -0.0017197 | -0.0057935 | -0.0016833 | -53.9246 | 66.243 | -56.5338 | 66.156 | -55.9113 | -56.3095 | -55.7236 | -55.3894 | 66.3437 | -56.543 | -56.369 | -56.4102 | -56.5292 | -56.2454 | 0 | -0.032043 | -0.11902 | 0.62256 | 0.81024 | 0.2243 | 0.81024 | 0.2243 | -0.009156 | 0.068665 | -122.644 | 0.1236 | 0.28839 | 0.004577 | 0.29755 | 0.013733 | 0.62256 | 122.6898 | 0.13275 | 0.17395 | 122.7768 | 122.8867 | 122.7768 | 122.8775 | -122.8088 | -122.818 | 122.6898 | 0.16479 | 2.6093 | 1.1444
2632.1719 | 123.0789 | -56.5247 | 66.2338 | -0.052948 | -1.9142e-05 | 0.061385 | 0.06755 | 0.003151 | 0.0019781 | 0.0056354 | 0.029175 | -0.00082025 | 0.00085443 | -0.00036738 | -0.0062057 | -0.0077161 | -0.0023243 | -53.9383 | 66.2476 | -56.5247 | 66.1743 | -55.8884 | -56.2866 | -55.7098 | -55.3711 | 66.2796 | -56.5155 | -56.1768 | -56.662 | -56.6711 | -56.2912 | 0 | 0.013733 | -0.05951 | 0.63629 | 0.81482 | 0.23804 | 0.81482 | 0.23804 | 0.009155 | 0.045776 | -122.4106 | -0.13733 | 0.23346 | -0.14648 | 0.2243 | -0.15564 | 0.63629 | 122.699 | -0.14648 | 0.33875 | 122.7722 | 122.7951 | 122.7722 | 122.8043 | -122.7585 | -122.7493 | 122.699 | 0.3479 | 2.5864 | 1.1536
2633.1719 | 123.0698 | -56.4651 | 66.2842 | -0.060578 | 0.0019035 | 0.06053 | 0.068191 | -0.0032578 | 0.0017645 | 0.0045672 | 0.010864 | -0.0014613 | 0.0023498 | 0.0017688 | -0.0021469 | -0.0040845 | -0.0014697 | -53.92 | 66.2613 | -56.5063 | 66.1697 | -55.8975 | -56.2775 | -55.719 | -55.3436 | 66.2796 | -56.5338 | -56.337 | -56.4011 | -56.5018 | -56.2225 | -0.041199 | -0.022888 | -0.11444 | 0.56763 | 0.74615 | 0.18768 | 0.78735 | 0.22888 | -0.068664 | -0.004578 | -122.6212 | 0.064087 | 0.24261 | -0.036621 | 0.31128 | 0.032043 | 0.60883 | 122.6761 | 0.13275 | 0.19684 | 122.7676 | 122.8134 | 122.7264 | 122.7448 | -122.7905 | -122.818 | 122.6349 | 0.12817 | 2.5452 | 1.1215
2634.1719 | 123.0698 | -56.4972 | 66.2842 | -0.068207 | 0.0010489 | 0.060103 | 0.067763 | -0.0043258 | 0.0039007 | 0.0047808 | 0.0047608 | -0.0010339 | 2.8e-08 | -0.0027174 | -0.0038559 | -0.0070753 | -0.0040333 | -53.9429 | 66.2521 | -56.5292 | 66.1697 | -55.9113 | -56.2958 | -55.719 | -55.3757 | 66.275 | -56.5338 | -56.3553 | -56.3828 | -56.4697 | -56.2134 | -0.032044 | -0.032044 | -0.11444 | 0.58594 | 0.7782 | 0.20142 | 0.81024 | 0.23346 | -0.036621 | -0.009156 | -122.6395 | 0.11444 | 0.28381 | 0.027465 | 0.32043 | 0.064086 | 0.61798 | 122.699 | 0.15106 | 0.17853 | 122.7814 | 122.8088 | 122.7493 | 122.7722 | -122.8134 | -122.818 | 122.6669 | 0.14191 | 2.5543 | 1.1215
2635.1719 | 123.0377 | -56.4835 | 66.2842 | -0.060578 | 0.00062166 | 0.061598 | 0.068191 | -0.0011214 | 0.00091009 | 0.0060626 | -0.11731 | 0.00024775 | 0.00021363 | 0.0013416 | -0.0034287 | -0.0036573 | -0.0014697 | -53.9108 | 66.2796 | -56.5201 | 66.1697 | -55.9341 | -55.8563 | -55.5771 | -55.3711 | 66.2659 | -56.543 | -56.3736 | -56.3782 | -56.4926 | -56.2408 | -0.036622 | -0.004578 | -0.11444 | 0.54932 | 0.90637 | 0.62714 | 0.94299 | 0.66376 | -0.05951 | -0.018311 | -122.6578 | 0.10529 | 0.24261 | -0.009156 | 0.30212 | 0.050354 | 0.58594 | 122.6898 | 0.16479 | 0.16937 | 122.7997 | 122.8088 | 122.7631 | 122.7493 | -122.8043 | -122.8271 | 122.6532 | 0.10986 | 2.5726 | 1.1124
2636.1719 | 123.056 | -56.5063 | 66.2933 | -0.083466 | 0.00040806 | 0.060316 | 0.068832 | -0.00048063 | 0.0036871 | 0.0054218 | 0.010864 | 0.0011023 | 0.0036316 | -0.0018628 | -0.0021469 | -0.0072889 | 0.0019483 | -53.952 | 66.2476 | -56.5338 | 66.156 | -55.957 | -56.3187 | -55.7236 | -55.426 | 66.3116 | -56.5475 | -56.3507 | -56.3828 | -56.5063 | -56.2408 | -0.027465 | -0.045776 | -0.13733 | 0.54932 | 0.78278 | 0.18768 | 0.81024 | 0.21515 | -0.041198 | 0.018311 | -122.644 | 0.1236 | 0.2655 | 0 | 0.3067 | 0.041198 | 0.57678 | 122.6898 | 0.16479 | 0.19684 | 122.7814 | 122.8592 | 122.7539 | 122.818 | -122.8271 | -122.8409 | 122.6624 | 0.15564 | 2.5543 | 1.0803
2637.1719 | 123.056 | -56.4743 | 66.2704 | -0.060578 | 0.00062166 | 0.061812 | 0.0699 | -0.0030442 | 0.0019781 | 0.0043536 | 0.016968 | 0.00088875 | 0.0019226 | -0.0084852 | -0.0038559 | -0.0038709 | -0.0033923 | -53.9291 | 66.2659 | -56.5155 | 66.1835 | -55.9021 | -56.2775 | -55.687 | -55.3574 | 66.3071 | -56.5292 | -56.3141 | -56.3828 | -56.488 | -56.2088 | -0.041199 | -0.004578 | -0.086975 | 0.5722 | 0.78735 | 0.19684 | 0.82855 | 0.23804 | -0.054932 | 0.036621 | -122.5845 | 0.091553 | 0.2655 | -0.013733 | 0.32043 | 0.041199 | 0.6134 | 122.699 | 0.14648 | 0.21515 | 122.7814 | 122.8363 | 122.7402 | 122.7814 | -122.786 | -122.7997 | 122.6578 | 0.16022 | 2.5452 | 1.1169
2638.1719 | 122.9553 | -56.5201 | 66.3116 | 0.030975 | -0.00066014 | 0.062025 | 0.070113 | -0.0028304 | 0.0024053 | 0.007558 | -0.06543 | 0.0013159 | 0.0012818 | 0.005614 | -0.0025741 | -0.0028027 | -0.00061526 | -53.9566 | 66.3116 | -56.5384 | 66.0919 | -56.0349 | -56.3828 | -55.806 | -55.4993 | 66.3574 | -56.5521 | -56.4056 | -56.4606 | -56.6025 | -56.2958 | -0.01831 | 0 | -0.21973 | 0.48523 | 0.71411 | 0.13733 | 0.73242 | 0.15564 | -0.032043 | 0.045776 | -122.7173 | 0.05951 | 0.22431 | -0.082397 | 0.25635 | -0.050354 | 0.50354 | 122.6303 | 0.091553 | 0.14648 | 122.85 | 122.9095 | 122.8317 | 122.8775 | -122.85 | -122.8638 | 122.612 | 0.11444 | 2.5635 | 1.0208
2639.1719 | 123.0331 | -56.4743 | 66.2842 | -0.098725 | -0.0010873 | 0.060957 | 0.068404 | -0.0032578 | 0.0013373 | 0.00414 | 0.010864 | 3.4148e-05 | 0.00021363 | -0.0014356 | -0.0012925 | -0.0070753 | -0.00018806 | -53.9383 | 66.2796 | -56.5109 | 66.1423 | -55.925 | -56.3004 | -55.7144 | -55.4031 | 66.2933 | -56.5109 | -56.3324 | -56.369 | -56.4789 | -56.218 | -0.036621 | -0.004578 | -0.14191 | 0.54932 | 0.75989 | 0.17395 | 0.79651 | 0.21057 | -0.036621 | 0.009155 | -122.6166 | 0.10528 | 0.25635 | -0.004578 | 0.29297 | 0.032043 | 0.58594 | 122.6532 | 0.14191 | 0.17853 | 122.7905 | 122.8043 | 122.7539 | 122.7676 | -122.7951 | -122.7951 | 122.6166 | 0.14191 | 2.536 | 1.0712
2640.1719 | 123.0469 | -56.4743 | 66.275 | -0.060578 | -0.0021555 | 0.059889 | 0.068618 | -0.00090783 | 0.0032599 | 0.0052082 | 0.010864 | 0.0011023 | -0.00021357 | -0.0018628 | -0.0015061 | -0.0066479 | -0.0010425 | -53.9566 | 66.275 | -56.5063 | 66.1469 | -55.9525 | -56.3324 | -55.7144 | -55.4352 | 66.3071 | -56.5292 | -56.3324 | -56.3873 | -56.5109 | -56.2225 | -0.032044 | 0 | -0.12817 | 0.52185 | 0.75989 | 0.14191 | 0.79193 | 0.17395 | -0.054932 | 0.032044 | -122.6074 | 0.086975 | 0.25177 | -0.036621 | 0.3067 | 0.018311 | 0.55389 | 122.6532 | 0.14191 | 0.19684 | 122.7814 | 122.8363 | 122.7493 | 122.7814 | -122.7814 | -122.8043 | 122.6212 | 0.14191 | 2.5177 | 1.0391
2641.1719 | 123.0103 | -56.4697 | 66.275 | -0.13687 | 0.00040806 | 0.064162 | 0.070541 | 0.0012284 | 0.00091009 | 0.0077716 | 0.044434 | -0.00039305 | -0.00021357 | 0.0024096 | -0.0015061 | -0.0077161 | 0.00023934 | -53.9749 | 66.275 | -56.5109 | 66.1285 | -55.9845 | -56.337 | -55.7236 | -55.4352 | 66.33 | -56.5201 | -56.3599 | -56.4148 | -56.5018 | -56.2317 | -0.041198 | 0 | -0.14648 | 0.48523 | 0.74616 | 0.13275 | 0.78735 | 0.17395 | -0.050354 | 0.054932 | -122.6349 | 0.054932 | 0.23804 | -0.032043 | 0.28839 | 0.018311 | 0.52643 | 122.6395 | 0.10529 | 0.16022 | 122.7859 | 122.85 | 122.7448 | 122.7997 | -122.7859 | -122.7951 | 122.5983 | 0.10986 | 2.4948 | 1.0345
2642.1719 | 123.0377 | -56.4835 | 66.2979 | -0.10635 | 0.0010489 | 0.062025 | 0.067336 | -0.001976 | 0.0015509 | 0.0045672 | 0.010864 | 0.0023839 | -0.0021362 | 0.00048702 | -0.0032151 | -0.0075025 | -0.0010425 | -53.9429 | 66.2888 | -56.488 | 66.1743 | -55.9433 | -56.3187 | -55.7053 | -55.4031 | 66.3437 | -56.5247 | -56.3187 | -56.3782 | -56.5018 | -56.2042 | -0.004578 | -0.009156 | -0.1236 | 0.54016 | 0.7782 | 0.16479 | 0.78278 | 0.16937 | -0.041199 | 0.045776 | -122.6166 | 0.10529 | 0.27923 | -0.018311 | 0.32043 | 0.022888 | 0.54474 | 122.6624 | 0.14648 | 0.20599 | 122.7768 | 122.8683 | 122.7722 | 122.8271 | -122.7859 | -122.8226 | 122.6578 | 0.16479 | 2.5406 | 1.0803
2643.1719 | 122.9416 | -56.4972 | 66.3666 | -0.060578 | -0.0015145 | 0.06053 | 0.071181 | 0.0012284 | 0.00048269 | 0.0043536 | -0.056274 | 0.0013159 | 0.0012818 | 0.0019824 | -0.0040695 | -0.0057935 | -0.00018806 | -53.952 | 66.3574 | -56.4972 | 66.0873 | -56.0074 | -56.3782 | -55.7831 | -55.5084 | 66.3895 | -56.5292 | -56.4148 | -56.4651 | -56.5018 | -56.1264 | 0 | -0.009155 | -0.27924 | 0.48981 | 0.71411 | 0.11902 | 0.71411 | 0.11902 | -0.032044 | 0.022888 | -122.7814 | 0.032043 | 0.37079 | -0.004578 | 0.40283 | 0.027466 | 0.48981 | 122.5845 | 0.064087 | 0.11444 | 122.8546 | 122.9187 | 122.8546 | 122.8867 | -122.8638 | -122.8958 | 122.5845 | 0.082397 | 2.5452 | 0.98877
2644.1719 | 123.0377 | -56.4835 | 66.2888 | -0.098725 | -0.0013009 | 0.061171 | 0.068618 | 0.00016017 | 0.0041143 | 0.0045672 | 0.001709 | 0.00046135 | 0.0012818 | -0.0042126 | -0.0025741 | -0.0055799 | -0.0010425 | -53.9566 | 66.2888 | -56.4972 | 66.1285 | -55.9525 | -56.3507 | -55.7465 | -55.4443 | 66.3254 | -56.5155 | -56.3553 | -56.4194 | -56.5063 | -56.2271 | -0.013733 | 0 | -0.16022 | 0.53101 | 0.737 | 0.13275 | 0.75073 | 0.14648 | -0.032044 | 0.036621 | -122.644 | 0.064086 | 0.25635 | -0.022889 | 0.28839 | 0.009155 | 0.54474 | 122.6257 | 0.09613 | 0.16022 | 122.7859 | 122.8409 | 122.7722 | 122.8088 | -122.7859 | -122.8043 | 122.612 | 0.12817 | 2.5269 | 1.0391
2645.1719 | 123.0011 | -56.4697 | 66.2842 | 0.32852 | -0.00087374 | 0.061385 | 0.067336 | -5.343e-05 | 0.0034735 | 0.0028582 | 0.0047608 | -0.00017945 | -0.00042717 | 0.0013416 | 0.00084389 | -0.0038709 | 0.00088014 | -54.0344 | 66.2933 | -56.4926 | 66.1102 | -55.9937 | -56.3599 | -55.7373 | -55.4626 | 66.3254 | -56.5201 | -56.369 | -56.4056 | -56.5109 | -56.2363 | -0.022888 | 0.009155 | -0.17395 | 0.47608 | 0.73242 | 0.10986 | 0.75531 | 0.13275 | -0.050354 | 0.041198 | -122.6532 | 0.064087 | 0.23346 | -0.041198 | 0.28381 | 0.009156 | 0.49896 | 122.6028 | 0.11444 | 0.15106 | 122.7859 | 122.8455 | 122.7631 | 122.7951 | -122.7768 | -122.8043 | 122.58 | 0.10071 | 2.4353 | 1.0071
2646.1719 | 123.0148 | -56.4972 | 66.3071 | -0.091095 | -0.0010873 | 0.063521 | 0.068404 | 0.0035782 | 0.0030463 | 0.0043536 | -0.059326 | -0.00017945 | 0.00064083 | -0.0048536 | 0.00063009 | -0.0057935 | -0.00040166 | -53.9612 | 66.2842 | -56.4835 | 66.1194 | -56.0165 | -56.0989 | -55.6732 | -55.4901 | 66.3071 | -56.5155 | -56.3782 | -56.4239 | -56.5521 | -56.2729 | 0.013733 | -0.022888 | -0.18768 | 0.48065 | 0.82397 | 0.39825 | 0.81024 | 0.38452 | -0.018311 | 0 | -122.6852 | 0.073242 | 0.2243 | -0.054932 | 0.24262 | -0.036621 | 0.46692 | 122.6028 | 0.091553 | 0.13733 | 122.7676 | 122.8226 | 122.7814 | 122.8043 | -122.7905 | -122.8226 | 122.6166 | 0.11902 | 2.536 | 1.0071
2647.1719 | 123.0011 | -56.4743 | 66.2796 | -0.098725 | 0.0025443 | 0.062666 | 0.068618 | -5.343e-05 | 0.0021917 | 0.0049946 | -0.019653 | -0.00060665 | 2.8e-08 | -0.00058098 | -0.0021469 | -0.0049389 | -0.0010425 | -53.9658 | 66.2888 | -56.4743 | 66.1377 | -55.9799 | -56.3553 | -55.7419 | -55.4764 | 66.3162 | -56.5018 | -56.2912 | -56.3141 | -56.6071 | -56.2592 | 0 | 0.009155 | -0.14191 | 0.49438 | 0.73242 | 0.11902 | 0.73242 | 0.11902 | -0.027466 | 0.036621 | -122.5708 | 0.16022 | 0.21515 | -0.13275 | 0.24262 | -0.10529 | 0.49438 | 122.612 | 0.18768 | 0.21057 | 122.7631 | 122.818 | 122.7631 | 122.7905 | -122.7539 | -122.7814 | 122.612 | 0.1831 | 2.5085 | 0.99792
2648.1719 | 122.9919 | -56.4743 | 66.3437 | -0.083466 | -0.00066014 | 0.062239 | 0.071395 | 0.0016556 | 0.0028327 | 0.0062762 | -0.077637 | 0.0015295 | 0.001068 | 0.0028368 | -0.0036423 | -0.0021619 | 0.0034435 | -53.9154 | 66.3528 | -56.4651 | 66.1423 | -55.9799 | -56.3232 | -55.7556 | -55.4489 | 66.3849 | -56.4972 | -56.3461 | -56.4468 | -56.5704 | -56.2454 | 0.009155 | 0.009155 | -0.20142 | 0.49438 | 0.71869 | 0.15106 | 0.70953 | 0.14191 | -0.022888 | 0.041199 | -122.6898 | 0.027466 | 0.22888 | -0.096131 | 0.25177 | -0.073243 | 0.48523 | 122.6074 | 0.050354 | 0.15106 | 122.818 | 122.8821 | 122.8271 | 122.8592 | -122.8088 | -122.8409 | 122.6166 | 0.12817 | 2.5589 | 1.0254
2649.1719 | 123.0011 | -56.4926 | 66.2933 | -0.091095 | -0.0015145 | 0.061385 | 0.065627 | 0.003151 | -0.0018671 | 0.0067036 | -0.01355 | 0.00024775 | -0.00042717 | -0.0037854 | -0.0032151 | -0.0028027 | -0.0023243 | -53.9566 | 66.2979 | -56.4651 | 66.1423 | -55.8014 | -56.2637 | -55.7922 | -55.4718 | 66.3116 | -56.5292 | -56.3782 | -56.4148 | -56.5338 | -56.2363 | 0.027466 | 0.004578 | -0.15106 | 0.69122 | 0.70038 | 0.22888 | 0.67291 | 0.20142 | -0.036621 | 0.018311 | -122.6715 | 0.07782 | 0.25635 | -0.041198 | 0.29297 | -0.004577 | 0.66376 | 122.6074 | 0.11444 | 0.15106 | 122.7631 | 122.8409 | 122.7905 | 122.8043 | -122.7585 | -122.8226 | 122.6349 | 0.11444 | 2.536 | 1.0208
2650.1719 | 123.0011 | -56.488 | 66.3025 | -0.15213 | 0.0019035 | 0.063307 | 0.069259 | 0.001442 | 0.0024053 | 0.0032856 | -0.01355 | 0.00046135 | 0.0021362 | -0.003999 | -0.0027877 | -0.0060071 | -0.0031787 | -53.9429 | 66.2704 | -56.488 | 66.1423 | -55.9341 | -56.3599 | -55.7098 | -55.4169 | 66.3162 | -56.5201 | -56.3553 | -56.4331 | -56.5338 | -56.2271 | 0 | -0.032043 | -0.16022 | 0.55389 | 0.7782 | 0.12817 | 0.7782 | 0.12817 | -0.032044 | 0.013733 | -122.6578 | 0.054932 | 0.26093 | -0.045776 | 0.29297 | -0.013732 | 0.55389 | 122.6303 | 0.086976 | 0.16479 | 122.7585 | 122.8363 | 122.7585 | 122.8043 | -122.7905 | -122.8226 | 122.6303 | 0.13275 | 2.5452 | 1.0712
2651.1719 | 123.0057 | -56.4697 | 66.3254 | -0.11398 | -0.00087374 | 0.062025 | 0.06755 | 0.0022964 | 0.0011237 | 0.0052082 | -0.0074462 | 0.00024775 | -0.00021357 | -0.0010084 | -0.0017197 | -0.0034437 | -0.0038197 | -53.9703 | 66.3162 | -56.4423 | 66.1469 | -55.9525 | -56.3461 | -55.7236 | -55.4535 | 66.3574 | -56.4972 | -56.3553 | -56.4148 | -56.5247 | -56.2363 | 0.027466 | -0.009155 | -0.17853 | 0.51727 | 0.74616 | 0.1236 | 0.71869 | 0.096131 | -0.027465 | 0.032044 | -122.6807 | 0.054932 | 0.23346 | -0.054931 | 0.26093 | -0.027466 | 0.48981 | 122.5891 | 0.082397 | 0.14191 | 122.7585 | 122.8546 | 122.7859 | 122.8271 | -122.7676 | -122.8226 | 122.6166 | 0.11444 | 2.4994 | 1.0162
2652.1719 | 123.0103 | -56.4697 | 66.2888 | -0.13687 | 0.00083526 | 0.063094 | 0.068191 | -0.00048063 | 0.0034735 | 0.0043536 | 0.0047608 | -0.00082025 | -0.00042717 | -0.001222 | -0.0021469 | -0.0049389 | -0.0010425 | -53.952 | 66.3254 | -56.456 | 66.1469 | -55.9616 | -56.3416 | -55.7281 | -55.4352 | 66.3345 | -56.5155 | -56.3461 | -56.4239 | -56.5201 | -56.2317 | 0.013733 | 0.036621 | -0.14191 | 0.50812 | 0.74158 | 0.12817 | 0.72784 | 0.11444 | -0.045776 | 0.045777 | -122.6349 | 0.045777 | 0.23804 | -0.050354 | 0.28381 | -0.004578 | 0.49438 | 122.6028 | 0.091553 | 0.16937 | 122.7814 | 122.85 | 122.7951 | 122.8043 | -122.7448 | -122.8043 | 122.6166 | 0.1236 | 2.5177 | 1.0345
2653.1719 | 123.0103 | -56.4606 | 66.33 | -0.075836 | -0.00023294 | 0.061171 | 0.069472 | 0.0020828 | -0.00058531 | 0.007558 | -0.010498 | 0.0013159 | 0.0025634 | 0.0041186 | -0.0012925 | -0.0051527 | -0.0010425 | -53.9474 | 66.3162 | -56.4423 | 66.1469 | -55.9479 | -56.3278 | -55.6961 | -55.3024 | 66.3666 | -56.4972 | -56.337 | -56.3873 | -56.5384 | -56.2546 | 0.01831 | -0.013733 | -0.1831 | 0.5127 | 0.76447 | 0.13275 | 0.74616 | 0.11444 | -0.036621 | 0.036621 | -122.6669 | 0.073242 | 0.20599 | -0.07782 | 0.24261 | -0.041199 | 0.49439 | 122.5891 | 0.10986 | 0.16022 | 122.7585 | 122.8638 | 122.7768 | 122.8271 | -122.7722 | -122.8271 | 122.6074 | 0.1236 | 2.5131 | 1.1581
2654.1719 | 123.0148 | -56.4377 | 66.2888 | -0.037689 | 0.00083526 | 0.06288 | 0.071181 | -5.343e-05 | 0.0017645 | 0.0054218 | -0.044067 | 0.00067495 | 2.8e-08 | -0.0059216 | -0.0015061 | -0.0042981 | -0.0025379 | -53.8742 | 66.2521 | -56.5018 | 66.1972 | -55.8792 | -56.3187 | -55.7098 | -55.3665 | 66.3116 | -56.4926 | -56.2866 | -56.3873 | -56.4972 | -56.1951 | -0.064087 | -0.036621 | -0.091552 | 0.55847 | 0.72784 | 0.11902 | 0.79193 | 0.1831 | -0.054932 | 0.022889 | -122.5754 | 0.050354 | 0.24262 | -0.059509 | 0.29755 | -0.004577 | 0.62256 | 122.699 | 0.10529 | 0.20599 | 122.7539 | 122.8043 | 122.6898 | 122.7493 | -122.7905 | -122.7814 | 122.6349 | 0.15106 | 2.5635 | 1.0712
2655.1719 | 123.0148 | -56.4514 | 66.3071 | -0.17502 | 0.00062166 | 0.060957 | 0.068618 | -0.001976 | 0.0026191 | 0.0045672 | -0.0074462 | 0.0017431 | -0.00042717 | 0.0034778 | -0.0019333 | -0.0051527 | 0.0019483 | -53.9246 | 66.2979 | -56.4743 | 66.188 | -55.8929 | -56.3095 | -55.687 | -55.3619 | 66.3208 | -56.4926 | -56.3141 | -56.3965 | -56.5155 | -56.1951 | -0.022888 | -0.009155 | -0.11902 | 0.55847 | 0.76447 | 0.14191 | 0.78735 | 0.16479 | -0.041199 | 0.013733 | -122.6212 | 0.054932 | 0.25635 | -0.064087 | 0.29755 | -0.022888 | 0.58136 | 122.6624 | 0.096131 | 0.17853 | 122.7722 | 122.8134 | 122.7493 | 122.7722 | -122.7814 | -122.7997 | 122.6395 | 0.13733 | 2.5269 | 1.0895
2656.1719 | 122.9828 | -56.456 | 66.3345 | -0.022431 | 0.00062166 | 0.060957 | 0.06755 | 0.00037377 | 0.0017645 | 0.0039264 | -0.025757 | 0.0013159 | -0.00021357 | 0.001128 | -0.00086511 | -0.0049389 | -0.00082886 | -53.9246 | 66.2888 | -56.4835 | 66.1514 | -55.925 | -56.3278 | -55.687 | -55.4123 | 66.3574 | -56.488 | -56.337 | -56.4148 | -56.5063 | -56.2134 | -0.027465 | -0.045777 | -0.18311 | 0.53101 | 0.76904 | 0.12817 | 0.79651 | 0.15564 | -0.032043 | 0.022888 | -122.6715 | 0.041199 | 0.24261 | -0.050354 | 0.27466 | -0.018311 | 0.55847 | 122.6349 | 0.073242 | 0.15106 | 122.7722 | 122.8455 | 122.7448 | 122.8134 | -122.818 | -122.8226 | 122.6074 | 0.11902 | 2.5314 | 1.0437
2657.1719 | 123.0194 | -56.4468 | 66.3025 | -0.045319 | -0.0023691 | 0.062453 | 0.069686 | 0.0037918 | 0.0043281 | 0.007558 | -0.037964 | 0.00067495 | -0.00064077 | -0.00015378 | -0.0030013 | -0.0049389 | 0.00066654 | -53.9017 | 66.3025 | -56.4468 | 66.2018 | -55.8929 | -56.3049 | -55.687 | -55.3665 | 66.3208 | -56.4743 | -56.2729 | -56.3782 | -56.5018 | -56.1813 | 0 | 0 | -0.10071 | 0.55389 | 0.75989 | 0.14191 | 0.75989 | 0.14191 | -0.027466 | 0.018311 | -122.5754 | 0.068664 | 0.2655 | -0.054932 | 0.29297 | -0.027466 | 0.55389 | 122.6486 | 0.09613 | 0.20142 | 122.7493 | 122.7951 | 122.7493 | 122.7676 | -122.7493 | -122.7768 | 122.6486 | 0.17395 | 2.5452 | 1.0803
2658.1719 | 122.9919 | -56.4377 | 66.3254 | -0.1445 | -0.00087374 | 0.060744 | 0.071181 | -5.343e-05 | 0.0030463 | 0.005849 | -0.010498 | 0.00067495 | 0.00085443 | 0.0019824 | -0.0017197 | -0.0049389 | 0.0021619 | -53.9474 | 66.3071 | -56.4835 | 66.1652 | -55.925 | -56.3049 | -55.6961 | -55.4398 | 66.3528 | -56.4697 | -56.3461 | -56.3828 | -56.4972 | -56.2042 | -0.045776 | -0.01831 | -0.16022 | 0.5127 | 0.74158 | 0.13275 | 0.78735 | 0.17853 | -0.032044 | 0.027466 | -122.6715 | 0.054932 | 0.23346 | -0.059509 | 0.2655 | -0.027465 | 0.55847 | 122.6486 | 0.086976 | 0.1236 | 122.7905 | 122.8226 | 122.7448 | 122.7905 | -122.8088 | -122.7951 | 122.6028 | 0.091553 | 2.4902 | 0.99793
2659.1719 | 123.0103 | -56.4331 | 66.3345 | -0.083466 | -0.00066014 | 0.061598 | 0.070541 | 0.0016556 | 0.0026191 | 0.007558 | -0.047119 | 0.0021703 | 2.8e-08 | -0.00036738 | -0.0021469 | -0.0047253 | 0.0047253 | -53.9154 | 66.2888 | -56.4789 | 66.2018 | -55.8884 | -56.2866 | -55.6778 | -55.3665 | 66.3483 | -56.4789 | -56.3049 | -56.3873 | -56.4926 | -56.1905 | -0.045777 | -0.045777 | -0.13275 | 0.54474 | 0.75531 | 0.14648 | 0.80109 | 0.19226 | -0.045777 | 0.013733 | -122.6395 | 0.045776 | 0.24261 | -0.05951 | 0.28839 | -0.013733 | 0.59051 | 122.6807 | 0.091553 | 0.17395 | 122.7676 | 122.8271 | 122.7219 | 122.7814 | -122.8134 | -122.8134 | 122.6349 | 0.12817 | 2.5177 | 1.0666
2660.1719 | 123.0103 | -56.4423 | 66.3208 | -0.18265 | 0.0033987 | 0.062239 | 0.069472 | 0.0029374 | 0.0039007 | 0.0052082 | -0.047119 | 0.00024775 | -0.00042717 | 0.0030506 | -0.0044967 | -0.0023755 | -0.00082886 | -53.9108 | 66.3162 | -56.456 | 66.2109 | -55.8701 | -56.2866 | -55.6641 | -55.3619 | 66.3391 | -56.4606 | -56.282 | -56.3736 | -56.4743 | -56.1768 | -0.013733 | -0.004578 | -0.10986 | 0.57221 | 0.7782 | 0.15564 | 0.79193 | 0.16937 | -0.01831 | 0.01831 | -122.6028 | 0.068665 | 0.2655 | -0.032043 | 0.28381 | -0.013733 | 0.58594 | 122.6669 | 0.086975 | 0.17853 | 122.7722 | 122.7997 | 122.7585 | 122.7814 | -122.7768 | -122.7814 | 122.6532 | 0.16022 | 2.5314 | 1.0803
2661.1719 | 123.0148 | -56.4468 | 66.3116 | -0.12924 | 0.00019446 | 0.059035 | 0.068832 | -0.00026703 | 0.00069649 | 0.0034992 | 0.0047608 | 0.00024775 | 0.00085443 | -0.00058098 | -0.0030013 | -0.0021619 | -0.0031787 | -53.8742 | 66.3162 | -56.4697 | 66.2064 | -55.8746 | -56.2866 | -55.6641 | -55.3482 | 66.3574 | -56.4743 | -56.2592 | -56.3553 | -56.4606 | -56.1539 | -0.022889 | 0.004577 | -0.10529 | 0.5722 | 0.78278 | 0.16022 | 0.80566 | 0.18311 | -0.027466 | 0.045776 | -122.5708 | 0.091552 | 0.29297 | -0.013733 | 0.32043 | 0.013733 | 0.59509 | 122.6761 | 0.11902 | 0.21515 | 122.7859 | 122.8317 | 122.7631 | 122.8043 | -122.7814 | -122.7859 | 122.6532 | 0.18768 | 2.5726 | 1.0986
2662.1719 | 123.024 | -56.4102 | 66.3345 | -0.1445 | -0.00023294 | 0.064589 | 0.069259 | -0.00026703 | 0.0021917 | 0.007558 | -0.037964 | 0.0023839 | 0.00021363 | 0.0017688 | -0.00065151 | -0.0060071 | 0.00088014 | -54.0436 | 66.2659 | -56.4606 | 66.2521 | -55.8517 | -56.2546 | -55.6595 | -55.3436 | 66.3528 | -56.4651 | -56.2592 | -56.3553 | -56.4651 | -56.1676 | -0.050354 | -0.068665 | -0.082398 | 0.55847 | 0.75073 | 0.15564 | 0.80109 | 0.20599 | -0.054932 | 0.01831 | -122.5937 | 0.054931 | 0.24261 | -0.054932 | 0.29755 | 0 | 0.60883 | 122.7127 | 0.10986 | 0.20599 | 122.7264 | 122.818 | 122.6761 | 122.7631 | -122.7951 | -122.7997 | 122.6624 | 0.15106 | 2.3666 | 1.0666
2663.1719 | 123.0011 | -56.4011 | 66.3803 | -0.098725 | 0.0010489 | 0.063307 | 0.0699 | -0.0030442 | 0.0039007 | 0.00414 | 0.0078126 | -0.00060665 | 0.00042723 | -0.00079478 | -0.0019333 | -0.0053663 | 0.0025891 | -53.8559 | 66.3483 | -56.4148 | 66.2613 | -55.8151 | -56.2042 | -55.6046 | -55.3207 | 66.394 | -56.4102 | -56.2637 | -56.3095 | -56.4194 | -56.131 | -0.013733 | -0.032043 | -0.11902 | 0.58594 | 0.79651 | 0.19684 | 0.81024 | 0.21057 | -0.009155 | 0.013733 | -122.644 | 0.091553 | 0.27008 | -0.018311 | 0.27924 | -0.009156 | 0.59967 | 122.6761 | 0.10071 | 0.14648 | 122.7631 | 122.8043 | 122.7493 | 122.7951 | -122.7951 | -122.7905 | 122.6624 | 0.13733 | 2.5452 | 1.0803
2664.1719 | 123.056 | -56.4331 | 66.3391 | -0.15976 | -0.00023294 | 0.063094 | 0.069045 | -0.0026168 | 0.0013373 | 0.0062762 | 0.023071 | -0.00082025 | -0.00064077 | -0.00058098 | -0.0019333 | -0.0017347 | -0.0010425 | -53.8879 | 66.2979 | -56.4514 | 66.2292 | -55.838 | -56.5338 | -55.7053 | -55.3619 | 66.394 | -56.4468 | -56.2637 | -56.3736 | -56.4514 | -56.1584 | -0.018311 | -0.041198 | -0.10986 | 0.59509 | 0.72784 | -0.10071 | 0.74616 | -0.082397 | -0.013733 | 0.054932 | -122.6028 | 0.059509 | 0.27466 | -0.018311 | 0.28839 | -0.004578 | 0.6134 | 122.6807 | 0.073242 | 0.1831 | 122.7493 | 122.8409 | 122.731 | 122.8271 | -122.7905 | -122.7859 | 122.6624 | 0.16937 | 2.5452 | 1.0712
2665.1719 | 123.0011 | -56.4377 | 66.3574 | -0.10635 | -0.00023294 | 0.063094 | 0.0699 | 0.0020828 | 0.0028327 | 0.005849 | -0.016602 | 0.0023839 | -0.00085457 | -0.00015378 | -0.0021469 | -0.0038709 | -0.0036059 | -53.8879 | 66.3437 | -56.4239 | 66.2201 | -55.8701 | -56.2729 | -55.6458 | -55.3345 | 66.3803 | -56.456 | -56.2683 | -56.3507 | -56.4789 | -56.1493 | 0.013733 | -0.013733 | -0.13733 | 0.56763 | 0.79193 | 0.16479 | 0.7782 | 0.15106 | -0.018311 | 0.022888 | -122.6257 | 0.086975 | 0.28839 | -0.041199 | 0.3067 | -0.022888 | 0.55389 | 122.644 | 0.10529 | 0.18768 | 122.7676 | 122.8363 | 122.7814 | 122.818 | -122.7814 | -122.8134 | 122.6578 | 0.16937 | 2.5497 | 1.1032
2666.1719 | 123.0057 | -56.4102 | 66.3254 | -0.15213 | 0.0012625 | 0.060957 | 0.069686 | 0.00037377 | 0.0015509 | 0.0067036 | -0.016602 | 3.4148e-05 | -0.00021357 | 5.9824e-05 | -0.0015061 | -0.0045117 | -0.0033923 | -53.8651 | 66.3254 | -56.4239 | 66.2155 | -55.8517 | -56.2592 | -55.6366 | -55.3345 | 66.3666 | -56.4468 | -56.2683 | -56.3644 | -56.4651 | -56.1584 | -0.013733 | 0 | -0.10986 | 0.55847 | 0.77362 | 0.15106 | 0.78735 | 0.16479 | -0.036621 | 0.041199 | -122.5937 | 0.045776 | 0.25177 | -0.054932 | 0.28839 | -0.018311 | 0.5722 | 122.6395 | 0.082397 | 0.17853 | 122.7493 | 122.8134 | 122.7356 | 122.7768 | -122.7493 | -122.7722 | 122.6257 | 0.14191 | 2.5452 | 1.0757
2667.1719 | 123.0011 | -56.4056 | 66.3712 | -0.1445 | 0.00083526 | 0.062239 | 0.070113 | 0.0016556 | 0.0028327 | 0.0045672 | -0.0013428 | 0.00024775 | 0.00042723 | -0.0010084 | -0.0015061 | -0.0030163 | -0.00082886 | -53.8925 | 66.3254 | -56.4239 | 66.2292 | -55.8517 | -56.2729 | -55.6183 | -55.3299 | 66.3712 | -56.4606 | -56.25 | -56.3599 | -56.456 | -56.1539 | -0.01831 | -0.045777 | -0.14191 | 0.55389 | 0.78735 | 0.13275 | 0.80566 | 0.15106 | -0.054931 | 0 | -122.6212 | 0.045777 | 0.25177 | -0.050354 | 0.3067 | 0.004577 | 0.5722 | 122.6532 | 0.10071 | 0.21057 | 122.7493 | 122.8317 | 122.731 | 122.7768 | -122.7951 | -122.8317 | 122.6349 | 0.15564 | 2.5131 | 1.0757
2668.1719 | 122.9645 | -56.3919 | 66.4032 | -0.068207 | -0.0015145 | 0.060744 | 0.0699 | -0.0015488 | 0.0039007 | 0.0047808 | -0.068481 | -0.00039305 | 0.00085443 | 0.0026232 | -0.0012925 | -0.0021619 | -0.00061526 | -53.8788 | 66.4307 | -56.4194 | 66.1789 | -55.9296 | -56.2592 | -55.7007 | -55.4077 | 66.4764 | -56.4514 | -56.282 | -56.3599 | -56.4743 | -56.163 | -0.027466 | 0.027466 | -0.2243 | 0.46234 | 0.69122 | 0.13275 | 0.71869 | 0.16022 | -0.059509 | 0.073242 | -122.6852 | 0.032044 | 0.22888 | -0.082397 | 0.28839 | -0.022888 | 0.48981 | 122.5983 | 0.091553 | 0.16937 | 122.85 | 122.9279 | 122.8226 | 122.8683 | -122.8226 | -122.8546 | 122.5708 | 0.10986 | 2.5131 | 0.98419
2669.1719 | 123.0148 | -56.4148 | 66.3437 | -0.17502 | -0.0013009 | 0.062453 | 0.069259 | 0.001442 | 0.0030463 | 0.003072 | -0.0074462 | -0.00017945 | 0.00042723 | 0.0071094 | -0.0019333 | -0.0021619 | 0.00045294 | -53.8696 | 66.3391 | -56.3919 | 66.2292 | -55.838 | -56.2363 | -55.6137 | -55.3345 | 66.3986 | -56.4377 | -56.2317 | -56.337 | -56.4423 | -56.1356 | 0.022888 | -0.004578 | -0.11444 | 0.57678 | 0.80109 | 0.17853 | 0.7782 | 0.15564 | -0.022888 | 0.054932 | -122.5754 | 0.07782 | 0.27924 | -0.027466 | 0.30212 | -0.004578 | 0.55389 | 122.6212 | 0.10071 | 0.20599 | 122.731 | 122.8363 | 122.7539 | 122.8134 | -122.7356 | -122.7814 | 122.644 | 0.18311 | 2.5452 | 1.0803
2670.1719 | 123.0515 | -56.3873 | 66.3483 | -0.022431 | -0.00066014 | 0.063948 | 0.068191 | 0.00037377 | 0.0028327 | 0.003072 | -0.034912 | -0.00060665 | 0.0019226 | -0.00079478 | -0.00043791 | -0.0036573 | 0.0021619 | -53.8788 | 66.3666 | -56.4011 | 66.243 | -55.8563 | -56.2546 | -55.632 | -55.3253 | 66.3757 | -56.4514 | -56.25 | -56.3187 | -56.4239 | -56.131 | -0.013733 | 0.01831 | -0.10529 | 0.53101 | 0.75531 | 0.13275 | 0.76904 | 0.14648 | -0.064087 | 0.027465 | -122.5983 | 0.068664 | 0.25635 | -0.036621 | 0.32044 | 0.027466 | 0.54474 | 122.644 | 0.13275 | 0.20142 | 122.7676 | 122.8271 | 122.7539 | 122.7631 | -122.7493 | -122.7997 | 122.6303 | 0.13733 | 2.5085 | 1.062
2671.1719 | 123.0103 | -56.4056 | 66.3483 | -0.11398 | 0.0021171 | 0.065016 | 0.069259 | -0.001976 | 0.0011237 | 0.0054218 | -0.01355 | 0.00024775 | 0.00042723 | -0.003999 | -0.0010787 | -0.0055799 | -0.00082886 | -53.8284 | 66.3162 | -56.4056 | 66.2476 | -55.8197 | -56.2454 | -55.6183 | -55.3024 | 66.3757 | -56.4331 | -56.218 | -56.3278 | -56.4331 | -56.1172 | 0 | -0.032044 | -0.10071 | 0.58594 | 0.78735 | 0.16022 | 0.78735 | 0.16022 | -0.027465 | 0.027465 | -122.5662 | 0.07782 | 0.28839 | -0.027465 | 0.31586 | 0 | 0.58594 | 122.6532 | 0.10528 | 0.21515 | 122.7219 | 122.8088 | 122.7219 | 122.7814 | -122.7539 | -122.7814 | 122.6532 | 0.18768 | 2.5772 | 1.1032
2672.1719 | 122.9965 | -56.3873 | 66.394 | -0.098725 | -0.00023294 | 0.061385 | 0.068191 | -0.0026168 | 0.0021917 | 0.0037128 | 0.016968 | 0.0015295 | -0.0021362 | -0.0014356 | -0.00065151 | -0.0036573 | -0.0025379 | -53.9062 | 66.394 | -56.4148 | 66.2018 | -55.8838 | -56.2454 | -55.6366 | -55.3848 | 66.4124 | -56.4331 | -56.2637 | -56.3461 | -56.4651 | -56.1539 | -0.027466 | 0 | -0.19226 | 0.50354 | 0.75073 | 0.14191 | 0.7782 | 0.16937 | -0.045776 | 0.018311 | -122.6578 | 0.041199 | 0.23346 | -0.07782 | 0.27923 | -0.032044 | 0.53101 | 122.6166 | 0.086975 | 0.16937 | 122.8088 | 122.8455 | 122.7814 | 122.7997 | -122.8088 | -122.8271 | 122.5891 | 0.1236 | 2.4811 | 1.0025
2673.1875 | 122.9965 | -56.4285 | 66.3757 | -0.10635 | 0.00019446 | 0.061385 | 0.070327 | -0.00090783 | 0.0017645 | 0.0060626 | -0.06543 | 0.0015295 | 0.00021363 | 0.005614 | -0.0021469 | -0.0051527 | -0.0042469 | -53.92 | 66.3849 | -56.4514 | 66.156 | -55.9616 | -56.337 | -55.7053 | -55.4031 | 66.3986 | -56.4514 | -56.282 | -56.3782 | -56.5063 | -56.1722 | -0.022888 | 0.009156 | -0.21973 | 0.46692 | 0.72327 | 0.091553 | 0.74616 | 0.11444 | -0.022888 | 0.022889 | -122.6578 | 0.050354 | 0.25635 | -0.07782 | 0.27924 | -0.054932 | 0.48981 | 122.6074 | 0.073242 | 0.16937 | 122.8363 | 122.85 | 122.8134 | 122.8271 | -122.8271 | -122.8271 | 122.5845 | 0.14648 | 2.5085 | 1.0254
2674.1719 | 123.0286 | -56.3736 | 66.3666 | -0.11398 | 0.00083526 | 0.063307 | 0.068404 | -0.0013352 | 0.0026191 | 0.0047808 | -0.019653 | 0.0011023 | -0.00085457 | -0.007417 | -0.0021469 | -0.0042981 | -0.0016833 | -53.8788 | 66.3345 | -56.4056 | 66.2384 | -55.8105 | -56.2363 | -55.6183 | -55.3207 | 66.4307 | -56.4239 | -56.2546 | -56.3507 | -56.4423 | -56.131 | -0.032044 | -0.032043 | -0.12817 | 0.56305 | 0.75531 | 0.13733 | 0.78735 | 0.16937 | -0.050354 | 0.064087 | -122.6212 | 0.022888 | 0.24262 | -0.068665 | 0.29297 | -0.018311 | 0.59509 | 122.644 | 0.073242 | 0.16937 | 122.7402 | 122.8546 | 122.7081 | 122.8043 | -122.7722 | -122.7905 | 122.612 | 0.11902 | 2.4948 | 1.0529
2675.1719 | 123.0194 | -56.3736 | 66.362 | -0.13687 | 0.0010489 | 0.062453 | 0.070968 | -0.0017624 | 0.0030463 | 0.0067036 | -0.01355 | 0.0025975 | 0.003418 | 0.00027342 | -0.0012925 | -0.0034437 | 0.0025891 | -53.8742 | 66.3803 | -56.3828 | 66.2476 | -55.806 | -56.2088 | -55.6183 | -55.3162 | 66.4078 | -56.4148 | -56.25 | -56.3278 | -56.4331 | -56.1264 | -0.009155 | 0.01831 | -0.11444 | 0.56763 | 0.75531 | 0.16479 | 0.76447 | 0.17395 | -0.041199 | 0.045776 | -122.612 | 0.045776 | 0.24719 | -0.059509 | 0.28839 | -0.01831 | 0.57678 | 122.6303 | 0.086975 | 0.16479 | 122.7631 | 122.8226 | 122.7539 | 122.7814 | -122.7448 | -122.7768 | 122.6212 | 0.1236 | 2.4994 | 1.0574
2676.1719 | 122.9965 | -56.3965 | 66.394 | -0.10635 | 0.00062166 | 0.062239 | 0.068618 | -0.0015488 | 0.00069649 | 0.0060626 | -0.0074462 | 0.00088875 | 0.0012818 | -0.0054944 | -0.0023605 | -0.0040845 | -0.00040166 | -53.8834 | 66.3986 | -56.4148 | 66.2201 | -55.8609 | -56.2546 | -55.6183 | -55.3802 | 66.4169 | -56.4239 | -56.2454 | -56.3141 | -56.4377 | -56.1401 | -0.018311 | 0.004578 | -0.17395 | 0.53558 | 0.7782 | 0.14191 | 0.79651 | 0.16022 | -0.027466 | 0.022888 | -122.6395 | 0.082397 | 0.25635 | -0.041199 | 0.28381 | -0.013733 | 0.55389 | 122.6349 | 0.10986 | 0.17853 | 122.8134 | 122.8409 | 122.7951 | 122.8134 | -122.8088 | -122.818 | 122.6166 | 0.15106 | 2.5131 | 1.0162
2677.1719 | 122.9965 | -56.3416 | 66.394 | -0.13687 | 0.0010489 | 0.060744 | 0.069472 | -0.0017624 | 0.00048269 | 0.0052082 | -0.01355 | 0.0017431 | -0.0012818 | -0.0018628 | -0.0023605 | -0.0045117 | 0.00023934 | -53.8605 | 66.3849 | -56.3828 | 66.2613 | -55.8105 | -56.2271 | -55.5908 | -55.2933 | 66.4124 | -56.4148 | -56.2225 | -56.3187 | -56.4239 | -56.0989 | -0.041198 | -0.009155 | -0.13275 | 0.53101 | 0.75073 | 0.11444 | 0.79193 | 0.15564 | -0.073242 | 0.018311 | -122.6166 | 0.022888 | 0.24262 | -0.082397 | 0.31586 | -0.009155 | 0.5722 | 122.644 | 0.09613 | 0.19226 | 122.7676 | 122.8271 | 122.7264 | 122.7539 | -122.7768 | -122.8088 | 122.6028 | 0.11902 | 2.4811 | 1.0483
2678.1875 | 123.0469 | -56.3461 | 66.4307 | -0.12924 | 0.00062166 | 0.06288 | 0.069472 | 0.00037377 | 0.0019781 | 0.0056354 | 0.035278 | -0.00082025 | -0.0014954 | 0.00091422 | -0.0023605 | -0.0034437 | -0.0033923 | -53.8879 | 66.3849 | -56.3736 | 66.243 | -55.8609 | -56.2271 | -55.6 | -55.3528 | 66.4444 | -56.3965 | -56.2363 | -56.2866 | -56.4148 | -56.1081 | -0.027466 | -0.045776 | -0.18768 | 0.48523 | 0.74615 | 0.11902 | 0.77362 | 0.14648 | -0.050354 | 0.013733 | -122.6669 | 0.059509 | 0.23804 | -0.068665 | 0.28839 | -0.018311 | 0.5127 | 122.6166 | 0.10986 | 0.16022 | 122.7585 | 122.8409 | 122.731 | 122.7905 | -122.8043 | -122.8271 | 122.5891 | 0.10986 | 2.4582 | 0.99335
2679.1719 | 123.0698 | -56.3461 | 66.4398 | -0.11398 | -0.00066014 | 0.060957 | 0.068618 | -0.00090783 | 5.5488e-05 | 0.0034992 | 0.0047608 | 0.0015295 | 0.00064083 | -0.0035718 | -0.0034287 | -0.0053663 | 2.554e-05 | -53.8467 | 66.3895 | -56.3644 | 66.275 | -55.8243 | -56.1996 | -55.5817 | -55.3024 | 66.4444 | -56.3782 | -56.1996 | -56.2637 | -56.3736 | -56.0989 | -0.018311 | -0.050354 | -0.16479 | 0.52185 | 0.76447 | 0.14648 | 0.78278 | 0.16479 | -0.032044 | 0.004578 | -122.6395 | 0.082397 | 0.24719 | -0.027466 | 0.27924 | 0.004578 | 0.54016 | 122.6395 | 0.11444 | 0.17853 | 122.7539 | 122.8226 | 122.7356 | 122.7905 | -122.8043 | -122.818 | 122.6212 | 0.14648 | 2.4994 | 1.0437
2680.1719 | 123.056 | -56.3416 | 66.4398 | -0.091095 | -0.0017281 | 0.062666 | 0.069472 | 0.00058737 | 0.0026191 | 0.0045672 | 0.016968 | -0.0012477 | -0.0014954 | 0.0086048 | -0.0027877 | -0.0049389 | -0.0025379 | -53.8605 | 66.4124 | -56.3736 | 66.2796 | -55.8243 | -56.1951 | -55.5771 | -55.2933 | 66.481 | -56.3919 | -56.2042 | -56.2775 | -56.3782 | -56.0944 | -0.032043 | -0.027465 | -0.16022 | 0.51727 | 0.76447 | 0.14648 | 0.79651 | 0.17853 | -0.050354 | 0.041199 | -122.644 | 0.064087 | 0.24719 | -0.036621 | 0.29755 | 0.013733 | 0.54932 | 122.6532 | 0.11444 | 0.18768 | 122.7859 | 122.8729 | 122.7539 | 122.8226 | -122.8134 | -122.8317 | 122.6212 | 0.13733 | 2.4811 | 1.0483
2681.1719 | 123.0515 | -56.3278 | 66.4764 | -0.052948 | -0.0013009 | 0.056898 | 0.067977 | -0.0028304 | 0.0021917 | 0.0060626 | -0.0074462 | -0.00039305 | 0.00021363 | 0.001128 | -0.0021469 | -0.0040845 | -0.0048877 | -53.5629 | 66.4902 | -56.2912 | 66.3208 | -55.7602 | -56.1264 | -55.545 | -55.2109 | 66.4627 | -56.369 | -56.1859 | -56.2363 | -56.3461 | -56.0715 | 0.036621 | 0.013733 | -0.15564 | 0.56763 | 0.78278 | 0.20142 | 0.74616 | 0.16479 | -0.041199 | -0.013732 | -122.6624 | 0.091553 | 0.25635 | -0.01831 | 0.29755 | 0.022889 | 0.53101 | 122.612 | 0.13275 | 0.18311 | 122.7814 | 122.8317 | 122.818 | 122.7905 | -122.7676 | -122.8455 | 122.6486 | 0.14191 | 2.7649 | 1.1169
2682.1719 | 123.0698 | -56.3278 | 66.4536 | -0.083466 | 0.0023307 | 0.061598 | 0.069686 | 0.0012284 | -0.00037171 | 0.0034992 | 0.010864 | 0.0023839 | -0.0012818 | -0.00464 | -0.0025741 | -0.0060071 | -0.00018806 | -53.8101 | 66.4261 | -56.3507 | 66.33 | -55.7648 | -56.1356 | -55.5222 | -55.2063 | 66.4719 | -56.3599 | -56.1584 | -56.2088 | -56.3278 | -56.0349 | -0.022888 | -0.027466 | -0.1236 | 0.56305 | 0.80566 | 0.19226 | 0.82855 | 0.21515 | -0.032043 | 0.018311 | -122.612 | 0.11902 | 0.29297 | 0 | 0.32501 | 0.032043 | 0.58594 | 122.6807 | 0.15106 | 0.20142 | 122.7768 | 122.8317 | 122.7539 | 122.7997 | -122.8043 | -122.8134 | 122.6578 | 0.16937 | 2.5177 | 1.1215
2683.1875 | 123.0469 | -56.3187 | 66.4444 | -0.10635 | 0.0010489 | 0.060316 | 0.070113 | -5.343e-05 | 0.00091009 | 0.0039264 | 0.032227 | -0.0010339 | 0.00021363 | 5.9824e-05 | -0.0038559 | -0.0042981 | 0.0032299 | -53.8284 | 66.4444 | -56.3507 | 66.3025 | -55.8105 | -56.1813 | -55.5313 | -55.2887 | 66.4398 | -56.369 | -56.1676 | -56.2454 | -56.3553 | -56.0623 | -0.032043 | 0 | -0.14191 | 0.50812 | 0.78735 | 0.13733 | 0.8194 | 0.16937 | -0.050354 | -0.004578 | -122.612 | 0.073243 | 0.25635 | -0.036621 | 0.3067 | 0.013733 | 0.54016 | 122.6532 | 0.1236 | 0.20142 | 122.7951 | 122.8088 | 122.7631 | 122.7585 | -122.7951 | -122.8134 | 122.6212 | 0.15106 | 2.4902 | 1.03
2684.1719 | 122.9919 | -56.3416 | 66.4398 | -0.10635 | 0.00083526 | 0.061812 | 0.069045 | 0.00080117 | 0.0024053 | 0.0052082 | -0.034912 | 0.0019567 | -0.0014954 | 0.0043322 | -0.0036423 | -0.0047253 | 0.00088014 | -53.8376 | 66.4169 | -56.3599 | 66.2659 | -55.8334 | -56.2134 | -55.5908 | -55.307 | 66.4398 | -56.3782 | -56.2134 | -56.3004 | -56.4194 | -56.1127 | -0.01831 | -0.022888 | -0.17395 | 0.50812 | 0.75073 | 0.12817 | 0.76904 | 0.14648 | -0.036621 | 0 | -122.6532 | 0.041199 | 0.22888 | -0.07782 | 0.2655 | -0.041199 | 0.52643 | 122.6257 | 0.07782 | 0.16479 | 122.7768 | 122.818 | 122.7585 | 122.7814 | -122.7997 | -122.818 | 122.6074 | 0.12817 | 2.504 | 1.0345
2685.1719 | 123.0331 | -56.3461 | 66.4536 | -0.11398 | -0.00044654 | 0.061385 | 0.069045 | -0.0021896 | 0.0015509 | 0.0049946 | 0.023071 | -0.00082025 | 0.0019226 | 0.0036914 | -0.0012925 | -0.0030163 | -0.0025379 | -53.8467 | 66.4352 | -56.3599 | 66.2842 | -55.8243 | -56.1905 | -55.5588 | -55.2979 | 66.4856 | -56.369 | -56.1905 | -56.25 | -56.3736 | -56.0669 | -0.013733 | -0.01831 | -0.16937 | 0.52185 | 0.78735 | 0.15564 | 0.80109 | 0.16937 | -0.022889 | 0.032044 | -122.644 | 0.09613 | 0.27923 | -0.027466 | 0.30212 | -0.004577 | 0.53558 | 122.644 | 0.11902 | 0.17853 | 122.7951 | 122.8546 | 122.7814 | 122.8317 | -122.8134 | -122.8226 | 122.6303 | 0.15564 | 2.4994 | 1.0483
2686.1719 | 123.0515 | -56.3049 | 66.4398 | -0.10635 | 0.0019035 | 0.063094 | 0.070113 | 0.001442 | 0.00069649 | 0.0043536 | -0.0013428 | 0.0021703 | 0.00021363 | 0.00027342 | -0.0010787 | -0.0040845 | 0.0010937 | -53.8193 | 66.4398 | -56.337 | 66.3345 | -55.7693 | -56.1447 | -55.5313 | -55.2612 | 66.4719 | -56.369 | -56.1539 | -56.2225 | -56.3324 | -56.0532 | -0.032043 | 0 | -0.10528 | 0.53558 | 0.77362 | 0.16022 | 0.80566 | 0.19226 | -0.064087 | 0.032044 | -122.5937 | 0.082398 | 0.25177 | -0.027465 | 0.31586 | 0.036622 | 0.56763 | 122.6715 | 0.14648 | 0.21515 | 122.7768 | 122.8409 | 122.7448 | 122.7768 | -122.7768 | -122.8088 | 122.6395 | 0.15106 | 2.4857 | 1.0437
2687.1719 | 123.1934 | -56.2683 | 66.5405 | -0.098725 | -0.00023294 | 0.060103 | 0.067763 | -0.0017624 | 0.0030463 | 0.0052082 | 0.02002 | 0.0019567 | 0.0014954 | -0.00079478 | -0.0012925 | -0.0038709 | -0.0010425 | -53.7827 | 66.4398 | -56.3095 | 66.3666 | -55.7144 | -56.0852 | -55.4764 | -55.1651 | 66.4902 | -56.3278 | -56.1356 | -56.1768 | -56.3004 | -56.0623 | -0.041198 | -0.10071 | -0.17395 | 0.55389 | 0.79193 | 0.18311 | 0.83313 | 0.2243 | -0.059509 | -0.050354 | -122.6761 | 0.091553 | 0.20599 | -0.032043 | 0.2655 | 0.027466 | 0.59509 | 122.6761 | 0.15106 | 0.19226 | 122.7493 | 122.818 | 122.7081 | 122.7585 | -122.85 | -122.8683 | 122.6349 | 0.13275 | 2.4857 | 1.1032
2688.1875 | 123.0423 | -56.3461 | 66.4215 | -0.11398 | 0.00062166 | 0.062239 | 0.070968 | -0.00069423 | 0.0019781 | 0.0052082 | -0.068481 | 0.00088875 | -0.0012818 | 0.0028368 | -0.0032151 | -0.0042981 | -0.0018971 | -53.8467 | 66.4398 | -56.3599 | 66.2796 | -55.806 | -56.2134 | -55.6091 | -55.2658 | 66.4627 | -56.3736 | -56.1676 | -56.2729 | -56.3919 | -56.0394 | -0.013733 | 0.01831 | -0.14191 | 0.54016 | 0.737 | 0.13275 | 0.75073 | 0.14648 | -0.027466 | 0.041199 | -122.5891 | 0.073242 | 0.3067 | -0.045777 | 0.33417 | -0.018311 | 0.55389 | 122.6395 | 0.10071 | 0.20599 | 122.7997 | 122.8363 | 122.7859 | 122.8088 | -122.7814 | -122.7951 | 122.6257 | 0.17853 | 2.4994 | 1.0803
2689.1719 | 123.0972 | -56.3049 | 66.4719 | -0.075836 | -0.0017281 | 0.060957 | 0.068832 | 0.0012284 | 0.0028327 | 0.0067036 | 0.016968 | 0.00046135 | -0.00021357 | 0.0030506 | -0.0027877 | -0.0064343 | -0.00061526 | -53.8101 | 66.4719 | -56.3324 | 66.3666 | -55.7144 | -56.0944 | -55.4993 | -55.1971 | 66.481 | -56.337 | -56.1218 | -56.1905 | -56.3004 | -56.0257 | -0.027465 | 0 | -0.10529 | 0.59052 | 0.80566 | 0.21057 | 0.83313 | 0.23804 | -0.032043 | 0.009155 | -122.5937 | 0.11444 | 0.27924 | 0.004578 | 0.31128 | 0.036621 | 0.61798 | 122.699 | 0.14648 | 0.21515 | 122.8043 | 122.818 | 122.7768 | 122.786 | -122.8043 | -122.8088 | 122.6715 | 0.18311 | 2.4948 | 1.1078
2690.1719 | 122.9874 | -56.3278 | 66.4352 | -0.098725 | -0.00023294 | 0.060957 | 0.072036 | -0.00069423 | 0.0024053 | 0.0034992 | -0.0074462 | 0.00067495 | 0.00042723 | -0.0042126 | -0.0019333 | -0.0021619 | -0.0038197 | -53.833 | 66.4398 | -56.3599 | 66.2888 | -55.7877 | -56.2042 | -55.5679 | -55.2979 | 66.4993 | -56.3736 | -56.1951 | -56.2775 | -56.3965 | -56.0898 | -0.032043 | 0.004577 | -0.14648 | 0.54016 | 0.75989 | 0.1236 | 0.79193 | 0.15564 | -0.045776 | 0.064087 | -122.6303 | 0.050354 | 0.23804 | -0.068664 | 0.28381 | -0.022888 | 0.5722 | 122.6486 | 0.09613 | 0.17853 | 122.7997 | 122.8729 | 122.7676 | 122.8271 | -122.7951 | -122.8088 | 122.6166 | 0.13275 | 2.4948 | 1.03
2691.1719 | 123.0103 | -56.2866 | 66.4902 | -0.0071715 | 0.0014761 | 0.061598 | 0.0699 | -0.0041122 | 0.0032599 | 0.0015766 | -0.0074462 | -0.00060665 | -0.0012818 | -0.0042126 | -0.0040695 | -0.0023755 | -0.0023243 | -53.7872 | 66.4627 | -56.2912 | 66.3666 | -55.7373 | -56.0806 | -55.5038 | -55.2155 | 66.5222 | -56.3187 | -56.1539 | -56.1996 | -56.3049 | -56.0394 | -0.004578 | -0.027465 | -0.1236 | 0.54932 | 0.78278 | 0.20599 | 0.78735 | 0.21057 | -0.032044 | 0.032044 | -122.644 | 0.086975 | 0.24719 | -0.018311 | 0.27924 | 0.013733 | 0.55389 | 122.6578 | 0.11902 | 0.1648 | 122.7539 | 122.8409 | 122.7493 | 122.8088 | -122.7814 | -122.8088 | 122.6532 | 0.13275 | 2.4994 | 1.0712
2692.1719 | 123.0148 | -56.3232 | 66.4536 | -0.060578 | 0.0014761 | 0.06288 | 0.070113 | -0.0034714 | 0.00091009 | 0.0028582 | -0.028809 | -0.00017945 | 0.00021363 | 0.0034778 | -0.0032151 | -0.0040845 | -0.0010425 | -53.801 | 66.4398 | -56.3187 | 66.33 | -55.7648 | -56.163 | -55.5588 | -55.2521 | 66.4627 | -56.3553 | -56.1768 | -56.2683 | -56.3782 | -56.0669 | 0.004577 | -0.013733 | -0.1236 | 0.55847 | 0.76447 | 0.16022 | 0.75989 | 0.15564 | -0.032044 | 0.009156 | -122.6303 | 0.054931 | 0.25635 | -0.054932 | 0.28839 | -0.022888 | 0.55389 | 122.6486 | 0.086975 | 0.17853 | 122.7585 | 122.818 | 122.7631 | 122.786 | -122.7722 | -122.8088 | 122.6532 | 0.14648 | 2.5223 | 1.0712
2693.1875 | 122.9919 | -56.3232 | 66.4581 | -0.11398 | 0.00040806 | 0.062025 | 0.068832 | -0.0021896 | 0.0011237 | 0.00414 | -0.022705 | 0.00046135 | 0.001068 | -0.00015378 | -0.0010787 | -0.0049389 | 0.00023934 | -53.833 | 66.4536 | -56.3278 | 66.3071 | -55.7556 | -56.1813 | -55.5267 | -55.2704 | 66.4719 | -56.3553 | -56.1584 | -56.2546 | -56.3782 | -56.0852 | -0.004578 | -0.004578 | -0.15106 | 0.56763 | 0.79651 | 0.14191 | 0.80109 | 0.14649 | -0.032044 | 0.013733 | -122.6166 | 0.068664 | 0.23804 | -0.054932 | 0.27008 | -0.022888 | 0.57221 | 122.6349 | 0.10071 | 0.19684 | 122.7814 | 122.8271 | 122.7768 | 122.7951 | -122.7859 | -122.8134 | 122.6303 | 0.16479 | 2.4902 | 1.0529
2694.1719 | 123.0835 | -56.2912 | 66.4902 | -0.060578 | -0.0013009 | 0.059889 | 0.069686 | -0.0043258 | 0.0030463 | 0.0052082 | 0.016968 | 0.00024775 | 0.001709 | -0.0027174 | -0.0021469 | -0.0051527 | -0.0027515 | -53.7872 | 66.4764 | -56.3095 | 66.3757 | -55.719 | -56.0852 | -55.4626 | -55.1834 | 66.4993 | -56.3049 | -56.0806 | -56.163 | -56.2729 | -56.0074 | -0.01831 | -0.013733 | -0.11444 | 0.5722 | 0.82855 | 0.20599 | 0.84686 | 0.2243 | -0.013733 | 0.009156 | -122.5708 | 0.12817 | 0.28381 | 0.018311 | 0.29755 | 0.032044 | 0.59051 | 122.6852 | 0.14191 | 0.22431 | 122.7859 | 122.8043 | 122.7676 | 122.7905 | -122.7997 | -122.7951 | 122.6669 | 0.21057 | 2.504 | 1.1078
2695.1719 | 123.0194 | -56.2775 | 66.4719 | -0.098725 | -1.9142e-05 | 0.061171 | 0.070113 | 0.00037377 | 0.0021917 | 0.0049946 | -0.025757 | 0.0013159 | 0.00085443 | -0.0044262 | -0.0015061 | -0.0038709 | 0.0015209 | -53.8284 | 66.481 | -56.3141 | 66.3025 | -55.8014 | -56.1722 | -55.5542 | -55.3024 | 66.4993 | -56.3324 | -56.1768 | -56.2775 | -56.3782 | -56.0623 | -0.036621 | 0.009155 | -0.16937 | 0.47607 | 0.72327 | 0.10529 | 0.75989 | 0.14191 | -0.054931 | 0.027466 | -122.6486 | 0 | 0.21515 | -0.10071 | 0.27008 | -0.045777 | 0.5127 | 122.6166 | 0.054931 | 0.15564 | 122.7951 | 122.8317 | 122.7585 | 122.7768 | -122.7859 | -122.8043 | 122.58 | 0.10071 | 2.449 | 0.97504
2696.1719 | 122.9736 | -56.3004 | 66.4719 | -0.12924 | 0.0016899 | 0.061385 | 0.071395 | -0.0043258 | 0.0017645 | 0.0043536 | 0.001709 | 0.0019567 | -0.00021357 | 0.0064684 | -0.0040695 | -0.0045117 | 0.0045117 | -53.8147 | 66.4444 | -56.3095 | 66.3071 | -55.7648 | -56.1722 | -55.5222 | -55.2567 | 66.4764 | -56.3461 | -56.1493 | -56.2408 | -56.369 | -56.0715 | -0.009155 | -0.027466 | -0.16479 | 0.53558 | 0.7782 | 0.12817 | 0.78735 | 0.13733 | -0.045776 | 0.004577 | -122.6212 | 0.059509 | 0.22888 | -0.068665 | 0.27466 | -0.022889 | 0.54474 | 122.6166 | 0.10529 | 0.19684 | 122.7539 | 122.8226 | 122.7448 | 122.7768 | -122.7814 | -122.818 | 122.6074 | 0.15106 | 2.4857 | 1.0437
2697.1719 | 123.0194 | -56.2271 | 66.4856 | -0.022431 | -0.00066014 | 0.059889 | 0.069045 | -0.0032578 | 0.0015509 | 0.0034992 | 0.029175 | 0.00046135 | -0.00085457 | -0.00229 | -0.00086511 | -0.0062207 | 0.0049389 | -53.7506 | 66.481 | -56.2958 | 66.3986 | -55.6686 | -56.0532 | -55.4398 | -55.1605 | 66.5268 | -56.3004 | -56.0532 | -55.8975 | -56.3873 | -56.1493 | -0.068664 | -0.004578 | -0.086975 | 0.55847 | 0.78735 | 0.17395 | 0.85602 | 0.24261 | -0.073242 | 0.041198 | -122.5388 | 0.32959 | 0.07782 | -0.16022 | 0.15106 | -0.086975 | 0.62714 | 122.6944 | 0.40283 | 0.24719 | 122.7768 | 122.8271 | 122.7081 | 122.7539 | -122.7814 | -122.7859 | 122.6257 | 0.17395 | 2.4765 | 1.0666
2698.1719 | 122.9828 | -56.3004 | 66.5497 | -0.098725 | -0.0023691 | 0.062453 | 0.071395 | -0.0013352 | 0.0015509 | 0.0045672 | -0.06543 | 0.00024775 | -0.00042717 | 0.0036914 | -0.0025741 | -0.0030163 | -0.0018971 | -53.7918 | 66.5314 | -56.3278 | 66.3162 | -55.7968 | -56.1356 | -55.545 | -55.2795 | 66.5771 | -56.3004 | -56.1722 | -56.2546 | -56.3644 | -56.044 | -0.027466 | -0.018311 | -0.23346 | 0.50354 | 0.75531 | 0.16479 | 0.78278 | 0.19226 | 0 | 0.027465 | -122.7219 | 0.045776 | 0.25635 | -0.064087 | 0.25635 | -0.064087 | 0.53101 | 122.644 | 0.045776 | 0.12817 | 122.8592 | 122.8775 | 122.8317 | 122.8775 | -122.8775 | -122.85 | 122.6166 | 0.12817 | 2.5085 | 1.0208
2699.1719 | 123.0331 | -56.2866 | 66.481 | -0.15976 | -0.00044654 | 0.062239 | 0.068618 | 0.00016017 | 0.0032599 | 0.0037128 | -0.022705 | 0.0017431 | 0.001068 | 0.00091422 | -0.0032151 | -0.0049389 | -0.0021107 | -53.7918 | 66.4581 | -56.3095 | 66.3483 | -55.7281 | -56.131 | -55.5038 | -55.2109 | 66.4902 | -56.3507 | -56.1264 | -56.2317 | -56.337 | -56.0211 | -0.022888 | -0.022888 | -0.13275 | 0.55847 | 0.78278 | 0.15564 | 0.80566 | 0.17853 | -0.064087 | 0.009155 | -122.6074 | 0.054932 | 0.2655 | -0.050354 | 0.32959 | 0.013733 | 0.58136 | 122.6578 | 0.11902 | 0.2243 | 122.7676 | 122.8409 | 122.7448 | 122.7768 | -122.7905 | -122.8317 | 122.6349 | 0.16022 | 2.4948 | 1.0757
2700.1719 | 122.9874 | -56.2592 | 66.4856 | -0.12924 | 0.0019035 | 0.060957 | 0.069259 | 0.0020828 | 0.00048269 | 0.0060626 | -0.016602 | 0.0019567 | -0.00042717 | 0.0036914 | 0.00020289 | -0.0047253 | 0.0028027 | -53.8101 | 66.4627 | -56.3095 | 66.3254 | -55.7419 | -56.1447 | -55.513 | -55.2567 | 66.5131 | -56.3232 | -56.1584 | -56.25 | -56.3416 | -56.0349 | -0.050354 | -0.022888 | -0.16022 | 0.51727 | 0.74616 | 0.11444 | 0.79651 | 0.16479 | -0.064087 | 0.027466 | -122.644 | 0.009155 | 0.2243 | -0.082398 | 0.28839 | -0.018311 | 0.56763 | 122.6349 | 0.073242 | 0.16479 | 122.7722 | 122.8363 | 122.7219 | 122.7722 | -122.7951 | -122.8088 | 122.5845 | 0.10071 | 2.449 | 1.0025
2701.1719 | 123.0469 | -56.25 | 66.5085 | -0.037689 | 0.00083526 | 0.060744 | 0.067763 | -0.00048063 | 0.0013373 | 0.0049946 | 0.02002 | 0.0023839 | 0.003418 | 0.0015552 | -0.0027877 | -0.0040845 | -0.0031787 | -53.7781 | 66.5176 | -56.2866 | 66.362 | -55.7098 | -56.0806 | -55.4535 | -55.1926 | 66.5451 | -56.282 | -56.0898 | -56.1447 | -56.2592 | -55.9891 | -0.036621 | 0.009155 | -0.14648 | 0.54016 | 0.79651 | 0.16937 | 0.83313 | 0.20599 | -0.032043 | 0.036621 | -122.5983 | 0.10529 | 0.26093 | -0.009155 | 0.29297 | 0.022888 | 0.57678 | 122.6486 | 0.13733 | 0.19226 | 122.8043 | 122.8271 | 122.7676 | 122.7951 | -122.7951 | -122.7905 | 122.612 | 0.16022 | 2.4719 | 1.0574
2702.1719 | 123.0011 | -56.2592 | 66.5314 | -0.10635 | -0.0013009 | 0.061598 | 0.068404 | -0.0024032 | 0.0030463 | 0.0039264 | 0.013916 | 0.0011023 | -0.00021357 | -0.0016492 | -0.0021469 | -0.0066479 | -0.0025379 | -53.7231 | 66.5131 | -56.282 | 66.33 | -55.7556 | -56.131 | -55.5313 | -55.2658 | 66.5314 | -56.3232 | -56.1356 | -56.1996 | -56.3232 | -56.0349 | -0.022888 | -0.01831 | -0.20142 | 0.50354 | 0.72784 | 0.12817 | 0.75073 | 0.15106 | -0.064087 | 0 | -122.6669 | 0.059509 | 0.2243 | -0.064087 | 0.28839 | 0 | 0.52643 | 122.612 | 0.1236 | 0.18768 | 122.7951 | 122.8546 | 122.7722 | 122.7905 | -122.8134 | -122.8546 | 122.5891 | 0.1236 | 2.536 | 0.99335
2703.1719 | 122.9874 | -56.2683 | 66.5451 | -0.03006 | -0.0013009 | 0.063307 | 0.072036 | 0.0012284 | -0.00015811 | 0.0060626 | -0.059326 | 0.0015295 | 0.00042723 | 0.0045458 | -0.0034287 | -0.0038709 | -0.0038197 | -53.7552 | 66.5588 | -56.3095 | 66.3254 | -55.7785 | -56.1172 | -55.5222 | -55.2475 | 66.5955 | -56.3004 | -56.1401 | -56.2225 | -56.369 | -56.0532 | -0.041198 | 0.013733 | -0.21973 | 0.48981 | 0.74615 | 0.15106 | 0.78735 | 0.19226 | -0.032043 | 0.050354 | -122.6852 | 0.045777 | 0.21515 | -0.10071 | 0.24719 | -0.068665 | 0.53101 | 122.6349 | 0.07782 | 0.16022 | 122.8683 | 122.8958 | 122.8271 | 122.8638 | -122.8546 | -122.8455 | 122.5937 | 0.12817 | 2.5131 | 1.0208
2704.1719 | 122.9507 | -56.2546 | 66.5497 | -0.060578 | -0.00087374 | 0.062239 | 0.071181 | -0.0041122 | 0.0026191 | 0.0073444 | -0.08374 | 0.00088875 | 0.0014954 | 0.0047594 | -0.0019333 | -0.0042981 | -0.00082886 | -53.7598 | 66.5451 | -56.3232 | 66.3391 | -55.7693 | -56.1493 | -55.5313 | -55.2612 | 66.5634 | -56.3095 | -56.1493 | -56.2546 | -56.3828 | -56.0532 | -0.068664 | -0.004578 | -0.21057 | 0.48523 | 0.72327 | 0.10529 | 0.79193 | 0.17395 | -0.054931 | 0.013733 | -122.699 | 0 | 0.20142 | -0.12817 | 0.25635 | -0.073242 | 0.55389 | 122.6624 | 0.054931 | 0.16022 | 122.8683 | 122.8729 | 122.7997 | 122.818 | -122.8729 | -122.8592 | 122.5937 | 0.10529 | 2.4948 | 0.99335
2705.1719 | 123.0103 | -56.2408 | 66.5268 | -0.1445 | -0.00044654 | 0.06053 | 0.068832 | -0.0011214 | 0.0026191 | 0.005849 | 0.041382 | 0.00067495 | -0.00064077 | 0.0030506 | -0.00065151 | -0.0060071 | 0.0025891 | -53.7918 | 66.4902 | -56.2958 | 66.3528 | -55.7693 | -56.1172 | -55.481 | -55.2521 | 66.5268 | -56.2958 | -56.2317 | -56.0715 | -56.2637 | -56.044 | -0.054931 | -0.036621 | -0.17395 | 0.4715 | 0.75989 | 0.1236 | 0.81482 | 0.17853 | -0.054931 | 0 | -122.7585 | 0.16937 | 0.19684 | -0.022888 | 0.25177 | 0.032043 | 0.52643 | 122.6486 | 0.2243 | 0.064087 | 122.7859 | 122.8226 | 122.731 | 122.7676 | -122.8226 | -122.8226 | 122.5937 | 0.009156 | 2.449 | 0.98877
2706.1719 | 123.0148 | -56.2546 | 66.5222 | -0.10635 | 0.00083526 | 0.063307 | 0.070113 | -0.001976 | 0.0017645 | 0.0077716 | -0.010498 | 0.0021703 | 0.00085443 | 0.003905 | -0.00086511 | -0.0047253 | 0.0010937 | -53.7552 | 66.4948 | -56.2729 | 66.3666 | -55.7144 | -56.1081 | -55.481 | -55.2063 | 66.5085 | -56.3004 | -56.1264 | -56.2088 | -56.3004 | -56.0303 | -0.01831 | -0.027466 | -0.15564 | 0.54016 | 0.77362 | 0.14649 | 0.79193 | 0.1648 | -0.045776 | -0.013733 | -122.6486 | 0.045777 | 0.22431 | -0.045776 | 0.27008 | 0 | 0.55847 | 122.6395 | 0.091553 | 0.17395 | 122.7676 | 122.8088 | 122.7493 | 122.7631 | -122.7951 | -122.8226 | 122.6212 | 0.12817 | 2.4994 | 1.0483
2707.1719 | 123.0377 | -56.2775 | 66.5176 | -0.1445 | -0.00023294 | 0.062239 | 0.067123 | -0.0013352 | 0.0032599 | 0.0037128 | 0.0047608 | 3.4148e-05 | -0.00064077 | 0.0032642 | -0.0010787 | -0.0036573 | -0.00082886 | -53.746 | 66.481 | -56.2683 | 66.3757 | -55.6915 | -56.0944 | -55.4718 | -55.1926 | 66.5405 | -56.3004 | -56.0989 | -56.1996 | -56.3141 | -56.0074 | 0.009155 | -0.036621 | -0.14191 | 0.58594 | 0.80566 | 0.18311 | 0.79651 | 0.17395 | -0.022888 | 0.022888 | -122.6166 | 0.07782 | 0.27008 | -0.036621 | 0.29297 | -0.013733 | 0.57678 | 122.644 | 0.10071 | 0.20142 | 122.7493 | 122.8409 | 122.7585 | 122.818 | -122.7859 | -122.818 | 122.6532 | 0.17853 | 2.5314 | 1.0849
2708.1719 | 123.0057 | -56.2271 | 66.5863 | -0.068207 | -0.0015145 | 0.060316 | 0.070327 | -0.0017624 | 0.00048269 | 0.0045672 | -0.0043946 | 0.00046135 | 0.0019226 | -0.0065626 | -0.0030013 | -0.0045117 | -0.0025379 | -53.7094 | 66.5543 | -56.25 | 66.4124 | -55.6778 | -56.044 | -55.426 | -55.1697 | 66.5909 | -56.2683 | -56.1172 | -56.1722 | -56.2958 | -56.0074 | -0.022888 | -0.032044 | -0.17395 | 0.54932 | 0.80109 | 0.18311 | 0.82397 | 0.20599 | -0.041199 | 0.004577 | -122.7036 | 0.054932 | 0.21973 | -0.068664 | 0.26093 | -0.027465 | 0.5722 | 122.6624 | 0.096131 | 0.15106 | 122.8043 | 122.8592 | 122.7814 | 122.818 | -122.8363 | -122.8546 | 122.6395 | 0.10986 | 2.5177 | 1.0574
2709.1719 | 122.9553 | -56.2546 | 66.5405 | -0.045319 | 0.00040806 | 0.061171 | 0.070541 | 0.001442 | 0.0026191 | 0.0064898 | -0.059326 | 0.0017431 | 0.00064083 | 0.0032642 | -0.0021469 | -0.0042981 | 0.0017345 | -53.714 | 66.5405 | -56.2729 | 66.3528 | -55.7419 | -56.1035 | -55.4947 | -55.2155 | 66.6092 | -56.2866 | -56.1218 | -56.2042 | -56.3416 | -55.9708 | -0.01831 | 0 | -0.18768 | 0.5127 | 0.75989 | 0.15106 | 0.7782 | 0.16937 | -0.032043 | 0.068665 | -122.6624 | 0.050354 | 0.28381 | -0.086975 | 0.31586 | -0.054932 | 0.53101 | 122.6257 | 0.082397 | 0.16479 | 122.8134 | 122.8958 | 122.7951 | 122.8638 | -122.8134 | -122.8271 | 122.6074 | 0.13275 | 2.5406 | 1.0391
2710.1719 | 123.0103 | -56.218 | 66.5268 | -0.10635 | 0.0014761 | 0.062025 | 0.068404 | 0.00016017 | 0.0011237 | 0.0047808 | 0.032227 | -0.0012477 | -0.0019226 | -0.0016492 | 0.00041649 | -0.0038709 | 0.0023755 | -53.7643 | 66.5359 | -56.2546 | 66.362 | -55.7465 | -56.1172 | -55.4535 | -55.2246 | 66.568 | -56.282 | -56.1539 | -56.0806 | -56.2775 | -56.0486 | -0.036621 | 0.009156 | -0.16479 | 0.4715 | 0.76447 | 0.10071 | 0.80109 | 0.13733 | -0.064086 | 0.041199 | -122.6807 | 0.13733 | 0.16937 | -0.059509 | 0.23346 | 0.004577 | 0.50812 | 122.6166 | 0.20142 | 0.12817 | 122.7905 | 122.85 | 122.7539 | 122.7859 | -122.7814 | -122.8088 | 122.58 | 0.064087 | 2.4536 | 0.99335
2711.1719 | 123.0606 | -56.1951 | 66.5543 | -0.052948 | 0.00083526 | 0.060103 | 0.068832 | 0.0022964 | 0.0019781 | 0.0056354 | 0.03833 | -0.0010339 | 0.00064083 | -0.0016492 | -0.0021469 | -0.0051527 | 2.554e-05 | -53.7231 | 66.5543 | -56.2363 | 66.4169 | -55.6824 | -56.0394 | -55.4169 | -55.1468 | 66.5771 | -56.25 | -56.0532 | -56.1035 | -56.2271 | -55.925 | -0.041199 | 0 | -0.13733 | 0.5127 | 0.7782 | 0.15564 | 0.8194 | 0.19684 | -0.054932 | 0.022888 | -122.6074 | 0.091552 | 0.27008 | -0.032044 | 0.32501 | 0.022888 | 0.55389 | 122.6532 | 0.14648 | 0.19684 | 122.7905 | 122.8271 | 122.7493 | 122.7722 | -122.7905 | -122.8043 | 122.612 | 0.14191 | 2.4719 | 1.0483
2712.1719 | 123.0286 | -56.2271 | 66.5405 | -0.075836 | 0.00019446 | 0.063734 | 0.068832 | 0.001442 | 0.0043281 | 0.0037128 | -0.016602 | 0.00067495 | 2.8e-08 | 0.0036914 | -0.0047103 | -0.0040845 | -0.0010425 | -53.6957 | 66.4948 | -56.2408 | 66.4078 | -55.5862 | -55.9479 | -55.4443 | -55.1285 | 66.5314 | -56.2637 | -56.0577 | -56.1539 | -56.2775 | -55.957 | -0.013733 | -0.045776 | -0.13275 | 0.64087 | 0.78278 | 0.27924 | 0.79651 | 0.29297 | -0.036621 | -0.009155 | -122.5983 | 0.073242 | 0.27008 | -0.050354 | 0.3067 | -0.013733 | 0.6546 | 122.6486 | 0.10986 | 0.20599 | 122.7356 | 122.7951 | 122.7219 | 122.7585 | -122.7814 | -122.8043 | 122.6349 | 0.16937 | 2.5314 | 1.0986
2713.1719 | 123.0606 | -56.1859 | 66.5771 | -0.28183 | -0.00087374 | 0.060744 | 0.066909 | -0.00026703 | 0.0030463 | 0.0045672 | 0.0078126 | 0.0013159 | -0.0010682 | 0.00070062 | -0.0015061 | -0.0049389 | -0.0014697 | -53.6819 | 66.5359 | -56.25 | 66.4444 | -55.6137 | -55.9662 | -55.3986 | -55.1285 | 66.6 | -56.2317 | -56.0532 | -56.0898 | -56.2317 | -55.9479 | -0.064087 | -0.041198 | -0.13275 | 0.5722 | 0.78735 | 0.21973 | 0.85144 | 0.28381 | -0.045776 | 0.022889 | -122.6303 | 0.09613 | 0.23804 | -0.045776 | 0.28381 | 0 | 0.63629 | 122.6944 | 0.14191 | 0.17853 | 122.7859 | 122.8317 | 122.7219 | 122.7859 | -122.8271 | -122.8088 | 122.6303 | 0.13275 | 2.504 | 1.0574
2714.1719 | 122.9599 | -56.1905 | 66.687 | -0.0071715 | -0.00066014 | 0.061812 | 0.069259 | -0.0030442 | 0.0021917 | 0.0049946 | -0.016602 | -0.00060665 | 0.00042723 | 0.0041186 | -0.0021469 | -0.0047253 | -0.0053149 | -53.7048 | 66.5726 | -56.2363 | 66.3483 | -55.751 | -56.0989 | -55.4901 | -55.2475 | 66.6458 | -56.2454 | -56.1218 | -56.2088 | -56.3232 | -56.1447 | -0.045776 | -0.11444 | -0.33874 | 0.43945 | 0.70038 | 0.091553 | 0.74615 | 0.13733 | -0.054931 | -0.041199 | -122.8088 | -0.01831 | 0.045777 | -0.13275 | 0.10071 | -0.07782 | 0.48523 | 122.5845 | 0.036621 | 0.1236 | 122.8088 | 122.8912 | 122.7631 | 122.8363 | -122.9233 | -122.9324 | 122.5388 | 0.068665 | 2.4857 | 0.94299
2715.1719 | 123.024 | -56.2225 | 66.5359 | -0.12924 | -0.00044654 | 0.062025 | 0.070541 | 0.003151 | 0.0047553 | 0.0043536 | -0.010498 | 0.0019567 | 0.001068 | -0.0018628 | -0.0027877 | -0.0036573 | 0.0010937 | -53.7094 | 66.5085 | -56.2592 | 66.4032 | -55.6458 | -56.0715 | -55.4214 | -55.1559 | 66.5588 | -56.2683 | -56.0577 | -56.1401 | -56.282 | -55.9799 | -0.036621 | -0.027466 | -0.13275 | 0.57678 | 0.80109 | 0.15106 | 0.83771 | 0.18768 | -0.045777 | 0.022888 | -122.5937 | 0.082397 | 0.24262 | -0.059509 | 0.28839 | -0.013732 | 0.6134 | 122.6624 | 0.12817 | 0.21057 | 122.7676 | 122.8271 | 122.731 | 122.7814 | -122.7951 | -122.8043 | 122.6257 | 0.1648 | 2.5131 | 1.0666
2716.1719 | 123.0606 | -56.2225 | 66.5497 | -0.15213 | -1.9142e-05 | 0.06288 | 0.068832 | -0.00048063 | 0.00069649 | 0.0073444 | -0.016602 | 0.0021703 | 2.8e-08 | 0.002196 | -0.0040695 | -0.0079297 | 0.0045117 | -53.6957 | 66.5314 | -56.2271 | 66.4398 | -55.6641 | -56.0532 | -55.4077 | -55.1422 | 66.5817 | -56.2637 | -56.044 | -56.1447 | -56.2637 | -55.9662 | -0.004578 | -0.018311 | -0.10986 | 0.55847 | 0.81482 | 0.16937 | 0.8194 | 0.17395 | -0.041199 | 0.032043 | -122.5937 | 0.07782 | 0.25635 | -0.041199 | 0.29755 | 0 | 0.56305 | 122.6669 | 0.11902 | 0.21973 | 122.7585 | 122.8455 | 122.7539 | 122.8043 | -122.7768 | -122.8134 | 122.6624 | 0.17853 | 2.5269 | 1.0803
2717.1719 | 123.0698 | -56.1951 | 66.5726 | -0.068207 | 0.00019446 | 0.06053 | 0.068618 | -0.0013352 | 0.00069649 | 0.0043536 | 0.02002 | -0.00039305 | 0.0014954 | -0.007417 | -0.0047103 | -0.0042981 | 0.00045294 | -53.6911 | 66.568 | -56.2088 | 66.4444 | -55.6503 | -56.0028 | -55.394 | -55.1239 | 66.5863 | -56.2454 | -55.9937 | -56.0669 | -56.1813 | -55.9113 | -0.013733 | -0.004578 | -0.12817 | 0.54474 | 0.80109 | 0.19226 | 0.81482 | 0.20599 | -0.050354 | 0.013733 | -122.5662 | 0.12817 | 0.28381 | 0.013733 | 0.33417 | 0.064087 | 0.55847 | 122.6532 | 0.17853 | 0.25177 | 122.7768 | 122.8317 | 122.7631 | 122.7814 | -122.7814 | -122.818 | 122.6395 | 0.20142 | 2.504 | 1.0712
2718.1719 | 122.9507 | -56.1813 | 66.6321 | 0.015716 | -1.9142e-05 | 0.058607 | 0.070968 | -0.00048063 | 0.0011237 | 0.0049946 | -0.062378 | 0.0015295 | -0.00064077 | 0.0043322 | -0.0015061 | -0.0038709 | 0.0010937 | -53.6774 | 66.6092 | -56.2454 | 66.3895 | -55.6961 | -56.0532 | -55.4626 | -55.1651 | 66.655 | -56.2271 | -56.0761 | -56.1722 | -56.2912 | -55.9799 | -0.064087 | -0.022888 | -0.24262 | 0.48523 | 0.71869 | 0.12817 | 0.78278 | 0.19226 | -0.045777 | 0.022888 | -122.7081 | 0.009155 | 0.20142 | -0.10986 | 0.24719 | -0.064087 | 0.54932 | 122.6349 | 0.054932 | 0.15106 | 122.8546 | 122.8821 | 122.7905 | 122.8363 | -122.8775 | -122.8592 | 122.5708 | 0.10528 | 2.504 | 1.0162
2719.1719 | 122.9553 | -56.2042 | 66.6504 | 0.00045798 | -0.0013009 | 0.061598 | 0.066909 | 0.0012284 | -0.00058531 | 0.0047808 | -0.010498 | 0.00067495 | 0.00064083 | 0.0060412 | -0.0010787 | -0.0042981 | 0.00045294 | -53.7003 | 66.6183 | -56.2271 | 66.3712 | -55.7281 | -56.0623 | -55.4718 | -55.2292 | 66.6687 | -56.2363 | -56.0989 | -56.1584 | -56.3141 | -55.9937 | -0.022888 | -0.032044 | -0.27924 | 0.47608 | 0.73242 | 0.14191 | 0.75531 | 0.16479 | -0.032043 | 0.01831 | -122.7493 | 0.045777 | 0.21057 | -0.10986 | 0.24262 | -0.07782 | 0.49896 | 122.5983 | 0.07782 | 0.13733 | 122.8455 | 122.905 | 122.8226 | 122.8729 | -122.8775 | -122.8867 | 122.5754 | 0.10529 | 2.504 | 0.97504
2720.1719 | 123.0194 | -56.2042 | 66.5588 | -0.12161 | 0.0021171 | 0.063521 | 0.067763 | -0.00048063 | 0.0032599 | 0.0096942 | 0.0047608 | 0.00088875 | -0.0019226 | 0.0028368 | -0.0010787 | -0.0038709 | 0.0019483 | -53.6865 | 66.5405 | -56.2317 | 66.4169 | -55.6412 | -56.0394 | -55.3986 | -55.1285 | 66.5863 | -56.2408 | -56.0532 | -56.131 | -56.2454 | -55.9479 | -0.027465 | -0.018311 | -0.14191 | 0.56305 | 0.80566 | 0.1648 | 0.83313 | 0.19226 | -0.036621 | 0.027466 | -122.612 | 0.073243 | 0.25635 | -0.041198 | 0.29297 | -0.004577 | 0.59052 | 122.6486 | 0.10986 | 0.18768 | 122.7722 | 122.8271 | 122.7448 | 122.7905 | -122.7905 | -122.7997 | 122.6212 | 0.15106 | 2.5177 | 1.0757
2721.1719 | 122.9965 | -56.2088 | 66.5771 | -0.1445 | 0.0010489 | 0.062025 | 0.068191 | -0.00069423 | 0.00069649 | 0.00414 | 0.047485 | -0.0010339 | 0.0021362 | -0.00058098 | -0.0017197 | -0.0066479 | 0.00045294 | -53.7186 | 66.5863 | -56.1951 | 66.4169 | -55.6778 | -56.0623 | -55.4077 | -55.0827 | 66.6229 | -56.1996 | -56.0715 | -56.131 | -56.2546 | -55.9708 | 0.013733 | 0.009156 | -0.16022 | 0.53101 | 0.80109 | 0.14648 | 0.78735 | 0.13275 | 0.009155 | 0.045777 | -122.6486 | 0.07782 | 0.23804 | -0.045777 | 0.22888 | -0.054932 | 0.51727 | 122.612 | 0.068665 | 0.12817 | 122.7814 | 122.8226 | 122.7951 | 122.8317 | -122.7722 | -122.7768 | 122.6257 | 0.13733 | 2.4902 | 1.1261
2722.1719 | 123.0698 | -56.2134 | 66.5771 | -0.014801 | -1.9142e-05 | 0.061385 | 0.0699 | -0.0017624 | 5.5488e-05 | 0.0022174 | 0.010864 | 0.0019567 | -0.00085457 | 0.0026232 | -0.0025741 | -0.0038709 | 2.554e-05 | -53.6407 | 66.5451 | -56.2317 | 66.4444 | -55.6458 | -56.044 | -55.3757 | -55.1239 | 66.5863 | -56.2271 | -56.0257 | -56.1172 | -56.2317 | -55.9296 | -0.01831 | -0.032043 | -0.13275 | 0.56763 | 0.83771 | 0.16937 | 0.85602 | 0.18768 | -0.013733 | 0.009156 | -122.6028 | 0.09613 | 0.28381 | -0.01831 | 0.29755 | -0.004577 | 0.58594 | 122.6761 | 0.10986 | 0.20142 | 122.7768 | 122.8134 | 122.7585 | 122.7997 | -122.8088 | -122.8043 | 122.6578 | 0.18768 | 2.5726 | 1.0895
2723.1875 | 123.0469 | -56.131 | 66.5909 | -0.068207 | -0.0019417 | 0.062239 | 0.066482 | -0.0013352 | 0.0030463 | 0.0056354 | 0.029175 | -0.00039305 | 0.00085443 | -0.00079478 | -0.0015061 | -0.0062207 | 0.0021619 | -53.6682 | 66.6046 | -56.1905 | 66.4719 | -55.6091 | -55.9525 | -55.3391 | -55.0735 | 66.6275 | -56.2042 | -55.9799 | -56.0394 | -56.163 | -55.8792 | -0.05951 | 0.013733 | -0.11902 | 0.52185 | 0.79193 | 0.17853 | 0.85144 | 0.23804 | -0.073243 | 0.036621 | -122.5708 | 0.091552 | 0.25177 | -0.032044 | 0.32501 | 0.041199 | 0.58136 | 122.6624 | 0.1648 | 0.22431 | 122.7951 | 122.8317 | 122.7356 | 122.7585 | -122.7814 | -122.7951 | 122.6028 | 0.15106 | 2.4628 | 1.0574
2724.1719 | 122.9736 | -56.1722 | 66.6275 | -0.075836 | -0.00087374 | 0.060316 | 0.069686 | 0.00037377 | 0.0019781 | 0.0039264 | 0.02002 | 0.0021703 | -0.00064077 | -0.0027174 | -0.0010787 | -0.0060071 | 2.554e-05 | -53.6407 | 66.6 | -56.1905 | 66.4764 | -55.6 | -55.9753 | -55.3574 | -55.1285 | 66.6641 | -56.1905 | -56.0577 | -56.1127 | -56.2408 | -55.9525 | -0.018311 | -0.027465 | -0.15106 | 0.5722 | 0.81482 | 0.19684 | 0.83313 | 0.21515 | -0.018311 | 0.036622 | -122.6852 | 0.059509 | 0.21973 | -0.068665 | 0.23804 | -0.050354 | 0.59052 | 122.6669 | 0.07782 | 0.13275 | 122.7905 | 122.8546 | 122.7722 | 122.8363 | -122.818 | -122.818 | 122.6486 | 0.11444 | 2.5314 | 1.0437
2725.1719 | 122.9965 | -56.1905 | 66.5909 | -0.091095 | -0.00023294 | 0.059676 | 0.069045 | -0.0030442 | 0.0013373 | 0.0067036 | 0.026123 | -0.0012477 | 0.0012818 | -0.0044262 | -0.00022431 | -0.0068615 | -0.0029651 | -53.6911 | 66.5771 | -56.2042 | 66.4215 | -55.6778 | -56.0257 | -55.4123 | -55.0507 | 66.6687 | -56.2225 | -56.0303 | -56.1264 | -56.2546 | -55.9479 | -0.013733 | -0.013733 | -0.16937 | 0.5127 | 0.7782 | 0.16479 | 0.79193 | 0.17853 | -0.032043 | 0.07782 | -122.6212 | 0.064087 | 0.24262 | -0.064087 | 0.27466 | -0.032044 | 0.52643 | 122.6257 | 0.09613 | 0.19226 | 122.7814 | 122.8912 | 122.7676 | 122.8592 | -122.7951 | -122.8134 | 122.612 | 0.16022 | 2.4994 | 1.1398
2726.1719 | 123.056 | -56.1768 | 66.5497 | -0.098725 | -0.00023294 | 0.060957 | 0.070968 | -5.343e-05 | 0.0017645 | 0.0047808 | -0.0074462 | 0.0017431 | -0.00085457 | -0.0025036 | -0.0032151 | -0.0051527 | -0.0010425 | -53.5492 | 66.5863 | -56.1996 | 66.4627 | -55.6183 | -56.0211 | -55.3757 | -55.0964 | 66.5909 | -56.218 | -56.0074 | -56.1035 | -56.2225 | -55.9158 | -0.022888 | 0.036621 | -0.086975 | 0.55847 | 0.80109 | 0.15564 | 0.82398 | 0.17853 | -0.041199 | 0.041198 | -122.5571 | 0.073242 | 0.26093 | -0.045776 | 0.30212 | -0.004577 | 0.58136 | 122.6624 | 0.11444 | 0.21057 | 122.7859 | 122.8088 | 122.7631 | 122.7676 | -122.7493 | -122.7676 | 122.6395 | 0.16937 | 2.6276 | 1.0803
2727.1719 | 123.0423 | -56.1859 | 66.5955 | -0.11398 | 0.0025443 | 0.061598 | 0.070541 | 0.0018692 | -0.0012261 | 0.0062762 | -0.037964 | 0.00046135 | -0.00064077 | 0.0043322 | -0.0021469 | -0.0025891 | 0.0025891 | -53.6453 | 66.5634 | -56.1722 | 66.3162 | -55.5634 | -55.8105 | -55.2979 | -55.0827 | 66.6138 | -56.1996 | -55.9982 | -56.0944 | -56.1996 | -55.9113 | 0.013733 | -0.032043 | -0.27924 | 0.62256 | 0.88806 | 0.37537 | 0.87433 | 0.36163 | -0.013733 | 0.018311 | -122.5937 | 0.091553 | 0.27466 | -0.013733 | 0.28839 | 0 | 0.60883 | 122.4884 | 0.10529 | 0.20142 | 122.7356 | 122.8134 | 122.7493 | 122.7997 | -122.7676 | -122.7951 | 122.5021 | 0.18768 | 2.5406 | 1.1032
2728.1719 | 123.0515 | -56.163 | 66.6183 | -0.091095 | 0.00019446 | 0.059462 | 0.066695 | -0.001976 | 0.0024053 | 0.0043536 | 0.02002 | -0.00017945 | -0.0010682 | -0.0025036 | -0.0012925 | -0.0025891 | -0.0027515 | -53.6728 | 66.6092 | -56.1676 | 66.4627 | -55.6183 | -55.9616 | -55.3574 | -55.1193 | 66.655 | -56.1905 | -56.0074 | -56.0532 | -56.1813 | -55.8929 | -0.004578 | -0.009155 | -0.15564 | 0.54474 | 0.80566 | 0.20142 | 0.81024 | 0.20599 | -0.027466 | 0.036621 | -122.6257 | 0.10986 | 0.27008 | -0.01831 | 0.29755 | 0.009156 | 0.54932 | 122.6303 | 0.13733 | 0.18311 | 122.7768 | 122.8455 | 122.7722 | 122.818 | -122.7859 | -122.8088 | 122.6257 | 0.15564 | 2.4902 | 1.0437
2729.1719 | 123.0103 | -56.1493 | 66.6092 | -0.17502 | -0.00044654 | 0.061171 | 0.071609 | -0.0021896 | 0.00069649 | 0.0047808 | -0.010498 | -0.00017945 | -0.0010682 | 0.00027342 | -0.0040695 | -0.0045117 | -0.0014697 | -53.6728 | 66.5817 | -56.2088 | 66.4581 | -55.6229 | -56.0394 | -55.3802 | -55.1239 | 66.6138 | -56.2134 | -56.0303 | -56.1081 | -56.2408 | -55.925 | -0.059509 | -0.027466 | -0.15106 | 0.52643 | 0.76904 | 0.10986 | 0.82855 | 0.16937 | -0.064087 | 0.004578 | -122.6395 | 0.041199 | 0.2243 | -0.091553 | 0.28839 | -0.027466 | 0.58594 | 122.6669 | 0.10529 | 0.18311 | 122.7905 | 122.8271 | 122.731 | 122.7631 | -122.818 | -122.8226 | 122.6074 | 0.11902 | 2.4765 | 1.0254
2730.1719 | 123.0469 | -56.1539 | 66.6092 | -0.098725 | -0.00087374 | 0.061171 | 0.071822 | 0.0033646 | 0.0028327 | 0.0054218 | -0.068481 | 0.0017431 | 0.00064083 | -0.0016492 | -0.0027877 | -0.0042981 | -0.0018971 | -53.6728 | 66.5771 | -56.2042 | 66.449 | -55.6412 | -56.012 | -55.3986 | -55.101 | 66.6275 | -56.2088 | -55.9845 | -56.0806 | -56.218 | -55.8838 | -0.050354 | -0.032044 | -0.16022 | 0.5127 | 0.75531 | 0.14191 | 0.80566 | 0.19226 | -0.054931 | 0.01831 | -122.5937 | 0.073243 | 0.27008 | -0.064087 | 0.32501 | -0.009156 | 0.56305 | 122.6532 | 0.12817 | 0.2243 | 122.7814 | 122.8363 | 122.731 | 122.7814 | -122.8134 | -122.818 | 122.6028 | 0.16937 | 2.4811 | 1.0529
2731.1719 | 123.0377 | -56.1539 | 66.5909 | -0.1445 | -0.00044654 | 0.063307 | 0.070113 | 0.0012284 | 0.0032599 | 0.0054218 | 0.029175 | 0.0021703 | 0.0012818 | 0.00048702 | -0.0023605 | -0.0025891 | -0.00061526 | -53.6362 | 66.5771 | -56.1859 | 66.4856 | -55.6641 | -56.2271 | -55.2933 | -55.0827 | 66.6504 | -56.1996 | -55.9799 | -56.0898 | -56.1905 | -55.8929 | -0.032043 | -0.013733 | -0.10528 | 0.48981 | 0.8606 | -0.073242 | 0.89264 | -0.041199 | -0.045776 | 0.05951 | -122.5708 | 0.064087 | 0.26093 | -0.036621 | 0.3067 | 0.009155 | 0.52185 | 122.6715 | 0.10986 | 0.21973 | 122.7631 | 122.85 | 122.731 | 122.8043 | -122.7768 | -122.7905 | 122.6395 | 0.17395 | 2.5177 | 1.0712
2732.1719 | 123.0194 | -56.1493 | 66.5955 | -0.15213 | -0.00087374 | 0.062025 | 0.0699 | 0.0010148 | 0.0032599 | 0.0088398 | -0.041016 | 0.0019567 | -0.0021362 | -0.0020764 | -0.0015061 | -0.0072889 | -0.0021107 | -53.6087 | 66.5726 | -56.163 | 66.4856 | -55.6091 | -56.0028 | -55.3711 | -55.0735 | 66.6367 | -56.1813 | -55.9525 | -56.0852 | -56.163 | -55.8746 | -0.013733 | -0.022888 | -0.10986 | 0.54016 | 0.7782 | 0.14648 | 0.79193 | 0.16022 | -0.032043 | 0.041199 | -122.5479 | 0.064087 | 0.27466 | -0.013733 | 0.3067 | 0.01831 | 0.55389 | 122.6486 | 0.09613 | 0.22888 | 122.7356 | 122.818 | 122.7219 | 122.7859 | -122.7585 | -122.7768 | 122.6349 | 0.19684 | 2.5406 | 1.0757
2733.1719 | 123.0377 | -56.1584 | 66.6046 | -0.091095 | 0.00019446 | 0.061598 | 0.069686 | -0.0021896 | 0.0034735 | 0.0037128 | -0.016602 | 0.00067495 | 0.00042723 | 0.0058276 | -0.0012925 | -0.0025891 | 0.0019483 | -53.627 | 66.6412 | -56.1539 | 66.4902 | -55.5862 | -55.9845 | -55.3391 | -55.0735 | 66.6458 | -56.1951 | -55.9753 | -56.0852 | -56.2088 | -55.8929 | 0.004577 | 0.036621 | -0.11444 | 0.5722 | 0.8194 | 0.17395 | 0.81482 | 0.16937 | -0.036621 | 0.041199 | -122.58 | 0.073242 | 0.2655 | -0.050354 | 0.30212 | -0.013733 | 0.56763 | 122.644 | 0.10986 | 0.21973 | 122.7951 | 122.8409 | 122.7997 | 122.8043 | -122.7585 | -122.7997 | 122.6486 | 0.18311 | 2.5314 | 1.0849
2734.1719 | 123.0515 | -56.1356 | 66.5909 | -0.068207 | 0.0021171 | 0.063307 | 0.070113 | 0.00037377 | 0.0041143 | 0.0069172 | -0.059326 | 0.00067495 | 0.001068 | 0.0024096 | -0.0012925 | -0.0032301 | 0.00045294 | -53.6545 | 66.6183 | -56.1813 | 66.4536 | -55.6229 | -56.0028 | -55.3757 | -55.1056 | 66.6412 | -56.218 | -55.9616 | -56.0669 | -56.2134 | -55.8655 | -0.045776 | 0.027466 | -0.13733 | 0.5127 | 0.75989 | 0.13275 | 0.80566 | 0.17853 | -0.082398 | 0.050354 | -122.5525 | 0.068664 | 0.27008 | -0.07782 | 0.35248 | 0.004578 | 0.55847 | 122.6349 | 0.15106 | 0.25635 | 122.7997 | 122.8592 | 122.7539 | 122.7768 | -122.7722 | -122.8088 | 122.5891 | 0.17395 | 2.4811 | 1.03
2735.1719 | 123.0515 | -56.131 | 66.6183 | -0.10635 | -0.0010873 | 0.06053 | 0.070541 | 0.00016017 | 0.0030463 | 0.0079852 | -0.037964 | 0.0030249 | 0.00021363 | 0.0045458 | -0.0012925 | -0.0025891 | -0.0012561 | -53.6819 | 66.6229 | -56.1996 | 66.4627 | -55.6366 | -56.0211 | -55.3802 | -55.0781 | 66.6687 | -56.1722 | -55.9799 | -56.0761 | -56.2042 | -55.8609 | -0.068665 | 0.004578 | -0.15564 | 0.49438 | 0.75073 | 0.10986 | 0.8194 | 0.17853 | -0.041199 | 0.050354 | -122.5983 | 0.054931 | 0.27008 | -0.073243 | 0.31128 | -0.032044 | 0.56305 | 122.6624 | 0.09613 | 0.19226 | 122.8226 | 122.8409 | 122.7539 | 122.7997 | -122.818 | -122.7905 | 122.5937 | 0.15106 | 2.449 | 1.0529
2736.1719 | 123.0606 | -56.1584 | 66.6138 | -0.11398 | 0.0016899 | 0.061812 | 0.069259 | 0.0016556 | 0.0041143 | 0.0049946 | -0.053223 | 0.00024775 | 2.8e-08 | -0.00015378 | -0.0019333 | -0.0036573 | -0.0033923 | -53.6819 | 66.6367 | -56.1905 | 66.4444 | -55.6641 | -56.0349 | -55.4077 | -55.1468 | 66.6595 | -56.2042 | -55.9799 | -56.0944 | -56.2088 | -55.8929 | -0.032044 | 0.022888 | -0.16937 | 0.49439 | 0.75073 | 0.1236 | 0.78278 | 0.15564 | -0.045777 | 0.045776 | -122.5937 | 0.064087 | 0.2655 | -0.050354 | 0.31128 | -0.004577 | 0.52643 | 122.6349 | 0.10986 | 0.22431 | 122.8271 | 122.8638 | 122.7951 | 122.818 | -122.8043 | -122.818 | 122.6028 | 0.17853 | 2.4765 | 1.0117
2737.1719 | 123.0057 | -56.1264 | 66.6138 | -0.13687 | -0.0013009 | 0.063734 | 0.069686 | -0.0015488 | 0.0036871 | 0.005849 | -0.0013428 | 3.4148e-05 | 0.0021362 | 0.00048702 | -0.0019333 | -0.0057935 | 0.0015209 | -53.6499 | 66.6092 | -56.1493 | 66.4764 | -55.6046 | -55.9937 | -55.3528 | -55.1147 | 66.655 | -56.1676 | -55.9937 | -56.0944 | -56.1951 | -55.8975 | -0.022888 | -0.004578 | -0.13733 | 0.52185 | 0.77362 | 0.13275 | 0.79651 | 0.15564 | -0.041199 | 0.041198 | -122.6074 | 0.032044 | 0.22888 | -0.068664 | 0.27008 | -0.027465 | 0.54474 | 122.6257 | 0.073243 | 0.17395 | 122.7585 | 122.8226 | 122.7356 | 122.7814 | -122.7631 | -122.7814 | 122.6028 | 0.13275 | 2.4765 | 1.0117
2738.1719 | 123.0377 | -56.1172 | 66.6641 | -0.12161 | -0.00044654 | 0.061385 | 0.068618 | -0.00026703 | 0.0032599 | 0.00414 | 0.035278 | -0.00017945 | 0.0014954 | -0.0035718 | -0.00086511 | -0.0032301 | -0.00018806 | -53.6682 | 66.6504 | -56.1447 | 66.4764 | -55.6091 | -55.9891 | -55.3391 | -55.1056 | 66.6824 | -56.1951 | -55.9937 | -56.0761 | -56.1493 | -55.7739 | -0.027465 | -0.013733 | -0.18768 | 0.50812 | 0.7782 | 0.12817 | 0.80566 | 0.15564 | -0.077819 | 0.01831 | -122.6578 | 0.041199 | 0.34332 | -0.032043 | 0.42114 | 0.045776 | 0.53558 | 122.6212 | 0.11902 | 0.20142 | 122.7951 | 122.8775 | 122.7676 | 122.7997 | -122.8088 | -122.8592 | 122.5937 | 0.1236 | 2.449 | 1.0117
2739.1719 | 123.024 | -56.1218 | 66.6275 | -0.10635 | 0.0016899 | 0.061385 | 0.071181 | -0.0021896 | 0.0021917 | 0.0064898 | -0.059326 | 0.0011023 | 2.8e-08 | 0.0030506 | -0.0015061 | -0.0042981 | -0.0021107 | -53.6453 | 66.6412 | -56.163 | 66.4856 | -55.6274 | -55.9845 | -55.3619 | -55.101 | 66.6458 | -56.1768 | -55.9525 | -56.0577 | -56.2042 | -55.8563 | -0.041199 | 0.013733 | -0.14191 | 0.49439 | 0.75989 | 0.13733 | 0.80109 | 0.17853 | -0.054932 | 0.018311 | -122.58 | 0.064087 | 0.2655 | -0.082398 | 0.32043 | -0.027466 | 0.53558 | 122.6486 | 0.11902 | 0.2243 | 122.8043 | 122.8226 | 122.7631 | 122.7676 | -122.7905 | -122.8043 | 122.6074 | 0.16937 | 2.4765 | 1.0208
2740.1719 | 122.9691 | -56.1401 | 66.6916 | -0.1445 | 0.0010489 | 0.062025 | 0.073104 | 0.0029374 | 0.00026909 | 0.005849 | -0.034912 | 0.0013159 | 0.0025634 | -0.0048536 | -0.0025741 | -0.0049389 | 0.00045294 | -53.6728 | 66.6916 | -56.1584 | 66.4124 | -55.6824 | -56.0577 | -55.4169 | -55.1926 | 66.7099 | -56.1996 | -56.0349 | -56.131 | -56.2866 | -55.9341 | -0.01831 | 0 | -0.27923 | 0.45776 | 0.72327 | 0.082398 | 0.74158 | 0.10071 | -0.059509 | 0.018311 | -122.7264 | 0.009156 | 0.20599 | -0.14648 | 0.2655 | -0.086975 | 0.47607 | 122.5708 | 0.068665 | 0.16479 | 122.85 | 122.9095 | 122.8317 | 122.85 | -122.85 | -122.8912 | 122.5525 | 0.10529 | 2.4673 | 0.94757
2741.1719 | 123.0103 | -56.0989 | 66.6412 | -0.12924 | 0.0031851 | 0.061598 | 0.069259 | -5.343e-05 | 0.0034735 | 0.0045672 | -0.016602 | 0.00067495 | 0.001709 | -0.00058098 | -0.0027877 | -0.0040845 | 0.0010937 | -53.6087 | 66.6367 | -56.1172 | 66.5085 | -55.5542 | -55.9708 | -55.3299 | -55.0369 | 66.6412 | -56.1676 | -56.0028 | -55.957 | -56.012 | -55.7785 | -0.018311 | -0.004577 | -0.13275 | 0.54474 | 0.76904 | 0.12817 | 0.78735 | 0.14648 | -0.068665 | 0 | -122.644 | 0.14191 | 0.32043 | 0.086975 | 0.3891 | 0.15564 | 0.56305 | 122.6257 | 0.21057 | 0.16479 | 122.7539 | 122.8088 | 122.7356 | 122.7402 | -122.7585 | -122.8088 | 122.6074 | 0.09613 | 2.4902 | 1.062
2742.1719 | 123.0194 | -56.1127 | 66.6687 | -0.10635 | 0.00040806 | 0.060957 | 0.068191 | 0.00058737 | 0.0015509 | 0.0045672 | 0.0047608 | -0.00060665 | 0.001068 | 0.0024096 | -0.0023605 | -0.0045117 | 0.00066654 | -53.5858 | 66.6275 | -56.1081 | 66.5131 | -55.5496 | -55.9341 | -55.3116 | -55.0369 | 66.6641 | -56.1676 | -55.9341 | -56.0349 | -56.1539 | -55.838 | 0.004578 | -0.041199 | -0.15564 | 0.56305 | 0.80109 | 0.17853 | 0.79651 | 0.17395 | -0.054932 | -0.004577 | -122.6028 | 0.07782 | 0.27466 | -0.041199 | 0.32959 | 0.013733 | 0.55847 | 122.6212 | 0.13275 | 0.23346 | 122.7356 | 122.8317 | 122.7402 | 122.7768 | -122.7768 | -122.8363 | 122.6257 | 0.17853 | 2.5269 | 1.0757
2743.1719 | 122.9736 | -56.1218 | 66.6779 | -0.13687 | 0.00062166 | 0.06288 | 0.07289 | -0.0026168 | 0.0041143 | 0.0056354 | -0.074585 | -0.00017945 | 0.00042723 | 0.0026232 | -0.0023605 | -0.0042981 | 0.0010937 | -53.6728 | 66.6824 | -56.1401 | 66.4261 | -55.6824 | -56.0394 | -55.3986 | -55.1376 | 66.7282 | -56.1813 | -55.9891 | -56.0989 | -56.25 | -55.9204 | -0.018311 | 0.004578 | -0.25177 | 0.43945 | 0.72327 | 0.082397 | 0.74158 | 0.10071 | -0.059509 | 0.050354 | -122.6669 | 0.022888 | 0.20142 | -0.12817 | 0.26093 | -0.068665 | 0.45776 | 122.5662 | 0.082397 | 0.19226 | 122.8226 | 122.9095 | 122.8043 | 122.85 | -122.818 | -122.8592 | 122.5479 | 0.13275 | 2.449 | 0.98419
2744.1719 | 122.9782 | -56.131 | 66.655 | -0.098725 | 0.00083526 | 0.06053 | 0.072463 | 0.00251 | 0.0034735 | 0.0081988 | -0.062378 | 0.0025975 | 0.002777 | 0.0026232 | -0.0025741 | -0.0051527 | -0.0021107 | -53.6636 | 66.687 | -56.1447 | 66.4398 | -55.687 | -56.0394 | -55.4123 | -55.1514 | 66.7374 | -56.1584 | -56.0165 | -56.1035 | -56.2592 | -55.9021 | -0.013733 | 0.032044 | -0.21515 | 0.44403 | 0.71869 | 0.091552 | 0.73242 | 0.10529 | -0.027466 | 0.082398 | -122.6715 | 0.027465 | 0.22888 | -0.12817 | 0.25635 | -0.10071 | 0.45776 | 122.5845 | 0.054931 | 0.14191 | 122.8317 | 122.8958 | 122.818 | 122.8683 | -122.7997 | -122.8134 | 122.5708 | 0.11444 | 2.4673 | 0.97961
2745.1719 | 123.0423 | -56.0944 | 66.6779 | -0.15976 | -0.00066014 | 0.063094 | 0.070968 | 0.00080117 | 0.0015509 | 0.0096942 | -0.086792 | 3.4148e-05 | 0.00042723 | 0.00027342 | -0.0027877 | -0.0064343 | -0.0018971 | -53.595 | 66.6229 | -56.1218 | 66.5359 | -55.5542 | -55.9296 | -55.2933 | -55.014 | 66.6275 | -56.163 | -55.9113 | -56.012 | -56.131 | -55.8289 | -0.027466 | -0.054931 | -0.14191 | 0.54016 | 0.80109 | 0.1648 | 0.82855 | 0.19226 | -0.068665 | -0.050354 | -122.5891 | 0.082397 | 0.2655 | -0.036621 | 0.33417 | 0.032044 | 0.56763 | 122.6578 | 0.15106 | 0.25177 | 122.7448 | 122.7905 | 122.7173 | 122.7219 | -122.7997 | -122.8409 | 122.6303 | 0.18311 | 2.4994 | 1.0803
2746.1719 | 123.0469 | -56.0623 | 66.6641 | -0.12161 | -0.00066014 | 0.063734 | 0.067763 | -0.0024032 | 0.0034735 | 0.0054218 | -0.022705 | -0.00017945 | 0.0021362 | -0.003999 | -0.00043791 | -0.0030163 | -0.0014697 | -53.5904 | 66.6321 | -56.0989 | 66.5359 | -55.545 | -55.9341 | -55.307 | -55.0369 | 66.6824 | -56.1447 | -55.9341 | -55.8517 | -56.1218 | -55.806 | -0.036621 | -0.032044 | -0.12817 | 0.51727 | 0.75531 | 0.12817 | 0.79193 | 0.16479 | -0.082397 | 0.01831 | -122.5983 | 0.21057 | 0.25635 | -0.059509 | 0.33875 | 0.022888 | 0.55389 | 122.6349 | 0.29297 | 0.21057 | 122.731 | 122.8271 | 122.6944 | 122.7448 | -122.7631 | -122.8088 | 122.5983 | 0.12817 | 2.4719 | 1.0254
2747.1719 | 122.9736 | -56.1172 | 66.7099 | -0.52597 | 0.00062166 | 0.060316 | 0.070327 | 0.00037377 | 0.0028327 | 0.0056354 | -0.059326 | 0.0019567 | -0.0014954 | 0.0017688 | -0.0021469 | -0.0049389 | 0.00045294 | -53.5172 | 66.6824 | -56.1539 | 66.4307 | -55.6595 | -56.0349 | -55.4123 | -55.1559 | 66.7328 | -56.1401 | -56.012 | -56.1172 | -56.2546 | -55.9433 | -0.036621 | -0.027466 | -0.27924 | 0.45776 | 0.70496 | 0.082398 | 0.74158 | 0.11902 | -0.022888 | 0.022888 | -122.7219 | 0 | 0.17395 | -0.13733 | 0.19684 | -0.11444 | 0.49439 | 122.5845 | 0.022888 | 0.12817 | 122.8363 | 122.8729 | 122.7997 | 122.85 | -122.8638 | -122.85 | 122.5479 | 0.10529 | 2.6001 | 0.9613
2748.1719 | 123.0148 | -56.0944 | 66.6595 | -0.068207 | 0.00040806 | 0.062025 | 0.068191 | -0.0011214 | 0.0011237 | 0.00414 | 0.032227 | 0.00067495 | 0.0023498 | -0.0044262 | -0.0027877 | -0.0062207 | -0.0014697 | -53.6041 | 66.6824 | -56.0806 | 66.5222 | -55.5542 | -55.9296 | -55.2933 | -55.0278 | 66.6824 | -56.1447 | -55.957 | -56.044 | -56.131 | -55.8426 | 0.013733 | 0.022888 | -0.13733 | 0.54016 | 0.80109 | 0.1648 | 0.78735 | 0.15106 | -0.050354 | 0.022888 | -122.6166 | 0.050354 | 0.25177 | -0.036621 | 0.30212 | 0.013733 | 0.52643 | 122.6028 | 0.10071 | 0.18768 | 122.7631 | 122.8271 | 122.7768 | 122.7768 | -122.7402 | -122.8043 | 122.6166 | 0.13733 | 2.4902 | 1.0666
2749.1719 | 123.0286 | -56.1081 | 66.687 | -0.12924 | 0.0033987 | 0.063307 | 0.069259 | -0.0015488 | 0.0013373 | 0.0067036 | -0.019653 | 0.00067495 | 0.0014954 | -0.0016492 | -0.0030013 | -0.0038709 | -0.0025379 | -53.6545 | 66.6183 | -56.1127 | 66.5588 | -55.5176 | -55.8884 | -55.275 | -54.9911 | 66.7236 | -56.1127 | -55.9158 | -56.0028 | -56.131 | -55.8243 | -0.004578 | -0.068665 | -0.12817 | 0.59051 | 0.83313 | 0.21973 | 0.83771 | 0.2243 | -0.004578 | 0.036621 | -122.6028 | 0.10528 | 0.28381 | -0.022888 | 0.28839 | -0.01831 | 0.59509 | 122.6715 | 0.10986 | 0.19684 | 122.731 | 122.8363 | 122.7264 | 122.8317 | -122.7997 | -122.7997 | 122.6669 | 0.19226 | 2.4536 | 1.1169
2750.1719 | 123.0194 | -56.0761 | 66.687 | -0.10635 | -0.00044654 | 0.062453 | 0.068832 | 0.0027238 | 0.0032599 | 0.0060626 | -0.028809 | -0.00039305 | -0.00042717 | -0.0035718 | -0.0012925 | -0.0038709 | 0.00045294 | -53.6179 | 66.7053 | -56.0944 | 66.5039 | -55.5359 | -55.9204 | -55.3162 | -55.014 | 66.6962 | -56.0944 | -55.8929 | -56.0028 | -56.1401 | -55.8151 | -0.01831 | 0.01831 | -0.18311 | 0.54016 | 0.75989 | 0.15564 | 0.7782 | 0.17395 | -0.01831 | 0.009155 | -122.58 | 0.073242 | 0.26093 | -0.064087 | 0.27923 | -0.045777 | 0.55847 | 122.5983 | 0.091552 | 0.20142 | 122.7997 | 122.7905 | 122.7814 | 122.7722 | -122.7814 | -122.7814 | 122.58 | 0.18311 | 2.4582 | 1.062
2751.1719 | 122.9874 | -56.1172 | 66.7007 | -0.098725 | -0.00023294 | 0.060957 | 0.072036 | 0.00058737 | 0.0026191 | 0.003072 | -0.025757 | 0.0011023 | 0.0021362 | 0.0060412 | -0.0023605 | -0.0040845 | 0.0019483 | -53.6316 | 66.7191 | -56.1218 | 66.449 | -55.6458 | -56.0074 | -55.3848 | -55.1102 | 66.7465 | -56.1493 | -55.9708 | -56.0898 | -56.2363 | -55.8929 | -0.004577 | 0.01831 | -0.25177 | 0.4715 | 0.73242 | 0.10986 | 0.737 | 0.11444 | -0.032043 | 0.045776 | -122.6715 | 0.027466 | 0.22431 | -0.11902 | 0.25635 | -0.086975 | 0.47607 | 122.5708 | 0.059509 | 0.17853 | 122.8409 | 122.8958 | 122.8363 | 122.8638 | -122.8226 | -122.85 | 122.5662 | 0.14648 | 2.4857 | 1.0071
2752.1719 | 122.9599 | -56.1081 | 66.7282 | -0.10635 | -0.00023294 | 0.060957 | 0.069259 | -5.343e-05 | 0.0028327 | 0.0081988 | -0.062378 | 0.0021703 | 0.00042723 | 0.00070062 | -0.0021469 | -0.0040845 | 2.554e-05 | -53.6362 | 66.7145 | -56.1035 | 66.4581 | -55.6458 | -56.0211 | -55.3757 | -55.1285 | 66.7511 | -56.1539 | -55.9753 | -56.0989 | -56.2271 | -55.8838 | 0.004577 | -0.013732 | -0.27008 | 0.46234 | 0.73242 | 0.086975 | 0.72785 | 0.082398 | -0.045777 | 0.022889 | -122.7036 | 0.009155 | 0.2243 | -0.11902 | 0.27008 | -0.073242 | 0.45776 | 122.5616 | 0.054932 | 0.17853 | 122.818 | 122.905 | 122.8226 | 122.8592 | -122.8317 | -122.8821 | 122.5662 | 0.13275 | 2.4719 | 0.97961
2753.1719 | 123.0331 | -56.0715 | 66.7557 | 0.13779 | 0.00062166 | 0.061385 | 0.068618 | 0.001442 | 0.0015509 | 0.0054218 | 0.065796 | 0.00046135 | -0.00085457 | 0.0015552 | -0.00022431 | -0.0055799 | 0.00023934 | -53.7048 | 66.7557 | -55.9982 | 66.5955 | -55.4535 | -55.8243 | -55.1834 | -54.9362 | 66.7511 | -56.0623 | -55.8655 | -55.9296 | -56.0257 | -55.7922 | 0.073242 | 0 | -0.16022 | 0.61798 | 0.88806 | 0.24719 | 0.81482 | 0.17395 | 0.009155 | -0.004577 | -122.6212 | 0.14191 | 0.27924 | 0.045776 | 0.27008 | 0.036621 | 0.54474 | 122.5937 | 0.13275 | 0.19684 | 122.7539 | 122.8134 | 122.8271 | 122.8226 | -122.7539 | -122.818 | 122.6669 | 0.20599 | 2.3666 | 1.1353
2754.1719 | 123.0103 | -56.0669 | 66.7374 | -0.068207 | -0.0010873 | 0.062025 | 0.07225 | -0.0021896 | -0.0014399 | 0.005849 | -0.044067 | 0.0028113 | 0.00042723 | 0.0036914 | -0.0023605 | -0.0025891 | -0.00040166 | -53.5995 | 66.7282 | -56.0486 | 66.4902 | -55.6 | -55.9708 | -55.3391 | -55.0644 | 66.7236 | -56.1035 | -55.9067 | -55.9982 | -56.1493 | -55.8151 | 0.018311 | -0.009156 | -0.24719 | 0.46692 | 0.72785 | 0.096131 | 0.70953 | 0.07782 | -0.036621 | -0.013733 | -122.644 | 0.068665 | 0.25177 | -0.082397 | 0.28839 | -0.045776 | 0.44861 | 122.5388 | 0.10529 | 0.19684 | 122.7768 | 122.8271 | 122.7951 | 122.7905 | -122.7859 | -122.8409 | 122.5571 | 0.16022 | 2.4673 | 1.0025
2755.1719 | 123.0103 | -56.0761 | 66.7191 | -0.10635 | 0.0016899 | 0.061171 | 0.071822 | 0.0016556 | 0.0019781 | 0.0056354 | -0.022705 | -0.00060665 | 2.8e-08 | -0.00079478 | 0.00041649 | -0.0038709 | 0.0015209 | -53.627 | 66.7099 | -56.0577 | 66.4856 | -55.6 | -55.9708 | -55.3299 | -55.0644 | 66.7282 | -56.1218 | -55.9204 | -56.0257 | -56.1539 | -55.8243 | 0.018311 | -0.009155 | -0.23346 | 0.47607 | 0.74616 | 0.10529 | 0.72784 | 0.086975 | -0.045776 | 0.009155 | -122.6395 | 0.050354 | 0.25177 | -0.07782 | 0.29755 | -0.032044 | 0.45776 | 122.5433 | 0.09613 | 0.20142 | 122.7676 | 122.85 | 122.786 | 122.8043 | -122.7768 | -122.8409 | 122.5616 | 0.15564 | 2.449 | 1.0117
2756.1719 | 123.0057 | -56.0532 | 66.7694 | -0.091095 | 0.00062166 | 0.06053 | 0.067123 | -0.001976 | 0.0019781 | 0.003072 | 0.050537 | 0.00046135 | -0.00021357 | -0.00079478 | -0.00086511 | -0.0055799 | -0.0012561 | -53.5126 | 66.7511 | -55.9662 | 66.6 | -55.4489 | -55.8243 | -55.1926 | -54.9545 | 66.7877 | -56.0623 | -55.8746 | -55.9387 | -56.0486 | -55.7877 | 0.086975 | -0.01831 | -0.16937 | 0.60425 | 0.8606 | 0.22888 | 0.77362 | 0.14191 | -0.009155 | 0.018311 | -122.644 | 0.11444 | 0.2655 | 0.004578 | 0.27466 | 0.013733 | 0.51727 | 122.5662 | 0.1236 | 0.18768 | 122.7173 | 122.85 | 122.8043 | 122.8409 | -122.7356 | -122.8317 | 122.6532 | 0.17853 | 2.5406 | 1.0986
2757.1719 | 123.0606 | -56.0532 | 66.7191 | -0.13687 | -0.0013009 | 0.06288 | 0.069686 | 0.0018692 | 0.0034735 | 0.0045672 | 0.016968 | 0.00088875 | -0.001709 | -0.0016492 | -0.0021469 | -0.0040845 | -0.0025379 | -53.4622 | 66.7007 | -56.012 | 66.5817 | -55.4764 | -55.8975 | -55.2475 | -54.9545 | 66.7007 | -56.0761 | -55.8746 | -55.9753 | -56.0989 | -55.7739 | 0.041199 | -0.01831 | -0.13733 | 0.57678 | 0.80566 | 0.15564 | 0.76447 | 0.11444 | -0.022888 | -0.01831 | -122.5937 | 0.07782 | 0.27924 | -0.045776 | 0.30212 | -0.022888 | 0.53558 | 122.5937 | 0.10071 | 0.20142 | 122.7127 | 122.7768 | 122.7539 | 122.7539 | -122.731 | -122.7951 | 122.6349 | 0.17853 | 2.5909 | 1.0986
2758.1719 | 123.0148 | -56.0349 | 66.7603 | -0.11398 | -0.0030099 | 0.062666 | 0.069472 | -0.00026703 | 0.0039007 | 0.003072 | 0.029175 | 0.0015295 | -0.00021357 | -0.0016492 | -0.00086511 | -0.0045117 | 0.0017345 | -53.5858 | 66.7099 | -56.0165 | 66.5359 | -55.5313 | -55.8929 | -55.2567 | -55.0232 | 66.7648 | -56.0944 | -55.8838 | -55.9753 | -56.1401 | -55.7968 | 0.01831 | -0.050354 | -0.2243 | 0.50354 | 0.7782 | 0.14191 | 0.75989 | 0.1236 | -0.059509 | 0.004578 | -122.644 | 0.059509 | 0.23804 | -0.10529 | 0.29755 | -0.045777 | 0.48523 | 122.5525 | 0.11902 | 0.21057 | 122.7264 | 122.8592 | 122.7448 | 122.7997 | -122.7768 | -122.8546 | 122.5708 | 0.15106 | 2.449 | 1.0117
2759.1719 | 122.9828 | -56.0623 | 66.7557 | -0.083466 | -0.00023294 | 0.06053 | 0.073531 | -0.001976 | 0.0021917 | 0.0056354 | -0.028809 | 0.0030249 | 0.0038452 | -0.0018628 | -0.0038559 | -0.0034437 | -0.0010425 | -53.595 | 66.7557 | -56.044 | 66.5039 | -55.6229 | -55.9799 | -55.3345 | -55.0735 | 66.774 | -56.0989 | -55.9616 | -56.0715 | -56.1951 | -55.8472 | 0.018311 | 0 | -0.25177 | 0.43945 | 0.72784 | 0.082398 | 0.70953 | 0.064087 | -0.036621 | 0.018311 | -122.7173 | -0.009155 | 0.21515 | -0.13275 | 0.25177 | -0.09613 | 0.42114 | 122.5479 | 0.027466 | 0.13733 | 122.7997 | 122.8729 | 122.818 | 122.8363 | -122.7997 | -122.8546 | 122.5662 | 0.10071 | 2.4673 | 0.98877
2760.1719 | 123.024 | -56.0715 | 66.7099 | -0.17502 | -0.0021555 | 0.063734 | 0.070327 | 0.0010148 | -0.00037171 | 0.0062762 | -0.047119 | 0.0013159 | 0.001709 | 0.0051868 | -0.0023605 | -0.0034437 | -0.00082886 | -53.5904 | 66.7282 | -56.012 | 66.5268 | -55.5817 | -55.9387 | -55.3162 | -55.0323 | 66.7603 | -56.0852 | -55.8792 | -55.9799 | -56.1172 | -55.7877 | 0.059509 | 0.01831 | -0.18311 | 0.48981 | 0.75531 | 0.13275 | 0.6958 | 0.073242 | -0.013733 | 0.050354 | -122.5891 | 0.091553 | 0.28381 | -0.045777 | 0.29755 | -0.032044 | 0.4303 | 122.5388 | 0.10529 | 0.20599 | 122.7402 | 122.8455 | 122.7997 | 122.8317 | -122.7219 | -122.7951 | 122.5983 | 0.19226 | 2.4811 | 1.0391
2761.1719 | 123.0057 | -56.0532 | 66.7465 | -0.13687 | -0.00087374 | 0.061812 | 0.071395 | -0.0024032 | 0.0036871 | 0.0060626 | -0.037964 | 0.0023839 | 0.00064083 | -0.00058098 | -0.0027877 | -0.0040845 | -0.00082886 | -53.5858 | 66.7465 | -56.0303 | 66.5268 | -55.5908 | -55.957 | -55.307 | -55.0278 | 66.7969 | -56.0989 | -55.8975 | -56.0074 | -56.1218 | -55.806 | 0.022889 | 0 | -0.21973 | 0.46234 | 0.74616 | 0.096131 | 0.72327 | 0.073242 | -0.045776 | 0.050354 | -122.644 | 0.045777 | 0.24719 | -0.068664 | 0.29297 | -0.022888 | 0.43945 | 122.5571 | 0.091553 | 0.20142 | 122.7768 | 122.8958 | 122.7997 | 122.85 | -122.7768 | -122.8455 | 122.58 | 0.15564 | 2.4673 | 1.0254
2762.1719 | 122.9691 | -56.044 | 66.7511 | -0.068207 | 0.00062166 | 0.060744 | 0.070327 | 0.0010148 | 0.0013373 | 0.0062762 | -0.028809 | 0.00024775 | 0.00042723 | 0.0058276 | -0.0017197 | -0.0038709 | 0.0047253 | -53.5767 | 66.7786 | -56.0577 | 66.5131 | -55.5908 | -55.9479 | -55.3207 | -55.0507 | 66.8106 | -56.0852 | -55.9067 | -56.0211 | -56.163 | -55.8105 | -0.013733 | 0.027465 | -0.23804 | 0.45319 | 0.72327 | 0.09613 | 0.737 | 0.10986 | -0.041199 | 0.059509 | -122.6578 | 0.022888 | 0.23346 | -0.11902 | 0.27466 | -0.07782 | 0.46692 | 122.5708 | 0.064087 | 0.17853 | 122.8363 | 122.8958 | 122.8226 | 122.8546 | -122.8088 | -122.8363 | 122.5571 | 0.13733 | 2.4673 | 0.99335
2763.1719 | 122.9874 | -55.9937 | 66.7328 | -0.1445 | -0.00066014 | 0.062025 | 0.070113 | -0.001976 | 0.0024053 | 0.0077716 | 0.023071 | -0.0012477 | 0.00042723 | -0.002931 | -0.0012925 | -0.0038709 | -0.0027515 | -53.5263 | 66.7236 | -56.012 | 66.5771 | -55.4626 | -55.8517 | -55.2155 | -54.95 | 66.7557 | -56.0669 | -55.8701 | -55.9616 | -56.0852 | -55.7831 | -0.018311 | -0.009155 | -0.15564 | 0.53101 | 0.7782 | 0.14191 | 0.79651 | 0.16022 | -0.073243 | 0.022888 | -122.6028 | 0.032043 | 0.21057 | -0.091553 | 0.28381 | -0.01831 | 0.54932 | 122.5891 | 0.10529 | 0.19684 | 122.7356 | 122.8226 | 122.7173 | 122.7493 | -122.7448 | -122.7997 | 122.5708 | 0.1236 | 2.4673 | 1.0437
2764.1719 | 123.024 | -56.0303 | 66.7374 | -0.060578 | -0.0015145 | 0.061812 | 0.07225 | 0.0010148 | 0.0017645 | 0.0073444 | -0.034912 | 0.0011023 | 0.00085443 | 0.0051868 | -0.0027877 | -0.0030163 | 0.00023934 | -53.5583 | 66.7465 | -56.0623 | 66.5405 | -55.5359 | -55.9158 | -55.2795 | -55.014 | 66.774 | -56.0761 | -55.8517 | -55.9708 | -56.1172 | -55.7602 | -0.032044 | 0.009155 | -0.19684 | 0.49438 | 0.75073 | 0.11444 | 0.78278 | 0.14648 | -0.045777 | 0.036621 | -122.5891 | 0.059509 | 0.27008 | -0.086976 | 0.31586 | -0.041199 | 0.52643 | 122.6028 | 0.10529 | 0.2243 | 122.8088 | 122.85 | 122.7768 | 122.8043 | -122.7997 | -122.8134 | 122.5708 | 0.17853 | 2.4719 | 1.0162
2765.1719 | 123.0377 | -56.0211 | 66.7328 | -0.1445 | 0.0023307 | 0.06288 | 0.068404 | -0.0013352 | 0.00091009 | 0.00414 | -0.0074462 | 0.0013159 | 0.00064083 | 5.9824e-05 | -0.0036423 | -0.0030163 | -0.0010425 | -53.5126 | 66.7191 | -56.0028 | 66.6138 | -55.4489 | -55.838 | -55.2109 | -54.9271 | 66.7648 | -56.0623 | -55.8426 | -55.9296 | -56.0486 | -55.7419 | 0.01831 | -0.013733 | -0.11902 | 0.5722 | 0.81024 | 0.18311 | 0.79193 | 0.1648 | -0.041199 | 0.032044 | -122.5754 | 0.091553 | 0.27924 | -0.027466 | 0.32044 | 0.013733 | 0.55389 | 122.6166 | 0.13275 | 0.21973 | 122.7219 | 122.8271 | 122.7402 | 122.7859 | -122.7356 | -122.7951 | 122.6349 | 0.17853 | 2.5085 | 1.0941
2766.1719 | 122.8867 | -56.0623 | 66.7969 | -0.068207 | 0.00019446 | 0.063094 | 0.07225 | -0.0017624 | 0.0015509 | 0.0071308 | -0.08374 | 0.0011023 | -0.0014954 | 0.0032642 | -0.0023605 | -0.0019483 | -0.0046741 | -53.54 | 66.7877 | -56.0669 | 66.5222 | -55.5908 | -55.9341 | -55.2933 | -55.0827 | 66.8518 | -56.0715 | -55.9341 | -56.0806 | -56.2225 | -55.8655 | -0.004578 | -0.009155 | -0.27466 | 0.4715 | 0.76904 | 0.12817 | 0.77362 | 0.13275 | -0.009155 | 0.054932 | -122.731 | -0.01831 | 0.19684 | -0.16022 | 0.20599 | -0.15106 | 0.47608 | 122.5891 | -0.009155 | 0.13733 | 122.8546 | 122.9233 | 122.85 | 122.9141 | -122.8638 | -122.8683 | 122.5845 | 0.12817 | 2.5223 | 0.97961
2767.1719 | 122.9141 | -56.044 | 66.7831 | -0.068207 | -0.00087374 | 0.060103 | 0.070754 | -0.0026168 | 0.0034735 | 0.0073444 | -0.059326 | 0.0015295 | 0.00042723 | 0.0068958 | -0.0015061 | -0.0025891 | -0.00040166 | -53.5217 | 66.7465 | -56.0577 | 66.5314 | -55.5496 | -55.925 | -55.2887 | -55.0369 | 66.861 | -56.0852 | -55.9113 | -56.0623 | -56.1813 | -55.838 | -0.013733 | -0.036621 | -0.25177 | 0.49438 | 0.75531 | 0.11902 | 0.76904 | 0.13275 | -0.041199 | 0.07782 | -122.6944 | -0.018311 | 0.20599 | -0.13733 | 0.24719 | -0.09613 | 0.50812 | 122.5891 | 0.022888 | 0.17395 | 122.8043 | 122.9462 | 122.7905 | 122.905 | -122.8409 | -122.8683 | 122.5754 | 0.13275 | 2.5223 | 1.0071
2768.1719 | 122.9965 | -56.0028 | 66.7786 | -0.15976 | 0.0012625 | 0.063094 | 0.068618 | -0.003685 | 0.00091009 | 0.0054218 | 0.047485 | 0.00088875 | 2.8e-08 | -0.0027174 | -0.0017197 | -0.0064343 | -0.0025379 | -53.5263 | 66.7786 | -56.0165 | 66.5817 | -55.4764 | -55.8792 | -55.2063 | -54.982 | 66.7694 | -56.044 | -55.8655 | -55.9433 | -56.0623 | -55.7648 | -0.013733 | 0 | -0.19684 | 0.52643 | 0.79651 | 0.1236 | 0.81024 | 0.13733 | -0.041198 | -0.009155 | -122.644 | 0.05951 | 0.23804 | -0.059509 | 0.27923 | -0.018311 | 0.54016 | 122.5983 | 0.10071 | 0.17853 | 122.7951 | 122.8134 | 122.7814 | 122.7722 | -122.7951 | -122.8226 | 122.5845 | 0.13733 | 2.4765 | 1.0208
2769.1719 | 123.0011 | -56.012 | 66.7831 | -0.045319 | -0.0015145 | 0.063948 | 0.069686 | -0.0015488 | 0.0058233 | 0.0049946 | -0.034912 | 0.0011023 | -0.00021357 | -0.0033582 | -0.0034287 | -0.0038709 | 2.554e-05 | -53.5629 | 66.7923 | -56.044 | 66.5405 | -55.5542 | -55.925 | -55.275 | -55.014 | 66.8152 | -56.0486 | -55.8792 | -55.9845 | -56.1172 | -55.7785 | -0.032043 | 0.009155 | -0.24262 | 0.45776 | 0.737 | 0.086975 | 0.76904 | 0.11902 | -0.036621 | 0.032044 | -122.6624 | 0.027466 | 0.23346 | -0.10529 | 0.27008 | -0.068665 | 0.48981 | 122.5845 | 0.064087 | 0.16937 | 122.8363 | 122.8638 | 122.8043 | 122.8271 | -122.8271 | -122.8317 | 122.5525 | 0.13275 | 2.449 | 0.99793
2770.1719 | 122.9599 | -56.0165 | 66.7923 | -0.11398 | 0.0029715 | 0.061171 | 0.0699 | 0.0010148 | 0.0030463 | 0.0034992 | -0.022705 | 0.0011023 | 0.001709 | 0.0015552 | -0.0021469 | -0.0075025 | -0.0012561 | -53.5446 | 66.7923 | -56.0577 | 66.5451 | -55.5725 | -55.9204 | -55.2841 | -55.0095 | 66.8106 | -56.0577 | -55.8975 | -55.9937 | -56.1218 | -55.7831 | -0.041198 | 0 | -0.24719 | 0.44403 | 0.73242 | 0.096131 | 0.77362 | 0.13733 | -0.041198 | 0.018311 | -122.6898 | 0.022889 | 0.23346 | -0.10529 | 0.27466 | -0.064087 | 0.48523 | 122.6028 | 0.064087 | 0.16022 | 122.85 | 122.8683 | 122.8088 | 122.8271 | -122.85 | -122.85 | 122.5616 | 0.11902 | 2.4719 | 1.0071
2771.1719 | 122.905 | -55.9845 | 66.8335 | -0.12924 | 0.0010489 | 0.062025 | 0.071822 | 0.001442 | 0.0019781 | 0.007558 | -0.06543 | 0.0015295 | 0.00064083 | 0.0058276 | -0.0030013 | -0.0013073 | 0.0013073 | -53.5629 | 66.8152 | -56.0394 | 66.4993 | -55.6274 | -55.9433 | -55.3207 | -55.0735 | 66.8518 | -56.0623 | -56.1081 | -55.8289 | -55.925 | -55.7327 | -0.054932 | -0.01831 | -0.33417 | 0.35706 | 0.66376 | 0.041199 | 0.71869 | 0.096131 | -0.07782 | 0.018311 | -122.9416 | 0.15564 | 0.25177 | 0.059509 | 0.32959 | 0.13733 | 0.41199 | 122.5388 | 0.23346 | -0.045776 | 122.8546 | 122.9141 | 122.7997 | 122.8363 | -122.8729 | -122.8958 | 122.4838 | -0.1236 | 2.4216 | 0.91095
2772.1719 | 122.9233 | -55.9937 | 66.8289 | -0.091095 | 0.0023307 | 0.062666 | 0.070113 | -5.343e-05 | 0.0021917 | 0.0045672 | -0.059326 | 0.00088875 | -0.00042717 | 0.0017688 | -0.0019333 | -0.0051527 | 2.554e-05 | -53.4988 | 66.806 | -56.0074 | 66.6 | -55.4947 | -55.8746 | -55.2567 | -54.9911 | 66.8289 | -56.012 | -55.8975 | -55.9982 | -56.1401 | -55.8014 | -0.013733 | -0.022888 | -0.22888 | 0.49896 | 0.737 | 0.11902 | 0.75073 | 0.13275 | -0.018311 | 0 | -122.7264 | -0.004578 | 0.19226 | -0.14649 | 0.21057 | -0.12817 | 0.5127 | 122.6074 | 0.013733 | 0.11444 | 122.8134 | 122.8409 | 122.7997 | 122.8226 | -122.8363 | -122.8409 | 122.5937 | 0.09613 | 2.4948 | 1.0025
2773.1719 | 123.0194 | -55.9845 | 66.7923 | -0.15213 | 0.00040806 | 0.062666 | 0.067336 | -0.00069423 | 0.0034735 | 0.0064898 | 0.047485 | -0.00060665 | 0.0021362 | 0.00048702 | -0.0012925 | -0.0042981 | 0.0015209 | -53.4805 | 66.7969 | -55.9845 | 66.6412 | -55.4352 | -55.838 | -55.1743 | -54.9179 | 66.8198 | -56.0211 | -55.8289 | -55.9387 | -56.0486 | -55.7419 | 0 | 0.004578 | -0.15106 | 0.54932 | 0.81024 | 0.14648 | 0.81024 | 0.14648 | -0.036621 | 0.027466 | -122.6212 | 0.045776 | 0.24262 | -0.064087 | 0.27924 | -0.027466 | 0.54932 | 122.6257 | 0.082397 | 0.19226 | 122.7814 | 122.8409 | 122.7814 | 122.8043 | -122.7768 | -122.8134 | 122.6257 | 0.15564 | 2.504 | 1.0666
2774.1719 | 122.9279 | -55.9982 | 66.8243 | -0.083466 | 0.00019446 | 0.059889 | 0.070327 | 0.0010148 | 0.0015509 | 0.0056354 | -0.053223 | 0.00067495 | 0.001068 | 0.0051868 | -0.0027877 | -0.0036573 | 0.0017345 | -53.508 | 66.8289 | -56.0303 | 66.568 | -55.513 | -55.8884 | -55.2658 | -55.0186 | 66.8655 | -56.0257 | -55.9067 | -55.9891 | -56.1447 | -55.8151 | -0.032043 | 0.004577 | -0.25635 | 0.48523 | 0.73242 | 0.10986 | 0.76447 | 0.14191 | -0.027466 | 0.041199 | -122.731 | 0.009155 | 0.1831 | -0.14648 | 0.21057 | -0.11902 | 0.51727 | 122.5983 | 0.036621 | 0.11902 | 122.8592 | 122.8912 | 122.8271 | 122.8638 | -122.8546 | -122.85 | 122.5662 | 0.091553 | 2.4902 | 0.97961
2775.1719 | 122.9233 | -55.9982 | 66.8289 | -0.045319 | 0.0016899 | 0.062666 | 0.070541 | 0.0050736 | 0.00091009 | 0.0060626 | -0.037964 | -0.00039305 | 0.001709 | -0.0031446 | -0.00022431 | -0.0013073 | -0.0023243 | -53.4714 | 66.8472 | -55.9891 | 66.5817 | -55.4855 | -55.8563 | -55.2475 | -54.9957 | 66.8747 | -56.0028 | -55.8838 | -55.9891 | -56.1401 | -55.7831 | 0.009155 | 0.018311 | -0.24719 | 0.5127 | 0.75073 | 0.14191 | 0.74158 | 0.13275 | -0.004578 | 0.045777 | -122.7127 | 0.009155 | 0.21515 | -0.14191 | 0.21973 | -0.13733 | 0.50354 | 122.5708 | 0.013733 | 0.11902 | 122.8363 | 122.8775 | 122.8455 | 122.8729 | -122.818 | -122.8317 | 122.58 | 0.11444 | 2.5269 | 1.0025
2776.1719 | 122.9645 | -55.9662 | 66.8472 | -0.091095 | 0.00019446 | 0.060957 | 0.070541 | -0.0011214 | 0.0030463 | 0.0069172 | -0.03186 | 0.0025975 | 0.001068 | 0.001128 | -0.0025741 | -0.0036573 | 2.554e-05 | -53.4668 | 66.8243 | -56.0028 | 66.5955 | -55.4718 | -55.8289 | -55.2246 | -54.9545 | 66.8655 | -56.0165 | -55.8655 | -55.9753 | -56.0989 | -55.7831 | -0.036621 | -0.022888 | -0.25177 | 0.49439 | 0.74158 | 0.13733 | 0.7782 | 0.17395 | -0.050354 | 0.018311 | -122.7127 | -0.009155 | 0.18311 | -0.13275 | 0.23346 | -0.082397 | 0.53101 | 122.5983 | 0.041199 | 0.15106 | 122.8271 | 122.8821 | 122.7905 | 122.8317 | -122.85 | -122.8638 | 122.5616 | 0.10071 | 2.4994 | 1.0117
2777.1719 | 123.0652 | -55.9662 | 66.7969 | -0.12924 | -1.9142e-05 | 0.063734 | 0.071822 | 0.00080117 | 0.0021917 | 0.0071308 | -0.0013428 | 0.0015295 | 2.8e-08 | 0.00048702 | -0.00043791 | -0.0030163 | 2.554e-05 | -53.5034 | 66.7969 | -56.0211 | 66.6 | -55.4901 | -55.8517 | -55.2109 | -54.9271 | 66.8106 | -55.9937 | -55.8014 | -55.9021 | -56.0165 | -55.7007 | -0.054931 | 0 | -0.19684 | 0.47607 | 0.75531 | 0.11444 | 0.81024 | 0.16937 | -0.027465 | 0.013733 | -122.5983 | 0.064087 | 0.2655 | -0.050354 | 0.29297 | -0.022889 | 0.53101 | 122.6212 | 0.091552 | 0.19226 | 122.818 | 122.8043 | 122.7631 | 122.7768 | -122.818 | -122.7905 | 122.5662 | 0.16479 | 2.4628 | 1.0391
2778.1719 | 123.0469 | -55.9525 | 66.7923 | -0.15213 | 0.00019446 | 0.061598 | 0.068832 | 0.0012284 | 0.0030463 | 0.0026446 | 0.044434 | -0.00017945 | 0.00021363 | -0.0014356 | -0.0015061 | -0.0055799 | 0.00023934 | -53.4622 | 66.7831 | -55.9616 | 66.655 | -55.3986 | -55.7693 | -55.1422 | -54.8767 | 66.806 | -55.9708 | -55.7922 | -55.8655 | -56.0028 | -55.6824 | -0.009155 | -0.009155 | -0.13733 | 0.55389 | 0.81024 | 0.18311 | 0.8194 | 0.19226 | -0.01831 | 0.013733 | -122.5845 | 0.086975 | 0.27008 | -0.050354 | 0.28839 | -0.032044 | 0.56305 | 122.6166 | 0.10529 | 0.17853 | 122.7448 | 122.7768 | 122.7356 | 122.7585 | -122.7539 | -122.7631 | 122.6074 | 0.16022 | 2.4902 | 1.0757
2779.1719 | 122.9691 | -55.957 | 66.8655 | -0.091095 | -1.9142e-05 | 0.061598 | 0.071395 | 0.004219 | 0.0030463 | 0.007558 | -0.044067 | 0.00046135 | 0.00042723 | 0.00091422 | -0.0019333 | -0.0034437 | -0.00040166 | -53.4531 | 66.8472 | -55.9753 | 66.6229 | -55.4443 | -55.8105 | -55.2017 | -54.9179 | 66.8838 | -55.9845 | -55.8289 | -55.9662 | -56.0944 | -55.7602 | -0.018311 | -0.018311 | -0.24262 | 0.5127 | 0.75531 | 0.14648 | 0.77362 | 0.16479 | -0.027466 | 0.01831 | -122.6944 | -0.009156 | 0.19684 | -0.13733 | 0.2243 | -0.10986 | 0.53101 | 122.5983 | 0.01831 | 0.15564 | 122.8226 | 122.8683 | 122.8043 | 122.8409 | -122.8409 | -122.85 | 122.58 | 0.12817 | 2.504 | 1.0391
2780.1719 | 123.0515 | -55.9387 | 66.8381 | -0.12924 | 0.0012625 | 0.059462 | 0.068832 | 0.00016017 | 0.0026191 | 0.0067036 | 0.096313 | 0.0038793 | 0.0038452 | -0.0014356 | 0.00084389 | -0.0057935 | 0.0017345 | -53.4576 | 66.8335 | -55.9433 | 66.6641 | -55.394 | -55.7465 | -55.1056 | -54.8859 | 66.8564 | -55.9982 | -55.7785 | -55.8426 | -55.9662 | -55.6778 | -0.004577 | -0.004578 | -0.17395 | 0.54474 | 0.83313 | 0.19226 | 0.83771 | 0.19684 | -0.059509 | 0.01831 | -122.6166 | 0.096131 | 0.26093 | -0.027466 | 0.32043 | 0.032043 | 0.54932 | 122.6074 | 0.15564 | 0.21973 | 122.7768 | 122.8546 | 122.7722 | 122.7951 | -122.7814 | -122.8363 | 122.6028 | 0.16022 | 2.4811 | 1.0529
2781.1719 | 122.8912 | -55.9845 | 66.8701 | -0.17502 | 0.0027579 | 0.060957 | 0.070113 | -0.00026703 | 0.0026191 | 0.0045672 | -0.053223 | 0.0011023 | 0.00064083 | 0.0026232 | -0.0032151 | -0.0036573 | 0.0013073 | -53.4851 | 66.8747 | -55.9891 | 66.5909 | -55.5313 | -55.8838 | -55.2658 | -55.0232 | 66.8976 | -56.0165 | -55.8655 | -55.9982 | -56.163 | -55.7739 | -0.004578 | 0.004578 | -0.27924 | 0.45319 | 0.71869 | 0.10071 | 0.72327 | 0.10529 | -0.032044 | 0.027466 | -122.7356 | -0.013733 | 0.21057 | -0.17853 | 0.24261 | -0.14648 | 0.45776 | 122.58 | 0.018311 | 0.15106 | 122.8638 | 122.9141 | 122.8592 | 122.8821 | -122.8592 | -122.8867 | 122.5754 | 0.11902 | 2.4994 | 0.9613
2782.1719 | 122.8867 | -55.9616 | 66.861 | -0.060578 | -0.0013009 | 0.060744 | 0.070968 | 0.0020828 | 0.0034735 | 0.0062762 | -0.03186 | 0.0019567 | 0.003418 | -0.00079478 | -0.0021469 | -0.0053663 | -0.0025379 | -53.4302 | 66.8518 | -55.9387 | 66.6595 | -55.4398 | -55.7831 | -55.1651 | -54.895 | 66.9113 | -55.9662 | -55.806 | -55.8929 | -56.0257 | -55.5817 | 0.022888 | -0.009155 | -0.20142 | 0.52185 | 0.79651 | 0.17853 | 0.77362 | 0.15564 | -0.004578 | 0.050354 | -122.6669 | 0.068665 | 0.37994 | -0.064087 | 0.38452 | -0.059509 | 0.49896 | 122.5983 | 0.073243 | 0.16022 | 122.7905 | 122.8775 | 122.8134 | 122.8729 | -122.7997 | -122.8271 | 122.6212 | 0.15564 | 2.5314 | 1.0666
2783.1719 | 122.8958 | -55.9708 | 66.8701 | -0.075836 | 0.0021171 | 0.060744 | 0.069045 | 0.0018692 | 0.0021917 | 0.0077716 | -0.041016 | 0.0019567 | 0.001709 | 0.005614 | -0.0019333 | -0.0038709 | 2.554e-05 | -53.4897 | 66.8564 | -55.9845 | 66.5634 | -55.5588 | -55.8746 | -55.2383 | -55.0369 | 66.9022 | -55.9937 | -55.8838 | -55.9708 | -56.1127 | -55.7693 | -0.013733 | -0.013733 | -0.3067 | 0.41199 | 0.73242 | 0.09613 | 0.74615 | 0.10986 | -0.022888 | 0.032044 | -122.7539 | 0 | 0.20142 | -0.14191 | 0.2243 | -0.11902 | 0.42572 | 122.5479 | 0.022888 | 0.10986 | 122.8409 | 122.8958 | 122.8271 | 122.8729 | -122.8546 | -122.8638 | 122.5342 | 0.086975 | 2.4811 | 0.93384
2784.1719 | 122.9919 | -55.9387 | 66.861 | -0.0071715 | 0.0016899 | 0.058821 | 0.070327 | -0.00048063 | 0.00069649 | 0.00050839 | 0.0047608 | 0.0019567 | 0.00021363 | 0.0013416 | -0.00065151 | -0.0019483 | 0.00066654 | -53.4302 | 66.9205 | -55.9204 | 66.655 | -55.4306 | -55.7648 | -55.1605 | -54.8996 | 66.9342 | -55.957 | -55.7877 | -55.8884 | -56.012 | -55.6915 | 0.018311 | 0.059509 | -0.20599 | 0.50812 | 0.7782 | 0.17395 | 0.75989 | 0.15564 | -0.01831 | 0.073242 | -122.6486 | 0.050354 | 0.24719 | -0.073242 | 0.2655 | -0.054932 | 0.48981 | 122.5754 | 0.068664 | 0.16937 | 122.8409 | 122.8912 | 122.8592 | 122.8729 | -122.7814 | -122.818 | 122.5937 | 0.15106 | 2.5085 | 1.0391
2785.1719 | 123.0606 | -55.9067 | 66.8289 | -0.11398 | 0.00062166 | 0.061171 | 0.069472 | 0.0016556 | 0.0026191 | 0.0064898 | 0.0078126 | 0.00046135 | 0.002777 | 0.0043322 | -0.0027877 | -0.0057935 | 0.0021619 | -53.4576 | 66.8381 | -55.9753 | 66.6504 | -55.4306 | -55.7968 | -55.1559 | -54.8859 | 66.8472 | -55.9753 | -55.751 | -55.8609 | -55.9982 | -55.6503 | -0.068665 | 0.009156 | -0.17853 | 0.47607 | 0.75073 | 0.10986 | 0.8194 | 0.17853 | -0.068665 | 0.018311 | -122.58 | 0.045776 | 0.25635 | -0.091553 | 0.32501 | -0.022888 | 0.54474 | 122.6257 | 0.11444 | 0.2243 | 122.8134 | 122.8226 | 122.7448 | 122.7539 | -122.8043 | -122.8043 | 122.5571 | 0.15564 | 2.449 | 1.0208
2786.1719 | 122.9736 | -55.9158 | 66.8976 | -0.052948 | 0.00019446 | 0.06053 | 0.069686 | 0.001442 | 0.0015509 | 0.0067036 | -0.022705 | 0.0011023 | 0.0021362 | -0.00058098 | -0.00022431 | -0.0036573 | -0.0036059 | -53.4485 | 66.8655 | -55.9753 | 66.6595 | -55.4031 | -55.7693 | -55.1376 | -54.8859 | 66.8976 | -55.9341 | -55.7877 | -55.9113 | -56.0303 | -55.7144 | -0.059509 | -0.032043 | -0.23804 | 0.5127 | 0.7782 | 0.14648 | 0.83771 | 0.20599 | -0.01831 | 0 | -122.6852 | 0.004578 | 0.20142 | -0.11444 | 0.21973 | -0.09613 | 0.5722 | 122.6349 | 0.022888 | 0.14648 | 122.8409 | 122.8317 | 122.7814 | 122.8134 | -122.8729 | -122.8317 | 122.5754 | 0.12817 | 2.4673 | 1.03
2787.1719 | 122.8912 | -55.9708 | 66.8747 | -0.083466 | -0.00044654 | 0.062025 | 0.071181 | -0.0015488 | 0.0030463 | 0.0045672 | -0.034912 | 0.00046135 | 0.0021362 | 0.001128 | -0.0027877 | -0.0049389 | -0.00040166 | -53.4668 | 66.9067 | -55.9662 | 66.6046 | -55.5084 | -55.8655 | -55.2292 | -55.0095 | 66.9067 | -55.9937 | -55.8655 | -55.9799 | -56.1127 | -55.7785 | 0.004577 | 0.032043 | -0.27008 | 0.46234 | 0.74158 | 0.10529 | 0.737 | 0.10071 | -0.022888 | 0.032043 | -122.7402 | -0.009155 | 0.19226 | -0.14191 | 0.21515 | -0.11902 | 0.45776 | 122.5708 | 0.013733 | 0.12817 | 122.8729 | 122.9004 | 122.8775 | 122.8775 | -122.8409 | -122.8683 | 122.5754 | 0.10529 | 2.504 | 0.9613
2788.1719 | 123.0743 | -55.9158 | 66.8427 | -0.13687 | 0.0016899 | 0.062666 | 0.070113 | 0.0012284 | 0.0030463 | 0.0069172 | 0.016968 | 0.0015295 | -0.00042717 | -0.0031446 | -0.0010787 | -0.0042981 | -0.0044605 | -53.4805 | 66.8472 | -55.9341 | 66.6641 | -55.4123 | -55.7602 | -55.1422 | -54.8538 | 66.8655 | -55.9616 | -55.7281 | -55.8472 | -55.9662 | -55.6412 | -0.01831 | 0.004578 | -0.17853 | 0.50354 | 0.77362 | 0.15564 | 0.79193 | 0.17395 | -0.045776 | 0.022889 | -122.5708 | 0.068665 | 0.27466 | -0.050354 | 0.32044 | -0.004578 | 0.52185 | 122.5983 | 0.11444 | 0.23346 | 122.7814 | 122.8271 | 122.7631 | 122.7814 | -122.7768 | -122.8043 | 122.58 | 0.18768 | 2.4353 | 1.062
2789.1719 | 122.9828 | -55.9067 | 66.9022 | -0.03006 | 0.00062166 | 0.059676 | 0.070113 | -0.00048063 | 0.0030463 | 0.005849 | -0.016602 | 0.0013159 | 0.001709 | -0.00229 | -0.0025741 | -0.0051527 | -0.0014697 | -53.3981 | 66.9022 | -55.9616 | 66.6962 | -55.394 | -55.751 | -55.1285 | -54.8676 | 66.925 | -55.925 | -55.7693 | -55.8563 | -55.9891 | -55.6732 | -0.054932 | 0 | -0.20599 | 0.5127 | 0.7782 | 0.15564 | 0.83313 | 0.21057 | -0.018311 | 0.022888 | -122.6715 | 0.050354 | 0.23346 | -0.082398 | 0.25177 | -0.064087 | 0.56763 | 122.6578 | 0.068665 | 0.15564 | 122.8638 | 122.85 | 122.8088 | 122.8317 | -122.8638 | -122.8271 | 122.6028 | 0.13733 | 2.5085 | 1.0391
2790.1719 | 122.9691 | -55.8975 | 66.8701 | -0.075836 | 0.0019035 | 0.063094 | 0.066909 | -0.0041122 | 0.0032599 | 0.00414 | 0.068848 | 3.4148e-05 | 0.00021363 | -0.0025036 | -0.0023605 | -0.0057935 | 0.0021619 | -53.4393 | 66.8701 | -55.9204 | 66.687 | -55.3757 | -55.7556 | -55.1102 | -54.8447 | 66.8793 | -55.957 | -55.7602 | -55.8563 | -55.9662 | -55.6595 | -0.022888 | 0 | -0.1831 | 0.52185 | 0.78735 | 0.14191 | 0.81024 | 0.16479 | -0.059509 | 0.009155 | -122.6303 | 0.041199 | 0.23804 | -0.068665 | 0.29755 | -0.009156 | 0.54474 | 122.6074 | 0.10071 | 0.19684 | 122.7905 | 122.8363 | 122.7676 | 122.7768 | -122.7905 | -122.8271 | 122.5845 | 0.13733 | 2.4582 | 1.0529
2791.1719 | 122.9599 | -55.9158 | 66.9159 | -0.045319 | 0.00083526 | 0.061171 | 0.0699 | 0.00016017 | 0.00026909 | 0.007558 | 0.0078126 | 0.0019567 | 0.003418 | 0.0086048 | -0.0021469 | -0.0064343 | 0.00088014 | -53.4119 | 66.9296 | -55.9341 | 66.7053 | -55.3802 | -55.7373 | -55.1193 | -54.8538 | 66.9388 | -55.9067 | -55.7693 | -55.8655 | -55.9845 | -55.6778 | -0.01831 | 0.013732 | -0.21057 | 0.53558 | 0.79651 | 0.17853 | 0.81482 | 0.19684 | 0.009156 | 0.022888 | -122.6852 | 0.050354 | 0.23804 | -0.068664 | 0.22888 | -0.07782 | 0.55389 | 122.6395 | 0.041198 | 0.13733 | 122.8638 | 122.8455 | 122.8455 | 122.8546 | -122.85 | -122.8226 | 122.6212 | 0.14648 | 2.504 | 1.062
2792.1719 | 122.937 | -55.8975 | 66.9479 | -0.11398 | -0.0017281 | 0.059248 | 0.0699 | 0.0010148 | 0.0024053 | 0.0084124 | 0.001709 | 0.0015295 | 0.0023498 | -0.0027174 | -0.0015061 | -0.0042981 | -0.00040166 | -53.4119 | 66.9342 | -55.9296 | 66.6687 | -55.4169 | -55.7602 | -55.1376 | -54.9179 | 66.9479 | -55.9387 | -55.8014 | -55.8701 | -56.0165 | -55.6961 | -0.032043 | -0.013733 | -0.27924 | 0.48065 | 0.75989 | 0.13733 | 0.79193 | 0.16937 | -0.041199 | 0 | -122.7493 | 0.027466 | 0.20142 | -0.11902 | 0.24262 | -0.07782 | 0.51269 | 122.5983 | 0.068665 | 0.13733 | 122.8638 | 122.8867 | 122.8317 | 122.8455 | -122.8775 | -122.8867 | 122.5662 | 0.09613 | 2.4857 | 0.97961
2793.1719 | 122.9828 | -55.8975 | 66.9205 | -0.022431 | 0.00040806 | 0.062666 | 0.069045 | 0.0012284 | 0.0034735 | 0.0067036 | -0.044067 | 0.00024775 | 0.00085443 | 0.0013416 | -0.0036423 | -0.0049389 | -0.0031787 | -53.3752 | 66.9067 | -55.925 | 66.7099 | -55.3802 | -55.7465 | -55.1285 | -54.8492 | 66.9525 | -55.9341 | -55.7648 | -55.8746 | -56.0074 | -55.6961 | -0.027466 | -0.013733 | -0.21057 | 0.51727 | 0.76904 | 0.15106 | 0.79651 | 0.17853 | -0.036621 | 0.032044 | -122.6852 | 0.022888 | 0.20142 | -0.10986 | 0.23804 | -0.073242 | 0.54474 | 122.6349 | 0.059509 | 0.16937 | 122.8317 | 122.8867 | 122.8043 | 122.85 | -122.8455 | -122.8546 | 122.6074 | 0.13275 | 2.5223 | 1.0483
2794.1719 | 122.9874 | -55.8884 | 66.9205 | -0.075836 | 0.0010489 | 0.061171 | 0.070541 | 0.0010148 | 0.0011237 | 0.0060626 | -0.0074462 | 0.0023839 | 0.001068 | 0.0019824 | 0.00084389 | -0.0040845 | -0.0018971 | -53.3661 | 66.925 | -55.9113 | 66.6962 | -55.3802 | -55.7281 | -55.1147 | -54.8447 | 66.9434 | -55.9158 | -55.751 | -55.838 | -55.9662 | -55.6595 | -0.022888 | 0.004578 | -0.2243 | 0.50812 | 0.77362 | 0.16022 | 0.79651 | 0.18311 | -0.027466 | 0.022888 | -122.6715 | 0.050354 | 0.22888 | -0.07782 | 0.25635 | -0.050354 | 0.53101 | 122.6074 | 0.07782 | 0.16479 | 122.8363 | 122.8592 | 122.8134 | 122.8317 | -122.8317 | -122.8363 | 122.5845 | 0.13733 | 2.5223 | 1.0437
2795.1719 | 122.9965 | -55.8838 | 66.8838 | -0.098725 | 0.00019446 | 0.062239 | 0.069686 | -0.0024032 | 0.00091009 | 0.0039264 | 0.026123 | 0.0011023 | 0.00042723 | -0.0016492 | -0.0019333 | -0.0051527 | -0.0031787 | -53.4027 | 66.8427 | -55.8975 | 66.7236 | -55.3482 | -55.7281 | -55.0781 | -54.808 | 66.8701 | -55.9387 | -55.7281 | -55.8426 | -55.9525 | -55.6549 | -0.013733 | -0.041199 | -0.16022 | 0.53558 | 0.80566 | 0.15564 | 0.8194 | 0.16937 | -0.054932 | -0.013733 | -122.612 | 0.041199 | 0.22888 | -0.068665 | 0.28381 | -0.013733 | 0.54932 | 122.6212 | 0.096131 | 0.21057 | 122.7402 | 122.8088 | 122.7264 | 122.7539 | -122.7814 | -122.8226 | 122.6074 | 0.15564 | 2.4811 | 1.0757
2796.1719 | 122.9324 | -55.9113 | 66.9617 | -0.083466 | -1.9142e-05 | 0.059035 | 0.070754 | 0.00037377 | 0.0032599 | 0.0062762 | 0.016968 | 0.0019567 | 0.00042723 | -0.0061352 | -0.00086511 | -0.0051527 | -0.0031787 | -53.389 | 66.9708 | -55.8975 | 66.6733 | -55.394 | -55.7236 | -55.1102 | -54.8721 | 66.9891 | -55.9113 | -55.7831 | -55.8701 | -55.9982 | -55.6595 | 0.013733 | 0.009155 | -0.28839 | 0.51727 | 0.80109 | 0.18768 | 0.78735 | 0.17395 | 0 | 0.027466 | -122.7448 | 0.041199 | 0.25177 | -0.086975 | 0.25177 | -0.086975 | 0.50354 | 122.5708 | 0.041199 | 0.12817 | 122.8683 | 122.9004 | 122.8821 | 122.9004 | -122.8592 | -122.8729 | 122.5845 | 0.12817 | 2.5223 | 1.0391
2797.1719 | 122.9919 | -55.8746 | 66.9479 | -0.045319 | 0.0016899 | 0.061812 | 0.073104 | 0.00486 | 0.0026191 | 0.0069172 | 0.001709 | 0.00067495 | 0.0012818 | 0.0026232 | -0.0025741 | -0.0032301 | 0.00045294 | -53.3524 | 66.9662 | -55.9158 | 66.7099 | -55.3665 | -55.7098 | -55.1147 | -54.8126 | 66.9571 | -55.9021 | -55.7373 | -55.8334 | -55.9708 | -55.6503 | -0.041199 | 0.018311 | -0.23804 | 0.50812 | 0.75989 | 0.16479 | 0.80109 | 0.20599 | -0.027466 | 0.009155 | -122.6852 | 0.041199 | 0.2243 | -0.09613 | 0.25177 | -0.068664 | 0.54932 | 122.6257 | 0.068665 | 0.16479 | 122.8821 | 122.8592 | 122.8409 | 122.8317 | -122.8638 | -122.85 | 122.5845 | 0.13733 | 2.5223 | 1.062
2798.1719 | 122.9279 | -55.8884 | 66.9342 | -0.12924 | 0.0014761 | 0.062025 | 0.069686 | 0.0040054 | 0.0013373 | 0.007558 | -0.0074462 | 0.0013159 | 0.0025634 | -0.00229 | -0.0025741 | -0.0062207 | -0.00061526 | -53.5263 | 66.8701 | -55.9525 | 66.6458 | -55.4031 | -55.8289 | -55.1605 | -54.9362 | 66.9388 | -55.9296 | -55.8014 | -55.8929 | -56.0394 | -55.7053 | -0.064087 | -0.064087 | -0.28839 | 0.48523 | 0.72785 | 0.05951 | 0.79193 | 0.1236 | -0.041198 | 0.004578 | -122.7356 | -0.004577 | 0.18311 | -0.15106 | 0.2243 | -0.10986 | 0.54932 | 122.5983 | 0.036621 | 0.12817 | 122.8226 | 122.8683 | 122.7585 | 122.8271 | -122.8867 | -122.8638 | 122.5342 | 0.086975 | 2.3621 | 0.95215
2799.1719 | 122.9233 | -55.8975 | 66.9434 | -0.03006 | 0.0014761 | 0.062453 | 0.070968 | 0.0018692 | 0.0021917 | 0.0056354 | -0.041016 | 0.00088875 | 0.00085443 | 0.0041186 | -0.0010787 | -0.0028027 | -0.0029651 | -53.3661 | 66.9571 | -55.8929 | 66.7007 | -55.3711 | -55.7327 | -55.1239 | -54.8355 | 66.9846 | -55.9296 | -55.7556 | -55.8746 | -56.0074 | -55.6915 | 0.004578 | 0.013733 | -0.24261 | 0.52643 | 0.77362 | 0.1648 | 0.76904 | 0.16022 | -0.032043 | 0.041199 | -122.699 | 0.022888 | 0.20599 | -0.10986 | 0.23804 | -0.07782 | 0.52185 | 122.5937 | 0.054931 | 0.17395 | 122.85 | 122.9141 | 122.8546 | 122.8821 | -122.8363 | -122.8729 | 122.5983 | 0.14191 | 2.5314 | 1.062
2800.1719 | 122.9233 | -55.8746 | 66.9891 | -0.014801 | -0.00023294 | 0.063094 | 0.06755 | 0.00016017 | 0.0045417 | 0.0047808 | 0.050537 | 0.0021703 | 0.0029906 | -0.00036738 | -1.0706e-05 | -0.0045117 | -0.00018806 | -53.389 | 66.9983 | -55.8884 | 66.5588 | -55.3757 | -55.7098 | -55.1468 | -54.8813 | 66.9891 | -55.9204 | -55.7693 | -55.8563 | -55.9753 | -55.6732 | -0.013733 | 0.009155 | -0.4303 | 0.49896 | 0.72784 | 0.16479 | 0.74158 | 0.17853 | -0.045776 | 0 | -122.7585 | 0.018311 | 0.20142 | -0.10071 | 0.24719 | -0.054932 | 0.5127 | 122.4472 | 0.064087 | 0.15106 | 122.8867 | 122.9095 | 122.8729 | 122.8638 | -122.8775 | -122.9095 | 122.4335 | 0.10529 | 2.4857 | 0.99335
2801.1719 | 122.9599 | -55.8609 | 66.9937 | -0.037689 | -0.0010873 | 0.062025 | 0.07225 | 0.0022964 | 0.0030463 | 0.0054218 | 0.001709 | 0.00067495 | 2.8e-08 | 0.0013416 | -0.0021469 | -0.0038709 | -0.00082886 | -53.3386 | 66.9662 | -55.9113 | 66.7328 | -55.3528 | -55.6961 | -55.0919 | -54.8218 | 66.9983 | -55.8838 | -55.719 | -55.8197 | -55.9479 | -55.632 | -0.050354 | -0.027465 | -0.26093 | 0.50812 | 0.76904 | 0.16479 | 0.8194 | 0.21515 | -0.022888 | 0.004578 | -122.7127 | 0.041199 | 0.22888 | -0.086975 | 0.25177 | -0.064087 | 0.55847 | 122.644 | 0.064087 | 0.16479 | 122.8775 | 122.8821 | 122.8271 | 122.8592 | -122.905 | -122.8775 | 122.5937 | 0.14191 | 2.5223 | 1.0391
2802.1719 | 122.9553 | -55.8517 | 67.0395 | -0.091095 | -0.0010873 | 0.062239 | 0.069472 | 0.00037377 | 0.00026909 | 0.0034992 | 0.010864 | 0.0013159 | 0.0012818 | -0.0044262 | 0.00084389 | -0.0057935 | -0.0048877 | -53.3707 | 66.9754 | -55.8838 | 66.7282 | -55.3665 | -55.7053 | -55.069 | -54.8447 | 67.0074 | -55.8884 | -55.7648 | -55.8243 | -55.9479 | -55.6595 | -0.032043 | -0.064087 | -0.31128 | 0.48523 | 0.78278 | 0.14648 | 0.81482 | 0.17853 | -0.036621 | -0.032044 | -122.8043 | 0.027466 | 0.19226 | -0.09613 | 0.22888 | -0.059509 | 0.51727 | 122.612 | 0.064087 | 0.1236 | 122.8592 | 122.8958 | 122.8271 | 122.8592 | -122.9233 | -122.9279 | 122.58 | 0.086975 | 2.4811 | 1.0071
2803.1719 | 123.0057 | -55.8929 | 66.9891 | -0.11398 | 0.00062166 | 0.063094 | 0.0699 | 0.0018692 | 0.0017645 | 0.0067036 | -0.037964 | 0.0011023 | -0.00085457 | 0.001128 | -0.0019333 | -0.0025891 | -0.0059559 | -53.3936 | 66.9388 | -55.925 | 66.6321 | -55.4718 | -55.7968 | -55.1788 | -54.9316 | 66.9754 | -55.925 | -55.7236 | -56.1813 | -56.0349 | -55.5588 | -0.032044 | -0.050354 | -0.35706 | 0.42114 | 0.71411 | 0.09613 | 0.74616 | 0.12817 | -0.032044 | -0.013733 | -122.7127 | -0.28839 | 0.33417 | -0.14191 | 0.36621 | -0.10986 | 0.45319 | 122.5571 | -0.25635 | 0.20142 | 122.8638 | 122.9004 | 122.8317 | 122.8683 | -122.9141 | -122.9141 | 122.525 | 0.16937 | 2.4994 | 0.9613
2804.1719 | 122.9187 | -55.8517 | 67.0074 | -0.068207 | -0.00087374 | 0.062239 | 0.069045 | -0.005394 | 0.0015509 | 0.0026446 | 0.010864 | 0.0017431 | 0.0012818 | -0.00079478 | -0.00086511 | -0.0057935 | -0.0031787 | -53.3707 | 66.9891 | -55.8929 | 66.7053 | -55.3619 | -55.6961 | -55.0827 | -54.7943 | 67.0486 | -55.8426 | -55.7785 | -55.8289 | -55.9616 | -55.6549 | -0.041198 | -0.01831 | -0.30212 | 0.48981 | 0.76904 | 0.15564 | 0.81024 | 0.19684 | 0.009156 | 0.041199 | -122.7859 | 0.022889 | 0.19684 | -0.10986 | 0.18768 | -0.11902 | 0.53101 | 122.5983 | 0.013733 | 0.064087 | 122.8821 | 122.8912 | 122.8409 | 122.9004 | -122.9004 | -122.85 | 122.5571 | 0.073243 | 2.4811 | 1.0574
2805.1719 | 122.9324 | -55.8472 | 66.9983 | -0.037689 | -0.00044654 | 0.061385 | 0.067336 | -0.0021896 | 0.0024053 | 0.0062762 | 0.0047608 | 0.0011023 | 0.00064083 | -0.001222 | -0.0025741 | -0.0057935 | 0.0013073 | -53.3615 | 66.9937 | -55.8884 | 66.7236 | -55.3894 | -55.6915 | -55.0827 | -54.8492 | 67.0349 | -55.8838 | -55.7327 | -55.8151 | -55.9525 | -55.6366 | -0.041199 | -0.004578 | -0.27466 | 0.45776 | 0.76447 | 0.15564 | 0.80566 | 0.19684 | -0.036621 | 0.036621 | -122.731 | 0.032043 | 0.21057 | -0.10529 | 0.24719 | -0.068665 | 0.49896 | 122.612 | 0.068664 | 0.15106 | 122.8821 | 122.9187 | 122.8409 | 122.8821 | -122.8867 | -122.8821 | 122.5708 | 0.11444 | 2.4857 | 0.99793
2806.1719 | 122.9324 | -55.8334 | 66.9846 | -0.075836 | -0.00044654 | 0.060103 | 0.069686 | -0.001976 | 0.0019781 | 0.0064898 | 0.03833 | 0.0023839 | 0.0032044 | -0.003999 | -0.0017197 | -0.0049389 | 0.0019483 | -53.3112 | 67.0166 | -55.8655 | 66.7511 | -55.3345 | -55.6686 | -55.0552 | -54.808 | 67.0029 | -55.8701 | -55.7419 | -55.8289 | -55.9525 | -55.6503 | -0.032044 | 0.032044 | -0.23346 | 0.49896 | 0.7782 | 0.16479 | 0.81024 | 0.19684 | -0.036621 | 0.018311 | -122.7264 | 0.004578 | 0.18311 | -0.11902 | 0.21973 | -0.082398 | 0.53101 | 122.6166 | 0.041199 | 0.12817 | 122.8821 | 122.8729 | 122.85 | 122.8363 | -122.85 | -122.8546 | 122.5845 | 0.091553 | 2.5223 | 1.0254
2807.1719 | 122.9782 | -55.8701 | 67.0074 | -0.022431 | -0.00044654 | 0.061598 | 0.071609 | 0.00058737 | 0.0021917 | 0.0064898 | -0.022705 | 0.0015295 | 0.0014954 | 5.9824e-05 | -0.0012925 | -0.0049389 | 0.0021619 | -53.3157 | 66.9983 | -55.8746 | 66.7557 | -55.3299 | -55.6595 | -55.0552 | -54.7806 | 66.9983 | -55.8701 | -55.6915 | -55.8151 | -55.925 | -55.6137 | -0.004578 | -0.009155 | -0.25177 | 0.54016 | 0.81482 | 0.21057 | 0.8194 | 0.21515 | 0 | -0.009155 | -122.699 | 0.054931 | 0.25635 | -0.054932 | 0.25635 | -0.054932 | 0.54474 | 122.6303 | 0.054931 | 0.17853 | 122.8729 | 122.8683 | 122.8683 | 122.8683 | -122.8821 | -122.8775 | 122.6257 | 0.17853 | 2.5543 | 1.0895
2808.1719 | 122.937 | -55.8609 | 66.9846 | -0.091095 | 0.00019446 | 0.060744 | 0.072463 | -0.00048063 | 0.0030463 | 0.0049946 | -0.041016 | -0.0010339 | 0.0023498 | 0.002196 | -0.00065151 | -0.0040845 | 0.0017345 | -53.3478 | 66.9754 | -55.9021 | 66.7007 | -55.394 | -55.7556 | -55.1376 | -54.8676 | 67.012 | -55.8975 | -55.7648 | -55.8517 | -56.0028 | -55.6778 | -0.041199 | -0.009155 | -0.28381 | 0.46692 | 0.72327 | 0.10529 | 0.76447 | 0.14648 | -0.036621 | 0.027466 | -122.7493 | 0.009155 | 0.18311 | -0.14191 | 0.21973 | -0.10529 | 0.50812 | 122.6028 | 0.045776 | 0.13275 | 122.8775 | 122.9095 | 122.8363 | 122.8729 | -122.8867 | -122.8821 | 122.5616 | 0.09613 | 2.5131 | 0.99335
2809.1719 | 123.0103 | -55.8197 | 66.9846 | -0.068207 | -1.9142e-05 | 0.060103 | 0.069472 | -0.0028304 | 0.00091009 | 0.0043536 | 0.053589 | 0.00088875 | 0.0012818 | 0.00048702 | -0.0027877 | -0.0047253 | 0.00045294 | -53.2791 | 66.9525 | -55.8105 | 66.8243 | -55.2475 | -55.5817 | -54.9545 | -54.6982 | 66.9937 | -55.8472 | -55.6549 | -55.719 | -55.8426 | -55.5634 | 0.009155 | -0.032043 | -0.16022 | 0.5722 | 0.86517 | 0.23804 | 0.85602 | 0.22888 | -0.027466 | 0.009155 | -122.6395 | 0.10071 | 0.25635 | -0.022888 | 0.28381 | 0.004578 | 0.56305 | 122.6349 | 0.12817 | 0.19226 | 122.7631 | 122.8409 | 122.7722 | 122.8134 | -122.7951 | -122.8317 | 122.644 | 0.16479 | 2.5406 | 1.1215
2810.1719 | 123.0194 | -55.8105 | 66.9983 | -0.12161 | -0.00066014 | 0.060103 | 0.069472 | -0.0030442 | 0.00069649 | 0.0054218 | 0.047485 | 0.0013159 | 0.00085443 | 0.0015552 | -0.0025741 | -0.0060071 | 0.00088014 | -53.2562 | 66.9708 | -55.8197 | 66.8518 | -55.2017 | -55.5634 | -54.9591 | -54.6844 | 66.9754 | -55.8426 | -55.6229 | -55.6778 | -55.8105 | -55.5496 | -0.009155 | -0.027466 | -0.14648 | 0.60883 | 0.85144 | 0.24719 | 0.8606 | 0.25635 | -0.032043 | -0.022888 | -122.6212 | 0.13275 | 0.26093 | 0 | 0.29297 | 0.032043 | 0.61798 | 122.6715 | 0.16479 | 0.21973 | 122.7905 | 122.818 | 122.7814 | 122.7859 | -122.818 | -122.8409 | 122.6624 | 0.18768 | 2.5543 | 1.1261
2811.1719 | 122.9874 | -55.7877 | 67.012 | -0.03006 | -0.0013009 | 0.061171 | 0.070327 | 0.0027238 | 0.0036871 | 0.0047808 | -0.0043946 | -0.0012477 | -0.0010682 | -0.0031446 | -0.0038559 | -0.0021619 | 0.0049389 | -53.3203 | 67.0303 | -55.8563 | 66.7648 | -55.3482 | -55.6503 | -55.0507 | -54.7714 | 67.0395 | -55.838 | -55.7007 | -55.7785 | -55.8975 | -55.5908 | -0.068664 | 0.01831 | -0.24719 | 0.43945 | 0.737 | 0.13733 | 0.80566 | 0.20599 | -0.050354 | 0.027466 | -122.7127 | 0.009156 | 0.19684 | -0.10986 | 0.24719 | -0.059509 | 0.50812 | 122.6212 | 0.05951 | 0.13733 | 122.8867 | 122.8775 | 122.818 | 122.8271 | -122.8683 | -122.85 | 122.5525 | 0.086975 | 2.4673 | 1.0162
2812.1719 | 122.9553 | -55.8197 | 67.0166 | 0.015716 | -1.9142e-05 | 0.059248 | 0.068618 | 0.0020828 | 0.0026191 | 0.0017902 | 0.016968 | 0.0021703 | 0.0032044 | 0.0019824 | -0.0038559 | -0.0049389 | 0.00088014 | -53.3203 | 67.0395 | -55.838 | 66.9388 | -55.3253 | -55.8792 | -55.1605 | -54.8447 | 67.0486 | -55.8563 | -55.7053 | -55.7922 | -55.9296 | -55.632 | -0.018311 | 0.022888 | -0.07782 | 0.49439 | 0.65918 | -0.059509 | 0.67749 | -0.041198 | -0.036621 | 0.032043 | -122.7219 | 0.027466 | 0.18768 | -0.10986 | 0.2243 | -0.073242 | 0.5127 | 122.7768 | 0.064087 | 0.15106 | 122.8775 | 122.905 | 122.8592 | 122.8683 | -122.8546 | -122.8729 | 122.7585 | 0.11444 | 2.4994 | 0.97504
2813.1719 | 122.9233 | -55.7968 | 67.0441 | -0.068207 | -0.0027963 | 0.06053 | 0.0699 | 0.0035782 | 0.0032599 | 0.0028582 | -0.0043946 | 0.00067495 | 0.0025634 | -0.0016492 | -0.00043791 | -0.0034437 | -0.0042469 | -53.3066 | 67.0303 | -55.8472 | 66.7419 | -55.3528 | -55.6503 | -55.0507 | -54.8035 | 67.0624 | -55.8655 | -55.6961 | -55.7693 | -55.9067 | -55.6137 | -0.050354 | -0.013733 | -0.30212 | 0.44403 | 0.74615 | 0.14648 | 0.79651 | 0.19684 | -0.068665 | 0.018311 | -122.7402 | 0.027466 | 0.18311 | -0.10986 | 0.25177 | -0.041198 | 0.49439 | 122.5891 | 0.096131 | 0.16937 | 122.8775 | 122.9279 | 122.8271 | 122.8592 | -122.8912 | -122.9095 | 122.5388 | 0.10071 | 2.4902 | 0.99335
2814.1719 | 123.0652 | -55.7877 | 67.0074 | -0.045319 | -1.9142e-05 | 0.060103 | 0.068191 | 0.0037918 | 0.0021917 | 0.002431 | 0.09021 | 0.00024775 | 0.0012818 | 0.0017688 | -0.0038559 | -0.0060071 | 0.0042981 | -53.2379 | 66.9983 | -55.8105 | 67.0715 | -55.0369 | -55.957 | -55.0735 | -54.7073 | 66.9891 | -55.8243 | -55.5954 | -55.6778 | -55.7831 | -55.4901 | -0.022888 | -0.009155 | 0.064087 | 0.75073 | 0.71411 | -0.16937 | 0.737 | -0.14648 | -0.036621 | -0.01831 | -122.6028 | 0.10986 | 0.29755 | 0.004578 | 0.33417 | 0.041199 | 0.77362 | 122.8821 | 0.14648 | 0.22888 | 122.8088 | 122.8134 | 122.7859 | 122.7768 | -122.818 | -122.8317 | 122.8592 | 0.19226 | 2.5497 | 1.0803
2815.1719 | 122.9416 | -55.8289 | 67.0395 | -0.075836 | -1.9142e-05 | 0.060744 | 0.069045 | 0.0018692 | 0.0013373 | 0.007558 | 0.044434 | 0.0025975 | 0.0025634 | -0.0010084 | -1.0706e-05 | -0.0053663 | 0.0021619 | -53.302 | 67.0441 | -55.8426 | 66.7648 | -55.3345 | -55.6412 | -54.9911 | -54.9271 | 67.067 | -55.8517 | -55.7053 | -55.7877 | -55.9021 | -55.5954 | -0.013733 | 0.004577 | -0.27466 | 0.49438 | 0.83771 | 0.18768 | 0.85144 | 0.20142 | -0.022889 | 0.027466 | -122.7448 | 0.041198 | 0.23346 | -0.073243 | 0.25635 | -0.050354 | 0.50812 | 122.6074 | 0.064087 | 0.14648 | 122.8867 | 122.9187 | 122.8729 | 122.8958 | -122.8821 | -122.8912 | 122.5937 | 0.1236 | 2.5269 | 0.90179
2816.1719 | 123.0423 | -55.7648 | 67.0074 | -0.03006 | 0.00062166 | 0.062239 | 0.068832 | 0.00037377 | 0.0011237 | 0.0081988 | 0.059692 | -0.0021021 | 0.00085443 | -0.003999 | -0.0036423 | -0.0042981 | 0.0019483 | -53.4851 | 66.9754 | -55.838 | 66.8518 | -55.2155 | -55.5267 | -54.9133 | -54.6433 | 67.0395 | -55.806 | -55.6046 | -55.6503 | -55.7785 | -55.4993 | -0.073242 | -0.032043 | -0.15564 | 0.54932 | 0.85144 | 0.23804 | 0.92468 | 0.31128 | -0.041198 | 0.032044 | -122.612 | 0.11444 | 0.2655 | -0.013732 | 0.3067 | 0.027466 | 0.62256 | 122.6898 | 0.15564 | 0.20142 | 122.8134 | 122.8455 | 122.7402 | 122.8043 | -122.8455 | -122.8134 | 122.6166 | 0.16022 | 2.2797 | 1.1215
2817.1719 | 123.0331 | -55.7693 | 67.0166 | -0.083466 | 0.0016899 | 0.060957 | 0.067336 | 0.00080117 | 0.0030463 | 0.0073444 | -0.059326 | 0.00088875 | 0.00021363 | -0.003999 | -0.0027877 | -0.0057935 | 0.0051525 | -53.2196 | 66.9983 | -55.7831 | 66.893 | -55.1971 | -55.0735 | -54.8172 | -54.5654 | 67.0258 | -55.838 | -55.5817 | -55.6412 | -55.7602 | -55.4993 | -0.013733 | -0.018311 | -0.1236 | 0.5722 | 0.95215 | 0.6958 | 0.96588 | 0.70953 | -0.068665 | 0.009155 | -122.5983 | 0.12817 | 0.27008 | 0.009155 | 0.33874 | 0.07782 | 0.58594 | 122.6761 | 0.19684 | 0.25635 | 122.7814 | 122.8638 | 122.7676 | 122.7951 | -122.7997 | -122.8546 | 122.6624 | 0.18768 | 2.5497 | 1.2039
2818.1719 | 123.024 | -55.7693 | 67.0303 | -0.045319 | 0.0016899 | 0.063094 | 0.069686 | 0.00058737 | 0.00091009 | 0.00414 | 0.032227 | 0.00067495 | -0.00064077 | -0.0048536 | -0.0036423 | -0.0045117 | -0.00061526 | -53.2379 | 66.98 | -55.7968 | 66.9022 | -55.188 | -55.5359 | -54.9225 | -54.6524 | 67.0349 | -55.806 | -55.5862 | -55.6595 | -55.7877 | -55.4993 | -0.027466 | -0.050354 | -0.12817 | 0.58136 | 0.84686 | 0.23346 | 0.87433 | 0.26093 | -0.036621 | 0.004578 | -122.6166 | 0.10986 | 0.27008 | -0.018311 | 0.3067 | 0.01831 | 0.60883 | 122.699 | 0.14648 | 0.21973 | 122.7768 | 122.8409 | 122.7493 | 122.8043 | -122.8271 | -122.8363 | 122.6715 | 0.1831 | 2.5314 | 1.1169
2819.1719 | 122.8683 | -55.7785 | 67.1173 | -0.037689 | 0.0025443 | 0.061598 | 0.069686 | 0.0012284 | 0.0021917 | 0.005849 | 0.0047608 | 0.0017431 | 0.00085443 | -0.00058098 | -0.0021469 | -0.0053663 | -0.0040333 | -53.2745 | 67.0441 | -55.8151 | 66.7969 | -55.2933 | -55.632 | -54.9957 | -54.776 | 67.0715 | -55.8105 | -55.6686 | -55.7556 | -55.8746 | -55.5908 | -0.036622 | -0.073243 | -0.32044 | 0.48523 | 0.78278 | 0.14648 | 0.8194 | 0.18311 | -0.032044 | -0.045777 | -122.786 | 0.022888 | 0.18768 | -0.096131 | 0.21973 | -0.064087 | 0.52185 | 122.612 | 0.054932 | 0.14191 | 122.8592 | 122.8821 | 122.8226 | 122.85 | -122.9324 | -122.9279 | 122.5754 | 0.10986 | 2.504 | 1.0025
2820.1719 | 122.9736 | -55.7785 | 67.0486 | -0.068207 | 0.0021171 | 0.060957 | 0.068191 | 0.0044328 | 0.0011237 | 0.0032856 | 0.032227 | 0.00046135 | 0.0019226 | -0.0014356 | -0.0019333 | -0.0066479 | -0.0010425 | -53.2242 | 67.0212 | -55.7968 | 66.8701 | -55.1971 | -55.5267 | -54.9179 | -54.657 | 67.0624 | -55.7693 | -55.5862 | -55.6595 | -55.8014 | -55.5038 | -0.018311 | -0.027466 | -0.17853 | 0.58136 | 0.8606 | 0.25177 | 0.87891 | 0.27008 | 0.009155 | 0.013733 | -122.6349 | 0.11902 | 0.27466 | -0.022889 | 0.2655 | -0.032044 | 0.59967 | 122.6669 | 0.10986 | 0.1831 | 122.818 | 122.8317 | 122.7997 | 122.8409 | -122.8455 | -122.818 | 122.6486 | 0.19226 | 2.5543 | 1.1215
2821.1719 | 123.0103 | -55.7144 | 66.9983 | -0.13687 | 0.00019446 | 0.060744 | 0.068618 | 0.00058737 | 0.0024053 | 0.0047808 | 0.026123 | 0.00046135 | 0.001068 | -0.00229 | -0.0030013 | -0.0068615 | 0.0032299 | -53.1921 | 66.9937 | -55.7831 | 66.9113 | -55.1376 | -55.4947 | -54.8721 | -54.5837 | 67.0258 | -55.7693 | -55.5496 | -55.687 | -55.3711 | -55.2567 | -0.068664 | -0.004578 | -0.086975 | 0.57678 | 0.84229 | 0.21973 | 0.91095 | 0.28839 | -0.054931 | 0.027466 | -122.5479 | 0.027466 | 0.45776 | 0.34332 | 0.5127 | 0.39825 | 0.64545 | 122.6944 | 0.082397 | 0.21973 | 122.7768 | 122.7951 | 122.7081 | 122.7402 | -122.7814 | -122.7676 | 122.6257 | 0.16479 | 2.5223 | 1.1307
2822.1719 | 123.0835 | -55.7419 | 67.0212 | -0.091095 | 0.00019446 | 0.060744 | 0.069045 | 0.001442 | 0.0019781 | 0.003072 | 0.035278 | -0.00082025 | 0.002777 | -0.0010084 | -0.00086511 | -0.0075025 | -0.00061526 | -53.2013 | 67.0166 | -55.8014 | 66.9159 | -55.1697 | -55.5038 | -54.8767 | -54.5975 | 67.0532 | -55.7785 | -55.5267 | -55.6046 | -55.7281 | -55.4398 | -0.05951 | -0.004577 | -0.10529 | 0.5722 | 0.86517 | 0.23804 | 0.92468 | 0.29755 | -0.036621 | 0.032044 | -122.5479 | 0.13733 | 0.30212 | 0.013733 | 0.33875 | 0.050354 | 0.63171 | 122.7173 | 0.17395 | 0.25177 | 122.818 | 122.8317 | 122.7585 | 122.7951 | -122.8226 | -122.7997 | 122.6578 | 0.21515 | 2.5406 | 1.1444
2823.1719 | 123.0515 | -55.7236 | 67.0395 | -0.068207 | -0.00066014 | 0.061812 | 0.068618 | -0.0017624 | 0.0015509 | 0.00414 | -0.089844 | -0.0010339 | -0.00064077 | 0.002196 | -0.0023605 | -0.0049389 | -0.0016833 | -53.183 | 67.0212 | -55.7739 | 66.8472 | -54.9133 | -55.1605 | -54.9911 | -54.5609 | 67.0212 | -55.7968 | -55.5267 | -55.6046 | -55.7327 | -55.4855 | -0.050354 | -0.018311 | -0.19226 | 0.81024 | 0.73242 | 0.56305 | 0.78278 | 0.6134 | -0.073242 | -0.018311 | -122.5662 | 0.11902 | 0.23804 | -0.009155 | 0.31128 | 0.064087 | 0.8606 | 122.6212 | 0.19226 | 0.27008 | 122.7951 | 122.818 | 122.7448 | 122.7448 | -122.8134 | -122.8363 | 122.5708 | 0.19684 | 2.5406 | 1.1627
2824.1719 | 123.0652 | -55.7327 | 67.0349 | -0.12161 | -0.00023294 | 0.059676 | 0.068832 | 0.00058737 | 0.0041143 | 0.0056354 | 0.016968 | 0.0013159 | -0.001709 | -0.00464 | -0.0027877 | -0.0070753 | -0.0014697 | -53.215 | 67.0303 | -55.7922 | 66.8976 | -55.1834 | -55.5313 | -54.8813 | -54.6249 | 67.0258 | -55.7785 | -55.545 | -55.6137 | -55.7236 | -55.4535 | -0.059509 | -0.004578 | -0.13733 | 0.54932 | 0.85144 | 0.20142 | 0.91095 | 0.26093 | -0.045776 | -0.009155 | -122.58 | 0.11902 | 0.27924 | 0.009155 | 0.32501 | 0.054931 | 0.60883 | 122.6898 | 0.16479 | 0.23346 | 122.8226 | 122.8043 | 122.7631 | 122.7585 | -122.8271 | -122.8134 | 122.6303 | 0.18768 | 2.5177 | 1.1078
2825.1719 | 123.0927 | -55.7373 | 67.0212 | -0.052948 | 0.0016899 | 0.060957 | 0.067977 | -0.0021896 | 0.0013373 | 0.0062762 | 0.0047608 | 3.4148e-05 | 0.00042723 | -0.00079478 | -0.0021469 | -0.0068615 | -0.0018971 | -53.2288 | 67.0486 | -55.7785 | 66.893 | -55.2109 | -55.5313 | -54.895 | -54.6478 | 67.0715 | -55.7739 | -55.5496 | -55.6137 | -55.7556 | -55.4581 | -0.041198 | 0.027466 | -0.12817 | 0.52643 | 0.84228 | 0.20599 | 0.88348 | 0.24719 | -0.036621 | 0.050354 | -122.5708 | 0.1236 | 0.27924 | -0.01831 | 0.31586 | 0.018311 | 0.56763 | 122.6715 | 0.16022 | 0.2243 | 122.8271 | 122.8455 | 122.7859 | 122.8088 | -122.7997 | -122.7951 | 122.6303 | 0.18768 | 2.5085 | 1.0895
2826.1719 | 123.024 | -55.7236 | 67.0532 | -0.10635 | -0.00023294 | 0.06053 | 0.068404 | -0.0032578 | 0.0021917 | 0.0043536 | 0.026123 | 0.0013159 | -0.00021357 | 0.0024096 | -0.0034287 | -0.0055799 | -0.0018971 | -53.215 | 67.0258 | -55.7785 | 66.8976 | -55.2109 | -55.545 | -54.9042 | -54.6387 | 67.0486 | -55.7739 | -55.5496 | -55.6183 | -55.7556 | -55.4672 | -0.054931 | -0.027466 | -0.15564 | 0.5127 | 0.8194 | 0.17853 | 0.87433 | 0.23346 | -0.050354 | -0.004578 | -122.6028 | 0.10529 | 0.25635 | -0.032043 | 0.3067 | 0.018311 | 0.56763 | 122.6761 | 0.15564 | 0.2243 | 122.8043 | 122.8226 | 122.7493 | 122.7722 | -122.8317 | -122.8271 | 122.6212 | 0.17395 | 2.5085 | 1.0849
2827.1719 | 122.9507 | -55.7419 | 67.0624 | -0.098725 | -0.00066014 | 0.062239 | 0.069686 | -0.0011214 | 0.0026191 | 0.0056354 | 0.023071 | 0.00067495 | -0.0012818 | -0.0031446 | -0.0038559 | -0.0051527 | -0.00040166 | -53.1784 | 67.0486 | -55.7648 | 66.8976 | -55.1651 | -55.513 | -54.9042 | -54.6387 | 67.099 | -55.7556 | -55.5634 | -55.6412 | -55.7922 | -55.5038 | -0.022889 | -0.013733 | -0.16479 | 0.57678 | 0.83771 | 0.22888 | 0.8606 | 0.25177 | -0.013733 | 0.036621 | -122.6257 | 0.10071 | 0.23804 | -0.050354 | 0.25177 | -0.036621 | 0.59967 | 122.6624 | 0.11444 | 0.19226 | 122.8134 | 122.8546 | 122.7905 | 122.8409 | -122.8271 | -122.818 | 122.6395 | 0.17853 | 2.5635 | 1.1032
2828.1719 | 123.0515 | -55.719 | 67.0715 | -0.068207 | -0.00023294 | 0.062453 | 0.067763 | -0.0024032 | 0.0021917 | 0.0056354 | 0.17871 | 0.0025975 | 0.001068 | 0.0015552 | -0.0025741 | -0.0057935 | -0.0029651 | -53.1601 | 67.0532 | -55.7419 | 66.9388 | -55.1331 | -55.4764 | -54.8721 | -54.7943 | 67.1036 | -55.7693 | -55.5038 | -55.6137 | -55.7373 | -55.4626 | -0.022888 | -0.01831 | -0.13275 | 0.58594 | 0.84686 | 0.24262 | 0.86975 | 0.2655 | -0.050354 | 0.032044 | -122.5754 | 0.10529 | 0.25635 | -0.018311 | 0.3067 | 0.032043 | 0.60882 | 122.6807 | 0.15564 | 0.2655 | 122.7951 | 122.8729 | 122.7722 | 122.8226 | -122.8134 | -122.8409 | 122.6578 | 0.21515 | 2.5589 | 0.92468
2829.1719 | 123.0194 | -55.7327 | 67.0395 | -0.083466 | 0.0010489 | 0.060957 | 0.068404 | -0.0017624 | 0.0013373 | 0.0037128 | 0.029175 | -0.00060665 | -0.0010682 | 0.0015552 | -0.0015061 | -0.0066479 | -0.0014697 | -53.1418 | 67.0532 | -55.7419 | 66.9754 | -55.0919 | -55.4672 | -54.8401 | -54.5609 | 67.0761 | -55.7556 | -55.6366 | -55.7098 | -55.6503 | -55.4031 | -0.009155 | 0.013733 | -0.064087 | 0.64087 | 0.89264 | 0.2655 | 0.90179 | 0.27466 | -0.022888 | 0.036621 | -122.6761 | 0.022888 | 0.32959 | 0.082397 | 0.35248 | 0.10529 | 0.65002 | 122.7173 | 0.045776 | 0.11902 | 122.7951 | 122.8317 | 122.7859 | 122.8088 | -122.7814 | -122.7951 | 122.7081 | 0.09613 | 2.5909 | 1.1719
2830.1719 | 123.0194 | -55.7281 | 67.0349 | 0.31326 | -0.00023294 | 0.063521 | 0.069472 | -0.0011214 | 0.0024053 | 0.0060626 | 0.0047608 | 0.00024775 | -0.00042717 | -0.00036738 | -0.0019333 | -0.0060071 | -0.0031787 | -53.2104 | 67.0624 | -55.8014 | 66.8747 | -55.2429 | -55.5817 | -54.9179 | -54.6753 | 67.1036 | -55.7556 | -55.5542 | -55.6503 | -55.7693 | -55.481 | -0.073243 | 0.027466 | -0.16022 | 0.48523 | 0.81024 | 0.14648 | 0.88348 | 0.21973 | -0.027466 | 0.068665 | -122.5891 | 0.077819 | 0.24719 | -0.041199 | 0.27466 | -0.013733 | 0.55847 | 122.6761 | 0.10529 | 0.20142 | 122.8638 | 122.8592 | 122.7905 | 122.8317 | -122.8363 | -122.7905 | 122.6028 | 0.17395 | 2.5177 | 1.0529
2831.1719 | 123.0606 | -55.7007 | 67.0624 | -0.052948 | -0.00044654 | 0.060744 | 0.069472 | -0.00026703 | 0.0045417 | 0.0062762 | 0.02002 | -0.00039305 | 0.00085443 | 5.9824e-05 | -0.0038559 | -0.0032301 | -0.0033923 | -53.1784 | 67.0532 | -55.7373 | 66.9617 | -55.1056 | -55.4672 | -54.8447 | -54.5334 | 67.1036 | -55.751 | -55.4718 | -55.545 | -55.6778 | -55.4123 | -0.036621 | -0.009155 | -0.10071 | 0.59509 | 0.85602 | 0.23346 | 0.89264 | 0.27008 | -0.050354 | 0.041199 | -122.5342 | 0.15564 | 0.28839 | 0.022889 | 0.33875 | 0.073243 | 0.63171 | 122.699 | 0.20599 | 0.27924 | 122.7905 | 122.8546 | 122.7539 | 122.8043 | -122.7997 | -122.8134 | 122.6624 | 0.22888 | 2.5223 | 1.1673
2832.1719 | 123.0698 | -55.6778 | 67.0532 | -0.060578 | -0.00044654 | 0.060957 | 0.068832 | -0.0017624 | 0.0021917 | 0.0052082 | 0.02002 | 0.00088875 | -0.00042717 | 0.0045458 | -0.00065151 | -0.0032301 | 0.00023934 | -53.1738 | 67.0578 | -55.7419 | 66.9525 | -55.1056 | -55.4489 | -54.8309 | -54.5517 | 67.0853 | -55.7373 | -55.4718 | -55.5359 | -55.687 | -55.4077 | -0.064087 | 0.004577 | -0.10071 | 0.5722 | 0.84686 | 0.22888 | 0.91095 | 0.29297 | -0.05951 | 0.032043 | -122.525 | 0.14191 | 0.27008 | -0.009156 | 0.32959 | 0.050354 | 0.63629 | 122.6944 | 0.20142 | 0.2655 | 122.7997 | 122.8226 | 122.7356 | 122.7631 | -122.7951 | -122.7905 | 122.6303 | 0.20599 | 2.504 | 1.1261
2833.1719 | 123.0011 | -55.6824 | 67.0944 | -0.060578 | 0.0012625 | 0.06288 | 0.0699 | -0.00069423 | 0.0036871 | 0.0045672 | -0.0043946 | 0.00024775 | -0.00085457 | 0.00070062 | -0.0038559 | -0.0049389 | 0.0019483 | -53.1281 | 67.0944 | -55.7465 | 66.9479 | -55.1376 | -55.4764 | -54.8538 | -54.5792 | 67.1173 | -55.719 | -55.5313 | -55.6 | -55.7281 | -55.4535 | -0.064087 | 0 | -0.14648 | 0.54474 | 0.82855 | 0.20599 | 0.89264 | 0.27008 | -0.036621 | 0.022889 | -122.6257 | 0.082397 | 0.22888 | -0.045776 | 0.2655 | -0.009155 | 0.60883 | 122.6944 | 0.11902 | 0.18768 | 122.8409 | 122.8363 | 122.7768 | 122.7997 | -122.8409 | -122.8134 | 122.6303 | 0.15106 | 2.5543 | 1.1032
2834.1719 | 123.024 | -55.7098 | 67.0807 | -0.12924 | -0.0015145 | 0.060103 | 0.069259 | 0.0046464 | 0.0032599 | 0.0032856 | 0.001709 | 0.0015295 | 0.00064083 | 0.002196 | -0.0027877 | -0.0051527 | 0.0013073 | -53.2013 | 67.0715 | -55.7556 | 66.9022 | -55.1926 | -55.5222 | -54.8996 | -54.6249 | 67.067 | -55.7465 | -55.513 | -55.6137 | -55.7281 | -55.4443 | -0.045776 | -0.009155 | -0.17853 | 0.51727 | 0.81024 | 0.18768 | 0.85602 | 0.23346 | -0.036621 | -0.013732 | -122.5937 | 0.096131 | 0.2655 | -0.01831 | 0.30212 | 0.018311 | 0.56305 | 122.6578 | 0.13275 | 0.23346 | 122.8271 | 122.8134 | 122.7814 | 122.7768 | -122.8363 | -122.8271 | 122.612 | 0.19684 | 2.5085 | 1.0849
2835.1719 | 123.0377 | -55.6778 | 67.1036 | -0.068207 | 0.00083526 | 0.062453 | 0.068832 | -0.0028304 | 0.0030463 | 0.0060626 | 0.023071 | 3.4148e-05 | 2.8e-08 | 5.9824e-05 | -0.0017197 | -0.0049389 | 0.0010937 | -53.1281 | 67.0486 | -55.7465 | 67.0029 | -55.069 | -55.4352 | -54.8218 | -54.2953 | 67.1768 | -55.6595 | -55.4947 | -55.5588 | -55.687 | -55.4123 | -0.068665 | -0.054932 | -0.10071 | 0.60883 | 0.85602 | 0.24261 | 0.92468 | 0.31128 | 0.01831 | 0.073242 | -122.5983 | 0.11902 | 0.2655 | -0.009156 | 0.24719 | -0.027466 | 0.67749 | 122.7493 | 0.10071 | 0.16479 | 122.7951 | 122.8363 | 122.7264 | 122.8546 | -122.85 | -122.7631 | 122.6807 | 0.18311 | 2.5497 | 1.3824
2836.1719 | 123.0148 | -55.6915 | 67.0715 | -0.091095 | -1.9142e-05 | 0.061171 | 0.069259 | -5.343e-05 | 0.0028327 | 0.003072 | 0.010864 | 0.0021703 | -0.0012818 | -0.00229 | -0.0017197 | -0.0028027 | -0.0025379 | -53.1235 | 67.0532 | -55.7236 | 67.0029 | -55.069 | -55.4169 | -54.808 | -54.5334 | 67.1173 | -55.6961 | -55.6 | -55.4764 | -55.7053 | -55.4489 | -0.032044 | -0.01831 | -0.068664 | 0.62256 | 0.88348 | 0.27466 | 0.91553 | 0.3067 | -0.004578 | 0.045777 | -122.6715 | 0.21515 | 0.24261 | -0.013733 | 0.24719 | -0.009155 | 0.6546 | 122.7264 | 0.21973 | 0.09613 | 122.7768 | 122.8134 | 122.7448 | 122.8088 | -122.7951 | -122.7676 | 122.6944 | 0.091552 | 2.5681 | 1.1581
2837.1719 | 123.0011 | -55.6824 | 67.0944 | -0.17502 | 0.00040806 | 0.059889 | 0.070968 | 0.0020828 | 0.0024053 | 0.0062762 | 0.0078126 | 0.0011023 | 0.00021363 | 0.0030506 | -0.00086511 | -0.0053663 | 0.0010937 | -53.2059 | 67.067 | -55.7373 | 66.9022 | -55.1834 | -55.5405 | -54.8859 | -54.6204 | 67.1494 | -55.7281 | -55.5084 | -55.5817 | -55.7373 | -55.4535 | -0.054932 | -0.027465 | -0.19226 | 0.49896 | 0.79651 | 0.14191 | 0.85144 | 0.19684 | -0.045776 | 0.054932 | -122.6028 | 0.10071 | 0.22888 | -0.054932 | 0.27466 | -0.009156 | 0.55389 | 122.6395 | 0.14648 | 0.21973 | 122.8043 | 122.8775 | 122.7493 | 122.8317 | -122.8317 | -122.8226 | 122.5845 | 0.17395 | 2.4765 | 1.062
2838.1719 | 123.1018 | -55.6183 | 67.1402 | -0.068207 | -1.9142e-05 | 0.060744 | 0.071395 | -0.0060348 | 0.0030463 | 0.0039264 | 0.001709 | 0.0013159 | -0.00042717 | 0.00027342 | -0.0012925 | -0.0055799 | -0.0023243 | -53.1189 | 67.0898 | -55.7236 | 67.012 | -55.0644 | -55.4352 | -54.7989 | -54.4922 | 67.1173 | -55.6915 | -55.4352 | -55.545 | -55.5862 | -55.2521 | -0.10529 | -0.050354 | -0.12817 | 0.55389 | 0.8194 | 0.1831 | 0.92468 | 0.28839 | -0.073242 | -0.022888 | -122.5754 | 0.073242 | 0.36621 | 0.032043 | 0.43945 | 0.10528 | 0.65918 | 122.7356 | 0.14648 | 0.25635 | 122.8134 | 122.8088 | 122.7081 | 122.7356 | -122.8638 | -122.8317 | 122.6303 | 0.1831 | 2.4994 | 1.1261
2839.1719 | 123.0469 | -55.6686 | 67.1127 | -0.29709 | 0.0014761 | 0.062666 | 0.068618 | 0.0016556 | 0.0021917 | 0.0088398 | -0.0013428 | 0.00067495 | 0.00064083 | 0.0024096 | -0.0027877 | -0.0032301 | -0.0033923 | -53.1006 | 67.067 | -55.6961 | 66.9708 | -55.0644 | -55.4214 | -54.8218 | -54.5197 | 67.1448 | -55.719 | -55.4718 | -55.545 | -55.6824 | -55.3986 | -0.027466 | -0.045776 | -0.14191 | 0.60425 | 0.84686 | 0.24719 | 0.87433 | 0.27466 | -0.050354 | 0.032043 | -122.5845 | 0.1236 | 0.27008 | -0.013733 | 0.32043 | 0.036621 | 0.63171 | 122.6669 | 0.17395 | 0.24719 | 122.7631 | 122.8638 | 122.7356 | 122.8134 | -122.8088 | -122.8317 | 122.6395 | 0.19684 | 2.5681 | 1.149
2840.1719 | 123.0743 | -55.6458 | 67.1082 | -0.12924 | 0.00040806 | 0.059676 | 0.070113 | -0.00026703 | 0.0030463 | 0.0081988 | 0.016968 | 0.0011023 | -0.0012818 | 0.00027342 | -0.0025741 | -0.0034437 | -0.0063831 | -53.1464 | 67.0853 | -55.7053 | 66.9846 | -55.0873 | -55.4077 | -54.7852 | -54.5059 | 67.1082 | -55.7007 | -55.426 | -55.5084 | -55.6458 | -55.3802 | -0.059509 | -0.022888 | -0.1236 | 0.55847 | 0.8606 | 0.23804 | 0.9201 | 0.29755 | -0.054932 | 0 | -122.5342 | 0.13733 | 0.2655 | 0 | 0.32044 | 0.054932 | 0.61798 | 122.6898 | 0.19226 | 0.27466 | 122.7905 | 122.8088 | 122.731 | 122.7539 | -122.8134 | -122.8088 | 122.6303 | 0.21973 | 2.4994 | 1.1398
2841.1719 | 123.056 | -55.6458 | 67.1036 | -0.083466 | -0.00066014 | 0.06053 | 0.070541 | -0.0021896 | 0.0049689 | 0.0064898 | 0.001709 | -0.00039305 | 0.00064083 | 0.0017688 | -0.0032151 | -0.0032301 | -0.0027515 | -53.1281 | 67.099 | -55.7007 | 66.9846 | -55.0827 | -55.4352 | -54.7943 | -54.4968 | 67.1539 | -55.6961 | -55.4489 | -55.513 | -55.6366 | -55.3711 | -0.054932 | -0.004578 | -0.11902 | 0.56305 | 0.85144 | 0.21057 | 0.90637 | 0.2655 | -0.050354 | 0.050354 | -122.5525 | 0.13275 | 0.27466 | 0.009155 | 0.32501 | 0.059509 | 0.61798 | 122.6852 | 0.18311 | 0.24719 | 122.7997 | 122.85 | 122.7448 | 122.7997 | -122.8043 | -122.7997 | 122.6303 | 0.19684 | 2.5177 | 1.149
2842.1719 | 123.024 | -55.6824 | 67.1082 | -0.098725 | -0.0017281 | 0.061171 | 0.069686 | 0.0018692 | 0.0011237 | 0.0049946 | 0.001709 | -0.00060665 | 0.00064083 | -0.00036738 | -0.0025741 | -0.0045117 | 0.0017345 | -53.1692 | 67.1036 | -55.7327 | 66.9571 | -55.1514 | -55.4901 | -54.8355 | -54.5975 | 67.1494 | -55.7144 | -55.481 | -55.5725 | -55.7098 | -55.4123 | -0.050354 | -0.004577 | -0.15106 | 0.53101 | 0.84686 | 0.19226 | 0.89722 | 0.24261 | -0.032044 | 0.041199 | -122.5891 | 0.10986 | 0.27008 | -0.027466 | 0.30212 | 0.004578 | 0.58136 | 122.6898 | 0.14191 | 0.23346 | 122.8363 | 122.8638 | 122.7859 | 122.8317 | -122.8409 | -122.8226 | 122.6395 | 0.20142 | 2.5131 | 1.0849
2843.1719 | 122.9416 | -55.6549 | 67.1768 | -0.083466 | -0.00087374 | 0.06053 | 0.071822 | 0.00058737 | 0.0028327 | 0.0045672 | -0.010498 | 0.0011023 | 0.00021363 | -0.00015378 | -0.0034287 | -0.0049389 | -0.00082886 | -53.1235 | 67.1356 | -55.7053 | 66.9662 | -55.1285 | -55.4718 | -54.8447 | -54.6066 | 67.1906 | -55.7098 | -55.513 | -55.6503 | -55.7602 | -55.4672 | -0.050354 | -0.041199 | -0.21057 | 0.52643 | 0.81024 | 0.18311 | 0.8606 | 0.23346 | -0.054932 | 0.013733 | -122.6898 | 0.004577 | 0.18768 | -0.10529 | 0.24262 | -0.050354 | 0.57678 | 122.6715 | 0.059509 | 0.19684 | 122.8409 | 122.9004 | 122.7905 | 122.8455 | -122.8821 | -122.8867 | 122.6212 | 0.14191 | 2.5314 | 1.0483
2844.1719 | 123.0515 | -55.6641 | 67.1219 | -0.098725 | -0.00066014 | 0.062239 | 0.069045 | -0.00090783 | 5.5488e-05 | 0.0067036 | -0.0043946 | 0.0017431 | -0.00085457 | -0.00036738 | -0.0032151 | -0.0057935 | -0.0014697 | -53.1052 | 67.131 | -55.687 | 66.9754 | -55.1193 | -55.4352 | -54.8264 | -54.5517 | 67.1402 | -55.7007 | -55.4489 | -55.5359 | -55.6366 | -55.3711 | -0.022889 | 0.009155 | -0.14648 | 0.54474 | 0.83771 | 0.22888 | 0.8606 | 0.25177 | -0.036622 | 0.018311 | -122.5708 | 0.12817 | 0.29297 | 0.027465 | 0.32959 | 0.064087 | 0.56763 | 122.6624 | 0.1648 | 0.25177 | 122.818 | 122.8409 | 122.7951 | 122.8043 | -122.8088 | -122.8226 | 122.6395 | 0.21515 | 2.5589 | 1.1124
2845.1719 | 122.9736 | -55.6549 | 67.1814 | -0.12924 | 0.00019446 | 0.06288 | 0.069472 | -0.0028304 | 0.0011237 | 0.0079852 | 0.001709 | 0.00088875 | -0.00064077 | 5.9824e-05 | -1.0706e-05 | -0.0070753 | 0.0015209 | -53.1097 | 67.1402 | -55.7007 | 66.9937 | -55.101 | -55.426 | -54.8035 | -54.5746 | 67.1951 | -55.687 | -55.4947 | -55.5862 | -55.7144 | -55.4398 | -0.045777 | -0.041198 | -0.18768 | 0.55389 | 0.85144 | 0.22888 | 0.89722 | 0.27466 | -0.032044 | 0.013733 | -122.6761 | 0.068664 | 0.21515 | -0.05951 | 0.24719 | -0.027466 | 0.59967 | 122.6944 | 0.10071 | 0.19226 | 122.8409 | 122.8821 | 122.7951 | 122.85 | -122.8821 | -122.8683 | 122.6486 | 0.16022 | 2.5452 | 1.0803
2846.1719 | 122.9416 | -55.6778 | 67.1677 | -0.060578 | 0.0010489 | 0.060744 | 0.069686 | -0.001976 | 0.0021917 | 0.0067036 | -0.071533 | -0.00017945 | -0.001709 | -0.0014356 | -0.0015061 | -0.0030163 | -0.0025379 | -53.1326 | 67.1539 | -55.7236 | 66.9205 | -55.2017 | -55.5267 | -54.8904 | -54.6616 | 67.2134 | -55.7007 | -55.513 | -55.6229 | -55.7648 | -55.4535 | -0.045777 | -0.013733 | -0.24719 | 0.47607 | 0.78735 | 0.15106 | 0.83313 | 0.19684 | -0.022889 | 0.045776 | -122.6807 | 0.054931 | 0.2243 | -0.086976 | 0.24719 | -0.064087 | 0.52185 | 122.644 | 0.07782 | 0.18768 | 122.8775 | 122.9141 | 122.8317 | 122.8912 | -122.8912 | -122.8683 | 122.5983 | 0.1648 | 2.5452 | 1.0162
2847.1719 | 123.056 | -55.632 | 67.1265 | -0.068207 | 0.00019446 | 0.062666 | 0.068191 | 0.00080117 | 0.00026909 | 0.0060626 | 0.032227 | -0.00082025 | 0.00064083 | 0.0024096 | -0.0032151 | -0.0038709 | -0.00082886 | -53.0731 | 67.131 | -55.6686 | 67.2363 | -54.9408 | -55.7877 | -54.9179 | -54.5334 | 67.131 | -55.687 | -55.4031 | -55.5222 | -55.6274 | -55.3528 | -0.036621 | 0.004577 | 0.10986 | 0.69122 | 0.71411 | -0.15564 | 0.75073 | -0.11902 | -0.054932 | 0.004577 | -122.5296 | 0.10986 | 0.27924 | 0.004578 | 0.33417 | 0.05951 | 0.72784 | 122.905 | 0.16479 | 0.28381 | 122.7997 | 122.818 | 122.7631 | 122.7631 | -122.7951 | -122.8134 | 122.8683 | 0.22888 | 2.5589 | 1.0986
2848.1719 | 123.024 | -55.5908 | 67.1402 | -0.045319 | 0.00040806 | 0.059889 | 0.068832 | -0.0015488 | 5.5488e-05 | 0.0032856 | 0.1543 | 0.0011023 | 0.0019226 | 0.0034778 | -0.0019333 | -0.0053663 | 2.554e-05 | -53.0548 | 67.1585 | -55.6549 | 67.0349 | -55.0323 | -55.3802 | -54.7394 | -54.7165 | 67.1722 | -55.6686 | -55.4031 | -55.5176 | -55.6229 | -55.3482 | -0.064087 | 0.01831 | -0.10529 | 0.55847 | 0.85144 | 0.21057 | 0.91553 | 0.27466 | -0.07782 | 0.032043 | -122.5433 | 0.073242 | 0.24261 | -0.032044 | 0.32043 | 0.045776 | 0.62256 | 122.6898 | 0.15106 | 0.2655 | 122.8134 | 122.8409 | 122.7493 | 122.7631 | -122.7951 | -122.8088 | 122.6257 | 0.18768 | 2.536 | 0.87433
2849.1719 | 123.0469 | -55.6183 | 67.1539 | -0.068207 | -1.9142e-05 | 0.061171 | 0.067123 | -5.343e-05 | 0.0028327 | 0.0071308 | 0.02002 | 0.00024775 | -0.0010682 | 0.002196 | -0.0023605 | -0.0062207 | -0.0010425 | -53.1143 | 67.1173 | -55.6961 | 66.9662 | -55.1331 | -55.4626 | -54.8218 | -54.5792 | 67.1722 | -55.6732 | -55.4398 | -55.545 | -55.6778 | -55.4031 | -0.07782 | -0.036621 | -0.18768 | 0.48523 | 0.79651 | 0.15564 | 0.87433 | 0.23346 | -0.054932 | 0.01831 | -122.5937 | 0.073242 | 0.21515 | -0.059509 | 0.27008 | -0.004577 | 0.56305 | 122.6624 | 0.12817 | 0.23346 | 122.8134 | 122.8455 | 122.7356 | 122.7905 | -122.85 | -122.8271 | 122.5845 | 0.17853 | 2.504 | 1.0391
2850.1719 | 123.0331 | -55.6412 | 67.1539 | -0.11398 | 0.0010489 | 0.058394 | 0.068191 | -0.0013352 | 0.0030463 | 0.0054218 | 0.029175 | 0.0013159 | 0.00064083 | -0.0031446 | -0.0019333 | -0.0040845 | -0.0010425 | -53.1052 | 67.1448 | -55.6503 | 67.0029 | -55.0827 | -55.426 | -54.7897 | -54.5151 | 67.1722 | -55.6778 | -55.4077 | -55.4901 | -55.6183 | -55.3482 | -0.009156 | -0.009156 | -0.15106 | 0.55847 | 0.85144 | 0.21515 | 0.8606 | 0.2243 | -0.036621 | 0.01831 | -122.5616 | 0.15106 | 0.29297 | 0.022888 | 0.32959 | 0.059509 | 0.56763 | 122.6532 | 0.18768 | 0.27008 | 122.7951 | 122.85 | 122.7859 | 122.8134 | -122.8043 | -122.8317 | 122.644 | 0.23346 | 2.536 | 1.1261
2851.1719 | 122.9736 | -55.6229 | 67.1585 | -0.068207 | -0.00044654 | 0.059035 | 0.073318 | -5.343e-05 | 0.0011237 | 0.005849 | -0.080688 | 0.0013159 | 0.0019226 | 0.0077502 | -0.0034287 | -0.0042981 | -0.0036059 | -53.0914 | 67.1906 | -55.7007 | 66.9754 | -55.1239 | -55.4535 | -54.8538 | -54.5609 | 67.2089 | -55.6686 | -55.4672 | -55.5771 | -55.7053 | -55.3986 | -0.07782 | 0.032044 | -0.1831 | 0.49896 | 0.76904 | 0.16937 | 0.84686 | 0.24719 | -0.045776 | 0.050354 | -122.6257 | 0.045777 | 0.2243 | -0.082397 | 0.27008 | -0.036621 | 0.57678 | 122.6761 | 0.091553 | 0.20142 | 122.8912 | 122.8775 | 122.8134 | 122.8317 | -122.8592 | -122.8271 | 122.5983 | 0.15564 | 2.5314 | 1.062
2852.1719 | 123.0469 | -55.6091 | 67.1494 | -0.098725 | 0.00062166 | 0.060957 | 0.068191 | -0.0013352 | 0.0026191 | 0.00093559 | 0.03833 | 0.00024775 | 0.00021363 | -0.0010084 | -0.0025741 | -0.0034437 | -0.0012561 | -53.1143 | 67.1631 | -55.6458 | 66.9937 | -55.101 | -55.4352 | -54.7668 | -54.5288 | 67.1722 | -55.6686 | -55.4123 | -55.5084 | -55.6229 | -55.3619 | -0.036621 | 0.013733 | -0.15564 | 0.50812 | 0.84228 | 0.17395 | 0.87891 | 0.21057 | -0.059509 | 0.022888 | -122.5616 | 0.10071 | 0.24719 | -0.013733 | 0.3067 | 0.045776 | 0.54474 | 122.6395 | 0.16022 | 0.25635 | 122.8088 | 122.8409 | 122.7722 | 122.7814 | -122.7951 | -122.818 | 122.6028 | 0.19684 | 2.4948 | 1.0803
2853.1719 | 122.9416 | -55.6458 | 67.218 | -0.022431 | -0.0017281 | 0.060103 | 0.069045 | -0.0013352 | 0.0021917 | 0.0047808 | -0.059326 | 0.0021703 | -0.0010682 | 0.0049732 | -0.0025741 | -0.0034437 | -0.0025379 | -53.1601 | 67.2134 | -55.7098 | 66.9434 | -55.1651 | -55.4855 | -54.8721 | -54.6249 | 67.2501 | -55.6732 | -55.4947 | -55.5862 | -55.7419 | -55.426 | -0.064087 | -0.004578 | -0.27466 | 0.48065 | 0.77362 | 0.16022 | 0.83771 | 0.2243 | -0.027466 | 0.032043 | -122.7127 | 0.059509 | 0.21973 | -0.09613 | 0.24719 | -0.068664 | 0.54474 | 122.6532 | 0.086975 | 0.17853 | 122.9233 | 122.9233 | 122.8592 | 122.8958 | -122.9279 | -122.8912 | 122.5891 | 0.15106 | 2.4857 | 1.0208
2854.1719 | 123.0469 | -55.6229 | 67.1814 | -0.13687 | -0.0015145 | 0.062025 | 0.067977 | 0.0022964 | 0.0041143 | 0.0073444 | 0.013916 | -0.00060665 | 0.002777 | -0.00058098 | -0.0010787 | -0.0057935 | -0.00082886 | -53.0869 | 67.1265 | -55.687 | 66.9983 | -55.1102 | -55.4352 | -54.8035 | -54.538 | 67.1768 | -55.6503 | -55.4123 | -55.5222 | -55.6366 | -55.3482 | -0.064087 | -0.054931 | -0.18311 | 0.5127 | 0.8194 | 0.18768 | 0.88348 | 0.25177 | -0.027466 | -0.004577 | -122.5937 | 0.10071 | 0.27466 | -0.013733 | 0.30212 | 0.013733 | 0.57678 | 122.6852 | 0.12817 | 0.23804 | 122.8134 | 122.8271 | 122.7493 | 122.7997 | -122.8683 | -122.8317 | 122.6212 | 0.21057 | 2.536 | 1.0849
2855.1719 | 123.0652 | -55.5908 | 67.186 | -0.098725 | 0.0021171 | 0.061171 | 0.068191 | -0.0032578 | 5.5488e-05 | 0.0026446 | 0.032227 | 0.00067495 | 0.001068 | -0.0035718 | -0.0034287 | -0.0062207 | -0.0023243 | -53.0228 | 67.1677 | -55.6503 | 67.1448 | -54.7073 | -55.4352 | -54.9866 | -54.4601 | 67.1768 | -55.6641 | -55.3757 | -55.4535 | -55.5908 | -55.3207 | -0.05951 | -0.01831 | -0.041199 | 0.88348 | 0.60425 | 0.15564 | 0.66376 | 0.21515 | -0.073242 | -0.009155 | -122.5616 | 0.13733 | 0.27008 | 0 | 0.34332 | 0.073242 | 0.94299 | 122.7951 | 0.21057 | 0.28839 | 122.818 | 122.8409 | 122.7585 | 122.7676 | -122.8363 | -122.85 | 122.7356 | 0.21515 | 2.5681 | 1.1307
2856.1719 | 122.9782 | -55.6046 | 67.2134 | -0.068207 | 0.0033987 | 0.062025 | 0.072036 | -0.0015488 | 0.0017645 | 0.0067036 | -0.080688 | 0.0023839 | -0.001709 | 0.0030506 | -0.0017197 | -0.0032301 | 0.00045294 | -53.0548 | 67.1814 | -55.7007 | 66.9983 | -55.101 | -55.4535 | -54.8492 | -54.5334 | 67.2272 | -55.6458 | -55.4489 | -55.5542 | -55.7053 | -55.3802 | -0.096131 | -0.032044 | -0.21515 | 0.50354 | 0.75531 | 0.15106 | 0.85144 | 0.24719 | -0.041199 | 0.013733 | -122.6624 | 0.050354 | 0.2243 | -0.10071 | 0.2655 | -0.059509 | 0.59967 | 122.699 | 0.091553 | 0.19684 | 122.8821 | 122.8729 | 122.7859 | 122.8317 | -122.9141 | -122.8592 | 122.6028 | 0.15564 | 2.5497 | 1.0712
2857.1719 | 122.9645 | -55.5817 | 67.2226 | -0.075836 | -0.0010873 | 0.061171 | 0.070754 | -0.0028304 | 0.0019781 | 0.0056354 | -0.0043946 | 0.00046135 | 0.0012818 | -0.010194 | -0.0012925 | -0.0038709 | 0.0010937 | -53.064 | 67.2043 | -55.6458 | 67.0074 | -55.0735 | -55.4031 | -54.8035 | -54.5517 | 67.2318 | -55.6458 | -55.4718 | -55.5588 | -55.687 | -55.4123 | -0.064087 | -0.01831 | -0.21515 | 0.50812 | 0.7782 | 0.17853 | 0.84229 | 0.24262 | -0.064087 | 0.009155 | -122.6944 | 0.022888 | 0.16937 | -0.10529 | 0.23346 | -0.041199 | 0.57221 | 122.6532 | 0.086975 | 0.17395 | 122.85 | 122.8775 | 122.7859 | 122.8134 | -122.8683 | -122.8683 | 122.5891 | 0.10986 | 2.5177 | 1.03
2858.1719 | 123.0194 | -55.6091 | 67.1356 | -0.083466 | -0.0019417 | 0.060744 | 0.069472 | -0.0026168 | 0.0032599 | 0.0073444 | 0.044434 | 0.00088875 | -0.00021357 | -0.003999 | -0.0017197 | -0.0068615 | -0.0016833 | -53.0319 | 67.1768 | -55.6229 | 67.1036 | -54.9728 | -55.3207 | -54.6936 | -54.4144 | 67.2043 | -55.6366 | -55.2383 | -55.2155 | -55.8426 | -55.5267 | -0.013733 | 0.041199 | -0.032043 | 0.63629 | 0.91553 | 0.28839 | 0.92926 | 0.30212 | -0.027466 | 0.068665 | -122.374 | 0.39368 | 0.082398 | -0.23346 | 0.10986 | -0.20599 | 0.65002 | 122.7264 | 0.42114 | 0.39825 | 122.7997 | 122.8409 | 122.7859 | 122.8134 | -122.7585 | -122.7722 | 122.7127 | 0.37079 | 2.5772 | 1.1948
2859.1719 | 123.0743 | -55.5817 | 67.1997 | -0.045319 | -0.00066014 | 0.059676 | 0.070113 | -0.0051804 | 0.0036871 | 0.00414 | 0.041382 | 0.0013159 | 0.0021362 | -0.0033582 | -0.0036423 | -0.0051527 | -0.00040166 | -53.0411 | 67.1814 | -55.6503 | 67.0853 | -54.982 | -55.3345 | -54.7028 | -54.4098 | 67.2089 | -55.6046 | -55.3482 | -55.4535 | -55.5679 | -55.2887 | -0.068665 | -0.018311 | -0.11444 | 0.59967 | 0.87891 | 0.24719 | 0.94757 | 0.31586 | -0.022888 | 0.009155 | -122.5479 | 0.12817 | 0.29297 | 0.013733 | 0.31586 | 0.036621 | 0.66833 | 122.7356 | 0.15106 | 0.25635 | 122.8317 | 122.8134 | 122.7631 | 122.7905 | -122.85 | -122.8043 | 122.6669 | 0.23346 | 2.5406 | 1.1719
2860.1719 | 123.0515 | -55.5634 | 67.2043 | -0.098725 | 0.0014761 | 0.062453 | 0.067123 | -0.0030442 | 0.0013373 | 0.00414 | 0.029175 | 0.00046135 | 0.0012818 | 0.002196 | -0.0025741 | -0.0070753 | 0.00045294 | -53.0411 | 67.1951 | -55.6137 | 67.0807 | -54.9728 | -55.3253 | -54.7165 | -54.4189 | 67.218 | -55.6274 | -55.3253 | -55.4214 | -55.5679 | -55.2933 | -0.050354 | -0.009156 | -0.1236 | 0.59051 | 0.84686 | 0.23804 | 0.89722 | 0.28839 | -0.064087 | 0.013733 | -122.5296 | 0.14191 | 0.27008 | -0.004578 | 0.33417 | 0.059509 | 0.64087 | 122.6944 | 0.20599 | 0.30212 | 122.8088 | 122.8455 | 122.7585 | 122.7814 | -122.818 | -122.8317 | 122.644 | 0.23804 | 2.5223 | 1.1444
2861.1719 | 122.8729 | -55.6274 | 67.2226 | -0.083466 | -0.0013009 | 0.060744 | 0.070754 | 0.003151 | 0.0024053 | 0.0071308 | -0.06543 | 0.0013159 | 0.001709 | 0.0015552 | -0.0034287 | -0.0034437 | 0.0034435 | -53.0228 | 67.2363 | -55.6366 | 67.0166 | -55.0827 | -55.4443 | -54.8172 | -54.5059 | 67.2546 | -55.6366 | -55.4077 | -55.5359 | -55.6641 | -55.3802 | -0.009156 | 0.013733 | -0.20599 | 0.54474 | 0.81024 | 0.1831 | 0.8194 | 0.19226 | -0.009156 | 0.032044 | -122.6303 | 0.091552 | 0.24719 | -0.036621 | 0.25635 | -0.027465 | 0.55389 | 122.6532 | 0.10071 | 0.22888 | 122.8729 | 122.8912 | 122.8638 | 122.8821 | -122.8592 | -122.8592 | 122.644 | 0.21973 | 2.6047 | 1.1215
2862.1719 | 123.0286 | -55.5817 | 67.2134 | -0.12924 | 0.00083526 | 0.06053 | 0.070327 | -0.0028304 | 0.00091009 | 0.0062762 | 0.035278 | -0.00082025 | 0.0019226 | -0.0018628 | -0.0019333 | -0.0057935 | -0.0051013 | -53.0823 | 67.1906 | -55.6458 | 67.0212 | -55.069 | -55.3986 | -54.7668 | -54.5105 | 67.2226 | -55.6046 | -55.3848 | -55.4718 | -55.6 | -55.3299 | -0.064087 | -0.022888 | -0.19226 | 0.5127 | 0.81482 | 0.1831 | 0.87891 | 0.24719 | -0.022888 | 0.009155 | -122.5983 | 0.10986 | 0.25177 | -0.018311 | 0.27466 | 0.004577 | 0.57678 | 122.6669 | 0.13275 | 0.21973 | 122.8363 | 122.8271 | 122.7722 | 122.8043 | -122.8592 | -122.818 | 122.6028 | 0.19684 | 2.4994 | 1.0712
2863.1719 | 123.0423 | -55.5634 | 67.218 | -0.075836 | 0.00019446 | 0.062025 | 0.068404 | -0.00048063 | 0.0013373 | 0.0026446 | 0.016968 | 0.0019567 | -0.0014954 | 0.0024096 | -0.0030013 | -0.0057935 | -0.0010425 | -53.0182 | 67.1906 | -55.5954 | 67.099 | -54.9957 | -55.3299 | -54.7211 | -54.4098 | 67.2226 | -55.6046 | -55.3482 | -55.4443 | -55.5588 | -55.3024 | -0.032044 | -0.027466 | -0.11902 | 0.56763 | 0.84228 | 0.23346 | 0.87433 | 0.2655 | -0.041199 | 0.004577 | -122.5662 | 0.11902 | 0.26093 | 0.004577 | 0.30212 | 0.045776 | 0.59967 | 122.6944 | 0.16022 | 0.25635 | 122.7859 | 122.8271 | 122.7539 | 122.7859 | -122.8134 | -122.8226 | 122.6624 | 0.21515 | 2.5452 | 1.1536
2864.1719 | 123.0469 | -55.5679 | 67.1997 | -0.060578 | 0.00062166 | 0.061171 | 0.067763 | -0.0030442 | 0.0015509 | 0.0043536 | 0.029175 | 0.00088875 | -0.00042717 | 0.0015552 | -0.0030013 | -0.0055799 | 0.00088014 | -53.064 | 67.218 | -55.6229 | 67.0624 | -55.0369 | -55.3665 | -54.7348 | -54.4785 | 67.2501 | -55.6229 | -55.3619 | -55.4581 | -55.5862 | -55.2933 | -0.054932 | 0.018311 | -0.13733 | 0.53101 | 0.83313 | 0.20142 | 0.88806 | 0.25635 | -0.054932 | 0.050354 | -122.5616 | 0.10986 | 0.27466 | -0.018311 | 0.32959 | 0.036621 | 0.58594 | 122.6852 | 0.16479 | 0.26093 | 122.8409 | 122.8729 | 122.7859 | 122.818 | -122.8226 | -122.8226 | 122.6303 | 0.20599 | 2.504 | 1.0895
2865.1719 | 123.056 | -55.545 | 67.2089 | -0.091095 | -0.0010873 | 0.061171 | 0.0699 | 0.0029374 | -0.0010125 | 0.0049946 | 0.02002 | -0.00060665 | 0.00021363 | -0.0014356 | -0.0032151 | -0.0045117 | -0.0036059 | -53.0777 | 67.2089 | -55.5634 | 67.1219 | -55.0415 | -55.3299 | -54.689 | -54.3869 | 67.2318 | -55.5954 | -55.3482 | -55.4306 | -55.5679 | -55.2795 | -0.01831 | 0 | -0.086975 | 0.50354 | 0.85602 | 0.21515 | 0.87433 | 0.23346 | -0.050354 | 0.022888 | -122.5571 | 0.11444 | 0.2655 | -0.022888 | 0.31586 | 0.027466 | 0.52185 | 122.6852 | 0.1648 | 0.24719 | 122.7722 | 122.8271 | 122.7539 | 122.7768 | -122.7722 | -122.8043 | 122.6669 | 0.19684 | 2.4673 | 1.1581
2866.1719 | 123.0103 | -55.5634 | 67.1997 | -0.12924 | 0.0010489 | 0.061171 | 0.069259 | -0.00026703 | 0.0034735 | 0.0037128 | 0.013916 | 0.00024775 | 0.0019226 | 0.0024096 | -0.0010787 | -0.0030163 | 0.00066654 | -53.0502 | 67.2134 | -55.6229 | 67.0486 | -55.0507 | -55.3848 | -54.7531 | -54.4739 | 67.218 | -55.6 | -55.3757 | -55.4672 | -55.5908 | -55.2933 | -0.05951 | 0.013733 | -0.15106 | 0.51269 | 0.81024 | 0.17853 | 0.86975 | 0.23804 | -0.036622 | 0.018311 | -122.5754 | 0.09613 | 0.27008 | -0.027466 | 0.3067 | 0.009156 | 0.5722 | 122.6715 | 0.13275 | 0.22431 | 122.8363 | 122.818 | 122.7768 | 122.7814 | -122.8226 | -122.7997 | 122.612 | 0.18768 | 2.5131 | 1.0895
2867.1719 | 123.0469 | -55.5313 | 67.2134 | -0.052948 | -0.00023294 | 0.060744 | 0.069686 | -0.0021896 | 0.0024053 | 0.0067036 | 0.02002 | 0.00067495 | 0.0021362 | -0.0020764 | -0.0025741 | -0.0060071 | 0.0010937 | -53.0365 | 67.218 | -55.6091 | 67.0807 | -54.9866 | -55.3207 | -54.7028 | -54.4189 | 67.2318 | -55.5725 | -55.3345 | -55.3986 | -55.545 | -55.275 | -0.07782 | 0.004578 | -0.13275 | 0.54474 | 0.82855 | 0.21057 | 0.90637 | 0.28839 | -0.041199 | 0.01831 | -122.5479 | 0.13275 | 0.25635 | -0.013733 | 0.29755 | 0.027466 | 0.62256 | 122.6898 | 0.17395 | 0.23804 | 122.8271 | 122.8043 | 122.7493 | 122.7631 | -122.8226 | -122.786 | 122.612 | 0.19684 | 2.4948 | 1.1124
2868.1719 | 123.0881 | -55.5496 | 67.2134 | -0.098725 | -1.9142e-05 | 0.061385 | 0.068618 | -0.00026703 | 0.0026191 | 0.0034992 | 0.013916 | -0.00082025 | 0.00042723 | 0.0034778 | -0.0017197 | -0.0032301 | 0.00088014 | -53.0182 | 67.2089 | -55.6 | 67.0807 | -55.0095 | -55.3482 | -54.6936 | -54.4327 | 67.2684 | -55.6046 | -55.3436 | -55.4077 | -55.5405 | -55.2933 | -0.050354 | -0.004578 | -0.13275 | 0.54016 | 0.85602 | 0.20142 | 0.90637 | 0.25177 | -0.054931 | 0.054932 | -122.5571 | 0.14191 | 0.25635 | 0.009156 | 0.31128 | 0.064087 | 0.59052 | 122.6807 | 0.19684 | 0.26093 | 122.8088 | 122.8729 | 122.7585 | 122.818 | -122.8134 | -122.818 | 122.6303 | 0.20599 | 2.5314 | 1.1169
2869.1719 | 122.9599 | -55.5496 | 67.2684 | -0.12161 | 0.00083526 | 0.059248 | 0.0699 | -0.00048063 | 0.00069649 | 0.007558 | 0.010864 | 0.00088875 | -0.0019226 | 0.0017688 | -0.0023605 | -0.0053663 | 0.0025891 | -52.9953 | 67.2272 | -55.5679 | 67.099 | -55.0095 | -55.3391 | -54.7119 | -54.4739 | 67.2592 | -55.5542 | -55.3894 | -55.4947 | -55.6229 | -55.3253 | -0.01831 | -0.041199 | -0.16937 | 0.54016 | 0.83771 | 0.21057 | 0.85602 | 0.22888 | -0.004577 | -0.009156 | -122.6578 | 0.054932 | 0.22431 | -0.073242 | 0.22888 | -0.068665 | 0.55847 | 122.6669 | 0.059509 | 0.16479 | 122.7951 | 122.8134 | 122.7768 | 122.8088 | -122.8363 | -122.8226 | 122.6486 | 0.16022 | 2.5543 | 1.0757
2870.1719 | 123.0469 | -55.5313 | 67.2226 | 0.038605 | 0.00083526 | 0.065871 | 0.071395 | 0.00251 | 0.0021917 | 0.0060626 | -0.0074462 | 0.0030249 | 0.001068 | -0.0010084 | -0.0021469 | -0.0047253 | -0.00082886 | -53.1967 | 67.218 | -55.5862 | 67.1265 | -54.9683 | -55.3024 | -54.657 | -54.3915 | 67.2638 | -55.5679 | -55.3207 | -55.4214 | -55.5496 | -55.2612 | -0.054932 | -0.004577 | -0.09613 | 0.56305 | 0.87433 | 0.22888 | 0.92926 | 0.28381 | -0.036621 | 0.041199 | -122.5433 | 0.10986 | 0.27008 | -0.018311 | 0.3067 | 0.01831 | 0.61798 | 122.7127 | 0.14648 | 0.24719 | 122.8043 | 122.8317 | 122.7493 | 122.7951 | -122.8088 | -122.7905 | 122.6578 | 0.21057 | 2.3346 | 1.1398
2871.1719 | 123.0515 | -55.5267 | 67.2455 | -0.052948 | -0.0017281 | 0.061171 | 0.069472 | 0.0016556 | 0.0034735 | 0.0069172 | 0.016968 | 0.0028113 | 0.0019226 | -0.00015378 | -0.0034287 | -0.0057935 | -0.0012561 | -52.9861 | 67.218 | -55.5862 | 67.1265 | -54.9637 | -55.3207 | -54.6799 | -54.3686 | 67.2546 | -55.5679 | -55.2933 | -55.4031 | -55.5084 | -55.2475 | -0.05951 | -0.027465 | -0.11902 | 0.56305 | 0.84686 | 0.20599 | 0.90637 | 0.2655 | -0.041199 | 0.009156 | -122.5388 | 0.1236 | 0.27923 | 0.01831 | 0.32043 | 0.059509 | 0.62256 | 122.7127 | 0.16479 | 0.27466 | 122.8043 | 122.8226 | 122.7448 | 122.7814 | -122.8317 | -122.8134 | 122.6532 | 0.23346 | 2.5406 | 1.1581
2872.1719 | 122.9736 | -55.5634 | 67.218 | -0.068207 | -0.00044654 | 0.060957 | 0.068618 | -0.00069423 | 0.00069649 | 0.007558 | 0.0047608 | 0.00024775 | 2.8e-08 | -0.001222 | -0.0017197 | -0.0068615 | -0.00082886 | -53.0319 | 67.2226 | -55.5908 | 67.0624 | -55.0323 | -55.3757 | -54.744 | -54.5197 | 67.2638 | -55.5679 | -55.3848 | -55.4581 | -55.5954 | -55.307 | -0.027466 | 0.004577 | -0.15564 | 0.531 | 0.8194 | 0.18768 | 0.84686 | 0.21515 | -0.004578 | 0.045776 | -122.6028 | 0.10528 | 0.25635 | -0.032044 | 0.26093 | -0.027466 | 0.55847 | 122.6532 | 0.10986 | 0.1831 | 122.8134 | 122.8317 | 122.7859 | 122.8271 | -122.8088 | -122.7859 | 122.6257 | 0.17853 | 2.5314 | 1.0437
2873.1719 | 122.9233 | -55.5634 | 67.2913 | -0.022431 | 0.00083526 | 0.060957 | 0.071395 | -0.0011214 | -0.0010125 | 0.0032856 | -0.06543 | 0.0017431 | 0.0012818 | 0.0019824 | -0.0017197 | -0.0047253 | -0.00061526 | -53.0228 | 67.2775 | -55.6 | 67.0074 | -55.2155 | -55.5313 | -54.7577 | -54.5425 | 67.3233 | -55.5908 | -55.3986 | -55.513 | -55.6549 | -55.3619 | -0.036622 | -0.013733 | -0.28381 | 0.3479 | 0.80566 | 0.032043 | 0.84229 | 0.068665 | -0.027466 | 0.032043 | -122.6898 | 0.050354 | 0.20142 | -0.091553 | 0.22888 | -0.064087 | 0.38452 | 122.6074 | 0.07782 | 0.19226 | 122.8775 | 122.9141 | 122.8409 | 122.8867 | -122.8912 | -122.8821 | 122.5708 | 0.16479 | 2.5406 | 1.0208
2874.1719 | 123.0057 | -55.5359 | 67.2546 | -0.15213 | -0.0015145 | 0.06288 | 0.068191 | -0.001976 | 0.0041143 | 0.0049946 | 0.010864 | 0.00088875 | -0.00021357 | -0.001222 | -0.0021469 | -0.0053663 | -0.00061526 | -53.009 | 67.2363 | -55.5862 | 67.067 | -55.014 | -55.3665 | -54.7119 | -54.4739 | 67.2775 | -55.5862 | -55.3574 | -55.4581 | -55.5588 | -55.2841 | -0.050354 | -0.018311 | -0.18768 | 0.52185 | 0.82397 | 0.16937 | 0.87433 | 0.21973 | -0.050354 | 0.022888 | -122.612 | 0.07782 | 0.25177 | -0.022888 | 0.30212 | 0.027466 | 0.57221 | 122.6532 | 0.12817 | 0.22888 | 122.8226 | 122.8638 | 122.7722 | 122.8134 | -122.8409 | -122.8409 | 122.6028 | 0.17853 | 2.5269 | 1.062
2875.1719 | 123.0515 | -55.5176 | 67.2592 | -0.075836 | 0.0014761 | 0.059462 | 0.069686 | 0.003151 | 0.0030463 | 0.0028582 | 0.016968 | 0.00067495 | -0.00042717 | -0.0037854 | -0.00043791 | -0.0042981 | -0.00018806 | -52.9999 | 67.2501 | -55.5771 | 67.1082 | -54.9683 | -55.2979 | -54.6753 | -54.4189 | 67.2821 | -55.5542 | -55.2933 | -55.4077 | -55.5222 | -55.2475 | -0.059509 | -0.009155 | -0.15106 | 0.54932 | 0.84228 | 0.21973 | 0.90179 | 0.27923 | -0.036621 | 0.022888 | -122.5525 | 0.10986 | 0.27008 | -0.004578 | 0.3067 | 0.032043 | 0.60882 | 122.6852 | 0.14648 | 0.26093 | 122.8271 | 122.8363 | 122.7676 | 122.7997 | -122.8363 | -122.8134 | 122.6257 | 0.2243 | 2.5177 | 1.0986
2876.1719 | 123.0331 | -55.5084 | 67.2775 | -0.075836 | -0.00044654 | 0.062666 | 0.070754 | 0.0012284 | 0.00048269 | 0.0049946 | 0.0047608 | 0.0017431 | 0.00021363 | 0.0017688 | -0.00086511 | -0.0055799 | -0.0029651 | -52.9861 | 67.2363 | -55.5634 | 67.1173 | -54.9591 | -55.3207 | -54.6661 | -54.4144 | 67.2821 | -55.5542 | -55.2887 | -55.3986 | -55.5405 | -55.2475 | -0.054931 | -0.041199 | -0.16022 | 0.54932 | 0.84229 | 0.18768 | 0.89722 | 0.24261 | -0.045776 | 0.004577 | -122.5662 | 0.10986 | 0.26093 | -0.032043 | 0.3067 | 0.013733 | 0.60425 | 122.6807 | 0.15564 | 0.2655 | 122.7997 | 122.8363 | 122.7448 | 122.7905 | -122.8409 | -122.8317 | 122.6257 | 0.21973 | 2.5223 | 1.0941
2877.1719 | 122.937 | -55.5084 | 67.3004 | -0.098725 | -0.00023294 | 0.062666 | 0.067123 | 0.0012284 | 0.0024053 | 0.0069172 | -0.0013428 | 0.00024775 | 0.0012818 | -0.00464 | -0.0032151 | -0.0062207 | 0.00045294 | -52.9449 | 67.2638 | -55.5542 | 67.1265 | -54.9316 | -55.2841 | -54.6616 | -54.4189 | 67.3004 | -55.545 | -55.3391 | -55.4306 | -55.5817 | -55.2933 | -0.045776 | -0.036621 | -0.17395 | 0.57678 | 0.84686 | 0.2243 | 0.89264 | 0.27008 | -0.036621 | 0 | -122.6395 | 0.07782 | 0.21515 | -0.073242 | 0.25177 | -0.036621 | 0.62256 | 122.6807 | 0.11444 | 0.20599 | 122.818 | 122.8455 | 122.7722 | 122.8088 | -122.8546 | -122.8455 | 122.6349 | 0.16937 | 2.5635 | 1.0895
2878.1719 | 122.9919 | -55.5038 | 67.2775 | -0.11398 | -0.00087374 | 0.06053 | 0.069259 | -0.00026703 | 0.0021917 | 0.0062762 | -0.019653 | -0.00017945 | 0.00021363 | 0.0019824 | -0.0017197 | -0.0060071 | -0.0021107 | -52.9221 | 67.2775 | -55.5496 | 67.1402 | -54.95 | -55.2704 | -54.657 | -54.3961 | 67.337 | -55.5359 | -55.3116 | -55.4306 | -55.5496 | -55.2704 | -0.045777 | 0 | -0.13733 | 0.55389 | 0.84686 | 0.23346 | 0.89264 | 0.27924 | -0.032044 | 0.059509 | -122.5891 | 0.073242 | 0.23346 | -0.045777 | 0.2655 | -0.013733 | 0.59967 | 122.6898 | 0.10529 | 0.2243 | 122.8271 | 122.8729 | 122.7814 | 122.8409 | -122.8271 | -122.8134 | 122.644 | 0.19226 | 2.5818 | 1.1078
2879.1719 | 123.0148 | -55.4993 | 67.2775 | -0.091095 | 0.00040806 | 0.062025 | 0.068191 | -0.0026168 | 0.0024053 | 0.005849 | 0.013916 | 0.00067495 | 0.001709 | -0.0042126 | -0.0019333 | -0.0062207 | -0.0010425 | -52.9816 | 67.2821 | -55.5817 | 67.1036 | -54.9774 | -55.3162 | -54.6844 | -54.4235 | 67.2913 | -55.545 | -55.3116 | -55.3802 | -55.5313 | -55.2429 | -0.082397 | 0.004577 | -0.17395 | 0.52185 | 0.81482 | 0.18311 | 0.89722 | 0.2655 | -0.045776 | 0.013733 | -122.5891 | 0.11902 | 0.25635 | -0.032043 | 0.30212 | 0.013733 | 0.60425 | 122.6852 | 0.16479 | 0.23346 | 122.8638 | 122.8363 | 122.7814 | 122.7905 | -122.8592 | -122.8226 | 122.6028 | 0.18768 | 2.5177 | 1.0757
2880.1719 | 123.0194 | -55.4993 | 67.2638 | -0.12924 | -0.0013009 | 0.061598 | 0.070113 | -0.0017624 | 0.0047553 | 0.0037128 | -0.0074462 | 0.00088875 | 0.001068 | 0.0043322 | -0.0015061 | -0.0064343 | -0.0010425 | -52.9953 | 67.2775 | -55.5679 | 67.099 | -54.982 | -55.307 | -54.6707 | -54.4235 | 67.2775 | -55.5267 | -55.2979 | -55.3802 | -55.5222 | -55.2658 | -0.068664 | 0.013733 | -0.16479 | 0.51727 | 0.82855 | 0.19226 | 0.89722 | 0.26093 | -0.027465 | 0.013733 | -122.5616 | 0.11902 | 0.23346 | -0.022888 | 0.26093 | 0.004577 | 0.58594 | 122.6669 | 0.14648 | 0.22888 | 122.8455 | 122.8043 | 122.7768 | 122.7768 | -122.8317 | -122.7905 | 122.5983 | 0.20142 | 2.504 | 1.0757
2881.1719 | 123.0286 | -55.4901 | 67.3187 | -0.12924 | 0.0010489 | 0.061598 | 0.070327 | -0.0028304 | 0.0026191 | 0.0017902 | -0.0043946 | -0.00082025 | 0.0012818 | 0.0017688 | -0.0019333 | -0.0051527 | 0.00066654 | -52.9221 | 67.2684 | -55.5267 | 67.1631 | -54.9271 | -55.2612 | -54.6433 | -54.364 | 67.3141 | -55.513 | -55.275 | -55.3757 | -55.5038 | -55.2246 | -0.036621 | -0.050354 | -0.15564 | 0.56305 | 0.84686 | 0.22888 | 0.88348 | 0.2655 | -0.022888 | -0.004578 | -122.5937 | 0.11444 | 0.2655 | -0.013733 | 0.28839 | 0.009155 | 0.59967 | 122.6898 | 0.13733 | 0.23804 | 122.7951 | 122.8271 | 122.7585 | 122.8043 | -122.8455 | -122.8317 | 122.6532 | 0.21515 | 2.5681 | 1.1261
2882.1719 | 123.0103 | -55.4901 | 67.2775 | -0.12161 | 0.00040806 | 0.061812 | 0.069686 | 0.0012284 | 5.5488e-05 | 0.0073444 | -0.0013428 | 0.00067495 | 0.00064083 | -0.00036738 | -0.0025741 | -0.0055799 | 0.00023934 | -52.977 | 67.2729 | -55.545 | 67.1036 | -54.9911 | -55.3207 | -54.689 | -54.4235 | 67.305 | -55.545 | -55.2933 | -55.4077 | -55.545 | -55.2475 | -0.054932 | -0.004578 | -0.17395 | 0.49896 | 0.80109 | 0.16937 | 0.85602 | 0.2243 | -0.054932 | 0.027466 | -122.5708 | 0.082397 | 0.24261 | -0.054932 | 0.29755 | 0 | 0.55389 | 122.6486 | 0.13733 | 0.25177 | 122.818 | 122.85 | 122.7631 | 122.7951 | -122.8226 | -122.8226 | 122.5937 | 0.19684 | 2.5131 | 1.0666
2883.1719 | 123.0469 | -55.4764 | 67.3187 | -0.037689 | -1.9142e-05 | 0.058821 | 0.068832 | -5.343e-05 | 0.0024053 | 0.0043536 | -0.0043946 | -0.0012477 | -0.00042717 | 0.002196 | -0.0025741 | -0.0030163 | 0.0013073 | -52.9175 | 67.2775 | -55.5359 | 67.1768 | -54.9042 | -55.2383 | -54.6204 | -54.3503 | 67.3141 | -55.5313 | -55.2429 | -55.3665 | -55.4855 | -55.22 | -0.05951 | -0.041199 | -0.14191 | 0.5722 | 0.85602 | 0.23804 | 0.91553 | 0.29755 | -0.054932 | -0.004578 | -122.5616 | 0.10986 | 0.25635 | -0.009156 | 0.31128 | 0.045776 | 0.63171 | 122.7127 | 0.1648 | 0.28839 | 122.8134 | 122.8455 | 122.7539 | 122.7905 | -122.8546 | -122.85 | 122.6532 | 0.23346 | 2.5589 | 1.1261
2884.1719 | 123.0606 | -55.4489 | 67.3187 | -0.11398 | -0.00066014 | 0.060957 | 0.068832 | -0.0034714 | 0.0036871 | 0.0015766 | 0.035278 | 0.00088875 | 0.001709 | -0.0020764 | -0.0036423 | -0.0045117 | -0.00061526 | -52.9495 | 67.2913 | -55.5405 | 67.1356 | -54.9454 | -55.275 | -54.6524 | -54.3594 | 67.3141 | -55.5313 | -55.2521 | -55.3619 | -55.5038 | -55.2063 | -0.091552 | -0.027466 | -0.18311 | 0.50354 | 0.79651 | 0.17395 | 0.88806 | 0.2655 | -0.082397 | -0.004578 | -122.5708 | 0.086976 | 0.24262 | -0.054931 | 0.32501 | 0.027466 | 0.59509 | 122.6761 | 0.16937 | 0.27924 | 122.8317 | 122.8455 | 122.7402 | 122.7631 | -122.8592 | -122.85 | 122.5845 | 0.19684 | 2.4994 | 1.0895
2885.1719 | 123.0469 | -55.4855 | 67.3096 | -0.22079 | 0.0038261 | 0.059248 | 0.069045 | 0.00016017 | 0.0017645 | 0.0073444 | 0.013916 | 3.4148e-05 | 0.0014954 | -0.00229 | -0.0027877 | -0.0057935 | -0.0025379 | -52.9495 | 67.2455 | -55.5267 | 67.1677 | -54.8767 | -55.2063 | -54.6249 | -54.3182 | 67.3233 | -55.513 | -55.2429 | -55.3391 | -55.481 | -55.2017 | -0.041198 | -0.064087 | -0.14191 | 0.60883 | 0.8606 | 0.27924 | 0.90179 | 0.32043 | -0.027465 | 0.013733 | -122.5525 | 0.14648 | 0.28381 | 0.004578 | 0.31128 | 0.032043 | 0.65002 | 122.6944 | 0.17395 | 0.27008 | 122.7722 | 122.8363 | 122.731 | 122.8088 | -122.8363 | -122.8226 | 122.6532 | 0.24262 | 2.536 | 1.1673
2886.1719 | 123.0515 | -55.4535 | 67.305 | -0.15976 | 0.0021171 | 0.062239 | 0.069259 | -0.00026703 | 0.0032599 | 0.0032856 | 0.02002 | 0.00024775 | 0.0014954 | -0.0018628 | -0.0012925 | -0.0064343 | 2.554e-05 | -52.8992 | 67.2775 | -55.5267 | 67.1906 | -54.8904 | -55.2292 | -54.5837 | -54.3137 | 67.3233 | -55.5084 | -55.2292 | -55.3116 | -55.426 | -55.1926 | -0.073242 | -0.027466 | -0.11444 | 0.56305 | 0.86975 | 0.2243 | 0.94299 | 0.29755 | -0.054932 | 0.01831 | -122.5342 | 0.14191 | 0.26093 | 0.027466 | 0.31586 | 0.082398 | 0.63629 | 122.7173 | 0.19684 | 0.27924 | 122.8043 | 122.8317 | 122.731 | 122.7768 | -122.8317 | -122.8134 | 122.644 | 0.2243 | 2.5543 | 1.1398
2887.1719 | 123.0606 | -55.4489 | 67.3187 | -0.12161 | -0.0015145 | 0.060103 | 0.070327 | -0.0017624 | 0.0049689 | 0.007558 | 0.041382 | 0.0032385 | -0.00064077 | -0.00015378 | -0.0019333 | -0.0072889 | 0.00066654 | -52.9083 | 67.2867 | -55.5222 | 67.1951 | -54.8996 | -55.2383 | -54.6112 | -54.2953 | 67.3233 | -55.4855 | -55.2155 | -55.3207 | -55.4443 | -55.1651 | -0.073242 | -0.032044 | -0.1236 | 0.54932 | 0.83771 | 0.21057 | 0.91095 | 0.28381 | -0.036621 | 0.004577 | -122.5342 | 0.12817 | 0.28381 | 0.004578 | 0.32043 | 0.041199 | 0.62256 | 122.7173 | 0.16479 | 0.27008 | 122.8088 | 122.8088 | 122.7356 | 122.7722 | -122.8409 | -122.8043 | 122.644 | 0.23346 | 2.5406 | 1.1536
2888.1719 | 122.9874 | -55.4718 | 67.3416 | -0.10635 | 0.00040806 | 0.059676 | 0.069259 | -0.0011214 | 0.00026909 | 0.0049946 | -0.0043946 | -0.00060665 | 0.00085443 | 0.0019824 | -0.0017197 | -0.0040845 | -0.0012561 | -52.8946 | 67.305 | -55.5038 | 67.1997 | -54.9042 | -55.2383 | -54.6158 | -54.3365 | 67.3737 | -55.5084 | -55.2612 | -55.3482 | -55.5084 | -55.1926 | -0.032043 | -0.036621 | -0.14191 | 0.56763 | 0.85602 | 0.23346 | 0.88806 | 0.2655 | -0.036621 | 0.032043 | -122.6028 | 0.1236 | 0.27924 | -0.036621 | 0.31586 | 0 | 0.59967 | 122.7036 | 0.16022 | 0.24719 | 122.8088 | 122.8821 | 122.7768 | 122.8455 | -122.8455 | -122.85 | 122.6715 | 0.21057 | 2.5772 | 1.1353
2889.1719 | 123.0148 | -55.4398 | 67.337 | -0.083466 | 0.00083526 | 0.060744 | 0.0699 | -0.00069423 | 0.00091009 | 0.0045672 | 0.0078126 | 0.00067495 | -0.00021357 | -0.002931 | -0.0019333 | -0.0060071 | -0.00040166 | -52.8671 | 67.3141 | -55.4626 | 67.1951 | -54.8767 | -55.2292 | -54.6066 | -54.3045 | 67.3462 | -55.4855 | -55.2429 | -55.3391 | -55.4993 | -55.1971 | -0.022888 | -0.022888 | -0.14191 | 0.56305 | 0.83313 | 0.21057 | 0.85602 | 0.23346 | -0.045777 | 0.009155 | -122.58 | 0.10071 | 0.24261 | -0.05951 | 0.28839 | -0.013733 | 0.58594 | 122.6578 | 0.14648 | 0.24262 | 122.7768 | 122.8317 | 122.7539 | 122.7859 | -122.7997 | -122.8226 | 122.6349 | 0.19684 | 2.5726 | 1.1353
2890.1719 | 123.0377 | -55.4626 | 67.2913 | -0.075836 | 0.00019446 | 0.060957 | 0.068404 | 0.0018692 | 0.0028327 | 0.003072 | -0.0074462 | 0.0017431 | -0.001709 | -0.0086988 | -0.0015061 | -0.0055799 | 0.0013073 | -52.9495 | 67.3004 | -55.5496 | 67.1448 | -54.9408 | -55.2887 | -54.6387 | -54.3823 | 67.3508 | -55.5038 | -55.2612 | -55.3711 | -55.4901 | -55.2109 | -0.086976 | 0.009155 | -0.14648 | 0.52185 | 0.82397 | 0.17395 | 0.91095 | 0.26093 | -0.041199 | 0.059509 | -122.5525 | 0.091552 | 0.25177 | -0.027466 | 0.29297 | 0.013733 | 0.60883 | 122.6944 | 0.13275 | 0.24262 | 122.85 | 122.8546 | 122.7631 | 122.8134 | -122.8409 | -122.7951 | 122.6074 | 0.20142 | 2.5131 | 1.0803
2891.1719 | 123.0652 | -55.4764 | 67.3325 | -0.10635 | -0.00087374 | 0.060103 | 0.069472 | 0.0022964 | 0.00026909 | 0.0028582 | 0.013916 | -0.00039305 | 2.8e-08 | 0.002196 | -0.0025741 | -0.0085705 | 0.0010937 | -52.858 | 67.2913 | -55.5084 | 67.2226 | -54.8401 | -55.188 | -54.5517 | -54.245 | 67.3553 | -55.4535 | -54.9866 | -55.5862 | -55.6549 | -55.2338 | -0.032044 | -0.041198 | -0.10986 | 0.63629 | 0.92468 | 0.28839 | 0.95673 | 0.32044 | 0.022888 | 0.022889 | -122.319 | -0.10986 | 0.24261 | -0.17853 | 0.21973 | -0.20142 | 0.66833 | 122.731 | -0.13275 | 0.46692 | 122.7997 | 122.8088 | 122.7676 | 122.8317 | -122.8409 | -122.7859 | 122.699 | 0.48981 | 2.6184 | 1.2314
2892.1719 | 123.0103 | -55.4581 | 67.3279 | -0.098725 | -0.0010873 | 0.061598 | 0.069686 | -0.00048063 | 0.0019781 | 0.0047808 | 0.010864 | 0.0019567 | 0.00085443 | -0.0016492 | 0.00041649 | -0.0047253 | -0.0010425 | -52.8122 | 67.3416 | -55.4855 | 67.1494 | -54.9774 | -55.2979 | -54.6707 | -54.3869 | 67.3508 | -55.4993 | -55.2658 | -55.3574 | -55.4993 | -55.2017 | -0.027466 | 0.013733 | -0.17853 | 0.48065 | 0.78735 | 0.16022 | 0.81482 | 0.18768 | -0.041199 | 0.022888 | -122.5937 | 0.10071 | 0.25635 | -0.041199 | 0.29755 | 0 | 0.50812 | 122.6349 | 0.14191 | 0.23346 | 122.8271 | 122.85 | 122.7997 | 122.8088 | -122.8134 | -122.8271 | 122.6074 | 0.19226 | 2.6459 | 1.0712
2893.1719 | 122.9553 | -55.4672 | 67.392 | -0.060578 | 0.0029715 | 0.061598 | 0.070113 | -5.343e-05 | 0.0047553 | 0.0064898 | -0.08374 | 0.0023839 | 0.0012818 | 0.00027342 | -0.0017197 | -0.0051527 | -0.0018971 | -52.8763 | 67.3508 | -55.5222 | 67.1448 | -54.9316 | -55.2933 | -54.6753 | -54.3686 | 67.3782 | -55.513 | -55.2155 | -55.3757 | -55.5313 | -55.2292 | -0.054932 | -0.041199 | -0.24719 | 0.53558 | 0.79193 | 0.17395 | 0.84686 | 0.22888 | -0.045776 | -0.013733 | -122.6074 | 0.091553 | 0.23804 | -0.064087 | 0.28381 | -0.018311 | 0.59052 | 122.6669 | 0.13733 | 0.29755 | 122.8729 | 122.8912 | 122.818 | 122.8455 | -122.9141 | -122.905 | 122.612 | 0.25177 | 2.5909 | 1.0986
2894.1719 | 123.0423 | -55.4214 | 67.3508 | -0.045319 | 0.0012625 | 0.060957 | 0.068618 | -0.001976 | 0.0034735 | 0.0049946 | 0.001709 | -0.0012477 | 0.00064083 | 0.0019824 | -0.0023605 | -0.0042981 | -0.0016833 | -52.8671 | 67.3462 | -55.4718 | 67.0074 | -54.9225 | -55.1056 | -54.5975 | -54.277 | 67.337 | -55.4718 | -55.2063 | -55.275 | -55.4306 | -55.1514 | -0.050354 | -0.004578 | -0.34332 | 0.49896 | 0.82397 | 0.31586 | 0.87433 | 0.36621 | -0.050354 | -0.013733 | -122.5571 | 0.14648 | 0.27008 | -0.009155 | 0.32043 | 0.041199 | 0.54932 | 122.4792 | 0.19684 | 0.2655 | 122.818 | 122.8088 | 122.7676 | 122.7585 | -122.8226 | -122.8226 | 122.4289 | 0.21515 | 2.5543 | 1.1444
2895.1719 | 123.0743 | -55.4169 | 67.3279 | -0.12924 | 0.00019446 | 0.060316 | 0.067977 | -0.0021896 | 0.0036871 | 0.0045672 | 0.041382 | 0.0011023 | 2.8e-08 | -0.0020764 | -0.0019333 | -0.0040845 | -0.0010425 | -52.8763 | 67.3325 | -55.4672 | 67.1997 | -54.8721 | -55.1971 | -54.5792 | -54.2862 | 67.3782 | -55.4718 | -55.1926 | -55.275 | -55.4123 | -55.1514 | -0.050354 | 0.004577 | -0.12817 | 0.54474 | 0.83771 | 0.21973 | 0.88806 | 0.27008 | -0.054932 | 0.050354 | -122.5204 | 0.14191 | 0.2655 | 0.004578 | 0.32043 | 0.05951 | 0.59509 | 122.6669 | 0.19684 | 0.27924 | 122.7997 | 122.85 | 122.7493 | 122.7951 | -122.7951 | -122.7997 | 122.6166 | 0.2243 | 2.5406 | 1.1307
2896.1719 | 123.0194 | -55.4306 | 67.3462 | -0.075836 | 0.00062166 | 0.059248 | 0.069686 | 0.0022964 | 0.0024053 | 0.0056354 | 0.016968 | 0.00088875 | -0.00042717 | -0.0031446 | -0.0034287 | -0.0062207 | -0.00018806 | -52.8946 | 67.3141 | -55.5038 | 67.1768 | -54.9133 | -55.2658 | -54.6112 | -54.3549 | 67.3599 | -55.4718 | -55.2383 | -55.3253 | -55.4581 | -55.1971 | -0.073242 | -0.032043 | -0.16937 | 0.51727 | 0.8194 | 0.16479 | 0.89264 | 0.23804 | -0.041199 | 0.013733 | -122.5845 | 0.10529 | 0.23346 | -0.027466 | 0.27466 | 0.013733 | 0.59051 | 122.6807 | 0.14648 | 0.23346 | 122.818 | 122.8317 | 122.7448 | 122.7905 | -122.85 | -122.818 | 122.6074 | 0.19226 | 2.536 | 1.0757
2897.1719 | 122.9507 | -55.4489 | 67.4423 | -0.075836 | 0.00019446 | 0.061385 | 0.069045 | 0.0029374 | 0.0015509 | 0.0064898 | -0.022705 | 0.0017431 | 0.00021363 | -0.0027174 | -0.0019333 | -0.0057935 | -0.00061526 | -52.8671 | 67.3462 | -55.4535 | 67.1768 | -54.9042 | -55.2383 | -54.6158 | -54.3503 | 67.4194 | -55.4581 | -55.275 | -55.3802 | -55.5267 | -55.2475 | -0.004577 | -0.096131 | -0.2655 | 0.54474 | 0.83313 | 0.21057 | 0.83771 | 0.21515 | -0.009155 | -0.022888 | -122.7173 | 0.068665 | 0.20142 | -0.077819 | 0.21057 | -0.068664 | 0.54932 | 122.6303 | 0.07782 | 0.18311 | 122.7997 | 122.8775 | 122.7951 | 122.8683 | -122.8958 | -122.9004 | 122.6257 | 0.17395 | 2.5818 | 1.0986
2898.1719 | 122.9279 | -55.4535 | 67.3965 | -0.052948 | 0.00019446 | 0.061812 | 0.071395 | 0.00016017 | 0.0017645 | 0.0060626 | -0.044067 | 0.0019567 | 0.001068 | -0.003999 | 0.00041649 | -0.0032301 | 0.00045294 | -52.9083 | 67.4149 | -55.481 | 67.1448 | -54.9591 | -55.2795 | -54.6433 | -54.3961 | 67.4515 | -55.4443 | -55.3162 | -55.3848 | -55.5725 | -55.2795 | -0.027466 | 0.018311 | -0.25177 | 0.49439 | 0.81024 | 0.17395 | 0.83771 | 0.20142 | 0.009155 | 0.054932 | -122.7127 | 0.068664 | 0.17395 | -0.11902 | 0.16479 | -0.12817 | 0.52185 | 122.6257 | 0.059509 | 0.12817 | 122.8958 | 122.8958 | 122.8683 | 122.905 | -122.8775 | -122.8409 | 122.5983 | 0.13733 | 2.5452 | 1.0574
2899.1719 | 123.0423 | -55.4169 | 67.3508 | -0.091095 | 0.00083526 | 0.063521 | 0.067763 | -0.0038986 | 0.0021917 | 0.0047808 | 0.035278 | -0.00082025 | 0.00064083 | -0.0037854 | -0.00086511 | -0.0049389 | -0.0036059 | -52.89 | 67.3553 | -55.481 | 67.1997 | -54.8676 | -55.22 | -54.5746 | -54.3045 | 67.3599 | -55.4626 | -55.1971 | -55.2795 | -55.4306 | -55.1468 | -0.064087 | 0.004578 | -0.15106 | 0.54932 | 0.84229 | 0.19684 | 0.90637 | 0.26092 | -0.045776 | 0.009155 | -122.5479 | 0.13733 | 0.27008 | -0.013733 | 0.31586 | 0.032043 | 0.6134 | 122.6807 | 0.1831 | 0.2655 | 122.8363 | 122.8226 | 122.7722 | 122.7768 | -122.8317 | -122.8134 | 122.6166 | 0.21973 | 2.5269 | 1.1124
2900.1719 | 122.9919 | -55.4352 | 67.3553 | -0.083466 | -0.0010873 | 0.06053 | 0.0699 | -0.004753 | 0.0026191 | 0.0052082 | -0.0074462 | 0.0011023 | 0.00085443 | -0.0069898 | -0.0025741 | -0.0055799 | -0.0012561 | -52.8946 | 67.3096 | -55.4764 | 67.2134 | -54.8126 | -55.2521 | -54.689 | -54.3594 | 67.3737 | -55.4718 | -55.2383 | -55.3482 | -55.4764 | -55.1834 | -0.041198 | -0.045777 | -0.14191 | 0.62256 | 0.74616 | 0.18311 | 0.78735 | 0.2243 | -0.036621 | 0.01831 | -122.5937 | 0.086975 | 0.25177 | -0.041198 | 0.28839 | -0.004577 | 0.66376 | 122.6898 | 0.1236 | 0.23346 | 122.7859 | 122.8455 | 122.7448 | 122.8088 | -122.8317 | -122.8271 | 122.6486 | 0.19684 | 2.5406 | 1.0757
2901.1719 | 123.0423 | -55.4214 | 67.3874 | -0.12161 | 0.0019035 | 0.061171 | 0.069045 | -0.0015488 | 0.0015509 | 0.0062762 | -0.03186 | 0.00046135 | 0.00042723 | 0.00070062 | -0.0034287 | -0.0045117 | -0.0023243 | -52.8122 | 67.3599 | -55.4581 | 67.1494 | -55.1056 | -55.1926 | -54.5059 | -54.2221 | 67.3645 | -55.4489 | -55.188 | -55.2795 | -55.4077 | -55.1285 | -0.036621 | -0.027466 | -0.23804 | 0.31586 | 0.91553 | 0.22888 | 0.95215 | 0.2655 | -0.027466 | -0.022888 | -122.5754 | 0.14191 | 0.29297 | 0.013733 | 0.32044 | 0.041199 | 0.35248 | 122.6074 | 0.16937 | 0.26093 | 122.818 | 122.8134 | 122.7814 | 122.7859 | -122.8455 | -122.8363 | 122.5708 | 0.23346 | 2.6093 | 1.1993
2902.1719 | 123.0377 | -55.3711 | 67.3737 | -0.12924 | -0.0013009 | 0.062025 | 0.069045 | -0.0017624 | 0.0026191 | 0.0037128 | -0.028809 | 0.0030249 | 0.00021363 | 0.0034778 | -0.0019333 | -0.0049389 | 0.0017345 | -52.7847 | 67.3553 | -55.4535 | 67.2638 | -54.7989 | -55.0049 | -54.2679 | -54.3594 | 67.392 | -55.4398 | -55.1834 | -55.2704 | -55.3711 | -55.1193 | -0.082397 | -0.01831 | -0.10986 | 0.5722 | 1.1032 | 0.36621 | 1.1856 | 0.44861 | -0.068664 | 0.018311 | -122.5571 | 0.10071 | 0.25177 | 0 | 0.32043 | 0.068664 | 0.6546 | 122.7173 | 0.16937 | 0.25635 | 122.8088 | 122.8317 | 122.7264 | 122.7631 | -122.8271 | -122.8134 | 122.6349 | 0.18768 | 2.5864 | 1.0117
2903.1719 | 122.937 | -55.4169 | 67.4194 | -0.091095 | 0.00040806 | 0.060316 | 0.070968 | -0.00026703 | 0.0017645 | 0.0037128 | -0.047119 | 0.00088875 | -0.0010682 | 0.0019824 | -0.0027877 | -0.0045117 | -0.00040166 | -52.8671 | 67.4561 | -55.481 | 67.1722 | -54.7028 | -55.2704 | -54.7531 | -54.3915 | 67.4515 | -55.4581 | -55.2612 | -55.3802 | -55.5267 | -55.2338 | -0.064087 | 0.036621 | -0.24719 | 0.71411 | 0.66376 | 0.14648 | 0.72784 | 0.21057 | -0.041199 | 0.032043 | -122.6807 | 0.036621 | 0.18311 | -0.10986 | 0.2243 | -0.068664 | 0.7782 | 122.6532 | 0.07782 | 0.19684 | 122.937 | 122.9095 | 122.8729 | 122.8683 | -122.9004 | -122.8775 | 122.5891 | 0.15564 | 2.5497 | 1.0254
2904.1719 | 123.024 | -55.4077 | 67.3645 | -0.11398 | 0.00062166 | 0.061385 | 0.067977 | 0.00251 | 0.0017645 | 0.0043536 | -0.0074462 | 3.4148e-05 | 2.8e-08 | -0.007417 | -0.00065151 | -0.0057935 | -0.0040333 | -52.89 | 67.3553 | -55.4443 | 67.1768 | -54.895 | -55.2383 | -54.5975 | -54.3228 | 67.4149 | -55.4672 | -55.2017 | -55.307 | -55.4581 | -55.1605 | -0.036621 | -0.009155 | -0.18768 | 0.5127 | 0.81024 | 0.16937 | 0.84686 | 0.20599 | -0.059509 | 0.050354 | -122.5662 | 0.10071 | 0.24719 | -0.050354 | 0.3067 | 0.009155 | 0.54932 | 122.6212 | 0.16022 | 0.2655 | 122.7997 | 122.8821 | 122.7631 | 122.8226 | -122.8088 | -122.8317 | 122.5845 | 0.20599 | 2.5177 | 1.0849
2905.1719 | 122.9599 | -55.4169 | 67.4057 | -0.037689 | 0.00019446 | 0.059462 | 0.067763 | -0.00048063 | 0.0019781 | 0.0039264 | -0.016602 | 0.0017431 | 2.8e-08 | -0.0014356 | 0.0016983 | -0.0057935 | -0.0033923 | -52.8168 | 67.3965 | -55.4169 | 67.2363 | -54.8584 | -55.1788 | -54.5471 | -54.2999 | 67.4423 | -55.4352 | -55.2383 | -55.3391 | -55.4855 | -55.2063 | 0 | -0.009156 | -0.16937 | 0.55847 | 0.86975 | 0.23804 | 0.86975 | 0.23804 | -0.018311 | 0.036621 | -122.644 | 0.07782 | 0.21057 | -0.068665 | 0.22888 | -0.050354 | 0.55847 | 122.6532 | 0.096131 | 0.19684 | 122.8134 | 122.8775 | 122.8134 | 122.8592 | -122.8226 | -122.8409 | 122.6532 | 0.17853 | 2.6001 | 1.1169
2906.1719 | 123.0606 | -55.3848 | 67.3965 | 0.15305 | -0.00087374 | 0.063734 | 0.070327 | -0.00026703 | 0.0034735 | 0.0047808 | -0.0043946 | -0.00017945 | -0.00085457 | -0.0018628 | -0.0019333 | -0.0055799 | 0.0010937 | -52.9953 | 67.3874 | -55.4214 | 67.2729 | -54.808 | -55.1468 | -54.5151 | -54.2313 | 67.4103 | -55.4077 | -55.1605 | -55.2704 | -55.3894 | -55.1193 | -0.036621 | -0.009155 | -0.1236 | 0.57678 | 0.86975 | 0.23804 | 0.90637 | 0.27466 | -0.022888 | 0.013733 | -122.5571 | 0.11444 | 0.2655 | -0.004577 | 0.28839 | 0.018311 | 0.6134 | 122.6944 | 0.13733 | 0.24719 | 122.8088 | 122.818 | 122.7722 | 122.7951 | -122.818 | -122.8043 | 122.6578 | 0.22431 | 2.3895 | 1.1536
2907.1719 | 123.0377 | -55.4031 | 67.3874 | -0.075836 | -0.0010873 | 0.061598 | 0.069472 | -5.343e-05 | 0.0024053 | 0.0049946 | 0.029175 | 0.0011023 | 0.00042723 | -0.0014356 | -0.0021469 | -0.0057935 | -0.0014697 | -52.8488 | 67.3691 | -55.4443 | 67.2226 | -54.8492 | -55.1971 | -54.5563 | -54.2816 | 67.3965 | -55.426 | -55.1697 | -55.275 | -55.4077 | -55.1193 | -0.041199 | -0.01831 | -0.16479 | 0.55389 | 0.84686 | 0.20599 | 0.88806 | 0.24719 | -0.022888 | 0.009155 | -122.5571 | 0.12817 | 0.28381 | -0.004578 | 0.3067 | 0.01831 | 0.59509 | 122.6669 | 0.15106 | 0.25635 | 122.8134 | 122.8226 | 122.7722 | 122.7997 | -122.8317 | -122.8134 | 122.6257 | 0.23346 | 2.5543 | 1.1215
2908.1719 | 123.0927 | -55.3665 | 67.3874 | -0.10635 | 0.00019446 | 0.062025 | 0.071181 | -0.00069423 | 0.0021917 | 0.0071308 | -0.0074462 | 0.0025975 | 0.00064083 | 0.00070062 | -0.0012925 | -0.0055799 | 0.0021619 | -52.7985 | 67.3965 | -55.4077 | 67.2775 | -54.7989 | -55.1422 | -54.5105 | -54.2084 | 67.424 | -55.4031 | -55.1239 | -55.2246 | -55.3574 | -55.0964 | -0.041199 | 0.009155 | -0.10986 | 0.56763 | 0.85602 | 0.2243 | 0.89722 | 0.2655 | -0.036621 | 0.036621 | -122.5113 | 0.14191 | 0.27008 | 0.009155 | 0.3067 | 0.045776 | 0.60883 | 122.6852 | 0.17853 | 0.27924 | 122.8043 | 122.8271 | 122.7631 | 122.7905 | -122.7951 | -122.7905 | 122.644 | 0.24262 | 2.5681 | 1.1581
2909.1719 | 123.0011 | -55.3528 | 67.4103 | -0.091095 | 0.0019035 | 0.062025 | 0.070754 | -0.001976 | 0.0026191 | 0.0049946 | 0.0078126 | 0.0015295 | 0.0023498 | 0.0041186 | -0.00086511 | -0.0045117 | -0.0027515 | -52.7939 | 67.4149 | -55.426 | 67.2729 | -54.8126 | -55.1422 | -54.5242 | -54.2313 | 67.4103 | -55.4443 | -55.1651 | -55.2795 | -55.4123 | -55.1376 | -0.073242 | 0.004578 | -0.13733 | 0.54016 | 0.82855 | 0.21057 | 0.90179 | 0.28381 | -0.091553 | 0 | -122.5754 | 0.073242 | 0.21515 | -0.059509 | 0.3067 | 0.032044 | 0.6134 | 122.699 | 0.16479 | 0.27924 | 122.8409 | 122.8546 | 122.7676 | 122.7631 | -122.8363 | -122.8546 | 122.6257 | 0.18768 | 2.5589 | 1.1215
2910.1719 | 123.0515 | -55.3619 | 67.4057 | -0.045319 | 0.00019446 | 0.060103 | 0.0699 | 0.003151 | 0.00069649 | 0.0081988 | 0.013916 | -0.00039305 | 2.8e-08 | -0.00079478 | -0.0010787 | 0.00018792 | -0.0012561 | -52.7756 | 67.392 | -55.3986 | 67.3096 | -54.7348 | -55.101 | -54.4785 | -54.1855 | 67.4332 | -55.4031 | -55.2612 | -55.188 | -55.3574 | -55.1193 | -0.036622 | -0.013733 | -0.096131 | 0.62714 | 0.88348 | 0.26093 | 0.92011 | 0.29755 | -0.041199 | 0.027466 | -122.6669 | 0.17395 | 0.24261 | 0.004577 | 0.28381 | 0.045776 | 0.66376 | 122.7081 | 0.21515 | 0.14191 | 122.7905 | 122.8363 | 122.7539 | 122.7951 | -122.8043 | -122.8088 | 122.6715 | 0.10071 | 2.5864 | 1.1765
2911.1719 | 123.0515 | -55.3711 | 67.3965 | -0.045319 | -0.0015145 | 0.062666 | 0.069045 | -0.0011214 | 0.0017645 | 0.0073444 | 0.0047608 | 0.0013159 | 0.00042723 | 0.0032642 | -0.0032151 | -0.0045117 | -0.00018806 | -52.803 | 67.4057 | -55.426 | 67.2592 | -54.8172 | -55.1651 | -54.5471 | -54.245 | 67.4515 | -55.4123 | -55.1376 | -55.2338 | -55.3711 | -55.0873 | -0.054931 | 0.009156 | -0.13733 | 0.55389 | 0.82397 | 0.20599 | 0.87891 | 0.26093 | -0.041198 | 0.054932 | -122.5342 | 0.13733 | 0.28381 | 0 | 0.32501 | 0.041198 | 0.60883 | 122.6852 | 0.17853 | 0.27466 | 122.8317 | 122.8638 | 122.7768 | 122.8226 | -122.8226 | -122.8088 | 122.6303 | 0.23346 | 2.5681 | 1.1261
2912.1719 | 122.9416 | -55.4077 | 67.4286 | -0.075836 | -0.0013009 | 0.061171 | 0.070754 | 0.0020828 | 0.0017645 | 0.009267 | -0.080688 | 0.0025975 | 2.8e-08 | -0.00015378 | -0.0017197 | -0.0023755 | -0.00040166 | -52.8076 | 67.4194 | -55.4626 | 67.2089 | -54.895 | -55.2383 | -54.6387 | -54.2999 | 67.4789 | -55.4352 | -55.2109 | -55.3619 | -55.5222 | -55.1926 | -0.054931 | -0.009155 | -0.21973 | 0.5127 | 0.76904 | 0.16937 | 0.82397 | 0.2243 | -0.027466 | 0.050354 | -122.6395 | 0.045777 | 0.21515 | -0.11444 | 0.24262 | -0.086975 | 0.56763 | 122.6715 | 0.073243 | 0.22431 | 122.8821 | 122.9141 | 122.8271 | 122.8867 | -122.8912 | -122.8638 | 122.6166 | 0.19684 | 2.6001 | 1.1078
2913.1719 | 122.905 | -55.3802 | 67.4469 | -0.014801 | 0.0010489 | 0.062239 | 0.070327 | 0.0018692 | 0.0024053 | 0.0060626 | -0.025757 | 0.0011023 | 0.001068 | 0.0043322 | 0.00084389 | -0.0057935 | -0.00082886 | -52.8168 | 67.4789 | -55.4352 | 67.186 | -54.8676 | -55.2109 | -54.5929 | -54.3365 | 67.4927 | -55.4077 | -55.2155 | -55.3299 | -55.4672 | -55.2109 | -0.054932 | 0.032044 | -0.26093 | 0.5127 | 0.78735 | 0.16937 | 0.84228 | 0.22431 | -0.027466 | 0.045777 | -122.6624 | 0.050354 | 0.16937 | -0.086975 | 0.19684 | -0.059509 | 0.56763 | 122.6212 | 0.07782 | 0.19226 | 122.9141 | 122.9004 | 122.8592 | 122.8729 | -122.8821 | -122.8546 | 122.5662 | 0.16479 | 2.5635 | 1.0437
2914.1719 | 123.0331 | -55.3665 | 67.4149 | -0.12161 | 0.00019446 | 0.060744 | 0.069472 | 0.0012284 | 0.0021917 | 0.00414 | 0.03833 | 0.0023839 | 0.00085443 | -0.0020764 | -0.00022431 | -0.0045117 | 0.00066654 | -52.8397 | 67.4057 | -55.4123 | 67.2409 | -54.8584 | -55.1697 | -54.5288 | -54.2633 | 67.4286 | -55.4123 | -55.1605 | -55.2612 | -55.3848 | -55.101 | -0.045776 | -0.009155 | -0.17395 | 0.50812 | 0.83771 | 0.19684 | 0.88348 | 0.24261 | -0.045776 | 0.013733 | -122.5754 | 0.10529 | 0.2655 | -0.018311 | 0.31128 | 0.027465 | 0.55389 | 122.6532 | 0.15106 | 0.25177 | 122.818 | 122.8409 | 122.7722 | 122.7951 | -122.8271 | -122.8271 | 122.6074 | 0.20599 | 2.5269 | 1.1032
2915.1719 | 123.0606 | -55.3391 | 67.4377 | -0.091095 | -0.00044654 | 0.059248 | 0.066482 | 0.0012284 | 0.0024053 | 0.0054218 | 0.035278 | 0.00067495 | 0.001068 | -0.0033582 | -0.00065151 | -0.0047253 | -0.0012561 | -52.7939 | 67.424 | -55.3894 | 67.2867 | -54.8172 | -55.1331 | -54.4922 | -54.2175 | 67.4469 | -55.3848 | -55.1147 | -55.2109 | -55.3528 | -55.069 | -0.050354 | -0.013733 | -0.15106 | 0.52185 | 0.84686 | 0.20599 | 0.89722 | 0.25635 | -0.045777 | 0.009155 | -122.5525 | 0.12817 | 0.27008 | -0.013733 | 0.31586 | 0.032044 | 0.5722 | 122.6761 | 0.17395 | 0.27008 | 122.8134 | 122.8317 | 122.7631 | 122.7859 | -122.8271 | -122.8226 | 122.6257 | 0.2243 | 2.5452 | 1.1215
2916.1719 | 123.0469 | -55.3482 | 67.4149 | -0.083466 | -0.00044654 | 0.062025 | 0.067123 | -0.00048063 | 0.0017645 | 0.0060626 | 0.044434 | 3.4148e-05 | 0.00085443 | 0.0032642 | -0.00022431 | -0.0028027 | -0.0038197 | -52.7893 | 67.4103 | -55.3986 | 67.2821 | -54.8172 | -55.1605 | -54.4922 | -54.2313 | 67.4377 | -55.3894 | -55.1102 | -55.2292 | -55.3574 | -55.0781 | -0.050354 | -0.004578 | -0.13275 | 0.53101 | 0.85602 | 0.18768 | 0.90637 | 0.23804 | -0.041198 | 0.022888 | -122.525 | 0.11902 | 0.27008 | -0.009155 | 0.31128 | 0.032043 | 0.58136 | 122.6807 | 0.16022 | 0.27924 | 122.8088 | 122.8271 | 122.7585 | 122.7859 | -122.8134 | -122.8043 | 122.6303 | 0.23804 | 2.5589 | 1.1169
2917.1719 | 122.9462 | -55.3574 | 67.4927 | -0.12161 | 0.0010489 | 0.060316 | 0.072677 | -0.0017624 | 0.0011237 | 0.00414 | -0.041016 | 0.00067495 | 0.00064083 | 5.9824e-05 | -0.0017197 | -0.0036573 | -0.0010425 | -52.7985 | 67.4744 | -55.4306 | 67.2043 | -54.8813 | -55.188 | -54.5929 | -54.3228 | 67.5156 | -55.3802 | -55.1834 | -55.3162 | -55.4718 | -55.1605 | -0.073242 | -0.018311 | -0.28839 | 0.47607 | 0.76446 | 0.16937 | 0.83771 | 0.24262 | -0.022888 | 0.022888 | -122.6761 | 0.041199 | 0.19684 | -0.11444 | 0.21973 | -0.091553 | 0.54932 | 122.6349 | 0.064087 | 0.19684 | 122.905 | 122.8958 | 122.8317 | 122.8729 | -122.9233 | -122.8729 | 122.5616 | 0.17395 | 2.5589 | 1.0345
2918.1719 | 123.0606 | -55.3116 | 67.4515 | -0.11398 | -0.0013009 | 0.061171 | 0.070541 | -0.0024032 | 0.0015509 | 0.0056354 | 0.20618 | 0.0013159 | 0.001709 | 0.001128 | -1.0706e-05 | -0.0066479 | -0.0044605 | -52.7252 | 67.4057 | -55.3757 | 67.3187 | -54.7348 | -55.0735 | -54.4785 | -54.3869 | 67.4789 | -55.3711 | -55.0919 | -55.22 | -55.3436 | -55.069 | -0.064087 | -0.045776 | -0.13275 | 0.57678 | 0.83313 | 0.23804 | 0.89722 | 0.30212 | -0.05951 | 0.027466 | -122.5433 | 0.091552 | 0.24261 | -0.032044 | 0.30212 | 0.027466 | 0.64087 | 122.6944 | 0.15106 | 0.27924 | 122.7814 | 122.85 | 122.7173 | 122.7905 | -122.8271 | -122.8226 | 122.6303 | 0.21973 | 2.5864 | 0.92468
2919.1719 | 122.9324 | -55.3574 | 67.4881 | -0.1445 | 0.00019446 | 0.064162 | 0.070968 | -0.0021896 | 0.0019781 | 0.007558 | 0.010864 | 0.0023839 | 0.00085443 | 0.001128 | -0.0023605 | -0.0040845 | 0.0053661 | -52.7481 | 67.4561 | -55.3802 | 67.2638 | -54.808 | -55.1285 | -54.5151 | -54.2679 | 67.4881 | -55.394 | -55.1834 | -55.2704 | -55.4306 | -55.1559 | -0.022888 | -0.032043 | -0.2243 | 0.54932 | 0.84228 | 0.22888 | 0.86517 | 0.25177 | -0.036621 | 0 | -122.6715 | 0.086975 | 0.20142 | -0.073242 | 0.23804 | -0.036621 | 0.5722 | 122.644 | 0.1236 | 0.21057 | 122.8363 | 122.8821 | 122.8134 | 122.8455 | -122.8683 | -122.8821 | 122.6212 | 0.17395 | 2.6093 | 1.0895
2920.1719 | 123.0057 | -55.3436 | 67.4194 | -0.098725 | -0.0010873 | 0.062453 | 0.069686 | 0.001442 | 0.0026191 | 0.0047808 | 0.013916 | 0.0011023 | -0.0010682 | -0.0031446 | -0.0019333 | -0.0042981 | 0.00023934 | -52.8259 | 67.3965 | -55.394 | 67.2409 | -54.8172 | -55.2063 | -54.5334 | -54.2633 | 67.4423 | -55.3619 | -55.1514 | -55.275 | -55.4214 | -55.1102 | -0.050354 | -0.022889 | -0.17853 | 0.52643 | 0.81024 | 0.13733 | 0.8606 | 0.18768 | -0.01831 | 0.022888 | -122.5708 | 0.068665 | 0.23346 | -0.07782 | 0.25177 | -0.05951 | 0.57678 | 122.6349 | 0.086975 | 0.21057 | 122.7905 | 122.8043 | 122.7402 | 122.786 | -122.8134 | -122.7814 | 122.5845 | 0.19226 | 2.5177 | 1.0803
2921.1719 | 123.0011 | -55.3574 | 67.4286 | -0.15213 | -0.00044654 | 0.060316 | 0.070754 | -0.0032578 | 0.0039007 | 0.0056354 | -0.0074462 | -0.0016749 | 0.00064083 | -0.00464 | -0.0030013 | -0.0049389 | -0.00082886 | -52.8076 | 67.4103 | -55.4169 | 67.2684 | -54.8172 | -55.188 | -54.5242 | -54.2404 | 67.4332 | -55.3848 | -55.1559 | -55.275 | -55.4031 | -55.0964 | -0.059509 | -0.018311 | -0.16022 | 0.54016 | 0.83313 | 0.16937 | 0.89264 | 0.22888 | -0.027466 | 0.004578 | -122.5845 | 0.082398 | 0.26093 | -0.045776 | 0.28839 | -0.01831 | 0.59967 | 122.6852 | 0.10986 | 0.22888 | 122.8271 | 122.818 | 122.7676 | 122.7905 | -122.8455 | -122.8134 | 122.6257 | 0.20142 | 2.5497 | 1.1169
2922.1719 | 122.9691 | -55.3436 | 67.4881 | -0.052948 | 0.00083526 | 0.058821 | 0.070754 | -0.00026703 | 0.0019781 | 0.0045672 | -0.068481 | 0.0023839 | 0.00085443 | 0.0064684 | -0.0030013 | -0.0045117 | 0.0025891 | -52.7481 | 67.4789 | -55.3848 | 67.2638 | -54.8218 | -55.1559 | -54.5425 | -54.2587 | 67.543 | -55.3757 | -55.1559 | -55.2841 | -55.4214 | -55.1147 | -0.041199 | -0.009155 | -0.2243 | 0.52185 | 0.80109 | 0.18768 | 0.84229 | 0.22888 | -0.032043 | 0.054932 | -122.644 | 0.059509 | 0.22888 | -0.07782 | 0.26093 | -0.045777 | 0.56305 | 122.6486 | 0.091552 | 0.21973 | 122.8638 | 122.9187 | 122.8226 | 122.8867 | -122.8729 | -122.8638 | 122.6074 | 0.18768 | 2.5955 | 1.0849
2923.1719 | 123.0103 | -55.3345 | 67.424 | -0.11398 | 0.0021171 | 0.062025 | 0.069045 | 0.00251 | 0.0030463 | 0.0056354 | -0.0013428 | 0.00067495 | 0.00021363 | -0.0035718 | -0.0015061 | -0.0053663 | -0.0018971 | -52.8076 | 67.424 | -55.3894 | 67.2546 | -54.8264 | -55.1788 | -54.5288 | -54.2633 | 67.4515 | -55.394 | -55.1468 | -55.2612 | -55.3894 | -55.0827 | -0.054931 | 0 | -0.16937 | 0.50812 | 0.80566 | 0.15564 | 0.86059 | 0.21057 | -0.059509 | 0.027466 | -122.5708 | 0.073243 | 0.25177 | -0.054931 | 0.31128 | 0.004578 | 0.56305 | 122.644 | 0.13275 | 0.24719 | 122.8134 | 122.8455 | 122.7585 | 122.7859 | -122.8134 | -122.818 | 122.5891 | 0.18768 | 2.5269 | 1.0712
2924.1719 | 123.0194 | -55.3299 | 67.4377 | -0.1445 | 0.00062166 | 0.061385 | 0.070113 | -0.0013352 | 0.0019781 | 0.0043536 | -0.025757 | 0.00024775 | 0.0025634 | -0.00036738 | -0.0019333 | -0.0053663 | -0.00061526 | -52.8076 | 67.4149 | -55.3802 | 67.2592 | -54.8172 | -55.188 | -54.5151 | -54.2542 | 67.4606 | -55.3848 | -55.1422 | -55.2658 | -55.394 | -55.101 | -0.050354 | -0.022888 | -0.17853 | 0.5127 | 0.81482 | 0.14191 | 0.86517 | 0.19226 | -0.054932 | 0.022888 | -122.58 | 0.064087 | 0.22888 | -0.064087 | 0.28381 | -0.009155 | 0.56305 | 122.6395 | 0.11902 | 0.24262 | 122.7951 | 122.8455 | 122.7448 | 122.7905 | -122.818 | -122.8226 | 122.5891 | 0.18768 | 2.5223 | 1.0757
2925.1719 | 122.9874 | -55.3528 | 67.424 | -0.12161 | -0.0017281 | 0.060316 | 0.070113 | 0.00037377 | 0.0036871 | 0.0090534 | 0.016968 | 0.0019567 | -0.001709 | 0.003905 | -0.0017197 | -0.0053663 | 0.0015209 | -52.7664 | 67.4286 | -55.3802 | 67.2638 | -54.7989 | -55.1743 | -54.5013 | -54.2267 | 67.4423 | -55.3757 | -55.1193 | -55.2658 | -55.3802 | -55.101 | -0.027466 | 0.004578 | -0.16022 | 0.55389 | 0.85144 | 0.17853 | 0.87891 | 0.20599 | -0.022888 | 0.018311 | -122.5433 | 0.086975 | 0.25177 | -0.027466 | 0.27466 | -0.004578 | 0.58136 | 122.644 | 0.10986 | 0.25635 | 122.8088 | 122.818 | 122.7814 | 122.7951 | -122.8043 | -122.7997 | 122.6166 | 0.23346 | 2.5864 | 1.1261
2926.1719 | 122.9645 | -55.3162 | 67.4835 | -0.13687 | 0.0010489 | 0.061598 | 0.0699 | 0.00058737 | 0.0011237 | 0.0028582 | 0.013916 | 0.0011023 | -0.0010682 | -0.0020764 | -0.0021469 | -0.0060071 | 0.0015209 | -52.7893 | 67.424 | -55.3848 | 67.2775 | -54.8126 | -55.1559 | -54.5059 | -54.2679 | 67.4698 | -55.3711 | -55.1193 | -55.2658 | -55.3757 | -55.101 | -0.068665 | -0.05951 | -0.20599 | 0.50354 | 0.81024 | 0.16022 | 0.87891 | 0.22888 | -0.054932 | -0.013733 | -122.6028 | 0.050354 | 0.21515 | -0.059509 | 0.27008 | -0.004577 | 0.57221 | 122.6624 | 0.10529 | 0.25177 | 122.8088 | 122.8409 | 122.7402 | 122.7859 | -122.8683 | -122.8546 | 122.5937 | 0.19684 | 2.5269 | 1.0483
2927.1719 | 123.0331 | -55.307 | 67.4744 | -0.15976 | 0.0012625 | 0.061598 | 0.070968 | 0.00037377 | 0.00048269 | 0.005849 | 0.016968 | -0.00039305 | -0.0021362 | -0.002931 | -0.0025741 | -0.0053663 | -0.0025379 | -52.7985 | 67.4515 | -55.3665 | 67.3325 | -54.7211 | -55.0415 | -54.4281 | -54.1306 | 67.511 | -55.3391 | -55.069 | -55.1651 | -55.2979 | -55.0369 | -0.059509 | -0.022888 | -0.14191 | 0.58594 | 0.87891 | 0.2655 | 0.93841 | 0.32501 | -0.032043 | 0.036621 | -122.5433 | 0.14191 | 0.27008 | 0.009155 | 0.30212 | 0.041198 | 0.64545 | 122.699 | 0.17395 | 0.27008 | 122.818 | 122.85 | 122.7585 | 122.818 | -122.8409 | -122.8134 | 122.6395 | 0.23804 | 2.5085 | 1.1765
2928.1719 | 123.0194 | -55.3253 | 67.4789 | -0.098725 | 0.0012625 | 0.060103 | 0.070113 | 0.001442 | 0.0032599 | 0.0043536 | 0.023071 | 0.00046135 | -0.0032044 | 0.002196 | -0.0015061 | -0.0062207 | -0.0010425 | -52.7756 | 67.4332 | -55.3848 | 67.2729 | -54.8126 | -55.1376 | -54.5059 | -54.1397 | 67.4973 | -55.307 | -55.1147 | -55.2017 | -55.3757 | -55.0919 | -0.05951 | -0.045776 | -0.20599 | 0.5127 | 0.8194 | 0.18768 | 0.87891 | 0.24719 | 0.01831 | 0.01831 | -122.5937 | 0.1236 | 0.23346 | -0.050354 | 0.21515 | -0.068664 | 0.57221 | 122.6578 | 0.10529 | 0.19226 | 122.818 | 122.8043 | 122.7585 | 122.8226 | -122.8638 | -122.7859 | 122.5983 | 0.21057 | 2.5497 | 1.1856
2929.1719 | 123.0103 | -55.3024 | 67.4469 | -0.16739 | -0.0013009 | 0.061385 | 0.0699 | -0.0032578 | 0.0019781 | 0.0054218 | -0.034912 | 0.00067495 | -0.00021357 | 0.0024096 | -0.00065151 | -0.0049389 | 0.00066654 | -52.7435 | 67.4149 | -55.3757 | 67.3004 | -54.776 | -55.1559 | -54.4968 | -54.1901 | 67.4789 | -55.3574 | -55.1056 | -55.2475 | -55.3848 | -55.0781 | -0.073242 | -0.032043 | -0.14648 | 0.52643 | 0.80566 | 0.14648 | 0.87891 | 0.21973 | -0.054932 | 0.032044 | -122.5525 | 0.054931 | 0.2243 | -0.082398 | 0.27924 | -0.027466 | 0.59967 | 122.6761 | 0.10986 | 0.25177 | 122.7905 | 122.8363 | 122.7173 | 122.7814 | -122.8226 | -122.8043 | 122.6028 | 0.19684 | 2.5589 | 1.1124
2930.1719 | 123.024 | -55.3024 | 67.4652 | -0.1445 | 0.0027579 | 0.063307 | 0.069045 | -0.0021896 | 0.0032599 | 0.0062762 | -0.019653 | 0.0017431 | -0.0014954 | -0.0010084 | -0.0027877 | -0.0051527 | -0.0021107 | -52.7344 | 67.4149 | -55.3665 | 67.305 | -54.7531 | -55.1193 | -54.4693 | -54.1672 | 67.4423 | -55.3528 | -55.0781 | -55.2292 | -55.3665 | -55.069 | -0.064087 | -0.050354 | -0.16022 | 0.54932 | 0.83313 | 0.1831 | 0.89722 | 0.24719 | -0.050354 | -0.022888 | -122.5433 | 0.073242 | 0.23346 | -0.064087 | 0.28381 | -0.013733 | 0.6134 | 122.6715 | 0.1236 | 0.27466 | 122.7814 | 122.7951 | 122.7173 | 122.7448 | -122.8317 | -122.818 | 122.6074 | 0.2243 | 2.5681 | 1.1353
2931.1719 | 123.0194 | -55.3162 | 67.4881 | -0.15976 | -0.00087374 | 0.059889 | 0.071609 | 0.0022964 | 0.0026191 | 0.0064898 | -0.016602 | 0.00024775 | 2.8e-08 | -0.0042126 | -0.0010787 | -0.0040845 | 0.0025891 | -52.7618 | 67.4606 | -55.3802 | 67.2913 | -54.7989 | -55.0827 | -54.3686 | -54.245 | 67.511 | -55.3299 | -55.1147 | -55.2292 | -55.3574 | -55.0552 | -0.064087 | -0.027466 | -0.19684 | 0.51727 | 0.94757 | 0.23346 | 1.0117 | 0.29755 | -0.013733 | 0.022888 | -122.6028 | 0.086975 | 0.26093 | -0.041199 | 0.27466 | -0.027466 | 0.58136 | 122.6715 | 0.10071 | 0.21515 | 122.8409 | 122.8409 | 122.7768 | 122.8271 | -122.8683 | -122.818 | 122.6074 | 0.20142 | 2.5543 | 1.0712
2932.1719 | 123.0011 | -55.2979 | 67.4606 | -0.075836 | 0.00083526 | 0.060957 | 0.069472 | 0.00251 | 0.0034735 | 0.0026446 | -0.044067 | 0.00067495 | -0.0012818 | -0.002931 | -0.0023605 | -0.0038709 | -0.0021107 | -52.739 | 67.4332 | -55.3253 | 67.3187 | -54.7485 | -55.1331 | -54.483 | -54.1901 | 67.4973 | -55.3436 | -55.0873 | -55.2155 | -55.3619 | -55.0644 | -0.027465 | -0.027465 | -0.14191 | 0.54932 | 0.81482 | 0.16479 | 0.84228 | 0.19226 | -0.045776 | 0.036621 | -122.5479 | 0.082398 | 0.23346 | -0.064086 | 0.27924 | -0.01831 | 0.57678 | 122.644 | 0.12817 | 0.25635 | 122.7585 | 122.8409 | 122.731 | 122.7951 | -122.7859 | -122.8043 | 122.6166 | 0.21057 | 2.5589 | 1.1078
2933.1719 | 123.0057 | -55.2841 | 67.4744 | -0.060578 | -0.0017281 | 0.060316 | 0.071609 | -0.0026168 | 0.00069649 | 0.0026446 | 0.02002 | 3.4148e-05 | 0.00064083 | -0.00079478 | -0.0032151 | -0.0051527 | -0.0061695 | -52.684 | 67.4652 | -55.3116 | 67.4103 | -54.6616 | -54.9957 | -54.3686 | -54.071 | 67.5247 | -55.2795 | -54.982 | -54.8538 | -55.4718 | -55.188 | -0.027465 | -0.009155 | -0.064087 | 0.62256 | 0.91553 | 0.28839 | 0.94299 | 0.31586 | 0.004578 | 0.050354 | -122.4564 | 0.4303 | 0.096131 | -0.18768 | 0.091553 | -0.19226 | 0.65002 | 122.7219 | 0.42572 | 0.29755 | 122.7768 | 122.8043 | 122.7493 | 122.8088 | -122.7859 | -122.7539 | 122.6944 | 0.30212 | 2.6001 | 1.2131
2934.1719 | 123.0286 | -55.2795 | 67.4881 | -0.068207 | -0.0017281 | 0.061598 | 0.070113 | -0.0013352 | 0.0034735 | 0.0090534 | -0.025757 | -0.00060665 | -0.0012818 | -0.0025036 | -0.0021469 | -0.0047253 | 0.0047253 | -52.739 | 67.4744 | -55.3528 | 67.2546 | -54.8035 | -55.1285 | -54.4876 | -54.2175 | 67.511 | -55.3299 | -55.0827 | -55.1926 | -55.3482 | -55.0461 | -0.073242 | -0.013733 | -0.23346 | 0.47607 | 0.79193 | 0.15106 | 0.86517 | 0.2243 | -0.050354 | 0.022888 | -122.5708 | 0.086975 | 0.23346 | -0.068665 | 0.28381 | -0.018311 | 0.54932 | 122.6074 | 0.13733 | 0.24719 | 122.8271 | 122.8409 | 122.7539 | 122.7905 | -122.8409 | -122.818 | 122.5342 | 0.19684 | 2.5406 | 1.062
2935.1719 | 123.0423 | -55.2521 | 67.4606 | -0.098725 | 0.00040806 | 0.063094 | 0.073318 | 0.0040054 | 0.0043281 | 0.0056354 | -0.050171 | 0.0013159 | -0.0014954 | 0.0032642 | -0.0019333 | -0.0040845 | -0.0025379 | -52.684 | 67.4698 | -55.3528 | 67.3508 | -54.7485 | -55.0964 | -54.4922 | -54.1306 | 67.4927 | -55.3436 | -55.1422 | -55.3116 | -55.2063 | -54.895 | -0.10071 | 0.009156 | -0.10986 | 0.50354 | 0.75989 | 0.15564 | 0.8606 | 0.25635 | -0.091553 | 0.032044 | -122.6028 | -0.059509 | 0.35705 | 0.045776 | 0.44861 | 0.13733 | 0.60425 | 122.7036 | 0.032044 | 0.20142 | 122.8226 | 122.8363 | 122.7219 | 122.7448 | -122.8134 | -122.8043 | 122.6028 | 0.10986 | 2.5681 | 1.1215
2936.1719 | 123.0194 | -55.2704 | 67.4652 | -0.098725 | 0.00083526 | 0.062666 | 0.070113 | -0.00069423 | 0.0021917 | 0.0054218 | -0.037964 | 0.0023839 | 0.001068 | 0.0017688 | -0.0034287 | -0.0051527 | 0.0023755 | -52.6154 | 67.4103 | -55.3253 | 67.3508 | -54.7302 | -55.0919 | -54.4647 | -54.1397 | 67.5201 | -55.3116 | -55.0323 | -55.1926 | -55.3391 | -55.0323 | -0.054931 | -0.054932 | -0.11444 | 0.54016 | 0.80566 | 0.17853 | 0.86059 | 0.23346 | -0.041198 | 0.054932 | -122.4976 | 0.07782 | 0.23804 | -0.068664 | 0.27923 | -0.027466 | 0.59509 | 122.6761 | 0.11902 | 0.27923 | 122.7356 | 122.8317 | 122.6807 | 122.7905 | -122.7905 | -122.7768 | 122.6212 | 0.23804 | 2.655 | 1.1307
2937.1719 | 123.0286 | -55.2979 | 67.4652 | -0.11398 | -0.0025827 | 0.061598 | 0.071395 | -0.00048063 | 0.0036871 | 0.0077716 | -0.025757 | 0.0019567 | -0.0012818 | 0.001128 | -0.0012925 | -0.0032301 | -0.00040166 | -52.684 | 67.4515 | -55.3345 | 67.3325 | -54.9774 | -55.0873 | -54.3503 | -54.1397 | 67.5156 | -55.3116 | -55.0323 | -55.1834 | -55.3299 | -55.0049 | -0.036621 | -0.013733 | -0.13275 | 0.32043 | 0.94757 | 0.21057 | 0.98419 | 0.24719 | -0.013732 | 0.050354 | -122.4976 | 0.11444 | 0.29297 | -0.032043 | 0.3067 | -0.018311 | 0.35706 | 122.6669 | 0.12817 | 0.27923 | 122.7859 | 122.8271 | 122.7493 | 122.8134 | -122.7997 | -122.7768 | 122.6303 | 0.2655 | 2.6138 | 1.1581
2938.1719 | 123.0606 | -55.275 | 67.5018 | -0.13687 | 0.00062166 | 0.062453 | 0.071609 | 0.0012284 | 0.0026191 | 0.0056354 | -0.03186 | 0.0011023 | 0.00042723 | -0.00036738 | -0.0027877 | -0.0028027 | 0.0013073 | -52.6932 | 67.4927 | -55.3391 | 67.3691 | -54.7256 | -55.0873 | -54.4601 | -54.1534 | 67.5293 | -55.3345 | -55.0095 | -55.0232 | -55.3528 | -55.0323 | -0.064087 | -0.009155 | -0.13275 | 0.54932 | 0.81482 | 0.18768 | 0.87891 | 0.25177 | -0.05951 | 0.027466 | -122.5113 | 0.25177 | 0.24261 | -0.07782 | 0.30212 | -0.01831 | 0.6134 | 122.7081 | 0.31128 | 0.32501 | 122.8317 | 122.8638 | 122.7676 | 122.8043 | -122.8409 | -122.8363 | 122.644 | 0.2655 | 2.5818 | 1.1215
2939.1719 | 123.0423 | -55.2933 | 67.4423 | -0.098725 | 0.00019446 | 0.060744 | 0.071609 | -0.001976 | 0.0024053 | 0.0071308 | -0.0074462 | 0.00024775 | -0.00064077 | -0.00015378 | -0.0010787 | -0.0032301 | -0.0012561 | -52.6794 | 67.4423 | -55.3482 | 67.337 | -54.7302 | -55.1102 | -54.4601 | -54.1443 | 67.5201 | -55.3253 | -55.0415 | -55.1788 | -55.3299 | -54.9957 | -0.054932 | 0 | -0.10529 | 0.56305 | 0.83313 | 0.18311 | 0.88806 | 0.23804 | -0.032043 | 0.07782 | -122.4838 | 0.11444 | 0.29755 | -0.036621 | 0.32959 | -0.004578 | 0.61798 | 122.6852 | 0.14648 | 0.28381 | 122.7905 | 122.8455 | 122.7356 | 122.8134 | -122.7905 | -122.7676 | 122.6303 | 0.25177 | 2.6138 | 1.149
2940.1719 | 123.0698 | -55.2567 | 67.4927 | -0.20554 | -0.0015145 | 0.062666 | 0.070968 | 0.0012284 | 0.0019781 | 0.0060626 | -0.0013428 | 0.00088875 | 2.8e-08 | -0.00079478 | -0.0023605 | -0.0042981 | -0.0018971 | -52.6703 | 67.4469 | -55.3207 | 67.3874 | -54.8676 | -55.2292 | -54.332 | -54.1534 | 67.5293 | -55.2933 | -55.0369 | -55.1743 | -55.307 | -54.9911 | -0.064087 | -0.045777 | -0.10529 | 0.3891 | 0.92468 | 0.027466 | 0.98877 | 0.091553 | -0.036621 | 0.036621 | -122.5296 | 0.082398 | 0.2655 | -0.050354 | 0.30212 | -0.013733 | 0.45319 | 122.7081 | 0.11902 | 0.25635 | 122.7676 | 122.8226 | 122.7036 | 122.7859 | -122.8134 | -122.7859 | 122.644 | 0.21973 | 2.5864 | 1.1032
2941.1719 | 123.0148 | -55.2795 | 67.5201 | -0.083466 | 0.00019446 | 0.062239 | 0.070968 | 0.00016017 | 0.0021917 | 0.0060626 | -0.062378 | 0.0019567 | 0.0019226 | -0.00058098 | -0.0015061 | -0.0040845 | 0.0015209 | -52.7252 | 67.5064 | -55.3391 | 67.2913 | -54.8126 | -55.1514 | -54.5151 | -54.1855 | 67.5339 | -55.3299 | -55.0507 | -55.2063 | -55.3528 | -55.0323 | -0.059509 | -0.013733 | -0.22888 | 0.46692 | 0.76447 | 0.12817 | 0.82397 | 0.18768 | -0.050354 | 0.013733 | -122.5708 | 0.073242 | 0.24719 | -0.073242 | 0.29755 | -0.022888 | 0.52643 | 122.6303 | 0.1236 | 0.27924 | 122.8455 | 122.8638 | 122.786 | 122.8134 | -122.8592 | -122.85 | 122.5708 | 0.22888 | 2.5543 | 1.0941
2942.1719 | 122.9782 | -55.2887 | 67.4927 | -0.091095 | -0.0010873 | 0.059889 | 0.071822 | -0.00090783 | 5.5488e-05 | 0.0081988 | -0.044067 | 0.0017431 | 0.00085443 | -0.00015378 | 0.00041649 | -0.0038709 | 0.0021619 | -52.7298 | 67.5293 | -55.3391 | 67.2684 | -54.8355 | -55.1834 | -54.5334 | -54.2221 | 67.5613 | -55.307 | -55.0873 | -55.2383 | -55.3894 | -55.0552 | -0.050354 | 0.036621 | -0.2243 | 0.45319 | 0.75531 | 0.10529 | 0.80566 | 0.15564 | -0.018311 | 0.068664 | -122.58 | 0.050354 | 0.23346 | -0.10071 | 0.25177 | -0.082397 | 0.50354 | 122.6074 | 0.068665 | 0.21973 | 122.8683 | 122.8683 | 122.818 | 122.85 | -122.8317 | -122.7997 | 122.5571 | 0.20142 | 2.5589 | 1.0666
2943.1719 | 123.0286 | -55.2704 | 67.4835 | -0.10635 | 0.00062166 | 0.061812 | 0.070968 | -0.0024032 | 0.0021917 | 0.0054218 | -0.059326 | 0.00024775 | 0.00085443 | 0.0045458 | -0.0012925 | -0.0034437 | 0.0021619 | -52.7023 | 67.5156 | -55.2933 | 67.3096 | -54.7623 | -55.1102 | -54.4785 | -54.1718 | 67.5247 | -55.3162 | -55.0369 | -55.1559 | -55.2887 | -54.9911 | -0.022888 | 0.032043 | -0.17395 | 0.50812 | 0.79193 | 0.16022 | 0.81482 | 0.18311 | -0.045776 | 0.041198 | -122.5204 | 0.11444 | 0.27924 | -0.01831 | 0.32501 | 0.027466 | 0.53101 | 122.6028 | 0.16022 | 0.27924 | 122.8088 | 122.8409 | 122.7859 | 122.7951 | -122.7768 | -122.7997 | 122.58 | 0.23346 | 2.5681 | 1.0986
2944.1719 | 122.9965 | -55.2841 | 67.5064 | -0.037689 | 0.0016899 | 0.062453 | 0.069259 | -0.0030442 | 0.0026191 | 0.0081988 | -0.062378 | 0.0013159 | 0.001068 | -0.00058098 | -0.00043791 | -0.0036573 | 0.0017345 | -52.7161 | 67.543 | -55.3162 | 67.2821 | -54.7897 | -55.1422 | -54.5013 | -54.1946 | 67.543 | -55.3345 | -55.0415 | -55.1971 | -55.3482 | -55.0232 | -0.032043 | 0.036621 | -0.22431 | 0.49438 | 0.78278 | 0.14191 | 0.81482 | 0.17395 | -0.050354 | 0.036621 | -122.5479 | 0.086975 | 0.26093 | -0.064087 | 0.31128 | -0.013733 | 0.52643 | 122.5983 | 0.13733 | 0.29297 | 122.8592 | 122.8775 | 122.8271 | 122.8271 | -122.8226 | -122.8409 | 122.5662 | 0.24261 | 2.5681 | 1.0895
2945.1719 | 123.056 | -55.2475 | 67.5064 | -0.12924 | -0.0010873 | 0.059889 | 0.068404 | 0.0010148 | 0.0013373 | 0.0079852 | -0.034912 | 0.0013159 | 0.0012818 | 0.0026232 | -0.0019333 | -0.0045117 | -0.0025379 | -52.6794 | 67.5201 | -55.307 | 67.3691 | -54.7165 | -55.0964 | -54.4556 | -54.1214 | 67.5293 | -55.307 | -55.0049 | -55.1514 | -55.3024 | -54.982 | -0.059509 | 0.013733 | -0.13733 | 0.53101 | 0.79193 | 0.15106 | 0.85144 | 0.21057 | -0.059509 | 0.022888 | -122.5113 | 0.096131 | 0.2655 | -0.054931 | 0.32501 | 0.004578 | 0.59051 | 122.6761 | 0.15564 | 0.30212 | 122.8271 | 122.8363 | 122.7676 | 122.7768 | -122.8134 | -122.8134 | 122.6166 | 0.24262 | 2.5681 | 1.1261
2946.1719 | 122.937 | -55.2704 | 67.5705 | -0.098725 | -0.00044654 | 0.06288 | 0.0699 | 0.00016017 | 0.0011237 | 0.0062762 | -0.050171 | 0.0015295 | 0.0012818 | -0.00036738 | -0.0012925 | -0.0032301 | 0.0010937 | -52.7252 | 67.5385 | -55.3207 | 67.2729 | -54.808 | -55.1651 | -54.5242 | -54.2313 | 67.5705 | -55.307 | -55.0919 | -55.2521 | -55.394 | -55.0644 | -0.050354 | -0.032044 | -0.29755 | 0.46234 | 0.74616 | 0.10529 | 0.79651 | 0.15564 | -0.036621 | 0 | -122.6624 | 0.018311 | 0.20599 | -0.1236 | 0.24262 | -0.086975 | 0.5127 | 122.5937 | 0.054932 | 0.21515 | 122.8592 | 122.8775 | 122.8088 | 122.8409 | -122.8912 | -122.8775 | 122.5433 | 0.17853 | 2.5452 | 1.0391
2947.1719 | 123.0057 | -55.275 | 67.4927 | -0.10635 | -0.00044654 | 0.061385 | 0.069686 | -0.00090783 | 0.00026909 | 0.0052082 | -0.034912 | -0.00017945 | 0.00064083 | 0.0028368 | -0.0021469 | -0.0036573 | 0.0028027 | -52.6978 | 67.5247 | -55.307 | 67.305 | -54.7852 | -55.1376 | -54.483 | -54.1855 | 67.5613 | -55.307 | -55.0369 | -55.1834 | -55.3253 | -55.0095 | -0.032044 | 0.032043 | -0.18768 | 0.48981 | 0.79193 | 0.13733 | 0.82397 | 0.16937 | -0.032044 | 0.068664 | -122.5296 | 0.091552 | 0.2655 | -0.050354 | 0.29755 | -0.01831 | 0.52185 | 122.612 | 0.1236 | 0.27008 | 122.8317 | 122.8683 | 122.7997 | 122.8363 | -122.7997 | -122.7997 | 122.58 | 0.23804 | 2.5772 | 1.0895
2948.1719 | 122.9095 | -55.2841 | 67.5522 | -0.10635 | -1.9142e-05 | 0.062239 | 0.075667 | 0.0022964 | 0.0024053 | 0.00414 | -0.0074462 | 0.0019567 | 0.0014954 | 0.0030506 | -0.00086511 | -0.0051527 | 0.0036571 | -52.7161 | 67.5385 | -55.307 | 67.4698 | -54.5975 | -55.2109 | -54.5334 | -54.2496 | 67.5613 | -55.2979 | -55.0964 | -55.2704 | -55.4077 | -55.0827 | -0.022888 | -0.013733 | -0.082397 | 0.68665 | 0.75073 | 0.073243 | 0.77362 | 0.096131 | -0.013733 | 0.009155 | -122.6486 | 0.013733 | 0.20142 | -0.1236 | 0.21515 | -0.10986 | 0.70953 | 122.7768 | 0.027466 | 0.20142 | 122.8455 | 122.8592 | 122.8226 | 122.8455 | -122.8592 | -122.85 | 122.7539 | 0.18768 | 2.5681 | 1.0345
2949.1719 | 122.9187 | -55.2429 | 67.5934 | -0.12161 | 0.0014761 | 0.059676 | 0.070113 | -0.001976 | 0.0024053 | 0.0084124 | -0.059326 | 3.4148e-05 | 2.8e-08 | -0.00015378 | -0.0044967 | -0.0068615 | 0.00023934 | -52.6978 | 67.5797 | -55.307 | 67.2546 | -54.8447 | -55.1834 | -54.538 | -54.2542 | 67.5842 | -55.3299 | -55.0095 | -55.3299 | -55.3345 | -55.0278 | -0.064087 | -0.013733 | -0.33875 | 0.39825 | 0.70496 | 0.059509 | 0.76904 | 0.1236 | -0.086975 | -0.009155 | -122.6028 | -0.086975 | 0.21515 | -0.091553 | 0.30212 | -0.004578 | 0.46234 | 122.5616 | 0 | 0.32044 | 122.8867 | 122.9141 | 122.8226 | 122.8271 | -122.9004 | -122.9233 | 122.4976 | 0.23346 | 2.5452 | 0.98877
2950.1719 | 122.9462 | -55.2567 | 67.5705 | 0.084381 | -0.0021555 | 0.060957 | 0.070968 | -0.0013352 | 0.0021917 | 0.0067036 | -0.03186 | 0.0015295 | 0.0014954 | -0.00058098 | -0.0017197 | -0.0032301 | -0.00082886 | -52.6291 | 67.5934 | -55.2933 | 67.3004 | -54.7943 | -55.1697 | -54.5059 | -54.2358 | 67.6117 | -55.2795 | -55.069 | -55.2429 | -55.394 | -55.0644 | -0.036621 | 0.022888 | -0.27008 | 0.46234 | 0.75073 | 0.086975 | 0.78735 | 0.1236 | -0.022888 | 0.041198 | -122.6395 | 0.013733 | 0.19226 | -0.13733 | 0.21515 | -0.11444 | 0.49896 | 122.5937 | 0.036621 | 0.21057 | 122.8867 | 122.8912 | 122.85 | 122.8683 | -122.8638 | -122.85 | 122.5571 | 0.18768 | 2.6276 | 1.0208
2951.1719 | 122.9095 | -55.2521 | 67.5705 | -0.10635 | -0.0015145 | 0.062025 | 0.070968 | -0.0030442 | 0.0019781 | 0.0071308 | 0.044434 | 0.0021703 | 0.0014954 | 0.0013416 | -0.00086511 | -0.0045117 | 0.0015209 | -52.7023 | 67.5751 | -55.3116 | 67.3233 | -55.1147 | -55.3848 | -54.3091 | -54.2679 | 67.63 | -55.2979 | -55.0964 | -55.2383 | -55.4031 | -55.0461 | -0.059509 | 0.004577 | -0.24719 | 0.13733 | 0.94299 | -0.13275 | 1.0025 | -0.073243 | -0.045777 | 0.059509 | -122.6669 | 0.013733 | 0.20599 | -0.15106 | 0.25177 | -0.10529 | 0.19684 | 122.6349 | 0.05951 | 0.20142 | 122.8867 | 122.9279 | 122.8271 | 122.8821 | -122.8821 | -122.8683 | 122.5754 | 0.15564 | 2.5497 | 0.98419
2952.1719 | 122.9553 | -55.2429 | 67.6071 | -0.12161 | 0.00062166 | 0.060957 | 0.0699 | -0.0062484 | 0.0047553 | 0.0067036 | -0.037964 | 0.0015295 | 0.0012818 | 0.00048702 | -0.00065151 | -0.0053663 | 0.0025891 | -52.6703 | 67.5934 | -55.3299 | 67.2775 | -54.8172 | -55.1651 | -54.5151 | -54.2725 | 67.6346 | -55.3116 | -55.1285 | -55.5313 | -55.1926 | -54.8676 | -0.086975 | -0.013733 | -0.32959 | 0.42572 | 0.72784 | 0.07782 | 0.81482 | 0.16479 | -0.068664 | 0.027466 | -122.7356 | -0.28839 | 0.37537 | 0.050354 | 0.44403 | 0.11902 | 0.5127 | 122.6074 | -0.21973 | 0.18311 | 122.9233 | 122.9462 | 122.8363 | 122.8775 | -122.937 | -122.9187 | 122.5204 | 0.11444 | 2.5726 | 0.97046
2953.1719 | 122.9599 | -55.275 | 67.5842 | -0.045319 | -0.0015145 | 0.063734 | 0.068832 | 0.0016556 | 0.0036871 | 0.0060626 | -0.025757 | 0.0028113 | 0.00021363 | 0.0058276 | -0.00086511 | -0.0070753 | -0.00082886 | -52.6474 | 67.5659 | -55.3162 | 67.2318 | -54.7714 | -55.0735 | -54.4876 | -54.2221 | 67.6254 | -55.2979 | -55.0735 | -55.22 | -55.3711 | -55.0507 | -0.041199 | -0.018311 | -0.35248 | 0.50354 | 0.78735 | 0.20142 | 0.82855 | 0.24262 | -0.022889 | 0.041198 | -122.6578 | 0.054931 | 0.2243 | -0.096131 | 0.24719 | -0.073242 | 0.54474 | 122.5479 | 0.07782 | 0.22431 | 122.8821 | 122.9233 | 122.8409 | 122.9004 | -122.9004 | -122.8821 | 122.5067 | 0.20142 | 2.6276 | 1.0529
2954.1719 | 122.9141 | -55.2338 | 67.6025 | -0.12161 | -0.00066014 | 0.061812 | 0.070113 | 0.00037377 | 0.00069649 | 0.0045672 | -0.034912 | 0.00088875 | -0.00042717 | -0.0037854 | -0.0042831 | -0.0045117 | 0.0023755 | -52.6703 | 67.5888 | -55.2658 | 67.2729 | -54.8264 | -55.1605 | -54.5242 | -54.2267 | 67.6163 | -55.2704 | -55.0507 | -55.2979 | -55.307 | -55.0003 | -0.032043 | -0.013733 | -0.32959 | 0.40741 | 0.70953 | 0.073243 | 0.74158 | 0.10529 | -0.036621 | 0.013733 | -122.6532 | -0.064087 | 0.23346 | -0.073242 | 0.27008 | -0.036621 | 0.43945 | 122.5388 | -0.027466 | 0.21973 | 122.8546 | 122.8867 | 122.8226 | 122.85 | -122.8683 | -122.8729 | 122.5067 | 0.18311 | 2.5635 | 1.0071
2955.1719 | 122.9462 | -55.2155 | 67.5934 | -0.03006 | 0.00019446 | 0.060744 | 0.071395 | 0.0033646 | 0.0013373 | 0.0073444 | -0.034912 | 0.0015295 | 0.00085443 | -0.0010084 | -0.0042831 | -0.0042981 | 0.0036571 | -52.6245 | 67.598 | -55.2521 | 67.3462 | -54.7211 | -55.0781 | -54.4418 | -54.126 | 67.6575 | -55.2429 | -55.0415 | -55.1971 | -55.3574 | -55.0095 | -0.036621 | 0.004577 | -0.24719 | 0.49439 | 0.77362 | 0.13733 | 0.81024 | 0.17395 | -0.027466 | 0.064087 | -122.6349 | 0.01831 | 0.20599 | -0.14191 | 0.23346 | -0.11444 | 0.53101 | 122.5983 | 0.045776 | 0.20142 | 122.85 | 122.9004 | 122.8134 | 122.8729 | -122.8455 | -122.8363 | 122.5616 | 0.17395 | 2.5909 | 1.0895
2956.1719 | 122.905 | -55.2383 | 67.6117 | -0.060578 | 0.00062166 | 0.061812 | 0.069259 | 0.00037377 | 0.00091009 | 0.0052082 | -0.022705 | -0.00039305 | 0.0012818 | 0.0026232 | -0.0015061 | -0.0036573 | 0.00045294 | -52.6428 | 67.6346 | -55.2658 | 67.3233 | -54.744 | -55.101 | -54.483 | -54.2038 | 67.6117 | -55.2567 | -55.0781 | -55.22 | -55.3619 | -55.0232 | -0.027466 | 0.022889 | -0.28839 | 0.49438 | 0.75531 | 0.13733 | 0.78278 | 0.16479 | -0.018311 | 0 | -122.6898 | 0.01831 | 0.21515 | -0.1236 | 0.23346 | -0.10529 | 0.52185 | 122.5891 | 0.036621 | 0.17853 | 122.9004 | 122.8683 | 122.8729 | 122.85 | -122.8775 | -122.8683 | 122.5616 | 0.16022 | 2.5955 | 1.0345
2957.1719 | 122.9141 | -55.2383 | 67.6117 | -0.03006 | 0.00062166 | 0.061598 | 0.070754 | 0.0033646 | 0.00069649 | 0.0064898 | -0.034912 | 0.0013159 | -0.0012818 | 0.0036914 | -0.0021469 | -0.0040845 | 0.00023934 | -52.6199 | 67.6163 | -55.2246 | 67.3508 | -54.7256 | -55.069 | -54.4601 | -54.1306 | 67.662 | -55.2567 | -55.0369 | -55.1926 | -55.3574 | -55.0095 | 0.013733 | 0.004578 | -0.26093 | 0.5127 | 0.7782 | 0.16937 | 0.76447 | 0.15564 | -0.018311 | 0.050354 | -122.6486 | 0.045776 | 0.22888 | -0.11902 | 0.24719 | -0.10071 | 0.49896 | 122.5754 | 0.064087 | 0.21973 | 122.8409 | 122.9187 | 122.8546 | 122.9004 | -122.8363 | -122.8683 | 122.5891 | 0.20142 | 2.6184 | 1.1078
2958.1719 | 122.9462 | -55.2017 | 67.63 | -0.022431 | -0.00044654 | 0.062025 | 0.070968 | -0.0028304 | 0.0032599 | 0.0067036 | -0.028809 | 0.0021703 | 0.001068 | -0.0010084 | -0.0021469 | -0.0038709 | -0.0018971 | -52.6016 | 67.6392 | -55.2475 | 67.3737 | -54.6799 | -55.0369 | -54.4327 | -54.1122 | 67.6346 | -55.2383 | -55.0323 | -55.1651 | -55.3299 | -54.9911 | -0.045777 | 0.009155 | -0.25635 | 0.52185 | 0.76904 | 0.16479 | 0.81482 | 0.21057 | -0.036621 | 0.004578 | -122.6624 | 0.036621 | 0.21057 | -0.12817 | 0.24719 | -0.091553 | 0.56763 | 122.6212 | 0.073242 | 0.20599 | 122.8867 | 122.8729 | 122.8409 | 122.8363 | -122.8775 | -122.8683 | 122.5754 | 0.16937 | 2.6001 | 1.0895
2959.1719 | 122.9645 | -55.1788 | 67.6346 | -0.037689 | -0.00023294 | 0.063307 | 0.069686 | -0.00069423 | 0.0011237 | 0.0060626 | -0.025757 | 0.0021703 | 0.0021362 | -0.0027174 | -0.0010787 | -0.0055799 | 0.0017345 | -52.5833 | 67.6529 | -55.22 | 67.392 | -54.6661 | -55.0186 | -54.4144 | -54.0985 | 67.6392 | -55.22 | -55.014 | -55.1514 | -55.3162 | -54.9911 | -0.041199 | 0.01831 | -0.24262 | 0.5127 | 0.76446 | 0.16022 | 0.80566 | 0.20142 | -0.041199 | 0.004577 | -122.6486 | 0.027466 | 0.18768 | -0.13733 | 0.22888 | -0.09613 | 0.55389 | 122.612 | 0.068665 | 0.20599 | 122.8729 | 122.8592 | 122.8317 | 122.818 | -122.8546 | -122.8546 | 122.5708 | 0.16479 | 2.5955 | 1.0803
2960.1719 | 122.9141 | -55.2063 | 67.6209 | -0.075836 | 0.0025443 | 0.062239 | 0.071181 | -0.0013352 | 0.0013373 | 0.0069172 | -0.016602 | 0.0011023 | 0.0023498 | 0.0028368 | -0.0017197 | -0.0036573 | -0.0033923 | -52.5925 | 67.6392 | -55.2246 | 67.3416 | -54.7302 | -55.0598 | -54.4464 | -54.1306 | 67.6483 | -55.2429 | -55.0323 | -55.188 | -55.3482 | -55.0186 | -0.01831 | 0.01831 | -0.27924 | 0.47607 | 0.75989 | 0.14648 | 0.7782 | 0.16479 | -0.036621 | 0.027465 | -122.6532 | 0.018311 | 0.18768 | -0.14191 | 0.2243 | -0.10529 | 0.49438 | 122.5662 | 0.054932 | 0.21057 | 122.8638 | 122.8912 | 122.8455 | 122.8546 | -122.8455 | -122.8638 | 122.5479 | 0.17395 | 2.6138 | 1.0757
2961.1719 | 122.937 | -55.1788 | 67.6346 | -0.052948 | 0.0014761 | 0.059462 | 0.069045 | -0.0013352 | 0.0041143 | 0.0049946 | -0.010498 | 0.0025975 | 0.00085443 | 0.0015552 | -0.0025741 | -0.0025891 | 0.0013073 | -52.5742 | 67.6254 | -55.2155 | 67.3782 | -54.6936 | -55.0323 | -54.4327 | -54.1031 | 67.662 | -55.2155 | -55.0186 | -55.1559 | -55.3116 | -54.9545 | -0.036621 | -0.009156 | -0.25635 | 0.48523 | 0.74615 | 0.14648 | 0.78278 | 0.1831 | -0.036621 | 0.027465 | -122.6532 | 0.022888 | 0.2243 | -0.13275 | 0.26093 | -0.09613 | 0.52185 | 122.5937 | 0.059509 | 0.19684 | 122.8409 | 122.8775 | 122.8043 | 122.8409 | -122.85 | -122.85 | 122.5571 | 0.16022 | 2.6047 | 1.0757
2962.1719 | 122.9782 | -55.1514 | 67.6575 | -0.10635 | -0.0023691 | 0.063094 | 0.070541 | -5.343e-05 | 0.0011237 | 0.0037128 | 0.013916 | 0.00067495 | 0.0023498 | 5.9824e-05 | -0.0023605 | 0.0029651 | -0.0016833 | -52.5558 | 67.6483 | -55.2155 | 67.3874 | -54.657 | -54.9866 | -54.3823 | -54.0665 | 67.6758 | -55.2017 | -55.0964 | -55.0323 | -55.2521 | -54.9225 | -0.064087 | -0.009156 | -0.27008 | 0.49439 | 0.76904 | 0.16479 | 0.83313 | 0.22888 | -0.050354 | 0.01831 | -122.7539 | 0.11902 | 0.22888 | -0.10071 | 0.27924 | -0.050354 | 0.55847 | 122.6028 | 0.16937 | 0.10529 | 122.8638 | 122.8775 | 122.7997 | 122.8271 | -122.8729 | -122.8592 | 122.5388 | 0.054931 | 2.5955 | 1.0849
2963.1719 | 122.9645 | -55.1743 | 67.6437 | 0.038605 | 0.00040806 | 0.061598 | 0.069686 | 0.0018692 | 0.0021917 | 0.0015766 | 0.0078126 | 0.0011023 | 0.0023498 | -0.00015378 | -0.0025741 | -0.0055799 | 0.00023934 | -52.5558 | 67.6437 | -55.2063 | 67.4011 | -54.6478 | -55.0049 | -54.3915 | -54.0665 | 67.662 | -55.2155 | -55.0095 | -55.1376 | -55.275 | -54.9454 | -0.032044 | 0 | -0.24262 | 0.52643 | 0.78278 | 0.16937 | 0.81482 | 0.20142 | -0.041199 | 0.01831 | -122.6532 | 0.036621 | 0.22888 | -0.10071 | 0.27008 | -0.059509 | 0.55847 | 122.6074 | 0.07782 | 0.20599 | 122.85 | 122.8775 | 122.818 | 122.8363 | -122.85 | -122.8592 | 122.5754 | 0.1648 | 2.6184 | 1.1078
2964.1719 | 122.9553 | -55.1697 | 67.6346 | -0.075836 | 0.00062166 | 0.062025 | 0.067977 | -0.0021896 | 0.0011237 | 0.0069172 | -0.01355 | 0.00088875 | 0.00021363 | 0.00048702 | -0.0021469 | -0.0028027 | -0.0029651 | -52.5467 | 67.6392 | -55.1971 | 67.4606 | -54.6295 | -54.9591 | -54.3777 | -54.0527 | 67.6941 | -55.1788 | -54.9637 | -55.1193 | -55.2612 | -54.9591 | -0.027466 | 0.004577 | -0.17395 | 0.54016 | 0.79193 | 0.21057 | 0.8194 | 0.23804 | -0.009155 | 0.059509 | -122.5983 | 0.050354 | 0.21057 | -0.091552 | 0.21973 | -0.082397 | 0.56763 | 122.6578 | 0.059509 | 0.21515 | 122.8363 | 122.8729 | 122.8088 | 122.8638 | -122.8317 | -122.8134 | 122.6303 | 0.20599 | 2.623 | 1.1169
2965.1719 | 122.9691 | -55.1788 | 67.6575 | -0.091095 | 0.0019035 | 0.061385 | 0.068191 | 0.0018692 | 0.0032599 | 0.0052082 | 0.032227 | 0.0011023 | 0.006836 | 0.0013416 | -0.0030013 | -0.0053663 | 0.0015209 | -52.5467 | 67.6392 | -55.2246 | 67.4286 | -54.6249 | -54.982 | -54.3732 | -54.126 | 67.6575 | -55.2063 | -54.9637 | -55.1468 | -55.22 | -54.9179 | -0.045776 | -0.018311 | -0.22888 | 0.55389 | 0.80566 | 0.19684 | 0.85144 | 0.24261 | -0.027466 | 0 | -122.6212 | 0.032043 | 0.26093 | -0.041199 | 0.28839 | -0.013733 | 0.59967 | 122.6532 | 0.059509 | 0.24262 | 122.8638 | 122.8638 | 122.818 | 122.8363 | -122.8821 | -122.8638 | 122.6074 | 0.21515 | 2.6321 | 1.0529
2966.1719 | 122.905 | -55.1559 | 67.6437 | -0.052948 | 0.0010489 | 0.062453 | 0.066909 | -0.00048063 | 0.0039007 | 0.0054218 | 0.013916 | 0.00067495 | 0.0014954 | 0.0043322 | -0.0012925 | -0.0034437 | -0.00040166 | -52.5284 | 67.662 | -55.22 | 67.4286 | -54.6433 | -54.9866 | -54.364 | -54.0482 | 67.6666 | -55.1788 | -54.95 | -55.0964 | -55.1697 | -55.069 | -0.064087 | 0.01831 | -0.21515 | 0.5127 | 0.79193 | 0.16937 | 0.85602 | 0.23346 | -0.022888 | 0.022888 | -122.5937 | 0.059509 | 0.086975 | -0.013733 | 0.10986 | 0.009155 | 0.57678 | 122.6486 | 0.082397 | 0.22888 | 122.8821 | 122.8455 | 122.818 | 122.8226 | -122.8638 | -122.8226 | 122.5845 | 0.20599 | 2.6276 | 1.1078
2967.1719 | 122.9507 | -55.1651 | 67.6392 | -0.10635 | 0.00062166 | 0.06053 | 0.070541 | -0.00048063 | 0.0030463 | 0.0086262 | 0.02002 | 0.0017431 | 0.0012818 | 0.003905 | -0.0023605 | -0.0057935 | 0.0019483 | -52.5421 | 67.6758 | -55.2063 | 67.4332 | -54.6204 | -55.0049 | -54.3686 | -54.0344 | 67.6895 | -55.188 | -54.9591 | -55.1239 | -55.2567 | -54.9271 | -0.041199 | 0.036621 | -0.20599 | 0.54474 | 0.79651 | 0.16022 | 0.83771 | 0.20142 | -0.022888 | 0.050354 | -122.5983 | 0.041199 | 0.23804 | -0.091553 | 0.26093 | -0.068665 | 0.58594 | 122.6395 | 0.064087 | 0.22888 | 122.8821 | 122.8775 | 122.8409 | 122.8546 | -122.8455 | -122.8271 | 122.5983 | 0.20599 | 2.623 | 1.1307
2968.1719 | 122.9691 | -55.1422 | 67.6575 | -0.10635 | -0.00023294 | 0.063094 | 0.070754 | 0.0010148 | 0.0028327 | 0.0047808 | -0.12646 | 0.0013159 | 0.0019226 | -0.00464 | -0.0021469 | -0.0062207 | -0.0018971 | -52.5192 | 67.6483 | -55.1926 | 67.4332 | -54.6204 | -54.9637 | -54.3549 | -53.9566 | 67.6987 | -55.1788 | -54.95 | -55.0781 | -55.2383 | -54.9225 | -0.050354 | -0.009156 | -0.2243 | 0.52185 | 0.78735 | 0.17853 | 0.83771 | 0.22888 | -0.036621 | 0.041198 | -122.6074 | 0.064087 | 0.21973 | -0.09613 | 0.25635 | -0.059509 | 0.5722 | 122.6257 | 0.10071 | 0.22888 | 122.8409 | 122.8775 | 122.7905 | 122.8409 | -122.85 | -122.8363 | 122.5754 | 0.19226 | 2.623 | 1.1856
2969.1719 | 122.9736 | -55.1422 | 67.6804 | -0.014801 | 0.0010489 | 0.060957 | 0.070968 | 0.00080117 | 0.0021917 | 0.0049946 | 0.023071 | -0.00060665 | 0.003418 | -0.0031446 | -0.0032151 | -0.0062207 | 0.0030163 | -52.5375 | 67.6712 | -55.1468 | 67.4194 | -54.6524 | -54.95 | -54.3594 | -54.0619 | 67.7078 | -55.1697 | -54.95 | -55.0827 | -55.2246 | -54.9225 | -0.004578 | -0.009155 | -0.26093 | 0.48981 | 0.78278 | 0.19226 | 0.78735 | 0.19684 | -0.027466 | 0.027466 | -122.6303 | 0.059509 | 0.21973 | -0.082397 | 0.24719 | -0.054931 | 0.49439 | 122.5662 | 0.086975 | 0.21973 | 122.818 | 122.8775 | 122.8134 | 122.85 | -122.8271 | -122.85 | 122.5616 | 0.19226 | 2.6047 | 1.0803
2970.1719 | 122.9599 | -55.1331 | 67.6849 | -0.052948 | 0.00062166 | 0.061812 | 0.069259 | 0.0027238 | 0.0015509 | 0.0054218 | -0.016602 | -0.00039305 | 0.0036316 | -0.0010084 | -0.0032151 | -0.0049389 | 2.554e-05 | -52.4872 | 67.6895 | -55.1971 | 67.4561 | -54.6021 | -54.95 | -54.3686 | -54.0253 | 67.6758 | -55.1697 | -54.95 | -55.0781 | -55.2246 | -54.9179 | -0.064087 | 0.004577 | -0.22888 | 0.53101 | 0.76447 | 0.18311 | 0.82855 | 0.24719 | -0.036621 | -0.009156 | -122.6349 | 0.054932 | 0.21515 | -0.091552 | 0.25177 | -0.054931 | 0.59509 | 122.6532 | 0.091553 | 0.21973 | 122.8867 | 122.8455 | 122.8226 | 122.8088 | -122.8821 | -122.8546 | 122.5891 | 0.18311 | 2.6459 | 1.1078
2971.1719 | 122.9645 | -55.1193 | 67.6895 | -0.091095 | -0.0017281 | 0.059889 | 0.068404 | -0.0013352 | 0.0011237 | 0.00414 | 0.02002 | -0.00039305 | 0.0040588 | 0.0077502 | -0.0023605 | -0.0047253 | 0.0017345 | -52.5055 | 67.7078 | -55.1834 | 67.4515 | -54.6387 | -54.9454 | -54.3549 | -54.0207 | 67.7353 | -55.1422 | -54.95 | -55.0827 | -55.2063 | -54.895 | -0.064087 | 0.018311 | -0.23804 | 0.48065 | 0.76447 | 0.17395 | 0.82855 | 0.23804 | -0.022888 | 0.045777 | -122.6395 | 0.036621 | 0.2243 | -0.086975 | 0.24719 | -0.064087 | 0.54474 | 122.6349 | 0.059509 | 0.19226 | 122.8912 | 122.8775 | 122.8271 | 122.8546 | -122.8729 | -122.8317 | 122.5708 | 0.16937 | 2.6138 | 1.0986
2972.1719 | 122.9645 | -55.1193 | 67.6895 | -0.052948 | -1.9142e-05 | 0.062453 | 0.068404 | 0.00037377 | 0.0041143 | 0.0056354 | 0.035278 | 0.00067495 | 0.0021362 | -0.0016492 | -0.0036423 | -0.0057935 | 0.0015209 | -52.5146 | 67.7216 | -55.1468 | 67.4469 | -54.6295 | -54.9362 | -54.3411 | -54.0527 | 67.7353 | -55.1559 | -54.9545 | -55.069 | -55.2155 | -54.9042 | -0.027466 | 0.032044 | -0.24262 | 0.48981 | 0.7782 | 0.18311 | 0.80567 | 0.21057 | -0.036621 | 0.045777 | -122.644 | 0.050354 | 0.21515 | -0.09613 | 0.25177 | -0.059509 | 0.51727 | 122.5937 | 0.086975 | 0.20142 | 122.8683 | 122.8912 | 122.8409 | 122.8546 | -122.8363 | -122.8455 | 122.5662 | 0.16479 | 2.6047 | 1.0666
2973.1719 | 122.9691 | -55.1102 | 67.7032 | -0.098725 | -0.00066014 | 0.059889 | 0.068618 | -0.0024032 | 0.0026191 | 0.0047808 | 0.044434 | 0.0017431 | 0.0023498 | 0.0013416 | -0.0015061 | -0.0047253 | -0.0027515 | -52.5055 | 67.6987 | -55.1193 | 67.4286 | -54.6387 | -54.95 | -54.3594 | -54.0619 | 67.7307 | -55.1651 | -54.9637 | -55.0644 | -55.2155 | -54.9179 | -0.009156 | -0.004578 | -0.27466 | 0.4715 | 0.75073 | 0.16022 | 0.75989 | 0.16937 | -0.054932 | 0.027466 | -122.6669 | 0.045776 | 0.19226 | -0.10529 | 0.24719 | -0.050354 | 0.48065 | 122.5479 | 0.10071 | 0.20142 | 122.818 | 122.8958 | 122.8088 | 122.8409 | -122.8226 | -122.8683 | 122.5388 | 0.14648 | 2.6047 | 1.0483
2974.1719 | 122.9599 | -55.1147 | 67.6895 | -0.03006 | 0.0010489 | 0.062666 | 0.0699 | -5.343e-05 | 0.0017645 | 0.0064898 | 0.001709 | -0.0012477 | 0.0012818 | 0.0030506 | -0.0032151 | -0.0064343 | 0.0017345 | -52.478 | 67.7216 | -55.1468 | 67.4606 | -54.6021 | -54.9408 | -54.3365 | -54.0024 | 67.7078 | -55.1605 | -54.9179 | -55.0644 | -55.22 | -54.9088 | -0.032044 | 0.032044 | -0.22888 | 0.51269 | 0.7782 | 0.17395 | 0.81024 | 0.20599 | -0.045776 | 0.018311 | -122.6074 | 0.050354 | 0.20599 | -0.10529 | 0.25177 | -0.05951 | 0.54474 | 122.6074 | 0.09613 | 0.24261 | 122.8683 | 122.8683 | 122.8363 | 122.8226 | -122.8363 | -122.85 | 122.5754 | 0.19684 | 2.6367 | 1.1124
2975.1719 | 123.0057 | -55.1193 | 67.7124 | -0.060578 | -0.0023691 | 0.062239 | 0.070754 | -0.00069423 | 0.0049689 | 0.0079852 | 0.013916 | 0.00024775 | 0.00021363 | 0.0034778 | -0.0025741 | -0.0047253 | -0.0012561 | -52.5009 | 67.7353 | -55.1422 | 67.4561 | -54.6158 | -54.9179 | -54.3503 | -54.0253 | 67.749 | -55.1559 | -54.9454 | -55.0552 | -55.2109 | -54.8904 | -0.022888 | 0.022889 | -0.25635 | 0.50354 | 0.76904 | 0.20142 | 0.79193 | 0.2243 | -0.036621 | 0.036621 | -122.6578 | 0.064087 | 0.22888 | -0.091552 | 0.2655 | -0.054931 | 0.52643 | 122.5983 | 0.10071 | 0.21057 | 122.8775 | 122.905 | 122.8546 | 122.8683 | -122.8546 | -122.8683 | 122.5754 | 0.17395 | 2.6184 | 1.0941
2976.1719 | 122.905 | -55.1239 | 67.7307 | -0.15213 | -0.0019417 | 0.060957 | 0.069259 | -0.00090783 | 0.0030463 | 0.0045672 | 0.050537 | 0.0028113 | 0.0036316 | 0.0015552 | -0.0017197 | -0.0053663 | 2.554e-05 | -52.5101 | 67.7811 | -55.1376 | 67.4057 | -54.6433 | -54.9591 | -54.3365 | -54.0619 | 67.7536 | -55.1514 | -54.9591 | -55.0735 | -55.1971 | -54.9316 | -0.013733 | 0.050354 | -0.32501 | 0.48065 | 0.78735 | 0.16479 | 0.80109 | 0.17853 | -0.027466 | 0.022888 | -122.6898 | 0.050354 | 0.19226 | -0.073243 | 0.21973 | -0.045777 | 0.49438 | 122.5433 | 0.07782 | 0.19226 | 122.9187 | 122.905 | 122.905 | 122.8775 | -122.8683 | -122.8821 | 122.5296 | 0.16479 | 2.6138 | 1.062
2977.1719 | 122.9507 | -55.1102 | 67.7353 | -0.083466 | -0.00087374 | 0.061171 | 0.069045 | -0.00048063 | 0.0030463 | 0.0077716 | 0.044434 | 0.0017431 | 0.00042723 | 0.0026232 | -0.0040695 | -0.0066479 | 0.00045294 | -52.4963 | 67.7582 | -55.1514 | 67.4423 | -54.6249 | -54.9454 | -54.3503 | -54.0344 | 67.7353 | -55.1285 | -54.9454 | -55.0415 | -55.1971 | -54.8996 | -0.041199 | 0.022888 | -0.29297 | 0.48523 | 0.75989 | 0.16479 | 0.80109 | 0.20599 | -0.018311 | 0 | -122.6807 | 0.068664 | 0.21057 | -0.086976 | 0.22888 | -0.068665 | 0.52643 | 122.5937 | 0.086975 | 0.1831 | 122.9095 | 122.8638 | 122.8683 | 122.8455 | -122.8867 | -122.8638 | 122.5525 | 0.16479 | 2.6138 | 1.0757
2978.1719 | 122.9141 | -55.1468 | 67.6941 | -0.11398 | 0.00062166 | 0.063094 | 0.071181 | 0.0027238 | 0.0015509 | 0.0077716 | -0.025757 | 0.0019567 | 2.8e-08 | 0.0013416 | -0.0010787 | -0.0032301 | -0.00082886 | -52.5192 | 67.7032 | -55.1834 | 67.4011 | -54.6616 | -55.0369 | -54.4052 | -54.1077 | 67.7261 | -55.1697 | -55.0003 | -55.1468 | -55.307 | -54.9454 | -0.036621 | 0.009155 | -0.29297 | 0.48523 | 0.74158 | 0.10986 | 0.7782 | 0.14648 | -0.022888 | 0.032043 | -122.6944 | 0 | 0.20142 | -0.16022 | 0.2243 | -0.13733 | 0.52185 | 122.5845 | 0.022888 | 0.16937 | 122.8867 | 122.8958 | 122.85 | 122.8729 | -122.8775 | -122.8638 | 122.5479 | 0.14649 | 2.6276 | 1.0391
2979.1719 | 122.9507 | -55.0964 | 67.7399 | -0.052948 | 0.00040806 | 0.062666 | 0.068191 | -5.343e-05 | 0.0013373 | 0.0073444 | 0.013916 | 0.0021703 | 0.001068 | -0.0010084 | -0.0023605 | -0.0047253 | 0.0019483 | -52.5101 | 67.7582 | -55.1605 | 67.4332 | -54.6158 | -54.9454 | -54.3274 | -54.0436 | 67.7582 | -55.1468 | -54.9591 | -55.069 | -55.22 | -54.9179 | -0.064086 | 0.018311 | -0.3067 | 0.48065 | 0.76904 | 0.15106 | 0.83313 | 0.21515 | -0.050354 | 0.018311 | -122.699 | 0.027466 | 0.17853 | -0.1236 | 0.22888 | -0.073242 | 0.54474 | 122.5937 | 0.07782 | 0.18768 | 122.9187 | 122.905 | 122.8546 | 122.8546 | -122.9004 | -122.8867 | 122.5296 | 0.13733 | 2.5864 | 1.0529
2980.1719 | 122.9416 | -55.1376 | 67.7582 | -0.03006 | -0.00066014 | 0.06288 | 0.068191 | 0.00016017 | 0.00091009 | 0.0056354 | 0.026123 | 0.0015295 | 0.0025634 | 0.0015552 | -0.0034287 | -0.0072889 | -0.00061526 | -52.4734 | 67.7536 | -55.1376 | 67.3096 | -54.6021 | -54.9271 | -54.3594 | -54.0298 | 67.7628 | -55.1468 | -54.9591 | -55.0552 | -55.1788 | -54.9088 | 0 | -0.004578 | -0.44861 | 0.53558 | 0.7782 | 0.21057 | 0.7782 | 0.21057 | -0.009156 | 0.004577 | -122.7173 | 0.082397 | 0.22888 | -0.041199 | 0.23804 | -0.032043 | 0.53558 | 122.4472 | 0.091553 | 0.18768 | 122.8912 | 122.9095 | 122.8912 | 122.9004 | -122.8958 | -122.905 | 122.4472 | 0.17853 | 2.6642 | 1.1078
2981.1719 | 122.9324 | -55.0781 | 67.7536 | -0.10635 | 0.0014761 | 0.059889 | 0.069259 | -0.0013352 | 0.0011237 | 0.0086262 | 0.013916 | 0.0013159 | 0.001068 | 0.0075366 | -0.0036423 | -0.0047253 | -0.00040166 | -52.4597 | 67.717 | -55.1468 | 67.4561 | -54.6204 | -54.9271 | -54.3365 | -54.0161 | 67.7536 | -55.1285 | -54.9088 | -55.0415 | -55.1743 | -54.8767 | -0.068665 | -0.036621 | -0.29755 | 0.45776 | 0.74158 | 0.15106 | 0.81024 | 0.21973 | -0.050354 | 0 | -122.6624 | 0.036621 | 0.20142 | -0.09613 | 0.25177 | -0.045776 | 0.52643 | 122.6028 | 0.086975 | 0.21973 | 122.8638 | 122.8821 | 122.7951 | 122.8317 | -122.9004 | -122.8821 | 122.5342 | 0.16937 | 2.6184 | 1.062
2982.1719 | 122.8958 | -55.0873 | 67.7444 | -0.068207 | -0.0015145 | 0.059676 | 0.068832 | 0.00080117 | 0.0021917 | 0.0037128 | 0.044434 | -0.00082025 | -0.00021357 | 5.9824e-05 | -0.0015061 | -0.0053663 | 0.00045294 | -52.4918 | 67.7536 | -55.1376 | 67.4652 | -54.5975 | -54.9225 | -54.3091 | -54.0161 | 67.7994 | -55.1285 | -54.9728 | -54.8126 | -55.1834 | -54.9225 | -0.050354 | 0.009155 | -0.27924 | 0.48981 | 0.7782 | 0.16479 | 0.82855 | 0.21515 | -0.041199 | 0.054931 | -122.7173 | 0.27466 | 0.16479 | -0.096131 | 0.20599 | -0.054932 | 0.54016 | 122.6028 | 0.31586 | 0.15564 | 122.8912 | 122.9279 | 122.8409 | 122.8867 | -122.8821 | -122.8729 | 122.5525 | 0.11444 | 2.5955 | 1.0712
2983.1719 | 122.9507 | -55.0964 | 67.7261 | -0.10635 | 0.00019446 | 0.062453 | 0.070327 | -0.00048063 | 0.0026191 | 0.0056354 | -0.047119 | -0.0010339 | 0.00064083 | 0.003905 | -0.0055649 | -0.0053663 | 0.0017345 | -52.5009 | 67.7124 | -55.1697 | 67.392 | -54.6982 | -55.0461 | -54.4006 | -54.0619 | 67.7307 | -55.1788 | -54.8401 | -55.1743 | -55.22 | -54.8767 | -0.073242 | -0.013733 | -0.33417 | 0.39825 | 0.6958 | 0.050354 | 0.76904 | 0.1236 | -0.082397 | 0.004578 | -122.5662 | -0.077819 | 0.21973 | -0.1236 | 0.30212 | -0.041199 | 0.4715 | 122.5616 | 0.004578 | 0.33874 | 122.8821 | 122.9095 | 122.8088 | 122.8271 | -122.8958 | -122.905 | 122.4884 | 0.25635 | 2.5955 | 1.0345
2984.1719 | 122.9324 | -55.0827 | 67.7536 | -0.045319 | 0.00040806 | 0.060744 | 0.0699 | 0.0029374 | 0.0028327 | 0.0067036 | 0.010864 | 0.0015295 | -0.00042717 | 0.00091422 | -0.0019333 | -0.0053663 | -0.0025379 | -52.4689 | 67.7811 | -55.1376 | 67.5247 | -54.3503 | -54.9728 | -54.4327 | -54.0253 | 67.7765 | -55.1239 | -54.9042 | -55.0369 | -55.1788 | -54.8904 | -0.054931 | 0.027466 | -0.22888 | 0.73242 | 0.65002 | 0.10986 | 0.70496 | 0.16479 | -0.041198 | 0.022888 | -122.6578 | 0.045777 | 0.19226 | -0.09613 | 0.23346 | -0.054932 | 0.78735 | 122.6624 | 0.086975 | 0.21973 | 122.9187 | 122.9004 | 122.8638 | 122.8592 | -122.8912 | -122.8775 | 122.6074 | 0.17853 | 2.6138 | 1.0574
2985.1719 | 122.905 | -55.1102 | 67.7673 | -0.091095 | -0.00023294 | 0.060744 | 0.069472 | -5.343e-05 | 0.00091009 | 0.007558 | 0.026123 | 0.0013159 | 0.00042723 | -0.0042126 | -0.0015061 | -0.0053663 | 0.00023934 | -52.4689 | 67.7628 | -55.0964 | 67.4789 | -54.5837 | -54.9042 | -54.2953 | -54.0253 | 67.7948 | -55.1193 | -55.0095 | -55.0919 | -55.1697 | -54.8813 | 0.013732 | -0.004578 | -0.28839 | 0.52643 | 0.81482 | 0.20599 | 0.80109 | 0.19226 | -0.009156 | 0.027466 | -122.7768 | 0.01831 | 0.22888 | -0.05951 | 0.23804 | -0.050354 | 0.5127 | 122.5754 | 0.027466 | 0.10986 | 122.8592 | 122.9141 | 122.8729 | 122.905 | -122.8638 | -122.8867 | 122.5891 | 0.10071 | 2.6413 | 1.0849
2986.1719 | 122.937 | -55.0598 | 67.7856 | -0.022431 | -0.00023294 | 0.060957 | 0.068618 | -0.00090783 | 0.0053961 | 0.0062762 | 0.041382 | 0.0036657 | 0.0038452 | 0.0036914 | -0.0019333 | -0.0060071 | -0.0018971 | -52.446 | 67.7582 | -55.101 | 67.4789 | -54.5792 | -54.9133 | -54.3091 | -53.9886 | 67.7994 | -55.1102 | -54.9088 | -55.0186 | -55.1743 | -54.8996 | -0.041199 | -0.027466 | -0.3067 | 0.48065 | 0.75073 | 0.14648 | 0.79193 | 0.18768 | -0.050354 | 0.013732 | -122.6944 | 0.041198 | 0.16022 | -0.11444 | 0.21057 | -0.064087 | 0.52185 | 122.58 | 0.091552 | 0.20142 | 122.8592 | 122.9095 | 122.818 | 122.8592 | -122.8867 | -122.8958 | 122.5388 | 0.15106 | 2.6138 | 1.0712
2987.1719 | 122.9324 | -55.0598 | 67.7719 | -0.075836 | 0.0010489 | 0.06053 | 0.068191 | -0.0011214 | 0.00048269 | 0.0045672 | 0.062744 | -0.00017945 | 0.0023498 | -0.0010084 | -0.0015061 | -0.0049389 | -0.00040166 | -52.4231 | 67.7673 | -55.1147 | 67.511 | -54.5425 | -54.8721 | -54.2908 | -53.9703 | 67.7902 | -55.0964 | -54.9133 | -55.014 | -55.1422 | -54.8767 | -0.054932 | -0.004578 | -0.26093 | 0.51727 | 0.76904 | 0.18768 | 0.82397 | 0.24261 | -0.036622 | 0.01831 | -122.6852 | 0.045776 | 0.18311 | -0.082398 | 0.21973 | -0.045776 | 0.5722 | 122.6257 | 0.082398 | 0.18311 | 122.8821 | 122.8867 | 122.8271 | 122.85 | -122.8867 | -122.8683 | 122.5708 | 0.14648 | 2.6367 | 1.0895
2988.1719 | 123.024 | -55.1056 | 67.7078 | -0.15976 | -0.0013009 | 0.061812 | 0.072463 | 0.001442 | 0.0041143 | 0.0049946 | -0.0074462 | 0.0028113 | 0.001068 | 0.0032642 | -0.0049241 | -0.0053663 | -0.0025379 | -52.4826 | 67.7124 | -55.1559 | 67.4927 | -54.5837 | -54.9454 | -54.3137 | -53.9566 | 67.7582 | -55.101 | -54.8538 | -55.0049 | -55.1422 | -54.8126 | -0.050354 | 0.004577 | -0.21515 | 0.52185 | 0.79193 | 0.16022 | 0.84229 | 0.21057 | 0.004578 | 0.050354 | -122.5616 | 0.10071 | 0.29297 | -0.036621 | 0.28839 | -0.041199 | 0.57221 | 122.6486 | 0.09613 | 0.24719 | 122.8683 | 122.8592 | 122.818 | 122.8638 | -122.8638 | -122.8088 | 122.5983 | 0.25177 | 2.623 | 1.149
2989.1719 | 122.9416 | -55.0644 | 67.7444 | -0.098725 | 0.00019446 | 0.060957 | 0.068404 | -0.0017624 | 0.0030463 | 0.0060626 | 0.044434 | -0.00039305 | 0.0019226 | -0.0042126 | -0.00022431 | -0.0055799 | -0.0044605 | -52.3911 | 67.7399 | -55.0873 | 67.5705 | -54.4785 | -54.8309 | -54.2084 | -53.9154 | 67.7856 | -55.0873 | -54.8813 | -55.0095 | -55.1285 | -54.8309 | -0.022888 | -0.004578 | -0.17395 | 0.58594 | 0.85602 | 0.23346 | 0.87891 | 0.25635 | -0.022888 | 0.041199 | -122.6257 | 0.054932 | 0.23346 | -0.064087 | 0.25635 | -0.041199 | 0.60883 | 122.6578 | 0.07782 | 0.20599 | 122.8271 | 122.8729 | 122.8043 | 122.85 | -122.8317 | -122.8317 | 122.6349 | 0.1831 | 2.6733 | 1.149
2990.1719 | 122.9553 | -55.0323 | 67.7948 | -0.098725 | -0.00087374 | 0.063307 | 0.069045 | 0.0010148 | -0.00015811 | 0.0060626 | 0.041382 | 0.00046135 | -0.0014954 | -0.00229 | -0.0038559 | -0.0072889 | -0.0016833 | -52.3727 | 67.7399 | -55.0644 | 67.5842 | -54.4693 | -54.8126 | -54.1946 | -53.9017 | 67.7765 | -55.0781 | -54.8447 | -54.9591 | -55.1102 | -54.8172 | -0.032043 | -0.054932 | -0.21057 | 0.56305 | 0.83771 | 0.21973 | 0.86975 | 0.25177 | -0.045776 | -0.018311 | -122.6395 | 0.073243 | 0.21515 | -0.077819 | 0.26093 | -0.032043 | 0.59509 | 122.6486 | 0.11902 | 0.23346 | 122.8043 | 122.8546 | 122.7722 | 122.8088 | -122.8592 | -122.8729 | 122.6166 | 0.18768 | 2.6596 | 1.1307
2991.1719 | 122.9324 | -55.0369 | 67.7994 | -0.075836 | -0.0010873 | 0.060744 | 0.0699 | 0.0016556 | -0.00015811 | 0.0052082 | 0.032227 | 0.0028113 | 0.00042723 | 0.0013416 | -0.0010787 | -0.0047253 | -0.00040166 | -52.3956 | 67.7994 | -55.0827 | 67.543 | -54.5334 | -54.8859 | -54.2633 | -53.952 | 67.7994 | -55.0644 | -54.8904 | -54.982 | -55.1376 | -54.863 | -0.045777 | 0 | -0.25635 | 0.50354 | 0.77362 | 0.15106 | 0.8194 | 0.19684 | -0.027466 | 0 | -122.6898 | 0.054931 | 0.17395 | -0.10071 | 0.20142 | -0.073242 | 0.54932 | 122.6257 | 0.082397 | 0.17395 | 122.8821 | 122.8638 | 122.8363 | 122.8363 | -122.8821 | -122.8638 | 122.58 | 0.14648 | 2.6413 | 1.0849
2992.1719 | 122.8958 | -55.0369 | 67.7994 | -0.052948 | 0.00062166 | 0.060957 | 0.069686 | -0.00026703 | 0.0013373 | 0.0047808 | 0.044434 | 0.0011023 | 0.001068 | -0.00015378 | -0.0012925 | -0.0068615 | -0.00082886 | -52.3727 | 67.7673 | -55.0735 | 67.5613 | -54.5059 | -54.8401 | -54.2542 | -53.92 | 67.8268 | -55.0552 | -54.8859 | -54.9957 | -55.1468 | -54.8492 | -0.036621 | -0.032043 | -0.23804 | 0.53101 | 0.78278 | 0.19684 | 0.8194 | 0.23346 | -0.018311 | 0.027466 | -122.6852 | 0.041198 | 0.18768 | -0.10986 | 0.20599 | -0.091553 | 0.56763 | 122.6349 | 0.059509 | 0.16937 | 122.8409 | 122.8821 | 122.8043 | 122.8638 | -122.8729 | -122.8546 | 122.5983 | 0.15106 | 2.6642 | 1.1169
2993.1719 | 123.0057 | -55.0415 | 67.6758 | -0.091095 | -0.00023294 | 0.060316 | 0.069259 | 0.00080117 | 0.0051825 | 0.003072 | -0.019653 | -0.00017945 | 0.00042723 | -0.0044262 | -0.0044967 | -0.0047253 | 0.0032299 | -52.3911 | 67.717 | -55.0964 | 67.5842 | -54.4922 | -54.8355 | -54.2175 | -53.8651 | 67.7444 | -55.0827 | -54.776 | -54.9454 | -55.0964 | -54.7668 | -0.054932 | 0.041199 | -0.091552 | 0.54932 | 0.82398 | 0.20599 | 0.87891 | 0.26093 | -0.041199 | 0.068665 | -122.4518 | 0.09613 | 0.27466 | -0.054932 | 0.31586 | -0.013733 | 0.60425 | 122.6807 | 0.13733 | 0.3067 | 122.8134 | 122.8271 | 122.7585 | 122.7859 | -122.7722 | -122.7585 | 122.6257 | 0.2655 | 2.6505 | 1.1765
2994.1719 | 122.9782 | -55.0232 | 67.7811 | -0.068207 | -0.0023691 | 0.062453 | 0.066695 | -0.0030442 | 0.00069649 | 0.00414 | 0.010864 | 0.00067495 | 0.0032044 | -0.0027174 | -0.0019333 | -0.0057935 | 0.0025891 | -52.3499 | 67.7628 | -55.0552 | 67.598 | -54.4373 | -54.7989 | -54.1855 | -53.8788 | 67.8177 | -55.0278 | -54.8218 | -54.95 | -55.0873 | -54.808 | -0.032044 | -0.018311 | -0.18311 | 0.58594 | 0.83771 | 0.2243 | 0.86975 | 0.25635 | -0.004578 | 0.036621 | -122.6028 | 0.073242 | 0.21515 | -0.064087 | 0.21973 | -0.059509 | 0.61798 | 122.6532 | 0.07782 | 0.20599 | 122.818 | 122.8455 | 122.7859 | 122.8409 | -122.8363 | -122.8088 | 122.6212 | 0.20142 | 2.6733 | 1.1444
2995.1719 | 122.9462 | -55.0186 | 67.8177 | -0.03006 | -0.0017281 | 0.060744 | 0.070754 | 0.001442 | 0.0021917 | 0.0047808 | -0.019653 | 0.0013159 | 0.0023498 | 0.0034778 | -0.0017197 | -0.0055799 | -0.0012561 | -52.3819 | 67.7994 | -55.069 | 67.543 | -54.5151 | -54.8584 | -54.2404 | -53.9474 | 67.8406 | -55.0644 | -54.8584 | -54.982 | -55.1285 | -54.8538 | -0.050354 | -0.018311 | -0.27466 | 0.50354 | 0.7782 | 0.16022 | 0.82855 | 0.21057 | -0.045776 | 0.022888 | -122.6761 | 0.036621 | 0.16479 | -0.10986 | 0.21057 | -0.064087 | 0.55389 | 122.612 | 0.082397 | 0.20599 | 122.8683 | 122.905 | 122.818 | 122.8592 | -122.8867 | -122.8821 | 122.5616 | 0.16022 | 2.6367 | 1.0712
2996.1719 | 123.0011 | -55.0095 | 67.7536 | -0.083466 | -1.9142e-05 | 0.059889 | 0.069472 | -0.0024032 | 0.0034735 | 0.0039264 | 0.03833 | -0.00082025 | 0.00021363 | -0.0084852 | -0.0025741 | -0.0060071 | 0.00066654 | -52.327 | 67.7628 | -55.0644 | 67.6254 | -54.4281 | -54.7668 | -54.1489 | -53.8284 | 67.7811 | -55.0323 | -54.7852 | -54.8813 | -55.0278 | -54.7348 | -0.054932 | 0.009155 | -0.12817 | 0.58136 | 0.86059 | 0.24261 | 0.91553 | 0.29755 | -0.022889 | 0.027466 | -122.5388 | 0.12817 | 0.27466 | -0.018311 | 0.29755 | 0.004578 | 0.63629 | 122.6898 | 0.15106 | 0.24719 | 122.8271 | 122.8134 | 122.7722 | 122.7905 | -122.818 | -122.786 | 122.6349 | 0.2243 | 2.6825 | 1.181
2997.1719 | 123.0103 | -55.0415 | 67.7902 | -0.091095 | 0.0014761 | 0.061812 | 0.067763 | -0.0030442 | 0.0015509 | 0.0071308 | 0.023071 | -0.00060665 | 0.00021363 | -0.0080578 | -0.0019333 | -0.0075025 | -0.0025379 | -52.3407 | 67.7628 | -55.0552 | 67.6529 | -54.3915 | -54.7577 | -54.1443 | -53.8147 | 67.7902 | -55.0323 | -54.7668 | -54.863 | -55.0049 | -54.7394 | -0.013733 | -0.027466 | -0.13733 | 0.65003 | 0.89722 | 0.28381 | 0.91095 | 0.29755 | 0.009155 | 0 | -122.5571 | 0.17853 | 0.30212 | 0.036621 | 0.29297 | 0.027466 | 0.66376 | 122.7081 | 0.16937 | 0.2655 | 122.818 | 122.8226 | 122.8043 | 122.8317 | -122.8455 | -122.8226 | 122.6944 | 0.27466 | 2.7008 | 1.2268
2998.1719 | 122.9691 | -55.0049 | 67.7856 | -0.11398 | 0.0012625 | 0.061812 | 0.068618 | 0.0022964 | 0.0019781 | 0.0060626 | 0.010864 | 0.00024775 | 0.0019226 | -0.001222 | -0.0023605 | -0.0070753 | 0.0017345 | -52.3224 | 67.7902 | -55.0507 | 67.63 | -54.4189 | -54.7577 | -54.1626 | -53.8513 | 67.8497 | -55.0507 | -54.808 | -54.9271 | -55.0735 | -54.776 | -0.045776 | 0.004577 | -0.15564 | 0.58594 | 0.84228 | 0.24719 | 0.88806 | 0.29297 | -0.045776 | 0.064086 | -122.5937 | 0.07782 | 0.22888 | -0.068664 | 0.27466 | -0.022888 | 0.63171 | 122.6807 | 0.1236 | 0.24262 | 122.8409 | 122.9004 | 122.7951 | 122.8546 | -122.8363 | -122.8363 | 122.6349 | 0.19684 | 2.6825 | 1.1536
2999.1719 | 123.0148 | -54.982 | 67.7628 | -0.13687 | 0.0010489 | 0.061812 | 0.069045 | -0.0045394 | 0.0017645 | 0.0067036 | 0.0078126 | 0.0013159 | -0.0012818 | -0.0016492 | -0.0023605 | -0.0034437 | 0.0013073 | -52.2949 | 67.7948 | -55.0323 | 67.5751 | -54.6753 | -54.7989 | -54.0894 | -53.7689 | 67.7811 | -55.0323 | -54.7668 | -54.8309 | -54.9683 | -54.7211 | -0.050354 | 0.032044 | -0.18768 | 0.3067 | 0.89264 | 0.18311 | 0.94299 | 0.23346 | -0.050354 | 0.018311 | -122.5296 | 0.15106 | 0.26093 | 0.013733 | 0.31128 | 0.064087 | 0.35706 | 122.6074 | 0.20142 | 0.2655 | 122.8271 | 122.8134 | 122.7768 | 122.7631 | -122.7951 | -122.7951 | 122.5571 | 0.21515 | 2.6871 | 1.2131
3000.1719 | 122.9919 | -54.9911 | 67.8131 | -0.12161 | -0.00023294 | 0.062239 | 0.069045 | 0.001442 | 0.0041143 | 0.0071308 | 0.0078126 | -0.00060665 | 0.0032044 | 0.0028368 | -0.0019333 | -0.0055799 | -0.0029651 | -52.3041 | 67.8131 | -55.0369 | 67.6575 | -54.3869 | -54.744 | -54.1351 | -53.801 | 67.8268 | -55.0095 | -54.7531 | -54.8538 | -55.0003 | -54.7394 | -0.045776 | 0 | -0.15564 | 0.60425 | 0.85602 | 0.24719 | 0.90179 | 0.29297 | -0.01831 | 0.013733 | -122.5662 | 0.13733 | 0.25177 | -0.009155 | 0.27008 | 0.009155 | 0.65002 | 122.6944 | 0.15564 | 0.25635 | 122.85 | 122.8363 | 122.8043 | 122.818 | -122.85 | -122.8226 | 122.6486 | 0.23804 | 2.6871 | 1.1902
3001.1719 | 122.9416 | -55.0186 | 67.8452 | -0.11398 | 0.00062166 | 0.062025 | 0.069045 | -0.0032578 | 0.00026909 | 0.005849 | 0.02002 | -0.0014613 | 0.0012818 | 0.00048702 | -0.0032151 | -0.0072889 | -0.0021107 | -52.3178 | 67.7994 | -55.0323 | 67.6346 | -54.4052 | -54.776 | -54.1626 | -53.833 | 67.8635 | -55.0278 | -54.7989 | -54.9179 | -55.069 | -54.7852 | -0.013733 | -0.045777 | -0.21057 | 0.6134 | 0.85602 | 0.24262 | 0.86975 | 0.25635 | -0.009155 | 0.01831 | -122.644 | 0.10071 | 0.23346 | -0.050354 | 0.24262 | -0.041199 | 0.62714 | 122.6669 | 0.10986 | 0.22888 | 122.8317 | 122.8912 | 122.818 | 122.8821 | -122.8775 | -122.8729 | 122.6532 | 0.21973 | 2.7008 | 1.1856
3002.1719 | 123.0057 | -54.9637 | 67.8268 | -0.12161 | 0.00083526 | 0.061171 | 0.070541 | 0.0035782 | 0.0041143 | 0.0052082 | -0.0043946 | 0.00067495 | -0.00021357 | 0.001128 | -0.0032151 | -0.0040845 | -0.00040166 | -52.2949 | 67.8131 | -55.0232 | 67.6666 | -54.3823 | -54.7531 | -54.1489 | -53.8147 | 67.8589 | -55.0049 | -54.776 | -54.8996 | -55.0278 | -54.744 | -0.059509 | -0.013733 | -0.16022 | 0.58136 | 0.81482 | 0.21057 | 0.87433 | 0.27008 | -0.041199 | 0.032044 | -122.6028 | 0.064087 | 0.21973 | -0.064087 | 0.26093 | -0.022888 | 0.64087 | 122.6898 | 0.10529 | 0.22888 | 122.8363 | 122.8638 | 122.7768 | 122.8226 | -122.85 | -122.8317 | 122.6303 | 0.18768 | 2.6688 | 1.149
3003.1719 | 123.0423 | -54.95 | 67.7994 | -0.098725 | -0.00066014 | 0.05818 | 0.071181 | 0.001442 | 0.0036871 | 0.0039264 | 0.14209 | 0.0011023 | 0.0012818 | 0.0034778 | -0.0023605 | -0.0057935 | -0.0029651 | -52.2812 | 67.8085 | -55.0232 | 67.6987 | -54.3274 | -54.7165 | -54.126 | -53.8193 | 67.868 | -55.014 | -54.7119 | -54.8309 | -54.982 | -54.7211 | -0.073242 | 0.009156 | -0.10071 | 0.62256 | 0.82397 | 0.23346 | 0.89722 | 0.3067 | -0.064087 | 0.068665 | -122.5113 | 0.11902 | 0.22888 | -0.032044 | 0.29297 | 0.032043 | 0.6958 | 122.7219 | 0.1831 | 0.30212 | 122.8317 | 122.8821 | 122.7585 | 122.818 | -122.8226 | -122.8134 | 122.6486 | 0.23804 | 2.6688 | 1.1307
3004.1719 | 123.1384 | -54.9042 | 67.8406 | -0.083466 | -0.0021555 | 0.060957 | 0.0699 | -0.0017624 | 0.0024053 | 0.0049946 | 0.02002 | -0.00082025 | -0.00064077 | 0.0034778 | -0.0019333 | -0.0060071 | 2.554e-05 | -52.2995 | 67.7948 | -55.014 | 67.6804 | -54.3411 | -54.7073 | -54.0985 | -53.7277 | 67.8131 | -54.9957 | -54.7165 | -54.8172 | -55.0781 | -54.6158 | -0.10986 | -0.045776 | -0.16022 | 0.56305 | 0.80566 | 0.19684 | 0.91553 | 0.3067 | -0.091553 | -0.027466 | -122.5571 | 0.086975 | 0.28839 | -0.17395 | 0.37994 | -0.082397 | 0.67291 | 122.6944 | 0.17853 | 0.27924 | 122.8088 | 122.8088 | 122.699 | 122.7173 | -122.8546 | -122.8363 | 122.5845 | 0.18768 | 2.6047 | 1.1765
3005.1719 | 123.056 | -54.9591 | 67.8177 | -0.098725 | 0.00062166 | 0.062666 | 0.066695 | 0.00251 | 0.0064643 | 0.0026446 | 0.026123 | 0.0011023 | 2.8e-08 | -0.00058098 | -0.0021469 | -0.0081433 | 0.0023755 | -52.2812 | 67.8131 | -55.0278 | 67.6254 | -54.2953 | -54.7623 | -54.1534 | -53.7689 | 67.8452 | -55.0049 | -54.6982 | -54.8126 | -54.9683 | -54.6844 | -0.068665 | -0.004578 | -0.19226 | 0.66376 | 0.80566 | 0.19684 | 0.87433 | 0.2655 | -0.045777 | 0.027466 | -122.5159 | 0.14648 | 0.27466 | -0.009156 | 0.32043 | 0.036621 | 0.73242 | 122.6532 | 0.19226 | 0.3067 | 122.8409 | 122.85 | 122.7722 | 122.8043 | -122.8455 | -122.8226 | 122.5845 | 0.26093 | 2.6779 | 1.1902
3006.1719 | 123.0515 | -54.9774 | 67.804 | -0.091095 | 0.00062166 | 0.060316 | 0.06755 | 0.0040054 | -0.00037171 | 0.0067036 | 0.026123 | 0.00067495 | 0.00085443 | 0.00048702 | -0.00086511 | -0.0081433 | 2.554e-05 | -52.2858 | 67.7902 | -55.0049 | 67.717 | -54.3045 | -54.689 | -54.0756 | -53.746 | 67.8452 | -54.9545 | -54.657 | -54.8401 | -55.0095 | -54.7211 | -0.027466 | -0.013733 | -0.086975 | 0.67291 | 0.90179 | 0.28839 | 0.92926 | 0.31586 | 0.022888 | 0.041199 | -122.4609 | 0.13733 | 0.25635 | -0.032043 | 0.23346 | -0.054931 | 0.70038 | 122.7219 | 0.11444 | 0.29755 | 122.7951 | 122.7997 | 122.7676 | 122.8226 | -122.8088 | -122.7585 | 122.6944 | 0.32044 | 2.6917 | 1.2314
3007.1719 | 123.0515 | -54.95 | 67.8268 | -0.060578 | -0.00044654 | 0.060957 | 0.068618 | -0.0032578 | 0.0011237 | 0.0011494 | 0.0047608 | -0.0010339 | 0.0019226 | 0.0019824 | -0.0032151 | -0.0057935 | -0.0023243 | -52.2903 | 67.8085 | -55.014 | 67.7078 | -54.3457 | -54.7302 | -54.0939 | -53.7552 | 67.8406 | -54.9957 | -54.7211 | -54.8264 | -54.9545 | -54.7028 | -0.064087 | -0.01831 | -0.11902 | 0.60425 | 0.85602 | 0.21973 | 0.9201 | 0.28381 | -0.045777 | 0.013733 | -122.5479 | 0.1236 | 0.24719 | -0.004578 | 0.29297 | 0.041199 | 0.66833 | 122.7219 | 0.16937 | 0.27466 | 122.8226 | 122.8363 | 122.7585 | 122.7905 | -122.8409 | -122.8226 | 122.6578 | 0.22888 | 2.6596 | 1.1948
3008.1719 | 123.0469 | -54.9591 | 67.804 | -0.098725 | -0.00087374 | 0.061385 | 0.068832 | 0.0022964 | 0.00048269 | 0.0032856 | 0.02002 | 0.00067495 | -0.00085457 | -0.0050672 | 0.00020289 | -0.0066479 | 0.00066654 | -52.2949 | 67.7948 | -55.0049 | 67.6758 | -54.3457 | -54.7211 | -54.1168 | -53.7323 | 67.8268 | -55.0003 | -54.6753 | -54.7806 | -54.9316 | -54.689 | -0.045777 | -0.009155 | -0.12817 | 0.6134 | 0.84228 | 0.23804 | 0.88806 | 0.28381 | -0.041199 | 0.022888 | -122.4792 | 0.17853 | 0.27008 | 0.027465 | 0.31128 | 0.068664 | 0.65918 | 122.6807 | 0.21973 | 0.32501 | 122.7997 | 122.8271 | 122.7539 | 122.7859 | -122.8088 | -122.8043 | 122.6349 | 0.28381 | 2.6642 | 1.2268
3009.1719 | 123.0652 | -54.9545 | 67.7948 | -0.12161 | 0.0025443 | 0.060316 | 0.069686 | -0.0038986 | 0.0021917 | 0.0020038 | 0.026123 | 3.4148e-05 | 0.00042723 | -0.001222 | -0.0057785 | -0.0070753 | 0.0030163 | -52.2583 | 67.804 | -55.0095 | 67.717 | -54.2953 | -54.6936 | -54.071 | -53.7048 | 67.8635 | -54.9866 | -54.7211 | -55.101 | -54.9591 | -54.6433 | -0.054931 | 0.009155 | -0.07782 | 0.65918 | 0.88348 | 0.26093 | 0.93841 | 0.31586 | -0.032043 | 0.068664 | -122.5159 | -0.14648 | 0.31128 | -0.004577 | 0.34332 | 0.027466 | 0.71411 | 122.7264 | -0.11444 | 0.2655 | 122.8134 | 122.85 | 122.7585 | 122.818 | -122.8043 | -122.7814 | 122.6715 | 0.23346 | 2.6962 | 1.2497
3010.1719 | 123.0194 | -54.95 | 67.8223 | -0.098725 | 0.00019446 | 0.061598 | 0.071181 | -0.00069423 | 0.00091009 | 0.0047808 | 0.029175 | 0.0025975 | -0.00064077 | -0.001222 | -0.0019333 | -0.0053663 | -0.0068103 | -52.3087 | 67.8177 | -55.0232 | 67.662 | -54.3961 | -54.7485 | -54.1306 | -53.8055 | 67.8589 | -55.0278 | -54.7028 | -54.8538 | -54.982 | -54.6982 | -0.073242 | -0.004578 | -0.16022 | 0.55389 | 0.8194 | 0.20142 | 0.89264 | 0.27466 | -0.07782 | 0.036621 | -122.525 | 0.09613 | 0.25177 | -0.032044 | 0.32959 | 0.045776 | 0.62714 | 122.6852 | 0.17395 | 0.32501 | 122.8409 | 122.8867 | 122.7676 | 122.8088 | -122.8455 | -122.85 | 122.612 | 0.24719 | 2.6413 | 1.1444
3011.1719 | 123.0469 | -54.9591 | 67.836 | -0.12924 | 0.00040806 | 0.060744 | 0.069686 | -0.0030442 | 0.0021917 | 0.0056354 | 0.0078126 | 0.0013159 | -0.0012818 | 0.0019824 | -0.0025741 | -0.0070753 | -0.00082886 | -52.3315 | 67.8314 | -55.0369 | 67.6392 | -54.4281 | -54.7623 | -54.1443 | -53.8193 | 67.8268 | -55.014 | -54.7211 | -54.8355 | -54.982 | -54.7165 | -0.07782 | -0.004578 | -0.19684 | 0.53101 | 0.81482 | 0.19684 | 0.89264 | 0.27466 | -0.054932 | -0.009156 | -122.5571 | 0.1236 | 0.24261 | -0.022889 | 0.29755 | 0.032043 | 0.60883 | 122.6761 | 0.17853 | 0.29297 | 122.8683 | 122.8409 | 122.7905 | 122.7859 | -122.8729 | -122.85 | 122.5983 | 0.23804 | 2.6276 | 1.1398
3012.1719 | 122.9279 | -54.982 | 67.8497 | -0.075836 | -0.00066014 | 0.063094 | 0.069472 | -0.00048063 | 0.0019781 | 0.0037128 | -0.11426 | 0.0019567 | -0.00064077 | 0.0075366 | -0.0044967 | -0.0045117 | 0.0010937 | -52.3178 | 67.8268 | -55.0369 | 67.63 | -54.4373 | -54.8126 | -54.2267 | -53.8605 | 67.8909 | -55.0095 | -54.7897 | -54.95 | -55.101 | -54.7623 | -0.054931 | -0.022888 | -0.21973 | 0.54474 | 0.75531 | 0.16937 | 0.81024 | 0.2243 | -0.027465 | 0.041199 | -122.6395 | 0.032044 | 0.21973 | -0.11902 | 0.24719 | -0.091553 | 0.59967 | 122.6669 | 0.059509 | 0.21973 | 122.8638 | 122.9004 | 122.8088 | 122.8729 | -122.8867 | -122.8592 | 122.612 | 0.19226 | 2.6642 | 1.1215
3013.1719 | 123.0286 | -54.9454 | 67.8131 | -0.075836 | 0.0014761 | 0.059889 | 0.067977 | 0.0018692 | 0.0019781 | 0.0039264 | 0.03833 | -0.0018885 | 0.0012818 | -0.0072034 | -0.0025741 | -0.0049389 | -0.0012561 | -52.3178 | 67.8223 | -55.0003 | 67.6666 | -54.3961 | -54.7531 | -54.126 | -53.7872 | 67.8635 | -54.9866 | -54.7165 | -54.8218 | -54.982 | -54.6753 | -0.054931 | 0.009156 | -0.14648 | 0.54932 | 0.8194 | 0.19226 | 0.87433 | 0.24719 | -0.041198 | 0.050354 | -122.5296 | 0.1236 | 0.27008 | -0.036621 | 0.31128 | 0.004577 | 0.60425 | 122.6669 | 0.1648 | 0.27008 | 122.8226 | 122.85 | 122.7676 | 122.8088 | -122.8134 | -122.7997 | 122.612 | 0.22888 | 2.6276 | 1.1581
3014.1719 | 122.9965 | -54.9545 | 67.836 | -0.1445 | 0.0014761 | 0.062666 | 0.067123 | -0.0041122 | 0.0024053 | 0.0060626 | 0.010864 | 0.0019567 | -0.00021357 | -0.00229 | -0.0021469 | -0.0064343 | -0.0010425 | -52.3087 | 67.8223 | -55.014 | 67.6483 | -54.3869 | -54.7668 | -54.1397 | -53.801 | 67.8726 | -54.9911 | -54.7165 | -54.8172 | -54.982 | -54.7028 | -0.059509 | -0.013733 | -0.18768 | 0.56763 | 0.81482 | 0.18768 | 0.87433 | 0.24719 | -0.036621 | 0.036621 | -122.5525 | 0.13733 | 0.25177 | -0.027466 | 0.28839 | 0.009155 | 0.62714 | 122.6624 | 0.17395 | 0.27466 | 122.8363 | 122.8638 | 122.7768 | 122.8271 | -122.85 | -122.8271 | 122.6028 | 0.23804 | 2.6459 | 1.1536
3015.1719 | 123.0286 | -54.9271 | 67.8589 | -0.098725 | 0.0012625 | 0.060103 | 0.069045 | -0.0013352 | 0.0045417 | 0.0032856 | -0.010498 | -0.0018885 | -0.00021357 | -0.0010084 | -0.0025741 | -0.0057935 | 0.0010937 | -52.3087 | 67.836 | -55.0049 | 67.7307 | -54.3594 | -54.8447 | -54.1489 | -53.8055 | 67.8726 | -54.9957 | -54.7119 | -54.8309 | -54.9911 | -54.7119 | -0.07782 | -0.022888 | -0.12817 | 0.56763 | 0.7782 | 0.082397 | 0.85602 | 0.16022 | -0.068665 | 0.013733 | -122.5708 | 0.09613 | 0.21515 | -0.064087 | 0.28381 | 0.004578 | 0.64545 | 122.7356 | 0.16479 | 0.28381 | 122.8409 | 122.8683 | 122.7631 | 122.7997 | -122.8638 | -122.8546 | 122.6578 | 0.21515 | 2.6184 | 1.1215
3016.1719 | 123.0286 | -54.9316 | 67.8452 | -0.10635 | -0.00044654 | 0.061598 | 0.068618 | -0.00048063 | -0.00015811 | 0.0060626 | 0.035278 | -0.00017945 | 0.0019226 | 0.00091422 | -0.0034287 | -0.0066479 | 0.0015209 | -52.3041 | 67.8406 | -55.0003 | 67.6758 | -54.3869 | -54.7531 | -54.1168 | -53.7827 | 67.8909 | -54.95 | -54.6982 | -54.808 | -54.9591 | -54.6707 | -0.068664 | -0.004578 | -0.16937 | 0.54474 | 0.81482 | 0.17853 | 0.88348 | 0.24719 | -0.01831 | 0.045776 | -122.5433 | 0.1236 | 0.26093 | -0.027465 | 0.27924 | -0.009155 | 0.6134 | 122.6761 | 0.14191 | 0.25177 | 122.8409 | 122.8409 | 122.7722 | 122.8226 | -122.8455 | -122.7951 | 122.6074 | 0.23346 | 2.6276 | 1.149
3017.1719 | 123.0194 | -54.95 | 67.8589 | -0.12161 | -0.00044654 | 0.061598 | 0.069045 | -0.0017624 | 0.0015509 | 0.0026446 | -0.010498 | 0.00046135 | 0.00042723 | 0.00027342 | -0.0021469 | -0.0042981 | -0.0010425 | -52.3041 | 67.8314 | -55.0049 | 67.662 | -54.3777 | -54.7623 | -54.1351 | -53.8055 | 67.868 | -54.9637 | -54.7119 | -54.8447 | -55.0232 | -54.6982 | -0.054932 | -0.027466 | -0.19684 | 0.5722 | 0.81482 | 0.18768 | 0.86975 | 0.24262 | -0.013733 | 0.009155 | -122.5708 | 0.10529 | 0.25177 | -0.073242 | 0.2655 | -0.059509 | 0.62714 | 122.6669 | 0.11902 | 0.25177 | 122.8363 | 122.8317 | 122.7814 | 122.818 | -122.8638 | -122.8226 | 122.612 | 0.23804 | 2.6459 | 1.1444
3018.1719 | 123.0011 | -54.9225 | 67.8452 | -0.083466 | -0.0010873 | 0.061598 | 0.070968 | -0.00069423 | 0.00069649 | 0.0067036 | -0.03186 | 0.0015295 | 0.00064083 | 0.0034778 | -0.0021469 | -0.0055799 | -0.0027515 | -52.2812 | 67.7994 | -54.9911 | 67.6712 | -54.364 | -54.776 | -54.126 | -53.7964 | 67.8452 | -54.982 | -54.7119 | -54.8401 | -55.0049 | -54.7073 | -0.068665 | -0.045777 | -0.17395 | 0.55847 | 0.79651 | 0.14648 | 0.86517 | 0.21515 | -0.05951 | 0 | -122.5571 | 0.082397 | 0.21515 | -0.082398 | 0.27466 | -0.022888 | 0.62714 | 122.6624 | 0.14191 | 0.27008 | 122.7905 | 122.8271 | 122.7219 | 122.7676 | -122.8363 | -122.8271 | 122.5937 | 0.21057 | 2.6413 | 1.1261
3019.1719 | 123.0377 | -54.9225 | 67.8589 | -0.045319 | -0.0010873 | 0.060744 | 0.0699 | -0.00069423 | 0.0017645 | 0.0071308 | -0.0074462 | 0.00024775 | -0.0010682 | -0.0010084 | -0.0032151 | -0.0053663 | -0.0023243 | -52.2949 | 67.8268 | -54.9957 | 67.662 | -54.3823 | -54.7531 | -54.1168 | -53.801 | 67.8955 | -54.9637 | -54.689 | -54.8309 | -55.014 | -54.7302 | -0.073243 | -0.032044 | -0.19684 | 0.54016 | 0.80566 | 0.16937 | 0.87891 | 0.24262 | -0.041199 | 0.036621 | -122.5479 | 0.091552 | 0.19226 | -0.091553 | 0.23346 | -0.050354 | 0.6134 | 122.6578 | 0.13275 | 0.27466 | 122.8226 | 122.8592 | 122.7493 | 122.818 | -122.8546 | -122.8226 | 122.5845 | 0.23346 | 2.6276 | 1.1215
3020.1719 | 122.9874 | -54.9362 | 67.8406 | -0.083466 | -0.0010873 | 0.062666 | 0.069259 | 0.0010148 | 0.0028327 | 0.005849 | -0.0013428 | 0.0013159 | 0.0021362 | -0.0016492 | -0.0030013 | -0.0036573 | 2.554e-05 | -52.2949 | 67.8314 | -54.9866 | 67.6758 | -54.3823 | -54.7531 | -54.126 | -53.7872 | 67.8726 | -54.9774 | -54.7028 | -54.8492 | -54.9774 | -54.6936 | -0.050354 | -0.009155 | -0.16479 | 0.55389 | 0.81024 | 0.1831 | 0.8606 | 0.23346 | -0.041199 | 0.032044 | -122.5433 | 0.086975 | 0.24261 | -0.041199 | 0.28381 | 0 | 0.60425 | 122.6624 | 0.12817 | 0.27466 | 122.818 | 122.85 | 122.7676 | 122.8088 | -122.8271 | -122.818 | 122.612 | 0.23346 | 2.6413 | 1.149
3021.1719 | 122.9965 | -54.9408 | 67.868 | -0.083466 | 0.00040806 | 0.059676 | 0.069045 | 0.001442 | 0.0021917 | 0.0067036 | -0.016602 | 0.0015295 | -0.0010682 | -0.0035718 | -0.0012925 | -0.0055799 | 0.0030163 | -52.2675 | 67.7994 | -54.9637 | 67.6758 | -54.3457 | -54.7577 | -54.1122 | -53.7689 | 67.8635 | -54.9545 | -54.6753 | -54.8401 | -54.9911 | -54.7028 | -0.022888 | -0.068665 | -0.19226 | 0.59509 | 0.82855 | 0.18311 | 0.85144 | 0.20599 | -0.013733 | -0.004578 | -122.5433 | 0.10071 | 0.23804 | -0.050354 | 0.25177 | -0.036621 | 0.61798 | 122.6395 | 0.11444 | 0.27924 | 122.7631 | 122.818 | 122.7402 | 122.8043 | -122.8317 | -122.8226 | 122.6166 | 0.2655 | 2.6733 | 1.1719
3022.1719 | 122.9736 | -54.9362 | 67.836 | -0.11398 | 0.00019446 | 0.062239 | 0.071181 | -0.0013352 | 0.0026191 | 0.007558 | -0.037964 | 0.0025975 | 0.00085443 | -0.0020764 | -0.0023605 | -0.0062207 | 0.00023934 | -52.24 | 67.8268 | -54.9774 | 67.7032 | -54.3182 | -54.7302 | -54.1077 | -53.7415 | 67.9092 | -54.9408 | -54.6753 | -54.8264 | -54.9683 | -54.689 | -0.041199 | -0.009156 | -0.13275 | 0.61798 | 0.82855 | 0.20599 | 0.86975 | 0.24719 | -0.004578 | 0.073242 | -122.5113 | 0.10986 | 0.24719 | -0.032044 | 0.25177 | -0.027466 | 0.65918 | 122.6807 | 0.11444 | 0.2655 | 122.8043 | 122.85 | 122.7631 | 122.8455 | -122.8134 | -122.7768 | 122.6395 | 0.26092 | 2.6962 | 1.1948
3023.1719 | 122.9919 | -54.9408 | 67.8635 | -0.1445 | 0.0044669 | 0.061385 | 0.068404 | 0.0016556 | 0.00048269 | 0.0043536 | -0.010498 | 0.00088875 | -0.0025636 | 0.0017688 | -0.0017197 | -0.0051527 | -0.00040166 | -52.2675 | 67.8589 | -54.982 | 67.6849 | -54.3503 | -54.7531 | -54.1077 | -53.7781 | 67.8864 | -54.9545 | -54.6844 | -54.8172 | -54.9866 | -54.6753 | -0.041199 | -0.004577 | -0.17853 | 0.59051 | 0.83313 | 0.18768 | 0.87433 | 0.22888 | -0.013733 | 0.022889 | -122.5479 | 0.1236 | 0.2655 | -0.045776 | 0.27924 | -0.032043 | 0.63171 | 122.6669 | 0.13733 | 0.27008 | 122.8409 | 122.8409 | 122.7997 | 122.8271 | -122.8455 | -122.818 | 122.6257 | 0.25635 | 2.6733 | 1.1627
3024.1719 | 123.0331 | -54.9179 | 67.8635 | 0.00045798 | 0.0025443 | 0.06053 | 0.069045 | 0.00251 | 0.0021917 | 0.0077716 | -0.06543 | 0.00067495 | 0.001709 | -0.0025036 | -0.0027877 | -0.0055799 | 2.554e-05 | -52.2308 | 67.836 | -54.95 | 67.717 | -54.3182 | -54.7348 | -54.0802 | -53.6957 | 67.9047 | -54.9408 | -54.6295 | -54.8172 | -54.9545 | -54.6478 | -0.032043 | -0.027465 | -0.14648 | 0.59967 | 0.83771 | 0.18311 | 0.86975 | 0.21515 | -0.022888 | 0.041199 | -122.493 | 0.10071 | 0.27008 | -0.036621 | 0.29297 | -0.013733 | 0.63171 | 122.6669 | 0.1236 | 0.31128 | 122.7859 | 122.8455 | 122.7539 | 122.8226 | -122.8134 | -122.8043 | 122.6349 | 0.28839 | 2.6871 | 1.2222
3025.1719 | 123.0331 | -54.9225 | 67.8452 | -0.098725 | 0.0033987 | 0.061385 | 0.072036 | 0.0029374 | 0.0039007 | 0.01119 | -0.071533 | -0.00039305 | 2.8e-08 | -0.0018628 | -0.0034287 | -0.0040845 | -0.0016833 | -52.2171 | 67.8223 | -54.9454 | 67.5613 | -54.4281 | -54.5517 | -53.9703 | -53.6728 | 67.8772 | -54.9362 | -54.6341 | -54.7806 | -54.9408 | -54.6387 | -0.022889 | -0.022888 | -0.28381 | 0.49438 | 0.95215 | 0.37079 | 0.97504 | 0.39368 | -0.013733 | 0.032043 | -122.4792 | 0.14191 | 0.28381 | -0.018311 | 0.29755 | -0.004578 | 0.51727 | 122.5067 | 0.15564 | 0.30212 | 122.7676 | 122.8134 | 122.7448 | 122.7997 | -122.7905 | -122.7814 | 122.4838 | 0.28839 | 2.7054 | 1.2497
3026.1719 | 123.0148 | -54.8996 | 67.8452 | -0.11398 | 0.0012625 | 0.060957 | 0.068404 | -0.00048063 | 0.0011237 | 0.0067036 | -0.01355 | 0.0021703 | -0.00064077 | 0.003905 | -0.0023605 | -0.0040845 | 0.00088014 | -52.2125 | 67.8406 | -54.9637 | 67.7261 | -54.2999 | -54.6982 | -54.071 | -53.7094 | 67.8955 | -54.9316 | -54.6249 | -54.7989 | -54.9408 | -54.6387 | -0.064087 | -0.004578 | -0.11902 | 0.59967 | 0.82855 | 0.20142 | 0.89264 | 0.2655 | -0.032044 | 0.050354 | -122.4701 | 0.10071 | 0.26093 | -0.041199 | 0.29297 | -0.009155 | 0.66376 | 122.6898 | 0.13275 | 0.3067 | 122.8043 | 122.8271 | 122.7402 | 122.7951 | -122.8088 | -122.7768 | 122.6257 | 0.27466 | 2.6871 | 1.1902
3027.1719 | 123.0331 | -54.9088 | 67.8452 | -0.0071715 | -0.0010873 | 0.061812 | 0.069686 | 0.00037377 | 0.00026909 | 0.005849 | -0.053223 | -0.00017945 | -0.00064077 | 0.0034778 | -0.0023605 | -0.0040845 | -0.00061526 | -52.2354 | 67.8635 | -54.95 | 67.7307 | -54.3045 | -54.7073 | -54.0756 | -53.7048 | 67.8772 | -54.9179 | -54.6295 | -54.8035 | -54.9179 | -54.6433 | -0.041199 | 0.01831 | -0.11444 | 0.60425 | 0.83313 | 0.20142 | 0.87433 | 0.24262 | -0.009156 | 0.032043 | -122.4747 | 0.10529 | 0.2655 | -0.009156 | 0.27466 | 0 | 0.64545 | 122.6807 | 0.11444 | 0.28839 | 122.8134 | 122.7951 | 122.7722 | 122.7859 | -122.7951 | -122.7631 | 122.6395 | 0.27923 | 2.6733 | 1.2039
3028.1719 | 123.0194 | -54.8996 | 67.8726 | -0.068207 | 0.00083526 | 0.062239 | 0.068191 | 0.00486 | 0.0034735 | 0.0032856 | -0.01355 | 0.00067495 | 0.0023498 | 0.0028368 | -0.00043791 | -0.0049389 | 2.554e-05 | -52.2217 | 67.8406 | -54.9408 | 67.717 | -54.2999 | -54.6936 | -54.0573 | -53.714 | 67.8818 | -54.9454 | -54.6433 | -54.8035 | -54.95 | -54.657 | -0.041199 | -0.032044 | -0.15564 | 0.59967 | 0.84228 | 0.20599 | 0.88348 | 0.24719 | -0.045777 | 0.009155 | -122.5159 | 0.09613 | 0.24262 | -0.050354 | 0.28839 | -0.004577 | 0.64087 | 122.6578 | 0.14191 | 0.30212 | 122.7814 | 122.8271 | 122.7402 | 122.7814 | -122.8134 | -122.818 | 122.6166 | 0.25635 | 2.6779 | 1.1856
3029.1719 | 123.0331 | -54.8676 | 67.8818 | -0.10635 | 0.0019035 | 0.06288 | 0.070968 | 0.00037377 | 0.0019781 | 0.0067036 | -0.06543 | 0.0028113 | -0.0019226 | -0.0044262 | -0.0047103 | -0.0055799 | 0.00023934 | -52.2034 | 67.8497 | -54.9591 | 67.749 | -54.2908 | -54.6982 | -54.071 | -53.7369 | 67.868 | -54.9454 | -54.5929 | -54.7806 | -54.9271 | -54.6112 | -0.091552 | -0.032044 | -0.13275 | 0.57678 | 0.79651 | 0.16937 | 0.88806 | 0.26093 | -0.07782 | -0.013733 | -122.4747 | 0.086975 | 0.25635 | -0.059509 | 0.33417 | 0.018311 | 0.66833 | 122.7081 | 0.16479 | 0.35248 | 122.8088 | 122.8134 | 122.7173 | 122.7356 | -122.8409 | -122.8271 | 122.6166 | 0.27466 | 2.6642 | 1.1307
3030.1719 | 123.0148 | -54.8859 | 67.868 | -0.1445 | 0.0029715 | 0.060744 | 0.068832 | 0.00058737 | 0.0011237 | 0.005849 | -0.01355 | -0.00060665 | 0.00021363 | 0.0024096 | -0.0023605 | -0.0051527 | 2.554e-05 | -52.1896 | 67.8864 | -54.9454 | 67.7353 | -54.2633 | -54.7028 | -54.0619 | -53.7003 | 67.9092 | -54.9179 | -54.6158 | -54.7714 | -54.9088 | -54.6066 | -0.05951 | 0.018311 | -0.13275 | 0.62256 | 0.82397 | 0.1831 | 0.88348 | 0.24262 | -0.032044 | 0.041199 | -122.4838 | 0.11444 | 0.27924 | -0.022888 | 0.31128 | 0.009156 | 0.68207 | 122.6807 | 0.14648 | 0.30212 | 122.8317 | 122.8271 | 122.7722 | 122.7951 | -122.8134 | -122.7859 | 122.6212 | 0.27008 | 2.6962 | 1.1856
3031.1719 | 123.0423 | -54.8859 | 67.8772 | -0.15213 | 0.00040806 | 0.061385 | 0.072463 | 0.00058737 | 0.0024053 | 0.0077716 | -0.08374 | 0.00088875 | -0.0014954 | 0.0019824 | -0.0034287 | -0.0042981 | 0.0023755 | -52.1942 | 67.8772 | -54.9545 | 67.7261 | -54.3137 | -54.6844 | -54.0756 | -53.6911 | 67.9092 | -54.9088 | -54.6021 | -54.776 | -54.9179 | -54.6066 | -0.068665 | 0 | -0.15106 | 0.5722 | 0.81024 | 0.20142 | 0.87891 | 0.27008 | -0.022888 | 0.032044 | -122.4792 | 0.10986 | 0.27924 | -0.032044 | 0.30212 | -0.009156 | 0.64087 | 122.6807 | 0.13275 | 0.3067 | 122.8317 | 122.818 | 122.7631 | 122.7951 | -122.8317 | -122.7859 | 122.612 | 0.28381 | 2.6916 | 1.1948
3032.1719 | 123.0606 | -54.8676 | 67.8452 | -0.068207 | 0.0014761 | 0.063094 | 0.069259 | -0.0034714 | 0.0028327 | 0.0069172 | -0.068481 | 0.00067495 | -0.00085457 | 5.9824e-05 | -0.0025741 | -0.0030163 | -0.00018806 | -52.2034 | 67.8864 | -54.9683 | 67.7261 | -54.3228 | -54.7028 | -54.0756 | -53.7048 | 67.9047 | -54.9362 | -54.5975 | -54.7806 | -54.9042 | -54.5837 | -0.10071 | 0.041199 | -0.11902 | 0.54474 | 0.79193 | 0.16479 | 0.89264 | 0.2655 | -0.068664 | 0.059509 | -122.4426 | 0.086975 | 0.28381 | -0.036621 | 0.35248 | 0.032043 | 0.64545 | 122.6944 | 0.15564 | 0.33874 | 122.8546 | 122.8409 | 122.7539 | 122.7722 | -122.8134 | -122.7814 | 122.5937 | 0.27008 | 2.6642 | 1.1627
3033.1719 | 123.056 | -54.8676 | 67.8909 | -0.12924 | -0.00044654 | 0.062453 | 0.069045 | -0.0021896 | 0.0011237 | 0.0081988 | -0.022705 | 0.0013159 | 0.00085443 | 0.0068958 | -0.0032151 | -0.0021619 | 0.00023934 | -52.1713 | 67.868 | -54.9454 | 67.6025 | -54.2175 | -54.4647 | -53.952 | -53.6407 | 67.9092 | -54.895 | -54.5883 | -54.7577 | -54.8996 | -54.5883 | -0.07782 | -0.022888 | -0.28839 | 0.65002 | 0.91553 | 0.40283 | 0.99335 | 0.48065 | -0.027466 | 0.018311 | -122.4792 | 0.10986 | 0.27924 | -0.032043 | 0.3067 | -0.004577 | 0.72785 | 122.5479 | 0.13733 | 0.3067 | 122.8134 | 122.8043 | 122.7356 | 122.7768 | -122.8363 | -122.7859 | 122.4701 | 0.27924 | 2.6962 | 1.2268
3034.1719 | 123.0331 | -54.8859 | 67.8772 | -0.15213 | -1.9142e-05 | 0.061812 | 0.068832 | 0.003151 | 0.0028327 | 0.0052082 | -0.14783 | 0.0025975 | 0.00042723 | -0.0052808 | -0.0032151 | -0.0060071 | -0.00018806 | -52.1759 | 67.8772 | -54.9454 | 67.7673 | -54.2587 | -54.6616 | -54.0573 | -53.6636 | 67.8726 | -54.9316 | -54.57 | -54.744 | -54.9088 | -54.5837 | -0.05951 | 0 | -0.10986 | 0.62714 | 0.82855 | 0.2243 | 0.88806 | 0.28381 | -0.045777 | -0.004577 | -122.4472 | 0.14191 | 0.30212 | -0.022888 | 0.3479 | 0.022889 | 0.68665 | 122.7127 | 0.18768 | 0.36163 | 122.8226 | 122.8043 | 122.7631 | 122.7585 | -122.8226 | -122.8088 | 122.6532 | 0.31586 | 2.71 | 1.2222
3035.1719 | 123.0698 | -54.8538 | 67.868 | -0.098725 | 0.00040806 | 0.06288 | 0.071822 | 0.0020828 | 0.0019781 | 0.0064898 | -0.050171 | 0.00088875 | 2.8e-08 | 0.0024096 | -0.00065151 | -0.0034437 | -0.0016833 | -52.1576 | 67.9001 | -54.9271 | 67.7673 | -54.277 | -54.6799 | -54.0436 | -53.6682 | 67.9001 | -54.9225 | -54.5746 | -54.6158 | -54.9225 | -54.6021 | -0.073242 | 0.032043 | -0.10071 | 0.57678 | 0.81024 | 0.17395 | 0.88348 | 0.24719 | -0.068664 | 0.032043 | -122.4426 | 0.23804 | 0.25177 | -0.068664 | 0.32043 | 0 | 0.65002 | 122.6944 | 0.3067 | 0.3479 | 122.8271 | 122.8226 | 122.7539 | 122.7539 | -122.7951 | -122.7905 | 122.6212 | 0.27924 | 2.6962 | 1.1856
3036.1719 | 123.056 | -54.8859 | 67.8955 | -0.11398 | 0.00019446 | 0.062025 | 0.067123 | 0.00058737 | 0.0036871 | 0.0062762 | -0.03186 | 0.00024775 | -0.00021357 | 0.00027342 | -0.0038559 | -0.0032301 | -0.0025379 | -52.1439 | 67.8818 | -54.9362 | 67.7536 | -54.2587 | -54.6799 | -54.0527 | -53.6774 | 67.923 | -54.8996 | -54.5746 | -54.7073 | -55.1239 | -54.7348 | -0.050354 | -0.013733 | -0.14191 | 0.62714 | 0.83313 | 0.20599 | 0.88348 | 0.25635 | -0.013733 | 0.027466 | -122.4701 | 0.17853 | 0.15106 | -0.23804 | 0.16479 | -0.2243 | 0.67749 | 122.6898 | 0.19226 | 0.32501 | 122.818 | 122.8226 | 122.7676 | 122.8088 | -122.8317 | -122.7951 | 122.6395 | 0.31128 | 2.742 | 1.2085
3037.1719 | 123.024 | -54.8721 | 67.9047 | -0.083466 | 0.0033987 | 0.060316 | 0.069045 | 0.00037377 | 0.0024053 | 0.0052082 | -0.028809 | 0.0013159 | -0.00021357 | -0.0069898 | -0.0021469 | -0.0049389 | 0.0025891 | -52.1439 | 67.8864 | -54.8904 | 67.7673 | -54.245 | -54.6616 | -54.0482 | -53.6499 | 67.9276 | -54.8721 | -54.5792 | -54.7394 | -54.8813 | -54.5746 | -0.018311 | -0.01831 | -0.13733 | 0.62714 | 0.82397 | 0.21057 | 0.84228 | 0.22888 | 0 | 0.022888 | -122.4838 | 0.13275 | 0.29755 | -0.009156 | 0.29755 | -0.009156 | 0.64545 | 122.6578 | 0.13275 | 0.29297 | 122.7768 | 122.7997 | 122.7585 | 122.7997 | -122.7951 | -122.7768 | 122.6395 | 0.29297 | 2.7283 | 1.2222
3038.1719 | 123.0331 | -54.8859 | 67.9001 | -0.11398 | 0.0016899 | 0.06053 | 0.072036 | -0.00048063 | 0.0028327 | 0.0049946 | -0.034912 | 0.0011023 | 0.00064083 | 0.0024096 | -0.0027877 | -0.0028027 | 0.00023934 | -52.1759 | 67.9276 | -54.9042 | 67.7536 | -54.2816 | -54.6616 | -54.0573 | -53.6545 | 67.9138 | -54.9179 | -54.5837 | -54.7577 | -54.8904 | -54.5746 | -0.018311 | 0.027466 | -0.14648 | 0.60425 | 0.82855 | 0.2243 | 0.84686 | 0.24262 | -0.032044 | 0.013733 | -122.4838 | 0.12817 | 0.31128 | -0.004578 | 0.34332 | 0.027466 | 0.62256 | 122.6578 | 0.16022 | 0.33417 | 122.8317 | 122.8317 | 122.8134 | 122.7997 | -122.8043 | -122.818 | 122.6395 | 0.30212 | 2.71 | 1.2314
3039.1719 | 123.0057 | -54.8401 | 67.9276 | -0.13687 | 0.00040806 | 0.063094 | 0.069686 | -0.0026168 | 0.0015509 | 0.005849 | 0.0047608 | -0.00082025 | 0.00042723 | 0.0017688 | -0.00022431 | -0.0036573 | -0.00061526 | -52.1393 | 67.8955 | -54.9088 | 67.7994 | -54.2633 | -54.6295 | -53.9886 | -53.6407 | 67.923 | -54.895 | -54.57 | -54.7256 | -54.8859 | -54.5609 | -0.068664 | -0.032043 | -0.12817 | 0.57678 | 0.85144 | 0.21057 | 0.9201 | 0.27923 | -0.054932 | -0.004577 | -122.4976 | 0.11444 | 0.27924 | -0.045776 | 0.33417 | 0.009156 | 0.64545 | 122.7081 | 0.16937 | 0.32501 | 122.8043 | 122.818 | 122.7356 | 122.7631 | -122.8363 | -122.8226 | 122.6395 | 0.27008 | 2.7008 | 1.1993
3040.1719 | 123.0377 | -54.8309 | 67.9001 | -0.12924 | -0.00023294 | 0.063521 | 0.070327 | 0.001442 | 0.0030463 | 0.0060626 | -0.050171 | 0.0011023 | -0.00085457 | -0.0018628 | -0.0017197 | -0.0034437 | -0.00082886 | -52.1301 | 67.9092 | -54.8904 | 67.7124 | -54.4373 | -54.5242 | -53.9108 | -53.627 | 67.9459 | -54.8721 | -54.5609 | -54.7348 | -54.8676 | -54.5609 | -0.059509 | 0.009156 | -0.18768 | 0.39368 | 0.9201 | 0.3067 | 0.97961 | 0.36621 | -0.041198 | 0.045777 | -122.4609 | 0.096131 | 0.27008 | -0.036621 | 0.31128 | 0.004577 | 0.45319 | 122.6028 | 0.13733 | 0.31128 | 122.7997 | 122.818 | 122.7402 | 122.7768 | -122.7905 | -122.7722 | 122.5433 | 0.27008 | 2.7008 | 1.2039
3041.1719 | 122.9874 | -54.8492 | 67.9184 | -0.11398 | -0.00066014 | 0.061385 | 0.070541 | 0.0010148 | 0.0030463 | 0.0079852 | -0.044067 | 0.0034521 | 0.001068 | -0.0018628 | 0.00020289 | -0.0047253 | -0.0033923 | -52.1072 | 67.9001 | -54.9133 | 67.7902 | -54.2313 | -54.6433 | -54.039 | -53.6911 | 67.9092 | -54.9088 | -54.538 | -54.7302 | -54.863 | -54.5609 | -0.064087 | -0.018311 | -0.12817 | 0.61798 | 0.81024 | 0.20599 | 0.87433 | 0.27008 | -0.059509 | -0.009155 | -122.4564 | 0.11902 | 0.28839 | -0.013733 | 0.3479 | 0.045776 | 0.68207 | 122.7036 | 0.17853 | 0.37079 | 122.8134 | 122.818 | 122.7493 | 122.7585 | -122.8317 | -122.8271 | 122.6395 | 0.31128 | 2.742 | 1.1581
3042.1719 | 123.0515 | -54.8172 | 67.9047 | -0.16739 | -1.9142e-05 | 0.060316 | 0.069259 | 0.0040054 | 0.0039007 | 0.0043536 | -0.028809 | 0.0011023 | -0.00021357 | -0.0086988 | -0.0030013 | -0.00045288 | -0.00082886 | -52.1255 | 67.923 | -54.895 | 67.7811 | -54.2313 | -54.6524 | -54.0344 | -53.6499 | 67.9367 | -54.9042 | -54.6661 | -54.6524 | -54.7028 | -54.4647 | -0.07782 | 0.018311 | -0.1236 | 0.58594 | 0.78278 | 0.16479 | 0.8606 | 0.24262 | -0.086975 | 0.032044 | -122.5708 | 0.16479 | 0.35248 | 0.11444 | 0.43945 | 0.20142 | 0.66376 | 122.6761 | 0.25177 | 0.23804 | 122.818 | 122.8409 | 122.7402 | 122.7539 | -122.7997 | -122.8088 | 122.5983 | 0.15106 | 2.6917 | 1.1673
3043.1719 | 123.0057 | -54.8309 | 67.9184 | -0.11398 | -0.00044654 | 0.06288 | 0.0699 | 0.0012284 | 0.0034735 | 0.0032856 | -0.037964 | 0.00088875 | -0.00042717 | 0.0028368 | -0.0034287 | -0.0030163 | 0.0025891 | -52.1118 | 67.9184 | -54.9225 | 67.7811 | -54.2358 | -54.6249 | -54.0482 | -53.6499 | 67.9642 | -54.8676 | -54.5471 | -54.7211 | -54.8813 | -54.5654 | -0.091552 | 0 | -0.13733 | 0.59509 | 0.78278 | 0.20599 | 0.87433 | 0.29755 | -0.036621 | 0.045776 | -122.4655 | 0.10986 | 0.2655 | -0.050354 | 0.30212 | -0.013733 | 0.68664 | 122.7036 | 0.14648 | 0.32043 | 122.8409 | 122.8317 | 122.7493 | 122.7951 | -122.8409 | -122.7859 | 122.612 | 0.28381 | 2.7191 | 1.181
3044.1719 | 122.9462 | -54.8492 | 68.0237 | 0.00045798 | -0.0013009 | 0.060744 | 0.068832 | 0.00058737 | 0.0013373 | 0.0069172 | -0.022705 | 0.0025975 | 0.00085443 | -0.0033582 | -0.0027877 | -0.0042981 | -0.00018806 | -52.1347 | 68.0008 | -54.8676 | 67.7353 | -54.2862 | -54.6524 | -54.0802 | -53.508 | 68.0786 | -54.8309 | -54.6341 | -54.7897 | -54.9133 | -54.6387 | -0.018311 | -0.022889 | -0.28839 | 0.56305 | 0.76904 | 0.19684 | 0.78735 | 0.21515 | 0.01831 | 0.054931 | -122.6578 | 0.059509 | 0.21057 | -0.064087 | 0.19226 | -0.082397 | 0.58136 | 122.6028 | 0.041199 | 0.19684 | 122.8683 | 122.9095 | 122.85 | 122.9279 | -122.8912 | -122.8546 | 122.5845 | 0.21515 | 2.7145 | 1.3412
3045.1719 | 123.0011 | -54.8126 | 67.9596 | -0.1445 | -0.00023294 | 0.06053 | 0.070754 | -0.0021896 | 0.0019781 | 0.0034992 | -0.019653 | 0.0013159 | 0.0019226 | 0.0026232 | -0.0040695 | -0.0028027 | -0.0018971 | -52.153 | 67.923 | -54.9271 | 67.7582 | -54.277 | -54.689 | -54.0802 | -53.6819 | 67.9733 | -54.8813 | -54.5654 | -54.7211 | -54.8813 | -54.5471 | -0.11444 | -0.036621 | -0.20142 | 0.53558 | 0.73242 | 0.1236 | 0.84686 | 0.23804 | -0.068665 | 0.013733 | -122.525 | 0.091553 | 0.2655 | -0.068665 | 0.33417 | 0 | 0.65002 | 122.6852 | 0.16022 | 0.31586 | 122.85 | 122.8546 | 122.7356 | 122.7859 | -122.8867 | -122.8409 | 122.5708 | 0.24719 | 2.6596 | 1.1307
3046.1719 | 123.0057 | -54.8218 | 67.9321 | -0.12161 | 0.00083526 | 0.059676 | 0.0699 | 0.0035782 | 0.0045417 | 0.0060626 | -0.041016 | 0.00067495 | 0.0014954 | -0.0061352 | -0.0015061 | -0.0025891 | -0.0010425 | -52.1713 | 67.9504 | -54.9179 | 67.7261 | -54.2862 | -54.6936 | -54.1077 | -53.6865 | 68.0008 | -54.8676 | -54.5792 | -54.744 | -54.9088 | -54.5929 | -0.096131 | 0.01831 | -0.20599 | 0.53558 | 0.71411 | 0.12817 | 0.81024 | 0.2243 | -0.045777 | 0.068664 | -122.5113 | 0.077819 | 0.22888 | -0.086975 | 0.27466 | -0.041198 | 0.63171 | 122.644 | 0.1236 | 0.28839 | 122.8683 | 122.8683 | 122.7722 | 122.8226 | -122.85 | -122.7997 | 122.5479 | 0.24261 | 2.6505 | 1.1353
3047.1719 | 123.0194 | -54.7989 | 67.9321 | -0.11398 | 0.0014761 | 0.063094 | 0.0699 | 0.00016017 | 0.0039007 | 0.0060626 | -0.010498 | 0.0028113 | 2.8e-08 | 0.0064684 | -0.0012925 | -0.0068615 | 0.0023755 | -52.1118 | 67.9276 | -54.8996 | 67.7856 | -54.2404 | -54.6524 | -54.0207 | -53.6179 | 67.9688 | -54.8767 | -54.538 | -54.7119 | -54.8767 | -54.5609 | -0.10071 | -0.004578 | -0.14648 | 0.55847 | 0.7782 | 0.14648 | 0.87891 | 0.24719 | -0.07782 | 0.036621 | -122.4701 | 0.086975 | 0.23804 | -0.07782 | 0.31586 | 0 | 0.65918 | 122.6852 | 0.16479 | 0.33874 | 122.8271 | 122.8455 | 122.7264 | 122.7676 | -122.8317 | -122.8088 | 122.5845 | 0.26093 | 2.6871 | 1.181
3048.1719 | 123.0286 | -54.8355 | 67.9138 | -0.10635 | -1.9142e-05 | 0.061171 | 0.070541 | -0.0034714 | 0.0021917 | 0.0043536 | -0.010498 | 0.0021703 | 0.0025634 | 0.0064684 | -0.0019333 | -0.0053663 | -0.0018971 | -52.1484 | 67.9825 | -54.895 | 67.7353 | -54.245 | -54.6433 | -54.0527 | -53.6407 | 67.9733 | -54.895 | -54.5517 | -54.7073 | -54.8676 | -54.5334 | -0.05951 | 0.068665 | -0.17853 | 0.59051 | 0.78278 | 0.19226 | 0.84229 | 0.25177 | -0.05951 | 0.05951 | -122.4655 | 0.12817 | 0.30212 | -0.032044 | 0.36163 | 0.027466 | 0.65002 | 122.6303 | 0.18768 | 0.34332 | 122.8775 | 122.8683 | 122.818 | 122.8088 | -122.8088 | -122.8088 | 122.5708 | 0.28381 | 2.6871 | 1.1948
3049.1719 | 123.0057 | -54.8035 | 67.9779 | -0.091095 | 0.00083526 | 0.06053 | 0.068404 | -0.0021896 | 0.0017645 | 0.0037128 | 0.050537 | -0.0012477 | 0.00042723 | 0.00027342 | -0.0025741 | -0.0068615 | 0.00045294 | -52.1164 | 67.955 | -54.8676 | 67.7902 | -54.213 | -54.5975 | -54.0115 | -53.627 | 67.9733 | -54.8492 | -54.5425 | -54.6844 | -54.8309 | -54.5517 | -0.064087 | -0.022888 | -0.18768 | 0.59051 | 0.79193 | 0.20599 | 0.85602 | 0.27008 | -0.045776 | -0.004577 | -122.5204 | 0.11902 | 0.25177 | -0.027466 | 0.29755 | 0.01831 | 0.6546 | 122.6578 | 0.16479 | 0.3067 | 122.8226 | 122.8226 | 122.7585 | 122.7768 | -122.8455 | -122.8271 | 122.5937 | 0.26093 | 2.6871 | 1.1765
3050.1719 | 122.9874 | -54.8309 | 67.955 | -0.068207 | 0.00040806 | 0.062239 | 0.0699 | -5.343e-05 | 0.0041143 | 0.0026446 | -0.041016 | -0.00082025 | 0.00064083 | 0.0077502 | -0.00086511 | -0.0023755 | 0.00023934 | -52.1576 | 67.9321 | -54.9133 | 67.7353 | -54.2953 | -54.7028 | -54.0894 | -53.7094 | 68.0008 | -54.863 | -54.5883 | -54.7577 | -54.9133 | -54.5837 | -0.082397 | -0.022888 | -0.21973 | 0.53558 | 0.74158 | 0.12817 | 0.82398 | 0.21057 | -0.032043 | 0.045776 | -122.5433 | 0.073243 | 0.24719 | -0.082397 | 0.27924 | -0.050354 | 0.61798 | 122.6486 | 0.10529 | 0.27466 | 122.8455 | 122.8638 | 122.7631 | 122.8317 | -122.8683 | -122.818 | 122.5662 | 0.24262 | 2.6733 | 1.1215
3051.1719 | 123.0652 | -54.7989 | 67.9504 | -0.12161 | -0.00087374 | 0.061598 | 0.069259 | 0.00037377 | 0.0021917 | 0.005849 | -0.041016 | 0.00046135 | 0.00064083 | 0.0075366 | -0.0025741 | -0.0032301 | 0.0010937 | -52.1255 | 67.9688 | -54.8813 | 67.7765 | -54.2221 | -54.6295 | -54.0161 | -53.6362 | 67.9962 | -54.8676 | -54.5334 | -54.6982 | -54.8721 | -54.5334 | -0.082398 | 0.018311 | -0.17395 | 0.57678 | 0.78278 | 0.16937 | 0.86517 | 0.25177 | -0.068665 | 0.045777 | -122.4838 | 0.10071 | 0.2655 | -0.073242 | 0.33417 | -0.004577 | 0.65918 | 122.6578 | 0.16937 | 0.33417 | 122.85 | 122.8638 | 122.7676 | 122.7951 | -122.8317 | -122.818 | 122.5754 | 0.2655 | 2.6733 | 1.1627
3052.1719 | 122.9279 | -54.8355 | 67.9733 | -0.10635 | -1.9142e-05 | 0.061171 | 0.073104 | -0.00069423 | 0.0013373 | 0.0064898 | -0.037964 | 0.0030249 | 0.0014954 | -0.0035718 | -0.0032151 | -0.0051527 | 0.0013073 | -52.1439 | 67.9916 | -54.9042 | 67.717 | -54.3045 | -54.7211 | -54.0939 | -53.7323 | 68.0328 | -54.863 | -54.6066 | -54.7806 | -54.9591 | -54.6204 | -0.068665 | 0.01831 | -0.25635 | 0.53101 | 0.74158 | 0.11444 | 0.81024 | 0.18311 | -0.027466 | 0.059509 | -122.58 | 0.054931 | 0.21515 | -0.1236 | 0.24262 | -0.09613 | 0.59967 | 122.6212 | 0.082397 | 0.25635 | 122.8958 | 122.8958 | 122.8271 | 122.8683 | -122.8775 | -122.8363 | 122.5525 | 0.22888 | 2.6917 | 1.1032
3053.1719 | 123.0057 | -54.8218 | 67.9733 | -0.098725 | 0.0012625 | 0.06288 | 0.07289 | 0.00080117 | 0.0051825 | 0.0073444 | -0.041016 | 0.0013159 | -0.001709 | 0.0015552 | -0.0019333 | -0.0049389 | 0.0013073 | -52.1301 | 68.0008 | -54.9042 | 67.7261 | -54.2725 | -54.6936 | -54.0939 | -53.7003 | 68.0145 | -54.8538 | -54.5746 | -54.7531 | -54.8996 | -54.5792 | -0.082398 | 0.027465 | -0.24719 | 0.54932 | 0.72784 | 0.12817 | 0.81024 | 0.21057 | -0.032044 | 0.041198 | -122.5479 | 0.068664 | 0.24261 | -0.07782 | 0.27466 | -0.045776 | 0.63171 | 122.6303 | 0.10071 | 0.27924 | 122.905 | 122.8683 | 122.8226 | 122.8363 | -122.8775 | -122.8271 | 122.5479 | 0.24719 | 2.6916 | 1.1215
3054.1719 | 123.1476 | -54.7485 | 68.0603 | -0.098725 | 0.00083526 | 0.060744 | 0.066482 | -0.0041122 | 0.0051825 | 0.0043536 | 0.035278 | -0.00017945 | -0.001709 | 0.0045458 | -0.0023605 | -0.0045117 | -0.0029651 | -52.0432 | 68.0099 | -54.8218 | 67.8772 | -54.0894 | -54.5105 | -53.9154 | -53.508 | 68.0099 | -54.7714 | -54.4922 | -54.6295 | -54.8813 | -54.4098 | -0.073242 | -0.050354 | -0.18311 | 0.65918 | 0.83313 | 0.23804 | 0.90637 | 0.31128 | -0.022888 | -0.050354 | -122.5525 | 0.11902 | 0.33874 | -0.13275 | 0.36163 | -0.10986 | 0.73242 | 122.699 | 0.14191 | 0.27924 | 122.8317 | 122.7814 | 122.7585 | 122.7585 | -122.8821 | -122.8317 | 122.6257 | 0.25635 | 2.7054 | 1.2405
3055.1719 | 122.9416 | -54.8309 | 67.9916 | -0.17502 | 0.0010489 | 0.059676 | 0.070541 | 0.003151 | 0.0028327 | 0.00072199 | -0.037964 | 0.00088875 | -0.00042717 | 0.00091422 | -0.00086511 | -0.0045117 | -0.0036059 | -52.0935 | 68.0237 | -54.8676 | 67.7353 | -54.2999 | -54.7073 | -54.1077 | -53.7186 | 68.042 | -54.8492 | -54.6021 | -54.7668 | -54.9408 | -54.6066 | -0.036621 | 0.032044 | -0.25635 | 0.53101 | 0.72327 | 0.1236 | 0.75989 | 0.16022 | -0.01831 | 0.050354 | -122.5937 | 0.064087 | 0.22431 | -0.10986 | 0.24262 | -0.091553 | 0.56763 | 122.6028 | 0.082397 | 0.24719 | 122.8912 | 122.8912 | 122.8546 | 122.8729 | -122.8592 | -122.8409 | 122.5662 | 0.22888 | 2.7374 | 1.1124
3056.1719 | 122.9507 | -54.7943 | 68.0328 | -0.098725 | 0.00062166 | 0.063094 | 0.0699 | -0.00069423 | 0.0021917 | 0.009267 | -0.044067 | 0.0011023 | 0.0014954 | 0.0051868 | -0.0012925 | -0.0032301 | 0.00023934 | -52.1805 | 67.9871 | -54.8676 | 67.5385 | -54.0894 | -54.3869 | -54.0573 | -53.6911 | 68.0603 | -54.8538 | -54.6112 | -54.7989 | -54.9637 | -54.6295 | -0.073242 | -0.045776 | -0.49438 | 0.70496 | 0.737 | 0.40741 | 0.81024 | 0.48065 | -0.059509 | 0.027466 | -122.644 | -0.004577 | 0.16479 | -0.16937 | 0.2243 | -0.10986 | 0.7782 | 122.406 | 0.054932 | 0.24262 | 122.8546 | 122.9141 | 122.7814 | 122.8546 | -122.9004 | -122.8867 | 122.3328 | 0.18311 | 2.6138 | 1.1032
3057.1719 | 122.9782 | -54.7943 | 68.0237 | -0.052948 | 0.0012625 | 0.063734 | 0.070113 | 0.00016017 | 0.0026191 | 0.0067036 | -0.059326 | -0.00017945 | 0.00064083 | 0.0024096 | -0.0042831 | -0.0036573 | 0.0047253 | -52.1439 | 68.0054 | -54.8767 | 67.6941 | -54.3411 | -54.7211 | -54.126 | -53.7735 | 68.0557 | -54.8447 | -54.6707 | -55.0735 | -54.7348 | -54.4373 | -0.082397 | -0.018311 | -0.32959 | 0.45319 | 0.66833 | 0.073243 | 0.75073 | 0.15564 | -0.050354 | 0.032043 | -122.6944 | -0.27923 | 0.35706 | 0.05951 | 0.40741 | 0.10986 | 0.53558 | 122.5708 | -0.22888 | 0.17395 | 122.8821 | 122.9004 | 122.7997 | 122.85 | -122.9004 | -122.8683 | 122.4884 | 0.1236 | 2.6505 | 1.0208
3058.1719 | 122.9553 | -54.8218 | 67.9779 | -0.12161 | -0.0010873 | 0.061598 | 0.072036 | -0.0011214 | 0.00091009 | 0.0073444 | -0.062378 | 0.0017431 | 0.00042723 | 0.0015552 | -0.00043791 | -0.0040845 | 0.0015209 | -52.1118 | 68.0374 | -54.9042 | 67.804 | -54.3732 | -54.657 | -54.0573 | -53.6957 | 68.074 | -54.8401 | -54.6112 | -54.7897 | -54.9454 | -54.6204 | -0.082398 | 0.05951 | -0.17395 | 0.44861 | 0.76446 | 0.16479 | 0.84686 | 0.24719 | -0.018311 | 0.096131 | -122.5891 | 0.032043 | 0.20142 | -0.1236 | 0.21973 | -0.10529 | 0.53101 | 122.7081 | 0.050354 | 0.22888 | 122.9416 | 122.9141 | 122.8592 | 122.8958 | -122.8821 | -122.818 | 122.6257 | 0.21057 | 2.71 | 1.1261
3059.1719 | 122.9233 | -54.808 | 68.0283 | -0.052948 | 0.0012625 | 0.06288 | 0.069045 | 0.00058737 | 0.0021917 | 0.0073444 | -0.037964 | 0.00024775 | 0.00042723 | 0.0017688 | -0.0019333 | -0.0047253 | 0.0032299 | -52.0889 | 68.0099 | -54.8767 | 67.7719 | -54.2404 | -54.657 | -54.071 | -53.6819 | 68.0695 | -54.8218 | -54.6158 | -54.7623 | -54.9362 | -54.6066 | -0.068665 | -0.01831 | -0.25635 | 0.56763 | 0.737 | 0.15106 | 0.80566 | 0.21973 | -0.013733 | 0.041199 | -122.644 | 0.045776 | 0.20142 | -0.12817 | 0.21515 | -0.11444 | 0.63629 | 122.6486 | 0.059509 | 0.20599 | 122.8867 | 122.8912 | 122.818 | 122.8775 | -122.905 | -122.85 | 122.58 | 0.19226 | 2.7191 | 1.1261
3060.1719 | 122.9553 | -54.7714 | 68.042 | -0.068207 | 0.00040806 | 0.061171 | 0.069472 | 0.0012284 | 0.0013373 | 0.0067036 | -0.050171 | 0.0023839 | 0.0014954 | -0.00229 | -0.00065151 | -0.0047253 | -0.0014697 | -52.0615 | 68.0237 | -54.8584 | 67.7856 | -54.2221 | -54.6295 | -54.0573 | -53.6499 | 68.0557 | -54.8355 | -54.5746 | -54.7348 | -54.9088 | -54.5792 | -0.086975 | -0.01831 | -0.25635 | 0.54932 | 0.71411 | 0.14191 | 0.80109 | 0.22888 | -0.064087 | 0.013733 | -122.6166 | 0.036621 | 0.19226 | -0.13733 | 0.25635 | -0.073242 | 0.63629 | 122.644 | 0.10071 | 0.26093 | 122.8821 | 122.8912 | 122.7951 | 122.8271 | -122.9004 | -122.8775 | 122.5571 | 0.19684 | 2.71 | 1.1215
3061.1719 | 122.9095 | -54.7897 | 68.0237 | -0.12924 | 0.0010489 | 0.060957 | 0.069045 | 0.00016017 | 0.00091009 | 0.0064898 | -0.044067 | 0.00088875 | 0.001068 | 0.0026232 | -0.0034287 | -0.0025891 | 0.0038709 | -52.0798 | 68.0328 | -54.8538 | 67.7628 | -54.2496 | -54.6707 | -54.0894 | -53.714 | 68.0603 | -54.863 | -54.6021 | -54.776 | -54.95 | -54.6021 | -0.064087 | 0.009155 | -0.26093 | 0.54016 | 0.70038 | 0.11902 | 0.76447 | 0.18311 | -0.073242 | 0.036621 | -122.6257 | 0.013733 | 0.18768 | -0.16022 | 0.26093 | -0.086975 | 0.60425 | 122.6166 | 0.086975 | 0.26093 | 122.8867 | 122.9233 | 122.8226 | 122.85 | -122.8775 | -122.8867 | 122.5525 | 0.18768 | 2.71 | 1.0757
3062.1719 | 122.9416 | -54.8035 | 68.0283 | -0.10635 | 0.00083526 | 0.062239 | 0.071609 | -0.00048063 | 0.0032599 | 0.0071308 | -0.025757 | 0.0017431 | 0.00042723 | -0.00015378 | 0.00063009 | -0.0045117 | -0.00082886 | -52.0523 | 68.042 | -54.8309 | 67.7719 | -54.2267 | -54.6295 | -54.039 | -53.6636 | 68.0923 | -54.8218 | -54.5837 | -54.7577 | -54.8996 | -54.5837 | -0.027466 | 0.013733 | -0.25635 | 0.57678 | 0.76447 | 0.17395 | 0.79193 | 0.20142 | -0.01831 | 0.064087 | -122.612 | 0.045777 | 0.21973 | -0.09613 | 0.23804 | -0.07782 | 0.60425 | 122.6028 | 0.064087 | 0.23804 | 122.8729 | 122.9141 | 122.8455 | 122.8958 | -122.8592 | -122.85 | 122.5754 | 0.21973 | 2.7512 | 1.1398
3063.1719 | 122.9507 | -54.7714 | 68.0511 | -0.083466 | -0.00023294 | 0.063307 | 0.069472 | 0.00080117 | 0.0043281 | 0.0037128 | -0.03186 | -0.00060665 | 0.001068 | -0.0067762 | -0.00022431 | -0.0034437 | 0.00088014 | -52.0432 | 68.0603 | -54.8126 | 67.8085 | -54.1809 | -54.6066 | -54.0298 | -53.6362 | 68.0557 | -54.8035 | -54.5746 | -54.7394 | -54.863 | -54.5609 | -0.041199 | 0.009156 | -0.24261 | 0.59051 | 0.74158 | 0.16479 | 0.78278 | 0.20599 | -0.032044 | 0.004578 | -122.6257 | 0.032043 | 0.21057 | -0.091553 | 0.24262 | -0.059509 | 0.63171 | 122.6212 | 0.064087 | 0.22888 | 122.8729 | 122.8592 | 122.8317 | 122.8271 | -122.8638 | -122.8546 | 122.58 | 0.19684 | 2.7283 | 1.1353
3064.1719 | 122.9187 | -54.7989 | 68.042 | -0.098725 | 0.0025443 | 0.062453 | 0.070327 | 0.0010148 | 0.0028327 | 0.0060626 | -0.022705 | 0.00024775 | 0.00085443 | -0.0016492 | -0.00065151 | -0.0045117 | 0.00045294 | -52.0798 | 68.0466 | -54.8492 | 67.7673 | -54.2221 | -54.6387 | -54.0436 | -53.6636 | 68.0786 | -54.8035 | -54.5746 | -54.7714 | -54.9362 | -54.5837 | -0.050354 | 0.004578 | -0.27466 | 0.57678 | 0.75531 | 0.16022 | 0.80566 | 0.21057 | -0.004578 | 0.036621 | -122.6166 | 0.027466 | 0.21515 | -0.13733 | 0.21973 | -0.13275 | 0.62714 | 122.6166 | 0.032044 | 0.22888 | 122.8958 | 122.8821 | 122.8455 | 122.8775 | -122.8912 | -122.8455 | 122.5662 | 0.2243 | 2.7191 | 1.1353
3065.1719 | 122.9279 | -54.8172 | 68.0878 | -0.045319 | 0.0016899 | 0.062666 | 0.069686 | -0.00090783 | 0.0011237 | 0.0052082 | -0.022705 | 0.0015295 | 0.00064083 | 0.00070062 | 0.00020289 | -0.0038709 | 0.0083569 | -52.0432 | 68.0511 | -54.8309 | 67.7902 | -54.1946 | -54.6433 | -54.0344 | -53.6407 | 68.0969 | -54.808 | -54.5837 | -54.7394 | -54.8996 | -54.5792 | -0.013733 | -0.036622 | -0.29755 | 0.62256 | 0.78278 | 0.17395 | 0.79651 | 0.18768 | 0.009156 | 0.009155 | -122.6715 | 0.07782 | 0.23804 | -0.082397 | 0.22888 | -0.091553 | 0.63629 | 122.6212 | 0.068664 | 0.2243 | 122.8821 | 122.905 | 122.8683 | 122.9141 | -122.9187 | -122.8958 | 122.6074 | 0.23346 | 2.774 | 1.1765
3066.1719 | 122.9736 | -54.7577 | 68.0557 | -0.037689 | 0.0031851 | 0.064375 | 0.069259 | 0.0012284 | 0.0013373 | 0.0052082 | 0.0047608 | 0.0019567 | 0.0025634 | 0.0026232 | -0.0010787 | -0.0036573 | 0.0015209 | -52.0111 | 68.0466 | -54.7943 | 67.8268 | -54.1306 | -54.57 | -54.1489 | -53.54 | 68.1061 | -54.7668 | -54.4922 | -54.6799 | -54.8309 | -54.5197 | -0.036622 | -0.009155 | -0.22888 | 0.62714 | 0.60882 | 0.18768 | 0.64545 | 0.22431 | -0.009156 | 0.050354 | -122.5479 | 0.077819 | 0.23804 | -0.073243 | 0.24719 | -0.064087 | 0.66376 | 122.6212 | 0.086975 | 0.27466 | 122.8409 | 122.8729 | 122.8043 | 122.8638 | -122.85 | -122.8226 | 122.5845 | 0.2655 | 2.7466 | 1.2177
3067.1719 | 122.9507 | -54.7485 | 68.0878 | -0.060578 | 0.0010489 | 0.062453 | 0.071395 | 0.0016556 | 0.0011237 | 0.007558 | 0.013916 | 0.0013159 | 0.001709 | -0.00036738 | -0.0012925 | -0.0049389 | 0.0023755 | -52.034 | 68.0557 | -54.8035 | 67.8268 | -54.1626 | -54.57 | -54.0024 | -53.5904 | 68.1152 | -54.7714 | -54.5242 | -54.7165 | -54.8538 | -54.538 | -0.054932 | -0.032044 | -0.26093 | 0.58594 | 0.74615 | 0.17853 | 0.80109 | 0.23346 | -0.022888 | 0.027465 | -122.612 | 0.032043 | 0.21057 | -0.10529 | 0.23346 | -0.082398 | 0.64087 | 122.6303 | 0.054931 | 0.24719 | 122.8592 | 122.8867 | 122.8043 | 122.8638 | -122.8912 | -122.8592 | 122.5754 | 0.2243 | 2.7145 | 1.1581
3068.1719 | 122.9599 | -54.7668 | 68.0832 | -0.13687 | -0.00023294 | 0.060316 | 0.069259 | 0.0027238 | 0.0036871 | 0.0071308 | -0.041016 | 0.0013159 | 0.00064083 | -0.00058098 | -0.0023605 | -0.0025891 | 0.00023934 | -52.0935 | 68.0603 | -54.7852 | 67.8177 | -54.126 | -54.5517 | -53.9795 | -53.5583 | 68.0969 | -54.776 | -54.5242 | -54.6753 | -54.8401 | -54.5059 | -0.01831 | -0.022888 | -0.2655 | 0.64087 | 0.78735 | 0.21515 | 0.80566 | 0.23346 | -0.009155 | 0.013733 | -122.6074 | 0.091553 | 0.26093 | -0.073242 | 0.27008 | -0.064087 | 0.65918 | 122.6028 | 0.10071 | 0.25177 | 122.8455 | 122.8729 | 122.8271 | 122.8638 | -122.8683 | -122.8592 | 122.5845 | 0.24262 | 2.6733 | 1.2085
3069.1719 | 122.9828 | -54.7485 | 68.0695 | -0.12161 | 0.0010489 | 0.059889 | 0.070541 | 0.0052872 | 0.0047553 | 0.005849 | 0.041382 | 0.00024775 | 0.001068 | -0.0010084 | -0.0027877 | -0.0028027 | 0.0017345 | -52.0065 | 68.0649 | -54.7897 | 67.8406 | -54.1489 | -54.7348 | -54.0298 | -53.5355 | 68.129 | -54.7211 | -54.4922 | -54.6616 | -54.8218 | -54.5105 | -0.041199 | -0.004578 | -0.22888 | 0.59967 | 0.71869 | 0.013733 | 0.75989 | 0.054932 | 0.027466 | 0.059509 | -122.5616 | 0.086975 | 0.23804 | -0.073242 | 0.21057 | -0.10071 | 0.64087 | 122.6303 | 0.059509 | 0.22888 | 122.8546 | 122.85 | 122.8134 | 122.8775 | -122.8592 | -122.7905 | 122.5891 | 0.25635 | 2.742 | 1.2131
3070.1719 | 122.9416 | -54.7348 | 68.0832 | -0.045319 | -0.00023294 | 0.060316 | 0.068404 | -0.00026703 | 0.00091009 | 0.0052082 | 0.001709 | -0.00017945 | 0.00085443 | -0.0080578 | -1.0706e-05 | -0.0038709 | -0.0023243 | -51.9882 | 68.0969 | -54.8126 | 67.8497 | -54.126 | -54.5563 | -53.9795 | -53.5538 | 68.1061 | -54.7897 | -54.4876 | -54.6387 | -54.8126 | -54.5059 | -0.07782 | 0.013733 | -0.23346 | 0.60883 | 0.75531 | 0.17853 | 0.83313 | 0.25635 | -0.054932 | 0.022888 | -122.5708 | 0.09613 | 0.22888 | -0.07782 | 0.28381 | -0.022888 | 0.68664 | 122.6624 | 0.15106 | 0.30212 | 122.9095 | 122.8958 | 122.8317 | 122.8409 | -122.8958 | -122.8729 | 122.5845 | 0.24719 | 2.7466 | 1.181
3071.1719 | 122.9141 | -54.7714 | 68.074 | -0.045319 | 0.0016899 | 0.063094 | 0.071395 | 0.00080117 | 0.0021917 | 0.0060626 | -0.0013428 | 0.0015295 | 0.00021363 | -0.0033582 | -0.0019333 | -0.0034437 | -0.0012561 | -51.9836 | 68.1061 | -54.776 | 67.8452 | -54.126 | -54.5425 | -53.9612 | -53.54 | 68.1473 | -54.7714 | -54.4922 | -54.6433 | -54.8035 | -54.451 | -0.004578 | 0.032043 | -0.22888 | 0.64545 | 0.81024 | 0.22888 | 0.81482 | 0.23346 | 0 | 0.073242 | -122.5662 | 0.12817 | 0.32043 | -0.032044 | 0.32043 | -0.032044 | 0.65002 | 122.6212 | 0.12817 | 0.27924 | 122.8821 | 122.9187 | 122.8775 | 122.9187 | -122.85 | -122.8455 | 122.6166 | 0.27924 | 2.7878 | 1.2314
3072.1719 | 122.9462 | -54.7302 | 68.0557 | -0.54123 | 0.0027579 | 0.060744 | 0.068404 | 0.00016017 | 0.0013373 | 0.0054218 | -0.0043946 | 0.0017431 | -0.00021357 | -0.005708 | -0.00065151 | -0.0066479 | 0.0021619 | -51.9241 | 68.074 | -54.7989 | 67.868 | -54.1031 | -54.5471 | -53.9886 | -53.5492 | 68.1244 | -54.7485 | -54.5105 | -54.6616 | -54.8355 | -54.5197 | -0.068664 | 0.018311 | -0.18768 | 0.62714 | 0.74158 | 0.18311 | 0.81024 | 0.25177 | -0.01831 | 0.068665 | -122.5662 | 0.068665 | 0.21057 | -0.10529 | 0.22888 | -0.086975 | 0.6958 | 122.6669 | 0.086975 | 0.23804 | 122.8729 | 122.8729 | 122.8043 | 122.8546 | -122.8546 | -122.8043 | 122.5983 | 0.21973 | 2.8061 | 1.181
3073.1719 | 122.9828 | -54.7256 | 68.1061 | -0.037689 | -0.0021555 | 0.061385 | 0.068404 | -0.0017624 | 0.0045417 | 0.0047808 | 0.032227 | 0.0017431 | 0.0021362 | 0.002196 | -0.00086511 | -0.0062207 | -0.0012561 | -51.9745 | 68.1015 | -54.7943 | 67.8497 | -54.1214 | -54.5151 | -53.9612 | -53.5263 | 68.1107 | -54.7806 | -54.5105 | -54.657 | -54.7943 | -54.4876 | -0.068665 | -0.004578 | -0.25635 | 0.60425 | 0.76447 | 0.21057 | 0.83313 | 0.27924 | -0.054932 | 0.004578 | -122.6166 | 0.068665 | 0.23804 | -0.068665 | 0.29297 | -0.013733 | 0.67291 | 122.644 | 0.1236 | 0.27008 | 122.8958 | 122.8912 | 122.8271 | 122.8363 | -122.9004 | -122.8867 | 122.5754 | 0.21515 | 2.7512 | 1.1993
3074.1719 | 122.9736 | -54.7165 | 68.1107 | -0.068207 | 0.00062166 | 0.064162 | 0.068832 | -0.00090783 | 0.0021917 | 0.0088398 | 0.03833 | -0.00017945 | 0.00085443 | 5.9824e-05 | -0.0019333 | -0.0047253 | 0.0013073 | -51.9699 | 68.0923 | -54.7989 | 67.8635 | -54.2496 | -54.5792 | -53.9108 | -53.5172 | 68.1473 | -54.744 | -54.4876 | -54.6478 | -54.7989 | -54.4922 | -0.082397 | -0.018311 | -0.24719 | 0.46692 | 0.80566 | 0.13733 | 0.88806 | 0.21973 | -0.027466 | 0.036621 | -122.5983 | 0.068665 | 0.22431 | -0.082397 | 0.25177 | -0.054931 | 0.54932 | 122.6624 | 0.096131 | 0.25635 | 122.8912 | 122.8912 | 122.8088 | 122.8638 | -122.9095 | -122.8546 | 122.58 | 0.22888 | 2.7466 | 1.1993
3075.1719 | 122.9645 | -54.7302 | 68.1244 | -0.13687 | 0.00019446 | 0.061598 | 0.067977 | 0.0010148 | 0.0011237 | 0.0081988 | -0.12341 | 0.0019567 | -0.00021357 | -0.00079478 | -0.00086511 | -0.0064343 | -0.0010425 | -51.9699 | 68.129 | -54.744 | 67.8909 | -54.0939 | -54.5471 | -53.952 | -53.4668 | 68.1335 | -54.7485 | -54.4739 | -54.6249 | -54.7806 | -54.4647 | -0.013733 | 0.004577 | -0.23346 | 0.63629 | 0.7782 | 0.18311 | 0.79193 | 0.19684 | -0.01831 | 0.009155 | -122.5983 | 0.10529 | 0.2655 | -0.050354 | 0.28381 | -0.032044 | 0.65002 | 122.6349 | 0.1236 | 0.27466 | 122.8729 | 122.8821 | 122.8592 | 122.8638 | -122.8683 | -122.8729 | 122.6212 | 0.25635 | 2.7603 | 1.2634
3076.1719 | 123.0011 | -54.7028 | 68.1061 | -0.083466 | -0.0010873 | 0.062666 | 0.071395 | 0.0033646 | 0.0028327 | 0.005849 | 0.023071 | 0.0021703 | 0.00042723 | -0.0037854 | -0.0040695 | -0.0055799 | -0.0031787 | -51.9745 | 68.129 | -54.7531 | 67.8635 | -54.1031 | -54.5334 | -53.9429 | -53.5446 | 68.1473 | -54.7531 | -54.451 | -54.6295 | -54.8264 | -54.4785 | -0.050354 | 0.022888 | -0.24262 | 0.59967 | 0.75989 | 0.16937 | 0.81024 | 0.21973 | -0.050354 | 0.041199 | -122.5571 | 0.073242 | 0.2243 | -0.1236 | 0.27466 | -0.073242 | 0.65002 | 122.6166 | 0.1236 | 0.30212 | 122.8821 | 122.9004 | 122.8317 | 122.85 | -122.8592 | -122.8592 | 122.5662 | 0.25177 | 2.7283 | 1.1581
3077.1719 | 122.9645 | -54.7073 | 68.1107 | -0.083466 | 0.0010489 | 0.062025 | 0.0699 | 0.00080117 | 0.0026191 | 0.001363 | 0.0078126 | 0.0011023 | 0.004486 | -0.00058098 | -0.00065151 | -0.0047253 | 0.0030163 | -51.9424 | 68.1061 | -54.7668 | 67.8635 | -54.0894 | -54.5151 | -53.9658 | -53.5309 | 68.1564 | -54.7211 | -54.5929 | -54.538 | -54.7714 | -54.4601 | -0.05951 | -0.004578 | -0.24719 | 0.61798 | 0.74158 | 0.19226 | 0.80109 | 0.25177 | -0.013733 | 0.045776 | -122.7036 | 0.16937 | 0.24719 | -0.064087 | 0.26093 | -0.050354 | 0.67749 | 122.6303 | 0.1831 | 0.12817 | 122.8729 | 122.8775 | 122.8134 | 122.8638 | -122.8775 | -122.8317 | 122.5708 | 0.11444 | 2.7649 | 1.1765
3078.1719 | 122.9416 | -54.7165 | 68.1015 | -0.068207 | 0.0016899 | 0.061812 | 0.069472 | 0.0052872 | 0.0013373 | 0.0064898 | -0.01355 | 3.4148e-05 | 0.00085443 | -0.0018628 | -0.0023605 | -0.0049389 | -0.00061526 | -51.9562 | 68.1198 | -54.744 | 67.868 | -54.1122 | -54.5242 | -53.952 | -53.5446 | 68.1381 | -54.7028 | -54.5013 | -54.6661 | -54.808 | -54.4922 | -0.027466 | 0.018311 | -0.23346 | 0.60425 | 0.76447 | 0.19226 | 0.79193 | 0.21973 | 0.013733 | 0.036622 | -122.6028 | 0.050354 | 0.22431 | -0.091552 | 0.21057 | -0.10529 | 0.63171 | 122.612 | 0.036621 | 0.20142 | 122.8638 | 122.8409 | 122.8363 | 122.8546 | -122.8455 | -122.8043 | 122.5845 | 0.21515 | 2.7603 | 1.1719
3079.1719 | 122.9233 | -54.7028 | 68.1152 | -0.045319 | -1.9142e-05 | 0.060957 | 0.072036 | 0.001442 | 0.0021917 | 0.0064898 | -0.01355 | 0.0040929 | 0.0019226 | -0.0035718 | -0.0019333 | -0.0055799 | 0.0019483 | -51.9791 | 68.1152 | -54.7623 | 67.8314 | -54.1306 | -54.5746 | -53.9932 | -53.5995 | 68.129 | -54.7302 | -54.5242 | -54.6936 | -54.8584 | -54.5425 | -0.059509 | 0 | -0.28381 | 0.57221 | 0.70953 | 0.12817 | 0.76904 | 0.18768 | -0.027466 | 0.013733 | -122.6395 | 0.009155 | 0.16022 | -0.15564 | 0.18768 | -0.12817 | 0.63171 | 122.5937 | 0.036621 | 0.20599 | 122.8775 | 122.8592 | 122.818 | 122.8317 | -122.8775 | -122.8455 | 122.5342 | 0.17853 | 2.7237 | 1.1032
3080.1719 | 122.9507 | -54.6753 | 68.1198 | -0.03006 | 0.0010489 | 0.060744 | 0.068618 | -0.00090783 | 0.0021917 | 0.0064898 | 0.041382 | 0.0032385 | -0.00021357 | -0.003999 | -0.0023605 | -0.0038709 | -0.0029651 | -51.9333 | 68.1335 | -54.7577 | 67.8818 | -54.0665 | -54.5059 | -53.9337 | -53.4988 | 68.1702 | -54.7165 | -54.4647 | -54.6295 | -54.7668 | -54.4693 | -0.082397 | 0.013733 | -0.23804 | 0.60883 | 0.74158 | 0.16937 | 0.82397 | 0.25177 | -0.041199 | 0.050354 | -122.5845 | 0.045776 | 0.20599 | -0.091553 | 0.24719 | -0.050354 | 0.69122 | 122.6395 | 0.086975 | 0.25177 | 122.8912 | 122.8867 | 122.8088 | 122.8455 | -122.8775 | -122.8363 | 122.5571 | 0.21057 | 2.742 | 1.1765
3081.1719 | 122.9691 | -54.6844 | 68.1107 | -0.037689 | -0.00087374 | 0.061598 | 0.0699 | -0.0026168 | 0.0036871 | 0.0049946 | -0.010498 | 3.4148e-05 | 0.00064083 | 0.0045458 | -0.0012925 | -0.0062207 | 0.0030163 | -51.947 | 68.1107 | -54.7302 | 67.9459 | -54.0436 | -54.483 | -53.9154 | -53.4988 | 68.161 | -54.7348 | -54.4647 | -54.6295 | -54.7943 | -54.4647 | -0.045777 | 0 | -0.16479 | 0.64087 | 0.76904 | 0.20142 | 0.81482 | 0.24719 | -0.050354 | 0.050354 | -122.5754 | 0.054931 | 0.21973 | -0.10986 | 0.27008 | -0.05951 | 0.68665 | 122.6761 | 0.10529 | 0.27008 | 122.8409 | 122.8958 | 122.7951 | 122.8455 | -122.8409 | -122.8455 | 122.6303 | 0.21973 | 2.7374 | 1.1856
3082.1719 | 122.937 | -54.689 | 68.1198 | -0.12924 | -1.9142e-05 | 0.061598 | 0.067123 | 0.0018692 | 0.00069649 | 0.0047808 | -0.071533 | 0.0015295 | 2.8e-08 | 0.00091422 | -0.0021469 | -0.0032301 | 0.0034435 | -51.9379 | 68.1244 | -54.7394 | 67.8955 | -54.0619 | -54.4968 | -53.9337 | -53.4119 | 68.1747 | -54.7394 | -54.4464 | -54.5975 | -54.7577 | -54.451 | -0.050354 | 0.004578 | -0.2243 | 0.62714 | 0.75531 | 0.19226 | 0.80566 | 0.24261 | -0.050354 | 0.054932 | -122.5662 | 0.091553 | 0.23804 | -0.068664 | 0.28839 | -0.01831 | 0.67749 | 122.6349 | 0.14191 | 0.29297 | 122.8638 | 122.9141 | 122.8134 | 122.8638 | -122.8592 | -122.8592 | 122.5845 | 0.24262 | 2.7512 | 1.2772
3083.1719 | 122.9462 | -54.689 | 68.1427 | -0.091095 | 0.00083526 | 0.060957 | 0.069045 | 0.00251 | 0.0019781 | 0.005849 | -0.0013428 | 0.0015295 | 0.00064083 | -0.0016492 | -0.0017197 | -0.0062207 | 0.00066654 | -51.9287 | 68.1564 | -54.7256 | 67.9047 | -54.0848 | -54.4968 | -53.9291 | -53.4897 | 68.1473 | -54.7073 | -54.451 | -54.5837 | -54.7485 | -54.4418 | -0.036621 | 0.013733 | -0.23804 | 0.60425 | 0.75989 | 0.19226 | 0.79651 | 0.22888 | -0.01831 | 0.004578 | -122.5937 | 0.10529 | 0.24719 | -0.059509 | 0.2655 | -0.041199 | 0.64087 | 122.6303 | 0.1236 | 0.25635 | 122.8821 | 122.8546 | 122.8455 | 122.8363 | -122.8683 | -122.85 | 122.5937 | 0.23804 | 2.7603 | 1.1993
3084.1719 | 122.937 | -54.689 | 68.1519 | -0.037689 | 0.0012625 | 0.061812 | 0.068191 | -0.00069423 | 0.0030463 | 0.0047808 | 0.013916 | 0.0023839 | 0.001068 | -0.0052808 | -0.0023605 | -0.0045117 | 0.00023934 | -51.9058 | 68.1519 | -54.7302 | 67.8955 | -54.039 | -54.4922 | -53.92 | -53.4714 | 68.1519 | -54.6936 | -54.4373 | -54.6204 | -54.7531 | -54.4327 | -0.041199 | 0 | -0.25635 | 0.65002 | 0.76904 | 0.19684 | 0.81024 | 0.23804 | -0.004578 | 0 | -122.5891 | 0.068665 | 0.25635 | -0.064087 | 0.26093 | -0.059509 | 0.69122 | 122.6257 | 0.073243 | 0.25635 | 122.8821 | 122.8455 | 122.8409 | 122.8409 | -122.8821 | -122.8455 | 122.5845 | 0.25177 | 2.7832 | 1.2177
3085.1719 | 122.9324 | -54.6616 | 68.1473 | -0.098725 | -0.00087374 | 0.062239 | 0.070327 | -0.0034714 | 0.0017645 | 0.0084124 | 0.0078126 | -0.00060665 | 0.0029906 | 0.0032642 | -1.0706e-05 | -0.0040845 | -0.00082886 | -51.9196 | 68.1519 | -54.7211 | 67.9276 | -54.0436 | -54.4785 | -53.9337 | -53.4668 | 68.1885 | -54.6982 | -54.4601 | -54.6249 | -54.7531 | -54.4556 | -0.059509 | 0.004577 | -0.21973 | 0.61798 | 0.72784 | 0.18311 | 0.78735 | 0.24261 | -0.036621 | 0.041199 | -122.6074 | 0.036621 | 0.20599 | -0.091553 | 0.24262 | -0.054932 | 0.67749 | 122.6486 | 0.073242 | 0.23804 | 122.8729 | 122.8867 | 122.8134 | 122.85 | -122.8683 | -122.8455 | 122.5891 | 0.20142 | 2.742 | 1.1948
3086.1719 | 122.9507 | -54.6707 | 68.1564 | -0.037689 | -0.00066014 | 0.061171 | 0.071181 | -0.0032578 | 0.0017645 | 0.0045672 | -0.11121 | 0.0013159 | 0.00064083 | 0.0062548 | -0.0017197 | -0.0081433 | -0.0038197 | -51.915 | 68.1381 | -54.7256 | 67.9138 | -54.0482 | -54.4785 | -53.9062 | -53.4027 | 68.1747 | -54.7165 | -54.4235 | -54.5929 | -54.7394 | -54.4373 | -0.054932 | -0.01831 | -0.24262 | 0.62256 | 0.76447 | 0.19226 | 0.8194 | 0.24719 | -0.045777 | 0.018311 | -122.58 | 0.077819 | 0.23346 | -0.068665 | 0.27924 | -0.022888 | 0.67749 | 122.6395 | 0.1236 | 0.29297 | 122.8638 | 122.8912 | 122.8088 | 122.8455 | -122.8821 | -122.8729 | 122.5845 | 0.24719 | 2.7557 | 1.268
3087.1719 | 122.9736 | -54.6707 | 68.1656 | -0.098725 | 0.00019446 | 0.061598 | 0.069686 | 0.001442 | 0.0017645 | 0.0056354 | 0.0047608 | 0.0015295 | 0.0014954 | -0.007417 | -0.0027877 | -0.0049389 | -0.0027515 | -51.915 | 68.1702 | -54.7165 | 67.9092 | -54.071 | -54.4922 | -53.9062 | -53.508 | 68.2159 | -54.689 | -54.4418 | -54.5837 | -54.7531 | -54.4235 | -0.045777 | 0.004578 | -0.25635 | 0.59967 | 0.76447 | 0.17853 | 0.81024 | 0.22431 | -0.018311 | 0.050354 | -122.6074 | 0.086975 | 0.24719 | -0.082398 | 0.2655 | -0.064087 | 0.64545 | 122.6257 | 0.10529 | 0.24719 | 122.8867 | 122.905 | 122.8409 | 122.8867 | -122.8821 | -122.8546 | 122.58 | 0.22888 | 2.7557 | 1.1627
3088.1719 | 122.9691 | -54.6661 | 68.1702 | -0.045319 | -0.00044654 | 0.062025 | 0.0699 | 0.0027238 | 0.0013373 | 0.0064898 | 0.0047608 | 0.00067495 | 0.0019226 | -0.0048536 | -0.0032151 | -0.0053663 | 0.0017345 | -51.8875 | 68.161 | -54.6982 | 67.9276 | -54.0436 | -54.4739 | -53.8925 | -53.4622 | 68.1931 | -54.689 | -54.4418 | -54.5929 | -54.744 | -54.4281 | -0.032043 | -0.009155 | -0.24262 | 0.62256 | 0.77362 | 0.19226 | 0.80566 | 0.2243 | -0.022888 | 0.022888 | -122.612 | 0.073242 | 0.23804 | -0.07782 | 0.26093 | -0.054932 | 0.6546 | 122.6257 | 0.09613 | 0.24719 | 122.8592 | 122.8821 | 122.8271 | 122.8592 | -122.8683 | -122.8592 | 122.5937 | 0.2243 | 2.7786 | 1.2039
3089.1719 | 122.9507 | -54.6524 | 68.1519 | -0.037689 | -0.0015145 | 0.061812 | 0.070113 | 0.0012284 | 0.0017645 | 0.0043536 | 0.023071 | 0.0038793 | 2.8e-08 | -0.002931 | -0.0023605 | -0.0038709 | -0.0016833 | -51.8875 | 68.1839 | -54.7028 | 67.9276 | -54.0344 | -54.4739 | -53.8879 | -53.4439 | 68.1976 | -54.6982 | -54.4189 | -54.57 | -54.7485 | -54.4144 | -0.050354 | 0.032044 | -0.2243 | 0.61798 | 0.76447 | 0.17853 | 0.81482 | 0.22888 | -0.045776 | 0.045777 | -122.5708 | 0.082398 | 0.23804 | -0.09613 | 0.28381 | -0.050354 | 0.66833 | 122.6303 | 0.12817 | 0.27924 | 122.8867 | 122.8958 | 122.8363 | 122.85 | -122.8546 | -122.85 | 122.58 | 0.23346 | 2.7649 | 1.2085
3090.1719 | 122.9828 | -54.657 | 68.161 | -0.037689 | 0.0016899 | 0.061171 | 0.068191 | 0.001442 | 0.0024053 | 0.0026446 | 0.062744 | 0.00067495 | 0.001068 | 0.00091422 | -0.0036423 | -0.0057935 | -0.00040166 | -51.8967 | 68.1656 | -54.7211 | 67.9138 | -54.0344 | -54.6387 | -53.9612 | -53.4164 | 68.2114 | -54.6707 | -54.4052 | -54.5837 | -54.7394 | -54.4464 | -0.064087 | 0.004577 | -0.24719 | 0.62256 | 0.6958 | 0.01831 | 0.75989 | 0.082397 | -0.013733 | 0.050354 | -122.5662 | 0.073242 | 0.21057 | -0.082398 | 0.2243 | -0.068665 | 0.68664 | 122.6349 | 0.086975 | 0.2655 | 122.8867 | 122.8821 | 122.8226 | 122.8683 | -122.8821 | -122.8317 | 122.5708 | 0.25177 | 2.7603 | 1.2405
3091.1719 | 122.9507 | -54.6478 | 68.1702 | -0.12924 | 0.00019446 | 0.061171 | 0.070327 | 0.0012284 | 0.0017645 | 0.005849 | -0.0013428 | 0.0015295 | 0.00042723 | -0.00229 | -0.0032151 | -0.0075025 | 0.0019483 | -51.8921 | 68.1564 | -54.7028 | 67.9321 | -54.0207 | -54.4693 | -53.8925 | -53.4668 | 68.1976 | -54.6753 | -54.3961 | -54.5654 | -54.7211 | -54.4144 | -0.054932 | -0.013733 | -0.23804 | 0.62714 | 0.75531 | 0.17853 | 0.81024 | 0.23346 | -0.027466 | 0.027466 | -122.5662 | 0.082397 | 0.23346 | -0.073242 | 0.26093 | -0.045776 | 0.68207 | 122.6349 | 0.10986 | 0.27924 | 122.8592 | 122.8729 | 122.8043 | 122.8455 | -122.8729 | -122.8455 | 122.58 | 0.25177 | 2.7557 | 1.181
3092.1719 | 122.9507 | -54.6478 | 68.1702 | -0.083466 | -1.9142e-05 | 0.060103 | 0.069686 | 0.0055008 | 0.0024053 | 0.0052082 | 0.016968 | 0.00024775 | -0.00021357 | -0.001222 | -0.00022431 | -0.0081433 | 0.00023934 | -51.8417 | 68.1656 | -54.7119 | 67.9413 | -54.007 | -54.4601 | -53.8834 | -53.4485 | 68.2068 | -54.7028 | -54.4189 | -54.5883 | -54.8218 | -54.5197 | -0.064087 | -0.004578 | -0.22888 | 0.64087 | 0.76447 | 0.18768 | 0.82855 | 0.25177 | -0.054932 | 0.036621 | -122.5891 | 0.059509 | 0.12817 | -0.17395 | 0.18311 | -0.11902 | 0.70496 | 122.6532 | 0.11444 | 0.28381 | 122.8775 | 122.9095 | 122.8134 | 122.8546 | -122.8821 | -122.8729 | 122.5891 | 0.22888 | 2.8061 | 1.1993
3093.1719 | 122.9599 | -54.6249 | 68.2114 | -0.060578 | 0.00062166 | 0.060103 | 0.068404 | 0.0022964 | 0.0013373 | 0.002431 | 0.032227 | 0.0011023 | 0.003418 | -0.00036738 | -0.0042831 | -0.0042981 | 0.00066654 | -51.8967 | 68.2159 | -54.6982 | 67.9184 | -54.0802 | -54.4556 | -53.8971 | -53.4851 | 68.2068 | -54.6616 | -54.4418 | -54.5471 | -54.7211 | -54.4281 | -0.073242 | 0.004577 | -0.29297 | 0.54474 | 0.72784 | 0.16937 | 0.80109 | 0.24262 | -0.036621 | -0.004578 | -122.6532 | 0.07782 | 0.19684 | -0.09613 | 0.23346 | -0.059509 | 0.61798 | 122.6166 | 0.11444 | 0.21973 | 122.9141 | 122.8683 | 122.8409 | 122.8317 | -122.9095 | -122.8729 | 122.5433 | 0.18311 | 2.7283 | 1.1398
3094.1719 | 122.9736 | -54.6295 | 68.2068 | -0.052948 | -0.00023294 | 0.059889 | 0.069259 | -0.00069423 | 0.0015509 | 0.005849 | 0.026123 | 0.0038793 | 0.0021362 | -0.00015378 | -0.0023605 | -0.0038709 | 0.0034435 | -51.8784 | 68.2159 | -54.6936 | 67.9047 | -54.0619 | -54.4647 | -53.9017 | -53.4943 | 68.2343 | -54.6341 | -54.4373 | -54.5471 | -54.7073 | -54.4235 | -0.064087 | 0.009155 | -0.30212 | 0.56763 | 0.72785 | 0.16479 | 0.79193 | 0.22888 | -0.004577 | 0.027466 | -122.644 | 0.082398 | 0.20599 | -0.077819 | 0.21057 | -0.073242 | 0.63171 | 122.5983 | 0.086975 | 0.19684 | 122.9095 | 122.8683 | 122.8455 | 122.8638 | -122.9004 | -122.8409 | 122.5342 | 0.19226 | 2.7512 | 1.1353
3095.1719 | 122.9233 | -54.6387 | 68.1839 | -0.13687 | -0.00023294 | 0.063734 | 0.072463 | -0.00026703 | 0.00048269 | 0.00414 | -0.01355 | 0.0021703 | 0.00085443 | -0.001222 | -0.0027877 | -0.0060071 | 0.00045294 | -51.9379 | 68.1793 | -54.7211 | 68.0649 | -54.0802 | -54.5975 | -53.9291 | -53.5217 | 68.2022 | -54.6982 | -54.4556 | -54.6295 | -54.7806 | -54.451 | -0.082397 | -0.004578 | -0.11902 | 0.55847 | 0.70953 | 0.041199 | 0.79193 | 0.1236 | -0.059509 | 0.01831 | -122.6395 | 0.009155 | 0.18768 | -0.14191 | 0.24719 | -0.082398 | 0.64087 | 122.7859 | 0.068664 | 0.24262 | 122.9004 | 122.9004 | 122.818 | 122.8409 | -122.905 | -122.8821 | 122.7036 | 0.18311 | 2.7008 | 1.1169
3096.1719 | 122.9645 | -54.6249 | 68.2205 | -0.075836 | -1.9142e-05 | 0.061598 | 0.069045 | -0.0021896 | 0.0013373 | 0.0060626 | 0.0078126 | 0.0013159 | 0.0014954 | -0.0035718 | -0.0021469 | -0.0051527 | -0.0016833 | -51.8555 | 68.2205 | -54.6799 | 67.9413 | -54.0207 | -54.4281 | -53.8651 | -53.4622 | 68.2571 | -54.6478 | -54.3961 | -54.5425 | -54.7119 | -54.3961 | -0.054932 | 0 | -0.27924 | 0.60425 | 0.75989 | 0.19684 | 0.81482 | 0.25177 | -0.022888 | 0.036621 | -122.6166 | 0.082397 | 0.22888 | -0.086975 | 0.25177 | -0.064087 | 0.65918 | 122.6212 | 0.10529 | 0.25177 | 122.9004 | 122.905 | 122.8455 | 122.8821 | -122.9004 | -122.8683 | 122.5662 | 0.22888 | 2.7695 | 1.1627
3097.1719 | 122.9874 | -54.6021 | 68.2343 | -0.075836 | -0.00066014 | 0.061171 | 0.068832 | 0.00058737 | 0.0034735 | 0.0026446 | 0.023071 | 0.0011023 | 0.00042723 | -0.00036738 | -0.0025741 | -0.0045117 | 0.00088014 | -51.8692 | 68.2251 | -54.657 | 67.9367 | -54.0482 | -54.4327 | -53.8651 | -53.4576 | 68.2251 | -54.6433 | -54.3961 | -54.5197 | -54.7028 | -54.3961 | -0.054931 | -0.009155 | -0.29755 | 0.55389 | 0.737 | 0.16937 | 0.79193 | 0.2243 | -0.041199 | -0.009155 | -122.6303 | 0.082398 | 0.20599 | -0.10071 | 0.24719 | -0.059509 | 0.60882 | 122.5937 | 0.1236 | 0.24719 | 122.8821 | 122.8683 | 122.8271 | 122.8271 | -122.8912 | -122.8775 | 122.5388 | 0.20599 | 2.7328 | 1.1444
3098.1719 | 122.9645 | -54.6158 | 68.2114 | -0.014801 | -0.00087374 | 0.061171 | 0.070113 | -0.00069423 | 0.0017645 | 0.00414 | 0.013916 | -0.00060665 | 0.002777 | -0.0031446 | -0.00065151 | -0.0051527 | 0.0013073 | -51.86 | 68.2343 | -54.6707 | 67.9276 | -54.039 | -54.4373 | -53.8696 | -53.4668 | 68.2343 | -54.6616 | -54.4098 | -54.5197 | -54.689 | -54.4098 | -0.054931 | 0.022888 | -0.28381 | 0.57678 | 0.74615 | 0.17853 | 0.80109 | 0.23346 | -0.045776 | 0.022888 | -122.6212 | 0.096131 | 0.20599 | -0.073242 | 0.25177 | -0.027466 | 0.63171 | 122.5983 | 0.14191 | 0.25177 | 122.905 | 122.8958 | 122.85 | 122.85 | -122.8821 | -122.8729 | 122.5433 | 0.20599 | 2.7557 | 1.149
3099.1719 | 122.9599 | -54.6066 | 68.2297 | -0.075836 | -0.00023294 | 0.060316 | 0.066909 | 0.0020828 | 0.0017645 | 0.0049946 | 0.026123 | 0.0013159 | 0.001709 | -0.0067762 | -0.0027877 | -0.0051527 | 0.0015209 | -51.8509 | 68.2297 | -54.6616 | 67.9321 | -54.0298 | -54.4601 | -53.8742 | -53.4714 | 68.2663 | -54.657 | -54.4098 | -54.538 | -54.6982 | -54.4189 | -0.054932 | 0 | -0.29755 | 0.57678 | 0.73242 | 0.14648 | 0.78735 | 0.20142 | -0.050354 | 0.036621 | -122.6395 | 0.068664 | 0.18768 | -0.091553 | 0.23804 | -0.041199 | 0.63171 | 122.5937 | 0.11902 | 0.24719 | 122.8912 | 122.9233 | 122.8363 | 122.8729 | -122.8912 | -122.8867 | 122.5388 | 0.19684 | 2.7557 | 1.1353
3100.1719 | 123.0377 | -54.6158 | 68.1839 | -0.083466 | 0.00083526 | 0.063307 | 0.065627 | -0.00026703 | 0.00048269 | 0.0017902 | 0.044434 | 0.0011023 | 0.00064083 | -0.0037854 | -0.0030013 | -0.0049389 | -0.0023243 | -51.8326 | 68.1381 | -54.6753 | 68.074 | -53.9932 | -54.4006 | -53.7781 | -53.3524 | 68.1747 | -54.6478 | -54.3137 | -54.4876 | -54.6616 | -54.3411 | -0.059509 | -0.045776 | -0.10986 | 0.62256 | 0.83771 | 0.21515 | 0.89722 | 0.27466 | -0.032043 | -0.009155 | -122.4976 | 0.12817 | 0.27466 | -0.045776 | 0.3067 | -0.013733 | 0.68207 | 122.7493 | 0.16022 | 0.33417 | 122.8134 | 122.8226 | 122.7539 | 122.7905 | -122.8592 | -122.8317 | 122.6898 | 0.30212 | 2.7832 | 1.2634
3101.1719 | 122.9462 | -54.6021 | 68.2526 | -0.037689 | -0.0015145 | 0.060316 | 0.069259 | 0.00058737 | -0.00015811 | 0.0054218 | 0.013916 | 0.0017431 | 0.00085443 | -0.0033582 | -0.0025741 | -0.0049389 | 0.00066654 | -51.8372 | 68.248 | -54.6341 | 67.9596 | -54.0207 | -54.4785 | -53.8925 | -53.4348 | 68.2571 | -54.6433 | -54.4189 | -54.5425 | -54.6982 | -54.4098 | -0.032043 | -0.004577 | -0.29297 | 0.58136 | 0.70953 | 0.1236 | 0.74158 | 0.15564 | -0.041199 | 0.004578 | -122.6715 | 0.059509 | 0.19226 | -0.09613 | 0.23346 | -0.054931 | 0.6134 | 122.5937 | 0.10071 | 0.22431 | 122.8821 | 122.9004 | 122.85 | 122.8592 | -122.8867 | -122.8958 | 122.5616 | 0.18311 | 2.7649 | 1.1673
3102.1719 | 122.937 | -54.5975 | 68.2297 | -0.052948 | -0.0017281 | 0.059248 | 0.068618 | 0.00037377 | 0.0013373 | 0.0039264 | -0.016602 | 0.00046135 | 0.0032044 | -0.0044262 | -0.0025741 | -0.0066479 | -0.0014697 | -51.8463 | 68.2251 | -54.6844 | 67.9367 | -54.039 | -54.4464 | -53.8742 | -53.4668 | 68.2526 | -54.657 | -54.3869 | -54.5242 | -54.7119 | -54.4006 | -0.086975 | -0.004577 | -0.29297 | 0.55847 | 0.72327 | 0.15106 | 0.81024 | 0.23804 | -0.059509 | 0.022888 | -122.6166 | 0.073242 | 0.19684 | -0.11444 | 0.25635 | -0.054932 | 0.64545 | 122.6212 | 0.13275 | 0.27008 | 122.9095 | 122.9095 | 122.8226 | 122.85 | -122.9141 | -122.8867 | 122.5342 | 0.21057 | 2.7512 | 1.1307
3103.1719 | 122.9599 | -54.5929 | 68.248 | -0.014801 | 0.00040806 | 0.059462 | 0.069472 | -0.0028304 | 0.0024053 | 0.0045672 | 0.0078126 | 0.0025975 | 0.00064083 | -0.00229 | -0.0015061 | -0.0055799 | -0.0021107 | -51.8326 | 68.2297 | -54.657 | 67.9321 | -54.0253 | -54.451 | -53.8788 | -53.4714 | 68.2526 | -54.6295 | -54.4052 | -54.5517 | -54.7211 | -54.4098 | -0.064086 | -0.018311 | -0.31586 | 0.56763 | 0.71411 | 0.14191 | 0.7782 | 0.20599 | -0.036621 | 0.004577 | -122.6532 | 0.041199 | 0.18311 | -0.12817 | 0.21973 | -0.091552 | 0.63171 | 122.5891 | 0.07782 | 0.22431 | 122.8867 | 122.8821 | 122.8226 | 122.8455 | -122.905 | -122.8775 | 122.525 | 0.18768 | 2.7603 | 1.1215
3104.1719 | 122.9233 | -54.6295 | 68.2526 | -0.098725 | -0.00044654 | 0.060103 | 0.070327 | 0.00037377 | 0.0034735 | 0.0052082 | 0.0078126 | 0.0015295 | -0.00042717 | 5.9824e-05 | 0.00041649 | -0.0057935 | -0.0014697 | -51.8372 | 68.2526 | -54.6799 | 67.9138 | -53.9795 | -54.4693 | -53.9062 | -53.4531 | 68.28 | -54.6204 | -54.4144 | -54.538 | -54.7119 | -54.4006 | -0.050354 | 0 | -0.33874 | 0.65002 | 0.72327 | 0.16022 | 0.77362 | 0.21057 | 0.009156 | 0.027466 | -122.6669 | 0.091553 | 0.22888 | -0.082397 | 0.21973 | -0.091553 | 0.70038 | 122.5937 | 0.082397 | 0.20599 | 122.9324 | 122.9004 | 122.8821 | 122.9095 | -122.9324 | -122.8729 | 122.5433 | 0.21515 | 2.7924 | 1.1765
3105.1719 | 122.9462 | -54.6204 | 68.1747 | -0.091095 | -1.9142e-05 | 0.060744 | 0.0699 | 0.0037918 | 0.0030463 | 0.0071308 | -0.034912 | 0.0019567 | -0.0010682 | 0.0041186 | -0.0019333 | -0.0068615 | -0.0014697 | -51.9379 | 68.1656 | -54.7394 | 67.9184 | -54.0253 | -54.5197 | -53.9017 | -53.4988 | 68.2205 | -54.657 | -54.4235 | -54.5929 | -54.7577 | -54.4235 | -0.11902 | -0.009156 | -0.25635 | 0.59509 | 0.71869 | 0.10071 | 0.83771 | 0.21973 | -0.036621 | 0.045776 | -122.5983 | 0.027465 | 0.19684 | -0.13733 | 0.23346 | -0.10071 | 0.71411 | 122.6578 | 0.064086 | 0.23346 | 122.905 | 122.8775 | 122.7859 | 122.8409 | -122.9141 | -122.8317 | 122.5388 | 0.19684 | 2.6825 | 1.1215
3106.1719 | 122.9187 | -54.5975 | 68.2434 | -0.052948 | 0.00062166 | 0.061385 | 0.068832 | -0.0024032 | 0.0026191 | 0.0047808 | 0.016968 | 0.0015295 | -0.00042717 | -0.005708 | -0.0023605 | -0.0062207 | 0.0019483 | -51.9516 | 68.2434 | -54.6753 | 67.9504 | -54.0253 | -54.4327 | -53.8467 | -53.4622 | 68.2938 | -54.6387 | -54.3915 | -54.5242 | -54.6982 | -54.4052 | -0.07782 | 0 | -0.29297 | 0.5722 | 0.75073 | 0.16479 | 0.82855 | 0.24262 | -0.041199 | 0.050354 | -122.6349 | 0.073242 | 0.19226 | -0.10071 | 0.23346 | -0.059509 | 0.65002 | 122.6257 | 0.11444 | 0.24719 | 122.9187 | 122.9324 | 122.8409 | 122.8912 | -122.9187 | -122.8821 | 122.5479 | 0.20599 | 2.6459 | 1.1353
3107.1719 | 122.9187 | -54.6158 | 68.2434 | -0.045319 | 0.00019446 | 0.060744 | 0.068191 | 0.0020828 | 0.0039007 | 0.0047808 | 0.044434 | -0.00039305 | 0.00042723 | -0.00229 | -0.0032151 | -0.0042981 | -0.0021107 | -51.7822 | 68.2297 | -54.6341 | 68.0237 | -53.9658 | -54.3777 | -53.8101 | -53.4256 | 68.2755 | -54.6112 | -54.3961 | -54.5471 | -54.6661 | -54.3869 | -0.01831 | -0.013733 | -0.21973 | 0.65002 | 0.80566 | 0.23804 | 0.82397 | 0.25635 | 0.004578 | 0.032044 | -122.6395 | 0.068665 | 0.22888 | -0.050354 | 0.2243 | -0.054932 | 0.66833 | 122.6578 | 0.064087 | 0.21515 | 122.8638 | 122.8867 | 122.8455 | 122.8912 | -122.8775 | -122.8546 | 122.6395 | 0.21973 | 2.8336 | 1.1902
3108.1719 | 122.9782 | -54.57 | 68.2571 | -0.052948 | -1.9142e-05 | 0.061171 | 0.068618 | -0.00069423 | 0.0026191 | 0.0022174 | 0.044434 | 0.0015295 | 0.00064083 | -0.0016492 | -0.0049241 | -0.0089979 | -0.0021107 | -51.7456 | 68.2114 | -54.6066 | 68.0511 | -53.9062 | -54.3365 | -53.7643 | -53.3432 | 68.28 | -54.5883 | -54.332 | -54.4647 | -54.6249 | -54.3457 | -0.036621 | -0.045776 | -0.20599 | 0.66376 | 0.80566 | 0.23346 | 0.84229 | 0.27008 | -0.018311 | 0.022888 | -122.5891 | 0.10528 | 0.2243 | -0.054932 | 0.24262 | -0.036621 | 0.70038 | 122.6578 | 0.1236 | 0.25635 | 122.818 | 122.8683 | 122.7814 | 122.85 | -122.8638 | -122.8455 | 122.6212 | 0.23804 | 2.8244 | 1.2268
3109.1719 | 122.937 | -54.5929 | 68.2617 | -0.045319 | 0.0019035 | 0.059035 | 0.068191 | 0.0010148 | 0.0028327 | 0.0049946 | 0.044434 | 0.0011023 | 0.00085443 | -0.0033582 | -0.0025741 | -0.0055799 | 0.00023934 | -51.7548 | 68.248 | -54.6387 | 68.0099 | -53.9337 | -54.3732 | -53.8101 | -53.4119 | 68.2938 | -54.6112 | -54.3732 | -54.5151 | -54.6524 | -54.3915 | -0.045776 | -0.013733 | -0.25177 | 0.65918 | 0.78278 | 0.21973 | 0.82855 | 0.2655 | -0.01831 | 0.032043 | -122.6349 | 0.07782 | 0.20142 | -0.059509 | 0.21973 | -0.041199 | 0.70496 | 122.6486 | 0.09613 | 0.23804 | 122.8867 | 122.905 | 122.8409 | 122.8867 | -122.9004 | -122.8729 | 122.6028 | 0.21973 | 2.8381 | 1.181
3110.1719 | 122.9462 | -54.6021 | 68.2388 | -0.083466 | -0.00066014 | 0.062453 | 0.070754 | 0.001442 | 0.0017645 | 0.0052082 | -0.050171 | 0.0013159 | -0.00085457 | 0.0017688 | -0.0025741 | -0.0055799 | 0.0023755 | -51.8417 | 68.2159 | -54.6844 | 67.923 | -54.0619 | -54.5105 | -53.9154 | -53.7231 | 68.1656 | -54.6799 | -54.3915 | -54.5929 | -54.744 | -54.4006 | -0.082397 | -0.022889 | -0.31586 | 0.54016 | 0.68665 | 0.091553 | 0.76904 | 0.17395 | -0.07782 | -0.073243 | -122.6303 | 0.009155 | 0.20142 | -0.14191 | 0.27924 | -0.064087 | 0.62256 | 122.6074 | 0.086975 | 0.28839 | 122.9004 | 122.8455 | 122.818 | 122.7676 | -122.9233 | -122.9187 | 122.525 | 0.21057 | 2.7603 | 0.87891
3111.1719 | 123.0057 | -54.5517 | 68.2388 | -0.03006 | 0.0031851 | 0.06053 | 0.067763 | -0.0043258 | 0.0028327 | 0.0054218 | 0.041382 | -0.0010339 | 0.00064083 | -0.0050672 | -0.0032151 | -0.0060071 | 0.0019483 | -51.7227 | 68.2159 | -54.5975 | 68.0786 | -53.8742 | -54.3182 | -53.746 | -53.3066 | 68.2526 | -54.5792 | -54.2953 | -54.4144 | -54.5654 | -54.3045 | -0.045776 | -0.022889 | -0.16022 | 0.67749 | 0.80566 | 0.23346 | 0.85144 | 0.27924 | -0.027466 | 0.013732 | -122.5342 | 0.13733 | 0.24719 | -0.013733 | 0.27466 | 0.013733 | 0.72327 | 122.6761 | 0.16479 | 0.28381 | 122.8134 | 122.8317 | 122.7676 | 122.8043 | -122.8363 | -122.818 | 122.6303 | 0.25635 | 2.829 | 1.2451
3112.1719 | 123.0469 | -54.5105 | 68.2205 | -0.098725 | 0.00083526 | 0.061171 | 0.066909 | -0.004753 | 0.0060369 | 0.0047808 | 0.065796 | 3.4148e-05 | 0.0029906 | -0.003999 | -0.0025741 | -0.0064343 | -0.0021107 | -51.7273 | 68.2068 | -54.5883 | 67.9871 | -53.7781 | -54.2908 | -53.7735 | -53.2837 | 68.2388 | -54.5654 | -54.2587 | -54.3869 | -54.5517 | -54.2953 | -0.07782 | -0.013733 | -0.23346 | 0.73242 | 0.737 | 0.21973 | 0.81482 | 0.29755 | -0.054932 | 0.018311 | -122.4792 | 0.1236 | 0.21515 | -0.041199 | 0.27008 | 0.013733 | 0.81024 | 122.5754 | 0.17853 | 0.3067 | 122.7951 | 122.8043 | 122.7173 | 122.7493 | -122.8088 | -122.7859 | 122.4976 | 0.25177 | 2.7832 | 1.2268
3113.1719 | 123.0469 | -54.5425 | 68.2526 | -0.075836 | 0.0033987 | 0.062453 | 0.067336 | 0.003151 | 0.0013373 | 0.0073444 | 0.016968 | 3.4148e-05 | 0.0012818 | 0.003905 | -0.0034287 | -0.0057935 | 0.00045294 | -51.7044 | 68.2205 | -54.5837 | 68.1152 | -53.8651 | -54.3228 | -53.7323 | -53.27 | 68.2526 | -54.5792 | -54.2862 | -54.3823 | -54.5517 | -54.2908 | -0.041198 | -0.032043 | -0.13733 | 0.67749 | 0.81024 | 0.21973 | 0.85144 | 0.26093 | -0.036621 | 0 | -122.5388 | 0.16022 | 0.25177 | -0.009155 | 0.28839 | 0.027466 | 0.71869 | 122.699 | 0.19684 | 0.29297 | 122.8043 | 122.8317 | 122.7631 | 122.7951 | -122.8363 | -122.8317 | 122.6578 | 0.25635 | 2.8381 | 1.2726
3114.1719 | 123.1018 | -54.5471 | 68.2388 | -0.11398 | 0.00062166 | 0.060316 | 0.068832 | 0.00037377 | 0.00026909 | 0.0034992 | 0.053589 | 0.00024775 | 0.0012818 | -0.0018628 | -0.0025741 | -0.0068615 | -0.0018971 | -51.7456 | 68.2388 | -54.5883 | 68.1061 | -53.8467 | -54.2999 | -53.7277 | -53.2516 | 68.2709 | -54.5609 | -54.2496 | -54.3915 | -54.4968 | -54.245 | -0.041199 | 0 | -0.13275 | 0.70038 | 0.8194 | 0.24719 | 0.8606 | 0.28839 | -0.013733 | 0.032043 | -122.4884 | 0.15564 | 0.30212 | 0.050354 | 0.31586 | 0.064087 | 0.74158 | 122.6944 | 0.16937 | 0.31128 | 122.8271 | 122.8317 | 122.786 | 122.818 | -122.8271 | -122.7997 | 122.6532 | 0.29755 | 2.8015 | 1.2955
3115.1719 | 123.0789 | -54.5425 | 68.248 | -0.1445 | 0.00040806 | 0.059035 | 0.070541 | 0.0022964 | 0.0030463 | 0.0039264 | 0.029175 | 0.0011023 | 0.0023498 | 5.9824e-05 | -0.0034287 | -0.0068615 | 0.00045294 | -51.741 | 68.2159 | -54.6066 | 68.074 | -53.9017 | -54.3274 | -53.7506 | -53.3112 | 68.2617 | -54.5837 | -54.2587 | -54.3915 | -54.538 | -54.2816 | -0.064086 | -0.032044 | -0.17395 | 0.64087 | 0.79193 | 0.21515 | 0.85602 | 0.27923 | -0.041198 | 0.013733 | -122.5067 | 0.15106 | 0.26093 | 0.004578 | 0.30212 | 0.045776 | 0.70496 | 122.6807 | 0.19226 | 0.32501 | 122.8226 | 122.8455 | 122.7585 | 122.8043 | -122.8546 | -122.8317 | 122.6166 | 0.28381 | 2.8015 | 1.2314
3116.1719 | 123.0835 | -54.5288 | 68.2114 | -0.098725 | -0.00023294 | 0.059462 | 0.067977 | -5.343e-05 | 0.0026191 | 0.0034992 | 0.044434 | -0.0012477 | 0.001709 | -0.0020764 | -0.0027877 | -0.0057935 | 0.0025891 | -51.709 | 68.2434 | -54.6112 | 68.1015 | -53.8513 | -54.3045 | -53.7186 | -53.2562 | 68.2526 | -54.5792 | -54.2496 | -54.3594 | -54.5242 | -54.2496 | -0.082397 | 0.032043 | -0.10986 | 0.67749 | 0.81024 | 0.22431 | 0.89264 | 0.3067 | -0.050354 | 0.041198 | -122.4609 | 0.16937 | 0.27924 | 0.004578 | 0.32959 | 0.054932 | 0.75989 | 122.7127 | 0.21973 | 0.32959 | 122.8546 | 122.8317 | 122.7722 | 122.7814 | -122.8226 | -122.7905 | 122.6303 | 0.27924 | 2.8198 | 1.2726
3117.1719 | 123.0515 | -54.538 | 68.248 | -0.068207 | -1.9142e-05 | 0.061171 | 0.068618 | -0.0028304 | 0.0034735 | 0.007558 | 0.032227 | 3.4148e-05 | 2.8e-08 | -0.00015378 | -0.0019333 | -0.0057935 | -0.0023243 | -51.7319 | 68.2388 | -54.5975 | 68.074 | -53.8834 | -54.3091 | -53.7323 | -53.2974 | 68.2709 | -54.57 | -54.2679 | -54.3823 | -54.5517 | -54.2679 | -0.059509 | -0.009155 | -0.17395 | 0.6546 | 0.80566 | 0.22888 | 0.86517 | 0.28839 | -0.032043 | 0.022888 | -122.5159 | 0.15564 | 0.27008 | -0.013733 | 0.30212 | 0.01831 | 0.71411 | 122.6715 | 0.18768 | 0.30212 | 122.8363 | 122.8409 | 122.7768 | 122.8088 | -122.8455 | -122.818 | 122.612 | 0.27008 | 2.8061 | 1.2405
3118.1719 | 123.024 | -54.5563 | 68.2297 | -0.12161 | 0.0012625 | 0.061598 | 0.069686 | -0.0038986 | 5.5488e-05 | 0.0060626 | 0.0078126 | -0.0010339 | 0.0019226 | 0.00091422 | -0.0036423 | -0.0075025 | 0.00045294 | -51.7685 | 68.2571 | -54.5929 | 68.0511 | -53.92 | -54.3686 | -53.7598 | -53.3295 | 68.2709 | -54.5746 | -54.2908 | -54.4006 | -54.57 | -54.2816 | -0.036622 | 0.027466 | -0.17853 | 0.63629 | 0.79651 | 0.18768 | 0.83313 | 0.22431 | -0.018311 | 0.041199 | -122.5204 | 0.15564 | 0.27466 | -0.013733 | 0.29297 | 0.004578 | 0.67291 | 122.644 | 0.17395 | 0.28381 | 122.85 | 122.8455 | 122.8134 | 122.8271 | -122.8226 | -122.8043 | 122.6074 | 0.2655 | 2.7878 | 1.2268
3119.1719 | 123.0469 | -54.5288 | 68.248 | -0.083466 | 0.00083526 | 0.062025 | 0.068832 | -0.0021896 | 0.0013373 | 0.0064898 | 0.010864 | 0.0015295 | -0.00085457 | -0.0052808 | -0.0042831 | -0.0057935 | 0.00023934 | -51.7273 | 68.2343 | -54.5975 | 68.0969 | -53.8879 | -54.3274 | -53.7231 | -53.302 | 68.2709 | -54.5792 | -54.2358 | -54.364 | -54.5425 | -54.2542 | -0.068664 | -0.013733 | -0.15106 | 0.64087 | 0.80566 | 0.20142 | 0.87433 | 0.27008 | -0.050354 | 0.022888 | -122.4838 | 0.1648 | 0.27466 | -0.013733 | 0.32501 | 0.036621 | 0.70953 | 122.6944 | 0.21515 | 0.34332 | 122.8317 | 122.85 | 122.7631 | 122.7997 | -122.8455 | -122.8271 | 122.6257 | 0.29297 | 2.8015 | 1.2268
3120.1719 | 123.0423 | -54.5288 | 68.2251 | -0.11398 | -0.0013009 | 0.059889 | 0.070754 | -0.00048063 | 0.0011237 | 0.0045672 | 0.010864 | -0.00039305 | -0.00021357 | -0.0010084 | -0.0023605 | -0.0047253 | -0.00018806 | -51.7364 | 68.28 | -54.5792 | 68.0695 | -53.92 | -54.3549 | -53.7415 | -53.3295 | 68.2709 | -54.57 | -54.2679 | -54.4052 | -54.5563 | -54.277 | -0.050354 | 0.054931 | -0.15564 | 0.60883 | 0.78735 | 0.17395 | 0.83771 | 0.22431 | -0.041198 | 0.045776 | -122.493 | 0.1236 | 0.25177 | -0.027465 | 0.29297 | 0.013733 | 0.65918 | 122.6486 | 0.16479 | 0.30212 | 122.8592 | 122.8409 | 122.8088 | 122.7997 | -122.8043 | -122.7951 | 122.5983 | 0.26093 | 2.7924 | 1.1993
3121.1719 | 123.0103 | -54.5517 | 68.248 | -0.091095 | 0.0010489 | 0.061385 | 0.070541 | -0.0011214 | 0.0032599 | 0.0043536 | -0.025757 | 0.0032385 | -0.00064077 | 5.9824e-05 | -0.0038559 | -0.0068615 | 0.0030163 | -51.7456 | 68.2205 | -54.5929 | 68.0603 | -53.9154 | -54.3686 | -53.7781 | -53.3386 | 68.2571 | -54.5975 | -54.2679 | -54.4327 | -54.6066 | -54.3091 | -0.041199 | -0.027466 | -0.18768 | 0.63629 | 0.77362 | 0.18311 | 0.81482 | 0.22431 | -0.045776 | 0.009155 | -122.5159 | 0.11902 | 0.24262 | -0.054931 | 0.28839 | -0.009155 | 0.67749 | 122.6532 | 0.16479 | 0.32959 | 122.8134 | 122.8546 | 122.7722 | 122.8088 | -122.8409 | -122.8455 | 122.612 | 0.28381 | 2.8061 | 1.2131
3122.1719 | 123.0103 | -54.5288 | 68.2159 | -0.15213 | 0.00019446 | 0.063521 | 0.070754 | 0.00080117 | 0.00048269 | 0.0060626 | -0.044067 | 0.0021703 | 0.00064083 | -0.0031446 | -0.0030013 | -0.0049389 | -0.00040166 | -51.7136 | 68.2022 | -54.5837 | 68.074 | -53.8879 | -54.364 | -53.7689 | -53.3249 | 68.2617 | -54.5883 | -54.2862 | -54.4281 | -54.5929 | -54.2908 | -0.054931 | -0.013733 | -0.14191 | 0.64087 | 0.75989 | 0.1648 | 0.81482 | 0.21973 | -0.059509 | 0.045777 | -122.5021 | 0.10071 | 0.23804 | -0.064087 | 0.29755 | -0.004578 | 0.6958 | 122.6578 | 0.16022 | 0.30212 | 122.7859 | 122.85 | 122.731 | 122.7905 | -122.7997 | -122.8043 | 122.6028 | 0.24262 | 2.8152 | 1.2039
3123.1719 | 123.0011 | -54.5288 | 68.2159 | -0.075836 | -1.9142e-05 | 0.062239 | 0.067977 | 0.0010148 | 0.0024053 | 0.0067036 | 0.0047608 | -0.00039305 | -0.00085457 | 0.0024096 | -0.0036423 | -0.0062207 | 0.0013073 | -51.741 | 68.2343 | -54.6204 | 68.074 | -53.9108 | -54.3777 | -53.7643 | -53.3249 | 68.2755 | -54.5792 | -54.2542 | -54.4281 | -54.5837 | -54.2999 | -0.091552 | 0.018311 | -0.14191 | 0.61798 | 0.76447 | 0.15106 | 0.85602 | 0.24261 | -0.050354 | 0.05951 | -122.4701 | 0.10071 | 0.22888 | -0.054931 | 0.27924 | -0.004577 | 0.70953 | 122.6944 | 0.15106 | 0.32501 | 122.8546 | 122.8546 | 122.7631 | 122.8043 | -122.8363 | -122.7951 | 122.6028 | 0.27466 | 2.7878 | 1.2039
3124.1719 | 122.9965 | -54.5334 | 68.2343 | -0.045319 | 0.0019035 | 0.063521 | 0.070327 | 0.001442 | 0.0028327 | 0.0062762 | -0.010498 | 0.0011023 | 0.00042723 | -0.0025036 | -0.0027877 | -0.0060071 | -0.0018971 | -51.7273 | 68.2251 | -54.5746 | 68.0649 | -53.8834 | -54.3549 | -53.7506 | -53.3157 | 68.2663 | -54.5929 | -54.2633 | -54.4235 | -54.5975 | -54.2862 | -0.041199 | -0.009155 | -0.16937 | 0.65002 | 0.78278 | 0.17853 | 0.82397 | 0.21973 | -0.05951 | 0.032043 | -122.4976 | 0.10986 | 0.24719 | -0.064087 | 0.3067 | -0.004577 | 0.69122 | 122.6395 | 0.16937 | 0.32959 | 122.7997 | 122.8592 | 122.7585 | 122.7997 | -122.8088 | -122.8271 | 122.5983 | 0.27008 | 2.8061 | 1.2177
3125.1719 | 122.9965 | -54.5288 | 68.2388 | -0.091095 | 0.00062166 | 0.062025 | 0.068832 | -0.001976 | 0.00069649 | 0.0079852 | -0.025757 | -0.00082025 | -0.00042717 | -0.00079478 | -0.0017197 | -0.0053663 | 0.0010937 | -51.6953 | 68.2571 | -54.57 | 68.1015 | -53.8467 | -54.3411 | -53.7369 | -53.2883 | 68.2571 | -54.5654 | -54.2404 | -54.4006 | -54.5746 | -54.277 | -0.041198 | 0.01831 | -0.13733 | 0.68207 | 0.79193 | 0.18768 | 0.83313 | 0.22888 | -0.036621 | 0.01831 | -122.4792 | 0.12817 | 0.25177 | -0.045776 | 0.28839 | -0.009155 | 0.72327 | 122.6715 | 0.16479 | 0.32501 | 122.8271 | 122.8226 | 122.786 | 122.786 | -122.8088 | -122.8043 | 122.6303 | 0.28839 | 2.8336 | 1.2405
3126.1719 | 123.0377 | -54.5151 | 68.2343 | -0.037689 | 0.00019446 | 0.062239 | 0.068832 | 0.0063554 | 0.00091009 | 0.0052082 | -0.041016 | 0.0021703 | -0.001709 | -0.00036738 | -0.0019333 | -0.0064343 | -0.0014697 | -51.6907 | 68.2205 | -54.5609 | 68.1152 | -53.8422 | -54.3365 | -53.7369 | -53.2654 | 68.28 | -54.5746 | -54.2175 | -54.3915 | -54.5792 | -54.2542 | -0.045776 | -0.013733 | -0.11902 | 0.67291 | 0.7782 | 0.17853 | 0.82397 | 0.2243 | -0.059509 | 0.045776 | -122.4518 | 0.1236 | 0.26093 | -0.064087 | 0.32043 | -0.004578 | 0.71869 | 122.6761 | 0.18311 | 0.35706 | 122.7814 | 122.8546 | 122.7356 | 122.7951 | -122.7951 | -122.8088 | 122.6303 | 0.29755 | 2.8244 | 1.2497
3127.1719 | 123.0011 | -54.4968 | 68.2388 | -0.17502 | -0.0019417 | 0.060316 | 0.069259 | -0.001976 | 0.0032599 | 0.0062762 | -0.025757 | 0.0013159 | -0.00085457 | -0.0067762 | -0.00086511 | -0.0064343 | 0.0021619 | -51.6907 | 68.2159 | -54.5425 | 68.0969 | -53.8467 | -54.3365 | -53.7415 | -53.2791 | 68.2892 | -54.5563 | -54.2587 | -54.4235 | -54.5792 | -54.2725 | -0.045777 | -0.022889 | -0.14191 | 0.65002 | 0.75531 | 0.16022 | 0.80109 | 0.20599 | -0.059509 | 0.050354 | -122.4976 | 0.073242 | 0.2243 | -0.082398 | 0.28381 | -0.022889 | 0.6958 | 122.6395 | 0.13275 | 0.29755 | 122.7585 | 122.8455 | 122.7127 | 122.786 | -122.7814 | -122.7951 | 122.5937 | 0.23804 | 2.8061 | 1.2177
3128.1719 | 123.0331 | -54.5197 | 68.2343 | -0.10635 | -0.0013009 | 0.063307 | 0.069259 | -5.343e-05 | 0.0043281 | 0.0056354 | -0.03186 | -0.0014613 | -0.0021362 | -0.0025036 | -0.0040695 | -0.0083569 | -0.0010425 | -51.6678 | 68.2343 | -54.5609 | 68.1107 | -53.8422 | -54.3365 | -53.9154 | -53.1189 | 68.2983 | -54.5288 | -54.2038 | -54.3869 | -54.5517 | -54.2496 | -0.041199 | 0 | -0.1236 | 0.67749 | 0.60425 | 0.1831 | 0.64545 | 0.2243 | -0.009156 | 0.064087 | -122.438 | 0.13275 | 0.27008 | -0.032044 | 0.27924 | -0.022888 | 0.71869 | 122.6715 | 0.14191 | 0.32501 | 122.7951 | 122.8271 | 122.7539 | 122.818 | -122.7951 | -122.7631 | 122.6303 | 0.31586 | 2.8519 | 1.4008
3129.1719 | 123.1064 | -54.5288 | 68.2297 | -0.12161 | 0.0016899 | 0.063307 | 0.069472 | 0.001442 | 0.0034735 | 0.0054218 | -0.056274 | 0.0011023 | -0.00085457 | -0.00036738 | -0.0021469 | -0.0042981 | -0.0021107 | -51.6907 | 68.2251 | -54.5746 | 68.1244 | -53.8422 | -54.2999 | -53.7277 | -53.27 | 68.2846 | -54.5609 | -54.1992 | -54.3457 | -54.7943 | -54.3549 | -0.045776 | -0.004577 | -0.10528 | 0.68665 | 0.80109 | 0.22888 | 0.84686 | 0.27466 | -0.032043 | 0.054932 | -122.4289 | 0.18311 | 0.17395 | -0.2655 | 0.20599 | -0.23346 | 0.73242 | 122.699 | 0.21515 | 0.36163 | 122.7997 | 122.8455 | 122.7539 | 122.8134 | -122.8043 | -122.7905 | 122.6532 | 0.32959 | 2.8381 | 1.2589
3130.1719 | 123.0194 | -54.5013 | 68.2617 | -0.15976 | 0.0012625 | 0.064162 | 0.069259 | -0.0011214 | 0.00026909 | 0.0052082 | -0.037964 | 3.4148e-05 | 0.00085443 | 0.00070062 | -0.0012925 | -0.0051527 | -0.0036059 | -51.6815 | 68.2434 | -54.5563 | 68.1107 | -53.8147 | -54.245 | -53.6957 | -53.2562 | 68.2983 | -54.538 | -54.1901 | -54.3686 | -54.5425 | -54.2404 | -0.054931 | -0.018311 | -0.15106 | 0.68665 | 0.80566 | 0.25635 | 0.8606 | 0.31128 | -0.036621 | 0.036621 | -122.4518 | 0.13275 | 0.26093 | -0.041199 | 0.29755 | -0.004578 | 0.74158 | 122.6669 | 0.16937 | 0.3479 | 122.7997 | 122.8363 | 122.7448 | 122.7997 | -122.818 | -122.7997 | 122.612 | 0.31128 | 2.8198 | 1.2451
3131.1719 | 123.0286 | -54.5013 | 68.2388 | -0.098725 | 0.00040806 | 0.062453 | 0.072677 | 0.0010148 | 0.0021917 | 0.0056354 | -0.098999 | 0.00024775 | -0.0023498 | 0.0060412 | -0.0023605 | -0.0042981 | -0.0029651 | -51.6632 | 68.2434 | -54.5746 | 68.1335 | -53.8239 | -54.3182 | -53.714 | -53.2288 | 68.2617 | -54.5517 | -54.1763 | -54.3594 | -54.5425 | -54.2267 | -0.073242 | 0.004577 | -0.10529 | 0.67749 | 0.78735 | 0.18311 | 0.8606 | 0.25635 | -0.050354 | 0.022888 | -122.4152 | 0.14191 | 0.27466 | -0.041199 | 0.32501 | 0.009155 | 0.75073 | 122.7081 | 0.19226 | 0.37537 | 122.818 | 122.8134 | 122.7448 | 122.7631 | -122.8134 | -122.7905 | 122.6349 | 0.32501 | 2.8381 | 1.2726
3132.1719 | 123.0423 | -54.5105 | 68.2434 | -0.13687 | 0.00019446 | 0.062666 | 0.069259 | -0.0034714 | 0.0043281 | 0.0067036 | -0.034912 | 0.00067495 | -0.001709 | -0.0052808 | -0.0038559 | -0.0047253 | 0.0021619 | -51.6449 | 68.2205 | -54.5334 | 68.1519 | -53.7964 | -54.2999 | -53.7048 | -53.2379 | 68.3075 | -54.5471 | -54.1855 | -54.3503 | -54.5563 | -54.2313 | -0.022888 | -0.022888 | -0.091553 | 0.71411 | 0.80566 | 0.21057 | 0.82855 | 0.23346 | -0.036621 | 0.064087 | -122.4289 | 0.16022 | 0.27924 | -0.045776 | 0.31586 | -0.009155 | 0.737 | 122.6852 | 0.19684 | 0.36163 | 122.7539 | 122.8546 | 122.731 | 122.818 | -122.7768 | -122.7905 | 122.6624 | 0.32501 | 2.8656 | 1.2726
3133.1719 | 123.0377 | -54.4876 | 68.248 | -0.11398 | -0.00066014 | 0.062239 | 0.070541 | -0.0045394 | 0.00048269 | 0.0086262 | -0.062378 | 0.0015295 | 0.00085443 | 0.0041186 | -0.0032151 | -0.0036573 | -0.0018971 | -51.6586 | 68.2617 | -54.538 | 68.0923 | -53.8376 | -54.3045 | -53.7323 | -53.2562 | 68.3258 | -54.5334 | -54.1946 | -54.364 | -54.5334 | -54.2267 | -0.050354 | 0.013733 | -0.15564 | 0.65002 | 0.75531 | 0.18311 | 0.80566 | 0.23346 | -0.045776 | 0.07782 | -122.4426 | 0.1236 | 0.26092 | -0.045776 | 0.3067 | 0 | 0.70038 | 122.6303 | 0.16937 | 0.33875 | 122.7997 | 122.8592 | 122.7493 | 122.8134 | -122.7859 | -122.7814 | 122.58 | 0.29297 | 2.829 | 1.2314
3134.1719 | 123.0469 | -54.4876 | 68.2755 | -0.10635 | 0.0036125 | 0.062453 | 0.068618 | 0.0027238 | 0.0032599 | 0.0032856 | -0.025757 | 0.0011023 | 0.00042723 | 0.001128 | -0.0049241 | -0.0055799 | 0.00066654 | -51.6312 | 68.2755 | -54.5517 | 68.1244 | -53.6819 | -54.126 | -53.7323 | -53.215 | 68.3212 | -54.5059 | -54.1718 | -54.3457 | -54.5197 | -54.2267 | -0.064087 | 0 | -0.15106 | 0.80566 | 0.75531 | 0.36163 | 0.8194 | 0.42572 | -0.01831 | 0.045776 | -122.4472 | 0.14191 | 0.26092 | -0.032043 | 0.27923 | -0.013733 | 0.86975 | 122.6761 | 0.16022 | 0.33417 | 122.8271 | 122.8271 | 122.7631 | 122.8088 | -122.8271 | -122.7814 | 122.612 | 0.31586 | 2.8564 | 1.2726
3135.1719 | 123.0011 | -54.4968 | 68.2571 | -0.075836 | 0.00083526 | 0.060957 | 0.071395 | -0.0015488 | 0.0036871 | 0.0054218 | -0.053223 | 0.00046135 | 0.00021363 | 0.00091422 | -0.0017197 | -0.0021619 | -0.00061526 | -51.6724 | 68.2983 | -54.57 | 68.0695 | -53.8925 | -54.332 | -53.7827 | -53.2791 | 68.3258 | -54.5563 | -54.1855 | -54.4006 | -54.5654 | -54.2358 | -0.073242 | 0.041199 | -0.18768 | 0.60425 | 0.71411 | 0.1648 | 0.78735 | 0.23804 | -0.059509 | 0.068665 | -122.4426 | 0.09613 | 0.26093 | -0.068665 | 0.32043 | -0.009156 | 0.67749 | 122.6395 | 0.15564 | 0.37079 | 122.8683 | 122.8821 | 122.7951 | 122.8226 | -122.8271 | -122.8134 | 122.5662 | 0.31128 | 2.8244 | 1.2177
3136.1719 | 123.0057 | -54.4922 | 68.2617 | -0.075836 | -1.9142e-05 | 0.063094 | 0.0699 | -0.0026168 | 5.5488e-05 | 0.0049946 | -0.068481 | 0.0011023 | -0.00021357 | 5.9824e-05 | -0.0010787 | -0.0047253 | -0.0025379 | -51.6953 | 68.3166 | -54.57 | 68.0603 | -53.9062 | -54.3869 | -53.7781 | -53.3157 | 68.3166 | -54.538 | -54.1946 | -54.3961 | -54.5517 | -54.2496 | -0.07782 | 0.054931 | -0.20142 | 0.58594 | 0.71411 | 0.10529 | 0.79193 | 0.1831 | -0.045777 | 0.054931 | -122.4564 | 0.09613 | 0.24261 | -0.05951 | 0.28839 | -0.013733 | 0.66376 | 122.6303 | 0.14191 | 0.34332 | 122.8867 | 122.8546 | 122.8088 | 122.8088 | -122.8317 | -122.7997 | 122.5525 | 0.29755 | 2.7969 | 1.1765
3137.1719 | 123.0606 | -54.4693 | 68.248 | -0.13687 | -0.0013009 | 0.062025 | 0.068191 | -0.0011214 | 0.0030463 | 0.0081988 | -0.028809 | 0.00067495 | -0.00085457 | -0.0027174 | -0.0027877 | -0.0040845 | -0.0021107 | -51.6266 | 68.2892 | -54.538 | 68.1335 | -53.8193 | -54.2816 | -53.7094 | -53.2379 | 68.3121 | -54.5151 | -54.1763 | -54.3411 | -54.5334 | -54.1946 | -0.068665 | 0.041199 | -0.11444 | 0.65002 | 0.75989 | 0.18768 | 0.82855 | 0.25635 | -0.045777 | 0.064087 | -122.4243 | 0.12817 | 0.27466 | -0.064087 | 0.32044 | -0.01831 | 0.71869 | 122.6715 | 0.17395 | 0.33875 | 122.8271 | 122.8271 | 122.7585 | 122.7814 | -122.7859 | -122.7631 | 122.6028 | 0.29297 | 2.8427 | 1.2314
3138.1719 | 123.0103 | -54.4693 | 68.2892 | -0.12924 | 0.00019446 | 0.060744 | 0.0699 | -0.0026168 | 0.0015509 | 0.0064898 | -0.019653 | 0.0025975 | -0.00021357 | -0.00036738 | -0.0032151 | -0.0045117 | -0.0012561 | -51.6357 | 68.2846 | -54.5563 | 68.1244 | -53.8284 | -54.3182 | -53.714 | -53.2425 | 68.3487 | -54.5288 | -54.1672 | -54.332 | -54.538 | -54.1946 | -0.086975 | -0.004578 | -0.16479 | 0.64087 | 0.75531 | 0.15106 | 0.84229 | 0.23804 | -0.05951 | 0.059509 | -122.4564 | 0.13733 | 0.27466 | -0.068665 | 0.33417 | -0.009155 | 0.72784 | 122.6807 | 0.19684 | 0.36163 | 122.8409 | 122.8775 | 122.7539 | 122.818 | -122.8455 | -122.818 | 122.5937 | 0.30212 | 2.8336 | 1.2268
3139.1719 | 123.0515 | -54.483 | 68.2983 | -0.11398 | -1.9142e-05 | 0.059462 | 0.070327 | 0.00037377 | 5.5488e-05 | 0.0060626 | -0.041016 | 0.0015295 | -0.001709 | 5.9824e-05 | -0.0025741 | -0.0045117 | 2.554e-05 | -51.6312 | 68.2846 | -54.5288 | 68.129 | -53.8055 | -54.2862 | -53.7231 | -53.2196 | 68.3395 | -54.4922 | -54.1626 | -54.332 | -54.5151 | -54.1763 | -0.045777 | -0.013733 | -0.16937 | 0.67749 | 0.75989 | 0.19684 | 0.80566 | 0.24262 | -0.009155 | 0.041199 | -122.4609 | 0.15106 | 0.3067 | -0.032044 | 0.31586 | -0.022889 | 0.72327 | 122.6578 | 0.16022 | 0.32959 | 122.8134 | 122.8317 | 122.7676 | 122.8226 | -122.8271 | -122.7905 | 122.612 | 0.32043 | 2.8519 | 1.2634
3140.1719 | 123.056 | -54.4556 | 68.3121 | -0.16739 | 0.00040806 | 0.060103 | 0.070541 | 0.00037377 | 0.0032599 | 0.0094806 | -0.01355 | 0.00067495 | 0.0023498 | -0.001222 | -0.0010787 | -0.0042981 | 0.0045117 | -51.59 | 68.2846 | -54.5151 | 68.1885 | -54.007 | -54.2725 | -53.5767 | -53.215 | 68.3166 | -54.5197 | -54.1672 | -54.3228 | -54.5013 | -54.1672 | -0.05951 | -0.027466 | -0.1236 | 0.44861 | 0.87891 | 0.1831 | 0.93842 | 0.24262 | -0.064087 | 0.004577 | -122.4792 | 0.13275 | 0.28839 | -0.045777 | 0.35248 | 0.01831 | 0.50812 | 122.7036 | 0.19684 | 0.35248 | 122.7997 | 122.8363 | 122.7402 | 122.7722 | -122.8271 | -122.8317 | 122.644 | 0.28839 | 2.8656 | 1.2405
3141.1719 | 123.0606 | -54.4556 | 68.2663 | -0.098725 | -0.0017281 | 0.061598 | 0.070327 | -0.0051804 | 0.00026909 | 0.0069172 | -0.047119 | 0.0017431 | 0.00042723 | -0.0025036 | -0.0049241 | -0.0060071 | 2.554e-05 | -51.5945 | 68.2892 | -54.538 | 68.161 | -53.7735 | -54.2679 | -53.6911 | -53.2516 | 68.2755 | -54.538 | -54.1351 | -54.3137 | -54.4876 | -54.1809 | -0.082398 | 0.022889 | -0.10528 | 0.68207 | 0.76446 | 0.18768 | 0.84686 | 0.27008 | -0.082398 | 0.009156 | -122.4014 | 0.14191 | 0.27466 | -0.032044 | 0.35706 | 0.050354 | 0.76447 | 122.699 | 0.2243 | 0.40283 | 122.8271 | 122.8134 | 122.7448 | 122.731 | -122.8043 | -122.8043 | 122.6166 | 0.32043 | 2.861 | 1.2039
3142.1719 | 122.9965 | -54.4601 | 68.2938 | -0.083466 | 0.00040806 | 0.062025 | 0.070754 | 0.00037377 | 0.0026191 | 0.0039264 | -0.059326 | 0.00046135 | 0.0023498 | -0.0020764 | -0.0036423 | -0.0047253 | -0.0021107 | -51.6449 | 68.3258 | -54.5654 | 68.0969 | -53.8559 | -54.3411 | -53.7415 | -53.2562 | 68.3533 | -54.5242 | -54.1809 | -54.3549 | -54.5059 | -54.1992 | -0.10529 | 0.032044 | -0.19684 | 0.60425 | 0.71869 | 0.11902 | 0.82397 | 0.22431 | -0.064087 | 0.059509 | -122.4747 | 0.10529 | 0.26093 | -0.045776 | 0.32501 | 0.018311 | 0.70953 | 122.6624 | 0.16937 | 0.34332 | 122.8912 | 122.8775 | 122.7859 | 122.8134 | -122.8592 | -122.818 | 122.5571 | 0.27924 | 2.8152 | 1.2039
3143.1719 | 122.9965 | -54.4876 | 68.2983 | -0.060578 | 0.0019035 | 0.062239 | 0.070968 | 0.00080117 | 0.0034735 | 0.0049946 | -0.056274 | 0.0036657 | 0.00085443 | 0.0017688 | -0.0012925 | -0.0038709 | -0.0038197 | -51.6449 | 68.3395 | -54.5471 | 68.0878 | -53.8559 | -54.3274 | -53.7598 | -53.2791 | 68.3716 | -54.5105 | -54.1901 | -54.3549 | -54.5425 | -54.2084 | -0.059509 | 0.041199 | -0.21057 | 0.63171 | 0.72784 | 0.16022 | 0.78735 | 0.21973 | -0.022888 | 0.073242 | -122.4884 | 0.13275 | 0.27924 | -0.054932 | 0.30212 | -0.032044 | 0.69122 | 122.6349 | 0.15564 | 0.32043 | 122.8867 | 122.8821 | 122.8271 | 122.8592 | -122.8455 | -122.8088 | 122.5754 | 0.29755 | 2.8427 | 1.2085
3144.1719 | 123.0423 | -54.4464 | 68.3029 | -0.13687 | -0.0013009 | 0.061385 | 0.072036 | -0.0028304 | 0.0026191 | 0.0049946 | -0.03186 | 0.0013159 | 0.001709 | 0.001128 | -0.0017197 | -0.0047253 | -0.0016833 | -51.5808 | 68.3212 | -54.5151 | 68.1473 | -53.7735 | -54.2587 | -53.6819 | -53.1784 | 68.3395 | -54.5105 | -54.1397 | -54.3137 | -54.4922 | -54.1672 | -0.068665 | 0.018311 | -0.15564 | 0.67291 | 0.76446 | 0.18768 | 0.83313 | 0.25635 | -0.064087 | 0.036622 | -122.4426 | 0.13275 | 0.27924 | -0.045776 | 0.34332 | 0.018311 | 0.74158 | 122.6624 | 0.19684 | 0.37079 | 122.8363 | 122.85 | 122.7676 | 122.7859 | -122.818 | -122.8134 | 122.5937 | 0.3067 | 2.8656 | 1.268
3145.1719 | 123.0286 | -54.4327 | 68.3075 | -0.12924 | 0.0012625 | 0.060957 | 0.069259 | -0.0017624 | 0.0026191 | 0.0060626 | -0.041016 | 0.00067495 | 0.001068 | -0.0020764 | -0.0019333 | -0.0055799 | -0.00018806 | -51.6037 | 68.3395 | -54.4876 | 68.161 | -53.7872 | -54.2816 | -53.6911 | -53.1876 | 68.3395 | -54.5013 | -54.1351 | -54.332 | -54.4922 | -54.1443 | -0.054932 | 0.032044 | -0.14648 | 0.64545 | 0.74158 | 0.15106 | 0.79651 | 0.20599 | -0.068665 | 0.032044 | -122.4426 | 0.10071 | 0.28839 | -0.059509 | 0.35706 | 0.009156 | 0.70038 | 122.6486 | 0.16937 | 0.36621 | 122.8271 | 122.8409 | 122.7722 | 122.7722 | -122.7951 | -122.8088 | 122.5937 | 0.29755 | 2.829 | 1.2451
3146.1719 | 123.0377 | -54.4189 | 68.3395 | -0.091095 | 0.00019446 | 0.063948 | 0.069045 | -0.0013352 | 0.0030463 | 0.0026446 | -0.037964 | -0.0010339 | 0.00042723 | -0.0010084 | -0.0038559 | -0.0047253 | 0.0015209 | -51.622 | 68.3166 | -54.5425 | 68.129 | -53.8055 | -54.2953 | -53.714 | -53.2059 | 68.3487 | -54.4785 | -54.1351 | -54.3274 | -54.5105 | -54.1718 | -0.1236 | -0.022889 | -0.21057 | 0.6134 | 0.70496 | 0.1236 | 0.82855 | 0.24719 | -0.05951 | 0.009155 | -122.4747 | 0.091552 | 0.24719 | -0.091553 | 0.3067 | -0.032043 | 0.737 | 122.6715 | 0.15106 | 0.34332 | 122.8592 | 122.8271 | 122.7356 | 122.7676 | -122.8821 | -122.818 | 122.5479 | 0.28381 | 2.7969 | 1.2131
3147.1719 | 123.0469 | -54.4235 | 68.3258 | -0.12161 | 0.0016899 | 0.062453 | 0.069045 | 0.00080117 | 5.5488e-05 | 0.0062762 | -0.016602 | 0.0011023 | 0.003418 | -0.0018628 | -0.0044967 | -0.0053663 | -0.0012561 | -51.5533 | 68.2938 | -54.5013 | 68.1885 | -53.7552 | -54.2542 | -53.6774 | -53.1647 | 68.3624 | -54.4739 | -54.0619 | -54.332 | -54.4601 | -54.1397 | -0.07782 | -0.032044 | -0.13733 | 0.66834 | 0.74616 | 0.16937 | 0.82397 | 0.24719 | -0.050354 | 0.036621 | -122.3877 | 0.091553 | 0.28381 | -0.036621 | 0.33417 | 0.013733 | 0.74616 | 122.6898 | 0.14191 | 0.41199 | 122.7951 | 122.8363 | 122.7173 | 122.7859 | -122.8271 | -122.7997 | 122.612 | 0.36163 | 2.8702 | 1.2589
3148.1719 | 123.0011 | -54.4189 | 68.248 | -0.068207 | -0.00087374 | 0.063094 | 0.069686 | -5.343e-05 | 0.0019781 | 0.0052082 | -0.03186 | 0.0019567 | 0.0019226 | 0.0041186 | -0.0036423 | -0.0053663 | -0.0029651 | -51.5762 | 68.3029 | -54.5059 | 68.1885 | -53.7552 | -54.2404 | -53.6682 | -53.1647 | 68.3624 | -54.4785 | -54.1168 | -54.3091 | -54.4693 | -54.1443 | -0.086975 | 0.054931 | -0.059509 | 0.66376 | 0.75073 | 0.17853 | 0.83771 | 0.2655 | -0.05951 | 0.11444 | -122.3648 | 0.10986 | 0.27466 | -0.050354 | 0.33417 | 0.009156 | 0.75073 | 122.6944 | 0.16937 | 0.36163 | 122.8088 | 122.8409 | 122.7219 | 122.7814 | -122.7539 | -122.7264 | 122.6074 | 0.30212 | 2.8427 | 1.2543
3149.1719 | 122.9507 | -54.451 | 68.3487 | -0.068207 | -0.00066014 | 0.059462 | 0.071609 | -0.0011214 | 0.0030463 | 0.0056354 | -0.037964 | 0.00024775 | 0.0012818 | 0.0028368 | -0.0027877 | -0.0045117 | 2.554e-05 | -51.5991 | 68.3807 | -54.5059 | 68.1061 | -53.8559 | -54.3503 | -53.7369 | -53.2562 | 68.3853 | -54.4739 | -54.1855 | -54.3686 | -54.5471 | -54.213 | -0.054931 | 0.032043 | -0.24262 | 0.59509 | 0.71411 | 0.10071 | 0.76904 | 0.15564 | -0.022888 | 0.036621 | -122.5342 | 0.082398 | 0.23804 | -0.09613 | 0.26093 | -0.073242 | 0.65002 | 122.612 | 0.10529 | 0.28839 | 122.8867 | 122.8592 | 122.8317 | 122.8363 | -122.8546 | -122.8226 | 122.5571 | 0.2655 | 2.8519 | 1.1948
3150.1719 | 122.9507 | -54.451 | 68.3578 | -0.15213 | 0.0010489 | 0.061812 | 0.069472 | 0.00037377 | 0.0032599 | 0.0052082 | -0.047119 | 0.0015295 | 0.002777 | -0.00058098 | -0.0025741 | -0.0028027 | -0.0014697 | -51.6083 | 68.367 | -54.4739 | 68.1061 | -53.8559 | -54.3411 | -53.7369 | -53.27 | 68.3853 | -54.483 | -54.213 | -54.3732 | -54.5654 | -54.2221 | -0.022888 | 0.009155 | -0.25177 | 0.59509 | 0.71411 | 0.10986 | 0.737 | 0.13275 | -0.032043 | 0.027466 | -122.5708 | 0.07782 | 0.22888 | -0.11444 | 0.26093 | -0.082398 | 0.61798 | 122.58 | 0.10986 | 0.27008 | 122.8409 | 122.8683 | 122.818 | 122.8363 | -122.8317 | -122.8409 | 122.5571 | 0.23804 | 2.8427 | 1.181
3151.1719 | 123.0148 | -54.4373 | 68.3578 | -0.091095 | 0.00040806 | 0.061385 | 0.070541 | -5.343e-05 | 0.0011237 | 0.0045672 | -0.022705 | 0.00046135 | -0.00042717 | 5.9824e-05 | -0.00086511 | -0.0040845 | 0.00045294 | -51.6037 | 68.3441 | -54.5059 | 68.1335 | -53.8101 | -54.2953 | -53.7048 | -53.2104 | 68.3945 | -54.4785 | -54.1489 | -54.2999 | -54.483 | -54.1718 | -0.068664 | -0.013733 | -0.2243 | 0.62714 | 0.73242 | 0.14191 | 0.80109 | 0.21057 | -0.041199 | 0.036621 | -122.5067 | 0.13733 | 0.2655 | -0.045776 | 0.3067 | -0.004577 | 0.6958 | 122.6395 | 0.17853 | 0.32959 | 122.85 | 122.8729 | 122.7814 | 122.8317 | -122.8638 | -122.8363 | 122.5708 | 0.28839 | 2.8336 | 1.2268
3152.1719 | 123.0057 | -54.4189 | 68.3578 | -0.10635 | -0.0015145 | 0.061598 | 0.06755 | -0.00026703 | 0.0017645 | 0.0062762 | -0.025757 | 3.4148e-05 | 0.002777 | 0.00091422 | -0.0030013 | -0.0032301 | 0.0010937 | -51.5854 | 68.3807 | -54.4968 | 68.1198 | -53.8193 | -54.3182 | -53.714 | -53.2288 | 68.4082 | -54.4464 | -54.1672 | -54.3365 | -54.5151 | -54.1946 | -0.07782 | 0.022888 | -0.23804 | 0.59967 | 0.70496 | 0.10071 | 0.78278 | 0.17853 | -0.027466 | 0.050354 | -122.525 | 0.082397 | 0.2243 | -0.096131 | 0.25177 | -0.068665 | 0.67749 | 122.6166 | 0.10986 | 0.27924 | 122.8775 | 122.8546 | 122.7997 | 122.8271 | -122.8546 | -122.8043 | 122.5388 | 0.25177 | 2.8336 | 1.1902
3153.1719 | 122.9462 | -54.451 | 68.367 | -0.060578 | 0.0010489 | 0.060957 | 0.070113 | 0.0027238 | 0.00091009 | 0.0056354 | -0.056274 | 0.0040929 | 0.00064083 | 0.0068958 | -0.0010787 | -0.0042981 | 0.0023755 | -51.5945 | 68.3807 | -54.5151 | 68.1198 | -53.8422 | -54.3182 | -53.7323 | -53.2516 | 68.4128 | -54.4601 | -54.1626 | -54.3457 | -54.538 | -54.2084 | -0.064087 | 0.013733 | -0.24719 | 0.60883 | 0.71869 | 0.13275 | 0.78278 | 0.19684 | -0.009155 | 0.045777 | -122.5296 | 0.10529 | 0.24262 | -0.086975 | 0.25177 | -0.07782 | 0.67291 | 122.6349 | 0.11444 | 0.29755 | 122.8958 | 122.8729 | 122.8317 | 122.8638 | -122.8821 | -122.8271 | 122.5708 | 0.28839 | 2.8564 | 1.1993
3154.1719 | 123.0286 | -54.4144 | 68.3441 | -0.13687 | -0.00066014 | 0.063307 | 0.0699 | -0.0034714 | 0.0019781 | 0.0037128 | -0.03186 | 0.00067495 | -0.001709 | 0.0013416 | -0.0015061 | -0.0040845 | -0.0016833 | -51.5579 | 68.3762 | -54.483 | 68.1564 | -53.7827 | -54.2633 | -53.6682 | -53.1784 | 68.399 | -54.451 | -54.1168 | -54.2725 | -54.4556 | -54.1351 | -0.068664 | 0.032044 | -0.18768 | 0.63171 | 0.74616 | 0.15106 | 0.81482 | 0.21973 | -0.036621 | 0.054932 | -122.4609 | 0.14191 | 0.27924 | -0.041198 | 0.31586 | -0.004577 | 0.70038 | 122.6395 | 0.17853 | 0.33417 | 122.8592 | 122.85 | 122.7905 | 122.8134 | -122.8271 | -122.7951 | 122.5708 | 0.29755 | 2.8564 | 1.236
3155.1719 | 123.0194 | -54.3777 | 68.3533 | -0.11398 | 0.00019446 | 0.060744 | 0.070327 | -0.0043258 | 0.0051825 | 0.0067036 | -0.019653 | 0.00088875 | 0.00042723 | -0.00015378 | -0.0019333 | -0.0040845 | 0.00088014 | -51.5671 | 68.3716 | -54.4693 | 68.1244 | -53.7827 | -54.2816 | -53.6957 | -53.2013 | 68.3945 | -54.451 | -54.1214 | -54.2999 | -54.4876 | -54.158 | -0.091552 | 0.018311 | -0.22888 | 0.59509 | 0.68207 | 0.096131 | 0.77362 | 0.18768 | -0.073242 | 0.041199 | -122.4747 | 0.07782 | 0.21973 | -0.10986 | 0.29297 | -0.036621 | 0.68664 | 122.5937 | 0.15106 | 0.32959 | 122.8409 | 122.8455 | 122.7493 | 122.7722 | -122.8226 | -122.8043 | 122.5021 | 0.25635 | 2.8107 | 1.1765
3156.1719 | 122.9233 | -54.4052 | 68.399 | -0.12161 | 0.0025443 | 0.061171 | 0.07289 | 0.0020828 | 5.5488e-05 | 0.0045672 | -0.025757 | 3.4148e-05 | -0.00021357 | 5.9824e-05 | -0.0017197 | -0.0062207 | -0.0014697 | -51.5579 | 68.3945 | -54.5151 | 68.28 | -53.8422 | -54.364 | -53.6774 | -53.2379 | 68.4631 | -54.4464 | -54.2084 | -54.3732 | -54.5654 | -54.2175 | -0.10986 | -0.004578 | -0.11902 | 0.56305 | 0.72784 | 0.041198 | 0.83771 | 0.15106 | -0.041199 | 0.064087 | -122.6074 | 0.032043 | 0.18768 | -0.16022 | 0.22888 | -0.11902 | 0.67291 | 122.7951 | 0.073242 | 0.23804 | 122.9095 | 122.9095 | 122.7997 | 122.8683 | -122.9141 | -122.8455 | 122.6852 | 0.19684 | 2.8473 | 1.1673
3157.1719 | 122.9141 | -54.4235 | 68.4174 | -0.12161 | -0.00044654 | 0.062453 | 0.070968 | 0.001442 | 0.0011237 | 0.0060626 | -0.034912 | 0.0013159 | -0.001709 | -0.003999 | -0.0021469 | -0.0068615 | -0.0023243 | -51.5717 | 68.4174 | -54.4968 | 68.1015 | -53.8376 | -54.3137 | -53.7369 | -53.4256 | 68.3624 | -54.4876 | -54.1534 | -54.3869 | -54.538 | -54.1946 | -0.073242 | 0 | -0.31586 | 0.58594 | 0.68665 | 0.10986 | 0.75989 | 0.18311 | -0.064087 | -0.054931 | -122.5708 | 0.036621 | 0.22888 | -0.11444 | 0.29297 | -0.050354 | 0.65918 | 122.5983 | 0.10071 | 0.33417 | 122.9141 | 122.85 | 122.8409 | 122.7859 | -122.9141 | -122.905 | 122.525 | 0.27008 | 2.8519 | 0.99793
3158.1719 | 122.9416 | -54.4144 | 68.4174 | -0.068207 | -0.0010873 | 0.060103 | 0.069686 | -0.00069423 | 0.0026191 | 0.0032856 | -0.0043946 | 0.0011023 | -0.0010682 | 0.0041186 | -0.0017197 | -0.0049389 | 0.00088014 | -51.5579 | 68.4128 | -54.4785 | 68.1335 | -53.8193 | -54.277 | -53.7094 | -53.2333 | 68.4357 | -54.4464 | -54.1672 | -54.3411 | -54.5288 | -54.2038 | -0.064087 | -0.004577 | -0.28381 | 0.59509 | 0.70496 | 0.13733 | 0.76904 | 0.20142 | -0.032043 | 0.018311 | -122.5845 | 0.073243 | 0.21057 | -0.11444 | 0.24262 | -0.082398 | 0.65918 | 122.612 | 0.10529 | 0.27924 | 122.8912 | 122.8821 | 122.8271 | 122.85 | -122.8958 | -122.8638 | 122.5479 | 0.24719 | 2.8564 | 1.181
3159.1719 | 122.9095 | -54.4189 | 68.4082 | -0.075836 | -0.00066014 | 0.062239 | 0.072463 | 0.0010148 | 5.5488e-05 | 0.0049946 | -0.047119 | 0.0019567 | 0.00021363 | -0.0010084 | -0.0017197 | -0.0057935 | 0.0030163 | -51.6037 | 68.4402 | -54.4785 | 68.1152 | -53.8376 | -54.2862 | -53.7231 | -53.2471 | 68.454 | -54.4327 | -54.1809 | -54.3549 | -54.5197 | -54.2038 | -0.05951 | 0.032044 | -0.29297 | 0.58136 | 0.6958 | 0.13275 | 0.75531 | 0.19226 | -0.013733 | 0.045776 | -122.5891 | 0.064087 | 0.21515 | -0.10071 | 0.22888 | -0.086975 | 0.64087 | 122.5937 | 0.07782 | 0.25177 | 122.9187 | 122.8867 | 122.8592 | 122.8729 | -122.8867 | -122.8409 | 122.5342 | 0.23804 | 2.8152 | 1.1719
3160.1719 | 122.9416 | -54.4052 | 68.4174 | -0.083466 | 0.00040806 | 0.061812 | 0.070968 | -0.0028304 | 0.0017645 | 0.001363 | -0.037964 | 0.0013159 | 0.0025634 | 0.003905 | -0.0021469 | -0.0057935 | 0.00023934 | -51.5442 | 68.4128 | -54.4876 | 68.248 | -53.8696 | -54.3045 | -53.6591 | -53.2242 | 68.4769 | -54.4464 | -54.1718 | -54.3594 | -54.538 | -54.1946 | -0.082398 | -0.004577 | -0.16937 | 0.53558 | 0.74615 | 0.10071 | 0.82855 | 0.18311 | -0.041199 | 0.05951 | -122.5891 | 0.045776 | 0.21057 | -0.13275 | 0.25177 | -0.091553 | 0.61798 | 122.7356 | 0.086975 | 0.27466 | 122.9004 | 122.9233 | 122.818 | 122.8821 | -122.905 | -122.8638 | 122.6532 | 0.23346 | 2.861 | 1.181
3161.1719 | 123.0606 | -54.3594 | 68.4219 | -0.052948 | 0.0025443 | 0.061598 | 0.06755 | -0.0021896 | 0.0030463 | 0.0049946 | 0.087158 | 0.0017431 | 0.0019226 | -0.0065626 | -0.00043791 | -0.0077161 | -0.0010425 | -51.4572 | 68.4082 | -54.4006 | 68.2571 | -53.6636 | -54.1351 | -53.5538 | -53.0823 | 68.4311 | -54.4052 | -54.0756 | -54.1855 | -54.3411 | -54.0756 | -0.041199 | -0.013733 | -0.16479 | 0.6958 | 0.80566 | 0.2243 | 0.84686 | 0.2655 | -0.045776 | 0.009155 | -122.4976 | 0.17395 | 0.28381 | 0.018311 | 0.32959 | 0.064087 | 0.737 | 122.6578 | 0.21973 | 0.32959 | 122.8088 | 122.8363 | 122.7676 | 122.7905 | -122.8226 | -122.8271 | 122.6166 | 0.28381 | 2.9022 | 1.2772
3162.1719 | 122.9416 | -54.3869 | 68.4265 | -0.10635 | 0.0016899 | 0.061385 | 0.070327 | 0.0027238 | 0.0013373 | 0.0056354 | -0.047119 | 0.0011023 | 0.0021362 | -0.0010084 | -0.0032151 | -0.0047253 | -0.0018971 | -51.4984 | 68.4128 | -54.4601 | 68.1519 | -53.7964 | -54.2679 | -53.7094 | -53.2013 | 68.4448 | -54.4327 | -54.1489 | -54.332 | -54.4968 | -54.1901 | -0.073242 | -0.013733 | -0.27466 | 0.59051 | 0.67749 | 0.11902 | 0.75073 | 0.19226 | -0.045776 | 0.01831 | -122.5754 | 0.054932 | 0.19684 | -0.10986 | 0.24262 | -0.064087 | 0.66376 | 122.612 | 0.10071 | 0.28381 | 122.8729 | 122.8775 | 122.7997 | 122.8317 | -122.8867 | -122.8592 | 122.5388 | 0.23804 | 2.8885 | 1.1856
3163.1719 | 122.937 | -54.4006 | 68.4311 | -0.10635 | 0.00040806 | 0.062239 | 0.070754 | -0.0011214 | 0.0039007 | 0.00414 | -0.068481 | 0.0028113 | 0.00064083 | 0.0030506 | -0.0023605 | -0.0034437 | 0.0028027 | -51.503 | 68.4265 | -54.451 | 68.1244 | -53.8376 | -54.2999 | -53.7094 | -53.2608 | 68.4631 | -54.4464 | -54.1626 | -54.3503 | -54.5288 | -54.1901 | -0.050354 | -0.004577 | -0.3067 | 0.56305 | 0.69122 | 0.10071 | 0.74158 | 0.15106 | -0.045776 | 0.032044 | -122.5937 | 0.050354 | 0.21057 | -0.12817 | 0.25635 | -0.082398 | 0.6134 | 122.5754 | 0.09613 | 0.28381 | 122.8775 | 122.9095 | 122.8271 | 122.8638 | -122.8821 | -122.8775 | 122.525 | 0.23804 | 2.8976 | 1.1398
3164.1719 | 122.9279 | -54.3869 | 68.4402 | -0.10635 | -0.0015145 | 0.063094 | 0.072036 | 0.003151 | 0.0024053 | 0.0079852 | -0.041016 | 0.0028113 | 0.0025634 | 0.002196 | -0.0010787 | -0.0049389 | 0.0013073 | -51.503 | 68.454 | -54.4739 | 68.1473 | -53.8147 | -54.2953 | -53.714 | -53.2333 | 68.5089 | -54.4235 | -54.1672 | -54.364 | -54.5425 | -54.2038 | -0.086975 | 0.013732 | -0.29297 | 0.5722 | 0.67291 | 0.091553 | 0.75989 | 0.17853 | -0.036621 | 0.068664 | -122.6074 | 0.022888 | 0.18311 | -0.15564 | 0.21973 | -0.11902 | 0.65918 | 122.6212 | 0.059509 | 0.25635 | 122.9279 | 122.9324 | 122.8409 | 122.8958 | -122.9141 | -122.8638 | 122.5342 | 0.21973 | 2.8839 | 1.1536
3165.1719 | 122.9553 | -54.3961 | 68.4402 | -0.075836 | 0.0021171 | 0.062453 | 0.071822 | 0.0010148 | 0.0024053 | 0.005849 | 0.10852 | 0.0017431 | 0.001709 | 0.001128 | -0.0017197 | -0.0064343 | 0.00023934 | -51.5213 | 68.4631 | -54.4464 | 68.1519 | -53.7506 | -54.7256 | -53.8696 | -53.2196 | 68.4998 | -54.4189 | -54.1489 | -54.3411 | -54.5425 | -54.1672 | -0.050354 | 0.022888 | -0.28839 | 0.64545 | 0.52643 | -0.32959 | 0.57678 | -0.27924 | -0.022888 | 0.059509 | -122.5891 | 0.054932 | 0.22888 | -0.14648 | 0.25177 | -0.1236 | 0.6958 | 122.5983 | 0.07782 | 0.27008 | 122.9095 | 122.9187 | 122.8592 | 122.8958 | -122.8867 | -122.8592 | 122.5479 | 0.24719 | 2.8748 | 1.1765
3166.1719 | 123.0515 | -54.3411 | 68.4448 | -0.13687 | 0.0010489 | 0.061598 | 0.068191 | -0.0043258 | 0.0013373 | 0.002431 | 0.071899 | 0.00088875 | 0.0012818 | -0.001222 | -0.0015061 | -0.0079297 | 0.00088014 | -51.4297 | 68.4219 | -54.4006 | 68.2663 | -53.6453 | -54.126 | -53.54 | -53.0594 | 68.454 | -54.3686 | -54.0298 | -54.1672 | -54.3365 | -54.0482 | -0.05951 | -0.022888 | -0.17853 | 0.6958 | 0.80109 | 0.21515 | 0.8606 | 0.27466 | -0.027466 | 0.009155 | -122.4747 | 0.17395 | 0.29297 | 0.004577 | 0.32043 | 0.032043 | 0.75531 | 122.6669 | 0.20142 | 0.33875 | 122.8226 | 122.8226 | 122.7631 | 122.7951 | -122.8455 | -122.8134 | 122.6074 | 0.31128 | 2.9114 | 1.2817
3167.1719 | 122.8821 | -54.4098 | 68.4402 | -0.098725 | 0.0010489 | 0.061812 | 0.07225 | 0.0029374 | 0.0028327 | 0.0049946 | -0.053223 | 0.00067495 | 0.00021363 | -0.00464 | -0.0010787 | -0.0049389 | 0.00066654 | -51.4709 | 68.454 | -54.4327 | 68.1473 | -53.8055 | -54.2816 | -53.7094 | -53.2242 | 68.4631 | -54.4098 | -54.1489 | -54.3274 | -54.7256 | -54.3365 | -0.022888 | 0.013732 | -0.29297 | 0.60425 | 0.70038 | 0.12817 | 0.72327 | 0.15106 | 0 | 0.022888 | -122.5891 | 0.082397 | 0.073242 | -0.31586 | 0.073242 | -0.31586 | 0.62714 | 122.58 | 0.082397 | 0.26093 | 122.8867 | 122.8729 | 122.8638 | 122.8729 | -122.8729 | -122.85 | 122.5571 | 0.26093 | 2.9388 | 1.1856
3168.1719 | 122.9828 | -54.3457 | 68.454 | -0.13687 | -0.0040781 | 0.058607 | 0.0699 | -0.0021896 | 0.0015509 | 0.0060626 | -0.010498 | 0.0019567 | 0.0021362 | 0.0051868 | -0.0017197 | -0.0040845 | 0.0023755 | -51.4572 | 68.4311 | -54.4418 | 68.1976 | -53.7369 | -54.2221 | -53.6545 | -53.1326 | 68.4448 | -54.4098 | -54.1031 | -54.2404 | -54.4281 | -54.1031 | -0.09613 | -0.022888 | -0.25635 | 0.60883 | 0.69122 | 0.1236 | 0.78735 | 0.21973 | -0.064087 | -0.009155 | -122.5571 | 0.10529 | 0.24262 | -0.082398 | 0.3067 | -0.018311 | 0.70496 | 122.6395 | 0.16937 | 0.3067 | 122.8729 | 122.8546 | 122.7768 | 122.7905 | -122.8958 | -122.8638 | 122.5433 | 0.24262 | 2.8885 | 1.2131
3169.1719 | 122.9462 | -54.3777 | 68.4402 | -0.098725 | 0.00040806 | 0.063948 | 0.069259 | 0.007637 | 0.0021917 | 0.0056354 | -0.010498 | 0.0019567 | 0.0038452 | -0.0025036 | 0.00020289 | -0.0045117 | 0.0017345 | -51.4755 | 68.486 | -54.4327 | 68.0832 | -53.5126 | -54.0573 | -53.6728 | -53.1738 | 68.5043 | -54.4189 | -54.1351 | -54.3137 | -54.5197 | -54.1946 | -0.054931 | 0.045776 | -0.35706 | 0.86517 | 0.70496 | 0.32043 | 0.75989 | 0.37537 | -0.041198 | 0.064086 | -122.5754 | 0.064087 | 0.18311 | -0.14191 | 0.2243 | -0.10071 | 0.9201 | 122.5159 | 0.10529 | 0.28381 | 122.9187 | 122.9233 | 122.8638 | 122.8821 | -122.8729 | -122.8592 | 122.4609 | 0.24262 | 2.9022 | 1.2039
3170.1719 | 122.9324 | -54.3594 | 68.4723 | -0.12161 | -0.00087374 | 0.062666 | 0.070754 | 0.001442 | 0.0043281 | 0.0054218 | -0.13257 | 0.0030249 | -0.0027772 | 0.0034778 | -0.0023605 | -0.0051527 | -0.00018806 | -51.4664 | 68.4586 | -54.4601 | 68.1473 | -53.7781 | -54.2587 | -53.6774 | -53.1647 | 68.454 | -54.4006 | -54.1306 | -54.3137 | -54.4922 | -54.158 | -0.10071 | -0.013733 | -0.32501 | 0.58136 | 0.68207 | 0.10071 | 0.78278 | 0.20142 | -0.041199 | -0.018311 | -122.6028 | 0.045776 | 0.20142 | -0.13275 | 0.24262 | -0.091552 | 0.68207 | 122.6074 | 0.086975 | 0.27008 | 122.9187 | 122.8546 | 122.818 | 122.8134 | -122.9324 | -122.8729 | 122.5067 | 0.22888 | 2.8931 | 1.1948
3171.1719 | 123.0148 | -54.3182 | 68.4357 | -0.18265 | -0.00066014 | 0.06288 | 0.069472 | -0.0011214 | 0.0039007 | 0.005849 | -0.028809 | 0.0011023 | -0.00021357 | -0.0014356 | -0.0021469 | -0.0064343 | 0.00045294 | -51.384 | 68.4128 | -54.4373 | 68.2892 | -53.6499 | -54.1351 | -53.5812 | -52.9221 | 68.4265 | -54.3549 | -54.0161 | -54.1901 | -54.364 | -54.0665 | -0.11902 | -0.022888 | -0.14648 | 0.66834 | 0.737 | 0.18311 | 0.85602 | 0.30212 | -0.036621 | -0.009155 | -122.4518 | 0.12817 | 0.25177 | -0.045777 | 0.28839 | -0.009156 | 0.78735 | 122.7264 | 0.16479 | 0.33875 | 122.85 | 122.7814 | 122.731 | 122.7448 | -122.8729 | -122.7905 | 122.6074 | 0.30212 | 2.9343 | 1.3962
3172.1719 | 122.818 | -54.3823 | 68.4265 | -0.075836 | -0.00023294 | 0.061812 | 0.070968 | -0.00048063 | 0.0019781 | 0.0086262 | -0.034912 | 0.00088875 | 0.0021362 | 0.0045458 | -0.00043791 | -0.0045117 | -0.0012561 | -51.4572 | 68.4906 | -54.4281 | 68.1747 | -53.7735 | -54.2633 | -53.6957 | -53.215 | 68.5181 | -54.3686 | -54.1306 | -54.3091 | -54.5059 | -54.1763 | -0.045777 | 0.064087 | -0.25177 | 0.60882 | 0.68664 | 0.11902 | 0.73242 | 0.16479 | 0.013733 | 0.091552 | -122.5571 | 0.073242 | 0.20599 | -0.1236 | 0.19226 | -0.13733 | 0.6546 | 122.6028 | 0.059509 | 0.23804 | 122.9187 | 122.8867 | 122.8729 | 122.9004 | -122.8546 | -122.7951 | 122.5571 | 0.25177 | 2.9251 | 1.1673
3173.1719 | 122.9141 | -54.364 | 68.4677 | -0.045319 | 0.0031851 | 0.061598 | 0.068618 | 0.003151 | 0.0019781 | 0.0054218 | -0.044067 | 0.0011023 | 0.001709 | 0.00070062 | -0.0017197 | -0.0032301 | 0.0019483 | -51.4252 | 68.4677 | -54.4418 | 68.1702 | -53.7643 | -54.2496 | -53.6682 | -53.2104 | 68.5089 | -54.4098 | -54.1534 | -54.332 | -54.5151 | -54.1763 | -0.077819 | 0 | -0.29755 | 0.59967 | 0.6958 | 0.11444 | 0.77362 | 0.19226 | -0.045776 | 0.041199 | -122.6212 | 0.032044 | 0.18768 | -0.15106 | 0.23346 | -0.10529 | 0.67749 | 122.612 | 0.07782 | 0.25635 | 122.9095 | 122.9187 | 122.8317 | 122.8729 | -122.9095 | -122.8775 | 122.5342 | 0.21057 | 2.9388 | 1.1536
3174.1719 | 122.937 | -54.3549 | 68.4586 | -0.075836 | 0.0012625 | 0.06288 | 0.072036 | 0.0033646 | 0.00091009 | 0.0056354 | -0.053223 | 0.0011023 | 0.001068 | -0.0010084 | -0.0034287 | -0.0030163 | -0.00082886 | -51.4206 | 68.4814 | -54.4418 | 68.1885 | -53.7506 | -54.2221 | -53.6591 | -53.1784 | 68.5226 | -54.3915 | -54.1351 | -54.3137 | -54.5105 | -54.1672 | -0.086975 | 0.022888 | -0.27008 | 0.60425 | 0.6958 | 0.13275 | 0.78278 | 0.21973 | -0.036621 | 0.064087 | -122.5937 | 0.041198 | 0.18768 | -0.15564 | 0.2243 | -0.11902 | 0.69122 | 122.6303 | 0.077819 | 0.25635 | 122.9233 | 122.9141 | 122.8363 | 122.8775 | -122.9004 | -122.85 | 122.5433 | 0.21973 | 2.9343 | 1.1765
3175.1719 | 122.9279 | -54.3411 | 68.5135 | -0.12924 | 0.00019446 | 0.061171 | 0.07289 | 0.0033646 | 0.00048269 | 0.0032856 | -0.18445 | 0.0028113 | 0.0019226 | 0.0054004 | -0.0010787 | -0.0066479 | -0.0010425 | -51.4389 | 68.4586 | -54.4235 | 68.1747 | -53.7643 | -54.245 | -53.6682 | -53.2242 | 68.4448 | -54.4006 | -54.1122 | -54.2953 | -54.4601 | -54.1489 | -0.082398 | -0.054932 | -0.33875 | 0.57678 | 0.67291 | 0.09613 | 0.75531 | 0.17853 | -0.05951 | -0.068665 | -122.6257 | 0.045776 | 0.19226 | -0.11902 | 0.25177 | -0.059509 | 0.65918 | 122.5983 | 0.10529 | 0.28839 | 122.8821 | 122.8455 | 122.7997 | 122.7859 | -122.937 | -122.9141 | 122.5159 | 0.22888 | 2.9022 | 1.1169
3176.1719 | 122.9233 | -54.3182 | 68.4906 | -0.091095 | -0.00066014 | 0.062453 | 0.069259 | -0.001976 | 0.0013373 | 0.0052082 | -0.041016 | 0.0017431 | 0.0038452 | 0.0047594 | -0.0027877 | -0.00066648 | 0.0017345 | -51.416 | 68.4814 | -54.4327 | 68.1656 | -53.7781 | -54.2587 | -53.6865 | -53.1967 | 68.5089 | -54.3915 | -54.245 | -54.3869 | -54.1718 | -53.9612 | -0.11444 | -0.009156 | -0.32501 | 0.54016 | 0.63171 | 0.059509 | 0.74616 | 0.17395 | -0.073242 | 0.01831 | -122.7356 | -0.068665 | 0.35706 | 0.14648 | 0.4303 | 0.21973 | 0.6546 | 122.5983 | 0.004577 | 0.14648 | 122.9141 | 122.9004 | 122.7997 | 122.8271 | -122.9233 | -122.8821 | 122.4838 | 0.073242 | 2.9022 | 1.1215
3177.1719 | 122.905 | -54.3686 | 68.4906 | -0.083466 | 0.00019446 | 0.061812 | 0.0699 | -0.00048063 | 0.0017645 | 0.00093559 | -0.025757 | 0.00067495 | -0.00064077 | 0.0015552 | -0.00065151 | -0.0028027 | 0.0023755 | -51.3977 | 68.4769 | -54.4052 | 68.1839 | -53.746 | -54.245 | -53.6407 | -53.1876 | 68.5226 | -54.3915 | -54.1397 | -54.2953 | -54.5013 | -54.158 | -0.036621 | -0.013733 | -0.3067 | 0.62256 | 0.72784 | 0.1236 | 0.76447 | 0.16022 | -0.022888 | 0.032043 | -122.6303 | 0.073242 | 0.21057 | -0.13275 | 0.23346 | -0.10986 | 0.65918 | 122.5891 | 0.09613 | 0.25177 | 122.8821 | 122.9141 | 122.8455 | 122.8912 | -122.8958 | -122.8821 | 122.5525 | 0.22888 | 2.9709 | 1.181
3178.1719 | 122.9187 | -54.3365 | 68.4906 | -0.13687 | 0.0014761 | 0.061385 | 0.070113 | 0.0027238 | 0.00069649 | 0.0069172 | -0.025757 | 0.00067495 | 2.8e-08 | -0.0016492 | -0.0010787 | -0.0030163 | 0.0015209 | -51.384 | 68.4952 | -54.3961 | 68.2159 | -53.7186 | -54.1946 | -53.627 | -53.1784 | 68.5272 | -54.3686 | -54.1168 | -54.2816 | -54.483 | -54.1489 | -0.059509 | 0.004577 | -0.27466 | 0.61798 | 0.70953 | 0.14191 | 0.76904 | 0.20142 | -0.032043 | 0.036621 | -122.6074 | 0.054932 | 0.18768 | -0.14648 | 0.21973 | -0.11444 | 0.67749 | 122.612 | 0.086975 | 0.25177 | 122.8912 | 122.8958 | 122.8317 | 122.8638 | -122.8867 | -122.8592 | 122.5525 | 0.21973 | 2.9526 | 1.1581
3179.1719 | 122.9324 | -54.3365 | 68.5043 | -0.12924 | 0.0010489 | 0.061812 | 0.068404 | -0.001976 | 0.0034735 | 0.0079852 | -0.0074462 | 0.00067495 | -0.00021357 | 0.0049732 | -0.0040695 | -0.0040845 | 2.554e-05 | -51.4114 | 68.4998 | -54.3777 | 68.161 | -53.7552 | -54.2496 | -53.6682 | -53.1555 | 68.541 | -54.3869 | -54.0665 | -54.332 | -54.4235 | -54.1122 | -0.041199 | -0.004577 | -0.34332 | 0.58136 | 0.66833 | 0.086975 | 0.70953 | 0.12817 | -0.050354 | 0.036622 | -122.5708 | 0.004578 | 0.2243 | -0.086975 | 0.27466 | -0.036621 | 0.62256 | 122.5388 | 0.054932 | 0.32043 | 122.8775 | 122.9279 | 122.8363 | 122.8775 | -122.8821 | -122.8912 | 122.4976 | 0.27008 | 2.9251 | 1.181
3180.1719 | 122.9279 | -54.3182 | 68.5318 | -0.11398 | -0.0015145 | 0.059889 | 0.070754 | 0.00016017 | -0.00015811 | 0.0047808 | -0.034912 | 3.4148e-05 | 0.0019226 | -0.00464 | 0.00020289 | -0.0042981 | -0.00018806 | -51.3336 | 68.5089 | -54.3869 | 68.2297 | -53.6728 | -54.1763 | -53.6133 | -53.0869 | 68.5547 | -54.3457 | -54.0802 | -54.2587 | -54.4373 | -54.1168 | -0.068665 | -0.022888 | -0.30212 | 0.64545 | 0.70496 | 0.14191 | 0.77362 | 0.21057 | -0.027466 | 0.022888 | -122.612 | 0.059509 | 0.20142 | -0.11902 | 0.22888 | -0.091553 | 0.71411 | 122.6166 | 0.086975 | 0.2655 | 122.8958 | 122.9004 | 122.8271 | 122.8729 | -122.9187 | -122.8775 | 122.5479 | 0.23804 | 2.9846 | 1.2314
3181.1719 | 122.9187 | -54.3365 | 68.4952 | -0.10635 | -0.00087374 | 0.060957 | 0.070113 | -0.00048063 | 0.0017645 | 0.0049946 | -0.028809 | 0.0011023 | 0.0012818 | -0.0037854 | -0.0030013 | -0.0049389 | 0.00066654 | -51.3794 | 68.5043 | -54.4189 | 68.2159 | -53.714 | -54.213 | -53.6362 | -53.1692 | 68.541 | -54.3686 | -54.1168 | -54.2908 | -54.4785 | -54.1397 | -0.082397 | 0.009155 | -0.27924 | 0.62256 | 0.70038 | 0.1236 | 0.78278 | 0.20599 | -0.032043 | 0.045777 | -122.612 | 0.045777 | 0.19684 | -0.14191 | 0.22888 | -0.10986 | 0.70496 | 122.6349 | 0.07782 | 0.25177 | 122.9233 | 122.9095 | 122.8409 | 122.8775 | -122.9141 | -122.8638 | 122.5525 | 0.21973 | 2.9572 | 1.1673
3182.1719 | 122.9095 | -54.3137 | 68.5226 | -0.091095 | -1.9142e-05 | 0.062453 | 0.069045 | -0.00026703 | 0.0011237 | 0.0077716 | -0.016602 | 3.4148e-05 | 0.0021362 | 0.0017688 | -0.0010787 | -0.0036573 | 0.0025891 | -51.3565 | 68.5043 | -54.4052 | 68.2251 | -53.6819 | -54.1946 | -53.6316 | -53.1281 | 68.5455 | -54.3411 | -54.1031 | -54.2725 | -54.4693 | -54.1351 | -0.091552 | -0.018311 | -0.29755 | 0.63171 | 0.68207 | 0.11902 | 0.77362 | 0.21057 | -0.027465 | 0.022888 | -122.6257 | 0.041199 | 0.17853 | -0.15564 | 0.20599 | -0.12817 | 0.72327 | 122.6303 | 0.068664 | 0.23804 | 122.9095 | 122.8867 | 122.818 | 122.8592 | -122.9279 | -122.8638 | 122.5388 | 0.21057 | 2.9572 | 1.1856
3183.1719 | 122.9004 | -54.3091 | 68.5226 | -0.060578 | 0.0012625 | 0.061171 | 0.071181 | 0.0012284 | 0.0047553 | 0.0064898 | -0.022705 | 0.0025975 | 0.0025634 | 0.0013416 | -0.0023605 | -0.0038709 | 0.00066654 | -51.3336 | 68.5135 | -54.3777 | 68.2251 | -53.6636 | -54.1626 | -53.595 | -53.0823 | 68.5318 | -54.3594 | -54.0985 | -54.2496 | -54.4556 | -54.0985 | -0.068665 | -0.009155 | -0.29755 | 0.64545 | 0.71411 | 0.14648 | 0.78278 | 0.21515 | -0.050354 | 0.009155 | -122.6212 | 0.059509 | 0.21057 | -0.14648 | 0.26093 | -0.09613 | 0.71411 | 122.6028 | 0.10986 | 0.26093 | 122.8912 | 122.8912 | 122.8226 | 122.8409 | -122.9004 | -122.8821 | 122.5342 | 0.21057 | 2.9755 | 1.2268
3184.1719 | 122.9782 | -54.2999 | 68.5226 | -0.098725 | -0.00087374 | 0.061385 | 0.069686 | 0.00251 | 0.0034735 | 0.003072 | -0.0013428 | 0.0011023 | 0.0012818 | -0.00036738 | -0.0027877 | -0.0036573 | -0.0016833 | -51.297 | 68.5455 | -54.3549 | 68.2022 | -53.627 | -54.0161 | -53.5629 | -53.0182 | 68.5638 | -54.3182 | -54.0253 | -54.1809 | -54.3732 | -54.0665 | -0.054931 | 0.022888 | -0.32044 | 0.67291 | 0.737 | 0.28381 | 0.79193 | 0.33875 | -0.01831 | 0.041199 | -122.5479 | 0.11902 | 0.23346 | -0.073242 | 0.25177 | -0.054932 | 0.72784 | 122.5571 | 0.13733 | 0.29297 | 122.9004 | 122.8821 | 122.8455 | 122.8638 | -122.8775 | -122.8409 | 122.5021 | 0.27466 | 3.0029 | 1.2817
3185.1719 | 122.9004 | -54.3228 | 68.5089 | -0.060578 | 0.00019446 | 0.060103 | 0.070754 | -0.0032578 | 0.0041143 | 0.0064898 | 0.0078126 | 0.0021703 | 0.0014954 | -0.0033582 | -0.0025741 | -0.0045117 | 0.0025891 | -51.3016 | 68.5226 | -54.3777 | 68.2663 | -53.6362 | -54.1214 | -53.5583 | -53.0594 | 68.5501 | -54.3274 | -54.0665 | -54.213 | -54.4189 | -54.0848 | -0.054932 | 0.013733 | -0.24262 | 0.68665 | 0.76447 | 0.20142 | 0.8194 | 0.25635 | -0.004578 | 0.041199 | -122.5754 | 0.10986 | 0.23804 | -0.09613 | 0.24262 | -0.091552 | 0.74158 | 122.644 | 0.11444 | 0.26093 | 122.9004 | 122.8775 | 122.8455 | 122.8729 | -122.8867 | -122.8363 | 122.5891 | 0.25635 | 3.0212 | 1.2634
3186.1719 | 122.9599 | -54.3228 | 68.5364 | -0.091095 | -1.9142e-05 | 0.060103 | 0.067977 | -0.0021896 | 0.0026191 | 0.005849 | -0.025757 | 0.0011023 | 0.00021363 | 0.0028368 | -0.0019333 | -0.0025891 | -0.0033923 | -51.3016 | 68.5501 | -54.3594 | 68.2892 | -53.6087 | -54.1214 | -53.5538 | -53.0502 | 68.5272 | -54.332 | -54.0573 | -54.213 | -54.3869 | -54.0802 | -0.036621 | 0.013733 | -0.24719 | 0.71411 | 0.76904 | 0.20142 | 0.80566 | 0.23804 | -0.009155 | -0.009155 | -122.5937 | 0.10986 | 0.24262 | -0.064087 | 0.25177 | -0.054932 | 0.75073 | 122.6486 | 0.11902 | 0.27466 | 122.9095 | 122.8592 | 122.8729 | 122.85 | -122.8958 | -122.8683 | 122.612 | 0.2655 | 3.0212 | 1.2726
3187.1719 | 122.9279 | -54.3091 | 68.541 | -0.083466 | -1.9142e-05 | 0.061385 | 0.069686 | -0.00048063 | 0.0049689 | 0.0032856 | -0.0043946 | 0.0023839 | 0.0025634 | -0.0016492 | -0.0030013 | -0.0068615 | -0.0014697 | -51.3016 | 68.5272 | -54.3549 | 68.2571 | -53.6545 | -54.1489 | -53.5995 | -53.0869 | 68.5547 | -54.332 | -54.0665 | -54.2496 | -54.4373 | -54.0939 | -0.045776 | -0.013733 | -0.28381 | 0.6546 | 0.70953 | 0.16022 | 0.75531 | 0.20599 | -0.022888 | 0.013732 | -122.6074 | 0.059509 | 0.21515 | -0.12817 | 0.23804 | -0.10529 | 0.70038 | 122.612 | 0.082397 | 0.2655 | 122.8821 | 122.8867 | 122.8363 | 122.8638 | -122.8958 | -122.8729 | 122.5662 | 0.24261 | 3.0075 | 1.2222
3188.1719 | 122.9324 | -54.2908 | 68.5181 | -0.037689 | 0.0019035 | 0.063734 | 0.069045 | 0.003151 | 0.0013373 | 0.0034992 | -0.0043946 | 0.0021703 | 2.8e-08 | -0.0037854 | -0.0025741 | -0.0045117 | -0.0031787 | -51.3016 | 68.541 | -54.3457 | 68.2892 | -53.627 | -54.1306 | -53.5629 | -53.0594 | 68.5593 | -54.3137 | -54.0527 | -54.2358 | -54.4189 | -54.0802 | -0.054932 | 0.022889 | -0.22888 | 0.66376 | 0.72784 | 0.16022 | 0.78278 | 0.21515 | -0.022889 | 0.041199 | -122.5708 | 0.054931 | 0.21057 | -0.12817 | 0.23346 | -0.10529 | 0.71869 | 122.6349 | 0.07782 | 0.26093 | 122.8867 | 122.8729 | 122.8317 | 122.85 | -122.8638 | -122.8317 | 122.58 | 0.23804 | 2.9892 | 1.2314
3189.1719 | 122.9324 | -54.3045 | 68.5364 | -0.03006 | 0.00083526 | 0.061385 | 0.069472 | -0.0024032 | 0.0021917 | 0.0067036 | -0.0074462 | 0.00088875 | 0.0014954 | 0.0034778 | -0.0021469 | -0.0042981 | 0.0036571 | -51.2741 | 68.5501 | -54.3549 | 68.2983 | -53.5904 | -54.126 | -53.5355 | -53.0228 | 68.5455 | -54.3137 | -54.0436 | -54.213 | -54.3961 | -54.0573 | -0.050354 | 0.013733 | -0.23804 | 0.71411 | 0.76904 | 0.17853 | 0.8194 | 0.22888 | -0.009156 | 0.009155 | -122.58 | 0.091552 | 0.24719 | -0.091553 | 0.25635 | -0.082397 | 0.76447 | 122.6532 | 0.10071 | 0.27008 | 122.905 | 122.8592 | 122.8546 | 122.85 | -122.8912 | -122.85 | 122.6028 | 0.26093 | 3.0304 | 1.2817
3190.1719 | 122.9416 | -54.2908 | 68.5501 | -0.014801 | 0.0027579 | 0.060316 | 0.069686 | -5.343e-05 | 0.0056097 | 0.0069172 | -0.0043946 | 0.0011023 | 0.00085443 | 0.003905 | -0.00043791 | -0.0060071 | 0.0047253 | -51.2558 | 68.5455 | -54.3457 | 68.3121 | -53.5858 | -54.1077 | -53.5309 | -53.0136 | 68.5776 | -54.3091 | -54.0161 | -54.1901 | -54.3686 | -54.0802 | -0.054932 | -0.004578 | -0.23804 | 0.70496 | 0.75989 | 0.1831 | 0.81482 | 0.23804 | -0.018311 | 0.027466 | -122.5662 | 0.10071 | 0.21057 | -0.07782 | 0.22888 | -0.059509 | 0.75989 | 122.6578 | 0.11902 | 0.29297 | 122.8912 | 122.8867 | 122.8363 | 122.8683 | -122.8958 | -122.8592 | 122.6028 | 0.27466 | 3.035 | 1.2772
3191.1719 | 122.9919 | -54.2679 | 68.5638 | -0.075836 | -0.00066014 | 0.062666 | 0.0699 | 0.0012284 | 0.0028327 | 0.0054218 | 0.013916 | 0.0019567 | 0.0025634 | 0.0015552 | -0.0025741 | -0.0040845 | 0.0017345 | -51.2421 | 68.5776 | -54.3549 | 68.2983 | -53.5904 | -54.071 | -53.5355 | -53.0045 | 68.5684 | -54.3228 | -54.0115 | -54.1718 | -54.364 | -54.0344 | -0.086975 | 0.013733 | -0.2655 | 0.67749 | 0.73242 | 0.19684 | 0.8194 | 0.28381 | -0.054932 | 0.004577 | -122.5754 | 0.09613 | 0.23346 | -0.096131 | 0.28839 | -0.041199 | 0.76447 | 122.6532 | 0.15106 | 0.31128 | 122.9324 | 122.8912 | 122.8455 | 122.8363 | -122.9187 | -122.8867 | 122.5662 | 0.25635 | 3.0258 | 1.2634
3192.1719 | 122.9507 | -54.2725 | 68.5455 | -0.060578 | 0.00083526 | 0.060957 | 0.069045 | -0.0060348 | 5.5488e-05 | 0.0069172 | 0.0078126 | -0.00060665 | -0.00021357 | -0.005708 | -0.00065151 | -0.0053663 | 0.00023934 | -51.2604 | 68.5364 | -54.3411 | 68.28 | -53.5995 | -54.0802 | -53.5309 | -53.0045 | 68.5867 | -54.3228 | -54.007 | -54.158 | -54.3228 | -54.0298 | -0.068664 | -0.009155 | -0.2655 | 0.67291 | 0.74158 | 0.19226 | 0.81024 | 0.26093 | -0.050354 | 0.041199 | -122.5525 | 0.11444 | 0.24262 | -0.050354 | 0.29297 | 0 | 0.74158 | 122.6212 | 0.16479 | 0.31586 | 122.8775 | 122.9095 | 122.8088 | 122.8592 | -122.8867 | -122.8683 | 122.5525 | 0.2655 | 3.0121 | 1.268
3193.1719 | 123.0011 | -54.2816 | 68.5867 | -0.11398 | -0.0017281 | 0.060744 | 0.068404 | 0.0022964 | 0.0045417 | 0.007558 | 0.016968 | 0.0013159 | 0.002777 | -0.00036738 | -0.0025741 | -0.0068615 | 0.0015209 | -51.2375 | 68.5593 | -54.3274 | 68.3212 | -53.5583 | -54.0894 | -53.5355 | -53.009 | 68.5684 | -54.2999 | -53.9978 | -54.1763 | -54.3503 | -54.0207 | -0.045777 | -0.027466 | -0.2655 | 0.72327 | 0.74616 | 0.19226 | 0.79193 | 0.23804 | -0.018311 | -0.018311 | -122.5845 | 0.10529 | 0.26093 | -0.068665 | 0.27924 | -0.050354 | 0.76904 | 122.6486 | 0.1236 | 0.30212 | 122.8867 | 122.8683 | 122.8409 | 122.85 | -122.9141 | -122.8867 | 122.6028 | 0.28381 | 3.0441 | 1.2726
3194.1719 | 122.9553 | -54.2679 | 68.5593 | -0.060578 | -0.0021555 | 0.060744 | 0.069472 | 0.0012284 | 0.00091009 | 0.0037128 | 0.023071 | 0.0015295 | 0.0019226 | -0.0020764 | -0.0027877 | -0.0047253 | 0.00066654 | -51.2375 | 68.5638 | -54.332 | 68.3212 | -53.5492 | -54.0894 | -53.5172 | -52.9907 | 68.5776 | -54.2908 | -54.007 | -54.1626 | -54.3365 | -54.0207 | -0.064087 | 0.004578 | -0.23804 | 0.71869 | 0.75073 | 0.17853 | 0.81482 | 0.24262 | -0.022888 | 0.018311 | -122.5662 | 0.10528 | 0.24719 | -0.068665 | 0.27008 | -0.045777 | 0.78278 | 122.6532 | 0.12817 | 0.28381 | 122.8958 | 122.8683 | 122.8317 | 122.8455 | -122.8912 | -122.85 | 122.5891 | 0.26093 | 3.0304 | 1.2772
3195.1719 | 122.9645 | -54.2542 | 68.5593 | -0.068207 | -0.00023294 | 0.062453 | 0.068618 | -0.0011214 | 0.0019781 | 0.0028582 | 0.026123 | 3.4148e-05 | 0.0029906 | 0.00070062 | -0.0021469 | -0.0047253 | -0.0010425 | -51.2329 | 68.573 | -54.2999 | 68.3304 | -53.5767 | -54.0756 | -53.508 | -52.9953 | 68.6005 | -54.2816 | -54.0115 | -54.1397 | -54.3182 | -54.0115 | -0.045777 | 0.013733 | -0.22888 | 0.67749 | 0.74615 | 0.17853 | 0.79193 | 0.2243 | -0.027466 | 0.041199 | -122.5708 | 0.11444 | 0.24261 | -0.064087 | 0.27008 | -0.036621 | 0.72327 | 122.6303 | 0.14191 | 0.27008 | 122.8729 | 122.8821 | 122.8271 | 122.8546 | -122.8592 | -122.8409 | 122.5845 | 0.24261 | 3.0212 | 1.2589
3196.1719 | 122.9004 | -54.2587 | 68.5226 | -0.052948 | -0.00044654 | 0.062025 | 0.069686 | 0.00058737 | 0.0019781 | 0.0047808 | 0.010864 | 0.00088875 | 0.0019226 | -0.0044262 | -0.0023605 | -0.0049389 | -0.0012561 | -51.2192 | 68.5822 | -54.3228 | 68.3258 | -53.5492 | -54.0802 | -53.5217 | -52.9816 | 68.6096 | -54.277 | -54.0024 | -54.158 | -54.3457 | -54.0527 | -0.064087 | 0.059509 | -0.19684 | 0.70953 | 0.737 | 0.17853 | 0.80109 | 0.24262 | -0.018311 | 0.086975 | -122.525 | 0.10071 | 0.20599 | -0.086975 | 0.22431 | -0.068664 | 0.77362 | 122.6486 | 0.11902 | 0.27466 | 122.905 | 122.8867 | 122.8409 | 122.8683 | -122.8455 | -122.7997 | 122.5845 | 0.25635 | 3.0396 | 1.2772
3197.1719 | 122.9736 | -54.2633 | 68.5822 | -0.037689 | 0.0012625 | 0.060957 | 0.068618 | 0.0022964 | 0.0032599 | 0.0062762 | 0.047485 | 0.0013159 | 0.002777 | 0.00027342 | -0.0019333 | -0.0055799 | 0.00045294 | -51.2558 | 68.6005 | -54.3137 | 68.2983 | -53.6224 | -54.071 | -53.54 | -53.0365 | 68.6096 | -54.2679 | -54.0115 | -54.1489 | -54.3457 | -54.0344 | -0.050354 | 0.018311 | -0.28381 | 0.64087 | 0.72327 | 0.19226 | 0.77362 | 0.24262 | -0.004577 | 0.027466 | -122.5937 | 0.11444 | 0.22888 | -0.082397 | 0.23346 | -0.07782 | 0.69122 | 122.612 | 0.11902 | 0.25635 | 122.9141 | 122.8775 | 122.8638 | 122.8729 | -122.8958 | -122.85 | 122.5616 | 0.25177 | 3.0075 | 1.2268
3198.1719 | 122.9324 | -54.2313 | 68.6325 | -0.052948 | -0.0025827 | 0.061385 | 0.068404 | 0.00016017 | 0.0026191 | 0.0060626 | 0.032227 | 0.0011023 | 0.001068 | -0.00058098 | -0.0023605 | -0.0057935 | -0.0010425 | -51.2512 | 68.573 | -54.3182 | 68.2892 | -53.6041 | -54.0894 | -53.5263 | -53.0548 | 68.6142 | -54.2725 | -54.0298 | -54.1443 | -54.3365 | -54.0298 | -0.086975 | -0.059509 | -0.34332 | 0.62714 | 0.70496 | 0.14191 | 0.79193 | 0.22888 | -0.041199 | -0.01831 | -122.6624 | 0.086975 | 0.20142 | -0.10529 | 0.24262 | -0.064087 | 0.71411 | 122.6074 | 0.12817 | 0.24262 | 122.8912 | 122.8867 | 122.8043 | 122.8455 | -122.9507 | -122.905 | 122.5204 | 0.20142 | 2.98 | 1.1765
3199.1719 | 122.9736 | -54.2404 | 68.5867 | -0.022431 | -0.00066014 | 0.061598 | 0.070113 | -0.0015488 | 0.0015509 | 0.005849 | 0.0078126 | 0.00088875 | 0.0019226 | -0.001222 | -0.0023605 | -0.0053663 | 0.0023755 | -51.2146 | 68.573 | -54.3228 | 68.335 | -53.5858 | -54.0665 | -53.5172 | -53.0045 | 68.5959 | -54.2633 | -54.007 | -54.1306 | -54.332 | -54.0115 | -0.082398 | -0.013733 | -0.25177 | 0.6546 | 0.72327 | 0.17395 | 0.80566 | 0.25635 | -0.022889 | 0.009155 | -122.5937 | 0.10986 | 0.22888 | -0.091553 | 0.25177 | -0.068664 | 0.737 | 122.6578 | 0.13275 | 0.25635 | 122.8958 | 122.8592 | 122.8134 | 122.8363 | -122.9095 | -122.85 | 122.5754 | 0.23346 | 3.0258 | 1.236
3200.1719 | 122.9828 | -54.2496 | 68.5822 | -0.052948 | 0.00083526 | 0.060744 | 0.0699 | 0.00016017 | 0.0021917 | 0.0017902 | 0.035278 | 0.0013159 | -0.00042717 | -0.0031446 | -0.0017197 | -0.0038709 | 0.0025891 | -51.2329 | 68.5959 | -54.3137 | 68.3212 | -53.6041 | -54.0848 | -53.5263 | -53.009 | 68.6005 | -54.2587 | -54.0024 | -54.1489 | -54.3228 | -54.0207 | -0.064087 | 0.013733 | -0.26093 | 0.64545 | 0.72327 | 0.16479 | 0.78735 | 0.22888 | -0.009155 | 0.018311 | -122.5845 | 0.10071 | 0.22888 | -0.073242 | 0.23804 | -0.064087 | 0.70953 | 122.6349 | 0.10986 | 0.25635 | 122.9095 | 122.8592 | 122.8455 | 122.85 | -122.8958 | -122.8409 | 122.5708 | 0.24719 | 3.0167 | 1.2405
3201.1719 | 122.9599 | -54.2175 | 68.573 | -0.12161 | 0.0021171 | 0.06053 | 0.069472 | -5.343e-05 | 0.0024053 | 0.005849 | -0.022705 | 0.00067495 | 0.00064083 | 0.0026232 | -0.0019333 | -0.0068615 | -0.0027515 | -51.1917 | 68.5913 | -54.3182 | 68.3395 | -53.5538 | -54.0573 | -53.5034 | -52.977 | 68.6508 | -54.2633 | -53.9932 | -54.1443 | -54.3228 | -54.0115 | -0.10071 | 0.018311 | -0.23346 | 0.66376 | 0.71411 | 0.16022 | 0.81482 | 0.26093 | -0.045777 | 0.07782 | -122.5662 | 0.073242 | 0.20599 | -0.10529 | 0.25177 | -0.059509 | 0.76447 | 122.6578 | 0.11902 | 0.27008 | 122.9095 | 122.9141 | 122.8088 | 122.8683 | -122.8912 | -122.8363 | 122.5571 | 0.2243 | 3.0258 | 1.2405
3202.1719 | 122.9691 | -54.2313 | 68.6005 | -0.037689 | 0.0010489 | 0.061385 | 0.068618 | -0.0015488 | 0.0013373 | 0.0032856 | 0.047485 | 0.00088875 | 0.0025634 | 0.0019824 | -0.0021469 | -0.0075025 | 0.00088014 | -51.2329 | 68.5684 | -54.3045 | 68.3075 | -53.5904 | -54.0802 | -53.5217 | -53.0273 | 68.6142 | -54.277 | -54.0298 | -54.1443 | -54.3457 | -54.0344 | -0.073242 | -0.032044 | -0.29297 | 0.64087 | 0.70953 | 0.15106 | 0.78278 | 0.2243 | -0.045777 | 0.013733 | -122.6303 | 0.086975 | 0.19684 | -0.11444 | 0.24262 | -0.068664 | 0.71411 | 122.612 | 0.13275 | 0.24719 | 122.8729 | 122.8912 | 122.7997 | 122.8455 | -122.905 | -122.8775 | 122.5388 | 0.20142 | 2.9984 | 1.2039
3203.1719 | 122.9828 | -54.2633 | 68.5822 | -0.075836 | 0.0010489 | 0.060957 | 0.068191 | -0.0015488 | 0.0032599 | 0.00414 | 0.029175 | 0.0019567 | 0.00021363 | 0.00070062 | -0.0038559 | -0.0053663 | -0.0018971 | -51.1963 | 68.6096 | -54.3228 | 68.3166 | -53.5767 | -54.071 | -53.508 | -53.0136 | 68.6279 | -54.2679 | -53.9932 | -54.1214 | -54.3182 | -54.0024 | -0.059509 | 0.027466 | -0.2655 | 0.68665 | 0.75531 | 0.19226 | 0.81482 | 0.25177 | -0.004577 | 0.045777 | -122.5754 | 0.14191 | 0.26093 | -0.054931 | 0.2655 | -0.050354 | 0.74616 | 122.6395 | 0.14648 | 0.27466 | 122.9324 | 122.8958 | 122.8729 | 122.8912 | -122.905 | -122.85 | 122.58 | 0.27008 | 3.067 | 1.2497
3204.1719 | 122.9279 | -54.1992 | 68.6142 | -0.052948 | 0.0014761 | 0.061598 | 0.067763 | -0.0032578 | 0.0026191 | 0.0047808 | -0.0074462 | 0.00046135 | 0.0012818 | -0.0035718 | -0.0012925 | -0.0053663 | 0.00088014 | -51.2146 | 68.6371 | -54.2862 | 68.2571 | -53.4119 | -53.8422 | -53.6087 | -52.9724 | 68.6234 | -54.2816 | -53.9886 | -54.126 | -54.332 | -54.0298 | -0.086975 | 0.022888 | -0.35706 | 0.78735 | 0.59051 | 0.35706 | 0.67749 | 0.44403 | -0.082397 | 0.009155 | -122.6028 | 0.073242 | 0.16937 | -0.13275 | 0.25177 | -0.050354 | 0.87433 | 122.5433 | 0.15564 | 0.29297 | 122.9233 | 122.905 | 122.8363 | 122.8226 | -122.9004 | -122.8958 | 122.4564 | 0.21057 | 2.9846 | 1.2268
3205.1719 | 122.8912 | -54.2221 | 68.6325 | -0.10635 | -1.9142e-05 | 0.061171 | 0.068832 | -0.0021896 | 0.00091009 | 0.0064898 | 0.050537 | 0.0015295 | 0.0040588 | -0.0065626 | -0.0025741 | -0.0064343 | -0.0016833 | -51.2009 | 68.605 | -54.2953 | 68.335 | -53.5492 | -54.071 | -53.4897 | -52.9907 | 68.6325 | -54.2358 | -54.0115 | -54.2999 | -54.3137 | -53.9886 | -0.073242 | -0.027465 | -0.29755 | 0.67291 | 0.73242 | 0.15106 | 0.80566 | 0.2243 | -0.013733 | 0 | -122.644 | -0.07782 | 0.23346 | -0.091553 | 0.24719 | -0.07782 | 0.74616 | 122.6303 | -0.064087 | 0.2243 | 122.9004 | 122.8683 | 122.8271 | 122.8546 | -122.9279 | -122.8683 | 122.5571 | 0.21057 | 3.0212 | 1.2314
3206.1719 | 122.9324 | -54.2221 | 68.6371 | -0.1445 | 0.0016899 | 0.060744 | 0.0699 | 0.0016556 | 0.0015509 | 0.0056354 | 0.023071 | 0.00067495 | 0.0023498 | -0.002931 | -0.0025741 | -0.0053663 | 0.00045294 | -51.2009 | 68.6508 | -54.3045 | 68.3487 | -53.5355 | -54.0619 | -53.4851 | -52.9999 | 68.66 | -54.2496 | -53.9795 | -54.1122 | -54.3045 | -54.007 | -0.082397 | 0.013733 | -0.28839 | 0.68665 | 0.737 | 0.16022 | 0.8194 | 0.24261 | -0.027466 | 0.022888 | -122.6166 | 0.10986 | 0.21515 | -0.082397 | 0.24262 | -0.054931 | 0.76904 | 122.6532 | 0.13733 | 0.27008 | 122.9553 | 122.9095 | 122.8729 | 122.8821 | -122.9416 | -122.8867 | 122.5708 | 0.24262 | 3.0212 | 1.2222
3207.1719 | 122.9233 | -54.2175 | 68.6371 | -0.091095 | 0.00062166 | 0.058821 | 0.069686 | -0.0017624 | 0.0015509 | 0.00414 | 0.044434 | 0.0013159 | 0.00085443 | -0.0069898 | -0.0032151 | -0.0057935 | -0.0010425 | -51.1688 | 68.6188 | -54.2633 | 68.486 | -53.6041 | -54.2633 | -53.5721 | -53.0273 | 68.6691 | -54.2496 | -53.9978 | -54.1306 | -54.3045 | -54.0024 | -0.045777 | -0.018311 | -0.15106 | 0.6134 | 0.64545 | -0.045777 | 0.69122 | 0 | -0.032044 | 0.032043 | -122.6349 | 0.086975 | 0.21515 | -0.086975 | 0.24719 | -0.054931 | 0.65918 | 122.7493 | 0.11902 | 0.25177 | 122.8821 | 122.9187 | 122.8363 | 122.8867 | -122.9004 | -122.8867 | 122.7036 | 0.21973 | 3.0487 | 1.1902
3208.1719 | 122.937 | -54.213 | 68.6462 | -0.068207 | -0.0021555 | 0.060744 | 0.069045 | -0.00090783 | 0.0011237 | 0.0032856 | 0.016968 | 0.00046135 | -0.00085457 | 0.0028368 | -0.0015061 | -0.0036573 | 0.0021619 | -51.1642 | 68.6554 | -54.2587 | 68.3807 | -53.5217 | -54.0436 | -53.4622 | -52.9633 | 68.6829 | -54.2221 | -54.0527 | -54.0527 | -54.3228 | -54.039 | -0.045776 | 0.009156 | -0.2655 | 0.69122 | 0.75073 | 0.16937 | 0.79651 | 0.21515 | -0.009155 | 0.036621 | -122.699 | 0.16022 | 0.17395 | -0.10986 | 0.18311 | -0.10071 | 0.737 | 122.6395 | 0.16937 | 0.16937 | 122.9141 | 122.905 | 122.8683 | 122.8958 | -122.905 | -122.8683 | 122.5937 | 0.16022 | 3.0487 | 1.2497
3209.1719 | 122.905 | -54.1992 | 68.692 | -0.068207 | -0.00066014 | 0.060957 | 0.0699 | -0.001976 | 0.0058233 | 0.0032856 | 0.02002 | 0.00046135 | 0.0025634 | 0.0036914 | -0.0023605 | -0.0049389 | -0.0012561 | -51.1459 | 68.6234 | -54.2358 | 68.367 | -53.5172 | -54.0527 | -53.4576 | -52.9678 | 68.6874 | -54.245 | -53.9749 | -54.0985 | -54.2953 | -54.0298 | -0.036621 | -0.068665 | -0.32501 | 0.68207 | 0.74158 | 0.14648 | 0.7782 | 0.18311 | -0.045776 | -0.004578 | -122.6669 | 0.10071 | 0.16937 | -0.09613 | 0.21515 | -0.050354 | 0.71869 | 122.6028 | 0.14648 | 0.27008 | 122.8592 | 122.9324 | 122.8226 | 122.8867 | -122.9279 | -122.937 | 122.5662 | 0.2243 | 3.0533 | 1.2314
3210.1719 | 122.9507 | -54.1901 | 68.6371 | -0.022431 | 0.0010489 | 0.062453 | 0.071609 | -0.0028304 | 0.0028327 | 0.0039264 | 0.02002 | 0.0017431 | 2.8e-08 | 0.00070062 | -0.0021469 | -0.0060071 | 0.0013073 | -51.1459 | 68.6646 | -54.2633 | 68.3899 | -53.6545 | -54.1946 | -53.4622 | -52.9861 | 68.692 | -54.2313 | -53.9658 | -54.1168 | -54.2999 | -53.9932 | -0.073243 | 0.027466 | -0.24719 | 0.53558 | 0.72784 | -0.004578 | 0.80109 | 0.068665 | -0.041199 | 0.054932 | -122.6028 | 0.073242 | 0.19684 | -0.10986 | 0.23804 | -0.068665 | 0.60883 | 122.6532 | 0.11444 | 0.2655 | 122.9279 | 122.9233 | 122.8546 | 122.8821 | -122.9004 | -122.8683 | 122.58 | 0.2243 | 3.0441 | 1.2039
3211.1719 | 122.9187 | -54.1901 | 68.66 | -0.068207 | 0.00083526 | 0.060744 | 0.070541 | 0.0010148 | 0.0036871 | 0.0049946 | 0.035278 | 0.0030249 | -0.00021357 | -0.003999 | -0.00065151 | -0.0068615 | -0.00040166 | -51.0773 | 68.6096 | -54.2358 | 68.4174 | -53.4393 | -53.9566 | -53.4027 | -52.9083 | 68.6783 | -54.2084 | -53.9383 | -54.0939 | -54.2633 | -53.9703 | -0.045777 | -0.050354 | -0.24262 | 0.75073 | 0.78735 | 0.23346 | 0.83313 | 0.27924 | -0.018311 | 0.018311 | -122.5983 | 0.09613 | 0.21973 | -0.073243 | 0.23804 | -0.054932 | 0.79651 | 122.6532 | 0.11444 | 0.27008 | 122.8455 | 122.8867 | 122.7997 | 122.8683 | -122.8958 | -122.8683 | 122.6074 | 0.25177 | 3.1128 | 1.2817
3212.1719 | 122.9279 | -54.2038 | 68.6142 | -0.060578 | -1.9142e-05 | 0.063521 | 0.072036 | -5.343e-05 | 0.0017645 | 0.0052082 | -0.050171 | 0.0013159 | 0.001709 | -0.0037854 | -0.0034287 | -0.0036573 | -0.0023243 | -51.1368 | 68.6096 | -54.2953 | 68.3395 | -53.5355 | -54.0939 | -53.5034 | -52.9861 | 68.6417 | -54.2587 | -54.007 | -54.1763 | -54.364 | -54.0207 | -0.091553 | -0.004578 | -0.27466 | 0.66833 | 0.70038 | 0.10986 | 0.79193 | 0.20142 | -0.054932 | 0.027466 | -122.6212 | 0.027465 | 0.1831 | -0.16022 | 0.23804 | -0.10529 | 0.75989 | 122.6349 | 0.082397 | 0.25177 | 122.905 | 122.9004 | 122.8134 | 122.8455 | -122.9095 | -122.8729 | 122.5433 | 0.19684 | 3.067 | 1.2177
3213.1719 | 123.0011 | -54.1672 | 68.6325 | -0.068207 | 0.00062166 | 0.062453 | 0.067763 | -5.343e-05 | 0.0026191 | 0.0049946 | 0.053589 | -0.00017945 | -0.00085457 | 0.00048702 | -0.0036423 | -0.0066479 | 2.554e-05 | -51.0635 | 68.6188 | -54.2084 | 68.4631 | -53.3844 | -53.9154 | -53.3569 | -52.8351 | 68.6508 | -54.2038 | -53.8971 | -54.0161 | -54.1718 | -53.9062 | -0.041199 | -0.013733 | -0.16937 | 0.78278 | 0.81024 | 0.25177 | 0.85144 | 0.29297 | -0.036621 | 0.018311 | -122.5296 | 0.15106 | 0.26093 | -0.004578 | 0.29755 | 0.032043 | 0.82397 | 122.6715 | 0.18768 | 0.3067 | 122.8271 | 122.8546 | 122.7859 | 122.818 | -122.8409 | -122.8363 | 122.6303 | 0.27008 | 3.1036 | 1.3321
3214.1719 | 122.9599 | -54.1901 | 68.66 | -0.014801 | 0.00083526 | 0.059889 | 0.068404 | 0.001442 | 0.0030463 | 0.0054218 | 0.0047608 | 3.4148e-05 | 0.001068 | -0.0054944 | -0.0027877 | -0.0053663 | -0.00082886 | -51.0727 | 68.6188 | -54.2221 | 68.4311 | -53.4302 | -53.9749 | -53.3844 | -52.8854 | 68.6508 | -54.1809 | -53.9474 | -54.0619 | -54.2404 | -53.9474 | -0.032044 | -0.041199 | -0.22888 | 0.75989 | 0.80566 | 0.21515 | 0.83771 | 0.24719 | 0.009155 | -0.009155 | -122.6074 | 0.12817 | 0.24261 | -0.050354 | 0.23346 | -0.059509 | 0.79193 | 122.6532 | 0.11902 | 0.23346 | 122.8409 | 122.8317 | 122.8088 | 122.8409 | -122.8821 | -122.8409 | 122.6212 | 0.24261 | 3.1174 | 1.3046
3215.1719 | 122.9553 | -54.1718 | 68.6279 | -0.083466 | 0.0016899 | 0.06288 | 0.067123 | 0.0040054 | 0.0017645 | 0.0043536 | 0.023071 | 0.00046135 | 2.8e-08 | -0.0037854 | -0.0023605 | -0.0066479 | -0.00040166 | -51.0498 | 68.6325 | -54.2267 | 68.4631 | -53.4119 | -53.9383 | -53.3707 | -52.8488 | 68.6737 | -54.1946 | -53.9062 | -54.0253 | -54.2084 | -53.9337 | -0.054932 | 0.004577 | -0.1648 | 0.75989 | 0.80109 | 0.23346 | 0.85602 | 0.28839 | -0.022888 | 0.045776 | -122.5342 | 0.14648 | 0.23804 | -0.036621 | 0.26093 | -0.013733 | 0.81482 | 122.6898 | 0.16937 | 0.28839 | 122.8592 | 122.8683 | 122.8043 | 122.8455 | -122.8546 | -122.8226 | 122.6349 | 0.2655 | 3.1219 | 1.3229
3216.1719 | 123.0286 | -54.1443 | 68.6462 | -0.1445 | 0.00040806 | 0.061171 | 0.068404 | -0.0015488 | 0.0036871 | 0.0060626 | 0.053589 | 0.00088875 | 0.0019226 | -0.0035718 | -0.0047103 | -0.0060071 | 0.00088014 | -51.0269 | 68.6325 | -54.1901 | 68.4998 | -53.3798 | -53.9017 | -53.3249 | -52.8076 | 68.6554 | -54.1718 | -53.8605 | -53.9841 | -54.1489 | -53.8971 | -0.045776 | -0.013733 | -0.14648 | 0.76447 | 0.8194 | 0.24262 | 0.86517 | 0.28839 | -0.027466 | 0.009156 | -122.5067 | 0.16022 | 0.24719 | -0.004578 | 0.27466 | 0.022888 | 0.81024 | 122.6898 | 0.18768 | 0.31128 | 122.8226 | 122.8271 | 122.7768 | 122.7997 | -122.8363 | -122.818 | 122.644 | 0.28381 | 3.1174 | 1.3367
3217.1719 | 122.9507 | -54.1489 | 68.6646 | -0.037689 | 0.00062166 | 0.061171 | 0.071181 | -0.0017624 | 0.0019781 | 0.002431 | 0.0078126 | -0.00039305 | 0.001709 | 0.0041186 | -0.0027877 | -0.0057935 | -0.0012561 | -51.0269 | 68.6508 | -54.1901 | 68.4631 | -53.4073 | -53.9474 | -53.3661 | -52.8671 | 68.7103 | -54.1718 | -53.9062 | -54.0298 | -54.2313 | -53.9429 | -0.041198 | -0.013733 | -0.20142 | 0.74158 | 0.78278 | 0.20142 | 0.82397 | 0.24261 | -0.022888 | 0.045776 | -122.5708 | 0.11902 | 0.20599 | -0.082397 | 0.22888 | -0.059509 | 0.78278 | 122.6532 | 0.14191 | 0.2655 | 122.8409 | 122.8821 | 122.7997 | 122.8592 | -122.8546 | -122.8363 | 122.612 | 0.24262 | 3.1219 | 1.2817
3218.1719 | 123.0377 | -54.1122 | 68.6325 | -0.12161 | -0.0015145 | 0.061598 | 0.068191 | -0.0013352 | 0.0030463 | 0.0037128 | 0.035278 | 0.0011023 | 0.0014954 | -0.0050672 | -0.0023605 | -0.0053663 | -0.0010425 | -50.8209 | 68.7057 | -54.1901 | 68.4952 | -53.3249 | -53.92 | -53.3203 | -52.771 | 68.6462 | -54.158 | -53.833 | -53.9474 | -54.1397 | -53.8559 | -0.077819 | 0.073243 | -0.13733 | 0.78735 | 0.79193 | 0.19226 | 0.86975 | 0.27008 | -0.045776 | 0.013733 | -122.4655 | 0.16479 | 0.25635 | -0.027465 | 0.30212 | 0.018311 | 0.86517 | 122.6852 | 0.21057 | 0.32501 | 122.8958 | 122.8043 | 122.818 | 122.7585 | -122.8226 | -122.7905 | 122.6074 | 0.27924 | 3.2913 | 1.3412
3219.1719 | 123.0469 | -54.0939 | 68.6554 | -0.098725 | 0.0014761 | 0.061385 | 0.069472 | -0.0030442 | 0.0011237 | 0.0071308 | 0.053589 | 0.0013159 | -0.00021357 | -0.00015378 | -0.0027877 | -0.0060071 | -0.0014697 | -50.9811 | 68.6417 | -54.1718 | 68.541 | -53.0182 | -53.7552 | -53.5263 | -52.739 | 68.6646 | -54.158 | -53.8147 | -53.9337 | -54.126 | -53.8651 | -0.07782 | -0.013733 | -0.11444 | 1.0757 | 0.56763 | 0.33875 | 0.64545 | 0.41657 | -0.064087 | 0.009155 | -122.4701 | 0.16022 | 0.22888 | -0.032044 | 0.29297 | 0.032043 | 1.1536 | 122.7127 | 0.2243 | 0.34332 | 122.8134 | 122.8226 | 122.7356 | 122.7585 | -122.8271 | -122.8134 | 122.6349 | 0.27924 | 3.1128 | 1.355
3220.1719 | 123.0286 | -54.1168 | 68.6783 | -0.098725 | 0.0023307 | 0.060957 | 0.070327 | -0.00026703 | 0.0015509 | 0.0071308 | 0.029175 | 0.0021703 | 0.0023498 | -0.0027174 | -0.0036423 | -0.0053663 | -0.0036059 | -51.004 | 68.66 | -54.1672 | 68.5226 | -53.3432 | -53.8834 | -53.3066 | -52.771 | 68.7012 | -54.1489 | -53.8193 | -53.9474 | -54.1443 | -53.8605 | -0.050354 | -0.018311 | -0.15564 | 0.77362 | 0.81024 | 0.23346 | 0.8606 | 0.28381 | -0.032044 | 0.022888 | -122.4976 | 0.16937 | 0.25635 | -0.027466 | 0.28839 | 0.004578 | 0.82397 | 122.6898 | 0.20142 | 0.32959 | 122.8271 | 122.85 | 122.7768 | 122.818 | -122.8455 | -122.8271 | 122.6395 | 0.29755 | 3.1128 | 1.3458
3221.1719 | 123.0286 | -54.1168 | 68.692 | 0.00045798 | 0.00083526 | 0.060744 | 0.067977 | 0.0012284 | 0.00048269 | 0.0049946 | 0.03833 | 0.0017431 | 0.00064083 | -0.0069898 | -0.0034287 | -0.0053663 | -0.0025379 | -51.0406 | 68.6462 | -54.2038 | 68.541 | -53.3478 | -53.8834 | -53.302 | -52.7573 | 68.6829 | -54.1397 | -53.801 | -53.9337 | -54.1214 | -53.8559 | -0.086975 | -0.045777 | -0.15106 | 0.76904 | 0.81482 | 0.23346 | 0.90179 | 0.32043 | -0.022888 | -0.009156 | -122.493 | 0.18311 | 0.26093 | -0.004578 | 0.28381 | 0.01831 | 0.85602 | 122.7448 | 0.20599 | 0.33875 | 122.85 | 122.8226 | 122.7631 | 122.7997 | -122.8958 | -122.8317 | 122.6578 | 0.31586 | 3.0762 | 1.3596
3222.1719 | 123.0377 | -54.0939 | 68.6691 | -0.083466 | -0.00044654 | 0.057753 | 0.070541 | -0.0043258 | 0.00091009 | 0.0026446 | 0.001709 | 0.0028113 | 0.00064083 | 0.002196 | -0.0034287 | -0.0064343 | -0.0012561 | -50.8621 | 68.6966 | -54.1397 | 68.5318 | -53.3569 | -53.8651 | -53.2791 | -52.7252 | 68.6874 | -54.1397 | -53.7964 | -53.9337 | -54.1077 | -53.8284 | -0.045776 | 0.027466 | -0.13733 | 0.737 | 0.81482 | 0.22888 | 0.8606 | 0.27466 | -0.045776 | 0.018311 | -122.4655 | 0.16022 | 0.2655 | -0.013733 | 0.31128 | 0.032043 | 0.78278 | 122.6715 | 0.20599 | 0.34332 | 122.8363 | 122.8271 | 122.7905 | 122.7814 | -122.8088 | -122.8088 | 122.6257 | 0.29755 | 3.2318 | 1.3687
3223.1719 | 123.0469 | -54.0985 | 68.6783 | -0.075836 | 0.00083526 | 0.062666 | 0.068191 | -0.0026168 | 0.00026909 | 0.0043536 | -0.053223 | -0.00017945 | 0.00021363 | 0.0013416 | -0.0021469 | -0.0053663 | -0.0021107 | -50.9308 | 68.6737 | -54.1809 | 68.486 | -53.0228 | -53.6407 | -53.4805 | -52.6886 | 68.6966 | -54.158 | -53.7827 | -53.9062 | -54.1031 | -53.8284 | -0.082397 | -0.004578 | -0.19226 | 1.0757 | 0.61798 | 0.45776 | 0.70038 | 0.54016 | -0.059509 | 0.01831 | -122.4609 | 0.19226 | 0.27008 | -0.004577 | 0.32959 | 0.054932 | 1.1581 | 122.6669 | 0.25177 | 0.37537 | 122.8546 | 122.8546 | 122.7722 | 122.7951 | -122.8592 | -122.8363 | 122.5845 | 0.31586 | 3.1677 | 1.4099
3224.1719 | 123.0331 | -54.1077 | 68.7057 | -0.037689 | 0.0010489 | 0.064375 | 0.068404 | -0.00069423 | 0.0026191 | 0.0060626 | 0.016968 | 0.00067495 | -0.0014954 | -0.0018628 | -0.0015061 | -0.0055799 | 0.0021619 | -50.9399 | 68.6737 | -54.1672 | 68.5364 | -53.3203 | -53.8742 | -53.2883 | -52.7618 | 68.7149 | -54.1168 | -53.7872 | -53.92 | -54.1122 | -53.8467 | -0.059509 | -0.032044 | -0.16937 | 0.78735 | 0.8194 | 0.23346 | 0.87891 | 0.29297 | -0.009155 | 0.009155 | -122.493 | 0.18768 | 0.26093 | -0.004578 | 0.27008 | 0.004577 | 0.84686 | 122.7036 | 0.19684 | 0.32959 | 122.8409 | 122.8317 | 122.7814 | 122.8226 | -122.8729 | -122.8226 | 122.644 | 0.32044 | 3.1677 | 1.3458
3225.1719 | 123.0377 | -54.0665 | 68.6874 | -0.045319 | 0.00019446 | 0.061171 | 0.066268 | -0.0011214 | 0.0017645 | 0.005849 | 0.029175 | 0.00024775 | -0.0012818 | 0.0051868 | -0.0038559 | -0.0042981 | -0.0018971 | -50.9583 | 68.6783 | -54.1763 | 68.5638 | -53.2974 | -53.8422 | -53.2654 | -52.6794 | 68.7103 | -54.1351 | -53.7689 | -53.9246 | -53.7872 | -53.6041 | -0.10986 | -0.009155 | -0.1236 | 0.76904 | 0.80109 | 0.2243 | 0.91095 | 0.33417 | -0.068665 | 0.022888 | -122.4564 | 0.14191 | 0.46234 | 0.27924 | 0.53101 | 0.3479 | 0.87891 | 122.7402 | 0.21057 | 0.36621 | 122.8546 | 122.8455 | 122.7448 | 122.7768 | -122.8638 | -122.8226 | 122.6303 | 0.29755 | 3.1082 | 1.387
3226.1719 | 123.0743 | -54.0527 | 68.692 | -0.11398 | 0.00062166 | 0.061812 | 0.067336 | -0.0017624 | 0.0015509 | 0.0015766 | 0.02002 | 0.0013159 | 0.0021362 | -0.0033582 | -0.0025741 | -0.0049389 | -0.0010425 | -50.9399 | 68.6783 | -54.1763 | 68.5593 | -53.2791 | -53.8422 | -53.2608 | -52.7069 | 68.7012 | -54.0985 | -53.7369 | -53.8742 | -54.0482 | -53.8101 | -0.1236 | -0.013733 | -0.13275 | 0.77362 | 0.79193 | 0.21057 | 0.91553 | 0.33417 | -0.045777 | 0.009155 | -122.4289 | 0.17853 | 0.24261 | 0.004577 | 0.28839 | 0.050354 | 0.89722 | 122.7356 | 0.2243 | 0.36163 | 122.8546 | 122.7997 | 122.731 | 122.7539 | -122.8683 | -122.7905 | 122.612 | 0.31586 | 3.1128 | 1.3458
3227.1719 | 123.024 | -54.0802 | 68.692 | -0.075836 | 0.0023307 | 0.061598 | 0.0699 | 0.0022964 | 0.0049689 | 0.0022174 | 0.016968 | -0.00060665 | 0.00021363 | 0.0019824 | -0.0032151 | -0.0070753 | -0.00082886 | -50.9354 | 68.6829 | -54.1214 | 68.5867 | -53.2425 | -53.9246 | -53.2974 | -52.7206 | 68.7103 | -54.1351 | -53.7598 | -53.9017 | -54.0939 | -53.8284 | -0.041199 | -0.009156 | -0.10529 | 0.83771 | 0.78278 | 0.15564 | 0.82397 | 0.19684 | -0.054932 | 0.01831 | -122.4518 | 0.17853 | 0.25177 | -0.013733 | 0.3067 | 0.041199 | 0.87891 | 122.7081 | 0.23346 | 0.37537 | 122.8043 | 122.8455 | 122.7631 | 122.7905 | -122.8134 | -122.8271 | 122.6669 | 0.32043 | 3.1448 | 1.3596
3228.1719 | 123.0377 | -54.0756 | 68.6829 | -0.083466 | -0.00044654 | 0.061598 | 0.067977 | 0.00058737 | 0.0017645 | 0.0071308 | 0.0047608 | 0.00067495 | 0.0023498 | -0.00058098 | -0.0025741 | -0.0060071 | -0.0016833 | -50.8987 | 68.6783 | -54.1397 | 68.5638 | -53.2654 | -53.8147 | -52.9724 | -52.89 | 68.7332 | -54.1306 | -53.7598 | -53.8971 | -54.0665 | -53.8101 | -0.064086 | -0.004577 | -0.11902 | 0.81024 | 1.1032 | 0.26093 | 1.1673 | 0.32501 | -0.054931 | 0.050354 | -122.4426 | 0.17853 | 0.2655 | 0.009156 | 0.32043 | 0.064087 | 0.87433 | 122.7036 | 0.23346 | 0.37079 | 122.818 | 122.8638 | 122.7539 | 122.8088 | -122.8226 | -122.8134 | 122.6395 | 0.31586 | 3.1769 | 1.1856
3229.1719 | 123.0194 | -54.0848 | 68.6691 | -0.068207 | 0.0016899 | 0.060103 | 0.068618 | -0.0017624 | 0.0039007 | 0.00414 | -0.0013428 | 0.0017431 | -0.0023498 | -0.006349 | -0.0032151 | -0.0079297 | 2.554e-05 | -50.9216 | 68.6737 | -54.1351 | 68.5913 | -53.2471 | -53.8055 | -53.2333 | -52.7023 | 68.7515 | -54.0848 | -53.8651 | -53.9932 | -53.9978 | -53.7827 | -0.050354 | 0.004578 | -0.077819 | 0.83771 | 0.85144 | 0.27924 | 0.90179 | 0.32959 | 0 | 0.082398 | -122.5342 | 0.091553 | 0.30212 | 0.086975 | 0.30212 | 0.086975 | 0.88806 | 122.7264 | 0.091553 | 0.21973 | 122.8088 | 122.8363 | 122.7585 | 122.8363 | -122.8043 | -122.7539 | 122.6761 | 0.21973 | 3.1631 | 1.3824
3230.1719 | 123.1338 | -54.0344 | 68.7653 | -0.052948 | -0.00023294 | 0.060316 | 0.070754 | -0.0021896 | 0.0043281 | 0.0047808 | 0.001709 | -0.0023157 | 0.00021363 | -0.0072034 | -0.0034287 | -0.0049389 | 2.554e-05 | -50.9216 | 68.6829 | -54.1306 | 68.5776 | -53.2425 | -53.8055 | -53.2471 | -52.6703 | 68.7195 | -54.1031 | -53.746 | -53.8788 | -54.0482 | -53.8239 | -0.09613 | -0.082398 | -0.18768 | 0.79193 | 0.78735 | 0.22888 | 0.88348 | 0.32501 | -0.068664 | -0.045777 | -122.5113 | 0.15564 | 0.21057 | -0.013733 | 0.27923 | 0.054931 | 0.88806 | 122.7081 | 0.2243 | 0.35706 | 122.8134 | 122.8226 | 122.7173 | 122.7539 | -122.8958 | -122.8683 | 122.612 | 0.28839 | 3.1128 | 1.3641
3231.1719 | 123.024 | -54.0665 | 68.7103 | 0.038605 | 0.0010489 | 0.064589 | 0.070754 | 0.00016017 | 0.0039007 | 0.0043536 | -0.010498 | 0.0011023 | 0.00042723 | 0.0013416 | -0.0025741 | -0.0053663 | 2.554e-05 | -51.1368 | 68.6783 | -54.1489 | 68.5913 | -53.2883 | -53.8284 | -53.2516 | -52.7069 | 68.7195 | -54.1031 | -53.7735 | -53.8971 | -54.0756 | -53.7964 | -0.082398 | -0.032043 | -0.11902 | 0.7782 | 0.81482 | 0.23804 | 0.89722 | 0.32044 | -0.036621 | 0.009155 | -122.4838 | 0.16937 | 0.27008 | -0.009156 | 0.3067 | 0.027465 | 0.8606 | 122.7402 | 0.20599 | 0.32959 | 122.8271 | 122.8226 | 122.7448 | 122.7859 | -122.8592 | -122.8134 | 122.6578 | 0.29297 | 2.9297 | 1.3596
3232.1719 | 123.0011 | -54.0756 | 68.7378 | -0.10635 | 0.0025443 | 0.06288 | 0.074813 | 0.00037377 | 0.0015509 | 0.0064898 | -0.12036 | 0.0011023 | -0.0010682 | 0.0024096 | -0.0012925 | -0.0040845 | -0.0018971 | -50.9262 | 68.7424 | -54.1763 | 68.5181 | -53.3524 | -53.9246 | -53.3524 | -52.771 | 68.7744 | -54.126 | -53.7872 | -54.007 | -54.2953 | -53.9612 | -0.10071 | 0.004578 | -0.21973 | 0.72327 | 0.72327 | 0.15106 | 0.82397 | 0.25177 | -0.050354 | 0.036621 | -122.525 | 0.068665 | 0.11444 | -0.21973 | 0.16479 | -0.16937 | 0.82397 | 122.6944 | 0.11902 | 0.33875 | 122.9187 | 122.9004 | 122.818 | 122.85 | -122.9141 | -122.8638 | 122.5937 | 0.28839 | 3.1494 | 1.3046
3233.1719 | 123.0606 | -54.071 | 68.7012 | -0.091095 | -0.0032235 | 0.060316 | 0.067123 | -0.00069423 | 0.0026191 | 0.0047808 | 0.0078126 | -0.00017945 | 0.0029906 | -0.0027174 | -0.0017197 | -0.0075025 | 0.0038709 | -50.9171 | 68.7057 | -54.158 | 68.5684 | -53.2745 | -53.8193 | -53.2425 | -52.7023 | 68.7378 | -54.0894 | -53.7094 | -53.8651 | -54.039 | -53.7735 | -0.086975 | 0.004578 | -0.13275 | 0.79651 | 0.82855 | 0.25177 | 0.91553 | 0.33875 | -0.01831 | 0.036621 | -122.4106 | 0.20599 | 0.29755 | 0.032044 | 0.31586 | 0.050354 | 0.88348 | 122.7264 | 0.2243 | 0.37994 | 122.8638 | 122.8271 | 122.7768 | 122.8088 | -122.8592 | -122.7905 | 122.6395 | 0.36163 | 3.154 | 1.3687
3234.1719 | 123.0881 | -54.0436 | 68.7057 | -0.075836 | -0.0019417 | 0.059462 | 0.068191 | -0.0024032 | 0.0026191 | 0.0071308 | 0.029175 | 0.0017431 | 0.001068 | 0.00070062 | -0.0015061 | -0.0038709 | -0.0025379 | -50.8713 | 68.7012 | -54.1168 | 68.6142 | -53.2104 | -53.7964 | -53.2379 | -52.6657 | 68.7469 | -54.0619 | -53.6911 | -53.8559 | -54.0985 | -53.7918 | -0.073242 | -0.004578 | -0.091553 | 0.83313 | 0.80566 | 0.24719 | 0.87891 | 0.32043 | -0.018311 | 0.041198 | -122.3969 | 0.18768 | 0.25177 | -0.054932 | 0.27008 | -0.036621 | 0.90637 | 122.731 | 0.20599 | 0.37079 | 122.818 | 122.8088 | 122.7448 | 122.7905 | -122.8226 | -122.7676 | 122.6578 | 0.35248 | 3.1723 | 1.3779
3235.1719 | 123.0194 | -54.0665 | 68.7424 | -0.014801 | -0.0027963 | 0.062239 | 0.068618 | 0.0010148 | 0.0032599 | 0.0052082 | 0.001709 | 0.00046135 | 0.0021362 | 0.0019824 | -0.0010787 | -0.0047253 | 0.0040845 | -50.8987 | 68.692 | -54.1168 | 68.5959 | -53.2562 | -53.8193 | -53.2425 | -52.7023 | 68.7469 | -54.0848 | -53.7369 | -53.8605 | -54.0665 | -53.7735 | -0.050354 | -0.050354 | -0.14649 | 0.81024 | 0.82397 | 0.24719 | 0.87433 | 0.29755 | -0.018311 | 0.004577 | -122.4792 | 0.20599 | 0.29297 | 0 | 0.31128 | 0.018311 | 0.8606 | 122.7127 | 0.2243 | 0.3479 | 122.8088 | 122.8317 | 122.7585 | 122.8134 | -122.8592 | -122.8271 | 122.6624 | 0.32959 | 3.1677 | 1.3641
3236.1719 | 123.0972 | -54.0482 | 68.7286 | -0.098725 | 0.00019446 | 0.061598 | 0.070113 | -0.0024032 | 0.0015509 | 0.0045672 | 0.0078126 | 0.0019567 | 0.0019226 | -0.00036738 | -0.0034287 | -0.0051527 | -0.0018971 | -50.8759 | 68.7378 | -54.1122 | 68.6096 | -53.215 | -53.7918 | -53.2104 | -52.6382 | 68.7607 | -54.0527 | -53.6865 | -53.8376 | -54.0298 | -53.7643 | -0.064087 | 0.009155 | -0.11902 | 0.83313 | 0.83771 | 0.25635 | 0.90179 | 0.32043 | -0.004577 | 0.032043 | -122.4152 | 0.21057 | 0.28381 | 0.018311 | 0.28839 | 0.022888 | 0.89722 | 122.7219 | 0.21515 | 0.36621 | 122.85 | 122.8134 | 122.7859 | 122.8088 | -122.8409 | -122.7814 | 122.6578 | 0.36163 | 3.1723 | 1.4099
3237.1719 | 122.9187 | -54.0985 | 68.7653 | -0.11398 | 0.0016899 | 0.061171 | 0.071609 | 0.0012284 | -0.00058531 | 0.0071308 | -0.092895 | 0.0032385 | 0.0032044 | 0.0030506 | -0.0010787 | -0.0060071 | -0.00082886 | -50.9766 | 68.7149 | -54.1901 | 68.4311 | -53.4668 | -53.9841 | -53.4073 | -53.0869 | 68.7149 | -54.1855 | -53.8239 | -53.9978 | -54.2404 | -53.8925 | -0.091552 | -0.050354 | -0.33417 | 0.63171 | 0.69122 | 0.11444 | 0.78278 | 0.20599 | -0.086975 | -0.050354 | -122.5891 | 0.10071 | 0.20599 | -0.14191 | 0.29297 | -0.054931 | 0.72327 | 122.6212 | 0.18768 | 0.36163 | 122.905 | 122.9004 | 122.8134 | 122.8134 | -122.9553 | -122.9507 | 122.5296 | 0.27466 | 3.1219 | 1.0117
3238.1719 | 123.0606 | -54.0253 | 68.7332 | -0.068207 | -0.00066014 | 0.060316 | 0.066695 | -0.00026703 | 0.0030463 | 0.0054218 | -0.089844 | 0.0021703 | 0.00064083 | 0.00091422 | -0.0027877 | -0.0064343 | -0.00040166 | -50.8392 | 68.7195 | -54.1122 | 68.6142 | -53.2471 | -53.4027 | -53.0045 | -52.6978 | 68.7469 | -54.0985 | -53.7094 | -53.8239 | -54.007 | -53.7781 | -0.086975 | -0.013733 | -0.11902 | 0.7782 | 1.0208 | 0.62256 | 1.1078 | 0.70953 | -0.073242 | 0.013733 | -122.4426 | 0.20142 | 0.24719 | 0.018311 | 0.32044 | 0.091553 | 0.86517 | 122.7264 | 0.27466 | 0.3891 | 122.8317 | 122.8455 | 122.7448 | 122.7722 | -122.8455 | -122.8317 | 122.6395 | 0.31586 | 3.186 | 1.3275
3239.1719 | 123.0423 | -54.0253 | 68.7286 | -0.083466 | 0.0010489 | 0.059035 | 0.068618 | -0.00026703 | 0.0017645 | 0.0049946 | 0.029175 | 0.0023839 | 0.0023498 | -0.0014356 | -0.0036423 | -0.0066479 | 0.0017345 | -50.8667 | 68.7515 | -54.1168 | 68.6005 | -53.2562 | -53.8055 | -53.2196 | -52.6566 | 68.779 | -54.0665 | -53.7003 | -53.8193 | -53.9978 | -53.7369 | -0.091552 | 0.022888 | -0.12817 | 0.76904 | 0.80567 | 0.21973 | 0.89722 | 0.31128 | -0.041198 | 0.050354 | -122.4289 | 0.20599 | 0.28839 | 0.027466 | 0.32959 | 0.068664 | 0.8606 | 122.7173 | 0.24719 | 0.36621 | 122.8683 | 122.8455 | 122.7768 | 122.8043 | -122.8455 | -122.7951 | 122.6257 | 0.32501 | 3.1586 | 1.3687
3240.1719 | 123.0515 | -54.0344 | 68.7607 | -0.13687 | 0.00019446 | 0.062025 | 0.069686 | 0.001442 | 0.0011237 | 0.0049946 | 0.016968 | 0.00088875 | 0.0012818 | 0.0036914 | -0.0030013 | -0.0047253 | -0.0012561 | -50.885 | 68.7378 | -54.0939 | 68.6005 | -53.2516 | -53.8101 | -53.2333 | -52.6794 | 68.7836 | -54.0665 | -53.6819 | -53.8376 | -54.0207 | -53.7552 | -0.059509 | -0.022888 | -0.16022 | 0.78278 | 0.80109 | 0.2243 | 0.8606 | 0.28381 | -0.032043 | 0.022888 | -122.4426 | 0.19684 | 0.27924 | 0.013733 | 0.31128 | 0.045776 | 0.84228 | 122.6944 | 0.22888 | 0.38452 | 122.8317 | 122.85 | 122.7722 | 122.818 | -122.8546 | -122.8271 | 122.6349 | 0.35248 | 3.1494 | 1.355
3241.1719 | 123.0789 | -54.0344 | 68.7469 | -0.068207 | -0.00087374 | 0.059676 | 0.067977 | -0.00090783 | 0.0019781 | 0.0054218 | 0.02002 | 0.0013159 | -0.00064077 | -0.0010084 | -0.0027877 | -0.0045117 | -0.00061526 | -50.8438 | 68.7607 | -54.0802 | 68.6325 | -53.2059 | -53.7827 | -53.1876 | -52.6062 | 68.7881 | -54.039 | -53.6591 | -53.8101 | -54.0024 | -53.7369 | -0.045776 | 0.013733 | -0.11444 | 0.82855 | 0.84686 | 0.25177 | 0.89264 | 0.29755 | -0.004577 | 0.041199 | -122.406 | 0.2243 | 0.29755 | 0.032044 | 0.30212 | 0.036621 | 0.87433 | 122.7127 | 0.22888 | 0.37994 | 122.8409 | 122.8271 | 122.7951 | 122.8226 | -122.8271 | -122.7859 | 122.6669 | 0.37537 | 3.1906 | 1.4282
3242.1719 | 122.9645 | -54.0573 | 68.7653 | -0.098725 | -0.00087374 | 0.060103 | 0.070541 | 0.0029374 | 0.0036871 | 0.0039264 | -0.12036 | 0.00046135 | 0.001068 | 0.0026232 | -0.0034287 | -0.0055799 | -0.0036059 | -50.8575 | 68.7424 | -54.1534 | 68.5501 | -53.3066 | -53.9017 | -53.3203 | -52.7527 | 68.811 | -54.0848 | -53.7781 | -53.9658 | -54.1626 | -53.8559 | -0.09613 | -0.022888 | -0.21515 | 0.75073 | 0.737 | 0.15564 | 0.83313 | 0.25177 | -0.027466 | 0.045776 | -122.5433 | 0.091553 | 0.20142 | -0.10529 | 0.22888 | -0.07782 | 0.84686 | 122.7036 | 0.11902 | 0.3067 | 122.8958 | 122.8958 | 122.7997 | 122.8683 | -122.9187 | -122.85 | 122.6074 | 0.27924 | 3.1998 | 1.3046
3243.1719 | 123.0652 | -53.9886 | 68.7515 | -0.075836 | -0.0023691 | 0.062239 | 0.069259 | -0.00026703 | 0.0015509 | 0.0052082 | 0.02002 | -0.00060665 | 0.00042723 | -0.0031446 | -0.00086511 | -0.0066479 | -0.00082886 | -50.8301 | 68.7561 | -54.0939 | 68.6188 | -53.2104 | -53.7735 | -53.183 | -52.6245 | 68.7744 | -54.0527 | -53.6636 | -53.7872 | -53.9841 | -53.7369 | -0.10529 | 0.004578 | -0.13275 | 0.7782 | 0.80566 | 0.21515 | 0.91095 | 0.32043 | -0.064087 | 0.022888 | -122.4152 | 0.20142 | 0.25177 | 0.004577 | 0.31586 | 0.068664 | 0.88348 | 122.7127 | 0.2655 | 0.3891 | 122.85 | 122.8271 | 122.7448 | 122.7631 | -122.8455 | -122.8043 | 122.6074 | 0.32501 | 3.1586 | 1.3641
3244.1719 | 123.0377 | -54.0115 | 68.7515 | -0.098725 | -0.0027963 | 0.060744 | 0.068404 | 0.0012284 | 0.0015509 | 0.0064898 | 0.02002 | 0.00088875 | 0.00042723 | -0.0010084 | -0.0019333 | -0.0053663 | -0.00082886 | -50.8255 | 68.7469 | -54.0665 | 68.6234 | -53.2288 | -53.7918 | -53.2013 | -52.6337 | 68.8019 | -54.0527 | -53.6591 | -53.7918 | -53.9841 | -53.7277 | -0.054931 | -0.004578 | -0.12817 | 0.78278 | 0.81024 | 0.21973 | 0.86517 | 0.27466 | -0.041198 | 0.050354 | -122.4106 | 0.21973 | 0.28381 | 0.027466 | 0.32501 | 0.068664 | 0.83771 | 122.6898 | 0.26093 | 0.39368 | 122.8134 | 122.8546 | 122.7585 | 122.8134 | -122.818 | -122.8043 | 122.6349 | 0.35248 | 3.186 | 1.3779
3245.1719 | 123.0469 | -53.9978 | 68.7515 | -0.091095 | -0.00044654 | 0.060957 | 0.068832 | 0.00080117 | 0.0026191 | 0.005849 | 0.026123 | -0.0012477 | 0.00085443 | -0.0052808 | -0.0017197 | -0.0057935 | -0.0065967 | -50.7889 | 68.7653 | -54.0482 | 68.6737 | -53.1647 | -53.7231 | -53.1692 | -52.6108 | 68.7973 | -54.0115 | -53.6499 | -53.7689 | -54.0527 | -53.7643 | -0.050354 | 0.013733 | -0.07782 | 0.83313 | 0.82855 | 0.27466 | 0.87891 | 0.32501 | -0.013733 | 0.045776 | -122.4014 | 0.22888 | 0.23346 | -0.054931 | 0.24719 | -0.041198 | 0.88348 | 122.7219 | 0.24262 | 0.36163 | 122.8134 | 122.8088 | 122.7631 | 122.7951 | -122.7997 | -122.7631 | 122.6715 | 0.3479 | 3.2089 | 1.387
3246.1719 | 123.0469 | -54.007 | 68.7515 | -0.11398 | -1.9142e-05 | 0.061171 | 0.069472 | -0.00026703 | 0.0032599 | 0.0032856 | 0.013916 | -0.00039305 | 0.00021363 | -0.0099804 | -0.0032151 | -0.0060071 | 2.554e-05 | -50.8209 | 68.7881 | -54.1031 | 68.6325 | -53.2242 | -53.7964 | -53.1921 | -52.6428 | 68.7836 | -54.0527 | -53.6591 | -53.801 | -53.9932 | -53.7277 | -0.09613 | 0.036621 | -0.11902 | 0.78278 | 0.81482 | 0.21057 | 0.91095 | 0.3067 | -0.045776 | 0.032043 | -122.4106 | 0.20599 | 0.27924 | 0.013733 | 0.32501 | 0.059509 | 0.87891 | 122.7356 | 0.25177 | 0.39368 | 122.8912 | 122.8363 | 122.7951 | 122.7905 | -122.8546 | -122.8043 | 122.6395 | 0.3479 | 3.186 | 1.3641
3247.1719 | 122.9553 | -54.0024 | 68.8248 | -0.0071715 | 0.00040806 | 0.061812 | 0.07225 | -5.343e-05 | 0.0019781 | 0.0056354 | -0.089844 | 0.0015295 | 0.00042723 | 0.0066822 | -0.0025741 | -0.0038709 | 2.554e-05 | -50.7935 | 68.811 | -54.0894 | 68.5776 | -53.2928 | -53.8284 | -53.2745 | -52.7161 | 68.8477 | -54.0482 | -53.7186 | -53.8879 | -54.0985 | -53.801 | -0.086975 | -0.013733 | -0.24719 | 0.70953 | 0.72784 | 0.17395 | 0.81482 | 0.26093 | -0.045777 | 0.022888 | -122.5433 | 0.11444 | 0.20142 | -0.096131 | 0.24719 | -0.050354 | 0.79651 | 122.6669 | 0.16022 | 0.32959 | 122.9004 | 122.8958 | 122.8134 | 122.85 | -122.9141 | -122.8729 | 122.58 | 0.28381 | 3.2089 | 1.2863
3248.1719 | 123.0743 | -54.0024 | 68.7881 | -0.060578 | 0.0010489 | 0.062666 | 0.069686 | -0.0045394 | 0.0011237 | 0.0039264 | 0.029175 | 0.00088875 | 0.001709 | -0.003999 | -0.0012925 | -0.0066479 | 0.0015209 | -50.7797 | 68.779 | -54.0573 | 68.66 | -53.1692 | -53.7369 | -53.1555 | -52.5787 | 68.7881 | -54.0207 | -53.6407 | -53.7781 | -53.9474 | -53.6911 | -0.054932 | -0.009155 | -0.12817 | 0.83313 | 0.84686 | 0.2655 | 0.90179 | 0.32044 | -0.018311 | 0 | -122.4289 | 0.2243 | 0.31128 | 0.054931 | 0.32959 | 0.073242 | 0.88806 | 122.7173 | 0.24262 | 0.37994 | 122.8363 | 122.8088 | 122.7814 | 122.7905 | -122.8455 | -122.8088 | 122.6624 | 0.36163 | 3.2227 | 1.4236
3249.1719 | 123.0789 | -53.9841 | 68.8065 | -0.045319 | 0.0016899 | 0.059676 | 0.069045 | -0.0024032 | 0.0013373 | 0.0090534 | 0.03833 | -0.00017945 | 0.001709 | 0.0017688 | -0.0027877 | -0.0075025 | 0.0053661 | -50.7889 | 68.7836 | -54.0573 | 68.6554 | -53.1784 | -53.7598 | -53.1692 | -52.5879 | 68.811 | -54.0344 | -53.6316 | -53.7827 | -53.9566 | -53.6957 | -0.073242 | -0.022889 | -0.15106 | 0.80566 | 0.81482 | 0.2243 | 0.88806 | 0.29755 | -0.050354 | 0.004577 | -122.4381 | 0.20142 | 0.28839 | 0.027466 | 0.33875 | 0.07782 | 0.87891 | 122.7127 | 0.25177 | 0.40283 | 122.8409 | 122.8455 | 122.7676 | 122.7951 | -122.8638 | -122.8409 | 122.6395 | 0.35248 | 3.1952 | 1.3962
3250.1719 | 123.0743 | -53.9703 | 68.7836 | -0.10635 | -0.00087374 | 0.061812 | 0.06755 | 0.00058737 | 0.0011237 | 0.0047808 | 0.02002 | 0.00067495 | -0.00085457 | 0.0028368 | -0.0025741 | -0.0079297 | -0.0012561 | -50.7843 | 68.7836 | -54.0848 | 68.6508 | -53.1921 | -53.7598 | -53.1509 | -52.6199 | 68.8156 | -54.007 | -53.6407 | -53.7781 | -53.9658 | -53.7094 | -0.11444 | 0 | -0.13275 | 0.7782 | 0.8194 | 0.21057 | 0.93384 | 0.32501 | -0.036621 | 0.032044 | -122.4243 | 0.19226 | 0.26093 | 0.004578 | 0.29755 | 0.041199 | 0.89264 | 122.7356 | 0.22888 | 0.36621 | 122.8683 | 122.8226 | 122.7539 | 122.7859 | -122.8683 | -122.7905 | 122.6212 | 0.32959 | 3.186 | 1.3504
3251.1719 | 123.0515 | -53.9429 | 68.7927 | -0.060578 | 0.0010489 | 0.059248 | 0.068404 | -0.0013352 | 0.0013373 | 0.0067036 | 0.023071 | -0.00017945 | -0.00064077 | 0.00027342 | -0.0023605 | -0.0081433 | 0.0028027 | -50.7339 | 68.7836 | -54.0298 | 68.7103 | -53.1189 | -53.7094 | -53.1372 | -52.5925 | 68.8477 | -53.9932 | -53.6041 | -53.8239 | -53.9749 | -53.6911 | -0.086975 | -0.009156 | -0.082398 | 0.82397 | 0.80566 | 0.23346 | 0.89264 | 0.32043 | -0.050354 | 0.054931 | -122.3969 | 0.11902 | 0.25177 | -0.032044 | 0.30212 | 0.01831 | 0.91095 | 122.7402 | 0.16937 | 0.3891 | 122.8134 | 122.8409 | 122.7264 | 122.7905 | -122.8226 | -122.786 | 122.6532 | 0.33874 | 3.2089 | 1.3504
3252.1719 | 123.056 | -53.9703 | 68.7973 | -0.075836 | -1.9142e-05 | 0.062453 | 0.070754 | 0.00037377 | 0.0024053 | 0.005849 | 0.016968 | 0.00024775 | -0.00021357 | 0.002196 | 0.00084389 | -0.0081433 | -0.00040166 | -50.7385 | 68.7881 | -54.0436 | 68.7057 | -53.1281 | -53.6911 | -53.1097 | -52.5513 | 68.811 | -54.0161 | -53.4164 | -54.0436 | -54.1763 | -53.7735 | -0.073242 | -0.009155 | -0.091552 | 0.84229 | 0.8606 | 0.27924 | 0.93384 | 0.35248 | -0.045776 | 0.013733 | -122.2137 | -0.073242 | 0.19684 | -0.20599 | 0.24261 | -0.16022 | 0.91553 | 122.7493 | -0.027466 | 0.59967 | 122.8317 | 122.8271 | 122.7585 | 122.7814 | -122.8409 | -122.8134 | 122.6761 | 0.55389 | 3.2318 | 1.4191
3253.1719 | 123.0423 | -53.9795 | 68.7881 | -0.11398 | 0.00062166 | 0.062453 | 0.070327 | -0.00048063 | 0.0011237 | 0.0060626 | 0.02002 | 0.00046135 | 0.00064083 | 0.00027342 | -0.0025741 | -0.0062207 | -0.00040166 | -50.7706 | 68.7881 | -54.0756 | 68.6554 | -53.2059 | -53.7689 | -53.1967 | -52.6474 | 68.8385 | -54.0253 | -53.6362 | -53.7781 | -53.9841 | -53.7094 | -0.096131 | 0 | -0.13275 | 0.77362 | 0.78278 | 0.21057 | 0.87891 | 0.3067 | -0.045777 | 0.050354 | -122.4243 | 0.20142 | 0.27008 | -0.004578 | 0.31586 | 0.041199 | 0.86975 | 122.731 | 0.24719 | 0.3891 | 122.8638 | 122.8638 | 122.7676 | 122.818 | -122.8638 | -122.8134 | 122.6349 | 0.34332 | 3.2089 | 1.3321
3254.1719 | 123.0606 | -53.9795 | 68.8065 | -0.098725 | -0.00044654 | 0.063094 | 0.067123 | -0.0041122 | 0.0039007 | 0.0047808 | 0.013916 | 0.00088875 | 0.002777 | 0.0034778 | -0.0025741 | -0.0055799 | -0.0038197 | -50.7843 | 68.7927 | -54.0527 | 68.6462 | -53.215 | -53.7872 | -53.183 | -52.6337 | 68.8522 | -54.0115 | -53.6453 | -53.7872 | -53.9841 | -53.7003 | -0.073242 | -0.013733 | -0.16022 | 0.76447 | 0.79651 | 0.19226 | 0.86975 | 0.2655 | -0.032044 | 0.045776 | -122.4518 | 0.19226 | 0.27924 | -0.004578 | 0.31128 | 0.027466 | 0.83771 | 122.699 | 0.22431 | 0.36621 | 122.8455 | 122.8638 | 122.7722 | 122.8317 | -122.8592 | -122.818 | 122.6257 | 0.33417 | 3.1952 | 1.3458
3255.1719 | 123.0652 | -53.9337 | 68.7881 | -0.091095 | 0.00019446 | 0.060103 | 0.069259 | -0.00026703 | 0.0021917 | 0.0020038 | 0.023071 | 0.0013159 | -0.0019226 | -0.001222 | -0.0036423 | -0.0028027 | -0.0036059 | -50.7431 | 68.7881 | -54.0482 | 68.6829 | -53.1418 | -53.7323 | -53.1326 | -52.5604 | 68.8477 | -54.0115 | -53.595 | -53.7552 | -53.9337 | -53.6682 | -0.11444 | 0 | -0.10529 | 0.79193 | 0.80109 | 0.20142 | 0.91553 | 0.31586 | -0.07782 | 0.059509 | -122.3831 | 0.17853 | 0.2655 | 0 | 0.34332 | 0.07782 | 0.90637 | 122.731 | 0.25635 | 0.41656 | 122.8363 | 122.8592 | 122.7219 | 122.7814 | -122.8363 | -122.7997 | 122.6166 | 0.33874 | 3.1906 | 1.3733
3256.1719 | 123.0652 | -53.9291 | 68.811 | -0.12924 | -0.0021555 | 0.061598 | 0.070541 | 0.003151 | 0.0024053 | 0.0039264 | 0.016968 | 0.0021703 | 0.0019226 | 0.0049732 | -0.0015061 | -0.0051527 | -0.00082886 | -50.7202 | 68.8065 | -54.0619 | 68.6783 | -53.1509 | -53.7323 | -53.1464 | -52.5787 | 68.8339 | -53.9932 | -53.5904 | -53.746 | -53.9246 | -53.6682 | -0.13275 | -0.004577 | -0.13275 | 0.7782 | 0.78278 | 0.19684 | 0.91553 | 0.32959 | -0.064087 | 0.022888 | -122.4014 | 0.18311 | 0.26093 | 0.004577 | 0.32501 | 0.068664 | 0.91095 | 122.7402 | 0.24719 | 0.40283 | 122.8683 | 122.8271 | 122.7356 | 122.7631 | -122.8729 | -122.8043 | 122.6074 | 0.33875 | 3.2089 | 1.3504
3257.1719 | 123.0743 | -53.9703 | 68.8065 | -0.083466 | -0.00066014 | 0.060744 | 0.070113 | -0.0021896 | 0.0045417 | 0.0020038 | 0.010864 | 0.00088875 | -0.00042717 | -0.00036738 | -0.0017197 | -0.0053663 | -0.0021107 | -50.7294 | 68.8156 | -54.0344 | 68.6966 | -53.1555 | -53.7277 | -53.1555 | -52.5696 | 68.8293 | -53.9886 | -53.6041 | -53.7369 | -53.9337 | -53.6682 | -0.064087 | 0.009155 | -0.10986 | 0.81482 | 0.81482 | 0.24262 | 0.87891 | 0.3067 | -0.01831 | 0.022888 | -122.4106 | 0.23346 | 0.30212 | 0.036621 | 0.32043 | 0.054931 | 0.87891 | 122.731 | 0.25177 | 0.38452 | 122.85 | 122.818 | 122.7859 | 122.7997 | -122.8409 | -122.7951 | 122.6669 | 0.36621 | 3.241 | 1.4008
3258.1719 | 123.0469 | -53.9337 | 68.8065 | -0.083466 | -0.00087374 | 0.06288 | 0.0699 | -0.0024032 | 0.0026191 | 0.0039264 | 0.0078126 | -0.0014613 | -0.003418 | 0.001128 | -0.0030013 | -0.0062207 | -0.0031787 | -50.7019 | 68.811 | -54.0253 | 68.7149 | -53.0823 | -53.6728 | -53.0914 | -52.359 | 68.8934 | -53.9246 | -53.5858 | -53.7781 | -53.9337 | -53.6819 | -0.091553 | 0.004577 | -0.091553 | 0.85144 | 0.84228 | 0.26093 | 0.93384 | 0.35248 | 0.009155 | 0.086975 | -122.3923 | 0.15564 | 0.25177 | 0 | 0.24261 | -0.009155 | 0.94299 | 122.7402 | 0.14648 | 0.33875 | 122.8363 | 122.818 | 122.7448 | 122.8271 | -122.8317 | -122.731 | 122.6486 | 0.3479 | 3.2318 | 1.5747
3259.1719 | 123.0881 | -53.9474 | 68.8248 | -0.0071715 | 0.0016899 | 0.061385 | 0.070327 | -0.0013352 | 0.0019781 | 0.0047808 | 0.013916 | 0.0021703 | 0.00021363 | 0.00027342 | -0.0017197 | -0.0098523 | -0.00018806 | -50.6882 | 68.8248 | -54.0024 | 68.7241 | -53.0914 | -53.6728 | -53.1052 | -52.5192 | 68.8705 | -53.9429 | -53.3844 | -53.9886 | -54.1489 | -53.7506 | -0.054931 | 0 | -0.10071 | 0.85602 | 0.84228 | 0.27466 | 0.89722 | 0.32959 | 0.004578 | 0.045776 | -122.2092 | -0.041198 | 0.19684 | -0.20142 | 0.19226 | -0.20599 | 0.91095 | 122.7264 | -0.045776 | 0.55847 | 122.8271 | 122.8134 | 122.7722 | 122.818 | -122.8271 | -122.7676 | 122.6715 | 0.56305 | 3.2593 | 1.4282
3260.1719 | 123.0652 | -53.9612 | 68.8477 | -0.11398 | -0.0013009 | 0.061812 | 0.069259 | 0.00037377 | 0.0013373 | 0.0020038 | 0.023071 | 0.00088875 | 0.0012818 | -0.00015378 | -0.0010787 | -0.0051527 | -0.0025379 | -50.7065 | 68.8065 | -54.0482 | 68.6874 | -53.1876 | -53.746 | -53.1418 | -52.5925 | 68.8568 | -53.9978 | -53.6087 | -53.746 | -53.952 | -53.6728 | -0.086975 | -0.041198 | -0.16022 | 0.77362 | 0.8194 | 0.21515 | 0.90637 | 0.30212 | -0.036621 | 0.009156 | -122.4564 | 0.21515 | 0.28839 | 0.009156 | 0.32501 | 0.045777 | 0.8606 | 122.7356 | 0.25177 | 0.3891 | 122.8546 | 122.8546 | 122.7676 | 122.818 | -122.8958 | -122.8455 | 122.6486 | 0.35248 | 3.2547 | 1.3687
3261.1719 | 123.0515 | -53.9612 | 68.8431 | -0.091095 | 0.0016899 | 0.060103 | 0.068618 | 0.0010148 | 0.0030463 | 0.0062762 | -0.0074462 | 0.0013159 | 0.00021363 | -0.0016492 | -0.0021469 | -0.0072889 | 0.00045294 | -50.7111 | 68.8339 | -54.0207 | 68.6691 | -53.183 | -53.746 | -53.1647 | -52.6062 | 68.866 | -53.9886 | -53.595 | -53.7506 | -53.9474 | -53.6774 | -0.059509 | -0.009156 | -0.17395 | 0.7782 | 0.79651 | 0.21515 | 0.85602 | 0.27466 | -0.027465 | 0.022888 | -122.4381 | 0.21057 | 0.28381 | 0.013733 | 0.31128 | 0.041198 | 0.83771 | 122.6898 | 0.23804 | 0.39368 | 122.8546 | 122.8546 | 122.7951 | 122.8271 | -122.8638 | -122.8317 | 122.6303 | 0.36621 | 3.2501 | 1.355
3262.1719 | 123.0606 | -53.9291 | 68.8339 | -0.11398 | 0.00019446 | 0.061171 | 0.069259 | 0.00016017 | 0.0034735 | 0.0056354 | -0.01355 | 0.00046135 | -0.0012818 | 0.0017688 | -0.0017197 | -0.0057935 | -0.0012561 | -50.6744 | 68.8477 | -54.0161 | 68.7195 | -53.1189 | -53.7003 | -53.1052 | -52.5238 | 68.8797 | -53.9566 | -53.5675 | -53.7094 | -53.8925 | -53.6407 | -0.086975 | 0.013733 | -0.11444 | 0.81024 | 0.82397 | 0.22888 | 0.91095 | 0.31586 | -0.027466 | 0.045777 | -122.4014 | 0.21973 | 0.28839 | 0.036621 | 0.31586 | 0.064087 | 0.89722 | 122.7356 | 0.24719 | 0.3891 | 122.8638 | 122.8363 | 122.7768 | 122.8088 | -122.85 | -122.7905 | 122.6486 | 0.36163 | 3.2547 | 1.4053
3263.1719 | 123.0743 | -53.92 | 68.8293 | -0.10635 | 0.00019446 | 0.061598 | 0.068404 | 0.0050736 | 0.0043281 | 0.0032856 | 0.010864 | 0.00024775 | -0.0010682 | 0.00091422 | -0.0038559 | -0.0072889 | -0.00082886 | -50.6973 | 68.8202 | -54.0161 | 68.7195 | -53.1143 | -53.6957 | -53.1189 | -52.5375 | 68.898 | -53.9749 | -53.5538 | -53.7186 | -53.9154 | -53.6316 | -0.09613 | -0.009156 | -0.10986 | 0.80566 | 0.80109 | 0.2243 | 0.89722 | 0.32043 | -0.054932 | 0.068664 | -122.3831 | 0.20142 | 0.28839 | 0.004578 | 0.34332 | 0.05951 | 0.90179 | 122.7356 | 0.25635 | 0.42114 | 122.8363 | 122.8729 | 122.7402 | 122.818 | -122.8455 | -122.8043 | 122.6395 | 0.36621 | 3.2227 | 1.3824
3264.1719 | 123.0331 | -53.9383 | 68.8522 | -0.083466 | -0.00044654 | 0.059462 | 0.067763 | 0.003151 | 0.0013373 | 0.0054218 | -0.0043946 | -0.00060665 | 0.00042723 | -0.001222 | -0.0030013 | -0.0060071 | -0.0010425 | -50.6378 | 68.8248 | -54.0024 | 68.7561 | -53.0685 | -53.6545 | -53.1052 | -52.2491 | 68.9438 | -53.8788 | -53.5812 | -53.7643 | -53.9017 | -53.6545 | -0.064087 | -0.027466 | -0.09613 | 0.86975 | 0.83313 | 0.28381 | 0.89722 | 0.3479 | 0.059509 | 0.091553 | -122.4335 | 0.17395 | 0.28381 | 0.036621 | 0.2243 | -0.022888 | 0.93384 | 122.7585 | 0.11444 | 0.29755 | 122.8271 | 122.8226 | 122.7631 | 122.8821 | -122.8546 | -122.731 | 122.6944 | 0.35706 | 3.3005 | 1.6891
3265.1719 | 123.1064 | -53.9429 | 68.8339 | -0.060578 | 0.00062166 | 0.059035 | 0.069472 | -0.00026703 | 0.0015509 | 0.0060626 | 0.016968 | 0.0013159 | 0.0032044 | -0.0082716 | -0.0034287 | -0.0070753 | -0.0023243 | -50.6424 | 68.8248 | -54.0024 | 68.7469 | -53.0731 | -53.6545 | -53.0777 | -52.4918 | 68.8843 | -53.9474 | -53.3524 | -53.9062 | -54.158 | -53.7689 | -0.059509 | -0.009155 | -0.086975 | 0.86975 | 0.86517 | 0.28839 | 0.92468 | 0.3479 | -0.004578 | 0.050354 | -122.1863 | 0.036621 | 0.17395 | -0.21515 | 0.17853 | -0.21057 | 0.92926 | 122.7493 | 0.041199 | 0.59509 | 122.8271 | 122.8317 | 122.7676 | 122.8271 | -122.8363 | -122.7814 | 122.6898 | 0.59051 | 3.3005 | 1.4511
3266.1719 | 123.1659 | -53.8696 | 68.9346 | -0.091095 | 0.00062166 | 0.061598 | 0.069259 | -0.0013352 | 0.0019781 | 0.0073444 | -0.0043946 | 0.0011023 | 0.00021363 | 5.9824e-05 | -0.0032151 | -0.0055799 | -0.0021107 | -50.6287 | 68.8568 | -53.9932 | 68.7607 | -53.0594 | -53.6636 | -53.0731 | -52.4918 | 68.8934 | -53.9337 | -53.5629 | -53.7094 | -53.8925 | -53.6224 | -0.1236 | -0.077819 | -0.17395 | 0.81024 | 0.79651 | 0.20599 | 0.9201 | 0.32959 | -0.064087 | -0.041198 | -122.4976 | 0.16022 | 0.24719 | -0.022888 | 0.31128 | 0.041199 | 0.93384 | 122.7539 | 0.2243 | 0.37079 | 122.85 | 122.8271 | 122.7264 | 122.7631 | -122.9279 | -122.8683 | 122.6303 | 0.3067 | 3.241 | 1.3779
3267.1719 | 123.0377 | -53.9154 | 68.8522 | -0.098725 | -0.00044654 | 0.063307 | 0.068404 | -0.0013352 | 0.0026191 | 0.00414 | 0.0078126 | 0.0015295 | 0.00085443 | 0.001128 | -0.0049241 | -0.0049389 | 2.554e-05 | -50.6699 | 68.8568 | -54.0207 | 68.7012 | -53.1509 | -53.7231 | -53.1281 | -52.565 | 68.9026 | -53.9795 | -53.5812 | -53.7369 | -53.9246 | -53.6453 | -0.10529 | 0.004578 | -0.15106 | 0.76447 | 0.78735 | 0.19226 | 0.89264 | 0.29755 | -0.064087 | 0.050354 | -122.4335 | 0.17853 | 0.27008 | -0.009156 | 0.33417 | 0.054931 | 0.86975 | 122.7219 | 0.24262 | 0.39825 | 122.8775 | 122.8821 | 122.7722 | 122.818 | -122.8729 | -122.8317 | 122.6166 | 0.33417 | 3.2455 | 1.3504
3268.1719 | 122.8958 | -53.9612 | 68.8934 | -0.060578 | -0.00023294 | 0.060103 | 0.073104 | -0.0032578 | 0.0030463 | 0.0062762 | -0.11121 | 0.0036657 | 0.0012818 | 0.0032642 | -0.0019333 | -0.0040845 | -0.0040333 | -50.7111 | 68.8889 | -54.0573 | 68.6417 | -53.2516 | -53.8376 | -53.2516 | -52.6932 | 68.9392 | -53.9703 | -53.6774 | -53.8605 | -54.0802 | -53.7598 | -0.09613 | -0.004578 | -0.25177 | 0.70953 | 0.70953 | 0.1236 | 0.80566 | 0.21973 | -0.009155 | 0.045776 | -122.5708 | 0.10071 | 0.20142 | -0.11902 | 0.21057 | -0.10986 | 0.80566 | 122.699 | 0.10986 | 0.29297 | 122.9462 | 122.9095 | 122.85 | 122.9004 | -122.9507 | -122.8638 | 122.6028 | 0.28381 | 3.2501 | 1.268
3269.1719 | 123.0515 | -53.8925 | 68.8522 | -0.075836 | -0.0017281 | 0.061598 | 0.069686 | 0.00080117 | 0.0028327 | 0.0071308 | 0.0047608 | -0.00039305 | 0.00064083 | -0.0016492 | -0.0025741 | -0.0051527 | 0.0025891 | -50.6378 | 68.8843 | -53.9886 | 68.7424 | -53.0914 | -53.6728 | -53.0731 | -52.5009 | 68.9026 | -53.92 | -53.5355 | -53.6682 | -53.8925 | -53.6133 | -0.09613 | 0.032043 | -0.10986 | 0.80109 | 0.8194 | 0.21973 | 0.91553 | 0.31586 | -0.027466 | 0.050354 | -122.3877 | 0.2243 | 0.27924 | 0 | 0.3067 | 0.027466 | 0.89722 | 122.731 | 0.25177 | 0.38452 | 122.8729 | 122.8226 | 122.7768 | 122.7951 | -122.8409 | -122.7722 | 122.6349 | 0.35706 | 3.2547 | 1.3916
3270.1719 | 123.0377 | -53.8651 | 68.8614 | -0.12161 | -0.0015145 | 0.062239 | 0.066482 | 0.0046464 | 0.0034735 | 0.0022174 | 0.02002 | 0.0017431 | 0.0023498 | -0.0065626 | -0.0030013 | -0.0070753 | 0.0030163 | -50.6378 | 68.8889 | -53.9703 | 68.7469 | -53.1006 | -53.6819 | -53.096 | -52.5192 | 68.8934 | -53.9612 | -53.5217 | -53.6728 | -53.8879 | -53.5995 | -0.10529 | 0.027466 | -0.11444 | 0.76447 | 0.76904 | 0.1831 | 0.87433 | 0.28839 | -0.096131 | 0.032044 | -122.3831 | 0.19226 | 0.2655 | -0.022888 | 0.36163 | 0.073243 | 0.86975 | 122.7173 | 0.28839 | 0.43945 | 122.8592 | 122.8546 | 122.7539 | 122.7585 | -122.8317 | -122.8226 | 122.612 | 0.34332 | 3.2272 | 1.3458
3271.1719 | 123.056 | -53.8971 | 68.8614 | -0.098725 | -0.00066014 | 0.062239 | 0.067763 | -0.004753 | 0.0030463 | 0.0062762 | 0.016968 | 0.00046135 | 0.00064083 | -0.0035718 | -0.0021469 | -0.0077161 | 0.0010937 | -50.6378 | 68.8705 | -53.9658 | 68.7332 | -53.1052 | -53.6957 | -53.1006 | -52.5284 | 68.9026 | -53.9291 | -53.54 | -53.6774 | -53.8788 | -53.6087 | -0.068664 | 0.009155 | -0.12817 | 0.79193 | 0.79651 | 0.20142 | 0.86517 | 0.27008 | -0.032043 | 0.041199 | -122.4014 | 0.21973 | 0.28839 | 0.018311 | 0.32043 | 0.050354 | 0.86059 | 122.699 | 0.25177 | 0.3891 | 122.8363 | 122.8317 | 122.7676 | 122.7997 | -122.8271 | -122.7905 | 122.6303 | 0.35706 | 3.2593 | 1.3687
3272.1719 | 122.9599 | -53.9017 | 68.9072 | -0.12161 | -0.00087374 | 0.06288 | 0.07225 | -5.343e-05 | 0.0064643 | 0.0049946 | -0.071533 | 0.0015295 | 0.001068 | 0.0081774 | -0.0021469 | -0.0047253 | -0.00018806 | -50.6241 | 68.898 | -53.9886 | 68.5959 | -53.0685 | -53.7048 | -53.1692 | -52.597 | 68.9484 | -53.9429 | -53.5995 | -53.7872 | -53.9886 | -53.6865 | -0.086975 | -0.009156 | -0.31128 | 0.83313 | 0.73242 | 0.19684 | 0.8194 | 0.28381 | -0.041199 | 0.041198 | -122.5067 | 0.11444 | 0.21515 | -0.086975 | 0.25635 | -0.045776 | 0.9201 | 122.5845 | 0.15564 | 0.34332 | 122.8867 | 122.8912 | 122.7997 | 122.85 | -122.8958 | -122.85 | 122.4976 | 0.30212 | 3.2776 | 1.3046
3273.1719 | 123.0148 | -53.8559 | 68.9621 | -0.075836 | 0.00019446 | 0.062239 | 0.068618 | 0.00080117 | 0.00091009 | 0.0047808 | 0.016968 | 3.4148e-05 | 0.0029906 | 0.00048702 | -0.0015061 | -0.0038709 | 0.0021619 | -50.5875 | 68.8568 | -53.9703 | 68.7698 | -53.0273 | -53.6041 | -53.0502 | -52.4551 | 68.9209 | -53.8879 | -53.4897 | -53.6591 | -53.8605 | -53.5995 | -0.11444 | -0.10528 | -0.19226 | 0.82855 | 0.80566 | 0.25177 | 0.9201 | 0.36621 | -0.032043 | -0.041199 | -122.4518 | 0.19684 | 0.25635 | -0.004578 | 0.28839 | 0.027465 | 0.94299 | 122.7402 | 0.22888 | 0.39825 | 122.8271 | 122.8088 | 122.7127 | 122.7768 | -122.9324 | -122.85 | 122.6257 | 0.36621 | 3.2684 | 1.4008
3274.1719 | 123.0423 | -53.9017 | 68.8934 | -0.12924 | -1.9142e-05 | 0.061385 | 0.069259 | -0.0024032 | 0.0011237 | 0.00414 | 0.023071 | 0.00067495 | 0.00064083 | 0.0015552 | -0.0021469 | -0.0068615 | -0.0023243 | -50.6287 | 68.9072 | -53.9566 | 68.7241 | -53.1052 | -53.6911 | -53.0914 | -52.5192 | 68.9163 | -53.9566 | -53.5309 | -53.6819 | -53.8834 | -53.6316 | -0.054932 | 0.013733 | -0.16937 | 0.79651 | 0.81024 | 0.21057 | 0.86517 | 0.2655 | -0.054932 | 0.022888 | -122.4243 | 0.21973 | 0.27008 | 0.01831 | 0.32501 | 0.073242 | 0.85144 | 122.6807 | 0.27466 | 0.42572 | 122.8638 | 122.8729 | 122.8088 | 122.818 | -122.85 | -122.85 | 122.6257 | 0.37079 | 3.273 | 1.3824
3275.1719 | 123.0469 | -53.8834 | 68.9026 | -0.052948 | -0.00044654 | 0.063094 | 0.067763 | -0.001976 | 0.0030463 | 0.0045672 | 0.026123 | 0.00046135 | -0.00064077 | 0.0019824 | -0.00086511 | -0.0057935 | -0.0012561 | -50.6104 | 68.8751 | -53.9612 | 68.7241 | -53.1189 | -53.6911 | -53.0914 | -52.5238 | 68.9117 | -53.92 | -53.5446 | -53.6819 | -53.9017 | -53.6087 | -0.07782 | -0.027466 | -0.17853 | 0.76447 | 0.79193 | 0.19226 | 0.86975 | 0.27008 | -0.036621 | 0.009155 | -122.4472 | 0.20142 | 0.27466 | -0.01831 | 0.31128 | 0.018311 | 0.84229 | 122.6852 | 0.23804 | 0.37537 | 122.8363 | 122.8317 | 122.7585 | 122.7951 | -122.8638 | -122.8226 | 122.6074 | 0.33874 | 3.273 | 1.3596
3276.1719 | 123.0423 | -53.8284 | 68.8889 | -0.12924 | 0.0014761 | 0.061385 | 0.069259 | 0.00058737 | 0.0015509 | 0.0052082 | 0.023071 | 0.0011023 | 0.00085443 | -0.0018628 | -0.0049241 | -0.0055799 | -0.0040333 | -50.5783 | 68.898 | -53.9566 | 68.7698 | -53.0457 | -53.6362 | -53.0502 | -52.4689 | 68.9301 | -53.8925 | -53.4988 | -53.6545 | -53.8513 | -53.5675 | -0.12817 | 0.009155 | -0.11902 | 0.78278 | 0.7782 | 0.19226 | 0.90637 | 0.32043 | -0.064087 | 0.041199 | -122.3877 | 0.17395 | 0.26093 | -0.022888 | 0.32501 | 0.041199 | 0.91095 | 122.7264 | 0.23804 | 0.39368 | 122.8546 | 122.8226 | 122.7264 | 122.7585 | -122.8455 | -122.7814 | 122.5983 | 0.32959 | 3.2501 | 1.3596
3277.1719 | 123.0515 | -53.8284 | 68.8934 | -0.10635 | 0.00083526 | 0.062025 | 0.066909 | -0.0026168 | 0.0041143 | 0.0026446 | 0.0047608 | 0.00088875 | -0.00064077 | -0.0031446 | -0.00086511 | -0.0055799 | -0.00040166 | -50.5829 | 68.9026 | -53.9474 | 68.7836 | -53.064 | -53.6316 | -53.0685 | -52.4643 | 68.9255 | -53.9062 | -53.4943 | -53.6453 | -53.8422 | -53.5767 | -0.11902 | 0.009155 | -0.10986 | 0.76446 | 0.75989 | 0.19684 | 0.87891 | 0.31586 | -0.07782 | 0.032043 | -122.3877 | 0.1831 | 0.25177 | -0.013733 | 0.32959 | 0.064087 | 0.88348 | 122.731 | 0.26093 | 0.41199 | 122.85 | 122.8317 | 122.731 | 122.7539 | -122.8409 | -122.7997 | 122.612 | 0.33417 | 3.2455 | 1.3641
3278.1719 | 123.0377 | -53.8467 | 68.9209 | -0.10635 | -0.00044654 | 0.061598 | 0.069259 | -0.0021896 | 0.0021917 | 0.0056354 | 0.023071 | 0.0015295 | 0.0023498 | -0.0010084 | -0.0019333 | -0.0055799 | -0.0014697 | -50.5692 | 68.9438 | -53.9246 | 68.7744 | -53.0731 | -53.6499 | -53.0457 | -52.4826 | 68.9301 | -53.9017 | -53.4943 | -53.6407 | -53.8239 | -53.5812 | -0.07782 | 0.022889 | -0.14648 | 0.77362 | 0.80109 | 0.19684 | 0.87891 | 0.27466 | -0.054931 | 0.009156 | -122.4152 | 0.20599 | 0.2655 | 0.022888 | 0.32043 | 0.077819 | 0.85144 | 122.699 | 0.26093 | 0.40741 | 122.8683 | 122.8317 | 122.7905 | 122.7768 | -122.8455 | -122.8226 | 122.6212 | 0.35248 | 3.2776 | 1.3641
3279.1719 | 123.0972 | -53.8055 | 68.9529 | -0.10635 | 0.0012625 | 0.061598 | 0.067763 | -0.00069423 | 0.0017645 | 0.0062762 | 0.023071 | 0.00024775 | 0.003418 | -0.001222 | -0.0047103 | -0.0055799 | -0.0023243 | -50.528 | 68.9117 | -53.9108 | 68.8293 | -52.9953 | -53.5812 | -53.0136 | -52.4002 | 68.9392 | -53.8742 | -53.4943 | -53.6224 | -53.6407 | -53.3798 | -0.10529 | -0.041199 | -0.1236 | 0.81024 | 0.79193 | 0.2243 | 0.89722 | 0.32959 | -0.068665 | -0.013733 | -122.4472 | 0.18311 | 0.42572 | 0.1648 | 0.49439 | 0.23346 | 0.91553 | 122.7402 | 0.25177 | 0.37994 | 122.8226 | 122.8134 | 122.7173 | 122.7448 | -122.8638 | -122.8271 | 122.6349 | 0.31128 | 3.2776 | 1.4053
3280.1719 | 123.0743 | -53.833 | 68.9301 | -0.12161 | -0.00044654 | 0.061385 | 0.067977 | -0.0021896 | 0.00026909 | 0.0084124 | -0.0013428 | 0.00067495 | 0.00021363 | 0.001128 | -0.0012925 | -0.0062207 | -0.0029651 | -50.5325 | 68.8934 | -53.9246 | 68.8065 | -53.0136 | -53.5904 | -53.0182 | -52.4094 | 68.9529 | -53.8742 | -53.476 | -53.6316 | -53.8284 | -53.5858 | -0.091553 | -0.036621 | -0.1236 | 0.8194 | 0.81482 | 0.24262 | 0.90637 | 0.33417 | -0.041199 | 0.022888 | -122.406 | 0.20142 | 0.24719 | 0.004578 | 0.28839 | 0.045777 | 0.91095 | 122.731 | 0.24262 | 0.39825 | 122.818 | 122.8271 | 122.7264 | 122.7859 | -122.8546 | -122.8043 | 122.6395 | 0.35706 | 3.3005 | 1.4236
3281.1719 | 123.0331 | -53.8422 | 68.9255 | -0.075836 | 0.0014761 | 0.061171 | 0.071181 | -5.343e-05 | 0.00091009 | 0.0047808 | 0.010864 | 0.0017431 | 0.00021363 | -0.0010084 | -0.0032151 | -0.0036573 | -0.0025379 | -50.5692 | 68.9072 | -53.9429 | 68.7561 | -53.0869 | -53.6728 | -53.0823 | -52.4918 | 68.9529 | -53.8696 | -53.5126 | -53.6545 | -53.8605 | -53.6041 | -0.10071 | -0.01831 | -0.16937 | 0.75531 | 0.75989 | 0.16937 | 0.8606 | 0.27008 | -0.027466 | 0.027466 | -122.438 | 0.18768 | 0.23804 | -0.018311 | 0.2655 | 0.009155 | 0.85602 | 122.699 | 0.21515 | 0.35706 | 122.85 | 122.8226 | 122.7493 | 122.7951 | -122.8683 | -122.7951 | 122.5983 | 0.32959 | 3.273 | 1.3504
3282.1719 | 123.056 | -53.8513 | 68.9255 | -0.098725 | -0.00023294 | 0.061812 | 0.070327 | -5.343e-05 | 0.0026191 | 0.0026446 | -0.0013428 | 0.00046135 | -0.00021357 | -0.0035718 | -1.0706e-05 | -0.0053663 | 0.0010937 | -50.5554 | 68.9301 | -53.9383 | 68.7561 | -53.0823 | -53.6682 | -53.0731 | -52.4826 | 68.9529 | -53.9017 | -53.5172 | -53.6499 | -53.8742 | -53.595 | -0.086975 | 0.004578 | -0.16937 | 0.76904 | 0.7782 | 0.1831 | 0.86517 | 0.27008 | -0.050354 | 0.027466 | -122.4426 | 0.20142 | 0.25635 | -0.022889 | 0.3067 | 0.027465 | 0.85602 | 122.6944 | 0.25177 | 0.38452 | 122.8683 | 122.8546 | 122.7814 | 122.8043 | -122.8638 | -122.8271 | 122.6074 | 0.33417 | 3.2959 | 1.3687
3283.1719 | 123.0743 | -53.8147 | 68.9392 | -0.11398 | -0.0010873 | 0.062453 | 0.067763 | -0.0021896 | 0.0039007 | 0.0073444 | 0.010864 | 0.00024775 | 0.001709 | -0.00036738 | -0.0012925 | -0.0057935 | -0.0010425 | -50.5142 | 68.9438 | -53.9154 | 68.7973 | -53.0273 | -53.6041 | -53.0502 | -52.4277 | 68.985 | -53.8879 | -53.4805 | -53.6041 | -53.8193 | -53.5675 | -0.10071 | 0.004578 | -0.14191 | 0.78735 | 0.76447 | 0.21057 | 0.86517 | 0.31128 | -0.073242 | 0.045776 | -122.4197 | 0.21057 | 0.24719 | -0.004578 | 0.32043 | 0.068664 | 0.88806 | 122.7127 | 0.28381 | 0.40741 | 122.8592 | 122.8729 | 122.7585 | 122.7997 | -122.8546 | -122.8271 | 122.612 | 0.33417 | 3.3005 | 1.387
3284.1719 | 123.0743 | -53.833 | 68.9346 | -0.083466 | 0.00019446 | 0.061598 | 0.069259 | 0.0027238 | 0.0019781 | 0.0064898 | 0.0078126 | -0.00060665 | -0.00085457 | 0.0049732 | -0.0019333 | -0.0049389 | -0.0012561 | -50.5142 | 68.9301 | -53.9246 | 68.811 | -53.0411 | -53.6179 | -53.0411 | -52.4185 | 68.9392 | -53.8742 | -53.4576 | -53.6041 | -53.8193 | -53.5583 | -0.091553 | -0.004577 | -0.1236 | 0.79193 | 0.79193 | 0.21515 | 0.88348 | 0.3067 | -0.041199 | 0.004578 | -122.3923 | 0.22888 | 0.27466 | 0.013733 | 0.31586 | 0.054932 | 0.88348 | 122.7356 | 0.27008 | 0.41656 | 122.8546 | 122.8134 | 122.7631 | 122.7722 | -122.8592 | -122.8088 | 122.644 | 0.37537 | 3.3188 | 1.4145
3285.1719 | 123.0515 | -53.8101 | 68.9255 | -0.12924 | -0.0025827 | 0.061385 | 0.068832 | -0.00069423 | 0.00091009 | 0.0037128 | 0.016968 | 0.0011023 | 0.00085443 | -0.0054944 | -0.0023605 | -0.0062207 | -0.00018806 | -50.5051 | 68.9117 | -53.9154 | 68.8065 | -53.0411 | -53.6362 | -53.0365 | -52.4277 | 68.9758 | -53.8834 | -53.4622 | -53.6041 | -53.8239 | -53.54 | -0.10529 | -0.013733 | -0.11902 | 0.76904 | 0.77362 | 0.17395 | 0.87891 | 0.27924 | -0.073242 | 0.050354 | -122.3877 | 0.20599 | 0.27008 | -0.013733 | 0.34332 | 0.059509 | 0.87433 | 122.7219 | 0.27924 | 0.42114 | 122.8271 | 122.8592 | 122.7219 | 122.7859 | -122.8409 | -122.8088 | 122.6166 | 0.3479 | 3.3051 | 1.3824
3286.1719 | 123.0606 | -53.8513 | 68.9346 | -0.03006 | -0.0010873 | 0.062025 | 0.067977 | 0.0020828 | 0.0028327 | 0.0049946 | 0.016968 | -0.00060665 | 0.00085443 | -0.00015378 | -0.0057785 | -0.0066479 | 0.0015209 | -50.4593 | 68.9484 | -53.9062 | 68.8568 | -52.9541 | -53.5767 | -52.9816 | -52.3956 | 68.9667 | -53.8696 | -53.4988 | -53.8879 | -53.8376 | -53.508 | -0.054932 | 0.013733 | -0.077819 | 0.89722 | 0.86975 | 0.27466 | 0.92468 | 0.32959 | -0.018311 | 0.032044 | -122.4335 | -0.036621 | 0.34332 | 0.013733 | 0.36163 | 0.032044 | 0.95215 | 122.7631 | -0.01831 | 0.37079 | 122.8546 | 122.8363 | 122.7997 | 122.818 | -122.8409 | -122.8043 | 122.7081 | 0.35248 | 3.392 | 1.4557
3287.1719 | 122.9782 | -53.7964 | 68.9346 | -0.075836 | -0.0013009 | 0.059462 | 0.067763 | 0.00016017 | 5.5488e-05 | 0.0064898 | -0.0074462 | -0.00060665 | -0.00064077 | -0.0042126 | -0.0025741 | -0.0045117 | -0.0018971 | -50.4639 | 68.9529 | -53.9246 | 68.8568 | -52.9633 | -53.5492 | -52.9999 | -52.3682 | 68.9758 | -53.8422 | -53.5126 | -53.3112 | -53.833 | -53.6865 | -0.12817 | 0.018311 | -0.077819 | 0.83313 | 0.79651 | 0.24719 | 0.92468 | 0.37537 | -0.045776 | 0.041199 | -122.4472 | 0.48523 | 0.10986 | -0.036621 | 0.15564 | 0.009155 | 0.9613 | 122.7814 | 0.53101 | 0.32959 | 122.8775 | 122.818 | 122.7493 | 122.7722 | -122.8592 | -122.7768 | 122.6532 | 0.28381 | 3.3325 | 1.4282
3288.1719 | 123.0423 | -53.8284 | 68.9621 | -0.098725 | 0.00019446 | 0.062239 | 0.067977 | 0.00251 | 0.0021917 | 0.0043536 | 0.013916 | 0.00046135 | 0.00064083 | -0.0061352 | -0.0023605 | -0.0047253 | 0.0028027 | -50.4959 | 68.9392 | -53.9017 | 68.8156 | -53.0365 | -53.6133 | -53.0365 | -52.4323 | 68.9941 | -53.8559 | -53.4714 | -53.6041 | -53.8193 | -53.5446 | -0.073242 | -0.022888 | -0.14648 | 0.79193 | 0.79193 | 0.21515 | 0.86517 | 0.28839 | -0.027466 | 0.032044 | -122.4335 | 0.2243 | 0.28381 | 0.009155 | 0.31128 | 0.036621 | 0.86517 | 122.7173 | 0.25177 | 0.38452 | 122.8409 | 122.85 | 122.7676 | 122.8226 | -122.8638 | -122.818 | 122.644 | 0.35705 | 3.3325 | 1.3962
3289.1719 | 123.0652 | -53.7918 | 69.0308 | -0.091095 | -0.0019417 | 0.06053 | 0.067977 | -0.00069423 | 0.0030463 | 0.0064898 | -0.022705 | 0.0021703 | 0.001068 | 0.0030506 | -0.0036423 | -0.0062207 | -0.0010425 | -50.4547 | 68.9575 | -53.8788 | 68.8705 | -52.9587 | -53.5721 | -52.9953 | -52.3499 | 68.9713 | -53.8193 | -53.4531 | -53.5904 | -53.7964 | -53.5355 | -0.086975 | -0.073242 | -0.16022 | 0.83313 | 0.79651 | 0.21973 | 0.88348 | 0.3067 | -0.027466 | -0.05951 | -122.4838 | 0.20142 | 0.25635 | -0.004578 | 0.28381 | 0.022888 | 0.92011 | 122.7493 | 0.22888 | 0.36621 | 122.8363 | 122.7905 | 122.7493 | 122.7631 | -122.9095 | -122.85 | 122.6624 | 0.33875 | 3.3371 | 1.442
3290.1719 | 123.0515 | -53.7781 | 68.9896 | -0.12161 | 0.0016899 | 0.059889 | 0.066909 | -0.0030442 | 0.0017645 | 0.0062762 | 0.02002 | 0.00046135 | 0.0032044 | -0.0014356 | -0.0019333 | -0.0064343 | -0.0012561 | -50.4456 | 68.9713 | -53.8971 | 68.8477 | -52.9449 | -53.5629 | -52.9816 | -52.3499 | 69.0079 | -53.8376 | -53.4302 | -53.5858 | -53.7964 | -53.5172 | -0.11902 | -0.018311 | -0.14191 | 0.83313 | 0.79651 | 0.21515 | 0.91553 | 0.33417 | -0.059509 | 0.018311 | -122.4197 | 0.19226 | 0.26093 | -0.018311 | 0.32043 | 0.041198 | 0.95215 | 122.7448 | 0.25177 | 0.40741 | 122.8683 | 122.8455 | 122.7493 | 122.7859 | -122.8867 | -122.8271 | 122.6257 | 0.3479 | 3.3325 | 1.4282
3291.1719 | 123.0927 | -53.7964 | 68.9713 | -0.15976 | -0.0017281 | 0.058394 | 0.069259 | 0.001442 | 0.0041143 | 0.0049946 | 0.0078126 | 0.0013159 | 0.001709 | 0.0047594 | -0.0042831 | -0.0015211 | -0.0021107 | -50.441 | 68.9575 | -53.8696 | 68.8522 | -52.9449 | -53.5675 | -52.9724 | -52.3407 | 69.0079 | -53.8284 | -53.4164 | -53.5675 | -53.7872 | -53.5034 | -0.073242 | -0.013732 | -0.11902 | 0.85144 | 0.82398 | 0.22888 | 0.89722 | 0.30212 | -0.032043 | 0.036622 | -122.3877 | 0.22888 | 0.29297 | 0.009156 | 0.32501 | 0.041199 | 0.92468 | 122.7219 | 0.26093 | 0.41199 | 122.8271 | 122.8363 | 122.7539 | 122.8043 | -122.8409 | -122.7997 | 122.6486 | 0.37994 | 3.3554 | 1.4557
3292.1719 | 123.0286 | -53.8055 | 68.985 | 0.1149 | 0.0012625 | 0.066512 | 0.066695 | 0.0020828 | 0.0036871 | 0.0062762 | -0.010498 | 0.00088875 | 0.00042723 | 0.0034778 | -0.0019333 | -0.0053663 | 0.0023755 | -50.6332 | 68.9713 | -53.8879 | 68.8614 | -52.9678 | -53.5629 | -52.9907 | -52.359 | 69.0262 | -53.8193 | -53.4576 | -53.5767 | -53.801 | -53.5263 | -0.082397 | -0.013733 | -0.1236 | 0.83771 | 0.81482 | 0.24262 | 0.89722 | 0.32501 | -0.013733 | 0.041199 | -122.4426 | 0.22888 | 0.27924 | 0.004578 | 0.29297 | 0.018311 | 0.9201 | 122.7493 | 0.24262 | 0.36163 | 122.8592 | 122.8455 | 122.7768 | 122.8317 | -122.8729 | -122.8043 | 122.6669 | 0.3479 | 3.1723 | 1.4465
3293.1719 | 123.0652 | -53.7827 | 68.9758 | -0.052948 | -0.00023294 | 0.059248 | 0.069259 | 0.0033646 | 0.0021917 | 0.005849 | -0.0013428 | -0.00017945 | 0.00042723 | -0.0027174 | -0.0017197 | -0.0064343 | 0.0025891 | -50.1526 | 69.0353 | -53.8284 | 68.811 | -53.0045 | -53.5446 | -53.0136 | -52.359 | 69.0308 | -53.8147 | -53.4393 | -53.5995 | -53.7918 | -53.5217 | -0.045776 | 0.059509 | -0.16479 | 0.7782 | 0.76904 | 0.23804 | 0.81482 | 0.28381 | -0.032043 | 0.054932 | -122.4152 | 0.18311 | 0.26093 | -0.009155 | 0.29297 | 0.022888 | 0.82397 | 122.6395 | 0.21515 | 0.37537 | 122.8638 | 122.8455 | 122.818 | 122.8134 | -122.8043 | -122.7905 | 122.5937 | 0.34332 | 3.6301 | 1.4236
3294.1719 | 123.0286 | -53.7872 | 68.9804 | -0.068207 | 0.0019035 | 0.062025 | 0.068191 | -0.0013352 | 0.0026191 | 0.0079852 | -0.0013428 | 0.00067495 | -0.00021357 | -0.0010084 | -0.0019333 | -0.0066479 | -0.00018806 | -50.4089 | 68.9621 | -53.8559 | 68.6966 | -52.9495 | -53.4897 | -53.0365 | -52.3682 | 69.017 | -53.8239 | -53.4164 | -53.5812 | -53.7735 | -53.5309 | -0.068665 | -0.018311 | -0.28381 | 0.83771 | 0.75073 | 0.29755 | 0.8194 | 0.36621 | -0.036622 | 0.036621 | -122.3969 | 0.20599 | 0.25635 | 0.013732 | 0.29297 | 0.050354 | 0.90637 | 122.5525 | 0.24262 | 0.40741 | 122.818 | 122.8409 | 122.7493 | 122.8043 | -122.8363 | -122.8043 | 122.4838 | 0.37079 | 3.3783 | 1.4191
3295.1719 | 123.0377 | -53.7689 | 68.985 | -0.068207 | -1.9142e-05 | 0.061598 | 0.069259 | 0.00251 | 0.00091009 | 0.0032856 | 0.02002 | 0.0011023 | 0.0023498 | -0.00058098 | -0.0012925 | -0.0053663 | 0.00066654 | -50.4227 | 68.9758 | -53.8513 | 68.8568 | -52.9587 | -53.5675 | -52.977 | -52.3544 | 69.0033 | -53.8193 | -53.4164 | -53.54 | -53.7552 | -53.4988 | -0.082397 | -0.009155 | -0.12817 | 0.81024 | 0.79193 | 0.20142 | 0.87433 | 0.28381 | -0.050354 | 0.018311 | -122.4014 | 0.22888 | 0.27008 | 0.013733 | 0.32043 | 0.064087 | 0.89264 | 122.7081 | 0.27924 | 0.40283 | 122.8271 | 122.8226 | 122.7448 | 122.7722 | -122.8363 | -122.8043 | 122.6257 | 0.35248 | 3.3463 | 1.4145
3296.1719 | 123.0194 | -53.7735 | 69.0033 | -0.12161 | -0.00044654 | 0.059462 | 0.069045 | 0.00251 | 0.0011237 | 0.0047808 | 0.016968 | -0.00060665 | -0.0025636 | 0.00091422 | -0.0040695 | -0.0066479 | -0.0014697 | -50.3677 | 69.0033 | -53.8605 | 68.898 | -52.8992 | -53.5263 | -52.9724 | -52.1393 | 69.0628 | -53.7689 | -53.4302 | -53.6133 | -53.7415 | -53.4897 | -0.086975 | 0 | -0.10529 | 0.87433 | 0.80109 | 0.24719 | 0.88806 | 0.33417 | 0.004578 | 0.059509 | -122.4335 | 0.16022 | 0.28381 | 0.032044 | 0.27924 | 0.027466 | 0.9613 | 122.7585 | 0.15564 | 0.33874 | 122.8638 | 122.8317 | 122.7768 | 122.8363 | -122.8638 | -122.7722 | 122.6715 | 0.34332 | 3.4058 | 1.6342
3297.1719 | 123.0606 | -53.7964 | 68.9667 | -0.037689 | 0.0019035 | 0.06053 | 0.067763 | -0.00090783 | 0.0011237 | 0.0062762 | 0.016968 | 0.00046135 | 0.0029906 | 0.00048702 | -0.0038559 | -0.0062207 | -0.0029651 | -50.386 | 68.9987 | -53.8467 | 68.8797 | -52.9083 | -53.5217 | -52.9266 | -52.3178 | 69.0262 | -53.7918 | -53.2059 | -53.8239 | -53.952 | -53.5721 | -0.050354 | 0.032043 | -0.086975 | 0.88806 | 0.86975 | 0.27466 | 0.9201 | 0.32501 | 0.004578 | 0.059509 | -122.1725 | -0.027466 | 0.2243 | -0.15564 | 0.21973 | -0.16022 | 0.93842 | 122.7264 | -0.032044 | 0.58594 | 122.8455 | 122.818 | 122.7951 | 122.8226 | -122.8134 | -122.7585 | 122.6761 | 0.59052 | 3.4103 | 1.4786
3298.1719 | 122.9095 | -53.8101 | 69.017 | -0.083466 | 0.00040806 | 0.061171 | 0.070541 | 0.0027238 | 0.0021917 | 0.010762 | -0.092895 | 0.0015295 | 0.00042723 | 0.0034778 | -0.0040695 | -0.0032301 | -0.0023243 | -50.4181 | 69.0033 | -53.92 | 68.779 | -53.0594 | -53.6591 | -53.0869 | -52.4643 | 69.0674 | -53.8559 | -53.5172 | -53.7003 | -53.9291 | -53.6041 | -0.10986 | -0.013733 | -0.23804 | 0.75073 | 0.72327 | 0.15106 | 0.83313 | 0.26093 | -0.045776 | 0.050354 | -122.5342 | 0.10986 | 0.20599 | -0.11902 | 0.25177 | -0.073242 | 0.8606 | 122.699 | 0.15564 | 0.33875 | 122.9233 | 122.9233 | 122.8134 | 122.8775 | -122.937 | -122.8729 | 122.5891 | 0.29297 | 3.392 | 1.3458
3299.1719 | 123.0698 | -53.7735 | 69.0079 | -0.098725 | 0.00062166 | 0.060316 | 0.068832 | -0.003685 | 0.0011237 | 0.003072 | 0.035278 | 0.00088875 | 0.0012818 | -0.00229 | 0.00041649 | -0.0055799 | -0.0040333 | -50.386 | 68.985 | -53.8467 | 68.8797 | -52.9175 | -53.5263 | -52.9449 | -52.3361 | 69.0216 | -53.7964 | -53.3844 | -53.5446 | -53.7323 | -53.4805 | -0.073242 | -0.022889 | -0.12817 | 0.85602 | 0.82855 | 0.24719 | 0.90179 | 0.32044 | -0.022888 | 0.013732 | -122.3923 | 0.22888 | 0.29297 | 0.041199 | 0.31586 | 0.064087 | 0.92926 | 122.7264 | 0.25177 | 0.41199 | 122.8317 | 122.818 | 122.7585 | 122.7951 | -122.8546 | -122.8043 | 122.6532 | 0.3891 | 3.3875 | 1.4374
3300.1719 | 123.0377 | -53.7689 | 69.017 | -0.060578 | 0.00040806 | 0.061171 | 0.067336 | -0.00048063 | 0.0026191 | 0.003072 | 0.032227 | 0.00024775 | 0.00085443 | 0.0019824 | -0.0023605 | -0.0047253 | 0.00066654 | -50.3265 | 69.0033 | -53.8376 | 69.0628 | -52.652 | -53.7918 | -53.2013 | -52.3544 | 69.0308 | -53.8055 | -53.3752 | -53.5538 | -53.7506 | -53.4851 | -0.068664 | -0.013733 | 0.045776 | 1.1169 | 0.56763 | -0.022888 | 0.63629 | 0.045776 | -0.036621 | 0.013733 | -122.3923 | 0.21515 | 0.28381 | 0.018311 | 0.32044 | 0.054932 | 1.1856 | 122.9004 | 0.25177 | 0.4303 | 122.8409 | 122.8363 | 122.7722 | 122.7997 | -122.8546 | -122.8226 | 122.8317 | 0.39368 | 3.4424 | 1.4145
3301.1719 | 123.0331 | -53.7689 | 68.9941 | -0.091095 | 0.0023307 | 0.062025 | 0.070113 | -0.001976 | 0.0024053 | 0.0022174 | 0.041382 | 0.00046135 | -0.00064077 | 0.0032642 | -0.0023605 | -0.0062207 | 0.0034435 | -50.3311 | 69.0308 | -53.8376 | 68.9117 | -52.8992 | -53.4851 | -52.9495 | -52.121 | 69.1132 | -53.7506 | -53.389 | -53.5904 | -53.7369 | -53.476 | -0.068664 | 0.036621 | -0.082398 | 0.86975 | 0.8194 | 0.28381 | 0.88806 | 0.35248 | 0.018311 | 0.11902 | -122.3831 | 0.17853 | 0.29297 | 0.032044 | 0.27466 | 0.013733 | 0.93841 | 122.7493 | 0.16022 | 0.36163 | 122.8683 | 122.8638 | 122.7997 | 122.8821 | -122.8317 | -122.7448 | 122.6807 | 0.37994 | 3.4378 | 1.6479
3302.1719 | 123.0469 | -53.7735 | 69.0079 | -0.075836 | -0.0015145 | 0.060103 | 0.068404 | -0.00090783 | 0.0041143 | 0.00414 | 0.02002 | 0.0019567 | 0.00042723 | 0.0032642 | -0.00022431 | -0.0030163 | -0.0018971 | -50.386 | 69.0216 | -53.8376 | 68.8614 | -52.9633 | -53.5629 | -52.9678 | -52.359 | 69.0537 | -53.7827 | -53.4073 | -53.5355 | -53.7552 | -53.4805 | -0.064086 | 0.013732 | -0.14648 | 0.81024 | 0.80566 | 0.21057 | 0.86975 | 0.27466 | -0.009155 | 0.045776 | -122.4152 | 0.23804 | 0.29297 | 0.018311 | 0.30212 | 0.027466 | 0.87433 | 122.699 | 0.24719 | 0.37537 | 122.8592 | 122.8363 | 122.7951 | 122.8271 | -122.8455 | -122.7905 | 122.6349 | 0.36621 | 3.3875 | 1.4145
3303.1719 | 122.9507 | -53.7735 | 69.0811 | -0.037689 | -0.0017281 | 0.061385 | 0.069259 | -0.00026703 | 0.00026909 | 0.0034992 | -0.034912 | 0.0011023 | 0.002777 | 0.0049732 | -0.0012925 | -0.0040845 | 0.00088014 | -50.3952 | 69.072 | -53.8651 | 68.8019 | -53.0411 | -53.627 | -53.0594 | -52.4597 | 69.1269 | -53.8055 | -53.4622 | -53.6362 | -53.8513 | -53.5538 | -0.091552 | -0.009156 | -0.27924 | 0.73242 | 0.71411 | 0.14648 | 0.80566 | 0.23804 | -0.032043 | 0.045776 | -122.5433 | 0.13733 | 0.21973 | -0.077819 | 0.25177 | -0.045776 | 0.82397 | 122.6669 | 0.16937 | 0.34332 | 122.937 | 122.9324 | 122.8455 | 122.9004 | -122.9462 | -122.8867 | 122.5754 | 0.31128 | 3.3783 | 1.3138
3304.1719 | 123.0103 | -53.746 | 69.017 | -0.052948 | -0.0021555 | 0.059462 | 0.070327 | -0.0049668 | 0.0039007 | 0.0077716 | -0.022705 | 0.0021703 | 0.00064083 | -0.0033582 | -0.0032151 | -0.0051527 | 0.0017345 | -50.2991 | 69.0308 | -53.8284 | 68.7103 | -53.0914 | -53.4348 | -52.9404 | -52.2858 | 69.0537 | -53.7872 | -53.3615 | -53.4988 | -53.714 | -53.4668 | -0.082397 | 0.013733 | -0.3067 | 0.6546 | 0.80566 | 0.31128 | 0.88806 | 0.39368 | -0.041198 | 0.036621 | -122.3785 | 0.24719 | 0.27924 | 0.032044 | 0.32043 | 0.073242 | 0.737 | 122.5388 | 0.28839 | 0.42572 | 122.8592 | 122.8409 | 122.7768 | 122.7997 | -122.8455 | -122.8043 | 122.4564 | 0.38452 | 3.447 | 1.4603
3305.1719 | 123.0286 | -53.714 | 69.0537 | -0.12161 | -0.0025827 | 0.060316 | 0.06755 | -0.001976 | 0.00069649 | 0.0034992 | 0.041382 | 3.4148e-05 | 0.00042723 | -0.0016492 | -0.0025741 | -0.0047253 | 0.0017345 | -50.3311 | 69.0445 | -53.8193 | 68.8889 | -52.9266 | -53.5355 | -52.9449 | -52.3178 | 69.0537 | -53.7689 | -53.3752 | -53.5034 | -53.7277 | -53.4439 | -0.10529 | -0.009155 | -0.16479 | 0.78735 | 0.76904 | 0.17853 | 0.87433 | 0.28381 | -0.054932 | 0 | -122.4289 | 0.21057 | 0.27008 | -0.013733 | 0.32501 | 0.041199 | 0.89264 | 122.7081 | 0.2655 | 0.39368 | 122.8638 | 122.8226 | 122.7585 | 122.7676 | -122.8729 | -122.8226 | 122.6028 | 0.33874 | 3.3829 | 1.3962
3306.1719 | 123.056 | -53.7369 | 69.0353 | -0.11398 | -0.0013009 | 0.061598 | 0.06755 | 0.00037377 | 0.0015509 | 0.0022174 | 0.02002 | -0.00060665 | 2.8e-08 | 0.0015552 | -0.0025741 | -0.0072889 | -0.0031787 | -50.3448 | 69.0216 | -53.8193 | 68.8797 | -52.9312 | -53.54 | -52.9495 | -52.3544 | 69.0491 | -53.7689 | -53.3798 | -53.5263 | -53.7277 | -53.4668 | -0.082398 | -0.013733 | -0.15564 | 0.80566 | 0.78735 | 0.19684 | 0.86975 | 0.27924 | -0.032044 | 0.013733 | -122.4152 | 0.21057 | 0.27008 | 0.009155 | 0.30212 | 0.041199 | 0.88806 | 122.699 | 0.24262 | 0.3891 | 122.8409 | 122.818 | 122.7585 | 122.7859 | -122.8546 | -122.8043 | 122.6166 | 0.35706 | 3.392 | 1.3824
3307.1719 | 123.0698 | -53.7369 | 69.0628 | -0.075836 | -0.00087374 | 0.061598 | 0.068832 | -0.0017624 | 0.0032599 | 0.0056354 | 0.023071 | -0.00082025 | 0.0021362 | 0.002196 | -0.0023605 | -0.0055799 | 0.00088014 | -50.2945 | 69.0079 | -53.8055 | 68.9163 | -52.8854 | -53.4897 | -52.9037 | -52.2629 | 69.0857 | -53.7689 | -53.334 | -53.4851 | -53.7003 | -53.4393 | -0.068665 | -0.054931 | -0.14648 | 0.85144 | 0.83313 | 0.24719 | 0.90179 | 0.31586 | -0.032044 | 0.022888 | -122.3969 | 0.25177 | 0.29755 | 0.036621 | 0.32959 | 0.068665 | 0.9201 | 122.7219 | 0.28381 | 0.43488 | 122.8134 | 122.8546 | 122.7448 | 122.8226 | -122.8683 | -122.8317 | 122.6532 | 0.40283 | 3.4424 | 1.474
3308.1719 | 123.0011 | -53.714 | 69.0857 | -0.091095 | 0.00083526 | 0.062666 | 0.069259 | -0.00026703 | 0.00069649 | 0.0034992 | -0.047119 | 0.0028113 | 2.8e-08 | 0.0013416 | -0.0017197 | -0.0055799 | 0.0015209 | -50.3174 | 69.0582 | -53.8605 | 68.8339 | -53.0182 | -53.5904 | -53.0182 | -52.4002 | 69.1223 | -53.7918 | -53.4439 | -53.6041 | -53.833 | -53.5034 | -0.14649 | -0.027465 | -0.25177 | 0.6958 | 0.6958 | 0.1236 | 0.84229 | 0.27008 | -0.07782 | 0.036621 | -122.5296 | 0.10986 | 0.21057 | -0.11902 | 0.28839 | -0.041199 | 0.84229 | 122.6944 | 0.18768 | 0.3479 | 122.9187 | 122.9141 | 122.7722 | 122.8363 | -122.9462 | -122.8775 | 122.5479 | 0.27008 | 3.3966 | 1.3138
3309.1719 | 123.0331 | -53.7277 | 69.0308 | -0.11398 | 0.00019446 | 0.060744 | 0.069045 | -0.00048063 | 0.0017645 | 0.0071308 | 0.010864 | 0.0011023 | 0.00021363 | 0.002196 | -0.0015061 | -0.0068615 | -0.0027515 | -50.3586 | 69.0537 | -53.8101 | 68.8477 | -52.977 | -53.5629 | -52.9678 | -52.3682 | 69.0811 | -53.7872 | -53.3936 | -53.54 | -53.7643 | -53.4943 | -0.082398 | 0.022888 | -0.18311 | 0.75073 | 0.75989 | 0.16479 | 0.84229 | 0.24719 | -0.059509 | 0.050354 | -122.4243 | 0.18768 | 0.23346 | -0.036621 | 0.29297 | 0.022888 | 0.83313 | 122.6578 | 0.24719 | 0.39368 | 122.8638 | 122.8683 | 122.7814 | 122.8088 | -122.8409 | -122.818 | 122.5754 | 0.33417 | 3.3691 | 1.3596
3310.1719 | 123.0331 | -53.7415 | 69.072 | -0.091095 | 0.0010489 | 0.062239 | 0.069472 | -0.0013352 | 0.0034735 | 0.003072 | 0.026123 | 0.00088875 | 0.00064083 | -0.010621 | -0.0012925 | -0.0057935 | 0.0023755 | -50.2991 | 69.0353 | -53.8101 | 68.8797 | -52.9358 | -53.5217 | -52.9495 | -52.3178 | 69.0857 | -53.7552 | -53.3661 | -53.5126 | -53.7277 | -53.4531 | -0.068665 | -0.036621 | -0.19226 | 0.80566 | 0.79193 | 0.21973 | 0.8606 | 0.28839 | -0.013733 | 0.013733 | -122.438 | 0.22888 | 0.28839 | 0.013733 | 0.30212 | 0.027466 | 0.87433 | 122.6898 | 0.24261 | 0.3891 | 122.8455 | 122.8409 | 122.7768 | 122.8271 | -122.8821 | -122.8271 | 122.6212 | 0.37537 | 3.4424 | 1.4236
3311.1719 | 123.0423 | -53.7369 | 69.0811 | -0.060578 | -1.9142e-05 | 0.060744 | 0.070327 | -0.0013352 | 0.0026191 | 0.003072 | 0.029175 | -0.00060665 | 0.0025634 | 0.0051868 | -0.00065151 | -0.0055799 | -0.0044605 | -50.3082 | 69.0445 | -53.8101 | 68.866 | -52.9358 | -53.5172 | -52.9587 | -52.3407 | 69.0628 | -53.7643 | -53.3798 | -53.5309 | -53.7369 | -53.4668 | -0.073243 | -0.036621 | -0.21515 | 0.80109 | 0.7782 | 0.21973 | 0.85144 | 0.29297 | -0.027466 | -0.018311 | -122.4609 | 0.20599 | 0.27008 | 0 | 0.29755 | 0.027466 | 0.87433 | 122.6761 | 0.23346 | 0.38452 | 122.8546 | 122.8271 | 122.7814 | 122.7997 | -122.8912 | -122.8455 | 122.6028 | 0.35706 | 3.4286 | 1.3962
3312.1719 | 123.0606 | -53.7094 | 69.0308 | -0.091095 | 0.0010489 | 0.059889 | 0.070541 | 0.001442 | 5.5488e-05 | 0.0047808 | 0.016968 | 0.0017431 | 0.00042723 | -0.0020764 | -0.0019333 | -0.0047253 | -0.0031787 | -50.2762 | 69.0445 | -53.8101 | 68.9301 | -52.8809 | -53.4851 | -52.9037 | -52.2858 | 69.072 | -53.7506 | -53.3295 | -53.4943 | -53.6911 | -53.4302 | -0.10071 | 0.013733 | -0.10071 | 0.82855 | 0.80566 | 0.22431 | 0.90637 | 0.32501 | -0.041198 | 0.041198 | -122.3602 | 0.21515 | 0.27924 | 0.018311 | 0.32043 | 0.059509 | 0.92926 | 122.7402 | 0.25635 | 0.42114 | 122.8546 | 122.8226 | 122.7539 | 122.7814 | -122.8409 | -122.7814 | 122.6395 | 0.37994 | 3.4332 | 1.4236
3313.1719 | 122.9324 | -53.7277 | 69.1315 | -0.03006 | -0.00066014 | 0.060103 | 0.067977 | 0.0018692 | 0.0028327 | 0.0011494 | -0.092895 | 0.0019567 | -0.00021357 | 0.001128 | -0.0034287 | -0.0045117 | 0.00045294 | -50.3128 | 69.1177 | -53.801 | 68.8385 | -52.9953 | -53.4805 | -52.803 | -52.5055 | 69.1635 | -53.7735 | -53.4348 | -53.5995 | -53.801 | -53.5263 | -0.073242 | -0.013733 | -0.29297 | 0.73242 | 0.92468 | 0.24719 | 0.99792 | 0.32043 | -0.045777 | 0.032043 | -122.5662 | 0.12817 | 0.20142 | -0.073242 | 0.24719 | -0.027465 | 0.80566 | 122.6395 | 0.17395 | 0.33875 | 122.9187 | 122.937 | 122.8455 | 122.8912 | -122.9324 | -122.905 | 122.5662 | 0.29297 | 3.4149 | 1.2222
3314.1719 | 123.056 | -53.7003 | 69.0765 | -0.098725 | -0.0015145 | 0.060744 | 0.069259 | -0.00069423 | 0.0039007 | 0.0049946 | 0.013916 | -0.0010339 | -0.00021357 | -0.00229 | -0.0032151 | -0.0062207 | -0.00061526 | -50.2808 | 69.0765 | -53.8055 | 68.9117 | -52.9037 | -53.5217 | -52.9266 | -52.3178 | 69.1086 | -53.7369 | -53.3478 | -53.4943 | -53.7094 | -53.4439 | -0.10529 | 0 | -0.16479 | 0.79651 | 0.77362 | 0.17853 | 0.87891 | 0.28381 | -0.036621 | 0.032044 | -122.4243 | 0.20599 | 0.25635 | -0.009156 | 0.29297 | 0.027465 | 0.90179 | 122.7173 | 0.24261 | 0.3891 | 122.8821 | 122.8455 | 122.7768 | 122.8088 | -122.8821 | -122.8134 | 122.612 | 0.35248 | 3.4195 | 1.3824
3315.1719 | 123.0331 | -53.6728 | 69.0628 | -0.083466 | -0.00066014 | 0.062453 | 0.069472 | -5.343e-05 | 0.0015509 | 0.0034992 | 0.035278 | 0.00067495 | 0.00064083 | 0.0051868 | -0.0021469 | -0.0055799 | 0.00066654 | -50.235 | 69.0903 | -53.7918 | 68.9255 | -52.8671 | -53.4714 | -52.8946 | -52.2125 | 69.1132 | -53.7506 | -53.3157 | -53.4668 | -53.6682 | -53.4073 | -0.11902 | 0.027466 | -0.13733 | 0.80566 | 0.7782 | 0.20142 | 0.89722 | 0.32043 | -0.077819 | 0.050354 | -122.3785 | 0.20599 | 0.2655 | 0.004578 | 0.34332 | 0.082397 | 0.92468 | 122.7173 | 0.28381 | 0.43488 | 122.8821 | 122.8638 | 122.7631 | 122.7859 | -122.8546 | -122.8134 | 122.5983 | 0.35706 | 3.4378 | 1.4603
3316.1719 | 123.0377 | -53.7003 | 69.0674 | -0.083466 | 0.0021171 | 0.06053 | 0.0699 | -0.0026168 | 0.0024053 | 0.0034992 | 0.0047608 | 3.4148e-05 | 0.00085443 | 0.005614 | -0.00043791 | -0.0068615 | -0.0010425 | -50.3082 | 69.0674 | -53.801 | 68.8751 | -52.9449 | -53.5446 | -52.9678 | -52.3453 | 69.1406 | -53.7735 | -53.3798 | -53.5446 | -53.7918 | -53.3569 | -0.10071 | 0 | -0.19226 | 0.75531 | 0.73242 | 0.15564 | 0.83313 | 0.25635 | -0.073243 | 0.073242 | -122.4472 | 0.15564 | 0.34332 | -0.091553 | 0.41656 | -0.01831 | 0.85602 | 122.6761 | 0.22888 | 0.39368 | 122.8683 | 122.9141 | 122.7676 | 122.8409 | -122.8683 | -122.8409 | 122.5754 | 0.32043 | 3.392 | 1.355
3317.1719 | 122.9919 | -53.714 | 69.0674 | -0.10635 | -0.0017281 | 0.061385 | 0.070968 | -0.0015488 | 0.0034735 | 0.0056354 | -0.0074462 | -0.00082025 | 0.0012818 | -0.0025036 | -0.0030013 | -0.0040845 | 0.00045294 | -50.2716 | 69.0811 | -53.7735 | 68.8843 | -52.9495 | -53.5721 | -52.9587 | -52.3499 | 69.0857 | -53.7231 | -53.3707 | -53.5355 | -53.7506 | -53.4622 | -0.05951 | 0.013733 | -0.18311 | 0.76447 | 0.75531 | 0.14191 | 0.81482 | 0.20142 | -0.009156 | 0.01831 | -122.4381 | 0.17853 | 0.25177 | -0.036621 | 0.26093 | -0.027465 | 0.82398 | 122.6578 | 0.18768 | 0.35248 | 122.8546 | 122.8088 | 122.7951 | 122.7997 | -122.8409 | -122.7905 | 122.5983 | 0.34332 | 3.4424 | 1.3641
3318.1719 | 123.0377 | -53.7094 | 69.072 | -0.11398 | -0.00044654 | 0.063521 | 0.069259 | -0.0028304 | 0.00069649 | 0.0034992 | -0.0013428 | 0.00067495 | -0.0010682 | -0.005708 | -0.0019333 | -0.0064343 | 0.0034435 | -50.2716 | 69.104 | -53.7827 | 68.898 | -52.9404 | -53.5446 | -52.9541 | -52.3361 | 69.0903 | -53.7552 | -53.3707 | -53.5538 | -53.7643 | -53.4622 | -0.073242 | 0.032044 | -0.17395 | 0.76904 | 0.75531 | 0.16479 | 0.82855 | 0.23804 | -0.045776 | 0.018311 | -122.4426 | 0.15564 | 0.24719 | -0.054931 | 0.29297 | -0.009155 | 0.84229 | 122.6807 | 0.20142 | 0.38452 | 122.8867 | 122.8455 | 122.8134 | 122.7997 | -122.8546 | -122.8271 | 122.6074 | 0.33875 | 3.4378 | 1.3733
3319.1719 | 122.9828 | -53.714 | 69.0994 | -0.098725 | -0.00044654 | 0.061598 | 0.069259 | -0.0024032 | 0.0045417 | 0.005849 | -0.0074462 | -0.00039305 | 0.00042723 | -0.0044262 | -0.0032151 | -0.0034437 | 0.0021619 | -50.267 | 69.0628 | -53.7689 | 68.9072 | -52.9175 | -53.5355 | -52.9358 | -52.3407 | 69.104 | -53.746 | -53.3615 | -53.54 | -53.7506 | -53.4714 | -0.054932 | -0.036621 | -0.19226 | 0.79651 | 0.7782 | 0.17853 | 0.83313 | 0.23346 | -0.032044 | 0.004578 | -122.4609 | 0.17395 | 0.24261 | -0.036621 | 0.27466 | -0.004577 | 0.85144 | 122.6761 | 0.20599 | 0.38452 | 122.8317 | 122.85 | 122.7768 | 122.818 | -122.8683 | -122.8455 | 122.6212 | 0.35248 | 3.447 | 1.3733
3320.1719 | 123.0011 | -53.7048 | 69.0811 | -0.10635 | -0.0015145 | 0.061598 | 0.070113 | -0.0030442 | 0.0013373 | 0.0060626 | -0.016602 | 0.0015295 | 0.0023498 | 0.0034778 | -0.0012925 | -0.0064343 | -0.0018971 | -50.2487 | 69.0811 | -53.7598 | 68.9804 | -52.8259 | -53.5538 | -53.0136 | -52.3407 | 69.1086 | -53.7369 | -53.3569 | -53.508 | -53.7552 | -53.4531 | -0.054932 | 0 | -0.10071 | 0.87891 | 0.69122 | 0.15106 | 0.74616 | 0.20599 | -0.032043 | 0.027466 | -122.4381 | 0.19684 | 0.25177 | -0.050354 | 0.28381 | -0.018311 | 0.93384 | 122.7402 | 0.22888 | 0.37994 | 122.8409 | 122.8455 | 122.7859 | 122.8134 | -122.8409 | -122.818 | 122.6852 | 0.3479 | 3.4561 | 1.3641
3321.1719 | 122.9736 | -53.7048 | 69.0857 | -0.091095 | -0.0010873 | 0.060316 | 0.067336 | 0.0016556 | 0.0032599 | 0.00414 | -0.016602 | 0.00024775 | 0.00064083 | -0.00079478 | -0.00086511 | -0.0047253 | -0.0012561 | -50.235 | 69.0857 | -53.7689 | 68.9026 | -52.9221 | -53.5309 | -52.9404 | -52.3224 | 69.1177 | -53.7186 | -53.2974 | -53.6133 | -53.7735 | -53.4622 | -0.064087 | 0 | -0.18311 | 0.78278 | 0.76447 | 0.17395 | 0.82855 | 0.23804 | -0.013733 | 0.032044 | -122.3831 | 0.091553 | 0.24262 | -0.068665 | 0.25635 | -0.054932 | 0.84686 | 122.6715 | 0.10529 | 0.42114 | 122.8546 | 122.8363 | 122.7905 | 122.8226 | -122.8546 | -122.8043 | 122.6074 | 0.40741 | 3.4698 | 1.3824
3322.1719 | 122.9874 | -53.6819 | 69.0765 | -0.068207 | 0.0029715 | 0.061812 | 0.071395 | 0.001442 | 0.0030463 | 0.0067036 | -0.022705 | -0.00039305 | 0.001709 | -0.00464 | -0.0030013 | -0.0038709 | 2.554e-05 | -50.2075 | 69.072 | -53.7781 | 68.9392 | -52.8625 | -53.5172 | -52.9129 | -52.2812 | 69.1269 | -53.6911 | -53.3249 | -53.5172 | -53.746 | -53.4485 | -0.09613 | -0.004578 | -0.13733 | 0.8194 | 0.76904 | 0.1648 | 0.86517 | 0.26093 | -0.009155 | 0.050354 | -122.4014 | 0.1648 | 0.23346 | -0.064087 | 0.24262 | -0.054932 | 0.91553 | 122.7173 | 0.17395 | 0.36621 | 122.85 | 122.818 | 122.7539 | 122.8088 | -122.8546 | -122.7676 | 122.6212 | 0.35706 | 3.4744 | 1.4008
3323.1719 | 123.0148 | -53.7094 | 69.0628 | -0.12924 | 0.0031851 | 0.061385 | 0.071181 | -0.00026703 | 0.0021917 | 0.005849 | -0.03186 | 0.0017431 | 0.00042723 | 0.008391 | -0.00086511 | -0.0070753 | -0.0027515 | -50.2029 | 69.0765 | -53.7735 | 68.9301 | -52.8534 | -53.4988 | -52.9129 | -52.2446 | 69.1406 | -53.714 | -53.3249 | -53.4988 | -53.7048 | -53.4348 | -0.064087 | 0.013733 | -0.13275 | 0.85602 | 0.79651 | 0.21057 | 0.8606 | 0.27466 | -0.004577 | 0.07782 | -122.3877 | 0.21057 | 0.27466 | 0.004578 | 0.27924 | 0.009155 | 0.9201 | 122.7036 | 0.21515 | 0.3891 | 122.85 | 122.8546 | 122.7859 | 122.85 | -122.8363 | -122.7768 | 122.6395 | 0.38452 | 3.5065 | 1.4648
3324.1719 | 122.9874 | -53.6865 | 69.0582 | -0.068207 | 0.0021171 | 0.060744 | 0.070327 | 0.00058737 | 0.0015509 | 0.0073444 | -0.022705 | 0.0011023 | 0.00042723 | 5.9824e-05 | -0.0019333 | -0.0042981 | -0.0029651 | -50.2121 | 69.0765 | -53.7735 | 68.9072 | -52.8854 | -53.5172 | -52.9358 | -52.3041 | 69.1177 | -53.7186 | -53.334 | -53.5217 | -53.7277 | -53.4302 | -0.086976 | 0.01831 | -0.15106 | 0.80109 | 0.75073 | 0.16937 | 0.83771 | 0.25635 | -0.032044 | 0.059509 | -122.3923 | 0.16479 | 0.25635 | -0.041199 | 0.28839 | -0.009155 | 0.88806 | 122.6807 | 0.19684 | 0.38452 | 122.85 | 122.8363 | 122.7631 | 122.8043 | -122.8317 | -122.7768 | 122.5937 | 0.35248 | 3.4744 | 1.3824
3325.1719 | 122.9919 | -53.6682 | 69.0903 | -0.16739 | 0.0016899 | 0.061598 | 0.069259 | -0.0024032 | 0.0021917 | 0.0077716 | -0.034912 | 0.0017431 | 0.0019226 | -0.0065626 | -0.0025741 | -0.0047253 | 0.00066654 | -50.1938 | 69.0628 | -53.7781 | 68.9484 | -52.858 | -53.5217 | -52.9175 | -52.2537 | 69.1315 | -53.7231 | -53.3157 | -53.4943 | -53.7277 | -53.4256 | -0.10986 | -0.027466 | -0.14191 | 0.81024 | 0.75073 | 0.14648 | 0.8606 | 0.25635 | -0.054932 | 0.041199 | -122.406 | 0.17395 | 0.24262 | -0.059509 | 0.29755 | -0.004577 | 0.9201 | 122.7264 | 0.22888 | 0.40741 | 122.8409 | 122.8546 | 122.731 | 122.7997 | -122.8683 | -122.8134 | 122.6166 | 0.35248 | 3.4744 | 1.4145
3326.1719 | 123.0057 | -53.6774 | 69.0811 | -0.18265 | -0.00044654 | 0.062453 | 0.069472 | 0.00016017 | 0.0039007 | 0.0071308 | -0.03186 | -0.0010339 | 0.00042723 | 0.0013416 | -0.0012925 | -0.0047253 | -0.00061526 | -50.1801 | 69.0765 | -53.7415 | 68.9438 | -52.8397 | -53.4897 | -52.9037 | -52.2354 | 69.1269 | -53.7003 | -53.3249 | -53.4988 | -53.7003 | -53.4027 | -0.064087 | -0.004578 | -0.13733 | 0.83771 | 0.77362 | 0.18768 | 0.83771 | 0.25177 | -0.022888 | 0.045776 | -122.406 | 0.17853 | 0.27466 | -0.022888 | 0.29755 | 0 | 0.90179 | 122.6852 | 0.20142 | 0.37537 | 122.818 | 122.8271 | 122.7539 | 122.8043 | -122.8226 | -122.7814 | 122.6212 | 0.35248 | 3.4973 | 1.442
3327.1719 | 122.9645 | -53.6591 | 69.0994 | -0.15213 | -1.9142e-05 | 0.061385 | 0.068191 | -0.00069423 | 0.0026191 | 0.0032856 | -0.022705 | 3.4148e-05 | 0.0014954 | -0.00229 | -0.00086511 | -0.0049389 | 0.0017345 | -50.1846 | 69.0903 | -53.7415 | 68.9392 | -52.89 | -53.5034 | -52.9221 | -52.2766 | 69.136 | -53.714 | -53.3249 | -53.4897 | -53.7094 | -53.4439 | -0.082397 | -0.009155 | -0.16022 | 0.76904 | 0.737 | 0.15564 | 0.8194 | 0.23804 | -0.054931 | 0.036621 | -122.4243 | 0.16937 | 0.21515 | -0.050354 | 0.27008 | 0.004577 | 0.85144 | 122.6807 | 0.2243 | 0.3891 | 122.8317 | 122.85 | 122.7493 | 122.7951 | -122.8409 | -122.8134 | 122.5983 | 0.33417 | 3.4744 | 1.3824
3328.1719 | 122.9828 | -53.6545 | 69.1223 | -0.1445 | 0.0021171 | 0.061385 | 0.069686 | 0.00016017 | 0.0024053 | 0.0056354 | -0.041016 | 0.0021703 | 0.00064083 | -0.0052808 | -0.0025741 | -0.0034437 | -0.00061526 | -50.1617 | 69.104 | -53.7277 | 68.9392 | -52.8397 | -53.5034 | -52.9129 | -52.2491 | 69.1223 | -53.6865 | -53.3157 | -53.4988 | -53.7048 | -53.421 | -0.073242 | -0.01831 | -0.1831 | 0.81482 | 0.74158 | 0.15106 | 0.81482 | 0.2243 | -0.032043 | 0 | -122.438 | 0.15564 | 0.23346 | -0.050354 | 0.2655 | -0.018311 | 0.88806 | 122.6669 | 0.18768 | 0.37079 | 122.8317 | 122.8088 | 122.7585 | 122.7768 | -122.85 | -122.8088 | 122.5937 | 0.33875 | 3.4927 | 1.4053
3329.1719 | 123.0515 | -53.6133 | 69.1132 | -0.15976 | -0.00044654 | 0.06288 | 0.069259 | 0.0010148 | 0.0045417 | 0.0067036 | -0.06543 | -0.0010339 | 2.8e-08 | 0.00027342 | -0.0049241 | -0.0036573 | -0.0023243 | -50.1251 | 69.0811 | -53.746 | 68.8385 | -52.7802 | -53.2608 | -52.8168 | -52.1805 | 69.1452 | -53.6911 | -53.27 | -53.4576 | -53.6865 | -53.3844 | -0.13275 | -0.032043 | -0.27466 | 0.83313 | 0.79651 | 0.35248 | 0.92926 | 0.48523 | -0.07782 | 0.032044 | -122.3831 | 0.15564 | 0.22888 | -0.073242 | 0.3067 | 0.004578 | 0.96588 | 122.5845 | 0.23346 | 0.42114 | 122.8271 | 122.8363 | 122.6944 | 122.7585 | -122.8592 | -122.8043 | 122.4518 | 0.34332 | 3.4882 | 1.4328
3330.1719 | 123.0515 | -53.6087 | 69.104 | -0.13687 | 0.00040806 | 0.064162 | 0.0699 | -0.0013352 | 0.0013373 | 0.005849 | -0.074585 | 0.0011023 | 0.00064083 | 0.001128 | -0.0021469 | -0.0062207 | -0.0025379 | -50.1205 | 69.1086 | -53.7231 | 68.9758 | -52.8488 | -53.4805 | -52.89 | -52.1667 | 69.1544 | -53.7369 | -53.2745 | -53.4164 | -53.6774 | -53.3569 | -0.11444 | 0.004578 | -0.12817 | 0.75989 | 0.71869 | 0.12817 | 0.83313 | 0.24262 | -0.12817 | 0.050354 | -122.3785 | 0.19226 | 0.25177 | -0.068664 | 0.37994 | 0.059509 | 0.87433 | 122.699 | 0.32043 | 0.46234 | 122.8317 | 122.8912 | 122.7173 | 122.7631 | -122.8271 | -122.8409 | 122.5845 | 0.33417 | 3.4882 | 1.442
3331.1719 | 123.0423 | -53.6453 | 69.1223 | -0.11398 | 0.00019446 | 0.062666 | 0.069686 | 0.00016017 | 0.0032599 | 0.0056354 | -0.019653 | -0.00060665 | 0.001709 | 0.0015552 | -0.0023605 | -0.0034437 | 0.0010937 | -50.1251 | 69.1132 | -53.6957 | 68.985 | -52.8122 | -53.4439 | -52.8671 | -52.1896 | 69.1589 | -53.6682 | -53.2471 | -53.4439 | -53.6774 | -53.3615 | -0.050354 | -0.009155 | -0.13733 | 0.83313 | 0.7782 | 0.20142 | 0.82855 | 0.25177 | -0.022888 | 0.036622 | -122.3694 | 0.20142 | 0.28381 | -0.032043 | 0.3067 | -0.009155 | 0.88348 | 122.6807 | 0.2243 | 0.42114 | 122.8088 | 122.8271 | 122.7585 | 122.8043 | -122.818 | -122.7905 | 122.6303 | 0.39825 | 3.5202 | 1.4557
3332.1719 | 123.0331 | -53.5858 | 69.1315 | -0.10635 | 0.0019035 | 0.059889 | 0.068191 | -0.0030442 | 0.0019781 | 0.0037128 | 0.03833 | -0.0018885 | 0.00064083 | 0.00091422 | -0.00086511 | -0.0034437 | 0.0010937 | -50.0565 | 69.1818 | -53.6545 | 69.0857 | -52.7115 | -53.3386 | -52.7664 | -52.1118 | 69.2047 | -53.6179 | -53.334 | -53.2928 | -53.6179 | -53.3615 | -0.068665 | 0.050354 | -0.045777 | 0.87433 | 0.8194 | 0.24719 | 0.88806 | 0.31586 | -0.032044 | 0.073242 | -122.4655 | 0.29297 | 0.2243 | -0.032044 | 0.25635 | 0 | 0.94299 | 122.7402 | 0.32501 | 0.28381 | 122.8363 | 122.8226 | 122.7676 | 122.7905 | -122.7859 | -122.7493 | 122.6715 | 0.25177 | 3.5294 | 1.474
3333.1719 | 123.0331 | -53.6041 | 69.1772 | -0.12924 | 0.00083526 | 0.063521 | 0.070113 | 0.005928 | 0.0028327 | 0.0071308 | 0.0047608 | -0.00060665 | -0.00021357 | 0.00048702 | -0.0030013 | -0.0060071 | 0.00088014 | -50.0656 | 69.1406 | -53.6957 | 69.0125 | -52.7985 | -53.6087 | -53.0731 | -52.1027 | 69.1956 | -53.6316 | -53.2333 | -53.4164 | -53.6636 | -53.3203 | -0.091553 | -0.036621 | -0.16479 | 0.80566 | 0.53101 | -0.004578 | 0.62256 | 0.086975 | -0.027466 | 0.018311 | -122.4106 | 0.18768 | 0.28381 | -0.059509 | 0.31128 | -0.032043 | 0.89722 | 122.7081 | 0.21515 | 0.39825 | 122.8363 | 122.8271 | 122.7448 | 122.7997 | -122.8729 | -122.8088 | 122.6166 | 0.37079 | 3.5385 | 1.5015
3334.1719 | 123.0331 | -53.6041 | 69.1772 | -0.11398 | -0.00044654 | 0.061385 | 0.069259 | 0.00080117 | 0.0026191 | 0.0037128 | -0.034912 | 0.00046135 | 0.0012818 | -0.0050672 | -0.0021469 | -0.0075025 | -0.0046741 | -50.0839 | 69.1635 | -53.6819 | 69.0399 | -52.7618 | -53.4027 | -52.8214 | -52.1439 | 69.2047 | -53.6453 | -53.2196 | -53.4027 | -53.6362 | -53.3249 | -0.07782 | -0.013733 | -0.13733 | 0.84229 | 0.78278 | 0.20142 | 0.8606 | 0.27924 | -0.041199 | 0.027466 | -122.3969 | 0.20142 | 0.27924 | -0.032043 | 0.32043 | 0.009156 | 0.92011 | 122.7219 | 0.24262 | 0.42572 | 122.8455 | 122.85 | 122.7676 | 122.8088 | -122.8592 | -122.8226 | 122.644 | 0.38452 | 3.5202 | 1.4603
3335.1719 | 123.0469 | -53.5721 | 69.191 | -0.15976 | 0.0014761 | 0.062239 | 0.070541 | -0.001976 | -0.00037171 | 0.0045672 | -0.025757 | 0.00067495 | 0.0023498 | -0.0014356 | -0.0015061 | -0.0051527 | 0.00088014 | -50.1205 | 69.136 | -53.7186 | 69.0216 | -52.7344 | -53.3936 | -52.8351 | -52.1622 | 69.2001 | -53.6179 | -53.215 | -53.3981 | -53.6362 | -53.3112 | -0.14648 | -0.054932 | -0.16937 | 0.83771 | 0.737 | 0.17853 | 0.88348 | 0.32501 | -0.045776 | 0.009155 | -122.406 | 0.17395 | 0.26093 | -0.064086 | 0.3067 | -0.01831 | 0.98419 | 122.7402 | 0.21973 | 0.40283 | 122.8546 | 122.818 | 122.7081 | 122.7722 | -122.9095 | -122.8088 | 122.5937 | 0.35706 | 3.4515 | 1.4099
3336.1719 | 123.0652 | -53.6087 | 69.1635 | -0.13687 | 0.00040806 | 0.062453 | 0.070754 | 0.0029374 | 0.00048269 | 0.0067036 | -0.056274 | 0.0015295 | 0.0021362 | 0.0051868 | -0.0027877 | -0.0042981 | 0.0023755 | -50.116 | 69.1681 | -53.7048 | 68.9621 | -52.8534 | -53.4805 | -52.9037 | -52.2171 | 69.2001 | -53.6407 | -53.2242 | -53.4256 | -53.6819 | -53.3569 | -0.09613 | 0.004578 | -0.20142 | 0.75531 | 0.70496 | 0.12817 | 0.80109 | 0.2243 | -0.032043 | 0.036621 | -122.3877 | 0.18311 | 0.25177 | -0.073242 | 0.28381 | -0.041199 | 0.85144 | 122.6669 | 0.21515 | 0.41656 | 122.8729 | 122.8409 | 122.7768 | 122.8088 | -122.8683 | -122.8043 | 122.5708 | 0.38452 | 3.4927 | 1.3916
3337.1719 | 123.024 | -53.5446 | 69.1544 | -0.068207 | 0.0010489 | 0.061385 | 0.070541 | 0.0010148 | 0.0039007 | 0.0047808 | -0.050171 | 0.00088875 | 0.00042723 | -0.00036738 | -0.0038559 | -0.0057935 | -0.0021107 | -50.0565 | 69.1681 | -53.6819 | 69.0353 | -52.7939 | -53.421 | -52.8351 | -52.1713 | 69.2093 | -53.6407 | -53.2059 | -53.3981 | -53.6407 | -53.2974 | -0.13733 | 0.013733 | -0.11902 | 0.75073 | 0.70953 | 0.1236 | 0.84686 | 0.26093 | -0.09613 | 0.054932 | -122.3602 | 0.14649 | 0.24719 | -0.09613 | 0.34332 | 0 | 0.88806 | 122.7173 | 0.24262 | 0.43487 | 122.85 | 122.85 | 122.7127 | 122.7539 | -122.8363 | -122.7951 | 122.58 | 0.33875 | 3.4882 | 1.3733
3338.1719 | 123.0515 | -53.5812 | 69.1498 | -0.083466 | 0.0014761 | 0.063094 | 0.0699 | 0.00080117 | 0.0026191 | 0.0060626 | -0.050171 | -0.00017945 | -0.00064077 | 0.002196 | -0.0019333 | -0.0051527 | 0.0040845 | -50.0885 | 69.1864 | -53.6774 | 68.9896 | -52.8351 | -53.4576 | -52.8763 | -52.1942 | 69.2047 | -53.6499 | -53.2196 | -53.3936 | -53.6499 | -53.3157 | -0.09613 | 0.036621 | -0.16022 | 0.74616 | 0.70496 | 0.1236 | 0.80109 | 0.21973 | -0.068664 | 0.054932 | -122.3694 | 0.18768 | 0.2655 | -0.068664 | 0.33417 | 0 | 0.84229 | 122.6669 | 0.25635 | 0.4303 | 122.8638 | 122.8546 | 122.7676 | 122.7859 | -122.8271 | -122.7997 | 122.5708 | 0.36163 | 3.4927 | 1.387
3339.1719 | 123.0103 | -53.595 | 69.191 | -0.11398 | -0.00087374 | 0.061385 | 0.068832 | -0.0021896 | 0.0026191 | 0.0086262 | -0.059326 | 0.0023839 | 0.00064083 | 0.0030506 | -0.0017197 | -0.0047253 | -0.00018806 | -50.1114 | 69.2093 | -53.7094 | 68.9438 | -52.8397 | -53.4805 | -52.8992 | -52.2171 | 69.2322 | -53.6591 | -53.2425 | -53.4256 | -53.6636 | -53.3386 | -0.11444 | 0.018311 | -0.24719 | 0.75531 | 0.6958 | 0.11444 | 0.81024 | 0.22888 | -0.064087 | 0.041199 | -122.4335 | 0.16937 | 0.25635 | -0.068664 | 0.32044 | -0.004577 | 0.86975 | 122.6532 | 0.23346 | 0.41656 | 122.9187 | 122.8912 | 122.8043 | 122.8271 | -122.9004 | -122.85 | 122.5388 | 0.35248 | 3.4836 | 1.3779
3340.1719 | 122.9736 | -53.5995 | 69.1956 | -0.12924 | 0.00062166 | 0.060103 | 0.069472 | 0.0012284 | 0.0026191 | 0.0056354 | -0.050171 | 0.0017431 | 0.00042723 | 0.0034778 | 0.00041649 | -0.0045117 | -0.00061526 | -50.0839 | 69.2276 | -53.6911 | 68.9438 | -52.8625 | -53.4897 | -52.9129 | -52.2583 | 69.2734 | -53.6362 | -53.2654 | -53.4714 | -53.7094 | -53.3707 | -0.091553 | 0.032043 | -0.25177 | 0.737 | 0.68664 | 0.10986 | 0.7782 | 0.20142 | -0.036621 | 0.077819 | -122.4609 | 0.12817 | 0.22888 | -0.10986 | 0.2655 | -0.073243 | 0.82855 | 122.6349 | 0.16479 | 0.37079 | 122.9187 | 122.9095 | 122.8271 | 122.8729 | -122.8867 | -122.8317 | 122.5433 | 0.33417 | 3.5156 | 1.3412
3341.1719 | 122.9233 | -53.5995 | 69.2093 | 0.008087 | -0.0019417 | 0.060316 | 0.070113 | 0.00037377 | 0.0024053 | 0.0052082 | -0.071533 | 0.0025975 | 0.00021363 | -0.00015378 | -0.0023605 | -0.0060071 | -0.00061526 | -50.116 | 69.2459 | -53.6774 | 68.9529 | -52.8854 | -53.4851 | -52.9266 | -52.2766 | 69.3054 | -53.6316 | -53.2974 | -53.476 | -53.7186 | -53.3752 | -0.07782 | 0.036621 | -0.25635 | 0.71411 | 0.67291 | 0.11444 | 0.75073 | 0.19226 | -0.032044 | 0.09613 | -122.5067 | 0.1236 | 0.2243 | -0.11902 | 0.25635 | -0.086975 | 0.79193 | 122.6303 | 0.15564 | 0.33417 | 122.9233 | 122.937 | 122.8455 | 122.905 | -122.8867 | -122.8409 | 122.5525 | 0.30212 | 3.4836 | 1.3229
3342.1719 | 122.9965 | -53.5767 | 69.1864 | -0.075836 | 0.0012625 | 0.059676 | 0.071822 | 0.001442 | 0.00069649 | 0.0062762 | -0.044067 | -0.00017945 | 0.00064083 | 0.0026232 | -0.0032151 | -0.0057935 | 0.0010937 | -50.0793 | 69.2413 | -53.6591 | 68.9713 | -52.858 | -53.4805 | -52.9083 | -52.2491 | 69.2413 | -53.6407 | -53.2425 | -53.4622 | -53.7003 | -53.3569 | -0.082398 | 0.054932 | -0.21515 | 0.71869 | 0.66833 | 0.09613 | 0.75073 | 0.17853 | -0.064087 | 0.054932 | -122.4289 | 0.11444 | 0.21973 | -0.1236 | 0.28381 | -0.059509 | 0.80109 | 122.6303 | 0.17853 | 0.39825 | 122.9004 | 122.8821 | 122.818 | 122.818 | -122.8455 | -122.8271 | 122.5479 | 0.33417 | 3.4973 | 1.3275
3343.1719 | 122.8775 | -53.6133 | 69.1727 | -0.11398 | 0.0010489 | 0.062666 | 0.068191 | 0.0010148 | 0.0058233 | 0.005849 | -0.06543 | -0.00060665 | 0.00085443 | 0.0051868 | 0.00063009 | -0.0045117 | 0.00023934 | -50.0931 | 69.2505 | -53.6774 | 68.9255 | -52.8946 | -53.4897 | -52.9312 | -52.3087 | 69.2688 | -53.6407 | -53.2791 | -53.4943 | -53.7186 | -53.3707 | -0.064087 | 0.07782 | -0.24719 | 0.71869 | 0.68207 | 0.1236 | 0.74616 | 0.18768 | -0.027466 | 0.096131 | -122.4518 | 0.11902 | 0.24261 | -0.10529 | 0.27008 | -0.07782 | 0.78278 | 122.6028 | 0.14648 | 0.36163 | 122.9279 | 122.9095 | 122.8638 | 122.8821 | -122.85 | -122.8134 | 122.5388 | 0.33417 | 3.5202 | 1.3046
3344.1719 | 122.9095 | -53.5904 | 69.2413 | -0.060578 | -0.0015145 | 0.059248 | 0.072463 | -0.0021896 | 0.0024053 | 0.0049946 | -0.053223 | 0.0021703 | 0.0032044 | -0.0016492 | -0.0019333 | -0.0051527 | -0.00018806 | -50.0473 | 69.2688 | -53.6591 | 68.9621 | -52.8534 | -53.4714 | -52.9129 | -52.2629 | 69.2963 | -53.6133 | -53.3066 | -53.4851 | -53.7094 | -53.3798 | -0.068665 | 0.027466 | -0.27924 | 0.737 | 0.67749 | 0.11902 | 0.74616 | 0.18768 | -0.022888 | 0.054932 | -122.5479 | 0.10529 | 0.21057 | -0.11902 | 0.23346 | -0.096131 | 0.80566 | 122.6212 | 0.12817 | 0.3067 | 122.9279 | 122.9095 | 122.8592 | 122.8867 | -122.9004 | -122.8546 | 122.5525 | 0.28381 | 3.5431 | 1.3275
3345.1719 | 122.905 | -53.6316 | 69.2413 | -0.052948 | 0.00062166 | 0.062025 | 0.071395 | 0.00016017 | 0.0021917 | 0.00414 | -0.056274 | 0.0013159 | 0.0019226 | -0.00015378 | -0.0030013 | -0.0028027 | -0.00061526 | -50.0519 | 69.2688 | -53.6819 | 68.9438 | -52.8809 | -53.5034 | -52.9449 | -52.3087 | 69.2871 | -53.6316 | -53.302 | -53.421 | -54.0436 | -53.5721 | -0.050354 | 0.027466 | -0.29755 | 0.75073 | 0.68665 | 0.12817 | 0.737 | 0.17853 | 0 | 0.045776 | -122.5433 | 0.21057 | 0.059509 | -0.41199 | 0.059509 | -0.41199 | 0.80109 | 122.6257 | 0.21057 | 0.32959 | 122.9507 | 122.9187 | 122.9004 | 122.9187 | -122.9233 | -122.8729 | 122.5754 | 0.32959 | 3.5797 | 1.3229
3346.1719 | 122.905 | -53.5767 | 69.2596 | -0.068207 | 0.00083526 | 0.062025 | 0.070113 | 0.00016017 | 0.0019781 | 0.0067036 | -0.034912 | 0.0017431 | 0.0012818 | 0.0026232 | -0.0019333 | -0.0053663 | 0.00066654 | -50.0381 | 69.2459 | -53.6545 | 68.9575 | -52.8534 | -53.4714 | -52.9037 | -52.2675 | 69.3054 | -53.595 | -53.2883 | -53.4897 | -53.714 | -53.3844 | -0.07782 | -0.013733 | -0.30212 | 0.72327 | 0.67291 | 0.10528 | 0.75073 | 0.1831 | -0.018311 | 0.045776 | -122.5479 | 0.086975 | 0.19226 | -0.13733 | 0.21057 | -0.11902 | 0.80109 | 122.612 | 0.10529 | 0.3067 | 122.9004 | 122.9004 | 122.8226 | 122.8821 | -122.9141 | -122.8546 | 122.5342 | 0.28839 | 3.5385 | 1.3092
3347.1719 | 122.9233 | -53.5675 | 69.2688 | -0.098725 | -0.00023294 | 0.061171 | 0.071395 | -0.0038986 | 0.0036871 | 0.0062762 | -0.010498 | 0.00088875 | 0.0036316 | -0.003999 | 0.00063009 | -0.0042981 | 0.0019483 | -50.0107 | 69.2688 | -53.6591 | 68.9941 | -52.8214 | -53.4302 | -52.8671 | -52.2034 | 69.2963 | -53.5858 | -53.2562 | -53.4622 | -53.6819 | -53.3661 | -0.091553 | 0 | -0.27466 | 0.74615 | 0.70038 | 0.13733 | 0.79193 | 0.22888 | -0.01831 | 0.027466 | -122.525 | 0.10529 | 0.20142 | -0.11444 | 0.21973 | -0.096131 | 0.83771 | 122.6532 | 0.1236 | 0.32959 | 122.9279 | 122.8821 | 122.8363 | 122.8638 | -122.9279 | -122.8546 | 122.5616 | 0.31128 | 3.5568 | 1.3641
3348.1719 | 122.9004 | -53.5583 | 69.278 | -0.091095 | -1.9142e-05 | 0.063734 | 0.069045 | -5.343e-05 | 0.0034735 | 0.0047808 | -0.044067 | 0.0015295 | -0.00042717 | -0.0037854 | -0.0036423 | -0.0066479 | 0.00066654 | -50.0336 | 69.2871 | -53.6362 | 68.9621 | -52.8625 | -53.476 | -52.9083 | -52.2537 | 69.3146 | -53.5995 | -53.302 | -53.4897 | -53.7231 | -53.3844 | -0.077819 | 0.009155 | -0.31586 | 0.6958 | 0.65002 | 0.082398 | 0.72784 | 0.16022 | -0.041198 | 0.036621 | -122.58 | 0.068665 | 0.17395 | -0.1648 | 0.21515 | -0.1236 | 0.77362 | 122.5983 | 0.10986 | 0.29755 | 122.9233 | 122.9141 | 122.8455 | 122.8729 | -122.9141 | -122.8775 | 122.5204 | 0.25635 | 3.5248 | 1.3046
3349.1719 | 122.9004 | -53.5583 | 69.2688 | -0.083466 | -0.00066014 | 0.061812 | 0.071609 | -0.0021896 | 0.0030463 | 0.0049946 | -0.03186 | 0.0019567 | -0.0012818 | 0.0045458 | 0.00084389 | -0.0032301 | 0.00088014 | -49.9878 | 69.278 | -53.6362 | 68.9941 | -52.8076 | -53.4256 | -52.8717 | -52.2125 | 69.3283 | -53.5904 | -53.2562 | -53.4851 | -53.6865 | -53.3707 | -0.077819 | 0.009155 | -0.27466 | 0.75073 | 0.68665 | 0.13275 | 0.76447 | 0.21057 | -0.032043 | 0.059509 | -122.525 | 0.073243 | 0.18768 | -0.12817 | 0.21973 | -0.09613 | 0.82855 | 122.6303 | 0.10529 | 0.33417 | 122.9141 | 122.9187 | 122.8363 | 122.8867 | -122.905 | -122.8592 | 122.5525 | 0.30212 | 3.5706 | 1.3458
3350.1719 | 122.9828 | -53.5217 | 69.2734 | -0.03006 | -1.9142e-05 | 0.061171 | 0.069686 | 0.0029374 | 0.0024053 | 0.0047808 | 0.0047608 | 0.0025975 | 0.00085443 | 0.0017688 | -0.0012925 | -0.0030163 | 0.00045294 | -49.942 | 69.2917 | -53.5995 | 69.0582 | -52.7344 | -53.3936 | -52.8259 | -52.1347 | 69.3146 | -53.5263 | -53.2059 | -53.3936 | -53.6224 | -53.3157 | -0.077819 | 0.018311 | -0.21515 | 0.78735 | 0.6958 | 0.12817 | 0.77362 | 0.20599 | -0.004577 | 0.041199 | -122.4792 | 0.12817 | 0.20599 | -0.10071 | 0.21057 | -0.096131 | 0.86517 | 122.6578 | 0.13275 | 0.32043 | 122.8912 | 122.8409 | 122.8134 | 122.8363 | -122.8729 | -122.7997 | 122.58 | 0.31586 | 3.5797 | 1.387
3351.1719 | 122.9645 | -53.5172 | 69.2963 | -0.083466 | 0.0014761 | 0.062025 | 0.069472 | -5.343e-05 | 0.0036871 | 0.0062762 | 0.016968 | 0.0017431 | 0.00042723 | -0.00079478 | -0.0030013 | -0.0047253 | 0.00023934 | -49.9374 | 69.3146 | -53.6224 | 69.0491 | -52.739 | -53.3615 | -52.8122 | -52.1164 | 69.3329 | -53.5446 | -53.1784 | -53.3661 | -53.6224 | -53.3112 | -0.10529 | 0.01831 | -0.24719 | 0.7782 | 0.70496 | 0.15564 | 0.81024 | 0.26093 | -0.027466 | 0.036621 | -122.4747 | 0.15106 | 0.20599 | -0.10529 | 0.23346 | -0.07782 | 0.88348 | 122.6715 | 0.17853 | 0.36621 | 122.937 | 122.8775 | 122.8317 | 122.85 | -122.9187 | -122.8409 | 122.5662 | 0.33874 | 3.5797 | 1.4008
3352.1719 | 122.9645 | -53.5217 | 69.3237 | -0.068207 | -0.00023294 | 0.062239 | 0.069045 | 0.0010148 | 0.00026909 | 0.0067036 | -0.019653 | 0.0019567 | 0.0025634 | 0.010527 | -0.0021469 | -0.0055799 | -0.00018806 | -49.9008 | 69.3283 | -53.5767 | 69.072 | -52.7161 | -53.3432 | -52.7802 | -52.1164 | 69.3741 | -53.5217 | -53.1738 | -53.3707 | -53.5904 | -53.2837 | -0.054931 | 0.004578 | -0.25177 | 0.80566 | 0.74158 | 0.17853 | 0.79651 | 0.23346 | 0 | 0.050354 | -122.4976 | 0.15106 | 0.23804 | -0.068664 | 0.23804 | -0.068664 | 0.8606 | 122.6486 | 0.15106 | 0.3479 | 122.905 | 122.8958 | 122.85 | 122.8958 | -122.9004 | -122.8455 | 122.5937 | 0.3479 | 3.6209 | 1.4053
3353.1719 | 122.9828 | -53.4897 | 69.3283 | -0.075836 | 0.00040806 | 0.061598 | 0.068832 | 0.00058737 | 0.0028327 | 0.0077716 | -0.01355 | 0.00088875 | 0.0012818 | -0.00015378 | -0.0019333 | -0.0038709 | 0.0013073 | -49.9191 | 69.3192 | -53.5767 | 68.9896 | -52.8076 | -53.2013 | -52.7481 | -52.0889 | 69.3832 | -53.5309 | -53.1555 | -53.3569 | -53.5812 | -53.27 | -0.086975 | -0.009155 | -0.33875 | 0.68207 | 0.74158 | 0.28839 | 0.82855 | 0.37537 | -0.041199 | 0.054932 | -122.4838 | 0.13275 | 0.21973 | -0.091553 | 0.26093 | -0.050354 | 0.76904 | 122.5662 | 0.17395 | 0.37537 | 122.8958 | 122.9141 | 122.8088 | 122.8729 | -122.905 | -122.8592 | 122.4792 | 0.33417 | 3.5706 | 1.4008
3354.1719 | 122.9828 | -53.4805 | 69.342 | -0.052948 | -0.00023294 | 0.064375 | 0.068191 | 0.00058737 | 0.0019781 | 0.00414 | -0.0074462 | 0.0025975 | 0.0025634 | 0.0013416 | -0.00022431 | -0.0040845 | 2.554e-05 | -49.8917 | 69.3329 | -53.5675 | 69.0811 | -52.6932 | -53.3157 | -52.7618 | -52.0752 | 69.3558 | -53.5172 | -53.1097 | -53.3249 | -53.5538 | -53.2288 | -0.086975 | -0.009155 | -0.26093 | 0.78735 | 0.71869 | 0.1648 | 0.80566 | 0.25177 | -0.036621 | 0.013733 | -122.4518 | 0.15564 | 0.25177 | -0.073242 | 0.28839 | -0.036621 | 0.87433 | 122.6486 | 0.19226 | 0.40741 | 122.9004 | 122.8729 | 122.8134 | 122.8363 | -122.9095 | -122.8592 | 122.5616 | 0.37079 | 3.5889 | 1.4053
3355.1719 | 122.9416 | -53.4805 | 69.342 | -0.052948 | -0.00023294 | 0.060744 | 0.068618 | 0.00080117 | 0.0034735 | 0.0034992 | 0.010864 | 0.0011023 | 0.0012818 | -0.0031446 | -0.0030013 | -0.0034437 | 0.0019483 | -49.8917 | 69.3558 | -53.5263 | 69.0903 | -52.7023 | -53.3157 | -52.771 | -52.0798 | 69.3558 | -53.5126 | -53.1647 | -53.3432 | -53.595 | -53.2516 | -0.045776 | 0.013733 | -0.25177 | 0.7782 | 0.70953 | 0.1648 | 0.75531 | 0.21057 | -0.032043 | 0.013733 | -122.5067 | 0.13733 | 0.22888 | -0.11444 | 0.26093 | -0.082398 | 0.82397 | 122.6166 | 0.16937 | 0.3479 | 122.8821 | 122.8683 | 122.8363 | 122.8363 | -122.8683 | -122.8546 | 122.5708 | 0.31586 | 3.5889 | 1.4008
3356.1719 | 122.9736 | -53.4485 | 69.3375 | -0.060578 | 0.0016899 | 0.06288 | 0.069259 | -5.343e-05 | 0.00026909 | 0.0062762 | -0.0043946 | 0.0025975 | 0.001068 | 0.00070062 | -0.00065151 | -0.0036573 | -0.00040166 | -49.8825 | 69.3604 | -53.5492 | 68.9987 | -52.7893 | -53.1784 | -52.739 | -52.0477 | 69.4061 | -53.4897 | -53.1509 | -53.3295 | -53.5583 | -53.2471 | -0.10071 | 0.022889 | -0.33875 | 0.65918 | 0.70953 | 0.27008 | 0.81024 | 0.37079 | -0.041199 | 0.068665 | -122.4884 | 0.11902 | 0.20142 | -0.10986 | 0.24262 | -0.068665 | 0.75989 | 122.5479 | 0.16022 | 0.33875 | 122.9095 | 122.8958 | 122.8088 | 122.8546 | -122.8867 | -122.8271 | 122.4472 | 0.29755 | 3.566 | 1.4008
3357.1719 | 122.9828 | -53.4576 | 69.3512 | -0.060578 | -0.0019417 | 0.060744 | 0.068832 | 0.0010148 | 0.0011237 | 0.0069172 | 0.0078126 | -0.00082025 | 0.001709 | -0.007417 | -0.00043791 | -0.0045117 | 0.0028027 | -49.9146 | 69.3695 | -53.5583 | 69.0948 | -52.7115 | -53.2883 | -52.739 | -52.0981 | 69.4244 | -53.4988 | -53.1555 | -53.3112 | -53.5355 | -53.2288 | -0.10071 | 0.018311 | -0.25635 | 0.74616 | 0.71869 | 0.16937 | 0.8194 | 0.27008 | -0.041198 | 0.073242 | -122.5067 | 0.14648 | 0.22888 | -0.077819 | 0.27008 | -0.036621 | 0.84686 | 122.6532 | 0.18768 | 0.34332 | 122.9279 | 122.9233 | 122.8271 | 122.8821 | -122.9095 | -122.85 | 122.5525 | 0.30212 | 3.5431 | 1.3596
3358.1719 | 122.9965 | -53.4622 | 69.3787 | -0.060578 | -0.00066014 | 0.061812 | 0.070754 | -0.00069423 | 0.0032599 | 0.00414 | 0.016968 | 0.0021703 | 0.0021362 | 0.0060412 | -0.0044967 | -0.0030163 | -0.0010425 | -49.8917 | 69.3787 | -53.5446 | 69.0857 | -52.7344 | -53.3157 | -52.7573 | -52.1118 | 69.4153 | -53.4897 | -53.1601 | -53.3203 | -53.5538 | -53.2516 | -0.082398 | 0 | -0.29297 | 0.72784 | 0.70496 | 0.14648 | 0.78735 | 0.22888 | -0.027466 | 0.036621 | -122.5388 | 0.14191 | 0.21057 | -0.091553 | 0.23804 | -0.064087 | 0.81024 | 122.6303 | 0.16937 | 0.32959 | 122.9233 | 122.905 | 122.8409 | 122.8775 | -122.9233 | -122.8683 | 122.5479 | 0.30212 | 3.5706 | 1.3504
3359.1719 | 122.9782 | -53.4531 | 69.3787 | -0.045319 | -0.0015145 | 0.061812 | 0.070754 | -0.003685 | 0.0028327 | 0.0039264 | -0.0013428 | -0.00039305 | 0.0025634 | 0.001128 | -0.0032151 | -0.0045117 | 0.0032299 | -49.855 | 69.3878 | -53.5583 | 69.1177 | -52.6932 | -53.27 | -52.7344 | -52.0523 | 69.3924 | -53.4943 | -53.1326 | -53.2974 | -53.5263 | -53.2333 | -0.10529 | 0.009155 | -0.26093 | 0.75989 | 0.71869 | 0.18311 | 0.82397 | 0.28839 | -0.041199 | 0.013733 | -122.5113 | 0.15564 | 0.21973 | -0.073242 | 0.26093 | -0.032043 | 0.86517 | 122.6761 | 0.19684 | 0.36163 | 122.9462 | 122.8867 | 122.8409 | 122.8455 | -122.937 | -122.8729 | 122.5708 | 0.32043 | 3.598 | 1.4008
3360.1719 | 122.9691 | -53.4439 | 69.3695 | 0.015716 | -0.00023294 | 0.06288 | 0.069045 | 0.0046464 | 0.0032599 | 0.0049946 | 0.010864 | 0.00088875 | 0.00085443 | -0.0033582 | -0.0032151 | -0.0045117 | -0.0010425 | -49.8779 | 69.3741 | -53.5492 | 69.1177 | -52.7023 | -53.2883 | -52.7435 | -52.066 | 69.4107 | -53.4805 | -53.1326 | -53.3112 | -53.54 | -53.2104 | -0.10529 | 0.004577 | -0.25177 | 0.74158 | 0.70038 | 0.15564 | 0.80566 | 0.26093 | -0.036621 | 0.041199 | -122.5021 | 0.13275 | 0.23346 | -0.09613 | 0.27008 | -0.059509 | 0.84686 | 122.6669 | 0.16937 | 0.3479 | 122.9233 | 122.8912 | 122.818 | 122.8546 | -122.9187 | -122.85 | 122.5616 | 0.31128 | 3.566 | 1.3779
3361.1719 | 122.9507 | -53.4393 | 69.3741 | -0.068207 | -1.9142e-05 | 0.063307 | 0.067763 | 0.00016017 | 0.0015509 | 0.0060626 | 0.010864 | 3.4148e-05 | 0.0040588 | -0.0010084 | -0.0012925 | -0.0051527 | -0.0014697 | -49.8688 | 69.4016 | -53.5217 | 69.1086 | -52.6978 | -53.2883 | -52.739 | -52.0706 | 69.429 | -53.5034 | -53.1555 | -53.2883 | -53.5172 | -53.215 | -0.082398 | 0.027466 | -0.2655 | 0.74158 | 0.70038 | 0.15106 | 0.78278 | 0.23346 | -0.064087 | 0.054932 | -122.5296 | 0.15106 | 0.2243 | -0.07782 | 0.28839 | -0.013733 | 0.82397 | 122.6303 | 0.21515 | 0.3479 | 122.9233 | 122.9324 | 122.8409 | 122.8683 | -122.8958 | -122.8775 | 122.5479 | 0.28381 | 3.5706 | 1.3687
3362.1719 | 122.9736 | -53.4439 | 69.3878 | -0.091095 | 0.0012625 | 0.062453 | 0.0699 | 0.001442 | 0.0030463 | 0.0073444 | 0.0078126 | 0.0021703 | 0.0019226 | -0.0016492 | -0.0027877 | -0.0042981 | 0.0013073 | -49.8276 | 69.397 | -53.5309 | 69.1452 | -52.652 | -53.2837 | -52.7252 | -52.0432 | 69.4061 | -53.4668 | -53.1235 | -53.3066 | -53.5172 | -53.1967 | -0.086975 | 0.009156 | -0.24261 | 0.79193 | 0.71869 | 0.16022 | 0.80566 | 0.24719 | -0.022888 | 0.018311 | -122.5113 | 0.13733 | 0.24719 | -0.073242 | 0.27008 | -0.050354 | 0.87891 | 122.6761 | 0.16022 | 0.34332 | 122.9279 | 122.8729 | 122.8409 | 122.85 | -122.9187 | -122.8546 | 122.5891 | 0.32043 | 3.6163 | 1.4008
3363.1719 | 122.9553 | -53.4576 | 69.3787 | -0.045319 | -0.00023294 | 0.061812 | 0.069686 | -0.00069423 | 0.0013373 | 0.00414 | -0.010498 | 0.00088875 | 0.0029906 | -0.0042126 | -0.0036423 | -0.0049389 | 0.00088014 | -49.8184 | 69.3924 | -53.508 | 69.1315 | -52.6611 | -53.2562 | -52.7206 | -52.0203 | 69.4016 | -53.4531 | -53.1326 | -53.2928 | -53.5034 | -53.2059 | -0.050354 | 0.013733 | -0.24719 | 0.79651 | 0.737 | 0.20142 | 0.78735 | 0.25177 | 0.004578 | 0.022888 | -122.5113 | 0.16479 | 0.25177 | -0.045776 | 0.24719 | -0.050354 | 0.84686 | 122.6395 | 0.16022 | 0.32043 | 122.9004 | 122.8546 | 122.85 | 122.8592 | -122.8867 | -122.8317 | 122.5891 | 0.32501 | 3.6392 | 1.4374
3364.1719 | 122.9599 | -53.4256 | 69.4199 | -0.075836 | 0.00062166 | 0.061385 | 0.068832 | 0.00016017 | 0.0028327 | 0.0045672 | 0.023071 | 0.0013159 | 0.0014954 | 0.0026232 | -0.0019333 | -0.0047253 | 0.00023934 | -49.8505 | 69.429 | -53.5217 | 69.104 | -52.6932 | -53.2883 | -52.7252 | -52.0935 | 69.4427 | -53.4622 | -53.1555 | -53.2974 | -53.5355 | -53.2196 | -0.096131 | 0.009155 | -0.31586 | 0.73242 | 0.70038 | 0.13733 | 0.79651 | 0.23346 | -0.036621 | 0.022888 | -122.5754 | 0.12817 | 0.20599 | -0.10986 | 0.24262 | -0.073242 | 0.82855 | 122.6257 | 0.16479 | 0.3067 | 122.9507 | 122.905 | 122.8546 | 122.8683 | -122.9416 | -122.8821 | 122.5296 | 0.27008 | 3.5751 | 1.3321
3365.1719 | 122.937 | -53.4073 | 69.429 | -0.03006 | -1.9142e-05 | 0.062239 | 0.067336 | -0.00026703 | 0.0036871 | 0.0034992 | 0.041382 | 0.00088875 | 0.0014954 | -0.003999 | -0.0040695 | -0.0070753 | -0.0021107 | -49.8734 | 69.3878 | -53.5172 | 69.1269 | -52.7023 | -53.2928 | -52.7252 | -52.0981 | 69.4519 | -53.476 | -53.1418 | -53.2883 | -53.5309 | -53.2104 | -0.10986 | -0.041199 | -0.30212 | 0.70496 | 0.68207 | 0.11444 | 0.79193 | 0.2243 | -0.068664 | 0.022888 | -122.5708 | 0.11902 | 0.19684 | -0.1236 | 0.2655 | -0.054932 | 0.81482 | 122.644 | 0.18768 | 0.33417 | 122.905 | 122.9279 | 122.7951 | 122.8592 | -122.9462 | -122.905 | 122.5342 | 0.2655 | 3.5339 | 1.3092
3366.1719 | 122.9828 | -53.4302 | 69.4107 | -0.045319 | 0.00083526 | 0.060316 | 0.068618 | 0.0037918 | -0.00058531 | 0.0045672 | 0.010864 | -0.00039305 | 0.0012818 | -0.0072034 | -0.0025741 | -0.0072889 | 0.0023755 | -49.8184 | 69.4336 | -53.4851 | 69.1498 | -52.6611 | -53.2471 | -52.7069 | -52.0477 | 69.4382 | -53.4256 | -53.1052 | -53.2745 | -53.508 | -53.1967 | -0.054931 | 0.022888 | -0.26093 | 0.76904 | 0.72327 | 0.18311 | 0.7782 | 0.23804 | 0.004578 | 0.027465 | -122.5159 | 0.15564 | 0.23346 | -0.07782 | 0.22888 | -0.082398 | 0.82397 | 122.6349 | 0.15106 | 0.32043 | 122.9187 | 122.8638 | 122.8638 | 122.8683 | -122.8958 | -122.8363 | 122.58 | 0.32501 | 3.6118 | 1.3824
3367.1719 | 122.9507 | -53.4393 | 69.429 | -0.075836 | 0.0019035 | 0.060744 | 0.070541 | -0.0017624 | -0.00015811 | 0.0026446 | -0.0043946 | 0.00067495 | 0.00021363 | 0.0051868 | -0.0010787 | -0.0075025 | 0.0028027 | -49.7818 | 69.4107 | -53.476 | 69.1544 | -52.6291 | -53.2608 | -52.7115 | -52.0157 | 69.4427 | -53.4393 | -52.9907 | -53.421 | -53.5309 | -53.1464 | -0.036621 | -0.01831 | -0.27466 | 0.81024 | 0.72784 | 0.17853 | 0.76447 | 0.21515 | 0 | 0.013733 | -122.4197 | 0.01831 | 0.29297 | -0.091553 | 0.29297 | -0.091553 | 0.84686 | 122.6303 | 0.01831 | 0.44861 | 122.8867 | 122.8821 | 122.85 | 122.8821 | -122.905 | -122.8683 | 122.5937 | 0.44861 | 3.6575 | 1.4236
3368.1719 | 122.9782 | -53.4027 | 69.4244 | -0.03006 | 0.00083526 | 0.061812 | 0.070541 | 0.0033646 | 0.0011237 | 0.0043536 | -0.03186 | 0.0028113 | 0.00085443 | 0.0047594 | -0.0027877 | -0.0049389 | -0.0027515 | -49.7818 | 69.4153 | -53.5263 | 69.1772 | -52.6199 | -53.2608 | -52.7023 | -52.0065 | 69.4382 | -53.4348 | -53.1509 | -53.2516 | -53.4348 | -53.1921 | -0.1236 | -0.009155 | -0.24719 | 0.78278 | 0.70038 | 0.14191 | 0.82397 | 0.2655 | -0.032043 | 0.013733 | -122.5754 | 0.15106 | 0.21057 | -0.032043 | 0.24261 | 0 | 0.90637 | 122.7036 | 0.1831 | 0.28381 | 122.9416 | 122.8729 | 122.818 | 122.8409 | -122.9507 | -122.8592 | 122.58 | 0.25177 | 3.6209 | 1.3962
3369.1719 | 123.0194 | -53.3752 | 69.3787 | -0.091095 | 0.00040806 | 0.061385 | 0.067763 | 0.0018692 | 0.0021917 | 0.0052082 | 0.074951 | -0.00082025 | 0.001709 | -0.005708 | -0.0010787 | -0.0068615 | 0.0028027 | -49.823 | 69.3558 | -53.476 | 69.1727 | -52.6154 | -53.2516 | -52.6611 | -52.0065 | 69.397 | -53.4348 | -53.0823 | -53.2471 | -53.4531 | -53.1509 | -0.10071 | -0.022888 | -0.20599 | 0.75989 | 0.71411 | 0.1236 | 0.81482 | 0.2243 | -0.059509 | 0.018311 | -122.4609 | 0.12817 | 0.2243 | -0.07782 | 0.28381 | -0.018311 | 0.8606 | 122.6486 | 0.18768 | 0.35248 | 122.8317 | 122.8317 | 122.731 | 122.7722 | -122.8546 | -122.8134 | 122.5479 | 0.29297 | 3.5522 | 1.3687
3370.1719 | 122.9691 | -53.3844 | 69.4473 | -0.075836 | -0.00044654 | 0.061812 | 0.071822 | 0.0061416 | 0.00091009 | 0.005849 | -0.0074462 | 0.00024775 | 0.0019226 | 0.0049732 | -0.0023605 | -0.0060071 | 0.0034435 | -49.7818 | 69.4061 | -53.4805 | 69.1956 | -52.6291 | -53.2471 | -52.6932 | -51.9699 | 69.429 | -53.4302 | -53.0594 | -53.2333 | -53.4531 | -53.1418 | -0.096131 | -0.041199 | -0.25177 | 0.75531 | 0.69122 | 0.13733 | 0.78735 | 0.23346 | -0.045777 | -0.018311 | -122.5067 | 0.15106 | 0.24261 | -0.068665 | 0.28839 | -0.022888 | 0.85144 | 122.6761 | 0.19684 | 0.37079 | 122.8867 | 122.8592 | 122.7905 | 122.8134 | -122.9279 | -122.8775 | 122.58 | 0.32501 | 3.6026 | 1.4145
3371.1719 | 122.9736 | -53.3844 | 69.4382 | 0.015716 | -1.9142e-05 | 0.059889 | 0.069472 | -0.0015488 | 0.0011237 | 0.0028582 | 0.0047608 | 0.0015295 | 0.0023498 | 0.0034778 | -0.0032151 | -0.0070753 | 0.0015209 | -49.7818 | 69.4519 | -53.4714 | 69.1956 | -52.6291 | -53.2242 | -52.6886 | -52.002 | 69.4702 | -53.4302 | -53.064 | -53.2333 | -53.4943 | -53.1692 | -0.086976 | 0.013733 | -0.24261 | 0.75531 | 0.6958 | 0.16022 | 0.78278 | 0.24719 | -0.045777 | 0.032044 | -122.5021 | 0.15106 | 0.21515 | -0.10986 | 0.26093 | -0.064087 | 0.84229 | 122.6669 | 0.19684 | 0.36621 | 122.9233 | 122.9004 | 122.8363 | 122.8546 | -122.9095 | -122.8683 | 122.58 | 0.32043 | 3.6026 | 1.3824
3372.1719 | 123.0103 | -53.3798 | 69.4656 | -0.060578 | 0.00019446 | 0.060103 | 0.067977 | -0.0013352 | 0.0019781 | 0.0049946 | 0.023071 | 0.0019567 | 2.8e-08 | 0.001128 | -0.0012925 | -0.0025891 | 0.00023934 | -49.7589 | 69.4382 | -53.476 | 69.1864 | -52.6245 | -53.215 | -52.6657 | -51.9836 | 69.4931 | -53.4164 | -53.0548 | -53.2196 | -53.4576 | -53.1647 | -0.09613 | -0.027466 | -0.27924 | 0.75531 | 0.71411 | 0.16479 | 0.81024 | 0.26093 | -0.036621 | 0.027466 | -122.5204 | 0.16022 | 0.21515 | -0.07782 | 0.25177 | -0.041199 | 0.85144 | 122.6624 | 0.19684 | 0.36163 | 122.9141 | 122.9095 | 122.818 | 122.8729 | -122.9416 | -122.8821 | 122.5662 | 0.32501 | 3.6209 | 1.3962
3373.1719 | 122.9599 | -53.4027 | 69.429 | -0.045319 | 0.00062166 | 0.061385 | 0.069259 | 0.0020828 | 0.0024053 | 0.0047808 | 0.035278 | 0.0011023 | 0.0021362 | 0.0045458 | -0.0010787 | -0.0049389 | -0.00082886 | -49.7589 | 69.4199 | -53.476 | 69.191 | -52.5787 | -53.2883 | -52.7939 | -51.9699 | 69.4702 | -53.4119 | -53.0319 | -53.2333 | -53.4576 | -53.1555 | -0.073242 | -0.009155 | -0.23804 | 0.82397 | 0.60883 | 0.11444 | 0.68207 | 0.18768 | -0.009155 | 0.041199 | -122.4609 | 0.16937 | 0.24719 | -0.054932 | 0.25635 | -0.045777 | 0.89722 | 122.6669 | 0.17853 | 0.37994 | 122.8958 | 122.8821 | 122.8226 | 122.8729 | -122.905 | -122.8409 | 122.5937 | 0.37079 | 3.6438 | 1.4328
3374.1719 | 123.0011 | -53.3798 | 69.3787 | -0.16739 | -0.00066014 | 0.062025 | 0.070113 | -0.0017624 | 0.0017645 | 0.0037128 | 0.056641 | 0.00024775 | 0.0023498 | -0.003999 | 0.00063009 | -0.0045117 | 0.0013073 | -49.7864 | 69.3878 | -53.4622 | 69.2139 | -52.5787 | -53.2288 | -52.6428 | -51.9424 | 69.4061 | -53.4164 | -53.0457 | -53.2196 | -53.4348 | -53.1418 | -0.082397 | 0.009155 | -0.1648 | 0.80109 | 0.737 | 0.15106 | 0.8194 | 0.23346 | -0.036621 | 0.027466 | -122.4243 | 0.16022 | 0.23804 | -0.054931 | 0.27466 | -0.01831 | 0.88348 | 122.6761 | 0.19684 | 0.37079 | 122.85 | 122.8226 | 122.7676 | 122.7859 | -122.8409 | -122.7951 | 122.5937 | 0.33417 | 3.5934 | 1.4374
3375.1719 | 122.9736 | -53.3798 | 69.4427 | -0.037689 | -0.00044654 | 0.062239 | 0.070113 | 0.001442 | 0.0017645 | 0.0054218 | -0.0043946 | 0.0013159 | 0.0021362 | 0.0026232 | -0.0015061 | -0.0038709 | -0.0012561 | -49.7498 | 69.4382 | -53.4714 | 69.2001 | -52.4734 | -53.2013 | -52.6337 | -51.9653 | 69.4839 | -53.3981 | -53.0457 | -53.2333 | -53.4576 | -53.1509 | -0.091553 | -0.004578 | -0.24262 | 0.90637 | 0.74615 | 0.17853 | 0.83771 | 0.27008 | -0.01831 | 0.041199 | -122.4884 | 0.14648 | 0.22888 | -0.07782 | 0.24719 | -0.05951 | 0.99793 | 122.6715 | 0.16479 | 0.35248 | 122.9095 | 122.8821 | 122.818 | 122.8638 | -122.9141 | -122.8409 | 122.58 | 0.33417 | 3.6301 | 1.4145
3376.1719 | 122.937 | -53.4027 | 69.4382 | -0.13687 | -0.0010873 | 0.062666 | 0.069686 | 0.0037918 | -0.0010125 | 0.0071308 | -0.041016 | 0.0013159 | 0.0021362 | 0.002196 | -0.0034287 | -0.0053663 | 0.0021619 | -49.7498 | 69.4519 | -53.4576 | 69.1727 | -52.6199 | -53.2516 | -52.6978 | -52.0111 | 69.4611 | -53.4119 | -53.0731 | -53.2516 | -53.4988 | -53.183 | -0.054932 | 0.013733 | -0.2655 | 0.78278 | 0.70496 | 0.15106 | 0.75989 | 0.20599 | -0.009155 | 0.022889 | -122.5113 | 0.15106 | 0.21973 | -0.09613 | 0.22888 | -0.086975 | 0.83771 | 122.6303 | 0.16022 | 0.33874 | 122.9095 | 122.8729 | 122.8546 | 122.8638 | -122.8958 | -122.85 | 122.5754 | 0.32959 | 3.653 | 1.3916
3377.1719 | 122.9553 | -53.389 | 69.429 | -0.11398 | 0.00040806 | 0.063094 | 0.067977 | 0.00080117 | 0.0026191 | 0.0062762 | -0.028809 | 0.0011023 | 0.00085443 | -0.00058098 | -0.0019333 | -0.0038709 | 0.00088014 | -49.7452 | 69.4382 | -53.4668 | 69.1589 | -52.6108 | -53.2562 | -52.6932 | -51.9928 | 69.4885 | -53.3981 | -53.0685 | -53.27 | -53.5034 | -53.1876 | -0.07782 | 0.009155 | -0.27008 | 0.7782 | 0.6958 | 0.13275 | 0.77362 | 0.21057 | -0.009155 | 0.059509 | -122.4976 | 0.11902 | 0.20142 | -0.11444 | 0.21057 | -0.10529 | 0.85602 | 122.6257 | 0.12817 | 0.32959 | 122.905 | 122.8867 | 122.8271 | 122.8775 | -122.8958 | -122.8271 | 122.5479 | 0.32043 | 3.6438 | 1.3962
3378.1719 | 122.9691 | -53.3707 | 69.4565 | -0.083466 | 0.00019446 | 0.062025 | 0.070113 | 0.0022964 | 0.00091009 | 0.0056354 | -0.025757 | 0.00046135 | 0.00042723 | -0.003999 | -0.0023605 | -0.0042981 | 0.0015209 | -49.7223 | 69.4473 | -53.4439 | 69.2368 | -52.5604 | -53.1692 | -52.6474 | -51.9012 | 69.4977 | -53.3844 | -53.0273 | -53.2242 | -53.4531 | -53.1326 | -0.073242 | -0.009155 | -0.21973 | 0.81024 | 0.72327 | 0.20142 | 0.79651 | 0.27466 | -0.013732 | 0.041199 | -122.4838 | 0.14648 | 0.23804 | -0.082397 | 0.25177 | -0.068665 | 0.88348 | 122.6807 | 0.16022 | 0.35706 | 122.8912 | 122.8821 | 122.818 | 122.8683 | -122.9004 | -122.8409 | 122.6074 | 0.34332 | 3.6484 | 1.4694
3379.1719 | 122.9645 | -53.3661 | 69.4748 | -0.037689 | -0.0017281 | 0.061812 | 0.068191 | 0.0022964 | 0.00026909 | 0.0049946 | -0.0074462 | -0.00017945 | 0.0012818 | -0.0010084 | -0.00065151 | -0.0057935 | -0.00040166 | -49.7177 | 69.4565 | -53.4439 | 69.2963 | -52.5467 | -53.1876 | -52.6474 | -51.9012 | 69.5068 | -53.4027 | -53.0182 | -53.215 | -53.4622 | -53.1418 | -0.07782 | -0.01831 | -0.17853 | 0.8194 | 0.71869 | 0.17853 | 0.79651 | 0.25635 | -0.036621 | 0.032044 | -122.493 | 0.15106 | 0.2243 | -0.09613 | 0.26093 | -0.059509 | 0.89722 | 122.7402 | 0.18768 | 0.38452 | 122.9004 | 122.9095 | 122.8226 | 122.8729 | -122.9187 | -122.8775 | 122.6624 | 0.3479 | 3.6484 | 1.4648
3380.1719 | 122.9553 | -53.3798 | 69.4702 | -0.052948 | 0.00040806 | 0.059676 | 0.071395 | -0.0045394 | 0.0034735 | 0.0028582 | -0.022705 | 0.00088875 | 0.0036316 | -0.0025036 | -0.0030013 | -0.0038709 | -0.0018971 | -49.7269 | 69.4839 | -53.4302 | 69.1818 | -52.5879 | -53.2379 | -52.6749 | -51.9699 | 69.5023 | -53.3844 | -53.0777 | -53.2471 | -53.4851 | -53.1784 | -0.050354 | 0.013733 | -0.28839 | 0.79193 | 0.70496 | 0.14191 | 0.75531 | 0.19226 | -0.004577 | 0.032043 | -122.5479 | 0.13275 | 0.20142 | -0.10529 | 0.20599 | -0.10071 | 0.84229 | 122.612 | 0.13733 | 0.3067 | 122.9141 | 122.8867 | 122.8638 | 122.8821 | -122.9004 | -122.8546 | 122.5616 | 0.30212 | 3.653 | 1.4099
3381.1719 | 122.9736 | -53.3981 | 69.4702 | -0.037689 | 0.00040806 | 0.063094 | 0.069045 | 0.00037377 | 0.0047553 | 0.0056354 | -0.010498 | 0.00046135 | 0.00085443 | -0.0016492 | -0.0038559 | -0.0045117 | 2.554e-05 | -49.7223 | 69.4748 | -53.4485 | 69.2001 | -52.5925 | -53.2288 | -52.6794 | -51.9653 | 69.5023 | -53.4073 | -53.0548 | -53.2425 | -53.4851 | -53.1601 | -0.050354 | 0.004577 | -0.27008 | 0.80566 | 0.71869 | 0.16937 | 0.76904 | 0.21973 | -0.009156 | 0.032043 | -122.525 | 0.15564 | 0.23804 | -0.086975 | 0.24719 | -0.077819 | 0.85602 | 122.6486 | 0.16479 | 0.35248 | 122.9233 | 122.9095 | 122.8729 | 122.9004 | -122.9187 | -122.8775 | 122.5983 | 0.34332 | 3.6758 | 1.4328
3382.1719 | 122.9462 | -53.3569 | 69.4656 | -0.060578 | -1.9142e-05 | 0.062666 | 0.069045 | 0.0033646 | 0.00048269 | 0.00414 | -0.019653 | 0.00067495 | 0.0012818 | 0.0028368 | -0.0019333 | -0.0045117 | -0.0027515 | -49.7177 | 69.4794 | -53.4576 | 69.2047 | -52.5833 | -53.2425 | -52.6611 | -51.9608 | 69.4794 | -53.3707 | -53.0502 | -53.2471 | -53.4714 | -53.1601 | -0.10071 | 0.013733 | -0.26093 | 0.77362 | 0.6958 | 0.11444 | 0.79651 | 0.21515 | -0.013733 | 0.013733 | -122.5159 | 0.10986 | 0.19684 | -0.11444 | 0.21057 | -0.10071 | 0.87433 | 122.6624 | 0.1236 | 0.32043 | 122.937 | 122.85 | 122.8363 | 122.8363 | -122.9233 | -122.8363 | 122.5616 | 0.3067 | 3.6392 | 1.3962
3383.1719 | 122.9095 | -53.3707 | 69.4565 | -0.052948 | -0.0017281 | 0.061812 | 0.068404 | -0.00069423 | 0.0039007 | 0.0081988 | -0.022705 | 0.0023839 | 0.00085443 | -0.0010084 | -0.0023605 | -0.0038709 | -0.0023243 | -49.7269 | 69.4748 | -53.4439 | 69.1727 | -52.652 | -53.2928 | -52.7161 | -52.0477 | 69.4885 | -53.3981 | -53.0823 | -53.27 | -53.5172 | -53.1738 | -0.073242 | 0.01831 | -0.28381 | 0.71869 | 0.6546 | 0.07782 | 0.72784 | 0.15106 | -0.027465 | 0.032043 | -122.5388 | 0.10071 | 0.19684 | -0.14648 | 0.2243 | -0.11902 | 0.79193 | 122.6166 | 0.12817 | 0.31586 | 122.9187 | 122.8867 | 122.8455 | 122.8592 | -122.9004 | -122.8546 | 122.5433 | 0.28839 | 3.6438 | 1.3229
3384.1719 | 122.9095 | -53.3524 | 69.4839 | -0.052948 | 0.0010489 | 0.063948 | 0.069259 | 0.0050736 | 0.0017645 | 0.0062762 | -0.010498 | 0.0015295 | 0.001709 | 0.00091422 | -0.0023605 | -0.0062207 | 0.0017345 | -49.7131 | 69.4839 | -53.4485 | 69.1772 | -52.6291 | -53.2516 | -52.7115 | -52.0157 | 69.516 | -53.3936 | -53.0731 | -53.2654 | -53.5126 | -53.1784 | -0.09613 | 0 | -0.3067 | 0.72327 | 0.64087 | 0.10071 | 0.737 | 0.19684 | -0.041199 | 0.032043 | -122.5571 | 0.086975 | 0.17395 | -0.16022 | 0.21515 | -0.11902 | 0.8194 | 122.6257 | 0.12817 | 0.32043 | 122.9324 | 122.9095 | 122.8363 | 122.8683 | -122.9324 | -122.8775 | 122.5296 | 0.27924 | 3.6392 | 1.3367
3385.1719 | 122.9736 | -53.3569 | 69.5114 | -0.060578 | 0.00040806 | 0.061598 | 0.069259 | -0.0013352 | 0.0028327 | 0.00414 | -0.016602 | 0.0011023 | 0.0012818 | 0.0017688 | -0.0017197 | -0.0060071 | -0.00061526 | -49.6674 | 69.4748 | -53.4119 | 69.2184 | -52.5558 | -53.2013 | -52.6382 | -51.9196 | 69.5023 | -53.3661 | -53.0319 | -53.2196 | -53.4348 | -53.1464 | -0.054931 | -0.036622 | -0.29297 | 0.80109 | 0.71869 | 0.15564 | 0.77362 | 0.21057 | -0.009155 | -0.009156 | -122.5433 | 0.13733 | 0.21057 | -0.077819 | 0.21973 | -0.068664 | 0.85602 | 122.6303 | 0.14649 | 0.33417 | 122.8867 | 122.8683 | 122.8317 | 122.8592 | -122.9233 | -122.8775 | 122.5754 | 0.32501 | 3.6896 | 1.4374
3386.1719 | 122.9645 | -53.3249 | 69.4702 | -0.12161 | -1.9142e-05 | 0.061385 | 0.068832 | -0.00048063 | 0.0011237 | 0.005849 | 0.0047608 | 0.0017431 | 0.00064083 | 0.0019824 | -0.0038559 | -0.0057935 | 0.0017345 | -49.6628 | 69.4931 | -53.421 | 69.2184 | -52.5467 | -53.1784 | -52.6199 | -51.915 | 69.5068 | -53.3661 | -53.0045 | -53.2104 | -53.4439 | -53.1143 | -0.096131 | 0.022888 | -0.25177 | 0.7782 | 0.70496 | 0.14648 | 0.80109 | 0.24262 | -0.041199 | 0.036621 | -122.4747 | 0.11444 | 0.21057 | -0.11902 | 0.25177 | -0.07782 | 0.87433 | 122.6395 | 0.15564 | 0.36163 | 122.9141 | 122.8729 | 122.818 | 122.8317 | -122.8912 | -122.8363 | 122.5433 | 0.32043 | 3.6621 | 1.4099
3387.1719 | 122.9279 | -53.3432 | 69.4977 | -0.091095 | -0.0010873 | 0.060744 | 0.069686 | -0.0038986 | 0.0013373 | 0.0054218 | -0.022705 | 0.0023839 | 0.0023498 | 0.0030506 | -0.0019333 | -0.0049389 | 0.0045117 | -49.6857 | 69.4794 | -53.421 | 69.1956 | -52.5742 | -53.2196 | -52.6611 | -51.9608 | 69.5023 | -53.3844 | -53.0548 | -53.2425 | -53.4622 | -53.1418 | -0.07782 | -0.018311 | -0.30212 | 0.76904 | 0.68207 | 0.1236 | 0.75989 | 0.20142 | -0.041198 | 0.004577 | -122.5525 | 0.10071 | 0.20142 | -0.11902 | 0.24261 | -0.07782 | 0.84686 | 122.6166 | 0.14191 | 0.32959 | 122.9004 | 122.8867 | 122.8226 | 122.8455 | -122.9187 | -122.8821 | 122.5388 | 0.28839 | 3.6575 | 1.3824
3388.1719 | 122.9324 | -53.3386 | 69.4839 | -0.083466 | -0.00023294 | 0.060744 | 0.068618 | 0.0020828 | 0.00091009 | 0.0060626 | -0.01355 | 0.0019567 | 0.00042723 | -0.00079478 | -0.0023605 | -0.0064343 | 0.0030163 | -49.6719 | 69.4839 | -53.4302 | 69.2001 | -52.597 | -53.2288 | -52.652 | -51.9516 | 69.5435 | -53.3844 | -53.0411 | -53.2379 | -53.4668 | -53.1281 | -0.091553 | 0 | -0.28381 | 0.74158 | 0.68664 | 0.10986 | 0.7782 | 0.20142 | -0.045776 | 0.059509 | -122.525 | 0.10071 | 0.21057 | -0.12817 | 0.25635 | -0.082398 | 0.83313 | 122.6303 | 0.14648 | 0.34332 | 122.9141 | 122.9279 | 122.8226 | 122.8821 | -122.9141 | -122.8683 | 122.5388 | 0.29755 | 3.6667 | 1.387
3389.1719 | 122.9462 | -53.3386 | 69.4977 | -0.014801 | 0.00040806 | 0.062453 | 0.0699 | 0.0027238 | 0.0017645 | 0.0047808 | -0.028809 | -0.00017945 | 0.0014954 | -0.0048536 | -0.0032151 | -0.0047253 | -0.00082886 | -49.6628 | 69.5068 | -53.3981 | 69.223 | -52.5696 | -53.2104 | -52.652 | -51.9333 | 69.5297 | -53.3798 | -53.0411 | -53.215 | -53.4576 | -53.1281 | -0.059509 | 0.009155 | -0.27466 | 0.76904 | 0.68664 | 0.12817 | 0.74615 | 0.18768 | -0.041199 | 0.032043 | -122.5388 | 0.1236 | 0.21057 | -0.11902 | 0.25177 | -0.07782 | 0.82855 | 122.6212 | 0.16479 | 0.33874 | 122.905 | 122.9095 | 122.8455 | 122.8683 | -122.8958 | -122.8775 | 122.5616 | 0.29755 | 3.6758 | 1.4053
3390.1719 | 122.9233 | -53.3203 | 69.5114 | -0.022431 | -0.0015145 | 0.062666 | 0.070754 | -0.0015488 | 0.0024053 | 0.005849 | -0.0043946 | -0.00017945 | 0.001068 | -0.00036738 | -0.0032151 | -0.0040845 | -0.0036059 | -49.649 | 69.4885 | -53.3936 | 69.2322 | -52.5604 | -53.2104 | -52.6382 | -51.915 | 69.5343 | -53.3615 | -53.0228 | -53.1967 | -53.4485 | -53.1143 | -0.073243 | -0.022889 | -0.27924 | 0.75989 | 0.68207 | 0.10986 | 0.75531 | 0.18311 | -0.041199 | 0.022888 | -122.5342 | 0.1236 | 0.20599 | -0.12817 | 0.24719 | -0.086975 | 0.83313 | 122.6257 | 0.16479 | 0.33875 | 122.8821 | 122.8958 | 122.8088 | 122.8546 | -122.905 | -122.8729 | 122.5525 | 0.29755 | 3.6713 | 1.4053
3391.1719 | 122.9233 | -53.3249 | 69.516 | -0.10635 | -1.9142e-05 | 0.062025 | 0.069045 | 0.00037377 | 0.0026191 | 0.0054218 | -0.019653 | -0.0010339 | 0.0025634 | -0.0067762 | -0.0023605 | -0.0057935 | -0.0010425 | -49.6719 | 69.5068 | -53.4119 | 69.1864 | -52.6154 | -53.2516 | -52.684 | -51.9974 | 69.5251 | -53.3615 | -53.0594 | -53.2288 | -53.4851 | -53.1601 | -0.086975 | -0.009155 | -0.32959 | 0.70953 | 0.64087 | 0.073242 | 0.72784 | 0.16022 | -0.036621 | 0.009155 | -122.5754 | 0.09613 | 0.1648 | -0.16022 | 0.20142 | -0.1236 | 0.79651 | 122.5983 | 0.13275 | 0.30212 | 122.9187 | 122.8867 | 122.8317 | 122.85 | -122.9279 | -122.8775 | 122.5113 | 0.2655 | 3.653 | 1.3275
3392.1719 | 122.9416 | -53.3066 | 69.5114 | -0.037689 | 0.0014761 | 0.061385 | 0.070113 | 0.0020828 | 0.00069649 | 0.002431 | -0.010498 | 0.00024775 | 2.8e-08 | 0.0043322 | -0.0010787 | -0.0047253 | 0.0023755 | -49.6262 | 69.516 | -53.389 | 69.2642 | -52.5192 | -53.1692 | -52.6062 | -51.8921 | 69.5251 | -53.334 | -52.9999 | -53.1921 | -53.4164 | -53.1052 | -0.082397 | 0.004577 | -0.24719 | 0.78735 | 0.70038 | 0.13733 | 0.78278 | 0.21973 | -0.027465 | 0.013732 | -122.5113 | 0.11444 | 0.20142 | -0.10986 | 0.22888 | -0.082398 | 0.86975 | 122.6532 | 0.14191 | 0.33417 | 122.905 | 122.8592 | 122.8226 | 122.8317 | -122.9004 | -122.8455 | 122.5708 | 0.3067 | 3.6804 | 1.4145
3393.1719 | 122.9645 | -53.3295 | 69.5435 | -0.098725 | -1.9142e-05 | 0.06053 | 0.068191 | -0.0038986 | 0.0032599 | 0.0037128 | -0.019653 | 0.00067495 | 0.001709 | 0.003905 | -0.0023605 | -0.0064343 | -0.00040166 | -49.6124 | 69.5251 | -53.3936 | 69.278 | -52.5101 | -53.1509 | -52.5925 | -51.8692 | 69.5709 | -53.3295 | -52.9816 | -53.1601 | -53.4073 | -53.0777 | -0.064087 | -0.018311 | -0.2655 | 0.8194 | 0.737 | 0.17853 | 0.80109 | 0.24262 | 0 | 0.027466 | -122.525 | 0.16937 | 0.25177 | -0.07782 | 0.25177 | -0.07782 | 0.88348 | 122.6715 | 0.16937 | 0.3479 | 122.9187 | 122.9004 | 122.8546 | 122.9004 | -122.937 | -122.8729 | 122.6074 | 0.3479 | 3.717 | 1.4603
3394.1719 | 122.9462 | -53.3386 | 69.5297 | -0.098725 | 0.0010489 | 0.063734 | 0.068832 | 0.0029374 | 0.0026191 | 0.0032856 | -0.0074462 | -0.0010339 | 0.002777 | 0.0013416 | -0.0032151 | -0.0060071 | 0.0019483 | -49.6262 | 69.5297 | -53.3936 | 69.2459 | -52.533 | -53.183 | -52.6382 | -51.9196 | 69.5801 | -53.3478 | -53.0136 | -53.1921 | -53.4302 | -53.1097 | -0.054932 | 0 | -0.28381 | 0.80566 | 0.70038 | 0.15564 | 0.75531 | 0.21057 | -0.009155 | 0.050354 | -122.5433 | 0.14648 | 0.22888 | -0.091553 | 0.23804 | -0.082398 | 0.8606 | 122.6395 | 0.15564 | 0.33417 | 122.9233 | 122.9279 | 122.8683 | 122.9187 | -122.9233 | -122.8775 | 122.5845 | 0.32501 | 3.7125 | 1.4191
3395.1719 | 122.9507 | -53.2791 | 69.5343 | -0.068207 | 0.0031851 | 0.060316 | 0.069686 | -0.0026168 | 0.0030463 | 0.0064898 | 0.016968 | 0.00024775 | 0.00042723 | 0.0043322 | -0.00065151 | -0.0047253 | 0.0036571 | -49.5712 | 69.548 | -53.3707 | 69.31 | -52.4734 | -53.1372 | -52.597 | -51.8463 | 69.5435 | -53.3112 | -52.9541 | -53.1418 | -53.3707 | -53.0457 | -0.091553 | 0.013733 | -0.2243 | 0.80566 | 0.68207 | 0.14191 | 0.77362 | 0.23346 | -0.032043 | 0.009155 | -122.4884 | 0.13733 | 0.23346 | -0.091553 | 0.2655 | -0.05951 | 0.89722 | 122.6807 | 0.16937 | 0.35706 | 122.9187 | 122.8546 | 122.8271 | 122.8226 | -122.905 | -122.8455 | 122.5891 | 0.32501 | 3.7079 | 1.4328
3396.1719 | 122.9507 | -53.2974 | 69.5435 | -0.060578 | -0.0013009 | 0.061171 | 0.070541 | 0.00080117 | 0.0030463 | 0.0037128 | -0.022705 | 0.0019567 | 0.002777 | 0.00027342 | -0.0030013 | -0.0053663 | 2.554e-05 | -49.585 | 69.5343 | -53.3707 | 69.2596 | -52.5055 | -53.1647 | -52.5925 | -51.8646 | 69.5801 | -53.3249 | -52.977 | -53.1692 | -53.4119 | -53.096 | -0.073243 | -0.009155 | -0.28381 | 0.79193 | 0.70496 | 0.13275 | 0.7782 | 0.20599 | -0.027466 | 0.036621 | -122.5204 | 0.12817 | 0.20142 | -0.11444 | 0.22888 | -0.086975 | 0.86517 | 122.6303 | 0.15564 | 0.3479 | 122.905 | 122.905 | 122.8317 | 122.8775 | -122.9141 | -122.8683 | 122.5571 | 0.32043 | 3.7125 | 1.4328
3397.1719 | 122.9141 | -53.2883 | 69.5251 | -0.037689 | 0.00083526 | 0.060316 | 0.070113 | -0.00026703 | 0.0043281 | 0.0099078 | -0.028809 | 0.0011023 | 0.001709 | 0.0066822 | -0.0032151 | -0.0047253 | 0.0010937 | -49.6033 | 69.5389 | -53.3707 | 69.2459 | -52.5513 | -53.1876 | -52.6337 | -51.9424 | 69.5663 | -53.3386 | -53.0045 | -53.1876 | -53.4348 | -53.1143 | -0.082398 | 0.013733 | -0.27923 | 0.737 | 0.6546 | 0.10071 | 0.737 | 0.18311 | -0.050354 | 0.041199 | -122.5296 | 0.10071 | 0.17395 | -0.14648 | 0.2243 | -0.09613 | 0.8194 | 122.6166 | 0.15106 | 0.33417 | 122.9095 | 122.905 | 122.8271 | 122.8546 | -122.8958 | -122.8638 | 122.5342 | 0.28381 | 3.685 | 1.3458
3398.1719 | 122.8958 | -53.2791 | 69.5572 | -0.083466 | 0.00083526 | 0.061171 | 0.069472 | -0.00048063 | 0.0028327 | 0.0049946 | 0.0078126 | 0.0021703 | 0.0014954 | 0.0036914 | -0.0032151 | -0.0066479 | 0.00066654 | -49.6078 | 69.5572 | -53.3569 | 69.2505 | -52.5604 | -53.183 | -52.6199 | -51.9196 | 69.5801 | -53.3203 | -52.9907 | -53.1738 | -53.421 | -53.1052 | -0.07782 | 0 | -0.3067 | 0.71869 | 0.65918 | 0.096131 | 0.737 | 0.17395 | -0.041198 | 0.022888 | -122.5479 | 0.10529 | 0.17395 | -0.14191 | 0.21515 | -0.10071 | 0.79651 | 122.6074 | 0.14648 | 0.32959 | 122.9141 | 122.9004 | 122.8363 | 122.8592 | -122.9141 | -122.8775 | 122.5296 | 0.28839 | 3.6713 | 1.3596
3399.1719 | 122.9553 | -53.2333 | 69.5389 | -0.26657 | -0.00087374 | 0.062025 | 0.068191 | -0.00090783 | 0.0024053 | 0.0034992 | 0.0047608 | 0.00088875 | 0.00064083 | -0.0025036 | -0.0030013 | -0.0049389 | 0.00023934 | -49.4843 | 69.5709 | -53.3615 | 69.3192 | -52.4368 | -53.1189 | -52.5513 | -51.8326 | 69.5709 | -53.2837 | -52.9266 | -53.1281 | -53.3615 | -53.0365 | -0.12817 | 0.032044 | -0.21973 | 0.79651 | 0.68207 | 0.11444 | 0.81024 | 0.24262 | -0.050354 | 0.032044 | -122.4655 | 0.10529 | 0.19684 | -0.12817 | 0.24719 | -0.07782 | 0.92468 | 122.6807 | 0.15564 | 0.35705 | 122.9324 | 122.8546 | 122.8043 | 122.8043 | -122.9004 | -122.8226 | 122.5525 | 0.3067 | 3.7491 | 1.4008
3400.1719 | 122.9553 | -53.27 | 69.5572 | -0.098725 | -0.00023294 | 0.062666 | 0.070327 | -0.0026168 | 0.0028327 | 0.0049946 | -0.019653 | 0.00024775 | 0.00021363 | -0.003999 | -0.0012925 | -0.0079297 | -0.00018806 | -49.5621 | 69.5572 | -53.3295 | 69.2871 | -52.4872 | -53.1601 | -52.597 | -51.8646 | 69.5892 | -53.302 | -52.9587 | -53.1692 | -53.3936 | -53.064 | -0.05951 | 0 | -0.27008 | 0.78278 | 0.67291 | 0.10986 | 0.73242 | 0.16937 | -0.032044 | 0.032043 | -122.5159 | 0.10071 | 0.20599 | -0.1236 | 0.23804 | -0.091553 | 0.84228 | 122.6166 | 0.13275 | 0.34332 | 122.8867 | 122.8912 | 122.8271 | 122.8592 | -122.8867 | -122.8592 | 122.5571 | 0.31128 | 3.7079 | 1.4053
3401.1719 | 122.9462 | -53.2608 | 69.5663 | -0.037689 | -0.0013009 | 0.061598 | 0.070113 | 0.00058737 | 0.00069649 | 0.0071308 | 0.0047608 | 0.00067495 | 0.001068 | -0.0052808 | -0.0025741 | -0.0049389 | -0.00061526 | -49.5438 | 69.5892 | -53.3386 | 69.2871 | -52.4872 | -53.1418 | -52.5879 | -51.8555 | 69.5938 | -53.2974 | -52.9587 | -53.1372 | -53.3798 | -53.0411 | -0.07782 | 0.022888 | -0.27924 | 0.77362 | 0.67291 | 0.11902 | 0.75073 | 0.19684 | -0.036621 | 0.027466 | -122.525 | 0.1236 | 0.21973 | -0.11902 | 0.25635 | -0.082398 | 0.85144 | 122.6257 | 0.16022 | 0.33875 | 122.9279 | 122.8912 | 122.85 | 122.8546 | -122.905 | -122.8638 | 122.5479 | 0.30212 | 3.717 | 1.4053
3402.1719 | 122.9645 | -53.2745 | 69.5709 | -0.091095 | -0.0023691 | 0.062239 | 0.0699 | -0.0017624 | 0.00048269 | 0.005849 | -0.010498 | 0.0013159 | 0.00085443 | 0.001128 | -0.0027877 | -0.0040845 | -0.0027515 | -49.5346 | 69.5755 | -53.3295 | 69.3008 | -52.4826 | -53.1143 | -52.5696 | -51.8234 | 69.5984 | -53.27 | -52.9358 | -53.1189 | -53.3569 | -53.0594 | -0.054932 | 0.004577 | -0.27008 | 0.79193 | 0.70496 | 0.16022 | 0.75989 | 0.21515 | 0.004578 | 0.027466 | -122.5067 | 0.15564 | 0.21515 | -0.082398 | 0.21057 | -0.086976 | 0.84686 | 122.6303 | 0.15106 | 0.33417 | 122.905 | 122.8683 | 122.85 | 122.8729 | -122.9004 | -122.8409 | 122.5754 | 0.33874 | 3.7399 | 1.4511
3403.1719 | 122.9416 | -53.2654 | 69.5709 | -0.11398 | -0.00087374 | 0.063734 | 0.069045 | 0.00016017 | 0.0021917 | 0.005849 | 0.013916 | -0.00039305 | 0.0019226 | 0.0017688 | -0.0010787 | -0.0032301 | -0.00040166 | -49.5209 | 69.5801 | -53.3157 | 69.3146 | -52.4551 | -53.1052 | -52.5513 | -51.8188 | 69.5984 | -53.2654 | -52.9266 | -53.1189 | -53.3569 | -53.0319 | -0.050354 | 0.009155 | -0.25635 | 0.81024 | 0.71411 | 0.16022 | 0.76446 | 0.21057 | 0 | 0.027466 | -122.4976 | 0.14648 | 0.23346 | -0.091553 | 0.23346 | -0.091553 | 0.8606 | 122.6303 | 0.14648 | 0.33874 | 122.8958 | 122.8638 | 122.8455 | 122.8638 | -122.8867 | -122.8363 | 122.58 | 0.33874 | 3.7445 | 1.4465
3404.1719 | 122.9233 | -53.2608 | 69.5938 | -0.10635 | -0.0013009 | 0.06053 | 0.068618 | -5.343e-05 | 0.0030463 | 0.0037128 | -0.01355 | 0.0017431 | 0.0019226 | -0.00079478 | -0.0017197 | -0.0049389 | -0.0031787 | -49.5392 | 69.5618 | -53.3432 | 69.3054 | -52.4918 | -53.1372 | -52.597 | -51.8509 | 69.6121 | -53.2745 | -52.9541 | -53.1418 | -53.389 | -53.064 | -0.082398 | -0.032043 | -0.28839 | 0.76904 | 0.66376 | 0.1236 | 0.74616 | 0.20599 | -0.013733 | 0.018311 | -122.5479 | 0.11902 | 0.19684 | -0.12817 | 0.21057 | -0.11444 | 0.85144 | 122.6486 | 0.13275 | 0.32043 | 122.905 | 122.8867 | 122.8226 | 122.8729 | -122.937 | -122.8683 | 122.5662 | 0.3067 | 3.7216 | 1.4099
3405.1719 | 122.9004 | -53.2745 | 69.5892 | -0.075836 | 0.0014761 | 0.06288 | 0.068191 | 0.0018692 | 0.0021917 | 0.0037128 | -0.0074462 | 0.0011023 | 0.00021363 | 0.002196 | -0.0038559 | -0.0068615 | 0.0038709 | -49.53 | 69.5801 | -53.3432 | 69.31 | -52.4872 | -53.1326 | -52.5833 | -51.8417 | 69.6075 | -53.2654 | -52.9541 | -53.1326 | -53.3936 | -53.0548 | -0.068665 | -0.009155 | -0.27923 | 0.78735 | 0.69122 | 0.14191 | 0.75989 | 0.21057 | 0.009155 | 0.018311 | -122.5433 | 0.14191 | 0.21973 | -0.11902 | 0.21057 | -0.12817 | 0.85602 | 122.6532 | 0.13275 | 0.31128 | 122.9233 | 122.8729 | 122.8546 | 122.8821 | -122.9324 | -122.8546 | 122.5845 | 0.32043 | 3.7445 | 1.4328
3406.1719 | 122.9874 | -53.2516 | 69.5663 | -0.068207 | 0.0023307 | 0.061385 | 0.0699 | -0.0032578 | 0.0032599 | 0.0052082 | 0.029175 | 0.00088875 | 0.00085443 | 0.0026232 | -0.0012925 | -0.0070753 | -0.0025379 | -49.4888 | 69.5801 | -53.334 | 69.3375 | -52.4048 | -53.0594 | -52.5238 | -51.7776 | 69.6304 | -53.2425 | -52.8992 | -53.0777 | -53.3203 | -53.0182 | -0.082397 | 0.013733 | -0.22888 | 0.84686 | 0.72784 | 0.19226 | 0.81024 | 0.27466 | 0.009155 | 0.064087 | -122.4655 | 0.17395 | 0.23346 | -0.068664 | 0.22431 | -0.077819 | 0.92926 | 122.6715 | 0.1648 | 0.34332 | 122.9141 | 122.8729 | 122.8317 | 122.8821 | -122.9004 | -122.8088 | 122.5891 | 0.35248 | 3.7628 | 1.474
3407.1719 | 122.9233 | -53.2471 | 69.6075 | -0.075836 | 0.00040806 | 0.062025 | 0.069045 | 0.0020828 | 0.0028327 | 0.0064898 | -0.0013428 | 3.4148e-05 | -0.0021362 | -0.0031446 | -0.0036423 | -0.0053663 | -0.0016833 | -49.498 | 69.5618 | -53.334 | 69.3283 | -52.4551 | -53.0869 | -52.565 | -51.8051 | 69.635 | -53.2654 | -52.9175 | -53.1052 | -53.3615 | -53.0273 | -0.086975 | -0.045776 | -0.27924 | 0.79193 | 0.68207 | 0.16022 | 0.76904 | 0.24719 | -0.018311 | 0.027466 | -122.525 | 0.14191 | 0.21973 | -0.11444 | 0.23804 | -0.09613 | 0.87891 | 122.6624 | 0.16022 | 0.3479 | 122.8958 | 122.9004 | 122.8088 | 122.8821 | -122.9416 | -122.8729 | 122.5754 | 0.32959 | 3.7491 | 1.442
3408.1719 | 122.9599 | -53.2471 | 69.5892 | -0.060578 | 0.00083526 | 0.060957 | 0.070327 | 0.00037377 | 0.0015509 | 0.0073444 | -0.01355 | 0.0021703 | 0.0032044 | -0.0025036 | -0.0015061 | -0.0049389 | -0.0018971 | -49.4888 | 69.5984 | -53.2837 | 69.3283 | -52.4323 | -53.0869 | -52.5421 | -51.796 | 69.635 | -53.2654 | -52.9037 | -53.0914 | -53.3386 | -53.0045 | -0.036621 | 0.009156 | -0.26092 | 0.81482 | 0.70496 | 0.16022 | 0.74158 | 0.19684 | -0.018311 | 0.045777 | -122.493 | 0.15564 | 0.24261 | -0.091553 | 0.26093 | -0.073242 | 0.85144 | 122.612 | 0.17395 | 0.36163 | 122.8821 | 122.9004 | 122.8455 | 122.8821 | -122.8729 | -122.8546 | 122.5754 | 0.34332 | 3.7582 | 1.4511
3409.1719 | 122.9691 | -53.2196 | 69.6075 | -0.12924 | 0.00019446 | 0.060316 | 0.070541 | -0.0017624 | 0.0019781 | 0.0052082 | 0.001709 | 0.00088875 | 0.00021363 | 0.00048702 | -0.0023605 | -0.0060071 | -0.0048877 | -49.4843 | 69.6213 | -53.2837 | 69.3512 | -52.4323 | -53.0685 | -52.5146 | -51.7731 | 69.635 | -53.2425 | -52.89 | -53.0548 | -53.3249 | -52.9861 | -0.064087 | 0.013733 | -0.25635 | 0.78735 | 0.70496 | 0.15106 | 0.76904 | 0.21515 | -0.022889 | 0.027466 | -122.4976 | 0.16479 | 0.23346 | -0.10529 | 0.25635 | -0.082397 | 0.85144 | 122.6349 | 0.18768 | 0.35248 | 122.905 | 122.8775 | 122.8409 | 122.8546 | -122.8912 | -122.85 | 122.5708 | 0.32959 | 3.7354 | 1.4465
3410.1719 | 122.9233 | -53.2013 | 69.5938 | -0.083466 | -0.00044654 | 0.062666 | 0.068404 | 0.00251 | 0.0015509 | 0.0049946 | -0.022705 | 0.00067495 | -0.00042717 | -0.001222 | -0.0012925 | -0.0062207 | 2.554e-05 | -49.4888 | 69.5938 | -53.3157 | 69.3237 | -52.4689 | -53.096 | -52.5375 | -51.8051 | 69.635 | -53.2608 | -52.9221 | -53.1052 | -53.3478 | -53.0045 | -0.11444 | 0 | -0.27008 | 0.73242 | 0.66376 | 0.10529 | 0.7782 | 0.21973 | -0.059509 | 0.041199 | -122.5159 | 0.09613 | 0.19684 | -0.14648 | 0.25635 | -0.086975 | 0.84686 | 122.6395 | 0.15564 | 0.33875 | 122.9095 | 122.8958 | 122.7951 | 122.8363 | -122.9095 | -122.8546 | 122.525 | 0.27924 | 3.7125 | 1.3962
3411.1719 | 122.9507 | -53.215 | 69.6259 | -0.12924 | 0.00040806 | 0.062666 | 0.069686 | 0.00080117 | 0.0017645 | 0.0064898 | -0.022705 | 0.0015295 | -0.00064077 | 0.00027342 | -0.0040695 | -0.0055799 | 0.0010937 | -49.4705 | 69.6213 | -53.2837 | 69.342 | -52.4414 | -53.0869 | -52.5238 | -51.796 | 69.6533 | -53.2562 | -52.8854 | -53.096 | -53.3249 | -53.0182 | -0.068664 | -0.004577 | -0.28381 | 0.77362 | 0.69122 | 0.12817 | 0.75989 | 0.19684 | -0.041199 | 0.027466 | -122.5113 | 0.11902 | 0.19684 | -0.10986 | 0.23804 | -0.068664 | 0.84228 | 122.6257 | 0.16022 | 0.37079 | 122.905 | 122.9095 | 122.8363 | 122.8683 | -122.9095 | -122.8821 | 122.5571 | 0.32959 | 3.7445 | 1.4191
3412.1719 | 122.9507 | -53.2242 | 69.6442 | -0.052948 | -0.00044654 | 0.060744 | 0.071181 | 0.00080117 | 0.0039007 | 0.0056354 | -0.0043946 | 0.00088875 | -0.00021357 | -0.0042126 | -0.0027877 | -0.0053663 | -0.0014697 | -49.4431 | 69.5892 | -53.2883 | 69.3512 | -52.4094 | -53.0685 | -52.533 | -51.7685 | 69.635 | -53.2516 | -52.8854 | -53.0731 | -53.3112 | -52.9999 | -0.064087 | -0.054932 | -0.29297 | 0.81482 | 0.69122 | 0.15564 | 0.75531 | 0.21973 | -0.027466 | -0.009155 | -122.5296 | 0.15106 | 0.2243 | -0.086975 | 0.25177 | -0.059509 | 0.87891 | 122.6395 | 0.17853 | 0.36621 | 122.8775 | 122.8867 | 122.8134 | 122.8592 | -122.9324 | -122.8958 | 122.5754 | 0.33874 | 3.7811 | 1.4557
3413.1719 | 122.9782 | -53.2059 | 69.603 | -0.068207 | 0.0010489 | 0.059676 | 0.069259 | 0.0022964 | 0.0043281 | 0.00029479 | 0.0047608 | 0.00088875 | -0.00064077 | 5.9824e-05 | -0.0027877 | -0.0075025 | -0.00061526 | -49.4339 | 69.6442 | -53.2745 | 69.3604 | -52.3911 | -53.0548 | -52.4918 | -51.7502 | 69.6487 | -53.2104 | -52.8488 | -53.0411 | -53.2608 | -52.9678 | -0.068664 | 0.041199 | -0.24261 | 0.81482 | 0.71411 | 0.15106 | 0.78278 | 0.21973 | -0.004577 | 0.045777 | -122.4518 | 0.16479 | 0.23804 | -0.054931 | 0.24261 | -0.050354 | 0.88348 | 122.6349 | 0.16937 | 0.36163 | 122.9187 | 122.8592 | 122.85 | 122.8546 | -122.8775 | -122.8134 | 122.5662 | 0.35706 | 3.772 | 1.4557
3414.1719 | 122.9782 | -53.1784 | 69.6121 | -0.083466 | 0.0012625 | 0.062453 | 0.0699 | 0.00058737 | 0.0041143 | 0.0045672 | 0.0047608 | 0.0013159 | 0.00085443 | -0.0044262 | -0.0025741 | -0.0060071 | 0.0028027 | -49.4247 | 69.6167 | -53.2654 | 69.3237 | -52.2675 | -53.009 | -52.4918 | -51.741 | 69.6716 | -53.2196 | -52.858 | -53.0273 | -53.2837 | -52.9816 | -0.086975 | 0.004577 | -0.28839 | 0.91095 | 0.68665 | 0.16937 | 0.77362 | 0.25635 | -0.041198 | 0.059509 | -122.4701 | 0.15106 | 0.19684 | -0.10528 | 0.23804 | -0.064087 | 0.99792 | 122.5891 | 0.19226 | 0.36163 | 122.8821 | 122.8912 | 122.7951 | 122.85 | -122.8775 | -122.8317 | 122.5021 | 0.32044 | 3.7537 | 1.4374
3415.1719 | 122.9736 | -53.1601 | 69.6442 | -0.075836 | 0.00040806 | 0.059462 | 0.067336 | 0.0010148 | 0.0019781 | 0.0052082 | 0.010864 | 0.0025975 | 0.0021362 | -0.0069898 | -0.0030013 | -0.0075025 | -0.00061526 | -49.4156 | 69.6304 | -53.2837 | 69.3787 | -52.3865 | -53.0273 | -52.4872 | -51.7181 | 69.6671 | -53.2379 | -52.8351 | -53.0273 | -53.2379 | -52.9358 | -0.1236 | -0.013733 | -0.2655 | 0.77362 | 0.67291 | 0.13275 | 0.79651 | 0.25635 | -0.07782 | 0.022888 | -122.4792 | 0.13275 | 0.2243 | -0.07782 | 0.30212 | 0 | 0.89722 | 122.6624 | 0.21057 | 0.40283 | 122.9141 | 122.905 | 122.7905 | 122.8271 | -122.9279 | -122.8821 | 122.5388 | 0.32501 | 3.7445 | 1.442
3416.1719 | 122.9599 | -53.1967 | 69.6396 | -0.083466 | -0.0015145 | 0.061385 | 0.068618 | 0.0035782 | 0.0019781 | 0.0052082 | 0.0047608 | 3.4148e-05 | -0.00021357 | -0.0048536 | -0.0012925 | -0.0040845 | 0.0010937 | -49.411 | 69.6442 | -53.2837 | 69.397 | -52.3773 | -53.0273 | -52.4643 | -51.6998 | 69.6625 | -53.2196 | -52.8305 | -52.9907 | -53.2608 | -52.9449 | -0.086975 | 0.004578 | -0.24261 | 0.8194 | 0.73242 | 0.16937 | 0.8194 | 0.25635 | -0.022888 | 0.022889 | -122.4701 | 0.20599 | 0.25177 | -0.064087 | 0.27466 | -0.041199 | 0.90637 | 122.6807 | 0.22888 | 0.3891 | 122.9279 | 122.8821 | 122.8409 | 122.8592 | -122.9233 | -122.8592 | 122.5937 | 0.36621 | 3.7857 | 1.4969
3417.1719 | 122.9782 | -53.1876 | 69.6396 | -0.014801 | 0.0016899 | 0.062239 | 0.069472 | 0.0057144 | -0.00015811 | 0.005849 | 0.023071 | 0.0019567 | 0.00064083 | -0.0018628 | -0.00086511 | -0.0077161 | -0.0010425 | -49.411 | 69.635 | -53.27 | 69.31 | -52.4826 | -52.9083 | -52.446 | -51.6815 | 69.6716 | -53.1876 | -52.8351 | -53.0136 | -53.2654 | -52.9449 | -0.082397 | -0.004577 | -0.32959 | 0.70496 | 0.74158 | 0.27924 | 0.82397 | 0.36163 | 0 | 0.032044 | -122.4747 | 0.17395 | 0.24262 | -0.07782 | 0.24262 | -0.07782 | 0.78735 | 122.58 | 0.17395 | 0.35248 | 122.905 | 122.8592 | 122.8226 | 122.8592 | -122.9095 | -122.8271 | 122.4976 | 0.35248 | 3.7766 | 1.506
3418.1719 | 122.9507 | -53.1418 | 69.6808 | -0.045319 | -0.00066014 | 0.060103 | 0.069472 | 0.0010148 | 0.0030463 | 0.0043536 | -0.01355 | 0.00067495 | 0.0032044 | 0.0017688 | -0.0027877 | -0.0040845 | 0.0010937 | -49.3835 | 69.635 | -53.2425 | 69.4016 | -52.3544 | -53.0045 | -52.4551 | -51.6907 | 69.6671 | -53.2013 | -52.8671 | -53.064 | -53.1647 | -52.9221 | -0.10071 | -0.045776 | -0.27924 | 0.78735 | 0.68665 | 0.13733 | 0.78735 | 0.23804 | -0.059509 | -0.013733 | -122.5479 | 0.07782 | 0.21973 | -0.022888 | 0.27924 | 0.036621 | 0.88806 | 122.644 | 0.13733 | 0.33417 | 122.8775 | 122.8683 | 122.7768 | 122.8088 | -122.9233 | -122.8821 | 122.5433 | 0.27466 | 3.7582 | 1.4511
3419.1719 | 122.9736 | -53.1647 | 69.6579 | -0.03006 | 0.00040806 | 0.061385 | 0.068618 | 0.0022964 | 0.0024053 | 0.0062762 | 0.016968 | 0.0013159 | 0.001068 | -0.0018628 | 0.00063009 | -0.0051527 | -0.0018971 | -49.4202 | 69.6808 | -53.2425 | 69.3741 | -52.4048 | -53.0182 | -52.4551 | -51.7731 | 69.7128 | -53.1967 | -52.8305 | -52.9907 | -53.2425 | -52.9495 | -0.07782 | 0.022888 | -0.28381 | 0.75989 | 0.70953 | 0.14648 | 0.78735 | 0.22431 | -0.032043 | 0.054932 | -122.4884 | 0.17395 | 0.21515 | -0.07782 | 0.24719 | -0.045777 | 0.83771 | 122.6166 | 0.20599 | 0.36621 | 122.9233 | 122.9095 | 122.8455 | 122.8775 | -122.9004 | -122.8546 | 122.5388 | 0.33417 | 3.7445 | 1.3916
3420.1719 | 122.9187 | -53.1692 | 69.6762 | -0.03006 | 0.0010489 | 0.061171 | 0.068404 | -0.0021896 | 0.00069649 | 0.00414 | 0.026123 | 0.00024775 | 0.0023498 | -0.0033582 | -0.0025741 | -0.0049389 | -0.00018806 | -49.4064 | 69.6808 | -53.2516 | 69.3832 | -52.4048 | -53.0273 | -52.4734 | -51.7593 | 69.7266 | -53.1738 | -52.8488 | -53.0045 | -53.2608 | -52.9587 | -0.082398 | 0.004578 | -0.29297 | 0.76447 | 0.6958 | 0.14191 | 0.7782 | 0.2243 | -0.004578 | 0.050354 | -122.525 | 0.16479 | 0.21057 | -0.091553 | 0.21515 | -0.086975 | 0.84686 | 122.6349 | 0.16937 | 0.32501 | 122.9324 | 122.9004 | 122.85 | 122.8958 | -122.9279 | -122.85 | 122.5525 | 0.32043 | 3.7628 | 1.4099
3421.1719 | 122.9828 | -53.1647 | 69.6991 | -0.075836 | 0.00019446 | 0.06288 | 0.068618 | -0.001976 | 0.0021917 | 0.0037128 | 0.026123 | 3.4148e-05 | 0.0014954 | -0.0035718 | -0.0015061 | -0.0053663 | 0.00045294 | -49.3973 | 69.6945 | -53.2562 | 69.3878 | -52.4094 | -52.9953 | -52.4506 | -51.7181 | 69.7037 | -53.1876 | -52.8259 | -52.9816 | -53.2425 | -52.9129 | -0.091553 | -0.004578 | -0.31128 | 0.75531 | 0.71411 | 0.16937 | 0.80566 | 0.26093 | -0.022888 | 0.004577 | -122.525 | 0.18311 | 0.25177 | -0.07782 | 0.27466 | -0.054932 | 0.84686 | 122.644 | 0.20599 | 0.36163 | 122.9507 | 122.8912 | 122.8592 | 122.8683 | -122.9553 | -122.8867 | 122.5525 | 0.33875 | 3.7674 | 1.4465
3422.1719 | 122.9507 | -53.1418 | 69.7128 | -0.037689 | -0.00066014 | 0.059889 | 0.067336 | -0.00048063 | 0.0021917 | 0.0052082 | 0.032227 | 0.00088875 | 0.00085443 | -0.0014356 | -0.0017197 | -0.0072889 | -0.0014697 | -49.379 | 69.7037 | -53.2425 | 69.3878 | -52.3819 | -53.009 | -52.4689 | -51.7364 | 69.7311 | -53.1647 | -52.8305 | -52.9999 | -53.2288 | -52.9221 | -0.10071 | -0.009156 | -0.32501 | 0.75989 | 0.67291 | 0.13275 | 0.77362 | 0.23346 | -0.022888 | 0.01831 | -122.5433 | 0.14191 | 0.21973 | -0.086975 | 0.24262 | -0.064087 | 0.8606 | 122.6303 | 0.16479 | 0.33417 | 122.9462 | 122.8958 | 122.8455 | 122.8729 | -122.9553 | -122.8775 | 122.5296 | 0.31128 | 3.7628 | 1.4053
3423.1719 | 122.9324 | -53.1418 | 69.6854 | -0.052948 | 0.00019446 | 0.063948 | 0.068191 | 0.00080117 | 0.0013373 | 0.0047808 | 0.03833 | 0.0017431 | 0.0049134 | -0.001222 | -0.0034287 | -0.0064343 | -0.0018971 | -49.4888 | 69.7266 | -53.2288 | 69.3924 | -52.3956 | -53.0136 | -52.4506 | -51.741 | 69.7266 | -53.183 | -52.8397 | -52.9999 | -53.2471 | -52.9449 | -0.086975 | 0.041198 | -0.29297 | 0.74616 | 0.69122 | 0.12817 | 0.7782 | 0.21515 | -0.041198 | 0.041198 | -122.525 | 0.14191 | 0.19684 | -0.10529 | 0.23804 | -0.064087 | 0.83313 | 122.6212 | 0.1831 | 0.34332 | 122.9553 | 122.9095 | 122.8683 | 122.8683 | -122.9141 | -122.8683 | 122.5342 | 0.30212 | 3.653 | 1.4008
3424.1719 | 122.9462 | -53.1464 | 69.7083 | -0.045319 | -0.00087374 | 0.061812 | 0.067977 | 0.0035782 | 0.0013373 | 0.0039264 | 0.02002 | 0.0028113 | -0.00042717 | 5.9824e-05 | -0.0032151 | -0.0049389 | 0.00023934 | -49.3652 | 69.6991 | -53.2471 | 69.4153 | -52.3911 | -52.9861 | -52.4551 | -51.709 | 69.7449 | -53.1464 | -52.8122 | -52.9907 | -53.2288 | -52.9175 | -0.10071 | -0.009155 | -0.29297 | 0.75531 | 0.69122 | 0.16022 | 0.79193 | 0.26093 | 0 | 0.036621 | -122.5204 | 0.15564 | 0.22888 | -0.082398 | 0.22888 | -0.082398 | 0.85602 | 122.6624 | 0.15564 | 0.33417 | 122.9462 | 122.8912 | 122.8455 | 122.8912 | -122.9553 | -122.8546 | 122.5616 | 0.33417 | 3.7811 | 1.4374
3425.1719 | 122.9553 | -53.1235 | 69.7037 | -0.060578 | 0.00019446 | 0.059889 | 0.067123 | -0.001976 | 0.0030463 | 0.0052082 | 0.03833 | 0.0021703 | 0.0012818 | 0.00070062 | -0.0042831 | -0.0066479 | -0.00061526 | -49.379 | 69.6991 | -53.2104 | 69.4061 | -52.3819 | -52.9907 | -52.4597 | -51.7364 | 69.7403 | -53.1647 | -52.8168 | -52.9953 | -53.2333 | -52.9358 | -0.086975 | -0.004577 | -0.29755 | 0.74158 | 0.66376 | 0.13275 | 0.75073 | 0.21973 | -0.041199 | 0.036621 | -122.5204 | 0.12817 | 0.18768 | -0.10986 | 0.22888 | -0.068664 | 0.82855 | 122.6166 | 0.16937 | 0.3479 | 122.9095 | 122.905 | 122.8226 | 122.8638 | -122.9141 | -122.8683 | 122.5296 | 0.3067 | 3.7445 | 1.387
3426.1719 | 122.9233 | -53.1464 | 69.7311 | -0.075836 | 0.00062166 | 0.059248 | 0.067977 | 0.00251 | 0.0013373 | 0.0077716 | 0.047485 | -0.00017945 | 0.00064083 | -0.0027174 | -0.0012925 | -0.0047253 | 0.00023934 | -49.3286 | 69.7037 | -53.1921 | 69.4336 | -52.3132 | -52.9633 | -52.4094 | -51.6678 | 69.7174 | -53.1464 | -52.7985 | -52.9724 | -53.2104 | -52.9358 | -0.045777 | -0.027466 | -0.29755 | 0.83313 | 0.737 | 0.18311 | 0.78278 | 0.22888 | 0 | -0.013733 | -122.5296 | 0.17395 | 0.21057 | -0.064087 | 0.21057 | -0.064087 | 0.87891 | 122.6257 | 0.17395 | 0.3479 | 122.8958 | 122.8638 | 122.85 | 122.8638 | -122.9233 | -122.8775 | 122.58 | 0.3479 | 3.8177 | 1.4786
3427.1719 | 122.9462 | -53.1097 | 69.7174 | -0.068207 | -0.00087374 | 0.060957 | 0.069259 | 0.00016017 | 0.00069649 | 0.0052082 | 0.053589 | -0.0014613 | 0.001068 | -0.0010084 | -0.0021469 | -0.0057935 | 0.00066654 | -49.2828 | 69.7128 | -53.1876 | 69.4931 | -52.272 | -52.9175 | -52.3636 | -51.6266 | 69.7174 | -53.1418 | -52.7802 | -52.9404 | -53.183 | -52.9312 | -0.07782 | -0.004577 | -0.2243 | 0.83771 | 0.74616 | 0.19226 | 0.82398 | 0.27008 | -0.032044 | 0 | -122.4976 | 0.16937 | 0.17853 | -0.073242 | 0.21057 | -0.041198 | 0.91553 | 122.6807 | 0.20142 | 0.36163 | 122.9004 | 122.8592 | 122.8226 | 122.8271 | -122.905 | -122.8592 | 122.6028 | 0.32959 | 3.8269 | 1.4832
3428.1719 | 122.9416 | -53.1143 | 69.7403 | -0.037689 | -1.9142e-05 | 0.062025 | 0.069259 | 0.0035782 | 0.0036871 | 0.0037128 | 0.032227 | 0.0025975 | 0.00064083 | -0.001222 | -0.0042831 | -0.0064343 | -0.0027515 | -49.3149 | 69.7083 | -53.1967 | 69.4565 | -52.3041 | -52.9724 | -52.4139 | -51.6541 | 69.754 | -53.1555 | -52.8076 | -52.9633 | -53.1967 | -52.9037 | -0.082397 | -0.032043 | -0.28381 | 0.81024 | 0.70038 | 0.14191 | 0.78278 | 0.2243 | -0.041199 | 0.013733 | -122.5479 | 0.15106 | 0.21057 | -0.082397 | 0.25177 | -0.041198 | 0.89264 | 122.6532 | 0.19226 | 0.3479 | 122.905 | 122.9095 | 122.8226 | 122.8683 | -122.937 | -122.8958 | 122.5708 | 0.3067 | 3.7994 | 1.4603
3429.1719 | 122.9507 | -53.0823 | 69.754 | -0.052948 | 0.0010489 | 0.061385 | 0.068404 | -0.0021896 | 0.00048269 | 0.0049946 | 0.050537 | 0.00024775 | -0.00021357 | -0.0035718 | -0.0030013 | -0.0051527 | -0.00061526 | -49.2691 | 69.6991 | -53.183 | 69.4794 | -52.2812 | -52.9129 | -52.3682 | -51.6174 | 69.7449 | -53.1097 | -52.7985 | -52.9129 | -53.1784 | -52.9175 | -0.10071 | -0.054931 | -0.27466 | 0.80109 | 0.71411 | 0.16937 | 0.81482 | 0.27008 | -0.027466 | -0.009155 | -122.5525 | 0.16937 | 0.1648 | -0.096131 | 0.19226 | -0.068665 | 0.90179 | 122.6624 | 0.19684 | 0.31128 | 122.8821 | 122.8546 | 122.7814 | 122.8271 | -122.937 | -122.8638 | 122.5616 | 0.28381 | 3.8132 | 1.4648
3430.1719 | 122.9828 | -53.096 | 69.7357 | -0.060578 | 0.0014761 | 0.061171 | 0.066695 | -0.004753 | 0.0030463 | 0.0043536 | 0.029175 | 0.00046135 | 0.0012818 | -0.00464 | -0.0032151 | -0.0062207 | -0.0048877 | -49.2691 | 69.6808 | -53.1692 | 69.5251 | -52.2583 | -52.89 | -52.327 | -51.5762 | 69.7266 | -53.1235 | -52.7573 | -52.9129 | -53.1281 | -52.8625 | -0.073242 | -0.054932 | -0.21057 | 0.83771 | 0.76904 | 0.20599 | 0.84228 | 0.27923 | -0.027466 | -0.009156 | -122.493 | 0.1831 | 0.23346 | -0.032044 | 0.26093 | -0.004578 | 0.91095 | 122.6944 | 0.21057 | 0.36621 | 122.85 | 122.85 | 122.7768 | 122.8226 | -122.905 | -122.8592 | 122.6212 | 0.33874 | 3.8269 | 1.5198
3431.1719 | 123.0103 | -53.0823 | 69.7037 | -0.045319 | 0.00019446 | 0.061385 | 0.066268 | -5.343e-05 | 0.0017645 | 0.0047808 | 0.032227 | 0.00067495 | 0.001709 | -0.00229 | -0.0038559 | -0.0051527 | -0.0018971 | -49.2554 | 69.6945 | -53.1738 | 69.5526 | -52.2125 | -52.8671 | -52.3087 | -51.5579 | 69.7311 | -53.1143 | -52.7115 | -52.8671 | -53.1052 | -52.8259 | -0.091553 | -0.009155 | -0.15106 | 0.86975 | 0.77362 | 0.21515 | 0.86517 | 0.3067 | -0.032044 | 0.027466 | -122.4152 | 0.21515 | 0.25635 | -0.022889 | 0.28839 | 0.009155 | 0.9613 | 122.7264 | 0.24719 | 0.40283 | 122.8683 | 122.8455 | 122.7768 | 122.8134 | -122.8775 | -122.818 | 122.6349 | 0.37079 | 3.8269 | 1.5244
3432.1719 | 122.9691 | -53.0869 | 69.7586 | -0.1445 | -0.0010873 | 0.060957 | 0.067336 | -0.00026703 | 0.0017645 | 0.0034992 | -0.0013428 | -0.0014613 | 0.00021363 | 0.002196 | -0.0034287 | -0.0049389 | 0.00045294 | -49.2554 | 69.7357 | -53.1692 | 69.5389 | -52.24 | -52.8854 | -52.3544 | -51.6037 | 69.7632 | -53.1235 | -52.7573 | -52.9221 | -53.1784 | -52.89 | -0.082397 | -0.022888 | -0.21973 | 0.84686 | 0.73242 | 0.20142 | 0.81482 | 0.28381 | -0.036621 | 0.004578 | -122.5159 | 0.16479 | 0.19684 | -0.091553 | 0.23346 | -0.054932 | 0.92926 | 122.7081 | 0.20142 | 0.36621 | 122.905 | 122.8867 | 122.8226 | 122.85 | -122.9279 | -122.8821 | 122.6257 | 0.32959 | 3.8315 | 1.4832
3433.1719 | 123.0423 | -53.0823 | 69.6945 | -0.03006 | 0.00083526 | 0.06053 | 0.066695 | 0.0046464 | 0.0036871 | 0.0047808 | 0.044434 | -0.00060665 | 0.0019226 | -0.0035718 | -0.0017197 | -0.0062207 | -0.0010425 | -49.2508 | 69.6762 | -53.1464 | 69.5206 | -52.1255 | -52.9266 | -52.3499 | -51.5396 | 69.7037 | -53.0914 | -52.6703 | -52.8488 | -53.0731 | -52.803 | -0.064087 | -0.018311 | -0.17395 | 0.95673 | 0.73242 | 0.15564 | 0.79651 | 0.21973 | -0.009156 | 0.009155 | -122.3648 | 0.23346 | 0.27923 | 0.009155 | 0.28839 | 0.018311 | 1.0208 | 122.6669 | 0.24262 | 0.42114 | 122.8226 | 122.7951 | 122.7585 | 122.7859 | -122.8409 | -122.7859 | 122.6028 | 0.41199 | 3.8315 | 1.5427
3434.1719 | 123.0515 | -53.0685 | 69.7174 | -0.014801 | -0.0017281 | 0.06053 | 0.068404 | 0.0029374 | 0.00069649 | 0.00414 | 0.02002 | 0.0011023 | 0.0019226 | 0.0017688 | -0.0019333 | -0.0064343 | -0.0046741 | -49.2279 | 69.6762 | -53.1372 | 69.5892 | -52.153 | -52.8259 | -52.2675 | -51.5076 | 69.7586 | -53.0869 | -52.6291 | -52.8717 | -53.0685 | -52.7847 | -0.068665 | -0.041199 | -0.12817 | 0.91553 | 0.80109 | 0.24261 | 0.86975 | 0.31128 | -0.018311 | 0.041199 | -122.3465 | 0.19684 | 0.28381 | 0 | 0.30212 | 0.018311 | 0.98419 | 122.7264 | 0.21515 | 0.45776 | 122.8134 | 122.8455 | 122.7448 | 122.8271 | -122.8546 | -122.8043 | 122.6578 | 0.43945 | 3.8406 | 1.561
3435.1719 | 122.9416 | -53.0823 | 69.7861 | -0.060578 | 0.00083526 | 0.062239 | 0.069259 | 0.00058737 | 0.0015509 | 0.0020038 | -0.037964 | 0.00088875 | 0.001068 | 0.002196 | -0.0038559 | -0.0040845 | 0.0053661 | -49.2874 | 69.7449 | -53.1601 | 69.4748 | -52.3224 | -52.9404 | -52.4094 | -51.6495 | 69.7952 | -53.1464 | -52.7527 | -52.9175 | -53.1967 | -52.8763 | -0.07782 | -0.041199 | -0.31128 | 0.75989 | 0.67291 | 0.14191 | 0.75073 | 0.21973 | -0.064087 | 0.009155 | -122.5388 | 0.1648 | 0.20599 | -0.11444 | 0.27008 | -0.050354 | 0.83771 | 122.6349 | 0.22888 | 0.39368 | 122.905 | 122.9416 | 122.8271 | 122.8775 | -122.9462 | -122.9324 | 122.5571 | 0.32959 | 3.7949 | 1.4328
3436.1719 | 123.0423 | -53.0823 | 69.7403 | -0.13687 | 0.0010489 | 0.061385 | 0.069259 | -0.00048063 | 0.00069649 | 0.0034992 | 0.047485 | -0.00060665 | 0.0012818 | -0.0067762 | -0.0027877 | -0.0070753 | -0.0018971 | -49.2142 | 69.7311 | -53.0914 | 69.6304 | -52.1851 | -52.9129 | -52.2812 | -51.4984 | 69.7403 | -53.0914 | -52.6566 | -52.7939 | -53.0457 | -52.7802 | -0.009156 | -0.009155 | -0.10986 | 0.89722 | 0.80109 | 0.16937 | 0.81024 | 0.17853 | -0.009156 | 0 | -122.3969 | 0.28839 | 0.30212 | 0.036621 | 0.31128 | 0.045777 | 0.90637 | 122.7219 | 0.29755 | 0.43488 | 122.8226 | 122.8317 | 122.8134 | 122.8226 | -122.8317 | -122.8317 | 122.7127 | 0.42572 | 3.8681 | 1.5839
3437.1719 | 123.056 | -53.0365 | 69.7266 | -0.10635 | -0.0025827 | 0.06053 | 0.066695 | 0.0029374 | 0.00048269 | 0.0045672 | 0.20312 | -0.0012477 | 0.00042723 | 0.00027342 | -0.0019333 | -0.0064343 | -0.0018971 | -49.1959 | 69.6899 | -53.1418 | 69.6259 | -52.1393 | -52.8168 | -52.2675 | -51.4206 | 69.809 | -53.064 | -52.6611 | -52.7939 | -53.064 | -52.7939 | -0.10529 | -0.036621 | -0.10071 | 0.89722 | 0.76904 | 0.21973 | 0.87433 | 0.32501 | -0.027466 | 0.082398 | -122.3877 | 0.24262 | 0.24262 | -0.027466 | 0.27008 | 0 | 1.0025 | 122.7676 | 0.27008 | 0.40283 | 122.8317 | 122.8729 | 122.7264 | 122.8455 | -122.8683 | -122.7905 | 122.6624 | 0.37537 | 3.8406 | 1.6159
3438.1719 | 123.0423 | -53.0319 | 69.7632 | -0.11398 | -0.00087374 | 0.061598 | 0.067763 | -0.0045394 | 0.0021917 | 0.0020038 | -0.01355 | 3.4148e-05 | -0.00021357 | 0.0049732 | -0.0030013 | -0.0049389 | -0.00061526 | -49.205 | 69.7174 | -53.1281 | 69.603 | -52.1851 | -52.8397 | -52.2812 | -51.5076 | 69.754 | -53.0823 | -52.6611 | -52.8076 | -53.0594 | -52.7847 | -0.096131 | -0.045777 | -0.16022 | 0.84686 | 0.75073 | 0.19226 | 0.84686 | 0.28839 | -0.050354 | -0.009156 | -122.4243 | 0.2243 | 0.24719 | -0.027466 | 0.29755 | 0.022888 | 0.94299 | 122.731 | 0.27466 | 0.42114 | 122.8455 | 122.8363 | 122.7493 | 122.7859 | -122.8912 | -122.8455 | 122.6349 | 0.37079 | 3.8269 | 1.5244
3439.1719 | 123.0469 | -53.0273 | 69.7357 | 0.038605 | 0.0016899 | 0.062453 | 0.067123 | -0.0011214 | 0.0013373 | 0.0067036 | 0.035278 | 3.4148e-05 | -0.00064077 | -0.007417 | -0.0036423 | -0.0057935 | -0.0031787 | -49.4247 | 69.7266 | -53.1326 | 69.6121 | -52.1713 | -52.8351 | -52.2537 | -51.4893 | 69.754 | -53.1006 | -52.6382 | -52.8168 | -53.0548 | -52.7802 | -0.10529 | -0.009156 | -0.1236 | 0.85602 | 0.77362 | 0.19226 | 0.87891 | 0.29755 | -0.073242 | 0.01831 | -122.374 | 0.21057 | 0.24719 | -0.027466 | 0.32044 | 0.045776 | 0.9613 | 122.7448 | 0.28381 | 0.46234 | 122.8592 | 122.8546 | 122.7539 | 122.7814 | -122.8683 | -122.8363 | 122.6395 | 0.3891 | 3.6026 | 1.5381
3440.1719 | 122.9324 | -53.1006 | 69.7586 | -0.060578 | -0.0021555 | 0.062239 | 0.071609 | -0.0024032 | 0.0026191 | 0.0073444 | -0.086792 | 0.00088875 | 0.00042723 | 0.0049732 | -0.0034287 | -0.0042981 | 0.00023934 | -49.2691 | 69.7495 | -53.183 | 69.4794 | -52.3132 | -52.9816 | -52.4231 | -51.6312 | 69.7678 | -53.1189 | -52.7435 | -52.9587 | -53.2196 | -52.8854 | -0.082397 | -0.009155 | -0.27924 | 0.78735 | 0.67749 | 0.11902 | 0.75989 | 0.20142 | -0.01831 | 0.009155 | -122.5021 | 0.14191 | 0.21515 | -0.11902 | 0.23346 | -0.10071 | 0.86975 | 122.6624 | 0.16022 | 0.37537 | 122.9324 | 122.8867 | 122.85 | 122.8683 | -122.9416 | -122.8775 | 122.58 | 0.35706 | 3.8315 | 1.4694
3441.1719 | 123.0377 | -53.0228 | 69.6945 | -0.11398 | 0.00040806 | 0.059889 | 0.068618 | -0.00090783 | 0.0013373 | 0.003072 | 0.010864 | -0.00082025 | 0.001068 | 0.0034778 | -0.0023605 | -0.0045117 | -0.0044605 | -49.2142 | 69.722 | -53.1143 | 69.5663 | -52.1896 | -52.8259 | -52.2766 | -51.503 | 69.7723 | -53.0914 | -52.6382 | -52.7847 | -53.0182 | -52.7527 | -0.091553 | 0.027466 | -0.12817 | 0.83313 | 0.74615 | 0.19684 | 0.83771 | 0.28839 | -0.068665 | 0.07782 | -122.3328 | 0.23804 | 0.27008 | 0.004578 | 0.33875 | 0.073243 | 0.92468 | 122.6807 | 0.3067 | 0.45319 | 122.8363 | 122.8638 | 122.7448 | 122.7951 | -122.8088 | -122.7859 | 122.5891 | 0.38452 | 3.8086 | 1.5198
3442.1719 | 123.0148 | -53.0182 | 69.7266 | -0.075836 | 0.00019446 | 0.060957 | 0.067763 | -0.0034714 | 0.00069649 | 0.0043536 | 0.029175 | 3.4148e-05 | 0.0012818 | -0.00036738 | -0.0019333 | -0.0070753 | 0.0010937 | -49.1821 | 69.7266 | -53.1235 | 69.6121 | -52.1301 | -52.803 | -52.24 | -51.4297 | 69.7678 | -53.0502 | -52.6245 | -52.8076 | -52.7206 | -52.5101 | -0.10529 | 0 | -0.11444 | 0.88806 | 0.7782 | 0.21515 | 0.88348 | 0.32043 | -0.032044 | 0.041199 | -122.3511 | 0.21057 | 0.50812 | 0.29755 | 0.54016 | 0.32959 | 0.99335 | 122.7356 | 0.24262 | 0.42572 | 122.85 | 122.818 | 122.7448 | 122.7859 | -122.85 | -122.7768 | 122.6303 | 0.39368 | 3.8361 | 1.5884
3443.1719 | 123.0698 | -53.009 | 69.7311 | -0.11398 | -0.00023294 | 0.060957 | 0.068191 | -0.00069423 | 0.0015509 | 0.0047808 | 0.044434 | -0.00017945 | -0.00064077 | 0.0013416 | -0.0057785 | -0.0066479 | -0.0023243 | -49.1913 | 69.7586 | -53.1006 | 69.6304 | -52.1072 | -52.8076 | -52.24 | -51.4343 | 69.7952 | -53.0594 | -52.5925 | -52.7618 | -52.9861 | -52.7344 | -0.091553 | 0.027466 | -0.10071 | 0.90179 | 0.76904 | 0.20142 | 0.8606 | 0.29297 | -0.050354 | 0.064087 | -122.3236 | 0.24719 | 0.27466 | 0.022888 | 0.32501 | 0.073242 | 0.99335 | 122.731 | 0.29755 | 0.46692 | 122.8592 | 122.8546 | 122.7676 | 122.8043 | -122.8317 | -122.7905 | 122.6395 | 0.41657 | 3.8177 | 1.5747
3444.1719 | 123.056 | -52.9907 | 69.7311 | -0.11398 | 0.0010489 | 0.059889 | 0.067763 | -0.0011214 | 0.0019781 | 0.0056354 | 0.026123 | 0.0017431 | 0.001709 | -0.0025036 | -0.0015061 | -0.0064343 | -0.0014697 | -49.1867 | 69.7586 | -53.0869 | 69.6121 | -52.1622 | -52.8122 | -52.2537 | -51.4389 | 69.7998 | -53.0685 | -52.597 | -52.7527 | -53.009 | -52.7481 | -0.09613 | 0.027466 | -0.11902 | 0.82855 | 0.737 | 0.17853 | 0.83313 | 0.27466 | -0.077819 | 0.068665 | -122.3282 | 0.23804 | 0.24262 | -0.01831 | 0.32043 | 0.059509 | 0.92468 | 122.699 | 0.31586 | 0.4715 | 122.8455 | 122.8683 | 122.7493 | 122.7905 | -122.818 | -122.7997 | 122.6028 | 0.39368 | 3.804 | 1.5518
3445.1719 | 122.9462 | -53.0548 | 69.809 | -0.037689 | -0.00044654 | 0.060957 | 0.070968 | -0.00048063 | 0.0019781 | 0.0064898 | -0.041016 | 0.0019567 | 0.0019226 | 0.0045458 | -0.0023605 | -0.0047253 | -0.00040166 | -49.2004 | 69.8273 | -53.1418 | 69.5389 | -52.272 | -52.9083 | -52.3544 | -51.5854 | 69.8364 | -53.0777 | -52.6886 | -52.8625 | -53.1189 | -52.8122 | -0.086975 | 0.018311 | -0.27008 | 0.78278 | 0.70038 | 0.14649 | 0.78735 | 0.23346 | -0.022888 | 0.027466 | -122.4976 | 0.19226 | 0.24262 | -0.064086 | 0.2655 | -0.041198 | 0.86975 | 122.6807 | 0.21515 | 0.3891 | 122.9691 | 122.9141 | 122.8821 | 122.8912 | -122.9507 | -122.8867 | 122.5937 | 0.36621 | 3.8544 | 1.4694
3446.1719 | 122.9965 | -53.0182 | 69.754 | -0.075836 | 0.0012625 | 0.059676 | 0.069686 | 0.00080117 | 0.0026191 | 0.0039264 | 0.013916 | -0.00039305 | 0.00085443 | -0.0020764 | -0.0019333 | -0.0055799 | 0.0021619 | -49.1364 | 69.7449 | -53.096 | 69.6304 | -52.0935 | -52.7893 | -52.2079 | -51.3886 | 69.7998 | -53.0548 | -52.6474 | -52.4734 | -52.9404 | -52.8717 | -0.07782 | -0.009155 | -0.1236 | 0.92468 | 0.81024 | 0.22888 | 0.88806 | 0.3067 | -0.036622 | 0.045777 | -122.4014 | 0.54474 | 0.14648 | 0.077819 | 0.18311 | 0.11444 | 1.0025 | 122.7264 | 0.58136 | 0.40741 | 122.8409 | 122.8546 | 122.7631 | 122.818 | -122.85 | -122.8088 | 122.6486 | 0.37079 | 3.8818 | 1.6296
3447.1719 | 123.0423 | -53.0045 | 69.7632 | -0.091095 | 0.00062166 | 0.061598 | 0.067123 | -0.00069423 | 0.0032599 | 0.0067036 | 0.029175 | 0.00067495 | 0.00085443 | -0.0059216 | -0.0010787 | -0.0049389 | 0.00045294 | -49.1913 | 69.7403 | -53.1006 | 69.5892 | -52.1851 | -52.8442 | -52.2675 | -51.4893 | 69.8044 | -53.064 | -52.6062 | -52.7756 | -53.0228 | -52.739 | -0.09613 | -0.022889 | -0.17395 | 0.8194 | 0.737 | 0.16022 | 0.83313 | 0.25635 | -0.059509 | 0.041198 | -122.3694 | 0.22888 | 0.2655 | -0.01831 | 0.32501 | 0.041199 | 0.91553 | 122.6898 | 0.28839 | 0.45776 | 122.8409 | 122.8683 | 122.7448 | 122.8088 | -122.8638 | -122.8271 | 122.5937 | 0.39825 | 3.8132 | 1.5152
3448.1719 | 123.0469 | -53.0045 | 69.7952 | -0.12924 | 0.00040806 | 0.060744 | 0.068191 | 0.005928 | 5.5488e-05 | 0.0062762 | 0.0047608 | -0.0016749 | 0.0012818 | 0.0013416 | -0.0030013 | -0.0062207 | -0.0038197 | -49.1821 | 69.7769 | -53.1052 | 69.5892 | -52.1942 | -52.8442 | -52.2629 | -51.4893 | 69.7861 | -53.0548 | -52.6154 | -52.7802 | -53.0365 | -52.7527 | -0.10071 | -0.01831 | -0.20599 | 0.81024 | 0.74158 | 0.16022 | 0.84229 | 0.26093 | -0.050354 | -0.009155 | -122.4106 | 0.22431 | 0.25177 | -0.032043 | 0.30212 | 0.018311 | 0.91095 | 122.6944 | 0.27466 | 0.43945 | 122.8821 | 122.8409 | 122.7814 | 122.7905 | -122.9004 | -122.85 | 122.5937 | 0.3891 | 3.8223 | 1.5152
3449.1719 | 123.056 | -53.0136 | 69.7815 | -0.12161 | -1.9142e-05 | 0.063094 | 0.068191 | -0.0011214 | 0.00069649 | 0.0022174 | 0.013916 | 0.00046135 | 2.8e-08 | 0.001128 | -0.0034287 | -0.0085705 | 0.0015209 | -49.1501 | 69.7632 | -53.1006 | 69.6259 | -52.1622 | -52.8305 | -52.24 | -51.4709 | 69.7723 | -53.0319 | -52.5742 | -52.7527 | -53.0045 | -52.739 | -0.086975 | -0.01831 | -0.15564 | 0.85144 | 0.77362 | 0.18311 | 0.8606 | 0.27008 | -0.01831 | -0.009155 | -122.3557 | 0.26093 | 0.27466 | 0.009155 | 0.29297 | 0.027465 | 0.93842 | 122.7264 | 0.27923 | 0.45776 | 122.8638 | 122.8043 | 122.7768 | 122.7859 | -122.8821 | -122.8134 | 122.6395 | 0.43945 | 3.8635 | 1.5427
3450.1719 | 123.0423 | -52.9953 | 69.7586 | -0.060578 | -0.00066014 | 0.060957 | 0.068618 | -0.0038986 | 0.0011237 | 0.0052082 | -0.0013428 | 3.4148e-05 | 2.8e-08 | 0.0019824 | -0.0044967 | -0.0034437 | 0.0015209 | -49.1867 | 69.7861 | -53.0731 | 69.6213 | -52.1713 | -52.8168 | -52.2629 | -51.4664 | 69.8181 | -53.0319 | -52.5833 | -52.7573 | -52.9907 | -52.7206 | -0.07782 | 0.027466 | -0.13733 | 0.82397 | 0.73242 | 0.17853 | 0.81024 | 0.25635 | -0.036621 | 0.059509 | -122.3419 | 0.23804 | 0.27466 | 0.004577 | 0.31128 | 0.041198 | 0.90179 | 122.6944 | 0.27466 | 0.44861 | 122.8592 | 122.85 | 122.7814 | 122.8134 | -122.8317 | -122.7905 | 122.6166 | 0.41199 | 3.8086 | 1.5289
3451.1719 | 123.0469 | -52.977 | 69.7815 | -0.12161 | -0.00044654 | 0.060316 | 0.068404 | -0.0011214 | 0.0015509 | 0.0043536 | 0.023071 | 0.00088875 | 0.0023498 | -0.00015378 | -0.0027877 | -0.0062207 | 0.0015209 | -49.1776 | 69.7861 | -53.0869 | 69.6259 | -52.1576 | -52.8305 | -52.2583 | -51.4801 | 69.8044 | -53.0502 | -52.597 | -52.7618 | -53.0228 | -52.7435 | -0.10986 | 0.004578 | -0.15564 | 0.8194 | 0.71869 | 0.14648 | 0.82855 | 0.25635 | -0.073242 | 0.022888 | -122.3785 | 0.21515 | 0.23346 | -0.045776 | 0.3067 | 0.027466 | 0.92926 | 122.7127 | 0.28839 | 0.45319 | 122.8729 | 122.8546 | 122.7631 | 122.7814 | -122.8683 | -122.8317 | 122.6028 | 0.37994 | 3.7994 | 1.4969
3452.1719 | 123.0743 | -52.9816 | 69.7632 | -0.068207 | 0.00019446 | 0.062025 | 0.068191 | -0.0026168 | 0.0011237 | 0.0071308 | 0.0078126 | 0.0021703 | -0.0014954 | -0.0033582 | -0.0049241 | -0.0042981 | 0.00045294 | -49.1547 | 69.7769 | -53.0914 | 69.6213 | -52.1393 | -52.7985 | -52.2217 | -51.4297 | 69.8273 | -53.0228 | -52.565 | -52.7435 | -52.977 | -52.7069 | -0.10986 | 0.013733 | -0.14191 | 0.84228 | 0.75989 | 0.1831 | 0.86975 | 0.29297 | -0.041199 | 0.064087 | -122.3282 | 0.23804 | 0.27466 | 0.004577 | 0.31586 | 0.045776 | 0.95215 | 122.7127 | 0.27924 | 0.45776 | 122.8683 | 122.85 | 122.7585 | 122.8088 | -122.8546 | -122.7859 | 122.6028 | 0.41656 | 3.8269 | 1.5518
3453.1719 | 123.056 | -52.9816 | 69.7861 | -0.083466 | 0.00040806 | 0.060103 | 0.068191 | 0.00058737 | 5.5488e-05 | 0.0045672 | 0.001709 | 0.00024775 | 0.00042723 | -0.0018628 | -0.0019333 | -0.0060071 | -0.0027515 | -49.1455 | 69.7861 | -53.0731 | 69.6304 | -52.1301 | -52.8122 | -52.2217 | -51.4618 | 69.8181 | -53.0273 | -52.5742 | -52.7344 | -52.9724 | -52.7298 | -0.091553 | 0 | -0.15564 | 0.85144 | 0.75989 | 0.16937 | 0.85144 | 0.26093 | -0.045777 | 0.032043 | -122.3602 | 0.24719 | 0.25177 | 0.009155 | 0.29755 | 0.054932 | 0.94299 | 122.7036 | 0.29297 | 0.45319 | 122.8592 | 122.8455 | 122.7676 | 122.7997 | -122.8592 | -122.8134 | 122.612 | 0.40741 | 3.8361 | 1.5198
3454.1719 | 123.0194 | -53.0228 | 69.7815 | -0.12161 | 0.0019035 | 0.060744 | 0.068832 | 0.0063554 | -0.00015811 | 0.0049946 | -0.016602 | -0.0031703 | 0.003418 | -0.00229 | -0.0025741 | -0.0055799 | 0.0028027 | -49.1638 | 69.7861 | -53.1006 | 69.603 | -52.1942 | -52.8488 | -52.272 | -51.384 | 69.7998 | -53.0045 | -52.597 | -52.7893 | -53.0457 | -52.7802 | -0.07782 | 0.004578 | -0.17853 | 0.82855 | 0.75073 | 0.17395 | 0.82855 | 0.25177 | 0.01831 | 0.018311 | -122.3785 | 0.23346 | 0.24262 | -0.022888 | 0.22431 | -0.041198 | 0.90637 | 122.7036 | 0.21515 | 0.40741 | 122.8867 | 122.8043 | 122.8088 | 122.8226 | -122.8821 | -122.7859 | 122.6257 | 0.42572 | 3.8589 | 1.6388
3455.1719 | 123.0835 | -52.9861 | 69.8181 | -0.11398 | 0.0021171 | 0.061171 | 0.069259 | -0.00069423 | 0.0034735 | 0.0037128 | -0.0013428 | 0.0017431 | 0.00064083 | 0.001128 | -0.0017197 | -0.0040845 | 2.554e-05 | -49.1638 | 69.7906 | -53.0777 | 69.6121 | -52.1759 | -52.8625 | -52.2537 | -51.503 | 69.8364 | -53.0319 | -52.6016 | -52.7847 | -53.0365 | -52.7847 | -0.091553 | -0.027466 | -0.20599 | 0.81024 | 0.73242 | 0.1236 | 0.82397 | 0.21515 | -0.045776 | 0.018311 | -122.4197 | 0.20142 | 0.20142 | -0.050354 | 0.24719 | -0.004578 | 0.90179 | 122.6898 | 0.24719 | 0.4303 | 122.8683 | 122.8683 | 122.7768 | 122.8226 | -122.8958 | -122.85 | 122.5983 | 0.38452 | 3.8223 | 1.4832
3456.1719 | 123.0377 | -52.9724 | 69.809 | -0.091095 | -0.0017281 | 0.059248 | 0.068618 | -0.0038986 | 0.00069649 | 0.0054218 | -0.01355 | 0.00088875 | -0.00021357 | 5.9824e-05 | -0.0019333 | -0.0060071 | 0.0017345 | -49.1547 | 69.8181 | -53.0823 | 69.548 | -52.2217 | -52.8442 | -52.2858 | -51.5213 | 69.8227 | -53.0365 | -52.597 | -52.7847 | -53.0365 | -52.7435 | -0.10986 | 0.009155 | -0.26093 | 0.75073 | 0.68664 | 0.12817 | 0.79651 | 0.23804 | -0.064087 | 0.013733 | -122.406 | 0.18768 | 0.22888 | -0.064087 | 0.29297 | 0 | 0.8606 | 122.6303 | 0.25177 | 0.43945 | 122.9004 | 122.8592 | 122.7905 | 122.7951 | -122.8912 | -122.8455 | 122.5204 | 0.37537 | 3.8177 | 1.4511
3457.1719 | 122.9965 | -52.9953 | 69.7998 | -0.014801 | 0.00062166 | 0.062025 | 0.066909 | 0.00080117 | 0.0021917 | 0.0052082 | -0.028809 | -0.00039305 | 0.00064083 | -0.0035718 | -0.0042831 | -0.0070753 | 0.00045294 | -49.1547 | 69.7815 | -53.064 | 69.6167 | -52.1759 | -52.8442 | -52.2446 | -51.4893 | 69.8318 | -53.0273 | -52.6337 | -52.803 | -53.0319 | -52.7573 | -0.068665 | -0.018311 | -0.18311 | 0.8194 | 0.75073 | 0.15106 | 0.8194 | 0.21973 | -0.032044 | 0.032043 | -122.4335 | 0.19226 | 0.23804 | -0.036621 | 0.27008 | -0.004577 | 0.88806 | 122.6807 | 0.2243 | 0.39368 | 122.8455 | 122.8592 | 122.7768 | 122.8271 | -122.8638 | -122.8271 | 122.612 | 0.36163 | 3.8406 | 1.506
3458.1719 | 122.9874 | -52.9816 | 69.7861 | -0.091095 | -1.9142e-05 | 0.063948 | 0.067977 | -0.0034714 | 0.0021917 | 0.003072 | -0.03186 | -0.0016749 | 0.00021363 | 0.0026232 | -0.0032151 | -0.0047253 | -0.0038197 | -49.1409 | 69.7906 | -53.0502 | 69.6075 | -52.1667 | -52.8534 | -52.2583 | -51.4709 | 69.8456 | -53.0182 | -52.5925 | -52.771 | -53.0273 | -52.7435 | -0.068665 | 0.004577 | -0.17853 | 0.81482 | 0.72327 | 0.12817 | 0.79193 | 0.19684 | -0.036621 | 0.059509 | -122.3785 | 0.21057 | 0.23804 | -0.045777 | 0.27466 | -0.009156 | 0.88348 | 122.6578 | 0.24719 | 0.42572 | 122.8409 | 122.8638 | 122.7722 | 122.8271 | -122.8363 | -122.8043 | 122.5891 | 0.3891 | 3.8406 | 1.5106
3459.1719 | 123.0011 | -52.9587 | 69.7998 | -0.083466 | 0.0012625 | 0.061385 | 0.067977 | -0.0021896 | 0.0034735 | 0.0045672 | -0.025757 | -0.00017945 | -0.00021357 | 0.0036914 | -0.0027877 | -0.0070753 | -0.0057423 | -49.1318 | 69.809 | -53.0502 | 69.6213 | -52.1393 | -52.8122 | -52.2583 | -51.4801 | 69.8502 | -53.0273 | -52.597 | -52.7985 | -53.0228 | -52.7252 | -0.091553 | 0.009155 | -0.17853 | 0.8194 | 0.70038 | 0.14648 | 0.79193 | 0.23804 | -0.068665 | 0.050354 | -122.3969 | 0.16022 | 0.23346 | -0.064087 | 0.30212 | 0.004578 | 0.91095 | 122.6715 | 0.22888 | 0.4303 | 122.8592 | 122.8775 | 122.7676 | 122.8088 | -122.85 | -122.8271 | 122.58 | 0.36163 | 3.8269 | 1.4786
3460.1719 | 123.0286 | -52.9816 | 69.8044 | -0.083466 | 0.0010489 | 0.06053 | 0.068191 | -0.00069423 | 0.0019781 | 0.0045672 | -0.016602 | 0.0032385 | 0.00064083 | -0.0054944 | -0.0030013 | -0.0062207 | -0.0031787 | -49.118 | 69.8273 | -53.0594 | 69.6259 | -52.1347 | -52.8397 | -52.2446 | -51.4847 | 69.8364 | -53.0273 | -52.5833 | -52.771 | -53.0182 | -52.739 | -0.07782 | 0.022889 | -0.17853 | 0.84686 | 0.737 | 0.14191 | 0.81482 | 0.21973 | -0.045777 | 0.032044 | -122.3877 | 0.21057 | 0.24261 | -0.036621 | 0.28839 | 0.009156 | 0.92468 | 122.6852 | 0.25635 | 0.44403 | 122.8867 | 122.8638 | 122.8088 | 122.818 | -122.8638 | -122.8317 | 122.6074 | 0.39825 | 3.8635 | 1.4969
3461.1719 | 123.0286 | -52.9541 | 69.8044 | -0.15213 | 0.00062166 | 0.061171 | 0.068618 | -0.0017624 | 0.0013373 | 0.0062762 | -0.047119 | 0.00024775 | 0.00085443 | 0.0024096 | -0.0027877 | -0.0038709 | 0.00088014 | -49.0631 | 69.7906 | -53.0502 | 69.6671 | -52.0981 | -52.7893 | -52.2263 | -51.4023 | 69.841 | -53.0136 | -52.5467 | -52.7481 | -53.0045 | -52.7023 | -0.09613 | -0.013733 | -0.13733 | 0.85602 | 0.72785 | 0.16479 | 0.82398 | 0.26093 | -0.059509 | 0.036621 | -122.3511 | 0.20599 | 0.25177 | -0.050354 | 0.31128 | 0.009155 | 0.95215 | 122.7173 | 0.2655 | 0.46692 | 122.8409 | 122.8546 | 122.7448 | 122.7951 | -122.8546 | -122.818 | 122.6212 | 0.40741 | 3.891 | 1.5518
3462.1719 | 123.0194 | -52.9724 | 69.8318 | -0.083466 | 0.0019035 | 0.062025 | 0.069045 | -0.0015488 | 0.0021917 | 0.0054218 | -0.041016 | 0.00024775 | 0.0012818 | 0.00070062 | -0.0036423 | -0.0051527 | 0.00066654 | -49.0677 | 69.7952 | -53.0777 | 69.6396 | -52.0844 | -52.7344 | -52.2034 | -51.416 | 69.8364 | -52.9907 | -52.5421 | -52.7344 | -52.9999 | -52.684 | -0.10529 | -0.036621 | -0.19226 | 0.88806 | 0.76904 | 0.23804 | 0.87433 | 0.34332 | -0.018311 | 0.004578 | -122.374 | 0.23804 | 0.28839 | -0.027466 | 0.3067 | -0.009155 | 0.99335 | 122.7173 | 0.25635 | 0.44861 | 122.8729 | 122.8271 | 122.7676 | 122.8088 | -122.9095 | -122.8226 | 122.612 | 0.4303 | 3.9047 | 1.5564
3463.1719 | 123.024 | -52.9495 | 69.7815 | -0.083466 | 0.0019035 | 0.061171 | 0.069472 | -0.0011214 | 0.0011237 | 0.003072 | -0.022705 | 0.00046135 | 0.001068 | 5.9824e-05 | -0.0015061 | -0.0038709 | -0.00061526 | -49.0814 | 69.809 | -53.0365 | 69.6671 | -52.0798 | -52.803 | -52.2217 | -51.4114 | 69.8593 | -52.9953 | -52.533 | -52.7298 | -52.9861 | -52.6932 | -0.086975 | 0.027466 | -0.11444 | 0.86975 | 0.72784 | 0.14648 | 0.81482 | 0.23346 | -0.045776 | 0.07782 | -122.3145 | 0.21973 | 0.25635 | -0.036621 | 0.30212 | 0.009155 | 0.95673 | 122.7036 | 0.2655 | 0.46234 | 122.8455 | 122.8546 | 122.7585 | 122.8088 | -122.818 | -122.7768 | 122.6166 | 0.41656 | 3.8681 | 1.5381
3464.1719 | 123.0331 | -52.9541 | 69.7906 | -0.091095 | 0.00062166 | 0.062666 | 0.069686 | 0.00058737 | 0.0032599 | 0.00414 | -0.050171 | -0.00017945 | -0.0010682 | 0.002196 | -0.0036423 | -0.0060071 | 0.0013073 | -49.0906 | 69.7998 | -53.0182 | 69.6625 | -52.0844 | -52.7664 | -52.1942 | -51.3886 | 69.8547 | -52.9861 | -52.5238 | -52.7298 | -52.977 | -52.6794 | -0.064086 | 0.009156 | -0.12817 | 0.86975 | 0.75989 | 0.18768 | 0.82397 | 0.25177 | -0.032043 | 0.064087 | -122.3145 | 0.22431 | 0.27466 | -0.022888 | 0.3067 | 0.009155 | 0.93384 | 122.6807 | 0.25635 | 0.46234 | 122.818 | 122.8409 | 122.7539 | 122.8088 | -122.8088 | -122.7768 | 122.6166 | 0.4303 | 3.8635 | 1.5656
3465.1719 | 123.056 | -52.9312 | 69.8181 | -0.11398 | 0.0023307 | 0.063307 | 0.070113 | 0.0012284 | 0.0039007 | 0.0052082 | -0.019653 | -0.0010339 | -0.00085457 | 0.0034778 | -0.0042831 | -0.0036573 | -0.00061526 | -49.0402 | 69.8044 | -53.0273 | 69.6899 | -52.2583 | -52.9312 | -52.0752 | -51.4252 | 69.8364 | -52.9953 | -52.5238 | -52.7298 | -52.977 | -52.652 | -0.096131 | -0.013733 | -0.12817 | 0.67291 | 0.85602 | 0 | 0.95215 | 0.096131 | -0.064087 | 0.018311 | -122.3419 | 0.20142 | 0.27923 | -0.045777 | 0.34332 | 0.01831 | 0.76904 | 122.7173 | 0.2655 | 0.4715 | 122.8317 | 122.8317 | 122.7356 | 122.7676 | -122.8455 | -122.8134 | 122.6212 | 0.40741 | 3.891 | 1.506
3466.1719 | 123.0423 | -52.9495 | 69.8181 | -0.16739 | 0.00040806 | 0.06053 | 0.069472 | -0.00026703 | 0.0017645 | 0.0047808 | -0.028809 | 0.00046135 | 0.0019226 | -0.0067762 | -0.00086511 | -0.0064343 | -0.0031787 | -49.0494 | 69.809 | -53.0228 | 69.6808 | -52.0798 | -52.771 | -52.2034 | -51.3977 | 69.841 | -52.977 | -52.5101 | -52.7206 | -52.9724 | -52.6794 | -0.073242 | -0.009155 | -0.13733 | 0.86975 | 0.74615 | 0.17853 | 0.8194 | 0.25177 | -0.027466 | 0.022888 | -122.3282 | 0.22888 | 0.27008 | -0.022888 | 0.29755 | 0.004578 | 0.94299 | 122.7036 | 0.25635 | 0.46692 | 122.8317 | 122.818 | 122.7585 | 122.7905 | -122.8409 | -122.7951 | 122.6303 | 0.43945 | 3.9001 | 1.5518
3467.1719 | 123.0698 | -52.9495 | 69.8273 | -0.15976 | -0.00044654 | 0.061385 | 0.068404 | -0.0024032 | -0.00015811 | 0.0049946 | -0.037964 | -0.00017945 | 0.00085443 | 0.00048702 | -0.0021469 | -0.0051527 | -0.0027515 | -49.0311 | 69.8135 | -53.0228 | 69.754 | -52.1164 | -52.7664 | -52.153 | -51.3611 | 69.841 | -52.977 | -52.5009 | -52.7206 | -52.9724 | -52.6657 | -0.073242 | -0.013733 | -0.073243 | 0.83313 | 0.79651 | 0.18311 | 0.86975 | 0.25635 | -0.027466 | 0.013732 | -122.3282 | 0.22888 | 0.28381 | -0.022888 | 0.31128 | 0.004578 | 0.90637 | 122.7768 | 0.25635 | 0.47607 | 122.8363 | 122.818 | 122.7631 | 122.7905 | -122.85 | -122.8043 | 122.7036 | 0.44861 | 3.9185 | 1.5884
3468.1719 | 122.9919 | -52.8992 | 69.8318 | -0.10635 | 0.0012625 | 0.063734 | 0.0699 | -0.0011214 | 0.0028327 | 0.00414 | -0.074585 | 0.0019567 | 0.00042723 | 0.0101 | -0.0012925 | -0.0062207 | -0.0021107 | -49.0952 | 69.8593 | -53.0548 | 69.603 | -52.153 | -52.8488 | -52.2766 | -51.4526 | 69.873 | -52.9953 | -52.5284 | -52.7298 | -52.9953 | -52.6932 | -0.15564 | 0.027466 | -0.22888 | 0.74615 | 0.62256 | 0.050354 | 0.7782 | 0.20599 | -0.09613 | 0.041199 | -122.3602 | 0.16937 | 0.20599 | -0.09613 | 0.30212 | 0 | 0.90179 | 122.6578 | 0.2655 | 0.46692 | 122.9141 | 122.8683 | 122.7585 | 122.7722 | -122.8867 | -122.8271 | 122.5021 | 0.37079 | 3.804 | 1.4465
3469.1719 | 122.9782 | -52.9541 | 69.8227 | -0.11398 | -0.00023294 | 0.062239 | 0.070327 | 0.0016556 | 0.0026191 | 0.0064898 | -0.074585 | -0.00017945 | 2.8e-08 | -0.00015378 | -0.0015061 | -0.0053663 | 0.0019483 | -49.0814 | 69.8639 | -53.0319 | 69.6121 | -52.1805 | -52.8625 | -52.2949 | -51.4847 | 69.9142 | -53.0045 | -52.5696 | -52.7802 | -53.0411 | -52.7252 | -0.077819 | 0.041199 | -0.21057 | 0.77362 | 0.65918 | 0.091553 | 0.737 | 0.16937 | -0.050354 | 0.091553 | -122.3923 | 0.17395 | 0.22888 | -0.086975 | 0.27924 | -0.036621 | 0.85144 | 122.644 | 0.22431 | 0.43488 | 122.8958 | 122.9187 | 122.818 | 122.8683 | -122.8546 | -122.8271 | 122.5662 | 0.38452 | 3.8727 | 1.4694
3470.1719 | 123.0515 | -52.9541 | 69.841 | -0.10635 | -0.0021555 | 0.062239 | 0.068832 | 0.00037377 | 0.0026191 | 0.0032856 | -0.041016 | 0.00067495 | 0.00085443 | -0.00058098 | -0.0019333 | -0.0042981 | 0.00066654 | -49.0677 | 69.8547 | -53.0548 | 69.6396 | -52.1393 | -52.8259 | -52.2491 | -51.4206 | 69.8868 | -52.977 | -52.5146 | -52.739 | -52.9953 | -52.6657 | -0.10071 | 0.013733 | -0.20142 | 0.81482 | 0.70496 | 0.12817 | 0.80566 | 0.22888 | -0.022888 | 0.045777 | -122.3557 | 0.21515 | 0.28839 | -0.041198 | 0.31128 | -0.01831 | 0.91553 | 122.6944 | 0.23804 | 0.46234 | 122.9095 | 122.8638 | 122.8088 | 122.8409 | -122.8958 | -122.818 | 122.5937 | 0.43945 | 3.8864 | 1.5335
3471.1719 | 123.0011 | -52.9083 | 69.841 | -0.045319 | 0.00019446 | 0.061385 | 0.069259 | -0.0017624 | 0.0036871 | 0.0045672 | -0.06543 | 0.00024775 | 0.00064083 | 0.00070062 | -0.0027877 | -0.0060071 | -0.0031787 | -49.0677 | 69.8914 | -53.0457 | 69.603 | -52.1576 | -52.8625 | -52.2812 | -51.4618 | 69.8822 | -53.0045 | -52.533 | -52.7618 | -53.0136 | -52.7069 | -0.13733 | 0.050354 | -0.23804 | 0.75073 | 0.62714 | 0.045776 | 0.76447 | 0.1831 | -0.096131 | 0.041199 | -122.374 | 0.14648 | 0.20142 | -0.10529 | 0.29755 | -0.009155 | 0.88806 | 122.6486 | 0.24262 | 0.4715 | 122.937 | 122.8867 | 122.7997 | 122.7905 | -122.8867 | -122.8455 | 122.5113 | 0.37537 | 3.8406 | 1.4465
3472.1719 | 122.9507 | -52.9449 | 69.873 | -0.068207 | -0.00023294 | 0.062025 | 0.067336 | 0.0016556 | 0.0028327 | 0.0067036 | -0.062378 | 0.0011023 | 0.001709 | 0.0071094 | -0.0023605 | -0.0038709 | 0.0030163 | -49.0814 | 69.8868 | -53.0228 | 69.5892 | -52.1805 | -52.8671 | -52.2812 | -51.4801 | 69.9051 | -52.9861 | -52.5558 | -52.7939 | -53.0502 | -52.7298 | -0.07782 | 0.013733 | -0.28381 | 0.76447 | 0.66376 | 0.07782 | 0.74158 | 0.15564 | -0.041199 | 0.032043 | -122.4289 | 0.15106 | 0.21515 | -0.10529 | 0.25635 | -0.064087 | 0.84228 | 122.612 | 0.19226 | 0.4303 | 122.9095 | 122.8912 | 122.8317 | 122.85 | -122.8958 | -122.8592 | 122.5342 | 0.3891 | 3.8635 | 1.4648
3473.1719 | 123.0011 | -52.9175 | 69.8318 | -0.083466 | 0.00019446 | 0.062025 | 0.069472 | 0.0029374 | 0.0026191 | 0.0060626 | -0.03186 | 0.0017431 | 0.001068 | 0.002196 | -0.0019333 | -0.0021619 | 0.0021619 | -49.0768 | 69.8822 | -53.0365 | 69.6304 | -52.153 | -52.8351 | -52.2491 | -51.4389 | 69.9051 | -52.9907 | -52.5238 | -52.7161 | -52.9953 | -52.6657 | -0.11902 | 0.050354 | -0.20142 | 0.76446 | 0.66833 | 0.082397 | 0.78735 | 0.20142 | -0.073243 | 0.073242 | -122.3557 | 0.20142 | 0.25177 | -0.07782 | 0.32501 | -0.004577 | 0.88348 | 122.6669 | 0.27466 | 0.46692 | 122.9187 | 122.8958 | 122.7997 | 122.8226 | -122.8683 | -122.8226 | 122.5479 | 0.39368 | 3.8406 | 1.4786
3474.1719 | 122.9691 | -52.9449 | 69.8547 | -0.068207 | 0.00083526 | 0.063734 | 0.071181 | 0.003151 | 0.0017645 | 0.0073444 | -0.047119 | 0.0015295 | 0.0019226 | -0.00079478 | -0.0012925 | -0.0030163 | 0.00045294 | -49.0585 | 69.8685 | -53.0319 | 69.5984 | -52.153 | -52.8442 | -52.2629 | -51.4664 | 69.9188 | -52.9678 | -52.5558 | -52.7664 | -53.0273 | -52.7206 | -0.086975 | 0.013733 | -0.25635 | 0.79193 | 0.68207 | 0.10071 | 0.76904 | 0.18768 | -0.022888 | 0.064087 | -122.4106 | 0.17853 | 0.2243 | -0.082398 | 0.24719 | -0.05951 | 0.87891 | 122.6303 | 0.20142 | 0.41199 | 122.9004 | 122.8867 | 122.8134 | 122.8638 | -122.8867 | -122.8226 | 122.5433 | 0.3891 | 3.8864 | 1.4786
3475.1719 | 122.9553 | -52.9633 | 69.9142 | -0.075836 | -1.9142e-05 | 0.060957 | 0.070327 | 0.0029374 | 0.00048269 | 0.0069172 | -0.062378 | 0.0023839 | 0.001068 | -0.00058098 | -0.0012925 | -0.0047253 | -0.0014697 | -49.0585 | 69.8822 | -53.0457 | 69.5709 | -52.2125 | -52.8763 | -52.3178 | -51.5396 | 69.9554 | -52.9861 | -52.6245 | -53.064 | -52.9221 | -52.5696 | -0.082397 | -0.032044 | -0.34332 | 0.75073 | 0.64545 | 0.086975 | 0.72784 | 0.16937 | -0.022888 | 0.041198 | -122.5388 | -0.10071 | 0.39368 | 0.041199 | 0.41656 | 0.064087 | 0.83313 | 122.6166 | -0.07782 | 0.36163 | 122.9279 | 122.9416 | 122.8455 | 122.9187 | -122.9599 | -122.9004 | 122.5342 | 0.33874 | 3.9047 | 1.4236
3476.1719 | 122.8683 | -52.9175 | 69.9097 | -0.083466 | 0.0021171 | 0.062025 | 0.068191 | 0.0037918 | 0.0043281 | 0.0062762 | -0.050171 | 0.00024775 | -0.0010682 | 0.00070062 | -0.0040695 | -0.0028027 | -0.0016833 | -49.0402 | 69.9142 | -53.009 | 69.603 | -52.1896 | -52.8625 | -52.2995 | -51.5121 | 69.9371 | -52.9678 | -52.5925 | -52.8259 | -53.096 | -52.739 | -0.091553 | 0.004578 | -0.3067 | 0.72784 | 0.61798 | 0.054931 | 0.70953 | 0.14648 | -0.050354 | 0.027466 | -122.5021 | 0.091552 | 0.17853 | -0.17853 | 0.22888 | -0.12817 | 0.8194 | 122.612 | 0.14191 | 0.37537 | 122.9233 | 122.905 | 122.8317 | 122.8546 | -122.9187 | -122.8775 | 122.5204 | 0.32501 | 3.8773 | 1.4053
3477.1719 | 122.9279 | -52.9449 | 69.9051 | -0.1445 | -1.9142e-05 | 0.06053 | 0.068832 | -0.0021896 | 0.0026191 | 0.0060626 | -0.092895 | 0.00067495 | 0.0019226 | -0.0035718 | -0.0027877 | -0.0047253 | 0.00088014 | -49.0494 | 69.9051 | -53.0228 | 69.5847 | -52.1805 | -52.8534 | -52.272 | -51.6678 | 69.873 | -52.9816 | -52.5513 | -52.8168 | -53.0319 | -52.7069 | -0.07782 | 0 | -0.32043 | 0.76447 | 0.67291 | 0.091552 | 0.75073 | 0.16937 | -0.036621 | -0.032043 | -122.4564 | 0.12817 | 0.23804 | -0.086975 | 0.27466 | -0.050354 | 0.84228 | 122.6074 | 0.16479 | 0.4303 | 122.9279 | 122.8546 | 122.85 | 122.818 | -122.9279 | -122.8867 | 122.5296 | 0.39368 | 3.8956 | 1.2772
3478.1719 | 122.9553 | -52.9678 | 69.9371 | -0.037689 | -0.00087374 | 0.061598 | 0.068404 | 0.00058737 | 0.00091009 | 0.0047808 | -0.044067 | 0.0015295 | 0.00085443 | -0.0016492 | -0.00022431 | -0.0042981 | 0.0021619 | -49.0356 | 69.9142 | -53.0228 | 69.5847 | -52.1805 | -52.8763 | -52.2812 | -51.5167 | 69.96 | -52.9724 | -52.5833 | -52.7527 | -53.4027 | -52.9541 | -0.054932 | -0.022888 | -0.35248 | 0.78735 | 0.68665 | 0.091552 | 0.74158 | 0.14648 | -0.004578 | 0.022888 | -122.5204 | 0.21515 | 0.013732 | -0.43488 | 0.01831 | -0.4303 | 0.84228 | 122.6074 | 0.21973 | 0.3891 | 122.937 | 122.9324 | 122.8821 | 122.9279 | -122.9599 | -122.9095 | 122.5525 | 0.38452 | 3.9322 | 1.4511
3479.1719 | 122.8958 | -52.9404 | 69.9234 | -0.03006 | 0.0010489 | 0.063521 | 0.071395 | -0.00069423 | 0.00091009 | 0.0060626 | -0.041016 | 0.0021703 | 0.0019226 | 0.0041186 | -0.00065151 | -0.0036573 | -0.0018971 | -49.0082 | 69.9005 | -53.0045 | 69.5938 | -52.1667 | -52.858 | -52.272 | -51.5213 | 69.96 | -52.9678 | -52.5833 | -52.8122 | -53.0685 | -52.7344 | -0.064087 | -0.022888 | -0.32959 | 0.77362 | 0.66833 | 0.082398 | 0.73242 | 0.14648 | -0.027465 | 0.036621 | -122.5067 | 0.12817 | 0.20599 | -0.12817 | 0.23346 | -0.10071 | 0.83771 | 122.5983 | 0.15564 | 0.38452 | 122.905 | 122.9279 | 122.8409 | 122.9004 | -122.9279 | -122.8912 | 122.5342 | 0.35706 | 3.9322 | 1.4191
3480.1719 | 122.8912 | -52.9495 | 69.8868 | -0.12161 | 0.0025443 | 0.060744 | 0.068832 | -0.001976 | -0.00058531 | 0.003072 | -0.12952 | 0.0021703 | 2.8e-08 | -0.001222 | -0.0017197 | -0.0053663 | -0.0016833 | -49.0402 | 69.9142 | -53.0319 | 69.5847 | -52.1667 | -52.8488 | -52.3087 | -51.2604 | 69.9509 | -52.9266 | -52.5696 | -52.7573 | -53.0411 | -52.7206 | -0.082397 | 0.027466 | -0.30212 | 0.78278 | 0.64087 | 0.10071 | 0.72327 | 0.1831 | 0.022888 | 0.064087 | -122.4564 | 0.19226 | 0.22888 | -0.091553 | 0.20599 | -0.11444 | 0.86517 | 122.6166 | 0.16937 | 0.35706 | 122.9462 | 122.8775 | 122.8638 | 122.9004 | -122.9187 | -122.8134 | 122.5342 | 0.37994 | 3.9093 | 1.6891
3481.1719 | 122.9233 | -52.8809 | 69.9371 | -0.091095 | 0.0010489 | 0.062666 | 0.071181 | -0.0032578 | 0.0015509 | 0.0045672 | -0.03186 | 0.0011023 | 0.0014954 | 0.0047594 | -0.0027877 | -0.0036573 | 0.0019483 | -49.0173 | 69.9234 | -53.009 | 69.5892 | -52.1759 | -52.8625 | -52.2949 | -51.5121 | 69.96 | -52.9587 | -52.684 | -52.9266 | -52.7481 | -52.5055 | -0.12817 | -0.013733 | -0.3479 | 0.70496 | 0.58594 | 0.01831 | 0.71411 | 0.14648 | -0.07782 | 0.022888 | -122.6212 | -0.045777 | 0.37537 | 0.13275 | 0.45319 | 0.21057 | 0.83313 | 122.5983 | 0.032043 | 0.27466 | 122.9324 | 122.9187 | 122.8043 | 122.8409 | -122.9462 | -122.8958 | 122.4701 | 0.19684 | 3.8635 | 1.3687
3482.1719 | 122.9095 | -52.9037 | 69.9326 | -0.11398 | -0.0017281 | 0.062239 | 0.069686 | 0.0010148 | 0.0028327 | 0.0043536 | -0.019653 | 0.0034521 | 0.00085443 | 0.00048702 | -0.0032151 | -0.0038709 | 0.0015209 | -48.9624 | 69.9188 | -52.9678 | 69.6579 | -52.0889 | -52.7756 | -52.2354 | -51.4069 | 69.96 | -52.9175 | -52.5467 | -52.7481 | -53.0136 | -52.684 | -0.064086 | -0.013733 | -0.27466 | 0.81482 | 0.66833 | 0.12817 | 0.73242 | 0.19226 | -0.013732 | 0.027466 | -122.4792 | 0.15564 | 0.21973 | -0.10986 | 0.23346 | -0.096131 | 0.87891 | 122.6257 | 0.16937 | 0.37079 | 122.8867 | 122.8775 | 122.8226 | 122.8638 | -122.9004 | -122.85 | 122.5616 | 0.35706 | 3.9413 | 1.4969
3483.1719 | 122.9462 | -52.8992 | 69.9463 | -0.083466 | 0.00062166 | 0.061171 | 0.070541 | -0.0011214 | 0.00026909 | 0.0020038 | -0.016602 | 0.00067495 | 0.003418 | 0.00027342 | -0.0017197 | -0.0053663 | 2.554e-05 | -48.9578 | 69.9326 | -52.9724 | 69.6762 | -52.0706 | -52.771 | -52.1988 | -51.3931 | 69.9783 | -52.8809 | -52.5284 | -52.7618 | -53.009 | -52.6749 | -0.073242 | -0.013733 | -0.27008 | 0.82855 | 0.70038 | 0.12817 | 0.77362 | 0.20142 | 0.018311 | 0.032044 | -122.4747 | 0.13733 | 0.2243 | -0.10986 | 0.20599 | -0.12817 | 0.90179 | 122.6486 | 0.11902 | 0.35248 | 122.905 | 122.8592 | 122.8317 | 122.8775 | -122.9187 | -122.8271 | 122.5754 | 0.37079 | 3.9413 | 1.506
3484.1719 | 122.9095 | -52.9037 | 69.9509 | -0.060578 | 0.0010489 | 0.06288 | 0.069472 | 0.0018692 | 0.0028327 | 0.0054218 | -0.019653 | 0.0011023 | 0.0012818 | 0.0045458 | -0.00022431 | -0.0038709 | 0.0032299 | -48.9716 | 69.9371 | -52.9541 | 69.6396 | -52.1164 | -52.7939 | -52.2263 | -51.4618 | 69.9692 | -52.9266 | -52.5604 | -52.7893 | -53.0365 | -52.7023 | -0.050354 | -0.013733 | -0.31128 | 0.78735 | 0.67749 | 0.10986 | 0.72785 | 0.16022 | -0.022888 | 0.01831 | -122.5113 | 0.11444 | 0.20142 | -0.13275 | 0.2243 | -0.10986 | 0.83771 | 122.5937 | 0.13733 | 0.36621 | 122.8912 | 122.8958 | 122.8409 | 122.8729 | -122.905 | -122.8775 | 122.5433 | 0.34332 | 3.9322 | 1.442
3485.1719 | 122.9324 | -52.9129 | 69.9234 | -0.083466 | -0.00023294 | 0.062666 | 0.071181 | 0.0046464 | 0.0013373 | 0.009267 | -0.0043946 | 0.00024775 | 0.0012818 | -0.005708 | -0.0032151 | -0.0047253 | -0.0018971 | -48.9578 | 69.9509 | -52.977 | 69.6579 | -52.066 | -52.7802 | -52.2171 | -51.3977 | 69.9783 | -52.9129 | -52.5558 | -52.7664 | -53.0319 | -52.6978 | -0.064087 | 0.027466 | -0.2655 | 0.84686 | 0.6958 | 0.13275 | 0.75989 | 0.19684 | 0 | 0.054932 | -122.4792 | 0.14648 | 0.21515 | -0.11902 | 0.21515 | -0.11902 | 0.91095 | 122.6349 | 0.14648 | 0.35706 | 122.9279 | 122.8912 | 122.8638 | 122.8912 | -122.9004 | -122.8363 | 122.5708 | 0.35706 | 3.9551 | 1.5152
3486.1719 | 122.9324 | -52.9037 | 69.9371 | -0.060578 | 0.00062166 | 0.060103 | 0.0699 | 0.00080117 | -0.00079891 | 0.0062762 | -0.016602 | -0.00082025 | 0.0029906 | 0.0028368 | -0.0023605 | -0.0055799 | 0.0034435 | -48.9258 | 69.9371 | -52.9678 | 69.6716 | -52.0615 | -52.7481 | -52.1988 | -51.3794 | 69.9783 | -52.9083 | -52.5375 | -52.7344 | -53.0136 | -52.6657 | -0.064086 | 0 | -0.2655 | 0.84229 | 0.70496 | 0.15564 | 0.76904 | 0.21973 | -0.004577 | 0.041199 | -122.4747 | 0.16937 | 0.23804 | -0.10986 | 0.24262 | -0.10529 | 0.90637 | 122.6395 | 0.17395 | 0.37079 | 122.905 | 122.8867 | 122.8409 | 122.8821 | -122.905 | -122.8455 | 122.5754 | 0.36621 | 3.978 | 1.5244
3487.1719 | 122.9462 | -52.89 | 69.928 | -0.10635 | 0.00040806 | 0.062453 | 0.068191 | -5.343e-05 | 0.0032599 | 0.0045672 | -0.019653 | 0.00046135 | -0.00021357 | 0.0054004 | -0.0010787 | -0.0047253 | 0.0019483 | -48.9441 | 69.9554 | -52.977 | 69.6396 | -52.1027 | -52.7847 | -52.2354 | -51.4343 | 69.9829 | -52.9175 | -52.5696 | -52.7618 | -53.0502 | -52.6978 | -0.086975 | 0.027465 | -0.28839 | 0.78735 | 0.6546 | 0.10529 | 0.74158 | 0.19226 | -0.027465 | 0.054931 | -122.4976 | 0.12817 | 0.19226 | -0.16022 | 0.21973 | -0.13275 | 0.87433 | 122.6166 | 0.15564 | 0.3479 | 122.9324 | 122.9004 | 122.8455 | 122.8729 | -122.905 | -122.8455 | 122.5296 | 0.32043 | 3.9459 | 1.4557
3488.1719 | 122.9324 | -52.89 | 69.9646 | -0.068207 | -0.0013009 | 0.061812 | 0.070541 | 0.0027238 | 0.0013373 | 0.0049946 | -0.022705 | 0.0028113 | 2.8e-08 | 5.9824e-05 | -0.0017197 | -0.0034437 | 0.00066654 | -48.9304 | 69.9234 | -52.9495 | 69.6625 | -52.0981 | -52.771 | -52.2354 | -51.4023 | 69.9692 | -52.9083 | -52.5421 | -52.7618 | -53.0045 | -52.684 | -0.059509 | -0.041199 | -0.30212 | 0.79193 | 0.6546 | 0.11902 | 0.71411 | 0.17853 | -0.01831 | 0.004577 | -122.5067 | 0.12817 | 0.20599 | -0.11444 | 0.2243 | -0.096131 | 0.85144 | 122.612 | 0.14648 | 0.36621 | 122.8729 | 122.8775 | 122.8134 | 122.8592 | -122.9141 | -122.8729 | 122.5525 | 0.3479 | 3.9597 | 1.4877
3489.1719 | 122.937 | -52.8442 | 69.96 | -0.068207 | 0.00062166 | 0.061598 | 0.069045 | -5.343e-05 | 0.0019781 | 0.0034992 | -0.010498 | 0.00046135 | 0.00085443 | -0.0033582 | -0.0034287 | -0.0047253 | 0.0045117 | -48.8846 | 69.9463 | -52.9541 | 69.7037 | -52.121 | -52.8534 | -52.1759 | -51.329 | 69.9875 | -52.8946 | -52.4826 | -52.6978 | -52.9266 | -52.6337 | -0.10986 | -0.013733 | -0.25635 | 0.72327 | 0.66833 | -0.009156 | 0.7782 | 0.10071 | -0.050354 | 0.027466 | -122.4426 | 0.14648 | 0.21057 | -0.082398 | 0.26093 | -0.032044 | 0.83313 | 122.6578 | 0.19684 | 0.41199 | 122.9004 | 122.8821 | 122.7905 | 122.8317 | -122.9141 | -122.8546 | 122.5479 | 0.36163 | 3.9597 | 1.5152
3490.1719 | 122.9507 | -52.8625 | 69.9646 | -0.091095 | -0.0015145 | 0.061385 | 0.0699 | 0.00058737 | 0.0017645 | 0.0054218 | 0.013916 | 0.0015295 | -0.00064077 | -0.001222 | -0.00065151 | -0.00066648 | 0.0015209 | -48.8754 | 69.9554 | -52.9404 | 69.7128 | -52.002 | -52.7023 | -52.1576 | -51.3382 | 69.9875 | -52.8854 | -52.5925 | -52.5742 | -52.9266 | -52.6199 | -0.07782 | -0.009156 | -0.25177 | 0.8606 | 0.70496 | 0.16022 | 0.78278 | 0.23804 | -0.022888 | 0.022888 | -122.5571 | 0.28839 | 0.24262 | -0.064087 | 0.2655 | -0.041199 | 0.93842 | 122.6532 | 0.31128 | 0.29297 | 122.8958 | 122.8729 | 122.818 | 122.85 | -122.905 | -122.85 | 122.5754 | 0.27008 | 3.9871 | 1.5244
3491.1719 | 123.0057 | -52.8717 | 69.8959 | -0.12161 | 0.0023307 | 0.061598 | 0.064986 | 0.0010148 | 0.0024053 | 0.0056354 | 0.050537 | -0.00017945 | 0.0014954 | -0.0089124 | -0.0025741 | -0.0051527 | -0.00018806 | -48.8663 | 69.9051 | -52.8854 | 69.7586 | -51.9699 | -52.7023 | -52.1164 | -51.2833 | 69.928 | -52.9129 | -52.4368 | -52.6428 | -52.8809 | -52.5925 | -0.013733 | 0.009155 | -0.13733 | 0.90179 | 0.75531 | 0.16937 | 0.76904 | 0.18311 | -0.041199 | 0.032044 | -122.3328 | 0.22888 | 0.27924 | -0.009155 | 0.32044 | 0.032044 | 0.91553 | 122.644 | 0.27008 | 0.47607 | 122.7905 | 122.8409 | 122.7768 | 122.7997 | -122.7814 | -122.8088 | 122.6303 | 0.43487 | 4.0054 | 1.5884
3492.1719 | 122.9416 | -52.8442 | 69.9646 | -0.075836 | -0.00087374 | 0.063521 | 0.069045 | 0.0016556 | 0.0032599 | 0.0052082 | -0.025757 | 0.0013159 | -0.0012818 | 0.001128 | -0.00086511 | -0.0028027 | -0.0025379 | -48.8846 | 69.96 | -52.9587 | 69.7128 | -52.0294 | -52.7481 | -52.1942 | -51.3657 | 69.9921 | -52.89 | -52.5146 | -52.7298 | -52.977 | -52.652 | -0.11444 | -0.004578 | -0.25177 | 0.81482 | 0.65002 | 0.09613 | 0.76446 | 0.21057 | -0.045777 | 0.027465 | -122.4792 | 0.11444 | 0.19226 | -0.13275 | 0.23804 | -0.086975 | 0.92926 | 122.6715 | 0.16022 | 0.37537 | 122.9187 | 122.8821 | 122.8043 | 122.8363 | -122.9233 | -122.8546 | 122.5571 | 0.32959 | 3.9597 | 1.4786
3493.1719 | 122.9691 | -52.8351 | 69.9966 | -0.12924 | 0.0010489 | 0.062239 | 0.070541 | 0.00016017 | 0.00069649 | 0.0047808 | 0.016968 | 0.0017431 | 0.0019226 | -0.0018628 | -0.0015061 | -0.0060071 | 0.0045117 | -48.8708 | 69.9646 | -52.9404 | 69.7311 | -52.0111 | -52.7023 | -52.153 | -51.3062 | 69.9966 | -52.9037 | -52.5009 | -52.7435 | -52.8442 | -52.6154 | -0.10529 | -0.032043 | -0.2655 | 0.82397 | 0.68207 | 0.13275 | 0.78735 | 0.23804 | -0.068665 | 0 | -122.4976 | 0.091553 | 0.21973 | -0.009155 | 0.28839 | 0.05951 | 0.92926 | 122.6715 | 0.16022 | 0.40283 | 122.905 | 122.9004 | 122.7997 | 122.8317 | -122.937 | -122.9004 | 122.5662 | 0.33417 | 3.9642 | 1.5289
3494.1719 | 122.9691 | -52.8397 | 69.9921 | -0.26657 | 0.0010489 | 0.059248 | 0.069686 | 0.0018692 | 0.00048269 | 0.0067036 | -0.010498 | -0.00060665 | 0.001709 | -0.002931 | -0.0015061 | -0.0040845 | -0.0038197 | -48.793 | 69.9829 | -52.9358 | 69.7357 | -51.9791 | -52.684 | -52.153 | -51.3382 | 70.0241 | -52.858 | -52.478 | -52.6794 | -52.9495 | -52.6245 | -0.09613 | -0.009155 | -0.25635 | 0.8606 | 0.68665 | 0.15564 | 0.78278 | 0.25177 | -0.01831 | 0.032044 | -122.4701 | 0.16022 | 0.21515 | -0.10986 | 0.23346 | -0.091553 | 0.95673 | 122.6715 | 0.17853 | 0.37994 | 122.9187 | 122.8821 | 122.8226 | 122.8638 | -122.9279 | -122.85 | 122.5754 | 0.36163 | 4.0466 | 1.5015
3495.1719 | 122.9645 | -52.8305 | 69.9966 | -0.091095 | 0.00062166 | 0.062239 | 0.067763 | 0.0040054 | 0.0019781 | 0.0039264 | 0.026123 | 0.0025975 | 0.00064083 | 0.00091422 | -0.0021469 | -0.0045117 | 0.00023934 | -48.848 | 69.9738 | -52.9083 | 69.7311 | -51.947 | -52.9129 | -52.1759 | -51.2924 | 70.0104 | -52.8442 | -52.4689 | -52.6794 | -52.9129 | -52.6108 | -0.07782 | -0.022888 | -0.2655 | 0.88348 | 0.6546 | -0.082398 | 0.73242 | -0.004578 | -0.013733 | 0.013733 | -122.4655 | 0.15106 | 0.21973 | -0.082398 | 0.23346 | -0.068665 | 0.9613 | 122.6395 | 0.16479 | 0.37537 | 122.8821 | 122.8546 | 122.8043 | 122.8409 | -122.905 | -122.8409 | 122.5616 | 0.36163 | 3.9825 | 1.5381
3496.1719 | 122.937 | -52.8717 | 69.9692 | -0.052948 | 0.0012625 | 0.062666 | 0.070541 | 0.00016017 | 0.0011237 | 0.0043536 | -0.025757 | 0.0019567 | 0.002777 | -0.0076306 | -0.00065151 | -0.0045117 | 0.0055797 | -48.9212 | 69.9921 | -52.9541 | 69.6487 | -52.0935 | -52.7985 | -52.2171 | -51.6449 | 69.9554 | -52.9221 | -52.4872 | -52.7573 | -52.9816 | -52.652 | -0.082398 | 0.022888 | -0.32043 | 0.7782 | 0.6546 | 0.073242 | 0.737 | 0.15564 | -0.050354 | -0.013733 | -122.4564 | 0.11444 | 0.21973 | -0.10986 | 0.27008 | -0.059509 | 0.8606 | 122.6028 | 0.16479 | 0.43487 | 122.9462 | 122.8775 | 122.8638 | 122.8271 | -122.9233 | -122.8912 | 122.5204 | 0.38452 | 3.9505 | 1.2268
3497.1719 | 122.9416 | -52.8442 | 70.0195 | -0.068207 | 0.00083526 | 0.061385 | 0.070327 | -0.0017624 | 5.5488e-05 | 0.0060626 | 0.023071 | 0.00046135 | 0.0014954 | 0.0034778 | -0.0017197 | -0.0053663 | 0.0021619 | -48.8617 | 70.047 | -52.9312 | 69.7083 | -52.0386 | -52.7069 | -52.153 | -51.3474 | 70.0378 | -52.8534 | -52.4734 | -52.6382 | -52.9083 | -52.5925 | -0.086975 | 0.027466 | -0.31128 | 0.80566 | 0.69122 | 0.13733 | 0.7782 | 0.2243 | -0.009156 | 0.018311 | -122.493 | 0.20599 | 0.25177 | -0.064087 | 0.26093 | -0.054931 | 0.89264 | 122.6395 | 0.21515 | 0.37994 | 122.9782 | 122.8912 | 122.8912 | 122.8821 | -122.9507 | -122.8729 | 122.5525 | 0.37079 | 3.9825 | 1.4969
3498.1719 | 122.9645 | -52.8076 | 70.0104 | -0.075836 | 0.00062166 | 0.063521 | 0.068618 | -0.0015488 | 0.00026909 | 0.0047808 | 0.0047608 | 0.0023839 | 0.00021363 | -0.0018628 | -0.0017197 | -0.0062207 | 2.554e-05 | -48.8251 | 70.0333 | -52.8809 | 69.754 | -51.9882 | -52.6657 | -52.121 | -51.3107 | 70.0378 | -52.8351 | -52.4551 | -52.6382 | -52.9037 | -52.5879 | -0.073242 | 0.022888 | -0.25635 | 0.8194 | 0.68664 | 0.14191 | 0.75989 | 0.21515 | -0.027466 | 0.027466 | -122.4655 | 0.16937 | 0.21973 | -0.096131 | 0.24719 | -0.068665 | 0.89264 | 122.6349 | 0.19684 | 0.37994 | 122.9141 | 122.8729 | 122.8409 | 122.8455 | -122.8912 | -122.8455 | 122.5616 | 0.35248 | 3.9825 | 1.4969
3499.1719 | 122.9691 | -52.8122 | 70.0333 | -0.045319 | 0.00083526 | 0.060744 | 0.070327 | -0.001976 | 0.00069649 | 0.0047808 | 0.023071 | 0.0028113 | 0.0023498 | 0.0030506 | -0.0025741 | -0.0051527 | 0.0021619 | -48.8297 | 70.047 | -52.9037 | 69.7495 | -52.0294 | -52.6657 | -52.1439 | -51.3153 | 70.0653 | -52.8351 | -52.446 | -52.6428 | -52.8763 | -52.597 | -0.091553 | 0.013733 | -0.28381 | 0.78278 | 0.66834 | 0.14649 | 0.75989 | 0.23804 | -0.022888 | 0.032044 | -122.4792 | 0.16937 | 0.21515 | -0.064087 | 0.23804 | -0.041199 | 0.87433 | 122.6532 | 0.19226 | 0.3891 | 122.9507 | 122.9004 | 122.8592 | 122.8775 | -122.937 | -122.8683 | 122.5616 | 0.36621 | 3.9825 | 1.4969
3500.1719 | 122.9645 | -52.8214 | 70.0195 | 0.00045798 | 0.0023307 | 0.06288 | 0.070327 | 0.0020828 | 0.0019781 | 0.0056354 | 0.0047608 | 0.00067495 | 0.003418 | -0.0067762 | -0.0036423 | -0.0068615 | 0.00088014 | -48.8113 | 70.0195 | -52.89 | 69.754 | -51.9882 | -52.6566 | -52.1164 | -51.2604 | 70.0562 | -52.8442 | -52.446 | -52.6474 | -52.89 | -52.5742 | -0.068665 | 0 | -0.2655 | 0.83313 | 0.70496 | 0.1648 | 0.77362 | 0.23346 | -0.022888 | 0.036621 | -122.4655 | 0.17395 | 0.24719 | -0.068665 | 0.27008 | -0.045777 | 0.90179 | 122.644 | 0.19684 | 0.39825 | 122.9095 | 122.9004 | 122.8409 | 122.8775 | -122.9095 | -122.8638 | 122.5754 | 0.37537 | 4.01 | 1.561
3501.1719 | 123.0148 | -52.8122 | 69.9783 | -0.083466 | -0.00066014 | 0.060103 | 0.066695 | 0.0016556 | 0.00069649 | 0.0026446 | 0.081055 | 0.0011023 | 0.002777 | -0.0067762 | -0.0021469 | -0.0055799 | 0.00023934 | -48.848 | 69.9783 | -52.9129 | 69.7586 | -51.9745 | -52.6794 | -52.0889 | -51.2878 | 69.9966 | -52.8442 | -52.4368 | -52.6108 | -52.8717 | -52.5833 | -0.10071 | 0 | -0.21973 | 0.83771 | 0.72327 | 0.13275 | 0.82397 | 0.23346 | -0.032043 | 0.01831 | -122.4152 | 0.20142 | 0.22888 | -0.059509 | 0.26093 | -0.027466 | 0.93842 | 122.6715 | 0.23346 | 0.40741 | 122.8912 | 122.8409 | 122.7905 | 122.8088 | -122.8912 | -122.8226 | 122.5708 | 0.37537 | 3.9642 | 1.5244
3502.1719 | 122.9553 | -52.8168 | 70.0195 | -0.037689 | 0.00019446 | 0.062239 | 0.068832 | -0.0021896 | 0.00069649 | 0.00414 | 0.026123 | -0.00060665 | 0.001068 | -0.00015378 | -0.0032151 | -0.0036573 | 0.00045294 | -48.8113 | 70.0241 | -52.8992 | 69.7403 | -52.0065 | -52.6703 | -52.1255 | -51.329 | 70.079 | -52.8305 | -52.4689 | -52.6382 | -52.8671 | -52.6154 | -0.082398 | 0.004578 | -0.27924 | 0.81024 | 0.69122 | 0.14648 | 0.77362 | 0.22888 | -0.013733 | 0.05951 | -122.4884 | 0.17853 | 0.20142 | -0.050354 | 0.21515 | -0.036621 | 0.89264 | 122.6395 | 0.19226 | 0.36163 | 122.9233 | 122.9095 | 122.8409 | 122.8958 | -122.9187 | -122.85 | 122.5571 | 0.3479 | 4.0054 | 1.4877
3503.1719 | 122.905 | -52.7893 | 70.0424 | -0.060578 | 0.0025443 | 0.062666 | 0.068832 | 0.0018692 | 0.0011237 | 0.0049946 | 0.047485 | 3.4148e-05 | 0.00042723 | -0.0078442 | -0.0025741 | -0.0062207 | -0.00061526 | -48.8113 | 70.0241 | -52.8625 | 69.7495 | -51.9745 | -52.652 | -52.1072 | -51.297 | 70.0928 | -52.8214 | -52.4872 | -52.6291 | -52.8763 | -52.5925 | -0.073242 | -0.01831 | -0.29297 | 0.81482 | 0.68207 | 0.13733 | 0.75531 | 0.21057 | -0.032043 | 0.050354 | -122.5296 | 0.16022 | 0.19684 | -0.086975 | 0.22888 | -0.054932 | 0.88806 | 122.612 | 0.19226 | 0.33417 | 122.8867 | 122.9141 | 122.8134 | 122.8821 | -122.905 | -122.8638 | 122.5388 | 0.30212 | 3.978 | 1.4923
3504.1719 | 122.9324 | -52.8122 | 70.0516 | -0.091095 | -0.00087374 | 0.061385 | 0.068618 | -0.0032578 | 0.0011237 | 0.0017902 | 0.09021 | 0.0013159 | 0.00021363 | -0.00015378 | -0.0017197 | -0.0055799 | -0.0031787 | -48.7976 | 70.047 | -52.89 | 69.7586 | -52.002 | -52.6794 | -52.0706 | -51.4435 | 70.0699 | -52.8534 | -52.4643 | -52.6337 | -52.8809 | -52.6016 | -0.07782 | -0.004578 | -0.29297 | 0.81024 | 0.74158 | 0.13275 | 0.8194 | 0.21057 | -0.041199 | 0.01831 | -122.5159 | 0.17853 | 0.21057 | -0.068664 | 0.25177 | -0.027465 | 0.88806 | 122.6486 | 0.21973 | 0.3891 | 122.937 | 122.9233 | 122.8592 | 122.8821 | -122.9416 | -122.905 | 122.5708 | 0.3479 | 4.0146 | 1.3687
3505.1719 | 122.9782 | -52.7847 | 70.047 | -0.091095 | -0.00066014 | 0.060957 | 0.069045 | 0.00058737 | 0.0011237 | 0.0037128 | 0.0047608 | 0.0023839 | 0.0019226 | 0.00091422 | -0.0049241 | -0.0072889 | 0.00088014 | -48.793 | 70.0607 | -52.8717 | 69.7906 | -51.9608 | -52.6245 | -52.1118 | -51.2741 | 70.0699 | -52.803 | -52.4277 | -52.6016 | -52.8717 | -52.5696 | -0.086975 | 0.013733 | -0.25635 | 0.82397 | 0.67291 | 0.16022 | 0.75989 | 0.24719 | -0.018311 | 0.022888 | -122.4747 | 0.1831 | 0.21515 | -0.086975 | 0.23346 | -0.068664 | 0.91095 | 122.6624 | 0.20142 | 0.37537 | 122.9324 | 122.8729 | 122.8455 | 122.8546 | -122.9187 | -122.85 | 122.5754 | 0.35706 | 3.9917 | 1.5106
3506.1719 | 122.9736 | -52.7802 | 70.0195 | -0.068207 | 0.00019446 | 0.064589 | 0.070754 | -5.343e-05 | -0.0010125 | 0.0054218 | -0.03186 | 0.0019567 | 2.8e-08 | -0.0010084 | -0.0032151 | -0.0040845 | 0.0017345 | -48.8525 | 69.9966 | -52.8854 | 69.7998 | -51.9745 | -52.652 | -52.0889 | -51.2421 | 70.047 | -52.8351 | -52.4231 | -52.6199 | -52.858 | -52.5787 | -0.10529 | -0.022888 | -0.21973 | 0.80566 | 0.69122 | 0.12817 | 0.79651 | 0.23346 | -0.054932 | 0.027466 | -122.4426 | 0.16022 | 0.20142 | -0.07782 | 0.25635 | -0.022888 | 0.91095 | 122.6852 | 0.21515 | 0.41199 | 122.8821 | 122.8821 | 122.7768 | 122.8271 | -122.905 | -122.8546 | 122.58 | 0.35705 | 3.9276 | 1.5381
3507.1719 | 122.9416 | -52.7939 | 70.0653 | -0.052948 | 0.0016899 | 0.06053 | 0.068618 | 0.0035782 | 0.0011237 | 0.0071308 | 0.0047608 | 0.0013159 | 0.001068 | -0.00464 | -0.0038559 | -0.0060071 | 0.00045294 | -48.7839 | 70.047 | -52.8763 | 69.7403 | -51.9928 | -52.6657 | -52.1118 | -51.2924 | 70.0974 | -52.8397 | -52.4368 | -52.6154 | -52.8809 | -52.5787 | -0.082398 | -0.018311 | -0.32501 | 0.80109 | 0.68207 | 0.12817 | 0.76447 | 0.21057 | -0.045777 | 0.032043 | -122.5021 | 0.17853 | 0.21515 | -0.086975 | 0.26093 | -0.041198 | 0.88348 | 122.6166 | 0.22431 | 0.40283 | 122.9233 | 122.937 | 122.8409 | 122.8912 | -122.9416 | -122.905 | 122.5342 | 0.35705 | 4.01 | 1.5015
3508.1719 | 122.9233 | -52.7939 | 70.047 | -0.11398 | 0.0031851 | 0.06053 | 0.067123 | -0.0013352 | -0.0014399 | 0.003072 | 0.03833 | -0.00060665 | 0.0025634 | 0.0032642 | -0.00086511 | -0.0057935 | -0.0012561 | -48.7198 | 70.047 | -52.8442 | 69.7906 | -51.9333 | -52.6016 | -52.0798 | -51.2558 | 70.079 | -52.7893 | -52.446 | -52.6062 | -52.8717 | -52.5879 | -0.050354 | 0 | -0.25635 | 0.86059 | 0.71411 | 0.19226 | 0.76446 | 0.24261 | 0.004577 | 0.032044 | -122.493 | 0.18768 | 0.20599 | -0.07782 | 0.20142 | -0.082397 | 0.91095 | 122.6349 | 0.18311 | 0.34332 | 122.8912 | 122.8683 | 122.8409 | 122.8729 | -122.8912 | -122.8363 | 122.5845 | 0.3479 | 4.0741 | 1.5381
3509.1719 | 123.0011 | -52.7893 | 70.0653 | -0.045319 | 0.0021171 | 0.061171 | 0.068191 | 0.0033646 | 0.0013373 | 0.0015766 | 0.041382 | 3.4148e-05 | 0.0012818 | -0.00015378 | -0.00065151 | -0.0062207 | -0.0012561 | -48.7015 | 70.0378 | -52.8214 | 69.8364 | -51.8692 | -52.5696 | -52.0294 | -51.2009 | 70.0653 | -52.7939 | -52.4094 | -52.5513 | -52.8122 | -52.5558 | -0.032043 | -0.027466 | -0.22888 | 0.9201 | 0.75989 | 0.21973 | 0.79193 | 0.25177 | -0.004577 | 0 | -122.4747 | 0.23804 | 0.23346 | -0.022888 | 0.23804 | -0.018311 | 0.95215 | 122.6578 | 0.24261 | 0.38452 | 122.8592 | 122.8592 | 122.8271 | 122.8546 | -122.8867 | -122.8592 | 122.6257 | 0.37994 | 4.0878 | 1.5884
3510.1719 | 123.056 | -52.7206 | 70.0745 | -0.091095 | 0.0012625 | 0.059248 | 0.070754 | -0.004753 | 0.0019781 | 0.0056354 | -0.022705 | -0.00082025 | 0.00042723 | 0.00091422 | -0.0023605 | -0.0049389 | 0.0023755 | -48.6649 | 70.0195 | -52.8305 | 69.9005 | -51.6998 | -52.1622 | -52.0248 | -51.0452 | 70.0241 | -52.7893 | -52.327 | -52.4689 | -52.739 | -52.4918 | -0.10986 | -0.054932 | -0.17395 | 1.0208 | 0.6958 | 0.55847 | 0.80566 | 0.66833 | -0.068665 | -0.050354 | -122.4014 | 0.25177 | 0.22888 | -0.018311 | 0.29755 | 0.050354 | 1.1307 | 122.731 | 0.32044 | 0.46234 | 122.85 | 122.8134 | 122.7402 | 122.7448 | -122.905 | -122.8638 | 122.6212 | 0.39368 | 4.0558 | 1.6754
3511.1719 | 123.0606 | -52.7344 | 70.047 | -0.091095 | -0.00066014 | 0.062239 | 0.066909 | -0.0021896 | 0.0011237 | 0.0034992 | 0.041382 | 0.00024775 | 0.0046996 | -0.0035718 | -0.0034287 | -0.0049389 | -0.0031787 | -48.7015 | 70.0241 | -52.8397 | 69.8959 | -51.828 | -52.533 | -51.9836 | -51.1368 | 70.0745 | -52.771 | -52.3361 | -52.4872 | -52.7618 | -52.478 | -0.10529 | -0.022888 | -0.15106 | 0.90637 | 0.75073 | 0.20142 | 0.85602 | 0.3067 | -0.036621 | 0.027466 | -122.3831 | 0.24719 | 0.25635 | -0.027466 | 0.29297 | 0.009155 | 1.0117 | 122.7356 | 0.28381 | 0.43487 | 122.8638 | 122.8455 | 122.7585 | 122.8088 | -122.8867 | -122.818 | 122.6303 | 0.39825 | 4.0329 | 1.5976
3512.1719 | 123.0652 | -52.7435 | 70.0562 | -0.022431 | 0.0010489 | 0.063521 | 0.066482 | -0.0017624 | 0.0030463 | 0.0039264 | 0.03833 | -0.00039305 | 0.0023498 | -0.00058098 | -0.0047103 | -0.0068615 | -0.0029651 | -48.674 | 70.0333 | -52.7985 | 69.96 | -51.8372 | -52.5833 | -51.9745 | -51.1139 | 70.047 | -52.771 | -52.3178 | -52.478 | -52.7298 | -52.4689 | -0.054932 | -0.022888 | -0.09613 | 0.90637 | 0.76904 | 0.16022 | 0.82397 | 0.21515 | -0.027466 | -0.009155 | -122.374 | 0.2655 | 0.27466 | 0.013733 | 0.30212 | 0.041199 | 0.9613 | 122.7585 | 0.29297 | 0.45319 | 122.8317 | 122.818 | 122.7768 | 122.7905 | -122.8546 | -122.8271 | 122.7036 | 0.42572 | 4.0695 | 1.6296
3513.1719 | 123.0606 | -52.739 | 70.0287 | -0.10635 | -0.00044654 | 0.059676 | 0.067977 | -0.00048063 | 0.0011237 | 0.003072 | 0.050537 | -0.00039305 | 0.00042723 | 0.0026232 | -0.0023605 | -0.0053663 | -0.0042469 | -48.6557 | 70.015 | -52.8168 | 69.9234 | -51.7822 | -52.5009 | -51.9516 | -51.1871 | 70.079 | -52.7435 | -52.2766 | -52.5513 | -52.7664 | -52.4597 | -0.077819 | -0.013733 | -0.10529 | 0.95673 | 0.78735 | 0.23804 | 0.86517 | 0.31586 | -0.004577 | 0.050354 | -122.3053 | 0.18768 | 0.27924 | -0.027465 | 0.28381 | -0.022888 | 1.0345 | 122.7402 | 0.19226 | 0.46692 | 122.8317 | 122.8226 | 122.7539 | 122.818 | -122.8455 | -122.7722 | 122.6624 | 0.46234 | 4.0833 | 1.5518
3514.1719 | 123.056 | -52.7298 | 70.047 | -0.16739 | 0.0014761 | 0.061812 | 0.068404 | -0.0011214 | 0.00091009 | 0.0086262 | 0.016968 | 0.00024775 | -0.00021357 | -0.003999 | -0.0019333 | -0.0051527 | -0.0040333 | -48.6328 | 70.015 | -52.8305 | 69.9188 | -51.7914 | -52.5284 | -51.9653 | -51.123 | 70.0745 | -52.7527 | -52.3132 | -52.478 | -52.7435 | -52.4597 | -0.10071 | -0.032043 | -0.12817 | 0.93841 | 0.76447 | 0.20142 | 0.86517 | 0.30212 | -0.022889 | 0.027466 | -122.3602 | 0.25177 | 0.27008 | -0.013733 | 0.29297 | 0.009156 | 1.0391 | 122.7493 | 0.27466 | 0.43945 | 122.8455 | 122.8271 | 122.7448 | 122.8043 | -122.8775 | -122.7997 | 122.6486 | 0.41656 | 4.097 | 1.6067
3515.1719 | 123.0835 | -52.6932 | 70.079 | -0.052948 | 0.0021171 | 0.061812 | 0.070113 | 0.00058737 | 0.0026191 | 0.0028582 | 0.062744 | 0.00024775 | 0.001709 | -0.00079478 | -0.0027877 | -0.0062207 | -0.00082886 | -48.6282 | 70.047 | -52.8076 | 70.1111 | -51.59 | -52.9083 | -52.1255 | -51.1414 | 70.0562 | -52.7756 | -52.2949 | -52.4689 | -52.7344 | -52.4551 | -0.11444 | -0.032044 | 0.032043 | 1.1032 | 0.56763 | -0.21515 | 0.68207 | -0.10071 | -0.082398 | -0.022889 | -122.374 | 0.2243 | 0.23804 | -0.041199 | 0.32043 | 0.041199 | 1.2177 | 122.9187 | 0.3067 | 0.48065 | 122.8546 | 122.8317 | 122.7402 | 122.7493 | -122.8867 | -122.8546 | 122.8043 | 0.39825 | 4.0649 | 1.5518
3516.1719 | 123.0469 | -52.7115 | 70.0424 | -0.068207 | 0.00019446 | 0.061598 | 0.068618 | 0.00058737 | 0.0030463 | 0.0047808 | 0.029175 | 3.4148e-05 | -0.00021357 | 0.00048702 | -0.0038559 | -0.0068615 | -0.0012561 | -48.6374 | 70.0516 | -52.7893 | 69.9234 | -51.7685 | -52.4689 | -51.9379 | -51.0635 | 70.0974 | -52.7481 | -52.3819 | -52.6291 | -52.6978 | -52.4048 | -0.07782 | 0.009156 | -0.11902 | 0.94299 | 0.77362 | 0.24262 | 0.85144 | 0.32044 | -0.036621 | 0.054932 | -122.4243 | 0.082398 | 0.3067 | 0.013733 | 0.34332 | 0.050354 | 1.0208 | 122.7127 | 0.11902 | 0.36621 | 122.8409 | 122.8455 | 122.7631 | 122.8088 | -122.8317 | -122.7905 | 122.6349 | 0.32959 | 4.0741 | 1.6479
3517.1719 | 123.0377 | -52.7023 | 70.0653 | -0.15976 | 0.00040806 | 0.06053 | 0.069686 | 0.00251 | 0.0032599 | 0.003072 | 0.013916 | -0.00082025 | 0.00064083 | -0.00015378 | -0.0021469 | -0.0068615 | -0.00018806 | -48.6786 | 70.047 | -52.8214 | 69.8822 | -51.8646 | -52.565 | -51.9974 | -51.1505 | 70.0745 | -52.7527 | -52.3087 | -52.4689 | -52.7344 | -52.4643 | -0.11902 | -0.018311 | -0.18311 | 0.83771 | 0.70496 | 0.13733 | 0.82398 | 0.25635 | -0.050354 | 0.009155 | -122.374 | 0.23346 | 0.23804 | -0.032043 | 0.28839 | 0.018311 | 0.95673 | 122.7036 | 0.28381 | 0.44403 | 122.8683 | 122.8271 | 122.7493 | 122.7768 | -122.8867 | -122.818 | 122.5845 | 0.39368 | 4.0237 | 1.5518
3518.1719 | 123.0331 | -52.6932 | 70.0562 | -0.0071715 | 0.0010489 | 0.061385 | 0.067336 | 0.00080117 | 0.0039007 | 0.0020038 | 0.013916 | -0.00039305 | 2.8e-08 | 0.0066822 | -0.0023605 | -0.0051527 | -0.00082886 | -48.6511 | 70.047 | -52.7939 | 69.9188 | -51.8097 | -52.5238 | -51.9333 | -51.091 | 70.0928 | -52.7435 | -52.2766 | -52.4506 | -52.6794 | -52.4368 | -0.10071 | -0.009155 | -0.13733 | 0.88348 | 0.75989 | 0.16937 | 0.86059 | 0.27008 | -0.050354 | 0.036621 | -122.3328 | 0.24261 | 0.25635 | 0.013733 | 0.3067 | 0.064087 | 0.98419 | 122.7127 | 0.29297 | 0.46692 | 122.8409 | 122.8363 | 122.7402 | 122.7859 | -122.85 | -122.7997 | 122.612 | 0.41656 | 4.0421 | 1.6022
3519.1719 | 123.0743 | -52.684 | 70.0607 | -0.12924 | 0.00062166 | 0.061598 | 0.068404 | 0.0016556 | 0.00069649 | 0.0043536 | 0.02002 | -0.0010339 | 0.0025634 | 0.0045458 | -0.0036423 | -0.0077161 | -0.0016833 | -48.642 | 70.0562 | -52.7893 | 69.9051 | -51.8188 | -52.5238 | -51.9562 | -51.0956 | 70.0745 | -52.7573 | -52.2766 | -52.4506 | -52.7115 | -52.4414 | -0.10529 | -0.004578 | -0.15564 | 0.86517 | 0.72784 | 0.16022 | 0.83313 | 0.2655 | -0.073242 | 0.013733 | -122.3373 | 0.23346 | 0.24262 | -0.027466 | 0.31586 | 0.045776 | 0.97046 | 122.6944 | 0.3067 | 0.48065 | 122.8455 | 122.8317 | 122.7402 | 122.7585 | -122.85 | -122.818 | 122.5891 | 0.40741 | 4.0421 | 1.5884
3520.1719 | 123.0377 | -52.6886 | 70.0424 | -0.098725 | 0.00040806 | 0.059889 | 0.070113 | 0.00037377 | 0.0011237 | 0.0022174 | 0.0047608 | -0.00060665 | -0.00021357 | 0.0019824 | -0.0044967 | -0.0066479 | -0.00040166 | -48.6374 | 70.047 | -52.7985 | 69.9051 | -51.8326 | -52.5421 | -51.9699 | -51.1368 | 70.0836 | -52.7481 | -52.2903 | -52.446 | -52.7115 | -52.4323 | -0.10986 | 0.004578 | -0.13733 | 0.85602 | 0.71869 | 0.14649 | 0.82855 | 0.25635 | -0.059509 | 0.041199 | -122.3328 | 0.24262 | 0.25635 | -0.022888 | 0.31586 | 0.036621 | 0.96588 | 122.7036 | 0.30212 | 0.45776 | 122.8455 | 122.8317 | 122.7356 | 122.7722 | -122.8409 | -122.7905 | 122.5937 | 0.39826 | 4.0512 | 1.5518
3521.1719 | 123.0927 | -52.6978 | 70.0745 | -0.13687 | 0.00083526 | 0.060744 | 0.068191 | -0.003685 | 0.0021917 | 0.0037128 | 0.0078126 | 0.00046135 | -0.00021357 | 0.00027342 | -0.0044967 | -0.0057935 | 0.00023934 | -48.6053 | 70.0699 | -52.8076 | 69.9371 | -51.7593 | -52.4826 | -51.9241 | -51.0544 | 70.0882 | -52.7206 | -52.2537 | -52.4139 | -52.6749 | -52.4139 | -0.10986 | -0.004578 | -0.13733 | 0.93842 | 0.77362 | 0.21515 | 0.88348 | 0.32501 | -0.022888 | 0.013733 | -122.3282 | 0.28381 | 0.28381 | 0.022888 | 0.3067 | 0.045776 | 1.0483 | 122.7448 | 0.3067 | 0.46692 | 122.8775 | 122.8088 | 122.7676 | 122.7859 | -122.8821 | -122.7951 | 122.6349 | 0.44403 | 4.0924 | 1.6434
3522.1719 | 123.0606 | -52.684 | 70.0562 | -0.12924 | -0.0013009 | 0.061385 | 0.066909 | -0.00048063 | 0.0015509 | 0.0045672 | 0.02002 | 3.4148e-05 | -0.00021357 | 0.002196 | -0.0032151 | -0.0068615 | -0.0018971 | -48.6145 | 70.0699 | -52.7893 | 69.928 | -51.7868 | -52.5101 | -51.9287 | -51.0681 | 70.0974 | -52.7206 | -52.2537 | -52.4185 | -52.6794 | -52.4231 | -0.10529 | 0.013733 | -0.12817 | 0.89722 | 0.75531 | 0.17395 | 0.8606 | 0.27924 | -0.036621 | 0.041199 | -122.3099 | 0.2655 | 0.26093 | 0.004578 | 0.29755 | 0.041199 | 1.0025 | 122.7173 | 0.30212 | 0.46692 | 122.8592 | 122.818 | 122.7539 | 122.7814 | -122.8455 | -122.7768 | 122.612 | 0.4303 | 4.0695 | 1.6159
3523.1719 | 123.0698 | -52.684 | 70.1019 | -0.075836 | 0.00019446 | 0.063307 | 0.069472 | 0.0010148 | 0.0021917 | 0.0054218 | 0.0078126 | -0.0012477 | -0.0010682 | -0.00079478 | -0.0021469 | -0.0057935 | -0.0012561 | -48.6008 | 70.0653 | -52.8076 | 69.9142 | -51.8005 | -52.4872 | -51.947 | -51.0864 | 70.1111 | -52.7298 | -52.2583 | -52.4323 | -52.6886 | -52.4323 | -0.1236 | -0.036621 | -0.18768 | 0.88348 | 0.737 | 0.19684 | 0.8606 | 0.32043 | -0.045776 | 0.009155 | -122.3602 | 0.25177 | 0.25177 | -0.004578 | 0.29755 | 0.041198 | 1.0071 | 122.7219 | 0.29755 | 0.4715 | 122.8729 | 122.8409 | 122.7493 | 122.7951 | -122.9095 | -122.8317 | 122.5983 | 0.42572 | 4.0833 | 1.5976
3524.1719 | 122.9691 | -52.7161 | 70.1019 | -0.014801 | -0.00087374 | 0.062453 | 0.069472 | -0.00090783 | 0.0021917 | 0.0045672 | -0.077637 | 0.0036657 | 0.0019226 | 0.0058276 | -0.0042831 | -0.0060071 | -0.0027515 | -48.6099 | 70.1157 | -52.7985 | 69.9051 | -51.8555 | -52.5558 | -52.0111 | -51.1597 | 70.166 | -52.771 | -52.3087 | -52.5192 | -52.7985 | -52.4826 | -0.082398 | 0.013733 | -0.19684 | 0.8606 | 0.70496 | 0.16022 | 0.78735 | 0.24262 | -0.054932 | 0.064087 | -122.4106 | 0.19684 | 0.23346 | -0.082398 | 0.28839 | -0.027466 | 0.94299 | 122.7036 | 0.25177 | 0.46234 | 122.9141 | 122.937 | 122.8317 | 122.8821 | -122.9004 | -122.8729 | 122.6212 | 0.40741 | 4.1061 | 1.5564
3525.1719 | 123.0469 | -52.684 | 70.1111 | -0.11398 | 0.00062166 | 0.061812 | 0.067123 | -0.003685 | 0.0024053 | 0.0047808 | 0.02002 | 0.0015295 | 0.00064083 | -0.0065626 | -0.0017197 | -0.0051527 | -0.0021107 | -48.6145 | 70.0928 | -52.7756 | 69.9097 | -51.8188 | -52.5146 | -51.947 | -51.1047 | 70.1294 | -52.7298 | -52.2675 | -52.4185 | -52.6978 | -52.4231 | -0.091553 | -0.018311 | -0.20142 | 0.86517 | 0.737 | 0.16937 | 0.82855 | 0.26093 | -0.045776 | 0.018311 | -122.3785 | 0.2655 | 0.26093 | -0.013733 | 0.3067 | 0.032043 | 0.95673 | 122.6852 | 0.31128 | 0.46234 | 122.8683 | 122.8592 | 122.7768 | 122.8134 | -122.8867 | -122.8409 | 122.5937 | 0.41656 | 4.0695 | 1.5793
3526.1719 | 123.024 | -52.6978 | 70.079 | -0.091095 | 0.0025443 | 0.061812 | 0.066054 | 0.00080117 | 0.00069649 | 0.0056354 | 0.023071 | -0.0010339 | 0.0012818 | -0.0018628 | -0.0044967 | -0.0055799 | -0.0021107 | -48.6008 | 70.1157 | -52.7664 | 69.9051 | -51.8188 | -52.5238 | -51.9653 | -51.1047 | 70.1248 | -52.7206 | -52.2629 | -52.4277 | -52.7069 | -52.4277 | -0.068664 | 0.036621 | -0.17395 | 0.87891 | 0.73242 | 0.17395 | 0.80109 | 0.24261 | -0.022888 | 0.045776 | -122.3419 | 0.27008 | 0.27008 | -0.009155 | 0.29297 | 0.013733 | 0.94757 | 122.6715 | 0.29297 | 0.45776 | 122.8821 | 122.8455 | 122.8134 | 122.8226 | -122.8455 | -122.7997 | 122.6028 | 0.43488 | 4.097 | 1.593
3527.1719 | 123.0789 | -52.6611 | 70.079 | -0.068207 | 0.00083526 | 0.062666 | 0.070113 | -0.0013352 | 0.0030463 | 0.0037128 | 0.0047608 | -0.0010339 | 0.00021363 | -0.006349 | -0.0030013 | -0.0072889 | -0.0044605 | -48.555 | 70.0974 | -52.771 | 69.9692 | -51.7685 | -52.478 | -51.9241 | -51.0498 | 70.134 | -52.7115 | -52.2263 | -52.3911 | -52.6566 | -52.3865 | -0.10986 | 0.01831 | -0.10986 | 0.89264 | 0.737 | 0.18311 | 0.84686 | 0.29297 | -0.050354 | 0.054931 | -122.3053 | 0.27008 | 0.27466 | 0.004578 | 0.32501 | 0.054932 | 1.0025 | 122.7402 | 0.32043 | 0.48523 | 122.8683 | 122.8455 | 122.7585 | 122.7951 | -122.85 | -122.7905 | 122.6303 | 0.43488 | 4.1061 | 1.6113
3528.1719 | 123.0423 | -52.6566 | 70.1065 | -0.10635 | -0.0025827 | 0.059676 | 0.069686 | -0.0021896 | 0.0039007 | 0.0049946 | 0.02002 | 0.0013159 | 0.0012818 | 0.001128 | -0.0012925 | -0.0075025 | 0.0013073 | -48.555 | 70.1202 | -52.7664 | 69.9646 | -51.7639 | -52.4872 | -51.9104 | -51.0452 | 70.1248 | -52.7161 | -52.2217 | -52.3865 | -52.6566 | -52.3865 | -0.10986 | 0.013733 | -0.14191 | 0.89264 | 0.74615 | 0.16937 | 0.85602 | 0.27923 | -0.059509 | 0.018311 | -122.3282 | 0.27008 | 0.27008 | 0 | 0.32959 | 0.059509 | 1.0025 | 122.731 | 0.32959 | 0.49438 | 122.8867 | 122.8409 | 122.7768 | 122.7814 | -122.8729 | -122.8226 | 122.6212 | 0.43487 | 4.1016 | 1.6113
3529.1719 | 123.0469 | -52.6657 | 70.1248 | -0.12161 | -0.0017281 | 0.060316 | 0.068404 | -0.005394 | 0.0017645 | 0.0032856 | -0.0043946 | 0.00024775 | -0.00021357 | 5.9824e-05 | -0.0027877 | -0.0066479 | 0.0030163 | -48.5596 | 70.1111 | -52.7573 | 69.9463 | -51.7685 | -52.4826 | -51.9241 | -51.0635 | 70.1614 | -52.7298 | -52.2171 | -52.3911 | -52.6382 | -52.3911 | -0.091553 | -0.013733 | -0.17853 | 0.89722 | 0.74158 | 0.1831 | 0.83313 | 0.27466 | -0.064087 | 0.036621 | -122.3419 | 0.27466 | 0.27466 | 0.027465 | 0.33874 | 0.091552 | 0.98877 | 122.7036 | 0.33874 | 0.5127 | 122.8683 | 122.8912 | 122.7768 | 122.8271 | -122.8821 | -122.8546 | 122.612 | 0.44861 | 4.1061 | 1.6022
3530.1719 | 122.9965 | -52.6794 | 70.0974 | -0.091095 | -0.0015145 | 0.061598 | 0.0699 | 0.0044328 | 0.0030463 | 0.0060626 | -0.0043946 | -0.00060665 | 0.0012818 | -0.0033582 | -0.0027877 | -0.0066479 | -0.00082886 | -48.6008 | 70.0974 | -52.7847 | 69.9188 | -51.8051 | -52.5375 | -51.9608 | -51.1093 | 70.1614 | -52.7069 | -52.2629 | -52.4414 | -52.7023 | -52.4185 | -0.10529 | 0 | -0.17853 | 0.87433 | 0.71869 | 0.14191 | 0.82397 | 0.24719 | -0.027466 | 0.064087 | -122.3602 | 0.23804 | 0.26093 | -0.022889 | 0.28839 | 0.004577 | 0.97961 | 122.7036 | 0.2655 | 0.44403 | 122.8821 | 122.8683 | 122.7768 | 122.8409 | -122.8821 | -122.8043 | 122.5983 | 0.41656 | 4.0787 | 1.5701
3531.1719 | 123.0331 | -52.6611 | 70.1111 | 0.45059 | 0.00019446 | 0.061812 | 0.066695 | -0.00048063 | 0.0026191 | 0.0032856 | -0.01355 | 0.00088875 | 0.00064083 | -0.0052808 | -0.0019333 | -0.0064343 | 0.0013073 | -48.6557 | 70.1385 | -52.7664 | 69.9005 | -51.8509 | -52.5513 | -51.9424 | -51.1093 | 70.134 | -52.7344 | -52.2583 | -52.4323 | -52.7115 | -52.4277 | -0.10529 | 0.027466 | -0.21057 | 0.81024 | 0.71869 | 0.10986 | 0.82397 | 0.21515 | -0.073242 | 0.022888 | -122.3694 | 0.22888 | 0.23346 | -0.050354 | 0.3067 | 0.022888 | 0.91553 | 122.6669 | 0.30212 | 0.47607 | 122.905 | 122.8683 | 122.7997 | 122.7951 | -122.8775 | -122.8455 | 122.5616 | 0.40283 | 4.0054 | 1.5518
3532.1719 | 123.0286 | -52.6382 | 70.1111 | -0.10635 | -0.0015145 | 0.061385 | 0.067977 | 0.00058737 | 0.0041143 | 0.0071308 | 0.013916 | 0.0025975 | 0.00064083 | -0.00015378 | -0.0036423 | -0.0055799 | 0.0023755 | -48.5641 | 70.1019 | -52.7573 | 69.9783 | -51.7731 | -52.4734 | -51.915 | -51.0635 | 70.1477 | -52.7023 | -52.2079 | -52.3819 | -52.6657 | -52.3911 | -0.11902 | -0.009155 | -0.13275 | 0.86517 | 0.72327 | 0.16479 | 0.84229 | 0.28381 | -0.064087 | 0.036621 | -122.319 | 0.25635 | 0.24719 | -0.027465 | 0.31128 | 0.036622 | 0.98419 | 122.7356 | 0.32043 | 0.49439 | 122.8592 | 122.85 | 122.7402 | 122.7859 | -122.8683 | -122.8134 | 122.6166 | 0.4303 | 4.0741 | 1.5747
3533.1719 | 123.0103 | -52.6428 | 70.1111 | -0.075836 | 0.0014761 | 0.060744 | 0.069472 | 0.001442 | 0.00091009 | 0.0060626 | -0.0043946 | 0.00067495 | 0.0014954 | 0.0024096 | -0.0025741 | -0.0047253 | 0.0040845 | -48.5596 | 70.1202 | -52.7481 | 69.9554 | -51.7776 | -52.478 | -51.915 | -51.0498 | 70.1569 | -52.7023 | -52.2308 | -52.4002 | -52.6566 | -52.3819 | -0.10529 | 0.009155 | -0.15564 | 0.86517 | 0.72784 | 0.1648 | 0.83313 | 0.27008 | -0.05951 | 0.045776 | -122.3419 | 0.24261 | 0.26093 | -0.013733 | 0.32043 | 0.045777 | 0.97046 | 122.7036 | 0.30212 | 0.4715 | 122.8683 | 122.8592 | 122.7631 | 122.7997 | -122.8592 | -122.8134 | 122.5983 | 0.41199 | 4.0833 | 1.593
3534.1719 | 123.0286 | -52.652 | 70.1202 | -0.098725 | 0.00019446 | 0.061171 | 0.069259 | -0.0015488 | 0.0024053 | 0.0047808 | 0.0047608 | 0.00024775 | -0.0032044 | 0.00091422 | -0.0025741 | -0.0051527 | 0.0036571 | -48.555 | 70.1065 | -52.7252 | 69.9646 | -51.7593 | -52.478 | -51.8967 | -51.0681 | 70.1477 | -52.6886 | -52.2354 | -52.4002 | -52.6566 | -52.3911 | -0.073242 | -0.013733 | -0.15564 | 0.89264 | 0.75531 | 0.17395 | 0.82855 | 0.24719 | -0.036621 | 0.027466 | -122.3557 | 0.25177 | 0.26093 | -0.004577 | 0.29755 | 0.032044 | 0.96588 | 122.6898 | 0.28839 | 0.45319 | 122.8317 | 122.8363 | 122.7585 | 122.7997 | -122.8455 | -122.8088 | 122.6166 | 0.41656 | 4.097 | 1.5839
3535.1719 | 123.0469 | -52.6154 | 70.1294 | -0.098725 | 0.0012625 | 0.060744 | 0.070754 | -0.00069423 | 0.00091009 | 0.00414 | -0.0074462 | -0.00017945 | 0.0014954 | 0.001128 | -0.0021469 | -0.0083569 | -0.00018806 | -48.5229 | 70.1157 | -52.7252 | 70.0195 | -51.6998 | -52.4139 | -51.8509 | -50.9857 | 70.166 | -52.6794 | -52.1896 | -52.3544 | -52.6108 | -52.3407 | -0.10986 | -0.013733 | -0.10986 | 0.91553 | 0.76447 | 0.20142 | 0.87433 | 0.31128 | -0.064087 | 0.036621 | -122.319 | 0.26093 | 0.27466 | 0.004577 | 0.33874 | 0.068664 | 1.0254 | 122.7448 | 0.32501 | 0.48981 | 122.8409 | 122.8455 | 122.731 | 122.7814 | -122.8546 | -122.8088 | 122.6349 | 0.42572 | 4.0924 | 1.6296
3536.1719 | 123.0698 | -52.6199 | 70.1385 | -0.11398 | -0.00044654 | 0.060957 | 0.067336 | -0.0026168 | 0.0015509 | 0.00414 | -0.0074462 | 3.4148e-05 | -0.00021357 | 0.0017688 | -0.0019333 | -0.0060071 | -0.00061526 | -48.5229 | 70.1431 | -52.7435 | 70.0104 | -51.6953 | -52.446 | -51.8738 | -50.9995 | 70.1752 | -52.6566 | -52.1713 | -52.3544 | -52.6108 | -52.3544 | -0.1236 | 0.004577 | -0.12817 | 0.92468 | 0.74616 | 0.17395 | 0.86975 | 0.29755 | -0.036621 | 0.036621 | -122.3099 | 0.2655 | 0.2655 | 0.009155 | 0.30212 | 0.045776 | 1.0483 | 122.7539 | 0.30212 | 0.48523 | 122.8867 | 122.8317 | 122.7631 | 122.7951 | -122.8821 | -122.7951 | 122.6303 | 0.44861 | 4.097 | 1.6205
3537.1719 | 123.0515 | -52.6474 | 70.1523 | -0.075836 | 0.0010489 | 0.061812 | 0.069259 | 0.00037377 | 0.0034735 | 0.0073444 | 0.001709 | 0.00088875 | 0.0021362 | -0.0037854 | -0.0015061 | -0.0051527 | 0.00023934 | -48.5413 | 70.1065 | -52.7298 | 69.9463 | -51.7548 | -52.4872 | -51.9333 | -51.059 | 70.2026 | -52.6749 | -52.2125 | -52.3773 | -52.6794 | -52.3773 | -0.082397 | -0.045777 | -0.20599 | 0.89264 | 0.71411 | 0.16022 | 0.79651 | 0.24261 | -0.027466 | 0.050354 | -122.3648 | 0.27008 | 0.27008 | -0.032043 | 0.29755 | -0.004577 | 0.97504 | 122.6761 | 0.29755 | 0.46234 | 122.8363 | 122.8775 | 122.7539 | 122.85 | -122.8821 | -122.8271 | 122.5937 | 0.43488 | 4.1061 | 1.5884
3538.1719 | 123.0469 | -52.652 | 70.1294 | -0.12924 | 0.0016899 | 0.061598 | 0.068618 | -0.00069423 | 0.0039007 | 0.0056354 | 0.001709 | 0.0015295 | 0.0029906 | 0.0058276 | -0.0023605 | -0.0077161 | -0.0014697 | -48.5321 | 70.1248 | -52.7618 | 69.9692 | -51.7639 | -52.4963 | -51.915 | -51.0818 | 70.1614 | -52.6611 | -52.2308 | -52.4048 | -52.6428 | -52.3773 | -0.10986 | -0.004578 | -0.16022 | 0.88806 | 0.737 | 0.15564 | 0.84686 | 0.2655 | -0.009155 | 0.032043 | -122.3602 | 0.24719 | 0.27466 | 0.009156 | 0.28381 | 0.018311 | 0.99792 | 122.731 | 0.25635 | 0.4303 | 122.8867 | 122.8226 | 122.7768 | 122.8134 | -122.8912 | -122.7905 | 122.6212 | 0.42114 | 4.1199 | 1.5701
3539.1719 | 123.0286 | -52.6108 | 70.1569 | -0.083466 | -0.00044654 | 0.063094 | 0.067123 | -0.003685 | 0.0021917 | 0.005849 | -0.0074462 | -0.00017945 | 0.00042723 | -0.0033582 | -0.0015061 | -0.0072889 | -0.0016833 | -48.5046 | 70.134 | -52.7298 | 70.0012 | -51.7136 | -52.4506 | -51.8738 | -51.0086 | 70.1797 | -52.6611 | -52.1713 | -52.3453 | -52.6108 | -52.359 | -0.11902 | -0.022888 | -0.15564 | 0.89722 | 0.737 | 0.16022 | 0.85602 | 0.27923 | -0.050354 | 0.022889 | -122.3282 | 0.2655 | 0.25177 | 0 | 0.30212 | 0.050354 | 1.0162 | 122.731 | 0.31586 | 0.48981 | 122.8638 | 122.8409 | 122.7448 | 122.7905 | -122.8867 | -122.818 | 122.612 | 0.43945 | 4.1061 | 1.6022
3540.1719 | 123.0652 | -52.6291 | 70.1431 | -0.052948 | 0.0027579 | 0.061598 | 0.066909 | -0.0013352 | 0.0015509 | 0.007558 | 0.001709 | 0.00046135 | 0.00064083 | -0.00015378 | -0.0023605 | -0.0053663 | 2.554e-05 | -48.5001 | 70.1797 | -52.7115 | 69.9966 | -51.7181 | -52.4323 | -51.8784 | -50.9903 | 70.1889 | -52.6474 | -52.1667 | -52.3453 | -52.597 | -52.3453 | -0.082398 | 0.036622 | -0.14648 | 0.91095 | 0.75073 | 0.19684 | 0.83313 | 0.27924 | -0.018311 | 0.045777 | -122.3099 | 0.28381 | 0.28381 | 0.032043 | 0.30212 | 0.050354 | 0.99335 | 122.7081 | 0.30212 | 0.48065 | 122.8912 | 122.8363 | 122.8088 | 122.818 | -122.8546 | -122.7905 | 122.6257 | 0.46234 | 4.129 | 1.6388
3541.1719 | 123.024 | -52.6062 | 70.1477 | -0.12924 | -0.0019417 | 0.060744 | 0.070113 | -0.0045394 | 0.0021917 | 0.0056354 | 0.010864 | 0.0011023 | 0.0021362 | -0.009126 | -0.0034287 | -0.0064343 | 0.0019483 | -48.5046 | 70.1706 | -52.7023 | 70.0195 | -51.6998 | -52.4551 | -51.8646 | -51.004 | 70.1797 | -52.652 | -52.1667 | -52.3499 | -52.6062 | -52.3407 | -0.096131 | 0.022888 | -0.12817 | 0.90637 | 0.74158 | 0.15106 | 0.83771 | 0.24719 | -0.045777 | 0.032044 | -122.3145 | 0.25635 | 0.2655 | 0 | 0.31128 | 0.045777 | 1.0025 | 122.7219 | 0.30212 | 0.48523 | 122.8729 | 122.8317 | 122.7768 | 122.7859 | -122.85 | -122.7997 | 122.6257 | 0.43945 | 4.1016 | 1.6022
3542.1719 | 123.0148 | -52.6154 | 70.1523 | -0.091095 | 0.0014761 | 0.060744 | 0.068191 | -0.0043258 | -0.00015811 | 0.007558 | 0.001709 | 0.0011023 | 0.001068 | 0.0043322 | -0.0036423 | -0.0051527 | -0.0033923 | -48.4451 | 70.1706 | -52.6886 | 70.0562 | -51.6174 | -52.3682 | -51.8143 | -50.9262 | 70.2118 | -52.6428 | -52.0981 | -52.0386 | -52.8076 | -52.5192 | -0.073243 | 0.01831 | -0.096131 | 0.99792 | 0.80109 | 0.24719 | 0.87433 | 0.32044 | -0.027466 | 0.059509 | -122.2504 | 0.57678 | 0.09613 | -0.19226 | 0.1236 | -0.16479 | 1.0712 | 122.7448 | 0.60425 | 0.54474 | 122.8592 | 122.8546 | 122.7859 | 122.8271 | -122.8409 | -122.7951 | 122.6715 | 0.51727 | 4.1702 | 1.6891
3543.1719 | 123.0377 | -52.597 | 70.1477 | -0.12161 | 0.0014761 | 0.062025 | 0.069045 | -0.00026703 | 0.0017645 | 0.0062762 | -0.0043946 | 0.00046135 | 0.00042723 | -0.0042126 | -0.0040695 | -0.0070753 | -0.0042469 | -48.4314 | 70.1614 | -52.6703 | 70.0516 | -51.6174 | -52.3773 | -51.796 | -50.9079 | 70.2118 | -52.6245 | -52.034 | -52.1713 | -52.9037 | -52.5101 | -0.073242 | 0.013733 | -0.09613 | 0.97961 | 0.80109 | 0.21973 | 0.87433 | 0.29297 | -0.027466 | 0.064087 | -122.1817 | 0.42572 | 0.086975 | -0.3067 | 0.11444 | -0.27924 | 1.0529 | 122.7219 | 0.45319 | 0.59052 | 122.8317 | 122.8363 | 122.7585 | 122.8088 | -122.818 | -122.7722 | 122.6486 | 0.56305 | 4.1656 | 1.6891
3544.1719 | 123.056 | -52.565 | 70.1614 | -0.075836 | -0.00023294 | 0.06053 | 0.067336 | -0.00090783 | 0.0032599 | 0.0037128 | -0.0043946 | -0.00060665 | -0.00021357 | 0.0047594 | -0.0034287 | -0.0053663 | -0.0033923 | -48.4589 | 70.1614 | -52.7069 | 70.0378 | -51.6907 | -52.4231 | -51.8509 | -50.9491 | 70.1935 | -52.6245 | -52.1439 | -52.3132 | -52.6062 | -52.327 | -0.14191 | 0 | -0.1236 | 0.87433 | 0.71411 | 0.14191 | 0.85602 | 0.28381 | -0.05951 | 0.032043 | -122.3053 | 0.25177 | 0.23804 | -0.041199 | 0.29755 | 0.018311 | 1.0162 | 122.7448 | 0.31128 | 0.48065 | 122.8683 | 122.818 | 122.7264 | 122.7585 | -122.8683 | -122.786 | 122.6028 | 0.42114 | 4.1061 | 1.6159
3545.1719 | 123.0515 | -52.5787 | 70.1935 | -0.083466 | -0.00044654 | 0.062666 | 0.068191 | -5.343e-05 | 0.0024053 | 0.0045672 | -0.019653 | 0.0025975 | -0.00064077 | -0.001222 | -0.00086511 | -0.0068615 | 0.00023934 | -48.4543 | 70.1981 | -52.7023 | 70.0424 | -51.6815 | -52.4139 | -51.8417 | -50.9766 | 70.2347 | -52.6474 | -52.1393 | -52.327 | -52.5787 | -52.3041 | -0.1236 | 0.004578 | -0.15106 | 0.89722 | 0.737 | 0.1648 | 0.8606 | 0.28839 | -0.068665 | 0.041199 | -122.3328 | 0.25177 | 0.27466 | 0 | 0.34332 | 0.068665 | 1.0208 | 122.7448 | 0.32043 | 0.50812 | 122.9004 | 122.8821 | 122.7768 | 122.8134 | -122.8958 | -122.8409 | 122.6212 | 0.43945 | 4.1245 | 1.6022
3546.1719 | 123.0469 | -52.5833 | 70.1889 | -0.068207 | -0.00066014 | 0.062239 | 0.067123 | -0.0013352 | 0.00091009 | 0.0052082 | -0.010498 | 0.00024775 | 0.00064083 | -0.0067762 | -0.00022431 | -0.0042981 | -0.00082886 | -48.3948 | 70.1935 | -52.6428 | 70.0928 | -51.5991 | -52.3407 | -51.796 | -50.9445 | 70.2484 | -52.6245 | -52.1164 | -52.2903 | -52.6382 | -52.3544 | -0.059509 | 0.004577 | -0.096131 | 0.98419 | 0.78735 | 0.24261 | 0.84686 | 0.30212 | -0.041199 | 0.059509 | -122.3053 | 0.29297 | 0.22888 | -0.054932 | 0.27008 | -0.013733 | 1.0437 | 122.7356 | 0.33417 | 0.50812 | 122.8363 | 122.8729 | 122.7768 | 122.8317 | -122.8317 | -122.8134 | 122.6761 | 0.46692 | 4.1885 | 1.6388
3547.1719 | 123.0331 | -52.5604 | 70.1981 | -0.075836 | 0.0012625 | 0.061385 | 0.067123 | -0.0024032 | 5.5488e-05 | 0.0060626 | -0.0013428 | 0.00067495 | -0.00064077 | -0.00229 | -0.0010787 | -0.0051527 | -0.0051013 | -48.3994 | 70.2164 | -52.6657 | 70.0974 | -51.59 | -52.3453 | -51.8051 | -50.9628 | 70.2667 | -52.597 | -52.0981 | -52.3727 | -52.597 | -52.2949 | -0.10528 | 0.018311 | -0.10071 | 0.97046 | 0.75531 | 0.21515 | 0.86059 | 0.32043 | -0.036621 | 0.068665 | -122.2961 | 0.18768 | 0.2655 | -0.036621 | 0.30212 | 0 | 1.0757 | 122.7631 | 0.2243 | 0.49896 | 122.8821 | 122.8638 | 122.7768 | 122.8271 | -122.8638 | -122.7951 | 122.6578 | 0.46234 | 4.1611 | 1.5976
3548.1719 | 122.9919 | -52.5879 | 70.2072 | -0.045319 | 0.0019035 | 0.060957 | 0.067763 | 0.0012284 | 0.00069649 | 0.005849 | -0.037964 | 0.00046135 | 0.001068 | 0.0049732 | -0.0012925 | -0.0038709 | -0.0027515 | -48.3948 | 70.1981 | -52.6611 | 70.0745 | -51.6449 | -52.359 | -51.8051 | -50.9445 | 70.2621 | -52.6108 | -52.1439 | -52.3224 | -52.5787 | -52.3132 | -0.073242 | -0.009155 | -0.13275 | 0.94299 | 0.78278 | 0.22888 | 0.85602 | 0.30212 | -0.022888 | 0.054932 | -122.3511 | 0.2655 | 0.27466 | 0.009156 | 0.29755 | 0.032044 | 1.0162 | 122.7356 | 0.28839 | 0.46692 | 122.8592 | 122.8729 | 122.7859 | 122.85 | -122.8683 | -122.818 | 122.6624 | 0.44403 | 4.1931 | 1.6434
3549.1719 | 123.0148 | -52.5604 | 70.2347 | -0.098725 | -0.00023294 | 0.061598 | 0.066909 | 0.0022964 | 0.0013373 | 0.0047808 | -0.037964 | 0.00046135 | 0.00021363 | 0.00091422 | -0.0019333 | -0.0047253 | -0.00018806 | -48.3948 | 70.2255 | -52.6291 | 70.0653 | -51.6266 | -52.359 | -51.8188 | -50.9537 | 70.2713 | -52.5925 | -52.1576 | -52.3087 | -52.5833 | -52.3178 | -0.068664 | -0.009155 | -0.16937 | 0.93384 | 0.74158 | 0.20142 | 0.81024 | 0.27008 | -0.032043 | 0.036621 | -122.3923 | 0.25177 | 0.24262 | -0.022888 | 0.27466 | 0.009155 | 1.0025 | 122.6944 | 0.28381 | 0.43487 | 122.8546 | 122.8638 | 122.786 | 122.8317 | -122.8638 | -122.8271 | 122.6257 | 0.40283 | 4.1656 | 1.6068
3550.1719 | 123.0011 | -52.5604 | 70.2484 | -0.075836 | 0.0010489 | 0.062239 | 0.068618 | 0.0018692 | -0.00037171 | 0.0026446 | 0.010864 | 0.0021703 | 0.0029906 | -0.001222 | -0.0012925 | -0.0053663 | -0.0021107 | -48.381 | 70.2118 | -52.6474 | 70.0653 | -51.6357 | -52.359 | -51.8051 | -50.9262 | 70.253 | -52.6016 | -52.1439 | -52.3132 | -52.5696 | -52.3178 | -0.086975 | -0.036621 | -0.1831 | 0.92468 | 0.75531 | 0.20142 | 0.84228 | 0.28839 | -0.041199 | 0.004578 | -122.3923 | 0.24719 | 0.24262 | -0.009155 | 0.28381 | 0.032044 | 1.0117 | 122.7127 | 0.28839 | 0.45776 | 122.8592 | 122.8546 | 122.7722 | 122.8134 | -122.8958 | -122.85 | 122.6257 | 0.41657 | 4.1794 | 1.6342
3551.1719 | 123.024 | -52.5558 | 70.2118 | -0.052948 | -0.00044654 | 0.060744 | 0.064986 | 0.0012284 | 0.0021917 | 0.0067036 | 0.11462 | -0.0031703 | 0.003418 | 0.001128 | -0.0027877 | -0.0051527 | -0.0012561 | -48.3582 | 70.2118 | -52.6382 | 70.0836 | -51.5991 | -52.3407 | -51.7136 | -51.1505 | 70.2667 | -52.6108 | -52.1118 | -52.2949 | -52.5421 | -52.2675 | -0.082398 | 0 | -0.12817 | 0.95673 | 0.84228 | 0.21515 | 0.92468 | 0.29755 | -0.054932 | 0.054932 | -122.3236 | 0.26093 | 0.28839 | 0.013733 | 0.34332 | 0.068665 | 1.0391 | 122.7219 | 0.31586 | 0.49896 | 122.85 | 122.8775 | 122.7676 | 122.8226 | -122.85 | -122.8226 | 122.6395 | 0.44403 | 4.1977 | 1.4053
3552.1719 | 123.0377 | -52.5558 | 70.2438 | -0.091095 | -0.0019417 | 0.060957 | 0.068191 | 0.0027238 | 0.0032599 | 0.0034992 | 0.20618 | 0.0019567 | 0.0042724 | 0.0043322 | -0.0027877 | -0.0032301 | 0.0010937 | -48.349 | 70.2118 | -52.6337 | 70.0974 | -51.5945 | -52.327 | -51.796 | -51.1093 | 70.2667 | -52.5833 | -52.0798 | -52.2949 | -52.5421 | -52.2812 | -0.07782 | -0.032043 | -0.14648 | 0.9613 | 0.75989 | 0.22888 | 0.83771 | 0.3067 | -0.027466 | 0.022889 | -122.3236 | 0.26093 | 0.27466 | 0.013733 | 0.30212 | 0.041199 | 1.0391 | 122.731 | 0.28839 | 0.50354 | 122.8455 | 122.85 | 122.7676 | 122.8226 | -122.8775 | -122.8271 | 122.6532 | 0.47607 | 4.2068 | 1.4465
3553.1719 | 122.9965 | -52.5467 | 70.2484 | -0.022431 | -0.0017281 | 0.062666 | 0.06755 | -0.0011214 | 0.0015509 | 0.00414 | -0.016602 | 0.0019567 | 0.00064083 | 0.0041186 | -0.0017197 | -0.0072889 | 0.0021619 | -48.3582 | 70.2118 | -52.6382 | 70.0836 | -51.6129 | -52.3636 | -51.8005 | -50.9262 | 70.2805 | -52.5833 | -52.1347 | -52.3132 | -52.5696 | -52.3041 | -0.091553 | -0.036621 | -0.16479 | 0.93384 | 0.74616 | 0.18311 | 0.83771 | 0.27466 | -0.036621 | 0.032044 | -122.3831 | 0.23346 | 0.24262 | -0.022888 | 0.27924 | 0.013733 | 1.0254 | 122.7219 | 0.27008 | 0.44861 | 122.85 | 122.8638 | 122.7585 | 122.8271 | -122.8867 | -122.8317 | 122.6303 | 0.41199 | 4.1885 | 1.6205
3554.1719 | 122.9507 | -52.5879 | 70.2896 | -0.052948 | 0.00062166 | 0.061598 | 0.066268 | 0.00037377 | 0.0019781 | 0.0054218 | -0.022705 | 0.00088875 | -0.00064077 | 0.00070062 | -0.0010787 | -0.0066479 | -0.0018971 | -48.381 | 70.2621 | -52.6108 | 70.0241 | -51.6861 | -52.4048 | -51.86 | -50.9995 | 70.3079 | -52.5879 | -52.2034 | -52.3865 | -52.652 | -52.3682 | -0.022888 | -0.027466 | -0.2655 | 0.90179 | 0.72785 | 0.18311 | 0.75073 | 0.20599 | 0 | 0.01831 | -122.493 | 0.20142 | 0.21973 | -0.064087 | 0.21973 | -0.064087 | 0.92468 | 122.6349 | 0.20142 | 0.38452 | 122.8729 | 122.8958 | 122.85 | 122.8958 | -122.9004 | -122.8775 | 122.612 | 0.38452 | 4.2068 | 1.5884
3555.1719 | 123.0011 | -52.533 | 70.2393 | -0.068207 | 0.00062166 | 0.062025 | 0.068832 | -5.343e-05 | 0.0013373 | 0.0047808 | 0.010864 | 0.00024775 | 0.00085443 | 0.002196 | -0.0021469 | -0.0036573 | 0.0010937 | -48.3398 | 70.2164 | -52.6108 | 70.0928 | -51.6083 | -52.3499 | -51.7868 | -50.8942 | 70.2667 | -52.5833 | -52.1118 | -52.272 | -52.5467 | -52.2858 | -0.07782 | -0.022888 | -0.14649 | 0.92468 | 0.74616 | 0.1831 | 0.82398 | 0.26093 | -0.050354 | 0.027466 | -122.3511 | 0.26093 | 0.24719 | -0.013733 | 0.29755 | 0.036621 | 1.0025 | 122.7036 | 0.31128 | 0.4715 | 122.8271 | 122.85 | 122.7493 | 122.7997 | -122.85 | -122.8226 | 122.6257 | 0.42114 | 4.1931 | 1.6388
3556.1719 | 122.9324 | -52.5604 | 70.285 | -0.083466 | 0.0023307 | 0.062239 | 0.066909 | 0.0012284 | 5.5488e-05 | 0.0064898 | -0.0013428 | -0.00039305 | 0.0012818 | -0.0010084 | -0.0015061 | -0.0049389 | -0.0021107 | -48.3444 | 70.253 | -52.6337 | 70.047 | -51.6403 | -52.3865 | -51.828 | -50.972 | 70.2942 | -52.5925 | -52.1713 | -52.3361 | -52.6199 | -52.3407 | -0.073242 | -0.032043 | -0.23804 | 0.9201 | 0.73242 | 0.17395 | 0.80566 | 0.24719 | -0.032043 | 0.009155 | -122.4564 | 0.2243 | 0.21973 | -0.059509 | 0.25177 | -0.027466 | 0.99335 | 122.6807 | 0.25635 | 0.42114 | 122.8867 | 122.8867 | 122.8134 | 122.8546 | -122.9187 | -122.8775 | 122.6074 | 0.3891 | 4.216 | 1.5884
3557.1719 | 122.9462 | -52.5558 | 70.285 | -0.022431 | 0.00040806 | 0.060316 | 0.0699 | 0.0020828 | 0.00069649 | 0.0047808 | 0.0047608 | 0.0017431 | 0.001068 | 0.00070062 | -0.00086511 | -0.0060071 | -0.00040166 | -48.3307 | 70.2576 | -52.6062 | 70.0699 | -51.6266 | -52.3544 | -51.8188 | -50.9491 | 70.3125 | -52.5879 | -52.1667 | -52.3544 | -52.6062 | -52.3224 | -0.050354 | -0.027466 | -0.21515 | 0.92926 | 0.737 | 0.20142 | 0.78735 | 0.25177 | -0.032044 | 0.027466 | -122.4518 | 0.20142 | 0.23346 | -0.050354 | 0.2655 | -0.01831 | 0.97961 | 122.6761 | 0.23346 | 0.42114 | 122.8638 | 122.9004 | 122.8134 | 122.8683 | -122.8912 | -122.8729 | 122.6257 | 0.3891 | 4.2252 | 1.6067
3558.1719 | 123.0469 | -52.5146 | 70.2667 | 0.038605 | -1.9142e-05 | 0.062666 | 0.069259 | 0.00037377 | 0.0017645 | 0.0052082 | 0.035278 | 0.00088875 | 0.001709 | -0.0059216 | -0.0010787 | -0.0042981 | -0.0021107 | -48.3994 | 70.2713 | -52.6062 | 70.1202 | -51.5945 | -52.3361 | -51.7593 | -50.8804 | 70.2667 | -52.5558 | -52.1027 | -52.2583 | -52.5284 | -52.2491 | -0.091553 | 0.004577 | -0.14648 | 0.9201 | 0.75531 | 0.17853 | 0.84686 | 0.27008 | -0.041199 | 0 | -122.3694 | 0.25635 | 0.2655 | -0.013733 | 0.3067 | 0.027466 | 1.0117 | 122.7264 | 0.29755 | 0.45319 | 122.8775 | 122.8226 | 122.7859 | 122.7814 | -122.8729 | -122.8226 | 122.6349 | 0.41199 | 4.1153 | 1.6342
3559.1719 | 123.056 | -52.5101 | 70.2667 | -0.075836 | 0.0010489 | 0.062453 | 0.066695 | -0.001976 | 0.00069649 | 0.0022174 | -0.016602 | 0.00046135 | 0.00085443 | -0.003999 | -0.0040695 | -0.0068615 | -0.0021107 | -48.3078 | 70.2484 | -52.6016 | 69.9371 | -51.8051 | -52.2766 | -51.7319 | -50.8667 | 70.2667 | -52.5467 | -52.0798 | -52.2308 | -52.4963 | -52.2491 | -0.091553 | -0.018311 | -0.32959 | 0.70496 | 0.7782 | 0.23346 | 0.86975 | 0.32501 | -0.036621 | 0 | -122.3465 | 0.27924 | 0.26093 | 0.013733 | 0.29755 | 0.050354 | 0.79651 | 122.5388 | 0.31586 | 0.46692 | 122.85 | 122.8134 | 122.7585 | 122.7768 | -122.8683 | -122.8134 | 122.4472 | 0.4303 | 4.2023 | 1.6434
3560.1719 | 123.0011 | -52.5055 | 70.2713 | -0.098725 | 0.00083526 | 0.063521 | 0.066695 | 0.00016017 | -0.00058531 | 0.0045672 | -0.0043946 | 0.0017431 | 2.8e-08 | -0.0027174 | -0.0015061 | -0.0047253 | -0.0021107 | -48.3032 | 70.253 | -52.6154 | 70.1157 | -51.5808 | -52.3087 | -51.7731 | -50.8896 | 70.3262 | -52.5558 | -52.0935 | -52.2812 | -52.5421 | -52.2812 | -0.10986 | -0.01831 | -0.15564 | 0.92468 | 0.73242 | 0.19684 | 0.84228 | 0.3067 | -0.050354 | 0.054932 | -122.3648 | 0.2243 | 0.2243 | -0.036621 | 0.27466 | 0.013733 | 1.0345 | 122.731 | 0.27466 | 0.46234 | 122.8683 | 122.8821 | 122.7585 | 122.8317 | -122.8867 | -122.8271 | 122.6212 | 0.41199 | 4.2023 | 1.6159
3561.1719 | 123.0011 | -52.5101 | 70.2667 | -0.11398 | -1.9142e-05 | 0.061385 | 0.066909 | 0.0022964 | 0.0030463 | 0.003072 | 0.02002 | 0.0015295 | -0.00064077 | 0.0036914 | -0.0021469 | -0.0060071 | -0.0010425 | -48.2803 | 70.2759 | -52.5925 | 70.1111 | -51.5762 | -52.3132 | -51.7593 | -50.8713 | 70.3125 | -52.5467 | -52.0844 | -52.2308 | -52.5284 | -52.2629 | -0.082397 | 0.009155 | -0.15564 | 0.93384 | 0.75073 | 0.19684 | 0.83313 | 0.27924 | -0.036621 | 0.045776 | -122.3511 | 0.27924 | 0.24719 | -0.01831 | 0.28381 | 0.018311 | 1.0162 | 122.7036 | 0.31586 | 0.46234 | 122.8683 | 122.8592 | 122.786 | 122.8226 | -122.8592 | -122.8134 | 122.6212 | 0.42572 | 4.2297 | 1.6388
3562.1719 | 123.0423 | -52.5192 | 70.2759 | -0.10635 | 0.00062166 | 0.063307 | 0.067763 | 0.0018692 | 0.0021917 | 0.0047808 | 0.016968 | 0.0011023 | 0.00064083 | 0.0036914 | -0.0015061 | -0.0047253 | -0.0025379 | -48.4543 | 70.253 | -52.597 | 70.1157 | -51.5533 | -52.2629 | -51.7319 | -50.8392 | 70.3354 | -52.5146 | -52.0569 | -52.2263 | -52.5101 | -52.2354 | -0.07782 | -0.022888 | -0.16022 | 0.96588 | 0.78735 | 0.25635 | 0.86517 | 0.33417 | 0.004578 | 0.059509 | -122.3328 | 0.29297 | 0.28381 | 0.009155 | 0.27923 | 0.004577 | 1.0437 | 122.7127 | 0.28839 | 0.45776 | 122.85 | 122.85 | 122.7722 | 122.8546 | -122.8729 | -122.7905 | 122.6349 | 0.46234 | 4.0649 | 1.68
3563.1719 | 122.9828 | -52.5238 | 70.3125 | -0.091095 | 0.00040806 | 0.061812 | 0.067763 | -0.001976 | 0.0015509 | 0.0043536 | 0.0078126 | 0.00024775 | 0.00042723 | 0.0017688 | -0.0015061 | -0.0057935 | 0.0013073 | -48.2941 | 70.2667 | -52.565 | 70.1248 | -51.5717 | -52.2903 | -51.7593 | -50.8804 | 70.3033 | -52.5558 | -52.1072 | -52.2583 | -52.5375 | -52.2446 | -0.041198 | -0.045776 | -0.18768 | 0.95215 | 0.76447 | 0.23346 | 0.80566 | 0.27466 | -0.032043 | -0.009155 | -122.4197 | 0.2655 | 0.27924 | -0.013733 | 0.31128 | 0.01831 | 0.99335 | 122.6898 | 0.29755 | 0.44861 | 122.8317 | 122.8592 | 122.7905 | 122.8271 | -122.8775 | -122.8683 | 122.6486 | 0.41656 | 4.2297 | 1.6434
3564.1719 | 123.0011 | -52.5101 | 70.2988 | -0.014801 | 0.0025443 | 0.060744 | 0.067977 | -0.0032578 | 0.0015509 | 0.0039264 | 0.032227 | -0.0012477 | 2.8e-08 | 0.00091422 | -0.0023605 | -0.0053663 | 0.0019483 | -48.2712 | 70.2667 | -52.6016 | 70.134 | -51.5762 | -52.2949 | -51.7319 | -50.853 | 70.3079 | -52.5375 | -52.0615 | -52.24 | -52.5009 | -52.2217 | -0.091553 | -0.032043 | -0.16479 | 0.93384 | 0.7782 | 0.21515 | 0.86975 | 0.3067 | -0.027466 | 0.009155 | -122.3602 | 0.27008 | 0.28839 | 0.009155 | 0.31586 | 0.036621 | 1.0254 | 122.7356 | 0.29755 | 0.47608 | 122.8683 | 122.8455 | 122.7768 | 122.818 | -122.9004 | -122.8363 | 122.644 | 0.44861 | 4.2389 | 1.6571
3565.1719 | 123.0835 | -52.4689 | 70.2896 | -0.091095 | 0.0010489 | 0.060957 | 0.068191 | 0.0012284 | 0.0030463 | 0.0056354 | 0.026123 | 0.0013159 | 0.00064083 | -0.001222 | -0.0030013 | -0.0070753 | -0.0014697 | -48.2666 | 70.2621 | -52.5833 | 70.166 | -51.5167 | -52.2949 | -51.7181 | -50.8026 | 70.3079 | -52.5238 | -52.0294 | -52.2125 | -52.4826 | -52.2125 | -0.11444 | -0.027466 | -0.1236 | 0.95215 | 0.75073 | 0.17395 | 0.86517 | 0.28839 | -0.054932 | 0.01831 | -122.319 | 0.25635 | 0.25635 | -0.013733 | 0.31128 | 0.041199 | 1.0666 | 122.7493 | 0.31128 | 0.49439 | 122.8455 | 122.8317 | 122.731 | 122.7768 | -122.8729 | -122.8134 | 122.6349 | 0.43945 | 4.2023 | 1.6663
3566.1719 | 123.0698 | -52.4689 | 70.2438 | -0.098725 | 0.00062166 | 0.064162 | 0.066268 | -0.00069423 | 0.00026909 | 0.0034992 | 0.032227 | 0.0019567 | -0.00042717 | 0.0024096 | -0.0051377 | -0.0049389 | -0.0053149 | -48.2712 | 70.2759 | -52.5604 | 70.166 | -51.5442 | -52.2995 | -51.7364 | -50.8255 | 70.3079 | -52.5192 | -52.0248 | -52.2171 | -52.446 | -52.2079 | -0.091553 | 0.032044 | -0.077819 | 0.92468 | 0.73242 | 0.16937 | 0.82398 | 0.26093 | -0.050354 | 0.064087 | -122.2687 | 0.25177 | 0.26093 | 0.022888 | 0.31128 | 0.073242 | 1.0162 | 122.7264 | 0.30212 | 0.49439 | 122.8363 | 122.8271 | 122.7448 | 122.7768 | -122.8043 | -122.7631 | 122.6349 | 0.44403 | 4.1977 | 1.6434
3567.1719 | 122.9782 | -52.5055 | 70.3033 | -0.091095 | -1.9142e-05 | 0.061171 | 0.070754 | 0.0022964 | 0.0013373 | 0.0064898 | -0.077637 | 0.0015295 | -0.00085457 | 0.0054004 | -0.0042831 | -0.0060071 | 0.0017345 | -48.2666 | 70.3171 | -52.6199 | 70.0882 | -51.6037 | -52.3682 | -51.8555 | -50.9079 | 70.3537 | -52.5421 | -52.0981 | -52.3041 | -52.597 | -52.2812 | -0.11444 | 0.013733 | -0.21515 | 0.90179 | 0.65002 | 0.13733 | 0.76447 | 0.25177 | -0.036621 | 0.050354 | -122.4014 | 0.20142 | 0.2243 | -0.091553 | 0.26093 | -0.054932 | 1.0162 | 122.7081 | 0.23804 | 0.44403 | 122.937 | 122.8958 | 122.8226 | 122.8592 | -122.9233 | -122.8455 | 122.5937 | 0.40741 | 4.2389 | 1.5976
3568.1719 | 122.9279 | -52.4826 | 70.3262 | -0.098725 | 0.0010489 | 0.059248 | 0.067763 | 0.00037377 | 0.00048269 | 0.0064898 | 0.047485 | 3.4148e-05 | 0.0019226 | -0.003999 | -0.0034287 | -0.0042981 | 0.00066654 | -48.2391 | 70.2667 | -52.5696 | 70.1569 | -51.4984 | -52.2583 | -51.6998 | -50.7935 | 70.2942 | -52.5192 | -52.0157 | -52.2079 | -52.4551 | -52.2079 | -0.086975 | -0.059509 | -0.16937 | 0.98419 | 0.78278 | 0.2243 | 0.86975 | 0.31128 | -0.036621 | -0.032044 | -122.3419 | 0.27466 | 0.27466 | 0.027466 | 0.31128 | 0.064087 | 1.0712 | 122.7264 | 0.31128 | 0.50354 | 122.8363 | 122.8134 | 122.7493 | 122.7768 | -122.8958 | -122.8455 | 122.6395 | 0.46692 | 4.2435 | 1.6891
3569.1719 | 123.056 | -52.4551 | 70.3033 | -0.045319 | 0.00083526 | 0.062025 | 0.066695 | -0.0026168 | -0.0010125 | 0.0017902 | -0.010498 | 0.00088875 | 0.0036316 | 0.0071094 | -0.0042831 | -0.0072889 | 0.00066654 | -48.2254 | 70.2988 | -52.5513 | 69.96 | -51.6129 | -52.1759 | -51.7502 | -50.8163 | 70.3125 | -52.5375 | -52.034 | -52.2034 | -52.4597 | -52.2034 | -0.096131 | -0.004578 | -0.34332 | 0.84229 | 0.70496 | 0.27924 | 0.80109 | 0.37537 | -0.082398 | 0.009155 | -122.3373 | 0.25177 | 0.25177 | -0.004578 | 0.33417 | 0.07782 | 0.93842 | 122.5113 | 0.33417 | 0.50354 | 122.85 | 122.85 | 122.7539 | 122.7676 | -122.8546 | -122.8409 | 122.4152 | 0.42114 | 4.2297 | 1.6388
3570.1719 | 123.0377 | -52.4506 | 70.2896 | -0.075836 | -0.00023294 | 0.061171 | 0.067977 | 0.0012284 | 0.0019781 | 0.0049946 | 0.035278 | -0.00060665 | 0.00064083 | 0.0026232 | -0.00065151 | -0.0055799 | 0.0032299 | -48.2117 | 70.2896 | -52.5879 | 70.1889 | -51.5121 | -52.2491 | -51.7227 | -50.8209 | 70.34 | -52.4689 | -51.9882 | -52.2354 | -52.4918 | -52.2171 | -0.13733 | 0 | -0.10071 | 0.93842 | 0.72784 | 0.20142 | 0.86517 | 0.33874 | -0.01831 | 0.050354 | -122.2778 | 0.21515 | 0.23346 | -0.041198 | 0.25177 | -0.022888 | 1.0757 | 122.7768 | 0.23346 | 0.48065 | 122.8775 | 122.8088 | 122.7402 | 122.7905 | -122.8775 | -122.7585 | 122.6395 | 0.46234 | 4.2389 | 1.6296
3571.1719 | 123.0103 | -52.4734 | 70.3445 | -0.083466 | 0.0014761 | 0.061598 | 0.069472 | -0.00069423 | 0.0013373 | 0.0071308 | 0.010864 | 0.0036657 | 0.00085443 | -0.002931 | -0.0030013 | -0.0051527 | 0.0019483 | -48.2162 | 70.2988 | -52.5238 | 70.1889 | -51.4847 | -52.2583 | -51.6907 | -50.7706 | 70.3217 | -52.5192 | -52.0248 | -52.1759 | -52.4551 | -52.1988 | -0.050354 | -0.045776 | -0.15564 | 0.98877 | 0.78278 | 0.21515 | 0.83313 | 0.2655 | -0.045776 | -0.022888 | -122.3694 | 0.29755 | 0.27466 | 0.018311 | 0.32043 | 0.064087 | 1.0391 | 122.7127 | 0.34332 | 0.49439 | 122.8226 | 122.8409 | 122.7722 | 122.7951 | -122.8683 | -122.8638 | 122.6624 | 0.44861 | 4.2572 | 1.7029
3572.1719 | 122.9141 | -52.5192 | 70.3217 | -0.091095 | 0.0010489 | 0.063521 | 0.069686 | 0.001442 | 0.0024053 | 0.0052082 | -0.089844 | 0.0015295 | 2.8e-08 | 0.0054004 | -0.0032151 | -0.0047253 | 0.00023934 | -48.2895 | 70.2942 | -52.6108 | 70.0424 | -51.6632 | -52.4185 | -51.8829 | -50.9903 | 70.3674 | -52.5421 | -52.1484 | -52.3819 | -52.6657 | -52.3315 | -0.091553 | -0.027466 | -0.27924 | 0.85602 | 0.63629 | 0.10071 | 0.72784 | 0.19226 | -0.022888 | 0.045777 | -122.4701 | 0.13733 | 0.18768 | -0.14648 | 0.21057 | -0.1236 | 0.94757 | 122.6532 | 0.16022 | 0.39368 | 122.905 | 122.9095 | 122.8134 | 122.8867 | -122.9324 | -122.8638 | 122.5616 | 0.37079 | 4.2297 | 1.5289
3573.1719 | 123.0103 | -52.4826 | 70.3033 | -0.12924 | -0.00066014 | 0.059676 | 0.066909 | -0.001976 | 0.00091009 | 0.0062762 | 0.023071 | -0.00017945 | 0.00085443 | -0.00229 | -0.0019333 | -0.0066479 | 0.0010937 | -48.2712 | 70.2988 | -52.5879 | 70.0974 | -51.5808 | -52.3499 | -51.7685 | -50.885 | 70.3308 | -52.5192 | -52.0706 | -52.2354 | -52.4918 | -52.2217 | -0.10529 | -0.004578 | -0.20599 | 0.90179 | 0.71411 | 0.13275 | 0.8194 | 0.23804 | -0.036621 | 0.027466 | -122.374 | 0.24719 | 0.26093 | -0.009155 | 0.29755 | 0.027466 | 1.0071 | 122.6852 | 0.28381 | 0.44861 | 122.8867 | 122.85 | 122.7814 | 122.8134 | -122.8912 | -122.8226 | 122.58 | 0.41199 | 4.2114 | 1.5976
3574.1719 | 123.0469 | -52.4414 | 70.3262 | -0.10635 | 0.00062166 | 0.061171 | 0.067977 | -5.343e-05 | 0.0045417 | 0.0067036 | 0.029175 | 0.00067495 | 0.0012818 | -0.003999 | -0.0023605 | -0.0053663 | -0.00082886 | -48.2483 | 70.3217 | -52.5421 | 70.134 | -51.5533 | -52.2858 | -51.7136 | -50.853 | 70.34 | -52.5146 | -52.0294 | -52.2034 | -52.4643 | -52.1942 | -0.10071 | -0.004578 | -0.19226 | 0.88806 | 0.72784 | 0.15564 | 0.82855 | 0.25635 | -0.073242 | 0.013733 | -122.3557 | 0.23804 | 0.24719 | -0.022888 | 0.32043 | 0.050354 | 0.98877 | 122.6761 | 0.31128 | 0.48523 | 122.8638 | 122.8546 | 122.7631 | 122.7814 | -122.8683 | -122.8409 | 122.5754 | 0.41199 | 4.1931 | 1.5884
3575.1719 | 123.0057 | -52.4826 | 70.2988 | -0.15213 | 0.0021171 | 0.061385 | 0.068404 | -0.0011214 | 0.00091009 | 0.0039264 | 0.035278 | 0.00067495 | -0.00064077 | -0.0033582 | -0.0032151 | -0.0062207 | -0.0036059 | -48.2529 | 70.2896 | -52.5787 | 70.1248 | -51.5717 | -52.3132 | -51.7364 | -50.8621 | 70.34 | -52.5192 | -52.0386 | -52.2125 | -52.4826 | -52.2079 | -0.09613 | -0.009155 | -0.17395 | 0.91095 | 0.74616 | 0.16937 | 0.84229 | 0.2655 | -0.036621 | 0.041199 | -122.3373 | 0.27008 | 0.27466 | 0 | 0.31128 | 0.036621 | 1.0071 | 122.7036 | 0.3067 | 0.48065 | 122.8683 | 122.8592 | 122.7722 | 122.8226 | -122.8775 | -122.818 | 122.6074 | 0.44403 | 4.2297 | 1.6205
3576.1719 | 123.056 | -52.4597 | 70.3217 | -0.15213 | 0.00083526 | 0.062453 | 0.068832 | -0.0013352 | 0.0019781 | 0.0052082 | 0.029175 | 0.0011023 | -0.00085457 | -0.0048536 | -0.0042831 | -0.0053663 | -0.0023243 | -48.2208 | 70.3171 | -52.5421 | 70.1523 | -51.5442 | -52.2812 | -51.709 | -50.8026 | 70.3491 | -52.5146 | -51.9882 | -52.1759 | -52.4368 | -52.1713 | -0.082397 | -0.004577 | -0.16937 | 0.91553 | 0.75073 | 0.17853 | 0.83313 | 0.26093 | -0.054931 | 0.027466 | -122.3099 | 0.28381 | 0.28839 | 0.022888 | 0.34332 | 0.077819 | 0.99792 | 122.6944 | 0.33875 | 0.52643 | 122.8592 | 122.8638 | 122.7768 | 122.8088 | -122.8638 | -122.8363 | 122.612 | 0.4715 | 4.2389 | 1.6571
3577.1719 | 122.9691 | -52.4872 | 70.3262 | -0.098725 | 0.0023307 | 0.062453 | 0.072463 | 0.0018692 | 0.00069649 | 0.0037128 | -0.098999 | 0.0011023 | 0.0019226 | 0.001128 | -0.0030013 | -0.0034437 | 0.0010937 | -48.2025 | 70.3674 | -52.5604 | 70.1065 | -51.6037 | -52.3773 | -51.828 | -50.8759 | 70.372 | -52.4963 | -52.0844 | -52.3087 | -52.5925 | -52.272 | -0.073242 | 0.041199 | -0.21973 | 0.88348 | 0.65918 | 0.10986 | 0.73242 | 0.18311 | -0.009155 | 0.045776 | -122.4106 | 0.17853 | 0.21515 | -0.10528 | 0.2243 | -0.09613 | 0.95673 | 122.6669 | 0.18768 | 0.41199 | 122.9279 | 122.8683 | 122.8546 | 122.8592 | -122.8867 | -122.8226 | 122.5937 | 0.40283 | 4.2847 | 1.6113
3578.1719 | 123.0331 | -52.4689 | 70.3125 | -0.11398 | -0.00044654 | 0.063094 | 0.068618 | -0.0011214 | 0.0017645 | 0.0034992 | 0.029175 | 0.00024775 | 0.001068 | 0.0034778 | -0.0023605 | -0.0072889 | -0.0031787 | -48.2346 | 70.3217 | -52.5604 | 70.1248 | -51.5671 | -52.3041 | -51.7227 | -50.8667 | 70.3674 | -52.5146 | -52.0203 | -52.2171 | -52.4734 | -52.1988 | -0.091553 | 0.009155 | -0.18768 | 0.90179 | 0.74615 | 0.16479 | 0.83771 | 0.25635 | -0.045776 | 0.054932 | -122.3328 | 0.25177 | 0.27008 | -0.004578 | 0.31586 | 0.041198 | 0.99335 | 122.6852 | 0.29755 | 0.49438 | 122.8821 | 122.8821 | 122.7905 | 122.8363 | -122.8729 | -122.8271 | 122.5937 | 0.44861 | 4.2343 | 1.6022
3579.1719 | 122.9965 | -52.4551 | 70.3033 | -0.037689 | -0.0010873 | 0.061598 | 0.067123 | 0.00251 | 0.0034735 | 0.0037128 | 0.010864 | 0.00088875 | 2.8e-08 | -0.00079478 | -0.0021469 | -0.0040845 | 0.0015209 | -48.2346 | 70.3079 | -52.5421 | 70.1157 | -51.5808 | -52.3453 | -51.7639 | -50.8759 | 70.3537 | -52.5284 | -52.0523 | -52.2446 | -52.5055 | -52.2308 | -0.086975 | 0.004577 | -0.18768 | 0.87433 | 0.69122 | 0.10986 | 0.7782 | 0.19684 | -0.073242 | 0.050354 | -122.3557 | 0.21057 | 0.2243 | -0.050354 | 0.29755 | 0.022888 | 0.9613 | 122.6578 | 0.28381 | 0.47607 | 122.85 | 122.8821 | 122.7631 | 122.8088 | -122.8455 | -122.8317 | 122.5708 | 0.40283 | 4.2206 | 1.5793
3580.1719 | 122.9828 | -52.478 | 70.3125 | -0.11398 | 0.0021171 | 0.062025 | 0.069259 | -0.00069423 | 0.0028327 | 0.00414 | -0.025757 | -0.0014613 | 0.0014954 | 0.0043322 | -0.0027877 | -0.0068615 | -0.00061526 | -48.2208 | 70.3171 | -52.5284 | 70.1477 | -51.5533 | -52.3361 | -51.7548 | -50.853 | 70.3491 | -52.5146 | -52.034 | -52.2537 | -52.533 | -52.2354 | -0.050354 | 0.004578 | -0.16479 | 0.92468 | 0.72327 | 0.14191 | 0.77362 | 0.19226 | -0.036621 | 0.036621 | -122.3465 | 0.2243 | 0.24261 | -0.054932 | 0.27923 | -0.018311 | 0.97504 | 122.6761 | 0.26093 | 0.48065 | 122.8455 | 122.8638 | 122.7951 | 122.8271 | -122.8409 | -122.8271 | 122.6257 | 0.44403 | 4.2572 | 1.6251
3581.1719 | 123.0148 | -52.4597 | 70.3262 | -0.11398 | 0.00083526 | 0.06053 | 0.068832 | 0.00016017 | 0.0028327 | 0.0032856 | 0.0078126 | 0.0017431 | 0.001709 | 0.0015552 | -0.0038559 | -0.0057935 | 0.0036571 | -48.2208 | 70.3262 | -52.5558 | 70.1294 | -51.5808 | -52.327 | -51.7502 | -50.8804 | 70.3537 | -52.5146 | -52.0432 | -52.2354 | -52.5009 | -52.2263 | -0.09613 | 0 | -0.19684 | 0.87891 | 0.70953 | 0.13275 | 0.80566 | 0.22888 | -0.054931 | 0.027466 | -122.3694 | 0.2243 | 0.23346 | -0.041199 | 0.28839 | 0.013732 | 0.97504 | 122.6852 | 0.27923 | 0.4715 | 122.8821 | 122.8683 | 122.7859 | 122.8134 | -122.8821 | -122.8409 | 122.5891 | 0.41656 | 4.2389 | 1.5793
3582.1719 | 122.9965 | -52.4551 | 70.3354 | -0.12161 | 0.0010489 | 0.062025 | 0.067123 | 0.001442 | 0.00069649 | 0.0056354 | -0.022705 | 0.00024775 | 0.0023498 | -0.00015378 | -0.0023605 | -0.0055799 | 0.00088014 | -48.2117 | 70.3217 | -52.5238 | 70.1385 | -51.5533 | -52.3224 | -51.741 | -50.8621 | 70.3629 | -52.4963 | -52.0157 | -52.2308 | -52.5238 | -52.2171 | -0.068665 | -0.013733 | -0.19684 | 0.90179 | 0.71411 | 0.13275 | 0.78278 | 0.20142 | -0.041199 | 0.027466 | -122.3511 | 0.2243 | 0.23804 | -0.068665 | 0.27924 | -0.027466 | 0.97046 | 122.6624 | 0.2655 | 0.48065 | 122.8455 | 122.8592 | 122.7768 | 122.818 | -122.8592 | -122.8317 | 122.5937 | 0.43945 | 4.2435 | 1.593
3583.1719 | 123.0057 | -52.4277 | 70.3079 | -0.068207 | -0.00087374 | 0.06053 | 0.070113 | -0.00069423 | 0.0028327 | 0.0073444 | -0.0043946 | -0.0014613 | 0.00064083 | -0.0014356 | -0.0038559 | -0.0036573 | -0.0014697 | -48.2071 | 70.3079 | -52.5009 | 70.1431 | -51.5533 | -52.3132 | -51.741 | -50.853 | 70.3674 | -52.4872 | -51.9974 | -52.1347 | -52.6108 | -52.2354 | -0.073243 | 0 | -0.16479 | 0.87433 | 0.68664 | 0.11444 | 0.75989 | 0.18768 | -0.05951 | 0.05951 | -122.3053 | 0.29297 | 0.19226 | -0.18311 | 0.25177 | -0.1236 | 0.94757 | 122.644 | 0.35248 | 0.48981 | 122.8088 | 122.8546 | 122.7356 | 122.7951 | -122.8088 | -122.7951 | 122.5708 | 0.4303 | 4.2206 | 1.5747
3584.1719 | 123.0011 | -52.4277 | 70.3308 | -0.12161 | 0.00083526 | 0.061171 | 0.070327 | -0.0026168 | 0.0024053 | 0.0022174 | -0.01355 | 0.0017431 | 0.00085443 | -0.0059216 | -0.0034287 | -0.0062207 | -0.0012561 | -48.1979 | 70.3171 | -52.5192 | 70.1523 | -51.5488 | -52.3087 | -51.7319 | -50.8438 | 70.3629 | -52.478 | -52.0203 | -52.2079 | -52.4963 | -52.1942 | -0.091553 | -0.013733 | -0.17853 | 0.87891 | 0.6958 | 0.11902 | 0.78735 | 0.21057 | -0.050354 | 0.032043 | -122.3511 | 0.21973 | 0.23346 | -0.068665 | 0.28381 | -0.018311 | 0.97046 | 122.6715 | 0.27008 | 0.45776 | 122.8363 | 122.8409 | 122.7448 | 122.7905 | -122.85 | -122.8088 | 122.58 | 0.40741 | 4.2297 | 1.5839
3585.1719 | 122.9965 | -52.4551 | 70.3262 | -0.13687 | -1.9142e-05 | 0.063094 | 0.067977 | 0.00016017 | 0.0030463 | 0.0054218 | -0.03186 | 0.00088875 | 0.001068 | 0.0017688 | -0.0027877 | -0.0051527 | 0.00045294 | -48.1888 | 70.3171 | -52.5192 | 70.166 | -51.5213 | -52.3087 | -51.7273 | -50.8163 | 70.3812 | -52.4918 | -52.0157 | -52.2125 | -52.4918 | -52.1896 | -0.064087 | -0.009155 | -0.16022 | 0.93384 | 0.72784 | 0.14648 | 0.79193 | 0.21057 | -0.036621 | 0.054932 | -122.3419 | 0.24262 | 0.2655 | -0.036621 | 0.30212 | 0 | 0.99793 | 122.6852 | 0.27924 | 0.47607 | 122.8363 | 122.8729 | 122.7722 | 122.8363 | -122.8455 | -122.818 | 122.6212 | 0.43945 | 4.2664 | 1.6388
3586.1719 | 123.0606 | -52.4185 | 70.3308 | -0.10635 | 0.0012625 | 0.061598 | 0.0699 | 0.0016556 | 0.0030463 | 0.0064898 | -0.03186 | 0.00088875 | 0.00085443 | 0.0045458 | -0.0036423 | -0.0042981 | -0.0016833 | -48.1384 | 70.3262 | -52.5009 | 70.2118 | -51.5442 | -52.2354 | -51.6907 | -50.766 | 70.3766 | -52.4918 | -51.9653 | -52.1805 | -52.4689 | -52.153 | -0.082398 | -0.004578 | -0.11902 | 0.87433 | 0.72784 | 0.1831 | 0.81024 | 0.2655 | -0.073242 | 0.045776 | -122.2961 | 0.23804 | 0.2655 | -0.050354 | 0.33874 | 0.022888 | 0.95673 | 122.7127 | 0.31128 | 0.52643 | 122.8271 | 122.8683 | 122.7448 | 122.7951 | -122.8317 | -122.8226 | 122.6303 | 0.45319 | 4.2801 | 1.6525
3587.1719 | 123.0515 | -52.4231 | 70.3217 | -0.12161 | 0.0016899 | 0.063521 | 0.070754 | -0.00069423 | 0.0011237 | 0.0079852 | -0.068481 | 3.4148e-05 | 0.00021363 | 0.00027342 | -0.0027877 | -0.0049389 | -0.0025379 | -48.1247 | 70.3308 | -52.5375 | 70.1935 | -51.4893 | -52.2812 | -51.709 | -50.7889 | 70.3812 | -52.4689 | -51.9379 | -52.2125 | -52.4139 | -52.121 | -0.11444 | 0.009156 | -0.12817 | 0.93384 | 0.71411 | 0.14191 | 0.82855 | 0.25635 | -0.045776 | 0.05951 | -122.2595 | 0.21057 | 0.30212 | 0.009156 | 0.3479 | 0.054932 | 1.0483 | 122.731 | 0.25635 | 0.53101 | 122.8683 | 122.85 | 122.7539 | 122.8043 | -122.8592 | -122.7905 | 122.6166 | 0.48523 | 4.2984 | 1.6342
3588.1719 | 122.9919 | -52.4002 | 70.3629 | -0.13687 | 0.0012625 | 0.060957 | 0.067977 | 0.00080117 | 0.0026191 | 0.0081988 | -0.010498 | 0.00046135 | -0.00042717 | -0.0018628 | -0.0025741 | -0.0038709 | 0.0013073 | -48.1293 | 70.34 | -52.5238 | 70.1797 | -51.4938 | -52.2903 | -51.6998 | -50.798 | 70.3766 | -52.4643 | -51.9791 | -52.1851 | -52.4689 | -52.1759 | -0.1236 | -0.022888 | -0.1831 | 0.90637 | 0.70038 | 0.10986 | 0.82397 | 0.23346 | -0.064086 | 0.013733 | -122.3419 | 0.21515 | 0.22431 | -0.068664 | 0.28839 | -0.004578 | 1.03 | 122.7036 | 0.27923 | 0.48523 | 122.8638 | 122.8409 | 122.7402 | 122.7768 | -122.8867 | -122.8271 | 122.58 | 0.42114 | 4.2709 | 1.6022
3589.1719 | 123.0423 | -52.3865 | 70.3445 | -0.13687 | 0.00040806 | 0.064589 | 0.067763 | -0.0043258 | 0.0043281 | 0.0049946 | 0.03833 | 0.00088875 | 0.00021363 | 0.0013416 | -0.0027877 | -0.0049389 | -0.0025379 | -48.1064 | 70.3171 | -52.5101 | 70.2072 | -51.4618 | -52.5375 | -51.7776 | -50.7935 | 70.3949 | -52.4368 | -51.9424 | -52.1713 | -52.4414 | -52.1393 | -0.1236 | -0.027465 | -0.13733 | 0.92468 | 0.60883 | -0.15106 | 0.73242 | -0.027466 | -0.050354 | 0.050354 | -122.287 | 0.21515 | 0.24719 | -0.054931 | 0.29755 | -0.004577 | 1.0483 | 122.7173 | 0.2655 | 0.49439 | 122.8271 | 122.8317 | 122.7036 | 122.7814 | -122.8546 | -122.7814 | 122.5937 | 0.44403 | 4.2801 | 1.593
3590.1719 | 123.0057 | -52.4185 | 70.3491 | -0.15976 | 0.0025443 | 0.062025 | 0.0699 | -0.0015488 | 0.0041143 | 0.007558 | -0.0043946 | 0.00024775 | 0.00021363 | 0.00048702 | -0.0015061 | -0.0036573 | 0.0030163 | -48.1155 | 70.34 | -52.4918 | 70.2209 | -51.4618 | -52.2491 | -51.6953 | -50.766 | 70.4041 | -52.4414 | -51.947 | -52.1622 | -52.4414 | -52.153 | -0.073242 | -0.009155 | -0.12817 | 0.95673 | 0.72327 | 0.16937 | 0.79651 | 0.24261 | -0.022888 | 0.054932 | -122.2961 | 0.25635 | 0.2655 | -0.022888 | 0.28839 | 0 | 1.03 | 122.7127 | 0.27924 | 0.49439 | 122.8317 | 122.8455 | 122.7585 | 122.8226 | -122.8409 | -122.7905 | 122.6395 | 0.4715 | 4.303 | 1.6525
3591.1719 | 123.0469 | -52.3727 | 70.3629 | -0.091095 | -0.0010873 | 0.062239 | 0.069045 | -5.343e-05 | 0.0043281 | 0.0062762 | -0.025757 | 3.4148e-05 | -0.00085457 | 0.0026232 | -0.0023605 | -0.0055799 | 0.00023934 | -48.0377 | 70.3079 | -52.5055 | 70.2209 | -51.4618 | -52.2491 | -51.6815 | -50.7294 | 70.3949 | -52.4551 | -51.9424 | -52.153 | -52.4368 | -52.1347 | -0.13275 | -0.054932 | -0.14191 | 0.91095 | 0.69122 | 0.1236 | 0.82397 | 0.25635 | -0.082397 | 0.032043 | -122.3053 | 0.21973 | 0.23804 | -0.064087 | 0.32043 | 0.01831 | 1.0437 | 122.7264 | 0.30212 | 0.5127 | 122.8134 | 122.85 | 122.6807 | 122.7676 | -122.8683 | -122.818 | 122.5937 | 0.4303 | 4.335 | 1.6434
3592.1719 | 123.056 | -52.4048 | 70.3491 | -0.12161 | 0.0014761 | 0.062239 | 0.070327 | -0.0038986 | 0.0017645 | 0.0043536 | 0.03833 | 0.00024775 | 0.00085443 | 0.0041186 | -0.0019333 | -0.0040845 | 0.0028027 | -48.0927 | 70.3583 | -52.4918 | 70.2026 | -51.4389 | -52.5055 | -51.8005 | -50.766 | 70.3857 | -52.4414 | -51.9241 | -52.1713 | -52.4323 | -52.1255 | -0.086975 | 0.009155 | -0.14648 | 0.96588 | 0.60425 | -0.10071 | 0.69122 | -0.013733 | -0.036621 | 0.036621 | -122.2733 | 0.23346 | 0.27924 | -0.027466 | 0.31586 | 0.009155 | 1.0529 | 122.6944 | 0.27008 | 0.51727 | 122.85 | 122.8271 | 122.7631 | 122.7905 | -122.8409 | -122.7905 | 122.6074 | 0.48065 | 4.3121 | 1.6388
3593.1719 | 123.0148 | -52.3819 | 70.3629 | -0.091095 | 0.0033987 | 0.061385 | 0.066695 | -0.00026703 | 0.0045417 | 0.0060626 | -0.016602 | -0.00082025 | -0.001709 | -0.00058098 | -0.0040695 | -0.0057935 | -0.0018971 | -48.0927 | 70.3491 | -52.4643 | 70.2209 | -51.4664 | -52.2308 | -51.6541 | -50.7248 | 70.4224 | -52.4185 | -51.9333 | -52.1484 | -52.4277 | -52.121 | -0.082397 | -0.013733 | -0.14191 | 0.91553 | 0.72784 | 0.15106 | 0.81024 | 0.23346 | -0.036621 | 0.059509 | -122.2961 | 0.23346 | 0.26093 | -0.045776 | 0.29755 | -0.009155 | 0.99792 | 122.6852 | 0.27008 | 0.48523 | 122.8134 | 122.8409 | 122.731 | 122.8043 | -122.8271 | -122.7814 | 122.6028 | 0.44861 | 4.2892 | 1.6571
3594.1719 | 123.0011 | -52.4094 | 70.372 | -0.068207 | -0.0010873 | 0.059889 | 0.070113 | -0.00090783 | 0.0019781 | 0.005849 | -0.074585 | 0.0021703 | -0.00021357 | 0.0026232 | -0.0034287 | -0.0049389 | 0.0021619 | -48.1384 | 70.3903 | -52.5192 | 70.1385 | -51.5762 | -52.3407 | -51.7731 | -50.8438 | 70.4269 | -52.446 | -52.0203 | -52.2125 | -52.5101 | -52.1805 | -0.10986 | 0.018311 | -0.23346 | 0.83313 | 0.63629 | 0.068665 | 0.74616 | 0.17853 | -0.036621 | 0.054932 | -122.3923 | 0.19684 | 0.22888 | -0.10071 | 0.2655 | -0.064087 | 0.94299 | 122.6578 | 0.23346 | 0.42572 | 122.9095 | 122.8729 | 122.7997 | 122.8363 | -122.8912 | -122.818 | 122.5479 | 0.3891 | 4.2709 | 1.5656
3595.1719 | 123.0331 | -52.3819 | 70.3674 | -0.1445 | 0.00062166 | 0.062453 | 0.068404 | -0.00090783 | 0.00026909 | 0.005849 | -0.050171 | 0.00067495 | -0.00021357 | 0.0041186 | -0.0027877 | -0.0040845 | 0.0021619 | -48.1247 | 70.3995 | -52.5192 | 70.166 | -51.5259 | -52.2903 | -51.7273 | -50.7935 | 70.4361 | -52.4139 | -51.9516 | -52.1667 | -52.4094 | -52.1118 | -0.13733 | 0.032043 | -0.20142 | 0.85602 | 0.6546 | 0.091553 | 0.79193 | 0.22888 | -0.032043 | 0.068664 | -122.319 | 0.21515 | 0.27008 | -0.027466 | 0.30212 | 0.004577 | 0.99335 | 122.6852 | 0.24719 | 0.46234 | 122.9187 | 122.85 | 122.7814 | 122.818 | -122.8867 | -122.7814 | 122.5479 | 0.4303 | 4.2572 | 1.5884
3596.1719 | 123.0103 | -52.4048 | 70.3857 | -0.052948 | 0.00062166 | 0.062239 | 0.068404 | -0.00026703 | 0.0021917 | 0.0079852 | -0.056274 | 0.00067495 | 0.0025634 | -0.002931 | -0.0023605 | -0.0021619 | 0.00045294 | -48.1293 | 70.3903 | -52.4826 | 70.1477 | -51.5671 | -52.3315 | -51.7685 | -50.8072 | 70.4407 | -52.446 | -51.9653 | -52.1896 | -52.4643 | -52.1484 | -0.07782 | 0.004578 | -0.23804 | 0.83771 | 0.63629 | 0.073242 | 0.71411 | 0.15106 | -0.041199 | 0.054932 | -122.3511 | 0.21515 | 0.25635 | -0.059509 | 0.29755 | -0.01831 | 0.91553 | 122.6303 | 0.25635 | 0.48065 | 122.8729 | 122.8867 | 122.7951 | 122.8455 | -122.8683 | -122.8317 | 122.5525 | 0.43945 | 4.2755 | 1.5976
3597.1719 | 123.0286 | -52.3727 | 70.372 | -0.12161 | 0.00083526 | 0.059676 | 0.070327 | 0.004219 | 0.0015509 | 0.0028582 | -0.019653 | 0.00024775 | 0.00064083 | -0.00015378 | -0.0042831 | -0.0053663 | -0.0021107 | -48.1018 | 70.372 | -52.5009 | 70.2072 | -51.4893 | -52.2675 | -51.6907 | -50.7523 | 70.4407 | -52.4323 | -51.9241 | -52.1301 | -52.4139 | -52.0981 | -0.12817 | 0 | -0.1648 | 0.88348 | 0.68207 | 0.10529 | 0.81024 | 0.23346 | -0.059509 | 0.068665 | -122.2961 | 0.24262 | 0.27466 | -0.041198 | 0.33417 | 0.018311 | 1.0117 | 122.7081 | 0.30212 | 0.50812 | 122.8729 | 122.8729 | 122.7448 | 122.8134 | -122.8729 | -122.8043 | 122.58 | 0.44861 | 4.2709 | 1.6205
3598.1719 | 122.9874 | -52.3727 | 70.3674 | -0.12924 | 0.00062166 | 0.063521 | 0.06755 | -0.0015488 | 0.00026909 | 0.0069172 | 0.010864 | 0.0013159 | 0.0019226 | 0.0013416 | -0.0025741 | -0.0057935 | -0.0033923 | -48.0652 | 70.3766 | -52.4643 | 70.2393 | -51.4389 | -52.24 | -51.6495 | -50.7156 | 70.4086 | -52.4231 | -51.9196 | -52.1484 | -52.4048 | -52.1164 | -0.091552 | 0.009155 | -0.12817 | 0.93384 | 0.72327 | 0.13275 | 0.81482 | 0.2243 | -0.050354 | 0.041198 | -122.287 | 0.22431 | 0.25635 | -0.032043 | 0.3067 | 0.018311 | 1.0254 | 122.7036 | 0.27466 | 0.50354 | 122.8409 | 122.8317 | 122.7493 | 122.7814 | -122.8317 | -122.7905 | 122.612 | 0.45319 | 4.3076 | 1.6571
3599.1719 | 123.0103 | -52.3636 | 70.3857 | -0.12161 | -1.9142e-05 | 0.060744 | 0.069686 | -0.00069423 | -0.00037171 | 0.0062762 | -0.071533 | 0.0013159 | 0.0021362 | 0.0075366 | -0.0036423 | -0.0028027 | -0.0023243 | -48.111 | 70.4224 | -52.4918 | 70.166 | -51.5305 | -52.3087 | -51.7364 | -50.7843 | 70.4315 | -52.4231 | -51.9516 | -52.1667 | -52.4643 | -52.1255 | -0.12817 | 0.036621 | -0.21973 | 0.83313 | 0.62714 | 0.054931 | 0.75531 | 0.1831 | -0.05951 | 0.045777 | -122.3373 | 0.19684 | 0.23804 | -0.10071 | 0.29755 | -0.041198 | 0.9613 | 122.6578 | 0.25635 | 0.4715 | 122.9141 | 122.8546 | 122.7859 | 122.7951 | -122.8775 | -122.8088 | 122.5296 | 0.41199 | 4.2526 | 1.5793
3600.1719 | 122.9736 | -52.3911 | 70.4453 | -0.045319 | -0.0010873 | 0.062025 | 0.073104 | 0.00016017 | 0.0026191 | 0.0094806 | -0.022705 | 0.00046135 | 0.00042723 | 0.0028368 | -0.00065151 | -0.0053663 | 0.0034435 | -48.1293 | 70.4315 | -52.4734 | 70.3217 | -51.3382 | -52.359 | -51.7868 | -50.885 | 70.5002 | -52.4231 | -51.9974 | -52.2446 | -52.5513 | -52.1896 | -0.082398 | -0.013732 | -0.1236 | 1.0529 | 0.60425 | 0.032043 | 0.68665 | 0.11444 | -0.032044 | 0.054932 | -122.4426 | 0.14648 | 0.20142 | -0.16022 | 0.23346 | -0.12817 | 1.1353 | 122.7951 | 0.17853 | 0.42572 | 122.905 | 122.9233 | 122.8226 | 122.8912 | -122.9187 | -122.8683 | 122.7127 | 0.39368 | 4.2618 | 1.506
3601.1719 | 122.9004 | -52.4002 | 70.4498 | -0.13687 | -1.9142e-05 | 0.061598 | 0.070113 | -0.0011214 | 0.0034735 | 0.0043536 | -0.062378 | 0.0021703 | -0.00042717 | 0.0043322 | -0.0023605 | -0.0038709 | 0.0034435 | -48.0927 | 70.4544 | -52.4918 | 70.1065 | -51.5945 | -52.3636 | -51.7731 | -50.7477 | 70.459 | -52.4506 | -52.0432 | -52.1667 | -52.5055 | -52.1942 | -0.091552 | 0.004578 | -0.34332 | 0.80566 | 0.62714 | 0.036622 | 0.71869 | 0.12817 | -0.050354 | 0.009155 | -122.493 | 0.23346 | 0.20599 | -0.10529 | 0.25635 | -0.054931 | 0.89722 | 122.5983 | 0.28381 | 0.40741 | 122.9462 | 122.9095 | 122.8546 | 122.8592 | -122.9416 | -122.9004 | 122.5067 | 0.35706 | 4.3076 | 1.6525
3602.1719 | 122.9416 | -52.3727 | 70.4224 | -0.10635 | 0.0019035 | 0.059889 | 0.068832 | -0.0041122 | 0.00069649 | 0.0032856 | -0.037964 | 0.0028113 | 2.8e-08 | 0.0034778 | -0.00065151 | -0.0045117 | -0.0031787 | -48.0469 | 70.459 | -52.4734 | 70.1477 | -51.5488 | -52.3041 | -51.7548 | -50.8484 | 70.4773 | -52.4231 | -51.9882 | -52.2171 | -52.4918 | -52.1759 | -0.10071 | 0.036621 | -0.27466 | 0.82398 | 0.61798 | 0.068665 | 0.71869 | 0.16937 | -0.050354 | 0.054932 | -122.4106 | 0.15564 | 0.19684 | -0.11902 | 0.24719 | -0.068664 | 0.92468 | 122.6212 | 0.20599 | 0.43488 | 122.9324 | 122.9004 | 122.8317 | 122.85 | -122.8958 | -122.8455 | 122.5204 | 0.38452 | 4.3259 | 1.5244
3603.1719 | 122.9874 | -52.359 | 70.3812 | -0.15213 | -0.00066014 | 0.06053 | 0.068191 | -0.0032578 | 0.0017645 | 0.0060626 | 0.001709 | 0.00088875 | -0.00064077 | -0.0014356 | -0.0017197 | -0.0049389 | 0.0023755 | -48.0194 | 70.4361 | -52.3956 | 70.2393 | -51.4206 | -52.2125 | -51.6449 | -50.7339 | 70.4315 | -52.3819 | -51.9287 | -52.1301 | -52.3911 | -52.1072 | -0.036621 | 0.054931 | -0.14191 | 0.93842 | 0.71411 | 0.14648 | 0.75073 | 0.18311 | -0.022888 | 0.050354 | -122.3099 | 0.22888 | 0.25177 | -0.032043 | 0.27466 | -0.009155 | 0.97504 | 122.6349 | 0.25177 | 0.45319 | 122.8317 | 122.8134 | 122.7951 | 122.7905 | -122.7768 | -122.7631 | 122.5983 | 0.4303 | 4.3396 | 1.6251
3604.1719 | 122.9645 | -52.3682 | 70.4315 | -0.091095 | -0.00023294 | 0.06288 | 0.070113 | 0.0029374 | 0.0013373 | 0.00414 | -0.050171 | 3.4148e-05 | 0.0023498 | 0.0032642 | -0.0023605 | -0.0038709 | 0.0028027 | -48.0652 | 70.4544 | -52.4643 | 70.1706 | -51.5213 | -52.2949 | -51.7227 | -50.8072 | 70.491 | -52.4048 | -51.9791 | -52.2034 | -52.4918 | -52.153 | -0.09613 | 0.022888 | -0.26093 | 0.84686 | 0.64545 | 0.073242 | 0.74158 | 0.16937 | -0.036621 | 0.059509 | -122.4106 | 0.16479 | 0.21515 | -0.1236 | 0.25177 | -0.086975 | 0.94299 | 122.6349 | 0.20142 | 0.42572 | 122.9187 | 122.8958 | 122.8226 | 122.8592 | -122.8958 | -122.8363 | 122.5388 | 0.3891 | 4.303 | 1.561
3605.1719 | 122.9599 | -52.359 | 70.4224 | -0.060578 | -0.00066014 | 0.062239 | 0.069259 | 0.00016017 | 0.0019781 | 0.0049946 | -0.077637 | 0.0032385 | 0.0029906 | -0.0020764 | -0.0015061 | -0.0034437 | 0.00066654 | -48.0606 | 70.4865 | -52.4872 | 70.1706 | -51.5488 | -52.3132 | -51.7273 | -50.8118 | 70.5002 | -52.4002 | -51.9791 | -52.1988 | -52.478 | -52.1805 | -0.12817 | 0.064087 | -0.25177 | 0.81024 | 0.63171 | 0.045777 | 0.75989 | 0.17395 | -0.041199 | 0.07782 | -122.4014 | 0.16022 | 0.17853 | -0.11902 | 0.21973 | -0.077819 | 0.93842 | 122.6578 | 0.20142 | 0.42114 | 122.9736 | 122.9004 | 122.8455 | 122.8592 | -122.9095 | -122.8226 | 122.5296 | 0.37994 | 4.2984 | 1.5472
3606.1719 | 122.9416 | -52.3544 | 70.4544 | -0.098725 | 0.0021171 | 0.061812 | 0.064986 | -0.0013352 | -0.00079891 | 0.007558 | -0.047119 | 0.00088875 | 0.001068 | 0.00048702 | -0.0023605 | -0.0038709 | -0.00040166 | -48.0469 | 70.4544 | -52.4826 | 70.1431 | -51.5854 | -52.2171 | -51.7136 | -50.8347 | 70.5002 | -52.3956 | -51.9928 | -52.2034 | -52.4872 | -52.1484 | -0.12817 | 0 | -0.31128 | 0.76904 | 0.64087 | 0.13733 | 0.76904 | 0.2655 | -0.041199 | 0.045776 | -122.4472 | 0.15106 | 0.20599 | -0.13275 | 0.24719 | -0.091553 | 0.89722 | 122.6257 | 0.19226 | 0.40283 | 122.937 | 122.8958 | 122.8088 | 122.8546 | -122.937 | -122.85 | 122.4976 | 0.36163 | 4.3076 | 1.5198
3607.1719 | 122.9187 | -52.3773 | 70.4773 | -0.098725 | -0.00087374 | 0.059676 | 0.071609 | -0.0028304 | 0.00069649 | 0.0054218 | -0.059326 | 0.0013159 | 0.001068 | 0.0030506 | -0.00043791 | -0.0057935 | -0.0012561 | -48.024 | 70.459 | -52.4597 | 70.1843 | -51.5121 | -52.2537 | -51.7136 | -50.8118 | 70.5185 | -52.4002 | -51.9882 | -52.2217 | -52.5055 | -52.1713 | -0.082398 | -0.018311 | -0.29297 | 0.86517 | 0.66376 | 0.1236 | 0.74615 | 0.20599 | -0.022889 | 0.041199 | -122.4655 | 0.15564 | 0.20599 | -0.12817 | 0.22888 | -0.10529 | 0.94757 | 122.644 | 0.17853 | 0.41199 | 122.9187 | 122.9187 | 122.8363 | 122.8958 | -122.937 | -122.8775 | 122.5616 | 0.3891 | 4.3533 | 1.5656
3608.1719 | 122.9919 | -52.3041 | 70.4269 | -0.13687 | -0.0013009 | 0.060744 | 0.065414 | 0.00058737 | 0.00026909 | 0.0020038 | 0.035278 | 0.0034521 | 0.00021363 | 0.00048702 | -0.0025741 | -0.0081433 | 2.554e-05 | -48.0057 | 70.4498 | -52.4002 | 70.2393 | -51.4206 | -52.2079 | -51.6357 | -50.7202 | 70.4636 | -52.3727 | -51.9012 | -52.0935 | -52.3865 | -52.0889 | -0.096131 | 0.022888 | -0.18768 | 0.88348 | 0.66833 | 0.09613 | 0.76447 | 0.19226 | -0.068665 | 0.036621 | -122.3282 | 0.21057 | 0.21515 | -0.082398 | 0.28381 | -0.013733 | 0.97962 | 122.6395 | 0.27924 | 0.4715 | 122.85 | 122.8363 | 122.7539 | 122.7676 | -122.8271 | -122.7997 | 122.5433 | 0.40283 | 4.2984 | 1.5839
3609.1719 | 122.9141 | -52.3224 | 70.5002 | -0.068207 | 0.00019446 | 0.061812 | 0.070541 | 0.004219 | 0.00069649 | 0.0034992 | -0.044067 | 0.0015295 | 0.0023498 | 0.00048702 | -0.0034287 | -0.0064343 | 0.0021619 | -47.9782 | 70.4773 | -52.4185 | 70.2301 | -51.4526 | -52.2308 | -51.6678 | -50.7477 | 70.5048 | -52.3682 | -51.947 | -52.1576 | -52.4506 | -52.1393 | -0.09613 | -0.022888 | -0.27008 | 0.86975 | 0.6546 | 0.091553 | 0.75073 | 0.18768 | -0.045776 | 0.004578 | -122.4472 | 0.16479 | 0.18311 | -0.12817 | 0.22888 | -0.082398 | 0.96588 | 122.6486 | 0.21057 | 0.42114 | 122.8958 | 122.8729 | 122.7997 | 122.8271 | -122.9187 | -122.8683 | 122.5525 | 0.37537 | 4.3442 | 1.5747
3610.1719 | 122.9004 | -52.3407 | 70.491 | -0.10635 | 0.00062166 | 0.064162 | 0.070113 | -0.0028304 | 0.0032599 | 0.0064898 | -0.028809 | 0.0030249 | 0.001068 | -0.00079478 | -0.0021469 | -0.0049389 | 0.00088014 | -48.0011 | 70.4819 | -52.4139 | 70.2164 | -51.4938 | -52.2446 | -51.7044 | -50.7889 | 70.5185 | -52.3773 | -51.9653 | -52.1759 | -52.4734 | -52.1576 | -0.073242 | -0.009155 | -0.27466 | 0.84686 | 0.63629 | 0.09613 | 0.70953 | 0.16937 | -0.036621 | 0.027466 | -122.4564 | 0.1648 | 0.18311 | -0.13275 | 0.21973 | -0.096131 | 0.9201 | 122.6303 | 0.20142 | 0.41199 | 122.8958 | 122.8958 | 122.8226 | 122.8592 | -122.905 | -122.8683 | 122.5571 | 0.37537 | 4.3396 | 1.5518
3611.1719 | 122.9095 | -52.3499 | 70.491 | -0.33524 | 0.0016899 | 0.060316 | 0.069472 | 0.00080117 | 0.0030463 | 0.0056354 | -0.01355 | 0.00067495 | -0.00064077 | -0.0031446 | 0.00041649 | -0.0060071 | -0.00061526 | -47.8546 | 70.4453 | -52.446 | 70.166 | -51.4893 | -52.2766 | -51.7181 | -50.7889 | 70.5231 | -52.3956 | -51.9562 | -52.1667 | -52.4643 | -52.1301 | -0.09613 | -0.045777 | -0.32501 | 0.8606 | 0.63171 | 0.073243 | 0.72784 | 0.16937 | -0.045776 | 0.032043 | -122.4472 | 0.18311 | 0.21973 | -0.11444 | 0.2655 | -0.068664 | 0.95673 | 122.612 | 0.22888 | 0.43945 | 122.8912 | 122.9187 | 122.7951 | 122.8729 | -122.937 | -122.8867 | 122.5159 | 0.39368 | 4.4952 | 1.561
3612.1719 | 122.905 | -52.3453 | 70.4865 | -0.052948 | 0.0012625 | 0.063094 | 0.070541 | 0.003151 | 0.00026909 | 0.007558 | -0.034912 | 0.0034521 | -0.00064077 | -0.0010084 | -0.0027877 | -0.0055799 | -0.00061526 | -47.9782 | 70.5093 | -52.4139 | 70.2072 | -51.4709 | -52.2491 | -51.6953 | -50.7935 | 70.5048 | -52.3727 | -51.9608 | -52.1713 | -52.4689 | -52.1439 | -0.068664 | 0.022888 | -0.27924 | 0.87433 | 0.65002 | 0.09613 | 0.71869 | 0.16479 | -0.027466 | 0.018311 | -122.4472 | 0.17395 | 0.20142 | -0.1236 | 0.22888 | -0.09613 | 0.94299 | 122.6212 | 0.20142 | 0.41199 | 122.9233 | 122.8775 | 122.8546 | 122.85 | -122.9004 | -122.8592 | 122.5525 | 0.38452 | 4.3671 | 1.5518
3613.1719 | 122.9782 | -52.3041 | 70.5002 | -0.091095 | 0.00083526 | 0.062239 | 0.064986 | -0.0028304 | 0.0034735 | 0.0064898 | 0.062744 | 3.4148e-05 | 0.0021362 | -0.006349 | -0.0019333 | -0.0072889 | 2.554e-05 | -47.905 | 70.5139 | -52.327 | 70.3308 | -51.3153 | -52.0935 | -51.5442 | -50.6378 | 70.5093 | -52.3132 | -51.8784 | -52.0523 | -52.3041 | -52.0386 | -0.022888 | 0.013733 | -0.16937 | 0.98877 | 0.75989 | 0.21057 | 0.78278 | 0.23346 | -0.009155 | 0.009155 | -122.3785 | 0.25177 | 0.2655 | 0 | 0.27466 | 0.009155 | 1.0117 | 122.6578 | 0.26093 | 0.43487 | 122.8409 | 122.8226 | 122.818 | 122.8134 | -122.8271 | -122.8134 | 122.6349 | 0.42572 | 4.3991 | 1.6663
3614.1719 | 122.9324 | -52.3087 | 70.5322 | -0.098725 | 0.0025443 | 0.062666 | 0.068618 | -0.0015488 | 0.0019781 | 0.0054218 | -0.028809 | 0.00046135 | 0.00021363 | 0.0075366 | -0.0021469 | -0.0047253 | 0.0013073 | -47.9187 | 70.4956 | -52.4139 | 70.2805 | -51.4069 | -52.1576 | -51.6266 | -50.6699 | 70.5414 | -52.3499 | -51.8784 | -52.0844 | -52.359 | -52.0798 | -0.10528 | -0.036622 | -0.25177 | 0.90179 | 0.68207 | 0.15106 | 0.78735 | 0.25635 | -0.041199 | 0.009155 | -122.4106 | 0.2243 | 0.22888 | -0.050354 | 0.27008 | -0.009155 | 1.0071 | 122.6944 | 0.2655 | 0.4715 | 122.9095 | 122.8912 | 122.8043 | 122.85 | -122.9462 | -122.8821 | 122.5891 | 0.4303 | 4.39 | 1.6388
3615.1719 | 122.9599 | -52.3132 | 70.5048 | -0.052948 | 0.0012625 | 0.062025 | 0.070541 | 0.00058737 | 0.0043281 | 0.0056354 | -0.016602 | 0.0019567 | 0.003418 | 0.0034778 | -0.0027877 | -0.0034437 | -0.0014697 | -48.0011 | 70.5048 | -52.4002 | 70.253 | -51.4069 | -52.1439 | -51.6083 | -50.679 | 70.5688 | -52.3361 | -51.8967 | -52.1072 | -52.3865 | -52.0935 | -0.086976 | 0 | -0.25177 | 0.90637 | 0.70496 | 0.16937 | 0.79193 | 0.25635 | -0.022889 | 0.064087 | -122.4014 | 0.20599 | 0.21973 | -0.073243 | 0.24262 | -0.050354 | 0.99335 | 122.6532 | 0.22888 | 0.43945 | 122.905 | 122.905 | 122.818 | 122.8821 | -122.905 | -122.8409 | 122.5662 | 0.41656 | 4.3121 | 1.6342
3616.1719 | 122.9691 | -52.2949 | 70.5276 | -0.10635 | 0.00019446 | 0.06288 | 0.067763 | -0.00069423 | 0.00069649 | 0.0039264 | -0.016602 | 0.0019567 | 0.002777 | 5.9824e-05 | -0.0030013 | -0.0049389 | -0.00040166 | -47.9187 | 70.5368 | -52.3865 | 70.2759 | -51.3886 | -52.1484 | -51.622 | -50.5966 | 70.5505 | -52.3315 | -51.8555 | -52.0889 | -52.3865 | -52.0569 | -0.091553 | 0.009155 | -0.25177 | 0.90637 | 0.67291 | 0.14648 | 0.76447 | 0.23804 | -0.036621 | 0.022888 | -122.3831 | 0.20599 | 0.23804 | -0.091553 | 0.27466 | -0.054932 | 0.99792 | 122.6624 | 0.24262 | 0.47607 | 122.9233 | 122.8821 | 122.8317 | 122.8455 | -122.9141 | -122.8592 | 122.5708 | 0.43945 | 4.3762 | 1.6983
3617.1719 | 122.9599 | -52.2675 | 70.5368 | -0.045319 | 0.00062166 | 0.059676 | 0.070754 | 0.0037918 | 0.0013373 | 0.0045672 | -0.016602 | 0.0021703 | 0.0014954 | -0.0037854 | -0.0038559 | -0.0049389 | -0.0033923 | -47.9095 | 70.546 | -52.3956 | 70.2713 | -51.3794 | -52.1576 | -51.6083 | -50.6653 | 70.546 | -52.327 | -51.8784 | -52.0706 | -52.3499 | -52.0706 | -0.12817 | 0.009155 | -0.2655 | 0.88806 | 0.65918 | 0.10986 | 0.78735 | 0.23804 | -0.059509 | 0.009155 | -122.4152 | 0.19684 | 0.19684 | -0.082398 | 0.25635 | -0.022889 | 1.0162 | 122.6669 | 0.25635 | 0.44861 | 122.9416 | 122.8729 | 122.8134 | 122.8134 | -122.9324 | -122.8638 | 122.5388 | 0.3891 | 4.3579 | 1.6022
3618.1875 | 122.9416 | -52.2903 | 70.578 | 0.015716 | -0.00087374 | 0.059889 | 0.067336 | -0.0030442 | 0.00091009 | 0.0028582 | 0.032227 | 0.0015295 | 0.0025634 | 0.002196 | -0.0023605 | -0.0066479 | -0.0016833 | -47.9416 | 70.5185 | -52.3819 | 70.2484 | -51.4206 | -52.153 | -51.622 | -50.6104 | 70.6467 | -52.2949 | -51.9424 | -52.0981 | -52.3773 | -52.0981 | -0.091553 | -0.059509 | -0.32959 | 0.86975 | 0.66833 | 0.13733 | 0.75989 | 0.22888 | -0.004578 | 0.068664 | -122.5204 | 0.19226 | 0.19226 | -0.086975 | 0.19684 | -0.082397 | 0.9613 | 122.6303 | 0.19684 | 0.35248 | 122.9004 | 122.9416 | 122.8088 | 122.937 | -122.9599 | -122.8729 | 122.5388 | 0.3479 | 4.3488 | 1.68
3619.1719 | 122.9782 | -52.2858 | 70.5597 | -0.098725 | 0.0012625 | 0.06288 | 0.069045 | 0.00080117 | 0.0015509 | 0.0064898 | 0.001709 | 0.0021703 | 0.0036316 | -0.001222 | -0.0023605 | -0.0042981 | -0.0010425 | -48.0103 | 70.5276 | -52.3773 | 70.2942 | -51.4069 | -52.1439 | -51.5945 | -50.6607 | 70.5872 | -52.327 | -51.8692 | -52.0889 | -52.3727 | -52.066 | -0.091552 | -0.032043 | -0.2655 | 0.87891 | 0.69122 | 0.14191 | 0.78278 | 0.23346 | -0.041198 | 0.027466 | -122.4289 | 0.19684 | 0.21973 | -0.086975 | 0.26093 | -0.045777 | 0.97046 | 122.6715 | 0.23804 | 0.45776 | 122.905 | 122.9141 | 122.8134 | 122.8729 | -122.937 | -122.8867 | 122.58 | 0.41656 | 4.2755 | 1.6251
3620.1719 | 122.9507 | -52.2766 | 70.5597 | 0.00045798 | -0.0017281 | 0.061385 | 0.068618 | -5.343e-05 | 5.5488e-05 | 0.0032856 | 0.0078126 | 0.0049475 | 0.002777 | -0.00079478 | -0.0027877 | -0.0034437 | 0.00088014 | -47.9004 | 70.5597 | -52.3682 | 70.2896 | -51.3931 | -52.121 | -51.5945 | -50.647 | 70.5917 | -52.3224 | -51.8509 | -52.0569 | -52.359 | -52.0432 | -0.091553 | 0 | -0.27008 | 0.88348 | 0.68207 | 0.15564 | 0.77362 | 0.24719 | -0.045777 | 0.032044 | -122.4106 | 0.21973 | 0.23346 | -0.082398 | 0.27924 | -0.036621 | 0.97504 | 122.6578 | 0.2655 | 0.4715 | 122.9279 | 122.9141 | 122.8363 | 122.8683 | -122.9279 | -122.8821 | 122.5662 | 0.42572 | 4.3762 | 1.6296
3621.1719 | 122.9553 | -52.2675 | 70.5505 | -0.014801 | -1.9142e-05 | 0.060103 | 0.069686 | -0.0032578 | 0.00091009 | 0.0017902 | 0.010864 | 0.0013159 | 0.0023498 | 0.001128 | -0.0023605 | -0.0066479 | 0.00023934 | -47.9233 | 70.5872 | -52.3636 | 70.2667 | -51.416 | -52.1576 | -51.5991 | -50.679 | 70.5963 | -52.2995 | -51.8692 | -52.066 | -52.3499 | -52.0432 | -0.09613 | 0.036621 | -0.28381 | 0.85144 | 0.66834 | 0.10986 | 0.76447 | 0.20599 | -0.032044 | 0.045776 | -122.4197 | 0.20142 | 0.2243 | -0.082398 | 0.25635 | -0.050354 | 0.94757 | 122.6303 | 0.23346 | 0.4303 | 122.9507 | 122.8958 | 122.8546 | 122.8638 | -122.9141 | -122.85 | 122.5342 | 0.39825 | 4.3442 | 1.5884
3622.1719 | 122.9691 | -52.2766 | 70.5597 | -0.12161 | 0.0012625 | 0.061598 | 0.068618 | 0.0022964 | 0.0021917 | 0.0020038 | 0.010864 | 0.0017431 | 0.0014954 | -0.0016492 | -0.0012925 | -0.0045117 | 0.00088014 | -47.9095 | 70.5643 | -52.3773 | 70.2988 | -51.3657 | -52.2629 | -51.6632 | -50.6287 | 70.5734 | -52.3132 | -51.8372 | -52.0798 | -52.3544 | -52.034 | -0.10071 | 0.004578 | -0.26093 | 0.91095 | 0.6134 | 0.013733 | 0.71411 | 0.11444 | -0.036621 | 0.013733 | -122.3969 | 0.19684 | 0.24261 | -0.07782 | 0.27923 | -0.041199 | 1.0117 | 122.6761 | 0.23346 | 0.47607 | 122.9416 | 122.8867 | 122.8409 | 122.85 | -122.937 | -122.8729 | 122.5754 | 0.43945 | 4.3671 | 1.6479
3623.1875 | 122.9141 | -52.2995 | 70.546 | -0.060578 | 0.00062166 | 0.062025 | 0.068191 | 0.0055008 | 0.0024053 | 0.0090534 | -0.028809 | 0.0017431 | 0.001709 | 0.0030506 | -0.00065151 | -0.0051527 | -0.00082886 | -47.9462 | 70.5505 | -52.3727 | 70.2347 | -51.4343 | -52.2034 | -51.6678 | -50.7614 | 70.5826 | -52.3407 | -51.9333 | -52.153 | -52.4368 | -52.1072 | -0.073242 | 0.004578 | -0.31128 | 0.86517 | 0.63171 | 0.096131 | 0.70496 | 0.16937 | -0.041198 | 0.036622 | -122.4792 | 0.14648 | 0.19226 | -0.13733 | 0.23346 | -0.096131 | 0.93842 | 122.6074 | 0.18768 | 0.40741 | 122.9233 | 122.9233 | 122.85 | 122.8821 | -122.9187 | -122.8867 | 122.5342 | 0.36621 | 4.3533 | 1.5381
3624.1719 | 122.9462 | -52.2537 | 70.578 | -0.075836 | 0.00062166 | 0.059889 | 0.069259 | -0.0021896 | 0.0032599 | 0.0032856 | -0.010498 | 0.0011023 | 0.0014954 | -0.001222 | -0.0023605 | -0.0051527 | -0.0025379 | -47.9187 | 70.5963 | -52.3544 | 70.2393 | -51.2283 | -51.9424 | -51.7044 | -50.6516 | 70.6146 | -52.3178 | -51.8829 | -52.0706 | -52.3544 | -52.066 | -0.10071 | 0.01831 | -0.33874 | 1.0254 | 0.54932 | 0.31128 | 0.65002 | 0.41199 | -0.064087 | 0.036621 | -122.4609 | 0.1831 | 0.18768 | -0.10071 | 0.25177 | -0.036621 | 1.1261 | 122.5937 | 0.24719 | 0.43487 | 122.9507 | 122.9324 | 122.85 | 122.8683 | -122.9324 | -122.8958 | 122.493 | 0.37079 | 4.335 | 1.6022
3625.1719 | 122.9324 | -52.2675 | 70.5734 | -0.045319 | -0.0010873 | 0.059889 | 0.069686 | 0.00016017 | 0.0011237 | 0.0020038 | 0.035278 | 0.0021703 | 0.0023498 | 0.00048702 | -0.0025741 | -0.0045117 | 0.0013073 | -47.8821 | 70.5963 | -52.327 | 70.2759 | -51.4069 | -52.1484 | -51.5808 | -50.6927 | 70.6055 | -52.3041 | -51.8784 | -52.0569 | -52.3453 | -52.0706 | -0.059509 | 0.022888 | -0.29755 | 0.8606 | 0.68665 | 0.11902 | 0.74615 | 0.17853 | -0.036621 | 0.032044 | -122.4518 | 0.21057 | 0.19684 | -0.07782 | 0.23346 | -0.041199 | 0.9201 | 122.6028 | 0.24719 | 0.42572 | 122.9233 | 122.9095 | 122.8638 | 122.8729 | -122.9004 | -122.8775 | 122.5433 | 0.3891 | 4.3854 | 1.5747
3626.1719 | 122.9645 | -52.2766 | 70.5551 | -0.075836 | -0.00066014 | 0.061171 | 0.070754 | -0.0017624 | 0.0021917 | 0.005849 | 0.001709 | 0.00067495 | 0.00085443 | -0.0018628 | -0.0036423 | -0.0072889 | 0.00045294 | -47.8958 | 70.6055 | -52.3407 | 70.2896 | -51.3748 | -52.1164 | -51.5762 | -50.6607 | 70.6146 | -52.2858 | -51.8509 | -52.0477 | -52.3224 | -52.0477 | -0.064087 | 0.050354 | -0.2655 | 0.90179 | 0.70038 | 0.16022 | 0.76447 | 0.2243 | -0.009156 | 0.059509 | -122.406 | 0.22888 | 0.22888 | -0.045777 | 0.23804 | -0.036621 | 0.96588 | 122.6303 | 0.23804 | 0.43488 | 122.9462 | 122.9004 | 122.8821 | 122.8912 | -122.8958 | -122.8409 | 122.5662 | 0.42572 | 4.3808 | 1.6159
3627.1719 | 122.9919 | -52.2446 | 70.578 | -0.03006 | 0.00062166 | 0.063307 | 0.06755 | 0.00037377 | 0.0011237 | 0.003072 | -0.0043946 | 0.00067495 | 0.00021363 | -0.00229 | -0.00086511 | -0.0057935 | -0.00061526 | -47.8638 | 70.5643 | -52.3224 | 70.3262 | -51.3153 | -52.0935 | -51.5671 | -50.6195 | 70.5963 | -52.2583 | -51.8372 | -52.034 | -52.3178 | -52.0203 | -0.07782 | -0.013733 | -0.25177 | 0.92926 | 0.67749 | 0.15106 | 0.75531 | 0.22888 | -0.013733 | 0.01831 | -122.4152 | 0.21057 | 0.2243 | -0.073242 | 0.23804 | -0.059509 | 1.0071 | 122.6486 | 0.2243 | 0.42114 | 122.8867 | 122.8546 | 122.8088 | 122.8409 | -122.9004 | -122.8363 | 122.5708 | 0.40741 | 4.3808 | 1.6251
3628.1875 | 123.0698 | -52.2308 | 70.5505 | -0.10635 | -1.9142e-05 | 0.06053 | 0.065841 | 0.00058737 | 0.0011237 | 0.0049946 | 0.09021 | 0.00046135 | 0.001068 | -0.0018628 | -0.00086511 | -0.0089979 | 0.0015209 | -47.8409 | 70.5597 | -52.2903 | 70.4224 | -51.1963 | -51.9974 | -51.4526 | -50.5646 | 70.5826 | -52.2354 | -51.7319 | -51.9699 | -52.2354 | -51.947 | -0.059509 | 0.009155 | -0.12817 | 1.0345 | 0.7782 | 0.23346 | 0.83771 | 0.29297 | -0.004578 | 0.032044 | -122.2824 | 0.26093 | 0.28381 | -0.004578 | 0.28839 | 0 | 1.0941 | 122.7127 | 0.2655 | 0.50354 | 122.85 | 122.818 | 122.7905 | 122.8134 | -122.8409 | -122.786 | 122.6532 | 0.49896 | 4.39 | 1.6663
3629.1719 | 122.9279 | -52.2354 | 70.6238 | -0.083466 | -1.9142e-05 | 0.060316 | 0.068191 | -0.0056076 | 0.0024053 | 0.0060626 | 0.032227 | 0.0030249 | 0.002777 | -0.007417 | -0.0023605 | -0.0047253 | -0.0023243 | -47.8912 | 70.5917 | -52.327 | 70.3079 | -51.3611 | -52.1118 | -51.5533 | -50.6378 | 70.6421 | -52.272 | -51.8829 | -52.0386 | -52.3315 | -52.0432 | -0.091552 | -0.032043 | -0.31586 | 0.87433 | 0.68207 | 0.1236 | 0.77362 | 0.21515 | -0.036621 | 0.018311 | -122.5067 | 0.19684 | 0.19226 | -0.09613 | 0.22888 | -0.059509 | 0.96588 | 122.6349 | 0.23346 | 0.3891 | 122.9187 | 122.9141 | 122.8271 | 122.8775 | -122.9507 | -122.8958 | 122.5433 | 0.35248 | 4.3442 | 1.5976
3630.1719 | 122.9645 | -52.2308 | 70.6009 | -0.060578 | -1.9142e-05 | 0.061598 | 0.072036 | 0.00016017 | 0.0011237 | 0.0037128 | -0.010498 | 0.0011023 | 0.00085443 | 0.0032642 | -0.0034287 | -0.0053663 | -0.0021107 | -47.8455 | 70.578 | -52.3132 | 70.3445 | -51.3336 | -52.1072 | -51.5533 | -50.5875 | 70.6146 | -52.2537 | -51.8188 | -52.0248 | -52.3041 | -51.9974 | -0.082397 | -0.022888 | -0.25635 | 0.89722 | 0.67749 | 0.1236 | 0.75989 | 0.20599 | -0.022888 | 0.013733 | -122.4197 | 0.20599 | 0.23346 | -0.073242 | 0.25635 | -0.050354 | 0.97961 | 122.6578 | 0.22888 | 0.43487 | 122.8912 | 122.8683 | 122.8088 | 122.8455 | -122.9141 | -122.8546 | 122.5754 | 0.41199 | 4.3854 | 1.6434
3631.1719 | 122.9645 | -52.2537 | 70.5734 | -0.10635 | -0.00044654 | 0.063734 | 0.070968 | 0.0012284 | 0.0051825 | 0.002431 | -0.010498 | 0.0021703 | -0.0014954 | 0.0019824 | -0.0021469 | -0.0047253 | 0.0025891 | -47.8592 | 70.5734 | -52.3499 | 70.2942 | -51.3611 | -52.1255 | -51.59 | -50.647 | 70.6009 | -52.272 | -51.8509 | -52.0615 | -52.3773 | -52.0386 | -0.096131 | 0 | -0.27924 | 0.89264 | 0.66376 | 0.12817 | 0.75989 | 0.22431 | -0.018311 | 0.027466 | -122.4243 | 0.19226 | 0.21515 | -0.1236 | 0.23346 | -0.10529 | 0.98877 | 122.644 | 0.21057 | 0.42114 | 122.9233 | 122.8729 | 122.8271 | 122.8546 | -122.9233 | -122.8455 | 122.5479 | 0.40283 | 4.3945 | 1.6067
3632.1719 | 122.9782 | -52.2491 | 70.5826 | 0.023346 | -0.0013009 | 0.062025 | 0.068404 | -0.0017624 | -0.0014399 | 0.00414 | 0.029175 | 0.0023839 | 0.0014954 | 0.00027342 | -0.0019333 | -0.0049389 | 0.0019483 | -47.8592 | 70.6009 | -52.3041 | 70.3491 | -51.3428 | -52.0752 | -51.5442 | -50.6058 | 70.6238 | -52.2583 | -51.828 | -52.0203 | -52.2858 | -51.9791 | -0.054931 | 0.01831 | -0.23346 | 0.90637 | 0.70496 | 0.17395 | 0.75989 | 0.22888 | -0.009155 | 0.041198 | -122.4106 | 0.22888 | 0.27008 | -0.036621 | 0.27924 | -0.027466 | 0.9613 | 122.6532 | 0.23804 | 0.4303 | 122.905 | 122.8821 | 122.85 | 122.8729 | -122.8867 | -122.8409 | 122.5983 | 0.42114 | 4.39 | 1.6434
3633.1875 | 122.9553 | -52.2263 | 70.61 | 0.008087 | -1.9142e-05 | 0.060103 | 0.069259 | -0.0017624 | 0.0015509 | 0.0077716 | 0.02002 | 0.0034521 | 0.00042723 | -0.00015378 | -0.0017197 | -0.0077161 | 0.0023755 | -47.8683 | 70.6192 | -52.3132 | 70.3125 | -51.3702 | -52.1072 | -51.5579 | -50.6424 | 70.665 | -52.2629 | -51.8417 | -52.0248 | -52.3087 | -52.0157 | -0.086975 | 0.009156 | -0.29755 | 0.85602 | 0.66833 | 0.11902 | 0.75531 | 0.20599 | -0.036621 | 0.054932 | -122.4518 | 0.20142 | 0.21057 | -0.082398 | 0.24719 | -0.045777 | 0.94299 | 122.6257 | 0.23804 | 0.42114 | 122.9324 | 122.9279 | 122.8455 | 122.8912 | -122.9233 | -122.8729 | 122.5388 | 0.38452 | 4.3579 | 1.5839
3634.1719 | 122.9645 | -52.2263 | 70.6009 | -0.022431 | -0.0010873 | 0.063734 | 0.067977 | 0.0016556 | 0.0030463 | 0.0028582 | -0.028809 | 0.0011023 | -0.00064077 | 0.00070062 | -0.0036423 | -0.0062207 | -0.0031787 | -47.8271 | 70.6055 | -52.3087 | 70.3629 | -51.297 | -52.0844 | -51.535 | -50.5646 | 70.6284 | -52.2583 | -51.8005 | -52.002 | -52.2858 | -51.9836 | -0.082398 | 0.004578 | -0.23804 | 0.92926 | 0.69122 | 0.14191 | 0.77362 | 0.2243 | -0.032044 | 0.027466 | -122.4014 | 0.2243 | 0.24261 | -0.05951 | 0.27466 | -0.027466 | 1.0117 | 122.6715 | 0.25635 | 0.45776 | 122.9141 | 122.8867 | 122.8317 | 122.8546 | -122.9095 | -122.8592 | 122.5891 | 0.42572 | 4.3991 | 1.6617
3635.1719 | 122.9553 | -52.2171 | 70.5963 | -0.12924 | 0.0014761 | 0.062025 | 0.067123 | 0.0040054 | 0.0015509 | 0.010976 | -0.0043946 | 3.4148e-05 | 0.0014954 | -0.0010084 | -0.0030013 | -0.0042981 | 0.00045294 | -47.8409 | 70.6146 | -52.3041 | 70.2805 | -51.4023 | -51.9516 | -51.503 | -50.5417 | 70.6146 | -52.2308 | -51.8005 | -52.0157 | -52.3087 | -51.9836 | -0.086975 | 0.018311 | -0.31586 | 0.81482 | 0.71411 | 0.2655 | 0.80109 | 0.35248 | -0.013733 | 0.018311 | -122.3969 | 0.20142 | 0.23346 | -0.091553 | 0.24719 | -0.07782 | 0.90179 | 122.5845 | 0.21515 | 0.4303 | 122.9187 | 122.8455 | 122.8317 | 122.8317 | -122.9004 | -122.8271 | 122.4976 | 0.41656 | 4.3762 | 1.6754
3636.1719 | 122.9462 | -52.1988 | 70.6238 | -0.068207 | -1.9142e-05 | 0.062453 | 0.067336 | -0.0045394 | 0.00069649 | 0.0056354 | 0.050537 | -0.00017945 | 0.0038452 | -0.005708 | -0.0017197 | -0.0072889 | 0.0023755 | -47.7905 | 70.6375 | -52.2491 | 70.3903 | -51.2604 | -52.0203 | -51.4709 | -50.5417 | 70.6284 | -52.2217 | -51.7914 | -51.9882 | -52.2446 | -51.9882 | -0.050354 | 0.013733 | -0.23346 | 0.93842 | 0.72784 | 0.17853 | 0.7782 | 0.22888 | -0.022888 | 0.004578 | -122.4152 | 0.21057 | 0.21057 | -0.045776 | 0.23346 | -0.022888 | 0.98877 | 122.6395 | 0.23346 | 0.4303 | 122.8867 | 122.85 | 122.8363 | 122.8271 | -122.8729 | -122.8455 | 122.5891 | 0.40741 | 4.4083 | 1.6571
3637.1719 | 122.9736 | -52.1851 | 70.6238 | -0.037689 | -0.00087374 | 0.060316 | 0.068404 | -0.0015488 | 0.0021917 | 0.0028582 | 0.041382 | 0.0021703 | 2.8e-08 | -0.006349 | -0.0036423 | -0.0072889 | -0.0029651 | -47.7768 | 70.6009 | -52.2446 | 70.4315 | -51.2283 | -51.9791 | -51.4389 | -50.5051 | 70.6329 | -52.1851 | -51.7776 | -51.9424 | -52.2079 | -51.9562 | -0.059509 | -0.022888 | -0.19226 | 0.95673 | 0.74616 | 0.20599 | 0.80566 | 0.2655 | 0 | 0.009156 | -122.4014 | 0.24262 | 0.22888 | -0.022888 | 0.22888 | -0.022888 | 1.0162 | 122.6761 | 0.24262 | 0.40741 | 122.8455 | 122.818 | 122.786 | 122.818 | -122.8683 | -122.8088 | 122.6166 | 0.40741 | 4.4083 | 1.68
3638.1719 | 123.0469 | -52.2125 | 70.5688 | -0.075836 | 0.00083526 | 0.062453 | 0.066482 | -0.0013352 | 0.0026191 | 0.0039264 | 0.016968 | 0.0019567 | 0.00064083 | -0.0050672 | -0.0025741 | -0.0038709 | -0.00040166 | -47.7997 | 70.5276 | -52.272 | 70.4132 | -51.2466 | -52.0432 | -51.4755 | -50.5005 | 70.6009 | -52.2125 | -51.741 | -51.9653 | -52.2354 | -51.9424 | -0.05951 | -0.041199 | -0.15564 | 0.96588 | 0.737 | 0.16937 | 0.79651 | 0.22888 | 0 | 0.032043 | -122.3099 | 0.24719 | 0.27008 | -0.022889 | 0.27008 | -0.022889 | 1.0254 | 122.6852 | 0.24719 | 0.4715 | 122.7997 | 122.8134 | 122.7402 | 122.8134 | -122.8409 | -122.7814 | 122.6257 | 0.4715 | 4.4128 | 1.712
3639.1719 | 122.9416 | -52.2125 | 70.6512 | -0.022431 | -0.0017281 | 0.060744 | 0.068832 | -0.0030442 | -0.0010125 | 0.0020038 | 0.0078126 | 0.0019567 | 0.0023498 | 0.00048702 | -0.0015061 | -0.0042981 | -0.00061526 | -47.8363 | 70.6467 | -52.2629 | 70.3583 | -51.3153 | -52.0798 | -51.5213 | -50.592 | 70.6741 | -52.2308 | -51.7914 | -52.0065 | -52.3361 | -52.0203 | -0.050354 | -0.004578 | -0.29297 | 0.89722 | 0.69122 | 0.13275 | 0.74158 | 0.1831 | -0.018311 | 0.022888 | -122.4426 | 0.20599 | 0.19226 | -0.1236 | 0.21057 | -0.10529 | 0.94757 | 122.6212 | 0.2243 | 0.43945 | 122.9095 | 122.905 | 122.8592 | 122.8867 | -122.9141 | -122.8821 | 122.5708 | 0.42114 | 4.3762 | 1.6205
3640.1719 | 122.9599 | -52.1622 | 70.6558 | -0.083466 | 0.0012625 | 0.064375 | 0.067336 | -0.0013352 | 0.0041143 | 0.0056354 | 0.03833 | 0.00046135 | 0.00042723 | -0.0078442 | -0.0017197 | -0.0051527 | 2.554e-05 | -47.7631 | 70.61 | -52.2354 | 70.4544 | -51.2238 | -51.9836 | -51.4435 | -50.5096 | 70.6558 | -52.1988 | -51.7685 | -51.9333 | -52.2217 | -51.9562 | -0.073243 | -0.045777 | -0.20142 | 0.93842 | 0.71869 | 0.17853 | 0.79193 | 0.25177 | -0.036622 | 0 | -122.4243 | 0.22888 | 0.20599 | -0.05951 | 0.24262 | -0.022888 | 1.0117 | 122.6898 | 0.2655 | 0.4303 | 122.8455 | 122.8546 | 122.7722 | 122.818 | -122.8912 | -122.8546 | 122.6166 | 0.39368 | 4.3991 | 1.6525
3641.1719 | 122.9553 | -52.1896 | 70.665 | -0.075836 | -0.00066014 | 0.063094 | 0.06755 | -0.0030442 | 5.5488e-05 | 0.0049946 | 0.029175 | 0.00088875 | 0.0029906 | -0.0018628 | -0.0023605 | -0.0077161 | -0.00018806 | -47.7859 | 70.6421 | -52.2675 | 70.372 | -51.3153 | -52.0432 | -51.4847 | -50.5966 | 70.6924 | -52.2034 | -51.8005 | -51.9745 | -52.272 | -52.0065 | -0.07782 | -0.022888 | -0.29297 | 0.87433 | 0.70496 | 0.14648 | 0.78278 | 0.2243 | -0.013733 | 0.027466 | -122.4655 | 0.21515 | 0.1831 | -0.082398 | 0.19684 | -0.068665 | 0.95215 | 122.6395 | 0.22888 | 0.40283 | 122.9095 | 122.8958 | 122.8317 | 122.8821 | -122.9324 | -122.8683 | 122.5616 | 0.3891 | 4.4037 | 1.593
3642.1719 | 122.9874 | -52.1484 | 70.6238 | -0.068207 | -1.9142e-05 | 0.061812 | 0.067763 | 0.00080117 | 0.0013373 | 0.0017902 | 0.02002 | 0.00067495 | 0.00064083 | -0.0016492 | -0.0017197 | -0.0070753 | -0.00061526 | -47.7585 | 70.5917 | -52.2263 | 70.4453 | -51.1963 | -51.9653 | -51.4023 | -50.4547 | 70.6467 | -52.2034 | -51.7273 | -51.8921 | -52.1713 | -51.9241 | -0.07782 | -0.032043 | -0.17853 | 0.95215 | 0.74615 | 0.18311 | 0.82397 | 0.26093 | -0.054932 | 0.022888 | -122.3511 | 0.25635 | 0.2243 | -0.022889 | 0.27924 | 0.032043 | 1.03 | 122.6715 | 0.31128 | 0.47607 | 122.818 | 122.85 | 122.7402 | 122.7951 | -122.85 | -122.8271 | 122.5937 | 0.42114 | 4.39 | 1.6937
3643.1719 | 123.0377 | -52.1576 | 70.5917 | -0.16739 | 0.00040806 | 0.064375 | 0.067123 | 0.00251 | 0.00069649 | 0.0026446 | -0.016602 | 0.0011023 | 0.0012818 | -0.0014356 | -0.0034287 | -0.0051527 | 2.554e-05 | -47.7081 | 70.5368 | -52.2858 | 70.4361 | -51.2329 | -52.0157 | -51.4572 | -50.473 | 70.6055 | -52.2125 | -51.7227 | -51.947 | -52.2125 | -51.9012 | -0.12817 | -0.054932 | -0.15564 | 0.92468 | 0.70038 | 0.14191 | 0.82855 | 0.27008 | -0.054931 | 0.013733 | -122.3145 | 0.21057 | 0.25635 | -0.054931 | 0.31128 | 0 | 1.0529 | 122.7219 | 0.2655 | 0.48981 | 122.8226 | 122.818 | 122.6944 | 122.7631 | -122.8775 | -122.8043 | 122.5937 | 0.43488 | 4.4495 | 1.6846
3644.1719 | 123.0194 | -52.1439 | 70.6238 | -0.022431 | -0.00044654 | 0.063521 | 0.067977 | 0.0020828 | 0.0039007 | 0.0054218 | 0.029175 | 0.00024775 | 0.0029906 | 0.0019824 | -0.00022431 | -0.010493 | -0.0014697 | -47.7493 | 70.6421 | -52.2171 | 70.3766 | -51.1139 | -51.9699 | -51.4343 | -50.4501 | 70.6512 | -52.2171 | -51.6907 | -51.8692 | -52.1576 | -51.8921 | -0.073242 | 0.018311 | -0.24719 | 1.03 | 0.70953 | 0.17395 | 0.78278 | 0.24719 | -0.073242 | 0.027466 | -122.3145 | 0.27466 | 0.25177 | -0.013733 | 0.32501 | 0.059509 | 1.1032 | 122.5937 | 0.3479 | 0.52643 | 122.8592 | 122.8683 | 122.7859 | 122.7951 | -122.8409 | -122.8409 | 122.5204 | 0.45319 | 4.3945 | 1.6937
3645.1719 | 123.0377 | -52.1622 | 70.6238 | -0.068207 | 0.00040806 | 0.061171 | 0.066482 | -0.00048063 | 0.0028327 | 0.0056354 | 0.062744 | -0.00082025 | 0.003418 | -0.001222 | -0.0032151 | -0.0066479 | 0.0028027 | -47.7264 | 70.6421 | -52.24 | 70.4773 | -51.1505 | -51.9379 | -51.384 | -50.2167 | 70.6924 | -52.153 | -51.7136 | -51.86 | -52.1622 | -51.8967 | -0.07782 | 0.018311 | -0.14648 | 1.0117 | 0.7782 | 0.2243 | 0.85602 | 0.30212 | 0.009155 | 0.068665 | -122.3373 | 0.30212 | 0.2655 | 0 | 0.25635 | -0.009155 | 1.0895 | 122.7173 | 0.29297 | 0.43945 | 122.8821 | 122.8455 | 122.8043 | 122.8546 | -122.8638 | -122.7768 | 122.6395 | 0.44861 | 4.4357 | 1.9455
3646.1719 | 122.9919 | -52.1347 | 70.6238 | -0.068207 | -0.00023294 | 0.062239 | 0.070968 | -0.0011214 | 0.0030463 | 0.0060626 | 0.029175 | 0.0021703 | 0.001068 | -0.0050672 | -0.0049241 | -0.0066479 | -0.0031787 | -47.7402 | 70.6329 | -52.2354 | 70.491 | -51.1597 | -51.9424 | -51.416 | -50.4501 | 70.665 | -52.1851 | -51.709 | -51.8784 | -52.1576 | -51.8692 | -0.10071 | 0.009156 | -0.13275 | 0.97504 | 0.71869 | 0.19226 | 0.8194 | 0.29297 | -0.050354 | 0.041199 | -122.3328 | 0.25635 | 0.2655 | -0.022888 | 0.31586 | 0.027466 | 1.0757 | 122.7264 | 0.3067 | 0.47608 | 122.8683 | 122.85 | 122.7676 | 122.7997 | -122.8592 | -122.8088 | 122.6257 | 0.42572 | 4.3945 | 1.6846
3647.1719 | 122.9507 | -52.1484 | 70.6696 | -0.045319 | 0.00040806 | 0.063307 | 0.069686 | -5.343e-05 | 0.0028327 | 0.0028582 | -0.010498 | -0.0012477 | 0.0014954 | -0.0010084 | -0.0034287 | -0.0055799 | -0.0059559 | -47.7356 | 70.665 | -52.2308 | 70.459 | -51.2146 | -51.9653 | -51.4297 | -50.4868 | 70.6879 | -52.1851 | -51.741 | -51.9287 | -52.2079 | -51.9379 | -0.082398 | -0.004578 | -0.21057 | 0.93384 | 0.71869 | 0.18311 | 0.80109 | 0.2655 | -0.036622 | 0.01831 | -122.4106 | 0.21973 | 0.21057 | -0.05951 | 0.24719 | -0.022888 | 1.0162 | 122.6898 | 0.25635 | 0.44403 | 122.8958 | 122.8729 | 122.8134 | 122.8363 | -122.9004 | -122.8546 | 122.6074 | 0.40741 | 4.4128 | 1.6617
3648.1719 | 122.9187 | -52.1576 | 70.6421 | -0.10635 | -0.00044654 | 0.062666 | 0.070754 | 0.0033646 | 5.5488e-05 | 0.0054218 | -0.071533 | -0.0010339 | 0.003418 | 0.00027342 | -0.0025741 | -0.0060071 | -0.0044605 | -47.7493 | 70.665 | -52.2308 | 70.4315 | -51.2466 | -52.0294 | -51.4801 | -50.5142 | 70.6787 | -52.1805 | -51.7364 | -51.9562 | -52.24 | -51.9516 | -0.073242 | 0.022888 | -0.21057 | 0.91095 | 0.67749 | 0.12817 | 0.75073 | 0.20142 | -0.022888 | 0.036621 | -122.3785 | 0.20142 | 0.20599 | -0.082397 | 0.22888 | -0.059509 | 0.98419 | 122.6624 | 0.2243 | 0.44403 | 122.8958 | 122.8592 | 122.8226 | 122.8363 | -122.8729 | -122.8226 | 122.5891 | 0.42114 | 4.4083 | 1.6434
3649.1719 | 123.0743 | -52.1484 | 70.6146 | -0.083466 | -1.9142e-05 | 0.059248 | 0.067336 | 0.001442 | 0.0045417 | 0.0056354 | 0.032227 | -0.00082025 | -0.0021362 | 0.0045458 | -0.0012925 | -0.0051527 | -0.0048877 | -47.7264 | 70.6512 | -52.2079 | 70.4681 | -51.178 | -51.9653 | -51.3886 | -50.4501 | 70.6696 | -52.1805 | -51.6678 | -51.8372 | -52.1118 | -51.86 | -0.05951 | 0.036621 | -0.14648 | 0.97046 | 0.75989 | 0.18311 | 0.8194 | 0.24262 | -0.032044 | 0.054932 | -122.2824 | 0.31128 | 0.28839 | 0.036621 | 0.32044 | 0.068665 | 1.03 | 122.6761 | 0.34332 | 0.5127 | 122.8592 | 122.85 | 122.7997 | 122.818 | -122.8226 | -122.7951 | 122.6166 | 0.48065 | 4.422 | 1.6983
3650.1719 | 123.0194 | -52.0981 | 70.6512 | -0.11398 | -0.00087374 | 0.063094 | 0.068618 | 0.00251 | 0.0015509 | 0.0064898 | 0.056641 | 0.0013159 | 2.8e-08 | -0.005708 | -0.0034287 | -0.0064343 | -0.0038197 | -47.6852 | 70.6375 | -52.2263 | 70.5185 | -51.1139 | -51.9058 | -51.3519 | -50.3723 | 70.697 | -52.1576 | -51.6586 | -51.828 | -52.1255 | -51.8509 | -0.12817 | -0.013733 | -0.13275 | 0.98419 | 0.74615 | 0.19226 | 0.87433 | 0.32043 | -0.05951 | 0.045776 | -122.3099 | 0.27008 | 0.24719 | -0.027466 | 0.3067 | 0.032044 | 1.1124 | 122.7448 | 0.32959 | 0.49896 | 122.8638 | 122.8546 | 122.7356 | 122.7951 | -122.8775 | -122.8088 | 122.6166 | 0.43945 | 4.4128 | 1.7258
3651.1719 | 122.9324 | -52.121 | 70.6787 | -0.075836 | -0.0010873 | 0.060744 | 0.065627 | -0.0015488 | 0.0026191 | 0.0017902 | 0.02002 | 0.00046135 | 0.0014954 | 0.0028368 | -0.0036423 | -0.0040845 | -0.00061526 | -47.7036 | 70.6604 | -52.2171 | 70.491 | -51.1642 | -51.9562 | -51.3977 | -50.473 | 70.7199 | -52.1896 | -51.7044 | -51.8875 | -52.1759 | -51.9012 | -0.09613 | -0.018311 | -0.18768 | 0.95673 | 0.72327 | 0.1648 | 0.8194 | 0.26093 | -0.068664 | 0.041199 | -122.3831 | 0.23346 | 0.21973 | -0.054931 | 0.28839 | 0.013733 | 1.0529 | 122.7081 | 0.30212 | 0.48523 | 122.8775 | 122.9095 | 122.7814 | 122.8409 | -122.8958 | -122.8683 | 122.612 | 0.41656 | 4.4174 | 1.648
3652.1719 | 122.9416 | -52.153 | 70.7108 | -0.037689 | 0.00062166 | 0.06288 | 0.067977 | 0.0016556 | 0.0015509 | 0.0052082 | -0.0074462 | 0.0028113 | 0.0012818 | -0.0018628 | -0.0030013 | -0.0066479 | -0.0027515 | -47.7036 | 70.697 | -52.24 | 70.4315 | -51.21 | -52.0248 | -51.4664 | -50.5051 | 70.7474 | -52.1713 | -51.7548 | -51.9608 | -52.2354 | -51.9608 | -0.086975 | -0.013733 | -0.27923 | 0.94299 | 0.68665 | 0.12817 | 0.77362 | 0.21515 | -0.018311 | 0.036621 | -122.4655 | 0.19226 | 0.19226 | -0.082398 | 0.21057 | -0.064087 | 1.03 | 122.6715 | 0.21057 | 0.41656 | 122.937 | 122.9187 | 122.85 | 122.9004 | -122.9507 | -122.8821 | 122.5845 | 0.39825 | 4.4495 | 1.6479
3653.1719 | 122.9141 | -52.1713 | 70.6604 | -0.060578 | 0.0012625 | 0.062453 | 0.069472 | 0.001442 | 0.0034735 | 0.0039264 | -0.086792 | 0.0015295 | 0.00064083 | 0.0036914 | -0.0036423 | -0.0042981 | -0.0023243 | -47.7356 | 70.6558 | -52.2354 | 70.4132 | -51.2512 | -52.0432 | -51.4938 | -50.5188 | 70.7108 | -52.1759 | -51.7456 | -51.9791 | -52.2858 | -51.947 | -0.064087 | -0.004577 | -0.24719 | 0.9201 | 0.67749 | 0.12817 | 0.74158 | 0.19226 | -0.004577 | 0.050354 | -122.406 | 0.19226 | 0.22431 | -0.11444 | 0.22888 | -0.10986 | 0.98419 | 122.6486 | 0.19684 | 0.4303 | 122.8912 | 122.8867 | 122.8271 | 122.8821 | -122.8958 | -122.8363 | 122.5845 | 0.42572 | 4.4357 | 1.6525
3654.1719 | 123.0515 | -52.1118 | 70.6512 | -0.098725 | 0.0014761 | 0.062025 | 0.067763 | -0.0017624 | 0.0021917 | 0.0015766 | 0.056641 | 0.0025975 | -0.0010682 | -0.00079478 | -0.0019333 | -0.0077161 | 0.0021619 | -47.6944 | 70.6375 | -52.2079 | 70.4956 | -51.1368 | -51.9333 | -51.3748 | -50.386 | 70.6696 | -52.1484 | -51.6266 | -51.8188 | -52.0798 | -51.828 | -0.096131 | -0.013733 | -0.15564 | 0.97504 | 0.737 | 0.17853 | 0.83313 | 0.27466 | -0.036621 | 0.018311 | -122.2778 | 0.29297 | 0.28381 | 0.032043 | 0.32043 | 0.068664 | 1.0712 | 122.7036 | 0.32959 | 0.52185 | 122.8455 | 122.818 | 122.7493 | 122.7814 | -122.8592 | -122.7997 | 122.6074 | 0.48523 | 4.4174 | 1.7258
3655.1719 | 123.0286 | -52.1118 | 70.6467 | -0.11398 | 0.0010489 | 0.060957 | 0.067977 | -0.0021896 | 0.0032599 | 0.00050839 | 0.02002 | -0.0023157 | 0.00021363 | -0.0010084 | -0.0019333 | -0.0075025 | -0.0014697 | -47.699 | 70.6558 | -52.1851 | 70.4956 | -51.1551 | -51.9379 | -51.3657 | -50.4272 | 70.6924 | -52.1622 | -51.6357 | -51.8234 | -52.0981 | -51.828 | -0.073243 | 0.009156 | -0.15106 | 0.95673 | 0.74615 | 0.17395 | 0.8194 | 0.24719 | -0.050354 | 0.045777 | -122.2824 | 0.28839 | 0.28381 | 0.013733 | 0.33417 | 0.064087 | 1.03 | 122.6807 | 0.33875 | 0.52643 | 122.8409 | 122.8546 | 122.7676 | 122.8043 | -122.8317 | -122.8088 | 122.6074 | 0.47607 | 4.4128 | 1.6846
3656.1719 | 123.056 | -52.1072 | 70.6787 | -0.098725 | -1.9142e-05 | 0.060744 | 0.068618 | -0.0013352 | 0.0021917 | 0.0034992 | 0.026123 | 0.00046135 | 0.0012818 | 0.00070062 | -0.0023605 | -0.0066479 | -0.0021107 | -47.6715 | 70.6604 | -52.1942 | 70.5276 | -51.1093 | -51.8921 | -51.3474 | -50.3723 | 70.6879 | -52.1255 | -51.6129 | -51.8005 | -52.0706 | -51.8143 | -0.086975 | -0.018311 | -0.15106 | 0.99793 | 0.75989 | 0.21515 | 0.84686 | 0.30212 | -0.01831 | 0.009155 | -122.2916 | 0.3067 | 0.29297 | 0.036621 | 0.31128 | 0.054931 | 1.0849 | 122.7219 | 0.32501 | 0.5127 | 122.8546 | 122.8134 | 122.7676 | 122.7951 | -122.8729 | -122.8043 | 122.6349 | 0.49439 | 4.4357 | 1.7349
3657.1719 | 123.0377 | -52.1164 | 70.6696 | -0.11398 | -0.00087374 | 0.061812 | 0.068832 | -5.343e-05 | 0.0041143 | 0.0047808 | 0.032227 | -0.0016749 | 0.002777 | -0.0031446 | -0.0019333 | -0.0055799 | -0.00082886 | -47.6669 | 70.6467 | -52.2034 | 70.5185 | -51.1459 | -51.915 | -51.3565 | -50.3952 | 70.6879 | -52.1439 | -51.6129 | -51.7868 | -52.0798 | -51.8417 | -0.086975 | -0.022889 | -0.15106 | 0.97046 | 0.75989 | 0.20142 | 0.84686 | 0.28839 | -0.027466 | 0.01831 | -122.2824 | 0.32959 | 0.27466 | 0.036621 | 0.30212 | 0.064087 | 1.0574 | 122.7219 | 0.35706 | 0.53101 | 122.85 | 122.8317 | 122.7631 | 122.8043 | -122.8729 | -122.8134 | 122.6349 | 0.50354 | 4.4495 | 1.7212
3658.1719 | 123.0148 | -52.0981 | 70.6787 | -0.10635 | 0.00040806 | 0.060744 | 0.068618 | 0.00058737 | 0.00069649 | 0.0045672 | 0.010864 | -0.00017945 | 0.0014954 | -0.0059216 | -0.0025741 | -0.0045117 | 0.00066654 | -47.6486 | 70.6924 | -52.1942 | 70.5231 | -51.1002 | -51.8967 | -51.3428 | -50.3952 | 70.7016 | -52.1439 | -51.6495 | -51.8188 | -52.1027 | -51.8326 | -0.096131 | 0.013733 | -0.15564 | 0.99792 | 0.75531 | 0.20142 | 0.85144 | 0.29755 | -0.045777 | 0.022888 | -122.3282 | 0.27923 | 0.2655 | -0.004578 | 0.31128 | 0.041199 | 1.0941 | 122.7173 | 0.32501 | 0.49438 | 122.8867 | 122.8455 | 122.7905 | 122.7997 | -122.8729 | -122.8226 | 122.6212 | 0.44861 | 4.4495 | 1.7029
3659.1719 | 123.0423 | -52.1118 | 70.665 | -0.11398 | -0.00044654 | 0.062239 | 0.067977 | -0.0015488 | 0.0013373 | 0.0034992 | 0.02002 | 0.00067495 | 0.0012818 | -0.0010084 | -0.0034287 | -0.0068615 | -0.0029651 | -47.6624 | 70.6558 | -52.1759 | 70.5276 | -51.1185 | -51.9058 | -51.3428 | -50.3632 | 70.7153 | -52.1255 | -51.6174 | -51.8005 | -52.0706 | -51.8234 | -0.064087 | -0.009155 | -0.13733 | 0.99335 | 0.76904 | 0.20599 | 0.83313 | 0.27008 | -0.013733 | 0.050354 | -122.2824 | 0.31128 | 0.28839 | 0.041198 | 0.30212 | 0.054931 | 1.0574 | 122.7036 | 0.32501 | 0.50812 | 122.8317 | 122.8409 | 122.7676 | 122.8271 | -122.8409 | -122.7905 | 122.6395 | 0.49438 | 4.4495 | 1.7487
3660.1719 | 123.0331 | -52.1027 | 70.6741 | -0.083466 | -0.00087374 | 0.060744 | 0.06755 | 0.0010148 | 0.0039007 | 0.0054218 | 0.0078126 | -0.00017945 | 0.00021363 | -0.00079478 | -0.0021469 | -0.0066479 | -0.0018971 | -47.6257 | 70.6787 | -52.1805 | 70.5368 | -51.1185 | -51.8967 | -51.3519 | -50.3906 | 70.7291 | -52.1301 | -51.622 | -51.828 | -52.0981 | -51.828 | -0.07782 | 0.004578 | -0.13733 | 0.98419 | 0.75073 | 0.20599 | 0.82855 | 0.28381 | -0.027466 | 0.054932 | -122.2961 | 0.27466 | 0.27466 | 0.004578 | 0.30212 | 0.032044 | 1.062 | 122.7173 | 0.30212 | 0.50812 | 122.8592 | 122.8592 | 122.7814 | 122.8317 | -122.8546 | -122.8043 | 122.6395 | 0.48065 | 4.4769 | 1.712
3661.1719 | 123.0469 | -52.0935 | 70.6879 | -0.045319 | 0.00040806 | 0.062239 | 0.069472 | 0.00037377 | 0.00026909 | 0.0064898 | 0.03833 | 0.00088875 | -0.00085457 | -0.0025036 | -0.0017197 | -0.0068615 | -0.00082886 | -47.6669 | 70.697 | -52.2034 | 70.4956 | -51.1597 | -51.9424 | -51.3565 | -50.4181 | 70.6833 | -52.1439 | -51.6312 | -51.8143 | -52.1072 | -51.8463 | -0.10986 | 0.009155 | -0.19226 | 0.93384 | 0.737 | 0.15106 | 0.84686 | 0.26093 | -0.050354 | -0.004577 | -122.319 | 0.27924 | 0.24719 | -0.013733 | 0.29755 | 0.036621 | 1.0437 | 122.699 | 0.32959 | 0.51269 | 122.9004 | 122.8271 | 122.7905 | 122.7768 | -122.8912 | -122.8317 | 122.5891 | 0.46234 | 4.4266 | 1.6754
3662.1719 | 122.9782 | -52.1255 | 70.6604 | -0.11398 | 0.0021171 | 0.062453 | 0.068404 | 0.0012284 | 0.0028327 | 0.0071308 | -0.025757 | -0.00017945 | 0.001709 | 5.9824e-05 | -0.0027877 | -0.0070753 | -0.00040166 | -47.6669 | 70.6284 | -52.1896 | 70.4681 | -51.1642 | -51.9882 | -51.4114 | -50.4547 | 70.6879 | -52.1622 | -51.6632 | -51.8829 | -52.1713 | -51.8829 | -0.064087 | -0.032043 | -0.19226 | 0.9613 | 0.71411 | 0.13733 | 0.7782 | 0.20142 | -0.036621 | 0.027466 | -122.3236 | 0.24261 | 0.24261 | -0.045777 | 0.27923 | -0.009156 | 1.0254 | 122.6578 | 0.27923 | 0.49896 | 122.818 | 122.85 | 122.7539 | 122.8134 | -122.85 | -122.8226 | 122.5937 | 0.46234 | 4.4586 | 1.6708
3663.1719 | 122.9553 | -52.0981 | 70.7336 | -0.068207 | -0.00044654 | 0.062025 | 0.06755 | -0.0017624 | 0.0019781 | 0.0062762 | -0.03186 | 0.0013159 | 0.00085443 | 0.0019824 | -0.0027877 | -0.0070753 | 2.554e-05 | -47.6257 | 70.6924 | -52.1439 | 70.5185 | -51.1414 | -51.915 | -51.3748 | -50.4272 | 70.7474 | -52.1347 | -51.6632 | -51.8784 | -52.1759 | -51.8829 | -0.045777 | -0.041199 | -0.21515 | 0.95673 | 0.72327 | 0.18311 | 0.76904 | 0.22888 | -0.036622 | 0.013732 | -122.3969 | 0.21973 | 0.21515 | -0.07782 | 0.25177 | -0.041198 | 1.0025 | 122.6624 | 0.25635 | 0.4715 | 122.8363 | 122.8821 | 122.7905 | 122.8455 | -122.8775 | -122.8683 | 122.6166 | 0.43488 | 4.4724 | 1.6708
3664.1719 | 123.0286 | -52.0752 | 70.6696 | -0.1445 | -1.9142e-05 | 0.060103 | 0.069045 | 0.001442 | 0.0019781 | 0.0045672 | 0.001709 | -0.00017945 | 0.00064083 | -0.00036738 | -0.0025741 | -0.0057935 | -0.0021107 | -47.6669 | 70.7016 | -52.1622 | 70.5185 | -51.1459 | -51.947 | -51.3565 | -50.4181 | 70.7199 | -52.1301 | -51.622 | -51.8097 | -52.1072 | -51.8326 | -0.086975 | 0.032043 | -0.15106 | 0.92926 | 0.71869 | 0.12817 | 0.80566 | 0.21515 | -0.054932 | 0.050354 | -122.2916 | 0.2655 | 0.24261 | -0.032044 | 0.29755 | 0.022888 | 1.0162 | 122.6807 | 0.32044 | 0.50812 | 122.8638 | 122.85 | 122.7768 | 122.7951 | -122.8317 | -122.7997 | 122.5937 | 0.45319 | 4.4083 | 1.6571
3665.1719 | 123.0652 | -52.0935 | 70.6924 | -0.11398 | 0.00019446 | 0.059889 | 0.068404 | -0.00069423 | 0.00069649 | 0.0054218 | -0.019653 | -0.00060665 | 0.001709 | 0.0026232 | -0.0025741 | -0.0036573 | -0.0029651 | -47.6715 | 70.6787 | -52.1759 | 70.4819 | -51.1734 | -51.9745 | -51.3886 | -50.4318 | 70.697 | -52.1576 | -51.6586 | -51.8646 | -52.2446 | -51.7548 | -0.082397 | -0.013733 | -0.21057 | 0.9201 | 0.70496 | 0.11902 | 0.78735 | 0.20142 | -0.064087 | 0.004577 | -122.3511 | 0.22888 | 0.33874 | -0.15106 | 0.40283 | -0.086975 | 1.0025 | 122.6578 | 0.29297 | 0.49896 | 122.8546 | 122.8546 | 122.7722 | 122.7905 | -122.8683 | -122.85 | 122.5754 | 0.43488 | 4.422 | 1.6617
3666.1719 | 122.9782 | -52.0981 | 70.6604 | -0.12924 | 0.0021171 | 0.061812 | 0.069259 | 0.0022964 | 0.0045417 | 0.0062762 | -0.016602 | -0.00082025 | -0.00021357 | -0.0031446 | -0.0030013 | -0.0047253 | -0.0033923 | -47.6624 | 70.6741 | -52.1851 | 70.491 | -51.1688 | -51.9699 | -51.3931 | -50.4456 | 70.7336 | -52.153 | -51.6266 | -51.8555 | -52.153 | -51.8555 | -0.086976 | 0.013733 | -0.16937 | 0.92926 | 0.70496 | 0.12817 | 0.79193 | 0.21515 | -0.054932 | 0.073243 | -122.287 | 0.24261 | 0.24261 | -0.054932 | 0.29755 | 0 | 1.0162 | 122.6761 | 0.29755 | 0.52643 | 122.8592 | 122.8867 | 122.7722 | 122.8317 | -122.8455 | -122.8134 | 122.5891 | 0.4715 | 4.4357 | 1.6525
3667.1719 | 122.9919 | -52.121 | 70.6879 | -0.16739 | 0.00083526 | 0.062666 | 0.069045 | -5.343e-05 | 0.0017645 | 0.003072 | -0.01355 | 0.0021703 | -0.00064077 | -0.00229 | -0.0027877 | -0.0060071 | -0.0038197 | -47.6486 | 70.6558 | -52.153 | 70.5048 | -51.1322 | -51.9745 | -51.3748 | -50.3998 | 70.7199 | -52.1347 | -51.6357 | -51.8555 | -52.1484 | -51.8555 | -0.032043 | -0.032043 | -0.1831 | 0.98877 | 0.74616 | 0.14648 | 0.7782 | 0.17853 | -0.013733 | 0.032044 | -122.3236 | 0.2655 | 0.2655 | -0.027465 | 0.27924 | -0.013732 | 1.0208 | 122.6578 | 0.27924 | 0.49896 | 122.8088 | 122.8546 | 122.7768 | 122.8409 | -122.8409 | -122.8226 | 122.6257 | 0.48523 | 4.4724 | 1.7212
3668.1719 | 122.9462 | -52.0477 | 70.7382 | -0.060578 | -0.00087374 | 0.061812 | 0.067763 | -0.0032578 | 0.0032599 | 0.0047808 | -0.0074462 | -0.0021021 | -0.0012818 | -0.0020764 | -0.0023605 | -0.0062207 | -0.0025379 | -47.5891 | 70.7382 | -52.1301 | 70.546 | -51.1093 | -51.8875 | -51.3336 | -50.4181 | 70.784 | -52.0981 | -51.6495 | -51.8463 | -52.1393 | -51.86 | -0.082398 | 0 | -0.19226 | 0.93841 | 0.71411 | 0.16022 | 0.79651 | 0.24262 | -0.050354 | 0.045777 | -122.3877 | 0.20142 | 0.18768 | -0.091553 | 0.23804 | -0.041199 | 1.0208 | 122.6761 | 0.25177 | 0.44861 | 122.8683 | 122.8821 | 122.7859 | 122.8317 | -122.8683 | -122.8363 | 122.5937 | 0.39825 | 4.4586 | 1.6296
3669.1719 | 122.9965 | -52.1027 | 70.7016 | -0.12924 | 0.00083526 | 0.06288 | 0.069259 | 0.0046464 | 0.0036871 | 0.0043536 | -0.068481 | 0.00024775 | 0.00042723 | 0.0051868 | -0.0027877 | -0.0047253 | -0.0018971 | -47.6807 | 70.697 | -52.2125 | 70.4498 | -51.2146 | -52.0294 | -51.4618 | -50.4639 | 70.7382 | -52.1576 | -51.6541 | -51.8921 | -52.1896 | -51.86 | -0.10986 | -0.004578 | -0.25177 | 0.88806 | 0.64087 | 0.073242 | 0.75073 | 0.18311 | -0.054932 | 0.036621 | -122.3557 | 0.21057 | 0.24262 | -0.086975 | 0.29755 | -0.032043 | 0.99792 | 122.6624 | 0.2655 | 0.50354 | 122.9095 | 122.8958 | 122.7997 | 122.8409 | -122.9141 | -122.8592 | 122.5525 | 0.44861 | 4.422 | 1.6388
3670.1719 | 123.0286 | -52.0981 | 70.6787 | -0.1445 | 0.0010489 | 0.062453 | 0.068404 | 0.0027238 | 0.00069649 | 0.0015766 | -0.08374 | 0.0032385 | 2.8e-08 | 0.00091422 | -0.0012925 | -0.0051527 | -0.0018971 | -47.6486 | 70.6879 | -52.2079 | 70.4865 | -51.1734 | -51.9836 | -51.4069 | -50.4135 | 70.7382 | -52.1393 | -51.6129 | -51.8326 | -52.1347 | -51.8097 | -0.10986 | 0.009155 | -0.19226 | 0.92468 | 0.69122 | 0.11444 | 0.80109 | 0.2243 | -0.041199 | 0.059509 | -122.2916 | 0.2655 | 0.28839 | -0.036622 | 0.32959 | 0.004577 | 1.0345 | 122.6944 | 0.3067 | 0.52643 | 122.8958 | 122.8775 | 122.7859 | 122.8363 | -122.8867 | -122.818 | 122.5845 | 0.48523 | 4.4495 | 1.6846
3671.1719 | 123.0103 | -52.0798 | 70.6741 | -0.12161 | 0.0025443 | 0.063948 | 0.068404 | -0.0041122 | 0.0024053 | 0.0077716 | -0.0074462 | 0.0017431 | 2.8e-08 | -0.0061352 | -0.0025741 | -0.0045117 | 0.0023755 | -47.612 | 70.6833 | -52.1759 | 70.5322 | -51.1002 | -51.9424 | -51.3428 | -50.3677 | 70.6924 | -52.1072 | -51.5945 | -51.8326 | -52.1164 | -51.8188 | -0.09613 | 0.009156 | -0.14191 | 0.97961 | 0.737 | 0.13733 | 0.83313 | 0.23346 | -0.027466 | 0.018311 | -122.2687 | 0.24719 | 0.26093 | -0.036621 | 0.28839 | -0.009155 | 1.0757 | 122.7081 | 0.27466 | 0.5127 | 122.8592 | 122.7997 | 122.7631 | 122.7722 | -122.85 | -122.7814 | 122.612 | 0.48523 | 4.4678 | 1.712
3672.1719 | 122.9919 | -52.0752 | 70.6833 | -0.1445 | -0.0021555 | 0.060744 | 0.069259 | -0.0013352 | 5.5488e-05 | 0.0056354 | 0.001709 | 0.00067495 | -0.00021357 | -0.003999 | -0.0034287 | -0.0042981 | -0.0025379 | -47.6257 | 70.6696 | -52.1667 | 70.5322 | -51.091 | -51.9287 | -51.3565 | -50.3769 | 70.697 | -52.1301 | -51.6312 | -51.8326 | -52.121 | -51.828 | -0.091553 | -0.013733 | -0.15106 | 0.98419 | 0.71869 | 0.14648 | 0.81024 | 0.23804 | -0.054932 | 0.013732 | -122.3145 | 0.24261 | 0.24719 | -0.045777 | 0.30212 | 0.009155 | 1.0757 | 122.699 | 0.29755 | 0.49896 | 122.8363 | 122.8271 | 122.7448 | 122.7722 | -122.85 | -122.8134 | 122.6074 | 0.44403 | 4.4495 | 1.6983
3673.1719 | 123.0011 | -52.0386 | 70.7336 | -0.037689 | -0.00044654 | 0.061812 | 0.067977 | -0.0011214 | 0.0024053 | 0.0052082 | 0.016968 | 3.4148e-05 | 0.00085443 | 0.0017688 | -0.0044967 | -0.0064343 | -0.0031787 | -47.5616 | 70.7245 | -52.153 | 70.5734 | -51.0635 | -51.8692 | -51.3107 | -50.354 | 70.7657 | -52.0981 | -51.6083 | -51.8051 | -52.0798 | -51.828 | -0.11444 | -0.009156 | -0.16022 | 0.97504 | 0.72784 | 0.16937 | 0.84229 | 0.28381 | -0.059509 | 0.032043 | -122.3419 | 0.23346 | 0.21057 | -0.041199 | 0.27008 | 0.01831 | 1.0895 | 122.7264 | 0.29297 | 0.48981 | 122.8775 | 122.8638 | 122.7631 | 122.8043 | -122.8867 | -122.8317 | 122.612 | 0.4303 | 4.4769 | 1.6846
3674.1719 | 123.0423 | -52.0706 | 70.7016 | -0.12924 | -0.00087374 | 0.062239 | 0.069686 | 0.0012284 | 0.0030463 | 0.0015766 | -0.062378 | -0.00060665 | 0.0023498 | 0.0051868 | -0.0032151 | -0.0038709 | 0.0019483 | -47.6395 | 70.6833 | -52.2034 | 70.5048 | -51.1368 | -51.9653 | -51.3794 | -50.4044 | 70.7291 | -52.1255 | -51.5808 | -51.8234 | -52.1164 | -51.796 | -0.13275 | -0.01831 | -0.19684 | 0.93384 | 0.69122 | 0.10529 | 0.82397 | 0.23804 | -0.054931 | 0.027466 | -122.2824 | 0.24719 | 0.27466 | -0.045776 | 0.32959 | 0.009155 | 1.0666 | 122.7081 | 0.30212 | 0.54474 | 122.8867 | 122.8546 | 122.7539 | 122.7997 | -122.905 | -122.8271 | 122.5754 | 0.48981 | 4.4312 | 1.6663
3675.1719 | 123.0331 | -52.0889 | 70.6833 | -0.075836 | -0.00044654 | 0.061812 | 0.070754 | 0.0063554 | 0.0019781 | 0.0052082 | -0.08374 | 0.00088875 | 2.8e-08 | 0.005614 | -0.0032151 | -0.0028027 | 0.0028027 | -47.6532 | 70.7016 | -52.1805 | 70.4681 | -51.1917 | -52.0111 | -51.4389 | -50.4456 | 70.7382 | -52.1301 | -51.6266 | -51.8555 | -52.1439 | -51.8326 | -0.091553 | 0.01831 | -0.21515 | 0.89722 | 0.65002 | 0.07782 | 0.74158 | 0.16937 | -0.041199 | 0.054931 | -122.3099 | 0.23346 | 0.25635 | -0.054932 | 0.29755 | -0.013733 | 0.98877 | 122.6486 | 0.27466 | 0.50354 | 122.8821 | 122.8683 | 122.7905 | 122.8271 | -122.8638 | -122.8134 | 122.5571 | 0.46234 | 4.4357 | 1.6434
3676.1719 | 122.9736 | -52.0752 | 70.6924 | -0.075836 | -0.0010873 | 0.061385 | 0.069045 | 0.0018692 | 0.0039007 | 0.0043536 | -0.050171 | 0.0015295 | -0.0012818 | 0.0045458 | -0.0015061 | -0.0040845 | -0.0016833 | -47.6669 | 70.7336 | -52.1851 | 70.4498 | -51.2238 | -52.0111 | -51.4435 | -50.4868 | 70.752 | -52.1576 | -51.6678 | -51.8967 | -52.1896 | -51.8784 | -0.10986 | 0.041199 | -0.24262 | 0.85144 | 0.63171 | 0.064087 | 0.74158 | 0.17395 | -0.082398 | 0.059509 | -122.3602 | 0.17853 | 0.19684 | -0.11444 | 0.27924 | -0.032043 | 0.9613 | 122.6349 | 0.26093 | 0.48981 | 122.9187 | 122.9095 | 122.8088 | 122.8271 | -122.8775 | -122.85 | 122.525 | 0.40741 | 4.4083 | 1.5884
3677.1719 | 122.9324 | -52.1439 | 70.7199 | -0.098725 | 0.0023307 | 0.061385 | 0.071609 | 0.0027238 | 0.0017645 | 0.0034992 | -0.08374 | 0.0034521 | 0.00021363 | 0.0036914 | -0.0012925 | -0.0049389 | 0.00045294 | -47.6715 | 70.7474 | -52.1667 | 70.4315 | -51.2375 | -52.0569 | -51.4755 | -50.5692 | 70.7657 | -52.1439 | -51.6861 | -51.8875 | -52.5467 | -52.1027 | -0.022888 | 0.027465 | -0.28839 | 0.90637 | 0.66833 | 0.086975 | 0.69122 | 0.10986 | 0 | 0.045776 | -122.406 | 0.25635 | 0.041199 | -0.40283 | 0.041199 | -0.40283 | 0.92926 | 122.5983 | 0.25635 | 0.45776 | 122.9141 | 122.9095 | 122.8912 | 122.9095 | -122.8867 | -122.8638 | 122.5754 | 0.45776 | 4.4724 | 1.5747
3678.1719 | 122.9874 | -52.066 | 70.7153 | -0.10635 | -0.00044654 | 0.06288 | 0.069686 | -5.343e-05 | 0.0026191 | 0.0017902 | 0.023071 | 0.00067495 | 0.0014954 | -0.0027174 | -0.0015061 | -0.0038709 | -0.0021107 | -47.612 | 70.7291 | -52.1439 | 70.5322 | -51.0864 | -51.9379 | -51.3474 | -50.3906 | 70.7336 | -52.1027 | -51.6083 | -51.8326 | -52.1118 | -51.8051 | -0.07782 | 0.013733 | -0.1831 | 0.97961 | 0.71869 | 0.12817 | 0.79651 | 0.20599 | -0.036621 | 0.018311 | -122.3236 | 0.23346 | 0.26093 | -0.045776 | 0.29755 | -0.009155 | 1.0574 | 122.6761 | 0.27008 | 0.49439 | 122.8729 | 122.8363 | 122.7951 | 122.7997 | -122.8592 | -122.818 | 122.5983 | 0.45776 | 4.454 | 1.6754
3679.1719 | 123.024 | -52.066 | 70.7245 | -0.15213 | -0.0013009 | 0.061812 | 0.070754 | -0.00069423 | 0.00091009 | 0.0047808 | -0.044067 | 3.4148e-05 | 2.8e-08 | 0.001128 | -0.0027877 | -0.0057935 | -0.0025379 | -47.6486 | 70.7108 | -52.1667 | 70.5093 | -51.1414 | -51.9745 | -51.3931 | -50.386 | 70.7199 | -52.1027 | -51.5854 | -51.8097 | -52.1027 | -51.7639 | -0.10071 | -0.013733 | -0.21515 | 0.92468 | 0.67291 | 0.091553 | 0.77362 | 0.19226 | -0.036621 | -0.004577 | -122.3099 | 0.25635 | 0.30212 | -0.036621 | 0.33874 | 0 | 1.0254 | 122.6761 | 0.29297 | 0.51727 | 122.8775 | 122.8226 | 122.7768 | 122.7859 | -122.8912 | -122.8271 | 122.5754 | 0.48065 | 4.4174 | 1.68
3680.1719 | 123.0652 | -52.0248 | 70.7108 | -0.13687 | 0.0012625 | 0.061385 | 0.069472 | -0.00026703 | 0.0034735 | 0.0047808 | -0.037964 | 0.0017431 | 0.0019226 | 0.00027342 | -0.0030013 | -0.0066479 | 0.00066654 | -47.5708 | 70.7062 | -52.1393 | 70.546 | -51.0773 | -51.9012 | -51.3428 | -50.3586 | 70.7428 | -52.0981 | -51.6037 | -52.002 | -51.9974 | -51.7181 | -0.11444 | -0.004577 | -0.16479 | 0.94757 | 0.68207 | 0.1236 | 0.79651 | 0.23804 | -0.073242 | 0.032044 | -122.3145 | 0.022888 | 0.3067 | 0.027466 | 0.37994 | 0.10071 | 1.062 | 122.6852 | 0.09613 | 0.49438 | 122.8455 | 122.8409 | 122.731 | 122.7676 | -122.85 | -122.8088 | 122.5708 | 0.42114 | 4.454 | 1.6663
3681.1719 | 122.9965 | -52.0706 | 70.7016 | -0.1445 | 0.00040806 | 0.064162 | 0.066054 | -0.00090783 | 0.0015509 | 0.0022174 | -0.0013428 | 0.0011023 | 2.8e-08 | 0.0013416 | -0.0032151 | -0.0049389 | -0.00082886 | -47.7127 | 70.665 | -52.1759 | 70.5597 | -51.0269 | -51.8784 | -51.3153 | -50.3448 | 70.7428 | -52.1118 | -51.5762 | -51.796 | -52.0889 | -51.7639 | -0.10528 | -0.036621 | -0.14191 | 1.0437 | 0.75531 | 0.19226 | 0.86059 | 0.29755 | -0.041198 | 0.041199 | -122.2778 | 0.27466 | 0.3067 | -0.01831 | 0.3479 | 0.022888 | 1.149 | 122.7356 | 0.31586 | 0.53558 | 122.8409 | 122.8546 | 122.7356 | 122.8134 | -122.8775 | -122.8134 | 122.6303 | 0.49439 | 4.3579 | 1.7258
3682.1719 | 122.9324 | -52.0752 | 70.7611 | -0.1445 | 0.00083526 | 0.062239 | 0.070968 | 0.0035782 | 0.0017645 | 0.005849 | -0.056274 | 0.00088875 | -0.00064077 | 0.0043322 | -0.0025741 | -0.0057935 | 0.00045294 | -47.6578 | 70.7565 | -52.1896 | 70.4361 | -51.2558 | -52.0248 | -51.4664 | -50.5234 | 70.784 | -52.1164 | -51.7914 | -52.1484 | -51.9608 | -51.6815 | -0.11444 | -0.004577 | -0.32501 | 0.8194 | 0.60883 | 0.050354 | 0.72327 | 0.16479 | -0.041199 | 0.022889 | -122.5525 | -0.073242 | 0.39368 | 0.11444 | 0.43487 | 0.15564 | 0.93384 | 122.6257 | -0.032043 | 0.32501 | 122.9462 | 122.9004 | 122.8317 | 122.8592 | -122.9507 | -122.8775 | 122.5113 | 0.28381 | 4.4174 | 1.5518
3683.1719 | 123.0469 | -52.0386 | 70.6375 | -0.083466 | 0.00062166 | 0.060957 | 0.068191 | -0.0024032 | 0.00069649 | 0.0045672 | -0.022705 | -0.00060665 | 0.0021362 | -0.002931 | -0.0042831 | -0.0066479 | 0.0019483 | -47.5937 | 70.7108 | -52.1393 | 70.5414 | -51.0818 | -51.8967 | -51.329 | -50.3448 | 70.7474 | -52.1027 | -51.5533 | -51.8005 | -52.0706 | -51.7548 | -0.10071 | 0.073242 | -0.09613 | 0.95673 | 0.70953 | 0.14191 | 0.81024 | 0.24262 | -0.064087 | 0.10986 | -122.1909 | 0.23804 | 0.28381 | -0.032044 | 0.3479 | 0.032043 | 1.0574 | 122.6807 | 0.30212 | 0.54932 | 122.85 | 122.85 | 122.7493 | 122.7859 | -122.7768 | -122.7402 | 122.58 | 0.48523 | 4.4449 | 1.6937
3684.1719 | 122.9187 | -52.0889 | 70.7657 | -0.083466 | -0.00023294 | 0.061812 | 0.071181 | 0.00080117 | 0.00026909 | 0.0060626 | -0.16614 | 0.0021703 | 0.00021363 | -0.00015378 | -0.0030013 | -0.0047253 | 0.0019483 | -47.6669 | 70.7794 | -52.1805 | 70.4453 | -51.2238 | -52.0203 | -51.5579 | -50.2396 | 70.7977 | -52.1164 | -51.6769 | -51.8784 | -52.2171 | -51.8646 | -0.091553 | 0.013733 | -0.32044 | 0.86517 | 0.53101 | 0.068664 | 0.62256 | 0.16022 | -0.027466 | 0.032043 | -122.4426 | 0.21057 | 0.2243 | -0.12817 | 0.25177 | -0.10071 | 0.95673 | 122.6257 | 0.23804 | 0.43945 | 122.9599 | 122.9141 | 122.8683 | 122.8867 | -122.9462 | -122.8821 | 122.5342 | 0.41199 | 4.422 | 1.8494
3685.1719 | 122.937 | -52.0798 | 70.752 | -0.075836 | -1.9142e-05 | 0.061598 | 0.070113 | 0.007637 | 0.0013373 | 0.0039264 | -0.059326 | 0.0013159 | 0.00021363 | -0.00015378 | -0.0010787 | -0.0047253 | -0.00018806 | -47.6166 | 70.7565 | -52.153 | 70.4681 | -51.1459 | -51.9562 | -51.3931 | -50.4639 | 70.8023 | -52.0889 | -51.6541 | -51.8784 | -52.1896 | -51.8509 | -0.073242 | 0.004578 | -0.28381 | 0.93384 | 0.68665 | 0.1236 | 0.75989 | 0.19684 | -0.009155 | 0.050354 | -122.406 | 0.20142 | 0.22888 | -0.10986 | 0.23804 | -0.10071 | 1.0071 | 122.6212 | 0.21057 | 0.43488 | 122.9095 | 122.8912 | 122.8363 | 122.8821 | -122.905 | -122.8409 | 122.5479 | 0.42572 | 4.4632 | 1.6159
3686.1719 | 122.9004 | -52.0706 | 70.7474 | -0.098725 | 0.00040806 | 0.062239 | 0.070113 | -0.00026703 | 0.0011237 | 0.0060626 | -0.059326 | -0.00082025 | -0.00021357 | 0.0045458 | -0.0015061 | -0.0038709 | 0.0034435 | -47.6303 | 70.7611 | -52.1759 | 70.4544 | -51.2192 | -52.0203 | -51.4481 | -50.4776 | 70.7886 | -52.1027 | -51.6769 | -51.9287 | -52.24 | -51.8829 | -0.10528 | 0.013733 | -0.29297 | 0.85144 | 0.62256 | 0.050354 | 0.72784 | 0.15564 | -0.032043 | 0.041199 | -122.4243 | 0.14191 | 0.18768 | -0.16937 | 0.21973 | -0.13733 | 0.95673 | 122.6303 | 0.17395 | 0.42572 | 122.937 | 122.8912 | 122.8317 | 122.8592 | -122.9233 | -122.85 | 122.525 | 0.39368 | 4.4403 | 1.593
3687.1719 | 122.9416 | -52.0798 | 70.7565 | -0.12924 | 0.0021171 | 0.062453 | 0.069686 | -0.00048063 | 0.0026191 | 0.00414 | -0.037964 | 0.0030249 | 0.0019226 | 0.0049732 | -0.00043791 | -0.0060071 | 0.0010937 | -47.6715 | 70.7611 | -52.1393 | 70.4407 | -51.1871 | -52.0203 | -51.4252 | -50.7248 | 70.7428 | -52.1484 | -51.622 | -51.9058 | -52.1896 | -51.8555 | -0.059509 | 0.004577 | -0.31586 | 0.89264 | 0.6546 | 0.059509 | 0.71411 | 0.11902 | -0.068664 | -0.013733 | -122.3785 | 0.17395 | 0.2243 | -0.10986 | 0.29297 | -0.041199 | 0.95215 | 122.58 | 0.24261 | 0.52643 | 122.9004 | 122.8912 | 122.8409 | 122.8226 | -122.8958 | -122.905 | 122.5204 | 0.45776 | 4.4083 | 1.355
3688.1719 | 122.9599 | -52.066 | 70.7565 | -0.03006 | -0.00087374 | 0.062239 | 0.069472 | -0.0032578 | 0.0026191 | 0.0056354 | -0.028809 | 0.00046135 | 0.00021363 | -0.0016492 | -0.0032151 | -0.0053663 | 0.0010937 | -47.6257 | 70.784 | -52.1347 | 70.4681 | -51.1734 | -51.9882 | -51.4206 | -50.4547 | 70.8115 | -52.0844 | -51.6403 | -51.8875 | -52.1713 | -51.8509 | -0.068665 | 0.027466 | -0.28839 | 0.89264 | 0.64545 | 0.07782 | 0.71411 | 0.14648 | -0.018311 | 0.054931 | -122.3969 | 0.17853 | 0.21515 | -0.10529 | 0.23346 | -0.086975 | 0.9613 | 122.6028 | 0.19684 | 0.44403 | 122.9187 | 122.8958 | 122.85 | 122.8775 | -122.8912 | -122.8409 | 122.5342 | 0.42572 | 4.4403 | 1.6113
3689.1719 | 122.9324 | -52.0569 | 70.7611 | -0.060578 | -0.00023294 | 0.061385 | 0.068191 | 0.00016017 | 0.0036871 | 0.0039264 | -0.044067 | 0.0017431 | 0.00064083 | -0.0027174 | -0.0012925 | -0.0047253 | 0.0053661 | -47.8821 | 70.7291 | -52.1713 | 70.5139 | -51.1459 | -51.9974 | -51.3931 | -50.4639 | 70.8252 | -52.0844 | -51.6449 | -51.8738 | -52.1713 | -51.8463 | -0.11444 | -0.032043 | -0.24719 | 0.91095 | 0.66376 | 0.05951 | 0.7782 | 0.17395 | -0.027466 | 0.064087 | -122.406 | 0.18311 | 0.21057 | -0.11444 | 0.23804 | -0.086975 | 1.0254 | 122.6852 | 0.21057 | 0.43945 | 122.9004 | 122.9095 | 122.786 | 122.8821 | -122.9324 | -122.8455 | 122.5708 | 0.41199 | 4.1748 | 1.593
3690.1719 | 122.9599 | -52.0294 | 70.7886 | -0.083466 | -1.9142e-05 | 0.060316 | 0.068404 | -0.0026168 | -0.00037171 | 0.005849 | -0.03186 | 0.0030249 | 0.001709 | 0.0017688 | -0.00043791 | -0.0068615 | 2.554e-05 | -47.58 | 70.8069 | -52.1072 | 70.5551 | -51.0635 | -51.8875 | -51.3382 | -50.3357 | 70.8389 | -52.0615 | -51.5762 | -51.7731 | -52.0981 | -51.7822 | -0.07782 | 0.018311 | -0.23346 | 0.96588 | 0.69122 | 0.14191 | 0.76904 | 0.21973 | -0.032043 | 0.050354 | -122.3648 | 0.25635 | 0.24719 | -0.068664 | 0.27923 | -0.036621 | 1.0437 | 122.6624 | 0.28839 | 0.48523 | 122.9141 | 122.9004 | 122.8363 | 122.8683 | -122.8958 | -122.85 | 122.5845 | 0.45319 | 4.4495 | 1.6937
3691.1719 | 122.9691 | -52.0386 | 70.7794 | -0.075836 | 0.0010489 | 0.06053 | 0.068404 | 0.0016556 | 0.0028327 | 0.0017902 | -0.019653 | 0.0023839 | 0.0023498 | 0.0013416 | -0.0019333 | -0.0051527 | 0.0034435 | -47.5388 | 70.8115 | -52.0935 | 70.5414 | -51.0864 | -51.8967 | -51.3519 | -50.3677 | 70.816 | -52.0569 | -51.59 | -51.8097 | -52.0935 | -51.7868 | -0.054932 | 0.032043 | -0.23804 | 0.95215 | 0.68664 | 0.14191 | 0.74158 | 0.19684 | -0.018311 | 0.036621 | -122.3694 | 0.22888 | 0.25177 | -0.054932 | 0.27008 | -0.036621 | 1.0071 | 122.6349 | 0.24719 | 0.46692 | 122.905 | 122.8729 | 122.85 | 122.8546 | -122.8729 | -122.8363 | 122.58 | 0.44861 | 4.4998 | 1.6708
3692.1719 | 122.9279 | -52.034 | 70.7703 | -0.075836 | 0.0014761 | 0.061598 | 0.070541 | -0.00090783 | 0.0049689 | 0.0069172 | -0.03186 | -0.00017945 | 0.0029906 | -0.0027174 | -0.0027877 | -0.0049389 | 0.0013073 | -47.5754 | 70.7703 | -52.1255 | 70.4956 | -51.1276 | -51.947 | -51.4023 | -50.4044 | 70.8206 | -52.0798 | -51.6312 | -51.8646 | -52.1759 | -51.8463 | -0.091552 | 0 | -0.27466 | 0.90637 | 0.63171 | 0.086976 | 0.72327 | 0.17853 | -0.045776 | 0.050354 | -122.4014 | 0.16937 | 0.18768 | -0.14191 | 0.23346 | -0.09613 | 0.99792 | 122.6212 | 0.21515 | 0.44861 | 122.8958 | 122.9004 | 122.8043 | 122.8546 | -122.8958 | -122.85 | 122.5296 | 0.40283 | 4.4586 | 1.6296
3693.1719 | 122.9691 | -52.0386 | 70.7886 | -0.10635 | 0.0012625 | 0.062453 | 0.070113 | -0.005394 | 0.0011237 | 0.0052082 | -0.019653 | 0.0023839 | 0.0014954 | 0.00048702 | -0.0015061 | -0.0042981 | 0.0036571 | -47.6212 | 70.784 | -52.1576 | 70.5414 | -51.265 | -51.9196 | -51.3565 | -50.4227 | 70.8344 | -52.0798 | -51.6495 | -51.8738 | -52.1576 | -51.8326 | -0.11902 | -0.004577 | -0.24719 | 0.77362 | 0.68207 | 0.11902 | 0.80109 | 0.23804 | -0.041199 | 0.045777 | -122.438 | 0.16479 | 0.20599 | -0.11902 | 0.24719 | -0.07782 | 0.89264 | 122.699 | 0.20599 | 0.4303 | 122.9416 | 122.9141 | 122.8226 | 122.8729 | -122.9462 | -122.8683 | 122.58 | 0.3891 | 4.4174 | 1.6159
3694.1719 | 122.9462 | -52.0248 | 70.7977 | -0.10635 | 0.00019446 | 0.059889 | 0.068832 | 0.0010148 | 0.0036871 | 0.0077716 | -0.019653 | 0.0013159 | 0.001709 | -0.00464 | -0.0023605 | -0.0060071 | 0.00045294 | -47.5525 | 70.8023 | -52.1027 | 70.5276 | -51.1047 | -51.9058 | -51.3611 | -50.3632 | 70.8389 | -52.0615 | -51.622 | -51.8417 | -52.1301 | -51.8234 | -0.07782 | 0.004578 | -0.27008 | 0.9201 | 0.66376 | 0.11902 | 0.74158 | 0.19684 | -0.036621 | 0.041199 | -122.4197 | 0.18311 | 0.20142 | -0.10529 | 0.23804 | -0.068665 | 0.99792 | 122.6303 | 0.21973 | 0.43945 | 122.905 | 122.9004 | 122.8271 | 122.8638 | -122.9004 | -122.8592 | 122.5525 | 0.40283 | 4.4724 | 1.6617
3695.1719 | 122.937 | -52.034 | 70.8115 | -0.075836 | -0.0027963 | 0.062453 | 0.069259 | 0.0069962 | 0.00069649 | 0.0047808 | -0.0013428 | 0.0021703 | 0.0023498 | 0.0024096 | -0.0015061 | -0.0042981 | 0.0015209 | -47.5433 | 70.8115 | -52.1164 | 70.5414 | -51.091 | -51.8921 | -51.3565 | -50.3677 | 70.8435 | -52.0798 | -51.59 | -51.8463 | -52.1118 | -51.8143 | -0.082397 | 0 | -0.27008 | 0.94299 | 0.67749 | 0.14191 | 0.75989 | 0.2243 | -0.045776 | 0.032044 | -122.4014 | 0.18768 | 0.21973 | -0.077819 | 0.2655 | -0.032043 | 1.0254 | 122.6578 | 0.23346 | 0.48981 | 122.9279 | 122.9233 | 122.8455 | 122.8775 | -122.9279 | -122.8912 | 122.5754 | 0.44403 | 4.4907 | 1.6663
3696.1719 | 122.905 | -52.0477 | 70.8023 | -0.10635 | 0.0021171 | 0.061171 | 0.071609 | 0.0033646 | 0.0039007 | 0.0064898 | -0.028809 | 0.0023839 | 0.0012818 | -0.0010084 | -0.0021469 | -0.0042981 | -0.00018806 | -47.5754 | 70.8115 | -52.1164 | 70.5048 | -51.123 | -51.9379 | -51.3794 | -50.3998 | 70.8435 | -52.0569 | -51.6403 | -51.8738 | -52.1576 | -51.8326 | -0.068665 | 0.009155 | -0.29755 | 0.92468 | 0.66833 | 0.10986 | 0.737 | 0.17853 | -0.009156 | 0.041199 | -122.4426 | 0.17395 | 0.21515 | -0.10986 | 0.2243 | -0.10071 | 0.99335 | 122.6212 | 0.18311 | 0.41656 | 122.9279 | 122.9004 | 122.8592 | 122.8912 | -122.9187 | -122.8592 | 122.5525 | 0.40741 | 4.4724 | 1.6479
3697.1719 | 122.905 | -52.0477 | 70.7977 | -0.098725 | -1.9142e-05 | 0.063734 | 0.069259 | -0.00069423 | 0.0030463 | 0.005849 | -0.03186 | 0.0015295 | 0.00021363 | -0.0016492 | -0.0015061 | -0.0051527 | -0.0036059 | -47.5479 | 70.8252 | -52.0706 | 70.5368 | -51.1139 | -51.9241 | -51.3794 | -50.386 | 70.8435 | -52.0752 | -51.622 | -51.8463 | -52.1484 | -51.8051 | -0.022889 | 0.027466 | -0.26093 | 0.93384 | 0.66833 | 0.1236 | 0.69122 | 0.14649 | -0.027466 | 0.045777 | -122.4197 | 0.20142 | 0.24261 | -0.10071 | 0.27008 | -0.073242 | 0.95673 | 122.6074 | 0.22888 | 0.45319 | 122.8958 | 122.9187 | 122.8729 | 122.8912 | -122.8683 | -122.8729 | 122.5845 | 0.42572 | 4.4998 | 1.6617
3698.1719 | 123.0515 | -51.9928 | 70.7382 | -0.11398 | -0.00044654 | 0.061385 | 0.068404 | -0.0021896 | 0.0030463 | 0.0039264 | 0.026123 | 0.0011023 | 0.0019226 | -0.00079478 | -0.0025741 | -0.0053663 | 0.0036571 | -47.5479 | 70.7932 | -52.0935 | 70.5688 | -51.0406 | -51.86 | -51.3016 | -50.2899 | 70.7748 | -52.034 | -51.5305 | -51.741 | -52.0477 | -51.7227 | -0.10071 | 0.054932 | -0.16937 | 0.95215 | 0.69122 | 0.13275 | 0.79193 | 0.23346 | -0.041199 | 0.036621 | -122.2687 | 0.25177 | 0.27008 | -0.054931 | 0.31128 | -0.013732 | 1.0529 | 122.6624 | 0.29297 | 0.50354 | 122.8867 | 122.8088 | 122.786 | 122.7676 | -122.8317 | -122.7722 | 122.5616 | 0.46234 | 4.4449 | 1.7029
3699.1719 | 122.9553 | -51.9928 | 70.8115 | -0.10635 | -0.00023294 | 0.061385 | 0.0699 | 0.0012284 | 0.0024053 | 0.0047808 | -0.0013428 | -0.0012477 | 0.00042723 | -0.0059216 | -0.0023605 | -0.0053663 | 0.0025891 | -47.5296 | 70.8252 | -52.0889 | 70.5505 | -51.0773 | -51.8921 | -51.3382 | -50.3494 | 70.8572 | -52.0477 | -51.6083 | -51.8234 | -52.1164 | -51.796 | -0.09613 | 0.013733 | -0.26093 | 0.91553 | 0.6546 | 0.10071 | 0.75073 | 0.19684 | -0.054931 | 0.045777 | -122.4197 | 0.16937 | 0.19684 | -0.1236 | 0.25177 | -0.068665 | 1.0117 | 122.6395 | 0.2243 | 0.43945 | 122.9141 | 122.905 | 122.818 | 122.85 | -122.9004 | -122.8592 | 122.5433 | 0.38452 | 4.4632 | 1.6434
3700.1719 | 122.9416 | -51.9882 | 70.816 | -0.075836 | -0.0013009 | 0.063521 | 0.069472 | 0.0018692 | 0.0019781 | 0.0047808 | -0.016602 | 0.0011023 | 0.0029906 | 0.0026232 | -0.0021469 | -0.0045117 | 0.00088014 | -47.5067 | 70.8344 | -52.0935 | 70.5688 | -51.0727 | -51.8829 | -51.3336 | -50.3311 | 70.8527 | -52.034 | -51.5808 | -51.828 | -52.0981 | -51.7776 | -0.10529 | 0.018311 | -0.24719 | 0.91553 | 0.6546 | 0.10528 | 0.75989 | 0.21057 | -0.045777 | 0.036621 | -122.3969 | 0.16022 | 0.21057 | -0.10986 | 0.25635 | -0.064086 | 1.0208 | 122.6624 | 0.20599 | 0.45319 | 122.9279 | 122.8867 | 122.8226 | 122.8409 | -122.9095 | -122.85 | 122.5571 | 0.40741 | 4.4815 | 1.6571
3701.1719 | 122.9187 | -52.0111 | 70.8115 | -0.068207 | -0.00087374 | 0.061598 | 0.068618 | -0.00026703 | 0.0011237 | 0.0056354 | -0.028809 | 0.0013159 | 0.0014954 | -0.00036738 | -0.0030013 | -0.0062207 | -0.0012561 | -47.5433 | 70.8344 | -52.0844 | 70.5414 | -51.1185 | -51.9012 | -51.3474 | -50.3723 | 70.8389 | -52.0248 | -51.6083 | -51.8509 | -52.1255 | -51.8097 | -0.073243 | 0.022889 | -0.27008 | 0.89264 | 0.66376 | 0.10986 | 0.737 | 0.18311 | -0.013733 | 0.027466 | -122.4197 | 0.16022 | 0.20142 | -0.11444 | 0.21515 | -0.10071 | 0.96588 | 122.6257 | 0.17395 | 0.41657 | 122.9187 | 122.8638 | 122.8455 | 122.85 | -122.8958 | -122.8363 | 122.5525 | 0.40283 | 4.4678 | 1.6388
3702.1719 | 122.9462 | -51.9791 | 70.816 | -0.037689 | 0.0021171 | 0.060957 | 0.068191 | 0.00037377 | 0.00091009 | 0.0054218 | -0.03186 | 0.0015295 | 0.0014954 | -0.00229 | -0.0019333 | -0.0062207 | 0.0060071 | -47.5159 | 70.8389 | -52.0935 | 70.5551 | -51.059 | -51.8509 | -51.3336 | -50.2441 | 70.8755 | -52.034 | -51.5488 | -51.7731 | -52.0569 | -51.7593 | -0.11444 | 0.022888 | -0.26093 | 0.9201 | 0.64545 | 0.12817 | 0.75989 | 0.24262 | -0.054932 | 0.059509 | -122.3648 | 0.20599 | 0.21973 | -0.07782 | 0.27466 | -0.022888 | 1.0345 | 122.6486 | 0.26093 | 0.48523 | 122.9324 | 122.9095 | 122.818 | 122.8546 | -122.9095 | -122.85 | 122.5342 | 0.4303 | 4.4632 | 1.7349
3703.1719 | 122.8958 | -52.0294 | 70.8298 | -0.12924 | -0.00066014 | 0.062666 | 0.070327 | 0.00016017 | 0.0019781 | 0.005849 | -0.053223 | -0.0014613 | 0.0021362 | -0.0031446 | 0.00020289 | -0.0055799 | 2.554e-05 | -47.5983 | 70.8344 | -52.1255 | 70.4865 | -51.1642 | -51.9791 | -51.5533 | -50.1572 | 70.8389 | -52.0477 | -51.6174 | -51.8417 | -52.1622 | -51.828 | -0.09613 | 0.004578 | -0.34332 | 0.86517 | 0.47607 | 0.050354 | 0.5722 | 0.14648 | -0.01831 | 0.009155 | -122.4472 | 0.18768 | 0.20142 | -0.13275 | 0.21973 | -0.11444 | 0.9613 | 122.612 | 0.20599 | 0.4303 | 122.9599 | 122.8867 | 122.8638 | 122.8683 | -122.9553 | -122.8775 | 122.5159 | 0.41199 | 4.4312 | 1.8723
3704.1719 | 123.0377 | -51.9562 | 70.784 | -0.12161 | 0.0014761 | 0.061171 | 0.069259 | 0.00058737 | 0.00048269 | 0.0056354 | -0.0013428 | -0.00017945 | 0.001709 | 0.00070062 | -0.0015061 | -0.0047253 | -0.0021107 | -47.5342 | 70.7748 | -52.1027 | 70.5643 | -51.0681 | -51.8875 | -51.3107 | -50.3036 | 70.7794 | -52.0477 | -51.5259 | -51.7364 | -52.0523 | -51.7181 | -0.14648 | -0.009156 | -0.21973 | 0.88806 | 0.64545 | 0.068665 | 0.79193 | 0.21515 | -0.091552 | -0.004578 | -122.3099 | 0.21973 | 0.23804 | -0.09613 | 0.32959 | -0.004578 | 1.0345 | 122.6669 | 0.31128 | 0.52185 | 122.8775 | 122.8271 | 122.731 | 122.7356 | -122.8867 | -122.8317 | 122.5204 | 0.4303 | 4.422 | 1.6525
3705.1719 | 122.937 | -51.9882 | 70.8618 | -0.0071715 | -0.0017281 | 0.060957 | 0.068832 | -0.00048063 | 0.00091009 | 0.0062762 | 0.026123 | 0.00088875 | 0.001709 | -0.0027174 | -0.0015061 | -0.0057935 | 0.00045294 | -47.5204 | 70.903 | -52.0386 | 70.4498 | -51.2283 | -51.8097 | -51.3245 | -50.3769 | 70.8755 | -52.0294 | -51.5945 | -51.7914 | -52.0798 | -51.8005 | -0.050354 | 0.041199 | -0.41199 | 0.75989 | 0.66376 | 0.17853 | 0.71411 | 0.22888 | -0.041199 | 0.013733 | -122.4564 | 0.19684 | 0.18768 | -0.091553 | 0.22888 | -0.050354 | 0.81024 | 122.4884 | 0.23804 | 0.43488 | 122.9416 | 122.905 | 122.8912 | 122.8638 | -122.9004 | -122.8912 | 122.438 | 0.39368 | 4.4678 | 1.6113
3706.1719 | 122.9599 | -51.9791 | 70.8572 | -0.052948 | -0.0013009 | 0.061171 | 0.067763 | 0.001442 | 0.0013373 | 0.0060626 | -0.0013428 | 0.00067495 | 0.001068 | -0.0020764 | -0.0023605 | -0.0040845 | 0.00066654 | -47.4838 | 70.8664 | -52.0569 | 70.5872 | -51.0498 | -51.8555 | -51.2924 | -50.3082 | 70.8664 | -52.0111 | -51.5396 | -51.7548 | -52.0523 | -51.7548 | -0.07782 | 0.009155 | -0.27008 | 0.92926 | 0.68665 | 0.1236 | 0.76447 | 0.20142 | -0.032043 | 0.009155 | -122.3969 | 0.2243 | 0.2243 | -0.073242 | 0.25635 | -0.041199 | 1.0071 | 122.644 | 0.25635 | 0.4715 | 122.9233 | 122.8775 | 122.8455 | 122.8455 | -122.9141 | -122.8683 | 122.5662 | 0.43945 | 4.4952 | 1.6708
3707.1719 | 122.9691 | -51.9653 | 70.8527 | -0.12924 | 0.0014761 | 0.062453 | 0.070327 | -0.0013352 | 0.0017645 | 0.0045672 | -0.0043946 | 0.00088875 | -0.00021357 | 0.0015552 | -0.0021469 | -0.0042981 | -0.0010425 | -47.5021 | 70.8527 | -52.0615 | 70.5322 | -51.1505 | -51.8372 | -51.2009 | -50.2853 | 70.9213 | -52.002 | -51.535 | -51.7685 | -52.066 | -51.7456 | -0.09613 | 0 | -0.32043 | 0.81482 | 0.76446 | 0.12817 | 0.86059 | 0.2243 | -0.036621 | 0.068665 | -122.3877 | 0.19684 | 0.21973 | -0.10071 | 0.25635 | -0.064087 | 0.91095 | 122.5937 | 0.23346 | 0.46692 | 122.9141 | 122.9233 | 122.818 | 122.8867 | -122.9141 | -122.8546 | 122.4976 | 0.4303 | 4.4632 | 1.68
3708.1719 | 122.9141 | -51.9928 | 70.8115 | -0.1445 | 0.00062166 | 0.061385 | 0.068832 | 0.004219 | 0.0032599 | 0.0049946 | 0.0047608 | 0.00024775 | 0.00085443 | -0.0050672 | -0.0027877 | -0.0051527 | 0.0030163 | -47.5662 | 70.8252 | -52.1072 | 70.4727 | -50.853 | -51.8051 | -51.3794 | -50.3998 | 70.8481 | -52.034 | -51.6083 | -51.8509 | -52.1484 | -51.8005 | -0.11444 | 0.013733 | -0.33875 | 1.1398 | 0.6134 | 0.18768 | 0.72784 | 0.30212 | -0.041199 | 0.036621 | -122.4197 | 0.14191 | 0.19226 | -0.15564 | 0.23346 | -0.11444 | 1.2543 | 122.58 | 0.18311 | 0.42572 | 122.9324 | 122.8821 | 122.818 | 122.8409 | -122.9187 | -122.8455 | 122.4655 | 0.38452 | 4.4266 | 1.593
3709.1719 | 123.0011 | -51.9516 | 70.8023 | -0.15976 | 0.0019035 | 0.062666 | 0.066909 | -0.0011214 | 0.0036871 | 0.0034992 | 0.053589 | 0.00088875 | -0.00021357 | -0.0018628 | -0.0021469 | -0.0062207 | 0.0023755 | -47.4747 | 70.7886 | -52.0523 | 70.6329 | -50.9811 | -51.8234 | -51.2421 | -50.2487 | 70.8023 | -52.0065 | -51.5167 | -51.7456 | -52.0294 | -51.709 | -0.10071 | -0.013733 | -0.16937 | 0.97046 | 0.70953 | 0.12817 | 0.81024 | 0.22888 | -0.054932 | 0 | -122.319 | 0.20599 | 0.24262 | -0.07782 | 0.29755 | -0.022888 | 1.0712 | 122.6852 | 0.26093 | 0.48981 | 122.8409 | 122.8088 | 122.7402 | 122.7539 | -122.8546 | -122.8088 | 122.5845 | 0.43487 | 4.4769 | 1.7029
3710.1719 | 122.9782 | -51.9791 | 70.8572 | -0.03006 | 0.0016899 | 0.06053 | 0.0699 | -0.00090783 | 0.0028327 | 0.0049946 | -0.019653 | 0.0015295 | 0.0012818 | 0.0051868 | -0.0025741 | -0.0060071 | 0.00045294 | -47.493 | 70.8664 | -52.0615 | 70.5872 | -51.091 | -51.8372 | -51.297 | -50.3494 | 70.8939 | -52.0294 | -51.5579 | -51.7639 | -52.0706 | -51.7502 | -0.082397 | 0.009155 | -0.27008 | 0.88806 | 0.68207 | 0.14191 | 0.76447 | 0.2243 | -0.050354 | 0.036621 | -122.4152 | 0.21515 | 0.22888 | -0.091553 | 0.27924 | -0.041199 | 0.97046 | 122.6486 | 0.2655 | 0.4715 | 122.9279 | 122.9233 | 122.8455 | 122.8729 | -122.9187 | -122.8867 | 122.5662 | 0.42114 | 4.4861 | 1.6296
3711.1719 | 122.9736 | -51.9653 | 70.8481 | -0.037689 | -0.00087374 | 0.062239 | 0.069045 | 0.0018692 | 0.0017645 | 0.007558 | 0.016968 | 0.00067495 | 0.001709 | -0.00079478 | -0.0034287 | -0.0042981 | 0.0032299 | -47.4838 | 70.8801 | -52.0477 | 70.5872 | -51.0727 | -51.8509 | -51.2924 | -50.3357 | 70.9442 | -51.9836 | -51.5396 | -51.7456 | -52.0432 | -51.7502 | -0.082397 | 0.032044 | -0.26093 | 0.89264 | 0.67291 | 0.11444 | 0.75531 | 0.19684 | -0.018311 | 0.096131 | -122.3877 | 0.21973 | 0.21515 | -0.07782 | 0.23346 | -0.059509 | 0.97504 | 122.6349 | 0.23804 | 0.44403 | 122.9279 | 122.9279 | 122.8455 | 122.9095 | -122.8958 | -122.8317 | 122.5525 | 0.42572 | 4.4815 | 1.6296
3712.1719 | 122.9828 | -51.9608 | 70.871 | -0.045319 | -0.00023294 | 0.062239 | 0.068618 | -0.00069423 | 0.0024053 | 0.0071308 | -0.016602 | 0.0015295 | 0.0021362 | 0.001128 | -0.0025741 | -0.0049389 | -0.0029651 | -47.4426 | 70.8618 | -52.0569 | 70.61 | -51.0086 | -51.8372 | -51.2787 | -50.2899 | 70.8847 | -51.9699 | -51.5167 | -51.741 | -52.0386 | -51.7273 | -0.096131 | -0.009156 | -0.26093 | 0.95215 | 0.68207 | 0.1236 | 0.7782 | 0.21973 | -0.009156 | 0.013733 | -122.3877 | 0.21973 | 0.23346 | -0.07782 | 0.24262 | -0.068664 | 1.0483 | 122.6669 | 0.22888 | 0.45319 | 122.9187 | 122.8546 | 122.8226 | 122.8455 | -122.9279 | -122.8409 | 122.5708 | 0.44403 | 4.5181 | 1.6708
3713.1719 | 123.0835 | -51.9791 | 70.7932 | -0.098725 | 0.00062166 | 0.062453 | 0.067763 | 0.0022964 | 0.0045417 | 0.0045672 | 0.032227 | 0.00067495 | 0.0012818 | 0.0060412 | -0.0019333 | -0.0053663 | 0.0019483 | -47.4655 | 70.7977 | -52.034 | 70.6192 | -50.9857 | -51.8143 | -51.2329 | -50.2304 | 70.8481 | -51.9836 | -51.4709 | -51.6495 | -52.2034 | -51.8143 | -0.054932 | 0.004577 | -0.17395 | 0.99335 | 0.74616 | 0.16479 | 0.80109 | 0.21973 | -0.004578 | 0.054931 | -122.2641 | 0.32959 | 0.16479 | -0.2243 | 0.16937 | -0.21973 | 1.0483 | 122.6532 | 0.33417 | 0.5127 | 122.8317 | 122.8317 | 122.7768 | 122.8271 | -122.8271 | -122.7768 | 122.5983 | 0.50812 | 4.5135 | 1.7487
3714.1719 | 122.9965 | -51.9562 | 70.8023 | -0.098725 | -1.9142e-05 | 0.060744 | 0.066909 | -0.003685 | 0.00048269 | 0.0039264 | 0.062744 | 0.0011023 | 0.0023498 | -0.0014356 | -0.0021469 | -0.010493 | -0.00018806 | -47.4792 | 70.8206 | -52.0432 | 70.6146 | -51.0086 | -51.8326 | -51.2558 | -50.2853 | 70.8664 | -51.9836 | -51.4023 | -51.8326 | -52.0203 | -51.7227 | -0.086975 | 0.018311 | -0.18768 | 0.94757 | 0.70038 | 0.1236 | 0.78735 | 0.21057 | -0.027466 | 0.064087 | -122.2046 | 0.1236 | 0.23346 | -0.064087 | 0.26093 | -0.036621 | 1.0345 | 122.6578 | 0.15106 | 0.58136 | 122.8638 | 122.85 | 122.7768 | 122.8226 | -122.8455 | -122.7859 | 122.5708 | 0.55389 | 4.4769 | 1.6708
3715.1719 | 122.9553 | -51.9424 | 70.8755 | -0.083466 | -0.00087374 | 0.059035 | 0.065414 | -5.343e-05 | 0.0028327 | 0.0069172 | -0.095947 | 0.0017431 | -0.0019226 | 0.0047594 | -0.0038559 | -0.0045117 | -0.00061526 | -47.4289 | 70.8527 | -52.0432 | 70.6238 | -51.0178 | -51.8417 | -51.329 | -50.1984 | 70.9213 | -51.9745 | -51.5076 | -51.7456 | -52.0294 | -51.7181 | -0.10071 | -0.022888 | -0.25177 | 0.92468 | 0.6134 | 0.10071 | 0.71411 | 0.20142 | -0.032043 | 0.045777 | -122.3831 | 0.19684 | 0.2243 | -0.086975 | 0.25635 | -0.054932 | 1.0254 | 122.6669 | 0.22888 | 0.46692 | 122.8958 | 122.8958 | 122.7951 | 122.8638 | -122.9187 | -122.85 | 122.5662 | 0.43488 | 4.5136 | 1.7441
3716.1719 | 122.9691 | -51.9196 | 70.871 | -0.10635 | 0.0016899 | 0.062239 | 0.068618 | -0.00026703 | 0.0030463 | 0.0060626 | -0.037964 | 0.0017431 | 0.0014954 | 0.0024096 | -0.0027877 | -0.0075025 | 0.0040845 | -47.4335 | 70.8801 | -52.0203 | 70.6192 | -50.9903 | -51.8097 | -51.2604 | -50.1846 | 70.9122 | -51.9791 | -51.4984 | -51.7227 | -52.066 | -51.741 | -0.10071 | 0.009155 | -0.25177 | 0.92926 | 0.65918 | 0.10986 | 0.75989 | 0.21057 | -0.059509 | 0.041198 | -122.3694 | 0.19684 | 0.17853 | -0.14648 | 0.23804 | -0.086975 | 1.03 | 122.6395 | 0.25635 | 0.48065 | 122.9004 | 122.8912 | 122.7997 | 122.8317 | -122.8912 | -122.85 | 122.5388 | 0.42114 | 4.4861 | 1.7349
3717.1719 | 122.9279 | -51.947 | 70.8618 | -0.12161 | 0.0016899 | 0.063094 | 0.071609 | 0.0029374 | 0.0021917 | 0.0052082 | -0.03186 | -0.00017945 | 0.001709 | -0.0014356 | -0.00086511 | -0.0060071 | -0.0012561 | -47.4747 | 70.8847 | -52.0523 | 70.5826 | -51.0727 | -51.8875 | -51.3336 | -50.3586 | 70.903 | -52.0203 | -51.5854 | -51.8097 | -52.1255 | -51.7731 | -0.10529 | 0.022889 | -0.27923 | 0.87433 | 0.6134 | 0.059509 | 0.71869 | 0.16479 | -0.073243 | 0.041199 | -122.4472 | 0.13733 | 0.17395 | -0.17853 | 0.24719 | -0.10529 | 0.97961 | 122.6349 | 0.21057 | 0.43488 | 122.937 | 122.9233 | 122.8317 | 122.85 | -122.9141 | -122.8821 | 122.5296 | 0.36163 | 4.4724 | 1.5884
3718.1719 | 122.9462 | -51.9379 | 70.8847 | -0.03006 | -1.9142e-05 | 0.062239 | 0.069472 | 0.0020828 | 0.0011237 | 0.0049946 | -0.037964 | 0.00024775 | 0.001068 | 0.007323 | -0.0019333 | -0.0051527 | -0.00082886 | -47.4014 | 70.871 | -52.0157 | 70.6055 | -50.9949 | -51.8188 | -51.2787 | -50.2579 | 70.8847 | -51.9608 | -51.5167 | -51.7502 | -52.0523 | -51.7273 | -0.07782 | -0.013733 | -0.27924 | 0.94299 | 0.65918 | 0.11902 | 0.737 | 0.19684 | -0.022888 | 0 | -122.4014 | 0.18768 | 0.21057 | -0.11444 | 0.23346 | -0.091553 | 1.0208 | 122.6212 | 0.21057 | 0.44403 | 122.8867 | 122.8455 | 122.8088 | 122.8226 | -122.9004 | -122.8455 | 122.5433 | 0.42114 | 4.5364 | 1.68
3719.1719 | 122.9691 | -51.947 | 70.8893 | -0.060578 | 0.0010489 | 0.063307 | 0.068404 | -0.00090783 | 0.00091009 | 0.0045672 | 0.013916 | 0.0032385 | 0.00042723 | -0.0025036 | -0.0012925 | -0.0047253 | -0.00018806 | -47.438 | 70.9122 | -52.0248 | 70.6055 | -51.0315 | -51.8097 | -51.265 | -50.2899 | 70.9305 | -51.9653 | -51.5167 | -51.7136 | -51.9928 | -51.6953 | -0.07782 | 0.022888 | -0.28381 | 0.91553 | 0.68207 | 0.13733 | 0.75989 | 0.21515 | -0.018311 | 0.041199 | -122.406 | 0.23346 | 0.25177 | -0.045777 | 0.27008 | -0.027466 | 0.99335 | 122.6303 | 0.25177 | 0.44861 | 122.937 | 122.8958 | 122.8592 | 122.8775 | -122.9141 | -122.8546 | 122.5525 | 0.4303 | 4.509 | 1.6571
3720.1719 | 122.9507 | -51.9287 | 70.8893 | -0.022431 | 0.00019446 | 0.061171 | 0.068404 | 0.00058737 | 0.0019781 | 0.0032856 | -0.0074462 | 0.0028113 | 0.0021362 | -0.0016492 | -0.0030013 | -0.0055799 | -0.0012561 | -47.4152 | 70.8893 | -51.9974 | 70.6284 | -50.9995 | -51.8051 | -51.2695 | -50.2625 | 70.9076 | -51.9608 | -51.5167 | -51.741 | -52.0432 | -51.7227 | -0.068664 | 0 | -0.26093 | 0.92926 | 0.65918 | 0.1236 | 0.72784 | 0.19226 | -0.032043 | 0.018311 | -122.406 | 0.18768 | 0.20599 | -0.11444 | 0.23804 | -0.082398 | 0.99792 | 122.6257 | 0.21973 | 0.44403 | 122.8867 | 122.8683 | 122.818 | 122.8363 | -122.8867 | -122.85 | 122.5571 | 0.41199 | 4.5136 | 1.6663
3721.1719 | 122.9004 | -51.9424 | 70.8801 | -0.083466 | -0.00087374 | 0.062239 | 0.070541 | -0.001976 | 0.0028327 | 0.0039264 | -0.034912 | 0.00046135 | 0.001709 | 0.0034778 | -0.0010787 | -0.0077161 | 0.00045294 | -47.4472 | 70.8939 | -52.0294 | 70.5963 | -51.0406 | -51.8463 | -51.297 | -50.2945 | 70.9213 | -51.9699 | -51.5579 | -51.7685 | -52.0569 | -51.7639 | -0.086975 | 0.013733 | -0.28381 | 0.90179 | 0.64545 | 0.096131 | 0.73242 | 0.18311 | -0.027466 | 0.041199 | -122.438 | 0.17395 | 0.17853 | -0.11444 | 0.20599 | -0.086975 | 0.98877 | 122.6257 | 0.20142 | 0.41199 | 122.9233 | 122.8912 | 122.8363 | 122.8638 | -122.9095 | -122.85 | 122.5388 | 0.38452 | 4.4952 | 1.6479
3722.1719 | 122.7814 | -52.002 | 70.7886 | -0.098725 | 0.00040806 | 0.062666 | 0.069686 | -0.0015488 | 0.0039007 | 0.0037128 | -0.03186 | 0.0017431 | 0.001068 | 0.0079638 | -0.0015061 | -0.0045117 | -0.00040166 | -47.4564 | 70.8755 | -52.0432 | 70.5734 | -51.1002 | -51.9058 | -51.3382 | -50.3632 | 70.9305 | -52.002 | -51.5808 | -51.796 | -52.0752 | -51.6678 | -0.041199 | 0.086975 | -0.21515 | 0.90179 | 0.66376 | 0.09613 | 0.70496 | 0.13733 | 0 | 0.14191 | -122.3694 | 0.20599 | 0.33417 | -0.073242 | 0.33417 | -0.073242 | 0.94299 | 122.6166 | 0.20599 | 0.42114 | 122.9187 | 122.9324 | 122.8775 | 122.9324 | -122.8317 | -122.7905 | 122.5754 | 0.42114 | 4.5456 | 1.6388
3723.1719 | 123.0148 | -51.9196 | 70.8664 | -0.17502 | -0.0013009 | 0.06288 | 0.067336 | 0.0018692 | 0.0011237 | 0.0022174 | 0.044434 | 3.4148e-05 | 2.8e-08 | 0.00091422 | -0.0017197 | -0.0077161 | -0.0014697 | -47.3969 | 70.8298 | -51.9882 | 70.665 | -50.9171 | -51.7685 | -51.1917 | -50.1801 | 70.8801 | -51.947 | -51.4435 | -51.6541 | -51.9608 | -51.6541 | -0.068664 | -0.036621 | -0.20142 | 1.0025 | 0.72785 | 0.15106 | 0.79651 | 0.21973 | -0.027465 | 0.013733 | -122.3099 | 0.2655 | 0.2655 | -0.041198 | 0.29297 | -0.013733 | 1.0712 | 122.6532 | 0.29297 | 0.50354 | 122.818 | 122.8271 | 122.7493 | 122.7997 | -122.8546 | -122.8134 | 122.5845 | 0.47608 | 4.5227 | 1.7395
3724.1719 | 122.9553 | -51.9196 | 70.8939 | -0.091095 | 0.00040806 | 0.062666 | 0.0699 | 0.0020828 | 0.00069649 | 0.0039264 | -0.022705 | 0.0011023 | 0.0014954 | 0.0019824 | -0.0017197 | -0.0042981 | 0.00088014 | -47.3923 | 70.8893 | -52.0203 | 70.7291 | -50.9262 | -51.7639 | -51.2192 | -50.2121 | 70.9305 | -51.947 | -51.4755 | -51.7319 | -52.0248 | -51.6953 | -0.10071 | -0.004578 | -0.16479 | 0.99335 | 0.70038 | 0.15564 | 0.80109 | 0.25635 | -0.027465 | 0.036621 | -122.3694 | 0.18768 | 0.22431 | -0.10529 | 0.25177 | -0.07782 | 1.0941 | 122.7493 | 0.21515 | 0.4715 | 122.9095 | 122.8775 | 122.8088 | 122.85 | -122.9141 | -122.8409 | 122.6486 | 0.44403 | 4.5273 | 1.7075
3725.1719 | 122.9828 | -51.9012 | 70.8984 | 0.00045798 | 0.0025443 | 0.06053 | 0.071395 | 0.0010148 | 0.0011237 | 0.0096942 | -0.028809 | 0.0017431 | 0.001068 | 0.00048702 | -0.0015061 | -0.0038709 | 0.00066654 | -47.3831 | 70.9076 | -52.0157 | 70.6329 | -51.0818 | -51.7502 | -51.1642 | -50.2029 | 70.9442 | -51.9562 | -51.4801 | -51.7136 | -52.002 | -51.6953 | -0.11444 | 0.009156 | -0.2655 | 0.8194 | 0.737 | 0.15106 | 0.85144 | 0.2655 | -0.054932 | 0.045777 | -122.3785 | 0.18768 | 0.20599 | -0.10071 | 0.26093 | -0.045776 | 0.93384 | 122.6486 | 0.24261 | 0.47607 | 122.9233 | 122.9004 | 122.8088 | 122.8455 | -122.9141 | -122.8546 | 122.5342 | 0.42114 | 4.5181 | 1.6983
3726.1719 | 122.9782 | -51.9104 | 70.9213 | -0.098725 | -0.00044654 | 0.061385 | 0.0699 | 0.003151 | 0.0011237 | 0.0045672 | -0.089844 | -0.00017945 | 0.0029906 | 0.0051868 | -0.0025741 | -0.0077161 | 0.00088014 | -47.3694 | 70.9122 | -52.002 | 70.6558 | -50.9674 | -51.7776 | -51.2466 | -50.1022 | 70.9579 | -51.9424 | -51.4709 | -51.6724 | -51.9836 | -51.6907 | -0.091553 | -0.009156 | -0.2655 | 0.94299 | 0.66376 | 0.13275 | 0.75531 | 0.2243 | -0.032044 | 0.036621 | -122.3923 | 0.23804 | 0.21973 | -0.073243 | 0.25177 | -0.041199 | 1.0345 | 122.6578 | 0.27008 | 0.4715 | 122.9141 | 122.9004 | 122.8226 | 122.8683 | -122.9233 | -122.8638 | 122.5662 | 0.43945 | 4.541 | 1.8082
3727.1719 | 122.9736 | -51.9104 | 70.903 | -0.068207 | -0.00023294 | 0.06053 | 0.068832 | 0.0029374 | 0.0021917 | 0.0056354 | -0.01355 | 0.0025975 | 0.001709 | 0.00070062 | -0.0032151 | -0.0036573 | -0.0031787 | -47.3831 | 70.9305 | -51.9836 | 70.6604 | -50.9583 | -51.7914 | -51.2329 | -50.2258 | 70.9488 | -51.9516 | -51.4984 | -51.7273 | -52.0248 | -51.6953 | -0.073243 | 0.027466 | -0.24262 | 0.95215 | 0.67749 | 0.11902 | 0.75073 | 0.19226 | -0.041199 | 0.045777 | -122.4014 | 0.18311 | 0.21515 | -0.11444 | 0.25635 | -0.073242 | 1.0254 | 122.644 | 0.2243 | 0.45319 | 122.9141 | 122.9004 | 122.8409 | 122.8592 | -122.8867 | -122.8546 | 122.5708 | 0.41199 | 4.5273 | 1.6846
3728.1719 | 123.0377 | -51.8784 | 70.8664 | -0.11398 | 0.00083526 | 0.063094 | 0.06755 | -0.0026168 | 0.0028327 | 0.00093559 | 0.02002 | 0.00067495 | 0.0021362 | 0.0013416 | -0.0027877 | -0.0049389 | 0.0032299 | -47.3923 | 70.8939 | -51.9928 | 70.6696 | -50.9537 | -51.7548 | -51.1963 | -50.2075 | 70.8984 | -51.9424 | -51.4206 | -51.6403 | -51.9379 | -51.6037 | -0.11444 | 0.027466 | -0.19684 | 0.92468 | 0.68207 | 0.1236 | 0.79651 | 0.23804 | -0.064087 | 0.032043 | -122.287 | 0.23804 | 0.27466 | -0.059509 | 0.33875 | 0.004578 | 1.0391 | 122.6624 | 0.30212 | 0.52185 | 122.8867 | 122.8409 | 122.7722 | 122.7768 | -122.8592 | -122.8088 | 122.5479 | 0.45776 | 4.4861 | 1.6708
3729.1719 | 122.9279 | -51.8829 | 70.9076 | -0.022431 | 0.00083526 | 0.064162 | 0.069686 | -0.00090783 | 0.0058233 | 0.0060626 | -0.01355 | 0.00088875 | 0.00085443 | 0.001128 | -0.0019333 | -0.0060071 | 0.0015209 | -47.4106 | 70.9488 | -52.0157 | 70.5826 | -51.0681 | -51.9012 | -51.3107 | -50.2716 | 70.9305 | -51.9974 | -51.5488 | -51.6907 | -52.0432 | -51.7227 | -0.13275 | 0.041199 | -0.32501 | 0.81482 | 0.57221 | -0.01831 | 0.70496 | 0.11444 | -0.11444 | 0.022888 | -122.4564 | 0.19226 | 0.16022 | -0.16022 | 0.27466 | -0.045777 | 0.94757 | 122.5983 | 0.3067 | 0.44861 | 122.9645 | 122.9279 | 122.8317 | 122.8134 | -122.9233 | -122.905 | 122.4655 | 0.33417 | 4.4724 | 1.6113
3730.1719 | 122.905 | -51.9012 | 70.9259 | -0.091095 | 0.0019035 | 0.062239 | 0.069472 | -0.00026703 | 0.0013373 | 0.0067036 | -0.044067 | 0.00046135 | -0.00021357 | 0.0013416 | -0.0032151 | -0.0064343 | 0.0047253 | -47.3969 | 70.9259 | -52.0157 | 70.5917 | -51.059 | -51.8738 | -51.297 | -50.3265 | 70.9488 | -51.9516 | -51.6129 | -51.9516 | -51.741 | -51.4847 | -0.11444 | 0 | -0.33417 | 0.84229 | 0.60425 | 0.027466 | 0.71869 | 0.14191 | -0.050354 | 0.022889 | -122.5388 | -0.050354 | 0.41657 | 0.16022 | 0.46692 | 0.21057 | 0.95673 | 122.6074 | 0 | 0.33875 | 122.9416 | 122.9004 | 122.8271 | 122.85 | -122.9416 | -122.8775 | 122.493 | 0.28839 | 4.5044 | 1.5747
3731.1719 | 122.9645 | -51.9012 | 70.9305 | -0.083466 | -0.00023294 | 0.063521 | 0.069045 | -0.00048063 | 0.0024053 | 0.0043536 | -0.010498 | 0.0040929 | 0.002777 | 0.0028368 | -0.0017197 | -0.0064343 | -0.0029651 | -47.3236 | 70.9671 | -51.9608 | 70.7108 | -50.9079 | -51.7593 | -51.2238 | -50.1892 | 70.99 | -51.9196 | -51.4435 | -51.6815 | -51.9653 | -51.6449 | -0.059509 | 0.036621 | -0.21973 | 0.99335 | 0.67749 | 0.14191 | 0.737 | 0.20142 | -0.018311 | 0.059509 | -122.374 | 0.21973 | 0.25635 | -0.064087 | 0.27466 | -0.045776 | 1.0529 | 122.6715 | 0.23804 | 0.47608 | 122.9279 | 122.9095 | 122.8683 | 122.8912 | -122.8912 | -122.85 | 122.612 | 0.45776 | 4.5776 | 1.712
3732.1719 | 123.0103 | -51.8509 | 70.9396 | -0.045319 | -0.00044654 | 0.061598 | 0.065627 | 0.0029374 | 0.0013373 | 0.0062762 | -0.0043946 | 0.0021703 | 0.00042723 | 0.00070062 | -0.0034287 | -0.0060071 | 0.00045294 | -47.3099 | 70.9488 | -51.9516 | 70.6879 | -50.9766 | -51.8463 | -51.1734 | -50.148 | 70.99 | -51.9012 | -51.4343 | -51.6586 | -51.9562 | -51.6586 | -0.10071 | 0.009156 | -0.25177 | 0.87433 | 0.67749 | 0.004578 | 0.7782 | 0.10529 | -0.050354 | 0.050354 | -122.374 | 0.19226 | 0.19226 | -0.10529 | 0.24262 | -0.054932 | 0.97504 | 122.6395 | 0.24262 | 0.46692 | 122.9004 | 122.8912 | 122.7997 | 122.8409 | -122.8912 | -122.8409 | 122.5388 | 0.41656 | 4.541 | 1.7029
3733.1719 | 123.0331 | -51.8646 | 70.8984 | -0.068207 | 0.0021171 | 0.063094 | 0.06755 | -0.001976 | 0.0028327 | 0.0026446 | 0.023071 | -0.0018885 | 0.00085443 | 0.0071094 | -0.0032151 | -0.0053663 | -0.00018806 | -47.3511 | 70.903 | -51.947 | 70.7199 | -50.9216 | -51.7639 | -51.178 | -50.1389 | 70.9259 | -51.9104 | -51.3931 | -51.6037 | -51.9104 | -51.59 | -0.082397 | 0.004578 | -0.17853 | 0.94299 | 0.68664 | 0.10071 | 0.76904 | 0.1831 | -0.045776 | 0.027466 | -122.2916 | 0.26093 | 0.27466 | -0.045776 | 0.32043 | 0 | 1.0254 | 122.6669 | 0.3067 | 0.51727 | 122.85 | 122.8363 | 122.7676 | 122.7905 | -122.8455 | -122.8088 | 122.5845 | 0.4715 | 4.5136 | 1.7258
3734.1719 | 123.0011 | -51.86 | 70.9579 | -0.12924 | 0.0016899 | 0.060744 | 0.068832 | 0.00016017 | 0.0043281 | 0.0039264 | -0.034912 | 0.0011023 | 0.0014954 | -0.001222 | -0.0030013 | -0.0057935 | -0.00040166 | -47.3145 | 70.9625 | -51.9608 | 70.7108 | -50.9171 | -51.7319 | -51.1963 | -50.1801 | 70.99 | -51.8967 | -51.4801 | -51.6953 | -51.8509 | -51.6174 | -0.10071 | 0.004577 | -0.24719 | 0.94299 | 0.66376 | 0.12817 | 0.76447 | 0.22888 | -0.036621 | 0.032043 | -122.4381 | 0.16479 | 0.24261 | 0.009155 | 0.27923 | 0.045776 | 1.0437 | 122.6715 | 0.20142 | 0.41656 | 122.9233 | 122.8867 | 122.8226 | 122.85 | -122.9187 | -122.8546 | 122.5708 | 0.37994 | 4.5456 | 1.68
3735.1719 | 122.9828 | -51.8784 | 70.9671 | -0.098725 | 0.00040806 | 0.062453 | 0.06755 | 0.0012284 | 0.0021917 | 0.0071308 | -0.0013428 | 0.0011023 | 0.0014954 | 0.00091422 | -0.0015061 | -0.0062207 | 0.0015209 | -47.3099 | 70.9763 | -51.947 | 70.7153 | -50.9171 | -51.7364 | -51.1963 | -50.1846 | 70.9991 | -51.915 | -51.4343 | -51.6815 | -51.947 | -51.6495 | -0.068664 | 0.009155 | -0.25177 | 0.9613 | 0.68207 | 0.14191 | 0.75073 | 0.21057 | -0.036621 | 0.032044 | -122.4014 | 0.19684 | 0.22888 | -0.068664 | 0.2655 | -0.032043 | 1.03 | 122.6624 | 0.23346 | 0.48065 | 122.9233 | 122.9141 | 122.8546 | 122.8775 | -122.9141 | -122.8821 | 122.5937 | 0.44403 | 4.5685 | 1.6937
3736.1719 | 122.9736 | -51.86 | 70.9625 | -0.083466 | 0.0021171 | 0.064375 | 0.067336 | 0.003151 | 0.0017645 | 0.003072 | -0.0074462 | 0.0011023 | -0.00021357 | 0.00091422 | -0.0032151 | -0.0068615 | -0.0044605 | -47.3923 | 70.9625 | -51.9516 | 70.7016 | -50.9354 | -51.7136 | -51.1688 | -50.1572 | 71.0175 | -51.9058 | -51.4343 | -51.6586 | -51.9516 | -51.6357 | -0.091553 | 0 | -0.26093 | 0.92468 | 0.69122 | 0.14648 | 0.78278 | 0.23804 | -0.045777 | 0.054932 | -122.3969 | 0.20142 | 0.2243 | -0.091553 | 0.27008 | -0.045776 | 1.0162 | 122.6532 | 0.24719 | 0.4715 | 122.9141 | 122.9233 | 122.8226 | 122.8775 | -122.9141 | -122.8683 | 122.5616 | 0.42572 | 4.4678 | 1.7029
3737.1719 | 122.9416 | -51.8692 | 70.9534 | -0.091095 | -0.00023294 | 0.062453 | 0.070327 | 0.0010148 | 0.0030463 | 0.0064898 | -0.019653 | 0.0028113 | 0.0023498 | 0.0019824 | -0.0036423 | -0.0040845 | 0.00066654 | -47.3053 | 70.9579 | -51.9379 | 70.6696 | -50.9354 | -51.7639 | -51.1963 | -50.2029 | 70.9946 | -51.9104 | -51.4572 | -51.6769 | -51.9882 | -51.6541 | -0.068664 | 0.004578 | -0.28381 | 0.93384 | 0.67291 | 0.10529 | 0.74158 | 0.17395 | -0.041198 | 0.041199 | -122.4106 | 0.19226 | 0.21515 | -0.11902 | 0.25635 | -0.07782 | 1.0025 | 122.6074 | 0.23346 | 0.45319 | 122.8958 | 122.905 | 122.8271 | 122.8638 | -122.8912 | -122.8638 | 122.5388 | 0.41199 | 4.5639 | 1.6663
3738.1719 | 122.905 | -51.8875 | 70.9625 | -0.075836 | 0.0027579 | 0.062025 | 0.069472 | 0.0018692 | 0.0049689 | 0.001363 | 0.029175 | 0.00046135 | 0.002777 | -0.0014356 | -0.0012925 | -0.0038709 | 0.0019483 | -47.3557 | 70.9579 | -51.9699 | 70.7611 | -50.7248 | -51.8005 | -51.2833 | -50.2716 | 71.0312 | -51.8921 | -51.4664 | -51.7227 | -52.0111 | -51.6861 | -0.082398 | -0.004577 | -0.20142 | 1.1627 | 0.60425 | 0.086975 | 0.68665 | 0.16937 | -0.004578 | 0.068665 | -122.4289 | 0.16479 | 0.20142 | -0.1236 | 0.20599 | -0.11902 | 1.2451 | 122.731 | 0.16937 | 0.42572 | 122.9279 | 122.9233 | 122.8455 | 122.9187 | -122.9324 | -122.8546 | 122.6486 | 0.42114 | 4.5319 | 1.6159
3739.1719 | 122.9645 | -51.8555 | 70.9946 | -0.022431 | -0.00044654 | 0.062025 | 0.070754 | 0.0010148 | 0.0015509 | 0.005849 | 0.010864 | 0.0015295 | 0.00021363 | 0.001128 | -0.00043791 | -0.0075025 | -0.00082886 | -47.2824 | 71.0403 | -51.9333 | 70.7108 | -50.9125 | -51.7273 | -51.1688 | -50.1709 | 71.0129 | -51.8875 | -51.3977 | -51.622 | -51.915 | -51.5991 | -0.07782 | 0.045776 | -0.28381 | 0.94299 | 0.68665 | 0.12817 | 0.76447 | 0.20599 | -0.032043 | 0.01831 | -122.3923 | 0.23346 | 0.25635 | -0.059509 | 0.28839 | -0.027466 | 1.0208 | 122.644 | 0.2655 | 0.48981 | 122.9736 | 122.9004 | 122.8958 | 122.8683 | -122.9279 | -122.8821 | 122.5662 | 0.45776 | 4.5731 | 1.6846
3740.1719 | 123.0011 | -51.8372 | 70.9442 | -0.045319 | 0.0027579 | 0.062025 | 0.070327 | -0.0017624 | 0.0015509 | 0.0011494 | 0.0047608 | 0.0015295 | -0.00021357 | 0.0041186 | -0.0021469 | -0.0036573 | 0.0034435 | -47.2504 | 71.0083 | -51.9333 | 70.7108 | -50.8987 | -51.7044 | -51.1688 | -50.1205 | 71.0266 | -51.8463 | -51.4114 | -51.6174 | -51.9104 | -51.6129 | -0.096131 | 0.064087 | -0.23346 | 0.93841 | 0.66833 | 0.13275 | 0.76447 | 0.22888 | -0.009155 | 0.082397 | -122.3557 | 0.21973 | 0.2243 | -0.073242 | 0.23346 | -0.064087 | 1.0345 | 122.644 | 0.22888 | 0.43488 | 122.9416 | 122.8729 | 122.8455 | 122.8638 | -122.8775 | -122.7905 | 122.5479 | 0.42572 | 4.5868 | 1.7166
3741.1719 | 122.9782 | -51.8509 | 70.9671 | -0.11398 | 0.00040806 | 0.060316 | 0.070327 | -0.00048063 | 0.0043281 | 0.0011494 | 0.0047608 | 0.0032385 | 0.0021362 | 0.0019824 | -0.0021469 | -0.0070753 | 2.554e-05 | -47.3145 | 70.9671 | -51.9196 | 70.7428 | -50.8896 | -51.7364 | -51.1459 | -50.1343 | 71.0449 | -51.8646 | -51.4023 | -51.6403 | -51.9104 | -51.6129 | -0.068665 | 0 | -0.2243 | 0.9613 | 0.70496 | 0.11444 | 0.77362 | 0.18311 | -0.013733 | 0.07782 | -122.3694 | 0.21057 | 0.23804 | -0.059509 | 0.25177 | -0.045776 | 1.03 | 122.6624 | 0.2243 | 0.46234 | 122.8867 | 122.9095 | 122.818 | 122.8958 | -122.8867 | -122.8317 | 122.5937 | 0.44861 | 4.5364 | 1.7166
3742.1719 | 122.9874 | -51.8326 | 71.0037 | -0.045319 | 0.00019446 | 0.059889 | 0.069472 | 0.0010148 | 0.00069649 | 0.00029479 | -0.01355 | 0.0013159 | 0.0023498 | -0.0067762 | -0.0010787 | -0.0045117 | -0.0016833 | -47.2366 | 71.0129 | -51.9104 | 70.7382 | -50.8987 | -51.709 | -51.1414 | -50.1434 | 71.0266 | -51.8829 | -51.4069 | -51.622 | -51.9104 | -51.5991 | -0.077819 | 0.009155 | -0.2655 | 0.93384 | 0.69122 | 0.1236 | 0.76904 | 0.20142 | -0.050354 | 0.022888 | -122.4106 | 0.21057 | 0.23346 | -0.077819 | 0.28381 | -0.027465 | 1.0117 | 122.6486 | 0.26093 | 0.47608 | 122.9233 | 122.9095 | 122.8455 | 122.8592 | -122.9141 | -122.8867 | 122.5708 | 0.42572 | 4.5959 | 1.6891
3743.1719 | 122.9507 | -51.8463 | 70.9671 | -0.060578 | 0.00040806 | 0.061171 | 0.068404 | 0.00080117 | 0.0013373 | 0.00414 | 0.0047608 | 0.00088875 | 0.001068 | 0.0028368 | -0.0038559 | -0.0042981 | 0.0032299 | -47.3145 | 70.9579 | -51.9379 | 70.6924 | -50.9811 | -51.7868 | -51.2054 | -50.2075 | 70.9808 | -51.8875 | -51.4114 | -51.6495 | -51.9516 | -51.6129 | -0.091553 | -0.009155 | -0.27466 | 0.86517 | 0.64087 | 0.059509 | 0.73242 | 0.15106 | -0.041199 | 0.013733 | -122.3785 | 0.19684 | 0.23346 | -0.10529 | 0.27466 | -0.064087 | 0.95673 | 122.6303 | 0.23804 | 0.47607 | 122.8958 | 122.8683 | 122.8043 | 122.8271 | -122.905 | -122.8546 | 122.5388 | 0.43488 | 4.5319 | 1.6388
3744.1719 | 122.9416 | -51.8326 | 70.9625 | -0.12924 | -1.9142e-05 | 0.061385 | 0.070968 | -0.0011214 | 0.0015509 | 0.0049946 | -0.025757 | 0.0023839 | 0.0025634 | -0.00079478 | -0.0027877 | -0.0036573 | -0.0016833 | -47.2412 | 70.9946 | -51.915 | 70.7245 | -50.8987 | -51.7227 | -51.1688 | -50.1297 | 71.0312 | -51.8372 | -51.4114 | -51.6357 | -51.9333 | -51.6037 | -0.082397 | 0.032044 | -0.23804 | 0.93384 | 0.66376 | 0.10986 | 0.74615 | 0.19226 | -0.004577 | 0.068665 | -122.374 | 0.19684 | 0.22888 | -0.10071 | 0.23346 | -0.096131 | 1.0162 | 122.6395 | 0.20142 | 0.42572 | 122.9095 | 122.8683 | 122.8271 | 122.8638 | -122.8775 | -122.7997 | 122.5571 | 0.42114 | 4.5914 | 1.7029
3745.1719 | 122.9599 | -51.8326 | 70.9808 | -0.21317 | 0.00040806 | 0.060744 | 0.067123 | 0.0018692 | 0.0039007 | 0.002431 | 0.001709 | 0.0011023 | 0.001068 | -0.00036738 | -0.0019333 | -0.0072889 | -0.0040333 | -47.2 | 71.0037 | -51.9012 | 70.7474 | -50.8575 | -51.6907 | -51.1414 | -50.1205 | 71.022 | -51.8875 | -51.3931 | -51.6312 | -51.915 | -51.5991 | -0.068664 | 0.022888 | -0.23346 | 0.97504 | 0.69122 | 0.14191 | 0.75989 | 0.21057 | -0.054931 | 0.041199 | -122.374 | 0.20142 | 0.23346 | -0.082397 | 0.28839 | -0.027466 | 1.0437 | 122.6486 | 0.25635 | 0.49439 | 122.905 | 122.9095 | 122.8363 | 122.8546 | -122.8821 | -122.8683 | 122.58 | 0.43945 | 4.6326 | 1.712
3746.1719 | 122.9233 | -51.8463 | 70.9808 | -0.037689 | -1.9142e-05 | 0.060957 | 0.069259 | 0.005928 | 0.0036871 | 0.0062762 | -0.044067 | 0.0015295 | 0.0032044 | 0.00070062 | -0.0053513 | -0.0045117 | 0.0010937 | -47.2549 | 70.9946 | -51.915 | 70.7062 | -50.9033 | -51.7548 | -51.178 | -50.1663 | 71.022 | -51.8509 | -51.4206 | -51.6541 | -51.9562 | -51.6357 | -0.068665 | 0.013733 | -0.27466 | 0.94299 | 0.66833 | 0.091552 | 0.737 | 0.16022 | -0.004578 | 0.041199 | -122.4014 | 0.19226 | 0.21057 | -0.10986 | 0.21515 | -0.10529 | 1.0117 | 122.6212 | 0.19684 | 0.4303 | 122.9095 | 122.8729 | 122.8409 | 122.8683 | -122.8958 | -122.8317 | 122.5525 | 0.42572 | 4.5914 | 1.68
3747.1719 | 122.9645 | -51.8326 | 70.9763 | -0.098725 | 0.00040806 | 0.064162 | 0.0699 | 0.0016556 | 0.0032599 | 0.00414 | -0.025757 | 0.0015295 | 0.0023498 | 0.001128 | -0.0017197 | -0.0045117 | 0.00023934 | -47.2183 | 70.9991 | -51.9058 | 70.7245 | -50.8713 | -51.7227 | -51.1642 | -50.1389 | 71.0587 | -51.8784 | -51.4206 | -51.6357 | -51.9379 | -51.6129 | -0.073242 | 0.022889 | -0.25177 | 0.9613 | 0.66833 | 0.10986 | 0.74158 | 0.18311 | -0.045776 | 0.082398 | -122.3969 | 0.19684 | 0.21973 | -0.10529 | 0.2655 | -0.059509 | 1.0345 | 122.6303 | 0.24262 | 0.45776 | 122.905 | 122.937 | 122.8317 | 122.8912 | -122.8821 | -122.8546 | 122.5571 | 0.41199 | 4.6143 | 1.6937
3748.1875 | 122.9416 | -51.8463 | 71.0129 | -0.075836 | 0.00083526 | 0.062453 | 0.068404 | 0.0012284 | 0.0047553 | 0.00414 | 0.0078126 | 0.0013159 | 0.0025634 | 0.0024096 | -0.0047103 | -0.0051527 | 0.0051525 | -47.2824 | 70.99 | -51.9379 | 70.5139 | -50.7065 | -51.5488 | -51.1917 | -50.1572 | 71.0403 | -51.86 | -51.4389 | -51.6678 | -51.9653 | -51.6357 | -0.091553 | -0.022888 | -0.49896 | 1.1398 | 0.6546 | 0.29755 | 0.74616 | 0.3891 | -0.013733 | 0.027466 | -122.4518 | 0.17853 | 0.21057 | -0.11902 | 0.2243 | -0.10529 | 1.2314 | 122.4518 | 0.19226 | 0.42114 | 122.9279 | 122.9004 | 122.8363 | 122.8867 | -122.9507 | -122.8729 | 122.3602 | 0.40741 | 4.5639 | 1.6891
3749.1719 | 122.9828 | -51.8005 | 71.022 | -0.037689 | 0.0021171 | 0.062025 | 0.069045 | -0.00026703 | 0.00026909 | 0.0028582 | 0.0047608 | 0.00067495 | 0.00042723 | -0.00058098 | -0.0040695 | -0.0051527 | -0.0014697 | -47.1954 | 71.0312 | -51.9058 | 70.7611 | -50.8392 | -51.6678 | -51.1368 | -50.1068 | 71.0449 | -51.8555 | -51.3748 | -51.5808 | -51.8829 | -51.5625 | -0.10529 | 0.009155 | -0.26093 | 0.9613 | 0.66376 | 0.13275 | 0.76904 | 0.23804 | -0.054932 | 0.022888 | -122.3969 | 0.21973 | 0.23804 | -0.082398 | 0.29297 | -0.027466 | 1.0666 | 122.6669 | 0.27466 | 0.48065 | 122.937 | 122.9004 | 122.8317 | 122.8455 | -122.9279 | -122.8775 | 122.5616 | 0.42572 | 4.6051 | 1.6937
3750.1719 | 122.9645 | -51.796 | 70.99 | -0.03006 | 0.0025443 | 0.060957 | 0.068832 | -0.00026703 | 0.0013373 | 0.005849 | 0.032227 | 0.00024775 | 0.00085443 | -0.00036738 | -0.0038559 | -0.0062207 | 0.00066654 | -47.2046 | 71.0175 | -51.8921 | 70.7657 | -50.7935 | -51.8509 | -51.1505 | -50.0839 | 71.0724 | -51.828 | -51.3611 | -51.5991 | -51.8692 | -51.59 | -0.096131 | 0.027466 | -0.2243 | 1.0025 | 0.64545 | -0.054932 | 0.74158 | 0.041199 | -0.032044 | 0.082398 | -122.3511 | 0.19684 | 0.20599 | -0.073243 | 0.23804 | -0.041199 | 1.0986 | 122.6578 | 0.22888 | 0.46692 | 122.9095 | 122.9004 | 122.8134 | 122.8683 | -122.8821 | -122.818 | 122.5616 | 0.43488 | 4.5914 | 1.712
3751.1719 | 123.0011 | -51.7776 | 71.0129 | -0.060578 | 0.0012625 | 0.059889 | 0.069472 | 0.00016017 | 0.00026909 | 0.0039264 | 0.013916 | 0.0019567 | 0.002777 | 0.005614 | -0.0025741 | -0.0045117 | -0.0021107 | -47.1909 | 71.0541 | -51.8921 | 70.7474 | -50.8713 | -51.6586 | -51.123 | -50.116 | 71.077 | -51.8372 | -51.3657 | -51.5762 | -51.8692 | -51.5625 | -0.11444 | 0.041199 | -0.2655 | 0.90637 | 0.6546 | 0.11902 | 0.76904 | 0.23346 | -0.059509 | 0.064087 | -122.3785 | 0.20142 | 0.21515 | -0.091553 | 0.27466 | -0.032044 | 1.0208 | 122.6395 | 0.26093 | 0.4715 | 122.9462 | 122.9141 | 122.8317 | 122.8546 | -122.905 | -122.85 | 122.525 | 0.41199 | 4.5868 | 1.6617
3752.1719 | 122.9507 | -51.796 | 71.0312 | -0.060578 | -0.00023294 | 0.061171 | 0.068618 | -0.0013352 | 0.0024053 | 0.0028582 | 0.010864 | 0.00088875 | 0.00021363 | 0.0034778 | -0.0017197 | -0.0051527 | -0.00082886 | -47.2458 | 71.0541 | -51.8417 | 70.7703 | -50.9125 | -51.7227 | -51.1276 | -50.1389 | 71.0815 | -51.8555 | -51.4023 | -51.6129 | -51.8875 | -51.5945 | -0.045777 | 0.022888 | -0.26093 | 0.88348 | 0.66833 | 0.073242 | 0.71411 | 0.11902 | -0.05951 | 0.050354 | -122.4335 | 0.18311 | 0.20142 | -0.091553 | 0.26093 | -0.032043 | 0.92926 | 122.612 | 0.24262 | 0.45319 | 122.8958 | 122.937 | 122.85 | 122.8775 | -122.8729 | -122.8867 | 122.5662 | 0.39368 | 4.5502 | 1.6571
3753.1719 | 122.9141 | -51.8188 | 71.0129 | -0.098725 | 0.0021171 | 0.062666 | 0.070327 | -0.0021896 | 0.0039007 | 0.0049946 | -0.037964 | 0.0017431 | 0.0036316 | 0.00091422 | -0.0010787 | -0.0053663 | 2.554e-05 | -47.2458 | 71.022 | -51.9287 | 70.6879 | -50.9628 | -51.7731 | -51.2009 | -50.2213 | 71.077 | -51.8829 | -51.4343 | -51.7044 | -51.9882 | -51.6495 | -0.10986 | 0.009156 | -0.32501 | 0.85602 | 0.61798 | 0.045777 | 0.72784 | 0.15564 | -0.064087 | 0.064087 | -122.4472 | 0.11444 | 0.16937 | -0.16937 | 0.23346 | -0.10528 | 0.96588 | 122.6166 | 0.17853 | 0.44861 | 122.9507 | 122.9599 | 122.8409 | 122.8958 | -122.9416 | -122.8958 | 122.5067 | 0.38452 | 4.5731 | 1.5976
3754.1719 | 122.9736 | -51.828 | 71.0129 | -0.068207 | -1.9142e-05 | 0.061171 | 0.067336 | -0.00048063 | 0.00026909 | 0.0020038 | 0.029175 | 0.0021703 | 0.0029906 | -0.002931 | -0.0036423 | -0.0066479 | 0.0036571 | -47.2229 | 71.0175 | -51.915 | 70.7199 | -50.8759 | -51.6953 | -51.1551 | -50.1251 | 71.0312 | -51.8463 | -51.3931 | -51.59 | -51.8921 | -51.5854 | -0.086975 | 0.004578 | -0.29297 | 0.95215 | 0.67291 | 0.13275 | 0.75989 | 0.21973 | -0.01831 | 0.018311 | -122.406 | 0.23804 | 0.24262 | -0.064087 | 0.26093 | -0.045777 | 1.0391 | 122.6349 | 0.25635 | 0.45319 | 122.9324 | 122.8775 | 122.8455 | 122.8592 | -122.9279 | -122.8592 | 122.5479 | 0.43488 | 4.6051 | 1.7029
3755.1719 | 122.9416 | -51.8463 | 71.0495 | -0.11398 | -0.0032235 | 0.061171 | 0.069259 | -0.0034714 | 0.0011237 | 0.0017902 | 0.029175 | 0.00024775 | 0.0036316 | -0.0033582 | -0.00065151 | -0.0053663 | 0.0013073 | -47.2366 | 70.99 | -51.9196 | 70.7245 | -50.9125 | -51.709 | -51.1597 | -50.1846 | 71.0403 | -51.8692 | -51.416 | -51.6266 | -51.9241 | -51.6312 | -0.073243 | -0.05951 | -0.32501 | 0.93384 | 0.68664 | 0.13733 | 0.75989 | 0.21057 | -0.022889 | -0.009156 | -122.4655 | 0.21973 | 0.21515 | -0.07782 | 0.23804 | -0.054931 | 1.0071 | 122.644 | 0.24262 | 0.45319 | 122.9095 | 122.9095 | 122.8363 | 122.8867 | -122.9691 | -122.9187 | 122.5708 | 0.4303 | 4.6097 | 1.6617
3756.1719 | 122.9691 | -51.828 | 71.0175 | -0.03006 | 0.00040806 | 0.061171 | 0.069686 | -0.0011214 | 0.00048269 | 0.003072 | 0.013916 | 0.00067495 | 0.0012818 | -0.001222 | -0.0038559 | -0.0028027 | 0.00088014 | -47.2412 | 71.0083 | -51.9241 | 70.7199 | -50.9079 | -51.6998 | -51.1597 | -50.148 | 71.0587 | -51.8555 | -51.4069 | -51.6083 | -51.8875 | -51.6037 | -0.09613 | -0.009155 | -0.29755 | 0.9201 | 0.66833 | 0.12817 | 0.76446 | 0.2243 | -0.027466 | 0.041199 | -122.4243 | 0.21973 | 0.2243 | -0.059509 | 0.25177 | -0.032043 | 1.0162 | 122.644 | 0.24719 | 0.44861 | 122.9324 | 122.9141 | 122.8363 | 122.8867 | -122.9416 | -122.8729 | 122.5479 | 0.42114 | 4.5868 | 1.68
3757.1719 | 122.9645 | -51.8188 | 71.0129 | -0.10635 | -0.00044654 | 0.062453 | 0.069472 | -0.0015488 | 0.0015509 | 0.0043536 | 0.016968 | 0.00046135 | 0.00042723 | -0.0027174 | -0.0015061 | -0.0075025 | 0.0025891 | -47.2321 | 71.0449 | -51.9196 | 70.7291 | -50.9216 | -51.6907 | -51.1551 | -50.1617 | 71.0403 | -51.8555 | -51.3886 | -51.5991 | -51.8967 | -51.6037 | -0.10071 | 0.032044 | -0.28381 | 0.89722 | 0.66376 | 0.12817 | 0.76447 | 0.22888 | -0.036621 | 0.027466 | -122.4014 | 0.21973 | 0.21515 | -0.077819 | 0.25177 | -0.041198 | 0.99793 | 122.6486 | 0.25635 | 0.46692 | 122.9645 | 122.8958 | 122.8638 | 122.8592 | -122.9324 | -122.8683 | 122.5479 | 0.4303 | 4.5868 | 1.6571
3758.1719 | 122.905 | -51.8463 | 71.0083 | -0.098725 | -0.0019417 | 0.062453 | 0.068618 | 0.0033646 | 0.0015509 | 0.007558 | -0.028809 | 0.00088875 | 0.0023498 | 0.0024096 | -0.0027877 | -0.0051527 | -0.0014697 | -47.2458 | 70.9946 | -51.915 | 70.6741 | -50.9537 | -51.796 | -51.2283 | -50.2167 | 71.0175 | -51.8921 | -51.4526 | -51.7044 | -51.9974 | -51.6541 | -0.068665 | -0.013733 | -0.33417 | 0.89264 | 0.61798 | 0.050354 | 0.68664 | 0.11902 | -0.045777 | 0.009155 | -122.4609 | 0.14191 | 0.19226 | -0.15106 | 0.23804 | -0.10528 | 0.9613 | 122.5891 | 0.18768 | 0.43945 | 122.9095 | 122.9095 | 122.8409 | 122.8638 | -122.9233 | -122.9004 | 122.5204 | 0.39368 | 4.6005 | 1.6296
3759.1719 | 122.8455 | -51.8097 | 71.022 | -0.068207 | 0.00083526 | 0.061598 | 0.066909 | -0.0021896 | -0.00015811 | 0.0028582 | 0.047485 | 0.0011023 | 0.0014954 | -0.002931 | -0.0010787 | -0.0081433 | -0.00018806 | -47.2092 | 71.0175 | -51.8829 | 70.7382 | -50.8759 | -51.6861 | -51.1368 | -50.1572 | 71.0678 | -51.8326 | -51.503 | -51.4526 | -51.7227 | -51.59 | -0.073243 | -0.004578 | -0.28381 | 0.93384 | 0.67291 | 0.1236 | 0.74616 | 0.19684 | -0.022889 | 0.045776 | -122.525 | 0.35705 | 0.21973 | 0.086975 | 0.24262 | 0.10986 | 1.0071 | 122.6212 | 0.37994 | 0.32959 | 122.9004 | 122.9004 | 122.8271 | 122.8775 | -122.905 | -122.8546 | 122.5479 | 0.3067 | 4.6005 | 1.6525
3760.1719 | 122.9416 | -51.8051 | 71.0449 | -0.11398 | 0.0010489 | 0.060957 | 0.068832 | -0.0032578 | 0.00026909 | 0.0045672 | 0.056641 | 0.00088875 | 0.00042723 | -0.0065626 | -0.0012925 | -0.0068615 | -0.0027515 | -47.2046 | 71.022 | -51.8829 | 70.7657 | -50.8484 | -51.6678 | -51.1414 | -50.1205 | 71.0724 | -51.8326 | -51.4114 | -51.5945 | -51.8784 | -51.5945 | -0.07782 | -0.022888 | -0.27924 | 0.95673 | 0.66376 | 0.13733 | 0.74158 | 0.21515 | -0.027466 | 0.027466 | -122.4564 | 0.21057 | 0.21057 | -0.073242 | 0.23804 | -0.045776 | 1.0345 | 122.6486 | 0.23804 | 0.42114 | 122.905 | 122.905 | 122.8271 | 122.8775 | -122.9279 | -122.8775 | 122.5708 | 0.39368 | 4.6005 | 1.6846
3761.1719 | 122.9736 | -51.8005 | 71.0358 | -0.068207 | 0.00062166 | 0.060957 | 0.068832 | 0.00080117 | 0.0015509 | 0.005849 | -0.0013428 | 0.00046135 | 0.0025634 | 0.003905 | -0.0012925 | -0.0060071 | -0.0057423 | -47.1909 | 71.0678 | -51.9058 | 70.7245 | -50.8942 | -51.7044 | -51.1459 | -50.1434 | 71.0495 | -51.8417 | -51.3748 | -51.5717 | -51.8784 | -51.5762 | -0.10529 | 0.032043 | -0.31128 | 0.90637 | 0.6546 | 0.09613 | 0.75989 | 0.20142 | -0.041199 | 0.013733 | -122.4106 | 0.22888 | 0.2243 | -0.07782 | 0.2655 | -0.036621 | 1.0117 | 122.6303 | 0.27008 | 0.46692 | 122.9736 | 122.8912 | 122.8683 | 122.85 | -122.9416 | -122.8775 | 122.525 | 0.42572 | 4.6097 | 1.6571
3762.1719 | 122.9782 | -51.796 | 71.0266 | -0.068207 | -0.00066014 | 0.06053 | 0.069259 | 0.0027238 | 0.0019781 | 0.0077716 | -0.016602 | 0.0017431 | 0.0025634 | 0.0081774 | -0.0023605 | -0.0049389 | 0.00088014 | -47.1588 | 71.0312 | -51.8967 | 70.7794 | -50.8484 | -51.6678 | -51.1185 | -50.0748 | 71.0678 | -51.8097 | -51.3519 | -51.5762 | -51.8692 | -51.5854 | -0.10071 | 0.004578 | -0.24719 | 0.94757 | 0.67749 | 0.12817 | 0.7782 | 0.22888 | -0.013733 | 0.041199 | -122.3785 | 0.21973 | 0.21057 | -0.073243 | 0.2243 | -0.05951 | 1.0483 | 122.6761 | 0.23346 | 0.45776 | 122.9279 | 122.8775 | 122.8271 | 122.8638 | -122.9233 | -122.8363 | 122.5754 | 0.44403 | 4.6371 | 1.7212
3763.1719 | 122.9462 | -51.7914 | 71.022 | -0.068207 | 0.00062166 | 0.063734 | 0.069259 | -0.0017624 | 0.0011237 | 0.0045672 | -0.037964 | 0.0017431 | 0.0012818 | 0.0015552 | -0.0017197 | -0.0057935 | 0.0013073 | -47.1771 | 71.0312 | -51.8829 | 70.7611 | -50.8713 | -51.6998 | -51.1597 | -50.1205 | 71.0495 | -51.8188 | -51.4023 | -51.6312 | -51.9424 | -51.6037 | -0.091553 | 0.009155 | -0.26093 | 0.9201 | 0.63171 | 0.091553 | 0.72327 | 0.18311 | -0.027466 | 0.027466 | -122.4243 | 0.16022 | 0.18768 | -0.15106 | 0.21515 | -0.1236 | 1.0117 | 122.644 | 0.18768 | 0.41657 | 122.9141 | 122.8683 | 122.8226 | 122.8409 | -122.905 | -122.8409 | 122.5525 | 0.3891 | 4.6143 | 1.6708
3764.1719 | 122.9691 | -51.7868 | 71.0678 | -0.060578 | -0.0013009 | 0.061171 | 0.070541 | 0.0016556 | -0.0010125 | 0.0032856 | 0.032227 | 0.0021703 | -0.00064077 | -0.00229 | -0.0025741 | -0.0075025 | -0.0014697 | -47.1817 | 71.0632 | -51.8784 | 70.7382 | -50.885 | -51.6907 | -51.1276 | -50.1297 | 71.0678 | -51.828 | -51.384 | -51.6083 | -51.8784 | -51.5808 | -0.091553 | -0.004578 | -0.32959 | 0.90179 | 0.65918 | 0.09613 | 0.75073 | 0.18768 | -0.041199 | 0 | -122.4518 | 0.17853 | 0.20599 | -0.091553 | 0.24719 | -0.050354 | 0.99335 | 122.6166 | 0.21973 | 0.44403 | 122.9416 | 122.8958 | 122.85 | 122.8546 | -122.9462 | -122.8958 | 122.525 | 0.40283 | 4.6051 | 1.6571
3765.1719 | 122.937 | -51.8143 | 70.99 | -0.083466 | 0.00040806 | 0.062453 | 0.069472 | 0.00058737 | 0.0011237 | 0.0043536 | -0.019653 | -0.0025293 | 0.0036316 | 0.00048702 | -0.0032151 | -0.0047253 | -0.0025379 | -47.2229 | 71.0175 | -51.9012 | 70.7153 | -50.9171 | -51.7548 | -51.1871 | -50.1572 | 71.0495 | -51.8326 | -51.3931 | -51.622 | -51.9058 | -51.5854 | -0.086975 | 0.027466 | -0.27466 | 0.89722 | 0.62714 | 0.059509 | 0.71411 | 0.14648 | -0.018311 | 0.05951 | -122.3831 | 0.19226 | 0.22888 | -0.091553 | 0.24719 | -0.073242 | 0.98419 | 122.6166 | 0.21057 | 0.43945 | 122.9187 | 122.8821 | 122.8317 | 122.8638 | -122.8912 | -122.8226 | 122.5296 | 0.42114 | 4.5914 | 1.6571
3766.1719 | 122.9553 | -51.7776 | 71.0678 | -0.014801 | 0.00040806 | 0.062453 | 0.068618 | -0.0015488 | 0.0019781 | 0.0039264 | 0.026123 | 0.00088875 | 0.0014954 | 0.0017688 | -0.0025741 | -0.0060071 | 0.00045294 | -47.1909 | 71.077 | -51.8234 | 70.7565 | -50.9079 | -51.709 | -51.1322 | -50.1022 | 71.109 | -51.8051 | -51.3748 | -51.5762 | -51.8875 | -51.5717 | -0.045776 | 0.009155 | -0.31128 | 0.86975 | 0.64545 | 0.068665 | 0.69122 | 0.11444 | -0.027466 | 0.041199 | -122.4426 | 0.20142 | 0.20599 | -0.10986 | 0.23346 | -0.082397 | 0.91553 | 122.58 | 0.22888 | 0.4303 | 122.9004 | 122.9141 | 122.8546 | 122.8867 | -122.8912 | -122.8729 | 122.5342 | 0.40283 | 4.5868 | 1.6754
3767.1719 | 122.937 | -51.7868 | 71.0724 | -0.022431 | 0.00019446 | 0.063307 | 0.067123 | 0.0020828 | 0.0030463 | 0.0056354 | 0.03833 | -0.00060665 | 0.0019226 | 0.0024096 | -0.0025741 | -0.0060071 | 0.00045294 | -47.1176 | 71.0541 | -51.8509 | 70.7794 | -50.8255 | -51.6632 | -51.1047 | -50.0702 | 71.0861 | -51.8143 | -51.3657 | -51.5625 | -51.8692 | -51.5854 | -0.064087 | -0.018311 | -0.29297 | 0.9613 | 0.68207 | 0.1236 | 0.74615 | 0.18768 | -0.027466 | 0.013733 | -122.4381 | 0.2243 | 0.20142 | -0.082398 | 0.22888 | -0.054932 | 1.0254 | 122.6303 | 0.25177 | 0.44861 | 122.905 | 122.9004 | 122.8409 | 122.8729 | -122.9233 | -122.8867 | 122.5662 | 0.42114 | 4.6692 | 1.7166
3768.1719 | 122.9599 | -51.7776 | 71.0541 | -0.083466 | -0.0027963 | 0.061598 | 0.069045 | -0.001976 | 0.0019781 | 0.0020038 | -0.01355 | 0.00046135 | 0.0032044 | 0.0054004 | -0.0049241 | -0.0055799 | 0.00023934 | -47.1039 | 71.0403 | -51.8692 | 70.7932 | -50.8163 | -51.6266 | -51.091 | -50.0473 | 71.077 | -51.8097 | -51.329 | -51.5625 | -51.8417 | -51.5396 | -0.091553 | -0.013733 | -0.26093 | 0.9613 | 0.68665 | 0.15106 | 0.7782 | 0.24262 | -0.032043 | 0.022888 | -122.3831 | 0.21515 | 0.23804 | -0.064087 | 0.27008 | -0.032044 | 1.0529 | 122.6624 | 0.24719 | 0.48065 | 122.9095 | 122.8867 | 122.818 | 122.8546 | -122.9233 | -122.8638 | 122.5708 | 0.44861 | 4.6738 | 1.7303
3769.1719 | 122.9233 | -51.7731 | 71.0815 | -0.10635 | -0.00087374 | 0.060957 | 0.067123 | 0.0010148 | 0.0019781 | 0.0069172 | 0.026123 | 0.00046135 | 0.003418 | -0.005708 | -0.0038559 | -0.0055799 | 0.00066654 | -47.1542 | 71.0678 | -51.828 | 70.7565 | -50.853 | -51.6724 | -51.1047 | -50.0153 | 71.1594 | -51.7639 | -51.384 | -51.5625 | -51.8738 | -51.5671 | -0.054932 | -0.013733 | -0.32501 | 0.9201 | 0.66833 | 0.10071 | 0.72327 | 0.15564 | 0.009155 | 0.07782 | -122.4655 | 0.21057 | 0.20599 | -0.10071 | 0.19684 | -0.10986 | 0.97504 | 122.5845 | 0.20142 | 0.37994 | 122.8958 | 122.9233 | 122.8409 | 122.9324 | -122.9095 | -122.8455 | 122.5296 | 0.3891 | 4.6188 | 1.7578
3770.1719 | 123.0331 | -51.7364 | 71.0266 | -0.12161 | 0.0012625 | 0.063307 | 0.067763 | 0.0018692 | 0.0021917 | 0.0022174 | 0.023071 | 0.0011023 | 0.0019226 | -0.0054944 | -0.0030013 | -0.0072889 | 0.00023934 | -47.0993 | 71.0037 | -51.828 | 70.8344 | -50.7706 | -51.6129 | -51.0406 | -49.9832 | 71.0266 | -51.796 | -51.2741 | -51.4938 | -51.796 | -51.4847 | -0.091553 | -0.022888 | -0.19226 | 0.96588 | 0.6958 | 0.1236 | 0.78735 | 0.21515 | -0.059509 | 0 | -122.3007 | 0.24262 | 0.25177 | -0.059509 | 0.31128 | 0 | 1.0574 | 122.6624 | 0.30212 | 0.52185 | 122.8317 | 122.8226 | 122.7402 | 122.7631 | -122.8546 | -122.8226 | 122.5708 | 0.46234 | 4.6371 | 1.7532
3771.1719 | 122.9553 | -51.7502 | 71.0495 | -0.075836 | -1.9142e-05 | 0.062239 | 0.070113 | 0.00037377 | 0.0024053 | 0.0022174 | -0.089844 | 0.0019567 | 0.0012818 | 0.002196 | -0.0047103 | -0.0057935 | -0.0023243 | -47.0764 | 71.0587 | -51.8555 | 70.8344 | -50.7889 | -51.6357 | -51.123 | -49.9374 | 71.1273 | -51.7822 | -51.2924 | -51.5259 | -51.86 | -51.5259 | -0.10529 | 0.009155 | -0.21515 | 0.9613 | 0.62714 | 0.11444 | 0.73242 | 0.21973 | -0.032044 | 0.077819 | -122.3419 | 0.2243 | 0.2243 | -0.10986 | 0.25635 | -0.077819 | 1.0666 | 122.6898 | 0.25635 | 0.48981 | 122.9141 | 122.9095 | 122.8088 | 122.8775 | -122.905 | -122.8317 | 122.5845 | 0.45776 | 4.6738 | 1.8127
3772.1719 | 122.9462 | -51.7502 | 71.0587 | -0.060578 | 0.0021171 | 0.061171 | 0.068832 | -5.343e-05 | 0.0021917 | 0.0049946 | -0.0013428 | 0.00067495 | 0.00064083 | 0.0032642 | -0.0036423 | -0.0053663 | -0.00082886 | -47.1085 | 71.0999 | -51.8372 | 70.7794 | -50.853 | -51.6449 | -51.091 | -50.0885 | 71.1227 | -51.8051 | -51.3519 | -51.5579 | -51.8555 | -51.5625 | -0.086975 | 0.041199 | -0.27924 | 0.89722 | 0.65918 | 0.10529 | 0.74616 | 0.19226 | -0.054932 | 0.064087 | -122.4106 | 0.19226 | 0.18768 | -0.10529 | 0.24262 | -0.050354 | 0.98419 | 122.6166 | 0.24719 | 0.45319 | 122.937 | 122.9279 | 122.85 | 122.8729 | -122.8958 | -122.8638 | 122.5296 | 0.39825 | 4.6417 | 1.6617
3773.1719 | 122.9279 | -51.7456 | 71.077 | -0.052948 | 0.00062166 | 0.063948 | 0.069472 | 0.0027238 | 0.0024053 | 0.00414 | -0.053223 | 0.0013159 | 2.8e-08 | 0.003905 | -0.0044967 | -0.0077161 | 0.00023934 | -47.0856 | 71.0541 | -51.8555 | 70.7977 | -50.8026 | -51.6495 | -51.1047 | -50.0381 | 71.0953 | -51.7914 | -51.3519 | -51.5762 | -51.8555 | -51.5579 | -0.10986 | -0.022888 | -0.27924 | 0.94299 | 0.64087 | 0.09613 | 0.75073 | 0.20599 | -0.045777 | 0.018311 | -122.4289 | 0.16937 | 0.18768 | -0.10986 | 0.23346 | -0.064087 | 1.0529 | 122.6532 | 0.21515 | 0.43945 | 122.9095 | 122.8867 | 122.7997 | 122.8409 | -122.9324 | -122.8683 | 122.5433 | 0.39368 | 4.66 | 1.7075
3774.1719 | 122.9553 | -51.7593 | 71.1182 | -0.075836 | -0.0017281 | 0.061171 | 0.068191 | -0.0011214 | 0.0015509 | 0.0028582 | 0.016968 | 0.0032385 | 0.0021362 | 0.00070062 | -0.0021469 | -0.0062207 | 0.00066654 | -47.0947 | 71.0861 | -51.8326 | 70.784 | -50.8301 | -51.6403 | -51.0956 | -50.1068 | 71.1227 | -51.8005 | -51.3474 | -51.5533 | -51.8234 | -51.5579 | -0.073243 | -0.032043 | -0.33417 | 0.92926 | 0.66376 | 0.11902 | 0.737 | 0.19226 | -0.041199 | 0.004578 | -122.4655 | 0.20599 | 0.20142 | -0.064087 | 0.24262 | -0.022888 | 1.0025 | 122.6166 | 0.24719 | 0.45319 | 122.9187 | 122.9233 | 122.8455 | 122.8821 | -122.9507 | -122.9187 | 122.5433 | 0.41199 | 4.6646 | 1.6525
3775.1719 | 122.9691 | -51.7914 | 71.0495 | -0.091095 | 0.0014761 | 0.06053 | 0.0699 | -0.00026703 | 0.0019781 | 0.0073444 | -0.0074462 | 0.0015295 | 0.0040588 | 0.0019824 | -0.0030013 | -0.0032301 | 0.0015209 | -47.1359 | 71.0724 | -51.8555 | 70.7565 | -50.8759 | -51.709 | -51.1276 | -50.1114 | 71.0953 | -51.8188 | -51.3519 | -51.5808 | -51.8967 | -51.5625 | -0.064087 | 0.022888 | -0.29297 | 0.91553 | 0.66376 | 0.082398 | 0.72784 | 0.14648 | -0.027466 | 0.045776 | -122.4014 | 0.21057 | 0.22888 | -0.10529 | 0.25635 | -0.077819 | 0.97962 | 122.612 | 0.23804 | 0.46692 | 122.9279 | 122.9141 | 122.8638 | 122.8867 | -122.905 | -122.8683 | 122.5479 | 0.43945 | 4.6555 | 1.68
3776.1719 | 122.9645 | -51.7456 | 71.0724 | -0.068207 | 0.00062166 | 0.061812 | 0.069259 | 0.0027238 | 0.0021917 | 0.0067036 | -0.0013428 | 0.0017431 | 0.00021363 | -0.0078442 | -0.0019333 | -0.0055799 | 0.00088014 | -47.0947 | 71.1044 | -51.8509 | 70.7794 | -50.8438 | -51.6312 | -51.091 | -50.061 | 71.1182 | -51.7822 | -51.3336 | -51.535 | -51.8372 | -51.5488 | -0.10529 | 0.032043 | -0.29297 | 0.90179 | 0.6546 | 0.11444 | 0.75989 | 0.21973 | -0.036622 | 0.045776 | -122.406 | 0.21057 | 0.19684 | -0.091553 | 0.23346 | -0.054931 | 1.0071 | 122.6303 | 0.24719 | 0.44861 | 122.9553 | 122.9004 | 122.85 | 122.8638 | -122.9233 | -122.8546 | 122.525 | 0.41199 | 4.6509 | 1.6846
3777.1719 | 122.9645 | -51.7593 | 71.0678 | -0.068207 | -0.00066014 | 0.061812 | 0.0699 | 0.0035782 | 0.0017645 | 0.0062762 | 0.001709 | 0.00046135 | 0.001068 | -0.0018628 | -0.0023605 | -0.0049389 | 0.0019483 | -47.081 | 71.109 | -51.86 | 70.7977 | -50.853 | -51.6449 | -51.1002 | -50.0748 | 71.1319 | -51.796 | -51.3382 | -51.5305 | -51.8234 | -51.5167 | -0.10071 | 0.041199 | -0.27008 | 0.90637 | 0.65918 | 0.11444 | 0.75989 | 0.21515 | -0.036621 | 0.064087 | -122.406 | 0.22888 | 0.24261 | -0.064087 | 0.27923 | -0.027466 | 1.0071 | 122.6578 | 0.2655 | 0.45776 | 122.9691 | 122.9279 | 122.8683 | 122.8912 | -122.9279 | -122.8638 | 122.5571 | 0.42114 | 4.6783 | 1.6846
3778.1719 | 122.9645 | -51.7456 | 71.0815 | -0.098725 | -0.00087374 | 0.065016 | 0.068832 | 0.001442 | 0.0026191 | 0.0052082 | -0.019653 | 0.0015295 | 0.001068 | 0.00091422 | -0.0025741 | -0.0055799 | -0.0018971 | -47.0306 | 71.077 | -51.8326 | 70.8206 | -50.7477 | -51.622 | -51.0864 | -50.0381 | 71.0907 | -51.7593 | -51.3199 | -51.5396 | -51.8234 | -51.5259 | -0.086976 | -0.004578 | -0.26093 | 0.99792 | 0.65918 | 0.1236 | 0.74615 | 0.21057 | -0.013733 | 0.009155 | -122.4014 | 0.20599 | 0.21973 | -0.07782 | 0.23346 | -0.064087 | 1.0849 | 122.6532 | 0.21973 | 0.43945 | 122.9095 | 122.85 | 122.8226 | 122.8363 | -122.9141 | -122.8409 | 122.5662 | 0.42572 | 4.715 | 1.7075
3779.1719 | 122.9416 | -51.7639 | 71.0541 | -0.075836 | 0.0012625 | 0.059889 | 0.069045 | 0.00058737 | -0.0012261 | 0.0084124 | -0.016602 | 0.0028113 | -0.00064077 | -0.0016492 | -0.00086511 | -0.0066479 | 0.0010937 | -47.0581 | 71.0861 | -51.8372 | 70.7382 | -50.6836 | -51.5762 | -51.0498 | -50.0473 | 71.109 | -51.7731 | -51.297 | -51.5442 | -51.828 | -51.5305 | -0.073242 | 0.032044 | -0.31586 | 1.0803 | 0.71411 | 0.18768 | 0.78735 | 0.26093 | -0.009155 | 0.054932 | -122.3511 | 0.21973 | 0.23346 | -0.064087 | 0.24261 | -0.054932 | 1.1536 | 122.5754 | 0.22888 | 0.47607 | 122.9233 | 122.8821 | 122.85 | 122.8729 | -122.8912 | -122.8271 | 122.5021 | 0.46692 | 4.7058 | 1.7166
3780.1719 | 123.0194 | -51.7502 | 71.022 | -0.12924 | -0.00066014 | 0.06288 | 0.068404 | 0.0010148 | 0.0026191 | 0.005849 | 0.032227 | -0.00039305 | -0.00085457 | -0.00079478 | -0.0021469 | -0.0072889 | -0.0027515 | -47.0489 | 71.0129 | -51.8326 | 70.8481 | -50.7477 | -51.6083 | -51.0452 | -49.9969 | 71.0587 | -51.8097 | -51.2512 | -51.4893 | -51.796 | -51.4755 | -0.082398 | -0.009156 | -0.17395 | 1.0025 | 0.70496 | 0.14191 | 0.78735 | 0.22431 | -0.059509 | 0.036621 | -122.2733 | 0.26093 | 0.27466 | -0.045776 | 0.33417 | 0.013733 | 1.0849 | 122.6807 | 0.32043 | 0.55847 | 122.8455 | 122.8683 | 122.7631 | 122.8088 | -122.8546 | -122.8317 | 122.5983 | 0.49896 | 4.7012 | 1.7532
3781.1719 | 122.9599 | -51.7136 | 71.1548 | -0.014801 | -0.0017281 | 0.061812 | 0.066909 | -0.00069423 | 0.00026909 | 0.0037128 | 0.032227 | 0.0011023 | 0.002777 | 0.0017688 | -0.00086511 | -0.0081433 | -0.0012561 | -47.0535 | 71.1227 | -51.7914 | 70.7977 | -50.8072 | -51.6312 | -51.059 | -50.0931 | 71.1411 | -51.7776 | -51.3428 | -51.5305 | -51.6907 | -51.3336 | -0.07782 | -0.032043 | -0.35706 | 0.90637 | 0.6546 | 0.082397 | 0.73242 | 0.16022 | -0.064087 | -0.013733 | -122.4976 | 0.18311 | 0.37994 | 0.022888 | 0.44403 | 0.086975 | 0.98419 | 122.5891 | 0.24719 | 0.43488 | 122.9141 | 122.9187 | 122.8363 | 122.8546 | -122.9462 | -122.9324 | 122.5113 | 0.37079 | 4.66 | 1.6205
3782.1719 | 122.9782 | -51.7319 | 71.0861 | -0.075836 | -0.00087374 | 0.063094 | 0.070327 | -0.00048063 | 0.0017645 | 0.0037128 | -0.019653 | 0.0011023 | 0.00085443 | -0.00229 | -0.0047103 | -0.0049389 | -0.0016833 | -47.0306 | 71.1136 | -51.8372 | 70.8252 | -50.7889 | -51.6083 | -51.0635 | -50.0427 | 71.1548 | -51.7731 | -51.3016 | -51.5076 | -51.8097 | -51.503 | -0.10529 | 0.027465 | -0.26093 | 0.94299 | 0.66833 | 0.1236 | 0.77362 | 0.22888 | -0.041198 | 0.068664 | -122.3877 | 0.22431 | 0.22888 | -0.077819 | 0.27008 | -0.036621 | 1.0483 | 122.6624 | 0.2655 | 0.4715 | 122.9507 | 122.9279 | 122.8455 | 122.8867 | -122.9233 | -122.8592 | 122.5571 | 0.4303 | 4.7012 | 1.6891
3783.1719 | 122.9599 | -51.7227 | 71.0632 | -0.091095 | -0.00023294 | 0.061171 | 0.068191 | 0.0029374 | 0.00048269 | 0.0054218 | -0.0013428 | 0.00088875 | 0.0025634 | 0.0043322 | -0.0042831 | -0.0038709 | 0.0036571 | -46.9986 | 71.0953 | -51.8143 | 70.8435 | -50.7568 | -51.6037 | -51.0544 | -49.9786 | 71.1365 | -51.7639 | -51.297 | -51.5076 | -51.796 | -51.4984 | -0.091553 | 0.032044 | -0.21973 | 0.96588 | 0.66834 | 0.11902 | 0.75989 | 0.21057 | -0.041199 | 0.073243 | -122.3602 | 0.21515 | 0.2243 | -0.073242 | 0.2655 | -0.032043 | 1.0574 | 122.6578 | 0.25635 | 0.46692 | 122.9095 | 122.9004 | 122.818 | 122.8592 | -122.8775 | -122.8271 | 122.5662 | 0.42572 | 4.7241 | 1.7441
3784.1719 | 122.9324 | -51.7227 | 71.0953 | -0.03006 | -1.9142e-05 | 0.061171 | 0.068404 | -0.0026168 | 0.00026909 | 0.005849 | -0.044067 | 0.0017431 | 0.0021362 | -0.0076306 | -0.0032151 | -0.0060071 | -0.00018806 | -47.0398 | 71.1365 | -51.8005 | 70.8206 | -50.7339 | -51.3199 | -51.0818 | -50.0336 | 71.1411 | -51.7868 | -51.3199 | -51.503 | -51.8234 | -51.5259 | -0.07782 | 0.041199 | -0.27466 | 0.98877 | 0.64087 | 0.40283 | 0.71869 | 0.48065 | -0.064087 | 0.045776 | -122.4152 | 0.21973 | 0.19684 | -0.10071 | 0.26092 | -0.036621 | 1.0666 | 122.6212 | 0.28381 | 0.46692 | 122.937 | 122.9279 | 122.8592 | 122.8638 | -122.8958 | -122.8821 | 122.5433 | 0.40283 | 4.6829 | 1.6891
3785.1719 | 122.9599 | -51.7181 | 71.1273 | -0.022431 | 0.00083526 | 0.061385 | 0.068832 | 0.003151 | 0.0024053 | 0.0039264 | 0.0047608 | 0.0023839 | 0.00085443 | 0.00091422 | -0.0025741 | -0.0051527 | 0.0015209 | -47.0032 | 71.1227 | -51.8051 | 70.8206 | -50.798 | -51.6129 | -51.0544 | -50.0565 | 71.1365 | -51.7593 | -51.3199 | -51.5076 | -51.8005 | -51.5076 | -0.086975 | -0.004577 | -0.3067 | 0.9201 | 0.66376 | 0.10529 | 0.75073 | 0.19226 | -0.041198 | 0.009156 | -122.4472 | 0.21057 | 0.21057 | -0.082397 | 0.25177 | -0.041199 | 1.0071 | 122.6257 | 0.25177 | 0.43945 | 122.9279 | 122.8958 | 122.8409 | 122.8546 | -122.9324 | -122.8867 | 122.5388 | 0.39825 | 4.715 | 1.6617
3786.1719 | 122.9828 | -51.7136 | 71.1136 | -0.10635 | -0.0010873 | 0.061385 | 0.070113 | -0.00069423 | 0.0041143 | 0.0060626 | -0.0013428 | 0.0030249 | 0.00021363 | -0.0044262 | -0.0021469 | -0.0064343 | -0.0029651 | -46.9894 | 71.1227 | -51.8051 | 70.8435 | -50.766 | -51.5854 | -51.0452 | -50.0061 | 71.1502 | -51.7273 | -51.2878 | -51.4893 | -51.7685 | -51.4755 | -0.091553 | 0.009156 | -0.27008 | 0.94757 | 0.66834 | 0.12817 | 0.75989 | 0.21973 | -0.013733 | 0.036622 | -122.4014 | 0.2243 | 0.23804 | -0.054932 | 0.25177 | -0.041199 | 1.0391 | 122.6486 | 0.23804 | 0.43945 | 122.9279 | 122.8775 | 122.8363 | 122.8638 | -122.9187 | -122.8409 | 122.5571 | 0.42572 | 4.7241 | 1.7075
3787.1719 | 122.9599 | -51.7136 | 71.109 | -0.052948 | 0.0010489 | 0.059676 | 0.071609 | -0.0011214 | 0.0015509 | 0.0034992 | 0.001709 | 0.0017431 | 0.002777 | -0.0027174 | -0.0025741 | -0.0051527 | -0.00082886 | -46.9986 | 71.1411 | -51.796 | 70.8527 | -50.7706 | -51.5808 | -51.0315 | -50.0061 | 71.1548 | -51.7364 | -51.2695 | -51.4938 | -51.7731 | -51.4755 | -0.082397 | 0.032043 | -0.25635 | 0.94299 | 0.68207 | 0.13275 | 0.76447 | 0.21515 | -0.022888 | 0.045776 | -122.3785 | 0.21973 | 0.23804 | -0.059509 | 0.26093 | -0.036621 | 1.0254 | 122.6486 | 0.24262 | 0.46692 | 122.937 | 122.8912 | 122.8546 | 122.8683 | -122.905 | -122.8455 | 122.5662 | 0.44403 | 4.715 | 1.7075
3788.1719 | 122.9095 | -51.7273 | 71.1365 | -0.03006 | -0.0013009 | 0.06053 | 0.069259 | 0.00058737 | 0.0024053 | 0.002431 | 0.035278 | -0.00039305 | 2.8e-08 | -0.0052808 | -0.0030013 | -0.0040845 | 0.00045294 | -46.9986 | 71.1182 | -51.7685 | 70.9717 | -50.6104 | -51.7502 | -51.1642 | -50.0656 | 71.1777 | -51.7639 | -51.3062 | -51.5305 | -51.8005 | -51.503 | -0.041199 | -0.018311 | -0.16479 | 1.1169 | 0.56305 | -0.022888 | 0.60425 | 0.018311 | -0.036621 | 0.041198 | -122.4426 | 0.19684 | 0.2243 | -0.073242 | 0.26093 | -0.036621 | 1.1581 | 122.7402 | 0.23346 | 0.45776 | 122.8867 | 122.9416 | 122.8455 | 122.905 | -122.905 | -122.9004 | 122.699 | 0.42114 | 4.7287 | 1.6617
3789.1719 | 122.9416 | -51.7136 | 71.1411 | -0.045319 | 0.0016899 | 0.061385 | 0.066909 | 0.0040054 | 0.00048269 | 0.002431 | 0.023071 | 0.00088875 | 0.00064083 | 0.0013416 | -0.0025741 | -0.0062207 | -0.0012561 | -46.9894 | 71.1319 | -51.7822 | 70.8389 | -50.7568 | -51.5945 | -51.0361 | -50.0244 | 71.1548 | -51.7273 | -51.3062 | -51.5121 | -51.8326 | -51.5213 | -0.068665 | -0.009155 | -0.30212 | 0.95673 | 0.67749 | 0.11902 | 0.74616 | 0.18768 | -0.013733 | 0.013733 | -122.4472 | 0.20142 | 0.19226 | -0.11902 | 0.20599 | -0.10529 | 1.0254 | 122.6212 | 0.21515 | 0.42114 | 122.9141 | 122.8821 | 122.8455 | 122.8683 | -122.9233 | -122.8683 | 122.5525 | 0.40741 | 4.7241 | 1.6891
3790.1719 | 122.9645 | -51.709 | 71.1227 | -0.052948 | -0.00023294 | 0.065871 | 0.067977 | 0.003151 | 0.0030463 | 0.0056354 | -0.016602 | 0.00046135 | 0.00085443 | 0.00091422 | -0.0023605 | -0.0055799 | -0.0029651 | -46.9666 | 71.1136 | -51.8005 | 70.8206 | -50.798 | -51.6037 | -51.0635 | -50.0336 | 71.1731 | -51.7456 | -51.3062 | -51.5076 | -51.8051 | -51.5167 | -0.091553 | -0.009156 | -0.30212 | 0.91095 | 0.64545 | 0.10529 | 0.737 | 0.19684 | -0.036621 | 0.050354 | -122.4289 | 0.20142 | 0.19226 | -0.096131 | 0.22888 | -0.05951 | 1.0025 | 122.6212 | 0.23804 | 0.43945 | 122.9141 | 122.9187 | 122.8226 | 122.8821 | -122.9233 | -122.8683 | 122.5296 | 0.40283 | 4.7424 | 1.6754
3791.1719 | 122.9233 | -51.6815 | 71.1548 | -0.083466 | -0.00044654 | 0.061812 | 0.068618 | -0.005394 | 0.00091009 | 0.0028582 | 0.041382 | 3.4148e-05 | 0.0025634 | 0.00091422 | -0.0021469 | -0.0066479 | -0.0012561 | -46.9666 | 71.1319 | -51.7685 | 70.8435 | -50.7477 | -51.5717 | -51.0178 | -49.9969 | 71.1777 | -51.7364 | -51.297 | -51.4984 | -51.7731 | -51.4893 | -0.086975 | -0.022888 | -0.31128 | 0.93384 | 0.66376 | 0.10986 | 0.75073 | 0.19684 | -0.054931 | 0.022888 | -122.4518 | 0.18311 | 0.19226 | -0.091552 | 0.24719 | -0.036621 | 1.0208 | 122.612 | 0.23804 | 0.43945 | 122.9004 | 122.9141 | 122.8134 | 122.8592 | -122.9233 | -122.8912 | 122.525 | 0.38452 | 4.715 | 1.6846
3792.1719 | 122.9187 | -51.709 | 71.1456 | 0.030975 | -1.9142e-05 | 0.063094 | 0.069472 | 0.0020828 | 0.0017645 | 0.0067036 | -0.025757 | 0.0019567 | 0.001709 | -0.0031446 | -0.0027877 | -0.0057935 | -0.0016833 | -46.9574 | 71.1548 | -51.7685 | 70.752 | -50.8713 | -51.5213 | -51.0132 | -50.0015 | 71.1685 | -51.7273 | -51.2695 | -51.4938 | -51.7822 | -51.4847 | -0.05951 | 0.009155 | -0.39368 | 0.83771 | 0.6958 | 0.18768 | 0.75531 | 0.24719 | -0.018311 | 0.022888 | -122.4152 | 0.21515 | 0.2243 | -0.073243 | 0.24262 | -0.054932 | 0.89722 | 122.5204 | 0.23346 | 0.45776 | 122.9233 | 122.8958 | 122.8638 | 122.8775 | -122.9141 | -122.8729 | 122.4609 | 0.43945 | 4.7516 | 1.7075
3793.1719 | 122.9416 | -51.6998 | 71.1456 | -0.083466 | -0.00066014 | 0.058607 | 0.0699 | 0.0035782 | 0.0011237 | 0.0039264 | -0.010498 | 0.0015295 | 0.00021363 | 0.00027342 | -0.0036423 | -0.0034437 | 0.0010937 | -46.9391 | 71.1594 | -51.796 | 70.871 | -50.766 | -51.5808 | -51.0269 | -50.0107 | 71.1777 | -51.7273 | -51.2695 | -51.4664 | -51.7822 | -51.4618 | -0.09613 | 0.013733 | -0.27466 | 0.93384 | 0.67291 | 0.11902 | 0.76904 | 0.21515 | -0.027466 | 0.032043 | -122.4152 | 0.23346 | 0.23804 | -0.082398 | 0.2655 | -0.054932 | 1.03 | 122.6669 | 0.26093 | 0.45776 | 122.9553 | 122.905 | 122.8592 | 122.8775 | -122.9416 | -122.8729 | 122.5708 | 0.4303 | 4.7607 | 1.6891
3794.1719 | 122.9187 | -51.6861 | 71.1411 | -0.068207 | 0.0010489 | 0.059035 | 0.068404 | -0.00048063 | -0.00037171 | 0.0022174 | 0.053589 | 0.00024775 | 0.00021363 | -0.00036738 | -0.0025741 | -0.0066479 | -0.0018971 | -46.8842 | 71.1273 | -51.7685 | 70.8984 | -50.679 | -51.5259 | -50.9583 | -49.942 | 71.1685 | -51.7044 | -51.2695 | -51.4526 | -51.7456 | -51.4801 | -0.082398 | -0.013733 | -0.24262 | 1.0071 | 0.72784 | 0.16022 | 0.81024 | 0.24261 | -0.018311 | 0.027466 | -122.4106 | 0.23346 | 0.20599 | -0.059509 | 0.2243 | -0.041198 | 1.0895 | 122.6669 | 0.25177 | 0.43488 | 122.8958 | 122.8729 | 122.8134 | 122.8546 | -122.9095 | -122.8455 | 122.5845 | 0.41656 | 4.8019 | 1.7441
3795.1719 | 122.9553 | -51.6724 | 71.1639 | -0.10635 | 0.00083526 | 0.061171 | 0.068404 | 0.0016556 | -0.00037171 | 0.0052082 | 0.0047608 | 0.00067495 | 0.0025634 | -0.00229 | -0.0025741 | -0.0040845 | -0.00040166 | -46.9162 | 71.1685 | -51.796 | 70.8664 | -50.7614 | -51.5717 | -51.0178 | -49.9969 | 71.2097 | -51.7319 | -51.2695 | -51.4801 | -51.7593 | -51.4618 | -0.1236 | 0.004578 | -0.29755 | 0.91095 | 0.6546 | 0.10071 | 0.7782 | 0.2243 | -0.05951 | 0.045777 | -122.4335 | 0.19226 | 0.21057 | -0.086975 | 0.27008 | -0.027465 | 1.0345 | 122.6624 | 0.25177 | 0.46234 | 122.9645 | 122.9416 | 122.8409 | 122.8821 | -122.9599 | -122.8958 | 122.5388 | 0.40283 | 4.7562 | 1.6754
3796.1719 | 122.9416 | -51.6632 | 71.2097 | -0.052948 | -0.00044654 | 0.061171 | 0.069472 | -0.00048063 | 0.0026191 | 0.0020038 | 0.0047608 | -0.00017945 | 0.001709 | -0.00058098 | -0.0019333 | -0.0064343 | -0.0042469 | -46.9162 | 71.1456 | -51.7502 | 70.8664 | -50.7202 | -51.5625 | -51.0178 | -49.9832 | 71.2051 | -51.6998 | -51.2787 | -51.4755 | -51.7822 | -51.5991 | -0.086975 | -0.064087 | -0.34332 | 0.94299 | 0.64545 | 0.10071 | 0.73242 | 0.18768 | -0.036621 | -0.004578 | -122.4884 | 0.18768 | 0.064087 | -0.11902 | 0.10071 | -0.082398 | 1.03 | 122.6166 | 0.2243 | 0.42114 | 122.8958 | 122.905 | 122.8088 | 122.8683 | -122.9599 | -122.9095 | 122.5296 | 0.38452 | 4.747 | 1.68
3797.1719 | 122.905 | -51.7044 | 71.1731 | -0.098725 | -0.00044654 | 0.062239 | 0.069045 | -0.0049668 | 0.0019781 | 0.0032856 | -0.0043946 | 0.0011023 | 0.0032044 | -0.0042126 | -0.0010787 | -0.0070753 | 0.0045117 | -46.907 | 71.1411 | -51.7548 | 70.8572 | -50.7111 | -51.5533 | -50.9995 | -49.9832 | 71.196 | -51.6998 | -51.2695 | -51.4709 | -51.7685 | -51.4984 | -0.050354 | -0.032044 | -0.31586 | 0.99335 | 0.70496 | 0.15106 | 0.75531 | 0.20142 | 0.004578 | 0.022888 | -122.4426 | 0.23346 | 0.20599 | -0.064087 | 0.20142 | -0.068665 | 1.0437 | 122.612 | 0.22888 | 0.4303 | 122.8958 | 122.8958 | 122.8455 | 122.9004 | -122.9279 | -122.8729 | 122.5616 | 0.43488 | 4.7974 | 1.7212
3798.1719 | 122.9736 | -51.6953 | 71.1548 | -0.083466 | 0.0012625 | 0.062239 | 0.068832 | 0.0010148 | 0.00091009 | 0.0049946 | -0.0074462 | 0.0015295 | 0.001068 | -0.0016492 | -0.0021469 | -0.0070753 | -0.0018971 | -46.9116 | 71.1823 | -51.7685 | 70.8984 | -50.7202 | -51.5625 | -50.9949 | -49.9695 | 71.2097 | -51.6907 | -51.2283 | -51.4481 | -51.7502 | -51.4343 | -0.073243 | 0.027466 | -0.25635 | 0.97504 | 0.70038 | 0.13275 | 0.77362 | 0.20599 | 0.004577 | 0.054932 | -122.3831 | 0.24719 | 0.26093 | -0.054932 | 0.25635 | -0.059509 | 1.0483 | 122.6669 | 0.24262 | 0.46234 | 122.9507 | 122.9004 | 122.8775 | 122.905 | -122.9233 | -122.8455 | 122.5937 | 0.46692 | 4.7836 | 1.7258
3799.1719 | 122.9645 | -51.6403 | 71.1731 | -0.037689 | 0.0010489 | 0.062239 | 0.069259 | 0.0020828 | 0.0013373 | 0.00414 | -0.01355 | 0.0030249 | 0.001709 | -0.0052808 | -0.0042831 | -0.0070753 | 0.0023755 | -46.8979 | 71.1868 | -51.7227 | 70.8847 | -50.7156 | -51.5396 | -50.972 | -49.9603 | 71.2097 | -51.6953 | -51.2192 | -51.4343 | -51.7319 | -51.4252 | -0.082397 | 0.013733 | -0.28839 | 0.92468 | 0.66834 | 0.10071 | 0.75073 | 0.18311 | -0.054931 | 0.036621 | -122.3923 | 0.20599 | 0.21515 | -0.091553 | 0.27008 | -0.036622 | 1.0071 | 122.6074 | 0.26093 | 0.47607 | 122.9095 | 122.905 | 122.8271 | 122.85 | -122.8958 | -122.8683 | 122.525 | 0.42114 | 4.7424 | 1.68
3800.1719 | 122.9095 | -51.6769 | 71.1868 | -0.075836 | -0.00023294 | 0.061385 | 0.069045 | -5.343e-05 | 5.5488e-05 | 0.0054218 | -0.03186 | 0.0028113 | -0.00021357 | -0.0069898 | -0.0021469 | -0.0057935 | 0.0010937 | -46.9116 | 71.2006 | -51.7639 | 70.8252 | -50.5783 | -51.3474 | -51.0818 | -49.9558 | 71.2006 | -51.6953 | -51.2466 | -51.4572 | -51.7593 | -51.4709 | -0.086975 | 0.013733 | -0.36163 | 1.0986 | 0.59509 | 0.32959 | 0.68207 | 0.41656 | -0.01831 | 0.013733 | -122.4335 | 0.21973 | 0.20599 | -0.082397 | 0.2243 | -0.064087 | 1.1856 | 122.5891 | 0.23804 | 0.44861 | 122.9645 | 122.8958 | 122.8775 | 122.8775 | -122.9507 | -122.8821 | 122.5021 | 0.4303 | 4.7653 | 1.7212
3801.1719 | 122.9141 | -51.6678 | 71.1456 | -0.060578 | -0.00087374 | 0.058607 | 0.0652 | 0.0020828 | 0.0034735 | 0.0026446 | 0.074951 | 0.00067495 | -0.00085457 | 0.0028368 | -1.0706e-05 | -0.0053663 | -0.0033923 | -46.8338 | 71.1502 | -51.7044 | 70.9259 | -50.6378 | -51.4893 | -50.9399 | -49.9054 | 71.2189 | -51.6724 | -51.2375 | -51.4297 | -51.741 | -51.4755 | -0.036621 | 0.004578 | -0.21973 | 1.03 | 0.72785 | 0.17853 | 0.76447 | 0.21515 | -0.004577 | 0.073242 | -122.3831 | 0.23804 | 0.19226 | -0.073242 | 0.19684 | -0.068665 | 1.0666 | 122.6303 | 0.24261 | 0.43487 | 122.8546 | 122.8912 | 122.818 | 122.8867 | -122.85 | -122.818 | 122.5937 | 0.4303 | 4.834 | 1.7624
3802.1719 | 122.8821 | -51.6678 | 71.1914 | -0.10635 | -0.0021555 | 0.061385 | 0.065414 | 0.0027238 | 0.0013373 | 0.0015766 | -0.0013428 | 0.0023839 | 0.001709 | -0.002931 | -0.0030013 | -0.0051527 | 0.00066654 | -46.8933 | 71.1914 | -51.7364 | 70.8801 | -50.7065 | -51.5488 | -50.9857 | -49.9649 | 71.228 | -51.6861 | -51.3474 | -51.4618 | -51.7456 | -51.4572 | -0.068664 | 0 | -0.31128 | 0.9613 | 0.68207 | 0.11902 | 0.75073 | 0.18768 | -0.01831 | 0.036621 | -122.5388 | 0.20599 | 0.21057 | -0.077819 | 0.22888 | -0.059509 | 1.03 | 122.6166 | 0.2243 | 0.33874 | 122.9279 | 122.9141 | 122.8592 | 122.8958 | -122.9279 | -122.8775 | 122.5479 | 0.32043 | 4.7745 | 1.7029
3803.1719 | 122.9736 | -51.6632 | 71.1777 | 0.008087 | 0.0023307 | 0.061385 | 0.070113 | 0.0033646 | 0.0019781 | 0.0079852 | -0.028809 | 0.0032385 | 0.001068 | 0.0075366 | -0.0021469 | -0.0057935 | -0.0010425 | -46.843 | 71.1868 | -51.7319 | 70.9167 | -50.6882 | -51.5121 | -50.9583 | -49.9283 | 71.2234 | -51.6769 | -51.21 | -51.4343 | -51.7181 | -51.4114 | -0.068665 | 0.009156 | -0.26093 | 0.97504 | 0.70496 | 0.15106 | 0.77362 | 0.21973 | -0.013733 | 0.045777 | -122.3877 | 0.22888 | 0.25177 | -0.054932 | 0.2655 | -0.041199 | 1.0437 | 122.6486 | 0.24262 | 0.46692 | 122.9187 | 122.9004 | 122.85 | 122.8867 | -122.9095 | -122.8546 | 122.58 | 0.45319 | 4.8203 | 1.7349
3804.1719 | 122.9416 | -51.6769 | 71.2143 | -0.12161 | 0.0014761 | 0.059676 | 0.067123 | -0.0011214 | 0.0051825 | 0.0037128 | 0.013916 | 0.0019567 | 0.0021362 | 0.002196 | -0.0012925 | -0.0034437 | 0.00066654 | -46.9345 | 71.2097 | -51.7364 | 70.8939 | -50.7202 | -51.535 | -50.9903 | -49.9603 | 71.2372 | -51.6815 | -51.2283 | -51.4389 | -51.7181 | -51.4389 | -0.059509 | -0.004577 | -0.32043 | 0.95673 | 0.68665 | 0.14191 | 0.74615 | 0.20142 | -0.004578 | 0.022889 | -122.4426 | 0.23804 | 0.23804 | -0.041199 | 0.24262 | -0.036621 | 1.0162 | 122.6303 | 0.24262 | 0.45319 | 122.9462 | 122.9187 | 122.8867 | 122.9141 | -122.9507 | -122.8958 | 122.5708 | 0.44861 | 4.7424 | 1.7166
3805.1719 | 122.9691 | -51.6586 | 71.1639 | -0.022431 | 0.00083526 | 0.060316 | 0.068832 | 0.003151 | 0.0011237 | 0.0037128 | 0.0047608 | 3.4148e-05 | 0.00085443 | 0.0017688 | -0.00043791 | -0.0060071 | 0.0010937 | -46.843 | 71.1914 | -51.7273 | 70.8984 | -50.7065 | -51.5213 | -50.9674 | -49.9237 | 71.2234 | -51.6678 | -51.21 | -51.4297 | -51.7227 | -51.4297 | -0.068665 | 0.027466 | -0.2655 | 0.95215 | 0.69122 | 0.13733 | 0.75989 | 0.20599 | -0.009156 | 0.05951 | -122.374 | 0.22888 | 0.22888 | -0.064087 | 0.23804 | -0.054931 | 1.0208 | 122.6257 | 0.23804 | 0.45776 | 122.9187 | 122.8912 | 122.85 | 122.8821 | -122.8912 | -122.8317 | 122.5571 | 0.44861 | 4.8157 | 1.7349
3806.1719 | 122.9004 | -51.6357 | 71.196 | -0.045319 | 0.00040806 | 0.060103 | 0.068832 | -0.00048063 | 0.0026191 | 0.0056354 | 0.12683 | 0.0028113 | 0.0012818 | -0.0031446 | -0.0012925 | -0.0053663 | -0.0012561 | -46.8475 | 71.2097 | -51.7227 | 70.903 | -50.6882 | -51.535 | -50.972 | -50.0153 | 71.2509 | -51.6586 | -51.2238 | -51.4435 | -51.7502 | -51.4526 | -0.086975 | 0.013733 | -0.29297 | 0.94757 | 0.66376 | 0.10071 | 0.75073 | 0.18768 | -0.022888 | 0.054932 | -122.4197 | 0.19226 | 0.1831 | -0.11444 | 0.20599 | -0.091553 | 1.0345 | 122.6257 | 0.21515 | 0.43488 | 122.9324 | 122.9095 | 122.8455 | 122.8867 | -122.9187 | -122.8546 | 122.5388 | 0.41199 | 4.7882 | 1.6205
3807.1719 | 122.9691 | -51.6312 | 71.1685 | -0.13687 | -0.00087374 | 0.06288 | 0.070327 | -0.00026703 | 0.0021917 | 0.0056354 | -0.12036 | 0.0028113 | -0.00042717 | 0.00091422 | -0.0036423 | -0.0032301 | 0.0019483 | -46.8109 | 71.1639 | -51.7502 | 70.9305 | -50.647 | -51.5305 | -50.9628 | -49.8047 | 71.2189 | -51.6449 | -51.1871 | -51.4252 | -51.709 | -51.416 | -0.11902 | -0.004578 | -0.23804 | 0.98419 | 0.66834 | 0.10071 | 0.78735 | 0.21973 | -0.013732 | 0.050354 | -122.3557 | 0.20599 | 0.21515 | -0.077819 | 0.22888 | -0.064087 | 1.1032 | 122.6807 | 0.21973 | 0.45776 | 122.9141 | 122.8638 | 122.7951 | 122.85 | -122.9187 | -122.8134 | 122.5616 | 0.44403 | 4.8203 | 1.8265
3808.1719 | 122.9279 | -51.6083 | 71.1868 | -0.1445 | 0.0010489 | 0.061385 | 0.066909 | -0.0017624 | 0.0019781 | 0.0069172 | 0.016968 | 0.0019567 | 0.0023498 | 0.0071094 | -0.0017197 | -0.0062207 | 0.00066654 | -46.8109 | 71.2143 | -51.741 | 70.9167 | -50.6836 | -51.5305 | -50.9674 | -49.9603 | 71.2555 | -51.6632 | -51.2192 | -51.4343 | -51.7044 | -51.4435 | -0.13275 | 0.027465 | -0.27008 | 0.92468 | 0.64087 | 0.077819 | 0.77362 | 0.21057 | -0.054932 | 0.068664 | -122.406 | 0.17395 | 0.16479 | -0.096131 | 0.21973 | -0.041199 | 1.0574 | 122.6578 | 0.22888 | 0.44403 | 122.9553 | 122.9187 | 122.8226 | 122.8638 | -122.9279 | -122.85 | 122.525 | 0.3891 | 4.7974 | 1.6479
3809.1719 | 122.9782 | -51.6083 | 71.196 | -0.075836 | -0.0023691 | 0.062239 | 0.065627 | -0.00090783 | 0.0017645 | 0.0054218 | 0.047485 | 0.00024775 | 0.0012818 | -0.00229 | -0.0042831 | -0.0066479 | -0.0042469 | -46.788 | 71.1914 | -51.6724 | 71.0129 | -50.5829 | -51.4069 | -50.853 | -49.8184 | 71.228 | -51.6312 | -51.1414 | -51.3519 | -51.6037 | -51.3702 | -0.064087 | -0.004578 | -0.18311 | 1.0254 | 0.75531 | 0.20142 | 0.8194 | 0.2655 | -0.022889 | 0.032043 | -122.3373 | 0.25635 | 0.23804 | 0.004577 | 0.26093 | 0.027466 | 1.0895 | 122.6852 | 0.27924 | 0.48981 | 122.8638 | 122.8592 | 122.7997 | 122.8363 | -122.8683 | -122.8271 | 122.6212 | 0.46692 | 4.8203 | 1.7899
3810.1719 | 122.9279 | -51.6083 | 71.2143 | -0.075836 | 0.0012625 | 0.062666 | 0.068832 | -0.0013352 | 0.00091009 | 0.0034992 | 0.013916 | -0.00060665 | 0.0036316 | -0.00079478 | -0.0017197 | -0.0083569 | 0.0017345 | -46.843 | 71.2143 | -51.7273 | 70.9122 | -50.6927 | -51.5213 | -50.9537 | -49.8138 | 71.2967 | -51.6083 | -51.2421 | -51.4297 | -51.7136 | -51.4343 | -0.11902 | 0 | -0.30212 | 0.91553 | 0.6546 | 0.086975 | 0.77362 | 0.20599 | 0 | 0.082398 | -122.4564 | 0.17853 | 0.17395 | -0.10529 | 0.17395 | -0.10529 | 1.0345 | 122.6395 | 0.17853 | 0.36621 | 122.9416 | 122.905 | 122.8226 | 122.905 | -122.9416 | -122.8226 | 122.5204 | 0.36621 | 4.7653 | 1.7944
3811.1719 | 122.9599 | -51.622 | 71.2143 | -0.03006 | -0.0010873 | 0.061385 | 0.068404 | -0.00048063 | 0.0028327 | 0.00414 | -0.016602 | 0.0011023 | 0.0023498 | -0.0035718 | -0.0010787 | -0.0060071 | 0.0021619 | -46.8109 | 71.2418 | -51.6998 | 70.9122 | -50.6653 | -51.5121 | -50.9583 | -49.9237 | 71.2784 | -51.6632 | -51.2054 | -51.416 | -51.6953 | -51.4114 | -0.07782 | 0.027466 | -0.30212 | 0.95673 | 0.66376 | 0.10986 | 0.74158 | 0.18768 | -0.041199 | 0.064087 | -122.4197 | 0.20599 | 0.21057 | -0.073242 | 0.25177 | -0.032043 | 1.0345 | 122.612 | 0.24719 | 0.45776 | 122.9416 | 122.9416 | 122.8638 | 122.9004 | -122.9141 | -122.8775 | 122.5342 | 0.41656 | 4.8111 | 1.6983
3812.1719 | 122.9874 | -51.5991 | 71.2326 | -0.098725 | 0.0025443 | 0.063307 | 0.0699 | 0.0020828 | 0.0028327 | 0.0020038 | -0.0043946 | 0.00067495 | 0.0032044 | -0.0050672 | -0.0027877 | -0.0070753 | -0.0010425 | -46.788 | 71.2234 | -51.7044 | 70.9488 | -50.647 | -51.4893 | -50.9354 | -49.8825 | 71.2555 | -51.6403 | -51.1642 | -51.3794 | -51.6815 | -51.384 | -0.10529 | -0.009155 | -0.28381 | 0.95215 | 0.66376 | 0.10986 | 0.76904 | 0.21515 | -0.041199 | 0.022888 | -122.3969 | 0.21973 | 0.21515 | -0.082398 | 0.25635 | -0.041199 | 1.0574 | 122.6532 | 0.26093 | 0.47607 | 122.9279 | 122.8958 | 122.8226 | 122.8546 | -122.937 | -122.8729 | 122.5479 | 0.43487 | 4.8111 | 1.7166
3813.1719 | 122.9004 | -51.6312 | 71.2372 | -0.045319 | 0.0010489 | 0.059462 | 0.066482 | 0.00058737 | 0.00026909 | 0.0034992 | 0.050537 | 0.00024775 | 0.0014954 | 0.0028368 | -0.0012925 | -0.0081433 | 0.00023934 | -46.7606 | 71.2326 | -51.6953 | 70.9534 | -50.6332 | -51.4847 | -50.9171 | -49.8871 | 71.2509 | -51.6129 | -51.2009 | -51.4069 | -51.6907 | -51.4252 | -0.064086 | -0.004578 | -0.28381 | 0.99793 | 0.71411 | 0.14649 | 0.7782 | 0.21057 | 0.018311 | 0.013733 | -122.4381 | 0.22431 | 0.20599 | -0.059509 | 0.18768 | -0.07782 | 1.062 | 122.6486 | 0.20599 | 0.41199 | 122.9279 | 122.8638 | 122.8638 | 122.8821 | -122.9324 | -122.85 | 122.5845 | 0.4303 | 4.8706 | 1.7441
3814.1719 | 122.9462 | -51.6312 | 71.2326 | -0.060578 | 0.00083526 | 0.062025 | 0.070113 | -0.0041122 | 0.0011237 | 0.0054218 | 0.010864 | 0.0017431 | 0.00085443 | 0.0047594 | -0.0015061 | -0.0055799 | 2.554e-05 | -46.788 | 71.2234 | -51.709 | 70.9442 | -50.6561 | -51.4893 | -50.9491 | -49.9741 | 71.2738 | -51.6083 | -51.178 | -51.4481 | -51.7273 | -51.416 | -0.077819 | -0.009155 | -0.28839 | 0.97504 | 0.68207 | 0.14191 | 0.75989 | 0.21973 | 0.022889 | 0.041199 | -122.4106 | 0.18311 | 0.21515 | -0.09613 | 0.19226 | -0.11902 | 1.0529 | 122.6532 | 0.16022 | 0.4303 | 122.9324 | 122.8821 | 122.8546 | 122.905 | -122.9416 | -122.8409 | 122.5754 | 0.45319 | 4.8431 | 1.6571
3815.1719 | 122.9599 | -51.5808 | 71.2189 | -0.083466 | 0.00040806 | 0.062453 | 0.068618 | -0.0017624 | 0.0036871 | 0.0056354 | 0.010864 | 0.0021703 | 0.0019226 | 0.0017688 | -0.0044967 | -0.0064343 | -0.0014697 | -46.7331 | 71.2234 | -51.6586 | 71.0083 | -50.5554 | -51.4206 | -50.8438 | -49.8184 | 71.2326 | -51.6174 | -51.1368 | -51.3519 | -51.6312 | -51.3565 | -0.077819 | 0.004578 | -0.21057 | 1.0254 | 0.737 | 0.16022 | 0.81482 | 0.23804 | -0.036621 | 0.013733 | -122.3557 | 0.22888 | 0.2243 | -0.050354 | 0.26093 | -0.013733 | 1.1032 | 122.6669 | 0.2655 | 0.48065 | 122.8821 | 122.85 | 122.8043 | 122.8134 | -122.8775 | -122.8363 | 122.5891 | 0.44403 | 4.8477 | 1.7624
3816.1719 | 123.024 | -51.5717 | 71.2006 | -0.052948 | -0.00066014 | 0.060957 | 0.068618 | -0.0041122 | 0.0015509 | 0.0047808 | 0.03833 | 0.0017431 | 2.8e-08 | -0.00015378 | -0.0025741 | -0.0068615 | 0.00088014 | -46.7056 | 71.2051 | -51.6541 | 70.8435 | -50.6973 | -51.2878 | -50.8163 | -49.7314 | 71.2234 | -51.6083 | -51.0956 | -51.2741 | -51.5579 | -51.2878 | -0.082398 | 0.004577 | -0.35706 | 0.87433 | 0.75531 | 0.28381 | 0.83771 | 0.36621 | -0.036621 | 0.022888 | -122.2961 | 0.29755 | 0.28381 | 0.013733 | 0.32043 | 0.050354 | 0.95673 | 122.4976 | 0.33417 | 0.51269 | 122.8592 | 122.8317 | 122.7768 | 122.7951 | -122.8546 | -122.8088 | 122.4152 | 0.47607 | 4.866 | 1.8402
3817.1719 | 123.0057 | -51.5854 | 71.2555 | -0.083466 | -0.00044654 | 0.060316 | 0.067336 | -0.0017624 | 0.00048269 | 0.0034992 | 0.044434 | 0.0013159 | -0.00064077 | -0.0042126 | -0.0042831 | -0.0075025 | 0.00066654 | -46.7102 | 71.2326 | -51.6495 | 71.0449 | -50.5142 | -51.3931 | -50.8347 | -49.7589 | 71.2463 | -51.6174 | -51.1002 | -51.3016 | -51.5808 | -51.329 | -0.064087 | -0.022888 | -0.21057 | 1.0712 | 0.75073 | 0.19226 | 0.81482 | 0.25635 | -0.032044 | -0.009155 | -122.3557 | 0.28381 | 0.25635 | 0.004577 | 0.28839 | 0.036621 | 1.1353 | 122.6944 | 0.31586 | 0.51727 | 122.8821 | 122.8638 | 122.818 | 122.8317 | -122.905 | -122.8729 | 122.6303 | 0.48523 | 4.8752 | 1.8265
3818.1719 | 122.9691 | -51.5854 | 71.2509 | -0.037689 | -1.9142e-05 | 0.060316 | 0.070113 | 0.0027238 | 0.0019781 | 0.0043536 | -0.050171 | 0.0019567 | 0.001068 | 0.005614 | -0.0017197 | -0.0083569 | 2.554e-05 | -46.7331 | 71.2463 | -51.6998 | 70.9991 | -50.6058 | -51.4389 | -50.9125 | -49.823 | 71.2646 | -51.6312 | -51.1414 | -51.3702 | -51.6769 | -51.3657 | -0.11444 | -0.004578 | -0.25177 | 0.97961 | 0.67291 | 0.14648 | 0.78735 | 0.26093 | -0.045777 | 0.013732 | -122.3923 | 0.21515 | 0.21973 | -0.091553 | 0.2655 | -0.045776 | 1.0941 | 122.699 | 0.26093 | 0.48981 | 122.9462 | 122.8958 | 122.8317 | 122.85 | -122.9507 | -122.8821 | 122.5845 | 0.44403 | 4.8523 | 1.7624
3819.1719 | 122.8912 | -51.59 | 71.2555 | -0.014801 | -0.0013009 | 0.063521 | 0.06755 | 0.00080117 | 0.0015509 | 0.0047808 | 0.010864 | 0.0019567 | 0.001068 | 0.0024096 | -0.0021469 | -0.0085705 | -0.00040166 | -46.7606 | 71.283 | -51.6907 | 70.9488 | -50.6287 | -51.4893 | -50.9125 | -49.8825 | 71.3104 | -51.622 | -51.1002 | -51.2283 | -51.7731 | -51.4984 | -0.10071 | 0.027466 | -0.3067 | 0.9613 | 0.67749 | 0.10071 | 0.7782 | 0.20142 | -0.032043 | 0.054932 | -122.3557 | 0.36163 | 0.091553 | -0.18311 | 0.1236 | -0.15106 | 1.062 | 122.6395 | 0.39368 | 0.52185 | 122.9736 | 122.9324 | 122.8729 | 122.9004 | -122.9462 | -122.8775 | 122.5388 | 0.48981 | 4.8294 | 1.7075
3820.1719 | 122.9324 | -51.59 | 71.2509 | -0.098725 | -1.9142e-05 | 0.062666 | 0.067977 | 0.001442 | -0.00015811 | 0.0039264 | -0.016602 | -0.00060665 | 0.0021362 | 0.0026232 | -0.0019333 | -0.0081433 | -0.0012561 | -46.875 | 71.283 | -51.6724 | 70.9488 | -50.6516 | -51.4755 | -50.9125 | -49.8871 | 71.3104 | -51.6174 | -51.1551 | -51.3886 | -51.6724 | -51.3931 | -0.082397 | 0.032043 | -0.30212 | 0.93842 | 0.67749 | 0.11444 | 0.75989 | 0.19684 | -0.027466 | 0.059509 | -122.406 | 0.20142 | 0.19684 | -0.082397 | 0.22431 | -0.054931 | 1.0208 | 122.6212 | 0.22888 | 0.46234 | 122.9553 | 122.9279 | 122.8729 | 122.9004 | -122.9233 | -122.8683 | 122.5388 | 0.43488 | 4.715 | 1.7029
3821.1719 | 122.9507 | -51.5717 | 71.2601 | -0.091095 | 0.00083526 | 0.05818 | 0.069045 | -0.00048063 | 0.0034735 | 0.0022174 | 0.032227 | -0.00017945 | 0.0012818 | -0.0031446 | -0.0015061 | -0.0055799 | -0.00061526 | -46.7011 | 71.2372 | -51.6541 | 70.9946 | -50.5646 | -51.4526 | -50.8804 | -49.8413 | 71.3104 | -51.5854 | -51.1597 | -51.3748 | -51.6632 | -51.384 | -0.082398 | -0.022888 | -0.2655 | 1.0071 | 0.69122 | 0.11902 | 0.77362 | 0.20142 | -0.013733 | 0.050354 | -122.4197 | 0.19684 | 0.18768 | -0.091553 | 0.20142 | -0.07782 | 1.0895 | 122.6486 | 0.21057 | 0.42572 | 122.8912 | 122.8958 | 122.8088 | 122.8821 | -122.9141 | -122.8455 | 122.5662 | 0.41199 | 4.8706 | 1.7303
3822.1719 | 122.9919 | -51.5488 | 71.2051 | -0.10635 | 0.00083526 | 0.062239 | 0.067977 | 0.0016556 | 5.5488e-05 | 0.003072 | 0.047485 | 0.00046135 | 0.00021363 | -0.006349 | -0.0036423 | -0.0092115 | 0.0017345 | -46.669 | 71.2326 | -51.622 | 71.0999 | -50.4639 | -51.329 | -50.7706 | -49.7223 | 71.2463 | -51.6037 | -51.1597 | -51.4114 | -51.4709 | -51.2238 | -0.073242 | 0.027466 | -0.10529 | 1.0849 | 0.7782 | 0.21973 | 0.85144 | 0.29297 | -0.054932 | 0.041199 | -122.3648 | 0.13733 | 0.32501 | 0.07782 | 0.37994 | 0.13275 | 1.1581 | 122.7219 | 0.19226 | 0.44403 | 122.8546 | 122.85 | 122.7814 | 122.7951 | -122.8271 | -122.8088 | 122.6486 | 0.3891 | 4.8798 | 1.8265
3823.1719 | 122.9691 | -51.5625 | 71.2784 | -0.03006 | -0.00023294 | 0.060957 | 0.069259 | 0.00037377 | 0.0024053 | 0.0084124 | -0.016602 | 0.00088875 | 0.00021363 | 0.00027342 | -0.0019333 | -0.0079297 | 0.00088014 | -46.7148 | 71.2601 | -51.6403 | 70.9717 | -50.6058 | -51.4618 | -50.9308 | -49.855 | 71.315 | -51.6083 | -51.1551 | -51.3565 | -51.6541 | -51.3565 | -0.07782 | -0.01831 | -0.3067 | 0.95673 | 0.63171 | 0.10071 | 0.70953 | 0.17853 | -0.045776 | 0.036621 | -122.4335 | 0.20599 | 0.20599 | -0.091553 | 0.25177 | -0.045777 | 1.0345 | 122.612 | 0.25177 | 0.45319 | 122.9004 | 122.9233 | 122.8226 | 122.8775 | -122.9187 | -122.8867 | 122.5342 | 0.40741 | 4.8477 | 1.7075
3824.1719 | 123.0606 | -51.5396 | 71.2555 | 0.076752 | -0.00023294 | 0.062666 | 0.06755 | 0.0016556 | 0.0019781 | 0.003072 | 0.068848 | -0.0012477 | 0.00085443 | -0.0014356 | -0.0010787 | -0.0055799 | 0.0017345 | -46.875 | 71.228 | -51.6495 | 71.0999 | -50.4868 | -51.3382 | -50.7889 | -49.7086 | 71.2646 | -51.5991 | -51.059 | -51.2512 | -51.535 | -51.265 | -0.10986 | -0.027466 | -0.15564 | 1.0529 | 0.75073 | 0.20142 | 0.8606 | 0.31128 | -0.059509 | 0.009155 | -122.3145 | 0.28839 | 0.27466 | 0.004578 | 0.33417 | 0.064087 | 1.1627 | 122.7493 | 0.3479 | 0.54016 | 122.8775 | 122.8638 | 122.7676 | 122.8043 | -122.905 | -122.8546 | 122.6395 | 0.48065 | 4.6646 | 1.8311
3825.1719 | 123.0331 | -51.5213 | 71.2372 | -0.037689 | 0.0012625 | 0.061171 | 0.068618 | 0.00251 | 0.00069649 | 0.0037128 | 0.044434 | 0.0011023 | 0.00021363 | -0.0042126 | -0.0015061 | -0.0047253 | 0.0025891 | -46.6553 | 71.228 | -51.5945 | 71.1273 | -50.4364 | -51.4481 | -50.798 | -49.6994 | 71.2738 | -51.5625 | -51.0406 | -51.2512 | -51.535 | -51.2741 | -0.073242 | -0.009156 | -0.10986 | 1.0849 | 0.72327 | 0.073242 | 0.79651 | 0.14648 | -0.041199 | 0.036621 | -122.2778 | 0.27008 | 0.24719 | -0.013733 | 0.28839 | 0.027466 | 1.1581 | 122.7219 | 0.31128 | 0.52185 | 122.8226 | 122.8363 | 122.7493 | 122.7951 | -122.8317 | -122.7997 | 122.6486 | 0.48065 | 4.866 | 1.8219
3826.1719 | 122.937 | -51.5854 | 71.2509 | -0.11398 | 0.00083526 | 0.062025 | 0.0699 | -0.00026703 | 0.0015509 | 0.007558 | -0.056274 | 0.0021703 | 0.002777 | 0.002196 | -0.0025741 | -0.0042981 | 0.0013073 | -46.7331 | 71.2326 | -51.7136 | 70.9579 | -50.6561 | -51.5259 | -50.9445 | -49.8917 | 71.2738 | -51.6403 | -51.1322 | -51.4023 | -51.6953 | -51.3702 | -0.12817 | -0.018311 | -0.29297 | 0.92926 | 0.64087 | 0.059509 | 0.76904 | 0.18768 | -0.054932 | 0.022888 | -122.3831 | 0.18311 | 0.21515 | -0.10986 | 0.27008 | -0.054931 | 1.0574 | 122.6715 | 0.23804 | 0.50812 | 122.9462 | 122.9141 | 122.818 | 122.8592 | -122.9645 | -122.8912 | 122.5433 | 0.45319 | 4.8523 | 1.6937
3827.1719 | 122.9233 | -51.5396 | 71.2875 | -0.091095 | -0.0010873 | 0.061812 | 0.067123 | 0.0020828 | 0.00069649 | 0.0039264 | 0.013916 | -0.00039305 | 0.0019226 | 0.0019824 | -0.0032151 | -0.0049389 | 0.0021619 | -46.6415 | 71.2784 | -51.6312 | 71.0312 | -50.5508 | -51.4297 | -50.8484 | -49.8184 | 71.3058 | -51.5717 | -51.1185 | -51.3565 | -51.6357 | -51.3519 | -0.091553 | -0.009156 | -0.25635 | 0.98877 | 0.69122 | 0.10986 | 0.78278 | 0.20142 | -0.032043 | 0.01831 | -122.406 | 0.18311 | 0.18768 | -0.09613 | 0.21973 | -0.064087 | 1.0803 | 122.6624 | 0.21515 | 0.45319 | 122.9095 | 122.8775 | 122.818 | 122.8455 | -122.9187 | -122.8592 | 122.5708 | 0.42114 | 4.8981 | 1.7212
3828.1719 | 122.9599 | -51.535 | 71.2646 | -0.075836 | 0.0016899 | 0.061385 | 0.070968 | -0.0017624 | 0.0011237 | 0.0037128 | -0.056274 | 3.4148e-05 | 0.00021363 | 0.0019824 | -0.0042831 | -0.0047253 | 0.0032299 | -46.6415 | 71.2967 | -51.6403 | 71.0358 | -50.5188 | -51.4206 | -50.8942 | -49.7726 | 71.3196 | -51.5945 | -51.0864 | -51.3336 | -51.6586 | -51.3382 | -0.10529 | 0.032044 | -0.22888 | 1.0162 | 0.64087 | 0.11444 | 0.74616 | 0.21973 | -0.059509 | 0.054932 | -122.3511 | 0.20142 | 0.19684 | -0.1236 | 0.25635 | -0.064087 | 1.1215 | 122.6761 | 0.26093 | 0.50812 | 122.937 | 122.9141 | 122.8317 | 122.8546 | -122.905 | -122.8592 | 122.5708 | 0.44861 | 4.8935 | 1.7624
3829.1719 | 122.9828 | -51.535 | 71.2051 | -0.068207 | 0.00019446 | 0.060103 | 0.066054 | -5.343e-05 | 0.0039007 | 0.0049946 | 0.047485 | 0.00067495 | 0.00064083 | -0.0018628 | -0.0027877 | -0.0081433 | -0.00040166 | -46.6049 | 71.2646 | -51.5717 | 71.109 | -50.4181 | -51.3199 | -50.7477 | -49.649 | 71.3058 | -51.5442 | -51.091 | -50.9354 | -51.4938 | -51.3886 | -0.036621 | 0.059509 | -0.09613 | 1.1169 | 0.78735 | 0.21515 | 0.82397 | 0.25177 | -0.009155 | 0.10071 | -122.2961 | 0.59967 | 0.14648 | 0.041199 | 0.15564 | 0.050354 | 1.1536 | 122.6807 | 0.60883 | 0.45319 | 122.8363 | 122.85 | 122.7997 | 122.8409 | -122.7768 | -122.7493 | 122.644 | 0.44403 | 4.9301 | 1.886
3830.1719 | 123.1705 | -51.4755 | 71.3379 | -0.091095 | 0.0014761 | 0.061598 | 0.066482 | -0.0028304 | 0.0019781 | 0.003072 | 0.062744 | -0.00017945 | -0.00085457 | -0.0069898 | -0.0030013 | -0.0094251 | 0.00088014 | -46.582 | 71.2555 | -51.5579 | 71.1456 | -50.3998 | -51.3016 | -50.7339 | -49.6124 | 71.3058 | -51.503 | -50.9766 | -51.1871 | -51.4664 | -51.2054 | -0.082397 | -0.082398 | -0.19226 | 1.0757 | 0.74158 | 0.17395 | 0.82397 | 0.25635 | -0.027466 | -0.032044 | -122.3145 | 0.28839 | 0.27008 | 0.009155 | 0.29755 | 0.036621 | 1.1581 | 122.7036 | 0.31586 | 0.52643 | 122.8134 | 122.8088 | 122.731 | 122.7814 | -122.8958 | -122.8409 | 122.6212 | 0.49896 | 4.8935 | 1.8631
3831.1719 | 122.9828 | -51.5396 | 71.283 | -0.11398 | -0.0019417 | 0.062025 | 0.068404 | 0.0010148 | 0.00091009 | 0.0047808 | -0.050171 | 0.0019567 | 0.001709 | 0.0028368 | -0.0030013 | -0.0064343 | -0.0031787 | -46.6278 | 71.315 | -51.6495 | 71.0449 | -50.5234 | -51.416 | -50.8575 | -49.8596 | 71.3196 | -51.5945 | -51.0956 | -51.3153 | -51.5854 | -51.3016 | -0.10986 | 0.032043 | -0.23804 | 1.0162 | 0.68207 | 0.1236 | 0.79193 | 0.23346 | -0.054931 | 0.036621 | -122.3785 | 0.2243 | 0.23804 | -0.045776 | 0.29297 | 0.009155 | 1.1261 | 122.6944 | 0.27923 | 0.49896 | 122.9645 | 122.9141 | 122.8546 | 122.8592 | -122.9324 | -122.8775 | 122.5845 | 0.44403 | 4.9118 | 1.68
3832.1719 | 122.9645 | -51.4984 | 71.3516 | -0.091095 | 0.00040806 | 0.060957 | 0.068832 | 0.00037377 | 0.0011237 | 0.0047808 | -0.0043946 | -0.00017945 | 0.0025634 | 0.0028368 | -0.0012925 | -0.0070753 | 0.0010937 | -46.6507 | 71.3379 | -51.6037 | 71.0175 | -50.5646 | -51.4252 | -50.8575 | -49.8093 | 71.347 | -51.5579 | -51.1139 | -51.3382 | -51.5808 | -51.2146 | -0.10529 | -0.013733 | -0.33417 | 0.93384 | 0.64087 | 0.073242 | 0.74616 | 0.17853 | -0.059509 | -0.004578 | -122.4655 | 0.16022 | 0.28381 | -0.082398 | 0.34332 | -0.022889 | 1.0391 | 122.6212 | 0.21973 | 0.44403 | 122.9416 | 122.905 | 122.8363 | 122.8455 | -122.9553 | -122.9095 | 122.5159 | 0.38452 | 4.8477 | 1.6891
3833.1719 | 122.9919 | -51.5305 | 71.2784 | -0.068207 | 0.00083526 | 0.061598 | 0.069045 | 0.00016017 | 0.0011237 | 0.0032856 | -0.044067 | 0.0017431 | 0.0014954 | 0.001128 | -0.0017197 | -0.0045117 | 0.00066654 | -46.637 | 71.2921 | -51.6037 | 71.0403 | -50.528 | -51.4069 | -50.853 | -49.7269 | 71.3104 | -51.5579 | -51.1642 | -51.2009 | -51.5625 | -51.265 | -0.073242 | 0.013733 | -0.23804 | 1.0025 | 0.67749 | 0.1236 | 0.75073 | 0.19684 | -0.027465 | 0.032044 | -122.4426 | 0.32959 | 0.2655 | -0.032043 | 0.29297 | -0.004578 | 1.0757 | 122.644 | 0.35705 | 0.39368 | 122.8958 | 122.8683 | 122.8226 | 122.8409 | -122.8821 | -122.8363 | 122.5708 | 0.36621 | 4.8935 | 1.8036
3834.1719 | 122.9874 | -51.503 | 71.283 | -0.10635 | -1.9142e-05 | 0.061812 | 0.065414 | 0.0020828 | 0.0034735 | 0.0056354 | 0.047485 | 0.0015295 | 0.00085443 | -0.0014356 | -0.0015061 | -0.0045117 | 0.0017345 | -46.5912 | 71.2692 | -51.59 | 71.0953 | -50.4456 | -51.3245 | -50.7523 | -49.6948 | 71.2967 | -51.5579 | -51.0452 | -51.2512 | -51.5488 | -51.2558 | -0.086975 | -0.013733 | -0.18768 | 1.0574 | 0.75073 | 0.17853 | 0.83771 | 0.2655 | -0.054931 | 0.013733 | -122.3282 | 0.25177 | 0.24719 | -0.045776 | 0.30212 | 0.009155 | 1.1444 | 122.6852 | 0.3067 | 0.5127 | 122.8592 | 122.8546 | 122.7722 | 122.7997 | -122.8729 | -122.8409 | 122.5983 | 0.45776 | 4.9118 | 1.8082
3835.1719 | 122.9141 | -51.5305 | 71.3562 | -0.060578 | -0.00066014 | 0.060744 | 0.068618 | 0.0018692 | 0.00069649 | 0.0039264 | 0.0047608 | 0.0011023 | 0.0014954 | -0.002931 | -0.0023605 | -0.0045117 | -0.0061695 | -46.5958 | 71.3104 | -51.5854 | 71.0266 | -50.5325 | -51.4069 | -50.8072 | -49.7864 | 71.3562 | -51.535 | -51.091 | -51.3245 | -51.6037 | -51.3199 | -0.054931 | -0.045776 | -0.32959 | 0.99792 | 0.72327 | 0.1236 | 0.7782 | 0.17853 | -0.004577 | 0 | -122.4472 | 0.20599 | 0.21057 | -0.073242 | 0.21515 | -0.068665 | 1.0529 | 122.612 | 0.21057 | 0.44403 | 122.8958 | 122.8912 | 122.8409 | 122.8867 | -122.9416 | -122.8912 | 122.5571 | 0.43945 | 4.9347 | 1.7441
3836.1719 | 123.024 | -51.5167 | 71.2509 | -0.12161 | -0.0010873 | 0.061171 | 0.0699 | -0.0013352 | 0.0032599 | 0.0071308 | -0.010498 | 0.00088875 | 0.001068 | -0.00229 | -0.0019333 | -0.0045117 | -0.0042469 | -46.6095 | 71.2372 | -51.6037 | 71.0999 | -50.4776 | -51.3977 | -50.8118 | -49.6948 | 71.2921 | -51.5625 | -51.0544 | -51.0818 | -51.535 | -51.265 | -0.086975 | -0.013733 | -0.15106 | 1.0391 | 0.70496 | 0.11902 | 0.79193 | 0.20599 | -0.045776 | 0.041198 | -122.3053 | 0.43488 | 0.25177 | -0.01831 | 0.29755 | 0.027466 | 1.1261 | 122.7036 | 0.48065 | 0.50812 | 122.8409 | 122.8546 | 122.7539 | 122.8088 | -122.8546 | -122.8134 | 122.6166 | 0.46234 | 4.9072 | 1.8219
3837.1719 | 123.0011 | -51.5121 | 71.2692 | -0.037689 | -1.9142e-05 | 0.062666 | 0.067763 | 0.0018692 | 0.00026909 | 0.0049946 | 0.023071 | -0.00060665 | -0.0012818 | -0.00036738 | -0.0032151 | -0.0064343 | -0.00018806 | -46.5866 | 71.2967 | -51.5808 | 71.1273 | -50.4456 | -51.3153 | -50.7523 | -49.6948 | 71.315 | -51.5442 | -51.0086 | -51.2238 | -51.5076 | -51.2512 | -0.068665 | 0.027466 | -0.14191 | 1.0666 | 0.75989 | 0.19684 | 0.82855 | 0.2655 | -0.032043 | 0.045776 | -122.2778 | 0.28839 | 0.26093 | 0.004578 | 0.29297 | 0.036621 | 1.1353 | 122.7081 | 0.32043 | 0.53558 | 122.8775 | 122.8592 | 122.8088 | 122.8271 | -122.85 | -122.8134 | 122.6395 | 0.50354 | 4.9255 | 1.8173
3838.1719 | 122.9507 | -51.5396 | 71.3058 | -0.083466 | 0.0014761 | 0.062239 | 0.071395 | 0.0035782 | 0.0036871 | 0.0069172 | -0.068481 | 0.0021703 | 0.0012818 | 0.0036914 | -0.0021469 | -0.0060071 | -0.0021107 | -46.6141 | 71.3287 | -51.6083 | 71.0266 | -50.5417 | -51.4481 | -50.8759 | -49.7726 | 71.3379 | -51.5579 | -51.1047 | -51.3565 | -51.6357 | -51.329 | -0.068664 | 0.022888 | -0.27924 | 0.99792 | 0.66376 | 0.091553 | 0.73242 | 0.16022 | -0.01831 | 0.032044 | -122.4106 | 0.18311 | 0.21057 | -0.09613 | 0.22888 | -0.07782 | 1.0666 | 122.6349 | 0.20142 | 0.45319 | 122.937 | 122.8958 | 122.8683 | 122.8775 | -122.9141 | -122.8638 | 122.5662 | 0.43488 | 4.9255 | 1.767
3839.1719 | 122.9645 | -51.4984 | 71.3242 | -0.045319 | 0.00040806 | 0.061812 | 0.06755 | 0.0016556 | 0.00091009 | 0.0026446 | 0.032227 | 0.0021703 | 0.00021363 | -0.0031446 | -0.0021469 | -0.0053663 | -0.0025379 | -46.5637 | 71.2875 | -51.5671 | 71.0953 | -50.4639 | -51.3336 | -50.7751 | -49.7269 | 71.3654 | -51.5305 | -51.0452 | -51.2833 | -51.5762 | -51.3107 | -0.068665 | -0.036621 | -0.22888 | 1.0345 | 0.72327 | 0.16479 | 0.79193 | 0.23346 | -0.032044 | 0.041198 | -122.3694 | 0.21515 | 0.18768 | -0.07782 | 0.21973 | -0.045776 | 1.1032 | 122.6624 | 0.24719 | 0.48523 | 122.8546 | 122.8958 | 122.7859 | 122.8638 | -122.8912 | -122.8546 | 122.5937 | 0.45319 | 4.9347 | 1.7715
3840.1719 | 122.8683 | -51.4847 | 71.3379 | -0.10635 | 0.00040806 | 0.061171 | 0.067977 | -0.00048063 | 0.0024053 | 0.0047808 | -0.01355 | 3.4148e-05 | 0.0032044 | -0.00015378 | -0.0036423 | -0.0060071 | -0.0033923 | -46.6141 | 71.3287 | -51.5717 | 71.0495 | -50.5234 | -51.3977 | -50.8301 | -49.7818 | 71.3837 | -51.5533 | -51.091 | -51.0773 | -51.6815 | -51.3611 | -0.086975 | -0.009156 | -0.28839 | 0.9613 | 0.6546 | 0.086975 | 0.74158 | 0.17395 | -0.068665 | 0.045776 | -122.4289 | 0.40741 | 0.1236 | -0.19684 | 0.19226 | -0.12817 | 1.0483 | 122.6212 | 0.47607 | 0.46234 | 122.9004 | 122.937 | 122.8134 | 122.8683 | -122.9095 | -122.8912 | 122.5342 | 0.39368 | 4.8706 | 1.7029
3841.1719 | 122.9507 | -51.4755 | 71.402 | -0.098725 | -0.0025827 | 0.059248 | 0.068191 | -0.00026703 | -0.0010125 | 0.0032856 | -0.016602 | 0.0021703 | 0.001068 | -0.001222 | -0.0019333 | -0.0051527 | 0.00066654 | -46.5866 | 71.3562 | -51.5671 | 71.0403 | -50.5417 | -51.3977 | -50.8118 | -49.7635 | 71.3745 | -51.5488 | -51.0818 | -51.297 | -51.6037 | -51.4114 | -0.091553 | -0.045777 | -0.36163 | 0.93384 | 0.66376 | 0.07782 | 0.75531 | 0.16937 | -0.073242 | -0.027466 | -122.4838 | 0.17853 | 0.064087 | -0.12817 | 0.13733 | -0.054932 | 1.0254 | 122.6074 | 0.25177 | 0.46692 | 122.9233 | 122.9233 | 122.8317 | 122.85 | -122.9691 | -122.9507 | 122.5159 | 0.39368 | 4.8889 | 1.712
3842.1719 | 122.9736 | -51.5076 | 71.3333 | -0.075836 | 0.00083526 | 0.061812 | 0.067336 | -0.0015488 | 0.0032599 | 0.0034992 | 0.041382 | -0.00039305 | 2.8e-08 | -0.0018628 | -0.0021469 | -0.0055799 | 0.0010937 | -46.5408 | 71.3196 | -51.5671 | 71.1273 | -50.4227 | -51.3107 | -50.7523 | -49.6902 | 71.3242 | -51.503 | -51.0315 | -51.2421 | -51.5121 | -51.2466 | -0.05951 | -0.013733 | -0.20599 | 1.0849 | 0.75531 | 0.19684 | 0.81482 | 0.25635 | 0.004577 | -0.009155 | -122.3648 | 0.2655 | 0.26093 | -0.004578 | 0.25635 | -0.009155 | 1.1444 | 122.6944 | 0.26093 | 0.4715 | 122.8867 | 122.8271 | 122.8271 | 122.8317 | -122.9004 | -122.8363 | 122.6349 | 0.47607 | 4.9667 | 1.8173
3843.1719 | 122.9691 | -51.503 | 71.3196 | -0.083466 | 0.0012625 | 0.059462 | 0.070968 | 0.0016556 | 0.0021917 | 0.0037128 | -0.047119 | 0.0023839 | 0.0014954 | 0.0041186 | -0.0021469 | -0.0047253 | -0.00082886 | -46.5454 | 71.315 | -51.5945 | 71.0861 | -50.4822 | -51.3748 | -50.8163 | -49.6994 | 71.3516 | -51.5213 | -51.0361 | -51.2741 | -51.4984 | -51.3657 | -0.091552 | -0.004578 | -0.23346 | 1.0208 | 0.68665 | 0.12817 | 0.7782 | 0.21973 | -0.01831 | 0.032044 | -122.3557 | 0.22888 | 0.13733 | 0.004578 | 0.15564 | 0.022888 | 1.1124 | 122.6807 | 0.24719 | 0.48523 | 122.9095 | 122.8729 | 122.818 | 122.8546 | -122.9141 | -122.8409 | 122.5891 | 0.46692 | 4.9576 | 1.8036
3844.1719 | 122.9233 | -51.4664 | 71.347 | -0.060578 | 0.0016899 | 0.062025 | 0.067763 | 0.0012284 | 5.5488e-05 | 0.0052082 | 0.047485 | 0.0013159 | 0.001068 | -0.001222 | -0.0025741 | -0.0064343 | 2.554e-05 | -46.55 | 71.347 | -51.5488 | 71.0724 | -50.4959 | -51.3519 | -50.7751 | -49.7543 | 71.3699 | -51.5305 | -51.0635 | -51.2878 | -51.5533 | -51.2878 | -0.082397 | 0 | -0.27466 | 0.97046 | 0.69122 | 0.11444 | 0.77362 | 0.19684 | -0.064087 | 0.022888 | -122.4106 | 0.17853 | 0.17853 | -0.086975 | 0.24262 | -0.022888 | 1.0529 | 122.6212 | 0.24262 | 0.46692 | 122.8958 | 122.9004 | 122.8134 | 122.8363 | -122.8958 | -122.8775 | 122.5388 | 0.40283 | 4.9164 | 1.712
3845.1719 | 122.9004 | -51.4938 | 71.3791 | -0.091095 | -0.00066014 | 0.061385 | 0.067336 | 0.006569 | 0.00069649 | 0.0043536 | 0.013916 | 3.4148e-05 | 0.001068 | -0.00079478 | -0.0038559 | -0.0064343 | 0.0040845 | -46.5363 | 71.3654 | -51.5579 | 71.0953 | -50.4639 | -51.3611 | -50.7843 | -49.704 | 71.3837 | -51.5076 | -51.0452 | -51.2833 | -51.5762 | -51.2924 | -0.064087 | -0.013733 | -0.28381 | 1.03 | 0.70953 | 0.13275 | 0.77362 | 0.19684 | -0.013733 | 0.004578 | -122.4243 | 0.21057 | 0.20142 | -0.082398 | 0.21515 | -0.068665 | 1.0941 | 122.6532 | 0.2243 | 0.46234 | 122.9233 | 122.8912 | 122.8592 | 122.8775 | -122.937 | -122.8867 | 122.5891 | 0.44861 | 4.9576 | 1.7899
3846.1719 | 123.0286 | -51.4297 | 71.347 | -0.12161 | -1.9142e-05 | 0.06288 | 0.067977 | 0.00058737 | 0.0026191 | 0.0043536 | 0.010864 | 3.4148e-05 | 2.8e-08 | 0.003905 | -0.0034287 | -0.0062207 | -0.0029651 | -46.4996 | 71.3333 | -51.5121 | 71.1731 | -50.3677 | -51.265 | -50.6973 | -49.6078 | 71.3745 | -51.4572 | -50.9766 | -51.1688 | -51.4755 | -51.1917 | -0.082397 | -0.013733 | -0.17395 | 1.062 | 0.73242 | 0.16479 | 0.81482 | 0.24719 | -0.027465 | 0.027466 | -122.3236 | 0.26093 | 0.23804 | -0.045776 | 0.2655 | -0.018311 | 1.1444 | 122.6852 | 0.28839 | 0.48065 | 122.8455 | 122.8317 | 122.7631 | 122.8043 | -122.8592 | -122.8043 | 122.6028 | 0.45319 | 4.9301 | 1.8219
3847.1719 | 122.9553 | -51.4893 | 71.3516 | -0.014801 | -0.00087374 | 0.060957 | 0.070327 | 0.0010148 | 0.0021917 | 0.0052082 | -0.037964 | 0.0030249 | 0.0012818 | -0.0014356 | -0.0032151 | -0.0068615 | 2.554e-05 | -46.5637 | 71.3654 | -51.5533 | 71.0678 | -50.5005 | -51.3748 | -50.8301 | -49.7589 | 71.3974 | -51.5259 | -51.0452 | -51.2695 | -51.5579 | -51.2741 | -0.064087 | 0.013732 | -0.28381 | 0.98877 | 0.65918 | 0.11444 | 0.72327 | 0.17853 | -0.036621 | 0.045776 | -122.3969 | 0.21973 | 0.21515 | -0.068664 | 0.25177 | -0.032043 | 1.0529 | 122.6212 | 0.25635 | 0.48065 | 122.9187 | 122.9233 | 122.8546 | 122.8867 | -122.905 | -122.8775 | 122.5571 | 0.44403 | 4.9255 | 1.7303
3848.1719 | 122.8775 | -51.4801 | 71.3379 | -0.13687 | 0.0016899 | 0.061812 | 0.070113 | 0.00080117 | 0.0024053 | 0.003072 | -0.074585 | 0.00088875 | -0.00021357 | 0.0030506 | -0.00086511 | -0.0057935 | 0.0068615 | -46.5546 | 71.3791 | -51.5717 | 71.0312 | -50.5417 | -51.4343 | -50.8759 | -49.791 | 71.402 | -51.5488 | -51.0773 | -51.3336 | -51.6495 | -51.3062 | -0.091552 | 0.041198 | -0.3067 | 0.93842 | 0.60425 | 0.045777 | 0.6958 | 0.13733 | -0.068664 | 0.064087 | -122.4152 | 0.14648 | 0.17395 | -0.16937 | 0.24262 | -0.10071 | 1.03 | 122.6028 | 0.21515 | 0.4715 | 122.9507 | 122.9507 | 122.8592 | 122.8821 | -122.9095 | -122.8867 | 122.5113 | 0.40283 | 4.9255 | 1.6891
3849.1719 | 122.9324 | -51.4709 | 71.3242 | -0.083466 | 0.0023307 | 0.062025 | 0.06755 | -5.343e-05 | 0.0015509 | 0.005849 | 0.041382 | 0.0015295 | -0.00085457 | 0.0034778 | -0.00043791 | -0.0049389 | -0.0021107 | -46.5088 | 71.3562 | -51.5488 | 71.1227 | -50.4318 | -51.3016 | -50.7385 | -49.6857 | 71.3882 | -51.5121 | -51.0223 | -51.2741 | -51.535 | -51.2558 | -0.07782 | 0.032043 | -0.20142 | 1.0391 | 0.73242 | 0.16937 | 0.81024 | 0.24719 | -0.041199 | 0.064087 | -122.3465 | 0.19684 | 0.21515 | -0.064087 | 0.25635 | -0.022888 | 1.1169 | 122.6715 | 0.23804 | 0.48981 | 122.905 | 122.9004 | 122.8271 | 122.8592 | -122.8729 | -122.8363 | 122.5937 | 0.44861 | 4.9622 | 1.7853
3850.1719 | 123.024 | -51.4297 | 71.3379 | -0.11398 | 0.00062166 | 0.061385 | 0.06755 | 0.00080117 | 0.0011237 | 0.0020038 | 0.056641 | -0.0021021 | 0.00064083 | 0.002196 | -0.0044967 | -0.0062207 | -0.0031787 | -46.5408 | 71.3242 | -51.5442 | 71.1731 | -50.3677 | -51.2741 | -50.7019 | -49.6078 | 71.347 | -51.503 | -50.9491 | -51.1597 | -51.4526 | -51.178 | -0.11444 | -0.013733 | -0.16479 | 1.062 | 0.72785 | 0.15564 | 0.84229 | 0.27008 | -0.073242 | 0.009155 | -122.287 | 0.27008 | 0.25177 | -0.022888 | 0.32501 | 0.050354 | 1.1765 | 122.7173 | 0.34332 | 0.55389 | 122.8683 | 122.85 | 122.7539 | 122.7768 | -122.8821 | -122.8409 | 122.6028 | 0.48065 | 4.8889 | 1.8219
3851.1719 | 122.8729 | -51.4755 | 71.3791 | -0.052948 | -1.9142e-05 | 0.060957 | 0.069045 | -0.00048063 | 0.0041143 | 0.0045672 | 0.010864 | 0.0025975 | 0.0023498 | 0.0079638 | -0.0036423 | -0.0034437 | 0.00088014 | -46.5637 | 71.3699 | -51.5533 | 71.077 | -50.473 | -51.3794 | -50.798 | -49.736 | 71.4203 | -51.4847 | -51.1185 | -51.1002 | -51.3886 | -51.2466 | -0.07782 | -0.009155 | -0.30212 | 1.0025 | 0.67749 | 0.09613 | 0.75531 | 0.17395 | -0.009155 | 0.041199 | -122.4976 | 0.37537 | 0.22888 | 0.086975 | 0.23804 | 0.09613 | 1.0803 | 122.6303 | 0.38452 | 0.36621 | 122.9233 | 122.905 | 122.8455 | 122.8958 | -122.9324 | -122.8638 | 122.5525 | 0.35706 | 4.9118 | 1.7395
3852.1719 | 122.9553 | -51.4755 | 71.3654 | -0.045319 | -0.00023294 | 0.060103 | 0.067763 | -0.001976 | 0.0026191 | 0.005849 | -0.028809 | 0.0019567 | 0.0012818 | 0.0024096 | -0.0042831 | -0.0060071 | 0.0010937 | -46.5591 | 71.4066 | -51.5762 | 71.0724 | -50.4776 | -51.3611 | -50.8026 | -49.7589 | 71.4111 | -51.4938 | -51.0452 | -51.2512 | -51.5671 | -51.2787 | -0.10071 | 0.041199 | -0.29297 | 0.99792 | 0.67291 | 0.11444 | 0.77362 | 0.21515 | -0.01831 | 0.045777 | -122.4106 | 0.2243 | 0.19684 | -0.091553 | 0.21515 | -0.073243 | 1.0986 | 122.6486 | 0.24261 | 0.44861 | 122.9828 | 122.905 | 122.8821 | 122.8867 | -122.9416 | -122.8592 | 122.5479 | 0.4303 | 4.9164 | 1.7166
3853.1719 | 122.9233 | -51.4755 | 71.3608 | 0.023346 | -0.0010873 | 0.061385 | 0.070113 | -0.0043258 | 0.0015509 | 0.0045672 | -0.03186 | 0.00067495 | 0.0038452 | 0.0043322 | -0.0032151 | -0.0070753 | 2.554e-05 | -46.5912 | 71.4294 | -51.5717 | 71.0724 | -50.4822 | -51.3382 | -50.8072 | -49.7498 | 71.4294 | -51.5076 | -51.0452 | -51.2558 | -51.5625 | -51.2741 | -0.09613 | 0.068664 | -0.28839 | 0.99335 | 0.66833 | 0.13733 | 0.76447 | 0.23346 | -0.032043 | 0.068664 | -122.406 | 0.21973 | 0.20142 | -0.086975 | 0.23346 | -0.054932 | 1.0895 | 122.644 | 0.25177 | 0.46234 | 123.0011 | 122.937 | 122.905 | 122.905 | -122.9324 | -122.8683 | 122.5479 | 0.4303 | 4.8843 | 1.7258
3854.1719 | 122.9416 | -51.4526 | 71.402 | -0.052948 | -0.00044654 | 0.06053 | 0.067123 | 0.00037377 | -0.00015811 | 0.0020038 | 0.013916 | 0.0028113 | 0.0025634 | -0.0050672 | -0.0012925 | -0.0085705 | 2.554e-05 | -46.5042 | 71.3654 | -51.5579 | 71.0953 | -50.4639 | -51.3474 | -50.7614 | -49.704 | 71.4066 | -51.4801 | -51.0406 | -51.2695 | -51.5442 | -51.265 | -0.10528 | -0.036622 | -0.3067 | 0.98877 | 0.69122 | 0.10529 | 0.79651 | 0.21057 | -0.027466 | 0.004577 | -122.4426 | 0.18311 | 0.18768 | -0.091552 | 0.21515 | -0.064086 | 1.0941 | 122.6532 | 0.21057 | 0.43945 | 122.9233 | 122.8867 | 122.818 | 122.8592 | -122.9599 | -122.8821 | 122.5479 | 0.41199 | 4.9484 | 1.7487
3855.1719 | 122.9233 | -51.4664 | 71.3791 | -0.083466 | 0.00019446 | 0.063734 | 0.067977 | -0.0015488 | 0.0032599 | 0.0056354 | 0.044434 | -0.00017945 | 0.0029906 | 0.0019824 | -0.0012925 | -0.0051527 | -0.00082886 | -46.4996 | 71.3379 | -51.5167 | 71.1227 | -50.4272 | -51.3062 | -50.7385 | -49.6994 | 71.3928 | -51.4847 | -51.0269 | -51.265 | -51.5167 | -51.2558 | -0.050354 | -0.041198 | -0.25635 | 1.0391 | 0.72784 | 0.16022 | 0.7782 | 0.21057 | -0.01831 | 0.013733 | -122.406 | 0.20142 | 0.21057 | -0.050354 | 0.22888 | -0.032044 | 1.0895 | 122.6395 | 0.21973 | 0.45776 | 122.8546 | 122.8775 | 122.8043 | 122.8592 | -122.8958 | -122.8638 | 122.5891 | 0.43945 | 4.9667 | 1.767
3856.1719 | 122.9599 | -51.4664 | 71.3928 | -0.083466 | 0.00040806 | 0.060103 | 0.069686 | 0.0029374 | -0.00079891 | 0.0052082 | -0.01355 | 0.0017431 | 0.0023498 | 0.0019824 | -0.0032151 | -0.0062207 | -0.0025379 | -46.5271 | 71.3882 | -51.5442 | 71.0861 | -50.4684 | -51.3519 | -50.8026 | -49.7177 | 71.4386 | -51.4801 | -51.0178 | -51.2466 | -51.5533 | -51.2375 | -0.077819 | -0.004577 | -0.3067 | 0.99792 | 0.66376 | 0.11444 | 0.74158 | 0.19226 | -0.013733 | 0.045777 | -122.4106 | 0.21973 | 0.22888 | -0.086975 | 0.24262 | -0.073242 | 1.0757 | 122.6303 | 0.23346 | 0.46234 | 122.9324 | 122.9187 | 122.8546 | 122.905 | -122.937 | -122.8729 | 122.5525 | 0.44861 | 4.9393 | 1.7487
3857.1719 | 123.0469 | -51.4252 | 71.3333 | 0.084381 | -0.0010873 | 0.063521 | 0.067336 | -0.0015488 | 0.0015509 | 0.0049946 | 0.065796 | -0.00082025 | 0.00085443 | -0.00229 | -0.0021469 | -0.0068615 | 0.00023934 | -46.6965 | 71.3425 | -51.5259 | 71.1868 | -50.3448 | -51.2329 | -50.6699 | -49.5712 | 71.3654 | -51.4801 | -50.9216 | -51.1322 | -51.4481 | -51.1826 | -0.10071 | 0.009155 | -0.14648 | 1.0803 | 0.75531 | 0.19226 | 0.85602 | 0.29297 | -0.054932 | 0.032043 | -122.2549 | 0.29297 | 0.24262 | -0.022888 | 0.29755 | 0.032044 | 1.181 | 122.7127 | 0.3479 | 0.55847 | 122.8683 | 122.8455 | 122.7676 | 122.7905 | -122.8592 | -122.8134 | 122.612 | 0.50354 | 4.7287 | 1.8539
3858.1719 | 122.9141 | -51.4709 | 71.3745 | -0.045319 | -1.9142e-05 | 0.059889 | 0.069045 | -0.0017624 | 0.0039007 | 0.00414 | -0.019653 | -0.00017945 | 0.0014954 | 0.002196 | -0.0042831 | -0.0049389 | -0.0012561 | -46.376 | 71.4569 | -51.5076 | 71.0632 | -50.4684 | -51.3657 | -50.798 | -49.7131 | 71.434 | -51.4664 | -51.0223 | -51.2375 | -51.5305 | -51.2421 | -0.036621 | 0.082397 | -0.31128 | 1.0025 | 0.67291 | 0.10529 | 0.70953 | 0.14191 | 0.004577 | 0.059509 | -122.3969 | 0.23346 | 0.22888 | -0.05951 | 0.22431 | -0.064087 | 1.0391 | 122.5708 | 0.22888 | 0.44403 | 122.9645 | 122.9004 | 122.9279 | 122.905 | -122.8821 | -122.8409 | 122.5342 | 0.44861 | 5.0949 | 1.7578
3859.1719 | 122.937 | -51.4481 | 71.3745 | -0.098725 | 0.0012625 | 0.061812 | 0.065627 | -0.00069423 | 0.0011237 | 0.0049946 | 0.026123 | -0.00017945 | 0.0012818 | 0.00070062 | -0.00086511 | -0.0070753 | -0.0018971 | -46.4767 | 71.402 | -51.5076 | 71.1273 | -50.3998 | -51.2741 | -50.7385 | -49.6765 | 71.4111 | -51.4664 | -51.0132 | -51.2329 | -51.5213 | -51.2558 | -0.059509 | 0.027466 | -0.24719 | 1.0483 | 0.70953 | 0.17395 | 0.76904 | 0.23346 | -0.018311 | 0.036621 | -122.3877 | 0.21515 | 0.19226 | -0.073242 | 0.21057 | -0.054931 | 1.1078 | 122.6349 | 0.23346 | 0.45319 | 122.9095 | 122.8775 | 122.85 | 122.8592 | -122.8821 | -122.8409 | 122.5754 | 0.43487 | 4.9713 | 1.7715
3860.1719 | 122.9233 | -51.4526 | 71.4066 | -0.098725 | 0.0012625 | 0.061171 | 0.068618 | -0.00026703 | 0.0019781 | 0.003072 | -0.019653 | 0.0040929 | 0.0014954 | 0.0054004 | -0.0025741 | -0.0040845 | -0.0029651 | -46.5317 | 71.3837 | -51.5259 | 71.0999 | -50.441 | -51.3519 | -50.7751 | -49.7086 | 71.4294 | -51.4755 | -51.0315 | -51.2375 | -51.59 | -51.2833 | -0.073242 | -0.022888 | -0.3067 | 1.0117 | 0.67749 | 0.10071 | 0.75073 | 0.17395 | -0.022888 | 0.022888 | -122.438 | 0.21515 | 0.16937 | -0.13733 | 0.19226 | -0.11444 | 1.0849 | 122.6257 | 0.23804 | 0.44403 | 122.9095 | 122.905 | 122.8363 | 122.8821 | -122.9324 | -122.8821 | 122.5525 | 0.42114 | 4.921 | 1.7441
3861.1719 | 122.9141 | -51.4526 | 71.3974 | -0.068207 | 0.0012625 | 0.061598 | 0.0699 | 0.00016017 | 0.00069649 | 0.0032856 | -0.01355 | 0.0017431 | 0.001709 | 0.0028368 | -0.0025741 | -0.0047253 | -0.00061526 | -46.5363 | 71.4157 | -51.535 | 71.0953 | -50.4501 | -51.3428 | -50.7797 | -49.6857 | 71.4478 | -51.4847 | -51.004 | -51.2329 | -51.5488 | -51.2375 | -0.082397 | 0.01831 | -0.30212 | 1.0025 | 0.67291 | 0.10986 | 0.75531 | 0.19226 | -0.032043 | 0.050354 | -122.4014 | 0.21973 | 0.21515 | -0.09613 | 0.24719 | -0.064087 | 1.0849 | 122.6303 | 0.25177 | 0.48065 | 122.9507 | 122.9324 | 122.8683 | 122.9004 | -122.9324 | -122.8821 | 122.5479 | 0.44861 | 4.9164 | 1.767
3862.1719 | 123.0469 | -51.4069 | 71.3837 | -0.11398 | -0.00066014 | 0.062025 | 0.066054 | -0.00090783 | 0.0032599 | 0.0045672 | -0.074585 | 0.0011023 | -0.00085457 | -0.0010084 | -0.00065151 | -0.0068615 | 0.0034435 | -46.4264 | 71.4066 | -51.4709 | 71.228 | -50.1709 | -50.8438 | -50.647 | -49.4659 | 71.3791 | -51.4572 | -50.9079 | -51.0864 | -51.3886 | -51.1368 | -0.064087 | 0.022888 | -0.15564 | 1.236 | 0.75989 | 0.56305 | 0.82397 | 0.62714 | -0.050354 | -0.004578 | -122.2916 | 0.32043 | 0.27008 | 0.01831 | 0.32043 | 0.068664 | 1.3 | 122.699 | 0.37079 | 0.54932 | 122.8775 | 122.8363 | 122.8134 | 122.7859 | -122.8546 | -122.8409 | 122.6349 | 0.49896 | 4.9805 | 1.9409
3863.1719 | 123.0286 | -51.4069 | 71.3882 | -0.075836 | 0.00062166 | 0.060957 | 0.065627 | -0.0021896 | 0.0032599 | 0.0054218 | 0.029175 | -0.00039305 | 0.0025634 | 0.001128 | -0.0036423 | -0.0042981 | -0.00082886 | -46.4355 | 71.3745 | -51.503 | 71.2006 | -50.3265 | -51.2283 | -50.6516 | -49.5346 | 71.4111 | -51.4343 | -50.9171 | -51.1276 | -51.4206 | -51.1551 | -0.096131 | -0.013733 | -0.18768 | 1.0803 | 0.75531 | 0.17853 | 0.85144 | 0.27466 | -0.027466 | 0.022888 | -122.3053 | 0.27923 | 0.25177 | -0.013733 | 0.27924 | 0.013733 | 1.1765 | 122.7036 | 0.3067 | 0.51727 | 122.8775 | 122.8455 | 122.7814 | 122.818 | -122.8912 | -122.8226 | 122.6074 | 0.48981 | 4.9713 | 1.8723
3864.1719 | 123.0972 | -51.384 | 71.3928 | -0.060578 | 0.00019446 | 0.060316 | 0.067123 | -0.0028304 | 0.0013373 | 0.0047808 | 0.032227 | 0.00067495 | 0.00085443 | -0.0025036 | -0.0034287 | -0.0062207 | -0.0018971 | -46.4264 | 71.3608 | -51.5121 | 71.2372 | -50.2762 | -51.1963 | -50.6378 | -49.4934 | 71.402 | -51.4343 | -50.8804 | -51.0956 | -51.3748 | -51.1459 | -0.12817 | -0.032043 | -0.15564 | 1.1078 | 0.74616 | 0.18768 | 0.87433 | 0.31586 | -0.050354 | 0.009156 | -122.2733 | 0.28839 | 0.23804 | 0.009155 | 0.28839 | 0.059509 | 1.236 | 122.7493 | 0.33874 | 0.55389 | 122.8729 | 122.8363 | 122.7448 | 122.7859 | -122.905 | -122.8271 | 122.6212 | 0.50354 | 4.9576 | 1.8906
3865.1719 | 123.0423 | -51.3977 | 71.3608 | -0.12924 | 0.00083526 | 0.06523 | 0.069686 | 0.0022964 | 0.0011237 | 0.0039264 | 0.026123 | 0.00024775 | 0.00042723 | -0.0018628 | -0.0023605 | -0.0070753 | -0.0029651 | -46.4401 | 71.347 | -51.4664 | 71.2555 | -50.354 | -51.2695 | -50.6516 | -49.5346 | 71.3882 | -51.4526 | -50.9079 | -51.123 | -51.4114 | -51.1414 | -0.068665 | -0.013733 | -0.10529 | 1.0437 | 0.74616 | 0.12817 | 0.81482 | 0.19684 | -0.054932 | 0.027466 | -122.2687 | 0.27466 | 0.25635 | -0.013733 | 0.31128 | 0.041199 | 1.1124 | 122.7219 | 0.32959 | 0.54474 | 122.8134 | 122.8409 | 122.7448 | 122.7859 | -122.8271 | -122.8134 | 122.6532 | 0.48981 | 4.9576 | 1.8631
3866.1719 | 123.056 | -51.3931 | 71.3837 | -0.083466 | 0.0010489 | 0.059462 | 0.068618 | 0.0022964 | 0.0011237 | 0.00414 | -0.086792 | 0.0049475 | -0.00021357 | -0.0018628 | -0.0038559 | -0.0051527 | -0.0025379 | -46.3852 | 71.3516 | -51.5076 | 71.228 | -50.3723 | -50.7843 | -50.4684 | -49.5026 | 71.3425 | -51.4297 | -50.9033 | -51.0818 | -51.3519 | -51.1093 | -0.11444 | -0.032043 | -0.15564 | 1.0208 | 0.92468 | 0.60883 | 1.0391 | 0.72327 | -0.036622 | -0.041199 | -122.287 | 0.31128 | 0.28381 | 0.041198 | 0.32044 | 0.07782 | 1.1353 | 122.7356 | 0.3479 | 0.52643 | 122.8592 | 122.7722 | 122.7448 | 122.7356 | -122.8912 | -122.8134 | 122.6212 | 0.48981 | 5.0079 | 1.8906
3867.1719 | 123.0103 | -51.3886 | 71.4111 | -0.045319 | -0.0013009 | 0.061171 | 0.067977 | 0.0016556 | 0.00069649 | 0.0045672 | 0.013916 | 3.4148e-05 | 0.0025634 | -0.0016492 | -0.0036423 | -0.0064343 | -0.0010425 | -46.4035 | 71.3928 | -51.4938 | 71.2234 | -50.3036 | -51.2146 | -50.6516 | -49.5392 | 71.4066 | -51.4389 | -50.9171 | -51.1276 | -51.4069 | -51.123 | -0.10528 | -0.018311 | -0.18768 | 1.0849 | 0.737 | 0.17395 | 0.84228 | 0.27923 | -0.050354 | -0.004578 | -122.3282 | 0.26093 | 0.2655 | -0.01831 | 0.31586 | 0.032044 | 1.1902 | 122.7173 | 0.31128 | 0.52185 | 122.8867 | 122.8455 | 122.7814 | 122.7951 | -122.905 | -122.85 | 122.612 | 0.4715 | 4.985 | 1.8494
3868.1719 | 123.0423 | -51.4069 | 71.3928 | -0.12161 | -0.00044654 | 0.063948 | 0.069686 | -0.0026168 | 0.00069649 | 0.007558 | 0.026123 | 0.0025975 | -0.0014954 | -0.00058098 | -0.0021469 | -0.0049389 | -0.0021107 | -46.4218 | 71.3608 | -51.4847 | 71.2372 | -50.2808 | -51.2146 | -50.6424 | -49.5346 | 71.4294 | -51.4572 | -50.8987 | -51.123 | -51.3931 | -51.1276 | -0.07782 | -0.032043 | -0.15564 | 1.1261 | 0.76447 | 0.19226 | 0.84228 | 0.27008 | -0.050354 | 0.036621 | -122.2916 | 0.28381 | 0.27923 | 0.013733 | 0.32959 | 0.064087 | 1.2039 | 122.7219 | 0.33417 | 0.55847 | 122.8455 | 122.8867 | 122.7676 | 122.8363 | -122.8775 | -122.85 | 122.644 | 0.50812 | 4.985 | 1.8723
3869.1719 | 123.056 | -51.3611 | 71.3928 | -0.052948 | 0.0014761 | 0.064589 | 0.06755 | 0.00058737 | 0.00091009 | 0.0071308 | 0.010864 | -0.0029567 | 0.00021363 | -0.0044262 | -0.0010787 | -0.0047253 | -0.0016833 | -46.5363 | 71.3608 | -51.4893 | 71.2418 | -50.2716 | -51.1734 | -50.6287 | -49.5026 | 71.4523 | -51.4114 | -50.8667 | -51.0864 | -51.3748 | -51.1322 | -0.12817 | -0.032043 | -0.15106 | 1.0895 | 0.73242 | 0.18768 | 0.8606 | 0.31586 | -0.050354 | 0.05951 | -122.2595 | 0.27466 | 0.22888 | -0.013733 | 0.27924 | 0.036621 | 1.2177 | 122.731 | 0.32501 | 0.54474 | 122.85 | 122.8638 | 122.7219 | 122.8134 | -122.8821 | -122.8043 | 122.6028 | 0.49439 | 4.8248 | 1.8585
3870.1719 | 123.0789 | -51.3702 | 71.3928 | -0.068207 | -0.00087374 | 0.06053 | 0.070754 | 0.00080117 | 0.0026191 | 0.0069172 | 0.03833 | 0.0011023 | -0.00021357 | -0.00229 | -0.0036423 | -0.0070753 | -0.0014697 | -46.3943 | 71.3837 | -51.4847 | 71.2418 | -50.2853 | -51.2054 | -50.6241 | -49.4797 | 71.4157 | -51.4206 | -50.8713 | -51.0635 | -51.3748 | -51.1093 | -0.11444 | -0.009155 | -0.15106 | 1.0849 | 0.74615 | 0.16479 | 0.8606 | 0.27924 | -0.050354 | 0.022888 | -122.2641 | 0.3067 | 0.26093 | -0.004578 | 0.31128 | 0.045776 | 1.1993 | 122.7264 | 0.35705 | 0.54932 | 122.8683 | 122.8363 | 122.7539 | 122.7859 | -122.8775 | -122.8134 | 122.612 | 0.49896 | 4.9759 | 1.8906
3871.1719 | 123.0743 | -51.3519 | 71.3791 | -0.091095 | 0.0012625 | 0.061385 | 0.06755 | 0.001442 | 0.0024053 | 0.002431 | 0.047485 | 0.00024775 | 0.0025634 | -0.00036738 | -0.0040695 | -0.0045117 | 0.0013073 | -46.4172 | 71.3791 | -51.4801 | 71.2372 | -50.2899 | -51.21 | -50.6332 | -49.5163 | 71.4111 | -51.3977 | -50.853 | -51.0864 | -51.3794 | -51.1139 | -0.12817 | 0 | -0.14191 | 1.062 | 0.71869 | 0.14191 | 0.84686 | 0.27008 | -0.045776 | 0.032044 | -122.2321 | 0.2655 | 0.23804 | -0.027466 | 0.28381 | 0.01831 | 1.1902 | 122.7173 | 0.31128 | 0.54474 | 122.8592 | 122.8088 | 122.731 | 122.7631 | -122.8592 | -122.7768 | 122.5891 | 0.49896 | 4.9347 | 1.8356
3872.1719 | 123.0606 | -51.4069 | 71.3562 | -0.075836 | -0.00087374 | 0.063094 | 0.067763 | -5.343e-05 | 0.0021917 | 0.0056354 | 0.03833 | 0.00024775 | 0.00064083 | 0.0013416 | -0.0062057 | -0.0070753 | 0.0040845 | -46.3852 | 71.3928 | -51.4526 | 71.2784 | -50.235 | -51.1734 | -50.6012 | -49.4705 | 71.3974 | -51.4023 | -50.9308 | -51.3153 | -51.3474 | -51.059 | -0.045777 | 0.036621 | -0.07782 | 1.1719 | 0.80566 | 0.23346 | 0.85144 | 0.27924 | 0.004577 | 0.041199 | -122.287 | 0.091552 | 0.3479 | 0.059509 | 0.34332 | 0.054932 | 1.2177 | 122.731 | 0.086975 | 0.4715 | 122.8455 | 122.7997 | 122.7997 | 122.8043 | -122.8088 | -122.7585 | 122.6852 | 0.47607 | 5.0217 | 1.9363
3873.1719 | 122.8912 | -51.4343 | 71.4294 | -0.03006 | -1.9142e-05 | 0.061812 | 0.068191 | 0.00058737 | 0.0019781 | 0.0052082 | -0.03186 | 0.0013159 | 0.00021363 | 0.0015552 | -0.0023605 | -0.0062207 | 0.0053661 | -46.4355 | 71.4569 | -51.4984 | 71.1456 | -50.386 | -51.2924 | -50.7248 | -49.6399 | 71.5073 | -51.4252 | -51.0361 | -51.2512 | -51.4755 | -51.2009 | -0.064087 | 0.027466 | -0.28381 | 1.0483 | 0.70953 | 0.14191 | 0.77362 | 0.20599 | 0.009155 | 0.07782 | -122.4655 | 0.1831 | 0.23346 | -0.041199 | 0.2243 | -0.050354 | 1.1124 | 122.644 | 0.17395 | 0.3891 | 122.9553 | 122.9324 | 122.8912 | 122.9416 | -122.9279 | -122.8546 | 122.58 | 0.39825 | 4.9988 | 1.7944
3874.1719 | 123.0377 | -51.3794 | 71.3974 | -0.068207 | -0.00066014 | 0.058821 | 0.068404 | -0.0026168 | -0.00037171 | 0.00414 | 0.023071 | 0.0011023 | 0.00064083 | -0.0018628 | -0.0030013 | -0.0049389 | -0.0040333 | -46.1472 | 71.4523 | -51.4389 | 71.2051 | -50.2991 | -51.2009 | -50.6561 | -49.4843 | 71.4432 | -51.4343 | -50.8621 | -51.091 | -51.3931 | -51.0956 | -0.059509 | 0.054932 | -0.19226 | 1.0803 | 0.72327 | 0.17853 | 0.78278 | 0.23804 | -0.054931 | 0.045776 | -122.2595 | 0.28839 | 0.28381 | -0.013732 | 0.33874 | 0.041199 | 1.1398 | 122.644 | 0.34332 | 0.5722 | 122.8912 | 122.8775 | 122.8317 | 122.8226 | -122.8363 | -122.8317 | 122.5845 | 0.51727 | 5.2322 | 1.8951
3875.1719 | 122.9965 | -51.3977 | 71.4157 | -0.037689 | 0.0014761 | 0.059035 | 0.067763 | -0.0015488 | -0.00058531 | 0.005849 | -0.0074462 | -0.00039305 | 0.001068 | 0.00027342 | -0.0030013 | -0.0064343 | -0.0040333 | -46.3669 | 71.3928 | -51.4664 | 71.2372 | -50.2853 | -51.2146 | -50.6378 | -49.5255 | 71.4432 | -51.4206 | -50.9079 | -51.123 | -51.4114 | -51.1368 | -0.068665 | -0.022888 | -0.17853 | 1.1124 | 0.75989 | 0.18311 | 0.82855 | 0.25177 | -0.022888 | 0.027466 | -122.3236 | 0.27466 | 0.26093 | -0.013733 | 0.28381 | 0.009155 | 1.181 | 122.7036 | 0.29755 | 0.51269 | 122.8592 | 122.8638 | 122.7905 | 122.8409 | -122.8821 | -122.8363 | 122.6349 | 0.48981 | 5.0308 | 1.8723
3876.1719 | 122.9279 | -51.3886 | 71.4523 | -0.075836 | -0.00044654 | 0.060957 | 0.067763 | -0.004753 | 5.5488e-05 | 0.0049946 | -0.010498 | 0.0025975 | 0.0012818 | 0.0013416 | -0.0023605 | -0.0077161 | -0.0018971 | -46.3852 | 71.434 | -51.4709 | 71.196 | -50.3448 | -51.2787 | -50.6973 | -49.5895 | 71.4752 | -51.4252 | -50.9491 | -51.1871 | -51.4801 | -51.2009 | -0.082397 | -0.018311 | -0.25635 | 1.0437 | 0.69122 | 0.10986 | 0.77362 | 0.19226 | -0.036621 | 0.022888 | -122.4014 | 0.20142 | 0.18768 | -0.091553 | 0.2243 | -0.054932 | 1.1261 | 122.6669 | 0.23804 | 0.47607 | 122.905 | 122.9004 | 122.8226 | 122.8638 | -122.9233 | -122.8775 | 122.5845 | 0.43945 | 5.0034 | 1.799
3877.1719 | 123.0515 | -51.384 | 71.4111 | -0.15976 | 0.00083526 | 0.061171 | 0.069045 | 0.00080117 | 0.0011237 | 0.0084124 | 0.02002 | 0.00046135 | 0.001068 | -0.0031446 | -0.0034287 | -0.0064343 | -0.0051013 | -46.3806 | 71.3882 | -51.4526 | 71.2418 | -50.2991 | -51.2054 | -50.6195 | -49.5209 | 71.4203 | -51.4252 | -50.8438 | -51.0681 | -51.3657 | -51.1139 | -0.068665 | -0.022888 | -0.16937 | 1.0849 | 0.76447 | 0.17853 | 0.83313 | 0.24719 | -0.041199 | 0.009155 | -122.2549 | 0.31586 | 0.27008 | 0.01831 | 0.31128 | 0.059509 | 1.1536 | 122.6944 | 0.35706 | 0.58136 | 122.8409 | 122.8455 | 122.7722 | 122.8043 | -122.8638 | -122.8363 | 122.6257 | 0.54016 | 5.0034 | 1.8631
3878.1719 | 123.0423 | -51.3748 | 71.402 | -0.091095 | -0.0017281 | 0.06053 | 0.066695 | -0.0015488 | 0.00048269 | 0.0049946 | 0.0078126 | 0.00024775 | 0.00085443 | 0.00070062 | -0.0025741 | -0.0051527 | 0.0019483 | -46.3715 | 71.4111 | -51.4618 | 71.2372 | -50.2899 | -51.2192 | -50.647 | -49.5255 | 71.4203 | -51.416 | -50.8621 | -51.0773 | -51.3611 | -51.1002 | -0.086975 | 0.009155 | -0.16479 | 1.0849 | 0.72784 | 0.15564 | 0.81482 | 0.24262 | -0.041199 | 0.01831 | -122.2641 | 0.29755 | 0.27466 | 0.013733 | 0.31586 | 0.054932 | 1.1719 | 122.699 | 0.33874 | 0.55389 | 122.8729 | 122.8363 | 122.786 | 122.7951 | -122.8638 | -122.818 | 122.612 | 0.5127 | 5.0034 | 1.8494
3879.1719 | 123.0789 | -51.329 | 71.434 | -0.083466 | 0.00083526 | 0.059889 | 0.068832 | -0.0045394 | 0.0024053 | 0.0047808 | 0.013916 | 0.00024775 | 0.00021363 | -0.0020764 | -0.0017197 | -0.0045117 | -0.0010425 | -46.3577 | 71.4066 | -51.4801 | 71.2692 | -50.2167 | -51.1734 | -50.5966 | -49.4339 | 71.4294 | -51.416 | -50.8118 | -51.0544 | -51.3428 | -51.0864 | -0.15106 | -0.027466 | -0.16479 | 1.1124 | 0.73242 | 0.15564 | 0.88348 | 0.3067 | -0.086975 | -0.004578 | -122.2458 | 0.27466 | 0.24261 | -0.013732 | 0.32959 | 0.073243 | 1.2634 | 122.7493 | 0.36163 | 0.60425 | 122.8867 | 122.8455 | 122.7356 | 122.7585 | -122.9141 | -122.85 | 122.5983 | 0.51727 | 4.9713 | 1.8951
3880.1719 | 123.0652 | -51.3519 | 71.3974 | -0.098725 | 0.0016899 | 0.061171 | 0.067763 | 0.0016556 | 0.0021917 | 0.0043536 | 0.0078126 | -0.0010339 | 0.0019226 | -0.0014356 | -0.0032151 | -0.0066479 | 0.00066654 | -46.3394 | 71.3791 | -51.4572 | 71.2692 | -50.2075 | -51.1597 | -50.6058 | -49.4614 | 71.434 | -51.4114 | -50.8347 | -51.0361 | -51.3153 | -51.0681 | -0.10529 | -0.018311 | -0.12817 | 1.1444 | 0.74616 | 0.19226 | 0.85144 | 0.29755 | -0.059509 | 0.036621 | -122.2321 | 0.31586 | 0.28381 | 0.036621 | 0.34332 | 0.09613 | 1.2497 | 122.7264 | 0.37537 | 0.57678 | 122.8363 | 122.8455 | 122.731 | 122.7859 | -122.8546 | -122.8088 | 122.6212 | 0.51727 | 5.0125 | 1.8906
3881.1719 | 123.0377 | -51.3428 | 71.4157 | -0.068207 | 0.00062166 | 0.061385 | 0.071609 | 0.0022964 | -0.00058531 | 0.0052082 | -0.025757 | -0.00039305 | -0.00085457 | 0.0045458 | -0.0030013 | -0.0057935 | 0.00045294 | -46.3303 | 71.4386 | -51.4252 | 71.315 | -50.2533 | -51.2375 | -50.6058 | -49.4614 | 71.4478 | -51.416 | -50.8392 | -51.0635 | -51.3565 | -51.1002 | -0.082398 | 0.022889 | -0.10071 | 1.0895 | 0.737 | 0.10529 | 0.8194 | 0.18768 | -0.073243 | 0.032044 | -122.2549 | 0.27923 | 0.24261 | -0.013733 | 0.31586 | 0.05951 | 1.1719 | 122.7402 | 0.35248 | 0.57678 | 122.8638 | 122.8638 | 122.7814 | 122.7905 | -122.8409 | -122.8317 | 122.6578 | 0.50354 | 5.0125 | 1.8814
3882.1719 | 123.0377 | -51.3565 | 71.4249 | -0.091095 | -0.00044654 | 0.059676 | 0.068832 | 0.0022964 | 0.0058233 | 0.0043536 | 0.02002 | -0.00039305 | 0.0012818 | 0.00070062 | -0.0034287 | -0.0066479 | -0.0014697 | -46.3028 | 71.4111 | -51.4435 | 71.4706 | -50.2441 | -51.5717 | -50.6973 | -49.5163 | 71.4157 | -51.3977 | -50.8392 | -51.0681 | -51.3382 | -51.0956 | -0.086975 | -0.013733 | 0.045776 | 1.1124 | 0.65918 | -0.21515 | 0.74615 | -0.12817 | -0.041199 | -0.009156 | -122.2641 | 0.28839 | 0.26093 | 0.01831 | 0.30212 | 0.059509 | 1.1993 | 122.9141 | 0.32959 | 0.55847 | 122.8546 | 122.8134 | 122.7676 | 122.7722 | -122.8683 | -122.8226 | 122.8271 | 0.51727 | 5.0537 | 1.8402
3883.1719 | 123.0423 | -51.3886 | 71.4386 | -0.098725 | 0.0014761 | 0.061598 | 0.066695 | 0.00058737 | 0.00048269 | 0.0020038 | 0.071899 | 0.0021703 | -0.0012818 | -0.0065626 | -0.0021469 | -0.0047253 | -0.0027515 | -46.2891 | 71.434 | -51.4435 | 71.2738 | -50.2167 | -51.1505 | -50.3494 | -49.7177 | 71.4661 | -51.4343 | -50.8438 | -51.0773 | -51.3474 | -51.0864 | -0.054931 | -0.004578 | -0.16479 | 1.1719 | 1.0391 | 0.23804 | 1.0941 | 0.29297 | -0.045776 | 0.027465 | -122.2824 | 0.31128 | 0.30212 | 0.041199 | 0.3479 | 0.086975 | 1.2268 | 122.7173 | 0.35705 | 0.59051 | 122.8775 | 122.9004 | 122.8226 | 122.8546 | -122.8821 | -122.8729 | 122.6624 | 0.54474 | 5.0995 | 1.6708
3884.1719 | 123.0652 | -51.3611 | 71.434 | -0.068207 | -0.00023294 | 0.061598 | 0.069045 | -0.0011214 | 0.0019781 | 0.0047808 | 0.013916 | -0.00017945 | 0.001068 | -0.0048536 | -0.0025741 | -0.0049389 | 2.554e-05 | -46.3348 | 71.4294 | -51.4618 | 71.2601 | -50.2441 | -51.1734 | -50.6104 | -49.4751 | 71.4294 | -51.4069 | -50.8347 | -51.0361 | -51.329 | -51.0864 | -0.10071 | -0.004578 | -0.17395 | 1.1169 | 0.75073 | 0.18768 | 0.85144 | 0.28839 | -0.045776 | -0.004578 | -122.2687 | 0.32501 | 0.27466 | 0.032043 | 0.32043 | 0.077819 | 1.2177 | 122.7219 | 0.37079 | 0.5722 | 122.8912 | 122.8363 | 122.7905 | 122.7905 | -122.8958 | -122.8409 | 122.6212 | 0.52643 | 5.0262 | 1.886
3885.1719 | 123.0423 | -51.3428 | 71.4432 | -0.083466 | -0.00023294 | 0.061385 | 0.069259 | -0.001976 | -0.00058531 | 0.00414 | 0.023071 | 0.0017431 | 0.0019226 | 0.0036914 | -0.0040695 | -0.0062207 | -0.0014697 | -46.3257 | 71.434 | -51.4252 | 71.2509 | -50.2533 | -51.1917 | -50.6058 | -49.4705 | 71.4432 | -51.3977 | -50.8163 | -51.0544 | -51.3382 | -51.0727 | -0.082398 | -0.009155 | -0.19226 | 1.0895 | 0.737 | 0.15106 | 0.8194 | 0.23346 | -0.054932 | 0 | -122.2595 | 0.28839 | 0.27008 | 0.004577 | 0.32501 | 0.059509 | 1.1719 | 122.6761 | 0.34332 | 0.58136 | 122.8592 | 122.8409 | 122.7768 | 122.7859 | -122.8683 | -122.8409 | 122.5937 | 0.52643 | 5.0171 | 1.8723
3886.1719 | 122.9782 | -51.3336 | 71.434 | -0.060578 | 0.00083526 | 0.061385 | 0.065841 | -5.343e-05 | 0.0011237 | 0.0034992 | 0.0078126 | -0.00017945 | 2.8e-08 | 0.00048702 | -0.0036423 | -0.0049389 | -0.0031787 | -46.2799 | 71.4478 | -51.4069 | 71.3196 | -50.1801 | -51.1093 | -50.5463 | -49.3835 | 71.4615 | -51.3794 | -50.8118 | -50.7385 | -51.4343 | -51.21 | -0.073242 | 0.013733 | -0.11444 | 1.1536 | 0.78735 | 0.2243 | 0.8606 | 0.29755 | -0.045777 | 0.027466 | -122.2458 | 0.59509 | 0.1236 | -0.10071 | 0.16937 | -0.054931 | 1.2268 | 122.7264 | 0.64087 | 0.56763 | 122.8546 | 122.8409 | 122.7814 | 122.7951 | -122.8409 | -122.8134 | 122.6532 | 0.52185 | 5.0537 | 1.9501
3887.1719 | 123.1659 | -51.297 | 71.521 | -0.11398 | -1.9142e-05 | 0.060744 | 0.066909 | 0.0050736 | 0.00048269 | 0.0045672 | 0.016968 | 0.0030249 | 0.0025634 | -0.0025036 | -0.0025741 | -0.0070753 | -0.0023243 | -46.2662 | 71.4111 | -51.4023 | 71.3013 | -50.1572 | -51.1276 | -50.5646 | -49.4064 | 71.4752 | -51.3428 | -50.7889 | -51.0223 | -51.2924 | -51.0956 | -0.10529 | -0.10986 | -0.21973 | 1.1398 | 0.73242 | 0.16937 | 0.83771 | 0.27466 | -0.045776 | -0.045776 | -122.3099 | 0.27466 | 0.20142 | 0.004578 | 0.24719 | 0.050354 | 1.2451 | 122.7036 | 0.32043 | 0.55389 | 122.8134 | 122.818 | 122.7081 | 122.7722 | -122.9233 | -122.8638 | 122.5983 | 0.50812 | 5.0308 | 1.8906
3888.1719 | 123.0377 | -51.329 | 71.4615 | -0.23605 | 0.0025443 | 0.061171 | 0.06755 | 0.00251 | 0.0019781 | 0.0028582 | -0.010498 | 0.0011023 | 0.00085443 | -0.0033582 | -0.0010787 | -0.0053663 | 0.0017345 | -46.1975 | 71.434 | -51.4252 | 71.3196 | -50.1801 | -51.123 | -50.592 | -49.4202 | 71.5073 | -51.3748 | -50.798 | -51.0315 | -51.3245 | -51.0681 | -0.09613 | -0.027466 | -0.14191 | 1.149 | 0.737 | 0.20599 | 0.83313 | 0.30212 | -0.045776 | 0.045776 | -122.2595 | 0.29755 | 0.26093 | 0.004578 | 0.3067 | 0.050354 | 1.2451 | 122.7448 | 0.34332 | 0.57678 | 122.8592 | 122.8821 | 122.7631 | 122.8363 | -122.8867 | -122.8363 | 122.6486 | 0.53101 | 5.1315 | 1.9089
3889.1719 | 123.0286 | -51.3382 | 71.4111 | 0.12253 | -0.00044654 | 0.064375 | 0.070968 | -0.003685 | 0.0017645 | 0.0043536 | 0.0078126 | -0.00039305 | 0.0025634 | -0.0025036 | -0.0010787 | -0.0055799 | -0.0016833 | -46.4905 | 71.4386 | -51.4343 | 71.2875 | -50.2075 | -51.1185 | -50.5829 | -49.4385 | 71.4752 | -51.3886 | -50.8163 | -51.0406 | -51.3245 | -51.0681 | -0.09613 | 0.027466 | -0.1236 | 1.1307 | 0.75531 | 0.21973 | 0.85144 | 0.31586 | -0.050354 | 0.064087 | -122.2275 | 0.29755 | 0.27008 | 0.013733 | 0.32044 | 0.064087 | 1.2268 | 122.7219 | 0.3479 | 0.57221 | 122.8729 | 122.8638 | 122.7768 | 122.8134 | -122.8455 | -122.7997 | 122.6257 | 0.52185 | 4.8477 | 1.8997
3890.1719 | 123.0515 | -51.3199 | 71.4478 | -0.068207 | 0.0023307 | 0.059248 | 0.065627 | -0.0017624 | 0.00069649 | 0.0049946 | -0.016602 | -0.0012477 | -0.00042717 | -0.00058098 | -0.0044967 | -0.0092115 | -0.0016833 | -46.051 | 71.5302 | -51.3657 | 71.3013 | -50.1389 | -51.1505 | -50.5646 | -49.411 | 71.489 | -51.3565 | -50.8072 | -51.0132 | -51.3153 | -51.0498 | -0.045777 | 0.082397 | -0.14648 | 1.181 | 0.75531 | 0.16937 | 0.80109 | 0.21515 | -0.036621 | 0.041199 | -122.2549 | 0.3067 | 0.27008 | 0.004577 | 0.3067 | 0.041198 | 1.2268 | 122.6669 | 0.34332 | 0.54932 | 122.8958 | 122.8455 | 122.85 | 122.8088 | -122.8134 | -122.8043 | 122.6212 | 0.5127 | 5.2689 | 1.9089
3891.1719 | 123.0469 | -51.3336 | 71.4386 | -0.075836 | -0.00087374 | 0.061598 | 0.066695 | 0.0027238 | 0.0017645 | 0.0032856 | 0.010864 | 0.0013159 | -0.00021357 | -0.0016492 | -0.0036423 | -0.0047253 | -0.0029651 | -46.2387 | 71.4569 | -51.3977 | 71.3287 | -50.1617 | -51.1185 | -50.5371 | -49.3881 | 71.4752 | -51.3382 | -50.7523 | -50.9811 | -51.2741 | -51.0361 | -0.064087 | 0.01831 | -0.10986 | 1.1719 | 0.79651 | 0.21515 | 0.8606 | 0.27924 | -0.004578 | 0.036621 | -122.1909 | 0.35248 | 0.29755 | 0.059509 | 0.30212 | 0.064087 | 1.236 | 122.7264 | 0.35706 | 0.58594 | 122.8546 | 122.8134 | 122.7905 | 122.8088 | -122.8363 | -122.7768 | 122.6624 | 0.58136 | 5.0949 | 1.9455
3892.1719 | 122.9782 | -51.3611 | 71.4935 | -0.10635 | 0.0016899 | 0.061812 | 0.070327 | 0.0018692 | 0.0026191 | 0.0047808 | -0.098999 | -0.0012477 | 0.00064083 | 0.0051868 | -0.0032151 | -0.0038709 | -0.0031787 | -46.2708 | 71.4615 | -51.4526 | 71.228 | -50.2625 | -51.2329 | -50.6699 | -49.5209 | 71.5393 | -51.384 | -50.8255 | -51.1047 | -51.4069 | -51.1185 | -0.091553 | -0.032043 | -0.2655 | 1.0986 | 0.69122 | 0.12817 | 0.78278 | 0.21973 | -0.022888 | 0.045777 | -122.319 | 0.25635 | 0.24262 | -0.045776 | 0.2655 | -0.022888 | 1.1902 | 122.6807 | 0.27924 | 0.55847 | 122.9141 | 122.9233 | 122.8226 | 122.9004 | -122.9462 | -122.8775 | 122.5891 | 0.53558 | 5.0903 | 1.8402
3893.1719 | 123.0011 | -51.329 | 71.4615 | -0.10635 | 0.0010489 | 0.062239 | 0.066482 | -0.0034714 | 0.0021917 | 0.0037128 | 0.0078126 | 0.00024775 | 0.00042723 | -0.001222 | -0.0015061 | -0.0057935 | -0.00061526 | -46.0144 | 71.5347 | -51.3748 | 71.2784 | -50.1755 | -51.123 | -50.5829 | -49.4202 | 71.4844 | -51.3748 | -50.8118 | -51.0178 | -51.3107 | -51.0544 | -0.045776 | 0.073242 | -0.18311 | 1.1536 | 0.74615 | 0.20599 | 0.79193 | 0.25177 | -0.045776 | 0.022888 | -122.2733 | 0.31128 | 0.27466 | 0.018311 | 0.32044 | 0.064087 | 1.1993 | 122.6532 | 0.35706 | 0.56305 | 122.9095 | 122.8592 | 122.8638 | 122.8134 | -122.8363 | -122.8363 | 122.6074 | 0.51727 | 5.3146 | 1.9089
3894.1719 | 123.0331 | -51.3336 | 71.4798 | -0.19028 | 0.00083526 | 0.060103 | 0.067336 | -0.0032578 | 0.0021917 | 0.0011494 | 0.001709 | -0.0023157 | 0.00042723 | 0.002196 | -0.0015061 | -0.0055799 | -0.0029651 | -46.344 | 71.4157 | -51.4114 | 71.283 | -50.1938 | -51.1093 | -50.5646 | -49.411 | 71.489 | -51.3336 | -50.798 | -51.0132 | -51.3245 | -51.0544 | -0.07782 | -0.064087 | -0.19684 | 1.1398 | 0.76904 | 0.2243 | 0.84686 | 0.30212 | 0 | 0.009156 | -122.2778 | 0.32043 | 0.27924 | 0.009155 | 0.27924 | 0.009155 | 1.2177 | 122.6944 | 0.32043 | 0.53558 | 122.8271 | 122.8226 | 122.7493 | 122.8226 | -122.8912 | -122.8134 | 122.6166 | 0.53558 | 4.9896 | 1.9226
3895.1719 | 122.9599 | -51.3245 | 71.489 | -0.068207 | -0.00044654 | 0.061385 | 0.069686 | -0.0011214 | 0.0011237 | 0.005849 | -0.0043946 | 0.0023839 | 0.00085443 | 0.002196 | -0.0021469 | -0.0036573 | -0.00018806 | -46.2158 | 71.489 | -51.4114 | 71.2646 | -50.2258 | -51.1642 | -50.6058 | -49.4843 | 71.5393 | -51.3702 | -50.8575 | -51.0956 | -51.3886 | -51.123 | -0.086975 | 0 | -0.22431 | 1.0986 | 0.71869 | 0.16022 | 0.80566 | 0.24719 | -0.045776 | 0.050354 | -122.3465 | 0.22888 | 0.20142 | -0.064087 | 0.24719 | -0.018311 | 1.1856 | 122.6761 | 0.27466 | 0.5127 | 122.9004 | 122.9095 | 122.8134 | 122.8638 | -122.9004 | -122.8592 | 122.5891 | 0.46692 | 5.1086 | 1.8402
3896.1719 | 122.937 | -51.3245 | 71.5027 | -0.083466 | -0.0017281 | 0.063734 | 0.069259 | -0.0026168 | 0.0017645 | 0.0054218 | -0.016602 | 0.00046135 | 0.00021363 | -0.00464 | -0.0032151 | -0.0070753 | -0.0012561 | -46.1975 | 71.5073 | -51.3977 | 71.3013 | -50.2075 | -51.1642 | -50.5737 | -49.4522 | 71.5668 | -51.3565 | -50.853 | -51.0681 | -51.3519 | -51.091 | -0.073242 | 0.004577 | -0.20142 | 1.1169 | 0.75073 | 0.16022 | 0.82398 | 0.23346 | -0.032043 | 0.064086 | -122.3557 | 0.25635 | 0.23346 | -0.027466 | 0.2655 | 0.004577 | 1.1902 | 122.699 | 0.28839 | 0.50354 | 122.905 | 122.9233 | 122.8317 | 122.8912 | -122.9004 | -122.8592 | 122.6257 | 0.4715 | 5.127 | 1.8723
3897.1719 | 122.937 | -51.3702 | 71.4523 | -0.15976 | -0.00044654 | 0.062239 | 0.071181 | -0.0013352 | 0.00026909 | 0.0032856 | -0.089844 | 0.0036657 | 0.0012818 | -0.003999 | -0.0012925 | -0.0066479 | 0.00023934 | -46.0739 | 71.4661 | -51.4297 | 71.1868 | -50.3174 | -51.329 | -50.7431 | -49.6078 | 71.4981 | -51.4069 | -50.9171 | -51.1642 | -51.4847 | -51.1505 | -0.05951 | 0.013732 | -0.2655 | 1.0529 | 0.62714 | 0.041198 | 0.68665 | 0.10071 | -0.036621 | 0.045776 | -122.3694 | 0.20599 | 0.21973 | -0.11444 | 0.25635 | -0.07782 | 1.1124 | 122.6166 | 0.24261 | 0.48981 | 122.8958 | 122.905 | 122.8363 | 122.8683 | -122.8821 | -122.8592 | 122.5571 | 0.45319 | 5.2963 | 1.7624
3898.1719 | 123.0194 | -51.2787 | 71.5073 | -0.068207 | 0.00083526 | 0.060957 | 0.065841 | -0.0017624 | 0.0030463 | 0.0039264 | 0.023071 | 0.00046135 | 0.001068 | 0.00070062 | -0.0023605 | -0.0072889 | 0.0030163 | -46.1472 | 71.5164 | -51.3702 | 71.3287 | -50.1205 | -51.0956 | -50.5188 | -49.3881 | 71.5256 | -51.3336 | -50.7797 | -50.9903 | -51.265 | -51.0223 | -0.091552 | 0.009155 | -0.17853 | 1.1581 | 0.75989 | 0.18311 | 0.85144 | 0.27466 | -0.054931 | 0.018311 | -122.287 | 0.28839 | 0.25635 | 0.013733 | 0.31128 | 0.068664 | 1.2497 | 122.699 | 0.34332 | 0.55389 | 122.8867 | 122.8592 | 122.7951 | 122.8043 | -122.8775 | -122.8409 | 122.6074 | 0.49896 | 5.1315 | 1.8906
3899.1719 | 123.0148 | -51.3016 | 71.4935 | -0.083466 | -0.0010873 | 0.062239 | 0.069259 | 0.0010148 | 0.0028327 | 0.005849 | 0.029175 | 0.00067495 | 0.0021362 | -0.0054944 | -0.00022431 | -0.0051527 | -0.00018806 | -46.1792 | 71.489 | -51.3657 | 71.315 | -50.1617 | -51.1139 | -50.56 | -49.4247 | 71.521 | -51.3428 | -50.7935 | -51.0178 | -51.297 | -51.0315 | -0.064087 | -0.004577 | -0.17853 | 1.1398 | 0.74158 | 0.18768 | 0.80566 | 0.25177 | -0.041198 | 0.027466 | -122.287 | 0.28381 | 0.27008 | 0.004578 | 0.31128 | 0.045776 | 1.2039 | 122.6807 | 0.32501 | 0.54932 | 122.8546 | 122.8638 | 122.7905 | 122.8226 | -122.8592 | -122.8363 | 122.6166 | 0.50812 | 5.1224 | 1.8768
3900.1719 | 122.9462 | -51.329 | 71.5073 | -0.083466 | -0.0010873 | 0.062239 | 0.068832 | -0.00048063 | 0.00069649 | 0.0028582 | -0.016602 | -0.00017945 | 0.0040588 | -0.0033582 | -0.0023605 | -0.0072889 | 0.00088014 | -46.2158 | 71.5256 | -51.3977 | 71.2555 | -50.2304 | -51.1551 | -50.6241 | -49.5209 | 71.5485 | -51.3611 | -50.8713 | -51.0864 | -51.4023 | -51.1276 | -0.068664 | 0.018311 | -0.25177 | 1.0986 | 0.70496 | 0.17395 | 0.77362 | 0.24262 | -0.032043 | 0.041199 | -122.3785 | 0.24261 | 0.20142 | -0.073242 | 0.23346 | -0.041199 | 1.1673 | 122.6532 | 0.27466 | 0.48981 | 122.9233 | 122.9095 | 122.8546 | 122.8775 | -122.905 | -122.8683 | 122.5845 | 0.45776 | 5.1132 | 1.8082
3901.1719 | 122.9324 | -51.2878 | 71.5347 | -0.12161 | -0.0036507 | 0.060957 | 0.071181 | -5.343e-05 | 0.0034735 | 0.0064898 | -0.022705 | 0.00046135 | 0.00085443 | -0.002931 | -0.0023605 | -0.0066479 | -0.0023243 | -46.2433 | 71.5942 | -51.3611 | 71.228 | -50.2625 | -51.2238 | -50.6287 | -49.53 | 71.5988 | -51.3428 | -50.8484 | -51.1002 | -51.3748 | -51.1093 | -0.073242 | 0.059509 | -0.3067 | 1.0254 | 0.65918 | 0.064087 | 0.73242 | 0.13733 | -0.054931 | 0.064087 | -122.3831 | 0.18768 | 0.17853 | -0.086975 | 0.23346 | -0.032044 | 1.0986 | 122.5891 | 0.24261 | 0.49438 | 122.9553 | 122.9416 | 122.8821 | 122.8867 | -122.8958 | -122.8775 | 122.5159 | 0.43945 | 5.0446 | 1.7578
3902.1719 | 122.9645 | -51.3153 | 71.489 | -0.10635 | 0.00040806 | 0.062666 | 0.070541 | 0.00080117 | 0.0013373 | 0.0043536 | -0.056274 | 0.0025975 | 0.0025634 | -0.0016492 | -0.0023605 | -0.0070753 | -0.0029651 | -46.2341 | 71.5073 | -51.4343 | 71.2051 | -50.2808 | -51.2741 | -50.6836 | -49.53 | 71.5485 | -51.3702 | -50.8438 | -51.123 | -51.416 | -51.0956 | -0.11902 | 0.01831 | -0.28381 | 1.0345 | 0.63171 | 0.041199 | 0.75073 | 0.16022 | -0.054931 | 0.059509 | -122.3328 | 0.19226 | 0.21973 | -0.10071 | 0.27466 | -0.045777 | 1.1536 | 122.6395 | 0.24719 | 0.52643 | 122.9416 | 122.9187 | 122.8226 | 122.8638 | -122.9233 | -122.8592 | 122.5204 | 0.4715 | 5.0812 | 1.7853
3903.1719 | 122.9507 | -51.2878 | 71.5347 | -0.091095 | 0.00083526 | 0.061385 | 0.067336 | 0.00037377 | 0.0024053 | 0.0047808 | -0.010498 | 0.0013159 | 0.0014954 | -0.002931 | -1.0706e-05 | -0.0053663 | 0.00066654 | -46.3074 | 71.5759 | -51.3794 | 71.2509 | -50.2487 | -51.1734 | -50.6195 | -49.5071 | 71.5668 | -51.3474 | -50.8392 | -51.0773 | -51.3794 | -51.0956 | -0.091553 | 0.041199 | -0.28381 | 1.0391 | 0.66833 | 0.11444 | 0.75989 | 0.20599 | -0.059509 | 0.032043 | -122.374 | 0.21057 | 0.19226 | -0.091553 | 0.25177 | -0.032044 | 1.1307 | 122.6303 | 0.27008 | 0.50812 | 122.9553 | 122.9141 | 122.8638 | 122.8546 | -122.9141 | -122.8821 | 122.5388 | 0.44861 | 4.9805 | 1.7807
3904.1719 | 122.9233 | -51.297 | 71.553 | -0.12924 | 0.00083526 | 0.061812 | 0.070113 | 0.0010148 | 0.00091009 | 0.0060626 | -0.016602 | 0.0019567 | 0.0019226 | 0.0017688 | -0.00065151 | -0.0032301 | -0.00082886 | -46.1563 | 71.5393 | -51.3977 | 71.2418 | -50.2304 | -51.1688 | -50.6287 | -49.5163 | 71.5988 | -51.329 | -50.8301 | -51.0544 | -51.3748 | -51.0956 | -0.10071 | -0.013733 | -0.31128 | 1.0666 | 0.66833 | 0.12817 | 0.76904 | 0.22888 | -0.032044 | 0.045776 | -122.3831 | 0.24262 | 0.20142 | -0.07782 | 0.23346 | -0.045776 | 1.1673 | 122.6395 | 0.27466 | 0.49896 | 122.937 | 122.9279 | 122.8363 | 122.8958 | -122.9507 | -122.8821 | 122.5388 | 0.46692 | 5.1407 | 1.7807
3905.1719 | 122.9233 | -51.2878 | 71.5439 | -0.068207 | -0.0010873 | 0.060957 | 0.067977 | -0.0024032 | 0.0017645 | 0.00414 | -0.0074462 | -0.00017945 | 0.0023498 | -0.0033582 | -0.0017197 | -0.0047253 | 0.00088014 | -46.1792 | 71.5393 | -51.3565 | 71.2509 | -50.2213 | -51.1871 | -50.6241 | -49.4934 | 71.5805 | -51.3474 | -50.8438 | -51.0818 | -51.3657 | -51.1276 | -0.068664 | -0.004577 | -0.29297 | 1.0666 | 0.66376 | 0.10071 | 0.73242 | 0.16937 | -0.059509 | 0.036621 | -122.3877 | 0.20599 | 0.16022 | -0.07782 | 0.21973 | -0.018311 | 1.1353 | 122.6074 | 0.2655 | 0.50354 | 122.8958 | 122.9279 | 122.8271 | 122.8683 | -122.9004 | -122.8912 | 122.5388 | 0.44403 | 5.1086 | 1.7944
3906.1719 | 122.905 | -51.2833 | 71.5393 | -0.091095 | -1.9142e-05 | 0.062025 | 0.068404 | 0.00016017 | -0.00079891 | 0.0047808 | -0.0043946 | 0.0013159 | 0.002777 | -0.0025036 | -0.0019333 | -0.0068615 | -0.0012561 | -46.17 | 71.5485 | -51.3702 | 71.2601 | -50.2304 | -51.1734 | -50.6058 | -49.4751 | 71.5622 | -51.329 | -50.8438 | -51.0635 | -51.3657 | -51.091 | -0.086975 | 0.009155 | -0.27924 | 1.0529 | 0.67749 | 0.10986 | 0.76447 | 0.19684 | -0.045777 | 0.022888 | -122.3831 | 0.21973 | 0.19226 | -0.082398 | 0.23804 | -0.036621 | 1.1398 | 122.6303 | 0.2655 | 0.48523 | 122.9187 | 122.8912 | 122.8317 | 122.8455 | -122.9095 | -122.8683 | 122.5433 | 0.43945 | 5.1132 | 1.8082
3907.1719 | 123.0194 | -51.2695 | 71.4844 | -0.11398 | -0.00044654 | 0.063094 | 0.067977 | 0.00080117 | 0.0017645 | 0.0054218 | -0.0013428 | -0.00060665 | -0.00021357 | 0.0049732 | -0.0019333 | -0.0049389 | -0.0016833 | -46.106 | 71.489 | -51.3611 | 71.2646 | -50.3998 | -51.1047 | -50.4456 | -49.3927 | 71.5073 | -51.3245 | -50.7706 | -50.9949 | -51.297 | -50.9995 | -0.091553 | 0.004578 | -0.21973 | 0.86975 | 0.82397 | 0.16479 | 0.91553 | 0.25635 | -0.054932 | 0.022888 | -122.2549 | 0.27466 | 0.27008 | -0.027466 | 0.32501 | 0.027466 | 0.9613 | 122.6257 | 0.32959 | 0.55389 | 122.85 | 122.8317 | 122.7585 | 122.7768 | -122.8455 | -122.8088 | 122.5342 | 0.49896 | 5.1636 | 1.8768
3908.1719 | 122.9416 | -51.297 | 71.5485 | -0.045319 | 0.0023307 | 0.057539 | 0.066909 | -0.0038986 | 0.0011237 | 0.0060626 | -0.01355 | 0.0013159 | 0.0046996 | -0.0037854 | -0.0023605 | -0.0051527 | 0.0010937 | -46.0648 | 71.6171 | -51.3245 | 71.2372 | -50.2213 | -51.178 | -50.6149 | -49.5071 | 71.5897 | -51.3153 | -50.8163 | -51.0635 | -51.3611 | -51.0681 | -0.027466 | 0.068664 | -0.31128 | 1.0757 | 0.68207 | 0.11902 | 0.70953 | 0.14648 | -0.018311 | 0.041199 | -122.3648 | 0.23346 | 0.22888 | -0.064087 | 0.24719 | -0.045776 | 1.1032 | 122.5616 | 0.25177 | 0.49896 | 122.9416 | 122.905 | 122.9141 | 122.8867 | -122.8729 | -122.8638 | 122.5342 | 0.48065 | 5.2322 | 1.7899
3909.1719 | 122.9553 | -51.2833 | 71.5439 | -0.03006 | -1.9142e-05 | 0.060957 | 0.066909 | 0.00037377 | 0.0026191 | 0.0034992 | -0.022705 | 0.0019567 | 0.0029906 | 0.0017688 | -0.0040695 | -0.0040845 | -0.0044605 | -46.1151 | 71.5897 | -51.3748 | 71.2692 | -50.2167 | -51.1551 | -50.6012 | -49.4385 | 71.608 | -51.3382 | -50.8072 | -51.0361 | -51.3474 | -51.0544 | -0.091553 | 0.045777 | -0.27466 | 1.0666 | 0.68207 | 0.12817 | 0.77362 | 0.21973 | -0.054932 | 0.064087 | -122.3511 | 0.24719 | 0.22888 | -0.064087 | 0.28381 | -0.009155 | 1.1581 | 122.644 | 0.30212 | 0.53101 | 122.9645 | 122.9462 | 122.8729 | 122.8912 | -122.9187 | -122.8821 | 122.5525 | 0.47607 | 5.1682 | 1.8448
3910.1719 | 122.9736 | -51.2558 | 71.5576 | -0.037689 | -0.00044654 | 0.061385 | 0.069472 | 0.0016556 | -0.00015811 | 0.0039264 | -0.0013428 | 0.0025975 | 0.0023498 | 0.0028368 | -0.0019333 | -0.0070753 | 0.0021619 | -46.1334 | 71.5805 | -51.3474 | 71.2738 | -50.2304 | -51.1551 | -50.6104 | -49.4659 | 71.5851 | -51.3245 | -50.8163 | -51.0361 | -51.3336 | -51.0498 | -0.091553 | 0.022888 | -0.28381 | 1.0254 | 0.64545 | 0.10071 | 0.737 | 0.19226 | -0.068665 | 0.027466 | -122.374 | 0.21973 | 0.20599 | -0.07782 | 0.27466 | -0.009155 | 1.1169 | 122.6212 | 0.28839 | 0.50812 | 122.9279 | 122.9095 | 122.8363 | 122.8409 | -122.905 | -122.8821 | 122.5296 | 0.43945 | 5.1224 | 1.7899
3911.1719 | 122.9874 | -51.3016 | 71.5713 | -0.098725 | 0.0021171 | 0.060957 | 0.068191 | 0.0055008 | 0.0015509 | 0.0028582 | -0.0074462 | -0.0010339 | 0.00085443 | 0.0015552 | -0.0036423 | -0.0060071 | 0.0013073 | -46.1243 | 71.5805 | -51.3702 | 71.2692 | -50.2304 | -51.1734 | -50.6012 | -49.4797 | 71.6125 | -51.3062 | -50.8118 | -51.0406 | -51.3428 | -51.0452 | -0.068664 | 0.009155 | -0.30212 | 1.0712 | 0.70038 | 0.12817 | 0.76904 | 0.19684 | -0.004577 | 0.041199 | -122.3831 | 0.26093 | 0.25635 | -0.041198 | 0.26093 | -0.036621 | 1.1398 | 122.6395 | 0.2655 | 0.49438 | 122.9507 | 122.9187 | 122.8821 | 122.9141 | -122.9416 | -122.8775 | 122.5708 | 0.48981 | 5.1773 | 1.8219
3912.1719 | 122.9279 | -51.2604 | 71.5759 | -0.091095 | -0.00087374 | 0.060744 | 0.067123 | 0.0027238 | 0.0036871 | 0.0054218 | -0.047119 | 0.0019567 | 2.8e-08 | 0.0054004 | -0.0036423 | -0.0057935 | 0.0013073 | -46.1334 | 71.5622 | -51.384 | 71.2646 | -50.2899 | -50.9125 | -50.4547 | -49.4568 | 71.5988 | -51.3153 | -50.8484 | -51.0452 | -51.3565 | -51.0773 | -0.1236 | -0.013733 | -0.31128 | 0.97046 | 0.80566 | 0.3479 | 0.92926 | 0.4715 | -0.054932 | 0.022888 | -122.4243 | 0.21515 | 0.1831 | -0.09613 | 0.23804 | -0.041198 | 1.0941 | 122.6486 | 0.27008 | 0.46692 | 122.9462 | 122.9141 | 122.8226 | 122.8592 | -122.9599 | -122.8912 | 122.525 | 0.41199 | 5.127 | 1.8036
3913.1719 | 122.9233 | -51.297 | 71.5851 | -0.045319 | -0.0015145 | 0.06053 | 0.069259 | 0.00080117 | 5.5488e-05 | 0.0060626 | 0.0047608 | -0.0018885 | 0.00064083 | -0.0016492 | -0.0010787 | -0.0062207 | 0.0042981 | -46.1243 | 71.5851 | -51.3428 | 71.2738 | -50.2029 | -51.1642 | -50.5966 | -49.3195 | 71.6583 | -51.2695 | -50.853 | -51.0544 | -51.3519 | -51.0635 | -0.045776 | 0 | -0.31128 | 1.0941 | 0.70038 | 0.13275 | 0.74615 | 0.17853 | 0.027466 | 0.073242 | -122.438 | 0.24262 | 0.23346 | -0.054932 | 0.20599 | -0.082398 | 1.1398 | 122.6166 | 0.21515 | 0.41656 | 122.9279 | 122.9279 | 122.8821 | 122.9553 | -122.9279 | -122.8546 | 122.5708 | 0.44403 | 5.1727 | 1.9775
3914.1719 | 122.937 | -51.2604 | 71.5851 | -0.045319 | -0.00087374 | 0.061598 | 0.069472 | -0.00026703 | 0.0015509 | 0.0056354 | 0.0078126 | 0.0030249 | 0.003418 | 0.001128 | -0.0036423 | -0.0040845 | -0.0012561 | -46.0968 | 71.5897 | -51.3657 | 71.2646 | -50.2029 | -51.1551 | -50.6012 | -49.4522 | 71.6354 | -51.3107 | -50.8209 | -51.0406 | -51.3611 | -51.059 | -0.10529 | 0.004578 | -0.32044 | 1.0574 | 0.65918 | 0.10529 | 0.76447 | 0.21057 | -0.050354 | 0.050354 | -122.406 | 0.21973 | 0.20142 | -0.10071 | 0.25177 | -0.050354 | 1.1627 | 122.6303 | 0.27008 | 0.48981 | 122.9553 | 122.9462 | 122.85 | 122.8958 | -122.9507 | -122.8958 | 122.525 | 0.43945 | 5.1636 | 1.8082
3915.1719 | 122.9599 | -51.2604 | 71.5668 | -0.068207 | -0.00023294 | 0.063094 | 0.067763 | 0.003151 | 0.0026191 | 0.0047808 | -0.0013428 | 0.0032385 | 0.00064083 | -0.0089124 | -0.0023605 | -0.0062207 | 0.0017345 | -46.106 | 71.5942 | -51.3611 | 71.2692 | -50.2167 | -51.1642 | -50.6058 | -49.4522 | 71.6217 | -51.2878 | -50.8301 | -51.0544 | -51.3336 | -51.059 | -0.10071 | 0.027466 | -0.29755 | 1.0437 | 0.6546 | 0.09613 | 0.75531 | 0.19684 | -0.027466 | 0.054932 | -122.3969 | 0.20599 | 0.20142 | -0.073242 | 0.22888 | -0.045776 | 1.1444 | 122.6303 | 0.23346 | 0.45776 | 122.9553 | 122.9095 | 122.8546 | 122.8821 | -122.9279 | -122.8546 | 122.5296 | 0.4303 | 5.1544 | 1.8082
3916.1719 | 122.9782 | -51.2558 | 71.5851 | -0.1445 | 0.00040806 | 0.063734 | 0.069259 | 0.0010148 | -0.00058531 | 0.0090534 | -0.0043946 | 0.00046135 | 0.0019226 | -0.00036738 | -0.0017197 | -0.0062207 | -0.0021107 | -46.0739 | 71.5988 | -51.3565 | 71.315 | -50.1892 | -51.1139 | -50.5875 | -49.3881 | 71.6217 | -51.2833 | -50.798 | -51.0178 | -51.3382 | -51.0223 | -0.10071 | 0.013733 | -0.27008 | 1.0666 | 0.66833 | 0.14191 | 0.76904 | 0.24261 | -0.027466 | 0.036621 | -122.3831 | 0.23804 | 0.23346 | -0.082398 | 0.26093 | -0.054932 | 1.1673 | 122.6715 | 0.2655 | 0.48523 | 122.9553 | 122.905 | 122.8546 | 122.8775 | -122.9416 | -122.8683 | 122.5708 | 0.45776 | 5.1819 | 1.8677
3917.1719 | 122.9691 | -51.2558 | 71.5805 | -0.022431 | -0.00066014 | 0.061385 | 0.067977 | 0.0012284 | 0.0017645 | 0.0052082 | 0.016968 | 0.0030249 | 0.0014954 | -0.0020764 | -0.0023605 | -0.0049389 | 0.00045294 | -46.0693 | 71.5851 | -51.3474 | 71.2875 | -50.1984 | -51.123 | -50.5783 | -49.4202 | 71.6354 | -51.297 | -50.8072 | -50.9995 | -51.3199 | -51.0178 | -0.091553 | 0.004578 | -0.29297 | 1.0574 | 0.67749 | 0.13275 | 0.76904 | 0.2243 | -0.041199 | 0.054932 | -122.3877 | 0.25635 | 0.23804 | -0.064087 | 0.27924 | -0.022888 | 1.149 | 122.6349 | 0.29755 | 0.48981 | 122.9324 | 122.9324 | 122.8409 | 122.8912 | -122.9279 | -122.8775 | 122.5433 | 0.44861 | 5.1865 | 1.8356
3918.1719 | 122.9324 | -51.265 | 71.5668 | -0.068207 | -1.9142e-05 | 0.062025 | 0.067123 | -0.0041122 | 0.0021917 | 0.0081988 | 0.013916 | 0.0028113 | 0.0014954 | -0.0014356 | 0.00020289 | -0.0062207 | 0.0036571 | -46.0785 | 71.5942 | -51.3382 | 71.1777 | -50.3265 | -51.0956 | -50.592 | -49.4522 | 71.6354 | -51.2787 | -50.8347 | -51.0452 | -51.3519 | -51.0498 | -0.073242 | 0.027466 | -0.3891 | 0.93842 | 0.67291 | 0.16937 | 0.74616 | 0.24262 | -0.013733 | 0.068665 | -122.4014 | 0.21973 | 0.21515 | -0.086975 | 0.22888 | -0.073242 | 1.0117 | 122.5159 | 0.23346 | 0.44403 | 122.9324 | 122.9141 | 122.8592 | 122.9004 | -122.905 | -122.8455 | 122.4426 | 0.4303 | 5.1865 | 1.8127
3919.1719 | 122.9279 | -51.265 | 71.5759 | -0.060578 | 0.00083526 | 0.062453 | 0.069045 | -5.343e-05 | 0.0015509 | 0.001363 | 0.087158 | 0.0023839 | 0.004486 | -0.0069898 | -0.0023605 | -0.0062207 | -0.00061526 | -46.0739 | 71.5942 | -51.3382 | 71.2875 | -50.1846 | -51.1368 | -50.592 | -49.5117 | 71.6446 | -51.2924 | -50.8255 | -51.059 | -51.3565 | -51.0635 | -0.073242 | 0.01831 | -0.28839 | 1.0803 | 0.67291 | 0.12817 | 0.74616 | 0.20142 | -0.027465 | 0.068664 | -122.4014 | 0.20599 | 0.20142 | -0.091552 | 0.22888 | -0.064087 | 1.1536 | 122.6257 | 0.23346 | 0.46692 | 122.9324 | 122.937 | 122.8592 | 122.9095 | -122.9141 | -122.8683 | 122.5525 | 0.43945 | 5.191 | 1.7532
3920.1719 | 122.8867 | -51.2558 | 71.5942 | -0.022431 | 0.0012625 | 0.058821 | 0.069472 | 0.00037377 | 0.0024053 | 0.0054218 | 0.013916 | 0.00024775 | 0.00085443 | -0.00015378 | -0.0023605 | -0.0062207 | -0.0010425 | -46.0739 | 71.6034 | -51.3382 | 71.2784 | -50.1801 | -51.1505 | -50.5783 | -49.4431 | 71.6171 | -51.3016 | -50.8026 | -50.8026 | -51.4481 | -51.1139 | -0.082398 | 0.009156 | -0.31586 | 1.0757 | 0.67749 | 0.10529 | 0.75989 | 0.18768 | -0.045777 | 0.022888 | -122.3969 | 0.45319 | 0.14191 | -0.19226 | 0.18768 | -0.14648 | 1.1581 | 122.6166 | 0.49896 | 0.49896 | 122.9416 | 122.9187 | 122.8592 | 122.8729 | -122.9324 | -122.8958 | 122.5342 | 0.45319 | 5.1819 | 1.8127
3921.1719 | 122.9141 | -51.2604 | 71.5713 | -0.052948 | 0.0014761 | 0.062239 | 0.068404 | -0.00026703 | 0.00091009 | 0.0034992 | 0.013916 | 0.0017431 | 0.0023498 | 0.0028368 | -0.00086511 | -0.0047253 | 2.554e-05 | -46.1884 | 71.608 | -51.3519 | 71.2692 | -50.1892 | -51.1642 | -50.5692 | -49.4476 | 71.6125 | -51.297 | -50.8301 | -51.0361 | -51.3336 | -51.0452 | -0.091553 | 0.036621 | -0.30212 | 1.0712 | 0.69122 | 0.09613 | 0.78278 | 0.18768 | -0.036621 | 0.041199 | -122.4014 | 0.2243 | 0.21515 | -0.073242 | 0.25177 | -0.036621 | 1.1627 | 122.6212 | 0.26093 | 0.46692 | 122.9599 | 122.9095 | 122.8683 | 122.8729 | -122.9233 | -122.8683 | 122.5296 | 0.4303 | 5.072 | 1.8127
3922.1719 | 122.937 | -51.2375 | 71.608 | -0.03006 | 0.00083526 | 0.060744 | 0.069259 | 0.0029374 | 0.0039007 | 0.00414 | 0.016968 | 0.0013159 | 0.003418 | 0.0026232 | -0.0015061 | -0.0042981 | -0.0016833 | -46.0419 | 71.6171 | -51.3153 | 71.3608 | -50.2533 | -51.329 | -50.6012 | -49.4431 | 71.6354 | -51.3016 | -50.8072 | -51.0406 | -51.3382 | -51.0498 | -0.07782 | 0.009155 | -0.24719 | 0.98419 | 0.63629 | -0.091553 | 0.71411 | -0.013733 | -0.064087 | 0.027466 | -122.4152 | 0.19684 | 0.18768 | -0.10071 | 0.25177 | -0.036621 | 1.062 | 122.6761 | 0.26093 | 0.49439 | 122.9324 | 122.937 | 122.8546 | 122.8729 | -122.9233 | -122.9095 | 122.5983 | 0.4303 | 5.1956 | 1.7944
3923.1719 | 122.9599 | -51.2421 | 71.608 | -0.03006 | -0.0013009 | 0.060316 | 0.070754 | 0.00058737 | 0.0028327 | 0.0049946 | 0.001709 | 0.0019567 | 0.0025634 | -0.002931 | -0.0038559 | -0.0040845 | 0.0049389 | -46.0236 | 71.6034 | -51.3382 | 71.3104 | -50.1801 | -51.1322 | -50.5783 | -49.4202 | 71.6354 | -51.3016 | -50.7889 | -51.0269 | -51.329 | -51.0315 | -0.096131 | -0.004577 | -0.29755 | 1.062 | 0.66376 | 0.10986 | 0.75989 | 0.20599 | -0.05951 | 0.027466 | -122.3969 | 0.21515 | 0.21057 | -0.086976 | 0.27008 | -0.027466 | 1.1581 | 122.6486 | 0.27466 | 0.5127 | 122.9416 | 122.937 | 122.8455 | 122.8775 | -122.9462 | -122.9095 | 122.5525 | 0.45319 | 5.2185 | 1.8219
3924.1719 | 122.9233 | -51.2421 | 71.6034 | -0.052948 | -0.0015145 | 0.061385 | 0.065414 | 0.0010148 | 0.0032599 | 0.0054218 | 0.013916 | 0.0025975 | 0.004486 | -0.0020764 | -0.0023605 | -0.0070753 | -0.0016833 | -46.0464 | 71.6217 | -51.3382 | 71.3013 | -50.1709 | -51.1322 | -50.5692 | -49.4339 | 71.6309 | -51.2833 | -50.8026 | -51.0132 | -51.3245 | -51.0406 | -0.096131 | 0.01831 | -0.30212 | 1.0712 | 0.67291 | 0.10986 | 0.76904 | 0.20599 | -0.041199 | 0.027465 | -122.406 | 0.22888 | 0.20142 | -0.082398 | 0.24262 | -0.041199 | 1.1673 | 122.6395 | 0.27008 | 0.48065 | 122.9599 | 122.9141 | 122.8638 | 122.8729 | -122.9416 | -122.8867 | 122.5433 | 0.43945 | 5.1956 | 1.8082
3925.1719 | 122.9187 | -51.2375 | 71.5942 | -0.03006 | 0.00062166 | 0.060103 | 0.069259 | 0.0018692 | 0.0021917 | 0.0047808 | 0.010864 | 0.0017431 | 0.002777 | 0.0032642 | -0.00065151 | -0.0068615 | 0.0038709 | -46.0052 | 71.6171 | -51.3428 | 71.2784 | -50.1251 | -51.1505 | -50.592 | -49.4247 | 71.6446 | -51.2787 | -50.798 | -51.0223 | -51.3474 | -51.0361 | -0.10529 | 0.022888 | -0.31586 | 1.1124 | 0.64545 | 0.086975 | 0.75073 | 0.19226 | -0.041199 | 0.050354 | -122.3923 | 0.21515 | 0.20142 | -0.10986 | 0.24262 | -0.068664 | 1.2177 | 122.6212 | 0.25635 | 0.48065 | 122.9599 | 122.9233 | 122.8546 | 122.8821 | -122.937 | -122.8729 | 122.5159 | 0.43945 | 5.2322 | 1.8127
3926.1719 | 122.9462 | -51.2329 | 71.5942 | -0.075836 | -0.00023294 | 0.060744 | 0.067336 | 0.001442 | 0.0026191 | 0.0039264 | 0.032227 | 0.00024775 | -0.00021357 | 0.0036914 | 0.00020289 | -0.0055799 | 0.0030163 | -45.9595 | 71.5713 | -51.2741 | 71.3608 | -50.0748 | -51.0681 | -50.5142 | -49.3469 | 71.608 | -51.2466 | -50.7935 | -50.9857 | -51.2878 | -51.0178 | -0.041199 | -0.022888 | -0.23346 | 1.1581 | 0.71869 | 0.16479 | 0.75989 | 0.20599 | -0.013733 | 0.013733 | -122.3877 | 0.24719 | 0.21515 | -0.054932 | 0.22888 | -0.041199 | 1.1993 | 122.6349 | 0.26093 | 0.45319 | 122.8455 | 122.8546 | 122.8043 | 122.8409 | -122.8683 | -122.8409 | 122.5937 | 0.43945 | 5.2734 | 1.886
3927.1719 | 122.9507 | -51.2238 | 71.608 | -0.098725 | 0.0014761 | 0.061598 | 0.066695 | -0.00026703 | 0.0024053 | 0.005849 | 0.03833 | 3.4148e-05 | 0.0029906 | 0.003905 | -0.0027877 | -0.0062207 | -0.0016833 | -45.9229 | 71.5897 | -51.2924 | 71.3837 | -50.0381 | -51.0315 | -50.4593 | -49.3011 | 71.6263 | -51.2421 | -50.7523 | -50.9537 | -51.2604 | -50.9857 | -0.068664 | -0.01831 | -0.2243 | 1.1856 | 0.76446 | 0.19226 | 0.83313 | 0.26093 | -0.01831 | 0.018311 | -122.3602 | 0.27008 | 0.23804 | -0.036621 | 0.25635 | -0.018311 | 1.2543 | 122.6761 | 0.28839 | 0.48981 | 122.8821 | 122.8683 | 122.8134 | 122.85 | -122.9004 | -122.85 | 122.6074 | 0.4715 | 5.3009 | 1.9226
3928.1719 | 122.9187 | -51.2283 | 71.6354 | -0.098725 | 0.0019035 | 0.062025 | 0.070968 | -0.0024032 | 0.0019781 | 0.0056354 | 0.050537 | -0.00060665 | 0.0021362 | -0.0037854 | -0.0015061 | -0.0072889 | 0.0019483 | -45.9457 | 71.6171 | -51.3062 | 71.3287 | -50.1068 | -51.0727 | -50.5142 | -49.3881 | 71.6492 | -51.2512 | -50.7935 | -50.9949 | -51.297 | -51.0315 | -0.077819 | -0.018311 | -0.3067 | 1.1215 | 0.71411 | 0.15564 | 0.79193 | 0.23346 | -0.022888 | 0.013733 | -122.4289 | 0.23346 | 0.19684 | -0.068664 | 0.21973 | -0.045776 | 1.1993 | 122.6349 | 0.25635 | 0.45776 | 122.9233 | 122.9004 | 122.8455 | 122.8775 | -122.9416 | -122.8867 | 122.5571 | 0.43488 | 5.2826 | 1.8402
3929.1719 | 122.9187 | -51.2192 | 71.6125 | -0.091095 | 0.00083526 | 0.061812 | 0.068191 | -0.0024032 | -0.0012261 | 0.002431 | 0.032227 | 0.0025975 | 2.8e-08 | -0.0016492 | -0.0040695 | -0.0079297 | -0.00082886 | -45.932 | 71.6217 | -51.2833 | 71.3745 | -50.0656 | -51.0452 | -50.4868 | -49.3423 | 71.6309 | -51.2421 | -50.7568 | -50.9766 | -51.2741 | -51.0178 | -0.064087 | 0.009155 | -0.23804 | 1.1536 | 0.73242 | 0.17395 | 0.79651 | 0.23804 | -0.022888 | 0.01831 | -122.3694 | 0.24262 | 0.20142 | -0.054932 | 0.2243 | -0.032044 | 1.2177 | 122.6578 | 0.2655 | 0.48523 | 122.905 | 122.8729 | 122.8409 | 122.85 | -122.8958 | -122.8546 | 122.5937 | 0.46234 | 5.2872 | 1.8768
3930.1719 | 122.9324 | -51.2009 | 71.6721 | -0.098725 | -0.0013009 | 0.059248 | 0.067336 | -0.001976 | 0.0015509 | 0.0037128 | 0.0078126 | 0.00046135 | 0.002777 | 0.00070062 | -0.0027877 | -0.0072889 | 0.0015209 | -45.9457 | 71.6263 | -51.3199 | 71.3333 | -50.1114 | -51.1093 | -50.5325 | -49.3881 | 71.6904 | -51.2329 | -50.7935 | -50.9949 | -51.3062 | -51.1139 | -0.11902 | -0.045776 | -0.33875 | 1.0895 | 0.66833 | 0.091553 | 0.78735 | 0.21057 | -0.032043 | 0.018311 | -122.4655 | 0.20599 | 0.086975 | -0.10528 | 0.11902 | -0.073242 | 1.2085 | 122.6532 | 0.23804 | 0.43945 | 122.9462 | 122.9233 | 122.8271 | 122.8912 | -122.9919 | -122.905 | 122.5342 | 0.40741 | 5.2551 | 1.8127
3931.1719 | 122.9324 | -51.2054 | 71.608 | -0.0071715 | 0.00040806 | 0.06288 | 0.068618 | 0.0018692 | 0.0019781 | 0.0028582 | 0.016968 | 0.00024775 | 0.0038452 | -0.0033582 | -0.0015061 | -0.0077161 | 0.0021619 | -45.9274 | 71.6309 | -51.2878 | 71.3379 | -50.0977 | -51.091 | -50.5005 | -49.3835 | 71.6537 | -51.2466 | -50.7843 | -50.9949 | -51.3107 | -51.0361 | -0.082398 | 0.022888 | -0.27008 | 1.1078 | 0.70496 | 0.11444 | 0.78735 | 0.19684 | -0.041199 | 0.045777 | -122.3923 | 0.21057 | 0.16937 | -0.10529 | 0.21057 | -0.064087 | 1.1902 | 122.6257 | 0.25177 | 0.46234 | 122.9187 | 122.9004 | 122.8363 | 122.8592 | -122.8958 | -122.8546 | 122.5433 | 0.42114 | 5.278 | 1.8219
3932.1719 | 122.9324 | -51.2054 | 71.6446 | -0.10635 | -0.00066014 | 0.060316 | 0.069259 | -0.0013352 | -0.0012261 | 0.0028582 | 0.02002 | 0.00024775 | 0.00042723 | -0.00079478 | -0.0015061 | -0.0062207 | 0.0025891 | -45.9137 | 71.6034 | -51.2741 | 71.3837 | -50.0473 | -51.0498 | -50.4776 | -49.3149 | 71.6492 | -51.2283 | -50.7523 | -50.9628 | -51.2741 | -51.0132 | -0.068665 | -0.041198 | -0.26093 | 1.1581 | 0.72784 | 0.15564 | 0.79651 | 0.2243 | -0.022889 | 0.004578 | -122.3969 | 0.24261 | 0.19226 | -0.068665 | 0.21515 | -0.045776 | 1.2268 | 122.6578 | 0.2655 | 0.47608 | 122.8775 | 122.8775 | 122.8088 | 122.8546 | -122.9187 | -122.8729 | 122.5891 | 0.45319 | 5.2917 | 1.8906
3933.1719 | 122.9874 | -51.1826 | 71.608 | -0.037689 | -0.0023691 | 0.061812 | 0.070113 | -0.003685 | 0.0019781 | 0.0064898 | 0.050537 | 0.00046135 | 2.8e-08 | -0.0042126 | -0.0036423 | -0.0066479 | -0.0027515 | -45.7535 | 71.6537 | -51.2329 | 71.4249 | -49.9741 | -51.004 | -50.4135 | -49.2325 | 71.608 | -51.1963 | -50.6882 | -50.8804 | -51.1642 | -50.9171 | -0.050354 | 0.045777 | -0.18311 | 1.2085 | 0.76904 | 0.17853 | 0.8194 | 0.22888 | -0.013733 | 0 | -122.2961 | 0.30212 | 0.2655 | 0.01831 | 0.27924 | 0.032043 | 1.2588 | 122.6578 | 0.31586 | 0.50812 | 122.8867 | 122.8043 | 122.8363 | 122.7905 | -122.8409 | -122.8043 | 122.6074 | 0.49439 | 5.4291 | 1.9501
3934.1719 | 123.0606 | -51.1734 | 71.6034 | -0.091095 | -0.0025827 | 0.063307 | 0.069686 | 0.0035782 | 0.0019781 | 0.00414 | -0.080688 | 3.4148e-05 | 0.001709 | -0.00229 | -0.0042831 | -0.0051527 | -0.0040333 | -45.8405 | 71.6263 | -51.2512 | 71.4523 | -49.9649 | -50.5325 | -50.267 | -49.1684 | 71.6171 | -51.2146 | -50.6744 | -50.8438 | -51.1414 | -50.9033 | -0.07782 | 0.022888 | -0.15106 | 1.2085 | 0.90637 | 0.64087 | 0.98419 | 0.71869 | -0.041199 | 0.013732 | -122.2778 | 0.32959 | 0.27008 | 0.032044 | 0.31128 | 0.073243 | 1.2863 | 122.7036 | 0.37079 | 0.54016 | 122.8775 | 122.8317 | 122.7997 | 122.7905 | -122.8546 | -122.818 | 122.6257 | 0.49896 | 5.3329 | 2.005
3935.1719 | 123.0377 | -51.1642 | 71.64 | -0.075836 | 0.00040806 | 0.06053 | 0.066268 | -0.0021896 | -0.00015811 | 0.0047808 | 0.010864 | 3.4148e-05 | 0.00021363 | -0.00229 | -0.0047103 | -0.0053663 | 0.0013073 | -45.8542 | 71.5942 | -51.2512 | 71.4523 | -49.9741 | -50.9857 | -50.3952 | -49.2233 | 71.6446 | -51.1917 | -50.6607 | -50.8621 | -51.1688 | -50.9079 | -0.086975 | -0.045777 | -0.18768 | 1.1902 | 0.76904 | 0.17853 | 0.85602 | 0.2655 | -0.027465 | 0.004577 | -122.3007 | 0.30212 | 0.25635 | -0.004577 | 0.28381 | 0.022888 | 1.2772 | 122.7036 | 0.32959 | 0.53101 | 122.8455 | 122.8363 | 122.7585 | 122.8088 | -122.8912 | -122.8317 | 122.6166 | 0.50354 | 5.3101 | 1.9409
3936.1719 | 123.0331 | -51.1642 | 71.64 | -0.28183 | 0.0023307 | 0.058821 | 0.068404 | 0.0027238 | 0.0021917 | 0.002431 | 0.010864 | 0.00067495 | 0.00021363 | 0.001128 | -0.0019333 | -0.0066479 | -0.00082886 | -45.8176 | 71.5942 | -51.2466 | 71.4615 | -49.9329 | -50.9537 | -50.4089 | -49.1959 | 71.6537 | -51.1917 | -50.6516 | -50.8392 | -51.1505 | -50.8987 | -0.082397 | -0.045777 | -0.17853 | 1.2314 | 0.75531 | 0.21057 | 0.83771 | 0.29297 | -0.027465 | 0.013733 | -122.2916 | 0.32501 | 0.2655 | 0.013733 | 0.29297 | 0.041198 | 1.3138 | 122.7081 | 0.35248 | 0.54016 | 122.8409 | 122.8455 | 122.7585 | 122.818 | -122.8867 | -122.8317 | 122.6257 | 0.5127 | 5.3467 | 1.9684
3937.1719 | 123.0286 | -51.178 | 71.6309 | -0.098725 | 0.0012625 | 0.061598 | 0.068191 | 0.0020828 | 0.00091009 | 0.0039264 | 0.001709 | 0.00024775 | 0.00085443 | -0.0031446 | -0.0032151 | -0.0070753 | 0.00045294 | -45.8313 | 71.608 | -51.2695 | 71.4661 | -49.9741 | -50.9766 | -50.4364 | -49.2325 | 71.6721 | -51.1963 | -50.7019 | -50.9033 | -51.1963 | -50.9125 | -0.091552 | -0.022888 | -0.16479 | 1.2039 | 0.74158 | 0.20142 | 0.83313 | 0.29297 | -0.01831 | 0.041199 | -122.3328 | 0.27466 | 0.2655 | -0.01831 | 0.28381 | 0 | 1.2955 | 122.7356 | 0.29297 | 0.49439 | 122.8775 | 122.8683 | 122.786 | 122.85 | -122.9004 | -122.8271 | 122.644 | 0.47608 | 5.3467 | 1.9455
3938.1719 | 123.0331 | -51.1688 | 71.6629 | -0.045319 | 0.0014761 | 0.061385 | 0.06755 | 0.0029374 | 0.0026191 | 0.0034992 | 0.010864 | 3.4148e-05 | 0.0014954 | -0.0020764 | -0.0044967 | -0.0060071 | -0.0057423 | -45.8267 | 71.64 | -51.2192 | 71.4661 | -49.9558 | -50.9674 | -50.4089 | -49.205 | 71.6583 | -51.2054 | -50.6561 | -50.8621 | -51.1642 | -50.9033 | -0.050354 | -0.022888 | -0.19684 | 1.2131 | 0.75989 | 0.20142 | 0.81024 | 0.25177 | -0.036621 | -0.004578 | -122.319 | 0.3067 | 0.2655 | 0.004577 | 0.30212 | 0.041198 | 1.2634 | 122.6852 | 0.34332 | 0.54932 | 122.8592 | 122.8638 | 122.8088 | 122.8271 | -122.8821 | -122.8683 | 122.6349 | 0.5127 | 5.3421 | 1.9638
3939.1719 | 123.0652 | -51.1642 | 71.6446 | -0.11398 | 0.0019035 | 0.060957 | 0.068191 | -0.00026703 | 0.0021917 | 0.0060626 | 0.023071 | 0.00024775 | 0.0014954 | 0.001128 | -0.0042831 | -0.0064343 | -0.0023243 | -45.8405 | 71.5942 | -51.2329 | 71.4661 | -49.9466 | -50.9491 | -50.3815 | -49.2142 | 71.6537 | -51.1917 | -50.6561 | -50.853 | -51.1505 | -50.8896 | -0.068664 | -0.050354 | -0.17853 | 1.2177 | 0.78278 | 0.21515 | 0.85144 | 0.28381 | -0.027465 | 0.009156 | -122.3007 | 0.31128 | 0.27466 | 0.013733 | 0.30212 | 0.041198 | 1.2863 | 122.699 | 0.33874 | 0.53558 | 122.8271 | 122.8455 | 122.7585 | 122.818 | -122.8775 | -122.8363 | 122.6303 | 0.50812 | 5.3238 | 1.9501
3940.1719 | 123.0789 | -51.1139 | 71.6354 | -0.098725 | 0.0019035 | 0.062453 | 0.066482 | -5.343e-05 | 0.0039007 | 0.0052082 | 0.029175 | -0.00017945 | 0.00021363 | 0.0032642 | -0.0042831 | -0.0057935 | -0.00018806 | -45.8176 | 71.6309 | -51.2146 | 71.4981 | -49.9191 | -50.9811 | -50.3815 | -49.1547 | 71.6537 | -51.178 | -50.6104 | -50.8072 | -51.1139 | -50.853 | -0.10071 | -0.004578 | -0.13733 | 1.1948 | 0.73242 | 0.13275 | 0.83313 | 0.23346 | -0.064087 | 0.018311 | -122.2458 | 0.3067 | 0.26093 | 0 | 0.32501 | 0.064087 | 1.2955 | 122.7127 | 0.37079 | 0.56763 | 122.8455 | 122.8317 | 122.7448 | 122.7676 | -122.85 | -122.8134 | 122.612 | 0.50354 | 5.2963 | 1.9592
3941.1719 | 123.056 | -51.1459 | 71.6583 | -0.052948 | 0.0012625 | 0.061385 | 0.068832 | 0.0016556 | 0.0013373 | 0.0056354 | -0.12036 | 0.0017431 | -0.001709 | -0.0014356 | -0.0034287 | -0.0057935 | 0.00066654 | -45.7764 | 71.6217 | -51.2466 | 71.4981 | -49.9878 | -50.528 | -50.2487 | -49.1272 | 71.6721 | -51.21 | -50.6424 | -50.8072 | -51.123 | -50.8804 | -0.10071 | -0.036621 | -0.16022 | 1.1581 | 0.89722 | 0.61798 | 0.99793 | 0.71869 | -0.064087 | 0.013733 | -122.3007 | 0.33875 | 0.2655 | 0.022888 | 0.32959 | 0.086975 | 1.2588 | 122.7448 | 0.40283 | 0.56763 | 122.8683 | 122.8821 | 122.7676 | 122.818 | -122.905 | -122.8683 | 122.644 | 0.50354 | 5.3696 | 2.0187
3942.1719 | 123.0331 | -51.1505 | 71.608 | -0.091095 | -0.00066014 | 0.06053 | 0.066482 | -0.00026703 | 0.0017645 | 0.0049946 | 0.03833 | -0.00082025 | 0.001709 | -0.0033582 | -0.0012925 | -0.0042981 | -0.0027515 | -45.7809 | 71.6125 | -51.2146 | 71.5073 | -49.8962 | -50.9262 | -50.3769 | -49.1638 | 71.6675 | -51.1642 | -50.7751 | -50.8255 | -51.0864 | -50.8667 | -0.064087 | 0.004578 | -0.10071 | 1.2543 | 0.77362 | 0.2243 | 0.83771 | 0.28839 | -0.013733 | 0.059509 | -122.3831 | 0.32501 | 0.28381 | 0.064087 | 0.29755 | 0.07782 | 1.3184 | 122.7219 | 0.33875 | 0.3891 | 122.8271 | 122.8317 | 122.7631 | 122.818 | -122.8226 | -122.7722 | 122.6578 | 0.37537 | 5.3696 | 1.9867
3943.1719 | 123.1659 | -51.1139 | 71.7178 | -0.12924 | 0.00040806 | 0.061385 | 0.069472 | 0.0020828 | 5.5488e-05 | 0.0017902 | 0.035278 | -0.00039305 | 0.00064083 | 0.002196 | -0.0040695 | -0.0047253 | -0.0014697 | -45.7855 | 71.6263 | -51.1963 | 71.5118 | -49.9008 | -50.9262 | -50.3494 | -49.1318 | 71.6675 | -51.1826 | -50.6104 | -50.8118 | -51.1093 | -51.0223 | -0.082397 | -0.091552 | -0.20599 | 1.2131 | 0.76447 | 0.18768 | 0.84686 | 0.27008 | -0.068664 | -0.050354 | -122.3282 | 0.30212 | 0.091553 | 0.004578 | 0.16022 | 0.073242 | 1.2955 | 122.7081 | 0.37079 | 0.5722 | 122.8226 | 122.85 | 122.7402 | 122.7814 | -122.9141 | -122.9004 | 122.6257 | 0.50354 | 5.3284 | 1.9821
3944.1719 | 123.0423 | -51.1414 | 71.6629 | -0.052948 | -0.00023294 | 0.062453 | 0.068618 | 0.0012284 | 0.0017645 | 0.0026446 | 0.02002 | 0.0011023 | -0.0012818 | -0.0016492 | -0.0032151 | -0.0070753 | -0.0025379 | -45.6985 | 71.6995 | -51.2146 | 71.4798 | -49.9054 | -50.972 | -50.3769 | -49.1638 | 71.6629 | -51.1734 | -50.647 | -50.8209 | -51.1322 | -50.8713 | -0.073243 | 0.036621 | -0.18311 | 1.236 | 0.76447 | 0.16937 | 0.83771 | 0.24262 | -0.032044 | 0 | -122.3099 | 0.32043 | 0.27008 | 0.009155 | 0.30212 | 0.041199 | 1.3092 | 122.6944 | 0.35248 | 0.52643 | 122.9141 | 122.8363 | 122.8409 | 122.8043 | -122.8775 | -122.8363 | 122.6212 | 0.49438 | 5.4428 | 1.9775
3945.1719 | 123.0469 | -51.1414 | 71.6583 | -0.068207 | 0.00019446 | 0.061598 | 0.0699 | -0.0017624 | -0.0012261 | 0.0047808 | 0.0047608 | -0.00017945 | 0.00042723 | 0.001128 | -0.0049241 | -0.0057935 | -0.0010425 | -45.7626 | 71.6675 | -51.1871 | 71.6309 | -50.1709 | -51.1505 | -50.3677 | -49.173 | 71.6537 | -51.1917 | -50.6058 | -50.8163 | -51.0956 | -50.8667 | -0.045777 | 0.009155 | -0.027466 | 0.97046 | 0.77362 | -0.009156 | 0.8194 | 0.036621 | -0.050354 | -0.004577 | -122.2641 | 0.32501 | 0.27466 | 0.045776 | 0.32501 | 0.09613 | 1.0162 | 122.818 | 0.37537 | 0.58594 | 122.8546 | 122.8455 | 122.8088 | 122.7951 | -122.8455 | -122.85 | 122.7722 | 0.53558 | 5.3787 | 1.9684
3946.1719 | 123.0377 | -51.1276 | 71.6675 | -0.098725 | 0.00062166 | 0.059889 | 0.068404 | -0.00090783 | 0.0032599 | 0.0047808 | 0.023071 | 0.0023839 | -0.0025636 | -0.0082716 | -0.0025741 | -0.0055799 | 0.0025891 | -45.7535 | 71.6492 | -51.1642 | 71.5439 | -49.8642 | -50.9171 | -50.354 | -48.8983 | 71.7361 | -51.1093 | -50.6241 | -50.8392 | -51.1093 | -50.8438 | -0.036621 | -0.01831 | -0.1236 | 1.2634 | 0.77362 | 0.21057 | 0.81024 | 0.24719 | 0.018311 | 0.068665 | -122.2916 | 0.28839 | 0.28381 | 0.018311 | 0.2655 | 0 | 1.3 | 122.7081 | 0.27008 | 0.48523 | 122.8134 | 122.8455 | 122.7768 | 122.8638 | -122.8317 | -122.7768 | 122.6715 | 0.50354 | 5.3741 | 2.2293
3947.1719 | 123.0698 | -51.1139 | 71.6583 | -0.091095 | 0.00083526 | 0.063734 | 0.069045 | -0.0011214 | 0.00026909 | 0.0062762 | 0.032227 | 0.0017431 | 0.0019226 | -0.00058098 | -0.0032151 | -0.0066479 | 0.0017345 | -45.7764 | 71.6446 | -51.2192 | 71.4844 | -49.9237 | -50.9583 | -50.3952 | -49.1592 | 71.7087 | -51.1734 | -50.6058 | -50.798 | -51.1139 | -50.8438 | -0.10529 | -0.013733 | -0.17395 | 1.1902 | 0.71869 | 0.15564 | 0.82397 | 0.26093 | -0.059509 | 0.050354 | -122.2641 | 0.31586 | 0.27008 | 0 | 0.32959 | 0.059509 | 1.2955 | 122.7036 | 0.37537 | 0.56763 | 122.8638 | 122.8821 | 122.7585 | 122.8226 | -122.8775 | -122.8317 | 122.5983 | 0.50812 | 5.3375 | 1.9547
3948.1719 | 123.0652 | -51.123 | 71.64 | -0.068207 | 0.00040806 | 0.062239 | 0.066482 | -0.0011214 | 0.0011237 | 0.0043536 | -0.0043946 | -0.00039305 | 0.0019226 | 0.001128 | -0.0034287 | -0.0066479 | -0.00018806 | -45.7535 | 71.6446 | -51.2009 | 71.5256 | -49.8688 | -50.9171 | -50.3586 | -49.0997 | 71.6949 | -51.1414 | -50.5554 | -50.7706 | -51.091 | -50.8347 | -0.07782 | 0.004577 | -0.11444 | 1.2543 | 0.76447 | 0.20599 | 0.84229 | 0.28381 | -0.01831 | 0.054931 | -122.1954 | 0.35248 | 0.28839 | 0.032044 | 0.3067 | 0.050354 | 1.3321 | 122.7264 | 0.37079 | 0.58594 | 122.8455 | 122.8363 | 122.7676 | 122.818 | -122.8409 | -122.7814 | 122.6486 | 0.56763 | 5.3696 | 2.0233
3949.1719 | 123.0743 | -51.1093 | 71.6446 | -0.060578 | 0.00040806 | 0.064162 | 0.067336 | -0.0030442 | 0.0019781 | 0.0060626 | 0.029175 | -0.00017945 | 0.0023498 | -0.0016492 | -0.0030013 | -0.0064343 | -0.0010425 | -45.7352 | 71.6629 | -51.2009 | 71.521 | -49.8779 | -50.9216 | -50.3403 | -49.1318 | 71.6766 | -51.1368 | -50.5783 | -50.7797 | -51.0773 | -50.8209 | -0.091553 | 0.018311 | -0.1236 | 1.2314 | 0.76904 | 0.18768 | 0.8606 | 0.27924 | -0.027466 | 0.032044 | -122.2229 | 0.32959 | 0.28839 | 0.032043 | 0.31586 | 0.059509 | 1.3229 | 122.7219 | 0.35706 | 0.55847 | 122.8638 | 122.8134 | 122.7722 | 122.7859 | -122.8455 | -122.7814 | 122.6303 | 0.53101 | 5.3741 | 1.9775
3950.1719 | 123.0698 | -51.1002 | 71.6492 | -0.091095 | -0.00044654 | 0.061171 | 0.068618 | -0.003685 | 0.0015509 | 0.0064898 | 0.0047608 | -0.0010339 | 0.0012818 | -0.0042126 | -0.0021469 | -0.0066479 | -0.0010425 | -45.7397 | 71.6629 | -51.21 | 71.5118 | -49.8871 | -50.9354 | -50.354 | -49.1318 | 71.6858 | -51.1414 | -50.56 | -50.7706 | -51.091 | -50.8209 | -0.10986 | 0.013733 | -0.13733 | 1.2131 | 0.74615 | 0.16479 | 0.85602 | 0.27466 | -0.041198 | 0.036621 | -122.2092 | 0.32959 | 0.27924 | 0.009156 | 0.32043 | 0.050354 | 1.3229 | 122.7219 | 0.37079 | 0.58136 | 122.8729 | 122.8271 | 122.7631 | 122.7859 | -122.8592 | -122.7905 | 122.612 | 0.54016 | 5.3604 | 1.9684
3951.1719 | 123.0881 | -51.1002 | 71.6583 | -0.083466 | 0.00019446 | 0.059889 | 0.069259 | -0.00048063 | 0.0026191 | 0.0052082 | 0.016968 | 0.0011023 | 0.00021363 | 0.0013416 | -0.00043791 | -0.010707 | -0.0010425 | -45.6985 | 71.6629 | -51.1826 | 71.5393 | -49.8459 | -50.885 | -50.3174 | -49.0906 | 71.7087 | -51.1414 | -50.3815 | -50.9216 | -51.3748 | -50.9262 | -0.082397 | 0.004578 | -0.11902 | 1.2543 | 0.78278 | 0.21515 | 0.86517 | 0.29755 | -0.041198 | 0.050354 | -122.0398 | 0.17853 | 0.17395 | -0.27466 | 0.21515 | -0.23346 | 1.3367 | 122.7219 | 0.21973 | 0.75989 | 122.8455 | 122.85 | 122.7631 | 122.8088 | -122.8409 | -122.7997 | 122.6395 | 0.71869 | 5.4016 | 2.0096
3952.1719 | 123.0789 | -51.1002 | 71.6675 | -0.075836 | 0.0014761 | 0.063521 | 0.069259 | 0.00058737 | 0.0013373 | 0.0064898 | 0.010864 | 0.0017431 | 0.00042723 | -0.0044262 | -0.00043791 | -0.0055799 | 0.0032299 | -45.7031 | 71.6721 | -51.2146 | 71.5347 | -49.8596 | -50.9079 | -50.322 | -49.0768 | 71.6995 | -51.0864 | -50.5554 | -50.7751 | -51.0818 | -50.8118 | -0.11444 | 0.004578 | -0.13275 | 1.2405 | 0.7782 | 0.19226 | 0.89264 | 0.3067 | 0.013733 | 0.032044 | -122.2229 | 0.32501 | 0.28839 | 0.018311 | 0.27466 | 0.004578 | 1.355 | 122.7493 | 0.31128 | 0.53101 | 122.8867 | 122.7859 | 122.7722 | 122.7997 | -122.8821 | -122.7539 | 122.6349 | 0.54474 | 5.397 | 2.0233
3953.1719 | 122.9782 | -51.1185 | 71.6949 | -0.075836 | 0.0019035 | 0.062239 | 0.068618 | -0.00069423 | 0.0017645 | 0.0086262 | -0.092895 | 0.0030249 | -0.00021357 | 0.002196 | -0.0034287 | -0.0047253 | 2.554e-05 | -45.7489 | 71.7453 | -51.21 | 71.4432 | -49.9969 | -51.004 | -50.4318 | -49.2371 | 71.7545 | -51.1734 | -50.6378 | -50.8759 | -51.2009 | -50.8987 | -0.091553 | 0.050354 | -0.25177 | 1.1215 | 0.68664 | 0.11444 | 0.7782 | 0.20599 | -0.054932 | 0.05951 | -122.3328 | 0.24262 | 0.21973 | -0.082398 | 0.27466 | -0.027466 | 1.2131 | 122.6532 | 0.29755 | 0.53558 | 122.9553 | 122.9279 | 122.8638 | 122.8729 | -122.905 | -122.8683 | 122.5616 | 0.48065 | 5.3696 | 1.8814
3954.1719 | 123.0194 | -51.1093 | 71.6537 | -0.075836 | 0.0021171 | 0.061171 | 0.068404 | -0.001976 | 0.0021917 | 0.0028582 | -0.010498 | 0.0017431 | 0.00085443 | -0.0025036 | -0.0012925 | -0.0053663 | -0.0023243 | -45.7352 | 71.6858 | -51.1917 | 71.4844 | -49.942 | -50.9857 | -50.386 | -49.2142 | 71.7133 | -51.1551 | -50.6104 | -50.8072 | -51.1414 | -50.8575 | -0.082397 | 0.032043 | -0.16937 | 1.1673 | 0.72327 | 0.1236 | 0.80566 | 0.20599 | -0.045776 | 0.059509 | -122.2641 | 0.30212 | 0.25177 | -0.032043 | 0.29755 | 0.013733 | 1.2497 | 122.6761 | 0.3479 | 0.54474 | 122.8775 | 122.8683 | 122.7951 | 122.8226 | -122.8455 | -122.8088 | 122.5937 | 0.49896 | 5.3741 | 1.8951
3955.1719 | 123.0194 | -51.0773 | 71.6675 | -0.12924 | 0.0010489 | 0.061171 | 0.068832 | -0.00048063 | 0.00069649 | 0.003072 | 0.0047608 | -0.0016749 | 0.001709 | 0.0030506 | -0.0015061 | -0.0060071 | 0.00066654 | -45.726 | 71.6812 | -51.1826 | 71.4981 | -49.8779 | -50.9308 | -50.3586 | -49.1638 | 71.7316 | -51.1459 | -50.5829 | -50.7797 | -51.091 | -50.8255 | -0.10528 | 0.013733 | -0.16937 | 1.1993 | 0.71869 | 0.14649 | 0.82397 | 0.25177 | -0.068664 | 0.064087 | -122.2504 | 0.29755 | 0.25177 | -0.013732 | 0.32044 | 0.054932 | 1.3046 | 122.6807 | 0.36621 | 0.56305 | 122.8638 | 122.8775 | 122.7585 | 122.8088 | -122.85 | -122.8134 | 122.5754 | 0.49439 | 5.3513 | 1.9135
3956.1719 | 123.0423 | -51.0864 | 71.6858 | -0.091095 | -0.0017281 | 0.061385 | 0.069472 | 0.0029374 | 0.0021917 | 0.0047808 | 0.0078126 | 0.00046135 | 0.0019226 | -0.00058098 | -0.0036423 | -0.0053663 | -0.00082886 | -45.7077 | 71.6858 | -51.1826 | 71.5073 | -49.8871 | -50.9445 | -50.354 | -49.1501 | 71.727 | -51.1276 | -50.5875 | -50.7935 | -51.0956 | -50.8163 | -0.09613 | 0 | -0.17853 | 1.1993 | 0.73242 | 0.14191 | 0.82855 | 0.23804 | -0.041199 | 0.041199 | -122.2733 | 0.29297 | 0.27008 | -0.009155 | 0.31128 | 0.032044 | 1.2955 | 122.6898 | 0.33417 | 0.54016 | 122.8683 | 122.8546 | 122.7722 | 122.8134 | -122.8683 | -122.8134 | 122.5937 | 0.49896 | 5.3787 | 1.9363
3957.1719 | 122.9965 | -51.0864 | 71.6812 | -0.10635 | 0.0023307 | 0.062239 | 0.068618 | -0.0024032 | 0.0024053 | 0.0039264 | 0.010864 | 0.0017431 | 2.8e-08 | 0.00091422 | -0.0021469 | -0.0053663 | -0.00061526 | -45.6894 | 71.6949 | -51.178 | 71.5118 | -49.9237 | -50.9537 | -50.3632 | -49.1867 | 71.7087 | -51.123 | -50.5966 | -50.8026 | -51.0956 | -50.8347 | -0.091553 | 0.013733 | -0.16937 | 1.1627 | 0.72327 | 0.13275 | 0.81482 | 0.22431 | -0.036621 | 0.027466 | -122.2778 | 0.28381 | 0.25177 | -0.009155 | 0.28839 | 0.027466 | 1.2543 | 122.6898 | 0.32043 | 0.52643 | 122.8729 | 122.8317 | 122.7814 | 122.7951 | -122.8592 | -122.8043 | 122.5983 | 0.48981 | 5.397 | 1.8997
3958.1719 | 123.0469 | -51.0727 | 71.6812 | -0.068207 | 0.0029715 | 0.060744 | 0.067763 | 0.00058737 | 0.0017645 | 0.0060626 | 0.0078126 | 3.4148e-05 | 0.001068 | -0.0031446 | -0.0034287 | -0.0055799 | -0.0018971 | -45.6573 | 71.6675 | -51.1688 | 71.5347 | -49.8734 | -50.9354 | -50.3265 | -49.1318 | 71.7224 | -51.123 | -50.5554 | -50.7568 | -51.0727 | -50.8163 | -0.09613 | -0.013733 | -0.14648 | 1.1993 | 0.74616 | 0.13733 | 0.84229 | 0.23346 | -0.050354 | 0.041199 | -122.2366 | 0.31586 | 0.25635 | 0 | 0.3067 | 0.050354 | 1.2955 | 122.7036 | 0.36621 | 0.56763 | 122.8363 | 122.8455 | 122.7402 | 122.7951 | -122.85 | -122.8043 | 122.6074 | 0.51727 | 5.4153 | 1.9409
3959.1719 | 123.0377 | -51.0818 | 71.6904 | -0.083466 | 0.00062166 | 0.060957 | 0.068191 | -0.0026168 | 0.0026191 | 0.0049946 | -0.0043946 | 0.0013159 | 0.001709 | 0.003905 | -0.0030013 | -0.0062207 | -0.0014697 | -45.6757 | 71.6766 | -51.178 | 71.5439 | -49.8642 | -50.9262 | -50.354 | -49.1501 | 71.7407 | -51.123 | -50.5554 | -50.7706 | -51.0727 | -50.8301 | -0.096131 | -0.013733 | -0.14648 | 1.2177 | 0.72784 | 0.15564 | 0.82397 | 0.25177 | -0.041199 | 0.050354 | -122.2458 | 0.31128 | 0.25177 | 0.009155 | 0.29297 | 0.050354 | 1.3138 | 122.7219 | 0.35248 | 0.56763 | 122.8546 | 122.8638 | 122.7585 | 122.8226 | -122.8683 | -122.8134 | 122.6257 | 0.52643 | 5.4062 | 1.9318
3960.1719 | 123.056 | -51.0818 | 71.6904 | -0.068207 | -0.00066014 | 0.060744 | 0.0699 | 0.0020828 | 0.0024053 | 0.0043536 | 0.0047608 | -0.00060665 | -0.0012818 | -0.0054944 | -0.0019333 | -0.0070753 | 0.00023934 | -45.6573 | 71.6858 | -51.178 | 71.5485 | -49.8322 | -50.9033 | -50.3036 | -49.086 | 71.7361 | -51.1047 | -50.5463 | -50.7431 | -51.0635 | -50.7843 | -0.096131 | -0.004578 | -0.14191 | 1.2497 | 0.7782 | 0.17853 | 0.87433 | 0.27466 | -0.022888 | 0.045776 | -122.2366 | 0.33875 | 0.29755 | 0.01831 | 0.32043 | 0.041198 | 1.3458 | 122.7264 | 0.36163 | 0.55847 | 122.8638 | 122.8409 | 122.7676 | 122.818 | -122.8683 | -122.7951 | 122.6303 | 0.53558 | 5.4245 | 1.9958
3961.1719 | 122.9919 | -51.123 | 71.6721 | -0.091095 | -1.9142e-05 | 0.06288 | 0.069686 | -5.343e-05 | 0.0034735 | 0.0049946 | 0.0047608 | 0.00046135 | 0.0012818 | -0.0054944 | -0.0047103 | -0.0075025 | -0.0010425 | -45.6848 | 71.6721 | -51.1734 | 71.4844 | -49.9054 | -50.9674 | -50.3769 | -49.2004 | 71.7316 | -51.1322 | -50.5737 | -50.8896 | -51.178 | -50.8621 | -0.050354 | 0 | -0.18768 | 1.2177 | 0.74616 | 0.15564 | 0.79651 | 0.20599 | -0.009155 | 0.059509 | -122.2458 | 0.23346 | 0.26093 | -0.054932 | 0.27008 | -0.045777 | 1.268 | 122.6578 | 0.24262 | 0.55847 | 122.8455 | 122.8638 | 122.7951 | 122.8546 | -122.8455 | -122.8043 | 122.6074 | 0.54932 | 5.4382 | 1.9226
3962.1719 | 123.0331 | -51.0956 | 71.6949 | -0.13687 | -0.0010873 | 0.061812 | 0.069686 | -0.001976 | 0.0017645 | 0.0037128 | -0.016602 | 0.0015295 | 0.001709 | -0.0031446 | -0.0021469 | -0.0057935 | -0.00018806 | -45.6757 | 71.6812 | -51.1597 | 71.4844 | -49.8917 | -50.9583 | -50.3723 | -49.1821 | 71.7407 | -51.1276 | -50.5646 | -50.8026 | -51.1047 | -50.8347 | -0.064087 | -0.013733 | -0.21057 | 1.2039 | 0.72327 | 0.13733 | 0.78735 | 0.20142 | -0.032044 | 0.045777 | -122.2595 | 0.29297 | 0.26093 | -0.009155 | 0.29297 | 0.022889 | 1.268 | 122.644 | 0.32501 | 0.56305 | 122.8409 | 122.8683 | 122.7768 | 122.8363 | -122.8546 | -122.8226 | 122.58 | 0.53101 | 5.4199 | 1.9135
3963.1719 | 123.0103 | -51.0727 | 71.7133 | -0.091095 | 0.00019446 | 0.061598 | 0.0699 | 0.0022964 | 0.0019781 | 0.0054218 | -0.019653 | -0.00082025 | 0.001068 | 0.00027342 | -0.0021469 | -0.0066479 | -0.0012561 | -45.6619 | 71.6904 | -51.1459 | 71.4935 | -49.9237 | -50.9674 | -50.3677 | -49.2004 | 71.7087 | -51.1414 | -50.5829 | -50.7935 | -51.123 | -50.8438 | -0.073242 | -0.022888 | -0.21973 | 1.149 | 0.70496 | 0.10529 | 0.7782 | 0.17853 | -0.068664 | -0.004578 | -122.2961 | 0.27924 | 0.22888 | -0.050354 | 0.29755 | 0.01831 | 1.2222 | 122.6395 | 0.3479 | 0.55847 | 122.8363 | 122.85 | 122.7631 | 122.7814 | -122.8592 | -122.8546 | 122.5662 | 0.48981 | 5.4108 | 1.8723
3964.1719 | 123.0011 | -51.0773 | 71.6995 | -0.11398 | 0.00062166 | 0.061812 | 0.066482 | 0.0018692 | 0.0017645 | 0.0047808 | -0.050171 | 0.00088875 | 0.0012818 | -0.0035718 | -0.0032151 | -0.0070753 | -0.0010425 | -45.6482 | 71.6721 | -51.1597 | 71.4981 | -49.8825 | -50.8026 | -50.3174 | -49.2096 | 71.7178 | -51.1505 | -50.6104 | -50.8255 | -51.1322 | -50.8301 | -0.082397 | -0.027466 | -0.20142 | 1.1948 | 0.75989 | 0.27466 | 0.84229 | 0.35706 | -0.073242 | 0.01831 | -122.3099 | 0.25177 | 0.24719 | -0.054931 | 0.32043 | 0.018311 | 1.2772 | 122.6578 | 0.32501 | 0.54016 | 122.8317 | 122.8683 | 122.7493 | 122.7951 | -122.8592 | -122.85 | 122.5754 | 0.46692 | 5.4291 | 1.8677
3965.1719 | 123.0377 | -51.0727 | 71.7224 | -0.068207 | -0.0010873 | 0.061598 | 0.069686 | 0.00016017 | 0.0024053 | 0.0084124 | 0.0047608 | 0.0017431 | 0.00021363 | -0.002931 | -0.0017197 | -0.0051527 | -0.00040166 | -45.639 | 71.7133 | -51.1688 | 71.5256 | -49.8596 | -50.9445 | -50.3357 | -49.1501 | 71.7453 | -51.1551 | -50.5646 | -50.7797 | -51.0818 | -50.8072 | -0.09613 | -0.009155 | -0.19684 | 1.2131 | 0.737 | 0.12817 | 0.83313 | 0.2243 | -0.082397 | 0.022888 | -122.287 | 0.29297 | 0.2655 | -0.009155 | 0.3479 | 0.073242 | 1.3092 | 122.6944 | 0.37537 | 0.59052 | 122.8821 | 122.9004 | 122.7859 | 122.818 | -122.8912 | -122.8775 | 122.5983 | 0.50812 | 5.4337 | 1.9226
3966.1719 | 123.0057 | -51.0727 | 71.7133 | -0.12161 | 0.00083526 | 0.060957 | 0.070327 | 0.0020828 | 0.0024053 | 0.0039264 | -0.019653 | 0.00088875 | 0.0012818 | -0.0010084 | -0.0015061 | -0.0049389 | -0.0044605 | -45.6482 | 71.6949 | -51.1826 | 71.5164 | -49.8688 | -50.9308 | -50.3677 | -49.1455 | 71.727 | -51.123 | -50.56 | -50.7843 | -51.1002 | -50.8255 | -0.10986 | -0.018311 | -0.19684 | 1.2039 | 0.70496 | 0.14191 | 0.81482 | 0.25177 | -0.050354 | 0.013733 | -122.2733 | 0.28839 | 0.24719 | -0.027466 | 0.29755 | 0.022888 | 1.3138 | 122.699 | 0.33875 | 0.56305 | 122.8775 | 122.85 | 122.7676 | 122.7997 | -122.8958 | -122.8363 | 122.5891 | 0.5127 | 5.4245 | 1.9272
3967.1719 | 122.9736 | -51.0773 | 71.7087 | -0.075836 | 0.00019446 | 0.061812 | 0.071609 | 0.0010148 | 0.0019781 | 0.0062762 | -0.028809 | 0.0023839 | -0.0032044 | -0.0048536 | -0.0036423 | -0.0055799 | 0.0025891 | -45.6345 | 71.6812 | -51.1597 | 71.5118 | -49.8688 | -50.9537 | -50.3586 | -49.1547 | 71.7453 | -51.123 | -50.5737 | -50.8026 | -51.1139 | -50.8438 | -0.082397 | -0.027466 | -0.19684 | 1.2085 | 0.71869 | 0.1236 | 0.80109 | 0.20599 | -0.045776 | 0.036621 | -122.2824 | 0.27466 | 0.23346 | -0.036621 | 0.27924 | 0.009155 | 1.2909 | 122.6715 | 0.32043 | 0.54932 | 122.8409 | 122.8683 | 122.7585 | 122.8226 | -122.8683 | -122.8317 | 122.5891 | 0.50354 | 5.4428 | 1.9226
3968.1719 | 123.0286 | -51.0864 | 71.6904 | -0.10635 | -0.00023294 | 0.06288 | 0.0699 | -0.0011214 | 0.0015509 | 0.0067036 | -0.025757 | 0.0015295 | -0.0010682 | -0.00079478 | -0.0023605 | -0.0077161 | -0.00040166 | -45.6299 | 71.7087 | -51.1414 | 71.5256 | -49.8779 | -50.9628 | -50.3494 | -49.1409 | 71.7682 | -51.1139 | -50.5737 | -50.8026 | -51.1139 | -50.8163 | -0.054931 | 0.01831 | -0.16479 | 1.2085 | 0.737 | 0.1236 | 0.79193 | 0.17853 | -0.027466 | 0.077819 | -122.2641 | 0.28381 | 0.27008 | -0.027466 | 0.29755 | 0 | 1.2634 | 122.6669 | 0.31128 | 0.54016 | 122.85 | 122.8821 | 122.7951 | 122.8546 | -122.8317 | -122.8043 | 122.612 | 0.5127 | 5.4565 | 1.9455
3969.1719 | 123.0057 | -51.0452 | 71.7361 | -0.1445 | -0.00087374 | 0.06053 | 0.068191 | -0.0032578 | 0.0019781 | 0.0067036 | 0.0078126 | -0.00039305 | -0.0012818 | 0.0013416 | -0.0034287 | -0.0040845 | -0.0057423 | -45.6253 | 71.7133 | -51.1505 | 71.5164 | -49.8917 | -50.9399 | -50.3311 | -49.1638 | 71.7499 | -51.091 | -50.5554 | -50.7706 | -51.091 | -50.8209 | -0.10529 | -0.022888 | -0.21973 | 1.1536 | 0.71411 | 0.10529 | 0.8194 | 0.21057 | -0.045776 | 0.013733 | -122.2916 | 0.27466 | 0.2243 | -0.045776 | 0.27008 | 0 | 1.2588 | 122.6669 | 0.32043 | 0.53558 | 122.8638 | 122.8409 | 122.7585 | 122.7951 | -122.8867 | -122.8271 | 122.5616 | 0.48981 | 5.4199 | 1.8814
3970.1719 | 123.0331 | -51.0452 | 71.7407 | -0.13687 | -0.0025827 | 0.060957 | 0.068404 | -0.00090783 | 0.0026191 | 0.0034992 | -0.010498 | 0.00024775 | 0.001068 | 0.0017688 | -0.0025741 | -0.0040845 | 0.0032299 | -45.5887 | 71.7041 | -51.1597 | 71.6034 | -49.9558 | -50.9583 | -50.3769 | -49.1409 | 71.7453 | -51.1093 | -50.56 | -50.766 | -51.0956 | -50.8118 | -0.11444 | -0.036621 | -0.13733 | 1.0895 | 0.66833 | 0.086975 | 0.78278 | 0.20142 | -0.064087 | 0.004577 | -122.3007 | 0.27924 | 0.23346 | -0.050354 | 0.29755 | 0.013733 | 1.2039 | 122.7631 | 0.34332 | 0.54932 | 122.8638 | 122.8546 | 122.7493 | 122.7905 | -122.9004 | -122.85 | 122.6486 | 0.48523 | 5.4565 | 1.9043
3971.1719 | 123.0011 | -51.0681 | 71.6949 | -0.098725 | -1.9142e-05 | 0.063094 | 0.070113 | -0.00026703 | 0.0013373 | 0.0045672 | -0.028809 | 0.00088875 | 0.0029906 | -0.00079478 | -0.0021469 | -0.0040845 | 0.00088014 | -45.5978 | 71.727 | -51.1276 | 71.6263 | -49.7589 | -51.0315 | -50.386 | -49.1638 | 71.7545 | -51.1047 | -50.5692 | -50.7797 | -51.0864 | -50.7935 | -0.05951 | 0.032044 | -0.068664 | 1.3092 | 0.68207 | 0.036621 | 0.74158 | 0.096131 | -0.036621 | 0.05951 | -122.2641 | 0.28839 | 0.27466 | -0.018311 | 0.31128 | 0.01831 | 1.3687 | 122.7539 | 0.32501 | 0.53558 | 122.8546 | 122.8592 | 122.7951 | 122.8226 | -122.8226 | -122.7997 | 122.6944 | 0.49896 | 5.4703 | 1.9043
3972.1719 | 123.0423 | -51.0452 | 71.727 | -0.12161 | 0.0021171 | 0.061598 | 0.069472 | 0.00080117 | 0.0024053 | 0.0047808 | 0.026123 | 0.0013159 | -0.0023498 | -0.003999 | -0.0027877 | -0.0064343 | 0.00088014 | -45.5704 | 71.7178 | -51.1322 | 71.5393 | -49.8093 | -50.9262 | -50.3265 | -49.1043 | 71.759 | -51.0956 | -50.528 | -50.7477 | -51.0498 | -50.7843 | -0.086975 | -0.009156 | -0.18768 | 1.236 | 0.71869 | 0.11902 | 0.80566 | 0.20599 | -0.050354 | 0.032043 | -122.2549 | 0.29755 | 0.26093 | -0.004578 | 0.31128 | 0.045776 | 1.3229 | 122.6715 | 0.3479 | 0.56763 | 122.85 | 122.8546 | 122.7631 | 122.8043 | -122.8592 | -122.8226 | 122.5845 | 0.51727 | 5.4749 | 1.9409
3973.1719 | 123.0057 | -51.0361 | 71.7407 | -0.052948 | -0.00066014 | 0.061171 | 0.06755 | 0.00016017 | -0.00037171 | 0.002431 | -0.022705 | 0.0011023 | 2.8e-08 | -0.0065626 | -0.0030013 | -0.0060071 | 0.00023934 | -45.5521 | 71.7316 | -51.1368 | 71.5439 | -49.8184 | -50.8987 | -50.3082 | -49.1089 | 71.759 | -51.0956 | -50.528 | -50.7385 | -51.0361 | -50.7843 | -0.10071 | -0.009156 | -0.19684 | 1.2177 | 0.72784 | 0.13733 | 0.82855 | 0.23804 | -0.059509 | 0.01831 | -122.2687 | 0.29755 | 0.25177 | 0 | 0.31128 | 0.059509 | 1.3184 | 122.6807 | 0.35706 | 0.56763 | 122.8683 | 122.8546 | 122.7676 | 122.7951 | -122.8775 | -122.8363 | 122.58 | 0.50812 | 5.484 | 1.9272
3974.1719 | 123.0194 | -51.059 | 71.759 | -0.098725 | -1.9142e-05 | 0.062453 | 0.069045 | -0.0013352 | 0.0019781 | 0.0045672 | -0.0074462 | -0.0014613 | 0.0036316 | -0.0033582 | -0.0019333 | -0.0060071 | 0.0023755 | -45.5566 | 71.7133 | -51.1368 | 71.5256 | -49.8367 | -50.9354 | -50.3494 | -49.0494 | 71.7636 | -51.0818 | -50.5417 | -50.7889 | -51.0956 | -50.8072 | -0.07782 | -0.045776 | -0.23346 | 1.2222 | 0.70953 | 0.1236 | 0.78735 | 0.20142 | -0.022888 | 0.004578 | -122.3007 | 0.27008 | 0.25177 | -0.036621 | 0.27466 | -0.013733 | 1.3 | 122.6624 | 0.29297 | 0.54016 | 122.85 | 122.8455 | 122.7722 | 122.8226 | -122.8958 | -122.8409 | 122.5845 | 0.51727 | 5.5023 | 2.0096
3975.1719 | 122.9919 | -51.0498 | 71.7316 | -0.1445 | 0.0010489 | 0.062025 | 0.068832 | 0.00037377 | 0.0017645 | 0.0071308 | -0.01355 | 0.00046135 | 0.001068 | 0.0013416 | -0.0034287 | -0.0045117 | -0.00082886 | -45.5566 | 71.7407 | -51.1551 | 71.5347 | -49.823 | -50.9308 | -50.3357 | -49.0402 | 71.7865 | -51.0818 | -50.5463 | -50.7568 | -51.091 | -50.8163 | -0.10529 | 0.009156 | -0.19684 | 1.2268 | 0.71411 | 0.11902 | 0.8194 | 0.2243 | -0.032043 | 0.054932 | -122.2778 | 0.29297 | 0.23346 | -0.041198 | 0.2655 | -0.009155 | 1.3321 | 122.6898 | 0.32501 | 0.53558 | 122.8958 | 122.8683 | 122.7905 | 122.8363 | -122.8867 | -122.8134 | 122.5845 | 0.50354 | 5.4932 | 2.0096
3976.1719 | 123.0515 | -51.0178 | 71.7224 | -0.10635 | 0.0010489 | 0.061385 | 0.068832 | -0.00048063 | 0.0013373 | 0.0017902 | -0.0074462 | 3.4148e-05 | -0.00021357 | 0.002196 | -0.0012925 | -0.0055799 | -0.0010425 | -45.5338 | 71.7407 | -51.1276 | 71.5668 | -49.791 | -50.9033 | -50.2991 | -49.0952 | 71.7728 | -51.0498 | -50.4913 | -50.7248 | -51.0223 | -50.766 | -0.10986 | 0.018311 | -0.15564 | 1.2268 | 0.71869 | 0.11444 | 0.82855 | 0.22431 | -0.032044 | 0.050354 | -122.2137 | 0.29297 | 0.25177 | -0.004578 | 0.28381 | 0.027466 | 1.3367 | 122.6944 | 0.32501 | 0.55847 | 122.8683 | 122.8226 | 122.7585 | 122.7905 | -122.85 | -122.7722 | 122.5845 | 0.52643 | 5.484 | 1.9226
3977.1719 | 123.0194 | -51.0269 | 71.7453 | -0.13687 | -0.0015145 | 0.059889 | 0.070113 | -0.003685 | 0.0026191 | 0.0054218 | -0.010498 | 0.00088875 | 0.00085443 | 0.0026232 | -0.0032151 | -0.0062207 | 0.0021619 | -45.5063 | 71.7545 | -51.1276 | 71.5576 | -49.7955 | -50.885 | -50.3082 | -49.0952 | 71.7865 | -51.0956 | -50.5142 | -50.7202 | -51.0452 | -50.7706 | -0.10071 | 0.009156 | -0.18768 | 1.2314 | 0.71869 | 0.14191 | 0.8194 | 0.24262 | -0.068664 | 0.041199 | -122.2595 | 0.3067 | 0.25635 | -0.01831 | 0.32501 | 0.050354 | 1.3321 | 122.6852 | 0.37537 | 0.58136 | 122.8821 | 122.8821 | 122.7814 | 122.8134 | -122.8729 | -122.8409 | 122.5845 | 0.5127 | 5.5206 | 1.9318
3978.1719 | 123.0331 | -51.0178 | 71.7682 | -0.12161 | 0.00062166 | 0.059889 | 0.068404 | 0.0012284 | 0.0021917 | 0.0037128 | -0.022705 | 0.00067495 | -0.0012818 | 0.00091422 | -0.0021469 | -0.0070753 | 0.0017345 | -45.5109 | 71.7499 | -51.123 | 71.5622 | -49.7864 | -50.8987 | -50.3036 | -49.086 | 71.8002 | -51.0956 | -50.4959 | -50.7111 | -51.0315 | -50.7751 | -0.10529 | -0.01831 | -0.20599 | 1.2314 | 0.71411 | 0.11902 | 0.8194 | 0.2243 | -0.07782 | 0.032044 | -122.2641 | 0.3067 | 0.24262 | -0.013733 | 0.32044 | 0.064087 | 1.3367 | 122.6852 | 0.38452 | 0.59967 | 122.8729 | 122.8958 | 122.7676 | 122.818 | -122.8912 | -122.8638 | 122.58 | 0.52185 | 5.5069 | 1.9318
3979.1719 | 123.0423 | -51.0178 | 71.7819 | -0.15213 | 0.00019446 | 0.059676 | 0.068618 | 0.0020828 | 0.0041143 | 0.0045672 | -0.0074462 | 0.0011023 | 0.0019226 | -0.003999 | -0.0038559 | -0.0047253 | 0.0010937 | -45.5154 | 71.759 | -51.1322 | 71.5713 | -49.7818 | -50.8759 | -50.2991 | -49.0814 | 71.8369 | -51.059 | -50.5051 | -50.7294 | -51.0269 | -50.7797 | -0.11444 | -0.022888 | -0.21057 | 1.236 | 0.71869 | 0.14191 | 0.83313 | 0.25635 | -0.041199 | 0.054932 | -122.287 | 0.28839 | 0.23804 | -0.009156 | 0.27924 | 0.032043 | 1.3504 | 122.7036 | 0.32959 | 0.55389 | 122.8912 | 122.8958 | 122.7768 | 122.8546 | -122.9141 | -122.8409 | 122.5891 | 0.5127 | 5.5023 | 1.9363
3980.1719 | 123.0377 | -51.0132 | 71.7499 | -0.10635 | 0.0014761 | 0.061812 | 0.068618 | -0.00069423 | 0.00069649 | 0.002431 | 0.001709 | 0.00088875 | 0.0014954 | -0.001222 | -0.0034287 | -0.0049389 | -0.00018806 | -45.4742 | 71.7682 | -51.0818 | 71.6125 | -49.7086 | -50.8301 | -50.2441 | -49.0128 | 71.8185 | -51.0406 | -50.4456 | -50.6653 | -50.9857 | -50.7202 | -0.068664 | 0.01831 | -0.13733 | 1.3046 | 0.76904 | 0.18311 | 0.83771 | 0.25177 | -0.027465 | 0.068664 | -122.1954 | 0.3479 | 0.29297 | 0.027466 | 0.32043 | 0.054931 | 1.3733 | 122.6944 | 0.37537 | 0.59509 | 122.85 | 122.8592 | 122.7814 | 122.8317 | -122.8317 | -122.7905 | 122.6257 | 0.56763 | 5.5389 | 2.0004
3981.1719 | 123.0148 | -51.0315 | 71.7773 | -0.098725 | 0.00019446 | 0.060316 | 0.068404 | -0.0038986 | 0.0036871 | 0.0052082 | -0.010498 | -0.00039305 | 0.0025634 | -0.0016492 | -0.0047103 | -0.0060071 | -0.0025379 | -45.5063 | 71.759 | -51.1276 | 71.5759 | -49.7681 | -50.8896 | -50.2808 | -49.0723 | 71.8048 | -51.0681 | -50.5005 | -50.7202 | -51.0223 | -50.7523 | -0.096131 | -0.018311 | -0.20142 | 1.2634 | 0.75073 | 0.14191 | 0.84686 | 0.23804 | -0.036621 | 0.027466 | -122.2778 | 0.31128 | 0.27924 | 0.009155 | 0.31586 | 0.045776 | 1.3596 | 122.7036 | 0.3479 | 0.56763 | 122.8867 | 122.8729 | 122.7905 | 122.8363 | -122.905 | -122.8455 | 122.6074 | 0.53101 | 5.5252 | 1.9592
3982.1719 | 123.0286 | -51.0223 | 71.759 | -0.11398 | -0.0015145 | 0.060744 | 0.066909 | 0.0018692 | 0.0015509 | 0.0067036 | -0.0074462 | 3.4148e-05 | 0.0019226 | 0.00070062 | -0.0019333 | -0.0070753 | 0.00045294 | -45.4834 | 71.7682 | -51.1047 | 71.5622 | -49.7681 | -50.8804 | -50.2991 | -49.0768 | 71.7911 | -51.0635 | -50.4776 | -50.7065 | -51.0086 | -50.7568 | -0.082397 | 0.009155 | -0.19684 | 1.2543 | 0.72327 | 0.14191 | 0.80566 | 0.2243 | -0.041199 | 0.032044 | -122.2366 | 0.31586 | 0.2655 | 0.013733 | 0.3067 | 0.054932 | 1.3367 | 122.6669 | 0.35706 | 0.58594 | 122.8729 | 122.8546 | 122.7905 | 122.8134 | -122.8638 | -122.8226 | 122.5845 | 0.54474 | 5.5389 | 1.9455
3983.1719 | 123.0743 | -50.9903 | 71.759 | -0.083466 | 0.00062166 | 0.060957 | 0.070327 | -0.0013352 | 0.00091009 | 0.0067036 | -0.0074462 | 0.00024775 | 0.0021362 | 0.0043322 | -0.0036423 | -0.0051527 | -0.0033923 | -45.4285 | 71.7911 | -51.0681 | 71.6217 | -49.704 | -50.8255 | -50.2258 | -48.9853 | 71.814 | -51.0178 | -50.4364 | -50.6378 | -50.9674 | -50.7156 | -0.07782 | 0.032044 | -0.13733 | 1.2863 | 0.76447 | 0.1648 | 0.84228 | 0.24262 | -0.027466 | 0.054932 | -122.1954 | 0.35248 | 0.27466 | 0.022888 | 0.30212 | 0.050354 | 1.3641 | 122.6898 | 0.37994 | 0.58136 | 122.8592 | 122.8317 | 122.7814 | 122.8043 | -122.8271 | -122.7768 | 122.612 | 0.55389 | 5.5618 | 2.005
3984.1719 | 123.0698 | -50.9857 | 71.7636 | -0.12161 | -0.0019417 | 0.063094 | 0.070113 | 0.0027238 | 0.0032599 | 0.0039264 | 0.001709 | -0.00082025 | 0.00021363 | -0.00058098 | -0.0044967 | -0.0060071 | -0.00018806 | -45.4147 | 71.7865 | -51.0818 | 71.6171 | -49.6948 | -50.8118 | -50.235 | -48.999 | 71.814 | -51.0498 | -50.4547 | -50.6516 | -50.9628 | -50.7202 | -0.09613 | 0.022888 | -0.14648 | 1.2909 | 0.75073 | 0.17395 | 0.84686 | 0.27008 | -0.064087 | 0.050354 | -122.2183 | 0.33417 | 0.2655 | 0.022888 | 0.32959 | 0.086975 | 1.387 | 122.699 | 0.39825 | 0.59509 | 122.8683 | 122.8638 | 122.7722 | 122.7997 | -122.8455 | -122.8134 | 122.6028 | 0.53101 | 5.571 | 1.9867
3985.1719 | 123.0698 | -50.9995 | 71.7865 | -0.045319 | -0.00066014 | 0.061598 | 0.068832 | 0.00080117 | 0.0032599 | 0.002431 | 0.013916 | 0.0015295 | -0.00021357 | 0.00070062 | 0.00041649 | -0.0036573 | -0.00061526 | -45.3781 | 71.7911 | -51.0864 | 71.6721 | -49.6216 | -50.7477 | -50.2304 | -48.9716 | 71.814 | -51.004 | -50.4547 | -50.6424 | -51.0178 | -50.7523 | -0.086975 | 0.004578 | -0.11444 | 1.3779 | 0.76904 | 0.25177 | 0.85602 | 0.33875 | -0.004577 | 0.027466 | -122.2412 | 0.35706 | 0.24719 | -0.01831 | 0.25177 | -0.013733 | 1.4648 | 122.7585 | 0.36163 | 0.54932 | 122.8775 | 122.818 | 122.7905 | 122.8134 | -122.8729 | -122.7905 | 122.6715 | 0.54474 | 5.6213 | 2.0279
3986.1719 | 123.0606 | -50.9949 | 71.7819 | -0.068207 | 0.00040806 | 0.062025 | 0.070113 | -0.0024032 | 0.0017645 | 0.0056354 | -0.0074462 | 0.00067495 | -0.0021362 | -0.0033582 | 0.00063009 | -0.0025891 | 0.0028027 | -45.3781 | 71.7773 | -51.0818 | 71.6812 | -49.6033 | -50.7797 | -50.2258 | -48.9532 | 71.8323 | -51.0361 | -50.4364 | -50.6287 | -51.0361 | -50.7339 | -0.086975 | -0.004577 | -0.10071 | 1.3916 | 0.76904 | 0.21515 | 0.85602 | 0.30212 | -0.041199 | 0.050354 | -122.2183 | 0.36621 | 0.26093 | -0.041199 | 0.30212 | 0 | 1.4786 | 122.7631 | 0.40741 | 0.59967 | 122.8592 | 122.8683 | 122.7722 | 122.8271 | -122.8638 | -122.818 | 122.6761 | 0.55847 | 5.6168 | 2.0416
3987.1719 | 123.056 | -50.9766 | 71.7636 | -0.075836 | -0.0010873 | 0.062239 | 0.068191 | -0.0013352 | 0.00091009 | 0.003072 | 0.023071 | 0.0030249 | 0.0012818 | 5.9824e-05 | -0.0019333 | -0.0057935 | -0.0016833 | -45.3873 | 71.7773 | -51.0544 | 71.6766 | -49.6124 | -50.7797 | -50.2121 | -49.0814 | 71.8414 | -50.9903 | -50.4044 | -50.7294 | -51.004 | -50.7019 | -0.07782 | 0.013733 | -0.086975 | 1.3641 | 0.76447 | 0.19684 | 0.84228 | 0.27466 | -0.013733 | 0.07782 | -122.168 | 0.24719 | 0.27466 | -0.027466 | 0.28839 | -0.013733 | 1.442 | 122.731 | 0.26093 | 0.58594 | 122.8317 | 122.8317 | 122.7539 | 122.818 | -122.818 | -122.7539 | 122.6532 | 0.5722 | 5.5893 | 1.8951
3988.1719 | 123.056 | -50.9628 | 71.7773 | -0.091095 | 0.0023307 | 0.06053 | 0.067763 | -0.00069423 | -0.0010125 | 0.0032856 | 0.001709 | -0.00017945 | 0.00021363 | 0.002196 | -0.00043791 | -0.0066479 | -0.0025379 | -45.3964 | 71.814 | -51.059 | 71.6446 | -49.6628 | -50.8072 | -50.2396 | -48.999 | 71.8231 | -51.0178 | -50.441 | -50.6653 | -50.9445 | -50.6836 | -0.09613 | 0.036621 | -0.13275 | 1.3 | 0.72327 | 0.15564 | 0.8194 | 0.25177 | -0.054931 | 0.045776 | -122.2183 | 0.29755 | 0.27924 | 0.018311 | 0.33417 | 0.073242 | 1.3962 | 122.7036 | 0.35248 | 0.57678 | 122.8729 | 122.8409 | 122.7768 | 122.7859 | -122.8363 | -122.7951 | 122.6074 | 0.52185 | 5.5664 | 1.9638
3989.1719 | 123.0835 | -50.9583 | 71.7773 | -0.091095 | -0.0021555 | 0.06288 | 0.068191 | -0.0017624 | 0.0028327 | 0.0032856 | 0.0047608 | 0.0017431 | 0.00042723 | 0.00027342 | -0.0036423 | -0.0053663 | -0.0025379 | -45.3827 | 71.7957 | -51.1002 | 71.6309 | -49.6719 | -50.8026 | -50.2304 | -48.967 | 71.8231 | -51.0315 | -50.4318 | -50.6378 | -50.9537 | -50.6882 | -0.14191 | 0.01831 | -0.14648 | 1.2863 | 0.72784 | 0.15564 | 0.86975 | 0.29755 | -0.073242 | 0.045776 | -122.2092 | 0.32044 | 0.27008 | 0.004578 | 0.34332 | 0.07782 | 1.4282 | 122.731 | 0.39368 | 0.59967 | 122.8958 | 122.8546 | 122.7539 | 122.7814 | -122.8775 | -122.8088 | 122.5891 | 0.52643 | 5.5756 | 1.9913
3990.1719 | 123.0515 | -50.9674 | 71.7957 | -0.12924 | -1.9142e-05 | 0.06053 | 0.067123 | -0.00026703 | 0.0021917 | 0.0034992 | -0.01355 | 0.00046135 | 0.0014954 | -0.0016492 | 0.0023391 | -0.0053663 | -0.0021107 | -45.3369 | 71.8048 | -51.0452 | 71.6949 | -49.5804 | -50.7431 | -50.1846 | -48.9441 | 71.8552 | -50.9995 | -50.4776 | -50.5692 | -51.004 | -50.7202 | -0.07782 | 0.009156 | -0.10071 | 1.387 | 0.78278 | 0.2243 | 0.8606 | 0.30212 | -0.032044 | 0.05951 | -122.2733 | 0.39825 | 0.24719 | -0.036621 | 0.27924 | -0.004577 | 1.4648 | 122.7402 | 0.4303 | 0.52185 | 122.85 | 122.8546 | 122.7722 | 122.8226 | -122.8409 | -122.7951 | 122.6624 | 0.48981 | 5.6305 | 2.0233
3991.1719 | 123.0423 | -50.9628 | 71.8094 | -0.10635 | 0.0012625 | 0.061385 | 0.067336 | -0.0013352 | 0.0032599 | 0.0037128 | -0.0043946 | 0.0021703 | 0.00064083 | -0.0018628 | -0.0040695 | -0.0053663 | 0.00045294 | -45.3323 | 71.8094 | -51.0361 | 71.7224 | -49.5758 | -50.7248 | -50.1663 | -48.9441 | 71.8277 | -50.9766 | -50.592 | -50.6012 | -50.8987 | -50.6973 | -0.073242 | 0 | -0.086975 | 1.387 | 0.79651 | 0.23804 | 0.86975 | 0.31128 | -0.013732 | 0.018311 | -122.4014 | 0.36163 | 0.2655 | 0.064087 | 0.27923 | 0.077819 | 1.4603 | 122.7585 | 0.37537 | 0.38452 | 122.8455 | 122.8043 | 122.7722 | 122.7905 | -122.8455 | -122.7859 | 122.6852 | 0.37079 | 5.6305 | 2.0187
3992.1719 | 123.0103 | -50.9399 | 71.8414 | -0.091095 | -0.00066014 | 0.060744 | 0.067123 | 0.0010148 | 0.00026909 | 0.0052082 | -0.047119 | -0.0010339 | 0.00042723 | 0.0026232 | -0.0012925 | -0.0057935 | -0.0021107 | -45.3232 | 71.8323 | -51.0452 | 71.6675 | -49.6078 | -50.766 | -50.2121 | -48.9441 | 71.8826 | -50.9903 | -50.4227 | -50.6516 | -50.972 | -50.6973 | -0.10529 | -0.009156 | -0.17395 | 1.3321 | 0.72784 | 0.17395 | 0.83313 | 0.27924 | -0.050354 | 0.041198 | -122.2641 | 0.28839 | 0.24261 | -0.032044 | 0.29297 | 0.01831 | 1.4374 | 122.7127 | 0.33875 | 0.56763 | 122.8775 | 122.8729 | 122.7722 | 122.8226 | -122.8867 | -122.8317 | 122.6074 | 0.51727 | 5.6168 | 1.9958
3993.1719 | 123.0469 | -50.9491 | 71.846 | -0.068207 | 0.00083526 | 0.060957 | 0.069045 | -5.343e-05 | 0.0017645 | 0.0056354 | -0.019653 | -0.00017945 | -0.00021357 | -0.0010084 | -0.0025741 | -0.0064343 | -0.00061526 | -45.3415 | 71.814 | -51.0178 | 71.6766 | -49.5987 | -50.7797 | -50.2029 | -48.9532 | 71.8735 | -50.9903 | -50.4318 | -50.6195 | -50.9537 | -50.6927 | -0.068664 | -0.032043 | -0.16937 | 1.3504 | 0.74616 | 0.16937 | 0.81482 | 0.23804 | -0.041198 | 0.027466 | -122.2778 | 0.32959 | 0.25635 | -0.004577 | 0.29755 | 0.036621 | 1.4191 | 122.6944 | 0.37079 | 0.55847 | 122.8317 | 122.8638 | 122.7631 | 122.8226 | -122.8638 | -122.8363 | 122.6257 | 0.51727 | 5.6076 | 1.9959
3994.1719 | 123.0469 | -50.9262 | 71.8552 | -0.045319 | 0.0023307 | 0.064162 | 0.069259 | -5.343e-05 | 0.0032599 | 0.0043536 | 0.001709 | 0.00067495 | -0.0010682 | -0.00036738 | -0.0023605 | -0.0068615 | -0.00082886 | -45.369 | 71.8048 | -51.0452 | 71.6949 | -49.585 | -50.7294 | -50.1801 | -48.9395 | 71.8643 | -50.9949 | -50.4227 | -50.6195 | -50.9445 | -50.6744 | -0.11902 | -0.050354 | -0.16022 | 1.3412 | 0.74615 | 0.19684 | 0.86517 | 0.31586 | -0.068665 | 0.009155 | -122.2778 | 0.3067 | 0.25177 | -0.018311 | 0.32043 | 0.050354 | 1.4603 | 122.7402 | 0.37537 | 0.5722 | 122.85 | 122.8592 | 122.731 | 122.7905 | -122.9004 | -122.85 | 122.6212 | 0.50354 | 5.5573 | 1.9867
3995.1719 | 123.0835 | -50.9354 | 71.8231 | -0.083466 | -0.00066014 | 0.059889 | 0.066268 | 0.0018692 | 0.0028327 | 0.0062762 | 0.013916 | 0.0021703 | -0.00064077 | -0.0076306 | -0.00065151 | -0.0042981 | -0.0029651 | -45.3369 | 71.8369 | -51.0132 | 71.6766 | -49.5483 | -50.7431 | -50.1892 | -48.9075 | 71.8918 | -50.9949 | -50.3815 | -50.6104 | -50.8987 | -50.6516 | -0.07782 | 0.013733 | -0.14648 | 1.387 | 0.74616 | 0.19226 | 0.82398 | 0.27008 | -0.059509 | 0.068665 | -122.2046 | 0.32501 | 0.28381 | 0.036621 | 0.34332 | 0.09613 | 1.4648 | 122.6898 | 0.38452 | 0.6134 | 122.85 | 122.8867 | 122.7722 | 122.8271 | -122.8363 | -122.818 | 122.612 | 0.55389 | 5.5984 | 2.0279
3996.1719 | 123.0789 | -50.9445 | 71.8369 | -0.12161 | -0.00066014 | 0.060744 | 0.068191 | 0.0012284 | 0.0021917 | 0.0049946 | 0.026123 | -0.00060665 | 0.00042723 | 0.0017688 | -0.0027877 | -0.0079297 | -0.0025379 | -45.3232 | 71.8277 | -51.0178 | 71.6904 | -49.5758 | -50.7385 | -50.1755 | -48.8983 | 71.8872 | -50.9628 | -50.3769 | -50.5966 | -50.9216 | -50.6287 | -0.073242 | -0.009155 | -0.14648 | 1.3687 | 0.76904 | 0.20599 | 0.84228 | 0.27924 | -0.018311 | 0.050354 | -122.2137 | 0.3479 | 0.31586 | 0.022888 | 0.33417 | 0.041199 | 1.442 | 122.7081 | 0.36621 | 0.58594 | 122.8455 | 122.85 | 122.7722 | 122.8317 | -122.8546 | -122.7997 | 122.6349 | 0.56763 | 5.6213 | 2.0462
3997.1719 | 123.0652 | -50.9308 | 71.8323 | -0.098725 | 0.00062166 | 0.062453 | 0.066482 | -0.0011214 | 0.0015509 | 0.0026446 | -0.074585 | 0.0013159 | -0.00085457 | -0.0018628 | -0.0034287 | -0.0064343 | -0.0012561 | -45.282 | 71.8414 | -50.9995 | 71.7087 | -49.411 | -50.3723 | -50.1984 | -48.8342 | 71.8597 | -50.972 | -50.3952 | -50.5737 | -50.9033 | -50.6653 | -0.068665 | 0.009156 | -0.1236 | 1.5198 | 0.73242 | 0.55847 | 0.80109 | 0.62714 | -0.041199 | 0.027466 | -122.2275 | 0.35706 | 0.2655 | 0.027466 | 0.3067 | 0.068665 | 1.5884 | 122.7081 | 0.39825 | 0.57678 | 122.8409 | 122.8317 | 122.7722 | 122.7905 | -122.8317 | -122.8043 | 122.6395 | 0.53558 | 5.6488 | 2.0966
3998.1719 | 123.0789 | -50.9308 | 71.8369 | -0.098725 | 0.0016899 | 0.061171 | 0.069259 | 0.0012284 | 0.0015509 | 0.0047808 | 0.02002 | 0.0032385 | 0.0019226 | -0.001222 | -0.0021469 | -0.0070753 | -0.0055287 | -45.2957 | 71.8414 | -50.9903 | 71.7316 | -49.5163 | -50.7156 | -50.1801 | -48.9029 | 71.8735 | -50.9537 | -50.3403 | -50.6378 | -50.972 | -50.6836 | -0.059509 | 0.004578 | -0.10529 | 1.4145 | 0.75073 | 0.21515 | 0.81024 | 0.27466 | -0.022888 | 0.036621 | -122.1771 | 0.29297 | 0.24719 | -0.041199 | 0.27008 | -0.018311 | 1.474 | 122.7219 | 0.31586 | 0.6134 | 122.8317 | 122.8271 | 122.7722 | 122.8043 | -122.8271 | -122.7905 | 122.6624 | 0.59051 | 5.6351 | 2.0279
3999.1719 | 123.0286 | -50.9308 | 71.8735 | -0.11398 | -0.0015145 | 0.063307 | 0.070968 | -0.0030442 | 0.0024053 | 0.0015766 | -0.0043946 | -0.0010339 | -0.00042717 | -0.00079478 | -0.0021469 | -0.0064343 | 0.0017345 | -45.2957 | 71.8231 | -51.0223 | 71.7087 | -49.5392 | -50.7339 | -50.1892 | -48.9212 | 71.8735 | -50.9674 | -50.4135 | -50.6149 | -50.9308 | -50.6516 | -0.091553 | -0.050354 | -0.16479 | 1.3916 | 0.74158 | 0.19684 | 0.83313 | 0.28839 | -0.036621 | 0 | -122.287 | 0.31586 | 0.27924 | 0 | 0.31586 | 0.036621 | 1.4832 | 122.731 | 0.35248 | 0.55389 | 122.8455 | 122.8409 | 122.7539 | 122.8043 | -122.8958 | -122.8409 | 122.6395 | 0.51727 | 5.6351 | 2.0096
4000.1719 | 123.0103 | -50.9079 | 71.8643 | 0.023346 | 0.0010489 | 0.063307 | 0.06755 | 0.0029374 | 0.0030463 | 0.0067036 | 0.010864 | 0.0013159 | 2.8e-08 | 0.0024096 | -0.0019333 | -0.0064343 | -0.0021107 | -45.5017 | 71.8231 | -51.0452 | 71.6995 | -49.5712 | -50.7019 | -50.148 | -48.9029 | 71.8918 | -50.9491 | -50.3906 | -50.6058 | -50.9125 | -50.6607 | -0.13733 | -0.041199 | -0.16479 | 1.3367 | 0.75989 | 0.20599 | 0.89722 | 0.34332 | -0.041199 | 0.027466 | -122.2549 | 0.30212 | 0.24719 | -0.004578 | 0.28839 | 0.036621 | 1.474 | 122.7448 | 0.34332 | 0.55847 | 122.8683 | 122.8409 | 122.731 | 122.7997 | -122.9095 | -122.8134 | 122.6074 | 0.51727 | 5.4062 | 2.005
4001.1719 | 123.056 | -50.9216 | 71.8826 | -0.075836 | -1.9142e-05 | 0.061385 | 0.067763 | -0.0017624 | -0.0012261 | 0.00414 | -0.03186 | -0.00017945 | 0.00085443 | -0.00079478 | -0.0034287 | -0.0075025 | -0.0042469 | -45.2774 | 71.8323 | -50.9995 | 71.553 | -49.8001 | -50.7202 | -50.1251 | -48.8846 | 71.8964 | -50.9811 | -50.386 | -50.6012 | -50.8896 | -50.6516 | -0.07782 | -0.050354 | -0.32959 | 1.1215 | 0.79651 | 0.20142 | 0.87433 | 0.27924 | -0.059509 | 0.013733 | -122.2687 | 0.32043 | 0.27008 | 0.032044 | 0.32959 | 0.091553 | 1.1993 | 122.5525 | 0.37994 | 0.59509 | 122.8317 | 122.8775 | 122.7539 | 122.818 | -122.8821 | -122.8638 | 122.4747 | 0.53558 | 5.6442 | 2.037
4002.1719 | 123.0469 | -50.9171 | 71.8414 | -0.15213 | -0.00023294 | 0.060744 | 0.065841 | 0.00058737 | 0.0028327 | 0.0056354 | 0.013916 | 0.00088875 | 0.0012818 | -0.00079478 | -0.0021469 | -0.0055799 | 0.00023934 | -45.3003 | 71.846 | -51.0223 | 71.6812 | -49.53 | -50.7294 | -50.1755 | -48.8937 | 71.8735 | -50.9628 | -50.3815 | -50.5829 | -50.885 | -50.6424 | -0.10529 | 0.004577 | -0.16022 | 1.387 | 0.74158 | 0.18768 | 0.84686 | 0.29297 | -0.045777 | 0.032043 | -122.2229 | 0.33417 | 0.27466 | 0.032043 | 0.32043 | 0.07782 | 1.4923 | 122.7036 | 0.37994 | 0.58136 | 122.8683 | 122.8363 | 122.7631 | 122.7905 | -122.8638 | -122.8043 | 122.5983 | 0.53558 | 5.6168 | 2.0233
4003.1719 | 123.0743 | -50.9216 | 71.8643 | -0.13687 | 0.00019446 | 0.060744 | 0.069686 | -0.0043258 | 0.0017645 | 0.0056354 | 0.013916 | 0.00088875 | 0.00042723 | 0.0051868 | -0.0027877 | -0.0068615 | 0.00066654 | -45.3094 | 71.8552 | -50.9857 | 71.6995 | -49.5529 | -50.7385 | -50.1801 | -48.9395 | 71.8964 | -50.9399 | -50.3815 | -50.6104 | -50.9033 | -50.6378 | -0.064087 | -0.009155 | -0.16479 | 1.3687 | 0.74158 | 0.18311 | 0.80566 | 0.24719 | -0.01831 | 0.032043 | -122.2458 | 0.31128 | 0.28381 | 0.018311 | 0.30212 | 0.036621 | 1.4328 | 122.6852 | 0.32959 | 0.55847 | 122.8409 | 122.8363 | 122.7768 | 122.818 | -122.85 | -122.8043 | 122.6212 | 0.54016 | 5.6122 | 1.9821
4004.1719 | 122.9782 | -50.9628 | 71.9101 | -0.13687 | -0.00087374 | 0.061385 | 0.070968 | -0.0028304 | 0.00048269 | 0.0071308 | -0.062378 | 0.0021703 | 0.0036316 | 0.0043322 | -0.0023605 | -0.0053663 | 0.0028027 | -45.3232 | 71.9147 | -51.0361 | 71.6125 | -49.6674 | -50.8163 | -50.2579 | -49.0311 | 71.9467 | -50.9628 | -50.4593 | -50.7065 | -51.0086 | -50.7248 | -0.073242 | 0.004578 | -0.29755 | 1.2955 | 0.70496 | 0.14648 | 0.7782 | 0.21973 | 0 | 0.036621 | -122.3694 | 0.25635 | 0.23804 | -0.045776 | 0.23804 | -0.045776 | 1.3687 | 122.6486 | 0.25635 | 0.50354 | 122.9507 | 122.9095 | 122.8775 | 122.9095 | -122.9462 | -122.8729 | 122.5754 | 0.50354 | 5.6396 | 1.9318
4005.1719 | 123.0743 | -50.885 | 71.8643 | -0.11398 | -0.0034371 | 0.060316 | 0.066695 | 0.00037377 | 0.0015509 | 0.0047808 | 0.026123 | 0.00067495 | 0.0049134 | -0.0018628 | -0.0027877 | -0.0042981 | -0.00061526 | -45.2591 | 71.8552 | -50.9628 | 71.7178 | -49.498 | -50.7019 | -50.1297 | -48.8617 | 71.9055 | -50.9308 | -50.3494 | -50.5508 | -50.8713 | -50.6241 | -0.07782 | -0.009155 | -0.14648 | 1.387 | 0.75531 | 0.18311 | 0.83313 | 0.26093 | -0.045776 | 0.041199 | -122.2137 | 0.33417 | 0.26093 | 0.013733 | 0.3067 | 0.059509 | 1.4648 | 122.6807 | 0.37994 | 0.58136 | 122.818 | 122.8363 | 122.7402 | 122.7905 | -122.8271 | -122.7951 | 122.6028 | 0.53558 | 5.6259 | 2.0233
4006.1719 | 123.0103 | -50.9125 | 71.8964 | -0.098725 | 0.00062166 | 0.060957 | 0.068618 | 0.0020828 | 0.0011237 | 0.0049946 | 0.02002 | -0.00060665 | -0.00085457 | -0.0014356 | -0.0025741 | -0.0060071 | 0.0017345 | -45.2545 | 71.8781 | -50.9766 | 71.7178 | -49.5026 | -50.7156 | -50.1663 | -48.9075 | 71.9009 | -50.9216 | -50.3998 | -50.5966 | -50.9308 | -50.6607 | -0.064086 | -0.01831 | -0.17853 | 1.4099 | 0.74615 | 0.19684 | 0.81024 | 0.26093 | -0.009155 | 0.004578 | -122.2961 | 0.31586 | 0.25177 | -0.01831 | 0.26093 | -0.009155 | 1.474 | 122.6944 | 0.32501 | 0.52185 | 122.8546 | 122.8226 | 122.7905 | 122.8134 | -122.8729 | -122.818 | 122.6303 | 0.5127 | 5.658 | 2.005
4007.1719 | 123.0743 | -50.9079 | 71.8735 | -0.052948 | 0.0012625 | 0.062453 | 0.066054 | -0.0043258 | 0.00069649 | 0.0064898 | 0.044434 | 0.0015295 | 0.001068 | -0.00079478 | -0.0074875 | -0.0096387 | -0.0014697 | -45.2271 | 71.8689 | -50.9674 | 71.7545 | -49.4339 | -50.6653 | -50.1068 | -48.8434 | 71.9238 | -50.9216 | -50.2029 | -50.8438 | -51.0132 | -50.6561 | -0.059509 | -0.004578 | -0.11902 | 1.474 | 0.80109 | 0.24262 | 0.8606 | 0.30212 | -0.013733 | 0.050354 | -122.0764 | 0.064087 | 0.25177 | -0.10529 | 0.2655 | -0.091553 | 1.5335 | 122.7219 | 0.07782 | 0.71869 | 122.8363 | 122.8455 | 122.7768 | 122.8317 | -122.8409 | -122.7951 | 122.6624 | 0.70496 | 5.6808 | 2.0645
4008.1719 | 122.9416 | -50.9033 | 71.9147 | -0.075836 | -0.00066014 | 0.061812 | 0.068618 | -0.00048063 | 0.0019781 | 0.003072 | 0.001709 | 0.0017431 | 0.0032044 | -0.0025036 | -0.0023605 | -0.0060071 | -0.0016833 | -45.2362 | 71.8826 | -50.9628 | 71.7133 | -49.5209 | -50.7156 | -50.1709 | -48.9349 | 71.9467 | -50.9445 | -50.4272 | -50.6424 | -50.9903 | -50.6836 | -0.05951 | -0.032044 | -0.20142 | 1.3824 | 0.73242 | 0.18768 | 0.79193 | 0.24719 | -0.041199 | 0.032043 | -122.3419 | 0.26093 | 0.21973 | -0.086975 | 0.26093 | -0.045776 | 1.442 | 122.6761 | 0.30212 | 0.51727 | 122.8455 | 122.8912 | 122.7859 | 122.85 | -122.8775 | -122.8592 | 122.6166 | 0.47607 | 5.6671 | 1.9684
4009.1719 | 122.937 | -50.9171 | 71.9101 | -0.098725 | 0.00062166 | 0.063734 | 0.069686 | 0.00016017 | 0.0030463 | 0.0077716 | -0.11426 | 0.0019567 | 0.0025634 | 0.0019824 | -0.00086511 | -0.0023755 | -0.0023243 | -45.3049 | 71.9009 | -51.0406 | 71.6171 | -49.6262 | -50.853 | -50.2808 | -49.0356 | 71.9604 | -50.9857 | -50.4868 | -50.7385 | -51.0681 | -50.7385 | -0.1236 | -0.009155 | -0.29297 | 1.2909 | 0.63629 | 0.064087 | 0.75989 | 0.18768 | -0.068665 | 0.050354 | -122.3969 | 0.17853 | 0.17853 | -0.15106 | 0.24719 | -0.082397 | 1.4145 | 122.6578 | 0.24719 | 0.49896 | 122.9416 | 122.9462 | 122.818 | 122.8775 | -122.9507 | -122.8958 | 122.5342 | 0.4303 | 5.6122 | 1.8814
4010.1719 | 123.0331 | -50.9033 | 71.8918 | -0.10635 | -0.00044654 | 0.061598 | 0.067763 | 0.001442 | 0.0032599 | 0.0060626 | 0.035278 | 0.0028113 | -0.00085457 | -0.0044262 | 0.00084389 | -0.0075025 | -0.0031787 | -45.2683 | 71.8826 | -50.972 | 71.6766 | -49.5346 | -50.7568 | -50.1709 | -48.9716 | 71.9284 | -50.9491 | -50.3952 | -50.5966 | -50.9171 | -50.6516 | -0.068665 | -0.009156 | -0.21515 | 1.3687 | 0.73242 | 0.14648 | 0.80109 | 0.21515 | -0.045777 | 0.036621 | -122.287 | 0.3067 | 0.25177 | -0.013733 | 0.29755 | 0.032044 | 1.4374 | 122.6486 | 0.35248 | 0.55389 | 122.8546 | 122.8775 | 122.7859 | 122.8317 | -122.8638 | -122.8409 | 122.58 | 0.50812 | 5.6351 | 1.9318
4011.1719 | 123.0789 | -50.8804 | 71.8735 | -0.13687 | -0.00023294 | 0.062025 | 0.067977 | 0.00016017 | 0.0019781 | 0.0054218 | 0.02002 | 0.0015295 | 0.00042723 | 0.001128 | -0.0032151 | -0.0066479 | -0.0014697 | -45.2408 | 71.8735 | -50.9674 | 71.6995 | -49.498 | -50.7294 | -50.1434 | -48.9075 | 71.9284 | -50.9125 | -50.3494 | -50.5554 | -50.8804 | -50.6012 | -0.086975 | 0 | -0.17395 | 1.3824 | 0.737 | 0.15106 | 0.82397 | 0.23804 | -0.032044 | 0.054932 | -122.2229 | 0.32501 | 0.27924 | 0 | 0.31128 | 0.032044 | 1.4694 | 122.6669 | 0.35706 | 0.56305 | 122.8409 | 122.8409 | 122.7539 | 122.8088 | -122.8409 | -122.7859 | 122.58 | 0.53101 | 5.6396 | 1.973
4012.1719 | 123.0331 | -50.8942 | 71.9147 | -0.11398 | -0.0013009 | 0.062666 | 0.069259 | -0.00026703 | 0.0024053 | 0.0047808 | 0.053589 | 0.0030249 | 0.001068 | -0.005708 | -0.0025741 | -0.0049389 | 0.0034435 | -45.2408 | 71.9055 | -50.9491 | 71.7178 | -49.5026 | -50.7202 | -50.148 | -48.9395 | 71.9193 | -50.9262 | -50.3494 | -50.5692 | -50.8804 | -50.6104 | -0.054932 | -0.009155 | -0.19684 | 1.3916 | 0.74616 | 0.17395 | 0.80109 | 0.22888 | -0.032043 | 0.004577 | -122.2641 | 0.32501 | 0.28381 | 0.013733 | 0.31586 | 0.045776 | 1.4465 | 122.6669 | 0.35706 | 0.57678 | 122.8546 | 122.8455 | 122.7997 | 122.8134 | -122.8638 | -122.8409 | 122.612 | 0.54474 | 5.6534 | 1.9547
4013.1719 | 123.0515 | -50.8713 | 71.9055 | -0.083466 | -0.0010873 | 0.061385 | 0.067123 | 0.0016556 | 0.0032599 | 0.0052082 | 0.02002 | 0.00067495 | 0.00085443 | -0.0014356 | -0.0040695 | -0.0064343 | -0.0044605 | -45.1859 | 71.9009 | -50.9537 | 71.7545 | -49.4431 | -50.6699 | -50.1068 | -48.848 | 71.933 | -50.9079 | -50.3311 | -50.5234 | -50.8255 | -50.5829 | -0.082397 | -0.004578 | -0.15106 | 1.4282 | 0.76447 | 0.20142 | 0.84686 | 0.28381 | -0.036621 | 0.027465 | -122.2366 | 0.3479 | 0.28839 | 0.045777 | 0.32501 | 0.082398 | 1.5106 | 122.7081 | 0.38452 | 0.57678 | 122.8546 | 122.8409 | 122.7722 | 122.8043 | -122.8592 | -122.8134 | 122.6257 | 0.54016 | 5.6854 | 2.0233
4014.1719 | 122.9874 | -50.8759 | 71.9421 | -0.037689 | -0.0017281 | 0.063307 | 0.072463 | 0.00080117 | 0.0019781 | 0.0067036 | -0.059326 | 0.0011023 | 0.00064083 | 0.0049732 | -0.0049241 | -0.0049389 | -0.0023243 | -45.2316 | 71.9421 | -50.9949 | 71.6492 | -49.5941 | -50.7797 | -50.2121 | -49.0036 | 72.0016 | -50.9491 | -50.4089 | -50.6424 | -50.9674 | -50.6836 | -0.11902 | 0 | -0.29297 | 1.2817 | 0.66376 | 0.09613 | 0.78278 | 0.21515 | -0.073243 | 0.059509 | -122.3511 | 0.23346 | 0.19226 | -0.091553 | 0.2655 | -0.01831 | 1.4008 | 122.644 | 0.3067 | 0.54016 | 122.937 | 122.9507 | 122.818 | 122.8775 | -122.937 | -122.8912 | 122.525 | 0.46692 | 5.6442 | 1.8723
4015.1719 | 123.0652 | -50.885 | 71.9238 | -0.075836 | -0.00066014 | 0.062025 | 0.068618 | -0.0041122 | 0.00026909 | 0.00414 | -0.0013428 | 0.0021703 | 0.0032044 | -0.0069898 | -0.0038559 | -0.0077161 | -0.0016833 | -45.1996 | 71.9238 | -50.9537 | 71.7316 | -49.4751 | -50.7156 | -50.1389 | -48.8937 | 71.9193 | -50.9216 | -50.3357 | -50.5508 | -50.8621 | -50.6104 | -0.068664 | 0 | -0.19226 | 1.4099 | 0.74616 | 0.16937 | 0.81482 | 0.23804 | -0.036621 | -0.004578 | -122.2595 | 0.33417 | 0.27466 | 0.022888 | 0.31128 | 0.059509 | 1.4786 | 122.6852 | 0.37079 | 0.58594 | 122.8775 | 122.8409 | 122.8088 | 122.8043 | -122.8775 | -122.8455 | 122.6166 | 0.54932 | 5.6854 | 1.9913
4016.1719 | 123.0103 | -50.8942 | 71.8826 | -0.098725 | -0.00087374 | 0.06288 | 0.0699 | -0.0011214 | 0.00091009 | 0.0060626 | 0.001709 | 0.00067495 | 0.00085443 | -0.0044262 | -0.0027877 | -0.0051527 | 0.0010937 | -45.2179 | 71.9055 | -50.9537 | 71.6858 | -49.53 | -50.7385 | -50.1617 | -48.9716 | 71.9376 | -50.9216 | -50.3815 | -50.592 | -50.9216 | -50.6332 | -0.059509 | 0.022889 | -0.19684 | 1.3641 | 0.73242 | 0.15564 | 0.79193 | 0.21515 | -0.027466 | 0.054932 | -122.2641 | 0.30212 | 0.26093 | -0.027466 | 0.28839 | 0 | 1.4236 | 122.6395 | 0.32959 | 0.54016 | 122.8592 | 122.8592 | 122.7997 | 122.8317 | -122.8363 | -122.8043 | 122.58 | 0.5127 | 5.6763 | 1.9226
4017.1719 | 123.0423 | -50.8759 | 71.8918 | -0.10635 | -0.00066014 | 0.062239 | 0.068618 | -0.00048063 | 0.0036871 | 0.0047808 | 0.0078126 | 0.00024775 | 0.0014954 | -0.0052808 | -0.0036423 | -0.0064343 | -0.0027515 | -45.1996 | 71.9009 | -50.9354 | 71.727 | -49.4705 | -50.7202 | -50.148 | -48.9212 | 71.9421 | -50.9171 | -50.3403 | -50.5463 | -50.8759 | -50.592 | -0.05951 | 0.009155 | -0.16479 | 1.4053 | 0.72784 | 0.15564 | 0.78735 | 0.21515 | -0.041199 | 0.050354 | -122.2321 | 0.32959 | 0.28381 | 0 | 0.32501 | 0.041199 | 1.4648 | 122.6624 | 0.37079 | 0.57678 | 122.8363 | 122.8592 | 122.7768 | 122.818 | -122.8271 | -122.8088 | 122.6028 | 0.53558 | 5.6763 | 1.9546
4018.1719 | 123.0698 | -50.8484 | 71.9238 | -0.098725 | -0.00066014 | 0.062025 | 0.067977 | -0.0026168 | 0.0041143 | 0.0060626 | -0.0043946 | -0.00039305 | -0.00042717 | 0.0028368 | -0.0019333 | -0.0060071 | -0.0021107 | -45.1584 | 71.9238 | -50.9445 | 71.759 | -49.4156 | -50.6744 | -50.1068 | -48.8525 | 71.9559 | -50.8987 | -50.2899 | -50.5005 | -50.8026 | -50.5829 | -0.09613 | 0 | -0.16479 | 1.4328 | 0.74158 | 0.17395 | 0.83771 | 0.27008 | -0.050354 | 0.032044 | -122.2137 | 0.3479 | 0.2655 | 0.045777 | 0.31586 | 0.096131 | 1.5289 | 122.7036 | 0.39826 | 0.60883 | 122.8683 | 122.8546 | 122.7722 | 122.8043 | -122.8683 | -122.8226 | 122.6074 | 0.55847 | 5.69 | 1.9958
4019.1719 | 122.9691 | -50.8804 | 71.9559 | -0.045319 | 0.00019446 | 0.060957 | 0.070968 | 0.0029374 | -0.00058531 | 0.0028582 | -0.068481 | 0.0023839 | 0.001709 | 0.003905 | -0.0025741 | -0.0064343 | 0.0017345 | -45.1904 | 71.9788 | -50.9491 | 71.6721 | -49.5392 | -50.7751 | -50.2167 | -48.9853 | 72.0291 | -50.9033 | -50.3815 | -50.6195 | -50.9491 | -50.6424 | -0.068665 | 0.022888 | -0.28381 | 1.3412 | 0.66376 | 0.10529 | 0.73242 | 0.17395 | -0.022888 | 0.073242 | -122.3373 | 0.26093 | 0.23804 | -0.068665 | 0.26093 | -0.045777 | 1.4099 | 122.6212 | 0.28381 | 0.52185 | 122.9279 | 122.9324 | 122.8592 | 122.9095 | -122.905 | -122.8592 | 122.5525 | 0.49896 | 5.69 | 1.8951
4020.1719 | 123.0194 | -50.8575 | 71.9193 | -0.098725 | 0.0012625 | 0.061812 | 0.066482 | -0.00026703 | 0.00091009 | 0.0015766 | 0.03833 | 0.0011023 | 0.0021362 | 0.00048702 | -0.0051377 | -0.0075025 | 2.554e-05 | -45.1721 | 71.9467 | -50.9262 | 71.759 | -49.4339 | -50.6882 | -50.1114 | -48.8983 | 71.9604 | -50.8942 | -50.322 | -50.5188 | -50.8392 | -50.5783 | -0.068664 | 0.027466 | -0.16022 | 1.4236 | 0.74615 | 0.16937 | 0.81482 | 0.23804 | -0.036621 | 0.041199 | -122.2412 | 0.33874 | 0.27924 | 0.018311 | 0.31586 | 0.054932 | 1.4923 | 122.6852 | 0.37537 | 0.57221 | 122.8729 | 122.8546 | 122.8043 | 122.818 | -122.8455 | -122.8134 | 122.6166 | 0.53558 | 5.6854 | 1.9592
4021.1719 | 123.0194 | -50.853 | 71.9238 | -0.11398 | 0.00083526 | 0.060957 | 0.068191 | -0.0013352 | 0.0013373 | 0.0054218 | 0.029175 | 0.00024775 | 0.00064083 | -0.0042126 | -0.0025741 | -0.0060071 | -0.0016833 | -45.1675 | 71.9284 | -50.9308 | 71.7545 | -49.4339 | -50.6927 | -50.1114 | -48.8892 | 71.9559 | -50.8942 | -50.3265 | -50.5463 | -50.853 | -50.5783 | -0.07782 | 0.004578 | -0.16937 | 1.4191 | 0.74158 | 0.16022 | 0.8194 | 0.23804 | -0.041199 | 0.032044 | -122.2504 | 0.3067 | 0.27466 | 0 | 0.31586 | 0.041199 | 1.4969 | 122.6852 | 0.3479 | 0.56763 | 122.8592 | 122.85 | 122.7814 | 122.8088 | -122.8546 | -122.818 | 122.6074 | 0.52643 | 5.6854 | 1.9638
4022.1719 | 123.0286 | -50.8163 | 71.9421 | -0.052948 | 0.00062166 | 0.059676 | 0.069045 | 0.0020828 | 0.0021917 | 0.00414 | 0.02002 | 0.0017431 | 0.00042723 | -0.00058098 | -0.0042831 | -0.0062207 | -0.0021107 | -45.1309 | 71.9238 | -50.9125 | 71.7957 | -49.3469 | -50.6378 | -50.061 | -48.8159 | 71.9467 | -50.8621 | -50.2853 | -50.4684 | -50.8026 | -50.5463 | -0.096131 | -0.018311 | -0.14648 | 1.4694 | 0.75531 | 0.17853 | 0.85144 | 0.27466 | -0.045777 | 0.004577 | -122.2275 | 0.3479 | 0.27008 | 0.013733 | 0.31586 | 0.05951 | 1.5656 | 122.7081 | 0.39368 | 0.57678 | 122.8363 | 122.8088 | 122.7402 | 122.7631 | -122.8546 | -122.8043 | 122.612 | 0.53101 | 5.6854 | 2.0004
4023.1719 | 122.9919 | -50.8484 | 71.9284 | -0.060578 | 0.0029715 | 0.063734 | 0.069045 | -0.0011214 | 0.0017645 | 0.0032856 | 0.001709 | -0.00082025 | 0.004486 | 0.0017688 | -0.0032151 | -0.0062207 | -0.00040166 | -45.163 | 71.9101 | -50.8896 | 71.7316 | -49.4568 | -50.7248 | -50.1343 | -48.8251 | 71.9742 | -50.8987 | -50.3677 | -50.5554 | -50.9216 | -50.6424 | -0.041198 | -0.018311 | -0.19684 | 1.3916 | 0.71411 | 0.1236 | 0.75531 | 0.16479 | -0.050354 | 0.045776 | -122.2961 | 0.29297 | 0.20599 | -0.073242 | 0.25635 | -0.022888 | 1.4328 | 122.6212 | 0.34332 | 0.53101 | 122.7997 | 122.8729 | 122.7585 | 122.8226 | -122.818 | -122.8271 | 122.58 | 0.48065 | 5.6854 | 2.0233
4024.1719 | 122.9736 | -50.8621 | 71.9284 | -0.13687 | -0.0015145 | 0.060957 | 0.070327 | 0.001442 | 0.0021917 | 0.0045672 | -0.0043946 | -0.00039305 | 0.0029906 | -0.00229 | -0.0053513 | -0.0064343 | 0.0015209 | -45.1813 | 71.933 | -50.9308 | 71.7407 | -49.4522 | -50.7385 | -50.1434 | -48.9212 | 71.9559 | -50.885 | -50.2716 | -50.6882 | -50.9033 | -50.6241 | -0.068664 | 0.004577 | -0.18768 | 1.4099 | 0.71869 | 0.1236 | 0.78735 | 0.19226 | -0.022888 | 0.027466 | -122.2 | 0.17395 | 0.23804 | -0.041198 | 0.26093 | -0.01831 | 1.4786 | 122.6715 | 0.19684 | 0.6134 | 122.8638 | 122.8409 | 122.7951 | 122.818 | -122.8592 | -122.8134 | 122.6028 | 0.59052 | 5.6808 | 1.9409
4025.1719 | 123.0423 | -50.8301 | 71.9696 | -0.13687 | 0.0010489 | 0.060957 | 0.070113 | 0.0010148 | 0.0019781 | 0.0045672 | -0.0013428 | -0.0016749 | 0.00021363 | -0.0035718 | -0.0034287 | -0.0060071 | 0.0036571 | -45.163 | 71.933 | -50.9216 | 71.7361 | -49.4431 | -50.7248 | -50.1251 | -48.912 | 71.9696 | -50.8804 | -50.3357 | -50.5692 | -50.8896 | -50.6699 | -0.091553 | -0.036621 | -0.23346 | 1.387 | 0.70496 | 0.10529 | 0.79651 | 0.19684 | -0.050354 | 0 | -122.3053 | 0.26093 | 0.16022 | -0.059509 | 0.21057 | -0.009155 | 1.4786 | 122.6578 | 0.31128 | 0.54474 | 122.8546 | 122.85 | 122.7631 | 122.7997 | -122.8912 | -122.85 | 122.5662 | 0.49439 | 5.6671 | 1.918
4026.1719 | 123.0469 | -50.8072 | 71.9559 | -0.075836 | 0.0021171 | 0.060103 | 0.069045 | -0.0034714 | 0.0017645 | 0.0056354 | -0.0074462 | 0.0013159 | 0.00085443 | -0.002931 | -0.0021469 | -0.0060071 | 0.00066654 | -45.1126 | 71.965 | -50.9033 | 71.7682 | -49.3927 | -50.6516 | -50.0748 | -48.8571 | 71.9833 | -50.8621 | -50.2762 | -50.5005 | -50.8163 | -50.5508 | -0.09613 | 0.009155 | -0.18768 | 1.4145 | 0.73242 | 0.15564 | 0.82855 | 0.25177 | -0.054932 | 0.027465 | -122.2321 | 0.3067 | 0.25635 | -0.009155 | 0.31128 | 0.045777 | 1.5106 | 122.6715 | 0.36163 | 0.58594 | 122.8683 | 122.8455 | 122.7722 | 122.7905 | -122.8592 | -122.818 | 122.5754 | 0.53101 | 5.6946 | 1.9501
4027.1719 | 123.0423 | -50.8255 | 71.9559 | -0.12161 | 0.0012625 | 0.061598 | 0.066909 | -0.0021896 | 0.0013373 | 0.0032856 | 0.016968 | 0.0013159 | 0.0025634 | -0.0044262 | -0.0034287 | -0.0060071 | -0.0010425 | -45.1172 | 71.965 | -50.9216 | 71.7636 | -49.3652 | -50.6882 | -50.0885 | -48.8571 | 71.9879 | -50.8667 | -50.2899 | -50.5096 | -50.8301 | -50.5463 | -0.096131 | 0.009155 | -0.19226 | 1.4603 | 0.737 | 0.13733 | 0.83313 | 0.23346 | -0.041199 | 0.032043 | -122.2458 | 0.31586 | 0.27923 | -0.004578 | 0.32043 | 0.036621 | 1.5564 | 122.6852 | 0.35705 | 0.57678 | 122.8867 | 122.8546 | 122.7905 | 122.8134 | -122.8775 | -122.8226 | 122.5891 | 0.53558 | 5.7083 | 1.9684
4028.1719 | 123.0286 | -50.8118 | 71.9788 | -0.12161 | -0.0023691 | 0.064803 | 0.07225 | 0.00037377 | 0.0032599 | 0.0056354 | -0.0074462 | -0.0018885 | 0.001709 | -0.0016492 | -0.0053513 | -0.0055799 | -0.0014697 | -45.1218 | 71.9696 | -50.9262 | 71.7636 | -49.379 | -50.679 | -50.0885 | -48.8754 | 71.9833 | -50.8667 | -50.2853 | -50.4959 | -50.8255 | -50.56 | -0.11444 | -0.009156 | -0.21515 | 1.4328 | 0.72327 | 0.13275 | 0.83771 | 0.24719 | -0.054931 | 0.004577 | -122.2641 | 0.31586 | 0.25177 | -0.013732 | 0.3067 | 0.041199 | 1.5472 | 122.6898 | 0.37079 | 0.58136 | 122.8958 | 122.85 | 122.7814 | 122.7951 | -122.905 | -122.8455 | 122.5754 | 0.52643 | 5.69 | 1.9363
4029.1719 | 123.024 | -50.8026 | 71.9742 | -0.075836 | 0.00040806 | 0.06288 | 0.069045 | 0.00037377 | 0.0028327 | 0.0037128 | 0.001709 | 3.4148e-05 | 0.001709 | -0.00079478 | -0.0027877 | -0.0081433 | -0.0044605 | -45.1218 | 71.9559 | -50.8987 | 71.7773 | -49.379 | -50.6973 | -50.0931 | -48.88 | 72.0062 | -50.8759 | -50.3036 | -50.5188 | -50.8392 | -50.5646 | -0.096131 | -0.01831 | -0.19684 | 1.4236 | 0.70953 | 0.10529 | 0.80566 | 0.20142 | -0.073242 | 0.032044 | -122.2778 | 0.28381 | 0.23804 | -0.036621 | 0.31128 | 0.036621 | 1.5198 | 122.6761 | 0.35705 | 0.5722 | 122.8546 | 122.8821 | 122.7585 | 122.8088 | -122.8729 | -122.85 | 122.58 | 0.49896 | 5.6808 | 1.9226
4030.1719 | 123.0103 | -50.8301 | 71.9742 | -0.098725 | -0.0021555 | 0.062239 | 0.069472 | 0.001442 | 0.0021917 | 0.0032856 | -0.0074462 | 0.0015295 | 0.0014954 | 0.0036914 | -0.0044967 | -0.0051527 | 0.0032299 | -45.1309 | 71.9238 | -50.8987 | 71.7636 | -49.379 | -50.6927 | -50.1114 | -48.88 | 72.0062 | -50.8759 | -50.2945 | -50.5005 | -50.8438 | -50.5646 | -0.068665 | -0.050354 | -0.21057 | 1.4511 | 0.71869 | 0.13733 | 0.78735 | 0.20599 | -0.045776 | 0.032044 | -122.2687 | 0.32959 | 0.2655 | -0.013733 | 0.31128 | 0.032043 | 1.5198 | 122.6624 | 0.37537 | 0.58136 | 122.8226 | 122.8821 | 122.7539 | 122.8363 | -122.8729 | -122.85 | 122.5937 | 0.53558 | 5.6992 | 1.9501
4031.1719 | 122.9965 | -50.8163 | 71.965 | -0.091095 | 0.0023307 | 0.058394 | 0.070968 | -0.0028304 | 0.0017645 | 0.0049946 | 0.0047608 | -0.00017945 | 0.00042723 | 0.00091422 | -0.0030013 | -0.0070753 | -0.00040166 | -45.1126 | 71.9467 | -50.9079 | 71.759 | -49.3881 | -50.6973 | -50.1022 | -48.8937 | 72.0016 | -50.8575 | -50.2991 | -50.5508 | -50.8713 | -50.592 | -0.091553 | -0.018311 | -0.20599 | 1.4282 | 0.71411 | 0.11902 | 0.80566 | 0.21057 | -0.041199 | 0.036621 | -122.2641 | 0.2655 | 0.2243 | -0.054932 | 0.2655 | -0.013733 | 1.5198 | 122.6669 | 0.3067 | 0.55847 | 122.8546 | 122.8592 | 122.7631 | 122.818 | -122.8729 | -122.8226 | 122.5754 | 0.51727 | 5.7037 | 1.9226
4032.1719 | 123.0103 | -50.8118 | 71.9696 | -0.12161 | -0.0010873 | 0.059676 | 0.066909 | -0.00048063 | -0.00037171 | 0.005849 | -0.022705 | 0.0011023 | 0.00085443 | -0.0061352 | -0.0012925 | -0.0068615 | -0.0025379 | -45.0943 | 71.9696 | -50.8759 | 71.7636 | -49.3927 | -50.6927 | -50.0839 | -48.8937 | 72.0245 | -50.8667 | -50.2945 | -50.528 | -50.8438 | -50.5737 | -0.064086 | 0 | -0.20599 | 1.4191 | 0.72785 | 0.11902 | 0.79193 | 0.1831 | -0.054931 | 0.054932 | -122.2641 | 0.28381 | 0.23804 | -0.032043 | 0.29297 | 0.022888 | 1.4832 | 122.6395 | 0.33874 | 0.5722 | 122.8455 | 122.8912 | 122.7814 | 122.8363 | -122.8455 | -122.8363 | 122.5754 | 0.51727 | 5.7175 | 1.918
4033.1719 | 123.056 | -50.8072 | 71.9696 | -0.091095 | -0.00087374 | 0.062666 | 0.068404 | -0.00090783 | 0.0036871 | 0.0054218 | 0.0078126 | 0.00024775 | 0.002777 | -0.0048536 | -0.0019333 | -0.0051527 | 0.00088014 | -45.0943 | 71.965 | -50.8759 | 71.8048 | -49.3423 | -50.6516 | -50.0702 | -48.8388 | 72.0245 | -50.8484 | -50.2625 | -50.4776 | -50.8026 | -50.5371 | -0.068664 | -0.004577 | -0.16479 | 1.4648 | 0.737 | 0.15564 | 0.80566 | 0.2243 | -0.041199 | 0.054932 | -122.2321 | 0.32959 | 0.27008 | 0.004578 | 0.31128 | 0.045777 | 1.5335 | 122.6807 | 0.37079 | 0.58594 | 122.8409 | 122.8729 | 122.7722 | 122.8317 | -122.8455 | -122.818 | 122.612 | 0.54474 | 5.7129 | 1.9684
4034.1719 | 123.0377 | -50.798 | 71.965 | -0.10635 | -0.00066014 | 0.059889 | 0.067763 | 0.0018692 | 0.0011237 | 0.0056354 | -0.0043946 | 0.0021703 | 0.00085443 | -0.00015378 | -0.0036423 | -0.0066479 | -0.00040166 | -45.0806 | 71.9742 | -50.8713 | 71.7911 | -49.3378 | -50.679 | -50.0702 | -48.8525 | 72.0383 | -50.853 | -50.267 | -50.4822 | -50.8163 | -50.5371 | -0.073242 | 0.009155 | -0.17395 | 1.4603 | 0.72785 | 0.11902 | 0.80109 | 0.19226 | -0.054931 | 0.073242 | -122.2321 | 0.31586 | 0.26093 | -0.01831 | 0.31586 | 0.036621 | 1.5335 | 122.6624 | 0.37079 | 0.58594 | 122.8455 | 122.8912 | 122.7722 | 122.8363 | -122.8363 | -122.818 | 122.5891 | 0.53101 | 5.7175 | 1.9455
4035.1719 | 123.0377 | -50.8118 | 71.9742 | -0.075836 | -0.00066014 | 0.061812 | 0.066482 | 0.00058737 | -0.00079891 | 0.003072 | 0.0047608 | 0.0015295 | 0.001068 | 0.0030506 | -0.00086511 | -0.0072889 | -0.0065967 | -45.0851 | 71.9696 | -50.8804 | 71.7773 | -49.3286 | -50.6653 | -50.0931 | -48.8617 | 72.02 | -50.853 | -50.2808 | -50.4868 | -50.8301 | -50.5417 | -0.068664 | -0.004578 | -0.19684 | 1.4832 | 0.71869 | 0.14648 | 0.78735 | 0.21515 | -0.041198 | 0.045776 | -122.2549 | 0.32501 | 0.27008 | -0.01831 | 0.31128 | 0.022888 | 1.5518 | 122.6578 | 0.36621 | 0.5722 | 122.85 | 122.8729 | 122.7814 | 122.8317 | -122.8546 | -122.8271 | 122.5891 | 0.53101 | 5.7266 | 1.9501
4036.1719 | 123.0286 | -50.8072 | 71.9879 | -0.037689 | -0.0017281 | 0.060957 | 0.069259 | -0.00069423 | 0.0017645 | 0.0026446 | -0.010498 | 3.4148e-05 | 0.001068 | 0.0017688 | -0.0042831 | -0.0077161 | -0.0021107 | -45.0806 | 71.9604 | -50.885 | 71.7773 | -49.3561 | -50.6607 | -50.0885 | -48.8434 | 72.0062 | -50.8392 | -50.2945 | -50.5005 | -50.8118 | -50.5417 | -0.07782 | -0.027466 | -0.21057 | 1.4511 | 0.71869 | 0.14648 | 0.79651 | 0.2243 | -0.032043 | 0.018311 | -122.2824 | 0.3067 | 0.2655 | -0.004578 | 0.29755 | 0.027465 | 1.5289 | 122.6624 | 0.33875 | 0.54474 | 122.8455 | 122.8455 | 122.7676 | 122.8134 | -122.8729 | -122.8271 | 122.5845 | 0.5127 | 5.7266 | 1.9638
4037.1719 | 123.0103 | -50.8118 | 72.0062 | -0.13687 | 0.0010489 | 0.062453 | 0.069686 | 0.0010148 | 0.0028327 | 0.0043536 | -0.025757 | 0.0028113 | -0.00021357 | 0.001128 | -0.0017197 | -0.0055799 | 0.0021619 | -45.0806 | 71.9833 | -50.8804 | 71.7957 | -49.3378 | -50.6927 | -50.0931 | -48.8617 | 72.02 | -50.8438 | -50.2945 | -50.5234 | -50.8392 | -50.5554 | -0.068664 | -0.022889 | -0.21057 | 1.474 | 0.71869 | 0.11902 | 0.78735 | 0.18768 | -0.032043 | 0.013732 | -122.3007 | 0.28839 | 0.25635 | -0.027465 | 0.28839 | 0.004578 | 1.5427 | 122.6761 | 0.32044 | 0.54932 | 122.8638 | 122.8638 | 122.7951 | 122.8317 | -122.8867 | -122.85 | 122.6074 | 0.51727 | 5.7312 | 1.9501
4038.1719 | 122.9874 | -50.7843 | 71.9925 | -0.13687 | -0.00044654 | 0.06053 | 0.068191 | -0.0015488 | 0.0021917 | 0.003072 | -0.019653 | 0.00088875 | 0.002777 | 0.0049732 | -0.0030013 | -0.0066479 | 0.0010937 | -45.076 | 72.0016 | -50.8621 | 71.7865 | -49.2188 | -50.6424 | -50.1617 | -48.8846 | 72.0016 | -50.8621 | -50.2945 | -50.5051 | -50.8438 | -50.5554 | -0.07782 | 0.009155 | -0.20599 | 1.5656 | 0.62256 | 0.14191 | 0.70038 | 0.21973 | -0.07782 | 0.009155 | -122.287 | 0.27924 | 0.22888 | -0.059509 | 0.3067 | 0.018311 | 1.6434 | 122.6486 | 0.35706 | 0.56763 | 122.8638 | 122.8638 | 122.7859 | 122.7859 | -122.8546 | -122.8546 | 122.5708 | 0.48981 | 5.7083 | 1.8997
4039.1719 | 123.0148 | -50.8026 | 71.9833 | -0.068207 | 0.0014761 | 0.060957 | 0.069045 | -0.0028304 | 0.0019781 | 0.0034992 | -0.028809 | -0.0027429 | 0.0023498 | 5.9824e-05 | -0.0019333 | -0.0064343 | -0.0027515 | -45.0714 | 71.9879 | -50.8575 | 71.7819 | -49.324 | -50.6744 | -50.0793 | -48.7885 | 72.0428 | -50.8575 | -50.267 | -50.528 | -50.8621 | -50.5554 | -0.054932 | 0.004578 | -0.20142 | 1.4786 | 0.72327 | 0.12817 | 0.7782 | 0.18311 | -0.054932 | 0.05951 | -122.2504 | 0.27466 | 0.24719 | -0.05951 | 0.30212 | -0.004578 | 1.5335 | 122.6395 | 0.32959 | 0.59051 | 122.8455 | 122.9004 | 122.7905 | 122.8455 | -122.8409 | -122.8409 | 122.5845 | 0.53558 | 5.7312 | 2.0142
4040.1719 | 123.056 | -50.7568 | 72.0016 | -0.060578 | -0.00023294 | 0.060957 | 0.070968 | -0.00026703 | 0.0024053 | 0.0043536 | 0.013916 | 0.00067495 | 0.001068 | 0.0015552 | -0.0038559 | -0.0049389 | 0.0019483 | -45.0302 | 72.02 | -50.8438 | 71.8506 | -49.2233 | -50.6012 | -50.0015 | -48.7473 | 72.052 | -50.8301 | -50.2029 | -50.4181 | -50.7614 | -50.4913 | -0.086975 | 0.01831 | -0.15106 | 1.5335 | 0.75531 | 0.15564 | 0.84229 | 0.24262 | -0.073242 | 0.050354 | -122.2046 | 0.33875 | 0.2655 | -0.004578 | 0.33875 | 0.068664 | 1.6205 | 122.6944 | 0.41199 | 0.62714 | 122.8638 | 122.8821 | 122.7768 | 122.8088 | -122.8455 | -122.8317 | 122.6074 | 0.55389 | 5.7266 | 2.0096
4041.1719 | 123.0469 | -50.7523 | 72.0062 | -0.11398 | -1.9142e-05 | 0.063734 | 0.066909 | 0.0022964 | -0.0010125 | 0.0054218 | -0.0043946 | 0.00024775 | 0.0021362 | -0.0031446 | -0.0021469 | -0.0062207 | -0.0012561 | -45.0027 | 72.0016 | -50.853 | 71.8506 | -49.2233 | -50.5966 | -50.0244 | -48.7701 | 72.0566 | -50.8209 | -50.2167 | -50.4318 | -50.7431 | -50.4822 | -0.10071 | -0.004578 | -0.15564 | 1.5289 | 0.72784 | 0.15564 | 0.82855 | 0.25635 | -0.068665 | 0.050354 | -122.2229 | 0.32043 | 0.27008 | 0.009155 | 0.33875 | 0.07782 | 1.6296 | 122.7036 | 0.3891 | 0.60425 | 122.8546 | 122.8775 | 122.7539 | 122.8088 | -122.8592 | -122.8271 | 122.6028 | 0.53558 | 5.7495 | 1.9821
4042.1719 | 123.0148 | -50.7614 | 72.0154 | -0.083466 | 0.0016899 | 0.062025 | 0.0699 | -0.0011214 | -0.0020807 | 0.00414 | 0.001709 | 0.00088875 | 0.00085443 | -0.0031446 | -0.0038559 | -0.0070753 | -0.0042469 | -45.0577 | 71.9925 | -50.8713 | 71.8002 | -49.2874 | -50.6516 | -50.0656 | -48.8342 | 72.0291 | -50.8209 | -50.2441 | -50.4776 | -50.8026 | -50.5463 | -0.10986 | -0.022888 | -0.21515 | 1.474 | 0.6958 | 0.10986 | 0.80566 | 0.21973 | -0.059509 | 0.013733 | -122.2595 | 0.28381 | 0.21515 | -0.041198 | 0.27466 | 0.018311 | 1.5839 | 122.6715 | 0.34332 | 0.57678 | 122.8638 | 122.85 | 122.7539 | 122.7905 | -122.8867 | -122.8363 | 122.5616 | 0.51727 | 5.7037 | 1.9272
4043.1719 | 123.0377 | -50.798 | 72.0108 | -0.068207 | -1.9142e-05 | 0.064375 | 0.067336 | -0.001976 | 0.0043281 | 0.0052082 | -0.0074462 | -0.00082025 | -0.00042717 | 0.0032642 | -0.0042831 | -0.0064343 | -0.0033923 | -44.9249 | 72.0062 | -50.8575 | 71.7911 | -49.2508 | -50.6653 | -50.0885 | -48.8297 | 72.0337 | -50.8163 | -50.267 | -50.4868 | -50.8118 | -50.528 | -0.059509 | -0.004577 | -0.21973 | 1.5472 | 0.70953 | 0.13275 | 0.76904 | 0.19226 | -0.01831 | 0.022888 | -122.2778 | 0.31128 | 0.27008 | -0.013733 | 0.28839 | 0.004577 | 1.6068 | 122.6486 | 0.32959 | 0.54932 | 122.8638 | 122.85 | 122.8043 | 122.8317 | -122.8683 | -122.8271 | 122.5891 | 0.53101 | 5.8731 | 1.9684
4044.1719 | 123.0011 | -50.7797 | 71.9925 | -0.075836 | 0.00019446 | 0.061812 | 0.070113 | 0.00251 | 0.0034735 | 0.0054218 | -0.03186 | 0.00046135 | 0.00042723 | 0.0017688 | -0.0023605 | -0.0053663 | -0.0046741 | -45.0394 | 71.9925 | -50.8621 | 71.8094 | -49.2554 | -50.6699 | -50.0656 | -48.8525 | 72.0383 | -50.8301 | -50.2579 | -50.4959 | -50.8347 | -50.528 | -0.082398 | 0 | -0.18311 | 1.5244 | 0.71411 | 0.10986 | 0.79651 | 0.19226 | -0.050354 | 0.045776 | -122.2504 | 0.28381 | 0.25177 | -0.054932 | 0.30212 | -0.004578 | 1.6068 | 122.6715 | 0.33417 | 0.5722 | 122.8546 | 122.8683 | 122.7722 | 122.818 | -122.8546 | -122.8226 | 122.5891 | 0.52185 | 5.7404 | 1.9272
4045.1719 | 123.0331 | -50.7797 | 72.0291 | -0.13687 | 0.00040806 | 0.060957 | 0.070754 | -0.0015488 | 0.0017645 | 0.005849 | -0.019653 | 0.0028113 | -0.00021357 | -0.0031446 | -0.0023605 | -0.0064343 | -0.0016833 | -45.0211 | 72.0108 | -50.8255 | 71.8094 | -49.2508 | -50.6516 | -50.0565 | -48.8159 | 72.052 | -50.8163 | -50.2533 | -50.5005 | -50.8438 | -50.5371 | -0.045776 | -0.018311 | -0.21973 | 1.5289 | 0.72327 | 0.12817 | 0.76904 | 0.17395 | -0.036621 | 0.022888 | -122.2824 | 0.27924 | 0.24262 | -0.064087 | 0.27924 | -0.027466 | 1.5747 | 122.6349 | 0.31586 | 0.56305 | 122.8363 | 122.8683 | 122.7905 | 122.8317 | -122.8546 | -122.8455 | 122.5891 | 0.52643 | 5.7587 | 1.9638
4046.1719 | 123.0286 | -50.766 | 72.02 | -0.17502 | -0.00087374 | 0.061812 | 0.068832 | -5.343e-05 | 0.00091009 | 0.0067036 | -0.0013428 | 0.0023839 | 0.001709 | 0.0017688 | -0.0030013 | -0.0070753 | 0.0038709 | -45.0027 | 72.0062 | -50.8438 | 71.8414 | -49.2188 | -50.6332 | -50.0427 | -48.8068 | 72.0978 | -50.7889 | -50.2304 | -50.4364 | -50.7706 | -50.5188 | -0.07782 | -0.013732 | -0.17853 | 1.5472 | 0.72327 | 0.13275 | 0.80109 | 0.21057 | -0.022888 | 0.07782 | -122.2504 | 0.32959 | 0.24719 | -0.004578 | 0.27008 | 0.01831 | 1.6251 | 122.6852 | 0.35248 | 0.55847 | 122.85 | 122.8867 | 122.7722 | 122.8638 | -122.8638 | -122.8088 | 122.6074 | 0.53558 | 5.7632 | 1.9592
4047.1719 | 123.0103 | -50.7477 | 72.0474 | -0.12924 | -0.0010873 | 0.060103 | 0.070113 | 0.0027238 | 0.00069649 | 0.005849 | -0.03186 | 0.00088875 | -0.00085457 | -0.0010084 | -0.0034287 | -0.0051527 | -0.0010425 | -44.9799 | 72.0108 | -50.8392 | 71.8231 | -49.2188 | -50.6241 | -50.029 | -48.8022 | 72.0612 | -50.7935 | -50.2304 | -50.4272 | -50.7751 | -50.5005 | -0.091552 | -0.036621 | -0.2243 | 1.5289 | 0.71869 | 0.1236 | 0.81024 | 0.21515 | -0.045776 | 0.013733 | -122.2778 | 0.32044 | 0.24719 | -0.027465 | 0.29297 | 0.018311 | 1.6205 | 122.6624 | 0.36621 | 0.56305 | 122.85 | 122.8546 | 122.7585 | 122.8088 | -122.8867 | -122.8409 | 122.5708 | 0.51727 | 5.7678 | 1.9455
4048.1719 | 123.0377 | -50.7202 | 72.0337 | -0.11398 | 0.0021171 | 0.061598 | 0.069686 | 0.0040054 | 0.00069649 | 0.0064898 | 0.023071 | 0.00088875 | -0.00064077 | -0.0027174 | -0.0027877 | -0.0045117 | -0.0027515 | -44.989 | 72.0428 | -50.8255 | 71.8597 | -49.1776 | -50.5783 | -50.0015 | -48.761 | 72.0657 | -50.7797 | -50.2075 | -50.4135 | -50.7431 | -50.473 | -0.10528 | 0.009156 | -0.17395 | 1.5427 | 0.71869 | 0.14191 | 0.82397 | 0.24719 | -0.059509 | 0.032044 | -122.2412 | 0.3067 | 0.24719 | -0.022888 | 0.3067 | 0.036621 | 1.6479 | 122.6852 | 0.36621 | 0.5722 | 122.8683 | 122.8455 | 122.7631 | 122.786 | -122.8592 | -122.8134 | 122.58 | 0.5127 | 5.7312 | 1.9592
4049.1719 | 123.0377 | -50.7614 | 72.0291 | -0.12161 | 0.00083526 | 0.063521 | 0.066695 | -0.00090783 | 0.0036871 | 0.0047808 | -0.041016 | 0.0015295 | 0.0023498 | 0.0036914 | -0.0025741 | -0.0049389 | 0.00088014 | -44.989 | 72.0337 | -50.8392 | 71.8231 | -49.2279 | -50.6516 | -50.0336 | -48.8159 | 72.0428 | -50.8072 | -50.2258 | -50.4639 | -50.7797 | -50.5051 | -0.077819 | 0.004577 | -0.20599 | 1.5335 | 0.72785 | 0.10986 | 0.80566 | 0.18768 | -0.045776 | 0.013733 | -122.2549 | 0.29755 | 0.25635 | -0.01831 | 0.30212 | 0.027466 | 1.6113 | 122.6624 | 0.34332 | 0.58136 | 122.8729 | 122.85 | 122.7951 | 122.8043 | -122.8683 | -122.8363 | 122.5845 | 0.53558 | 5.7724 | 1.9455
4050.1719 | 123.0331 | -50.7797 | 72.052 | -0.091095 | -1.9142e-05 | 0.059676 | 0.069259 | -0.0015488 | 0.0028327 | 0.00414 | -0.016602 | 0.00046135 | 2.8e-08 | -0.00058098 | -0.0040695 | -0.0068615 | -0.0016833 | -44.9844 | 72.0383 | -50.8163 | 71.8414 | -49.1501 | -50.5005 | -50.0244 | -48.8297 | 72.0657 | -50.7797 | -50.2441 | -50.4547 | -50.798 | -50.5051 | -0.036621 | -0.013733 | -0.21057 | 1.6296 | 0.75531 | 0.27924 | 0.79193 | 0.31586 | 0 | 0.013733 | -122.2961 | 0.32501 | 0.27466 | -0.018311 | 0.27466 | -0.018311 | 1.6663 | 122.6578 | 0.32501 | 0.53558 | 122.8546 | 122.8455 | 122.818 | 122.8455 | -122.8683 | -122.8317 | 122.6212 | 0.53558 | 5.7953 | 1.9501
4051.1719 | 123.0057 | -50.7523 | 72.0566 | -0.091095 | 0.00040806 | 0.062666 | 0.068191 | 0.00058737 | 0.0019781 | 0.0034992 | -0.03186 | -0.0012477 | 0.001709 | 0.001128 | -0.0010787 | -0.0068615 | 0.0023755 | -44.9524 | 72.0154 | -50.8163 | 71.846 | -49.173 | -50.6241 | -50.0153 | -48.7747 | 72.0657 | -50.7797 | -50.235 | -50.473 | -50.7935 | -50.5142 | -0.064087 | -0.041199 | -0.21057 | 1.5793 | 0.737 | 0.12817 | 0.80109 | 0.19226 | -0.027466 | 0.009155 | -122.2916 | 0.27924 | 0.23804 | -0.041199 | 0.2655 | -0.013733 | 1.6434 | 122.6624 | 0.3067 | 0.54474 | 122.8317 | 122.8455 | 122.7676 | 122.818 | -122.8729 | -122.8363 | 122.5983 | 0.51727 | 5.7999 | 1.9775
4052.1719 | 122.9965 | -50.7523 | 72.0108 | -0.12924 | 0.0016899 | 0.062239 | 0.070327 | -0.0017624 | 0.00069649 | 0.0054218 | -0.010498 | 0.00046135 | 0.0019226 | -0.0025036 | -0.00043791 | -0.0055799 | -0.0059559 | -44.9936 | 72.0474 | -50.8438 | 71.846 | -49.1776 | -50.6104 | -50.0381 | -48.8113 | 72.0749 | -50.7843 | -50.2396 | -50.3586 | -50.8575 | -50.5508 | -0.091553 | 0.036621 | -0.16479 | 1.5747 | 0.71411 | 0.14191 | 0.80566 | 0.23346 | -0.032044 | 0.064087 | -122.2504 | 0.39368 | 0.20142 | -0.10529 | 0.23346 | -0.073242 | 1.6663 | 122.6898 | 0.42572 | 0.54474 | 122.8912 | 122.8592 | 122.7997 | 122.8271 | -122.8546 | -122.7951 | 122.5983 | 0.5127 | 5.7587 | 1.9409
4053.1719 | 122.9324 | -50.7202 | 72.0428 | -0.11398 | 0.00019446 | 0.062239 | 0.068191 | 0.00058737 | 0.0026191 | 0.0052082 | -0.034912 | 0.00046135 | 0.00042723 | 0.001128 | -0.0032151 | -0.0057935 | -0.0016833 | -44.9707 | 72.0428 | -50.798 | 71.8506 | -49.1638 | -50.6104 | -50.0336 | -48.8022 | 72.0795 | -50.7935 | -50.2213 | -50.441 | -50.7797 | -50.5051 | -0.07782 | 0 | -0.19226 | 1.5564 | 0.68665 | 0.10986 | 0.76447 | 0.18768 | -0.073242 | 0.036621 | -122.2641 | 0.27924 | 0.21515 | -0.059509 | 0.28839 | 0.013733 | 1.6342 | 122.6486 | 0.35248 | 0.5722 | 122.8409 | 122.8729 | 122.7631 | 122.7997 | -122.8409 | -122.8363 | 122.5708 | 0.49896 | 5.7495 | 1.918
4054.1719 | 122.9782 | -50.7385 | 72.0337 | 0.29037 | -1.9142e-05 | 0.06053 | 0.068191 | -0.0011214 | 0.0021917 | 0.003072 | 0.0047608 | 0.0015295 | 0.00021363 | 0.0049732 | -0.0012925 | -0.0070753 | 0.00023934 | -45.0256 | 72.0291 | -50.798 | 71.8369 | -49.1684 | -50.6012 | -50.0153 | -48.7793 | 72.1115 | -50.7706 | -50.2029 | -50.4227 | -50.7614 | -50.4776 | -0.05951 | -0.004577 | -0.19684 | 1.5701 | 0.72327 | 0.13733 | 0.78278 | 0.19684 | -0.032044 | 0.07782 | -122.2366 | 0.31586 | 0.26093 | -0.022889 | 0.29297 | 0.009155 | 1.6296 | 122.6349 | 0.3479 | 0.56763 | 122.8271 | 122.8821 | 122.7676 | 122.85 | -122.8317 | -122.8043 | 122.5754 | 0.53558 | 5.7129 | 1.9592
4055.1719 | 122.9324 | -50.7248 | 72.1207 | -0.060578 | -0.00023294 | 0.063521 | 0.070113 | 0.00058737 | 0.00091009 | 0.0047808 | -0.050171 | 0.0013159 | -0.00064077 | 0.0030506 | -0.0036423 | -0.0051527 | -0.00018806 | -44.9432 | 72.1252 | -50.8072 | 71.8231 | -49.2142 | -50.6332 | -50.0702 | -48.8068 | 72.1436 | -50.7797 | -50.2487 | -50.473 | -50.8118 | -50.5234 | -0.082398 | 0.004577 | -0.29755 | 1.5106 | 0.6546 | 0.091552 | 0.737 | 0.17395 | -0.054932 | 0.022888 | -122.3694 | 0.25177 | 0.20142 | -0.086976 | 0.25635 | -0.032044 | 1.593 | 122.6303 | 0.3067 | 0.53101 | 122.9324 | 122.9233 | 122.85 | 122.8683 | -122.9279 | -122.9004 | 122.5479 | 0.47607 | 5.7816 | 1.918
4056.1719 | 122.9782 | -50.6927 | 72.0428 | -0.091095 | 0.0016899 | 0.062025 | 0.068191 | 0.00251 | -0.0012261 | 0.0032856 | 0.0078126 | 0.0013159 | 0.00042723 | -0.0014356 | -0.0019333 | -0.0066479 | 0.0019483 | -44.9387 | 72.0749 | -50.7843 | 71.9238 | -49.054 | -50.6607 | -50.0565 | -48.793 | 72.0932 | -50.7614 | -50.2167 | -50.4227 | -50.7751 | -50.4639 | -0.091553 | 0.032043 | -0.11902 | 1.6388 | 0.63629 | 0.032043 | 0.72784 | 0.1236 | -0.068665 | 0.050354 | -122.2595 | 0.27008 | 0.22888 | -0.082397 | 0.29755 | -0.013732 | 1.7303 | 122.7081 | 0.33875 | 0.54474 | 122.8592 | 122.8546 | 122.7676 | 122.7859 | -122.8271 | -122.8043 | 122.6166 | 0.47607 | 5.7541 | 1.8997
4057.1719 | 123.0103 | -50.7339 | 72.0657 | -0.12924 | 0.0010489 | 0.059035 | 0.067123 | 0.0012284 | 0.00026909 | 0.00414 | -0.03186 | -0.0010339 | 0.00085443 | -0.001222 | -0.0034287 | -0.0057935 | 0.0019483 | -44.9478 | 72.0795 | -50.7797 | 71.8643 | -49.118 | -50.6012 | -49.8734 | -48.7839 | 72.1024 | -50.7797 | -50.2213 | -50.4181 | -50.7614 | -50.4959 | -0.045776 | 0.013733 | -0.20142 | 1.6159 | 0.8606 | 0.13275 | 0.90637 | 0.17853 | -0.045776 | 0.036621 | -122.287 | 0.31586 | 0.23804 | -0.027466 | 0.28381 | 0.01831 | 1.6617 | 122.644 | 0.36163 | 0.55847 | 122.8592 | 122.8821 | 122.8134 | 122.8363 | -122.8455 | -122.8455 | 122.5983 | 0.5127 | 5.7861 | 1.9501
4058.1719 | 122.9828 | -50.7202 | 72.0703 | -0.10635 | 0.0014761 | 0.061812 | 0.070113 | -0.0021896 | 0.00069649 | 0.0056354 | -0.047119 | 0.0013159 | 0.00085443 | 0.00048702 | 0.00041649 | -0.0038709 | 0.0019483 | -44.9203 | 72.052 | -50.766 | 71.8735 | -49.086 | -50.5875 | -50.0015 | -48.7381 | 72.1024 | -50.7614 | -50.1846 | -50.4501 | -50.7614 | -50.4776 | -0.045776 | -0.01831 | -0.19684 | 1.6342 | 0.71869 | 0.13275 | 0.76447 | 0.17853 | -0.041199 | 0.032044 | -122.2549 | 0.27008 | 0.24262 | -0.041199 | 0.28381 | 0 | 1.68 | 122.6395 | 0.31128 | 0.57678 | 122.818 | 122.8638 | 122.7722 | 122.8226 | -122.8363 | -122.8317 | 122.5937 | 0.53558 | 5.7999 | 1.9821
4059.1719 | 123.0011 | -50.7202 | 72.0795 | -0.13687 | 0.0023307 | 0.062025 | 0.069686 | -0.0066756 | 0.0024053 | 0.003072 | -0.010498 | 0.0011023 | 0.0029906 | 0.002196 | -0.0066329 | -0.0049389 | 0.0010937 | -44.9158 | 72.084 | -50.7889 | 71.8643 | -49.118 | -50.5829 | -49.9969 | -48.761 | 72.1069 | -50.7568 | -50.2258 | -50.441 | -50.7614 | -50.4776 | -0.068664 | 0.004577 | -0.21515 | 1.6022 | 0.72327 | 0.13733 | 0.79193 | 0.20599 | -0.036621 | 0.027466 | -122.3053 | 0.27924 | 0.24262 | -0.041199 | 0.27924 | -0.004578 | 1.6708 | 122.6532 | 0.31586 | 0.53101 | 122.8729 | 122.8638 | 122.8043 | 122.8271 | -122.8683 | -122.8363 | 122.5845 | 0.49439 | 5.8044 | 1.9592
4060.1719 | 122.8958 | -50.6882 | 72.1527 | -0.060578 | 0.00083526 | 0.061171 | 0.070968 | -0.0017624 | 0.0011237 | 0.00050839 | -0.03186 | 0.0028113 | 0.0032044 | 0.002196 | -0.0030013 | -0.0053663 | -0.0010425 | -44.9249 | 72.1298 | -50.766 | 72.0016 | -49.2004 | -50.7889 | -50.116 | -48.848 | 72.1619 | -50.7614 | -50.235 | -50.4593 | -50.798 | -50.5005 | -0.07782 | -0.022888 | -0.15106 | 1.4877 | 0.5722 | -0.10071 | 0.65002 | -0.022888 | -0.073243 | 0.009155 | -122.3877 | 0.22888 | 0.18768 | -0.10986 | 0.26093 | -0.036621 | 1.5656 | 122.7676 | 0.30212 | 0.52643 | 122.8958 | 122.9233 | 122.818 | 122.85 | -122.9187 | -122.9141 | 122.6898 | 0.45319 | 5.7632 | 1.8402
4061.1719 | 123.0469 | -50.6699 | 72.0978 | -0.098725 | 0.0012625 | 0.061171 | 0.070113 | 0.00016017 | 0.0036871 | 0.0054218 | 0.032227 | 0.0025975 | 0.0012818 | -0.00058098 | -0.0027877 | -0.0072889 | 0.0030163 | -44.8654 | 72.1161 | -50.7614 | 71.9193 | -49.0356 | -50.5005 | -49.9237 | -48.6649 | 72.1436 | -50.6973 | -50.1251 | -50.3311 | -50.647 | -50.4044 | -0.091553 | 0.018311 | -0.17853 | 1.6342 | 0.74615 | 0.16937 | 0.83771 | 0.26093 | -0.027466 | 0.045777 | -122.2229 | 0.33874 | 0.2655 | 0.022888 | 0.29297 | 0.050354 | 1.7258 | 122.6807 | 0.36621 | 0.57221 | 122.8775 | 122.8409 | 122.7859 | 122.8134 | -122.8592 | -122.7951 | 122.5891 | 0.54474 | 5.8044 | 2.005
4062.1719 | 122.9919 | -50.7065 | 72.0795 | -0.10635 | 0.00019446 | 0.062025 | 0.067336 | 0.00037377 | 0.0017645 | 0.0045672 | 0.016968 | 0.0015295 | 0.0023498 | 0.002196 | -0.0032151 | -0.0053663 | -0.0025379 | -44.902 | 72.084 | -50.7614 | 71.8872 | -49.086 | -50.5554 | -49.9695 | -48.7198 | 72.1573 | -50.7339 | -50.1663 | -50.3815 | -50.7111 | -50.4364 | -0.054932 | 0.004577 | -0.19226 | 1.6205 | 0.737 | 0.15106 | 0.79193 | 0.20599 | -0.027466 | 0.07782 | -122.2458 | 0.32501 | 0.27008 | -0.004578 | 0.29755 | 0.022888 | 1.6754 | 122.6486 | 0.35248 | 0.56763 | 122.8455 | 122.8912 | 122.7905 | 122.8638 | -122.8409 | -122.8134 | 122.5937 | 0.54016 | 5.8044 | 1.9867
4063.1719 | 123.0286 | -50.6836 | 72.1069 | -0.083466 | 0.0021171 | 0.060316 | 0.069045 | 0.0035782 | 0.0013373 | 0.0052082 | 0.026123 | 3.4148e-05 | 0.00085443 | 0.002196 | -0.0042831 | -0.0053663 | 0.00088014 | -44.8288 | 72.1069 | -50.7477 | 71.9055 | -49.0997 | -50.5875 | -49.9832 | -48.7381 | 72.1527 | -50.7431 | -50.1663 | -50.3769 | -50.7294 | -50.4456 | -0.064087 | 0 | -0.20142 | 1.5839 | 0.70038 | 0.096131 | 0.76447 | 0.16022 | -0.059509 | 0.045776 | -122.2733 | 0.3067 | 0.23804 | -0.045776 | 0.29755 | 0.013733 | 1.648 | 122.6532 | 0.36621 | 0.57678 | 122.8546 | 122.8958 | 122.7905 | 122.8363 | -122.8546 | -122.85 | 122.5891 | 0.51727 | 5.8548 | 1.9455
4064.1719 | 123.0515 | -50.6653 | 72.1069 | -0.12924 | 0.0012625 | 0.061171 | 0.066909 | 0.001442 | 0.00026909 | 0.0043536 | 0.001709 | 0.00067495 | 0.00085443 | 0.001128 | -0.0027877 | -0.0077161 | 0.0025891 | -44.8425 | 72.0978 | -50.7431 | 71.9238 | -49.0265 | -50.5051 | -49.942 | -48.6832 | 72.139 | -50.7111 | -50.1343 | -50.3494 | -50.6653 | -50.4135 | -0.07782 | -0.009156 | -0.18311 | 1.6388 | 0.72327 | 0.16022 | 0.80109 | 0.23804 | -0.045777 | 0.032043 | -122.2412 | 0.31586 | 0.25177 | 0 | 0.29755 | 0.045777 | 1.7166 | 122.6669 | 0.36163 | 0.57678 | 122.8409 | 122.85 | 122.7631 | 122.8043 | -122.85 | -122.818 | 122.5891 | 0.53101 | 5.8228 | 1.9821
4065.1719 | 122.9782 | -50.6744 | 72.1756 | -0.0071715 | 0.0014761 | 0.062666 | 0.070754 | 0.0010148 | 0.0011237 | 0.0067036 | -0.074585 | 0.00024775 | 0.00021363 | 0.003905 | -0.0053513 | -0.0055799 | -0.0023243 | -44.8242 | 72.1207 | -50.7706 | 71.8918 | -49.0494 | -50.56 | -50.0107 | -48.7244 | 72.1848 | -50.7202 | -50.1984 | -50.4364 | -50.7065 | -50.4501 | -0.096131 | -0.054931 | -0.28381 | 1.6251 | 0.66376 | 0.11444 | 0.75989 | 0.21057 | -0.045777 | 0.009155 | -122.374 | 0.23804 | 0.2243 | -0.032044 | 0.27008 | 0.013733 | 1.7212 | 122.6624 | 0.28381 | 0.52185 | 122.8912 | 122.905 | 122.7951 | 122.8592 | -122.9462 | -122.8958 | 122.5662 | 0.47607 | 5.8502 | 1.9501
4066.1719 | 122.9874 | -50.6607 | 72.1161 | -0.083466 | 0.0014761 | 0.061171 | 0.068404 | -0.00026703 | 0.0032599 | 0.0039264 | -0.041016 | 0.0015295 | 0.001068 | -0.0059216 | -0.0017197 | -0.0062207 | 0.00045294 | -44.8425 | 72.0657 | -50.7614 | 71.9055 | -49.0265 | -50.5554 | -49.9603 | -48.7198 | 72.1527 | -50.6973 | -50.1526 | -50.3906 | -50.7065 | -50.4227 | -0.10071 | -0.050354 | -0.21057 | 1.6342 | 0.70038 | 0.10529 | 0.80109 | 0.20599 | -0.036621 | 0.036621 | -122.2687 | 0.27008 | 0.23804 | -0.045776 | 0.27466 | -0.009155 | 1.7349 | 122.6669 | 0.3067 | 0.54474 | 122.8271 | 122.85 | 122.7264 | 122.8134 | -122.8775 | -122.8134 | 122.5662 | 0.50812 | 5.8182 | 1.9409
4067.1719 | 123.0103 | -50.679 | 72.1115 | -0.10635 | 0.0014761 | 0.063307 | 0.068404 | 0.0040054 | 0.0028327 | 0.0049946 | -0.0043946 | 0.0019567 | 0.0021362 | 0.0024096 | -0.0042831 | -0.0064343 | 0.0010937 | -44.8517 | 72.1069 | -50.7294 | 71.9147 | -49.0173 | -50.5325 | -49.9695 | -48.7244 | 72.1573 | -50.7065 | -50.116 | -50.3769 | -50.7614 | -50.4456 | -0.050354 | -0.004577 | -0.19684 | 1.6617 | 0.70953 | 0.14648 | 0.75989 | 0.19684 | -0.027466 | 0.045777 | -122.2275 | 0.30212 | 0.23346 | -0.082398 | 0.26093 | -0.054932 | 1.712 | 122.644 | 0.32959 | 0.59052 | 122.8363 | 122.8638 | 122.7859 | 122.8363 | -122.8409 | -122.818 | 122.5937 | 0.56305 | 5.8273 | 1.9547
4068.1719 | 123.024 | -50.6561 | 72.1161 | -0.12924 | -0.00023294 | 0.062239 | 0.069045 | -0.005394 | 0.0028327 | 0.0045672 | 0.0078126 | -0.0010339 | 0.0012818 | -0.0014356 | -0.0021469 | -0.0057935 | 0.0025891 | -44.8563 | 72.1115 | -50.7614 | 71.9147 | -49.0265 | -50.5417 | -49.9695 | -48.6923 | 72.1573 | -50.6973 | -50.1343 | -50.354 | -50.6973 | -50.4135 | -0.10529 | -0.004578 | -0.20142 | 1.6296 | 0.68665 | 0.11444 | 0.79193 | 0.21973 | -0.041199 | 0.041199 | -122.2504 | 0.30212 | 0.24262 | -0.041199 | 0.28381 | 0 | 1.7349 | 122.6761 | 0.34332 | 0.56305 | 122.8729 | 122.8546 | 122.7676 | 122.8134 | -122.8775 | -122.8134 | 122.5708 | 0.52185 | 5.7999 | 1.9638
4069.1719 | 123.0286 | -50.647 | 72.1298 | -0.091095 | 0.00062166 | 0.062239 | 0.067763 | -0.0026168 | 0.0032599 | 0.0060626 | -0.0013428 | 0.0025975 | 0.0021362 | 0.003905 | -0.0015061 | -0.0066479 | -0.0010425 | -44.7922 | 72.1252 | -50.7294 | 71.9604 | -48.9578 | -50.4822 | -49.9008 | -48.6374 | 72.1619 | -50.679 | -50.0977 | -50.3082 | -50.6424 | -50.3723 | -0.082397 | -0.004578 | -0.16937 | 1.6891 | 0.74616 | 0.1648 | 0.82855 | 0.24719 | -0.032043 | 0.032043 | -122.2275 | 0.33875 | 0.27466 | 0.004578 | 0.3067 | 0.036621 | 1.7715 | 122.6898 | 0.37079 | 0.58136 | 122.8546 | 122.8409 | 122.7722 | 122.8088 | -122.8592 | -122.8088 | 122.6074 | 0.54932 | 5.8548 | 2.0096
4070.1719 | 122.9691 | -50.6332 | 72.171 | -0.060578 | -0.0019417 | 0.061812 | 0.071822 | 0.0037918 | 5.5488e-05 | 0.0047808 | -0.077637 | 0.0021703 | 0.0023498 | -0.0010084 | -0.0030013 | -0.0055799 | -0.00061526 | -44.7922 | 72.1664 | -50.7202 | 71.9193 | -48.999 | -50.5325 | -49.9832 | -48.6832 | 72.2076 | -50.7065 | -50.1297 | -50.3815 | -50.7111 | -50.3952 | -0.086975 | -0.004578 | -0.25177 | 1.6342 | 0.65002 | 0.10071 | 0.737 | 0.18768 | -0.073242 | 0.036621 | -122.3007 | 0.25177 | 0.23804 | -0.07782 | 0.31128 | -0.004578 | 1.7212 | 122.6395 | 0.32501 | 0.57678 | 122.8867 | 122.9141 | 122.7997 | 122.8409 | -122.8912 | -122.8775 | 122.5525 | 0.50354 | 5.8411 | 1.9501
4071.1719 | 123.0331 | -50.6378 | 72.1298 | -0.098725 | -0.0010873 | 0.06288 | 0.067977 | -0.0028304 | 0.0015509 | 0.0039264 | 0.0047608 | 0.0021703 | 0.00042723 | -0.0014356 | -0.0034287 | -0.0057935 | 0.00023934 | -44.7922 | 72.1481 | -50.6927 | 71.9467 | -48.9487 | -50.4959 | -49.9008 | -48.6786 | 72.1848 | -50.6836 | -50.1022 | -50.3403 | -50.6607 | -50.3632 | -0.054932 | 0.01831 | -0.18311 | 1.6891 | 0.737 | 0.14191 | 0.79193 | 0.19684 | -0.045777 | 0.054931 | -122.2321 | 0.29755 | 0.27466 | -0.022889 | 0.32043 | 0.022888 | 1.7441 | 122.6395 | 0.34332 | 0.58136 | 122.8409 | 122.8683 | 122.7859 | 122.8226 | -122.8226 | -122.8134 | 122.5845 | 0.53558 | 5.8456 | 1.9592
4072.1719 | 123.0698 | -50.6241 | 72.1664 | -0.052948 | -0.0015145 | 0.062239 | 0.069045 | -0.0024032 | 0.0011237 | 0.0052082 | 0.0078126 | 0.0011023 | 0.0029906 | -0.0025036 | -0.0012925 | -0.0053663 | 0.0040845 | -44.7739 | 72.1527 | -50.6882 | 71.9971 | -48.8846 | -50.4501 | -49.8688 | -48.6008 | 72.1802 | -50.6699 | -50.0473 | -50.2853 | -50.5966 | -50.3311 | -0.064087 | -0.013733 | -0.16937 | 1.7395 | 0.75531 | 0.17395 | 0.8194 | 0.23804 | -0.045777 | 0.013733 | -122.2137 | 0.33875 | 0.29297 | 0.027465 | 0.33874 | 0.073242 | 1.8036 | 122.6852 | 0.38452 | 0.62256 | 122.8409 | 122.85 | 122.7768 | 122.8043 | -122.8546 | -122.8363 | 122.6212 | 0.57678 | 5.8502 | 2.0233
4073.1719 | 123.0927 | -50.6378 | 72.1298 | -0.1445 | 0.0010489 | 0.062239 | 0.067123 | -0.0013352 | 0.0017645 | 0.0026446 | 0.0047608 | -0.00060665 | -0.00042717 | -0.0014356 | -0.00022431 | -0.0053663 | -0.00040166 | -44.8242 | 72.1527 | -50.6927 | 71.9513 | -48.9624 | -50.5142 | -49.9237 | -48.6832 | 72.1573 | -50.6561 | -50.1205 | -50.3586 | -50.6836 | -50.5508 | -0.054932 | 0.022888 | -0.17853 | 1.6754 | 0.71411 | 0.1236 | 0.76904 | 0.17853 | -0.018311 | 0.027466 | -122.2504 | 0.27923 | 0.086975 | -0.045777 | 0.10529 | -0.027466 | 1.7303 | 122.644 | 0.29755 | 0.53558 | 122.8455 | 122.8134 | 122.7905 | 122.7951 | -122.8226 | -122.786 | 122.5891 | 0.51727 | 5.8136 | 1.9547
4074.1719 | 123.0286 | -50.6241 | 72.1481 | -0.068207 | -1.9142e-05 | 0.060316 | 0.07225 | -0.00048063 | 0.0017645 | 0.0060626 | -0.034912 | 0.00067495 | 0.0029906 | -0.00079478 | -0.0025741 | -0.0064343 | 0.0017345 | -44.8105 | 72.1527 | -50.7156 | 71.9467 | -48.9624 | -50.5188 | -49.9283 | -48.674 | 72.1848 | -50.6653 | -50.1114 | -50.3632 | -50.6744 | -50.3906 | -0.091553 | 0.004578 | -0.20142 | 1.6617 | 0.6958 | 0.10529 | 0.78735 | 0.19684 | -0.041199 | 0.036621 | -122.2595 | 0.26093 | 0.23346 | -0.050354 | 0.27466 | -0.009155 | 1.7532 | 122.6624 | 0.30212 | 0.55389 | 122.8683 | 122.85 | 122.7768 | 122.8088 | -122.8638 | -122.8134 | 122.5708 | 0.5127 | 5.8136 | 1.9501
4075.1719 | 122.9965 | -50.6012 | 72.29 | -0.075836 | 0.0010489 | 0.060744 | 0.0699 | 0.00080117 | 0.0026191 | 0.0045672 | -0.028809 | 0.00046135 | 0.0014954 | -0.00036738 | -0.0021469 | -0.0047253 | 0.0017345 | -44.7647 | 72.2214 | -50.6744 | 71.933 | -48.967 | -50.5234 | -49.9603 | -48.7152 | 72.258 | -50.6699 | -50.1434 | -50.3906 | -50.7111 | -50.3357 | -0.073242 | -0.068664 | -0.35706 | 1.6342 | 0.64087 | 0.07782 | 0.71411 | 0.15106 | -0.068665 | -0.032043 | -122.4335 | 0.21057 | 0.2655 | -0.10986 | 0.33417 | -0.041199 | 1.7075 | 122.6074 | 0.27924 | 0.52643 | 122.8958 | 122.9279 | 122.8226 | 122.8592 | -122.9645 | -122.9599 | 122.5342 | 0.45776 | 5.8365 | 1.886
4076.1719 | 123.0057 | -50.6287 | 72.1756 | -0.15976 | -0.00044654 | 0.060316 | 0.070327 | 0.00080117 | 0.00048269 | 0.0043536 | -0.0013428 | 0.00067495 | 0.00021363 | -0.0016492 | -0.0030013 | -0.0060071 | -0.00040166 | -44.7784 | 72.1573 | -50.6699 | 71.9513 | -48.9349 | -50.4913 | -49.9237 | -48.6099 | 72.1848 | -50.647 | -50.0931 | -50.3494 | -50.6744 | -50.3815 | -0.041199 | -0.01831 | -0.2243 | 1.6937 | 0.70496 | 0.13733 | 0.74615 | 0.17853 | -0.018311 | 0.009155 | -122.2687 | 0.27924 | 0.24719 | -0.045776 | 0.2655 | -0.027465 | 1.7349 | 122.6212 | 0.29755 | 0.55389 | 122.8271 | 122.8317 | 122.7859 | 122.8134 | -122.8455 | -122.8226 | 122.58 | 0.53558 | 5.8502 | 2.0187
4077.1719 | 123.0286 | -50.6241 | 72.1573 | -0.12161 | 0.0010489 | 0.060744 | 0.069259 | -0.00026703 | 0.0015509 | 0.0032856 | -0.0013428 | 0.0015295 | 0.00064083 | 0.0015552 | -0.0025741 | -0.0064343 | -0.0036059 | -44.7784 | 72.1573 | -50.6836 | 71.9788 | -48.9304 | -50.5005 | -49.9191 | -48.6374 | 72.2031 | -50.6516 | -50.0473 | -50.3723 | -50.7111 | -50.386 | -0.05951 | 0 | -0.17853 | 1.6937 | 0.70496 | 0.1236 | 0.76447 | 0.18311 | -0.027466 | 0.045776 | -122.2046 | 0.25177 | 0.23804 | -0.086976 | 0.2655 | -0.05951 | 1.7532 | 122.6624 | 0.27924 | 0.60425 | 122.8409 | 122.8546 | 122.7814 | 122.8271 | -122.8409 | -122.8088 | 122.6028 | 0.57678 | 5.8456 | 1.9867
4078.1719 | 123.0148 | -50.5875 | 72.1802 | -0.17502 | 0.0019035 | 0.06053 | 0.069045 | -0.0015488 | 0.00026909 | 0.0026446 | -0.022705 | 0.00046135 | 0.00064083 | -0.00464 | -0.00086511 | -0.0051527 | -0.0018971 | -44.7693 | 72.1619 | -50.7019 | 71.965 | -48.8892 | -50.4868 | -49.8871 | -48.6465 | 72.2031 | -50.6607 | -50.0839 | -50.3082 | -50.6332 | -50.3677 | -0.11444 | -0.018311 | -0.21515 | 1.6983 | 0.70038 | 0.10071 | 0.81482 | 0.21515 | -0.073243 | 0.022888 | -122.2641 | 0.27923 | 0.21973 | -0.045777 | 0.29297 | 0.027466 | 1.8127 | 122.6669 | 0.35248 | 0.57678 | 122.8638 | 122.8638 | 122.7493 | 122.7905 | -122.8821 | -122.8409 | 122.5525 | 0.50354 | 5.8182 | 1.9409
4079.1719 | 123.024 | -50.6012 | 72.1756 | -0.12161 | 0.0010489 | 0.061812 | 0.069259 | 0.001442 | 0.0028327 | 0.0054218 | -0.053223 | 0.00088875 | 0.0019226 | 0.00027342 | -0.0015061 | -0.0045117 | -0.0031787 | -44.7235 | 72.1527 | -50.6607 | 72.0062 | -48.8342 | -50.4593 | -49.8825 | -48.5825 | 72.2076 | -50.6241 | -50.0473 | -50.322 | -50.6378 | -50.3357 | -0.05951 | -0.022888 | -0.16937 | 1.767 | 0.71869 | 0.14191 | 0.7782 | 0.20142 | -0.022888 | 0.032044 | -122.2229 | 0.27924 | 0.2655 | -0.036621 | 0.28839 | -0.013733 | 1.8265 | 122.6669 | 0.30212 | 0.57678 | 122.8134 | 122.8317 | 122.7539 | 122.8088 | -122.8363 | -122.7997 | 122.6074 | 0.55389 | 5.8777 | 2.0187
4080.1719 | 122.9782 | -50.592 | 72.1664 | -0.11398 | -1.9142e-05 | 0.063094 | 0.071181 | 0.0018692 | 0.0030463 | 0.0043536 | -0.019653 | 3.4148e-05 | 0.0021362 | 0.0015552 | -0.0038559 | -0.0051527 | -0.0018971 | -44.7327 | 72.1664 | -50.679 | 71.9788 | -48.8342 | -50.4684 | -49.91 | -48.6328 | 72.2351 | -50.6744 | -50.0793 | -50.3311 | -50.6516 | -50.3769 | -0.086975 | 0 | -0.18768 | 1.7578 | 0.68207 | 0.1236 | 0.76904 | 0.21057 | -0.082397 | 0.068664 | -122.2458 | 0.26093 | 0.21515 | -0.059509 | 0.29755 | 0.022888 | 1.8448 | 122.6578 | 0.34332 | 0.59509 | 122.8455 | 122.9095 | 122.7585 | 122.8271 | -122.8455 | -122.8409 | 122.5708 | 0.5127 | 5.8594 | 1.9592
4081.1719 | 123.0057 | -50.6012 | 72.1939 | -0.10635 | 0.0014761 | 0.061598 | 0.068832 | -5.343e-05 | 0.0024053 | 0.0037128 | -0.050171 | 0.00067495 | 0.00064083 | -0.0048536 | -0.0017197 | -0.0049389 | -0.0010425 | -44.7235 | 72.1756 | -50.6561 | 71.9971 | -48.8205 | -50.4684 | -49.8825 | -48.6008 | 72.226 | -50.6516 | -50.0748 | -50.3403 | -50.6424 | -50.3586 | -0.054932 | -0.018311 | -0.19684 | 1.7807 | 0.71869 | 0.13275 | 0.77362 | 0.18768 | -0.050354 | 0.032043 | -122.2687 | 0.26093 | 0.24261 | -0.041199 | 0.29297 | 0.009155 | 1.8356 | 122.6532 | 0.31128 | 0.57678 | 122.8317 | 122.8775 | 122.7768 | 122.8271 | -122.85 | -122.8455 | 122.5983 | 0.52643 | 5.8777 | 2.0004
4082.1719 | 122.9828 | -50.5783 | 72.1939 | -0.091095 | 0.00083526 | 0.063521 | 0.068618 | 0.0016556 | 0.0032599 | 0.0088398 | -0.01355 | 0.0021703 | 0.0029906 | -0.0061352 | -0.0019333 | -0.0077161 | 0.0019483 | -44.7327 | 72.1802 | -50.6378 | 71.9833 | -48.8434 | -50.4822 | -49.8917 | -48.6465 | 72.2122 | -50.6241 | -50.061 | -50.322 | -50.6332 | -50.3586 | -0.059509 | -0.013733 | -0.21057 | 1.7349 | 0.68664 | 0.09613 | 0.74615 | 0.15564 | -0.045776 | 0.01831 | -122.2549 | 0.25635 | 0.21973 | -0.054932 | 0.2655 | -0.009156 | 1.7944 | 122.6212 | 0.30212 | 0.56305 | 122.818 | 122.8363 | 122.7585 | 122.7905 | -122.8317 | -122.818 | 122.5616 | 0.51727 | 5.8456 | 1.9318
4083.1719 | 122.9965 | -50.592 | 72.2076 | -0.091095 | -0.00087374 | 0.059889 | 0.069259 | -0.00026703 | -0.0010125 | 0.0056354 | -0.0013428 | 0.00067495 | 0.00021363 | -0.002931 | -0.0023605 | -0.0040845 | -0.0027515 | -44.7189 | 72.1802 | -50.6653 | 71.9971 | -48.8251 | -50.4684 | -49.8825 | -48.6145 | 72.2397 | -50.6287 | -50.0473 | -50.2899 | -50.647 | -50.3586 | -0.073242 | -0.027466 | -0.21057 | 1.767 | 0.70953 | 0.1236 | 0.78278 | 0.19684 | -0.036621 | 0.032043 | -122.2549 | 0.30212 | 0.23346 | -0.054932 | 0.27008 | -0.018311 | 1.8402 | 122.6624 | 0.33874 | 0.58136 | 122.8455 | 122.8683 | 122.7722 | 122.8317 | -122.8729 | -122.8363 | 122.5891 | 0.54474 | 5.8731 | 1.9775
4084.1719 | 122.9691 | -50.5508 | 72.1802 | -0.11398 | -0.00044654 | 0.062453 | 0.067977 | -0.00069423 | 0.0032599 | 0.005849 | -0.041016 | 0.00088875 | 0.00021363 | 0.0049732 | -0.0012925 | -0.0075025 | 0.00023934 | -44.6777 | 72.1848 | -50.6332 | 72.0245 | -48.793 | -50.4593 | -49.8596 | -48.5916 | 72.2305 | -50.6058 | -50.0427 | -50.3082 | -50.6287 | -50.322 | -0.082398 | 0.004577 | -0.15564 | 1.7578 | 0.69122 | 0.091552 | 0.77362 | 0.17395 | -0.054932 | 0.050354 | -122.2229 | 0.24261 | 0.22888 | -0.07782 | 0.28381 | -0.022888 | 1.8402 | 122.6578 | 0.29755 | 0.56305 | 122.818 | 122.8363 | 122.7356 | 122.7814 | -122.8134 | -122.7859 | 122.5754 | 0.50812 | 5.8731 | 1.9592
4085.1719 | 123.0515 | -50.5417 | 72.1939 | -0.12161 | 0.00083526 | 0.062239 | 0.070541 | 0.00080117 | 0.00091009 | 0.007558 | -0.053223 | 0.0025975 | -0.0010682 | 0.0051868 | -0.0049241 | -0.0047253 | -0.0021107 | -44.7006 | 72.1939 | -50.6744 | 72.0016 | -48.8113 | -50.473 | -49.9008 | -48.5641 | 72.2351 | -50.6058 | -50.0107 | -50.2853 | -50.6012 | -50.2899 | -0.13275 | 0 | -0.19226 | 1.7303 | 0.64087 | 0.068665 | 0.77362 | 0.20142 | -0.064087 | 0.041198 | -122.2046 | 0.25635 | 0.25177 | -0.059509 | 0.31586 | 0.004578 | 1.8631 | 122.6761 | 0.32043 | 0.59509 | 122.8683 | 122.8409 | 122.7356 | 122.7768 | -122.8683 | -122.7997 | 122.5433 | 0.53101 | 5.8411 | 1.9775
4086.1719 | 122.9919 | -50.5508 | 72.2031 | -0.15976 | 0.0014761 | 0.062025 | 0.069472 | 0.001442 | 0.0024053 | 0.005849 | -0.034912 | -0.0010339 | 0.0021362 | -0.00229 | -0.0030013 | -0.0062207 | -0.0016833 | -44.6503 | 72.1893 | -50.6378 | 72.0337 | -48.7289 | -50.4318 | -49.855 | -48.5458 | 72.2214 | -50.6332 | -50.0061 | -50.267 | -50.5966 | -50.2991 | -0.086975 | -0.013733 | -0.16937 | 1.8219 | 0.6958 | 0.11902 | 0.78278 | 0.20599 | -0.082398 | 0.018311 | -122.2092 | 0.28381 | 0.25177 | -0.045777 | 0.33417 | 0.036621 | 1.9089 | 122.6715 | 0.36621 | 0.62714 | 122.8271 | 122.8546 | 122.7402 | 122.7722 | -122.8409 | -122.8363 | 122.5845 | 0.54474 | 5.9006 | 2.005
4087.1719 | 123.0377 | -50.5783 | 72.1985 | -0.15976 | 0.00040806 | 0.061812 | 0.068832 | -0.0021896 | 0.0026191 | 0.0045672 | -0.019653 | 0.0028113 | 0.00085443 | 0.0017688 | -0.0038559 | -0.0055799 | -0.0029651 | -44.6365 | 72.1893 | -50.6287 | 72.0383 | -48.7244 | -50.4089 | -49.8367 | -48.5458 | 72.2351 | -50.6287 | -49.9969 | -50.2625 | -50.5875 | -50.2945 | -0.050354 | -0.009155 | -0.16022 | 1.8539 | 0.74158 | 0.16937 | 0.79193 | 0.21973 | -0.050354 | 0.036621 | -122.1954 | 0.31586 | 0.28381 | -0.009155 | 0.33417 | 0.041199 | 1.9043 | 122.6669 | 0.36621 | 0.63171 | 122.818 | 122.8638 | 122.7676 | 122.8134 | -122.8271 | -122.8271 | 122.6166 | 0.58136 | 5.9418 | 2.0325
4088.1719 | 123.0103 | -50.5463 | 72.2076 | -0.091095 | 0.00083526 | 0.061598 | 0.069686 | -0.0017624 | 0.0030463 | 0.0039264 | -0.041016 | -0.00039305 | 0.00042723 | -0.0016492 | -0.0025741 | -0.0060071 | 0.0013073 | -44.6411 | 72.1802 | -50.6561 | 72.1298 | -48.7701 | -50.4089 | -49.8138 | -48.5321 | 72.2443 | -50.5646 | -49.9878 | -50.2487 | -50.5737 | -50.2853 | -0.10986 | -0.027466 | -0.07782 | 1.7761 | 0.73242 | 0.13733 | 0.84229 | 0.24719 | -0.01831 | 0.036621 | -122.1954 | 0.29755 | 0.26093 | -0.027465 | 0.27924 | -0.009155 | 1.886 | 122.786 | 0.31586 | 0.57678 | 122.8363 | 122.8088 | 122.7264 | 122.7905 | -122.8638 | -122.7722 | 122.6761 | 0.55847 | 5.9052 | 2.0142
4089.1719 | 123.0103 | -50.5692 | 72.2122 | -0.1445 | -0.0013009 | 0.062239 | 0.069045 | 0.001442 | 0.0021917 | 0.0037128 | -0.03186 | 0.00067495 | 0.0019226 | 0.0034778 | -0.0032151 | -0.0053663 | 0.0017345 | -44.6457 | 72.1985 | -50.5829 | 72.0749 | -48.7106 | -50.4135 | -49.8276 | -48.5321 | 72.2351 | -50.5966 | -49.9786 | -50.2853 | -50.5829 | -50.2945 | -0.013733 | -0.013733 | -0.13733 | 1.8585 | 0.74158 | 0.15564 | 0.75531 | 0.16937 | -0.027466 | 0.022888 | -122.1909 | 0.28381 | 0.27466 | -0.013733 | 0.30212 | 0.013733 | 1.8723 | 122.6578 | 0.31128 | 0.61798 | 122.7814 | 122.8317 | 122.7676 | 122.8043 | -122.7951 | -122.8088 | 122.644 | 0.59052 | 5.9235 | 2.037
4090.1719 | 122.9874 | -50.528 | 72.226 | -0.098725 | 0.00083526 | 0.063307 | 0.070327 | -0.0015488 | 0.0034735 | 0.0056354 | -0.041016 | 3.4148e-05 | 0.00021363 | -0.00058098 | -0.0036423 | -0.0055799 | -0.00018806 | -44.6274 | 72.2214 | -50.6058 | 72.0657 | -48.6786 | -50.4089 | -49.8367 | -48.5275 | 72.2672 | -50.592 | -49.9832 | -50.2579 | -50.5829 | -50.2991 | -0.07782 | -0.004577 | -0.16022 | 1.8494 | 0.69122 | 0.11902 | 0.76904 | 0.19684 | -0.064087 | 0.041199 | -122.2092 | 0.27008 | 0.22888 | -0.054932 | 0.29297 | 0.009155 | 1.9272 | 122.6715 | 0.33417 | 0.60883 | 122.8271 | 122.8592 | 122.7493 | 122.7951 | -122.8317 | -122.818 | 122.5937 | 0.54474 | 5.9006 | 2.0004
4091.1719 | 123.0469 | -50.528 | 72.2214 | -0.12924 | -0.0019417 | 0.062239 | 0.069259 | 0.003151 | 0.0024053 | 0.0049946 | -0.019653 | 0.0011023 | 0.00064083 | -0.0014356 | -0.0019333 | -0.0034437 | -0.0029651 | -44.8288 | 72.1893 | -50.6241 | 72.0978 | -48.6557 | -50.4044 | -49.8047 | -48.5275 | 72.2397 | -50.5829 | -49.9832 | -50.235 | -50.5829 | -50.2762 | -0.09613 | -0.032044 | -0.1236 | 1.8723 | 0.72327 | 0.1236 | 0.8194 | 0.21973 | -0.054932 | 0.01831 | -122.2046 | 0.29297 | 0.25177 | -0.054932 | 0.3067 | 0 | 1.9684 | 122.7219 | 0.3479 | 0.59967 | 122.8134 | 122.8226 | 122.7173 | 122.7676 | -122.8455 | -122.8043 | 122.6257 | 0.54474 | 5.6992 | 2.0004
4092.1719 | 123.024 | -50.5325 | 72.2443 | -0.098725 | 0.0021171 | 0.063094 | 0.070113 | 0.0040054 | 0.0013373 | 0.00414 | -0.06543 | 0.0013159 | -0.00042717 | 0.0028368 | -0.0034287 | -0.0051527 | 0.00088014 | -44.6503 | 72.2214 | -50.6378 | 72.02 | -48.7381 | -50.4501 | -49.8688 | -48.5413 | 72.2626 | -50.5875 | -49.9832 | -50.2533 | -50.5783 | -50.2579 | -0.10528 | -0.022888 | -0.22431 | 1.7944 | 0.66376 | 0.082398 | 0.76904 | 0.18768 | -0.054931 | 0.01831 | -122.2275 | 0.27924 | 0.27466 | -0.045776 | 0.32959 | 0.009155 | 1.8997 | 122.6578 | 0.33417 | 0.60425 | 122.8592 | 122.85 | 122.7539 | 122.7951 | -122.8821 | -122.8317 | 122.5525 | 0.54932 | 5.8823 | 1.9913
4093.1719 | 123.0194 | -50.5508 | 72.1985 | -0.083466 | 0.0019035 | 0.060744 | 0.070754 | -5.343e-05 | 0.0017645 | 0.0052082 | -0.06543 | 0.0017431 | 0.0014954 | -0.0018628 | -0.0021469 | -0.0064343 | 0.0013073 | -44.6686 | 72.2397 | -50.6241 | 72.0108 | -48.7473 | -50.4593 | -49.9008 | -48.5825 | 72.29 | -50.5737 | -50.0015 | -50.2487 | -50.592 | -50.2716 | -0.073242 | 0.041199 | -0.18768 | 1.8036 | 0.65002 | 0.091552 | 0.72327 | 0.16479 | -0.022888 | 0.091553 | -122.2 | 0.30212 | 0.27924 | -0.041199 | 0.30212 | -0.018311 | 1.8768 | 122.6349 | 0.32501 | 0.5722 | 122.8638 | 122.8638 | 122.7905 | 122.8409 | -122.8226 | -122.7722 | 122.5616 | 0.54932 | 5.8823 | 1.9684
4094.1719 | 123.056 | -50.5234 | 72.2351 | -0.11398 | -0.00023294 | 0.06288 | 0.070327 | -0.00090783 | 0.0039007 | 0.0071308 | -0.034912 | -0.0014613 | 0.001068 | -0.00229 | -0.0025741 | -0.0057935 | 0.0015209 | -44.6045 | 72.2351 | -50.5829 | 72.0795 | -48.642 | -50.3723 | -49.8047 | -48.5138 | 72.2763 | -50.5829 | -49.9603 | -50.2258 | -50.5508 | -50.2625 | -0.05951 | 0 | -0.15564 | 1.8814 | 0.71869 | 0.15106 | 0.7782 | 0.21057 | -0.05951 | 0.041199 | -122.1954 | 0.29755 | 0.26093 | -0.027466 | 0.32044 | 0.032044 | 1.9409 | 122.6624 | 0.35706 | 0.62256 | 122.818 | 122.8592 | 122.7585 | 122.7997 | -122.818 | -122.818 | 122.6028 | 0.56305 | 5.9189 | 2.0096
4095.1719 | 123.0377 | -50.5325 | 72.2305 | -0.068207 | 0.0012625 | 0.063734 | 0.070327 | 0.00080117 | 0.0017645 | 0.005849 | -0.041016 | -0.00060665 | -0.001709 | -0.0044262 | -0.0027877 | -0.0060071 | 0.00045294 | -44.6182 | 72.2626 | -50.6195 | 72.052 | -48.6694 | -50.3998 | -49.8459 | -48.5184 | 72.2855 | -50.592 | -49.9603 | -50.2213 | -50.56 | -50.2441 | -0.086975 | 0.032043 | -0.17853 | 1.8631 | 0.68665 | 0.13275 | 0.77362 | 0.21973 | -0.059509 | 0.054931 | -122.1909 | 0.31128 | 0.28839 | -0.027466 | 0.3479 | 0.032043 | 1.9501 | 122.6715 | 0.37079 | 0.63171 | 122.8821 | 122.8775 | 122.7951 | 122.818 | -122.85 | -122.8226 | 122.5845 | 0.57221 | 5.9143 | 2.0142
4096.1719 | 123.0377 | -50.5005 | 72.2122 | -0.1445 | 0.0016899 | 0.061171 | 0.069686 | 0.0022964 | 0.0030463 | 0.0054218 | -0.019653 | 0.00088875 | 0.001068 | 0.001128 | -0.0017197 | -0.0049389 | 0.0017345 | -44.5587 | 72.2305 | -50.5875 | 72.0795 | -48.6099 | -50.3723 | -49.8047 | -48.674 | 72.2443 | -50.592 | -49.9283 | -50.1938 | -50.5371 | -50.2487 | -0.086975 | 0.018311 | -0.13275 | 1.8906 | 0.6958 | 0.12817 | 0.78278 | 0.21515 | -0.091553 | 0.032044 | -122.1405 | 0.3067 | 0.25177 | -0.036621 | 0.34332 | 0.054932 | 1.9775 | 122.6669 | 0.39825 | 0.66376 | 122.818 | 122.8363 | 122.731 | 122.7448 | -122.7997 | -122.8043 | 122.58 | 0.5722 | 5.9418 | 1.8265
4097.1719 | 123.0972 | -50.528 | 72.258 | -0.10635 | -0.00066014 | 0.062239 | 0.069686 | 0.0012284 | 0.00048269 | 0.0034992 | -0.034912 | 0.00067495 | 0.0012818 | 0.0034778 | -0.0025741 | -0.0077161 | 2.554e-05 | -44.5541 | 72.2717 | -50.6012 | 72.0795 | -48.5962 | -50.3723 | -49.8001 | -48.4909 | 72.29 | -50.5463 | -49.942 | -50.1801 | -50.7843 | -50.3769 | -0.073242 | 0.013733 | -0.17853 | 1.9318 | 0.72784 | 0.15564 | 0.80109 | 0.22888 | -0.018311 | 0.032043 | -122.2 | 0.3479 | 0.15106 | -0.25635 | 0.16937 | -0.23804 | 2.005 | 122.6807 | 0.36621 | 0.60425 | 122.8729 | 122.8363 | 122.7997 | 122.818 | -122.8592 | -122.8043 | 122.6074 | 0.58594 | 5.9738 | 2.037
4098.1719 | 122.9599 | -50.5188 | 72.2672 | -0.052948 | -0.00087374 | 0.060957 | 0.070327 | 0.0022964 | 0.0024053 | 0.0054218 | -0.059326 | 0.0017431 | 0.001068 | -0.0020764 | -0.0012925 | -0.0068615 | 0.0015209 | -44.6274 | 72.2809 | -50.6149 | 72.02 | -48.6877 | -50.4547 | -49.9008 | -48.6008 | 72.3129 | -50.5737 | -49.9969 | -50.2762 | -50.6058 | -50.3082 | -0.09613 | 0.013733 | -0.24719 | 1.8311 | 0.61798 | 0.064087 | 0.71411 | 0.16022 | -0.054931 | 0.045776 | -122.2641 | 0.24262 | 0.21057 | -0.086975 | 0.2655 | -0.032044 | 1.9272 | 122.6349 | 0.29755 | 0.57678 | 122.8958 | 122.8867 | 122.7997 | 122.8317 | -122.8821 | -122.8409 | 122.5388 | 0.52185 | 5.8914 | 1.918
4099.1719 | 122.9691 | -50.5234 | 72.2672 | -0.098725 | -0.0019417 | 0.063094 | 0.071181 | -0.0013352 | 0.0030463 | 0.0049946 | -0.050171 | 0.0028113 | 0.001709 | -0.0027174 | -0.0019333 | -0.0055799 | -0.00061526 | -44.632 | 72.2992 | -50.6104 | 72.0016 | -48.6877 | -50.4593 | -49.8871 | -48.5962 | 72.3541 | -50.5829 | -50.0198 | -50.2945 | -50.6241 | -50.3128 | -0.086976 | 0.032043 | -0.2655 | 1.8356 | 0.63629 | 0.064086 | 0.72327 | 0.15106 | -0.05951 | 0.086975 | -122.287 | 0.22888 | 0.21057 | -0.10071 | 0.27008 | -0.041198 | 1.9226 | 122.612 | 0.28839 | 0.56305 | 122.9095 | 122.937 | 122.8226 | 122.8775 | -122.8775 | -122.85 | 122.525 | 0.50354 | 5.8914 | 1.9272
4100.1719 | 122.9279 | -50.5234 | 72.2855 | -0.12161 | -0.0010873 | 0.060744 | 0.0699 | 0.00016017 | -0.00015811 | 0.0060626 | -0.037964 | 0.0025975 | 0.001709 | 0.003905 | -0.0015061 | -0.0040845 | -0.0025379 | -44.5633 | 72.3404 | -50.592 | 71.9971 | -48.6832 | -50.4776 | -49.9054 | -48.6145 | 72.3587 | -50.592 | -50.0336 | -50.3036 | -50.6332 | -50.3128 | -0.068665 | 0.054932 | -0.28839 | 1.8402 | 0.61798 | 0.045776 | 0.68664 | 0.11444 | -0.068665 | 0.073243 | -122.319 | 0.21973 | 0.21057 | -0.10986 | 0.27924 | -0.041199 | 1.9089 | 122.5891 | 0.28839 | 0.55847 | 122.9324 | 122.9507 | 122.8638 | 122.8821 | -122.8775 | -122.8775 | 122.5204 | 0.48981 | 5.9601 | 1.9089
4101.1719 | 123.0011 | -50.5142 | 72.29 | -0.11398 | -0.0010873 | 0.062239 | 0.068618 | 0.00016017 | 0.0015509 | 0.0026446 | -0.044067 | 0.0019567 | 0.00042723 | -0.001222 | -0.0012925 | -0.0051527 | -0.0038197 | -44.6045 | 72.3358 | -50.5783 | 71.9971 | -48.6557 | -50.4547 | -49.8596 | -48.5687 | 72.3679 | -50.5692 | -49.9878 | -50.2579 | -50.592 | -50.2762 | -0.064087 | 0.045776 | -0.29297 | 1.8585 | 0.6546 | 0.059509 | 0.71869 | 0.1236 | -0.054932 | 0.07782 | -122.2778 | 0.25635 | 0.23804 | -0.07782 | 0.29297 | -0.022888 | 1.9226 | 122.5754 | 0.31128 | 0.58136 | 122.9141 | 122.937 | 122.85 | 122.8821 | -122.8683 | -122.8592 | 122.5113 | 0.52643 | 5.9097 | 1.9455
4102.1719 | 123.0286 | -50.5005 | 72.2809 | -0.045319 | -0.0010873 | 0.063734 | 0.072463 | -0.00090783 | 0.0026191 | 0.0047808 | -0.01355 | 0.0017431 | -0.00021357 | -0.0035718 | -0.0023605 | -0.0051527 | 0.00066654 | -44.5862 | 72.2809 | -50.56 | 72.0566 | -48.5779 | -50.3906 | -49.8184 | -48.5092 | 72.3129 | -50.5325 | -49.942 | -50.2075 | -50.528 | -50.2258 | -0.05951 | 0 | -0.2243 | 1.9226 | 0.68207 | 0.10986 | 0.74158 | 0.16937 | -0.032044 | 0.032043 | -122.2229 | 0.29297 | 0.27466 | -0.027466 | 0.3067 | 0.004578 | 1.9821 | 122.6166 | 0.32501 | 0.59052 | 122.8409 | 122.8455 | 122.7814 | 122.8134 | -122.8409 | -122.8134 | 122.5571 | 0.55847 | 5.9143 | 1.9913
4103.1719 | 123.0331 | -50.5051 | 72.2946 | -0.12924 | -0.0010873 | 0.062239 | 0.071181 | -0.0013352 | 0.0013373 | 0.0056354 | -0.0074462 | 0.0017431 | 0.0023498 | -0.0042126 | -0.0032151 | -0.0064343 | 2.554e-05 | -44.5816 | 72.3221 | -50.5692 | 72.0428 | -48.6008 | -50.4135 | -49.8322 | -48.5321 | 72.3084 | -50.5463 | -49.9558 | -50.2121 | -50.5325 | -50.2304 | -0.064087 | 0.027466 | -0.25177 | 1.9043 | 0.67291 | 0.091553 | 0.737 | 0.15564 | -0.041199 | 0.013733 | -122.2504 | 0.29297 | 0.27466 | -0.027466 | 0.31586 | 0.013733 | 1.9684 | 122.612 | 0.33417 | 0.59051 | 122.8912 | 122.8546 | 122.8271 | 122.8134 | -122.8638 | -122.8409 | 122.5479 | 0.54932 | 5.9235 | 1.973
4104.1719 | 122.9874 | -50.4959 | 72.2992 | -0.1445 | -0.0017281 | 0.061598 | 0.069686 | 0.0016556 | 0.0011237 | 0.0032856 | -0.019653 | 0.00067495 | 0.00064083 | 0.001128 | -0.0059921 | -0.0083569 | 0.0089977 | -44.5862 | 72.3129 | -50.5692 | 72.0245 | -48.5916 | -50.4318 | -49.855 | -48.555 | 72.345 | -50.528 | -49.9649 | -50.2258 | -50.5829 | -50.2625 | -0.073242 | 0.013733 | -0.27466 | 1.9043 | 0.64087 | 0.064087 | 0.71411 | 0.13733 | -0.032043 | 0.045777 | -122.2641 | 0.27008 | 0.23346 | -0.086975 | 0.2655 | -0.054932 | 1.9775 | 122.5937 | 0.30212 | 0.56305 | 122.8821 | 122.8729 | 122.8088 | 122.8409 | -122.8683 | -122.8271 | 122.5204 | 0.53101 | 5.9097 | 1.9409
4105.1719 | 122.9553 | -50.4959 | 72.3129 | -0.12924 | 0.0025443 | 0.063094 | 0.070327 | -0.0024032 | 0.00048269 | 0.0043536 | -0.044067 | 0.00067495 | 0.0029906 | 0.0058276 | -0.0021469 | -0.0051527 | 0.0049389 | -44.5724 | 72.3267 | -50.56 | 72.0245 | -48.5916 | -50.4272 | -49.8642 | -48.555 | 72.3495 | -50.56 | -49.9924 | -50.2762 | -50.5783 | -50.2808 | -0.064087 | 0.013733 | -0.28839 | 1.9043 | 0.63171 | 0.068665 | 0.6958 | 0.13275 | -0.064087 | 0.036621 | -122.3053 | 0.21973 | 0.21515 | -0.082397 | 0.27924 | -0.01831 | 1.9684 | 122.5845 | 0.28381 | 0.56763 | 122.8867 | 122.9095 | 122.8226 | 122.8455 | -122.8729 | -122.8729 | 122.5204 | 0.50354 | 5.9235 | 1.9409
4106.1719 | 122.8775 | -50.4547 | 72.3679 | -0.060578 | 0.0025443 | 0.062025 | 0.070541 | -0.0017624 | 0.0024053 | 0.0047808 | -0.062378 | 0.0013159 | 0.00085443 | 0.008391 | -0.0017197 | -0.0062207 | -0.0072375 | -44.5816 | 72.3312 | -50.5508 | 72.0062 | -48.6328 | -50.4593 | -49.8917 | -48.5962 | 72.3862 | -50.5371 | -50.1709 | -50.0427 | -50.3815 | -50.2121 | -0.09613 | -0.036621 | -0.36163 | 1.8219 | 0.56305 | -0.004578 | 0.65918 | 0.091552 | -0.082397 | 0.01831 | -122.5388 | 0.41199 | 0.24262 | 0.073242 | 0.32501 | 0.15564 | 1.918 | 122.5571 | 0.49438 | 0.36621 | 122.8821 | 122.9233 | 122.7859 | 122.8409 | -122.9187 | -122.905 | 122.4609 | 0.28381 | 5.8731 | 1.8585
4107.1719 | 122.8043 | -50.528 | 72.2763 | -0.075836 | -0.00023294 | 0.062025 | 0.068832 | -0.0028304 | 0.0026191 | 0.0043536 | -0.03186 | 0.0013159 | -0.00042717 | -0.0052808 | -0.0027877 | -0.0055799 | 0.00066654 | -44.5633 | 72.345 | -50.5737 | 72.0062 | -48.6008 | -50.4593 | -49.8688 | -48.6191 | 72.3816 | -50.5142 | -50.0153 | -50.2853 | -50.647 | -50.267 | -0.045776 | 0.068665 | -0.27008 | 1.9272 | 0.65918 | 0.068664 | 0.70496 | 0.11444 | 0.013733 | 0.10529 | -122.2916 | 0.24262 | 0.26093 | -0.11902 | 0.24719 | -0.13275 | 1.973 | 122.58 | 0.22888 | 0.49896 | 122.9187 | 122.8958 | 122.8729 | 122.9095 | -122.85 | -122.7905 | 122.5342 | 0.5127 | 5.9647 | 1.9089
4108.1719 | 122.9141 | -50.4868 | 72.345 | -0.28946 | 0.0051077 | 0.060744 | 0.0699 | 0.00016017 | 0.00069649 | 0.0049946 | -0.028809 | 0.0013159 | 0.00085443 | -0.003999 | -0.0019333 | -0.0070753 | -0.00018806 | -44.339 | 72.3816 | -50.5554 | 72.0108 | -48.5596 | -50.441 | -49.8734 | -48.5825 | 72.3907 | -50.5325 | -49.9969 | -50.2625 | -50.6104 | -50.2853 | -0.068665 | 0.036621 | -0.33417 | 1.9272 | 0.6134 | 0.045776 | 0.68207 | 0.11444 | -0.045777 | 0.045776 | -122.3419 | 0.2243 | 0.20142 | -0.1236 | 0.24719 | -0.07782 | 1.9958 | 122.5662 | 0.27008 | 0.53558 | 122.937 | 122.9233 | 122.8683 | 122.8775 | -122.9004 | -122.8775 | 122.4976 | 0.48981 | 6.1478 | 1.9043
4109.1719 | 122.937 | -50.4822 | 72.3495 | -0.083466 | -1.9142e-05 | 0.062025 | 0.068618 | 0.0016556 | 0.0036871 | 0.0034992 | -0.01355 | 0.0019567 | 0.00042723 | -0.0014356 | -0.0025741 | -0.0049389 | 0.0045117 | -44.545 | 72.3679 | -50.5646 | 71.9879 | -48.587 | -50.3723 | -49.8413 | -48.5641 | 72.3999 | -50.5142 | -50.0015 | -50.2625 | -50.5966 | -50.2762 | -0.082397 | 0.018311 | -0.36163 | 1.8951 | 0.64087 | 0.10986 | 0.72327 | 0.19226 | -0.032043 | 0.050354 | -122.3511 | 0.21973 | 0.20599 | -0.11444 | 0.23804 | -0.082398 | 1.9775 | 122.5525 | 0.25177 | 0.5127 | 122.9324 | 122.9141 | 122.85 | 122.8821 | -122.9141 | -122.8638 | 122.4701 | 0.48065 | 5.9372 | 1.918
4110.1719 | 122.9782 | -50.4776 | 72.345 | -0.083466 | 0.00040806 | 0.061171 | 0.069472 | -0.0011214 | 0.0019781 | 0.0039264 | -0.0043946 | 0.0019567 | 0.0012818 | -0.0020764 | -0.0030013 | -0.0055799 | -0.00082886 | -44.5358 | 72.3541 | -50.56 | 72.0566 | -48.5229 | -50.4089 | -49.8138 | -48.5458 | 72.3816 | -50.4959 | -49.9466 | -50.2258 | -50.5646 | -50.235 | -0.082398 | 0.009155 | -0.28839 | 1.9547 | 0.66376 | 0.068664 | 0.74616 | 0.15106 | -0.018311 | 0.036621 | -122.2916 | 0.25177 | 0.24262 | -0.086975 | 0.26093 | -0.068664 | 2.037 | 122.6166 | 0.27008 | 0.54932 | 122.9141 | 122.8775 | 122.8317 | 122.8592 | -122.905 | -122.8409 | 122.5342 | 0.53101 | 5.9418 | 1.9318
4111.1719 | 122.9828 | -50.4639 | 72.3084 | -0.11398 | -0.00087374 | 0.062239 | 0.070327 | -5.343e-05 | -0.00037171 | 0.0062762 | -0.016602 | 0.0023839 | 0.0032044 | -0.0052808 | -0.00043791 | -0.0051527 | 0.0021619 | -44.5312 | 72.3633 | -50.5417 | 72.0703 | -48.5046 | -50.4089 | -49.8322 | -48.5275 | 72.3862 | -50.4959 | -49.9603 | -50.2075 | -50.5417 | -50.2533 | -0.07782 | 0.054931 | -0.23804 | 1.9592 | 0.63171 | 0.054931 | 0.70953 | 0.13275 | -0.032044 | 0.077819 | -122.2687 | 0.25635 | 0.21057 | -0.07782 | 0.24262 | -0.045776 | 2.037 | 122.612 | 0.28839 | 0.53558 | 122.905 | 122.8821 | 122.8271 | 122.85 | -122.85 | -122.8043 | 122.5342 | 0.50354 | 5.9326 | 1.9363
4112.1719 | 122.9599 | -50.4593 | 72.3633 | -0.13687 | -0.00087374 | 0.062666 | 0.071395 | 0.0029374 | 0.0015509 | 0.0067036 | -0.010498 | 0.0015295 | 0.0012818 | 0.00027342 | -0.0023605 | -0.0038709 | 0.00088014 | -44.5267 | 72.3679 | -50.5325 | 72.0474 | -48.5138 | -50.3998 | -49.8276 | -48.5275 | 72.3862 | -50.5051 | -49.9512 | -50.2213 | -50.5508 | -50.2396 | -0.073242 | 0.004578 | -0.31586 | 1.9455 | 0.63171 | 0.05951 | 0.70496 | 0.13275 | -0.045776 | 0.022888 | -122.3145 | 0.23804 | 0.21973 | -0.091552 | 0.2655 | -0.045776 | 2.0187 | 122.58 | 0.28381 | 0.55389 | 122.9004 | 122.8912 | 122.8271 | 122.8455 | -122.8958 | -122.8683 | 122.5067 | 0.50812 | 5.9326 | 1.9318
4113.1719 | 122.9187 | -50.4822 | 72.3724 | -0.091095 | -0.0013009 | 0.063307 | 0.071181 | -0.0015488 | 0.0032599 | 0.0077716 | -0.077637 | -0.0014613 | 0.00085443 | -0.0025036 | -0.0023605 | -0.0047253 | -0.0012561 | -44.5267 | 72.377 | -50.5371 | 72.0291 | -48.5046 | -50.4135 | -50.0427 | -48.2895 | 72.4136 | -50.5005 | -50.0153 | -50.2396 | -50.6104 | -50.2625 | -0.054931 | 0.004577 | -0.34332 | 1.9775 | 0.43945 | 0.068665 | 0.49438 | 0.1236 | -0.01831 | 0.041198 | -122.3877 | 0.24262 | 0.21973 | -0.12817 | 0.23804 | -0.10986 | 2.0325 | 122.5662 | 0.26093 | 0.48523 | 122.9141 | 122.9141 | 122.8592 | 122.8958 | -122.9095 | -122.8729 | 122.5113 | 0.46692 | 5.9555 | 2.1927
4114.1719 | 122.9416 | -50.4639 | 72.3587 | -0.052948 | 0.00062166 | 0.062453 | 0.070968 | 0.0044328 | 0.0030463 | 0.0026446 | -0.037964 | 0.0017431 | 0.003418 | 0.0024096 | -0.0027877 | -0.0068615 | 0.00023934 | -44.5084 | 72.377 | -50.5371 | 72.0245 | -48.4955 | -50.4227 | -49.8505 | -48.6832 | 72.3495 | -50.5142 | -49.9466 | -50.2625 | -50.5692 | -50.2487 | -0.073242 | 0.01831 | -0.33417 | 1.9684 | 0.6134 | 0.041199 | 0.68664 | 0.11444 | -0.050354 | -0.009156 | -122.3053 | 0.20142 | 0.21515 | -0.10529 | 0.2655 | -0.054932 | 2.0416 | 122.5616 | 0.25177 | 0.56763 | 122.9141 | 122.8638 | 122.8409 | 122.8134 | -122.8958 | -122.8729 | 122.4884 | 0.51727 | 5.9555 | 1.7807
4115.1719 | 122.9645 | -50.4547 | 72.3633 | -0.11398 | -0.00066014 | 0.061598 | 0.0699 | -0.00026703 | 0.0011237 | 0.0045672 | -0.010498 | 0.0023839 | 0.00042723 | -0.00058098 | -0.0015061 | -0.0051527 | -0.00040166 | -44.5267 | 72.3816 | -50.5234 | 72.0703 | -48.468 | -50.3815 | -49.8322 | -48.5138 | 72.4182 | -50.4868 | -49.9603 | -50.2258 | -50.5646 | -50.2441 | -0.068664 | 0.018311 | -0.29297 | 1.9867 | 0.62256 | 0.073242 | 0.69122 | 0.14191 | -0.032043 | 0.054932 | -122.3236 | 0.22888 | 0.21057 | -0.10986 | 0.24261 | -0.07782 | 2.0554 | 122.5937 | 0.26093 | 0.52643 | 122.905 | 122.905 | 122.8363 | 122.8729 | -122.8867 | -122.85 | 122.525 | 0.49439 | 5.928 | 1.9409
4116.1719 | 123.0469 | -50.4044 | 72.3541 | -0.098725 | 0.00040806 | 0.063307 | 0.069259 | -0.0011214 | 0.0021917 | 0.0071308 | 0.013916 | 0.0017431 | 0.0029906 | 0.003905 | -0.0032151 | -0.0030163 | 0.0032299 | -44.4992 | 72.3724 | -50.5142 | 72.1207 | -48.3765 | -50.3265 | -49.7543 | -48.4314 | 72.4091 | -50.473 | -49.8871 | -50.1389 | -50.4684 | -50.1709 | -0.10986 | 0.018311 | -0.23346 | 2.0279 | 0.65002 | 0.07782 | 0.75989 | 0.18768 | -0.068664 | 0.054932 | -122.2412 | 0.2655 | 0.23346 | -0.064087 | 0.30212 | 0.004577 | 2.1378 | 122.6349 | 0.33417 | 0.58594 | 122.8867 | 122.8821 | 122.7768 | 122.8134 | -122.8683 | -122.8271 | 122.525 | 0.51727 | 5.9052 | 1.973
4117.1719 | 123.0286 | -50.4318 | 72.3495 | -0.098725 | -0.0019417 | 0.063948 | 0.069472 | 0.0010148 | 0.0043281 | 0.0067036 | -0.0074462 | 3.4148e-05 | 0.001709 | 0.001128 | -0.0038559 | -0.0042981 | -0.00040166 | -44.4855 | 72.3541 | -50.5188 | 72.1252 | -48.3627 | -50.3357 | -49.7635 | -48.4589 | 72.3724 | -50.4639 | -49.8825 | -50.1617 | -50.4822 | -50.148 | -0.086975 | 0.004578 | -0.2243 | 2.0691 | 0.66833 | 0.096131 | 0.75531 | 0.18311 | -0.032043 | 0.022889 | -122.2321 | 0.27008 | 0.28381 | -0.050354 | 0.31586 | -0.018311 | 2.1561 | 122.644 | 0.30212 | 0.58136 | 122.8729 | 122.8363 | 122.7859 | 122.8043 | -122.8683 | -122.8134 | 122.5571 | 0.54932 | 5.9463 | 1.973
4118.1719 | 123.0286 | -50.3998 | 72.3541 | -0.10635 | 0.00040806 | 0.062666 | 0.069045 | 0.0022964 | 0.0045417 | 0.0037128 | -0.016602 | -0.00082025 | 0.00021363 | 0.0043322 | -0.0030013 | -0.0053663 | -0.0016833 | -44.4855 | 72.3953 | -50.4959 | 72.1161 | -48.3627 | -50.3632 | -49.7543 | -48.4543 | 72.3816 | -50.4684 | -49.9008 | -50.1343 | -50.4547 | -50.1572 | -0.096131 | 0.041199 | -0.23804 | 2.037 | 0.64545 | 0.036621 | 0.74158 | 0.13275 | -0.068665 | 0.027466 | -122.2549 | 0.2655 | 0.24261 | -0.054932 | 0.31128 | 0.013733 | 2.1332 | 122.612 | 0.33417 | 0.56763 | 122.8912 | 122.85 | 122.7951 | 122.7814 | -122.85 | -122.8226 | 122.5159 | 0.49896 | 5.9143 | 1.9455
4119.1719 | 123.0194 | -50.4181 | 72.3999 | -0.15213 | 0.0016899 | 0.064803 | 0.068618 | -0.0015488 | 0.0024053 | 0.0045672 | -0.022705 | 0.0015295 | 0.001068 | -0.00464 | -0.0023605 | -0.0053663 | -0.0029651 | -44.4809 | 72.3862 | -50.5188 | 72.0978 | -48.3627 | -50.3677 | -49.7818 | -48.436 | 72.4182 | -50.4684 | -49.8917 | -50.1434 | -50.4959 | -50.1801 | -0.10071 | -0.013733 | -0.30212 | 2.0554 | 0.63629 | 0.050354 | 0.737 | 0.15106 | -0.050354 | 0.018311 | -122.2916 | 0.27466 | 0.23804 | -0.07782 | 0.28839 | -0.027466 | 2.1561 | 122.6166 | 0.32501 | 0.57678 | 122.905 | 122.8867 | 122.8043 | 122.8363 | -122.9187 | -122.8683 | 122.5159 | 0.52643 | 5.9372 | 1.9821
4120.1719 | 122.9324 | -50.441 | 72.3907 | -0.11398 | -0.0025827 | 0.062239 | 0.071609 | 0.0010148 | 0.0017645 | 0.0060626 | -0.037964 | 0.0021703 | 0.001068 | 0.0036914 | -0.0036423 | -0.0051527 | -0.00018806 | -44.3069 | 72.4182 | -50.5005 | 72.0886 | -48.3765 | -50.3998 | -49.8138 | -48.5001 | 72.4548 | -50.4822 | -49.9649 | -50.2029 | -50.5554 | -50.2167 | -0.059509 | 0.027466 | -0.30212 | 2.0645 | 0.62714 | 0.041199 | 0.68664 | 0.10071 | -0.041199 | 0.064087 | -122.3557 | 0.23804 | 0.2243 | -0.11444 | 0.2655 | -0.073242 | 2.124 | 122.5891 | 0.27924 | 0.51727 | 122.9187 | 122.937 | 122.8592 | 122.8958 | -122.8912 | -122.8729 | 122.5296 | 0.47607 | 6.134 | 1.9409
4121.1719 | 123.0652 | -50.3677 | 72.3999 | -0.11398 | 0.0023307 | 0.060744 | 0.066054 | -0.0013352 | 0.0017645 | 0.0056354 | 0.084106 | 0.0011023 | 0.0012818 | -0.003999 | -0.0019333 | -0.0049389 | 0.00023934 | -44.3939 | 72.4136 | -50.4272 | 72.2122 | -48.2162 | -50.2121 | -49.6399 | -48.3353 | 72.4365 | -50.4364 | -49.8184 | -50.0336 | -50.3494 | -50.1068 | -0.059509 | 0.013733 | -0.18768 | 2.1515 | 0.72784 | 0.15564 | 0.78735 | 0.21515 | -0.068664 | 0.036621 | -122.2183 | 0.33417 | 0.26093 | 0.018311 | 0.32959 | 0.086975 | 2.211 | 122.6395 | 0.40283 | 0.61798 | 122.8409 | 122.8729 | 122.7814 | 122.8043 | -122.8271 | -122.8363 | 122.58 | 0.54932 | 5.9738 | 2.0325
4122.1719 | 122.9279 | -50.4089 | 72.4091 | -0.11398 | 0.00019446 | 0.063521 | 0.07225 | 0.0029374 | 0.0043281 | 0.0073444 | -0.037964 | -0.00039305 | 0.0029906 | -0.00058098 | -0.0032151 | -0.0051527 | -0.00061526 | -44.4809 | 72.4182 | -50.5096 | 71.933 | -48.1293 | -50.1022 | -49.791 | -48.4634 | 72.4915 | -50.441 | -49.9329 | -50.2167 | -50.5463 | -50.2213 | -0.10071 | 0.009155 | -0.47608 | 2.2797 | 0.61798 | 0.3067 | 0.71869 | 0.40741 | -0.032043 | 0.082397 | -122.3419 | 0.19226 | 0.18768 | -0.13733 | 0.21973 | -0.10529 | 2.3804 | 122.4426 | 0.2243 | 0.50812 | 122.9279 | 122.9324 | 122.8271 | 122.9004 | -122.9187 | -122.85 | 122.3419 | 0.47607 | 5.928 | 1.9455
4123.1719 | 122.9691 | -50.386 | 72.3816 | -0.060578 | -0.0017281 | 0.062025 | 0.0699 | 0.0027238 | 0.0019781 | 0.0060626 | -0.034912 | 0.0028113 | 0.0036316 | 0.0043322 | -0.0032151 | -0.0055799 | 0.0017345 | -44.4214 | 72.3907 | -50.4822 | 72.1115 | -48.3444 | -50.354 | -49.7681 | -48.4589 | 72.4457 | -50.4456 | -49.9008 | -50.1709 | -50.5051 | -50.1984 | -0.096131 | 0.009155 | -0.27008 | 2.0416 | 0.61798 | 0.032043 | 0.71411 | 0.12817 | -0.05951 | 0.064087 | -122.2824 | 0.21515 | 0.18768 | -0.11902 | 0.24719 | -0.059509 | 2.1378 | 122.5937 | 0.27466 | 0.54474 | 122.8729 | 122.8912 | 122.7768 | 122.8317 | -122.8638 | -122.8271 | 122.4976 | 0.48523 | 5.9647 | 1.9272
4124.1719 | 123.0515 | -50.3769 | 72.377 | -0.060578 | 0.00062166 | 0.061385 | 0.0699 | 0.00251 | 0.0024053 | 0.0037128 | -0.01355 | 0.0019567 | 0.00042723 | 0.0017688 | -0.0030013 | -0.0040845 | -0.00040166 | -44.4077 | 72.4091 | -50.4501 | 72.1756 | -48.2666 | -50.2945 | -49.7177 | -48.3582 | 72.4411 | -50.4181 | -49.8413 | -50.0748 | -50.4272 | -50.1068 | -0.073242 | 0.032044 | -0.20142 | 2.1103 | 0.65918 | 0.082397 | 0.73242 | 0.15564 | -0.041199 | 0.064087 | -122.2183 | 0.30212 | 0.27008 | -0.050354 | 0.31128 | -0.009155 | 2.1835 | 122.6257 | 0.34332 | 0.57678 | 122.8592 | 122.8592 | 122.7859 | 122.818 | -122.8271 | -122.7951 | 122.5525 | 0.53558 | 5.9692 | 2.0187
4125.1719 | 123.0194 | -50.386 | 72.3953 | -0.13687 | 0.00040806 | 0.062025 | 0.070113 | 0.0016556 | 0.0024053 | 0.0052082 | 0.0047608 | 0.00046135 | 0.001709 | 0.001128 | -0.0019333 | -0.0055799 | -0.00018806 | -44.4122 | 72.3999 | -50.4639 | 72.1436 | -48.2529 | -50.3174 | -49.7269 | -48.3902 | 72.4319 | -50.4318 | -49.8642 | -50.116 | -50.4181 | -50.1114 | -0.07782 | 0.004577 | -0.25177 | 2.1332 | 0.65918 | 0.068664 | 0.737 | 0.14648 | -0.045777 | 0.036621 | -122.2595 | 0.27008 | 0.27466 | -0.032044 | 0.32043 | 0.013733 | 2.211 | 122.6074 | 0.31586 | 0.56763 | 122.8638 | 122.8638 | 122.7859 | 122.818 | -122.8592 | -122.8271 | 122.5296 | 0.52185 | 5.9738 | 1.9958
4126.1719 | 123.0881 | -50.3403 | 72.4045 | -0.11398 | -0.0013009 | 0.063521 | 0.069259 | 0.0012284 | 0.00026909 | 0.0034992 | 0.071899 | 3.4148e-05 | 0.0019226 | -0.001222 | -0.0023605 | -0.0077161 | -0.0033923 | -44.3253 | 72.4228 | -50.4089 | 72.2443 | -48.1155 | -50.1709 | -49.5941 | -48.2712 | 72.4686 | -50.4044 | -49.791 | -50.0107 | -50.3403 | -50.0748 | -0.068665 | 0.018311 | -0.16022 | 2.2247 | 0.74616 | 0.16937 | 0.81482 | 0.23804 | -0.064087 | 0.064087 | -122.1954 | 0.32959 | 0.2655 | 0 | 0.32959 | 0.064087 | 2.2934 | 122.6532 | 0.39368 | 0.6134 | 122.8317 | 122.8729 | 122.7631 | 122.8088 | -122.8134 | -122.8088 | 122.5845 | 0.54932 | 6.015 | 2.0691
4127.1719 | 122.9324 | -50.3906 | 72.4365 | -0.10635 | -0.00087374 | 0.060744 | 0.076736 | 0.0022964 | -0.0012261 | 0.0037128 | -0.047119 | 0.0038793 | 0.003418 | 0.0013416 | -0.0038559 | -0.0045117 | -0.00018806 | -44.3802 | 72.4274 | -50.4822 | 72.345 | -48.1476 | -50.441 | -49.7452 | -48.4634 | 72.4869 | -50.4364 | -49.9146 | -50.1938 | -50.5371 | -50.1846 | -0.091553 | -0.009155 | -0.091552 | 2.243 | 0.64545 | -0.050354 | 0.737 | 0.041199 | -0.045776 | 0.050354 | -122.3511 | 0.19684 | 0.20599 | -0.14648 | 0.25177 | -0.10071 | 2.3346 | 122.8271 | 0.24261 | 0.52185 | 122.9095 | 122.9233 | 122.818 | 122.8775 | -122.9187 | -122.8729 | 122.7356 | 0.47607 | 6.0104 | 1.9272
4128.1719 | 122.8958 | -50.3906 | 72.4365 | -0.12924 | 0.0036125 | 0.06288 | 0.07289 | 0.00037377 | -0.0012261 | 0.0067036 | -0.21497 | 0.0015295 | -0.0019226 | 0.0058276 | -0.0044967 | -0.0047253 | 0.00045294 | -44.3939 | 72.4411 | -50.4639 | 72.1344 | -48.262 | -50.3403 | -49.7864 | -48.2529 | 72.4823 | -50.4089 | -49.9146 | -50.1663 | -50.5142 | -50.2029 | -0.073242 | 0.004578 | -0.30212 | 2.1286 | 0.60425 | 0.050354 | 0.67749 | 0.1236 | -0.018311 | 0.045777 | -122.3511 | 0.2243 | 0.18768 | -0.1236 | 0.20599 | -0.10529 | 2.2018 | 122.5983 | 0.24261 | 0.49438 | 122.905 | 122.8912 | 122.8317 | 122.8729 | -122.9004 | -122.8455 | 122.525 | 0.47607 | 5.9967 | 2.1378
4129.1719 | 122.9599 | -50.3769 | 72.4365 | -0.10635 | 0.0019035 | 0.064589 | 0.071395 | -0.0011214 | 0.00069649 | 0.00414 | -0.034912 | 0.0032385 | 0.00085443 | -0.0018628 | -0.0023605 | -0.0051527 | 0.0030163 | -44.4077 | 72.4594 | -50.4593 | 72.139 | -48.2346 | -50.3265 | -49.7452 | -48.4451 | 72.4777 | -50.4181 | -49.8825 | -50.1617 | -50.5096 | -50.1892 | -0.082398 | 0.022889 | -0.29755 | 2.1423 | 0.63171 | 0.050354 | 0.71411 | 0.13275 | -0.041199 | 0.041199 | -122.319 | 0.21515 | 0.18768 | -0.13275 | 0.22888 | -0.091553 | 2.2247 | 122.5983 | 0.25635 | 0.53558 | 122.9187 | 122.8958 | 122.8363 | 122.8546 | -122.8958 | -122.8546 | 122.5159 | 0.49439 | 5.9692 | 1.9318
4130.1719 | 122.9416 | -50.3632 | 72.4457 | -0.19028 | -1.9142e-05 | 0.062666 | 0.069472 | 0.0050736 | 0.0015509 | 0.0020038 | -0.041016 | 0.0017431 | 0.0023498 | 5.9824e-05 | -0.00086511 | -0.0053663 | 0.0023755 | -44.2612 | 72.4869 | -50.4135 | 72.1481 | -48.2208 | -50.3632 | -49.7452 | -48.4497 | 72.4915 | -50.4318 | -49.8734 | -50.1617 | -50.5051 | -50.1938 | -0.050354 | 0.041198 | -0.29755 | 2.1423 | 0.61798 | 0 | 0.66833 | 0.050354 | -0.068665 | 0.045776 | -122.319 | 0.20142 | 0.16937 | -0.14191 | 0.23804 | -0.073242 | 2.1927 | 122.5616 | 0.27008 | 0.55847 | 122.9004 | 122.9233 | 122.85 | 122.8546 | -122.8592 | -122.8775 | 122.5113 | 0.48981 | 6.102 | 1.9135
4131.1719 | 123.0194 | -50.3357 | 72.4457 | -0.068207 | 0.0016899 | 0.06288 | 0.067977 | -0.0024032 | 0.0017645 | 0.0039264 | 0.071899 | 0.0011023 | -0.00021357 | -0.0037854 | -0.0019333 | -0.0079297 | -0.0012561 | -44.2657 | 72.4823 | -50.3815 | 72.2672 | -48.0377 | -50.1526 | -49.585 | -48.2941 | 72.4731 | -50.3632 | -49.8001 | -49.9969 | -50.3494 | -50.0839 | -0.045777 | 0.036621 | -0.17853 | 2.298 | 0.75073 | 0.1831 | 0.79651 | 0.22888 | -0.027466 | 0.027466 | -122.2458 | 0.33874 | 0.25177 | -0.013733 | 0.27924 | 0.013733 | 2.3438 | 122.6486 | 0.36621 | 0.56305 | 122.8638 | 122.8363 | 122.818 | 122.8088 | -122.8271 | -122.8088 | 122.6028 | 0.53558 | 6.0699 | 2.0416
4132.1719 | 122.9736 | -50.3815 | 72.4594 | -0.075836 | -0.0010873 | 0.062666 | 0.069259 | 0.00016017 | 5.5488e-05 | 0.0052082 | -0.059326 | 0.00088875 | 0.00085443 | 0.0024096 | -0.0025741 | -0.0066479 | -0.00061526 | -44.3893 | 72.4594 | -50.4364 | 72.1756 | -48.1842 | -50.3174 | -49.7269 | -48.3948 | 72.4777 | -50.3998 | -49.8688 | -50.1205 | -50.4639 | -50.1526 | -0.054931 | 0 | -0.28381 | 2.1973 | 0.6546 | 0.064087 | 0.70953 | 0.11902 | -0.01831 | 0.01831 | -122.3282 | 0.26093 | 0.22888 | -0.082397 | 0.24719 | -0.064087 | 2.2522 | 122.612 | 0.27924 | 0.53101 | 122.8958 | 122.8775 | 122.8409 | 122.8592 | -122.8958 | -122.8592 | 122.5571 | 0.5127 | 5.9921 | 1.9867
4133.1719 | 122.9599 | -50.3906 | 72.4411 | -0.037689 | 0.00040806 | 0.062453 | 0.070754 | -0.0013352 | 0.0011237 | 0.0043536 | -0.034912 | 0.0011023 | 0.001709 | 0.0034778 | -0.0030013 | -0.0062207 | 0.0025891 | -44.3665 | 72.4869 | -50.4272 | 72.1481 | -48.1796 | -50.3174 | -49.7314 | -48.4222 | 72.5189 | -50.4044 | -49.8734 | -50.1389 | -50.4959 | -50.1526 | -0.036621 | 0.045776 | -0.29297 | 2.211 | 0.65918 | 0.073242 | 0.6958 | 0.10986 | -0.013733 | 0.07782 | -122.3145 | 0.25177 | 0.23804 | -0.10529 | 0.25177 | -0.091553 | 2.2476 | 122.5754 | 0.2655 | 0.53101 | 122.9141 | 122.9233 | 122.8775 | 122.9095 | -122.8683 | -122.8455 | 122.5388 | 0.51727 | 6.0242 | 1.9684
4134.1719 | 122.8912 | -50.354 | 72.4594 | -0.083466 | 0.0021171 | 0.065871 | 0.070968 | 0.0020828 | -0.00037171 | 0.003072 | -0.050171 | 0.0025975 | 0.00042723 | -0.00079478 | -0.0010787 | -0.0062207 | 0.0038709 | -44.3344 | 72.4777 | -50.3998 | 72.1481 | -48.1796 | -50.3036 | -49.736 | -48.4543 | 72.5418 | -50.3952 | -49.8917 | -50.1663 | -50.4959 | -50.1892 | -0.045776 | 0.01831 | -0.31128 | 2.1744 | 0.61798 | 0.050354 | 0.66376 | 0.09613 | -0.041199 | 0.082397 | -122.3511 | 0.18768 | 0.1648 | -0.14191 | 0.20599 | -0.10071 | 2.2202 | 122.5479 | 0.22888 | 0.50354 | 122.8775 | 122.937 | 122.8317 | 122.8958 | -122.8592 | -122.8546 | 122.5021 | 0.46234 | 6.0196 | 1.8997
4135.1719 | 122.9233 | -50.354 | 72.4915 | -0.10635 | -0.00087374 | 0.062239 | 0.071609 | 0.0040054 | 0.0030463 | 0.0060626 | -0.03186 | -0.00017945 | 0.0021362 | 0.0071094 | -0.0021469 | -0.0062207 | 0.00023934 | -44.3665 | 72.5006 | -50.441 | 72.1664 | -48.1201 | -50.2991 | -49.7314 | -48.4177 | 72.5098 | -50.3769 | -49.8779 | -50.1617 | -50.4959 | -50.1617 | -0.086975 | 0.009155 | -0.32501 | 2.2339 | 0.62256 | 0.054932 | 0.70953 | 0.14191 | -0.022888 | 0.018311 | -122.3694 | 0.19226 | 0.19226 | -0.14191 | 0.21515 | -0.11902 | 2.3209 | 122.6074 | 0.21515 | 0.49896 | 122.9416 | 122.8867 | 122.8546 | 122.8638 | -122.9324 | -122.8683 | 122.5204 | 0.47607 | 5.9875 | 1.9363
4136.1719 | 123.0148 | -50.3128 | 72.4731 | -0.11398 | -0.00044654 | 0.06288 | 0.066482 | 0.00016017 | 0.0013373 | 0.0056354 | 0.068848 | 3.4148e-05 | 0.0014954 | -0.0031446 | -0.0012925 | -0.0066479 | 0.00023934 | -44.3527 | 72.464 | -50.3815 | 72.2351 | -48.0331 | -50.2258 | -49.6307 | -48.3307 | 72.4823 | -50.3815 | -49.8001 | -50.029 | -50.3494 | -50.0839 | -0.068665 | -0.009156 | -0.23804 | 2.2797 | 0.68207 | 0.086975 | 0.75073 | 0.15564 | -0.068665 | 0.009155 | -122.2733 | 0.28381 | 0.22888 | -0.036621 | 0.29755 | 0.032044 | 2.3483 | 122.6166 | 0.35248 | 0.58136 | 122.8455 | 122.8638 | 122.7768 | 122.7951 | -122.8546 | -122.8546 | 122.5479 | 0.5127 | 5.9601 | 1.9821
4137.1719 | 122.9645 | -50.354 | 72.464 | 0.12253 | -0.00044654 | 0.062453 | 0.0699 | 0.00251 | 0.00091009 | 0.0043536 | -0.041016 | 0.0015295 | 0.001068 | -0.006349 | -0.0047103 | -0.0051527 | 0.0019483 | -44.3985 | 72.5098 | -50.4044 | 72.1802 | -48.1247 | -50.3082 | -49.6902 | -48.3856 | 72.5143 | -50.3998 | -49.8642 | -50.0885 | -50.4684 | -50.148 | -0.050354 | 0.045777 | -0.28381 | 2.2293 | 0.66376 | 0.045776 | 0.71411 | 0.09613 | -0.045776 | 0.050354 | -122.3282 | 0.2655 | 0.20599 | -0.11444 | 0.25177 | -0.068665 | 2.2797 | 122.5845 | 0.31128 | 0.53558 | 122.9141 | 122.9141 | 122.8638 | 122.8683 | -122.8683 | -122.8638 | 122.5342 | 0.48981 | 5.9555 | 1.9684
4138.1719 | 122.9507 | -50.3311 | 72.4823 | -0.075836 | -0.0021555 | 0.061598 | 0.073745 | 0.0040054 | -0.00037171 | 0.002431 | 0.0047608 | 0.0017431 | 0.00085443 | -0.00058098 | -0.0027877 | -0.0053663 | -0.0029651 | -44.371 | 72.496 | -50.4227 | 72.3541 | -47.9095 | -50.354 | -49.736 | -48.4268 | 72.551 | -50.3769 | -49.8596 | -50.148 | -50.4684 | -50.1526 | -0.091552 | 0.013733 | -0.12817 | 2.4216 | 0.59509 | -0.022888 | 0.68664 | 0.068664 | -0.045776 | 0.068664 | -122.3419 | 0.18311 | 0.17853 | -0.13733 | 0.2243 | -0.091553 | 2.5131 | 122.7768 | 0.22888 | 0.51727 | 122.9187 | 122.9279 | 122.8271 | 122.8821 | -122.905 | -122.8592 | 122.6852 | 0.4715 | 5.9601 | 1.9043
4139.1719 | 122.9462 | -50.322 | 72.4915 | -0.11398 | 0.0014761 | 0.063094 | 0.069045 | -5.343e-05 | -0.0014399 | 0.0056354 | -0.056274 | 0.00088875 | 0.001709 | -0.0020764 | -0.0027877 | -0.0075025 | 0.0038709 | -44.3802 | 72.5143 | -50.4227 | 72.1573 | -48.0927 | -50.2853 | -49.7131 | -48.6649 | 72.4869 | -50.4227 | -49.8322 | -50.0885 | -50.4868 | -50.148 | -0.10071 | 0.022888 | -0.33417 | 2.2293 | 0.60882 | 0.036621 | 0.70953 | 0.13733 | -0.10071 | -0.004578 | -122.3236 | 0.23346 | 0.17395 | -0.1648 | 0.27466 | -0.064087 | 2.33 | 122.58 | 0.33417 | 0.59052 | 122.937 | 122.9095 | 122.8363 | 122.8088 | -122.9141 | -122.9141 | 122.4792 | 0.48981 | 5.9418 | 1.6571
4140.1719 | 122.9416 | -50.3265 | 72.5098 | -0.052948 | -1.9142e-05 | 0.062239 | 0.070968 | -0.00069423 | 0.0024053 | 0.0056354 | -0.028809 | 0.0019567 | 0.0019226 | 0.002196 | -0.0032151 | -0.0064343 | -0.00040166 | -44.339 | 72.5189 | -50.3723 | 72.2122 | -48.0103 | -50.2304 | -49.6628 | -48.3536 | 72.5601 | -50.354 | -49.8367 | -50.1205 | -50.473 | -50.1389 | -0.045776 | 0.009155 | -0.29755 | 2.3163 | 0.66376 | 0.09613 | 0.70953 | 0.14191 | -0.027466 | 0.050354 | -122.3465 | 0.20599 | 0.18768 | -0.14648 | 0.21515 | -0.11902 | 2.3621 | 122.5845 | 0.23346 | 0.51727 | 122.8912 | 122.9141 | 122.8455 | 122.8867 | -122.8821 | -122.8638 | 122.5388 | 0.48981 | 5.9875 | 1.973
4141.1719 | 122.937 | -50.3448 | 72.4915 | -0.037689 | 0.0021171 | 0.064803 | 0.071181 | -0.0026168 | 0.00069649 | 0.0047808 | -0.034912 | 0.0023839 | 0.0025634 | -0.0020764 | -0.0036423 | -0.0066479 | -0.00018806 | -44.3161 | 72.5281 | -50.3677 | 72.226 | -47.9919 | -50.235 | -49.6582 | -48.3398 | 72.5601 | -50.3494 | -49.8322 | -50.0977 | -50.441 | -50.116 | -0.022888 | 0.036621 | -0.2655 | 2.3529 | 0.68665 | 0.10986 | 0.70953 | 0.13275 | -0.004577 | 0.068665 | -122.3236 | 0.24719 | 0.22888 | -0.09613 | 0.23346 | -0.091553 | 2.3758 | 122.5937 | 0.25177 | 0.51727 | 122.8958 | 122.9095 | 122.8729 | 122.905 | -122.8592 | -122.8409 | 122.5708 | 0.5127 | 6.0287 | 2.005
4142.1719 | 122.9507 | -50.3128 | 72.5143 | -0.075836 | -0.00023294 | 0.064375 | 0.071181 | -0.0021896 | 0.0019781 | 0.00093559 | -0.03186 | 0.0030249 | 0.001709 | 0.002196 | -0.0019333 | -0.0064343 | -0.00082886 | -44.2932 | 72.5006 | -50.3677 | 72.2443 | -47.9553 | -50.2121 | -49.6262 | -48.2986 | 72.583 | -50.3265 | -49.8047 | -50.0748 | -50.4135 | -50.0931 | -0.054932 | -0.013733 | -0.27008 | 2.3575 | 0.68664 | 0.10071 | 0.74158 | 0.15564 | -0.013733 | 0.068665 | -122.319 | 0.23804 | 0.21973 | -0.10071 | 0.23346 | -0.086975 | 2.4124 | 122.612 | 0.25177 | 0.52185 | 122.8683 | 122.9095 | 122.8134 | 122.8958 | -122.8821 | -122.8409 | 122.5571 | 0.50812 | 6.0196 | 2.0142
4143.1719 | 122.9233 | -50.3174 | 72.5189 | -0.060578 | 0.0010489 | 0.064375 | 0.070968 | -0.0015488 | 0.0019781 | 0.0037128 | -0.03186 | 0.0019567 | 0.0012818 | 0.0024096 | -0.00086511 | -0.0053663 | 0.0021619 | -44.3161 | 72.5189 | -50.3586 | 72.2076 | -48.0057 | -50.2304 | -49.6765 | -48.3307 | 72.583 | -50.3448 | -49.8505 | -50.1114 | -50.4501 | -50.1251 | -0.041199 | 0 | -0.31128 | 2.3117 | 0.64087 | 0.086975 | 0.68207 | 0.12817 | -0.027466 | 0.064087 | -122.3694 | 0.20599 | 0.19226 | -0.13275 | 0.21973 | -0.10528 | 2.3529 | 122.5662 | 0.23346 | 0.49439 | 122.8775 | 122.9279 | 122.8363 | 122.9004 | -122.8775 | -122.8638 | 122.525 | 0.46692 | 6.0013 | 1.9867
4144.1719 | 122.937 | -50.3128 | 72.5052 | -0.18265 | 0.0010489 | 0.061598 | 0.071609 | 0.00080117 | 0.0030463 | 0.0037128 | -0.0074462 | 0.0011023 | 0.001068 | -0.00058098 | -0.0032151 | -0.0042981 | 0.0047253 | -44.3069 | 72.5601 | -50.3586 | 72.2031 | -47.9874 | -50.267 | -49.6811 | -48.349 | 72.551 | -50.3357 | -49.8276 | -50.0885 | -50.4181 | -50.1251 | -0.045777 | 0.054932 | -0.30212 | 2.3254 | 0.63171 | 0.045776 | 0.67749 | 0.091553 | -0.022888 | 0.045776 | -122.3328 | 0.2243 | 0.18768 | -0.10529 | 0.21057 | -0.082398 | 2.3712 | 122.5616 | 0.24719 | 0.50812 | 122.9187 | 122.8867 | 122.8729 | 122.8638 | -122.8638 | -122.8409 | 122.5159 | 0.48523 | 6.0059 | 1.9638
4145.1719 | 122.905 | -50.3311 | 72.5418 | -0.10635 | 0.0021171 | 0.063734 | 0.069472 | -0.0013352 | 0.0021917 | 0.0062762 | -0.044067 | 0.0025975 | 0.001709 | 0.0028368 | -0.0012925 | -0.0057935 | 0.0015209 | -44.3298 | 72.5464 | -50.3815 | 72.1939 | -47.9691 | -50.267 | -49.6902 | -48.381 | 72.5601 | -50.3494 | -49.8322 | -50.116 | -50.4547 | -50.1205 | -0.050354 | 0.004578 | -0.3479 | 2.3621 | 0.64087 | 0.064087 | 0.69122 | 0.11444 | -0.01831 | 0.018311 | -122.374 | 0.21515 | 0.21057 | -0.1236 | 0.22888 | -0.10529 | 2.4124 | 122.5754 | 0.23346 | 0.51727 | 122.9279 | 122.9095 | 122.8775 | 122.8912 | -122.9233 | -122.8912 | 122.525 | 0.49896 | 6.0013 | 1.9501
4146.1719 | 122.9553 | -50.2945 | 72.5418 | -0.075836 | 0.0016899 | 0.06288 | 0.069686 | 0.00037377 | 0.00091009 | 0.0049946 | -0.041016 | 0.0025975 | 0.00021363 | 0.0026232 | -0.0034287 | -0.0060071 | -0.0023243 | -44.3161 | 72.5372 | -50.3403 | 72.2305 | -47.9416 | -50.2121 | -49.6628 | -48.349 | 72.5876 | -50.3311 | -49.823 | -50.0977 | -50.4227 | -50.0931 | -0.045776 | -0.004578 | -0.31128 | 2.3529 | 0.63171 | 0.082398 | 0.67749 | 0.12817 | -0.036621 | 0.045776 | -122.3648 | 0.19684 | 0.20142 | -0.12817 | 0.23804 | -0.091552 | 2.3987 | 122.5708 | 0.23346 | 0.50812 | 122.8775 | 122.9187 | 122.8317 | 122.8821 | -122.8821 | -122.8729 | 122.525 | 0.4715 | 5.9784 | 1.9455
4147.1719 | 122.9095 | -50.2808 | 72.5235 | -0.052948 | 0.0023307 | 0.062453 | 0.069259 | 0.001442 | 0.00048269 | 0.0064898 | -0.03186 | 0.0030249 | 0.002777 | -0.0035718 | -0.0012925 | -0.0079297 | 0.0038709 | -44.3024 | 72.5418 | -50.3586 | 72.2488 | -47.905 | -50.1801 | -49.6399 | -48.3124 | 72.6013 | -50.3265 | -49.8001 | -50.0656 | -50.4044 | -50.0793 | -0.07782 | 0.01831 | -0.27466 | 2.3758 | 0.64087 | 0.10071 | 0.71869 | 0.17853 | -0.045776 | 0.077819 | -122.3236 | 0.21515 | 0.20142 | -0.1236 | 0.24719 | -0.07782 | 2.4536 | 122.6074 | 0.26093 | 0.52643 | 122.9004 | 122.9279 | 122.8226 | 122.8821 | -122.8821 | -122.85 | 122.5296 | 0.48065 | 5.9784 | 1.9684
4148.1719 | 122.9874 | -50.2579 | 72.5739 | -0.068207 | 0.00040806 | 0.062666 | 0.070113 | 0.00080117 | 0.0028327 | 0.0045672 | -0.03186 | -0.0012477 | 0.0025634 | 0.00048702 | -0.0019333 | -0.0068615 | 0.0032299 | -44.2383 | 72.5739 | -50.3265 | 72.3221 | -47.7951 | -50.116 | -49.5804 | -48.2208 | 72.5967 | -50.2899 | -49.7498 | -50.0107 | -50.3357 | -50.0473 | -0.068664 | 0 | -0.25177 | 2.4628 | 0.67749 | 0.14191 | 0.74616 | 0.21057 | -0.032043 | 0.022888 | -122.3236 | 0.24719 | 0.21057 | -0.077819 | 0.24262 | -0.045776 | 2.5314 | 122.6486 | 0.27924 | 0.54016 | 122.9004 | 122.8867 | 122.8317 | 122.8546 | -122.9004 | -122.8638 | 122.58 | 0.50812 | 6.0196 | 2.037
4149.1719 | 122.9462 | -50.2945 | 72.583 | -0.098725 | 0.0019035 | 0.062025 | 0.070327 | -0.00026703 | 0.00069649 | 0.003072 | -0.01355 | 0.00067495 | 0.00021363 | 0.0049732 | -0.0021469 | -0.0064343 | 0.0023755 | -44.2703 | 72.5693 | -50.3082 | 72.2763 | -47.8226 | -50.1526 | -49.6033 | -48.2529 | 72.6151 | -50.2991 | -49.7681 | -50.0381 | -50.3723 | -50.0656 | -0.013733 | -0.013733 | -0.3067 | 2.4719 | 0.69122 | 0.14191 | 0.70496 | 0.15564 | -0.004577 | 0.032043 | -122.3511 | 0.25635 | 0.22888 | -0.077819 | 0.23346 | -0.073242 | 2.4857 | 122.5845 | 0.26093 | 0.53101 | 122.8775 | 122.9141 | 122.8638 | 122.9095 | -122.8912 | -122.8821 | 122.5708 | 0.52643 | 6.0242 | 2.0416
4150.1719 | 122.9782 | -50.2579 | 72.5601 | -0.045319 | -0.00044654 | 0.061812 | 0.071181 | 0.00037377 | 0.0024053 | 0.0047808 | -0.016602 | -0.00060665 | 0.0014954 | -0.00058098 | -0.0030013 | -0.0062207 | -0.00040166 | -44.2474 | 72.5784 | -50.3082 | 72.2855 | -47.818 | -50.1434 | -49.5987 | -48.2483 | 72.6059 | -50.3036 | -49.7589 | -50.0244 | -50.354 | -50.061 | -0.050354 | 0.01831 | -0.27466 | 2.4399 | 0.65918 | 0.11444 | 0.70953 | 0.16479 | -0.045776 | 0.045776 | -122.319 | 0.23346 | 0.19684 | -0.09613 | 0.24262 | -0.050354 | 2.4902 | 122.5937 | 0.27924 | 0.54474 | 122.8867 | 122.9095 | 122.8363 | 122.8638 | -122.8683 | -122.8638 | 122.5433 | 0.49896 | 6.0104 | 2.0096
4151.1719 | 122.9324 | -50.2396 | 72.551 | -0.068207 | 0.00040806 | 0.063521 | 0.069045 | 0.0018692 | 0.0019781 | 0.0032856 | -0.01355 | 0.0038793 | 0.00085443 | -0.0018628 | -0.0017197 | -0.0051527 | 0.0017345 | -44.2703 | 72.5739 | -50.3174 | 72.2672 | -47.8271 | -50.1709 | -49.6262 | -48.2666 | 72.6105 | -50.3036 | -49.7635 | -50.0565 | -50.3906 | -50.0748 | -0.07782 | 0.022889 | -0.28381 | 2.4124 | 0.6134 | 0.068665 | 0.69122 | 0.14648 | -0.064087 | 0.05951 | -122.3145 | 0.1831 | 0.16479 | -0.15106 | 0.22888 | -0.086975 | 2.4902 | 122.5845 | 0.24719 | 0.54016 | 122.8912 | 122.9141 | 122.8134 | 122.85 | -122.8683 | -122.8546 | 122.5067 | 0.47607 | 5.9692 | 1.973
4152.1719 | 122.9233 | -50.2716 | 72.5739 | -0.10635 | 0.00062166 | 0.064589 | 0.070968 | -0.0013352 | 0.00091009 | 0.0026446 | -0.034912 | 0.0021703 | 0.0012818 | 0.0041186 | -0.0032151 | -0.0055799 | 0.00066654 | -44.3069 | 72.5647 | -50.322 | 72.2305 | -47.8546 | -50.2121 | -49.649 | -48.3353 | 72.6151 | -50.3174 | -49.7955 | -50.0839 | -50.4318 | -50.0931 | -0.050354 | -0.009156 | -0.34332 | 2.417 | 0.62256 | 0.059509 | 0.67291 | 0.10986 | -0.045777 | 0.041198 | -122.3694 | 0.18768 | 0.17853 | -0.16022 | 0.2243 | -0.11444 | 2.4673 | 122.5525 | 0.23346 | 0.52185 | 122.8867 | 122.9324 | 122.8363 | 122.8867 | -122.8958 | -122.8912 | 122.5021 | 0.47607 | 5.9647 | 1.9363
4153.1719 | 122.9553 | -50.2533 | 72.5693 | -0.098725 | 0.00040806 | 0.063734 | 0.070968 | -0.0011214 | -0.0012261 | 0.0034992 | 0.0078126 | 0.0011023 | 0.0032044 | -0.0033582 | -0.0030013 | -0.0064343 | 0.0021619 | -44.2291 | 72.5876 | -50.2853 | 72.3129 | -47.7585 | -50.1434 | -49.5804 | -48.23 | 72.6196 | -50.2853 | -49.7406 | -50.0153 | -50.3586 | -50.0153 | -0.032043 | 0.01831 | -0.25635 | 2.4948 | 0.67291 | 0.10986 | 0.70496 | 0.14191 | -0.032043 | 0.050354 | -122.3099 | 0.23804 | 0.23804 | -0.10529 | 0.27008 | -0.073243 | 2.5269 | 122.5983 | 0.27008 | 0.54474 | 122.8729 | 122.905 | 122.8409 | 122.8729 | -122.8546 | -122.8546 | 122.5662 | 0.5127 | 6.0242 | 2.0233
4154.1719 | 122.9736 | -50.235 | 72.583 | -0.068207 | -0.00087374 | 0.061812 | 0.070541 | -0.00048063 | 0.0030463 | 0.0034992 | 0.001709 | 0.0011023 | 0.00085443 | -0.0061352 | -0.0032151 | -0.0053663 | -0.00082886 | -44.2245 | 72.6013 | -50.2899 | 72.3267 | -47.7264 | -50.1297 | -49.5483 | -48.1934 | 72.6242 | -50.2487 | -49.736 | -49.9741 | -50.2991 | -50.0015 | -0.054932 | 0.01831 | -0.25635 | 2.5085 | 0.68664 | 0.10529 | 0.74158 | 0.16022 | -0.013733 | 0.041199 | -122.319 | 0.26093 | 0.23346 | -0.064087 | 0.24719 | -0.050354 | 2.5635 | 122.6166 | 0.27466 | 0.51269 | 122.8912 | 122.8729 | 122.8363 | 122.8592 | -122.8729 | -122.8317 | 122.5616 | 0.49896 | 6.0104 | 2.0416
4155.1719 | 122.9782 | -50.2167 | 72.5922 | -0.098725 | 0.00083526 | 0.063094 | 0.069472 | -5.343e-05 | 0.0015509 | 0.0052082 | 0.001709 | 0.0013159 | 0.0036316 | 0.0019824 | -0.0023605 | -0.0072889 | 0.0021619 | -44.22 | 72.6151 | -50.3082 | 72.3129 | -47.7219 | -50.1068 | -49.5483 | -48.2117 | 72.6562 | -50.2487 | -49.7269 | -49.9603 | -50.2899 | -50.0198 | -0.091553 | 0.022888 | -0.27924 | 2.4948 | 0.66833 | 0.10986 | 0.75989 | 0.20142 | -0.032043 | 0.064087 | -122.319 | 0.25635 | 0.19684 | -0.073242 | 0.22888 | -0.041199 | 2.5864 | 122.6212 | 0.28839 | 0.52185 | 122.9233 | 122.905 | 122.8317 | 122.8729 | -122.9004 | -122.8409 | 122.5296 | 0.48981 | 5.9967 | 2.005
4156.1719 | 122.9874 | -50.235 | 72.6242 | -0.052948 | 0.00040806 | 0.06288 | 0.069045 | -0.001976 | 0.0024053 | 0.00414 | -0.16003 | 0.0036657 | 0.00085443 | 0.0024096 | -0.0040695 | -0.0047253 | 0.0032299 | -44.2154 | 72.6105 | -50.2899 | 72.3267 | -47.6898 | -50.116 | -49.5483 | -48.1201 | 72.6608 | -50.2579 | -49.7131 | -49.9329 | -50.2991 | -49.9924 | -0.054932 | -0.013733 | -0.29755 | 2.5452 | 0.68664 | 0.11902 | 0.74158 | 0.17395 | -0.022889 | 0.036621 | -122.3373 | 0.30212 | 0.24261 | -0.064087 | 0.2655 | -0.041198 | 2.6001 | 122.6166 | 0.32501 | 0.54474 | 122.9004 | 122.9187 | 122.8455 | 122.8958 | -122.9141 | -122.8821 | 122.5616 | 0.52185 | 6.0196 | 2.1149
4157.1719 | 122.9645 | -50.2075 | 72.6196 | -0.091095 | 0.0010489 | 0.063734 | 0.069045 | 0.003151 | 0.00026909 | 0.0043536 | -0.022705 | 0.0015295 | 0.0014954 | -0.00079478 | -0.0027877 | -0.0072889 | 0.0036571 | -44.2062 | 72.6151 | -50.2853 | 72.3495 | -47.6852 | -50.0885 | -49.5346 | -48.1796 | 72.6654 | -50.2579 | -49.7086 | -50.0244 | -50.2167 | -49.9878 | -0.077819 | -0.004578 | -0.27008 | 2.5223 | 0.67291 | 0.11902 | 0.75073 | 0.19684 | -0.050354 | 0.045776 | -122.3282 | 0.18311 | 0.21973 | -0.009155 | 0.27008 | 0.041199 | 2.6001 | 122.6349 | 0.23346 | 0.54932 | 122.9004 | 122.9233 | 122.8226 | 122.8729 | -122.905 | -122.8775 | 122.5571 | 0.49896 | 6.0013 | 2.0279
4158.1719 | 122.9874 | -50.2258 | 72.6105 | -0.083466 | -1.9142e-05 | 0.062666 | 0.068191 | 0.00037377 | 0.0019781 | 0.0049946 | -0.016602 | 0.00067495 | 0.0019226 | 0.001128 | -0.0019333 | -0.0081433 | -0.00040166 | -44.2108 | 72.6242 | -50.2258 | 72.3495 | -47.6624 | -50.1114 | -49.5438 | -48.1979 | 72.6288 | -50.2533 | -49.7131 | -49.9786 | -50.3128 | -49.9969 | 0 | 0.013733 | -0.26093 | 2.5635 | 0.68207 | 0.11444 | 0.68207 | 0.11444 | -0.027466 | 0.01831 | -122.3236 | 0.24719 | 0.22888 | -0.086975 | 0.25635 | -0.059509 | 2.5635 | 122.5754 | 0.27466 | 0.54016 | 122.85 | 122.8821 | 122.85 | 122.8546 | -122.8363 | -122.8638 | 122.5754 | 0.5127 | 6.015 | 2.0279
4159.1719 | 122.9507 | -50.2258 | 72.6196 | -0.068207 | 0.0027579 | 0.062239 | 0.072463 | -0.0028304 | 0.0021917 | 0.00414 | -0.0043946 | -0.00039305 | 0.0023498 | -0.00079478 | -0.0038559 | -0.0038709 | 0.0021619 | -44.2062 | 72.6334 | -50.2716 | 72.3679 | -47.6212 | -50.0839 | -49.53 | -48.1613 | 72.6471 | -50.2533 | -49.6948 | -49.9695 | -50.3082 | -49.9969 | -0.045776 | 0.013733 | -0.25177 | 2.6047 | 0.6958 | 0.14191 | 0.74158 | 0.18768 | -0.027466 | 0.027466 | -122.3145 | 0.25635 | 0.22888 | -0.082398 | 0.25635 | -0.054932 | 2.6505 | 122.6395 | 0.28381 | 0.55847 | 122.905 | 122.9004 | 122.8592 | 122.8729 | -122.8912 | -122.8729 | 122.5937 | 0.53101 | 6.0196 | 2.0645
4160.1719 | 122.9324 | -50.2167 | 72.6242 | -0.083466 | 0.00040806 | 0.06288 | 0.072036 | -0.00048063 | 0.0034735 | 0.0043536 | 0.001709 | 0.00024775 | 0.0014954 | -0.0050672 | -0.0027877 | -0.0064343 | 0.00045294 | -44.22 | 72.6059 | -50.2625 | 72.3221 | -47.6486 | -50.1205 | -49.5712 | -48.1934 | 72.6654 | -50.235 | -49.7406 | -49.9832 | -50.3265 | -50.0015 | -0.045776 | -0.018311 | -0.30212 | 2.5681 | 0.64545 | 0.096131 | 0.69122 | 0.14191 | -0.01831 | 0.041198 | -122.3648 | 0.23346 | 0.21515 | -0.10986 | 0.23346 | -0.091553 | 2.6138 | 122.5845 | 0.25177 | 0.49438 | 122.8683 | 122.9004 | 122.8226 | 122.8821 | -122.8867 | -122.8592 | 122.5388 | 0.47607 | 5.9967 | 2.0233
4161.1719 | 122.9507 | -50.2029 | 72.6608 | -0.091095 | 0.0025443 | 0.063521 | 0.072463 | 0.0012284 | 0.0030463 | 0.007558 | 0.0078126 | 0.0030249 | 0.0025634 | -0.00079478 | 0.0014847 | -0.0072889 | 0.0040845 | -44.1879 | 72.6425 | -50.2625 | 72.3312 | -47.6074 | -50.0793 | -49.5209 | -48.1476 | 72.6654 | -50.2396 | -49.6857 | -49.8917 | -50.2533 | -49.9741 | -0.059509 | -0.018311 | -0.32959 | 2.5955 | 0.68207 | 0.1236 | 0.74158 | 0.1831 | -0.036621 | 0.004577 | -122.3465 | 0.31128 | 0.22888 | -0.050354 | 0.2655 | -0.013733 | 2.655 | 122.5937 | 0.3479 | 0.55389 | 122.905 | 122.905 | 122.8455 | 122.8683 | -122.9233 | -122.9004 | 122.5342 | 0.51727 | 6.015 | 2.0554
4162.1719 | 122.9691 | -50.2075 | 72.6471 | -0.11398 | -0.00087374 | 0.063307 | 0.069259 | 0.0010148 | 0.0030463 | 0.0064898 | 0.023071 | -0.00017945 | 0.002777 | 5.9824e-05 | -0.0021469 | -0.0066479 | 0.0021619 | -44.2062 | 72.67 | -50.2716 | 72.3679 | -47.6303 | -50.0839 | -49.5026 | -48.1796 | 72.6791 | -50.2167 | -49.704 | -49.9329 | -50.2625 | -49.9924 | -0.064086 | 0.022888 | -0.27924 | 2.5772 | 0.70496 | 0.1236 | 0.76904 | 0.18768 | -0.009155 | 0.032043 | -122.3511 | 0.27466 | 0.21515 | -0.054931 | 0.2243 | -0.045776 | 2.6413 | 122.6395 | 0.28381 | 0.5127 | 122.9416 | 122.8958 | 122.8775 | 122.8867 | -122.9187 | -122.8638 | 122.5754 | 0.50354 | 6.0013 | 2.0279
4163.1719 | 122.9553 | -50.1938 | 72.6242 | -0.045319 | 0.0016899 | 0.062239 | 0.070754 | -0.001976 | 0.0036871 | 0.0039264 | 0.0078126 | 0.0019567 | 2.8e-08 | 5.9824e-05 | -0.0042831 | -0.0045117 | 0.0017345 | -44.1742 | 72.6517 | -50.267 | 72.377 | -47.5754 | -50.0793 | -49.5255 | -48.1567 | 72.6929 | -50.2213 | -49.6902 | -49.9283 | -50.2625 | -49.9695 | -0.073242 | 0.027465 | -0.24719 | 2.6184 | 0.66833 | 0.11444 | 0.74158 | 0.18768 | -0.027465 | 0.068664 | -122.3145 | 0.2655 | 0.22431 | -0.068664 | 0.25177 | -0.041199 | 2.6917 | 122.644 | 0.29297 | 0.53101 | 122.9187 | 122.9141 | 122.8455 | 122.8867 | -122.8912 | -122.8455 | 122.5708 | 0.50354 | 6.0196 | 2.037
4164.1719 | 122.9874 | -50.1984 | 72.6471 | -0.060578 | -0.00023294 | 0.065016 | 0.068191 | -0.0011214 | 0.0021917 | 0.00414 | 0.001709 | 0.00024775 | 0.00021363 | 0.0013416 | -0.0038559 | -0.0055799 | -0.00018806 | -44.1605 | 72.6471 | -50.2625 | 72.3587 | -47.5571 | -50.0565 | -49.5071 | -48.1476 | 72.6791 | -50.2167 | -49.6811 | -49.9237 | -50.2579 | -49.9649 | -0.064087 | 0 | -0.28839 | 2.6413 | 0.69122 | 0.14191 | 0.75531 | 0.20599 | -0.018311 | 0.032043 | -122.3282 | 0.27466 | 0.23346 | -0.05951 | 0.25177 | -0.041199 | 2.7054 | 122.6212 | 0.29297 | 0.53558 | 122.9095 | 122.8958 | 122.8455 | 122.8775 | -122.9095 | -122.8638 | 122.5571 | 0.51727 | 6.0379 | 2.0508
4165.1719 | 122.9599 | -50.1663 | 72.6425 | -0.060578 | 0.00062166 | 0.063948 | 0.071395 | -0.0041122 | 0.0017645 | 0.0032856 | 0.0078126 | 0.0015295 | 0.0023498 | -0.0025036 | -0.0025741 | -0.0064343 | 0.00066654 | -44.1742 | 72.6425 | -50.2579 | 72.3679 | -47.6212 | -50.1709 | -49.53 | -48.1247 | 72.6883 | -50.2304 | -49.6765 | -49.9466 | -50.2533 | -49.9603 | -0.091553 | 0 | -0.27466 | 2.5452 | 0.63629 | -0.004577 | 0.72785 | 0.086976 | -0.064087 | 0.045776 | -122.319 | 0.21973 | 0.20599 | -0.086975 | 0.27008 | -0.022888 | 2.6367 | 122.6257 | 0.28381 | 0.55389 | 122.9004 | 122.9187 | 122.8088 | 122.8546 | -122.9004 | -122.8729 | 122.5342 | 0.48981 | 5.9921 | 2.0416
4166.1719 | 122.9874 | -50.1755 | 72.6379 | -0.098725 | 0.0029715 | 0.062453 | 0.071395 | 0.0018692 | 0.0028327 | 0.0028582 | 0.02002 | 0.0028113 | 0.00085443 | -0.0027174 | -0.0030013 | -0.0075025 | 0.0042981 | -44.165 | 72.6334 | -50.2441 | 72.3862 | -47.5113 | -50.0702 | -49.498 | -48.111 | 72.6791 | -50.2029 | -49.649 | -49.9054 | -50.2579 | -49.9558 | -0.068665 | -0.004577 | -0.25177 | 2.6642 | 0.67749 | 0.10529 | 0.74616 | 0.17395 | -0.027466 | 0.041199 | -122.287 | 0.27008 | 0.21973 | -0.082398 | 0.24719 | -0.054932 | 2.7328 | 122.6303 | 0.29755 | 0.55389 | 122.8775 | 122.8821 | 122.8088 | 122.8546 | -122.8821 | -122.8409 | 122.5616 | 0.52643 | 6.0104 | 2.0645
4167.1719 | 122.9736 | -50.1801 | 72.6746 | -0.052948 | 0.0027579 | 0.06288 | 0.070754 | -0.0024032 | 0.0039007 | 0.0039264 | 0.02002 | 0.00067495 | 0.0021362 | 0.00070062 | -0.0032151 | -0.0057935 | 0.0038709 | -44.1605 | 72.6562 | -50.2441 | 72.3862 | -47.5204 | -50.0519 | -49.5026 | -48.1247 | 72.6837 | -50.2258 | -49.6628 | -50.029 | -50.1755 | -49.91 | -0.064087 | -0.018311 | -0.28839 | 2.6596 | 0.67749 | 0.12817 | 0.74158 | 0.19226 | -0.045776 | 0.009155 | -122.3373 | 0.15106 | 0.27008 | 0.004578 | 0.31586 | 0.050354 | 2.7237 | 122.6303 | 0.19684 | 0.56305 | 122.9004 | 122.9095 | 122.8363 | 122.8638 | -122.9187 | -122.9004 | 122.5662 | 0.51727 | 6.0196 | 2.0554
4168.1719 | 122.9599 | -50.1984 | 72.6105 | -0.11398 | -0.00044654 | 0.062453 | 0.070541 | 0.0044328 | 0.0030463 | 0.00414 | 0.0047608 | 0.00067495 | 0.0012818 | 0.002196 | -0.0023605 | -0.0068615 | 0.0019483 | -44.133 | 72.6334 | -50.235 | 72.3953 | -47.4884 | -50.061 | -49.5255 | -48.1247 | 72.67 | -50.2258 | -49.6719 | -49.9603 | -50.267 | -49.9695 | -0.036621 | 0.022888 | -0.21515 | 2.71 | 0.67291 | 0.13733 | 0.70953 | 0.17395 | -0.027466 | 0.059509 | -122.2824 | 0.23804 | 0.22888 | -0.068665 | 0.25635 | -0.041199 | 2.7466 | 122.6303 | 0.2655 | 0.55389 | 122.8683 | 122.8958 | 122.8317 | 122.8683 | -122.8455 | -122.8363 | 122.5937 | 0.52643 | 6.0654 | 2.0737
4169.1719 | 122.9645 | -50.1984 | 72.6746 | -0.060578 | -1.9142e-05 | 0.061385 | 0.070541 | -0.0049668 | 0.00069649 | 0.0043536 | 0.016968 | 0.0017431 | 0.0021362 | 0.00027342 | -0.0034287 | -0.0072889 | 0.00088014 | -44.1879 | 72.67 | -50.2579 | 72.345 | -47.5296 | -50.0793 | -49.5117 | -48.1796 | 72.702 | -50.2396 | -49.704 | -49.9283 | -50.2579 | -49.9649 | -0.05951 | -0.004578 | -0.32959 | 2.6688 | 0.68664 | 0.11902 | 0.74616 | 0.17853 | -0.041199 | 0.027465 | -122.3785 | 0.27008 | 0.23346 | -0.05951 | 0.27466 | -0.018311 | 2.7283 | 122.6028 | 0.31128 | 0.53558 | 122.9279 | 122.9416 | 122.8683 | 122.9004 | -122.9324 | -122.9141 | 122.5433 | 0.49439 | 6.0104 | 2.0187
4170.1719 | 122.9874 | -50.1801 | 72.6608 | -0.052948 | -1.9142e-05 | 0.063307 | 0.069259 | -5.343e-05 | 0.0017645 | 0.0077716 | 0.026123 | 0.00067495 | 0.0025634 | -0.0065626 | -0.00022431 | -0.0055799 | -0.0023243 | -44.133 | 72.67 | -50.2258 | 72.3816 | -47.4884 | -50.0519 | -49.4843 | -48.1384 | 72.6791 | -50.1846 | -49.6582 | -49.9054 | -50.2487 | -49.9466 | -0.045776 | 0.009155 | -0.27924 | 2.6917 | 0.6958 | 0.12817 | 0.74158 | 0.17395 | -0.004577 | 0.01831 | -122.319 | 0.27466 | 0.23346 | -0.068664 | 0.23804 | -0.064087 | 2.7374 | 122.6074 | 0.27923 | 0.52643 | 122.8958 | 122.8638 | 122.85 | 122.8592 | -122.8867 | -122.8455 | 122.5616 | 0.52185 | 6.0471 | 2.0416
4171.1719 | 122.9919 | -50.1663 | 72.6837 | -0.052948 | 0.0010489 | 0.064803 | 0.070327 | 0.001442 | 0.0017645 | 0.00414 | -0.0074462 | 0.0011023 | 0.0021362 | -0.001222 | -0.0032151 | -0.0068615 | -0.0010425 | -44.1467 | 72.67 | -50.2121 | 72.3862 | -47.4609 | -50.0381 | -49.4843 | -48.1339 | 72.702 | -50.1801 | -49.6628 | -49.8871 | -50.2487 | -49.9374 | -0.045776 | -0.013733 | -0.29755 | 2.7054 | 0.68207 | 0.12817 | 0.72784 | 0.17395 | -0.013733 | 0.01831 | -122.3465 | 0.27924 | 0.22888 | -0.082397 | 0.24262 | -0.068664 | 2.7512 | 122.5983 | 0.29297 | 0.51727 | 122.8821 | 122.8821 | 122.8363 | 122.8683 | -122.8958 | -122.8638 | 122.5525 | 0.50354 | 6.0196 | 2.0325
4172.1719 | 122.9187 | -50.1343 | 72.6608 | -0.083466 | -0.00023294 | 0.063307 | 0.0699 | -0.0011214 | 0.0017645 | 0.0049946 | -0.0043946 | 0.00088875 | 0.0021362 | -0.00464 | -0.0027877 | -0.0066479 | -0.00018806 | -44.1101 | 72.6608 | -50.2258 | 72.3862 | -47.4106 | -50.0427 | -49.4888 | -48.0927 | 72.6883 | -50.2121 | -49.6536 | -49.9054 | -50.2258 | -49.8276 | -0.091553 | 0 | -0.27466 | 2.7237 | 0.64545 | 0.091552 | 0.737 | 0.18311 | -0.07782 | 0.027465 | -122.3145 | 0.22888 | 0.3067 | -0.091553 | 0.38452 | -0.013733 | 2.8152 | 122.612 | 0.3067 | 0.55847 | 122.8867 | 122.9004 | 122.7951 | 122.8226 | -122.8867 | -122.8729 | 122.5204 | 0.48065 | 6.0242 | 2.0416
4173.1719 | 122.9782 | -50.1572 | 72.6608 | -0.075836 | 0.0012625 | 0.064162 | 0.069686 | 0.00037377 | -0.00058531 | 0.0067036 | -0.0013428 | 0.0013159 | 0.0032044 | -0.0035718 | -0.0017197 | -0.0051527 | -0.0018971 | -44.1193 | 72.6837 | -50.235 | 72.3907 | -47.4243 | -50.0153 | -49.4705 | -48.0927 | 72.7158 | -50.2121 | -49.6445 | -49.8962 | -50.2441 | -49.9329 | -0.077819 | 0.022888 | -0.27008 | 2.7328 | 0.68665 | 0.14191 | 0.76447 | 0.21973 | -0.054931 | 0.054931 | -122.3053 | 0.26093 | 0.2243 | -0.086975 | 0.27924 | -0.032044 | 2.8107 | 122.6257 | 0.31586 | 0.56763 | 122.9187 | 122.9279 | 122.8409 | 122.8729 | -122.8958 | -122.8729 | 122.5479 | 0.5127 | 6.0379 | 2.0645
4174.1719 | 122.9782 | -50.1572 | 72.67 | -0.11398 | 0.00062166 | 0.062666 | 0.067977 | -0.0011214 | 0.0013373 | 0.0043536 | 0.0078126 | 0.0019567 | 0.0019226 | -0.00464 | -0.0021469 | -0.0064343 | -0.00040166 | -44.1238 | 72.702 | -50.235 | 72.3999 | -47.4106 | -50.0198 | -49.4568 | -48.1064 | 72.6929 | -50.1846 | -49.6536 | -49.8871 | -50.235 | -49.9237 | -0.077819 | 0.032043 | -0.27008 | 2.7466 | 0.70038 | 0.13733 | 0.7782 | 0.21515 | -0.027465 | 0.022888 | -122.3236 | 0.27008 | 0.23346 | -0.077819 | 0.26093 | -0.050354 | 2.8244 | 122.6349 | 0.29755 | 0.53101 | 122.937 | 122.8775 | 122.8592 | 122.85 | -122.905 | -122.8546 | 122.5571 | 0.50354 | 6.0333 | 2.0508
4175.1719 | 122.9462 | -50.148 | 72.6929 | -0.098725 | -0.00023294 | 0.060316 | 0.069259 | 0.003151 | 0.0026191 | 0.0022174 | 0.023071 | 0.0023839 | 0.00085443 | -0.0025036 | -0.0044967 | -0.0062207 | 0.0028027 | -44.1284 | 72.6929 | -50.2304 | 72.3679 | -47.4289 | -50.061 | -49.4888 | -48.1476 | 72.7386 | -50.1801 | -49.6582 | -49.9146 | -50.2487 | -49.9603 | -0.082398 | 0 | -0.32501 | 2.7191 | 0.65918 | 0.086975 | 0.74158 | 0.16937 | -0.032044 | 0.045776 | -122.3511 | 0.23346 | 0.18768 | -0.10071 | 0.21973 | -0.068664 | 2.8015 | 122.5983 | 0.2655 | 0.52185 | 122.9233 | 122.9187 | 122.8409 | 122.8867 | -122.9233 | -122.8729 | 122.5159 | 0.48981 | 6.0196 | 2.0004
4176.1719 | 122.9782 | -50.1389 | 72.6883 | -0.037689 | -1.9142e-05 | 0.064162 | 0.067763 | -0.0026168 | 0.0017645 | 0.0062762 | 0.013916 | 0.00046135 | 0.0025634 | -0.0072034 | -0.0019333 | -0.0051527 | 0.0019483 | -44.1238 | 72.7066 | -50.235 | 72.3907 | -47.3923 | -50.0153 | -49.4705 | -48.1064 | 72.7341 | -50.1709 | -49.6445 | -49.8734 | -50.2213 | -49.9191 | -0.09613 | 0.018311 | -0.29755 | 2.7466 | 0.66833 | 0.1236 | 0.76447 | 0.21973 | -0.032043 | 0.045777 | -122.3328 | 0.2655 | 0.21973 | -0.082397 | 0.25177 | -0.050354 | 2.8427 | 122.6257 | 0.29755 | 0.52643 | 122.9416 | 122.905 | 122.8455 | 122.8729 | -122.9233 | -122.8592 | 122.5296 | 0.49439 | 6.015 | 2.0325
4177.1719 | 122.9874 | -50.1434 | 72.7112 | -0.083466 | -1.9142e-05 | 0.06288 | 0.070968 | 0.001442 | 0.00091009 | 0.0045672 | 0.02002 | 0.0028113 | -0.00042717 | -0.0018628 | 0.00020289 | -0.0072889 | -0.0031787 | -44.1147 | 72.6929 | -50.1801 | 72.3953 | -47.3831 | -50.029 | -49.4614 | -48.1384 | 72.7249 | -50.1755 | -49.6445 | -49.8596 | -50.2213 | -49.9191 | -0.036621 | -0.018311 | -0.31586 | 2.7603 | 0.68207 | 0.11444 | 0.71869 | 0.15106 | -0.032043 | 0.013733 | -122.3557 | 0.28381 | 0.22431 | -0.077819 | 0.25635 | -0.045776 | 2.7969 | 122.5754 | 0.31586 | 0.53101 | 122.8729 | 122.9004 | 122.8363 | 122.8683 | -122.8912 | -122.8867 | 122.5388 | 0.49896 | 6.0287 | 2.005
4178.1719 | 122.937 | -50.1251 | 72.6883 | -0.12924 | 0.00040806 | 0.060744 | 0.069259 | 0.0016556 | 0.00048269 | 0.0069172 | 0.013916 | 0.00067495 | 2.8e-08 | -0.002931 | -0.0038559 | -0.0062207 | -0.00082886 | -44.1147 | 72.7249 | -50.2029 | 72.3907 | -47.3602 | -50.0336 | -49.4659 | -48.1155 | 72.7341 | -50.1617 | -49.6628 | -49.8734 | -50.235 | -49.9374 | -0.07782 | 0.036622 | -0.29755 | 2.7649 | 0.65918 | 0.091553 | 0.737 | 0.16937 | -0.036621 | 0.045777 | -122.3511 | 0.25177 | 0.18768 | -0.10986 | 0.2243 | -0.073242 | 2.8427 | 122.5937 | 0.28839 | 0.49896 | 122.9279 | 122.8958 | 122.85 | 122.8592 | -122.8912 | -122.85 | 122.5159 | 0.46234 | 6.0104 | 2.0096
4179.1719 | 122.9736 | -50.1389 | 72.6883 | -0.068207 | 0.0012625 | 0.061812 | 0.069686 | 0.0055008 | 0.0017645 | 0.0049946 | 0.010864 | 0.00088875 | 0.0032044 | -0.00464 | -0.0034287 | -0.0066479 | -0.00061526 | -44.0872 | 72.702 | -50.1984 | 72.4228 | -47.3328 | -50.0107 | -49.4522 | -48.0927 | 72.7249 | -50.1663 | -49.6353 | -49.8688 | -50.2075 | -49.9054 | -0.059509 | 0.013733 | -0.2655 | 2.8061 | 0.68665 | 0.12817 | 0.74615 | 0.18768 | -0.027466 | 0.036622 | -122.3236 | 0.27008 | 0.23346 | -0.068665 | 0.26093 | -0.041199 | 2.8656 | 122.6212 | 0.29755 | 0.53101 | 122.9004 | 122.8912 | 122.8409 | 122.8638 | -122.8867 | -122.8546 | 122.5616 | 0.50354 | 6.0516 | 2.0462
4180.1719 | 122.9462 | -50.1389 | 72.7112 | -0.0071715 | -1.9142e-05 | 0.062239 | 0.0699 | 0.0029374 | 0.00048269 | 0.0049946 | 0.013916 | 0.0025975 | 0.002777 | -0.00036738 | -0.0038559 | -0.0051527 | 0.0030163 | -44.0918 | 72.7203 | -50.1984 | 72.4091 | -47.3236 | -50.029 | -49.4614 | -48.1064 | 72.7524 | -50.1755 | -49.649 | -49.8688 | -50.2029 | -49.91 | -0.059509 | 0.009155 | -0.30212 | 2.8152 | 0.67749 | 0.10986 | 0.737 | 0.16937 | -0.036621 | 0.041198 | -122.3602 | 0.27008 | 0.22888 | -0.064087 | 0.2655 | -0.027466 | 2.8748 | 122.6074 | 0.3067 | 0.52643 | 122.9187 | 122.9279 | 122.8592 | 122.8912 | -122.9095 | -122.8867 | 122.5479 | 0.48981 | 6.0471 | 2.0325
4181.1719 | 122.9782 | -50.1297 | 72.7295 | -0.068207 | 0.00040806 | 0.062666 | 0.069045 | 0.0029374 | 0.0021917 | 0.00414 | 0.0078126 | 0.0025975 | 0.0025634 | -0.0048536 | -0.00086511 | -0.0079297 | -0.0016833 | -44.0872 | 72.7341 | -50.1801 | 72.4182 | -47.3099 | -50.0381 | -49.4522 | -48.111 | 72.7615 | -50.148 | -49.6399 | -49.8688 | -50.2121 | -49.9191 | -0.050354 | 0.004578 | -0.31128 | 2.8198 | 0.67749 | 0.091553 | 0.72784 | 0.14191 | -0.01831 | 0.032044 | -122.3694 | 0.26093 | 0.21057 | -0.082397 | 0.22888 | -0.064087 | 2.8702 | 122.5983 | 0.27924 | 0.50812 | 122.9141 | 122.9095 | 122.8638 | 122.8912 | -122.9095 | -122.8775 | 122.5479 | 0.48981 | 6.0425 | 2.0187
4182.1719 | 122.9187 | -50.1068 | 72.7936 | -0.045319 | 0.0012625 | 0.062666 | 0.068191 | -0.0049668 | 0.00069649 | 0.0028582 | 0.050537 | 0.0011023 | 0.0023498 | -0.003999 | -0.0019333 | -0.0064343 | -0.0012561 | -44.0872 | 72.7341 | -50.1572 | 72.4045 | -47.2778 | -50.0381 | -49.4339 | -48.0927 | 72.7615 | -50.1572 | -49.649 | -49.855 | -50.2029 | -49.9283 | -0.050354 | -0.059509 | -0.3891 | 2.829 | 0.67291 | 0.068665 | 0.72327 | 0.11902 | -0.050354 | -0.032043 | -122.4426 | 0.25177 | 0.17853 | -0.09613 | 0.22888 | -0.045776 | 2.8793 | 122.5616 | 0.30212 | 0.50812 | 122.8912 | 122.9187 | 122.8409 | 122.8683 | -122.9507 | -122.9507 | 122.5113 | 0.45776 | 6.0196 | 2.0142
4183.1719 | 122.9324 | -50.1205 | 72.7524 | -0.037689 | 0.00019446 | 0.063948 | 0.068404 | 0.00037377 | 0.0013373 | 0.0034992 | 0.023071 | 0.0028113 | 0.0014954 | -0.0048536 | -0.0019333 | -0.0062207 | 0.00023934 | -44.046 | 72.7249 | -50.1755 | 72.4365 | -47.2458 | -49.9969 | -49.4064 | -48.0743 | 72.7707 | -50.1297 | -49.6582 | -49.8596 | -50.1984 | -49.9237 | -0.054932 | -0.027465 | -0.31586 | 2.8748 | 0.71411 | 0.1236 | 0.76904 | 0.17853 | -0.009156 | 0.018311 | -122.4106 | 0.26093 | 0.19684 | -0.07782 | 0.20599 | -0.068664 | 2.9297 | 122.612 | 0.27008 | 0.4715 | 122.9004 | 122.9004 | 122.8455 | 122.8912 | -122.9279 | -122.8821 | 122.5571 | 0.46234 | 6.0745 | 2.0462
4184.1719 | 122.9416 | -50.1068 | 72.7295 | -0.10635 | 0.0016899 | 0.062025 | 0.071609 | 0.0033646 | 0.00048269 | 0.0034992 | 0.001709 | 0.0038793 | 0.001709 | 0.0017688 | -0.0021469 | -0.0068615 | -0.00040166 | -44.0689 | 72.7478 | -50.1846 | 72.4136 | -47.2595 | -50.0061 | -49.4476 | -48.0881 | 72.7615 | -50.1572 | -49.6307 | -49.8596 | -50.1984 | -49.9008 | -0.077819 | 0.018311 | -0.31586 | 2.8473 | 0.65918 | 0.10071 | 0.737 | 0.17853 | -0.050354 | 0.032044 | -122.3602 | 0.24719 | 0.20599 | -0.091552 | 0.25635 | -0.041198 | 2.9251 | 122.5983 | 0.29755 | 0.52643 | 122.9324 | 122.9187 | 122.8546 | 122.8683 | -122.9141 | -122.8867 | 122.5204 | 0.47607 | 6.0379 | 2.0187
4185.1719 | 122.9279 | -50.1068 | 72.7432 | -0.045319 | 0.00019446 | 0.063734 | 0.068832 | -0.0021896 | 0.0015509 | 0.0026446 | 0.044434 | 0.0011023 | 0.00042723 | -0.00229 | -0.0044967 | -0.0079297 | -0.0014697 | -44.0598 | 72.7432 | -50.1434 | 72.4365 | -47.2137 | -49.9878 | -49.4293 | -48.0789 | 72.7844 | -50.148 | -49.6445 | -49.8734 | -50.1801 | -49.9054 | -0.036621 | 0 | -0.3067 | 2.8931 | 0.67749 | 0.11902 | 0.71411 | 0.15564 | -0.041198 | 0.041199 | -122.3877 | 0.23346 | 0.20142 | -0.073242 | 0.24261 | -0.032044 | 2.9297 | 122.58 | 0.27466 | 0.50354 | 122.8867 | 122.9324 | 122.85 | 122.8912 | -122.8867 | -122.8912 | 122.5433 | 0.46234 | 6.0471 | 2.0279
4186.1719 | 122.937 | -50.1068 | 72.7295 | -0.037689 | 0.00083526 | 0.060744 | 0.069472 | -0.003685 | 0.00069649 | 0.0032856 | 0.013916 | 0.0011023 | 0.001068 | -0.00015378 | -0.0032151 | -0.0064343 | -0.0033923 | -44.0598 | 72.7844 | -50.1709 | 72.4503 | -47.3236 | -50.1526 | -49.4156 | -48.1155 | 72.7982 | -50.1343 | -49.6216 | -49.8596 | -50.1984 | -49.9146 | -0.064086 | 0.054932 | -0.27924 | 2.7832 | 0.69122 | -0.045776 | 0.75531 | 0.01831 | -0.027465 | 0.068665 | -122.3511 | 0.24719 | 0.19226 | -0.091552 | 0.21973 | -0.064087 | 2.8473 | 122.6212 | 0.27466 | 0.5127 | 122.9553 | 122.9324 | 122.8912 | 122.905 | -122.9004 | -122.8638 | 122.5571 | 0.48523 | 6.0471 | 1.9913
4187.1719 | 122.9279 | -50.1343 | 72.6929 | -0.037689 | 0.0016899 | 0.064375 | 0.071395 | -0.00026703 | -0.0012261 | 0.0073444 | -0.056274 | 0.0028113 | 0.001068 | 0.0024096 | -0.0030013 | -0.0051527 | 0.0015209 | -44.0689 | 72.7249 | -50.1938 | 72.3862 | -47.2641 | -50.0748 | -49.4888 | -48.1247 | 72.7707 | -50.1663 | -49.6674 | -49.9329 | -50.2991 | -49.9466 | -0.05951 | 0.032044 | -0.3067 | 2.8702 | 0.64545 | 0.059509 | 0.70496 | 0.11902 | -0.032044 | 0.07782 | -122.3602 | 0.20142 | 0.18768 | -0.1648 | 0.21973 | -0.13275 | 2.9297 | 122.58 | 0.23346 | 0.49896 | 122.9187 | 122.937 | 122.8592 | 122.905 | -122.8867 | -122.8592 | 122.5204 | 0.46692 | 6.0654 | 2.0096
4188.1719 | 122.9736 | -50.0519 | 72.789 | -0.022431 | -0.0013009 | 0.062453 | 0.068191 | 0.00037377 | 0.0026191 | 0.005849 | 0.026123 | 0.0023839 | 0.0019226 | -0.0054944 | -0.0015061 | -0.0085705 | 0.00023934 | -44.0552 | 72.7615 | -50.1572 | 72.4503 | -47.1542 | -50.0015 | -49.4156 | -48.0743 | 72.8027 | -50.1343 | -49.6307 | -49.8459 | -50.1801 | -49.942 | -0.10529 | -0.027465 | -0.33875 | 2.8976 | 0.63629 | 0.050354 | 0.74158 | 0.15564 | -0.082397 | 0.013733 | -122.4197 | 0.20599 | 0.10986 | -0.12817 | 0.19226 | -0.045777 | 3.0029 | 122.6074 | 0.28839 | 0.50354 | 122.9187 | 122.937 | 122.8134 | 122.8546 | -122.9462 | -122.9233 | 122.5021 | 0.42114 | 5.9967 | 1.9775
4189.1719 | 122.9965 | -50.0748 | 72.7478 | -0.075836 | 0.00083526 | 0.063094 | 0.068618 | 0.0018692 | 0.00048269 | 0.0060626 | 0.053589 | -0.0014613 | 0.001709 | -0.0059216 | -0.0012925 | -0.0087843 | 0.0030163 | -43.9728 | 72.7295 | -50.1205 | 72.5327 | -47.0306 | -49.8871 | -49.3149 | -47.9553 | 72.757 | -50.1205 | -49.5529 | -49.7772 | -50.1068 | -49.823 | -0.045776 | -0.018311 | -0.21515 | 3.0441 | 0.75989 | 0.18768 | 0.80566 | 0.23346 | -0.045776 | 0.009155 | -122.3007 | 0.29755 | 0.25177 | -0.032044 | 0.29755 | 0.013732 | 3.0899 | 122.6532 | 0.34332 | 0.56763 | 122.85 | 122.8775 | 122.8043 | 122.8317 | -122.8683 | -122.8683 | 122.6074 | 0.52185 | 6.102 | 2.1194
4190.1719 | 123.0148 | -50.0381 | 72.7341 | -0.068207 | 0.0021171 | 0.062239 | 0.068404 | 0.00037377 | 0.0013373 | 0.0032856 | 0.053589 | 0.0011023 | 0.00021363 | -0.0010084 | -0.0012925 | -0.0060071 | 0.0017345 | -43.9453 | 72.7112 | -50.1114 | 72.5464 | -47.0123 | -49.8642 | -49.3103 | -47.937 | 72.7661 | -50.116 | -49.5209 | -49.7269 | -50.0748 | -49.823 | -0.073242 | -0.022888 | -0.18768 | 3.0258 | 0.72784 | 0.17395 | 0.80109 | 0.24719 | -0.07782 | 0.032043 | -122.2549 | 0.31128 | 0.21515 | -0.036621 | 0.29297 | 0.041199 | 3.0991 | 122.6578 | 0.3891 | 0.59509 | 122.8226 | 122.8821 | 122.7493 | 122.8043 | -122.8455 | -122.85 | 122.5845 | 0.51727 | 6.0928 | 2.1011
4191.1719 | 122.9645 | -50.0565 | 72.7753 | -0.060578 | 0.00083526 | 0.063521 | 0.068404 | -5.343e-05 | -0.00015811 | 0.0011494 | 0.029175 | 0.0019567 | 0.00021363 | -0.0027174 | -0.0027877 | -0.0081433 | 0.0051525 | -43.9728 | 72.7478 | -50.0977 | 72.5189 | -47.0306 | -49.91 | -49.3423 | -47.9919 | 72.789 | -50.0885 | -49.5667 | -49.791 | -50.1205 | -49.8596 | -0.041198 | -0.027466 | -0.25635 | 3.0258 | 0.71411 | 0.14648 | 0.75531 | 0.18768 | -0.032043 | 0.013732 | -122.3419 | 0.2655 | 0.19684 | -0.064086 | 0.22888 | -0.032043 | 3.067 | 122.6166 | 0.29755 | 0.52185 | 122.8455 | 122.8775 | 122.8043 | 122.8455 | -122.8729 | -122.8638 | 122.5754 | 0.48981 | 6.0837 | 2.0645
4192.1719 | 123.0331 | -50.0565 | 72.6883 | -0.12924 | 0.0014761 | 0.064375 | 0.070968 | 0.0010148 | 0.0021917 | 0.0060626 | -0.041016 | 0.0015295 | 0.0012818 | 0.00048702 | -0.0047103 | -0.0070753 | -0.0036059 | -44.0186 | 72.7249 | -50.1434 | 72.5235 | -47.0352 | -49.9741 | -49.3744 | -47.9599 | 72.7295 | -50.116 | -49.5071 | -49.7635 | -50.1068 | -49.791 | -0.086975 | 0.036622 | -0.16479 | 3.0212 | 0.68207 | 0.082398 | 0.76904 | 0.16937 | -0.059509 | 0.041199 | -122.1954 | 0.29297 | 0.2655 | -0.050354 | 0.32501 | 0.009155 | 3.1082 | 122.6669 | 0.35248 | 0.60883 | 122.8683 | 122.8455 | 122.7814 | 122.7859 | -122.8317 | -122.8043 | 122.58 | 0.54932 | 6.0379 | 2.0966
4193.1719 | 122.9233 | -50.0519 | 72.7936 | -0.13687 | -0.00066014 | 0.062666 | 0.069686 | -0.00048063 | 0.00026909 | 0.0047808 | 0.02002 | 0.00024775 | 0.001709 | -0.00464 | -0.0034287 | -0.0079297 | -0.0016833 | -43.9957 | 72.8119 | -50.1343 | 72.4731 | -47.0535 | -49.9466 | -49.3698 | -48.0148 | 72.8119 | -50.0748 | -49.5804 | -49.8093 | -50.1526 | -49.8734 | -0.082397 | 0.018311 | -0.32043 | 2.9984 | 0.68207 | 0.10529 | 0.76446 | 0.18768 | -0.022888 | 0.018311 | -122.374 | 0.24261 | 0.17853 | -0.10071 | 0.20142 | -0.07782 | 3.0807 | 122.6074 | 0.2655 | 0.49439 | 122.9462 | 122.8867 | 122.8638 | 122.8638 | -122.9279 | -122.8683 | 122.525 | 0.4715 | 6.0562 | 2.037
4194.1719 | 122.9416 | -50.0565 | 72.8027 | -0.083466 | -0.0017281 | 0.063948 | 0.068404 | -0.0028304 | 0.0036871 | 0.0020038 | 0.02002 | 0.0028113 | 0.00085443 | 0.0041186 | -0.0017197 | -0.0072889 | -0.00040166 | -43.9682 | 72.7753 | -50.1068 | 72.496 | -47.0215 | -49.9329 | -49.3423 | -48.0103 | 72.8165 | -50.0839 | -49.5712 | -49.8184 | -50.1434 | -49.8688 | -0.050354 | -0.027465 | -0.3067 | 3.035 | 0.71411 | 0.1236 | 0.76447 | 0.17395 | -0.027465 | 0.013733 | -122.374 | 0.23804 | 0.18768 | -0.086975 | 0.21515 | -0.05951 | 3.0853 | 122.6028 | 0.2655 | 0.5127 | 122.8821 | 122.9004 | 122.8317 | 122.8729 | -122.9095 | -122.8867 | 122.5525 | 0.48523 | 6.0883 | 2.0462
4195.1719 | 122.9187 | -50.0565 | 72.789 | -0.068207 | 0.00083526 | 0.062025 | 0.070113 | 0.0022964 | 0.0030463 | 0.0039264 | 0.001709 | -0.00039305 | 0.0012818 | -0.002931 | -0.0021469 | -0.0081433 | 0.0010937 | -43.9499 | 72.7936 | -50.1068 | 72.5143 | -46.9803 | -49.91 | -49.3378 | -47.9782 | 72.8027 | -50.0977 | -49.5621 | -49.8138 | -50.148 | -49.8642 | -0.050354 | 0.004578 | -0.27466 | 3.0762 | 0.71869 | 0.14648 | 0.76904 | 0.19684 | -0.041198 | 0.013733 | -122.3511 | 0.24262 | 0.19226 | -0.091552 | 0.23346 | -0.050354 | 3.1265 | 122.6212 | 0.28381 | 0.53558 | 122.9004 | 122.9004 | 122.85 | 122.8592 | -122.8958 | -122.8867 | 122.5708 | 0.49439 | 6.1066 | 2.0782
4196.1719 | 123.0011 | -50.0336 | 72.7524 | -0.075836 | 0.00019446 | 0.062666 | 0.068832 | 0.0016556 | 0.00026909 | 0.003072 | 0.016968 | -0.00039305 | 2.8e-08 | -0.0065626 | -0.0038559 | -0.0051527 | 0.0010937 | -43.9087 | 72.7295 | -50.0656 | 72.6013 | -46.8842 | -49.8505 | -49.2828 | -47.8683 | 72.8073 | -50.0565 | -49.4659 | -49.6994 | -50.029 | -49.7589 | -0.032044 | -0.022888 | -0.15106 | 3.1494 | 0.75073 | 0.1831 | 0.78278 | 0.21515 | -0.022889 | 0.054932 | -122.2183 | 0.33417 | 0.27466 | 0.004577 | 0.29755 | 0.027466 | 3.1815 | 122.6669 | 0.35706 | 0.59052 | 122.7951 | 122.8638 | 122.7631 | 122.8409 | -122.818 | -122.8088 | 122.6349 | 0.56763 | 6.1249 | 2.1652
4197.1719 | 123.0377 | -50.029 | 72.7798 | -0.037689 | -0.0013009 | 0.063734 | 0.068404 | 0.0020828 | 0.0015509 | 0.0056354 | 0.035278 | -0.0012477 | -0.0010682 | 0.0017688 | -0.0025741 | -0.0079297 | -0.00082886 | -43.9636 | 72.7707 | -50.0885 | 72.6105 | -46.8521 | -49.8413 | -49.2508 | -47.8867 | 72.8027 | -50.0336 | -49.4568 | -49.6857 | -50.029 | -49.7498 | -0.059509 | -0.009155 | -0.16937 | 3.1769 | 0.7782 | 0.18768 | 0.83771 | 0.24719 | -0.004577 | 0.022888 | -122.2366 | 0.34332 | 0.27924 | 0 | 0.28381 | 0.004577 | 3.2364 | 122.699 | 0.3479 | 0.57678 | 122.8592 | 122.8363 | 122.7997 | 122.8317 | -122.8683 | -122.8134 | 122.6395 | 0.57221 | 6.0654 | 2.1423
4198.1719 | 122.9324 | -50.0153 | 72.8256 | -0.10635 | 0.0021171 | 0.062453 | 0.069686 | 0.00016017 | -0.0018671 | 0.0052082 | 0.029175 | 0.00046135 | 0.00021363 | -0.0035718 | -0.0017197 | -0.0070753 | -0.0010425 | -43.9224 | 72.7661 | -50.0839 | 72.583 | -46.8704 | -49.8596 | -49.2691 | -47.905 | 72.821 | -50.0473 | -49.5117 | -49.736 | -50.0793 | -49.8001 | -0.068664 | -0.05951 | -0.24261 | 3.1448 | 0.74616 | 0.15564 | 0.81482 | 0.2243 | -0.032043 | -0.004578 | -122.3373 | 0.27924 | 0.21515 | -0.064087 | 0.24719 | -0.032044 | 3.2135 | 122.6669 | 0.31128 | 0.53558 | 122.85 | 122.8683 | 122.7814 | 122.8363 | -122.9095 | -122.8729 | 122.5983 | 0.50354 | 6.0928 | 2.1103
4199.1719 | 122.9965 | -50.029 | 72.7936 | -0.060578 | 0.00019446 | 0.062239 | 0.068191 | -0.0041122 | 0.0011237 | 0.0039264 | -0.0013428 | -0.00017945 | 0.00064083 | 0.0013416 | -0.0053513 | -0.0081433 | -0.0031787 | -43.9041 | 72.7753 | -50.0656 | 72.6151 | -46.8338 | -49.8367 | -49.2783 | -47.8867 | 72.8439 | -50.0793 | -49.4843 | -49.7269 | -50.0565 | -49.7818 | -0.036621 | -0.01831 | -0.17853 | 3.1952 | 0.75073 | 0.19226 | 0.78735 | 0.22888 | -0.050354 | 0.050354 | -122.2778 | 0.30212 | 0.24719 | -0.027466 | 0.29755 | 0.022888 | 3.2318 | 122.6807 | 0.35248 | 0.59509 | 122.8409 | 122.9233 | 122.8043 | 122.8729 | -122.8592 | -122.8729 | 122.644 | 0.54474 | 6.1249 | 2.1423
4200.1719 | 122.905 | -50.0336 | 72.821 | -0.052948 | 0.0012625 | 0.06288 | 0.069686 | -0.0026168 | 0.00048269 | 0.0047808 | 0.0047608 | 0.0015295 | 0.0021362 | -0.00015378 | -0.00043791 | -0.0081433 | -0.0016833 | -43.9407 | 72.8256 | -50.061 | 72.5372 | -46.8887 | -49.9008 | -49.3561 | -47.9645 | 72.8577 | -50.0748 | -49.5392 | -49.7635 | -50.1114 | -49.8459 | -0.027466 | 0.004578 | -0.28381 | 3.1448 | 0.67749 | 0.13275 | 0.70496 | 0.16022 | -0.041199 | 0.036621 | -122.3602 | 0.27008 | 0.18768 | -0.07782 | 0.22888 | -0.036621 | 3.1723 | 122.5983 | 0.31128 | 0.53558 | 122.8867 | 122.9324 | 122.8592 | 122.8912 | -122.8821 | -122.8958 | 122.5708 | 0.49438 | 6.0928 | 2.0691
4201.1719 | 122.9233 | -50.0107 | 72.8256 | -0.060578 | 0.00062166 | 0.062239 | 0.070113 | 0.0012284 | 0.00069649 | 0.0026446 | 0.001709 | -0.0010339 | 0.0019226 | 0.0024096 | -0.00065151 | -0.0072889 | 0.0010937 | -43.9087 | 72.821 | -50.0839 | 72.5464 | -46.8796 | -49.9283 | -49.3149 | -47.9553 | 72.8622 | -50.0473 | -49.5438 | -49.7543 | -50.1114 | -49.8276 | -0.073242 | -0.004578 | -0.27924 | 3.1311 | 0.6958 | 0.082397 | 0.76904 | 0.15564 | -0.036621 | 0.036621 | -122.3694 | 0.25635 | 0.1831 | -0.10071 | 0.21973 | -0.064087 | 3.2043 | 122.6303 | 0.29297 | 0.50354 | 122.905 | 122.9095 | 122.8317 | 122.8729 | -122.9095 | -122.8729 | 122.5571 | 0.46692 | 6.102 | 2.0554
4202.1719 | 122.9095 | -50.0198 | 72.8485 | -0.098725 | 0.0012625 | 0.062239 | 0.069472 | 0.00058737 | 0.0026191 | 0.0049946 | 0.001709 | -0.00017945 | 0.002777 | -0.0042126 | -0.0015061 | -0.0062207 | 2.554e-05 | -43.9178 | 72.8256 | -50.0473 | 72.5693 | -46.843 | -49.9008 | -49.3103 | -47.937 | 72.8577 | -50.0473 | -49.5209 | -49.7589 | -50.0839 | -49.8413 | -0.027466 | -0.022888 | -0.27924 | 3.1769 | 0.70953 | 0.11902 | 0.737 | 0.14648 | -0.027466 | 0.009155 | -122.3694 | 0.26093 | 0.17853 | -0.064087 | 0.20599 | -0.036621 | 3.2043 | 122.6166 | 0.28839 | 0.52643 | 122.8729 | 122.905 | 122.8455 | 122.8775 | -122.8958 | -122.8958 | 122.5891 | 0.49896 | 6.102 | 2.0828
4203.1719 | 122.9782 | -49.9832 | 72.7982 | -0.060578 | 0.00040806 | 0.064162 | 0.069472 | -0.0045394 | 0.0028327 | 0.0049946 | 0.047485 | -0.00082025 | 0.0021362 | -0.0069898 | -0.0023605 | -0.0081433 | 0.00023934 | -43.8904 | 72.7798 | -50.0519 | 72.6242 | -46.7285 | -49.8047 | -49.2325 | -47.8546 | 72.8714 | -50.0427 | -49.4247 | -49.6719 | -50.0153 | -49.7452 | -0.068665 | -0.018311 | -0.17395 | 3.2547 | 0.75073 | 0.17853 | 0.8194 | 0.24719 | -0.05951 | 0.073242 | -122.2229 | 0.31128 | 0.23804 | -0.032044 | 0.29755 | 0.027466 | 3.3234 | 122.6761 | 0.37079 | 0.61798 | 122.8317 | 122.9141 | 122.7631 | 122.8546 | -122.85 | -122.8409 | 122.6074 | 0.55847 | 6.0928 | 2.1286
4204.1719 | 122.9828 | -49.9741 | 72.8119 | -0.091095 | 0.0021171 | 0.060744 | 0.069259 | -0.00090783 | 0.0013373 | 0.0056354 | 0.023071 | 0.0013159 | 0.001068 | -0.0059216 | -0.0047103 | -0.0060071 | -0.0021107 | -43.8858 | 72.821 | -50.0473 | 72.6288 | -46.7194 | -49.8138 | -49.2416 | -47.8455 | 72.8394 | -50.029 | -49.4339 | -49.6628 | -50.0061 | -49.7452 | -0.073242 | 0.009155 | -0.18311 | 3.2547 | 0.73242 | 0.16022 | 0.80566 | 0.23346 | -0.054932 | 0.027465 | -122.2458 | 0.31128 | 0.22888 | -0.032044 | 0.28381 | 0.022888 | 3.3279 | 122.6761 | 0.36621 | 0.59509 | 122.8683 | 122.8683 | 122.7951 | 122.8134 | -122.8592 | -122.8409 | 122.6028 | 0.54016 | 6.0883 | 2.1286
4205.1719 | 122.9233 | -50.0061 | 72.8394 | -0.060578 | 0.0012625 | 0.063734 | 0.069686 | -0.0015488 | 0.0028327 | 0.0049946 | 0.0078126 | 0.0019567 | 0.0021362 | -0.0052808 | -0.0027877 | -0.0055799 | 0.0030163 | -43.895 | 72.8302 | -50.0336 | 72.5693 | -46.788 | -49.8917 | -49.2874 | -47.9462 | 72.8897 | -50.0336 | -49.5163 | -49.7543 | -50.0793 | -49.8093 | -0.027465 | -0.009155 | -0.27008 | 3.2181 | 0.71869 | 0.11444 | 0.74615 | 0.14191 | -0.027465 | 0.050354 | -122.3557 | 0.25177 | 0.19684 | -0.073242 | 0.2243 | -0.045777 | 3.2455 | 122.6028 | 0.27924 | 0.51727 | 122.8638 | 122.9233 | 122.8363 | 122.8958 | -122.8729 | -122.8729 | 122.5754 | 0.48981 | 6.1111 | 2.0599
4206.1719 | 122.9279 | -50.0061 | 72.876 | -0.037689 | -1.9142e-05 | 0.05818 | 0.070541 | 0.0010148 | 0.0026191 | 0.0047808 | -0.019653 | 0.00067495 | 2.8e-08 | -0.0042126 | -0.0030013 | -0.0087843 | 0.0021619 | -43.7027 | 72.9263 | -50.029 | 72.5281 | -46.8201 | -49.8962 | -49.3378 | -47.9324 | 72.8943 | -50.0336 | -49.498 | -49.7314 | -50.0931 | -49.791 | -0.022888 | 0.050354 | -0.3479 | 3.186 | 0.66833 | 0.10986 | 0.69122 | 0.13275 | -0.027465 | 0.01831 | -122.374 | 0.27466 | 0.21515 | -0.086975 | 0.24261 | -0.05951 | 3.2089 | 122.5571 | 0.30212 | 0.53558 | 122.9553 | 122.9279 | 122.9324 | 122.9004 | -122.905 | -122.9095 | 122.5342 | 0.50812 | 6.3034 | 2.0737
4207.1719 | 122.9324 | -49.9924 | 72.8531 | -0.12161 | -0.00087374 | 0.062453 | 0.071181 | 0.004219 | 0.0013373 | 0.0052082 | -0.019653 | 0.0013159 | 0.003418 | 0.0015552 | -0.00065151 | -0.0064343 | -0.0023243 | -43.9407 | 72.9309 | -50.0427 | 72.5327 | -46.7606 | -49.8779 | -49.3332 | -47.9507 | 72.8989 | -50.0381 | -49.4934 | -49.7177 | -50.0839 | -49.8001 | -0.050354 | 0.07782 | -0.32043 | 3.2318 | 0.65918 | 0.11444 | 0.70953 | 0.16479 | -0.045776 | 0.045777 | -122.3465 | 0.27466 | 0.19226 | -0.091552 | 0.23804 | -0.045776 | 3.2822 | 122.5754 | 0.32044 | 0.54474 | 122.9736 | 122.937 | 122.9233 | 122.8912 | -122.8958 | -122.8912 | 122.525 | 0.49896 | 6.0516 | 2.0416
4208.1719 | 122.9279 | -49.9969 | 72.8348 | -0.1445 | 0.0012625 | 0.060957 | 0.071181 | -0.0017624 | 0.0011237 | 0.0060626 | -0.022705 | 0.0013159 | 0.00021363 | 0.00048702 | -0.0032151 | -0.0053663 | 0.00023934 | -43.8858 | 72.8897 | -50.061 | 72.5555 | -46.7377 | -49.8871 | -49.3149 | -47.937 | 72.9034 | -50.0153 | -49.4888 | -49.7452 | -50.0793 | -49.791 | -0.064087 | 0.054931 | -0.27924 | 3.2593 | 0.68207 | 0.10986 | 0.74615 | 0.17395 | -0.018311 | 0.068664 | -122.3236 | 0.25177 | 0.20599 | -0.082398 | 0.2243 | -0.064087 | 3.3234 | 122.6166 | 0.27008 | 0.52643 | 122.9507 | 122.9187 | 122.8867 | 122.9004 | -122.8958 | -122.85 | 122.5525 | 0.50812 | 6.1111 | 2.0599
4209.1719 | 122.9233 | -49.9695 | 72.8439 | -0.083466 | -0.00087374 | 0.061171 | 0.069686 | -0.00069423 | 0.00069649 | 0.0043536 | -0.01355 | 0.00024775 | 0.001068 | 0.003905 | -0.0021469 | -0.0047253 | -0.0027515 | -43.8995 | 72.8989 | -50.061 | 72.551 | -46.7468 | -49.8825 | -49.3149 | -47.937 | 72.9034 | -50.0244 | -49.498 | -49.736 | -50.0656 | -49.7818 | -0.091553 | 0.054932 | -0.29297 | 3.2227 | 0.6546 | 0.086975 | 0.74615 | 0.17853 | -0.054932 | 0.059509 | -122.3419 | 0.23346 | 0.18768 | -0.096131 | 0.24262 | -0.041199 | 3.3142 | 122.612 | 0.28839 | 0.52643 | 122.9599 | 122.9279 | 122.8683 | 122.8729 | -122.905 | -122.8683 | 122.5204 | 0.4715 | 6.0699 | 2.0325
4210.1719 | 122.8821 | -49.9741 | 72.8851 | -0.075836 | 0.00062166 | 0.063521 | 0.068191 | 0.00080117 | 0.00069649 | 0.0052082 | 0.013916 | 0.0028113 | 0.001709 | -0.00058098 | -0.0012925 | -0.0055799 | -0.0010425 | -43.9041 | 72.876 | -50.0473 | 72.5739 | -46.7056 | -49.8688 | -49.2828 | -47.9233 | 72.908 | -50.029 | -49.379 | -49.585 | -50.1938 | -49.9008 | -0.073242 | -0.009155 | -0.31128 | 3.2684 | 0.69122 | 0.10529 | 0.76447 | 0.17853 | -0.054932 | 0.022888 | -122.2641 | 0.3891 | 0.073242 | -0.21973 | 0.12817 | -0.16479 | 3.3417 | 122.6212 | 0.44403 | 0.65002 | 122.9233 | 122.937 | 122.85 | 122.8821 | -122.9324 | -122.9141 | 122.5479 | 0.59509 | 6.0699 | 2.0508
4211.1719 | 122.9141 | -49.9512 | 72.8897 | -0.091095 | -0.00023294 | 0.063094 | 0.069472 | -0.00069423 | 5.5488e-05 | 0.0034992 | 0.016968 | 0.00067495 | 0.00064083 | -0.00015378 | -0.0023605 | -0.0040845 | -0.00018806 | -43.9087 | 72.8851 | -50.0107 | 72.5601 | -46.6782 | -49.8596 | -49.2966 | -47.9095 | 72.9355 | -50.0198 | -49.5621 | -49.7772 | -50.0153 | -49.7543 | -0.059509 | -0.004577 | -0.32959 | 3.273 | 0.6546 | 0.091553 | 0.71411 | 0.15106 | -0.068664 | 0.045777 | -122.4518 | 0.17395 | 0.19684 | -0.064087 | 0.2655 | 0.004577 | 3.3325 | 122.5708 | 0.24261 | 0.45776 | 122.8958 | 122.9553 | 122.8363 | 122.8867 | -122.9004 | -122.9095 | 122.5113 | 0.3891 | 6.0425 | 2.0416
4212.1719 | 122.9416 | -49.9558 | 72.8806 | -0.060578 | 0.0014761 | 0.061598 | 0.072036 | -0.0015488 | 0.0013373 | 0.0028582 | -0.028809 | -0.00017945 | 0.0021362 | 0.0043322 | -0.0019333 | -0.0053663 | -0.0021107 | -43.8858 | 72.8851 | -50.0244 | 72.5739 | -46.669 | -49.8505 | -49.2966 | -47.9095 | 72.9355 | -50.0061 | -49.4751 | -49.6902 | -50.0519 | -49.7681 | -0.068664 | 0.004578 | -0.3067 | 3.2867 | 0.65918 | 0.10529 | 0.72784 | 0.17395 | -0.050354 | 0.054932 | -122.3557 | 0.2655 | 0.18768 | -0.09613 | 0.23804 | -0.045776 | 3.3554 | 122.5983 | 0.31586 | 0.53101 | 122.9095 | 122.9416 | 122.8409 | 122.8912 | -122.905 | -122.8867 | 122.5296 | 0.48065 | 6.0699 | 2.0462
4213.1719 | 122.9462 | -49.9603 | 72.9126 | -0.091095 | -0.00044654 | 0.064589 | 0.070754 | -0.0030442 | 0.00026909 | 0.0039264 | -0.019653 | 0.0011023 | 0.001068 | 0.0030506 | -0.0023605 | -0.0051527 | -0.00082886 | -43.8858 | 72.8943 | -50.0244 | 72.5647 | -46.6599 | -49.855 | -49.2966 | -47.9004 | 72.8989 | -49.9969 | -49.4522 | -49.6811 | -50.0427 | -49.736 | -0.064087 | -0.018311 | -0.3479 | 3.3005 | 0.66376 | 0.10529 | 0.72784 | 0.16937 | -0.036621 | -0.013733 | -122.3648 | 0.27924 | 0.2243 | -0.082398 | 0.26093 | -0.045777 | 3.3646 | 122.5891 | 0.31586 | 0.54474 | 122.9187 | 122.8958 | 122.8546 | 122.8592 | -122.937 | -122.9095 | 122.525 | 0.50812 | 6.0745 | 2.0599
4214.1719 | 122.9599 | -49.9283 | 72.8577 | -0.083466 | -0.00023294 | 0.063094 | 0.072463 | 0.00080117 | -0.00015811 | 0.0062762 | -0.041016 | 0.0017431 | -0.00042717 | -0.0078442 | -0.0023605 | -0.0045117 | 2.554e-05 | -43.8354 | 72.8989 | -50.0107 | 72.6334 | -46.5912 | -49.8413 | -49.2691 | -47.8455 | 72.9034 | -49.9924 | -49.4293 | -49.6765 | -50.0198 | -49.7086 | -0.082397 | 0.041199 | -0.2243 | 3.3371 | 0.65918 | 0.086975 | 0.74158 | 0.16937 | -0.064087 | 0.045776 | -122.287 | 0.25177 | 0.21973 | -0.091552 | 0.28381 | -0.027465 | 3.4195 | 122.644 | 0.31586 | 0.56305 | 122.9095 | 122.8958 | 122.8271 | 122.8317 | -122.8683 | -122.85 | 122.5616 | 0.49896 | 6.0928 | 2.0828
4215.1719 | 122.9645 | -49.9329 | 72.8531 | -0.0071715 | 0.00083526 | 0.063521 | 0.0699 | -0.00069423 | -0.00015811 | 0.0047808 | -0.019653 | 0.0019567 | 0.001709 | -0.001222 | -0.0012925 | -0.0072889 | -0.0010425 | -43.8354 | 72.9172 | -50.0244 | 72.6059 | -46.5546 | -49.8367 | -49.2325 | -47.8638 | 72.9172 | -49.9832 | -49.4202 | -49.6719 | -50.0198 | -49.7177 | -0.091553 | 0.064087 | -0.24719 | 3.3783 | 0.70038 | 0.09613 | 0.79193 | 0.18768 | -0.050354 | 0.064087 | -122.2733 | 0.26093 | 0.21515 | -0.086975 | 0.2655 | -0.036621 | 3.4698 | 122.6303 | 0.31128 | 0.56305 | 122.9416 | 122.9004 | 122.85 | 122.85 | -122.8775 | -122.8363 | 122.5388 | 0.5127 | 6.0974 | 2.0691
4216.1719 | 122.9782 | -49.9558 | 72.8577 | -0.060578 | 0.0019035 | 0.063094 | 0.070113 | -0.00026703 | 0.0053961 | 0.0062762 | -0.050171 | 0.0023839 | 0.001068 | 0.001128 | -0.0023605 | -0.0060071 | 0.0034435 | -43.8492 | 72.8668 | -50.0381 | 72.6059 | -46.5546 | -49.8367 | -49.2783 | -47.8683 | 72.8714 | -49.9741 | -49.4568 | -49.6857 | -50.0519 | -49.7269 | -0.082397 | 0.009155 | -0.25177 | 3.4012 | 0.67749 | 0.11902 | 0.75989 | 0.20142 | -0.01831 | 0.013733 | -122.3145 | 0.27008 | 0.22888 | -0.09613 | 0.24719 | -0.07782 | 3.4836 | 122.644 | 0.28839 | 0.51727 | 122.905 | 122.8455 | 122.8226 | 122.8271 | -122.8958 | -122.8317 | 122.5616 | 0.49896 | 6.1066 | 2.0874
4217.1719 | 122.9553 | -49.942 | 72.9126 | -0.037689 | -0.0019417 | 0.064162 | 0.0699 | 0.001442 | 0.00091009 | 0.001363 | -0.0074462 | 0.0017431 | 0.0021362 | 0.0028368 | -0.0019333 | -0.0053663 | -0.0016833 | -43.8492 | 72.9034 | -50.0107 | 72.5876 | -46.5775 | -49.8459 | -49.2783 | -47.8729 | 72.9309 | -49.9832 | -49.4476 | -49.6857 | -50.0153 | -49.7269 | -0.068664 | -0.009156 | -0.32501 | 3.3646 | 0.66376 | 0.096131 | 0.73242 | 0.16479 | -0.041198 | 0.01831 | -122.3602 | 0.25635 | 0.21515 | -0.073242 | 0.25635 | -0.032044 | 3.4332 | 122.5983 | 0.29755 | 0.53558 | 122.9141 | 122.9141 | 122.8455 | 122.8729 | -122.9233 | -122.8958 | 122.5296 | 0.49439 | 6.0928 | 2.0691
4218.1719 | 122.9736 | -49.9466 | 72.8897 | -0.075836 | -0.0019417 | 0.063521 | 0.068404 | -0.0013352 | -0.00058531 | 0.0049946 | 0.013916 | 0.00067495 | -0.00021357 | 0.00091422 | -0.0015061 | -0.0075025 | -0.0021107 | -43.8492 | 72.9034 | -50.0244 | 72.5739 | -46.5454 | -49.8367 | -49.2691 | -47.8912 | 72.9446 | -49.9786 | -49.4431 | -49.6628 | -50.0153 | -49.736 | -0.07782 | 0.013733 | -0.31586 | 3.4012 | 0.67749 | 0.10986 | 0.75531 | 0.18768 | -0.032044 | 0.054932 | -122.3328 | 0.28381 | 0.21057 | -0.068665 | 0.24261 | -0.036621 | 3.479 | 122.5983 | 0.31586 | 0.53558 | 122.9279 | 122.9233 | 122.85 | 122.8912 | -122.9141 | -122.8683 | 122.5204 | 0.50354 | 6.0974 | 2.0554
4219.1719 | 122.9645 | -49.9374 | 72.8851 | -0.075836 | -0.0017281 | 0.06288 | 0.070327 | 0.0046464 | 0.0024053 | 0.0045672 | -0.0013428 | -0.00039305 | 0.0021362 | -0.00036738 | -0.0030013 | -0.0053663 | -0.0018971 | -43.8171 | 72.908 | -50.0198 | 72.6288 | -46.4905 | -49.8001 | -49.2416 | -47.8317 | 72.9401 | -49.9741 | -49.4064 | -49.6674 | -50.0061 | -49.7131 | -0.082397 | 0.022888 | -0.25635 | 3.447 | 0.6958 | 0.13733 | 0.7782 | 0.21973 | -0.036621 | 0.054931 | -122.2916 | 0.27008 | 0.2243 | -0.068665 | 0.26093 | -0.032044 | 3.5294 | 122.6486 | 0.3067 | 0.56763 | 122.9279 | 122.9141 | 122.8455 | 122.8775 | -122.905 | -122.8592 | 122.5662 | 0.53101 | 6.1203 | 2.1057
4220.1719 | 122.9416 | -49.91 | 72.8943 | -0.075836 | 0.0025443 | 0.06523 | 0.069686 | 0.0022964 | 0.0030463 | 0.0056354 | -0.047119 | 0.0017431 | 0.0019226 | 0.0013416 | -0.0030013 | -0.0047253 | 0.0030163 | -43.8171 | 72.8989 | -49.9878 | 72.6471 | -46.4127 | -49.7955 | -49.2371 | -47.8088 | 72.9309 | -49.9695 | -49.4064 | -49.6719 | -50.0107 | -49.7131 | -0.07782 | 0.004578 | -0.24719 | 3.4973 | 0.67291 | 0.11444 | 0.75073 | 0.19226 | -0.059509 | 0.036621 | -122.3007 | 0.23804 | 0.19684 | -0.10071 | 0.25635 | -0.041199 | 3.5751 | 122.6349 | 0.29755 | 0.56305 | 122.8867 | 122.9004 | 122.8088 | 122.8409 | -122.8821 | -122.8638 | 122.5571 | 0.50354 | 6.0928 | 2.1011
4221.1719 | 122.9645 | -49.9283 | 72.8943 | -0.052948 | 0.00062166 | 0.063521 | 0.070327 | 0.00016017 | 0.00069649 | 0.0032856 | -0.028809 | 0.0017431 | 0.0025634 | 0.001128 | -0.0023605 | -0.0049389 | 0.00088014 | -43.808 | 72.9034 | -49.9695 | 72.5601 | -46.4767 | -49.6994 | -49.2096 | -47.7997 | 72.9538 | -49.9237 | -49.3881 | -49.6719 | -50.029 | -49.6902 | -0.041198 | 0.009155 | -0.33417 | 3.4515 | 0.71869 | 0.22888 | 0.75989 | 0.27008 | 0.004578 | 0.059509 | -122.2824 | 0.25635 | 0.23804 | -0.10071 | 0.23346 | -0.10529 | 3.4927 | 122.5296 | 0.25177 | 0.53558 | 122.8729 | 122.8775 | 122.8317 | 122.8821 | -122.8638 | -122.818 | 122.4884 | 0.54016 | 6.1203 | 2.1286
4222.1719 | 122.9645 | -49.9329 | 72.8851 | -0.091095 | -0.0010873 | 0.062025 | 0.070968 | -5.343e-05 | 0.0045417 | 0.0054218 | 0.0047608 | 0.00024775 | 0.00085443 | 0.00048702 | -0.0025741 | -0.0042981 | 0.0028027 | -43.8171 | 72.9218 | -49.9924 | 72.6379 | -46.4859 | -49.8871 | -49.2325 | -47.7997 | 72.963 | -49.9558 | -49.3927 | -49.6719 | -49.9924 | -49.6902 | -0.05951 | 0.036621 | -0.24719 | 3.447 | 0.70038 | 0.045776 | 0.75989 | 0.10529 | -0.022889 | 0.07782 | -122.2778 | 0.26093 | 0.24261 | -0.05951 | 0.2655 | -0.036621 | 3.5065 | 122.6303 | 0.28381 | 0.56305 | 122.9141 | 122.9187 | 122.8546 | 122.8958 | -122.8775 | -122.8409 | 122.5708 | 0.54016 | 6.1157 | 2.1332
4223.1719 | 122.9965 | -49.9237 | 72.9126 | -0.068207 | 0.0029715 | 0.064589 | 0.070754 | 0.00016017 | 0.0034735 | 0.0034992 | 0.053589 | 0.0025975 | 0.002777 | 0.00091422 | -0.0021469 | -0.0053663 | 0.00045294 | -43.7988 | 72.9309 | -49.9741 | 72.6379 | -46.376 | -49.9374 | -49.2416 | -47.7676 | 72.9584 | -49.9237 | -49.3881 | -49.6582 | -49.9924 | -49.6857 | -0.050354 | 0.01831 | -0.27466 | 3.5477 | 0.68207 | -0.013733 | 0.73242 | 0.036621 | 0 | 0.045776 | -122.3007 | 0.2655 | 0.23804 | -0.068665 | 0.23804 | -0.068665 | 3.598 | 122.612 | 0.2655 | 0.53558 | 122.905 | 122.8821 | 122.8546 | 122.8821 | -122.8867 | -122.8363 | 122.5616 | 0.53558 | 6.1249 | 2.1561
4224.1719 | 122.9691 | -49.8825 | 72.9218 | -0.083466 | -0.00023294 | 0.063734 | 0.071395 | -0.0013352 | 0.0024053 | 0.00414 | 0.010864 | 0.0019567 | 0.0021362 | -0.00015378 | -0.0010787 | -0.0064343 | 0.0030163 | -43.7851 | 72.9355 | -49.9649 | 72.6517 | -46.3715 | -49.7772 | -49.2188 | -47.8043 | 72.9401 | -49.9374 | -49.3881 | -49.649 | -49.9695 | -49.6719 | -0.082398 | 0.013733 | -0.27008 | 3.511 | 0.66376 | 0.10528 | 0.74616 | 0.18768 | -0.054932 | 0.01831 | -122.3099 | 0.23346 | 0.21057 | -0.086975 | 0.2655 | -0.032043 | 3.5934 | 122.6166 | 0.28839 | 0.54932 | 122.9004 | 122.8775 | 122.818 | 122.8226 | -122.8867 | -122.8592 | 122.5342 | 0.49438 | 6.0974 | 2.0782
4225.1719 | 122.9691 | -49.942 | 72.9172 | -0.052948 | 0.0012625 | 0.064589 | 0.069045 | -0.0015488 | 0.00091009 | 0.0049946 | 0.001709 | 0.0013159 | 0.0025634 | 0.0015552 | -0.0019333 | -0.0049389 | -0.0014697 | -43.8034 | 72.9401 | -49.9786 | 72.6562 | -46.3715 | -49.7726 | -49.2188 | -47.8134 | 72.9401 | -49.9558 | -49.3744 | -49.6353 | -49.9832 | -49.6902 | -0.036621 | 0.022888 | -0.26093 | 3.5706 | 0.72327 | 0.16937 | 0.75989 | 0.20599 | -0.013733 | 0.022888 | -122.2916 | 0.3067 | 0.25177 | -0.041198 | 0.2655 | -0.027465 | 3.6072 | 122.6349 | 0.32044 | 0.58136 | 122.9187 | 122.8958 | 122.8821 | 122.8821 | -122.8958 | -122.8729 | 122.5983 | 0.56763 | 6.1386 | 2.1286
4226.1719 | 122.9874 | -49.8917 | 72.9218 | -0.10635 | -0.0015145 | 0.064375 | 0.070754 | 0.00251 | 0.00069649 | 0.0034992 | 0.001709 | -0.00039305 | 0.00042723 | 0.00070062 | -0.0030013 | -0.0072889 | 2.554e-05 | -43.8034 | 72.8989 | -49.9603 | 72.67 | -46.3165 | -49.7955 | -49.2096 | -47.7539 | 72.9309 | -49.9374 | -49.3607 | -49.6445 | -49.9969 | -49.6582 | -0.068664 | -0.022888 | -0.25177 | 3.5751 | 0.68207 | 0.096131 | 0.75073 | 0.16479 | -0.045776 | 0.009155 | -122.2824 | 0.24719 | 0.23346 | -0.10529 | 0.27924 | -0.059509 | 3.6438 | 122.6303 | 0.29297 | 0.57678 | 122.8592 | 122.8683 | 122.7905 | 122.8226 | -122.8821 | -122.8592 | 122.5616 | 0.53101 | 6.0883 | 2.1378
4227.1719 | 122.8775 | -49.9146 | 72.9446 | -0.10635 | -0.00023294 | 0.064162 | 0.070968 | 0.0022964 | 0.0019781 | 0.0060626 | -0.016602 | 0.0019567 | 0.0042724 | -0.002931 | -0.0017197 | -0.0062207 | -0.0023243 | -43.7988 | 72.9355 | -49.9695 | 72.6196 | -46.3715 | -49.8505 | -49.2645 | -47.8729 | 72.963 | -49.9512 | -49.4431 | -49.7131 | -50.0473 | -49.7269 | -0.054931 | -0.009155 | -0.32501 | 3.5431 | 0.65003 | 0.064087 | 0.70496 | 0.11902 | -0.036621 | 0.018311 | -122.3877 | 0.20142 | 0.18768 | -0.13275 | 0.2243 | -0.09613 | 3.598 | 122.5891 | 0.23804 | 0.50812 | 122.905 | 122.9141 | 122.85 | 122.8775 | -122.9141 | -122.8958 | 122.5342 | 0.4715 | 6.1157 | 2.0416
4228.1719 | 122.9645 | -49.8917 | 72.9309 | -0.10635 | -0.00023294 | 0.060957 | 0.071395 | 0.00058737 | 0.0011237 | 0.0039264 | -0.0074462 | 0.00024775 | 0.0029906 | -0.00229 | -0.0015061 | -0.0062207 | 0.0030163 | -43.7622 | 72.9263 | -49.9374 | 72.6242 | -46.2799 | -49.791 | -49.2004 | -47.7951 | 72.9904 | -49.9329 | -49.4019 | -49.6674 | -49.9924 | -49.6994 | -0.045776 | -0.004577 | -0.3067 | 3.6118 | 0.69122 | 0.10071 | 0.737 | 0.14648 | -0.041198 | 0.059509 | -122.3328 | 0.22431 | 0.19226 | -0.10071 | 0.23346 | -0.05951 | 3.6575 | 122.5616 | 0.2655 | 0.53101 | 122.8638 | 122.9233 | 122.818 | 122.8821 | -122.8683 | -122.8638 | 122.5159 | 0.48981 | 6.1295 | 2.0966
4229.1719 | 122.9507 | -49.8825 | 72.963 | -0.068207 | 0.00019446 | 0.064589 | 0.070327 | 0.005928 | 0.0019781 | 0.0017902 | -0.0074462 | 0.00088875 | 0.0021362 | 0.0036914 | -0.00065151 | -0.0053663 | -0.0018971 | -43.7714 | 72.9538 | -49.9512 | 72.6608 | -46.2616 | -49.7772 | -49.2096 | -47.7676 | 72.963 | -49.9146 | -49.3881 | -49.6353 | -49.9741 | -49.6674 | -0.068665 | -0.009156 | -0.30212 | 3.6209 | 0.67291 | 0.10528 | 0.74158 | 0.17395 | -0.032044 | 0 | -122.3511 | 0.24719 | 0.21515 | -0.091553 | 0.24719 | -0.059509 | 3.6896 | 122.612 | 0.27924 | 0.52643 | 122.905 | 122.8775 | 122.8363 | 122.8455 | -122.9141 | -122.8775 | 122.5433 | 0.49438 | 6.1111 | 2.1149
4230.1719 | 122.9691 | -49.8734 | 72.9492 | -0.045319 | -0.00066014 | 0.063948 | 0.071822 | -0.0021896 | 0.0039007 | 0.0045672 | -0.0074462 | 0.00088875 | 0.0021362 | -0.0048536 | -0.0021469 | -0.0053663 | -0.0016833 | -43.7347 | 72.9675 | -49.9146 | 72.6837 | -46.2158 | -49.7498 | -49.1684 | -47.7722 | 72.9767 | -49.91 | -49.3744 | -49.6353 | -49.9832 | -49.6811 | -0.041199 | 0.01831 | -0.2655 | 3.6575 | 0.70496 | 0.1236 | 0.74616 | 0.1648 | -0.036621 | 0.027466 | -122.3236 | 0.23804 | 0.19226 | -0.10986 | 0.22888 | -0.073242 | 3.6987 | 122.5983 | 0.27466 | 0.53558 | 122.8821 | 122.8867 | 122.8409 | 122.85 | -122.8638 | -122.8592 | 122.5571 | 0.49896 | 6.1386 | 2.1011
4231.1719 | 122.9782 | -49.8734 | 72.9538 | -0.098725 | -0.00044654 | 0.064162 | 0.070754 | 0.00251 | 0.0019781 | 0.0077716 | 0.013916 | 0.0025975 | 0.00042723 | -0.0031446 | -0.0030013 | -0.0072889 | 0.0015209 | -43.7256 | 72.963 | -49.9329 | 72.6746 | -46.2021 | -49.7406 | -49.1821 | -47.7631 | 73.0041 | -49.9054 | -49.3698 | -49.6033 | -49.9558 | -49.6399 | -0.059509 | 0.009156 | -0.27923 | 3.6713 | 0.69122 | 0.13275 | 0.75073 | 0.19226 | -0.032044 | 0.050354 | -122.3236 | 0.27008 | 0.23346 | -0.082398 | 0.2655 | -0.050354 | 3.7308 | 122.6074 | 0.30213 | 0.53558 | 122.8958 | 122.9095 | 122.8363 | 122.8775 | -122.8867 | -122.8592 | 122.5479 | 0.50354 | 6.1478 | 2.1103
4232.1719 | 122.9828 | -49.8734 | 72.9492 | -0.045319 | -0.0010873 | 0.065657 | 0.069472 | -0.004753 | 0.0024053 | 0.0020038 | 0.001709 | 0.0015295 | 0.00064083 | 0.0041186 | -0.0034287 | -0.0077161 | 0.00045294 | -43.7302 | 72.9446 | -49.9329 | 72.6791 | -46.17 | -49.7543 | -49.1821 | -47.7402 | 72.995 | -49.9008 | -49.3561 | -49.5941 | -49.9512 | -49.6307 | -0.059509 | -0.004578 | -0.27008 | 3.7033 | 0.69122 | 0.11902 | 0.75073 | 0.17853 | -0.027466 | 0.045776 | -122.3053 | 0.27924 | 0.24261 | -0.07782 | 0.27008 | -0.050354 | 3.7628 | 122.612 | 0.3067 | 0.54474 | 122.8775 | 122.8958 | 122.818 | 122.8683 | -122.8821 | -122.85 | 122.5525 | 0.51727 | 6.1432 | 2.1332
4233.1719 | 122.9599 | -49.8688 | 72.9538 | -0.022431 | 0.00062166 | 0.06523 | 0.069686 | -0.00069423 | 0.00048269 | 0.0026446 | -0.0013428 | 0.0034521 | 0.00064083 | -0.0014356 | -0.0015061 | -0.0060071 | 0.0047253 | -43.7302 | 72.9813 | -49.9146 | 72.6562 | -46.2387 | -49.7223 | -49.0906 | -47.7448 | 72.9996 | -49.8871 | -49.3332 | -49.6033 | -49.9603 | -49.6582 | -0.045777 | 0.027466 | -0.29755 | 3.6301 | 0.7782 | 0.14648 | 0.82398 | 0.19226 | -0.018311 | 0.045777 | -122.287 | 0.2655 | 0.21057 | -0.091553 | 0.22888 | -0.073242 | 3.6758 | 122.5708 | 0.28381 | 0.55389 | 122.8958 | 122.8867 | 122.85 | 122.8683 | -122.8683 | -122.8409 | 122.525 | 0.53558 | 6.1386 | 2.124
4234.1719 | 122.9095 | -49.9008 | 72.9584 | -0.045319 | -0.00044654 | 0.065871 | 0.071181 | 0.00251 | 0.00048269 | 0.0069172 | -0.010498 | 0.00024775 | 0.0014954 | -0.0054944 | -0.0032151 | -0.0072889 | -0.00082886 | -43.7759 | 72.9584 | -49.9374 | 72.6379 | -46.2112 | -49.8276 | -49.2325 | -47.8638 | 73.0087 | -49.9146 | -49.4064 | -49.6811 | -50.0381 | -49.7086 | -0.036621 | 0 | -0.32044 | 3.6896 | 0.66833 | 0.073242 | 0.70496 | 0.10986 | -0.013733 | 0.050354 | -122.3648 | 0.21973 | 0.19226 | -0.13733 | 0.20599 | -0.1236 | 3.7262 | 122.5754 | 0.23346 | 0.50812 | 122.8958 | 122.9233 | 122.8592 | 122.9095 | -122.8958 | -122.8729 | 122.5388 | 0.49439 | 6.1249 | 2.037
4235.1719 | 122.9279 | -49.8459 | 72.9675 | -0.068207 | 0.0021171 | 0.063094 | 0.070113 | 0.00080117 | 0.00048269 | 0.0067036 | -0.025757 | 0.0015295 | 0.0014954 | 0.0075366 | -0.0012925 | -0.0070753 | 0.0017345 | -43.7073 | 72.963 | -49.91 | 72.6791 | -46.1014 | -49.7772 | -49.1913 | -47.7539 | 72.9904 | -49.9008 | -49.3744 | -49.6445 | -49.9741 | -49.6719 | -0.064087 | -0.004577 | -0.28839 | 3.7445 | 0.6546 | 0.068664 | 0.71869 | 0.13275 | -0.054932 | 0.022888 | -122.3419 | 0.20142 | 0.17395 | -0.12817 | 0.22888 | -0.073242 | 3.8086 | 122.5891 | 0.25635 | 0.52643 | 122.8729 | 122.8912 | 122.8088 | 122.8363 | -122.8775 | -122.8683 | 122.525 | 0.4715 | 6.1386 | 2.092
4236.1719 | 122.9233 | -49.8642 | 72.9446 | -0.052948 | 0.00083526 | 0.064375 | 0.071609 | -0.00026703 | 0.0036871 | 0.0047808 | -0.019653 | 3.4148e-05 | 0.0014954 | -0.00229 | -0.0019333 | -0.0083569 | 0.00088014 | -43.7256 | 72.9675 | -49.91 | 72.6929 | -46.1105 | -49.7589 | -49.1821 | -47.7539 | 72.9858 | -49.91 | -49.3652 | -49.617 | -49.9786 | -49.6765 | -0.045776 | 0.022888 | -0.25177 | 3.7537 | 0.68207 | 0.10529 | 0.72784 | 0.15106 | -0.045776 | 0.041199 | -122.3099 | 0.24719 | 0.18768 | -0.11444 | 0.23346 | -0.068665 | 3.7994 | 122.6028 | 0.29297 | 0.54474 | 122.8775 | 122.8958 | 122.8317 | 122.85 | -122.8546 | -122.8546 | 122.5571 | 0.49896 | 6.1386 | 2.1103
4237.1719 | 122.937 | -49.8138 | 72.9446 | -0.075836 | -0.00087374 | 0.063094 | 0.071181 | -0.00090783 | 0.0026191 | 0.0045672 | -0.0013428 | 0.0013159 | 0.0019226 | -0.0014356 | -0.0036423 | -0.0049389 | -0.00040166 | -43.6935 | 72.9721 | -49.9008 | 72.6974 | -46.0739 | -49.7498 | -49.1409 | -47.731 | 73.0087 | -49.9054 | -49.3515 | -49.617 | -49.9512 | -49.6353 | -0.086975 | 0.027466 | -0.24719 | 3.7399 | 0.67291 | 0.064087 | 0.75989 | 0.15106 | -0.091553 | 0.064087 | -122.2961 | 0.19684 | 0.17853 | -0.13733 | 0.27008 | -0.045776 | 3.8269 | 122.5983 | 0.28839 | 0.5539 | 122.8729 | 122.9141 | 122.7859 | 122.8226 | -122.8455 | -122.85 | 122.5113 | 0.46234 | 6.1203 | 2.0828
4238.1719 | 123.0148 | -49.8276 | 72.9355 | -0.083466 | -0.00044654 | 0.064589 | 0.0699 | -0.0032578 | 0.0011237 | 0.003072 | 0.10242 | 0.0013159 | 0.001709 | -0.0089124 | -0.0015061 | -0.0081433 | 0.0034435 | -43.721 | 72.9721 | -49.8688 | 72.6929 | -46.0648 | -49.704 | -49.0814 | -47.731 | 72.9401 | -49.8779 | -49.3103 | -49.53 | -49.8688 | -49.5987 | -0.041198 | 0.036621 | -0.24262 | 3.7628 | 0.74616 | 0.1236 | 0.78735 | 0.1648 | -0.050354 | 0.004577 | -122.2458 | 0.29755 | 0.22888 | -0.041198 | 0.27924 | 0.009156 | 3.804 | 122.5616 | 0.3479 | 0.56763 | 122.8409 | 122.818 | 122.7997 | 122.7676 | -122.8043 | -122.8134 | 122.5204 | 0.51727 | 6.1066 | 2.0966
4239.1719 | 122.9462 | -49.8413 | 72.9721 | 0.008087 | 0.00019446 | 0.061171 | 0.071609 | 0.0027238 | 0.0043281 | 0.0069172 | -0.019653 | 0.0023839 | 0.0019226 | 0.0062548 | -0.0034287 | -0.0064343 | -0.0027515 | -43.6707 | 72.9904 | -49.9008 | 72.7158 | -46.0098 | -49.7177 | -49.1501 | -47.7036 | 73.0133 | -49.8413 | -49.2966 | -49.5758 | -49.9237 | -49.6033 | -0.059509 | 0.01831 | -0.25635 | 3.8315 | 0.69122 | 0.1236 | 0.75073 | 0.18311 | 0 | 0.041199 | -122.2687 | 0.2655 | 0.23804 | -0.082397 | 0.23804 | -0.082397 | 3.891 | 122.6166 | 0.2655 | 0.54474 | 122.8912 | 122.8546 | 122.8317 | 122.8546 | -122.8729 | -122.8134 | 122.5571 | 0.54474 | 6.1707 | 2.1378
4240.1719 | 122.937 | -49.8367 | 72.963 | -0.098725 | -1.9142e-05 | 0.06288 | 0.070968 | 0.003151 | 0.0032599 | 0.005849 | 0.0047608 | 0.0015295 | 0.0023498 | -0.0048536 | -0.0012925 | -0.0066479 | -0.0042469 | -43.6661 | 72.995 | -49.9146 | 72.7066 | -45.9778 | -49.7177 | -49.1409 | -47.7036 | 73.0179 | -49.8825 | -49.3195 | -49.5529 | -49.91 | -49.5895 | -0.07782 | 0.032043 | -0.25635 | 3.8589 | 0.6958 | 0.11902 | 0.77362 | 0.19684 | -0.045776 | 0.054931 | -122.2824 | 0.28381 | 0.24719 | -0.073242 | 0.29297 | -0.027466 | 3.9368 | 122.6212 | 0.32959 | 0.56305 | 122.9095 | 122.9004 | 122.8317 | 122.8546 | -122.8775 | -122.8455 | 122.5433 | 0.51727 | 6.1707 | 2.1332
4241.1719 | 122.9279 | -49.855 | 72.9904 | -0.068207 | 0.0029715 | 0.06523 | 0.069472 | 0.0012284 | 0.0017645 | 0.0052082 | -0.034912 | 0.0011023 | 0.0025634 | 0.00027342 | -0.0036423 | -0.0053663 | 0.00066654 | -43.7027 | 72.9767 | -49.9146 | 72.6791 | -46.0052 | -49.7681 | -49.1776 | -47.7631 | 73.0453 | -49.8825 | -49.3652 | -49.6307 | -49.9878 | -49.6628 | -0.059509 | -0.013732 | -0.31128 | 3.8498 | 0.67749 | 0.086976 | 0.737 | 0.14649 | -0.027465 | 0.054932 | -122.3557 | 0.2243 | 0.19226 | -0.13275 | 0.21973 | -0.10529 | 3.9093 | 122.5937 | 0.25177 | 0.51727 | 122.8912 | 122.9279 | 122.8317 | 122.9004 | -122.905 | -122.8729 | 122.5342 | 0.48981 | 6.1523 | 2.092
4242.1719 | 122.8363 | -49.8917 | 72.9126 | -0.091095 | 0.0010489 | 0.064162 | 0.074172 | 0.00251 | 0.0043281 | 0.0049946 | -0.037964 | 0.0015295 | 0.0021362 | -0.002931 | -0.0017197 | -0.0066479 | 0.00045294 | -43.7622 | 72.9767 | -49.9191 | 72.6334 | -46.0602 | -49.8322 | -49.2279 | -47.8271 | 73.0133 | -49.91 | -49.3835 | -49.649 | -50.0061 | -49.6445 | -0.027465 | 0.064087 | -0.27924 | 3.8315 | 0.66376 | 0.05951 | 0.69122 | 0.086975 | -0.01831 | 0.10071 | -122.2961 | 0.24262 | 0.24719 | -0.11444 | 0.2655 | -0.096131 | 3.8589 | 122.5525 | 0.26093 | 0.52643 | 122.8958 | 122.9233 | 122.8683 | 122.905 | -122.8317 | -122.8226 | 122.525 | 0.50812 | 6.1295 | 2.0645
4243.1719 | 123.0331 | -49.8184 | 72.9309 | -0.18265 | 0.0021171 | 0.065657 | 0.070113 | 0.0016556 | 0.0015509 | 0.005849 | 0.053589 | 0.00024775 | 0.001709 | -0.0014356 | -0.0012925 | -0.0068615 | -0.0040333 | -43.6844 | 72.9218 | -49.8962 | 72.7478 | -45.8679 | -49.704 | -49.086 | -47.6486 | 72.9675 | -49.8642 | -49.2783 | -49.53 | -49.8734 | -49.5758 | -0.07782 | -0.009155 | -0.1831 | 3.9505 | 0.73242 | 0.11444 | 0.81024 | 0.19226 | -0.045777 | 0.036621 | -122.2092 | 0.28839 | 0.24261 | -0.054932 | 0.28839 | -0.009155 | 4.0283 | 122.644 | 0.33417 | 0.58594 | 122.818 | 122.8317 | 122.7402 | 122.7859 | -122.8271 | -122.7951 | 122.5662 | 0.54016 | 6.134 | 2.1698
4244.1719 | 122.9416 | -49.8413 | 72.9675 | -0.068207 | -0.00087374 | 0.064803 | 0.073531 | -0.00069423 | 5.5488e-05 | 0.0054218 | -0.041016 | -0.00039305 | 0.0014954 | 0.0077502 | -0.0025741 | -0.0042981 | -0.0027515 | -43.6935 | 72.9858 | -49.91 | 72.6974 | -45.9274 | -49.7635 | -49.1684 | -47.7539 | 73.0133 | -49.8871 | -49.3469 | -49.6216 | -49.9786 | -49.6536 | -0.068664 | 0.018311 | -0.27008 | 3.9139 | 0.67291 | 0.07782 | 0.74158 | 0.14648 | -0.045776 | 0.045777 | -122.3145 | 0.21973 | 0.18768 | -0.13733 | 0.23346 | -0.091553 | 3.9825 | 122.6074 | 0.2655 | 0.54016 | 122.8958 | 122.9004 | 122.8271 | 122.8546 | -122.8775 | -122.8546 | 122.5388 | 0.49439 | 6.1478 | 2.0874
4245.1719 | 122.9782 | -49.8001 | 72.9813 | -0.098725 | -1.9142e-05 | 0.064162 | 0.070541 | 0.0050736 | 0.0011237 | 0.00414 | -0.010498 | 3.4148e-05 | 0.003418 | 0.0015552 | -0.0015061 | -0.0060071 | -0.0051013 | -43.6569 | 72.9996 | -49.8734 | 72.6791 | -45.7581 | -49.6811 | -49.1043 | -47.699 | 73.0408 | -49.8596 | -49.2828 | -49.5758 | -49.9008 | -49.6124 | -0.073242 | 0.018311 | -0.30212 | 4.0421 | 0.6958 | 0.11902 | 0.76904 | 0.19226 | -0.059509 | 0.059509 | -122.2641 | 0.2243 | 0.18768 | -0.10071 | 0.24719 | -0.041199 | 4.1153 | 122.5525 | 0.28381 | 0.57678 | 122.8729 | 122.9004 | 122.7997 | 122.8409 | -122.8546 | -122.8409 | 122.4792 | 0.51727 | 6.1432 | 2.1011
4246.1719 | 122.9324 | -49.7955 | 72.9813 | -0.12924 | 0.00040806 | 0.063307 | 0.068832 | 0.00037377 | 0.00069649 | 0.0032856 | 0.010864 | 0.00067495 | 0.0025634 | 0.0013416 | -1.0706e-05 | -0.0081433 | 0.00045294 | -43.6661 | 73.0225 | -49.8734 | 72.7341 | -45.932 | -49.7406 | -49.054 | -47.6669 | 73.0728 | -49.8413 | -49.2828 | -49.5529 | -49.8962 | -49.5941 | -0.07782 | 0.041199 | -0.24719 | 3.8635 | 0.74158 | 0.054931 | 0.8194 | 0.13275 | -0.045777 | 0.091553 | -122.2641 | 0.24262 | 0.20142 | -0.10071 | 0.24719 | -0.054931 | 3.9413 | 122.6074 | 0.28839 | 0.55847 | 122.8958 | 122.9141 | 122.818 | 122.8683 | -122.8546 | -122.8226 | 122.5296 | 0.5127 | 6.1295 | 2.1286
4247.1719 | 122.9416 | -49.8138 | 72.9767 | -0.098725 | 0.00040806 | 0.062239 | 0.070968 | 0.0010148 | 0.0021917 | 0.0069172 | -0.053223 | 0.00088875 | 0.0014954 | -0.00015378 | -0.0027877 | -0.0060071 | -0.0016833 | -43.6615 | 73.0087 | -49.8596 | 72.7203 | -45.8588 | -49.736 | -49.1364 | -47.7127 | 73.0362 | -49.8642 | -49.3332 | -49.5804 | -49.9237 | -49.6216 | -0.045776 | 0.032043 | -0.25635 | 3.9551 | 0.67749 | 0.07782 | 0.72327 | 0.1236 | -0.050354 | 0.059509 | -122.3099 | 0.23346 | 0.19226 | -0.10986 | 0.24262 | -0.059509 | 4.0009 | 122.58 | 0.28381 | 0.53101 | 122.8683 | 122.9004 | 122.8226 | 122.85 | -122.8363 | -122.8409 | 122.5342 | 0.48065 | 6.1523 | 2.1011
4248.1719 | 122.9691 | -49.8001 | 72.9675 | -0.10635 | 0.00019446 | 0.064375 | 0.068832 | -0.0028304 | 0.0015509 | 0.0032856 | 0.087158 | -0.0010339 | 0.0023498 | -0.0067762 | -0.0023605 | -0.0072889 | 0.0036571 | -43.6752 | 72.9675 | -49.8505 | 72.7478 | -45.7809 | -49.6902 | -49.0677 | -47.6852 | 73.0087 | -49.8276 | -49.2691 | -49.5758 | -49.7498 | -49.4843 | -0.050354 | 0 | -0.21973 | 4.0192 | 0.73242 | 0.10986 | 0.78278 | 0.16022 | -0.027466 | 0.041199 | -122.2366 | 0.2243 | 0.31586 | 0.050354 | 0.34332 | 0.07782 | 4.0695 | 122.5983 | 0.25177 | 0.55847 | 122.818 | 122.8363 | 122.7676 | 122.8088 | -122.818 | -122.7951 | 122.5479 | 0.53101 | 6.1249 | 2.1149
4249.1719 | 122.9233 | -49.8184 | 73.027 | -0.060578 | 0.0012625 | 0.066939 | 0.071609 | 0.0035782 | 0.0030463 | 0.007558 | -0.053223 | 0.0013159 | 0.0014954 | 5.9824e-05 | -0.0027877 | -0.0047253 | -0.0016833 | -43.6661 | 73.0316 | -49.91 | 72.702 | -45.8496 | -49.7635 | -49.1501 | -47.7631 | 73.0682 | -49.855 | -49.3378 | -49.6078 | -49.9558 | -49.649 | -0.091553 | 0.004577 | -0.32501 | 3.9688 | 0.66834 | 0.054931 | 0.75989 | 0.14648 | -0.036622 | 0.041198 | -122.3648 | 0.21057 | 0.16937 | -0.13733 | 0.20599 | -0.10071 | 4.0604 | 122.612 | 0.24719 | 0.51727 | 122.9416 | 122.9233 | 122.85 | 122.8867 | -122.937 | -122.8821 | 122.5204 | 0.48065 | 6.1523 | 2.0554
4250.1719 | 122.9187 | -49.8276 | 73.0041 | -0.083466 | 0.0014761 | 0.068434 | 0.072036 | -0.0026168 | 0.0028327 | 0.0047808 | 0.12683 | 0.00067495 | 0.0019226 | 0.0041186 | -0.0021469 | -0.0072889 | -0.0018971 | -43.6981 | 73.0362 | -49.8779 | 72.702 | -45.8542 | -50.1205 | -49.3423 | -47.7127 | 73.0865 | -49.8047 | -49.3057 | -49.6033 | -49.9786 | -49.6399 | -0.050354 | 0.032044 | -0.30212 | 3.9734 | 0.48523 | -0.29297 | 0.53558 | -0.24261 | 0.022889 | 0.082398 | -122.3099 | 0.22431 | 0.18768 | -0.15106 | 0.16479 | -0.17395 | 4.0237 | 122.58 | 0.20142 | 0.49896 | 122.9141 | 122.8912 | 122.8638 | 122.9141 | -122.8821 | -122.8088 | 122.5296 | 0.52185 | 6.1295 | 2.1149
4251.1719 | 122.9462 | -49.8184 | 73.027 | -0.12161 | -0.00044654 | 0.066298 | 0.073318 | 0.0016556 | 0.00048269 | 0.0073444 | -0.037964 | 3.4148e-05 | 0.00042723 | -0.0069898 | -0.0047103 | -0.0053663 | 0.0036571 | -43.6569 | 73.0179 | -49.8917 | 72.7066 | -45.7901 | -49.7543 | -49.1226 | -47.7448 | 73.0728 | -49.8642 | -49.3332 | -49.6033 | -49.9695 | -49.6216 | -0.073243 | -0.009156 | -0.32044 | 4.0283 | 0.6958 | 0.064087 | 0.76904 | 0.13733 | -0.045777 | 0.045776 | -122.3602 | 0.21515 | 0.19684 | -0.15106 | 0.24262 | -0.10529 | 4.1016 | 122.5983 | 0.26093 | 0.53101 | 122.9095 | 122.937 | 122.8363 | 122.8912 | -122.9187 | -122.8912 | 122.525 | 0.48523 | 6.1615 | 2.0737
4252.1719 | 122.9462 | -49.7864 | 72.995 | -0.091095 | 0.0014761 | 0.064589 | 0.068404 | -0.00048063 | 0.0024053 | 0.0067036 | -0.022705 | 0.0015295 | 0.0019226 | 0.00091422 | -0.0023605 | -0.0057935 | 0.0023755 | -43.6157 | 73.0133 | -49.8642 | 72.7203 | -45.7169 | -49.704 | -49.1089 | -47.6807 | 73.0408 | -49.8276 | -49.2874 | -49.5621 | -49.9146 | -49.5987 | -0.07782 | 0.018311 | -0.27466 | 4.0695 | 0.67749 | 0.082398 | 0.75531 | 0.16022 | -0.041199 | 0.045776 | -122.2824 | 0.2243 | 0.18768 | -0.12817 | 0.22888 | -0.086975 | 4.1473 | 122.5845 | 0.2655 | 0.54016 | 122.8775 | 122.8683 | 122.7997 | 122.8271 | -122.8592 | -122.8226 | 122.5067 | 0.49896 | 6.1707 | 2.1057
4253.1719 | 122.937 | -49.8001 | 72.9996 | -0.10635 | 0.0016899 | 0.06523 | 0.071395 | -0.0013352 | 0.0017645 | 0.0056354 | -0.034912 | -0.00039305 | 2.8e-08 | 0.0041186 | -0.0012925 | -0.0079297 | 0.0017345 | -43.602 | 73.0362 | -49.8688 | 72.7524 | -45.6757 | -49.6719 | -49.0952 | -47.6715 | 73.0591 | -49.8367 | -49.2783 | -49.5621 | -49.9008 | -49.5804 | -0.068664 | 0.036621 | -0.24719 | 4.1245 | 0.70496 | 0.12817 | 0.77362 | 0.19684 | -0.036621 | 0.059509 | -122.2778 | 0.23804 | 0.21973 | -0.10071 | 0.25635 | -0.064087 | 4.1931 | 122.6212 | 0.27466 | 0.55847 | 122.905 | 122.8958 | 122.8363 | 122.8592 | -122.8683 | -122.8363 | 122.5525 | 0.52185 | 6.1981 | 2.1286
4254.1719 | 122.9279 | -49.8459 | 73.0041 | -0.060578 | -0.00044654 | 0.06523 | 0.073104 | 0.0029374 | 0.0024053 | 0.0049946 | -0.028809 | 0.0011023 | 0.0014954 | 0.0032642 | -0.00086511 | -0.0066479 | -0.00061526 | -43.6523 | 73.0087 | -49.8917 | 72.7158 | -45.7031 | -49.7269 | -49.1272 | -47.7127 | 73.0682 | -49.8505 | -49.3332 | -49.5804 | -49.9329 | -49.6216 | -0.045777 | 0.004578 | -0.28839 | 4.1428 | 0.71869 | 0.11902 | 0.76447 | 0.16479 | -0.004578 | 0.064087 | -122.3373 | 0.2655 | 0.2243 | -0.086975 | 0.22888 | -0.082397 | 4.1885 | 122.6074 | 0.27008 | 0.51727 | 122.9004 | 122.9187 | 122.8546 | 122.9141 | -122.8958 | -122.8546 | 122.5616 | 0.5127 | 6.1935 | 2.1332
4255.1719 | 122.9004 | -49.823 | 73.0087 | -0.060578 | -0.00023294 | 0.064375 | 0.071181 | -0.0015488 | 0.0019781 | 0.00414 | -0.028809 | 0.0023839 | 0.001068 | -0.0035718 | -0.0015061 | -0.0042981 | -0.0010425 | -43.6615 | 73.0225 | -49.8825 | 72.6746 | -45.7214 | -49.7818 | -49.173 | -47.7905 | 73.0637 | -49.8642 | -49.3515 | -49.6353 | -49.9878 | -49.6445 | -0.059509 | 0.013733 | -0.33417 | 4.1016 | 0.65002 | 0.041199 | 0.70953 | 0.10071 | -0.041199 | 0.054932 | -122.3602 | 0.18768 | 0.17853 | -0.1648 | 0.21973 | -0.1236 | 4.1611 | 122.5571 | 0.22888 | 0.5127 | 122.905 | 122.9279 | 122.8455 | 122.8867 | -122.8912 | -122.8729 | 122.4976 | 0.4715 | 6.1615 | 2.0325
4256.1719 | 122.9004 | -49.8184 | 73.0087 | -0.12924 | 0.00019446 | 0.063094 | 0.072677 | -0.00090783 | 0.0026191 | 0.0060626 | -0.025757 | 0.0028113 | -0.00021357 | 0.0028368 | -0.00043791 | -0.0055799 | 0.0017345 | -43.6478 | 73.0316 | -49.8688 | 72.6837 | -45.6894 | -49.7772 | -49.1592 | -47.7859 | 73.027 | -49.8734 | -49.3469 | -49.6078 | -49.9832 | -49.6353 | -0.050354 | 0.022888 | -0.32501 | 4.129 | 0.65918 | 0.041198 | 0.70953 | 0.091552 | -0.054932 | 0.018311 | -122.3557 | 0.21057 | 0.18311 | -0.16479 | 0.23804 | -0.10986 | 4.1794 | 122.5525 | 0.2655 | 0.52643 | 122.9004 | 122.9004 | 122.85 | 122.8455 | -122.8775 | -122.8821 | 122.5021 | 0.4715 | 6.1707 | 2.0325
4257.1719 | 122.9141 | -49.8276 | 73.0362 | -0.068207 | 0.00062166 | 0.066725 | 0.070754 | -0.0049668 | 0.0024053 | 0.003072 | -0.03186 | 0.0011023 | 0.001068 | 0.00070062 | -0.0012925 | -0.0053663 | 0.00045294 | -43.6386 | 73.0453 | -49.8688 | 72.6974 | -45.6573 | -49.7452 | -49.1455 | -47.7631 | 73.082 | -49.8596 | -49.3378 | -49.6216 | -49.9649 | -49.6307 | -0.041198 | 0.009155 | -0.33874 | 4.1702 | 0.68207 | 0.082398 | 0.72327 | 0.1236 | -0.032043 | 0.045776 | -122.374 | 0.20599 | 0.19684 | -0.13733 | 0.22888 | -0.10529 | 4.2114 | 122.5662 | 0.23804 | 0.52185 | 122.9141 | 122.9416 | 122.8729 | 122.9095 | -122.905 | -122.8958 | 122.525 | 0.48981 | 6.189 | 2.0645
4258.1719 | 122.9324 | -49.8276 | 73.0316 | -0.12161 | 0.00040806 | 0.063734 | 0.072036 | -0.00048063 | 0.0013373 | 0.0028582 | -0.03186 | 0.0015295 | 0.0014954 | -0.0037854 | -0.0034287 | -0.0055799 | -0.0031787 | -43.6752 | 73.0499 | -49.8642 | 72.464 | -45.8496 | -49.379 | -48.9532 | -47.7081 | 73.0682 | -49.8642 | -49.3378 | -49.585 | -49.942 | -49.6262 | -0.036621 | 0.018311 | -0.56763 | 3.978 | 0.87433 | 0.44861 | 0.91095 | 0.48523 | -0.036621 | 0.036621 | -122.3694 | 0.24262 | 0.20142 | -0.11444 | 0.23804 | -0.07782 | 4.0146 | 122.3282 | 0.27924 | 0.52643 | 122.9141 | 122.9324 | 122.8775 | 122.8958 | -122.8958 | -122.8958 | 122.2916 | 0.48981 | 6.1523 | 2.1194
4259.1719 | 122.9507 | -49.7864 | 73.0225 | -0.068207 | -1.9142e-05 | 0.062666 | 0.071822 | -0.00090783 | 0.0013373 | 0.00414 | -0.028809 | 0.0034521 | 0.0040588 | 0.0045458 | -0.0034287 | -0.0062207 | 0.0017345 | -43.5974 | 73.0179 | -49.8505 | 72.7524 | -45.5338 | -49.6765 | -49.0906 | -47.6624 | 73.0591 | -49.8184 | -49.2691 | -49.5483 | -49.8962 | -49.5895 | -0.064087 | -0.004578 | -0.27008 | 4.2526 | 0.6958 | 0.10986 | 0.75989 | 0.17395 | -0.032043 | 0.036621 | -122.2916 | 0.23804 | 0.19684 | -0.10986 | 0.22888 | -0.07782 | 4.3167 | 122.6028 | 0.27008 | 0.54932 | 122.8683 | 122.8775 | 122.8043 | 122.8455 | -122.8729 | -122.8409 | 122.5388 | 0.51727 | 6.189 | 2.124
4260.1719 | 122.9279 | -49.823 | 73.0408 | -0.083466 | 0.00083526 | 0.065016 | 0.069472 | 0.001442 | 0.0019781 | 0.0047808 | -0.0074462 | 0.0025975 | 0.00064083 | -0.0037854 | -0.0027877 | -0.0060071 | 0.0010937 | -43.6066 | 73.0408 | -49.8825 | 72.7249 | -45.5383 | -49.7223 | -49.118 | -47.7081 | 73.0911 | -49.8184 | -49.3195 | -49.5667 | -49.9146 | -49.5987 | -0.059509 | 0 | -0.31586 | 4.2847 | 0.70496 | 0.10071 | 0.76446 | 0.16022 | 0.004578 | 0.050354 | -122.3602 | 0.25635 | 0.2243 | -0.091553 | 0.21973 | -0.096131 | 4.3442 | 122.6074 | 0.25177 | 0.49896 | 122.9233 | 122.9095 | 122.8638 | 122.9141 | -122.9233 | -122.8592 | 122.5479 | 0.50354 | 6.2164 | 2.1149
4261.1719 | 122.9553 | -49.8138 | 73.0133 | -0.052948 | 0.0012625 | 0.064162 | 0.074172 | 0.0022964 | 0.0039007 | 0.0052082 | 0.013916 | 0.0019567 | 0.00064083 | 0.003905 | -1.0706e-05 | -0.0072889 | 0.00088014 | -43.6386 | 73.0499 | -49.8825 | 72.7112 | -45.5383 | -49.7406 | -49.0997 | -47.7219 | 73.0545 | -49.8459 | -49.2874 | -49.5575 | -49.9146 | -49.5895 | -0.068664 | 0.036621 | -0.30212 | 4.2755 | 0.71411 | 0.073242 | 0.78278 | 0.14191 | -0.032043 | 0.041198 | -122.3007 | 0.25635 | 0.2243 | -0.10071 | 0.25635 | -0.068665 | 4.3442 | 122.5937 | 0.28839 | 0.55847 | 122.9324 | 122.9004 | 122.8638 | 122.8683 | -122.8958 | -122.8592 | 122.525 | 0.52643 | 6.1752 | 2.092
4262.1719 | 122.8867 | -49.7955 | 73.0179 | -0.10635 | 0.0029715 | 0.064375 | 0.071822 | -0.00048063 | 0.0032599 | 0.0043536 | -0.037964 | 0.0017431 | 0.00064083 | 0.0013416 | -0.0032151 | -0.0070753 | -0.0021107 | -43.6203 | 73.0362 | -49.8642 | 72.7112 | -45.5429 | -49.7726 | -49.1318 | -47.7768 | 73.0865 | -49.823 | -49.3103 | -49.5758 | -49.942 | -49.5895 | -0.068665 | 0.018311 | -0.3067 | 4.2526 | 0.66376 | 0.022888 | 0.73242 | 0.091553 | -0.027466 | 0.068665 | -122.3282 | 0.21973 | 0.20599 | -0.14648 | 0.23346 | -0.11902 | 4.3213 | 122.5754 | 0.24719 | 0.5127 | 122.9004 | 122.9095 | 122.8317 | 122.8821 | -122.8821 | -122.8409 | 122.5067 | 0.48523 | 6.1752 | 2.0187
4263.1719 | 122.8958 | -49.7818 | 73.0545 | -0.098725 | 0.0010489 | 0.063734 | 0.073958 | -0.00026703 | 0.0021917 | 0.00414 | -0.025757 | 0.0015295 | 0.0021362 | 0.00027342 | -0.0019333 | -0.0062207 | 0.0032299 | -43.6157 | 73.0682 | -49.8505 | 72.7203 | -45.52 | -49.7543 | -49.1226 | -47.7356 | 73.1003 | -49.823 | -49.3195 | -49.5941 | -49.9603 | -49.6124 | -0.068665 | 0.013733 | -0.33417 | 4.2618 | 0.65918 | 0.027466 | 0.72784 | 0.096131 | -0.041199 | 0.045777 | -122.374 | 0.18768 | 0.16937 | -0.17853 | 0.21057 | -0.13733 | 4.3304 | 122.5708 | 0.22888 | 0.50354 | 122.9187 | 122.9233 | 122.85 | 122.8821 | -122.905 | -122.8775 | 122.5021 | 0.46234 | 6.1661 | 2.0462
4264.1719 | 122.9324 | -49.7864 | 73.0774 | -0.098725 | -0.00023294 | 0.066084 | 0.072677 | 0.0022964 | 0.0024053 | 0.0064898 | -0.034912 | 0.0043065 | 0.00064083 | 0.00070062 | -0.0030013 | -0.0053663 | 0.00045294 | -43.5791 | 73.0637 | -49.8505 | 72.7158 | -45.4788 | -49.7314 | -49.118 | -47.7402 | 73.0865 | -49.823 | -49.3195 | -49.5895 | -49.9374 | -49.6124 | -0.064087 | -0.013733 | -0.36163 | 4.3076 | 0.66833 | 0.054932 | 0.73242 | 0.11902 | -0.036621 | 0.009155 | -122.3969 | 0.19684 | 0.17395 | -0.15106 | 0.21057 | -0.11444 | 4.3716 | 122.5662 | 0.23346 | 0.50354 | 122.9141 | 122.9095 | 122.85 | 122.8729 | -122.9279 | -122.9004 | 122.5021 | 0.46692 | 6.2073 | 2.0462
4265.1719 | 122.9141 | -49.7772 | 73.0774 | -0.098725 | -1.9142e-05 | 0.065871 | 0.070754 | -0.00069423 | 0.0019781 | 0.0062762 | -0.010498 | 0.00088875 | 0.0023498 | -0.0014356 | -0.0023605 | -0.0064343 | 0.0032299 | -43.5654 | 73.0728 | -49.823 | 72.7386 | -45.4239 | -49.7269 | -49.0814 | -47.7127 | 73.1186 | -49.8184 | -49.292 | -49.5575 | -49.9054 | -49.5758 | -0.045776 | -0.004578 | -0.33875 | 4.3533 | 0.6958 | 0.050354 | 0.74158 | 0.09613 | -0.041198 | 0.041198 | -122.3694 | 0.21973 | 0.20142 | -0.12817 | 0.24261 | -0.086976 | 4.3991 | 122.5616 | 0.26093 | 0.52643 | 122.8958 | 122.937 | 122.85 | 122.8958 | -122.9004 | -122.8958 | 122.5159 | 0.48523 | 6.2119 | 2.0645
4266.1719 | 122.9553 | -49.7818 | 73.0774 | -0.03006 | -0.00023294 | 0.063734 | 0.071181 | -0.0013352 | 0.0024053 | 0.0079852 | -0.034912 | 0.0013159 | 0.00064083 | 0.002196 | -0.0034287 | -0.0083569 | 0.0028027 | -43.5379 | 73.1049 | -49.8276 | 72.7661 | -45.3918 | -49.6994 | -49.0677 | -47.6852 | 73.0911 | -49.7955 | -49.2691 | -49.5621 | -49.9146 | -49.5895 | -0.045777 | 0.027465 | -0.31128 | 4.39 | 0.71411 | 0.082397 | 0.75989 | 0.12817 | -0.013733 | 0.013732 | -122.3465 | 0.21973 | 0.19226 | -0.13275 | 0.20599 | -0.11902 | 4.4357 | 122.5937 | 0.23346 | 0.52643 | 122.9324 | 122.8867 | 122.8867 | 122.8729 | -122.905 | -122.8729 | 122.5479 | 0.5127 | 6.2439 | 2.0966
4267.1719 | 122.937 | -49.7452 | 73.0865 | -0.075836 | 0.0019035 | 0.065871 | 0.071181 | -0.00069423 | 0.0036871 | 0.0077716 | -0.028809 | 0.0019567 | -0.00042717 | 0.0030506 | -0.0017197 | -0.0036573 | 0.0010937 | -43.5242 | 73.0774 | -49.8047 | 72.7707 | -45.3369 | -49.6811 | -49.0677 | -47.6578 | 73.114 | -49.7498 | -49.2599 | -49.5392 | -49.8962 | -49.5621 | -0.059509 | -0.009155 | -0.31586 | 4.4083 | 0.67749 | 0.064087 | 0.737 | 0.1236 | -0.004578 | 0.027466 | -122.3465 | 0.20599 | 0.18311 | -0.15106 | 0.18768 | -0.14648 | 4.4678 | 122.5754 | 0.21057 | 0.48981 | 122.8821 | 122.8638 | 122.8226 | 122.8592 | -122.8912 | -122.8363 | 122.5159 | 0.48523 | 6.221 | 2.0874
4268.1719 | 122.9416 | -49.7635 | 73.0591 | -0.091095 | -0.00023294 | 0.064375 | 0.071609 | -0.001976 | 0.0017645 | 0.0032856 | -0.025757 | 0.00088875 | 0.0012818 | -0.00058098 | -0.0027877 | -0.0053663 | 0.0019483 | -43.5333 | 73.0774 | -49.8047 | 72.7753 | -45.3003 | -49.6811 | -49.054 | -47.6532 | 73.1232 | -49.791 | -49.2599 | -49.53 | -49.8825 | -49.5529 | -0.041198 | 0.018311 | -0.28381 | 4.4632 | 0.70953 | 0.082398 | 0.75073 | 0.1236 | -0.027466 | 0.064087 | -122.319 | 0.23346 | 0.21057 | -0.11902 | 0.23804 | -0.091552 | 4.5044 | 122.58 | 0.26093 | 0.53101 | 122.8821 | 122.9141 | 122.8409 | 122.8867 | -122.8638 | -122.85 | 122.5388 | 0.50354 | 6.2302 | 2.1103
4269.1719 | 122.9141 | -49.7452 | 73.0591 | -0.068207 | 0.0012625 | 0.064162 | 0.07289 | 0.0018692 | 0.0019781 | 0.0045672 | -0.022705 | 0.00088875 | 0.0019226 | -0.0014356 | 0.00020289 | -0.0049389 | 0.0021619 | -43.5516 | 73.1049 | -49.8322 | 72.7386 | -45.3415 | -49.7086 | -49.0768 | -47.699 | 73.1415 | -49.7818 | -49.292 | -49.5758 | -49.8917 | -49.5895 | -0.086975 | 0.045776 | -0.32044 | 4.4037 | 0.66834 | 0.036621 | 0.75531 | 0.1236 | -0.036621 | 0.082397 | -122.3511 | 0.16937 | 0.15564 | -0.14648 | 0.19226 | -0.10986 | 4.4907 | 122.5708 | 0.20599 | 0.48981 | 122.937 | 122.9233 | 122.85 | 122.8867 | -122.8912 | -122.8409 | 122.4838 | 0.45319 | 6.1935 | 2.0462
4270.1719 | 122.9095 | -49.7726 | 73.0774 | -0.12161 | 0.0014761 | 0.06523 | 0.072463 | 0.0022964 | 0.0030463 | 0.0062762 | -0.03186 | 0.0013159 | 2.8e-08 | 0.0017688 | -0.0019333 | -0.0064343 | 0.00045294 | -43.5196 | 73.0957 | -49.8138 | 72.7707 | -45.2911 | -49.704 | -49.0631 | -47.6898 | 73.1186 | -49.8093 | -49.2828 | -49.5483 | -49.9008 | -49.5621 | -0.041199 | 0.01831 | -0.3067 | 4.4815 | 0.70953 | 0.068665 | 0.75073 | 0.10986 | -0.036621 | 0.041198 | -122.3602 | 0.2243 | 0.21057 | -0.12817 | 0.24719 | -0.091553 | 4.5227 | 122.5845 | 0.26093 | 0.52643 | 122.9095 | 122.9279 | 122.8683 | 122.8912 | -122.8912 | -122.8867 | 122.5433 | 0.48981 | 6.2531 | 2.0828
4271.1719 | 122.9095 | -49.7589 | 73.0911 | -0.083466 | 0.0025443 | 0.065871 | 0.07289 | -0.0043258 | 0.0013373 | 0.002431 | -0.01355 | 3.4148e-05 | 0.0019226 | -0.0052808 | -0.0023605 | -0.0053663 | 0.0021619 | -43.5379 | 73.1094 | -49.8093 | 72.7753 | -45.2179 | -49.6765 | -49.0494 | -47.6532 | 73.1369 | -49.791 | -49.2599 | -49.5346 | -49.9054 | -49.5667 | -0.050354 | 0.018311 | -0.31586 | 4.541 | 0.70953 | 0.082397 | 0.75989 | 0.13275 | -0.032044 | 0.045777 | -122.3511 | 0.2243 | 0.19226 | -0.14649 | 0.2243 | -0.11444 | 4.5914 | 122.5845 | 0.25635 | 0.53101 | 122.9187 | 122.9279 | 122.8683 | 122.8958 | -122.9004 | -122.8821 | 122.5342 | 0.49896 | 6.221 | 2.1057
4272.1719 | 122.905 | -49.7406 | 73.1049 | -0.037689 | -0.00023294 | 0.063734 | 0.072036 | 0.00080117 | 0.00048269 | 0.0037128 | 0.001709 | 0.0015295 | 0.0023498 | -0.0031446 | -0.0021469 | -0.0057935 | -0.0023243 | -43.5013 | 73.1186 | -49.791 | 72.7982 | -45.1767 | -49.6536 | -49.0402 | -47.612 | 73.1277 | -49.7726 | -49.2416 | -49.5026 | -49.8505 | -49.5529 | -0.050354 | 0.013733 | -0.3067 | 4.5639 | 0.70038 | 0.086976 | 0.75073 | 0.13733 | -0.032043 | 0.022889 | -122.3465 | 0.23804 | 0.18768 | -0.10986 | 0.21973 | -0.07782 | 4.6143 | 122.5891 | 0.27008 | 0.53101 | 122.9095 | 122.9004 | 122.8592 | 122.8683 | -122.8958 | -122.8775 | 122.5388 | 0.49896 | 6.2393 | 2.1286
4273.1719 | 122.9599 | -49.6994 | 73.0911 | -0.10635 | 0.0014761 | 0.064589 | 0.070754 | -0.0030442 | 0.0021917 | 0.0047808 | -0.019653 | 0.0015295 | 0.0025634 | 0.0030506 | -0.0032151 | -0.0053663 | 0.0049389 | -43.4601 | 73.1049 | -49.7818 | 72.8165 | -45.195 | -49.6307 | -48.912 | -47.5479 | 73.1506 | -49.736 | -49.1913 | -49.4522 | -49.7955 | -49.498 | -0.082397 | 0.013733 | -0.27466 | 4.5044 | 0.78735 | 0.068665 | 0.86975 | 0.15106 | -0.036621 | 0.05951 | -122.2824 | 0.24719 | 0.20142 | -0.09613 | 0.23804 | -0.059509 | 4.5868 | 122.5983 | 0.28381 | 0.54474 | 122.8867 | 122.8867 | 122.8043 | 122.85 | -122.8729 | -122.8271 | 122.5159 | 0.50812 | 6.2393 | 2.1515
4274.1719 | 122.9462 | -49.7543 | 73.0957 | -0.060578 | -0.00066014 | 0.064375 | 0.072463 | 0.0016556 | 0.0019781 | 0.0071308 | -0.022705 | 0.0032385 | 0.0014954 | 0.001128 | -0.0017197 | -0.0057935 | -0.0010425 | -43.5059 | 73.114 | -49.7955 | 72.7753 | -45.1447 | -49.6765 | -49.0356 | -47.6624 | 73.1598 | -49.7452 | -49.2645 | -49.5346 | -49.8825 | -49.5438 | -0.041199 | 0.018311 | -0.32043 | 4.6097 | 0.71869 | 0.077819 | 0.75989 | 0.11902 | 0.009155 | 0.064087 | -122.3602 | 0.21973 | 0.21057 | -0.12817 | 0.20142 | -0.13733 | 4.6509 | 122.5708 | 0.21057 | 0.48065 | 122.9095 | 122.905 | 122.8683 | 122.9141 | -122.8912 | -122.8409 | 122.5296 | 0.48981 | 6.2485 | 2.092
4275.1719 | 122.9782 | -49.7223 | 73.1277 | -0.083466 | 0.0010489 | 0.063734 | 0.070968 | 0.00037377 | 0.00091009 | 0.0054218 | 0.013916 | 0.0011023 | 0.00064083 | -0.0076306 | -0.0036423 | -0.0075025 | 2.554e-05 | -43.4555 | 73.1461 | -49.7635 | 72.8394 | -45.0394 | -49.6078 | -48.9807 | -47.5571 | 73.1644 | -49.7406 | -49.2004 | -49.4568 | -49.8093 | -49.5071 | -0.041199 | 0.01831 | -0.28839 | 4.6829 | 0.74158 | 0.11444 | 0.78278 | 0.15564 | -0.018311 | 0.036621 | -122.3282 | 0.2655 | 0.21515 | -0.086975 | 0.23346 | -0.068664 | 4.7241 | 122.6028 | 0.28381 | 0.54016 | 122.9095 | 122.905 | 122.8683 | 122.8867 | -122.8912 | -122.8683 | 122.5616 | 0.52185 | 6.2668 | 2.1652
4276.1719 | 122.8912 | -49.7543 | 73.0453 | -0.1445 | -1.9142e-05 | 0.067152 | 0.073745 | 0.00037377 | 0.0017645 | 0.0052082 | 0.0078126 | 0.00067495 | 0.00042723 | -0.0020764 | -0.0017197 | -0.0062207 | 0.0025891 | -43.5104 | 73.1186 | -49.7726 | 72.7661 | -45.1172 | -49.6948 | -49.0585 | -47.6807 | 73.1415 | -49.7681 | -49.2462 | -49.5163 | -49.8734 | -49.53 | -0.018311 | 0.073242 | -0.27924 | 4.6371 | 0.6958 | 0.059509 | 0.71411 | 0.07782 | -0.013733 | 0.09613 | -122.2916 | 0.23804 | 0.2243 | -0.11902 | 0.23804 | -0.10529 | 4.6555 | 122.5388 | 0.25177 | 0.52185 | 122.8912 | 122.9095 | 122.8729 | 122.8958 | -122.818 | -122.8134 | 122.5204 | 0.50812 | 6.2439 | 2.0737
4277.1719 | 122.9691 | -49.7131 | 73.1323 | -0.068207 | -0.00087374 | 0.064589 | 0.071181 | -0.0011214 | 0.0032599 | 0.0037128 | -0.016602 | 0.0036657 | -0.00021357 | 0.001128 | -0.0019333 | -0.0036573 | 0.00045294 | -43.4509 | 73.1049 | -49.7589 | 72.8302 | -45.0027 | -49.617 | -48.9899 | -47.58 | 73.1735 | -49.7452 | -49.2096 | -49.4797 | -49.8322 | -49.5026 | -0.045776 | -0.027466 | -0.30212 | 4.7104 | 0.72327 | 0.096131 | 0.76904 | 0.14191 | -0.032043 | 0.041199 | -122.3419 | 0.23346 | 0.21057 | -0.11902 | 0.24262 | -0.086975 | 4.7562 | 122.5891 | 0.2655 | 0.53558 | 122.8638 | 122.9187 | 122.818 | 122.8867 | -122.8912 | -122.8775 | 122.5433 | 0.50354 | 6.2622 | 2.1332
4278.1719 | 122.9187 | -49.7406 | 73.0957 | -0.091095 | -0.00023294 | 0.065016 | 0.073531 | 0.0018692 | 0.0024053 | 0.0037128 | -0.0043946 | 0.00067495 | 0.0023498 | 0.00070062 | -0.0023605 | -0.0053663 | -0.00082886 | -43.4372 | 73.1277 | -49.7589 | 72.8485 | -44.9341 | -49.6124 | -48.9716 | -47.5571 | 73.1506 | -49.7726 | -49.2004 | -49.4797 | -49.823 | -49.5117 | -0.01831 | 0.032044 | -0.24719 | 4.8065 | 0.76904 | 0.12817 | 0.78735 | 0.14648 | -0.032043 | 0.054932 | -122.2961 | 0.26093 | 0.22888 | -0.082397 | 0.26093 | -0.050354 | 4.8248 | 122.6074 | 0.29297 | 0.5722 | 122.8867 | 122.9233 | 122.8683 | 122.8912 | -122.8546 | -122.8683 | 122.5891 | 0.54016 | 6.3034 | 2.1835
4279.1719 | 122.937 | -49.6948 | 73.1186 | -0.037689 | 0.00062166 | 0.064162 | 0.073531 | 0.0010148 | 0.0030463 | 0.0073444 | -0.0043946 | 0.00088875 | 0.0032044 | -0.00079478 | -0.0015061 | -0.0064343 | -0.0036059 | -43.4326 | 73.1644 | -49.7726 | 72.8439 | -44.8975 | -49.5804 | -48.9578 | -47.5479 | 73.1735 | -49.7269 | -49.1776 | -49.4522 | -49.8047 | -49.4705 | -0.07782 | 0.045777 | -0.27466 | 4.7974 | 0.737 | 0.11444 | 0.81482 | 0.19226 | -0.032044 | 0.054932 | -122.2961 | 0.24261 | 0.2243 | -0.10986 | 0.25635 | -0.077819 | 4.8752 | 122.6166 | 0.27466 | 0.54932 | 122.937 | 122.9004 | 122.8592 | 122.8683 | -122.8912 | -122.8455 | 122.5388 | 0.51727 | 6.2622 | 2.1469
4280.1719 | 122.9599 | -49.6948 | 73.1415 | -0.052948 | 0.0010489 | 0.063734 | 0.070754 | -0.00090783 | 0.0021917 | 0.0060626 | -0.0074462 | -0.0016749 | 0.0019226 | -0.0027174 | -0.0038559 | -0.0051527 | 0.0042981 | -43.3731 | 73.1552 | -49.7635 | 72.8577 | -44.838 | -49.5575 | -48.9395 | -47.5388 | 73.1735 | -49.7177 | -49.1638 | -49.4431 | -49.7635 | -49.4568 | -0.068665 | 0.013733 | -0.28381 | 4.8569 | 0.75531 | 0.13733 | 0.82397 | 0.20599 | -0.022888 | 0.032044 | -122.3053 | 0.25177 | 0.23804 | -0.068665 | 0.26093 | -0.045777 | 4.9255 | 122.6212 | 0.27466 | 0.55389 | 122.9187 | 122.8912 | 122.85 | 122.8683 | -122.905 | -122.8592 | 122.5525 | 0.53101 | 6.3217 | 2.1561
4281.1719 | 122.9462 | -49.6719 | 73.1323 | -0.075836 | -0.0019417 | 0.064803 | 0.071822 | -0.001976 | 0.0013373 | 0.0032856 | 0.0047608 | 0.0025975 | 0.0023498 | -0.00036738 | -0.0038559 | -0.0064343 | -0.00082886 | -43.3685 | 73.1277 | -49.7177 | 72.9172 | -44.9799 | -49.5987 | -48.9075 | -47.5021 | 73.1827 | -49.7177 | -49.1592 | -49.411 | -49.7498 | -49.4568 | -0.045776 | -0.004577 | -0.21515 | 4.6921 | 0.76447 | 0.073242 | 0.81024 | 0.11902 | -0.045776 | 0.050354 | -122.2916 | 0.26093 | 0.21515 | -0.07782 | 0.26093 | -0.032044 | 4.7379 | 122.6349 | 0.3067 | 0.55847 | 122.8455 | 122.9004 | 122.7997 | 122.8546 | -122.85 | -122.85 | 122.5891 | 0.5127 | 6.3034 | 2.1698
4282.1719 | 122.9324 | -49.7131 | 73.1232 | -0.075836 | 0.00062166 | 0.064803 | 0.071181 | 0.0010148 | 0.0030463 | 0.00414 | 0.0078126 | 0.0013159 | 0.0021362 | 0.002196 | -0.0021469 | -0.0055799 | 0.0019483 | -43.3777 | 73.1369 | -49.7589 | 72.8485 | -44.783 | -49.5895 | -48.9624 | -47.5433 | 73.1689 | -49.7406 | -49.1867 | -49.4614 | -49.8093 | -49.5026 | -0.045776 | 0.013733 | -0.27466 | 4.9301 | 0.75073 | 0.1236 | 0.79651 | 0.16937 | -0.027466 | 0.045776 | -122.3099 | 0.25177 | 0.21057 | -0.09613 | 0.23804 | -0.068664 | 4.9759 | 122.6074 | 0.27924 | 0.55389 | 122.8958 | 122.9095 | 122.85 | 122.8821 | -122.8821 | -122.8638 | 122.5616 | 0.52643 | 6.3354 | 2.1698
4283.1719 | 122.9507 | -49.6994 | 73.1232 | -0.091095 | 0.00040806 | 0.066084 | 0.07225 | -0.0041122 | 0.0015509 | 0.0060626 | -0.0043946 | 0.00046135 | 0.0019226 | -0.0035718 | -0.0019333 | -0.0070753 | -0.00082886 | -43.3548 | 73.1598 | -49.7772 | 72.8577 | -44.7784 | -49.5712 | -48.9441 | -47.5342 | 73.1598 | -49.704 | -49.1684 | -49.4476 | -49.7864 | -49.4843 | -0.07782 | 0.036621 | -0.2655 | 4.921 | 0.75531 | 0.12817 | 0.83313 | 0.20599 | -0.004577 | 0.036621 | -122.2916 | 0.25177 | 0.21515 | -0.086975 | 0.21973 | -0.082398 | 4.9988 | 122.6349 | 0.25635 | 0.53558 | 122.937 | 122.8638 | 122.8592 | 122.8592 | -122.9004 | -122.8271 | 122.5571 | 0.53101 | 6.3446 | 2.1652
4284.1719 | 122.9599 | -49.6811 | 73.114 | -0.052948 | -1.9142e-05 | 0.066725 | 0.069045 | 0.0012284 | 0.0043281 | 0.0026446 | -0.0043946 | 0.0019567 | 0.0012818 | 5.9824e-05 | -0.0027877 | -0.0051527 | -0.0033923 | -43.4235 | 73.1277 | -49.736 | 72.876 | -44.7418 | -49.5621 | -48.912 | -47.5159 | 73.1735 | -49.7177 | -49.1684 | -49.4385 | -49.7681 | -49.4614 | -0.054932 | 0.013733 | -0.23804 | 4.9393 | 0.76904 | 0.11902 | 0.82398 | 0.17395 | -0.036621 | 0.059509 | -122.2824 | 0.24261 | 0.21973 | -0.086975 | 0.25635 | -0.050354 | 4.9942 | 122.612 | 0.27923 | 0.54932 | 122.8638 | 122.8912 | 122.8088 | 122.8546 | -122.85 | -122.8317 | 122.5571 | 0.5127 | 6.2576 | 2.1652
4285.1719 | 122.9645 | -49.6719 | 73.1277 | -0.03006 | 0.00040806 | 0.066298 | 0.074172 | 0.0016556 | 0.00026909 | 0.0054218 | 0.016968 | 0.0011023 | 0.001068 | -0.001222 | -0.0032151 | -0.0066479 | 0.0017345 | -43.3411 | 73.1461 | -49.7589 | 72.876 | -44.7922 | -49.5804 | -48.8525 | -47.5021 | 73.1918 | -49.7131 | -49.1409 | -49.4247 | -49.7589 | -49.4705 | -0.086975 | 0.01831 | -0.25177 | 4.8798 | 0.8194 | 0.091553 | 0.90637 | 0.17853 | -0.041199 | 0.064086 | -122.2687 | 0.24719 | 0.20142 | -0.086975 | 0.24262 | -0.045776 | 4.9667 | 122.6349 | 0.28839 | 0.57221 | 122.905 | 122.905 | 122.818 | 122.8638 | -122.8867 | -122.8409 | 122.5479 | 0.53101 | 6.3309 | 2.1698
4286.1719 | 122.9736 | -49.6765 | 73.1415 | -0.052948 | 0.0016899 | 0.065657 | 0.071822 | -0.0028304 | -0.0012261 | 0.0017902 | 0.010864 | 0.00088875 | 0.001068 | -0.0048536 | -0.0019333 | -0.0047253 | -0.0012561 | -43.3136 | 73.1644 | -49.7177 | 72.8668 | -44.6686 | -49.5438 | -48.9258 | -47.5342 | 73.1689 | -49.7131 | -49.1364 | -49.3973 | -49.7589 | -49.4522 | -0.041198 | 0.022889 | -0.27466 | 5.0079 | 0.75073 | 0.13275 | 0.79193 | 0.17395 | -0.036621 | 0.027466 | -122.2778 | 0.27924 | 0.2243 | -0.082397 | 0.26093 | -0.045776 | 5.0491 | 122.5845 | 0.31586 | 0.57678 | 122.8821 | 122.8821 | 122.8409 | 122.8455 | -122.8592 | -122.8546 | 122.5433 | 0.54016 | 6.3629 | 2.1423
4287.1719 | 122.9828 | -49.6902 | 73.1735 | -0.068207 | 0.0010489 | 0.06523 | 0.07289 | -0.001976 | 0.0026191 | 0.00414 | 0.029175 | 0.0023839 | 0.0032044 | 0.00048702 | -0.0030013 | -0.0064343 | 0.0015209 | -43.3456 | 73.1689 | -49.7223 | 72.8622 | -44.6732 | -49.5438 | -48.9212 | -47.5296 | 73.1873 | -49.6948 | -49.1592 | -49.4019 | -49.7498 | -49.4522 | -0.032043 | -0.004578 | -0.31128 | 5.0171 | 0.76904 | 0.14648 | 0.80109 | 0.17853 | -0.004577 | 0.013733 | -122.3328 | 0.28839 | 0.23804 | -0.059509 | 0.24261 | -0.054932 | 5.0491 | 122.5845 | 0.29297 | 0.53558 | 122.8912 | 122.8821 | 122.8592 | 122.8775 | -122.8958 | -122.8683 | 122.5525 | 0.53101 | 6.3446 | 2.1606
4288.1719 | 123.056 | -49.6902 | 73.1506 | -0.098725 | 0.00083526 | 0.06523 | 0.071822 | -0.0030442 | 0.0011237 | 0.003072 | -0.01355 | 0.0023839 | 0.0012818 | 0.0094592 | -0.0023605 | -0.0064343 | 0.0025891 | -43.2953 | 73.1781 | -49.7406 | 72.8806 | -44.5908 | -49.5392 | -48.9258 | -47.493 | 73.1873 | -49.7177 | -49.1638 | -49.411 | -49.7452 | -49.4476 | -0.050354 | 0.027466 | -0.27008 | 5.0995 | 0.76447 | 0.15106 | 0.81482 | 0.20142 | -0.027465 | 0.036621 | -122.3145 | 0.27924 | 0.24262 | -0.054931 | 0.27008 | -0.027466 | 5.1498 | 122.6212 | 0.3067 | 0.55389 | 122.9187 | 122.905 | 122.8683 | 122.8775 | -122.8912 | -122.8683 | 122.5708 | 0.52643 | 6.395 | 2.1973
4289.1719 | 122.9416 | -49.6536 | 73.1415 | -0.052948 | -0.0017281 | 0.06822 | 0.071822 | -0.0011214 | 0.0019781 | 0.0067036 | -0.0043946 | -0.0018885 | 2.8e-08 | 5.9824e-05 | -0.0023605 | -0.0081433 | 2.554e-05 | -43.3594 | 73.1415 | -49.7452 | 72.8714 | -44.545 | -49.5438 | -48.9166 | -47.5021 | 73.2147 | -49.7177 | -49.1592 | -49.4247 | -49.7818 | -49.4522 | -0.091553 | 0 | -0.27008 | 5.1086 | 0.737 | 0.10986 | 0.82855 | 0.20142 | -0.064087 | 0.073243 | -122.3007 | 0.22888 | 0.20142 | -0.12817 | 0.2655 | -0.064087 | 5.2002 | 122.6166 | 0.29297 | 0.55847 | 122.8867 | 122.9324 | 122.7951 | 122.8683 | -122.8867 | -122.8592 | 122.525 | 0.49438 | 6.2942 | 2.1515
4290.1719 | 122.9736 | -49.6582 | 73.1369 | -0.091095 | -1.9142e-05 | 0.064803 | 0.073104 | 0.0012284 | 0.0019781 | 0.002431 | 0.001709 | 0.00024775 | 0.0014954 | 0.001128 | -0.0023605 | -0.0081433 | 0.0015209 | -43.2907 | 73.1461 | -49.7131 | 72.8851 | -44.4397 | -49.5209 | -48.8708 | -47.4747 | 73.1964 | -49.7131 | -49.1592 | -49.4064 | -49.7452 | -49.4339 | -0.054932 | 0.009155 | -0.25177 | 5.2185 | 0.78735 | 0.13733 | 0.84229 | 0.19226 | -0.054932 | 0.059509 | -122.2961 | 0.25177 | 0.2243 | -0.086975 | 0.27924 | -0.032043 | 5.2734 | 122.5983 | 0.3067 | 0.55389 | 122.8592 | 122.9095 | 122.8043 | 122.8546 | -122.85 | -122.85 | 122.5433 | 0.49896 | 6.3675 | 2.1835
4291.1719 | 122.9736 | -49.6628 | 73.1461 | -0.045319 | 0.0021171 | 0.064589 | 0.074813 | 0.00251 | 0.00026909 | 0.0069172 | -0.034912 | 0.0017431 | -0.0023498 | 5.9824e-05 | -0.0027877 | -0.0070753 | -0.0016833 | -43.277 | 73.1735 | -49.7131 | 72.8851 | -44.4809 | -49.5438 | -48.9166 | -47.4152 | 73.2239 | -49.704 | -49.1272 | -49.3835 | -49.7452 | -49.4568 | -0.050354 | 0.027466 | -0.26093 | 5.1819 | 0.74616 | 0.11902 | 0.79651 | 0.16937 | -0.041198 | 0.07782 | -122.2733 | 0.27924 | 0.20599 | -0.082397 | 0.24719 | -0.041199 | 5.2322 | 122.5983 | 0.32043 | 0.57678 | 122.8867 | 122.9279 | 122.8363 | 122.8867 | -122.8592 | -122.85 | 122.5479 | 0.53558 | 6.3858 | 2.2476
4292.1719 | 122.9874 | -49.6536 | 73.1598 | -0.068207 | 0.00040806 | 0.06523 | 0.07289 | -0.0034714 | 0.0043281 | 0.0064898 | 0.001709 | 0.0023839 | 0.001709 | 0.00048702 | 0.0012711 | -0.0070753 | 0.0025891 | -43.2587 | 73.1461 | -49.7498 | 72.8897 | -44.4351 | -49.5483 | -48.912 | -47.4792 | 73.2056 | -49.6994 | -49.1043 | -49.3698 | -49.7314 | -49.411 | -0.096131 | -0.013733 | -0.27008 | 5.2185 | 0.74158 | 0.10528 | 0.83771 | 0.20142 | -0.045777 | 0.045776 | -122.2641 | 0.28381 | 0.24261 | -0.07782 | 0.28839 | -0.032043 | 5.3146 | 122.6395 | 0.32959 | 0.59509 | 122.8958 | 122.905 | 122.7997 | 122.8592 | -122.9095 | -122.8592 | 122.5433 | 0.54932 | 6.395 | 2.1744
4293.1719 | 122.9645 | -49.6719 | 73.1873 | -0.022431 | -1.9142e-05 | 0.065871 | 0.072036 | -0.005394 | 0.00048269 | 0.0064898 | 0.02002 | 0.0030249 | 0.00064083 | -0.0072034 | -0.0017197 | -0.0064343 | 0.0017345 | -43.2861 | 73.2101 | -49.704 | 72.8577 | -44.458 | -49.5575 | -48.9029 | -47.525 | 73.2285 | -49.6719 | -49.1547 | -49.3652 | -49.7269 | -49.4431 | -0.032043 | 0.022888 | -0.32959 | 5.2139 | 0.76904 | 0.11444 | 0.80109 | 0.14648 | 0 | 0.041199 | -122.3419 | 0.3067 | 0.22888 | -0.054932 | 0.22888 | -0.054932 | 5.246 | 122.5616 | 0.3067 | 0.51727 | 122.9141 | 122.9004 | 122.8821 | 122.9004 | -122.8912 | -122.8592 | 122.5296 | 0.51727 | 6.3858 | 2.1469
4294.1719 | 122.9599 | -49.6582 | 73.2056 | -0.052948 | -0.00044654 | 0.063521 | 0.071609 | -0.0021896 | 0.0011237 | 0.0026446 | 0.044434 | 0.0019567 | 0.0023498 | 0.0028368 | -0.0021469 | -0.0057935 | 0.0021619 | -43.2724 | 73.1781 | -49.7314 | 72.8485 | -44.4305 | -49.5529 | -48.912 | -47.5479 | 73.201 | -49.6948 | -49.1592 | -49.3927 | -49.7452 | -49.4431 | -0.073242 | -0.027465 | -0.35706 | 5.2277 | 0.74616 | 0.10529 | 0.8194 | 0.17853 | -0.036621 | -0.004577 | -122.3648 | 0.2655 | 0.21515 | -0.086975 | 0.25177 | -0.050354 | 5.3009 | 122.58 | 0.30212 | 0.53558 | 122.9095 | 122.8958 | 122.8363 | 122.8592 | -122.937 | -122.9004 | 122.5067 | 0.49896 | 6.3858 | 2.1103
4295.1719 | 122.9279 | -49.6674 | 73.1873 | -0.075836 | 0.0012625 | 0.066512 | 0.071609 | -0.0011214 | 0.0021917 | 0.0034992 | 0.035278 | 0.00067495 | 0.00085443 | -0.00036738 | -0.0025741 | -0.0070753 | 0.00045294 | -43.2724 | 73.2285 | -49.7223 | 72.8714 | -44.3848 | -49.5575 | -48.9166 | -47.5296 | 73.2468 | -49.6857 | -49.1638 | -49.3973 | -49.7269 | -49.4476 | -0.054932 | 0.041199 | -0.31586 | 5.2826 | 0.75073 | 0.10986 | 0.80566 | 0.16479 | -0.018311 | 0.059509 | -122.3511 | 0.27008 | 0.21973 | -0.05951 | 0.23804 | -0.041199 | 5.3375 | 122.5937 | 0.28839 | 0.52185 | 122.9507 | 122.9324 | 122.8958 | 122.9141 | -122.9095 | -122.8729 | 122.5388 | 0.50354 | 6.395 | 2.1378
4296.1719 | 122.9828 | -49.6674 | 73.2147 | -0.1445 | -0.00023294 | 0.064162 | 0.072677 | 0.0012284 | 0.00048269 | 0.0060626 | -0.01355 | 0.00067495 | 0.00085443 | 0.0017688 | -0.00086511 | -0.0053663 | -0.0040333 | -43.2129 | 73.1873 | -49.736 | 72.8943 | -44.2978 | -49.5483 | -48.8754 | -47.4701 | 73.201 | -49.6857 | -49.205 | -49.2874 | -49.7131 | -49.4064 | -0.068665 | -0.027466 | -0.32043 | 5.3696 | 0.79193 | 0.11902 | 0.8606 | 0.18768 | -0.018311 | -0.013733 | -122.4197 | 0.37994 | 0.26093 | -0.045777 | 0.27924 | -0.027466 | 5.4382 | 122.6303 | 0.39825 | 0.48065 | 122.9233 | 122.8867 | 122.8546 | 122.8683 | -122.9507 | -122.9004 | 122.5616 | 0.46234 | 6.4545 | 2.1973
4297.1719 | 122.9645 | -49.6399 | 73.1918 | -0.098725 | 0.00083526 | 0.06758 | 0.07225 | 0.00080117 | 0.0021917 | 0.0064898 | 0.023071 | 0.0013159 | 0.0023498 | -0.0097668 | -0.0032151 | -0.0089979 | 0.0010937 | -43.2083 | 73.1873 | -49.704 | 72.908 | -44.2474 | -49.5392 | -48.8846 | -47.4701 | 73.2193 | -49.6811 | -49.118 | -49.3881 | -49.7269 | -49.4247 | -0.064086 | -0.004577 | -0.28381 | 5.3925 | 0.75531 | 0.10071 | 0.8194 | 0.16479 | -0.041198 | 0.027466 | -122.3099 | 0.25177 | 0.21515 | -0.086975 | 0.25635 | -0.045777 | 5.4565 | 122.612 | 0.29297 | 0.56305 | 122.8912 | 122.9004 | 122.8271 | 122.8592 | -122.8958 | -122.8729 | 122.5479 | 0.52185 | 6.4316 | 2.1698
4298.1719 | 122.9874 | -49.6674 | 73.1598 | -0.060578 | 0.0012625 | 0.065657 | 0.072036 | 0.0040054 | 0.00048269 | 0.0049946 | 0.010864 | -0.00017945 | 0.0029906 | -0.0020764 | -0.0012925 | -0.0062207 | 0.0019483 | -43.1992 | 73.1827 | -49.7086 | 72.8897 | -44.2337 | -49.5209 | -48.8663 | -47.4472 | 73.2193 | -49.6765 | -49.1135 | -49.3698 | -49.7086 | -49.4293 | -0.041199 | 0.022888 | -0.27008 | 5.4337 | 0.80109 | 0.14648 | 0.84228 | 0.18768 | -0.009156 | 0.059509 | -122.2733 | 0.29755 | 0.23804 | -0.041199 | 0.24719 | -0.032043 | 5.4749 | 122.5983 | 0.3067 | 0.56305 | 122.8912 | 122.8958 | 122.85 | 122.8867 | -122.8683 | -122.8363 | 122.5571 | 0.55389 | 6.4682 | 2.2202
4299.1719 | 122.9736 | -49.6353 | 73.1689 | -0.052948 | -0.00044654 | 0.065016 | 0.072677 | -0.0011214 | 0.0028327 | 0.0067036 | 0.013916 | 0.0017431 | 0.0021362 | -0.00058098 | -0.0012925 | -0.0072889 | 0.00023934 | -43.1992 | 73.1873 | -49.7131 | 72.9034 | -44.1971 | -49.5117 | -48.8708 | -47.4701 | 73.2422 | -49.6811 | -49.118 | -49.3515 | -49.7314 | -49.4156 | -0.07782 | 0.018311 | -0.2655 | 5.4382 | 0.76447 | 0.1236 | 0.84229 | 0.20142 | -0.045776 | 0.073242 | -122.287 | 0.28381 | 0.21973 | -0.09613 | 0.2655 | -0.050354 | 5.5161 | 122.6166 | 0.32959 | 0.56305 | 122.9004 | 122.9233 | 122.8226 | 122.8775 | -122.8821 | -122.85 | 122.5388 | 0.51727 | 6.4362 | 2.1652
4300.1719 | 122.937 | -49.6582 | 73.201 | -0.03006 | -0.00023294 | 0.065871 | 0.069259 | 0.00058737 | 0.0034735 | 0.0026446 | 0.02002 | 0.0017431 | 0.0025634 | -0.001222 | -0.0030013 | -0.0051527 | -0.00082886 | -43.2358 | 73.1781 | -49.7177 | 72.8851 | -44.1879 | -49.5392 | -48.8983 | -47.525 | 73.2468 | -49.6948 | -49.1547 | -49.4019 | -49.736 | -49.4476 | -0.059509 | -0.022888 | -0.31586 | 5.4703 | 0.75989 | 0.11902 | 0.8194 | 0.17853 | -0.036621 | 0.045776 | -122.3557 | 0.25635 | 0.21057 | -0.07782 | 0.24719 | -0.041199 | 5.5298 | 122.6028 | 0.29297 | 0.54016 | 122.8958 | 122.9416 | 122.8363 | 122.905 | -122.9187 | -122.8958 | 122.5433 | 0.50354 | 6.4224 | 2.1332
4301.1719 | 122.937 | -49.6445 | 73.2239 | -0.068207 | -0.0010873 | 0.064162 | 0.074172 | 0.00058737 | -0.00037171 | 0.00414 | 0.029175 | 0.0023839 | 0.0021362 | 0.0030506 | -0.0017197 | -0.0072889 | -0.00040166 | -43.1992 | 73.2468 | -49.6536 | 72.8943 | -44.1833 | -49.5667 | -48.8754 | -47.5021 | 73.2605 | -49.6857 | -49.1592 | -49.3835 | -49.7314 | -49.4431 | -0.009155 | 0.022888 | -0.32959 | 5.4611 | 0.76904 | 0.07782 | 0.7782 | 0.086975 | -0.041199 | 0.036621 | -122.3831 | 0.26093 | 0.20142 | -0.086975 | 0.24262 | -0.045776 | 5.4703 | 122.5479 | 0.30212 | 0.52643 | 122.9004 | 122.9462 | 122.8912 | 122.905 | -122.8775 | -122.9095 | 122.5388 | 0.48523 | 6.4453 | 2.1423
4302.1719 | 122.9416 | -49.6216 | 73.2056 | 0.023346 | 0.0014761 | 0.065871 | 0.073958 | -0.0024032 | 0.00091009 | 0.0045672 | 0.0047608 | 0.0013159 | 0.00085443 | -0.005708 | -0.0040695 | -0.0057935 | -0.0014697 | -43.1717 | 73.2239 | -49.6948 | 72.8943 | -44.1147 | -49.5346 | -48.8708 | -47.5067 | 73.2422 | -49.6765 | -49.118 | -49.3515 | -49.7269 | -49.4293 | -0.073242 | 0.018311 | -0.31128 | 5.5069 | 0.75073 | 0.086975 | 0.82397 | 0.16022 | -0.054932 | 0.036621 | -122.3236 | 0.27008 | 0.19226 | -0.10529 | 0.24719 | -0.050354 | 5.5801 | 122.5891 | 0.32501 | 0.55847 | 122.9187 | 122.9187 | 122.8455 | 122.8638 | -122.9004 | -122.8821 | 122.5159 | 0.50354 | 6.4499 | 2.1149
4303.1719 | 122.9416 | -49.6628 | 73.1827 | -0.052948 | 0.0010489 | 0.065871 | 0.074599 | 0.0010148 | 0.0030463 | 0.0028582 | -0.0043946 | 0.0021703 | 0.003418 | 0.0047594 | -0.0019333 | -0.0049389 | 0.00066654 | -43.1442 | 73.1964 | -49.6948 | 72.9126 | -44.0277 | -49.53 | -48.8525 | -47.4518 | 73.2239 | -49.6765 | -49.0997 | -49.3607 | -49.7177 | -49.4339 | -0.032043 | 0.013733 | -0.27008 | 5.6351 | 0.81024 | 0.13275 | 0.84228 | 0.16479 | -0.013733 | 0.041199 | -122.2824 | 0.30212 | 0.22888 | -0.054931 | 0.24262 | -0.041198 | 5.6671 | 122.6074 | 0.31586 | 0.57678 | 122.8912 | 122.9004 | 122.8592 | 122.8867 | -122.8775 | -122.8592 | 122.5754 | 0.56305 | 6.5186 | 2.211
4304.1719 | 123.0469 | -49.649 | 73.1232 | -0.15976 | 0.0029715 | 0.06822 | 0.072677 | -0.00090783 | 0.0030463 | 0.0054218 | 0.03833 | 3.4148e-05 | 0.001068 | -0.0054944 | -0.0010787 | -0.0053663 | -0.00061526 | -43.0847 | 73.0957 | -49.7177 | 72.963 | -43.9407 | -49.4934 | -48.8022 | -47.3923 | 73.1506 | -49.6628 | -49.054 | -49.3195 | -49.6582 | -49.3698 | -0.068664 | -0.027466 | -0.16022 | 5.7083 | 0.84686 | 0.15564 | 0.91553 | 0.2243 | -0.013733 | 0.027466 | -122.1771 | 0.32959 | 0.27924 | -0.009155 | 0.29297 | 0.004578 | 5.777 | 122.6807 | 0.34332 | 0.60883 | 122.8134 | 122.8134 | 122.7448 | 122.7997 | -122.8409 | -122.786 | 122.612 | 0.59509 | 6.5643 | 2.2568
4305.1719 | 122.9462 | -49.6353 | 73.1781 | -0.083466 | 0.00062166 | 0.063094 | 0.073318 | -0.00026703 | 0.0034735 | 0.0056354 | -0.01355 | 0.00024775 | -0.00064077 | -0.00229 | -0.0025741 | -0.0064343 | 0.0036571 | -43.1213 | 73.2101 | -49.6948 | 72.908 | -43.9774 | -49.5117 | -48.8571 | -47.4884 | 73.2239 | -49.6628 | -49.1272 | -49.3469 | -49.7131 | -49.4064 | -0.059509 | 0.032043 | -0.27008 | 5.658 | 0.7782 | 0.1236 | 0.83771 | 0.1831 | -0.027466 | 0.045776 | -122.3053 | 0.28839 | 0.22888 | -0.07782 | 0.25635 | -0.050354 | 5.7175 | 122.6028 | 0.31586 | 0.53558 | 122.905 | 122.8867 | 122.8455 | 122.8592 | -122.8729 | -122.8409 | 122.5433 | 0.50812 | 6.514 | 2.1469
4306.1719 | 122.9599 | -49.6445 | 73.2101 | -0.10635 | 0.0012625 | 0.06758 | 0.073318 | 0.0027238 | 0.0024053 | 0.0079852 | 0.016968 | 0.0023839 | 0.001068 | -0.00015378 | -0.0040695 | -0.0070753 | 0.00045294 | -43.1351 | 73.2147 | -49.6994 | 72.908 | -43.927 | -49.5117 | -48.8571 | -47.4747 | 73.2422 | -49.6857 | -49.1135 | -49.3469 | -49.7223 | -49.4247 | -0.054932 | 0.004578 | -0.30212 | 5.7175 | 0.78735 | 0.13275 | 0.84228 | 0.18768 | -0.041199 | 0.032043 | -122.3236 | 0.29755 | 0.21973 | -0.07782 | 0.26093 | -0.036621 | 5.7724 | 122.6074 | 0.33874 | 0.5722 | 122.9141 | 122.9279 | 122.8592 | 122.8867 | -122.9095 | -122.8958 | 122.5525 | 0.53101 | 6.5094 | 2.1698
4307.1719 | 122.8958 | -49.6353 | 73.1964 | -0.03006 | -0.00044654 | 0.065871 | 0.072463 | 0.00037377 | 0.00091009 | 0.0069172 | 0.013916 | 0.0023839 | 0.0012818 | 0.0017688 | -0.0019333 | -0.0068615 | -0.0023243 | -43.1763 | 73.2101 | -49.6719 | 72.8989 | -43.9224 | -49.5987 | -48.8754 | -47.493 | 73.2422 | -49.6582 | -49.1592 | -49.4019 | -49.7406 | -49.4476 | -0.036621 | 0.013733 | -0.29755 | 5.7129 | 0.75989 | 0.036621 | 0.79651 | 0.073242 | -0.022888 | 0.045776 | -122.3557 | 0.23346 | 0.18768 | -0.10529 | 0.21057 | -0.082398 | 5.7495 | 122.5708 | 0.25635 | 0.49896 | 122.8821 | 122.9004 | 122.8455 | 122.8775 | -122.8683 | -122.8546 | 122.5342 | 0.47607 | 6.459 | 2.1423
4308.1719 | 122.9691 | -49.649 | 73.1964 | -0.03006 | 0.0012625 | 0.063734 | 0.072463 | 0.0010148 | 0.0017645 | 0.0054218 | 0.010864 | 0.00024775 | 0.0014954 | 5.9824e-05 | -0.0036423 | -0.0068615 | 0.00088014 | -43.0939 | 73.1918 | -49.7177 | 72.8806 | -43.8812 | -49.5483 | -48.848 | -47.5067 | 73.233 | -49.6719 | -49.1226 | -49.3607 | -49.7269 | -49.4293 | -0.068664 | -0.004578 | -0.31586 | 5.7678 | 0.80109 | 0.10071 | 0.86975 | 0.16937 | -0.022888 | 0.036621 | -122.319 | 0.28839 | 0.21973 | -0.07782 | 0.24262 | -0.054932 | 5.8365 | 122.5983 | 0.31128 | 0.54932 | 122.9095 | 122.905 | 122.8409 | 122.8821 | -122.9141 | -122.8683 | 122.5296 | 0.52643 | 6.5552 | 2.1423
4309.1719 | 122.9279 | -49.6765 | 73.1461 | -0.11398 | 0.0031851 | 0.066939 | 0.074813 | 0.0037918 | -0.0010125 | 0.0056354 | -0.044067 | 0.0023839 | 0.001709 | 0.0030506 | -0.0017197 | -0.0079297 | -0.0016833 | -43.1305 | 73.1781 | -49.7498 | 72.8302 | -43.9133 | -49.617 | -48.9349 | -47.5845 | 73.2056 | -49.7086 | -49.1821 | -49.4339 | -49.8093 | -49.4751 | -0.073242 | 0.032044 | -0.31586 | 5.7632 | 0.74158 | 0.05951 | 0.81482 | 0.13275 | -0.032043 | 0.059509 | -122.3282 | 0.24262 | 0.20142 | -0.13275 | 0.23346 | -0.10071 | 5.8365 | 122.58 | 0.27466 | 0.52643 | 122.9279 | 122.9141 | 122.8546 | 122.8821 | -122.8958 | -122.8546 | 122.5067 | 0.49438 | 6.546 | 2.092
4310.1719 | 122.9507 | -49.6078 | 73.1506 | -0.060578 | 0.0012625 | 0.066725 | 0.074386 | 0.00016017 | 0.0047553 | 0.0071308 | 0.013916 | -0.00060665 | 0.00085443 | 0.0019824 | -0.0023605 | -0.0072889 | 0.0019483 | -43.0298 | 73.1689 | -49.7223 | 72.9218 | -43.7485 | -49.5071 | -48.8251 | -47.4701 | 73.2422 | -49.6582 | -49.0997 | -49.3744 | -49.7177 | -49.4247 | -0.11444 | 0.01831 | -0.22888 | 5.8594 | 0.78278 | 0.10071 | 0.89722 | 0.21515 | -0.050354 | 0.091552 | -122.2504 | 0.23346 | 0.18311 | -0.10986 | 0.23346 | -0.059509 | 5.9738 | 122.644 | 0.28381 | 0.55847 | 122.8912 | 122.9004 | 122.7768 | 122.85 | -122.8729 | -122.8088 | 122.5296 | 0.50812 | 6.5781 | 2.1378
4311.1719 | 122.9416 | -49.6353 | 73.1827 | -0.060578 | 0.0012625 | 0.065443 | 0.074172 | 0.00016017 | 0.0017645 | 0.0088398 | -0.010498 | 0.0017431 | 0.0019226 | -0.0010084 | -0.0021469 | -0.0072889 | 0.0010937 | -43.0435 | 73.1964 | -49.6948 | 72.9172 | -43.6844 | -49.5163 | -48.8205 | -47.4472 | 73.2422 | -49.6674 | -49.1089 | -49.3652 | -49.7086 | -49.4293 | -0.059509 | 0.013733 | -0.2655 | 5.9509 | 0.81482 | 0.11902 | 0.87433 | 0.17853 | -0.032043 | 0.059509 | -122.2916 | 0.27008 | 0.20599 | -0.073242 | 0.23804 | -0.041199 | 6.0104 | 122.612 | 0.30212 | 0.55847 | 122.8912 | 122.9095 | 122.8317 | 122.8775 | -122.8775 | -122.85 | 122.5525 | 0.52643 | 6.5918 | 2.1881
4312.1719 | 122.9553 | -49.6765 | 73.1644 | -0.037689 | 0.0016899 | 0.066725 | 0.073318 | -0.0030442 | -0.00015811 | 0.0049946 | -0.016602 | 0.0025975 | 0.0019226 | -0.0031446 | -0.0021469 | -0.0079297 | -0.0012561 | -43.0573 | 73.2147 | -49.704 | 72.9218 | -43.6478 | -49.5255 | -48.8388 | -47.4701 | 73.2239 | -49.6902 | -49.1043 | -49.3652 | -49.736 | -49.4293 | -0.027465 | 0.050354 | -0.24262 | 6.0287 | 0.83771 | 0.15106 | 0.86517 | 0.17853 | -0.013733 | 0.059509 | -122.2687 | 0.31128 | 0.24719 | -0.059509 | 0.26093 | -0.045776 | 6.0562 | 122.6257 | 0.32501 | 0.58594 | 122.9187 | 122.9141 | 122.8912 | 122.9004 | -122.8683 | -122.8546 | 122.5983 | 0.5722 | 6.6193 | 2.2064
4313.1719 | 122.9736 | -49.6353 | 73.1827 | -0.052948 | 0.0010489 | 0.065871 | 0.075027 | 0.0035782 | 0.00069649 | 0.0056354 | -0.022705 | 0.00088875 | 0.0023498 | 0.0017688 | -0.0032151 | -0.0062207 | -0.0040333 | -43.0527 | 73.201 | -49.7269 | 72.8943 | -43.6157 | -49.5255 | -48.8251 | -47.4701 | 73.2193 | -49.6902 | -49.1318 | -49.3561 | -49.7177 | -49.411 | -0.091553 | 0.018311 | -0.28839 | 6.0196 | 0.81024 | 0.10986 | 0.90179 | 0.20142 | -0.054932 | 0.036621 | -122.3145 | 0.27924 | 0.2243 | -0.082397 | 0.27924 | -0.027465 | 6.1111 | 122.6212 | 0.33417 | 0.55847 | 122.9279 | 122.9095 | 122.8363 | 122.8546 | -122.9095 | -122.8729 | 122.5296 | 0.50354 | 6.5826 | 2.1652
4314.1719 | 122.9965 | -49.6536 | 73.1232 | -0.15213 | 0.0014761 | 0.066725 | 0.073745 | 0.00037377 | 0.0013373 | 0.0026446 | 0.041382 | -0.00017945 | 0.0012818 | -0.006349 | -0.0025741 | -0.0057935 | 0.0036571 | -43.0573 | 73.1003 | -49.6857 | 72.9218 | -43.5059 | -49.5209 | -48.7839 | -47.4426 | 73.1277 | -49.7086 | -49.1226 | -49.3607 | -49.6902 | -49.411 | -0.032044 | -0.022888 | -0.20142 | 6.1478 | 0.86975 | 0.13275 | 0.90179 | 0.16479 | -0.054932 | 0.004578 | -122.2458 | 0.29297 | 0.24261 | -0.036622 | 0.29755 | 0.01831 | 6.1798 | 122.6074 | 0.3479 | 0.58594 | 122.7859 | 122.8363 | 122.7539 | 122.7814 | -122.8088 | -122.8317 | 122.5754 | 0.53101 | 6.5964 | 2.211
4315.1719 | 122.9462 | -49.6536 | 73.1735 | -0.03006 | 0.0016899 | 0.066084 | 0.071822 | -0.00069423 | -0.00037171 | 0.0034992 | -0.0013428 | 0.0011023 | 0.0023498 | 0.00070062 | -0.0027877 | -0.0079297 | 0.0023755 | -43.0801 | 73.1735 | -49.7406 | 72.8485 | -43.5654 | -49.5667 | -48.848 | -47.5159 | 73.2193 | -49.6994 | -49.1776 | -49.4064 | -49.7589 | -49.4522 | -0.086976 | 0 | -0.32501 | 6.0883 | 0.80566 | 0.086975 | 0.89264 | 0.17395 | -0.045777 | 0.045776 | -122.3511 | 0.24719 | 0.20142 | -0.10529 | 0.24719 | -0.059509 | 6.1752 | 122.5891 | 0.29297 | 0.52185 | 122.9141 | 122.9187 | 122.8271 | 122.8729 | -122.9141 | -122.8729 | 122.5021 | 0.47607 | 6.5735 | 2.1378
4316.1719 | 122.9782 | -49.6582 | 73.1918 | -0.098725 | 0.00019446 | 0.067793 | 0.074599 | -0.0017624 | 0.00091009 | 0.0056354 | 0.001709 | 0.0023839 | 2.8e-08 | -0.0025036 | -0.0030013 | -0.0075025 | 0.00088014 | -43.0161 | 73.1873 | -49.736 | 72.8897 | -43.4921 | -49.5438 | -48.8571 | -47.4884 | 73.2147 | -49.6994 | -49.1409 | -49.379 | -49.7223 | -49.4247 | -0.07782 | -0.004577 | -0.30212 | 6.1661 | 0.80109 | 0.11444 | 0.87891 | 0.19226 | -0.041199 | 0.022889 | -122.3328 | 0.27924 | 0.23346 | -0.064087 | 0.27466 | -0.022888 | 6.2439 | 122.6257 | 0.32043 | 0.55847 | 122.9233 | 122.9141 | 122.8455 | 122.8729 | -122.9279 | -122.8912 | 122.5479 | 0.51727 | 6.6422 | 2.1698
4317.1719 | 122.9736 | -49.6628 | 73.1827 | -0.12924 | 0.00040806 | 0.06758 | 0.07524 | 0.0012284 | 0.0021917 | 0.0067036 | -0.028809 | 0.00046135 | 0.001709 | 0.0051868 | -0.0023605 | -0.0064343 | 0.0013073 | -42.984 | 73.1598 | -49.7452 | 72.8806 | -43.4052 | -49.53 | -48.8388 | -47.4701 | 73.201 | -49.704 | -49.1272 | -49.4431 | -49.6628 | -49.4339 | -0.082397 | -0.022888 | -0.30212 | 6.2576 | 0.82398 | 0.13275 | 0.90637 | 0.21515 | -0.041198 | 0.018311 | -122.3099 | 0.21973 | 0.22888 | 0 | 0.27008 | 0.041198 | 6.34 | 122.6257 | 0.26093 | 0.57678 | 122.905 | 122.905 | 122.8226 | 122.8638 | -122.9279 | -122.8867 | 122.5433 | 0.53558 | 6.6788 | 2.1927
4318.1719 | 122.9828 | -49.6674 | 73.1598 | -0.12924 | 0.0014761 | 0.065871 | 0.073745 | 0.00080117 | 0.0015509 | 0.0034992 | -0.044067 | 0.0019567 | -0.0010682 | -0.0016492 | -0.0038559 | -0.0060071 | 0.0025891 | -42.9565 | 73.1506 | -49.7589 | 72.8806 | -43.364 | -49.5712 | -48.8388 | -47.4747 | 73.1735 | -49.704 | -49.1043 | -49.4202 | -49.7818 | -49.4705 | -0.091553 | -0.009155 | -0.27924 | 6.3034 | 0.82855 | 0.09613 | 0.9201 | 0.18768 | -0.036621 | 0.013733 | -122.2641 | 0.24719 | 0.19684 | -0.11444 | 0.23346 | -0.07782 | 6.395 | 122.6395 | 0.28381 | 0.59967 | 122.9095 | 122.8775 | 122.818 | 122.8409 | -122.9187 | -122.8638 | 122.5479 | 0.56305 | 6.7108 | 2.1927
4319.1719 | 122.9416 | -49.6445 | 73.1644 | -0.12161 | 0.00040806 | 0.068648 | 0.074599 | -0.001976 | 0.0030463 | 0.0056354 | -0.010498 | 0.00088875 | 0.0038452 | -0.00229 | -0.00086511 | -0.0068615 | -0.00018806 | -42.9703 | 73.1644 | -49.736 | 72.8714 | -43.3228 | -49.5438 | -48.8297 | -47.4472 | 73.2101 | -49.6857 | -49.1135 | -49.379 | -49.8413 | -49.4568 | -0.091553 | 0 | -0.29297 | 6.3217 | 0.81482 | 0.10071 | 0.90637 | 0.19226 | -0.041199 | 0.045776 | -122.2778 | 0.2655 | 0.18768 | -0.19684 | 0.22888 | -0.15564 | 6.4133 | 122.6074 | 0.3067 | 0.5722 | 122.9004 | 122.8958 | 122.8088 | 122.8546 | -122.9004 | -122.85 | 122.5159 | 0.53101 | 6.6742 | 2.1973
4320.1719 | 122.9599 | -49.6765 | 73.1415 | -0.098725 | -1.9142e-05 | 0.067152 | 0.074599 | -0.00026703 | 0.0015509 | 0.0028582 | -0.0013428 | 0.0023839 | 0.00021363 | -0.00079478 | -0.0044967 | -0.0064343 | 0.00045294 | -42.9428 | 73.1689 | -49.736 | 72.876 | -43.2861 | -49.5483 | -48.8434 | -47.4655 | 73.1827 | -49.7131 | -49.1272 | -49.4019 | -49.7406 | -49.4522 | -0.059509 | 0.027466 | -0.2655 | 6.3904 | 0.83313 | 0.12817 | 0.89264 | 0.18768 | -0.036621 | 0.041199 | -122.2687 | 0.27466 | 0.2243 | -0.064087 | 0.26093 | -0.027466 | 6.4499 | 122.612 | 0.31128 | 0.58594 | 122.905 | 122.8958 | 122.8455 | 122.8592 | -122.8775 | -122.8546 | 122.5525 | 0.54932 | 6.7337 | 2.211
4321.1719 | 122.9691 | -49.6994 | 73.1461 | -0.052948 | -0.0027963 | 0.065657 | 0.072677 | 0.00080117 | 0.0026191 | 0.00414 | 0.02002 | 0.0019567 | -0.0010682 | -0.00015378 | -0.0019333 | -0.0064343 | 0.0038709 | -42.9565 | 73.1552 | -49.7498 | 72.8485 | -43.2678 | -49.5667 | -48.8525 | -47.5159 | 73.1873 | -49.6902 | -49.1501 | -49.3835 | -49.7635 | -49.4568 | -0.050354 | 0.009155 | -0.29755 | 6.4316 | 0.84686 | 0.13275 | 0.89722 | 0.18311 | 0.009155 | 0.041199 | -122.2961 | 0.31586 | 0.24262 | -0.064087 | 0.23346 | -0.073242 | 6.4819 | 122.5983 | 0.3067 | 0.54016 | 122.905 | 122.8775 | 122.8546 | 122.8867 | -122.8958 | -122.8363 | 122.5479 | 0.54932 | 6.7429 | 2.1835
4322.1719 | 122.9645 | -49.6765 | 73.1415 | -0.052948 | -1.9142e-05 | 0.068861 | 0.073531 | 0.0022964 | 0.0013373 | 0.005849 | -0.0043946 | 0.0025975 | 0.00085443 | -0.0050672 | -0.0030013 | -0.0047253 | 2.554e-05 | -42.9153 | 73.1644 | -49.7314 | 72.8668 | -43.1763 | -49.5483 | -48.8251 | -47.4792 | 73.1918 | -49.7452 | -49.1455 | -49.3835 | -49.7498 | -49.4522 | -0.054931 | 0.022889 | -0.27466 | 6.5002 | 0.85144 | 0.12817 | 0.90637 | 0.1831 | -0.068664 | 0.050354 | -122.287 | 0.29297 | 0.2243 | -0.073242 | 0.29297 | -0.004578 | 6.5552 | 122.5983 | 0.36163 | 0.59967 | 122.8958 | 122.937 | 122.8409 | 122.8683 | -122.8729 | -122.8867 | 122.5433 | 0.53101 | 6.7612 | 2.1973
4323.1719 | 122.9645 | -49.6628 | 73.114 | -0.045319 | 0.0016899 | 0.066084 | 0.074813 | 0.001442 | 0.0017645 | 0.0054218 | -0.016602 | 0.0017431 | 0.0014954 | 0.0041186 | -0.0019333 | -0.0060071 | -0.0016833 | -42.9016 | 73.1552 | -49.7406 | 72.876 | -43.1168 | -49.5346 | -48.8434 | -47.4701 | 73.1735 | -49.7086 | -49.1318 | -49.4019 | -49.7543 | -49.4659 | -0.07782 | 0.041198 | -0.23804 | 6.546 | 0.8194 | 0.12817 | 0.89722 | 0.20599 | -0.045776 | 0.059509 | -122.2458 | 0.26093 | 0.19684 | -0.091552 | 0.24262 | -0.045776 | 6.6238 | 122.6166 | 0.3067 | 0.57678 | 122.8958 | 122.8821 | 122.818 | 122.8363 | -122.8546 | -122.8226 | 122.5388 | 0.53101 | 6.7612 | 2.1927
4324.1719 | 122.9599 | -49.6994 | 73.1232 | -0.098725 | 0.00083526 | 0.067366 | 0.075454 | -0.0026168 | 0.0036871 | 0.0062762 | -0.022705 | 0.0011023 | 0.0019226 | -0.0033582 | -0.0036423 | -0.0055799 | -0.0038197 | -42.9245 | 73.1323 | -49.7498 | 72.8439 | -43.1076 | -49.617 | -48.8617 | -47.5571 | 73.1598 | -49.7269 | -49.2096 | -49.4614 | -49.8138 | -49.5026 | -0.050354 | 0.009155 | -0.27924 | 6.5918 | 0.83771 | 0.082398 | 0.88806 | 0.13275 | -0.027466 | 0.036621 | -122.3328 | 0.23804 | 0.19684 | -0.11444 | 0.22431 | -0.086975 | 6.6422 | 122.5937 | 0.2655 | 0.51727 | 122.8821 | 122.8867 | 122.8317 | 122.8592 | -122.8729 | -122.85 | 122.5433 | 0.48981 | 6.7749 | 2.1423
4325.1719 | 122.9874 | -49.704 | 73.1323 | -0.068207 | 0.0023307 | 0.068648 | 0.074813 | -0.0013352 | 0.0015509 | 0.0039264 | -0.047119 | 0.0013159 | -0.00042717 | -0.0035718 | 0.00020289 | -0.0053663 | 2.554e-05 | -42.865 | 73.1094 | -49.7589 | 72.8714 | -42.9474 | -49.5529 | -48.8297 | -47.4655 | 73.1689 | -49.7314 | -49.1592 | -49.4476 | -49.791 | -49.4705 | -0.054932 | -0.022888 | -0.26093 | 6.7566 | 0.87433 | 0.15106 | 0.92926 | 0.20599 | -0.027466 | 0.036621 | -122.2916 | 0.25635 | 0.23346 | -0.086976 | 0.26093 | -0.05951 | 6.8115 | 122.6303 | 0.28381 | 0.5722 | 122.8683 | 122.9004 | 122.8134 | 122.8729 | -122.8912 | -122.8638 | 122.5754 | 0.54474 | 6.839 | 2.2385
4326.1719 | 122.9462 | -49.7223 | 73.1003 | -0.091095 | 0.00019446 | 0.066725 | 0.075454 | -0.0028304 | 0.0045417 | 0.0067036 | -0.0074462 | 0.0011023 | 0.00042723 | -0.0020764 | -0.0015061 | -0.0072889 | 0.00023934 | -42.8329 | 73.1277 | -49.7452 | 72.9172 | -42.897 | -49.5483 | -48.8068 | -47.4884 | 73.1873 | -49.7498 | -49.1638 | -49.4247 | -49.791 | -49.4888 | -0.022888 | 0.027466 | -0.18311 | 6.8253 | 0.91553 | 0.17395 | 0.93842 | 0.19684 | -0.027466 | 0.086975 | -122.2641 | 0.29755 | 0.23346 | -0.068665 | 0.26093 | -0.041199 | 6.8481 | 122.6624 | 0.32501 | 0.58594 | 122.8729 | 122.937 | 122.85 | 122.9095 | -122.8455 | -122.85 | 122.6395 | 0.55847 | 6.8893 | 2.2339
4327.1719 | 122.9507 | -49.704 | 73.1232 | -0.083466 | 0.0010489 | 0.068434 | 0.076522 | -5.343e-05 | 0.00069649 | 0.0022174 | 0.001709 | 0.00046135 | 0.0014954 | -0.002931 | -0.0019333 | -0.0053663 | -0.00061526 | -42.8055 | 73.1186 | -49.7726 | 72.7615 | -42.9382 | -49.4476 | -48.8205 | -47.4884 | 73.1735 | -49.7406 | -49.1638 | -49.4247 | -49.7864 | -49.4797 | -0.068665 | -0.004578 | -0.36163 | 6.7657 | 0.88348 | 0.25635 | 0.95215 | 0.32501 | -0.036622 | 0.050354 | -122.287 | 0.27923 | 0.2243 | -0.082398 | 0.26093 | -0.045776 | 6.8344 | 122.5342 | 0.31586 | 0.57678 | 122.8912 | 122.9141 | 122.8226 | 122.8775 | -122.8958 | -122.8638 | 122.4655 | 0.54016 | 6.8985 | 2.2156
4328.1719 | 122.9462 | -49.7223 | 73.1094 | -0.045319 | -0.0010873 | 0.068861 | 0.076736 | -0.0011214 | 0.0024053 | 0.0084124 | 0.029175 | 0.0011023 | 0.0019226 | -0.0059216 | -0.0015061 | -0.0081433 | -0.00061526 | -42.7826 | 73.1369 | -49.7864 | 72.8256 | -42.8329 | -49.5621 | -48.8388 | -47.5296 | 73.1644 | -49.7452 | -49.173 | -49.4202 | -49.7864 | -49.5026 | -0.064087 | 0.027466 | -0.28381 | 6.8893 | 0.88348 | 0.16022 | 0.94757 | 0.2243 | -0.022888 | 0.054932 | -122.2824 | 0.30212 | 0.21973 | -0.064087 | 0.24262 | -0.041199 | 6.9534 | 122.612 | 0.32501 | 0.5722 | 122.9233 | 122.9095 | 122.8592 | 122.8867 | -122.8958 | -122.8546 | 122.5479 | 0.54932 | 6.9397 | 2.1927
4329.1719 | 122.9599 | -49.7131 | 73.114 | -0.075836 | -0.00066014 | 0.066298 | 0.075667 | -5.343e-05 | 0.00048269 | 0.009267 | 0.010864 | 0.00088875 | 0.0019226 | 0.00048702 | -0.0032151 | -0.0053663 | 0.0068615 | -42.778 | 73.1277 | -49.7955 | 72.8485 | -42.7734 | -49.5712 | -48.8251 | -47.5296 | 73.1644 | -49.7498 | -49.173 | -49.4476 | -49.8001 | -49.5026 | -0.082397 | 0.013733 | -0.2655 | 6.9397 | 0.88806 | 0.14191 | 0.97046 | 0.2243 | -0.036621 | 0.050354 | -122.287 | 0.2655 | 0.21057 | -0.086975 | 0.24719 | -0.050354 | 7.0221 | 122.644 | 0.30212 | 0.57678 | 122.9233 | 122.9141 | 122.8409 | 122.8775 | -122.9095 | -122.8638 | 122.5616 | 0.54016 | 6.9351 | 2.1835
4330.1719 | 122.9828 | -49.7269 | 73.1003 | -0.11398 | 0.00083526 | 0.067793 | 0.075881 | 0.0012284 | 0.0026191 | 0.0084124 | -0.0043946 | 0.0019567 | 0.0038452 | 0.001128 | -0.0042831 | -0.0064343 | -0.0033923 | -42.7505 | 73.114 | -49.791 | 72.8256 | -42.6773 | -49.5895 | -48.8205 | -47.5571 | 73.114 | -49.7635 | -49.1821 | -49.4705 | -49.7955 | -49.4751 | -0.064087 | 0.013733 | -0.27466 | 7.0496 | 0.90637 | 0.13733 | 0.97046 | 0.20142 | -0.036621 | 0.013733 | -122.2824 | 0.25635 | 0.25177 | -0.068664 | 0.28839 | -0.032043 | 7.1136 | 122.6166 | 0.29297 | 0.58136 | 122.905 | 122.8775 | 122.8409 | 122.8409 | -122.8912 | -122.8638 | 122.5525 | 0.54474 | 6.9763 | 2.1698
4331.1719 | 122.9416 | -49.7406 | 73.0728 | -0.083466 | 0.0010489 | 0.068861 | 0.076736 | -0.0011214 | 0.0028327 | 0.0049946 | -0.010498 | 0.0025975 | 0.0023498 | -0.003999 | -0.0034287 | -0.0068615 | 0.0025891 | -42.7414 | 73.1003 | -49.7681 | 72.8027 | -42.6361 | -49.6216 | -48.88 | -47.5479 | 73.1232 | -49.7589 | -49.2096 | -49.4843 | -49.8276 | -49.5438 | -0.027465 | 0.027466 | -0.27008 | 7.1045 | 0.8606 | 0.11902 | 0.88806 | 0.14648 | -0.01831 | 0.050354 | -122.2824 | 0.25635 | 0.19684 | -0.086975 | 0.21515 | -0.068665 | 7.132 | 122.5708 | 0.27466 | 0.54932 | 122.8683 | 122.8821 | 122.8409 | 122.8638 | -122.8409 | -122.8317 | 122.5433 | 0.53101 | 6.9992 | 2.1927
4332.1719 | 122.905 | -49.7589 | 73.0774 | -0.13687 | 0.0010489 | 0.069502 | 0.07524 | -0.00090783 | 0.0019781 | 0.0069172 | -0.019653 | 0.0025975 | 0.0040588 | -0.0010084 | -0.0034287 | -0.0055799 | -0.00040166 | -42.7551 | 73.0408 | -49.823 | 72.757 | -42.627 | -49.6811 | -48.8983 | -47.612 | 73.0911 | -49.7818 | -49.2737 | -49.5483 | -49.8917 | -49.5712 | -0.064087 | -0.036622 | -0.32044 | 7.132 | 0.8606 | 0.07782 | 0.92468 | 0.14191 | -0.022888 | 0.013732 | -122.3511 | 0.21057 | 0.18768 | -0.13275 | 0.21057 | -0.10986 | 7.196 | 122.58 | 0.23346 | 0.50812 | 122.8638 | 122.8729 | 122.7997 | 122.85 | -122.9004 | -122.8592 | 122.5159 | 0.48523 | 7.0038 | 2.1469
4333.1719 | 122.9965 | -49.7314 | 73.1003 | -0.10635 | 0.0012625 | 0.069502 | 0.076095 | -0.00048063 | 0.0021917 | 0.0067036 | 0.013916 | 0.0034521 | 0.001709 | -0.0020764 | -0.0034287 | -0.0062207 | 0.00023934 | -42.6865 | 73.0865 | -49.8184 | 72.8027 | -42.4759 | -49.5987 | -48.8434 | -47.5159 | 73.082 | -49.7818 | -49.2142 | -49.53 | -49.7314 | -49.5071 | -0.086975 | -0.013733 | -0.29755 | 7.2556 | 0.88806 | 0.13275 | 0.97504 | 0.21973 | -0.050354 | -0.018311 | -122.3145 | 0.20142 | 0.2243 | 0 | 0.27466 | 0.050354 | 7.3425 | 122.6212 | 0.25177 | 0.56763 | 122.905 | 122.8638 | 122.818 | 122.8134 | -122.9187 | -122.8821 | 122.5342 | 0.51727 | 7.045 | 2.2156
4334.1719 | 122.9507 | -49.7452 | 73.0774 | -0.045319 | 0.00062166 | 0.069289 | 0.078017 | 0.0027238 | 0.0024053 | 0.0039264 | -0.01355 | 0.00024775 | 0.0012818 | -0.0037854 | -0.00065151 | -0.0077161 | 0.0013073 | -42.6544 | 73.1003 | -49.7955 | 72.7982 | -42.4301 | -49.6262 | -48.8434 | -47.5388 | 73.1186 | -49.7818 | -49.2279 | -49.5071 | -49.8413 | -49.5483 | -0.050354 | 0.022888 | -0.27924 | 7.3151 | 0.90179 | 0.11902 | 0.95215 | 0.16937 | -0.036621 | 0.041198 | -122.3053 | 0.23804 | 0.19684 | -0.096131 | 0.23346 | -0.05951 | 7.3654 | 122.5937 | 0.27466 | 0.55389 | 122.8958 | 122.9004 | 122.8455 | 122.8638 | -122.8729 | -122.8592 | 122.5433 | 0.51727 | 7.0908 | 2.2064
4335.1719 | 122.9736 | -49.7589 | 73.0637 | -0.075836 | -0.00044654 | 0.067793 | 0.075667 | -0.0034714 | 0.0028327 | 0.0077716 | 0.016968 | 0.0015295 | 0.0025634 | -0.0010084 | -0.0023605 | -0.0075025 | 0.00045294 | -42.6773 | 73.114 | -49.8367 | 72.7661 | -42.3706 | -49.6216 | -48.8525 | -47.5708 | 73.1186 | -49.791 | -49.2325 | -49.4751 | -49.8413 | -49.5438 | -0.07782 | 0.050354 | -0.29755 | 7.3883 | 0.90637 | 0.13733 | 0.98419 | 0.21515 | -0.032044 | 0.054931 | -122.2961 | 0.28381 | 0.21515 | -0.082398 | 0.24719 | -0.050354 | 7.4661 | 122.6028 | 0.31586 | 0.55847 | 122.9507 | 122.9095 | 122.8729 | 122.8775 | -122.9004 | -122.8546 | 122.525 | 0.52643 | 7.0816 | 2.1881
4336.1719 | 122.9416 | -49.7726 | 73.0637 | -0.098725 | 0.0023307 | 0.068861 | 0.076095 | 0.0012284 | 0.0034735 | 0.0079852 | 0.016968 | 0.00046135 | 0.0014954 | 0.0015552 | -0.0027877 | -0.0055799 | -0.0023243 | -42.6132 | 73.0591 | -49.8276 | 72.7844 | -42.2607 | -49.6262 | -48.8388 | -47.5342 | 73.1003 | -49.8138 | -49.2188 | -49.4751 | -49.8276 | -49.5163 | -0.054932 | -0.004578 | -0.27924 | 7.5119 | 0.93384 | 0.14648 | 0.98877 | 0.20142 | -0.041199 | 0.036621 | -122.2824 | 0.29755 | 0.25635 | -0.054932 | 0.29755 | -0.013733 | 7.5668 | 122.612 | 0.33874 | 0.59509 | 122.8867 | 122.9141 | 122.8317 | 122.8729 | -122.8912 | -122.8775 | 122.5571 | 0.55389 | 7.1594 | 2.2385
4337.1719 | 122.9233 | -49.8047 | 73.0408 | -0.10635 | 0.0021171 | 0.06758 | 0.076095 | 0.0010148 | 0.0032599 | 0.0054218 | -0.025757 | 0.0030249 | 0.00064083 | 0.0013416 | -0.0030013 | -0.0070753 | 0.0023755 | -42.6224 | 73.0545 | -49.8505 | 72.7249 | -42.215 | -49.6948 | -48.8937 | -47.6074 | 73.0911 | -49.8001 | -49.2783 | -49.5621 | -49.9054 | -49.5987 | -0.045777 | 0.013733 | -0.31586 | 7.5897 | 0.91095 | 0.10986 | 0.95673 | 0.15564 | 0.004577 | 0.050354 | -122.319 | 0.24261 | 0.20599 | -0.10071 | 0.20142 | -0.10529 | 7.6355 | 122.5754 | 0.23804 | 0.52185 | 122.905 | 122.8912 | 122.8592 | 122.8958 | -122.8912 | -122.8409 | 122.5296 | 0.52643 | 7.1823 | 2.1973
4338.1719 | 122.9279 | -49.8138 | 73.0362 | -0.060578 | 0.0023307 | 0.070143 | 0.076736 | 0.0018692 | 0.0028327 | 0.007558 | -0.0043946 | 0.0013159 | 0.001709 | -0.001222 | -0.0042831 | -0.0070753 | -0.0016833 | -42.5766 | 73.0133 | -49.8642 | 72.7203 | -42.1417 | -49.6857 | -48.8937 | -47.612 | 73.0499 | -49.8322 | -49.2828 | -49.5529 | -49.9237 | -49.5941 | -0.050354 | -0.022888 | -0.31586 | 7.6721 | 0.9201 | 0.12817 | 0.97046 | 0.17853 | -0.01831 | 0.013733 | -122.319 | 0.26093 | 0.21973 | -0.10986 | 0.23804 | -0.091553 | 7.7225 | 122.5845 | 0.27924 | 0.54932 | 122.8775 | 122.8821 | 122.8271 | 122.8638 | -122.9004 | -122.8683 | 122.5342 | 0.53101 | 7.2372 | 2.2018
4339.1719 | 122.9141 | -49.8138 | 73.0179 | -0.091095 | 0.00019446 | 0.068007 | 0.076736 | 0.00058737 | 0.0019781 | 0.0081988 | -0.01355 | 0.0028113 | 0.0014954 | 0.0041186 | -0.0034287 | -0.0070753 | -0.00018806 | -42.572 | 73.0316 | -49.8413 | 72.7386 | -42.0502 | -49.6811 | -48.88 | -47.5937 | 73.0591 | -49.8322 | -49.2783 | -49.5483 | -49.9146 | -49.6033 | -0.027466 | 0.013733 | -0.27924 | 7.7637 | 0.93384 | 0.13275 | 0.9613 | 0.16022 | -0.01831 | 0.041199 | -122.2961 | 0.2655 | 0.21057 | -0.10071 | 0.22888 | -0.082398 | 7.7911 | 122.58 | 0.28381 | 0.55389 | 122.8729 | 122.8912 | 122.8455 | 122.8729 | -122.8592 | -122.85 | 122.5525 | 0.53558 | 7.2418 | 2.2202
4340.1719 | 122.9233 | -49.823 | 73.0179 | -0.091095 | 0.00062166 | 0.072066 | 0.076308 | -0.0017624 | 0.0021917 | 0.0084124 | -0.010498 | 0.0011023 | 0.00085443 | 0.0049732 | -0.0027877 | -0.0049389 | 0.00066654 | -42.5858 | 73.0041 | -49.8825 | 72.6746 | -42.0136 | -49.7406 | -48.9304 | -47.6761 | 73.027 | -49.8459 | -49.324 | -49.6033 | -49.9603 | -49.649 | -0.059509 | -0.013733 | -0.34332 | 7.8094 | 0.89264 | 0.082397 | 0.95215 | 0.14191 | -0.022888 | 0.009156 | -122.3419 | 0.21973 | 0.17395 | -0.13733 | 0.19684 | -0.11444 | 7.869 | 122.5571 | 0.24262 | 0.52185 | 122.8867 | 122.8729 | 122.8271 | 122.85 | -122.9004 | -122.8638 | 122.4976 | 0.49896 | 7.2372 | 2.1469
4341.1719 | 122.9507 | -49.8367 | 72.9904 | -0.068207 | 0.00062166 | 0.070143 | 0.07759 | 0.00037377 | 0.0021917 | 0.0062762 | -0.0013428 | 0.00024775 | 0.0012818 | -0.00036738 | -0.0025741 | -0.0077161 | 0.0021619 | -42.5171 | 73.0179 | -49.8505 | 72.7295 | -41.8716 | -49.6948 | -48.88 | -47.5983 | 73.0179 | -49.8642 | -49.2828 | -49.5529 | -49.91 | -49.617 | -0.013733 | 0.027466 | -0.26093 | 7.9651 | 0.95673 | 0.14191 | 0.97046 | 0.15564 | -0.027466 | 0.027466 | -122.2733 | 0.28381 | 0.21973 | -0.073242 | 0.24719 | -0.045776 | 7.9788 | 122.58 | 0.31128 | 0.58136 | 122.8683 | 122.8821 | 122.8546 | 122.8546 | -122.8409 | -122.8546 | 122.5662 | 0.55389 | 7.3196 | 2.2385
4342.1719 | 122.9691 | -49.823 | 72.9996 | -0.075836 | 0.00083526 | 0.06822 | 0.076095 | 0.0018692 | 0.00026909 | 0.0081988 | 0.02002 | 0.0017431 | 0.0036316 | -0.0020764 | -0.0012925 | -0.0062207 | -0.0036059 | -42.4576 | 73.0225 | -49.91 | 72.7249 | -41.7572 | -49.6628 | -48.8754 | -47.5891 | 73.0362 | -49.855 | -49.292 | -49.53 | -49.91 | -49.5987 | -0.086975 | 0.022888 | -0.27466 | 8.0658 | 0.94757 | 0.16022 | 1.0345 | 0.24719 | -0.032044 | 0.036621 | -122.2916 | 0.29297 | 0.2243 | -0.086975 | 0.25635 | -0.054931 | 8.1528 | 122.6349 | 0.32501 | 0.56305 | 122.9324 | 122.8912 | 122.8455 | 122.8592 | -122.9095 | -122.8546 | 122.5479 | 0.53101 | 7.3654 | 2.2339
4343.1719 | 122.9828 | -49.8413 | 72.9813 | -0.068207 | -0.0021555 | 0.070357 | 0.076308 | -0.0030442 | 0.0026191 | 0.0060626 | 0.0078126 | 0.00088875 | 0.0012818 | -0.00464 | -0.0025741 | -0.0077161 | 0.0032299 | -42.4301 | 73.0087 | -49.8779 | 72.702 | -41.6611 | -49.6902 | -48.8846 | -47.5983 | 73.0362 | -49.8734 | -49.3011 | -49.5575 | -49.9146 | -49.6124 | -0.036621 | 0.027466 | -0.27924 | 8.1802 | 0.95673 | 0.15106 | 0.99335 | 0.18768 | -0.032043 | 0.054932 | -122.2824 | 0.28381 | 0.22888 | -0.073242 | 0.26093 | -0.041199 | 8.2169 | 122.58 | 0.31586 | 0.5722 | 122.8867 | 122.9095 | 122.85 | 122.8775 | -122.8592 | -122.8546 | 122.5433 | 0.54016 | 7.4112 | 2.243
4344.1719 | 122.9782 | -49.8322 | 72.9813 | -0.098725 | 0.0021171 | 0.069716 | 0.078017 | 0.0029374 | 0.0032599 | 0.0090534 | -0.041016 | 0.0015295 | 0.00042723 | -0.00058098 | -0.0032151 | -0.0060071 | -0.00018806 | -42.421 | 72.9767 | -49.9146 | 72.6929 | -41.5558 | -49.7177 | -48.88 | -47.5479 | 73.0087 | -49.8779 | -49.2966 | -49.5667 | -49.9146 | -49.6124 | -0.082398 | -0.004577 | -0.28839 | 8.2764 | 0.95215 | 0.11444 | 1.0345 | 0.19684 | -0.045777 | 0.027466 | -122.2778 | 0.2655 | 0.21973 | -0.082398 | 0.2655 | -0.036621 | 8.3588 | 122.6074 | 0.31128 | 0.58136 | 122.8912 | 122.8867 | 122.8088 | 122.8409 | -122.8958 | -122.8592 | 122.525 | 0.53558 | 7.4112 | 2.2842
4345.1719 | 122.9645 | -49.8596 | 72.9401 | -0.068207 | -0.0019417 | 0.06822 | 0.078445 | 0.001442 | 0.0043281 | 0.0088398 | -0.016602 | 0.0030249 | 0.001709 | -0.0052808 | -0.0038559 | -0.0045117 | -0.0010425 | -42.3935 | 72.9446 | -49.9512 | 72.6837 | -41.4413 | -49.7131 | -48.8892 | -47.6212 | 72.9904 | -49.9008 | -49.3057 | -49.5667 | -49.9466 | -49.6628 | -0.091553 | 0.004578 | -0.25635 | 8.4183 | 0.97046 | 0.14648 | 1.062 | 0.23804 | -0.041199 | 0.050354 | -122.2458 | 0.29297 | 0.19684 | -0.086975 | 0.23804 | -0.045776 | 8.5098 | 122.6349 | 0.33417 | 0.59509 | 122.8958 | 122.8912 | 122.8043 | 122.85 | -122.8912 | -122.8409 | 122.5433 | 0.55389 | 7.4661 | 2.2385
4346.1719 | 122.9645 | -49.8917 | 72.9446 | -0.11398 | 0.0023307 | 0.071425 | 0.07994 | 0.0033646 | 0.0024053 | 0.0073444 | -0.028809 | 0.0011023 | 0.0012818 | -0.0025036 | -0.0012925 | -0.0060071 | -0.00018806 | -42.3569 | 72.9172 | -49.9374 | 72.6517 | -41.3635 | -49.7589 | -48.8937 | -47.6578 | 72.9721 | -49.9329 | -49.3744 | -49.6353 | -49.9924 | -49.6765 | -0.045776 | -0.027466 | -0.29297 | 8.5281 | 0.99793 | 0.13275 | 1.0437 | 0.17853 | -0.041198 | 0.027466 | -122.319 | 0.25635 | 0.21515 | -0.10071 | 0.25635 | -0.05951 | 8.5739 | 122.5891 | 0.29755 | 0.55847 | 122.8546 | 122.905 | 122.8088 | 122.8638 | -122.8821 | -122.8775 | 122.5433 | 0.51727 | 7.5348 | 2.2339
4347.1719 | 122.9279 | -49.9054 | 72.8943 | -0.10635 | -1.9142e-05 | 0.071852 | 0.07759 | 0.0020828 | 0.0028327 | 0.0086262 | -0.010498 | 0.00067495 | -0.0010682 | -0.0033582 | -0.0059921 | -0.0051527 | -0.0042469 | -42.3248 | 72.9355 | -49.9466 | 72.6425 | -41.2491 | -49.7589 | -48.8983 | -47.6807 | 72.9309 | -49.9191 | -49.3881 | -49.6353 | -49.9924 | -49.6902 | -0.041198 | 0.041199 | -0.25177 | 8.6563 | 1.0071 | 0.14649 | 1.0483 | 0.18768 | -0.013732 | 0.036621 | -122.2824 | 0.27008 | 0.21515 | -0.086975 | 0.22888 | -0.073243 | 8.6975 | 122.5891 | 0.28381 | 0.53101 | 122.8821 | 122.85 | 122.8409 | 122.8363 | -122.8409 | -122.8134 | 122.5479 | 0.51727 | 7.5806 | 2.2247
4348.1719 | 122.905 | -49.942 | 72.8714 | -0.068207 | 0.00019446 | 0.07292 | 0.079726 | 0.00080117 | 0.0021917 | 0.0056354 | -0.019653 | 0.0021703 | 0.0021362 | -0.0067762 | -0.0027877 | -0.0057935 | 0.0010937 | -42.3294 | 72.8897 | -49.9924 | 72.5739 | -41.185 | -49.8596 | -48.9716 | -47.7493 | 72.9263 | -49.9878 | -49.4522 | -49.7177 | -50.0977 | -49.7543 | -0.050354 | 0.01831 | -0.29755 | 8.757 | 0.97046 | 0.082398 | 1.0208 | 0.13275 | -0.045776 | 0.054932 | -122.3236 | 0.22431 | 0.18768 | -0.15564 | 0.23346 | -0.10986 | 8.8074 | 122.5662 | 0.27008 | 0.53558 | 122.8821 | 122.9141 | 122.8317 | 122.8683 | -122.8638 | -122.8592 | 122.5159 | 0.48981 | 7.6126 | 2.1927
4349.1719 | 122.9507 | -49.9603 | 72.8577 | -0.060578 | -1.9142e-05 | 0.071425 | 0.078658 | -0.0013352 | 0.0026191 | 0.005849 | 0.0047608 | 0.00046135 | 0.001709 | -0.0031446 | -0.0027877 | -0.0060071 | -0.0023243 | -42.2516 | 72.8851 | -50.0153 | 72.583 | -41.0202 | -49.8001 | -48.9304 | -47.699 | 72.9034 | -49.9832 | -49.4156 | -49.6719 | -50.029 | -49.7223 | -0.054932 | 0.027466 | -0.27466 | 8.9401 | 1.03 | 0.16022 | 1.0849 | 0.21515 | -0.022888 | 0.045776 | -122.2733 | 0.28839 | 0.23804 | -0.068665 | 0.26093 | -0.045777 | 8.9951 | 122.5983 | 0.31128 | 0.56763 | 122.9004 | 122.8867 | 122.8455 | 122.8638 | -122.8729 | -122.8409 | 122.5433 | 0.54474 | 7.7087 | 2.2614
4350.1719 | 122.9691 | -49.9786 | 72.8485 | -0.068207 | -0.00087374 | 0.07057 | 0.079085 | 0.0035782 | 5.5488e-05 | 0.0079852 | 0.0078126 | 0.0019567 | -0.0014954 | -0.00079478 | -0.0023605 | -0.0066479 | 0.0047253 | -42.2104 | 72.8485 | -50.0198 | 72.5693 | -40.8875 | -49.8138 | -48.9441 | -47.7402 | 72.8668 | -50.0153 | -49.4431 | -49.6902 | -50.061 | -49.7681 | -0.041198 | 0 | -0.27924 | 9.0912 | 1.0345 | 0.16479 | 1.0757 | 0.20599 | -0.036621 | 0.01831 | -122.2916 | 0.28839 | 0.21057 | -0.082397 | 0.24719 | -0.045776 | 9.1324 | 122.5891 | 0.32501 | 0.57221 | 122.8683 | 122.8821 | 122.8271 | 122.8455 | -122.8683 | -122.8638 | 122.5479 | 0.53558 | 7.7682 | 2.2385
4351.1719 | 122.9507 | -49.9969 | 72.8027 | -0.091095 | 0.00083526 | 0.07057 | 0.079299 | -0.0032578 | 0.0034735 | 0.0084124 | 0.02002 | 0.0019567 | -0.00085457 | -0.00229 | -0.0044967 | -0.0057935 | 0.0015209 | -42.1967 | 72.789 | -50.0748 | 72.464 | -40.8188 | -49.8413 | -48.9075 | -47.7722 | 72.8531 | -50.0702 | -49.4522 | -49.7589 | -50.1022 | -49.7955 | -0.07782 | -0.013733 | -0.33875 | 9.1782 | 1.0895 | 0.15564 | 1.1673 | 0.23346 | -0.073242 | 0.050354 | -122.2549 | 0.23804 | 0.20142 | -0.10529 | 0.27466 | -0.032044 | 9.256 | 122.5388 | 0.31128 | 0.61798 | 122.8638 | 122.9233 | 122.7859 | 122.85 | -122.8775 | -122.8729 | 122.4609 | 0.54474 | 7.8003 | 2.2247
4352.1719 | 122.9324 | -50.061 | 72.757 | -0.03006 | 0.00062166 | 0.072279 | 0.080154 | 0.0035782 | 0.00069649 | 0.0060626 | -0.010498 | 0.0019567 | 0.0023498 | -0.00058098 | -0.0032151 | -0.0053663 | -0.0012561 | -42.1371 | 72.7798 | -50.1205 | 72.5006 | -40.6036 | -49.91 | -48.999 | -47.8363 | 72.8073 | -50.0839 | -49.5255 | -49.8047 | -50.1663 | -49.8459 | -0.059509 | 0.022888 | -0.25635 | 9.4574 | 1.062 | 0.15106 | 1.1215 | 0.21057 | -0.022888 | 0.050354 | -122.2824 | 0.25635 | 0.21515 | -0.10529 | 0.23804 | -0.082398 | 9.5169 | 122.6212 | 0.27924 | 0.55847 | 122.9004 | 122.8912 | 122.8409 | 122.8683 | -122.8775 | -122.8409 | 122.5616 | 0.53558 | 7.9239 | 2.2247
4353.1719 | 122.9645 | -50.0839 | 72.7341 | -0.075836 | -0.00066014 | 0.07057 | 0.080154 | -0.00026703 | 0.0028327 | 0.0073444 | -0.028809 | 0.0011023 | 0.00064083 | 0.0017688 | -0.0036423 | -0.0053663 | -0.0025379 | -42.0868 | 72.7478 | -50.1434 | 72.4777 | -40.4251 | -49.9237 | -49.0173 | -47.8455 | 72.7936 | -50.1434 | -49.5529 | -49.8459 | -50.1892 | -49.8688 | -0.05951 | 0.013733 | -0.25635 | 9.6588 | 1.0666 | 0.16022 | 1.1261 | 0.21973 | -0.05951 | 0.059509 | -122.287 | 0.23804 | 0.21515 | -0.10529 | 0.27466 | -0.045776 | 9.7183 | 122.6212 | 0.29755 | 0.59052 | 122.8912 | 122.937 | 122.8317 | 122.8775 | -122.8775 | -122.8775 | 122.5616 | 0.53101 | 7.9971 | 2.2385
4354.1719 | 122.9553 | -50.1068 | 72.702 | -0.075836 | 0.0021171 | 0.072707 | 0.080154 | 0.0010148 | 0.0015509 | 0.0077716 | -0.016602 | 0.0019567 | 0.0023498 | 0.0060412 | -0.00065151 | -0.0072889 | 0.0015209 | -42.0181 | 72.7066 | -50.1572 | 72.4091 | -40.2145 | -49.9786 | -49.0356 | -47.8775 | 72.7478 | -50.1526 | -49.5758 | -49.855 | -50.2167 | -49.9008 | -0.050354 | 0.004578 | -0.29297 | 9.8923 | 1.0712 | 0.12817 | 1.1215 | 0.17853 | -0.045776 | 0.045777 | -122.2778 | 0.25177 | 0.20599 | -0.10986 | 0.25177 | -0.064087 | 9.9426 | 122.5662 | 0.29755 | 0.57678 | 122.8638 | 122.9004 | 122.8134 | 122.8546 | -122.8592 | -122.8546 | 122.5159 | 0.53101 | 8.0887 | 2.2293
4355.1719 | 122.9691 | -50.1755 | 72.6471 | -0.098725 | -0.00044654 | 0.072066 | 0.079299 | 0.0040054 | 0.0024053 | 0.0071308 | 0.010864 | 0.0036657 | 0.00085443 | -0.0048536 | -0.0017197 | -0.0068615 | 0.0023755 | -41.9174 | 72.6471 | -50.235 | 72.3633 | -39.9353 | -50.0015 | -49.054 | -47.937 | 72.6837 | -50.2029 | -49.6445 | -49.9054 | -50.2487 | -49.9329 | -0.059509 | 0 | -0.28381 | 10.2402 | 1.1215 | 0.17395 | 1.181 | 0.23346 | -0.027466 | 0.036621 | -122.2916 | 0.27008 | 0.24262 | -0.073242 | 0.27008 | -0.045776 | 10.2997 | 122.5983 | 0.29755 | 0.55847 | 122.8821 | 122.8867 | 122.8226 | 122.8592 | -122.8821 | -122.85 | 122.5388 | 0.53101 | 8.2581 | 2.2385
4356.1719 | 122.9599 | -50.2945 | 72.5235 | -0.03006 | 0.00019446 | 0.073775 | 0.081435 | 0.00037377 | 0.0017645 | 0.012044 | -0.0043946 | 0.0030249 | 0.0036316 | -0.00079478 | -0.0034287 | -0.0062207 | -0.00082886 | -41.7847 | 72.5235 | -50.3494 | 72.226 | -39.5554 | -50.0061 | -49.1226 | -48.0194 | 72.5784 | -50.3357 | -49.7543 | -50.0244 | -50.3815 | -50.0748 | -0.054931 | 0 | -0.29755 | 10.7391 | 1.1719 | 0.28839 | 1.2268 | 0.34332 | -0.041198 | 0.054931 | -122.2778 | 0.27008 | 0.21973 | -0.086975 | 0.26093 | -0.045777 | 10.7941 | 122.5754 | 0.31128 | 0.58136 | 122.8729 | 122.9141 | 122.818 | 122.8729 | -122.8729 | -122.8592 | 122.5204 | 0.54016 | 8.5098 | 2.2751
4357.1719 | 122.9645 | -52.7664 | 70.0333 | -0.1445 | 0.0019035 | 0.08531 | 0.099593 | 0.001442 | 0.0043281 | 0.013539 | 0.016968 | 0.00046135 | -0.00021357 | 0.0028368 | -0.0034287 | -0.0051527 | 0.0017345 | -38.8458 | 70.0699 | -52.8122 | 69.7678 | -30.5374 | -52.4139 | -50.9033 | -50.4272 | 70.1019 | -52.7893 | -52.1896 | -52.4689 | -52.8305 | -52.5146 | -0.045777 | 0.036621 | -0.2655 | 22.229 | 1.8631 | 0.35248 | 1.9089 | 0.39826 | -0.022889 | 0.068665 | -122.2229 | 0.29755 | 0.25177 | -0.064087 | 0.27466 | -0.041198 | 22.2748 | 122.58 | 0.32044 | 0.59967 | 122.8821 | 122.8912 | 122.8363 | 122.8683 | -122.8455 | -122.8226 | 122.5342 | 0.57678 | 13.9206 | 2.3392
4358.1719 | 122.9507 | -55.8243 | 67.0212 | -0.18265 | -0.00023294 | 0.10945 | 0.13377 | 0.0050736 | 0.0036871 | 0.017385 | -0.025757 | 0.00088875 | 0.0021362 | -0.00079478 | -0.0027877 | -0.0064343 | -0.00061526 | -35.6644 | 67.0166 | -55.8609 | 66.7099 | -16.1224 | -55.307 | -52.9358 | -53.334 | 67.0441 | -55.8105 | -55.1834 | -55.5176 | -55.8975 | -55.545 | -0.036621 | -0.004577 | -0.31128 | 39.7018 | 2.8885 | 0.51727 | 2.9251 | 0.55389 | 0.013733 | 0.022888 | -122.2046 | 0.3067 | 0.27924 | -0.073242 | 0.2655 | -0.086975 | 39.7385 | 122.5708 | 0.29297 | 0.62714 | 122.8775 | 122.8546 | 122.8409 | 122.8683 | -122.8821 | -122.8317 | 122.5342 | 0.64087 | 20.1599 | 2.4902
4359.1719 | 122.9691 | -55.8517 | 66.9388 | -0.13687 | -0.00023294 | 0.11265 | 0.1374 | -0.00090783 | 0.0051825 | 0.017385 | 0.013916 | -0.00017945 | 0.0019226 | 0.0041186 | -0.0038559 | -0.0055799 | 0.00045294 | -35.6415 | 66.9388 | -55.8792 | 66.7145 | -14.2181 | -55.2887 | -52.7573 | -53.3112 | 67.012 | -55.9021 | -55.1788 | -55.5038 | -55.9113 | -55.5679 | -0.027465 | 0 | -0.2243 | 41.6336 | 3.0945 | 0.56305 | 3.1219 | 0.59051 | -0.050354 | 0.073242 | -122.1176 | 0.3479 | 0.28381 | -0.059509 | 0.33417 | -0.009155 | 41.6611 | 122.5937 | 0.39825 | 0.72327 | 122.818 | 122.9141 | 122.7905 | 122.8638 | -122.818 | -122.8409 | 122.5662 | 0.67291 | 20.2103 | 2.5406
4360.1719 | 122.9782 | -55.8701 | 66.9159 | -0.13687 | 0.00040806 | 0.11458 | 0.1404 | 0.00016017 | 0.0051825 | 0.019094 | 0.032227 | 3.4148e-05 | 0.0019226 | 0.0034778 | -0.0038559 | -0.0060071 | 0.00088014 | -35.614 | 66.9434 | -55.9113 | 66.6779 | -12.7853 | -55.3574 | -52.739 | -53.2974 | 66.9754 | -55.8701 | -55.1926 | -55.5359 | -55.9067 | -55.5725 | -0.041199 | 0.027465 | -0.23804 | 43.0847 | 3.1311 | 0.5127 | 3.1723 | 0.55389 | 0 | 0.059509 | -122.1085 | 0.33417 | 0.29755 | -0.036621 | 0.29755 | -0.036621 | 43.1259 | 122.5891 | 0.33417 | 0.67749 | 122.8546 | 122.8455 | 122.8134 | 122.8455 | -122.8271 | -122.7859 | 122.5479 | 0.67749 | 20.256 | 2.5726
4361.1719 | 122.9645 | -55.8472 | 66.9388 | -0.12924 | -0.0013009 | 0.11735 | 0.14232 | 0.0027238 | 0.0041143 | 0.021657 | -0.019653 | 0.00046135 | 0.0019226 | -0.0035718 | -0.0027877 | -0.0064343 | 0.00045294 | -35.6552 | 66.9617 | -55.8884 | 66.6733 | -11.618 | -55.2933 | -52.5421 | -53.334 | 66.9571 | -55.9067 | -55.2429 | -55.6046 | -55.8334 | -55.5313 | -0.041199 | 0.022888 | -0.2655 | 44.2291 | 3.3051 | 0.55389 | 3.3463 | 0.59509 | -0.059509 | 0.01831 | -122.1817 | 0.24262 | 0.31586 | 0.013733 | 0.37537 | 0.073242 | 44.2703 | 122.5616 | 0.30212 | 0.66376 | 122.85 | 122.8638 | 122.8088 | 122.8043 | -122.8271 | -122.8455 | 122.5204 | 0.60425 | 20.192 | 2.5131
4362.1719 | 122.9828 | -55.8792 | 66.9388 | -0.13687 | -0.00023294 | 0.12077 | 0.14744 | 0.0046464 | 0.0036871 | 0.020803 | 0.0047608 | 0.00024775 | 0.0014954 | 0.00027342 | -0.0017197 | -0.0077161 | 0.00066654 | -35.6918 | 66.9159 | -55.8975 | 66.6733 | -10.4279 | -55.3024 | -52.4323 | -53.3249 | 66.9846 | -55.9158 | -55.22 | -55.5176 | -55.9067 | -55.5771 | -0.018311 | -0.022888 | -0.2655 | 45.4514 | 3.447 | 0.57678 | 3.4653 | 0.59509 | -0.036622 | 0.045776 | -122.1588 | 0.36163 | 0.30212 | -0.027466 | 0.33875 | 0.009156 | 45.4697 | 122.5708 | 0.39825 | 0.6958 | 122.8134 | 122.9004 | 122.7951 | 122.8638 | -122.8363 | -122.8546 | 122.5525 | 0.65918 | 20.1874 | 2.5543
4363.1719 | 122.9233 | -55.751 | 67.0532 | -0.12924 | 0.0036125 | 0.1291 | 0.15535 | 0.004219 | 0.0024053 | 0.022512 | 0.02002 | 0.0025975 | 0.001709 | -0.0042126 | -0.0027877 | -0.0066479 | -0.0027515 | -35.9573 | 67.0807 | -55.7922 | 66.7511 | -9.8328 | -55.2155 | -52.3041 | -53.2745 | 67.0898 | -55.7831 | -55.1285 | -55.4214 | -55.8243 | -55.4947 | -0.041198 | 0.027465 | -0.30212 | 45.9183 | 3.447 | 0.53558 | 3.4882 | 0.57678 | -0.032043 | 0.036621 | -122.1817 | 0.32959 | 0.25635 | -0.073242 | 0.28839 | -0.041199 | 45.9595 | 122.5433 | 0.36163 | 0.6546 | 122.8729 | 122.8729 | 122.8317 | 122.8409 | -122.8455 | -122.8363 | 122.5021 | 0.62256 | 19.7937 | 2.4765
4364.1719 | 122.9416 | -52.6016 | 70.2072 | -0.28946 | 0.0014761 | 0.32243 | 0.33693 | -0.0017624 | 0.0019781 | 0.012471 | -0.0013428 | 3.4148e-05 | 0.0021362 | 0.0015552 | -0.0025741 | -0.0062207 | 0.00045294 | -41.1026 | 70.1935 | -52.7115 | 69.8959 | -34.0485 | -52.2537 | -50.5096 | -50.2487 | 70.253 | -52.6062 | -52.0065 | -52.272 | -52.6474 | -52.3315 | -0.10986 | -0.013733 | -0.31128 | 18.5532 | 2.092 | 0.3479 | 2.2018 | 0.45776 | -0.004577 | 0.045777 | -122.2137 | 0.32959 | 0.27008 | -0.045776 | 0.27466 | -0.041199 | 18.663 | 122.6074 | 0.33417 | 0.59967 | 122.905 | 122.8592 | 122.7951 | 122.8546 | -122.9187 | -122.8134 | 122.4976 | 0.59509 | 11.499 | 2.3529
4365.1719 | 122.905 | -53.8055 | 68.9529 | -0.30472 | 0.00083526 | 0.2812 | 0.30125 | -0.0011214 | 0.0041143 | 0.014394 | 0.0078126 | 0.00088875 | 0.0025634 | -0.00058098 | -0.0015061 | -0.0066479 | 0.0013073 | -39.5508 | 68.9896 | -53.9246 | 68.6371 | -27.0676 | -53.4485 | -51.2192 | -51.4435 | 69.0216 | -53.8422 | -53.215 | -53.54 | -53.92 | -53.5721 | -0.11902 | 0.036621 | -0.31586 | 26.738 | 2.5864 | 0.35706 | 2.7054 | 0.47607 | -0.036621 | 0.068664 | -122.168 | 0.2655 | 0.23346 | -0.11444 | 0.27008 | -0.07782 | 26.857 | 122.5616 | 0.30212 | 0.62714 | 122.9141 | 122.8638 | 122.7951 | 122.8271 | -122.8775 | -122.7951 | 122.4426 | 0.59052 | 14.2548 | 2.3621
4366.1719 | 122.905 | -52.5375 | 70.2164 | -0.42679 | -0.0021555 | 0.38246 | 0.39632 | 0.003151 | 0.0028327 | 0.01888 | -0.010498 | 0.0015295 | 0.0012818 | 0.002196 | -0.0032151 | -0.0068615 | 0.0019483 | -41.5466 | 70.2118 | -52.6474 | 69.9005 | -35.7697 | -52.066 | -50.4135 | -50.1526 | 70.2759 | -52.565 | -51.9287 | -52.2354 | -52.597 | -52.2949 | -0.10986 | -0.004578 | -0.31586 | 16.7679 | 2.124 | 0.4715 | 2.2339 | 0.58136 | -0.027465 | 0.059509 | -122.1451 | 0.30212 | 0.24262 | -0.059509 | 0.27008 | -0.032044 | 16.8777 | 122.5479 | 0.32959 | 0.63629 | 122.8592 | 122.8409 | 122.7493 | 122.8134 | -122.8638 | -122.7814 | 122.4381 | 0.60883 | 10.9909 | 2.3849
4367.1719 | 122.9233 | -52.3224 | 70.4178 | -0.38864 | 0.0012625 | 0.41963 | 0.43455 | 0.0020828 | 0.0032599 | 0.013112 | 0.0078126 | -0.00017945 | 0.001068 | -0.0016492 | -0.0034287 | -0.0075025 | -0.0016833 | -41.9083 | 70.3995 | -52.4323 | 70.1111 | -37.0697 | -52.0157 | -50.2533 | -50.0015 | 70.459 | -52.3636 | -51.7593 | -52.0111 | -52.3819 | -52.0935 | -0.10986 | -0.018311 | -0.3067 | 15.2527 | 2.0691 | 0.3067 | 2.179 | 0.41656 | -0.041198 | 0.041198 | -122.1771 | 0.31128 | 0.22888 | -0.059509 | 0.27008 | -0.018311 | 15.3625 | 122.5433 | 0.35248 | 0.60425 | 122.8317 | 122.8226 | 122.7219 | 122.7814 | -122.85 | -122.7814 | 122.4335 | 0.56305 | 10.4141 | 2.3209
4368.1719 | 122.9279 | -51.4938 | 71.2646 | -0.39627 | -1.9142e-05 | 0.37627 | 0.38927 | -0.00090783 | 0.0032599 | 0.010121 | 0.016968 | 0.0017431 | 0.0012818 | -0.0016492 | -0.0025741 | -0.0051527 | -0.00018806 | -42.3065 | 71.2418 | -51.5808 | 70.9625 | -38.8367 | -51.1917 | -49.6445 | -49.1776 | 71.3379 | -51.503 | -50.8987 | -51.1871 | -51.5488 | -51.2466 | -0.086976 | -0.022888 | -0.30212 | 12.6572 | 1.8494 | 0.30212 | 1.9363 | 0.3891 | -0.009156 | 0.073243 | -122.1634 | 0.3067 | 0.24719 | -0.054932 | 0.25635 | -0.045776 | 12.7441 | 122.5433 | 0.31586 | 0.60425 | 122.8226 | 122.8409 | 122.7356 | 122.8317 | -122.8455 | -122.7676 | 122.4564 | 0.59509 | 9.1873 | 2.3163
4369.1719 | 122.8912 | -51.7181 | 71.0449 | -0.4039 | -0.00044654 | 0.41023 | 0.42323 | 0.0033646 | 0.0024053 | 0.011403 | -0.01355 | 0.0011023 | 0.001709 | 0.0028368 | -0.0038559 | -0.0040845 | 0.0010937 | -42.2379 | 71.0449 | -51.8188 | 70.7153 | -38.324 | -51.4206 | -49.6628 | -49.4202 | 71.0724 | -51.7319 | -51.1276 | -51.4069 | -51.7731 | -51.4893 | -0.10071 | 0 | -0.32959 | 13.3942 | 2.0554 | 0.29755 | 2.1561 | 0.39826 | -0.013733 | 0.027466 | -122.1725 | 0.31128 | 0.22888 | -0.054931 | 0.24262 | -0.041198 | 13.4949 | 122.5342 | 0.32501 | 0.60425 | 122.8638 | 122.8043 | 122.7631 | 122.7905 | -122.8638 | -122.7768 | 122.4335 | 0.59051 | 9.4803 | 2.298
4370.1719 | 122.9507 | -51.6815 | 70.9808 | -0.51071 | 0.0016899 | 0.43864 | 0.44801 | 0.0016556 | 0.0045417 | 0.018026 | 0.026123 | -0.0016749 | 0.0021362 | -0.0072034 | -0.0025741 | -0.0055799 | -0.0021107 | -42.2928 | 70.9625 | -51.7914 | 70.7794 | -38.4933 | -51.3886 | -49.6628 | -49.324 | 70.9946 | -51.7227 | -51.1002 | -51.1826 | -51.6037 | -51.384 | -0.10986 | -0.018311 | -0.20142 | 13.1882 | 2.0187 | 0.29297 | 2.1286 | 0.40283 | -0.041198 | 0.013733 | -122.081 | 0.49896 | 0.29755 | 0.07782 | 0.33875 | 0.11902 | 13.298 | 122.5708 | 0.54016 | 0.62256 | 122.7539 | 122.7173 | 122.644 | 122.6761 | -122.7722 | -122.7036 | 122.4609 | 0.58136 | 9.3887 | 2.3575
4371.1719 | 122.8455 | -51.5167 | 71.2234 | -0.41153 | 0.00040806 | 0.44441 | 0.45827 | -0.00069423 | 0.0013373 | 0.012685 | 0.0078126 | 0.0011023 | 0.002777 | -0.0072034 | -0.0032151 | -0.0066479 | -0.0027515 | -42.4255 | 71.2097 | -51.6312 | 70.8572 | -38.9511 | -51.2604 | -49.5438 | -49.2599 | 71.2601 | -51.5533 | -50.9766 | -51.2329 | -51.6083 | -51.2924 | -0.11444 | -0.013733 | -0.36621 | 12.5656 | 1.973 | 0.25635 | 2.0874 | 0.37079 | -0.036621 | 0.036621 | -122.2 | 0.28381 | 0.22431 | -0.091552 | 0.26093 | -0.054931 | 12.6801 | 122.4884 | 0.32044 | 0.57678 | 122.8409 | 122.8134 | 122.7264 | 122.7768 | -122.8546 | -122.7768 | 122.374 | 0.54016 | 9.0912 | 2.2568
4372.1719 | 122.8821 | -51.5396 | 71.196 | -0.46494 | 0.0016899 | 0.47539 | 0.48646 | -0.0011214 | 0.0036871 | 0.014394 | 0.0047608 | 0.0017431 | 0.00085443 | -0.003999 | -0.0049241 | -0.0079297 | -0.0021107 | -42.3569 | 71.1777 | -51.6129 | 70.871 | -38.6307 | -51.2375 | -49.4156 | -49.2279 | 71.2326 | -51.5717 | -50.9537 | -51.2238 | -51.59 | -51.2833 | -0.073242 | -0.018311 | -0.32501 | 12.9089 | 2.124 | 0.30212 | 2.1973 | 0.37537 | -0.032043 | 0.036621 | -122.1497 | 0.31586 | 0.25635 | -0.050354 | 0.28839 | -0.018311 | 12.9822 | 122.4838 | 0.3479 | 0.61798 | 122.7905 | 122.8043 | 122.7173 | 122.7722 | -122.8088 | -122.7676 | 122.4106 | 0.58594 | 9.1827 | 2.3117
4373.1719 | 122.8409 | -51.7731 | 70.9213 | -0.52597 | 0.0019035 | 0.52452 | 0.54051 | -0.0017624 | 0.0036871 | 0.015462 | -0.0074462 | 0.0019567 | 0.00085443 | -0.00229 | -0.00022431 | -0.0087843 | -0.0010425 | -42.2104 | 70.9259 | -51.8692 | 70.6329 | -37.8799 | -51.4435 | -49.4659 | -49.4522 | 70.9946 | -51.7868 | -51.1917 | -51.4435 | -51.828 | -51.535 | -0.096131 | 0.004577 | -0.28839 | 13.8931 | 2.3071 | 0.32959 | 2.4033 | 0.42572 | -0.013733 | 0.073242 | -122.113 | 0.32959 | 0.23804 | -0.054932 | 0.25177 | -0.041199 | 13.9893 | 122.5021 | 0.34332 | 0.59509 | 122.7951 | 122.7814 | 122.699 | 122.7676 | -122.7905 | -122.7081 | 122.406 | 0.58136 | 9.5627 | 2.3209
4374.1719 | 122.8592 | -51.5442 | 71.1594 | -0.55649 | 0.00019446 | 0.53499 | 0.55226 | -0.0024032 | 0.0015509 | 0.017385 | -0.0013428 | 0.0023839 | -0.00042717 | 0.00027342 | -0.00086511 | -0.0057935 | -0.00018806 | -42.3019 | 71.1365 | -51.6449 | 70.8206 | -38.0859 | -51.265 | -49.2462 | -49.2508 | 71.1914 | -51.6083 | -50.9903 | -51.2421 | -51.6266 | -51.3245 | -0.10071 | -0.022888 | -0.33875 | 13.4583 | 2.298 | 0.27923 | 2.3987 | 0.37994 | -0.064087 | 0.032043 | -122.1497 | 0.30212 | 0.21973 | -0.082398 | 0.28381 | -0.018311 | 13.559 | 122.4655 | 0.36621 | 0.61798 | 122.7814 | 122.7997 | 122.6807 | 122.7356 | -122.8043 | -122.7676 | 122.3648 | 0.55389 | 9.2422 | 2.2934
4375.1719 | 122.8729 | -51.1459 | 71.4661 | -0.58701 | 0.00083526 | 0.51597 | 0.52833 | -5.343e-05 | 0.0045417 | 0.016317 | -0.0013428 | -0.00060665 | 0.00064083 | -0.0010084 | -0.0036423 | -0.0079297 | -0.0012561 | -42.4118 | 71.4752 | -51.2833 | 71.2006 | -38.1409 | -50.9262 | -48.9029 | -48.8571 | 71.5118 | -51.2192 | -50.56 | -50.8255 | -51.1734 | -50.8759 | -0.13733 | 0.009156 | -0.2655 | 13.0051 | 2.243 | 0.21973 | 2.3804 | 0.35706 | -0.073242 | 0.045777 | -122.0261 | 0.32044 | 0.27008 | -0.027466 | 0.34332 | 0.045776 | 13.1424 | 122.4838 | 0.39368 | 0.65918 | 122.7585 | 122.731 | 122.6212 | 122.6578 | -122.7493 | -122.6852 | 122.3465 | 0.58594 | 8.7341 | 2.2888
4376.1719 | 122.8317 | -51.2604 | 71.3974 | -0.54886 | 0.0023307 | 0.56276 | 0.57661 | 0.0016556 | 0.0034735 | 0.017812 | 0.0078126 | 0.00067495 | 0.0029906 | -0.00079478 | -0.0023605 | -0.0051527 | -0.0021107 | -42.2699 | 71.3837 | -51.384 | 71.0495 | -37.2437 | -51.0178 | -48.7701 | -49.0219 | 71.4386 | -51.3245 | -50.7294 | -50.9766 | -51.3474 | -51.0498 | -0.1236 | -0.013733 | -0.3479 | 14.0167 | 2.4902 | 0.24262 | 2.6138 | 0.36621 | -0.064087 | 0.041199 | -122.1268 | 0.28381 | 0.21057 | -0.086975 | 0.27466 | -0.022888 | 14.1403 | 122.4335 | 0.3479 | 0.59509 | 122.7676 | 122.7631 | 122.644 | 122.699 | -122.7814 | -122.7219 | 122.3099 | 0.53101 | 8.9905 | 2.2385
4377.1719 | 122.7814 | -51.416 | 71.2692 | -0.62515 | 0.00019446 | 0.61574 | 0.63429 | 0.0027238 | 0.0026191 | 0.019094 | -0.041016 | 0.00088875 | 0.00064083 | 0.0026232 | -0.0032151 | -0.0072889 | 2.554e-05 | -42.2607 | 71.2921 | -51.4618 | 70.9076 | -36.6394 | -50.9079 | -48.3673 | -49.1638 | 71.315 | -51.4572 | -50.8896 | -51.1322 | -51.4984 | -51.2054 | -0.045776 | 0.022888 | -0.36163 | 14.7766 | 3.0487 | 0.50812 | 3.0945 | 0.55389 | -0.041198 | 0.045776 | -122.1588 | 0.28381 | 0.21057 | -0.082397 | 0.25177 | -0.041199 | 14.8224 | 122.3694 | 0.32501 | 0.56763 | 122.7539 | 122.7722 | 122.7081 | 122.731 | -122.731 | -122.7264 | 122.3236 | 0.52643 | 9.1553 | 2.2522
4378.1719 | 122.7814 | -51.5533 | 71.1136 | -0.6633 | -0.00066014 | 0.68153 | 0.69688 | -0.0021896 | 0.0011237 | 0.018239 | 0.010864 | 0.00046135 | 0.0014954 | -0.0018628 | -0.0038559 | -0.0053663 | 0.0036571 | -42.1921 | 71.0678 | -51.6357 | 70.752 | -36.1908 | -51.2741 | -48.587 | -49.2828 | 71.1594 | -51.5991 | -51.0178 | -51.2512 | -51.6312 | -51.3336 | -0.082397 | -0.045776 | -0.36163 | 15.3625 | 2.9663 | 0.27924 | 3.0487 | 0.36163 | -0.045776 | 0.045777 | -122.1313 | 0.30212 | 0.21973 | -0.07782 | 0.2655 | -0.032044 | 15.4449 | 122.3877 | 0.3479 | 0.58136 | 122.7036 | 122.7585 | 122.6212 | 122.7127 | -122.7493 | -122.7127 | 122.3053 | 0.53558 | 9.3613 | 2.2705
4379.1719 | 122.8043 | -51.4755 | 71.1914 | -0.793 | -0.00087374 | 0.75801 | 0.77891 | 0.00251 | 0.0019781 | 0.02123 | 0.001709 | 0.0030249 | 0.0029906 | 0.00070062 | -0.0027877 | -0.0055799 | 0.00045294 | -42.1417 | 71.1319 | -51.5579 | 70.8527 | -35.6552 | -51.1505 | -48.143 | -49.1638 | 71.2234 | -51.503 | -50.8759 | -51.1551 | -51.5442 | -51.2512 | -0.082397 | -0.059509 | -0.33875 | 15.8203 | 3.3325 | 0.32501 | 3.4149 | 0.40741 | -0.027466 | 0.032044 | -122.0673 | 0.32043 | 0.2243 | -0.068664 | 0.25177 | -0.041198 | 15.9027 | 122.4106 | 0.3479 | 0.62714 | 122.6898 | 122.7264 | 122.6074 | 122.699 | -122.7493 | -122.6944 | 122.3282 | 0.59967 | 9.3338 | 2.3117
4380.1719 | 122.7768 | -51.1688 | 71.4569 | -0.80063 | -1.9142e-05 | 0.75481 | 0.77635 | -0.0017624 | 0.0024053 | 0.022084 | -0.016602 | 0.0017431 | 0.001709 | 0.00070062 | -0.0032151 | -0.0064343 | -0.0023243 | -42.2791 | 71.4249 | -51.2833 | 71.1182 | -37.0926 | -50.8713 | -47.5204 | -48.8892 | 71.5347 | -51.2421 | -50.6104 | -50.8759 | -51.2421 | -50.9354 | -0.11444 | -0.032043 | -0.33875 | 14.0762 | 3.6484 | 0.29755 | 3.7628 | 0.41199 | -0.073242 | 0.07782 | -122.0673 | 0.29297 | 0.23346 | -0.073242 | 0.3067 | 0 | 14.1907 | 122.4014 | 0.36621 | 0.63171 | 122.7081 | 122.7768 | 122.5937 | 122.7036 | -122.7402 | -122.699 | 122.287 | 0.55847 | 8.8898 | 2.2797
4381.1719 | 122.7631 | -51.4984 | 71.1365 | -0.9761 | 0.00019446 | 0.93468 | 0.9528 | 0.0037918 | 0.0017645 | 0.028707 | 0.0078126 | 0.0017431 | 0.00021363 | 0.003905 | -0.0032151 | -0.0066479 | 0.0066479 | -42.0364 | 71.0724 | -51.5442 | 70.7428 | -34.4742 | -51.1459 | -46.9116 | -49.205 | 71.1548 | -51.535 | -50.9171 | -51.1597 | -51.5533 | -51.2466 | -0.045776 | -0.064087 | -0.39368 | 17.0242 | 4.5868 | 0.35248 | 4.6326 | 0.39825 | -0.036621 | 0.01831 | -122.0535 | 0.33874 | 0.25177 | -0.054932 | 0.28839 | -0.018311 | 17.07 | 122.287 | 0.37537 | 0.61798 | 122.6166 | 122.6898 | 122.5708 | 122.6532 | -122.6807 | -122.6715 | 122.2412 | 0.58136 | 9.462 | 2.2934
4382.1719 | 122.7448 | -51.5762 | 71.0266 | -1.0295 | -0.00044654 | 1.0656 | 1.0942 | -0.0017624 | 0.0032599 | 0.041951 | 0.0078126 | 0.0032385 | 0.00085443 | 0.0028368 | -0.0038559 | -0.0083569 | 0.0038709 | -42.0181 | 70.9671 | -51.622 | 70.6146 | -34.7855 | -51.2329 | -44.7006 | -49.292 | 71.0815 | -51.5945 | -51.0132 | -51.2833 | -51.6449 | -51.329 | -0.045776 | -0.059509 | -0.41199 | 16.7908 | 6.8756 | 0.34332 | 6.9214 | 0.3891 | -0.01831 | 0.054932 | -122.0398 | 0.29297 | 0.24719 | -0.068664 | 0.2655 | -0.050354 | 16.8365 | 122.2366 | 0.31128 | 0.58136 | 122.5891 | 122.6761 | 122.5433 | 122.6578 | -122.6486 | -122.6212 | 122.1909 | 0.56305 | 9.5581 | 2.2842
4383.1719 | 122.6944 | -51.1551 | 71.4386 | -1.0753 | 0.00083526 | 1.0065 | 1.112 | -0.0013352 | 0.0036871 | 0.10817 | -0.010498 | 0.0023839 | 0.001068 | 0.0026232 | -0.0012925 | -0.0068615 | 0.00023934 | -42.3203 | 71.3516 | -51.2375 | 71.022 | -37.0789 | -50.8118 | -49.3423 | -48.8892 | 71.4981 | -51.1734 | -50.6058 | -50.8667 | -51.2329 | -50.9262 | -0.082398 | -0.086975 | -0.41656 | 14.0762 | 1.8127 | 0.34332 | 1.8951 | 0.42572 | -0.018311 | 0.059509 | -122.0444 | 0.28839 | 0.22888 | -0.07782 | 0.24719 | -0.059509 | 14.1586 | 122.2595 | 0.3067 | 0.56763 | 122.5891 | 122.6715 | 122.5067 | 122.6532 | -122.6761 | -122.612 | 122.1771 | 0.54932 | 8.8348 | 2.2659
4384.1719 | 122.644 | -51.796 | 70.7977 | -1.4034 | -0.0010873 | 1.1504 | 1.4057 | 0.00080117 | 0.0041143 | 0.2575 | 0.044434 | 0.0028113 | 0.0029906 | -0.00015378 | -0.0032151 | -0.0042981 | -0.00082886 | -42.3431 | 70.7062 | -51.7822 | 70.3445 | -34.9228 | -51.3336 | -11.6547 | -49.4888 | 70.8389 | -51.8097 | -51.2604 | -51.4572 | -51.8692 | -51.5808 | 0.013732 | -0.091552 | -0.45319 | 16.8732 | 40.1413 | 0.46234 | 40.1276 | 0.44861 | -0.013733 | 0.041199 | -122.0581 | 0.33875 | 0.21515 | -0.073243 | 0.22888 | -0.05951 | 16.8594 | 122.1268 | 0.35248 | 0.54932 | 122.4884 | 122.6486 | 122.5021 | 122.6349 | -122.58 | -122.6074 | 122.1405 | 0.53558 | 9.4528 | 2.3071
4385.1719 | 122.6486 | -52.2034 | 70.3583 | -1.6551 | 0.0016899 | 1.3711 | 1.6488 | 0.00080117 | 0.0030463 | 0.28484 | 0.02002 | 0.0011023 | 0.0012818 | 0.001128 | -0.0012925 | -0.0060071 | 0.00045294 | -42.0319 | 70.1981 | -52.2354 | 69.873 | -32.7713 | -51.7731 | -6.1798 | -49.9054 | 70.3537 | -52.2675 | -51.6495 | -51.9196 | -52.2858 | -51.9928 | -0.032044 | -0.16022 | -0.48523 | 19.4321 | 46.0236 | 0.4303 | 46.0556 | 0.46234 | -0.064087 | -0.004577 | -122.0078 | 0.28381 | 0.21057 | -0.082398 | 0.27466 | -0.018311 | 19.4641 | 122.1085 | 0.3479 | 0.61798 | 122.4335 | 122.6212 | 122.4014 | 122.5571 | -122.5937 | -122.6257 | 122.0764 | 0.55389 | 10.1715 | 2.298
4386.1719 | 122.6074 | -51.9287 | 70.5872 | -1.5636 | -0.0017281 | 1.3401 | 1.6289 | 0.00080117 | 0.0028327 | 0.3062 | 0.03833 | 0.00088875 | 0.0014954 | 0.00091422 | -0.0023605 | -0.0068615 | 0.00023934 | -41.9312 | 70.4819 | -51.9562 | 70.1294 | -28.2944 | -51.5121 | -4.3213 | -49.6445 | 70.6421 | -51.9379 | -51.3748 | -51.6357 | -52.0065 | -51.6953 | -0.027466 | -0.10529 | -0.45776 | 23.6343 | 47.6074 | 0.41656 | 47.6349 | 0.44403 | -0.009155 | 0.054932 | -121.962 | 0.29297 | 0.23346 | -0.07782 | 0.24262 | -0.068665 | 23.6618 | 122.0856 | 0.30212 | 0.56305 | 122.438 | 122.58 | 122.4106 | 122.5708 | -122.5433 | -122.525 | 122.0581 | 0.55389 | 9.9976 | 2.2842
4387.1719 | 122.5388 | -53.0045 | 69.4656 | -1.6628 | -1.9142e-05 | 1.4487 | 1.7372 | -0.0021896 | 0.0034735 | 0.281 | -0.0074462 | 0.0013159 | 0.00021363 | 0.005614 | -0.0025741 | -0.0047253 | -0.0014697 | -40.567 | 69.2184 | -53.1509 | 68.9529 | -22.5952 | -52.6474 | -6.8756 | -50.6332 | 69.5343 | -53.0411 | -52.446 | -52.684 | -53.0685 | -52.7344 | -0.14648 | -0.24719 | -0.5127 | 30.4092 | 46.1288 | 0.35706 | 46.2753 | 0.50354 | -0.036621 | 0.068665 | -121.9116 | 0.32043 | 0.27008 | -0.064086 | 0.3067 | -0.027465 | 30.5557 | 122.1039 | 0.35706 | 0.59509 | 122.3694 | 122.5754 | 122.2229 | 122.5388 | -122.6166 | -122.5067 | 121.9574 | 0.55847 | 12.4374 | 2.3712
4388.1719 | 122.6212 | -55.957 | 66.5359 | -0.9761 | -0.00044654 | 0.93211 | 1.0498 | 0.001442 | -0.0016535 | 0.067372 | 0.0078126 | 0.00024775 | 0.0029906 | 0.0086048 | -0.0034287 | -0.0079297 | 0.00023934 | -9.2331 | 66.3574 | -56.0989 | 66.1285 | -9.8328 | 8.6288 | 26.001 | -53.3798 | 66.655 | -55.9387 | -55.2887 | -55.6503 | -56.0349 | -55.7098 | -0.14191 | -0.17853 | -0.40741 | 46.1243 | 81.958 | 64.5859 | 82.0999 | 64.7278 | 0.01831 | 0.11902 | -121.8246 | 0.3067 | 0.24719 | -0.07782 | 0.22888 | -0.09613 | 46.2662 | 122.2275 | 0.28839 | 0.65002 | 122.4564 | 122.5937 | 122.3145 | 122.612 | -122.6349 | -122.4747 | 122.0856 | 0.66833 | 46.7239 | 2.5772
4389.1719 | 122.6303 | -55.3391 | 67.1768 | -1.3118 | 0.00083526 | 1.373 | 1.4657 | 0.0018692 | -0.0025079 | 0.069722 | 0.013916 | 3.4148e-05 | 0.0019226 | -0.001222 | -0.0025741 | -0.0053663 | -0.0010425 | -10.7758 | 66.8976 | -55.5313 | 66.6458 | -13.179 | 7.3288 | 28.6011 | -52.9358 | 67.2043 | -55.426 | -54.7165 | -55.0049 | -55.3986 | -55.0323 | -0.19226 | -0.27924 | -0.53101 | 42.16 | 83.9401 | 62.6678 | 84.1324 | 62.8601 | -0.086975 | 0.027466 | -121.8933 | 0.33417 | 0.3067 | -0.05951 | 0.39368 | 0.027465 | 42.3523 | 122.1771 | 0.42114 | 0.70953 | 122.4289 | 122.6303 | 122.2366 | 122.5433 | -122.7081 | -122.6028 | 121.9849 | 0.62256 | 44.5633 | 2.4033
4390.1719 | 122.5204 | -53.6316 | 68.8522 | -2.0518 | 0.00019446 | 2.0607 | 2.135 | 0.00251 | -0.00015811 | 0.064168 | 0.035278 | 0.0015295 | -0.00042717 | -0.0048536 | -0.0021469 | -0.0066479 | -0.00082886 | -17.4545 | 68.3853 | -53.8147 | 68.1198 | -22.4625 | 0.50354 | 21.579 | -51.3886 | 68.7012 | -53.8055 | -53.0319 | -53.2791 | -53.6728 | -53.3981 | -0.18311 | -0.46692 | -0.73242 | 31.1691 | 75.2106 | 54.1351 | 75.3937 | 54.3182 | -0.17395 | -0.15106 | -121.8842 | 0.35248 | 0.23346 | -0.041199 | 0.40741 | 0.13275 | 31.3522 | 121.9345 | 0.52643 | 0.77362 | 122.2 | 122.5067 | 122.0169 | 122.3328 | -122.6669 | -122.6578 | 121.7514 | 0.59967 | 36.1771 | 2.243
4391.1719 | 122.4152 | -53.4531 | 68.9529 | -2.563 | 0.00062166 | 2.5191 | 2.2841 | -0.0015488 | -0.00079891 | 0.042806 | 0.047485 | 3.4148e-05 | 2.8e-08 | -0.0093396 | -0.0036423 | -0.0075025 | 0.0010937 | -17.2897 | 68.8843 | -53.2883 | 68.1381 | -18.6218 | 2.2293 | 0.6546 | -51.3519 | 68.6829 | -53.7781 | -52.8442 | -53.1189 | -53.4988 | -53.2059 | 0.16479 | -0.068665 | -0.81482 | 34.8312 | 54.1077 | 55.6824 | 53.9429 | 55.5176 | -0.32501 | -0.27008 | -121.7972 | 0.33417 | 0.24719 | -0.045776 | 0.5722 | 0.27924 | 34.6664 | 121.4264 | 0.65918 | 0.93384 | 122.1725 | 122.4609 | 122.3373 | 122.1359 | -122.2412 | -122.731 | 121.5912 | 0.60883 | 36.1633 | 2.1011
4392.1719 | 122.4426 | -52.9175 | 69.4702 | -3.036 | -1.9142e-05 | 3.0047 | 3.0365 | -0.00048063 | -0.0012261 | 0.053701 | 0.050537 | 0.00046135 | 0.0012818 | 0.0049732 | -0.0030013 | -0.0072889 | 0.00023934 | -18.7729 | 69.2734 | -52.739 | 68.8889 | -19.3359 | -1.3 | 15.0467 | -50.3403 | 69.5663 | -52.8946 | -52.3544 | -52.6199 | -52.9724 | -52.6749 | 0.17853 | -0.19684 | -0.58136 | 33.5815 | 67.9642 | 51.6174 | 67.7856 | 51.4389 | 0.022888 | 0.09613 | -121.8246 | 0.29755 | 0.24261 | -0.054932 | 0.21973 | -0.07782 | 33.403 | 121.6278 | 0.27466 | 0.54016 | 122.0123 | 122.4609 | 122.1909 | 122.4838 | -122.2092 | -122.3648 | 121.8063 | 0.56305 | 34.1446 | 2.5772
4393.1719 | 122.4701 | -52.7527 | 69.5847 | -3.0208 | -0.00044654 | 3.0107 | 3.0499 | -0.0011214 | -0.00079891 | 0.058614 | 0.016968 | 0.0025975 | 0.003418 | -0.00464 | -0.0021469 | -0.0075025 | 0.0030163 | -17.9214 | 69.3512 | -52.6154 | 68.9896 | -15.7425 | -0.737 | 17.1844 | -50.386 | 69.6579 | -52.739 | -52.1667 | -52.4414 | -52.8168 | -52.4918 | 0.13733 | -0.23346 | -0.59509 | 37.0102 | 69.9371 | 52.0157 | 69.7998 | 51.8784 | 0.013733 | 0.073242 | -121.7514 | 0.31128 | 0.26093 | -0.064086 | 0.24719 | -0.077819 | 36.8729 | 121.6049 | 0.29755 | 0.57221 | 121.9666 | 122.3969 | 122.1039 | 122.4106 | -122.2 | -122.3236 | 121.7422 | 0.58594 | 34.8312 | 2.3666
4394.1719 | 122.3419 | -53.5446 | 68.6417 | -5.6987 | -1.9142e-05 | 5.6566 | 5.7273 | 0.00037377 | -0.00015811 | 0.075917 | 0.0078126 | 0.0011023 | -0.00021357 | 0.0032642 | -0.00043791 | -0.0083569 | 0.00023934 | -15.4312 | 68.2251 | -53.1097 | 67.8131 | -0.73242 | 2.5085 | 38.6398 | -51.1414 | 68.7332 | -53.5355 | -52.9221 | -53.2059 | -53.5904 | -53.2928 | 0.43488 | -0.41656 | -0.82855 | 52.8122 | 92.1844 | 56.0532 | 91.7496 | 55.6183 | 0.009156 | 0.091552 | -121.5637 | 0.33875 | 0.25177 | -0.045776 | 0.24261 | -0.054932 | 52.3773 | 120.9229 | 0.32959 | 0.6134 | 121.3348 | 122.2687 | 121.7697 | 122.2778 | -121.7514 | -122.1771 | 121.3577 | 0.62256 | 38.1134 | 2.4033
4395.1719 | 122.3465 | -54.9179 | 67.2821 | -3.4328 | 0.0010489 | 3.2486 | 3.3398 | 0.00037377 | -0.0016535 | 0.081472 | 0.096313 | 0.0017431 | 0.0023498 | -0.00079478 | -0.0023605 | -0.0066479 | -0.0014697 | -10.8627 | 66.7603 | -55.0644 | 66.3895 | 17.4179 | 7.9788 | 38.4613 | -52.6566 | 67.1631 | -55.1102 | -54.3228 | -54.6066 | -55.0049 | -54.689 | -0.14648 | -0.52185 | -0.89264 | 72.3358 | 93.3792 | 62.8967 | 93.5257 | 63.0432 | -0.19226 | -0.11902 | -121.6049 | 0.31128 | 0.22888 | -0.086975 | 0.42114 | 0.10529 | 72.4823 | 121.4539 | 0.50354 | 0.78735 | 121.8246 | 122.2733 | 121.6782 | 122.081 | -122.3465 | -122.3923 | 121.3074 | 0.59509 | 44.0552 | 2.2614
4396.1719 | 122.2275 | -53.9658 | 68.2251 | -4.3178 | 0.0010489 | 4.4095 | 4.3298 | 0.0010148 | -0.0016535 | 0.075063 | 0.044434 | 0.0011023 | 0.00085443 | 0.0041186 | -0.0017197 | -0.0062207 | -0.0012561 | -13.1653 | 67.9276 | -53.6453 | 67.3599 | 9.8007 | 5.0354 | 40.0818 | -51.6266 | 68.1656 | -54.0665 | -53.4943 | -53.7369 | -53.9017 | -53.5538 | 0.32043 | -0.29755 | -0.86517 | 63.7665 | 94.0475 | 59.0012 | 93.7271 | 58.6807 | -0.10071 | -0.05951 | -121.7194 | 0.22888 | 0.41199 | 0.064087 | 0.5127 | 0.1648 | 63.446 | 121.0052 | 0.32959 | 0.5722 | 121.5729 | 122.2321 | 121.8933 | 122.1313 | -121.8704 | -122.2916 | 121.3257 | 0.4715 | 40.8005 | 2.3392
4397.1719 | 122.2 | -52.5192 | 69.4794 | -6.8355 | 0.00040806 | 6.736 | 6.8238 | 0.0012284 | 5.5488e-05 | 0.078694 | 0.041382 | -0.0014613 | 0.00064083 | -0.0020764 | -0.0015061 | -0.0072889 | -0.00082886 | -15.9256 | 68.898 | -52.0203 | 68.605 | 7.1915 | 1.5244 | 41.304 | -50.1068 | 69.5389 | -52.5375 | -51.8738 | -52.153 | -52.5284 | -52.2629 | 0.49896 | -0.58136 | -0.87433 | 59.7107 | 93.8232 | 54.0436 | 93.3243 | 53.5446 | -0.018311 | 0.059509 | -121.3531 | 0.36621 | 0.25635 | -0.009155 | 0.27466 | 0.009156 | 59.2117 | 120.6253 | 0.38452 | 0.66376 | 120.9183 | 122.0764 | 121.4172 | 122.0581 | -121.4996 | -122.0169 | 121.1243 | 0.64545 | 36.5936 | 2.4124
4398.1719 | 122.1725 | -52.3361 | 69.6533 | -6.4616 | 0.0014761 | 6.322 | 6.2938 | -0.0013352 | -0.00058531 | 0.076772 | 0.035278 | 0.0013159 | 0.0021362 | 0.0019824 | -0.0025741 | -0.0081433 | -0.0014697 | -15.6235 | 69.1086 | -51.9058 | 68.8202 | 12.7853 | 1.8723 | 41.1346 | -49.9695 | 69.635 | -52.4277 | -51.6586 | -51.9562 | -52.3315 | -52.0752 | 0.4303 | -0.54474 | -0.83313 | 65.1215 | 93.4708 | 54.2084 | 93.0405 | 53.7781 | -0.091552 | -0.01831 | -121.3119 | 0.37994 | 0.26093 | 0.004578 | 0.35248 | 0.09613 | 64.6912 | 120.726 | 0.4715 | 0.76904 | 121.0144 | 122.0627 | 121.4447 | 121.9711 | -121.5591 | -122.081 | 121.1563 | 0.67749 | 36.7126 | 2.3666
4399.1719 | 122.1085 | -51.86 | 70.015 | -6.6447 | 0.0046805 | 6.4694 | 6.4547 | -0.00026703 | -0.0020807 | 0.076772 | 0.035278 | 0.0019567 | 0.0014954 | -0.0016492 | -0.0040695 | -0.0075025 | -0.0031787 | -15.1291 | 69.4748 | -51.416 | 69.1818 | 13.3392 | 2.7878 | 43.6661 | -49.4659 | 70.0424 | -51.9196 | -51.2466 | -51.5213 | -51.8921 | -51.6037 | 0.44403 | -0.54016 | -0.83313 | 65.1993 | 95.5261 | 54.6478 | 95.0821 | 54.2038 | -0.05951 | 0.027465 | -121.2616 | 0.33874 | 0.25635 | -0.032044 | 0.31586 | 0.027466 | 64.7552 | 120.5978 | 0.39825 | 0.67291 | 120.8908 | 121.962 | 121.3348 | 121.9025 | -121.431 | -121.9345 | 121.0419 | 0.6134 | 36.731 | 2.3941
4400.1719 | 122.1222 | -51.3199 | 70.6055 | -6.515 | 0.0085257 | 6.3778 | 6.478 | -0.0032578 | 0.0013373 | 0.077626 | 0.032227 | 3.4148e-05 | 0.00085443 | -0.0035718 | -0.0049241 | -0.0064343 | -0.00061526 | -15.2847 | 70.079 | -50.8392 | 69.7357 | 4.4403 | 2.5131 | 39.4775 | -48.9578 | 70.6558 | -51.3153 | -50.679 | -50.9354 | -51.3107 | -51.059 | 0.48065 | -0.52643 | -0.86975 | 55.7602 | 90.7974 | 53.833 | 90.3168 | 53.3524 | 0.004577 | 0.050354 | -121.2845 | 0.38452 | 0.26093 | 0.009155 | 0.25635 | 0.004578 | 55.2795 | 120.575 | 0.37994 | 0.63629 | 120.9183 | 121.9711 | 121.3989 | 121.9757 | -121.4447 | -121.9208 | 121.0556 | 0.64087 | 36.0352 | 2.3621
4401.1719 | 121.788 | -50.9354 | 70.5185 | -15.8916 | 0.0072441 | 7.106 | 7.0024 | 0.0033646 | -0.0035761 | 0.072927 | 0.047485 | 0.0011023 | 0.0023498 | 0.0026232 | -0.0015061 | -0.0072889 | -0.0018971 | -15.5182 | 69.1177 | -49.6719 | 68.7424 | -0.022888 | 1.4923 | 38.4155 | -48.6191 | 70.5688 | -50.9674 | -50.3128 | -50.5508 | -50.9079 | -50.6516 | 1.2634 | -1.4008 | -1.7761 | 50.9125 | 89.3509 | 52.4277 | 88.0875 | 51.1642 | -0.032043 | 0.050354 | -120.8313 | 0.38452 | 0.28381 | 0.027466 | 0.31586 | 0.059509 | 49.649 | 118.4143 | 0.41656 | 0.6546 | 118.7897 | 121.5363 | 120.0531 | 121.5042 | -120.1904 | -121.4859 | 119.6777 | 0.62256 | 35.4172 | 2.3163
4402.1719 | 122.1542 | -38.0081 | 84.0042 | -0.098725 | -0.00087374 | 0.013106 | 0.010085 | -0.00069423 | -0.0046441 | -0.00098701 | 0.03833 | -0.00017945 | 0.0032044 | 0.0049732 | -0.0038559 | -0.0066479 | 0.00045294 | -36.7401 | -8.6838 | -38.1042 | -38.0905 | -38.2141 | -38.5208 | -38.2187 | -36.3281 | 84.0408 | -38.0264 | -37.5778 | -37.7335 | -37.999 | -37.8067 | -0.09613 | -92.688 | -122.0947 | -0.20599 | -0.21057 | -0.51269 | -0.11444 | -0.41656 | -0.01831 | 0.036622 | -121.582 | 0.27466 | 0.20142 | 0.009156 | 0.21973 | 0.027466 | -0.10986 | 0.013733 | 0.29297 | 0.44861 | 29.4205 | 122.0673 | 29.3243 | 122.049 | -122.1085 | -122.0306 | -0.082397 | 0.4303 | 1.268 | 1.68
4403.1719 | 122.3465 | -36.8683 | 85.2859 | -0.075836 | -0.0013009 | 0.013106 | 0.0045309 | -0.0021896 | -0.0010125 | -0.002696 | 0.0078126 | -0.0012477 | 0.003418 | -0.0061352 | -0.0030013 | -0.0096387 | 0.0017345 | -35.6552 | -8.6929 | -36.9873 | -37.1246 | -36.9232 | -37.056 | -37.0193 | -35.2158 | 85.318 | -36.9049 | -36.5295 | -36.7996 | -36.8546 | -36.6486 | -0.11902 | -93.9789 | -122.4106 | -0.054932 | -0.15106 | -0.18768 | -0.032043 | -0.068664 | -0.036621 | 0.032043 | -121.8155 | 0.068664 | 0.21973 | 0.013733 | 0.25635 | 0.050354 | 0.064087 | -0.13733 | 0.10529 | 0.37537 | 28.2944 | 122.2229 | 28.1754 | 122.1863 | -122.2733 | -122.1909 | -0.25635 | 0.33874 | 1.2131 | 1.6525
4404.1719 | 122.4289 | -35.2158 | 86.9843 | -0.098725 | -1.9142e-05 | 0.01396 | 0.0070943 | -0.0011214 | 5.5488e-05 | -0.0024822 | 0.013916 | -0.00060665 | 0.00085443 | -0.00079478 | -0.0032151 | -0.0062207 | 0.0015209 | -34.1537 | -8.6929 | -35.3668 | -35.5179 | -35.3577 | -35.4904 | -35.4218 | -33.7509 | 87.0071 | -35.2798 | -34.8724 | -34.9777 | -35.289 | -35.0967 | -0.15106 | -95.6772 | -122.5021 | -0.14191 | -0.20599 | -0.27466 | -0.054932 | -0.1236 | -0.064087 | 0.022888 | -121.8567 | 0.23804 | 0.11902 | -0.073242 | 0.1831 | -0.009155 | 0.009155 | -0.15106 | 0.30212 | 0.40741 | 26.6739 | 122.287 | 26.5228 | 122.2229 | -122.3511 | -122.2641 | -0.30212 | 0.34332 | 1.062 | 1.4648
4405.1719 | 122.4609 | -33.2291 | 89.0167 | -0.052948 | -0.00023294 | 0.010756 | 0.0088033 | 0.0012284 | -0.0012261 | -0.0014142 | 0.010864 | -0.0010339 | -0.00021357 | 0.00027342 | -0.0042831 | -0.0068615 | 0.00066654 | -32.2495 | -8.6838 | -33.3893 | -33.522 | -33.3664 | -33.5083 | -33.4442 | -31.8649 | 89.0671 | -33.3069 | -32.9178 | -32.991 | -33.316 | -33.1055 | -0.16022 | -97.7005 | -122.5388 | -0.13733 | -0.21515 | -0.27924 | -0.054932 | -0.11902 | -0.07782 | 0.050354 | -121.9345 | 0.23804 | 0.1236 | -0.086975 | 0.20142 | -0.009155 | 0.022888 | -0.13275 | 0.31586 | 0.3891 | 24.7055 | 122.374 | 24.5453 | 122.2961 | -122.406 | -122.3236 | -0.29297 | 0.31128 | 0.97961 | 1.3641
4406.1719 | 122.4609 | -31.3797 | 90.8615 | -0.075836 | -0.0021555 | 0.014387 | 0.0070943 | 0.0018692 | -0.00037171 | -0.00034601 | -0.0043946 | -0.00039305 | 0.001068 | 0.0043322 | -0.0023605 | -0.0081433 | 2.554e-05 | -30.4825 | -8.6929 | -31.5308 | -31.6864 | -31.5216 | -31.6589 | -31.5765 | -30.098 | 90.8844 | -31.4484 | -31.105 | -31.1874 | -31.4621 | -31.2927 | -0.15106 | -99.5544 | -122.5479 | -0.14191 | -0.19684 | -0.27924 | -0.045776 | -0.12817 | -0.068664 | 0.022888 | -121.9666 | 0.19226 | 0.086975 | -0.082397 | 0.15564 | -0.013733 | 0.009156 | -0.15564 | 0.26093 | 0.34332 | 22.8378 | 122.3328 | 22.6868 | 122.2641 | -122.3923 | -122.3099 | -0.3067 | 0.27466 | 0.89722 | 1.2817
4407.1719 | 122.5113 | -30.0705 | 92.2119 | -0.083466 | -0.0021555 | 0.014601 | 0.0077353 | 0.00016017 | -0.0016535 | -0.0033368 | 0.02002 | 0.0021703 | 0.00042723 | 0.00091422 | -0.0038559 | -0.0070753 | -0.00061526 | -29.1779 | -8.6929 | -30.1666 | -30.3085 | -30.098 | -30.2994 | -30.1987 | -28.7888 | 92.2302 | -30.1071 | -29.7958 | -29.8691 | -30.1254 | -29.9744 | -0.09613 | -100.9048 | -122.5204 | -0.027465 | -0.12817 | -0.22888 | -0.032043 | -0.13275 | -0.036621 | 0.018311 | -122.0078 | 0.20142 | 0.096131 | -0.054931 | 0.13275 | -0.01831 | 0.068665 | -0.14191 | 0.23804 | 0.31128 | 21.4737 | 122.3373 | 21.3776 | 122.3007 | -122.3785 | -122.319 | -0.23804 | 0.27466 | 0.89264 | 1.2817
4408.1719 | 122.4838 | -28.9078 | 93.3929 | -0.052948 | -0.00023294 | 0.012892 | 0.0064535 | 0.0016556 | -0.0020807 | 0.00050839 | 0.013916 | -0.00017945 | -0.0029908 | -0.0014356 | -0.0038559 | -0.0077161 | -0.00018806 | -28.0701 | -8.6884 | -29.0222 | -29.1367 | -28.9307 | -29.1275 | -29.0497 | -27.5803 | 93.4799 | -28.9444 | -28.6697 | -28.7659 | -28.9673 | -28.8162 | -0.11444 | -102.0813 | -122.5296 | -0.022888 | -0.14191 | -0.21973 | -0.027466 | -0.10528 | -0.036621 | 0.086975 | -122.0627 | 0.14191 | 0.091553 | -0.059509 | 0.12817 | -0.022888 | 0.091553 | -0.11444 | 0.17853 | 0.27466 | 20.3339 | 122.4243 | 20.2194 | 122.3877 | -122.4152 | -122.3373 | -0.22888 | 0.23804 | 0.83771 | 1.3275
4409.1719 | 122.5204 | -27.7634 | 94.5511 | -0.091095 | -0.00023294 | 0.014815 | 0.0053853 | 0.00058737 | -0.0018671 | -0.0012006 | 0.023071 | -0.00017945 | 0.00021363 | -0.0018628 | -0.0021469 | -0.0072889 | -0.0018971 | -27.0035 | -8.6929 | -27.919 | -28.0151 | -27.8412 | -28.0334 | -27.919 | -26.6464 | 94.5648 | -27.8366 | -27.5665 | -27.5894 | -27.8595 | -27.6855 | -0.15564 | -103.244 | -122.5662 | -0.07782 | -0.15564 | -0.27008 | 0 | -0.11444 | -0.073242 | 0.013733 | -122.1176 | 0.17395 | 0.07782 | -0.09613 | 0.15106 | -0.022888 | 0.077819 | -0.096131 | 0.24719 | 0.27008 | 19.2261 | 122.4014 | 19.0704 | 122.3282 | -122.4701 | -122.3877 | -0.25177 | 0.19684 | 0.75989 | 1.1169
4410.1719 | 122.5159 | -26.6693 | 95.6223 | -0.068207 | -0.0015145 | 0.014174 | 0.0070943 | -0.0017624 | 0.0011237 | 0.0020038 | -0.0013428 | 0.0023839 | 0.00064083 | 0.0024096 | -0.0032151 | -0.0096387 | -0.0044605 | -25.9827 | -8.6929 | -26.8616 | -26.9348 | -26.7792 | -26.9531 | -26.825 | -25.6348 | 95.6589 | -26.7609 | -26.5228 | -26.5091 | -26.7883 | -26.6144 | -0.19226 | -104.3152 | -122.5571 | -0.10986 | -0.15564 | -0.28381 | 0.036621 | -0.091553 | -0.091552 | 0.036622 | -122.1451 | 0.16022 | 0.054932 | -0.11902 | 0.14648 | -0.027466 | 0.082397 | -0.073242 | 0.25177 | 0.23804 | 18.1686 | 122.4197 | 17.9764 | 122.3282 | -122.4838 | -122.3831 | -0.2655 | 0.14649 | 0.68665 | 1.0345
4411.1719 | 122.5433 | -25.9277 | 96.4233 | -0.045319 | -0.0010873 | 0.016096 | 0.0098715 | 0.0040054 | -0.0018671 | 0.0028582 | -0.010498 | 0.00088875 | 0.0012818 | -0.001222 | -0.0021469 | -0.0085705 | -0.0018971 | -25.1999 | -8.6838 | -26.0101 | -26.1475 | -25.9918 | -26.207 | -26.0696 | -24.9344 | 96.4691 | -25.9781 | -25.7675 | -25.7401 | -26.0513 | -25.8774 | -0.082398 | -105.1071 | -122.5708 | -0.064087 | -0.14191 | -0.27924 | -0.059509 | -0.19684 | -0.050354 | 0.045776 | -122.1909 | 0.18768 | 0.050354 | -0.1236 | 0.10071 | -0.073243 | 0.018311 | -0.13733 | 0.23804 | 0.21057 | 17.3264 | 122.4472 | 17.244 | 122.3969 | -122.4335 | -122.4014 | -0.21973 | 0.16022 | 0.72784 | 0.99335
4412.1719 | 122.4884 | -25.0305 | 97.3022 | -0.098725 | 0.0010489 | 0.016524 | 0.0092307 | 0.00080117 | -0.00058531 | -0.0046186 | -0.0074462 | 0.00067495 | 0.001709 | -0.00464 | -0.0023605 | -0.0057935 | -0.0016833 | -24.3851 | -8.6929 | -25.1633 | -25.264 | -25.1175 | -25.3281 | -25.1724 | -24.0555 | 97.3618 | -25.1175 | -24.9023 | -24.8795 | -25.1633 | -25.0259 | -0.13275 | -105.9952 | -122.5662 | -0.086975 | -0.14191 | -0.29755 | -0.009155 | -0.1648 | -0.086975 | 0.059509 | -122.2046 | 0.15106 | 0.004578 | -0.13275 | 0.091553 | -0.045776 | 0.045776 | -0.10071 | 0.23804 | 0.21515 | 16.4703 | 122.4792 | 16.3376 | 122.3923 | -122.4655 | -122.4197 | -0.23346 | 0.12817 | 0.64545 | 0.97504
4413.1719 | 122.5616 | -24.1516 | 98.1857 | -0.068207 | -0.0017281 | 0.014815 | 0.0079489 | -0.00026703 | 0.0011237 | -0.002055 | -0.016602 | 0.0021703 | -0.00085457 | 0.0043322 | -0.0047103 | -0.0062207 | -0.0023243 | -23.5336 | -8.6975 | -24.3027 | -24.3393 | -24.2065 | -24.4125 | -24.2615 | -23.204 | 98.2224 | -24.2615 | -24.028 | -23.9639 | -24.2615 | -24.1241 | -0.15106 | -106.8832 | -122.525 | -0.054932 | -0.10986 | -0.26093 | 0.041198 | -0.10986 | -0.10986 | 0.036621 | -122.2137 | 0.18768 | 0.027465 | -0.10986 | 0.13733 | 0 | 0.09613 | -0.036621 | 0.29755 | 0.23346 | 15.6052 | 122.4838 | 15.4541 | 122.374 | -122.4884 | -122.4472 | -0.18768 | 0.1236 | 0.61798 | 0.94757
4414.1719 | 122.5525 | -23.6664 | 98.6984 | -0.060578 | -0.0034371 | 0.017378 | 0.0068807 | 0.0012284 | -0.0022943 | -0.00013241 | -0.016602 | -0.00060665 | 0.001709 | 0.0015552 | -0.0023605 | -0.0068615 | 0.0019483 | -23.0484 | -8.6975 | -23.8174 | -23.877 | -23.7259 | -23.9365 | -23.79 | -22.7188 | 98.7259 | -23.7442 | -23.5519 | -23.5062 | -23.7808 | -23.6252 | -0.15106 | -107.3959 | -122.5754 | -0.059509 | -0.1236 | -0.27008 | 0.027466 | -0.11902 | -0.07782 | 0.027466 | -122.2504 | 0.16022 | 0.041199 | -0.11444 | 0.11902 | -0.036621 | 0.091553 | -0.059509 | 0.23804 | 0.19226 | 15.1199 | 122.4701 | 14.9689 | 122.3923 | -122.5159 | -122.4426 | -0.21057 | 0.11444 | 0.61798 | 0.94757
4415.1719 | 122.5388 | -23.0759 | 99.2798 | -0.13687 | -0.00044654 | 0.016951 | 0.0079489 | -0.00069423 | 0.0011237 | 0.001363 | -0.0013428 | 0.0023839 | 0.001068 | 0.0026232 | -0.0034287 | -0.0066479 | -0.00061526 | -22.4945 | -8.6975 | -23.2361 | -23.291 | -23.1354 | -23.378 | -23.2132 | -22.1741 | 99.3347 | -23.1674 | -22.9706 | -22.9202 | -23.1995 | -23.0576 | -0.16022 | -107.9773 | -122.5708 | -0.059509 | -0.13733 | -0.30212 | 0.022888 | -0.14191 | -0.091552 | 0.054932 | -122.2504 | 0.15564 | 0.018311 | -0.1236 | 0.10986 | -0.032044 | 0.10071 | -0.054932 | 0.24719 | 0.19684 | 14.5386 | 122.5021 | 14.3784 | 122.4106 | -122.5159 | -122.4472 | -0.21515 | 0.10529 | 0.58136 | 0.90179
4416.1719 | 122.5845 | -22.3801 | 99.9573 | -0.060578 | 0.00019446 | 0.016951 | 0.0073081 | -0.0021896 | -0.0014399 | -0.00055961 | -0.010498 | 0.00067495 | 0.00085443 | -0.0020764 | -0.0019333 | -0.0083569 | 0.0019483 | -21.7987 | -8.6929 | -22.4991 | -22.5403 | -22.3938 | -22.6227 | -22.4442 | -21.4737 | 100.0214 | -22.4533 | -22.2565 | -22.1787 | -22.4716 | -22.3297 | -0.11902 | -108.6502 | -122.4976 | -0.013733 | -0.064087 | -0.24262 | 0.054931 | -0.1236 | -0.073242 | 0.064087 | -122.2137 | 0.20142 | 0.050354 | -0.091553 | 0.1236 | -0.018311 | 0.10528 | -0.041199 | 0.27466 | 0.19684 | 13.8062 | 122.4747 | 13.6871 | 122.4014 | -122.4564 | -122.4106 | -0.16022 | 0.1236 | 0.58136 | 0.90637
4417.1719 | 122.5525 | -21.8491 | 100.5569 | -0.13687 | -0.00066014 | 0.015883 | 0.0090169 | 0.003151 | -0.00015811 | 0.00093559 | -0.0013428 | 0.00088875 | -0.0012818 | 0.008391 | -0.0025741 | -0.0053663 | -0.0074513 | -21.2036 | -8.6884 | -21.8994 | -21.9589 | -21.8079 | -22.0596 | -21.8765 | -20.9244 | 100.6485 | -21.8765 | -21.785 | -21.6202 | -22.0001 | -21.7712 | -0.050354 | -109.2453 | -122.5159 | 0.041199 | -0.027466 | -0.21057 | 0.022888 | -0.16022 | -0.027466 | 0.091553 | -122.3419 | 0.22888 | 0.07782 | -0.15106 | 0.10529 | -0.1236 | 0.091553 | -0.059509 | 0.25635 | 0.091553 | 13.2111 | 122.525 | 13.1607 | 122.4976 | -122.4564 | -122.4335 | -0.10986 | 0.064087 | 0.64545 | 0.92468
4418.1719 | 122.525 | -21.1075 | 101.2711 | -0.15213 | -0.0021555 | 0.016951 | 0.010512 | 0.00037377 | 0.00091009 | -0.00098701 | -0.025757 | 0.0013159 | -0.00021357 | 0.00027342 | -0.0017197 | -0.0060071 | 0.00066654 | -20.5215 | -8.6975 | -21.2128 | -21.2128 | -21.048 | -21.3409 | -21.1441 | -20.2148 | 101.3397 | -21.167 | -20.993 | -20.9427 | -21.2311 | -21.0709 | -0.10529 | -109.9686 | -122.4838 | 0.059509 | -0.036621 | -0.23346 | 0.068665 | -0.12817 | -0.059509 | 0.068665 | -122.2641 | 0.16479 | 0.036621 | -0.1236 | 0.09613 | -0.064087 | 0.1648 | 0 | 0.2243 | 0.17395 | 12.5153 | 122.5067 | 12.41 | 122.4472 | -122.4838 | -122.438 | -0.10529 | 0.11444 | 0.58594 | 0.89264
4419.1719 | 122.5891 | -20.4987 | 101.9119 | -0.075836 | -0.0030099 | 0.01866 | 0.0083761 | -0.001976 | 0.00026909 | -0.0029096 | -0.0043946 | 0.0025975 | 0.0023498 | -0.0027174 | -0.0025741 | -0.0062207 | -0.0021107 | -19.9631 | -8.6929 | -20.5994 | -20.6406 | -20.5078 | -20.7596 | -20.5627 | -19.6838 | 101.9577 | -20.5719 | -20.3888 | -20.311 | -20.6314 | -20.4758 | -0.10071 | -110.6049 | -122.5525 | -0.009155 | -0.064087 | -0.26093 | 0.036621 | -0.16022 | -0.073242 | 0.045777 | -122.3007 | 0.18768 | 0.022888 | -0.13275 | 0.09613 | -0.05951 | 0.091553 | -0.041199 | 0.26092 | 0.1831 | 11.9064 | 122.5296 | 11.8057 | 122.4564 | -122.5113 | -122.4838 | -0.14191 | 0.10986 | 0.53558 | 0.81482
4420.1719 | 122.6166 | -19.8212 | 102.5528 | -0.03006 | -0.0023691 | 0.014387 | 0.0073081 | -0.0024032 | -0.00015811 | -0.00013241 | 0.0078126 | 3.4148e-05 | 0.00021363 | 0.0026232 | -0.0036423 | -0.0085705 | 0.00045294 | -19.249 | -8.6975 | -19.9219 | -19.8944 | -19.725 | -20.0088 | -19.8212 | -18.9194 | 102.6123 | -19.8807 | -19.6701 | -19.5831 | -19.8853 | -19.7479 | -0.10071 | -111.2503 | -122.4472 | 0.09613 | 0 | -0.18768 | 0.10071 | -0.086975 | -0.059509 | 0.05951 | -122.2229 | 0.23804 | 0.073242 | -0.064087 | 0.13275 | -0.004578 | 0.19684 | 0.027466 | 0.29755 | 0.21057 | 11.2244 | 122.493 | 11.1237 | 122.4335 | -122.4747 | -122.4335 | -0.073242 | 0.15106 | 0.57221 | 0.90179
4421.1719 | 122.5845 | -19.2902 | 103.125 | -0.052948 | -0.0010873 | 0.016737 | 0.0094443 | -0.0024032 | -0.0012261 | -0.002055 | -0.016602 | 0.0019567 | 0.00042723 | 0.00048702 | -0.0023605 | -0.0049389 | 0.0013073 | -18.7775 | -8.6975 | -19.4 | -19.4046 | -19.2673 | -19.5419 | -19.3039 | -18.4799 | 103.1662 | -19.368 | -19.1483 | -19.0521 | -19.3542 | -19.2169 | -0.10986 | -111.8225 | -122.5296 | 0.022888 | -0.013733 | -0.25177 | 0.09613 | -0.14191 | -0.07782 | 0.041199 | -122.2733 | 0.23804 | 0.073242 | -0.064087 | 0.15106 | 0.013733 | 0.13275 | -0.004578 | 0.31586 | 0.21973 | 10.7025 | 122.5342 | 10.5927 | 122.4564 | -122.525 | -122.493 | -0.11444 | 0.14191 | 0.5127 | 0.81024
4422.1719 | 122.58 | -18.8004 | 103.6102 | -0.091095 | -0.0010873 | 0.015883 | 0.010299 | -0.0013352 | 0.0013373 | 0.00050839 | -0.010498 | 0.0013159 | -0.0014954 | -0.0014356 | -0.0025741 | -0.0057935 | 0.00045294 | -18.2831 | -8.6929 | -18.9102 | -18.8919 | -18.7958 | -19.0659 | -18.8095 | -18.0084 | 103.6606 | -18.8965 | -18.6722 | -18.5577 | -18.9011 | -18.7683 | -0.10986 | -112.3032 | -122.5021 | 0.004578 | -0.009155 | -0.2655 | 0.10071 | -0.15564 | -0.09613 | 0.050354 | -122.2824 | 0.24261 | 0.032043 | -0.10071 | 0.12817 | -0.004578 | 0.11444 | 0.01831 | 0.33874 | 0.2243 | 10.2173 | 122.5571 | 10.1074 | 122.4609 | -122.5204 | -122.5067 | -0.091553 | 0.12817 | 0.51727 | 0.79193
4423.1719 | 122.58 | -18.663 | 103.7613 | -0.022431 | -0.0025827 | 0.012251 | 0.0094443 | 0.0018692 | -0.00037171 | 0.0037128 | -0.010498 | -0.00060665 | 0.00021363 | 0.0051868 | -0.0019333 | -0.0066479 | 0.0021619 | -17.9993 | -8.6975 | -18.75 | -18.0908 | -17.9718 | -18.8736 | -18.0359 | -17.8619 | 103.8254 | -18.7408 | -18.5394 | -18.4479 | -18.7637 | -18.631 | -0.086975 | -112.4588 | -121.8521 | 0.69122 | 0.62714 | -0.21057 | 0.71411 | -0.1236 | -0.07782 | 0.064086 | -122.3007 | 0.21515 | 0.032044 | -0.10071 | 0.10986 | -0.022888 | 0.7782 | 0.65918 | 0.29297 | 0.20142 | 10.0525 | 122.5662 | 9.9655 | 122.4884 | -122.5113 | -122.5021 | 0.57221 | 0.1236 | 0.66376 | 0.80109
4424.1719 | 122.5937 | -18.0542 | 104.3381 | -0.12161 | 0.0025443 | 0.01396 | 0.0079489 | -0.0011214 | -0.0022943 | 0.0052082 | -0.01355 | -0.00017945 | 0.00021363 | 0.0024096 | -0.0027877 | -0.0068615 | -0.0025379 | -17.3859 | -8.6929 | -18.1412 | -17.5003 | -17.363 | -18.2739 | -17.4271 | -17.2394 | 104.4525 | -18.0908 | -17.9077 | -17.8116 | -18.1137 | -17.9718 | -0.086975 | -113.031 | -121.8384 | 0.69122 | 0.62714 | -0.21973 | 0.71411 | -0.13275 | -0.036621 | 0.11444 | -122.2458 | 0.24262 | 0.082397 | -0.059509 | 0.11902 | -0.022888 | 0.7782 | 0.64087 | 0.27924 | 0.18311 | 9.4482 | 122.5433 | 9.3613 | 122.5067 | -122.4792 | -122.4289 | 0.55389 | 0.14648 | 0.66833 | 0.81482
4425.1719 | 122.5983 | -17.5461 | 104.8553 | -0.11398 | 0.0010489 | 0.013747 | 0.0079489 | 0.00080117 | 0.0017645 | 0.0067036 | -0.071533 | 3.4148e-05 | 0.00064083 | -0.0014356 | -0.0038559 | -0.0055799 | 0.0013073 | -16.9006 | -8.6975 | -17.6743 | -16.983 | -16.7999 | -17.7521 | -16.9052 | -16.7496 | 104.9469 | -17.6193 | -17.3996 | -17.3538 | -17.6468 | -17.4912 | -0.12817 | -113.5529 | -121.8384 | 0.74615 | 0.64087 | -0.20599 | 0.76904 | -0.07782 | -0.073242 | 0.091552 | -122.2549 | 0.19226 | 0.054932 | -0.10071 | 0.12817 | -0.027466 | 0.87433 | 0.69122 | 0.2655 | 0.21973 | 8.9767 | 122.5662 | 8.8486 | 122.493 | -122.5296 | -122.4747 | 0.56305 | 0.14648 | 0.64545 | 0.79651
4426.1719 | 122.5159 | -17.0883 | 105.4092 | -0.037689 | -0.0021555 | 0.012892 | 0.0070943 | -0.0021896 | -0.0022943 | 0.0084124 | -0.022705 | 0.0015295 | 2.8e-08 | 0.0062548 | -0.0034287 | -0.0060071 | -0.0025379 | -16.3971 | -8.6975 | -17.157 | -16.4566 | -16.3055 | -17.2302 | -16.3788 | -16.301 | 105.4871 | -17.1341 | -16.9601 | -16.8823 | -17.1844 | -17.07 | -0.068664 | -114.1068 | -121.8658 | 0.78278 | 0.70953 | -0.14191 | 0.7782 | -0.073243 | -0.045776 | 0.07782 | -122.3694 | 0.20599 | 0.018311 | -0.09613 | 0.064087 | -0.050354 | 0.85144 | 0.70038 | 0.25177 | 0.17395 | 8.4595 | 122.6212 | 8.3908 | 122.5754 | -122.5662 | -122.5433 | 0.63171 | 0.12817 | 0.69122 | 0.78735
4427.1719 | 122.58 | -16.5939 | 105.8395 | -0.091095 | 0.00040806 | 0.011183 | 0.0077353 | 0.0044328 | -0.0018671 | 0.0062762 | -0.03186 | 0.0013159 | -0.00021357 | 0.0043322 | -0.0023605 | -0.0070753 | -0.0010425 | -15.9851 | -8.7021 | -16.7267 | -15.9576 | -15.8432 | -16.8091 | -15.8936 | -15.8386 | 105.8853 | -16.6946 | -16.452 | -16.3879 | -16.6992 | -16.5573 | -0.13275 | -114.5416 | -121.7972 | 0.75073 | 0.70038 | -0.21515 | 0.83313 | -0.082397 | -0.10071 | 0.045776 | -122.2916 | 0.20599 | 0.036621 | -0.10529 | 0.13733 | -0.004578 | 0.88348 | 0.76904 | 0.3067 | 0.24262 | 8.0246 | 122.58 | 7.8918 | 122.4792 | -122.5662 | -122.5342 | 0.63629 | 0.14191 | 0.60883 | 0.75531
4428.1719 | 122.6028 | -16.1636 | 106.2607 | -0.091095 | -0.0019417 | 0.01161 | 0.010085 | -0.0021896 | -0.0012261 | 0.0056354 | -0.01355 | 0.0028113 | -0.0012818 | 0.0028368 | -0.0019333 | -0.0066479 | -0.0053149 | -15.5411 | -8.7021 | -16.2872 | -15.5319 | -15.3854 | -16.3925 | -15.4633 | -15.4221 | 106.3202 | -16.2598 | -16.0355 | -15.9622 | -16.2552 | -16.1133 | -0.1236 | -114.9628 | -121.7926 | 0.7782 | 0.70038 | -0.22888 | 0.82397 | -0.10529 | -0.096131 | 0.059509 | -122.2961 | 0.20142 | 0.050354 | -0.091553 | 0.14648 | 0.004578 | 0.90179 | 0.75531 | 0.29755 | 0.2243 | 7.5851 | 122.58 | 7.4615 | 122.4838 | -122.5479 | -122.5204 | 0.63171 | 0.12817 | 0.62256 | 0.74158
4429.1719 | 122.612 | -15.7471 | 106.6956 | -0.068207 | -0.0015145 | 0.015456 | 0.0064535 | -0.0032578 | -0.0012261 | 0.0052082 | 0.0078126 | 0.0011023 | -0.0010682 | 0.0036914 | -0.0025741 | -0.0070753 | -0.0025379 | -15.1382 | -8.6929 | -15.8569 | -15.0925 | -14.978 | -15.9485 | -15.0467 | -15.0055 | 106.7688 | -15.8295 | -15.6235 | -15.5548 | -15.8249 | -15.6967 | -0.10986 | -115.3885 | -121.788 | 0.76904 | 0.70038 | -0.20142 | 0.81024 | -0.091552 | -0.082398 | 0.073242 | -122.319 | 0.19226 | 0.050354 | -0.07782 | 0.13275 | 0.004578 | 0.87891 | 0.76447 | 0.27466 | 0.20599 | 7.164 | 122.5983 | 7.0541 | 122.5159 | -122.5525 | -122.525 | 0.6546 | 0.1236 | 0.60883 | 0.74158
4430.1719 | 122.6028 | -15.3442 | 107.1167 | -0.10635 | 0.0019035 | 0.013319 | 0.0092307 | 0.0010148 | -0.0022943 | 0.0032856 | -0.022705 | 0.0023839 | 0.0025634 | 0.0043322 | -0.0030013 | -0.0068615 | -0.0018971 | -14.7491 | -8.6929 | -15.4358 | -14.7079 | -14.5889 | -15.5502 | -14.653 | -14.5798 | 107.1671 | -15.4175 | -15.1886 | -15.1382 | -15.4175 | -15.271 | -0.091553 | -115.8096 | -121.8246 | 0.75531 | 0.69122 | -0.20599 | 0.78278 | -0.11444 | -0.073242 | 0.050354 | -122.3053 | 0.20599 | 0.073242 | -0.073242 | 0.14648 | 0 | 0.84686 | 0.72784 | 0.27923 | 0.22888 | 6.7429 | 122.5845 | 6.6513 | 122.5113 | -122.5525 | -122.5342 | 0.63629 | 0.15564 | 0.59509 | 0.76447
4431.1719 | 122.5388 | -15.0696 | 107.4188 | -0.03006 | -0.0017281 | 0.012892 | 0.0098715 | -0.0011214 | -0.0010125 | 0.0064898 | -0.03186 | 0.0025975 | 0.00085443 | -0.0033582 | -0.0017197 | -0.0066479 | -0.0012561 | -14.415 | -8.6975 | -15.152 | -14.3326 | -14.2044 | -15.2115 | -14.2868 | -14.3005 | 107.5195 | -15.1382 | -14.9597 | -14.9002 | -15.1611 | -15.0467 | -0.082398 | -116.1163 | -121.7514 | 0.86517 | 0.78278 | -0.14191 | 0.86517 | -0.059509 | -0.068665 | 0.10071 | -122.3785 | 0.16937 | 0.022888 | -0.091553 | 0.091553 | -0.022888 | 0.94757 | 0.8194 | 0.23804 | 0.17853 | 6.4545 | 122.6578 | 6.3721 | 122.5891 | -122.5708 | -122.5571 | 0.737 | 0.10986 | 0.6546 | 0.76904
4432.1719 | 122.6028 | -14.6484 | 107.8125 | -0.083466 | -0.00044654 | 0.013319 | 0.0077353 | 0.003151 | -0.0020807 | 0.0062762 | -0.059326 | 0.0015295 | 0.00021363 | 0.0043322 | -0.00065151 | -0.0064343 | 2.554e-05 | -14.035 | -8.7021 | -14.7812 | -13.8977 | -13.7604 | -14.8132 | -13.8611 | -13.7924 | 107.8445 | -14.7354 | -14.4516 | -14.447 | -14.6896 | -14.566 | -0.13275 | -116.5146 | -121.7102 | 0.88806 | 0.78735 | -0.16479 | 0.9201 | -0.032043 | -0.086976 | 0.032043 | -122.2641 | 0.20142 | 0.082397 | -0.041199 | 0.16937 | 0.045777 | 1.0208 | 0.88348 | 0.28839 | 0.28381 | 6.0791 | 122.58 | 5.9463 | 122.493 | -122.5937 | -122.5479 | 0.75073 | 0.19684 | 0.6134 | 0.85602
4433.1719 | 122.5891 | -14.2044 | 108.2199 | -0.068207 | -1.9142e-05 | 0.017165 | 0.0092307 | 0.00037377 | 0.00048269 | 0.0060626 | -0.016602 | 0.0030249 | 0.00042723 | -0.0010084 | -0.0025741 | -0.0075025 | -0.00061526 | -13.6459 | -8.7021 | -14.3738 | -13.5361 | -13.3713 | -14.3784 | -13.4811 | -13.3759 | 108.2794 | -14.2914 | -14.0167 | -13.9938 | -14.2822 | -14.122 | -0.16937 | -116.922 | -121.756 | 0.83313 | 0.72327 | -0.17395 | 0.89264 | -0.004578 | -0.086975 | 0.059509 | -122.2366 | 0.21057 | 0.082398 | -0.07782 | 0.16937 | 0.009155 | 1.0025 | 0.83771 | 0.29755 | 0.27466 | 5.6717 | 122.5708 | 5.5023 | 122.4838 | -122.5937 | -122.5113 | 0.66833 | 0.18768 | 0.55847 | 0.82855
4434.1719 | 122.6074 | -13.9069 | 108.5449 | -0.075836 | -0.00087374 | 0.013319 | 0.0098715 | -0.0049668 | -0.00058531 | 0.0045672 | -0.0074462 | 0.0013159 | -0.00021357 | -0.0027174 | -0.0036423 | -0.0085705 | -0.0016833 | -13.3347 | -8.6975 | -14.0213 | -13.2202 | -13.092 | -14.09 | -13.1516 | -13.1241 | 108.609 | -14.0167 | -13.7512 | -13.7054 | -13.9618 | -13.8474 | -0.11444 | -117.2424 | -121.7651 | 0.81482 | 0.75531 | -0.18311 | 0.86975 | -0.068665 | -0.10986 | 0.064087 | -122.2961 | 0.20142 | 0.059509 | -0.054932 | 0.16937 | 0.054932 | 0.92926 | 0.80109 | 0.31128 | 0.2655 | 5.3238 | 122.6257 | 5.2094 | 122.5159 | -122.5662 | -122.5616 | 0.68665 | 0.15564 | 0.5722 | 0.78278
4435.1719 | 122.6166 | -13.7375 | 108.7372 | -0.10635 | -0.00023294 | 0.013533 | 0.0075217 | -0.0028304 | -0.0010125 | 0.0060626 | 0.0078126 | 0.0025975 | -0.0010682 | 0.001128 | -0.0030013 | -0.0070753 | 0.00023934 | -13.1332 | -8.6975 | -13.8336 | -12.9044 | -12.8036 | -13.8748 | -12.8494 | -12.9089 | 108.7967 | -13.8245 | -13.5406 | -13.504 | -13.7924 | -13.6414 | -0.09613 | -117.4347 | -121.6415 | 0.93384 | 0.88806 | -0.13733 | 0.98419 | -0.041199 | -0.086975 | 0.059509 | -122.2778 | 0.23346 | 0.096131 | -0.054931 | 0.18311 | 0.032044 | 1.03 | 0.92926 | 0.32043 | 0.28381 | 5.1361 | 122.6212 | 5.04 | 122.5342 | -122.5708 | -122.5616 | 0.83313 | 0.19684 | 0.60425 | 0.82855
4436.1719 | 122.5845 | -13.4583 | 109.0668 | -0.052948 | 0.00040806 | 0.013106 | 0.0096579 | 0.0018692 | -0.0010125 | 0.0054218 | -0.074585 | 0.0021703 | 0.0014954 | -0.0048536 | -0.0059921 | -0.0055799 | -0.0021107 | -12.8311 | -8.6884 | -13.5635 | -12.6938 | -12.6022 | -13.6139 | -12.6251 | -12.6297 | 109.1263 | -13.5178 | -13.2523 | -13.2431 | -13.5315 | -13.3759 | -0.10529 | -117.7551 | -121.7606 | 0.85602 | 0.83313 | -0.15564 | 0.93842 | -0.050354 | -0.059509 | 0.05951 | -122.319 | 0.21515 | 0.082398 | -0.073242 | 0.14191 | -0.013733 | 0.9613 | 0.86975 | 0.27466 | 0.2655 | 4.8752 | 122.644 | 4.7699 | 122.5845 | -122.6303 | -122.5845 | 0.76446 | 0.20599 | 0.62714 | 0.82855
4437.1719 | 122.6212 | -13.1195 | 109.3414 | -0.11398 | 0.00083526 | 0.014815 | 0.0081625 | 0.0040054 | -0.00015811 | 0.007558 | 0.001709 | 0.0013159 | -0.0021362 | 0.0015552 | -0.0030013 | -0.0087843 | -0.0014697 | -12.5336 | -8.6884 | -13.2156 | -12.3276 | -12.1994 | -13.2751 | -12.2543 | -12.2772 | 109.4513 | -13.1973 | -12.9181 | -12.8769 | -13.1607 | -13.0325 | -0.09613 | -118.0298 | -121.669 | 0.92011 | 0.86517 | -0.15564 | 0.9613 | -0.059509 | -0.07782 | 0.10986 | -122.2595 | 0.24262 | 0.086975 | -0.041199 | 0.16479 | 0.036621 | 1.0162 | 0.88806 | 0.32043 | 0.27924 | 4.5273 | 122.6486 | 4.4312 | 122.5708 | -122.5571 | -122.5388 | 0.79193 | 0.20142 | 0.58594 | 0.84229
4438.1719 | 122.6074 | -12.9227 | 109.5978 | -0.060578 | -0.00066014 | 0.013106 | 0.010299 | -0.001976 | 0.00026909 | 0.0045672 | 0.001709 | 0.00067495 | 0.00042723 | 5.9824e-05 | -0.0012925 | -0.0079297 | 0.0013073 | -12.323 | -8.6838 | -12.9776 | -12.0895 | -11.9751 | -13.0554 | -12.03 | -11.9934 | 109.6573 | -12.973 | -12.6938 | -12.6709 | -12.9318 | -12.8036 | -0.054932 | -118.2816 | -121.6873 | 0.94757 | 0.89264 | -0.13275 | 0.94757 | -0.07782 | -0.050354 | 0.05951 | -122.2916 | 0.25177 | 0.11902 | -0.009156 | 0.16937 | 0.041198 | 1.0025 | 0.88806 | 0.30212 | 0.27923 | 4.2938 | 122.6303 | 4.2389 | 122.58 | -122.5754 | -122.5708 | 0.83313 | 0.22888 | 0.59967 | 0.92926
4439.1719 | 122.5937 | -12.6389 | 109.8587 | -0.17502 | -1.9142e-05 | 0.014387 | 0.0083761 | 0.00037377 | -0.0018671 | 0.0032856 | -0.016602 | 0.0011023 | 2.8e-08 | -0.0016492 | -0.0040695 | -0.0075025 | -0.0025379 | -12.0255 | -8.67 | -12.735 | -11.7966 | -11.6776 | -12.7762 | -11.7462 | -11.6776 | 109.8999 | -12.7167 | -12.3962 | -12.4146 | -12.6709 | -12.5336 | -0.09613 | -118.5287 | -121.6553 | 0.9613 | 0.89264 | -0.13733 | 0.98877 | -0.041199 | -0.07782 | 0.041198 | -122.2549 | 0.2243 | 0.10529 | -0.032043 | 0.18311 | 0.045777 | 1.0574 | 0.93842 | 0.30212 | 0.32043 | 4.0649 | 122.6166 | 3.9688 | 122.5388 | -122.5937 | -122.5754 | 0.84229 | 0.24261 | 0.6134 | 0.9613
4440.1719 | 122.6212 | -12.3596 | 110.1242 | -0.1445 | -0.0025827 | 0.014387 | 0.0098715 | -0.0011214 | 0.0019781 | 0.0069172 | -0.022705 | 0.00067495 | -0.00021357 | 0.001128 | -0.0027877 | -0.0072889 | 0.0017345 | -11.7279 | -8.6563 | -12.4558 | -11.4441 | -11.3159 | -12.4786 | -11.4029 | -11.3709 | 110.1974 | -12.4374 | -12.117 | -12.1307 | -12.3734 | -12.2543 | -0.096131 | -118.7805 | -121.5683 | 1.0437 | 0.95673 | -0.11902 | 1.0529 | -0.022888 | -0.07782 | 0.073242 | -122.2412 | 0.22888 | 0.10529 | -0.013733 | 0.18311 | 0.064087 | 1.1398 | 1.0117 | 0.3067 | 0.32043 | 3.7994 | 122.6349 | 3.7033 | 122.5571 | -122.58 | -122.5616 | 0.91553 | 0.24262 | 0.63171 | 0.98877
4441.1719 | 122.6166 | -12.1536 | 110.3622 | -0.083466 | -0.00087374 | 0.013747 | 0.0068807 | 0.001442 | -0.00058531 | 0.0039264 | -0.0074462 | 0.00067495 | -0.00064077 | 5.9824e-05 | -0.0021469 | -0.0066479 | -0.0036059 | -11.5448 | -8.6426 | -12.2177 | -11.2701 | -11.1511 | -12.2681 | -11.1969 | -11.174 | 110.4309 | -12.236 | -11.8927 | -11.8973 | -12.1765 | -12.0575 | -0.064087 | -119.0048 | -121.6324 | 1.0025 | 0.95673 | -0.11444 | 1.0208 | -0.050354 | -0.082398 | 0.068664 | -122.2549 | 0.25635 | 0.09613 | -0.022889 | 0.17853 | 0.059509 | 1.0666 | 0.94757 | 0.33874 | 0.34332 | 3.5751 | 122.6669 | 3.511 | 122.5845 | -122.58 | -122.5983 | 0.88348 | 0.26093 | 0.60882 | 0.97961
4442.1719 | 122.6303 | -11.8149 | 110.701 | -0.075836 | -0.00087374 | 0.011824 | 0.0077353 | 0.0012284 | 0.00026909 | 0.0071308 | 0.013916 | -0.00082025 | 0.00085443 | -0.00036738 | -0.0019333 | -0.0070753 | 0.00045294 | -11.1877 | -8.606 | -11.8835 | -10.8765 | -10.7758 | -11.911 | -10.8078 | -10.9131 | 110.7697 | -11.9064 | -11.5311 | -11.5356 | -11.7783 | -11.6821 | -0.068665 | -119.3069 | -121.5775 | 1.0391 | 1.0071 | -0.096131 | 1.0757 | -0.027466 | -0.091553 | 0.068664 | -122.2321 | 0.27923 | 0.13275 | 0.036621 | 0.2243 | 0.12817 | 1.1078 | 1.0071 | 0.37079 | 0.37537 | 3.2776 | 122.6761 | 3.2089 | 122.5845 | -122.5845 | -122.6074 | 0.93842 | 0.28381 | 0.62714 | 0.90179
4443.1719 | 122.6303 | -11.4487 | 111.0809 | -0.13687 | 0.00040806 | 0.013106 | 0.0092307 | 0.0050736 | -0.0014399 | 0.0071308 | -0.010498 | -0.00039305 | 0.00042723 | -0.001222 | -0.0032151 | -0.0060071 | -0.0038197 | -10.849 | -8.5739 | -11.5494 | -10.5148 | -10.3912 | -11.5677 | -10.437 | -10.4782 | 111.1313 | -11.5448 | -11.174 | -11.1969 | -11.4578 | -11.348 | -0.10071 | -119.6548 | -121.5958 | 1.0574 | 1.0117 | -0.11902 | 1.1124 | -0.018311 | -0.096131 | 0.050354 | -122.2549 | 0.25177 | 0.10071 | -0.009156 | 0.19684 | 0.086975 | 1.1581 | 1.0345 | 0.3479 | 0.37079 | 2.9755 | 122.6761 | 2.8748 | 122.58 | -122.6303 | -122.6257 | 0.93384 | 0.27466 | 0.59967 | 0.97046
4444.1719 | 122.644 | -11.2747 | 111.2366 | -0.037689 | 0.00040806 | 0.010115 | 0.0096579 | -5.343e-05 | -0.0014399 | 0.005849 | 0.0078126 | 0.00067495 | -0.00021357 | 0.00027342 | -0.0044967 | -0.0083569 | -0.00018806 | -10.6613 | -8.5144 | -11.3617 | -10.2264 | -10.1395 | -11.38 | -10.1807 | -10.2539 | 111.3144 | -11.3251 | -10.9909 | -11.0367 | -11.2656 | -11.142 | -0.086975 | -119.751 | -121.463 | 1.1353 | 1.0941 | -0.10529 | 1.181 | -0.018311 | -0.050354 | 0.07782 | -122.2275 | 0.23804 | 0.13275 | 0.009155 | 0.1831 | 0.059509 | 1.2222 | 1.1353 | 0.28839 | 0.33417 | 2.8473 | 122.6395 | 2.7603 | 122.5891 | -122.5983 | -122.5616 | 1.0483 | 0.28381 | 0.6134 | 1.0208
4445.1719 | 122.6486 | -11.0504 | 111.4517 | -0.068207 | -0.0010873 | 0.01161 | 0.0088033 | 0.0020828 | -0.0022943 | 0.0062762 | -0.0043946 | -0.00082025 | -0.0014954 | -0.0027174 | -0.0030013 | -0.0072889 | 0.0017345 | -10.4416 | -8.4778 | -11.142 | -10.0204 | -9.9197 | -11.174 | -9.9655 | -10.0525 | 111.5295 | -11.1237 | -10.7712 | -10.7986 | -11.0779 | -10.9314 | -0.091553 | -119.9295 | -121.4722 | 1.1307 | 1.0849 | -0.1236 | 1.1765 | -0.032043 | -0.073242 | 0.07782 | -122.2229 | 0.25177 | 0.11902 | -0.027466 | 0.19226 | 0.045776 | 1.2222 | 1.1215 | 0.32501 | 0.35248 | 2.6642 | 122.6532 | 2.5726 | 122.58 | -122.5937 | -122.5754 | 1.03 | 0.27924 | 0.60883 | 0.99792
4446.1719 | 122.6715 | -10.9177 | 111.5936 | -0.091095 | 0.0019035 | 0.012465 | 0.0068807 | -0.0028304 | -0.00037171 | 0.0064898 | -0.03186 | -0.00060665 | 0.00064083 | 0.0032642 | -0.0032151 | -0.0053663 | 2.554e-05 | -10.2631 | -8.4457 | -11.0321 | -9.8923 | -9.7504 | -11.0321 | -9.8465 | -9.8694 | 111.6348 | -11.0184 | -10.6018 | -10.6476 | -10.8948 | -10.7666 | -0.11444 | -120.0394 | -121.4859 | 1.1673 | 1.0712 | -0.11444 | 1.1856 | 0 | -0.10071 | 0.041199 | -122.1954 | 0.27008 | 0.15106 | 0.022889 | 0.25177 | 0.1236 | 1.2817 | 1.1398 | 0.37079 | 0.41656 | 2.5864 | 122.6532 | 2.4719 | 122.5525 | -122.6257 | -122.612 | 1.0254 | 0.31586 | 0.6546 | 1.0483
4447.1719 | 122.6669 | -10.7117 | 111.7859 | -0.10635 | -1.9142e-05 | 0.013747 | 0.0083761 | 0.0050736 | -0.0010125 | 0.0081988 | -0.047119 | 0.0013159 | -0.00064077 | -0.00036738 | -0.0017197 | -0.0062207 | 0.0010937 | -10.0388 | -8.3725 | -10.7941 | -9.5764 | -9.4162 | -10.7986 | -9.5947 | -9.6451 | 111.8591 | -10.8124 | -10.3775 | -10.4187 | -10.6705 | -10.5423 | -0.082397 | -120.1584 | -121.3623 | 1.2955 | 1.1169 | -0.086975 | 1.1993 | -0.004578 | -0.10071 | 0.073242 | -122.1634 | 0.29297 | 0.16937 | 0.041199 | 0.27008 | 0.14191 | 1.3779 | 1.2177 | 0.39368 | 0.43488 | 2.4216 | 122.6715 | 2.3392 | 122.5708 | -122.58 | -122.5983 | 1.1353 | 0.33417 | 0.67291 | 1.0666
4448.1719 | 122.6166 | -10.6567 | 111.8729 | -0.11398 | 0.00019446 | 0.012679 | 0.0064535 | 0.0010148 | -0.00079891 | 0.007558 | -0.01355 | -0.00039305 | 0.00042723 | -0.0025036 | -0.00086511 | -0.0075025 | -0.00061526 | -10.0342 | -8.3542 | -10.7712 | -9.6313 | -9.5215 | -10.7758 | -9.5581 | -9.6405 | 111.9232 | -10.7391 | -10.3546 | -10.3821 | -10.6613 | -10.5331 | -0.11444 | -120.2271 | -121.5042 | 1.1353 | 1.0986 | -0.11902 | 1.2131 | -0.004578 | -0.082398 | 0.050354 | -122.2275 | 0.27466 | 0.1236 | -0.004578 | 0.20599 | 0.07782 | 1.2497 | 1.1398 | 0.35706 | 0.38452 | 2.417 | 122.6624 | 2.3026 | 122.58 | -122.644 | -122.612 | 1.0254 | 0.30212 | 0.62256 | 1.0162
4449.1719 | 122.6624 | -10.6888 | 111.882 | -0.11398 | -0.00066014 | 0.012465 | 0.0098715 | -0.00090783 | 5.5488e-05 | 0.0090534 | -0.016602 | 0.0017431 | 0.0021362 | 0.0034778 | -0.0034287 | -0.0057935 | 0.0030163 | -10.0113 | -8.3038 | -10.7666 | -9.4437 | -9.3475 | -10.7529 | -9.375 | -9.6176 | 111.9507 | -10.7391 | -10.3592 | -10.3912 | -10.6339 | -10.5423 | -0.07782 | -120.1859 | -121.3257 | 1.3412 | 1.3138 | -0.064087 | 1.3916 | 0.013733 | -0.050354 | 0.068665 | -122.2412 | 0.29755 | 0.14649 | 0.054932 | 0.19684 | 0.10529 | 1.4191 | 1.3229 | 0.3479 | 0.37994 | 2.4628 | 122.6898 | 2.3849 | 122.6395 | -122.6486 | -122.6212 | 1.2451 | 0.32959 | 0.67749 | 1.0712
4450.1719 | 122.6624 | -10.5423 | 111.9919 | -0.083466 | -0.0015145 | 0.011397 | 0.010299 | -0.00048063 | 5.5488e-05 | 0.0094806 | -0.025757 | 0.0025975 | -0.00064077 | 0.00091422 | -0.0021469 | -0.0064343 | 0.00045294 | -9.8648 | -8.2489 | -10.611 | -9.2972 | -9.2239 | -10.6339 | -9.3704 | -9.5123 | 112.0056 | -10.6567 | -10.2081 | -10.2264 | -10.5011 | -10.3912 | -0.068665 | -120.2408 | -121.2891 | 1.3184 | 1.1719 | -0.091553 | 1.2405 | -0.022888 | -0.11444 | 0.013733 | -122.2 | 0.31586 | 0.15106 | 0.041198 | 0.2655 | 0.15564 | 1.387 | 1.3138 | 0.4303 | 0.44861 | 2.3621 | 122.6624 | 2.2934 | 122.5479 | -122.6028 | -122.6486 | 1.2451 | 0.33417 | 0.67749 | 1.03
4451.1719 | 122.644 | -10.3638 | 112.1933 | -0.091095 | -0.0015145 | 0.0088332 | 0.0083761 | 0.00016017 | -0.00058531 | 0.0096942 | -0.0013428 | -0.00017945 | 0.0021362 | -0.0059216 | -0.0027877 | -0.0062207 | -0.0040333 | -9.6817 | -8.1802 | -10.4462 | -9.137 | -9.0271 | -10.4553 | -9.0729 | -9.3063 | 112.262 | -10.4462 | -10.0296 | -10.0845 | -10.3455 | -10.231 | -0.082397 | -120.3735 | -121.3303 | 1.3367 | 1.2909 | -0.091552 | 1.3733 | -0.009155 | -0.082397 | 0.068665 | -122.2229 | 0.27924 | 0.13275 | 0.018311 | 0.21515 | 0.10071 | 1.4191 | 1.3092 | 0.36163 | 0.41657 | 2.2659 | 122.7081 | 2.1835 | 122.6257 | -122.6395 | -122.6395 | 1.2268 | 0.33417 | 0.68207 | 1.0574
4452.1719 | 122.6578 | -10.1715 | 112.3947 | -0.091095 | -0.0019417 | 0.012038 | 0.0083761 | -0.00026703 | 5.5488e-05 | 0.0073444 | 0.016968 | 0.0017431 | -0.0012818 | 0.00091422 | -0.0025741 | -0.0053663 | -0.0012561 | -9.4894 | -8.0704 | -10.2676 | -8.9127 | -8.8165 | -10.2493 | -8.876 | -9.0866 | 112.4451 | -10.2356 | -9.8282 | -9.874 | -10.1257 | -10.0021 | -0.09613 | -120.4651 | -121.3074 | 1.355 | 1.2955 | -0.07782 | 1.3916 | 0.01831 | -0.064087 | 0.050354 | -122.2229 | 0.29755 | 0.16937 | 0.045777 | 0.23346 | 0.10986 | 1.4511 | 1.355 | 0.36163 | 0.40741 | 2.1973 | 122.6807 | 2.1011 | 122.6166 | -122.6624 | -122.6303 | 1.2589 | 0.34332 | 0.68207 | 1.0849
4453.1719 | 122.6761 | -9.9472 | 112.5504 | -0.11398 | -0.0013009 | 0.010756 | 0.0085897 | 0.00058737 | -0.0010125 | 0.005849 | -0.025757 | 0.00088875 | -0.0027772 | -0.00079478 | -0.0030013 | -0.0055799 | 0.0013073 | -9.2468 | -7.9559 | -10.0388 | -8.67 | -8.5236 | -9.9976 | -8.6334 | -8.812 | 112.6648 | -10.0159 | -9.5764 | -9.6405 | -9.8969 | -9.7824 | -0.091552 | -120.5063 | -121.2204 | 1.4236 | 1.3138 | -0.050354 | 1.4053 | 0.041198 | -0.068664 | 0.11444 | -122.1268 | 0.3067 | 0.16479 | 0.050354 | 0.23346 | 0.11902 | 1.5152 | 1.3687 | 0.37537 | 0.43945 | 2.0828 | 122.6807 | 1.9913 | 122.612 | -122.5891 | -122.5662 | 1.2772 | 0.37079 | 0.70038 | 1.1353
4454.1719 | 122.6898 | -9.7961 | 112.706 | -0.10635 | 0.00040806 | 0.014815 | 0.0098715 | -0.0011214 | -0.0020807 | 0.0079852 | 0.02002 | 0.0023839 | 0.00085443 | -0.00079478 | -0.0017197 | -0.0068615 | 0.00088014 | -9.1003 | -7.869 | -9.9106 | -8.5556 | -8.4183 | -10.0983 | -8.6609 | -8.6838 | 112.7518 | -9.9335 | -9.4345 | -9.5123 | -9.7824 | -9.6497 | -0.11444 | -120.575 | -121.2616 | 1.3779 | 1.1353 | -0.30212 | 1.2497 | -0.18768 | -0.13733 | 0.045776 | -122.1405 | 0.28381 | 0.14649 | 0.013733 | 0.28381 | 0.15106 | 1.4923 | 1.355 | 0.42114 | 0.49896 | 2.0416 | 122.6852 | 1.9272 | 122.5479 | -122.6166 | -122.6395 | 1.2405 | 0.36163 | 0.6958 | 1.1124
4455.1719 | 122.6624 | -9.8373 | 112.7106 | -0.098725 | -0.00066014 | 0.011183 | 0.0075217 | -0.0028304 | -0.00058531 | 0.0084124 | -0.010498 | 0.0025975 | -0.00042717 | -0.0033582 | -0.0027877 | -0.0064343 | -0.0027515 | -9.1644 | -7.8506 | -9.9106 | -8.5648 | -8.4732 | -9.8923 | -8.5144 | -8.7662 | 112.7792 | -9.906 | -9.4803 | -9.5078 | -9.7961 | -9.6771 | -0.073242 | -120.5612 | -121.2753 | 1.3641 | 1.3229 | -0.054932 | 1.3962 | 0.01831 | -0.068665 | 0.068665 | -122.1909 | 0.32959 | 0.16022 | 0.041198 | 0.22888 | 0.10986 | 1.4374 | 1.3458 | 0.39825 | 0.42572 | 2.0599 | 122.6852 | 1.9867 | 122.6166 | -122.6212 | -122.6166 | 1.2726 | 0.35706 | 0.67291 | 1.0712
4456.1719 | 122.6669 | -9.6313 | 112.9028 | -0.098725 | 0.00019446 | 0.010542 | 0.0073081 | 0.001442 | 0.00069649 | 0.009267 | -0.0074462 | 0.00067495 | -0.00064077 | -0.0086988 | -0.0030013 | -0.0064343 | 0.00088014 | -8.9722 | -7.7225 | -9.7137 | -8.3817 | -8.2764 | -9.7229 | -8.3542 | -8.5831 | 112.9852 | -9.7321 | -9.2972 | -9.3475 | -9.613 | -9.5123 | -0.082397 | -120.6253 | -121.2845 | 1.355 | 1.2772 | -0.091552 | 1.3596 | -0.009155 | -0.10071 | 0.082397 | -122.2 | 0.28381 | 0.11902 | 0.018311 | 0.21973 | 0.11902 | 1.4374 | 1.3321 | 0.38452 | 0.43488 | 1.9913 | 122.7173 | 1.9089 | 122.6166 | -122.6166 | -122.6349 | 1.2497 | 0.33417 | 0.65918 | 1.0483
4457.1719 | 122.6715 | -9.4666 | 113.0768 | -0.13687 | 0.00019446 | 0.011183 | 0.0070943 | -0.0015488 | 5.5488e-05 | 0.0064898 | -0.0074462 | 0.0015295 | -0.0019226 | -0.00079478 | -0.0032151 | -0.0066479 | -0.00082886 | -8.7982 | -7.6035 | -9.5489 | -8.1985 | -8.0978 | -9.5581 | -8.1299 | -8.4091 | 113.1134 | -9.5352 | -9.1049 | -9.1553 | -9.4345 | -9.3246 | -0.082397 | -120.6802 | -121.2753 | 1.3687 | 1.3367 | -0.091552 | 1.4191 | -0.009155 | -0.068664 | 0.036621 | -122.1817 | 0.31128 | 0.14191 | 0.032044 | 0.21057 | 0.10071 | 1.4511 | 1.3504 | 0.37994 | 0.4303 | 1.9455 | 122.6486 | 1.8631 | 122.58 | -122.6257 | -122.612 | 1.268 | 0.36163 | 0.66833 | 1.0574
4458.1719 | 122.6578 | -9.3018 | 113.269 | -0.098725 | -0.00044654 | 0.011824 | 0.0060263 | -0.0013352 | -0.0033625 | 0.0077716 | -0.01355 | 0.0021703 | 0.001068 | 0.00048702 | -0.0025741 | -0.0055799 | -0.0044605 | -8.6243 | -7.4753 | -9.3796 | -8.0109 | -7.8964 | -9.3658 | -7.9559 | -8.2169 | 113.324 | -9.3704 | -8.9172 | -8.9996 | -9.2743 | -9.1644 | -0.07782 | -120.7443 | -121.2799 | 1.4053 | 1.3458 | -0.064087 | 1.4236 | 0.013733 | -0.068664 | 0.054932 | -122.1863 | 0.30212 | 0.13733 | 0.027466 | 0.20599 | 0.09613 | 1.4832 | 1.3687 | 0.37079 | 0.45319 | 1.9043 | 122.6944 | 1.8265 | 122.6257 | -122.6486 | -122.6395 | 1.2909 | 0.38452 | 0.67749 | 1.0849
4459.1719 | 122.6761 | -9.1461 | 113.3881 | -0.12924 | -0.0013009 | 0.014174 | 0.0064535 | -0.0028304 | -0.00058531 | 0.0073444 | -0.0074462 | 0.0017431 | 0.0012818 | 0.0026232 | -0.0027877 | -0.0064343 | 0.00088014 | -8.4686 | -7.3471 | -9.2011 | -7.8278 | -7.7042 | -9.1782 | -7.782 | -8.0338 | 113.4888 | -9.2285 | -8.7433 | -8.8394 | -9.1095 | -8.9813 | -0.054932 | -120.7352 | -121.2158 | 1.442 | 1.3641 | -0.032044 | 1.4191 | 0.022888 | -0.082398 | 0.10071 | -122.1313 | 0.3067 | 0.16479 | 0.036621 | 0.24719 | 0.11902 | 1.4969 | 1.3733 | 0.3891 | 0.48523 | 1.8539 | 122.7173 | 1.799 | 122.6349 | -122.5891 | -122.6166 | 1.3184 | 0.40283 | 0.67749 | 1.1124
4460.1719 | 122.7448 | -8.9905 | 113.4796 | -0.12161 | -1.9142e-05 | 0.012892 | 0.0094443 | 0.0016556 | -0.0022943 | 0.0090534 | -0.044067 | 0.0011023 | -0.0014954 | 0.002196 | -0.0036423 | -0.0060071 | -0.0016833 | -8.2901 | -7.2144 | -9.0454 | -7.6492 | -7.5439 | -9.0179 | -7.6401 | -7.8873 | 113.6398 | -9.0637 | -8.5602 | -8.6426 | -8.9081 | -8.7891 | -0.054931 | -120.694 | -121.1288 | 1.4465 | 1.3504 | -0.027465 | 1.4053 | 0.027466 | -0.073242 | 0.16022 | -122.0398 | 0.3479 | 0.20142 | 0.082398 | 0.27466 | 0.15564 | 1.5015 | 1.3962 | 0.42114 | 0.50354 | 1.8311 | 122.7036 | 1.7761 | 122.6303 | -122.525 | -122.5433 | 1.3412 | 0.4303 | 0.70038 | 1.1032
4461.1719 | 122.699 | -8.7753 | 113.7634 | -0.13687 | -0.00087374 | 0.012251 | 0.0088033 | 0.0029374 | -0.00058531 | 0.01119 | -0.071533 | 0.00088875 | 0.001068 | 0.0019824 | -0.0025741 | -0.0060071 | -0.0036059 | -8.0704 | -7.0267 | -8.8531 | -7.4478 | -7.338 | -8.8211 | -7.402 | -7.6721 | 113.855 | -8.8577 | -8.3176 | -8.4229 | -8.7021 | -8.5831 | -0.077819 | -120.7901 | -121.2112 | 1.4374 | 1.3733 | -0.045776 | 1.4511 | 0.032043 | -0.082397 | 0.091552 | -122.081 | 0.35248 | 0.19226 | 0.073243 | 0.27466 | 0.15564 | 1.5152 | 1.4053 | 0.43487 | 0.54016 | 1.8265 | 122.7127 | 1.7487 | 122.6303 | -122.6166 | -122.6212 | 1.3275 | 0.45776 | 0.70496 | 1.1032
4462.1719 | 122.699 | -8.6151 | 113.9648 | -0.068207 | -0.0023691 | 0.012465 | 0.0083761 | -0.001976 | -0.0020807 | 0.0081988 | 0.013916 | 0.0017431 | 0.00021363 | 0.00048702 | -0.0021469 | -0.0070753 | -0.00082886 | -7.9559 | -6.8344 | -8.6792 | -7.2739 | -7.1732 | -8.638 | -7.2418 | -7.5623 | 114.0335 | -8.67 | -8.2031 | -8.2764 | -8.5464 | -8.432 | -0.064087 | -120.7993 | -121.2387 | 1.442 | 1.3733 | -0.022888 | 1.4374 | 0.041199 | -0.054932 | 0.068664 | -122.168 | 0.33874 | 0.1831 | 0.068664 | 0.23804 | 0.1236 | 1.506 | 1.4053 | 0.39368 | 0.46692 | 1.8448 | 122.7036 | 1.7807 | 122.6486 | -122.644 | -122.6349 | 1.3412 | 0.41199 | 0.65918 | 1.0529
4463.1719 | 122.6944 | -8.3679 | 114.1891 | -0.091095 | -0.0015145 | 0.01161 | 0.0081625 | -0.0030442 | -0.0014399 | 0.007558 | -0.0043946 | 0.00046135 | 0.00042723 | 0.00048702 | -0.0030013 | -0.0064343 | 0.0028027 | -7.7087 | -6.6147 | -8.4274 | -7.045 | -6.9214 | -8.4 | -6.9672 | -7.3563 | 114.267 | -8.4457 | -7.9559 | -8.0383 | -8.3038 | -8.2031 | -0.059509 | -120.8038 | -121.2341 | 1.4465 | 1.4008 | -0.032043 | 1.4603 | 0.027466 | -0.07782 | 0.07782 | -122.1451 | 0.32959 | 0.16479 | 0.064087 | 0.24262 | 0.14191 | 1.506 | 1.3824 | 0.40741 | 0.48981 | 1.8127 | 122.7127 | 1.7532 | 122.6349 | -122.6166 | -122.6349 | 1.3229 | 0.41199 | 0.65918 | 1.0117
4464.1719 | 122.6944 | -8.1161 | 114.4684 | -0.12161 | -0.00066014 | 0.012679 | 0.0075217 | -0.0011214 | 0.00026909 | 0.0079852 | -0.022705 | 0.00088875 | -0.0012818 | -0.00036738 | -0.0030013 | -0.0072889 | -0.0012561 | -7.4615 | -6.3995 | -8.2077 | -6.7795 | -6.6467 | -8.1619 | -6.7245 | -7.1091 | 114.5096 | -8.1894 | -7.7087 | -7.7911 | -8.0612 | -7.9514 | -0.091553 | -120.8679 | -121.2479 | 1.4694 | 1.3916 | -0.045776 | 1.4832 | 0.045777 | -0.073242 | 0.041199 | -122.1771 | 0.32501 | 0.16479 | 0.054932 | 0.23804 | 0.12817 | 1.561 | 1.4282 | 0.39825 | 0.48065 | 1.8082 | 122.699 | 1.7166 | 122.6257 | -122.6761 | -122.6578 | 1.3367 | 0.40741 | 0.6546 | 1.0071
4465.1719 | 122.7036 | -7.9514 | 114.6469 | -0.12161 | -0.00066014 | 0.012892 | 0.0098715 | -0.0034714 | -0.0012261 | 0.007558 | -0.0074462 | 0.00067495 | -0.0014954 | -0.0035718 | -0.0051377 | -0.0070753 | 0.0036571 | -7.283 | -6.2347 | -8.0109 | -6.5689 | -6.459 | -7.9697 | -6.5369 | -6.8939 | 114.7202 | -8.0338 | -7.5302 | -7.6263 | -7.8735 | -7.7774 | -0.059509 | -120.8817 | -121.2158 | 1.4923 | 1.4145 | -0.018311 | 1.474 | 0.041198 | -0.082397 | 0.073242 | -122.1771 | 0.32501 | 0.17395 | 0.07782 | 0.25635 | 0.16022 | 1.5518 | 1.442 | 0.40741 | 0.50354 | 1.7761 | 122.7539 | 1.7166 | 122.6715 | -122.6578 | -122.6807 | 1.3824 | 0.42114 | 0.66834 | 1.0574
4466.1719 | 122.6944 | -7.7728 | 114.7888 | -0.10635 | 0.00040806 | 0.010542 | 0.0081625 | -0.0013352 | 0.00048269 | 0.0062762 | -0.034912 | 0.0034521 | 0.00085443 | 0.0041186 | -0.00022431 | -0.0079297 | -0.00040166 | -7.1411 | -6.0974 | -7.8827 | -6.4133 | -6.2576 | -7.8186 | -6.3721 | -6.72 | 114.8483 | -7.8552 | -7.3563 | -7.4478 | -7.7042 | -7.5943 | -0.10986 | -120.8862 | -121.2021 | 1.5152 | 1.4008 | -0.045777 | 1.5106 | 0.064086 | -0.082398 | 0.05951 | -122.1451 | 0.32501 | 0.17853 | 0.068664 | 0.26093 | 0.15106 | 1.6251 | 1.4694 | 0.40741 | 0.49896 | 1.7853 | 122.7036 | 1.6754 | 122.6212 | -122.6715 | -122.644 | 1.3596 | 0.41657 | 0.63171 | 1.0529
4467.1719 | 122.7402 | -7.663 | 114.8895 | -0.098725 | 0.0010489 | 0.012251 | 0.0073081 | 0.00016017 | -0.00079891 | 0.0094806 | -0.059326 | 0.0017431 | -0.0012818 | -0.00015378 | -0.0023605 | -0.0045117 | -0.0025379 | -6.9717 | -5.9601 | -7.7408 | -6.2714 | -6.1386 | -7.6904 | -6.2347 | -6.5872 | 114.9719 | -7.7362 | -7.2052 | -7.3059 | -7.5714 | -7.4432 | -0.07782 | -120.8496 | -121.1609 | 1.5244 | 1.4282 | -0.027466 | 1.506 | 0.050354 | -0.073242 | 0.082398 | -122.0947 | 0.35706 | 0.21973 | 0.091553 | 0.29297 | 0.16479 | 1.6022 | 1.4694 | 0.4303 | 0.53101 | 1.7807 | 122.7081 | 1.7029 | 122.6349 | -122.6303 | -122.6257 | 1.3916 | 0.45776 | 0.69122 | 1.0757
4468.1719 | 122.731 | -7.4341 | 115.1184 | -0.075836 | -0.00023294 | 0.012251 | 0.0090169 | 0.0012284 | -0.00058531 | 0.0071308 | -0.041016 | 0.0019567 | 0.00064083 | 5.9824e-05 | -0.0030013 | -0.0060071 | -0.0025379 | -6.7703 | -5.7449 | -7.5302 | -6.0699 | -5.9463 | -7.4753 | -6.0287 | -6.3766 | 115.1916 | -7.5348 | -6.9855 | -7.077 | -7.3517 | -7.2144 | -0.09613 | -120.8633 | -121.1884 | 1.4877 | 1.4053 | -0.041199 | 1.5015 | 0.054931 | -0.10071 | 0.073242 | -122.1039 | 0.35706 | 0.21973 | 0.082397 | 0.32043 | 0.18311 | 1.5839 | 1.4603 | 0.45776 | 0.54932 | 1.7853 | 122.7264 | 1.6891 | 122.6257 | -122.6486 | -122.6532 | 1.3641 | 0.44861 | 0.66376 | 1.0574
4469.1719 | 122.7081 | -7.338 | 115.21 | -0.15213 | -0.00044654 | 0.011397 | 0.0092307 | -0.0013352 | 0.00048269 | 0.0090534 | -0.01355 | 0.0017431 | -0.0014954 | 0.0015552 | -0.00065151 | -0.0057935 | -0.00018806 | -6.6971 | -5.6625 | -7.4112 | -5.9692 | -5.8228 | -7.3654 | -5.9509 | -6.2988 | 115.2878 | -7.4478 | -6.9122 | -6.9992 | -7.2693 | -7.1823 | -0.073242 | -120.8725 | -121.1792 | 1.5152 | 1.387 | -0.027465 | 1.4603 | 0.045777 | -0.10986 | 0.07782 | -122.1222 | 0.33874 | 0.15564 | 0.068665 | 0.2655 | 0.17853 | 1.5884 | 1.442 | 0.44861 | 0.53558 | 1.7487 | 122.7356 | 1.6754 | 122.6257 | -122.6212 | -122.6578 | 1.3687 | 0.42572 | 0.64087 | 1.0391
4470.1719 | 122.7081 | -7.1915 | 115.4068 | -0.12924 | -0.0013009 | 0.010115 | 0.0079489 | -5.343e-05 | -0.0012261 | 0.0073444 | -0.01355 | 0.0017431 | 0.00085443 | 0.00027342 | -0.0025741 | -0.0060071 | 0.0013073 | -6.4728 | -5.5206 | -7.2922 | -5.7861 | -5.6671 | -7.2189 | -5.7678 | -6.1478 | 115.4526 | -7.283 | -6.752 | -6.8481 | -7.1091 | -7.0038 | -0.10071 | -120.9274 | -121.1929 | 1.5244 | 1.4236 | -0.027466 | 1.5244 | 0.073242 | -0.091553 | 0.045777 | -122.1588 | 0.34332 | 0.18768 | 0.082397 | 0.27924 | 0.17395 | 1.6251 | 1.506 | 0.43487 | 0.53101 | 1.7715 | 122.7356 | 1.6708 | 122.644 | -122.699 | -122.6898 | 1.4053 | 0.43945 | 0.71869 | 1.0437
4471.1719 | 122.7219 | -7.1274 | 115.4663 | -0.13687 | -0.00066014 | 0.012465 | 0.0073081 | 0.0020828 | -0.0012261 | 0.0096942 | -0.041016 | 0.00024775 | 0.0012818 | -0.0020764 | -0.0034287 | -0.0042981 | -0.0018971 | -6.4499 | -5.4199 | -7.1869 | -5.8456 | -5.658 | -6.9946 | -5.6213 | -6.0379 | 115.5212 | -7.2006 | -6.6559 | -6.7612 | -6.9992 | -6.9168 | -0.05951 | -120.8862 | -121.312 | 1.4694 | 1.506 | 0.13275 | 1.5656 | 0.19226 | -0.073243 | 0.054931 | -122.1222 | 0.36621 | 0.21057 | 0.12817 | 0.28381 | 0.20142 | 1.5289 | 1.3412 | 0.43945 | 0.54474 | 1.767 | 122.7219 | 1.7075 | 122.6486 | -122.6532 | -122.6669 | 1.2817 | 0.4715 | 0.67749 | 1.0895
4472.1719 | 122.7676 | -6.9031 | 115.6677 | -0.091095 | 0.00019446 | 0.01097 | 0.0083761 | 0.0012284 | -0.0020807 | 0.0090534 | -0.041016 | 0.0011023 | -0.0023498 | 0.002196 | -0.0015061 | -0.0051527 | 0.0017345 | -6.2302 | -5.2139 | -6.9763 | -5.4932 | -5.3513 | -6.9031 | -5.452 | -5.8411 | 115.7318 | -6.9901 | -6.4407 | -6.4911 | -6.8161 | -6.7062 | -0.073242 | -120.8817 | -121.1609 | 1.5518 | 1.4511 | 0 | 1.5244 | 0.073242 | -0.086975 | 0.064087 | -122.1085 | 0.41199 | 0.19684 | 0.086975 | 0.28381 | 0.17395 | 1.6251 | 1.4832 | 0.49896 | 0.54932 | 1.7624 | 122.7219 | 1.6891 | 122.6349 | -122.644 | -122.6578 | 1.4099 | 0.46234 | 0.67291 | 1.062
4473.1719 | 122.7356 | -6.8298 | 115.7272 | -0.13687 | -0.00044654 | 0.014601 | 0.0094443 | 0.0012284 | -0.0022943 | 0.009267 | -0.047119 | 0.00024775 | 0.0019226 | -0.00036738 | -0.0025741 | -0.0064343 | 2.554e-05 | -6.1478 | -5.1453 | -6.9122 | -5.4291 | -5.2963 | -6.8573 | -5.3787 | -5.7861 | 115.8188 | -6.926 | -6.3583 | -6.4545 | -6.7383 | -6.6238 | -0.082397 | -120.8725 | -121.1563 | 1.5335 | 1.4511 | -0.027466 | 1.5335 | 0.054931 | -0.09613 | 0.091553 | -122.0856 | 0.37537 | 0.20599 | 0.091553 | 0.30212 | 0.18768 | 1.6159 | 1.4832 | 0.4715 | 0.56763 | 1.767 | 122.7448 | 1.6846 | 122.6486 | -122.6395 | -122.6532 | 1.4008 | 0.4715 | 0.68207 | 1.0437
4474.1719 | 122.7585 | -6.5689 | 115.9653 | -0.12924 | 0.00019446 | 0.011183 | 0.0083761 | 0.0044328 | 0.00026909 | 0.0071308 | -0.047119 | -0.00060665 | 0.001068 | 0.0015552 | -0.00065151 | -0.0042981 | -0.0021107 | -5.896 | -4.8935 | -6.6605 | -5.1682 | -5.0308 | -6.5918 | -5.1178 | -5.5756 | 116.0522 | -6.6879 | -6.1066 | -6.2119 | -6.4774 | -6.3721 | -0.091552 | -120.8588 | -121.1334 | 1.5381 | 1.4511 | -0.022888 | 1.5427 | 0.068664 | -0.11902 | 0.086975 | -122.0718 | 0.35706 | 0.19684 | 0.091553 | 0.31586 | 0.21057 | 1.6296 | 1.4923 | 0.47607 | 0.58136 | 1.767 | 122.7402 | 1.6754 | 122.6212 | -122.6257 | -122.6532 | 1.4008 | 0.46234 | 0.67291 | 0.99335
4475.1719 | 122.6669 | -6.4224 | 116.185 | -0.037689 | -0.0038643 | 0.010756 | 0.0083761 | -0.0017624 | -0.0018671 | 0.0099078 | -0.089844 | 0.0032385 | 0.0021362 | 0.0015552 | -0.0038559 | -0.0051527 | -0.00040166 | -5.7907 | -4.6829 | -6.5231 | -5.0858 | -4.9713 | -6.5186 | -5.04 | -5.4794 | 116.2903 | -6.5048 | -5.9921 | -6.102 | -6.3904 | -6.2714 | -0.10071 | -120.8679 | -121.2708 | 1.4511 | 1.3824 | -0.096131 | 1.4832 | 0.004577 | -0.082398 | 0.10529 | -122.1771 | 0.32043 | 0.15106 | 0.032043 | 0.23346 | 0.11444 | 1.5518 | 1.4374 | 0.40283 | 0.5127 | 1.8402 | 122.7951 | 1.7395 | 122.7127 | -122.7081 | -122.6898 | 1.3367 | 0.4303 | 0.63171 | 0.94299
4476.1719 | 122.7493 | -6.1523 | 116.4276 | -0.15976 | 0.00083526 | 0.012892 | 0.0081625 | -0.0017624 | 0.00026909 | 0.0073444 | -0.034912 | 0.00067495 | -0.0025636 | -0.0031446 | -1.0706e-05 | -0.0036573 | 0.0017345 | -5.571 | -4.5181 | -6.3171 | -4.7928 | -4.6417 | -6.2256 | -4.7241 | -5.1544 | 116.4642 | -6.2897 | -5.7037 | -5.7816 | -6.0379 | -5.9418 | -0.16479 | -120.9457 | -121.2204 | 1.5106 | 1.4282 | -0.073242 | 1.593 | 0.091553 | -0.13733 | 0.036621 | -122.1313 | 0.37079 | 0.21057 | 0.11444 | 0.3479 | 0.25177 | 1.6754 | 1.5244 | 0.50812 | 0.58594 | 1.799 | 122.7539 | 1.6342 | 122.6166 | -122.7448 | -122.7173 | 1.3596 | 0.44861 | 0.58136 | 0.99793
4477.1719 | 122.7493 | -6.0883 | 116.5009 | -0.098725 | -0.0025827 | 0.010542 | 0.0090169 | -0.0038986 | -0.0014399 | 0.010549 | -0.03186 | 0.00067495 | 0.0012818 | 0.002196 | -0.0042831 | -0.0072889 | -0.00018806 | -5.3879 | -4.3625 | -6.0608 | -4.6509 | -4.4998 | -5.9921 | -4.6051 | -5.0079 | 116.6428 | -6.0883 | -5.6076 | -5.7266 | -5.9601 | -5.8502 | 0.027466 | -120.8633 | -121.1517 | 1.5884 | 1.4832 | 0.096131 | 1.4557 | 0.068665 | 0 | 0.14191 | -122.1085 | 0.36163 | 0.23804 | 0.12817 | 0.23804 | 0.12817 | 1.561 | 1.4099 | 0.36163 | 0.48065 | 1.6983 | 122.731 | 1.7258 | 122.731 | -122.5616 | -122.5891 | 1.4374 | 0.48065 | 0.70038 | 1.0803
4478.1719 | 122.731 | -5.7907 | 116.7938 | -0.091095 | -0.0019417 | 0.012465 | 0.0092307 | 0.00037377 | -0.0020807 | 0.0094806 | -0.03186 | 0.0015295 | 0.0012818 | 0.0047594 | -0.0027877 | -0.0049389 | -0.0016833 | -5.1956 | -4.0741 | -5.896 | -4.4037 | -4.2618 | -5.8319 | -4.3488 | -4.834 | 116.89 | -5.8823 | -5.3238 | -5.4199 | -5.6992 | -5.571 | -0.10529 | -120.8679 | -121.1975 | 1.5289 | 1.442 | -0.041199 | 1.5472 | 0.064087 | -0.091553 | 0.096131 | -122.1176 | 0.37079 | 0.21973 | 0.091552 | 0.31128 | 0.18311 | 1.6342 | 1.4923 | 0.46234 | 0.55847 | 1.8219 | 122.7722 | 1.7166 | 122.6807 | -122.6898 | -122.6761 | 1.387 | 0.46692 | 0.59509 | 0.95673
4479.1719 | 122.699 | -5.7632 | 116.8762 | -0.075836 | -0.00044654 | 0.013106 | 0.0092307 | -0.00048063 | -0.00037171 | 0.011403 | -0.037964 | 0.00046135 | -0.001709 | -0.00229 | -0.0025741 | -0.0049389 | -0.0014697 | -5.0766 | -4.0009 | -5.7632 | -4.3625 | -4.2618 | -5.8182 | -4.3213 | -4.8203 | 116.9449 | -5.8731 | -5.3009 | -5.4016 | -5.69 | -5.5756 | 0 | -120.8771 | -121.2387 | 1.5015 | 1.442 | -0.054931 | 1.442 | -0.054931 | -0.10986 | 0.068664 | -122.1771 | 0.36163 | 0.18768 | 0.073243 | 0.29755 | 0.18311 | 1.5015 | 1.4008 | 0.4715 | 0.57221 | 1.7624 | 122.818 | 1.7624 | 122.7081 | -122.6395 | -122.7493 | 1.4008 | 0.46234 | 0.68665 | 0.94299
4480.1719 | 122.6852 | -5.7312 | 116.8854 | -0.10635 | -0.00066014 | 0.015456 | 0.0096579 | -0.00048063 | 0.0011237 | 0.0084124 | -0.074585 | 0.0025975 | 0.00064083 | 0.0036914 | -0.0021469 | -0.0053663 | -0.0023243 | -5.0995 | -3.9551 | -5.7358 | -4.3167 | -4.1702 | -5.7999 | -4.2618 | -4.8203 | 116.9724 | -5.8548 | -5.3192 | -5.4291 | -5.69 | -5.5756 | -0.004578 | -120.8405 | -121.2021 | 1.561 | 1.4694 | -0.068665 | 1.474 | -0.064087 | -0.1236 | 0.086975 | -122.2046 | 0.30212 | 0.15564 | 0.041199 | 0.27923 | 0.16479 | 1.5656 | 1.4191 | 0.42572 | 0.53558 | 1.7807 | 122.8271 | 1.7761 | 122.7036 | -122.6212 | -122.7402 | 1.4145 | 0.41199 | 0.63171 | 0.91095
4481.1719 | 122.6166 | -5.658 | 117.0822 | -0.075836 | -0.0021555 | 0.013533 | 0.010726 | -0.0026168 | -0.00079891 | 0.0071308 | -0.086792 | 0.00067495 | -0.0010682 | 0.00027342 | -0.0019333 | -0.0053663 | -0.0036059 | -5.04 | -3.8773 | -5.7724 | -4.2892 | -4.1748 | -5.7632 | -4.2252 | -4.7836 | 117.0914 | -5.7587 | -5.2551 | -5.3696 | -5.6213 | -5.452 | -0.11444 | -120.9595 | -121.3715 | 1.4832 | 1.4328 | -0.10529 | 1.5472 | 0.009155 | -0.10071 | 0.009156 | -122.3373 | 0.28839 | 0.20599 | 0.036621 | 0.3067 | 0.13733 | 1.5976 | 1.4832 | 0.3891 | 0.50354 | 1.8951 | 122.85 | 1.7807 | 122.7493 | -122.8546 | -122.8409 | 1.3687 | 0.40283 | 0.61798 | 0.87433
4482.1719 | 122.6166 | -5.4703 | 117.1875 | -0.098725 | -0.0010873 | 0.012251 | 0.010085 | -0.0013352 | -0.00058531 | 0.0062762 | -0.059326 | 0.00067495 | 0.00021363 | -0.0076306 | -0.0015061 | -0.0057935 | 0.0013073 | -4.8752 | -3.6804 | -5.571 | -4.0787 | -3.9917 | -5.603 | -4.0146 | -4.6051 | 117.2653 | -5.5801 | -5.0446 | -5.1956 | -5.4611 | -5.3421 | -0.10071 | -120.8679 | -121.2662 | 1.4786 | 1.4557 | -0.13275 | 1.5564 | -0.032043 | -0.10986 | 0.07782 | -122.2321 | 0.27466 | 0.12817 | 0.009155 | 0.23804 | 0.11902 | 1.5793 | 1.4923 | 0.38452 | 0.53558 | 1.8906 | 122.8455 | 1.7899 | 122.7356 | -122.7585 | -122.7676 | 1.3916 | 0.42572 | 0.59509 | 0.86517
4483.1719 | 122.6395 | -5.2414 | 117.3981 | -0.098725 | -0.0010873 | 0.011183 | 0.0073081 | 0.00080117 | -0.00015811 | 0.0062762 | 0.047485 | 0.0030249 | 0.0019226 | -0.00464 | -0.0017197 | -0.0068615 | 0.0028027 | -4.6509 | -3.511 | -5.3101 | -3.9047 | -3.717 | -5.5115 | -3.7949 | -4.3625 | 117.5171 | -5.3284 | -4.8203 | -4.9438 | -5.2094 | -5.0858 | -0.068665 | -120.9091 | -121.3028 | 1.5244 | 1.4465 | -0.27008 | 1.5152 | -0.20142 | -0.086975 | 0.11902 | -122.2183 | 0.29755 | 0.15564 | 0.032043 | 0.24262 | 0.11902 | 1.593 | 1.4053 | 0.38452 | 0.50812 | 1.799 | 122.8455 | 1.7303 | 122.7585 | -122.7081 | -122.7264 | 1.3367 | 0.42114 | 0.59051 | 0.87891
4484.1719 | 122.6166 | -5.1682 | 117.5079 | -0.17502 | 0.00040806 | 0.012038 | 0.010726 | 0.00016017 | -0.0018671 | 0.011403 | -0.022705 | 0.0032385 | 0.00085443 | 0.0058276 | -0.0021469 | -0.0057935 | 0.0019483 | -4.5593 | -3.4149 | -5.2505 | -3.8406 | -3.7308 | -5.2414 | -3.7765 | -4.2801 | 117.5629 | -5.2689 | -4.7653 | -4.8706 | -5.2094 | -5.0125 | -0.082397 | -120.9229 | -121.3486 | 1.4374 | 1.3916 | -0.073242 | 1.474 | 0.009155 | -0.10071 | 0.054931 | -122.2733 | 0.29755 | 0.15564 | -0.041199 | 0.25635 | 0.059509 | 1.5198 | 1.4099 | 0.39825 | 0.50354 | 1.8356 | 122.8317 | 1.7532 | 122.731 | -122.7585 | -122.7768 | 1.3275 | 0.40283 | 0.60883 | 0.88806
4485.1719 | 122.612 | -5.04 | 117.6315 | -0.083466 | -0.0015145 | 0.01161 | 0.0088033 | -0.00026703 | 0.00048269 | 0.010121 | -0.037964 | 0.0025975 | 0.0023498 | 0.0024096 | -0.0025741 | -0.0040845 | -0.0029651 | -4.4586 | -3.3051 | -5.1086 | -3.717 | -3.6209 | -5.1407 | -3.653 | -4.1656 | 117.7139 | -5.127 | -4.6555 | -4.747 | -5.0217 | -4.8889 | -0.068665 | -120.9366 | -121.3486 | 1.4191 | 1.387 | -0.10071 | 1.4557 | -0.032043 | -0.086975 | 0.082397 | -122.287 | 0.29297 | 0.15106 | 0.018311 | 0.23804 | 0.10529 | 1.4877 | 1.3916 | 0.37994 | 0.4715 | 1.8036 | 122.8409 | 1.7349 | 122.7539 | -122.7402 | -122.7585 | 1.3229 | 0.38452 | 0.58136 | 0.87433
4486.1719 | 122.6349 | -4.8248 | 117.8604 | -0.052948 | -1.9142e-05 | 0.013747 | 0.011153 | -0.0017624 | 0.0013373 | 0.0099078 | -0.025757 | -0.00017945 | 0.001068 | 0.00048702 | -0.0036423 | -0.0094251 | 0.0036571 | -4.2343 | -3.0991 | -4.9118 | -3.4653 | -3.36 | -4.8889 | -3.4103 | -3.9917 | 117.9428 | -4.9118 | -4.4678 | -4.5181 | -4.8294 | -4.6692 | -0.086975 | -120.9595 | -121.3257 | 1.4648 | 1.4145 | -0.064087 | 1.5015 | 0.022888 | -0.086975 | 0.082397 | -122.3282 | 0.3067 | 0.15564 | -0.004578 | 0.24261 | 0.082397 | 1.5518 | 1.4465 | 0.39368 | 0.44403 | 1.8127 | 122.8546 | 1.7258 | 122.7676 | -122.7722 | -122.7722 | 1.3596 | 0.35706 | 0.59051 | 0.83313
4487.1719 | 122.7539 | -4.628 | 118.0252 | -0.014801 | 0.00083526 | 0.011397 | 0.0070943 | -0.0026168 | -0.0016535 | 0.0054218 | 0.096313 | 0.0015295 | 0.00064083 | 0.00027342 | -0.0047103 | -0.0079297 | -0.0010425 | -3.9871 | -2.9434 | -4.6967 | -3.1723 | -3.0212 | -4.5639 | -3.035 | -3.7994 | 118.0435 | -4.7241 | -4.184 | -4.2114 | -4.4678 | -4.3991 | -0.068664 | -120.9686 | -121.1975 | 1.6068 | 1.593 | 0.064087 | 1.6617 | 0.13275 | -0.09613 | 0.01831 | -122.2092 | 0.41656 | 0.22888 | 0.16022 | 0.32501 | 0.25635 | 1.6754 | 1.5244 | 0.51269 | 0.54016 | 1.7532 | 122.7676 | 1.6846 | 122.6715 | -122.7219 | -122.7493 | 1.4557 | 0.44403 | 0.64087 | 0.82855
4488.1719 | 122.6395 | -4.5502 | 118.1534 | -0.075836 | -0.0023691 | 0.012038 | 0.0083761 | 0.00016017 | -0.0014399 | 0.0099078 | -0.041016 | 0.0030249 | 0.00085443 | 0.0013416 | -0.0030013 | -0.0068615 | -0.00061526 | -3.923 | -2.7603 | -4.6097 | -3.1357 | -3.0167 | -4.5639 | -3.0808 | -3.6621 | 118.1992 | -4.6188 | -4.1565 | -4.2389 | -4.509 | -4.3854 | -0.059509 | -120.9137 | -121.2891 | 1.5335 | 1.4694 | -0.013733 | 1.5289 | 0.045776 | -0.068664 | 0.045777 | -122.3099 | 0.31128 | 0.16479 | 0.041199 | 0.23346 | 0.10986 | 1.593 | 1.474 | 0.37994 | 0.46234 | 1.8494 | 122.818 | 1.7899 | 122.7493 | -122.7631 | -122.7722 | 1.4145 | 0.39368 | 0.62714 | 0.88806
4489.1719 | 122.6807 | -4.4449 | 118.2266 | -0.068207 | -0.00066014 | 0.010329 | 0.0088033 | -0.00026703 | 0.00048269 | 0.0086262 | -0.028809 | 0.0023839 | 0.0012818 | 0.00070062 | -0.0027877 | -0.0064343 | 0.00045294 | -3.6804 | -2.6321 | -4.4998 | -2.9526 | -2.8198 | -4.4357 | -2.9022 | -3.5431 | 118.3319 | -4.5273 | -4.0421 | -4.1153 | -4.39 | -4.2664 | -0.054932 | -120.8588 | -121.1792 | 1.6251 | 1.5427 | 0.009155 | 1.5976 | 0.064087 | -0.082398 | 0.10528 | -122.2687 | 0.32959 | 0.17853 | 0.054931 | 0.26093 | 0.13733 | 1.68 | 1.5472 | 0.41199 | 0.48523 | 1.8677 | 122.8592 | 1.8127 | 122.7768 | -122.7264 | -122.7539 | 1.4923 | 0.40283 | 0.76447 | 0.90179
4490.1719 | 122.6395 | -4.3625 | 118.3228 | -0.0071715 | -0.00087374 | 0.014601 | 0.010512 | -0.00026703 | -0.0010125 | 0.0077716 | -0.037964 | 0.0025975 | -0.00064077 | 0.0096728 | -0.00022431 | -0.0075025 | -0.0025379 | -3.7491 | -2.5772 | -4.4357 | -2.948 | -2.8198 | -4.4083 | -2.8793 | -3.5019 | 118.4006 | -4.454 | -3.9688 | -4.0604 | -4.335 | -4.1885 | -0.073242 | -120.9 | -121.2708 | 1.5427 | 1.4832 | -0.045776 | 1.5564 | 0.027466 | -0.091553 | 0.07782 | -122.2916 | 0.30212 | 0.17395 | 0.027466 | 0.2655 | 0.11902 | 1.6159 | 1.4877 | 0.39368 | 0.48523 | 1.8585 | 122.8546 | 1.7853 | 122.7631 | -122.7585 | -122.7768 | 1.4145 | 0.39368 | 0.6134 | 0.8606
4491.1719 | 122.6807 | -4.2618 | 118.4052 | -0.12161 | -1.9142e-05 | 0.013533 | 0.010299 | -0.0015488 | -0.0010125 | 0.0069172 | -0.041016 | 0.0028113 | 0.0023498 | -0.0035718 | -0.0030013 | -0.0060071 | -0.0033923 | -3.6346 | -2.4033 | -4.2801 | -2.7924 | -2.6596 | -4.2847 | -2.742 | -3.3737 | 118.4692 | -4.3488 | -3.8589 | -3.9597 | -4.2114 | -4.0878 | -0.01831 | -120.8084 | -121.1975 | 1.6022 | 1.5198 | -0.022888 | 1.5381 | -0.004578 | -0.086975 | 0.064087 | -122.2641 | 0.30212 | 0.17395 | 0.050354 | 0.26092 | 0.13733 | 1.6205 | 1.4877 | 0.3891 | 0.48981 | 1.8768 | 122.818 | 1.8585 | 122.731 | -122.6852 | -122.7539 | 1.4694 | 0.40283 | 0.62714 | 0.88806
4492.1719 | 122.7173 | -4.1153 | 118.5471 | -0.091095 | 0.00062166 | 0.012465 | 0.0066671 | -0.0028304 | 0.00026909 | 0.0086262 | 0.041382 | 0.00024775 | 0.00021363 | 0.0015552 | -0.0012925 | -0.0081433 | 0.0019483 | -3.5065 | -2.3804 | -4.1885 | -2.6138 | -2.4399 | -4.0833 | -2.5406 | -3.1723 | 118.5928 | -4.2297 | -3.6758 | -3.7399 | -3.9825 | -3.891 | -0.073243 | -120.9274 | -121.1609 | 1.6754 | 1.5747 | 0.032043 | 1.648 | 0.10529 | -0.11444 | 0.045776 | -122.2229 | 0.37537 | 0.2243 | 0.13275 | 0.33874 | 0.24719 | 1.7487 | 1.5747 | 0.48981 | 0.55389 | 1.8082 | 122.8226 | 1.7349 | 122.7081 | -122.7356 | -122.7768 | 1.5015 | 0.43945 | 0.60882 | 0.94299
4493.1719 | 122.6898 | -3.9917 | 118.6798 | -0.098725 | -0.0019417 | 0.013747 | 0.0092307 | -5.343e-05 | -0.0020807 | 0.0084124 | -0.016602 | 0.0040929 | 0.00042723 | 0.0019824 | -0.0040695 | -0.0070753 | -0.0010425 | -3.3875 | -2.1835 | -4.0833 | -2.5223 | -2.3804 | -4.0009 | -2.4582 | -3.0304 | 118.8171 | -4.0558 | -3.5934 | -3.6621 | -3.9047 | -3.8223 | -0.091553 | -120.8633 | -121.2021 | 1.6113 | 1.5335 | -0.009155 | 1.6251 | 0.082398 | -0.064087 | 0.13733 | -122.2733 | 0.32959 | 0.16937 | 0.086975 | 0.23346 | 0.15106 | 1.7029 | 1.561 | 0.39368 | 0.46234 | 1.8997 | 122.8729 | 1.8082 | 122.8088 | -122.7631 | -122.7356 | 1.4694 | 0.39825 | 0.60425 | 0.9613
4494.1719 | 122.6486 | -3.8498 | 118.8766 | 0.008087 | -0.00066014 | 0.012038 | 0.0073081 | 0.0010148 | 0.00091009 | 0.010976 | 0.0047608 | 0.0021703 | 0.00085443 | -0.00079478 | -0.0034287 | -0.0077161 | -0.00061526 | -3.2822 | -2.092 | -3.9734 | -2.4216 | -2.2842 | -3.8727 | -2.3575 | -2.9984 | 118.8766 | -3.9825 | -3.4698 | -3.5477 | -3.7949 | -3.6667 | -0.1236 | -120.9686 | -121.2982 | 1.5656 | 1.4923 | -0.022889 | 1.6159 | 0.10071 | -0.13275 | 0 | -122.3465 | 0.30212 | 0.1831 | 0.054931 | 0.31586 | 0.18768 | 1.6891 | 1.5518 | 0.43488 | 0.51269 | 1.8814 | 122.8592 | 1.7578 | 122.7264 | -122.85 | -122.8592 | 1.4282 | 0.37994 | 0.56763 | 0.85144
4495.1719 | 122.7127 | -3.8177 | 118.8766 | -0.045319 | -0.0013009 | 0.010329 | 0.0064535 | 0.0012284 | -0.0010125 | 0.010121 | 0.016968 | 0.0013159 | 0.0025634 | -0.00036738 | -0.0038559 | -0.0060071 | 0.0013073 | -3.2318 | -2.0096 | -3.8864 | -2.3712 | -2.243 | -3.7949 | -2.2888 | -2.9572 | 118.9545 | -3.9276 | -3.4149 | -3.4653 | -3.7216 | -3.6072 | -0.068665 | -120.8862 | -121.2479 | 1.5747 | 1.5289 | 0.022888 | 1.5976 | 0.091553 | -0.10986 | 0.07782 | -122.2916 | 0.35248 | 0.21057 | 0.09613 | 0.32043 | 0.20599 | 1.6434 | 1.5152 | 0.46234 | 0.51269 | 1.8768 | 122.8821 | 1.8082 | 122.7722 | -122.7631 | -122.8043 | 1.4465 | 0.40283 | 0.58594 | 0.8606
4496.1719 | 122.6944 | -3.6987 | 118.9957 | -0.12924 | -0.0023691 | 0.0088332 | 0.0083761 | 0.003151 | -0.00079891 | 0.0060626 | -0.019653 | 0.0028113 | 0.0012818 | -0.0059216 | -0.0042831 | -0.0053663 | -0.00061526 | -3.1174 | -1.9226 | -3.7903 | -2.2659 | -2.1194 | -3.7033 | -2.1973 | -2.7466 | 119.0964 | -3.772 | -3.2822 | -3.3691 | -3.6163 | -3.5065 | -0.091553 | -120.9183 | -121.2616 | 1.5793 | 1.5015 | -0.004578 | 1.593 | 0.086975 | -0.073243 | 0.10071 | -122.2778 | 0.32959 | 0.19226 | 0.082397 | 0.2655 | 0.15564 | 1.6708 | 1.5244 | 0.40283 | 0.48981 | 1.8677 | 122.8683 | 1.7761 | 122.7951 | -122.7859 | -122.7676 | 1.4328 | 0.41656 | 0.58136 | 0.95215
4497.1719 | 122.731 | -3.598 | 119.0414 | -0.091095 | -0.00066014 | 0.012251 | 0.0073081 | -0.005394 | -0.00015811 | 0.0079852 | 0.056641 | 0.0019567 | 0.0025634 | -0.0048536 | -0.0015061 | -0.0060071 | 0.0030163 | -3.0304 | -1.8768 | -3.6804 | -2.1286 | -1.9684 | -3.5797 | -2.0462 | -2.7328 | 119.1101 | -3.6942 | -3.1769 | -3.2364 | -3.5065 | -3.4012 | -0.082398 | -120.9183 | -121.17 | 1.6296 | 1.5518 | 0.01831 | 1.6342 | 0.10071 | -0.096131 | 0.068664 | -122.2183 | 0.36163 | 0.19684 | 0.091552 | 0.29297 | 0.18768 | 1.712 | 1.5518 | 0.45776 | 0.51727 | 1.8036 | 122.8043 | 1.7212 | 122.7081 | -122.7219 | -122.7356 | 1.4694 | 0.42114 | 0.56763 | 0.86517
4498.1719 | 122.7081 | -3.5339 | 119.1605 | -0.03006 | -0.0010873 | 0.012251 | 0.0094443 | -0.00090783 | 5.5488e-05 | 0.011617 | -0.019653 | 0.0015295 | -0.00042717 | 0.0015552 | -0.0036423 | -0.0042981 | -0.0033923 | -2.9388 | -1.7441 | -3.6026 | -2.0508 | -1.9318 | -3.5202 | -2.0096 | -2.6642 | 119.252 | -3.6072 | -3.1219 | -3.1952 | -3.4515 | -3.3325 | -0.068664 | -120.9045 | -121.2112 | 1.6022 | 1.5244 | 0.013733 | 1.593 | 0.082397 | -0.073242 | 0.091553 | -122.2824 | 0.33875 | 0.20142 | 0.082398 | 0.27466 | 0.15564 | 1.6708 | 1.5518 | 0.41199 | 0.48523 | 1.8585 | 122.8592 | 1.7899 | 122.7859 | -122.7631 | -122.7676 | 1.4832 | 0.41199 | 0.59509 | 0.86975
4499.1719 | 122.7264 | -3.4332 | 119.2795 | -0.037689 | -0.0025827 | 0.013533 | 0.010512 | -0.0032578 | -0.0027215 | 0.0067036 | -0.0074462 | 0.0021703 | 0.0019226 | -0.0080578 | -0.0038559 | -0.0072889 | -0.0021107 | -2.8519 | -1.6708 | -3.511 | -1.9775 | -1.8311 | -3.4195 | -1.9135 | -2.5955 | 119.3573 | -3.5294 | -3.0396 | -3.0899 | -3.3417 | -3.241 | -0.077819 | -120.9503 | -121.257 | 1.6022 | 1.5198 | 0.013733 | 1.5976 | 0.091552 | -0.09613 | 0.07782 | -122.319 | 0.34332 | 0.19226 | 0.091553 | 0.28839 | 0.18768 | 1.68 | 1.5335 | 0.43945 | 0.48981 | 1.8402 | 122.8867 | 1.7624 | 122.7905 | -122.7905 | -122.8088 | 1.4557 | 0.39368 | 0.58136 | 0.83771
4500.1719 | 122.7219 | -3.3829 | 119.3024 | -0.060578 | 0.00062166 | 0.012892 | 0.0092307 | -0.0021896 | -0.00058531 | 0.0088398 | 0.0078126 | 0.0045203 | -0.0012818 | -0.005708 | -0.0038559 | -0.0083569 | -0.0010425 | -2.8061 | -1.5884 | -3.4698 | -1.9135 | -1.7761 | -3.3646 | -1.8585 | -2.5406 | 119.3893 | -3.479 | -2.9938 | -3.0487 | -3.2822 | -3.186 | -0.086975 | -120.8908 | -121.2158 | 1.6068 | 1.5244 | 0.018311 | 1.6113 | 0.10529 | -0.09613 | 0.086975 | -122.2961 | 0.33417 | 0.19684 | 0.10071 | 0.29297 | 0.19684 | 1.6937 | 1.5564 | 0.4303 | 0.48523 | 1.8814 | 122.8683 | 1.7944 | 122.7722 | -122.7722 | -122.7814 | 1.4694 | 0.3891 | 0.57678 | 0.84229
4501.1719 | 122.6944 | -3.3554 | 119.3893 | -0.083466 | -0.00087374 | 0.012251 | 0.0075217 | -0.00090783 | 5.5488e-05 | 0.0081988 | -0.0074462 | -0.00060665 | 0.001709 | 0.00027342 | -0.0025741 | -0.0060071 | 0.00066654 | -2.7786 | -1.5244 | -3.4149 | -1.9455 | -1.7853 | -3.3234 | -1.8356 | -2.5681 | 119.4672 | -3.4332 | -2.9755 | -3.0167 | -3.2547 | -3.1677 | -0.059509 | -120.9137 | -121.3348 | 1.5701 | 1.5198 | 0.032044 | 1.5793 | 0.091553 | -0.07782 | 0.07782 | -122.3648 | 0.33875 | 0.18768 | 0.10071 | 0.2655 | 0.17853 | 1.6296 | 1.4694 | 0.41657 | 0.45776 | 1.8906 | 122.9004 | 1.8311 | 122.8226 | -122.8043 | -122.8226 | 1.4099 | 0.37994 | 0.57678 | 0.78735
4502.1719 | 122.7402 | -3.3096 | 119.3939 | -0.17502 | -0.00023294 | 0.010115 | 0.0088033 | 0.00016017 | -0.0018671 | 0.0090534 | -0.010498 | 0.0030249 | 0.0012818 | -0.005708 | -0.0019333 | -0.0070753 | 0.0021619 | -2.6688 | -1.5152 | -3.3691 | -1.8768 | -1.7487 | -3.3646 | -1.799 | -2.5085 | 119.4763 | -3.3966 | -2.9068 | -2.9984 | -3.2181 | -3.1082 | -0.05951 | -120.9091 | -121.2708 | 1.561 | 1.5106 | -0.054932 | 1.5701 | 0.004578 | -0.086975 | 0.082397 | -122.3007 | 0.31128 | 0.20142 | 0.091552 | 0.28839 | 0.17853 | 1.6205 | 1.4923 | 0.39825 | 0.48981 | 1.8539 | 122.8729 | 1.7944 | 122.7859 | -122.7631 | -122.7905 | 1.4328 | 0.40283 | 0.64087 | 0.80109
4503.1719 | 122.7219 | -3.2867 | 119.4443 | -0.045319 | -0.0023691 | 0.01097 | 0.010726 | 0.0022964 | 0.00026909 | 0.0071308 | 0.02002 | 0.0013159 | 0.0012818 | -0.001222 | -0.0032151 | -0.0064343 | -0.00082886 | -2.6962 | -1.4694 | -3.3417 | -1.8265 | -1.7166 | -3.2593 | -1.7578 | -2.4811 | 119.5358 | -3.3646 | -2.8885 | -2.9343 | -3.1906 | -3.0899 | -0.054932 | -120.9137 | -121.2708 | 1.5701 | 1.5289 | 0.027466 | 1.5839 | 0.082398 | -0.07782 | 0.091553 | -122.3328 | 0.35248 | 0.19684 | 0.09613 | 0.27466 | 0.17395 | 1.6251 | 1.5152 | 0.4303 | 0.47607 | 1.8723 | 122.9004 | 1.8173 | 122.8226 | -122.7859 | -122.8088 | 1.4603 | 0.39825 | 0.59051 | 0.80566
4504.1719 | 122.7173 | -3.2181 | 119.5084 | -0.060578 | -0.0013009 | 0.011183 | 0.0081625 | 0.0016556 | -0.0014399 | 0.0084124 | -0.01355 | 0.0017431 | 0.0032044 | 0.0015552 | -0.0042831 | -0.0049389 | 0.00023934 | -2.5909 | -1.4099 | -3.2822 | -1.7395 | -1.593 | -3.1769 | -1.6571 | -2.3758 | 119.5724 | -3.2867 | -2.8061 | -2.861 | -3.1036 | -3.0075 | -0.064087 | -120.9183 | -121.2479 | 1.6251 | 1.561 | 0.041199 | 1.6251 | 0.10529 | -0.068664 | 0.064087 | -122.3145 | 0.35706 | 0.21057 | 0.11444 | 0.27924 | 0.1831 | 1.6891 | 1.5427 | 0.42572 | 0.48065 | 1.8723 | 122.8592 | 1.8082 | 122.7905 | -122.7905 | -122.7951 | 1.4786 | 0.41199 | 0.62714 | 0.84229
4505.1719 | 122.6898 | -3.1494 | 119.5541 | -0.03006 | -1.9142e-05 | 0.012465 | 0.0064535 | -0.0056076 | -0.0010125 | 0.0096942 | 0.0078126 | 0.0025975 | -0.00085457 | 0.00027342 | -0.0042831 | -0.0066479 | 0.0028027 | -2.5635 | -1.3458 | -3.2318 | -1.6708 | -1.5472 | -3.1265 | -1.6067 | -2.33 | 119.632 | -3.2501 | -2.742 | -2.7969 | -3.0624 | -2.9526 | -0.082398 | -120.9 | -121.225 | 1.6022 | 1.5427 | 0.022888 | 1.6251 | 0.10529 | -0.10071 | 0.07782 | -122.2961 | 0.35248 | 0.19684 | 0.086975 | 0.29755 | 0.18768 | 1.6846 | 1.561 | 0.45319 | 0.50812 | 1.886 | 122.8821 | 1.8036 | 122.7814 | -122.7859 | -122.8043 | 1.4786 | 0.40741 | 0.58594 | 0.8194
4506.1719 | 122.7219 | -3.1174 | 119.6045 | -0.045319 | 0.0016899 | 0.011183 | 0.0075217 | -0.00026703 | 0.00026909 | 0.005849 | 0.0078126 | 0.0021703 | 0.0019226 | -0.0020764 | -0.0021469 | -0.0055799 | 0.0010937 | -2.4994 | -1.3046 | -3.1815 | -1.6205 | -1.4786 | -3.0853 | -1.5564 | -2.2659 | 119.6869 | -3.1815 | -2.7054 | -2.7924 | -3.0121 | -2.9022 | -0.064087 | -120.9091 | -121.225 | 1.6388 | 1.561 | 0.032044 | 1.6251 | 0.096131 | -0.064087 | 0.082398 | -122.3099 | 0.32501 | 0.21515 | 0.10529 | 0.27924 | 0.16937 | 1.7029 | 1.561 | 0.3891 | 0.47608 | 1.8768 | 122.8683 | 1.8127 | 122.8043 | -122.7859 | -122.7859 | 1.4969 | 0.41199 | 0.61798 | 0.85144
4507.1719 | 122.7768 | -3.0258 | 119.6503 | -0.11398 | -0.0021555 | 0.011824 | 0.0075217 | -5.343e-05 | 0.0015509 | 0.0086262 | 0.059692 | 0.0017431 | 2.8e-08 | -0.0042126 | -0.0012925 | -0.0085705 | -0.0053149 | -2.4628 | -1.3138 | -3.1219 | -1.5198 | -1.3687 | -2.98 | -1.4465 | -2.1652 | 119.6915 | -3.1128 | -2.6001 | -2.6642 | -2.9022 | -2.7969 | -0.09613 | -120.9641 | -121.17 | 1.6571 | 1.5793 | 0.045776 | 1.6754 | 0.14191 | -0.086975 | 0.041198 | -122.2504 | 0.36163 | 0.22888 | 0.1236 | 0.31586 | 0.21057 | 1.7532 | 1.6022 | 0.44861 | 0.51269 | 1.8082 | 122.8043 | 1.712 | 122.7173 | -122.7722 | -122.7631 | 1.506 | 0.42572 | 0.56305 | 0.8606
4508.1719 | 122.7219 | -3.0441 | 119.7006 | -0.03006 | -0.0025827 | 0.010542 | 0.0083761 | -0.0015488 | -0.0014399 | 0.0081988 | 0.029175 | 0.00088875 | -0.0012818 | 0.003905 | -0.0012925 | -0.0072889 | -0.0042469 | -2.4902 | -1.1856 | -3.1403 | -1.561 | -1.4191 | -3.0624 | -1.4694 | -2.3163 | 119.7327 | -3.1448 | -2.7328 | -2.7557 | -2.9755 | -2.7237 | -0.096131 | -120.8862 | -121.2616 | 1.6251 | 1.5747 | -0.018311 | 1.6708 | 0.07782 | -0.10071 | 0.032043 | -122.4335 | 0.28839 | 0.32043 | 0.068664 | 0.42114 | 0.16937 | 1.7212 | 1.5793 | 0.3891 | 0.41199 | 1.9547 | 122.8775 | 1.8585 | 122.7768 | -122.8409 | -122.8455 | 1.4832 | 0.31128 | 0.55389 | 0.72784
4509.1719 | 122.6669 | -3.0396 | 119.7372 | -0.083466 | -0.0023691 | 0.013319 | 0.010085 | -0.0026168 | -0.0037897 | 0.0067036 | 0.02002 | 0.0049475 | 0.00042723 | -0.0033582 | -0.0025741 | -0.0068615 | 2.554e-05 | -2.449 | -1.1536 | -3.0991 | -1.5289 | -1.3916 | -3.0258 | -1.4236 | -2.2705 | 119.7968 | -3.1128 | -2.6688 | -2.7237 | -2.9617 | -2.8656 | -0.059509 | -120.8908 | -121.2662 | 1.6479 | 1.6159 | 0.013733 | 1.6754 | 0.073242 | -0.073242 | 0.059509 | -122.406 | 0.31586 | 0.17395 | 0.07782 | 0.24719 | 0.15106 | 1.7075 | 1.5701 | 0.3891 | 0.44403 | 1.9455 | 122.9095 | 1.886 | 122.8363 | -122.8363 | -122.85 | 1.5106 | 0.37079 | 0.59051 | 0.76904
4510.1719 | 122.7081 | -3.0075 | 119.783 | -0.022431 | 0.00019446 | 0.011397 | 0.0096579 | 0.00080117 | -0.0016535 | 0.0090534 | 0.010864 | 0.0030249 | 0.0021362 | 0.0026232 | -0.0036423 | -0.0070753 | 0.0032299 | -2.3804 | -1.1215 | -3.0853 | -1.3046 | -1.2497 | -3.0808 | -1.4282 | -2.2385 | 119.8425 | -3.0487 | -2.623 | -2.6505 | -2.8976 | -2.8107 | -0.07782 | -120.9045 | -121.0876 | 1.7578 | 1.5793 | -0.073243 | 1.6571 | 0.004577 | -0.041199 | 0.059509 | -122.406 | 0.35705 | 0.19684 | 0.10986 | 0.23804 | 0.15106 | 1.8356 | 1.7807 | 0.39825 | 0.42572 | 1.9638 | 122.8912 | 1.886 | 122.85 | -122.8683 | -122.8317 | 1.7029 | 0.38452 | 0.62714 | 0.76904
4511.1719 | 122.7356 | -2.9526 | 119.8013 | -0.0071715 | 0.0012625 | 0.012892 | 0.0066671 | -0.0013352 | -0.00079891 | 0.0086262 | 0.001709 | 0.0043065 | 0.001709 | -0.0018628 | -0.0034287 | -0.0075025 | 0.0023755 | -2.3392 | -1.0803 | -3.0167 | -1.442 | -1.3367 | -2.916 | -1.3687 | -2.1744 | 119.8791 | -3.035 | -2.5818 | -2.6047 | -2.8473 | -2.7512 | -0.064087 | -120.8817 | -121.2433 | 1.6159 | 1.5839 | 0.036621 | 1.6479 | 0.10071 | -0.082397 | 0.077819 | -122.3831 | 0.3479 | 0.20142 | 0.10529 | 0.28381 | 0.18768 | 1.68 | 1.5747 | 0.4303 | 0.45319 | 1.9363 | 122.9141 | 1.8723 | 122.8317 | -122.818 | -122.8363 | 1.5106 | 0.37079 | 0.6134 | 0.7782
4512.1719 | 122.7219 | -2.9251 | 119.8196 | -0.037689 | -0.00066014 | 0.011397 | 0.010726 | 0.0016556 | -0.0022943 | 0.0088398 | -0.0074462 | 0.0028113 | 0.0014954 | 0.0015552 | -0.00086511 | -0.0057935 | 0.0030163 | -2.2888 | -1.03 | -2.9617 | -1.4008 | -1.2955 | -2.8976 | -1.3504 | -2.1744 | 119.9112 | -3.035 | -2.5589 | -2.5864 | -2.829 | -2.742 | -0.036621 | -120.8496 | -121.2204 | 1.6296 | 1.5747 | 0.027466 | 1.6113 | 0.064087 | -0.10986 | 0.091553 | -122.3785 | 0.33875 | 0.18311 | 0.096131 | 0.29297 | 0.20599 | 1.6663 | 1.561 | 0.44861 | 0.47607 | 1.9318 | 122.9462 | 1.8951 | 122.8363 | -122.7814 | -122.8546 | 1.5244 | 0.36621 | 0.63629 | 0.75073
4513.1719 | 122.7036 | -2.8793 | 119.8517 | -0.075836 | -0.00023294 | 0.012251 | 0.010299 | 0.00080117 | -0.0020807 | 0.0090534 | 0.001709 | 0.0025975 | 0.00042723 | 0.0049732 | -0.0027877 | -0.0072889 | -0.0025379 | -2.243 | -1.0391 | -2.9388 | -1.355 | -1.2268 | -2.8702 | -1.2909 | -2.1057 | 119.9432 | -2.9755 | -2.4948 | -2.5452 | -2.7695 | -2.6962 | -0.05951 | -120.8908 | -121.2067 | 1.6525 | 1.5884 | 0.009155 | 1.6479 | 0.068665 | -0.096131 | 0.091552 | -122.3465 | 0.33417 | 0.1831 | 0.10986 | 0.27924 | 0.20599 | 1.712 | 1.5839 | 0.4303 | 0.48065 | 1.8997 | 122.9187 | 1.8402 | 122.8226 | -122.7905 | -122.8271 | 1.5244 | 0.38452 | 0.63629 | 0.77362
4514.1719 | 122.699 | -2.8473 | 119.9066 | -0.060578 | -0.0030099 | 0.010756 | 0.0064535 | -5.343e-05 | -0.0014399 | 0.010549 | 0.044434 | 0.0043065 | -0.00064077 | -0.0018628 | -0.00086511 | -0.0070753 | -0.00040166 | -2.243 | -1.0071 | -2.9297 | -1.3596 | -1.2405 | -2.8519 | -1.2817 | -2.124 | 120.0119 | -2.9022 | -2.5085 | -2.5314 | -2.774 | -2.6779 | -0.082397 | -120.9137 | -121.2662 | 1.6068 | 1.5656 | -0.004578 | 1.6479 | 0.077819 | -0.054932 | 0.10529 | -122.4152 | 0.31586 | 0.16937 | 0.073242 | 0.22431 | 0.12817 | 1.6891 | 1.5701 | 0.37079 | 0.39368 | 1.9226 | 122.9141 | 1.8402 | 122.8592 | -122.8363 | -122.8088 | 1.4877 | 0.33875 | 0.60425 | 0.72327
4515.1719 | 122.6898 | -2.8152 | 119.9799 | -0.045319 | -0.00066014 | 0.01097 | 0.0068807 | -0.00069423 | -0.0031489 | 0.0060626 | 0.032227 | 0.00024775 | 0.00042723 | -0.0027174 | -0.0021469 | -0.0075025 | -0.00040166 | -2.1652 | -0.9613 | -2.8473 | -1.3046 | -1.1719 | -2.742 | -1.2268 | -2.0599 | 120.0256 | -2.8931 | -2.4765 | -2.4765 | -2.7237 | -2.6505 | -0.032043 | -120.9412 | -121.2845 | 1.6434 | 1.5884 | 0.073243 | 1.6205 | 0.10529 | -0.077819 | 0.045777 | -122.4564 | 0.33875 | 0.16479 | 0.091553 | 0.24261 | 0.16937 | 1.6754 | 1.5427 | 0.41657 | 0.41657 | 1.886 | 122.9187 | 1.8539 | 122.8409 | -122.8271 | -122.8729 | 1.5106 | 0.33875 | 0.65002 | 0.75531
4516.1719 | 122.7081 | -2.774 | 119.9799 | -0.060578 | -0.00066014 | 0.010542 | 0.0092307 | -0.00069423 | 0.00048269 | 0.0090534 | 0.059692 | 0.0019567 | 0.00021363 | -0.0025036 | -0.0027877 | -0.0079297 | 0.0017345 | -2.124 | -0.94757 | -2.8381 | -1.2405 | -1.1124 | -2.7145 | -1.1627 | -2.0142 | 120.0256 | -2.8473 | -2.4399 | -2.4353 | -2.6871 | -2.6093 | -0.064087 | -120.9274 | -121.2204 | 1.6617 | 1.6113 | 0.059509 | 1.6754 | 0.1236 | -0.073242 | 0.045777 | -122.4197 | 0.33874 | 0.1648 | 0.086975 | 0.23804 | 0.16022 | 1.7258 | 1.5976 | 0.41199 | 0.40741 | 1.8906 | 122.8729 | 1.8265 | 122.7997 | -122.818 | -122.8271 | 1.5335 | 0.33417 | 0.65002 | 0.75989
4517.1719 | 122.7402 | -2.742 | 120.0211 | -0.022431 | -0.0013009 | 0.01161 | 0.0070943 | 0.0046464 | -0.0014399 | 0.010549 | 0.001709 | 0.0017431 | 0.00085443 | 0.00027342 | -0.0021469 | -0.0075025 | -0.0018971 | -2.1378 | -0.91095 | -2.8152 | -1.236 | -1.1536 | -2.7237 | -1.181 | -2.0187 | 120.108 | -2.8336 | -2.4078 | -2.4124 | -2.6596 | -2.5818 | -0.073243 | -120.932 | -121.257 | 1.5884 | 1.561 | 0.01831 | 1.6342 | 0.091553 | -0.091553 | 0.086975 | -122.4289 | 0.32959 | 0.16022 | 0.082397 | 0.25177 | 0.17395 | 1.6617 | 1.5793 | 0.42114 | 0.42572 | 1.9043 | 122.9416 | 1.8311 | 122.85 | -122.8363 | -122.8546 | 1.506 | 0.33417 | 0.60425 | 0.72327
4518.1719 | 122.7081 | -2.6962 | 120.0119 | -0.052948 | 0.00062166 | 0.010542 | 0.0085897 | -0.00069423 | -0.0040033 | 0.0084124 | 0.0078126 | 0.0030249 | 0.001709 | -0.0025036 | -0.0015061 | -0.0064343 | -0.00018806 | -2.1057 | -0.86517 | -2.7649 | -1.1032 | -1.03 | -2.829 | -1.1719 | -2.0187 | 120.1263 | -2.7924 | -2.3849 | -2.3804 | -2.6413 | -2.5406 | -0.068665 | -120.8771 | -121.1151 | 1.6663 | 1.5244 | -0.13275 | 1.593 | -0.064086 | -0.09613 | 0.11444 | -122.3969 | 0.31586 | 0.15564 | 0.054932 | 0.25177 | 0.15106 | 1.7349 | 1.6617 | 0.41199 | 0.40741 | 1.8997 | 122.9187 | 1.8311 | 122.8226 | -122.7768 | -122.8043 | 1.593 | 0.31128 | 0.59051 | 0.67749
4519.1719 | 122.7676 | -2.7191 | 120.0531 | -0.022431 | -0.0017281 | 0.012679 | 0.0096579 | 0.0018692 | -0.00079891 | 0.010335 | -0.025757 | 0.0025975 | 0.0012818 | 0.0013416 | -0.0021469 | -0.0057935 | 0.0025891 | -2.0737 | -0.86975 | -2.7878 | -1.2085 | -1.0941 | -2.6642 | -1.1215 | -1.9363 | 120.1263 | -2.774 | -2.3254 | -2.33 | -2.5864 | -2.4719 | -0.068665 | -120.9229 | -121.2616 | 1.6251 | 1.5976 | 0.054931 | 1.6663 | 0.1236 | -0.054932 | 0.073242 | -122.3785 | 0.3891 | 0.24719 | 0.13275 | 0.30212 | 0.18768 | 1.6937 | 1.5793 | 0.44403 | 0.44861 | 1.918 | 122.9004 | 1.8494 | 122.8455 | -122.8409 | -122.8271 | 1.5106 | 0.39368 | 0.64545 | 0.78278
4520.1719 | 122.7173 | -2.6596 | 120.0943 | -0.037689 | -1.9142e-05 | 0.013106 | 0.0096579 | 0.001442 | 0.00048269 | 0.011617 | 0.084106 | 0.0011023 | 0.0021362 | -0.00229 | -0.0023605 | -0.0083569 | -0.0010425 | -2.0508 | -0.82855 | -2.7283 | -1.2131 | -1.0941 | -2.655 | -1.1307 | -1.9089 | 120.2271 | -2.7145 | -2.3254 | -2.3392 | -2.5818 | -2.4948 | -0.068664 | -120.9229 | -121.3074 | 1.5656 | 1.5289 | 0.004578 | 1.5976 | 0.073242 | -0.054932 | 0.13275 | -122.4197 | 0.32043 | 0.16479 | 0.07782 | 0.21973 | 0.13275 | 1.6342 | 1.5152 | 0.37537 | 0.3891 | 1.8997 | 122.9416 | 1.8311 | 122.8867 | -122.8226 | -122.8088 | 1.4465 | 0.33417 | 0.60883 | 0.75073
4521.1719 | 122.7036 | -2.6321 | 120.1263 | -0.022431 | -0.0017281 | 0.012038 | 0.0081625 | -5.343e-05 | -0.00079891 | 0.01183 | 0.001709 | 0.0053747 | 0.00021363 | 0.0013416 | -0.0015061 | -0.0068615 | -0.00082886 | -2.0142 | -0.81482 | -2.7145 | -1.181 | -1.062 | -2.6367 | -1.0895 | -1.7578 | 120.2591 | -2.7008 | -2.3071 | -2.3071 | -2.5635 | -2.4765 | -0.082398 | -120.9412 | -121.3074 | 1.5701 | 1.5427 | -0.004578 | 1.6251 | 0.07782 | -0.068665 | 0.13275 | -122.4335 | 0.32501 | 0.15564 | 0.068664 | 0.22431 | 0.13733 | 1.6525 | 1.5335 | 0.39368 | 0.39368 | 1.8997 | 122.9599 | 1.8173 | 122.8912 | -122.8409 | -122.8271 | 1.4511 | 0.32501 | 0.61798 | 0.87433
4522.1719 | 122.731 | -2.6184 | 120.1447 | -0.11398 | -0.0027963 | 0.012038 | 0.0083761 | -0.00069423 | 0.00026909 | 0.0081988 | 0.026123 | 0.00067495 | 0.0023498 | -0.0014356 | -0.0025741 | -0.0087843 | 0.0015209 | -1.9913 | -0.81024 | -2.6825 | -1.1398 | -1.0208 | -2.6093 | -1.0666 | -1.8997 | 120.2042 | -2.7008 | -2.3026 | -2.2934 | -2.5314 | -2.4445 | -0.064087 | -120.9549 | -121.2845 | 1.5976 | 1.5518 | 0.009155 | 1.6159 | 0.073242 | -0.082398 | 0.05951 | -122.4472 | 0.32501 | 0.17395 | 0.086975 | 0.25635 | 0.16937 | 1.6617 | 1.5427 | 0.40741 | 0.39826 | 1.8723 | 122.905 | 1.8082 | 122.8226 | -122.8271 | -122.8455 | 1.4786 | 0.31586 | 0.62714 | 0.71869
4523.1719 | 122.699 | -2.6276 | 120.1675 | -0.045319 | 0.00019446 | 0.012892 | 0.0077353 | -0.0015488 | 0.0013373 | 0.0079852 | 0.016968 | 0.0025975 | 0.001709 | 0.001128 | -0.0023605 | -0.0083569 | 0.0057935 | -1.9775 | -0.78735 | -2.6688 | -1.1398 | -1.0071 | -2.6001 | -1.0666 | -1.8768 | 120.2271 | -2.7145 | -2.2842 | -2.2842 | -2.5131 | -2.449 | -0.041199 | -120.9549 | -121.3074 | 1.6205 | 1.561 | 0.027465 | 1.6022 | 0.068664 | -0.086976 | 0.059509 | -122.4518 | 0.34332 | 0.17853 | 0.11444 | 0.2655 | 0.20142 | 1.6617 | 1.5289 | 0.4303 | 0.4303 | 1.8814 | 122.9416 | 1.8402 | 122.8546 | -122.8363 | -122.8821 | 1.4877 | 0.34332 | 0.65002 | 0.75073
4524.1719 | 122.7448 | -2.7191 | 120.0577 | -0.022431 | -0.0017281 | 0.01097 | 0.0098715 | 0.0012284 | -0.0012261 | 0.012258 | -0.016602 | 0.0011023 | 0.0019226 | 5.9824e-05 | -0.0038559 | -0.0081433 | -0.0014697 | -2.0004 | -0.79651 | -2.774 | -1.0895 | -0.95673 | -2.6688 | -1.0345 | -1.8951 | 120.1584 | -2.7924 | -2.3117 | -2.3392 | -2.6138 | -2.4994 | -0.054932 | -120.8542 | -121.1472 | 1.7624 | 1.6846 | 0.050354 | 1.7395 | 0.10529 | -0.073242 | 0.10071 | -122.3694 | 0.37994 | 0.21973 | 0.10529 | 0.29297 | 0.17853 | 1.8173 | 1.6846 | 0.45319 | 0.48065 | 1.9775 | 122.9507 | 1.9226 | 122.8775 | -122.8317 | -122.85 | 1.6296 | 0.40741 | 0.71869 | 0.82397
4525.1719 | 122.7448 | -2.7191 | 120.0897 | -0.037689 | -0.0010873 | 0.012679 | 0.0083761 | 0.00037377 | -0.0016535 | 0.005849 | -0.025757 | 0.0034521 | 0.001709 | -0.0018628 | -0.0032151 | -0.0068615 | 0.00045294 | -1.9913 | -0.75989 | -2.7603 | -1.1078 | -0.97504 | -2.6505 | -1.0162 | -1.9318 | 120.1401 | -2.7695 | -2.3163 | -2.3163 | -2.5955 | -2.4811 | -0.041199 | -120.8496 | -121.1975 | 1.7441 | 1.7029 | 0.068664 | 1.7441 | 0.10986 | -0.050354 | 0.050354 | -122.406 | 0.40283 | 0.23804 | 0.1236 | 0.28839 | 0.17395 | 1.7853 | 1.6525 | 0.45319 | 0.45319 | 2.0004 | 122.9095 | 1.9592 | 122.8592 | -122.85 | -122.8592 | 1.6113 | 0.40283 | 0.72784 | 0.78735
4526.1719 | 122.7676 | -2.6917 | 120.0851 | -0.045319 | -1.9142e-05 | 0.011824 | 0.010299 | 0.0035782 | 0.00069649 | 0.0084124 | 0.001709 | 0.00088875 | 0.00021363 | -0.00079478 | -0.0025741 | -0.0068615 | 0.00088014 | -1.9821 | -0.74158 | -2.7512 | -1.0895 | -0.9613 | -2.6276 | -1.0162 | -1.9043 | 120.1538 | -2.7649 | -2.298 | -2.3026 | -2.5772 | -2.4811 | -0.05951 | -120.8267 | -121.1746 | 1.7303 | 1.6754 | 0.064087 | 1.7349 | 0.1236 | -0.073243 | 0.068665 | -122.3831 | 0.3891 | 0.21057 | 0.11444 | 0.28381 | 0.18768 | 1.7899 | 1.6617 | 0.46234 | 0.46692 | 2.0096 | 122.9187 | 1.9501 | 122.8455 | -122.8363 | -122.85 | 1.6022 | 0.39368 | 0.70953 | 0.78735
4527.1719 | 122.7539 | -2.6733 | 120.0851 | -0.022431 | 0.0025443 | 0.011824 | 0.0081625 | 0.0012284 | -0.0014399 | 0.0081988 | 0.010864 | 0.0011023 | 0.001709 | 0.005614 | -0.0038559 | -0.0055799 | -0.0038197 | -1.9547 | -0.70038 | -2.7145 | -1.0712 | -0.94757 | -2.623 | -0.99792 | -1.8906 | 120.1721 | -2.7557 | -2.2705 | -2.2797 | -2.5452 | -2.4582 | -0.041199 | -120.7855 | -121.1563 | 1.7258 | 1.6754 | 0.050354 | 1.7166 | 0.091553 | -0.082397 | 0.086975 | -122.3557 | 0.39368 | 0.21515 | 0.12817 | 0.29755 | 0.21057 | 1.767 | 1.6434 | 0.47607 | 0.48523 | 2.0142 | 122.9279 | 1.973 | 122.8455 | -122.7997 | -122.8409 | 1.6022 | 0.40283 | 0.71869 | 0.78278
4528.1719 | 122.7768 | -2.623 | 120.1035 | -0.014801 | -0.0010873 | 0.010756 | 0.0098715 | 0.003151 | 0.0015509 | 0.01119 | -0.022705 | 0.0017431 | 0.00085443 | 0.0041186 | -0.0040695 | -0.0066479 | 0.0019483 | -1.9363 | -0.68665 | -2.7054 | -1.0666 | -0.9201 | -2.6093 | -0.98877 | -1.8814 | 120.195 | -2.742 | -2.2522 | -2.2614 | -2.5314 | -2.4445 | -0.082397 | -120.7901 | -121.17 | 1.7029 | 1.6342 | 0.013733 | 1.7166 | 0.09613 | -0.11902 | 0.091552 | -122.3557 | 0.36163 | 0.17853 | 0.091553 | 0.29755 | 0.21057 | 1.7853 | 1.6388 | 0.48065 | 0.48981 | 2.0187 | 122.937 | 1.9363 | 122.818 | -122.8088 | -122.8455 | 1.5564 | 0.37079 | 0.68665 | 0.74158
4529.1719 | 122.6807 | -2.6138 | 120.1447 | -0.068207 | -0.0023691 | 0.012465 | 0.0064535 | 0.001442 | 5.5488e-05 | 0.0084124 | -0.025757 | 0.0015295 | -0.00021357 | -0.0042126 | -0.0040695 | -0.0070753 | -0.0014697 | -1.9455 | -0.67749 | -2.7008 | -1.0803 | -0.97046 | -2.6413 | -1.0025 | -1.8951 | 120.2454 | -2.6871 | -2.2659 | -2.2842 | -2.5589 | -2.4307 | -0.086975 | -120.8221 | -121.225 | 1.6434 | 1.6113 | -0.027465 | 1.6983 | 0.05951 | -0.073242 | 0.10071 | -122.4106 | 0.32959 | 0.18311 | 0.054932 | 0.25635 | 0.12817 | 1.7303 | 1.6205 | 0.40283 | 0.42114 | 2.0233 | 122.9324 | 1.9363 | 122.8592 | -122.8455 | -122.8317 | 1.5335 | 0.3479 | 0.66833 | 0.71869
4530.1719 | 122.7722 | -2.5726 | 120.163 | -0.045319 | -0.0019417 | 0.01097 | 0.0060263 | 0.0016556 | -0.0010125 | 0.010549 | 0.0078126 | 0.0019567 | -0.00021357 | 0.0019824 | -0.0034287 | -0.0072889 | 0.00066654 | -1.8723 | -0.65918 | -2.6138 | -1.0162 | -0.90637 | -2.5543 | -0.9613 | -1.8539 | 120.282 | -2.6642 | -2.1973 | -2.2018 | -2.4765 | -2.3804 | -0.041199 | -120.8221 | -121.1792 | 1.6663 | 1.6113 | 0.018311 | 1.6525 | 0.05951 | -0.091553 | 0.11902 | -122.3602 | 0.37079 | 0.19226 | 0.096131 | 0.28381 | 0.18768 | 1.7075 | 1.5976 | 0.46234 | 0.46692 | 1.9547 | 122.9462 | 1.9135 | 122.8546 | -122.7768 | -122.8271 | 1.5564 | 0.37537 | 0.70038 | 0.71869
4531.1719 | 122.7814 | -2.5497 | 120.195 | -0.060578 | -0.0017281 | 0.011824 | 0.0066671 | 0.004219 | -0.0020807 | 0.005849 | -0.01355 | 0.0023839 | 0.00021363 | -0.002931 | -0.0017197 | -0.0079297 | 0.0017345 | -1.8173 | -0.70038 | -2.6413 | -0.98419 | -0.84228 | -2.5131 | -0.92468 | -1.7624 | 120.2682 | -2.6413 | -2.1698 | -2.1652 | -2.4628 | -2.3483 | -0.091552 | -120.8954 | -121.1792 | 1.7075 | 1.6251 | 0.036621 | 1.7166 | 0.12817 | -0.091552 | 0.073243 | -122.3648 | 0.38452 | 0.20142 | 0.086975 | 0.29297 | 0.17853 | 1.799 | 1.6571 | 0.47607 | 0.4715 | 1.9409 | 122.9095 | 1.8494 | 122.818 | -122.8363 | -122.8363 | 1.5656 | 0.37994 | 0.73242 | 0.78735
4532.1719 | 122.7676 | -2.4673 | 120.2637 | -0.060578 | 0.0014761 | 0.012679 | 0.0085897 | 0.0016556 | -0.00058531 | 0.0090534 | -0.01355 | 0.0025975 | 0.0014954 | -0.0037854 | -0.0027877 | -0.0040845 | -0.0010425 | -1.7899 | -0.65918 | -2.6093 | -0.97046 | -0.81482 | -2.4902 | -0.90637 | -1.7395 | 120.3049 | -2.6093 | -2.124 | -2.1515 | -2.417 | -2.3117 | -0.14191 | -120.9229 | -121.2341 | 1.6525 | 1.561 | -0.022888 | 1.7029 | 0.11902 | -0.14191 | 0.041199 | -122.3877 | 0.31586 | 0.15564 | 0.050354 | 0.29755 | 0.19226 | 1.7944 | 1.6388 | 0.45776 | 0.48523 | 1.9501 | 122.9141 | 1.8082 | 122.7722 | -122.8729 | -122.8729 | 1.4969 | 0.34332 | 0.67749 | 0.72784
4533.1719 | 122.7676 | -2.5223 | 120.2316 | -0.052948 | -0.0010873 | 0.012038 | 0.0073081 | -0.00069423 | -0.0033625 | 0.0079852 | -0.01355 | 0.0032385 | 0.0019226 | -0.00229 | -0.0038559 | -0.0075025 | 0.0015209 | -1.767 | -0.63171 | -2.5955 | -0.95673 | -0.81482 | -2.4719 | -0.89264 | -1.7166 | 120.3049 | -2.5772 | -2.1423 | -2.1378 | -2.4078 | -2.3026 | -0.073242 | -120.8633 | -121.1884 | 1.7075 | 1.6296 | 0.050354 | 1.7029 | 0.1236 | -0.054931 | 0.073243 | -122.374 | 0.38452 | 0.21973 | 0.11444 | 0.27466 | 0.16937 | 1.7807 | 1.6388 | 0.43945 | 0.43487 | 1.9638 | 122.8821 | 1.8906 | 122.8271 | -122.8271 | -122.8088 | 1.5656 | 0.37994 | 0.75531 | 0.80566
4534.1719 | 122.8226 | -2.4902 | 120.2316 | -0.12924 | -0.0015145 | 0.012038 | 0.0070943 | 0.0035782 | -0.00037171 | 0.010335 | 0.0078126 | 0.0028113 | 0.00085443 | -0.0018628 | -0.0053513 | -0.0064343 | -0.0014697 | -1.7075 | -0.6546 | -2.5681 | -0.87891 | -0.737 | -2.449 | -0.84228 | -1.6479 | 120.2728 | -2.5864 | -2.0599 | -2.0782 | -2.3438 | -2.2247 | -0.07782 | -120.8862 | -121.1105 | 1.7532 | 1.6479 | 0.041198 | 1.7258 | 0.11902 | -0.096131 | 0.041199 | -122.2916 | 0.41199 | 0.2655 | 0.14648 | 0.36163 | 0.24261 | 1.8311 | 1.6891 | 0.50812 | 0.52643 | 1.9135 | 122.8592 | 1.8356 | 122.7631 | -122.7997 | -122.818 | 1.6113 | 0.4303 | 0.78278 | 0.84228
4535.1719 | 122.7859 | -2.4628 | 120.3003 | -0.03006 | -0.0019417 | 0.01097 | 0.0068807 | 0.0029374 | 0.00069649 | 0.010121 | -0.016602 | 0.00046135 | 0.001068 | -0.0035718 | -0.0015061 | -0.0096387 | -0.00018806 | -1.7258 | -0.64087 | -2.5543 | -0.9201 | -0.78278 | -2.4765 | -0.87433 | -1.7075 | 120.3461 | -2.5864 | -2.1378 | -1.9638 | -2.3254 | -2.2659 | -0.091552 | -120.9412 | -121.2204 | 1.68 | 1.5884 | -0.013732 | 1.68 | 0.07782 | -0.1236 | 0.045776 | -122.438 | 0.49896 | 0.19684 | 0.13733 | 0.32043 | 0.26093 | 1.7715 | 1.6342 | 0.62256 | 0.44861 | 1.9135 | 122.9324 | 1.8219 | 122.8088 | -122.8546 | -122.8867 | 1.5427 | 0.32501 | 0.737 | 0.75531
4536.1719 | 122.7219 | -2.504 | 120.2545 | 0.061493 | -0.00066014 | 0.011183 | 0.0079489 | 0.0022964 | 0.00091009 | 0.0079852 | 0.02002 | 0.0028113 | 0.0012818 | 0.00027342 | -0.0036423 | -0.0083569 | 0.0040845 | -1.7487 | -0.5722 | -2.5406 | -0.94757 | -0.83313 | -2.4673 | -0.8606 | -1.7532 | 120.3598 | -2.6047 | -2.1561 | -2.1286 | -2.4216 | -2.3071 | -0.036621 | -120.8267 | -121.2021 | 1.6708 | 1.6434 | 0.036621 | 1.68 | 0.073242 | -0.10071 | 0.10528 | -122.4106 | 0.37537 | 0.19684 | 0.082397 | 0.29755 | 0.1831 | 1.7075 | 1.593 | 0.47607 | 0.44861 | 1.9684 | 122.9645 | 1.9318 | 122.8638 | -122.7951 | -122.8592 | 1.5564 | 0.3479 | 0.75531 | 0.75073
4537.1719 | 122.7539 | -2.504 | 120.2682 | -0.037689 | -0.00066014 | 0.0075516 | 0.0083761 | 0.0010148 | -0.00015811 | 0.010549 | 0.02002 | 0.0021703 | 0.0019226 | 0.001128 | -0.0042831 | -0.0066479 | -0.0012561 | -1.5656 | -0.58136 | -2.536 | -0.93842 | -0.81482 | -2.4902 | -0.8606 | -1.7349 | 120.3644 | -2.5772 | -2.1332 | -2.1194 | -2.4033 | -2.3117 | -0.032044 | -120.8496 | -121.2067 | 1.6891 | 1.6434 | 0.013733 | 1.6754 | 0.045777 | -0.073242 | 0.09613 | -122.4014 | 0.38452 | 0.19226 | 0.10071 | 0.2655 | 0.17395 | 1.7212 | 1.5976 | 0.45776 | 0.44403 | 1.9547 | 122.9416 | 1.9226 | 122.8683 | -122.8043 | -122.8455 | 1.5656 | 0.37079 | 0.93841 | 0.76904
4538.1719 | 122.7585 | -2.4445 | 120.3598 | -0.098725 | 0.0016899 | 0.014815 | 0.010085 | 0.00080117 | -0.0016535 | 0.005849 | -0.028809 | 0.0034521 | -0.00042717 | 0.00027342 | -0.0034287 | -0.0057935 | 0.0021619 | -1.6205 | -0.59509 | -2.5085 | -0.89722 | -0.76446 | -2.3895 | -0.83771 | -1.6113 | 120.4147 | -2.5177 | -2.037 | -2.0691 | -2.33 | -2.211 | -0.064087 | -120.9549 | -121.257 | 1.68 | 1.6067 | 0.054932 | 1.6708 | 0.11902 | -0.073242 | 0.054932 | -122.3969 | 0.37537 | 0.23346 | 0.11444 | 0.3067 | 0.18768 | 1.7441 | 1.6113 | 0.44861 | 0.48065 | 1.9135 | 122.9324 | 1.8494 | 122.8592 | -122.8683 | -122.8775 | 1.5472 | 0.40741 | 0.82398 | 0.83313
4539.1719 | 122.7997 | -2.3895 | 120.314 | -0.11398 | -0.0019417 | 0.01161 | 0.0073081 | 0.00016017 | -0.0014399 | 0.0086262 | 0.081055 | 0.0023839 | 2.8e-08 | -0.0014356 | -0.0030013 | -0.0089979 | -0.0027515 | -1.6251 | -0.59052 | -2.4765 | -0.86517 | -0.91095 | -2.417 | -0.86517 | -1.6159 | 120.3598 | -2.5406 | -1.9958 | -1.9592 | -2.2385 | -2.1606 | -0.086975 | -120.9045 | -121.1792 | 1.4786 | 1.5244 | -0.027466 | 1.6113 | 0.059509 | -0.15106 | 0.045776 | -122.3099 | 0.4303 | 0.22888 | 0.15106 | 0.37994 | 0.30212 | 1.5656 | 1.6113 | 0.58136 | 0.54474 | 1.886 | 122.9004 | 1.799 | 122.7493 | -122.7905 | -122.8546 | 1.5244 | 0.39368 | 0.76446 | 0.77362
4540.1719 | 122.7402 | -2.4033 | 120.3781 | -0.098725 | 0.0014761 | 0.01097 | 0.0085897 | 0.0016556 | -0.0016535 | 0.012471 | -0.016602 | 0.0017431 | 0.0014954 | 0.0045458 | -0.0027877 | -0.0066479 | 0.0013073 | -1.4832 | -0.5722 | -2.4353 | -0.87891 | -0.74616 | -2.3621 | -0.83313 | -1.6067 | 120.4651 | -2.504 | -2.0325 | -2.0508 | -2.3346 | -2.2064 | -0.032044 | -120.9503 | -121.257 | 1.6571 | 1.5701 | 0.041198 | 1.6022 | 0.073242 | -0.10071 | 0.086975 | -122.4106 | 0.35248 | 0.19684 | 0.068664 | 0.29755 | 0.16937 | 1.6891 | 1.5564 | 0.45319 | 0.4715 | 1.8631 | 122.9691 | 1.8311 | 122.8683 | -122.8134 | -122.8821 | 1.5244 | 0.37079 | 0.9201 | 0.79651
4541.1719 | 122.7951 | -2.3758 | 120.4147 | -0.10635 | -0.0019417 | 0.010329 | 0.0081625 | 0.0022964 | 0.0015509 | 0.0081988 | -0.022705 | 0.0030249 | 0.0021362 | 0.0024096 | -0.0034287 | -0.0055799 | 0.0030163 | -1.5427 | -0.55389 | -2.4261 | -0.8606 | -0.74158 | -2.3209 | -0.81024 | -1.5244 | 120.4971 | -2.4582 | -1.9821 | -2.005 | -2.2568 | -2.1561 | -0.050354 | -120.9686 | -121.2753 | 1.6342 | 1.5656 | 0.054931 | 1.6159 | 0.10528 | -0.082398 | 0.082397 | -122.3969 | 0.37079 | 0.21973 | 0.11902 | 0.30212 | 0.20142 | 1.6846 | 1.5656 | 0.45319 | 0.47607 | 1.8723 | 122.9553 | 1.8219 | 122.8729 | -122.8409 | -122.8729 | 1.5152 | 0.39368 | 0.83313 | 0.85144
4542.1719 | 122.731 | -2.3621 | 120.3964 | -0.091095 | -1.9142e-05 | 0.01161 | 0.0085897 | 0.0055008 | 0.0015509 | 0.0084124 | -0.019653 | 0.0017431 | 2.8e-08 | 0.0062548 | -0.0015061 | -0.0075025 | 0.0021619 | -1.5335 | -0.55847 | -2.4216 | -0.83771 | -0.69122 | -2.3071 | -0.79651 | -1.5381 | 120.5246 | -2.4261 | -1.9958 | -2.0096 | -2.2751 | -2.179 | -0.059509 | -120.9549 | -121.2341 | 1.6708 | 1.5656 | 0.054932 | 1.6251 | 0.11444 | -0.064086 | 0.12817 | -122.3923 | 0.35248 | 0.18311 | 0.086976 | 0.24719 | 0.15106 | 1.7303 | 1.5839 | 0.41656 | 0.4303 | 1.8631 | 122.9507 | 1.8036 | 122.8867 | -122.818 | -122.8226 | 1.5244 | 0.36621 | 0.82855 | 0.82398
4543.1719 | 122.7768 | -2.3895 | 120.4147 | -0.060578 | -0.0030099 | 0.012892 | 0.0096579 | 0.001442 | -0.00079891 | 0.009267 | 0.016968 | 0.0036657 | -0.00021357 | -0.00079478 | -0.0051377 | -0.0068615 | -0.0016833 | -1.5289 | -0.53101 | -2.4445 | -0.87891 | -0.74616 | -2.3209 | -0.78735 | -1.5564 | 120.4834 | -2.449 | -1.9913 | -1.9592 | -2.243 | -2.1515 | -0.054932 | -120.9457 | -121.2936 | 1.6434 | 1.6022 | 0.068664 | 1.6571 | 0.1236 | -0.05951 | 0.068664 | -122.406 | 0.4303 | 0.23804 | 0.14648 | 0.29755 | 0.20599 | 1.6983 | 1.5656 | 0.48981 | 0.45776 | 1.9135 | 122.9324 | 1.8585 | 122.8729 | -122.8592 | -122.8638 | 1.5106 | 0.39825 | 0.86059 | 0.83313
4544.1875 | 122.7539 | -2.3529 | 120.4376 | -0.098725 | 0.0010489 | 0.011397 | 0.0079489 | -0.0013352 | -0.00037171 | 0.0084124 | -0.016602 | 0.0019567 | 0.0040588 | -0.0042126 | -0.0025741 | -0.0072889 | 0.0036571 | -1.4877 | -0.54474 | -2.4033 | -0.84686 | -0.71411 | -2.3026 | -0.78278 | -1.5106 | 120.5109 | -2.4307 | -1.9592 | -1.9547 | -2.243 | -2.1286 | -0.050354 | -120.9824 | -121.2845 | 1.6388 | 1.5701 | 0.050354 | 1.6205 | 0.10071 | -0.07782 | 0.073242 | -122.3969 | 0.39825 | 0.2243 | 0.10986 | 0.30212 | 0.18768 | 1.6891 | 1.5564 | 0.47607 | 0.4715 | 1.8585 | 122.9416 | 1.8082 | 122.8638 | -122.8409 | -122.8683 | 1.506 | 0.39368 | 0.86517 | 0.84228
4545.1719 | 122.7493 | -2.3209 | 120.4559 | -0.045319 | 0.00062166 | 0.011397 | 0.0081625 | 0.0018692 | -0.00015811 | 0.010335 | -0.050171 | 0.00088875 | 0.0012818 | 0.00027342 | -0.0023605 | -0.0075025 | 0.0013073 | -1.4694 | -0.53101 | -2.3895 | -0.83771 | -0.70953 | -2.3071 | -0.74616 | -1.4786 | 120.575 | -2.3712 | -1.9363 | -1.9409 | -2.243 | -2.1469 | -0.068664 | -120.9869 | -121.2936 | 1.6113 | 1.5747 | 0.013733 | 1.6434 | 0.082397 | -0.050354 | 0.11902 | -122.3923 | 0.37994 | 0.17395 | 0.07782 | 0.2243 | 0.12817 | 1.68 | 1.5518 | 0.4303 | 0.43488 | 1.8585 | 122.9462 | 1.7899 | 122.8958 | -122.8455 | -122.8271 | 1.4832 | 0.38452 | 0.85144 | 0.84228
4546.1719 | 122.7585 | -2.33 | 120.4559 | -0.10635 | -0.00066014 | 0.01097 | 0.0060263 | 0.0022964 | -0.0010125 | 0.0081988 | -0.034912 | 0.00024775 | 0.00064083 | -0.0052808 | -0.0034287 | -0.0053663 | 0.0017345 | -1.4511 | -0.51727 | -2.3941 | -0.83313 | -0.70038 | -2.2751 | -0.76904 | -1.4511 | 120.5841 | -2.3666 | -1.9409 | -1.9318 | -2.2339 | -2.124 | -0.064087 | -120.9732 | -121.2891 | 1.6296 | 1.561 | 0.054932 | 1.6251 | 0.11902 | -0.036621 | 0.12817 | -122.3969 | 0.39825 | 0.20599 | 0.09613 | 0.24261 | 0.13275 | 1.6937 | 1.561 | 0.43488 | 0.42572 | 1.8768 | 122.9507 | 1.8127 | 122.9141 | -122.85 | -122.8226 | 1.4969 | 0.3891 | 0.87891 | 0.87891
4547.1719 | 122.7127 | -2.3529 | 120.4559 | -0.060578 | -0.0015145 | 0.011824 | 0.0090169 | 0.00058737 | -0.00079891 | 0.012044 | -0.025757 | 0.0017431 | -0.00042717 | 0.003905 | -0.00043791 | -0.011561 | 0.0021619 | -1.4603 | -0.52185 | -2.4033 | -0.86517 | -0.74158 | -2.3254 | -0.8194 | -1.5564 | 120.5338 | -2.4261 | -2.005 | -1.9775 | -2.2797 | -2.1561 | -0.050354 | -120.9778 | -121.3211 | 1.6113 | 1.5335 | 0.027466 | 1.5839 | 0.07782 | -0.073242 | 0.077819 | -122.4609 | 0.37537 | 0.19684 | 0.073242 | 0.27008 | 0.14648 | 1.6617 | 1.5381 | 0.44861 | 0.42114 | 1.8814 | 122.9599 | 1.8311 | 122.8867 | -122.8592 | -122.8821 | 1.4877 | 0.3479 | 0.89264 | 0.79651
4548.1719 | 122.7356 | -2.3209 | 120.4559 | -0.091095 | -0.00023294 | 0.012038 | 0.0070943 | 0.0027238 | -0.0014399 | 0.0084124 | -0.034912 | 0.0036657 | 0.00021363 | -0.0084852 | -0.0036423 | -0.0066479 | -0.00082886 | -1.4603 | -0.5127 | -2.3758 | -0.86975 | -0.76904 | -2.33 | -0.79193 | -1.5472 | 120.5658 | -2.4033 | -1.9638 | -1.9501 | -2.2659 | -2.1378 | -0.054931 | -120.9686 | -121.3257 | 1.5518 | 1.5289 | -0.009155 | 1.5839 | 0.045776 | -0.082397 | 0.10986 | -122.4197 | 0.37079 | 0.18311 | 0.054932 | 0.2655 | 0.13733 | 1.6067 | 1.506 | 0.45319 | 0.43945 | 1.8631 | 122.9691 | 1.8082 | 122.8867 | -122.8317 | -122.8592 | 1.4511 | 0.35706 | 0.8606 | 0.77362
4549.1875 | 122.7585 | -2.3575 | 120.4559 | -0.014801 | -0.0025827 | 0.014174 | 0.0081625 | 0.001442 | 0.00091009 | 0.009267 | -0.0013428 | 0.0030249 | 0.0012818 | 0.0028368 | -0.0042831 | -0.0070753 | 0.0013073 | -1.3229 | -0.4715 | -2.3895 | -0.80566 | -0.65918 | -2.2842 | -0.74158 | -1.5152 | 120.5429 | -2.417 | -1.9638 | -1.9592 | -2.2522 | -2.1652 | -0.032043 | -120.9274 | -121.2616 | 1.6983 | 1.6159 | 0.073242 | 1.6479 | 0.10528 | -0.059509 | 0.086975 | -122.4197 | 0.39825 | 0.19226 | 0.10529 | 0.25177 | 0.1648 | 1.7303 | 1.5839 | 0.45776 | 0.45319 | 1.918 | 122.9599 | 1.886 | 122.9004 | -122.8455 | -122.8729 | 1.5518 | 0.39368 | 1.0345 | 0.84229
4550.1719 | 122.7631 | -2.298 | 120.4742 | -0.091095 | -0.0023691 | 0.012679 | 0.0085897 | 0.00016017 | -0.0010125 | 0.007558 | -0.028809 | 3.4148e-05 | 0.00064083 | 0.0013416 | -0.0021469 | -0.0075025 | -0.0016833 | -1.3641 | -0.50354 | -2.3758 | -0.81482 | -0.66376 | -2.2751 | -0.63629 | -1.4465 | 120.607 | -2.3483 | -1.9089 | -1.9135 | -2.1973 | -2.0966 | -0.077819 | -120.9778 | -121.2891 | 1.6342 | 1.6617 | 0.022889 | 1.7395 | 0.10071 | -0.050354 | 0.13275 | -122.3831 | 0.38452 | 0.20142 | 0.10071 | 0.25177 | 0.15106 | 1.712 | 1.561 | 0.43488 | 0.43945 | 1.8723 | 122.9553 | 1.7944 | 122.905 | -122.85 | -122.8226 | 1.4832 | 0.3891 | 0.93384 | 0.85144
4551.1719 | 122.7539 | -2.1698 | 120.5978 | -0.075836 | 0.0012625 | 0.015028 | 0.0070943 | -0.0026168 | -0.00015811 | 0.0062762 | -0.0074462 | 0.0019567 | 0.00042723 | 0.0096728 | -0.0057785 | -0.0057935 | 0.00045294 | -1.3 | -0.4715 | -2.2385 | -0.79651 | -0.6546 | -2.1286 | -0.59967 | -1.3367 | 120.7489 | -2.2202 | -1.799 | -1.7761 | -2.0874 | -1.9821 | -0.068664 | -121.0693 | -121.3943 | 1.5152 | 1.5701 | 0.041199 | 1.6388 | 0.10986 | -0.050354 | 0.15106 | -122.3968 | 0.39368 | 0.18768 | 0.082398 | 0.23804 | 0.13275 | 1.5839 | 1.442 | 0.44403 | 0.42114 | 1.767 | 122.9691 | 1.6983 | 122.9187 | -122.8363 | -122.818 | 1.3733 | 0.37079 | 0.86975 | 0.83313
4552.1719 | 122.7539 | -2.1011 | 120.6848 | -0.12924 | -1.9142e-05 | 0.012892 | 0.0094443 | 0.0012284 | 0.0011237 | 0.0071308 | -0.025757 | 0.00088875 | 0.0012818 | 0.001128 | -0.0017197 | -0.0070753 | -0.0014697 | -1.3 | -0.45776 | -2.179 | -0.83313 | -0.72327 | -2.1286 | -0.75531 | -1.355 | 120.7718 | -2.1973 | -1.7441 | -1.7441 | -2.0462 | -1.9363 | -0.07782 | -121.1426 | -121.5179 | 1.3779 | 1.3458 | -0.027466 | 1.4236 | 0.050354 | -0.096131 | 0.086976 | -122.4289 | 0.35706 | 0.1648 | 0.054931 | 0.26093 | 0.15106 | 1.4557 | 1.3458 | 0.45319 | 0.45319 | 1.7212 | 122.9691 | 1.6434 | 122.8729 | -122.8638 | -122.8821 | 1.268 | 0.35706 | 0.80109 | 0.74616
4553.1719 | 122.7859 | -2.0874 | 120.7031 | -0.15213 | -0.00044654 | 0.012465 | 0.0079489 | 0.001442 | -0.00037171 | 0.0088398 | -0.0043946 | 0.00088875 | 2.8e-08 | -0.0027174 | -0.0015061 | -0.0079297 | -0.0010425 | -1.2543 | -0.43945 | -2.1423 | -0.79651 | -0.6958 | -2.0279 | -0.71411 | -1.3046 | 120.7947 | -2.1698 | -1.6937 | -1.6891 | -1.973 | -1.8723 | -0.054932 | -121.1426 | -121.4996 | 1.3916 | 1.3733 | 0.059509 | 1.4282 | 0.11444 | -0.082398 | 0.091553 | -122.3969 | 0.39825 | 0.21515 | 0.11444 | 0.29755 | 0.19684 | 1.4465 | 1.3458 | 0.48065 | 0.47607 | 1.7029 | 122.9645 | 1.6479 | 122.8821 | -122.8455 | -122.8729 | 1.2909 | 0.39368 | 0.83313 | 0.78278
4554.1875 | 122.7402 | -1.9775 | 120.8267 | -0.03006 | -0.0010873 | 0.014174 | 0.010299 | 0.00037377 | -0.0016535 | 0.0088398 | -0.028809 | 0.0019567 | 0.00085443 | 0.00091422 | -0.0032151 | -0.0087843 | -0.0014697 | -1.0712 | -0.43488 | -1.9775 | -0.75073 | -0.62714 | -1.918 | -0.6958 | -1.181 | 120.9229 | -2.037 | -1.6113 | -1.593 | -1.9043 | -1.7899 | 0 | -121.2616 | -121.5775 | 1.3504 | 1.2817 | 0.059509 | 1.2817 | 0.059509 | -0.059509 | 0.096131 | -122.438 | 0.38452 | 0.18768 | 0.073242 | 0.24719 | 0.13275 | 1.3504 | 1.2268 | 0.44403 | 0.42572 | 1.5427 | 122.9599 | 1.5427 | 122.9004 | -122.8043 | -122.8638 | 1.2268 | 0.36621 | 0.90637 | 0.79651
4555.1719 | 122.7676 | -1.8265 | 120.9595 | -0.083466 | -0.0045053 | 0.014815 | 0.0081625 | 0.00251 | 0.0026191 | 0.0049946 | 0.010864 | 0.0017431 | 0.00042723 | -0.001222 | -0.0040695 | -0.0064343 | 0.0040845 | -1.1261 | -0.42572 | -1.8997 | -0.69122 | -0.62256 | -1.8585 | -0.67291 | -1.0712 | 121.0831 | -1.8997 | -1.4557 | -1.4465 | -1.7349 | -1.6251 | -0.073242 | -121.3852 | -121.6507 | 1.2039 | 1.1536 | -0.032044 | 1.2268 | 0.041198 | -0.073242 | 0.1236 | -122.4152 | 0.37994 | 0.20142 | 0.091553 | 0.27466 | 0.1648 | 1.2772 | 1.2085 | 0.45319 | 0.44403 | 1.474 | 122.9828 | 1.4008 | 122.9095 | -122.8592 | -122.8592 | 1.1353 | 0.37079 | 0.70038 | 0.75531
4556.1719 | 122.7676 | -1.8036 | 120.9961 | -0.15213 | -0.0010873 | 0.015669 | 0.010085 | 0.0057144 | -0.00079891 | 0.00414 | 0.029175 | 0.0019567 | -0.00021357 | -0.002931 | -0.0032151 | -0.0066479 | 0.0047253 | -1.1078 | -0.43945 | -1.8677 | -0.737 | -0.54016 | -1.8036 | -0.70496 | -1.0666 | 121.1014 | -1.8906 | -1.442 | -1.4282 | -1.7349 | -1.6022 | -0.064087 | -121.4355 | -121.7331 | 1.2634 | 1.0986 | 0 | 1.1627 | 0.064087 | -0.086975 | 0.10528 | -122.4381 | 0.37537 | 0.20142 | 0.068665 | 0.28839 | 0.15564 | 1.3275 | 1.1307 | 0.46234 | 0.44861 | 1.4282 | 122.9919 | 1.3641 | 122.905 | -122.8638 | -122.8867 | 1.0666 | 0.36163 | 0.6958 | 0.737
4557.1719 | 122.7722 | -1.7395 | 121.0464 | -0.083466 | -0.0010873 | 0.015242 | 0.010299 | 0.00251 | -0.00015811 | 0.0034992 | -0.010498 | 0.00088875 | 0.004486 | 0.0043322 | -0.0034287 | -0.0075025 | -0.0027515 | -1.03 | -0.43945 | -1.8356 | -0.72327 | -0.59509 | -1.7212 | -0.68207 | -0.80109 | 121.2021 | -1.7944 | -1.3641 | -1.355 | -1.6525 | -1.5427 | -0.09613 | -121.4859 | -121.7697 | 1.1444 | 1.0574 | 0.018311 | 1.1536 | 0.11444 | -0.054932 | 0.15564 | -122.4106 | 0.38452 | 0.19684 | 0.086975 | 0.25177 | 0.14191 | 1.2405 | 1.1124 | 0.43945 | 0.4303 | 1.3962 | 122.9965 | 1.3 | 122.9416 | -122.8821 | -122.8409 | 1.0162 | 0.37537 | 0.70953 | 0.93842
4558.1719 | 122.8409 | -1.6754 | 121.0831 | -0.098725 | -0.00044654 | 0.013106 | 0.0058127 | -0.0021896 | 5.5488e-05 | 0.0043536 | 0.071899 | 0.0011023 | 0.0025634 | -0.0067762 | -0.0036423 | -0.0072889 | 0.0021619 | -0.95215 | -0.44861 | -1.6891 | -0.64545 | -0.49896 | -1.5289 | -0.56763 | -0.78278 | 121.1792 | -1.7258 | -1.3046 | -1.1032 | -1.6113 | -1.4832 | -0.013733 | -121.5317 | -121.7285 | 1.1765 | 1.1078 | 0.14648 | 1.1215 | 0.16022 | -0.050354 | 0.09613 | -122.3877 | 0.57221 | 0.19226 | 0.064087 | 0.24262 | 0.11444 | 1.1902 | 1.0437 | 0.62256 | 0.42114 | 1.2405 | 122.905 | 1.2268 | 122.8546 | -122.7722 | -122.8088 | 1.03 | 0.37079 | 0.72327 | 0.89264
4559.1875 | 122.7539 | -1.4832 | 121.3348 | -0.022431 | -0.0019417 | 0.018233 | 0.0068807 | -0.00048063 | -0.00079891 | 0.00072199 | 0.0047608 | 0.00067495 | 0.0019226 | 0.0036914 | -0.0015061 | -0.0055799 | 2.554e-05 | -0.95215 | -0.39825 | -1.5518 | -0.737 | -0.6546 | -1.4832 | -0.66376 | -0.78735 | 121.431 | -1.561 | -1.1673 | -1.1078 | -1.4053 | -1.3138 | -0.068665 | -121.7331 | -122.0718 | 0.82855 | 0.8194 | 0 | 0.88806 | 0.068665 | -0.07782 | 0.09613 | -122.5021 | 0.37537 | 0.16937 | 0.07782 | 0.24719 | 0.15564 | 0.89722 | 0.81482 | 0.45319 | 0.39368 | 1.1536 | 122.9919 | 1.0849 | 122.9141 | -122.8867 | -122.8958 | 0.74615 | 0.31586 | 0.53101 | 0.6958
4560.1719 | 122.8409 | -1.4511 | 121.3074 | -0.17502 | -1.9142e-05 | 0.018233 | 0.0088033 | 0.00016017 | 0.0015509 | 0.0056354 | 0.016968 | 0.0025975 | 0.001709 | 0.0032642 | -0.0032151 | -0.0083569 | -0.00082886 | -0.86517 | -0.43945 | -1.5198 | -0.79193 | -0.64545 | -1.3138 | -0.54016 | -0.62256 | 121.344 | -1.5793 | -1.062 | -1.0345 | -1.3046 | -1.2131 | -0.068664 | -121.7468 | -122.0993 | 0.80566 | 0.91095 | 0.13733 | 0.97961 | 0.20599 | -0.12817 | 0.036621 | -122.3694 | 0.41657 | 0.23804 | 0.14648 | 0.36621 | 0.27466 | 0.87433 | 0.72784 | 0.54474 | 0.51727 | 1.0803 | 122.9233 | 1.0117 | 122.7951 | -122.8271 | -122.8867 | 0.65918 | 0.3891 | 0.58594 | 0.82855
4561.1719 | 122.7173 | -1.4511 | 121.3943 | -0.060578 | 0.0029715 | 0.016737 | 0.0083761 | -0.0015488 | -0.0018671 | 0.0043536 | -0.050171 | 0.00067495 | 0.00042723 | 0.0013416 | -0.0036423 | -0.0077161 | 0.0025891 | -0.9201 | -0.39825 | -1.5152 | -0.75531 | -0.67291 | -1.4786 | -0.69122 | -0.76446 | 121.4813 | -1.5244 | -1.1398 | -1.0941 | -1.3916 | -1.2497 | -0.064087 | -121.7926 | -122.1497 | 0.7782 | 0.75989 | -0.027466 | 0.82398 | 0.036621 | -0.073242 | 0.086975 | -122.5342 | 0.35706 | 0.20142 | 0.059509 | 0.27466 | 0.13275 | 0.84229 | 0.75989 | 0.4303 | 0.38452 | 1.1169 | 123.0057 | 1.0529 | 122.9324 | -122.9095 | -122.9187 | 0.6958 | 0.31128 | 0.53101 | 0.68665
4562.1719 | 122.8043 | -1.3367 | 121.4905 | -0.1445 | -0.0021555 | 0.018446 | 0.0090169 | 0.00037377 | -0.00058531 | 0.0034992 | -0.053223 | 0.0019567 | 0.00064083 | 0.0017688 | -0.0025741 | -0.0081433 | 0.0042981 | -0.86975 | -0.37994 | -1.4145 | -0.73242 | -0.63171 | -1.3962 | -0.66376 | -0.67749 | 121.5408 | -1.4648 | -0.97504 | -1.062 | -1.3641 | -1.2314 | -0.07782 | -121.8704 | -122.2229 | 0.70496 | 0.67291 | -0.059509 | 0.75073 | 0.018311 | -0.12817 | 0.050354 | -122.4655 | 0.27466 | 0.10529 | -0.027466 | 0.23346 | 0.10071 | 0.78278 | 0.68207 | 0.40283 | 0.48981 | 1.0345 | 123.0057 | 0.95673 | 122.8775 | -122.905 | -122.9553 | 0.60425 | 0.36163 | 0.46692 | 0.65918
4563.1719 | 122.8821 | -1.2909 | 121.4813 | -0.10635 | -0.00066014 | 0.01631 | 0.0055991 | 0.00080117 | -0.0012261 | 0.002431 | 0.074951 | 0.0015295 | 0.0012818 | 0.0017688 | -0.0042831 | -0.0096387 | -0.0021107 | -0.78278 | -0.37994 | -1.3412 | -0.6134 | -0.4715 | -1.1948 | -0.49896 | -0.45776 | 121.55 | -1.3824 | -0.91553 | -0.82855 | -1.0895 | -1.0391 | -0.050354 | -121.8613 | -122.0947 | 0.8194 | 0.79193 | 0.096131 | 0.84229 | 0.14648 | -0.091552 | 0.068665 | -122.3969 | 0.46234 | 0.25177 | 0.20142 | 0.34332 | 0.29297 | 0.86975 | 0.72784 | 0.55389 | 0.46692 | 0.9613 | 122.9324 | 0.91095 | 122.8409 | -122.8226 | -122.8638 | 0.67749 | 0.37537 | 0.50812 | 0.83313
4564.1719 | 122.8821 | -1.2634 | 121.4813 | -0.075836 | 0.00062166 | 0.018446 | 0.0066671 | -5.343e-05 | 0.00026909 | 0.00414 | -0.0013428 | -0.00017945 | 0.0014954 | -0.0033582 | -0.0047103 | -0.0066479 | -0.0014697 | -0.737 | -0.41657 | -1.3046 | -0.60425 | -0.48065 | -1.1765 | -0.54474 | -0.42572 | 121.5775 | -1.3458 | -0.85602 | -0.82398 | -1.3321 | -1.1215 | -0.041198 | -121.8979 | -122.0856 | 0.78278 | 0.71869 | 0.086975 | 0.75989 | 0.12817 | -0.082397 | 0.096131 | -122.3373 | 0.43945 | 0.14191 | -0.068664 | 0.2243 | 0.013733 | 0.82397 | 0.70038 | 0.52185 | 0.48981 | 0.88806 | 122.9233 | 0.84686 | 122.8409 | -122.7859 | -122.8271 | 0.65918 | 0.40741 | 0.52643 | 0.83771
4565.1719 | 122.7859 | -1.2543 | 121.5454 | -0.037689 | -0.00023294 | 0.018874 | 0.0098715 | 0.003151 | -0.00037171 | 0.002431 | -0.025757 | 0.0011023 | -0.0012818 | 0.0030506 | -0.0030013 | -0.0066479 | -0.0029651 | -0.7782 | -0.36163 | -1.3 | -0.66834 | -0.54016 | -1.1581 | -0.49439 | -0.44861 | 121.6827 | -1.2863 | -0.91095 | -0.9201 | -1.1719 | -1.0757 | -0.045777 | -121.907 | -122.2137 | 0.71411 | 0.75989 | 0.09613 | 0.80566 | 0.14191 | -0.032044 | 0.13733 | -122.4564 | 0.33417 | 0.17853 | 0.082397 | 0.21057 | 0.11444 | 0.75989 | 0.63171 | 0.36621 | 0.37537 | 0.93842 | 122.9691 | 0.89264 | 122.937 | -122.8455 | -122.8317 | 0.58594 | 0.34332 | 0.47607 | 0.80566
4566.1719 | 122.7402 | -1.2405 | 121.5866 | -0.12924 | -0.0015145 | 0.017592 | 0.012435 | 0.00016017 | -0.0031489 | 0.0032856 | -0.059326 | 0.0028113 | 0.001068 | -0.0025036 | -0.0030013 | -0.0053663 | 0.00045294 | -0.80109 | -0.37079 | -1.3092 | -0.737 | -0.63629 | -1.2863 | -0.65002 | -0.50812 | 121.6644 | -1.3229 | -0.94757 | -0.93384 | -1.2039 | -1.0757 | -0.068664 | -121.9574 | -122.3236 | 0.60425 | 0.59052 | -0.045776 | 0.65918 | 0.022888 | -0.082397 | 0.07782 | -122.5342 | 0.3067 | 0.1648 | 0.036622 | 0.24719 | 0.11902 | 0.67291 | 0.5722 | 0.3891 | 0.37537 | 0.93841 | 122.9874 | 0.86975 | 122.905 | -122.8958 | -122.9095 | 0.50354 | 0.29297 | 0.43945 | 0.73242
4567.1719 | 122.7539 | -1.1993 | 121.6049 | -0.075836 | -0.0015145 | 0.020796 | 0.0094443 | 0.00080117 | -0.0012261 | 0.0043536 | -0.053223 | 0.0021703 | 0.0019226 | -0.00058098 | -0.0015061 | -0.0066479 | 0.0010937 | -0.78278 | -0.32959 | -1.268 | -0.70953 | -0.63171 | -1.2451 | -0.65002 | -0.46692 | 121.7331 | -1.2955 | -0.89264 | -0.88806 | -1.149 | -1.03 | -0.068664 | -121.9345 | -122.3145 | 0.56763 | 0.54932 | -0.045776 | 0.61798 | 0.022888 | -0.09613 | 0.12817 | -122.4976 | 0.31128 | 0.16937 | 0.050354 | 0.2655 | 0.14648 | 0.63629 | 0.55847 | 0.40741 | 0.40283 | 0.93841 | 123.0286 | 0.86975 | 122.9324 | -122.8729 | -122.9004 | 0.48981 | 0.3067 | 0.41656 | 0.73242
4568.1719 | 122.8363 | -1.1261 | 121.669 | -0.12924 | 0.00040806 | 0.019087 | 0.0066671 | -0.001976 | 0.00026909 | 0.0020038 | 0.053589 | -0.0012477 | 0.00021363 | -0.0080578 | -0.0012925 | -0.0066479 | -0.0012561 | -0.67749 | -0.37537 | -1.1765 | -0.58136 | -0.45776 | -1.0071 | -0.48981 | -0.22888 | 121.756 | -1.1902 | -0.76904 | -0.71411 | -0.94757 | -0.89264 | -0.050354 | -122.0444 | -122.2504 | 0.66833 | 0.63629 | 0.11902 | 0.68665 | 0.16937 | -0.064087 | 0.086975 | -122.438 | 0.41199 | 0.23346 | 0.17853 | 0.29755 | 0.24261 | 0.71869 | 0.59509 | 0.47607 | 0.42114 | 0.80109 | 122.9462 | 0.75073 | 122.8821 | -122.8455 | -122.8592 | 0.54474 | 0.35706 | 0.44861 | 0.89722
4569.1719 | 122.818 | -1.0529 | 121.7468 | -0.13687 | -0.00023294 | 0.020796 | 0.0077353 | 0.00080117 | -0.00037171 | 8.1188e-05 | 0.047485 | 3.4148e-05 | 0.001068 | -0.005708 | -0.0025741 | -0.0068615 | 0.0021619 | -0.67291 | -0.36163 | -1.0895 | -0.58594 | -0.44403 | -1.0025 | -0.49896 | -0.20599 | 121.8018 | -1.1353 | -0.70953 | -0.65918 | -0.92468 | -0.82398 | -0.036622 | -122.1085 | -122.3328 | 0.60882 | 0.55389 | 0.050354 | 0.59052 | 0.086976 | -0.082398 | 0.054932 | -122.4564 | 0.39368 | 0.22888 | 0.12817 | 0.31128 | 0.21057 | 0.64545 | 0.50354 | 0.47607 | 0.42572 | 0.72784 | 122.937 | 0.69122 | 122.8546 | -122.8363 | -122.8821 | 0.46692 | 0.34332 | 0.37994 | 0.84686
4570.1719 | 122.7493 | -1.0483 | 121.8063 | -0.10635 | -0.0010873 | 0.018874 | 0.0092307 | 0.003151 | 0.0011237 | 0.0011494 | -0.050171 | 0.0025975 | 0.0014954 | 0.001128 | -0.0038559 | -0.0060071 | -0.00082886 | -0.73242 | -0.32959 | -1.1215 | -0.68207 | -0.60883 | -1.0803 | -0.6134 | -0.3067 | 121.8658 | -1.1353 | -0.74158 | -0.72784 | -0.99335 | -0.87891 | -0.073242 | -122.1359 | -122.4884 | 0.43945 | 0.43488 | -0.032043 | 0.50812 | 0.041199 | -0.086975 | 0.05951 | -122.5479 | 0.32043 | 0.16937 | 0.054932 | 0.25635 | 0.14191 | 0.5127 | 0.43945 | 0.40741 | 0.39368 | 0.79193 | 123.0011 | 0.71869 | 122.9141 | -122.9279 | -122.9416 | 0.36621 | 0.3067 | 0.31586 | 0.74158
4571.1719 | 122.7768 | -0.98419 | 121.8018 | -0.10635 | -0.00023294 | 0.021651 | 0.010726 | 0.00080117 | -0.0014399 | 0.0017902 | -0.047119 | 0.00046135 | -0.00042717 | -0.003999 | -0.0017197 | -0.0087843 | 0.0015209 | -0.65002 | -0.35248 | -1.0666 | -0.64087 | -0.50812 | -0.97961 | -0.57678 | -0.07782 | 121.9849 | -1.0666 | -0.67749 | -0.67291 | -0.90637 | -0.81482 | -0.082397 | -122.1542 | -122.4426 | 0.47607 | 0.40741 | 0.004578 | 0.48981 | 0.086975 | -0.082397 | 0.1831 | -122.4792 | 0.31128 | 0.16937 | 0.07782 | 0.25177 | 0.16022 | 0.55847 | 0.42572 | 0.39368 | 0.3891 | 0.71411 | 123.0515 | 0.63171 | 122.9691 | -122.8683 | -122.8683 | 0.34332 | 0.3067 | 0.33417 | 0.90637
4572.1719 | 122.7631 | -1.0117 | 121.8658 | -0.083466 | 0.00083526 | 0.019942 | 0.0075217 | 0.00058737 | -0.0016535 | 0.0060626 | -0.041016 | 0.0011023 | 0.00085443 | -0.00015378 | -0.0036423 | -0.0083569 | -0.0012561 | -0.65002 | -0.3067 | -1.0254 | -0.6546 | -0.54016 | -0.99792 | -0.58594 | -0.21515 | 121.9299 | -1.0895 | -0.70038 | -0.69122 | -0.94299 | -0.83313 | -0.013733 | -122.1725 | -122.5204 | 0.4715 | 0.42572 | 0.013733 | 0.43945 | 0.027466 | -0.07782 | 0.064087 | -122.5662 | 0.32043 | 0.17853 | 0.068665 | 0.25635 | 0.14648 | 0.48523 | 0.37079 | 0.39825 | 0.3891 | 0.71869 | 123.0194 | 0.70496 | 122.9416 | -122.8912 | -122.9553 | 0.35706 | 0.31128 | 0.36163 | 0.79651
4573.1719 | 122.8455 | -0.93842 | 121.8063 | -0.068207 | 0.00062166 | 0.018874 | 0.0083761 | 0.0018692 | 0.00069649 | 0.0015766 | -0.019653 | 0.00088875 | -0.00042717 | -0.0014356 | -0.0030013 | -0.0075025 | -0.00018806 | -0.6134 | -0.3479 | -1.0071 | -0.56305 | -0.4303 | -0.90179 | -0.48523 | -0.082397 | 121.9116 | -1.0391 | -0.54932 | -0.54474 | -0.7782 | -0.6958 | -0.068664 | -122.1542 | -122.3694 | 0.50812 | 0.45319 | 0.036622 | 0.52185 | 0.10529 | -0.10071 | 0.10529 | -122.3557 | 0.39368 | 0.24262 | 0.16022 | 0.34332 | 0.26093 | 0.57678 | 0.44403 | 0.49438 | 0.48981 | 0.65918 | 122.9507 | 0.59052 | 122.85 | -122.8134 | -122.8455 | 0.37537 | 0.3891 | 0.32501 | 0.85602
4574.1719 | 122.8088 | -0.94299 | 121.8338 | 0.030975 | -0.0025827 | 0.019728 | 0.0094443 | 0.001442 | -0.00015811 | 0.0017902 | -0.022705 | 0.0021703 | 0.00064083 | 0.0043322 | -0.0023605 | -0.0055799 | -0.0014697 | -0.67749 | -0.31128 | -1.0071 | -0.65918 | -0.55389 | -0.97961 | -0.58136 | -0.16937 | 121.9437 | -1.0391 | -0.64087 | -0.59967 | -0.8606 | -0.75073 | -0.064087 | -122.1451 | -122.493 | 0.3891 | 0.36163 | -0.036621 | 0.42572 | 0.027466 | -0.096131 | 0.10986 | -122.4747 | 0.34332 | 0.19226 | 0.082397 | 0.28839 | 0.17853 | 0.45319 | 0.3479 | 0.43945 | 0.39825 | 0.6958 | 122.9828 | 0.63171 | 122.8867 | -122.8409 | -122.8729 | 0.28381 | 0.30212 | 0.2655 | 0.77362
4575.1719 | 122.7905 | -0.97504 | 121.8796 | -0.075836 | -0.0025827 | 0.02101 | 0.010512 | -0.00048063 | -0.0018671 | -0.00034601 | -0.050171 | 0.0028113 | 0.0019226 | -0.002931 | -0.0019333 | -0.0055799 | 0.0053661 | -0.68207 | -0.3067 | -1.0117 | -0.6546 | -0.58136 | -0.98877 | -0.58594 | -0.20599 | 121.9849 | -1.062 | -0.64545 | -0.64545 | -0.90637 | -0.78278 | -0.036621 | -122.1863 | -122.5342 | 0.39368 | 0.3891 | -0.013733 | 0.42572 | 0.022888 | -0.086975 | 0.10529 | -122.525 | 0.32959 | 0.19226 | 0.068665 | 0.27924 | 0.15564 | 0.4303 | 0.35706 | 0.41656 | 0.41656 | 0.70496 | 123.0469 | 0.66834 | 122.9599 | -122.8912 | -122.9416 | 0.32044 | 0.32959 | 0.29297 | 0.76904
4576.1719 | 122.7585 | -0.94757 | 121.875 | -0.052948 | -0.0023691 | 0.021864 | 0.011794 | 0.0029374 | 0.00048269 | 0.00050839 | -0.071533 | 0.0040929 | -0.00021357 | 0.0028368 | -0.0040695 | -0.0075025 | 0.0038709 | -0.65918 | -0.31128 | -1.0391 | -0.68665 | -0.59967 | -1.0025 | -0.62256 | -0.2243 | 121.9849 | -1.0437 | -0.64087 | -0.6546 | -0.90179 | -0.77362 | -0.091553 | -122.1863 | -122.5616 | 0.3479 | 0.32501 | -0.054931 | 0.41656 | 0.036622 | -0.09613 | 0.10986 | -122.5159 | 0.29297 | 0.17395 | 0.045777 | 0.27008 | 0.14191 | 0.43945 | 0.35248 | 0.3891 | 0.40283 | 0.72784 | 123.0286 | 0.63629 | 122.9324 | -122.9141 | -122.9187 | 0.26093 | 0.3067 | 0.28839 | 0.72327
4577.1719 | 122.8546 | -0.9201 | 121.8658 | -0.068207 | 0.0010489 | 0.019301 | 0.0085897 | 0.001442 | 0.0011237 | 0.0015766 | 0.0047608 | 0.0019567 | -0.0019226 | -0.0018628 | -0.0017197 | -0.0062207 | -0.00061526 | -0.6546 | -0.31128 | -0.99335 | -0.61798 | -0.5127 | -0.95215 | -0.54932 | -0.10986 | 121.9574 | -1.03 | -0.55847 | -0.55389 | -0.82398 | -0.72327 | -0.073242 | -122.1771 | -122.4838 | 0.40741 | 0.37079 | -0.032043 | 0.44403 | 0.041199 | -0.10986 | 0.091552 | -122.4243 | 0.36621 | 0.19684 | 0.09613 | 0.3067 | 0.20599 | 0.48065 | 0.37537 | 0.47607 | 0.4715 | 0.68207 | 122.9874 | 0.60883 | 122.8775 | -122.8592 | -122.8958 | 0.30212 | 0.36163 | 0.2655 | 0.81024
4578.1719 | 122.7859 | -0.94757 | 121.8613 | -0.091095 | -1.9142e-05 | 0.019942 | 0.0096579 | 0.00016017 | 0.0019781 | 0.0026446 | -0.053223 | 0.0025975 | 0.00085443 | -0.0033582 | -0.0021469 | -0.0072889 | 2.554e-05 | -0.51727 | -0.28381 | -0.95673 | -0.59509 | -0.49439 | -0.88806 | -0.53558 | -0.10071 | 121.994 | -1.0117 | -0.61798 | -0.60883 | -0.8606 | -0.75989 | -0.009155 | -122.1451 | -122.4564 | 0.45319 | 0.41199 | 0.059509 | 0.42114 | 0.068664 | -0.064087 | 0.13275 | -122.4792 | 0.33875 | 0.18768 | 0.086975 | 0.25177 | 0.15106 | 0.46234 | 0.36163 | 0.40283 | 0.39368 | 0.67291 | 123.0057 | 0.66376 | 122.9416 | -122.818 | -122.8729 | 0.35248 | 0.32959 | 0.4303 | 0.84686
4579.1719 | 122.8683 | -0.90637 | 121.8018 | -0.091095 | 0.00062166 | 0.022078 | 0.0060263 | 0.003151 | 0.0017645 | 0.0017902 | 0.035278 | -0.0021021 | -0.0010682 | -0.00229 | -0.0023605 | -0.0094251 | -0.0010425 | -0.56763 | -0.31128 | -0.94299 | -0.54016 | -0.39368 | -0.82855 | -0.4715 | 0.018311 | 121.962 | -0.98419 | -0.51727 | -0.48065 | -0.72327 | -0.65002 | -0.036621 | -122.113 | -122.3419 | 0.51269 | 0.43487 | 0.07782 | 0.4715 | 0.11444 | -0.07782 | 0.16022 | -122.319 | 0.42572 | 0.25635 | 0.1831 | 0.33417 | 0.26092 | 0.54932 | 0.40283 | 0.50354 | 0.46692 | 0.63171 | 122.9462 | 0.59509 | 122.8683 | -122.7448 | -122.7859 | 0.36621 | 0.3891 | 0.33874 | 0.92468
4580.1719 | 122.7631 | -0.94757 | 121.907 | -0.052948 | -0.00023294 | 0.022292 | 0.0077353 | 0.001442 | -0.0027215 | 0.0017902 | -0.047119 | 0.0036657 | -0.00042717 | 0.0017688 | -0.0017197 | -0.0077161 | -0.00040166 | -0.61798 | -0.30212 | -0.97504 | -0.63629 | -0.52643 | -0.92468 | -0.57678 | -0.13733 | 121.994 | -1.0071 | -0.63629 | -0.63171 | -0.86517 | -0.76446 | -0.027466 | -122.2092 | -122.5433 | 0.42114 | 0.37079 | 0.022888 | 0.39826 | 0.050354 | -0.059509 | 0.086976 | -122.5433 | 0.31586 | 0.18311 | 0.082398 | 0.24262 | 0.14191 | 0.44861 | 0.33875 | 0.37537 | 0.37079 | 0.67291 | 123.0011 | 0.64545 | 122.9416 | -122.8821 | -122.9141 | 0.31128 | 0.31128 | 0.32959 | 0.81024
4581.1719 | 122.8088 | -0.91095 | 121.9254 | -0.091095 | -0.00023294 | 0.02101 | 0.0085897 | 0.0018692 | -0.00058531 | 0.0037128 | -0.028809 | 0.0025975 | 0.0021362 | -0.003999 | -0.0021469 | -0.0085705 | 0.0017345 | -0.64087 | -0.31128 | -0.98877 | -0.66834 | -0.54932 | -0.94299 | -0.57678 | -0.1236 | 122.0261 | -1.0254 | -0.54474 | -0.58136 | -0.84686 | -0.74616 | -0.07782 | -122.2366 | -122.5937 | 0.36163 | 0.33417 | -0.032043 | 0.41199 | 0.045777 | -0.11444 | 0.10071 | -122.4701 | 0.32959 | 0.1648 | 0.064087 | 0.27924 | 0.17853 | 0.43945 | 0.32044 | 0.44403 | 0.48065 | 0.67749 | 123.0515 | 0.59967 | 122.937 | -122.9141 | -122.9507 | 0.24262 | 0.36621 | 0.27008 | 0.78735
4582.1719 | 122.7493 | -0.9201 | 121.9437 | -0.091095 | 0.0010489 | 0.019514 | 0.0083761 | 0.0018692 | -0.0010125 | 0.0043536 | -0.059326 | 0.0034521 | 0.001068 | -0.0037854 | -0.0032151 | -0.0053663 | 0.00045294 | -0.63171 | -0.30212 | -0.97504 | -0.66376 | -0.54474 | -0.94757 | -0.59509 | -0.19226 | 122.0032 | -1.0162 | -0.62256 | -0.59967 | -0.87433 | -0.74616 | -0.054932 | -122.2458 | -122.6074 | 0.37537 | 0.32501 | -0.027466 | 0.37994 | 0.027466 | -0.09613 | 0.059509 | -122.5662 | 0.32043 | 0.17395 | 0.045776 | 0.27008 | 0.14191 | 0.4303 | 0.31128 | 0.41656 | 0.39368 | 0.67291 | 123.0194 | 0.61798 | 122.9233 | -122.9187 | -122.9599 | 0.25635 | 0.29755 | 0.28839 | 0.72784
4583.1719 | 122.7493 | -0.9201 | 121.9894 | -0.052948 | 0.00040806 | 0.019942 | 0.0081625 | 0.0016556 | 0.0019781 | 0.0037128 | -0.022705 | 0.0032385 | 0.001068 | -0.00229 | -0.0012925 | -0.0062207 | 0.00066654 | -0.61798 | -0.28381 | -0.98419 | -0.6546 | -0.53101 | -0.9201 | -0.57678 | -0.15564 | 122.0169 | -1.0117 | -0.60425 | -0.59052 | -0.85144 | -0.75531 | -0.064087 | -122.2733 | -122.644 | 0.3891 | 0.34332 | 0 | 0.40741 | 0.064087 | -0.091553 | 0.027466 | -122.5937 | 0.32959 | 0.16479 | 0.068665 | 0.25635 | 0.16022 | 0.45319 | 0.32959 | 0.42114 | 0.40741 | 0.70038 | 123.0286 | 0.63629 | 122.937 | -122.9736 | -123.0011 | 0.2655 | 0.31586 | 0.30212 | 0.76446
4584.1719 | 122.8912 | -0.87433 | 121.9437 | -0.12924 | -0.0010873 | 0.021651 | 0.0064535 | -0.003685 | 0.00069649 | 0.0015766 | 0.081055 | 0.0011023 | 0.00042723 | -0.007417 | -0.0030013 | -0.0089979 | -0.0012561 | -0.60425 | -0.35248 | -0.94757 | -0.54932 | -0.4303 | -0.80109 | -0.43945 | 0 | 121.9986 | -0.93842 | -0.48065 | -0.4303 | -0.67291 | -0.60883 | -0.073242 | -122.2961 | -122.493 | 0.44403 | 0.43488 | 0.073243 | 0.50812 | 0.14649 | -0.064087 | 0.054931 | -122.4243 | 0.44403 | 0.2655 | 0.20142 | 0.32959 | 0.2655 | 0.51727 | 0.39826 | 0.50812 | 0.45776 | 0.59509 | 122.937 | 0.52185 | 122.8729 | -122.8912 | -122.8821 | 0.32501 | 0.39368 | 0.27008 | 0.87433
4585.1719 | 122.7768 | -0.91553 | 121.9482 | -0.022431 | -1.9142e-05 | 0.020796 | 0.0083761 | 0.0022964 | -0.0012261 | -0.0016278 | -0.050171 | 0.0034521 | -0.0014954 | 0.0045458 | -0.0027877 | -0.0081433 | 0.0047253 | -0.55389 | -0.24261 | -0.86975 | -0.59509 | -0.48523 | -0.87433 | -0.52643 | -0.068665 | 122.0398 | -0.97046 | -0.58136 | -0.57678 | -0.82855 | -0.74158 | 0.045776 | -122.1909 | -122.5433 | 0.4303 | 0.3891 | 0.041198 | 0.34332 | -0.004578 | -0.054932 | 0.091553 | -122.5296 | 0.33874 | 0.17395 | 0.086975 | 0.22888 | 0.14191 | 0.38452 | 0.27466 | 0.39368 | 0.3891 | 0.62714 | 123.0103 | 0.67291 | 122.9553 | -122.818 | -122.9187 | 0.32043 | 0.33417 | 0.36163 | 0.84686
4586.1719 | 122.7585 | -0.91095 | 121.9803 | -0.083466 | -0.00044654 | 0.02101 | 0.011367 | 0.0022964 | 0.00048269 | 0.0028582 | -0.044067 | 0.0015295 | 0.0023498 | -0.0086988 | -0.0019333 | -0.0066479 | 0.0010937 | -0.59967 | -0.29755 | -0.94757 | -0.63171 | -0.54016 | -0.91095 | -0.58136 | -0.16937 | 122.049 | -0.99792 | -0.58594 | -0.5722 | -0.84686 | -0.71869 | -0.036621 | -122.2778 | -122.612 | 0.37079 | 0.32959 | 0 | 0.36621 | 0.036621 | -0.086975 | 0.068664 | -122.5662 | 0.33875 | 0.19226 | 0.064087 | 0.27924 | 0.15106 | 0.40741 | 0.31586 | 0.42572 | 0.41199 | 0.65003 | 123.0469 | 0.6134 | 122.9599 | -122.9279 | -122.9782 | 0.27924 | 0.32501 | 0.31128 | 0.74158
4587.1719 | 122.8271 | -0.86975 | 121.9849 | -0.060578 | -0.0021555 | 0.020583 | 0.0096579 | -0.0015488 | -0.00079891 | 0.0043536 | -0.025757 | 0.0038793 | -0.00064077 | -0.003999 | -0.0034287 | -0.0051527 | -0.00018806 | -0.55847 | -0.29755 | -0.93384 | -0.57678 | -0.46692 | -0.81482 | -0.51727 | -0.054932 | 122.0718 | -0.92926 | -0.50354 | -0.48523 | -0.72327 | -0.65918 | -0.064087 | -122.2824 | -122.5616 | 0.40283 | 0.35248 | 0.054932 | 0.41656 | 0.11902 | -0.059509 | 0.086975 | -122.4884 | 0.38452 | 0.21057 | 0.14648 | 0.27008 | 0.20599 | 0.46692 | 0.35706 | 0.44403 | 0.42572 | 0.63629 | 123.0011 | 0.57221 | 122.9416 | -122.9187 | -122.9141 | 0.29297 | 0.36621 | 0.31128 | 0.81482
4588.1719 | 122.7722 | -0.86975 | 121.994 | -0.052948 | 0.0012625 | 0.019942 | 0.0066671 | 0.0037918 | -0.0018671 | 0.0026446 | -0.034912 | 0.0055883 | 0.00064083 | -0.00058098 | -0.0012925 | -0.0066479 | 0.0010937 | -0.55389 | -0.24719 | -0.85602 | -0.6134 | -0.49439 | -0.83771 | -0.54016 | -0.10986 | 122.0901 | -0.95215 | -0.53558 | -0.53558 | -0.77362 | -0.69122 | 0.013733 | -122.2412 | -122.6074 | 0.37537 | 0.32959 | 0.032043 | 0.31586 | 0.01831 | -0.082397 | 0.09613 | -122.5296 | 0.33417 | 0.17853 | 0.09613 | 0.26092 | 0.17853 | 0.36163 | 0.24261 | 0.41656 | 0.41656 | 0.60883 | 123.0423 | 0.62256 | 122.9599 | -122.85 | -122.9462 | 0.25635 | 0.33417 | 0.31586 | 0.75989
4589.1719 | 122.7631 | -0.8606 | 121.994 | -0.075836 | -0.00066014 | 0.019942 | 0.0081625 | -0.00026703 | -0.00037171 | 0.00029479 | -0.01355 | 0.0019567 | 0.0025634 | 0.003905 | -0.0021469 | -0.0062207 | 0.0017345 | -0.59967 | -0.28839 | -0.93384 | -0.63629 | -0.53558 | -0.88806 | -0.56305 | -0.1831 | 122.0673 | -0.95673 | -0.55847 | -0.54474 | -0.8194 | -0.68207 | -0.073242 | -122.2824 | -122.6303 | 0.32501 | 0.29755 | -0.027466 | 0.37079 | 0.045776 | -0.09613 | 0.073242 | -122.5525 | 0.31586 | 0.17853 | 0.041199 | 0.27466 | 0.13733 | 0.39825 | 0.29755 | 0.41199 | 0.39825 | 0.64545 | 123.024 | 0.57221 | 122.9279 | -122.9279 | -122.9507 | 0.2243 | 0.30212 | 0.26093 | 0.67749
4590.1719 | 122.7997 | -0.81024 | 122.0306 | -0.037689 | 0.0025443 | 0.019514 | 0.0085897 | 0.00080117 | -0.0018671 | 0.00072199 | -0.01355 | 0.0030249 | 0.00085443 | 0.0043322 | -0.0017197 | -0.0070753 | 0.0019483 | -0.54932 | -0.27924 | -0.89264 | -0.59052 | -0.45776 | -0.81024 | -0.51727 | -0.10529 | 122.0856 | -0.92926 | -0.50354 | -0.45776 | -0.74616 | -0.63629 | -0.082397 | -122.3099 | -122.6212 | 0.35248 | 0.29297 | 0 | 0.37537 | 0.082397 | -0.11902 | 0.054931 | -122.5342 | 0.35248 | 0.17395 | 0.064087 | 0.29297 | 0.1831 | 0.43487 | 0.30212 | 0.4715 | 0.42572 | 0.6134 | 123.0148 | 0.53101 | 122.8958 | -122.9233 | -122.9599 | 0.21973 | 0.3067 | 0.26093 | 0.70496
4591.1719 | 122.8226 | -0.82398 | 122.0032 | -0.098725 | -0.00023294 | 0.022078 | 0.0081625 | 0.0012284 | 0.00026909 | 0.0017902 | -0.010498 | 0.0028113 | 0.00085443 | -0.0050672 | -0.0010787 | -0.0051527 | -0.00082886 | -0.54932 | -0.29755 | -0.89264 | -0.5722 | -0.44861 | -0.78735 | -0.49896 | -0.091553 | 122.081 | -0.92926 | -0.48981 | -0.48065 | -0.74158 | -0.6546 | -0.068664 | -122.3007 | -122.5754 | 0.37537 | 0.32501 | 0.036621 | 0.39368 | 0.10528 | -0.10528 | 0.07782 | -122.493 | 0.34332 | 0.16937 | 0.082398 | 0.27466 | 0.18768 | 0.44403 | 0.32043 | 0.44861 | 0.43945 | 0.59509 | 123.0103 | 0.52643 | 122.905 | -122.8958 | -122.9324 | 0.25177 | 0.33417 | 0.27466 | 0.73242
4592.1719 | 122.8317 | -0.85144 | 122.0032 | -0.10635 | -0.0013009 | 0.02101 | 0.0081625 | -0.00069423 | -0.00037171 | 0.00093559 | 0.010864 | 0.00046135 | -0.00085457 | -0.005708 | -0.0021469 | -0.0062207 | -0.00040166 | -0.53558 | -0.28839 | -0.89722 | -0.55847 | -0.44403 | -0.78278 | -0.47607 | -0.10071 | 122.1039 | -0.94757 | -0.48523 | -0.48065 | -0.73242 | -0.63629 | -0.045777 | -122.2916 | -122.5616 | 0.40741 | 0.37537 | 0.068664 | 0.42114 | 0.11444 | -0.096131 | 0.10071 | -122.4884 | 0.37079 | 0.21515 | 0.11902 | 0.31128 | 0.21515 | 0.45319 | 0.33875 | 0.46692 | 0.46234 | 0.60883 | 123.0515 | 0.56305 | 122.9553 | -122.9004 | -122.9507 | 0.29297 | 0.36621 | 0.31586 | 0.75073
4593.1719 | 122.8958 | -0.83771 | 121.962 | -0.075836 | 0.00062166 | 0.019942 | 0.0075217 | 0.00016017 | -0.00037171 | 0.003072 | -0.0043946 | 0.0021703 | -0.00064077 | -0.0031446 | -0.00065151 | -0.0068615 | -0.00040166 | -0.57678 | -0.27008 | -0.90637 | -0.56305 | -0.45319 | -0.82398 | -0.49896 | -0.10529 | 122.081 | -0.9201 | -0.4303 | -0.43488 | -0.68207 | -0.58136 | -0.068664 | -122.2321 | -122.525 | 0.38452 | 0.33875 | 0.013733 | 0.40741 | 0.082397 | -0.082397 | 0.11902 | -122.3923 | 0.40283 | 0.25635 | 0.15564 | 0.33874 | 0.23804 | 0.45319 | 0.34332 | 0.48523 | 0.48981 | 0.63629 | 123.0011 | 0.56763 | 122.9187 | -122.8683 | -122.8821 | 0.27466 | 0.40741 | 0.26093 | 0.73242
4594.1719 | 122.905 | -0.82855 | 121.9574 | -0.10635 | -1.9142e-05 | 0.021437 | 0.0085897 | -5.343e-05 | 0.00048269 | -0.00055961 | 0.062744 | 0.00046135 | 0.0025634 | -0.0027174 | -0.0034287 | -0.0053663 | -0.00082886 | -0.53101 | -0.32501 | -0.8606 | -0.50354 | -0.36163 | -0.737 | -0.42572 | -0.18768 | 121.9986 | -0.91095 | -0.42114 | -0.40283 | -0.6546 | -0.5722 | -0.032044 | -122.2824 | -122.4609 | 0.46692 | 0.40283 | 0.091552 | 0.43488 | 0.1236 | -0.082398 | 0.041199 | -122.3785 | 0.42572 | 0.25635 | 0.17395 | 0.33875 | 0.25635 | 0.49896 | 0.35706 | 0.50812 | 0.48981 | 0.53558 | 122.9095 | 0.50354 | 122.8271 | -122.818 | -122.8683 | 0.32501 | 0.40741 | 0.29755 | 0.64087
4595.1719 | 122.8271 | -0.84686 | 121.9986 | -0.075836 | 0.00062166 | 0.022505 | 0.0083761 | -0.00048063 | -0.00058531 | -0.00013241 | -0.0043946 | 0.0030249 | 0.0021362 | -0.0025036 | -0.0038559 | -0.0062207 | -0.0027515 | -0.5722 | -0.27008 | -0.90179 | -0.58594 | -0.46692 | -0.78735 | -0.48065 | -0.1831 | 122.0856 | -0.91095 | -0.49896 | -0.45319 | -0.72327 | -0.64545 | -0.054931 | -122.2687 | -122.5845 | 0.37994 | 0.36621 | 0.059509 | 0.42114 | 0.11444 | -0.064087 | 0.086975 | -122.4976 | 0.39368 | 0.20142 | 0.1236 | 0.2655 | 0.18768 | 0.43488 | 0.31586 | 0.45776 | 0.41199 | 0.63171 | 122.9965 | 0.57678 | 122.9324 | -122.9004 | -122.9095 | 0.26093 | 0.3479 | 0.27466 | 0.66376
4596.1719 | 122.8409 | -0.83771 | 122.0078 | -0.075836 | -0.0015145 | 0.021864 | 0.0088033 | 0.0010148 | -0.0014399 | -0.00098701 | -0.019653 | 0.0023839 | 0.00042723 | 0.0060412 | -0.0040695 | -0.0057935 | 2.554e-05 | -0.54474 | -0.28381 | -0.92468 | -0.55389 | -0.43488 | -0.78735 | -0.48981 | -0.16022 | 122.0901 | -0.90637 | -0.48065 | -0.4715 | -0.71869 | -0.62714 | -0.086975 | -122.2916 | -122.5616 | 0.40283 | 0.3479 | 0.050354 | 0.43488 | 0.13733 | -0.068664 | 0.082398 | -122.4884 | 0.36621 | 0.21057 | 0.11902 | 0.27924 | 0.18768 | 0.48981 | 0.37079 | 0.43487 | 0.42572 | 0.64087 | 122.9965 | 0.5539 | 122.9279 | -122.9324 | -122.9141 | 0.28381 | 0.35706 | 0.29297 | 0.67749
4597.1719 | 122.85 | -0.84228 | 122.0169 | 0.00045798 | -0.00044654 | 0.021223 | 0.0096579 | -0.001976 | 0.00048269 | 0.003072 | -0.0074462 | 0.0036657 | 0.00042723 | 0.00048702 | -0.0034287 | -0.0051527 | -0.0023243 | -0.54474 | -0.26093 | -0.90179 | -0.56305 | -0.44403 | -0.77362 | -0.4715 | -0.18768 | 122.1085 | -0.93842 | -0.4715 | -0.45319 | -0.71869 | -0.62714 | -0.059509 | -122.2778 | -122.58 | 0.39825 | 0.37079 | 0.068664 | 0.4303 | 0.12817 | -0.096131 | 0.091552 | -122.4884 | 0.3891 | 0.21515 | 0.1236 | 0.31128 | 0.21973 | 0.45776 | 0.33874 | 0.48523 | 0.46692 | 0.64087 | 123.0469 | 0.58136 | 122.9507 | -122.9187 | -122.9553 | 0.27924 | 0.37079 | 0.29755 | 0.6546
4598.1719 | 122.85 | -0.85144 | 122.0215 | -0.083466 | 0.0019035 | 0.02101 | 0.0098715 | -0.0015488 | -0.00037171 | 0.001363 | 0.010864 | 0.0021703 | 0.0014954 | 0.00048702 | -0.0032151 | -0.0068615 | 0.00066654 | -0.55847 | -0.25635 | -0.90637 | -0.58594 | -0.4715 | -0.76446 | -0.48523 | -0.21973 | 122.1085 | -0.91095 | -0.46692 | -0.44861 | -0.6958 | -0.6134 | -0.054932 | -122.2778 | -122.6074 | 0.37994 | 0.36621 | 0.086975 | 0.42114 | 0.14191 | -0.05951 | 0.086975 | -122.4884 | 0.40283 | 0.23804 | 0.15564 | 0.29755 | 0.21515 | 0.43487 | 0.32043 | 0.46234 | 0.44403 | 0.65002 | 123.0194 | 0.59509 | 122.9599 | -122.9279 | -122.9324 | 0.2655 | 0.38452 | 0.29297 | 0.63171
4599.1719 | 122.8134 | -0.80109 | 122.0215 | -0.060578 | 0.00040806 | 0.022078 | 0.0088033 | 0.0018692 | 0.00069649 | 0.00029479 | -0.0074462 | 0.0047339 | 2.8e-08 | -0.0010084 | -0.0023605 | -0.0064343 | 0.0025891 | -0.54932 | -0.25635 | -0.88348 | -0.55847 | -0.42572 | -0.77362 | -0.48065 | -0.15106 | 122.2137 | -0.85602 | -0.44861 | -0.45776 | -0.71869 | -0.62714 | -0.082398 | -122.2778 | -122.58 | 0.37537 | 0.32043 | 0.027465 | 0.40283 | 0.10986 | -0.054932 | 0.19226 | -122.4701 | 0.34332 | 0.17395 | 0.082397 | 0.22888 | 0.13733 | 0.45776 | 0.32501 | 0.39825 | 0.40741 | 0.62714 | 123.0698 | 0.54474 | 123.0148 | -122.905 | -122.8775 | 0.24261 | 0.35248 | 0.25177 | 0.65002
4600.1719 | 122.7951 | -0.84686 | 122.0306 | -0.075836 | -0.0021555 | 0.017805 | 0.0075217 | -0.0045394 | 0.0011237 | 0.00072199 | 0.03833 | 0.0034521 | 0.0012818 | -0.0067762 | -0.0015061 | -0.0085705 | 0.0010937 | -0.58136 | -0.24719 | -0.89722 | -0.58136 | -0.47607 | -0.78278 | -0.50354 | -0.28381 | 122.0993 | -0.92926 | -0.52643 | -0.48065 | -0.737 | -0.66376 | -0.050354 | -122.2778 | -122.612 | 0.37079 | 0.34332 | 0.064087 | 0.39368 | 0.11444 | -0.082397 | 0.068664 | -122.5571 | 0.36621 | 0.18311 | 0.10986 | 0.2655 | 0.19226 | 0.42114 | 0.31586 | 0.44861 | 0.40283 | 0.65003 | 123.0286 | 0.59967 | 122.9462 | -122.9279 | -122.9599 | 0.2655 | 0.32044 | 0.2655 | 0.56305
4601.1719 | 122.85 | -0.8194 | 122.0169 | -0.068207 | -0.0015145 | 0.022292 | 0.0073081 | 0.0016556 | 5.5488e-05 | 0.0017902 | 0.001709 | 0.0030249 | 2.8e-08 | -0.0010084 | -0.0040695 | -0.0094251 | -0.0027515 | -0.54474 | -0.24719 | -0.89722 | -0.5722 | -0.44403 | -0.75073 | -0.46692 | -0.2243 | 122.1313 | -0.92926 | -0.46234 | -0.44403 | -0.6958 | -0.60883 | -0.07782 | -122.2641 | -122.5891 | 0.37537 | 0.35248 | 0.068665 | 0.4303 | 0.14649 | -0.10986 | 0.11444 | -122.4792 | 0.37537 | 0.21057 | 0.1236 | 0.32043 | 0.23346 | 0.45319 | 0.32501 | 0.48523 | 0.46692 | 0.65003 | 123.0606 | 0.57221 | 122.9507 | -122.9141 | -122.9462 | 0.24719 | 0.35706 | 0.27466 | 0.59509
4602.1719 | 122.8363 | -0.81482 | 122.0123 | -0.075836 | -0.0013009 | 0.019514 | 0.0096579 | -5.343e-05 | -0.0027215 | 0.00093559 | -0.0013428 | 0.00024775 | 0.00042723 | -0.0025036 | -0.0040695 | -0.0053663 | 0.0013073 | -0.50812 | -0.27008 | -0.8606 | -0.55389 | -0.42572 | -0.74158 | -0.47607 | -0.20142 | 122.1405 | -0.89722 | -0.46234 | -0.45776 | -0.70496 | -0.6134 | -0.045777 | -122.2824 | -122.5662 | 0.3891 | 0.33874 | 0.073242 | 0.38452 | 0.11902 | -0.082398 | 0.12817 | -122.4747 | 0.35705 | 0.20142 | 0.10986 | 0.28381 | 0.19226 | 0.43488 | 0.3067 | 0.43945 | 0.43488 | 0.59052 | 123.0377 | 0.54474 | 122.9553 | -122.8729 | -122.9095 | 0.26092 | 0.35248 | 0.3067 | 0.6134
4603.1719 | 122.8363 | -0.83313 | 122.0169 | -0.083466 | -0.00087374 | 0.021223 | 0.0081625 | -0.005394 | -0.00015811 | -0.00034601 | 0.013916 | 0.0017431 | 0.0012818 | -0.0025036 | -0.0032151 | -0.0068615 | 0.0010937 | -0.54474 | -0.2243 | -0.84228 | -0.5722 | -0.48981 | -0.76904 | -0.48065 | -0.27008 | 122.0947 | -0.92926 | -0.48065 | -0.44861 | -0.74158 | -0.63629 | -0.009155 | -122.2412 | -122.5891 | 0.34332 | 0.35248 | 0.064087 | 0.36163 | 0.073242 | -0.09613 | 0.07782 | -122.4976 | 0.38452 | 0.19684 | 0.091553 | 0.29297 | 0.18768 | 0.35248 | 0.27008 | 0.48065 | 0.44861 | 0.61798 | 123.024 | 0.60883 | 122.9279 | -122.8592 | -122.9462 | 0.26093 | 0.35248 | 0.28839 | 0.56305
4604.1719 | 122.8363 | -0.84686 | 122.0215 | -0.091095 | -0.0021555 | 0.019728 | 0.0079489 | -0.0028304 | 0.0015509 | -0.0016278 | 0.029175 | 0.0011023 | 0.003418 | 0.0079638 | -0.0015061 | -0.0057935 | 0.0017345 | -0.55847 | -0.23804 | -0.86975 | -0.60883 | -0.49896 | -0.74616 | -0.49439 | -0.2655 | 122.1588 | -0.89264 | -0.48523 | -0.45319 | -0.71869 | -0.63629 | -0.022888 | -122.2595 | -122.6303 | 0.3479 | 0.35248 | 0.10071 | 0.37537 | 0.1236 | -0.045776 | 0.13733 | -122.5067 | 0.39368 | 0.21057 | 0.12817 | 0.25635 | 0.17395 | 0.37079 | 0.26093 | 0.43945 | 0.40741 | 0.63171 | 123.0515 | 0.60883 | 123.0057 | -122.8912 | -122.9141 | 0.23804 | 0.36163 | 0.28839 | 0.58136
4605.1719 | 122.8088 | -0.81024 | 122.081 | -0.083466 | -0.0015145 | 0.01866 | 0.0081625 | -0.00026703 | -0.0033625 | 0.0011494 | 0.03833 | 0.00088875 | 0.0021362 | 0.0019824 | 0.00020289 | -0.0077161 | -0.00061526 | -0.55847 | -0.23804 | -0.87891 | -0.58594 | -0.4715 | -0.76446 | -0.49439 | -0.27466 | 122.1313 | -0.91553 | -0.46234 | -0.45319 | -0.71869 | -0.63629 | -0.068664 | -122.319 | -122.6669 | 0.33875 | 0.31586 | 0.045777 | 0.38452 | 0.11444 | -0.10528 | 0.050354 | -122.5433 | 0.35706 | 0.17395 | 0.091553 | 0.27924 | 0.19684 | 0.40741 | 0.29297 | 0.46234 | 0.45319 | 0.64087 | 123.0469 | 0.57221 | 122.9416 | -122.9599 | -122.9965 | 0.2243 | 0.3479 | 0.25177 | 0.53558
4606.1719 | 122.7859 | -0.84228 | 122.0718 | -0.068207 | 0.00062166 | 0.020369 | 0.0079489 | -0.0032578 | -0.00015811 | 0.002431 | 0.059692 | 0.0011023 | 0.0012818 | -0.0014356 | -0.0027877 | -0.0064343 | -0.0012561 | -0.5127 | -0.24719 | -0.84228 | -0.56305 | -0.44861 | -0.71869 | -0.45776 | -0.25177 | 122.1313 | -0.90637 | -0.49439 | -0.44861 | -0.70496 | -0.65002 | 0 | -122.319 | -122.6349 | 0.39368 | 0.38452 | 0.1236 | 0.38452 | 0.1236 | -0.064087 | 0.05951 | -122.5662 | 0.39368 | 0.19226 | 0.13733 | 0.25635 | 0.20142 | 0.39368 | 0.27924 | 0.45776 | 0.41199 | 0.59509 | 123.0377 | 0.59509 | 122.9736 | -122.9141 | -122.9782 | 0.27924 | 0.3479 | 0.32959 | 0.59051
4607.1719 | 122.8043 | -0.80566 | 122.0535 | -0.060578 | -0.0015145 | 0.019301 | 0.0060263 | -0.00069423 | 5.5488e-05 | -0.00055961 | 0.026123 | 0.0017431 | 0.0014954 | 0.0015552 | -0.0040695 | -0.0081433 | -0.0048877 | -0.50354 | -0.24261 | -0.8606 | -0.5127 | -0.42114 | -0.6958 | -0.4303 | -0.2243 | 122.1405 | -0.89264 | -0.48523 | -0.44403 | -0.72784 | -0.6546 | -0.054932 | -122.2961 | -122.5662 | 0.38452 | 0.37537 | 0.10986 | 0.4303 | 0.1648 | -0.086975 | 0.086975 | -122.5388 | 0.36163 | 0.15106 | 0.07782 | 0.23804 | 0.16479 | 0.43945 | 0.3479 | 0.44861 | 0.40741 | 0.61798 | 123.0331 | 0.56305 | 122.9462 | -122.9141 | -122.9462 | 0.29297 | 0.32044 | 0.30212 | 0.58136
4608.1719 | 122.7859 | -0.8194 | 122.0535 | -0.12161 | -0.00023294 | 0.018233 | 0.0079489 | 0.001442 | -0.00058531 | 0.00029479 | 0.026123 | 0.0015295 | -0.00021357 | -0.0037854 | -0.0047103 | -0.0085705 | 0.0042981 | -0.55847 | -0.24719 | -0.88348 | -0.56763 | -0.4715 | -0.75073 | -0.48981 | -0.27008 | 122.1405 | -0.89722 | -0.48523 | -0.44861 | -0.71869 | -0.66834 | -0.064087 | -122.3007 | -122.6212 | 0.3479 | 0.32959 | 0.068665 | 0.39368 | 0.13275 | -0.07782 | 0.086975 | -122.5388 | 0.37079 | 0.15106 | 0.10071 | 0.22888 | 0.17853 | 0.41199 | 0.31586 | 0.44861 | 0.41199 | 0.63629 | 123.0377 | 0.57221 | 122.9599 | -122.937 | -122.9507 | 0.25177 | 0.33417 | 0.26093 | 0.54932
4609.1719 | 122.8317 | -0.80566 | 122.0535 | -0.060578 | -0.00023294 | 0.018874 | 0.010299 | -5.343e-05 | -0.0016535 | 0.001363 | -0.0043946 | 0.0038793 | -0.0012818 | -0.0033582 | -0.0027877 | -0.0075025 | 0.0030163 | -0.52185 | -0.24719 | -0.86517 | -0.52643 | -0.39825 | -0.72327 | -0.47607 | -0.18768 | 122.1634 | -0.89722 | -0.42114 | -0.41657 | -0.67749 | -0.59967 | -0.059509 | -122.3007 | -122.58 | 0.40741 | 0.32959 | 0.082397 | 0.3891 | 0.14191 | -0.091553 | 0.10986 | -122.4747 | 0.3891 | 0.20599 | 0.12817 | 0.29755 | 0.21973 | 0.46692 | 0.33874 | 0.48065 | 0.47607 | 0.61798 | 123.0606 | 0.55847 | 122.9691 | -122.9187 | -122.9507 | 0.27924 | 0.38452 | 0.28381 | 0.61798
4610.1719 | 122.8409 | -0.82855 | 122.0535 | -0.045319 | 0.00019446 | 0.019514 | 0.0079489 | -0.00026703 | -0.0010125 | 0.0017902 | 0.001709 | 0.0015295 | -0.00042717 | 5.9824e-05 | -0.0021469 | -0.0077161 | 0.00045294 | -0.51727 | -0.2243 | -0.85144 | -0.55847 | -0.46692 | -0.72784 | -0.48065 | -0.23804 | 122.1542 | -0.90179 | -0.44403 | -0.41657 | -0.71411 | -0.60425 | -0.022888 | -122.2778 | -122.612 | 0.36163 | 0.3479 | 0.10071 | 0.37079 | 0.1236 | -0.073242 | 0.10071 | -122.4976 | 0.41199 | 0.2243 | 0.11444 | 0.29755 | 0.18768 | 0.38452 | 0.29297 | 0.48523 | 0.45776 | 0.62714 | 123.056 | 0.60425 | 122.9828 | -122.905 | -122.9553 | 0.27008 | 0.38452 | 0.31128 | 0.59051
4611.1719 | 122.7951 | -0.8194 | 122.0993 | -0.068207 | -0.0017281 | 0.016737 | 0.0090169 | -0.00026703 | -0.0016535 | 0.00072199 | 0.013916 | 0.0045203 | 0.001068 | -0.00036738 | -0.00086511 | -0.0053663 | -0.0014697 | -0.55847 | -0.23346 | -0.86517 | -0.59509 | -0.4715 | -0.737 | -0.48523 | -0.24719 | 122.1771 | -0.89264 | -0.46692 | -0.44403 | -0.71411 | -0.62714 | -0.045776 | -122.3328 | -122.6944 | 0.3479 | 0.33417 | 0.082397 | 0.37994 | 0.12817 | -0.073242 | 0.07782 | -122.5662 | 0.37537 | 0.19226 | 0.10529 | 0.2655 | 0.17853 | 0.39368 | 0.27008 | 0.44861 | 0.42572 | 0.63171 | 123.0698 | 0.58594 | 122.9965 | -122.9645 | -122.9919 | 0.2243 | 0.35248 | 0.26093 | 0.57221
4612.1719 | 122.8134 | -0.8194 | 122.0993 | -0.037689 | -0.00087374 | 0.021651 | 0.0073081 | 0.00016017 | -0.0031489 | -0.00013241 | 0.03833 | 0.00067495 | 0.001709 | -0.0016492 | -0.0040695 | -0.0062207 | -0.0018971 | -0.55389 | -0.23346 | -0.83771 | -0.57678 | -0.46234 | -0.72327 | -0.48065 | -0.24261 | 122.1771 | -0.90637 | -0.46234 | -0.44403 | -0.70953 | -0.63629 | -0.018311 | -122.3328 | -122.6761 | 0.35706 | 0.33875 | 0.09613 | 0.35706 | 0.11444 | -0.086975 | 0.07782 | -122.5616 | 0.37537 | 0.18311 | 0.10986 | 0.27008 | 0.19684 | 0.37537 | 0.26093 | 0.46234 | 0.44403 | 0.60425 | 123.0835 | 0.58594 | 122.9965 | -122.937 | -123.0057 | 0.24262 | 0.35706 | 0.2655 | 0.57678
4613.1719 | 122.8134 | -0.81482 | 122.1268 | -0.075836 | -0.0025827 | 0.01866 | 0.0083761 | -5.343e-05 | -0.00079891 | -0.002055 | 0.016968 | 0.0032385 | 0.0023498 | -0.00058098 | 0.00020289 | -0.0062207 | 0.00045294 | -0.56305 | -0.23346 | -0.87891 | -0.55847 | -0.45319 | -0.72327 | -0.4715 | -0.24719 | 122.1725 | -0.87891 | -0.45776 | -0.43488 | -0.6958 | -0.63171 | -0.064087 | -122.3602 | -122.6852 | 0.36163 | 0.34332 | 0.091552 | 0.40741 | 0.15564 | -0.064087 | 0.045776 | -122.5845 | 0.37994 | 0.1831 | 0.11902 | 0.24719 | 0.1831 | 0.42572 | 0.32043 | 0.44403 | 0.42114 | 0.64545 | 123.0515 | 0.58136 | 122.9874 | -123.0057 | -123.0057 | 0.25635 | 0.35705 | 0.25177 | 0.56763
4614.1875 | 122.8867 | -0.80109 | 122.0444 | -0.068207 | 0.00083526 | 0.020583 | 0.0060263 | 0.00037377 | 0.00026909 | 0.0026446 | 0.059692 | 0.00024775 | -0.00021357 | -0.0025036 | -0.0030013 | -0.0077161 | 0.0021619 | -0.50812 | -0.25635 | -0.82855 | -0.48981 | -0.39368 | -0.6546 | -0.39825 | -0.27008 | 122.1039 | -0.88348 | -0.37537 | -0.32501 | -0.6134 | -0.54474 | -0.027466 | -122.3007 | -122.5342 | 0.40741 | 0.40283 | 0.14648 | 0.4303 | 0.17395 | -0.082398 | 0.059509 | -122.4197 | 0.47607 | 0.25635 | 0.18768 | 0.33875 | 0.27008 | 0.43487 | 0.33874 | 0.55847 | 0.50812 | 0.5722 | 122.9874 | 0.54474 | 122.905 | -122.8729 | -122.9279 | 0.31128 | 0.42572 | 0.29297 | 0.531
4615.1719 | 122.8134 | -0.8194 | 122.1039 | -0.10635 | -0.0021555 | 0.020796 | 0.010085 | -0.0011214 | 5.5488e-05 | -0.0024822 | 0.02002 | 0.0032385 | 0.00042723 | -0.00058098 | -0.0036423 | -0.0062207 | 0.0038709 | -0.52185 | -0.2243 | -0.82398 | -0.55389 | -0.45319 | -0.70038 | -0.46692 | -0.20599 | 122.2092 | -0.88348 | -0.44403 | -0.4303 | -0.69122 | -0.62714 | -0.004578 | -122.3282 | -122.6578 | 0.36621 | 0.35248 | 0.11902 | 0.35706 | 0.1236 | -0.064087 | 0.10528 | -122.5479 | 0.3891 | 0.19226 | 0.12817 | 0.25635 | 0.19226 | 0.37079 | 0.27008 | 0.45319 | 0.43945 | 0.59967 | 123.0927 | 0.59509 | 123.0286 | -122.9279 | -122.9874 | 0.2655 | 0.37537 | 0.29755 | 0.6134
4616.1719 | 122.8088 | -0.76446 | 122.1405 | -0.045319 | -0.0015145 | 0.018019 | 0.0081625 | 0.0010148 | -0.00037171 | 0.0015766 | -0.0074462 | 0.0023839 | 0.00085443 | 0.0043322 | -0.0017197 | -0.0092115 | -0.0012561 | -0.52185 | -0.21973 | -0.83313 | -0.55389 | -0.45776 | -0.70038 | -0.45776 | -0.20599 | 122.2046 | -0.87433 | -0.31586 | -0.33417 | -0.75989 | -0.64545 | -0.068665 | -122.3602 | -122.6944 | 0.3067 | 0.3067 | 0.064087 | 0.37537 | 0.13275 | -0.10986 | 0.064087 | -122.4564 | 0.4303 | 0.11902 | 0.004577 | 0.22888 | 0.11444 | 0.37537 | 0.27924 | 0.54016 | 0.55847 | 0.6134 | 123.0789 | 0.54474 | 122.9691 | -122.9736 | -123.0148 | 0.21057 | 0.44861 | 0.24261 | 0.55847
4617.1719 | 122.8363 | -0.7782 | 122.1634 | -0.037689 | -0.0021555 | 0.01866 | 0.0077353 | 0.00080117 | -0.0010125 | 0.00072199 | -0.010498 | 0.0013159 | 0.00021363 | 5.9824e-05 | -0.0027877 | -0.0064343 | -0.0051013 | -0.52643 | -0.21973 | -0.83313 | -0.54932 | -0.46234 | -0.6958 | -0.45776 | -0.20142 | 122.2 | -0.87433 | -0.41657 | -0.40741 | -0.6958 | -0.59967 | -0.054932 | -122.3831 | -122.7127 | 0.31586 | 0.32043 | 0.082397 | 0.37537 | 0.13733 | -0.096131 | 0.036621 | -122.58 | 0.37079 | 0.17853 | 0.082397 | 0.27466 | 0.17853 | 0.37079 | 0.28381 | 0.46692 | 0.45776 | 0.6134 | 123.0743 | 0.55847 | 122.9782 | -122.9965 | -123.0377 | 0.22888 | 0.36163 | 0.25177 | 0.57678
4618.1719 | 122.8455 | -0.8194 | 122.1268 | -0.045319 | -0.00023294 | 0.01866 | 0.0094443 | 0.0012284 | -0.00058531 | -0.00013241 | -0.0043946 | 0.0021703 | -0.0010682 | -0.00015378 | -0.0012925 | -0.0072889 | -0.00018806 | -0.5127 | -0.19226 | -0.80109 | -0.54474 | -0.45319 | -0.67291 | -0.45776 | -0.20142 | 122.2046 | -0.8606 | -0.40741 | -0.37994 | -0.68207 | -0.59509 | 0.018311 | -122.319 | -122.6715 | 0.36621 | 0.36163 | 0.14648 | 0.34332 | 0.12817 | -0.041199 | 0.07782 | -122.5342 | 0.43945 | 0.2243 | 0.13733 | 0.2655 | 0.17853 | 0.3479 | 0.25635 | 0.48065 | 0.45319 | 0.60882 | 123.0652 | 0.62714 | 123.024 | -122.9279 | -122.9874 | 0.27466 | 0.41199 | 0.3067 | 0.61798
4619.1875 | 122.9324 | -0.72784 | 122.0947 | -0.068207 | -0.0019417 | 0.019942 | 0.0068807 | 0.001442 | -0.0031489 | 0.0022174 | 0.065796 | 0.0011023 | 0.00021363 | 0.00048702 | -0.0015061 | -0.0077161 | -0.00061526 | -0.46234 | -0.24719 | -0.76904 | -0.42114 | -0.3067 | -0.56763 | -0.32044 | -0.018311 | 122.1817 | -0.80566 | -0.30212 | -0.26093 | -0.51727 | -0.4715 | -0.041199 | -122.3419 | -122.5159 | 0.42114 | 0.40741 | 0.16022 | 0.44861 | 0.20142 | -0.07782 | 0.086975 | -122.3969 | 0.46692 | 0.25635 | 0.21057 | 0.33417 | 0.28839 | 0.46234 | 0.3479 | 0.54474 | 0.50354 | 0.52185 | 122.9874 | 0.48065 | 122.9095 | -122.8638 | -122.9004 | 0.3067 | 0.42572 | 0.2655 | 0.70953
4620.1719 | 122.8271 | -0.76446 | 122.0947 | -0.10635 | 0.00040806 | 0.020583 | 0.0083761 | 0.0035782 | -0.0016535 | -0.00098701 | 0.029175 | 0.0030249 | -0.0012818 | -0.0016492 | -0.0030013 | -0.0083569 | 0.0017345 | -0.45319 | -0.23804 | -0.79193 | -0.46692 | -0.36163 | -0.59052 | -0.39825 | -0.10986 | 122.1863 | -0.82855 | -0.37994 | -0.35706 | -0.64087 | -0.56305 | -0.027466 | -122.3328 | -122.5616 | 0.40283 | 0.36621 | 0.17395 | 0.39368 | 0.20142 | -0.064087 | 0.091552 | -122.4747 | 0.40741 | 0.20142 | 0.1236 | 0.2655 | 0.18768 | 0.4303 | 0.32501 | 0.4715 | 0.44861 | 0.55389 | 123.0148 | 0.52643 | 122.9507 | -122.8867 | -122.9233 | 0.29755 | 0.38452 | 0.31128 | 0.6546
4621.1719 | 122.8134 | -0.79193 | 122.1451 | -0.037689 | -0.00044654 | 0.018019 | 0.0090169 | -0.0011214 | -0.0016535 | 0.00072199 | 0.016968 | 0.0025975 | 0.001068 | -0.010835 | -0.0032151 | -0.0066479 | 0.00066654 | -0.51727 | -0.21973 | -0.8194 | -0.52643 | -0.43488 | -0.65002 | -0.44403 | -0.16937 | 122.2046 | -0.85602 | -0.40283 | -0.39368 | -0.65918 | -0.58594 | -0.027466 | -122.3648 | -122.6715 | 0.35706 | 0.3479 | 0.14191 | 0.37537 | 0.16937 | -0.064087 | 0.059509 | -122.5479 | 0.39825 | 0.20599 | 0.13275 | 0.27008 | 0.19684 | 0.38452 | 0.29297 | 0.46234 | 0.45319 | 0.59967 | 123.0606 | 0.5722 | 122.9965 | -122.9645 | -123.0011 | 0.2655 | 0.3891 | 0.27466 | 0.62256
4622.1719 | 122.818 | -0.77362 | 122.1588 | -0.060578 | 0.00019446 | 0.021864 | 0.0075217 | -0.0030442 | -0.0035761 | -0.0024822 | -0.010498 | 0.0021703 | 0.0032044 | -0.0031446 | -0.0036423 | -0.0070753 | -0.00082886 | -0.52643 | -0.19684 | -0.83313 | -0.54932 | -0.43945 | -0.64545 | -0.43945 | -0.16937 | 122.2412 | -0.82855 | -0.39368 | -0.37537 | -0.66376 | -0.58136 | -0.059509 | -122.3557 | -122.7081 | 0.33417 | 0.33417 | 0.12817 | 0.39368 | 0.18768 | -0.054931 | 0.082398 | -122.5525 | 0.39826 | 0.19226 | 0.10986 | 0.24719 | 0.16479 | 0.39368 | 0.28381 | 0.45319 | 0.43487 | 0.63629 | 123.0698 | 0.57678 | 123.0148 | -122.9919 | -122.9874 | 0.2243 | 0.37994 | 0.24719 | 0.60425
4623.1719 | 122.85 | -0.74616 | 122.1313 | 0.023346 | -0.0010873 | 0.019514 | 0.0088033 | -0.00090783 | -0.00037171 | -0.00077341 | 0.016968 | 0.00024775 | 0.002777 | 0.0036914 | -0.0023605 | -0.0077161 | -0.0012561 | -0.45319 | -0.21057 | -0.78278 | -0.49439 | -0.38452 | -0.59967 | -0.40741 | -0.11444 | 122.2275 | -0.82398 | -0.3891 | -0.36163 | -0.64545 | -0.57678 | -0.036621 | -122.3419 | -122.6257 | 0.36163 | 0.33875 | 0.14648 | 0.37537 | 0.18311 | -0.07782 | 0.09613 | -122.5204 | 0.38452 | 0.16937 | 0.10071 | 0.24719 | 0.17853 | 0.39826 | 0.28839 | 0.46234 | 0.43488 | 0.57221 | 123.0515 | 0.53558 | 122.9736 | -122.9141 | -122.9553 | 0.25177 | 0.35706 | 0.29297 | 0.63171
4624.1719 | 122.8043 | -0.737 | 122.1588 | -0.12161 | -0.0015145 | 0.02101 | 0.010512 | -0.0032578 | -0.0014399 | 0.002431 | -0.059326 | 0.0028113 | 0.0012818 | 0.00091422 | -0.0025741 | -0.0066479 | 0.0017345 | -0.50354 | -0.20599 | -0.80109 | -0.54932 | -0.46692 | -0.6958 | -0.4715 | -0.15106 | 122.2366 | -0.82398 | -0.35706 | -0.38452 | -0.68207 | -0.5722 | -0.064086 | -122.3648 | -122.7081 | 0.27008 | 0.2655 | 0.041199 | 0.32959 | 0.10528 | -0.086975 | 0.07782 | -122.5159 | 0.35248 | 0.1648 | 0.054932 | 0.25177 | 0.14191 | 0.33417 | 0.25177 | 0.43945 | 0.46692 | 0.59509 | 123.0606 | 0.53101 | 122.9736 | -122.9599 | -122.9828 | 0.18768 | 0.37994 | 0.23346 | 0.58594
4625.1719 | 122.8134 | -0.74158 | 122.1451 | -0.045319 | -0.00087374 | 0.02101 | 0.0083761 | 0.00016017 | 5.5488e-05 | 0.00029479 | 0.02002 | 0.0011023 | 0.00085443 | -0.00015378 | 0.00041649 | -0.0079297 | -0.0031787 | -0.49439 | -0.20599 | -0.77362 | -0.52185 | -0.41657 | -0.62714 | -0.42572 | -0.12817 | 122.2504 | -0.83771 | -0.35706 | -0.37079 | -0.63171 | -0.57678 | -0.032044 | -122.3511 | -122.6669 | 0.32501 | 0.31586 | 0.11444 | 0.3479 | 0.14648 | -0.096131 | 0.10528 | -122.5021 | 0.37079 | 0.1648 | 0.10986 | 0.26093 | 0.20599 | 0.35706 | 0.25177 | 0.46692 | 0.48065 | 0.56763 | 123.0881 | 0.53558 | 122.9919 | -122.9187 | -122.9828 | 0.21973 | 0.38452 | 0.24719 | 0.6134
4626.1719 | 122.818 | -0.75073 | 122.1542 | 0.015716 | -0.00044654 | 0.019514 | 0.0079489 | -0.0013352 | -0.0027215 | -0.00034601 | -0.01355 | 0.0034521 | 0.0014954 | 0.005614 | -0.0017197 | -0.0070753 | -0.00040166 | -0.50354 | -0.17853 | -0.79193 | -0.54474 | -0.4303 | -0.62256 | -0.42114 | -0.13275 | 122.2458 | -0.83313 | -0.37994 | -0.35706 | -0.64087 | -0.57678 | -0.041199 | -122.3328 | -122.699 | 0.32043 | 0.32959 | 0.12817 | 0.37079 | 0.16937 | -0.082398 | 0.091553 | -122.5342 | 0.39368 | 0.17395 | 0.10986 | 0.25635 | 0.19226 | 0.36163 | 0.24719 | 0.47607 | 0.45319 | 0.6134 | 123.0789 | 0.5722 | 122.9965 | -122.9462 | -122.9874 | 0.20599 | 0.37079 | 0.24719 | 0.61798
4627.1719 | 122.8226 | -0.74158 | 122.1771 | -0.045319 | -0.0032235 | 0.019728 | 0.0085897 | 0.0044328 | -0.0012261 | -0.0035504 | 0.001709 | 0.00024775 | 0.0019226 | 0.0026232 | -0.0047103 | -0.0075025 | -0.0046741 | -0.49439 | -0.18768 | -0.79193 | -0.53558 | -0.42114 | -0.62714 | -0.42114 | -0.12817 | 122.2733 | -0.81482 | -0.37537 | -0.35248 | -0.62256 | -0.55389 | -0.050354 | -122.3648 | -122.7127 | 0.32043 | 0.32043 | 0.11444 | 0.37079 | 0.1648 | -0.073242 | 0.09613 | -122.5525 | 0.3891 | 0.18768 | 0.11902 | 0.26092 | 0.19226 | 0.37079 | 0.25635 | 0.46234 | 0.43945 | 0.60425 | 123.0881 | 0.55389 | 123.0148 | -122.9691 | -122.9919 | 0.20599 | 0.36621 | 0.24719 | 0.6134
4628.1719 | 122.8455 | -0.72784 | 122.1497 | -0.068207 | -0.0010873 | 0.021864 | 0.0070943 | 0.0010148 | 0.0013373 | -0.00077341 | 0.016968 | 0.0028113 | 2.8e-08 | -0.0014356 | -0.0025741 | -0.0079297 | -0.0036059 | -0.42114 | -0.21057 | -0.75989 | -0.44403 | -0.33417 | -0.54016 | -0.37079 | -0.013733 | 122.2733 | -0.80566 | -0.32959 | -0.32501 | -0.58594 | -0.53101 | -0.032044 | -122.3602 | -122.5937 | 0.39368 | 0.35706 | 0.18768 | 0.3891 | 0.21973 | -0.07782 | 0.1236 | -122.4792 | 0.40283 | 0.19684 | 0.14191 | 0.27466 | 0.21973 | 0.42572 | 0.31586 | 0.48065 | 0.47607 | 0.54932 | 123.0789 | 0.51727 | 123.0011 | -122.9095 | -122.9553 | 0.28381 | 0.39825 | 0.3067 | 0.71411
4629.1719 | 122.8088 | -0.74616 | 122.1909 | -0.060578 | -0.0010873 | 0.020155 | 0.0092307 | 0.00058737 | -0.0012261 | -0.0014142 | 0.02002 | 0.0013159 | 0.001068 | 0.0034778 | -0.0012925 | -0.0070753 | 0.0040845 | -0.46692 | -0.20599 | -0.7782 | -0.49896 | -0.39368 | -0.6134 | -0.41657 | -0.091553 | 122.2549 | -0.82855 | -0.36163 | -0.33417 | -0.62714 | -0.55389 | -0.032043 | -122.3969 | -122.6898 | 0.35248 | 0.32959 | 0.13275 | 0.36163 | 0.16479 | -0.082397 | 0.064087 | -122.5525 | 0.41199 | 0.19226 | 0.11902 | 0.27466 | 0.20142 | 0.38452 | 0.27924 | 0.49438 | 0.46692 | 0.5722 | 123.0835 | 0.54016 | 123.0011 | -122.9691 | -123.0194 | 0.24719 | 0.38452 | 0.27924 | 0.6546
4630.1719 | 122.818 | -0.75073 | 122.1588 | -0.083466 | 0.00040806 | 0.021223 | 0.0060263 | -0.0032578 | 0.0019781 | 0.0017902 | 0.0078126 | 0.00088875 | 0.00021363 | -0.0067762 | -0.0025741 | -0.0085705 | -0.0025379 | -0.45319 | -0.18768 | -0.76446 | -0.49896 | -0.37079 | -0.58594 | -0.39825 | -0.064087 | 122.2641 | -0.80566 | -0.33875 | -0.32501 | -0.6134 | -0.56305 | -0.013733 | -122.3465 | -122.6578 | 0.37994 | 0.35248 | 0.16479 | 0.36621 | 0.17853 | -0.054932 | 0.10529 | -122.4976 | 0.42572 | 0.18768 | 0.13733 | 0.24262 | 0.19226 | 0.39368 | 0.2655 | 0.48065 | 0.46692 | 0.57678 | 123.0698 | 0.56305 | 123.0148 | -122.9233 | -122.9645 | 0.25177 | 0.41199 | 0.29755 | 0.68664
4631.1719 | 122.8455 | -0.72784 | 122.1954 | -0.03006 | -0.00023294 | 0.020155 | 0.0092307 | 0.0029374 | 0.0017645 | -0.00055961 | 0.010864 | 0.0011023 | 0.0012818 | -0.001222 | -0.0027877 | -0.0085705 | -0.0018971 | -0.43488 | -0.20142 | -0.74158 | -0.46234 | -0.3479 | -0.55389 | -0.39368 | -0.041199 | 122.2778 | -0.80109 | -0.33875 | -0.32959 | -0.58594 | -0.53101 | -0.013733 | -122.3969 | -122.6578 | 0.37994 | 0.33417 | 0.17395 | 0.3479 | 0.18768 | -0.073242 | 0.082397 | -122.5342 | 0.39825 | 0.19684 | 0.14191 | 0.27008 | 0.21515 | 0.39368 | 0.27924 | 0.4715 | 0.46234 | 0.54016 | 123.0789 | 0.52643 | 123.0057 | -122.937 | -122.9965 | 0.2655 | 0.3891 | 0.29297 | 0.68665
4632.1719 | 122.818 | -0.70953 | 122.1954 | -0.12924 | -0.0025827 | 0.020369 | 0.0094443 | 0.0012284 | 0.0017645 | 0.001363 | 0.0078126 | 0.0015295 | 0.0014954 | -0.00079478 | -0.0012925 | -0.0042981 | -0.00082886 | -0.41199 | -0.20142 | -0.74616 | -0.42572 | -0.32044 | -0.52643 | -0.35248 | 0.018311 | 122.2504 | -0.77362 | -0.33417 | -0.29755 | -0.58594 | -0.50812 | -0.036621 | -122.3969 | -122.6212 | 0.3891 | 0.35706 | 0.18311 | 0.39368 | 0.21973 | -0.064087 | 0.054931 | -122.5296 | 0.41199 | 0.20142 | 0.1236 | 0.2655 | 0.18768 | 0.42572 | 0.32044 | 0.47608 | 0.43945 | 0.54474 | 123.024 | 0.50812 | 122.9599 | -122.9416 | -122.9691 | 0.28381 | 0.37537 | 0.29755 | 0.72784
4633.1719 | 122.8638 | -0.737 | 122.168 | -0.068207 | -0.0017281 | 0.020796 | 0.0073081 | -0.001976 | -0.00015811 | 0.0011494 | 0.050537 | 0.0019567 | -0.00064077 | -0.0016492 | -0.0038559 | -0.0089979 | -0.00061526 | -0.42114 | -0.21515 | -0.74158 | -0.4303 | -0.3067 | -0.51727 | -0.33875 | 0.027466 | 122.2458 | -0.79193 | -0.31586 | -0.30212 | -0.55847 | -0.50812 | -0.004577 | -122.3831 | -122.5983 | 0.4303 | 0.39825 | 0.21973 | 0.40283 | 0.2243 | -0.054931 | 0.07782 | -122.4838 | 0.43488 | 0.22888 | 0.17853 | 0.28381 | 0.23346 | 0.43488 | 0.31128 | 0.48981 | 0.47607 | 0.52643 | 123.0377 | 0.52185 | 122.9828 | -122.9095 | -122.9599 | 0.3067 | 0.42114 | 0.31586 | 0.76447
4634.1719 | 122.8043 | -0.737 | 122.1725 | -0.091095 | 0.0010489 | 0.021864 | 0.0088033 | 0.0046464 | 0.0017645 | 0.0032856 | -0.071533 | 0.0032385 | 0.00064083 | 0.0058276 | -0.0034287 | -0.0053663 | 0.00045294 | -0.49439 | -0.19226 | -0.79193 | -0.51727 | -0.48065 | -0.67291 | -0.46692 | -0.07782 | 122.2824 | -0.82398 | -0.32501 | -0.37994 | -0.66376 | -0.54932 | -0.054931 | -122.3648 | -122.6898 | 0.25635 | 0.27008 | 0.064087 | 0.32501 | 0.11902 | -0.086975 | 0.10986 | -122.4976 | 0.35706 | 0.18768 | 0.073243 | 0.27466 | 0.16022 | 0.31128 | 0.27466 | 0.44403 | 0.49896 | 0.59967 | 123.1064 | 0.54474 | 123.0194 | -122.9645 | -122.9965 | 0.21973 | 0.41199 | 0.24261 | 0.65918
4635.1719 | 122.9416 | -0.6958 | 122.1497 | -0.03006 | -1.9142e-05 | 0.019514 | 0.0075217 | -0.00090783 | 0.00026909 | 0.00050839 | 0.056641 | 0.00067495 | 0.0014954 | -0.00229 | -0.00043791 | -0.0087843 | 0.00066654 | -0.41657 | -0.21057 | -0.75989 | -0.37079 | -0.24719 | -0.49439 | -0.29755 | 0.10986 | 122.2137 | -0.78278 | -0.23804 | -0.21515 | -0.48981 | -0.44861 | -0.064087 | -122.3602 | -122.5204 | 0.44861 | 0.39826 | 0.20142 | 0.46234 | 0.2655 | -0.086975 | 0.064087 | -122.3877 | 0.48065 | 0.24719 | 0.20599 | 0.33417 | 0.29297 | 0.5127 | 0.3891 | 0.56763 | 0.54474 | 0.54932 | 122.9965 | 0.48523 | 122.9095 | -122.9095 | -122.9324 | 0.32501 | 0.45776 | 0.27924 | 0.80566
4636.1719 | 122.8455 | -0.75073 | 122.1542 | -0.075836 | -0.0015145 | 0.020796 | 0.010085 | 0.00058737 | -0.00058531 | 0.0022174 | 0.023071 | 0.00067495 | -0.00021357 | 0.0013416 | -0.0019333 | -0.0070753 | 0.00023934 | -0.42572 | -0.20599 | -0.76904 | -0.43945 | -0.32959 | -0.54474 | -0.35248 | 0.009155 | 122.2458 | -0.82855 | -0.3479 | -0.32501 | -0.62256 | -0.55389 | -0.018311 | -122.3602 | -122.5937 | 0.42114 | 0.39825 | 0.20599 | 0.41657 | 0.2243 | -0.07782 | 0.091553 | -122.5021 | 0.42572 | 0.19684 | 0.12817 | 0.27466 | 0.20599 | 0.43945 | 0.32959 | 0.50354 | 0.48065 | 0.56305 | 123.0743 | 0.54474 | 122.9965 | -122.9233 | -122.9828 | 0.31128 | 0.40283 | 0.32501 | 0.75989
4637.1719 | 122.9324 | -0.71869 | 122.113 | -0.022431 | 0.0025443 | 0.019514 | 0.0079489 | 0.00251 | 0.0019781 | 0.0017902 | 0.047485 | 0.0025975 | -0.00021357 | 0.0026232 | -0.0027877 | -0.0066479 | -0.00040166 | -0.42572 | -0.21973 | -0.76904 | -0.39368 | -0.27466 | -0.49896 | -0.31128 | 0.086975 | 122.2046 | -0.8194 | -0.27008 | -0.23804 | -0.53558 | -0.48065 | -0.050354 | -122.3328 | -122.5067 | 0.44403 | 0.40741 | 0.21973 | 0.45776 | 0.27008 | -0.10071 | 0.091553 | -122.3831 | 0.48065 | 0.23804 | 0.18311 | 0.33875 | 0.28381 | 0.49439 | 0.37537 | 0.58136 | 0.54932 | 0.54932 | 123.024 | 0.49896 | 122.9233 | -122.8821 | -122.9324 | 0.32501 | 0.44861 | 0.29297 | 0.80566
4638.1719 | 122.8775 | -0.78735 | 122.1039 | -0.052948 | -0.0030099 | 0.019301 | 0.0088033 | 0.00058737 | -0.0022943 | -0.0012006 | 0.047485 | 0.0028113 | -0.0021362 | -0.00079478 | -0.0034287 | -0.0075025 | 0.0036571 | -0.43945 | -0.22888 | -0.82855 | -0.41199 | -0.32044 | -0.53101 | -0.34332 | 0.018311 | 122.1542 | -0.85144 | -0.33417 | -0.31128 | -0.6134 | -0.55389 | -0.041198 | -122.3328 | -122.5159 | 0.46692 | 0.44403 | 0.25635 | 0.48523 | 0.29755 | -0.064086 | 0.050354 | -122.438 | 0.47608 | 0.23346 | 0.17395 | 0.29755 | 0.23804 | 0.50812 | 0.41656 | 0.54016 | 0.51727 | 0.59967 | 123.0057 | 0.55847 | 122.9416 | -122.9324 | -122.9553 | 0.37537 | 0.45319 | 0.3479 | 0.80566
4639.1719 | 122.8317 | -0.79651 | 122.1405 | 0.00045798 | -0.0013009 | 0.019514 | 0.0085897 | 0.0020828 | -0.00037171 | 0.00029479 | -0.0013428 | 0.0023839 | 0.001068 | -0.001222 | -0.0027877 | -0.0085705 | 0.0013073 | -0.47607 | -0.20599 | -0.80566 | -0.49896 | -0.3891 | -0.59052 | -0.41199 | -0.036621 | 122.2321 | -0.85144 | -0.37537 | -0.37079 | -0.66834 | -0.59967 | -0.009155 | -122.3465 | -122.6395 | 0.40741 | 0.38452 | 0.20599 | 0.39368 | 0.21515 | -0.054931 | 0.091553 | -122.5159 | 0.42572 | 0.19684 | 0.12817 | 0.25177 | 0.1831 | 0.41657 | 0.3067 | 0.48065 | 0.47607 | 0.59967 | 123.0835 | 0.59052 | 123.0286 | -122.9462 | -122.9919 | 0.29755 | 0.42114 | 0.32044 | 0.75989
4640.1719 | 122.9645 | -0.73242 | 122.0993 | -0.15976 | -0.0019417 | 0.019728 | 0.0079489 | -5.343e-05 | -0.00058531 | 0.0017902 | 0.013916 | 0.0015295 | -0.001709 | -0.0018628 | -0.0027877 | -0.0075025 | -0.0016833 | -0.46692 | -0.20142 | -0.79193 | -0.42114 | -0.32501 | -0.54932 | -0.33417 | 0.073242 | 122.1954 | -0.83313 | -0.24261 | -0.24261 | -0.54016 | -0.46692 | -0.059509 | -122.3007 | -122.5204 | 0.40741 | 0.39826 | 0.18311 | 0.45776 | 0.24262 | -0.10071 | 0.096131 | -122.3419 | 0.48981 | 0.2655 | 0.19226 | 0.36621 | 0.29297 | 0.46692 | 0.37079 | 0.59052 | 0.59052 | 0.59052 | 123.0286 | 0.53101 | 122.9279 | -122.8912 | -122.9324 | 0.31128 | 0.48981 | 0.2655 | 0.80566
4641.1719 | 122.9691 | -0.72327 | 122.0947 | -0.11398 | -0.0015145 | 0.019728 | 0.0081625 | 0.0012284 | 0.0019781 | 0.00029479 | 0.013916 | 0.0021703 | 0.001068 | -0.003999 | -0.0034287 | -0.0085705 | -0.0012561 | -0.44403 | -0.23346 | -0.80109 | -0.3891 | -0.27008 | -0.49896 | -0.3067 | 0.1236 | 122.1771 | -0.82398 | -0.24261 | -0.21973 | -0.51727 | -0.45776 | -0.077819 | -122.3282 | -122.4838 | 0.45319 | 0.41657 | 0.2243 | 0.49438 | 0.30212 | -0.10071 | 0.082397 | -122.3373 | 0.50354 | 0.2655 | 0.20599 | 0.36621 | 0.3067 | 0.531 | 0.41199 | 0.60425 | 0.58136 | 0.56763 | 123.0011 | 0.48981 | 122.9004 | -122.8958 | -122.9187 | 0.33417 | 0.48065 | 0.27924 | 0.84686
4642.1719 | 122.8958 | -0.737 | 122.1497 | -0.11398 | 0.00019446 | 0.019728 | 0.0062399 | -0.00048063 | 0.0021917 | 0.0011494 | 0.013916 | -0.00039305 | 2.8e-08 | 0.00070062 | -0.0032151 | -0.0070753 | -0.0042469 | -0.42572 | -0.21057 | -0.78278 | -0.42114 | -0.31586 | -0.51727 | -0.33417 | 0.09613 | 122.2229 | -0.8194 | -0.29297 | -0.26093 | -0.5722 | -0.50354 | -0.045776 | -122.3602 | -122.5708 | 0.42114 | 0.40283 | 0.21973 | 0.44861 | 0.2655 | -0.082397 | 0.073242 | -122.4426 | 0.47607 | 0.23346 | 0.1648 | 0.31586 | 0.24719 | 0.46692 | 0.36163 | 0.55847 | 0.52643 | 0.57221 | 123.0423 | 0.52643 | 122.9599 | -122.9324 | -122.9691 | 0.31586 | 0.44403 | 0.31128 | 0.83313
4643.1719 | 122.8363 | -0.75531 | 122.1497 | -0.075836 | 0.00040806 | 0.019728 | 0.0098715 | 0.001442 | -0.0012261 | 0.00072199 | -0.0043946 | 0.0021703 | 0.00064083 | 0.0030506 | -0.0044967 | -0.0075025 | -0.0018971 | -0.44861 | -0.21057 | -0.78735 | -0.43945 | -0.35248 | -0.54474 | -0.38452 | 0.045776 | 122.2412 | -0.82855 | -0.33417 | -0.31586 | -0.62256 | -0.55389 | -0.032044 | -122.3602 | -122.5891 | 0.40283 | 0.37079 | 0.21057 | 0.40283 | 0.24262 | -0.073242 | 0.091553 | -122.4838 | 0.43945 | 0.20142 | 0.13275 | 0.27466 | 0.20599 | 0.43488 | 0.3479 | 0.51269 | 0.49438 | 0.57678 | 123.0698 | 0.54474 | 122.9965 | -122.937 | -122.9782 | 0.31586 | 0.42114 | 0.3067 | 0.80109
4644.1719 | 122.8775 | -0.75073 | 122.1542 | -0.068207 | -0.00066014 | 0.019942 | 0.010512 | 0.00486 | -0.0012261 | 0.00414 | -0.050171 | 0.0028113 | -0.00064077 | 0.001128 | -0.0042831 | -0.0051527 | -0.0010425 | -0.48065 | -0.17395 | -0.79651 | -0.49439 | -0.42572 | -0.60425 | -0.41199 | 0.041199 | 122.2733 | -0.83771 | -0.29755 | -0.28839 | -0.62714 | -0.53558 | -0.045777 | -122.3282 | -122.6486 | 0.32501 | 0.33874 | 0.14648 | 0.38452 | 0.19226 | -0.086976 | 0.11902 | -122.4518 | 0.46234 | 0.21515 | 0.1236 | 0.30212 | 0.21057 | 0.37079 | 0.30212 | 0.54932 | 0.54016 | 0.62256 | 123.111 | 0.57678 | 123.024 | -122.9507 | -122.9919 | 0.25635 | 0.45319 | 0.27008 | 0.79193
4645.1719 | 122.9782 | -0.70953 | 122.1313 | -0.098725 | -0.0015145 | 0.020583 | 0.0081625 | -0.00026703 | -0.00079891 | -0.00077341 | 0.059692 | 0.0023839 | 2.8e-08 | -0.0067762 | -0.00022431 | -0.0068615 | -0.0023243 | -0.46234 | -0.20142 | -0.77362 | -0.3891 | -0.30212 | -0.52643 | -0.3067 | 0.14648 | 122.2321 | -0.81482 | -0.20142 | -0.20142 | -0.50812 | -0.45776 | -0.064087 | -122.3328 | -122.5204 | 0.40741 | 0.40283 | 0.18311 | 0.46692 | 0.24719 | -0.10528 | 0.10071 | -122.3328 | 0.50812 | 0.25177 | 0.20142 | 0.35705 | 0.3067 | 0.4715 | 0.38452 | 0.6134 | 0.6134 | 0.5722 | 123.0469 | 0.50812 | 122.9416 | -122.905 | -122.9462 | 0.32044 | 0.50812 | 0.24719 | 0.85602
4646.1719 | 122.9874 | -0.72327 | 122.1039 | -0.060578 | -0.00044654 | 0.019087 | 0.0077353 | -0.00048063 | -0.00079891 | -0.00034601 | 0.041382 | 0.0032385 | 0.00064083 | 0.00070062 | -0.0027877 | -0.0060071 | -0.0016833 | -0.43488 | -0.21057 | -0.78278 | -0.36621 | -0.27466 | -0.48981 | -0.29755 | 0.19226 | 122.2 | -0.79651 | -0.21515 | -0.19226 | -0.52185 | -0.47607 | -0.059509 | -122.3145 | -122.4701 | 0.44861 | 0.42572 | 0.23346 | 0.48523 | 0.29297 | -0.073242 | 0.09613 | -122.319 | 0.53101 | 0.24719 | 0.20142 | 0.32044 | 0.27466 | 0.50812 | 0.41657 | 0.60425 | 0.58136 | 0.57221 | 122.9965 | 0.5127 | 122.9233 | -122.8867 | -122.9004 | 0.35706 | 0.50812 | 0.28839 | 0.91553
4647.1719 | 122.9187 | -0.71869 | 122.168 | -0.12924 | -0.0021555 | 0.020583 | 0.0081625 | -0.00069423 | -0.00079891 | -0.00013241 | 0.026123 | 0.0025975 | 0.0014954 | -0.0020764 | -0.0042831 | -0.0066479 | -0.0036059 | -0.45776 | -0.20599 | -0.7782 | -0.44403 | -0.37079 | -0.55847 | -0.34332 | 0.10071 | 122.2092 | -0.81024 | -0.24719 | -0.23804 | -0.57678 | -0.48981 | -0.059509 | -122.374 | -122.612 | 0.3479 | 0.37537 | 0.16022 | 0.43487 | 0.21973 | -0.091553 | 0.041198 | -122.4152 | 0.48065 | 0.22888 | 0.14191 | 0.32044 | 0.23346 | 0.40741 | 0.33417 | 0.57221 | 0.56305 | 0.5722 | 123.0194 | 0.5127 | 122.9279 | -122.9462 | -122.9782 | 0.27466 | 0.4715 | 0.26093 | 0.8194
4648.1719 | 122.9187 | -0.72327 | 122.1313 | -0.12161 | -0.0015145 | 0.018233 | 0.0090169 | 0.003151 | 0.00069649 | 0.0026446 | 0.026123 | 0.0013159 | 0.002777 | -0.001222 | -0.0027877 | -0.0072889 | -0.0029651 | -0.45319 | -0.18768 | -0.78278 | -0.4303 | -0.36163 | -0.54016 | -0.34332 | 0.12817 | 122.2733 | -0.81024 | -0.23346 | -0.20142 | -0.54932 | -0.48065 | -0.059509 | -122.319 | -122.5616 | 0.36163 | 0.37994 | 0.18311 | 0.43945 | 0.24262 | -0.086975 | 0.14191 | -122.3648 | 0.52185 | 0.24261 | 0.17395 | 0.32959 | 0.26093 | 0.42114 | 0.35248 | 0.60883 | 0.57678 | 0.59509 | 123.0835 | 0.53558 | 122.9965 | -122.9141 | -122.9416 | 0.29297 | 0.48981 | 0.27008 | 0.85144
4649.1719 | 122.8638 | -0.737 | 122.1542 | -0.060578 | -0.00066014 | 0.018874 | 0.0073081 | -5.343e-05 | 0.0013373 | 0.00093559 | 0.016968 | 0.0011023 | 0.00064083 | -0.0037854 | -0.0055649 | -0.0079297 | -0.0023243 | -0.42114 | -0.19684 | -0.76446 | -0.40741 | -0.32959 | -0.49439 | -0.32044 | 0.14191 | 122.2641 | -0.81024 | -0.28381 | -0.24719 | -0.58136 | -0.51727 | -0.027465 | -122.3511 | -122.5616 | 0.40741 | 0.41656 | 0.24261 | 0.44403 | 0.27008 | -0.073242 | 0.10986 | -122.438 | 0.48981 | 0.21973 | 0.15564 | 0.29297 | 0.22888 | 0.43487 | 0.35705 | 0.56305 | 0.52643 | 0.56763 | 123.0743 | 0.54016 | 123.0011 | -122.9187 | -122.9645 | 0.32959 | 0.45319 | 0.31586 | 0.87891
4650.1719 | 122.9599 | -0.66834 | 122.1451 | -0.098725 | -0.00023294 | 0.020796 | 0.0073081 | 0.00080117 | 0.00069649 | 0.001363 | 0.016968 | 0.0028113 | 2.8e-08 | -0.00036738 | -0.00043791 | -0.0094251 | -0.0021107 | -0.42572 | -0.17853 | -0.72327 | -0.37994 | -0.29297 | -0.46234 | -0.27008 | 0.2243 | 122.2595 | -0.77362 | -0.17853 | -0.15106 | -0.48523 | -0.42114 | -0.054932 | -122.3236 | -122.525 | 0.37537 | 0.39825 | 0.20599 | 0.45319 | 0.26093 | -0.10529 | 0.11444 | -122.3236 | 0.51727 | 0.24719 | 0.18311 | 0.35248 | 0.28839 | 0.4303 | 0.34332 | 0.62256 | 0.59509 | 0.54474 | 123.0331 | 0.48981 | 122.9279 | -122.8683 | -122.9187 | 0.28839 | 0.48981 | 0.24262 | 0.89264
4651.1719 | 122.9599 | -0.67291 | 122.1817 | -0.075836 | -1.9142e-05 | 0.019301 | 0.0073081 | 0.001442 | 0.00026909 | -0.00055961 | 0.001709 | 0.00067495 | -0.0010682 | -0.0016492 | -0.0027877 | -0.0075025 | -0.00040166 | -0.3891 | -0.17395 | -0.70038 | -0.33875 | -0.23346 | -0.43488 | -0.25635 | 0.28839 | 122.2733 | -0.7782 | -0.17853 | -0.13275 | -0.46692 | -0.43488 | -0.027465 | -122.3557 | -122.5204 | 0.43945 | 0.41656 | 0.23804 | 0.44403 | 0.2655 | -0.10528 | 0.091552 | -122.3602 | 0.54016 | 0.23804 | 0.20599 | 0.34332 | 0.31128 | 0.46692 | 0.36163 | 0.64545 | 0.59967 | 0.52643 | 123.0515 | 0.49896 | 122.9462 | -122.8821 | -122.9599 | 0.33417 | 0.49438 | 0.28381 | 0.9613
4652.1719 | 122.9141 | -0.67749 | 122.2 | -0.068207 | -0.00066014 | 0.019942 | 0.0098715 | 0.001442 | -0.00079891 | 0.00029479 | -0.0074462 | 0.0036657 | -0.00021357 | 0.009032 | -0.0038559 | -0.0081433 | 0.00045294 | -0.43945 | -0.17853 | -0.737 | -0.39825 | -0.3479 | -0.52643 | -0.33417 | 0.17853 | 122.2733 | -0.7782 | -0.2243 | -0.17395 | -0.53558 | -0.45776 | -0.05951 | -122.3785 | -122.5983 | 0.32959 | 0.34332 | 0.15106 | 0.40283 | 0.21057 | -0.10071 | 0.073242 | -122.4243 | 0.50354 | 0.21973 | 0.14191 | 0.32043 | 0.24261 | 0.3891 | 0.33875 | 0.60425 | 0.55389 | 0.55847 | 123.0515 | 0.49896 | 122.9507 | -122.937 | -122.9782 | 0.27924 | 0.45319 | 0.23804 | 0.85602
4653.1719 | 122.8226 | -0.72327 | 122.2229 | -0.052948 | -0.0019417 | 0.018874 | 0.0068807 | 0.0020828 | -0.0014399 | -0.002055 | -0.03186 | 0.0032385 | -0.00021357 | 0.008391 | -0.0036423 | -0.0038709 | -0.0018971 | -0.46692 | -0.14191 | -0.76446 | -0.46234 | -0.40741 | -0.56305 | -0.37079 | 0.10529 | 122.319 | -0.79651 | -0.27466 | -0.25177 | -0.59967 | -0.52185 | -0.041198 | -122.3648 | -122.6852 | 0.31586 | 0.35248 | 0.16022 | 0.39368 | 0.20142 | -0.073242 | 0.096131 | -122.4976 | 0.4715 | 0.20142 | 0.1236 | 0.27466 | 0.19684 | 0.35705 | 0.30212 | 0.54474 | 0.52185 | 0.62256 | 123.1155 | 0.58136 | 123.0423 | -122.9874 | -123.0194 | 0.26093 | 0.44861 | 0.25635 | 0.82855
4654.1719 | 122.8729 | -0.68207 | 122.2137 | -0.075836 | -0.00087374 | 0.021437 | 0.010512 | 0.0010148 | -0.0022943 | 0.0011494 | -0.059326 | 0.0053747 | 0.001068 | 0.0054004 | -0.0012925 | -0.0070753 | -0.00082886 | -0.43945 | -0.14191 | -0.76904 | -0.43488 | -0.37079 | -0.52185 | -0.37537 | 0.1831 | 122.3282 | -0.79193 | -0.2243 | -0.20599 | -0.59052 | -0.4715 | -0.086975 | -122.3557 | -122.6486 | 0.31128 | 0.3067 | 0.16022 | 0.39368 | 0.24719 | -0.10986 | 0.11444 | -122.438 | 0.47607 | 0.21057 | 0.091553 | 0.32043 | 0.20142 | 0.39825 | 0.33417 | 0.58594 | 0.56763 | 0.62714 | 123.1201 | 0.54016 | 123.0103 | -122.9828 | -123.0057 | 0.24719 | 0.45776 | 0.24262 | 0.86517
4655.1719 | 122.9462 | -0.65002 | 122.1863 | -0.091095 | 0.00019446 | 0.020369 | 0.0081625 | -0.00048063 | 0.00026909 | -0.0016278 | -0.016602 | 0.0013159 | 0.00085443 | -0.00058098 | -0.0021469 | -0.0072889 | -0.0031787 | -0.37994 | -0.1831 | -0.71869 | -0.3479 | -0.2655 | -0.48065 | -0.3067 | 0.27008 | 122.2733 | -0.737 | -0.15564 | -0.13733 | -0.50812 | -0.40283 | -0.068665 | -122.3694 | -122.5342 | 0.38452 | 0.34332 | 0.16937 | 0.41199 | 0.23804 | -0.086976 | 0.086975 | -122.3419 | 0.5127 | 0.24719 | 0.14191 | 0.33417 | 0.22888 | 0.45319 | 0.37079 | 0.59967 | 0.58136 | 0.53558 | 123.0103 | 0.46692 | 122.9233 | -122.905 | -122.9233 | 0.30212 | 0.49438 | 0.27008 | 0.92011
4656.1719 | 122.9141 | -0.66376 | 122.1634 | -0.11398 | 0.00062166 | 0.021437 | 0.0075217 | -0.0017624 | 5.5488e-05 | 0.0032856 | 0.013916 | 0.0017431 | 0.0014954 | -0.001222 | -0.0025741 | -0.0068615 | 0.00023934 | -0.43945 | -0.1831 | -0.69122 | -0.39368 | -0.31128 | -0.48981 | -0.31586 | 0.21973 | 122.2824 | -0.77362 | -0.21057 | -0.16479 | -0.54474 | -0.43488 | -0.027466 | -122.3465 | -122.5571 | 0.35248 | 0.3479 | 0.17395 | 0.37537 | 0.20142 | -0.10986 | 0.11902 | -122.374 | 0.49896 | 0.22888 | 0.11902 | 0.33875 | 0.22888 | 0.37994 | 0.29755 | 0.60883 | 0.56305 | 0.50812 | 123.056 | 0.48065 | 122.9462 | -122.8546 | -122.937 | 0.27008 | 0.45319 | 0.2243 | 0.88348
4657.1719 | 122.9004 | -0.66834 | 122.2 | -0.12161 | -0.00023294 | 0.020796 | 0.01094 | 0.00058737 | -0.0018671 | 0.0034992 | -0.0013428 | 0.0017431 | -0.0012818 | 0.00091422 | -0.0027877 | -0.0060071 | -0.0016833 | -0.42114 | -0.17853 | -0.72784 | -0.37994 | -0.3067 | -0.5127 | -0.32044 | 0.25177 | 122.2549 | -0.75989 | -0.18768 | -0.15106 | -0.50354 | -0.42114 | -0.059509 | -122.3785 | -122.58 | 0.36163 | 0.3479 | 0.15564 | 0.40741 | 0.21515 | -0.091553 | 0.054932 | -122.3877 | 0.51727 | 0.24719 | 0.1648 | 0.33875 | 0.25635 | 0.42114 | 0.3479 | 0.60883 | 0.57221 | 0.54932 | 123.0148 | 0.48981 | 122.9233 | -122.9279 | -122.9599 | 0.28839 | 0.48065 | 0.24719 | 0.9201
4658.1719 | 122.9233 | -0.64545 | 122.1954 | -0.060578 | -0.0015145 | 0.020583 | 0.0085897 | -0.0045394 | 5.5488e-05 | 0.00093559 | 0.02002 | 0.0023839 | -0.0019226 | -0.003999 | -0.0038559 | -0.0083569 | -0.0010425 | -0.42114 | -0.16479 | -0.71869 | -0.39825 | -0.31586 | -0.47607 | -0.31128 | 0.25635 | 122.2916 | -0.75531 | -0.17853 | -0.10986 | -0.48523 | -0.42572 | -0.073242 | -122.3602 | -122.5937 | 0.32959 | 0.33417 | 0.16937 | 0.40741 | 0.24262 | -0.10986 | 0.09613 | -122.374 | 0.53558 | 0.21973 | 0.16022 | 0.32959 | 0.27008 | 0.40283 | 0.32044 | 0.64545 | 0.57678 | 0.55389 | 123.0469 | 0.48065 | 122.937 | -122.9141 | -122.9507 | 0.24719 | 0.46692 | 0.2243 | 0.9018
4659.1719 | 122.8638 | -0.70038 | 122.1817 | -0.052948 | -0.0010873 | 0.01866 | 0.0075217 | -0.00048063 | 0.00069649 | -0.00013241 | -0.0013428 | 0.0030249 | 0.001068 | 0.00027342 | -0.0034287 | -0.0062207 | 0.0013073 | -0.40283 | -0.16479 | -0.737 | -0.37537 | -0.32044 | -0.48065 | -0.31128 | 0.23804 | 122.2778 | -0.79193 | -0.24719 | -0.19226 | -0.57678 | -0.49896 | -0.036622 | -122.3465 | -122.5571 | 0.37994 | 0.3891 | 0.21973 | 0.42572 | 0.25635 | -0.091553 | 0.09613 | -122.4289 | 0.50812 | 0.20142 | 0.1236 | 0.29297 | 0.21515 | 0.41656 | 0.36163 | 0.59967 | 0.54474 | 0.5722 | 123.0698 | 0.53558 | 122.9782 | -122.9187 | -122.9736 | 0.32501 | 0.45319 | 0.29755 | 0.93841
4660.1719 | 122.9095 | -0.66834 | 122.1817 | -0.15213 | -0.00044654 | 0.019514 | 0.0068807 | 0.001442 | -0.0010125 | 0.0022174 | -0.01355 | 0.00046135 | 0.0012818 | -0.0035718 | -0.0025741 | -0.0075025 | 0.00023934 | -0.40283 | -0.16479 | -0.70496 | -0.37079 | -0.28381 | -0.50354 | -0.3067 | 0.27008 | 122.3053 | -0.76446 | -0.19684 | -0.14648 | -0.53101 | -0.45319 | -0.036621 | -122.3465 | -122.5525 | 0.38452 | 0.36163 | 0.1648 | 0.39825 | 0.20142 | -0.09613 | 0.1236 | -122.3785 | 0.52185 | 0.21515 | 0.13733 | 0.31128 | 0.23346 | 0.42114 | 0.33417 | 0.61798 | 0.56763 | 0.54016 | 123.0698 | 0.50354 | 122.9736 | -122.8867 | -122.9462 | 0.29755 | 0.4715 | 0.2655 | 0.93842
4661.1719 | 122.9553 | -0.66834 | 122.1909 | -0.12161 | 0.0019035 | 0.020796 | 0.0081625 | -0.00026703 | 0.00069649 | 0.00093559 | -0.034912 | 0.0011023 | -0.0014954 | -0.00058098 | -0.0036423 | -0.0077161 | -0.0021107 | -0.37079 | -0.16022 | -0.71411 | -0.32501 | -0.26093 | -0.46692 | -0.28839 | 0.33417 | 122.2961 | -0.737 | -0.15106 | -0.10986 | -0.49439 | -0.40283 | -0.045776 | -122.3511 | -122.5159 | 0.40741 | 0.37994 | 0.20142 | 0.42572 | 0.24719 | -0.068665 | 0.10529 | -122.3419 | 0.55847 | 0.2655 | 0.17395 | 0.33417 | 0.24261 | 0.45319 | 0.3891 | 0.62714 | 0.58594 | 0.55389 | 123.0331 | 0.50812 | 122.9645 | -122.905 | -122.9279 | 0.34332 | 0.51727 | 0.29755 | 1.0025
4662.1719 | 122.9691 | -0.65918 | 122.1954 | -0.098725 | 0.0010489 | 0.020369 | 0.0098715 | -0.00048063 | 0.00048269 | 0.00414 | -0.047119 | 0.0021703 | 0.00021363 | 0.0019824 | -0.0030013 | -0.0070753 | -0.0029651 | -0.37079 | -0.16937 | -0.71869 | -0.35706 | -0.27008 | -0.48065 | -0.28839 | 0.3479 | 122.2916 | -0.74158 | -0.1236 | -0.10071 | -0.49439 | -0.39368 | -0.059509 | -122.3648 | -122.5525 | 0.3891 | 0.37079 | 0.17853 | 0.4303 | 0.23804 | -0.082397 | 0.09613 | -122.319 | 0.55847 | 0.2655 | 0.16479 | 0.3479 | 0.24719 | 0.44861 | 0.36163 | 0.64087 | 0.61798 | 0.54932 | 123.0331 | 0.48981 | 122.9507 | -122.9141 | -122.937 | 0.30212 | 0.53558 | 0.28839 | 1.0071
4663.1719 | 122.905 | -0.67291 | 122.2092 | -0.15213 | 0.0012625 | 0.018233 | 0.0094443 | -0.0034714 | 0.0019781 | 0.0020038 | -0.016602 | 0.0017431 | 0.001068 | -0.0014356 | -0.0027877 | -0.0079297 | -0.00061526 | -0.40283 | -0.15564 | -0.71411 | -0.36163 | -0.27466 | -0.49439 | -0.29755 | 0.3067 | 122.2595 | -0.74616 | -0.16022 | -0.14648 | -0.51727 | -0.43488 | -0.041198 | -122.3648 | -122.5708 | 0.39825 | 0.37537 | 0.17853 | 0.41657 | 0.21973 | -0.073242 | 0.050354 | -122.3694 | 0.52643 | 0.23804 | 0.15564 | 0.31128 | 0.22888 | 0.43945 | 0.35248 | 0.59967 | 0.58594 | 0.55847 | 123.0057 | 0.51727 | 122.9324 | -122.9233 | -122.9553 | 0.31128 | 0.5127 | 0.27008 | 0.97961
4664.1719 | 122.9187 | -0.66376 | 122.2 | -0.12924 | -0.00087374 | 0.019514 | 0.0088033 | -0.0015488 | 0.00091009 | -0.0012006 | -0.016602 | 0.00088875 | -0.00085457 | -0.00015378 | -0.0047103 | -0.0085705 | 0.0015209 | -0.37994 | -0.16937 | -0.70496 | -0.32959 | -0.26093 | -0.45776 | -0.28381 | 0.35706 | 122.3053 | -0.75073 | -0.16022 | -0.1236 | -0.5127 | -0.42572 | -0.041199 | -122.3694 | -122.5296 | 0.40283 | 0.37994 | 0.20599 | 0.42114 | 0.24719 | -0.086975 | 0.10529 | -122.3602 | 0.54016 | 0.23804 | 0.15106 | 0.32501 | 0.23804 | 0.44403 | 0.37537 | 0.62714 | 0.59051 | 0.53558 | 123.056 | 0.49438 | 122.9691 | -122.905 | -122.9507 | 0.33417 | 0.50354 | 0.28381 | 1.0208
4665.1719 | 122.9004 | -0.66376 | 122.2183 | -0.11398 | -0.00044654 | 0.021223 | 0.0085897 | -0.00026703 | -0.0012261 | 0.0017902 | 0.001709 | 3.4148e-05 | 0.00064083 | -0.002931 | -0.0034287 | -0.0083569 | -0.0012561 | -0.37994 | -0.16937 | -0.70496 | -0.34332 | -0.27924 | -0.4303 | -0.28381 | 0.32044 | 122.319 | -0.75989 | -0.19226 | -0.1236 | -0.52185 | -0.45319 | -0.041199 | -122.3877 | -122.5616 | 0.38452 | 0.37994 | 0.23346 | 0.42114 | 0.27466 | -0.096131 | 0.10071 | -122.4106 | 0.54016 | 0.21057 | 0.14191 | 0.3067 | 0.23804 | 0.42572 | 0.36163 | 0.63629 | 0.56763 | 0.53558 | 123.0789 | 0.49438 | 122.9828 | -122.9233 | -122.9782 | 0.32043 | 0.4715 | 0.28381 | 0.98419
4666.1719 | 122.9507 | -0.64545 | 122.2092 | -0.11398 | 0.00083526 | 0.02101 | 0.0088033 | 0.00486 | -0.0018671 | -0.0014142 | -0.071533 | 0.0038793 | 2.8e-08 | -0.0010084 | -0.0051377 | -0.0077161 | -0.0038197 | -0.38452 | -0.12817 | -0.72327 | -0.33875 | -0.28381 | -0.46692 | -0.27008 | 0.36621 | 122.3099 | -0.75073 | -0.12817 | -0.09613 | -0.48523 | -0.37537 | -0.07782 | -122.3373 | -122.5479 | 0.36163 | 0.37537 | 0.17853 | 0.45319 | 0.25635 | -0.10528 | 0.10071 | -122.3373 | 0.54932 | 0.27008 | 0.16022 | 0.37537 | 0.2655 | 0.43945 | 0.38452 | 0.6546 | 0.62256 | 0.59509 | 123.0606 | 0.51727 | 122.9553 | -122.9324 | -122.9599 | 0.3067 | 0.51727 | 0.26093 | 1.0117
4667.1719 | 122.9233 | -0.64087 | 122.1909 | -0.1445 | -0.0015145 | 0.020583 | 0.011153 | 0.0016556 | 0.0013373 | 0.0017902 | 0.001709 | 0.0019567 | 0.00064083 | -0.0020764 | -0.0021469 | -0.0072889 | -0.00082886 | -0.37537 | -0.16479 | -0.68207 | -0.32501 | -0.25635 | -0.45319 | -0.27008 | 0.39825 | 122.2916 | -0.75073 | -0.1236 | -0.09613 | -0.48523 | -0.3891 | -0.041199 | -122.3557 | -122.5159 | 0.38452 | 0.37079 | 0.18768 | 0.41199 | 0.22888 | -0.10986 | 0.10071 | -122.3145 | 0.54474 | 0.25177 | 0.15564 | 0.36163 | 0.2655 | 0.42572 | 0.35706 | 0.6546 | 0.62714 | 0.51727 | 123.0423 | 0.47607 | 122.9324 | -122.8729 | -122.9416 | 0.31586 | 0.51727 | 0.2655 | 1.0391
4668.1719 | 122.8455 | -0.70038 | 122.2366 | -0.091095 | -0.00044654 | 0.020155 | 0.010085 | -0.00069423 | -0.00058531 | 0.001363 | -0.089844 | 0.0032385 | 0.00085443 | 0.0019824 | -0.0019333 | -0.0049389 | 0.0017345 | -0.4303 | -0.13275 | -0.74616 | -0.44403 | -0.39825 | -0.58136 | -0.37079 | 0.23804 | 122.319 | -0.78735 | -0.23804 | -0.20599 | -0.6134 | -0.48523 | -0.045777 | -122.3694 | -122.6807 | 0.30212 | 0.32959 | 0.11902 | 0.37537 | 0.1648 | -0.086976 | 0.082398 | -122.4747 | 0.49438 | 0.21515 | 0.086975 | 0.30212 | 0.17395 | 0.3479 | 0.30212 | 0.58136 | 0.54932 | 0.6134 | 123.1064 | 0.56763 | 123.0194 | -122.9828 | -123.024 | 0.25635 | 0.46234 | 0.27008 | 0.93841
4669.1719 | 122.937 | -0.6546 | 122.1725 | -0.11398 | -0.00044654 | 0.020796 | 0.01094 | 0.00058737 | 0.00091009 | 0.0026446 | -0.019653 | 0.0036657 | 2.8e-08 | 0.0047594 | -0.0032151 | -0.0066479 | 0.00023934 | -0.37079 | -0.1236 | -0.73242 | -0.33417 | -0.2655 | -0.46234 | -0.27924 | 0.38452 | 122.2641 | -0.75073 | -0.13275 | -0.082397 | -0.52643 | -0.38452 | -0.07782 | -122.2961 | -122.5067 | 0.3891 | 0.37537 | 0.19226 | 0.45319 | 0.27008 | -0.09613 | 0.091553 | -122.3053 | 0.57221 | 0.27008 | 0.12817 | 0.36621 | 0.2243 | 0.46692 | 0.39826 | 0.66833 | 0.61798 | 0.60883 | 123.0148 | 0.53101 | 122.9187 | -122.905 | -122.9233 | 0.32044 | 0.52185 | 0.28381 | 1.0391
4670.1719 | 122.9507 | -0.68207 | 122.1771 | -0.068207 | 0.00083526 | 0.019087 | 0.0047445 | -0.0030442 | 0.0015509 | -0.0018414 | 0.016968 | 0.00024775 | -0.0010682 | -0.0044262 | -0.0032151 | -0.0089979 | 0.00066654 | -0.34332 | -0.13733 | -0.737 | -0.32501 | -0.21973 | -0.39825 | -0.24261 | 0.39368 | 122.287 | -0.76446 | -0.16022 | -0.073242 | -0.49439 | -0.41199 | -0.054932 | -122.3145 | -122.5021 | 0.46234 | 0.43945 | 0.28381 | 0.49438 | 0.33875 | -0.082397 | 0.10986 | -122.3373 | 0.60883 | 0.27008 | 0.18768 | 0.35248 | 0.27008 | 0.51727 | 0.41199 | 0.69122 | 0.60425 | 0.59967 | 123.0515 | 0.54474 | 122.9691 | -122.9141 | -122.9416 | 0.35706 | 0.52185 | 0.33875 | 1.0757
4671.1719 | 122.9507 | -0.6546 | 122.2137 | -0.060578 | -0.0021555 | 0.019942 | 0.0094443 | 0.00037377 | -0.0010125 | 0.0011494 | -0.044067 | 0.0038793 | -0.00042717 | 0.0068958 | -0.0034287 | -0.0053663 | 0.0013073 | -0.35248 | -0.15106 | -0.70953 | -0.32044 | -0.24261 | -0.43945 | -0.27008 | 0.41657 | 122.287 | -0.75989 | -0.1236 | -0.064087 | -0.48981 | -0.39368 | -0.054932 | -122.3648 | -122.5342 | 0.41199 | 0.38452 | 0.21515 | 0.43945 | 0.27008 | -0.10529 | 0.073242 | -122.3373 | 0.59052 | 0.26093 | 0.1648 | 0.36621 | 0.27008 | 0.46692 | 0.3891 | 0.6958 | 0.63629 | 0.55847 | 123.0469 | 0.50354 | 122.9416 | -122.9233 | -122.9736 | 0.33417 | 0.53101 | 0.30212 | 1.0712
4672.1719 | 122.8821 | -0.68665 | 122.2046 | -0.12161 | -0.00087374 | 0.020583 | 0.011581 | -0.0017624 | 0.0032599 | 0.002431 | -0.044067 | 0.0025975 | 0.002777 | -0.002931 | -0.0047103 | -0.0062207 | 0.0019483 | -0.43488 | -0.10986 | -0.76446 | -0.42572 | -0.33875 | -0.54474 | -0.33417 | 0.31586 | 122.3007 | -0.78735 | -0.19226 | -0.16022 | -0.56305 | -0.45319 | -0.077819 | -122.3145 | -122.6303 | 0.3479 | 0.35248 | 0.14191 | 0.4303 | 0.21973 | -0.10071 | 0.09613 | -122.3969 | 0.52643 | 0.23346 | 0.1236 | 0.33417 | 0.2243 | 0.42572 | 0.33874 | 0.62714 | 0.59509 | 0.6546 | 123.0881 | 0.57678 | 122.9874 | -122.9691 | -122.9919 | 0.26093 | 0.49438 | 0.25177 | 1.0025
4673.1719 | 122.8729 | -0.71411 | 122.2092 | -0.098725 | -0.0013009 | 0.017165 | 0.010299 | 0.0046464 | 0.0011237 | 0.00072199 | -0.068481 | 0.0034521 | 0.001068 | -0.0035718 | -0.0027877 | -0.0049389 | 0.00088014 | -0.4303 | -0.10986 | -0.7782 | -0.4303 | -0.37079 | -0.54016 | -0.35706 | 0.32959 | 122.319 | -0.7782 | -0.21515 | -0.16937 | -0.60425 | -0.48523 | -0.064087 | -122.319 | -122.6395 | 0.34332 | 0.35706 | 0.17395 | 0.42114 | 0.23804 | -0.064087 | 0.10986 | -122.4243 | 0.54474 | 0.22888 | 0.10986 | 0.29297 | 0.17395 | 0.40741 | 0.3479 | 0.60882 | 0.56305 | 0.66833 | 123.0972 | 0.60425 | 123.0331 | -122.9874 | -122.9874 | 0.28381 | 0.49896 | 0.28381 | 1.0437
4674.1719 | 122.9279 | -0.67749 | 122.1954 | -0.11398 | -1.9142e-05 | 0.019942 | 0.0085897 | -0.0043258 | 0.0015509 | 0.00093559 | 0.013916 | 0.0017431 | -0.00021357 | 0.002196 | -0.0034287 | -0.0083569 | -0.00082886 | -0.3891 | -0.15106 | -0.71869 | -0.36621 | -0.28839 | -0.47607 | -0.27924 | 0.37994 | 122.2778 | -0.76904 | -0.1831 | -0.10986 | -0.52643 | -0.42572 | -0.041199 | -122.3465 | -122.5616 | 0.3891 | 0.39825 | 0.20142 | 0.43945 | 0.24262 | -0.091553 | 0.082397 | -122.3785 | 0.56763 | 0.25177 | 0.15106 | 0.34332 | 0.24262 | 0.4303 | 0.35248 | 0.65918 | 0.58594 | 0.56763 | 123.0469 | 0.52643 | 122.9553 | -122.9141 | -122.9645 | 0.31128 | 0.49439 | 0.28839 | 1.0574
4675.1719 | 122.9279 | -0.6546 | 122.2229 | -0.091095 | -0.0017281 | 0.018233 | 0.0075217 | -0.0021896 | 0.00069649 | 8.1188e-05 | 0.029175 | 0.0011023 | 0.00042723 | -0.0059216 | -0.0019333 | -0.0072889 | -0.0023243 | -0.3479 | -0.13275 | -0.70953 | -0.32501 | -0.23346 | -0.39368 | -0.24719 | 0.45319 | 122.2961 | -0.76446 | -0.16479 | -0.073242 | -0.48981 | -0.42114 | -0.054932 | -122.3557 | -122.5479 | 0.42114 | 0.40741 | 0.26093 | 0.46234 | 0.31586 | -0.10986 | 0.073243 | -122.3877 | 0.58136 | 0.23346 | 0.1648 | 0.34332 | 0.27466 | 0.47608 | 0.38452 | 0.69122 | 0.59967 | 0.57678 | 123.0606 | 0.52185 | 122.9507 | -122.9324 | -122.9874 | 0.32959 | 0.48981 | 0.3067 | 1.1078
4676.1719 | 122.85 | -0.68665 | 122.2687 | -0.068207 | -0.00044654 | 0.019514 | 0.0098715 | 0.0063554 | -0.0027215 | 0.002431 | -0.06543 | 0.0034521 | -0.00021357 | 0.0026232 | -0.0010787 | -0.0038709 | 0.0023755 | -0.40741 | -0.10986 | -0.72784 | -0.42114 | -0.37537 | -0.54016 | -0.35706 | 0.34332 | 122.3419 | -0.75989 | -0.22888 | -0.21973 | -0.64545 | -0.48523 | -0.041198 | -122.3785 | -122.6898 | 0.31128 | 0.32959 | 0.14648 | 0.37079 | 0.18768 | -0.073242 | 0.073242 | -122.4976 | 0.46692 | 0.20142 | 0.041199 | 0.27466 | 0.11444 | 0.35248 | 0.3067 | 0.54016 | 0.53101 | 0.61798 | 123.1018 | 0.57678 | 123.0286 | -122.9965 | -123.0286 | 0.2655 | 0.45776 | 0.27924 | 1.03
4677.1719 | 122.8775 | -0.68665 | 122.2504 | -0.068207 | -0.00066014 | 0.019087 | 0.0094443 | 0.001442 | 0.0015509 | 0.0037128 | -0.037964 | 0.0015295 | -0.00021357 | 0.0017688 | -0.0012925 | -0.0070753 | 0.0021619 | -0.41657 | -0.11444 | -0.72784 | -0.4303 | -0.36163 | -0.52643 | -0.34332 | 0.37994 | 122.3511 | -0.7782 | -0.1831 | -0.14648 | -0.58594 | -0.44861 | -0.041198 | -122.3648 | -122.6807 | 0.32501 | 0.34332 | 0.16022 | 0.38452 | 0.20142 | -0.091552 | 0.10071 | -122.4335 | 0.54016 | 0.23804 | 0.10071 | 0.32959 | 0.19226 | 0.36621 | 0.29755 | 0.63171 | 0.59509 | 0.6134 | 123.1293 | 0.5722 | 123.0377 | -122.9782 | -123.0286 | 0.25635 | 0.50354 | 0.27008 | 1.0666
4678.1719 | 122.8455 | -0.65918 | 122.2458 | -0.12924 | -0.0013009 | 0.021651 | 0.010085 | -0.0013352 | 0.00069649 | 0.001363 | -0.050171 | 0.0045203 | 0.00085443 | 0.0026232 | -0.0027877 | -0.0047253 | -0.0021107 | -0.42114 | -0.09613 | -0.72784 | -0.4303 | -0.37994 | -0.53558 | -0.35706 | 0.3891 | 122.3694 | -0.74616 | -0.17853 | -0.15106 | -0.60425 | -0.45319 | -0.068664 | -122.3419 | -122.6761 | 0.27924 | 0.30212 | 0.1236 | 0.37079 | 0.19226 | -0.086975 | 0.1236 | -122.4243 | 0.50812 | 0.20599 | 0.054932 | 0.29297 | 0.14191 | 0.3479 | 0.29755 | 0.59509 | 0.56763 | 0.63171 | 123.1155 | 0.56305 | 123.0286 | -122.9736 | -122.9919 | 0.22888 | 0.48065 | 0.23804 | 1.0483
4679.1719 | 122.9233 | -0.61798 | 122.2549 | -0.15976 | -1.9142e-05 | 0.02101 | 0.0070943 | -5.343e-05 | 0.0011237 | 0.00029479 | 0.035278 | 0.0034521 | 0.00064083 | -0.0027174 | -0.0012925 | -0.0068615 | 0.00066654 | -0.3479 | -0.13733 | -0.65918 | -0.33417 | -0.24261 | -0.41199 | -0.24719 | 0.50812 | 122.3328 | -0.70496 | -0.10986 | -0.064087 | -0.48523 | -0.37537 | -0.041199 | -122.3923 | -122.5891 | 0.37537 | 0.37079 | 0.20599 | 0.41199 | 0.24719 | -0.086975 | 0.07782 | -122.3648 | 0.55389 | 0.24262 | 0.13275 | 0.32959 | 0.21973 | 0.41656 | 0.32501 | 0.64087 | 0.59509 | 0.52185 | 123.0377 | 0.48065 | 122.9507 | -122.9141 | -122.9599 | 0.28381 | 0.50812 | 0.27008 | 1.1261
4680.1719 | 122.9691 | -0.63629 | 122.2137 | -0.098725 | -0.0032235 | 0.019301 | 0.0068807 | -0.0024032 | -0.0012261 | 0.00093559 | 0.050537 | 0.00067495 | 0.00021363 | -0.0076306 | -0.0019333 | -0.0083569 | -0.0051013 | -0.35248 | -0.13733 | -0.68665 | -0.30212 | -0.19226 | -0.36163 | -0.19684 | 0.59509 | 122.3282 | -0.70953 | -0.082397 | -0.004578 | -0.4303 | -0.36621 | -0.050354 | -122.3511 | -122.5159 | 0.44403 | 0.43945 | 0.27466 | 0.48981 | 0.32501 | -0.073242 | 0.11444 | -122.2961 | 0.63171 | 0.27008 | 0.20599 | 0.34332 | 0.27924 | 0.49438 | 0.38452 | 0.70496 | 0.62714 | 0.54932 | 123.0377 | 0.49896 | 122.9645 | -122.9004 | -122.9233 | 0.33417 | 0.5539 | 0.28381 | 1.2314
4681.1719 | 122.8409 | -0.66834 | 122.2824 | -0.098725 | -0.0013009 | 0.021651 | 0.0094443 | -0.0013352 | -0.00079891 | 0.0037128 | -0.050171 | 0.0049475 | 0.00085443 | 5.9824e-05 | -0.0027877 | -0.0066479 | 0.00088014 | -0.41199 | -0.091553 | -0.71411 | -0.4303 | -0.40741 | -0.54474 | -0.38452 | 0.3891 | 122.3831 | -0.76446 | -0.19226 | -0.17395 | -0.6134 | -0.45319 | -0.045776 | -122.374 | -122.7127 | 0.26093 | 0.28381 | 0.1236 | 0.32959 | 0.16937 | -0.09613 | 0.10071 | -122.4747 | 0.49439 | 0.21515 | 0.054932 | 0.31128 | 0.15106 | 0.3067 | 0.28381 | 0.59051 | 0.5722 | 0.62256 | 123.1476 | 0.57678 | 123.0515 | -122.9965 | -123.0469 | 0.23804 | 0.47607 | 0.25635 | 1.0574
4682.1719 | 122.8317 | -0.68207 | 122.2595 | -0.13687 | -0.00044654 | 0.020583 | 0.010299 | -5.343e-05 | -0.0016535 | 0.0011494 | -0.059326 | 0.0028113 | 0.00021363 | 0.0013416 | -0.0030013 | -0.0051527 | -0.00018806 | -0.39825 | -0.086975 | -0.71411 | -0.4303 | -0.39825 | -0.53558 | -0.36163 | 0.39368 | 122.3648 | -0.75531 | -0.19226 | -0.20142 | -0.63171 | -0.48981 | -0.032043 | -122.3465 | -122.6898 | 0.28381 | 0.32044 | 0.14648 | 0.35248 | 0.17853 | -0.073242 | 0.10529 | -122.4518 | 0.48065 | 0.19226 | 0.050354 | 0.2655 | 0.1236 | 0.31586 | 0.28381 | 0.55389 | 0.56305 | 0.62714 | 123.1201 | 0.59509 | 123.0469 | -122.9736 | -123.0148 | 0.25177 | 0.48981 | 0.28381 | 1.0757
4683.1719 | 122.8363 | -0.69122 | 122.2504 | -0.068207 | -0.00066014 | 0.017805 | 0.0098715 | -0.0011214 | 0.00026909 | 0.00072199 | -0.050171 | 0.0021703 | 0.00064083 | -0.0014356 | -0.0015061 | -0.0064343 | -0.00061526 | -0.40283 | -0.091553 | -0.72784 | -0.42114 | -0.37537 | -0.52643 | -0.35706 | 0.42114 | 122.3465 | -0.75989 | -0.21515 | -0.18768 | -0.62714 | -0.47607 | -0.036621 | -122.3419 | -122.6715 | 0.31586 | 0.33417 | 0.1648 | 0.37079 | 0.20142 | -0.068665 | 0.096131 | -122.4655 | 0.50354 | 0.21515 | 0.064087 | 0.28381 | 0.13275 | 0.35248 | 0.3067 | 0.57221 | 0.54474 | 0.63629 | 123.1064 | 0.59967 | 123.0377 | -122.9782 | -123.0103 | 0.27008 | 0.47607 | 0.28839 | 1.1124
4684.1719 | 122.9828 | -0.6546 | 122.2183 | -0.068207 | -0.0010873 | 0.020796 | 0.0068807 | -0.0013352 | 0.0013373 | 0.00093559 | -0.0013428 | 0.0017431 | 0.0021362 | 0.0034778 | -0.0025741 | -0.0070753 | -0.00018806 | -0.33417 | -0.13275 | -0.6958 | -0.3067 | -0.24719 | -0.40741 | -0.23804 | 0.60883 | 122.319 | -0.72327 | -0.07782 | -0.032043 | -0.48065 | -0.36621 | -0.041199 | -122.3511 | -122.525 | 0.40741 | 0.41657 | 0.24719 | 0.45776 | 0.28839 | -0.068665 | 0.10071 | -122.2961 | 0.62256 | 0.28839 | 0.17395 | 0.35706 | 0.24261 | 0.44861 | 0.3891 | 0.69122 | 0.64545 | 0.56305 | 123.0423 | 0.52185 | 122.9736 | -122.9141 | -122.9416 | 0.3479 | 0.57678 | 0.32044 | 1.2634
4685.1719 | 122.8317 | -0.69122 | 122.2458 | -0.052948 | -0.00023294 | 0.019301 | 0.01094 | -0.0032578 | -0.00015811 | 0.0028582 | -0.062378 | 0.0038793 | -0.00042717 | 0.0041186 | -0.0015061 | -0.0068615 | -0.0025379 | -0.41199 | -0.073242 | -0.737 | -0.45319 | -0.40283 | -0.53101 | -0.35706 | 0.42572 | 122.3557 | -0.77362 | -0.20142 | -0.17853 | -0.63629 | -0.4715 | -0.045777 | -122.319 | -122.699 | 0.28839 | 0.33417 | 0.16022 | 0.37994 | 0.20599 | -0.082398 | 0.10986 | -122.4472 | 0.5127 | 0.21973 | 0.054931 | 0.30212 | 0.13733 | 0.33417 | 0.28381 | 0.59509 | 0.5722 | 0.66376 | 123.1293 | 0.61798 | 123.0469 | -122.9828 | -123.0194 | 0.23804 | 0.48981 | 0.27924 | 1.1169
4686.1719 | 122.8363 | -0.69122 | 122.2778 | -0.098725 | -0.0013009 | 0.019301 | 0.0098715 | -0.0013352 | 0.0015509 | 0.001363 | -0.037964 | 0.0036657 | -0.00021357 | -0.0018628 | -0.0034287 | -0.0064343 | 0.0049389 | -0.40283 | -0.07782 | -0.72327 | -0.42572 | -0.38452 | -0.52643 | -0.37537 | 0.44861 | 122.3557 | -0.7782 | -0.21515 | -0.16937 | -0.62256 | -0.49439 | -0.032044 | -122.3557 | -122.7036 | 0.3067 | 0.31586 | 0.1648 | 0.3479 | 0.19684 | -0.086975 | 0.07782 | -122.493 | 0.52185 | 0.19684 | 0.068664 | 0.28381 | 0.15564 | 0.33875 | 0.29755 | 0.60882 | 0.56305 | 0.64545 | 123.1339 | 0.6134 | 123.0469 | -123.0011 | -123.056 | 0.2655 | 0.47607 | 0.28839 | 1.1398
4687.1719 | 122.8455 | -0.68665 | 122.2504 | -0.075836 | 0.00062166 | 0.02101 | 0.01094 | -0.00026703 | -0.0014399 | 0.00414 | -0.059326 | 0.0043065 | 0.0012818 | 0.0028368 | -0.0017197 | -0.0051527 | 2.554e-05 | -0.41199 | -0.082397 | -0.73242 | -0.41657 | -0.42114 | -0.54474 | -0.32959 | 0.48523 | 122.374 | -0.75989 | -0.18768 | -0.16022 | -0.60883 | -0.46234 | -0.045776 | -122.3328 | -122.6669 | 0.2655 | 0.35706 | 0.14191 | 0.40283 | 0.18768 | -0.073242 | 0.1236 | -122.438 | 0.52643 | 0.2243 | 0.07782 | 0.29755 | 0.15106 | 0.31128 | 0.31586 | 0.59967 | 0.57221 | 0.65003 | 123.1339 | 0.60425 | 123.0606 | -122.9828 | -123.0103 | 0.27008 | 0.49896 | 0.27466 | 1.1719
4688.1719 | 122.8363 | -0.68207 | 122.2733 | -0.022431 | -0.00066014 | 0.020369 | 0.010299 | -0.0011214 | 0.00026909 | 0.003072 | -0.03186 | 0.0045203 | 0.0021362 | 0.0043322 | -0.0025741 | -0.0060071 | 0.0038709 | -0.39825 | -0.082397 | -0.70953 | -0.39368 | -0.36163 | -0.50354 | -0.31586 | 0.53558 | 122.3557 | -0.737 | -0.16937 | -0.17395 | -0.60425 | -0.44403 | -0.027466 | -122.3557 | -122.6669 | 0.32044 | 0.36621 | 0.17853 | 0.39368 | 0.20599 | -0.054932 | 0.082398 | -122.4426 | 0.50812 | 0.23804 | 0.07782 | 0.29297 | 0.13275 | 0.3479 | 0.31586 | 0.56305 | 0.56763 | 0.62714 | 123.0927 | 0.59967 | 123.0377 | -122.9828 | -123.0103 | 0.28839 | 0.5127 | 0.28381 | 1.2177
4689.1719 | 122.8912 | -1.3504 | 121.5408 | -0.083466 | -0.0021555 | 0.012465 | 0.0058127 | -0.00026703 | 0.0045417 | 0.0034992 | -0.0074462 | 0.0047339 | -0.00042717 | -0.00079478 | -0.0040695 | -0.0066479 | 0.0049389 | -0.71411 | -0.1831 | -1.4236 | -0.44861 | -0.3479 | -0.87891 | -0.37079 | 0.12817 | 121.6507 | -1.4557 | -0.65918 | -0.62256 | -1.236 | -1.1124 | -0.073242 | -121.7239 | -121.9894 | 1.0025 | 0.97961 | 0.4715 | 1.0529 | 0.54474 | -0.10529 | 0.10986 | -122.2 | 0.72784 | 0.23804 | 0.11444 | 0.34332 | 0.21973 | 1.0757 | 0.97504 | 0.83313 | 0.79651 | 1.2405 | 123.1064 | 1.1673 | 123.0011 | -122.9645 | -122.9965 | 0.9018 | 0.69122 | 0.63629 | 1.4786
4690.1719 | 122.8912 | -1.3412 | 121.5683 | -0.091095 | -0.00044654 | 0.012038 | 0.0068807 | 0.0018692 | 0.0013373 | 0.00414 | -0.010498 | 0.0043065 | -0.00042717 | -0.0014356 | -0.0023605 | -0.0064343 | 0.0028027 | -0.62256 | -0.15564 | -1.4099 | -0.4715 | -0.37079 | -0.78735 | -0.40741 | 0.14648 | 121.6553 | -1.442 | -0.67749 | -0.60425 | -1.2405 | -1.1032 | -0.068664 | -121.7239 | -122.0398 | 0.97046 | 0.93384 | 0.55389 | 1.0025 | 0.62256 | -0.10071 | 0.086975 | -122.2458 | 0.737 | 0.23804 | 0.10071 | 0.33875 | 0.20142 | 1.0391 | 0.93841 | 0.83771 | 0.76447 | 1.2543 | 123.0972 | 1.1856 | 122.9965 | -122.9782 | -123.0103 | 0.86975 | 0.66376 | 0.71869 | 1.4877
4691.1719 | 122.8638 | -1.3367 | 121.5958 | -0.083466 | -0.0010873 | 0.015456 | 0.0079489 | 0.001442 | 0.0017645 | 0.0043536 | -0.037964 | 0.0025975 | 0.0040588 | -0.0033582 | -0.0032151 | -0.0051527 | -0.0021107 | -0.66376 | -0.16022 | -1.4053 | -0.52643 | -0.48065 | -0.85144 | -0.41657 | 0.086975 | 121.6782 | -1.4374 | -0.67749 | -0.62714 | -1.2772 | -1.0941 | -0.068664 | -121.756 | -122.1222 | 0.85602 | 0.9201 | 0.48523 | 0.98877 | 0.55389 | -0.10071 | 0.082398 | -122.2733 | 0.70953 | 0.24262 | 0.059509 | 0.34332 | 0.16022 | 0.92468 | 0.87891 | 0.81024 | 0.75989 | 1.2451 | 123.1155 | 1.1765 | 123.0148 | -123.0011 | -123.0331 | 0.81024 | 0.65918 | 0.67291 | 1.4236
4692.1719 | 122.8729 | -1.3412 | 121.6049 | -0.091095 | -0.00044654 | 0.012679 | 0.010726 | 0.004219 | 0.0028327 | 0.007558 | -0.025757 | 0.0028113 | -0.00021357 | -0.002931 | -0.00086511 | -0.0068615 | 0.0015209 | -0.66376 | -0.16022 | -1.3916 | -0.49439 | -0.43488 | -0.8194 | -0.41657 | 0.11902 | 121.6599 | -1.4328 | -0.65918 | -0.59967 | -1.2543 | -1.0941 | -0.050354 | -121.7651 | -122.0993 | 0.90637 | 0.92468 | 0.52185 | 0.97504 | 0.5722 | -0.091552 | 0.054932 | -122.2641 | 0.74158 | 0.24719 | 0.086976 | 0.33875 | 0.17853 | 0.95673 | 0.89722 | 0.83313 | 0.77362 | 1.2314 | 123.0927 | 1.181 | 123.0011 | -122.9965 | -123.0377 | 0.84686 | 0.68207 | 0.67749 | 1.4603
4693.1719 | 122.8775 | -1.3458 | 121.6003 | -0.060578 | 0.00019446 | 0.015669 | 0.0088033 | -0.00026703 | 0.0017645 | 0.00093559 | -0.025757 | 0.0023839 | 0.00085443 | 0.0026232 | -0.0040695 | -0.0055799 | -0.00040166 | -0.62714 | -0.15564 | -1.3962 | -0.46692 | -0.38452 | -0.78735 | -0.39368 | 0.20142 | 121.6919 | -1.4099 | -0.65918 | -0.60425 | -1.236 | -1.0895 | -0.050354 | -121.756 | -122.0673 | 0.9613 | 0.95215 | 0.55847 | 1.0025 | 0.60883 | -0.064087 | 0.091553 | -122.2595 | 0.74158 | 0.25635 | 0.10986 | 0.32043 | 0.17395 | 1.0117 | 0.92926 | 0.80566 | 0.75073 | 1.2405 | 123.1018 | 1.1902 | 123.0377 | -122.9965 | -123.0103 | 0.87891 | 0.68665 | 0.71869 | 1.5472
4694.1719 | 122.8867 | -1.3641 | 121.5271 | -0.060578 | 0.00040806 | 0.013533 | 0.0088033 | 0.0022964 | 0.0024053 | 0.0054218 | -0.019653 | 0.0036657 | 0.00021363 | 0.0024096 | -0.0023605 | -0.0057935 | -0.0014697 | -0.67749 | -0.15564 | -1.4328 | -0.46692 | -0.36621 | -0.84686 | -0.3891 | 0.19226 | 121.637 | -1.474 | -0.67749 | -0.63171 | -1.2817 | -1.0941 | -0.068664 | -121.6827 | -121.994 | 0.99792 | 0.97504 | 0.51727 | 1.0437 | 0.58594 | -0.10986 | 0.10986 | -122.2046 | 0.73242 | 0.27008 | 0.082398 | 0.37994 | 0.19226 | 1.0666 | 0.96588 | 0.84229 | 0.79651 | 1.2772 | 123.111 | 1.2085 | 123.0011 | -122.9599 | -123.0011 | 0.89722 | 0.68665 | 0.68665 | 1.5564
4695.1719 | 122.8592 | -1.387 | 121.5546 | -0.083466 | -0.00087374 | 0.013106 | 0.010299 | -0.0021896 | 0.0013373 | 0.0045672 | -0.0013428 | 0.0025975 | 0.0029906 | -0.0037854 | -0.0012925 | -0.0053663 | 0.0060071 | -0.69122 | -0.16022 | -1.4191 | -0.46692 | -0.41199 | -0.88348 | -0.41199 | 0.17853 | 121.6644 | -1.4648 | -0.69122 | -0.73242 | -1.2955 | -1.1353 | -0.032043 | -121.7148 | -122.0215 | 0.97504 | 0.97504 | 0.50354 | 1.0071 | 0.53558 | -0.07782 | 0.10986 | -122.2458 | 0.6546 | 0.25177 | 0.091553 | 0.32959 | 0.16937 | 1.0071 | 0.95215 | 0.73242 | 0.77362 | 1.2589 | 123.1293 | 1.2268 | 123.0515 | -122.9736 | -123.0194 | 0.92011 | 0.6958 | 0.6958 | 1.5656
4696.1719 | 122.9095 | -1.3824 | 121.5683 | -0.098725 | 0.00040806 | 0.012038 | 0.0079489 | 0.0022964 | 0.0017645 | 0.0073444 | -0.0013428 | 0.0011023 | -0.00042717 | 0.0043322 | -0.0019333 | -0.0057935 | 0.00088014 | -0.66376 | -0.14191 | -1.4099 | -0.45776 | -0.3891 | -0.81024 | -0.36621 | 0.26093 | 121.669 | -1.4511 | -0.63171 | -0.65918 | -1.2268 | -1.0849 | -0.027466 | -121.7102 | -122.0261 | 0.99335 | 1.0162 | 0.5722 | 1.0437 | 0.59967 | -0.068665 | 0.10071 | -122.2 | 0.72327 | 0.29755 | 0.15564 | 0.36621 | 0.2243 | 1.0208 | 0.95215 | 0.79193 | 0.8194 | 1.268 | 123.1201 | 1.2405 | 123.0515 | -122.9782 | -123.0194 | 0.92468 | 0.75073 | 0.71869 | 1.6434
4697.1719 | 122.8912 | -1.3504 | 121.5683 | -0.083466 | -0.0017281 | 0.014174 | 0.0088033 | 0.0018692 | 0.0036871 | 0.0079852 | -0.01355 | 0.0023839 | 0.0023498 | -0.002931 | -0.0019333 | -0.0057935 | -0.00040166 | -0.62256 | -0.15106 | -1.387 | -0.4303 | -0.35248 | -0.78278 | -0.3479 | 0.3067 | 121.6782 | -1.4145 | -0.60883 | -0.64545 | -1.2177 | -1.0529 | -0.036621 | -121.7194 | -121.9986 | 0.99792 | 1.0025 | 0.56763 | 1.0391 | 0.60425 | -0.064087 | 0.10986 | -122.1771 | 0.70496 | 0.29755 | 0.13275 | 0.36163 | 0.19684 | 1.0345 | 0.95673 | 0.76904 | 0.80566 | 1.236 | 123.0927 | 1.1993 | 123.0286 | -122.9553 | -122.9828 | 0.9201 | 0.74158 | 0.72784 | 1.6571
4698.1719 | 122.8363 | -1.3458 | 121.6232 | -0.083466 | -1.9142e-05 | 0.014174 | 0.0081625 | 0.0012284 | 0.0030463 | 0.0045672 | -0.044067 | 0.0038793 | 0.001709 | 0.0015552 | -0.0025741 | -0.0055799 | -0.0010425 | -0.6546 | -0.14191 | -1.3779 | -0.46234 | -0.41199 | -0.83313 | -0.39825 | 0.24261 | 121.701 | -1.4191 | -0.65002 | -0.67749 | -1.2634 | -1.0757 | -0.032044 | -121.7651 | -122.0856 | 0.93384 | 0.94757 | 0.5127 | 0.97962 | 0.54474 | -0.073242 | 0.07782 | -122.2733 | 0.66834 | 0.27008 | 0.082397 | 0.34332 | 0.15564 | 0.96588 | 0.91553 | 0.74158 | 0.76904 | 1.236 | 123.1201 | 1.2039 | 123.0469 | -123.0011 | -123.0423 | 0.88348 | 0.6958 | 0.69122 | 1.5884
4699.1719 | 122.8775 | -1.2817 | 121.6507 | -0.052948 | 0.00019446 | 0.011824 | 0.0068807 | -0.0034714 | 0.0036871 | 0.0032856 | -0.028809 | 0.0040929 | 0.0012818 | -0.0020764 | -0.0025741 | -0.0081433 | 0.0040845 | -0.63171 | -0.13275 | -1.3412 | -0.44861 | -0.40741 | -0.81024 | -0.3891 | 0.31586 | 121.7377 | -1.3687 | -0.60425 | -0.64545 | -1.236 | -1.0529 | -0.05951 | -121.7834 | -122.0993 | 0.87433 | 0.89264 | 0.4715 | 0.95215 | 0.53101 | -0.086975 | 0.086975 | -122.2549 | 0.63629 | 0.22888 | 0.045776 | 0.31586 | 0.13275 | 0.93384 | 0.89264 | 0.72327 | 0.76447 | 1.2085 | 123.1064 | 1.149 | 123.0194 | -122.9919 | -123.0194 | 0.83313 | 0.67749 | 0.65002 | 1.5976
4700.1719 | 122.8592 | -1.3046 | 121.6644 | -0.13687 | -1.9142e-05 | 0.014601 | 0.0092307 | 0.00037377 | 0.0028327 | 0.0028582 | -0.016602 | 0.0049475 | 0.001709 | -0.00464 | -0.0019333 | -0.0064343 | 0.0023755 | -0.63629 | -0.1236 | -1.3504 | -0.48065 | -0.45319 | -0.82398 | -0.42572 | 0.29297 | 121.7468 | -1.3916 | -0.60883 | -0.63629 | -1.2268 | -1.0391 | -0.045777 | -121.788 | -122.1451 | 0.85144 | 0.87891 | 0.48065 | 0.92468 | 0.52643 | -0.086976 | 0.082397 | -122.2733 | 0.66833 | 0.2655 | 0.077819 | 0.35248 | 0.1648 | 0.89722 | 0.86975 | 0.75531 | 0.78278 | 1.2268 | 123.1384 | 1.181 | 123.0515 | -123.0148 | -123.056 | 0.82397 | 0.6958 | 0.66833 | 1.5976
4701.1719 | 122.905 | -1.2589 | 121.6553 | -0.083466 | -0.0027963 | 0.014174 | 0.010085 | -0.00026703 | 0.0043281 | 0.0045672 | -0.01355 | 0.0028113 | 0.0040588 | 0.0026232 | -0.0034287 | -0.0072889 | 0.0017345 | -0.57678 | -0.13275 | -1.3138 | -0.40283 | -0.33875 | -0.70496 | -0.33417 | 0.43945 | 121.7422 | -1.3458 | -0.54016 | -0.55389 | -1.1353 | -0.96588 | -0.054932 | -121.788 | -122.0581 | 0.9201 | 0.92468 | 0.55389 | 0.97962 | 0.60883 | -0.086975 | 0.086976 | -122.1954 | 0.70496 | 0.29297 | 0.1236 | 0.37994 | 0.21057 | 0.97504 | 0.91095 | 0.79193 | 0.80566 | 1.181 | 123.0881 | 1.1261 | 123.0011 | -122.9691 | -123.0011 | 0.85602 | 0.71869 | 0.68207 | 1.6983
4702.1719 | 122.9004 | -1.268 | 121.6553 | -0.075836 | 0.0014761 | 0.012892 | 0.0081625 | 0.00080117 | 0.0021917 | 0.00414 | 0.0078126 | 0.0028113 | 0.00021363 | 0.0024096 | -0.0023605 | -0.0081433 | 0.0038709 | -0.57678 | -0.14191 | -1.3229 | -0.42572 | -0.32959 | -0.70038 | -0.32501 | 0.4715 | 121.7422 | -1.3412 | -0.53558 | -0.54474 | -1.1353 | -0.9613 | -0.054932 | -121.7972 | -122.081 | 0.93841 | 0.94299 | 0.56763 | 0.99792 | 0.62256 | -0.073243 | 0.086976 | -122.1909 | 0.72327 | 0.3067 | 0.13275 | 0.37994 | 0.20599 | 0.99335 | 0.89722 | 0.79651 | 0.80566 | 1.181 | 123.0835 | 1.1261 | 123.0103 | -122.9782 | -122.9965 | 0.84229 | 0.73242 | 0.69122 | 1.7395
4703.1719 | 122.9187 | -1.2726 | 121.669 | -0.060578 | 0.00083526 | 0.013106 | 0.0058127 | -0.00090783 | 0.0043281 | 0.0052082 | 0.001709 | 0.0058019 | 0.0014954 | 0.0036914 | -0.0030013 | -0.0057935 | -0.00082886 | -0.54474 | -0.14648 | -1.3046 | -0.41657 | -0.33875 | -0.68207 | -0.33417 | 0.50812 | 121.7697 | -1.3458 | -0.51727 | -0.54474 | -1.1215 | -0.98419 | -0.032043 | -121.8155 | -122.0856 | 0.93384 | 0.93842 | 0.59052 | 0.97046 | 0.62256 | -0.073242 | 0.10071 | -122.1863 | 0.72784 | 0.28839 | 0.15106 | 0.36163 | 0.2243 | 0.96588 | 0.88806 | 0.80109 | 0.82855 | 1.1581 | 123.1155 | 1.1261 | 123.0423 | -122.9736 | -123.0148 | 0.85602 | 0.75531 | 0.72784 | 1.7807
4704.1719 | 122.8958 | -1.2222 | 121.7194 | -0.075836 | -0.0013009 | 0.013319 | 0.0075217 | -0.00090783 | 0.0019781 | -0.00013241 | -0.0043946 | 0.0025975 | 0.00021363 | -0.00058098 | -0.0032151 | -0.0062207 | 0.0015209 | -0.54016 | -0.12817 | -1.268 | -0.42114 | -0.35248 | -0.69122 | -0.33417 | 0.53558 | 121.7972 | -1.3138 | -0.5127 | -0.53558 | -1.1169 | -0.9613 | -0.045776 | -121.8475 | -122.1405 | 0.86975 | 0.88806 | 0.53101 | 0.93384 | 0.57678 | -0.091553 | 0.07782 | -122.2321 | 0.68665 | 0.26092 | 0.10529 | 0.35248 | 0.19684 | 0.91553 | 0.84686 | 0.7782 | 0.80109 | 1.1398 | 123.111 | 1.0941 | 123.0194 | -122.9874 | -123.0331 | 0.80109 | 0.70953 | 0.68207 | 1.7578
4705.1719 | 122.9004 | -1.2268 | 121.7239 | -0.052948 | -0.00066014 | 0.014815 | 0.0088033 | 0.0012284 | 0.0024053 | 0.0054218 | 0.026123 | 0.0051611 | 0.00064083 | -0.0025036 | -0.00065151 | -0.0064343 | 0.0015209 | -0.53558 | -0.1236 | -1.2817 | -0.42114 | -0.33417 | -0.67291 | -0.32959 | 0.55847 | 121.8018 | -1.3046 | -0.50354 | -0.52185 | -1.0803 | -0.93384 | -0.054931 | -121.8475 | -122.1451 | 0.89264 | 0.89722 | 0.55389 | 0.95215 | 0.60883 | -0.077819 | 0.07782 | -122.2275 | 0.70496 | 0.29297 | 0.14648 | 0.37079 | 0.2243 | 0.94757 | 0.86059 | 0.78278 | 0.80109 | 1.1581 | 123.1064 | 1.1032 | 123.0286 | -123.0057 | -123.0286 | 0.80566 | 0.72327 | 0.69122 | 1.7853
4706.1719 | 122.9233 | -1.2314 | 121.7056 | -0.052948 | -0.00023294 | 0.013106 | 0.0088033 | 0.0061416 | 0.0013373 | 0.00414 | -0.028809 | 0.0030249 | 0.0012818 | 0.0036914 | -0.0023605 | -0.0081433 | -0.0031787 | -0.52185 | -0.12817 | -1.2909 | -0.41657 | -0.34332 | -0.66834 | -0.32501 | 0.4303 | 121.8063 | -1.3184 | -0.52185 | -0.54932 | -1.0849 | -0.97046 | -0.05951 | -121.8338 | -122.1222 | 0.88806 | 0.90637 | 0.56305 | 0.96588 | 0.62256 | -0.086975 | 0.10071 | -122.2275 | 0.68207 | 0.26093 | 0.14648 | 0.3479 | 0.23346 | 0.94757 | 0.87433 | 0.76904 | 0.79651 | 1.1627 | 123.1247 | 1.1032 | 123.0377 | -122.9965 | -123.024 | 0.81482 | 0.70953 | 0.70953 | 1.6617
4707.1719 | 122.8912 | -1.1993 | 121.7148 | -0.075836 | 0.00019446 | 0.014815 | 0.0098715 | -0.0028304 | 0.0028327 | 0.0064898 | -0.0043946 | 0.0038793 | 0.0025634 | 0.00048702 | -0.0030013 | -0.0053663 | 0.00088014 | -0.54016 | -0.11902 | -1.2589 | -0.41657 | -0.35706 | -0.66834 | -0.33875 | 0.49439 | 121.8292 | -1.2909 | -0.49896 | -0.55847 | -1.1032 | -0.97961 | -0.059509 | -121.8338 | -122.1313 | 0.84228 | 0.8606 | 0.53101 | 0.9201 | 0.59052 | -0.091553 | 0.11444 | -122.2137 | 0.64087 | 0.21973 | 0.096131 | 0.31128 | 0.18768 | 0.90179 | 0.84228 | 0.73242 | 0.79193 | 1.1398 | 123.1201 | 1.0803 | 123.0286 | -122.9736 | -123.0057 | 0.78278 | 0.70038 | 0.65918 | 1.6937
4708.1719 | 122.8683 | -1.2451 | 121.7056 | -0.075836 | 0.0014761 | 0.014601 | 0.0075217 | 0.0057144 | 0.0032599 | 0.0032856 | -0.0043946 | 0.0043065 | 0.00021363 | -0.0010084 | -0.0019333 | -0.0075025 | 0.0023755 | -0.55389 | -0.11902 | -1.268 | -0.43488 | -0.37994 | -0.70038 | -0.36163 | 0.46692 | 121.8155 | -1.3275 | -0.51727 | -0.59509 | -1.1353 | -1.0162 | -0.022888 | -121.8246 | -122.1405 | 0.86517 | 0.88348 | 0.54474 | 0.90637 | 0.56763 | -0.082398 | 0.10986 | -122.2229 | 0.65002 | 0.22888 | 0.10986 | 0.31128 | 0.19226 | 0.88806 | 0.83313 | 0.73242 | 0.81024 | 1.149 | 123.143 | 1.1261 | 123.0606 | -122.9736 | -123.0331 | 0.81024 | 0.72784 | 0.69122 | 1.712
4709.1719 | 122.8958 | -1.2497 | 121.7056 | -0.083466 | -1.9142e-05 | 0.012679 | 0.0088033 | 0.00251 | 0.0028327 | 0.0026446 | 0.016968 | 0.0023839 | -0.001709 | 0.0013416 | -0.0036423 | -0.0066479 | 0.0021619 | -0.54474 | -0.14648 | -1.268 | -0.42572 | -0.3479 | -0.67749 | -0.35706 | 0.49896 | 121.7834 | -1.3184 | -0.49896 | -0.56763 | -1.1215 | -0.97961 | -0.01831 | -121.8521 | -122.1313 | 0.9018 | 0.89264 | 0.5722 | 0.91095 | 0.59052 | -0.068664 | 0.07782 | -122.2046 | 0.68207 | 0.27008 | 0.12817 | 0.33875 | 0.19684 | 0.92011 | 0.84229 | 0.75073 | 0.8194 | 1.1215 | 123.1018 | 1.1032 | 123.0331 | -122.9736 | -123.024 | 0.82398 | 0.75073 | 0.70496 | 1.7487
4710.1719 | 122.9233 | -1.2497 | 121.7239 | -0.068207 | -1.9142e-05 | 0.015669 | 0.0068807 | 0.00251 | 0.0043281 | 0.0022174 | 0.023071 | 0.0038793 | 0.0012818 | 0.0026232 | -0.0034287 | -0.0064343 | -0.0012561 | -0.54932 | -0.10529 | -1.2772 | -0.43945 | -0.39368 | -0.65918 | -0.34332 | 0.46692 | 121.8063 | -1.2909 | -0.48981 | -0.51727 | -1.0849 | -0.97046 | -0.027466 | -121.8292 | -122.1634 | 0.85602 | 0.90637 | 0.59052 | 0.93384 | 0.61798 | -0.041199 | 0.082397 | -122.2137 | 0.73242 | 0.27924 | 0.1648 | 0.32044 | 0.20599 | 0.88348 | 0.83771 | 0.77362 | 0.80109 | 1.1719 | 123.0972 | 1.1444 | 123.056 | -123.0011 | -123.0148 | 0.81024 | 0.75989 | 0.70038 | 1.7166
4711.1719 | 122.9279 | -1.2039 | 121.756 | -0.052948 | -0.0025827 | 0.012679 | 0.0070943 | -5.343e-05 | 0.0030463 | 0.0060626 | 0.044434 | 0.0043065 | 0.0025634 | 0.0034778 | -0.0030013 | -0.0062207 | 0.0023755 | -0.54932 | -0.10529 | -1.2772 | -0.44861 | -0.39825 | -0.66376 | -0.35706 | 0.52185 | 121.8384 | -1.2909 | -0.48523 | -0.52643 | -1.0941 | -0.97961 | -0.073243 | -121.8613 | -122.2046 | 0.80566 | 0.84686 | 0.54016 | 0.9201 | 0.6134 | -0.086976 | 0.082398 | -122.2412 | 0.67749 | 0.2243 | 0.10986 | 0.31128 | 0.19684 | 0.87891 | 0.82855 | 0.76447 | 0.80566 | 1.1719 | 123.1293 | 1.0986 | 123.0423 | -123.0331 | -123.0469 | 0.75531 | 0.71869 | 0.6546 | 1.7258
4712.1719 | 122.9279 | -1.1856 | 121.7514 | -0.091095 | 0.0014761 | 0.014601 | 0.0098715 | 0.0027238 | 0.0017645 | 0.0064898 | -0.0013428 | 0.0038793 | 0.0021362 | 5.9824e-05 | -0.0038559 | -0.0068615 | 0.0042981 | -0.51727 | -0.11902 | -1.2451 | -0.40741 | -0.32959 | -0.63171 | -0.31586 | 0.62714 | 121.8475 | -1.2772 | -0.43488 | -0.50354 | -1.0483 | -0.93842 | -0.059509 | -121.8704 | -122.1588 | 0.85602 | 0.86975 | 0.55389 | 0.92926 | 0.6134 | -0.091553 | 0.09613 | -122.1863 | 0.68207 | 0.24719 | 0.13733 | 0.33874 | 0.22888 | 0.91553 | 0.83771 | 0.77362 | 0.84229 | 1.1261 | 123.1247 | 1.0666 | 123.0331 | -122.9965 | -123.0286 | 0.7782 | 0.75073 | 0.66834 | 1.8127
4713.1719 | 122.8958 | -1.2039 | 121.7651 | -0.075836 | 0.00062166 | 0.014174 | 0.0077353 | 0.0020828 | 0.0032599 | 0.0047808 | 0.013916 | 0.0049475 | 0.003418 | -0.0025036 | -0.00022431 | -0.0060071 | 0.0036571 | -0.56305 | -0.11444 | -1.2497 | -0.44403 | -0.39368 | -0.68665 | -0.36621 | 0.59967 | 121.8521 | -1.2726 | -0.43945 | -0.48981 | -1.0941 | -0.95215 | -0.045777 | -121.8796 | -122.2092 | 0.81024 | 0.83771 | 0.51727 | 0.88348 | 0.56305 | -0.068665 | 0.086975 | -122.2046 | 0.71411 | 0.25177 | 0.10986 | 0.32044 | 0.17853 | 0.85602 | 0.80566 | 0.78278 | 0.83313 | 1.1353 | 123.1247 | 1.0895 | 123.056 | -123.0148 | -123.0377 | 0.75989 | 0.76447 | 0.64087 | 1.8036
4714.1719 | 122.9416 | -1.1765 | 121.7789 | -0.10635 | 0.00083526 | 0.014601 | 0.0098715 | 0.00058737 | 0.0034735 | 0.00414 | -0.044067 | 0.0032385 | 0.0014954 | 0.0034778 | -0.0034287 | -0.0068615 | 2.554e-05 | -0.49896 | -0.10529 | -1.2268 | -0.40283 | -0.32501 | -0.60883 | -0.32044 | 0.70038 | 121.8521 | -1.2543 | -0.39825 | -0.48065 | -1.0437 | -0.9201 | -0.050354 | -121.8842 | -122.1817 | 0.85144 | 0.85602 | 0.56763 | 0.90637 | 0.61798 | -0.077819 | 0.073242 | -122.1771 | 0.6958 | 0.25635 | 0.13275 | 0.33417 | 0.21057 | 0.90179 | 0.82397 | 0.77362 | 0.85602 | 1.1215 | 123.1064 | 1.0712 | 123.0286 | -123.0057 | -123.0331 | 0.77362 | 0.7782 | 0.67749 | 1.8768
4715.1719 | 122.9279 | -1.1719 | 121.7697 | -0.11398 | 0.00019446 | 0.015028 | 0.0075217 | -0.005394 | 0.00069649 | 0.0077716 | 0.023071 | 0.0025975 | 0.0023498 | -0.0059216 | -0.0051377 | -0.0066479 | -0.0053149 | -0.52185 | -0.10529 | -1.2177 | -0.4303 | -0.36163 | -0.60883 | -0.32959 | 0.65918 | 121.8658 | -1.2543 | -0.39368 | -0.42572 | -1.0162 | -0.90179 | -0.045776 | -121.875 | -122.2 | 0.81024 | 0.84228 | 0.56305 | 0.88806 | 0.60883 | -0.082397 | 0.096131 | -122.1634 | 0.74616 | 0.27008 | 0.15564 | 0.35248 | 0.23804 | 0.85602 | 0.78735 | 0.82855 | 0.86059 | 1.1124 | 123.1201 | 1.0666 | 123.0377 | -122.9874 | -123.024 | 0.74158 | 0.7782 | 0.65002 | 1.8311
4716.1719 | 122.9324 | -1.1444 | 121.7697 | -0.068207 | -1.9142e-05 | 0.015456 | 0.0092307 | 0.0020828 | 0.0032599 | 0.0049946 | -0.0013428 | 0.0047339 | 0.00021363 | 0.0043322 | -0.0040695 | -0.0057935 | 0.0021619 | -0.48065 | -0.11902 | -1.2222 | -0.3891 | -0.33875 | -0.59967 | -0.32959 | 0.75531 | 121.8658 | -1.2177 | -0.35248 | -0.42572 | -1.0071 | -0.89264 | -0.07782 | -121.8887 | -122.1588 | 0.80566 | 0.81482 | 0.54474 | 0.89264 | 0.62256 | -0.073242 | 0.096131 | -122.1222 | 0.71869 | 0.25177 | 0.13733 | 0.32501 | 0.21057 | 0.88348 | 0.83313 | 0.79193 | 0.86517 | 1.1032 | 123.0835 | 1.0254 | 123.0103 | -122.9919 | -122.9874 | 0.75531 | 0.79193 | 0.66376 | 1.8997
4717.1719 | 122.8867 | -1.1444 | 121.8109 | -0.045319 | -0.0015145 | 0.015242 | 0.0070943 | 0.0020828 | 0.0045417 | 0.0022174 | 0.044434 | 0.0023839 | 0.001068 | -0.0086988 | -0.0012925 | -0.0087843 | -0.0012561 | -0.46234 | -0.14191 | -1.1581 | -0.3891 | -0.3067 | -0.54932 | -0.28381 | 0.7782 | 121.907 | -1.2177 | -0.37537 | -0.41657 | -0.98877 | -0.89722 | -0.013733 | -121.9528 | -122.2 | 0.83771 | 0.8606 | 0.59509 | 0.87433 | 0.60883 | -0.073242 | 0.09613 | -122.1863 | 0.72784 | 0.24719 | 0.15564 | 0.32043 | 0.22888 | 0.85144 | 0.76904 | 0.80109 | 0.84229 | 1.0162 | 123.1247 | 1.0025 | 123.0515 | -122.9691 | -123.0286 | 0.75531 | 0.76904 | 0.68207 | 1.9226
4718.1719 | 122.8729 | -1.1307 | 121.8475 | -0.11398 | -0.00044654 | 0.016524 | 0.0058127 | -0.001976 | -0.00058531 | 0.0028582 | 0.044434 | 0.0023839 | 0.001709 | -0.0018628 | -0.0021469 | -0.0081433 | 0.0013073 | -0.48981 | -0.11444 | -1.1627 | -0.4303 | -0.36163 | -0.60883 | -0.33875 | 0.75531 | 121.9482 | -1.2085 | -0.37537 | -0.41199 | -0.96588 | -0.89264 | -0.032044 | -121.962 | -122.2778 | 0.76904 | 0.79193 | 0.52185 | 0.82397 | 0.55389 | -0.07782 | 0.10071 | -122.2229 | 0.71869 | 0.23804 | 0.1648 | 0.31586 | 0.24262 | 0.80109 | 0.73242 | 0.79651 | 0.83313 | 1.0483 | 123.1567 | 1.0162 | 123.0789 | -123.0103 | -123.056 | 0.70038 | 0.75531 | 0.64087 | 1.886
4719.1719 | 122.9416 | -1.1032 | 121.8384 | -0.060578 | 0.00040806 | 0.014815 | 0.0085897 | 0.003151 | 0.0019781 | 0.0032856 | 0.0047608 | 0.0045203 | 0.00085443 | 0.0015552 | -0.0019333 | -0.0077161 | 0.0038709 | -0.47607 | -0.10986 | -1.1581 | -0.37994 | -0.33875 | -0.58136 | -0.32044 | 0.84228 | 121.9391 | -1.1948 | -0.28839 | -0.36163 | -0.9613 | -0.85144 | -0.054932 | -121.9482 | -122.2183 | 0.76446 | 0.78277 | 0.52185 | 0.83771 | 0.57678 | -0.091553 | 0.10071 | -122.1268 | 0.74158 | 0.25177 | 0.14191 | 0.34332 | 0.23346 | 0.8194 | 0.7782 | 0.83313 | 0.90637 | 1.0483 | 123.1338 | 0.99335 | 123.0423 | -122.9965 | -123.0331 | 0.72327 | 0.81482 | 0.62714 | 1.9455
4720.1719 | 122.8821 | -1.1261 | 121.843 | -0.045319 | 0.0012625 | 0.014174 | 0.0075217 | -0.003685 | 0.0015509 | 0.0043536 | 0.001709 | 0.0043065 | 0.0023498 | -0.0025036 | -0.0032151 | -0.0064343 | 0.0036571 | -0.50812 | -0.10529 | -1.149 | -0.43488 | -0.3891 | -0.6134 | -0.33875 | 0.78278 | 121.9391 | -1.1902 | -0.3479 | -0.38452 | -0.97504 | -0.86975 | -0.022888 | -121.9482 | -122.2778 | 0.737 | 0.78735 | 0.5127 | 0.81024 | 0.53558 | -0.064087 | 0.09613 | -122.1909 | 0.74158 | 0.25635 | 0.15106 | 0.32043 | 0.21515 | 0.75989 | 0.71411 | 0.80566 | 0.84229 | 1.0437 | 123.1293 | 1.0208 | 123.0652 | -122.9919 | -123.0331 | 0.69122 | 0.7782 | 0.61798 | 1.9089
4721.1719 | 122.8912 | -1.1169 | 121.8704 | -0.068207 | 0.00019446 | 0.016737 | 0.0062399 | -0.0060348 | 0.0026191 | 0.0017902 | 0.041382 | 0.0051611 | 0.0014954 | -0.0054944 | -0.0023605 | -0.0098523 | 2.554e-05 | -0.4715 | -0.12817 | -1.1398 | -0.40283 | -0.34332 | -0.59967 | -0.31586 | 0.80566 | 121.9437 | -1.1581 | -0.34332 | -0.37994 | -0.95673 | -0.88348 | -0.022889 | -121.9986 | -122.2733 | 0.77362 | 0.80109 | 0.51727 | 0.82397 | 0.54016 | -0.041199 | 0.073243 | -122.2137 | 0.737 | 0.23346 | 0.16022 | 0.27466 | 0.20142 | 0.79651 | 0.737 | 0.7782 | 0.81482 | 1.0117 | 123.1018 | 0.98877 | 123.0606 | -123.0103 | -123.0286 | 0.71411 | 0.77362 | 0.64545 | 1.9226
4722.1719 | 122.8867 | -1.0941 | 121.8704 | -0.03006 | 0.00040806 | 0.015456 | 0.0066671 | -0.0013352 | 0.0043281 | 0.0011494 | 0.044434 | 0.0025975 | -0.00064077 | -0.0065626 | -0.00043791 | -0.0057935 | -0.0027515 | -0.44861 | -0.14191 | -1.1169 | -0.37079 | -0.31128 | -0.53558 | -0.29297 | 0.86975 | 121.9299 | -1.1673 | -0.30212 | -0.33875 | -0.93384 | -0.85144 | -0.022888 | -122.0123 | -122.2412 | 0.78278 | 0.80109 | 0.55847 | 0.82397 | 0.58136 | -0.073242 | 0.05951 | -122.1725 | 0.75531 | 0.24262 | 0.16022 | 0.31586 | 0.23346 | 0.80566 | 0.74615 | 0.82855 | 0.86517 | 0.97504 | 123.0972 | 0.95215 | 123.024 | -122.9874 | -123.0377 | 0.72327 | 0.79193 | 0.64545 | 1.9638
4723.1719 | 123.0011 | -1.062 | 121.843 | -0.12161 | -0.00066014 | 0.014815 | 0.0073081 | 0.0022964 | 0.0021917 | -0.00013241 | 0.074951 | 0.0032385 | 0.0029906 | 0.00091422 | -0.0040695 | -0.0085705 | 0.00045294 | -0.4303 | -0.15106 | -1.1032 | -0.32044 | -0.23346 | -0.47607 | -0.21973 | 0.99335 | 121.9162 | -1.1307 | -0.21973 | -0.23804 | -0.82398 | -0.75073 | -0.041198 | -121.994 | -122.1634 | 0.82855 | 0.84228 | 0.58594 | 0.88348 | 0.62714 | -0.068664 | 0.073242 | -122.0627 | 0.82397 | 0.31128 | 0.23804 | 0.37994 | 0.3067 | 0.86975 | 0.78277 | 0.89264 | 0.91095 | 0.95215 | 123.0469 | 0.91095 | 122.9782 | -122.9462 | -122.9736 | 0.74158 | 0.84228 | 0.63171 | 2.0554
4724.1719 | 122.9141 | -1.0757 | 121.8796 | -0.022431 | 0.00083526 | 0.014815 | 0.0092307 | -0.00048063 | 0.0026191 | 0.0047808 | -0.037964 | 0.0034521 | -0.0010682 | 0.0028368 | -0.0038559 | -0.0051527 | 0.0036571 | -0.45319 | -0.10986 | -1.1444 | -0.38452 | -0.34332 | -0.56305 | -0.31586 | 0.87891 | 121.994 | -1.1673 | -0.25177 | -0.32044 | -0.92926 | -0.81482 | -0.068664 | -121.9894 | -122.2641 | 0.73242 | 0.75989 | 0.5127 | 0.82855 | 0.58136 | -0.091552 | 0.11444 | -122.1313 | 0.75531 | 0.26093 | 0.14648 | 0.35248 | 0.23804 | 0.80109 | 0.75989 | 0.84686 | 0.91553 | 1.0345 | 123.1613 | 0.96588 | 123.0698 | -123.024 | -123.0469 | 0.69122 | 0.82397 | 0.62256 | 1.9547
4725.1719 | 122.8821 | -1.1124 | 121.8842 | -0.083466 | -0.0019417 | 0.014601 | 0.0079489 | 0.00037377 | 0.0017645 | 0.0026446 | 0.010864 | 0.0038793 | 0.0029906 | 0.00027342 | -0.0025741 | -0.0079297 | 0.0021619 | -0.5127 | -0.10529 | -1.1536 | -0.4303 | -0.37537 | -0.59967 | -0.33417 | 0.82855 | 121.9757 | -1.1948 | -0.31128 | -0.34332 | -0.97504 | -0.8606 | -0.041198 | -121.9894 | -122.3145 | 0.737 | 0.7782 | 0.5127 | 0.8194 | 0.55389 | -0.082397 | 0.091553 | -122.1954 | 0.76904 | 0.25177 | 0.13733 | 0.33417 | 0.21973 | 0.7782 | 0.72327 | 0.85144 | 0.88348 | 1.0483 | 123.1705 | 1.0071 | 123.0881 | -123.0377 | -123.0789 | 0.68207 | 0.80109 | 0.59967 | 1.9409
4726.1719 | 122.8729 | -1.0895 | 121.875 | -0.098725 | 0.0012625 | 0.01396 | 0.012649 | -0.001976 | 0.0028327 | 0.0015766 | -0.056274 | 0.0060155 | 0.00085443 | 0.0024096 | -0.0040695 | -0.0045117 | -0.0010425 | -0.4715 | -0.1236 | -1.1169 | -0.43488 | -0.37994 | -0.62256 | -0.36621 | 0.85602 | 121.9849 | -1.1627 | -0.2655 | -0.35248 | -0.98877 | -0.83771 | -0.027465 | -121.9986 | -122.3099 | 0.70953 | 0.72327 | 0.46692 | 0.75073 | 0.49438 | -0.073242 | 0.10986 | -122.1405 | 0.737 | 0.25177 | 0.10071 | 0.32501 | 0.17395 | 0.737 | 0.68207 | 0.81024 | 0.89722 | 0.99335 | 123.1476 | 0.96588 | 123.0743 | -122.9919 | -123.0377 | 0.6546 | 0.82397 | 0.61798 | 1.9455
4727.1719 | 122.9599 | -1.0574 | 121.8658 | -0.098725 | -0.00044654 | 0.015242 | 0.0060263 | -0.0013352 | 0.00069649 | 0.0037128 | 0.074951 | 0.0036657 | 0.00085443 | -0.00015378 | -0.0040695 | -0.0072889 | -0.0016833 | -0.40741 | -0.14648 | -1.0757 | -0.32501 | -0.26093 | -0.4715 | -0.25177 | 0.99335 | 121.9574 | -1.1307 | -0.16937 | -0.20599 | -0.82398 | -0.74158 | -0.018311 | -122.0123 | -122.1909 | 0.79651 | 0.80566 | 0.58594 | 0.82397 | 0.60425 | -0.073242 | 0.091552 | -122.0352 | 0.85144 | 0.31586 | 0.23346 | 0.3891 | 0.3067 | 0.81482 | 0.75073 | 0.92468 | 0.9613 | 0.92926 | 123.0881 | 0.91095 | 123.0148 | -122.9416 | -122.9965 | 0.73242 | 0.88806 | 0.65002 | 2.0508
4728.1719 | 122.8821 | -1.0757 | 121.9299 | -0.03006 | -1.9142e-05 | 0.015028 | 0.0070943 | -0.0041122 | 0.0019781 | 0.00029479 | 0.010864 | 0.0032385 | 0.001068 | -0.002931 | -0.00043791 | -0.0087843 | 0.0015209 | -0.48523 | -0.09613 | -1.0986 | -0.4303 | -0.37079 | -0.57678 | -0.33417 | 0.88348 | 122.0169 | -1.149 | -0.23346 | -0.27008 | -0.90637 | -0.82398 | -0.022888 | -122.0261 | -122.3602 | 0.70496 | 0.74158 | 0.49896 | 0.76447 | 0.52185 | -0.073242 | 0.086975 | -122.1634 | 0.80566 | 0.25177 | 0.16937 | 0.32501 | 0.24262 | 0.72784 | 0.66833 | 0.87891 | 0.91553 | 1.0025 | 123.1659 | 0.97961 | 123.0927 | -123.0286 | -123.0789 | 0.64545 | 0.84229 | 0.59052 | 1.9592
4729.1719 | 122.9919 | -1.0254 | 121.875 | -0.075836 | 0.00040806 | 0.016951 | 0.0051717 | 0.0052872 | -0.00015811 | 0.0047808 | 0.056641 | 0.0034521 | 0.001068 | -0.0031446 | -0.0021469 | -0.0068615 | 0.00066654 | -0.41199 | -0.14191 | -1.0712 | -0.30212 | -0.24261 | -0.45319 | -0.2243 | 1.0345 | 121.9666 | -1.1032 | -0.11902 | -0.16937 | -0.77362 | -0.70496 | -0.045776 | -122.0169 | -122.1771 | 0.78278 | 0.80109 | 0.5722 | 0.84686 | 0.61798 | -0.077819 | 0.091553 | -121.994 | 0.85602 | 0.32043 | 0.25177 | 0.39825 | 0.32959 | 0.82855 | 0.76904 | 0.93384 | 0.98419 | 0.92926 | 123.0698 | 0.88348 | 122.9919 | -122.9462 | -122.9782 | 0.72327 | 0.90637 | 0.6134 | 2.0599
4730.1719 | 123.0057 | -1.0117 | 121.8933 | -0.022431 | -0.00023294 | 0.017378 | 0.0077353 | -0.0011214 | 0.00026909 | 0.003072 | 0.047485 | 0.0036657 | 2.8e-08 | 0.0015552 | -0.0036423 | -0.0072889 | -0.0023243 | -0.42114 | -0.14191 | -1.0666 | -0.29755 | -0.23804 | -0.45776 | -0.21515 | 1.0574 | 121.994 | -1.0849 | -0.086975 | -0.1236 | -0.737 | -0.66834 | -0.054931 | -122.0352 | -122.1909 | 0.77362 | 0.79651 | 0.55389 | 0.85144 | 0.60882 | -0.073242 | 0.10071 | -121.9803 | 0.88806 | 0.34332 | 0.27466 | 0.41656 | 0.3479 | 0.82855 | 0.76904 | 0.9613 | 0.99792 | 0.92468 | 123.0789 | 0.86975 | 123.0057 | -122.9599 | -122.9782 | 0.71411 | 0.92468 | 0.59051 | 2.0691
4731.1719 | 122.9141 | -1.0117 | 121.962 | -0.091095 | -0.00066014 | 0.015242 | 0.0083761 | -5.343e-05 | 0.0011237 | 0.0020038 | -0.022705 | 0.0058019 | 0.0025634 | -0.00036738 | -0.0047103 | -0.0057935 | -0.00082886 | -0.45319 | -0.09613 | -1.0803 | -0.41657 | -0.38452 | -0.56305 | -0.33875 | 0.90637 | 122.0398 | -1.1124 | -0.16937 | -0.21515 | -0.85602 | -0.75531 | -0.068664 | -122.0581 | -122.3785 | 0.62714 | 0.67291 | 0.44861 | 0.74158 | 0.51727 | -0.10071 | 0.07782 | -122.1313 | 0.79651 | 0.25635 | 0.15564 | 0.35706 | 0.25635 | 0.6958 | 0.66376 | 0.89722 | 0.94299 | 0.98419 | 123.1522 | 0.91553 | 123.0515 | -123.0423 | -123.0743 | 0.59509 | 0.84228 | 0.55847 | 1.918
4732.1719 | 122.9919 | -0.98419 | 121.9345 | -0.091095 | 0.00019446 | 0.015242 | 0.0064535 | -0.0032578 | 0.0026191 | 0.0032856 | 0.023071 | 0.0034521 | 0.001709 | -0.0016492 | -0.0017197 | -0.0083569 | -0.00040166 | -0.41199 | -0.1236 | -1.0162 | -0.31128 | -0.24719 | -0.43488 | -0.23804 | 1.0849 | 122.0123 | -1.0529 | -0.068665 | -0.11444 | -0.75073 | -0.67749 | -0.032043 | -122.0581 | -122.2458 | 0.737 | 0.74615 | 0.54932 | 0.7782 | 0.58136 | -0.068664 | 0.07782 | -122.0032 | 0.86975 | 0.3067 | 0.23346 | 0.37537 | 0.30212 | 0.76904 | 0.70496 | 0.93841 | 0.98419 | 0.89264 | 123.0652 | 0.8606 | 122.9965 | -122.9507 | -122.9874 | 0.67291 | 0.91553 | 0.5722 | 2.0691
4733.1719 | 122.8821 | -1.0208 | 121.9574 | -0.03006 | -0.00044654 | 0.014601 | 0.0083761 | 0.0022964 | 0.00069649 | 0.002431 | -0.022705 | 0.0064429 | 0.0023498 | -0.0044262 | -0.0036423 | -0.0081433 | 0.0023755 | -0.46692 | -0.10986 | -1.0849 | -0.41657 | -0.37994 | -0.5722 | -0.31586 | 0.94299 | 122.0581 | -1.1169 | -0.16479 | -0.20599 | -0.86517 | -0.78278 | -0.064087 | -122.0673 | -122.374 | 0.64087 | 0.70496 | 0.44861 | 0.76904 | 0.5127 | -0.09613 | 0.10071 | -122.1222 | 0.81482 | 0.23804 | 0.15564 | 0.33417 | 0.25177 | 0.70496 | 0.66833 | 0.91095 | 0.95215 | 0.97504 | 123.175 | 0.91095 | 123.0789 | -123.0423 | -123.0743 | 0.60425 | 0.85602 | 0.55389 | 1.9638
4734.1719 | 122.8912 | -1.0208 | 121.9574 | -0.075836 | -0.00066014 | 0.016096 | 0.0085897 | 0.001442 | 0.0021917 | 0.0052082 | 0.013916 | 0.0060155 | -0.00021357 | 0.0015552 | -0.0036423 | -0.0079297 | 0.0013073 | -0.42114 | -0.11444 | -1.03 | -0.40283 | -0.33875 | -0.55389 | -0.30212 | 0.99792 | 122.0352 | -1.0941 | -0.14191 | -0.19684 | -0.84228 | -0.76904 | -0.009155 | -122.0718 | -122.3602 | 0.68207 | 0.71869 | 0.46692 | 0.72784 | 0.47607 | -0.073242 | 0.07782 | -122.0993 | 0.82397 | 0.25177 | 0.17853 | 0.32501 | 0.25177 | 0.69122 | 0.62714 | 0.89722 | 0.95215 | 0.91553 | 123.1293 | 0.90637 | 123.056 | -122.9874 | -123.0515 | 0.61798 | 0.87891 | 0.59967 | 2.0187
4735.1719 | 122.9782 | -0.97961 | 121.9208 | -0.068207 | 0.00040806 | 0.015669 | 0.0058127 | 0.0033646 | 0.0017645 | 0.0022174 | 0.047485 | 0.0036657 | 2.8e-08 | -0.0052808 | -0.0044967 | -0.0068615 | -0.0010425 | -0.40283 | -0.14648 | -1.0254 | -0.29297 | -0.21057 | -0.43945 | -0.19226 | 1.1902 | 122.0306 | -1.0666 | -0.027466 | -0.07782 | -0.72327 | -0.66376 | -0.045777 | -122.0673 | -122.2137 | 0.76904 | 0.78735 | 0.54016 | 0.83313 | 0.58594 | -0.086975 | 0.10986 | -121.9482 | 0.90179 | 0.31586 | 0.25635 | 0.40283 | 0.34332 | 0.81482 | 0.73242 | 0.98877 | 1.0391 | 0.87891 | 123.0972 | 0.83313 | 123.0103 | -122.9462 | -122.9874 | 0.68664 | 0.95215 | 0.57678 | 2.1698
4736.1719 | 122.9095 | -0.98877 | 121.9757 | -0.12161 | 0.0012625 | 0.016737 | 0.01094 | 0.00251 | 0.0039007 | 0.002431 | -0.080688 | 0.0043065 | 0.0025634 | 0.0045458 | -0.0040695 | -0.0064343 | -0.00061526 | -0.43488 | -0.1236 | -1.0437 | -0.37079 | -0.3479 | -0.54016 | -0.32044 | 1.0666 | 122.0535 | -1.0849 | -0.07782 | -0.18768 | -0.85602 | -0.73242 | -0.054931 | -122.0993 | -122.3465 | 0.64087 | 0.66834 | 0.44861 | 0.72327 | 0.50354 | -0.09613 | 0.07782 | -122.0535 | 0.80109 | 0.25635 | 0.13275 | 0.35248 | 0.22888 | 0.6958 | 0.67291 | 0.89722 | 1.0071 | 0.9201 | 123.1384 | 0.86517 | 123.0423 | -123.0194 | -123.0606 | 0.61798 | 0.91095 | 0.5539 | 2.0554
4737.1719 | 122.9599 | -0.98877 | 121.9437 | -0.083466 | 0.0012625 | 0.01396 | 0.0079489 | -0.0028304 | 0.0019781 | 0.0017902 | 0.02002 | 0.0051611 | 0.0023498 | -0.00079478 | -0.0025741 | -0.0075025 | -0.0042469 | -0.45319 | -0.12817 | -1.0025 | -0.36621 | -0.31128 | -0.5127 | -0.27466 | 1.0941 | 122.049 | -1.0849 | -0.013733 | -0.09613 | -0.75531 | -0.66834 | -0.013732 | -122.0718 | -122.3099 | 0.67749 | 0.71411 | 0.47608 | 0.72784 | 0.48981 | -0.09613 | 0.10529 | -121.9574 | 0.89264 | 0.32044 | 0.23346 | 0.41656 | 0.32959 | 0.69122 | 0.63629 | 0.98877 | 1.0712 | 0.87433 | 123.1339 | 0.8606 | 123.0377 | -122.9462 | -123.0286 | 0.62256 | 0.97504 | 0.53558 | 2.0828
4738.1719 | 122.9782 | -0.9613 | 121.9574 | -0.083466 | -0.0015145 | 0.016737 | 0.0081625 | -0.001976 | 0.0017645 | 0.0056354 | 0.03833 | 0.0038793 | 0.00085443 | 0.0043322 | -0.0030013 | -0.0062207 | 0.0032299 | -0.44403 | -0.11902 | -1.0345 | -0.37079 | -0.31128 | -0.49439 | -0.27466 | 1.1307 | 122.049 | -1.0712 | -0.004578 | -0.082397 | -0.74616 | -0.66834 | -0.073242 | -122.0764 | -122.3282 | 0.65003 | 0.68665 | 0.46692 | 0.75989 | 0.54016 | -0.10986 | 0.091553 | -121.962 | 0.87891 | 0.29297 | 0.21515 | 0.40283 | 0.32501 | 0.72327 | 0.66376 | 0.98877 | 1.0666 | 0.91553 | 123.1201 | 0.84229 | 123.0103 | -122.9919 | -123.0286 | 0.59052 | 0.95673 | 0.51727 | 2.092
4739.1719 | 123.0103 | -0.95215 | 121.9574 | -0.045319 | 0.00019446 | 0.016951 | 0.0075217 | 0.0012284 | 0.0032599 | 0.0022174 | 0.032227 | 0.0072973 | -0.00042717 | -0.00015378 | -0.0042831 | -0.0047253 | -0.0016833 | -0.37537 | -0.14191 | -1.0208 | -0.29755 | -0.22888 | -0.4303 | -0.21057 | 1.2039 | 122.0352 | -1.0483 | 0.032043 | -0.027466 | -0.67749 | -0.63629 | -0.068665 | -122.0993 | -122.2549 | 0.72327 | 0.74158 | 0.52185 | 0.81024 | 0.59051 | -0.096131 | 0.07782 | -121.9254 | 0.92468 | 0.31586 | 0.27466 | 0.41199 | 0.37079 | 0.79193 | 0.72327 | 1.0208 | 1.0803 | 0.87891 | 123.0835 | 0.81024 | 122.9874 | -122.9782 | -123.0057 | 0.6546 | 0.98419 | 0.57678 | 2.1561
4740.1719 | 122.9874 | -0.95215 | 121.9803 | -0.083466 | -0.0013009 | 0.01631 | 0.0092307 | -0.0041122 | 0.0028327 | 0.0043536 | 0.044434 | 0.0055883 | 0.00064083 | -0.0014356 | -0.0027877 | -0.0064343 | -0.0016833 | -0.38452 | -0.14191 | -1.0071 | -0.27924 | -0.21973 | -0.40741 | -0.19226 | 1.2177 | 122.0398 | -1.0391 | 0.054932 | -0.009155 | -0.66834 | -0.6134 | -0.054932 | -122.1222 | -122.2595 | 0.73242 | 0.75989 | 0.54474 | 0.81482 | 0.59967 | -0.086976 | 0.059509 | -121.9254 | 0.94299 | 0.33874 | 0.28381 | 0.42572 | 0.37079 | 0.78735 | 0.72784 | 1.03 | 1.0941 | 0.86517 | 123.0789 | 0.81024 | 122.9919 | -122.9874 | -123.0194 | 0.67291 | 1.0071 | 0.56763 | 2.1698
4741.1719 | 122.8912 | -0.99335 | 122.0078 | -0.060578 | 0.0014761 | 0.017805 | 0.0092307 | -0.0011214 | 0.0021917 | 0.00072199 | -0.03186 | 0.0064429 | 0.00064083 | -0.00015378 | -0.0030013 | -0.0057935 | -0.00082886 | -0.44861 | -0.10071 | -1.0483 | -0.42114 | -0.3891 | -0.53101 | -0.33417 | 1.0757 | 122.0993 | -1.062 | -0.036621 | -0.13733 | -0.80566 | -0.71411 | -0.054932 | -122.1085 | -122.4289 | 0.60425 | 0.65918 | 0.46234 | 0.71411 | 0.51727 | -0.068665 | 0.091553 | -122.0444 | 0.85602 | 0.27924 | 0.18768 | 0.3479 | 0.25635 | 0.65918 | 0.62714 | 0.92468 | 1.0254 | 0.94757 | 123.1613 | 0.89264 | 123.0927 | -123.056 | -123.0698 | 0.5722 | 0.95673 | 0.54474 | 2.0691
4742.1719 | 122.9874 | -0.94757 | 121.9574 | -0.083466 | -0.0015145 | 0.015028 | 0.0070943 | 0.00016017 | 0.0024053 | 0.0047808 | 0.013916 | 0.0040929 | 0.0012818 | -0.00229 | -0.00065151 | -0.0081433 | 0.0028027 | -0.41657 | -0.12817 | -1.0025 | -0.34332 | -0.29755 | -0.48523 | -0.25177 | 1.1856 | 122.0535 | -1.0574 | 0.045776 | -0.018311 | -0.6958 | -0.61798 | -0.054931 | -122.0856 | -122.3007 | 0.65003 | 0.6958 | 0.46234 | 0.75073 | 0.51727 | -0.10986 | 0.096131 | -121.9116 | 0.92926 | 0.32959 | 0.25177 | 0.43945 | 0.36163 | 0.70496 | 0.65918 | 1.0391 | 1.1032 | 0.87433 | 123.111 | 0.8194 | 123.0011 | -122.9599 | -123.0148 | 0.60425 | 0.99335 | 0.53101 | 2.1332
4743.1719 | 123.0469 | -0.96588 | 121.9574 | -0.075836 | -0.0013009 | 0.015669 | 0.0077353 | 0.0016556 | 0.0015509 | 0.0037128 | 0.056641 | 0.0055883 | 0.0014954 | 0.0017688 | -0.0021469 | -0.0070753 | 0.00045294 | -0.37994 | -0.12817 | -1.0117 | -0.28839 | -0.21057 | -0.40283 | -0.21515 | 1.3046 | 122.0535 | -1.0391 | 0.054932 | 0.027466 | -0.65918 | -0.6134 | -0.045777 | -122.0856 | -122.2458 | 0.75531 | 0.75073 | 0.56305 | 0.79651 | 0.60883 | -0.073243 | 0.096131 | -121.9025 | 0.99335 | 0.35248 | 0.3067 | 0.42572 | 0.37994 | 0.80109 | 0.72327 | 1.0666 | 1.0941 | 0.88348 | 123.0927 | 0.83771 | 123.0194 | -122.9691 | -122.9965 | 0.67749 | 1.0208 | 0.58594 | 2.2705
4744.1719 | 122.9462 | -0.97046 | 121.9849 | -0.11398 | 0.0012625 | 0.016524 | 0.0070943 | -0.0015488 | 0.0015509 | 0.001363 | -0.01355 | 0.0055883 | 0.0025634 | -0.0016492 | -0.0042831 | -0.0085705 | -0.00061526 | -0.37537 | -0.14191 | -1.0025 | -0.31586 | -0.27008 | -0.4303 | -0.24261 | 1.2405 | 122.0352 | -1.0437 | 0.022888 | -0.004578 | -0.68207 | -0.64545 | -0.032043 | -122.1268 | -122.3007 | 0.70038 | 0.72784 | 0.54016 | 0.75989 | 0.5722 | -0.073242 | 0.050354 | -121.962 | 0.96588 | 0.32501 | 0.28839 | 0.39825 | 0.36163 | 0.73242 | 0.68664 | 1.0391 | 1.0666 | 0.86059 | 123.0789 | 0.82855 | 123.0057 | -122.9874 | -123.0286 | 0.6546 | 0.99335 | 0.59509 | 2.211
4745.1719 | 122.9782 | -0.9201 | 121.9711 | -0.10635 | -0.00023294 | 0.01631 | 0.0098715 | -0.0021896 | 0.0015509 | 0.00029479 | -0.016602 | 0.0075109 | -0.00064077 | -0.0035718 | -0.0032151 | -0.0072889 | -0.00061526 | -0.38452 | -0.14648 | -0.99792 | -0.31586 | -0.25177 | -0.48065 | -0.24719 | 1.2405 | 122.0718 | -1.0208 | 0.082397 | 0.009155 | -0.68665 | -0.62256 | -0.07782 | -122.1176 | -122.287 | 0.66833 | 0.67291 | 0.43945 | 0.75073 | 0.51727 | -0.10071 | 0.10071 | -121.8887 | 0.92926 | 0.29755 | 0.23346 | 0.39825 | 0.33417 | 0.74615 | 0.68207 | 1.03 | 1.1032 | 0.85144 | 123.0927 | 0.77362 | 122.9919 | -122.9691 | -122.9919 | 0.60425 | 1.0025 | 0.53558 | 2.1606
4746.1719 | 122.9691 | -0.92926 | 121.9757 | -0.15976 | -0.0034371 | 0.014387 | 0.0068807 | 0.00251 | 0.0024053 | 0.0022174 | 0.001709 | 0.0045203 | 2.8e-08 | -0.00464 | -0.0025741 | -0.0070753 | -0.0018971 | -0.42572 | -0.13733 | -0.99792 | -0.34332 | -0.32501 | -0.48065 | -0.25635 | 1.2131 | 122.1085 | -1.0254 | 0.07782 | 0.041199 | -0.67291 | -0.62256 | -0.068665 | -122.113 | -122.319 | 0.60425 | 0.67291 | 0.44861 | 0.74158 | 0.51727 | -0.096131 | 0.13275 | -121.8979 | 0.97046 | 0.3067 | 0.25635 | 0.40283 | 0.35248 | 0.67291 | 0.6546 | 1.0666 | 1.1032 | 0.8606 | 123.1338 | 0.79193 | 123.0377 | -122.9736 | -123.0011 | 0.58594 | 1.0071 | 0.50354 | 2.1423
4747.1719 | 122.9645 | -0.91553 | 122.0123 | -0.083466 | -0.0010873 | 0.016951 | 0.0083761 | 0.0027238 | 0.00091009 | 0.00414 | -0.01355 | 0.0055883 | 0.0019226 | 0.0024096 | -0.0047103 | -0.0083569 | 0.0036571 | -0.40741 | -0.12817 | -0.94299 | -0.3479 | -0.32044 | -0.48065 | -0.27466 | 1.2131 | 122.1222 | -1.0071 | 0.10529 | 0.045776 | -0.69122 | -0.60425 | -0.027466 | -122.1405 | -122.3602 | 0.59509 | 0.64087 | 0.43487 | 0.66833 | 0.46234 | -0.091553 | 0.10986 | -121.907 | 0.9613 | 0.31128 | 0.2243 | 0.40283 | 0.31586 | 0.62256 | 0.59509 | 1.0529 | 1.1124 | 0.81482 | 123.1293 | 0.78735 | 123.0377 | -122.9553 | -123.0194 | 0.56763 | 1.0208 | 0.50812 | 2.1286
4748.1719 | 122.9782 | -0.90179 | 122.0215 | -0.11398 | -1.9142e-05 | 0.017165 | 0.0070943 | -0.0017624 | 0.0030463 | 0.001363 | 0.0078126 | 0.0040929 | 0.0019226 | 0.0017688 | -0.0044967 | -0.0077161 | 0.0032299 | -0.41657 | -0.14191 | -0.9613 | -0.33417 | -0.3067 | -0.46234 | -0.25635 | 1.268 | 122.1085 | -0.99792 | 0.15106 | 0.059509 | -0.63629 | -0.56763 | -0.05951 | -122.1634 | -122.3557 | 0.59509 | 0.64545 | 0.43945 | 0.70496 | 0.49896 | -0.096131 | 0.086975 | -121.8704 | 0.9613 | 0.33417 | 0.2655 | 0.4303 | 0.36163 | 0.6546 | 0.62714 | 1.0574 | 1.149 | 0.8194 | 123.1064 | 0.75989 | 123.0103 | -122.9828 | -123.0194 | 0.56763 | 1.0529 | 0.48523 | 2.1698
4749.1719 | 123.0011 | -0.89264 | 122.0078 | -0.091095 | -0.0010873 | 0.018233 | 0.0081625 | 0.0012284 | 0.0032599 | 0.0022174 | -0.0043946 | 0.0062291 | 0.0014954 | -0.0020764 | -0.0030013 | -0.0064343 | -0.0010425 | -0.36621 | -0.14191 | -0.94299 | -0.29297 | -0.24261 | -0.40283 | -0.2243 | 1.3458 | 122.1085 | -0.97961 | 0.16022 | 0.10986 | -0.58594 | -0.54016 | -0.050354 | -122.1497 | -122.3007 | 0.65002 | 0.66833 | 0.48981 | 0.71869 | 0.54016 | -0.086975 | 0.10071 | -121.8475 | 1.0025 | 0.35248 | 0.3067 | 0.43945 | 0.39368 | 0.70038 | 0.65002 | 1.0895 | 1.1398 | 0.80109 | 123.0881 | 0.75073 | 123.0011 | -122.9507 | -122.9874 | 0.59967 | 1.0529 | 0.52643 | 2.2385
4750.1719 | 122.9645 | -0.89722 | 122.0398 | -0.098725 | -0.0019417 | 0.020155 | 0.0088033 | -0.00069423 | 0.00091009 | 0.00072199 | -0.016602 | 0.0047339 | 0.0012818 | -0.0020764 | -0.0015061 | -0.0075025 | -0.0014697 | -0.39825 | -0.15564 | -0.95673 | -0.33875 | -0.29755 | -0.48065 | -0.27008 | 1.2726 | 122.1176 | -0.98877 | 0.14191 | 0.054932 | -0.62714 | -0.56763 | -0.059509 | -122.1954 | -122.3785 | 0.59967 | 0.62714 | 0.41657 | 0.68664 | 0.47607 | -0.091553 | 0.07782 | -121.8979 | 0.95215 | 0.32959 | 0.27008 | 0.42114 | 0.36163 | 0.65918 | 0.61798 | 1.0437 | 1.1307 | 0.80109 | 123.1064 | 0.74158 | 123.0148 | -122.9965 | -123.0286 | 0.55847 | 1.0391 | 0.49896 | 2.1698
4751.1719 | 123.0011 | -0.90637 | 121.9986 | -0.083466 | -0.00066014 | 0.017805 | 0.0085897 | 0.0018692 | 0.0039007 | 0.0028582 | -0.037964 | 0.0060155 | 0.0014954 | 0.0032642 | -0.0032151 | -0.0047253 | -0.00082886 | -0.36163 | -0.13275 | -0.9613 | -0.29297 | -0.25177 | -0.44403 | -0.23346 | 1.3458 | 122.0947 | -1.0025 | 0.21057 | 0.07782 | -0.60883 | -0.56305 | -0.054932 | -122.1313 | -122.2916 | 0.6546 | 0.67291 | 0.46234 | 0.72785 | 0.51727 | -0.09613 | 0.096131 | -121.788 | 0.98419 | 0.34332 | 0.29755 | 0.43945 | 0.39368 | 0.70953 | 0.66834 | 1.0803 | 1.2131 | 0.82855 | 123.0972 | 0.77362 | 123.0011 | -122.9599 | -123.0011 | 0.6134 | 1.1169 | 0.54474 | 2.2522
4752.1719 | 122.9736 | -0.92926 | 122.0169 | -0.11398 | 0.00019446 | 0.019728 | 0.0075217 | 0.0012284 | 0.0021917 | 0.0054218 | -0.010498 | 0.0077245 | 0.0021362 | -0.0050672 | -0.0030013 | -0.0057935 | -0.00018806 | -0.37537 | -0.15564 | -0.97046 | -0.31128 | -0.26093 | -0.46234 | -0.25635 | 1.3504 | 122.1268 | -0.98419 | 0.19684 | 0.073242 | -0.62256 | -0.56305 | -0.041199 | -122.1725 | -122.3282 | 0.66833 | 0.67291 | 0.46692 | 0.71411 | 0.50812 | -0.054932 | 0.10986 | -121.8201 | 1.0025 | 0.36621 | 0.3067 | 0.42114 | 0.36163 | 0.70953 | 0.65918 | 1.0574 | 1.181 | 0.81482 | 123.111 | 0.77362 | 123.056 | -122.9874 | -123.0011 | 0.61798 | 1.1261 | 0.55389 | 2.2797
4753.1719 | 122.9691 | -0.89722 | 122.0123 | -0.12161 | -0.00066014 | 0.017378 | 0.0077353 | 0.00058737 | 0.0030463 | 0.0020038 | 0.0078126 | 0.0072973 | 0.0019226 | -0.0033582 | -0.0032151 | -0.0066479 | 0.00066654 | -0.40741 | -0.1236 | -0.97046 | -0.34332 | -0.30212 | -0.45776 | -0.25177 | 1.3138 | 122.1313 | -0.99792 | 0.1831 | 0.082397 | -0.60425 | -0.56305 | -0.073242 | -122.1359 | -122.3557 | 0.59509 | 0.64545 | 0.43945 | 0.71869 | 0.51269 | -0.10071 | 0.11902 | -121.8292 | 0.97961 | 0.33417 | 0.29297 | 0.43488 | 0.39368 | 0.66833 | 0.62714 | 1.0803 | 1.181 | 0.84686 | 123.1293 | 0.77362 | 123.0286 | -122.9828 | -123.0103 | 0.55389 | 1.0803 | 0.48981 | 2.211
4754.1719 | 123.0103 | -0.89264 | 122.0123 | -0.098725 | 0.0010489 | 0.017805 | 0.0077353 | -0.0013352 | 0.0011237 | 0.0064898 | 0.013916 | 0.0058019 | 0.003418 | 0.00070062 | -0.0034287 | -0.0047253 | 0.0023755 | -0.37079 | -0.13275 | -0.94299 | -0.29755 | -0.23346 | -0.3891 | -0.21515 | 1.4191 | 122.113 | -0.98419 | 0.27924 | 0.16937 | -0.52185 | -0.52185 | -0.050354 | -122.1451 | -122.3099 | 0.65918 | 0.67749 | 0.50354 | 0.72784 | 0.55389 | -0.091553 | 0.10071 | -121.7331 | 1.062 | 0.37079 | 0.37079 | 0.46234 | 0.46234 | 0.70953 | 0.64545 | 1.1536 | 1.2634 | 0.81024 | 123.0972 | 0.75989 | 123.0057 | -122.9553 | -122.9965 | 0.59509 | 1.1719 | 0.52185 | 2.3117
4755.1719 | 122.9691 | -0.91553 | 122.0078 | -0.098725 | -1.9142e-05 | 0.017592 | 0.0077353 | 0.004219 | 0.00091009 | 0.0043536 | -0.028809 | 0.0068701 | 0.0025634 | -0.0033582 | -0.0027877 | -0.0075025 | 0.0025891 | -0.38452 | -0.13733 | -0.9613 | -0.32501 | -0.2655 | -0.4715 | -0.24719 | 1.3824 | 122.113 | -0.99335 | 0.23346 | 0.07782 | -0.59052 | -0.57678 | -0.045777 | -122.1451 | -122.3328 | 0.65002 | 0.66834 | 0.44403 | 0.71411 | 0.48981 | -0.07782 | 0.10529 | -121.7743 | 0.99335 | 0.33874 | 0.32501 | 0.41656 | 0.40283 | 0.6958 | 0.63629 | 1.0712 | 1.2268 | 0.82398 | 123.1064 | 0.7782 | 123.0286 | -122.9691 | -123.0011 | 0.59051 | 1.149 | 0.53101 | 2.298
4756.1719 | 122.9599 | -0.90637 | 122.0169 | -0.13687 | 0.00083526 | 0.01866 | 0.0085897 | 0.0029374 | -0.00015811 | 0.0032856 | -0.0074462 | 0.0087927 | 0.00064083 | -0.00229 | -0.0040695 | -0.0034437 | 0.0025891 | -0.41657 | -0.13275 | -0.96588 | -0.3479 | -0.31586 | -0.47607 | -0.28381 | 1.355 | 122.113 | -0.97961 | 0.2243 | 0.086975 | -0.59052 | -0.57678 | -0.059509 | -122.1497 | -122.3648 | 0.59051 | 0.62256 | 0.4303 | 0.68207 | 0.48981 | -0.073242 | 0.09613 | -121.7926 | 0.99335 | 0.32959 | 0.31586 | 0.40283 | 0.3891 | 0.65002 | 0.61798 | 1.0666 | 1.2039 | 0.83313 | 123.0927 | 0.77362 | 123.0194 | -122.9828 | -122.9965 | 0.55847 | 1.1307 | 0.48981 | 2.2614
4757.1719 | 122.9462 | -0.9201 | 122.0078 | -0.052948 | -0.0021555 | 0.019087 | 0.0096579 | -0.001976 | 0.0021917 | -0.00077341 | -0.0043946 | 0.0066565 | 0.00085443 | 0.0034778 | -0.0030013 | -0.0057935 | 0.0038709 | -0.40741 | -0.11444 | -0.97046 | -0.35248 | -0.31586 | -0.45776 | -0.26093 | 1.3412 | 122.1313 | -0.99792 | 0.24261 | 0.13733 | -0.56763 | -0.55847 | -0.050354 | -122.1222 | -122.3602 | 0.60425 | 0.65918 | 0.46234 | 0.70953 | 0.51269 | -0.07782 | 0.1236 | -121.7651 | 1.0574 | 0.36163 | 0.35248 | 0.43945 | 0.4303 | 0.6546 | 0.61798 | 1.1353 | 1.2405 | 0.85602 | 123.1293 | 0.80566 | 123.0515 | -122.9782 | -123.0057 | 0.56763 | 1.1627 | 0.51269 | 2.2614
4758.1719 | 123.0194 | -0.88806 | 121.9986 | -0.10635 | 0.0010489 | 0.018233 | 0.0088033 | -0.00048063 | 0.0028327 | 0.002431 | -0.062378 | 0.0081517 | 0.00085443 | -0.0037854 | -0.0032151 | -0.0057935 | -0.0038197 | -0.34332 | -0.15106 | -0.96588 | -0.29755 | -0.27466 | -0.44403 | -0.25177 | 1.4694 | 122.081 | -1.0025 | 0.32959 | 0.16479 | -0.54016 | -0.52185 | -0.077819 | -122.1497 | -122.2961 | 0.6134 | 0.63629 | 0.44403 | 0.71411 | 0.52185 | -0.11444 | 0.082398 | -121.669 | 1.0529 | 0.36621 | 0.3479 | 0.48065 | 0.46234 | 0.69122 | 0.66834 | 1.1673 | 1.3321 | 0.81482 | 123.0835 | 0.737 | 122.9691 | -122.9645 | -123.0011 | 0.59052 | 1.2177 | 0.54474 | 2.3575
4759.1719 | 123.0103 | -0.90637 | 122.0169 | -0.11398 | -0.00066014 | 0.018233 | 0.0062399 | -0.0011214 | 0.0028327 | 0.003072 | 0.0078126 | 0.0070837 | -0.00021357 | -0.0061352 | -0.0027877 | -0.0068615 | 2.554e-05 | -0.40741 | -0.12817 | -0.9613 | -0.32959 | -0.29297 | -0.43488 | -0.25635 | 1.4191 | 122.1313 | -0.97961 | 0.29297 | 0.16022 | -0.53558 | -0.53558 | -0.054932 | -122.1451 | -122.3465 | 0.6134 | 0.65002 | 0.4715 | 0.70496 | 0.52643 | -0.073242 | 0.11444 | -121.7239 | 1.0666 | 0.37079 | 0.37079 | 0.44403 | 0.44403 | 0.66834 | 0.63171 | 1.1398 | 1.2726 | 0.83313 | 123.111 | 0.7782 | 123.0377 | -122.9782 | -122.9965 | 0.57678 | 1.1993 | 0.49896 | 2.3254
4760.1719 | 122.9691 | -0.88806 | 122.0078 | -0.083466 | 0.00019446 | 0.017378 | 0.0098715 | -5.343e-05 | 0.00026909 | 0.0037128 | -0.028809 | 0.0085791 | 0.001068 | -0.0025036 | -0.0030013 | -0.0083569 | -0.0018971 | -0.38452 | -0.13733 | -0.93842 | -0.32044 | -0.2655 | -0.45319 | -0.2655 | 1.4374 | 122.1039 | -0.98419 | 0.29755 | 0.1236 | -0.55389 | -0.54016 | -0.050354 | -122.1451 | -122.3282 | 0.62256 | 0.62256 | 0.43488 | 0.67291 | 0.48523 | -0.09613 | 0.096131 | -121.7102 | 1.0117 | 0.3479 | 0.33417 | 0.44403 | 0.4303 | 0.67291 | 0.61798 | 1.1078 | 1.2817 | 0.80109 | 123.0881 | 0.75073 | 122.9919 | -122.9462 | -122.9919 | 0.56763 | 1.1856 | 0.50354 | 2.3254
4761.1719 | 122.9691 | -0.92926 | 122.0215 | -0.098725 | -0.00087374 | 0.017805 | 0.0098715 | 0.0016556 | -0.00079891 | 0.0028582 | -0.028809 | 0.0087927 | -0.00042717 | -0.0037854 | -0.0038559 | -0.0042981 | 0.0030163 | -0.41199 | -0.12817 | -0.95673 | -0.3479 | -0.31128 | -0.46234 | -0.25635 | 1.4465 | 122.1085 | -0.99792 | 0.29755 | 0.15106 | -0.54016 | -0.56305 | -0.027466 | -122.1497 | -122.3694 | 0.61798 | 0.67291 | 0.46692 | 0.70038 | 0.49438 | -0.068665 | 0.086975 | -121.7239 | 1.0803 | 0.36621 | 0.3891 | 0.43488 | 0.45776 | 0.64545 | 0.60883 | 1.149 | 1.2955 | 0.82855 | 123.1064 | 0.80109 | 123.0377 | -122.9782 | -123.0194 | 0.58136 | 1.2268 | 0.51727 | 2.3758
4762.1719 | 122.9736 | -0.91095 | 122.0032 | -0.098725 | -0.0013009 | 0.018874 | 0.0070943 | -0.0017624 | 0.0024053 | 0.00093559 | -0.041016 | 0.0066565 | 0.001068 | 0.001128 | -0.0021469 | -0.0049389 | -0.00061526 | -0.36621 | -0.14191 | -0.9613 | -0.31128 | -0.26093 | -0.44403 | -0.26093 | 1.5289 | 122.0993 | -0.99335 | 0.36621 | 0.16479 | -0.53101 | -0.53558 | -0.050354 | -122.1451 | -122.3145 | 0.65003 | 0.65003 | 0.46692 | 0.70038 | 0.51727 | -0.082397 | 0.09613 | -121.637 | 1.0757 | 0.37537 | 0.37994 | 0.45776 | 0.46234 | 0.70038 | 0.65003 | 1.1581 | 1.3596 | 0.8194 | 123.0927 | 0.76904 | 123.0103 | -122.9645 | -122.9965 | 0.59967 | 1.2772 | 0.54474 | 2.4399
4763.1719 | 122.9965 | -0.89264 | 122.0078 | -0.091095 | 0.0012625 | 0.016524 | 0.0090169 | 0.00016017 | 0.0026191 | 0.003072 | -0.041016 | 0.0092199 | 0.0014954 | 0.00048702 | -0.0030013 | -0.0064343 | 0.0030163 | -0.37079 | -0.14648 | -0.93842 | -0.28839 | -0.27466 | -0.4303 | -0.24719 | 1.5884 | 122.1268 | -0.97961 | 0.37079 | 0.21057 | -0.50812 | -0.51727 | -0.045777 | -122.1542 | -122.2961 | 0.61798 | 0.64545 | 0.46234 | 0.69122 | 0.50812 | -0.086975 | 0.11902 | -121.637 | 1.1032 | 0.37537 | 0.38452 | 0.46234 | 0.4715 | 0.66376 | 0.65003 | 1.1902 | 1.3504 | 0.79193 | 123.1064 | 0.74615 | 123.0194 | -122.9462 | -122.9874 | 0.60425 | 1.2634 | 0.52185 | 2.4811
4764.1719 | 122.9645 | -0.90637 | 122.0169 | -0.10635 | 0.00019446 | 0.020155 | 0.0068807 | 0.001442 | -0.00015811 | 0.00072199 | -0.019653 | 0.0070837 | -0.00021357 | -0.00079478 | -0.0023605 | -0.0070753 | 0.0013073 | -0.42572 | -0.14191 | -0.95673 | -0.36621 | -0.32501 | -0.46692 | -0.28381 | 1.5427 | 122.1359 | -0.98419 | 0.32044 | 0.21515 | -0.49439 | -0.52643 | -0.050354 | -122.1588 | -122.3831 | 0.58136 | 0.62256 | 0.43945 | 0.67291 | 0.48981 | -0.07782 | 0.11902 | -121.6965 | 1.1215 | 0.37994 | 0.41199 | 0.45776 | 0.48981 | 0.63171 | 0.59051 | 1.1993 | 1.3046 | 0.81482 | 123.1201 | 0.76446 | 123.0423 | -122.9736 | -123.0011 | 0.54016 | 1.2268 | 0.48065 | 2.449
4765.1719 | 122.9553 | -0.91095 | 122.0123 | -0.12924 | -0.00023294 | 0.018233 | 0.0096579 | 0.0020828 | 0.0021917 | 0.0047808 | -0.022705 | 0.010288 | 0.003418 | -0.0031446 | -0.0019333 | -0.0055799 | 2.554e-05 | -0.39368 | -0.15564 | -0.95673 | -0.32959 | -0.27924 | -0.45776 | -0.26093 | 1.5839 | 122.113 | -0.99792 | 0.3479 | 0.21057 | -0.49439 | -0.53101 | -0.045776 | -122.168 | -122.3419 | 0.63171 | 0.65003 | 0.45319 | 0.6958 | 0.49896 | -0.086975 | 0.10071 | -121.6644 | 1.1215 | 0.37994 | 0.41657 | 0.46692 | 0.50354 | 0.67749 | 0.62714 | 1.2085 | 1.3458 | 0.80109 | 123.111 | 0.75531 | 123.024 | -122.9691 | -123.0103 | 0.58136 | 1.2589 | 0.51727 | 2.4948
4766.1719 | 123.0103 | -0.90637 | 121.9757 | -0.12924 | -0.00023294 | 0.019514 | 0.0077353 | -0.00026703 | 0.0032599 | 0.0032856 | -0.044067 | 0.0090063 | 0.00085443 | -0.0027174 | -0.0032151 | -0.0053663 | 0.0017345 | -0.36621 | -0.16479 | -0.94299 | -0.30212 | -0.27008 | -0.43945 | -0.25177 | 1.6571 | 122.1085 | -0.97961 | 0.42114 | 0.2655 | -0.44403 | -0.47607 | -0.036621 | -122.1405 | -122.2778 | 0.63629 | 0.6546 | 0.46692 | 0.69122 | 0.50354 | -0.073242 | 0.13275 | -121.5546 | 1.1719 | 0.4303 | 0.46234 | 0.50354 | 0.53558 | 0.67291 | 0.64087 | 1.2451 | 1.4008 | 0.7782 | 123.0881 | 0.74158 | 123.0148 | -122.9187 | -122.9553 | 0.60425 | 1.3275 | 0.54016 | 2.5635
4767.1719 | 122.9874 | -0.91553 | 122.0169 | -0.11398 | 0.0019035 | 0.019087 | 0.0068807 | 0.00037377 | 0.0017645 | 0.0067036 | -0.019653 | 0.010715 | 0.0042724 | -0.00036738 | -0.0047103 | -0.0066479 | 0.0010937 | -0.41199 | -0.14191 | -0.92926 | -0.34332 | -0.32501 | -0.48065 | -0.27008 | 1.6067 | 122.1268 | -0.98877 | 0.37079 | 0.23804 | -0.46692 | -0.49896 | -0.013733 | -122.1588 | -122.3602 | 0.59051 | 0.64545 | 0.43487 | 0.65918 | 0.44861 | -0.073243 | 0.10986 | -121.6461 | 1.1536 | 0.41656 | 0.44861 | 0.48981 | 0.52185 | 0.60425 | 0.58594 | 1.2268 | 1.3596 | 0.78735 | 123.1155 | 0.77362 | 123.0423 | -122.9462 | -123.0057 | 0.5722 | 1.2863 | 0.50354 | 2.5223
4768.1719 | 122.9782 | -0.90179 | 122.0306 | -0.083466 | -0.00087374 | 0.020583 | 0.0094443 | 0.00016017 | 0.0013373 | 0.002431 | -0.022705 | 0.0085791 | 0.0023498 | -0.0027174 | -0.0051377 | -0.0040845 | -0.0018971 | -0.39368 | -0.14191 | -0.92468 | -0.35248 | -0.31586 | -0.4715 | -0.27466 | 1.6113 | 122.1268 | -0.97961 | 0.40283 | 0.24719 | -0.44403 | -0.48981 | -0.022889 | -122.1725 | -122.3831 | 0.58594 | 0.62714 | 0.4303 | 0.65003 | 0.45319 | -0.07782 | 0.09613 | -121.6278 | 1.149 | 0.41199 | 0.45776 | 0.48981 | 0.53558 | 0.60883 | 0.57221 | 1.2268 | 1.3824 | 0.78278 | 123.1064 | 0.75989 | 123.0286 | -122.9553 | -123.0103 | 0.54932 | 1.3046 | 0.50812 | 2.5131
4769.1719 | 122.9828 | -0.90179 | 122.0215 | -0.022431 | -0.0017281 | 0.018019 | 0.0070943 | -0.0013352 | -0.00079891 | 0.00050839 | -0.019653 | 0.010075 | 0.001709 | 0.0028368 | -0.0025741 | -0.0055799 | 0.0010937 | -0.38452 | -0.15106 | -0.94757 | -0.30212 | -0.27466 | -0.37994 | -0.22888 | 1.6434 | 122.1268 | -0.97961 | 0.41199 | 0.29297 | -0.40741 | -0.49896 | -0.045777 | -122.1725 | -122.3236 | 0.62714 | 0.67291 | 0.52185 | 0.71869 | 0.56763 | -0.07782 | 0.10529 | -121.6095 | 1.1948 | 0.40283 | 0.49438 | 0.48065 | 0.5722 | 0.67291 | 0.64545 | 1.2726 | 1.3916 | 0.79651 | 123.1064 | 0.75073 | 123.0286 | -122.9691 | -123.0011 | 0.59967 | 1.3138 | 0.51727 | 2.5452
4770.1719 | 122.9919 | -0.87433 | 122.0215 | -0.068207 | 0.00083526 | 0.018874 | 0.0085897 | -0.0015488 | 0.00069649 | 0.0022174 | -0.06543 | 0.011783 | 0.0042724 | 5.9824e-05 | -0.0055649 | -0.0040845 | 0.0036571 | -0.42114 | -0.10986 | -0.95673 | -0.3479 | -0.35248 | -0.48981 | -0.28839 | 1.6342 | 122.1359 | -0.97961 | 0.46692 | 0.3067 | -0.41657 | -0.47607 | -0.082397 | -122.1313 | -122.3694 | 0.52185 | 0.58594 | 0.38452 | 0.66833 | 0.46692 | -0.10528 | 0.11444 | -121.5546 | 1.181 | 0.39826 | 0.45776 | 0.50354 | 0.56305 | 0.60425 | 0.60883 | 1.2863 | 1.4465 | 0.84686 | 123.1155 | 0.76447 | 123.0103 | -122.9782 | -123.0011 | 0.52643 | 1.3412 | 0.45319 | 2.5085
4771.1719 | 123.0103 | -0.88348 | 122.0535 | -0.11398 | 0.00040806 | 0.017805 | 0.0098715 | 0.001442 | 5.5488e-05 | 0.0034992 | -0.041016 | 0.012852 | 0.0023498 | 0.0043322 | -0.0034287 | -0.0034437 | 0.00066654 | -0.37537 | -0.13733 | -0.93384 | -0.32501 | -0.30212 | -0.45319 | -0.25177 | 1.6251 | 122.1497 | -0.96588 | 0.50354 | 0.29755 | -0.3891 | -0.42572 | -0.050354 | -122.1909 | -122.3785 | 0.58136 | 0.63171 | 0.4303 | 0.68207 | 0.48065 | -0.082397 | 0.09613 | -121.55 | 1.181 | 0.45776 | 0.49439 | 0.54016 | 0.57678 | 0.63171 | 0.60883 | 1.2634 | 1.4694 | 0.79651 | 123.1155 | 0.74616 | 123.0331 | -122.9874 | -123.0194 | 0.55847 | 1.387 | 0.50812 | 2.5085
4772.1719 | 123.0194 | -0.85144 | 122.0306 | -0.12161 | 0.00083526 | 0.019514 | 0.0094443 | -0.00069423 | 0.0032599 | 0.0026446 | -0.06543 | 0.010075 | 0.002777 | -0.00036738 | -0.0032151 | -0.0028027 | 0.0021619 | -0.3891 | -0.14648 | -0.94757 | -0.34332 | -0.28839 | -0.45776 | -0.26093 | 1.6571 | 122.1268 | -0.97046 | 0.50812 | 0.30212 | -0.38452 | -0.43945 | -0.096131 | -122.1771 | -122.374 | 0.56305 | 0.59051 | 0.39368 | 0.68665 | 0.48981 | -0.11902 | 0.09613 | -121.5225 | 1.1536 | 0.41199 | 0.46692 | 0.53101 | 0.58594 | 0.65918 | 0.60425 | 1.2726 | 1.4786 | 0.80109 | 123.0972 | 0.70496 | 122.9782 | -122.9782 | -123.0011 | 0.50812 | 1.3596 | 0.46234 | 2.5085
4773.1719 | 122.9507 | -0.91553 | 122.0764 | -0.060578 | 0.0012625 | 0.020583 | 0.0083761 | -0.00048063 | 0.0011237 | 0.0015766 | -0.019653 | 0.011997 | 0.001709 | -0.0018628 | -0.0019333 | -0.0053663 | 0.00066654 | -0.39368 | -0.14191 | -0.9613 | -0.35706 | -0.31128 | -0.41657 | -0.2655 | 1.6617 | 122.168 | -0.98419 | 0.41199 | 0.27008 | -0.39825 | -0.52643 | -0.045777 | -122.2183 | -122.4335 | 0.60425 | 0.65002 | 0.49896 | 0.6958 | 0.54474 | -0.068665 | 0.091553 | -121.6644 | 1.1856 | 0.3891 | 0.51727 | 0.45776 | 0.58594 | 0.65003 | 0.60425 | 1.2543 | 1.3962 | 0.8194 | 123.1522 | 0.77362 | 123.0835 | -123.0377 | -123.0606 | 0.55847 | 1.3275 | 0.52185 | 2.5772
4774.1719 | 122.9965 | -0.91553 | 122.0032 | -0.098725 | -0.00044654 | 0.020583 | 0.0088033 | -0.0017624 | 0.00048269 | 8.1188e-05 | 0.026123 | 0.012424 | 0.0036316 | 0.0030506 | -0.0036423 | -0.0028027 | 0.0055797 | -0.42572 | -0.14648 | -0.97046 | -0.36621 | -0.33417 | -0.4715 | -0.27008 | 1.6617 | 122.0764 | -1.0117 | 0.45776 | 0.33875 | -0.3479 | -0.49896 | -0.054932 | -122.1497 | -122.3694 | 0.58136 | 0.64545 | 0.44403 | 0.70038 | 0.49896 | -0.096131 | 0.073242 | -121.5454 | 1.2543 | 0.41656 | 0.56763 | 0.5127 | 0.66376 | 0.63629 | 0.60425 | 1.3504 | 1.4694 | 0.82397 | 123.0881 | 0.76904 | 122.9919 | -122.9736 | -123.0148 | 0.54932 | 1.3733 | 0.48981 | 2.5772
4775.1719 | 123.0103 | -0.90179 | 121.9986 | -0.13687 | -0.0017281 | 0.01866 | 0.0090169 | -0.00048063 | 0.0019781 | 0.0049946 | -0.041016 | 0.012638 | 0.005127 | 0.0041186 | -0.0036423 | -0.0051527 | 0.0032299 | -0.42572 | -0.15564 | -0.97046 | -0.33875 | -0.33417 | -0.47607 | -0.28381 | 1.7303 | 122.081 | -1.0117 | 0.52185 | 0.33417 | -0.33875 | -0.44403 | -0.068665 | -122.1542 | -122.3373 | 0.56763 | 0.61798 | 0.42572 | 0.68665 | 0.49438 | -0.10986 | 0.082398 | -121.4767 | 1.236 | 0.45776 | 0.56305 | 0.56763 | 0.67291 | 0.63629 | 0.63171 | 1.3458 | 1.5335 | 0.81482 | 123.0927 | 0.74615 | 122.9828 | -122.9691 | -123.0103 | 0.56305 | 1.4236 | 0.47607 | 2.6321
4776.1719 | 123.0103 | -0.92468 | 121.9986 | -0.068207 | 0.00040806 | 0.020155 | 0.010085 | -0.00026703 | 0.0021917 | 0.0032856 | -0.044067 | 0.013065 | 0.0019226 | 0.005614 | -0.0010787 | -0.0051527 | -0.0021107 | -0.4303 | -0.13275 | -0.99792 | -0.40283 | -0.39368 | -0.51727 | -0.32501 | 1.6891 | 122.1176 | -0.99792 | 0.49896 | 0.33417 | -0.37079 | -0.47607 | -0.073242 | -122.1313 | -122.4014 | 0.53101 | 0.59967 | 0.40741 | 0.67291 | 0.48065 | -0.073242 | 0.11902 | -121.4996 | 1.2589 | 0.44861 | 0.55389 | 0.52185 | 0.62714 | 0.60425 | 0.59509 | 1.3321 | 1.4969 | 0.86517 | 123.1155 | 0.79193 | 123.0423 | -122.9965 | -122.9965 | 0.52185 | 1.4236 | 0.49439 | 2.6138
4777.1719 | 122.9233 | -0.94757 | 122.0215 | -0.075836 | 0.0025443 | 0.019942 | 0.0085897 | 0.0027238 | 0.0013373 | 0.0032856 | -0.077637 | 0.013065 | 0.0042724 | 0.0034778 | -0.0015061 | -0.0028027 | 0.0017345 | -0.46234 | -0.13275 | -1.0162 | -0.45776 | -0.45776 | -0.5722 | -0.3891 | 1.6159 | 122.1222 | -1.0437 | 0.42572 | 0.25177 | -0.43945 | -0.54932 | -0.068664 | -122.1542 | -122.4792 | 0.48981 | 0.55847 | 0.37537 | 0.62714 | 0.44403 | -0.09613 | 0.10071 | -121.5958 | 1.1993 | 0.39826 | 0.50812 | 0.49438 | 0.60425 | 0.55847 | 0.55847 | 1.2955 | 1.4694 | 0.88348 | 123.1659 | 0.81482 | 123.0698 | -123.0377 | -123.0652 | 0.48981 | 1.3733 | 0.48523 | 2.5635
4778.1719 | 122.905 | -0.95215 | 122.0352 | -0.0071715 | -0.0023691 | 0.01866 | 0.0083761 | 0.00486 | 0.0028327 | 0.0049946 | -0.10205 | 0.017124 | 0.006195 | 0.0098864 | -0.0010787 | -0.0025891 | 0.0038709 | -0.47607 | -0.15564 | -1.0117 | -0.48981 | -0.48523 | -0.58594 | -0.36621 | 1.6479 | 122.1313 | -1.0529 | 0.41657 | 0.24719 | -0.4303 | -0.55389 | -0.05951 | -122.1909 | -122.525 | 0.46692 | 0.58594 | 0.36621 | 0.64545 | 0.42572 | -0.10071 | 0.096131 | -121.6187 | 1.1993 | 0.39825 | 0.52185 | 0.49896 | 0.62256 | 0.52643 | 0.52185 | 1.3 | 1.4694 | 0.85602 | 123.1842 | 0.79651 | 123.0835 | -123.0469 | -123.0881 | 0.46234 | 1.3687 | 0.47607 | 2.6001
4779.1719 | 123.0011 | -0.92926 | 121.994 | -0.060578 | -0.0013009 | 0.020369 | 0.0081625 | 0.00058737 | 0.0015509 | 0.0032856 | -0.041016 | 0.01392 | 0.0064086 | 0.0064684 | -0.0012925 | -0.0010937 | 0.0034435 | -0.46234 | -0.12817 | -0.99792 | -0.42572 | -0.39825 | -0.53558 | -0.34332 | 1.8082 | 122.1039 | -1.03 | 0.50812 | 0.34332 | -0.31128 | -0.47607 | -0.068665 | -122.1222 | -122.4197 | 0.53101 | 0.58594 | 0.39368 | 0.6546 | 0.46234 | -0.10071 | 0.10986 | -121.4859 | 1.2726 | 0.45319 | 0.61798 | 0.55389 | 0.71869 | 0.59967 | 0.5722 | 1.3733 | 1.5381 | 0.86975 | 123.1338 | 0.80109 | 123.0331 | -122.9919 | -123.024 | 0.50354 | 1.4374 | 0.46692 | 2.7374
4780.1719 | 122.9187 | -0.96588 | 122.0306 | -0.098725 | -0.00066014 | 0.022719 | 0.0088033 | -0.0017624 | 0.0041143 | 0.0049946 | -0.041016 | 0.015842 | 0.0032044 | 0.00048702 | -0.0015061 | -0.0028027 | 0.0023755 | -0.46234 | -0.11902 | -1.0025 | -0.47607 | -0.44403 | -0.55847 | -0.3891 | 1.7166 | 122.1085 | -1.0437 | 0.44861 | 0.25635 | -0.40283 | -0.55847 | -0.036621 | -122.1497 | -122.5067 | 0.52185 | 0.57678 | 0.40741 | 0.6134 | 0.44403 | -0.07782 | 0.077819 | -121.582 | 1.2222 | 0.40741 | 0.56305 | 0.48523 | 0.64087 | 0.55847 | 0.52643 | 1.3 | 1.4923 | 0.88348 | 123.1522 | 0.84686 | 123.0743 | -123.0331 | -123.0743 | 0.48981 | 1.4145 | 0.50354 | 2.6825
4781.1719 | 123.0057 | -0.93384 | 121.9986 | -0.098725 | -0.0025827 | 0.019301 | 0.0098715 | -0.0032578 | 0.0013373 | 0.0049946 | -0.028809 | 0.01627 | 0.0057678 | -0.0033582 | -0.0036423 | -0.0032301 | -0.00082886 | -0.45776 | -0.14648 | -0.99792 | -0.40741 | -0.3891 | -0.51727 | -0.32501 | 1.8448 | 122.1085 | -1.03 | 0.5722 | 0.40283 | -0.25177 | -0.46234 | -0.064087 | -122.1451 | -122.406 | 0.54474 | 0.60883 | 0.41656 | 0.67291 | 0.48065 | -0.09613 | 0.10986 | -121.4264 | 1.3367 | 0.4715 | 0.68207 | 0.56763 | 0.7782 | 0.60883 | 0.59051 | 1.4328 | 1.6022 | 0.85144 | 123.1384 | 0.78735 | 123.0423 | -122.9965 | -123.0286 | 0.52643 | 1.506 | 0.47607 | 2.7786
4782.1719 | 122.9004 | -0.97961 | 122.0398 | -0.083466 | -0.00023294 | 0.022505 | 0.010726 | 0.0022964 | 0.00091009 | 0.0052082 | -0.044067 | 0.017338 | 0.0070496 | -0.0065626 | -0.0012925 | -0.0010937 | 0.00066654 | -0.4715 | -0.14648 | -1.03 | -0.48065 | -0.4715 | -0.57678 | -0.39825 | 1.7761 | 122.1176 | -1.0529 | 0.45319 | 0.27008 | -0.36163 | -0.55389 | -0.050354 | -122.1863 | -122.5204 | 0.50812 | 0.58136 | 0.40283 | 0.63171 | 0.45319 | -0.073242 | 0.07782 | -121.5866 | 1.2497 | 0.42572 | 0.61798 | 0.49896 | 0.69122 | 0.55847 | 0.54932 | 1.3229 | 1.506 | 0.88348 | 123.1705 | 0.83313 | 123.0972 | -123.0698 | -123.0927 | 0.49896 | 1.4328 | 0.50812 | 2.7557
4783.1719 | 122.9095 | -0.97504 | 122.0123 | -0.037689 | -0.00066014 | 0.022078 | 0.010299 | 0.00080117 | 0.0039007 | 0.0034992 | -0.059326 | 0.01691 | 0.0042724 | 0.003905 | -0.00065151 | -0.0036573 | 0.00088014 | -0.46234 | -0.16479 | -1.0208 | -0.46692 | -0.45319 | -0.57678 | -0.3891 | 1.8219 | 122.1222 | -1.0483 | 0.48065 | 0.29297 | -0.32501 | -0.54932 | -0.045776 | -122.1771 | -122.4792 | 0.52185 | 0.58594 | 0.39826 | 0.63171 | 0.44403 | -0.073242 | 0.10986 | -121.5317 | 1.268 | 0.42572 | 0.65003 | 0.49896 | 0.72327 | 0.56763 | 0.55389 | 1.3412 | 1.5289 | 0.85602 | 123.1705 | 0.81024 | 123.0972 | -123.0331 | -123.0606 | 0.50812 | 1.4557 | 0.5127 | 2.7969
4784.1719 | 123.0194 | -0.98419 | 121.9299 | -0.15213 | -0.0010873 | 0.020369 | 0.0060263 | 0.00080117 | 0.0015509 | 0.0017902 | 0.016968 | 0.017124 | 0.005127 | -0.0033582 | -0.0036423 | -0.0028027 | 0.0021619 | -0.42114 | -0.1831 | -1.0345 | -0.36621 | -0.31586 | -0.47607 | -0.29297 | 2.0096 | 122.0261 | -1.0712 | 0.60425 | 0.43488 | -0.18768 | -0.45776 | -0.050354 | -122.113 | -122.2961 | 0.66833 | 0.69122 | 0.50812 | 0.74158 | 0.55847 | -0.086975 | 0.09613 | -121.3257 | 1.4191 | 0.52643 | 0.79651 | 0.6134 | 0.88348 | 0.71869 | 0.66833 | 1.506 | 1.6754 | 0.85144 | 123.0972 | 0.80109 | 123.0103 | -122.9645 | -123.0011 | 0.61798 | 1.5884 | 0.56305 | 2.9938
4785.1719 | 122.9187 | -1.0345 | 121.9803 | -0.12161 | -0.0013009 | 0.019514 | 0.0081625 | -0.00048063 | 0.0024053 | 0.0039264 | -0.050171 | 0.018192 | 0.004486 | -0.005708 | -0.0042831 | -0.0023755 | -0.0014697 | -0.47607 | -0.16022 | -1.0529 | -0.49439 | -0.49896 | -0.59052 | -0.39825 | 1.8814 | 122.0764 | -1.1169 | 0.54474 | 0.29755 | -0.29297 | -0.55389 | -0.01831 | -122.1405 | -122.4747 | 0.53558 | 0.63629 | 0.44403 | 0.6546 | 0.46234 | -0.082397 | 0.09613 | -121.4355 | 1.3321 | 0.48065 | 0.74158 | 0.56305 | 0.82397 | 0.55389 | 0.55847 | 1.4145 | 1.6617 | 0.89264 | 123.1934 | 0.87433 | 123.111 | -123.0331 | -123.0972 | 0.54016 | 1.5793 | 0.55847 | 2.916
4786.1719 | 122.9599 | -1.0162 | 121.962 | -0.068207 | 0.00019446 | 0.020369 | 0.0081625 | -0.00090783 | 0.0024053 | 0.0015766 | -0.037964 | 0.019688 | 0.0049134 | -0.0018628 | -0.0010787 | -0.0025891 | -0.00082886 | -0.42114 | -0.15564 | -1.062 | -0.42572 | -0.40283 | -0.50812 | -0.3479 | 2.0096 | 122.081 | -1.0941 | 0.59052 | 0.36163 | -0.22888 | -0.51727 | -0.045777 | -122.1176 | -122.3877 | 0.6134 | 0.66834 | 0.50812 | 0.71411 | 0.55389 | -0.07782 | 0.11902 | -121.3715 | 1.3779 | 0.49896 | 0.78735 | 0.57678 | 0.86517 | 0.65918 | 0.63629 | 1.4557 | 1.6846 | 0.90637 | 123.175 | 0.86059 | 123.0972 | -123.024 | -123.056 | 0.59052 | 1.6067 | 0.59509 | 3.0258
4787.1719 | 123.0148 | -0.97504 | 121.9437 | -0.12161 | 0.0014761 | 0.021223 | 0.0062399 | 0.0029374 | 0.0026191 | 0.0037128 | -0.016602 | 0.01926 | 0.0074768 | -0.0014356 | -0.0044967 | -0.0030163 | -0.0016833 | -0.39825 | -0.17853 | -1.0254 | -0.35706 | -0.32959 | -0.47607 | -0.28839 | 2.124 | 122.049 | -1.0712 | 0.67291 | 0.4303 | -0.11902 | -0.43488 | -0.050354 | -122.1222 | -122.3007 | 0.64545 | 0.68665 | 0.49896 | 0.737 | 0.54932 | -0.09613 | 0.10529 | -121.2708 | 1.4053 | 0.54016 | 0.85602 | 0.63629 | 0.95215 | 0.6958 | 0.66833 | 1.5015 | 1.7441 | 0.84686 | 123.1201 | 0.79651 | 123.024 | -122.9691 | -123.0148 | 0.61798 | 1.648 | 0.57678 | 3.0991
4788.1719 | 122.9279 | -1.0208 | 121.9711 | -0.052948 | 0.00062166 | 0.021223 | 0.0081625 | 0.00486 | 0.0011237 | 0.0020038 | -0.034912 | 0.019688 | 0.0087586 | 0.00070062 | -0.0032151 | -0.00066648 | 0.0019483 | -0.4715 | -0.17395 | -1.062 | -0.45776 | -0.4303 | -0.54474 | -0.3891 | 2.0874 | 122.081 | -1.0941 | 0.58136 | 0.33417 | -0.21515 | -0.53101 | -0.041199 | -122.1451 | -122.4289 | 0.59051 | 0.63171 | 0.47607 | 0.67291 | 0.51727 | -0.073242 | 0.10986 | -121.3898 | 1.355 | 0.48981 | 0.80566 | 0.56305 | 0.87891 | 0.63171 | 0.60425 | 1.4282 | 1.6754 | 0.88806 | 123.175 | 0.84686 | 123.1018 | -123.0331 | -123.0652 | 0.56305 | 1.6022 | 0.54932 | 3.1082
4789.1719 | 122.9187 | -1.0483 | 121.962 | -0.060578 | 0.00019446 | 0.021223 | 0.0090169 | 0.0016556 | 0.0017645 | 0.002431 | -0.034912 | 0.02161 | 0.0076904 | 0.002196 | -0.0010787 | -0.0021619 | 0.0017345 | -0.47607 | -0.16937 | -1.0483 | -0.49439 | -0.48065 | -0.58136 | -0.40283 | 2.1881 | 122.0718 | -1.0986 | 0.57678 | 0.33417 | -0.19684 | -0.54932 | 0 | -122.1313 | -122.4564 | 0.56763 | 0.64545 | 0.46692 | 0.64545 | 0.46692 | -0.050354 | 0.10986 | -121.3852 | 1.3824 | 0.49896 | 0.85144 | 0.54932 | 0.90179 | 0.56763 | 0.55389 | 1.4328 | 1.6754 | 0.87891 | 123.1705 | 0.87891 | 123.1201 | -123.0103 | -123.0606 | 0.55389 | 1.6251 | 0.5722 | 3.2364
4790.1719 | 122.9279 | -1.0162 | 121.9666 | -0.060578 | 0.00040806 | 0.021651 | 0.0060263 | -0.0017624 | 0.0034735 | 0.002431 | -0.034912 | 0.021824 | 0.0064086 | 0.0054004 | -0.0030013 | -0.0019483 | 0.0013073 | -0.46692 | -0.17395 | -1.0574 | -0.46234 | -0.4303 | -0.54474 | -0.37079 | 2.2568 | 122.0352 | -1.0941 | 0.63171 | 0.40283 | -0.14191 | -0.50812 | -0.041199 | -122.1405 | -122.4289 | 0.58594 | 0.64545 | 0.4715 | 0.68664 | 0.5127 | -0.07782 | 0.068664 | -121.3348 | 1.4191 | 0.50812 | 0.87433 | 0.58594 | 0.95215 | 0.62714 | 0.59509 | 1.4969 | 1.7258 | 0.88348 | 123.1293 | 0.84228 | 123.0515 | -123.024 | -123.0606 | 0.55389 | 1.6479 | 0.54932 | 3.273
4791.1719 | 122.9553 | -1.0391 | 121.9208 | -0.022431 | 0.00083526 | 0.022078 | 0.0088033 | -0.0017624 | 0.0043281 | 0.002431 | -0.01355 | 0.022678 | 0.0087586 | 0.00070062 | -0.0015061 | -0.0013073 | 0.0049389 | -0.46692 | -0.17395 | -1.0757 | -0.45776 | -0.4303 | -0.54932 | -0.35706 | 2.3529 | 122.0398 | -1.1032 | 0.64545 | 0.42572 | -0.082397 | -0.50354 | -0.036621 | -122.0947 | -122.3785 | 0.60883 | 0.68207 | 0.48981 | 0.71869 | 0.52643 | -0.064086 | 0.11902 | -121.2753 | 1.4648 | 0.53558 | 0.95673 | 0.59967 | 1.0208 | 0.64545 | 0.61798 | 1.5289 | 1.7487 | 0.90179 | 123.143 | 0.86517 | 123.0789 | -122.9965 | -123.024 | 0.58136 | 1.6846 | 0.5722 | 3.392
4792.1719 | 122.9782 | -1.0117 | 121.9391 | -0.091095 | -0.00023294 | 0.023146 | 0.0060263 | -0.0015488 | 0.00069649 | 0.0017902 | 0.065796 | 0.021824 | 0.0076904 | -0.0016492 | -0.0021469 | -0.0038709 | 0.0025891 | -0.48065 | -0.20599 | -1.0529 | -0.43945 | -0.4303 | -0.50812 | -0.32959 | 2.4078 | 122.0032 | -1.1124 | 0.67749 | 0.49896 | 0.027466 | -0.45319 | -0.041198 | -122.1451 | -122.3785 | 0.58136 | 0.68207 | 0.50354 | 0.72327 | 0.54474 | -0.10071 | 0.064087 | -121.2616 | 1.5106 | 0.55847 | 1.0391 | 0.65918 | 1.1398 | 0.62256 | 0.6134 | 1.6113 | 1.7899 | 0.84686 | 123.1155 | 0.80566 | 123.0148 | -122.9919 | -123.0515 | 0.5722 | 1.6891 | 0.53101 | 3.4195
4793.1719 | 122.9507 | -1.0529 | 121.9482 | -0.075836 | 0.0019035 | 0.021437 | 0.0085897 | 0.003151 | 0.0024053 | 0.0022174 | -0.010498 | 0.024601 | 0.0081176 | -0.0033582 | -0.0055649 | 0.00040152 | 0.0019483 | -0.50354 | -0.1831 | -1.1169 | -0.4715 | -0.50354 | -0.55389 | -0.3891 | 2.4536 | 122.0444 | -1.1307 | 0.6546 | 0.43488 | -0.009155 | -0.48523 | -0.064087 | -122.1313 | -122.4197 | 0.54932 | 0.66376 | 0.49896 | 0.72784 | 0.56305 | -0.07782 | 0.096131 | -121.2936 | 1.4877 | 0.56763 | 1.0437 | 0.64545 | 1.1215 | 0.6134 | 0.64545 | 1.5656 | 1.7853 | 0.93384 | 123.175 | 0.86975 | 123.0972 | -123.0652 | -123.0789 | 0.58136 | 1.7075 | 0.54932 | 3.5065
4794.1719 | 122.9324 | -1.0529 | 121.9574 | -0.045319 | 0.0010489 | 0.022505 | 0.0094443 | -0.0015488 | 0.0028327 | 0.0026446 | -0.03186 | 0.025455 | 0.0074768 | 0.0013416 | -0.0017197 | 0.0016833 | 0.0028027 | -0.48981 | -0.19226 | -1.1078 | -0.46692 | -0.46234 | -0.54932 | -0.38452 | 2.4948 | 122.0627 | -1.1169 | 0.65918 | 0.43945 | 0.018311 | -0.50354 | -0.054932 | -122.1497 | -122.4243 | 0.59052 | 0.66834 | 0.50354 | 0.72327 | 0.55847 | -0.064087 | 0.10529 | -121.2982 | 1.4923 | 0.54932 | 1.0712 | 0.6134 | 1.1353 | 0.64545 | 0.64087 | 1.5564 | 1.7761 | 0.91553 | 123.1796 | 0.86059 | 123.1155 | -123.0652 | -123.0743 | 0.58594 | 1.712 | 0.56305 | 3.5477
4795.1719 | 122.9553 | -1.0895 | 121.8979 | -0.037689 | 0.00062166 | 0.022505 | 0.0090169 | -5.343e-05 | -0.00015811 | 0.003072 | -0.010498 | 0.027378 | 0.0089722 | -0.00464 | -0.0021469 | 0.00040152 | 0.00023934 | -0.48981 | -0.19684 | -1.1215 | -0.47607 | -0.46234 | -0.56763 | -0.39368 | 2.6505 | 121.994 | -1.1673 | 0.68665 | 0.46692 | 0.073242 | -0.5127 | -0.032043 | -122.0947 | -122.374 | 0.62714 | 0.6958 | 0.52185 | 0.72784 | 0.55389 | -0.077819 | 0.096131 | -121.2112 | 1.5564 | 0.57678 | 1.1627 | 0.6546 | 1.2405 | 0.65918 | 0.64545 | 1.6342 | 1.8539 | 0.92468 | 123.1613 | 0.89264 | 123.0835 | -123.0194 | -123.0652 | 0.6134 | 1.7761 | 0.59967 | 3.7399
4796.1719 | 122.937 | -1.0712 | 121.9025 | -0.03006 | 0.0016899 | 0.023146 | 0.0085897 | -0.00069423 | 0.0043281 | 0.001363 | -0.037964 | 0.027164 | 0.0089722 | 0.003905 | -0.0030013 | 0.0021105 | 0.0028027 | -0.48523 | -0.19684 | -1.1078 | -0.48065 | -0.45776 | -0.56305 | -0.38452 | 2.6047 | 121.994 | -1.149 | 0.70953 | 0.48065 | 0.086975 | -0.49439 | -0.036621 | -122.0993 | -122.3831 | 0.6134 | 0.68665 | 0.50812 | 0.72327 | 0.54474 | -0.07782 | 0.091553 | -121.1929 | 1.5518 | 0.57678 | 1.1581 | 0.6546 | 1.236 | 0.65002 | 0.62714 | 1.6296 | 1.8585 | 0.91095 | 123.143 | 0.87433 | 123.0652 | -123.0103 | -123.0515 | 0.59051 | 1.7807 | 0.58594 | 3.6758
4797.1719 | 122.9141 | -1.0941 | 121.8933 | -0.068207 | -0.0010873 | 0.023573 | 0.0085897 | 0.0027238 | 0.0041143 | 0.0032856 | -0.01355 | 0.02631 | 0.0089722 | -0.00015378 | -0.0032151 | -0.0010937 | 0.0036571 | -0.5127 | -0.21515 | -1.1536 | -0.53558 | -0.53101 | -0.61798 | -0.44403 | 2.6367 | 121.9894 | -1.1765 | 0.65918 | 0.43945 | 0.054932 | -0.55389 | -0.059509 | -122.1085 | -122.4289 | 0.56305 | 0.65002 | 0.47607 | 0.70953 | 0.53558 | -0.082398 | 0.09613 | -121.2341 | 1.5335 | 0.54016 | 1.149 | 0.62256 | 1.2314 | 0.62256 | 0.61798 | 1.6159 | 1.8356 | 0.93841 | 123.1659 | 0.87891 | 123.0835 | -123.0469 | -123.0698 | 0.55847 | 1.7532 | 0.58136 | 3.7308
4798.1719 | 122.937 | -1.1581 | 121.8567 | -0.03006 | -0.00066014 | 0.023787 | 0.0085897 | 0.0029374 | 0.0030463 | 0.0028582 | -0.03186 | 0.030155 | 0.0076904 | 0.0015552 | -0.0025741 | 0.0027515 | 0.0036571 | -0.50354 | -0.22888 | -1.1856 | -0.49896 | -0.48981 | -0.58136 | -0.42114 | 4.5364 | 121.9254 | -1.2039 | 0.72327 | 0.49896 | 0.36163 | -0.51727 | -0.027466 | -122.0856 | -122.3557 | 0.66834 | 0.737 | 0.57678 | 0.76446 | 0.60425 | -0.045776 | 0.068665 | -121.1334 | 1.6571 | 0.64087 | 1.5198 | 0.68665 | 1.5656 | 0.6958 | 0.68665 | 1.7029 | 1.9272 | 0.95673 | 123.1293 | 0.92926 | 123.0835 | -123.0423 | -123.0606 | 0.65918 | 1.8814 | 0.6546 | 5.6946
4799.1719 | 122.9416 | -1.1581 | 121.8201 | -0.022431 | -0.0013009 | 0.024428 | 0.0073081 | -0.004753 | 0.0015509 | 0.0039264 | -0.034912 | 0.030155 | 0.009613 | -0.0035718 | -0.0021469 | 0.0014697 | 0.0045117 | -0.50354 | -0.2243 | -1.1948 | -0.51727 | -0.48981 | -0.59052 | -0.41657 | 4.8569 | 121.8979 | -1.2268 | 0.74616 | 0.48065 | 0.4303 | -0.53558 | -0.036621 | -122.0444 | -122.3373 | 0.66834 | 0.74158 | 0.56763 | 0.7782 | 0.60425 | -0.068665 | 0.07782 | -121.0739 | 1.6388 | 0.62256 | 1.5884 | 0.69122 | 1.6571 | 0.70496 | 0.67749 | 1.7075 | 1.973 | 0.97046 | 123.1247 | 0.93384 | 123.056 | -123.0148 | -123.0469 | 0.64087 | 1.9043 | 0.6546 | 6.015
4800.1719 | 122.9187 | -1.2039 | 121.8063 | -0.075836 | 0.0023307 | 0.025069 | 0.0098715 | 0.0029374 | 0.0026191 | 0.005849 | -0.022705 | 0.034855 | 0.0093994 | 0.0015552 | -0.0036423 | 0.0057421 | 0.0072887 | -0.54474 | -0.24719 | -1.2497 | -0.53558 | -0.53101 | -0.63629 | -0.45319 | 5.2414 | 121.8796 | -1.268 | 0.71411 | 0.4715 | 0.44861 | -0.58136 | -0.045777 | -122.0535 | -122.3419 | 0.67291 | 0.75073 | 0.56763 | 0.79651 | 0.6134 | -0.064087 | 0.073243 | -121.0922 | 1.6754 | 0.62256 | 1.6525 | 0.68665 | 1.7166 | 0.71869 | 0.71411 | 1.7395 | 1.9821 | 1.0025 | 123.1476 | 0.95673 | 123.0835 | -123.056 | -123.0743 | 0.66834 | 1.918 | 0.65918 | 6.4453
4801.1719 | 122.9233 | -1.2314 | 121.7743 | -0.098725 | 0.00062166 | 0.025282 | 0.0068807 | -0.00026703 | 0.0024053 | 0.0054218 | -0.041016 | 0.036991 | 0.010895 | 5.9824e-05 | -0.0019333 | 0.0025379 | 0.0023755 | -0.56305 | -0.24719 | -1.2772 | -0.5722 | -0.57678 | -0.66834 | -0.48523 | 5.4382 | 121.8842 | -1.2909 | 0.70953 | 0.44403 | 0.5722 | -0.58136 | -0.045777 | -122.0215 | -122.3465 | 0.6546 | 0.74616 | 0.56305 | 0.79193 | 0.60883 | -0.05951 | 0.10986 | -121.0648 | 1.6754 | 0.65002 | 1.8036 | 0.70953 | 1.8631 | 0.70038 | 0.70496 | 1.7349 | 2.0004 | 1.03 | 123.175 | 0.98419 | 123.1155 | -123.0515 | -123.0652 | 0.65918 | 1.9409 | 0.66834 | 6.6696
4802.1719 | 122.905 | -1.2589 | 121.7148 | -0.10635 | -0.00087374 | 0.024855 | 0.0073081 | 0.0044328 | 0.0041143 | 0.0037128 | -0.03186 | 0.037205 | 0.011536 | -0.00058098 | 0.00041649 | 0.0059557 | 0.0023755 | -0.6134 | -0.2655 | -1.3412 | -0.61798 | -0.64545 | -0.73242 | -0.52643 | 6.1981 | 121.8018 | -1.3596 | 0.76446 | 0.44861 | 0.63171 | -0.60883 | -0.082398 | -121.9803 | -122.3328 | 0.6134 | 0.73242 | 0.52643 | 0.81482 | 0.60883 | -0.10071 | 0.086975 | -120.9503 | 1.7075 | 0.65002 | 1.8906 | 0.75073 | 1.9913 | 0.6958 | 0.72327 | 1.8082 | 2.124 | 1.0757 | 123.1613 | 0.99335 | 123.0606 | -123.056 | -123.0743 | 0.64087 | 2.0233 | 0.64545 | 7.457
4803.1719 | 122.9279 | -1.3184 | 121.6415 | -0.083466 | 0.0010489 | 0.024855 | 0.0088033 | 0.003151 | 0.0039007 | 0.0043536 | -0.03186 | 0.041477 | 0.010895 | 0.0013416 | -0.0010787 | 0.0055285 | 0.0060071 | -0.59509 | -0.27924 | -1.387 | -0.57678 | -0.5722 | -0.68207 | -0.47607 | 7.3563 | 121.7468 | -1.3916 | 0.79651 | 0.50354 | 0.86975 | -0.62256 | -0.068665 | -121.9208 | -122.2183 | 0.74615 | 0.84229 | 0.63629 | 0.91095 | 0.70496 | -0.073243 | 0.10528 | -120.845 | 1.8219 | 0.6958 | 2.1881 | 0.76904 | 2.2614 | 0.81482 | 0.81024 | 1.8951 | 2.1881 | 1.1078 | 123.1384 | 1.0391 | 123.0652 | -123.0286 | -123.0331 | 0.74158 | 2.1149 | 0.72327 | 8.6746
4804.1719 | 122.9507 | -1.4099 | 121.5637 | -0.098725 | 0.0021171 | 0.027632 | 0.0058127 | 0.0020828 | 0.0026191 | 0.0032856 | -0.022705 | 0.048313 | 0.011108 | -0.0042126 | -0.0021469 | 0.0080921 | -0.0021107 | -0.63171 | -0.3067 | -1.4603 | -0.58594 | -0.59052 | -0.68665 | -0.5127 | 8.9951 | 121.6644 | -1.4877 | 0.83313 | 0.53101 | 1.1215 | -0.66834 | -0.050354 | -121.8704 | -122.1497 | 0.8194 | 0.89722 | 0.72327 | 0.94757 | 0.77362 | -0.07782 | 0.10071 | -120.7306 | 1.9409 | 0.74158 | 2.5314 | 0.8194 | 2.6093 | 0.86975 | 0.87433 | 2.0187 | 2.3209 | 1.1536 | 123.1522 | 1.1032 | 123.0743 | -123.024 | -123.0515 | 0.82398 | 2.243 | 0.7782 | 10.405
4805.1719 | 122.9599 | -1.5884 | 121.3348 | -0.014801 | 0.0012625 | 0.023787 | 0.0064535 | 0.003151 | 0.0077459 | 0.0034992 | -0.028809 | 0.056003 | 0.013458 | -0.0033582 | -0.0049241 | 0.013433 | 0.00066654 | -0.64545 | -0.33417 | -1.6479 | -0.63171 | -0.63629 | -0.72784 | -0.53101 | 12.1262 | 121.4401 | -1.6891 | 0.82855 | 0.50354 | 1.561 | -0.80109 | -0.059509 | -121.669 | -121.9666 | 0.95215 | 1.0574 | 0.8606 | 1.1169 | 0.92011 | -0.10071 | 0.10529 | -120.5063 | 2.092 | 0.78735 | 3.1494 | 0.88806 | 3.2501 | 1.0117 | 1.0162 | 2.1927 | 2.5177 | 1.3138 | 123.1293 | 1.2543 | 123.0286 | -122.9828 | -123.024 | 0.95673 | 2.417 | 0.94299 | 13.7146
4806.1719 | 122.9462 | -2.0187 | 120.8954 | -0.045319 | 0.0014761 | 0.032759 | 0.0060263 | -0.0013352 | 0.0060369 | 0.0077716 | -0.03186 | 0.080997 | 0.018372 | -0.0010084 | -0.00065151 | 0.018987 | 0.0072887 | -0.83771 | -0.5127 | -2.0462 | -0.79651 | -0.83771 | -0.93842 | -0.6958 | 20.9793 | 121.0968 | -2.0508 | 0.90637 | 0.53101 | 2.5406 | -1.0117 | -0.027466 | -121.4081 | -121.6919 | 1.181 | 1.3229 | 1.0803 | 1.3504 | 1.1078 | -0.032043 | 0.20142 | -119.989 | 2.5497 | 1.0071 | 4.5593 | 1.0391 | 4.5914 | 1.2085 | 1.2497 | 2.5818 | 2.9572 | 1.5335 | 123.1476 | 1.506 | 123.1155 | -122.9416 | -122.9462 | 1.2222 | 2.9251 | 1.181 | 22.998
4807.1719 | 122.8729 | -1.6937 | 121.2799 | -0.045319 | -0.00023294 | 0.023573 | 0.0066671 | 0.0022964 | 0.0043281 | 0.0034992 | 0.001709 | 0.071384 | 0.01239 | -0.006349 | -0.0032151 | 0.021123 | 0.0025891 | -0.70038 | -0.39825 | -1.6525 | -0.7782 | -0.78278 | -0.83771 | -0.66376 | 7.4158 | 121.4447 | -1.7532 | 0.84686 | 0.56305 | 0.4303 | -0.96588 | 0.041199 | -121.6782 | -122.0581 | 0.91095 | 1.03 | 0.85602 | 0.98877 | 0.81482 | -0.059509 | 0.1648 | -120.433 | 2.2568 | 0.72785 | 2.124 | 0.78735 | 2.1835 | 0.86975 | 0.87433 | 2.3163 | 2.6001 | 1.2543 | 123.1979 | 1.2955 | 123.1384 | -122.9324 | -123.0331 | 0.91553 | 2.5406 | 0.99335 | 9.1095
4808.1719 | 122.9187 | -3.9597 | 119.1284 | -0.045319 | 0.00040806 | 0.025282 | 0.0073081 | 0.0020828 | 0.0062507 | 0.0084124 | -0.034912 | 0.12436 | 0.024139 | 0.0032642 | -0.0034287 | 0.034795 | 0.0036571 | -0.79651 | -0.56763 | -2.124 | -0.74158 | -0.80566 | -0.93384 | -0.78278 | 23.1354 | 120.2545 | -2.5864 | 1.0529 | 0.37537 | 22.0642 | -0.68665 | 1.8356 | -119.696 | -119.87 | 3.154 | 3.1769 | 3.0258 | 1.3412 | 1.1902 | 1.3733 | 1.1261 | -118.0756 | 4.335 | 3.273 | 26.0239 | 1.8997 | 24.6506 | 1.3184 | 1.3824 | 2.9617 | 3.6392 | 1.5564 | 122.8409 | 3.392 | 124.2142 | -121.2524 | -121.7148 | 3.2181 | 5.0125 | 3.1631 | 27.095
4809.1719 | 122.9187 | -2.4216 | 120.5795 | -0.083466 | 0.00062166 | 0.051344 | 0.0073081 | -0.00026703 | 0.0064643 | 0.0060626 | -0.044067 | 0.10514 | 0.019653 | 0.00048702 | -0.0027877 | 0.031591 | 0.0049389 | -0.97046 | -0.64545 | -2.4582 | -0.86975 | -1.0254 | -1.1032 | -0.84686 | 9.7687 | 120.6894 | -2.4353 | 0.94299 | 0.50812 | 8.2443 | -1.0025 | -0.036621 | -121.225 | -121.4493 | 1.3962 | 1.5747 | 1.3184 | 1.6113 | 1.355 | -0.013733 | 0.10986 | -119.6365 | 2.9297 | 1.4191 | 10.6659 | 1.4328 | 10.6796 | 1.4328 | 1.5884 | 2.9434 | 3.3783 | 1.8127 | 123.1247 | 1.7761 | 123.111 | -123.0377 | -123.0148 | 1.5518 | 3.3646 | 1.4511 | 12.1902
4810.1719 | 122.8775 | -2.7054 | 120.1492 | -0.075836 | 0.0016899 | 0.056898 | 0.0077353 | -0.0017624 | 0.0056097 | 0.0099078 | -0.050171 | 0.12586 | 0.023499 | -0.0020764 | -0.0027877 | 0.036077 | 0.0057935 | -1.1353 | -0.68665 | -2.7054 | -1.0254 | -1.1353 | -1.0849 | -0.87891 | 13.6093 | 120.5521 | -2.5818 | 0.97961 | 0.49896 | 5.6717 | -1.2131 | 0 | -120.8359 | -121.1746 | 1.5701 | 1.8265 | 1.6205 | 1.8265 | 1.6205 | 0.1236 | 0.40283 | -119.1696 | 3.2043 | 1.4923 | 8.3771 | 1.3687 | 8.2535 | 1.5701 | 1.68 | 3.0807 | 3.5614 | 2.0187 | 123.1339 | 2.0187 | 123.2574 | -122.8546 | -122.731 | 1.68 | 3.685 | 1.5701 | 16.3147
4811.1719 | 122.937 | -4.5456 | 118.2449 | -0.068207 | 0.0023307 | 0.081679 | 0.0055991 | 0.00251 | 0.0092413 | 0.0094806 | -0.06543 | 0.18781 | 0.040588 | -0.00058098 | -0.0032151 | 0.064275 | 0.01092 | -1.7944 | -1.2497 | -4.6555 | -1.4694 | -1.9409 | -1.7532 | -1.3229 | 27.5208 | 118.6661 | -4.3488 | 1.1719 | 0.45319 | 21.8033 | -1.6663 | -0.10986 | -119.4946 | -119.7144 | 2.6047 | 3.2227 | 2.7924 | 3.3325 | 2.9022 | 0.19684 | 0.42114 | -117.0731 | 4.9988 | 2.8793 | 26.3489 | 2.6825 | 26.152 | 2.7145 | 3.186 | 4.8019 | 5.5206 | 3.4058 | 123.0148 | 3.2959 | 123.2117 | -122.9004 | -122.5937 | 3.0762 | 5.7175 | 2.7512 | 32.0663
4812.1719 | 122.9736 | -2.3483 | 120.5475 | -0.091095 | 0.0025443 | 0.053481 | 0.0058127 | -0.0030442 | 0.0083869 | 0.0090534 | -0.022705 | 0.13611 | 0.026276 | 0.0019824 | -0.0010787 | 0.04569 | 0.0055797 | -1.0712 | -0.6958 | -2.655 | -1.0712 | -1.2543 | -1.2817 | -0.97504 | 11.2061 | 120.4651 | -2.6825 | 1.0437 | 0.58136 | 4.0009 | -1.0574 | -0.3067 | -121.2433 | -121.6187 | 1.0941 | 1.3733 | 1.0666 | 1.68 | 1.3733 | -0.33417 | -0.082397 | -119.5038 | 2.9297 | 1.2909 | 6.3492 | 1.6251 | 6.6833 | 1.4008 | 1.5839 | 3.2639 | 3.7262 | 1.9592 | 123.1476 | 1.6525 | 122.8134 | -123.2025 | -123.23 | 1.2772 | 3.392 | 1.2772 | 13.5544
4813.1719 | 122.937 | -3.9688 | 119.0735 | -0.022431 | 0.0016899 | 0.065443 | 0.0060263 | 0.001442 | 0.010523 | 0.013112 | -0.086792 | 0.2237 | 0.039307 | 0.0026232 | -0.0036423 | 0.091832 | 0.0064343 | -1.6205 | -1.1536 | -3.8956 | -1.442 | -1.799 | -1.7715 | -1.3504 | 21.9177 | 119.1559 | -3.9185 | 1.2085 | 0.53558 | 14.3646 | -2.0554 | 0.073242 | -120.2271 | -120.5154 | 2.1698 | 2.6184 | 2.1973 | 2.5452 | 2.124 | 0.050354 | 0.082398 | -117.865 | 4.5044 | 1.9135 | 18.3334 | 1.8631 | 18.2831 | 2.0966 | 2.4536 | 4.454 | 5.127 | 2.742 | 123.0743 | 2.8152 | 123.1247 | -122.9691 | -122.9919 | 2.5269 | 5.1773 | 2.3483 | 25.8865
4814.1719 | 122.8363 | -3.1448 | 119.9936 | -0.03006 | 0.00019446 | 0.064162 | 0.0062399 | -0.00090783 | 0.0068915 | 0.0088398 | -0.06543 | 0.14295 | 0.034821 | -0.0025036 | -0.0027877 | 0.04804 | 0.0072887 | -1.4923 | -0.96588 | -3.5202 | -1.2863 | -1.6205 | -1.474 | -1.0071 | 14.1586 | 119.9982 | -3.1174 | 1.1444 | 0.56763 | 5.5893 | -1.712 | -0.37537 | -120.9595 | -121.2799 | 1.5244 | 2.1378 | 1.6708 | 2.5131 | 2.0462 | 0.027465 | 0.004578 | -118.8492 | 3.7125 | 1.4328 | 8.7341 | 1.4053 | 8.7067 | 1.8997 | 2.2339 | 3.685 | 4.2618 | 2.5543 | 123.1155 | 2.179 | 123.143 | -123.5138 | -123.111 | 1.8585 | 4.2892 | 1.6525 | 17.3035
4815.1719 | 122.937 | -2.8976 | 120.195 | -0.083466 | 0.0023307 | 0.044722 | 0.0064535 | -0.00069423 | 0.0092413 | 0.011403 | -0.06543 | 0.14679 | 0.03653 | -0.00015378 | -0.0034287 | 0.046544 | 0.0092113 | -1.2085 | -0.72327 | -2.6276 | -1.0071 | -1.2451 | -1.3779 | -0.98877 | 5.6488 | 120.401 | -2.742 | 1.3687 | 0.58594 | 1.2863 | -1.1948 | 0.27008 | -120.9183 | -121.2021 | 1.6525 | 1.9089 | 1.5198 | 1.6388 | 1.2497 | 0.15564 | 0.20599 | -118.8263 | 3.4836 | 1.7029 | 4.184 | 1.5472 | 4.0283 | 1.3824 | 1.6205 | 3.3279 | 4.1107 | 1.9043 | 123.143 | 2.1744 | 123.2986 | -122.8226 | -122.937 | 1.8906 | 4.2664 | 1.6891 | 8.5464
4816.1719 | 122.8912 | -4.8111 | 118.1122 | -0.045319 | 0.0038261 | 0.075697 | 0.0058127 | -0.0015488 | 0.013086 | 0.011617 | -0.089844 | 0.21451 | 0.056396 | 0.0028368 | -0.0019333 | 0.067907 | 0.011561 | -1.7532 | -1.2543 | -4.7012 | -1.5381 | -1.9363 | -1.8356 | -1.387 | 16.4795 | 118.4372 | -4.5319 | 1.3779 | 0.4715 | 14.9048 | -2.0416 | 0.10986 | -119.3665 | -119.6503 | 2.8748 | 3.4241 | 2.9755 | 3.3142 | 2.8656 | 0.27924 | 0.32501 | -116.7343 | 5.2826 | 2.7695 | 19.7159 | 2.4902 | 19.4366 | 2.7649 | 3.1631 | 5.0034 | 5.9097 | 3.447 | 122.9691 | 3.5568 | 123.2483 | -122.8134 | -122.644 | 3.273 | 6.189 | 3.0579 | 21.2906
4817.1719 | 122.8912 | -3.7125 | 119.133 | -0.091095 | 0.0016899 | 0.046858 | 0.0049581 | 0.001442 | 0.013727 | 0.014394 | -0.077637 | 0.18631 | 0.035461 | 0.002196 | -0.0015061 | 0.072393 | 0.012202 | -1.5472 | -0.98877 | -3.2181 | -1.3 | -1.6525 | -1.7578 | -1.3275 | 4.7653 | 119.7235 | -3.3966 | 1.5564 | 0.55847 | 7.8598 | -2.1973 | 0.49438 | -120.1218 | -120.433 | 2.0599 | 2.3849 | 1.9547 | 1.8906 | 1.4603 | 0.31586 | 0.59051 | -117.5766 | 4.2709 | 1.5152 | 11.5723 | 1.1993 | 11.2564 | 1.5656 | 1.918 | 3.9551 | 4.953 | 2.2293 | 123.1201 | 2.7237 | 123.436 | -122.3511 | -122.5296 | 2.4124 | 5.2689 | 2.1652 | 8.4778
4818.1719 | 122.8821 | -4.7699 | 118.0023 | -0.1445 | 0.0025443 | 0.10966 | 0.0036765 | 0.0016556 | 0.019709 | 0.024221 | -0.12036 | 0.32752 | 0.059174 | -0.0031446 | -0.0049241 | 0.13221 | 0.015407 | -2.4078 | -1.799 | -5.1819 | -2.092 | -2.4719 | -2.5726 | -2.0828 | 19.2535 | 117.8696 | -5.2368 | 1.7441 | 0.71411 | 16.0309 | -2.6459 | -0.41199 | -119.8013 | -120.0943 | 2.298 | 2.6871 | 2.1973 | 3.0991 | 2.6093 | -0.46692 | -0.13275 | -116.2582 | 5.484 | 2.124 | 20.8008 | 2.5909 | 21.2677 | 2.71 | 3.0899 | 5.9509 | 6.9809 | 3.3829 | 123.1064 | 2.9709 | 122.6395 | -123.1842 | -123.2391 | 2.6779 | 6.514 | 2.3621 | 24.0234
4819.1719 | 122.8958 | -5.9738 | 117.0456 | -0.014801 | 0.0053213 | 0.12312 | 0.0028219 | 0.00080117 | 0.018 | 0.021443 | -0.12952 | 0.36832 | 0.082245 | -0.0010084 | -0.0038559 | 0.1196 | 0.012629 | -2.7328 | -1.9913 | -6.7612 | -2.2705 | -3.1723 | -2.9068 | -2.2018 | 22.9385 | 116.2537 | -6.6147 | 2.2339 | 0.60425 | 18.3517 | -2.7603 | -0.78735 | -119.0369 | -119.3161 | 2.8015 | 3.772 | 3.067 | 4.5593 | 3.8544 | -0.64087 | -0.79193 | -114.8117 | 6.5781 | 3.2135 | 24.3256 | 3.8544 | 24.9664 | 3.5889 | 4.4907 | 7.2189 | 8.8486 | 4.7699 | 122.8683 | 3.9825 | 122.2275 | -123.8068 | -123.6603 | 3.7033 | 8.2077 | 3.241 | 28.9124
4820.1719 | 122.8134 | -10.8124 | 111.9461 | -0.068207 | 0.0087393 | 0.24104 | -0.0029459 | -0.0011214 | 0.034022 | 0.043019 | -0.25769 | 0.70755 | 0.1427 | -0.0027174 | -0.0021469 | 0.2623 | -0.00040166 | -5.0583 | -3.8498 | -11.1511 | -4.1565 | -5.7632 | -5.2917 | -4.0466 | 41.1804 | 111.7722 | -11.1008 | 3.4195 | 1.1673 | 36.1771 | 5.3696 | -0.33874 | -115.7959 | -116.1026 | 5.0491 | 6.7657 | 5.5206 | 7.1045 | 5.8594 | -0.28839 | -0.17395 | -108.5266 | 11.9797 | 16.1819 | 46.9894 | 16.4703 | 47.2778 | 5.3879 | 6.9946 | 12.2681 | 14.5203 | 7.3013 | 122.8729 | 6.9626 | 122.5845 | -123.0972 | -123.0469 | 6.6559 | 14.2319 | 5.7541 | 51.9928
4821.1719 | 122.7905 | -11.2518 | 111.5341 | -0.060578 | 0.0085257 | 0.23421 | -0.0027323 | -0.0017624 | 0.029108 | 0.032125 | -0.20886 | 0.60544 | 0.15146 | -0.00058098 | -0.0034287 | 0.18155 | -0.0038197 | -4.5914 | -3.4653 | -11.0504 | -3.8315 | -5.3833 | -4.7836 | -3.6804 | 36.7538 | 111.8271 | -11.0825 | 3.5248 | 0.99792 | 38.9923 | 5.2505 | 0.20142 | -114.9994 | -115.3656 | 5.8685 | 7.5714 | 6.4682 | 7.37 | 6.2668 | 0.16937 | 0.29297 | -108.0093 | 12.2498 | 16.5024 | 50.2441 | 16.333 | 50.0748 | 5.6671 | 7.2189 | 12.0804 | 14.6072 | 7.5851 | 122.9095 | 7.7866 | 123.0789 | -122.5845 | -122.6166 | 7.4203 | 14.7766 | 6.6605 | 48.0057
4822.1719 | 122.905 | -6.7062 | 115.8508 | -0.068207 | 0.0046805 | 0.1714 | 0.0011129 | -5.343e-05 | 0.018641 | 0.020803 | -0.11426 | 0.44458 | 0.11151 | -0.0037854 | -0.0012925 | 0.13242 | -0.0036059 | -3.4378 | -2.2705 | -6.9214 | -2.417 | -3.2501 | -3.1586 | -2.3758 | 15.4816 | 116.3864 | -6.3354 | 2.8198 | 1.181 | 14.1815 | 3.7354 | -0.21515 | -118.1213 | -118.2678 | 3.4561 | 4.3304 | 3.5477 | 4.5456 | 3.7628 | 0.37079 | 0.53558 | -113.031 | 7.8873 | 10.4416 | 20.8878 | 10.0708 | 20.517 | 3.6713 | 4.5044 | 7.5165 | 9.1553 | 4.6509 | 122.7219 | 4.4357 | 123.0927 | -122.7722 | -122.1863 | 4.2892 | 9.5261 | 3.2684 | 22.1878
4823.1719 | 122.7127 | -42.746 | 79.7195 | -0.10635 | 0.050823 | 1.3811 | -0.044816 | 0.00058737 | 0.17245 | 0.19918 | -1.5211 | 0.65458 | 1.9423 | 0.0058276 | 3.1428 | 0.074529 | -0.0025379 | -21.0571 | -8.7662 | -42.5491 | -16.9418 | -21.8582 | -22.2794 | -16.452 | 48.8983 | 79.2801 | -42.7094 | 10.6522 | 79.1702 | 53.5172 | 17.7612 | 0.19684 | -88.4857 | -96.6614 | 20.8878 | 26.2939 | 20.4666 | 26.0971 | 20.2698 | 0.036621 | -0.43945 | -69.0674 | 121.9162 | 60.5072 | 96.2631 | 60.4706 | 96.2265 | 20.6909 | 25.6073 | 121.8796 | 53.3615 | 33.783 | 121.9894 | 33.9798 | 122.0261 | -122.2687 | -122.4289 | 25.8041 | 53.3981 | 21.6888 | 91.6443
4824.1719 | 122.6944 | -0.34332 | 122.4792 | -0.075836 | -0.0015145 | 0.013533 | 0.0085897 | -0.00069423 | 0.00048269 | -0.0014142 | 0.026123 | 0.0015295 | 0.016449 | 0.0051868 | 0.018147 | -0.0055799 | 0.0023755 | -0.18768 | 0.073242 | -0.38452 | -0.23346 | -0.15564 | -0.2243 | -0.16479 | -0.13733 | 0.27008 | -0.39368 | -0.10529 | 0.041199 | -0.15106 | -0.10529 | -0.041198 | -122.406 | -122.7127 | 0.18768 | 0.17853 | 0.11902 | 0.21973 | 0.16022 | -0.050354 | -122.2092 | -122.5845 | 0.38452 | 0.23804 | 0.19226 | 0.28839 | 0.24261 | 0.22888 | 0.15106 | 0.43488 | 0.28839 | 0.45776 | 0.66376 | 0.41656 | 0.6134 | -122.8638 | -122.8729 | 0.10986 | 0.23804 | 0.15564 | 0.20599
4825.1719 | 122.7631 | -0.33417 | 122.5204 | -0.03006 | -0.0023691 | 0.013106 | 0.0060263 | 0.00037377 | -0.00058531 | -0.002055 | 0.023071 | 0.0025975 | 0.01709 | 0.0051868 | 0.016438 | -0.0055799 | -0.0012561 | -0.19684 | 0.073242 | -0.35706 | -0.24719 | -0.16479 | -0.2243 | -0.15106 | -0.17395 | 0.27008 | -0.36163 | -0.14191 | 0 | -0.16479 | -0.10529 | -0.022889 | -122.4472 | -122.7676 | 0.16937 | 0.1831 | 0.10986 | 0.20599 | 0.13275 | -0.027466 | -122.2504 | -122.6624 | 0.33417 | 0.22888 | 0.16937 | 0.25635 | 0.19684 | 0.19226 | 0.10986 | 0.36163 | 0.21973 | 0.4303 | 0.63171 | 0.40741 | 0.60425 | -122.8775 | -122.8821 | 0.086975 | 0.19226 | 0.13733 | 0.16022
4826.1719 | 122.7356 | -0.37537 | 122.5113 | -0.0071715 | 0.0012625 | 0.017378 | 0.0079489 | 0.00037377 | -0.0010125 | 0.00072199 | 0.010864 | 0.0047339 | 0.015808 | 0.0043322 | 0.017934 | -0.0060071 | 0.0028027 | -0.21973 | 0.050354 | -0.40283 | -0.27466 | -0.20142 | -0.25177 | -0.16479 | -0.17395 | 0.29297 | -0.40283 | -0.13733 | 0 | -0.1831 | -0.14648 | -0.027466 | -122.4609 | -122.7859 | 0.17395 | 0.21057 | 0.1236 | 0.23804 | 0.15106 | -0.027466 | -122.2183 | -122.6486 | 0.37537 | 0.22888 | 0.19226 | 0.25635 | 0.21973 | 0.20142 | 0.12817 | 0.40283 | 0.2655 | 0.45319 | 0.6958 | 0.42572 | 0.66833 | -122.9141 | -122.9141 | 0.10071 | 0.23804 | 0.15564 | 0.20142
4827.1719 | 122.7631 | -0.37537 | 122.4976 | -0.12161 | -0.0013009 | 0.012892 | 0.0077353 | 0.001442 | -0.00037171 | -0.00013241 | 0.041382 | 0.0023839 | 0.015167 | 0.00091422 | 0.019643 | -0.0062207 | -0.0023243 | -0.21057 | 0.036621 | -0.41199 | -0.25177 | -0.16937 | -0.25177 | -0.16479 | -0.16479 | 0.28381 | -0.40283 | -0.15564 | -0.032043 | -0.17395 | -0.14191 | -0.036621 | -122.4609 | -122.7493 | 0.20599 | 0.21057 | 0.1236 | 0.24719 | 0.16022 | -0.027466 | -122.2137 | -122.6532 | 0.34332 | 0.23346 | 0.20142 | 0.26093 | 0.22888 | 0.24261 | 0.16022 | 0.37079 | 0.24719 | 0.44861 | 0.68664 | 0.41199 | 0.65918 | -122.9095 | -122.9004 | 0.1236 | 0.21973 | 0.16479 | 0.21057
4828.1719 | 122.7585 | -0.38452 | 122.5296 | -0.045319 | -0.00023294 | 0.016951 | 0.0058127 | 0.00037377 | 0.0011237 | 0.002431 | 0.032227 | 0.0021703 | 0.016663 | 0.0034778 | 0.019215 | -0.0092115 | -0.00018806 | -0.18768 | 0.036621 | -0.41199 | -0.23346 | -0.14191 | -0.21973 | -0.13275 | -0.13733 | 0.27466 | -0.41199 | -0.13733 | -0.022888 | -0.17395 | -0.15106 | -0.027466 | -122.493 | -122.7631 | 0.24261 | 0.25177 | 0.16479 | 0.27924 | 0.19226 | -0.027466 | -122.2549 | -122.6669 | 0.36163 | 0.23346 | 0.21057 | 0.26092 | 0.23804 | 0.27008 | 0.17853 | 0.3891 | 0.27466 | 0.44861 | 0.68664 | 0.42114 | 0.65918 | -122.9416 | -122.9416 | 0.15106 | 0.24719 | 0.19684 | 0.24719
4829.1719 | 122.7859 | -0.37994 | 122.5342 | -0.075836 | 0.00040806 | 0.014174 | 0.0073081 | -0.0026168 | -0.00037171 | 0.00050839 | 0.03833 | 0.0019567 | 0.015808 | 0.0064684 | 0.018361 | -0.0057935 | -0.0038197 | -0.23346 | 0.068665 | -0.41657 | -0.27008 | -0.16937 | -0.24719 | -0.17853 | -0.16937 | 0.2655 | -0.40741 | -0.16022 | -0.027466 | -0.1831 | -0.13733 | -0.036621 | -122.4655 | -122.8043 | 0.21057 | 0.20142 | 0.13275 | 0.23804 | 0.16937 | -0.027466 | -122.2687 | -122.6944 | 0.35248 | 0.24261 | 0.19684 | 0.27008 | 0.22431 | 0.24719 | 0.14648 | 0.37994 | 0.24719 | 0.48523 | 0.67291 | 0.44861 | 0.64545 | -122.9507 | -122.9416 | 0.10986 | 0.21973 | 0.14649 | 0.21057
4830.1719 | 122.7814 | -0.35248 | 122.5616 | -0.022431 | -0.0010873 | 0.013533 | 0.0098715 | -0.00048063 | -0.0010125 | -0.0024822 | 0.016968 | 0.0013159 | 0.017517 | 0.008391 | 0.019002 | -0.0075025 | -0.0040333 | -0.21057 | 0.054932 | -0.40283 | -0.25177 | -0.17853 | -0.24261 | -0.16479 | -0.17853 | 0.27008 | -0.39825 | -0.13275 | -0.041199 | -0.1831 | -0.11902 | -0.050354 | -122.5067 | -122.8134 | 0.17395 | 0.18768 | 0.10986 | 0.23804 | 0.16022 | -0.045776 | -122.2916 | -122.6944 | 0.31128 | 0.23346 | 0.16937 | 0.27924 | 0.21515 | 0.2243 | 0.15106 | 0.35706 | 0.2655 | 0.45776 | 0.66834 | 0.40741 | 0.62256 | -122.9645 | -122.9599 | 0.10071 | 0.21973 | 0.14191 | 0.17395
4831.1719 | 122.7814 | -0.34332 | 122.5616 | -0.037689 | -0.0021555 | 0.01396 | 0.0077353 | -0.0015488 | -0.00037171 | -0.00098701 | 0.013916 | 0.0030249 | 0.016449 | 0.0034778 | 0.019429 | -0.0066479 | 2.554e-05 | -0.20142 | 0.054932 | -0.37994 | -0.26093 | -0.16022 | -0.25177 | -0.15106 | -0.16937 | 0.28381 | -0.37537 | -0.15564 | -0.045776 | -0.1831 | -0.11902 | -0.036621 | -122.5067 | -122.8226 | 0.18311 | 0.19226 | 0.091553 | 0.22888 | 0.12817 | -0.032043 | -122.2778 | -122.7173 | 0.29755 | 0.2243 | 0.16022 | 0.25635 | 0.19226 | 0.21973 | 0.11902 | 0.32959 | 0.21973 | 0.43488 | 0.65918 | 0.39825 | 0.62714 | -122.9416 | -122.937 | 0.082398 | 0.18768 | 0.14191 | 0.17395
4832.1719 | 122.7951 | -0.33875 | 122.5754 | -0.091095 | 0.0021171 | 0.013533 | 0.0066671 | -5.343e-05 | -0.0025079 | -0.002696 | 0.010864 | 0.0025975 | 0.018372 | 0.011382 | 0.018574 | -0.0070753 | -0.0036059 | -0.21973 | 0.050354 | -0.39368 | -0.24261 | -0.15564 | -0.24261 | -0.14648 | -0.17853 | 0.28381 | -0.3891 | -0.15106 | -0.050354 | -0.19684 | -0.12817 | -0.054932 | -122.525 | -122.818 | 0.18311 | 0.19226 | 0.09613 | 0.24719 | 0.15106 | -0.050354 | -122.2916 | -122.7264 | 0.28839 | 0.21057 | 0.14191 | 0.26092 | 0.19226 | 0.23804 | 0.15106 | 0.33874 | 0.23804 | 0.44403 | 0.67291 | 0.3891 | 0.62256 | -122.9691 | -122.9645 | 0.09613 | 0.18768 | 0.11902 | 0.16022
4833.1719 | 122.7997 | -0.33417 | 122.58 | -0.052948 | -0.0010873 | 0.015028 | 0.0079489 | -0.00048063 | -0.0016535 | -0.0022686 | 0.010864 | 0.00088875 | 0.018158 | 0.00070062 | 0.019002 | -0.0066479 | -0.00061526 | -0.16479 | 0.064087 | -0.36621 | -0.22888 | -0.14191 | -0.2243 | -0.1236 | -0.15106 | 0.25635 | -0.37079 | -0.13733 | -0.027466 | -0.14191 | -0.10529 | -0.032044 | -122.5159 | -122.8088 | 0.19226 | 0.21057 | 0.10986 | 0.24262 | 0.14191 | -0.036622 | -122.3236 | -122.7173 | 0.3067 | 0.22888 | 0.19226 | 0.2655 | 0.22888 | 0.2243 | 0.13733 | 0.34332 | 0.23346 | 0.4303 | 0.62714 | 0.39825 | 0.59052 | -122.9462 | -122.9507 | 0.10528 | 0.19684 | 0.16937 | 0.1831
4834.1719 | 122.937 | -0.29755 | 122.58 | -0.12161 | -1.9142e-05 | 0.012679 | 0.0053853 | -0.00048063 | -0.00079891 | -0.0022686 | 0.03833 | 0.0011023 | 0.019226 | 0.0034778 | 0.019002 | -0.0066479 | -0.0042469 | -0.13275 | 0.045776 | -0.32501 | -0.1236 | -0.027466 | -0.10986 | -0.054932 | -0.036621 | 0.21057 | -0.32959 | -0.045776 | 0.064087 | -0.050354 | -0.022888 | -0.027466 | -122.5342 | -122.7036 | 0.27008 | 0.24261 | 0.18768 | 0.27008 | 0.21515 | -0.032044 | -122.3694 | -122.6257 | 0.36163 | 0.27466 | 0.24719 | 0.3067 | 0.27924 | 0.29755 | 0.20142 | 0.39368 | 0.28381 | 0.37079 | 0.54016 | 0.34332 | 0.50812 | -122.905 | -122.9095 | 0.17395 | 0.25177 | 0.16479 | 0.26092
4835.1719 | 122.9233 | -0.27008 | 122.5754 | -0.075836 | -0.00087374 | 0.013106 | 0.0070943 | 0.0018692 | 0.00069649 | -0.00077341 | 0.059692 | 0.0025975 | 0.015808 | 0.0019824 | 0.017934 | -0.0062207 | -0.0029651 | -0.11444 | 0.018311 | -0.31586 | -0.10986 | 0 | -0.10071 | -0.036621 | -0.018311 | 0.22888 | -0.31586 | -0.041199 | 0.073242 | -0.045776 | -0.004578 | -0.045776 | -122.5571 | -122.6852 | 0.27008 | 0.23346 | 0.16937 | 0.27924 | 0.21515 | -0.045776 | -122.3465 | -122.6166 | 0.34332 | 0.2655 | 0.22431 | 0.31128 | 0.27008 | 0.31586 | 0.20599 | 0.3891 | 0.27466 | 0.33417 | 0.54474 | 0.28839 | 0.49896 | -122.8912 | -122.8912 | 0.16022 | 0.22888 | 0.15564 | 0.25177
4836.1719 | 122.8134 | -0.3067 | 122.6349 | -0.045319 | 0.00062166 | 0.012038 | 0.0079489 | 0.001442 | -0.00037171 | -0.0018414 | -0.0074462 | 0.0047339 | 0.019012 | 0.0041186 | 0.019856 | -0.0060071 | 0.00045294 | -0.15106 | 0.050354 | -0.3479 | -0.19684 | -0.10529 | -0.1831 | -0.1236 | -0.13275 | 0.26093 | -0.33875 | -0.13733 | -0.009155 | -0.15106 | -0.10071 | -0.041198 | -122.5845 | -122.8317 | 0.20142 | 0.18311 | 0.1236 | 0.2243 | 0.16479 | -0.032043 | -122.374 | -122.7722 | 0.29755 | 0.20599 | 0.15564 | 0.23804 | 0.18768 | 0.24261 | 0.15106 | 0.32959 | 0.20142 | 0.39825 | 0.59967 | 0.35706 | 0.56763 | -122.9828 | -122.9736 | 0.10986 | 0.16937 | 0.15564 | 0.17395
4837.1719 | 122.8546 | -0.29755 | 122.6028 | -0.045319 | -0.00087374 | 0.012465 | 0.0073081 | -5.343e-05 | 0.0024053 | 0.00093559 | 0.02002 | 0.0023839 | 0.018372 | 0.0058276 | 0.017293 | -0.0072889 | -0.0046741 | -0.11444 | 0.045776 | -0.32044 | -0.15564 | -0.064087 | -0.13733 | -0.086975 | -0.07782 | 0.24261 | -0.33417 | -0.10986 | -0.004578 | -0.13275 | -0.073242 | -0.022889 | -122.5571 | -122.7585 | 0.23346 | 0.21057 | 0.16022 | 0.23346 | 0.18311 | -0.036621 | -122.3602 | -122.7127 | 0.29297 | 0.2243 | 0.16479 | 0.26092 | 0.20142 | 0.25635 | 0.1648 | 0.32959 | 0.2243 | 0.36621 | 0.57678 | 0.34332 | 0.54016 | -122.9233 | -122.937 | 0.14191 | 0.18768 | 0.1831 | 0.21973
4838.1719 | 122.8958 | -0.28381 | 122.6074 | -0.045319 | -0.00044654 | 0.014387 | 0.0070943 | -0.00048063 | 5.5488e-05 | -0.00098701 | 0.010864 | 0.0017431 | 0.016022 | 0.0026232 | 0.016438 | -0.0068615 | -0.0016833 | -0.11902 | 0.045776 | -0.32959 | -0.1236 | -0.027466 | -0.11444 | -0.068665 | -0.054932 | 0.23346 | -0.32501 | -0.068665 | 0.050354 | -0.086975 | -0.022888 | -0.045777 | -122.5616 | -122.731 | 0.25635 | 0.21515 | 0.16937 | 0.26092 | 0.21515 | -0.041199 | -122.374 | -122.6761 | 0.33417 | 0.26092 | 0.19684 | 0.30212 | 0.23804 | 0.30212 | 0.20599 | 0.37537 | 0.25635 | 0.37537 | 0.55847 | 0.32959 | 0.51727 | -122.937 | -122.9324 | 0.16022 | 0.21515 | 0.16479 | 0.22888
4839.1719 | 122.937 | -0.27008 | 122.5983 | -0.060578 | 0.00040806 | 0.014601 | 0.0081625 | -0.00048063 | 0.0017645 | 0.0020038 | 0.023071 | 0.0023839 | 0.016449 | 0.003905 | 0.019429 | -0.0089979 | -0.0040333 | -0.10986 | 0.032043 | -0.31128 | -0.10986 | -0.009155 | -0.11444 | -0.054932 | -0.032043 | 0.21515 | -0.31128 | -0.045776 | 0.07782 | -0.050354 | 0.004578 | -0.041198 | -122.5662 | -122.7081 | 0.26093 | 0.21515 | 0.15564 | 0.25635 | 0.19684 | -0.041198 | -122.3831 | -122.644 | 0.3479 | 0.27466 | 0.21973 | 0.31586 | 0.26092 | 0.30212 | 0.20142 | 0.3891 | 0.2655 | 0.34332 | 0.52643 | 0.30212 | 0.48523 | -122.9095 | -122.9095 | 0.16022 | 0.22431 | 0.16022 | 0.23804
4840.1719 | 122.9553 | -0.27924 | 122.6074 | -0.052948 | -1.9142e-05 | 0.013533 | 0.0083761 | -0.00048063 | 5.5488e-05 | -0.00098701 | 0.059692 | 0.00024775 | 0.017517 | 0.010741 | 0.019002 | -0.0075025 | -0.0010425 | -0.10529 | 0.013733 | -0.31586 | -0.11902 | 0 | -0.10986 | -0.027466 | 0.004578 | 0.22888 | -0.31128 | -0.032043 | 0.09613 | -0.036621 | -0.009155 | -0.036621 | -122.5937 | -122.7264 | 0.27924 | 0.25177 | 0.16937 | 0.28839 | 0.20599 | -0.032043 | -122.3785 | -122.6395 | 0.37537 | 0.27008 | 0.24261 | 0.30212 | 0.27466 | 0.31586 | 0.19684 | 0.40741 | 0.27924 | 0.32959 | 0.54016 | 0.29297 | 0.50812 | -122.9233 | -122.9187 | 0.16022 | 0.24719 | 0.17395 | 0.28381
4841.1719 | 122.9736 | -0.27466 | 122.612 | -0.052948 | -1.9142e-05 | 0.014387 | 0.0092307 | -0.0034714 | -0.0010125 | 8.1188e-05 | 0.02002 | 0.0028113 | 0.017303 | 0.0013416 | 0.017293 | -0.0064343 | 0.0017345 | -0.13275 | 0.050354 | -0.33417 | -0.14648 | -0.050354 | -0.15564 | -0.054932 | -0.054932 | 0.22888 | -0.32501 | -0.027466 | 0.073242 | -0.050354 | 0.004578 | -0.059509 | -122.5616 | -122.7585 | 0.2243 | 0.21973 | 0.11902 | 0.27924 | 0.17853 | -0.050354 | -122.3831 | -122.6395 | 0.3479 | 0.27924 | 0.2243 | 0.32959 | 0.27466 | 0.28381 | 0.18768 | 0.39825 | 0.29755 | 0.38452 | 0.55389 | 0.32501 | 0.50354 | -122.9462 | -122.937 | 0.12817 | 0.24719 | 0.14191 | 0.21973
4842.1719 | 122.9599 | -0.27466 | 122.6028 | -0.098725 | -0.0013009 | 0.014601 | 0.0079489 | -0.0021896 | -0.0016535 | 0.00093559 | 0.02002 | 0.0023839 | 0.016449 | 0.0058276 | 0.018147 | -0.0077161 | -0.0012561 | -0.15564 | 0.041199 | -0.32959 | -0.13733 | -0.07782 | -0.16022 | -0.07782 | -0.073242 | 0.2243 | -0.32959 | -0.059509 | 0.073242 | -0.07782 | -0.013733 | -0.054932 | -122.5616 | -122.7402 | 0.19684 | 0.19684 | 0.11444 | 0.25177 | 0.16937 | -0.054932 | -122.3785 | -122.6624 | 0.3479 | 0.26093 | 0.19684 | 0.31586 | 0.25177 | 0.25177 | 0.19226 | 0.40283 | 0.27008 | 0.37079 | 0.55389 | 0.31586 | 0.49896 | -122.9324 | -122.9324 | 0.13733 | 0.21515 | 0.11902 | 0.20142
4843.1719 | 122.9736 | -0.27008 | 122.6166 | -0.037689 | -0.00066014 | 0.014815 | 0.0083761 | -0.0017624 | -0.0012261 | -0.00055961 | -0.0074462 | 0.0017431 | 0.015594 | 0.011382 | 0.016225 | -0.0085705 | -0.0051013 | -0.11444 | 0.036621 | -0.3067 | -0.11444 | 0.004578 | -0.10071 | -0.036621 | 0.027466 | 0.20142 | -0.33417 | -0.018311 | 0.09613 | -0.041199 | 0.009155 | -0.036621 | -122.58 | -122.731 | 0.27466 | 0.23346 | 0.16937 | 0.27008 | 0.20599 | -0.064086 | -122.4152 | -122.6349 | 0.36621 | 0.27924 | 0.22888 | 0.34332 | 0.29297 | 0.31128 | 0.19226 | 0.4303 | 0.31586 | 0.34332 | 0.53558 | 0.3067 | 0.4715 | -122.9233 | -122.9507 | 0.15564 | 0.25177 | 0.15564 | 0.29755
4844.1719 | 122.9828 | -0.27008 | 122.5937 | -0.068207 | -1.9142e-05 | 0.013533 | 0.0070943 | -0.0015488 | -0.00079891 | 0.00050839 | 0.023071 | 0.0015295 | 0.018158 | 0.00048702 | 0.016865 | -0.0062207 | -0.0031787 | -0.14191 | 0.045776 | -0.32959 | -0.10529 | -0.022888 | -0.12817 | -0.041199 | 0.013733 | 0.21515 | -0.31586 | -0.009155 | 0.10529 | -0.018311 | 0.022888 | -0.059509 | -122.5479 | -122.699 | 0.24719 | 0.22888 | 0.14191 | 0.28839 | 0.20142 | -0.045776 | -122.3785 | -122.6028 | 0.37537 | 0.29297 | 0.25177 | 0.33875 | 0.29755 | 0.3067 | 0.2243 | 0.42114 | 0.3067 | 0.37537 | 0.53101 | 0.31586 | 0.48523 | -122.9233 | -122.9095 | 0.1648 | 0.26093 | 0.12817 | 0.28381
4845.1719 | 122.9736 | -0.28381 | 122.6212 | -0.083466 | -0.0010873 | 0.013533 | 0.0064535 | -0.0021896 | -0.00015811 | -0.0016278 | 0.010864 | 0.0013159 | 0.014954 | 0.0051868 | 0.01772 | -0.0066479 | 0.0025891 | -0.13275 | 0.036621 | -0.32501 | -0.13275 | -0.045776 | -0.13733 | -0.054932 | -0.041199 | 0.21515 | -0.34332 | -0.022888 | 0.082397 | -0.032043 | 0.013733 | -0.041199 | -122.5845 | -122.7539 | 0.23804 | 0.22888 | 0.14648 | 0.27008 | 0.18768 | -0.05951 | -122.406 | -122.644 | 0.36621 | 0.29755 | 0.25177 | 0.35706 | 0.31128 | 0.27924 | 0.19226 | 0.42572 | 0.32043 | 0.36163 | 0.55847 | 0.32043 | 0.49896 | -122.9462 | -122.9645 | 0.15106 | 0.26092 | 0.15106 | 0.24261
4846.1719 | 122.9828 | -0.27924 | 122.5983 | -0.091095 | 0.00040806 | 0.01631 | 0.0094443 | 0.00037377 | -0.00037171 | 0.00093559 | 0.0078126 | 0.00067495 | 0.016022 | 0.0017688 | 0.018788 | -0.0038709 | 0.0021619 | -0.15564 | 0.041199 | -0.32044 | -0.13733 | -0.068665 | -0.16479 | -0.082397 | -0.059509 | 0.20599 | -0.32501 | -0.041199 | 0.064087 | -0.054932 | 0 | -0.041199 | -122.5571 | -122.7356 | 0.21057 | 0.19684 | 0.11444 | 0.23804 | 0.15564 | -0.045776 | -122.3923 | -122.6395 | 0.34332 | 0.27924 | 0.2243 | 0.32501 | 0.27008 | 0.25177 | 0.18311 | 0.3891 | 0.28381 | 0.36163 | 0.53101 | 0.32043 | 0.48523 | -122.9187 | -122.9233 | 0.14191 | 0.23804 | 0.1236 | 0.21973
4847.1719 | 122.9782 | -0.2655 | 122.6349 | -0.083466 | 0.0014761 | 0.014815 | 0.0077353 | -0.00069423 | 0.0011237 | 0.0015766 | 0.016968 | 0.0021703 | 0.015808 | 0.007323 | 0.018147 | -0.0057935 | -0.0031787 | -0.15106 | 0.041199 | -0.32044 | -0.16937 | -0.07782 | -0.17853 | -0.07782 | -0.082397 | 0.21973 | -0.33875 | -0.045776 | 0.041199 | -0.073242 | -0.018311 | -0.054932 | -122.5937 | -122.8043 | 0.18768 | 0.18768 | 0.086975 | 0.24262 | 0.14191 | -0.073242 | -122.4152 | -122.6807 | 0.3067 | 0.24719 | 0.19226 | 0.32043 | 0.2655 | 0.24262 | 0.15106 | 0.37994 | 0.29297 | 0.36163 | 0.55847 | 0.3067 | 0.48523 | -122.9553 | -122.9736 | 0.09613 | 0.21973 | 0.11444 | 0.18311
4848.1719 | 122.8775 | -0.3067 | 122.6257 | -0.052948 | -0.0023691 | 0.015242 | 0.0098715 | 0.00016017 | -0.0018671 | -0.002696 | -0.095947 | 0.0036657 | 0.016663 | 0.0092456 | 0.016865 | -0.0057935 | -0.0031787 | -0.13275 | 0.064087 | -0.36163 | -0.18768 | -0.091553 | -0.21057 | -0.13733 | -0.082397 | 0.25177 | -0.34332 | -0.068665 | -0.018311 | -0.11902 | -0.041199 | -0.054931 | -122.5616 | -122.8134 | 0.21515 | 0.16937 | 0.096131 | 0.2243 | 0.15106 | -0.036621 | -122.374 | -122.6944 | 0.28839 | 0.2655 | 0.18768 | 0.30212 | 0.2243 | 0.27008 | 0.17395 | 0.32501 | 0.27466 | 0.42572 | 0.59509 | 0.37079 | 0.55847 | -122.9874 | -122.9691 | 0.11902 | 0.23804 | 0.17395 | 0.2243
4849.1719 | 122.9233 | -0.27466 | 122.612 | -0.13687 | -0.0019417 | 0.013533 | 0.010085 | 0.00058737 | -0.0029351 | 0.0011494 | -0.025757 | 0.0017431 | 0.015808 | 0.0058276 | 0.018574 | -0.0055799 | -0.0018971 | -0.14191 | 0.022888 | -0.31586 | -0.15564 | -0.041199 | -0.17395 | -0.082397 | -0.073242 | 0.20599 | -0.31586 | -0.050354 | 0.032043 | -0.086975 | -0.036621 | -0.041199 | -122.5891 | -122.7676 | 0.23346 | 0.19226 | 0.10071 | 0.23346 | 0.14191 | -0.041199 | -122.406 | -122.6624 | 0.3067 | 0.23804 | 0.18768 | 0.27924 | 0.22888 | 0.27466 | 0.16022 | 0.3479 | 0.2655 | 0.33875 | 0.52185 | 0.29755 | 0.48065 | -122.9279 | -122.9279 | 0.11902 | 0.2243 | 0.13275 | 0.20142
4850.1719 | 122.9645 | -0.28381 | 122.6212 | -0.091095 | -0.0038643 | 0.013319 | 0.0098715 | 0.00037377 | -0.00058531 | -0.002055 | 0.010864 | 0.0025975 | 0.014954 | -0.00058098 | 0.018788 | -0.0075025 | -0.0025379 | -0.16479 | 0.045776 | -0.32044 | -0.17395 | -0.091553 | -0.18768 | -0.07782 | -0.10986 | 0.23804 | -0.32501 | -0.050354 | 0.054932 | -0.07782 | -0.022888 | -0.036622 | -122.5754 | -122.7951 | 0.19226 | 0.20599 | 0.09613 | 0.24262 | 0.13275 | -0.041199 | -122.3831 | -122.6715 | 0.33874 | 0.26092 | 0.20599 | 0.30212 | 0.24719 | 0.22888 | 0.14649 | 0.37994 | 0.27466 | 0.36621 | 0.56305 | 0.32959 | 0.52185 | -122.9416 | -122.9462 | 0.10986 | 0.23346 | 0.11902 | 0.17395
4851.1719 | 122.9599 | -0.27924 | 122.6395 | -0.052948 | 0.00083526 | 0.015883 | 0.0083761 | 0.00058737 | -0.00037171 | 0.0011494 | -0.010498 | 0.0015295 | 0.016876 | 0.0077502 | 0.020283 | -0.0077161 | -0.0057423 | -0.16937 | 0.050354 | -0.32959 | -0.16479 | -0.07782 | -0.17853 | -0.082397 | -0.10529 | 0.21057 | -0.34332 | -0.059509 | 0.041199 | -0.10986 | -0.027466 | -0.050354 | -122.5891 | -122.8043 | 0.20142 | 0.19684 | 0.10071 | 0.24719 | 0.15106 | -0.064087 | -122.4289 | -122.699 | 0.32043 | 0.25177 | 0.16937 | 0.31586 | 0.23346 | 0.25177 | 0.16479 | 0.38452 | 0.28381 | 0.37994 | 0.55389 | 0.32959 | 0.48981 | -122.9691 | -122.9828 | 0.11444 | 0.21973 | 0.10986 | 0.17395
4852.1719 | 122.9599 | -0.27466 | 122.6212 | -0.12924 | -0.00066014 | 0.013533 | 0.0088033 | 0.0016556 | -0.0020807 | -0.00055961 | -0.022705 | 0.0017431 | 0.015381 | 0.0079638 | 0.019429 | -0.0060071 | -0.0018971 | -0.16479 | 0.045776 | -0.33875 | -0.15106 | -0.082397 | -0.16937 | -0.086975 | -0.09613 | 0.21515 | -0.32501 | -0.07782 | 0.036621 | -0.10071 | -0.032043 | -0.064087 | -122.5754 | -122.7722 | 0.19226 | 0.18768 | 0.10529 | 0.25177 | 0.16937 | -0.050354 | -122.406 | -122.699 | 0.31128 | 0.24262 | 0.17395 | 0.29297 | 0.2243 | 0.25635 | 0.18768 | 0.36163 | 0.24719 | 0.38452 | 0.54016 | 0.32043 | 0.48981 | -122.9599 | -122.9462 | 0.1236 | 0.19684 | 0.10986 | 0.17853
4853.1719 | 122.8638 | -0.32044 | 122.6395 | -0.022431 | -0.0017281 | 0.012679 | 0.0092307 | 0.0029374 | -0.0027215 | 0.0015766 | -0.034912 | 0.0043065 | 0.017517 | 0.0036914 | 0.019215 | -0.0060071 | -0.0031787 | -0.20142 | 0.07782 | -0.35706 | -0.22888 | -0.13733 | -0.21973 | -0.14648 | -0.17395 | 0.25177 | -0.3479 | -0.13275 | -0.050354 | -0.16022 | -0.07782 | -0.036621 | -122.5616 | -122.8683 | 0.18311 | 0.17395 | 0.10071 | 0.21057 | 0.13733 | -0.027465 | -122.3877 | -122.7722 | 0.27008 | 0.24262 | 0.16022 | 0.27008 | 0.18768 | 0.21973 | 0.12817 | 0.29755 | 0.21515 | 0.43488 | 0.59967 | 0.39826 | 0.57221 | -122.9965 | -122.9874 | 0.091553 | 0.18768 | 0.11902 | 0.14649
4854.1719 | 122.9645 | -0.27924 | 122.6212 | -0.060578 | -0.0021555 | 0.013106 | 0.0090169 | -0.00090783 | -0.00037171 | 8.1188e-05 | -0.0043946 | 0.0019567 | 0.018372 | 0.001128 | 0.017506 | -0.0070753 | -0.0023243 | -0.14191 | 0.022888 | -0.32501 | -0.15564 | -0.045776 | -0.19684 | -0.082397 | -0.082397 | 0.21973 | -0.33417 | -0.059509 | 0.027466 | -0.10071 | -0.022888 | -0.045776 | -122.5983 | -122.7768 | 0.23346 | 0.19684 | 0.082398 | 0.24262 | 0.12817 | -0.054931 | -122.4014 | -122.6807 | 0.3067 | 0.25635 | 0.17853 | 0.31128 | 0.23346 | 0.27924 | 0.16937 | 0.36163 | 0.27466 | 0.3479 | 0.55389 | 0.30212 | 0.49896 | -122.9462 | -122.9553 | 0.1236 | 0.21973 | 0.13733 | 0.19684
4855.1719 | 123.0057 | -0.25635 | 122.612 | -0.15976 | -0.00066014 | 0.015456 | 0.0088033 | 0.0010148 | -0.00015811 | -0.0018414 | -0.041016 | 0.0030249 | 0.015808 | 0.0049732 | 0.017293 | -0.0064343 | -0.0046741 | -0.10071 | 0.027466 | -0.31586 | -0.11444 | -0.022888 | -0.16022 | -0.082397 | -0.022888 | 0.19684 | -0.31586 | -0.004578 | 0.068665 | -0.07782 | 0.022888 | -0.059509 | -122.5845 | -122.7264 | 0.23346 | 0.17395 | 0.096131 | 0.23346 | 0.15564 | -0.059509 | -122.4152 | -122.6166 | 0.32501 | 0.27924 | 0.17853 | 0.33875 | 0.23804 | 0.29297 | 0.20142 | 0.38452 | 0.31128 | 0.34332 | 0.5127 | 0.28381 | 0.45319 | -122.9279 | -122.9279 | 0.14191 | 0.25177 | 0.15564 | 0.23346
4856.1719 | 122.9645 | -0.25177 | 122.5983 | -0.11398 | 0.0012625 | 0.015669 | 0.0081625 | 0.0040054 | 0.0026191 | 0.0011494 | -0.059326 | 0.0013159 | 0.014099 | 0.011382 | 0.017934 | -0.0045117 | -0.0023243 | -0.10071 | 0.027466 | -0.32959 | -0.11902 | -0.018311 | -0.14648 | -0.068665 | -0.027466 | 0.21057 | -0.32501 | -0.004578 | 0.086975 | -0.064087 | 0.009155 | -0.07782 | -122.5708 | -122.7173 | 0.23346 | 0.1831 | 0.10529 | 0.26092 | 0.18311 | -0.073242 | -122.3877 | -122.6028 | 0.33874 | 0.26093 | 0.18768 | 0.33417 | 0.26093 | 0.31128 | 0.21057 | 0.41199 | 0.32043 | 0.35706 | 0.53558 | 0.27924 | 0.46234 | -122.9279 | -122.9233 | 0.13275 | 0.24719 | 0.15106 | 0.2243
4857.1719 | 122.9416 | -0.28839 | 122.6028 | -0.10635 | -0.0027963 | 0.012679 | 0.0081625 | -0.00026703 | -0.00079891 | -0.00055961 | -0.022705 | 0.0017431 | 0.016022 | 0.0041186 | 0.016438 | -0.0068615 | -0.0029651 | -0.14648 | 0.045776 | -0.29755 | -0.16479 | -0.064087 | -0.18768 | -0.07782 | -0.091553 | 0.21973 | -0.31128 | -0.059509 | 0.027466 | -0.09613 | -0.013733 | -0.009155 | -122.5571 | -122.7676 | 0.2243 | 0.21057 | 0.10071 | 0.21973 | 0.10986 | -0.022888 | -122.3831 | -122.6624 | 0.31586 | 0.27466 | 0.19226 | 0.29755 | 0.21515 | 0.23346 | 0.13275 | 0.33874 | 0.25177 | 0.34332 | 0.53101 | 0.33417 | 0.50812 | -122.9004 | -122.9141 | 0.1236 | 0.22888 | 0.14191 | 0.19684
4858.1719 | 122.8546 | -0.32501 | 122.6395 | -0.083466 | -0.00023294 | 0.014387 | 0.010085 | -0.00069423 | 0.00069649 | 0.0022174 | -0.019653 | 0.0019567 | 0.013672 | 0.0094592 | 0.018574 | -0.0075025 | -0.0046741 | -0.16479 | 0.064087 | -0.3479 | -0.21515 | -0.10986 | -0.20142 | -0.13275 | -0.16479 | 0.25177 | -0.35248 | -0.13275 | -0.027466 | -0.15564 | -0.091553 | -0.022888 | -122.5754 | -122.8546 | 0.21515 | 0.19226 | 0.1236 | 0.21515 | 0.14648 | -0.027466 | -122.3877 | -122.7722 | 0.29755 | 0.23346 | 0.16937 | 0.26093 | 0.19684 | 0.23804 | 0.13275 | 0.32501 | 0.21973 | 0.41199 | 0.60425 | 0.3891 | 0.57678 | -122.9874 | -122.9919 | 0.10986 | 0.19226 | 0.16022 | 0.16022
4859.1719 | 122.9874 | -0.28839 | 122.6028 | -0.15213 | 0.0010489 | 0.014601 | 0.0088033 | 0.0016556 | -0.0016535 | -0.00034601 | -0.034912 | 0.00046135 | 0.016022 | 0.0068958 | 0.018361 | -0.0072889 | 0.00066654 | -0.13733 | 0.022888 | -0.32501 | -0.13733 | -0.032043 | -0.16937 | -0.082397 | -0.032043 | 0.20599 | -0.34332 | -0.027466 | 0.050354 | -0.086975 | -0.013733 | -0.036621 | -122.58 | -122.7402 | 0.25635 | 0.20599 | 0.11902 | 0.24262 | 0.15564 | -0.054932 | -122.3969 | -122.6303 | 0.33875 | 0.27466 | 0.20142 | 0.32959 | 0.25635 | 0.29297 | 0.18768 | 0.39368 | 0.31586 | 0.3479 | 0.54932 | 0.31128 | 0.49439 | -122.9279 | -122.9462 | 0.15106 | 0.26093 | 0.15106 | 0.25635
4860.1719 | 122.9507 | -0.29297 | 122.6028 | -0.13687 | 0.00019446 | 0.015242 | 0.0090169 | 0.00251 | -0.00015811 | 0.00029479 | -0.019653 | 0.0017431 | 0.012817 | 0.010314 | 0.01772 | -0.0064343 | -0.0025379 | -0.14191 | 0.036621 | -0.32959 | -0.15106 | -0.032043 | -0.15564 | -0.091553 | -0.050354 | 0.20599 | -0.33875 | -0.004578 | 0.068665 | -0.064087 | -0.004578 | -0.036621 | -122.5662 | -122.7539 | 0.26093 | 0.20142 | 0.13733 | 0.23804 | 0.17395 | -0.045776 | -122.3969 | -122.6074 | 0.36163 | 0.28839 | 0.22888 | 0.33417 | 0.27466 | 0.29755 | 0.17853 | 0.40741 | 0.33417 | 0.36621 | 0.54474 | 0.32959 | 0.49896 | -122.9324 | -122.9416 | 0.14191 | 0.28839 | 0.15106 | 0.24261
4861.1719 | 122.9736 | -0.29297 | 122.612 | -0.10635 | -0.0015145 | 0.016524 | 0.0083761 | -0.0021896 | -0.0018671 | 0.0028582 | -0.025757 | 0.0019567 | 0.015381 | 0.0049732 | 0.019429 | -0.0068615 | -0.0046741 | -0.12817 | 0.022888 | -0.33417 | -0.13275 | -0.022888 | -0.16937 | -0.068665 | -0.032043 | 0.20599 | -0.32044 | -0.022888 | 0.059509 | -0.068665 | 0.022888 | -0.041198 | -122.5891 | -122.7448 | 0.27008 | 0.2243 | 0.1236 | 0.2655 | 0.16479 | -0.027466 | -122.406 | -122.6349 | 0.35248 | 0.31586 | 0.2243 | 0.34332 | 0.25177 | 0.31128 | 0.20142 | 0.37994 | 0.29755 | 0.35706 | 0.52643 | 0.31586 | 0.49896 | -122.9462 | -122.9324 | 0.16022 | 0.27008 | 0.16479 | 0.26093
4862.1719 | 122.9874 | -0.27466 | 122.6074 | -0.10635 | -0.0015145 | 0.015669 | 0.0081625 | 0.0022964 | 0.00069649 | 0.00029479 | -0.034912 | 0.0023839 | 0.013031 | 0.0028368 | 0.018574 | -0.0055799 | -0.0012561 | -0.12817 | 0.013733 | -0.33875 | -0.12817 | -0.032043 | -0.15564 | -0.064087 | -0.032043 | 0.20599 | -0.33875 | 0 | 0.064087 | -0.050354 | 0.018311 | -0.064087 | -122.5937 | -122.7356 | 0.24262 | 0.21057 | 0.11902 | 0.27466 | 0.18311 | -0.064087 | -122.4014 | -122.6074 | 0.33875 | 0.29297 | 0.2243 | 0.35706 | 0.28839 | 0.3067 | 0.21057 | 0.40283 | 0.33875 | 0.35248 | 0.54474 | 0.28839 | 0.48065 | -122.9462 | -122.9462 | 0.14648 | 0.27466 | 0.14648 | 0.24262
4863.1719 | 122.9828 | -0.28839 | 122.6028 | -0.052948 | -0.00044654 | 0.017378 | 0.01094 | 0.0012284 | 0.0021917 | 0.001363 | -0.050171 | 0.0017431 | 0.01474 | 0.008391 | 0.017079 | -0.0045117 | -0.0036059 | -0.16937 | 0.041199 | -0.36163 | -0.17395 | -0.086975 | -0.20142 | -0.10071 | -0.064087 | 0.21515 | -0.33875 | -0.009155 | 0.050354 | -0.07782 | 0.013733 | -0.073242 | -122.5616 | -122.7768 | 0.20142 | 0.18768 | 0.086975 | 0.26092 | 0.16022 | -0.050354 | -122.3877 | -122.612 | 0.33875 | 0.30212 | 0.21057 | 0.35248 | 0.26093 | 0.27466 | 0.18768 | 0.3891 | 0.32959 | 0.40283 | 0.55389 | 0.32959 | 0.50354 | -122.9645 | -122.9416 | 0.11444 | 0.27924 | 0.11902 | 0.2243
4864.1719 | 122.9782 | -0.27008 | 122.6349 | -0.1445 | -0.0017281 | 0.014174 | 0.0092307 | 0.00251 | -0.00079891 | -0.0014142 | -0.056274 | 0.0028113 | 0.013245 | 0.008391 | 0.019429 | -0.0066479 | -0.0044605 | -0.1236 | 0.009155 | -0.32959 | -0.13733 | -0.018311 | -0.16937 | -0.073242 | -0.036621 | 0.21057 | -0.32044 | -0.009155 | 0.059509 | -0.082397 | -0.004578 | -0.059509 | -122.6257 | -122.7722 | 0.25177 | 0.19684 | 0.10071 | 0.25635 | 0.16022 | -0.050354 | -122.4243 | -122.644 | 0.32959 | 0.2655 | 0.18768 | 0.31586 | 0.23804 | 0.31128 | 0.19226 | 0.37994 | 0.31128 | 0.33875 | 0.53101 | 0.27924 | 0.48065 | -122.9645 | -122.9553 | 0.13275 | 0.26093 | 0.14649 | 0.23346
4865.1719 | 122.9965 | -0.28839 | 122.6074 | -0.13687 | -0.00023294 | 0.016951 | 0.010085 | 0.00016017 | -0.00015811 | 8.1188e-05 | -0.016602 | 0.0011023 | 0.014099 | 0.0041186 | 0.018147 | -0.0070753 | -0.0014697 | -0.12817 | 0.022888 | -0.33417 | -0.14191 | -0.041199 | -0.15106 | -0.082397 | -0.027466 | 0.21057 | -0.33875 | 0.013733 | 0.064087 | -0.07782 | 0.018311 | -0.045776 | -122.5845 | -122.7493 | 0.24719 | 0.20599 | 0.13733 | 0.25177 | 0.1831 | -0.050354 | -122.3969 | -122.5937 | 0.35248 | 0.3067 | 0.21057 | 0.35706 | 0.26093 | 0.29297 | 0.19226 | 0.40283 | 0.35248 | 0.35706 | 0.54932 | 0.31128 | 0.49896 | -122.9416 | -122.9462 | 0.14648 | 0.30212 | 0.16022 | 0.26093
4866.1719 | 123.0011 | -0.25177 | 122.6349 | -0.12161 | -0.00023294 | 0.015669 | 0.0075217 | -0.0011214 | 5.5488e-05 | -0.00013241 | -0.03186 | 0.0015295 | 0.013458 | 0.0024096 | 0.019002 | -0.0064343 | -0.0068103 | -0.11444 | 0.022888 | -0.31586 | -0.12817 | -0.036621 | -0.15564 | -0.068665 | -0.032043 | 0.19684 | -0.31586 | -0.004578 | 0.073242 | -0.073242 | 0.018311 | -0.064087 | -122.612 | -122.7631 | 0.21515 | 0.1831 | 0.09613 | 0.24719 | 0.16022 | -0.064087 | -122.4381 | -122.6395 | 0.32501 | 0.27008 | 0.17853 | 0.33417 | 0.24261 | 0.27924 | 0.18768 | 0.3891 | 0.31128 | 0.33875 | 0.5127 | 0.27466 | 0.44861 | -122.9507 | -122.9507 | 0.1236 | 0.24719 | 0.13733 | 0.21973
4867.1719 | 123.0057 | -0.28381 | 122.6303 | -0.10635 | 0.00019446 | 0.015883 | 0.0073081 | 0.004219 | -0.0025079 | 0.0022174 | -0.050171 | 0.00088875 | 0.014099 | 0.0024096 | 0.017293 | -0.0040845 | -0.0014697 | -0.11902 | 0.032043 | -0.31586 | -0.14191 | -0.041199 | -0.14648 | -0.07782 | -0.036621 | 0.20142 | -0.34332 | -0.013733 | 0.073242 | -0.064087 | 0.013733 | -0.032044 | -122.5983 | -122.7722 | 0.24261 | 0.20599 | 0.13733 | 0.23804 | 0.16937 | -0.05951 | -122.4289 | -122.644 | 0.35706 | 0.29755 | 0.21973 | 0.35706 | 0.27924 | 0.27466 | 0.17395 | 0.41656 | 0.32959 | 0.3479 | 0.54474 | 0.31586 | 0.48523 | -122.9462 | -122.9736 | 0.14191 | 0.27008 | 0.16479 | 0.24719
4868.1719 | 123.0148 | -0.26093 | 122.6349 | -0.12924 | -0.00023294 | 0.013747 | 0.0094443 | 0.00037377 | 0.00091009 | -0.0014142 | -0.044067 | 0.0011023 | 0.016663 | 0.0049732 | 0.017293 | -0.0051527 | -0.0012561 | -0.11902 | 0.036621 | -0.3067 | -0.11902 | -0.036621 | -0.14648 | -0.07782 | -0.036621 | 0.19684 | -0.32501 | 0.009155 | 0.082397 | -0.059509 | 0.027466 | -0.045777 | -122.5983 | -122.7539 | 0.2243 | 0.18311 | 0.11444 | 0.22888 | 0.16022 | -0.064087 | -122.4381 | -122.6257 | 0.34332 | 0.28839 | 0.20142 | 0.35248 | 0.2655 | 0.27008 | 0.18768 | 0.40741 | 0.33417 | 0.34332 | 0.52185 | 0.29755 | 0.45776 | -122.9416 | -122.9599 | 0.14191 | 0.27008 | 0.14191 | 0.2243
4869.1719 | 122.9279 | -0.27924 | 122.644 | -0.091095 | -0.0013009 | 0.013106 | 0.010299 | 0.00080117 | -0.00079891 | -0.002055 | -0.041016 | 0.0034521 | 0.016235 | 0.0032642 | 0.018147 | -0.0064343 | -0.0036059 | -0.19684 | 0.073242 | -0.34332 | -0.23346 | -0.13275 | -0.26093 | -0.13733 | -0.11902 | 0.2243 | -0.33875 | -0.059509 | 0 | -0.12817 | -0.004578 | -0.064087 | -122.5708 | -122.8775 | 0.14648 | 0.14191 | 0.018311 | 0.20599 | 0.082398 | -0.059509 | -122.4197 | -122.7036 | 0.27924 | 0.27466 | 0.15106 | 0.33417 | 0.21057 | 0.21057 | 0.10986 | 0.33875 | 0.27924 | 0.41656 | 0.56305 | 0.35248 | 0.50354 | -122.9874 | -122.9828 | 0.045777 | 0.21973 | 0.082398 | 0.16022
4870.1719 | 122.9324 | -0.31586 | 122.6486 | -0.11398 | -0.0013009 | 0.015242 | 0.010085 | 0.00058737 | 0.00091009 | 0.0015766 | -0.071533 | 0.0040929 | 0.016449 | 0.0028368 | 0.019215 | -0.0062207 | -0.00040166 | -0.18768 | 0.082397 | -0.35706 | -0.24719 | -0.13733 | -0.2655 | -0.14191 | -0.15564 | 0.24719 | -0.34332 | -0.082397 | -0.013733 | -0.14648 | -0.032043 | -0.041199 | -122.5662 | -122.8958 | 0.17853 | 0.17395 | 0.050354 | 0.21515 | 0.091553 | -0.027466 | -122.4014 | -122.731 | 0.30212 | 0.28381 | 0.16937 | 0.31128 | 0.19684 | 0.21973 | 0.10986 | 0.32959 | 0.26093 | 0.43945 | 0.59052 | 0.39825 | 0.56305 | -123.0057 | -122.9919 | 0.068665 | 0.23346 | 0.12817 | 0.16022
4871.1719 | 123.0194 | -0.25177 | 122.6212 | -0.052948 | -0.00066014 | 0.016524 | 0.0085897 | -0.00026703 | -0.0012261 | 0.00029479 | -0.016602 | 0.00067495 | 0.014954 | 0.0047594 | 0.017506 | -0.0081433 | -0.0040333 | -0.10529 | 0.036621 | -0.31586 | -0.13733 | -0.022888 | -0.15106 | -0.064087 | -0.045776 | 0.21057 | -0.31128 | 0.004578 | 0.059509 | -0.073242 | 0.018311 | -0.064087 | -122.5845 | -122.7585 | 0.22888 | 0.18768 | 0.10071 | 0.25177 | 0.16479 | -0.059509 | -122.4106 | -122.6166 | 0.31128 | 0.27008 | 0.17853 | 0.32959 | 0.23804 | 0.29297 | 0.17853 | 0.37079 | 0.31586 | 0.35248 | 0.52185 | 0.28839 | 0.46234 | -122.937 | -122.9324 | 0.11444 | 0.25635 | 0.14648 | 0.20599
4872.1719 | 123.0011 | -0.24261 | 122.6212 | -0.12924 | -1.9142e-05 | 0.017378 | 0.0070943 | -0.001976 | 0.00091009 | -0.00013241 | -0.037964 | 0.0021703 | 0.016235 | 0.0019824 | 0.019429 | -0.0066479 | -0.0014697 | -0.11902 | 0.027466 | -0.28381 | -0.13275 | -0.036621 | -0.15106 | -0.07782 | -0.036621 | 0.18768 | -0.3067 | 0 | 0.07782 | -0.064087 | 0.027466 | -0.041198 | -122.5937 | -122.7539 | 0.20599 | 0.16479 | 0.091553 | 0.20599 | 0.13275 | -0.064087 | -122.4335 | -122.6212 | 0.32044 | 0.27008 | 0.17853 | 0.33417 | 0.24261 | 0.24719 | 0.15106 | 0.38452 | 0.3067 | 0.31128 | 0.49438 | 0.27008 | 0.4303 | -122.905 | -122.9279 | 0.10986 | 0.24261 | 0.1236 | 0.20599
4873.2031 | 122.9187 | -0.28381 | 122.6669 | -0.075836 | 0.0016899 | 0.014601 | 0.0085897 | 0.0012284 | 5.5488e-05 | 0.0015766 | -0.074585 | 0.0030249 | 0.017517 | 0.0051868 | 0.018361 | -0.0028027 | 0.0017345 | -0.15106 | 0.059509 | -0.32501 | -0.19684 | -0.07782 | -0.19226 | -0.12817 | -0.091553 | 0.22888 | -0.33417 | -0.064087 | -0.009155 | -0.12817 | -0.022888 | -0.041199 | -122.6074 | -122.8638 | 0.20599 | 0.15564 | 0.091552 | 0.19684 | 0.13275 | -0.050354 | -122.438 | -122.731 | 0.27466 | 0.26092 | 0.15564 | 0.31128 | 0.20599 | 0.24719 | 0.12817 | 0.32501 | 0.27008 | 0.38452 | 0.56305 | 0.34332 | 0.5127 | -122.9919 | -123.0011 | 0.086975 | 0.21973 | 0.13275 | 0.19226
4874.1719 | 122.9919 | -0.26093 | 122.644 | -0.12924 | -0.00044654 | 0.015028 | 0.0090169 | -0.00069423 | -0.00058531 | 0.00029479 | -0.037964 | 0.0032385 | 0.017517 | 0.0026232 | 0.02007 | -0.0060071 | -0.0016833 | -0.12817 | 0.045776 | -0.31128 | -0.14191 | -0.041199 | -0.15564 | -0.091553 | -0.041199 | 0.20142 | -0.30212 | -0.018311 | 0.068665 | -0.054932 | 0.032043 | -0.050354 | -122.5983 | -122.7859 | 0.21973 | 0.16937 | 0.10529 | 0.21973 | 0.15564 | -0.041199 | -122.4426 | -122.6624 | 0.32959 | 0.29297 | 0.20599 | 0.33417 | 0.24719 | 0.27008 | 0.16937 | 0.37079 | 0.28381 | 0.35705 | 0.50354 | 0.3067 | 0.46234 | -122.9553 | -122.9462 | 0.11902 | 0.24261 | 0.13275 | 0.21973
4875.1719 | 122.9919 | -0.26093 | 122.6624 | -0.075836 | -0.00066014 | 0.016096 | 0.0096579 | 0.0012284 | -0.00037171 | 0.001363 | -0.019653 | 0.0015295 | 0.014526 | 0.00091422 | 0.02007 | -0.0057935 | -0.0012561 | -0.14648 | 0.050354 | -0.33417 | -0.16937 | -0.068665 | -0.15106 | -0.082397 | -0.064087 | 0.18768 | -0.31128 | -0.018311 | 0.073242 | -0.054932 | 0.041199 | -0.073242 | -122.612 | -122.8317 | 0.19226 | 0.17853 | 0.10986 | 0.25177 | 0.1831 | -0.050354 | -122.4747 | -122.6807 | 0.33417 | 0.30212 | 0.20599 | 0.35248 | 0.25635 | 0.2655 | 0.16479 | 0.38452 | 0.29297 | 0.38452 | 0.49896 | 0.31128 | 0.44861 | -122.9965 | -122.9736 | 0.091552 | 0.24261 | 0.11444 | 0.19684
4876.1719 | 122.9324 | -0.28839 | 122.6578 | -0.068207 | -0.00023294 | 0.01396 | 0.01094 | 0.0035782 | 0.00026909 | 0.0017902 | -0.071533 | 0.0017431 | 0.016876 | 0.0054004 | 0.017506 | -0.0053663 | -0.0016833 | -0.19684 | 0.07782 | -0.33875 | -0.23804 | -0.14648 | -0.25635 | -0.15564 | -0.15106 | 0.22888 | -0.32959 | -0.09613 | -0.027466 | -0.15106 | -0.022888 | -0.050354 | -122.58 | -122.8958 | 0.14191 | 0.13275 | 0.032043 | 0.18311 | 0.082397 | -0.041199 | -122.4289 | -122.7539 | 0.26093 | 0.2655 | 0.13733 | 0.3067 | 0.17853 | 0.19226 | 0.10071 | 0.30212 | 0.23346 | 0.41657 | 0.55847 | 0.36621 | 0.51727 | -122.9965 | -122.9874 | 0.050354 | 0.19226 | 0.091553 | 0.13733
4877.1719 | 122.9507 | -0.30212 | 122.699 | -0.052948 | 0.00040806 | 0.016096 | 0.010726 | -0.00090783 | 0.0013373 | -0.00098701 | -0.044067 | 0.00088875 | 0.017731 | 0.010955 | 0.017934 | -0.0057935 | -0.0036059 | -0.14648 | 0.050354 | -0.32501 | -0.19226 | -0.10986 | -0.19684 | -0.14191 | -0.10071 | 0.2243 | -0.32959 | -0.073242 | 0 | -0.11444 | -0.018311 | -0.022888 | -122.6486 | -122.8912 | 0.19226 | 0.16022 | 0.10529 | 0.18311 | 0.12817 | -0.027466 | -122.4747 | -122.7722 | 0.30212 | 0.28381 | 0.18768 | 0.31128 | 0.21515 | 0.21515 | 0.13275 | 0.32959 | 0.25635 | 0.37537 | 0.55389 | 0.35248 | 0.52643 | -123.024 | -123.0286 | 0.10986 | 0.22888 | 0.15564 | 0.20142
4878.2344 | 122.9874 | -0.27466 | 122.644 | -0.12161 | -0.0013009 | 0.015456 | 0.0055991 | -0.0015488 | -0.00079891 | -0.0018414 | 0.062744 | 3.4148e-05 | 0.017303 | 0.0043322 | 0.020283 | -0.0081433 | 0.0045117 | -0.18768 | 0.045776 | -0.31586 | -0.1831 | -0.086975 | -0.17853 | -0.091553 | -0.11444 | 0.21973 | -0.33417 | -0.07782 | 0.054932 | -0.082397 | 0.013733 | -0.041199 | -122.5983 | -122.8271 | 0.18768 | 0.18311 | 0.09613 | 0.2243 | 0.13733 | -0.059509 | -122.4243 | -122.7219 | 0.32959 | 0.28839 | 0.19226 | 0.3479 | 0.25177 | 0.22888 | 0.13275 | 0.3891 | 0.25635 | 0.36163 | 0.55389 | 0.32043 | 0.49439 | -122.9599 | -122.9782 | 0.091553 | 0.19684 | 0.086975 | 0.16022
4879.1719 | 123.0194 | -0.2655 | 122.6532 | -0.052948 | 0.00040806 | 0.015242 | 0.0058127 | -0.0077438 | 0.00048269 | -0.0014142 | 0.026123 | 0.0013159 | 0.015808 | -0.0018628 | 0.01772 | -0.0062207 | -0.00061526 | -0.16479 | 0.050354 | -0.31586 | -0.16479 | -0.073242 | -0.15564 | -0.07782 | -0.10529 | 0.19684 | -0.31586 | -0.059509 | 0.073242 | -0.073242 | 0.032043 | -0.050354 | -122.6028 | -122.818 | 0.19226 | 0.18768 | 0.10986 | 0.23804 | 0.16022 | -0.050354 | -122.4564 | -122.7127 | 0.33874 | 0.29755 | 0.19226 | 0.3479 | 0.24261 | 0.24261 | 0.15106 | 0.3891 | 0.25635 | 0.36621 | 0.5127 | 0.31586 | 0.46234 | -122.9691 | -122.9691 | 0.10071 | 0.20599 | 0.10071 | 0.16022
4880.2188 | 123.0194 | -0.2655 | 122.6669 | -0.037689 | -0.0017281 | 0.01631 | 0.0075217 | -0.0026168 | 0.0013373 | 8.1188e-05 | 0.02002 | 0.0019567 | 0.015167 | 0.0041186 | 0.01772 | -0.0075025 | -0.00082886 | -0.13275 | 0.032043 | -0.3067 | -0.14648 | -0.032043 | -0.13733 | -0.045776 | -0.054932 | 0.19684 | -0.32501 | -0.032043 | 0.082397 | -0.045776 | 0.027466 | -0.041199 | -122.6349 | -122.8134 | 0.23346 | 0.21973 | 0.12817 | 0.26093 | 0.16937 | -0.059509 | -122.4701 | -122.699 | 0.3479 | 0.29297 | 0.21973 | 0.35248 | 0.27924 | 0.27466 | 0.16022 | 0.40741 | 0.29297 | 0.33874 | 0.52185 | 0.29755 | 0.46234 | -122.9736 | -122.9919 | 0.11902 | 0.23346 | 0.13275 | 0.21057
4881.1719 | 123.0011 | -0.24719 | 122.6578 | -0.13687 | -0.00044654 | 0.01631 | 0.01094 | 0.0029374 | 0.00091009 | 8.1188e-05 | -0.056274 | 0.0023839 | 0.014099 | 0.0071094 | 0.016225 | -0.0045117 | -0.0025379 | -0.1831 | 0.054932 | -0.32501 | -0.16479 | -0.082397 | -0.19684 | -0.11902 | -0.07782 | 0.21515 | -0.31128 | -0.018311 | 0.050354 | -0.054932 | 0.027466 | -0.07782 | -122.6028 | -122.8226 | 0.16479 | 0.12817 | 0.050354 | 0.20599 | 0.12817 | -0.064087 | -122.4426 | -122.6761 | 0.29755 | 0.27466 | 0.19226 | 0.33874 | 0.25635 | 0.24262 | 0.16022 | 0.36163 | 0.29297 | 0.37994 | 0.52643 | 0.30212 | 0.46234 | -122.9828 | -122.9691 | 0.082397 | 0.22888 | 0.064087 | 0.16937
4882.1719 | 122.9874 | -0.24719 | 122.6807 | -0.091095 | -0.00087374 | 0.014174 | 0.0077353 | 0.001442 | 0.00048269 | 0.0011494 | 0.02002 | 0.0017431 | 0.015167 | 0.0045458 | 0.017293 | -0.0072889 | -0.0044605 | -0.13275 | 0.013733 | -0.28381 | -0.1236 | -0.004578 | -0.15564 | -0.068665 | -0.041199 | 0.19226 | -0.31128 | -0.018311 | 0.059509 | -0.073242 | 0.018311 | -0.036621 | -122.6669 | -122.8043 | 0.24261 | 0.17853 | 0.091552 | 0.21515 | 0.12817 | -0.064087 | -122.4884 | -122.699 | 0.3067 | 0.2655 | 0.17395 | 0.32959 | 0.23804 | 0.27923 | 0.16022 | 0.37079 | 0.29297 | 0.29755 | 0.50354 | 0.26093 | 0.43945 | -122.9645 | -122.9919 | 0.1236 | 0.22888 | 0.11444 | 0.20599
4883.1719 | 122.9919 | -0.27008 | 122.6761 | -0.068207 | -0.0017281 | 0.016524 | 0.0088033 | -0.0015488 | -0.0025079 | -0.00055961 | 0.02002 | 0.0028113 | 0.015594 | 0.0086048 | 0.019002 | -0.0085705 | -0.00061526 | -0.16937 | 0.054932 | -0.29755 | -0.17395 | -0.082397 | -0.1831 | -0.073242 | -0.09613 | 0.19684 | -0.32501 | -0.073242 | 0.041199 | -0.11444 | -0.004578 | -0.027465 | -122.6212 | -122.85 | 0.18768 | 0.19684 | 0.086976 | 0.2243 | 0.11444 | -0.054931 | -122.4792 | -122.7493 | 0.31128 | 0.2655 | 0.15564 | 0.32043 | 0.21057 | 0.21515 | 0.1236 | 0.36621 | 0.25177 | 0.35248 | 0.52185 | 0.32501 | 0.46692 | -122.9736 | -123.0011 | 0.096131 | 0.19684 | 0.10071 | 0.17395
4884.1719 | 123.0011 | -0.25635 | 122.6715 | -0.083466 | 0.0010489 | 0.013319 | 0.0070943 | 0.00037377 | 0.0011237 | 0.00050839 | 0.02002 | 0.00067495 | 0.015808 | 0.0032642 | 0.019856 | -0.0060071 | -0.0025379 | -0.14191 | 0.036621 | -0.32501 | -0.16937 | -0.073242 | -0.17395 | -0.086975 | -0.09613 | 0.21515 | -0.31586 | -0.059509 | 0.045776 | -0.082397 | 0.009155 | -0.068664 | -122.6349 | -122.8409 | 0.18311 | 0.16937 | 0.082398 | 0.23804 | 0.15106 | -0.059509 | -122.4564 | -122.731 | 0.30212 | 0.2655 | 0.17395 | 0.32501 | 0.23346 | 0.25177 | 0.15564 | 0.36163 | 0.25635 | 0.36163 | 0.53101 | 0.29297 | 0.4715 | -122.9965 | -122.9874 | 0.086975 | 0.19684 | 0.11444 | 0.16022
4885.1719 | 122.9828 | -0.27008 | 122.6532 | -0.098725 | -0.0019417 | 0.015883 | 0.0096579 | -0.00026703 | -0.0010125 | -0.00098701 | -0.059326 | 0.0034521 | 0.013458 | 0.011809 | 0.017293 | -0.0057935 | -0.0023243 | -0.16479 | 0.041199 | -0.33417 | -0.16479 | -0.064087 | -0.17853 | -0.09613 | -0.064087 | 0.18768 | -0.32959 | -0.022888 | 0.045776 | -0.07782 | 0.041199 | -0.064086 | -122.612 | -122.818 | 0.20599 | 0.17395 | 0.091553 | 0.23804 | 0.15564 | -0.059509 | -122.4655 | -122.6761 | 0.31586 | 0.31128 | 0.19226 | 0.37079 | 0.25177 | 0.27008 | 0.16937 | 0.37537 | 0.3067 | 0.37537 | 0.51727 | 0.31128 | 0.45776 | -122.9874 | -122.9828 | 0.10529 | 0.24719 | 0.10529 | 0.20599
4886.1719 | 122.9736 | -0.26093 | 122.6715 | -0.091095 | -0.0017281 | 0.013533 | 0.0098715 | -0.0043258 | -0.0037897 | 0.00072199 | -0.044067 | 0.0025975 | 0.015381 | 0.0079638 | 0.018788 | -0.0053663 | 2.554e-05 | -0.16937 | 0.068665 | -0.32959 | -0.18768 | -0.091553 | -0.21973 | -0.12817 | -0.09613 | 0.19226 | -0.3067 | -0.027466 | 0.036621 | -0.091553 | 0.032043 | -0.068665 | -122.6028 | -122.8592 | 0.16937 | 0.13275 | 0.041198 | 0.20142 | 0.10986 | -0.045777 | -122.4792 | -122.699 | 0.29755 | 0.29297 | 0.16937 | 0.33874 | 0.21515 | 0.23804 | 0.14191 | 0.34332 | 0.27924 | 0.39826 | 0.49896 | 0.32959 | 0.45319 | -123.0011 | -122.9782 | 0.073242 | 0.23346 | 0.091552 | 0.1648
4887.1719 | 122.9691 | -0.2655 | 122.6761 | -0.091095 | -0.00023294 | 0.016524 | 0.011367 | 0.0044328 | -0.0025079 | 0.001363 | -0.074585 | 0.0049475 | 0.015808 | 0.0043322 | 0.019856 | -0.0049389 | 0.0010937 | -0.17853 | 0.059509 | -0.33417 | -0.21515 | -0.12817 | -0.22888 | -0.13733 | -0.1236 | 0.19226 | -0.33417 | -0.032043 | 0.022888 | -0.11444 | -0.004578 | -0.068664 | -122.6166 | -122.8912 | 0.13733 | 0.12817 | 0.036621 | 0.19684 | 0.10528 | -0.068664 | -122.4838 | -122.7081 | 0.28839 | 0.26092 | 0.15106 | 0.32959 | 0.21973 | 0.20599 | 0.11902 | 0.35706 | 0.30212 | 0.39368 | 0.52643 | 0.32501 | 0.45776 | -123.0103 | -123.0103 | 0.050354 | 0.23346 | 0.086975 | 0.14191
4888.1719 | 122.9141 | -0.32501 | 122.6807 | -0.045319 | -0.0025827 | 0.015242 | 0.0088033 | -0.0015488 | 0.0019781 | -0.0022686 | -0.019653 | 0.0011023 | 0.016235 | 0.0068958 | 0.019643 | -0.0077161 | 0.0019483 | -0.20599 | 0.082397 | -0.34332 | -0.23346 | -0.15106 | -0.21973 | -0.14648 | -0.21057 | 0.24261 | -0.35248 | -0.14191 | -0.027466 | -0.16479 | -0.064087 | -0.018311 | -122.5983 | -122.9141 | 0.17395 | 0.17853 | 0.10529 | 0.19684 | 0.1236 | -0.027466 | -122.438 | -122.8226 | 0.29755 | 0.26093 | 0.16022 | 0.28839 | 0.18768 | 0.19226 | 0.10986 | 0.32501 | 0.21057 | 0.42572 | 0.59509 | 0.40741 | 0.56763 | -123.024 | -123.0331 | 0.091553 | 0.18311 | 0.11902 | 0.11444
4889.1719 | 122.8775 | -0.29297 | 122.7036 | -0.068207 | -0.0015145 | 0.012679 | 0.0090169 | -0.00048063 | 0.00048269 | 8.1188e-05 | -0.010498 | 0.0030249 | 0.017944 | 0.0066822 | 0.019215 | -0.0060071 | -0.0031787 | -0.20142 | 0.059509 | -0.3479 | -0.23804 | -0.14191 | -0.22888 | -0.15106 | -0.1831 | 0.2243 | -0.35248 | -0.14191 | -0.036621 | -0.17853 | -0.064087 | -0.054931 | -122.644 | -122.9416 | 0.15106 | 0.14191 | 0.064087 | 0.19684 | 0.11902 | -0.059509 | -122.4792 | -122.8455 | 0.25635 | 0.22888 | 0.11444 | 0.28839 | 0.17395 | 0.20599 | 0.10986 | 0.31586 | 0.21057 | 0.40741 | 0.57678 | 0.35248 | 0.51727 | -123.0515 | -123.056 | 0.054932 | 0.15106 | 0.091553 | 0.10986
4890.1719 | 122.9095 | -0.28381 | 122.7081 | -0.1445 | -0.00087374 | 0.01631 | 0.0094443 | 0.0027238 | -0.0018671 | 0.0015766 | -0.056274 | 0.0025975 | 0.013458 | 0.0079638 | 0.018574 | -0.0047253 | -0.0016833 | -0.18768 | 0.059509 | -0.3479 | -0.23804 | -0.16022 | -0.25635 | -0.18768 | -0.17853 | 0.19684 | -0.35248 | -0.10529 | -0.036621 | -0.18768 | -0.050354 | -0.064087 | -122.6486 | -122.9462 | 0.1236 | 0.09613 | 0.027465 | 0.16022 | 0.091552 | -0.068665 | -122.5113 | -122.8134 | 0.24719 | 0.23346 | 0.09613 | 0.30212 | 0.1648 | 0.18768 | 0.10986 | 0.31586 | 0.24719 | 0.40741 | 0.54932 | 0.34332 | 0.48065 | -123.056 | -123.0606 | 0.045776 | 0.17853 | 0.09613 | 0.10528
4891.1719 | 122.9645 | -0.27008 | 122.699 | -0.075836 | -0.00066014 | 0.014174 | 0.0098715 | 0.0018692 | -0.0016535 | 0.00093559 | -0.034912 | 0.0030249 | 0.017731 | 0.0096728 | 0.01772 | -0.0040845 | -0.0021107 | -0.18768 | 0.068665 | -0.33875 | -0.21515 | -0.13275 | -0.2243 | -0.14648 | -0.13275 | 0.21057 | -0.32501 | -0.059509 | 0.013733 | -0.10986 | -0.009155 | -0.068664 | -122.6303 | -122.9141 | 0.13733 | 0.1236 | 0.045777 | 0.19226 | 0.11444 | -0.054931 | -122.4884 | -122.7585 | 0.28381 | 0.26093 | 0.16022 | 0.31586 | 0.21515 | 0.20599 | 0.1236 | 0.33875 | 0.2655 | 0.40741 | 0.53558 | 0.33875 | 0.48065 | -123.0377 | -123.024 | 0.054932 | 0.21057 | 0.082398 | 0.13733
4892.1719 | 122.9233 | -0.27924 | 122.7081 | -0.098725 | -0.0017281 | 0.013533 | 0.012008 | 0.0018692 | -0.00079891 | 0.003072 | -0.025757 | 0.0017431 | 0.018799 | 0.0054004 | 0.019643 | -0.0045117 | -0.0018971 | -0.21057 | 0.068665 | -0.32959 | -0.23346 | -0.14648 | -0.25635 | -0.14648 | -0.16022 | 0.21515 | -0.31586 | -0.07782 | -0.018311 | -0.14648 | -0.032043 | -0.050354 | -122.6395 | -122.9416 | 0.13275 | 0.13275 | 0.022888 | 0.18311 | 0.073242 | -0.036621 | -122.493 | -122.7859 | 0.26092 | 0.24719 | 0.13275 | 0.28381 | 0.16937 | 0.18311 | 0.096131 | 0.29755 | 0.23804 | 0.39826 | 0.53101 | 0.3479 | 0.49438 | -123.0377 | -123.024 | 0.045777 | 0.20142 | 0.068665 | 0.11902
4893.1719 | 122.9004 | -0.28839 | 122.6944 | -0.083466 | -0.00066014 | 0.015883 | 0.0098715 | 0.0016556 | -0.0010125 | 0.0017902 | -0.034912 | 0.0038793 | 0.016876 | 0.0049732 | 0.01772 | -0.0075025 | -0.0012561 | -0.20142 | 0.054932 | -0.37537 | -0.25635 | -0.17395 | -0.27924 | -0.1831 | -0.1831 | 0.22888 | -0.32959 | -0.09613 | -0.045776 | -0.17395 | -0.050354 | -0.086975 | -122.6395 | -122.9507 | 0.11444 | 0.10529 | 0.009155 | 0.19226 | 0.09613 | -0.041199 | -122.4655 | -122.7905 | 0.24262 | 0.23804 | 0.11444 | 0.27924 | 0.15564 | 0.20142 | 0.11902 | 0.28381 | 0.23346 | 0.4303 | 0.55847 | 0.34332 | 0.51727 | -123.0698 | -123.024 | 0.032043 | 0.19226 | 0.086975 | 0.10529
4894.1719 | 123.0286 | -0.28381 | 122.644 | -0.098725 | -0.0030099 | 0.015028 | 0.0079489 | -0.0049668 | -0.00079891 | 0.0049946 | 0.056641 | 0.00046135 | 0.015381 | -0.0035718 | 0.018788 | -0.0083569 | -0.00082886 | -0.16022 | 0.032043 | -0.32501 | -0.15106 | -0.022888 | -0.12817 | -0.045776 | -0.036621 | 0.20142 | -0.31586 | -0.018311 | 0.10529 | -0.027466 | 0.050354 | -0.041199 | -122.612 | -122.7951 | 0.26092 | 0.23804 | 0.15564 | 0.27924 | 0.19684 | -0.032044 | -122.4426 | -122.6624 | 0.3891 | 0.33417 | 0.25635 | 0.36621 | 0.28839 | 0.30212 | 0.17395 | 0.42114 | 0.29755 | 0.35706 | 0.51727 | 0.31586 | 0.48523 | -122.9691 | -122.9599 | 0.13275 | 0.2655 | 0.1236 | 0.24719
4895.1719 | 123.024 | -0.28839 | 122.6944 | -0.068207 | -0.0017281 | 0.015456 | 0.0051717 | -0.00048063 | -0.00015811 | -0.0031232 | 0.053589 | 0.0034521 | 0.014313 | 0.00070062 | 0.019002 | -0.0068615 | -0.00018806 | -0.14191 | 0.032043 | -0.31128 | -0.15106 | -0.050354 | -0.13733 | -0.064087 | -0.064087 | 0.19684 | -0.30212 | -0.041199 | 0.082397 | -0.022888 | 0.032043 | -0.022888 | -122.6624 | -122.8455 | 0.23804 | 0.2243 | 0.15106 | 0.24719 | 0.17395 | -0.013733 | -122.4976 | -122.7356 | 0.37079 | 0.32043 | 0.2655 | 0.33417 | 0.27924 | 0.26092 | 0.16022 | 0.38452 | 0.26093 | 0.34332 | 0.49896 | 0.32043 | 0.48523 | -123.0057 | -122.9965 | 0.13733 | 0.24719 | 0.14648 | 0.2243
4896.1719 | 123.0057 | -0.23804 | 122.6898 | -0.091095 | -1.9142e-05 | 0.015456 | 0.011581 | 0.001442 | 0.00048269 | -0.00034601 | -0.071533 | 0.0023839 | 0.016235 | 0.0017688 | 0.01772 | -0.0057935 | 0.00023934 | -0.17853 | 0.073242 | -0.32501 | -0.19226 | -0.11902 | -0.21057 | -0.1236 | -0.068665 | 0.19226 | -0.32044 | -0.054932 | 0.045776 | -0.10529 | 0.032043 | -0.086975 | -122.6166 | -122.8821 | 0.11902 | 0.11444 | 0.027466 | 0.20142 | 0.11444 | -0.082398 | -122.4976 | -122.7448 | 0.28381 | 0.27008 | 0.13275 | 0.35248 | 0.21515 | 0.20599 | 0.13275 | 0.36621 | 0.2655 | 0.39825 | 0.5127 | 0.31128 | 0.4303 | -123.0148 | -123.0103 | 0.045776 | 0.1831 | 0.059509 | 0.16937
4897.1719 | 122.9599 | -0.27008 | 122.7173 | -0.11398 | -0.0032235 | 0.014815 | 0.0075217 | -0.0021896 | -0.00079891 | 0.00072199 | -0.071533 | 0.0023839 | 0.017517 | 0.0054004 | 0.019429 | -0.0047253 | -0.0040333 | -0.17853 | 0.068665 | -0.32959 | -0.21973 | -0.13733 | -0.2243 | -0.13733 | -0.13733 | 0.20599 | -0.31128 | -0.068665 | 0.013733 | -0.14191 | 0.004578 | -0.059509 | -122.6486 | -122.937 | 0.13275 | 0.13275 | 0.045777 | 0.19226 | 0.10529 | -0.041198 | -122.5113 | -122.7859 | 0.28381 | 0.27466 | 0.12817 | 0.31586 | 0.16937 | 0.19226 | 0.10986 | 0.32501 | 0.24261 | 0.39826 | 0.51727 | 0.33875 | 0.47608 | -123.0469 | -123.0286 | 0.050354 | 0.20142 | 0.091553 | 0.13275
4898.1719 | 122.905 | -0.28381 | 122.7081 | -0.083466 | 0.00083526 | 0.013319 | 0.0096579 | -0.0043258 | 0.0017645 | -0.0016278 | -0.06543 | 0.0036657 | 0.016876 | 0.0096728 | 0.017293 | -0.0057935 | -0.0027515 | -0.18768 | 0.07782 | -0.33417 | -0.23804 | -0.17853 | -0.26093 | -0.1831 | -0.20599 | 0.2243 | -0.32959 | -0.11902 | -0.068665 | -0.20599 | -0.050354 | -0.050354 | -122.6303 | -122.9462 | 0.10528 | 0.10071 | 0.022888 | 0.15106 | 0.073242 | -0.045777 | -122.4838 | -122.8271 | 0.21515 | 0.23346 | 0.077819 | 0.27924 | 0.1236 | 0.15564 | 0.09613 | 0.26092 | 0.21057 | 0.41199 | 0.55389 | 0.36163 | 0.50812 | -123.0423 | -123.0377 | 0.045776 | 0.16479 | 0.09613 | 0.077819
4899.1719 | 122.905 | -0.29755 | 122.731 | -0.060578 | -0.0010873 | 0.015669 | 0.010085 | 0.001442 | 0.00026909 | -0.00013241 | -0.062378 | 0.0017431 | 0.017517 | 0.0088184 | 0.01772 | -0.0049389 | -0.0036059 | -0.19226 | 0.07782 | -0.32501 | -0.24719 | -0.16937 | -0.26093 | -0.17395 | -0.19684 | 0.21057 | -0.32959 | -0.10071 | -0.059509 | -0.1831 | -0.054932 | -0.027466 | -122.6532 | -122.9782 | 0.12817 | 0.1236 | 0.036621 | 0.15106 | 0.064087 | -0.032044 | -122.5204 | -122.8317 | 0.23804 | 0.24261 | 0.11444 | 0.27466 | 0.14649 | 0.15564 | 0.07782 | 0.27008 | 0.22888 | 0.40283 | 0.54016 | 0.37537 | 0.50812 | -123.056 | -123.0606 | 0.050354 | 0.19684 | 0.10528 | 0.10071
4900.1719 | 122.8821 | -0.29297 | 122.7264 | -0.083466 | -0.0021555 | 0.014815 | 0.011794 | -0.0015488 | -0.00037171 | -0.0014142 | -0.056274 | 0.0028113 | 0.016663 | 0.012236 | 0.018788 | -0.0057935 | -0.0023243 | -0.17395 | 0.082397 | -0.32959 | -0.25177 | -0.15564 | -0.26093 | -0.17395 | -0.19684 | 0.2243 | -0.32044 | -0.14191 | -0.068665 | -0.20142 | -0.068665 | -0.036621 | -122.644 | -122.9782 | 0.13733 | 0.11902 | 0.032044 | 0.15564 | 0.068665 | -0.027466 | -122.5021 | -122.8683 | 0.2243 | 0.2243 | 0.091553 | 0.25177 | 0.11902 | 0.17395 | 0.07782 | 0.25177 | 0.17853 | 0.41199 | 0.54474 | 0.37537 | 0.51727 | -123.056 | -123.0469 | 0.041199 | 0.15106 | 0.11902 | 0.096131
4901.1719 | 122.8821 | -0.28839 | 122.7127 | -0.083466 | -0.00066014 | 0.015028 | 0.0096579 | 0.0037918 | -0.00079891 | 0.00050839 | -0.062378 | 0.0023839 | 0.017731 | 0.0064684 | 0.018788 | -0.0062207 | 0.0021619 | -0.20142 | 0.064087 | -0.33875 | -0.27466 | -0.20142 | -0.30212 | -0.20599 | -0.20599 | 0.21515 | -0.32959 | -0.13275 | -0.064087 | -0.19684 | -0.054932 | -0.050354 | -122.6486 | -122.9874 | 0.086975 | 0.082397 | -0.013733 | 0.13275 | 0.036621 | -0.041199 | -122.4976 | -122.8455 | 0.2243 | 0.23346 | 0.091553 | 0.27466 | 0.13275 | 0.13733 | 0.064087 | 0.2655 | 0.19684 | 0.40283 | 0.54474 | 0.35248 | 0.50354 | -123.0515 | -123.0423 | 0.013733 | 0.15564 | 0.086975 | 0.082397
4902.1719 | 123.0103 | -0.25177 | 122.6944 | -0.037689 | -0.0015145 | 0.016096 | 0.0062399 | -5.343e-05 | -0.0012261 | 0.001363 | 0.02002 | 0.00088875 | 0.016876 | 0.00091422 | 0.019856 | -0.0087843 | 2.554e-05 | -0.15106 | 0.032043 | -0.30212 | -0.16937 | -0.032043 | -0.17853 | -0.10071 | -0.091553 | 0.17395 | -0.30212 | -0.064087 | 0.036621 | -0.10529 | 0.004578 | -0.050354 | -122.6624 | -122.8638 | 0.21973 | 0.15106 | 0.073242 | 0.20142 | 0.1236 | -0.050354 | -122.5204 | -122.7585 | 0.28839 | 0.25635 | 0.14648 | 0.3067 | 0.19684 | 0.27008 | 0.13275 | 0.33875 | 0.23804 | 0.33417 | 0.47607 | 0.28381 | 0.42572 | -122.9965 | -122.9965 | 0.082397 | 0.18768 | 0.10071 | 0.16022
4903.1875 | 122.9004 | -0.28839 | 122.7402 | -0.03006 | -1.9142e-05 | 0.01396 | 0.0077353 | 0.0027238 | 0.0011237 | -0.0012006 | 0.016968 | 0.00088875 | 0.018158 | 0.0017688 | 0.018574 | -0.0066479 | -0.0063831 | -0.17853 | 0.073242 | -0.32044 | -0.24719 | -0.15106 | -0.21515 | -0.15564 | -0.17853 | 0.20599 | -0.32501 | -0.15106 | -0.050354 | -0.16479 | -0.064087 | -0.032044 | -122.6669 | -122.9874 | 0.13733 | 0.13275 | 0.073242 | 0.1648 | 0.10529 | -0.036621 | -122.5342 | -122.8912 | 0.23804 | 0.2243 | 0.1236 | 0.26093 | 0.16022 | 0.16937 | 0.073243 | 0.27466 | 0.17395 | 0.39368 | 0.53101 | 0.36163 | 0.49439 | -123.0606 | -123.0652 | 0.041199 | 0.13733 | 0.10986 | 0.10986
4904.2031 | 122.937 | -0.29297 | 122.7127 | -0.022431 | 0.00040806 | 0.015028 | 0.0083761 | 0.00016017 | 0.00048269 | -0.00013241 | -0.010498 | 0.0034521 | 0.016876 | 0.0026232 | 0.019002 | -0.0070753 | -0.0012561 | -0.17395 | 0.068665 | -0.32959 | -0.2243 | -0.16022 | -0.21515 | -0.16022 | -0.19226 | 0.21973 | -0.33875 | -0.13733 | -0.036621 | -0.16479 | -0.045776 | -0.036621 | -122.644 | -122.937 | 0.13275 | 0.13275 | 0.07782 | 0.16937 | 0.11444 | -0.045776 | -122.493 | -122.85 | 0.25635 | 0.24719 | 0.12817 | 0.29297 | 0.17395 | 0.16937 | 0.10529 | 0.30212 | 0.20142 | 0.39826 | 0.55847 | 0.36163 | 0.5127 | -123.0423 | -123.0515 | 0.068665 | 0.15564 | 0.11902 | 0.10071
4905.1719 | 122.8683 | -0.28839 | 122.7585 | -0.098725 | -1.9142e-05 | 0.016524 | 0.0081625 | -0.00026703 | -0.00037171 | 0.00050839 | -0.074585 | 0.0028113 | 0.016876 | 0.0075366 | 0.016438 | -0.0070753 | -0.00061526 | -0.17853 | 0.045776 | -0.31586 | -0.24261 | -0.16022 | -0.26093 | -0.19226 | -0.20599 | 0.20142 | -0.33417 | -0.14191 | -0.073242 | -0.21515 | -0.068665 | -0.027466 | -122.7127 | -123.0011 | 0.12817 | 0.09613 | 0.027466 | 0.1236 | 0.054932 | -0.045776 | -122.5571 | -122.9004 | 0.21515 | 0.21973 | 0.073242 | 0.2655 | 0.11902 | 0.15564 | 0.073242 | 0.26092 | 0.19226 | 0.36163 | 0.53558 | 0.33417 | 0.48981 | -123.0743 | -123.0927 | 0.045776 | 0.14648 | 0.10986 | 0.082397
4906.1719 | 122.9324 | -0.27466 | 122.7448 | -0.022431 | -0.00023294 | 0.013533 | 0.0098715 | 0.005928 | -0.00015811 | -0.00077341 | -0.050171 | 0.0021703 | 0.018799 | 0.010741 | 0.018361 | -0.0047253 | 2.554e-05 | -0.15564 | 0.064087 | -0.32044 | -0.19684 | -0.09613 | -0.20599 | -0.13275 | -0.12817 | 0.21057 | -0.31128 | -0.11444 | -0.032043 | -0.17853 | -0.027466 | -0.045777 | -122.6807 | -122.9416 | 0.17853 | 0.14191 | 0.068664 | 0.18768 | 0.11444 | -0.036621 | -122.5342 | -122.8592 | 0.24262 | 0.24719 | 0.09613 | 0.28381 | 0.13275 | 0.22431 | 0.1236 | 0.27924 | 0.19684 | 0.38452 | 0.52185 | 0.33875 | 0.48523 | -123.0652 | -123.056 | 0.07782 | 0.16022 | 0.11902 | 0.14648
4907.1719 | 122.9095 | -0.28839 | 122.7356 | -0.060578 | -0.00044654 | 0.015456 | 0.0088033 | 0.0016556 | -0.0012261 | 0.0015766 | -0.06543 | 0.0040929 | 0.015381 | -0.00058098 | 0.02007 | -0.0062207 | -0.0016833 | -0.19226 | 0.068665 | -0.34332 | -0.25635 | -0.17853 | -0.27924 | -0.19226 | -0.23346 | 0.23346 | -0.30212 | -0.13733 | -0.073242 | -0.20142 | -0.041199 | -0.054932 | -122.6669 | -122.9919 | 0.10986 | 0.09613 | 0.009155 | 0.15106 | 0.064087 | -0.013733 | -122.5021 | -122.8729 | 0.21515 | 0.24719 | 0.086975 | 0.26093 | 0.10071 | 0.16479 | 0.086975 | 0.22888 | 0.16479 | 0.41199 | 0.53558 | 0.35706 | 0.52185 | -123.0789 | -123.0377 | 0.032043 | 0.15106 | 0.09613 | 0.054932
4908.2344 | 122.937 | -0.28839 | 122.7036 | -0.0071715 | 0.0012625 | 0.014601 | 0.0096579 | 0.0018692 | -0.0018671 | -0.00077341 | 0.016968 | 0.0023839 | 0.017731 | 0.0041186 | 0.017079 | -0.0047253 | 0.00066654 | -0.14191 | 0.07782 | -0.32959 | -0.20142 | -0.10529 | -0.18768 | -0.12817 | -0.10529 | 0.21057 | -0.32044 | -0.09613 | 0 | -0.1236 | -0.018311 | -0.041199 | -122.6257 | -122.905 | 0.18311 | 0.16022 | 0.10071 | 0.20142 | 0.14191 | -0.032044 | -122.493 | -122.7997 | 0.28839 | 0.27008 | 0.1648 | 0.30212 | 0.19684 | 0.2243 | 0.12817 | 0.32044 | 0.22431 | 0.40741 | 0.53101 | 0.36621 | 0.49896 | -123.0331 | -123.024 | 0.086975 | 0.19226 | 0.14648 | 0.18311
4909.1719 | 122.9599 | -0.27924 | 122.7448 | -0.060578 | -0.0021555 | 0.014815 | 0.011367 | -0.0017624 | 0.0013373 | 0.00029479 | -0.03186 | 0.0025975 | 0.015381 | 0.0028368 | 0.02007 | -0.0066479 | -0.00018806 | -0.14648 | 0.073242 | -0.31586 | -0.21057 | -0.09613 | -0.19684 | -0.1236 | -0.10071 | 0.20599 | -0.32044 | -0.091553 | -0.018311 | -0.13733 | -0.018311 | -0.036621 | -122.6715 | -122.9553 | 0.18311 | 0.15564 | 0.082398 | 0.19226 | 0.11902 | -0.041199 | -122.5388 | -122.8363 | 0.26092 | 0.26092 | 0.14191 | 0.30212 | 0.18311 | 0.21973 | 0.10529 | 0.30212 | 0.22888 | 0.3891 | 0.52643 | 0.35248 | 0.48523 | -123.0606 | -123.0652 | 0.068665 | 0.18768 | 0.13275 | 0.17853
4910.1719 | 122.9416 | -0.2655 | 122.7173 | -0.014801 | -0.0019417 | 0.01631 | 0.0070943 | -5.343e-05 | -0.00058531 | -0.0014142 | -0.016602 | 0.0028113 | 0.016663 | 0.0015552 | 0.019215 | -0.0081433 | -0.0010425 | -0.14191 | 0.050354 | -0.32044 | -0.20599 | -0.10529 | -0.19226 | -0.12817 | -0.1236 | 0.21057 | -0.31128 | -0.09613 | 0.004578 | -0.12817 | -0.022888 | -0.054932 | -122.6669 | -122.9233 | 0.16022 | 0.13733 | 0.073242 | 0.19226 | 0.12817 | -0.045776 | -122.5067 | -122.8134 | 0.27008 | 0.24261 | 0.13733 | 0.28839 | 0.1831 | 0.21515 | 0.11444 | 0.31586 | 0.21515 | 0.37079 | 0.52185 | 0.31586 | 0.47607 | -123.0377 | -123.0286 | 0.059509 | 0.16937 | 0.1236 | 0.14191
4911.1875 | 122.9279 | -0.27466 | 122.699 | -0.075836 | -0.0025827 | 0.015028 | 0.0083761 | 0.0046464 | -0.0010125 | -0.0012006 | -0.025757 | 0.0021703 | 0.018158 | 0.0028368 | 0.019215 | -0.0064343 | 2.554e-05 | -0.21057 | 0.086975 | -0.32959 | -0.27008 | -0.16022 | -0.27466 | -0.17853 | -0.17853 | 0.21515 | -0.31586 | -0.10529 | -0.036621 | -0.1831 | -0.045776 | -0.054932 | -122.612 | -122.9691 | 0.11444 | 0.09613 | 0 | 0.15106 | 0.054932 | -0.041199 | -122.4838 | -122.8043 | 0.23804 | 0.22888 | 0.091553 | 0.27008 | 0.13275 | 0.16937 | 0.059509 | 0.27924 | 0.21057 | 0.41656 | 0.53101 | 0.36163 | 0.48981 | -123.0286 | -123.0148 | 0.004577 | 0.16937 | 0.064087 | 0.09613
4912.75 | 122.9095 | -0.28839 | 122.7356 | -0.098725 | -0.0025827 | 0.015669 | 0.0085897 | 0.00058737 | 0.00048269 | -0.002696 | -0.0074462 | 0.0015295 | 0.016663 | 0.0036914 | 0.017506 | -0.0068615 | 0.0030163 | -0.18768 | 0.054932 | -0.32501 | -0.2655 | -0.16479 | -0.27008 | -0.17395 | -0.18768 | 0.20142 | -0.31586 | -0.13275 | -0.059509 | -0.17395 | -0.045776 | -0.036621 | -122.6807 | -123.0011 | 0.1236 | 0.11444 | 0.01831 | 0.15106 | 0.054931 | -0.027466 | -122.5342 | -122.8683 | 0.22888 | 0.24262 | 0.11444 | 0.27008 | 0.14191 | 0.16022 | 0.059509 | 0.25635 | 0.18311 | 0.37994 | 0.51727 | 0.34332 | 0.48981 | -123.0606 | -123.0515 | 0.022888 | 0.15564 | 0.10071 | 0.10071
4913.6875 | 122.9095 | -0.27924 | 122.731 | -0.052948 | -0.00023294 | 0.01396 | 0.0088033 | -0.00090783 | -0.0020807 | -0.00034601 | 0.035278 | 0.0019567 | 0.017303 | 0.0015552 | 0.020283 | -0.0064343 | -0.0038197 | -0.19684 | 0.054932 | -0.32959 | -0.2655 | -0.16022 | -0.22888 | -0.15564 | -0.18768 | 0.21973 | -0.32501 | -0.14191 | -0.032043 | -0.16022 | -0.050354 | -0.050354 | -122.6761 | -122.9965 | 0.11902 | 0.1236 | 0.050354 | 0.17395 | 0.10071 | -0.045776 | -122.5113 | -122.8729 | 0.24719 | 0.22888 | 0.11902 | 0.27466 | 0.1648 | 0.16937 | 0.064087 | 0.29297 | 0.18311 | 0.38452 | 0.54474 | 0.33417 | 0.49896 | -123.0606 | -123.056 | 0.013733 | 0.13733 | 0.082398 | 0.091553
4915.3594 | 122.9919 | -0.23804 | 122.6944 | -0.037689 | -0.0010873 | 0.01396 | 0.0049581 | 0.00251 | -0.00015811 | -0.00098701 | 0.056641 | 0.0017431 | 0.016022 | 0.0024096 | 0.016865 | -0.0068615 | -0.0018971 | -0.16479 | 0.022888 | -0.28839 | -0.19226 | -0.091553 | -0.17853 | -0.086975 | -0.1236 | 0.17853 | -0.30212 | -0.082397 | 0.032043 | -0.09613 | 0.009155 | -0.050354 | -122.6715 | -122.8867 | 0.14648 | 0.15106 | 0.059509 | 0.20142 | 0.10986 | -0.064087 | -122.5159 | -122.7768 | 0.27008 | 0.24719 | 0.14191 | 0.31128 | 0.20599 | 0.19684 | 0.09613 | 0.33417 | 0.21973 | 0.31128 | 0.48065 | 0.26093 | 0.41656 | -122.9828 | -122.9965 | 0.045776 | 0.15564 | 0.073242 | 0.11444
4915.9531 | 123.0835 | -0.2243 | 122.7173 | -0.083466 | -1.9142e-05 | 0.016524 | 0.0092307 | 0.0022964 | -0.0016535 | 0.00029479 | 0.013916 | 0.0025975 | 0.017517 | 0.0041186 | 0.016652 | -0.0068615 | -0.0040333 | -0.11444 | 0.041199 | -0.30212 | -0.13733 | -0.022888 | -0.14648 | -0.064087 | -0.041199 | 0.19226 | -0.28381 | -0.018311 | 0.054932 | -0.073242 | 0.032043 | -0.07782 | -122.6761 | -122.8546 | 0.20142 | 0.16022 | 0.07782 | 0.23804 | 0.15564 | -0.059509 | -122.525 | -122.7356 | 0.27924 | 0.25635 | 0.15106 | 0.31586 | 0.21057 | 0.27924 | 0.16479 | 0.33874 | 0.2655 | 0.34332 | 0.47607 | 0.2655 | 0.41656 | -123.0194 | -123.0011 | 0.086975 | 0.20599 | 0.10986 | 0.18311
4917.9688 | 122.8958 | -0.29755 | 122.7402 | -0.083466 | 0.0010489 | 0.014815 | 0.0096579 | 0.0020828 | 0.0024053 | 0.002431 | -0.03186 | 0.0040929 | 0.016022 | 0.0043322 | 0.01772 | -0.0083569 | -0.0012561 | -0.19226 | 0.054932 | -0.32501 | -0.2655 | -0.20599 | -0.28839 | -0.21515 | -0.2243 | 0.21973 | -0.32959 | -0.15106 | -0.073242 | -0.20599 | -0.064087 | -0.027466 | -122.6852 | -123.0057 | 0.091552 | 0.082397 | 0.009155 | 0.10986 | 0.036621 | -0.032044 | -122.5204 | -122.8912 | 0.2243 | 0.23346 | 0.091552 | 0.2655 | 0.1236 | 0.11902 | 0.059509 | 0.25635 | 0.17853 | 0.37994 | 0.54932 | 0.35248 | 0.51727 | -123.0652 | -123.0698 | 0.032043 | 0.14648 | 0.10528 | 0.073242
4918.9844 | 122.9507 | -0.29755 | 122.7585 | 0.00045798 | -0.00023294 | 0.013747 | 0.0073081 | 0.00016017 | -0.00058531 | 0.001363 | 0.029175 | 0.0015295 | 0.015808 | 0.0043322 | 0.019002 | -0.0081433 | -0.0027515 | -0.16937 | 0.045776 | -0.31586 | -0.2243 | -0.09613 | -0.18768 | -0.13275 | -0.16937 | 0.21515 | -0.31586 | -0.16022 | -0.032043 | -0.15106 | -0.064087 | -0.018311 | -122.7127 | -122.9828 | 0.20142 | 0.16479 | 0.10986 | 0.18311 | 0.12817 | -0.018311 | -122.5433 | -122.9187 | 0.2655 | 0.23346 | 0.14648 | 0.25177 | 0.16479 | 0.21973 | 0.091553 | 0.28381 | 0.15564 | 0.36163 | 0.53101 | 0.34332 | 0.5127 | -123.0743 | -123.0743 | 0.073242 | 0.13733 | 0.12817 | 0.12817
4919.7031 | 123.0286 | -0.27008 | 122.7264 | -0.098725 | -0.0015145 | 0.015456 | 0.0062399 | -0.0032578 | -0.00079891 | -0.00077341 | 0.056641 | 0.0011023 | 0.017944 | 0.0047594 | 0.018147 | -0.0087843 | -0.0016833 | -0.16937 | 0.036621 | -0.3067 | -0.17395 | -0.082397 | -0.16022 | -0.082397 | -0.11444 | 0.19684 | -0.30212 | -0.064087 | 0.064087 | -0.068665 | 0.032043 | -0.036621 | -122.6898 | -122.9004 | 0.18768 | 0.18768 | 0.10986 | 0.2243 | 0.14648 | -0.032043 | -122.5296 | -122.7905 | 0.33417 | 0.30212 | 0.20142 | 0.33417 | 0.23346 | 0.2243 | 0.13275 | 0.36621 | 0.23804 | 0.34332 | 0.49896 | 0.3067 | 0.46692 | -123.0331 | -123.0286 | 0.096131 | 0.20599 | 0.10071 | 0.15564
4921.0469 | 123.0103 | -0.2655 | 122.731 | -0.098725 | -0.00044654 | 0.014174 | 0.0079489 | -0.0015488 | -0.00058531 | -0.0016278 | 0.053589 | 0.0015295 | 0.017944 | 0.003905 | 0.018361 | -0.0079297 | -0.00018806 | -0.17853 | 0.018311 | -0.30212 | -0.1831 | -0.07782 | -0.18768 | -0.10529 | -0.11902 | 0.16479 | -0.29297 | -0.073242 | 0.022888 | -0.11444 | 0.013733 | -0.036621 | -122.7127 | -122.9141 | 0.18768 | 0.16022 | 0.07782 | 0.19684 | 0.11444 | -0.027466 | -122.5662 | -122.8043 | 0.28839 | 0.27924 | 0.15106 | 0.3067 | 0.17853 | 0.2243 | 0.11902 | 0.31586 | 0.21973 | 0.32044 | 0.45776 | 0.28381 | 0.4303 | -123.0331 | -123.024 | 0.082398 | 0.19226 | 0.086975 | 0.14648
4924.6875 | 123.0515 | -0.22888 | 122.731 | -0.075836 | -0.00044654 | 0.013533 | 0.0088033 | 0.0010148 | -0.0010125 | -0.003764 | 0.032227 | 3.4148e-05 | 0.017731 | 0.00070062 | 0.016865 | -0.0081433 | 0.00066654 | -0.13275 | 0.027466 | -0.27924 | -0.15106 | -0.050354 | -0.12817 | -0.064087 | -0.036621 | 0.16937 | -0.29297 | -0.059509 | 0.073242 | -0.027466 | 0.041199 | -0.050354 | -122.7036 | -122.8821 | 0.17853 | 0.16479 | 0.10071 | 0.21515 | 0.15106 | -0.064087 | -122.5616 | -122.7905 | 0.30212 | 0.27008 | 0.20142 | 0.33417 | 0.2655 | 0.22888 | 0.12817 | 0.36621 | 0.23346 | 0.3067 | 0.46234 | 0.25635 | 0.39826 | -123.0103 | -123.024 | 0.07782 | 0.16937 | 0.096131 | 0.19226
4925.2812 | 123.0377 | -0.25635 | 122.7448 | -0.11398 | -0.0015145 | 0.013106 | 0.0079489 | 0.0016556 | 0.0013373 | 0.00029479 | 0.023071 | 0.0011023 | 0.014526 | 0.00091422 | 0.017934 | -0.0077161 | -0.00061526 | -0.16479 | 0.032043 | -0.28381 | -0.17395 | -0.082397 | -0.17395 | -0.091553 | -0.11902 | 0.20142 | -0.31128 | -0.064087 | 0.041199 | -0.082397 | 0.013733 | -0.027465 | -122.7127 | -122.9187 | 0.17395 | 0.1648 | 0.082398 | 0.19226 | 0.10986 | -0.054931 | -122.5433 | -122.8088 | 0.29755 | 0.27008 | 0.17395 | 0.32501 | 0.22888 | 0.20142 | 0.10986 | 0.35248 | 0.24719 | 0.31586 | 0.5127 | 0.28839 | 0.45776 | -123.0286 | -123.056 | 0.082398 | 0.19226 | 0.091553 | 0.13733
4926.1719 | 122.9324 | -0.28839 | 122.7493 | -0.10635 | -0.00087374 | 0.014174 | 0.0083761 | -0.00048063 | -0.0022943 | -0.0031232 | -0.12036 | 0.0011023 | 0.014954 | 0.011595 | 0.018361 | -0.0077161 | -0.00040166 | -0.17395 | 0.059509 | -0.32959 | -0.25635 | -0.20142 | -0.28381 | -0.20142 | -0.2243 | 0.2243 | -0.32501 | -0.13275 | -0.07782 | -0.21973 | -0.041199 | -0.041199 | -122.6898 | -123.0057 | 0.086975 | 0.086975 | 0.004578 | 0.12817 | 0.045777 | -0.036621 | -122.525 | -122.8821 | 0.21057 | 0.24719 | 0.068664 | 0.28381 | 0.10529 | 0.12817 | 0.073242 | 0.24719 | 0.19226 | 0.3891 | 0.54932 | 0.3479 | 0.5127 | -123.0789 | -123.0743 | 0.032043 | 0.15564 | 0.11444 | 0.064087
4927.1719 | 122.9462 | -0.28381 | 122.7585 | -0.091095 | 0.0016899 | 0.014815 | 0.0083761 | -0.0034714 | -0.0027215 | -0.00034601 | 0.02002 | 0.0013159 | 0.016235 | 0.0096728 | 0.018574 | -0.0092115 | -0.0018971 | -0.11902 | 0.050354 | -0.29755 | -0.16937 | -0.068665 | -0.16022 | -0.082397 | -0.10986 | 0.20142 | -0.32044 | -0.11902 | -0.009155 | -0.13733 | -0.041199 | -0.013733 | -122.7081 | -122.9279 | 0.21515 | 0.20142 | 0.1236 | 0.21515 | 0.13733 | -0.036622 | -122.5571 | -122.8775 | 0.27466 | 0.24261 | 0.14648 | 0.27924 | 0.18311 | 0.22888 | 0.12817 | 0.31128 | 0.20142 | 0.3479 | 0.52185 | 0.33417 | 0.48523 | -123.056 | -123.0789 | 0.11444 | 0.16479 | 0.16479 | 0.17395
4928.1719 | 123.0423 | -0.24261 | 122.7173 | -0.075836 | 0.00040806 | 0.014815 | 0.0060263 | -0.003685 | 0.0015509 | -0.0041912 | 0.035278 | 0.00067495 | 0.015381 | 0.001128 | 0.019215 | -0.0066479 | 0.00045294 | -0.11902 | 0.027466 | -0.28839 | -0.10986 | 0.004578 | -0.10071 | -0.036621 | -0.013733 | 0.1831 | -0.28839 | -0.059509 | 0.086975 | -0.022888 | 0.041199 | -0.045776 | -122.6898 | -122.8271 | 0.24719 | 0.20599 | 0.14191 | 0.25177 | 0.18768 | -0.045776 | -122.5342 | -122.7768 | 0.32959 | 0.28381 | 0.21973 | 0.32959 | 0.2655 | 0.29297 | 0.17853 | 0.37537 | 0.22888 | 0.31586 | 0.4715 | 0.27008 | 0.42572 | -123.0057 | -123.0057 | 0.13275 | 0.18311 | 0.1236 | 0.22888
4929.1719 | 123.0469 | -0.23346 | 122.731 | -0.075836 | 0.00019446 | 0.013533 | 0.0077353 | 0.0010148 | -0.00058531 | -0.00098701 | 0.023071 | 3.4148e-05 | 0.016022 | 0.0071094 | 0.018788 | -0.0062207 | -0.0044605 | -0.11902 | 0.032043 | -0.28381 | -0.09613 | 0.018311 | -0.086975 | -0.013733 | -0.009155 | 0.17853 | -0.28839 | -0.032043 | 0.091553 | -0.036621 | 0.041199 | -0.050354 | -122.699 | -122.8271 | 0.25177 | 0.21973 | 0.14648 | 0.27008 | 0.19684 | -0.054932 | -122.5525 | -122.7631 | 0.32501 | 0.27466 | 0.19684 | 0.32959 | 0.25177 | 0.30212 | 0.18768 | 0.37994 | 0.25635 | 0.31586 | 0.46692 | 0.2655 | 0.41199 | -123.0148 | -123.0194 | 0.13733 | 0.20142 | 0.11444 | 0.2243
4930.1719 | 123.0698 | -0.21973 | 122.7539 | -0.083466 | -0.0027963 | 0.014174 | 0.0064535 | -0.0011214 | 0.00091009 | -0.002055 | 0.044434 | 0.0028113 | 0.016022 | 0.0026232 | 0.018147 | -0.0096387 | -0.0018971 | -0.1236 | 0.013733 | -0.28839 | -0.11902 | -0.004578 | -0.10529 | -0.045776 | -0.004578 | 0.17395 | -0.27008 | -0.027466 | 0.10986 | -0.027466 | 0.059509 | -0.068664 | -122.7402 | -122.8729 | 0.21515 | 0.17395 | 0.11444 | 0.24262 | 0.18311 | -0.050354 | -122.58 | -122.7814 | 0.32959 | 0.27924 | 0.19226 | 0.32959 | 0.24262 | 0.28381 | 0.16937 | 0.37994 | 0.24262 | 0.30212 | 0.44403 | 0.23346 | 0.39368 | -123.0423 | -123.024 | 0.10071 | 0.19226 | 0.096131 | 0.21515
4931.1719 | 122.9645 | -0.2655 | 122.7585 | -0.045319 | 0.0012625 | 0.013319 | 0.0096579 | 0.0033646 | 5.5488e-05 | 0.0028582 | -0.092895 | 0.0038793 | 0.015594 | 0.009032 | 0.01772 | -0.0066479 | -0.00040166 | -0.12817 | 0.07782 | -0.31586 | -0.17853 | -0.09613 | -0.19226 | -0.13733 | -0.10986 | 0.21057 | -0.30212 | -0.091553 | -0.009155 | -0.13733 | -0.027466 | -0.050354 | -122.6807 | -122.937 | 0.16937 | 0.12817 | 0.073242 | 0.17853 | 0.1236 | -0.036621 | -122.5479 | -122.85 | 0.25635 | 0.23804 | 0.12817 | 0.27466 | 0.16479 | 0.21973 | 0.13733 | 0.29297 | 0.21057 | 0.39368 | 0.5127 | 0.34332 | 0.47607 | -123.0743 | -123.0606 | 0.086975 | 0.17395 | 0.13733 | 0.15564
4932.1719 | 123.056 | -0.25635 | 122.7173 | -0.10635 | -0.0015145 | 0.012251 | 0.0083761 | -0.0017624 | -0.0010125 | 0.001363 | 0.03833 | 0.0028113 | 0.015167 | -0.00036738 | 0.018574 | -0.0089979 | -0.0012561 | -0.1236 | 0.036621 | -0.28381 | -0.11902 | 0.009155 | -0.09613 | -0.032043 | 0.013733 | 0.1831 | -0.27466 | -0.032043 | 0.09613 | -0.032043 | 0.045776 | -0.027465 | -122.6807 | -122.8363 | 0.2655 | 0.22431 | 0.16022 | 0.25177 | 0.18768 | -0.01831 | -122.5342 | -122.7493 | 0.35248 | 0.30212 | 0.22431 | 0.32043 | 0.24262 | 0.29297 | 0.16479 | 0.37079 | 0.24262 | 0.32043 | 0.45776 | 0.29297 | 0.43945 | -123.0011 | -122.9919 | 0.13733 | 0.22431 | 0.13275 | 0.27008
4933.1719 | 123.0698 | -0.24719 | 122.7173 | -0.091095 | 0.0016899 | 0.015456 | 0.012008 | -0.00026703 | -0.0010125 | -0.00034601 | 0.0078126 | 0.0028113 | 0.015594 | -0.0033582 | 0.018574 | -0.0092115 | -0.00082886 | -0.13733 | 0.027466 | -0.28381 | -0.13275 | -0.004578 | -0.10529 | -0.032043 | 0.013733 | 0.15564 | -0.30212 | 0 | 0.09613 | -0.022888 | 0.054932 | -0.036621 | -122.6898 | -122.85 | 0.24261 | 0.21515 | 0.14191 | 0.25177 | 0.17853 | -0.054932 | -122.5616 | -122.7173 | 0.34332 | 0.30212 | 0.2243 | 0.35706 | 0.27924 | 0.27923 | 0.15106 | 0.39825 | 0.30212 | 0.31128 | 0.45776 | 0.27466 | 0.40283 | -123.0011 | -123.0194 | 0.11444 | 0.24719 | 0.10986 | 0.26093
4934.1719 | 123.0469 | -0.23804 | 122.7402 | -0.083466 | -0.0027963 | 0.013319 | 0.0079489 | 0.0012284 | 0.00091009 | 0.0022174 | 0.026123 | 0.0021703 | 0.015381 | 0.0043322 | 0.017293 | -0.0079297 | -0.0016833 | -0.13275 | 0.050354 | -0.27008 | -0.13733 | -0.032043 | -0.12817 | -0.059509 | -0.050354 | 0.16022 | -0.27466 | -0.032043 | 0.091553 | -0.027466 | 0.032043 | -0.032044 | -122.6898 | -122.8775 | 0.20599 | 0.17853 | 0.10986 | 0.21057 | 0.14191 | -0.036621 | -122.58 | -122.7722 | 0.32959 | 0.27008 | 0.21057 | 0.3067 | 0.24719 | 0.23804 | 0.13275 | 0.36621 | 0.24262 | 0.32044 | 0.43488 | 0.28839 | 0.39825 | -123.0103 | -123.0148 | 0.10071 | 0.20599 | 0.10529 | 0.18768
4935.1719 | 123.056 | -0.25177 | 122.7402 | -0.068207 | -0.00023294 | 0.015242 | 0.0045309 | -0.00026703 | -0.00079891 | 0.0011494 | 0.013916 | 0.0015295 | 0.017517 | 0.005614 | 0.017293 | -0.0083569 | 0.00066654 | -0.1236 | 0.013733 | -0.28839 | -0.10986 | 0.013733 | -0.09613 | -0.041199 | 0 | 0.16479 | -0.28839 | -0.036621 | 0.10071 | -0.045776 | 0.032043 | -0.036621 | -122.7264 | -122.85 | 0.2655 | 0.21057 | 0.15564 | 0.24719 | 0.19226 | -0.036621 | -122.5754 | -122.7768 | 0.35248 | 0.28381 | 0.20599 | 0.32043 | 0.24262 | 0.30212 | 0.17853 | 0.3891 | 0.25177 | 0.30212 | 0.45319 | 0.2655 | 0.41656 | -123.0286 | -123.0286 | 0.14191 | 0.21515 | 0.12817 | 0.25177
4936.1719 | 123.0057 | -0.2655 | 122.7676 | -0.10635 | 0.00019446 | 0.013533 | 0.010512 | -5.343e-05 | -0.0018671 | 0.00093559 | -0.077637 | 0.0011023 | 0.016663 | 0.0066822 | 0.018361 | -0.0081433 | -0.00061526 | -0.17853 | 0.059509 | -0.29755 | -0.20142 | -0.14648 | -0.18768 | -0.13733 | -0.13733 | 0.20142 | -0.3067 | -0.11444 | -0.009155 | -0.14648 | -0.022888 | -0.032043 | -122.7081 | -122.9691 | 0.11902 | 0.12817 | 0.07782 | 0.16022 | 0.10986 | -0.041199 | -122.5662 | -122.8821 | 0.25635 | 0.24261 | 0.11902 | 0.28381 | 0.16022 | 0.15106 | 0.09613 | 0.29755 | 0.19226 | 0.35705 | 0.50812 | 0.32501 | 0.46692 | -123.0652 | -123.0743 | 0.064087 | 0.15106 | 0.086975 | 0.12817
4937.1719 | 123.056 | -0.25177 | 122.7173 | -0.083466 | 0.00019446 | 0.015669 | 0.0092307 | -0.0021896 | 0.00026909 | -0.00077341 | 0.02002 | 0.0011023 | 0.01709 | 0.0032642 | 0.017079 | -0.0068615 | -0.00061526 | -0.12817 | 0.041199 | -0.28381 | -0.1236 | -0.009155 | -0.11444 | -0.045776 | -0.018311 | 0.15564 | -0.29297 | -0.018311 | 0.086975 | -0.022888 | 0.036621 | -0.032043 | -122.6761 | -122.8409 | 0.24261 | 0.20599 | 0.13733 | 0.23804 | 0.16937 | -0.041199 | -122.5616 | -122.7356 | 0.33874 | 0.28839 | 0.22888 | 0.32959 | 0.27008 | 0.27466 | 0.16022 | 0.37994 | 0.27466 | 0.32501 | 0.44861 | 0.29297 | 0.40741 | -123.0011 | -123.0103 | 0.12817 | 0.23346 | 0.1236 | 0.23346
4938.1719 | 123.0103 | -0.27008 | 122.7402 | -0.12161 | -0.00066014 | 0.01396 | 0.0066671 | -0.00069423 | -0.0012261 | 0.0026446 | 0.02002 | 0.0021703 | 0.016663 | 0.0064684 | 0.019002 | -0.0068615 | -0.0014697 | -0.10986 | 0.027466 | -0.28381 | -0.13275 | -0.032043 | -0.12817 | -0.059509 | -0.059509 | 0.1831 | -0.29297 | -0.07782 | 0.054932 | -0.082397 | 0.004578 | -0.013732 | -122.7127 | -122.8729 | 0.23804 | 0.21057 | 0.14191 | 0.2243 | 0.15564 | -0.022888 | -122.5571 | -122.818 | 0.32501 | 0.27466 | 0.18768 | 0.29755 | 0.21057 | 0.25177 | 0.15106 | 0.3479 | 0.21515 | 0.31128 | 0.47607 | 0.29755 | 0.45319 | -123.024 | -123.0331 | 0.13733 | 0.19226 | 0.16022 | 0.21057
4939.1719 | 123.056 | -0.25177 | 122.7173 | -0.075836 | -0.0013009 | 0.013106 | 0.0066671 | -0.0011214 | -0.00079891 | -0.00077341 | 0.010864 | 0.0025975 | 0.01709 | 0.0068958 | 0.017506 | -0.0072889 | -0.0016833 | -0.13733 | 0.045776 | -0.29755 | -0.13733 | -0.036621 | -0.14191 | -0.073242 | -0.050354 | 0.16937 | -0.29297 | -0.041199 | 0.068665 | -0.050354 | 0.045776 | -0.045776 | -122.6715 | -122.8546 | 0.21515 | 0.17853 | 0.10986 | 0.2243 | 0.15564 | -0.041199 | -122.5479 | -122.7585 | 0.32044 | 0.29755 | 0.20142 | 0.33874 | 0.24261 | 0.26092 | 0.16022 | 0.36163 | 0.25177 | 0.34332 | 0.46234 | 0.29755 | 0.42114 | -123.0148 | -123.0103 | 0.11444 | 0.21057 | 0.11444 | 0.20142
4940.1719 | 123.0057 | -0.27008 | 122.7356 | -0.091095 | -0.00087374 | 0.017378 | 0.0066671 | -0.0017624 | 0.00091009 | -0.0031232 | 0.010864 | 0.0034521 | 0.01474 | 0.0045458 | 0.01772 | -0.0083569 | 0.00088014 | -0.17395 | 0.027466 | -0.3067 | -0.16937 | -0.073242 | -0.15106 | -0.082397 | -0.09613 | 0.1236 | -0.31586 | -0.068665 | 0.041199 | -0.086975 | 0.013733 | -0.036621 | -122.7081 | -122.905 | 0.19684 | 0.18768 | 0.11902 | 0.2243 | 0.15564 | -0.045776 | -122.612 | -122.8043 | 0.31128 | 0.28381 | 0.18311 | 0.32959 | 0.22888 | 0.23346 | 0.13733 | 0.35706 | 0.24719 | 0.33417 | 0.43945 | 0.29755 | 0.39368 | -123.0423 | -123.0515 | 0.10071 | 0.20142 | 0.096131 | 0.17395
4941.1719 | 123.0331 | -0.25635 | 122.7402 | -0.052948 | -0.00023294 | 0.015883 | 0.0094443 | -5.343e-05 | -0.0012261 | 0.0011494 | -0.0043946 | 0.00067495 | 0.01709 | 0.0086048 | 0.017079 | -0.0064343 | -0.0046741 | -0.14648 | 0.041199 | -0.28381 | -0.15106 | -0.059509 | -0.15106 | -0.082397 | -0.07782 | 0.16479 | -0.28381 | -0.059509 | 0.059509 | -0.068665 | 0.022888 | -0.027465 | -122.699 | -122.8912 | 0.19684 | 0.17395 | 0.10529 | 0.20142 | 0.13275 | -0.027465 | -122.5754 | -122.7997 | 0.31586 | 0.27924 | 0.18768 | 0.3067 | 0.21515 | 0.2243 | 0.13275 | 0.34332 | 0.2243 | 0.32501 | 0.44861 | 0.29755 | 0.42114 | -123.024 | -123.024 | 0.10529 | 0.19684 | 0.10986 | 0.17853
4942.1719 | 123.0469 | -0.24719 | 122.731 | -0.091095 | -0.00087374 | 0.015242 | 0.0064535 | 0.00058737 | -0.0010125 | 8.1188e-05 | -0.019653 | 0.0019567 | 0.018372 | 0.0017688 | 0.018788 | -0.0085705 | 0.0010937 | -0.13275 | 0.022888 | -0.30212 | -0.13275 | -0.022888 | -0.1236 | -0.045776 | -0.032043 | 0.15564 | -0.27924 | -0.032043 | 0.09613 | -0.027466 | 0.050354 | -0.054932 | -122.7081 | -122.8638 | 0.2243 | 0.20142 | 0.1236 | 0.25635 | 0.17853 | -0.032044 | -122.5754 | -122.7631 | 0.34332 | 0.29755 | 0.21973 | 0.32959 | 0.25177 | 0.27924 | 0.16937 | 0.37537 | 0.24719 | 0.32501 | 0.43488 | 0.27008 | 0.40283 | -123.0331 | -123.0103 | 0.11444 | 0.21515 | 0.11444 | 0.21515
4943.1719 | 123.0606 | -0.24719 | 122.7219 | -0.075836 | -0.0017281 | 0.015669 | 0.011153 | 0.003151 | -0.0012261 | 0.00050839 | 0.010864 | 0.00046135 | 0.017303 | 0.001128 | 0.016438 | -0.0075025 | -0.0036059 | -0.13733 | 0.027466 | -0.29297 | -0.11902 | -0.018311 | -0.14191 | -0.050354 | -0.032043 | 0.17395 | -0.29755 | -0.032043 | 0.082397 | -0.045776 | 0.054932 | -0.045777 | -122.6944 | -122.8409 | 0.22888 | 0.19684 | 0.10528 | 0.24261 | 0.15106 | -0.050354 | -122.5479 | -122.7539 | 0.32959 | 0.30212 | 0.20142 | 0.35248 | 0.25177 | 0.27466 | 0.17395 | 0.37994 | 0.2655 | 0.32043 | 0.4715 | 0.27466 | 0.42114 | -123.0148 | -123.0194 | 0.12817 | 0.21515 | 0.10986 | 0.21515
4944.1719 | 123.0103 | -0.24719 | 122.7539 | -0.10635 | 0.0010489 | 0.014601 | 0.0096579 | -0.0015488 | 0.0013373 | -0.002696 | -0.0074462 | 0.0032385 | 0.01709 | 0.0066822 | 0.017506 | -0.0055799 | -0.00061526 | -0.15564 | 0.041199 | -0.28839 | -0.17853 | -0.091553 | -0.1831 | -0.091553 | -0.10529 | 0.17395 | -0.3067 | -0.064087 | 0.050354 | -0.073242 | 0.027466 | -0.041199 | -122.7127 | -122.9324 | 0.15564 | 0.15564 | 0.064087 | 0.19684 | 0.10529 | -0.05951 | -122.58 | -122.818 | 0.29755 | 0.27466 | 0.17395 | 0.33417 | 0.23346 | 0.19684 | 0.10986 | 0.35706 | 0.24261 | 0.32959 | 0.48065 | 0.28839 | 0.42114 | -123.0423 | -123.0606 | 0.068664 | 0.1831 | 0.091552 | 0.14191
4945.1719 | 123.0698 | -0.24719 | 122.7219 | -0.068207 | -1.9142e-05 | 0.013747 | 0.0077353 | -0.0015488 | 5.5488e-05 | 0.00050839 | -0.0013428 | 0.0017431 | 0.017944 | 0.0066822 | 0.017506 | -0.0070753 | -0.0027515 | -0.15106 | 0.041199 | -0.27466 | -0.14191 | -0.050354 | -0.15106 | -0.064087 | -0.073242 | 0.18768 | -0.29297 | -0.059509 | 0.068665 | -0.068665 | 0.032043 | -0.027466 | -122.6807 | -122.8638 | 0.19684 | 0.1831 | 0.09613 | 0.21057 | 0.1236 | -0.045777 | -122.5342 | -122.7814 | 0.31586 | 0.27924 | 0.17853 | 0.32501 | 0.2243 | 0.2243 | 0.13275 | 0.36163 | 0.23346 | 0.31586 | 0.48065 | 0.28839 | 0.43488 | -122.9965 | -123.0148 | 0.10528 | 0.18768 | 0.09613 | 0.17395
4946.1719 | 123.0057 | -0.25177 | 122.7585 | -0.12161 | 0.00083526 | 0.014174 | 0.010512 | -0.0026168 | -0.0035761 | 0.0022174 | -0.016602 | 0.0019567 | 0.015594 | 0.0019824 | 0.018147 | -0.0064343 | -0.0036059 | -0.15564 | 0.045776 | -0.28381 | -0.17853 | -0.091553 | -0.18768 | -0.10529 | -0.10986 | 0.1831 | -0.28381 | -0.07782 | 0.032043 | -0.10986 | 0 | -0.032043 | -122.7127 | -122.937 | 0.16022 | 0.14648 | 0.064087 | 0.17853 | 0.09613 | -0.032043 | -122.5754 | -122.8363 | 0.28381 | 0.25177 | 0.14191 | 0.28381 | 0.17395 | 0.19226 | 0.10528 | 0.31586 | 0.20599 | 0.32959 | 0.46692 | 0.29755 | 0.43488 | -123.0423 | -123.0423 | 0.073242 | 0.17395 | 0.09613 | 0.14191
4947.1719 | 123.0606 | -0.2243 | 122.7173 | -0.10635 | 0.00019446 | 0.013106 | 0.0083761 | 0.00016017 | 5.5488e-05 | 0.00072199 | -0.025757 | 0.0017431 | 0.016449 | 0.010527 | 0.018361 | -0.0075025 | -0.0036059 | -0.13275 | 0.036621 | -0.29297 | -0.11902 | -0.018311 | -0.13275 | -0.036621 | -0.032043 | 0.16022 | -0.28381 | -0.027466 | 0.091553 | -0.041199 | 0.050354 | -0.068665 | -122.6807 | -122.8363 | 0.20599 | 0.18768 | 0.091553 | 0.25635 | 0.16022 | -0.059509 | -122.5571 | -122.7448 | 0.31586 | 0.27466 | 0.18311 | 0.33417 | 0.24261 | 0.27466 | 0.17395 | 0.37537 | 0.25635 | 0.32959 | 0.44403 | 0.26093 | 0.38452 | -123.0103 | -123.0011 | 0.10529 | 0.19684 | 0.091553 | 0.19226
4948.1719 | 123.0103 | -0.23804 | 122.7356 | -0.12161 | -0.0013009 | 0.015669 | 0.011153 | -0.0017624 | 0.00091009 | -0.00055961 | -0.016602 | 0.0013159 | 0.01709 | 0.00027342 | 0.017293 | -0.0049389 | -0.0014697 | -0.16479 | 0.013733 | -0.28839 | -0.16479 | -0.068665 | -0.19226 | -0.11444 | -0.1236 | 0.16937 | -0.3067 | -0.073242 | 0.022888 | -0.10986 | -0.009155 | -0.050354 | -122.7219 | -122.9004 | 0.16937 | 0.1236 | 0.045776 | 0.17395 | 0.09613 | -0.068665 | -122.5662 | -122.8088 | 0.26093 | 0.22888 | 0.12817 | 0.29755 | 0.19684 | 0.21973 | 0.1236 | 0.32959 | 0.23346 | 0.30212 | 0.47607 | 0.25177 | 0.40741 | -123.024 | -123.0423 | 0.073242 | 0.16479 | 0.073242 | 0.11444
4949.1719 | 123.0103 | -0.24719 | 122.7402 | -0.091095 | 0.0012625 | 0.015242 | 0.0068807 | -0.0011214 | -0.00079891 | -0.0018414 | 0.010864 | 0.0015295 | 0.015594 | 0.0028368 | 0.016865 | -0.0079297 | -0.0016833 | -0.15564 | 0.032043 | -0.28381 | -0.17853 | -0.09613 | -0.17395 | -0.086975 | -0.10986 | 0.17395 | -0.3067 | -0.073242 | 0.032043 | -0.10986 | 0 | -0.036621 | -122.7081 | -122.9187 | 0.15106 | 0.16022 | 0.073242 | 0.19684 | 0.10986 | -0.05951 | -122.5662 | -122.8134 | 0.27924 | 0.24719 | 0.13733 | 0.3067 | 0.19684 | 0.18768 | 0.10528 | 0.33874 | 0.23346 | 0.31586 | 0.48065 | 0.27924 | 0.42114 | -123.024 | -123.0469 | 0.068664 | 0.17395 | 0.091552 | 0.13733
4950.1719 | 122.9919 | -0.25177 | 122.7539 | -0.052948 | 0.0012625 | 0.015883 | 0.0088033 | 0.00080117 | -0.0018671 | -0.0029096 | -0.041016 | 0.0015295 | 0.015808 | 0.00091422 | 0.017506 | -0.0085705 | -0.0038197 | -0.15564 | 0.036621 | -0.27924 | -0.16937 | -0.07782 | -0.1831 | -0.11902 | -0.12817 | 0.17853 | -0.29297 | -0.086975 | 0.036621 | -0.10986 | 0.013733 | -0.027466 | -122.7173 | -122.9233 | 0.17395 | 0.13275 | 0.068665 | 0.16022 | 0.096131 | -0.041199 | -122.5754 | -122.8409 | 0.28839 | 0.2655 | 0.14191 | 0.3067 | 0.18311 | 0.20142 | 0.10986 | 0.32959 | 0.20599 | 0.31586 | 0.4715 | 0.28839 | 0.4303 | -123.0331 | -123.0469 | 0.082397 | 0.16479 | 0.09613 | 0.1236
4951.1719 | 123.0194 | -0.25177 | 122.7493 | -0.075836 | -0.00087374 | 0.015242 | 0.0066671 | -0.00048063 | -0.0014399 | 0.00072199 | -0.016602 | 0.0017431 | 0.016449 | 0.0077502 | 0.019643 | -0.0066479 | -0.00061526 | -0.16479 | 0.013733 | -0.29297 | -0.17853 | -0.082397 | -0.18768 | -0.09613 | -0.12817 | 0.17853 | -0.29297 | -0.068665 | 0.013733 | -0.12817 | -0.018311 | -0.041199 | -122.7356 | -122.9279 | 0.16937 | 0.15564 | 0.064087 | 0.19684 | 0.10529 | -0.041199 | -122.5708 | -122.818 | 0.2655 | 0.23346 | 0.1236 | 0.27466 | 0.16479 | 0.21057 | 0.11444 | 0.3067 | 0.2243 | 0.3067 | 0.4715 | 0.2655 | 0.4303 | -123.0423 | -123.0423 | 0.073242 | 0.1831 | 0.086975 | 0.1236
4952.1719 | 123.0515 | -0.23804 | 122.731 | -0.098725 | -0.00066014 | 0.012892 | 0.0066671 | 0.00251 | 0.00091009 | -0.0033368 | -0.03186 | 0.0017431 | 0.018372 | 0.0043322 | 0.016225 | -0.0047253 | -0.0025379 | -0.13275 | 0.004578 | -0.28381 | -0.11902 | -0.018311 | -0.16022 | -0.086975 | -0.041199 | 0.16479 | -0.28381 | -0.045776 | 0.036621 | -0.09613 | 0.013733 | -0.045776 | -122.7264 | -122.85 | 0.21973 | 0.15106 | 0.07782 | 0.19684 | 0.1236 | -0.045776 | -122.5662 | -122.7768 | 0.27466 | 0.25177 | 0.14191 | 0.29755 | 0.18768 | 0.2655 | 0.16479 | 0.32043 | 0.23804 | 0.28839 | 0.44861 | 0.24261 | 0.40283 | -123.0148 | -123.0148 | 0.11902 | 0.19226 | 0.10529 | 0.19684
4953.1719 | 123.0286 | -0.25635 | 122.7539 | -0.083466 | 0.00019446 | 0.013319 | 0.0083761 | 0.0027238 | -0.0014399 | 8.1188e-05 | -0.010498 | 0.00046135 | 0.016022 | 0.0066822 | 0.019002 | -0.0051527 | -0.0014697 | -0.15564 | 0.041199 | -0.28839 | -0.16479 | -0.064087 | -0.16022 | -0.082397 | -0.091553 | 0.16937 | -0.30212 | -0.050354 | 0.073242 | -0.068665 | 0.022888 | -0.032043 | -122.7127 | -122.9187 | 0.19226 | 0.17395 | 0.096131 | 0.20599 | 0.12817 | -0.045776 | -122.5845 | -122.8043 | 0.32959 | 0.27924 | 0.18768 | 0.32501 | 0.23346 | 0.2243 | 0.1236 | 0.37537 | 0.25177 | 0.32959 | 0.4715 | 0.29755 | 0.42572 | -123.0423 | -123.056 | 0.091553 | 0.20599 | 0.10071 | 0.1648
4954.2344 | 123.0698 | -0.25635 | 122.731 | -0.091095 | 0.0019035 | 0.016096 | 0.0075217 | -0.0030442 | -0.0018671 | 0.00093559 | -0.0013428 | 0.0019567 | 0.015167 | 0.0049732 | 0.017079 | -0.0081433 | -0.0023243 | -0.13733 | 0.036621 | -0.29297 | -0.1236 | -0.004578 | -0.11902 | -0.045776 | -0.013733 | 0.15564 | -0.28381 | -0.041199 | 0.10529 | -0.018311 | 0.050354 | -0.036621 | -122.6944 | -122.8546 | 0.25177 | 0.21057 | 0.13733 | 0.24719 | 0.17395 | -0.027465 | -122.5754 | -122.7722 | 0.36163 | 0.3067 | 0.23804 | 0.33417 | 0.2655 | 0.28839 | 0.16937 | 0.3891 | 0.24261 | 0.32959 | 0.43945 | 0.29297 | 0.41199 | -123.024 | -123.0148 | 0.13275 | 0.21515 | 0.11902 | 0.24262
4955.1719 | 123.0377 | -0.25177 | 122.7219 | -0.15213 | -0.00044654 | 0.013106 | 0.0088033 | -0.0021896 | -0.0010125 | -0.0024822 | -0.025757 | 0.0021703 | 0.018799 | 0.0066822 | 0.019429 | -0.0085705 | 0.00023934 | -0.16479 | 0.004578 | -0.28839 | -0.16479 | -0.091553 | -0.1831 | -0.10071 | -0.13275 | 0.16022 | -0.30212 | -0.086975 | 0.027466 | -0.10529 | 0 | -0.036621 | -122.7173 | -122.8867 | 0.16022 | 0.15106 | 0.068665 | 0.18768 | 0.10529 | -0.050354 | -122.5616 | -122.8088 | 0.27924 | 0.25177 | 0.14648 | 0.30212 | 0.19684 | 0.19684 | 0.1236 | 0.32959 | 0.21515 | 0.29297 | 0.46234 | 0.25635 | 0.41199 | -123.0103 | -123.024 | 0.086975 | 0.16479 | 0.086975 | 0.11902
4956.1719 | 123.0515 | -0.26093 | 122.7264 | -0.075836 | -0.0013009 | 0.014815 | 0.0085897 | -0.0011214 | 0.0021917 | 0.0034992 | -0.010498 | 0.0038793 | 0.01709 | 0.0051868 | 0.017934 | -0.0070753 | 0.00045294 | -0.16022 | 0.027466 | -0.28381 | -0.16937 | -0.073242 | -0.19684 | -0.09613 | -0.11902 | 0.17395 | -0.29755 | -0.07782 | 0.009155 | -0.1236 | 0 | -0.022888 | -122.699 | -122.8958 | 0.18768 | 0.1648 | 0.064087 | 0.18768 | 0.086975 | -0.036621 | -122.5525 | -122.8043 | 0.27008 | 0.26093 | 0.13733 | 0.29755 | 0.17395 | 0.21057 | 0.11444 | 0.3067 | 0.21973 | 0.31128 | 0.4715 | 0.28839 | 0.43488 | -123.0103 | -123.024 | 0.091552 | 0.18311 | 0.10071 | 0.14191
4957.1719 | 123.0606 | -0.24719 | 122.6852 | -0.083466 | 0.00019446 | 0.01396 | 0.0083761 | -0.0041122 | 0.00048269 | 8.1188e-05 | -0.0013428 | 0.0011023 | 0.015808 | 0.0028368 | 0.016225 | -0.0068615 | -0.00061526 | -0.14191 | 0.013733 | -0.28381 | -0.13275 | -0.027466 | -0.11902 | -0.054932 | -0.045776 | 0.15106 | -0.27924 | -0.027466 | 0.091553 | -0.032043 | 0.022888 | -0.036621 | -122.6715 | -122.818 | 0.21973 | 0.19226 | 0.12817 | 0.22888 | 0.16479 | -0.032044 | -122.5342 | -122.7127 | 0.33874 | 0.27008 | 0.21515 | 0.30212 | 0.24719 | 0.25635 | 0.15106 | 0.37079 | 0.25177 | 0.29755 | 0.4303 | 0.26093 | 0.39825 | -122.9691 | -122.9645 | 0.11444 | 0.21973 | 0.10528 | 0.20142
4958.1719 | 123.0698 | -0.26093 | 122.7264 | -0.1445 | 0.0010489 | 0.014174 | 0.0085897 | 0.00037377 | -0.0016535 | -0.00055961 | -0.053223 | 0.0034521 | 0.018158 | 0.0049732 | 0.016652 | -0.0053663 | -0.0029651 | -0.16937 | 0.032043 | -0.29297 | -0.16479 | -0.07782 | -0.1831 | -0.09613 | -0.13733 | 0.16022 | -0.30212 | -0.086975 | 0.013733 | -0.10986 | 0 | -0.032044 | -122.6944 | -122.8912 | 0.18311 | 0.1648 | 0.07782 | 0.19684 | 0.10986 | -0.041199 | -122.5662 | -122.8134 | 0.27466 | 0.26093 | 0.15106 | 0.30212 | 0.19226 | 0.21515 | 0.12817 | 0.31586 | 0.21515 | 0.32501 | 0.46234 | 0.29297 | 0.42114 | -123.0194 | -123.0286 | 0.09613 | 0.17395 | 0.091552 | 0.1236
4959.1719 | 123.0698 | -0.23804 | 122.7219 | -0.068207 | 0.00040806 | 0.01631 | 0.0090169 | 0.0050736 | -0.0020807 | 0.00093559 | -0.08374 | 0.0032385 | 0.015381 | 0.0030506 | 0.015797 | -0.0049389 | -0.0025379 | -0.10986 | -0.004578 | -0.27924 | -0.11902 | -0.022888 | -0.16022 | -0.086975 | -0.050354 | 0.15564 | -0.27924 | -0.013733 | 0.050354 | -0.07782 | 0.041199 | -0.041199 | -122.7264 | -122.8409 | 0.21515 | 0.15106 | 0.07782 | 0.19226 | 0.11902 | -0.041199 | -122.5662 | -122.7356 | 0.28839 | 0.27924 | 0.16022 | 0.32043 | 0.20142 | 0.25635 | 0.16022 | 0.32959 | 0.2655 | 0.27466 | 0.43488 | 0.23346 | 0.39368 | -123.0011 | -123.0011 | 0.11902 | 0.2243 | 0.12817 | 0.18768
4960.1719 | 123.0652 | -0.2243 | 122.7081 | -0.12161 | -0.0010873 | 0.015028 | 0.0092307 | -0.0013352 | -0.00015811 | -0.0012006 | -0.053223 | 0.0023839 | 0.017731 | 0.011595 | 0.02007 | -0.0047253 | 0.0013073 | -0.1236 | 0.022888 | -0.26093 | -0.14191 | -0.027466 | -0.14648 | -0.091553 | -0.050354 | 0.15106 | -0.27466 | -0.027466 | 0.041199 | -0.073242 | 0.036621 | -0.036621 | -122.6852 | -122.85 | 0.19684 | 0.13275 | 0.07782 | 0.16937 | 0.11444 | -0.050354 | -122.5571 | -122.7356 | 0.2655 | 0.26093 | 0.15106 | 0.31128 | 0.20142 | 0.23346 | 0.11902 | 0.31586 | 0.24719 | 0.28381 | 0.42572 | 0.24719 | 0.37537 | -122.9691 | -122.9828 | 0.082397 | 0.19684 | 0.10071 | 0.17395
4961.1719 | 123.0377 | -0.26093 | 122.7173 | -0.098725 | -0.0036507 | 0.015456 | 0.0096579 | 0.0016556 | -0.0014399 | 0.0017902 | -0.016602 | 0.0015295 | 0.016235 | 0.0019824 | 0.01772 | -0.0083569 | 0.0032299 | -0.17395 | 0.027466 | -0.27008 | -0.17395 | -0.07782 | -0.19226 | -0.10986 | -0.12817 | 0.17853 | -0.3067 | -0.086975 | 0.022888 | -0.10529 | -0.009155 | -0.009156 | -122.6898 | -122.8912 | 0.18311 | 0.15106 | 0.068664 | 0.16022 | 0.07782 | -0.045777 | -122.5388 | -122.8043 | 0.28381 | 0.25177 | 0.15564 | 0.29755 | 0.20142 | 0.19226 | 0.096131 | 0.32959 | 0.21973 | 0.29755 | 0.48523 | 0.28839 | 0.43945 | -122.9874 | -123.024 | 0.086975 | 0.17395 | 0.086975 | 0.13275
4962.1719 | 123.0194 | -0.24719 | 122.7036 | -0.10635 | 0.00019446 | 0.014601 | 0.0077353 | 0.00080117 | 0.00069649 | -0.0012006 | -0.047119 | 0.0021703 | 0.016022 | 0.003905 | 0.017506 | -0.0072889 | -0.0012561 | -0.13275 | 0.018311 | -0.25635 | -0.12817 | -0.027466 | -0.16479 | -0.091553 | -0.045776 | 0.15106 | -0.27924 | -0.041199 | 0.059509 | -0.07782 | 0.009155 | -0.009156 | -122.6852 | -122.8317 | 0.21973 | 0.15564 | 0.082397 | 0.1648 | 0.091553 | -0.032044 | -122.5525 | -122.7448 | 0.3067 | 0.25635 | 0.16937 | 0.28839 | 0.20142 | 0.22888 | 0.12817 | 0.33874 | 0.23804 | 0.27466 | 0.4303 | 0.2655 | 0.39825 | -122.9599 | -122.9828 | 0.11902 | 0.20599 | 0.11444 | 0.20142
4963.2344 | 123.0286 | -0.25177 | 122.7127 | -0.091095 | -0.0023691 | 0.013533 | 0.0051717 | -0.0028304 | -0.0016535 | 0.0015766 | -0.0013428 | 0.0047339 | 0.01709 | 0.00070062 | 0.019429 | -0.0068615 | -0.00082886 | -0.16937 | 0.032043 | -0.28381 | -0.17395 | -0.09613 | -0.17853 | -0.086975 | -0.1236 | 0.16022 | -0.30212 | -0.086975 | 0.027466 | -0.09613 | -0.004578 | -0.032043 | -122.6807 | -122.8867 | 0.15564 | 0.16479 | 0.073242 | 0.19684 | 0.10528 | -0.050354 | -122.5525 | -122.7997 | 0.27924 | 0.24719 | 0.15564 | 0.29755 | 0.20599 | 0.18768 | 0.10986 | 0.32959 | 0.21515 | 0.31586 | 0.46234 | 0.28381 | 0.41199 | -122.9965 | -123.0148 | 0.07782 | 0.16479 | 0.082397 | 0.12817
4964.1719 | 123.0423 | -0.24261 | 122.7402 | -0.15213 | 0.0014761 | 0.015883 | 0.0090169 | 0.0057144 | -0.0022943 | -0.00055961 | -0.022705 | 0.0032385 | 0.016663 | 0.0060412 | 0.020924 | -0.0064343 | 0.0034435 | -0.14191 | 0.009155 | -0.29755 | -0.14648 | -0.041199 | -0.16479 | -0.07782 | -0.050354 | 0.16937 | -0.26093 | -0.054932 | 0.036621 | -0.091553 | 0.004578 | -0.054931 | -122.731 | -122.8867 | 0.20142 | 0.16479 | 0.07782 | 0.21973 | 0.13275 | -0.01831 | -122.5708 | -122.7951 | 0.27924 | 0.24719 | 0.15106 | 0.2655 | 0.16937 | 0.25635 | 0.15106 | 0.29755 | 0.20599 | 0.3067 | 0.4303 | 0.25177 | 0.41199 | -123.0377 | -123.0011 | 0.096131 | 0.18768 | 0.10071 | 0.19226
4965.1719 | 123.0789 | -0.23346 | 122.7493 | -0.13687 | -0.00044654 | 0.017805 | 0.0085897 | 0.0033646 | -0.00037171 | 0.001363 | -0.056274 | 0.0015295 | 0.015381 | 0.0094592 | 0.017079 | -0.0055799 | -0.00082886 | -0.11902 | 0.013733 | -0.27008 | -0.14191 | -0.041199 | -0.14191 | -0.082397 | -0.054932 | 0.14191 | -0.29755 | -0.018311 | 0.064087 | -0.086975 | 0.041199 | -0.036622 | -122.7356 | -122.8912 | 0.19226 | 0.15106 | 0.091552 | 0.18768 | 0.12817 | -0.064087 | -122.6074 | -122.7676 | 0.29755 | 0.27466 | 0.14648 | 0.33874 | 0.21057 | 0.22888 | 0.12817 | 0.36163 | 0.27923 | 0.28381 | 0.43945 | 0.24719 | 0.37537 | -123.0194 | -123.0469 | 0.091552 | 0.21515 | 0.11444 | 0.17853
4966.2344 | 122.937 | -0.2655 | 122.7676 | -0.052948 | 0.0012625 | 0.014815 | 0.010726 | 0.004219 | -0.0014399 | 0.002431 | -0.08374 | 0.0038793 | 0.014099 | 0.008391 | 0.018574 | -0.0064343 | -0.00061526 | -0.17395 | 0.041199 | -0.31128 | -0.24719 | -0.14648 | -0.24719 | -0.17853 | -0.19226 | 0.18768 | -0.29297 | -0.12817 | -0.082397 | -0.20142 | -0.07782 | -0.045776 | -122.7264 | -123.0148 | 0.11902 | 0.086975 | 0.018311 | 0.13275 | 0.064087 | -0.027466 | -122.58 | -122.8958 | 0.18311 | 0.18768 | 0.064087 | 0.21515 | 0.091553 | 0.16479 | 0.064087 | 0.21057 | 0.16479 | 0.35248 | 0.48065 | 0.3067 | 0.45319 | -123.0789 | -123.0606 | 0.018311 | 0.13733 | 0.091553 | 0.073242
4967.1719 | 123.0652 | -0.21515 | 122.7264 | -0.052948 | -0.00066014 | 0.016096 | 0.0088033 | 0.0010148 | -0.0027215 | -0.00055961 | -0.050171 | 0.0034521 | 0.015594 | 0.0019824 | 0.019643 | -0.0081433 | 0.0017345 | -0.16022 | 0.036621 | -0.29755 | -0.16937 | -0.054932 | -0.17395 | -0.09613 | -0.091553 | 0.15106 | -0.27924 | -0.036621 | 0.045776 | -0.082397 | 0.054932 | -0.082397 | -122.6898 | -122.8958 | 0.16022 | 0.11902 | 0.041199 | 0.20142 | 0.1236 | -0.064087 | -122.5754 | -122.7631 | 0.26093 | 0.27008 | 0.13275 | 0.33417 | 0.19684 | 0.24261 | 0.12817 | 0.32501 | 0.24261 | 0.33417 | 0.4303 | 0.25177 | 0.36621 | -123.024 | -123.0057 | 0.045776 | 0.17853 | 0.054932 | 0.1236
4968.1719 | 123.056 | -0.22888 | 122.7539 | -0.12161 | -0.0015145 | 0.016096 | 0.0058127 | 0.00080117 | -0.0029351 | 0.0026446 | -0.056274 | 0.0030249 | 0.015167 | 0.0094592 | 0.019429 | -0.0060071 | -0.00061526 | -0.11902 | 0.027466 | -0.2655 | -0.14191 | -0.032043 | -0.17395 | -0.10071 | -0.054932 | 0.15564 | -0.28839 | -0.022888 | 0.054932 | -0.073242 | 0.045776 | -0.036621 | -122.7264 | -122.8958 | 0.19684 | 0.12817 | 0.054932 | 0.16479 | 0.091553 | -0.059509 | -122.5983 | -122.7768 | 0.28381 | 0.27466 | 0.15564 | 0.33417 | 0.21515 | 0.23346 | 0.1236 | 0.34332 | 0.2655 | 0.29297 | 0.44403 | 0.25635 | 0.38452 | -123.0194 | -123.0423 | 0.086975 | 0.20599 | 0.10986 | 0.17395
4969.1719 | 123.056 | -0.23346 | 122.7173 | -0.098725 | -0.00087374 | 0.013319 | 0.0098715 | -5.343e-05 | 0.00069649 | 0.00029479 | -0.044067 | 0.0025975 | 0.016876 | 0.002196 | 0.01772 | -0.0064343 | 0.0021619 | -0.1236 | 0.022888 | -0.27008 | -0.14648 | -0.041199 | -0.16022 | -0.086975 | -0.054932 | 0.14191 | -0.27924 | -0.022888 | 0.068665 | -0.073242 | 0.041199 | -0.036622 | -122.6944 | -122.8638 | 0.19226 | 0.14648 | 0.073242 | 0.18311 | 0.10986 | -0.045777 | -122.5754 | -122.7402 | 0.30212 | 0.27466 | 0.16022 | 0.32043 | 0.20599 | 0.22888 | 0.1236 | 0.3479 | 0.25635 | 0.29297 | 0.42114 | 0.25635 | 0.37537 | -122.9874 | -122.9965 | 0.086975 | 0.21057 | 0.10986 | 0.17853
4970.1719 | 123.0606 | -0.2243 | 122.7402 | -0.098725 | 0.0010489 | 0.014601 | 0.0079489 | 0.001442 | -0.00058531 | -0.00013241 | -0.062378 | 0.0017431 | 0.015381 | 0.0015552 | 0.018574 | -0.0038709 | -0.0040333 | -0.15564 | 0.018311 | -0.3067 | -0.15106 | -0.045776 | -0.16479 | -0.10071 | -0.07782 | 0.15564 | -0.28381 | -0.027466 | 0.054932 | -0.073242 | 0.041199 | -0.082398 | -122.7219 | -122.8912 | 0.17853 | 0.1236 | 0.059509 | 0.20599 | 0.14191 | -0.059509 | -122.5845 | -122.7676 | 0.27924 | 0.2655 | 0.15106 | 0.32501 | 0.21057 | 0.26093 | 0.15564 | 0.33874 | 0.25635 | 0.32501 | 0.43945 | 0.24261 | 0.37994 | -123.0469 | -123.024 | 0.073242 | 0.19684 | 0.068664 | 0.14648
4971.1719 | 123.0377 | -0.22888 | 122.731 | -0.12924 | -0.0019417 | 0.015669 | 0.010512 | -0.00048063 | 0.00048269 | -0.00098701 | -0.019653 | 0.0025975 | 0.018799 | 0.005614 | 0.018361 | -0.0045117 | -0.00082886 | -0.17853 | 0.027466 | -0.3067 | -0.19226 | -0.07782 | -0.19226 | -0.10986 | -0.086975 | 0.15564 | -0.28839 | -0.050354 | 0.041199 | -0.082397 | 0.036621 | -0.07782 | -122.7036 | -122.9233 | 0.15106 | 0.11902 | 0.036621 | 0.19684 | 0.11444 | -0.059509 | -122.5754 | -122.7814 | 0.27008 | 0.2655 | 0.14649 | 0.32501 | 0.20599 | 0.22888 | 0.11444 | 0.32959 | 0.23804 | 0.33417 | 0.44403 | 0.25635 | 0.38452 | -123.0377 | -123.0194 | 0.036621 | 0.17853 | 0.050354 | 0.14191
4972.1719 | 123.0469 | -0.23804 | 122.7173 | -0.075836 | -0.00023294 | 0.017805 | 0.0088033 | 0.00037377 | 0.0011237 | 0.00050839 | -0.053223 | 0.0011023 | 0.017731 | 0.0081774 | 0.019215 | -0.0064343 | -0.00082886 | -0.1236 | 0.004578 | -0.29297 | -0.14191 | -0.050354 | -0.16022 | -0.091553 | -0.064087 | 0.14648 | -0.27924 | -0.027466 | 0.054932 | -0.082397 | 0.045776 | -0.054932 | -122.7127 | -122.8592 | 0.18768 | 0.14648 | 0.07782 | 0.20142 | 0.13275 | -0.041199 | -122.5708 | -122.7448 | 0.29297 | 0.28381 | 0.15564 | 0.32501 | 0.19684 | 0.24261 | 0.15106 | 0.33417 | 0.25177 | 0.29755 | 0.42572 | 0.24261 | 0.38452 | -123.0103 | -122.9965 | 0.09613 | 0.21057 | 0.11444 | 0.17395
4973.1719 | 122.9965 | -0.25177 | 122.7539 | -0.098725 | -0.0019417 | 0.01396 | 0.0096579 | 0.00080117 | -0.0012261 | -0.00013241 | -0.059326 | 0.0036657 | 0.018158 | 0.0051868 | 0.01772 | -0.0057935 | 0.0013073 | -0.18768 | 0.050354 | -0.31128 | -0.2243 | -0.13733 | -0.23346 | -0.15106 | -0.13733 | 0.16479 | -0.30212 | -0.073242 | 0.013733 | -0.13275 | 0.004578 | -0.059509 | -122.7036 | -122.9782 | 0.11444 | 0.10071 | 0.018311 | 0.16022 | 0.07782 | -0.050354 | -122.5891 | -122.8271 | 0.2655 | 0.25635 | 0.11902 | 0.3067 | 0.16937 | 0.17395 | 0.086975 | 0.31586 | 0.22888 | 0.36163 | 0.46692 | 0.30212 | 0.41656 | -123.0652 | -123.056 | 0.027466 | 0.17853 | 0.064087 | 0.11444
4974.1719 | 123.0148 | -0.24261 | 122.7402 | -0.091095 | 0.0010489 | 0.013319 | 0.01094 | 0.0010148 | -0.00079891 | 0.00072199 | -0.056274 | 0.0038793 | 0.015381 | 0.0058276 | 0.017293 | -0.0062207 | -0.0027515 | -0.21057 | 0.068665 | -0.32044 | -0.25177 | -0.14191 | -0.25177 | -0.16479 | -0.16937 | 0.18768 | -0.30212 | -0.10986 | -0.022888 | -0.15106 | -0.022888 | -0.07782 | -122.6715 | -122.9919 | 0.10071 | 0.07782 | -0.009155 | 0.15564 | 0.068665 | -0.059509 | -122.5525 | -122.85 | 0.21973 | 0.21973 | 0.091553 | 0.27924 | 0.15106 | 0.17853 | 0.068665 | 0.27924 | 0.19226 | 0.3891 | 0.48981 | 0.31128 | 0.4303 | -123.0606 | -123.0423 | -0.009155 | 0.13275 | 0.032044 | 0.073242
4975.1719 | 123.0606 | -0.22888 | 122.7127 | -0.083466 | -0.0010873 | 0.015028 | 0.0083761 | 0.001442 | 0.00091009 | -0.00098701 | -0.022705 | 0.0032385 | 0.018585 | 0.00091422 | 0.01772 | -0.0060071 | -0.0023243 | -0.1831 | 0.036621 | -0.30212 | -0.19226 | -0.07782 | -0.18768 | -0.10529 | -0.09613 | 0.14648 | -0.28839 | -0.050354 | 0.041199 | -0.091553 | 0.027466 | -0.073242 | -122.6761 | -122.905 | 0.15106 | 0.1236 | 0.041199 | 0.19684 | 0.11444 | -0.059509 | -122.5662 | -122.7631 | 0.27008 | 0.25635 | 0.13733 | 0.31586 | 0.19684 | 0.2243 | 0.10986 | 0.32959 | 0.23804 | 0.33875 | 0.43488 | 0.2655 | 0.37537 | -123.0148 | -123.0011 | 0.036621 | 0.17853 | 0.045777 | 0.13275
4976.1719 | 123.056 | -0.21515 | 122.7264 | -0.11398 | -0.00087374 | 0.014601 | 0.0068807 | -0.00069423 | 5.5488e-05 | -0.0012006 | -0.01355 | 0.0028113 | 0.015808 | 0.003905 | 0.018361 | -0.0081433 | -0.0048877 | -0.13733 | 0.004578 | -0.28381 | -0.16022 | -0.032043 | -0.16937 | -0.086975 | -0.059509 | 0.14191 | -0.27466 | -0.022888 | 0.064087 | -0.07782 | 0.036621 | -0.068664 | -122.7219 | -122.8867 | 0.18311 | 0.12817 | 0.045776 | 0.19684 | 0.11444 | -0.059509 | -122.5845 | -122.7493 | 0.27924 | 0.25177 | 0.13733 | 0.31128 | 0.19684 | 0.25177 | 0.1236 | 0.33875 | 0.25177 | 0.28839 | 0.41657 | 0.21973 | 0.35706 | -123.0103 | -123.0011 | 0.054932 | 0.19226 | 0.07782 | 0.15564
4977.1719 | 123.0377 | -0.24261 | 122.7631 | -0.083466 | -0.0015145 | 0.016524 | 0.0083761 | 0.00016017 | -0.00015811 | 0.00050839 | -0.022705 | 0.0040929 | 0.018799 | 0.0054004 | 0.020283 | -0.0045117 | -0.0018971 | -0.20142 | 0.041199 | -0.31586 | -0.24719 | -0.14648 | -0.25177 | -0.17395 | -0.16022 | 0.16022 | -0.30212 | -0.10071 | -0.013733 | -0.13275 | 0.009155 | -0.073242 | -122.7219 | -123.0103 | 0.096131 | 0.068665 | -0.009155 | 0.14191 | 0.064087 | -0.059509 | -122.6028 | -122.8638 | 0.22888 | 0.25177 | 0.10986 | 0.31128 | 0.16937 | 0.16937 | 0.068665 | 0.28839 | 0.20142 | 0.35706 | 0.46234 | 0.28381 | 0.40283 | -123.0789 | -123.0652 | -0.004577 | 0.14191 | 0.041199 | 0.082398
4978.1719 | 123.0057 | -0.27466 | 122.7539 | -0.15213 | -0.00066014 | 0.014387 | 0.010299 | 0.00058737 | -0.00079891 | 0.00029479 | -0.034912 | 0.0030249 | 0.019653 | 0.002196 | 0.019643 | -0.0053663 | -0.0018971 | -0.21515 | 0.041199 | -0.31128 | -0.25635 | -0.17853 | -0.26093 | -0.17395 | -0.1831 | 0.19226 | -0.28381 | -0.11444 | -0.032043 | -0.16022 | -0.036621 | -0.036621 | -122.7127 | -123.0103 | 0.09613 | 0.10071 | 0.013733 | 0.13733 | 0.050354 | -0.009155 | -122.5616 | -122.8683 | 0.24262 | 0.23804 | 0.11444 | 0.24719 | 0.1236 | 0.13275 | 0.054931 | 0.25177 | 0.16937 | 0.35248 | 0.47607 | 0.31586 | 0.46692 | -123.0652 | -123.0377 | 0.01831 | 0.16022 | 0.059509 | 0.091553
4979.1719 | 123.0698 | -0.23346 | 122.7448 | -0.083466 | 0.0019035 | 0.014174 | 0.010299 | 0.0018692 | 0.0013373 | 0.0020038 | -0.034912 | 0.0030249 | 0.018585 | 0.0068958 | 0.02007 | -0.0053663 | 0.0015209 | -0.1831 | 0.045776 | -0.31128 | -0.21515 | -0.09613 | -0.21515 | -0.13275 | -0.11902 | 0.14648 | -0.28839 | -0.064087 | 0.036621 | -0.10986 | 0.027466 | -0.07782 | -122.699 | -122.9599 | 0.13733 | 0.10071 | 0.01831 | 0.17853 | 0.09613 | -0.054932 | -122.5983 | -122.8088 | 0.27008 | 0.26093 | 0.1236 | 0.31586 | 0.17853 | 0.21515 | 0.09613 | 0.32501 | 0.2243 | 0.35705 | 0.43488 | 0.27924 | 0.37994 | -123.056 | -123.0331 | 0.01831 | 0.16937 | 0.050354 | 0.11444
4980.1719 | 122.9233 | -0.27466 | 122.7585 | -0.091095 | -0.0010873 | 0.014815 | 0.0092307 | 0.0063554 | 0.0017645 | 0.00029479 | -0.074585 | 0.0013159 | 0.015808 | 0.0015552 | 0.019856 | -0.0057935 | -0.0042469 | -0.21057 | 0.050354 | -0.31128 | -0.27924 | -0.19226 | -0.27466 | -0.21515 | -0.24719 | 0.19684 | -0.29755 | -0.17395 | -0.086975 | -0.2243 | -0.07782 | -0.036621 | -122.7081 | -123.0377 | 0.082397 | 0.059509 | 0 | 0.09613 | 0.036621 | -0.022888 | -122.5616 | -122.9324 | 0.18768 | 0.19684 | 0.050354 | 0.21973 | 0.073242 | 0.11902 | 0.032043 | 0.21057 | 0.1236 | 0.36163 | 0.49438 | 0.32501 | 0.4715 | -123.0698 | -123.056 | -0.004578 | 0.10071 | 0.064087 | 0.027466
4981.1719 | 122.9507 | -0.29755 | 122.7539 | -0.13687 | 0.0014761 | 0.014601 | 0.0079489 | 0.00016017 | -0.00037171 | 0.00029479 | -0.025757 | 0.0019567 | 0.018799 | 0.0045458 | 0.019856 | -0.0057935 | 2.554e-05 | -0.23346 | 0.050354 | -0.32044 | -0.27924 | -0.18768 | -0.29297 | -0.20599 | -0.24719 | 0.16479 | -0.32501 | -0.16937 | -0.091553 | -0.21973 | -0.059509 | -0.022889 | -122.7036 | -123.0331 | 0.10986 | 0.091552 | 0.004577 | 0.11444 | 0.027466 | -0.027466 | -122.5891 | -122.9233 | 0.20599 | 0.23804 | 0.077819 | 0.2655 | 0.10529 | 0.13275 | 0.041199 | 0.23346 | 0.15564 | 0.37079 | 0.48981 | 0.3479 | 0.46234 | -123.0743 | -123.0789 | 0.01831 | 0.12817 | 0.064087 | 0.050354
4982.1719 | 122.9874 | -0.28381 | 122.7402 | -0.083466 | -0.0013009 | 0.015028 | 0.0090169 | -0.00090783 | -0.0010125 | -0.0014142 | -0.03186 | 0.0023839 | 0.017731 | 0.002196 | 0.020711 | -0.0068615 | -0.0025379 | -0.21515 | 0.086975 | -0.32501 | -0.27008 | -0.17853 | -0.27924 | -0.18768 | -0.20599 | 0.18768 | -0.30212 | -0.14648 | -0.064087 | -0.19684 | -0.036621 | -0.041199 | -122.6532 | -123.0103 | 0.10528 | 0.09613 | 0.004577 | 0.13733 | 0.045776 | -0.018311 | -122.5525 | -122.8867 | 0.21973 | 0.24719 | 0.086975 | 0.2655 | 0.10529 | 0.14648 | 0.054931 | 0.23804 | 0.15564 | 0.41199 | 0.48981 | 0.37079 | 0.4715 | -123.0652 | -123.0423 | 0.013732 | 0.13733 | 0.068664 | 0.077819
4983.1719 | 122.9507 | -0.27008 | 122.7631 | -0.083466 | -0.00023294 | 0.015242 | 0.0098715 | 0.0022964 | -0.0029351 | -0.00098701 | -0.041016 | 0.0032385 | 0.017517 | 0.0013416 | 0.019856 | -0.0077161 | 0.0013073 | -0.21973 | 0.036621 | -0.32959 | -0.27466 | -0.17853 | -0.29297 | -0.19684 | -0.2243 | 0.16937 | -0.32044 | -0.16479 | -0.082397 | -0.2243 | -0.050354 | -0.059509 | -122.7264 | -123.0377 | 0.091553 | 0.073243 | -0.022888 | 0.13275 | 0.036621 | -0.050354 | -122.5937 | -122.9279 | 0.18768 | 0.21973 | 0.045777 | 0.27008 | 0.096131 | 0.15106 | 0.054932 | 0.23804 | 0.15564 | 0.36621 | 0.48981 | 0.3067 | 0.43945 | -123.0927 | -123.0835 | -0.004577 | 0.10529 | 0.050354 | 0.045777
4984.1719 | 122.9462 | -0.27466 | 122.7676 | -0.083466 | 0.00083526 | 0.015028 | 0.0081625 | 0.00251 | -0.00037171 | -0.00034601 | -0.050171 | 0.0034521 | 0.017303 | 5.9824e-05 | 0.018574 | -0.0051527 | 0.0028027 | -0.22888 | 0.032043 | -0.31128 | -0.27924 | -0.20142 | -0.29755 | -0.19226 | -0.23804 | 0.16479 | -0.29755 | -0.16479 | -0.086975 | -0.21973 | -0.064087 | -0.036621 | -122.7356 | -123.0469 | 0.073242 | 0.082397 | -0.022888 | 0.11902 | 0.013733 | -0.022888 | -122.6028 | -122.9324 | 0.18768 | 0.21057 | 0.054931 | 0.23346 | 0.077819 | 0.10986 | 0.032043 | 0.21057 | 0.13275 | 0.34332 | 0.46234 | 0.3067 | 0.43945 | -123.0789 | -123.0652 | -0.004578 | 0.10986 | 0.045776 | 0.036621
4985.1719 | 122.9507 | -0.27008 | 122.7768 | -0.075836 | -0.0013009 | 0.014387 | 0.010512 | -0.00090783 | -0.0012261 | 0.00093559 | -0.06543 | 0.0021703 | 0.017303 | 0.0101 | 0.017934 | -0.0070753 | 2.554e-05 | -0.21057 | 0.073242 | -0.31586 | -0.27466 | -0.21057 | -0.29297 | -0.2243 | -0.24719 | 0.16479 | -0.32501 | -0.16022 | -0.082397 | -0.22888 | -0.073242 | -0.045776 | -122.7036 | -123.0515 | 0.05951 | 0.045777 | -0.022888 | 0.091553 | 0.022888 | -0.054931 | -122.612 | -122.937 | 0.18768 | 0.19684 | 0.041199 | 0.25177 | 0.09613 | 0.10529 | 0.041199 | 0.24262 | 0.1648 | 0.3891 | 0.48981 | 0.34332 | 0.43488 | -123.0927 | -123.1018 | -0.004577 | 0.10986 | 0.05951 | 0.022889
4986.2344 | 122.9553 | -0.27008 | 122.7722 | -0.03006 | -0.0013009 | 0.015669 | 0.011367 | 0.00037377 | 0.0017645 | 0.0020038 | -0.022705 | 0.0036657 | 0.017517 | 0.0045458 | 0.017934 | -0.0079297 | -0.00082886 | -0.21057 | 0.050354 | -0.31586 | -0.28839 | -0.20599 | -0.27924 | -0.21515 | -0.26093 | 0.18768 | -0.32044 | -0.16022 | -0.082397 | -0.21057 | -0.054932 | -0.045776 | -122.7219 | -123.0606 | 0.064087 | 0.054932 | -0.009155 | 0.10071 | 0.036621 | -0.050354 | -122.5845 | -122.9324 | 0.18768 | 0.21515 | 0.05951 | 0.2655 | 0.10986 | 0.10986 | 0.027466 | 0.23804 | 0.16022 | 0.36621 | 0.50812 | 0.32044 | 0.45776 | -123.0881 | -123.0927 | -0.01831 | 0.10986 | 0.05951 | 0.009156
4987.1719 | 122.9141 | -0.27924 | 122.7859 | -0.03006 | 0.00019446 | 0.016096 | 0.0079489 | 0.0029374 | 0.00026909 | -0.0024822 | -0.03186 | 0.0023839 | 0.017517 | 0.0045458 | 0.020711 | -0.0047253 | -0.0012561 | -0.20142 | 0.036621 | -0.31128 | -0.25177 | -0.16479 | -0.27466 | -0.20142 | -0.22888 | 0.16479 | -0.31128 | -0.19226 | -0.082397 | -0.21515 | -0.082397 | -0.032043 | -122.7493 | -123.0377 | 0.11444 | 0.07782 | 0.004578 | 0.10986 | 0.036621 | -0.032043 | -122.6212 | -122.9782 | 0.19684 | 0.19684 | 0.064087 | 0.22888 | 0.09613 | 0.14648 | 0.059509 | 0.22888 | 0.11902 | 0.3479 | 0.47607 | 0.31586 | 0.44403 | -123.0972 | -123.0972 | 0.027466 | 0.086975 | 0.07782 | 0.050354
4988.1719 | 122.9416 | -0.28839 | 122.7676 | -0.045319 | -0.0021555 | 0.015883 | 0.0083761 | 0.0016556 | -0.00037171 | 0.0017902 | -0.037964 | 0.0017431 | 0.017303 | 0.0060412 | 0.018788 | -0.0060071 | 0.00066654 | -0.17853 | 0.054932 | -0.30212 | -0.2655 | -0.13733 | -0.25635 | -0.1831 | -0.19226 | 0.16479 | -0.31128 | -0.16937 | -0.082397 | -0.19684 | -0.073242 | -0.013733 | -122.7127 | -123.0331 | 0.15106 | 0.10529 | 0.032043 | 0.11902 | 0.045776 | -0.022888 | -122.6028 | -122.937 | 0.20599 | 0.21515 | 0.091553 | 0.23804 | 0.11444 | 0.16479 | 0.036621 | 0.22888 | 0.14191 | 0.35706 | 0.47607 | 0.34332 | 0.45319 | -123.0698 | -123.0789 | 0.022888 | 0.11902 | 0.10986 | 0.09613
4989.1719 | 122.937 | -0.29297 | 122.7814 | -0.12161 | -0.0013009 | 0.015028 | 0.0096579 | 0.0012284 | 0.00026909 | -0.00098701 | -0.028809 | 0.0021703 | 0.016235 | -0.0048536 | 0.018574 | -0.0068615 | -0.0036059 | -0.22888 | 0.045776 | -0.32501 | -0.28839 | -0.18768 | -0.29755 | -0.20599 | -0.2243 | 0.17853 | -0.32959 | -0.16479 | -0.086975 | -0.20142 | -0.059509 | -0.032043 | -122.7356 | -123.0698 | 0.10529 | 0.086975 | -0.004577 | 0.11902 | 0.027466 | -0.036621 | -122.6028 | -122.9462 | 0.20599 | 0.23346 | 0.091553 | 0.27008 | 0.12817 | 0.13733 | 0.036621 | 0.24261 | 0.16479 | 0.37079 | 0.50812 | 0.33874 | 0.4715 | -123.1064 | -123.111 | 0.004578 | 0.12817 | 0.064087 | 0.068665
4990.1719 | 122.9599 | -0.2655 | 122.7951 | -0.10635 | 0.00062166 | 0.016096 | 0.0098715 | 0.0040054 | 0.0017645 | -0.0016278 | -0.044067 | 0.0013159 | 0.018158 | 0.005614 | 0.018361 | -0.0068615 | -0.0021107 | -0.19226 | 0.041199 | -0.30212 | -0.24719 | -0.13733 | -0.25635 | -0.19226 | -0.19684 | 0.16022 | -0.32959 | -0.15564 | -0.068665 | -0.20142 | -0.068665 | -0.036621 | -122.7539 | -123.0423 | 0.12817 | 0.073242 | 0.009155 | 0.10986 | 0.045776 | -0.064087 | -122.6349 | -122.9507 | 0.19684 | 0.19684 | 0.064087 | 0.26092 | 0.12817 | 0.16479 | 0.054932 | 0.26092 | 0.17395 | 0.34332 | 0.48981 | 0.3067 | 0.42572 | -123.0972 | -123.1247 | 0.018311 | 0.10986 | 0.073242 | 0.068665
4991.2344 | 123.0194 | -0.2655 | 122.7631 | -0.022431 | -0.0017281 | 0.014815 | 0.0081625 | 0.0022964 | -0.0012261 | -0.0018414 | -0.010498 | 0.0032385 | 0.015808 | 0.0047594 | 0.019856 | -0.0064343 | 0.00045294 | -0.1831 | 0.036621 | -0.3067 | -0.23346 | -0.10986 | -0.20599 | -0.14191 | -0.15564 | 0.15564 | -0.3067 | -0.13275 | -0.036621 | -0.15564 | -0.013733 | -0.041199 | -122.7264 | -122.9965 | 0.15564 | 0.1236 | 0.059509 | 0.16479 | 0.10071 | -0.041199 | -122.6074 | -122.8958 | 0.22888 | 0.25177 | 0.10986 | 0.29297 | 0.15106 | 0.19684 | 0.073243 | 0.27008 | 0.17395 | 0.34332 | 0.46234 | 0.30212 | 0.42114 | -123.0698 | -123.0698 | 0.032044 | 0.13275 | 0.082398 | 0.10986
4992.1719 | 123.0515 | -0.25635 | 122.7539 | -0.15213 | -0.0017281 | 0.013747 | 0.0058127 | -0.0021896 | -0.00058531 | -0.0014142 | 0.035278 | 0.00088875 | 0.018158 | 0.00048702 | 0.018147 | -0.0070753 | -0.0016833 | -0.15564 | 0 | -0.27924 | -0.1831 | -0.036621 | -0.16937 | -0.091553 | -0.07782 | 0.13733 | -0.28381 | -0.10071 | 0.022888 | -0.091553 | 0.004578 | -0.022888 | -122.7539 | -122.937 | 0.21973 | 0.1648 | 0.086975 | 0.18768 | 0.10986 | -0.027465 | -122.6166 | -122.8546 | 0.27924 | 0.26093 | 0.1648 | 0.28839 | 0.19226 | 0.24261 | 0.096131 | 0.3067 | 0.1831 | 0.27924 | 0.42114 | 0.25635 | 0.39368 | -123.0331 | -123.0377 | 0.073243 | 0.15564 | 0.10071 | 0.17853
4993.1719 | 122.9782 | -0.30212 | 122.7859 | -0.075836 | 0.00062166 | 0.014815 | 0.010512 | 0.0033646 | 0.00091009 | 0.00093559 | -0.037964 | 0.0015295 | 0.020081 | 0.0030506 | 0.017934 | -0.0057935 | -0.0031787 | -0.21057 | 0.041199 | -0.33417 | -0.28381 | -0.19684 | -0.29297 | -0.20142 | -0.21515 | 0.16022 | -0.32044 | -0.17853 | -0.10071 | -0.22888 | -0.073242 | -0.032043 | -122.7448 | -123.0698 | 0.10529 | 0.10071 | 0.009155 | 0.13275 | 0.041198 | -0.018311 | -122.6257 | -122.9645 | 0.20142 | 0.22888 | 0.073242 | 0.24719 | 0.091553 | 0.13733 | 0.050354 | 0.21973 | 0.14191 | 0.37537 | 0.48065 | 0.34332 | 0.46234 | -123.1201 | -123.1064 | 0.018311 | 0.1236 | 0.091553 | 0.086975
4994.1719 | 123.0286 | -0.2655 | 122.7539 | -0.098725 | 0.0010489 | 0.017165 | 0.0085897 | -0.0024032 | 0.00091009 | 0.00093559 | -0.0074462 | 0.0036657 | 0.016449 | 0.0026232 | 0.017293 | -0.0057935 | -0.0029651 | -0.17395 | 0.045776 | -0.32959 | -0.22888 | -0.1236 | -0.21515 | -0.15564 | -0.14648 | 0.15564 | -0.29755 | -0.14648 | -0.036621 | -0.16022 | -0.041199 | -0.064087 | -122.7081 | -122.9828 | 0.14191 | 0.10986 | 0.050354 | 0.17395 | 0.11444 | -0.032043 | -122.5983 | -122.9004 | 0.22888 | 0.2243 | 0.10529 | 0.25635 | 0.13733 | 0.20599 | 0.10071 | 0.26092 | 0.15106 | 0.37537 | 0.45319 | 0.31128 | 0.42114 | -123.0835 | -123.0515 | 0.036621 | 0.11902 | 0.091553 | 0.11902
4995.1719 | 123.0103 | -0.27466 | 122.7814 | 0.00045798 | -0.0017281 | 0.015669 | 0.0073081 | 0.00080117 | 5.5488e-05 | 8.1188e-05 | 0.016968 | 0.0017431 | 0.018158 | 0.0071094 | 0.019856 | -0.0051527 | 0.0010937 | -0.20142 | 0.041199 | -0.32959 | -0.23346 | -0.14191 | -0.20142 | -0.16479 | -0.16022 | 0.15106 | -0.32044 | -0.13733 | -0.036621 | -0.15564 | -0.041199 | -0.054932 | -122.7402 | -123.0148 | 0.13275 | 0.10986 | 0.073242 | 0.16479 | 0.12817 | -0.045777 | -122.6303 | -122.9187 | 0.23804 | 0.23346 | 0.11902 | 0.27924 | 0.1648 | 0.18768 | 0.096131 | 0.28381 | 0.18311 | 0.37079 | 0.4715 | 0.31586 | 0.42572 | -123.111 | -123.1018 | 0.041199 | 0.13733 | 0.073242 | 0.11444
4996.1719 | 123.0331 | -0.27466 | 122.7585 | 0.015716 | -0.0010873 | 0.015456 | 0.0073081 | -0.0038986 | -0.0025079 | -0.0018414 | -0.01355 | 0.0032385 | 0.018158 | 0.005614 | 0.016438 | -0.0060071 | -0.0029651 | -0.17395 | 0.036621 | -0.33417 | -0.22888 | -0.12817 | -0.21057 | -0.15564 | -0.14191 | 0.16022 | -0.29755 | -0.14191 | -0.036621 | -0.16937 | -0.045776 | -0.059509 | -122.7219 | -122.9874 | 0.14648 | 0.11902 | 0.064087 | 0.17853 | 0.1236 | -0.022888 | -122.5983 | -122.9004 | 0.23804 | 0.22888 | 0.10529 | 0.25177 | 0.12817 | 0.20599 | 0.10528 | 0.26092 | 0.15564 | 0.37079 | 0.45776 | 0.31128 | 0.43488 | -123.0927 | -123.056 | 0.045776 | 0.13275 | 0.10071 | 0.13275
4997.25 | 123.1247 | -0.23804 | 122.731 | -0.03006 | -0.00044654 | 0.01161 | 0.0064535 | 0.00016017 | -0.00058531 | 8.1188e-05 | 0.096313 | 0.00067495 | 0.017731 | -0.0016492 | 0.019429 | -0.0072889 | 0.0025891 | -0.15564 | 0.018311 | -0.28381 | -0.16479 | -0.018311 | -0.12817 | -0.073242 | -0.041199 | 0.12817 | -0.29297 | -0.059509 | 0.068665 | -0.050354 | 0.022888 | -0.045776 | -122.7127 | -122.8958 | 0.21973 | 0.16479 | 0.10986 | 0.21057 | 0.15564 | -0.054932 | -122.6028 | -122.7905 | 0.3067 | 0.26093 | 0.18768 | 0.31586 | 0.24261 | 0.2655 | 0.11902 | 0.36163 | 0.23346 | 0.30212 | 0.42114 | 0.25635 | 0.36621 | -123.0148 | -123.024 | 0.073242 | 0.17853 | 0.082397 | 0.19684
4998.1719 | 123.0148 | -0.27924 | 122.7814 | -0.083466 | 0.00083526 | 0.015456 | 0.0088033 | -0.0015488 | -0.0018671 | -0.00034601 | 0.0078126 | 0.0032385 | 0.017731 | 0.0013416 | 0.019856 | -0.0057935 | -0.0023243 | -0.21057 | 0.032043 | -0.31586 | -0.26093 | -0.1831 | -0.23346 | -0.18768 | -0.17853 | 0.16022 | -0.31586 | -0.16479 | -0.036621 | -0.15564 | -0.050354 | -0.036621 | -122.7493 | -123.0423 | 0.096131 | 0.091553 | 0.045777 | 0.12817 | 0.082398 | -0.036621 | -122.6212 | -122.9462 | 0.24261 | 0.22888 | 0.1236 | 0.2655 | 0.16022 | 0.13275 | 0.054932 | 0.27924 | 0.15106 | 0.3479 | 0.47607 | 0.31128 | 0.43945 | -123.0972 | -123.0972 | 0.018311 | 0.11444 | 0.068665 | 0.10071
4999.1719 | 122.9965 | -0.27008 | 122.7814 | -0.045319 | -0.00023294 | 0.015028 | 0.0083761 | -0.00069423 | -0.00015811 | -0.0012006 | -0.010498 | 0.0013159 | 0.018372 | 0.0058276 | 0.020283 | -0.0062207 | -0.0025379 | -0.21057 | 0.022888 | -0.32044 | -0.27008 | -0.1831 | -0.25177 | -0.17853 | -0.21515 | 0.16937 | -0.32959 | -0.20142 | -0.068665 | -0.18768 | -0.07782 | -0.050354 | -122.7585 | -123.0515 | 0.086976 | 0.091553 | 0.018311 | 0.14191 | 0.068665 | -0.059509 | -122.612 | -122.9828 | 0.20142 | 0.19226 | 0.082398 | 0.25177 | 0.14191 | 0.13733 | 0.050354 | 0.26092 | 0.12817 | 0.34332 | 0.49896 | 0.29297 | 0.43945 | -123.1018 | -123.111 | 0 | 0.068665 | 0.05951 | 0.054932
5000.1719 | 122.9874 | -0.27924 | 122.7676 | -0.022431 | 0.00062166 | 0.014387 | 0.0096579 | -0.00026703 | 0.00026909 | 0.00072199 | -0.0013428 | 0.0011023 | 0.019012 | 0.0043322 | 0.019002 | -0.0070753 | 0.0025891 | -0.20599 | 0.032043 | -0.32959 | -0.25635 | -0.16022 | -0.21973 | -0.17853 | -0.1831 | 0.15564 | -0.31128 | -0.17395 | -0.032043 | -0.17395 | -0.027466 | -0.050354 | -122.7356 | -123.024 | 0.11902 | 0.10071 | 0.059509 | 0.15106 | 0.10986 | -0.032043 | -122.612 | -122.9416 | 0.24719 | 0.25177 | 0.10529 | 0.28381 | 0.13733 | 0.16937 | 0.073242 | 0.27924 | 0.13733 | 0.36163 | 0.46692 | 0.31128 | 0.43488 | -123.0972 | -123.0789 | 0.022888 | 0.10529 | 0.073242 | 0.096131
5001.1719 | 122.9553 | -0.28839 | 122.7951 | -0.091095 | 0.00019446 | 0.014601 | 0.0064535 | -0.0032578 | -0.0012261 | 8.1188e-05 | -0.0013428 | 0.0036657 | 0.018799 | 0.0054004 | 0.016865 | -0.0083569 | -0.0031787 | -0.23804 | 0.032043 | -0.32501 | -0.28381 | -0.17395 | -0.24719 | -0.18768 | -0.21515 | 0.16479 | -0.32501 | -0.20599 | -0.07782 | -0.19226 | -0.07782 | -0.036621 | -122.7631 | -123.0789 | 0.11444 | 0.10071 | 0.041199 | 0.13733 | 0.07782 | -0.036621 | -122.6303 | -123.0011 | 0.21057 | 0.21057 | 0.09613 | 0.24719 | 0.13275 | 0.15106 | 0.041199 | 0.24719 | 0.11902 | 0.35706 | 0.48981 | 0.32043 | 0.45319 | -123.1201 | -123.1201 | 0.004578 | 0.082397 | 0.050354 | 0.073242
5002.1719 | 122.9828 | -0.28381 | 122.7905 | -0.10635 | -1.9142e-05 | 0.01396 | 0.010085 | 0.0020828 | 0.0017645 | -0.0014142 | -0.041016 | 0.0036657 | 0.017731 | 0.0071094 | 0.018147 | -0.0070753 | -0.0010425 | -0.2243 | 0.041199 | -0.31586 | -0.28381 | -0.20142 | -0.30212 | -0.20142 | -0.21057 | 0.16937 | -0.33875 | -0.17853 | -0.09613 | -0.21973 | -0.068665 | -0.032044 | -122.7493 | -123.0743 | 0.082397 | 0.082397 | -0.018311 | 0.11444 | 0.013733 | -0.054932 | -122.6212 | -122.9691 | 0.18768 | 0.21515 | 0.064086 | 0.27008 | 0.11902 | 0.11444 | 0.032044 | 0.24262 | 0.16022 | 0.35706 | 0.50812 | 0.32501 | 0.45319 | -123.1064 | -123.1293 | 0 | 0.10528 | 0.059509 | 0.073242
5003.1719 | 122.9874 | -0.28839 | 122.7814 | 0.023346 | -1.9142e-05 | 0.01396 | 0.011153 | 0.0029374 | -0.0014399 | -0.002055 | 0.0078126 | 0.0030249 | 0.01709 | 0.0043322 | 0.016652 | -0.0064343 | -0.00040166 | -0.19684 | 0.032043 | -0.33875 | -0.27466 | -0.17395 | -0.23346 | -0.17853 | -0.20142 | 0.16479 | -0.33417 | -0.16937 | -0.032043 | -0.17395 | -0.050354 | -0.050354 | -122.7493 | -123.056 | 0.11444 | 0.10986 | 0.054932 | 0.16022 | 0.10529 | -0.045776 | -122.6166 | -122.9507 | 0.25635 | 0.23804 | 0.11444 | 0.28381 | 0.16022 | 0.1648 | 0.064087 | 0.30212 | 0.16479 | 0.37079 | 0.49896 | 0.32043 | 0.45319 | -123.1201 | -123.1155 | 0.013733 | 0.11902 | 0.091553 | 0.086975
5004.1719 | 122.9324 | -0.29297 | 122.7722 | -0.075836 | -0.00044654 | 0.014815 | 0.0077353 | -0.00090783 | -0.00037171 | -0.00098701 | 0.035278 | 0.0030249 | 0.016876 | 0.0077502 | 0.017506 | -0.0075025 | -0.0053149 | -0.24261 | 0.036621 | -0.32959 | -0.28381 | -0.17395 | -0.25177 | -0.17395 | -0.21973 | 0.16022 | -0.33417 | -0.21057 | -0.082397 | -0.20599 | -0.082397 | -0.036621 | -122.7356 | -123.056 | 0.11902 | 0.11902 | 0.041199 | 0.15564 | 0.07782 | -0.041198 | -122.612 | -122.9828 | 0.21057 | 0.21057 | 0.086975 | 0.25177 | 0.12817 | 0.15564 | 0.045777 | 0.25177 | 0.1236 | 0.36621 | 0.49438 | 0.32959 | 0.45319 | -123.1018 | -123.1064 | 0.009156 | 0.082398 | 0.050354 | 0.073242
5005.1719 | 122.9645 | -0.3067 | 122.7814 | -0.045319 | -0.00044654 | 0.014601 | 0.0077353 | -0.00090783 | 0.00048269 | -0.0024822 | 0.013916 | 0.0034521 | 0.018799 | -0.00036738 | 0.018574 | -0.0098523 | 0.0030163 | -0.21515 | 0.022888 | -0.32044 | -0.27008 | -0.17853 | -0.24719 | -0.1831 | -0.21515 | 0.16022 | -0.32044 | -0.20599 | -0.068665 | -0.19684 | -0.10529 | -0.013733 | -122.7585 | -123.0515 | 0.12817 | 0.1236 | 0.05951 | 0.13733 | 0.073243 | -0.013733 | -122.6212 | -122.9874 | 0.23804 | 0.20142 | 0.10986 | 0.21515 | 0.1236 | 0.14191 | 0.050354 | 0.25177 | 0.11444 | 0.34332 | 0.48065 | 0.32959 | 0.46692 | -123.1018 | -123.1018 | 0.036621 | 0.10071 | 0.091553 | 0.091553
5006.1719 | 122.9965 | -0.3067 | 122.8088 | -0.091095 | 0.00083526 | 0.013319 | 0.0064535 | -0.001976 | -0.00037171 | -0.0029096 | 0.02002 | 0.0034521 | 0.016449 | 0.0043322 | 0.018361 | -0.0068615 | 0.0021619 | -0.19684 | 0.022888 | -0.32501 | -0.2655 | -0.14648 | -0.22888 | -0.16937 | -0.20142 | 0.15564 | -0.32044 | -0.20599 | -0.082397 | -0.19684 | -0.082397 | -0.01831 | -122.7859 | -123.0743 | 0.16022 | 0.13733 | 0.07782 | 0.15564 | 0.09613 | -0.013733 | -122.6532 | -123.0148 | 0.2243 | 0.2243 | 0.10986 | 0.23804 | 0.1236 | 0.17853 | 0.059509 | 0.23804 | 0.11444 | 0.3479 | 0.47608 | 0.32959 | 0.46234 | -123.1338 | -123.1293 | 0.041199 | 0.10071 | 0.10986 | 0.10529
5007.1719 | 123.0011 | -0.28839 | 122.7814 | -0.052948 | -0.00066014 | 0.01396 | 0.0090169 | 0.00037377 | 5.5488e-05 | -0.00055961 | 0.029175 | 0.0034521 | 0.017303 | 0.0077502 | 0.01772 | -0.0083569 | -0.0029651 | -0.16479 | 0.004578 | -0.3067 | -0.23346 | -0.10529 | -0.19226 | -0.13733 | -0.15564 | 0.14648 | -0.32044 | -0.19684 | -0.064087 | -0.1831 | -0.07782 | -0.018311 | -122.7768 | -123.0148 | 0.18311 | 0.15106 | 0.09613 | 0.16937 | 0.11444 | -0.032044 | -122.6349 | -122.9782 | 0.2243 | 0.21057 | 0.10529 | 0.24262 | 0.13733 | 0.20142 | 0.073243 | 0.25635 | 0.1236 | 0.31128 | 0.46692 | 0.29297 | 0.43488 | -123.0881 | -123.1018 | 0.054932 | 0.091553 | 0.1236 | 0.13275
5008.1719 | 122.9919 | -0.28381 | 122.7722 | -0.0071715 | -0.0015145 | 0.014601 | 0.0073081 | -0.00026703 | -0.0033625 | -0.0029096 | -0.0013428 | 0.0028113 | 0.018158 | 0.0068958 | 0.018361 | -0.0072889 | -0.0048877 | -0.21973 | 0.027466 | -0.33417 | -0.29297 | -0.17395 | -0.25635 | -0.17853 | -0.21057 | 0.16479 | -0.32044 | -0.20142 | -0.082397 | -0.20599 | -0.09613 | -0.050354 | -122.7448 | -123.0652 | 0.10986 | 0.10528 | 0.027465 | 0.15564 | 0.077819 | -0.036622 | -122.6074 | -122.9736 | 0.20142 | 0.18768 | 0.077819 | 0.22431 | 0.11444 | 0.16022 | 0.041198 | 0.23804 | 0.11902 | 0.36163 | 0.48523 | 0.31128 | 0.44861 | -123.1064 | -123.0927 | -0.009156 | 0.082397 | 0.064086 | 0.073242
5009.1719 | 123.0377 | -0.27466 | 122.7676 | -0.068207 | -0.0021555 | 0.012679 | 0.0062399 | 0.0040054 | 0.00069649 | -0.0024822 | 0.026123 | 0.0032385 | 0.019653 | 0.0045458 | 0.018574 | -0.0068615 | -0.0014697 | -0.15106 | -0.018311 | -0.3067 | -0.1831 | -0.054932 | -0.16022 | -0.1236 | -0.13275 | 0.1236 | -0.3067 | -0.16479 | -0.004578 | -0.14191 | -0.036621 | -0.032044 | -122.7859 | -122.9507 | 0.21973 | 0.15106 | 0.11444 | 0.18311 | 0.14648 | -0.032044 | -122.644 | -122.9324 | 0.27008 | 0.23804 | 0.13275 | 0.27008 | 0.16479 | 0.25177 | 0.1236 | 0.30212 | 0.14191 | 0.28839 | 0.4303 | 0.25635 | 0.39825 | -123.0743 | -123.0743 | 0.091553 | 0.10986 | 0.1236 | 0.14191
5010.2344 | 123.0789 | -0.27008 | 122.7539 | -0.091095 | 0.00083526 | 0.015456 | 0.0088033 | 0.00037377 | -0.00015811 | 0.00050839 | 0.056641 | 0.0013159 | 0.016663 | -0.0018628 | 0.01772 | -0.0077161 | -0.0016833 | -0.14191 | -0.013733 | -0.27924 | -0.15564 | -0.027466 | -0.13733 | -0.082397 | -0.064087 | 0.10986 | -0.3067 | -0.11444 | 0.054932 | -0.086975 | 0 | -0.009155 | -122.7676 | -122.9095 | 0.24262 | 0.18768 | 0.13275 | 0.19684 | 0.14191 | -0.036621 | -122.644 | -122.8683 | 0.32501 | 0.27008 | 0.18311 | 0.3067 | 0.21973 | 0.25177 | 0.1236 | 0.36163 | 0.19226 | 0.2655 | 0.41656 | 0.25635 | 0.37994 | -123.0331 | -123.0606 | 0.11444 | 0.15564 | 0.12817 | 0.20599
5011.1719 | 122.9828 | -0.29297 | 122.7951 | -0.052948 | -0.00044654 | 0.012892 | 0.0094443 | 0.00058737 | 0.00026909 | 0.00093559 | -0.022705 | 0.0038793 | 0.017944 | 0.002196 | 0.016652 | -0.0062207 | -0.0040333 | -0.22888 | 0.032043 | -0.33417 | -0.27008 | -0.19226 | -0.27466 | -0.19226 | -0.21973 | 0.16022 | -0.32959 | -0.21973 | -0.082397 | -0.19684 | -0.082397 | -0.041198 | -122.7631 | -123.0652 | 0.10071 | 0.10071 | 0.018311 | 0.14191 | 0.059509 | -0.036621 | -122.6349 | -123.0148 | 0.21057 | 0.21057 | 0.096131 | 0.24719 | 0.13275 | 0.14191 | 0.064086 | 0.24719 | 0.10986 | 0.36621 | 0.48981 | 0.32501 | 0.45319 | -123.1293 | -123.1247 | 0.022888 | 0.073242 | 0.064087 | 0.073242
5012.1719 | 122.9828 | -0.29297 | 122.7997 | -0.0071715 | 0.00083526 | 0.01396 | 0.0088033 | -0.00090783 | -0.0020807 | -0.0012006 | 0.001709 | 0.0040929 | 0.018158 | 0.0036914 | 0.019215 | -0.0060071 | -0.0010425 | -0.23804 | 0.036621 | -0.32959 | -0.27924 | -0.17853 | -0.2655 | -0.17395 | -0.21973 | 0.14191 | -0.33417 | -0.21515 | -0.07782 | -0.21973 | -0.086975 | -0.036621 | -122.7631 | -123.0789 | 0.11444 | 0.11902 | 0.027466 | 0.15564 | 0.064087 | -0.041198 | -122.6578 | -123.0148 | 0.21515 | 0.20599 | 0.073242 | 0.24719 | 0.11444 | 0.15106 | 0.050354 | 0.25635 | 0.11902 | 0.36621 | 0.47607 | 0.32959 | 0.43488 | -123.1293 | -123.1338 | 0.013733 | 0.07782 | 0.054932 | 0.073242
5013.1719 | 122.9965 | -0.3067 | 122.7676 | -0.083466 | 0.0010489 | 0.014174 | 0.0098715 | -0.0028304 | 0.00026909 | -0.00098701 | 0.001709 | 0.0045203 | 0.019653 | 0.0088184 | 0.019215 | -0.0062207 | 0.0017345 | -0.2243 | 0.032043 | -0.3479 | -0.27466 | -0.19684 | -0.2655 | -0.19684 | -0.21973 | 0.15564 | -0.3479 | -0.20142 | -0.07782 | -0.20599 | -0.07782 | -0.041198 | -122.7356 | -123.0423 | 0.10986 | 0.10986 | 0.041199 | 0.15106 | 0.082397 | -0.041198 | -122.612 | -122.9691 | 0.22888 | 0.22888 | 0.10071 | 0.27008 | 0.14191 | 0.15106 | 0.073242 | 0.27008 | 0.14648 | 0.37994 | 0.50354 | 0.33874 | 0.46234 | -123.1155 | -123.1155 | 0.032044 | 0.10529 | 0.082398 | 0.086975
5014.1719 | 122.9965 | -0.2655 | 122.7676 | -0.098725 | -0.00066014 | 0.016737 | 0.0068807 | -0.0041122 | -0.00037171 | -0.0018414 | 0.03833 | 0.0013159 | 0.018799 | 0.0066822 | 0.017293 | -0.0077161 | -0.0029651 | -0.16479 | 0 | -0.29297 | -0.17853 | -0.059509 | -0.14648 | -0.10529 | -0.11902 | 0.11444 | -0.3067 | -0.16022 | -0.013733 | -0.14648 | -0.041199 | -0.027466 | -122.7676 | -122.9462 | 0.20599 | 0.16022 | 0.11902 | 0.18768 | 0.14648 | -0.041199 | -122.6532 | -122.9279 | 0.25177 | 0.2243 | 0.11902 | 0.2655 | 0.16022 | 0.23346 | 0.11444 | 0.29297 | 0.14648 | 0.29297 | 0.42114 | 0.2655 | 0.37994 | -123.0606 | -123.0743 | 0.086975 | 0.10529 | 0.10071 | 0.14648
5015.1719 | 123.0377 | -0.28381 | 122.7493 | -0.075836 | -0.0021555 | 0.016524 | 0.0081625 | 0.0018692 | -0.00037171 | -0.0039776 | 0.029175 | 0.0015295 | 0.017944 | 0.0026232 | 0.01772 | -0.0062207 | -0.0029651 | -0.15564 | -0.004578 | -0.3067 | -0.18768 | -0.054932 | -0.16022 | -0.10986 | -0.10529 | 0.11902 | -0.30212 | -0.13733 | 0.013733 | -0.10071 | -0.027466 | -0.022889 | -122.7539 | -122.937 | 0.22888 | 0.17395 | 0.1236 | 0.19684 | 0.14648 | -0.018311 | -122.6303 | -122.8867 | 0.29755 | 0.25635 | 0.1831 | 0.27466 | 0.20142 | 0.25177 | 0.11902 | 0.31586 | 0.16479 | 0.30212 | 0.42114 | 0.27923 | 0.40283 | -123.056 | -123.0515 | 0.09613 | 0.14648 | 0.12817 | 0.17853
5016.1719 | 122.9507 | -0.28381 | 122.7997 | -0.075836 | -0.00087374 | 0.015242 | 0.0073081 | -0.0024032 | -0.00079891 | -0.00055961 | 0.001709 | 0.00067495 | 0.014954 | 0.005614 | 0.017934 | -0.0051527 | -0.0027515 | -0.16022 | 0.004578 | -0.3067 | -0.23346 | -0.12817 | -0.22888 | -0.16479 | -0.1831 | 0.13275 | -0.33875 | -0.20599 | -0.054932 | -0.19684 | -0.09613 | -0.022889 | -122.7951 | -123.0331 | 0.15564 | 0.11902 | 0.054931 | 0.14191 | 0.07782 | -0.054932 | -122.6669 | -123.0057 | 0.22888 | 0.18768 | 0.086975 | 0.24262 | 0.14191 | 0.17853 | 0.073243 | 0.28381 | 0.13275 | 0.31128 | 0.4715 | 0.28839 | 0.41656 | -123.1064 | -123.1384 | 0.050354 | 0.077819 | 0.1236 | 0.10071
5017.1719 | 122.9691 | -0.29755 | 122.7768 | -0.037689 | -0.00066014 | 0.013747 | 0.0060263 | -0.0021896 | -0.00037171 | -0.00013241 | -0.019653 | 0.0036657 | 0.019226 | 0.0043322 | 0.017293 | -0.0079297 | 0.00088014 | -0.23346 | 0.036621 | -0.33875 | -0.27924 | -0.17395 | -0.25635 | -0.19226 | -0.2243 | 0.16022 | -0.33875 | -0.21973 | -0.082397 | -0.21515 | -0.10529 | -0.041199 | -122.7402 | -123.056 | 0.1236 | 0.10528 | 0.041198 | 0.14648 | 0.082397 | -0.041199 | -122.6166 | -122.9965 | 0.21515 | 0.19226 | 0.082397 | 0.23346 | 0.1236 | 0.1648 | 0.059509 | 0.25635 | 0.11902 | 0.37537 | 0.49896 | 0.33417 | 0.45776 | -123.1155 | -123.1155 | 0.01831 | 0.077819 | 0.064087 | 0.073242
5018.1719 | 122.9782 | -0.28381 | 122.7539 | -0.091095 | -0.00066014 | 0.013106 | 0.0066671 | 0.00016017 | -0.00058531 | -0.0065412 | 0.032227 | 0.0017431 | 0.018585 | 0.0064684 | 0.019643 | -0.0068615 | -0.0036059 | -0.16479 | 0.004578 | -0.29297 | -0.21973 | -0.10071 | -0.1831 | -0.13733 | -0.15106 | 0.13275 | -0.32501 | -0.20142 | -0.054932 | -0.19226 | -0.09613 | -0.009156 | -122.7493 | -122.9736 | 0.1831 | 0.14648 | 0.10071 | 0.15564 | 0.10986 | -0.041199 | -122.6212 | -122.9553 | 0.22888 | 0.18768 | 0.091552 | 0.22888 | 0.13275 | 0.19226 | 0.073242 | 0.27008 | 0.1236 | 0.29755 | 0.45776 | 0.28839 | 0.41656 | -123.0469 | -123.0789 | 0.064086 | 0.082397 | 0.11902 | 0.13275
5019.1719 | 122.9645 | -0.27924 | 122.7402 | -0.068207 | -0.00044654 | 0.015028 | 0.0070943 | -0.0021896 | -0.00058531 | 0.00050839 | 0.010864 | 0.00088875 | 0.017517 | 0.003905 | 0.018147 | -0.0062207 | -0.0018971 | -0.15564 | 0 | -0.3067 | -0.1831 | -0.07782 | -0.15564 | -0.11444 | -0.13275 | 0.12817 | -0.30212 | -0.16022 | -0.022888 | -0.16022 | -0.064087 | -0.027466 | -122.7402 | -122.9233 | 0.20142 | 0.16479 | 0.1236 | 0.19226 | 0.15106 | -0.022888 | -122.612 | -122.9004 | 0.25635 | 0.21515 | 0.11902 | 0.23804 | 0.14191 | 0.22888 | 0.1236 | 0.27924 | 0.14191 | 0.3067 | 0.4303 | 0.27924 | 0.40741 | -123.0469 | -123.0423 | 0.096131 | 0.11902 | 0.1236 | 0.14648
5020.1719 | 123.024 | -0.26093 | 122.7768 | -0.10635 | 0.00040806 | 0.01396 | 0.0083761 | 0.00058737 | -0.0014399 | -0.0014142 | 0.032227 | 0.0032385 | 0.016235 | 0.00048702 | 0.016865 | -0.0057935 | -0.00040166 | -0.15106 | -0.022888 | -0.29297 | -0.1831 | -0.064087 | -0.16937 | -0.10529 | -0.1236 | 0.12817 | -0.3067 | -0.16937 | -0.013733 | -0.13733 | -0.054932 | -0.032044 | -122.7997 | -122.9599 | 0.19684 | 0.15564 | 0.091552 | 0.18768 | 0.1236 | -0.045777 | -122.6486 | -122.9462 | 0.24719 | 0.20599 | 0.1236 | 0.25177 | 0.16937 | 0.22888 | 0.10986 | 0.29297 | 0.13733 | 0.27008 | 0.43488 | 0.23804 | 0.3891 | -123.0698 | -123.0835 | 0.07782 | 0.091552 | 0.10986 | 0.13733
5021.1719 | 123.024 | -0.27466 | 122.7585 | -0.11398 | -1.9142e-05 | 0.014174 | 0.0068807 | 0.0022964 | -0.00058531 | -0.0018414 | 0.023071 | 3.4148e-05 | 0.020721 | -0.00079478 | 0.019856 | -0.0072889 | -0.0031787 | -0.16022 | 0.013733 | -0.29755 | -0.16479 | -0.068665 | -0.16479 | -0.11444 | -0.11444 | 0.1236 | -0.32044 | -0.13275 | -0.013733 | -0.13733 | -0.032043 | -0.022888 | -122.7448 | -122.9233 | 0.20599 | 0.16022 | 0.10986 | 0.1831 | 0.13275 | -0.045777 | -122.6349 | -122.8912 | 0.26093 | 0.24262 | 0.13733 | 0.28839 | 0.18311 | 0.22888 | 0.13275 | 0.3067 | 0.18768 | 0.31128 | 0.44403 | 0.28839 | 0.39825 | -123.056 | -123.0789 | 0.10986 | 0.14191 | 0.11444 | 0.16022
5022.1719 | 123.0652 | -0.25635 | 122.7676 | -0.075836 | 0.0025443 | 0.018019 | 0.0092307 | 0.0052872 | 5.5488e-05 | -0.00098701 | 0.032227 | 0.0032385 | 0.016663 | 0.0041186 | 0.017079 | -0.0079297 | 2.554e-05 | -0.15106 | -0.013733 | -0.27008 | -0.1831 | -0.054932 | -0.15564 | -0.10986 | -0.10071 | 0.13275 | -0.31586 | -0.12817 | -0.004578 | -0.1236 | -0.050354 | -0.013733 | -122.7814 | -122.9507 | 0.20142 | 0.14649 | 0.10071 | 0.16022 | 0.11444 | -0.059509 | -122.6349 | -122.8958 | 0.25177 | 0.20599 | 0.13275 | 0.2655 | 0.19226 | 0.21515 | 0.086976 | 0.31128 | 0.18768 | 0.25635 | 0.44861 | 0.24262 | 0.3891 | -123.0377 | -123.0835 | 0.073243 | 0.12817 | 0.10529 | 0.15564
5023.1719 | 122.9874 | -0.29297 | 122.7997 | -0.11398 | -0.0021555 | 0.014601 | 0.0088033 | 0.0012284 | -0.0016535 | -0.0014142 | -0.0043946 | 0.0036657 | 0.016235 | 0.0058276 | 0.019429 | -0.0062207 | -0.00018806 | -0.19226 | 0.027466 | -0.31586 | -0.24719 | -0.14648 | -0.2243 | -0.17395 | -0.20142 | 0.13275 | -0.33417 | -0.21057 | -0.07782 | -0.20142 | -0.11444 | -0.022888 | -122.7722 | -123.0469 | 0.14648 | 0.11902 | 0.068665 | 0.14191 | 0.091553 | -0.041198 | -122.6669 | -123.0103 | 0.21515 | 0.17853 | 0.091553 | 0.21973 | 0.13275 | 0.16937 | 0.068665 | 0.25635 | 0.1236 | 0.34332 | 0.46692 | 0.32043 | 0.42572 | -123.1155 | -123.1338 | 0.045777 | 0.082398 | 0.10071 | 0.091553
5024.1719 | 122.9736 | -0.28839 | 122.7814 | -0.083466 | -0.0013009 | 0.016524 | 0.0092307 | 0.0012284 | -0.00058531 | -0.00013241 | -0.019653 | 0.0019567 | 0.016022 | 0.002196 | 0.019643 | -0.0055799 | -0.00040166 | -0.18768 | 0.013733 | -0.31586 | -0.24261 | -0.14191 | -0.25635 | -0.17395 | -0.19684 | 0.16022 | -0.31586 | -0.20599 | -0.073242 | -0.19226 | -0.10529 | -0.027466 | -122.7676 | -123.024 | 0.14648 | 0.11444 | 0.032043 | 0.14191 | 0.059509 | -0.027466 | -122.6212 | -122.9874 | 0.21515 | 0.18311 | 0.09613 | 0.21057 | 0.1236 | 0.17395 | 0.073242 | 0.24261 | 0.10986 | 0.32959 | 0.47607 | 0.30212 | 0.44861 | -123.0972 | -123.0972 | 0.045776 | 0.082397 | 0.10071 | 0.091553
5025.1719 | 123.0057 | -0.28839 | 122.7631 | -0.03006 | -0.00023294 | 0.014387 | 0.0094443 | 0.003151 | -0.0022943 | -0.0031232 | 0.013916 | -0.00017945 | 0.016449 | 0.0019824 | 0.016652 | -0.0096387 | -0.0025379 | -0.18768 | 0.004578 | -0.33417 | -0.25635 | -0.13733 | -0.23346 | -0.19226 | -0.20599 | 0.13733 | -0.32501 | -0.21057 | -0.082397 | -0.19226 | -0.10529 | -0.045776 | -122.7585 | -123.0194 | 0.15106 | 0.09613 | 0.054932 | 0.14191 | 0.10071 | -0.036621 | -122.6257 | -122.9736 | 0.20599 | 0.18311 | 0.09613 | 0.21973 | 0.13275 | 0.19684 | 0.077819 | 0.24262 | 0.11444 | 0.33875 | 0.46234 | 0.29297 | 0.42572 | -123.0972 | -123.0881 | 0.032043 | 0.07782 | 0.10071 | 0.082397
5026.1719 | 122.9919 | -0.29297 | 122.7722 | -0.075836 | -0.0010873 | 0.01396 | 0.0068807 | -0.00048063 | -0.0012261 | -0.0029096 | -0.0074462 | 0.0036657 | 0.016449 | -0.00036738 | 0.018788 | -0.0070753 | 0.0017345 | -0.17395 | 0.018311 | -0.31128 | -0.24719 | -0.14191 | -0.24261 | -0.16937 | -0.18768 | 0.13275 | -0.30212 | -0.20142 | -0.073242 | -0.21515 | -0.082397 | -0.01831 | -122.7539 | -123.0194 | 0.15106 | 0.1236 | 0.050354 | 0.14191 | 0.068664 | -0.009155 | -122.6395 | -122.9736 | 0.21973 | 0.21057 | 0.07782 | 0.21973 | 0.086975 | 0.16937 | 0.064087 | 0.22888 | 0.10071 | 0.32959 | 0.43488 | 0.31128 | 0.42572 | -123.0835 | -123.0743 | 0.045777 | 0.091553 | 0.11902 | 0.10529
5027.1719 | 122.9782 | -0.29297 | 122.7905 | 0.015716 | 0.0010489 | 0.015242 | 0.0058127 | -0.0015488 | -0.00037171 | -0.0024822 | -0.016602 | 0.0043065 | 0.019653 | 0.013091 | 0.018361 | -0.0096387 | 0.0028027 | -0.23346 | 0.018311 | -0.33875 | -0.28381 | -0.17395 | -0.27466 | -0.19226 | -0.2243 | 0.12817 | -0.32959 | -0.21973 | -0.086975 | -0.20599 | -0.10529 | -0.045776 | -122.7722 | -123.0743 | 0.11902 | 0.10071 | 0.018311 | 0.14648 | 0.064087 | -0.036621 | -122.6624 | -123.0103 | 0.20599 | 0.18768 | 0.086975 | 0.2243 | 0.1236 | 0.1648 | 0.054932 | 0.24261 | 0.10986 | 0.35706 | 0.45776 | 0.31128 | 0.42114 | -123.1293 | -123.1201 | 0.009156 | 0.073242 | 0.05951 | 0.068665
5028.2344 | 122.9645 | -0.29297 | 122.8226 | -0.052948 | -0.0019417 | 0.014601 | 0.0083761 | 0.0061416 | -0.0025079 | 0.00072199 | -0.022705 | 0.0040929 | 0.016663 | 0.0034778 | 0.018788 | -0.0062207 | 0.0013073 | -0.23346 | 0.013733 | -0.32959 | -0.27924 | -0.20142 | -0.27008 | -0.1831 | -0.2243 | 0.12817 | -0.32959 | -0.21057 | -0.086975 | -0.21515 | -0.09613 | -0.036621 | -122.8088 | -123.1018 | 0.091553 | 0.10986 | 0.022888 | 0.14649 | 0.059509 | -0.036621 | -122.6944 | -123.0331 | 0.20599 | 0.19684 | 0.07782 | 0.23346 | 0.11444 | 0.12817 | 0.050354 | 0.24261 | 0.11902 | 0.34332 | 0.45776 | 0.3067 | 0.42114 | -123.1522 | -123.1522 | 0.013733 | 0.082398 | 0.05951 | 0.068665
5029.1719 | 122.9828 | -0.29297 | 122.7905 | -0.098725 | -0.0013009 | 0.012465 | 0.0085897 | -5.343e-05 | 0.0011237 | 0.0011494 | -0.0074462 | 0.0021703 | 0.017517 | 0.0096728 | 0.016865 | -0.0075025 | 0.0017345 | -0.24261 | 0.027466 | -0.32959 | -0.28381 | -0.18768 | -0.27924 | -0.18768 | -0.22888 | 0.12817 | -0.34332 | -0.21973 | -0.09613 | -0.2243 | -0.10529 | -0.036621 | -122.7631 | -123.0743 | 0.10529 | 0.10529 | 0.013733 | 0.14191 | 0.050354 | -0.050354 | -122.6624 | -123.0103 | 0.19684 | 0.18768 | 0.068665 | 0.23804 | 0.11902 | 0.14191 | 0.045777 | 0.24719 | 0.1236 | 0.35706 | 0.4715 | 0.32043 | 0.42114 | -123.1201 | -123.1338 | 0.009156 | 0.073242 | 0.050354 | 0.064087
5030.1719 | 122.9782 | -0.30212 | 122.7859 | 0.038605 | -0.0017281 | 0.012465 | 0.0073081 | 0.00251 | -0.0025079 | -0.00055961 | -0.0074462 | 0.0030249 | 0.018158 | 0.0024096 | 0.019002 | -0.0092115 | -0.0031787 | -0.23346 | 0.027466 | -0.34332 | -0.27924 | -0.1831 | -0.26093 | -0.1831 | -0.23804 | 0.13733 | -0.33875 | -0.23346 | -0.09613 | -0.21515 | -0.11444 | -0.041199 | -122.7585 | -123.0652 | 0.11902 | 0.11902 | 0.041199 | 0.16022 | 0.082398 | -0.036621 | -122.6486 | -123.0194 | 0.20599 | 0.18768 | 0.086975 | 0.2243 | 0.1236 | 0.16022 | 0.064087 | 0.24262 | 0.10529 | 0.37079 | 0.47607 | 0.32959 | 0.43945 | -123.1293 | -123.1247 | 0.022888 | 0.068665 | 0.068665 | 0.064087
5031.1719 | 122.9645 | -0.30212 | 122.7768 | -0.060578 | -0.0027963 | 0.015028 | 0.0081625 | 0.0027238 | 0.00048269 | -0.00098701 | 0.013916 | 0.00067495 | 0.019226 | 0.0049732 | 0.018361 | -0.0075025 | -0.00040166 | -0.25177 | 0.022888 | -0.33875 | -0.29755 | -0.19684 | -0.2655 | -0.20142 | -0.23804 | 0.11902 | -0.34332 | -0.22888 | -0.07782 | -0.21973 | -0.09613 | -0.036621 | -122.7539 | -123.0743 | 0.10529 | 0.10071 | 0.036621 | 0.13733 | 0.073242 | -0.041199 | -122.6578 | -123.0057 | 0.2243 | 0.20599 | 0.082397 | 0.24719 | 0.1236 | 0.14191 | 0.041199 | 0.2655 | 0.11444 | 0.36163 | 0.46234 | 0.32501 | 0.42114 | -123.1155 | -123.1201 | 0.004578 | 0.073242 | 0.050354 | 0.064087
5032.1719 | 122.9736 | -0.29755 | 122.7676 | -0.11398 | -0.00087374 | 0.016524 | 0.0081625 | -0.0056076 | 0.00091009 | -0.002055 | -0.0013428 | 0.0049475 | 0.016663 | 0.0030506 | 0.019002 | -0.0075025 | -0.0023243 | -0.24261 | 0.022888 | -0.32501 | -0.29297 | -0.1831 | -0.26093 | -0.20599 | -0.22888 | 0.13275 | -0.33875 | -0.21515 | -0.082397 | -0.21515 | -0.10986 | -0.027466 | -122.7448 | -123.0606 | 0.11444 | 0.091552 | 0.036621 | 0.11902 | 0.064087 | -0.041199 | -122.6349 | -122.9828 | 0.21515 | 0.18768 | 0.082397 | 0.22888 | 0.1236 | 0.14191 | 0.032043 | 0.25635 | 0.1236 | 0.3479 | 0.4715 | 0.32043 | 0.4303 | -123.0927 | -123.1064 | 0.004577 | 0.082397 | 0.054931 | 0.068664
5033.1719 | 122.9782 | -0.29297 | 122.7951 | -0.052948 | -0.00023294 | 0.015456 | 0.0090169 | -0.001976 | -0.00079891 | 0.00093559 | -0.01355 | 0.0034521 | 0.018158 | 0.005614 | 0.018147 | -0.0075025 | 0.00045294 | -0.23346 | 0.022888 | -0.35706 | -0.28839 | -0.17853 | -0.25635 | -0.19684 | -0.22888 | 0.13733 | -0.34332 | -0.20142 | -0.07782 | -0.20599 | -0.10071 | -0.064087 | -122.7722 | -123.0835 | 0.11444 | 0.096131 | 0.036621 | 0.16022 | 0.10071 | -0.050354 | -122.6578 | -122.9965 | 0.21515 | 0.19226 | 0.086975 | 0.24261 | 0.13733 | 0.17853 | 0.068665 | 0.2655 | 0.14191 | 0.37994 | 0.48065 | 0.31586 | 0.4303 | -123.1522 | -123.1384 | 0.004578 | 0.091553 | 0.05951 | 0.064087
5034.1719 | 122.9553 | -0.3067 | 122.7814 | -0.083466 | -0.0023691 | 0.014174 | 0.0081625 | -0.00048063 | 0.0011237 | 0.00093559 | -0.0043946 | 0.0047339 | 0.017517 | 0.005614 | 0.017079 | -0.0068615 | -0.00040166 | -0.22888 | 0.022888 | -0.33417 | -0.3067 | -0.18768 | -0.26093 | -0.19226 | -0.22888 | 0.11902 | -0.34332 | -0.23804 | -0.10071 | -0.21057 | -0.10529 | -0.027465 | -122.7585 | -123.0881 | 0.11902 | 0.11444 | 0.045777 | 0.14191 | 0.073242 | -0.036621 | -122.6624 | -123.0194 | 0.20599 | 0.20142 | 0.096131 | 0.23804 | 0.13275 | 0.14648 | 0.027465 | 0.24261 | 0.10529 | 0.35706 | 0.46234 | 0.32959 | 0.42572 | -123.1155 | -123.1247 | 0 | 0.068665 | 0.07782 | 0.07782
5035.1719 | 123.0103 | -0.27924 | 122.7859 | -0.060578 | -0.00087374 | 0.016951 | 0.0088033 | -5.343e-05 | -0.0020807 | -0.002696 | 0.026123 | 0.0015295 | 0.018585 | 0.0019824 | 0.019002 | -0.0079297 | 0.00066654 | -0.16479 | -0.004578 | -0.32501 | -0.21973 | -0.10529 | -0.1831 | -0.1236 | -0.15564 | 0.11444 | -0.31128 | -0.17853 | -0.059509 | -0.17853 | -0.073242 | -0.045776 | -122.7905 | -123.0057 | 0.17395 | 0.15564 | 0.096131 | 0.20142 | 0.14191 | -0.032043 | -122.6715 | -122.9645 | 0.21973 | 0.20599 | 0.10071 | 0.23804 | 0.13275 | 0.21973 | 0.10529 | 0.25177 | 0.13275 | 0.32043 | 0.42572 | 0.27466 | 0.39368 | -123.111 | -123.0972 | 0.059509 | 0.10071 | 0.11444 | 0.1236
5036.1719 | 122.9782 | -0.29755 | 122.7768 | -0.03006 | -0.00066014 | 0.015669 | 0.0092307 | 0.00058737 | -0.0025079 | 0.0022174 | -0.03186 | 0.0015295 | 0.01709 | 0.0066822 | 0.017934 | -0.0075025 | -0.0025379 | -0.22888 | 0.032043 | -0.33417 | -0.2655 | -0.16022 | -0.2243 | -0.17853 | -0.1831 | 0.1236 | -0.32501 | -0.16937 | -0.068665 | -0.1831 | -0.059509 | -0.036621 | -122.7448 | -123.0423 | 0.13733 | 0.11902 | 0.073242 | 0.15564 | 0.10986 | -0.027466 | -122.6532 | -122.9462 | 0.22888 | 0.23804 | 0.11444 | 0.2655 | 0.14191 | 0.17395 | 0.068664 | 0.25635 | 0.15564 | 0.36621 | 0.44861 | 0.32959 | 0.42114 | -123.111 | -123.1018 | 0.032043 | 0.12817 | 0.068664 | 0.11444
5037.1719 | 122.9782 | -0.32044 | 122.7585 | -0.03006 | 0.0012625 | 0.014815 | 0.0079489 | -0.00048063 | -0.0012261 | 0.00093559 | -0.0013428 | 0.0019567 | 0.014954 | 0.0075366 | 0.014729 | -0.0066479 | -0.00040166 | -0.24719 | 0.032043 | -0.34332 | -0.3067 | -0.20599 | -0.2655 | -0.21973 | -0.24719 | 0.13733 | -0.33417 | -0.20599 | -0.07782 | -0.20599 | -0.10071 | -0.022888 | -122.7264 | -123.0652 | 0.11444 | 0.10071 | 0.054932 | 0.1236 | 0.07782 | -0.013732 | -122.6212 | -122.9645 | 0.24262 | 0.21973 | 0.11444 | 0.23346 | 0.12817 | 0.13733 | 0.036621 | 0.25635 | 0.12817 | 0.37537 | 0.4715 | 0.35248 | 0.45776 | -123.1018 | -123.0927 | 0.013733 | 0.11444 | 0.073243 | 0.073243
5038.1719 | 122.9507 | -0.30212 | 122.7722 | -0.068207 | -0.0017281 | 0.01396 | 0.0092307 | 0.00016017 | 0.00069649 | -0.002055 | -0.019653 | 0.0025975 | 0.01709 | 0.0036914 | 0.017293 | -0.0051527 | -0.00018806 | -0.24261 | 0.022888 | -0.3479 | -0.30212 | -0.19684 | -0.26093 | -0.21057 | -0.23346 | 0.15106 | -0.34332 | -0.20599 | -0.082397 | -0.21057 | -0.10071 | -0.045776 | -122.7493 | -123.0743 | 0.10529 | 0.091553 | 0.041199 | 0.13733 | 0.086975 | -0.041199 | -122.6212 | -122.9782 | 0.21973 | 0.20142 | 0.091553 | 0.24261 | 0.13275 | 0.15106 | 0.045776 | 0.26093 | 0.13733 | 0.37079 | 0.49438 | 0.32501 | 0.45319 | -123.1201 | -123.1155 | 0 | 0.09613 | 0.059509 | 0.068665
5039.1719 | 122.9919 | -0.30212 | 122.7951 | -0.037689 | -0.0013009 | 0.014174 | 0.0092307 | -0.003685 | -0.0014399 | -0.00055961 | -0.0074462 | 0.0021703 | 0.019653 | 0.0077502 | 0.019002 | -0.0077161 | 0.0021619 | -0.23346 | 0.018311 | -0.33417 | -0.3067 | -0.19226 | -0.26093 | -0.19226 | -0.2243 | 0.13733 | -0.32501 | -0.21057 | -0.091553 | -0.21515 | -0.091553 | -0.032043 | -122.7768 | -123.1018 | 0.10986 | 0.10986 | 0.041199 | 0.14191 | 0.073242 | -0.022888 | -122.6578 | -123.0057 | 0.21057 | 0.21057 | 0.086975 | 0.23346 | 0.10986 | 0.14191 | 0.027465 | 0.23346 | 0.11444 | 0.35248 | 0.46234 | 0.32044 | 0.43945 | -123.1293 | -123.1201 | -0.004578 | 0.091553 | 0.068665 | 0.07782
5040.1719 | 123.0103 | -0.29297 | 122.7814 | 0.008087 | -0.0015145 | 0.016524 | 0.010726 | 0.0029374 | -0.0012261 | 0.00029479 | 0.001709 | 0.0030249 | 0.016663 | 0.0026232 | 0.017934 | -0.0070753 | 0.0025891 | -0.23346 | 0.022888 | -0.35248 | -0.28839 | -0.20142 | -0.26093 | -0.21057 | -0.21515 | 0.12817 | -0.32959 | -0.21515 | -0.068665 | -0.18768 | -0.082397 | -0.059509 | -122.7585 | -123.0698 | 0.091553 | 0.082398 | 0.032044 | 0.14191 | 0.091553 | -0.036621 | -122.6532 | -122.9965 | 0.2243 | 0.21057 | 0.10529 | 0.24719 | 0.14191 | 0.15106 | 0.064087 | 0.26092 | 0.11444 | 0.37537 | 0.45776 | 0.31586 | 0.42114 | -123.1339 | -123.111 | 0.004578 | 0.07782 | 0.05951 | 0.07782
5041.1719 | 123.0057 | -0.29297 | 122.7768 | 0.030975 | -0.0015145 | 0.01631 | 0.010085 | 0.0029374 | -0.0016535 | -0.0016278 | -0.010498 | 0.0028113 | 0.016663 | 0.003905 | 0.018361 | -0.0066479 | -0.0053149 | -0.23346 | 0.009155 | -0.33875 | -0.28381 | -0.19226 | -0.2655 | -0.21057 | -0.23346 | 0.14648 | -0.33417 | -0.2243 | -0.082397 | -0.21057 | -0.10071 | -0.045776 | -122.7676 | -123.0606 | 0.10071 | 0.082398 | 0.027466 | 0.12817 | 0.073242 | -0.041198 | -122.6303 | -123.0011 | 0.21057 | 0.19226 | 0.082398 | 0.23346 | 0.1236 | 0.14648 | 0.054932 | 0.25177 | 0.10986 | 0.3479 | 0.48065 | 0.30212 | 0.43945 | -123.1155 | -123.111 | 0.009156 | 0.068665 | 0.05951 | 0.05951
5042.1719 | 122.9965 | -0.31586 | 122.7814 | -0.060578 | -0.00087374 | 0.013106 | 0.0092307 | -0.00090783 | -0.00079891 | -0.00055961 | 0.010864 | 0.0038793 | 0.020508 | -0.0031446 | 0.018574 | -0.0081433 | -0.0018971 | -0.25635 | 0.027466 | -0.3479 | -0.28381 | -0.19226 | -0.25635 | -0.20142 | -0.2243 | 0.13275 | -0.3479 | -0.22888 | -0.091553 | -0.20599 | -0.10986 | -0.032043 | -122.7539 | -123.0652 | 0.1236 | 0.11444 | 0.059509 | 0.14648 | 0.091552 | -0.032043 | -122.6486 | -123.0103 | 0.2243 | 0.20599 | 0.10986 | 0.23804 | 0.14191 | 0.15564 | 0.064087 | 0.25635 | 0.11902 | 0.37537 | 0.48065 | 0.34332 | 0.44861 | -123.1293 | -123.1293 | 0.032044 | 0.086975 | 0.059509 | 0.091553
5043.2344 | 123.0423 | -0.28381 | 122.7631 | -0.045319 | 0.0012625 | 0.01631 | 0.010085 | 0.0033646 | -0.0010125 | 0.0060626 | -0.044067 | 0.0023839 | 0.017517 | -0.001222 | 0.017293 | -0.0072889 | 0.0013073 | -0.20142 | 0.018311 | -0.33417 | -0.23804 | -0.12817 | -0.24261 | -0.18768 | -0.15564 | 0.1236 | -0.32044 | -0.16937 | -0.045776 | -0.19226 | -0.07782 | -0.050354 | -122.7448 | -123.0011 | 0.15564 | 0.09613 | 0.041198 | 0.14648 | 0.091552 | -0.036622 | -122.6395 | -122.9324 | 0.23804 | 0.20599 | 0.091552 | 0.24262 | 0.12817 | 0.20599 | 0.09613 | 0.27466 | 0.15106 | 0.35248 | 0.44403 | 0.30212 | 0.40741 | -123.0972 | -123.0835 | 0.045776 | 0.11444 | 0.082397 | 0.12817
5044.1719 | 123.0286 | -0.27924 | 122.7676 | -0.037689 | -0.00087374 | 0.015456 | 0.0079489 | -0.00069423 | -0.0010125 | -0.00034601 | -0.01355 | 0.0013159 | 0.017944 | 0.0045458 | 0.018147 | -0.0068615 | 2.554e-05 | -0.23804 | 0.018311 | -0.35706 | -0.30212 | -0.20599 | -0.26093 | -0.21057 | -0.22888 | 0.13733 | -0.34332 | -0.19226 | -0.059509 | -0.21515 | -0.068665 | -0.07782 | -122.7493 | -123.0698 | 0.073242 | 0.068665 | 0.018311 | 0.14648 | 0.096131 | -0.064087 | -122.6303 | -122.9599 | 0.21973 | 0.21057 | 0.064087 | 0.27466 | 0.12817 | 0.15106 | 0.054932 | 0.28381 | 0.15106 | 0.37537 | 0.48065 | 0.29755 | 0.41656 | -123.1247 | -123.111 | -0.022888 | 0.086975 | 0.041199 | 0.050354
5045.1719 | 123.0057 | -0.34332 | 122.7448 | -0.022431 | -0.00066014 | 0.017592 | 0.0092307 | 0.004219 | -0.0027215 | 0.00050839 | 0.0078126 | 0.0038793 | 0.018585 | 0.001128 | 0.019215 | -0.0077161 | -0.0031787 | -0.27924 | -0.004578 | -0.36621 | -0.31586 | -0.21973 | -0.29297 | -0.22888 | -0.2655 | 0.09613 | -0.37537 | -0.27924 | -0.13733 | -0.24261 | -0.15106 | -0.022888 | -122.7493 | -123.0606 | 0.1236 | 0.11444 | 0.050354 | 0.13733 | 0.073242 | -0.032043 | -122.6486 | -123.024 | 0.20599 | 0.19226 | 0.10071 | 0.2243 | 0.13275 | 0.14648 | 0.050354 | 0.23804 | 0.09613 | 0.36163 | 0.4715 | 0.33874 | 0.43945 | -123.111 | -123.1201 | 0.027466 | 0.064087 | 0.064087 | 0.07782
5046.1719 | 122.9919 | -0.32959 | 122.7631 | -0.098725 | 0.0012625 | 0.015669 | 0.0066671 | -0.0026168 | -0.00058531 | -0.0029096 | 0.023071 | 0.0043065 | 0.016876 | -0.00058098 | 0.019429 | -0.0066479 | 0.00088014 | -0.28839 | -0.004578 | -0.37079 | -0.32501 | -0.21515 | -0.29755 | -0.22888 | -0.25635 | 0.07782 | -0.37994 | -0.27924 | -0.13733 | -0.24261 | -0.14648 | -0.041199 | -122.7676 | -123.0881 | 0.11444 | 0.10071 | 0.032044 | 0.14191 | 0.073243 | -0.050354 | -122.6852 | -123.0423 | 0.19226 | 0.18311 | 0.086975 | 0.23346 | 0.13733 | 0.15564 | 0.045777 | 0.24261 | 0.10071 | 0.36621 | 0.45776 | 0.32501 | 0.40741 | -123.1339 | -123.143 | 0.004578 | 0.050354 | 0.041199 | 0.073242
5047.1719 | 123.0057 | -0.32501 | 122.7493 | -0.052948 | -0.0013009 | 0.015456 | 0.0096579 | 0.00037377 | -0.00015811 | -0.0016278 | -0.0074462 | 0.0047339 | 0.01709 | 0.0088184 | 0.018574 | -0.0064343 | -0.0031787 | -0.28839 | 0.009155 | -0.37994 | -0.33417 | -0.23804 | -0.30212 | -0.23346 | -0.27924 | 0.091553 | -0.37994 | -0.26093 | -0.14191 | -0.24261 | -0.13733 | -0.054932 | -122.7402 | -123.0835 | 0.086975 | 0.091553 | 0.022888 | 0.14649 | 0.07782 | -0.054932 | -122.6578 | -123.0103 | 0.18311 | 0.18768 | 0.082397 | 0.24261 | 0.13733 | 0.14191 | 0.045777 | 0.23804 | 0.11902 | 0.3891 | 0.4715 | 0.33417 | 0.41657 | -123.1293 | -123.1293 | -0.009155 | 0.064087 | 0.036621 | 0.045776
5048.1719 | 122.9599 | -0.3479 | 122.7539 | -0.03006 | -1.9142e-05 | 0.016096 | 0.0094443 | 0.001442 | -0.00037171 | 8.1188e-05 | 0.0078126 | 0.0040929 | 0.012817 | 0.0088184 | 0.019856 | -0.0081433 | -0.0025379 | -0.27008 | -0.022888 | -0.35706 | -0.31586 | -0.20599 | -0.28381 | -0.2243 | -0.25177 | 0.09613 | -0.37079 | -0.27924 | -0.11902 | -0.23804 | -0.14648 | -0.009156 | -122.7768 | -123.0698 | 0.14191 | 0.1236 | 0.064087 | 0.13275 | 0.073243 | -0.022889 | -122.6578 | -123.0331 | 0.22888 | 0.20142 | 0.10986 | 0.2243 | 0.13275 | 0.15106 | 0.041199 | 0.25177 | 0.091553 | 0.33417 | 0.46692 | 0.32501 | 0.44403 | -123.111 | -123.1247 | 0.032043 | 0.068664 | 0.077819 | 0.09613
5049.1719 | 123.0515 | -0.30212 | 122.7631 | -0.12924 | 0.00040806 | 0.018446 | 0.0075217 | -5.343e-05 | 5.5488e-05 | -0.0012006 | 0.041382 | -0.00060665 | 0.014099 | 0.0024096 | 0.01772 | -0.0081433 | -0.0014697 | -0.21515 | -0.064087 | -0.33417 | -0.21973 | -0.10071 | -0.21057 | -0.14191 | -0.15564 | 0.050354 | -0.34332 | -0.18768 | -0.045776 | -0.16022 | -0.07782 | -0.032043 | -122.8271 | -122.9828 | 0.20142 | 0.16022 | 0.091553 | 0.19226 | 0.1236 | -0.041199 | -122.7127 | -122.9507 | 0.25635 | 0.2243 | 0.14191 | 0.2655 | 0.18311 | 0.23346 | 0.11444 | 0.29755 | 0.15564 | 0.27008 | 0.39368 | 0.23804 | 0.35248 | -123.0972 | -123.1064 | 0.082397 | 0.11444 | 0.086975 | 0.14648
5050.2344 | 123.0515 | -0.32501 | 122.7585 | -0.083466 | -0.0019417 | 0.015883 | 0.0070943 | 0.001442 | -0.0022943 | 0.0017902 | -0.025757 | 0.0038793 | 0.017731 | 0.003905 | 0.017293 | -0.0072889 | -0.0033923 | -0.26093 | -0.018311 | -0.37079 | -0.32044 | -0.2243 | -0.28381 | -0.23346 | -0.23804 | 0.07782 | -0.35248 | -0.24261 | -0.091553 | -0.2243 | -0.10071 | -0.045777 | -122.7768 | -123.0789 | 0.10071 | 0.091553 | 0.041199 | 0.13733 | 0.086976 | -0.027466 | -122.6807 | -123.0011 | 0.23346 | 0.2243 | 0.10071 | 0.25177 | 0.12817 | 0.14648 | 0.050354 | 0.26093 | 0.10986 | 0.35248 | 0.4303 | 0.3067 | 0.40283 | -123.1293 | -123.111 | 0.004577 | 0.082397 | 0.064087 | 0.086975
5051.1719 | 122.9645 | -0.33417 | 122.7219 | -0.045319 | -0.00023294 | 0.017165 | 0.0085897 | 0.0022964 | -0.0014399 | -0.00034601 | -0.0043946 | 0.0021703 | 0.015808 | 0.00091422 | 0.019643 | -0.0066479 | -0.0057423 | -0.2655 | -0.018311 | -0.37537 | -0.32959 | -0.23346 | -0.3067 | -0.24261 | -0.27008 | 0.082397 | -0.35706 | -0.27466 | -0.12817 | -0.25635 | -0.15564 | -0.041199 | -122.7402 | -123.0515 | 0.10071 | 0.091552 | 0.027465 | 0.13275 | 0.068664 | -0.022889 | -122.6395 | -122.9965 | 0.20599 | 0.17853 | 0.077819 | 0.20142 | 0.10071 | 0.14191 | 0.045776 | 0.22888 | 0.082398 | 0.35705 | 0.43945 | 0.31586 | 0.41656 | -123.0972 | -123.0789 | 0.004577 | 0.059509 | 0.068664 | 0.064086
5052.1719 | 122.9736 | -0.3479 | 122.7631 | -0.0071715 | -0.00023294 | 0.015669 | 0.0090169 | 0.0018692 | 0.0013373 | -0.00034601 | -0.01355 | 0.0030249 | 0.013458 | 0.0071094 | 0.016865 | -0.0066479 | -0.0010425 | -0.2655 | -0.018311 | -0.3891 | -0.32044 | -0.2243 | -0.31128 | -0.22888 | -0.26093 | 0.091553 | -0.37079 | -0.2655 | -0.14191 | -0.25177 | -0.14191 | -0.041199 | -122.7814 | -123.0835 | 0.1236 | 0.11902 | 0.036621 | 0.16022 | 0.07782 | -0.022889 | -122.6715 | -123.0286 | 0.20599 | 0.20599 | 0.09613 | 0.22888 | 0.11902 | 0.16479 | 0.068664 | 0.22888 | 0.10529 | 0.37079 | 0.46234 | 0.32959 | 0.43945 | -123.1522 | -123.1339 | 0.027465 | 0.082397 | 0.082397 | 0.086975
5053.1719 | 122.9782 | -0.32959 | 122.7539 | 0.008087 | -0.0017281 | 0.016737 | 0.0085897 | -0.0021896 | -0.0016535 | -0.0016278 | -0.0043946 | 0.0015295 | 0.018799 | 0.0045458 | 0.016438 | -0.010707 | 0.0028027 | -0.2655 | -0.004578 | -0.37537 | -0.32959 | -0.23346 | -0.30212 | -0.23346 | -0.27924 | 0.082397 | -0.36163 | -0.25635 | -0.13275 | -0.25177 | -0.14648 | -0.045776 | -122.7585 | -123.0835 | 0.096131 | 0.096131 | 0.027466 | 0.14191 | 0.073242 | -0.032043 | -122.6715 | -123.0103 | 0.19684 | 0.18311 | 0.07782 | 0.21515 | 0.10986 | 0.14191 | 0.045776 | 0.22888 | 0.10528 | 0.37079 | 0.44403 | 0.32501 | 0.41199 | -123.1293 | -123.1155 | 0 | 0.073242 | 0.064087 | 0.050354
5054.1719 | 122.9736 | -0.33417 | 122.731 | -0.083466 | -0.00023294 | 0.018446 | 0.0066671 | 0.0022964 | -0.0012261 | 0.0011494 | 0.013916 | 0.0032385 | 0.01709 | 0.0062548 | 0.018788 | -0.0070753 | -0.0059559 | -0.24261 | -0.022888 | -0.35706 | -0.3067 | -0.19226 | -0.2655 | -0.21057 | -0.25177 | 0.10071 | -0.36163 | -0.27008 | -0.11444 | -0.24261 | -0.16022 | -0.022889 | -122.7539 | -123.0377 | 0.14191 | 0.1236 | 0.068664 | 0.14648 | 0.091553 | -0.027466 | -122.6303 | -123.0011 | 0.21973 | 0.17395 | 0.091552 | 0.20142 | 0.11902 | 0.16479 | 0.050354 | 0.24719 | 0.091552 | 0.33417 | 0.46234 | 0.31128 | 0.43488 | -123.0881 | -123.0927 | 0.027465 | 0.064086 | 0.091552 | 0.082397
5055.1719 | 122.9691 | -0.32959 | 122.7493 | -0.075836 | -0.00044654 | 0.015883 | 0.0060263 | 0.00080117 | -0.0010125 | -0.002696 | -0.0043946 | 0.00067495 | 0.016235 | 0.0045458 | 0.018361 | -0.0083569 | 0.0013073 | -0.21973 | -0.022888 | -0.35248 | -0.3067 | -0.15564 | -0.27008 | -0.19684 | -0.22888 | 0.10071 | -0.3479 | -0.24719 | -0.11444 | -0.24719 | -0.15106 | -0.022888 | -122.7722 | -123.056 | 0.17395 | 0.13275 | 0.059509 | 0.15564 | 0.082397 | -0.01831 | -122.6486 | -122.9965 | 0.21515 | 0.17853 | 0.082398 | 0.19684 | 0.10071 | 0.19684 | 0.045776 | 0.23346 | 0.10071 | 0.32959 | 0.44861 | 0.3067 | 0.4303 | -123.1018 | -123.0972 | 0.022888 | 0.082398 | 0.10986 | 0.10071
5056.1719 | 123.0927 | -0.27008 | 122.7127 | -0.068207 | -0.0013009 | 0.018446 | 0.0068807 | -0.003685 | 0.0026191 | 0.0022174 | 0.041382 | 0.0019567 | 0.015808 | 0.005614 | 0.017293 | -0.0070753 | -0.0048877 | -0.18768 | -0.036621 | -0.32959 | -0.21057 | -0.086975 | -0.1831 | -0.14648 | -0.1236 | 0.059509 | -0.32959 | -0.17395 | -0.022888 | -0.13275 | -0.064087 | -0.059509 | -122.7493 | -122.9233 | 0.18311 | 0.1236 | 0.086976 | 0.18311 | 0.14649 | -0.059509 | -122.6532 | -122.8867 | 0.24719 | 0.20599 | 0.13733 | 0.2655 | 0.19684 | 0.24261 | 0.11902 | 0.3067 | 0.15564 | 0.29297 | 0.3891 | 0.23346 | 0.32959 | -123.0423 | -123.0423 | 0.05951 | 0.096131 | 0.082398 | 0.14649
5057.1719 | 122.9828 | -0.3479 | 122.7585 | -0.03006 | -0.0013009 | 0.015456 | 0.0068807 | -0.00090783 | -0.0031489 | 0.0020038 | 0.02002 | 0.0011023 | 0.016449 | 0.0088184 | 0.017934 | -0.0081433 | -0.0055287 | -0.27008 | -0.013733 | -0.37079 | -0.32044 | -0.21057 | -0.29755 | -0.23346 | -0.2655 | 0.10529 | -0.36163 | -0.27008 | -0.12817 | -0.25635 | -0.15106 | -0.022889 | -122.7722 | -123.0789 | 0.13733 | 0.11444 | 0.050354 | 0.13733 | 0.073243 | -0.013733 | -122.6532 | -123.0286 | 0.21973 | 0.19684 | 0.091552 | 0.21057 | 0.10528 | 0.16022 | 0.050354 | 0.23346 | 0.091552 | 0.35706 | 0.46692 | 0.33417 | 0.45319 | -123.1293 | -123.1201 | 0.027465 | 0.077819 | 0.077819 | 0.082397
5058.1719 | 122.9782 | -0.3479 | 122.7631 | -0.052948 | -0.00044654 | 0.016524 | 0.0094443 | -0.0017624 | -0.0016535 | 0.0011494 | -0.0013428 | 0.0021703 | 0.01709 | 0.005614 | 0.016865 | -0.010066 | 0.00023934 | -0.26093 | -0.027466 | -0.37537 | -0.30212 | -0.20142 | -0.29297 | -0.23804 | -0.24261 | 0.10529 | -0.36163 | -0.25177 | -0.13275 | -0.25177 | -0.13733 | -0.027466 | -122.7905 | -123.0652 | 0.14648 | 0.10986 | 0.054931 | 0.13733 | 0.082397 | -0.013733 | -122.6578 | -123.0148 | 0.21515 | 0.21057 | 0.09613 | 0.2243 | 0.10986 | 0.17395 | 0.073242 | 0.22888 | 0.10986 | 0.3479 | 0.46692 | 0.32043 | 0.45319 | -123.1384 | -123.1247 | 0.045776 | 0.09613 | 0.086975 | 0.10528
5059.1719 | 123.0057 | -0.33417 | 122.7402 | -0.068207 | -0.00023294 | 0.016524 | 0.0088033 | 0.00080117 | -0.0012261 | -0.0033368 | 0.023071 | 0.0023839 | 0.018585 | 0.0032642 | 0.017293 | -0.010493 | -0.0027515 | -0.23804 | -0.013733 | -0.34332 | -0.30212 | -0.20142 | -0.27924 | -0.21515 | -0.24719 | 0.082397 | -0.36621 | -0.2655 | -0.11902 | -0.26093 | -0.16022 | -0.009156 | -122.7539 | -123.0423 | 0.13275 | 0.11902 | 0.054931 | 0.12817 | 0.064087 | -0.032044 | -122.6578 | -123.0057 | 0.21515 | 0.17395 | 0.073242 | 0.20599 | 0.10529 | 0.14191 | 0.041199 | 0.24719 | 0.10071 | 0.32959 | 0.44861 | 0.32043 | 0.41656 | -123.0835 | -123.1064 | 0.032043 | 0.068664 | 0.09613 | 0.086975
5060.1719 | 123.0103 | -0.32959 | 122.7676 | -0.083466 | -0.00044654 | 0.015883 | 0.0098715 | 0.001442 | -0.0010125 | -0.0016278 | 0.013916 | 0.00088875 | 0.014099 | 0.0013416 | 0.018788 | -0.0060071 | -0.0016833 | -0.21515 | -0.022888 | -0.33417 | -0.28381 | -0.16479 | -0.27008 | -0.21973 | -0.23346 | 0.09613 | -0.36621 | -0.25635 | -0.10986 | -0.25635 | -0.15106 | -0.004577 | -122.7905 | -123.0515 | 0.16479 | 0.10986 | 0.059509 | 0.11444 | 0.064086 | -0.036621 | -122.6715 | -123.024 | 0.21973 | 0.17853 | 0.073242 | 0.21515 | 0.10986 | 0.16937 | 0.050354 | 0.25635 | 0.10986 | 0.31128 | 0.46234 | 0.3067 | 0.42572 | -123.1018 | -123.1339 | 0.045777 | 0.073242 | 0.11444 | 0.096131
5061.1719 | 122.9828 | -0.32959 | 122.7448 | -0.03006 | 0.00019446 | 0.015669 | 0.0073081 | -0.00090783 | 0.00069649 | -0.0035504 | 0.032227 | 0.0030249 | 0.014954 | 0.003905 | 0.017934 | -0.0055799 | 0.0030163 | -0.21515 | -0.050354 | -0.33875 | -0.27466 | -0.14648 | -0.23804 | -0.1831 | -0.21515 | 0.082397 | -0.35248 | -0.24261 | -0.10529 | -0.23346 | -0.12817 | -0.009155 | -122.7951 | -123.0194 | 0.18311 | 0.14649 | 0.091553 | 0.15564 | 0.10071 | -0.022888 | -122.6624 | -122.9874 | 0.2243 | 0.20142 | 0.096131 | 0.2243 | 0.11902 | 0.19226 | 0.064087 | 0.24719 | 0.10986 | 0.28839 | 0.43488 | 0.27924 | 0.41199 | -123.0835 | -123.0972 | 0.054932 | 0.086975 | 0.11444 | 0.11444
5062.1719 | 123.0148 | -0.33875 | 122.7631 | -0.083466 | -0.0017281 | 0.017165 | 0.0094443 | 0.003151 | 0.0021917 | 0.00029479 | -0.028809 | 0.0025975 | 0.01709 | 0.0036914 | 0.018361 | -0.0057935 | 0.00045294 | -0.2655 | -0.018311 | -0.37537 | -0.32501 | -0.2243 | -0.31128 | -0.23804 | -0.27008 | 0.10071 | -0.36163 | -0.26093 | -0.1236 | -0.25635 | -0.12817 | -0.036621 | -122.7814 | -123.0881 | 0.11444 | 0.10071 | 0.027466 | 0.13733 | 0.064087 | -0.022888 | -122.6624 | -123.024 | 0.21515 | 0.21057 | 0.082397 | 0.23346 | 0.10528 | 0.15106 | 0.050354 | 0.23804 | 0.10071 | 0.35705 | 0.46234 | 0.32043 | 0.43945 | -123.1384 | -123.1247 | 0.013733 | 0.07782 | 0.073242 | 0.068664
5063.1719 | 122.9828 | -0.32044 | 122.7676 | -0.091095 | -0.0013009 | 0.017805 | 0.0096579 | 0.0010148 | 0.0015509 | -0.00077341 | -0.044067 | 0.0025975 | 0.018158 | 0.007323 | 0.019643 | -0.0057935 | -0.0021107 | -0.24261 | -0.018311 | -0.36163 | -0.33417 | -0.23804 | -0.32959 | -0.25635 | -0.27924 | 0.086975 | -0.36163 | -0.2655 | -0.14191 | -0.29297 | -0.12817 | -0.041198 | -122.7859 | -123.1018 | 0.082398 | 0.064087 | -0.009155 | 0.10528 | 0.032043 | -0.041198 | -122.6807 | -123.0331 | 0.17853 | 0.19226 | 0.027466 | 0.23346 | 0.068664 | 0.1236 | 0.027466 | 0.21973 | 0.09613 | 0.34332 | 0.44861 | 0.30212 | 0.40741 | -123.1293 | -123.1293 | -0.013732 | 0.054932 | 0.07782 | 0.041199
5064.1719 | 122.9599 | -0.34332 | 122.7448 | -0.052948 | -0.0015145 | 0.015669 | 0.0083761 | -0.0026168 | -0.0012261 | -0.00034601 | 0.010864 | 0.0034521 | 0.016022 | 0.0054004 | 0.018788 | -0.0072889 | 0.0034435 | -0.25177 | -0.018311 | -0.37079 | -0.32044 | -0.21515 | -0.27924 | -0.2243 | -0.26093 | 0.10071 | -0.36621 | -0.25635 | -0.10986 | -0.24719 | -0.16022 | -0.027466 | -122.7631 | -123.0652 | 0.12817 | 0.11902 | 0.064087 | 0.14648 | 0.091553 | -0.022888 | -122.644 | -123.0011 | 0.23346 | 0.18311 | 0.096131 | 0.20599 | 0.11902 | 0.15564 | 0.050354 | 0.25635 | 0.10986 | 0.35248 | 0.46692 | 0.32501 | 0.44403 | -123.1155 | -123.111 | 0.022888 | 0.086975 | 0.091553 | 0.082398
5065.1719 | 122.9645 | -0.33875 | 122.7402 | -0.083466 | -0.00023294 | 0.016951 | 0.0079489 | -0.0013352 | -0.0040033 | -0.00077341 | 0.026123 | 0.0021703 | 0.017303 | 0.003905 | 0.01772 | -0.0092115 | -0.0010425 | -0.25177 | -0.036621 | -0.35706 | -0.3067 | -0.18768 | -0.28839 | -0.20142 | -0.24719 | 0.10071 | -0.35248 | -0.25635 | -0.1236 | -0.2243 | -0.14191 | -0.018311 | -122.7768 | -123.0469 | 0.15106 | 0.13733 | 0.050354 | 0.15564 | 0.068665 | -0.013733 | -122.6395 | -122.9965 | 0.21515 | 0.19684 | 0.11444 | 0.21057 | 0.12817 | 0.16937 | 0.050354 | 0.22888 | 0.09613 | 0.32043 | 0.45319 | 0.30212 | 0.43945 | -123.0972 | -123.0927 | 0.032043 | 0.082397 | 0.086975 | 0.091553
5066.1719 | 122.9599 | -0.32959 | 122.7768 | -0.068207 | -0.0015145 | 0.01631 | 0.0081625 | 0.003151 | -0.0020807 | -0.0018414 | 0.016968 | 0.0040929 | 0.016235 | -0.00229 | 0.017934 | -0.0081433 | -0.0068103 | -0.21515 | -0.036621 | -0.36621 | -0.29297 | -0.17853 | -0.27924 | -0.20599 | -0.22888 | 0.091553 | -0.35706 | -0.24719 | -0.10529 | -0.23804 | -0.15564 | -0.036621 | -122.8134 | -123.0698 | 0.15106 | 0.1236 | 0.050354 | 0.16022 | 0.086975 | -0.027466 | -122.6852 | -123.024 | 0.2243 | 0.17395 | 0.091553 | 0.20142 | 0.11902 | 0.18768 | 0.073242 | 0.25177 | 0.10986 | 0.32959 | 0.44861 | 0.29297 | 0.42114 | -123.143 | -123.1338 | 0.036621 | 0.082398 | 0.11444 | 0.10071
5067.2344 | 123.0286 | -0.31586 | 122.7356 | -0.075836 | -0.0021555 | 0.016737 | 0.0094443 | -0.0015488 | 5.5488e-05 | -0.0012006 | -0.044067 | 0.0030249 | 0.016876 | 0.0017688 | 0.015584 | -0.0075025 | -0.00082886 | -0.23804 | -0.018311 | -0.36621 | -0.27466 | -0.16479 | -0.28839 | -0.2243 | -0.19226 | 0.091553 | -0.3479 | -0.20599 | -0.091553 | -0.20599 | -0.09613 | -0.050354 | -122.7539 | -123.0103 | 0.15106 | 0.091553 | 0.027466 | 0.14191 | 0.07782 | -0.032043 | -122.644 | -122.9416 | 0.2243 | 0.21973 | 0.10986 | 0.25177 | 0.14191 | 0.20142 | 0.091553 | 0.25635 | 0.14191 | 0.3479 | 0.43945 | 0.29755 | 0.40741 | -123.1018 | -123.0835 | 0.041199 | 0.10986 | 0.07782 | 0.1236
5068.1719 | 122.9736 | -0.3479 | 122.7768 | -0.083466 | -0.00023294 | 0.014815 | 0.0073081 | 0.0035782 | -0.0018671 | -0.00013241 | -0.056274 | 0.0032385 | 0.01709 | 0.010527 | 0.020497 | -0.0047253 | -0.0033923 | -0.2655 | -0.027466 | -0.3479 | -0.32044 | -0.24261 | -0.34332 | -0.27008 | -0.27924 | 0.10071 | -0.37537 | -0.25635 | -0.16022 | -0.29297 | -0.16022 | 0 | -122.8043 | -123.0972 | 0.10528 | 0.077819 | 0.004577 | 0.077819 | 0.004577 | -0.027466 | -122.6761 | -123.0331 | 0.18768 | 0.18768 | 0.054931 | 0.21515 | 0.082397 | 0.10528 | 0.027465 | 0.21515 | 0.11902 | 0.32043 | 0.47607 | 0.32043 | 0.44861 | -123.1247 | -123.1522 | 0.027465 | 0.091552 | 0.082397 | 0.068664
5069.1719 | 122.9691 | -0.33417 | 122.7356 | -0.045319 | -0.00044654 | 0.016951 | 0.0062399 | -0.00090783 | 0.0011237 | -0.00013241 | 0.016968 | 0.0032385 | 0.017731 | 0.0054004 | 0.016865 | -0.0068615 | 0.0034435 | -0.27466 | -0.004578 | -0.36163 | -0.32959 | -0.21515 | -0.29297 | -0.22888 | -0.27008 | 0.10071 | -0.35248 | -0.26093 | -0.12817 | -0.24719 | -0.14648 | -0.027466 | -122.7402 | -123.0652 | 0.11902 | 0.10528 | 0.041198 | 0.13275 | 0.068664 | -0.018311 | -122.6349 | -122.9965 | 0.20599 | 0.18768 | 0.086975 | 0.20599 | 0.10529 | 0.14648 | 0.032043 | 0.2243 | 0.091553 | 0.35705 | 0.45319 | 0.32959 | 0.43488 | -123.0972 | -123.0881 | 0.004577 | 0.073242 | 0.059509 | 0.064086
5070.1719 | 123.1064 | -0.29755 | 122.7356 | -0.083466 | 0.00019446 | 0.015456 | 0.0068807 | -0.00069423 | -0.00058531 | -0.0014142 | 0.047485 | 0.0015295 | 0.018158 | 0.0015552 | 0.019429 | -0.0077161 | -0.0038197 | -0.20599 | -0.059509 | -0.32959 | -0.20142 | -0.068665 | -0.17395 | -0.14191 | -0.10529 | 0.059509 | -0.33417 | -0.14191 | 0 | -0.1236 | -0.054932 | -0.032044 | -122.7951 | -122.937 | 0.22888 | 0.15564 | 0.1236 | 0.18768 | 0.15564 | -0.036621 | -122.6761 | -122.8775 | 0.29755 | 0.24261 | 0.17395 | 0.27924 | 0.21057 | 0.26092 | 0.12817 | 0.33417 | 0.19226 | 0.27008 | 0.39368 | 0.23804 | 0.35705 | -123.0652 | -123.0698 | 0.09613 | 0.15564 | 0.091552 | 0.19226
5071.1719 | 123.0698 | -0.31586 | 122.7264 | -0.075836 | 0.00019446 | 0.015456 | 0.0079489 | -0.0011214 | -0.0018671 | -0.00098701 | 0.02002 | 0.0025975 | 0.016022 | -0.00015378 | 0.017079 | -0.0075025 | -0.00061526 | -0.20142 | -0.041199 | -0.32959 | -0.23804 | -0.11444 | -0.20599 | -0.16479 | -0.16022 | 0.064087 | -0.33875 | -0.19684 | -0.045776 | -0.16937 | -0.09613 | -0.013733 | -122.7676 | -122.9645 | 0.20142 | 0.15106 | 0.10986 | 0.16479 | 0.1236 | -0.022888 | -122.6624 | -122.9233 | 0.27008 | 0.21973 | 0.14648 | 0.24262 | 0.16937 | 0.21515 | 0.091553 | 0.29297 | 0.14191 | 0.28839 | 0.40283 | 0.27466 | 0.37994 | -123.056 | -123.0652 | 0.07782 | 0.11902 | 0.11444 | 0.15564
5072.1719 | 122.9919 | -0.34332 | 122.7722 | -0.03006 | 0.00040806 | 0.015456 | 0.0075217 | -0.0021896 | 0.0015509 | -0.0012006 | -0.016602 | 0.0030249 | 0.018158 | 0.0026232 | 0.018147 | -0.0072889 | -0.0021107 | -0.28381 | -0.027466 | -0.37537 | -0.33875 | -0.24261 | -0.31128 | -0.24719 | -0.27008 | 0.10529 | -0.37537 | -0.27008 | -0.14191 | -0.2655 | -0.15564 | -0.032043 | -122.7997 | -123.111 | 0.10071 | 0.096131 | 0.032044 | 0.12817 | 0.064087 | -0.032043 | -122.6669 | -123.0423 | 0.20142 | 0.18768 | 0.07782 | 0.21973 | 0.10986 | 0.13275 | 0.036621 | 0.23346 | 0.10528 | 0.3479 | 0.48065 | 0.31586 | 0.44861 | -123.1476 | -123.1476 | 0.004578 | 0.073242 | 0.05951 | 0.073242
5073.1719 | 122.9965 | -0.31586 | 122.7539 | -0.03006 | 0.0016899 | 0.016737 | 0.0090169 | 0.0027238 | -0.00015811 | -0.0029096 | -0.056274 | 0.0047339 | 0.016663 | 0.008391 | 0.019002 | -0.0053663 | 0.00045294 | -0.27008 | -0.036621 | -0.37994 | -0.3479 | -0.26093 | -0.35248 | -0.27466 | -0.26093 | 0.082397 | -0.37537 | -0.23804 | -0.14191 | -0.27008 | -0.14191 | -0.064087 | -122.7905 | -123.1018 | 0.054932 | 0.041199 | -0.036621 | 0.10529 | 0.027466 | -0.059509 | -122.6715 | -122.9919 | 0.17395 | 0.17395 | 0.045776 | 0.23346 | 0.10528 | 0.11902 | 0.032044 | 0.23346 | 0.13733 | 0.34332 | 0.45776 | 0.27924 | 0.39825 | -123.1338 | -123.1293 | -0.032043 | 0.07782 | 0.045776 | 0.054932
5074.1719 | 123.0194 | -0.34332 | 122.731 | -0.098725 | 0.0012625 | 0.016737 | 0.0090169 | -0.001976 | 0.00048269 | 0.00072199 | 0.016968 | 0.0015295 | 0.016235 | 0.0094592 | 0.019643 | -0.0081433 | 0.0017345 | -0.2243 | -0.054932 | -0.36163 | -0.28839 | -0.16937 | -0.26093 | -0.21057 | -0.24261 | 0.082397 | -0.35248 | -0.25635 | -0.1236 | -0.24261 | -0.14191 | -0.01831 | -122.7859 | -123.0194 | 0.17395 | 0.13275 | 0.082398 | 0.15106 | 0.10071 | -0.009155 | -122.6486 | -122.9874 | 0.21973 | 0.20142 | 0.10071 | 0.21057 | 0.10986 | 0.19226 | 0.073242 | 0.22888 | 0.09613 | 0.3067 | 0.43488 | 0.28839 | 0.42572 | -123.0927 | -123.0835 | 0.054932 | 0.086975 | 0.11902 | 0.10071
5075.1719 | 123.0469 | -0.32501 | 122.7402 | -0.075836 | -0.00023294 | 0.016096 | 0.0053853 | 0.00016017 | 0.00069649 | -0.0024822 | 0.032227 | 0.0030249 | 0.017731 | 0.0064684 | 0.018361 | -0.0083569 | 2.554e-05 | -0.2243 | -0.064087 | -0.33875 | -0.28381 | -0.16022 | -0.24719 | -0.18768 | -0.2243 | 0.086975 | -0.34332 | -0.26093 | -0.10986 | -0.23804 | -0.13733 | -0.013733 | -122.8043 | -123.024 | 0.1648 | 0.13733 | 0.07782 | 0.15106 | 0.091553 | -0.018311 | -122.6532 | -123.0011 | 0.21515 | 0.18768 | 0.086975 | 0.20599 | 0.10529 | 0.17853 | 0.054932 | 0.23346 | 0.082398 | 0.27466 | 0.4303 | 0.26093 | 0.41199 | -123.0789 | -123.0835 | 0.041199 | 0.064087 | 0.10071 | 0.10071
5076.1719 | 122.9965 | -0.35248 | 122.7631 | -0.0071715 | -0.0021555 | 0.015242 | 0.0077353 | 0.00080117 | -0.0018671 | -0.00034601 | -0.010498 | 0.0017431 | 0.017517 | 0.010955 | 0.017293 | -0.0060071 | 0.00023934 | -0.28381 | -0.032043 | -0.37079 | -0.33875 | -0.2243 | -0.30212 | -0.25177 | -0.25177 | 0.082397 | -0.36621 | -0.26093 | -0.12817 | -0.27008 | -0.14648 | -0.018311 | -122.7951 | -123.1018 | 0.12817 | 0.10071 | 0.050354 | 0.11902 | 0.068665 | -0.013733 | -122.6807 | -123.024 | 0.2243 | 0.20599 | 0.082397 | 0.21973 | 0.09613 | 0.14648 | 0.032044 | 0.23804 | 0.10529 | 0.33875 | 0.44861 | 0.32044 | 0.43488 | -123.1339 | -123.1293 | 0.013733 | 0.091553 | 0.068665 | 0.10071
5077.1719 | 123.0103 | -0.31128 | 122.7448 | -0.060578 | 0.00083526 | 0.016096 | 0.0058127 | 0.0012284 | 0.00069649 | -0.0018414 | 0.0047608 | 0.0019567 | 0.017517 | 0.00048702 | 0.01772 | -0.0077161 | 0.0030163 | -0.22888 | -0.059509 | -0.36163 | -0.2655 | -0.13275 | -0.2243 | -0.1831 | -0.19226 | 0.07782 | -0.35706 | -0.23346 | -0.086975 | -0.24719 | -0.12817 | -0.050354 | -122.8043 | -123.0103 | 0.17853 | 0.12817 | 0.086975 | 0.17853 | 0.13733 | -0.045777 | -122.6669 | -122.9782 | 0.2243 | 0.1831 | 0.064087 | 0.22888 | 0.10986 | 0.22888 | 0.09613 | 0.27008 | 0.1236 | 0.30212 | 0.43488 | 0.25177 | 0.3891 | -123.1064 | -123.1018 | 0.045776 | 0.07782 | 0.082397 | 0.11902
5078.1719 | 123.0057 | -0.32044 | 122.7676 | -0.052948 | 0.0010489 | 0.016524 | 0.0062399 | 0.00251 | -0.0016535 | 0.00093559 | 0.032227 | 0.0030249 | 0.018372 | 0.0058276 | 0.018361 | -0.0085705 | -0.00040166 | -0.21973 | -0.064087 | -0.3479 | -0.25177 | -0.13275 | -0.21515 | -0.17853 | -0.18768 | 0.064087 | -0.34332 | -0.2243 | -0.091553 | -0.2243 | -0.13733 | -0.027465 | -122.8317 | -123.0194 | 0.18768 | 0.14191 | 0.10529 | 0.16937 | 0.13275 | -0.022888 | -122.7036 | -122.9919 | 0.22888 | 0.18311 | 0.096131 | 0.20599 | 0.11902 | 0.21515 | 0.09613 | 0.25177 | 0.11902 | 0.28381 | 0.40741 | 0.25635 | 0.38452 | -123.1155 | -123.111 | 0.068665 | 0.096131 | 0.10071 | 0.13275
5079.1719 | 122.9736 | -0.34332 | 122.7676 | -0.052948 | -0.00044654 | 0.014815 | 0.0092307 | 0.001442 | -0.00037171 | -0.0044048 | -0.022705 | 0.0015295 | 0.017303 | 0.0094592 | 0.018788 | -0.0072889 | 0.0017345 | -0.28839 | -0.022888 | -0.37079 | -0.32501 | -0.23804 | -0.3067 | -0.24719 | -0.28839 | 0.086975 | -0.37994 | -0.25177 | -0.1236 | -0.25635 | -0.13733 | -0.027466 | -122.7905 | -123.0927 | 0.10529 | 0.096131 | 0.036621 | 0.1236 | 0.064087 | -0.036621 | -122.6807 | -123.0194 | 0.21973 | 0.20599 | 0.086975 | 0.24261 | 0.1236 | 0.13275 | 0.045777 | 0.25635 | 0.12817 | 0.3479 | 0.46692 | 0.32043 | 0.4303 | -123.1384 | -123.1476 | 0.018311 | 0.091553 | 0.054932 | 0.054932
5080.1719 | 123.0103 | -0.31586 | 122.7493 | -0.037689 | 0.00062166 | 0.016096 | 0.0075217 | -0.00090783 | 0.0013373 | -0.002696 | -0.016602 | 0.0032385 | 0.01474 | 0.0034778 | 0.018361 | -0.0072889 | -0.0029651 | -0.28381 | -0.027466 | -0.37537 | -0.33875 | -0.22888 | -0.30212 | -0.25177 | -0.28381 | 0.064087 | -0.38452 | -0.2655 | -0.12817 | -0.2655 | -0.12817 | -0.059509 | -122.7768 | -123.0881 | 0.086975 | 0.064087 | 0.013733 | 0.1236 | 0.073242 | -0.068664 | -122.6852 | -123.0148 | 0.18768 | 0.18768 | 0.050354 | 0.25635 | 0.11902 | 0.14648 | 0.036621 | 0.25635 | 0.11902 | 0.3479 | 0.44861 | 0.28839 | 0.37994 | -123.1247 | -123.1339 | -0.022888 | 0.050354 | 0.032044 | 0.032044
5081.1719 | 122.9919 | -0.32501 | 122.7768 | -0.075836 | -0.0013009 | 0.016524 | 0.0062399 | 0.00016017 | -0.0010125 | -0.0024822 | 0.0047608 | 0.0040929 | 0.015808 | 0.0041186 | 0.017934 | -0.0068615 | 0.0015209 | -0.25177 | -0.032043 | -0.3479 | -0.31586 | -0.20599 | -0.28381 | -0.2243 | -0.24719 | 0.073242 | -0.36163 | -0.2655 | -0.11444 | -0.24261 | -0.14648 | -0.022888 | -122.8088 | -123.0927 | 0.11902 | 0.10071 | 0.041199 | 0.1236 | 0.064087 | -0.036621 | -122.7036 | -123.0423 | 0.21057 | 0.17853 | 0.082397 | 0.21515 | 0.11902 | 0.14191 | 0.032043 | 0.24719 | 0.09613 | 0.31586 | 0.43488 | 0.29297 | 0.39825 | -123.1247 | -123.1384 | 0.009155 | 0.059509 | 0.073242 | 0.07782
5082.1719 | 122.9965 | -0.34332 | 122.7402 | -0.022431 | -0.00023294 | 0.017805 | 0.0073081 | 0.0010148 | -0.00079891 | -0.0024822 | 0.0047608 | 0.0011023 | 0.019226 | -0.00079478 | 0.018147 | -0.0087843 | -0.0010425 | -0.23346 | -0.050354 | -0.35248 | -0.29297 | -0.1831 | -0.27008 | -0.20599 | -0.22888 | 0.073242 | -0.35248 | -0.26093 | -0.1236 | -0.24261 | -0.16022 | -0.009155 | -122.7905 | -123.0331 | 0.16022 | 0.13733 | 0.073242 | 0.14648 | 0.082397 | -0.009155 | -122.6669 | -123.0011 | 0.21973 | 0.18311 | 0.10071 | 0.19226 | 0.10986 | 0.16937 | 0.059509 | 0.22888 | 0.091553 | 0.30212 | 0.42572 | 0.29297 | 0.41656 | -123.0927 | -123.0927 | 0.050354 | 0.082398 | 0.10986 | 0.11444
5083.1719 | 122.9691 | -0.33875 | 122.7676 | -0.022431 | -0.0019417 | 0.016096 | 0.0073081 | -0.0021896 | 0.0017645 | -0.0018414 | 0.0047608 | 0.0025975 | 0.01709 | 0.0036914 | 0.019643 | -0.0057935 | 0.0013073 | -0.28839 | -0.032043 | -0.35706 | -0.33417 | -0.22888 | -0.30212 | -0.26093 | -0.27008 | 0.091553 | -0.38452 | -0.27466 | -0.13733 | -0.25635 | -0.15106 | -0.018311 | -122.7997 | -123.1018 | 0.10986 | 0.07782 | 0.036621 | 0.096131 | 0.054932 | -0.045776 | -122.6761 | -123.0423 | 0.20142 | 0.18768 | 0.082397 | 0.23346 | 0.12817 | 0.12817 | 0.022889 | 0.24719 | 0.10986 | 0.32501 | 0.47607 | 0.3067 | 0.4303 | -123.1247 | -123.1522 | 0.004578 | 0.064087 | 0.050354 | 0.068664
5084.1719 | 122.9874 | -0.33875 | 122.7493 | -0.014801 | -0.00023294 | 0.016951 | 0.0079489 | 0.001442 | -0.0010125 | -0.00055961 | 0.044434 | 0.0028113 | 0.016235 | 0.0041186 | 0.019856 | -0.0064343 | -0.0042469 | -0.21973 | -0.059509 | -0.32959 | -0.2655 | -0.13275 | -0.22888 | -0.18768 | -0.19226 | 0.073242 | -0.35248 | -0.23804 | -0.1236 | -0.24719 | -0.15564 | 0.009155 | -122.8088 | -123.0148 | 0.20599 | 0.15106 | 0.10986 | 0.14191 | 0.10071 | -0.013733 | -122.6761 | -122.9874 | 0.21515 | 0.18311 | 0.091553 | 0.19684 | 0.10529 | 0.19684 | 0.064087 | 0.22888 | 0.11444 | 0.27008 | 0.42572 | 0.27924 | 0.41199 | -123.0789 | -123.1018 | 0.073242 | 0.10071 | 0.11902 | 0.14648
5085.2344 | 122.9965 | -0.3067 | 122.7631 | -0.037689 | 0.00062166 | 0.017592 | 0.0096579 | -0.00048063 | -0.0012261 | -0.00098701 | -0.056274 | 0.0047339 | 0.017731 | -0.00079478 | 0.019215 | -0.0072889 | -0.0036059 | -0.23804 | -0.036621 | -0.36163 | -0.29297 | -0.16479 | -0.27924 | -0.2243 | -0.19684 | 0.073242 | -0.32959 | -0.18768 | -0.11444 | -0.24719 | -0.11444 | -0.054931 | -122.7997 | -123.056 | 0.14191 | 0.082398 | 0.027466 | 0.13733 | 0.082397 | -0.022888 | -122.6898 | -122.9507 | 0.19226 | 0.19226 | 0.05951 | 0.21515 | 0.082398 | 0.19684 | 0.068664 | 0.21515 | 0.14191 | 0.32501 | 0.40283 | 0.27008 | 0.37994 | -123.1247 | -123.0927 | 0.013733 | 0.11902 | 0.068665 | 0.10986
5086.1719 | 122.9736 | -0.33875 | 122.7493 | -0.068207 | 0.0010489 | 0.015028 | 0.0077353 | -0.0026168 | -0.00037171 | 0.0011494 | 0.0047608 | 0.0021703 | 0.014526 | 0.0043322 | 0.018574 | -0.0064343 | -0.0033923 | -0.29297 | -0.018311 | -0.39368 | -0.33417 | -0.23346 | -0.30212 | -0.2655 | -0.27008 | 0.086975 | -0.39368 | -0.2655 | -0.12817 | -0.2655 | -0.14648 | -0.054932 | -122.7676 | -123.0835 | 0.10529 | 0.073242 | 0.036621 | 0.12817 | 0.091553 | -0.054932 | -122.6624 | -123.0148 | 0.21057 | 0.19226 | 0.073242 | 0.24719 | 0.12817 | 0.16022 | 0.05951 | 0.2655 | 0.12817 | 0.37537 | 0.48065 | 0.32043 | 0.42572 | -123.143 | -123.143 | 0.004578 | 0.073242 | 0.045776 | 0.068664
5087.1719 | 123.0103 | -0.31128 | 122.7539 | -0.098725 | -0.00066014 | 0.01631 | 0.010512 | 0.0020828 | -0.00037171 | -0.00034601 | -0.034912 | 0.0025975 | 0.016876 | 0.0013416 | 0.017506 | -0.0083569 | 0.0013073 | -0.24719 | -0.032043 | -0.36621 | -0.28839 | -0.16937 | -0.28381 | -0.22888 | -0.18768 | 0.068665 | -0.35248 | -0.20142 | -0.10071 | -0.21057 | -0.11444 | -0.054932 | -122.7859 | -123.0423 | 0.14191 | 0.082397 | 0.027466 | 0.13733 | 0.082398 | -0.041199 | -122.6852 | -122.9553 | 0.21057 | 0.19684 | 0.10071 | 0.23804 | 0.14191 | 0.19684 | 0.07782 | 0.25177 | 0.15106 | 0.33417 | 0.42114 | 0.27924 | 0.37994 | -123.1201 | -123.1064 | 0.022888 | 0.10986 | 0.064087 | 0.1236
5088.2344 | 123.0606 | -0.34332 | 122.7448 | -0.091095 | 0.0014761 | 0.015028 | 0.0047445 | -0.0030442 | -0.0012261 | -0.0018414 | 0.035278 | 0.00067495 | 0.015381 | 0.00048702 | 0.016011 | -0.0060071 | -0.0042469 | -0.21515 | -0.059509 | -0.34332 | -0.23804 | -0.11902 | -0.21057 | -0.16937 | -0.16937 | 0.059509 | -0.35248 | -0.21057 | -0.064087 | -0.16937 | -0.091553 | 0 | -122.8043 | -122.9828 | 0.2243 | 0.17395 | 0.13275 | 0.17395 | 0.13275 | -0.009155 | -122.6852 | -122.9553 | 0.27924 | 0.25177 | 0.17395 | 0.26093 | 0.18311 | 0.2243 | 0.10529 | 0.28839 | 0.14191 | 0.28381 | 0.41199 | 0.28381 | 0.40283 | -123.0881 | -123.0972 | 0.10529 | 0.13275 | 0.12817 | 0.17395
5089.1719 | 123.0148 | -0.32044 | 122.7448 | -0.052948 | 0.00040806 | 0.017592 | 0.0051717 | -0.00026703 | -0.0025079 | -0.0012006 | 0.03833 | 0.0021703 | 0.015594 | 0.0013416 | 0.018361 | -0.0087843 | 0.0013073 | -0.2243 | -0.050354 | -0.3479 | -0.27008 | -0.15106 | -0.23346 | -0.21973 | -0.20599 | 0.059509 | -0.35706 | -0.23346 | -0.1236 | -0.23804 | -0.13733 | -0.027465 | -122.7951 | -123.0148 | 0.16937 | 0.10071 | 0.086976 | 0.12817 | 0.11444 | -0.036621 | -122.6852 | -122.9782 | 0.19684 | 0.18311 | 0.082398 | 0.21973 | 0.11902 | 0.19684 | 0.077819 | 0.23346 | 0.1236 | 0.29755 | 0.41656 | 0.27008 | 0.37994 | -123.0927 | -123.1018 | 0.050354 | 0.086976 | 0.096131 | 0.11444
5090.1719 | 123.0194 | -0.33417 | 122.7448 | -0.052948 | 0.00019446 | 0.018233 | 0.0073081 | 0.00080117 | -0.0027215 | -0.0014142 | 0.035278 | 0.0038793 | 0.017517 | 0.0075366 | 0.017506 | -0.0068615 | -0.0016833 | -0.23346 | -0.059509 | -0.35706 | -0.2655 | -0.15564 | -0.23346 | -0.1831 | -0.17395 | 0.050354 | -0.37079 | -0.23346 | -0.082397 | -0.21057 | -0.13275 | -0.022889 | -122.8043 | -123.0103 | 0.17853 | 0.15106 | 0.10071 | 0.17395 | 0.1236 | -0.036622 | -122.6944 | -122.9782 | 0.25177 | 0.20142 | 0.1236 | 0.23804 | 0.16022 | 0.20142 | 0.091553 | 0.28839 | 0.13733 | 0.29755 | 0.42114 | 0.27466 | 0.38452 | -123.1018 | -123.1155 | 0.068664 | 0.10071 | 0.10071 | 0.16022
5091.1719 | 123.0331 | -0.3067 | 122.7448 | -0.052948 | -0.00087374 | 0.015456 | 0.0073081 | 0.0040054 | -0.0014399 | -0.0033368 | 0.016968 | 0.0028113 | 0.017731 | 0.010314 | 0.019215 | -0.0083569 | -0.0025379 | -0.21973 | -0.059509 | -0.3479 | -0.22888 | -0.1236 | -0.2243 | -0.15564 | -0.17395 | 0.054932 | -0.35248 | -0.20599 | -0.059509 | -0.19684 | -0.10529 | -0.041198 | -122.8043 | -122.9736 | 0.18311 | 0.15106 | 0.082398 | 0.19226 | 0.1236 | -0.045776 | -122.6898 | -122.9507 | 0.24719 | 0.20142 | 0.10986 | 0.24719 | 0.15564 | 0.2243 | 0.11902 | 0.29297 | 0.14648 | 0.28839 | 0.40741 | 0.24719 | 0.36163 | -123.0927 | -123.0972 | 0.07782 | 0.10071 | 0.086975 | 0.13275
5092.1719 | 123.0881 | -0.29755 | 122.7493 | -0.091095 | 0.0010489 | 0.015242 | 0.0041037 | 0.00037377 | -0.00058531 | -0.00098701 | 0.029175 | 0.0017431 | 0.015167 | 0.0047594 | 0.016652 | -0.0075025 | 0.0032299 | -0.21973 | -0.07782 | -0.36621 | -0.23346 | -0.11902 | -0.18768 | -0.16937 | -0.13275 | 0.041199 | -0.34332 | -0.1831 | -0.041199 | -0.15564 | -0.10529 | -0.068665 | -122.8271 | -122.9828 | 0.17853 | 0.12817 | 0.10986 | 0.19684 | 0.17853 | -0.045777 | -122.7081 | -122.9324 | 0.25635 | 0.19226 | 0.14191 | 0.23804 | 0.18768 | 0.24719 | 0.13275 | 0.30212 | 0.16022 | 0.28839 | 0.38452 | 0.21973 | 0.33874 | -123.1155 | -123.0927 | 0.064087 | 0.11444 | 0.077819 | 0.16479
5093.1719 | 122.9919 | -0.31128 | 122.7585 | -0.098725 | 0.0042533 | 0.017805 | 0.0068807 | -0.001976 | -0.00037171 | -0.0031232 | -0.0013428 | 0.0032385 | 0.013245 | 0.0028368 | 0.018788 | -0.0075025 | -0.0059559 | -0.2243 | -0.059509 | -0.34332 | -0.27924 | -0.16479 | -0.25177 | -0.20599 | -0.21515 | 0.068665 | -0.35248 | -0.25635 | -0.09613 | -0.23804 | -0.16937 | -0.032044 | -122.818 | -123.0377 | 0.14648 | 0.10528 | 0.059509 | 0.13733 | 0.091553 | -0.041199 | -122.6898 | -123.0148 | 0.21515 | 0.14191 | 0.073242 | 0.18311 | 0.11444 | 0.17853 | 0.064087 | 0.25635 | 0.09613 | 0.28381 | 0.42114 | 0.25177 | 0.37994 | -123.1018 | -123.111 | 0.032043 | 0.054931 | 0.086975 | 0.09613
5094.1719 | 123.024 | -0.32044 | 122.7631 | -0.083466 | -0.0010873 | 0.016096 | 0.0075217 | 0.0012284 | 0.00069649 | -0.00098701 | 0.0047608 | 0.0017431 | 0.01709 | 0.0051868 | 0.016011 | -0.0077161 | -0.0036059 | -0.21057 | -0.068665 | -0.3479 | -0.26093 | -0.15106 | -0.23346 | -0.17395 | -0.19226 | 0.045776 | -0.35706 | -0.25177 | -0.10986 | -0.21515 | -0.12817 | -0.027465 | -122.8317 | -123.024 | 0.16937 | 0.14649 | 0.086976 | 0.17395 | 0.11444 | -0.036621 | -122.7173 | -123.0148 | 0.21057 | 0.19226 | 0.10529 | 0.22888 | 0.14191 | 0.19684 | 0.086975 | 0.24719 | 0.10529 | 0.27924 | 0.40283 | 0.25177 | 0.36621 | -123.111 | -123.1201 | 0.05951 | 0.068665 | 0.10986 | 0.12817
5095.1719 | 123.0469 | -0.32044 | 122.7448 | -0.083466 | -0.0010873 | 0.016951 | 0.0064535 | 0.0016556 | 0.00048269 | -0.00077341 | 0.02002 | 0.0011023 | 0.015381 | 0.0051868 | 0.01772 | -0.0072889 | -0.0074513 | -0.20599 | -0.064087 | -0.33417 | -0.24261 | -0.12817 | -0.21057 | -0.16022 | -0.17395 | 0.054932 | -0.34332 | -0.22888 | -0.068665 | -0.20599 | -0.10986 | -0.013732 | -122.8088 | -122.9874 | 0.19226 | 0.16022 | 0.10986 | 0.17395 | 0.1236 | -0.022888 | -122.6898 | -122.9736 | 0.25177 | 0.21057 | 0.11444 | 0.23346 | 0.13733 | 0.20599 | 0.091552 | 0.27466 | 0.11444 | 0.27008 | 0.39825 | 0.25635 | 0.37537 | -123.0789 | -123.0881 | 0.07782 | 0.091553 | 0.11444 | 0.14649
5096.1719 | 123.0469 | -0.31128 | 122.7539 | -0.060578 | -1.9142e-05 | 0.014815 | 0.0068807 | 0.0020828 | 0.00026909 | 0.00072199 | -0.0013428 | 0.0011023 | 0.015167 | 0.002196 | 0.019215 | -0.0094251 | 0.0023755 | -0.21057 | -0.068665 | -0.33417 | -0.22888 | -0.11902 | -0.21973 | -0.16022 | -0.15106 | 0.064087 | -0.33875 | -0.1831 | -0.041199 | -0.16022 | -0.09613 | -0.022888 | -122.8226 | -122.9828 | 0.19226 | 0.15106 | 0.091552 | 0.17395 | 0.11444 | -0.027466 | -122.6898 | -122.937 | 0.27008 | 0.21515 | 0.15106 | 0.24262 | 0.17853 | 0.21515 | 0.10528 | 0.29755 | 0.15564 | 0.2655 | 0.40283 | 0.24261 | 0.37537 | -123.0881 | -123.0927 | 0.082397 | 0.12817 | 0.10071 | 0.16022
5097.1719 | 123.0835 | -0.3067 | 122.7493 | -0.091095 | -0.00087374 | 0.016524 | 0.0058127 | -0.00090783 | -0.00015811 | -0.0031232 | 0.016968 | 0.0015295 | 0.015594 | 0.0032642 | 0.017506 | -0.0096387 | -0.00040166 | -0.21515 | -0.073242 | -0.34332 | -0.20142 | -0.10529 | -0.19226 | -0.16022 | -0.12817 | 0.054932 | -0.34332 | -0.18768 | -0.041199 | -0.15106 | -0.068665 | -0.036621 | -122.8226 | -122.9507 | 0.20142 | 0.14648 | 0.11444 | 0.18311 | 0.15106 | -0.036621 | -122.6944 | -122.937 | 0.2655 | 0.23804 | 0.15564 | 0.27466 | 0.19226 | 0.23804 | 0.14191 | 0.30212 | 0.15564 | 0.27008 | 0.39825 | 0.23346 | 0.36163 | -123.0927 | -123.0927 | 0.10529 | 0.11902 | 0.091553 | 0.17853
5098.1719 | 123.0927 | -0.3067 | 122.7402 | -0.075836 | 0.0014761 | 0.016096 | 0.0075217 | 0.0010148 | -0.00015811 | -0.0016278 | 0.001709 | 0.00046135 | 0.016022 | 0.0041186 | 0.017934 | -0.0066479 | -0.0014697 | -0.19684 | -0.059509 | -0.34332 | -0.20599 | -0.091553 | -0.20142 | -0.15564 | -0.1236 | 0.041199 | -0.35248 | -0.15564 | -0.018311 | -0.15106 | -0.064087 | -0.036621 | -122.7997 | -122.9462 | 0.21515 | 0.15106 | 0.10529 | 0.18768 | 0.14191 | -0.045776 | -122.699 | -122.8958 | 0.28839 | 0.24261 | 0.15564 | 0.28839 | 0.20142 | 0.25177 | 0.13733 | 0.33417 | 0.19684 | 0.28381 | 0.39368 | 0.24719 | 0.3479 | -123.0835 | -123.0927 | 0.10071 | 0.15106 | 0.10986 | 0.18311
5099.1719 | 123.1018 | -0.3067 | 122.7402 | -0.060578 | -0.00087374 | 0.015883 | 0.0085897 | -0.0030442 | -0.0010125 | -0.00098701 | 0.023071 | 0.00088875 | 0.014099 | 0.007323 | 0.017079 | -0.010066 | -0.0018971 | -0.21057 | -0.064087 | -0.34332 | -0.21515 | -0.07782 | -0.19226 | -0.13275 | -0.11444 | 0.041199 | -0.32501 | -0.16479 | -0.018311 | -0.12817 | -0.064087 | -0.036621 | -122.8043 | -122.9553 | 0.22888 | 0.17395 | 0.11444 | 0.21057 | 0.15106 | -0.01831 | -122.699 | -122.905 | 0.28839 | 0.24261 | 0.17853 | 0.26093 | 0.19684 | 0.2655 | 0.12817 | 0.3067 | 0.16022 | 0.27924 | 0.36621 | 0.24261 | 0.3479 | -123.0835 | -123.0652 | 0.091553 | 0.14191 | 0.096131 | 0.19226
5100.1719 | 123.0927 | -0.32501 | 122.7539 | -0.075836 | 0.0023307 | 0.015456 | 0.0083761 | 0.0022964 | -0.00037171 | -0.0024822 | 0.016968 | 0.0028113 | 0.015808 | 0.0030506 | 0.018147 | -0.0087843 | -0.0027515 | -0.21515 | -0.059509 | -0.32501 | -0.2243 | -0.11902 | -0.2243 | -0.16937 | -0.16937 | 0.059509 | -0.33875 | -0.20599 | -0.059509 | -0.20599 | -0.10986 | 0 | -122.8134 | -122.9782 | 0.20599 | 0.15564 | 0.10071 | 0.15564 | 0.10071 | -0.013733 | -122.6944 | -122.9599 | 0.2655 | 0.21515 | 0.11902 | 0.22888 | 0.13275 | 0.20599 | 0.10071 | 0.27924 | 0.13275 | 0.2655 | 0.39825 | 0.2655 | 0.38452 | -123.0789 | -123.0927 | 0.10071 | 0.11902 | 0.10986 | 0.15564
5101.1719 | 123.0148 | -0.32959 | 122.7722 | -0.10635 | 0.0012625 | 0.015883 | 0.0075217 | 0.00016017 | 0.00026909 | -0.0012006 | -0.0043946 | 0.0036657 | 0.016663 | 0.0045458 | 0.019643 | -0.0049389 | -0.0046741 | -0.23804 | -0.050354 | -0.35706 | -0.3067 | -0.1831 | -0.28381 | -0.2243 | -0.22888 | 0.073242 | -0.36163 | -0.25635 | -0.11902 | -0.25177 | -0.16022 | -0.027466 | -122.8226 | -123.0789 | 0.14649 | 0.10529 | 0.045777 | 0.13275 | 0.073243 | -0.032043 | -122.699 | -123.0286 | 0.21057 | 0.16937 | 0.07782 | 0.20142 | 0.10986 | 0.17395 | 0.050354 | 0.24261 | 0.10528 | 0.3067 | 0.43488 | 0.27924 | 0.40283 | -123.1293 | -123.1338 | 0.022888 | 0.073242 | 0.091553 | 0.10071
5102.2344 | 123.0972 | -0.29755 | 122.731 | -0.083466 | -0.00044654 | 0.015242 | 0.0070943 | -0.00026703 | 5.5488e-05 | -0.005473 | 0.0078126 | 0.0021703 | 0.016663 | 0.0077502 | 0.019002 | -0.0062207 | 0.00088014 | -0.19226 | -0.059509 | -0.35248 | -0.21515 | -0.082397 | -0.20142 | -0.14648 | -0.10986 | 0.032043 | -0.33875 | -0.15106 | -0.009155 | -0.11902 | -0.073242 | -0.054932 | -122.7905 | -122.9462 | 0.21515 | 0.15106 | 0.09613 | 0.20599 | 0.15106 | -0.041199 | -122.699 | -122.8821 | 0.28839 | 0.2243 | 0.17853 | 0.2655 | 0.21973 | 0.27008 | 0.13733 | 0.32959 | 0.18768 | 0.29297 | 0.37079 | 0.23804 | 0.32959 | -123.0835 | -123.0698 | 0.082397 | 0.14648 | 0.10528 | 0.18768
5103.1719 | 123.0743 | -0.32501 | 122.7493 | -0.060578 | -0.0010873 | 0.015242 | 0.0083761 | -0.0034714 | -0.0029351 | -0.00077341 | -0.016602 | 0.0011023 | 0.015594 | 0.0015552 | 0.020711 | -0.0081433 | -0.0051013 | -0.2243 | -0.064087 | -0.32959 | -0.25635 | -0.15106 | -0.24261 | -0.19684 | -0.19226 | 0.045776 | -0.36163 | -0.23804 | -0.091553 | -0.23346 | -0.13733 | -0.004578 | -122.8134 | -123.0057 | 0.17395 | 0.12817 | 0.082397 | 0.13275 | 0.086975 | -0.036621 | -122.7036 | -122.9874 | 0.23346 | 0.18768 | 0.091553 | 0.2243 | 0.12817 | 0.17853 | 0.073242 | 0.27008 | 0.1236 | 0.2655 | 0.40741 | 0.26093 | 0.37079 | -123.0789 | -123.111 | 0.068664 | 0.086975 | 0.10071 | 0.13275
5104.1719 | 123.0972 | -0.28381 | 122.7493 | -0.060578 | -0.00087374 | 0.014174 | 0.0070943 | 0.00080117 | -0.0027215 | -0.00098701 | 0.013916 | 0.0023839 | 0.015594 | -0.002931 | 0.016652 | -0.0055799 | -0.0023243 | -0.19684 | -0.086975 | -0.33875 | -0.21515 | -0.07782 | -0.20142 | -0.14191 | -0.11444 | 0.036621 | -0.32959 | -0.16022 | -0.018311 | -0.11902 | -0.068665 | -0.054932 | -122.8363 | -122.9645 | 0.20599 | 0.14191 | 0.082397 | 0.19684 | 0.13733 | -0.045777 | -122.7127 | -122.9095 | 0.2655 | 0.21515 | 0.16479 | 0.26092 | 0.21057 | 0.26093 | 0.1236 | 0.31128 | 0.16937 | 0.25177 | 0.36621 | 0.19684 | 0.32043 | -123.0881 | -123.0789 | 0.068664 | 0.1236 | 0.086975 | 0.16937
5105.2344 | 123.0331 | -0.32501 | 122.7631 | -0.045319 | -0.0023691 | 0.015242 | 0.010512 | 0.00058737 | -0.0022943 | 0.001363 | -0.028809 | 0.0038793 | 0.019012 | 0.0077502 | 0.017293 | -0.0057935 | -0.0012561 | -0.24719 | -0.045776 | -0.38452 | -0.32501 | -0.2243 | -0.28381 | -0.23804 | -0.2243 | 0.07782 | -0.36621 | -0.21973 | -0.10529 | -0.23804 | -0.11444 | -0.059509 | -122.8088 | -123.0881 | 0.10071 | 0.086975 | 0.041199 | 0.14648 | 0.10071 | -0.041199 | -122.6852 | -122.9828 | 0.21973 | 0.21057 | 0.086975 | 0.25177 | 0.12817 | 0.16022 | 0.059509 | 0.26093 | 0.14648 | 0.33875 | 0.44403 | 0.27924 | 0.40283 | -123.1476 | -123.1293 | 0 | 0.10529 | 0.07782 | 0.10071
5106.1719 | 123.0698 | -0.29297 | 122.7356 | -0.060578 | -0.00066014 | 0.015242 | 0.0081625 | 0.0033646 | -0.0018671 | 0.00093559 | 0.0047608 | 0.00046135 | 0.016449 | 0.0019824 | 0.017934 | -0.0066479 | -0.0012561 | -0.21973 | -0.068665 | -0.3479 | -0.2243 | -0.09613 | -0.21973 | -0.16022 | -0.14648 | 0.027466 | -0.37079 | -0.17395 | -0.032043 | -0.15564 | -0.09613 | -0.054931 | -122.8043 | -122.9599 | 0.19684 | 0.13275 | 0.073242 | 0.18768 | 0.12817 | -0.07782 | -122.7081 | -122.9095 | 0.26093 | 0.19684 | 0.13733 | 0.27466 | 0.21515 | 0.25177 | 0.1236 | 0.33875 | 0.19684 | 0.27924 | 0.39825 | 0.2243 | 0.32043 | -123.0835 | -123.1064 | 0.068665 | 0.11902 | 0.073242 | 0.14648
5107.1719 | 123.0789 | -0.29755 | 122.7539 | -0.098725 | 0.0019035 | 0.016096 | 0.0060263 | -0.00048063 | 0.0013373 | 0.00050839 | 0.02002 | 0.0032385 | 0.016876 | 0.010527 | 0.017934 | -0.0075025 | -0.0010425 | -0.21973 | -0.091553 | -0.34332 | -0.22888 | -0.10071 | -0.21973 | -0.15564 | -0.11902 | 0.050354 | -0.36163 | -0.17853 | -0.004578 | -0.13733 | -0.073242 | -0.045777 | -122.8455 | -122.9828 | 0.19684 | 0.14191 | 0.077819 | 0.18768 | 0.1236 | -0.064087 | -122.7036 | -122.9324 | 0.29297 | 0.2243 | 0.16022 | 0.28839 | 0.2243 | 0.24261 | 0.11444 | 0.35705 | 0.1831 | 0.25177 | 0.41199 | 0.20599 | 0.3479 | -123.0972 | -123.1155 | 0.068664 | 0.11902 | 0.077819 | 0.17853
5108.1719 | 123.1064 | -0.28381 | 122.731 | -0.098725 | 0.0012625 | 0.015028 | 0.0058127 | 0.003151 | -0.0012261 | -0.00013241 | 0.010864 | 0.0030249 | 0.019653 | 0.0034778 | 0.016225 | -0.0055799 | -0.0031787 | -0.21057 | -0.07782 | -0.34332 | -0.21973 | -0.091553 | -0.19684 | -0.15106 | -0.12817 | 0.018311 | -0.33875 | -0.16937 | -0.022888 | -0.12817 | -0.054932 | -0.05951 | -122.8088 | -122.9507 | 0.19226 | 0.13275 | 0.086975 | 0.19226 | 0.14648 | -0.054932 | -122.7127 | -122.9004 | 0.26092 | 0.22888 | 0.15564 | 0.28381 | 0.21057 | 0.25177 | 0.1236 | 0.31586 | 0.16937 | 0.2655 | 0.35706 | 0.20599 | 0.30212 | -123.0743 | -123.0698 | 0.064086 | 0.11444 | 0.073242 | 0.15564
5109.1719 | 123.0881 | -0.30212 | 122.7493 | -0.075836 | -0.0017281 | 0.015456 | 0.0070943 | 0.00016017 | 0.00026909 | -0.0018414 | 0.023071 | 0.0019567 | 0.017517 | 0.0047594 | 0.015584 | -0.0087843 | -0.0040333 | -0.19684 | -0.07782 | -0.34332 | -0.21973 | -0.091553 | -0.19684 | -0.13733 | -0.11444 | 0.036621 | -0.33417 | -0.16022 | 0.004578 | -0.13733 | -0.059509 | -0.041199 | -122.8271 | -122.9691 | 0.21057 | 0.16479 | 0.10529 | 0.20599 | 0.14648 | -0.032043 | -122.7127 | -122.9095 | 0.3067 | 0.24261 | 0.16479 | 0.27466 | 0.19684 | 0.25177 | 0.1236 | 0.33875 | 0.17395 | 0.2655 | 0.37079 | 0.2243 | 0.33875 | -123.0927 | -123.0835 | 0.082397 | 0.14191 | 0.10529 | 0.18768
5110.1719 | 123.0972 | -0.30212 | 122.731 | -0.12161 | -0.0015145 | 0.013106 | 0.0077353 | -0.0013352 | -0.0022943 | -0.0018414 | 0.02002 | 0.00067495 | 0.016235 | 0.0034778 | 0.016865 | -0.0087843 | 0.00066654 | -0.20142 | -0.07782 | -0.33417 | -0.20142 | -0.064087 | -0.17853 | -0.12817 | -0.10529 | 0.041199 | -0.32501 | -0.13733 | -0.022888 | -0.12817 | -0.059509 | -0.032043 | -122.8088 | -122.9324 | 0.23804 | 0.17395 | 0.1236 | 0.20599 | 0.15564 | -0.022888 | -122.6898 | -122.8683 | 0.27924 | 0.24261 | 0.17395 | 0.2655 | 0.19684 | 0.27008 | 0.13275 | 0.30212 | 0.18768 | 0.25635 | 0.36621 | 0.2243 | 0.34332 | -123.0652 | -123.056 | 0.10071 | 0.16479 | 0.10071 | 0.19684
5111.1719 | 123.1247 | -0.29297 | 122.7448 | -0.091095 | -0.0010873 | 0.015456 | 0.0090169 | 0.00037377 | -0.00037171 | -0.00013241 | 0.032227 | 0.0017431 | 0.017731 | 0.0013416 | 0.016011 | -0.0085705 | -0.00040166 | -0.2243 | -0.068665 | -0.33417 | -0.19684 | -0.068665 | -0.18768 | -0.14648 | -0.082397 | 0.041199 | -0.33417 | -0.16479 | -0.013733 | -0.14648 | -0.050354 | -0.041198 | -122.8134 | -122.9416 | 0.2243 | 0.14648 | 0.10529 | 0.18768 | 0.14648 | -0.041198 | -122.7036 | -122.9095 | 0.27924 | 0.24261 | 0.14648 | 0.28381 | 0.18768 | 0.2655 | 0.13733 | 0.32043 | 0.16937 | 0.2655 | 0.37537 | 0.2243 | 0.33417 | -123.0789 | -123.0789 | 0.096131 | 0.12817 | 0.068665 | 0.21057
5112.1719 | 123.1064 | -0.32501 | 122.7539 | -0.091095 | 0.00019446 | 0.015028 | 0.0085897 | 0.00016017 | -0.0042169 | 0.0015766 | -0.010498 | 0.0015295 | 0.01474 | 0.0032642 | 0.018788 | -0.0075025 | -0.00061526 | -0.21973 | -0.07782 | -0.32959 | -0.21057 | -0.073242 | -0.20599 | -0.13733 | -0.09613 | 0.045776 | -0.34332 | -0.15106 | -0.027466 | -0.13733 | -0.064087 | -0.004578 | -122.8317 | -122.9645 | 0.25177 | 0.18768 | 0.11902 | 0.19226 | 0.1236 | -0.018311 | -122.7081 | -122.905 | 0.29755 | 0.26093 | 0.18768 | 0.27924 | 0.20599 | 0.25635 | 0.11902 | 0.31586 | 0.19226 | 0.25177 | 0.3891 | 0.24719 | 0.37079 | -123.0835 | -123.0972 | 0.11444 | 0.17395 | 0.10529 | 0.22888
5113.1719 | 123.0606 | -0.30212 | 122.7493 | -0.052948 | 0.0010489 | 0.014815 | 0.0081625 | 0.0012284 | -0.0014399 | -0.0035504 | -0.03186 | 0.0017431 | 0.015167 | 0.005614 | 0.01772 | -0.0077161 | 0.0013073 | -0.20599 | -0.073242 | -0.34332 | -0.22888 | -0.11902 | -0.22888 | -0.16479 | -0.14648 | 0.027466 | -0.3479 | -0.18768 | -0.054932 | -0.19226 | -0.09613 | -0.041199 | -122.8226 | -122.9782 | 0.18311 | 0.13733 | 0.073242 | 0.17853 | 0.11444 | -0.045776 | -122.7219 | -122.937 | 0.24719 | 0.20599 | 0.10986 | 0.25177 | 0.15564 | 0.2243 | 0.11444 | 0.29297 | 0.16022 | 0.27008 | 0.37537 | 0.22888 | 0.32959 | -123.0927 | -123.0972 | 0.073242 | 0.11444 | 0.09613 | 0.15564
5114.2344 | 123.0057 | -0.34332 | 122.7905 | -0.037689 | 0.00019446 | 0.014174 | 0.0077353 | 0.0022964 | -0.0018671 | -0.0012006 | -0.044067 | 0.0017431 | 0.014954 | 0.0081774 | 0.018147 | -0.0089979 | -0.00061526 | -0.24719 | -0.064087 | -0.36163 | -0.3067 | -0.21057 | -0.29297 | -0.23346 | -0.25177 | 0.054932 | -0.37079 | -0.25177 | -0.11902 | -0.25635 | -0.17853 | -0.01831 | -122.8546 | -123.0972 | 0.13275 | 0.10986 | 0.050354 | 0.12817 | 0.068664 | -0.027466 | -122.7356 | -123.0423 | 0.2243 | 0.16479 | 0.086975 | 0.19226 | 0.11444 | 0.15106 | 0.054931 | 0.25177 | 0.11902 | 0.29755 | 0.42572 | 0.27924 | 0.39825 | -123.1522 | -123.1613 | 0.036621 | 0.091553 | 0.096131 | 0.091553
5115.1719 | 123.1247 | -0.32501 | 122.7081 | -0.10635 | 0.0014761 | 0.015028 | 0.0068807 | 0.00016017 | -0.0014399 | -0.003764 | 0.016968 | 0.0025975 | 0.016663 | -0.0010084 | 0.018788 | -0.0094251 | -0.0070239 | -0.21973 | -0.068665 | -0.35706 | -0.22888 | -0.086975 | -0.20599 | -0.13733 | -0.10529 | 0.027466 | -0.34332 | -0.13275 | 0.022888 | -0.10986 | -0.050354 | -0.032044 | -122.7768 | -122.937 | 0.23804 | 0.18768 | 0.11902 | 0.21973 | 0.15106 | -0.018311 | -122.6807 | -122.8409 | 0.3479 | 0.27466 | 0.21515 | 0.29297 | 0.23346 | 0.27008 | 0.12817 | 0.36621 | 0.21057 | 0.28839 | 0.37079 | 0.25635 | 0.35248 | -123.0652 | -123.0515 | 0.09613 | 0.19226 | 0.10529 | 0.21973
5116.1719 | 123.1384 | -0.31128 | 122.731 | -0.083466 | -0.00044654 | 0.014601 | 0.0068807 | -5.343e-05 | -0.0010125 | -0.0024822 | 0.010864 | 0.0017431 | 0.016449 | 0.003905 | 0.017079 | -0.0075025 | 0.0015209 | -0.22888 | -0.082397 | -0.3479 | -0.23346 | -0.11902 | -0.2243 | -0.15564 | -0.12817 | 0.036621 | -0.33875 | -0.13275 | -0.009155 | -0.12817 | -0.054932 | -0.036621 | -122.8134 | -122.9645 | 0.19226 | 0.15564 | 0.086975 | 0.19226 | 0.1236 | -0.027466 | -122.6944 | -122.8638 | 0.30212 | 0.25635 | 0.1831 | 0.28381 | 0.21057 | 0.22888 | 0.11444 | 0.32959 | 0.20599 | 0.2655 | 0.37537 | 0.22888 | 0.3479 | -123.0789 | -123.0698 | 0.07782 | 0.17853 | 0.082397 | 0.1831
5117.1719 | 123.1293 | -0.29297 | 122.7356 | -0.083466 | -0.00066014 | 0.014815 | 0.0068807 | -5.343e-05 | -0.0010125 | -0.002696 | -0.0013428 | 0.00088875 | 0.016876 | 0.001128 | 0.018147 | -0.0087843 | 2.554e-05 | -0.24261 | -0.09613 | -0.32959 | -0.24261 | -0.13275 | -0.23346 | -0.16479 | -0.17395 | 0.027466 | -0.36163 | -0.16022 | -0.022888 | -0.15564 | -0.064087 | -0.036621 | -122.8317 | -122.9782 | 0.16022 | 0.12817 | 0.05951 | 0.16479 | 0.096131 | -0.068664 | -122.7081 | -122.8958 | 0.27008 | 0.22888 | 0.13733 | 0.29755 | 0.20599 | 0.19684 | 0.086975 | 0.33874 | 0.20142 | 0.23346 | 0.3891 | 0.19684 | 0.32043 | -123.0652 | -123.0972 | 0.050354 | 0.13275 | 0.050354 | 0.11902
5118.1719 | 123.1293 | -0.3067 | 122.7402 | -0.091095 | -0.00023294 | 0.016524 | 0.0066671 | 0.00037377 | -0.0016535 | -0.0012006 | -0.0013428 | 0.00024775 | 0.015594 | 0.0049732 | 0.018788 | -0.0062207 | -0.0012561 | -0.25635 | -0.059509 | -0.35248 | -0.24719 | -0.14191 | -0.26093 | -0.17395 | -0.16022 | 0.032043 | -0.3479 | -0.16937 | -0.022888 | -0.16479 | -0.068665 | -0.045776 | -122.7997 | -122.9874 | 0.16479 | 0.13275 | 0.045777 | 0.17853 | 0.091553 | -0.041198 | -122.7081 | -122.9095 | 0.28381 | 0.23804 | 0.14191 | 0.27924 | 0.1831 | 0.21057 | 0.10529 | 0.32501 | 0.17853 | 0.29297 | 0.37994 | 0.24719 | 0.33874 | -123.0927 | -123.0881 | 0.05951 | 0.13733 | 0.050354 | 0.14648
5119.1719 | 123.0103 | -0.34332 | 122.7722 | -0.060578 | -0.0013009 | 0.015883 | 0.0098715 | -0.00026703 | 0.00048269 | 0.0028582 | -0.12036 | 0.0025975 | 0.01709 | 0.00070062 | 0.017079 | -0.0047253 | -0.0010425 | -0.27008 | -0.054932 | -0.39368 | -0.31586 | -0.22888 | -0.3479 | -0.27466 | -0.27008 | 0.068665 | -0.35706 | -0.2655 | -0.17395 | -0.3067 | -0.16022 | -0.050354 | -122.8271 | -123.0881 | 0.11444 | 0.068665 | -0.004577 | 0.11902 | 0.045777 | -0.013733 | -122.7036 | -123.0377 | 0.16937 | 0.18311 | 0.036621 | 0.19684 | 0.050354 | 0.16479 | 0.07782 | 0.18311 | 0.091553 | 0.33875 | 0.42572 | 0.28839 | 0.41199 | -123.1659 | -123.1293 | 0.027466 | 0.07782 | 0.073242 | 0.073242
5120.1719 | 123.1201 | -0.30212 | 122.7127 | -0.10635 | -0.00044654 | 0.015456 | 0.0058127 | 0.0027238 | 0.00026909 | 0.0015766 | 0.013916 | 0.0030249 | 0.015167 | 0.0041186 | 0.017934 | -0.0075025 | -0.0031787 | -0.24719 | -0.073242 | -0.33875 | -0.25177 | -0.1236 | -0.23804 | -0.16937 | -0.15564 | 0.032043 | -0.35706 | -0.15106 | -0.009155 | -0.14191 | -0.064087 | -0.036621 | -122.7859 | -122.9645 | 0.17853 | 0.13275 | 0.064087 | 0.16937 | 0.10071 | -0.054932 | -122.6807 | -122.8638 | 0.29297 | 0.23804 | 0.16022 | 0.29297 | 0.21515 | 0.21515 | 0.086975 | 0.3479 | 0.20599 | 0.2655 | 0.3891 | 0.22888 | 0.33417 | -123.0515 | -123.0698 | 0.050354 | 0.15106 | 0.054932 | 0.14648
5121.1719 | 123.143 | -0.32501 | 122.7402 | -0.052948 | -0.00023294 | 0.015456 | 0.0079489 | -0.0017624 | -0.0012261 | -0.0035504 | 0.013916 | 0.0013159 | 0.017731 | 5.9824e-05 | 0.017293 | -0.0068615 | -0.0042469 | -0.25635 | -0.086975 | -0.34332 | -0.25635 | -0.15106 | -0.25177 | -0.16937 | -0.16479 | 0.045776 | -0.36163 | -0.16937 | -0.032043 | -0.15564 | -0.086975 | -0.018311 | -122.8271 | -122.9965 | 0.17395 | 0.15564 | 0.073242 | 0.17395 | 0.091553 | -0.036621 | -122.6944 | -122.9095 | 0.29297 | 0.23804 | 0.16937 | 0.27466 | 0.20599 | 0.19226 | 0.086975 | 0.32959 | 0.19226 | 0.25635 | 0.40741 | 0.23804 | 0.37079 | -123.0835 | -123.1018 | 0.068664 | 0.15564 | 0.068664 | 0.16022
5122.1719 | 123.0972 | -0.32044 | 122.7081 | -0.11398 | -0.00044654 | 0.013747 | 0.0064535 | -0.0032578 | -0.0010125 | -0.0041912 | 0.010864 | 0.0021703 | 0.016663 | 0.0066822 | 0.017293 | -0.0075025 | 0.00066654 | -0.27008 | -0.064087 | -0.3479 | -0.25635 | -0.16479 | -0.27008 | -0.18768 | -0.18768 | 0.027466 | -0.35706 | -0.1831 | -0.036621 | -0.17395 | -0.082397 | -0.027465 | -122.7722 | -122.9645 | 0.15564 | 0.13275 | 0.050354 | 0.16022 | 0.077819 | -0.036621 | -122.6807 | -122.8912 | 0.28381 | 0.23804 | 0.14649 | 0.27466 | 0.18311 | 0.1831 | 0.091552 | 0.32043 | 0.17395 | 0.28381 | 0.38452 | 0.25635 | 0.3479 | -123.056 | -123.0652 | 0.064087 | 0.13733 | 0.050354 | 0.13275
5123.1719 | 123.0881 | -0.30212 | 122.7219 | -0.13687 | -0.00023294 | 0.016096 | 0.0062399 | 0.00016017 | -0.0020807 | -0.0014142 | -0.0043946 | 0.0030249 | 0.015808 | 0.0032642 | 0.017934 | -0.0072889 | 0.0015209 | -0.26093 | -0.059509 | -0.3479 | -0.2655 | -0.16479 | -0.25177 | -0.20599 | -0.21515 | 0.027466 | -0.35706 | -0.1831 | -0.050354 | -0.17853 | -0.086975 | -0.045776 | -122.7814 | -122.9874 | 0.13733 | 0.09613 | 0.050354 | 0.14191 | 0.09613 | -0.054932 | -122.6944 | -122.905 | 0.25177 | 0.21515 | 0.1236 | 0.27008 | 0.17853 | 0.1831 | 0.082397 | 0.3067 | 0.17395 | 0.28839 | 0.38452 | 0.24261 | 0.32959 | -123.0698 | -123.0789 | 0.036621 | 0.11902 | 0.041199 | 0.086975
5124.1719 | 123.024 | -0.31128 | 122.7722 | -0.060578 | -0.00087374 | 0.015456 | 0.0098715 | 0.00058737 | 0.0019781 | -0.002696 | -0.080688 | 0.0028113 | 0.016449 | 0.0101 | 0.018361 | -0.0077161 | -0.00082886 | -0.27924 | -0.041199 | -0.37994 | -0.31586 | -0.23804 | -0.3067 | -0.24719 | -0.24719 | 0.064087 | -0.38452 | -0.21973 | -0.09613 | -0.2243 | -0.13275 | -0.068665 | -122.8134 | -123.0881 | 0.073242 | 0.064087 | 0.004577 | 0.13275 | 0.073242 | -0.073242 | -122.7081 | -122.9919 | 0.21515 | 0.17853 | 0.086975 | 0.25177 | 0.16022 | 0.14191 | 0.064087 | 0.28839 | 0.16479 | 0.33875 | 0.44861 | 0.27008 | 0.37537 | -123.1522 | -123.1567 | -0.004578 | 0.091552 | 0.032043 | 0.064087
5125.1719 | 123.1155 | -0.32044 | 122.7356 | -0.11398 | -1.9142e-05 | 0.014815 | 0.0083761 | -0.0017624 | 0.00026909 | -0.0014142 | 0.035278 | 0.0025975 | 0.016876 | 0.0045458 | 0.018147 | -0.0053663 | 0.00045294 | -0.2655 | -0.050354 | -0.34332 | -0.25635 | -0.16937 | -0.27466 | -0.18768 | -0.20599 | 0.045776 | -0.3479 | -0.1831 | -0.041199 | -0.17853 | -0.086975 | -0.022888 | -122.7859 | -122.9919 | 0.15106 | 0.13275 | 0.045777 | 0.15564 | 0.068665 | -0.027465 | -122.6898 | -122.9187 | 0.27924 | 0.23346 | 0.14191 | 0.26092 | 0.16937 | 0.17395 | 0.086975 | 0.3067 | 0.16479 | 0.29297 | 0.39368 | 0.27008 | 0.36621 | -123.0789 | -123.0835 | 0.064087 | 0.13733 | 0.054932 | 0.11444
5126.1719 | 123.0469 | -0.32501 | 122.7173 | -0.083466 | -0.00066014 | 0.016524 | 0.0075217 | 0.0012284 | -0.0022943 | 0.0017902 | 0.016968 | 0.0017431 | 0.016876 | 0.011595 | 0.017293 | -0.0075025 | -0.0040333 | -0.27924 | -0.064087 | -0.35248 | -0.28381 | -0.16479 | -0.29755 | -0.20142 | -0.21515 | 0.032043 | -0.36163 | -0.18768 | -0.064087 | -0.20142 | -0.11444 | -0.027466 | -122.7814 | -123.0011 | 0.16022 | 0.1236 | 0.027466 | 0.15106 | 0.054932 | -0.036621 | -122.6852 | -122.905 | 0.26093 | 0.21057 | 0.1236 | 0.24719 | 0.16022 | 0.18768 | 0.068665 | 0.29755 | 0.17395 | 0.28839 | 0.39368 | 0.26093 | 0.35706 | -123.0698 | -123.0789 | 0.041199 | 0.13733 | 0.045776 | 0.10986
5127.1719 | 123.0698 | -0.31586 | 122.7402 | -0.068207 | -0.0023691 | 0.012892 | 0.0075217 | -0.0013352 | -0.0020807 | 0.00072199 | 0.0078126 | 0.0013159 | 0.014526 | 0.0019824 | 0.018361 | -0.0089979 | -0.0027515 | -0.26093 | -0.07782 | -0.35248 | -0.28839 | -0.1831 | -0.27466 | -0.21057 | -0.2243 | 0.022888 | -0.34332 | -0.19226 | -0.073242 | -0.20599 | -0.10071 | -0.036621 | -122.818 | -123.0286 | 0.13275 | 0.10529 | 0.041199 | 0.14191 | 0.07782 | -0.027466 | -122.7173 | -122.9324 | 0.24261 | 0.21515 | 0.10986 | 0.24261 | 0.13733 | 0.16937 | 0.064087 | 0.27008 | 0.15106 | 0.27466 | 0.36621 | 0.23804 | 0.33875 | -123.0927 | -123.0835 | 0.027466 | 0.1236 | 0.054932 | 0.091553
5128.1719 | 123.0698 | -0.3067 | 122.7173 | -0.075836 | -0.00087374 | 0.014601 | 0.0092307 | -0.00090783 | -0.0018671 | -0.0022686 | 0.001709 | 0.0017431 | 0.016663 | 0.0019824 | 0.019643 | -0.0060071 | 0.00023934 | -0.2655 | -0.082397 | -0.36621 | -0.28381 | -0.16937 | -0.28381 | -0.20142 | -0.2243 | 0.032043 | -0.35706 | -0.19226 | -0.073242 | -0.21515 | -0.11444 | -0.059509 | -122.7997 | -123.0011 | 0.13733 | 0.10529 | 0.022889 | 0.16479 | 0.082398 | -0.050354 | -122.6852 | -122.9095 | 0.23346 | 0.19226 | 0.091553 | 0.24261 | 0.14191 | 0.19684 | 0.082398 | 0.28381 | 0.16479 | 0.28381 | 0.3891 | 0.2243 | 0.33874 | -123.0835 | -123.0743 | 0.022889 | 0.11444 | 0.041199 | 0.082398
5129.1719 | 123.0057 | -0.31128 | 122.7631 | -0.060578 | -0.00087374 | 0.015883 | 0.012008 | -0.0021896 | -0.0018671 | -0.00034601 | -0.08374 | 0.0013159 | 0.014526 | 0.011168 | 0.016438 | -0.0068615 | -0.0044605 | -0.24261 | -0.054932 | -0.40283 | -0.3067 | -0.1831 | -0.28839 | -0.22888 | -0.20599 | 0.059509 | -0.37537 | -0.21515 | -0.11444 | -0.24719 | -0.11902 | -0.091553 | -122.818 | -123.0698 | 0.12817 | 0.082397 | 0.022888 | 0.17395 | 0.11444 | -0.064087 | -122.7036 | -122.9782 | 0.19684 | 0.19226 | 0.064087 | 0.25635 | 0.12817 | 0.21973 | 0.09613 | 0.26092 | 0.16022 | 0.3479 | 0.43487 | 0.25635 | 0.37079 | -123.1659 | -123.1384 | 0.004577 | 0.09613 | 0.068664 | 0.10528
5130.1719 | 123.0698 | -0.31586 | 122.7356 | -0.11398 | -0.00066014 | 0.016737 | 0.0085897 | 0.00037377 | -0.0014399 | -0.002055 | -0.0043946 | 0.0017431 | 0.017517 | 0.00027342 | 0.01772 | -0.010066 | -0.00018806 | -0.2655 | -0.059509 | -0.36163 | -0.28839 | -0.19226 | -0.28381 | -0.20142 | -0.22888 | 0.032043 | -0.36621 | -0.20599 | -0.068665 | -0.21515 | -0.11444 | -0.045776 | -122.7951 | -123.024 | 0.1236 | 0.11444 | 0.032044 | 0.16022 | 0.07782 | -0.050354 | -122.7036 | -122.9416 | 0.24719 | 0.20142 | 0.10071 | 0.25177 | 0.15106 | 0.16937 | 0.073242 | 0.29755 | 0.16022 | 0.30212 | 0.39825 | 0.25635 | 0.3479 | -123.0972 | -123.1018 | 0.027466 | 0.10986 | 0.050354 | 0.086975
5131.1719 | 123.0652 | -0.29297 | 122.7585 | -0.15976 | 0.00062166 | 0.015883 | 0.0064535 | 0.00080117 | -0.00058531 | -0.0014142 | -0.03186 | 0.0040929 | 0.017303 | 0.0036914 | 0.01772 | -0.0085705 | -0.0027515 | -0.24261 | -0.10986 | -0.32959 | -0.24719 | -0.11902 | -0.2655 | -0.17853 | -0.15106 | 0.022888 | -0.3479 | -0.16479 | -0.054932 | -0.17853 | -0.086975 | -0.036621 | -122.8683 | -123.0057 | 0.17395 | 0.11444 | 0.027466 | 0.15106 | 0.064087 | -0.054931 | -122.7356 | -122.9233 | 0.23804 | 0.20599 | 0.11444 | 0.26092 | 0.16937 | 0.21057 | 0.082398 | 0.29297 | 0.1831 | 0.21973 | 0.37079 | 0.18311 | 0.31586 | -123.0881 | -123.1064 | 0.045777 | 0.12817 | 0.050354 | 0.14191
5132.1719 | 123.1155 | -0.30212 | 122.7356 | -0.091095 | 0.0014761 | 0.015028 | 0.0085897 | 0.00037377 | 0.00091009 | 0.0026446 | -0.050171 | 0.0017431 | 0.015594 | -0.00015378 | 0.017079 | -0.0055799 | 0.0015209 | -0.2243 | -0.091553 | -0.35248 | -0.24261 | -0.11902 | -0.27008 | -0.17853 | -0.14648 | 0.027466 | -0.34332 | -0.13275 | -0.036621 | -0.16937 | -0.068665 | -0.050354 | -122.8271 | -122.9782 | 0.18311 | 0.1236 | 0.032043 | 0.17395 | 0.082397 | -0.041199 | -122.7081 | -122.8683 | 0.2655 | 0.23346 | 0.13275 | 0.27466 | 0.17395 | 0.23346 | 0.10986 | 0.3067 | 0.21057 | 0.26093 | 0.37079 | 0.21057 | 0.32959 | -123.0881 | -123.0789 | 0.059509 | 0.16937 | 0.07782 | 0.15564
5133.1719 | 123.1293 | -0.28381 | 122.7219 | -0.1445 | 0.00019446 | 0.015028 | 0.0088033 | -0.0013352 | 0.0030463 | 8.1188e-05 | -0.041016 | 0.0023839 | 0.018799 | 0.0034778 | 0.018147 | -0.0072889 | 0.0017345 | -0.22888 | -0.086975 | -0.34332 | -0.24719 | -0.1236 | -0.26093 | -0.19684 | -0.13275 | 0.041199 | -0.35706 | -0.14648 | -0.045776 | -0.16937 | -0.068665 | -0.05951 | -122.8088 | -122.9691 | 0.16022 | 0.086975 | 0.022888 | 0.14648 | 0.082398 | -0.073243 | -122.6807 | -122.8683 | 0.23804 | 0.21515 | 0.11444 | 0.28839 | 0.18768 | 0.21973 | 0.096131 | 0.31128 | 0.21057 | 0.25635 | 0.39825 | 0.19684 | 0.32501 | -123.0652 | -123.0789 | 0.036621 | 0.13733 | 0.054931 | 0.15106
5134.1719 | 123.0927 | -0.29755 | 122.7448 | -0.045319 | -0.0017281 | 0.015456 | 0.0090169 | -0.003685 | -0.0016535 | -0.00013241 | 0.001709 | 0.00088875 | 0.015808 | 0.00070062 | 0.01772 | -0.0053663 | -0.0036059 | -0.22888 | -0.086975 | -0.33417 | -0.22888 | -0.10986 | -0.21973 | -0.17395 | -0.14648 | 0.027466 | -0.35706 | -0.16937 | -0.045776 | -0.15564 | -0.091553 | -0.036621 | -122.8317 | -122.9736 | 0.18768 | 0.1236 | 0.077819 | 0.16022 | 0.11444 | -0.05951 | -122.7173 | -122.9141 | 0.25177 | 0.20599 | 0.14191 | 0.2655 | 0.20142 | 0.2243 | 0.10528 | 0.31128 | 0.18768 | 0.24719 | 0.38452 | 0.21057 | 0.32501 | -123.0789 | -123.1018 | 0.068664 | 0.12817 | 0.068664 | 0.15106
5135.1719 | 123.1293 | -0.29297 | 122.6898 | -0.13687 | -0.00087374 | 0.015883 | 0.0090169 | -0.0011214 | 0.0011237 | 8.1188e-05 | -0.028809 | 0.0017431 | 0.017303 | 0.0026232 | 0.018147 | -0.0079297 | -0.0038197 | -0.23346 | -0.10529 | -0.33417 | -0.24719 | -0.12817 | -0.25635 | -0.17853 | -0.14648 | 0.027466 | -0.33417 | -0.16022 | -0.045776 | -0.17853 | -0.082397 | -0.041198 | -122.7951 | -122.937 | 0.16479 | 0.11444 | 0.036621 | 0.15564 | 0.077819 | -0.041198 | -122.6624 | -122.85 | 0.24719 | 0.21057 | 0.11444 | 0.25177 | 0.15564 | 0.20599 | 0.086975 | 0.28839 | 0.17395 | 0.22888 | 0.36163 | 0.18768 | 0.32043 | -123.024 | -123.024 | 0.045777 | 0.13275 | 0.05951 | 0.14648
5136.1719 | 123.1247 | -0.28839 | 122.7264 | -0.10635 | 0.00019446 | 0.015669 | 0.0060263 | 0.00037377 | 0.0028327 | -0.0031232 | -0.025757 | 0.0038793 | 0.016449 | 0.0041186 | 0.017293 | -0.0057935 | -0.0031787 | -0.22888 | -0.07782 | -0.34332 | -0.24261 | -0.12817 | -0.26093 | -0.19226 | -0.14648 | 0.018311 | -0.35706 | -0.15106 | -0.041199 | -0.17395 | -0.068665 | -0.054932 | -122.8043 | -122.9691 | 0.16022 | 0.09613 | 0.027466 | 0.15106 | 0.082398 | -0.068665 | -122.7081 | -122.8775 | 0.24719 | 0.21973 | 0.11444 | 0.28839 | 0.18311 | 0.21515 | 0.10071 | 0.31586 | 0.20599 | 0.2655 | 0.37537 | 0.21057 | 0.3067 | -123.0698 | -123.0835 | 0.045776 | 0.13733 | 0.059509 | 0.14191
5137.1719 | 123.1338 | -0.29297 | 122.7127 | -0.060578 | -0.0019417 | 0.017378 | 0.0075217 | -0.0030442 | -0.0035761 | -0.002055 | -0.053223 | 0.0030249 | 0.015167 | 0.003905 | 0.017506 | -0.0066479 | 0.00066654 | -0.22888 | -0.09613 | -0.35248 | -0.21515 | -0.11902 | -0.25177 | -0.18768 | -0.13275 | 0.027466 | -0.35248 | -0.14191 | -0.045776 | -0.17395 | -0.068665 | -0.059509 | -122.8088 | -122.9279 | 0.17395 | 0.10529 | 0.041199 | 0.1648 | 0.10071 | -0.059509 | -122.6852 | -122.8546 | 0.24719 | 0.2243 | 0.11902 | 0.28381 | 0.17853 | 0.23346 | 0.13733 | 0.3067 | 0.21057 | 0.25635 | 0.37994 | 0.19684 | 0.32043 | -123.0652 | -123.0652 | 0.07782 | 0.15106 | 0.064087 | 0.16022
5138.1719 | 123.111 | -0.29755 | 122.7127 | -0.13687 | -0.0010873 | 0.017805 | 0.0094443 | -0.0026168 | 0.00091009 | -0.00098701 | -0.062378 | 0.0019567 | 0.015167 | 0.0047594 | 0.017293 | -0.0051527 | -0.00061526 | -0.23804 | -0.086975 | -0.36621 | -0.24719 | -0.14191 | -0.27008 | -0.19226 | -0.16479 | 0.018311 | -0.35248 | -0.13733 | -0.045776 | -0.17853 | -0.073242 | -0.068665 | -122.7997 | -122.9599 | 0.15564 | 0.10528 | 0.027465 | 0.17395 | 0.09613 | -0.054932 | -122.6944 | -122.85 | 0.25177 | 0.2243 | 0.11902 | 0.27924 | 0.17395 | 0.2243 | 0.11902 | 0.3067 | 0.21515 | 0.27924 | 0.37079 | 0.21057 | 0.31586 | -123.0789 | -123.0652 | 0.050354 | 0.16022 | 0.059509 | 0.13275
5139.1719 | 123.0423 | -0.33417 | 122.7264 | -0.083466 | 0.00040806 | 0.013319 | 0.0092307 | 0.0016556 | -0.0014399 | -0.0016278 | -0.056274 | 0.0015295 | 0.017303 | 0.0077502 | 0.019643 | -0.0053663 | 0.0019483 | -0.31586 | -0.059509 | -0.39368 | -0.3479 | -0.24719 | -0.37079 | -0.27924 | -0.27924 | 0.054932 | -0.39825 | -0.23346 | -0.13733 | -0.25177 | -0.14191 | -0.05951 | -122.7859 | -123.0743 | 0.086975 | 0.054931 | -0.036622 | 0.11444 | 0.022888 | -0.064087 | -122.6715 | -122.9599 | 0.19684 | 0.19226 | 0.082397 | 0.25635 | 0.14648 | 0.14649 | 0.045777 | 0.26092 | 0.16479 | 0.33417 | 0.45319 | 0.27466 | 0.3891 | -123.1201 | -123.1247 | -0.013733 | 0.10071 | 0.01831 | 0.054931
5140.1719 | 123.1293 | -0.30212 | 122.6944 | -0.15213 | 0.0027579 | 0.017805 | 0.0092307 | 0.0016556 | 0.00048269 | 0.00072199 | -0.044067 | 0.00088875 | 0.015594 | 0.0015552 | 0.018361 | -0.0066479 | -0.00018806 | -0.22888 | -0.09613 | -0.35248 | -0.26093 | -0.13275 | -0.27924 | -0.19226 | -0.15106 | 0.004578 | -0.3479 | -0.13733 | -0.054932 | -0.18768 | -0.068665 | -0.050354 | -122.7905 | -122.9553 | 0.16937 | 0.10986 | 0.022888 | 0.16022 | 0.073242 | -0.045776 | -122.6898 | -122.8317 | 0.24719 | 0.23346 | 0.11444 | 0.27924 | 0.16022 | 0.21973 | 0.091553 | 0.29297 | 0.21057 | 0.25635 | 0.35248 | 0.20599 | 0.3067 | -123.0469 | -123.0423 | 0.041199 | 0.16479 | 0.073242 | 0.15106
5141.2344 | 123.0881 | -0.31586 | 122.7173 | -0.098725 | -0.0019417 | 0.018233 | 0.0090169 | -0.00026703 | -0.00015811 | -0.0012006 | 0.0078126 | 0.0025975 | 0.018158 | 0.007323 | 0.01772 | -0.0068615 | -0.0021107 | -0.27466 | -0.10071 | -0.34332 | -0.29297 | -0.17853 | -0.29755 | -0.21515 | -0.21515 | 0.013733 | -0.37079 | -0.20599 | -0.07782 | -0.19226 | -0.11444 | -0.027466 | -122.818 | -123.0103 | 0.13733 | 0.10071 | 0.018311 | 0.12817 | 0.045777 | -0.054932 | -122.7036 | -122.9233 | 0.23804 | 0.20142 | 0.1236 | 0.25635 | 0.17853 | 0.16479 | 0.050354 | 0.29297 | 0.16479 | 0.24261 | 0.38452 | 0.21515 | 0.32959 | -123.0606 | -123.0881 | 0.022888 | 0.10986 | 0.041199 | 0.10071
5142.1719 | 123.1338 | -0.31128 | 122.699 | -0.098725 | 0.00040806 | 0.015669 | 0.0090169 | 0.00058737 | -0.0029351 | 0.00072199 | -0.037964 | 0.00088875 | 0.017944 | 0.0047594 | 0.018574 | -0.0066479 | 0.00045294 | -0.23804 | -0.10071 | -0.34332 | -0.23804 | -0.14191 | -0.2655 | -0.19226 | -0.15106 | 0.018311 | -0.37537 | -0.15564 | -0.050354 | -0.17853 | -0.059509 | -0.032044 | -122.7997 | -122.937 | 0.16937 | 0.11902 | 0.045776 | 0.15106 | 0.07782 | -0.064087 | -122.6807 | -122.8546 | 0.26092 | 0.25177 | 0.13275 | 0.31586 | 0.19684 | 0.20142 | 0.10529 | 0.32501 | 0.21973 | 0.24261 | 0.39368 | 0.21057 | 0.32959 | -123.0423 | -123.0743 | 0.073242 | 0.15564 | 0.073242 | 0.16022
5143.1719 | 123.0652 | -0.32501 | 122.7173 | -0.10635 | -0.00066014 | 0.016524 | 0.0085897 | -0.0011214 | -0.0029351 | -0.0018414 | -0.053223 | 0.0019567 | 0.016235 | 0.0026232 | 0.018361 | -0.0070753 | -0.0033923 | -0.3067 | -0.07782 | -0.3891 | -0.32044 | -0.22888 | -0.33875 | -0.25177 | -0.23346 | 0.027466 | -0.37537 | -0.17395 | -0.07782 | -0.21973 | -0.082397 | -0.064087 | -122.7951 | -123.0377 | 0.09613 | 0.073242 | -0.013733 | 0.13733 | 0.050354 | -0.050354 | -122.6898 | -122.8912 | 0.24719 | 0.24262 | 0.10529 | 0.29297 | 0.15564 | 0.16022 | 0.068664 | 0.29755 | 0.20142 | 0.31128 | 0.40283 | 0.24719 | 0.35248 | -123.1064 | -123.0927 | 0.004577 | 0.15106 | 0.01831 | 0.091553
5144.1719 | 123.0652 | -0.32959 | 122.7402 | -0.12924 | 0.0023307 | 0.015242 | 0.01094 | -0.00069423 | -0.0012261 | 0.0011494 | -0.068481 | 0.0028113 | 0.018158 | 0.0030506 | 0.017293 | -0.0057935 | 0.00088014 | -0.3067 | -0.064087 | -0.39368 | -0.3479 | -0.23346 | -0.37994 | -0.27008 | -0.27008 | 0.036621 | -0.36163 | -0.20599 | -0.12817 | -0.25177 | -0.13275 | -0.064087 | -122.8043 | -123.0881 | 0.096131 | 0.059509 | -0.050354 | 0.1236 | 0.013733 | -0.032043 | -122.7036 | -122.9462 | 0.20142 | 0.19684 | 0.07782 | 0.22888 | 0.10986 | 0.16022 | 0.045777 | 0.23346 | 0.15564 | 0.32959 | 0.39825 | 0.2655 | 0.36621 | -123.1338 | -123.1018 | -0.01831 | 0.1236 | 0.022888 | 0.059509
5145.1719 | 123.0194 | -0.33875 | 122.7173 | -0.014801 | 0.00019446 | 0.014815 | 0.010512 | 0.0033646 | -0.0014399 | 0.002431 | -0.056274 | 0.0021703 | 0.01709 | 0.0077502 | 0.016865 | -0.0062207 | 0.00023934 | -0.32044 | -0.073242 | -0.40283 | -0.37079 | -0.27466 | -0.39368 | -0.3067 | -0.29755 | 0.045776 | -0.39368 | -0.24261 | -0.15106 | -0.28381 | -0.15106 | -0.064087 | -122.7905 | -123.0881 | 0.064087 | 0.032043 | -0.054932 | 0.09613 | 0.009155 | -0.054932 | -122.6715 | -122.9599 | 0.18768 | 0.18768 | 0.054932 | 0.24261 | 0.10986 | 0.12817 | 0.032043 | 0.24261 | 0.15106 | 0.32959 | 0.43945 | 0.2655 | 0.38452 | -123.1201 | -123.111 | -0.032044 | 0.09613 | 0.01831 | 0.041199
5146.1719 | 122.9965 | -0.36163 | 122.731 | -0.075836 | -0.0017281 | 0.013319 | 0.0096579 | 0.0037918 | -0.0018671 | 0.0015766 | -0.08374 | 0.0019567 | 0.01709 | 0.0045458 | 0.019856 | -0.0079297 | 0.00023934 | -0.31128 | -0.064087 | -0.39825 | -0.40283 | -0.31586 | -0.39368 | -0.32044 | -0.35248 | 0.045776 | -0.39825 | -0.27466 | -0.1831 | -0.32501 | -0.18768 | -0.036621 | -122.7951 | -123.1339 | 0.045776 | 0.041198 | -0.032044 | 0.077819 | 0.004577 | -0.036621 | -122.6852 | -123.0057 | 0.17853 | 0.17395 | 0.036621 | 0.21057 | 0.073242 | 0.082397 | -0.004578 | 0.21515 | 0.1236 | 0.33417 | 0.44403 | 0.29755 | 0.40741 | -123.1293 | -123.1293 | -0.041199 | 0.086975 | 0.050354 | 0.009155
5147.1719 | 123.0286 | -0.36621 | 122.7768 | -0.075836 | -0.0010873 | 0.015669 | 0.0096579 | -0.0030442 | -0.00079891 | -0.0029096 | -0.062378 | 0.0040929 | 0.016449 | 0.0075366 | 0.018788 | -0.0070753 | -0.0018971 | -0.32501 | -0.073242 | -0.39825 | -0.37994 | -0.28839 | -0.39825 | -0.3067 | -0.32501 | 0.032043 | -0.41199 | -0.27466 | -0.17853 | -0.32044 | -0.16937 | -0.032043 | -122.85 | -123.1567 | 0.07782 | 0.059509 | -0.032043 | 0.091552 | 0 | -0.045776 | -122.7448 | -123.0515 | 0.18768 | 0.19684 | 0.045776 | 0.24261 | 0.091552 | 0.10986 | 0.01831 | 0.23346 | 0.13733 | 0.32501 | 0.44403 | 0.29297 | 0.39825 | -123.175 | -123.1888 | -0.013733 | 0.091553 | 0.041199 | 0.041199
5148.1719 | 123.0377 | -0.37079 | 122.7219 | -0.12161 | -0.00023294 | 0.015669 | 0.011581 | 0.0018692 | -0.00037171 | -0.0012006 | -0.050171 | 0.0040929 | 0.018372 | 0.002196 | 0.019643 | -0.0072889 | -0.0023243 | -0.32044 | -0.07782 | -0.3891 | -0.36163 | -0.2655 | -0.37537 | -0.3067 | -0.28381 | 0.036621 | -0.40741 | -0.23346 | -0.13733 | -0.27924 | -0.12817 | -0.01831 | -122.7997 | -123.0835 | 0.10529 | 0.064087 | -0.004577 | 0.082397 | 0.013733 | -0.036621 | -122.6852 | -122.9553 | 0.23346 | 0.24261 | 0.091553 | 0.27924 | 0.12817 | 0.1236 | 0.027466 | 0.27008 | 0.17395 | 0.31128 | 0.44403 | 0.29297 | 0.40741 | -123.111 | -123.1293 | 0.009156 | 0.13733 | 0.050354 | 0.086976
5149.1719 | 123.0469 | -0.35248 | 122.7081 | -0.083466 | -0.0013009 | 0.01396 | 0.0098715 | 0.0035782 | -0.0027215 | 0.0011494 | -0.044067 | 0.0025975 | 0.016876 | 0.0060412 | 0.020283 | -0.0077161 | 0.0015209 | -0.32044 | -0.068665 | -0.39825 | -0.3891 | -0.29297 | -0.37537 | -0.29755 | -0.3067 | 0.054932 | -0.3891 | -0.24719 | -0.16022 | -0.28381 | -0.16479 | -0.045776 | -122.7768 | -123.0972 | 0.059509 | 0.054932 | -0.022888 | 0.10071 | 0.022888 | -0.036621 | -122.6532 | -122.9553 | 0.19226 | 0.18768 | 0.068665 | 0.2243 | 0.10529 | 0.10529 | 0.009155 | 0.22888 | 0.14191 | 0.32959 | 0.44403 | 0.28381 | 0.40741 | -123.1064 | -123.0972 | -0.036621 | 0.10529 | 0.032043 | 0.045776
5150.1719 | 123.0743 | -0.33875 | 122.7356 | -0.10635 | -1.9142e-05 | 0.013319 | 0.0088033 | 0.0012284 | 5.5488e-05 | 0.00072199 | -0.03186 | 0.0032385 | 0.018372 | 0.0049732 | 0.019215 | -0.0075025 | -0.00018806 | -0.33417 | -0.086975 | -0.3891 | -0.35248 | -0.23346 | -0.36163 | -0.27466 | -0.25635 | 0.013733 | -0.38452 | -0.19226 | -0.10986 | -0.21973 | -0.11444 | -0.050354 | -122.8226 | -123.0881 | 0.10529 | 0.064087 | -0.022888 | 0.11444 | 0.027466 | -0.045776 | -122.7219 | -122.9279 | 0.22888 | 0.2243 | 0.11902 | 0.27008 | 0.16479 | 0.15564 | 0.036621 | 0.27466 | 0.19226 | 0.30212 | 0.39825 | 0.25177 | 0.35248 | -123.1247 | -123.1201 | -0.013733 | 0.14648 | 0.004578 | 0.082397
5151.1719 | 123.1064 | -0.32501 | 122.6852 | -0.11398 | 0.00062166 | 0.015456 | 0.0098715 | 0.0010148 | 0.00069649 | -0.0029096 | -0.010498 | 0.0023839 | 0.018158 | 0.007323 | 0.018361 | -0.0068615 | -0.0044605 | -0.2655 | -0.11444 | -0.37537 | -0.27466 | -0.14191 | -0.27924 | -0.21515 | -0.16937 | -0.004578 | -0.37079 | -0.1831 | -0.068665 | -0.1831 | -0.086975 | -0.050354 | -122.7997 | -122.9599 | 0.18311 | 0.10986 | 0.045776 | 0.16022 | 0.09613 | -0.045777 | -122.6898 | -122.8683 | 0.25635 | 0.23804 | 0.14191 | 0.28381 | 0.18768 | 0.23346 | 0.10071 | 0.30212 | 0.18768 | 0.26092 | 0.36621 | 0.21057 | 0.32043 | -123.0606 | -123.056 | 0.050354 | 0.14191 | 0.059509 | 0.15564
5152.1719 | 123.0515 | -0.34332 | 122.7219 | -0.068207 | -0.0015145 | 0.016524 | 0.0062399 | 0.0010148 | 0.00069649 | -0.0014142 | -0.037964 | 0.0040929 | 0.018585 | 0.002196 | 0.019215 | -0.0070753 | -0.00040166 | -0.33417 | -0.086975 | -0.40283 | -0.37994 | -0.27466 | -0.3891 | -0.29297 | -0.30212 | 0.018311 | -0.41199 | -0.23346 | -0.16022 | -0.27466 | -0.14191 | -0.059509 | -122.8088 | -123.1018 | 0.068665 | 0.050354 | -0.045776 | 0.10986 | 0.013733 | -0.068664 | -122.7036 | -122.9553 | 0.18311 | 0.20142 | 0.068665 | 0.27008 | 0.13733 | 0.12817 | 0.022888 | 0.25177 | 0.17853 | 0.31586 | 0.4303 | 0.25635 | 0.36163 | -123.1247 | -123.1338 | -0.036621 | 0.10986 | 0.009156 | 0.041199
5153.1719 | 122.9965 | -0.36621 | 122.7356 | -0.052948 | -0.0013009 | 0.016096 | 0.0083761 | 0.00080117 | -0.00015811 | 0.00093559 | -0.062378 | 0.0023839 | 0.018585 | 0.0066822 | 0.018361 | -0.0051527 | 0.0017345 | -0.33417 | -0.068665 | -0.3891 | -0.37994 | -0.31128 | -0.40741 | -0.31586 | -0.35248 | 0.036621 | -0.40283 | -0.29755 | -0.21057 | -0.34332 | -0.17853 | -0.022888 | -122.8043 | -123.1155 | 0.054932 | 0.050354 | -0.041199 | 0.073242 | -0.018311 | -0.036621 | -122.699 | -123.0331 | 0.15564 | 0.18768 | 0.022888 | 0.2243 | 0.059509 | 0.07782 | 0.009155 | 0.19226 | 0.10529 | 0.32043 | 0.43945 | 0.29755 | 0.40283 | -123.1247 | -123.1384 | -0.013733 | 0.068665 | 0.032044 | 0.013733
5154.1719 | 123.0194 | -0.37079 | 122.7585 | -0.075836 | -0.0010873 | 0.016524 | 0.0079489 | 0.0027238 | -0.00058531 | -0.0031232 | -0.059326 | 0.0032385 | 0.015381 | 0.0062548 | 0.018788 | -0.0062207 | 0.00066654 | -0.33417 | -0.07782 | -0.39368 | -0.4303 | -0.32501 | -0.42114 | -0.3479 | -0.37079 | 0.027466 | -0.40283 | -0.28839 | -0.19684 | -0.33875 | -0.18768 | -0.022888 | -122.8363 | -123.1888 | 0.045777 | 0.022889 | -0.050354 | 0.045777 | -0.027466 | -0.032043 | -122.731 | -123.0469 | 0.17395 | 0.18311 | 0.032044 | 0.21515 | 0.064087 | 0.068665 | -0.036621 | 0.20599 | 0.11444 | 0.31586 | 0.4303 | 0.29297 | 0.39825 | -123.1522 | -123.1613 | -0.059509 | 0.082398 | 0.036622 | 0
5155.1719 | 123.0927 | -0.35248 | 122.699 | -0.068207 | 0.00062166 | 0.013747 | 0.0088033 | 0.00016017 | -0.00015811 | -0.00034601 | -0.028809 | 0.0032385 | 0.018799 | 0.0068958 | 0.018788 | -0.0072889 | 0.00066654 | -0.32044 | -0.09613 | -0.41199 | -0.35706 | -0.23804 | -0.38452 | -0.27924 | -0.27924 | 0.027466 | -0.38452 | -0.21973 | -0.11444 | -0.23804 | -0.1236 | -0.059509 | -122.7951 | -123.056 | 0.11444 | 0.073242 | -0.032043 | 0.13275 | 0.027466 | -0.032043 | -122.6715 | -122.9187 | 0.23804 | 0.22888 | 0.11444 | 0.26093 | 0.14648 | 0.17395 | 0.054931 | 0.27008 | 0.16479 | 0.31586 | 0.41199 | 0.25635 | 0.37994 | -123.111 | -123.0835 | -0.004578 | 0.13275 | 0.032043 | 0.073242
5156.1719 | 123.0469 | -0.37537 | 122.7356 | -0.091095 | -0.00087374 | 0.013319 | 0.010726 | -0.0026168 | -0.0014399 | -0.00055961 | -0.056274 | 0.0047339 | 0.018799 | 0.0071094 | 0.020711 | -0.0068615 | 0.00023934 | -0.33417 | -0.07782 | -0.40741 | -0.3891 | -0.30212 | -0.41199 | -0.31586 | -0.33875 | 0.045776 | -0.39825 | -0.27466 | -0.19226 | -0.32501 | -0.17395 | -0.032044 | -122.8134 | -123.1247 | 0.073242 | 0.059509 | -0.036621 | 0.091553 | -0.004577 | -0.022888 | -122.6898 | -123.0103 | 0.1831 | 0.20142 | 0.050354 | 0.2243 | 0.073242 | 0.10529 | 0.018311 | 0.20599 | 0.1236 | 0.32959 | 0.44403 | 0.29755 | 0.42114 | -123.143 | -123.1338 | -0.013733 | 0.10071 | 0.041199 | 0.036621
5157.1719 | 123.0011 | -0.36621 | 122.7448 | -0.075836 | 0.0012625 | 0.014387 | 0.0081625 | -0.0032578 | -0.0029351 | 0.0028582 | -0.059326 | 0.0023839 | 0.018799 | 0.0028368 | 0.020497 | -0.0060071 | -0.00082886 | -0.34332 | -0.091553 | -0.40741 | -0.40741 | -0.29297 | -0.40741 | -0.32501 | -0.3479 | 0.032043 | -0.39825 | -0.28839 | -0.21515 | -0.33875 | -0.1831 | -0.041199 | -122.8363 | -123.1522 | 0.073242 | 0.041199 | -0.041199 | 0.082398 | 0 | -0.032043 | -122.7127 | -123.0331 | 0.15106 | 0.18311 | 0.027466 | 0.21515 | 0.059509 | 0.11444 | 0 | 0.1831 | 0.10986 | 0.31586 | 0.4303 | 0.27466 | 0.39825 | -123.1522 | -123.143 | -0.041199 | 0.07782 | 0.022888 | 0.018311
5158.2344 | 123.0103 | -0.36621 | 122.7264 | -0.045319 | 0.0014761 | 0.014387 | 0.0092307 | 0.00251 | -0.0022943 | 0.00029479 | -0.028809 | 0.0017431 | 0.017944 | 0.011595 | 0.017079 | -0.0077161 | -0.0012561 | -0.31128 | -0.09613 | -0.40283 | -0.3479 | -0.23804 | -0.35248 | -0.29755 | -0.27924 | 0.022888 | -0.3891 | -0.28381 | -0.16937 | -0.30212 | -0.16479 | -0.036621 | -122.8226 | -123.0743 | 0.12817 | 0.068665 | 0.013733 | 0.10529 | 0.050354 | -0.022888 | -122.7036 | -123.0103 | 0.19684 | 0.20142 | 0.064087 | 0.2243 | 0.086975 | 0.1648 | 0.054932 | 0.21973 | 0.10529 | 0.3067 | 0.41199 | 0.27008 | 0.3891 | -123.1293 | -123.1155 | 0.018311 | 0.082398 | 0.054932 | 0.086975

## Thermal Data
Fire Time | North 25 C | Cable 1
-0.0583 | 24.7127 | 22.5338
0.9417 | 24.7167 | 22.5419
1.9417 | 24.7226 | 22.5406
2.9573 | 24.7578 | 22.5211
3.9417 | 25.2215 | 22.5427
4.9417 | 26.4773 | 22.539
5.9417 | 28.5204 | 22.5352
6.9417 | 31.2227 | 22.5484
7.9417 | 34.4968 | 22.5313
8.9417 | 38.2069 | 22.5421
9.9417 | 42.2401 | 22.5399
10.9417 | 46.55 | 22.5364
11.9417 | 51.1029 | 22.5516
12.9417 | 55.9274 | 22.5363
13.9417 | 60.9459 | 22.5606
14.9417 | 66.0634 | 22.5561
15.9417 | 71.3279 | 22.5592
16.9417 | 76.7815 | 22.5648
17.9417 | 82.3348 | 22.5701
18.9417 | 87.9342 | 22.5667
19.9417 | 93.6245 | 22.5606
20.9417 | 99.376 | 22.5931
21.9417 | 105.3244 | 22.5769
22.9417 | 111.3525 | 22.6132
23.9417 | 117.3011 | 22.6297
24.9417 | 123.2779 | 22.6149
25.9417 | 129.2352 | 22.66
26.9417 | 135.1879 | 22.6767
27.9417 | 141.274 | 22.6881
28.9417 | 147.337 | 22.7253
29.9417 | 153.3254 | 22.7604
30.9417 | 159.2594 | 22.7836
31.9417 | 165.2018 | 22.7967
32.9417 | 171.2128 | 22.8434
33.9417 | 177.1565 | 22.8934
34.9417 | 183.0188 | 22.9309
35.9417 | 188.8974 | 22.9892
36.9417 | 194.9388 | 23.0437
37.9417 | 200.9009 | 23.0906
38.9417 | 206.8122 | 23.1464
39.9417 | 212.7184 | 23.2052
40.9417 | 218.6257 | 23.2763
41.9417 | 224.5491 | 23.3476
42.9417 | 230.4076 | 23.4224
43.9417 | 236.2344 | 23.5324
44.9417 | 242.051 | 23.6091
45.9417 | 247.8068 | 23.6922
46.9417 | 253.4948 | 23.8064
47.9417 | 259.2081 | 23.8719
48.9417 | 264.9228 | 24.0083
49.9417 | 270.6181 | 24.1156
50.9417 | 276.3175 | 24.2423
51.9417 | 281.9137 | 24.3856
52.9417 | 287.4316 | 24.5138
53.9417 | 292.9591 | 24.652
54.9417 | 298.5151 | 24.7917
55.9417 | 303.9135 | 24.957
56.9417 | 309.4971 | 25.1123
57.9417 | 315.0494 | 25.2834
58.9417 | 320.4777 | 25.4577
59.9417 | 325.8182 | 25.6338
60.9417 | 331.2335 | 25.8242
61.9417 | 336.7032 | 26.0407
62.9417 | 342.0004 | 26.242
63.9417 | 347.1295 | 26.456
64.9417 | 352.3309 | 26.6882
65.9417 | 356.9325 | 26.918
66.9417 | 361.1314 | 27.1433
67.9417 | 364.8861 | 27.3936
68.9417 | 368.5883 | 27.6442
69.9417 | 371.9798 | 27.9114
70.9417 | 375.2738 | 28.1903
71.9417 | 378.5676 | 28.4731
72.9417 | 381.6407 | 28.7579
73.9417 | 384.6293 | 29.0637
74.9417 | 387.3682 | 29.3594
75.9417 | 389.8895 | 29.6789
76.9417 | 392.202 | 30.0002
77.9417 | 394.3284 | 30.3244
78.9417 | 395.9375 | 30.6481
79.9417 | 397.2985 | 31.017
80.9417 | 398.4093 | 31.3651
81.9417 | 399.3917 | 31.7168
82.9417 | 400.2626 | 32.0843
83.9417 | 400.9043 | 32.4812
84.9417 | 401.2975 | 32.8631
85.9417 | 401.4778 | 33.2651
86.9417 | 401.8745 | 33.6605
87.9417 | 401.9974 | 34.0771
88.9417 | 401.9716 | 34.4899
89.9417 | 401.9424 | 34.8905
90.9417 | 401.815 | 35.3196
91.9417 | 401.6484 | 35.7602
92.9417 | 401.6201 | 36.18
93.9417 | 401.4577 | 36.6161
94.9417 | 401.4013 | 37.0516
95.9417 | 401.3564 | 37.5129
96.9417 | 401.1442 | 37.9531
97.9417 | 401.0717 | 38.396
98.9417 | 401.0266 | 38.8392
99.9417 | 401.0136 | 39.3075
100.9417 | 400.9454 | 39.7621
101.9417 | 400.8537 | 40.2159
102.9417 | 400.7647 | 40.6813
103.9417 | 400.6913 | 41.1477
104.9417 | 400.6975 | 41.6189
105.9417 | 400.8315 | 42.094
106.9417 | 400.983 | 42.5677
107.9417 | 401.1197 | 43.0332
108.9417 | 401.2481 | 43.511
109.9417 | 401.3089 | 43.9824
110.9417 | 401.4159 | 44.4742
111.9417 | 401.4527 | 44.955
112.9417 | 401.5116 | 45.4491
113.9417 | 401.5383 | 45.9174
114.9417 | 401.7866 | 46.4229
115.9417 | 401.9494 | 46.9063
116.9417 | 402.0513 | 47.3971
117.9417 | 402.158 | 47.8967
118.9417 | 402.2927 | 48.3689
119.9417 | 402.2997 | 48.885
120.9417 | 402.3826 | 49.3787
121.9417 | 402.5104 | 49.8824
122.9417 | 402.5629 | 50.3823
123.9417 | 402.6538 | 50.8805
124.9417 | 402.6827 | 51.3828
125.9417 | 402.8164 | 51.8897
126.9417 | 402.9517 | 52.3939
127.9417 | 403.1055 | 52.886
128.9417 | 403.23 | 53.4013
129.9417 | 403.3746 | 53.9008
130.9417 | 403.4011 | 54.4077
131.9417 | 403.4612 | 54.9203
132.9417 | 403.4849 | 55.4301
133.9417 | 403.5074 | 55.9359
134.9417 | 403.5556 | 56.4349
135.9417 | 403.699 | 56.9541
136.9417 | 403.7884 | 57.4701
137.9417 | 403.8768 | 57.9772
138.9417 | 403.9317 | 58.4824
139.9417 | 404.0295 | 58.9841
140.9417 | 404.1822 | 59.484
141.9417 | 404.3567 | 60.0126
142.9417 | 404.4324 | 60.5078
143.9417 | 404.5562 | 61.0124
144.9417 | 404.6463 | 61.5274
145.9417 | 404.6562 | 62.0551
146.9417 | 404.6943 | 62.5575
147.9417 | 404.7687 | 63.0747
148.9417 | 404.8301 | 63.5879
149.9417 | 404.8527 | 64.103
150.9417 | 404.9351 | 64.6129
151.9417 | 405.0018 | 65.1194
152.9417 | 405.0635 | 65.634
153.9417 | 405.0173 | 66.1419
154.9417 | 404.9685 | 66.6752
155.9417 | 404.9489 | 67.1676
156.9417 | 404.8893 | 67.697
157.9417 | 404.9439 | 68.2036
158.9417 | 404.8343 | 68.7243
159.9417 | 404.8318 | 69.2374
160.9417 | 404.8679 | 69.745
161.9417 | 404.9113 | 70.2661
162.9417 | 405.0329 | 70.7808
163.9417 | 405.0218 | 71.3022
164.9417 | 405.0914 | 71.7928
165.9417 | 405.0175 | 72.3342
166.9417 | 404.9389 | 72.8452
167.9417 | 404.8701 | 73.3746
168.9417 | 404.843 | 73.8895
169.9417 | 404.8552 | 74.4219
170.9417 | 404.9124 | 74.9322
171.9417 | 404.9474 | 75.4648
172.9417 | 405.0223 | 75.9643
173.9417 | 405.1089 | 76.4792
174.9417 | 405.0585 | 77.0125
175.9417 | 404.9569 | 77.5163
176.9417 | 404.7578 | 78.0365
177.9417 | 404.5992 | 78.5714
178.9417 | 404.5725 | 79.063
179.9417 | 404.542 | 79.5919
180.9417 | 404.4523 | 80.1133
181.9417 | 404.3818 | 80.6479
182.9417 | 404.3214 | 81.1744
183.9417 | 404.3357 | 81.6869
184.9417 | 404.4702 | 82.2298
185.9417 | 404.4135 | 82.7583
186.9417 | 404.2843 | 83.2844
187.9417 | 404.4178 | 83.807
188.9417 | 404.5321 | 84.3307
189.9417 | 404.4665 | 84.864
190.9417 | 404.4735 | 85.4031
191.9417 | 404.4943 | 85.9259
192.9417 | 404.4673 | 86.4601
193.9417 | 404.5104 | 86.9894
194.9417 | 404.4368 | 87.5255
195.9417 | 404.4268 | 88.077
196.9417 | 404.4017 | 88.6143
197.9417 | 404.302 | 89.1698
198.9417 | 404.2429 | 89.742
199.9417 | 404.2148 | 90.3174
200.9417 | 404.1886 | 90.8983
201.9417 | 404.173 | 91.4741
202.9417 | 404.0971 | 92.0842
203.9417 | 404.0882 | 92.6987
204.9417 | 404.1844 | 93.2993
205.9417 | 404.2368 | 93.9273
206.9417 | 404.2619 | 94.5571
207.9417 | 404.2343 | 95.2036
208.9417 | 404.2305 | 95.8686
209.9417 | 404.2312 | 96.5282
210.9417 | 404.2152 | 97.209
211.9417 | 404.2071 | 97.8851
212.9417 | 404.1828 | 98.5649
213.9417 | 404.2499 | 99.2624
214.9417 | 404.269 | 99.9433
215.9417 | 404.2898 | 100.6253
216.9417 | 404.2541 | 101.3003
217.9417 | 404.2595 | 101.9601
218.9417 | 404.3397 | 102.6045
219.9417 | 404.3285 | 103.2228
220.9417 | 404.0715 | 103.8095
221.9417 | 404.0487 | 104.3747
222.9417 | 403.9492 | 104.9242
223.9417 | 403.7761 | 105.468
224.9417 | 403.7575 | 106.0301
225.9417 | 403.8357 | 106.5383
226.9417 | 403.7293 | 107.0473
227.9417 | 403.5977 | 107.5436
228.9417 | 403.6862 | 108.0194
229.9417 | 403.5652 | 108.4878
230.9417 | 403.6536 | 108.9547
231.9417 | 403.6202 | 109.4035
232.9417 | 403.65 | 109.8455
233.9417 | 403.6684 | 110.2648
234.9417 | 403.7154 | 110.6965
235.9417 | 403.7952 | 111.1117
236.9573 | 403.8529 | 111.5162
237.9417 | 403.8728 | 111.9071
238.9417 | 403.8107 | 112.2914
239.9417 | 403.77 | 112.6673
240.9417 | 403.5882 | 113.0376
241.9417 | 403.4272 | 113.3923
242.9417 | 403.4088 | 113.7592
243.9417 | 403.4489 | 114.1141
244.9417 | 403.4241 | 114.4592
245.9417 | 403.4522 | 114.8275
246.9417 | 403.4534 | 115.1759
247.9417 | 403.3894 | 115.522
248.9417 | 403.3713 | 115.8565
249.9417 | 403.4023 | 116.1938
250.9417 | 403.3196 | 116.5357
251.9417 | 403.1225 | 116.8576
252.9417 | 403.1054 | 117.1954
253.9417 | 403.0963 | 117.5356
254.9417 | 403.0634 | 117.8579
255.9417 | 403.0258 | 118.2062
256.9417 | 402.8415 | 118.5443
257.9417 | 402.8226 | 118.861
258.9417 | 402.9031 | 119.2036
259.9417 | 402.9979 | 119.5481
260.9417 | 402.9824 | 119.8896
261.9417 | 402.9603 | 120.2299
262.9417 | 402.8613 | 120.5554
263.9417 | 402.9581 | 120.9217
264.9417 | 403.0439 | 121.2567
265.9417 | 403.0933 | 121.6031
266.9573 | 403.1171 | 121.9482
267.9417 | 402.9867 | 122.2934
268.9417 | 402.9361 | 122.6301
269.9417 | 403.0063 | 122.9678
270.9417 | 402.949 | 123.3053
271.9417 | 402.9412 | 123.6563
272.9417 | 402.8871 | 124.0022
273.9417 | 402.8737 | 124.3609
274.9417 | 402.8884 | 124.6983
275.9417 | 402.8792 | 125.0399
276.9417 | 402.9139 | 125.3759
277.9417 | 402.9529 | 125.7444
278.9417 | 403.0071 | 126.0594
279.9417 | 402.9889 | 126.3999
280.9417 | 402.9034 | 126.7688
281.9417 | 402.9183 | 127.0919
282.9417 | 402.9083 | 127.4434
283.9417 | 403.0016 | 127.7869
284.9417 | 402.9953 | 128.109
285.9417 | 402.9774 | 128.4643
286.9417 | 402.9176 | 128.8044
287.9417 | 402.9228 | 129.1292
288.9417 | 402.9401 | 129.4842
289.9417 | 403.0207 | 129.8176
290.9417 | 403.0817 | 130.1565
291.9417 | 403.1309 | 130.4995
292.9417 | 403.0966 | 130.8638
293.9417 | 403.0573 | 131.194
294.9417 | 403.0577 | 131.5328
295.9417 | 403.0445 | 131.8663
296.9417 | 403.1144 | 132.1849
297.9417 | 403.1559 | 132.5226
298.9417 | 403.1338 | 132.8539
299.9417 | 403.1935 | 133.1933
300.9417 | 403.1815 | 133.5236
301.9417 | 403.1911 | 133.85
302.9417 | 403.0961 | 134.1979
303.9417 | 402.9056 | 134.5391
304.9417 | 402.8776 | 134.8537
305.9417 | 402.8675 | 135.1928
306.9417 | 402.8004 | 135.4976
307.9417 | 402.754 | 135.8314
308.9417 | 402.7482 | 136.1663
309.9417 | 402.8245 | 136.5004
310.9417 | 402.7808 | 136.8233
311.9417 | 402.4786 | 137.1329
312.9417 | 402.4729 | 137.4738
313.9417 | 402.5511 | 137.8102
314.9417 | 402.493 | 138.1355
315.9417 | 402.3296 | 138.4747
316.9417 | 402.3468 | 138.808
317.9417 | 402.477 | 139.1489
318.9417 | 402.5119 | 139.4765
319.9417 | 402.5603 | 139.8273
320.9417 | 402.6019 | 140.193
321.9417 | 402.5753 | 140.5436
322.9417 | 402.5949 | 140.8834
323.9417 | 402.6179 | 141.2123
324.9417 | 402.5372 | 141.558
325.9417 | 402.5405 | 141.9084
326.9417 | 402.5471 | 142.2442
327.9417 | 402.436 | 142.6022
328.9417 | 402.4386 | 142.9538
329.9417 | 402.5845 | 143.3007
330.9417 | 402.6551 | 143.6337
331.9417 | 402.6932 | 143.9809
332.9417 | 402.7415 | 144.3557
333.9417 | 402.7727 | 144.6933
334.9417 | 402.8158 | 145.0531
335.9417 | 402.7583 | 145.3982
336.9417 | 402.6618 | 145.7733
337.9417 | 402.7793 | 146.1155
338.9417 | 402.9283 | 146.5039
339.9417 | 402.8781 | 146.8695
340.9417 | 402.8431 | 147.2342
341.9417 | 402.897 | 147.5984
342.9417 | 402.9267 | 147.9693
343.9417 | 402.8668 | 148.3295
344.9417 | 402.8276 | 148.6845
345.9417 | 402.7721 | 149.0506
346.9417 | 402.7152 | 149.4278
347.9417 | 402.6451 | 149.7917
348.9417 | 402.5582 | 150.1619
349.9417 | 402.5747 | 150.5386
350.9417 | 402.6693 | 150.9112
351.9417 | 402.624 | 151.2931
352.9417 | 402.5991 | 151.6647
353.9417 | 402.484 | 152.0358
354.9417 | 402.4485 | 152.4119
355.9417 | 402.5124 | 152.7911
356.9417 | 402.5252 | 153.1645
357.9417 | 402.438 | 153.5359
358.9417 | 402.4624 | 153.9225
359.9417 | 402.4494 | 154.3014
360.9417 | 402.5264 | 154.6858
361.9417 | 402.4844 | 155.0572
362.9417 | 402.368 | 155.4385
363.9417 | 402.3971 | 155.8268
364.9417 | 402.4157 | 156.2001
365.9417 | 402.4279 | 156.5996
366.9417 | 402.58 | 156.9752
367.9417 | 402.5374 | 157.3602
368.9417 | 402.5229 | 157.7491
369.9417 | 402.4995 | 158.1323
370.9417 | 402.4807 | 158.5288
371.9417 | 402.4314 | 158.9223
372.9417 | 402.248 | 159.3271
373.9417 | 402.1706 | 159.7031
374.9417 | 402.2817 | 160.0939
375.9417 | 402.2398 | 160.4931
376.9417 | 402.1162 | 160.9037
377.9417 | 401.987 | 161.3001
378.9417 | 401.867 | 161.6793
379.9417 | 401.7555 | 162.0796
380.9417 | 401.769 | 162.4618
381.9417 | 401.6931 | 162.8674
382.9417 | 401.6089 | 163.2444
383.9417 | 401.4118 | 163.6616
384.9417 | 401.436 | 164.027
385.9417 | 401.2236 | 164.4378
386.9573 | 401.2619 | 164.8339
387.9417 | 401.0861 | 165.2203
388.9417 | 401.0138 | 165.6206
389.9417 | 400.9042 | 166.0066
390.9417 | 400.8321 | 166.4077
391.9417 | 400.8506 | 166.7963
392.9417 | 400.7902 | 167.1851
393.9417 | 400.7908 | 167.5787
394.9417 | 400.8212 | 167.9799
395.9417 | 400.7047 | 168.3767
396.9417 | 400.7193 | 168.7413
397.9417 | 400.5847 | 169.1903
398.9417 | 400.5081 | 169.5739
399.9417 | 400.3465 | 169.9717
400.9417 | 400.3868 | 170.3694
401.9417 | 400.4328 | 170.7588
402.9417 | 400.4949 | 171.1363
403.9417 | 400.3896 | 171.5268
404.9417 | 400.3735 | 171.8981
405.9417 | 400.4269 | 172.3022
406.9417 | 400.5482 | 172.695
407.9417 | 400.6837 | 173.0758
408.9417 | 400.899 | 173.4688
409.9417 | 400.9107 | 173.8524
410.9417 | 400.8952 | 174.2394
411.9417 | 400.8867 | 174.6323
412.9417 | 400.9009 | 175.0455
413.9417 | 400.9472 | 175.4329
414.9417 | 400.9645 | 175.8154
415.9417 | 400.9025 | 176.2152
416.9417 | 400.9756 | 176.6066
417.9417 | 401.0971 | 176.9949
418.9417 | 401.2115 | 177.3721
419.9417 | 401.3179 | 177.7823
420.9417 | 401.3714 | 178.1698
421.9417 | 401.4701 | 178.5599
422.9417 | 401.4145 | 178.9516
423.9417 | 401.2796 | 179.3461
424.9417 | 401.301 | 179.76
425.9417 | 401.1416 | 180.1549
426.9417 | 401.1304 | 180.5456
427.9417 | 401.1286 | 180.9268
428.9417 | 401.0712 | 181.3363
429.9417 | 401.0079 | 181.7245
430.9417 | 400.9149 | 182.1224
431.9417 | 400.8879 | 182.5217
432.9417 | 400.8794 | 182.9216
433.9417 | 400.7593 | 183.3002
434.9417 | 400.7536 | 183.6977
435.9417 | 400.7641 | 184.1036
436.9417 | 400.649 | 184.4984
437.9417 | 400.58 | 184.8925
438.9417 | 400.5741 | 185.3035
439.9417 | 400.5547 | 185.7613
440.9417 | 400.6421 | 186.1808
441.9417 | 400.7687 | 186.5809
442.9417 | 400.9103 | 187.0091
443.9417 | 400.9155 | 187.4118
444.9417 | 400.9708 | 187.7912
445.9417 | 400.8747 | 188.1735
446.9417 | 400.8424 | 188.5397
447.9417 | 400.7843 | 188.9226
448.9417 | 400.8639 | 189.2819
449.9417 | 400.9949 | 189.6138
450.9417 | 401.0569 | 189.9828
451.9417 | 401.1334 | 190.3236
452.9417 | 401.0071 | 190.6635
453.9417 | 401.0259 | 191.0033
454.9417 | 401.1642 | 191.3362
455.9417 | 401.2927 | 191.6704
456.9417 | 401.3624 | 192.013
457.9417 | 401.4986 | 192.3541
458.9417 | 401.4005 | 192.6933
459.9417 | 401.2638 | 193.0387
460.9417 | 401.1254 | 193.3602
461.9417 | 401.1385 | 193.7233
462.9417 | 401.2174 | 194.0259
463.9417 | 401.2117 | 194.4048
464.9417 | 401.2743 | 194.7364
465.9417 | 401.3273 | 195.0696
466.9417 | 401.3362 | 195.3967
467.9417 | 401.315 | 195.7145
468.9417 | 401.4203 | 196.0686
469.9417 | 401.5053 | 196.3812
470.9417 | 401.6124 | 196.6995
471.9417 | 401.623 | 197.0359
472.9417 | 401.8006 | 197.3622
473.9417 | 401.9009 | 197.6965
474.9417 | 401.9655 | 198.0203
475.9417 | 402.005 | 198.361
476.9417 | 401.9967 | 198.6885
477.9417 | 402.0441 | 199.025
478.9417 | 402.1019 | 199.3661
479.9417 | 401.9309 | 199.6871
480.9417 | 401.8137 | 200.0201
481.9417 | 401.7666 | 200.3555
482.9417 | 401.7914 | 200.6791
483.9417 | 401.9434 | 201.021
484.9417 | 402.05 | 201.3319
485.9417 | 402.0472 | 201.6648
486.9417 | 402.0678 | 201.999
487.9417 | 402.101 | 202.3342
488.9417 | 402.1388 | 202.6518
489.9417 | 402.1533 | 202.9722
490.9417 | 402.1398 | 203.2945
491.9417 | 402.2134 | 203.6129
492.9417 | 402.2687 | 203.929
493.9417 | 402.3035 | 204.2519
494.9417 | 402.3889 | 204.5687
495.9417 | 402.3792 | 204.8815
496.9417 | 402.2561 | 205.202
497.9417 | 402.249 | 205.5065
498.9417 | 402.3006 | 205.8326
499.9417 | 402.3608 | 206.1221
500.9417 | 402.3205 | 206.4252
501.9417 | 402.2098 | 206.7396
502.9417 | 402.1459 | 207.043
503.9417 | 402.0743 | 207.3473
504.9417 | 402.0742 | 207.6546
505.9417 | 402.0899 | 207.9471
506.9417 | 402.0686 | 208.2474
507.9417 | 402.2018 | 208.5647
508.9417 | 402.1818 | 208.868
509.9417 | 401.9911 | 209.1781
510.9417 | 401.9935 | 209.4766
511.9417 | 401.949 | 209.7626
512.9417 | 402.0075 | 210.0702
513.9417 | 401.9286 | 210.3579
514.9417 | 401.905 | 210.6661
515.9417 | 401.9452 | 210.9603
516.9417 | 401.8485 | 211.2531
517.9417 | 401.8001 | 211.5446
518.9417 | 401.8424 | 211.8485
519.9417 | 401.8973 | 212.1371
520.9417 | 401.8735 | 212.4341
521.9417 | 401.9126 | 212.7224
522.9417 | 401.9115 | 213.0153
523.9417 | 401.9349 | 213.3087
524.9417 | 401.8839 | 213.572
525.9417 | 401.8908 | 213.888
526.9417 | 401.8033 | 214.1463
527.9417 | 401.7261 | 214.4541
528.9417 | 401.712 | 214.7744
529.9417 | 401.5591 | 215.0778
530.9417 | 401.5429 | 215.39
531.9417 | 401.4672 | 215.7088
532.9417 | 401.3701 | 216.0003
533.9417 | 401.2319 | 216.2926
534.9417 | 401.1122 | 216.5756
535.9417 | 401.1799 | 216.8907
536.9417 | 401.2313 | 217.1641
537.9417 | 401.3597 | 217.4585
538.9417 | 401.3751 | 217.727
539.9417 | 401.2766 | 218.0171
540.9417 | 401.1798 | 218.3001
541.9417 | 401.0334 | 218.5709
542.9417 | 401.0364 | 218.8316
543.9417 | 401.1649 | 219.1072
544.9417 | 401.2872 | 219.3855
545.9417 | 401.2738 | 219.6646
546.9417 | 401.2251 | 220.0054
547.9417 | 401.2924 | 220.3326
548.9417 | 401.3077 | 220.6515
549.9417 | 401.4595 | 220.9402
550.9417 | 401.4852 | 221.2231
551.9417 | 401.5313 | 221.4898
552.9417 | 401.5111 | 221.7739
553.9417 | 401.4209 | 222.0366
554.9417 | 401.476 | 222.307
555.9417 | 401.5612 | 222.5775
556.9417 | 401.6835 | 222.8421
557.9417 | 401.6714 | 223.0739
558.9417 | 401.7236 | 223.3201
559.9417 | 401.8423 | 223.5627
560.9417 | 401.9149 | 223.786
561.9417 | 401.9136 | 224.0438
562.9417 | 401.8643 | 224.2822
563.9417 | 401.8718 | 224.5132
564.9417 | 401.9096 | 224.7269
565.9417 | 401.9475 | 224.9897
566.9417 | 401.9293 | 225.2148
567.9417 | 401.9448 | 225.4534
568.9417 | 401.9404 | 225.7058
569.9417 | 401.8117 | 225.9667
570.9417 | 401.8264 | 226.2252
571.9417 | 401.9155 | 226.4875
572.9417 | 401.9411 | 226.7472
573.9417 | 401.9266 | 227.0014
574.9417 | 401.8664 | 227.2508
575.9417 | 401.9203 | 227.5016
576.9417 | 401.8549 | 227.7694
577.9417 | 401.8369 | 228.021
578.9417 | 401.8661 | 228.2837
579.9417 | 401.9481 | 228.5479
580.9417 | 402.0328 | 228.8038
581.9417 | 401.9555 | 229.0495
582.9417 | 401.7738 | 229.3139
583.9417 | 401.8268 | 229.5643
584.9417 | 401.8666 | 229.8012
585.9417 | 401.9747 | 230.0542
586.9417 | 401.9795 | 230.3015
587.9417 | 401.9602 | 230.5386
588.9417 | 401.897 | 230.7628
589.9417 | 401.8662 | 231.0009
590.9417 | 401.828 | 231.2507
591.9417 | 401.8308 | 231.4854
592.9417 | 401.9301 | 231.7333
593.9417 | 401.9565 | 231.9953
594.9417 | 401.9457 | 232.2581
595.9417 | 401.7454 | 232.4994
596.9417 | 401.7329 | 232.7511
597.9417 | 401.6896 | 232.998
598.9417 | 401.6426 | 233.2393
599.9417 | 401.5468 | 233.4747
600.9417 | 401.5594 | 233.7102
601.9417 | 401.4865 | 233.9546
602.9573 | 401.4154 | 234.1908
603.9417 | 401.4524 | 234.4195
604.9417 | 401.4674 | 234.6473
605.9417 | 401.4502 | 234.8896
606.9417 | 401.4924 | 235.1142
607.9417 | 401.4086 | 235.3624
608.9417 | 401.357 | 235.5895
609.9417 | 401.4106 | 235.817
610.9417 | 401.367 | 236.0474
611.9417 | 401.2335 | 236.2751
612.9417 | 401.2018 | 236.4985
613.9417 | 401.1645 | 236.724
614.9417 | 401.2967 | 236.9692
615.9417 | 401.4037 | 237.2098
616.9417 | 401.387 | 237.4694
617.9417 | 401.3142 | 237.6916
618.9417 | 401.2731 | 237.9406
619.9417 | 401.1772 | 238.1877
620.9417 | 401.1741 | 238.4377
621.9417 | 401.0236 | 238.666
622.9417 | 401.0423 | 238.9135
623.9417 | 401.1063 | 239.1522
624.9417 | 401.1616 | 239.3944
625.9417 | 401.1121 | 239.63
626.9417 | 401.1319 | 239.8631
627.9417 | 401.2988 | 240.1084
628.9417 | 401.4045 | 240.3586
629.9417 | 401.4834 | 240.5474
630.9417 | 401.4352 | 240.7797
631.9417 | 401.4116 | 241.0032
632.9417 | 401.3906 | 241.2285
633.9417 | 401.3368 | 241.4456
634.9417 | 401.4198 | 241.6745
635.9417 | 401.4594 | 241.9138
636.9417 | 401.3209 | 242.1172
637.9417 | 401.4347 | 242.3536
638.9417 | 401.4699 | 242.5674
639.9417 | 401.469 | 242.8052
640.9417 | 401.412 | 243.0327
641.9417 | 401.5182 | 243.2429
642.9417 | 401.6144 | 243.4634
643.9417 | 401.527 | 243.69
644.9417 | 401.4264 | 243.906
645.9417 | 401.2773 | 244.136
646.9417 | 401.1709 | 244.3407
647.9417 | 401.2187 | 244.5542
648.9417 | 401.0829 | 244.773
649.9417 | 401.2437 | 244.9748
650.9417 | 401.4783 | 245.1769
651.9417 | 401.6053 | 245.3972
652.9417 | 401.5 | 245.6568
653.9417 | 401.618 | 245.9028
654.9417 | 401.8015 | 246.1242
655.9417 | 401.894 | 246.3751
656.9417 | 402.0404 | 246.603
657.9417 | 401.9007 | 246.8226
658.9417 | 401.7949 | 247.0708
659.9417 | 401.8896 | 247.3017
660.9417 | 401.8685 | 247.5237
661.9417 | 401.8206 | 247.7586
662.9417 | 401.7626 | 247.9653
663.9417 | 401.7693 | 248.2067
664.9417 | 401.7056 | 248.4409
665.9417 | 401.5589 | 248.6637
666.9417 | 401.5156 | 248.887
667.9417 | 401.5416 | 249.0858
668.9417 | 401.2991 | 249.3101
669.9417 | 401.242 | 249.5278
670.9417 | 401.1467 | 249.7324
671.9417 | 400.9715 | 249.9631
672.9417 | 400.8426 | 250.1862
673.9417 | 400.8603 | 250.383
674.9417 | 400.9019 | 250.6197
675.9417 | 400.998 | 250.852
676.9417 | 400.9845 | 251.0707
677.9417 | 400.8846 | 251.289
678.9417 | 400.9304 | 251.4968
679.9417 | 401.0026 | 251.7153
680.9417 | 400.943 | 251.929
681.9417 | 400.8117 | 252.1472
682.9417 | 400.8131 | 252.3414
683.9417 | 400.874 | 252.5447
684.9417 | 400.8913 | 252.7448
685.9417 | 400.8283 | 252.9562
686.9417 | 400.8473 | 253.1524
687.9417 | 400.7907 | 253.3858
688.9417 | 400.7595 | 253.5639
689.9417 | 400.8223 | 253.776
690.9417 | 400.84 | 253.9531
691.9417 | 400.8866 | 254.1631
692.9417 | 400.8614 | 254.3275
693.9417 | 400.7895 | 254.5433
694.9417 | 400.8132 | 254.756
695.9417 | 400.7698 | 254.9411
696.9417 | 400.8338 | 255.13
697.9417 | 400.953 | 255.3043
698.9417 | 401.0152 | 255.4711
699.9417 | 401.1854 | 255.6681
700.9417 | 401.274 | 255.8617
701.9417 | 401.2989 | 256.0627
702.9417 | 401.2405 | 256.2354
703.9417 | 401.1279 | 256.4375
704.9417 | 401.1018 | 256.6277
705.9417 | 401.1794 | 256.8273
706.9417 | 401.1428 | 257.0389
707.9417 | 401.1676 | 257.2388
708.9417 | 401.1549 | 257.4395
709.9417 | 401.1803 | 257.6405
710.9417 | 401.0639 | 257.8458
711.9417 | 401.1003 | 258.0255
712.9417 | 401.1044 | 258.2058
713.9417 | 401.0744 | 258.384
714.9417 | 400.9766 | 258.5812
715.9417 | 400.9028 | 258.7731
716.9417 | 400.8281 | 258.9684
717.9417 | 400.8426 | 259.1807
718.9417 | 400.8569 | 259.3865
719.9417 | 400.8675 | 259.5876
720.9417 | 400.9379 | 259.7821
721.9417 | 401.013 | 259.991
722.9417 | 401.0431 | 260.1955
723.9417 | 400.8268 | 260.4105
724.9417 | 400.8178 | 260.6125
725.9417 | 400.8893 | 260.8013
726.9417 | 400.9115 | 260.9979
727.9417 | 400.9033 | 261.1824
728.9417 | 400.946 | 261.3782
729.9417 | 401.038 | 261.5504
730.9417 | 401.0688 | 261.7198
731.9417 | 401.0423 | 261.9001
732.9417 | 401.0328 | 262.0821
733.9417 | 400.8946 | 262.2687
734.9417 | 400.9012 | 262.4476
735.9417 | 400.9175 | 262.6175
736.9417 | 400.879 | 262.7907
737.9417 | 400.79 | 262.9825
738.9417 | 400.703 | 263.1585
739.9417 | 400.7545 | 263.3305
740.9417 | 400.8207 | 263.5112
741.9417 | 400.7633 | 263.6714
742.9417 | 400.5706 | 263.8323
743.9417 | 400.4014 | 263.9916
744.9417 | 400.3983 | 264.1707
745.9417 | 400.1752 | 264.3327
746.9417 | 400.0585 | 264.4971
747.9417 | 400.1903 | 264.6475
748.9417 | 400.1147 | 264.7802
749.9417 | 400.1755 | 264.9282
750.9417 | 400.3165 | 265.0764
751.9417 | 400.3905 | 265.2273
752.9417 | 400.3153 | 265.3834
753.9417 | 400.1429 | 265.488
754.9417 | 400.1397 | 265.6517
755.9417 | 400.059 | 265.7867
756.9417 | 400.1296 | 265.9503
757.9417 | 400.1532 | 266.1094
758.9417 | 400.0359 | 266.2423
759.9417 | 399.9024 | 266.3783
760.9417 | 399.8342 | 266.5029
761.9417 | 399.8641 | 266.6563
762.9417 | 399.9427 | 266.7968
763.9417 | 400.0321 | 266.9459
764.9417 | 400.1386 | 267.0993
765.9417 | 400.1924 | 267.2371
766.9417 | 400.1606 | 267.3746
767.9417 | 400.2351 | 267.5184
768.9417 | 400.3032 | 267.6259
769.9417 | 400.44 | 267.7943
770.9417 | 400.5957 | 267.9417
771.9417 | 400.6388 | 268.0821
772.9417 | 400.5822 | 268.228
773.9417 | 400.6822 | 268.364
774.9417 | 400.7047 | 268.4861
775.9417 | 400.7319 | 268.6309
776.9417 | 400.8216 | 268.7556
777.9417 | 401.0847 | 268.8905
778.9417 | 401.1394 | 269.0307
779.9417 | 401.2187 | 269.1701
780.9417 | 401.1887 | 269.3014
781.9417 | 401.3323 | 269.4234
782.9417 | 401.3366 | 269.5473
783.9417 | 401.33 | 269.6881
784.9417 | 401.2889 | 269.806
785.9417 | 401.352 | 269.9568
786.9417 | 401.3587 | 270.0973
787.9417 | 401.3826 | 270.2389
788.9417 | 401.3743 | 270.3832
789.9417 | 401.3919 | 270.5234
790.9417 | 401.397 | 270.6599
791.9417 | 401.3251 | 270.8057
792.9417 | 401.2575 | 270.9572
793.9417 | 401.1734 | 271.1033
794.9417 | 401.186 | 271.2531
795.9417 | 401.0935 | 271.3857
796.9417 | 401.0432 | 271.5458
797.9417 | 400.9798 | 271.6616
798.9417 | 400.8079 | 271.8314
799.9417 | 400.6838 | 271.9835
800.9417 | 400.729 | 272.1484
801.9417 | 400.6375 | 272.3297
802.9417 | 400.6437 | 272.5058
803.9417 | 400.6654 | 272.6642
804.9417 | 400.7349 | 272.8386
805.9417 | 400.8612 | 273.0131
806.9417 | 400.832 | 273.1905
807.9417 | 400.8169 | 273.3536
808.9417 | 400.7779 | 273.545
809.9417 | 400.8255 | 273.7214
810.9417 | 400.932 | 273.8926
811.9417 | 400.9438 | 274.0386
812.9417 | 401.0224 | 274.2089
813.9417 | 401.0261 | 274.3573
814.9417 | 401.0414 | 274.5098
815.9417 | 400.9865 | 274.6604
816.9417 | 401.1313 | 274.8218
817.9417 | 401.1699 | 274.965
818.9417 | 401.1744 | 275.1257
819.9417 | 401.164 | 275.2706
820.9417 | 401.3769 | 275.4281
821.9417 | 401.5003 | 275.5677
822.9417 | 401.612 | 275.7354
823.9417 | 401.6778 | 275.8826
824.9417 | 401.7481 | 276.0382
825.9417 | 401.776 | 276.1977
826.9417 | 401.8521 | 276.3591
827.9417 | 401.7936 | 276.5134
828.9417 | 401.7891 | 276.6709
829.9417 | 401.8362 | 276.8038
830.9417 | 401.9507 | 276.9547
831.9417 | 401.9268 | 277.0911
832.9417 | 401.9668 | 277.2386
833.9417 | 402.0825 | 277.3777
834.9417 | 402.0848 | 277.5284
835.9417 | 402.0297 | 277.6694
836.9417 | 402.0235 | 277.8126
837.9417 | 402.0441 | 277.944
838.9417 | 402.097 | 278.0747
839.9417 | 402.1007 | 278.2031
840.9417 | 401.9518 | 278.3338
841.9417 | 401.8787 | 278.4576
842.9417 | 401.8336 | 278.5752
843.9417 | 401.7986 | 278.6956
844.9417 | 401.8003 | 278.8198
845.9417 | 401.7598 | 278.9355
846.9417 | 401.5379 | 279.0731
847.9417 | 401.4455 | 279.1816
848.9417 | 401.4859 | 279.3104
849.9417 | 401.4617 | 279.4179
850.9417 | 401.3645 | 279.5452
851.9417 | 401.152 | 279.6598
852.9417 | 401.1465 | 279.7786
853.9417 | 400.9925 | 279.9019
854.9417 | 401.0455 | 280.0282
855.9417 | 400.9897 | 280.1519
856.9417 | 401.0256 | 280.2552
857.9417 | 401.0547 | 280.3666
858.9417 | 400.9568 | 280.4846
859.9417 | 400.9408 | 280.6135
860.9417 | 400.9222 | 280.7336
861.9417 | 400.9084 | 280.8366
862.9417 | 400.9652 | 280.9596
863.9417 | 400.9573 | 281.0779
864.9417 | 400.8568 | 281.1937
865.9417 | 400.8127 | 281.2945
866.9417 | 400.8449 | 281.4155
867.9417 | 400.775 | 281.5355
868.9417 | 400.7138 | 281.6571
869.9417 | 400.772 | 281.7459
870.9417 | 400.6882 | 281.8823
871.9417 | 400.6189 | 281.9941
872.9417 | 400.6794 | 282.1025
873.9417 | 400.6932 | 282.2446
874.9417 | 400.7428 | 282.3493
875.9417 | 400.7604 | 282.488
876.9417 | 400.7209 | 282.5988
877.9417 | 400.7526 | 282.7269
878.9417 | 400.7624 | 282.8398
879.9417 | 400.7985 | 282.971
880.9417 | 400.9597 | 283.0922
881.9417 | 400.9939 | 283.209
882.9417 | 401.0843 | 283.3135
883.9417 | 401.1822 | 283.4483
884.9417 | 401.2552 | 283.5646
885.9417 | 401.2965 | 283.6866
886.9417 | 401.3018 | 283.8121
887.9417 | 401.342 | 283.9241
888.9417 | 401.4284 | 284.0653
889.9417 | 401.3892 | 284.1924
890.9417 | 401.3387 | 284.3233
891.9417 | 401.4508 | 284.427
892.9417 | 401.4539 | 284.5438
893.9417 | 401.2881 | 284.6542
894.9417 | 401.1586 | 284.7822
895.9417 | 401.2505 | 284.8911
896.9417 | 401.2427 | 284.9944
897.9417 | 401.1817 | 285.1198
898.9417 | 401.0915 | 285.2309
899.9417 | 401.2232 | 285.3404
900.9417 | 401.1536 | 285.4599
901.9417 | 401.0333 | 285.5547
902.9417 | 401.045 | 285.6473
903.9417 | 401.1318 | 285.7604
904.9417 | 401.1735 | 285.8666
905.9417 | 401.0871 | 285.9802
906.9417 | 401.0029 | 286.0712
907.9417 | 400.9155 | 286.1895
908.9417 | 400.9026 | 286.2846
909.9417 | 400.8526 | 286.3914
910.9417 | 400.7601 | 286.4981
911.9417 | 400.6828 | 286.5989
912.9417 | 400.7372 | 286.715
913.9417 | 400.7403 | 286.838
914.9417 | 400.7181 | 286.9195
915.9417 | 400.8448 | 287.0367
916.9417 | 400.9253 | 287.1599
917.9417 | 400.9622 | 287.2525
918.9417 | 400.9911 | 287.3619
919.9417 | 401.014 | 287.4719
920.9417 | 401.0881 | 287.5904
921.9417 | 401.1141 | 287.6958
922.9417 | 401.0957 | 287.8135
923.9417 | 401.1271 | 287.9227
924.9417 | 401.0334 | 288.0379
925.9417 | 401.1673 | 288.1454
926.9417 | 401.0986 | 288.2771
927.9417 | 401.129 | 288.3779
928.9417 | 401.1165 | 288.487
929.9417 | 401.0795 | 288.5802
930.9417 | 401.0747 | 288.693
931.9417 | 401.0504 | 288.8043
932.9417 | 401.0853 | 288.9269
933.9417 | 401.1725 | 289.0171
934.9417 | 401.1918 | 289.1275
935.9417 | 401.2313 | 289.2308
936.9417 | 401.1511 | 289.3245
937.9417 | 401.1585 | 289.428
938.9417 | 401.1674 | 289.5359
939.9417 | 401.2325 | 289.6384
940.9417 | 401.2201 | 289.7112
941.9417 | 401.2377 | 289.8255
942.9417 | 401.3373 | 289.9284
943.9417 | 401.3708 | 290.0229
944.9417 | 401.2625 | 290.1311
945.9417 | 401.2272 | 290.228
946.9417 | 401.3186 | 290.3245
947.9417 | 401.3655 | 290.4257
948.9417 | 401.3379 | 290.5358
949.9417 | 401.3501 | 290.616
950.9417 | 401.4239 | 290.7135
951.9417 | 401.3868 | 290.8131
952.9417 | 401.3129 | 290.9065
953.9417 | 401.2743 | 290.9948
954.9417 | 401.3679 | 291.0594
955.9417 | 401.2381 | 291.1627
956.9417 | 401.1953 | 291.2284
957.9417 | 401.2839 | 291.321
958.9417 | 401.0489 | 291.4052
959.9417 | 401.0332 | 291.4752
960.9417 | 401.0841 | 291.5409
961.9417 | 401.0537 | 291.607
962.9417 | 400.9891 | 291.6736
963.9417 | 400.7035 | 291.7477
964.9417 | 400.5674 | 291.8065
965.9417 | 400.5452 | 291.8791
966.9417 | 400.4981 | 291.9361
967.9417 | 400.4594 | 291.9882
968.9417 | 400.3147 | 292.0716
969.9417 | 400.3821 | 292.12
970.9417 | 400.3234 | 292.1829
971.9417 | 400.3586 | 292.2528
972.9417 | 400.2983 | 292.2923
973.9417 | 400.1708 | 292.3562
974.9417 | 400.2277 | 292.4092
975.9417 | 400.2675 | 292.4608
976.9417 | 400.3262 | 292.5126
977.9417 | 400.3544 | 292.5811
978.9417 | 400.3079 | 292.6168
979.9417 | 400.2237 | 292.6647
980.9417 | 400.2942 | 292.7189
981.9417 | 400.4441 | 292.7524
982.9417 | 400.5085 | 292.7929
983.9417 | 400.604 | 292.83
984.9417 | 400.6163 | 292.8728
985.9417 | 400.5796 | 292.901
986.9417 | 400.5164 | 292.9341
987.9417 | 400.5573 | 292.96
988.9417 | 400.7582 | 292.9734
989.9417 | 400.7752 | 292.9798
990.9417 | 400.8063 | 292.9996
991.9417 | 400.7717 | 293.0275
992.9417 | 400.8506 | 293.0333
993.9417 | 400.8718 | 293.0378
994.9417 | 400.9559 | 293.0425
995.9417 | 400.9166 | 293.0403
996.9417 | 400.9214 | 293.0417
997.9417 | 400.9922 | 293.0414
998.9417 | 401.0038 | 293.0429
999.9417 | 401.0357 | 293.0373
1000.9417 | 400.9496 | 293.0357
1001.9417 | 400.9353 | 293.0323
1002.9417 | 400.9604 | 293.0242
1003.9417 | 400.9514 | 293.0166
1004.9417 | 401.0018 | 292.9894
1005.9417 | 401.0576 | 293.04
1006.9417 | 401.0977 | 293.1158
1007.9417 | 401.1648 | 293.2147
1008.9417 | 401.2114 | 293.3483
1009.9417 | 401.1783 | 293.4868
1010.9417 | 401.2052 | 293.6293
1011.9417 | 401.2208 | 293.7857
1012.9417 | 401.3251 | 293.934
1013.9417 | 401.3553 | 294.0861
1014.9417 | 401.2533 | 294.2191
1015.9417 | 401.1432 | 294.3585
1016.9417 | 401.0309 | 294.5054
1017.9417 | 401.0926 | 294.6431
1018.9417 | 401.1407 | 294.7962
1019.9417 | 401.2819 | 294.928
1020.9417 | 401.3333 | 295.0729
1021.9417 | 401.3494 | 295.2058
1022.9417 | 401.4117 | 295.3637
1023.9417 | 401.5209 | 295.5572
1024.9417 | 401.5583 | 295.6936
1025.9417 | 401.6303 | 295.8703
1026.9417 | 401.6863 | 296.0537
1027.9417 | 401.7142 | 296.2294
1028.9417 | 401.8342 | 296.4134
1029.9417 | 401.8375 | 296.6193
1030.9417 | 401.7519 | 296.8231
1031.9417 | 401.6851 | 297.0682
1032.9417 | 401.6396 | 297.2801
1033.9417 | 401.5933 | 297.4998
1034.9417 | 401.5123 | 297.7138
1035.9417 | 401.4795 | 297.9461
1036.9417 | 401.3961 | 298.1725
1037.9417 | 401.3057 | 298.4082
1038.9417 | 401.3629 | 298.6596
1039.9417 | 401.4292 | 298.9191
1040.9417 | 401.3701 | 299.2108
1041.9417 | 401.3347 | 299.4702
1042.9417 | 401.4797 | 299.7358
1043.9417 | 401.376 | 299.9865
1044.9417 | 401.2698 | 300.2514
1045.9417 | 401.2636 | 300.511
1046.9417 | 401.178 | 300.7778
1047.9417 | 401.0992 | 301.0505
1048.9417 | 401.1029 | 301.3119
1049.9417 | 401.0847 | 301.568
1050.9417 | 401.1208 | 301.8204
1051.9417 | 401.1052 | 302.0737
1052.9417 | 400.8826 | 302.3013
1053.9417 | 400.7974 | 302.5315
1054.9417 | 400.7777 | 302.7351
1055.9417 | 400.9238 | 302.9489
1056.9417 | 400.9264 | 303.1289
1057.9417 | 400.9495 | 303.328
1058.9417 | 401.0654 | 303.5184
1059.9417 | 401.0793 | 303.7166
1060.9417 | 400.9912 | 303.8667
1061.9417 | 401.0171 | 304.0209
1062.9417 | 401.0001 | 304.1926
1063.9417 | 400.913 | 304.3076
1064.9417 | 400.7747 | 304.4152
1065.9417 | 400.7422 | 304.5025
1066.9417 | 400.7251 | 304.5831
1067.9417 | 400.7032 | 304.6204
1068.9417 | 400.5718 | 304.6485
1069.9417 | 400.5393 | 304.6433
1070.9417 | 400.5355 | 304.6057
1071.9417 | 400.5561 | 304.5491
1072.9417 | 400.5878 | 304.534
1073.9417 | 400.6075 | 304.4957
1074.9417 | 400.6239 | 304.4684
1075.9417 | 400.6935 | 304.4067
1076.9417 | 400.7619 | 304.3625
1077.9417 | 400.7194 | 304.3018
1078.9417 | 400.6186 | 304.2287
1079.9417 | 400.5369 | 304.1914
1080.9417 | 400.5851 | 304.1202
1081.9417 | 400.6974 | 304.0227
1082.9417 | 400.7121 | 303.903
1083.9417 | 400.6224 | 303.7741
1084.9417 | 400.6487 | 303.6253
1085.9417 | 400.6876 | 303.469
1086.9417 | 400.7576 | 303.319
1087.9417 | 400.7767 | 303.1543
1088.9417 | 400.6768 | 303.0059
1089.9417 | 400.5442 | 302.8586
1090.9417 | 400.5146 | 302.7168
1091.9417 | 400.5268 | 302.585
1092.9417 | 400.6578 | 302.4273
1093.9417 | 400.7468 | 302.3085
1094.9417 | 400.6186 | 302.1898
1095.9417 | 400.6547 | 302.0799
1096.9417 | 400.7418 | 301.9767
1097.9417 | 400.7105 | 301.8709
1098.9417 | 400.7505 | 301.764
1099.9417 | 400.8668 | 301.6804
1100.9417 | 400.9673 | 301.6154
1101.9417 | 400.9443 | 301.5763
1102.9417 | 400.9533 | 301.5339
1103.9417 | 400.9311 | 301.505
1104.9417 | 400.8832 | 301.4646
1105.9417 | 400.9948 | 301.4902
1106.9417 | 401.0071 | 301.5002
1107.9417 | 401.0535 | 301.5124
1108.9417 | 401.0019 | 301.5224
1109.9417 | 400.9257 | 301.5229
1110.9417 | 400.9723 | 301.5161
1111.9417 | 401.0424 | 301.5211
1112.9417 | 401.0619 | 301.5154
1113.9417 | 401.1229 | 301.4905
1114.9417 | 401.1809 | 301.4868
1115.9417 | 401.1979 | 301.4879
1116.9417 | 401.3064 | 301.4535
1117.9417 | 401.299 | 301.4618
1118.9417 | 401.2642 | 301.4121
1119.9417 | 401.2994 | 301.4208
1120.9417 | 401.3972 | 301.4198
1121.9417 | 401.4632 | 301.459
1122.9417 | 401.3252 | 301.4898
1123.9417 | 401.3514 | 301.4985
1124.9417 | 401.4202 | 301.5311
1125.9417 | 401.5132 | 301.5526
1126.9417 | 401.5786 | 301.5724
1127.9417 | 401.6627 | 301.5827
1128.9417 | 401.5889 | 301.6009
1129.9417 | 401.5751 | 301.6302
1130.9417 | 401.5842 | 301.6699
1131.9417 | 401.6042 | 301.7099
1132.9417 | 401.4991 | 301.7463
1133.9417 | 401.4828 | 301.8101
1134.9417 | 401.5814 | 301.8505
1135.9417 | 401.6937 | 301.9308
1136.9417 | 401.7183 | 301.9887
1137.9417 | 401.7019 | 302.0381
1138.9417 | 401.688 | 302.107
1139.9417 | 401.6738 | 302.1875
1140.9417 | 401.5924 | 302.2614
1141.9417 | 401.5007 | 302.3349
1142.9417 | 401.3431 | 302.3956
1143.9417 | 401.1656 | 302.4745
1144.9417 | 401.0536 | 302.5398
1145.9417 | 401.2165 | 302.626
1146.9417 | 401.3054 | 302.6717
1147.9417 | 401.3573 | 302.7736
1148.9417 | 401.4355 | 302.86
1149.9417 | 401.4968 | 302.934
1150.9417 | 401.3959 | 303.0133
1151.9417 | 401.4633 | 303.1161
1152.9417 | 401.4862 | 303.1849
1153.9417 | 401.6538 | 303.2866
1154.9417 | 401.6604 | 303.3405
1155.9417 | 401.589 | 303.4505
1156.9417 | 401.709 | 303.5453
1157.9417 | 401.7654 | 303.6347
1158.9417 | 401.7706 | 303.7467
1159.9417 | 401.7765 | 303.8435
1160.9417 | 401.7392 | 303.9293
1161.9417 | 401.7691 | 304.0298
1162.9417 | 401.7568 | 304.1514
1163.9417 | 401.6878 | 304.2613
1164.9417 | 401.6826 | 304.3661
1165.9417 | 401.552 | 304.4623
1166.9417 | 401.4909 | 304.5851
1167.9417 | 401.45 | 304.6674
1168.9417 | 401.4059 | 304.7762
1169.9417 | 401.3846 | 304.8703
1170.9417 | 401.3609 | 304.9888
1171.9417 | 401.2835 | 305.1064
1172.9417 | 401.3127 | 305.2015
1173.9417 | 401.2285 | 305.3128
1174.9417 | 401.174 | 305.4254
1175.9417 | 401.0946 | 305.5309
1176.9417 | 401.1094 | 305.6365
1177.9417 | 401.1764 | 305.7467
1178.9417 | 401.3016 | 305.8567
1179.9417 | 401.3632 | 305.9596
1180.9417 | 401.3857 | 306.0576
1181.9417 | 401.2795 | 306.1562
1182.9417 | 401.2487 | 306.2548
1183.9417 | 401.2444 | 306.3531
1184.9417 | 401.2586 | 306.4356
1185.9417 | 401.3357 | 306.5459
1186.9417 | 401.3827 | 306.6341
1187.9417 | 401.5375 | 306.747
1188.9417 | 401.6751 | 306.8481
1189.9417 | 401.6517 | 306.9424
1190.9417 | 401.6303 | 307.0449
1191.9417 | 401.5045 | 307.1504
1192.9417 | 401.5015 | 307.2471
1193.9417 | 401.502 | 307.3441
1194.9417 | 401.6123 | 307.4451
1195.9417 | 401.5816 | 307.5579
1196.9417 | 401.5143 | 307.6491
1197.9417 | 401.5153 | 307.7465
1198.9417 | 401.5402 | 307.8354
1199.9417 | 401.5353 | 307.9525
1200.9417 | 401.4579 | 308.0326
1201.9417 | 401.3919 | 308.1449
1202.9417 | 401.3437 | 308.2373
1203.9417 | 401.2613 | 308.3414
1204.9417 | 401.2929 | 308.4382
1205.9417 | 401.3457 | 308.5418
1206.9417 | 401.3257 | 308.635
1207.9417 | 401.2897 | 308.7526
1208.9417 | 401.2621 | 308.8392
1209.9417 | 401.2607 | 308.9446
1210.9417 | 401.141 | 309.0503
1211.9417 | 401.039 | 309.1778
1212.9417 | 401.019 | 309.2841
1213.9417 | 400.9729 | 309.3923
1214.9417 | 400.9568 | 309.497
1215.9417 | 400.8955 | 309.604
1216.9417 | 400.8714 | 309.7246
1217.9417 | 400.7901 | 309.8249
1218.9417 | 400.874 | 309.932
1219.9417 | 400.9503 | 310.0591
1220.9417 | 400.8842 | 310.1762
1221.9417 | 400.9466 | 310.2897
1222.9417 | 400.9648 | 310.4176
1223.9417 | 401.0532 | 310.526
1224.9417 | 400.9864 | 310.6619
1225.9417 | 401.0603 | 310.7924
1226.9417 | 401.0255 | 310.9057
1227.9417 | 401.1106 | 311.0409
1228.9417 | 401.0605 | 311.1813
1229.9417 | 401.0434 | 311.3137
1230.9417 | 401.1132 | 311.4333
1231.9417 | 401.1398 | 311.5685
1232.9417 | 401.2291 | 311.7078
1233.9417 | 401.3041 | 311.8407
1234.9417 | 401.1937 | 311.9624
1235.9417 | 401.2221 | 312.1072
1236.9417 | 401.3644 | 312.2327
1237.9417 | 401.4915 | 312.3747
1238.9417 | 401.5273 | 312.5251
1239.9417 | 401.5233 | 312.6412
1240.9417 | 401.451 | 312.797
1241.9417 | 401.4615 | 312.9254
1242.9417 | 401.4799 | 313.0827
1243.9417 | 401.3684 | 313.2167
1244.9417 | 401.3808 | 313.3531
1245.9417 | 401.4867 | 313.5082
1246.9417 | 401.4311 | 313.6485
1247.9417 | 401.3187 | 313.7964
1248.9417 | 401.2628 | 313.9392
1249.9417 | 401.3095 | 314.0626
1250.9417 | 401.2552 | 314.1973
1251.9417 | 401.4058 | 314.3388
1252.9417 | 401.413 | 314.4801
1253.9417 | 401.3674 | 314.6049
1254.9417 | 401.384 | 314.7375
1255.9417 | 401.4601 | 314.8764
1256.9417 | 401.4561 | 314.999
1257.9417 | 401.5072 | 315.1234
1258.9417 | 401.5306 | 315.2609
1259.9417 | 401.5881 | 315.3774
1260.9417 | 401.7075 | 315.4958
1261.9417 | 401.6634 | 315.627
1262.9417 | 401.6035 | 315.7353
1263.9417 | 401.5582 | 315.8724
1264.9417 | 401.5306 | 316.0013
1265.9417 | 401.5852 | 316.0989
1266.9417 | 401.6804 | 316.2413
1267.9417 | 401.7126 | 316.3545
1268.9417 | 401.6729 | 316.489
1269.9417 | 401.6338 | 316.6084
1270.9417 | 401.6682 | 316.7311
1271.9417 | 401.6416 | 316.8351
1272.9417 | 401.7256 | 316.9596
1273.9417 | 401.917 | 317.0689
1274.9417 | 402.0369 | 317.1929
1275.9417 | 401.9961 | 317.3046
1276.9417 | 401.9609 | 317.4189
1277.9417 | 401.9243 | 317.5332
1278.9417 | 401.8019 | 317.6413
1279.9417 | 401.8287 | 317.7837
1280.9417 | 401.9115 | 317.8854
1281.9417 | 401.9035 | 318.0237
1282.9417 | 401.9066 | 318.1403
1283.9417 | 401.812 | 318.2652
1284.9417 | 401.7531 | 318.3854
1285.9417 | 401.7013 | 318.5114
1286.9417 | 401.7634 | 318.6401
1287.9417 | 401.8115 | 318.7551
1288.9417 | 401.8066 | 318.8841
1289.9417 | 401.7736 | 318.9956
1290.9417 | 401.7109 | 319.1177
1291.9417 | 401.66 | 319.2493
1292.9417 | 401.7188 | 319.3646
1293.9417 | 401.7939 | 319.4997
1294.9417 | 401.704 | 319.6108
1295.9417 | 401.6949 | 319.7372
1296.9417 | 401.664 | 319.8582
1297.9417 | 401.6443 | 319.968
1298.9417 | 401.7121 | 320.116
1299.9417 | 401.7508 | 320.2284
1300.9417 | 401.5624 | 320.3569
1301.9417 | 401.5229 | 320.4993
1302.9417 | 401.4503 | 320.6117
1303.9417 | 401.334 | 320.7383
1304.9417 | 401.3004 | 320.865
1305.9417 | 401.277 | 320.9904
1306.9417 | 401.3476 | 321.092
1307.9417 | 401.2686 | 321.2324
1308.9417 | 401.2058 | 321.3501
1309.9417 | 401.2228 | 321.4754
1310.9417 | 401.0526 | 321.6154
1311.9417 | 400.947 | 321.7183
1312.9417 | 400.9578 | 321.8402
1313.9417 | 400.9741 | 321.9805
1314.9417 | 401.0043 | 322.0985
1315.9417 | 400.9866 | 322.22
1316.9417 | 401.0125 | 322.3489
1317.9417 | 401.005 | 322.4745
1318.9417 | 401.0015 | 322.5812
1319.9417 | 401.0069 | 322.7126
1320.9417 | 400.8821 | 322.828
1321.9417 | 400.8473 | 322.9658
1322.9417 | 400.808 | 323.0855
1323.9417 | 400.7176 | 323.2052
1324.9417 | 400.8475 | 323.3328
1325.9417 | 400.9013 | 323.4247
1326.9417 | 400.9053 | 323.5857
1327.9417 | 400.8861 | 323.7064
1328.9417 | 400.9797 | 323.829
1329.9417 | 401.0566 | 323.9307
1330.9417 | 401.1239 | 324.0478
1331.9417 | 401.0804 | 324.1577
1332.9417 | 401.1957 | 324.294
1333.9417 | 401.2009 | 324.4034
1334.9417 | 401.299 | 324.5314
1335.9417 | 401.3183 | 324.6192
1336.9417 | 401.4028 | 324.7708
1337.9417 | 401.429 | 324.8816
1338.9417 | 401.4114 | 325.0014
1339.9417 | 401.5605 | 325.1227
1340.9417 | 401.5524 | 325.2301
1341.9417 | 401.5634 | 325.3419
1342.9417 | 401.5713 | 325.4743
1343.9417 | 401.6215 | 325.5937
1344.9417 | 401.668 | 325.7038
1345.9417 | 401.7384 | 325.827
1346.9417 | 401.7507 | 325.9451
1347.9417 | 401.6272 | 326.0503
1348.9417 | 401.6337 | 326.1846
1349.9417 | 401.6346 | 326.3
1350.9417 | 401.6135 | 326.4008
1351.9417 | 401.6768 | 326.5288
1352.9417 | 401.5768 | 326.6386
1353.9417 | 401.4778 | 326.7565
1354.9417 | 401.4011 | 326.8836
1355.9417 | 401.4385 | 327.0022
1356.9417 | 401.4994 | 327.1195
1357.9417 | 401.4723 | 327.2315
1358.9417 | 401.3916 | 327.3551
1359.9417 | 401.3355 | 327.4645
1360.9417 | 401.1889 | 327.5853
1361.9417 | 401.2074 | 327.6946
1362.9417 | 401.1719 | 327.8122
1363.9417 | 401.0474 | 327.9543
1364.9417 | 400.9708 | 328.0631
1365.9417 | 400.9824 | 328.1705
1366.9417 | 400.9457 | 328.2954
1367.9417 | 401.0611 | 328.4086
1368.9417 | 401.0995 | 328.5224
1369.9417 | 400.945 | 328.6407
1370.9417 | 401.0012 | 328.7552
1371.9417 | 401.0217 | 328.8618
1372.9417 | 401.0883 | 328.9705
1373.9417 | 401.1652 | 329.088
1374.9417 | 401.1232 | 329.1965
1375.9417 | 401.026 | 329.3207
1376.9417 | 401.1028 | 329.4119
1377.9417 | 401.1492 | 329.5359
1378.9417 | 401.1751 | 329.6542
1379.9417 | 401.2449 | 329.749
1380.9417 | 401.2873 | 329.8618
1381.9417 | 401.2475 | 329.9782
1382.9417 | 401.1744 | 330.085
1383.9417 | 401.0186 | 330.1995
1384.9417 | 401.0401 | 330.3149
1385.9417 | 401.1347 | 330.4249
1386.9417 | 401.1211 | 330.5361
1387.9417 | 401.1956 | 330.6495
1388.9417 | 401.2251 | 330.7517
1389.9417 | 401.1917 | 330.8686
1390.9417 | 401.3526 | 330.9723
1391.9417 | 401.5061 | 331.0887
1392.9417 | 401.702 | 331.2057
1393.9417 | 401.7651 | 331.3029
1394.9417 | 401.7699 | 331.4283
1395.9417 | 401.7328 | 331.5383
1396.9417 | 401.6024 | 331.6402
1397.9417 | 401.6358 | 331.7457
1398.9417 | 401.6431 | 331.8508
1399.9417 | 401.7005 | 331.9652
1400.9417 | 401.6837 | 332.0799
1401.9417 | 401.6484 | 332.1795
1402.9417 | 401.5909 | 332.2938
1403.9417 | 401.6771 | 332.4185
1404.9417 | 401.7478 | 332.5244
1405.9417 | 401.7846 | 332.6275
1406.9417 | 401.7456 | 332.7359
1407.9417 | 401.6918 | 332.8456
1408.9417 | 401.6537 | 332.948
1409.9417 | 401.7334 | 333.0501
1410.9417 | 401.7774 | 333.1545
1411.9417 | 401.7249 | 333.2726
1412.9417 | 401.5727 | 333.3935
1413.9417 | 401.5366 | 333.4872
1414.9417 | 401.3798 | 333.6104
1415.9417 | 401.2391 | 333.7096
1416.9417 | 401.2758 | 333.829
1417.9417 | 401.1905 | 333.9301
1418.9417 | 401.1301 | 334.0359
1419.9417 | 401.0599 | 334.1462
1420.9417 | 401.0581 | 334.2398
1421.9417 | 400.9739 | 334.3577
1422.9417 | 401.0019 | 334.4606
1423.9417 | 400.9956 | 334.5577
1424.9417 | 401.027 | 334.676
1425.9417 | 401.0249 | 334.7734
1426.9417 | 400.9337 | 334.8875
1427.9417 | 400.9781 | 334.9653
1428.9417 | 401.0386 | 335.0806
1429.9417 | 401.1059 | 335.1918
1430.9417 | 401.1377 | 335.3052
1431.9417 | 401.0018 | 335.4048
1432.9417 | 401.0012 | 335.5107
1433.9417 | 401.0063 | 335.6078
1434.9417 | 400.9305 | 335.6967
1435.9417 | 400.9048 | 335.824
1436.9417 | 400.9513 | 335.9356
1437.9417 | 400.9989 | 336.0266
1438.9417 | 401.121 | 336.1223
1439.9417 | 401.224 | 336.2359
1440.9417 | 401.2748 | 336.3301
1441.9417 | 401.2799 | 336.4408
1442.9417 | 401.3064 | 336.5277
1443.9417 | 401.3167 | 336.6286
1444.9417 | 401.3583 | 336.7358
1445.9417 | 401.3992 | 336.8385
1446.9417 | 401.448 | 336.9494
1447.9417 | 401.4604 | 337.0373
1448.9417 | 401.3779 | 337.1493
1449.9417 | 401.4465 | 337.2475
1450.9417 | 401.4374 | 337.328
1451.9417 | 401.2852 | 337.4263
1452.9417 | 401.2522 | 337.5326
1453.9417 | 401.2852 | 337.6385
1454.9417 | 401.3374 | 337.7324
1455.9417 | 401.3261 | 337.8445
1456.9417 | 401.3343 | 337.9405
1457.9417 | 401.3762 | 338.0307
1458.9417 | 401.4467 | 338.1223
1459.9417 | 401.4021 | 338.2253
1460.9417 | 401.4231 | 338.3206
1461.9417 | 401.3752 | 338.4304
1462.9417 | 401.2564 | 338.528
1463.9417 | 401.0901 | 338.6283
1464.9417 | 400.9101 | 338.73
1465.9417 | 400.8877 | 338.8187
1466.9417 | 400.9245 | 338.9122
1467.9417 | 400.9055 | 339.0137
1468.9417 | 400.931 | 339.1002
1469.9417 | 400.8816 | 339.202
1470.9417 | 400.9619 | 339.2911
1471.9417 | 400.9697 | 339.3933
1472.9417 | 401.014 | 339.4854
1473.9417 | 401.0224 | 339.5741
1474.9417 | 401.0016 | 339.679
1475.9417 | 401.1262 | 339.7678
1476.9417 | 401.1627 | 339.8463
1477.9417 | 401.2088 | 339.9517
1478.9417 | 401.2397 | 340.0457
1479.9417 | 401.1876 | 340.1436
1480.9417 | 401.0749 | 340.2183
1481.9417 | 401.0572 | 340.3204
1482.9417 | 400.9504 | 340.4165
1483.9417 | 400.7682 | 340.5196
1484.9417 | 400.8398 | 340.607
1485.9417 | 400.9248 | 340.6956
1486.9417 | 400.9148 | 340.777
1487.9417 | 400.9353 | 340.8864
1488.9417 | 400.9597 | 340.9735
1489.9417 | 401.0294 | 341.0779
1490.9417 | 400.9432 | 341.1707
1491.9417 | 400.9106 | 341.271
1492.9417 | 400.8934 | 341.3466
1493.9417 | 400.9787 | 341.4283
1494.9417 | 401.0146 | 341.5492
1495.9417 | 401.039 | 341.6162
1496.9417 | 401.1745 | 341.7423
1497.9417 | 401.2296 | 341.8344
1498.9417 | 401.2935 | 341.9281
1499.9417 | 401.2117 | 342.0212
1500.9417 | 401.1832 | 342.1197
1501.9417 | 401.0719 | 342.2017
1502.9417 | 401.2408 | 342.2892
1503.9417 | 401.2511 | 342.3915
1504.9417 | 401.1578 | 342.4848
1505.9417 | 401.1687 | 342.5724
1506.9417 | 401.2826 | 342.6756
1507.9417 | 401.3687 | 342.7552
1508.9417 | 401.4909 | 342.8513
1509.9417 | 401.4231 | 342.934
1510.9417 | 401.5342 | 343.0267
1511.9417 | 401.6336 | 343.1282
1512.9417 | 401.6788 | 343.2086
1513.9417 | 401.687 | 343.3012
1514.9417 | 401.724 | 343.3856
1515.9417 | 401.9248 | 343.4771
1516.9417 | 401.9564 | 343.5661
1517.9417 | 402.0281 | 343.6494
1518.9417 | 402.0369 | 343.7445
1519.9417 | 402.0552 | 343.8435
1520.9417 | 402.0846 | 343.922
1521.9417 | 402.031 | 344.0135
1522.9417 | 401.9279 | 344.1071
1523.9417 | 401.8325 | 344.1885
1524.9417 | 401.8613 | 344.2748
1525.9417 | 401.658 | 344.3624
1526.9417 | 401.5961 | 344.459
1527.9417 | 401.7277 | 344.5287
1528.9417 | 401.7787 | 344.6312
1529.9417 | 401.8455 | 344.7159
1530.9417 | 401.9044 | 344.8013
1531.9417 | 401.8823 | 344.8885
1532.9417 | 401.891 | 344.9793
1533.9417 | 401.7808 | 345.0467
1534.9417 | 401.6531 | 345.1401
1535.9417 | 401.6427 | 345.225
1536.9417 | 401.6406 | 345.3032
1537.9417 | 401.6082 | 345.3911
1538.9417 | 401.4389 | 345.4764
1539.9417 | 401.281 | 345.5578
1540.9417 | 401.2308 | 345.6352
1541.9417 | 401.1649 | 345.7234
1542.9417 | 401.1479 | 345.7683
1543.9417 | 401.2501 | 345.8925
1544.9417 | 401.3358 | 345.9426
1545.9417 | 401.2825 | 346.0233
1546.9417 | 401.3335 | 346.1294
1547.9417 | 401.3124 | 346.1969
1548.9417 | 401.3554 | 346.2986
1549.9417 | 401.3268 | 346.3714
1550.9417 | 401.1984 | 346.4573
1551.9417 | 401.1518 | 346.5288
1552.9417 | 401.0646 | 346.597
1553.9417 | 401.0431 | 346.6704
1554.9417 | 400.9622 | 346.7435
1555.9417 | 400.9014 | 346.8444
1556.9417 | 400.8892 | 346.9147
1557.9417 | 400.887 | 346.9652
1558.9417 | 400.9632 | 347.0534
1559.9417 | 400.9718 | 347.1314
1560.9417 | 400.9468 | 347.2073
1561.9417 | 400.8904 | 347.2723
1562.9417 | 400.8884 | 347.363
1563.9417 | 400.9471 | 347.4274
1564.9417 | 400.8768 | 347.4904
1565.9417 | 400.922 | 347.5555
1566.9417 | 400.9148 | 347.6381
1567.9417 | 400.9315 | 347.7195
1568.9417 | 401.0049 | 347.7849
1569.9417 | 401.0514 | 347.8563
1570.9417 | 401.1729 | 347.9154
1571.9417 | 401.2583 | 348.0066
1572.9417 | 401.2734 | 348.066
1573.9417 | 401.2438 | 348.1488
1574.9417 | 401.1939 | 348.2271
1575.9417 | 401.191 | 348.2634
1576.9417 | 401.2384 | 348.3536
1577.9417 | 401.1453 | 348.4026
1578.9417 | 401.2392 | 348.4912
1579.9417 | 401.2281 | 348.5478
1580.9417 | 401.1229 | 348.6254
1581.9417 | 400.947 | 348.6791
1582.9417 | 400.8969 | 348.7583
1583.9417 | 400.795 | 348.8305
1584.9417 | 400.8229 | 348.8901
1585.9417 | 400.7916 | 348.9659
1586.9417 | 400.6728 | 349.016
1587.9417 | 400.8036 | 349.1125
1588.9417 | 400.9194 | 349.158
1589.9417 | 400.9107 | 349.2351
1590.9417 | 401.0228 | 349.2967
1591.9417 | 401.0294 | 349.3544
1592.9417 | 401.0866 | 349.4384
1593.9417 | 401.1164 | 349.4993
1594.9417 | 401.1787 | 349.5691
1595.9417 | 401.24 | 349.6376
1596.9417 | 401.1199 | 349.6919
1597.9417 | 400.9808 | 349.7644
1598.9417 | 400.9172 | 349.8368
1599.9417 | 400.9283 | 349.8873
1600.9417 | 400.9403 | 349.9641
1601.9417 | 400.9741 | 350.009
1602.9417 | 400.9564 | 350.0855
1603.9417 | 400.9162 | 350.1587
1604.9417 | 401.0423 | 350.2126
1605.9417 | 401.1695 | 350.2685
1606.9417 | 401.1866 | 350.3462
1607.9417 | 401.1867 | 350.413
1608.9417 | 401.3586 | 350.4687
1609.9417 | 401.5474 | 350.5276
1610.9417 | 401.6024 | 350.579
1611.9417 | 401.6083 | 350.6304
1612.9417 | 401.5885 | 350.6865
1613.9417 | 401.6535 | 350.7555
1614.9417 | 401.6046 | 350.803
1615.9417 | 401.5801 | 350.8709
1616.9417 | 401.5641 | 350.9252
1617.9417 | 401.4753 | 350.9878
1618.9417 | 401.3704 | 351.0435
1619.9417 | 401.3949 | 351.1081
1620.9417 | 401.3976 | 351.1812
1621.9417 | 401.4361 | 351.2354
1622.9417 | 401.5043 | 351.2775
1623.9417 | 401.632 | 351.3382
1624.9417 | 401.7306 | 351.3948
1625.9417 | 401.7952 | 351.4497
1626.9417 | 401.8456 | 351.5078
1627.9417 | 401.7611 | 351.5766
1628.9417 | 401.8031 | 351.6308
1629.9417 | 401.7854 | 351.6878
1630.9417 | 401.7361 | 351.7391
1631.9417 | 401.7679 | 351.8009
1632.9417 | 401.7649 | 351.8539
1633.9417 | 401.7936 | 351.9052
1634.9417 | 401.6755 | 351.9695
1635.9417 | 401.7257 | 352.0304
1636.9417 | 401.6892 | 352.0706
1637.9417 | 401.7543 | 352.1382
1638.9417 | 401.7436 | 352.1858
1639.9417 | 401.6164 | 352.2391
1640.9417 | 401.5664 | 352.305
1641.9417 | 401.6371 | 352.3366
1642.9417 | 401.7688 | 352.4118
1643.9417 | 401.7737 | 352.4543
1644.9417 | 401.7068 | 352.5106
1645.9417 | 401.5653 | 352.5534
1646.9417 | 401.4399 | 352.6172
1647.9417 | 401.3881 | 352.6708
1648.9417 | 401.4344 | 352.7137
1649.9417 | 401.3966 | 352.7661
1650.9417 | 401.5358 | 352.8308
1651.9417 | 401.5901 | 352.8657
1652.9417 | 401.6015 | 352.9104
1653.9417 | 401.5476 | 352.9596
1654.9417 | 401.3802 | 353.0142
1655.9417 | 401.3128 | 353.0731
1656.9417 | 401.3808 | 353.1145
1657.9417 | 401.4365 | 353.1626
1658.9417 | 401.4356 | 353.2229
1659.9417 | 401.3654 | 353.2734
1660.9417 | 401.3474 | 353.3037
1661.9417 | 401.3856 | 353.3729
1662.9417 | 401.3892 | 353.4193
1663.9417 | 401.4562 | 353.4722
1664.9417 | 401.5185 | 353.5123
1665.9417 | 401.6402 | 353.5713
1666.9417 | 401.7713 | 353.6116
1667.9417 | 401.8448 | 353.6623
1668.9417 | 401.9778 | 353.7074
1669.9417 | 401.9696 | 353.7813
1670.9417 | 402.0487 | 353.8287
1671.9417 | 402.112 | 353.8896
1672.9417 | 402.136 | 353.9371
1673.9417 | 402.171 | 353.991
1674.9417 | 402.0837 | 354.048
1675.9417 | 402.0714 | 354.0994
1676.9417 | 401.9472 | 354.1479
1677.9417 | 401.972 | 354.203
1678.9417 | 401.9913 | 354.2527
1679.9417 | 401.9933 | 354.2879
1680.9417 | 402.0074 | 354.3516
1681.9417 | 402.0035 | 354.3901
1682.9417 | 401.9691 | 354.4276
1683.9417 | 401.9236 | 354.4915
1684.9417 | 401.9775 | 354.5118
1685.9417 | 402.0244 | 354.584
1686.9417 | 402.0989 | 354.631
1687.9417 | 402.0882 | 354.6694
1688.9417 | 402.0816 | 354.7222
1689.9417 | 402.038 | 354.7468
1690.9417 | 402.0472 | 354.8029
1691.9417 | 402.0721 | 354.8523
1692.9417 | 402.0613 | 354.8898
1693.9417 | 401.9633 | 354.9241
1694.9417 | 401.9793 | 354.9815
1695.9417 | 401.9304 | 355.0144
1696.9417 | 401.8736 | 355.0632
1697.9417 | 401.8337 | 355.1039
1698.9417 | 402.0002 | 355.1471
1699.9417 | 402.0986 | 355.1797
1700.9417 | 402.1049 | 355.2409
1701.9417 | 402.0733 | 355.264
1702.9417 | 402.1296 | 355.3141
1703.9417 | 402.2176 | 355.3594
1704.9417 | 402.3001 | 355.3956
1705.9417 | 402.225 | 355.446
1706.9417 | 402.1345 | 355.4822
1707.9417 | 401.9872 | 355.516
1708.9417 | 401.9152 | 355.5572
1709.9417 | 401.8669 | 355.6
1710.9417 | 401.8992 | 355.6392
1711.9417 | 401.8198 | 355.6845
1712.9417 | 401.705 | 355.7224
1713.9417 | 401.6569 | 355.7648
1714.9417 | 401.6948 | 355.8112
1715.9417 | 401.7398 | 355.8509
1716.9417 | 401.5544 | 355.8998
1717.9417 | 401.4817 | 355.9307
1718.9417 | 401.428 | 355.9627
1719.9417 | 401.3936 | 355.9906
1720.9417 | 401.503 | 356.0439
1721.9417 | 401.58 | 356.0911
1722.9417 | 401.4587 | 356.1168
1723.9417 | 401.4067 | 356.1669
1724.9417 | 401.315 | 356.1885
1725.9417 | 401.349 | 356.2527
1726.9417 | 401.3187 | 356.2892
1727.9417 | 401.2888 | 356.3245
1728.9417 | 401.2927 | 356.3525
1729.9417 | 401.2738 | 356.4054
1730.9417 | 401.3255 | 356.438
1731.9417 | 401.4456 | 356.4884
1732.9417 | 401.5368 | 356.518
1733.9417 | 401.6269 | 356.5669
1734.9417 | 401.4436 | 356.6044
1735.9417 | 401.4825 | 356.6164
1736.9417 | 401.4821 | 356.6787
1737.9417 | 401.6074 | 356.7152
1738.9417 | 401.7333 | 356.7289
1739.9417 | 401.8858 | 356.7856
1740.9417 | 401.8296 | 356.8177
1741.9417 | 401.8156 | 356.8543
1742.9417 | 401.7361 | 356.8807
1743.9417 | 401.6705 | 356.9347
1744.9417 | 401.6431 | 356.9658
1745.9417 | 401.5329 | 356.9978
1746.9417 | 401.4643 | 357.022
1747.9417 | 401.4945 | 357.0669
1748.9417 | 401.4928 | 357.1036
1749.9417 | 401.544 | 357.1361
1750.9417 | 401.5705 | 357.1675
1751.9417 | 401.6213 | 357.2014
1752.9417 | 401.7374 | 357.2289
1753.9417 | 401.7651 | 357.269
1754.9417 | 401.7198 | 357.3011
1755.9417 | 401.7887 | 357.3377
1756.9417 | 401.8623 | 357.3612
1757.9417 | 401.9431 | 357.3883
1758.9417 | 402.0213 | 357.4459
1759.9417 | 401.9658 | 357.4743
1760.9417 | 401.9052 | 357.506
1761.9417 | 401.8693 | 357.5503
1762.9417 | 401.8888 | 357.5761
1763.9417 | 401.7847 | 357.6192
1764.9417 | 401.6285 | 357.6481
1765.9417 | 401.6277 | 357.6811
1766.9417 | 401.6869 | 357.7005
1767.9417 | 401.6712 | 357.7456
1768.9417 | 401.7393 | 357.7648
1769.9417 | 401.7575 | 357.8212
1770.9417 | 401.7355 | 357.8564
1771.9417 | 401.7197 | 357.8804
1772.9417 | 401.7613 | 357.9234
1773.9417 | 401.7745 | 357.9599
1774.9417 | 401.7932 | 357.9799
1775.9417 | 401.721 | 358.0178
1776.9417 | 401.7308 | 358.0526
1777.9417 | 401.8095 | 358.0792
1778.9417 | 401.7802 | 358.1136
1779.9417 | 401.8357 | 358.1424
1780.9417 | 401.7834 | 358.1792
1781.9417 | 401.7462 | 358.2109
1782.9417 | 401.8778 | 358.2377
1783.9417 | 402.0184 | 358.266
1784.9417 | 402.0982 | 358.2902
1785.9417 | 402.1017 | 358.324
1786.9417 | 402.1391 | 358.3655
1787.9417 | 402.1908 | 358.3967
1788.9417 | 402.1966 | 358.4356
1789.9417 | 402.1022 | 358.4435
1790.9417 | 402.0613 | 358.4612
1791.9417 | 402.1507 | 358.4984
1792.9417 | 402.097 | 358.5386
1793.9417 | 402.1036 | 358.561
1794.9417 | 402.069 | 358.6058
1795.9417 | 402.1063 | 358.6205
1796.9417 | 401.9537 | 358.6482
1797.9417 | 401.8876 | 358.6803
1798.9417 | 402.0267 | 358.7139
1799.9417 | 402.0425 | 358.7437
1800.9417 | 401.9486 | 358.7754
1801.9417 | 402.0122 | 358.7966
1802.9417 | 402.0341 | 358.8291
1803.9417 | 402.0079 | 358.8621
1804.9417 | 401.8212 | 358.8924
1805.9417 | 401.6631 | 358.921
1806.9417 | 401.5947 | 358.9519
1807.9417 | 401.4648 | 358.9867
1808.9417 | 401.4307 | 358.9997
1809.9417 | 401.3846 | 359.039
1810.9417 | 401.3425 | 359.0778
1811.9417 | 401.3835 | 359.0958
1812.9417 | 401.3498 | 359.1279
1813.9417 | 401.4191 | 359.1389
1814.9417 | 401.4338 | 359.193
1815.9417 | 401.2515 | 359.2155
1816.9417 | 401.211 | 359.2402
1817.9417 | 401.3368 | 359.2676
1818.9417 | 401.4022 | 359.3026
1819.9417 | 401.403 | 359.3224
1820.9417 | 401.3928 | 359.3582
1821.9417 | 401.3795 | 359.377
1822.9417 | 401.467 | 359.4213
1823.9417 | 401.3939 | 359.4447
1824.9417 | 401.3928 | 359.4568
1825.9417 | 401.5158 | 359.4924
1826.9417 | 401.6053 | 359.5144
1827.9417 | 401.6451 | 359.5532
1828.9417 | 401.7693 | 359.5634
1829.9417 | 401.8874 | 359.597
1830.9417 | 401.9299 | 359.6201
1831.9417 | 402.0719 | 359.6667
1832.9417 | 402.2358 | 359.6935
1833.9417 | 402.3619 | 359.7157
1834.9417 | 402.3301 | 359.7333
1835.9417 | 402.3352 | 359.7742
1836.9417 | 402.3838 | 359.7865
1837.9417 | 402.4557 | 359.8185
1838.9417 | 402.5558 | 359.8428
1839.9417 | 402.467 | 359.8689
1840.9417 | 402.3101 | 359.8868
1841.9417 | 402.265 | 359.9064
1842.9417 | 402.1707 | 359.9338
1843.9417 | 402.1869 | 359.9769
1844.9417 | 402.175 | 360.011
1845.9417 | 402.1851 | 360.0384
1846.9417 | 402.0938 | 360.0491
1847.9417 | 402.0049 | 360.0927
1848.9417 | 401.9603 | 360.1162
1849.9417 | 401.8392 | 360.1427
1850.9417 | 401.7726 | 360.1654
1851.9417 | 401.7105 | 360.1939
1852.9417 | 401.6319 | 360.2193
1853.9417 | 401.5501 | 360.2453
1854.9417 | 401.5611 | 360.2778
1855.9417 | 401.5007 | 360.2983
1856.9417 | 401.3669 | 360.3062
1857.9417 | 401.4141 | 360.3383
1858.9417 | 401.4392 | 360.3807
1859.9417 | 401.3922 | 360.3976
1860.9417 | 401.429 | 360.4167
1861.9417 | 401.4389 | 360.4427
1862.9417 | 401.431 | 360.4668
1863.9417 | 401.4977 | 360.5035
1864.9417 | 401.6391 | 360.5278
1865.9417 | 401.6428 | 360.5572
1866.9417 | 401.7173 | 360.5738
1867.9417 | 401.7688 | 360.5943
1868.9417 | 401.7287 | 360.6222
1869.9417 | 401.7095 | 360.643
1870.9417 | 401.7301 | 360.6776
1871.9417 | 401.7761 | 360.6772
1872.9417 | 401.831 | 360.7179
1873.9417 | 401.8549 | 360.7394
1874.9417 | 401.7253 | 360.7516
1875.9417 | 401.7944 | 360.7797
1876.9417 | 401.8048 | 360.812
1877.9417 | 401.8028 | 360.8315
1878.9417 | 401.8352 | 360.8564
1879.9417 | 401.9466 | 360.8782
1880.9417 | 401.9179 | 360.8893
1881.9417 | 401.9438 | 360.913
1882.9417 | 401.9735 | 360.9351
1883.9417 | 401.9022 | 360.9468
1884.9417 | 401.8189 | 360.9714
1885.9417 | 401.7994 | 361.0046
1886.9417 | 401.8191 | 361.0205
1887.9417 | 401.8476 | 361.0219
1888.9417 | 401.9396 | 361.0641
1889.9417 | 401.9818 | 361.0995
1890.9417 | 401.8817 | 361.1117
1891.9417 | 401.9736 | 361.1292
1892.9417 | 402.0218 | 361.1631
1893.9417 | 402.0115 | 361.1771
1894.9417 | 402.0579 | 361.1946
1895.9417 | 401.9858 | 361.2286
1896.9417 | 401.9152 | 361.2493
1897.9417 | 401.7268 | 361.2568
1898.9417 | 401.6609 | 361.2885
1899.9417 | 401.7546 | 361.3035
1900.9417 | 401.8915 | 361.3145
1901.9417 | 401.8814 | 361.3487
1902.9417 | 401.8921 | 361.3789
1903.9417 | 401.7675 | 361.3935
1904.9417 | 401.5818 | 361.4015
1905.9417 | 401.5227 | 361.4306
1906.9417 | 401.5509 | 361.446
1907.9417 | 401.5834 | 361.4826
1908.9417 | 401.5645 | 361.4955
1909.9417 | 401.54 | 361.5192
1910.9417 | 401.5845 | 361.533
1911.9417 | 401.7098 | 361.5533
1912.9417 | 401.7947 | 361.5714
1913.9417 | 401.7869 | 361.5981
1914.9417 | 401.6885 | 361.6173
1915.9417 | 401.7052 | 361.6374
1916.9417 | 401.7508 | 361.6611
1917.9417 | 401.7752 | 361.6761
1918.9417 | 401.7449 | 361.6988
1919.9417 | 401.7601 | 361.7069
1920.9417 | 401.8667 | 361.7417
1921.9417 | 402.0072 | 361.7679
1922.9417 | 402.0737 | 361.7445
1923.9417 | 402.1216 | 361.8061
1924.9417 | 402.1207 | 361.8262
1925.9417 | 401.9799 | 361.8465
1926.9417 | 401.9332 | 361.8683
1927.9417 | 402.0048 | 361.8743
1928.9417 | 402.0713 | 361.8994
1929.9417 | 402.0694 | 361.9223
1930.9417 | 402.1028 | 361.9323
1931.9417 | 402.0418 | 361.9499
1932.9417 | 402.0399 | 361.9839
1933.9417 | 401.9858 | 362.0006
1934.9417 | 401.7958 | 362.0157
1935.9417 | 401.84 | 362.0335
1936.9417 | 401.8099 | 362.0641
1937.9417 | 401.7491 | 362.0655
1938.9417 | 401.881 | 362.1122
1939.9417 | 401.8909 | 362.1178
1940.9417 | 401.9354 | 362.1318
1941.9417 | 401.8436 | 362.1624
1942.9417 | 401.824 | 362.186
1943.9417 | 401.8851 | 362.1966
1944.9417 | 401.8784 | 362.2172
1945.9417 | 401.7429 | 362.2538
1946.9417 | 401.6391 | 362.2507
1947.9417 | 401.4352 | 362.2847
1948.9417 | 401.3846 | 362.3018
1949.9417 | 401.3717 | 362.3195
1950.9417 | 401.4233 | 362.3386
1951.9417 | 401.4 | 362.3488
1952.9417 | 401.3504 | 362.3798
1953.9417 | 401.3702 | 362.3915
1954.9417 | 401.4367 | 362.4195
1955.9417 | 401.5491 | 362.4438
1956.9417 | 401.4203 | 362.4459
1957.9417 | 401.3101 | 362.4544
1958.9417 | 401.3548 | 362.5062
1959.9417 | 401.3919 | 362.5128
1960.9417 | 401.4442 | 362.5333
1961.9417 | 401.5174 | 362.5455
1962.9417 | 401.5994 | 362.5684
1963.9417 | 401.7086 | 362.5891
1964.9417 | 401.8315 | 362.6089
1965.9417 | 401.8621 | 362.6199
1966.9417 | 401.8799 | 362.6478
1967.9417 | 401.8578 | 362.661
1968.9417 | 401.8942 | 362.6788
1969.9417 | 401.9779 | 362.7057
1970.9417 | 401.9398 | 362.7106
1971.9417 | 402.0169 | 362.7226
1972.9417 | 402.064 | 362.7607
1973.9417 | 402.1095 | 362.7673
1974.9417 | 401.9124 | 362.7827
1975.9417 | 401.7796 | 362.8179
1976.9417 | 401.734 | 362.8082
1977.9417 | 401.7142 | 362.8461
1978.9417 | 401.6131 | 362.8593
1979.9417 | 401.6378 | 362.8865
1980.9417 | 401.5791 | 362.891
1981.9417 | 401.5354 | 362.9229
1982.9417 | 401.6306 | 362.9302
1983.9417 | 401.7445 | 362.9461
1984.9417 | 401.7777 | 362.9636
1985.9417 | 401.7435 | 362.9827
1986.9417 | 401.684 | 363.0139
1987.9417 | 401.5756 | 363.0176
1988.9417 | 401.5156 | 363.0427
1989.9417 | 401.5182 | 363.0508
1990.9417 | 401.6143 | 363.0717
1991.9417 | 401.685 | 363.0974
1992.9417 | 401.7564 | 363.0945
1993.9417 | 401.6972 | 363.1135
1994.9417 | 401.8509 | 363.1481
1995.9417 | 401.823 | 363.1463
1996.9417 | 401.7935 | 363.1657
1997.9417 | 401.7746 | 363.1789
1998.9417 | 401.7882 | 363.2067
1999.9417 | 401.8518 | 363.2355
2000.9417 | 401.8316 | 363.2641
2001.9417 | 401.7844 | 363.2665
2002.9417 | 401.725 | 363.2818
2003.9417 | 401.6632 | 363.3121
2004.9417 | 401.614 | 363.3229
2005.9417 | 401.5747 | 363.343
2006.9417 | 401.5954 | 363.3622
2007.9417 | 401.6833 | 363.3923
2008.9417 | 401.8345 | 363.4048
2009.9417 | 401.9232 | 363.4128
2010.9417 | 401.9663 | 363.426
2011.9417 | 401.9937 | 363.451
2012.9417 | 402.0015 | 363.4676
2013.9417 | 401.9542 | 363.4814
2014.9417 | 401.9125 | 363.493
2015.9417 | 401.907 | 363.5195
2016.9417 | 401.9931 | 363.5385
2017.9417 | 402.0221 | 363.5498
2018.9417 | 402.1274 | 363.5715
2019.9417 | 402.0197 | 363.5942
2020.9417 | 401.9494 | 363.6055
2021.9417 | 401.8849 | 363.6382
2022.9417 | 401.9112 | 363.6408
2023.9417 | 401.9145 | 363.6312
2024.9417 | 401.9162 | 363.6776
2025.9417 | 402.0088 | 363.6885
2026.9417 | 402.0331 | 363.7125
2027.9417 | 402.0401 | 363.7146
2028.9417 | 402.0445 | 363.7421
2029.9417 | 402.0655 | 363.7593
2030.9417 | 402.0741 | 363.7708
2031.9417 | 402.0936 | 363.7796
2032.9417 | 402.0738 | 363.809
2033.9417 | 402.0373 | 363.8073
2034.9417 | 401.9964 | 363.8258
2035.9417 | 402.0481 | 363.8589
2036.9417 | 402.1573 | 363.8642
2037.9417 | 401.7714 | 363.8713
2038.9417 | 401.677 | 363.9024
2039.9417 | 401.6479 | 363.919
2040.9417 | 401.5528 | 363.9262
2041.9417 | 401.54 | 363.9475
2042.9417 | 401.5125 | 363.9679
2043.9417 | 401.4843 | 363.9874
2044.9417 | 401.5679 | 364.006
2045.9417 | 401.6439 | 364.0137
2046.9417 | 401.7852 | 364.0405
2047.9417 | 401.8354 | 364.0536
2048.9417 | 401.769 | 364.0596
2049.9417 | 401.8342 | 364.0849
2050.9417 | 401.8317 | 364.0885
2051.9417 | 401.8243 | 364.113
2052.9417 | 401.8258 | 364.1226
2053.9417 | 401.9437 | 364.1383
2054.9417 | 401.9574 | 364.1458
2055.9417 | 401.8613 | 364.1555
2056.9417 | 401.8739 | 364.1717
2057.9417 | 401.9429 | 364.1831
2058.9417 | 401.8488 | 364.2061
2059.9417 | 401.906 | 364.2081
2060.9417 | 401.9662 | 364.2466
2061.9417 | 401.8436 | 364.2478
2062.9417 | 401.7868 | 364.265
2063.9417 | 401.7849 | 364.2881
2064.9417 | 401.7732 | 364.298
2065.9417 | 401.8429 | 364.3075
2066.9417 | 401.9399 | 364.3158
2067.9417 | 401.9713 | 364.3221
2068.9417 | 402.003 | 364.3515
2069.9417 | 401.942 | 364.3683
2070.9417 | 401.9417 | 364.3729
2071.9417 | 401.9482 | 364.3808
2072.9417 | 401.9007 | 364.3915
2073.9417 | 401.8915 | 364.41
2074.9417 | 401.9321 | 364.4123
2075.9417 | 401.8359 | 364.4407
2076.9417 | 401.8064 | 364.4461
2077.9417 | 401.7312 | 364.462
2078.9417 | 401.6986 | 364.4829
2079.9417 | 401.7356 | 364.4859
2080.9417 | 401.8837 | 364.4852
2081.9417 | 401.9156 | 364.5084
2082.9417 | 402.01 | 364.5208
2083.9417 | 401.9838 | 364.5453
2084.9417 | 401.9892 | 364.5468
2085.9417 | 401.887 | 364.5622
2086.9417 | 401.7425 | 364.5764
2087.9417 | 401.734 | 364.5721
2088.9417 | 401.8477 | 364.6002
2089.9417 | 401.935 | 364.6057
2090.9417 | 402.0186 | 364.61
2091.9417 | 401.9568 | 364.6274
2092.9417 | 401.8877 | 364.6574
2093.9417 | 401.9517 | 364.6674
2094.9417 | 402.1423 | 364.6793
2095.9417 | 402.2434 | 364.6837
2096.9417 | 402.3163 | 364.7055
2097.9417 | 402.2606 | 364.7039
2098.9417 | 402.2392 | 364.7138
2099.9417 | 402.1765 | 364.7201
2100.9417 | 402.1801 | 364.7404
2101.9417 | 402.0824 | 364.763
2102.9417 | 402.1129 | 364.7675
2103.9417 | 402.163 | 364.7738
2104.9417 | 402.1844 | 364.7899
2105.9417 | 402.2473 | 364.8119
2106.9417 | 402.2279 | 364.8278
2107.9417 | 402.2471 | 364.8262
2108.9417 | 402.2682 | 364.8439
2109.9417 | 402.2838 | 364.8621
2110.9417 | 402.3845 | 364.8704
2111.9417 | 402.4248 | 364.8801
2112.9417 | 402.3266 | 364.8945
2113.9417 | 402.414 | 364.9176
2114.9417 | 402.5193 | 364.9258
2115.9417 | 402.4405 | 364.9419
2116.9417 | 402.3696 | 364.9683
2117.9417 | 402.3327 | 364.9755
2118.9417 | 402.2941 | 364.992
2119.9417 | 402.2634 | 364.9934
2120.9417 | 402.1625 | 365.0115
2121.9417 | 402.1431 | 365.0318
2122.9417 | 401.9759 | 365.037
2123.9417 | 401.8368 | 365.055
2124.9417 | 401.6823 | 365.0634
2125.9417 | 401.6144 | 365.0924
2126.9417 | 401.6207 | 365.103
2127.9417 | 401.6044 | 365.1082
2128.9417 | 401.527 | 365.116
2129.9417 | 401.3903 | 365.1382
2130.9417 | 401.3981 | 365.1442
2131.9417 | 401.1357 | 365.1644
2132.9417 | 401.0392 | 365.1718
2133.9417 | 401.1093 | 365.1845
2134.9417 | 401.0211 | 365.196
2135.9417 | 401.061 | 365.2083
2136.9417 | 401.0785 | 365.2232
2137.9417 | 401.1089 | 365.2298
2138.9417 | 401.159 | 365.2471
2139.9417 | 401.2397 | 365.2681
2140.9417 | 401.2766 | 365.2694
2141.9417 | 401.3007 | 365.2834
2142.9417 | 401.269 | 365.2863
2143.9417 | 401.4142 | 365.2912
2144.9417 | 401.5217 | 365.3112
2145.9417 | 401.5838 | 365.3111
2146.9417 | 401.578 | 365.3108
2147.9417 | 401.5886 | 365.3143
2148.9417 | 401.6767 | 365.3451
2149.9417 | 401.7418 | 365.3403
2150.9417 | 401.7628 | 365.3665
2151.9417 | 401.7608 | 365.3891
2152.9417 | 401.769 | 365.3884
2153.9417 | 401.9048 | 365.4033
2154.9417 | 402.0122 | 365.399
2155.9417 | 402.1122 | 365.4263
2156.9417 | 402.2167 | 365.4261
2157.9417 | 402.3185 | 365.4364
2158.9417 | 402.3297 | 365.4547
2159.9417 | 402.2044 | 365.4517
2160.9417 | 402.2755 | 365.4768
2161.9417 | 402.3718 | 365.4829
2162.9417 | 402.4343 | 365.4981
2163.9417 | 402.4816 | 365.5124
2164.9417 | 402.5269 | 365.5103
2165.9417 | 402.6037 | 365.5184
2166.9417 | 402.708 | 365.5281
2167.9417 | 402.7198 | 365.5329
2168.9417 | 402.7585 | 365.564
2169.9417 | 402.6414 | 365.5796
2170.9417 | 402.4613 | 365.5821
2171.9417 | 402.3886 | 365.6022
2172.9417 | 402.4499 | 365.617
2173.9417 | 402.4417 | 365.6236
2174.9417 | 402.4877 | 365.6444
2175.9417 | 402.5313 | 365.6412
2176.9417 | 402.4246 | 365.6616
2177.9417 | 402.2814 | 365.6719
2178.9417 | 402.2953 | 365.6756
2179.9417 | 402.3087 | 365.6996
2180.9417 | 402.2875 | 365.7063
2181.9417 | 402.4003 | 365.71
2182.9417 | 402.4113 | 365.7266
2183.9417 | 402.3865 | 365.7329
2184.9417 | 402.2307 | 365.7526
2185.9417 | 402.2098 | 365.7505
2186.9417 | 402.1462 | 365.767
2187.9417 | 402.1764 | 365.778
2188.9417 | 402.1305 | 365.7934
2189.9417 | 402.0465 | 365.8093
2190.9417 | 402.1156 | 365.8237
2191.9417 | 402.1066 | 365.8391
2192.9417 | 401.9912 | 365.8507
2193.9417 | 401.9135 | 365.8113
2194.9417 | 401.8195 | 365.8674
2195.9417 | 401.5859 | 365.8866
2196.9417 | 401.564 | 365.8826
2197.9417 | 401.4071 | 365.8921
2198.9417 | 401.4463 | 365.914
2199.9417 | 401.3202 | 365.9208
2200.9417 | 401.3224 | 365.9264
2201.9417 | 401.3238 | 365.936
2202.9417 | 401.3829 | 365.9381
2203.9417 | 401.3854 | 365.9466
2204.9417 | 401.4538 | 365.9686
2205.9417 | 401.3401 | 365.9812
2206.9417 | 401.4192 | 365.9806
2207.9417 | 401.432 | 365.9983
2208.9417 | 401.3493 | 365.9994
2209.9417 | 401.356 | 366.0104
2210.9417 | 401.2347 | 366.0305
2211.9417 | 401.1845 | 366.0201
2212.9417 | 401.292 | 366.0374
2213.9417 | 401.3632 | 366.0605
2214.9417 | 401.369 | 366.0521
2215.9417 | 401.2113 | 366.07
2216.9417 | 401.2045 | 366.0746
2217.9417 | 401.1836 | 366.0882
2218.9417 | 401.2134 | 366.0924
2219.9417 | 401.3115 | 366.1
2220.9417 | 401.4337 | 366.1049
2221.9417 | 401.4702 | 366.111
2222.9417 | 401.4485 | 366.1185
2223.9417 | 401.4951 | 366.1385
2224.9417 | 401.5207 | 366.1264
2225.9417 | 401.6025 | 366.1393
2226.9417 | 401.6377 | 366.1549
2227.9417 | 401.6318 | 366.149
2228.9417 | 401.6189 | 366.1664
2229.9417 | 401.6182 | 366.1776
2230.9417 | 401.4567 | 366.1722
2231.9417 | 401.4443 | 366.1831
2232.9417 | 401.4093 | 366.1778
2233.9417 | 401.5437 | 366.188
2234.9417 | 401.5656 | 366.2158
2235.9417 | 401.5064 | 366.2097
2236.9417 | 401.5824 | 366.219
2237.9417 | 401.4803 | 366.2288
2238.9417 | 401.3835 | 366.2308
2239.9417 | 401.3743 | 366.2389
2240.9417 | 401.4487 | 366.2453
2241.9417 | 401.45 | 366.2524
2242.9417 | 401.5037 | 366.2558
2243.9417 | 401.5226 | 366.2536
2244.9417 | 401.423 | 366.2732
2245.9417 | 401.5079 | 366.2724
2246.9417 | 401.5815 | 366.2869
2247.9417 | 401.7273 | 366.2865
2248.9417 | 401.8186 | 366.3025
2249.9417 | 401.707 | 366.3093
2250.9417 | 401.7394 | 366.298
2251.9417 | 401.7668 | 366.3117
2252.9417 | 401.7966 | 366.3213
2253.9417 | 401.8465 | 366.3464
2254.9417 | 401.7856 | 366.3418
2255.9417 | 401.8062 | 366.343
2256.9417 | 401.9002 | 366.3537
2257.9417 | 401.7207 | 366.373
2258.9417 | 401.709 | 366.3679
2259.9417 | 401.7458 | 366.3794
2260.9417 | 401.8013 | 366.3832
2261.9417 | 401.9692 | 366.4043
2262.9417 | 402.098 | 366.4023
2263.9417 | 402.0841 | 366.4003
2264.9417 | 401.9563 | 366.4263
2265.9417 | 401.9863 | 366.4155
2266.9417 | 402.116 | 366.4412
2267.9417 | 402.1455 | 366.4586
2268.9417 | 402.2731 | 366.452
2269.9417 | 402.2695 | 366.4604
2270.9417 | 402.1615 | 366.4663
2271.9417 | 402.1774 | 366.4785
2272.9417 | 402.2044 | 366.4816
2273.9417 | 402.2785 | 366.4681
2274.9417 | 402.3945 | 366.4973
2275.9417 | 402.4136 | 366.5022
2276.9417 | 402.3403 | 366.5081
2277.9417 | 402.3986 | 366.4998
2278.9417 | 402.283 | 366.5294
2279.9417 | 402.2882 | 366.5251
2280.9417 | 402.2291 | 366.5312
2281.9417 | 402.2214 | 366.5379
2282.9417 | 402.2008 | 366.5424
2283.9417 | 402.1153 | 366.5589
2284.9417 | 402.0319 | 366.5361
2285.9417 | 401.9584 | 366.5708
2286.9417 | 401.9357 | 366.5733
2287.9417 | 401.912 | 366.5815
2288.9417 | 401.8799 | 366.5854
2289.9417 | 401.8798 | 366.6019
2290.9417 | 401.9 | 366.5922
2291.9417 | 401.8555 | 366.6016
2292.9417 | 401.84 | 366.6171
2293.9417 | 401.785 | 366.6362
2294.9417 | 401.7366 | 366.6246
2295.9417 | 401.6628 | 366.6397
2296.9417 | 401.7135 | 366.6581
2297.9417 | 401.6915 | 366.6563
2298.9417 | 401.4879 | 366.665
2299.9417 | 401.4996 | 366.6738
2300.9417 | 401.4934 | 366.6811
2301.9417 | 401.4 | 366.6827
2302.9417 | 401.3446 | 366.6852
2303.9417 | 401.4195 | 366.7026
2304.9417 | 401.6102 | 366.7086
2305.9417 | 401.514 | 366.7167
2306.9417 | 401.401 | 366.7169
2307.9417 | 401.2964 | 366.7166
2308.9417 | 401.2609 | 366.7251
2309.9417 | 401.3176 | 366.7373
2310.9417 | 401.3464 | 366.7403
2311.9417 | 401.3849 | 366.727
2312.9417 | 401.3961 | 366.7438
2313.9417 | 401.4331 | 366.7427
2314.9417 | 401.2948 | 366.7488
2315.9417 | 401.3625 | 366.7576
2316.9417 | 401.535 | 366.7678
2317.9417 | 401.4962 | 366.7595
2318.9417 | 401.3247 | 366.7689
2319.9417 | 401.2495 | 366.7739
2320.9417 | 401.3532 | 366.7962
2321.9417 | 401.3821 | 366.7838
2322.9417 | 401.2884 | 366.8059
2323.9417 | 401.3343 | 366.7926
2324.9417 | 401.0522 | 366.8124
2325.9417 | 401.0245 | 366.8087
2326.9417 | 401.1118 | 366.8141
2327.9417 | 401.1818 | 366.8089
2328.9417 | 401.2883 | 366.8181
2329.9417 | 401.4192 | 366.8312
2330.9417 | 401.5482 | 366.8242
2331.9417 | 401.5936 | 366.829
2332.9417 | 401.5906 | 366.8487
2333.9417 | 401.61 | 366.853
2334.9417 | 401.6172 | 366.8653
2335.9417 | 401.7122 | 366.8503
2336.9417 | 401.8444 | 366.8588
2337.9417 | 401.8436 | 366.8659
2338.9417 | 401.7974 | 366.8705
2339.9417 | 401.8593 | 366.874
2340.9417 | 401.9433 | 366.8776
2341.9417 | 401.8855 | 366.8868
2342.9417 | 401.8377 | 366.8897
2343.9417 | 401.9048 | 366.8859
2344.9417 | 401.9284 | 366.9018
2345.9417 | 402.0638 | 366.9014
2346.9417 | 402.1122 | 366.901
2347.9417 | 402.1916 | 366.9157
2348.9417 | 402.2469 | 366.9153
2349.9417 | 402.2512 | 366.9171
2350.9417 | 402.2081 | 366.9288
2351.9417 | 402.2896 | 366.9171
2352.9417 | 402.3056 | 366.9248
2353.9417 | 402.1738 | 366.9442
2354.9417 | 402.3078 | 366.938
2355.9417 | 402.4347 | 366.9519
2356.9417 | 402.4909 | 366.9558
2357.9417 | 402.4209 | 366.9626
2358.9417 | 402.3755 | 366.9601
2359.9417 | 402.1931 | 366.9726
2360.9417 | 402.1508 | 366.963
2361.9417 | 402.1341 | 366.9722
2362.9417 | 401.9534 | 366.9929
2363.9417 | 401.9093 | 366.9957
2364.9417 | 401.9418 | 366.9919
2365.9417 | 402.0454 | 367.0022
2366.9417 | 402.0718 | 367.0146
2367.9417 | 402.0525 | 367.0178
2368.9417 | 402.1151 | 367.01
2369.9417 | 402.1212 | 367.0283
2370.9417 | 402.1156 | 367.0371
2371.9417 | 402.1547 | 367.0235
2372.9417 | 402.2024 | 367.0263
2373.9417 | 402.1445 | 367.0445
2374.9417 | 402.1226 | 367.0404
2375.9417 | 402.1103 | 367.0495
2376.9417 | 402.018 | 367.0662
2377.9417 | 401.8409 | 367.0671
2378.9417 | 401.6481 | 367.0791
2379.9417 | 401.695 | 367.0778
2380.9417 | 401.7492 | 367.1007
2381.9417 | 401.703 | 367.102
2382.9417 | 401.6598 | 367.1142
2383.9417 | 401.6176 | 367.1044
2384.9417 | 401.5697 | 367.1196
2385.9417 | 401.5599 | 367.1245
2386.9417 | 401.6018 | 367.1219
2387.9417 | 401.6728 | 367.1328
2388.9417 | 401.6558 | 367.1286
2389.9417 | 401.61 | 367.14
2390.9417 | 401.62 | 367.1464
2391.9417 | 401.6902 | 367.1546
2392.9417 | 401.6893 | 367.1355
2393.9417 | 401.7156 | 367.1488
2394.9417 | 401.693 | 367.1635
2395.9417 | 401.5275 | 367.1537
2396.9417 | 401.4823 | 367.1778
2397.9417 | 401.4975 | 367.1595
2398.9417 | 401.4941 | 367.1834
2399.9417 | 401.4265 | 367.1947
2400.9417 | 401.2223 | 367.1903
2401.9417 | 401.0292 | 367.1938
2402.9417 | 401.0478 | 367.1957
2403.9417 | 401.928 | 367.1919
2404.9417 | 403.605 | 367.2103
2405.9417 | 405.9702 | 367.2069
2406.9417 | 408.7667 | 367.2144
2407.9417 | 412.1071 | 367.2196
2408.9417 | 415.7519 | 367.2271
2409.9417 | 419.2583 | 367.2222
2410.9417 | 422.6471 | 367.2204
2411.9417 | 425.8588 | 367.2419
2412.9417 | 428.6952 | 367.2518
2413.9417 | 431.0879 | 367.2817
2414.9417 | 433.228 | 367.2821
2415.9417 | 434.8758 | 367.3158
2416.9417 | 436.1017 | 367.3517
2417.9417 | 437.136 | 367.346
2418.9417 | 437.9549 | 367.4324
2419.9417 | 438.5734 | 367.4721
2420.9417 | 438.8649 | 367.5282
2421.9417 | 439.1272 | 367.5964
2422.9417 | 439.3338 | 367.6702
2423.9417 | 439.4527 | 367.7322
2424.9417 | 439.4142 | 367.8159
2425.9417 | 439.36 | 367.9296
2426.9417 | 439.3715 | 367.9881
2427.9417 | 439.2935 | 368.096
2428.9417 | 439.253 | 368.1912
2429.9417 | 439.2089 | 368.2983
2430.9417 | 439.1836 | 368.3934
2431.9417 | 439.1087 | 368.5112
2432.9417 | 439.0116 | 368.6272
2433.9417 | 438.9586 | 368.7293
2434.9417 | 438.9528 | 368.8679
2435.9417 | 438.8987 | 368.9824
2436.9417 | 438.8514 | 369.1136
2437.9417 | 438.8331 | 369.2228
2438.9417 | 438.7158 | 369.3325
2439.9417 | 438.7702 | 369.4583
2440.9417 | 438.8252 | 369.6071
2441.9417 | 438.705 | 369.7352
2442.9417 | 438.7019 | 369.8426
2443.9417 | 438.7291 | 369.9881
2444.9417 | 438.8689 | 370.1203
2445.9417 | 438.993 | 370.2547
2446.9417 | 439.0689 | 370.3871
2447.9417 | 439.179 | 370.5184
2448.9417 | 439.1627 | 370.6565
2449.9417 | 439.1152 | 370.7862
2450.9417 | 439.1664 | 370.9172
2451.9417 | 439.3859 | 371.0445
2452.9417 | 439.6486 | 371.1787
2453.9417 | 439.7697 | 371.3062
2454.9417 | 439.6585 | 371.4479
2455.9417 | 439.8053 | 371.5843
2456.9417 | 439.8625 | 371.7146
2457.9417 | 439.7697 | 371.8359
2458.9417 | 439.8592 | 371.9709
2459.9417 | 440.1238 | 372.0937
2460.9417 | 440.4065 | 372.2333
2461.9417 | 440.5732 | 372.3676
2462.9417 | 440.6819 | 372.4848
2463.9417 | 440.768 | 372.6218
2464.9417 | 440.7903 | 372.7446
2465.9417 | 440.8023 | 372.8853
2466.9417 | 440.9398 | 373.0086
2467.9417 | 440.9637 | 373.153
2468.9417 | 440.9406 | 373.2758
2469.9417 | 441.0217 | 373.3952
2470.9417 | 441.2229 | 373.5256
2471.9417 | 441.3487 | 373.6662
2472.9417 | 441.441 | 373.7851
2473.9417 | 441.4501 | 373.9045
2474.9417 | 441.5644 | 374.0325
2475.9417 | 441.6559 | 374.1663
2476.9417 | 441.5452 | 374.3024
2477.9417 | 441.4043 | 374.4146
2478.9417 | 441.3585 | 374.553
2479.9417 | 441.4544 | 374.6772
2480.9417 | 441.5821 | 374.792
2481.9417 | 441.5013 | 374.9265
2482.9417 | 441.4458 | 375.0325
2483.9417 | 441.6117 | 375.1646
2484.9417 | 441.5919 | 375.2863
2485.9417 | 441.5888 | 375.409
2486.9417 | 441.6937 | 375.5214
2487.9417 | 441.7777 | 375.6523
2488.9573 | 441.7688 | 375.7825
2489.9417 | 441.7453 | 375.8916
2490.9417 | 441.7953 | 376.0235
2491.9417 | 441.8256 | 376.1331
2492.9417 | 441.7071 | 376.2592
2493.9417 | 441.6562 | 376.3798
2494.9417 | 441.635 | 376.4983
2495.9417 | 441.7832 | 376.6118
2496.9417 | 441.9605 | 376.7373
2497.9417 | 442.0681 | 376.8473
2498.9417 | 441.9901 | 376.9585
2499.9417 | 441.9888 | 377.0749
2500.9417 | 441.9828 | 377.1892
2501.9417 | 442.0826 | 377.2999
2502.9417 | 442.0922 | 377.4059
2503.9417 | 442.055 | 377.5379
2504.9417 | 442.1539 | 377.6427
2505.9417 | 442.1523 | 377.76
2506.9417 | 442.1359 | 377.8664
2507.9417 | 442.1979 | 377.9761
2508.9417 | 442.2849 | 378.1035
2509.9417 | 442.3082 | 378.1975
2510.9417 | 442.39 | 378.3223
2511.9417 | 442.3563 | 378.4198
2512.9417 | 442.3884 | 378.5454
2513.9417 | 442.4496 | 378.6593
2514.9417 | 442.6194 | 378.7605
2515.9417 | 442.6462 | 378.8734
2516.9417 | 442.716 | 378.984
2517.9417 | 442.6725 | 379.0848
2518.9417 | 442.7296 | 379.2009
2519.9417 | 442.7889 | 379.3261
2520.9417 | 442.8855 | 379.4293
2521.9417 | 442.9751 | 379.5107
2522.9417 | 442.914 | 379.6365
2523.9417 | 442.7848 | 379.7264
2524.9417 | 442.6323 | 379.8489
2525.9417 | 442.6594 | 379.9443
2526.9417 | 442.7457 | 380.0675
2527.9417 | 442.8031 | 380.1702
2528.9417 | 442.8072 | 380.2446
2529.9417 | 442.7744 | 380.3589
2530.9417 | 442.7859 | 380.4656
2531.9417 | 442.9072 | 380.5721
2532.9417 | 442.8549 | 380.669
2533.9417 | 442.9005 | 380.7786
2534.9417 | 442.8467 | 380.8742
2535.9417 | 442.8157 | 380.9905
2536.9417 | 442.7806 | 381.0878
2537.9417 | 442.6553 | 381.1798
2538.9417 | 442.582 | 381.2818
2539.9417 | 442.3294 | 381.3708
2540.9417 | 442.2693 | 381.4818
2541.9417 | 442.3839 | 381.576
2542.9417 | 442.4637 | 381.6821
2543.9417 | 442.5726 | 381.7813
2544.9417 | 442.5755 | 381.8748
2545.9417 | 442.672 | 381.9793
2546.9417 | 442.7053 | 382.0608
2547.9417 | 442.6402 | 382.1688
2548.9417 | 442.4858 | 382.265
2549.9417 | 442.4629 | 382.3613
2550.9417 | 442.3697 | 382.4664
2551.9417 | 442.3996 | 382.5645
2552.9417 | 442.23 | 382.658
2553.9417 | 442.1744 | 382.7606
2554.9417 | 442.1076 | 382.854
2555.9417 | 442.1231 | 382.9427
2556.9417 | 442.2401 | 383.0432
2557.9417 | 442.4407 | 383.1479
2558.9417 | 442.5488 | 383.2362
2559.9417 | 442.6944 | 383.3379
2560.9417 | 442.833 | 383.4289
2561.9417 | 442.958 | 383.5336
2562.9417 | 443.0432 | 383.6318
2563.9417 | 443.0296 | 383.7141
2564.9417 | 442.9452 | 383.8172
2565.9417 | 442.8703 | 383.9167
2566.9417 | 442.8458 | 383.9969
2567.9417 | 442.8877 | 384.105
2568.9417 | 442.8726 | 384.1992
2569.9417 | 442.901 | 384.2848
2570.9417 | 442.9506 | 384.3873
2571.9417 | 443.0032 | 384.4882
2572.9417 | 443.0351 | 384.5818
2573.9417 | 443.0289 | 384.6818
2574.9417 | 442.9207 | 384.76
2575.9417 | 442.9995 | 384.8579
2576.9417 | 442.9003 | 384.9629
2577.9417 | 442.6972 | 385.0462
2578.9417 | 442.6188 | 385.1556
2579.9417 | 442.5401 | 385.2419
2580.9417 | 442.4457 | 385.3432
2581.9417 | 442.3634 | 385.4327
2582.9417 | 442.3517 | 385.5209
2583.9417 | 442.4476 | 385.6211
2584.9417 | 442.4547 | 385.7235
2585.9417 | 442.3896 | 385.8065
2586.9417 | 442.3613 | 385.908
2587.9417 | 442.2873 | 385.9943
2588.9417 | 442.1655 | 386.0874
2589.9417 | 442.0532 | 386.188
2590.9417 | 442.0308 | 386.2854
2591.9417 | 442.1048 | 386.3782
2592.9417 | 441.9516 | 386.4602
2593.9417 | 442.0619 | 386.5601
2594.9417 | 442.104 | 386.6564
2595.9417 | 442.1252 | 386.7386
2596.9417 | 442.098 | 386.8361
2597.9417 | 442.0848 | 386.9151
2598.9417 | 442.1232 | 387.0229
2599.9417 | 442.084 | 387.1117
2600.9417 | 441.9608 | 387.1994
2601.9417 | 441.9646 | 387.2889
2602.9417 | 442.0352 | 387.3895
2603.9417 | 441.7991 | 387.4715
2604.9417 | 441.7511 | 387.5664
2605.9417 | 441.7401 | 387.6626
2606.9417 | 441.6453 | 387.7583
2607.9417 | 441.6155 | 387.8381
2608.9417 | 441.4617 | 387.9271
2609.9417 | 441.5362 | 388.0227
2610.9417 | 441.5256 | 388.1241
2611.9417 | 441.6223 | 388.2088
2612.9417 | 441.6586 | 388.2752
2613.9417 | 441.7775 | 388.391
2614.9417 | 441.8915 | 388.4625
2615.9417 | 442.04 | 388.5826
2616.9417 | 441.9968 | 388.6457
2617.9417 | 441.9487 | 388.7447
2618.9417 | 441.9136 | 388.8438
2619.9417 | 441.9286 | 388.9215
2620.9417 | 441.7496 | 389.0136
2621.9417 | 441.6619 | 389.0936
2622.9417 | 441.6915 | 389.1805
2623.9417 | 441.6566 | 389.2506
2624.9417 | 441.7082 | 389.3501
2625.9417 | 441.7492 | 389.4453
2626.9417 | 441.5533 | 389.5091
2627.9417 | 441.4964 | 389.5945
2628.9417 | 441.4921 | 389.6927
2629.9417 | 441.4648 | 389.7758
2630.9417 | 441.5368 | 389.8438
2631.9417 | 441.5819 | 389.9408
2632.9417 | 441.6937 | 390.0205
2633.9417 | 441.781 | 390.0918
2634.9417 | 441.7284 | 390.1933
2635.9417 | 441.5908 | 390.2688
2636.9417 | 441.5849 | 390.364
2637.9417 | 441.6228 | 390.4306
2638.9417 | 441.4762 | 390.5106
2639.9417 | 441.6022 | 390.6029
2640.9417 | 441.6855 | 390.6702
2641.9417 | 441.5797 | 390.769
2642.9417 | 441.5554 | 390.8357
2643.9417 | 441.536 | 390.9235
2644.9417 | 441.5071 | 391.0129
2645.9417 | 441.6243 | 391.0809
2646.9417 | 441.748 | 391.162
2647.9417 | 441.7444 | 391.2473
2648.9417 | 441.7361 | 391.329
2649.9417 | 441.7151 | 391.402
2650.9417 | 441.7733 | 391.487
2651.9417 | 441.7647 | 391.5626
2652.9417 | 441.8292 | 391.6307
2653.9417 | 441.8726 | 391.7072
2654.9417 | 441.8631 | 391.7867
2655.9417 | 441.8535 | 391.8603
2656.9417 | 441.9172 | 391.9446
2657.9417 | 441.9977 | 392.0117
2658.9417 | 442.0489 | 392.0899
2659.9417 | 442.0318 | 392.1667
2660.9417 | 442.1174 | 392.2449
2661.9417 | 442.0545 | 392.3188
2662.9417 | 442.052 | 392.3984
2663.9417 | 441.9752 | 392.4756
2664.9417 | 441.9274 | 392.5468
2665.9417 | 441.9243 | 392.6105
2666.9417 | 441.9773 | 392.7069
2667.9417 | 441.9582 | 392.7674
2668.9417 | 441.994 | 392.8308
2669.9417 | 441.9782 | 392.9133
2670.9417 | 442.0447 | 392.9839
2671.9417 | 442.1007 | 393.0463
2672.9417 | 442.0346 | 393.1264
2673.9417 | 442.1093 | 393.2022
2674.9417 | 442.1491 | 393.2758
2675.9417 | 442.1151 | 393.3406
2676.9417 | 441.8969 | 393.4096
2677.9417 | 441.8756 | 393.4803
2678.9417 | 441.8886 | 393.5511
2679.9417 | 441.9101 | 393.6132
2680.9417 | 441.7699 | 393.6746
2681.9417 | 441.7514 | 393.7356
2682.9417 | 441.7827 | 393.8071
2683.9417 | 441.8744 | 393.8693
2684.9417 | 441.9826 | 393.9487
2685.9417 | 442.0905 | 394.0234
2686.9417 | 442.1185 | 394.0897
2687.9417 | 442.0182 | 394.1508
2688.9417 | 442.0123 | 394.2201
2689.9417 | 442.1633 | 394.2813
2690.9417 | 442.2769 | 394.358
2691.9417 | 442.3499 | 394.4226
2692.9417 | 442.4028 | 394.4925
2693.9417 | 442.4952 | 394.5574
2694.9417 | 442.4171 | 394.6105
2695.9417 | 442.4076 | 394.674
2696.9417 | 442.4274 | 394.7581
2697.9417 | 442.5049 | 394.8066
2698.9417 | 442.4857 | 394.8719
2699.9417 | 442.5166 | 394.916
2700.9417 | 442.5506 | 394.9754
2701.9417 | 442.6236 | 395.059
2702.9417 | 442.5041 | 395.1225
2703.9417 | 442.4662 | 395.1809
2704.9417 | 442.4524 | 395.2402
2705.9417 | 442.4949 | 395.3088
2706.9417 | 442.5167 | 395.3553
2707.9417 | 442.5716 | 395.4183
2708.9417 | 442.4866 | 395.4692
2709.9417 | 442.4615 | 395.5318
2710.9417 | 442.4157 | 395.5862
2711.9417 | 442.3414 | 395.6496
2712.9417 | 442.2727 | 395.6998
2713.9417 | 442.3933 | 395.7583
2714.9417 | 442.4942 | 395.809
2715.9417 | 442.4853 | 395.8652
2716.9417 | 442.3931 | 395.9272
2717.9417 | 442.3283 | 395.9765
2718.9417 | 442.2304 | 396.042
2719.9417 | 442.051 | 396.0594
2720.9417 | 442.2274 | 396.141
2721.9417 | 442.2315 | 396.1996
2722.9417 | 442.1821 | 396.2361
2723.9417 | 442.1261 | 396.3081
2724.9417 | 442.1389 | 396.3528
2725.9417 | 442.1928 | 396.4128
2726.9417 | 442.2865 | 396.4617
2727.9417 | 442.2713 | 396.5032
2728.9417 | 442.1684 | 396.5565
2729.9417 | 442.2147 | 396.6116
2730.9417 | 442.2104 | 396.668
2731.9417 | 442.2656 | 396.7154
2732.9417 | 442.2162 | 396.7669
2733.9417 | 442.256 | 396.8232
2734.9417 | 442.327 | 396.8541
2735.9417 | 442.2698 | 396.915
2736.9417 | 442.2218 | 396.9601
2737.9417 | 442.1666 | 397.0035
2738.9417 | 442.142 | 397.0516
2739.9417 | 442.214 | 397.1091
2740.9417 | 442.2899 | 397.1456
2741.9417 | 442.1308 | 397.1975
2742.9417 | 442.0609 | 397.2406
2743.9417 | 441.9305 | 397.2834
2744.9417 | 441.8466 | 397.3318
2745.9417 | 441.8912 | 397.3699
2746.9417 | 441.9227 | 397.4262
2747.9417 | 441.8892 | 397.4661
2748.9417 | 441.8776 | 397.5204
2749.9417 | 442.0215 | 397.5558
2750.9417 | 442.1883 | 397.5864
2751.9417 | 442.1935 | 397.6377
2752.9417 | 442.1878 | 397.6828
2753.9417 | 442.2836 | 397.7067
2754.9417 | 442.282 | 397.7499
2755.9417 | 442.2976 | 397.7829
2756.9417 | 442.2713 | 397.8346
2757.9417 | 442.1944 | 397.8807
2758.9417 | 442.0739 | 397.9279
2759.9417 | 442.1422 | 397.9729
2760.9417 | 442.103 | 398.0132
2761.9417 | 442.0774 | 398.0553
2762.9417 | 442.2777 | 398.1002
2763.9417 | 442.308 | 398.1408
2764.9417 | 442.376 | 398.1724
2765.9417 | 442.417 | 398.2191
2766.9417 | 442.5504 | 398.2492
2767.9417 | 442.5364 | 398.2861
2768.9417 | 442.4909 | 398.327
2769.9417 | 442.5765 | 398.3672
2770.9417 | 442.6452 | 398.4104
2771.9417 | 442.6852 | 398.4459
2772.9417 | 442.7293 | 398.4893
2773.9417 | 442.6664 | 398.5097
2774.9417 | 442.4817 | 398.5682
2775.9417 | 442.41 | 398.6067
2776.9417 | 442.328 | 398.6399
2777.9417 | 442.3457 | 398.6919
2778.9417 | 442.2817 | 398.6805
2779.9417 | 442.2621 | 398.7583
2780.9417 | 442.0948 | 398.794
2781.9417 | 442.0207 | 398.833
2782.9417 | 441.9955 | 398.8685
2783.9417 | 441.9723 | 398.8978
2784.9417 | 441.929 | 398.9379
2785.9417 | 441.6764 | 398.9803
2786.9417 | 441.5593 | 399.0204
2787.9417 | 441.5088 | 399.0553
2788.9417 | 441.2921 | 399.0954
2789.9417 | 441.3023 | 399.1325
2790.9417 | 441.312 | 399.1723
2791.9417 | 441.2417 | 399.1868
2792.9417 | 441.1933 | 399.2225
2793.9417 | 441.1256 | 399.2767
2794.9417 | 441.056 | 399.2972
2795.9417 | 441.0943 | 399.3381
2796.9417 | 440.9602 | 399.3642
2797.9417 | 440.9657 | 399.4016
2798.9417 | 440.9885 | 399.4293
2799.9417 | 440.9536 | 399.4701
2800.9417 | 440.8957 | 399.5096
2801.9417 | 440.8974 | 399.53
2802.9417 | 440.9848 | 399.5733
2803.9417 | 440.8924 | 399.6027
2804.9417 | 440.8889 | 399.6236
2805.9417 | 440.9915 | 399.6478
2806.9417 | 441.0924 | 399.6991
2807.9417 | 441.1429 | 399.726
2808.9417 | 441.1715 | 399.7557
2809.9417 | 441.1043 | 399.7795
2810.9417 | 440.9686 | 399.8152
2811.9417 | 440.9772 | 399.8531
2812.9417 | 441.0414 | 399.8782
2813.9417 | 440.973 | 399.9018
2814.9417 | 441.1199 | 399.9428
2815.9417 | 441.2156 | 399.9774
2816.9417 | 441.2425 | 400.0008
2817.9417 | 441.3176 | 400.0331
2818.9417 | 441.4048 | 400.0412
2819.9417 | 441.5205 | 400.0862
2820.9417 | 441.5668 | 400.1298
2821.9417 | 441.5976 | 400.1496
2822.9417 | 441.7021 | 400.1734
2823.9417 | 441.6982 | 400.199
2824.9417 | 441.6564 | 400.2374
2825.9417 | 441.6538 | 400.2673
2826.9417 | 441.5934 | 400.3087
2827.9417 | 441.6138 | 400.3308
2828.9417 | 441.6663 | 400.3569
2829.9417 | 441.72 | 400.3971
2830.9417 | 441.6147 | 400.4272
2831.9417 | 441.5777 | 400.4408
2832.9417 | 441.5702 | 400.4868
2833.9417 | 441.5676 | 400.5023
2834.9417 | 441.5921 | 400.5644
2835.9417 | 441.5725 | 400.584
2836.9417 | 441.4075 | 400.6179
2837.9417 | 441.2497 | 400.6373
2838.9417 | 441.2862 | 400.6806
2839.9417 | 441.3292 | 400.713
2840.9417 | 441.3358 | 400.75
2841.9417 | 441.5049 | 400.7702
2842.9417 | 441.6307 | 400.807
2843.9417 | 441.6039 | 400.8379
2844.9417 | 441.5939 | 400.8858
2845.9417 | 441.621 | 400.9097
2846.9417 | 441.6228 | 400.9449
2847.9417 | 441.7427 | 400.9733
2848.9417 | 441.6576 | 400.995
2849.9417 | 441.5776 | 401.0223
2850.9417 | 441.5487 | 401.0538
2851.9417 | 441.6248 | 401.0835
2852.9417 | 441.7064 | 401.1184
2853.9417 | 441.7132 | 401.1647
2854.9417 | 441.757 | 401.1936
2855.9417 | 441.6368 | 401.2136
2856.9417 | 441.6248 | 401.2557
2857.9417 | 441.5538 | 401.2763
2858.9417 | 441.6356 | 401.2849
2859.9417 | 441.7668 | 401.3493
2860.9417 | 441.8778 | 401.3851
2861.9417 | 441.8411 | 401.4274
2862.9417 | 441.8425 | 401.4623
2863.9417 | 441.6933 | 401.4687
2864.9417 | 441.3912 | 401.5144
2865.9417 | 441.3866 | 401.5542
2866.9417 | 441.5095 | 401.5848
2867.9417 | 441.5752 | 401.6055
2868.9417 | 441.6126 | 401.6468
2869.9417 | 441.7794 | 401.6812
2870.9417 | 441.9544 | 401.7004
2871.9417 | 442.0574 | 401.7428
2872.9417 | 442.0629 | 401.7595
2873.9417 | 442.1383 | 401.7856
2874.9417 | 442.1761 | 401.8159
2875.9417 | 442.1382 | 401.8557
2876.9417 | 442.1485 | 401.8831
2877.9417 | 442.2181 | 401.8912
2878.9417 | 442.1303 | 401.934
2879.9417 | 442.157 | 401.9688
2880.9417 | 442.2032 | 401.9956
2881.9417 | 442.0964 | 402.0235
2882.9417 | 442.0953 | 402.0507
2883.9417 | 442.0856 | 402.0706
2884.9417 | 442.0676 | 402.101
2885.9417 | 441.9427 | 402.1019
2886.9417 | 441.8671 | 402.1408
2887.9417 | 441.792 | 402.1674
2888.9417 | 441.8351 | 402.1931
2889.9417 | 441.9529 | 402.205
2890.9417 | 442.1112 | 402.2382
2891.9417 | 442.0601 | 402.2511
2892.9417 | 442.0795 | 402.2919
2893.9417 | 442.2304 | 402.3052
2894.9417 | 442.3901 | 402.3236
2895.9417 | 442.4807 | 402.3559
2896.9417 | 442.5774 | 402.3702
2897.9417 | 442.6232 | 402.3921
2898.9417 | 442.6104 | 402.4236
2899.9417 | 442.5646 | 402.4393
2900.9417 | 442.5225 | 402.453
2901.9417 | 442.5317 | 402.4599
2902.9417 | 442.6886 | 402.502
2903.9417 | 442.697 | 402.5362
2904.9417 | 442.6214 | 402.534
2905.9417 | 442.4562 | 402.5715
2906.9417 | 442.409 | 402.5931
2907.9417 | 442.3835 | 402.6134
2908.9417 | 442.3736 | 402.6311
2909.9417 | 442.3868 | 402.6467
2910.9417 | 442.3145 | 402.678
2911.9417 | 442.1957 | 402.6893
2912.9417 | 442.2141 | 402.7169
2913.9417 | 442.2578 | 402.7438
2914.9417 | 442.373 | 402.7661
2915.9417 | 442.3655 | 402.7649
2916.9417 | 442.2314 | 402.7976
2917.9417 | 442.1434 | 402.8179
2918.9417 | 442.1268 | 402.8461
2919.9417 | 442.1289 | 402.8693
2920.9417 | 442.1049 | 402.8965
2921.9417 | 442.1068 | 402.8989
2922.9417 | 442.074 | 402.9246
2923.9417 | 441.953 | 402.9406
2924.9417 | 441.8996 | 402.9565
2925.9417 | 441.8898 | 402.9795
2926.9417 | 441.7173 | 402.9952
2927.9417 | 441.7442 | 403.0168
2928.9417 | 441.7702 | 403.0269
2929.9417 | 441.6621 | 403.0503
2930.9417 | 441.6362 | 403.0632
2931.9417 | 441.6063 | 403.0863
2932.9417 | 441.5328 | 403.1004
2933.9417 | 441.5627 | 403.1371
2934.9417 | 441.4966 | 403.1441
2935.9417 | 441.4743 | 403.1606
2936.9417 | 441.4751 | 403.1616
2937.9417 | 441.3998 | 403.1868
2938.9417 | 441.3922 | 403.2208
2939.9417 | 441.4067 | 403.2302
2940.9417 | 441.3009 | 403.265
2941.9417 | 441.2791 | 403.276
2942.9417 | 441.3294 | 403.2837
2943.9417 | 441.1943 | 403.31
2944.9417 | 441.2605 | 403.3308
2945.9417 | 441.2949 | 403.3566
2946.9417 | 441.4067 | 403.3839
2947.9417 | 441.3977 | 403.3991
2948.9417 | 441.4172 | 403.4219
2949.9417 | 441.4876 | 403.4383
2950.9417 | 441.6679 | 403.4489
2951.9417 | 441.786 | 403.4901
2952.9417 | 441.7858 | 403.4982
2953.9417 | 441.8701 | 403.5226
2954.9417 | 441.8035 | 403.5471
2955.9417 | 441.8507 | 403.5717
2956.9417 | 442.0254 | 403.5912
2957.9417 | 442.109 | 403.6122
2958.9417 | 442.1537 | 403.6461
2959.9417 | 442.2414 | 403.6527
2960.9417 | 442.3231 | 403.6639
2961.9417 | 442.3776 | 403.7065
2962.9417 | 442.3664 | 403.73
2963.9417 | 442.2371 | 403.7477
2964.9417 | 442.2604 | 403.7631
2965.9417 | 442.3405 | 403.802
2966.9417 | 442.2716 | 403.8294
2967.9417 | 442.1649 | 403.8506
2968.9417 | 442.224 | 403.87
2969.9417 | 442.3188 | 403.8971
2970.9417 | 442.2874 | 403.9242
2971.9417 | 442.188 | 403.943
2972.9417 | 442.1333 | 403.9736
2973.9417 | 442.0885 | 403.9963
2974.9417 | 442.0953 | 403.9994
2975.9417 | 442.1288 | 404.037
2976.9417 | 441.8986 | 404.0598
2977.9417 | 441.7995 | 404.0763
2978.9417 | 441.6887 | 404.0896
2979.9417 | 441.7393 | 404.1154
2980.9417 | 441.7586 | 404.1321
2981.9417 | 441.8244 | 404.1503
2982.9417 | 441.9038 | 404.1639
2983.9417 | 441.9609 | 404.2014
2984.9417 | 441.9668 | 404.2139
2985.9417 | 442.1078 | 404.2409
2986.9417 | 442.0594 | 404.263
2987.9417 | 441.9561 | 404.2716
2988.9417 | 441.9736 | 404.3029
2989.9417 | 441.9333 | 404.3243
2990.9417 | 441.896 | 404.3386
2991.9417 | 441.8664 | 404.3668
2992.9417 | 441.8022 | 404.3819
2993.9417 | 441.7265 | 404.4133
2994.9417 | 441.7164 | 404.4226
2995.9417 | 441.6885 | 404.4576
2996.9417 | 441.5707 | 404.4748
2997.9417 | 441.5205 | 404.5085
2998.9417 | 441.4191 | 404.5282
2999.9417 | 441.4528 | 404.5472
3000.9417 | 441.4158 | 404.5708
3001.9417 | 441.4827 | 404.5954
3002.9417 | 441.4608 | 404.6241
3003.9573 | 441.5755 | 404.6488
3004.9417 | 441.5647 | 404.6564
3005.9417 | 441.5392 | 404.6843
3006.9417 | 441.5987 | 404.7077
3007.9417 | 441.5633 | 404.7199
3008.9417 | 441.5219 | 404.7347
3009.9417 | 441.5478 | 404.74
3010.9417 | 441.5505 | 404.7514
3011.9417 | 441.6592 | 404.7791
3012.9417 | 441.6682 | 404.7973
3013.9417 | 441.7309 | 404.8128
3014.9417 | 441.77 | 404.8295
3015.9417 | 441.6377 | 404.8393
3016.9417 | 441.6425 | 404.8394
3017.9417 | 441.7303 | 404.8511
3018.9417 | 441.7135 | 404.8625
3019.9417 | 441.7093 | 404.8681
3020.9417 | 441.8007 | 404.8761
3021.9417 | 441.7976 | 404.886
3022.9417 | 441.7375 | 404.8956
3023.9417 | 441.7029 | 404.9035
3024.9417 | 441.6351 | 404.897
3025.9417 | 441.5833 | 404.9084
3026.9417 | 441.6304 | 404.9106
3027.9417 | 441.5103 | 404.9174
3028.9417 | 441.3883 | 404.9125
3029.9417 | 441.3141 | 404.9175
3030.9417 | 441.3564 | 404.9124
3031.9417 | 441.3735 | 404.9187
3032.9417 | 441.3565 | 404.9238
3033.9417 | 441.3098 | 404.9267
3034.9417 | 441.2775 | 404.9092
3035.9417 | 441.2281 | 404.9272
3036.9417 | 441.2798 | 404.9104
3037.9417 | 441.2271 | 404.9058
3038.9417 | 441.1281 | 404.9081
3039.9417 | 441.0798 | 404.9194
3040.9417 | 441.0587 | 404.91
3041.9417 | 441.0352 | 404.9167
3042.9417 | 440.9808 | 404.9155
3043.9417 | 440.8943 | 404.9175
3044.9417 | 440.876 | 404.9191
3045.9417 | 440.83 | 404.9289
3046.9417 | 440.8981 | 404.925
3047.9417 | 440.9028 | 404.9218
3048.9417 | 440.9024 | 404.9308
3049.9417 | 440.8816 | 404.9247
3050.9417 | 440.7504 | 404.9315
3051.9417 | 440.7707 | 404.9302
3052.9417 | 440.7141 | 404.9363
3053.9417 | 440.7548 | 404.9427
3054.9417 | 440.8311 | 404.9348
3055.9417 | 440.953 | 404.9222
3056.9417 | 440.9113 | 404.9309
3057.9417 | 440.6871 | 404.9233
3058.9417 | 440.6404 | 404.9301
3059.9417 | 440.753 | 404.9399
3060.9417 | 440.6448 | 404.9396
3061.9417 | 440.6669 | 404.9417
3062.9417 | 440.7295 | 404.9344
3063.9417 | 440.646 | 404.9307
3064.9417 | 440.6509 | 404.9295
3065.9417 | 440.6533 | 404.9514
3066.9417 | 440.6351 | 404.9428
3067.9417 | 440.5759 | 404.9475
3068.9417 | 440.6338 | 404.9422
3069.9417 | 440.8119 | 404.9431
3070.9417 | 440.9981 | 404.9318
3071.9417 | 440.9561 | 404.9264
3072.9417 | 440.9003 | 404.9428
3073.9417 | 440.9083 | 404.945
3074.9417 | 440.7425 | 404.9493
3075.9417 | 440.6937 | 404.925
3076.9417 | 440.7854 | 404.9507
3077.9417 | 440.8617 | 404.9305
3078.9417 | 440.8407 | 404.9297
3079.9417 | 440.7556 | 404.9432
3080.9417 | 440.8031 | 404.9488
3081.9417 | 440.9054 | 404.9328
3082.9417 | 440.9244 | 404.9359
3083.9417 | 440.9457 | 404.9455
3084.9417 | 441.0755 | 404.9411
3085.9417 | 441.0863 | 404.9444
3086.9417 | 441.0348 | 404.9202
3087.9417 | 441.063 | 404.9402
3088.9417 | 441.2356 | 404.9331
3089.9417 | 441.2971 | 404.9292
3090.9417 | 441.3256 | 404.9358
3091.9417 | 441.3763 | 404.9314
3092.9417 | 441.3723 | 404.9246
3093.9417 | 441.4009 | 404.9207
3094.9417 | 441.4626 | 404.922
3095.9417 | 441.3265 | 404.9073
3096.9417 | 441.2973 | 404.9176
3097.9417 | 441.0994 | 404.9146
3098.9417 | 441.102 | 404.8894
3099.9417 | 441.0374 | 404.9082
3100.9417 | 441.2704 | 404.9107
3101.9417 | 441.4838 | 404.9177
3102.9417 | 441.3766 | 404.8989
3103.9417 | 441.3093 | 404.896
3104.9417 | 441.2192 | 404.8739
3105.9417 | 441.292 | 404.8935
3106.9417 | 441.3851 | 404.8977
3107.9417 | 441.3574 | 404.8845
3108.9417 | 441.2899 | 404.8862
3109.9417 | 441.247 | 404.8824
3110.9417 | 441.2801 | 404.8874
3111.9417 | 441.3143 | 404.8794
3112.9417 | 441.2124 | 404.8829
3113.9417 | 441.2504 | 404.8892
3114.9417 | 441.2455 | 404.8931
3115.9417 | 441.1328 | 404.9
3116.9417 | 441.026 | 404.8938
3117.9417 | 441.0473 | 404.8925
3118.9417 | 441.0021 | 404.907
3119.9417 | 441.0387 | 404.9182
3120.9417 | 441.034 | 404.9107
3121.9417 | 440.9595 | 404.913
3122.9417 | 440.9595 | 404.9126
3123.9417 | 440.922 | 404.9201
3124.9417 | 440.8225 | 404.9133
3125.9417 | 440.6716 | 404.9031
3126.9417 | 440.7394 | 404.927
3127.9417 | 440.8217 | 404.9191
3128.9417 | 440.8606 | 404.9186
3129.9417 | 440.9625 | 404.9207
3130.9417 | 440.9817 | 404.9271
3131.9417 | 440.9089 | 404.8994
3132.9417 | 440.9725 | 404.8948
3133.9417 | 440.9897 | 404.8925
3134.9417 | 441.0249 | 404.8899
3135.9417 | 441.0356 | 404.886
3136.9417 | 441.0724 | 404.8863
3137.9417 | 441.1305 | 404.8664
3138.9417 | 441.202 | 404.8703
3139.9417 | 441.0755 | 404.8652
3140.9417 | 441.118 | 404.8435
3141.9417 | 441.1312 | 404.8468
3142.9417 | 441.028 | 404.8408
3143.9417 | 441.1175 | 404.8525
3144.9417 | 441.1314 | 404.8448
3145.9417 | 441.138 | 404.8289
3146.9417 | 441.2694 | 404.8428
3147.9417 | 441.4 | 404.8452
3148.9417 | 441.4262 | 404.8399
3149.9417 | 441.4667 | 404.8428
3150.9417 | 441.4872 | 404.8159
3151.9417 | 441.4866 | 404.8384
3152.9417 | 441.5228 | 404.8362
3153.9417 | 441.3878 | 404.8295
3154.9417 | 441.2708 | 404.8186
3155.9417 | 441.4071 | 404.8164
3156.9417 | 441.5581 | 404.8239
3157.9417 | 441.6482 | 404.8086
3158.9417 | 441.5784 | 404.8214
3159.9417 | 441.4619 | 404.825
3160.9417 | 441.5288 | 404.8345
3161.9417 | 441.5035 | 404.8326
3162.9417 | 441.4538 | 404.8328
3163.9417 | 441.4925 | 404.8305
3164.9417 | 441.4063 | 404.8237
3165.9417 | 441.2776 | 404.8276
3166.9417 | 441.2826 | 404.841
3167.9417 | 441.387 | 404.8494
3168.9417 | 441.3087 | 404.8496
3169.9417 | 441.2282 | 404.8464
3170.9417 | 441.1718 | 404.8314
3171.9417 | 441.0992 | 404.8369
3172.9417 | 441.2498 | 404.8357
3173.9417 | 441.401 | 404.8288
3174.9417 | 441.5362 | 404.856
3175.9417 | 441.5781 | 404.8352
3176.9417 | 441.4595 | 404.8439
3177.9417 | 441.3573 | 404.834
3178.9417 | 441.3313 | 404.8329
3179.9417 | 441.2326 | 404.831
3180.9417 | 441.1001 | 404.8231
3181.9417 | 441.1705 | 404.8381
3182.9417 | 441.2506 | 404.8211
3183.9417 | 441.2945 | 404.8228
3184.9417 | 441.3323 | 404.8279
3185.9417 | 441.4384 | 404.81
3186.9417 | 441.3674 | 404.8236
3187.9417 | 441.3483 | 404.8264
3188.9417 | 441.4706 | 404.8144
3189.9417 | 441.4628 | 404.8157
3190.9417 | 441.4125 | 404.823
3191.9417 | 441.3646 | 404.809
3192.9417 | 441.321 | 404.8159
3193.9417 | 441.3224 | 404.8126
3194.9417 | 441.3938 | 404.8181
3195.9417 | 441.3957 | 404.8261
3196.9417 | 441.3185 | 404.8236
3197.9417 | 441.3378 | 404.8156
3198.9417 | 441.3775 | 404.8269
3199.9417 | 441.3936 | 404.8188
3200.9417 | 441.398 | 404.8106
3201.9417 | 441.353 | 404.8413
3202.9417 | 441.2546 | 404.8249
3203.9417 | 441.1873 | 404.8383
3204.9417 | 441.308 | 404.8251
3205.9417 | 441.4288 | 404.818
3206.9417 | 441.4421 | 404.8064
3207.9417 | 441.5154 | 404.7971
3208.9417 | 441.4454 | 404.802
3209.9417 | 441.4099 | 404.7805
3210.9417 | 441.3995 | 404.7901
3211.9417 | 441.4013 | 404.79
3212.9417 | 441.45 | 404.763
3213.9417 | 441.469 | 404.7678
3214.9417 | 441.4636 | 404.7633
3215.9417 | 441.3105 | 404.753
3216.9417 | 441.3933 | 404.7469
3217.9417 | 441.4195 | 404.7514
3218.9417 | 441.3974 | 404.7402
3219.9417 | 441.364 | 404.7351
3220.9417 | 441.3835 | 404.7239
3221.9417 | 441.4339 | 404.7184
3222.9417 | 441.4473 | 404.7279
3223.9417 | 441.3398 | 404.7199
3224.9417 | 441.2738 | 404.7012
3225.9417 | 441.1029 | 404.7144
3226.9417 | 441.0394 | 404.694
3227.9417 | 441.0701 | 404.7057
3228.9417 | 441.122 | 404.6947
3229.9417 | 441.1674 | 404.6881
3230.9417 | 441.3063 | 404.6763
3231.9417 | 441.4254 | 404.6798
3232.9417 | 441.3246 | 404.6698
3233.9417 | 441.3422 | 404.654
3234.9417 | 441.235 | 404.6619
3235.9417 | 441.2008 | 404.6429
3236.9417 | 441.1555 | 404.6456
3237.9417 | 440.875 | 404.6327
3238.9417 | 440.7936 | 404.6285
3239.9417 | 440.9137 | 404.6103
3240.9417 | 441.1281 | 404.6112
3241.9417 | 441.1324 | 404.6076
3242.9417 | 441.0831 | 404.6011
3243.9417 | 440.9743 | 404.5858
3244.9417 | 440.8594 | 404.5791
3245.9417 | 440.8215 | 404.5786
3246.9417 | 440.7914 | 404.5616
3247.9417 | 440.6407 | 404.5738
3248.9417 | 440.5965 | 404.5612
3249.9417 | 440.6155 | 404.557
3250.9417 | 440.5875 | 404.5436
3251.9417 | 440.6825 | 404.5308
3252.9417 | 440.7862 | 404.5175
3253.9417 | 440.7769 | 404.51
3254.9417 | 440.7604 | 404.5048
3255.9417 | 440.803 | 404.504
3256.9417 | 440.8234 | 404.5012
3257.9417 | 440.9758 | 404.5027
3258.9417 | 440.9225 | 404.4851
3259.9417 | 440.9047 | 404.4854
3260.9417 | 440.959 | 404.4685
3261.9417 | 440.8538 | 404.4533
3262.9417 | 441.0614 | 404.4608
3263.9417 | 441.2839 | 404.4399
3264.9417 | 441.3306 | 404.4514
3265.9417 | 441.4858 | 404.4349
3266.9417 | 441.628 | 404.4381
3267.9417 | 441.5855 | 404.4201
3268.9417 | 441.6847 | 404.4097
3269.9417 | 441.5551 | 404.4113
3270.9417 | 441.4277 | 404.3991
3271.9417 | 441.5202 | 404.3876
3272.9417 | 441.5197 | 404.3849
3273.9417 | 441.5443 | 404.3703
3274.9417 | 441.6515 | 404.3619
3275.9417 | 441.6854 | 404.3368
3276.9417 | 441.7364 | 404.3403
3277.9417 | 441.8408 | 404.3335
3278.9417 | 441.9014 | 404.3193
3279.9417 | 441.9965 | 404.3118
3280.9417 | 441.9625 | 404.2973
3281.9417 | 441.8752 | 404.2976
3282.9417 | 441.7547 | 404.2902
3283.9417 | 441.8085 | 404.283
3284.9417 | 441.9128 | 404.2881
3285.9417 | 442.0125 | 404.2903
3286.9417 | 441.9917 | 404.2701
3287.9417 | 441.8698 | 404.2916
3288.9417 | 441.7374 | 404.2705
3289.9417 | 441.7851 | 404.2764
3290.9417 | 441.7761 | 404.2656
3291.9417 | 441.7222 | 404.277
3292.9417 | 441.6014 | 404.2551
3293.9417 | 441.6205 | 404.248
3294.9417 | 441.4659 | 404.2515
3295.9417 | 441.4669 | 404.2782
3296.9417 | 441.4772 | 404.2779
3297.9417 | 441.5471 | 404.2652
3298.9417 | 441.5593 | 404.2723
3299.9417 | 441.5935 | 404.2736
3300.9417 | 441.5137 | 404.2709
3301.9417 | 441.551 | 404.2858
3302.9417 | 441.613 | 404.2934
3303.9417 | 441.6653 | 404.2955
3304.9417 | 441.7023 | 404.2967
3305.9417 | 441.7196 | 404.306
3306.9417 | 441.8005 | 404.3208
3307.9417 | 441.937 | 404.3251
3308.9417 | 442.0668 | 404.3211
3309.9417 | 442.1109 | 404.3197
3310.9417 | 442.2218 | 404.3409
3311.9417 | 442.2569 | 404.3452
3312.9417 | 442.3163 | 404.3438
3313.9417 | 442.367 | 404.3516
3314.9417 | 442.536 | 404.362
3315.9417 | 442.4118 | 404.3608
3316.9417 | 442.4199 | 404.3583
3317.9417 | 442.3565 | 404.3624
3318.9417 | 442.3757 | 404.3674
3319.9417 | 442.3695 | 404.384
3320.9417 | 442.3918 | 404.4055
3321.9417 | 442.3426 | 404.3981
3322.9417 | 442.2785 | 404.4028
3323.9417 | 442.2989 | 404.3888
3324.9417 | 442.1147 | 404.3957
3325.9417 | 441.9405 | 404.4203
3326.9417 | 441.923 | 404.4263
3327.9417 | 441.9011 | 404.4123
3328.9417 | 441.8982 | 404.4223
3329.9417 | 441.8817 | 404.4141
3330.9417 | 441.842 | 404.4246
3331.9417 | 441.7694 | 404.4283
3332.9417 | 441.8335 | 404.4197
3333.9417 | 441.7752 | 404.4374
3334.9417 | 441.7226 | 404.4455
3335.9417 | 441.7775 | 404.4408
3336.9417 | 441.6988 | 404.4481
3337.9417 | 441.7742 | 404.4523
3338.9417 | 441.882 | 404.4647
3339.9417 | 441.955 | 404.4614
3340.9417 | 441.9678 | 404.4628
3341.9417 | 441.83 | 404.4775
3342.9417 | 442.026 | 404.462
3343.9417 | 442.1874 | 404.4816
3344.9417 | 442.2266 | 404.4843
3345.9417 | 442.3632 | 404.484
3346.9417 | 442.3797 | 404.4784
3347.9417 | 442.2692 | 404.4872
3348.9417 | 442.2947 | 404.4855
3349.9417 | 442.3235 | 404.4856
3350.9417 | 442.3207 | 404.4949
3351.9417 | 442.2129 | 404.4972
3352.9417 | 442.1997 | 404.4904
3353.9417 | 442.0598 | 404.4945
3354.9417 | 441.8964 | 404.4995
3355.9417 | 441.7236 | 404.4956
3356.9417 | 441.6693 | 404.5028
3357.9417 | 441.5016 | 404.5138
3358.9417 | 441.5226 | 404.5175
3359.9417 | 441.5727 | 404.5201
3360.9417 | 441.6415 | 404.5031
3361.9417 | 441.6185 | 404.5298
3362.9417 | 441.6425 | 404.5177
3363.9417 | 441.6599 | 404.5399
3364.9417 | 441.7162 | 404.5422
3365.9417 | 441.668 | 404.5553
3366.9417 | 441.6602 | 404.5571
3367.9417 | 441.5893 | 404.5685
3368.9417 | 441.589 | 404.5577
3369.9417 | 441.5569 | 404.5518
3370.9417 | 441.5589 | 404.5582
3371.9417 | 441.4721 | 404.5558
3372.9417 | 441.3555 | 404.5692
3373.9417 | 441.4801 | 404.5486
3374.9417 | 441.3702 | 404.5632
3375.9417 | 441.3121 | 404.5745
3376.9417 | 441.445 | 404.5637
3377.9417 | 441.6062 | 404.5587
3378.9417 | 441.5979 | 404.5638
3379.9417 | 441.7352 | 404.5763
3380.9417 | 441.7405 | 404.565
3381.9417 | 441.7287 | 404.5815
3382.9417 | 441.6928 | 404.5666
3383.9417 | 441.5754 | 404.5766
3384.9417 | 441.6031 | 404.5913
3385.9417 | 441.6612 | 404.6028
3386.9417 | 441.7478 | 404.5935
3387.9417 | 441.6771 | 404.5893
3388.9417 | 441.5662 | 404.6012
3389.9417 | 441.6411 | 404.6105
3390.9417 | 441.6387 | 404.6234
3391.9417 | 441.6124 | 404.6238
3392.9417 | 441.6234 | 404.6342
3393.9417 | 441.6797 | 404.6288
3394.9417 | 441.5529 | 404.6459
3395.9417 | 441.5918 | 404.6456
3396.9417 | 441.6867 | 404.6558
3397.9417 | 441.7466 | 404.6741
3398.9417 | 441.8966 | 404.683
3399.9417 | 441.8259 | 404.6742
3400.9417 | 441.6817 | 404.685
3401.9417 | 441.6248 | 404.6853
3402.9417 | 441.6986 | 404.7014
3403.9417 | 441.7225 | 404.7007
3404.9417 | 441.733 | 404.7208
3405.9417 | 441.6542 | 404.7274
3406.9417 | 441.7308 | 404.7292
3407.9417 | 441.7048 | 404.7327
3408.9417 | 441.5869 | 404.7475
3409.9417 | 441.6199 | 404.7534
3410.9417 | 441.4744 | 404.7686
3411.9417 | 441.4576 | 404.7904
3412.9417 | 441.4678 | 404.7987
3413.9417 | 441.5955 | 404.8065
3414.9417 | 441.6064 | 404.8082
3415.9417 | 441.6261 | 404.8289
3416.9417 | 441.6334 | 404.8405
3417.9417 | 441.4829 | 404.8451
3418.9417 | 441.4464 | 404.8618
3419.9417 | 441.4656 | 404.8707
3420.9417 | 441.4879 | 404.8822
3421.9417 | 441.5633 | 404.8907
3422.9417 | 441.5807 | 404.9018
3423.9417 | 441.5304 | 404.9169
3424.9417 | 441.4915 | 404.931
3425.9417 | 441.3704 | 404.9432
3426.9417 | 441.3174 | 404.9531
3427.9417 | 441.2328 | 404.9394
3428.9417 | 440.917 | 404.9749
3429.9417 | 440.9053 | 404.9832
3430.9417 | 440.8915 | 404.9811
3431.9417 | 440.8109 | 405.0006
3432.9417 | 440.8283 | 404.9891
3433.9417 | 440.7193 | 405.0107
3434.9417 | 440.6691 | 405.0174
3435.9417 | 440.8285 | 405.0277
3436.9417 | 440.8992 | 405.0335
3437.9417 | 440.9508 | 405.0295
3438.9417 | 440.8518 | 405.0357
3439.9417 | 440.8761 | 405.0436
3440.9417 | 441.0052 | 405.0606
3441.9417 | 441.0304 | 405.0607
3442.9417 | 441.0331 | 405.0632
3443.9417 | 440.9677 | 405.0736
3444.9417 | 440.9336 | 405.081
3445.9417 | 440.9654 | 405.0818
3446.9417 | 441.0649 | 405.0934
3447.9417 | 440.9874 | 405.1108
3448.9417 | 440.8776 | 405.1118
3449.9573 | 441.0908 | 405.1021
3450.9417 | 441.3666 | 405.1334
3451.9417 | 441.5239 | 405.1372
3452.9417 | 441.5216 | 405.1348
3453.9417 | 441.5646 | 405.1582
3454.9417 | 441.6499 | 405.1673
3455.9417 | 441.7162 | 405.1862
3456.9417 | 441.7177 | 405.197
3457.9417 | 441.7602 | 405.2183
3458.9417 | 441.8212 | 405.2354
3459.9417 | 441.9517 | 405.2585
3460.9417 | 442.0462 | 405.2513
3461.9417 | 441.9866 | 405.2808
3462.9417 | 442.0231 | 405.2902
3463.9417 | 441.8349 | 405.3083
3464.9417 | 441.9087 | 405.3354
3465.9417 | 441.9729 | 405.3315
3466.9417 | 442.0003 | 405.3534
3467.9417 | 442.0453 | 405.3565
3468.9417 | 441.9012 | 405.3758
3469.9417 | 441.833 | 405.3786
3470.9417 | 441.7151 | 405.4026
3471.9417 | 441.8098 | 405.418
3472.9417 | 442.0129 | 405.4311
3473.9417 | 441.9118 | 405.451
3474.9417 | 441.9647 | 405.4599
3475.9417 | 441.9663 | 405.4874
3476.9417 | 442.1395 | 405.4972
3477.9417 | 442.2413 | 405.505
3478.9417 | 442.3098 | 405.5207
3479.9417 | 442.2285 | 405.5496
3480.9417 | 442.1328 | 405.5493
3481.9417 | 442.0816 | 405.5692
3482.9417 | 442.1809 | 405.5949
3483.9417 | 442.1745 | 405.6108
3484.9417 | 442.3142 | 405.6254
3485.9417 | 442.3497 | 405.6331
3486.9417 | 442.2906 | 405.6455
3487.9417 | 442.195 | 405.6714
3488.9417 | 442.1839 | 405.6821
3489.9417 | 442.0544 | 405.6888
3490.9417 | 442.0241 | 405.7092
3491.9417 | 441.9733 | 405.7297
3492.9417 | 441.9497 | 405.7358
3493.9417 | 441.9668 | 405.7391
3494.9417 | 441.9602 | 405.7565
3495.9417 | 441.8888 | 405.7759
3496.9417 | 441.8517 | 405.7843
3497.9417 | 441.9027 | 405.7936
3498.9417 | 441.8471 | 405.8051
3499.9417 | 441.9108 | 405.8187
3500.9417 | 441.9651 | 405.8335
3501.9417 | 441.9176 | 405.8395
3502.9417 | 441.8701 | 405.8574
3503.9417 | 441.7912 | 405.8621
3504.9417 | 441.6664 | 405.8679
3505.9417 | 441.7298 | 405.8695
3506.9417 | 441.5838 | 405.9013
3507.9417 | 441.5726 | 405.9092
3508.9417 | 441.5062 | 405.9076
3509.9417 | 441.4768 | 405.9341
3510.9417 | 441.5072 | 405.9399
3511.9417 | 441.4439 | 405.9547
3512.9417 | 441.4762 | 405.9568
3513.9417 | 441.5299 | 405.9709
3514.9417 | 441.4903 | 405.9517
3515.9417 | 441.4787 | 405.9838
3516.9417 | 441.4238 | 405.996
3517.9417 | 441.5683 | 405.9955
3518.9417 | 441.6067 | 406.012
3519.9417 | 441.6415 | 406.0137
3520.9417 | 441.6539 | 406.0048
3521.9417 | 441.723 | 406.0425
3522.9417 | 441.8504 | 406.0504
3523.9417 | 441.7961 | 406.0521
3524.9417 | 441.8766 | 406.0586
3525.9417 | 441.9384 | 406.064
3526.9417 | 441.9319 | 406.0878
3527.9417 | 441.8494 | 406.0917
3528.9417 | 441.8031 | 406.1112
3529.9417 | 441.8623 | 406.1176
3530.9417 | 441.8961 | 406.1291
3531.9417 | 441.8093 | 406.1408
3532.9417 | 441.7849 | 406.1567
3533.9417 | 441.5696 | 406.1822
3534.9417 | 441.5036 | 406.1994
3535.9417 | 441.531 | 406.2
3536.9417 | 441.5133 | 406.2173
3537.9417 | 441.364 | 406.2472
3538.9417 | 441.2837 | 406.2589
3539.9417 | 441.2861 | 406.2689
3540.9417 | 441.2715 | 406.2949
3541.9417 | 441.2783 | 406.3032
3542.9417 | 441.3342 | 406.3264
3543.9417 | 441.3463 | 406.3374
3544.9417 | 441.4474 | 406.3646
3545.9417 | 441.6153 | 406.3773
3546.9417 | 441.6105 | 406.4113
3547.9417 | 441.616 | 406.4044
3548.9417 | 441.6239 | 406.439
3549.9417 | 441.6725 | 406.4507
3550.9417 | 441.6717 | 406.4782
3551.9417 | 441.6948 | 406.4853
3552.9417 | 441.6943 | 406.5037
3553.9417 | 441.7116 | 406.5077
3554.9417 | 441.599 | 406.5337
3555.9417 | 441.5353 | 406.5415
3556.9417 | 441.4783 | 406.565
3557.9417 | 441.4557 | 406.5737
3558.9417 | 441.5769 | 406.5972
3559.9417 | 441.6289 | 406.6054
3560.9417 | 441.7179 | 406.6294
3561.9417 | 441.5362 | 406.6348
3562.9417 | 441.5263 | 406.6442
3563.9417 | 441.5256 | 406.6656
3564.9417 | 441.547 | 406.6748
3565.9417 | 441.5635 | 406.6957
3566.9417 | 441.5663 | 406.716
3567.9417 | 441.6768 | 406.7236
3568.9417 | 441.6779 | 406.7434
3569.9417 | 441.7009 | 406.7567
3570.9417 | 441.7505 | 406.7655
3571.9417 | 441.8686 | 406.8011
3572.9417 | 441.9021 | 406.8129
3573.9417 | 441.9072 | 406.829
3574.9417 | 441.7742 | 406.8489
3575.9417 | 441.708 | 406.8618
3576.9417 | 441.7053 | 406.8607
3577.9417 | 441.6142 | 406.8888
3578.9417 | 441.6438 | 406.9024
3579.9417 | 441.667 | 406.913
3580.9417 | 441.6529 | 406.9067
3581.9417 | 441.6797 | 406.9355
3582.9417 | 441.6726 | 406.9487
3583.9417 | 441.6017 | 406.9622
3584.9417 | 441.5532 | 406.9452
3585.9417 | 441.7341 | 406.9683
3586.9417 | 441.7837 | 406.9907
3587.9417 | 441.8757 | 406.9855
3588.9417 | 441.9312 | 407.0232
3589.9417 | 441.8274 | 407.0294
3590.9417 | 441.7758 | 407.0581
3591.9417 | 441.7158 | 407.0748
3592.9417 | 441.7684 | 407.0704
3593.9417 | 441.7658 | 407.094
3594.9417 | 441.7331 | 407.107
3595.9417 | 441.8821 | 407.1084
3596.9417 | 442.0163 | 407.1413
3597.9417 | 442.1396 | 407.16
3598.9417 | 442.1835 | 407.1794
3599.9417 | 442.1347 | 407.1929
3600.9417 | 442.0972 | 407.2139
3601.9417 | 442.1601 | 407.2259
3602.9417 | 442.1993 | 407.241
3603.9417 | 442.2925 | 407.2747
3604.9417 | 442.3552 | 407.295
3605.9417 | 442.4495 | 407.3005
3606.9417 | 442.4472 | 407.3284
3607.9417 | 442.3859 | 407.3501
3608.9417 | 442.4579 | 407.3812
3609.9417 | 442.4849 | 407.3896
3610.9417 | 442.4627 | 407.4114
3611.9417 | 442.3677 | 407.4429
3612.9417 | 442.3828 | 407.4557
3613.9417 | 442.3884 | 407.4798
3614.9417 | 442.3561 | 407.4911
3615.9417 | 442.3242 | 407.5035
3616.9417 | 442.3551 | 407.5427
3617.9417 | 442.2515 | 407.5566
3618.9417 | 442.1881 | 407.5855
3619.9417 | 442.2404 | 407.5984
3620.9417 | 442.1864 | 407.6108
3621.9417 | 442.1653 | 407.6363
3622.9417 | 442.2018 | 407.6613
3623.9417 | 442.1491 | 407.6826
3624.9417 | 441.984 | 407.7015
3625.9417 | 442.0121 | 407.7208
3626.9417 | 442.0802 | 407.724
3627.9417 | 441.9114 | 407.7665
3628.9417 | 441.8972 | 407.7884
3629.9417 | 441.9486 | 407.8032
3630.9417 | 442.0084 | 407.8154
3631.9417 | 441.9316 | 407.8416
3632.9417 | 441.8984 | 407.852
3633.9417 | 441.998 | 407.8779
3634.9417 | 442.0523 | 407.8964
3635.9417 | 442.016 | 407.9112
3636.9417 | 442.0702 | 407.9308
3637.9417 | 441.9882 | 407.9419
3638.9417 | 442.0221 | 407.96
3639.9417 | 442.0001 | 407.9811
3640.9417 | 441.8762 | 408.0106
3641.9417 | 441.742 | 408.0228
3642.9417 | 441.6637 | 408.0464
3643.9417 | 441.6636 | 408.0553
3644.9417 | 441.7655 | 408.0787
3645.9417 | 441.8283 | 408.0871
3646.9417 | 441.7605 | 408.1149
3647.9417 | 441.8447 | 408.1279
3648.9417 | 441.9314 | 408.1451
3649.9417 | 441.9725 | 408.1346
3650.9417 | 441.9335 | 408.1704
3651.9417 | 441.9629 | 408.1971
3652.9417 | 441.9338 | 408.2047
3653.9417 | 441.83 | 408.2094
3654.9417 | 441.8024 | 408.2277
3655.9417 | 441.7502 | 408.2462
3656.9417 | 441.674 | 408.2648
3657.9417 | 441.6554 | 408.2798
3658.9417 | 441.629 | 408.2828
3659.9417 | 441.6014 | 408.3026
3660.9417 | 441.574 | 408.3037
3661.9417 | 441.5958 | 408.3238
3662.9417 | 441.5802 | 408.3364
3663.9417 | 441.4773 | 408.3623
3664.9417 | 441.437 | 408.3543
3665.9417 | 441.4833 | 408.3614
3666.9417 | 441.5933 | 408.3969
3667.9417 | 441.7322 | 408.4062
3668.9417 | 441.8393 | 408.4157
3669.9417 | 441.9937 | 408.4242
3670.9417 | 442.041 | 408.4411
3671.9417 | 441.9409 | 408.4519
3672.9417 | 442.0604 | 408.466
3673.9417 | 442.1878 | 408.4683
3674.9417 | 442.3336 | 408.4801
3675.9417 | 442.496 | 408.4847
3676.9417 | 442.5961 | 408.4966
3677.9417 | 442.5883 | 408.5251
3678.9417 | 442.5312 | 408.5231
3679.9417 | 442.5897 | 408.5216
3680.9417 | 442.6428 | 408.5531
3681.9417 | 442.7199 | 408.5654
3682.9417 | 442.8128 | 408.5777
3683.9417 | 442.841 | 408.5659
3684.9417 | 442.7788 | 408.5765
3685.9417 | 442.7964 | 408.6043
3686.9417 | 442.6714 | 408.6142
3687.9417 | 442.5365 | 408.6365
3688.9417 | 442.5027 | 408.6482
3689.9417 | 442.4826 | 408.6639
3690.9417 | 442.6194 | 408.6676
3691.9417 | 442.6245 | 408.682
3692.9417 | 442.5322 | 408.7037
3693.9417 | 442.4497 | 408.7078
3694.9417 | 442.4553 | 408.7275
3695.9417 | 442.3823 | 408.7427
3696.9417 | 442.1029 | 408.7565
3697.9417 | 441.9594 | 408.7527
3698.9417 | 441.9266 | 408.7885
3699.9417 | 442.0029 | 408.7891
3700.9417 | 441.9124 | 408.8
3701.9417 | 441.8494 | 408.8345
3702.9417 | 441.7062 | 408.8383
3703.9417 | 441.7338 | 408.8569
3704.9417 | 441.7916 | 408.8751
3705.9417 | 441.9103 | 408.87
3706.9417 | 441.9414 | 408.9114
3707.9417 | 441.9285 | 408.9134
3708.9417 | 441.8814 | 408.9207
3709.9417 | 441.8162 | 408.9663
3710.9417 | 441.8551 | 408.9743
3711.9417 | 441.864 | 408.9706
3712.9417 | 441.7497 | 409.0008
3713.9417 | 441.6199 | 409.0103
3714.9417 | 441.6041 | 409.0306
3715.9417 | 441.7676 | 409.0391
3716.9417 | 441.8021 | 409.0628
3717.9417 | 441.6719 | 409.09
3718.9417 | 441.6457 | 409.1116
3719.9417 | 441.683 | 409.1301
3720.9417 | 441.738 | 409.1485
3721.9417 | 441.8229 | 409.1688
3722.9417 | 441.8752 | 409.1786
3723.9417 | 441.7098 | 409.1945
3724.9417 | 441.6113 | 409.2118
3725.9417 | 441.5584 | 409.2522
3726.9417 | 441.5841 | 409.2505
3727.9417 | 441.6677 | 409.2786
3728.9417 | 441.6668 | 409.3017
3729.9417 | 441.5847 | 409.3044
3730.9417 | 441.7085 | 409.3199
3731.9417 | 441.8082 | 409.3428
3732.9417 | 441.918 | 409.3514
3733.9417 | 442.0561 | 409.3624
3734.9417 | 441.936 | 409.3817
3735.9417 | 441.9623 | 409.4047
3736.9417 | 442.1399 | 409.3967
3737.9417 | 442.1575 | 409.4095
3738.9417 | 442.25 | 409.4267
3739.9417 | 442.2732 | 409.4392
3740.9417 | 442.3397 | 409.4578
3741.9417 | 442.3556 | 409.4523
3742.9417 | 442.3358 | 409.4795
3743.9417 | 442.2453 | 409.477
3744.9417 | 442.3272 | 409.5005
3745.9417 | 442.4882 | 409.5136
3746.9417 | 442.4728 | 409.5168
3747.9417 | 442.5427 | 409.5406
3748.9417 | 442.4954 | 409.5351
3749.9417 | 442.5501 | 409.5592
3750.9417 | 442.5398 | 409.5734
3751.9417 | 442.5707 | 409.6029
3752.9417 | 442.4913 | 409.6022
3753.9417 | 442.4991 | 409.6254
3754.9417 | 442.5373 | 409.6294
3755.9417 | 442.5695 | 409.6477
3756.9417 | 442.5368 | 409.6617
3757.9417 | 442.5347 | 409.6859
3758.9417 | 442.5631 | 409.681
3759.9417 | 442.5478 | 409.7044
3760.9417 | 442.4337 | 409.7216
3761.9417 | 442.5444 | 409.7367
3762.9417 | 442.7133 | 409.7427
3763.9417 | 442.8532 | 409.773
3764.9417 | 442.8484 | 409.7864
3765.9417 | 442.8572 | 409.7984
3766.9417 | 442.8061 | 409.8186
3767.9417 | 442.7561 | 409.8257
3768.9417 | 442.7782 | 409.8461
3769.9417 | 442.8843 | 409.8695
3770.9417 | 442.8461 | 409.8819
3771.9417 | 442.7004 | 409.9047
3772.9417 | 442.6112 | 409.9249
3773.9417 | 442.6428 | 409.9442
3774.9417 | 442.7068 | 409.9633
3775.9417 | 442.6789 | 409.9977
3776.9417 | 442.7087 | 410.0137
3777.9417 | 442.7614 | 410.0429
3778.9417 | 442.8039 | 410.0638
3779.9417 | 442.8434 | 410.071
3780.9417 | 442.7699 | 410.0986
3781.9417 | 442.8312 | 410.1309
3782.9417 | 442.8891 | 410.1584
3783.9417 | 442.8069 | 410.1643
3784.9417 | 442.7927 | 410.1921
3785.9417 | 442.8109 | 410.2055
3786.9417 | 442.7431 | 410.232
3787.9417 | 442.7366 | 410.2572
3788.9417 | 442.8102 | 410.2627
3789.9417 | 442.657 | 410.2658
3790.9417 | 442.5938 | 410.2849
3791.9417 | 442.5743 | 410.3112
3792.9417 | 442.56 | 410.3117
3793.9417 | 442.5413 | 410.33
3794.9417 | 442.5183 | 410.3389
3795.9417 | 442.3547 | 410.3558
3796.9417 | 442.2264 | 410.3616
3797.9417 | 442.214 | 410.3936
3798.9417 | 442.265 | 410.3723
3799.9417 | 442.2296 | 410.3921
3800.9417 | 442.2246 | 410.4094
3801.9417 | 442.1614 | 410.4064
3802.9417 | 442.1463 | 410.4352
3803.9417 | 442.1692 | 410.4367
3804.9417 | 442.2056 | 410.4352
3805.9417 | 442.2343 | 410.4615
3806.9417 | 442.1351 | 410.4502
3807.9417 | 442.1625 | 410.4841
3808.9417 | 442.2391 | 410.4952
3809.9417 | 442.2089 | 410.5038
3810.9417 | 442.0585 | 410.5111
3811.9417 | 442.0626 | 410.5215
3812.9417 | 442.0066 | 410.5141
3813.9417 | 441.8058 | 410.5191
3814.9417 | 441.6858 | 410.5506
3815.9417 | 441.6191 | 410.5415
3816.9417 | 441.6837 | 410.5543
3817.9417 | 441.609 | 410.569
3818.9417 | 441.5195 | 410.5851
3819.9417 | 441.4827 | 410.581
3820.9417 | 441.4757 | 410.5659
3821.9417 | 441.5313 | 410.5951
3822.9417 | 441.6099 | 410.5945
3823.9417 | 441.5277 | 410.6146
3824.9417 | 441.5452 | 410.6282
3825.9417 | 441.3793 | 410.6358
3826.9417 | 441.2661 | 410.6636
3827.9417 | 441.3246 | 410.6805
3828.9417 | 441.2676 | 410.6836
3829.9417 | 441.2557 | 410.6906
3830.9417 | 441.3389 | 410.7104
3831.9417 | 441.2312 | 410.7206
3832.9417 | 441.279 | 410.7295
3833.9417 | 441.3824 | 410.7513
3834.9417 | 441.4848 | 410.7688
3835.9417 | 441.6391 | 410.7704
3836.9417 | 441.6892 | 410.7875
3837.9417 | 441.5994 | 410.8148
3838.9417 | 441.6056 | 410.8368
3839.9417 | 441.6193 | 410.8542
3840.9417 | 441.6449 | 410.8569
3841.9417 | 441.7669 | 410.8968
3842.9417 | 441.8502 | 410.9068
3843.9417 | 441.9252 | 410.9348
3844.9417 | 441.8141 | 410.9453
3845.9417 | 441.7393 | 410.9832
3846.9417 | 441.8304 | 410.9967
3847.9417 | 441.8211 | 411.0226
3848.9417 | 441.6467 | 411.0411
3849.9417 | 441.5332 | 411.0806
3850.9417 | 441.5561 | 411.0732
3851.9417 | 441.5288 | 411.122
3852.9417 | 441.5214 | 411.129
3853.9417 | 441.5879 | 411.1621
3854.9417 | 441.6659 | 411.188
3855.9417 | 441.6727 | 411.2117
3856.9417 | 441.7156 | 411.2275
3857.9417 | 441.6715 | 411.2586
3858.9417 | 441.7721 | 411.2745
3859.9417 | 441.8277 | 411.2876
3860.9417 | 441.7844 | 411.3327
3861.9417 | 441.8105 | 411.361
3862.9417 | 441.7484 | 411.3849
3863.9417 | 441.7515 | 411.4065
3864.9417 | 441.6113 | 411.4299
3865.9417 | 441.3402 | 411.4518
3866.9417 | 441.3273 | 411.4752
3867.9417 | 441.3783 | 411.5127
3868.9417 | 441.4877 | 411.5237
3869.9417 | 441.4939 | 411.5404
3870.9417 | 441.3485 | 411.5664
3871.9417 | 441.2391 | 411.5821
3872.9417 | 441.2059 | 411.6114
3873.9417 | 441.2658 | 411.6105
3874.9417 | 441.3819 | 411.6467
3875.9417 | 441.259 | 411.6487
3876.9417 | 441.1592 | 411.6709
3877.9417 | 441.3089 | 411.6836
3878.9417 | 441.391 | 411.6881
3879.9417 | 441.2769 | 411.7069
3880.9417 | 441.3604 | 411.7357
3881.9417 | 441.5404 | 411.7529
3882.9417 | 441.6329 | 411.7483
3883.9417 | 441.6756 | 411.771
3884.9417 | 441.5732 | 411.7885
3885.9417 | 441.5291 | 411.7999
3886.9417 | 441.571 | 411.808
3887.9417 | 441.7184 | 411.8275
3888.9417 | 441.7593 | 411.8383
3889.9417 | 441.7707 | 411.8371
3890.9417 | 441.7884 | 411.8501
3891.9417 | 441.8781 | 411.8644
3892.9417 | 441.9289 | 411.8646
3893.9417 | 441.9101 | 411.8699
3894.9417 | 441.9413 | 411.8656
3895.9417 | 442.0487 | 411.9033
3896.9417 | 442.0092 | 411.9052
3897.9417 | 442.0254 | 411.9236
3898.9417 | 442.0437 | 411.9307
3899.9417 | 442.056 | 411.9394
3900.9417 | 442.0819 | 411.9538
3901.9417 | 442.1293 | 411.9651
3902.9417 | 442.0955 | 411.9649
3903.9417 | 442.0536 | 411.9898
3904.9417 | 442.0322 | 411.989
3905.9417 | 441.9663 | 412.0193
3906.9417 | 442.0557 | 412.0248
3907.9417 | 441.9476 | 412.0524
3908.9417 | 441.9278 | 412.0732
3909.9417 | 441.8618 | 412.0805
3910.9417 | 441.7602 | 412.0932
3911.9417 | 441.7761 | 412.1234
3912.9417 | 441.8102 | 412.1348
3913.9417 | 441.827 | 412.148
3914.9417 | 441.7553 | 412.1726
3915.9417 | 441.7959 | 412.1804
3916.9417 | 441.5928 | 412.2051
3917.9417 | 441.4826 | 412.2174
3918.9417 | 441.492 | 412.2281
3919.9417 | 441.4739 | 412.2642
3920.9417 | 441.5148 | 412.2705
3921.9417 | 441.5106 | 412.3026
3922.9417 | 441.5452 | 412.3108
3923.9417 | 441.5649 | 412.329
3924.9417 | 441.6409 | 412.3319
3925.9417 | 441.5753 | 412.3821
3926.9417 | 441.5025 | 412.3792
3927.9417 | 441.5351 | 412.3961
3928.9417 | 441.6558 | 412.4222
3929.9417 | 441.8596 | 412.4253
3930.9417 | 441.8275 | 412.4414
3931.9417 | 441.7656 | 412.4574
3932.9417 | 441.774 | 412.4608
3933.9417 | 441.805 | 412.4681
3934.9417 | 441.7976 | 412.4803
3935.9417 | 441.7022 | 412.4472
3936.9417 | 441.7912 | 412.4856
3937.9417 | 441.7272 | 412.4965
3938.9417 | 441.6117 | 412.4986
3939.9417 | 441.5315 | 412.5135
3940.9417 | 441.503 | 412.511
3941.9417 | 441.5877 | 412.5258
3942.9417 | 441.5941 | 412.5395
3943.9417 | 441.4617 | 412.535
3944.9417 | 441.3554 | 412.5398
3945.9417 | 441.33 | 412.5742
3946.9417 | 441.2632 | 412.569
3947.9417 | 441.1779 | 412.587
3948.9417 | 441.1415 | 412.5938
3949.9417 | 440.9865 | 412.6193
3950.9417 | 440.9395 | 412.6342
3951.9417 | 440.9718 | 412.6538
3952.9417 | 441.0382 | 412.6545
3953.9417 | 441.1297 | 412.6845
3954.9417 | 441.1133 | 412.6934
3955.9417 | 441.2095 | 412.72
3956.9417 | 441.2464 | 412.7283
3957.9417 | 441.2726 | 412.7521
3958.9417 | 441.2062 | 412.7784
3959.9417 | 441.0758 | 412.7898
3960.9417 | 440.9916 | 412.805
3961.9417 | 441.0851 | 412.8282
3962.9417 | 441.1952 | 412.8312
3963.9417 | 441.3613 | 412.8622
3964.9417 | 441.4659 | 412.8792
3965.9417 | 441.6189 | 412.9086
3966.9417 | 441.6439 | 412.9184
3967.9417 | 441.6001 | 412.936
3968.9417 | 441.6955 | 412.9523
3969.9417 | 441.7598 | 412.9568
3970.9417 | 441.7824 | 412.9508
3971.9417 | 441.8247 | 412.9785
3972.9417 | 441.8153 | 413.0166
3973.9417 | 441.9164 | 413.0378
3974.9417 | 442.0379 | 413.0421
3975.9417 | 442.1343 | 413.054
3976.9417 | 442.1124 | 413.0734
3977.9417 | 442.0402 | 413.1022
3978.9417 | 442.0614 | 413.0919
3979.9417 | 442.1218 | 413.1206
3980.9417 | 442.0741 | 413.1197
3981.9417 | 442.0077 | 413.1397
3982.9417 | 441.8429 | 413.1571
3983.9417 | 441.6628 | 413.1794
3984.9417 | 441.6087 | 413.1811
3985.9417 | 441.6231 | 413.2012
3986.9417 | 441.5894 | 413.2048
3987.9417 | 441.4241 | 413.2127
3988.9417 | 441.3415 | 413.2184
3989.9417 | 441.3045 | 413.2357
3990.9417 | 441.3791 | 413.2439
3991.9417 | 441.3682 | 413.2374
3992.9417 | 441.2259 | 413.2628
3993.9417 | 441.2143 | 413.2375
3994.9417 | 441.1406 | 413.2723
3995.9417 | 441.165 | 413.2564
3996.9417 | 441.1632 | 413.2717
3997.9417 | 441.2873 | 413.2829
3998.9417 | 441.3713 | 413.2823
3999.9417 | 441.4597 | 413.2873
4000.9417 | 441.4902 | 413.2947
4001.9417 | 441.4944 | 413.2839
4002.9417 | 441.4732 | 413.2919
4003.9417 | 441.5214 | 413.2786
4004.9417 | 441.631 | 413.3091
4005.9417 | 441.6339 | 413.3145
4006.9417 | 441.6622 | 413.3148
4007.9417 | 441.6559 | 413.3119
4008.9417 | 441.5525 | 413.306
4009.9417 | 441.4859 | 413.3077
4010.9417 | 441.445 | 413.3196
4011.9417 | 441.28 | 413.3275
4012.9417 | 441.3514 | 413.3345
4013.9417 | 441.3869 | 413.352
4014.9417 | 441.3449 | 413.3578
4015.9417 | 441.3561 | 413.3721
4016.9417 | 441.3724 | 413.3725
4017.9417 | 441.3314 | 413.3821
4018.9417 | 441.2848 | 413.4073
4019.9417 | 441.4059 | 413.4316
4020.9417 | 441.3346 | 413.4328
4021.9417 | 441.1739 | 413.4425
4022.9417 | 441.1115 | 413.4568
4023.9417 | 441.1806 | 413.478
4024.9417 | 441.1898 | 413.4906
4025.9417 | 441.1436 | 413.4891
4026.9417 | 441.243 | 413.5144
4027.9417 | 441.1729 | 413.5424
4028.9417 | 441.2599 | 413.5444
4029.9417 | 441.3289 | 413.5584
4030.9417 | 441.3026 | 413.5873
4031.9417 | 441.2517 | 413.5972
4032.9417 | 441.272 | 413.6133
4033.9417 | 441.2223 | 413.6326
4034.9417 | 441.2048 | 413.6343
4035.9417 | 441.2317 | 413.6544
4036.9417 | 441.2316 | 413.6666
4037.9417 | 441.2246 | 413.6697
4038.9417 | 441.3329 | 413.7073
4039.9417 | 441.3975 | 413.7157
4040.9417 | 441.4939 | 413.7301
4041.9417 | 441.5127 | 413.7393
4042.9417 | 441.4885 | 413.7659
4043.9417 | 441.5022 | 413.7775
4044.9417 | 441.6114 | 413.7931
4045.9417 | 441.5833 | 413.8184
4046.9417 | 441.6823 | 413.816
4047.9417 | 441.6606 | 413.8321
4048.9417 | 441.6316 | 413.8519
4049.9417 | 441.5556 | 413.8735
4050.9417 | 441.5583 | 413.8879
4051.9417 | 441.6369 | 413.8961
4052.9417 | 441.6841 | 413.9154
4053.9417 | 441.7088 | 413.9302
4054.9417 | 441.533 | 413.9446
4055.9417 | 441.5031 | 413.9551
4056.9417 | 441.4283 | 413.9599
4057.9417 | 441.3156 | 413.9814
4058.9417 | 441.3102 | 413.9781
4059.9417 | 441.3904 | 413.9991
4060.9417 | 441.5208 | 414.0058
4061.9417 | 441.518 | 414.0174
4062.9417 | 441.4527 | 414.0332
4063.9417 | 441.4218 | 414.0354
4064.9417 | 441.4272 | 414.0359
4065.9417 | 441.5008 | 414.0476
4066.9417 | 441.4548 | 414.0458
4067.9417 | 441.4305 | 414.0616
4068.9417 | 441.4892 | 414.0707
4069.9417 | 441.6223 | 414.0673
4070.9417 | 441.6482 | 414.0603
4071.9417 | 441.6027 | 414.061
4072.9417 | 441.62 | 414.053
4073.9417 | 441.6167 | 414.0646
4074.9417 | 441.4491 | 414.0657
4075.9417 | 441.3743 | 414.0682
4076.9417 | 441.3636 | 414.0555
4077.9417 | 441.3415 | 414.0771
4078.9417 | 441.3757 | 414.0669
4079.9417 | 441.4132 | 414.0739
4080.9417 | 441.3781 | 414.0704
4081.9417 | 441.3025 | 414.0644
4082.9417 | 441.3518 | 414.0599
4083.9417 | 441.4523 | 414.0794
4084.9417 | 441.4897 | 414.0621
4085.9417 | 441.5447 | 414.0621
4086.9417 | 441.6252 | 414.0733
4087.9417 | 441.5756 | 414.0651
4088.9417 | 441.6313 | 414.0729
4089.9417 | 441.4778 | 414.0681
4090.9417 | 441.458 | 414.0699
4091.9417 | 441.4778 | 414.0795
4092.9417 | 441.3762 | 414.0736
4093.9417 | 441.2973 | 414.0572
4094.9417 | 441.219 | 414.086
4095.9417 | 441.2972 | 414.0733
4096.9417 | 441.3962 | 414.0904
4097.9417 | 441.4906 | 414.1
4098.9417 | 441.2686 | 414.1178
4099.9417 | 441.1532 | 414.1139
4100.9417 | 441.1666 | 414.112
4101.9417 | 441.1467 | 414.1432
4102.9417 | 441.0948 | 414.1535
4103.9417 | 441.1156 | 414.1706
4104.9417 | 441.0938 | 414.1745
4105.9417 | 441.0703 | 414.1849
4106.9417 | 441.046 | 414.2076
4107.9417 | 441.0274 | 414.2216
4108.9417 | 441.0333 | 414.2373
4109.9417 | 441.0604 | 414.2524
4110.9417 | 441.174 | 414.2721
4111.9417 | 441.2748 | 414.2902
4112.9417 | 441.24 | 414.3067
4113.9417 | 441.3304 | 414.3172
4114.9417 | 441.335 | 414.3315
4115.9417 | 441.4601 | 414.3521
4116.9417 | 441.4555 | 414.3674
4117.9417 | 441.4315 | 414.3805
4118.9417 | 441.3259 | 414.3856
4119.9417 | 441.2521 | 414.4075
4120.9417 | 441.357 | 414.4164
4121.9417 | 441.3948 | 414.3927
4122.9417 | 441.3276 | 414.4215
4123.9417 | 441.2338 | 414.42
4124.9417 | 441.2278 | 414.441
4125.9417 | 441.2383 | 414.4431
4126.9417 | 441.3308 | 414.4416
4127.9417 | 441.409 | 414.4411
4128.9417 | 441.5236 | 414.4449
4129.9417 | 441.5385 | 414.457
4130.9417 | 441.6454 | 414.4436
4131.9417 | 441.5865 | 414.4662
4132.9417 | 441.6869 | 414.4649
4133.9417 | 441.8269 | 414.472
4134.9417 | 441.7846 | 414.4692
4135.9417 | 441.8447 | 414.4723
4136.9417 | 441.8721 | 414.4907
4137.9417 | 441.8342 | 414.4887
4138.9417 | 441.6799 | 414.4937
4139.9417 | 441.5815 | 414.5022
4140.9417 | 441.5498 | 414.4959
4141.9417 | 441.4368 | 414.509
4142.9417 | 441.5017 | 414.5266
4143.9417 | 441.3376 | 414.5429
4144.9417 | 441.2665 | 414.5502
4145.9417 | 441.2858 | 414.5674
4146.9417 | 441.2985 | 414.5629
4147.9417 | 441.4287 | 414.5844
4148.9417 | 441.387 | 414.5823
4149.9417 | 441.3951 | 414.6065
4150.9417 | 441.3812 | 414.5924
4151.9417 | 441.3895 | 414.6204
4152.9417 | 441.4364 | 414.625
4153.9417 | 441.5377 | 414.6185
4154.9417 | 441.5826 | 414.6388
4155.9417 | 441.5595 | 414.6513
4156.9417 | 441.5144 | 414.6645
4157.9417 | 441.4694 | 414.669
4158.9417 | 441.517 | 414.6761
4159.9417 | 441.5262 | 414.6671
4160.9417 | 441.5368 | 414.6876
4161.9417 | 441.5778 | 414.6937
4162.9417 | 441.6839 | 414.7016
4163.9417 | 441.6767 | 414.7053
4164.9417 | 441.5125 | 414.7205
4165.9417 | 441.4367 | 414.7227
4166.9417 | 441.3661 | 414.7237
4167.9417 | 441.2796 | 414.7265
4168.9417 | 441.2926 | 414.7228
4169.9417 | 441.2218 | 414.7245
4170.9417 | 441.2807 | 414.7417
4171.9417 | 441.3925 | 414.7382
4172.9417 | 441.512 | 414.7403
4173.9417 | 441.5701 | 414.7407
4174.9417 | 441.4725 | 414.7481
4175.9417 | 441.5358 | 414.7318
4176.9417 | 441.6517 | 414.7357
4177.9417 | 441.6538 | 414.7439
4178.9417 | 441.6399 | 414.7325
4179.9417 | 441.7073 | 414.7346
4180.9417 | 441.6715 | 414.7285
4181.9417 | 441.6862 | 414.7177
4182.9417 | 441.7746 | 414.6971
4183.9417 | 441.7946 | 414.7078
4184.9417 | 441.7537 | 414.7115
4185.9417 | 441.7457 | 414.6966
4186.9417 | 441.6214 | 414.6965
4187.9417 | 441.4973 | 414.6897
4188.9417 | 441.3857 | 414.6819
4189.9417 | 441.3583 | 414.6658
4190.9417 | 441.3588 | 414.6571
4191.9417 | 441.2974 | 414.6409
4192.9417 | 441.2839 | 414.6395
4193.9417 | 441.3266 | 414.6364
4194.9417 | 441.4036 | 414.6131
4195.9417 | 441.5128 | 414.6337
4196.9417 | 441.6121 | 414.6053
4197.9417 | 441.6273 | 414.6243
4198.9417 | 441.4037 | 414.6137
4199.9417 | 441.4318 | 414.6082
4200.9417 | 441.3312 | 414.599
4201.9417 | 441.3673 | 414.6033
4202.9417 | 441.3941 | 414.6031
4203.9417 | 441.3249 | 414.5955
4204.9417 | 441.3967 | 414.5905
4205.9417 | 441.2948 | 414.5707
4206.9417 | 441.4583 | 414.585
4207.9417 | 441.4948 | 414.5869
4208.9417 | 441.6105 | 414.5918
4209.9417 | 441.702 | 414.5753
4210.9417 | 441.8289 | 414.589
4211.9417 | 441.941 | 414.5957
4212.9417 | 441.9508 | 414.6066
4213.9417 | 441.9263 | 414.603
4214.9417 | 441.8378 | 414.6145
4215.9417 | 441.889 | 414.6196
4216.9417 | 441.7795 | 414.6348
4217.9417 | 441.6736 | 414.6452
4218.9417 | 441.5075 | 414.6478
4219.9417 | 441.4581 | 414.6681
4220.9417 | 441.4765 | 414.6733
4221.9417 | 441.4324 | 414.6843
4222.9417 | 441.517 | 414.6978
4223.9417 | 441.5328 | 414.6918
4224.9417 | 441.5397 | 414.7269
4225.9417 | 441.5859 | 414.7237
4226.9417 | 441.583 | 414.7402
4227.9417 | 441.5335 | 414.7431
4228.9417 | 441.4398 | 414.753
4229.9417 | 441.4062 | 414.7757
4230.9417 | 441.503 | 414.7778
4231.9417 | 441.5916 | 414.7861
4232.9417 | 441.6226 | 414.7964
4233.9417 | 441.638 | 414.8047
4234.9417 | 441.6257 | 414.8022
4235.9417 | 441.4937 | 414.7701
4236.9417 | 441.3026 | 414.8268
4237.9417 | 441.1938 | 414.8415
4238.9417 | 441.1458 | 414.8276
4239.9417 | 441.158 | 414.8334
4240.9417 | 441.2536 | 414.8693
4241.9417 | 441.2276 | 414.8563
4242.9417 | 441.2725 | 414.8791
4243.9417 | 441.3291 | 414.8861
4244.9417 | 441.3054 | 414.8843
4245.9417 | 441.4288 | 414.8862
4246.9417 | 441.3985 | 414.9012
4247.9417 | 441.2738 | 414.9039
4248.9417 | 441.2386 | 414.9054
4249.9417 | 441.312 | 414.9153
4250.9417 | 441.4549 | 414.926
4251.9417 | 441.5263 | 414.9304
4252.9417 | 441.7255 | 414.9496
4253.9417 | 441.8289 | 414.937
4254.9417 | 441.8805 | 414.9496
4255.9417 | 441.9434 | 414.9603
4256.9417 | 441.878 | 414.9492
4257.9417 | 441.9009 | 414.9526
4258.9417 | 441.8932 | 414.954
4259.9417 | 441.883 | 414.9564
4260.9417 | 441.7841 | 414.9455
4261.9417 | 441.8175 | 414.9379
4262.9417 | 441.9456 | 414.9389
4263.9417 | 442.1062 | 414.9371
4264.9417 | 442.1366 | 414.915
4265.9417 | 442.1505 | 414.9232
4266.9417 | 442.263 | 414.9083
4267.9417 | 442.3033 | 414.8995
4268.9417 | 442.3996 | 414.8959
4269.9417 | 442.3421 | 414.8845
4270.9417 | 442.2778 | 414.8741
4271.9417 | 442.1554 | 414.8663
4272.9417 | 441.9917 | 414.8662
4273.9417 | 441.9709 | 414.8539
4274.9417 | 442.0304 | 414.8586
4275.9417 | 441.9925 | 414.8666
4276.9417 | 441.996 | 414.8747
4277.9417 | 441.8479 | 414.8822
4278.9417 | 441.9348 | 414.8583
4279.9417 | 441.9603 | 414.862
4280.9417 | 441.9749 | 414.8688
4281.9417 | 441.9549 | 414.8786
4282.9417 | 442.0237 | 414.8881
4283.9417 | 442.0162 | 414.8762
4284.9417 | 441.9725 | 414.8974
4285.9417 | 441.8502 | 414.9018
4286.9417 | 441.8797 | 414.8974
4287.9417 | 441.9597 | 414.8998
4288.9417 | 441.955 | 414.898
4289.9417 | 441.9345 | 414.9224
4290.9417 | 441.8555 | 414.9284
4291.9417 | 441.7734 | 414.9295
4292.9417 | 441.8068 | 414.9368
4293.9417 | 441.9521 | 414.9585
4294.9417 | 441.9909 | 414.9637
4295.9417 | 442.1741 | 414.9758
4296.9417 | 442.0296 | 414.9825
4297.9417 | 442.0981 | 415.0023
4298.9417 | 442.0561 | 415.0099
4299.9417 | 442.0208 | 415.014
4300.9417 | 442.1302 | 415.0178
4301.9417 | 442.0225 | 415.0169
4302.9417 | 442.1416 | 415.0456
4303.9417 | 442.2032 | 415.0484
4304.9417 | 442.2329 | 415.0599
4305.9417 | 442.3955 | 415.0597
4306.9417 | 442.4947 | 415.067
4307.9417 | 442.4736 | 415.0625
4308.9417 | 442.4157 | 415.0865
4309.9417 | 442.5193 | 415.095
4310.9417 | 442.7147 | 415.1117
4311.9417 | 442.7306 | 415.1136
4312.9417 | 442.6686 | 415.1121
4313.9417 | 442.5965 | 415.1209
4314.9417 | 442.4483 | 415.1298
4315.9417 | 442.4093 | 415.132
4316.9417 | 442.3596 | 415.1455
4317.9417 | 442.3874 | 415.1462
4318.9417 | 442.5312 | 415.1438
4319.9417 | 442.5232 | 415.1429
4320.9417 | 442.4766 | 415.1613
4321.9417 | 442.5942 | 415.1695
4322.9417 | 442.6127 | 415.1747
4323.9417 | 442.4915 | 415.1596
4324.9417 | 442.4362 | 415.176
4325.9417 | 442.4047 | 415.1788
4326.9417 | 442.2365 | 415.1917
4327.9417 | 442.1486 | 415.1949
4328.9417 | 442.0469 | 415.203
4329.9417 | 442.0978 | 415.2026
4330.9417 | 442.1526 | 415.2098
4331.9417 | 441.944 | 415.2226
4332.9417 | 441.9645 | 415.2219
4333.9417 | 442.1475 | 415.2262
4334.9417 | 442.2661 | 415.2375
4335.9417 | 442.4351 | 415.2288
4336.9417 | 442.5029 | 415.2463
4337.9417 | 442.5117 | 415.2452
4338.9417 | 442.3272 | 415.248
4339.9417 | 442.2702 | 415.2508
4340.9417 | 442.3168 | 415.2482
4341.9417 | 442.2972 | 415.2582
4342.9417 | 442.3765 | 415.2621
4343.9417 | 442.3623 | 415.2587
4344.9417 | 442.324 | 415.2743
4345.9417 | 442.3214 | 415.284
4346.9417 | 442.2033 | 415.2771
4347.9417 | 442.189 | 415.2765
4348.9417 | 442.1853 | 415.2737
4349.9417 | 442.1289 | 415.2696
4350.9417 | 442.0871 | 415.2669
4351.9417 | 442.1187 | 415.2774
4352.9417 | 442.1506 | 415.2587
4353.9417 | 442.1055 | 415.2783
4354.9417 | 442.1138 | 415.2706
4355.9417 | 442.1047 | 415.265
4356.9417 | 442.0008 | 415.269
4357.9417 | 441.9657 | 415.2609
4358.9417 | 442.0652 | 415.2489
4359.9417 | 442.1295 | 415.2476
4360.9417 | 442.1412 | 415.2388
4361.9417 | 442.0808 | 415.2493
4362.9417 | 442.0321 | 415.2366
4363.9417 | 442.051 | 415.2216
4364.9417 | 442.2011 | 415.2351
4365.9417 | 442.1619 | 415.2273
4366.9417 | 442.0936 | 415.2341
4367.9417 | 442.0676 | 415.2214
4368.9417 | 442.2002 | 415.2366
4369.9417 | 442.2808 | 415.2376
4370.9417 | 442.3148 | 415.241
4371.9417 | 442.3185 | 415.2434
4372.9417 | 442.3989 | 415.2588
4373.9417 | 442.3835 | 415.2672
4374.9417 | 442.343 | 415.2802
4375.9417 | 442.4091 | 415.2795
4376.9417 | 442.4811 | 415.2795
4377.9417 | 442.6005 | 415.2986
4378.9417 | 442.7214 | 415.2972
4379.9417 | 442.8375 | 415.317
4380.9417 | 442.671 | 415.313
4381.9417 | 442.6124 | 415.3325
4382.9417 | 442.6407 | 415.3192
4383.9417 | 442.7107 | 415.3472
4384.9417 | 442.7105 | 415.3538
4385.9417 | 442.6165 | 415.3604
4386.9417 | 442.3317 | 415.3767
4387.9417 | 442.1461 | 415.3698
4388.9417 | 442.0047 | 415.3864
4389.9417 | 441.9594 | 415.4444
4390.9417 | 441.9698 | 415.5805
4391.9417 | 442.0451 | 415.7516
4392.9417 | 442.1303 | 415.8694
4393.9417 | 442.138 | 416.103
4394.9417 | 442.1286 | 416.3976
4395.9417 | 442.2145 | 417.176
4396.9417 | 442.2479 | 417.7508
4397.9417 | 442.3525 | 418.2276
4398.9417 | 442.5204 | 418.7035
4399.9417 | 442.5968 | 419.3817
4400.9417 | 442.7575 | 420.3469
4401.9417 | 442.9115 | 421.3129
4402.9417 | 443.0785 | 422.2048
4403.9417 | 443.2101 | 422.26
4404.9417 | 443.3198 | 423.0664
4405.9417 | 443.5557 | 423.9262
4406.9417 | 443.6635 | 424.5039
4407.9417 | 443.9437 | 425.7653
4408.9417 | 444.1086 | 426.7971
4409.9417 | 444.2247 | 427.9689
4410.9417 | 444.3741 | 430.3857
4411.9417 | 444.3587 | 433.3942
4412.9417 | 444.3941 | 436.3942
4413.9417 | 444.4361 | 439.3071
4414.9417 | 444.5449 | 442.2642
4415.9417 | 444.4353 | 445.0981
4416.9417 | 444.4468 | 448.0902
4417.9417 | 444.5778 | 451.2429
4418.9417 | 444.5874 | 454.3124
4419.9417 | 444.6495 | 457.5424
4420.9417 | 444.7597 | 461.6887
4421.9417 | 444.952 | 466.7861
4422.9417 | 445.1461 | 476.0344
4423.9417 | 445.3242 | 484.9469
4424.9417 | 445.4397 | 526.4345
4425.9417 | 445.4018 | 566.4475
4426.9417 | 445.3947 | 586.4175
4427.9417 | 445.5125 | 609.7758
4428.9417 | 445.5953 | 624.5044
4429.9417 | 445.5985 | 643.091
4430.9417 | 445.5019 | 670.083
4431.9417 | 445.4243 | 678.4077
4432.9417 | 445.3837 | 685.0416
4433.9417 | 445.3505 | 690.3326
4434.9417 | 445.3679 | 700.0756
4435.9417 | 445.3805 | 700.9884
4436.9417 | 445.3453 | 700.4216
4437.9417 | 445.2864 | 695.5667
4438.9417 | 445.1604 | 691.2841
4439.9417 | 445.08 | 689.8691
4440.9417 | 444.9908 | 687.7564
4441.9417 | 444.801 | 685.5382
4442.9417 | 444.8956 | 685.6606
4443.9417 | 444.7965 | 681.8046
4444.9417 | 444.5725 | 680.9246
4445.9417 | 444.5065 | 678.7719
4446.9417 | 444.4806 | 676.4409
4447.9417 | 444.527 | 673.6196
4448.9417 | 444.4536 | 671.4116
4449.9417 | 444.3888 | 670.8602
4450.9417 | 444.3499 | 674.3598
4451.9417 | 444.3082 | 674.6485
4452.9417 | 444.2974 | 676.8151
4453.9417 | 444.382 | 677.8536
4454.9417 | 444.3081 | 680.8683
4455.9417 | 444.2219 | 681.9913
4456.9417 | 444.2399 | 682.6881
4457.9417 | 444.1754 | 683.5993
4458.9417 | 444.1135 | 684.675
4459.9417 | 444.0413 | 685.7736
4460.9417 | 443.9633 | 685.1652
4461.9417 | 443.9449 | 686.7185
4462.9417 | 443.9391 | 690.5069
4463.9417 | 443.7535 | 693.7255
4464.9417 | 443.6021 | 697.6104
4465.9417 | 443.5472 | 701.2529
4466.9417 | 443.6063 | 703.5999
4467.9417 | 443.5755 | 710.1046
4468.9417 | 443.4754 | 709.7888
4469.9417 | 443.3476 | 708.9447
4470.9417 | 443.3329 | 709.512
4471.9417 | 443.2908 | 710.6785
4472.9417 | 443.2923 | 712.0086
4473.9417 | 443.1475 | 714.8131
4474.9417 | 443.114 | 717.1815
4475.9417 | 443.1019 | 718.1123
4476.9417 | 443.0774 | 718.8816
4477.9417 | 443.061 | 719.2888
4478.9417 | 443.1012 | 716.9357
4479.9417 | 443.0906 | 714.6791
4480.9417 | 443.0484 | 713.5541
4481.9417 | 443.0195 | 713.1096
4482.9417 | 442.9187 | 713.601
4483.9417 | 442.8353 | 713.4851
4484.9417 | 442.76 | 713.4024
4485.9417 | 442.7337 | 711.5276
4486.9417 | 442.7714 | 712.4313
4487.9417 | 442.7973 | 712.4466
4488.9417 | 443.0008 | 713.6533
4489.9417 | 442.9921 | 715.1036
4490.9417 | 442.9406 | 715.6757
4491.9417 | 442.8786 | 717.4825
4492.9417 | 442.8185 | 719.6488
4493.9417 | 442.7529 | 720.0122
4494.9417 | 442.7723 | 719.2897
4495.9417 | 442.7179 | 722.2242
4496.9417 | 442.6409 | 725.494
4497.9417 | 442.7136 | 728.2115
4498.9417 | 442.741 | 730.3007
4499.9417 | 442.7374 | 736.2935
4500.9417 | 442.7073 | 736.1662
4501.9417 | 442.7832 | 741.0069
4502.9417 | 442.894 | 740.4655
4503.9417 | 442.9862 | 736.7418
4504.9417 | 443.0922 | 740.3465
4505.9417 | 443.1558 | 743.3694
4506.9417 | 443.127 | 742.1381
4507.9417 | 443.1047 | 743.2153
4508.9417 | 443.1234 | 743.2497
4509.9417 | 443.1559 | 741.8245
4510.9417 | 443.1823 | 743.1587
4511.9417 | 443.2297 | 744.0641
4512.9417 | 443.2266 | 746.0636
4513.9417 | 443.1855 | 744.0105
4514.9417 | 443.2195 | 742.8533
4515.9417 | 443.2322 | 741.7727
4516.9417 | 443.28 | 741.0778
4517.9417 | 443.2874 | 741.4927
4518.9417 | 443.3039 | 739.84
4519.9417 | 443.4709 | 739.0884
4520.9417 | 443.496 | 738.743
4521.9417 | 443.4063 | 739.2524
4522.9417 | 443.3761 | 739.3148
4523.9417 | 443.3141 | 738.4815
4524.9417 | 443.2857 | 736.2839
4525.9417 | 443.3112 | 736.9007
4526.9417 | 443.2992 | 735.8821
4527.9417 | 443.2162 | 735.8903
4528.9417 | 443.1879 | 735.9862
4529.9417 | 443.2446 | 735.1789
4530.9417 | 443.303 | 735.2647
4531.9417 | 443.2928 | 736.051
4532.9417 | 443.2084 | 735.9741
4533.9417 | 443.0999 | 736.1888
4534.9417 | 443.0386 | 734.9661
4535.9417 | 442.9834 | 735.0893
4536.9417 | 442.9454 | 734.8147
4537.9417 | 442.9166 | 733.5709
4538.9417 | 442.9418 | 733.8384
4539.9417 | 443.0817 | 733.0617
4540.9417 | 443.1318 | 734.0052
4541.9417 | 443.206 | 733.2674
4542.9417 | 443.3321 | 733.1404
4543.9417 | 443.4075 | 732.3936
4544.9417 | 443.3752 | 731.2071
4545.9417 | 443.3016 | 730.903
4546.9417 | 443.3002 | 731.2539
4547.9417 | 443.2977 | 730.2377
4548.9417 | 443.2617 | 731.0693
4549.9417 | 443.1844 | 730.2106
4550.9417 | 443.2026 | 730.0613
4551.9417 | 443.1884 | 729.7685
4552.9417 | 443.1684 | 729.7332
4553.9417 | 443.2216 | 729.1379
4554.9417 | 443.2284 | 728.3514
4555.9417 | 443.203 | 728.2043
4556.9417 | 443.2064 | 727.7425
4557.9417 | 443.201 | 727.0999
4558.9417 | 443.1303 | 727.5729
4559.9417 | 443.1667 | 727.7369
4560.9417 | 443.249 | 728.1841
4561.9417 | 443.1991 | 728.7096
4562.9417 | 443.2031 | 728.1219
4563.9417 | 443.1864 | 727.9038
4564.9417 | 443.1837 | 727.766
4565.9417 | 443.1295 | 727.3204
4566.9417 | 443.0877 | 726.2484
4567.9417 | 443.0831 | 726.0739
4568.9417 | 443.0887 | 726.3933
4569.9417 | 443.0532 | 726.2274
4570.9417 | 443.0086 | 725.5095
4571.9417 | 442.9664 | 725.2942
4572.9417 | 442.9949 | 724.2551
4573.9417 | 443.0095 | 723.9682
4574.9417 | 442.8857 | 723.5972
4575.9417 | 442.8129 | 723.1507
4576.9417 | 442.7262 | 723.3993
4577.9417 | 442.6714 | 722.7942
4578.9417 | 442.6259 | 722.5742
4579.9417 | 442.7074 | 722.0838
4580.9417 | 442.7278 | 722.2843
4581.9417 | 442.7281 | 721.8851
4582.9417 | 442.6789 | 721.4838
4583.9417 | 442.6595 | 720.996
4584.9417 | 442.6559 | 720.5217
4585.9417 | 442.7038 | 719.9886
4586.9417 | 442.7828 | 719.4881
4587.9417 | 442.8302 | 718.7908
4588.9417 | 442.7352 | 718.2779
4589.9417 | 442.6326 | 717.0614
4590.9417 | 442.6319 | 717.1491
4591.9417 | 442.6423 | 716.7678
4592.9417 | 442.6657 | 716.1806
4593.9417 | 442.6843 | 716.2923
4594.9417 | 442.6846 | 716.3099
4595.9417 | 442.6737 | 716.5794
4596.9417 | 442.6729 | 716.8112
4597.9417 | 442.6373 | 716.6095
4598.9417 | 442.6301 | 716.0635
4599.9417 | 442.6624 | 715.4273
4600.9417 | 442.7181 | 714.2863
4601.9417 | 442.7104 | 713.8821
4602.9417 | 442.682 | 713.4922
4603.9417 | 442.6054 | 713.1397
4604.9417 | 442.5111 | 712.224
4605.9417 | 442.4919 | 711.5472
4606.9417 | 442.4374 | 711.2047
4607.9417 | 442.3221 | 711.252
4608.9417 | 442.244 | 710.5477
4609.9417 | 442.2571 | 710.262
4610.9417 | 442.179 | 710.1198
4611.9417 | 442.2311 | 709.6367
4612.9417 | 442.2256 | 709.5391
4613.9417 | 442.1538 | 708.423
4614.9417 | 442.1097 | 707.4922
4615.9417 | 442.0351 | 706.7356
4616.9417 | 442.0078 | 706.6731
4617.9417 | 441.9957 | 706.4006
4618.9417 | 441.9517 | 706.1128
4619.9417 | 441.778 | 705.8781
4620.9417 | 441.689 | 704.6017
4621.9417 | 441.7115 | 704.5635
4622.9417 | 441.7516 | 703.9392
4623.9417 | 441.7187 | 702.9638
4624.9417 | 441.602 | 703.595
4625.9417 | 441.4056 | 703.734
4626.9417 | 441.2143 | 703.3393
4627.9417 | 440.9914 | 702.599
4628.9417 | 440.8588 | 702.3883
4629.9417 | 440.6035 | 701.9414
4630.9417 | 440.3109 | 701.7182
4631.9417 | 440.094 | 701.7855
4632.9417 | 439.9995 | 701.6788
4633.9417 | 439.9329 | 701.3777
4634.9417 | 439.849 | 700.6448
4635.9417 | 439.7173 | 700.5803
4636.9417 | 439.4419 | 700.3342
4637.9417 | 439.2352 | 699.9658
4638.9417 | 439.0219 | 699.2334
4639.9417 | 438.7517 | 698.9238
4640.9417 | 438.5788 | 698.2822
4641.9417 | 438.3065 | 697.3327
4642.9417 | 438.0861 | 697.037
4643.9417 | 437.7455 | 697.4895
4644.9417 | 437.4397 | 697.2371
4645.9417 | 437.2245 | 697.5699
4646.9417 | 436.8917 | 698.1087
4647.9417 | 436.5826 | 698.2338
4648.9417 | 436.3048 | 698.4549
4649.9417 | 436.0366 | 697.8038
4650.9417 | 435.8706 | 697.6377
4651.9417 | 435.6568 | 697.5269
4652.9417 | 435.4186 | 696.6593
4653.9417 | 435.2121 | 695.5589
4654.9417 | 435.0424 | 695.0187
4655.9417 | 434.7697 | 694.7589
4656.9417 | 434.4611 | 695.2983
4657.9417 | 434.1725 | 694.966
4658.9417 | 433.9328 | 693.7826
4659.9417 | 433.6989 | 692.8023
4660.9417 | 433.4858 | 691.726
4661.9417 | 433.2291 | 690.7936
4662.9417 | 432.9293 | 690.2328
4663.9417 | 432.6915 | 690.0226
4664.9417 | 432.4154 | 689.7058
4665.9417 | 432.0775 | 689.6128
4666.9417 | 431.8688 | 689.3657
4667.9417 | 431.7064 | 688.7193
4668.9417 | 431.5143 | 687.514
4669.9417 | 431.2753 | 688.0589
4670.9417 | 431.0271 | 688.4988
4671.9417 | 430.6799 | 688.3822
4672.9417 | 430.3628 | 687.0585
4673.9417 | 430.0233 | 686.2954
4674.9417 | 429.6739 | 685.6614
4675.9417 | 429.3229 | 684.776
4676.9417 | 429.1074 | 683.8329
4677.9417 | 428.9004 | 682.8585
4678.9417 | 428.5108 | 681.9617
4679.9417 | 428.2204 | 681.3866
4680.9417 | 427.8953 | 680.4883
4681.9417 | 427.547 | 679.3108
4682.9417 | 427.2548 | 678.7059
4683.9417 | 426.966 | 677.889
4684.9417 | 426.6866 | 677.4122
4685.9417 | 426.4306 | 677.0423
4686.9417 | 426.1428 | 676.595
4687.9417 | 425.923 | 676.1874
4688.9417 | 425.5863 | 675.5483
4689.9417 | 425.2783 | 674.8298
4690.9417 | 425.0249 | 673.0968
4691.9417 | 424.7013 | 671.933
4692.9417 | 424.3533 | 671.2503
4693.9417 | 424.0403 | 671.1142
4694.9417 | 423.7803 | 670.6763
4695.9417 | 423.4725 | 669.3479
4696.9417 | 423.2171 | 668.521
4697.9417 | 422.9599 | 667.6115
4698.9417 | 422.7011 | 667.03
4699.9417 | 422.3086 | 666.5001
4700.9417 | 421.9776 | 665.2725
4701.9417 | 421.7172 | 664.5361
4702.9417 | 421.3506 | 664.0035
4703.9417 | 421.0377 | 663.1879
4704.9417 | 420.7412 | 662.604
4705.9417 | 420.3699 | 662.1069
4706.9417 | 420.0607 | 661.8149
4707.9417 | 419.7964 | 660.4805
4708.9417 | 419.4297 | 659.6846
4709.9417 | 419.044 | 658.9014
4710.9417 | 418.7374 | 658.305
4711.9417 | 418.377 | 657.652
4712.9417 | 418.0169 | 656.8363
4713.9417 | 417.5799 | 655.9003
4714.9417 | 417.1671 | 654.9035
4715.9417 | 416.8315 | 653.9369
4716.9417 | 416.4989 | 653.1271
4717.9417 | 416.1964 | 652.8916
4718.9417 | 415.8865 | 652.261
4719.9417 | 415.5827 | 652.4758
4720.9417 | 415.2277 | 652.4101
4721.9417 | 414.9045 | 652.6237
4722.9417 | 414.5779 | 652.68
4723.9417 | 414.2628 | 652.0124
4724.9417 | 413.995 | 650.6564
4725.9417 | 413.5726 | 650.011
4726.9417 | 413.1951 | 649.1111
4727.9417 | 412.9164 | 647.4171
4728.9417 | 412.5796 | 646.5176
4729.9417 | 412.2223 | 645.7249
4730.9417 | 411.8874 | 645.2668
4731.9417 | 411.5413 | 644.8429
4732.9417 | 411.2073 | 643.4768
4733.9417 | 410.8623 | 642.423
4734.9417 | 410.4876 | 640.7963
4735.9417 | 410.1687 | 639.651
4736.9417 | 409.6837 | 638.5924
4737.9417 | 409.2204 | 637.9054
4738.9417 | 408.8927 | 636.9202
4739.9417 | 408.4961 | 635.6049
4740.9417 | 408.1889 | 633.6864
4741.9417 | 407.9164 | 633.2098
4742.9417 | 407.6141 | 632.9456
4743.9417 | 407.2801 | 631.8329
4744.9417 | 406.9918 | 630.828
4745.9417 | 406.6028 | 630.6302
4746.9417 | 406.1695 | 628.9274
4747.9417 | 405.8483 | 627.9547
4748.9417 | 405.5559 | 626.9734
4749.9417 | 405.2609 | 625.9216
4750.9417 | 404.9059 | 625.2363
4751.9417 | 404.5958 | 623.4669
4752.9417 | 404.1973 | 622.4253
4753.9417 | 403.7595 | 621.0562
4754.9417 | 403.49 | 620.1126
4755.9417 | 403.1004 | 619.8372
4756.9417 | 402.6626 | 618.6985
4757.9417 | 402.3045 | 617.9431
4758.9417 | 401.9183 | 617.2566
4759.9417 | 401.611 | 616.5219
4760.9417 | 401.3582 | 615.4756
4761.9417 | 401.0811 | 614.7709
4762.9417 | 400.6896 | 614.2249
4763.9417 | 400.2329 | 614.3082
4764.9417 | 399.9267 | 612.6304
4765.9417 | 399.6665 | 612.4029
4766.9417 | 399.3379 | 612.2849
4767.9417 | 398.9851 | 612.0246
4768.9417 | 398.5174 | 611.6191
4769.9417 | 398.0559 | 610.7672
4770.9417 | 397.7065 | 610.308
4771.9417 | 397.3494 | 609.834
4772.9417 | 397.015 | 609.097
4773.9417 | 396.6049 | 608.0884
4774.9417 | 396.2841 | 606.7075
4775.9417 | 395.9418 | 605.2593
4776.9417 | 395.6358 | 604.1208
4777.9417 | 395.3101 | 603.5987
4778.9417 | 394.9289 | 602.8836
4779.9417 | 394.5621 | 602.3732
4780.9417 | 394.1838 | 602.2066
4781.9417 | 393.8163 | 601.2087
4782.9417 | 393.3284 | 599.9368
4783.9417 | 393.0222 | 599.4298
4784.9417 | 392.5748 | 598.4267
4785.9417 | 392.1103 | 597.4755
4786.9417 | 391.7528 | 597.055
4787.9417 | 391.4509 | 596.0187
4788.9417 | 391.0703 | 594.7746
4789.9417 | 390.7766 | 593.5799
4790.9417 | 390.3584 | 592.6198
4791.9417 | 389.9811 | 591.4625
4792.9417 | 389.6227 | 590.2043
4793.9417 | 389.1837 | 588.8056
4794.9417 | 388.7791 | 587.8992
4795.9417 | 388.4158 | 585.6295
4796.9417 | 388.1328 | 583.8648
4797.9417 | 387.8122 | 582.8786
4798.9417 | 387.3612 | 581.7945
4799.9417 | 387.0195 | 579.5327
4800.9417 | 386.7176 | 576.6935
4801.9417 | 386.3929 | 574.2546
4802.9417 | 386.0072 | 572.0036
4803.9417 | 385.5755 | 569.132
4804.9417 | 385.2588 | 566.2826
4805.9417 | 384.9765 | 564.0955
4806.9417 | 384.5827 | 561.4277
4807.9417 | 384.1904 | 557.06
4808.9417 | 383.7644 | 556.2228
4809.9417 | 383.3903 | 551.4216
4810.9417 | 382.9442 | 548.5307
4811.9417 | 382.6457 | 545.761
4812.9417 | 382.2341 | 542.8312
4813.9417 | 381.9074 | 532.1246
4814.9417 | 381.5621 | 536.4637
4815.9417 | 381.0656 | 529.6632
4816.9417 | 380.5997 | 526.644
4817.9417 | 380.1773 | 519.0117
4818.9417 | 379.7718 | 516.8075
4819.9417 | 379.3116 | 496.0927
4820.9417 | 378.963 | 488.3785
4821.9417 | 378.5463 | 495.9401
4822.9417 | 378.1985 | 466.6713
4823.9417 | 377.9006 | 485.6297
4824.9417 | 377.6242 | 525.8658
4825.9417 | 377.3211 | 528.953
4826.9417 | 376.9207 | 527.7792
4827.9417 | 376.4433 | 525.8376
4828.9417 | 376.0294 | 525.4665
4829.9417 | 375.5748 | 524.8107
4830.9417 | 375.2059 | 524.449
4831.9417 | 374.8428 | 523.2686
4832.9417 | 374.4379 | 522.9553
4833.9417 | 374.0682 | 522.3799
4834.9417 | 373.7266 | 522.406
4835.9417 | 373.4175 | 522.2447
4836.9417 | 373.0767 | 522.6363
4837.9417 | 372.6347 | 522.8333
4838.9417 | 372.286 | 520.6936
4839.9417 | 371.9424 | 520.2036
4840.9417 | 371.5749 | 523.0538
4841.9417 | 371.1687 | 521.7182
4842.9417 | 370.775 | 521.2947
4843.9417 | 370.4045 | 520.3091
4844.9417 | 370.1618 | 518.9864
4845.9417 | 369.8724 | 518.2298
4846.9417 | 369.5375 | 518.1129
4847.9417 | 369.159 | 518.3323
4848.9417 | 368.7416 | 517.9983
4849.9417 | 368.4531 | 517.8884
4850.9417 | 368.1252 | 517.2748
4851.9417 | 367.73 | 516.4825
4852.9417 | 367.3083 | 516.1732
4853.9417 | 366.9008 | 516.2083
4854.9417 | 366.466 | 516.2734
4855.9417 | 365.998 | 516.3176
4856.9417 | 365.5449 | 515.3041
4857.9417 | 365.2996 | 514.8911
4858.9417 | 365.0055 | 513.5466
4859.9417 | 364.7167 | 513.0862
4860.9417 | 364.4059 | 513.2363
4861.9417 | 363.9651 | 512.6938
4862.9417 | 363.5673 | 512.3046
4863.9417 | 363.2046 | 511.8497
4864.9417 | 362.9108 | 511.0176
4865.9417 | 362.4877 | 510.6458
4866.9417 | 362.1078 | 509.6905
4867.9417 | 361.7423 | 509.6531
4868.9417 | 361.3291 | 508.4746
4869.9417 | 360.8879 | 508.2988
4870.9417 | 360.5006 | 508.2068
4871.9417 | 360.178 | 507.8196
4872.9417 | 359.8363 | 507.2067
4873.9417 | 359.4901 | 506.6253
4874.9417 | 359.1832 | 506.3411
4875.9417 | 358.8534 | 506.028
4876.9417 | 358.5532 | 506.3052
4877.9417 | 358.2401 | 506.2584
4878.9417 | 357.8728 | 505.0012
4879.9417 | 357.4463 | 505.2913
4880.9417 | 357.1004 | 503.6208
4881.9417 | 356.7349 | 502.8104
4882.9417 | 356.3941 | 502.4299
4883.9417 | 356.0488 | 501.5614
4884.9417 | 355.721 | 500.5972
4885.9417 | 355.3529 | 500.5814
4886.9417 | 355.0065 | 500.9513
4887.9417 | 354.6046 | 501.5713
4888.9417 | 354.1844 | 500.959
4889.9417 | 353.9577 | 499.9573
4890.9417 | 353.6398 | 499.2676
4891.9417 | 353.2301 | 499.9298
4892.9417 | 352.8386 | 499.1057
4893.9417 | 352.4979 | 499.2676
4894.9417 | 352.1425 | 498.6563
4895.9417 | 351.7567 | 497.8294
4896.9417 | 351.3817 | 497.5188
4897.9417 | 351.0805 | 497.3543
4898.9417 | 350.681 | 497.927
4899.9417 | 350.358 | 497.0767
4900.9417 | 349.9277 | 496.2787
4901.9417 | 349.5343 | 495.3879
4902.9417 | 349.2067 | 495.7458
4903.9417 | 348.8194 | 495.6137
4904.9417 | 348.411 | 495.79
4905.9417 | 348.0709 | 494.9136
4906.9417 | 347.6979 | 494.5802
4907.9417 | 347.3587 | 493.7364
4908.9417 | 347.0016 | 493.6641
4909.9417 | 346.6682 | 492.8095
4910.9417 | 346.3093 | 492.5948
4911.9417 | 345.9527 | 492.2645
4912.9417 | 345.5624 | 492.0017
4913.9417 | 345.1572 | 491.7808
4914.9417 | 344.6947 | 492.6082
4915.9417 | 344.3703 | 492.4878
4916.9417 | 344.0113 | 492.2361
4917.9417 | 343.555 | 491.5861
4918.9417 | 343.2145 | 491.2873
4919.9417 | 342.9457 | 490.7762
4920.9417 | 342.6806 | 490.6084
4921.9417 | 342.3607 | 490.6618
4922.9417 | 342.0758 | 489.4794
4923.9417 | 341.6776 | 489.536
4924.9417 | 341.2923 | 488.9864
4925.9417 | 340.973 | 488.9277
4926.9417 | 340.6219 | 488.9768
4927.9417 | 340.2996 | 488.152
4928.9417 | 339.909 | 488.1261
4929.9417 | 339.5583 | 487.6135
4930.9417 | 339.2841 | 487.4648
4931.9417 | 338.9528 | 487.1129
4932.9417 | 338.6716 | 486.3789
4933.9417 | 338.3589 | 484.6278
4934.9417 | 338.0596 | 484.211
4935.9417 | 337.761 | 484.5945
4936.9417 | 337.4457 | 485.0418
4937.9417 | 337.1335 | 485.0112
4938.9417 | 336.7535 | 485.6441
4939.9417 | 336.4234 | 485.7264
4940.9417 | 336.0241 | 485.3832
4941.9417 | 335.6293 | 484.035
4942.9417 | 335.2581 | 484.1533
4943.9417 | 334.9775 | 484.4073
4944.9417 | 334.6622 | 483.0736
4945.9417 | 334.3323 | 482.6589
4946.9417 | 334.034 | 483.1258
4947.9417 | 333.7645 | 482.4485
4948.9417 | 333.406 | 480.6342
4949.9417 | 332.9115 | 480.1424
4950.9417 | 332.4568 | 480.5395
4951.9417 | 332.1846 | 479.4272
4952.9417 | 331.8935 | 478.4063
4953.9417 | 331.4603 | 478.4696
4954.9417 | 331.0913 | 478.3356
4955.9417 | 330.7244 | 478.2742
4956.9417 | 330.4245 | 478.0184
4957.9417 | 330.1462 | 478.5705
4958.9417 | 329.9022 | 478.6735
4959.9417 | 329.6011 | 478.0748
4960.9417 | 329.2891 | 478.2816
4961.9417 | 328.9616 | 478.3392
4962.9417 | 328.5929 | 477.442
4963.9417 | 328.3153 | 476.9558
4964.9417 | 327.9854 | 476.474
4965.9417 | 327.6639 | 476.3544
4966.9417 | 327.3421 | 475.7779
4967.9417 | 327.058 | 475.0243
4968.9417 | 326.7383 | 473.7568
4969.9417 | 326.3979 | 473.3906
4970.9417 | 326.0758 | 472.8313
4971.9417 | 325.6388 | 473.3961
4972.9417 | 325.3335 | 472.7354
4973.9417 | 325.0061 | 471.796
4974.9417 | 324.6185 | 470.8075
4975.9417 | 324.291 | 470.0197
4976.9417 | 324.0375 | 468.7629
4977.9417 | 323.7158 | 468.7539
4978.9417 | 323.3067 | 468.5231
4979.9417 | 323.0339 | 468.7729
4980.9417 | 322.7298 | 468.6507
4981.9417 | 322.2868 | 467.7077
4982.9417 | 321.9261 | 467.8761
4983.9417 | 321.6254 | 467.3845
4984.9417 | 321.2873 | 466.8055
4985.9417 | 320.9643 | 465.7285
4986.9417 | 320.7254 | 465.7732
4987.9417 | 320.4455 | 464.9828
4988.9417 | 320.139 | 464.203
4989.9417 | 319.8141 | 463.5734
4990.9417 | 319.5253 | 462.9505
4991.9417 | 319.2125 | 462.4393
4992.9417 | 318.9226 | 462.095
4993.9417 | 318.6314 | 462.2283
4994.9417 | 318.3131 | 461.2886
4995.9417 | 317.9876 | 461.5839
4996.9417 | 317.6841 | 461.4777
4997.9417 | 317.38 | 461.3899
4998.9417 | 317.1157 | 461.4906
4999.9417 | 316.8378 | 461.1121
5000.9417 | 316.5542 | 460.7927
5001.9417 | 316.2808 | 460.5939
5002.9417 | 315.925 | 460.1235
5003.9417 | 315.6032 | 459.4038
5004.9417 | 315.2413 | 459.1668
5005.9417 | 314.9563 | 458.8045
5006.9417 | 314.6824 | 458.7354
5007.9417 | 314.3726 | 458.7251
5008.9417 | 314.1156 | 458.1568
5009.9417 | 313.8161 | 458.0796
5010.9417 | 313.4794 | 457.6906
5011.9417 | 313.1429 | 457.5042
5012.9417 | 312.8052 | 456.7497
5013.9417 | 312.4912 | 456.3463
5014.9417 | 312.2123 | 456.0156
5015.9417 | 311.8831 | 455.049
5016.9417 | 311.5246 | 454.9421
5017.9417 | 311.2856 | 455.6143
5018.9417 | 310.9803 | 455.0919
5019.9417 | 310.702 | 454.2646
5020.9417 | 310.343 | 454.494
5021.9417 | 310.0123 | 454.0738
5022.9417 | 309.8302 | 453.8592
5023.9417 | 309.5463 | 453.7984
5024.9417 | 309.2678 | 453.566
5025.9417 | 308.9878 | 453.6512
5026.9417 | 308.6967 | 453.6764
5027.9417 | 308.4253 | 452.6109
5028.9417 | 308.0884 | 452.5919
5029.9417 | 307.7479 | 452.2245
5030.9417 | 307.4153 | 451.7377
5031.9417 | 307.1312 | 450.5974
5032.9417 | 306.852 | 450.5029
5033.9417 | 306.5976 | 450.5674
5034.9417 | 306.3139 | 450.6113
5035.9417 | 306.0402 | 450.3782
5036.9417 | 305.7669 | 450.0282
5037.9417 | 305.5071 | 449.8483
5038.9417 | 305.2758 | 449.3429
5039.9417 | 305.0243 | 448.8356
5040.9417 | 304.7815 | 448.274
5041.9417 | 304.4688 | 448.1681
5042.9417 | 304.2171 | 447.3992
5043.9417 | 303.9418 | 447.0803
5044.9417 | 303.6767 | 447.1897
5045.9417 | 303.3924 | 446.2524
5046.9417 | 303.0649 | 445.9329
5047.9417 | 302.7948 | 445.282
5048.9417 | 302.4359 | 445.2701
5049.9417 | 302.1204 | 444.7899
5050.9417 | 301.7647 | 444.411
5051.9417 | 301.4517 | 444.1207
5052.9417 | 301.23 | 443.0936
5053.9417 | 301.0411 | 442.5552
5054.9417 | 300.7641 | 442.4692
5055.9417 | 300.4635 | 441.9171
5056.9417 | 300.1899 | 441.394
5057.9417 | 299.8875 | 441.3678
5058.9417 | 299.6819 | 440.6797
5059.9417 | 299.4616 | 440.869
5060.9417 | 299.1739 | 441.0366
5061.9417 | 298.8736 | 440.7508
5062.9417 | 298.6399 | 439.9132
5063.9417 | 298.3941 | 439.2946
5064.9417 | 298.1014 | 439.1394
5065.9417 | 297.8093 | 439.1656
5066.9417 | 297.4648 | 439.5271
5067.9417 | 297.2351 | 438.9337
5068.9417 | 296.9785 | 438.4721
5069.9417 | 296.7335 | 438.738
5070.9417 | 296.5066 | 438.3401
5071.9417 | 296.1561 | 438.0378
5072.9417 | 295.7953 | 437.456
5073.9417 | 295.5139 | 437.1027
5074.9417 | 295.1585 | 436.9809
5075.9417 | 294.8113 | 437.2072
5076.9417 | 294.6022 | 437.1911
5077.9417 | 294.4027 | 437.5091
5078.9417 | 294.1515 | 436.4349
5079.9417 | 293.8068 | 435.4445
5080.9417 | 293.5554 | 435.1304
5081.9417 | 293.3431 | 435.0833
5082.9417 | 293.0369 | 433.7728
5083.9417 | 292.7019 | 432.7933
5084.9417 | 292.4018 | 432.8069
5085.9417 | 292.1269 | 432.0436
5086.9417 | 291.8677 | 432.3954
5087.9417 | 291.5744 | 432.7399
5088.9417 | 291.3712 | 432.4569
5089.9417 | 291.1103 | 430.5174
5090.9417 | 290.8543 | 429.9438
5091.9417 | 290.5714 | 429.3006
5092.9417 | 290.3364 | 429.1291
5093.9417 | 290.0778 | 429.2521
5094.9417 | 289.7984 | 429.5327
5095.9417 | 289.5484 | 428.5448
5096.9417 | 289.2921 | 429.1413
5097.9417 | 288.9587 | 428.9258
5098.9417 | 288.6335 | 429.5018
5099.9417 | 288.3808 | 429.2246
5100.9417 | 288.1078 | 429.9676
5101.9417 | 287.8721 | 429.9762
5102.9417 | 287.617 | 431.1331
5103.9417 | 287.3375 | 431.1442
5104.9417 | 287.0724 | 429.8375
5105.9417 | 286.793 | 428.8165
5106.9417 | 286.5633 | 428.5265
5107.9417 | 286.3184 | 428.1028
5108.9417 | 286.0297 | 427.7537
5109.9417 | 285.8125 | 428.0126
5110.9417 | 285.6118 | 427.1897
5111.9417 | 285.3497 | 426.0391
5112.9417 | 285.0392 | 425.9197
5113.9417 | 284.7548 | 424.3989
5114.9417 | 284.5195 | 423.7811
5115.9417 | 284.2809 | 423.5206
5116.9417 | 284.0324 | 423.478
5117.9417 | 283.7481 | 422.3727
5118.9417 | 283.4546 | 422.9898
5119.9417 | 283.1238 | 422.2856
5120.9417 | 282.8294 | 422.0741
5121.9417 | 282.6138 | 421.3759
5122.9417 | 282.3744 | 420.7568
5123.9417 | 282.1255 | 420.7995
5124.9417 | 281.93 | 420.6913
5125.9417 | 281.705 | 420.0261
5126.9417 | 281.5233 | 420.3198
5127.9417 | 281.2777 | 420.0409
5128.9417 | 280.9807 | 421.0032
5129.9417 | 280.7956 | 421.8672
5130.9417 | 280.6021 | 422.5861
5131.9417 | 280.3586 | 422.5443
5132.9417 | 280.1628 | 421.2045
5133.9417 | 279.8977 | 420.2274
5134.9417 | 279.6202 | 419.0565
5135.9417 | 279.354 | 418.3812
5136.9417 | 279.0552 | 417.8119
5137.9417 | 278.7735 | 417.4377
5138.9417 | 278.5442 | 417.5538
5139.9417 | 278.1892 | 417.681
5140.9417 | 277.8426 | 416.8351
5141.9417 | 277.6283 | 416.5006
5142.9417 | 277.3792 | 416.1337
5143.9417 | 277.1298 | 415.7347
5144.9417 | 276.9026 | 415.9623
5145.9417 | 276.7387 | 415.6631
5146.9417 | 276.5213 | 415.413
5147.9417 | 276.2426 | 415.8611
5148.9417 | 276.0199 | 415.8951
5149.9417 | 275.694 | 415.8623
5150.9417 | 275.4401 | 415.9299
5151.9417 | 275.2547 | 415.9056
5152.9417 | 274.9742 | 415.0673
5153.9417 | 274.6679 | 414.4574
5154.9417 | 274.4433 | 413.7039
5155.9417 | 274.2336 | 413.9344
5156.9417 | 273.9744 | 413.1814
5157.9417 | 273.7705 | 412.4147
5158.9417 | 273.5033 | 411.4382