## Test Conditions
DESIREE-FIRE Test Number 10 - Circuit Simulator Data Only
Test Date: | 2009-07-21
DCSim DAQ Start Time | 14:53
DCSim Time for Synchronization | 14:54
Heat Source Synchronization | 0:02 | minutes:seconds
Heat Source DAQ Start Time | 14:52
Heat Source Start Time | 14:56
DCSim Offset | 0:03 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 170 | seconds
Heat Source Offset | 0:04 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 264 | seconds
Heat Source Stop Time | 15:37
Test Duration | 0:41 | minutes:seconds
| 2465 | seconds
CT500 Turns | 1 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 1
Pre-Test Baseline: | Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.078125 | 123.4406 | -61.1389 | 62.1872 | 0.14964 | -9.5248e-05 | 0.0045366 | 0.0098242 | 0.083097 | 0.010174 | 0.072791 | -61.322 | 62.3703 | -61.3495 | -61.2534 | 62.1323 | 0.11902 | -0.11902 | 0.21515 | 62.2101 | -61.3541 | -0.21057 | 0.1831 | -0.1831 | -0.11444 | -0.054932 | -0.21515 | 0.022888 | 0.027466 | 61.0199 | 61.3541 | 123.2712 | 123.5092 | -0.1831 | 123.349 | 61.2579 | -0.21515 | 123.5092 | -0.1831 | 61.2579 | 123.2712 | 123.349 | -123.5367 | -123.5413
0.96875 | 123.4406 | -61.1343 | 62.1918 | -0.30813 | -0.0075722 | -0.0029404 | -0.0019248 | 0.076688 | -0.0058484 | 0.072791 | -61.1664 | 62.3383 | -61.3449 | -61.2717 | 62.1231 | 0.13733 | -0.10071 | 0.23804 | 62.2604 | -61.3358 | -0.21057 | 0.14648 | -0.032044 | -0.13733 | -0.068664 | -0.20142 | 0.068665 | 0.17853 | 61.0336 | 61.3724 | 123.2574 | 123.4726 | -0.032044 | 123.3948 | 61.2717 | -0.20142 | 123.4726 | -0.032044 | 61.2717 | 123.2574 | 123.3948 | -123.5367 | -123.5275
1.9219 | 123.4451 | -61.1343 | 62.1735 | 0.39378 | 0.012723 | 0.0077416 | -0.0051288 | 0.063871 | 0.011242 | 0.073859 | -61.3129 | 62.3428 | -61.3495 | -61.2946 | 62.0956 | 0.086975 | -0.10071 | 0.19684 | 62.233 | -61.377 | -0.21515 | 0.16937 | -0.17853 | -0.16022 | -0.07782 | -0.24262 | 0.059509 | 0.036621 | 61.0336 | 61.3312 | 123.23 | 123.4772 | -0.17853 | 123.3673 | 61.2213 | -0.24262 | 123.4772 | -0.17853 | 61.2213 | 123.23 | 123.3673 | -123.5229 | -123.5504
2.9844 | 123.436 | -61.1755 | 62.1506 | 0.39378 | 0.0073818 | 0.0098776 | 0.010892 | 0.070279 | 0.013378 | 0.067451 | -61.3129 | 62.3611 | -61.3815 | -61.2625 | 62.1048 | 0.10529 | -0.10529 | 0.2243 | 62.2375 | -61.3586 | -0.20599 | 0.21057 | -0.13733 | -0.086975 | -0.045777 | -0.18311 | 0.086975 | 0.068665 | 61.0703 | 61.3998 | 123.2803 | 123.5367 | -0.13733 | 123.4131 | 61.2808 | -0.18311 | 123.5367 | -0.13733 | 61.2808 | 123.2803 | 123.4131 | -123.5321 | -123.5092
3.9219 | 123.4863 | -61.1526 | 62.1826 | 0.348 | 0.0052458 | 0.0056046 | -0.01047 | 0.069211 | -0.0015754 | 0.063178 | -61.3083 | 62.3474 | -61.3724 | -61.3403 | 62.1094 | 0.054932 | -0.054932 | 0.16937 | 62.2238 | -61.3724 | -0.21973 | 0.16479 | -0.15564 | -0.18768 | -0.073242 | -0.21973 | 0.041199 | 0.064086 | 61.0977 | 61.322 | 123.262 | 123.5001 | -0.15564 | 123.3765 | 61.2076 | -0.21973 | 123.5001 | -0.15564 | 61.2076 | 123.262 | 123.3765 | -123.555 | -123.555
4.9844 | 123.5092 | -61.116 | 62.1918 | -0.094502 | 0.010586 | 0.00026463 | 0.00021117 | 0.067075 | 0.019787 | 0.074928 | -61.235 | 62.3566 | -61.3449 | -61.3083 | 62.0819 | 0.091553 | -0.050354 | 0.16937 | 62.2467 | -61.3541 | -0.22888 | 0.16479 | -0.11902 | -0.19226 | -0.10986 | -0.23804 | 0.054932 | 0.10986 | 61.0657 | 61.2854 | 123.1979 | 123.4726 | -0.11902 | 123.3627 | 61.2076 | -0.23804 | 123.4726 | -0.11902 | 61.2076 | 123.1979 | 123.3627 | -123.5367 | -123.5458
5.9219 | 123.468 | -61.1389 | 62.1506 | 0.4243 | 0.011654 | -0.0050764 | -0.00085683 | 0.072416 | 0.011242 | 0.070655 | -61.2991 | 62.3245 | -61.377 | -61.3632 | 62.0499 | 0.068665 | 0.032043 | 0.10071 | 62.233 | -61.3815 | -0.23804 | 0.17395 | -0.16022 | -0.2243 | -0.10071 | -0.24262 | 0.082397 | 0.07782 | 61.171 | 61.2396 | 123.1888 | 123.4634 | -0.16022 | 123.3719 | 61.2076 | -0.24262 | 123.4634 | -0.16022 | 61.2076 | 123.1888 | 123.3719 | -123.5275 | -123.5321
6.9844 | 123.5092 | -61.1298 | 62.1964 | -0.27761 | 0.0084498 | 0.0045366 | 0.013029 | 0.074552 | -0.0069164 | 0.065314 | -61.2625 | 62.3566 | -61.3495 | -61.2579 | 62.0956 | 0.09613 | -0.036621 | 0.17853 | 62.265 | -61.3312 | -0.21973 | 0.16022 | -0.13275 | -0.12817 | -0.10071 | -0.20142 | 0.068665 | 0.086975 | 61.0931 | 61.3083 | 123.2254 | 123.4863 | -0.13275 | 123.3948 | 61.2259 | -0.20142 | 123.4863 | -0.13275 | 61.2259 | 123.2254 | 123.3948 | -123.5458 | -123.5275
7.9219 | 123.4543 | -61.1481 | 62.1735 | 0.45481 | 0.0052458 | 0.0098776 | 0.0012792 | 0.073484 | -0.00050737 | 0.073859 | -61.3083 | 62.3337 | -61.3678 | -61.3083 | 62.1094 | 0.073242 | -0.082397 | 0.1831 | 62.2284 | -61.3632 | -0.21973 | 0.16022 | -0.16022 | -0.16022 | -0.064087 | -0.21515 | 0.054932 | 0.059509 | 61.0657 | 61.3312 | 123.2574 | 123.4818 | -0.16022 | 123.3765 | 61.2213 | -0.21515 | 123.4818 | -0.16022 | 61.2213 | 123.2574 | 123.3765 | -123.5413 | -123.5367
8.9844 | 123.4818 | -61.116 | 62.2192 | -0.3539 | -9.5248e-05 | 0.0024006 | -0.00085683 | 0.077756 | 0.0080376 | 0.067451 | -61.2534 | 62.3611 | -61.3266 | -61.2991 | 62.0773 | 0.073242 | -0.068665 | 0.1831 | 62.265 | -61.3358 | -0.21057 | 0.14191 | -0.13733 | -0.1831 | -0.14191 | -0.21973 | 0.045777 | 0.073242 | 61.0474 | 61.2991 | 123.1934 | 123.4772 | -0.13733 | 123.381 | 61.1893 | -0.21973 | 123.4772 | -0.13733 | 61.1893 | 123.1934 | 123.381 | -123.5458 | -123.555
9.9219 | 123.5641 | -61.0886 | 62.1643 | 0.45481 | 0.00097275 | -0.0072124 | -0.020083 | 0.059598 | 0.0080376 | 0.066383 | -61.235 | 62.2513 | -61.3312 | -61.4548 | 61.9812 | -0.054932 | 0.068665 | 0.045776 | 62.265 | -61.4182 | -0.24261 | 0.086975 | -0.14648 | -0.36621 | -0.18311 | -0.32959 | 0.10071 | 0.096131 | 61.1572 | 61.1343 | 123.0698 | 123.3398 | -0.14648 | 123.3536 | 61.0336 | -0.32959 | 123.3398 | -0.14648 | 61.0336 | 123.0698 | 123.3536 | -123.4955 | -123.5825
10.9844 | 123.4909 | -61.1572 | 62.1918 | -0.079243 | 0.0095178 | 0.021627 | -0.0061968 | 0.066007 | 0.0016286 | 0.063178 | -61.2305 | 62.3657 | -61.3358 | -61.2991 | 62.0636 | 0.064087 | -0.059509 | 0.16022 | 62.2559 | -61.3678 | -0.17853 | 0.17395 | -0.073242 | -0.14191 | -0.12817 | -0.21057 | 0.064087 | 0.10529 | 61.0977 | 61.3174 | 123.2208 | 123.523 | -0.073242 | 123.4131 | 61.2213 | -0.21057 | 123.523 | -0.073242 | 61.2213 | 123.2208 | 123.4131 | -123.5275 | -123.5596
11.9219 | 123.5413 | -61.0977 | 62.1323 | 0.40904 | -0.015048 | 0.0024006 | -0.0072648 | 0.05853 | 0.0091056 | 0.069587 | -61.2488 | 62.2375 | -61.3815 | -61.4639 | 61.9766 | -0.059509 | 0.050354 | 0.068665 | 62.2696 | -61.3861 | -0.28381 | 0.10529 | -0.15106 | -0.36621 | -0.15564 | -0.28839 | 0.13733 | 0.13275 | 61.1481 | 61.1664 | 123.0743 | 123.3353 | -0.15106 | 123.3673 | 61.0382 | -0.28839 | 123.3353 | -0.15106 | 61.0382 | 123.0743 | 123.3673 | -123.5138 | -123.5184
12.9844 | 123.5596 | -61.0794 | 62.1414 | 0.39378 | -0.0097082 | -0.0018714 | -0.013674 | 0.072416 | 0.010174 | 0.087745 | -61.2167 | 62.2696 | -61.3174 | -61.4502 | 61.972 | -0.07782 | 0.050354 | 0.059509 | 62.2604 | -61.4319 | -0.23804 | 0.12817 | -0.13733 | -0.37079 | -0.16937 | -0.35248 | 0.11902 | 0.10071 | 61.1298 | 61.1389 | 123.0515 | 123.349 | -0.13733 | 123.3398 | 61.0016 | -0.35248 | 123.349 | -0.13733 | 61.0016 | 123.0515 | 123.3398 | -123.4589 | -123.5733
13.9219 | 123.6008 | -61.1114 | 62.1368 | 0.48533 | -0.0086402 | 0.0077416 | -0.01581 | 0.055326 | 0.0069696 | 0.068519 | -61.2396 | 62.2513 | -61.3266 | -61.4456 | 61.9537 | -0.059509 | 0.054932 | 0.064087 | 62.2421 | -61.3998 | -0.21515 | 0.11444 | -0.12817 | -0.33417 | -0.18311 | -0.28839 | 0.10529 | 0.086975 | 61.1664 | 61.1755 | 123.0652 | 123.3627 | -0.12817 | 123.3536 | 61.0519 | -0.28839 | 123.3627 | -0.12817 | 61.0519 | 123.0652 | 123.3536 | -123.4634 | -123.5367
14.9844 | 123.4314 | -61.1801 | 62.2101 | 0.348 | 0.0031088 | 0.0034686 | 0.0012792 | 0.060666 | 0.013378 | 0.066383 | -61.3083 | 62.3566 | -61.3861 | -61.29 | 62.1048 | 0.064087 | -0.091553 | 0.1831 | 62.2147 | -61.3724 | -0.20599 | 0.14648 | -0.12817 | -0.10986 | -0.10529 | -0.19226 | 0.004578 | 0.077819 | 61.0886 | 61.3632 | 123.2849 | 123.5367 | -0.12817 | 123.3948 | 61.2442 | -0.19226 | 123.5367 | -0.12817 | 61.2442 | 123.2849 | 123.3948 | -123.5962 | -123.5825
15.9219 | 123.5138 | -61.0977 | 62.1826 | 0.30223 | -0.0054352 | 0.0013326 | -0.0072648 | 0.056394 | -0.017597 | 0.067451 | -61.2946 | 62.2604 | -61.3358 | -61.377 | 62.0087 | 0.022888 | -0.013733 | 0.11444 | 62.265 | -61.3586 | -0.23804 | 0.07782 | -0.19684 | -0.27924 | -0.17395 | -0.26093 | 0.082398 | 0.041198 | 61.084 | 61.2122 | 123.1064 | 123.3582 | -0.19684 | 123.3627 | 61.1206 | -0.26093 | 123.3582 | -0.19684 | 61.1206 | 123.1064 | 123.3627 | -123.5184 | -123.5413
16.9844 | 123.4222 | -61.1389 | 62.1918 | 0.33274 | -0.0011632 | 0.019491 | -0.0029928 | 0.071348 | 0.014446 | 0.064246 | -61.2808 | 62.3474 | -61.3403 | -61.2488 | 62.1094 | 0.082397 | -0.11902 | 0.22888 | 62.2375 | -61.3541 | -0.20142 | 0.15564 | -0.14191 | -0.10986 | -0.082397 | -0.21515 | 0.045777 | 0.059509 | 61.0199 | 61.3678 | 123.2483 | 123.4863 | -0.14191 | 123.3765 | 61.2213 | -0.21515 | 123.4863 | -0.14191 | 61.2213 | 123.2483 | 123.3765 | -123.5321 | -123.5458
17.9219 | 123.5596 | -61.1023 | 62.1872 | 0.042827 | 0.0020408 | 0.0077416 | -0.011538 | 0.066007 | -0.015461 | 0.078132 | -61.2579 | 62.2513 | -61.3586 | -61.441 | 61.9858 | -0.013733 | 0.009155 | 0.086975 | 62.2742 | -61.3907 | -0.25635 | 0.064087 | -0.15564 | -0.33875 | -0.20142 | -0.28839 | 0.086975 | 0.10071 | 61.1114 | 61.1893 | 123.0881 | 123.3536 | -0.15564 | 123.3765 | 61.0886 | -0.28839 | 123.3536 | -0.15564 | 61.0886 | 123.0881 | 123.3765 | -123.5458 | -123.5779
18.9844 | 123.5184 | -61.1343 | 62.178 | 0.45481 | 0.0031088 | 0.013082 | 0.010892 | 0.057462 | 0.0048326 | 0.063178 | -61.2854 | 62.3062 | -61.377 | -61.2213 | 62.0361 | -0.032043 | -0.064087 | 0.14648 | 62.2284 | -61.377 | -0.24262 | 0.12817 | -0.15106 | -0.086975 | -0.14191 | -0.24262 | 0.050354 | 0.091553 | 61.0703 | 61.2808 | 123.1705 | 123.4406 | -0.15106 | 123.3627 | 61.1023 | -0.24262 | 123.4406 | -0.15106 | 61.1023 | 123.1705 | 123.3627 | -123.555 | -123.555
19.9219 | 123.5229 | -61.1114 | 62.1552 | 0.058086 | -0.0065042 | -0.024302 | -0.017947 | 0.056394 | -0.013325 | 0.070655 | -61.29 | 62.2467 | -61.3495 | -61.3861 | 62.0224 | -0.013733 | 0.018311 | 0.10986 | 62.2787 | -61.3678 | -0.23804 | 0.091553 | -0.17853 | -0.27466 | -0.13275 | -0.25635 | 0.1236 | 0.059509 | 61.1298 | 61.2213 | 123.1338 | 123.3582 | -0.17853 | 123.3902 | 61.0977 | -0.25635 | 123.3582 | -0.17853 | 61.0977 | 123.1338 | 123.3902 | -123.5046 | -123.5229
20.9844 | 123.5504 | -61.116 | 62.178 | 0.77525 | 0.0041778 | -0.010416 | 0.0012792 | 0.061735 | 0.0016286 | 0.071723 | -61.29 | 62.2879 | -61.3449 | -61.3449 | 62.0132 | -0.032043 | 0.004578 | 0.091553 | 62.2055 | -61.3586 | -0.22888 | 0.10986 | -0.17395 | -0.22888 | -0.1648 | -0.24262 | 0.027465 | 0.054932 | 61.1206 | 61.2076 | 123.1293 | 123.4039 | -0.17395 | 123.3215 | 61.084 | -0.24262 | 123.4039 | -0.17395 | 61.084 | 123.1293 | 123.3215 | -123.523 | -123.5367
21.9219 | 123.5229 | -61.1069 | 62.1689 | 0.19541 | -0.010776 | -0.016825 | -0.023287 | 0.064939 | -0.0047804 | 0.065314 | -61.3037 | 62.2375 | -61.3449 | -61.377 | 62.0224 | -0.009155 | -0.009155 | 0.13275 | 62.2696 | -61.3632 | -0.23804 | 0.068665 | -0.19684 | -0.27008 | -0.14648 | -0.25635 | 0.10071 | 0.041199 | 61.0977 | 61.2396 | 123.1293 | 123.3444 | -0.19684 | 123.3765 | 61.0977 | -0.25635 | 123.3444 | -0.19684 | 61.0977 | 123.1293 | 123.3765 | -123.5138 | -123.5321
22.9844 | 123.5413 | -61.0886 | 62.1414 | 0.36326 | -0.0097082 | 0.00026463 | -0.0061968 | 0.064939 | -0.0047804 | 0.063178 | -61.2396 | 62.2833 | -61.3495 | -61.4044 | 61.9904 | -0.059509 | 0.022888 | 0.068665 | 62.2787 | -61.409 | -0.26093 | 0.14191 | -0.15106 | -0.31586 | -0.15106 | -0.32043 | 0.13733 | 0.10986 | 61.1115 | 61.1572 | 123.0789 | 123.3719 | -0.15106 | 123.3673 | 61.0291 | -0.32043 | 123.3719 | -0.15106 | 61.0291 | 123.0789 | 123.3673 | -123.4909 | -123.5504
23.9219 | 123.5641 | -61.0794 | 62.178 | -0.018208 | -0.012912 | 0.0024006 | -0.014742 | 0.067075 | -0.014393 | 0.071723 | -61.2854 | 62.2559 | -61.3403 | -61.409 | 61.9858 | -0.022888 | 0.032043 | 0.10986 | 62.2696 | -61.3632 | -0.26092 | 0.077819 | -0.20599 | -0.32959 | -0.19226 | -0.28381 | 0.091552 | 0.054932 | 61.1115 | 61.1893 | 123.0652 | 123.3353 | -0.20599 | 123.349 | 61.0565 | -0.28381 | 123.3353 | -0.20599 | 61.0565 | 123.0652 | 123.349 | -123.5184 | -123.5413
24.9688 | 123.4451 | -61.1389 | 62.2009 | 0.14964 | 0.0041778 | 0.0056046 | 0.018369 | 0.067075 | 0.0091056 | 0.065314 | -61.2946 | 62.3383 | -61.3724 | -61.2259 | 62.114 | 0.091553 | -0.12817 | 0.23346 | 62.2147 | -61.3449 | -0.23346 | 0.13733 | -0.15564 | -0.086975 | -0.086975 | -0.20599 | 0.013733 | 0.077819 | 61.0107 | 61.3724 | 123.2529 | 123.4772 | -0.15564 | 123.3536 | 61.2305 | -0.20599 | 123.4772 | -0.15564 | 61.2305 | 123.2529 | 123.3536 | -123.5733 | -123.5458
25.9219 | 123.468 | -61.1206 | 62.2101 | -0.44545 | -9.5248e-05 | -0.0040084 | -0.0019248 | 0.062803 | 0.00056063 | 0.072791 | -61.322 | 62.2696 | -61.3403 | -61.3449 | 62.0407 | 0.073242 | -0.027466 | 0.15106 | 62.2833 | -61.3586 | -0.21973 | 0.059509 | -0.20142 | -0.22431 | -0.16937 | -0.23804 | 0.073242 | 0.018311 | 61.0931 | 61.2717 | 123.1613 | 123.3902 | -0.20142 | 123.4039 | 61.1938 | -0.23804 | 123.3902 | -0.20142 | 61.1938 | 123.1613 | 123.4039 | -123.5504 | -123.5687
26.9844 | 123.5825 | -61.0977 | 62.1506 | 0.43956 | 0.010586 | 0.0024006 | 0.0023482 | 0.059598 | -0.0015754 | 0.078132 | -61.2213 | 62.2833 | -61.3403 | -61.4044 | 61.9904 | -0.054932 | 0.041199 | 0.059509 | 62.2559 | -61.3907 | -0.24261 | 0.13275 | -0.1236 | -0.3067 | -0.16022 | -0.29297 | 0.10529 | 0.11902 | 61.1389 | 61.1572 | 123.0881 | 123.381 | -0.1236 | 123.3536 | 61.0428 | -0.29297 | 123.381 | -0.1236 | 61.0428 | 123.0881 | 123.3536 | -123.4909 | -123.5413
27.9219 | 123.5779 | -61.0794 | 62.1918 | -0.27761 | -0.0075722 | -0.0082804 | -0.01047 | 0.055326 | -0.0079844 | 0.081336 | -61.203 | 62.2421 | -61.322 | -61.4365 | 61.9766 | -0.018311 | 0.050354 | 0.068665 | 62.2971 | -61.3953 | -0.24261 | 0.050354 | -0.1236 | -0.35705 | -0.21515 | -0.31586 | 0.10529 | 0.11902 | 61.1298 | 61.1481 | 123.056 | 123.3215 | -0.1236 | 123.3765 | 61.0611 | -0.31586 | 123.3215 | -0.1236 | 61.0611 | 123.056 | 123.3765 | -123.5138 | -123.587
28.9844 | 123.5596 | -61.0703 | 62.1368 | 0.39378 | -0.0065042 | -0.0082804 | -0.011538 | 0.060666 | -0.00050737 | 0.081336 | -61.235 | 62.2192 | -61.3403 | -61.4273 | 61.972 | -0.036621 | 0.054932 | 0.059509 | 62.2375 | -61.3815 | -0.27008 | 0.082397 | -0.16479 | -0.35706 | -0.16479 | -0.31128 | 0.10071 | 0.10529 | 61.1252 | 61.1298 | 123.0423 | 123.2895 | -0.16479 | 123.3078 | 61.0336 | -0.31128 | 123.2895 | -0.16479 | 61.0336 | 123.0423 | 123.3078 | -123.4772 | -123.5184
29.9219 | 123.6099 | -61.084 | 62.178 | -0.29287 | -0.0075722 | -0.011485 | -0.0072648 | 0.049985 | -0.015461 | 0.064246 | -61.1938 | 62.2421 | -61.3174 | -61.4365 | 61.9629 | -0.018311 | 0.050354 | 0.07782 | 62.2971 | -61.3541 | -0.23346 | 0.064086 | -0.10986 | -0.35248 | -0.21515 | -0.27008 | 0.11902 | 0.1236 | 61.1343 | 61.1618 | 123.0469 | 123.3261 | -0.10986 | 123.381 | 61.0657 | -0.27008 | 123.3261 | -0.10986 | 61.0657 | 123.0469 | 123.381 | -123.4955 | -123.5321
30.9844 | 123.5687 | -61.084 | 62.178 | 0.058086 | -0.016117 | -0.017893 | -0.01047 | 0.044645 | -0.0090524 | 0.071723 | -61.2762 | 62.2238 | -61.3449 | -61.4044 | 61.9949 | -0.013733 | 0.027466 | 0.086975 | 62.2742 | -61.3632 | -0.26093 | 0.045776 | -0.19226 | -0.32043 | -0.18311 | -0.27924 | 0.09613 | 0.068665 | 61.1114 | 61.171 | 123.0789 | 123.3078 | -0.19226 | 123.3582 | 61.0703 | -0.27924 | 123.3078 | -0.19226 | 61.0703 | 123.0789 | 123.3582 | -123.523 | -123.5413
31.9219 | 123.5138 | -61.0931 | 62.1918 | -0.33864 | 0.0041778 | -0.017893 | -0.0051288 | 0.060666 | -0.015461 | 0.073859 | -61.2213 | 62.2604 | -61.3174 | -61.3586 | 62.0132 | 0.036621 | 0.013733 | 0.14191 | 62.2833 | -61.3678 | -0.2243 | 0.068665 | -0.12817 | -0.2655 | -0.17853 | -0.27466 | 0.091553 | 0.096131 | 61.1069 | 61.235 | 123.1064 | 123.3536 | -0.12817 | 123.3765 | 61.1298 | -0.27466 | 123.3536 | -0.12817 | 61.1298 | 123.1064 | 123.3765 | -123.5092 | -123.5596
32.9844 | 123.5825 | -61.0931 | 62.1826 | 0.01231 | -0.0054352 | -0.022166 | -0.0072648 | 0.066007 | -0.012257 | 0.073859 | -61.2442 | 62.2604 | -61.3312 | -61.4227 | 61.9949 | -0.022888 | 0.027466 | 0.07782 | 62.2833 | -61.3815 | -0.23804 | 0.07782 | -0.15106 | -0.32959 | -0.18768 | -0.28839 | 0.10071 | 0.086975 | 61.1206 | 61.171 | 123.0881 | 123.3536 | -0.15106 | 123.3765 | 61.0703 | -0.28839 | 123.3536 | -0.15106 | 61.0703 | 123.0881 | 123.3765 | -123.5138 | -123.5641
33.9219 | 123.4909 | -61.084 | 62.2101 | -0.41494 | -0.017185 | -0.011485 | 0.014097 | 0.051053 | -0.0047804 | 0.065314 | -61.235 | 62.265 | -61.3449 | -61.2762 | 62.0636 | 0.064087 | -0.041199 | 0.14648 | 62.2925 | -61.3403 | -0.26093 | 0.054932 | -0.15106 | -0.19226 | -0.14648 | -0.25635 | 0.082397 | 0.10986 | 61.0428 | 61.2305 | 123.1476 | 123.349 | -0.15106 | 123.3765 | 61.1481 | -0.25635 | 123.349 | -0.15106 | 61.1481 | 123.1476 | 123.3765 | -123.555 | -123.5504
34.9844 | 123.5733 | -61.1023 | 62.178 | -0.048725 | -0.0097082 | -0.0061444 | -0.013674 | 0.051053 | -0.0015754 | 0.063178 | -61.2762 | 62.2742 | -61.3266 | -61.3724 | 62.0224 | 0.009155 | 0 | 0.10986 | 62.2375 | -61.3495 | -0.2243 | 0.09613 | -0.17395 | -0.27008 | -0.15564 | -0.24719 | 0.059509 | 0.050354 | 61.1023 | 61.2122 | 123.1247 | 123.3765 | -0.17395 | 123.3398 | 61.1114 | -0.24719 | 123.3765 | -0.17395 | 61.1114 | 123.1247 | 123.3398 | -123.5046 | -123.5275
35.9219 | 123.5092 | -61.1298 | 62.2238 | -0.88796 | -0.0065042 | -0.0093484 | 0.0023482 | 0.060666 | 0.010174 | 0.074928 | -61.2259 | 62.3016 | -61.3358 | -61.2991 | 62.0819 | 0.086975 | -0.045776 | 0.18768 | 62.2742 | -61.3495 | -0.20599 | 0.07782 | -0.09613 | -0.16937 | -0.14191 | -0.21973 | 0.050354 | 0.10986 | 61.084 | 61.3174 | 123.2117 | 123.4314 | -0.09613 | 123.4039 | 61.2167 | -0.21973 | 123.4314 | -0.09613 | 61.2167 | 123.2117 | 123.4039 | -123.5596 | -123.5733
36.9844 | 123.555 | -61.084 | 62.178 | 0.01231 | -0.011844 | -0.015757 | -0.013674 | 0.061735 | -0.017597 | 0.070655 | -61.2762 | 62.265 | -61.3358 | -61.3907 | 62.0132 | -0.004578 | 0.018311 | 0.09613 | 62.2467 | -61.3678 | -0.25177 | 0.086975 | -0.19226 | -0.3067 | -0.1648 | -0.28381 | 0.068664 | 0.059509 | 61.1023 | 61.1801 | 123.0972 | 123.349 | -0.19226 | 123.3307 | 61.0794 | -0.28381 | 123.349 | -0.19226 | 61.0794 | 123.0972 | 123.3307 | -123.5138 | -123.5458
37.9219 | 123.4726 | -61.084 | 62.233 | -0.47597 | -9.5248e-05 | -0.013621 | 0.016233 | 0.063871 | -0.0090524 | 0.061042 | -61.2717 | 62.3016 | -61.3312 | -61.2579 | 62.1277 | 0.11902 | -0.10071 | 0.20142 | 62.2559 | -61.3495 | -0.24719 | 0.068665 | -0.18768 | -0.17395 | -0.10529 | -0.2655 | 0.022888 | 0.05951 | 60.9833 | 61.2854 | 123.2117 | 123.3856 | -0.18768 | 123.3398 | 61.203 | -0.2655 | 123.3856 | -0.18768 | 61.203 | 123.2117 | 123.3398 | -123.5641 | -123.5825
38.9844 | 123.5321 | -61.0931 | 62.1643 | 0.10386 | -0.012912 | -0.0082804 | -0.0040608 | 0.054258 | -0.020801 | 0.081336 | -61.3037 | 62.2238 | -61.3449 | -61.3861 | 62.0178 | -0.004578 | -0.013733 | 0.11444 | 62.2421 | -61.3632 | -0.25177 | 0.059509 | -0.21057 | -0.29297 | -0.14648 | -0.27008 | 0.077819 | 0.041199 | 61.0794 | 61.2076 | 123.111 | 123.317 | -0.21057 | 123.3353 | 61.0886 | -0.27008 | 123.317 | -0.21057 | 61.0886 | 123.111 | 123.3353 | -123.5092 | -123.5275
39.9219 | 123.4726 | -61.1298 | 62.2055 | 0.39378 | 0.0031088 | -0.016825 | 0.026914 | 0.056394 | -0.0079844 | 0.064246 | -61.2946 | 62.3199 | -61.3586 | -61.2762 | 62.0819 | 0.036621 | -0.068665 | 0.16937 | 62.2147 | -61.3495 | -0.22888 | 0.11444 | -0.16479 | -0.14648 | -0.1236 | -0.21973 | 0.009156 | 0.064087 | 61.0611 | 61.2991 | 123.2117 | 123.4497 | -0.16479 | 123.3444 | 61.1664 | -0.21973 | 123.4497 | -0.16479 | 61.1664 | 123.2117 | 123.3444 | -123.5641 | -123.555
40.9844 | 123.5367 | -61.0931 | 62.178 | 0.10386 | -0.0065042 | 0.0024006 | -0.014742 | 0.063871 | -0.015461 | 0.068519 | -61.29 | 62.2421 | -61.3541 | -61.3953 | 62.0361 | 0.009155 | 0.009155 | 0.11902 | 62.2421 | -61.3724 | -0.26093 | 0.064086 | -0.19684 | -0.30212 | -0.14191 | -0.27923 | 0.064086 | 0.064087 | 61.1023 | 61.2122 | 123.1293 | 123.3353 | -0.19684 | 123.3353 | 61.1023 | -0.27923 | 123.3353 | -0.19684 | 61.1023 | 123.1293 | 123.3353 | -123.5321 | -123.5504
41.9219 | 123.468 | -61.1206 | 62.2192 | -0.33864 | 0.0020408 | 0.0056046 | 0.014097 | 0.068143 | 0.0059006 | 0.070655 | -61.29 | 62.3749 | -61.3358 | -61.2213 | 62.114 | 0.1236 | -0.10986 | 0.22888 | 62.2238 | -61.322 | -0.21515 | 0.15564 | -0.16937 | -0.10071 | -0.10528 | -0.20142 | 0.004578 | 0.045776 | 61.0107 | 61.3495 | 123.2346 | 123.4955 | -0.16937 | 123.3444 | 61.2442 | -0.20142 | 123.4955 | -0.16937 | 61.2442 | 123.2346 | 123.3444 | -123.555 | -123.5413
42.9688 | 123.5641 | -61.0657 | 62.1918 | -0.12502 | -0.01398 | 0.0045366 | -0.0051288 | 0.059598 | -0.0090524 | 0.080268 | -61.29 | 62.2467 | -61.3586 | -61.4136 | 61.9949 | -0.013733 | 0.045776 | 0.082397 | 62.2833 | -61.377 | -0.29297 | 0.054932 | -0.2243 | -0.3479 | -0.19684 | -0.31128 | 0.091553 | 0.068665 | 61.1114 | 61.1481 | 123.0606 | 123.3124 | -0.2243 | 123.349 | 61.0519 | -0.31128 | 123.3124 | -0.2243 | 61.0519 | 123.0606 | 123.349 | -123.5504 | -123.5687
43.9219 | 123.4451 | -61.1298 | 62.1872 | -0.3539 | 0.0020408 | 0.0088096 | 0.0087562 | 0.057462 | 0.0069696 | 0.063178 | -61.2808 | 62.3566 | -61.3449 | -61.2579 | 62.0956 | 0.11902 | -0.082397 | 0.21057 | 62.2467 | -61.3266 | -0.21515 | 0.16937 | -0.15106 | -0.12817 | -0.091553 | -0.19684 | 0.059509 | 0.064087 | 61.0474 | 61.3403 | 123.2254 | 123.4863 | -0.15106 | 123.3765 | 61.2488 | -0.19684 | 123.4863 | -0.15106 | 61.2488 | 123.2254 | 123.3765 | -123.5321 | -123.5138
44.9844 | 123.5092 | -61.1069 | 62.2009 | -0.10976 | 0.0095178 | -0.0029404 | 0.017301 | 0.068143 | 0.0026966 | 0.068519 | -61.2396 | 62.3566 | -61.3403 | -61.2946 | 62.0636 | 0.068665 | -0.041199 | 0.15564 | 62.233 | -61.3312 | -0.23346 | 0.15564 | -0.13275 | -0.18768 | -0.13733 | -0.2243 | 0.032043 | 0.10071 | 61.0657 | 61.2625 | 123.1705 | 123.4634 | -0.13275 | 123.3398 | 61.1755 | -0.2243 | 123.4634 | -0.13275 | 61.1755 | 123.1705 | 123.3398 | -123.5413 | -123.5321
45.9219 | 123.5092 | -61.1114 | 62.1964 | -0.12502 | -9.5248e-05 | 0.024831 | 0.017301 | 0.062803 | 0.0016286 | 0.074928 | -61.2305 | 62.384 | -61.3358 | -61.3037 | 62.0728 | 0.054932 | -0.054932 | 0.15564 | 62.2284 | -61.322 | -0.2243 | 0.18768 | -0.11902 | -0.19226 | -0.1236 | -0.21057 | 0.032044 | 0.10529 | 61.0565 | 61.2671 | 123.1842 | 123.4955 | -0.11902 | 123.3398 | 61.1664 | -0.21057 | 123.4955 | -0.11902 | 61.1664 | 123.1842 | 123.3398 | -123.5321 | -123.5184
46.9219 | 123.4772 | -61.1069 | 62.1918 | -0.23183 | 0.00097275 | -0.0018714 | 0.014097 | 0.07562 | 0.01231 | 0.074928 | -61.2305 | 62.3474 | -61.3358 | -61.2991 | 62.0911 | 0.07782 | -0.036621 | 0.17395 | 62.2513 | -61.3541 | -0.22888 | 0.15564 | -0.1236 | -0.19226 | -0.10071 | -0.24719 | 0.05951 | 0.10529 | 61.0703 | 61.2808 | 123.1979 | 123.4543 | -0.1236 | 123.3582 | 61.1847 | -0.24719 | 123.4543 | -0.1236 | 61.1847 | 123.1979 | 123.3582 | -123.5275 | -123.5458
47.9844 | 123.4772 | -61.1389 | 62.1964 | -0.094502 | 0.00097275 | -0.013621 | -0.0040608 | 0.073484 | 0.0059006 | 0.077064 | -61.2488 | 62.3291 | -61.3815 | -61.2946 | 62.0865 | 0.091553 | -0.027466 | 0.17853 | 62.2604 | -61.3266 | -0.24262 | 0.13275 | -0.10986 | -0.15564 | -0.10986 | -0.18768 | 0.064087 | 0.13275 | 61.1115 | 61.3174 | 123.2254 | 123.468 | -0.10986 | 123.3994 | 61.2305 | -0.18768 | 123.468 | -0.10986 | 61.2305 | 123.2254 | 123.3994 | -123.5779 | -123.5229
48.9219 | 123.4863 | -61.1206 | 62.2055 | -0.063984 | 0.0095178 | -0.010416 | 0.0055522 | 0.063871 | 0.0059006 | 0.074928 | -61.2167 | 62.3749 | -61.3266 | -61.3083 | 62.0911 | 0.064087 | -0.036621 | 0.16479 | 62.2559 | -61.3632 | -0.20599 | 0.16937 | -0.096131 | -0.18768 | -0.11444 | -0.24262 | 0.050354 | 0.10986 | 61.084 | 61.2854 | 123.2117 | 123.4955 | -0.096131 | 123.3765 | 61.1847 | -0.24262 | 123.4955 | -0.096131 | 61.1847 | 123.2117 | 123.3765 | -123.5321 | -123.5687
49.9844 | 123.5504 | -61.084 | 62.1414 | 0.30223 | -0.0075722 | 0.00026463 | -0.013674 | 0.070279 | -0.0037124 | 0.064246 | -61.2442 | 62.2604 | -61.3495 | -61.441 | 62.0041 | -0.054932 | 0.050354 | 0.086975 | 62.2284 | -61.377 | -0.2655 | 0.11902 | -0.16022 | -0.35706 | -0.13733 | -0.29297 | 0.086976 | 0.10529 | 61.1343 | 61.171 | 123.0881 | 123.3444 | -0.16022 | 123.3124 | 61.0291 | -0.29297 | 123.3444 | -0.16022 | 61.0291 | 123.0881 | 123.3124 | -123.4909 | -123.5184
50.9219 | 123.4772 | -61.1206 | 62.2009 | -0.063984 | 0.010586 | 0.0034686 | 0.015165 | 0.071348 | 0.014446 | 0.069587 | -61.2259 | 62.352 | -61.3541 | -61.2946 | 62.0773 | 0.068665 | -0.045776 | 0.1831 | 62.2513 | -61.3449 | -0.23346 | 0.15106 | -0.10529 | -0.17395 | -0.1236 | -0.22431 | 0.050354 | 0.12817 | 61.0748 | 61.3037 | 123.1979 | 123.4726 | -0.10529 | 123.3719 | 61.1893 | -0.22431 | 123.4726 | -0.10529 | 61.1893 | 123.1979 | 123.3719 | -123.555 | -123.5458
51.9219 | 123.4451 | -61.1389 | 62.2009 | 0.19541 | 0.016995 | 0.0077416 | 0.013029 | 0.071348 | -0.011188 | 0.067451 | -61.2762 | 62.3795 | -61.3495 | -61.2534 | 62.0911 | 0.10071 | -0.09613 | 0.19226 | 62.2467 | -61.3815 | -0.21057 | 0.17853 | -0.13733 | -0.11444 | -0.10986 | -0.24262 | 0.045776 | 0.073242 | 61.0428 | 61.3312 | 123.23 | 123.5184 | -0.13733 | 123.3856 | 61.2396 | -0.24262 | 123.5184 | -0.13733 | 61.2396 | 123.23 | 123.3856 | -123.5504 | -123.5825
52.9844 | 123.4726 | -61.1114 | 62.2055 | -0.32338 | 0.0020408 | -0.0093484 | 0.00021117 | 0.073484 | 0.0026966 | 0.073859 | -61.29 | 62.3703 | -61.3724 | -61.2671 | 62.114 | 0.14191 | -0.10986 | 0.23346 | 62.2467 | -61.3449 | -0.26093 | 0.16479 | -0.17853 | -0.15564 | -0.091552 | -0.23346 | 0.041199 | 0.082397 | 61.0016 | 61.3449 | 123.2254 | 123.4818 | -0.17853 | 123.3582 | 61.2534 | -0.23346 | 123.4818 | -0.17853 | 61.2534 | 123.2254 | 123.3582 | -123.5779 | -123.5504
53.9219 | 123.4451 | -61.1343 | 62.2055 | 0.13438 | -0.0054352 | 0.022695 | 0.0087562 | 0.068143 | 0.011242 | 0.068519 | -61.203 | 62.4115 | -61.3403 | -61.2854 | 62.114 | 0.10529 | -0.09613 | 0.21973 | 62.2375 | -61.3815 | -0.20599 | 0.20599 | -0.068665 | -0.15106 | -0.091552 | -0.24719 | 0.032044 | 0.13733 | 61.0382 | 61.3541 | 123.2483 | 123.5458 | -0.068665 | 123.3719 | 61.2396 | -0.24719 | 123.5458 | -0.068665 | 61.2396 | 123.2483 | 123.3719 | -123.5458 | -123.587
54.9844 | 123.555 | -61.0931 | 62.1414 | 0.058086 | 0.0031088 | 0.0056046 | -0.0072648 | 0.071348 | 0.0091056 | 0.063178 | -61.2305 | 62.2742 | -61.3449 | -61.4273 | 61.9812 | -0.059509 | 0.045776 | 0.082397 | 62.2513 | -61.3815 | -0.25177 | 0.13275 | -0.13733 | -0.33417 | -0.16022 | -0.28839 | 0.10986 | 0.11444 | 61.1389 | 61.1755 | 123.0743 | 123.3673 | -0.13733 | 123.3444 | 61.0336 | -0.28839 | 123.3673 | -0.13733 | 61.0336 | 123.0743 | 123.3444 | -123.4863 | -123.5229
55.9219 | 123.4634 | -61.1298 | 62.1918 | 0.10386 | 0.00097275 | 0.00026463 | 0.0076882 | 0.069211 | 0.0048326 | 0.061042 | -61.2396 | 62.3795 | -61.3632 | -61.2762 | 62.0819 | 0.091553 | -0.068665 | 0.19226 | 62.2467 | -61.3861 | -0.23346 | 0.18768 | -0.10986 | -0.14648 | -0.10986 | -0.25635 | 0.054932 | 0.1236 | 61.0611 | 61.322 | 123.2117 | 123.5092 | -0.10986 | 123.3765 | 61.2213 | -0.25635 | 123.5092 | -0.10986 | 61.2213 | 123.2117 | 123.3765 | -123.555 | -123.5779
56.9688 | 123.5916 | -61.0748 | 62.1918 | -0.29287 | -0.0097082 | -0.0018714 | -0.017947 | 0.061735 | -0.020801 | 0.082404 | -61.1984 | 62.2787 | -61.3358 | -61.4548 | 61.9812 | -0.027466 | 0.064087 | 0.09613 | 62.3199 | -61.3678 | -0.26093 | 0.086976 | -0.1236 | -0.37994 | -0.21057 | -0.29297 | 0.12817 | 0.13733 | 61.1389 | 61.171 | 123.056 | 123.3536 | -0.1236 | 123.3948 | 61.0474 | -0.29297 | 123.3536 | -0.1236 | 61.0474 | 123.056 | 123.3948 | -123.5275 | -123.5596
57.9219 | 123.4589 | -61.1572 | 62.1964 | 0.37852 | 0.0041778 | 0.0066726 | 0.00021117 | 0.066007 | -0.0015754 | 0.077064 | -61.3174 | 62.352 | -61.377 | -61.2671 | 62.1048 | 0.091553 | -0.10071 | 0.21973 | 62.2375 | -61.3632 | -0.21973 | 0.15564 | -0.16022 | -0.10986 | -0.091553 | -0.20599 | 0.041199 | 0.059509 | 61.0565 | 61.377 | 123.262 | 123.5092 | -0.16022 | 123.3948 | 61.2488 | -0.20599 | 123.5092 | -0.16022 | 61.2488 | 123.262 | 123.3948 | -123.5733 | -123.5596
58.9844 | 123.468 | -61.1252 | 62.2238 | -0.24709 | -9.5248e-05 | 0.0013326 | 0.0066202 | 0.066007 | -0.0037124 | 0.063178 | -61.2625 | 62.3749 | -61.3495 | -61.3953 | 61.7661 | 0.12817 | 0.13733 | 0.2243 | 62.265 | -61.3266 | -0.2243 | 0.15106 | -0.13733 | -0.27008 | -0.45776 | -0.20142 | 0.041199 | 0.086975 | 61.2625 | 61.3495 | 122.8912 | 123.5001 | -0.13733 | 123.3902 | 61.2534 | -0.20142 | 123.5001 | -0.13733 | 61.2534 | 122.8912 | 123.3902 | -123.5733 | -123.5504
59.9219 | 123.4634 | -61.1572 | 62.2055 | 0.348 | 0.0063138 | 0.0024006 | 0.0044842 | 0.073484 | 0.00056063 | 0.063178 | -61.3174 | 62.3611 | -61.3861 | -61.2579 | 62.1094 | 0.073242 | -0.10071 | 0.22888 | 62.2147 | -61.3586 | -0.22888 | 0.15564 | -0.16022 | -0.10071 | -0.09613 | -0.20142 | 0.009156 | 0.068664 | 61.0565 | 61.3861 | 123.2666 | 123.5184 | -0.16022 | 123.3719 | 61.2305 | -0.20142 | 123.5184 | -0.16022 | 61.2305 | 123.2666 | 123.3719 | -123.5916 | -123.5641
60.9844 | 123.436 | -61.1618 | 62.1552 | 0.10386 | -9.5248e-05 | -0.0082804 | 0.0055522 | 0.073484 | 0.016583 | 0.068519 | -61.2808 | 62.3932 | -61.3632 | -61.2762 | 62.114 | 0.10071 | -0.082397 | 0.21515 | 62.2513 | -61.3861 | -0.20142 | 0.23804 | -0.11902 | -0.11444 | -0.041198 | -0.2243 | 0.096131 | 0.082397 | 61.0794 | 61.377 | 123.2758 | 123.555 | -0.11902 | 123.4131 | 61.2625 | -0.2243 | 123.555 | -0.11902 | 61.2625 | 123.2758 | 123.4131 | -123.5184 | -123.5413
61.9219 | 123.436 | -61.1572 | 62.1964 | 0.33274 | 0.016995 | 0.029104 | 0.0034162 | 0.067075 | 0.0016286 | 0.071723 | -61.7249 | 62.3154 | -61.4227 | -61.322 | 62.146 | 0.13275 | -0.09613 | 0.23346 | 62.2467 | -61.3586 | -0.2655 | 0.11902 | -0.56763 | -0.16479 | -0.050354 | -0.20142 | 0.050354 | -0.30213 | 61.0611 | 61.3907 | 123.3032 | 123.4726 | -0.56763 | 123.4039 | 61.29 | -0.20142 | 123.4726 | -0.56763 | 61.29 | 123.3032 | 123.4039 | -123.6191 | -123.555
62.9219 | 123.4589 | -61.1389 | 62.1597 | 0.40904 | 0.019131 | 0.0056046 | 0.0034162 | 0.063871 | 0.011242 | 0.078132 | -61.2991 | 62.3474 | -61.3861 | -61.2808 | 62.1185 | 0.064087 | -0.10529 | 0.20142 | 62.2101 | -61.3861 | -0.24719 | 0.18768 | -0.16022 | -0.14191 | -0.041199 | -0.24719 | 0.050354 | 0.086975 | 61.0336 | 61.3403 | 123.2574 | 123.4863 | -0.16022 | 123.349 | 61.203 | -0.24719 | 123.4863 | -0.16022 | 61.203 | 123.2574 | 123.349 | -123.5458 | -123.5458
63.9844 | 123.4863 | -61.1206 | 62.1872 | -0.30813 | 0.011654 | 0.0034686 | 0.0076882 | 0.068143 | 0.010174 | 0.072791 | -61.2534 | 62.3795 | -61.3586 | -61.2946 | 62.0682 | 0.07782 | -0.059509 | 0.19226 | 62.2559 | -61.377 | -0.23804 | 0.19226 | -0.13275 | -0.17395 | -0.11902 | -0.25635 | 0.068664 | 0.10529 | 61.0611 | 61.3129 | 123.1888 | 123.5001 | -0.13275 | 123.3765 | 61.1984 | -0.25635 | 123.5001 | -0.13275 | 61.1984 | 123.1888 | 123.3765 | -123.5458 | -123.5641
64.9219 | 123.6237 | -61.1114 | 62.1872 | 0.47007 | 0.0084498 | -0.011485 | -0.01047 | 0.061735 | 0.0059006 | 0.078132 | -61.2259 | 62.2833 | -61.3403 | -61.4456 | 61.9629 | -0.054932 | 0.07782 | 0.10071 | 62.2375 | -61.4136 | -0.22888 | 0.09613 | -0.11444 | -0.33417 | -0.2243 | -0.30212 | 0.050354 | 0.11444 | 61.1893 | 61.2122 | 123.0743 | 123.3948 | -0.11444 | 123.349 | 61.0565 | -0.30212 | 123.3948 | -0.11444 | 61.0565 | 123.0743 | 123.349 | -123.5275 | -123.6008
65.9844 | 123.468 | -61.1298 | 62.2375 | 0.22593 | 0.010586 | 0.018423 | 0.0098242 | 0.072416 | 0.013378 | 0.06211 | -61.2991 | 62.3474 | -61.3998 | -61.2579 | 62.1277 | 0.14648 | -0.10529 | 0.21057 | 62.2604 | -61.3449 | -0.27008 | 0.10986 | -0.16937 | -0.12817 | -0.10986 | -0.21515 | 0.022888 | 0.10071 | 61.0245 | 61.3403 | 123.2574 | 123.4772 | -0.16937 | 123.3902 | 61.2762 | -0.21515 | 123.4772 | -0.16937 | 61.2762 | 123.2574 | 123.3902 | -123.6374 | -123.5825
66.9219 | 123.5596 | -61.0977 | 62.1552 | 0.48533 | -0.0043672 | 0.0077416 | -0.01581 | 0.059598 | 0.016583 | 0.069587 | -61.2396 | 62.3062 | -61.3724 | -61.441 | 61.908 | -0.045776 | 0.064087 | 0.09613 | 62.2559 | -61.409 | -0.27466 | 0.15106 | -0.14191 | -0.34332 | -0.24719 | -0.31128 | 0.10071 | 0.13275 | 61.1618 | 61.1938 | 123.0057 | 123.4039 | -0.14191 | 123.3536 | 61.0519 | -0.31128 | 123.4039 | -0.14191 | 61.0519 | 123.0057 | 123.3536 | -123.5275 | -123.5641
67.9844 | 123.4634 | -61.1389 | 62.178 | 0.39378 | 0.0063138 | 0.021627 | 0.013029 | 0.067075 | 0.0059006 | 0.05677 | -61.3083 | 62.3749 | -61.3678 | -61.2625 | 62.114 | 0.07782 | -0.10071 | 0.19684 | 62.2284 | -61.3724 | -0.22888 | 0.19684 | -0.16937 | -0.1236 | -0.064087 | -0.23346 | 0.050354 | 0.059509 | 61.0382 | 61.3358 | 123.2529 | 123.5138 | -0.16937 | 123.3673 | 61.2167 | -0.23346 | 123.5138 | -0.16937 | 61.2167 | 123.2529 | 123.3673 | -123.5458 | -123.5504
68.9219 | 123.4909 | -61.1206 | 62.1826 | 0.48533 | -0.0032992 | -0.022166 | 0.0023482 | 0.064939 | 0.0091056 | 0.074928 | -61.2625 | 62.3108 | -61.4044 | -61.3312 | 62.0407 | 0.041199 | -0.041199 | 0.16022 | 62.265 | -61.3907 | -0.28381 | 0.12817 | -0.14191 | -0.21057 | -0.14191 | -0.27008 | 0.082398 | 0.14191 | 61.0794 | 61.2808 | 123.1613 | 123.4314 | -0.14191 | 123.3856 | 61.1618 | -0.27008 | 123.4314 | -0.14191 | 61.1618 | 123.1613 | 123.3856 | -123.587 | -123.5733
69.9844 | 123.4451 | -61.1343 | 62.1918 | 0.10386 | 0.010586 | 0.016286 | -0.0051288 | 0.063871 | 0.015514 | 0.070655 | -61.2762 | 62.3703 | -61.377 | -61.2671 | 62.1094 | 0.091553 | -0.10071 | 0.20142 | 62.2375 | -61.3632 | -0.24262 | 0.17853 | -0.14191 | -0.13275 | -0.082397 | -0.22888 | 0.045777 | 0.10071 | 61.0336 | 61.3358 | 123.2437 | 123.5046 | -0.14191 | 123.3719 | 61.2259 | -0.22888 | 123.5046 | -0.14191 | 61.2259 | 123.2437 | 123.3719 | -123.5687 | -123.555
70.9219 | 123.5367 | -61.0886 | 62.146 | 0.31749 | -9.5248e-05 | -0.0050764 | -0.016879 | 0.049985 | -0.0015754 | 0.066383 | -61.235 | 62.2421 | -61.3449 | -61.4548 | 61.972 | -0.045776 | 0.050354 | 0.082397 | 62.2925 | -61.4182 | -0.25635 | 0.09613 | -0.14648 | -0.36621 | -0.17395 | -0.32959 | 0.14648 | 0.10986 | 61.1389 | 61.171 | 123.0606 | 123.3307 | -0.14648 | 123.381 | 61.0428 | -0.32959 | 123.3307 | -0.14648 | 61.0428 | 123.0606 | 123.381 | -123.4909 | -123.5641
71.9844 | 123.468 | -61.1114 | 62.2009 | -0.0029495 | 0.0052458 | 0.013082 | 0.0087562 | 0.064939 | 0.01231 | 0.070655 | -61.2442 | 62.3703 | -61.3541 | -61.2991 | 62.0636 | 0.073242 | -0.068665 | 0.17853 | 62.2559 | -61.3861 | -0.24262 | 0.16937 | -0.13275 | -0.18768 | -0.13733 | -0.27466 | 0.054931 | 0.10986 | 61.0428 | 61.29 | 123.175 | 123.4818 | -0.13275 | 123.3673 | 61.1847 | -0.27466 | 123.4818 | -0.13275 | 61.1847 | 123.175 | 123.3673 | -123.555 | -123.587
72.9219 | 123.5596 | -61.116 | 62.1368 | 0.37852 | -0.0011632 | -0.0040084 | -0.020083 | 0.057462 | -0.0079844 | 0.071723 | -61.235 | 62.2604 | -61.3907 | -61.4319 | 61.9766 | -0.050354 | 0.036621 | 0.068665 | 62.2879 | -61.3953 | -0.27466 | 0.1236 | -0.11902 | -0.31586 | -0.16022 | -0.27924 | 0.15106 | 0.15564 | 61.1526 | 61.1847 | 123.0927 | 123.3765 | -0.11902 | 123.4039 | 61.0657 | -0.27924 | 123.3765 | -0.11902 | 61.0657 | 123.0927 | 123.4039 | -123.5275 | -123.5321
73.9844 | 123.4863 | -61.116 | 62.1964 | -0.23183 | 0.0052458 | -0.0050764 | 0.016233 | 0.069211 | 0.015514 | 0.064246 | -61.235 | 62.3611 | -61.3495 | -61.2946 | 62.0453 | 0.064087 | -0.036621 | 0.18768 | 62.265 | -61.377 | -0.23346 | 0.16479 | -0.11902 | -0.17853 | -0.15106 | -0.26093 | 0.068665 | 0.11444 | 61.0794 | 61.3037 | 123.1613 | 123.4772 | -0.11902 | 123.381 | 61.1801 | -0.26093 | 123.4772 | -0.11902 | 61.1801 | 123.1613 | 123.381 | -123.5458 | -123.5733
74.9219 | 123.5458 | -61.1023 | 62.1597 | 0.4243 | -0.011844 | -0.013621 | -0.013674 | 0.059598 | -0.0079844 | 0.077064 | -61.2396 | 62.2421 | -61.3678 | -61.441 | 61.9766 | -0.054932 | 0.050354 | 0.073242 | 62.3016 | -61.3953 | -0.2655 | 0.082397 | -0.13733 | -0.33875 | -0.1831 | -0.29297 | 0.14191 | 0.12817 | 61.1526 | 61.1755 | 123.0789 | 123.3444 | -0.13733 | 123.4039 | 61.0474 | -0.29297 | 123.3444 | -0.13733 | 61.0474 | 123.0789 | 123.4039 | -123.5275 | -123.555
75.9219 | 123.5779 | -61.1023 | 62.146 | 0.62266 | -0.0097082 | 0.01415 | 0.0012792 | 0.05853 | 0.0016286 | 0.083472 | -61.2305 | 62.2696 | -61.3678 | -61.441 | 61.9904 | -0.054932 | 0.054932 | 0.041199 | 62.2559 | -61.3998 | -0.2655 | 0.1236 | -0.12817 | -0.33875 | -0.15564 | -0.29755 | 0.10986 | 0.13733 | 61.1572 | 61.1435 | 123.0927 | 123.3719 | -0.12817 | 123.3582 | 61.0474 | -0.29755 | 123.3719 | -0.12817 | 61.0474 | 123.0927 | 123.3582 | -123.5138 | -123.5458
76.9844 | 123.555 | -61.0886 | 62.1597 | 0.36326 | 0.0041778 | 0.0077416 | 0.0076882 | 0.064939 | -0.0026434 | 0.068519 | -61.2762 | 62.3199 | -61.3724 | -61.3678 | 62.027 | -0.022888 | -0.004578 | 0.10529 | 62.2559 | -61.409 | -0.28381 | 0.16022 | -0.18768 | -0.27924 | -0.13275 | -0.32043 | 0.09613 | 0.09613 | 61.084 | 61.1938 | 123.1155 | 123.4085 | -0.18768 | 123.3444 | 61.0657 | -0.32043 | 123.4085 | -0.18768 | 61.0657 | 123.1155 | 123.3444 | -123.5321 | -123.5687
77.9219 | 123.5367 | -61.1069 | 62.1735 | 0.348 | -0.0022312 | -0.0061444 | -0.0061968 | 0.042508 | -0.016529 | 0.070655 | -61.2488 | 62.265 | -61.3403 | -61.4044 | 62.0178 | -0.032043 | 0.004578 | 0.10529 | 62.2375 | -61.3998 | -0.23346 | 0.091553 | -0.14191 | -0.29755 | -0.15564 | -0.29297 | 0.064087 | 0.091553 | 61.1115 | 61.2122 | 123.1247 | 123.3719 | -0.14191 | 123.3444 | 61.0748 | -0.29297 | 123.3719 | -0.14191 | 61.0748 | 123.1247 | 123.3444 | -123.5138 | -123.5733
78.9844 | 123.4085 | -61.1343 | 62.1872 | 0.22593 | 0.024472 | 0.0077416 | 0.019437 | 0.052121 | 0.01231 | 0.072791 | -61.3129 | 62.3611 | -61.3907 | -61.2396 | 62.1231 | 0.11444 | -0.15106 | 0.25177 | 62.2147 | -61.3678 | -0.25635 | 0.17395 | -0.17853 | -0.10529 | -0.064087 | -0.23346 | 0.027466 | 0.07782 | 60.9833 | 61.3861 | 123.2574 | 123.4955 | -0.17853 | 123.349 | 61.2488 | -0.23346 | 123.4955 | -0.17853 | 61.2488 | 123.2574 | 123.349 | -123.5779 | -123.555
79.9219 | 123.5458 | -61.1023 | 62.1414 | 0.47007 | -0.0065042 | 0.013082 | -0.0061968 | 0.059598 | -0.012257 | 0.070655 | -61.2488 | 62.2467 | -61.3632 | -61.4227 | 61.9858 | -0.041199 | 0.022888 | 0.10529 | 62.2696 | -61.409 | -0.26093 | 0.10529 | -0.14648 | -0.32043 | -0.15564 | -0.3067 | 0.12817 | 0.11444 | 61.1252 | 61.2076 | 123.0881 | 123.349 | -0.14648 | 123.3719 | 61.0611 | -0.3067 | 123.349 | -0.14648 | 61.0611 | 123.0881 | 123.3719 | -123.5046 | -123.5504
80.9219 | 123.5458 | -61.0977 | 62.146 | 0.36326 | -0.0054352 | -0.015757 | -0.0029928 | 0.063871 | -0.0026434 | 0.057838 | -61.2488 | 62.265 | -61.3724 | -61.4227 | 61.9858 | -0.050354 | 0.027466 | 0.086975 | 62.2742 | -61.4044 | -0.27466 | 0.11902 | -0.15106 | -0.32501 | -0.16022 | -0.3067 | 0.12817 | 0.1236 | 61.1252 | 61.1847 | 123.0835 | 123.3627 | -0.15106 | 123.3719 | 61.0474 | -0.3067 | 123.3627 | -0.15106 | 61.0474 | 123.0835 | 123.3719 | -123.5184 | -123.5504
81.9844 | 123.5504 | -61.0886 | 62.1597 | 0.37852 | 0.0020408 | 0.00026463 | -0.01047 | 0.05853 | -0.0079844 | 0.070655 | -61.2259 | 62.2604 | -61.3724 | -61.4319 | 61.9675 | -0.064087 | 0.045776 | 0.054932 | 62.2742 | -61.4136 | -0.28381 | 0.10071 | -0.13733 | -0.34332 | -0.19226 | -0.32501 | 0.11444 | 0.14648 | 61.1343 | 61.1435 | 123.056 | 123.349 | -0.13733 | 123.3627 | 61.0245 | -0.32501 | 123.349 | -0.13733 | 61.0245 | 123.056 | 123.3627 | -123.5321 | -123.5733
82.9219 | 123.5779 | -61.1206 | 62.1506 | 0.51585 | -0.0043672 | -0.0050764 | 0.0012792 | 0.052121 | -0.012257 | 0.075996 | -61.2213 | 62.2696 | -61.3495 | -61.4182 | 61.972 | -0.068665 | 0.054932 | 0.059509 | 62.265 | -61.4273 | -0.22888 | 0.11902 | -0.10071 | -0.29755 | -0.17853 | -0.3067 | 0.11444 | 0.12817 | 61.1755 | 61.1801 | 123.0927 | 123.3902 | -0.10071 | 123.3856 | 61.0519 | -0.3067 | 123.3902 | -0.10071 | 61.0519 | 123.0927 | 123.3856 | -123.5001 | -123.5779
83.9844 | 123.4314 | -61.1389 | 62.2147 | 0.40904 | -9.5248e-05 | 0.012014 | 0.017301 | 0.066007 | 0.0069696 | 0.072791 | -61.2946 | 62.3566 | -61.3586 | -61.2488 | 62.1277 | 0.09613 | -0.11902 | 0.20142 | 62.2238 | -61.3632 | -0.21973 | 0.14191 | -0.15564 | -0.10986 | -0.086975 | -0.2243 | 0.009155 | 0.064087 | 61.0199 | 61.3403 | 123.2666 | 123.4955 | -0.15564 | 123.3627 | 61.235 | -0.2243 | 123.4955 | -0.15564 | 61.235 | 123.2666 | 123.3627 | -123.5733 | -123.5779
84.9219 | 123.5229 | -61.1023 | 62.1414 | 0.37852 | -0.01398 | 0.0066726 | -0.017947 | 0.057462 | -0.017597 | 0.071723 | -61.2259 | 62.2513 | -61.3632 | -61.4227 | 61.9766 | -0.036621 | 0.032043 | 0.068665 | 62.2559 | -61.3861 | -0.26093 | 0.10986 | -0.1236 | -0.32043 | -0.16479 | -0.28381 | 0.11444 | 0.13733 | 61.1343 | 61.171 | 123.0789 | 123.3536 | -0.1236 | 123.3582 | 61.0657 | -0.28381 | 123.3536 | -0.1236 | 61.0657 | 123.0789 | 123.3582 | -123.5046 | -123.5275
85.9688 | 123.4497 | -61.1023 | 62.233 | -0.41494 | 0.0020408 | -0.013621 | 0.0076882 | 0.068143 | -0.0069164 | 0.06211 | -61.2854 | 62.384 | -61.3678 | -61.2488 | 62.1048 | 0.11444 | -0.091553 | 0.23346 | 62.2559 | -61.3541 | -0.2655 | 0.15106 | -0.18311 | -0.14648 | -0.12817 | -0.25177 | 0.022888 | 0.082398 | 61.0107 | 61.3358 | 123.2071 | 123.4863 | -0.18311 | 123.3582 | 61.2167 | -0.25177 | 123.4863 | -0.18311 | 61.2167 | 123.2071 | 123.3582 | -123.6008 | -123.587
86.9219 | 123.5504 | -61.1069 | 62.1552 | 0.28697 | -0.0054352 | -0.0082804 | 0.00021117 | 0.056394 | -0.0047804 | 0.072791 | -61.2762 | 62.2513 | -61.3678 | -61.3907 | 62.027 | -0.018311 | -0.009155 | 0.11444 | 62.265 | -61.3815 | -0.26093 | 0.096131 | -0.16937 | -0.28381 | -0.12817 | -0.27466 | 0.10986 | 0.091553 | 61.0977 | 61.2213 | 123.1339 | 123.3582 | -0.16937 | 123.3719 | 61.0886 | -0.27466 | 123.3582 | -0.16937 | 61.0886 | 123.1339 | 123.3719 | -123.5229 | -123.5367
87.9688 | 123.4589 | -61.1252 | 62.2009 | 0.042827 | 0.013791 | 0.021627 | 0.020506 | 0.062803 | 0.016583 | 0.057838 | -61.2534 | 62.3703 | -61.3815 | -61.2717 | 62.0911 | 0.07782 | -0.082397 | 0.20142 | 62.2513 | -61.3861 | -0.25635 | 0.16937 | -0.12817 | -0.14648 | -0.10986 | -0.26093 | 0.050354 | 0.12817 | 61.0428 | 61.3266 | 123.2162 | 123.4955 | -0.12817 | 123.3765 | 61.203 | -0.26093 | 123.4955 | -0.12817 | 61.203 | 123.2162 | 123.3765 | -123.5825 | -123.587
88.9219 | 123.4909 | -61.1114 | 62.1506 | 0.45481 | -0.0075722 | -0.0093484 | -0.0083338 | 0.064939 | -0.0079844 | 0.077064 | -61.2625 | 62.2421 | -61.3724 | -61.3998 | 62.0132 | -0.018311 | -0.004578 | 0.11444 | 62.2787 | -61.3815 | -0.26093 | 0.091552 | -0.15106 | -0.28839 | -0.13733 | -0.27008 | 0.12817 | 0.10986 | 61.1069 | 61.2259 | 123.1247 | 123.3536 | -0.15106 | 123.3902 | 61.0931 | -0.27008 | 123.3536 | -0.15106 | 61.0931 | 123.1247 | 123.3902 | -123.5229 | -123.5321
89.9844 | 123.4589 | -61.1526 | 62.2055 | 0.24119 | 0.0073818 | 0.030172 | 0.014097 | 0.056394 | 0.0069696 | 0.059974 | -61.3129 | 62.3795 | -61.3632 | -61.2259 | 62.1323 | 0.086975 | -0.11444 | 0.21515 | 62.2055 | -61.3678 | -0.21057 | 0.17395 | -0.16022 | -0.073242 | -0.073242 | -0.21515 | 0 | 0.050354 | 61.0382 | 61.3678 | 123.2849 | 123.5321 | -0.16022 | 123.3582 | 61.2396 | -0.21515 | 123.5321 | -0.16022 | 61.2396 | 123.2849 | 123.3582 | -123.5687 | -123.5733
90.9219 | 123.5413 | -61.1023 | 62.178 | 0.11912 | -0.0065042 | -0.021098 | -0.013674 | 0.05853 | -0.0079844 | 0.06211 | -61.2762 | 62.2604 | -61.377 | -61.3907 | 62.0316 | 0.009155 | -0.018311 | 0.13275 | 62.2513 | -61.3815 | -0.27466 | 0.082397 | -0.17395 | -0.28839 | -0.14649 | -0.27924 | 0.073242 | 0.10071 | 61.084 | 61.235 | 123.1338 | 123.3627 | -0.17395 | 123.3536 | 61.1114 | -0.27924 | 123.3627 | -0.17395 | 61.1114 | 123.1338 | 123.3536 | -123.555 | -123.5596
91.9688 | 123.4222 | -61.1298 | 62.2101 | 0.25645 | 0.0063138 | -0.0082804 | 0.022642 | 0.059598 | 0.0037646 | 0.064246 | -61.2991 | 62.352 | -61.3632 | -61.235 | 62.1231 | 0.09613 | -0.13275 | 0.21973 | 62.2147 | -61.3724 | -0.23346 | 0.14191 | -0.16937 | -0.10528 | -0.086975 | -0.24261 | 0.004578 | 0.064087 | 60.997 | 61.3495 | 123.2529 | 123.4818 | -0.16937 | 123.3444 | 61.2259 | -0.24261 | 123.4818 | -0.16937 | 61.2259 | 123.2529 | 123.3444 | -123.5733 | -123.5825
92.9219 | 123.5367 | -61.0977 | 62.1826 | 0.073345 | -0.0075722 | -0.018961 | -0.01047 | 0.062803 | -0.016529 | 0.070655 | -61.3083 | 62.2879 | -61.3724 | -61.3724 | 62.0407 | -0.004578 | -0.009155 | 0.12817 | 62.3154 | -61.3907 | -0.27466 | 0.10529 | -0.21057 | -0.27466 | -0.14191 | -0.29297 | 0.13275 | 0.064086 | 61.0886 | 61.2259 | 123.1384 | 123.3856 | -0.21057 | 123.4131 | 61.0931 | -0.29297 | 123.3856 | -0.21057 | 61.0931 | 123.1384 | 123.4131 | -123.555 | -123.5733
93.9844 | 123.436 | -61.1206 | 62.2147 | 0.10386 | 0.0073818 | 0.013082 | 0.0044842 | 0.063871 | 0.016583 | 0.06211 | -61.2488 | 62.3383 | -61.3815 | -61.2579 | 62.0819 | 0.082397 | -0.086975 | 0.19226 | 62.2513 | -61.3815 | -0.26093 | 0.1236 | -0.12817 | -0.13733 | -0.13275 | -0.26093 | 0.036621 | 0.13275 | 61.0336 | 61.3129 | 123.2025 | 123.4589 | -0.12817 | 123.3719 | 61.203 | -0.26093 | 123.4589 | -0.12817 | 61.203 | 123.2025 | 123.3719 | -123.5962 | -123.5962
94.9219 | 123.5184 | -61.0886 | 62.1597 | 0.042827 | -0.017185 | -0.014689 | -0.0051288 | 0.066007 | -0.0079844 | 0.069587 | -61.29 | 62.3016 | -61.3586 | -61.3815 | 62.0224 | 0.004578 | -0.009155 | 0.14191 | 62.265 | -61.377 | -0.27008 | 0.14191 | -0.20142 | -0.29297 | -0.13733 | -0.28839 | 0.10529 | 0.068665 | 61.0794 | 61.2305 | 123.111 | 123.3902 | -0.20142 | 123.3536 | 61.0931 | -0.28839 | 123.3902 | -0.20142 | 61.0931 | 123.111 | 123.3536 | -123.5184 | -123.5367
95.9844 | 123.4451 | -61.1114 | 62.2147 | 0.088604 | 0.0095178 | 0.010946 | 0.020506 | 0.068143 | 0.0059006 | 0.070655 | -61.2625 | 62.3428 | -61.377 | -61.2534 | 62.1048 | 0.073242 | -0.086975 | 0.20142 | 62.2284 | -61.3907 | -0.2655 | 0.12817 | -0.15106 | -0.14191 | -0.10986 | -0.27924 | 0.013733 | 0.11444 | 61.0245 | 61.3129 | 123.2162 | 123.4543 | -0.15106 | 123.3398 | 61.1847 | -0.27924 | 123.4543 | -0.15106 | 61.1847 | 123.2162 | 123.3398 | -123.5916 | -123.6053
96.9219 | 123.5046 | -61.0931 | 62.1689 | 0.18016 | -0.0075722 | 0.00026463 | -0.0040608 | 0.064939 | -0.013325 | 0.06211 | -61.29 | 62.2513 | -61.3861 | -61.3815 | 62.027 | 0.013733 | -0.009155 | 0.13275 | 62.2513 | -61.3907 | -0.29297 | 0.082398 | -0.19684 | -0.28839 | -0.14191 | -0.29755 | 0.082398 | 0.09613 | 61.084 | 61.2259 | 123.1201 | 123.3444 | -0.19684 | 123.3444 | 61.1069 | -0.29755 | 123.3444 | -0.19684 | 61.1069 | 123.1201 | 123.3444 | -123.555 | -123.5596
97.9844 | 123.5413 | -61.1206 | 62.146 | 0.37852 | 0.00097275 | -0.0093484 | -0.0051288 | 0.069211 | -0.0079844 | 0.066383 | -61.2488 | 62.2971 | -61.3449 | -61.4136 | 61.9812 | -0.050354 | 0.050354 | 0.073242 | 62.2696 | -61.3907 | -0.22431 | 0.15106 | -0.12817 | -0.29297 | -0.16479 | -0.27008 | 0.1236 | 0.096131 | 61.171 | 61.1938 | 123.1018 | 123.4177 | -0.12817 | 123.3902 | 61.0703 | -0.27008 | 123.4177 | -0.12817 | 61.0703 | 123.1018 | 123.3902 | -123.4909 | -123.5367
98.9219 | 123.555 | -61.0886 | 62.2009 | 0.027569 | -0.0097082 | -0.0040084 | -0.01047 | 0.052121 | -0.018665 | 0.068519 | -61.2671 | 62.2513 | -61.377 | -61.409 | 62.0132 | -0.013733 | 0.013733 | 0.10986 | 62.3016 | -61.3907 | -0.28839 | 0.050354 | -0.17853 | -0.32043 | -0.18768 | -0.30212 | 0.10071 | 0.10986 | 61.1023 | 61.1984 | 123.1018 | 123.3398 | -0.17853 | 123.3902 | 61.0748 | -0.30212 | 123.3398 | -0.17853 | 61.0748 | 123.1018 | 123.3902 | -123.5779 | -123.5916
99.9688 | 123.4497 | -61.1298 | 62.2009 | 0.01231 | 0.0095178 | 0.0024006 | 0.027982 | 0.05853 | 0.0037646 | 0.069587 | -61.2305 | 62.3566 | -61.3541 | -61.2534 | 62.0773 | 0.07782 | -0.068665 | 0.17853 | 62.2559 | -61.3861 | -0.2243 | 0.15564 | -0.10071 | -0.1236 | -0.1236 | -0.25635 | 0.054931 | 0.1236 | 61.0611 | 61.3083 | 123.2071 | 123.4863 | -0.10071 | 123.3856 | 61.2076 | -0.25635 | 123.4863 | -0.10071 | 61.2076 | 123.2071 | 123.3856 | -123.555 | -123.587
100.9219 | 123.5504 | -61.0886 | 62.178 | -0.15554 | -0.023593 | -0.0050764 | -0.013674 | 0.054258 | -0.012257 | 0.073859 | -61.2625 | 62.2604 | -61.3586 | -61.409 | 62.0087 | -0.022888 | 0.041199 | 0.10529 | 62.2925 | -61.377 | -0.27008 | 0.082397 | -0.17395 | -0.32043 | -0.16937 | -0.28839 | 0.11444 | 0.096131 | 61.1298 | 61.1938 | 123.0972 | 123.349 | -0.17395 | 123.381 | 61.0657 | -0.28839 | 123.349 | -0.17395 | 61.0657 | 123.0972 | 123.381 | -123.5367 | -123.555
101.9219 | 123.587 | -61.0703 | 62.178 | -0.094502 | -0.01398 | -0.037119 | -0.00085683 | 0.052121 | -0.02721 | 0.072791 | -61.2488 | 62.2787 | -61.3586 | -61.4182 | 61.9858 | -0.032043 | 0.027466 | 0.091553 | 62.2879 | -61.3861 | -0.28839 | 0.10071 | -0.17853 | -0.3479 | -0.19226 | -0.31586 | 0.10986 | 0.10986 | 61.0977 | 61.1618 | 123.056 | 123.349 | -0.17853 | 123.3582 | 61.0382 | -0.31586 | 123.349 | -0.17853 | 61.0382 | 123.056 | 123.3582 | -123.5367 | -123.5641
102.9844 | 123.587 | -61.0748 | 62.1918 | -0.079243 | -0.011844 | -0.017893 | -0.0029928 | 0.054258 | -0.020801 | 0.068519 | -61.2167 | 62.2696 | -61.3358 | -61.4365 | 61.972 | -0.036621 | 0.07782 | 0.068665 | 62.2879 | -61.3724 | -0.26093 | 0.07782 | -0.14191 | -0.36163 | -0.21973 | -0.29755 | 0.096131 | 0.11902 | 61.1526 | 61.1435 | 123.0469 | 123.3444 | -0.14191 | 123.3627 | 61.0382 | -0.29755 | 123.3444 | -0.14191 | 61.0382 | 123.0469 | 123.3627 | -123.5275 | -123.5641
103.9219 | 123.5275 | -61.0657 | 62.1735 | 0.058086 | 0.00097275 | -0.017893 | -0.00085683 | 0.055326 | -0.015461 | 0.065314 | -61.2671 | 62.2604 | -61.3586 | -61.3998 | 61.9858 | -0.013733 | 0 | 0.10986 | 62.265 | -61.3815 | -0.29297 | 0.086975 | -0.20142 | -0.33417 | -0.18768 | -0.31586 | 0.091553 | 0.091553 | 61.0657 | 61.1755 | 123.0515 | 123.3261 | -0.20142 | 123.3307 | 61.0519 | -0.31586 | 123.3261 | -0.20142 | 61.0519 | 123.0515 | 123.3307 | -123.5321 | -123.555
104.9844 | 123.5504 | -61.0931 | 62.1368 | 0.40904 | -0.0086402 | -0.0029404 | 0.011961 | 0.048917 | -0.0047804 | 0.066383 | -61.235 | 62.2833 | -61.3449 | -61.4182 | 61.9629 | -0.059509 | 0.059509 | 0.054932 | 62.2559 | -61.4136 | -0.25177 | 0.14648 | -0.14191 | -0.32501 | -0.17395 | -0.32043 | 0.11902 | 0.10986 | 61.1526 | 61.1481 | 123.056 | 123.3765 | -0.14191 | 123.349 | 61.0336 | -0.32043 | 123.3765 | -0.14191 | 61.0336 | 123.056 | 123.349 | -123.4818 | -123.5504
105.9219 | 123.6099 | -61.0748 | 62.1735 | -0.38442 | -0.0086402 | -0.0072124 | 0.00021117 | 0.060666 | -0.013325 | 0.064246 | -61.1801 | 62.2559 | -61.3541 | -61.4319 | 61.9492 | -0.059509 | 0.086975 | 0.050354 | 62.2787 | -61.3678 | -0.27924 | 0.082397 | -0.10529 | -0.35706 | -0.2243 | -0.29297 | 0.10529 | 0.17395 | 61.1618 | 61.1252 | 123.024 | 123.3307 | -0.10529 | 123.3536 | 61.0153 | -0.29297 | 123.3307 | -0.10529 | 61.0153 | 123.024 | 123.3536 | -123.5275 | -123.5413
106.9219 | 123.4818 | -61.116 | 62.2192 | -0.44545 | -0.018253 | -0.011485 | 0.016233 | 0.054258 | 0.0016286 | 0.074928 | -61.2396 | 62.3291 | -61.3449 | -61.2946 | 62.0636 | 0.086975 | -0.050354 | 0.19684 | 62.265 | -61.3449 | -0.22888 | 0.10986 | -0.1236 | -0.17853 | -0.15564 | -0.22888 | 0.045777 | 0.10529 | 61.0657 | 61.3129 | 123.1796 | 123.4451 | -0.1236 | 123.381 | 61.203 | -0.22888 | 123.4451 | -0.1236 | 61.203 | 123.1796 | 123.381 | -123.5641 | -123.5641
107.9844 | 123.5687 | -61.0748 | 62.1964 | -0.048725 | -0.0054352 | -0.015757 | 0.0012792 | 0.059598 | -0.020801 | 0.05677 | -61.203 | 62.265 | -61.3403 | -61.4548 | 61.9766 | -0.036621 | 0.07782 | 0.064087 | 62.3062 | -61.3953 | -0.2655 | 0.068665 | -0.12817 | -0.37994 | -0.21973 | -0.32043 | 0.10986 | 0.13733 | 61.1526 | 61.1389 | 123.0515 | 123.3398 | -0.12817 | 123.381 | 61.0382 | -0.32043 | 123.3398 | -0.12817 | 61.0382 | 123.0515 | 123.381 | -123.5367 | -123.5916
108.9219 | 123.436 | -61.1298 | 62.2375 | -0.32338 | -0.0043672 | 0.0045366 | 0.013029 | 0.048917 | -0.018665 | 0.064246 | -61.2854 | 62.3199 | -61.3541 | -61.235 | 62.0682 | 0.086975 | -0.082397 | 0.21515 | 62.2787 | -61.3358 | -0.2243 | 0.082397 | -0.15564 | -0.10528 | -0.16937 | -0.20599 | 0.041199 | 0.068665 | 61.0474 | 61.3449 | 123.1979 | 123.4497 | -0.15564 | 123.4085 | 61.2167 | -0.20599 | 123.4497 | -0.15564 | 61.2167 | 123.1979 | 123.4085 | -123.5916 | -123.5733
109.9219 | 123.5596 | -61.0794 | 62.1597 | -0.24709 | -0.0086402 | -0.0093484 | 0.0023482 | 0.062803 | -0.02187 | 0.077064 | -61.1847 | 62.2696 | -61.3312 | -61.4044 | 61.9675 | -0.027466 | 0.064087 | 0.086975 | 62.2787 | -61.3632 | -0.25177 | 0.10986 | -0.10528 | -0.32501 | -0.19226 | -0.28381 | 0.11902 | 0.14648 | 61.1435 | 61.1664 | 123.0469 | 123.349 | -0.10528 | 123.3582 | 61.0519 | -0.28381 | 123.349 | -0.10528 | 61.0519 | 123.0469 | 123.3582 | -123.4909 | -123.5229
110.9688 | 123.5367 | -61.0977 | 62.1964 | 0.22593 | -0.0043672 | -0.026438 | 0.0034162 | 0.062803 | -0.018665 | 0.06211 | -61.2808 | 62.2696 | -61.3358 | -61.3541 | 62.0178 | -0.018311 | -0.022888 | 0.1236 | 62.2513 | -61.3907 | -0.23804 | 0.073242 | -0.18311 | -0.25635 | -0.17853 | -0.29297 | 0.054932 | 0.054931 | 61.0748 | 61.2213 | 123.1155 | 123.3673 | -0.18311 | 123.349 | 61.0794 | -0.29297 | 123.3673 | -0.18311 | 61.0794 | 123.1155 | 123.349 | -123.5321 | -123.587
111.9219 | 123.4497 | -61.1389 | 62.2375 | -0.41494 | -0.0032992 | 0.0045366 | 0.0087562 | 0.05853 | -0.011188 | 0.057838 | -61.2854 | 62.352 | -61.3953 | -61.2213 | 62.1094 | 0.11902 | -0.1236 | 0.21973 | 62.2284 | -61.3129 | -0.25635 | 0.11444 | -0.14648 | -0.082397 | -0.12817 | -0.17395 | -0.009155 | 0.10986 | 61.0153 | 61.3586 | 123.2483 | 123.4909 | -0.14648 | 123.3673 | 61.2579 | -0.17395 | 123.4909 | -0.14648 | 61.2579 | 123.2483 | 123.3673 | -123.6328 | -123.5504
112.9844 | 123.5641 | -61.084 | 62.2009 | -0.39968 | -0.0011632 | -0.030711 | 0.0044842 | 0.051053 | -0.0090524 | 0.074928 | -60.9558 | 62.3566 | -61.3083 | -61.3495 | 61.9812 | -0.004578 | 0.004578 | 0.10986 | 62.2787 | -61.377 | -0.22431 | 0.15564 | 0.12817 | -0.2655 | -0.21973 | -0.29297 | 0.07782 | 0.35248 | 61.0886 | 61.1938 | 123.0652 | 123.4406 | 0.12817 | 123.3627 | 61.0794 | -0.29297 | 123.4406 | 0.12817 | 61.0794 | 123.0652 | 123.3627 | -123.5092 | -123.5779
113.9219 | 123.468 | -61.1298 | 62.2009 | 0.31749 | -9.5248e-05 | 0.0034686 | 0.015165 | 0.064939 | -0.0069164 | 0.071723 | -61.3358 | 62.3474 | -61.3861 | -61.2396 | 62.1002 | 0.12817 | -0.086975 | 0.2243 | 62.2559 | -61.3174 | -0.25635 | 0.14648 | -0.20599 | -0.10986 | -0.10071 | -0.18768 | 0.054931 | 0.050354 | 61.0428 | 61.3541 | 123.23 | 123.4772 | -0.20599 | 123.3856 | 61.2579 | -0.18768 | 123.4772 | -0.20599 | 61.2579 | 123.23 | 123.3856 | -123.587 | -123.5184
114.9844 | 123.587 | -61.084 | 62.1918 | -0.033467 | -0.0011632 | 0.0066726 | -0.013674 | 0.059598 | -0.028278 | 0.074928 | -61.2213 | 62.2559 | -61.3678 | -61.4548 | 61.9675 | -0.027466 | 0.07782 | 0.064087 | 62.2879 | -61.377 | -0.28381 | 0.064087 | -0.13733 | -0.37079 | -0.2243 | -0.29297 | 0.096131 | 0.14648 | 61.1618 | 61.1481 | 123.0515 | 123.3398 | -0.13733 | 123.3719 | 61.0565 | -0.29297 | 123.3398 | -0.13733 | 61.0565 | 123.0515 | 123.3719 | -123.5596 | -123.5687
115.9219 | 123.4268 | -61.1298 | 62.2238 | -0.46071 | -9.5248e-05 | -0.011485 | 0.010892 | 0.064939 | -0.0090524 | 0.066383 | -61.2625 | 62.3383 | -61.3815 | -61.235 | 62.1277 | 0.13733 | -0.11444 | 0.23346 | 62.2604 | -61.3358 | -0.25177 | 0.11444 | -0.13275 | -0.10528 | -0.09613 | -0.20599 | 0.036621 | 0.11902 | 61.0153 | 61.3632 | 123.2574 | 123.468 | -0.13275 | 123.3902 | 61.2671 | -0.20599 | 123.468 | -0.13275 | 61.2671 | 123.2574 | 123.3902 | -123.6053 | -123.5596
116.9844 | 123.5962 | -61.0611 | 62.1872 | -0.10976 | -0.015048 | -0.015757 | -0.0051288 | 0.052121 | -0.019733 | 0.077064 | -61.171 | 62.2696 | -61.3358 | -61.4594 | 61.9629 | -0.054932 | 0.050354 | 0.082397 | 62.3016 | -61.3586 | -0.27466 | 0.082397 | -0.10986 | -0.39825 | -0.2243 | -0.29755 | 0.11444 | 0.16479 | 61.1114 | 61.1435 | 123.024 | 123.3307 | -0.10986 | 123.3627 | 61.0062 | -0.29755 | 123.3307 | -0.10986 | 61.0062 | 123.024 | 123.3627 | -123.5229 | -123.5458
117.9219 | 123.5001 | -61.084 | 62.2009 | -0.30813 | 0.016995 | -0.026438 | 0.0012792 | 0.055326 | -0.011188 | 0.063178 | -61.203 | 62.3016 | -61.3495 | -61.3495 | 62.0361 | 0.045776 | -0.018311 | 0.15106 | 62.2787 | -61.3541 | -0.2655 | 0.10071 | -0.11902 | -0.2655 | -0.16479 | -0.27008 | 0.07782 | 0.14648 | 61.0657 | 61.235 | 123.1201 | 123.3856 | -0.11902 | 123.3627 | 61.1298 | -0.27008 | 123.3856 | -0.11902 | 61.1298 | 123.1201 | 123.3627 | -123.5504 | -123.555
118.9688 | 123.5275 | -61.0886 | 62.1597 | 0.40904 | -0.0043672 | -0.0018714 | -0.0019248 | 0.056394 | -0.0079844 | 0.073859 | -61.2442 | 62.233 | -61.3861 | -61.4044 | 62.0087 | -0.027466 | 0.032043 | 0.091553 | 62.2513 | -61.3907 | -0.29755 | 0.073242 | -0.15564 | -0.31586 | -0.15106 | -0.30212 | 0.091553 | 0.14191 | 61.1206 | 61.1801 | 123.0972 | 123.3215 | -0.15564 | 123.3398 | 61.0611 | -0.30212 | 123.3215 | -0.15564 | 61.0611 | 123.0972 | 123.3398 | -123.5458 | -123.5504
119.9219 | 123.468 | -61.1389 | 62.1964 | -0.23183 | -9.5248e-05 | -0.010416 | 0.017301 | 0.055326 | -0.0058484 | 0.065314 | -61.2717 | 62.3383 | -61.377 | -61.2305 | 62.1185 | 0.11444 | -0.10986 | 0.21515 | 62.2284 | -61.3312 | -0.23804 | 0.14191 | -0.13275 | -0.091553 | -0.07782 | -0.19226 | 0.032044 | 0.10529 | 61.0291 | 61.3541 | 123.2574 | 123.4772 | -0.13275 | 123.3673 | 61.2534 | -0.19226 | 123.4772 | -0.13275 | 61.2534 | 123.2574 | 123.3673 | -123.5733 | -123.5275
120.9844 | 123.4177 | -61.1023 | 62.2192 | -0.39968 | -0.0032992 | -0.020029 | 0.0098242 | 0.057462 | -0.0015754 | 0.066383 | -61.2625 | 62.3474 | -61.3724 | -61.2946 | 62.0911 | 0.09613 | -0.10071 | 0.17853 | 62.2513 | -61.3449 | -0.27008 | 0.12817 | -0.16022 | -0.19226 | -0.12817 | -0.24262 | 0.032044 | 0.10986 | 61.0016 | 61.2808 | 123.1934 | 123.4497 | -0.16022 | 123.3536 | 61.1984 | -0.24262 | 123.4497 | -0.16022 | 61.1984 | 123.1934 | 123.3536 | -123.5916 | -123.5641
121.9219 | 123.4451 | -61.1069 | 62.233 | -0.50649 | 0.0063138 | -0.024302 | 0.017301 | 0.062803 | -0.00050737 | 0.067451 | -61.2717 | 62.3749 | -61.3541 | -61.2442 | 62.1048 | 0.1236 | -0.10529 | 0.22888 | 62.2559 | -61.3541 | -0.24719 | 0.14191 | -0.16479 | -0.13733 | -0.12817 | -0.24719 | 0.022888 | 0.082398 | 61.0016 | 61.3358 | 123.2117 | 123.4818 | -0.16479 | 123.3627 | 61.2305 | -0.24719 | 123.4818 | -0.16479 | 61.2305 | 123.2117 | 123.3627 | -123.587 | -123.587
122.9844 | 123.4589 | -61.1252 | 62.2147 | -0.46071 | 0.00097275 | -0.018961 | 0.013029 | 0.064939 | -0.0079844 | 0.068519 | -61.3037 | 62.352 | -61.3815 | -61.3129 | 62.1414 | 0.11444 | -0.10529 | 0.24261 | 62.2467 | -61.3174 | -0.25635 | 0.13733 | -0.17853 | -0.18768 | -0.073243 | -0.19226 | 0.032043 | 0.07782 | 61.0199 | 61.3678 | 123.2666 | 123.4772 | -0.17853 | 123.3719 | 61.2396 | -0.19226 | 123.4772 | -0.17853 | 61.2396 | 123.2666 | 123.3719 | -123.5962 | -123.5321
123.9219 | 123.4131 | -61.1526 | 62.2101 | -0.4302 | 0.0020408 | -0.0040084 | 0.019437 | 0.073484 | -0.00050737 | 0.063178 | -61.2946 | 62.3749 | -61.3495 | -61.2625 | 62.1231 | 0.13733 | -0.24261 | 0.32044 | 62.2833 | -61.3083 | -0.19684 | 0.1648 | -0.14191 | -0.10986 | -0.086975 | -0.15564 | 0.073242 | 0.054931 | 60.91 | 61.4731 | 123.2758 | 123.5275 | -0.14191 | 123.436 | 61.29 | -0.15564 | 123.5275 | -0.14191 | 61.29 | 123.2758 | 123.436 | -123.5596 | -123.5184
124.9844 | 123.5138 | -61.0931 | 62.2101 | -0.3539 | -0.0054352 | -0.011485 | 0.0044842 | 0.064939 | -0.0047804 | 0.073859 | -61.2167 | 62.3199 | -61.3724 | -61.3861 | 62.0316 | 0.022888 | -0.009155 | 0.12817 | 62.3108 | -61.3678 | -0.27923 | 0.10986 | -0.1236 | -0.29297 | -0.17853 | -0.27466 | 0.10071 | 0.15564 | 61.084 | 61.2213 | 123.1247 | 123.4131 | -0.1236 | 123.4039 | 61.116 | -0.27466 | 123.4131 | -0.1236 | 61.116 | 123.1247 | 123.4039 | -123.5825 | -123.5779
125.9219 | 123.468 | -61.1069 | 62.233 | -0.29287 | 0.012723 | -0.017893 | 0.0023482 | 0.061735 | -0.0026434 | 0.068519 | -61.2717 | 62.3795 | -61.3815 | -61.2579 | 62.1094 | 0.11444 | -0.09613 | 0.21515 | 62.2513 | -61.3403 | -0.27466 | 0.14648 | -0.16479 | -0.15106 | -0.1236 | -0.23346 | 0.018311 | 0.10986 | 61.0107 | 61.322 | 123.2162 | 123.4863 | -0.16479 | 123.3582 | 61.2213 | -0.23346 | 123.4863 | -0.16479 | 61.2213 | 123.2162 | 123.3582 | -123.6145 | -123.5733
126.9844 | 123.5229 | -61.1023 | 62.2147 | -0.3539 | -0.012912 | -0.016825 | -0.019015 | 0.056394 | 0.00056063 | 0.059974 | -61.2213 | 62.2925 | -61.3449 | -61.3815 | 62.0178 | 0.022888 | 0.018311 | 0.13733 | 62.3016 | -61.3724 | -0.24262 | 0.077819 | -0.11902 | -0.27924 | -0.19684 | -0.27008 | 0.086975 | 0.1236 | 61.1206 | 61.2396 | 123.1201 | 123.3948 | -0.11902 | 123.4039 | 61.1252 | -0.27008 | 123.3948 | -0.11902 | 61.1252 | 123.1201 | 123.4039 | -123.5596 | -123.587
127.9219 | 123.4726 | -61.116 | 62.2009 | -0.21657 | -0.0032992 | 0.0024006 | 0.014097 | 0.062803 | 0.010174 | 0.067451 | -61.2167 | 62.3932 | -61.3403 | -61.2808 | 62.0636 | 0.064087 | -0.054932 | 0.17395 | 62.233 | -61.3861 | -0.2243 | 0.19226 | -0.10071 | -0.16479 | -0.13733 | -0.27008 | 0.032043 | 0.1236 | 61.0611 | 61.29 | 123.1796 | 123.5092 | -0.10071 | 123.349 | 61.1801 | -0.27008 | 123.5092 | -0.10071 | 61.1801 | 123.1796 | 123.349 | -123.5413 | -123.587
128.9219 | 123.468 | -61.1298 | 62.2192 | -0.20131 | 0.0020408 | 0.0045366 | 0.0098242 | 0.062803 | 0.0026966 | 0.06211 | -61.2167 | 62.3932 | -61.3953 | -61.29 | 62.0636 | 0.064087 | -0.054932 | 0.16937 | 62.2559 | -61.3953 | -0.2655 | 0.17395 | -0.086975 | -0.16022 | -0.15564 | -0.2655 | 0.036621 | 0.17853 | 61.0748 | 61.2991 | 123.1934 | 123.5229 | -0.086975 | 123.3856 | 61.1938 | -0.2655 | 123.5229 | -0.086975 | 61.1938 | 123.1934 | 123.3856 | -123.6145 | -123.6145
129.9844 | 123.5229 | -61.0886 | 62.2101 | -0.36916 | -0.010776 | -0.010416 | -0.01581 | 0.05853 | -0.013325 | 0.058906 | -61.2259 | 62.3199 | -61.3495 | -61.3632 | 62.0453 | 0.045776 | -0.009155 | 0.15564 | 62.2971 | -61.3541 | -0.26093 | 0.10986 | -0.13733 | -0.27466 | -0.16479 | -0.2655 | 0.086975 | 0.1236 | 61.0794 | 61.2442 | 123.1338 | 123.4085 | -0.13733 | 123.3856 | 61.1343 | -0.2655 | 123.4085 | -0.13733 | 61.1343 | 123.1338 | 123.3856 | -123.5596 | -123.5641
130.9219 | 123.5596 | -61.0931 | 62.1368 | 0.39378 | -0.011844 | 0.00026463 | -0.00085683 | 0.05319 | -0.011188 | 0.080268 | -61.2396 | 62.2421 | -61.3861 | -61.4365 | 61.9904 | -0.050354 | 0.045776 | 0.068665 | 62.2559 | -61.3678 | -0.29297 | 0.10529 | -0.14648 | -0.34332 | -0.14648 | -0.27466 | 0.11902 | 0.14648 | 61.1389 | 61.1618 | 123.0835 | 123.3353 | -0.14648 | 123.349 | 61.0428 | -0.27466 | 123.3353 | -0.14648 | 61.0428 | 123.0835 | 123.349 | -123.5229 | -123.5046
131.9688 | 123.5733 | -61.1206 | 62.1735 | -0.10976 | -0.0075722 | -0.031779 | -0.011538 | 0.05853 | -0.0079844 | 0.069587 | -61.2717 | 62.265 | -61.3678 | -61.4136 | 61.9995 | -0.004578 | 0.036621 | 0.09613 | 62.2742 | -61.3586 | -0.24719 | 0.091553 | -0.15106 | -0.29297 | -0.17395 | -0.23804 | 0.10071 | 0.096131 | 61.1572 | 61.2167 | 123.1201 | 123.3856 | -0.15106 | 123.3948 | 61.116 | -0.23804 | 123.3856 | -0.15106 | 61.116 | 123.1201 | 123.3948 | -123.5413 | -123.5321
132.9219 | 123.4543 | -61.1206 | 62.2147 | 0.14964 | 0.0095178 | 0.024831 | 0.014097 | 0.047849 | 0.0037646 | 0.064246 | -61.2488 | 62.3749 | -61.3815 | -61.2396 | 62.1002 | 0.10071 | -0.09613 | 0.21515 | 62.2421 | -61.3495 | -0.26093 | 0.16022 | -0.12817 | -0.11902 | -0.11444 | -0.22888 | 0.027465 | 0.13275 | 61.0245 | 61.3358 | 123.2208 | 123.4955 | -0.12817 | 123.3627 | 61.2213 | -0.22888 | 123.4955 | -0.12817 | 61.2213 | 123.2208 | 123.3627 | -123.5962 | -123.5641
133.9688 | 123.5458 | -61.0931 | 62.178 | -0.10976 | -0.015048 | -0.013621 | -0.012606 | 0.046781 | -0.014393 | 0.077064 | -61.322 | 62.265 | -61.3907 | -61.3724 | 62.0407 | 0.027466 | -0.013733 | 0.12817 | 62.2467 | -61.3678 | -0.29755 | 0.086975 | -0.22888 | -0.27923 | -0.13733 | -0.27466 | 0.068664 | 0.068665 | 61.0794 | 61.2213 | 123.1338 | 123.3582 | -0.22888 | 123.3398 | 61.1206 | -0.27466 | 123.3582 | -0.22888 | 61.1206 | 123.1338 | 123.3398 | -123.5687 | -123.5458
134.9219 | 123.4863 | -61.116 | 62.1964 | 0.027569 | 0.0095178 | -0.0040084 | 0.017301 | 0.052121 | 0.015514 | 0.059974 | -61.2305 | 62.3566 | -61.3724 | -61.2579 | 62.0682 | 0.064087 | -0.064087 | 0.19684 | 62.265 | -61.3953 | -0.25635 | 0.16022 | -0.11444 | -0.14191 | -0.12817 | -0.27924 | 0.068665 | 0.14191 | 61.0519 | 61.3129 | 123.1842 | 123.4726 | -0.11444 | 123.381 | 61.1801 | -0.27924 | 123.4726 | -0.11444 | 61.1801 | 123.1842 | 123.381 | -123.5687 | -123.5916
135.9844 | 123.4589 | -61.1298 | 62.1918 | 0.10386 | 0.0020408 | -0.0018714 | 0.010892 | 0.057462 | 0.010174 | 0.067451 | -61.2579 | 62.3657 | -61.3586 | -61.2671 | 62.0956 | 0.073242 | -0.086975 | 0.19226 | 62.2238 | -61.3724 | -0.22888 | 0.17395 | -0.12817 | -0.13733 | -0.09613 | -0.24261 | 0.032044 | 0.10071 | 61.0428 | 61.322 | 123.2254 | 123.4955 | -0.12817 | 123.3536 | 61.203 | -0.24261 | 123.4955 | -0.12817 | 61.203 | 123.2254 | 123.3536 | -123.5504 | -123.5641
136.9219 | 123.5321 | -61.0931 | 62.1643 | 0.4243 | 0.0041778 | 0.012014 | 0.00021117 | 0.062803 | -0.01012 | 0.0792 | -61.2396 | 62.2742 | -61.3998 | -61.4227 | 62.0087 | -0.050354 | 0.013733 | 0.09613 | 62.2742 | -61.377 | -0.3067 | 0.10986 | -0.14648 | -0.32959 | -0.15564 | -0.28381 | 0.10986 | 0.16022 | 61.1069 | 61.1893 | 123.1018 | 123.3673 | -0.14648 | 123.3673 | 61.0428 | -0.28381 | 123.3673 | -0.14648 | 61.0428 | 123.1018 | 123.3673 | -123.5641 | -123.5413
137.9688 | 123.5001 | -61.0886 | 62.2101 | -0.079243 | -0.0065042 | -0.00080337 | 0.0098242 | 0.061735 | 0.0016286 | 0.071723 | -61.4456 | 62.3154 | -61.4044 | -61.3266 | 62.0453 | 0.050354 | -0.018311 | 0.20142 | 62.2787 | -61.3449 | -0.31586 | 0.10529 | -0.35706 | -0.23804 | -0.16479 | -0.25635 | 0.068665 | -0.041199 | 61.0703 | 61.29 | 123.1338 | 123.4039 | -0.35706 | 123.3673 | 61.1389 | -0.25635 | 123.4039 | -0.35706 | 61.1389 | 123.1338 | 123.3673 | -123.6145 | -123.555
138.9219 | 123.468 | -61.084 | 62.1964 | 0.01231 | 0.0095178 | 0.00026463 | 0.015165 | 0.064939 | 0.0059006 | 0.072791 | -61.2442 | 62.3703 | -61.3953 | -61.2671 | 62.0865 | 0.064087 | -0.064087 | 0.20142 | 62.2467 | -61.3678 | -0.31128 | 0.17395 | -0.16022 | -0.18311 | -0.10986 | -0.28381 | 0.050354 | 0.15106 | 61.0199 | 61.2854 | 123.1705 | 123.4543 | -0.16022 | 123.3307 | 61.1481 | -0.28381 | 123.4543 | -0.16022 | 61.1481 | 123.1705 | 123.3307 | -123.5916 | -123.5641
139.9219 | 123.4451 | -61.1252 | 62.1918 | 0.058086 | -0.0054352 | -0.0040084 | 0.0034162 | 0.056394 | -0.00050737 | 0.084541 | -61.2488 | 62.3749 | -61.3953 | -61.2854 | 62.0865 | 0.07782 | -0.059509 | 0.19226 | 62.2375 | -61.377 | -0.27008 | 0.18311 | -0.1236 | -0.16022 | -0.10529 | -0.25177 | 0.045777 | 0.14648 | 61.0657 | 61.3174 | 123.2117 | 123.5001 | -0.1236 | 123.3627 | 61.203 | -0.25177 | 123.5001 | -0.1236 | 61.203 | 123.2117 | 123.3627 | -123.587 | -123.5687
140.9844 | 123.5596 | -61.084 | 62.1552 | 0.28697 | -0.0075722 | 0.00026463 | -0.0019248 | 0.054258 | -0.0069164 | 0.072791 | -61.2488 | 62.2833 | -61.3724 | -61.441 | 61.9812 | -0.041199 | 0.045776 | 0.07782 | 62.2604 | -61.3861 | -0.28839 | 0.12817 | -0.16479 | -0.35706 | -0.17395 | -0.30212 | 0.10529 | 0.1236 | 61.1298 | 61.1618 | 123.0652 | 123.3673 | -0.16479 | 123.3444 | 61.0428 | -0.30212 | 123.3673 | -0.16479 | 61.0428 | 123.0652 | 123.3444 | -123.5275 | -123.5413
141.9219 | 123.4314 | -61.171 | 62.2055 | 0.24119 | 0.0073818 | 0.0088096 | 0.0055522 | 0.066007 | 0.01231 | 0.070655 | -61.2808 | 62.3978 | -61.3632 | -61.235 | 62.1323 | 0.10986 | -0.10529 | 0.23346 | 62.2238 | -61.3495 | -0.19226 | 0.19226 | -0.10986 | -0.064087 | -0.073242 | -0.17853 | 0.018311 | 0.082397 | 61.0657 | 61.4044 | 123.3032 | 123.5687 | -0.10986 | 123.3948 | 61.2808 | -0.17853 | 123.5687 | -0.10986 | 61.2808 | 123.3032 | 123.3948 | -123.5687 | -123.555
142.9844 | 123.3765 | -61.1801 | 62.1735 | -0.018208 | 0.010586 | 0.026968 | 0.011961 | 0.068143 | 0.0091056 | 0.0792 | -61.3449 | 62.3611 | -61.4273 | -61.2396 | 62.1414 | 0.11902 | -0.11902 | 0.22888 | 62.2559 | -61.3678 | -0.24719 | 0.18768 | -0.16479 | -0.059509 | -0.032044 | -0.18768 | 0.082397 | 0.082397 | 61.0611 | 61.409 | 123.3215 | 123.5413 | -0.16479 | 123.436 | 61.2991 | -0.18768 | 123.5413 | -0.16479 | 61.2991 | 123.3215 | 123.436 | -123.6008 | -123.5413
143.9219 | 123.4772 | -61.1389 | 62.2192 | -0.0029495 | 0.011654 | 0.0045366 | 0.011961 | 0.066007 | 0.015514 | 0.070655 | -61.2488 | 62.4023 | -61.3724 | -61.2854 | 62.0956 | 0.086975 | -0.07782 | 0.18768 | 62.2742 | -61.377 | -0.23346 | 0.18311 | -0.10986 | -0.14648 | -0.1236 | -0.23804 | 0.054932 | 0.1236 | 61.0611 | 61.3266 | 123.2346 | 123.5413 | -0.10986 | 123.4131 | 61.2259 | -0.23804 | 123.5413 | -0.10986 | 61.2259 | 123.2346 | 123.4131 | -123.5916 | -123.5962
144.9844 | 123.5046 | -61.1069 | 62.178 | -0.12502 | -9.5248e-05 | -0.016825 | 0.017301 | 0.066007 | 0.0016286 | 0.064246 | -61.2534 | 62.4161 | -61.3495 | -61.2991 | 62.0682 | 0.064087 | -0.045776 | 0.17395 | 62.2513 | -61.3907 | -0.24261 | 0.23804 | -0.14648 | -0.19226 | -0.10986 | -0.28381 | 0.073242 | 0.09613 | 61.0611 | 61.2808 | 123.175 | 123.523 | -0.14648 | 123.3582 | 61.171 | -0.28381 | 123.523 | -0.14648 | 61.171 | 123.175 | 123.3582 | -123.5275 | -123.5687
145.9219 | 123.5184 | -61.0931 | 62.1552 | 0.39378 | 0.0020408 | -0.0072124 | -0.011538 | 0.059598 | 0.0026966 | 0.078132 | -61.235 | 62.3062 | -61.3632 | -61.4136 | 62.0132 | -0.013733 | 0.009155 | 0.10986 | 62.2879 | -61.4044 | -0.27008 | 0.15106 | -0.14191 | -0.32043 | -0.14191 | -0.31128 | 0.13275 | 0.12817 | 61.1023 | 61.203 | 123.1064 | 123.3994 | -0.14191 | 123.381 | 61.0794 | -0.31128 | 123.3994 | -0.14191 | 61.0794 | 123.1064 | 123.381 | -123.5184 | -123.5596
146.9844 | 123.4818 | -61.1298 | 62.2055 | -0.18605 | 0.0041778 | 0.013082 | 0.015165 | 0.064939 | 0.013378 | 0.068519 | -61.2076 | 62.3978 | -61.3907 | -61.2991 | 62.059 | 0.064087 | -0.050354 | 0.1831 | 62.2513 | -61.377 | -0.26093 | 0.19226 | -0.07782 | -0.16937 | -0.14648 | -0.24719 | 0.045777 | 0.18311 | 61.0794 | 61.3129 | 123.1888 | 123.5275 | -0.07782 | 123.381 | 61.1938 | -0.24719 | 123.5275 | -0.07782 | 61.1938 | 123.1888 | 123.381 | -123.5962 | -123.5825
147.9219 | 123.5001 | -61.1298 | 62.1689 | 0.43956 | -9.5248e-05 | 0.0077416 | 0.0087562 | 0.063871 | 0.0026966 | 0.067451 | -61.3037 | 62.3474 | -61.409 | -61.3266 | 62.059 | 0.027466 | -0.041199 | 0.15106 | 62.2787 | -61.3815 | -0.27924 | 0.17853 | -0.17395 | -0.19684 | -0.10986 | -0.25177 | 0.10986 | 0.10529 | 61.0886 | 61.2808 | 123.1888 | 123.4772 | -0.17395 | 123.4085 | 61.1572 | -0.25177 | 123.4772 | -0.17395 | 61.1572 | 123.1888 | 123.4085 | -123.5779 | -123.5504
148.9844 | 123.4634 | -61.116 | 62.2009 | 0.058086 | 0.012723 | -0.013621 | 0.00021117 | 0.064939 | 0.010174 | 0.061042 | -61.203 | 62.3932 | -61.3586 | -61.3129 | 62.059 | 0.064087 | -0.041199 | 0.17395 | 62.2513 | -61.3678 | -0.24262 | 0.19226 | -0.086975 | -0.19684 | -0.14191 | -0.25177 | 0.050354 | 0.15564 | 61.0748 | 61.29 | 123.175 | 123.5092 | -0.086975 | 123.3673 | 61.1801 | -0.25177 | 123.5092 | -0.086975 | 61.1801 | 123.175 | 123.3673 | -123.5596 | -123.5687
149.9219 | 123.4543 | -61.1481 | 62.1826 | -1.1626 | 0.0073818 | -0.015757 | 0.0076882 | 0.062803 | 0.0069696 | 0.073859 | -61.3586 | 62.3703 | -61.4136 | -61.2808 | 62.1094 | 0.073242 | -0.11444 | 0.21973 | 62.2467 | -61.3815 | -0.2655 | 0.18768 | -0.21057 | -0.13275 | -0.073242 | -0.23346 | 0.064087 | 0.054931 | 61.0336 | 61.3678 | 123.2574 | 123.5184 | -0.21057 | 123.3948 | 61.2213 | -0.23346 | 123.5184 | -0.21057 | 61.2213 | 123.2574 | 123.3948 | -123.5962 | -123.5641
150.9844 | 123.4818 | -61.1298 | 62.1735 | 0.30223 | 0.0095178 | -0.0093484 | -0.00085683 | 0.062803 | -0.0026434 | 0.061042 | -61.2991 | 62.3337 | -61.3861 | -61.3037 | 62.0956 | 0.068665 | -0.082397 | 0.19226 | 62.2467 | -61.3815 | -0.25635 | 0.16022 | -0.16937 | -0.17395 | -0.07782 | -0.25177 | 0.073242 | 0.086975 | 61.0474 | 61.322 | 123.2254 | 123.4634 | -0.16937 | 123.3765 | 61.1984 | -0.25177 | 123.4634 | -0.16937 | 61.1984 | 123.2254 | 123.3765 | -123.5596 | -123.555
151.9219 | 123.4543 | -61.1435 | 62.1964 | 0.40904 | 0.0084498 | 0.00026463 | 0.0066202 | 0.068143 | 0.00056063 | 0.072791 | -61.3037 | 62.3566 | -61.409 | -61.2808 | 62.114 | 0.082397 | -0.10529 | 0.2243 | 62.2192 | -61.3861 | -0.2655 | 0.16022 | -0.16022 | -0.13733 | -0.082397 | -0.24261 | 0.022888 | 0.10529 | 61.0382 | 61.3678 | 123.2574 | 123.5001 | -0.16022 | 123.3627 | 61.2259 | -0.24261 | 123.5001 | -0.16022 | 61.2259 | 123.2574 | 123.3627 | -123.6053 | -123.5825
152.9844 | 123.5046 | -61.1389 | 62.1735 | 0.4243 | 0.0063138 | 0.012014 | -0.0019248 | 0.067075 | 0.014446 | 0.067451 | -61.3083 | 62.384 | -61.3861 | -61.322 | 62.0911 | 0.050354 | -0.064087 | 0.1831 | 62.2604 | -61.377 | -0.24719 | 0.21057 | -0.16937 | -0.1831 | -0.082398 | -0.23804 | 0.086975 | 0.077819 | 61.0748 | 61.322 | 123.23 | 123.5229 | -0.16937 | 123.3994 | 61.1893 | -0.23804 | 123.5229 | -0.16937 | 61.1893 | 123.23 | 123.3994 | -123.5596 | -123.5504
153.9219 | 123.4909 | -61.1206 | 62.1735 | 0.22593 | -0.0022312 | -0.0072124 | 0.0087562 | 0.054258 | 0.0016286 | 0.074928 | -61.3312 | 62.3657 | -61.4227 | -61.2946 | 62.1048 | 0.073242 | -0.091553 | 0.20142 | 62.2604 | -61.3998 | -0.30212 | 0.19226 | -0.21057 | -0.17395 | -0.068665 | -0.27924 | 0.086975 | 0.091552 | 61.0291 | 61.322 | 123.2254 | 123.4863 | -0.21057 | 123.381 | 61.1938 | -0.27924 | 123.4863 | -0.21057 | 61.1938 | 123.2254 | 123.381 | -123.5962 | -123.5733
154.9844 | 123.4955 | -61.1298 | 62.2238 | -0.29287 | 0.015927 | -0.011485 | 0.00021117 | 0.056394 | 0.0080376 | 0.067451 | -61.2396 | 62.3978 | -61.3815 | -61.2991 | 62.0636 | 0.07782 | -0.073242 | 0.19226 | 62.2742 | -61.3953 | -0.25177 | 0.17395 | -0.10986 | -0.16937 | -0.16022 | -0.2655 | 0.050354 | 0.14191 | 61.0565 | 61.322 | 123.1934 | 123.5275 | -0.10986 | 123.4039 | 61.2076 | -0.2655 | 123.5275 | -0.10986 | 61.2076 | 123.1934 | 123.4039 | -123.6053 | -123.6191
155.9219 | 123.5413 | -61.1069 | 62.178 | 0.36326 | -0.010776 | -0.0029404 | -0.013674 | 0.063871 | -0.020801 | 0.074928 | -61.2946 | 62.2833 | -61.3953 | -61.3998 | 61.9995 | -0.004578 | -0.013733 | 0.13733 | 62.2787 | -61.377 | -0.28839 | 0.10528 | -0.18768 | -0.29297 | -0.17853 | -0.27008 | 0.10071 | 0.10071 | 61.0931 | 61.2442 | 123.1064 | 123.3902 | -0.18768 | 123.3856 | 61.1023 | -0.27008 | 123.3902 | -0.18768 | 61.1023 | 123.1064 | 123.3856 | -123.5733 | -123.555
156.9844 | 123.5138 | -61.1114 | 62.178 | 0.51585 | -0.0011632 | -0.013621 | 0.0066202 | 0.052121 | 0.0059006 | 0.064246 | -61.2991 | 62.2971 | -61.3907 | -61.3403 | 62.0407 | 0.013733 | -0.036621 | 0.15106 | 62.2284 | -61.3953 | -0.27924 | 0.11902 | -0.18768 | -0.22888 | -0.13733 | -0.28381 | 0.050354 | 0.091553 | 61.0748 | 61.2625 | 123.1522 | 123.4085 | -0.18768 | 123.3398 | 61.1252 | -0.28381 | 123.4085 | -0.18768 | 61.1252 | 123.1522 | 123.3398 | -123.5687 | -123.5733
157.9219 | 123.5687 | -61.1023 | 62.146 | 0.13438 | 0.0041778 | -0.0050764 | -0.0040608 | 0.05319 | -0.0047804 | 0.066383 | -61.2259 | 62.3291 | -61.3632 | -61.4136 | 61.9766 | -0.068665 | 0.041199 | 0.059509 | 62.2833 | -61.3953 | -0.26093 | 0.18311 | -0.1236 | -0.31128 | -0.16937 | -0.29297 | 0.13733 | 0.13733 | 61.1435 | 61.1618 | 123.0789 | 123.4314 | -0.1236 | 123.3856 | 61.0336 | -0.29297 | 123.4314 | -0.1236 | 61.0336 | 123.0789 | 123.3856 | -123.5092 | -123.5413
158.9844 | 123.4314 | -61.1481 | 62.2238 | 0.25645 | 0.010586 | -0.011485 | 0.0076882 | 0.066007 | 0.0059006 | 0.066383 | -61.3083 | 62.3749 | -61.3861 | -61.2167 | 62.1323 | 0.086975 | -0.10986 | 0.22888 | 62.233 | -61.3678 | -0.23804 | 0.15106 | -0.16022 | -0.068665 | -0.091553 | -0.21973 | 0.009155 | 0.077819 | 61.0382 | 61.377 | 123.2803 | 123.5229 | -0.16022 | 123.381 | 61.235 | -0.21973 | 123.5229 | -0.16022 | 61.235 | 123.2803 | 123.381 | -123.6099 | -123.5916
159.9219 | 123.5641 | -61.084 | 62.1643 | -0.10976 | -0.0054352 | -0.022166 | -0.016879 | 0.052121 | -0.01012 | 0.071723 | -61.2488 | 62.2833 | -61.3861 | -61.4182 | 61.9904 | -0.050354 | 0.050354 | 0.082397 | 62.2833 | -61.4044 | -0.30212 | 0.11902 | -0.16479 | -0.33417 | -0.17395 | -0.32043 | 0.11902 | 0.13733 | 61.1343 | 61.1664 | 123.0743 | 123.3673 | -0.16479 | 123.3673 | 61.0336 | -0.32043 | 123.3673 | -0.16479 | 61.0336 | 123.0743 | 123.3673 | -123.5504 | -123.5687
160.9844 | 123.5413 | -61.1572 | 62.1552 | 0.36326 | 0.0095178 | 0.0066726 | 0.019437 | 0.057462 | 0.016583 | 0.069587 | -61.3358 | 62.352 | -61.4044 | -61.2534 | 62.0956 | 0.09613 | -0.11902 | 0.24261 | 62.2513 | -61.3861 | -0.24719 | 0.19684 | -0.17853 | -0.09613 | -0.059509 | -0.22888 | 0.096131 | 0.068665 | 61.0382 | 61.3998 | 123.2529 | 123.5092 | -0.17853 | 123.4085 | 61.2534 | -0.22888 | 123.5092 | -0.17853 | 61.2534 | 123.2529 | 123.4085 | -123.5596 | -123.5413
161.9219 | 123.5184 | -61.0977 | 62.1552 | 0.348 | -0.0065042 | -0.018961 | -0.011538 | 0.060666 | -0.0069164 | 0.064246 | -61.2991 | 62.2787 | -61.4044 | -61.4044 | 62.0178 | 0 | 0.027466 | 0.12817 | 62.2833 | -61.3953 | -0.3067 | 0.1236 | -0.20142 | -0.3067 | -0.13733 | -0.29755 | 0.12817 | 0.10529 | 61.1252 | 61.2259 | 123.1155 | 123.3765 | -0.20142 | 123.381 | 61.0977 | -0.29755 | 123.3765 | -0.20142 | 61.0977 | 123.1155 | 123.381 | -123.5596 | -123.5504
162.9844 | 123.5596 | -61.1023 | 62.1643 | 0.45481 | 0.0041778 | 0.0056046 | -0.0029928 | 0.051053 | 0.0016286 | 0.061042 | -61.2213 | 62.2879 | -61.3861 | -61.4639 | 61.9812 | -0.045776 | 0.027466 | 0.09613 | 62.2787 | -61.441 | -0.28381 | 0.1236 | -0.11902 | -0.36163 | -0.18311 | -0.33875 | 0.11444 | 0.16479 | 61.1298 | 61.1984 | 123.0835 | 123.3902 | -0.11902 | 123.381 | 61.0565 | -0.33875 | 123.3902 | -0.11902 | 61.0565 | 123.0835 | 123.381 | -123.5504 | -123.6053
163.9219 | 123.4955 | -61.1069 | 62.1689 | 0.21067 | -0.0043672 | -0.017893 | -0.0061968 | 0.051053 | -0.0015754 | 0.0792 | -61.2808 | 62.265 | -61.3724 | -61.409 | 61.9995 | -0.009155 | 0.004578 | 0.11444 | 62.2742 | -61.4044 | -0.2655 | 0.096131 | -0.17395 | -0.30212 | -0.16937 | -0.29755 | 0.10529 | 0.091552 | 61.1115 | 61.2213 | 123.1064 | 123.3719 | -0.17395 | 123.381 | 61.0977 | -0.29755 | 123.3719 | -0.17395 | 61.0977 | 123.1064 | 123.381 | -123.5413 | -123.5733
164.9844 | 123.4314 | -61.1298 | 62.1918 | 0.18016 | 0.0073818 | -0.013621 | 0.021574 | 0.05853 | 0.011242 | 0.069587 | -61.2991 | 62.4069 | -61.4182 | -61.2213 | 62.1094 | 0.10986 | -0.14648 | 0.22888 | 62.2238 | -61.3907 | -0.28839 | 0.21515 | -0.16937 | -0.091552 | -0.082397 | -0.26093 | 0.032044 | 0.11902 | 60.9833 | 61.3586 | 123.2391 | 123.5367 | -0.16937 | 123.3536 | 61.2396 | -0.26093 | 123.5367 | -0.16937 | 61.2396 | 123.2391 | 123.3536 | -123.6099 | -123.5825
165.9219 | 123.5046 | -61.1069 | 62.1506 | 0.30223 | 0.0041778 | -0.015757 | -0.0040608 | 0.051053 | -0.019733 | 0.071723 | -61.2579 | 62.2559 | -61.3953 | -61.4227 | 61.9995 | -0.054932 | 0.045776 | 0.086975 | 62.2787 | -61.4136 | -0.28839 | 0.10529 | -0.15106 | -0.31586 | -0.15106 | -0.3067 | 0.12817 | 0.13733 | 61.1526 | 61.1938 | 123.1064 | 123.3627 | -0.15106 | 123.3856 | 61.0519 | -0.3067 | 123.3627 | -0.15106 | 61.0519 | 123.1064 | 123.3856 | -123.5458 | -123.5641
166.9844 | 123.5367 | -61.0611 | 62.1689 | 1.2025 | -0.0022312 | -0.02537 | -0.0051288 | 0.051053 | -0.0079844 | 0.064246 | -61.1847 | 62.2925 | -61.3586 | -61.4594 | 61.9583 | -0.07782 | 0.054932 | 0.086975 | 62.2971 | -61.4273 | -0.29755 | 0.1236 | -0.1236 | -0.39825 | -0.21057 | -0.36621 | 0.12817 | 0.17395 | 61.116 | 61.1481 | 123.0194 | 123.3536 | -0.1236 | 123.3582 | 60.9833 | -0.36621 | 123.3536 | -0.1236 | 60.9833 | 123.0194 | 123.3582 | -123.5275 | -123.5962
167.9219 | 123.5275 | -61.0977 | 62.2147 | -1.01 | -0.011844 | -0.017893 | -0.017947 | 0.044645 | -0.0090524 | 0.066383 | -61.3358 | 62.2925 | -61.3678 | -61.3998 | 62.0041 | -0.018311 | -0.013733 | 0.13733 | 62.2696 | -61.3907 | -0.27008 | 0.077819 | -0.23804 | -0.30212 | -0.21057 | -0.29297 | 0.054931 | 0.032044 | 61.084 | 61.235 | 123.1018 | 123.3902 | -0.23804 | 123.3673 | 61.0794 | -0.29297 | 123.3902 | -0.23804 | 61.0794 | 123.1018 | 123.3673 | -123.5825 | -123.6053
168.9844 | 123.5641 | -61.084 | 62.1643 | 0.45481 | -0.0086402 | -0.0072124 | 0.00021117 | 0.049985 | -0.00050737 | 0.063178 | -61.2259 | 62.3108 | -61.3403 | -61.4182 | 61.9766 | -0.068665 | 0.041199 | 0.054932 | 62.265 | -61.4227 | -0.25635 | 0.14648 | -0.14191 | -0.33417 | -0.18768 | -0.33874 | 0.10071 | 0.11444 | 61.1252 | 61.1389 | 123.0606 | 123.3948 | -0.14191 | 123.349 | 61.0153 | -0.33874 | 123.3948 | -0.14191 | 61.0153 | 123.0606 | 123.349 | -123.5046 | -123.587
169.9219 | 123.5458 | -61.0931 | 62.1643 | -0.30813 | -0.0054352 | -0.036051 | -0.0019248 | 0.048917 | -0.015461 | 0.078132 | -61.2534 | 62.3062 | -61.3861 | -61.3998 | 62.0178 | 0 | 0.009155 | 0.13733 | 62.2787 | -61.3724 | -0.29297 | 0.14191 | -0.16022 | -0.3067 | -0.14648 | -0.27923 | 0.11444 | 0.13275 | 61.1023 | 61.2305 | 123.111 | 123.3994 | -0.16022 | 123.3719 | 61.0931 | -0.27923 | 123.3994 | -0.16022 | 61.0931 | 123.111 | 123.3719 | -123.5504 | -123.5367
170.9844 | 123.5367 | -61.1023 | 62.1826 | 0.6074 | -0.0065042 | -0.032847 | -0.01581 | 0.047849 | -0.0058484 | 0.070655 | -61.2488 | 62.2696 | -61.4182 | -61.4182 | 61.972 | -0.059509 | 0.050354 | 0.07782 | 62.2787 | -61.4319 | -0.31586 | 0.086975 | -0.14648 | -0.31586 | -0.21057 | -0.32959 | 0.096131 | 0.16937 | 61.1526 | 61.1801 | 123.0743 | 123.3719 | -0.14648 | 123.381 | 61.0428 | -0.32959 | 123.3719 | -0.14648 | 61.0428 | 123.0743 | 123.381 | -123.6008 | -123.6145
171.9219 | 123.5184 | -61.084 | 62.1735 | 0.27171 | -0.0032992 | -0.020029 | -0.0019248 | 0.047849 | -0.013325 | 0.063178 | -61.2717 | 62.2971 | -61.3861 | -61.3815 | 62.0041 | 0.004578 | 0.009155 | 0.12817 | 62.2742 | -61.3861 | -0.30212 | 0.1236 | -0.18768 | -0.29755 | -0.16937 | -0.30212 | 0.10071 | 0.11444 | 61.0931 | 61.2122 | 123.0881 | 123.381 | -0.18768 | 123.3582 | 61.0886 | -0.30212 | 123.381 | -0.18768 | 61.0886 | 123.0881 | 123.3582 | -123.5596 | -123.5596
172.9844 | 123.5413 | -61.116 | 62.1918 | 0.30223 | -0.012912 | -0.011485 | -0.0094018 | 0.049985 | 0.0037646 | 0.057838 | -61.2579 | 62.2787 | -61.3495 | -61.3815 | 61.9995 | -0.018311 | -0.009155 | 0.1236 | 62.2833 | -61.4044 | -0.23346 | 0.086976 | -0.14191 | -0.2655 | -0.19226 | -0.28839 | 0.091553 | 0.091552 | 61.1069 | 61.2396 | 123.1155 | 123.3948 | -0.14191 | 123.3994 | 61.0977 | -0.28839 | 123.3948 | -0.14191 | 61.0977 | 123.1155 | 123.3994 | -123.5413 | -123.5962
173.9219 | 123.5825 | -61.0703 | 62.2055 | -0.094502 | -0.0086402 | -0.014689 | 0.00021117 | 0.05319 | -0.018665 | 0.061042 | -61.2305 | 62.2742 | -61.3907 | -61.409 | 61.9629 | -0.027466 | 0.054932 | 0.073242 | 62.3016 | -61.3724 | -0.32044 | 0.068665 | -0.16022 | -0.33875 | -0.24261 | -0.30212 | 0.096131 | 0.16022 | 61.1252 | 61.1435 | 123.0331 | 123.3444 | -0.16022 | 123.3719 | 61.0428 | -0.30212 | 123.3444 | -0.16022 | 61.0428 | 123.0331 | 123.3719 | -123.5962 | -123.5779
174.9844 | 123.4222 | -61.1343 | 62.2238 | 0.31749 | -9.5248e-05 | 0.0024006 | 0.033323 | 0.051053 | 0.0026966 | 0.066383 | -61.3037 | 62.3657 | -61.4227 | -61.1893 | 62.1323 | 0.082397 | -0.11902 | 0.2243 | 62.2421 | -61.377 | -0.28839 | 0.14191 | -0.16937 | -0.054932 | -0.091553 | -0.24262 | 0.01831 | 0.11902 | 61.0153 | 61.3586 | 123.2666 | 123.5001 | -0.16937 | 123.3765 | 61.2167 | -0.24262 | 123.5001 | -0.16937 | 61.2167 | 123.2666 | 123.3765 | -123.6465 | -123.6008
175.9219 | 123.555 | -61.0748 | 62.1643 | -0.018208 | -0.01398 | -0.02537 | -0.01047 | 0.049985 | -0.013325 | 0.065314 | -61.2488 | 62.2787 | -61.3724 | -61.4136 | 61.9858 | -0.045776 | 0.036621 | 0.086975 | 62.3245 | -61.3586 | -0.29755 | 0.11444 | -0.17395 | -0.33874 | -0.17853 | -0.28381 | 0.16022 | 0.1236 | 61.1114 | 61.1618 | 123.0606 | 123.3536 | -0.17395 | 123.3994 | 61.0291 | -0.28381 | 123.3536 | -0.17395 | 61.0291 | 123.0606 | 123.3994 | -123.5367 | -123.523
176.9844 | 123.5275 | -61.1069 | 62.1872 | 0.30223 | -0.0075722 | -0.013621 | -0.0051288 | 0.056394 | -0.025074 | 0.068519 | -61.2808 | 62.2742 | -61.3724 | -61.3907 | 62.027 | -0.027466 | 0.004578 | 0.11902 | 62.2925 | -61.4044 | -0.2655 | 0.086975 | -0.17395 | -0.28381 | -0.16022 | -0.29755 | 0.10528 | 0.091552 | 61.1115 | 61.2259 | 123.1339 | 123.381 | -0.17395 | 123.3994 | 61.0794 | -0.29755 | 123.381 | -0.17395 | 61.0794 | 123.1339 | 123.3994 | -123.5596 | -123.5916
177.9219 | 123.5596 | -61.084 | 62.1964 | -0.048725 | -0.0054352 | -0.014689 | -0.01047 | 0.042508 | -0.018665 | 0.077064 | -61.2305 | 62.2696 | -61.377 | -61.409 | 61.9812 | -0.032043 | 0.036621 | 0.086975 | 62.2971 | -61.377 | -0.29297 | 0.073242 | -0.14648 | -0.32501 | -0.21515 | -0.29297 | 0.10071 | 0.14648 | 61.1206 | 61.171 | 123.0652 | 123.3536 | -0.14648 | 123.381 | 61.0519 | -0.29297 | 123.3536 | -0.14648 | 61.0519 | 123.0652 | 123.381 | -123.5733 | -123.5733
178.9844 | 123.5733 | -61.0886 | 62.1735 | 1.3093 | -0.012912 | -0.028574 | 0.0023482 | 0.038236 | -0.016529 | 0.061042 | -61.1755 | 62.2742 | -61.377 | -61.4227 | 61.9675 | -0.068665 | 0.054932 | 0.068665 | 62.2833 | -61.4044 | -0.28839 | 0.10071 | -0.086975 | -0.33417 | -0.20599 | -0.31586 | 0.10986 | 0.20142 | 61.1435 | 61.1572 | 123.056 | 123.3627 | -0.086975 | 123.3719 | 61.0199 | -0.31586 | 123.3627 | -0.086975 | 61.0199 | 123.056 | 123.3719 | -123.5504 | -123.5779
179.9219 | 123.5641 | -61.0657 | 62.1826 | 0.01231 | -0.012912 | -0.0082804 | -0.0061968 | 0.043577 | -0.019733 | 0.068519 | -61.2579 | 62.2742 | -61.3449 | -61.4182 | 61.9812 | -0.036621 | 0.036621 | 0.086975 | 62.2604 | -61.3861 | -0.27924 | 0.091553 | -0.19226 | -0.35248 | -0.20142 | -0.32043 | 0.07782 | 0.086975 | 61.1023 | 61.1526 | 123.0469 | 123.3398 | -0.19226 | 123.3261 | 61.0291 | -0.32043 | 123.3398 | -0.19226 | 61.0291 | 123.0469 | 123.3261 | -123.5275 | -123.5687
180.9688 | 123.5687 | -61.084 | 62.1643 | 0.43956 | -0.0011632 | -0.011485 | 0.014097 | 0.056394 | 0.0069696 | 0.074928 | -61.2167 | 62.2925 | -61.3815 | -61.3632 | 61.9995 | -0.045776 | 0.022888 | 0.082397 | 62.2421 | -61.4182 | -0.29755 | 0.12817 | -0.13275 | -0.27924 | -0.16479 | -0.33417 | 0.077819 | 0.1648 | 61.1069 | 61.1664 | 123.0835 | 123.3765 | -0.13275 | 123.3261 | 61.0382 | -0.33417 | 123.3765 | -0.13275 | 61.0382 | 123.0835 | 123.3261 | -123.5458 | -123.5825
181.9219 | 123.5413 | -61.084 | 62.1826 | -0.094502 | -0.011844 | -0.013621 | -0.0040608 | 0.057462 | -0.024006 | 0.075996 | -61.2579 | 62.2925 | -61.3724 | -61.3953 | 62.0132 | -0.022888 | 0.032043 | 0.091553 | 62.3154 | -61.3678 | -0.28839 | 0.10986 | -0.17395 | -0.31128 | -0.16937 | -0.28381 | 0.13275 | 0.11444 | 61.116 | 61.1755 | 123.0972 | 123.3765 | -0.17395 | 123.3994 | 61.0611 | -0.28381 | 123.3765 | -0.17395 | 61.0611 | 123.0972 | 123.3994 | -123.555 | -123.5504
182.9844 | 123.5138 | -61.0886 | 62.1918 | -0.10976 | -0.0032992 | -0.0050764 | 0.0023482 | 0.045713 | -0.026142 | 0.072791 | -61.2396 | 62.2925 | -61.3586 | -61.3998 | 62.0178 | 0.009155 | 0.004578 | 0.13275 | 62.2742 | -61.377 | -0.27008 | 0.10071 | -0.15106 | -0.31128 | -0.17395 | -0.28839 | 0.082398 | 0.11902 | 61.0931 | 61.2213 | 123.1064 | 123.381 | -0.15106 | 123.3627 | 61.0977 | -0.28839 | 123.381 | -0.15106 | 61.0977 | 123.1064 | 123.3627 | -123.5504 | -123.5687
183.9219 | 123.6008 | -61.0886 | 62.2009 | -0.24709 | -0.0097082 | -0.024302 | 0.0044842 | 0.056394 | -0.019733 | 0.077064 | -61.1801 | 62.2742 | -61.3541 | -61.4319 | 61.9492 | -0.041199 | 0.059509 | 0.073242 | 62.2879 | -61.3815 | -0.2655 | 0.073242 | -0.091553 | -0.34332 | -0.25177 | -0.29297 | 0.086975 | 0.17395 | 61.1481 | 61.1618 | 123.0377 | 123.3627 | -0.091553 | 123.3765 | 61.0474 | -0.29297 | 123.3627 | -0.091553 | 61.0474 | 123.0377 | 123.3765 | -123.555 | -123.5825
184.9844 | 123.5229 | -61.0794 | 62.1597 | 0.31749 | 0.00097275 | -0.017893 | 0.0034162 | 0.048917 | -0.014393 | 0.065314 | -61.2442 | 62.2787 | -61.3632 | -61.3724 | 61.9995 | -0.032043 | 0.013733 | 0.10986 | 62.2421 | -61.3998 | -0.28381 | 0.11902 | -0.16479 | -0.29297 | -0.16022 | -0.32043 | 0.082397 | 0.11902 | 61.0931 | 61.1893 | 123.0789 | 123.3582 | -0.16479 | 123.3215 | 61.0474 | -0.32043 | 123.3582 | -0.16479 | 61.0474 | 123.0789 | 123.3215 | -123.5229 | -123.5596
185.9219 | 123.5779 | -61.0886 | 62.1964 | 0.01231 | -0.012912 | 0.0045366 | -0.012606 | 0.037168 | -0.019733 | 0.068519 | -61.2625 | 62.265 | -61.3861 | -61.3953 | 61.9904 | -0.018311 | 0.013733 | 0.09613 | 62.2696 | -61.3815 | -0.29755 | 0.068665 | -0.17395 | -0.3067 | -0.20599 | -0.29297 | 0.073242 | 0.1236 | 61.1023 | 61.1847 | 123.0789 | 123.3536 | -0.17395 | 123.3582 | 61.0703 | -0.29297 | 123.3536 | -0.17395 | 61.0703 | 123.0789 | 123.3582 | -123.5825 | -123.5779
186.9844 | 123.5001 | -61.1069 | 62.1826 | 0.11912 | -0.0075722 | -0.013621 | -0.0029928 | 0.046781 | -0.011188 | 0.063178 | -61.2854 | 62.2604 | -61.3678 | -61.377 | 62.0224 | -0.004578 | -0.009155 | 0.12817 | 62.265 | -61.4044 | -0.26093 | 0.07782 | -0.17853 | -0.27008 | -0.16022 | -0.29755 | 0.082398 | 0.082398 | 61.0977 | 61.235 | 123.1293 | 123.3673 | -0.17853 | 123.3719 | 61.1023 | -0.29755 | 123.3673 | -0.17853 | 61.1023 | 123.1293 | 123.3719 | -123.5504 | -123.587
187.9219 | 123.5825 | -61.0703 | 62.1826 | -0.21657 | -0.0022312 | -0.030711 | -0.0051288 | 0.038236 | -0.0090524 | 0.072791 | -61.2122 | 62.2742 | -61.3724 | -61.3907 | 61.9308 | -0.059509 | 0.09613 | 0.050354 | 62.3199 | -61.3815 | -0.30212 | 0.091553 | -0.14191 | -0.32044 | -0.25177 | -0.31128 | 0.13733 | 0.16022 | 61.1664 | 61.1206 | 123.0011 | 123.3444 | -0.14191 | 123.3902 | 61.0107 | -0.31128 | 123.3444 | -0.14191 | 61.0107 | 123.0011 | 123.3902 | -123.555 | -123.5641
188.9844 | 123.4726 | -61.1435 | 62.178 | 0.058086 | 0.00097275 | -0.0072124 | 0.02371 | 0.044645 | 0.0026966 | 0.057838 | -61.2946 | 62.3291 | -61.3998 | -61.2625 | 62.0865 | 0.050354 | -0.07782 | 0.19226 | 62.233 | -61.3586 | -0.25635 | 0.15106 | -0.15106 | -0.11902 | -0.091553 | -0.21515 | 0.054931 | 0.10529 | 61.0657 | 61.3358 | 123.23 | 123.4726 | -0.15106 | 123.3765 | 61.1938 | -0.21515 | 123.4726 | -0.15106 | 61.1938 | 123.23 | 123.3765 | -123.5779 | -123.5367
189.9219 | 123.5321 | -61.0748 | 62.1735 | -0.33864 | -0.0022312 | -0.014689 | 0.0023482 | 0.05319 | -0.016529 | 0.075996 | -61.1984 | 62.3016 | -61.3815 | -61.4044 | 61.9949 | -0.032043 | -0.07782 | 0.11902 | 62.3428 | -61.3403 | -0.3067 | 0.12817 | -0.1236 | -0.32959 | -0.17853 | -0.2655 | 0.16937 | 0.18311 | 60.997 | 61.1938 | 123.0698 | 123.3765 | -0.1236 | 123.4177 | 61.0428 | -0.2655 | 123.3765 | -0.1236 | 61.0428 | 123.0698 | 123.4177 | -123.555 | -123.5138
190.9844 | 123.6008 | -61.0611 | 62.1918 | -0.20131 | -0.016117 | -0.016825 | 0.0034162 | 0.040372 | -0.024006 | 0.075996 | -61.2213 | 62.2742 | -61.377 | -61.4182 | 61.9583 | -0.054932 | 0.09613 | 0.064087 | 62.2833 | -61.3815 | -0.31586 | 0.082398 | -0.16022 | -0.35706 | -0.23346 | -0.32044 | 0.091553 | 0.15564 | 61.1572 | 61.1252 | 123.0194 | 123.3353 | -0.16022 | 123.3444 | 61.0062 | -0.32044 | 123.3353 | -0.16022 | 61.0062 | 123.0194 | 123.3444 | -123.5687 | -123.5733
191.9219 | 123.5641 | -61.0886 | 62.2009 | -0.079243 | -0.0032992 | -0.023234 | -0.0029928 | 0.045713 | -0.013325 | 0.072791 | -61.2305 | 62.2696 | -61.3724 | -61.3998 | 61.9858 | -0.045776 | 0.054932 | 0.082397 | 62.2879 | -61.3632 | -0.28381 | 0.068664 | -0.14191 | -0.31128 | -0.21515 | -0.27466 | 0.086975 | 0.14191 | 61.1435 | 61.171 | 123.0743 | 123.3582 | -0.14191 | 123.3765 | 61.0428 | -0.27466 | 123.3582 | -0.14191 | 61.0428 | 123.0743 | 123.3765 | -123.5733 | -123.5641
192.9844 | 123.5733 | -61.0931 | 62.1552 | 0.56163 | -0.0022312 | -0.031779 | 0.019437 | 0.045713 | -0.00050737 | 0.073859 | -61.1984 | 62.3245 | -61.3678 | -61.4365 | 61.972 | -0.073242 | 0.050354 | 0.07782 | 62.2559 | -61.3907 | -0.27466 | 0.16937 | -0.10529 | -0.34332 | -0.1831 | -0.29755 | 0.10071 | 0.16937 | 61.1435 | 61.171 | 123.0652 | 123.4177 | -0.10529 | 123.349 | 61.0199 | -0.29755 | 123.4177 | -0.10529 | 61.0199 | 123.0652 | 123.349 | -123.5229 | -123.5458
193.9219 | 123.587 | -61.0886 | 62.2009 | -0.53701 | -0.010776 | 0.021627 | -0.0051288 | 0.052121 | -0.026142 | 0.075996 | -61.203 | 62.2604 | -61.3678 | -61.4319 | 61.9446 | -0.027466 | 0.050354 | 0.086975 | 62.2925 | -61.3586 | -0.27924 | 0.059509 | -0.11444 | -0.34332 | -0.25635 | -0.27008 | 0.091552 | 0.16479 | 61.1389 | 61.1755 | 123.0331 | 123.349 | -0.11444 | 123.381 | 61.0611 | -0.27008 | 123.349 | -0.11444 | 61.0611 | 123.0331 | 123.381 | -123.5687 | -123.5596
194.9844 | 123.5001 | -61.1252 | 62.2009 | 0.4243 | -0.0022312 | -0.017893 | 0.019437 | 0.05853 | -0.0026434 | 0.063178 | -61.29 | 62.3337 | -61.377 | -61.2671 | 62.059 | 0.045776 | -0.064087 | 0.16937 | 62.2101 | -61.3724 | -0.25177 | 0.13275 | -0.16479 | -0.14191 | -0.14191 | -0.24719 | 0.009155 | 0.086975 | 61.0611 | 61.2946 | 123.1842 | 123.4589 | -0.16479 | 123.3353 | 61.171 | -0.24719 | 123.4589 | -0.16479 | 61.171 | 123.1842 | 123.3353 | -123.5779 | -123.5733
195.9219 | 123.555 | -61.0794 | 62.1826 | -0.38442 | -0.0086402 | -0.017893 | 0.011961 | 0.051053 | -0.0090524 | 0.06211 | -61.2167 | 62.2971 | -61.3586 | -61.4594 | 62.114 | -0.022888 | 0.022888 | 0.11902 | 62.3062 | -61.3815 | -0.27924 | 0.11444 | -0.13733 | -0.37994 | -0.068664 | -0.30212 | 0.1236 | 0.14191 | 61.1023 | 61.1984 | 123.1934 | 123.3765 | -0.13733 | 123.3856 | 61.0565 | -0.30212 | 123.3765 | -0.13733 | 61.0565 | 123.1934 | 123.3856 | -123.5413 | -123.5641
196.9844 | 123.4818 | -61.0977 | 62.2238 | -0.47597 | -0.012912 | -0.020029 | 0.0066202 | 0.051053 | -0.0047804 | 0.065314 | -61.2396 | 62.352 | -61.3586 | -61.322 | 62.059 | 0.068665 | -0.050354 | 0.17395 | 62.2696 | -61.3403 | -0.26093 | 0.12817 | -0.14191 | -0.2243 | -0.16479 | -0.24261 | 0.045776 | 0.11902 | 61.0474 | 61.2717 | 123.1567 | 123.4497 | -0.14191 | 123.3673 | 61.1664 | -0.24261 | 123.4497 | -0.14191 | 61.1664 | 123.1567 | 123.3673 | -123.5825 | -123.5641
197.9219 | 123.5825 | -61.0886 | 62.1552 | -0.3539 | -0.0065042 | -0.012553 | 0.0055522 | 0.051053 | -0.024006 | 0.068519 | -61.2076 | 62.2879 | -61.3632 | -61.409 | 61.908 | 0.032043 | 0.16937 | 0.31128 | 62.3383 | -61.3541 | -0.27466 | 0.13275 | -0.11902 | -0.32043 | -0.24719 | -0.2655 | 0.18311 | 0.15564 | 61.2579 | 61.3998 | 122.9965 | 123.3765 | -0.11902 | 123.4268 | 61.1206 | -0.2655 | 123.3765 | -0.11902 | 61.1206 | 122.9965 | 123.4268 | -123.5184 | -123.5092
198.9844 | 123.5184 | -61.1069 | 62.1597 | 0.10386 | -0.017185 | -0.023234 | 0.0023482 | 0.052121 | -0.028278 | 0.047157 | -61.2808 | 62.2742 | -61.3815 | -61.3815 | 62.0773 | 0.009155 | 0.009155 | 0.17395 | 62.2879 | -61.3586 | -0.27466 | 0.11444 | -0.17395 | -0.27466 | -0.082397 | -0.25177 | 0.12817 | 0.10071 | 61.116 | 61.2808 | 123.1842 | 123.381 | -0.17395 | 123.3948 | 61.116 | -0.25177 | 123.381 | -0.17395 | 61.116 | 123.1842 | 123.3948 | -123.5413 | -123.5184
199.9219 | 123.5962 | -61.0245 | 62.1872 | -0.10976 | -0.012912 | -0.02537 | -0.0061968 | 0.042508 | -0.013325 | 0.070655 | -61.2259 | 62.2787 | -61.3632 | -61.3998 | 61.9812 | -0.050354 | 0.054932 | 0.068665 | 62.2696 | -61.4044 | -0.33874 | 0.091553 | -0.20142 | -0.37537 | -0.20599 | -0.37994 | 0.082397 | 0.13733 | 61.0794 | 61.0931 | 123.0057 | 123.3032 | -0.20142 | 123.2941 | 60.9741 | -0.37994 | 123.3032 | -0.20142 | 60.9741 | 123.0057 | 123.2941 | -123.5504 | -123.5916
200.9844 | 123.5641 | -61.0931 | 62.2009 | -0.26235 | -0.0075722 | -0.026438 | 0.013029 | 0.045713 | -0.017597 | 0.068519 | -61.1984 | 62.2833 | -61.3586 | -61.409 | 62.1002 | -0.050354 | 0.036621 | 0.13275 | 62.2925 | -61.3586 | -0.2655 | 0.082397 | -0.10529 | -0.31586 | -0.10071 | -0.2655 | 0.091552 | 0.16022 | 61.1298 | 61.2259 | 123.1934 | 123.3765 | -0.10529 | 123.3856 | 61.0428 | -0.2655 | 123.3765 | -0.10529 | 61.0428 | 123.1934 | 123.3856 | -123.5596 | -123.5596
201.9219 | 123.4543 | -61.0657 | 62.2696 | -0.29287 | -0.0054352 | -0.00080337 | -0.0019248 | 0.045713 | -0.014393 | 0.066383 | -61.1847 | 62.2787 | -61.3541 | -61.4182 | 61.9766 | -0.032043 | 0.068665 | 0.09613 | 62.3016 | -61.3815 | -0.28839 | 0.009156 | -0.11902 | -0.35248 | -0.29297 | -0.31586 | 0.032044 | 0.16937 | 61.1343 | 61.1618 | 123.0423 | 123.3444 | -0.11902 | 123.3673 | 61.0336 | -0.31586 | 123.3444 | -0.11902 | 61.0336 | 123.0423 | 123.3673 | -123.6237 | -123.6511
202.9219 | 123.5458 | -61.0748 | 62.2101 | -0.30813 | -0.0032992 | -0.020029 | 0.010892 | 0.039304 | -0.017597 | 0.071723 | -61.203 | 62.2879 | -61.3678 | -61.3632 | 62.0041 | 0.022888 | 0.022888 | 0.12817 | 62.2971 | -61.3815 | -0.29297 | 0.07782 | -0.12817 | -0.28839 | -0.20599 | -0.3067 | 0.086975 | 0.16479 | 61.0977 | 61.203 | 123.0789 | 123.3627 | -0.12817 | 123.3719 | 61.0977 | -0.3067 | 123.3627 | -0.12817 | 61.0977 | 123.0789 | 123.3719 | -123.5779 | -123.5916
203.9688 | 123.5138 | -61.1114 | 62.1735 | 0.48533 | 0.0052458 | -0.0061444 | 0.014097 | 0.04144 | 0.00056063 | 0.067451 | -61.2625 | 62.3337 | -61.3907 | -61.3358 | 62.0453 | -0.009155 | -0.022888 | 0.12817 | 62.2467 | -61.377 | -0.27924 | 0.16022 | -0.15106 | -0.2243 | -0.12817 | -0.2655 | 0.073242 | 0.12817 | 61.0886 | 61.2396 | 123.1567 | 123.4451 | -0.15106 | 123.3582 | 61.1023 | -0.2655 | 123.4451 | -0.15106 | 61.1023 | 123.1567 | 123.3582 | -123.5641 | -123.5504
204.9219 | 123.5275 | -61.0565 | 62.2192 | -0.36916 | -0.012912 | -0.0082804 | -0.0019248 | 0.051053 | -0.014393 | 0.069587 | -61.2122 | 62.2925 | -61.3586 | -61.3724 | 62.0087 | 0.004578 | 0.022888 | 0.12817 | 62.3199 | -61.3449 | -0.30212 | 0.073242 | -0.15564 | -0.31586 | -0.21057 | -0.28839 | 0.10071 | 0.14648 | 61.0794 | 61.1847 | 123.0652 | 123.349 | -0.15564 | 123.3765 | 61.0611 | -0.28839 | 123.349 | -0.15564 | 61.0611 | 123.0652 | 123.3765 | -123.5779 | -123.5641
205.9219 | 123.5779 | -61.0886 | 62.1964 | -0.4302 | -0.01398 | -0.014689 | 0.0044842 | 0.047849 | -0.0079844 | 0.081336 | -61.203 | 62.2833 | -61.3678 | -61.4136 | 61.9766 | -0.032043 | 0.064087 | 0.086975 | 62.3016 | -61.3861 | -0.27924 | 0.086975 | -0.11444 | -0.32501 | -0.21973 | -0.29755 | 0.10529 | 0.16479 | 61.1526 | 61.1755 | 123.0652 | 123.3719 | -0.11444 | 123.3902 | 61.0565 | -0.29755 | 123.3719 | -0.11444 | 61.0565 | 123.0652 | 123.3902 | -123.5641 | -123.5825
206.9688 | 123.5138 | -61.0886 | 62.2009 | 0.4243 | -0.0065042 | -0.0072124 | -0.0051288 | 0.043577 | -0.0026434 | 0.057838 | -61.2625 | 62.265 | -61.3861 | -61.3861 | 62.0087 | -0.027466 | 0.009155 | 0.11902 | 62.2604 | -61.3953 | -0.29755 | 0.064087 | -0.17395 | -0.29755 | -0.19226 | -0.3067 | 0.059509 | 0.1236 | 61.0977 | 61.2076 | 123.0972 | 123.3536 | -0.17395 | 123.349 | 61.0611 | -0.3067 | 123.3536 | -0.17395 | 61.0611 | 123.0972 | 123.349 | -123.587 | -123.5962
207.9219 | 123.5458 | -61.0794 | 62.1826 | -0.44545 | -0.011844 | -0.013621 | 0.010892 | 0.057462 | -0.015461 | 0.068519 | -61.2213 | 62.3062 | -61.3678 | -61.3586 | 62.0087 | 0.027466 | 0.013733 | 0.11902 | 62.2787 | -61.3724 | -0.28839 | 0.1236 | -0.14191 | -0.27924 | -0.17395 | -0.29297 | 0.096131 | 0.14648 | 61.0931 | 61.1984 | 123.0881 | 123.3856 | -0.14191 | 123.3582 | 61.1069 | -0.29297 | 123.3856 | -0.14191 | 61.1069 | 123.0881 | 123.3582 | -123.5504 | -123.555
208.9844 | 123.555 | -61.0886 | 62.1964 | -0.0029495 | -0.01398 | -0.041392 | -0.0029928 | 0.047849 | -0.020801 | 0.072791 | -61.2671 | 62.2833 | -61.3861 | -61.409 | 62.0041 | -0.018311 | 0.032043 | 0.11902 | 62.2879 | -61.3586 | -0.29755 | 0.086975 | -0.17853 | -0.32043 | -0.19226 | -0.27008 | 0.091553 | 0.11902 | 61.1206 | 61.2076 | 123.0927 | 123.3719 | -0.17853 | 123.3765 | 61.0703 | -0.27008 | 123.3719 | -0.17853 | 61.0703 | 123.0927 | 123.3765 | -123.5825 | -123.555
209.9219 | 123.4406 | -61.1114 | 62.2375 | -0.3539 | 0.00097275 | -0.022166 | 0.0076882 | 0.048917 | -0.0015754 | 0.071723 | -61.29 | 62.3657 | -61.3724 | -61.377 | 62.0316 | 0.14191 | -0.10986 | 0.2243 | 62.2467 | -61.3358 | -0.26093 | 0.12817 | -0.17853 | -0.2655 | -0.20599 | -0.2243 | 0.009155 | 0.082397 | 61.0016 | 61.3358 | 123.143 | 123.4772 | -0.17853 | 123.3582 | 61.2534 | -0.2243 | 123.4772 | -0.17853 | 61.2534 | 123.143 | 123.3582 | -123.6099 | -123.5733
210.9844 | 123.5779 | -61.0703 | 62.1872 | -0.10976 | -0.010776 | -0.015757 | 0.00021117 | 0.047849 | -0.011188 | 0.071723 | -61.2579 | 62.2559 | -61.3632 | -61.3907 | 61.9949 | -0.022888 | 0.041199 | 0.10529 | 62.2787 | -61.3678 | -0.29297 | 0.068664 | -0.18768 | -0.32044 | -0.19226 | -0.29755 | 0.091553 | 0.10528 | 61.1114 | 61.1755 | 123.0652 | 123.3261 | -0.18768 | 123.349 | 61.0474 | -0.29755 | 123.3261 | -0.18768 | 61.0474 | 123.0652 | 123.349 | -123.5504 | -123.555
211.9219 | 123.4314 | -61.116 | 62.2421 | -0.24709 | -0.0032992 | -0.0072124 | 0.010892 | 0.05319 | -0.0079844 | 0.072791 | -61.2854 | 62.3108 | -61.3998 | -61.2808 | 62.0682 | 0.11902 | -0.082397 | 0.22888 | 62.2879 | -61.3449 | -0.28381 | 0.068665 | -0.16937 | -0.16479 | -0.17395 | -0.22888 | 0.045777 | 0.11444 | 61.0336 | 61.3449 | 123.1842 | 123.4268 | -0.16937 | 123.4039 | 61.235 | -0.22888 | 123.4268 | -0.16937 | 61.235 | 123.1842 | 123.4039 | -123.642 | -123.587
212.9844 | 123.5458 | -61.0886 | 62.1918 | 0.042827 | -0.024662 | -0.0061444 | 0.0044842 | 0.05319 | -0.022938 | 0.066383 | -61.2534 | 62.2925 | -61.3632 | -61.4044 | 61.9812 | -0.022888 | 0.036621 | 0.11902 | 62.2925 | -61.3541 | -0.27466 | 0.10071 | -0.16479 | -0.31586 | -0.21057 | -0.2655 | 0.10071 | 0.10986 | 61.1252 | 61.2076 | 123.0698 | 123.381 | -0.16479 | 123.381 | 61.0657 | -0.2655 | 123.381 | -0.16479 | 61.0657 | 123.0698 | 123.381 | -123.555 | -123.5458
213.9219 | 123.5275 | -61.0886 | 62.2192 | -0.3539 | -0.012912 | -0.013621 | 0.0098242 | 0.044645 | -0.0037124 | 0.058906 | -61.2122 | 62.3245 | -61.3724 | -61.3495 | 62.0132 | 0.032043 | 0 | 0.16022 | 62.3016 | -61.3678 | -0.28381 | 0.10529 | -0.1236 | -0.26093 | -0.20599 | -0.27924 | 0.082398 | 0.16022 | 61.0886 | 61.2488 | 123.1018 | 123.4131 | -0.1236 | 123.3902 | 61.1206 | -0.27924 | 123.4131 | -0.1236 | 61.1206 | 123.1018 | 123.3902 | -123.5916 | -123.587
214.9844 | 123.555 | -61.0931 | 62.1826 | -0.094502 | 0.0031088 | -0.018961 | -0.0040608 | 0.048917 | -0.011188 | 0.069587 | -61.2442 | 62.2787 | -61.3998 | -61.3907 | 61.9904 | -0.018311 | 0.041199 | 0.10986 | 62.2742 | -61.3678 | -0.3067 | 0.096131 | -0.15106 | -0.29755 | -0.19226 | -0.27466 | 0.091553 | 0.15564 | 61.1343 | 61.203 | 123.0835 | 123.3719 | -0.15106 | 123.3673 | 61.0748 | -0.27466 | 123.3719 | -0.15106 | 61.0748 | 123.0835 | 123.3673 | -123.5825 | -123.5504
215.9219 | 123.4268 | -61.1298 | 62.2421 | -1.1779 | -0.0022312 | -0.022166 | 0.0098242 | 0.062803 | -0.013325 | 0.064246 | -61.2946 | 62.3474 | -61.3815 | -61.2625 | 62.0911 | 0.13275 | -0.10529 | 0.23804 | 62.2559 | -61.3266 | -0.25177 | 0.10529 | -0.16479 | -0.13275 | -0.15106 | -0.19684 | 0.013733 | 0.086975 | 61.0245 | 61.3678 | 123.2208 | 123.4772 | -0.16479 | 123.3856 | 61.2625 | -0.19684 | 123.4772 | -0.16479 | 61.2625 | 123.2208 | 123.3856 | -123.6237 | -123.5687
216.9844 | 123.4726 | -61.1023 | 62.2604 | -0.41494 | 0.0031088 | -0.0040084 | 0.018369 | 0.054258 | -0.0047804 | 0.05677 | -61.2213 | 62.3428 | -61.3724 | -61.3037 | 62.0453 | 0.086975 | -0.059509 | 0.21515 | 62.2787 | -61.3495 | -0.27008 | 0.082397 | -0.11902 | -0.20142 | -0.21515 | -0.24719 | 0.018311 | 0.15106 | 61.0428 | 61.3174 | 123.1476 | 123.4451 | -0.11902 | 123.381 | 61.1893 | -0.24719 | 123.4451 | -0.11902 | 61.1893 | 123.1476 | 123.381 | -123.6328 | -123.6099
217.9219 | 123.4222 | -61.116 | 62.2421 | -0.15554 | -0.0032992 | -0.016825 | 0.0034162 | 0.052121 | -0.00050737 | 0.058906 | -61.29 | 62.3749 | -61.3953 | -61.2122 | 62.1185 | 0.11902 | -0.10986 | 0.23804 | 62.233 | -61.3449 | -0.27924 | 0.13275 | -0.17395 | -0.09613 | -0.1236 | -0.22888 | -0.009155 | 0.10529 | 61.0062 | 61.3541 | 123.2346 | 123.4909 | -0.17395 | 123.349 | 61.235 | -0.22888 | 123.4909 | -0.17395 | 61.235 | 123.2346 | 123.349 | -123.6374 | -123.587
218.9844 | 123.5001 | -61.0886 | 62.1689 | 0.30223 | -0.0065042 | -0.018961 | -0.0019248 | 0.055326 | -0.016529 | 0.073859 | -61.3174 | 62.2787 | -61.3815 | -61.3632 | 62.0316 | -0.004578 | -0.009155 | 0.13275 | 62.2513 | -61.3724 | -0.29297 | 0.10986 | -0.22888 | -0.27466 | -0.13733 | -0.28381 | 0.082398 | 0.064087 | 61.0794 | 61.2213 | 123.1201 | 123.3673 | -0.22888 | 123.3398 | 61.084 | -0.28381 | 123.3673 | -0.22888 | 61.084 | 123.1201 | 123.3398 | -123.5504 | -123.5413
219.9219 | 123.4497 | -61.1481 | 62.2421 | -0.52175 | -0.0086402 | -0.048869 | 0.010892 | 0.060666 | -0.016529 | 0.068519 | -61.29 | 62.3795 | -61.3907 | -61.2442 | 62.1002 | 0.1236 | -0.10529 | 0.24261 | 62.2696 | -61.3403 | -0.24262 | 0.13733 | -0.14191 | -0.096131 | -0.14191 | -0.19226 | 0.027466 | 0.10071 | 61.0428 | 61.3907 | 123.2483 | 123.5275 | -0.14191 | 123.4177 | 61.2717 | -0.19226 | 123.5275 | -0.14191 | 61.2717 | 123.2483 | 123.4177 | -123.6328 | -123.5825
220.9219 | 123.4268 | -61.1252 | 62.2375 | -2.3223 | -0.0011632 | -0.037119 | 0.013029 | 0.068143 | -0.011188 | 0.067451 | -61.3403 | 62.3611 | -61.4136 | -61.2167 | 62.1185 | 0.13275 | -0.11444 | 0.22888 | 62.2513 | -61.3586 | -0.28839 | 0.1236 | -0.21515 | -0.091553 | -0.11902 | -0.23346 | 0.013733 | 0.073242 | 61.0107 | 61.3541 | 123.2437 | 123.4863 | -0.21515 | 123.3765 | 61.2579 | -0.23346 | 123.4863 | -0.21515 | 61.2579 | 123.2437 | 123.3765 | -123.6511 | -123.5962
221.9844 | 123.4589 | -61.1023 | 62.233 | -0.41494 | 0.0041778 | -0.0061444 | 0.026914 | 0.054258 | -0.0047804 | 0.067451 | -61.29 | 62.3978 | -61.3907 | -61.2488 | 62.114 | 0.13275 | -0.086975 | 0.24719 | 62.2467 | -61.322 | -0.28839 | 0.16479 | -0.18768 | -0.14648 | -0.11902 | -0.21973 | 0.013733 | 0.10071 | 61.0153 | 61.3495 | 123.2162 | 123.5001 | -0.18768 | 123.349 | 61.235 | -0.21973 | 123.5001 | -0.18768 | 61.235 | 123.2162 | 123.349 | -123.6237 | -123.555
222.9219 | 123.4863 | -61.0931 | 62.2009 | -0.26235 | -0.0043672 | -0.0082804 | 0.014097 | 0.057462 | -0.0015754 | 0.067451 | -61.2442 | 62.3795 | -61.4136 | -61.2625 | 62.0865 | 0.082397 | -0.073242 | 0.21057 | 62.2696 | -61.3449 | -0.32043 | 0.17853 | -0.15106 | -0.16937 | -0.11444 | -0.25177 | 0.068664 | 0.16937 | 61.0199 | 61.3037 | 123.1796 | 123.4726 | -0.15106 | 123.3627 | 61.1755 | -0.25177 | 123.4726 | -0.15106 | 61.1755 | 123.1796 | 123.3627 | -123.6145 | -123.5458
223.9844 | 123.5687 | -61.0611 | 62.2009 | -3.8482 | -0.0075722 | 0.018423 | -0.0094018 | 0.055326 | -0.015461 | 0.082404 | -61.4777 | 62.3154 | -61.4136 | -61.4685 | 61.9675 | 0.004578 | 0.064087 | 0.091553 | 62.3245 | -61.3449 | -0.35248 | 0.11444 | -0.41656 | -0.40741 | -0.23346 | -0.28381 | 0.1236 | -0.064087 | 61.1252 | 61.1526 | 123.0286 | 123.3765 | -0.41656 | 123.3856 | 61.0657 | -0.28381 | 123.3765 | -0.41656 | 61.0657 | 123.0286 | 123.3856 | -123.6145 | -123.5458
224.9219 | 123.4863 | -61.1069 | 62.2147 | -0.36916 | -0.0043672 | -0.014689 | 0.0098242 | 0.059598 | 0.0016286 | 0.070655 | -61.2625 | 62.4069 | -61.3861 | -61.2625 | 62.1048 | 0.11902 | -0.082397 | 0.21973 | 62.2787 | -61.3266 | -0.27923 | 0.19226 | -0.15564 | -0.15564 | -0.10986 | -0.21973 | 0.064087 | 0.1236 | 61.0245 | 61.3266 | 123.2117 | 123.5138 | -0.15564 | 123.3856 | 61.2259 | -0.21973 | 123.5138 | -0.15564 | 61.2259 | 123.2117 | 123.3856 | -123.6008 | -123.5413
225.9844 | 123.5962 | -61.1023 | 62.1506 | 0.11912 | -0.0075722 | -0.0093484 | -0.013674 | 0.048917 | -0.024006 | 0.064246 | -61.29 | 62.2925 | -61.3724 | -61.3907 | 62.0361 | 0.009155 | -0.013733 | 0.14648 | 62.265 | -61.3632 | -0.27008 | 0.14191 | -0.18768 | -0.28839 | -0.11444 | -0.26093 | 0.11444 | 0.082397 | 61.0886 | 61.2488 | 123.1384 | 123.3948 | -0.18768 | 123.3673 | 61.1114 | -0.26093 | 123.3948 | -0.18768 | 61.1114 | 123.1384 | 123.3673 | -123.5229 | -123.5138
226.9219 | 123.4406 | -61.1252 | 62.2055 | 0.073345 | 0.0041778 | -0.032847 | 0.014097 | 0.052121 | 0.014446 | 0.070655 | -61.2396 | 62.3886 | -61.4044 | -61.2625 | 62.0728 | 0.082397 | -0.082397 | 0.20599 | 62.2375 | -61.3815 | -0.27924 | 0.18311 | -0.11444 | -0.13733 | -0.13275 | -0.25635 | 0.032044 | 0.16479 | 61.0428 | 61.3312 | 123.1979 | 123.5138 | -0.11444 | 123.3627 | 61.2076 | -0.25635 | 123.5138 | -0.11444 | 61.2076 | 123.1979 | 123.3627 | -123.6099 | -123.587
227.9844 | 123.3948 | -61.1114 | 62.2147 | -0.4302 | -0.0043672 | -0.0093484 | 0.0066202 | 0.063871 | -0.017597 | 0.059974 | -61.29 | 62.3703 | -61.4182 | -61.2579 | 62.1094 | 0.13733 | -0.17395 | 0.21973 | 62.3016 | -61.3174 | -0.3067 | 0.15564 | -0.17853 | -0.14649 | -0.10529 | -0.20599 | 0.086975 | 0.12817 | 60.9375 | 61.3312 | 123.2208 | 123.4818 | -0.17853 | 123.4131 | 61.2488 | -0.20599 | 123.4818 | -0.17853 | 61.2488 | 123.2208 | 123.4131 | -123.6328 | -123.5321
228.9219 | 123.468 | -61.084 | 62.2238 | -0.32338 | 0.0063138 | 0.0013326 | 0.0076882 | 0.056394 | -0.0047804 | 0.068519 | -61.2579 | 62.4161 | -61.377 | -61.2946 | 62.0819 | 0.086975 | -0.059509 | 0.19226 | 62.2833 | -61.3632 | -0.29297 | 0.19226 | -0.17395 | -0.21057 | -0.14191 | -0.27924 | 0.059509 | 0.11902 | 61.0245 | 61.2762 | 123.1659 | 123.5001 | -0.17395 | 123.3673 | 61.171 | -0.27924 | 123.5001 | -0.17395 | 61.171 | 123.1659 | 123.3673 | -123.6008 | -123.587
229.9844 | 123.5138 | -61.0794 | 62.2055 | -0.3539 | -0.01398 | -0.018961 | 0.0044842 | 0.060666 | -0.02187 | 0.082404 | -61.2167 | 62.352 | -61.3632 | -61.3632 | 62.0407 | 0.050354 | -0.004578 | 0.17853 | 62.3245 | -61.3632 | -0.28381 | 0.14648 | -0.13733 | -0.28381 | -0.1648 | -0.28381 | 0.11902 | 0.14648 | 61.0748 | 61.2579 | 123.1201 | 123.4314 | -0.13733 | 123.4039 | 61.1298 | -0.28381 | 123.4314 | -0.13733 | 61.1298 | 123.1201 | 123.4039 | -123.5687 | -123.5687
230.9219 | 123.4726 | -61.084 | 62.2101 | -0.18605 | 0.0063138 | -0.016825 | 0.0076882 | 0.064939 | 0.0016286 | 0.063178 | -61.2259 | 62.384 | -61.4136 | -61.2808 | 62.0865 | 0.10986 | -0.041199 | 0.1831 | 62.2742 | -61.3632 | -0.32959 | 0.17395 | -0.14191 | -0.19684 | -0.1236 | -0.27924 | 0.064087 | 0.18768 | 61.0428 | 61.2671 | 123.1705 | 123.468 | -0.14191 | 123.3582 | 61.1938 | -0.27924 | 123.468 | -0.14191 | 61.1938 | 123.1705 | 123.3582 | -123.6237 | -123.5733
231.9844 | 123.4909 | -61.0931 | 62.2101 | -0.033467 | -0.0075722 | -0.011485 | 0.0076882 | 0.05853 | 0.0026966 | 0.075996 | -61.2213 | 62.3978 | -61.3815 | -61.2717 | 62.0773 | 0.07782 | -0.041199 | 0.19226 | 62.2696 | -61.3632 | -0.28839 | 0.18768 | -0.12817 | -0.17853 | -0.13275 | -0.27008 | 0.059509 | 0.16022 | 61.0519 | 61.2854 | 123.1705 | 123.4909 | -0.12817 | 123.3627 | 61.171 | -0.27008 | 123.4909 | -0.12817 | 61.171 | 123.1705 | 123.3627 | -123.5916 | -123.5733
232.9219 | 123.4955 | -61.116 | 62.2055 | -0.36916 | -0.0011632 | -0.013621 | 0.014097 | 0.068143 | -0.011188 | 0.085609 | -61.2671 | 62.384 | -61.4136 | -61.2808 | 62.0728 | 0.09613 | -0.050354 | 0.22888 | 62.2925 | -61.377 | -0.29755 | 0.17853 | -0.15106 | -0.16479 | -0.13275 | -0.26093 | 0.086975 | 0.14648 | 61.0657 | 61.3449 | 123.1888 | 123.5001 | -0.15106 | 123.4085 | 61.2122 | -0.26093 | 123.5001 | -0.15106 | 61.2122 | 123.1888 | 123.4085 | -123.6191 | -123.5825
233.9844 | 123.5825 | -61.0519 | 62.1918 | -0.14028 | -0.0075722 | -0.036051 | -0.013674 | 0.059598 | -0.012257 | 0.067451 | -61.2259 | 62.2925 | -61.4044 | -61.4456 | 61.9675 | -0.045776 | 0.054932 | 0.09613 | 62.3245 | -61.3678 | -0.35248 | 0.10071 | -0.17395 | -0.39368 | -0.2243 | -0.31586 | 0.13275 | 0.17853 | 61.1069 | 61.1481 | 123.0194 | 123.3444 | -0.17395 | 123.3765 | 61.0062 | -0.31586 | 123.3444 | -0.17395 | 61.0062 | 123.0194 | 123.3765 | -123.5962 | -123.5596
234.9219 | 123.4772 | -61.1435 | 62.233 | -0.56752 | 0.0095178 | -0.023234 | 0.00021117 | 0.062803 | -0.014393 | 0.065314 | -61.2625 | 62.4115 | -61.3907 | -61.2534 | 62.0865 | 0.10071 | -0.09613 | 0.23346 | 62.2513 | -61.3495 | -0.24719 | 0.17853 | -0.11902 | -0.10986 | -0.14648 | -0.20599 | 0.018311 | 0.12817 | 61.0474 | 61.377 | 123.23 | 123.555 | -0.11902 | 123.3948 | 61.2442 | -0.20599 | 123.555 | -0.11902 | 61.2442 | 123.23 | 123.3948 | -123.6237 | -123.5825
235.9844 | 123.5367 | -61.1069 | 62.178 | 0.14964 | -0.0097082 | -0.014689 | -0.0019248 | 0.060666 | -0.0090524 | 0.063178 | -61.2717 | 62.2696 | -61.3907 | -61.3724 | 62.027 | -0.004578 | -0.004578 | 0.13733 | 62.3016 | -61.3861 | -0.28381 | 0.091552 | -0.16479 | -0.2655 | -0.15106 | -0.27923 | 0.1236 | 0.11902 | 61.1023 | 61.2442 | 123.1339 | 123.3765 | -0.16479 | 123.4085 | 61.1023 | -0.27923 | 123.3765 | -0.16479 | 61.1023 | 123.1339 | 123.4085 | -123.5687 | -123.5641
236.9219 | 123.4589 | -61.1023 | 62.2284 | -0.46071 | -0.0065042 | -0.013621 | 0.0087562 | 0.052121 | -0.013325 | 0.06211 | -61.29 | 62.3749 | -61.3815 | -61.235 | 62.1002 | 0.10529 | -0.11444 | 0.42114 | 62.2971 | -61.3495 | -0.27924 | 0.14648 | -0.18768 | -0.13275 | -0.12817 | -0.24719 | 0.068664 | 0.091553 | 60.9879 | 61.5234 | 123.2025 | 123.4772 | -0.18768 | 123.3994 | 61.2076 | -0.24719 | 123.4772 | -0.18768 | 61.2076 | 123.2025 | 123.3994 | -123.6099 | -123.5779
237.9844 | 123.468 | -61.1114 | 62.2192 | -0.36916 | -0.0022312 | -0.0061444 | 0.0076882 | 0.059598 | -0.01012 | 0.066383 | -61.2488 | 62.3657 | -61.3861 | -61.3083 | 62.0682 | 0.064087 | -0.091553 | 0.24719 | 62.2925 | -61.3449 | -0.27466 | 0.14649 | -0.13733 | -0.19684 | -0.15106 | -0.23346 | 0.073242 | 0.13733 | 61.0199 | 61.3586 | 123.1796 | 123.4772 | -0.13733 | 123.4039 | 61.1755 | -0.23346 | 123.4772 | -0.13733 | 61.1755 | 123.1796 | 123.4039 | -123.6053 | -123.5641
238.9219 | 123.436 | -61.1252 | 62.2284 | -1.3762 | 0.00097275 | -0.0093484 | 0.0066202 | 0.064939 | -0.0026434 | 0.061042 | -61.2946 | 62.3566 | -61.3861 | -61.2625 | 62.1048 | 0.13275 | -0.086975 | 0.23346 | 62.2925 | -61.3358 | -0.26093 | 0.12817 | -0.16937 | -0.13733 | -0.1236 | -0.21057 | 0.064086 | 0.091552 | 61.0382 | 61.3586 | 123.23 | 123.4818 | -0.16937 | 123.4177 | 61.2579 | -0.21057 | 123.4818 | -0.16937 | 61.2579 | 123.23 | 123.4177 | -123.6145 | -123.5641
239.9844 | 123.5413 | -61.1023 | 62.1735 | 0.56163 | -0.012912 | -0.043528 | 0.0012792 | 0.05319 | -0.013325 | 0.069587 | -61.2396 | 62.2742 | -61.3861 | -61.4319 | 61.9766 | -0.054932 | 0.059509 | 0.086975 | 62.3016 | -61.3953 | -0.28381 | 0.10071 | -0.13733 | -0.32959 | -0.19684 | -0.29297 | 0.12817 | 0.14648 | 61.1618 | 61.1893 | 123.0789 | 123.3765 | -0.13733 | 123.4039 | 61.0474 | -0.29297 | 123.3765 | -0.13733 | 61.0474 | 123.0789 | 123.4039 | -123.5596 | -123.5687
240.9219 | 123.5733 | -61.0657 | 62.1826 | -0.6133 | -0.011844 | -0.041392 | -0.0051288 | 0.046781 | -0.0069164 | 0.066383 | -61.2396 | 62.2787 | -61.3678 | -61.3907 | 61.9812 | -0.009155 | 0.022888 | 0.1236 | 62.3062 | -61.3815 | -0.30212 | 0.096131 | -0.17395 | -0.32501 | -0.20142 | -0.31586 | 0.1236 | 0.12817 | 61.0886 | 61.1893 | 123.0469 | 123.3444 | -0.17395 | 123.3719 | 61.0565 | -0.31586 | 123.3444 | -0.17395 | 61.0565 | 123.0469 | 123.3719 | -123.5504 | -123.5641
241.9844 | 123.5825 | -61.0657 | 62.1826 | -0.048725 | -0.020389 | -0.028574 | -0.0029928 | 0.049985 | -0.032551 | 0.067451 | -61.2488 | 62.2925 | -61.4044 | -61.4227 | 61.9904 | -0.013733 | 0.036621 | 0.10986 | 62.3016 | -61.3632 | -0.33874 | 0.10986 | -0.1831 | -0.35705 | -0.19226 | -0.29755 | 0.11902 | 0.15564 | 61.1023 | 61.1755 | 123.056 | 123.3582 | -0.1831 | 123.3673 | 61.0519 | -0.29755 | 123.3582 | -0.1831 | 61.0519 | 123.056 | 123.3673 | -123.587 | -123.5458
242.9219 | 123.4955 | -61.084 | 62.2009 | -0.29287 | -0.016117 | -0.037119 | 0.016233 | 0.049985 | -0.015461 | 0.064246 | -61.1984 | 62.3108 | -61.377 | -61.377 | 62.0087 | 0.013733 | 0.009155 | 0.12817 | 62.2971 | -61.377 | -0.29297 | 0.10986 | -0.11444 | -0.29297 | -0.19226 | -0.29297 | 0.09613 | 0.17853 | 61.0931 | 61.2122 | 123.0927 | 123.3948 | -0.11444 | 123.381 | 61.0977 | -0.29297 | 123.3948 | -0.11444 | 61.0977 | 123.0927 | 123.381 | -123.5779 | -123.5779
243.9844 | 123.5458 | -61.0748 | 62.1643 | 0.37852 | 0.00097275 | -0.012553 | 0.015165 | 0.042508 | -0.011188 | 0.058906 | -61.2076 | 62.2696 | -61.3998 | -61.409 | 61.9537 | -0.064087 | 0.050354 | 0.068665 | 62.265 | -61.4227 | -0.32501 | 0.10529 | -0.13275 | -0.33417 | -0.21057 | -0.3479 | 0.10071 | 0.19226 | 61.1252 | 61.1435 | 123.0286 | 123.3444 | -0.13275 | 123.3398 | 61.0107 | -0.3479 | 123.3444 | -0.13275 | 61.0107 | 123.0286 | 123.3398 | -123.5641 | -123.587
244.9219 | 123.468 | -61.1069 | 62.2192 | -0.4302 | -0.0043672 | -0.0072124 | 0.0044842 | 0.043577 | -0.014393 | 0.066383 | -61.2213 | 62.3337 | -61.3861 | -61.322 | 62.0407 | 0.054932 | -0.032043 | 0.17853 | 62.3016 | -61.3586 | -0.27923 | 0.11444 | -0.11444 | -0.21515 | -0.17853 | -0.25177 | 0.082398 | 0.16479 | 61.0748 | 61.2854 | 123.1476 | 123.4406 | -0.11444 | 123.4085 | 61.1618 | -0.25177 | 123.4406 | -0.11444 | 61.1618 | 123.1476 | 123.4085 | -123.6053 | -123.5779
245.9844 | 123.5825 | -61.0611 | 62.1552 | -0.12502 | -0.0054352 | -0.021098 | -0.0072648 | 0.055326 | -0.025074 | 0.069587 | -61.1893 | 62.2742 | -61.3632 | -61.4548 | 61.9263 | -0.027466 | 0.064087 | 0.07782 | 62.3199 | -61.4044 | -0.30212 | 0.11902 | -0.12817 | -0.39368 | -0.22888 | -0.34332 | 0.1648 | 0.17395 | 61.1252 | 61.1389 | 122.9874 | 123.3353 | -0.12817 | 123.381 | 61.0336 | -0.34332 | 123.3353 | -0.12817 | 61.0336 | 122.9874 | 123.381 | -123.5184 | -123.5596
246.9219 | 123.5367 | -61.0931 | 62.2147 | -0.29287 | -0.010776 | -0.014689 | 0.0034162 | 0.052121 | -0.018665 | 0.071723 | -61.203 | 62.3016 | -61.3678 | -61.3815 | 61.9949 | -0.004578 | 0.004578 | 0.13733 | 62.3291 | -61.3724 | -0.27466 | 0.086975 | -0.10986 | -0.28839 | -0.21973 | -0.27923 | 0.11444 | 0.16479 | 61.0977 | 61.2305 | 123.0881 | 123.3948 | -0.10986 | 123.4222 | 61.0886 | -0.27923 | 123.3948 | -0.10986 | 61.0886 | 123.0881 | 123.4222 | -123.5825 | -123.587
247.9844 | 123.4863 | -61.116 | 62.1964 | -0.33864 | -0.0032992 | -0.0072124 | 0.022642 | 0.043577 | -0.024006 | 0.063178 | -61.2625 | 62.3611 | -61.3861 | -61.2396 | 62.0544 | 0.07782 | -0.086975 | 0.21515 | 62.3108 | -61.3358 | -0.27008 | 0.16479 | -0.14648 | -0.1236 | -0.14191 | -0.21973 | 0.11444 | 0.1236 | 61.0291 | 61.3312 | 123.1705 | 123.4772 | -0.14648 | 123.4268 | 61.1938 | -0.21973 | 123.4772 | -0.14648 | 61.1938 | 123.1705 | 123.4268 | -123.5825 | -123.5321
248.9219 | 123.5779 | -61.0657 | 62.178 | -0.36916 | -0.018253 | -0.029642 | -0.016879 | 0.051053 | -0.0037124 | 0.070655 | -61.2991 | 62.3291 | -61.3541 | -61.441 | 61.9858 | 0.009155 | 0.036621 | 0.050354 | 62.2925 | -61.3815 | -0.28839 | 0.15106 | -0.23346 | -0.37537 | -0.19226 | -0.31586 | 0.11444 | 0.054932 | 61.1023 | 61.116 | 123.0515 | 123.3948 | -0.23346 | 123.3582 | 61.0748 | -0.31586 | 123.3948 | -0.23346 | 61.0748 | 123.0515 | 123.3582 | -123.5321 | -123.5596
249.9219 | 123.5001 | -61.084 | 62.1918 | -0.3539 | -0.012912 | -0.027506 | -0.0040608 | 0.044645 | -0.016529 | 0.073859 | -61.203 | 62.2879 | -61.3541 | -61.5692 | 62.027 | 0.17853 | 0.25177 | -0.032043 | 62.3016 | -61.3907 | -0.27008 | 0.096131 | -0.11902 | -0.48523 | -0.16479 | -0.3067 | 0.10986 | 0.15106 | 61.3358 | 61.0519 | 123.111 | 123.3719 | -0.11902 | 123.3856 | 61.2625 | -0.3067 | 123.3719 | -0.11902 | 61.2625 | 123.111 | 123.3856 | -123.5458 | -123.5825
250.9844 | 123.5458 | -61.0886 | 62.2009 | 0.027569 | -0.011844 | -0.030711 | -0.0083338 | 0.044645 | -0.024006 | 0.068519 | -61.2579 | 62.2787 | -61.3724 | -61.4044 | 61.9858 | -0.018311 | 0.022888 | 0.10986 | 62.2971 | -61.3861 | -0.28381 | 0.07782 | -0.16937 | -0.31586 | -0.21515 | -0.29755 | 0.09613 | 0.11444 | 61.1115 | 61.1984 | 123.0743 | 123.3673 | -0.16937 | 123.3856 | 61.0703 | -0.29755 | 123.3673 | -0.16937 | 61.0703 | 123.0743 | 123.3856 | -123.5733 | -123.587
251.9219 | 123.4589 | -61.0977 | 62.233 | -0.47597 | -0.0097082 | -0.030711 | 0.0012792 | 0.049985 | -0.0090524 | 0.061042 | -61.2167 | 62.3383 | -61.3678 | -61.2946 | 62.0544 | 0.068665 | -0.064087 | 0.21057 | 62.3108 | -61.3449 | -0.27008 | 0.10529 | -0.11902 | -0.19684 | -0.17853 | -0.24719 | 0.07782 | 0.15106 | 61.0336 | 61.3083 | 123.1522 | 123.436 | -0.11902 | 123.4085 | 61.1664 | -0.24719 | 123.436 | -0.11902 | 61.1664 | 123.1522 | 123.4085 | -123.6008 | -123.5779
252.9844 | 123.587 | -61.0931 | 62.1964 | -0.048725 | -0.016117 | -0.016825 | -0.0061968 | 0.049985 | -0.016529 | 0.070655 | -61.2259 | 62.2787 | -61.3815 | -61.4044 | 61.9949 | -0.032043 | 0.045776 | 0.082397 | 62.3108 | -61.3632 | -0.28839 | 0.082398 | -0.13275 | -0.31128 | -0.20142 | -0.27008 | 0.11444 | 0.15564 | 61.1389 | 61.1755 | 123.0881 | 123.3719 | -0.13275 | 123.4039 | 61.0611 | -0.27008 | 123.3719 | -0.13275 | 61.0611 | 123.0881 | 123.4039 | -123.5779 | -123.5596
253.9219 | 123.4314 | -61.0703 | 62.2147 | -0.26235 | -0.016117 | -0.029642 | 0.0044842 | 0.052121 | -0.013325 | 0.065314 | -61.1893 | 62.2971 | -61.3815 | -61.4136 | 61.9675 | -0.022888 | 0.068665 | 0.013733 | 62.3611 | -61.3724 | -0.31128 | 0.082397 | -0.11902 | -0.34332 | -0.24719 | -0.30212 | 0.14648 | 0.19226 | 61.1389 | 61.084 | 123.0377 | 123.3673 | -0.11902 | 123.4314 | 61.0474 | -0.30212 | 123.3673 | -0.11902 | 61.0474 | 123.0377 | 123.4314 | -123.5962 | -123.587
254.9844 | 123.5138 | -61.0794 | 62.2055 | 0.042827 | -0.0054352 | -0.036051 | 0.0055522 | 0.042508 | -0.022938 | 0.077064 | -61.2671 | 62.2971 | -61.4182 | -61.3724 | 62.0178 | -0.009155 | -0.032043 | 0.15106 | 62.2879 | -61.3586 | -0.33874 | 0.091553 | -0.18768 | -0.29297 | -0.18768 | -0.27924 | 0.082398 | 0.15106 | 61.0474 | 61.2305 | 123.0972 | 123.3765 | -0.18768 | 123.3673 | 61.0703 | -0.27924 | 123.3765 | -0.18768 | 61.0703 | 123.0972 | 123.3673 | -123.6237 | -123.5641
255.9219 | 123.587 | -61.0611 | 62.2009 | -0.23183 | -0.0032992 | -0.017893 | 0.0034162 | 0.039304 | -0.02187 | 0.069587 | -61.171 | 62.2925 | -61.3815 | -61.4319 | 61.9537 | -0.073242 | 0.054932 | 0.082397 | 62.2925 | -61.409 | -0.32044 | 0.091552 | -0.10986 | -0.37079 | -0.24719 | -0.3479 | 0.091552 | 0.21057 | 61.116 | 61.1435 | 123.0148 | 123.3536 | -0.10986 | 123.3536 | 60.9879 | -0.3479 | 123.3536 | -0.10986 | 60.9879 | 123.0148 | 123.3536 | -123.5825 | -123.6099
256.9844 | 123.5046 | -61.1298 | 62.1689 | 0.28697 | -0.016117 | -0.018961 | 0.00021117 | 0.042508 | -0.014393 | 0.061042 | -61.2717 | 62.2513 | -61.3907 | -61.3541 | 62.0224 | 0.018311 | -0.018311 | 0.14648 | 62.2742 | -61.3815 | -0.26093 | 0.082398 | -0.14191 | -0.2243 | -0.14648 | -0.25177 | 0.10529 | 0.11902 | 61.1115 | 61.2762 | 123.1522 | 123.381 | -0.14191 | 123.4039 | 61.1481 | -0.25177 | 123.381 | -0.14191 | 61.1481 | 123.1522 | 123.4039 | -123.5596 | -123.5504
257.9219 | 123.5367 | -61.0703 | 62.2238 | -0.23183 | -0.0075722 | -0.018961 | -0.0040608 | 0.046781 | -0.017597 | 0.068519 | -61.1984 | 62.3199 | -61.3724 | -61.377 | 61.9904 | 0.004578 | 0.022888 | 0.12817 | 62.2971 | -61.3541 | -0.30212 | 0.09613 | -0.12817 | -0.3067 | -0.23346 | -0.28381 | 0.073242 | 0.17395 | 61.0931 | 61.1984 | 123.0606 | 123.3902 | -0.12817 | 123.3673 | 61.0748 | -0.28381 | 123.3902 | -0.12817 | 61.0748 | 123.0606 | 123.3673 | -123.5962 | -123.5779
258.9844 | 123.5596 | -61.0886 | 62.1643 | 0.48533 | -0.0032992 | -0.010416 | 0.0076882 | 0.044645 | -0.016529 | 0.064246 | -61.084 | 62.2971 | -61.4182 | -61.3815 | 62.0041 | -0.086975 | 0.027466 | 0.10071 | 62.2787 | -61.3953 | -0.32959 | 0.13275 | 0.004578 | -0.29297 | -0.16022 | -0.3067 | 0.11444 | 0.33417 | 61.116 | 61.1893 | 123.0927 | 123.3856 | 0.004578 | 123.3673 | 61.0016 | -0.3067 | 123.3856 | 0.004578 | 61.0016 | 123.0927 | 123.3673 | -123.5825 | -123.5596
259.9219 | 123.5779 | -61.0565 | 62.1964 | -0.033467 | 0.0020408 | -0.0072124 | 0.0055522 | 0.039304 | -0.024006 | 0.070655 | -61.2213 | 62.2787 | -61.3907 | -61.4502 | 61.9263 | -0.041199 | 0.082397 | 0.073242 | 62.2971 | -61.3678 | -0.33417 | 0.082398 | -0.16479 | -0.39368 | -0.27008 | -0.31128 | 0.10071 | 0.16937 | 61.1389 | 61.1298 | 122.9828 | 123.3353 | -0.16479 | 123.3536 | 61.0153 | -0.31128 | 123.3353 | -0.16479 | 61.0153 | 122.9828 | 123.3536 | -123.587 | -123.5641
260.9844 | 123.5367 | -61.084 | 62.1689 | -0.0029495 | -0.01398 | -0.021098 | -0.0040608 | 0.042508 | -0.02187 | 0.068519 | -61.2488 | 62.265 | -61.3449 | -61.3861 | 61.9858 | -0.013733 | 0.022888 | 0.10986 | 62.3199 | -61.3632 | -0.26093 | 0.096131 | -0.16479 | -0.30212 | -0.1831 | -0.27924 | 0.15106 | 0.096131 | 61.1069 | 61.1938 | 123.0698 | 123.349 | -0.16479 | 123.4039 | 61.0703 | -0.27924 | 123.349 | -0.16479 | 61.0703 | 123.0698 | 123.4039 | -123.5138 | -123.5321
261.9219 | 123.5184 | -61.0748 | 62.178 | 0.027569 | -0.0043672 | -0.021098 | -0.011538 | 0.046781 | -0.02721 | 0.074928 | -61.2762 | 62.2925 | -61.3861 | -61.3266 | 61.9904 | -0.013733 | 0.004578 | 0.15564 | 62.2879 | -61.3998 | -0.31128 | 0.11444 | -0.20142 | -0.25177 | -0.18768 | -0.32501 | 0.10986 | 0.10986 | 61.0794 | 61.2305 | 123.0652 | 123.3673 | -0.20142 | 123.3627 | 61.0611 | -0.32501 | 123.3673 | -0.20142 | 61.0611 | 123.0652 | 123.3627 | -123.5641 | -123.5779
262.9844 | 123.5138 | -61.084 | 62.1872 | 0.53111 | -0.022525 | 0.00026463 | 0.014097 | 0.048917 | 0.0026966 | 0.054633 | -61.2076 | 62.2833 | -61.3724 | -61.3998 | 61.972 | -0.045776 | 0.027466 | -0.11444 | 62.2559 | -61.4319 | -0.28839 | 0.09613 | -0.1236 | -0.31586 | -0.21515 | -0.3479 | 0.068664 | 0.16479 | 61.1114 | 60.9695 | 123.056 | 123.3673 | -0.1236 | 123.3398 | 61.0382 | -0.3479 | 123.3673 | -0.1236 | 61.0382 | 123.056 | 123.3398 | -123.5596 | -123.6191
263.9219 | 123.6145 | -61.1069 | 62.2055 | -0.10976 | -0.016117 | -0.040324 | -0.0094018 | 0.043577 | -0.024006 | 0.066383 | -61.2305 | 62.2833 | -61.3907 | -61.4044 | 61.972 | -0.050354 | 0.054932 | 0.10071 | 62.2879 | -61.3678 | -0.28381 | 0.07782 | -0.1236 | -0.29755 | -0.23346 | -0.26093 | 0.082398 | 0.16022 | 61.1618 | 61.2076 | 123.0789 | 123.3902 | -0.1236 | 123.3948 | 61.0565 | -0.26093 | 123.3902 | -0.1236 | 61.0565 | 123.0789 | 123.3948 | -123.5962 | -123.5733
264.9844 | 123.4863 | -61.1252 | 62.2055 | 0.50059 | 0.0052458 | -0.022166 | 0.011961 | 0.045713 | 0.0059006 | 0.058906 | -61.2854 | 62.352 | -61.4319 | -61.3174 | 62.0499 | 0.018311 | -0.027466 | 0.15564 | 62.2147 | -61.377 | -0.3067 | 0.14648 | -0.16022 | -0.19226 | -0.15564 | -0.25177 | 0.009156 | 0.14648 | 61.0977 | 61.2808 | 123.175 | 123.4772 | -0.16022 | 123.3398 | 61.1435 | -0.25177 | 123.4772 | -0.16022 | 61.1435 | 123.175 | 123.3398 | -123.6374 | -123.5825
265.9219 | 123.5733 | -61.0794 | 62.1918 | -0.094502 | -0.0032992 | -0.011485 | -0.0040608 | 0.052121 | -0.020801 | 0.065314 | -61.1984 | 62.2925 | -61.3724 | -61.4227 | 61.9766 | -0.045776 | 0.086975 | 0.059509 | 62.3062 | -61.3678 | -0.29297 | 0.10071 | -0.11902 | -0.34332 | -0.21515 | -0.28839 | 0.11444 | 0.17395 | 61.1664 | 61.1389 | 123.056 | 123.3719 | -0.11902 | 123.3856 | 61.0336 | -0.28839 | 123.3719 | -0.11902 | 61.0336 | 123.056 | 123.3856 | -123.5641 | -123.5596
266.9844 | 123.5504 | -61.0977 | 62.1735 | 0.40904 | -0.0032992 | -0.0018714 | 0.0087562 | 0.042508 | -0.0069164 | 0.070655 | -61.2442 | 62.3428 | -61.4227 | -61.3632 | 62.0087 | -0.009155 | 0.027466 | 0.059509 | 62.2421 | -61.3953 | -0.32501 | 0.16937 | -0.14648 | -0.2655 | -0.16479 | -0.29755 | 0.068664 | 0.17853 | 61.1252 | 61.1572 | 123.1064 | 123.4406 | -0.14648 | 123.3398 | 61.0886 | -0.29755 | 123.4406 | -0.14648 | 61.0886 | 123.1064 | 123.3398 | -123.5962 | -123.5687
267.9219 | 123.5092 | -61.1023 | 62.2238 | 0.13438 | -0.0075722 | -0.024302 | -0.0040608 | 0.052121 | -0.016529 | 0.067451 | -61.2762 | 62.2879 | -61.3907 | -61.3586 | 62.0316 | 0.013733 | -0.018311 | 0.14648 | 62.2742 | -61.3907 | -0.28839 | 0.064087 | -0.17395 | -0.25635 | -0.19226 | -0.28839 | 0.050354 | 0.11444 | 61.084 | 61.2488 | 123.1338 | 123.3902 | -0.17395 | 123.3765 | 61.116 | -0.28839 | 123.3902 | -0.17395 | 61.116 | 123.1338 | 123.3765 | -123.6145 | -123.6145
268.9844 | 123.4222 | -61.1298 | 62.2009 | 0.348 | 0.013791 | 0.0088096 | 0.019437 | 0.044645 | -0.0090524 | 0.065314 | -61.5005 | 62.3428 | -61.4227 | -61.235 | 62.0361 | 0.086975 | -0.045776 | 0.22888 | 62.233 | -61.3358 | -0.29297 | 0.14191 | -0.37079 | -0.10528 | -0.16479 | -0.20599 | 0.032043 | -0.07782 | 61.084 | 61.3586 | 123.1659 | 123.4726 | -0.37079 | 123.3627 | 61.2167 | -0.20599 | 123.4726 | -0.37079 | 61.2167 | 123.1659 | 123.3627 | -123.6237 | -123.5367
269.9219 | 123.5321 | -61.0931 | 62.1643 | 0.042827 | -0.011844 | -0.012553 | -0.00085683 | 0.056394 | -0.019733 | 0.067451 | -61.2854 | 62.2742 | -61.3861 | -61.3632 | 62.0956 | 0 | -0.032043 | 0.14648 | 62.2742 | -61.3678 | -0.29297 | 0.10986 | -0.19226 | -0.27008 | -0.068665 | -0.27466 | 0.10986 | 0.10071 | 61.0611 | 61.2396 | 123.1888 | 123.3673 | -0.19226 | 123.3673 | 61.0931 | -0.27466 | 123.3673 | -0.19226 | 61.0931 | 123.1888 | 123.3673 | -123.5504 | -123.5321
270.9844 | 123.4406 | -61.1435 | 62.1735 | 0.348 | 0.0020408 | 0.00026463 | 0.030119 | 0.052121 | 0.00056063 | 0.063178 | -61.3174 | 62.3703 | -61.4044 | -61.2305 | 62.1094 | 0.09613 | -0.11902 | 0.23346 | 62.2192 | -61.3495 | -0.26093 | 0.19684 | -0.17395 | -0.086975 | -0.064087 | -0.20599 | 0.045776 | 0.086975 | 61.0245 | 61.377 | 123.2529 | 123.5138 | -0.17395 | 123.3627 | 61.2396 | -0.20599 | 123.5138 | -0.17395 | 61.2396 | 123.2529 | 123.3627 | -123.5779 | -123.5229
271.9219 | 123.5367 | -61.0931 | 62.1735 | 0.10386 | -0.0075722 | -0.028574 | -0.013674 | 0.048917 | -0.018665 | 0.075996 | -61.3037 | 62.2787 | -61.3998 | -61.3724 | 62.0132 | -0.004578 | 0.009155 | 0.12817 | 62.2833 | -61.3815 | -0.3067 | 0.10529 | -0.21057 | -0.27923 | -0.16022 | -0.28839 | 0.10986 | 0.09613 | 61.1023 | 61.2213 | 123.1064 | 123.3719 | -0.21057 | 123.3765 | 61.0886 | -0.28839 | 123.3719 | -0.21057 | 61.0886 | 123.1064 | 123.3765 | -123.5733 | -123.555
272.9844 | 123.5046 | -61.1069 | 62.1597 | 0.348 | -0.0022312 | -0.016825 | -0.0072648 | 0.049985 | -0.012257 | 0.067451 | -61.2671 | 62.3291 | -61.3586 | -61.3907 | 62.0224 | -0.009155 | 0.004578 | 0.1236 | 62.2742 | -61.3953 | -0.25177 | 0.16937 | -0.16022 | -0.28381 | -0.13733 | -0.28839 | 0.11444 | 0.091553 | 61.1115 | 61.2305 | 123.1293 | 123.436 | -0.16022 | 123.381 | 61.0977 | -0.28839 | 123.436 | -0.16022 | 61.0977 | 123.1293 | 123.381 | -123.5184 | -123.555
273.9219 | 123.5641 | -61.0748 | 62.1735 | -0.079243 | -0.017185 | -0.014689 | -0.0083338 | 0.044645 | -0.02187 | 0.072791 | -61.2717 | 62.3016 | -61.3907 | -61.3953 | 61.9904 | -0.018311 | 0.036621 | 0.11444 | 62.2925 | -61.377 | -0.31586 | 0.12817 | -0.19684 | -0.32043 | -0.18311 | -0.30212 | 0.11902 | 0.11902 | 61.1114 | 61.1893 | 123.0652 | 123.3765 | -0.19684 | 123.3673 | 61.0565 | -0.30212 | 123.3765 | -0.19684 | 61.0565 | 123.0652 | 123.3673 | -123.5641 | -123.5504
274.9844 | 123.4726 | -61.1206 | 62.2192 | 0.22593 | 0.0073818 | -0.011485 | 0.017301 | 0.05319 | 0.00056063 | 0.067451 | -61.2854 | 62.3795 | -61.4136 | -61.2579 | 62.0682 | 0.045776 | -0.07782 | 0.19226 | 62.2147 | -61.3632 | -0.29297 | 0.16022 | -0.1648 | -0.13733 | -0.15106 | -0.24262 | -0.004577 | 0.12817 | 61.0428 | 61.3129 | 123.1888 | 123.5001 | -0.1648 | 123.3353 | 61.1664 | -0.24262 | 123.5001 | -0.1648 | 61.1664 | 123.1888 | 123.3353 | -123.6328 | -123.5825
275.9219 | 123.5138 | -61.0886 | 62.1872 | 0.10386 | -0.01398 | -0.021098 | -0.013674 | 0.04144 | -0.014393 | 0.071723 | -61.29 | 62.2925 | -61.3998 | -61.3861 | 62.0316 | 0.004578 | -0.004578 | 0.13733 | 62.265 | -61.377 | -0.31128 | 0.10528 | -0.20142 | -0.29755 | -0.15564 | -0.28839 | 0.07782 | 0.10986 | 61.084 | 61.2259 | 123.1201 | 123.381 | -0.20142 | 123.3536 | 61.0931 | -0.28839 | 123.381 | -0.20142 | 61.0931 | 123.1201 | 123.3536 | -123.587 | -123.5641
276.9688 | 123.4863 | -61.1023 | 62.2192 | -0.018208 | 0.014859 | -0.028574 | 0.025846 | 0.044645 | 0.00056063 | 0.059974 | -61.2076 | 62.4023 | -61.3861 | -61.2854 | 61.9995 | 0.054932 | -0.013733 | 0.17395 | 62.265 | -61.3907 | -0.28381 | 0.18311 | -0.10529 | -0.18311 | -0.21973 | -0.28839 | 0.045777 | 0.17853 | 61.0886 | 61.2762 | 123.1018 | 123.5046 | -0.10529 | 123.3673 | 61.1572 | -0.28839 | 123.5046 | -0.10529 | 61.1572 | 123.1018 | 123.3673 | -123.6053 | -123.6099
277.9219 | 123.5138 | -61.0931 | 62.1643 | 0.19541 | -0.016117 | -0.028574 | -0.0040608 | 0.05319 | -0.011188 | 0.070655 | -61.2762 | 62.3062 | -61.4273 | -61.3724 | 62.027 | -0.009155 | 0 | 0.14648 | 62.2879 | -61.3861 | -0.33417 | 0.14191 | -0.18311 | -0.27923 | -0.13733 | -0.29297 | 0.1236 | 0.15106 | 61.0931 | 61.2396 | 123.1201 | 123.3994 | -0.18311 | 123.381 | 61.084 | -0.29297 | 123.3994 | -0.18311 | 61.084 | 123.1201 | 123.381 | -123.5916 | -123.5504
278.9219 | 123.5458 | -61.0931 | 62.1918 | 0.10386 | -0.017185 | -0.014689 | -0.012606 | 0.027555 | -0.031483 | 0.073859 | -61.2808 | 62.3199 | -61.3861 | -61.3861 | 62.0041 | 0.045776 | -0.004578 | 0.10529 | 62.2833 | -61.3724 | -0.29297 | 0.12817 | -0.18768 | -0.29297 | -0.18768 | -0.27923 | 0.091553 | 0.10529 | 61.0886 | 61.1984 | 123.0972 | 123.4131 | -0.18768 | 123.3765 | 61.1389 | -0.27923 | 123.4131 | -0.18768 | 61.1389 | 123.0972 | 123.3765 | -123.5779 | -123.5641
279.9844 | 123.5321 | -61.0565 | 62.1964 | 0.47007 | -0.0097082 | 0.022695 | 0.019437 | 0.039304 | -0.0079844 | 0.073859 | -61.2076 | 62.2925 | -61.3724 | -61.4273 | 62.1323 | -0.041199 | 0.004578 | -0.091553 | 62.233 | -61.4227 | -0.31586 | 0.09613 | -0.15106 | -0.37079 | -0.064087 | -0.36621 | 0.036621 | 0.16479 | 61.0611 | 60.965 | 123.1888 | 123.349 | -0.15106 | 123.2895 | 61.0153 | -0.36621 | 123.349 | -0.15106 | 61.0153 | 123.1888 | 123.2895 | -123.5687 | -123.6191
280.9219 | 123.5092 | -61.1114 | 62.1597 | 0.37852 | -0.010776 | -0.039256 | 0.0098242 | 0.037168 | -0.013325 | 0.077064 | -61.2671 | 62.2787 | -61.4136 | -61.3815 | 62.0087 | -0.018311 | 0.009155 | 0.13733 | 62.265 | -61.409 | -0.30212 | 0.11902 | -0.15564 | -0.27008 | -0.15106 | -0.29755 | 0.10529 | 0.14648 | 61.1206 | 61.2488 | 123.1201 | 123.3902 | -0.15564 | 123.3765 | 61.0931 | -0.29755 | 123.3902 | -0.15564 | 61.0931 | 123.1201 | 123.3765 | -123.5733 | -123.5687
281.9844 | 123.4589 | -61.1023 | 62.2055 | 3.7507 | -9.5248e-05 | -0.0478 | 0.013029 | 0.052121 | -0.0026434 | 0.074928 | -61.0382 | 62.3795 | -61.4044 | -61.1984 | 62.1414 | 0.059509 | -0.10986 | 0.23346 | 62.2467 | -61.3861 | -0.30212 | 0.17395 | 0.064087 | -0.09613 | -0.064087 | -0.28381 | 0.041199 | 0.36621 | 60.9924 | 61.3358 | 123.2437 | 123.4818 | 0.064087 | 123.349 | 61.1618 | -0.28381 | 123.4818 | 0.064087 | 61.1618 | 123.2437 | 123.349 | -123.6099 | -123.5916
282.9219 | 123.5138 | -61.0977 | 62.1643 | 0.14964 | -0.011844 | -0.00080337 | -0.0083338 | 0.04144 | -0.025074 | 0.070655 | -61.29 | 62.2742 | -61.3998 | -61.3815 | 62.0224 | 0.009155 | -0.013733 | 0.14648 | 62.265 | -61.3907 | -0.30212 | 0.10986 | -0.19226 | -0.28381 | -0.14191 | -0.29297 | 0.10071 | 0.10986 | 61.084 | 61.2442 | 123.1201 | 123.3719 | -0.19226 | 123.3627 | 61.1069 | -0.29297 | 123.3719 | -0.19226 | 61.1069 | 123.1201 | 123.3627 | -123.5641 | -123.555
283.9219 | 123.5046 | -61.116 | 62.178 | 0.24119 | -0.015048 | -0.029642 | -0.0019248 | 0.04144 | -0.019733 | 0.0792 | -61.2854 | 62.2742 | -61.3861 | -61.3586 | 62.0178 | 0 | -0.009155 | 0.13733 | 62.2604 | -61.3861 | -0.27008 | 0.09613 | -0.16937 | -0.24262 | -0.16022 | -0.27008 | 0.082397 | 0.10071 | 61.1069 | 61.2534 | 123.1338 | 123.3902 | -0.16937 | 123.3765 | 61.116 | -0.27008 | 123.3902 | -0.16937 | 61.116 | 123.1338 | 123.3765 | -123.5641 | -123.5641
284.9844 | 123.5641 | -61.0748 | 62.1643 | 0.47007 | -0.016117 | -0.014689 | 0.0055522 | 0.043577 | -0.024006 | 0.06211 | -61.2167 | 62.2787 | -61.3861 | -61.2579 | 62.0361 | -0.091553 | 0.064087 | 0.09613 | 62.3062 | -61.4136 | -0.31128 | 0.11444 | -0.14191 | -0.18311 | -0.12817 | -0.33874 | 0.14191 | 0.16937 | 61.1389 | 61.171 | 123.111 | 123.3536 | -0.14191 | 123.381 | 60.9833 | -0.33874 | 123.3536 | -0.14191 | 60.9833 | 123.111 | 123.381 | -123.5504 | -123.5779
285.9219 | 123.5413 | -61.0931 | 62.1597 | -0.094502 | -0.020389 | -0.028574 | 0.0023482 | 0.048917 | -0.016529 | 0.067451 | -61.2579 | 62.2879 | -61.4044 | -61.3861 | 61.9858 | -0.009155 | 0.032043 | 0.1236 | 62.2787 | -61.3953 | -0.31128 | 0.12817 | -0.1648 | -0.29297 | -0.17395 | -0.30212 | 0.11902 | 0.14648 | 61.1252 | 61.2167 | 123.0789 | 123.381 | -0.1648 | 123.3719 | 61.084 | -0.30212 | 123.381 | -0.1648 | 61.084 | 123.0789 | 123.3719 | -123.5641 | -123.555
286.9844 | 123.4497 | -61.1206 | 62.2101 | 0.18016 | 0.0063138 | -0.022166 | 0.02905 | 0.055326 | 0.0048326 | 0.072791 | -61.3266 | 62.384 | -61.3907 | -61.2305 | 62.1185 | 0.09613 | -0.11444 | 0.22888 | 62.2284 | -61.3678 | -0.27008 | 0.17395 | -0.20599 | -0.10986 | -0.091553 | -0.24719 | 0.018311 | 0.064087 | 61.0062 | 61.3495 | 123.2391 | 123.5046 | -0.20599 | 123.349 | 61.2167 | -0.24719 | 123.5046 | -0.20599 | 61.2167 | 123.2391 | 123.349 | -123.6008 | -123.5779
287.9219 | 123.5229 | -61.0977 | 62.1735 | 0.27171 | -0.0043672 | -0.036051 | 0.00021117 | 0.045713 | -0.014393 | 0.052497 | -61.2671 | 62.2696 | -61.3998 | -61.3815 | 62.0132 | -0.009155 | 0 | 0.11902 | 62.265 | -61.3953 | -0.30212 | 0.09613 | -0.16937 | -0.28381 | -0.16022 | -0.29755 | 0.091553 | 0.13275 | 61.0977 | 61.2167 | 123.111 | 123.3673 | -0.16937 | 123.3627 | 61.0886 | -0.29755 | 123.3673 | -0.16937 | 61.0886 | 123.111 | 123.3627 | -123.5733 | -123.5687
288.9844 | 123.4726 | -61.0977 | 62.1872 | -0.8727 | -0.0043672 | -0.017893 | 0.022642 | 0.042508 | -0.00050737 | 0.064246 | -61.3083 | 62.3932 | -61.409 | -61.2579 | 62.0956 | 0.082397 | -0.091553 | 0.20599 | 62.2284 | -61.3632 | -0.31128 | 0.20599 | -0.21057 | -0.16022 | -0.091553 | -0.2655 | 0.041199 | 0.10071 | 61.0062 | 61.3037 | 123.1934 | 123.4909 | -0.21057 | 123.3261 | 61.1801 | -0.2655 | 123.4909 | -0.21057 | 61.1801 | 123.1934 | 123.3261 | -123.5962 | -123.5504
289.9219 | 123.5184 | -61.1023 | 62.1643 | 0.11912 | -0.010776 | -0.0061444 | -0.021151 | 0.055326 | -0.017597 | 0.067451 | -61.2808 | 62.2925 | -61.4044 | -61.377 | 62.0224 | 0.004578 | -0.009155 | 0.13733 | 62.265 | -61.3632 | -0.30212 | 0.12817 | -0.17853 | -0.27466 | -0.14191 | -0.26093 | 0.10071 | 0.1236 | 61.0931 | 61.2396 | 123.1247 | 123.3948 | -0.17853 | 123.3673 | 61.1069 | -0.26093 | 123.3948 | -0.17853 | 61.1069 | 123.1247 | 123.3673 | -123.5687 | -123.5275
290.9688 | 123.4909 | -61.1252 | 62.2192 | -0.23183 | 0.0020408 | -0.029642 | 0.016233 | 0.066007 | 0.00056063 | 0.072791 | -61.2259 | 62.4298 | -61.409 | -61.2671 | 62.0544 | 0.064087 | -0.050354 | 0.18768 | 62.2787 | -61.3586 | -0.28381 | 0.21057 | -0.10071 | -0.14191 | -0.16479 | -0.23346 | 0.05951 | 0.18311 | 61.0748 | 61.3129 | 123.1796 | 123.555 | -0.10071 | 123.4039 | 61.1893 | -0.23346 | 123.555 | -0.10071 | 61.1893 | 123.1796 | 123.4039 | -123.6282 | -123.5779
291.9219 | 123.5138 | -61.0748 | 62.1872 | 0.65318 | -0.016117 | -0.048869 | -0.0029928 | 0.045713 | -0.011188 | 0.074928 | -61.2717 | 62.3199 | -61.3815 | -61.4136 | 61.9995 | -0.013733 | -0.027466 | 0.13275 | 62.2787 | -61.3815 | -0.3067 | 0.13275 | -0.19684 | -0.33874 | -0.18768 | -0.3067 | 0.091553 | 0.10986 | 61.0474 | 61.2076 | 123.0743 | 123.3948 | -0.19684 | 123.3536 | 61.0611 | -0.3067 | 123.3948 | -0.19684 | 61.0611 | 123.0743 | 123.3536 | -123.5687 | -123.5687
292.9844 | 123.5184 | -61.0703 | 62.1964 | -0.41494 | -0.017185 | -0.026438 | 0.0023482 | 0.054258 | -0.018665 | 0.064246 | -61.2259 | 62.3108 | -61.3724 | -61.3724 | 62.0132 | 0.027466 | 0.022888 | 0.12817 | 62.3245 | -61.3724 | -0.30212 | 0.11444 | -0.15564 | -0.30212 | -0.18311 | -0.30212 | 0.12817 | 0.14648 | 61.0931 | 61.1984 | 123.0835 | 123.381 | -0.15564 | 123.3948 | 61.0977 | -0.30212 | 123.381 | -0.15564 | 61.0977 | 123.0835 | 123.3948 | -123.5687 | -123.5687
293.9219 | 123.5733 | -61.0657 | 62.178 | -0.079243 | -0.0065042 | -0.031779 | -0.016879 | 0.042508 | -0.02721 | 0.074928 | -61.2488 | 62.2879 | -61.3907 | -61.409 | 61.9949 | -0.009155 | 0.045776 | 0.10986 | 62.3062 | -61.4044 | -0.32501 | 0.10986 | -0.1831 | -0.34332 | -0.18311 | -0.33874 | 0.12817 | 0.14191 | 61.1114 | 61.1755 | 123.0606 | 123.3536 | -0.1831 | 123.3719 | 61.0565 | -0.33874 | 123.3536 | -0.1831 | 61.0565 | 123.0606 | 123.3719 | -123.5687 | -123.5825
294.9688 | 123.4634 | -61.1206 | 62.1826 | 0.1649 | 0.0084498 | -0.016825 | 0.010892 | 0.057462 | -0.0047804 | 0.068519 | -61.2762 | 62.3611 | -61.3998 | -61.2625 | 62.0865 | 0.059509 | -0.068665 | 0.19226 | 62.2421 | -61.3907 | -0.27924 | 0.17853 | -0.15564 | -0.14191 | -0.09613 | -0.27008 | 0.059509 | 0.1236 | 61.0519 | 61.3129 | 123.2071 | 123.4818 | -0.15564 | 123.3627 | 61.1801 | -0.27008 | 123.4818 | -0.15564 | 61.1801 | 123.2071 | 123.3627 | -123.5825 | -123.5733
295.9219 | 123.5367 | -61.0886 | 62.1689 | 0.21067 | -0.015048 | -0.048869 | -0.0061968 | 0.040372 | -0.02187 | 0.068519 | -61.2579 | 62.2833 | -61.3907 | -61.3861 | 62.0316 | -0.004578 | -0.009155 | 0.14191 | 62.265 | -61.3815 | -0.30212 | 0.11444 | -0.16937 | -0.29755 | -0.13733 | -0.29297 | 0.096131 | 0.13275 | 61.0794 | 61.2305 | 123.1201 | 123.3719 | -0.16937 | 123.3536 | 61.084 | -0.29297 | 123.3719 | -0.16937 | 61.084 | 123.1201 | 123.3536 | -123.5596 | -123.5504
296.9688 | 123.4589 | -61.1206 | 62.2009 | -0.6133 | 0.0084498 | -0.0061444 | 0.0087562 | 0.054258 | -0.0026434 | 0.061042 | -61.3083 | 62.384 | -61.4136 | -61.2625 | 62.0956 | 0.064087 | -0.082397 | 0.20142 | 62.2467 | -61.3815 | -0.29297 | 0.18311 | -0.18768 | -0.14191 | -0.10529 | -0.26093 | 0.045776 | 0.10528 | 61.0382 | 61.322 | 123.2162 | 123.5046 | -0.18768 | 123.3673 | 61.1847 | -0.26093 | 123.5046 | -0.18768 | 61.1847 | 123.2162 | 123.3673 | -123.6145 | -123.5825
297.9219 | 123.5275 | -61.1069 | 62.1689 | 0.027569 | -0.0075722 | -0.021098 | -0.0061968 | 0.042508 | -0.026142 | 0.070655 | -61.2762 | 62.2971 | -61.4365 | -61.3861 | 61.9904 | 0.041199 | 0.09613 | 0.13275 | 62.3016 | -61.3495 | -0.32959 | 0.12817 | -0.16937 | -0.27923 | -0.17853 | -0.24261 | 0.13275 | 0.16022 | 61.203 | 61.2396 | 123.0972 | 123.4039 | -0.16937 | 123.4085 | 61.1481 | -0.24261 | 123.4039 | -0.16937 | 61.1481 | 123.0972 | 123.4085 | -123.6053 | -123.5184
298.9844 | 123.4726 | -61.1023 | 62.1872 | 0.48533 | 0.0041778 | -0.014689 | 0.02371 | 0.044645 | 0.00056063 | 0.071723 | -61.2946 | 62.3611 | -61.4319 | -61.2946 | 62.0773 | 0.036621 | -0.068665 | 0.19226 | 62.2467 | -61.3724 | -0.32959 | 0.17395 | -0.19226 | -0.19226 | -0.10986 | -0.27008 | 0.059509 | 0.13733 | 61.0336 | 61.2946 | 123.1796 | 123.4634 | -0.19226 | 123.349 | 61.1389 | -0.27008 | 123.4634 | -0.19226 | 61.1389 | 123.1796 | 123.349 | -123.6191 | -123.5596
299.9219 | 123.5596 | -61.0703 | 62.178 | 0.11912 | -0.015048 | -0.034983 | -0.0040608 | 0.046781 | -0.026142 | 0.065314 | -61.2625 | 62.3062 | -61.4136 | -61.4136 | 62.0132 | -0.013733 | 0.004578 | 0.1236 | 62.2696 | -61.3861 | -0.34332 | 0.12817 | -0.19226 | -0.34332 | -0.1648 | -0.31586 | 0.091552 | 0.15106 | 61.0748 | 61.1938 | 123.0835 | 123.3765 | -0.19226 | 123.3398 | 61.0565 | -0.31586 | 123.3765 | -0.19226 | 61.0565 | 123.0835 | 123.3398 | -123.5916 | -123.5641
300.9844 | 123.4589 | -61.1435 | 62.1964 | 0.30223 | 0.011654 | -0.0082804 | 0.019437 | 0.044645 | -0.0015754 | 0.072791 | -61.3174 | 62.384 | -61.3998 | -61.2305 | 62.1094 | 0.07782 | -0.10071 | 0.22888 | 62.2375 | -61.3678 | -0.25635 | 0.18768 | -0.17395 | -0.086975 | -0.086975 | -0.2243 | 0.041199 | 0.082397 | 61.0428 | 61.3724 | 123.2529 | 123.5275 | -0.17395 | 123.381 | 61.2213 | -0.2243 | 123.5275 | -0.17395 | 61.2213 | 123.2529 | 123.381 | -123.5962 | -123.5641
301.9219 | 123.5275 | -61.0703 | 62.1826 | -0.0029495 | -0.0043672 | -0.037119 | -0.0083338 | 0.054258 | -0.02187 | 0.06211 | -61.2717 | 62.3199 | -61.3998 | -61.4044 | 61.9904 | -0.022888 | 0 | 0.11902 | 62.3016 | -61.3861 | -0.32959 | 0.13733 | -0.20142 | -0.33417 | -0.19226 | -0.31586 | 0.11902 | 0.12817 | 61.0703 | 61.1893 | 123.0606 | 123.3902 | -0.20142 | 123.3719 | 61.0474 | -0.31586 | 123.3902 | -0.20142 | 61.0474 | 123.0606 | 123.3719 | -123.5825 | -123.5687
302.9844 | 123.587 | -61.0657 | 62.1872 | -0.53701 | -0.017185 | -0.032847 | 0.0055522 | 0.046781 | -0.012257 | 0.071723 | -61.1893 | 62.3108 | -61.3449 | -61.441 | 61.9583 | -0.041199 | 0.07782 | 0.059509 | 62.3016 | -61.3953 | -0.27924 | 0.1236 | -0.1236 | -0.37537 | -0.22888 | -0.32959 | 0.11444 | 0.15564 | 61.1435 | 61.1252 | 123.024 | 123.3765 | -0.1236 | 123.3673 | 61.0245 | -0.32959 | 123.3765 | -0.1236 | 61.0245 | 123.024 | 123.3673 | -123.5321 | -123.5825
303.9219 | 123.5458 | -61.0794 | 62.1964 | 0.13438 | -0.018253 | -0.013621 | 0.0066202 | 0.045713 | -0.028278 | 0.069587 | -61.2854 | 62.2971 | -61.409 | -61.3724 | 62.0132 | 0.013733 | 0.009155 | 0.1236 | 62.2696 | -61.3815 | -0.32959 | 0.10071 | -0.20599 | -0.29297 | -0.18311 | -0.30212 | 0.073242 | 0.1236 | 61.0886 | 61.203 | 123.0927 | 123.3765 | -0.20599 | 123.349 | 61.0931 | -0.30212 | 123.3765 | -0.20599 | 61.0931 | 123.0927 | 123.349 | -123.6053 | -123.5779
304.9844 | 123.5046 | -61.0886 | 62.1689 | 0.33274 | -0.0043672 | -0.0082804 | -0.0019248 | 0.043577 | -0.011188 | 0.067451 | -61.2625 | 62.2696 | -61.3998 | -61.3815 | 62.0087 | -0.004578 | 0.009155 | 0.1236 | 62.2696 | -61.3907 | -0.31128 | 0.10071 | -0.17395 | -0.29297 | -0.16022 | -0.30212 | 0.10071 | 0.13733 | 61.0977 | 61.2122 | 123.0972 | 123.3582 | -0.17395 | 123.3582 | 61.084 | -0.30212 | 123.3582 | -0.17395 | 61.084 | 123.0972 | 123.3582 | -123.5687 | -123.5596
305.9219 | 123.5825 | -61.0703 | 62.2055 | -0.23183 | -0.01398 | -0.032847 | -0.013674 | 0.042508 | -0.029346 | 0.063178 | -61.1984 | 62.3108 | -61.3678 | -61.409 | 61.9537 | -0.027466 | 0.054932 | 0.07782 | 62.3154 | -61.3815 | -0.29755 | 0.10529 | -0.12817 | -0.33875 | -0.25177 | -0.31128 | 0.10986 | 0.16937 | 61.1252 | 61.1481 | 123.024 | 123.381 | -0.12817 | 123.3856 | 61.0428 | -0.31128 | 123.381 | -0.12817 | 61.0428 | 123.024 | 123.3856 | -123.5733 | -123.587
306.9219 | 123.5504 | -61.0611 | 62.2101 | -0.094502 | -0.0065042 | -0.036051 | 0.0023482 | 0.0361 | -0.025074 | 0.070655 | -61.2488 | 62.2879 | -61.3907 | -61.4227 | 61.972 | -0.018311 | 0.036621 | 0.10071 | 62.3428 | -61.3678 | -0.32959 | 0.07782 | -0.18768 | -0.36163 | -0.23804 | -0.3067 | 0.13275 | 0.14191 | 61.0977 | 61.1618 | 123.0331 | 123.349 | -0.18768 | 123.4039 | 61.0428 | -0.3067 | 123.349 | -0.18768 | 61.0428 | 123.0331 | 123.4039 | -123.6008 | -123.5779
307.9219 | 123.4955 | -61.1023 | 62.233 | -0.30813 | -0.0011632 | -0.031779 | 0.020506 | 0.044645 | 0.0016286 | 0.06211 | -61.2259 | 62.3978 | -61.3861 | -61.2625 | 62.0728 | 0.064087 | -0.059509 | 0.19684 | 62.2787 | -61.3495 | -0.28381 | 0.16479 | -0.1236 | -0.16022 | -0.16022 | -0.24719 | 0.045777 | 0.16022 | 61.0428 | 61.2991 | 123.175 | 123.5001 | -0.1236 | 123.381 | 61.1664 | -0.24719 | 123.5001 | -0.1236 | 61.1664 | 123.175 | 123.381 | -123.6191 | -123.5825
308.9844 | 123.5367 | -61.1023 | 62.178 | 0.33274 | -0.01398 | -0.044596 | 0.0012792 | 0.054258 | -0.016529 | 0.067451 | -61.235 | 62.3062 | -61.4044 | -61.409 | 61.9858 | -0.050354 | 0.032043 | 0.091553 | 62.2833 | -61.3861 | -0.30212 | 0.12817 | -0.13275 | -0.3067 | -0.19226 | -0.28381 | 0.10528 | 0.16937 | 61.1343 | 61.1938 | 123.0881 | 123.4085 | -0.13275 | 123.3856 | 61.0519 | -0.28381 | 123.4085 | -0.13275 | 61.0519 | 123.0881 | 123.3856 | -123.5825 | -123.5641
309.9219 | 123.5229 | -61.0931 | 62.2055 | 0.042827 | -0.010776 | -0.039256 | -0.0019248 | 0.046781 | -0.019733 | 0.06211 | -61.2991 | 62.2879 | -61.4136 | -61.3678 | 62.0132 | 0 | -0.004578 | 0.14191 | 62.2833 | -61.3724 | -0.32043 | 0.082398 | -0.20599 | -0.27466 | -0.19226 | -0.27923 | 0.07782 | 0.11444 | 61.0886 | 61.235 | 123.1064 | 123.381 | -0.20599 | 123.3765 | 61.0931 | -0.27923 | 123.381 | -0.20599 | 61.0931 | 123.1064 | 123.3765 | -123.6191 | -123.5779
310.9688 | 123.4772 | -61.0931 | 62.1918 | 0.48533 | 0.011654 | 0.0088096 | 0.021574 | 0.048917 | -0.0026434 | 0.057838 | -61.2717 | 62.3657 | -61.4227 | -61.2946 | 62.059 | 0.018311 | -0.045776 | 0.1831 | 62.2559 | -61.4044 | -0.32959 | 0.17395 | -0.17853 | -0.20142 | -0.13275 | -0.31128 | 0.064087 | 0.15106 | 61.0474 | 61.2762 | 123.1522 | 123.4589 | -0.17853 | 123.349 | 61.1115 | -0.31128 | 123.4589 | -0.17853 | 61.1115 | 123.1522 | 123.349 | -123.6145 | -123.5962
311.9219 | 123.5458 | -61.0748 | 62.1689 | -0.048725 | -0.0022312 | -0.037119 | 0.00021117 | 0.057462 | -0.014393 | 0.066383 | -61.2534 | 62.2971 | -61.3953 | -61.4182 | 61.9812 | -0.032043 | 0.041199 | 0.10071 | 62.3154 | -61.377 | -0.32043 | 0.12817 | -0.17853 | -0.34332 | -0.18768 | -0.30212 | 0.14648 | 0.14191 | 61.116 | 61.1755 | 123.056 | 123.3719 | -0.17853 | 123.3902 | 61.0428 | -0.30212 | 123.3719 | -0.17853 | 61.0428 | 123.056 | 123.3902 | -123.5641 | -123.5458
312.9219 | 123.4131 | -61.1252 | 62.2101 | -0.048725 | -0.0075722 | -0.014689 | 0.030119 | 0.056394 | -0.0037124 | 0.05677 | -61.203 | 62.4298 | -61.3953 | -61.2625 | 62.0636 | 0.041199 | -0.050354 | 0.17853 | 62.2604 | -61.3953 | -0.27008 | 0.21973 | -0.07782 | -0.13733 | -0.14648 | -0.27008 | 0.050354 | 0.19226 | 61.0748 | 61.3037 | 123.1888 | 123.555 | -0.07782 | 123.3856 | 61.1664 | -0.27008 | 123.555 | -0.07782 | 61.1664 | 123.1888 | 123.3856 | -123.6053 | -123.6053
313.9844 | 123.5413 | -61.0703 | 62.1689 | 0.48533 | -0.01398 | -0.026438 | 0.00021117 | 0.044645 | -0.011188 | 0.068519 | -61.2076 | 62.2879 | -61.3861 | -61.528 | 61.7065 | -0.036621 | 0.21057 | 0.09613 | 62.3108 | -61.4044 | -0.31586 | 0.11902 | -0.13733 | -0.45776 | -0.46234 | -0.33417 | 0.14191 | 0.17853 | 61.2808 | 61.1664 | 122.7768 | 123.3582 | -0.13733 | 123.381 | 61.0336 | -0.33417 | 123.3582 | -0.13733 | 61.0336 | 122.7768 | 123.381 | -123.555 | -123.5733
314.9219 | 123.5458 | -61.0931 | 62.1918 | -0.033467 | -0.0097082 | -0.018961 | -0.0029928 | 0.047849 | -0.019733 | 0.081336 | -61.2717 | 62.2879 | -61.4227 | -61.3907 | 61.9904 | -0.009155 | 0.013733 | 0.11444 | 62.2833 | -61.377 | -0.32959 | 0.096131 | -0.17853 | -0.29755 | -0.20142 | -0.28381 | 0.091553 | 0.15106 | 61.1069 | 61.2076 | 123.0835 | 123.381 | -0.17853 | 123.3765 | 61.084 | -0.28381 | 123.381 | -0.17853 | 61.084 | 123.0835 | 123.3765 | -123.6145 | -123.5687
315.9219 | 123.5001 | -61.1023 | 62.1872 | 0.14964 | -0.0075722 | -0.027506 | -0.01047 | 0.043577 | -0.018665 | 0.075996 | -61.2854 | 62.2879 | -61.4044 | -61.3586 | 62.0316 | -0.018311 | 0.004578 | 0.14648 | 62.2696 | -61.3724 | -0.30212 | 0.10071 | -0.18311 | -0.25635 | -0.15564 | -0.27008 | 0.082397 | 0.11902 | 61.1069 | 61.2488 | 123.1338 | 123.3902 | -0.18311 | 123.3719 | 61.084 | -0.27008 | 123.3902 | -0.18311 | 61.084 | 123.1338 | 123.3719 | -123.5916 | -123.5596
316.9219 | 123.5229 | -61.0794 | 62.2101 | 1.5992 | -0.019321 | -0.027506 | 0.0087562 | 0.030759 | -0.024006 | 0.070655 | -61.2259 | 62.3199 | -61.3953 | -61.3907 | 61.9858 | -0.018311 | 0.004578 | 0.13275 | 62.2787 | -61.3907 | -0.31586 | 0.10986 | -0.14648 | -0.31128 | -0.2243 | -0.31128 | 0.068665 | 0.16937 | 61.084 | 61.2122 | 123.0652 | 123.3994 | -0.14648 | 123.3582 | 61.0611 | -0.31128 | 123.3994 | -0.14648 | 61.0611 | 123.0652 | 123.3582 | -123.6053 | -123.6008
317.9219 | 123.4634 | -61.1114 | 62.2604 | -0.29287 | -0.019321 | -0.028574 | 0.015165 | 0.051053 | -0.0069164 | 0.071723 | -61.2717 | 62.3932 | -61.3953 | -61.2442 | 62.1094 | 0.1236 | -0.10529 | 0.25177 | 62.2833 | -61.3632 | -0.28381 | 0.13275 | -0.16022 | -0.13275 | -0.15106 | -0.25177 | 0.022888 | 0.1236 | 61.0062 | 61.3632 | 123.2208 | 123.5046 | -0.16022 | 123.3948 | 61.235 | -0.25177 | 123.5046 | -0.16022 | 61.235 | 123.2208 | 123.3948 | -123.6557 | -123.6237
318.9219 | 123.5092 | -61.0748 | 62.2055 | 0.073345 | -9.5248e-05 | -0.030711 | -0.013674 | 0.051053 | -0.028278 | 0.067451 | -61.2854 | 62.2787 | -61.4182 | -61.3678 | 62.027 | 0.064087 | 0.013733 | 0.16937 | 62.2925 | -61.3678 | -0.34332 | 0.073243 | -0.21057 | -0.29297 | -0.17853 | -0.29297 | 0.086975 | 0.13275 | 61.0886 | 61.2442 | 123.1018 | 123.3536 | -0.21057 | 123.3673 | 61.1389 | -0.29297 | 123.3536 | -0.21057 | 61.1389 | 123.1018 | 123.3673 | -123.6237 | -123.5733
319.9844 | 123.4818 | -61.1206 | 62.1872 | 0.65318 | 0.00097275 | -0.012553 | 0.0034162 | 0.046781 | -0.0090524 | 0.066383 | -61.2808 | 62.3474 | -61.4182 | -61.2625 | 62.0865 | 0.059509 | -0.07782 | 0.20142 | 62.2375 | -61.3586 | -0.29755 | 0.16022 | -0.16022 | -0.14191 | -0.10071 | -0.23804 | 0.050354 | 0.13733 | 61.0428 | 61.322 | 123.2071 | 123.468 | -0.16022 | 123.3582 | 61.1801 | -0.23804 | 123.468 | -0.16022 | 61.1801 | 123.2071 | 123.3582 | -123.6053 | -123.5458
320.9219 | 123.5641 | -61.0748 | 62.178 | -0.094502 | -0.01398 | -0.010416 | -0.0029928 | 0.038236 | -0.022938 | 0.068519 | -61.2305 | 62.3291 | -61.3953 | -61.4182 | 61.9492 | -0.032043 | 0.073242 | 0.091553 | 62.3245 | -61.3724 | -0.32043 | 0.15106 | -0.15564 | -0.34332 | -0.22888 | -0.29755 | 0.14648 | 0.16479 | 61.1481 | 61.1664 | 123.024 | 123.4039 | -0.15564 | 123.3994 | 61.0428 | -0.29755 | 123.4039 | -0.15564 | 61.0428 | 123.024 | 123.3994 | -123.5733 | -123.5504
321.9844 | 123.5138 | -61.0886 | 62.1918 | 0.37852 | -0.01398 | -0.022166 | 0.0044842 | 0.042508 | -0.02187 | 0.064246 | -61.2717 | 62.2925 | -61.409 | -61.3815 | 62.0224 | -0.013733 | 0 | 0.12817 | 62.2833 | -61.4044 | -0.32043 | 0.10071 | -0.1831 | -0.29297 | -0.16937 | -0.31586 | 0.091553 | 0.13733 | 61.0886 | 61.2167 | 123.111 | 123.381 | -0.1831 | 123.3719 | 61.0748 | -0.31586 | 123.381 | -0.1831 | 61.0748 | 123.111 | 123.3719 | -123.6008 | -123.5962
322.9219 | 123.4863 | -61.1023 | 62.2055 | -0.46071 | -0.0075722 | -0.013621 | 0.0044842 | 0.043577 | -0.02187 | 0.078132 | -61.235 | 62.3383 | -61.3953 | -61.2808 | 62.0636 | 0.07782 | -0.068665 | 0.20142 | 62.3016 | -61.3724 | -0.29297 | 0.13275 | -0.13275 | -0.17853 | -0.14191 | -0.27008 | 0.096131 | 0.16022 | 61.0336 | 61.3037 | 123.1659 | 123.4406 | -0.13275 | 123.4039 | 61.1801 | -0.27008 | 123.4406 | -0.13275 | 61.1801 | 123.1659 | 123.4039 | -123.6008 | -123.5779
323.9844 | 123.6008 | -61.0428 | 62.178 | -0.079243 | -0.011844 | -0.012553 | 0.0023482 | 0.039304 | -0.016529 | 0.075996 | -61.2442 | 62.2879 | -61.3953 | -61.4136 | 61.9766 | -0.022888 | 0.054932 | 0.10529 | 62.2696 | -61.3861 | -0.35248 | 0.10986 | -0.20142 | -0.37079 | -0.20142 | -0.34332 | 0.091552 | 0.15106 | 61.0977 | 61.1481 | 123.0194 | 123.3307 | -0.20142 | 123.3124 | 61.0199 | -0.34332 | 123.3307 | -0.20142 | 61.0199 | 123.0194 | 123.3124 | -123.5733 | -123.5641
324.9219 | 123.5275 | -61.0977 | 62.2009 | 0.01231 | -0.0011632 | -0.030711 | -0.0019248 | 0.039304 | -0.018665 | 0.071723 | -61.2854 | 62.2833 | -61.4136 | -61.3586 | 62.0178 | 0.013733 | -0.022888 | 0.14648 | 62.2696 | -61.3998 | -0.31586 | 0.082397 | -0.18768 | -0.26093 | -0.18311 | -0.30212 | 0.068664 | 0.12817 | 61.0748 | 61.2442 | 123.1155 | 123.381 | -0.18768 | 123.3673 | 61.1115 | -0.30212 | 123.381 | -0.18768 | 61.1115 | 123.1155 | 123.3673 | -123.6145 | -123.6008
325.9219 | 123.5092 | -61.0886 | 62.2009 | 0.21067 | -0.0097082 | -0.021098 | 0.00021117 | 0.055326 | -0.022938 | 0.077064 | -61.2671 | 62.2742 | -61.3998 | -61.3678 | 62.0178 | -0.004578 | -0.013733 | 0.14648 | 62.2742 | -61.3724 | -0.31128 | 0.073242 | -0.17853 | -0.27924 | -0.18311 | -0.28381 | 0.073242 | 0.13275 | 61.0748 | 61.235 | 123.1064 | 123.3627 | -0.17853 | 123.3627 | 61.084 | -0.28381 | 123.3627 | -0.17853 | 61.084 | 123.1064 | 123.3627 | -123.6008 | -123.5733
326.9844 | 123.4497 | -61.1435 | 62.2284 | 0.39378 | -0.012912 | -0.00080337 | 0.015165 | 0.05319 | -0.0058484 | 0.068519 | -61.29 | 62.3611 | -61.4319 | -61.29 | 62.0682 | 0.082397 | -0.10986 | 0.21515 | 62.2421 | -61.3724 | -0.28839 | 0.13275 | -0.14648 | -0.14648 | -0.16022 | -0.22888 | 0.013732 | 0.14191 | 61.0336 | 61.3586 | 123.2117 | 123.5046 | -0.14648 | 123.3856 | 61.2259 | -0.22888 | 123.5046 | -0.14648 | 61.2259 | 123.2117 | 123.3856 | -123.6603 | -123.6008
327.9219 | 123.4543 | -61.1069 | 62.2192 | 0.97361 | -0.0075722 | -0.04246 | 0.019437 | 0.044645 | -0.014393 | 0.080268 | -61.2579 | 62.3611 | -61.4456 | -61.2305 | 62.0956 | 0.091553 | -0.11902 | 0.23346 | 62.2742 | -61.3632 | -0.33875 | 0.14191 | -0.15106 | -0.1236 | -0.1236 | -0.25635 | 0.054932 | 0.18768 | 60.9879 | 61.3403 | 123.2025 | 123.468 | -0.15106 | 123.381 | 61.1984 | -0.25635 | 123.468 | -0.15106 | 61.1984 | 123.2025 | 123.381 | -123.6649 | -123.5825
328.9844 | 123.5321 | -61.1023 | 62.1643 | 0.30223 | -0.0075722 | 0.0024006 | 0.00021117 | 0.051053 | -0.019733 | 0.069587 | -61.235 | 62.2787 | -61.409 | -61.4136 | 62.0041 | -0.041199 | 0.027466 | 0.10529 | 62.3016 | -61.4136 | -0.3067 | 0.11444 | -0.13275 | -0.31128 | -0.16022 | -0.31128 | 0.13733 | 0.17395 | 61.1298 | 61.2076 | 123.1064 | 123.381 | -0.13275 | 123.4039 | 61.0611 | -0.31128 | 123.381 | -0.13275 | 61.0611 | 123.1064 | 123.4039 | -123.5733 | -123.5779
329.9219 | 123.5321 | -61.0931 | 62.1689 | 0.33274 | 0.0020408 | -0.020029 | -0.0051288 | 0.043577 | -0.018665 | 0.071723 | -61.2488 | 62.3062 | -61.3998 | -61.3998 | 62.0361 | -0.032043 | 0.009155 | 0.11444 | 62.2742 | -61.4044 | -0.3067 | 0.13733 | -0.15564 | -0.3067 | -0.13275 | -0.31128 | 0.10529 | 0.15106 | 61.1023 | 61.2076 | 123.1293 | 123.3994 | -0.15564 | 123.3673 | 61.0611 | -0.31128 | 123.3994 | -0.15564 | 61.0611 | 123.1293 | 123.3673 | -123.5687 | -123.5733
330.9844 | 123.5367 | -61.0794 | 62.1872 | 0.37852 | -0.0032992 | -0.034983 | 0.0034162 | 0.04144 | -0.016529 | 0.058906 | -61.2396 | 62.2833 | -61.3998 | -61.3998 | 62.0087 | -0.018311 | -0.004578 | 0.12817 | 62.265 | -61.3953 | -0.32043 | 0.09613 | -0.16022 | -0.32043 | -0.17853 | -0.31586 | 0.07782 | 0.16022 | 61.0748 | 61.2076 | 123.0881 | 123.3627 | -0.16022 | 123.3444 | 61.0611 | -0.31586 | 123.3627 | -0.16022 | 61.0611 | 123.0881 | 123.3444 | -123.587 | -123.5825
331.9219 | 123.4909 | -61.0703 | 62.178 | 0.13438 | -0.0011632 | -0.037119 | 0.0012792 | 0.044645 | -0.028278 | 0.072791 | -61.29 | 62.3199 | -61.3815 | -61.3586 | 62.027 | 0.009155 | -0.032043 | 0.14648 | 62.2971 | -61.3724 | -0.31128 | 0.14191 | -0.21973 | -0.28839 | -0.15106 | -0.30212 | 0.11902 | 0.091553 | 61.0382 | 61.2167 | 123.0972 | 123.3902 | -0.21973 | 123.3673 | 61.0794 | -0.30212 | 123.3902 | -0.21973 | 61.0794 | 123.0972 | 123.3673 | -123.5596 | -123.5504
332.9844 | 123.436 | -61.1069 | 62.2147 | -5.0231 | -0.0054352 | 0.0056046 | 0.016233 | 0.038236 | -0.0090524 | 0.065314 | -61.3449 | 62.3795 | -61.4136 | -61.2625 | 62.0682 | 0.059509 | -0.10529 | 0.22888 | 62.265 | -61.3724 | -0.3067 | 0.16479 | -0.23804 | -0.15564 | -0.14648 | -0.2655 | 0.050354 | 0.068664 | 61.0016 | 61.3358 | 123.175 | 123.4863 | -0.23804 | 123.3719 | 61.1664 | -0.2655 | 123.4863 | -0.23804 | 61.1664 | 123.175 | 123.3719 | -123.6282 | -123.587
333.9219 | 123.5046 | -61.0886 | 62.1872 | 0.10386 | -0.01398 | -0.024302 | -0.0094018 | 0.05319 | -0.015461 | 0.06211 | -61.2762 | 62.3016 | -61.3907 | -61.4044 | 62.0224 | 0.027466 | -0.013733 | 0.1236 | 62.265 | -61.3586 | -0.30212 | 0.11444 | -0.18768 | -0.31586 | -0.1648 | -0.27008 | 0.07782 | 0.11444 | 61.0748 | 61.2122 | 123.111 | 123.3902 | -0.18768 | 123.3536 | 61.116 | -0.27008 | 123.3902 | -0.18768 | 61.116 | 123.111 | 123.3536 | -123.5779 | -123.5458
334.9844 | 123.4863 | -61.1298 | 62.2009 | -1.1016 | 0.00097275 | -0.015757 | 0.02371 | 0.048917 | 0.014446 | 0.070655 | -61.2534 | 62.3749 | -61.4044 | -61.2396 | 62.1002 | 0.064087 | -0.045776 | 0.18768 | 62.2925 | -61.3632 | -0.27466 | 0.17395 | -0.1236 | -0.10986 | -0.10071 | -0.23346 | 0.091552 | 0.15106 | 61.084 | 61.3174 | 123.23 | 123.5046 | -0.1236 | 123.4222 | 61.1938 | -0.23346 | 123.5046 | -0.1236 | 61.1938 | 123.23 | 123.4222 | -123.6053 | -123.5641
335.9219 | 123.5413 | -61.1069 | 62.1689 | 0.4243 | -0.0065042 | -0.028574 | 0.0066202 | 0.047849 | 0.0059006 | 0.080268 | -61.2167 | 62.3062 | -61.4182 | -61.5601 | 61.7432 | -0.013733 | 0.2243 | 0.073242 | 62.3108 | -61.4044 | -0.31128 | 0.13733 | -0.10986 | -0.45319 | -0.42572 | -0.29755 | 0.14191 | 0.20142 | 61.3312 | 61.1801 | 122.85 | 123.4131 | -0.10986 | 123.4177 | 61.0931 | -0.29755 | 123.4131 | -0.10986 | 61.0931 | 122.85 | 123.4177 | -123.587 | -123.5733
336.9844 | 123.4543 | -61.1069 | 62.1964 | 0.4243 | 0.00097275 | -0.021098 | 0.014097 | 0.040372 | -0.0026434 | 0.057838 | -61.3312 | 62.4069 | -61.441 | -61.2305 | 62.1048 | 0.09613 | -0.11444 | 0.22888 | 62.2192 | -61.3907 | -0.33417 | 0.21057 | -0.2243 | -0.1236 | -0.091553 | -0.28381 | 0.022888 | 0.10986 | 60.9924 | 61.3358 | 123.2117 | 123.5138 | -0.2243 | 123.3261 | 61.203 | -0.28381 | 123.5138 | -0.2243 | 61.203 | 123.2117 | 123.3261 | -123.6374 | -123.587
337.9219 | 123.5641 | -61.084 | 62.1689 | 0.4243 | -0.0043672 | -0.011485 | 0.0012792 | 0.048917 | -0.014393 | 0.061042 | -61.1938 | 62.2971 | -61.409 | -61.3861 | 61.972 | -0.091553 | 0.073242 | 0.10529 | 62.2925 | -61.4136 | -0.32501 | 0.12817 | -0.10986 | -0.30212 | -0.19684 | -0.32959 | 0.1236 | 0.21515 | 61.1572 | 61.1893 | 123.056 | 123.381 | -0.10986 | 123.3765 | 60.9924 | -0.32959 | 123.381 | -0.10986 | 60.9924 | 123.056 | 123.3765 | -123.5779 | -123.5825
338.9219 | 123.5687 | -61.1023 | 62.1689 | 0.48533 | -0.0011632 | -0.020029 | 0.00021117 | 0.043577 | 0.0016286 | 0.069587 | -61.2122 | 62.3291 | -61.409 | -61.4273 | 61.9583 | -0.054932 | 0.050354 | 0.091553 | 62.2833 | -61.4227 | -0.3067 | 0.16022 | -0.10986 | -0.32501 | -0.21057 | -0.32043 | 0.11444 | 0.19684 | 61.1526 | 61.1938 | 123.0606 | 123.4314 | -0.10986 | 123.3856 | 61.0474 | -0.32043 | 123.4314 | -0.10986 | 61.0474 | 123.0606 | 123.3856 | -123.5779 | -123.5916
339.9844 | 123.4543 | -61.1298 | 62.1918 | 2.5605 | -9.5248e-05 | -0.017893 | 0.014097 | 0.043577 | -0.011188 | 0.070655 | -61.1938 | 62.384 | -61.4319 | -61.2717 | 62.1094 | 0.086975 | -0.091553 | 0.2243 | 62.233 | -61.3724 | -0.30212 | 0.19226 | -0.064087 | -0.14191 | -0.082397 | -0.24261 | 0.041199 | 0.23804 | 61.0382 | 61.3541 | 123.2391 | 123.5138 | -0.064087 | 123.3627 | 61.2167 | -0.24261 | 123.5138 | -0.064087 | 61.2167 | 123.2391 | 123.3627 | -123.6237 | -123.5641
340.9219 | 123.4955 | -61.0794 | 62.178 | 0.40904 | -0.0032992 | -0.029642 | 0.0012792 | 0.059598 | -0.017597 | 0.061042 | -61.203 | 62.3245 | -61.3815 | -61.4365 | 61.9766 | 0 | 0.10986 | -0.073242 | 62.2421 | -61.4273 | -0.30212 | 0.14648 | -0.1236 | -0.35705 | -0.20142 | -0.3479 | 0.064086 | 0.17853 | 61.1893 | 61.0062 | 123.056 | 123.4039 | -0.1236 | 123.3215 | 61.0794 | -0.3479 | 123.4039 | -0.1236 | 61.0794 | 123.056 | 123.3215 | -123.5596 | -123.6053
341.9219 | 123.5413 | -61.084 | 62.1368 | 0.39378 | 0.0020408 | -0.010416 | 0.0012792 | 0.051053 | -0.012257 | 0.065314 | -61.2122 | 62.3016 | -61.3953 | -61.4044 | 61.9766 | -0.054932 | 0.041199 | 0.091553 | 62.2742 | -61.3953 | -0.31128 | 0.1648 | -0.12817 | -0.32043 | -0.16022 | -0.31128 | 0.13733 | 0.18311 | 61.1252 | 61.1755 | 123.0606 | 123.3856 | -0.12817 | 123.3582 | 61.0291 | -0.31128 | 123.3856 | -0.12817 | 61.0291 | 123.0606 | 123.3582 | -123.5321 | -123.5321
342.9844 | 123.4268 | -61.1664 | 62.2055 | 0.073345 | -9.5248e-05 | -0.0018714 | 0.024778 | 0.047849 | 0.0026966 | 0.066383 | -61.29 | 62.4069 | -61.409 | -61.2259 | 62.1552 | 0.11444 | -0.14648 | 0.27008 | 62.2421 | -61.3953 | -0.24262 | 0.20142 | -0.1236 | -0.059509 | -0.050354 | -0.22888 | 0.036621 | 0.11902 | 61.0199 | 61.4365 | 123.3215 | 123.5733 | -0.1236 | 123.4085 | 61.2808 | -0.22888 | 123.5733 | -0.1236 | 61.2808 | 123.3215 | 123.4085 | -123.6145 | -123.6008
343.9219 | 123.436 | -61.116 | 62.2101 | 1.6755 | -0.0054352 | -0.013621 | 0.0044842 | 0.056394 | -0.011188 | 0.069587 | -61.2442 | 62.3978 | -61.409 | -61.2579 | 62.1048 | 0.064087 | -0.091553 | 0.21515 | 62.2513 | -61.377 | -0.29297 | 0.18768 | -0.12817 | -0.14191 | -0.10529 | -0.26093 | 0.041199 | 0.16479 | 61.0245 | 61.3312 | 123.2208 | 123.5138 | -0.12817 | 123.3673 | 61.1801 | -0.26093 | 123.5138 | -0.12817 | 61.1801 | 123.2208 | 123.3673 | -123.6191 | -123.587
344.9844 | 123.4818 | -61.1023 | 62.1964 | -0.033467 | -0.0043672 | -0.022166 | 0.015165 | 0.060666 | 0.0059006 | 0.05677 | -61.2167 | 62.4115 | -61.3998 | -61.2946 | 62.0682 | 0.064087 | -0.041199 | 0.18768 | 62.2742 | -61.377 | -0.29755 | 0.21515 | -0.11444 | -0.19226 | -0.12817 | -0.27466 | 0.07782 | 0.18311 | 61.0611 | 61.29 | 123.1705 | 123.5138 | -0.11444 | 123.3765 | 61.1664 | -0.27466 | 123.5138 | -0.11444 | 61.1664 | 123.1705 | 123.3765 | -123.5962 | -123.5733
345.9219 | 123.4863 | -61.1023 | 62.1872 | 0.25645 | 0.00097275 | 0.0024006 | 0.0076882 | 0.046781 | -0.0037124 | 0.075996 | -61.3037 | 62.4069 | -61.4456 | -61.2946 | 62.0956 | 0.054932 | -0.059509 | 0.19684 | 62.2696 | -61.3724 | -0.34332 | 0.21973 | -0.20142 | -0.19226 | -0.091553 | -0.27008 | 0.082397 | 0.14191 | 61.0428 | 61.2991 | 123.1979 | 123.5092 | -0.20142 | 123.3719 | 61.1572 | -0.27008 | 123.5092 | -0.20142 | 61.1572 | 123.1979 | 123.3719 | -123.6328 | -123.5596
346.9844 | 123.4451 | -61.0977 | 62.2375 | -2.4138 | -0.0022312 | 0.00026463 | -0.0029928 | 0.059598 | -0.0026434 | 0.067451 | -61.4685 | 62.4435 | -61.4548 | -61.2808 | 62.1094 | 0.15564 | -0.073242 | 0.26093 | 62.2925 | -61.3586 | -0.35706 | 0.20599 | -0.37079 | -0.18311 | -0.12817 | -0.26093 | 0.054931 | -0.013733 | 61.0245 | 61.3586 | 123.2071 | 123.5413 | -0.37079 | 123.3902 | 61.2534 | -0.26093 | 123.5413 | -0.37079 | 61.2534 | 123.2071 | 123.3902 | -123.6923 | -123.5962
347.9219 | 123.4955 | -61.0931 | 62.1826 | 0.51585 | 0.0063138 | -0.0040084 | -0.00085683 | 0.033964 | -0.00050737 | 0.069587 | -61.2717 | 62.3657 | -61.4319 | -61.3358 | 62.0544 | 0.018311 | -0.036621 | 0.16479 | 62.2787 | -61.3953 | -0.33875 | 0.18311 | -0.17853 | -0.24261 | -0.12817 | -0.30212 | 0.096131 | 0.16022 | 61.0565 | 61.2579 | 123.1476 | 123.4589 | -0.17853 | 123.3719 | 61.1115 | -0.30212 | 123.4589 | -0.17853 | 61.1115 | 123.1476 | 123.3719 | -123.6145 | -123.5779
348.9844 | 123.4589 | -61.116 | 62.233 | -0.21657 | 0.00097275 | -0.031779 | 0.010892 | 0.064939 | 0.0037646 | 0.074928 | -61.235 | 62.4161 | -61.3998 | -61.2854 | 62.0636 | 0.064087 | -0.086975 | 0.21057 | 62.3108 | -61.3953 | -0.28381 | 0.18311 | -0.11902 | -0.16937 | -0.16937 | -0.27924 | 0.07782 | 0.1648 | 61.0291 | 61.3266 | 123.1796 | 123.5321 | -0.11902 | 123.4268 | 61.1801 | -0.27924 | 123.5321 | -0.11902 | 61.1801 | 123.1796 | 123.4268 | -123.6328 | -123.6282
349.9219 | 123.4222 | -61.1343 | 62.2101 | 0.19541 | 0.0095178 | -0.010416 | 0.00021117 | 0.047849 | 0.0026966 | 0.061042 | -61.3129 | 62.4023 | -61.4273 | -61.2305 | 62.114 | 0.09613 | -0.11444 | 0.24719 | 62.2559 | -61.377 | -0.29297 | 0.19226 | -0.17853 | -0.096131 | -0.09613 | -0.24262 | 0.045776 | 0.11444 | 61.0199 | 61.3815 | 123.2483 | 123.5367 | -0.17853 | 123.3902 | 61.2305 | -0.24262 | 123.5367 | -0.17853 | 61.2305 | 123.2483 | 123.3902 | -123.6374 | -123.587
350.9844 | 123.4268 | -61.1069 | 62.2009 | 0.088604 | 0.0052458 | 0.018423 | 0.014097 | 0.057462 | 0.0080376 | 0.063178 | -61.2579 | 62.4115 | -61.4273 | -61.2717 | 62.1002 | 0.091553 | -0.082397 | 0.22888 | 62.2559 | -61.3953 | -0.32043 | 0.21057 | -0.15106 | -0.16479 | -0.10071 | -0.28839 | 0.054931 | 0.16937 | 61.0245 | 61.3358 | 123.2071 | 123.5184 | -0.15106 | 123.3627 | 61.1984 | -0.28839 | 123.5184 | -0.15106 | 61.1984 | 123.2071 | 123.3627 | -123.6282 | -123.5962
351.9219 | 123.5733 | -61.1572 | 62.1964 | 0.43956 | 0.0020408 | -0.036051 | 0.0066202 | 0.054258 | 0.0037646 | 0.071723 | -61.29 | 62.4252 | -61.4548 | -61.2625 | 62.1185 | 0.09613 | -0.09613 | 0.31586 | 62.2055 | -61.3953 | -0.29755 | 0.22888 | -0.13275 | -0.10529 | -0.07782 | -0.23804 | 0.009155 | 0.1648 | 61.0611 | 61.4731 | 123.2758 | 123.5825 | -0.13275 | 123.3627 | 61.2534 | -0.23804 | 123.5825 | -0.13275 | 61.2534 | 123.2758 | 123.3627 | -123.6511 | -123.5916
352.9844 | 123.4222 | -61.0977 | 62.2284 | 1.2025 | 0.010586 | -0.0029404 | 0.0012792 | 0.059598 | -0.0079844 | 0.066383 | -61.235 | 62.3978 | -61.441 | -61.2579 | 62.0865 | 0.10986 | -0.11444 | 0.25635 | 62.3154 | -61.3724 | -0.34332 | 0.16937 | -0.13733 | -0.16022 | -0.14191 | -0.27466 | 0.086975 | 0.20599 | 60.9833 | 61.3541 | 123.1842 | 123.4955 | -0.13733 | 123.4131 | 61.2076 | -0.27466 | 123.4955 | -0.13733 | 61.2076 | 123.1842 | 123.4131 | -123.6694 | -123.6008
353.9219 | 123.468 | -61.1526 | 62.2238 | -0.36916 | -0.0022312 | -0.043528 | 0.0055522 | 0.057462 | 0.0069696 | 0.065314 | -61.1343 | 62.4207 | -61.4319 | -61.2396 | 62.0728 | 0.068665 | -0.09613 | 0.2243 | 62.2559 | -61.377 | -0.27924 | 0.19684 | 0.018311 | -0.086975 | -0.15106 | -0.2243 | 0.032043 | 0.29755 | 61.0565 | 61.377 | 123.2254 | 123.5733 | 0.018311 | 123.4085 | 61.2213 | -0.2243 | 123.5733 | 0.018311 | 61.2213 | 123.2254 | 123.4085 | -123.6557 | -123.6008
354.9844 | 123.4406 | -61.1023 | 62.2238 | 0.088604 | 0.0020408 | -0.023234 | 0.0066202 | 0.063871 | -0.0015754 | 0.078132 | -61.2442 | 62.4207 | -61.4227 | -61.29 | 62.0819 | 0.082397 | -0.09613 | 0.23346 | 62.2742 | -61.3953 | -0.32043 | 0.19684 | -0.14191 | -0.18768 | -0.14191 | -0.29297 | 0.050354 | 0.17853 | 61.0062 | 61.3358 | 123.1842 | 123.5229 | -0.14191 | 123.3765 | 61.1847 | -0.29297 | 123.5229 | -0.14191 | 61.1847 | 123.1842 | 123.3765 | -123.6465 | -123.6191
355.9219 | 123.4772 | -61.1114 | 62.2009 | 0.43956 | 0.00097275 | -0.0050764 | 0.0012792 | 0.05319 | -0.0026434 | 0.066383 | -61.2854 | 62.3795 | -61.4365 | -61.3037 | 62.0773 | 0.045776 | -0.064087 | 0.20599 | 62.2696 | -61.4044 | -0.32501 | 0.17853 | -0.17395 | -0.19226 | -0.1236 | -0.29297 | 0.068664 | 0.15106 | 61.0474 | 61.3174 | 123.1888 | 123.4909 | -0.17395 | 123.381 | 61.1572 | -0.29297 | 123.4909 | -0.17395 | 61.1572 | 123.1888 | 123.381 | -123.6374 | -123.6053
356.9844 | 123.4222 | -61.0931 | 62.2238 | -0.49123 | -0.010776 | -0.030711 | -0.0029928 | 0.061735 | -0.011188 | 0.068519 | -61.29 | 62.4023 | -61.4182 | -61.2991 | 62.1094 | 0.12817 | -0.09613 | 0.26093 | 62.3016 | -61.3815 | -0.32501 | 0.17853 | -0.19684 | -0.20599 | -0.11444 | -0.28839 | 0.07782 | 0.12817 | 60.997 | 61.3541 | 123.2025 | 123.4955 | -0.19684 | 123.3948 | 61.2213 | -0.28839 | 123.4955 | -0.19684 | 61.2213 | 123.2025 | 123.3948 | -123.642 | -123.6053
357.9219 | 123.4543 | -61.1114 | 62.2009 | 0.10386 | 0.0073818 | -0.023234 | 0.011961 | 0.05853 | 0.011242 | 0.063178 | -61.2579 | 62.4207 | -61.4182 | -61.2717 | 62.0865 | 0.086975 | -0.082397 | 0.2243 | 62.2787 | -61.3861 | -0.3067 | 0.21973 | -0.14649 | -0.16022 | -0.11444 | -0.27466 | 0.07782 | 0.16022 | 61.0291 | 61.3358 | 123.1979 | 123.5321 | -0.14649 | 123.3902 | 61.1984 | -0.27466 | 123.5321 | -0.14649 | 61.1984 | 123.1979 | 123.3902 | -123.6191 | -123.587
358.9844 | 123.4268 | -61.1069 | 62.2513 | -0.44545 | -0.0011632 | 0.0098776 | 0.014097 | 0.054258 | -0.0069164 | 0.061042 | -61.29 | 62.4115 | -61.4365 | -61.0428 | 62.2055 | 0.041199 | -0.24261 | 0.29297 | 62.2604 | -61.3815 | -0.32959 | 0.16022 | -0.1831 | 0.064087 | -0.045777 | -0.27466 | 0.009155 | 0.14648 | 60.8643 | 61.3998 | 123.3124 | 123.5184 | -0.1831 | 123.3673 | 61.1481 | -0.27466 | 123.5184 | -0.1831 | 61.1481 | 123.3124 | 123.3673 | -123.6877 | -123.6328
359.9219 | 123.4131 | -61.1343 | 62.2055 | 0.19541 | 0.010586 | -0.02537 | 0.017301 | 0.05319 | 0.015514 | 0.067451 | -61.2671 | 62.4115 | -61.4227 | -61.2442 | 62.0911 | 0.086975 | -0.10529 | 0.27008 | 62.2833 | -61.3953 | -0.28839 | 0.20599 | -0.13275 | -0.10986 | -0.11444 | -0.26093 | 0.07782 | 0.15564 | 61.0291 | 61.4044 | 123.2254 | 123.5458 | -0.13275 | 123.4177 | 61.2213 | -0.26093 | 123.5458 | -0.13275 | 61.2213 | 123.2254 | 123.4177 | -123.6282 | -123.6008
360.9844 | 123.4634 | -61.1023 | 62.2604 | -0.68959 | 0.0063138 | -0.038187 | 0.0087562 | 0.060666 | -0.0069164 | 0.066383 | -61.2442 | 62.4435 | -61.4227 | -61.2625 | 62.0911 | 0.11902 | -0.10071 | 0.25177 | 62.3199 | -61.3724 | -0.32043 | 0.1831 | -0.14191 | -0.16022 | -0.16937 | -0.27008 | 0.059509 | 0.17853 | 61.0016 | 61.3541 | 123.1934 | 123.5458 | -0.14191 | 123.4222 | 61.2213 | -0.27008 | 123.5458 | -0.14191 | 61.2213 | 123.1934 | 123.4222 | -123.6832 | -123.6328
361.9219 | 123.4131 | -61.1435 | 62.1826 | 0.30223 | 0.0063138 | -0.024302 | 0.010892 | 0.060666 | 0.017651 | 0.069587 | -61.2991 | 62.4115 | -61.441 | -61.2717 | 62.1094 | 0.09613 | -0.11902 | 0.25635 | 62.2833 | -61.377 | -0.29755 | 0.22888 | -0.15564 | -0.12817 | -0.073242 | -0.23346 | 0.10071 | 0.14191 | 61.0245 | 61.3998 | 123.2529 | 123.555 | -0.15564 | 123.4268 | 61.2396 | -0.23346 | 123.555 | -0.15564 | 61.2396 | 123.2529 | 123.4268 | -123.6237 | -123.5596
362.9844 | 123.4863 | -61.1114 | 62.2101 | -0.12502 | -0.0043672 | -0.015757 | 0.011961 | 0.063871 | -0.0047804 | 0.0792 | -61.2671 | 62.4115 | -61.4365 | -61.2854 | 62.0682 | 0.064087 | -0.068665 | 0.21057 | 62.2925 | -61.409 | -0.32501 | 0.20142 | -0.15564 | -0.17395 | -0.14191 | -0.29755 | 0.082397 | 0.16937 | 61.0428 | 61.322 | 123.1796 | 123.5229 | -0.15564 | 123.4039 | 61.1755 | -0.29755 | 123.5229 | -0.15564 | 61.1755 | 123.1796 | 123.4039 | -123.6465 | -123.6191
363.9219 | 123.4543 | -61.116 | 62.2101 | 0.027569 | -9.5248e-05 | -0.013621 | 0.011961 | 0.057462 | -0.0090524 | 0.063178 | -61.2259 | 62.4115 | -61.4044 | -61.29 | 62.0819 | 0.082397 | -0.086975 | 0.23346 | 62.2787 | -61.3998 | -0.28839 | 0.20142 | -0.10986 | -0.17395 | -0.12817 | -0.28381 | 0.068665 | 0.17853 | 61.0291 | 61.3495 | 123.1979 | 123.5275 | -0.10986 | 123.3948 | 61.1984 | -0.28381 | 123.5275 | -0.10986 | 61.1984 | 123.1979 | 123.3948 | -123.6145 | -123.6099
364.9844 | 123.468 | -61.084 | 62.2375 | -0.29287 | -9.5248e-05 | -0.023234 | 0.0066202 | 0.061735 | -0.0037124 | 0.077064 | -61.2808 | 62.4161 | -61.4365 | -61.2671 | 62.0865 | 0.11902 | -0.091553 | 0.24719 | 62.3108 | -61.3815 | -0.35248 | 0.17853 | -0.19684 | -0.18311 | -0.15106 | -0.29755 | 0.073242 | 0.15564 | 60.9924 | 61.3312 | 123.1705 | 123.5001 | -0.19684 | 123.3948 | 61.203 | -0.29755 | 123.5001 | -0.19684 | 61.203 | 123.1705 | 123.3948 | -123.674 | -123.6191
365.9219 | 123.4085 | -61.1298 | 62.2055 | 0.042827 | -9.5248e-05 | -0.029642 | 0.010892 | 0.05319 | -0.0037124 | 0.06211 | -61.2762 | 62.4115 | -61.4227 | -61.2717 | 62.1048 | 0.10071 | -0.11902 | 0.24261 | 62.2787 | -61.3953 | -0.29297 | 0.20599 | -0.14648 | -0.14191 | -0.10071 | -0.2655 | 0.073243 | 0.14648 | 61.0107 | 61.3724 | 123.2346 | 123.5413 | -0.14648 | 123.4085 | 61.2305 | -0.2655 | 123.5413 | -0.14648 | 61.2305 | 123.2346 | 123.4085 | -123.6282 | -123.6008
366.9688 | 123.5779 | -61.0748 | 62.1964 | -0.18605 | -0.010776 | -0.031779 | -0.014742 | 0.047849 | -0.015461 | 0.075996 | -61.1984 | 62.3291 | -61.409 | -61.4777 | 61.94 | -0.045776 | 0.091553 | 0.07782 | 62.3383 | -61.4182 | -0.33417 | 0.13275 | -0.1236 | -0.40283 | -0.25635 | -0.34332 | 0.14191 | 0.21057 | 61.1664 | 61.1526 | 123.0148 | 123.4039 | -0.1236 | 123.4131 | 61.0291 | -0.34332 | 123.4039 | -0.1236 | 61.0291 | 123.0148 | 123.4131 | -123.6053 | -123.6145
367.9219 | 123.5275 | -61.1023 | 62.178 | 0.51585 | 0.0041778 | -0.029642 | 0.0098242 | 0.056394 | -0.0037124 | 0.069587 | -61.2625 | 62.3749 | -61.4365 | -61.3586 | 62.0178 | -0.018311 | -0.013733 | 0.13733 | 62.3108 | -61.4227 | -0.33417 | 0.19684 | -0.16022 | -0.25635 | -0.16022 | -0.32043 | 0.13275 | 0.17395 | 61.0886 | 61.2396 | 123.1201 | 123.4772 | -0.16022 | 123.4131 | 61.084 | -0.32043 | 123.4772 | -0.16022 | 61.084 | 123.1201 | 123.4131 | -123.6145 | -123.6008
368.9844 | 123.5138 | -61.084 | 62.2284 | -0.38442 | -0.011844 | -0.033915 | -0.01047 | 0.051053 | -0.018665 | 0.055701 | -61.2122 | 62.352 | -61.4044 | -61.409 | 61.9949 | 0.018311 | 0.013733 | 0.15564 | 62.3428 | -61.3998 | -0.32043 | 0.1236 | -0.12817 | -0.32501 | -0.23346 | -0.31586 | 0.11444 | 0.19226 | 61.0977 | 61.2396 | 123.0789 | 123.436 | -0.12817 | 123.4268 | 61.1023 | -0.31586 | 123.436 | -0.12817 | 61.1023 | 123.0789 | 123.4268 | -123.6328 | -123.6282
369.9219 | 123.4314 | -61.1069 | 62.2147 | 0.18016 | -0.0043672 | -0.041392 | 0.011961 | 0.044645 | 0.0016286 | 0.065314 | -61.2167 | 62.4298 | -61.3861 | -61.2808 | 62.0453 | 0.064087 | -0.064087 | 0.21973 | 62.2971 | -61.377 | -0.27923 | 0.21515 | -0.10986 | -0.17395 | -0.16937 | -0.27008 | 0.082397 | 0.16937 | 61.0428 | 61.3266 | 123.1522 | 123.5367 | -0.10986 | 123.4039 | 61.171 | -0.27008 | 123.5367 | -0.10986 | 61.171 | 123.1522 | 123.4039 | -123.6008 | -123.5916
370.9688 | 123.4451 | -61.1069 | 62.2192 | -0.033467 | -0.0086402 | -0.034983 | -0.0094018 | 0.055326 | -0.017597 | 0.06211 | -61.2671 | 62.3703 | -61.4365 | -61.2762 | 62.1002 | 0.10986 | -0.091553 | 0.24261 | 62.3199 | -61.3632 | -0.32959 | 0.15106 | -0.16022 | -0.16937 | -0.11902 | -0.25635 | 0.10071 | 0.16937 | 61.0153 | 61.3495 | 123.2071 | 123.4772 | -0.16022 | 123.4268 | 61.2167 | -0.25635 | 123.4772 | -0.16022 | 61.2167 | 123.2071 | 123.4268 | -123.6557 | -123.5825
371.9219 | 123.4314 | -61.0977 | 62.2192 | 0.21067 | -0.0065042 | -0.022166 | 0.021574 | 0.051053 | 0.0048326 | 0.070655 | -61.2671 | 62.4207 | -61.3998 | -61.2671 | 62.0682 | 0.073242 | -0.10529 | 0.2243 | 62.2742 | -61.4182 | -0.30212 | 0.20142 | -0.16937 | -0.16937 | -0.15106 | -0.32043 | 0.054932 | 0.13275 | 60.9924 | 61.322 | 123.1659 | 123.5184 | -0.16937 | 123.3719 | 61.171 | -0.32043 | 123.5184 | -0.16937 | 61.171 | 123.1659 | 123.3719 | -123.6191 | -123.6374
372.9688 | 123.5733 | -61.0611 | 62.2009 | -0.38442 | -0.0097082 | -0.018961 | -0.01047 | 0.042508 | -0.024006 | 0.072791 | -61.1893 | 62.3108 | -61.4136 | -61.4319 | 61.9629 | -0.036621 | 0.050354 | 0.10986 | 62.3474 | -61.409 | -0.35248 | 0.10986 | -0.12817 | -0.37079 | -0.23804 | -0.3479 | 0.14648 | 0.2243 | 61.1114 | 61.171 | 123.024 | 123.3719 | -0.12817 | 123.4085 | 61.0245 | -0.3479 | 123.3719 | -0.12817 | 61.0245 | 123.024 | 123.4085 | -123.6145 | -123.6099
373.9219 | 123.4589 | -61.1069 | 62.2101 | -0.58278 | 0.0052458 | -0.011485 | 0.010892 | 0.052121 | 0.0016286 | 0.06211 | -61.2076 | 62.3978 | -61.3953 | -61.2762 | 62.059 | 0.068665 | -0.059509 | 0.19684 | 62.3016 | -61.4044 | -0.28839 | 0.18768 | -0.10071 | -0.16937 | -0.15106 | -0.29755 | 0.091553 | 0.18768 | 61.0474 | 61.3037 | 123.1659 | 123.5046 | -0.10071 | 123.4085 | 61.1755 | -0.29755 | 123.5046 | -0.10071 | 61.1755 | 123.1659 | 123.4085 | -123.6053 | -123.6145
374.9844 | 123.4909 | -61.0794 | 62.2147 | -0.41494 | -0.015048 | -0.034983 | -0.00085683 | 0.052121 | -0.01012 | 0.057838 | -61.1938 | 62.3611 | -61.3861 | -61.3724 | 62.0041 | 0.013733 | -0.013733 | 0.16937 | 62.352 | -61.3998 | -0.3067 | 0.14648 | -0.11444 | -0.29297 | -0.21057 | -0.32043 | 0.13733 | 0.19226 | 61.0657 | 61.2488 | 123.0835 | 123.4406 | -0.11444 | 123.4314 | 61.0931 | -0.32043 | 123.4406 | -0.11444 | 61.0931 | 123.0835 | 123.4314 | -123.6008 | -123.6145
375.9219 | 123.4543 | -61.116 | 62.2101 | -0.0029495 | -0.0022312 | -0.0061444 | 0.0087562 | 0.046781 | 0.0048326 | 0.070655 | -61.2213 | 62.4161 | -61.4365 | -61.2625 | 62.0956 | 0.07782 | -0.082397 | 0.21515 | 62.2879 | -61.4136 | -0.32043 | 0.20599 | -0.10529 | -0.14648 | -0.11444 | -0.29755 | 0.07782 | 0.21515 | 61.0336 | 61.3312 | 123.2117 | 123.5321 | -0.10529 | 123.4039 | 61.1938 | -0.29755 | 123.5321 | -0.10529 | 61.1938 | 123.2117 | 123.4039 | -123.6465 | -123.6237
376.9219 | 123.4909 | -61.1023 | 62.2101 | -0.12502 | 0.0052458 | -0.028574 | 0.02371 | 0.052121 | 0.0037646 | 0.068519 | -61.203 | 62.4069 | -61.4319 | -61.2946 | 62.0636 | 0.064087 | -0.050354 | 0.17853 | 62.3199 | -61.3953 | -0.32959 | 0.19684 | -0.10071 | -0.19226 | -0.14648 | -0.29297 | 0.10986 | 0.22888 | 61.0519 | 61.2808 | 123.1659 | 123.5092 | -0.10071 | 123.4222 | 61.1664 | -0.29297 | 123.5092 | -0.10071 | 61.1664 | 123.1659 | 123.4222 | -123.642 | -123.6053
377.9844 | 123.4497 | -61.1069 | 62.2467 | 0.56163 | 0.0073818 | -0.028574 | 0.0055522 | 0.063871 | 0.0048326 | 0.070655 | -61.1893 | 62.3978 | -61.441 | -61.3037 | 62.0819 | 0.086975 | -0.050354 | 0.20142 | 62.3016 | -61.3953 | -0.33417 | 0.15106 | -0.082397 | -0.19684 | -0.16479 | -0.28839 | 0.054932 | 0.25177 | 61.0565 | 61.3083 | 123.1888 | 123.5046 | -0.082397 | 123.4085 | 61.1938 | -0.28839 | 123.5046 | -0.082397 | 61.1938 | 123.1888 | 123.4085 | -123.6877 | -123.642
378.9219 | 123.468 | -61.1114 | 62.1918 | -0.048725 | 0.016995 | -0.0040084 | 0.015165 | 0.052121 | -0.0037124 | 0.072791 | -61.2259 | 62.439 | -61.4182 | -61.2946 | 62.0544 | 0.064087 | -0.045776 | 0.18768 | 62.3016 | -61.3907 | -0.3067 | 0.24719 | -0.11444 | -0.18311 | -0.13733 | -0.27924 | 0.10986 | 0.19226 | 61.0657 | 61.2991 | 123.1659 | 123.5504 | -0.11444 | 123.4131 | 61.1755 | -0.27924 | 123.5504 | -0.11444 | 61.1755 | 123.1659 | 123.4131 | -123.6099 | -123.5825
379.9844 | 123.5092 | -61.0611 | 62.233 | -0.39968 | -0.0043672 | -0.024302 | -0.0051288 | 0.056394 | -0.017597 | 0.080268 | -61.2213 | 62.3428 | -61.4182 | -61.3815 | 62.0224 | 0.054932 | -0.022888 | 0.16937 | 62.3245 | -61.3953 | -0.35706 | 0.10986 | -0.16022 | -0.32044 | -0.21057 | -0.33417 | 0.091553 | 0.19684 | 61.0382 | 61.2305 | 123.0835 | 123.4039 | -0.16022 | 123.3856 | 61.116 | -0.33417 | 123.4039 | -0.16022 | 61.116 | 123.0835 | 123.3856 | -123.6511 | -123.6282
380.9219 | 123.4177 | -61.116 | 62.2238 | 0.14964 | 0.0063138 | -0.0072124 | 0.017301 | 0.055326 | 0.0037646 | 0.059974 | -61.2854 | 62.4069 | -61.4182 | -61.2305 | 62.1231 | 0.086975 | -0.15106 | 0.23804 | 62.2604 | -61.409 | -0.30212 | 0.1831 | -0.16937 | -0.11444 | -0.10071 | -0.29297 | 0.036621 | 0.13275 | 60.965 | 61.3541 | 123.2391 | 123.5229 | -0.16937 | 123.3765 | 61.203 | -0.29297 | 123.5229 | -0.16937 | 61.203 | 123.2391 | 123.3765 | -123.642 | -123.6328
381.9844 | 123.555 | -61.0657 | 62.2147 | -0.30813 | -0.019321 | -0.039256 | -0.01047 | 0.055326 | -0.01012 | 0.068519 | -60.9329 | 62.3749 | -61.3815 | -61.3815 | 61.9949 | -0.059509 | 0.032043 | 0.12817 | 62.3566 | -61.3998 | -0.31586 | 0.16022 | 0.13275 | -0.31586 | -0.21973 | -0.33417 | 0.14191 | 0.44861 | 61.0977 | 61.1938 | 123.0606 | 123.4406 | 0.13275 | 123.4222 | 61.0062 | -0.33417 | 123.4406 | 0.13275 | 61.0062 | 123.0606 | 123.4222 | -123.5962 | -123.6145
382.9219 | 123.4955 | -61.0931 | 62.2284 | -0.23183 | -9.5248e-05 | -0.00080337 | 0.013029 | 0.054258 | 0.0059006 | 0.073859 | -61.2167 | 62.4435 | -61.4044 | -61.3083 | 62.0544 | 0.073242 | -0.050354 | 0.17853 | 62.3108 | -61.4044 | -0.31128 | 0.21515 | -0.1236 | -0.21515 | -0.17395 | -0.31128 | 0.082397 | 0.18768 | 61.0428 | 61.2717 | 123.1476 | 123.5367 | -0.1236 | 123.4039 | 61.1664 | -0.31128 | 123.5367 | -0.1236 | 61.1664 | 123.1476 | 123.4039 | -123.6328 | -123.6328
383.9844 | 123.5367 | -61.0748 | 62.2421 | 0.21067 | -0.026798 | -0.010416 | -0.0083338 | 0.054258 | -0.0058484 | 0.075996 | -61.203 | 62.3154 | -61.409 | -61.4227 | 61.9766 | -0.013733 | 0.054932 | 0.1236 | 62.3291 | -61.4044 | -0.33417 | 0.073243 | -0.12817 | -0.3479 | -0.2655 | -0.32959 | 0.086976 | 0.20599 | 61.1298 | 61.1984 | 123.0515 | 123.3902 | -0.12817 | 123.4039 | 61.0611 | -0.32959 | 123.3902 | -0.12817 | 61.0611 | 123.0515 | 123.4039 | -123.6511 | -123.6465
384.9219 | 123.4772 | -61.0886 | 62.2559 | -0.26235 | 0.0052458 | -0.022166 | 0.0076882 | 0.042508 | -0.0058484 | 0.065314 | -61.2534 | 62.4207 | -61.4273 | -61.2762 | 62.0819 | 0.09613 | -0.09613 | 0.22888 | 62.2925 | -61.3632 | -0.33874 | 0.16479 | -0.16479 | -0.18768 | -0.17395 | -0.27466 | 0.036621 | 0.17395 | 60.9924 | 61.3174 | 123.1705 | 123.5092 | -0.16479 | 123.381 | 61.1847 | -0.27466 | 123.5092 | -0.16479 | 61.1847 | 123.1705 | 123.381 | -123.6832 | -123.6191
385.9688 | 123.5504 | -61.0748 | 62.1964 | -0.094502 | -0.0032992 | -0.031779 | -0.011538 | 0.043577 | -0.024006 | 0.071723 | -61.235 | 62.3108 | -61.409 | -61.4502 | 61.972 | -0.032043 | 0.041199 | 0.1236 | 62.3566 | -61.4044 | -0.33417 | 0.11444 | -0.16022 | -0.37537 | -0.2243 | -0.32959 | 0.16022 | 0.17395 | 61.116 | 61.1984 | 123.0469 | 123.3856 | -0.16022 | 123.4314 | 61.0428 | -0.32959 | 123.3856 | -0.16022 | 61.0428 | 123.0469 | 123.4314 | -123.6053 | -123.6008
386.9219 | 123.4131 | -61.1206 | 62.2467 | -2.8869 | -0.0022312 | -0.024302 | 0.011961 | 0.051053 | -0.0037124 | 0.068519 | -61.2854 | 62.4344 | -61.4182 | -61.2305 | 62.059 | 0.10071 | -0.07782 | 0.28381 | 62.3154 | -61.3724 | -0.29755 | 0.18768 | -0.1648 | -0.10986 | -0.18768 | -0.25177 | 0.068665 | 0.13275 | 61.0428 | 61.4044 | 123.1796 | 123.555 | -0.1648 | 123.436 | 61.2213 | -0.25177 | 123.555 | -0.1648 | 61.2213 | 123.1796 | 123.436 | -123.6649 | -123.6191
387.9844 | 123.4955 | -61.0931 | 62.233 | -0.1708 | 0.0031088 | -0.041392 | 0.0055522 | 0.054258 | -0.0015754 | 0.069587 | -61.203 | 62.3703 | -61.4044 | -61.3037 | 62.0544 | 0.054932 | -0.036621 | 0.19684 | 62.3108 | -61.3861 | -0.31128 | 0.13733 | -0.10986 | -0.21057 | -0.17853 | -0.29297 | 0.07782 | 0.20142 | 61.0565 | 61.29 | 123.1476 | 123.4634 | -0.10986 | 123.4039 | 61.1481 | -0.29297 | 123.4634 | -0.10986 | 61.1481 | 123.1476 | 123.4039 | -123.6374 | -123.6191
388.9219 | 123.436 | -61.1206 | 62.2421 | 0.40904 | 0.0063138 | -0.015757 | 0.0087562 | 0.057462 | -0.0069164 | 0.065314 | -61.2534 | 62.4435 | -61.4182 | -61.2808 | 62.1002 | 0.10071 | -0.11444 | 0.22888 | 62.3154 | -61.3449 | -0.29755 | 0.20142 | -0.13275 | -0.16022 | -0.14191 | -0.22431 | 0.073243 | 0.16479 | 61.0062 | 61.3495 | 123.2208 | 123.5641 | -0.13275 | 123.436 | 61.2213 | -0.22431 | 123.5641 | -0.13275 | 61.2213 | 123.2208 | 123.436 | -123.6603 | -123.587
389.9844 | 123.587 | -61.0611 | 62.2101 | -0.36916 | -0.016117 | -0.0093484 | -0.012606 | 0.043577 | -0.032551 | 0.063178 | -61.2167 | 62.2971 | -61.3907 | -61.4594 | 61.9446 | -0.036621 | 0.054932 | 0.086975 | 62.3703 | -61.3998 | -0.32959 | 0.086975 | -0.15564 | -0.39825 | -0.2655 | -0.33875 | 0.16022 | 0.17395 | 61.116 | 61.1481 | 123.0057 | 123.3582 | -0.15564 | 123.4314 | 61.0245 | -0.33875 | 123.3582 | -0.15564 | 61.0245 | 123.0057 | 123.4314 | -123.6008 | -123.6099
390.9219 | 123.4222 | -61.084 | 62.2192 | -0.4302 | -0.01398 | -0.018961 | -0.0029928 | 0.055326 | -0.0079844 | 0.064246 | -61.2396 | 62.3886 | -61.4044 | -61.2991 | 62.0682 | 0.073242 | -0.10071 | 0.21057 | 62.3016 | -61.3953 | -0.32043 | 0.16937 | -0.15564 | -0.21515 | -0.15106 | -0.31128 | 0.082398 | 0.16479 | 60.9833 | 61.2946 | 123.1522 | 123.4726 | -0.15564 | 123.3856 | 61.1572 | -0.31128 | 123.4726 | -0.15564 | 61.1572 | 123.1522 | 123.3856 | -123.6237 | -123.6145
391.9844 | 123.5367 | -61.0657 | 62.1918 | -0.063984 | -0.015048 | -0.040324 | -0.0061968 | 0.048917 | -0.017597 | 0.077064 | -61.2305 | 62.2925 | -61.3998 | -61.4365 | 61.9629 | -0.027466 | 0.022888 | 0.11444 | 62.3383 | -61.4044 | -0.33417 | 0.10071 | -0.16479 | -0.37079 | -0.22888 | -0.33874 | 0.14648 | 0.16937 | 61.0886 | 61.1801 | 123.0286 | 123.3582 | -0.16479 | 123.4039 | 61.0382 | -0.33874 | 123.3582 | -0.16479 | 61.0382 | 123.0286 | 123.4039 | -123.5916 | -123.5962
392.9219 | 123.4314 | -61.0977 | 62.2513 | -0.079243 | -0.0043672 | -0.04246 | 0.019437 | 0.042508 | -0.017597 | 0.073859 | -61.2671 | 62.3611 | -61.3815 | -61.2488 | 62.0682 | 0.1236 | -0.10071 | 0.23346 | 62.3062 | -61.3632 | -0.28381 | 0.10986 | -0.16937 | -0.15106 | -0.18311 | -0.2655 | 0.054931 | 0.11444 | 60.997 | 61.3312 | 123.1659 | 123.4589 | -0.16937 | 123.4039 | 61.2213 | -0.2655 | 123.4589 | -0.16937 | 61.2213 | 123.1659 | 123.4039 | -123.6328 | -123.6145
393.9844 | 123.4726 | -61.084 | 62.2101 | 0.13438 | -0.015048 | -0.021098 | -0.0019248 | 0.040372 | -0.022938 | 0.065314 | -61.2671 | 62.2925 | -61.4136 | -61.3861 | 62.0041 | 0 | -0.013733 | 0.14648 | 62.2971 | -61.3953 | -0.32959 | 0.082397 | -0.18311 | -0.30212 | -0.20599 | -0.31128 | 0.086975 | 0.14648 | 61.0703 | 61.2305 | 123.0881 | 123.3765 | -0.18311 | 123.381 | 61.084 | -0.31128 | 123.3765 | -0.18311 | 61.084 | 123.0881 | 123.381 | -123.6237 | -123.6053
394.9219 | 123.468 | -61.0931 | 62.233 | 0.39378 | 0.0084498 | -0.033915 | 0.0098242 | 0.055326 | -0.0037124 | 0.070655 | -61.2625 | 62.3795 | -61.4273 | -61.2442 | 62.0682 | 0.09613 | -0.10071 | 0.23804 | 62.2833 | -61.377 | -0.33417 | 0.14648 | -0.16937 | -0.15106 | -0.16479 | -0.28381 | 0.050354 | 0.16479 | 60.9924 | 61.3312 | 123.1613 | 123.4726 | -0.16937 | 123.3765 | 61.1893 | -0.28381 | 123.4726 | -0.16937 | 61.1893 | 123.1613 | 123.3765 | -123.6603 | -123.6099
395.9844 | 123.5229 | -61.084 | 62.1872 | 0.073345 | -0.011844 | -0.054209 | -0.0083338 | 0.040372 | -0.026142 | 0.074928 | -61.2808 | 62.3108 | -61.4227 | -61.3495 | 62.0773 | -0.013733 | -0.022888 | 0.14191 | 62.3245 | -61.377 | -0.33874 | 0.1236 | -0.19684 | -0.2655 | -0.10986 | -0.29297 | 0.13733 | 0.14191 | 61.0611 | 61.2259 | 123.1613 | 123.3948 | -0.19684 | 123.4085 | 61.0703 | -0.29297 | 123.3948 | -0.19684 | 61.0703 | 123.1613 | 123.4085 | -123.6099 | -123.5641
396.9219 | 123.4497 | -61.0794 | 62.2284 | -0.36916 | -0.018253 | -0.024302 | 0.0076882 | 0.045713 | -0.014393 | 0.066383 | -61.2488 | 62.384 | -61.4182 | -61.2808 | 62.0224 | 0.086975 | -0.07782 | 0.25177 | 62.3154 | -61.3861 | -0.33874 | 0.15564 | -0.16937 | -0.20142 | -0.20599 | -0.3067 | 0.086975 | 0.16937 | 61.0016 | 61.3312 | 123.1018 | 123.4634 | -0.16937 | 123.3948 | 61.1664 | -0.3067 | 123.4634 | -0.16937 | 61.1664 | 123.1018 | 123.3948 | -123.6465 | -123.6145
397.9688 | 123.5229 | -61.0977 | 62.1964 | 0.25645 | -9.5248e-05 | -0.026438 | 0.00021117 | 0.046781 | -0.011188 | 0.059974 | -61.2854 | 62.3062 | -61.3953 | -61.3632 | 62.0178 | -0.004578 | -0.009155 | 0.14191 | 62.3291 | -61.3861 | -0.29755 | 0.10986 | -0.18768 | -0.2655 | -0.17853 | -0.28839 | 0.13275 | 0.10986 | 61.0886 | 61.2396 | 123.1155 | 123.4039 | -0.18768 | 123.4268 | 61.0931 | -0.28839 | 123.4039 | -0.18768 | 61.0931 | 123.1155 | 123.4268 | -123.5916 | -123.5825
398.9219 | 123.5184 | -61.0611 | 62.2238 | -0.44545 | -0.017185 | -0.029642 | 0.017301 | 0.044645 | -0.0037124 | 0.069587 | -61.2122 | 62.3428 | -61.3861 | -61.3586 | 62.0087 | 0.027466 | -0.022888 | 0.16022 | 62.3245 | -61.3861 | -0.32501 | 0.11902 | -0.15106 | -0.29755 | -0.21515 | -0.32501 | 0.10071 | 0.17395 | 61.0382 | 61.2213 | 123.0698 | 123.4039 | -0.15106 | 123.3856 | 61.0886 | -0.32501 | 123.4039 | -0.15106 | 61.0886 | 123.0698 | 123.3856 | -123.6099 | -123.6099
399.9688 | 123.5229 | -61.0977 | 62.1826 | 0.36326 | -0.012912 | -0.010416 | 0.0066202 | 0.046781 | -0.019733 | 0.066383 | -61.2488 | 62.3108 | -61.4182 | -61.3815 | 61.9995 | -0.022888 | 0 | 0.11444 | 62.2833 | -61.4227 | -0.32043 | 0.12817 | -0.15106 | -0.28381 | -0.1831 | -0.32501 | 0.10071 | 0.16937 | 61.0977 | 61.2122 | 123.0972 | 123.4085 | -0.15106 | 123.381 | 61.0748 | -0.32501 | 123.4085 | -0.15106 | 61.0748 | 123.0972 | 123.381 | -123.6008 | -123.6053
400.9219 | 123.4543 | -61.0931 | 62.2284 | -0.47597 | -0.010776 | -0.036051 | 0.011961 | 0.0361 | -0.0079844 | 0.066383 | -61.2396 | 62.3474 | -61.3953 | -61.2946 | 62.0499 | 0.064087 | -0.045776 | 0.19226 | 62.3245 | -61.3907 | -0.30212 | 0.11902 | -0.14648 | -0.20142 | -0.17853 | -0.29755 | 0.09613 | 0.15564 | 61.0474 | 61.2854 | 123.143 | 123.4406 | -0.14648 | 123.4177 | 61.1572 | -0.29755 | 123.4406 | -0.14648 | 61.1572 | 123.143 | 123.4177 | -123.6237 | -123.6191
401.9844 | 123.5504 | -61.0931 | 62.1735 | 0.39378 | -0.0086402 | -0.020029 | 0.010892 | 0.039304 | 0.0037646 | 0.058906 | -61.2396 | 62.3291 | -61.4273 | -61.3953 | 61.9995 | -0.045776 | 0.013733 | 0.10071 | 62.2879 | -61.4182 | -0.33417 | 0.15564 | -0.14648 | -0.30212 | -0.17395 | -0.32501 | 0.11444 | 0.18768 | 61.1069 | 61.1938 | 123.0927 | 123.4222 | -0.14648 | 123.381 | 61.0474 | -0.32501 | 123.4222 | -0.14648 | 61.0474 | 123.0927 | 123.381 | -123.6008 | -123.5916
402.9219 | 123.5413 | -61.0657 | 62.2284 | -0.4302 | -0.010776 | -0.024302 | 0.0034162 | 0.048917 | -0.014393 | 0.06211 | -61.2076 | 62.3474 | -61.3953 | -61.3724 | 61.9995 | 0.013733 | 0.009155 | 0.13275 | 62.3108 | -61.3815 | -0.32959 | 0.11902 | -0.14191 | -0.3067 | -0.22888 | -0.31586 | 0.082397 | 0.18768 | 61.0748 | 61.1984 | 123.0652 | 123.4131 | -0.14191 | 123.3765 | 61.0794 | -0.31586 | 123.4131 | -0.14191 | 61.0794 | 123.0652 | 123.3765 | -123.6237 | -123.6099
403.9844 | 123.4268 | -61.1114 | 62.2375 | -0.41494 | -0.0054352 | -0.030711 | 0.016233 | 0.043577 | -0.015461 | 0.067451 | -61.2854 | 62.3886 | -61.4319 | -61.2488 | 62.3383 | 0.17853 | -0.18768 | 0.13733 | 62.265 | -61.377 | -0.32044 | 0.15106 | -0.17395 | -0.13733 | 0.10071 | -0.2655 | 0.027466 | 0.14648 | 60.9238 | 61.2488 | 123.4497 | 123.5001 | -0.17395 | 123.3765 | 61.29 | -0.2655 | 123.5001 | -0.17395 | 61.29 | 123.4497 | 123.3765 | -123.6694 | -123.6145
404.9219 | 123.587 | -61.0794 | 62.2055 | -0.048725 | -0.022525 | -0.036051 | -0.0061968 | 0.049985 | -0.02721 | 0.073859 | -61.1984 | 62.3062 | -61.4273 | -61.4594 | 61.9629 | -0.064087 | 0.07782 | 0.082397 | 62.3383 | -61.377 | -0.3479 | 0.10071 | -0.11902 | -0.37994 | -0.24261 | -0.29755 | 0.13275 | 0.22888 | 61.1572 | 61.1618 | 123.0423 | 123.3856 | -0.11902 | 123.4177 | 61.0153 | -0.29755 | 123.3856 | -0.11902 | 61.0153 | 123.0423 | 123.4177 | -123.6328 | -123.5825
405.9219 | 123.6465 | -61.0519 | 62.2696 | -0.27761 | -0.017185 | -0.037119 | -0.0061968 | 0.0361 | -0.015461 | 0.06211 | -61.1984 | 62.3199 | -61.3678 | -61.409 | 61.9583 | -0.032043 | 0.054932 | 0.10071 | 62.3199 | -61.3861 | -0.31586 | 0.050354 | -0.14648 | -0.35706 | -0.31128 | -0.33417 | 0.050354 | 0.16937 | 61.1069 | 61.1526 | 123.0103 | 123.3719 | -0.14648 | 123.3719 | 61.0199 | -0.33417 | 123.3719 | -0.14648 | 61.0199 | 123.0103 | 123.3719 | -123.6374 | -123.6557
406.9688 | 123.555 | -61.0748 | 62.1597 | 0.45481 | -0.0054352 | -0.018961 | 0.0076882 | 0.0361 | -0.0026434 | 0.071723 | -61.2122 | 62.3199 | -61.4044 | -61.4365 | 61.6653 | -0.10529 | 0.16937 | 0.16022 | 62.3245 | -61.3861 | -0.32959 | 0.16022 | -0.13733 | -0.36163 | -0.49439 | -0.31128 | 0.16479 | 0.19226 | 61.2442 | 61.235 | 122.7402 | 123.3948 | -0.13733 | 123.3994 | 60.9695 | -0.31128 | 123.3948 | -0.13733 | 60.9695 | 122.7402 | 123.3994 | -123.5641 | -123.5458
407.9219 | 123.4863 | -61.1069 | 62.2147 | -0.4302 | -0.010776 | -0.026438 | 0.0044842 | 0.04144 | -0.012257 | 0.061042 | -61.2213 | 62.3428 | -61.3998 | -61.3266 | 62.027 | 0.050354 | -0.027466 | 0.17853 | 62.3383 | -61.3724 | -0.29297 | 0.12817 | -0.11444 | -0.21973 | -0.18768 | -0.2655 | 0.1236 | 0.17853 | 61.0794 | 61.2854 | 123.1339 | 123.4497 | -0.11444 | 123.4451 | 61.1572 | -0.2655 | 123.4497 | -0.11444 | 61.1572 | 123.1339 | 123.4451 | -123.6145 | -123.587
408.9844 | 123.5504 | -61.0703 | 62.1918 | -0.29287 | -0.0043672 | -0.023234 | 0.0087562 | 0.049985 | -0.035755 | 0.072791 | -61.2213 | 62.3062 | -61.377 | -61.3449 | 61.8988 | 0 | 0.09613 | 0.07782 | 62.3245 | -61.3861 | -0.3067 | 0.11444 | -0.15106 | -0.27466 | -0.29297 | -0.31586 | 0.13275 | 0.15564 | 61.1664 | 61.1481 | 122.9691 | 123.3765 | -0.15106 | 123.3948 | 61.0703 | -0.31586 | 123.3765 | -0.15106 | 61.0703 | 122.9691 | 123.3948 | -123.5687 | -123.5779
409.9219 | 123.5779 | -61.0794 | 62.2147 | -0.44545 | -0.027866 | -0.021098 | -0.0029928 | 0.040372 | -0.020801 | 0.070655 | -61.171 | 62.3016 | -61.3998 | -61.409 | 61.9675 | -0.022888 | 0.050354 | 0.082397 | 62.3383 | -61.3678 | -0.32043 | 0.086975 | -0.091552 | -0.32959 | -0.24719 | -0.28839 | 0.1236 | 0.22888 | 61.1298 | 61.1618 | 123.0469 | 123.381 | -0.091552 | 123.4177 | 61.0565 | -0.28839 | 123.381 | -0.091552 | 61.0565 | 123.0469 | 123.4177 | -123.6145 | -123.5825
410.9844 | 123.5138 | -61.0886 | 62.1735 | 0.36326 | -0.017185 | -0.038187 | 0.0012792 | 0.038236 | -0.016529 | 0.066383 | -61.2396 | 62.2742 | -61.4273 | -61.3861 | 61.9904 | -0.036621 | 0.027466 | 0.10529 | 62.2787 | -61.3953 | -0.33874 | 0.10071 | -0.15106 | -0.29755 | -0.18311 | -0.3067 | 0.10529 | 0.18768 | 61.116 | 61.1938 | 123.0789 | 123.3627 | -0.15106 | 123.3673 | 61.0519 | -0.3067 | 123.3627 | -0.15106 | 61.0519 | 123.0789 | 123.3673 | -123.6008 | -123.5687
411.9219 | 123.5321 | -61.0703 | 62.1735 | 0.1649 | -0.020389 | -0.018961 | 0.0023482 | 0.039304 | -0.031483 | 0.074928 | -61.29 | 62.3199 | -61.441 | -61.3724 | 62.0041 | -0.004578 | -0.009155 | 0.1236 | 62.3016 | -61.3815 | -0.37079 | 0.14648 | -0.21973 | -0.30212 | -0.16937 | -0.31128 | 0.12817 | 0.15106 | 61.0611 | 61.1938 | 123.0743 | 123.3902 | -0.21973 | 123.3719 | 61.0657 | -0.31128 | 123.3902 | -0.21973 | 61.0657 | 123.0743 | 123.3719 | -123.6145 | -123.555
412.9844 | 123.5733 | -61.0748 | 62.1826 | -0.10976 | -0.020389 | -0.021098 | -0.0029928 | 0.040372 | -0.020801 | 0.061042 | -61.2259 | 62.3154 | -61.3815 | -61.409 | 61.9629 | -0.041199 | 0.036621 | 0.091553 | 62.3062 | -61.3815 | -0.3067 | 0.13275 | -0.15106 | -0.33417 | -0.21973 | -0.3067 | 0.1236 | 0.15564 | 61.1114 | 61.1664 | 123.0377 | 123.3902 | -0.15106 | 123.381 | 61.0336 | -0.3067 | 123.3902 | -0.15106 | 61.0336 | 123.0377 | 123.381 | -123.5641 | -123.5641
413.9219 | 123.5001 | -61.1023 | 62.2421 | -0.30813 | 0.0020408 | -0.02537 | 0.019437 | 0.047849 | 0.0048326 | 0.068519 | -61.2076 | 62.4161 | -61.3953 | -61.2534 | 62.0682 | 0.073242 | -0.068665 | 0.20599 | 62.2879 | -61.3724 | -0.29297 | 0.17395 | -0.10529 | -0.15106 | -0.17395 | -0.27008 | 0.045777 | 0.18768 | 61.0336 | 61.3083 | 123.1705 | 123.5184 | -0.10529 | 123.3902 | 61.1755 | -0.27008 | 123.5184 | -0.10529 | 61.1755 | 123.1705 | 123.3902 | -123.6374 | -123.6145
414.9844 | 123.5275 | -61.0977 | 62.1735 | 0.47007 | -0.02573 | -0.015757 | -0.00085683 | 0.043577 | -0.022938 | 0.067451 | -61.2213 | 62.2925 | -61.4044 | -61.4227 | 61.9812 | -0.045776 | 0.032043 | 0.091553 | 62.3108 | -61.4182 | -0.3067 | 0.11902 | -0.1236 | -0.32501 | -0.19226 | -0.32043 | 0.13733 | 0.18311 | 61.1298 | 61.1893 | 123.0789 | 123.3902 | -0.1236 | 123.4085 | 61.0519 | -0.32043 | 123.3902 | -0.1236 | 61.0519 | 123.0789 | 123.4085 | -123.5779 | -123.5916
415.9219 | 123.5596 | -61.0474 | 62.1689 | -0.12502 | -0.016117 | -0.045664 | 0.0023482 | 0.032895 | -0.032551 | 0.067451 | -61.2442 | 62.3016 | -61.4044 | -61.3953 | 61.9904 | -0.050354 | 0.027466 | 0.10986 | 62.3062 | -61.3907 | -0.35706 | 0.13275 | -0.19684 | -0.3479 | -0.17853 | -0.34332 | 0.13733 | 0.16022 | 61.0748 | 61.1572 | 123.0377 | 123.349 | -0.19684 | 123.3536 | 60.997 | -0.34332 | 123.349 | -0.19684 | 60.997 | 123.0377 | 123.3536 | -123.5733 | -123.5596
416.9844 | 123.5184 | -61.0703 | 62.1643 | 0.48533 | -0.015048 | -0.013621 | 0.0066202 | 0.039304 | -0.01012 | 0.068519 | -61.203 | 62.3062 | -61.3815 | -61.6196 | 61.8668 | 0.013733 | 0.15564 | 0.054932 | 62.3016 | -61.409 | -0.31128 | 0.14191 | -0.13275 | -0.54932 | -0.29755 | -0.33875 | 0.13733 | 0.17853 | 61.2259 | 61.1252 | 122.937 | 123.3765 | -0.13275 | 123.3719 | 61.084 | -0.33875 | 123.3765 | -0.13275 | 61.084 | 122.937 | 123.3719 | -123.5458 | -123.5733
417.9219 | 123.5596 | -61.0611 | 62.1689 | -0.033467 | -0.0086402 | -0.039256 | -0.0040608 | 0.038236 | -0.024006 | 0.073859 | -61.2762 | 62.2925 | -61.4182 | -61.377 | 61.9995 | -0.009155 | 0 | 0.13275 | 62.3016 | -61.4044 | -0.35706 | 0.1236 | -0.21515 | -0.31586 | -0.16937 | -0.34332 | 0.13275 | 0.14191 | 61.0611 | 61.1938 | 123.0606 | 123.3536 | -0.21515 | 123.3627 | 61.0519 | -0.34332 | 123.3536 | -0.21515 | 61.0519 | 123.0606 | 123.3627 | -123.587 | -123.5733
418.9844 | 123.5001 | -60.997 | 62.2192 | -0.36916 | -0.0075722 | -0.058482 | 0.0044842 | 0.035032 | -0.024006 | 0.070655 | -61.1893 | 62.3199 | -61.3998 | -61.4044 | 61.9675 | -0.018311 | 0.041199 | 0.11902 | 62.3383 | -61.3907 | -0.40283 | 0.10071 | -0.19226 | -0.40741 | -0.25177 | -0.39368 | 0.11902 | 0.21057 | 61.0382 | 61.116 | 122.9645 | 123.317 | -0.19226 | 123.3353 | 60.9787 | -0.39368 | 123.317 | -0.19226 | 60.9787 | 122.9645 | 123.3353 | -123.6191 | -123.6099
419.9219 | 123.5275 | -61.0748 | 62.1826 | 0.088604 | -0.019321 | -0.044596 | -0.0019248 | 0.0361 | -0.020801 | 0.04502 | -61.2808 | 62.3062 | -61.409 | -61.3541 | 62.0499 | 0.013733 | 0.022888 | 0.17395 | 62.3062 | -61.3861 | -0.33417 | 0.1236 | -0.20599 | -0.27924 | -0.13275 | -0.31128 | 0.1236 | 0.12817 | 61.0977 | 61.2488 | 123.1247 | 123.381 | -0.20599 | 123.381 | 61.0886 | -0.31128 | 123.381 | -0.20599 | 61.0886 | 123.1247 | 123.381 | -123.5916 | -123.5687
420.9688 | 123.4772 | -61.0977 | 62.2238 | -0.1708 | 0.018063 | -0.026438 | 0.021574 | 0.045713 | -0.0026434 | 0.059974 | -61.2076 | 62.4023 | -61.4044 | -61.2534 | 62.0636 | 0.054932 | -0.036621 | 0.17853 | 62.2879 | -61.4044 | -0.3067 | 0.17853 | -0.10986 | -0.15564 | -0.16022 | -0.3067 | 0.064087 | 0.19684 | 61.0611 | 61.2762 | 123.1613 | 123.5001 | -0.10986 | 123.3856 | 61.1526 | -0.3067 | 123.5001 | -0.10986 | 61.1526 | 123.1613 | 123.3856 | -123.6282 | -123.6282
421.9219 | 123.5825 | -61.0336 | 62.1964 | -0.12502 | -0.01398 | -0.054209 | -0.0072648 | 0.04144 | -0.029346 | 0.078132 | -61.235 | 62.3154 | -61.4319 | -61.4182 | 61.972 | -0.036621 | 0.045776 | 0.10071 | 62.3245 | -61.3861 | -0.39825 | 0.11902 | -0.20142 | -0.38452 | -0.2243 | -0.35248 | 0.12817 | 0.19684 | 61.0794 | 61.1343 | 123.0057 | 123.349 | -0.20142 | 123.3582 | 60.997 | -0.35248 | 123.349 | -0.20142 | 60.997 | 123.0057 | 123.3582 | -123.6282 | -123.5825
422.9844 | 123.5458 | -61.0748 | 62.1231 | -0.0029495 | 0.010586 | -0.013621 | 0.011961 | 0.0361 | -0.00050737 | 0.067451 | -61.1984 | 62.3383 | -61.3953 | -61.377 | 61.9766 | -0.059509 | 0.041199 | 0.082397 | 62.2696 | -61.4227 | -0.32043 | 0.21515 | -0.1236 | -0.30212 | -0.14648 | -0.3479 | 0.14648 | 0.19684 | 61.116 | 61.1572 | 123.0515 | 123.4131 | -0.1236 | 123.3444 | 61.0153 | -0.3479 | 123.4131 | -0.1236 | 61.0153 | 123.0515 | 123.3444 | -123.5184 | -123.5458
423.9219 | 123.6053 | -61.0382 | 62.1964 | -0.47597 | -0.012912 | -0.031779 | 0.0044842 | 0.028623 | -0.030414 | 0.072791 | -61.2259 | 62.3291 | -61.4227 | -61.4273 | 61.9766 | -0.041199 | 0.073242 | 0.07782 | 62.3199 | -61.3907 | -0.38452 | 0.13275 | -0.18768 | -0.3891 | -0.21973 | -0.35248 | 0.1236 | 0.19684 | 61.1114 | 61.116 | 123.0148 | 123.3673 | -0.18768 | 123.3582 | 60.997 | -0.35248 | 123.3673 | -0.18768 | 60.997 | 123.0148 | 123.3582 | -123.6191 | -123.587
424.9844 | 123.5229 | -61.1114 | 62.1414 | 0.57688 | 0.0031088 | -0.024302 | 0.0087562 | 0.044645 | -0.0079844 | 0.058906 | -61.2396 | 62.3566 | -61.4182 | -61.3632 | 62.0132 | -0.032043 | -0.009155 | 0.12817 | 62.3016 | -61.377 | -0.3067 | 0.21515 | -0.12817 | -0.25177 | -0.12817 | -0.2655 | 0.16022 | 0.17853 | 61.1023 | 61.2396 | 123.1247 | 123.468 | -0.12817 | 123.4131 | 61.0794 | -0.2655 | 123.468 | -0.12817 | 61.0794 | 123.1247 | 123.4131 | -123.5596 | -123.5184
425.9219 | 123.5413 | -61.0931 | 62.1689 | 0.33274 | -0.0097082 | -0.029642 | 0.0012792 | 0.038236 | -0.018665 | 0.055701 | -61.2442 | 62.2971 | -61.4548 | -61.3815 | 62.0041 | -0.027466 | 0.018311 | 0.11902 | 62.2833 | -61.4044 | -0.36163 | 0.12817 | -0.15106 | -0.28839 | -0.16479 | -0.31128 | 0.11444 | 0.21057 | 61.1115 | 61.2122 | 123.0972 | 123.3902 | -0.15106 | 123.3765 | 61.0657 | -0.31128 | 123.3902 | -0.15106 | 61.0657 | 123.0972 | 123.3765 | -123.6237 | -123.5733
426.9844 | 123.5733 | -61.0931 | 62.1597 | 0.40904 | -0.010776 | -0.029642 | -0.0019248 | 0.059598 | -0.024006 | 0.06211 | -61.1298 | 62.3108 | -61.4273 | -61.3815 | 61.9812 | -0.07782 | 0.045776 | 0.1236 | 62.3016 | -61.441 | -0.33417 | 0.15106 | -0.036621 | -0.28839 | -0.17853 | -0.3479 | 0.14191 | 0.29755 | 61.1389 | 61.2167 | 123.0743 | 123.4039 | -0.036621 | 123.3948 | 61.0153 | -0.3479 | 123.4039 | -0.036621 | 61.0153 | 123.0743 | 123.3948 | -123.587 | -123.6008
427.9219 | 123.5046 | -61.0977 | 62.178 | 0.30223 | -0.012912 | -0.029642 | 0.0012792 | 0.038236 | -0.022938 | 0.070655 | -61.2717 | 62.3016 | -61.3998 | -61.3632 | 62.027 | -0.004578 | 0.004578 | 0.13733 | 62.2879 | -61.3907 | -0.30212 | 0.1236 | -0.17395 | -0.2655 | -0.15106 | -0.29297 | 0.10986 | 0.12817 | 61.1023 | 61.235 | 123.1247 | 123.3994 | -0.17395 | 123.3856 | 61.0931 | -0.29297 | 123.3994 | -0.17395 | 61.0931 | 123.1247 | 123.3856 | -123.5779 | -123.5687
428.9844 | 123.4451 | -61.1298 | 62.2147 | 0.27171 | 0.0031088 | -0.031779 | 0.016233 | 0.037168 | -0.013325 | 0.063178 | -61.3083 | 62.3978 | -61.4227 | -61.2213 | 62.0956 | 0.091553 | -0.11902 | 0.25177 | 62.233 | -61.3907 | -0.29297 | 0.1831 | -0.17853 | -0.091552 | -0.11902 | -0.26093 | 0.01831 | 0.11444 | 61.0107 | 61.3815 | 123.2254 | 123.5275 | -0.17853 | 123.3627 | 61.2213 | -0.26093 | 123.5275 | -0.17853 | 61.2213 | 123.2254 | 123.3627 | -123.6374 | -123.6053
429.9219 | 123.5458 | -61.084 | 62.178 | 0.10386 | -0.0097082 | -0.033915 | 0.0076882 | 0.043577 | -0.013325 | 0.072791 | -61.2854 | 62.3199 | -61.4273 | -61.377 | 62.0178 | -0.009155 | 0 | 0.14191 | 62.2925 | -61.4136 | -0.34332 | 0.14191 | -0.20142 | -0.29297 | -0.16022 | -0.32959 | 0.11444 | 0.14191 | 61.084 | 61.2259 | 123.1018 | 123.4039 | -0.20142 | 123.3765 | 61.0748 | -0.32959 | 123.4039 | -0.20142 | 61.0748 | 123.1018 | 123.3765 | -123.6053 | -123.5916
430.9844 | 123.5458 | -61.0703 | 62.146 | 0.40904 | -0.0065042 | -0.026438 | 0.0023482 | 0.0361 | -0.018665 | 0.064246 | -61.1481 | 62.3108 | -61.4594 | -61.377 | 61.9812 | -0.082397 | 0.054932 | 0.11444 | 62.3062 | -61.4319 | -0.3891 | 0.1648 | -0.07782 | -0.3067 | -0.16479 | -0.36163 | 0.16022 | 0.31128 | 61.1252 | 61.1847 | 123.0515 | 123.381 | -0.07782 | 123.3765 | 60.9879 | -0.36163 | 123.381 | -0.07782 | 60.9879 | 123.0515 | 123.3765 | -123.6053 | -123.5779
431.9219 | 123.5413 | -61.0931 | 62.1918 | 0.33274 | -0.010776 | -0.0040084 | -0.0083338 | 0.037168 | -0.016529 | 0.069587 | -61.2717 | 62.2879 | -61.4365 | -61.3678 | 62.0361 | -0.004578 | -0.022888 | 0.14191 | 62.2833 | -61.409 | -0.34332 | 0.096131 | -0.17853 | -0.27466 | -0.15564 | -0.31586 | 0.091553 | 0.16479 | 61.0703 | 61.235 | 123.1293 | 123.381 | -0.17853 | 123.3765 | 61.0886 | -0.31586 | 123.381 | -0.17853 | 61.0886 | 123.1293 | 123.3765 | -123.6282 | -123.6008
432.9844 | 123.5001 | -61.0703 | 62.1964 | 0.088604 | -0.0065042 | -0.036051 | -0.00085683 | 0.037168 | -0.016529 | 0.058906 | -61.2762 | 62.3291 | -61.3998 | -61.3724 | 61.9034 | 0.013733 | 0.068665 | 0.1236 | 62.265 | -61.3724 | -0.32959 | 0.13275 | -0.20599 | -0.30212 | -0.29297 | -0.30212 | 0.068665 | 0.1236 | 61.1389 | 61.1938 | 122.9736 | 123.3994 | -0.20599 | 123.3353 | 61.084 | -0.30212 | 123.3994 | -0.20599 | 61.084 | 122.9736 | 123.3353 | -123.5962 | -123.5687
433.9219 | 123.4818 | -61.084 | 62.2055 | 0.31749 | -0.0065042 | -0.039256 | -0.00085683 | 0.045713 | -0.02187 | 0.067451 | -61.2625 | 62.2971 | -61.4136 | -61.3815 | 61.9949 | -0.032043 | 0.009155 | 0.12817 | 62.2925 | -61.409 | -0.32959 | 0.091553 | -0.17853 | -0.29755 | -0.21057 | -0.32501 | 0.086975 | 0.15106 | 61.0931 | 61.2122 | 123.0789 | 123.381 | -0.17853 | 123.3765 | 61.0519 | -0.32501 | 123.381 | -0.17853 | 61.0519 | 123.0789 | 123.3765 | -123.6191 | -123.6145
434.9844 | 123.5001 | -61.0977 | 62.1872 | 0.45481 | 0.013791 | -0.021098 | 0.022642 | 0.044645 | -0.0026434 | 0.05677 | -61.2762 | 62.3932 | -61.4044 | -61.2946 | 62.0316 | 0.018311 | -0.041199 | 0.17395 | 62.2604 | -61.3953 | -0.3067 | 0.20599 | -0.17853 | -0.19684 | -0.15564 | -0.29755 | 0.073242 | 0.12817 | 61.0565 | 61.2717 | 123.1293 | 123.4909 | -0.17853 | 123.3582 | 61.116 | -0.29755 | 123.4909 | -0.17853 | 61.116 | 123.1293 | 123.3582 | -123.5916 | -123.5825
435.9219 | 123.5504 | -61.0474 | 62.2055 | 0.088604 | -0.011844 | -0.037119 | -0.0040608 | 0.033964 | -0.029346 | 0.067451 | -61.2488 | 62.3062 | -61.4227 | -61.4044 | 61.9949 | -0.018311 | 0.022888 | 0.12817 | 62.2971 | -61.4273 | -0.37537 | 0.10071 | -0.20142 | -0.35706 | -0.21057 | -0.37994 | 0.091553 | 0.17395 | 61.0703 | 61.1755 | 123.0423 | 123.3536 | -0.20142 | 123.3444 | 61.0291 | -0.37994 | 123.3536 | -0.20142 | 61.0291 | 123.0423 | 123.3444 | -123.6282 | -123.6328
436.9844 | 123.4818 | -61.1206 | 62.2101 | 0.80577 | 0.011654 | -0.023234 | 0.019437 | 0.04144 | -0.0037124 | 0.06211 | -61.1664 | 62.4115 | -61.4319 | -61.2534 | 62.0773 | 0.07782 | -0.054932 | 0.19226 | 62.2971 | -61.3907 | -0.31128 | 0.20142 | -0.045777 | -0.13275 | -0.13275 | -0.27008 | 0.086975 | 0.2655 | 61.0657 | 61.3129 | 123.1979 | 123.5321 | -0.045777 | 123.4177 | 61.1984 | -0.27008 | 123.5321 | -0.045777 | 61.1984 | 123.1979 | 123.4177 | -123.642 | -123.6008
437.9219 | 123.5413 | -61.116 | 62.146 | 3.0946 | 0.00097275 | -0.016825 | -0.0040608 | 0.027555 | -0.013325 | 0.057838 | -61.2305 | 62.2971 | -61.4319 | -61.4227 | 62.0178 | -0.041199 | 0.022888 | 0.068665 | 62.3062 | -61.409 | -0.31586 | 0.15106 | -0.11444 | -0.3067 | -0.12817 | -0.29297 | 0.16022 | 0.20142 | 61.1389 | 61.1847 | 123.1338 | 123.4131 | -0.11444 | 123.4222 | 61.0748 | -0.29297 | 123.4131 | -0.11444 | 61.0748 | 123.1338 | 123.4222 | -123.5779 | -123.555
438.9688 | 123.4634 | -61.0886 | 62.2009 | -0.24709 | 0.0031088 | -0.026438 | 0.018369 | 0.05319 | -0.0015754 | 0.073859 | -61.2076 | 62.439 | -61.4136 | -61.2579 | 62.0728 | 0.073242 | -0.054932 | 0.19226 | 62.2879 | -61.3953 | -0.32501 | 0.23804 | -0.11902 | -0.16937 | -0.12817 | -0.3067 | 0.086975 | 0.20599 | 61.0336 | 61.2808 | 123.1613 | 123.5275 | -0.11902 | 123.3765 | 61.1618 | -0.3067 | 123.5275 | -0.11902 | 61.1618 | 123.1613 | 123.3765 | -123.6145 | -123.5962
439.9219 | 123.5504 | -61.0977 | 62.1231 | 0.37852 | -0.0065042 | -0.021098 | 0.00021117 | 0.048917 | -0.016529 | 0.071723 | -61.2488 | 62.3657 | -61.441 | -61.3632 | 62.027 | 0 | 0.041199 | 0.12817 | 62.265 | -61.4319 | -0.34332 | 0.24262 | -0.15106 | -0.2655 | -0.09613 | -0.33417 | 0.14191 | 0.19226 | 61.1389 | 61.2259 | 123.1247 | 123.4634 | -0.15106 | 123.3627 | 61.0977 | -0.33417 | 123.4634 | -0.15106 | 61.0977 | 123.1247 | 123.3627 | -123.5641 | -123.555
440.9844 | 123.4634 | -61.0748 | 62.2009 | -0.14028 | -9.5248e-05 | -0.0018714 | 0.016233 | 0.05319 | 0.0016286 | 0.064246 | -61.2259 | 62.4252 | -61.4273 | -61.2808 | 62.0773 | 0.073242 | -0.082397 | 0.20142 | 62.2879 | -61.377 | -0.35248 | 0.2243 | -0.15106 | -0.20599 | -0.1236 | -0.30212 | 0.086975 | 0.20142 | 60.9924 | 61.2762 | 123.1522 | 123.5001 | -0.15106 | 123.3627 | 61.1481 | -0.30212 | 123.5001 | -0.15106 | 61.1481 | 123.1522 | 123.3627 | -123.6282 | -123.5779
441.9219 | 123.5367 | -61.0886 | 62.1552 | 1.0652 | -0.0097082 | -0.040324 | 0.0023482 | 0.048917 | -0.011188 | 0.081336 | -61.1893 | 62.3016 | -61.4182 | -61.4044 | 61.9858 | -0.059509 | 0.050354 | 0.10071 | 62.3154 | -61.409 | -0.32959 | 0.14649 | -0.10071 | -0.31586 | -0.16937 | -0.32043 | 0.16022 | 0.22888 | 61.1389 | 61.1893 | 123.0743 | 123.3902 | -0.10071 | 123.4039 | 61.0291 | -0.32043 | 123.3902 | -0.10071 | 61.0291 | 123.0743 | 123.4039 | -123.5733 | -123.5641
442.9688 | 123.4589 | -61.0931 | 62.2238 | 0.01231 | 0.010586 | -0.022166 | 0.014097 | 0.035032 | -0.00050737 | 0.074928 | -61.235 | 62.4115 | -61.4273 | -61.2534 | 62.0773 | 0.09613 | -0.091553 | 0.21057 | 62.265 | -61.4182 | -0.33417 | 0.18768 | -0.14191 | -0.16022 | -0.14648 | -0.32501 | 0.041199 | 0.19226 | 61.0016 | 61.3037 | 123.1705 | 123.5046 | -0.14191 | 123.3582 | 61.1893 | -0.32501 | 123.5046 | -0.14191 | 61.1893 | 123.1705 | 123.3582 | -123.6511 | -123.642
443.9219 | 123.555 | -61.084 | 62.1506 | 0.48533 | -0.016117 | -0.0040084 | -0.0029928 | 0.043577 | -0.012257 | 0.067451 | -61.2167 | 62.3199 | -61.4182 | -61.4731 | 62.0453 | -0.064087 | 0.009155 | 0.10071 | 62.3016 | -61.4182 | -0.33417 | 0.16937 | -0.13275 | -0.3891 | -0.10529 | -0.33417 | 0.15106 | 0.20142 | 61.0931 | 61.1847 | 123.1293 | 123.4039 | -0.13275 | 123.3856 | 61.0199 | -0.33417 | 123.4039 | -0.13275 | 61.0199 | 123.1293 | 123.3856 | -123.5687 | -123.5687
444.9844 | 123.4451 | -61.1114 | 62.1964 | 0.40904 | 0.0063138 | -0.018961 | 0.011961 | 0.038236 | -0.00050737 | 0.067451 | -61.3037 | 62.3932 | -61.441 | -61.3174 | 62.0544 | 0.10529 | -0.12817 | 0.21515 | 62.2604 | -61.3998 | -0.32959 | 0.19684 | -0.19226 | -0.20599 | -0.14191 | -0.28839 | 0.064087 | 0.13733 | 60.9833 | 61.3266 | 123.1659 | 123.5046 | -0.19226 | 123.3719 | 61.2167 | -0.28839 | 123.5046 | -0.19226 | 61.2167 | 123.1659 | 123.3719 | -123.6374 | -123.5962
445.9219 | 123.5779 | -61.0977 | 62.1689 | 0.45481 | -0.01398 | -0.026438 | -0.0061968 | 0.057462 | -0.014393 | 0.06211 | -61.2625 | 62.3291 | -61.4319 | -61.3815 | 62.0132 | 0 | 0.027466 | 0.1236 | 62.2742 | -61.4227 | -0.33417 | 0.16022 | -0.16479 | -0.28381 | -0.15564 | -0.32501 | 0.10529 | 0.16937 | 61.1252 | 61.2213 | 123.111 | 123.4268 | -0.16479 | 123.3719 | 61.0977 | -0.32501 | 123.4268 | -0.16479 | 61.0977 | 123.111 | 123.3719 | -123.6008 | -123.5916
446.9844 | 123.5458 | -61.0748 | 62.1414 | 0.45481 | -0.0022312 | -0.033915 | -0.00085683 | 0.042508 | -0.014393 | 0.067451 | -61.2259 | 62.3474 | -61.4182 | -61.4548 | 61.94 | -0.041199 | 0.054932 | 0.10986 | 62.2925 | -61.4365 | -0.34332 | 0.20599 | -0.15106 | -0.37994 | -0.20142 | -0.36163 | 0.15106 | 0.19226 | 61.1298 | 61.1847 | 123.0148 | 123.4222 | -0.15106 | 123.3673 | 61.0336 | -0.36163 | 123.4222 | -0.15106 | 61.0336 | 123.0148 | 123.3673 | -123.5596 | -123.5779
447.9219 | 123.5458 | -61.0794 | 62.1597 | 0.59214 | -0.011844 | -0.013621 | 0.00021117 | 0.045713 | -0.016529 | 0.071723 | -61.203 | 62.3428 | -61.409 | -61.4136 | 61.972 | -0.054932 | 0.050354 | 0.10071 | 62.3062 | -61.4136 | -0.32959 | 0.18311 | -0.1236 | -0.33417 | -0.18768 | -0.33417 | 0.14648 | 0.20599 | 61.1298 | 61.1801 | 123.0515 | 123.4222 | -0.1236 | 123.3856 | 61.0245 | -0.33417 | 123.4222 | -0.1236 | 61.0245 | 123.0515 | 123.3856 | -123.5687 | -123.5733
448.9844 | 123.4406 | -61.1343 | 62.2238 | 0.31749 | 0.011654 | -0.026438 | 0.015165 | 0.056394 | -0.016529 | 0.063178 | -61.2946 | 62.439 | -61.441 | -61.2213 | 62.1185 | 0.09613 | -0.09613 | 0.24719 | 62.2559 | -61.3632 | -0.3067 | 0.21515 | -0.16022 | -0.086975 | -0.10529 | -0.22888 | 0.032043 | 0.14648 | 61.0382 | 61.3815 | 123.2529 | 123.5733 | -0.16022 | 123.3902 | 61.2305 | -0.22888 | 123.5733 | -0.16022 | 61.2305 | 123.2529 | 123.3902 | -123.6649 | -123.587
449.9219 | 123.5413 | -61.0657 | 62.1368 | 0.4243 | -0.0054352 | -0.024302 | -0.0072648 | 0.031827 | -0.022938 | 0.084541 | -61.2213 | 62.3291 | -61.4136 | -61.29 | 61.908 | -0.054932 | 0.086975 | 0.068665 | 62.3062 | -61.441 | -0.3479 | 0.19226 | -0.15564 | -0.2243 | -0.22888 | -0.37537 | 0.16937 | 0.19226 | 61.1526 | 61.1343 | 122.9736 | 123.3948 | -0.15564 | 123.3719 | 61.0107 | -0.37537 | 123.3948 | -0.15564 | 61.0107 | 122.9736 | 123.3719 | -123.5504 | -123.5779
450.9688 | 123.4497 | -61.0886 | 62.233 | 0.39378 | -0.0011632 | -0.028574 | 0.015165 | 0.051053 | -0.0026434 | 0.067451 | -61.2534 | 62.4207 | -61.4227 | -61.2717 | 62.0911 | 0.11444 | -0.09613 | 0.23346 | 62.2833 | -61.3541 | -0.33417 | 0.18768 | -0.16479 | -0.1831 | -0.14191 | -0.2655 | 0.050354 | 0.16937 | 60.9924 | 61.322 | 123.1796 | 123.5092 | -0.16479 | 123.3719 | 61.203 | -0.2655 | 123.5092 | -0.16479 | 61.203 | 123.1796 | 123.3719 | -123.6557 | -123.587
451.9219 | 123.5367 | -61.0886 | 62.1689 | 0.50059 | -0.0054352 | -0.031779 | -0.00085683 | 0.045713 | -0.014393 | 0.070655 | -61.203 | 62.3154 | -61.4182 | -61.4319 | 61.972 | -0.054932 | 0.054932 | 0.091553 | 62.3062 | -61.4227 | -0.32959 | 0.14648 | -0.11444 | -0.34332 | -0.19684 | -0.33417 | 0.13733 | 0.21515 | 61.1435 | 61.1801 | 123.0606 | 123.4039 | -0.11444 | 123.3948 | 61.0336 | -0.33417 | 123.4039 | -0.11444 | 61.0336 | 123.0606 | 123.3948 | -123.587 | -123.5916
452.9219 | 123.4955 | -61.0748 | 62.2238 | 0.43956 | 0.0052458 | -0.017893 | 0.0066202 | 0.040372 | -0.00050737 | 0.077064 | -61.2579 | 62.3749 | -61.4502 | -61.3312 | 62.0316 | 0.004578 | -0.045776 | 0.16937 | 62.2559 | -61.3815 | -0.37537 | 0.15106 | -0.18311 | -0.25635 | -0.19226 | -0.3067 | 0.032043 | 0.19226 | 61.0291 | 61.2442 | 123.1064 | 123.4497 | -0.18311 | 123.3307 | 61.0794 | -0.3067 | 123.4497 | -0.18311 | 61.0794 | 123.1064 | 123.3307 | -123.674 | -123.6053
453.9844 | 123.5596 | -61.1023 | 62.178 | 0.91258 | -0.0086402 | -0.011485 | 0.0055522 | 0.038236 | -0.0058484 | 0.05677 | -61.1893 | 62.3245 | -61.4227 | -61.4227 | 61.9766 | -0.059509 | 0.050354 | 0.09613 | 62.3291 | -61.4227 | -0.32043 | 0.14648 | -0.086975 | -0.32043 | -0.20142 | -0.32043 | 0.15106 | 0.23346 | 61.1526 | 61.1984 | 123.0789 | 123.4268 | -0.086975 | 123.4314 | 61.0428 | -0.32043 | 123.4268 | -0.086975 | 61.0428 | 123.0789 | 123.4314 | -123.6008 | -123.6008
454.9219 | 123.5001 | -61.1114 | 62.1277 | 0.53111 | -0.0075722 | -0.029642 | -0.0051288 | 0.052121 | -0.0090524 | 0.078132 | -61.2122 | 62.3428 | -61.4227 | -61.4319 | 61.9675 | -0.059509 | 0.050354 | 0.091553 | 62.2971 | -61.4227 | -0.31128 | 0.21515 | -0.10071 | -0.32044 | -0.16022 | -0.31128 | 0.16937 | 0.21057 | 61.1618 | 61.203 | 123.0789 | 123.4543 | -0.10071 | 123.4085 | 61.0519 | -0.31128 | 123.4543 | -0.10071 | 61.0519 | 123.0789 | 123.4085 | -123.5504 | -123.5504
455.9688 | 123.4451 | -61.116 | 62.2284 | -0.018208 | -0.0065042 | -0.041392 | -0.00085683 | 0.052121 | -0.0079844 | 0.072791 | -61.2717 | 62.3978 | -61.4273 | -61.29 | 62.1048 | 0.12817 | -0.10986 | 0.26093 | 62.3199 | -61.3724 | -0.31128 | 0.16937 | -0.15564 | -0.17395 | -0.1236 | -0.25635 | 0.091552 | 0.15564 | 61.0062 | 61.377 | 123.2208 | 123.5138 | -0.15564 | 123.436 | 61.2442 | -0.25635 | 123.5138 | -0.15564 | 61.2442 | 123.2208 | 123.436 | -123.6557 | -123.6008
456.9219 | 123.5321 | -61.1114 | 62.1735 | 0.13438 | -9.5248e-05 | -0.036051 | 0.0023482 | 0.033964 | -0.0015754 | 0.072791 | -61.2076 | 62.3795 | -61.4365 | -61.4136 | 61.9766 | -0.059509 | 0.036621 | 0.091553 | 62.2742 | -61.4227 | -0.32501 | 0.20599 | -0.096131 | -0.30212 | -0.19684 | -0.31128 | 0.10071 | 0.22888 | 61.1481 | 61.203 | 123.0881 | 123.4909 | -0.096131 | 123.3856 | 61.0519 | -0.31128 | 123.4909 | -0.096131 | 61.0519 | 123.0881 | 123.3856 | -123.6099 | -123.5962
457.9844 | 123.4955 | -61.0703 | 62.233 | -0.18605 | 0.0020408 | -0.015757 | 0.017301 | 0.055326 | 0.01231 | 0.074928 | -61.2167 | 62.4161 | -61.4319 | -61.29 | 62.0544 | 0.059509 | -0.032043 | 0.20142 | 62.3062 | -61.4044 | -0.36163 | 0.18311 | -0.14648 | -0.21973 | -0.17853 | -0.33417 | 0.073242 | 0.21515 | 61.0382 | 61.2717 | 123.1247 | 123.4863 | -0.14648 | 123.3765 | 61.1298 | -0.33417 | 123.4863 | -0.14648 | 61.1298 | 123.1247 | 123.3765 | -123.6649 | -123.6374
458.9219 | 123.5046 | -61.1114 | 62.178 | 0.4243 | 0.015927 | -0.034983 | -0.0019248 | 0.047849 | -0.013325 | 0.071723 | -61.2717 | 62.3795 | -61.4594 | -61.3312 | 62.0407 | 0 | -0.018311 | 0.15106 | 62.2971 | -61.409 | -0.3479 | 0.20142 | -0.16022 | -0.21973 | -0.13733 | -0.29755 | 0.11902 | 0.18768 | 61.0931 | 61.2625 | 123.1522 | 123.4909 | -0.16022 | 123.4085 | 61.1114 | -0.29755 | 123.4909 | -0.16022 | 61.1114 | 123.1522 | 123.4085 | -123.6374 | -123.587
459.9844 | 123.4268 | -61.1298 | 62.1918 | 0.25645 | 0.0041778 | -0.012553 | 0.020506 | 0.054258 | -0.0047804 | 0.058906 | -61.2808 | 62.4481 | -61.4456 | -61.2396 | 62.1094 | 0.11444 | -0.14648 | 0.26093 | 62.2604 | -61.3998 | -0.31586 | 0.25635 | -0.15106 | -0.10986 | -0.082397 | -0.27008 | 0.068665 | 0.1648 | 60.9833 | 61.3907 | 123.2391 | 123.5779 | -0.15106 | 123.3902 | 61.2442 | -0.27008 | 123.5779 | -0.15106 | 61.2442 | 123.2391 | 123.3902 | -123.6374 | -123.5916
460.9219 | 123.5367 | -61.0931 | 62.1094 | 0.39378 | -0.0075722 | -0.0061444 | -0.0040608 | 0.05319 | -0.018665 | 0.073859 | -61.2259 | 62.3383 | -61.4136 | -61.4182 | 61.972 | -0.07782 | 0.045776 | 0.091553 | 62.3245 | -61.441 | -0.32043 | 0.22888 | -0.13275 | -0.32501 | -0.13733 | -0.3479 | 0.21515 | 0.18768 | 61.1389 | 61.1847 | 123.0652 | 123.4314 | -0.13275 | 123.4177 | 61.0153 | -0.3479 | 123.4314 | -0.13275 | 61.0153 | 123.0652 | 123.4177 | -123.5229 | -123.5504
461.9688 | 123.436 | -61.0977 | 62.2375 | -0.39968 | -0.0022312 | -0.031779 | 0.0076882 | 0.054258 | -0.0079844 | 0.067451 | -61.2488 | 62.3978 | -61.4227 | -61.2854 | 62.1735 | 0.12817 | -0.1236 | 0.24261 | 62.3199 | -61.3541 | -0.32501 | 0.16022 | -0.15106 | -0.18768 | -0.064087 | -0.25635 | 0.082397 | 0.17395 | 60.9741 | 61.3403 | 123.2712 | 123.4955 | -0.15106 | 123.4177 | 61.2259 | -0.25635 | 123.4955 | -0.15106 | 61.2259 | 123.2712 | 123.4177 | -123.6603 | -123.5916
462.9219 | 123.5367 | -61.0886 | 62.1689 | 0.57688 | -0.0043672 | -0.026438 | 0.0044842 | 0.048917 | -0.0090524 | 0.070655 | -61.2259 | 62.3474 | -61.4273 | -61.3678 | 61.9812 | -0.10529 | 0.018311 | 0.12817 | 62.2879 | -61.441 | -0.33874 | 0.17853 | -0.13733 | -0.27924 | -0.18768 | -0.35248 | 0.11902 | 0.20142 | 61.1069 | 61.2167 | 123.0698 | 123.436 | -0.13733 | 123.3765 | 60.9833 | -0.35248 | 123.436 | -0.13733 | 60.9833 | 123.0698 | 123.3765 | -123.5962 | -123.6099
463.9844 | 123.4909 | -61.1069 | 62.2147 | -0.38442 | 0.0063138 | -0.032847 | 0.010892 | 0.042508 | 0.0026966 | 0.066383 | -61.235 | 62.4298 | -61.4456 | -61.2717 | 62.0682 | 0.09613 | -0.064087 | 0.21515 | 62.3108 | -61.3678 | -0.33875 | 0.21515 | -0.12817 | -0.16479 | -0.14648 | -0.26093 | 0.09613 | 0.21057 | 61.0428 | 61.322 | 123.175 | 123.5367 | -0.12817 | 123.4177 | 61.203 | -0.26093 | 123.5367 | -0.12817 | 61.203 | 123.175 | 123.4177 | -123.6603 | -123.5825
464.9219 | 123.4909 | -61.1023 | 62.1552 | 0.4243 | 0.0020408 | -0.011485 | 0.0087562 | 0.048917 | -0.0037124 | 0.068519 | -61.2808 | 62.3932 | -61.4548 | -61.322 | 62.0499 | 0.022888 | -0.050354 | 0.17395 | 62.2696 | -61.3907 | -0.35248 | 0.23804 | -0.17853 | -0.21973 | -0.10528 | -0.28839 | 0.11444 | 0.17395 | 61.0519 | 61.2762 | 123.1522 | 123.4955 | -0.17853 | 123.3719 | 61.1252 | -0.28839 | 123.4955 | -0.17853 | 61.1252 | 123.1522 | 123.3719 | -123.6099 | -123.5458
465.9844 | 123.4177 | -61.0977 | 62.2238 | -0.39968 | -0.0011632 | -0.023234 | 0.0055522 | 0.052121 | -0.0069164 | 0.065314 | -61.29 | 62.4161 | -61.441 | -61.2579 | 62.0911 | 0.12817 | -0.10071 | 0.25177 | 62.3062 | -61.3678 | -0.34332 | 0.19226 | -0.19226 | -0.16022 | -0.13275 | -0.27008 | 0.082397 | 0.15106 | 60.997 | 61.3495 | 123.1888 | 123.5138 | -0.19226 | 123.4039 | 61.2259 | -0.27008 | 123.5138 | -0.19226 | 61.2259 | 123.1888 | 123.4039 | -123.6649 | -123.5916
466.9219 | 123.4131 | -61.1114 | 62.2192 | 0.21067 | 0.0063138 | -0.0082804 | 0.014097 | 0.048917 | -0.0047804 | 0.067451 | -61.2762 | 62.384 | -61.4365 | -61.2259 | 62.114 | 0.11902 | -0.15564 | 0.2655 | 62.2787 | -61.3907 | -0.32501 | 0.1648 | -0.1648 | -0.11444 | -0.10528 | -0.27924 | 0.05951 | 0.16022 | 60.9558 | 61.377 | 123.2254 | 123.4955 | -0.1648 | 123.3902 | 61.2305 | -0.27924 | 123.4955 | -0.1648 | 61.2305 | 123.2254 | 123.3902 | -123.6557 | -123.6099
467.9219 | 123.4085 | -61.1435 | 62.1735 | 0.33274 | -0.0097082 | -0.027506 | 0.0044842 | 0.057462 | -0.0079844 | 0.06211 | -61.29 | 62.4344 | -61.441 | -61.2534 | 62.0956 | 0.082397 | -0.11444 | 0.2243 | 62.2742 | -61.4044 | -0.29755 | 0.26093 | -0.14648 | -0.10986 | -0.07782 | -0.26093 | 0.10071 | 0.15106 | 61.0291 | 61.3678 | 123.2391 | 123.5779 | -0.14648 | 123.4177 | 61.2259 | -0.26093 | 123.5779 | -0.14648 | 61.2259 | 123.2391 | 123.4177 | -123.6145 | -123.5779
468.9844 | 123.4497 | -61.0794 | 62.265 | -0.38442 | -0.0011632 | -0.028574 | 0.013029 | 0.059598 | -0.012257 | 0.064246 | -61.0336 | 62.4435 | -61.409 | -61.2213 | 62.1323 | 0.10071 | -0.12817 | 0.27466 | 62.3062 | -61.3678 | -0.32959 | 0.17853 | 0.045777 | -0.14191 | -0.13275 | -0.28839 | 0.041198 | 0.37537 | 60.9512 | 61.3541 | 123.2117 | 123.5229 | 0.045777 | 123.3856 | 61.1801 | -0.28839 | 123.5229 | 0.045777 | 61.1801 | 123.2117 | 123.3856 | -123.674 | -123.6328
469.9219 | 123.4909 | -61.1252 | 62.1735 | 0.50059 | 0.0031088 | -0.015757 | 0.0044842 | 0.047849 | -0.00050737 | 0.058906 | -61.29 | 62.384 | -61.4502 | -61.3129 | 62.0636 | 0.050354 | -0.064087 | 0.19226 | 62.2971 | -61.4044 | -0.32501 | 0.21057 | -0.16479 | -0.18768 | -0.10986 | -0.27924 | 0.1236 | 0.16022 | 61.0611 | 61.3174 | 123.1888 | 123.5092 | -0.16479 | 123.4222 | 61.1755 | -0.27924 | 123.5092 | -0.16479 | 61.1755 | 123.1888 | 123.4222 | -123.6237 | -123.5779
470.9844 | 123.4451 | -61.1114 | 62.2467 | -0.52175 | -0.0086402 | -0.026438 | 0.00021117 | 0.052121 | -0.0069164 | 0.066383 | -61.2991 | 62.3795 | -61.4182 | -61.2762 | 62.0956 | 0.11444 | -0.10986 | 0.25635 | 62.3337 | -61.3586 | -0.3067 | 0.13275 | -0.18768 | -0.1648 | -0.15106 | -0.24719 | 0.086975 | 0.11902 | 61.0016 | 61.3678 | 123.2071 | 123.4909 | -0.18768 | 123.4451 | 61.2259 | -0.24719 | 123.4909 | -0.18768 | 61.2259 | 123.2071 | 123.4451 | -123.6649 | -123.6053
471.9219 | 123.4314 | -61.1298 | 62.2147 | 0.22593 | -0.0011632 | -0.018961 | 0.010892 | 0.049985 | -0.00050737 | 0.070655 | -61.2854 | 62.4207 | -61.4502 | -61.235 | 62.0773 | 0.073242 | -0.11902 | 0.26093 | 62.2742 | -61.3861 | -0.32043 | 0.20599 | -0.15564 | -0.10528 | -0.13733 | -0.25635 | 0.059509 | 0.16479 | 61.0107 | 61.3907 | 123.2071 | 123.5504 | -0.15564 | 123.4039 | 61.203 | -0.25635 | 123.5504 | -0.15564 | 61.203 | 123.2071 | 123.4039 | -123.6649 | -123.6008
472.9844 | 123.5275 | -61.1252 | 62.2192 | 0.43956 | -0.0086402 | -0.017893 | 0.018369 | 0.056394 | 0.0037646 | 0.081336 | -61.2991 | 62.4252 | -61.4685 | -61.2442 | 62.114 | 0.082397 | -0.10071 | 0.3067 | 62.2421 | -61.4273 | -0.34332 | 0.20599 | -0.17395 | -0.11902 | -0.10528 | -0.30212 | 0.022888 | 0.16937 | 61.0245 | 61.4319 | 123.2391 | 123.5504 | -0.17395 | 123.3673 | 61.2076 | -0.30212 | 123.5504 | -0.17395 | 61.2076 | 123.2391 | 123.3673 | -123.6877 | -123.6465
473.9219 | 123.4497 | -61.0977 | 62.1918 | 0.058086 | -0.0011632 | -0.011485 | 0.020506 | 0.063871 | -0.0058484 | 0.068519 | -61.2305 | 62.4161 | -61.4502 | -61.2671 | 62.0773 | 0.07782 | -0.086975 | 0.21973 | 62.2971 | -61.3861 | -0.35248 | 0.22431 | -0.13275 | -0.16937 | -0.11444 | -0.28839 | 0.10529 | 0.21973 | 61.0107 | 61.3174 | 123.175 | 123.5138 | -0.13275 | 123.3948 | 61.1755 | -0.28839 | 123.5138 | -0.13275 | 61.1755 | 123.175 | 123.3948 | -123.642 | -123.5779
474.9844 | 123.4406 | -61.0886 | 62.2421 | -0.36916 | -9.5248e-05 | -0.017893 | -0.0029928 | 0.043577 | -0.020801 | 0.063178 | -61.29 | 62.4161 | -61.4365 | -61.2717 | 62.1002 | 0.13275 | -0.10529 | 0.26093 | 62.3154 | -61.3586 | -0.3479 | 0.17395 | -0.20142 | -0.1831 | -0.14191 | -0.27008 | 0.073243 | 0.14648 | 60.9833 | 61.3495 | 123.1888 | 123.5046 | -0.20142 | 123.4039 | 61.2213 | -0.27008 | 123.5046 | -0.20142 | 61.2213 | 123.1888 | 123.4039 | -123.6786 | -123.6008
475.9219 | 123.4772 | -61.1298 | 62.1964 | -0.0029495 | -0.0011632 | -0.029642 | 0.017301 | 0.059598 | -0.0026434 | 0.097358 | -61.2213 | 62.4435 | -61.4227 | -61.29 | 61.9537 | 0.045776 | -0.032043 | 0.14648 | 62.2971 | -61.4182 | -0.29297 | 0.24719 | -0.091552 | -0.16022 | -0.24262 | -0.28839 | 0.10071 | 0.20142 | 61.0977 | 61.2762 | 123.0835 | 123.5733 | -0.091552 | 123.4268 | 61.1755 | -0.28839 | 123.5733 | -0.091552 | 61.1755 | 123.0835 | 123.4268 | -123.6191 | -123.6145
476.9844 | 123.5184 | -61.0611 | 62.2009 | 0.21067 | -0.0032992 | -0.041392 | -0.0040608 | 0.045713 | -0.018665 | 0.071723 | -61.2122 | 62.3383 | -61.4136 | -61.4227 | 61.9949 | -0.004578 | 0.027466 | 0.12817 | 62.352 | -61.4182 | -0.35248 | 0.13733 | -0.15106 | -0.36163 | -0.20599 | -0.35706 | 0.15106 | 0.20142 | 61.0886 | 61.1893 | 123.056 | 123.3994 | -0.15106 | 123.4131 | 61.0565 | -0.35706 | 123.3994 | -0.15106 | 61.0565 | 123.056 | 123.4131 | -123.6145 | -123.6191
477.9219 | 123.4177 | -61.1298 | 62.2147 | 0.25645 | 0.0020408 | -0.016825 | 0.0076882 | 0.051053 | -0.0015754 | 0.057838 | -61.2991 | 62.4435 | -61.4777 | -61.2213 | 62.1277 | 0.10071 | -0.11902 | 0.25177 | 62.2833 | -61.409 | -0.3479 | 0.22888 | -0.16937 | -0.091552 | -0.086975 | -0.27924 | 0.068664 | 0.17853 | 61.0107 | 61.3815 | 123.2574 | 123.5733 | -0.16937 | 123.4131 | 61.2305 | -0.27924 | 123.5733 | -0.16937 | 61.2305 | 123.2574 | 123.4131 | -123.6923 | -123.6237
478.9844 | 123.5596 | -61.0703 | 62.1689 | -0.033467 | -0.01398 | -0.022166 | -0.019015 | 0.039304 | -0.029346 | 0.086677 | -61.2534 | 62.3428 | -61.4182 | -61.4365 | 61.9812 | -0.027466 | 0.036621 | 0.11902 | 62.3337 | -61.4136 | -0.3479 | 0.17395 | -0.18311 | -0.36621 | -0.18768 | -0.34332 | 0.16479 | 0.16479 | 61.1069 | 61.1893 | 123.0515 | 123.4131 | -0.18311 | 123.4039 | 61.0428 | -0.34332 | 123.4131 | -0.18311 | 61.0428 | 123.0515 | 123.4039 | -123.587 | -123.5825
479.9219 | 123.4634 | -61.0977 | 62.233 | -0.29287 | 0.0073818 | -0.036051 | 0.017301 | 0.044645 | -0.0026434 | 0.072791 | -61.2442 | 62.439 | -61.409 | -61.2717 | 62.0499 | 0.086975 | -0.07782 | 0.21973 | 62.3245 | -61.3953 | -0.31128 | 0.20599 | -0.14648 | -0.17395 | -0.1831 | -0.29755 | 0.091553 | 0.16479 | 61.0199 | 61.3174 | 123.1476 | 123.5367 | -0.14648 | 123.4222 | 61.1847 | -0.29755 | 123.5367 | -0.14648 | 61.1847 | 123.1476 | 123.4222 | -123.642 | -123.6282
480.9844 | 123.5138 | -61.0703 | 62.2009 | -0.3539 | -0.012912 | -0.016825 | -0.0051288 | 0.047849 | -0.022938 | 0.068519 | -61.2122 | 62.3611 | -61.3998 | -61.3953 | 61.9904 | 0.009155 | 0.009155 | 0.13733 | 62.3383 | -61.3907 | -0.32959 | 0.16022 | -0.14191 | -0.32501 | -0.21057 | -0.32044 | 0.13733 | 0.18768 | 61.0794 | 61.2076 | 123.0606 | 123.4314 | -0.14191 | 123.4085 | 61.0794 | -0.32044 | 123.4314 | -0.14191 | 61.0794 | 123.0606 | 123.4085 | -123.6008 | -123.5916
481.9219 | 123.4406 | -61.0886 | 62.265 | -0.39968 | 0.0031088 | -0.038187 | 0.0055522 | 0.046781 | -0.0047804 | 0.069587 | -61.1252 | 62.4344 | -61.4044 | -61.2579 | 62.1323 | 0.10529 | -0.1236 | 0.27466 | 62.3245 | -61.3724 | -0.31586 | 0.16937 | -0.036621 | -0.16937 | -0.13275 | -0.28381 | 0.059509 | 0.27924 | 60.965 | 61.3632 | 123.2208 | 123.5229 | -0.036621 | 123.4131 | 61.1938 | -0.28381 | 123.5229 | -0.036621 | 61.1938 | 123.2208 | 123.4131 | -123.6694 | -123.6374
482.9219 | 123.468 | -61.0886 | 62.2559 | -0.24709 | -0.0065042 | -0.037119 | 0.013029 | 0.045713 | -0.00050737 | 0.072791 | -61.2671 | 62.439 | -61.4456 | -61.2534 | 62.0911 | 0.10529 | -0.091553 | 0.23804 | 62.3291 | -61.377 | -0.35706 | 0.18311 | -0.17853 | -0.16479 | -0.16479 | -0.28839 | 0.073243 | 0.17853 | 60.997 | 61.3266 | 123.1796 | 123.5275 | -0.17853 | 123.4177 | 61.1938 | -0.28839 | 123.5275 | -0.17853 | 61.1938 | 123.1796 | 123.4177 | -123.7015 | -123.6328
483.9844 | 123.5001 | -61.084 | 62.1597 | 0.40904 | -0.017185 | -0.033915 | -0.01047 | 0.038236 | -0.02187 | 0.071723 | -61.3083 | 62.3245 | -61.4319 | -61.3861 | 62.0224 | -0.022888 | -0.013733 | 0.15564 | 62.3474 | -61.4227 | -0.3479 | 0.16479 | -0.22431 | -0.30212 | -0.13733 | -0.33874 | 0.18768 | 0.1236 | 61.0703 | 61.2396 | 123.1064 | 123.4085 | -0.22431 | 123.4314 | 61.0611 | -0.33874 | 123.4085 | -0.22431 | 61.0611 | 123.1064 | 123.4314 | -123.5916 | -123.5825
484.9219 | 123.4131 | -61.1114 | 62.2604 | -0.4302 | -9.5248e-05 | -0.029642 | 0.00021117 | 0.038236 | -0.0069164 | 0.053565 | -61.2717 | 62.4115 | -61.4456 | -61.3129 | 62.2604 | 0.21515 | -0.13733 | 0.1236 | 62.2787 | -61.3632 | -0.33417 | 0.15106 | -0.16022 | -0.20142 | 0 | -0.25177 | 0.018311 | 0.17395 | 60.9741 | 61.235 | 123.3719 | 123.5229 | -0.16022 | 123.3902 | 61.3266 | -0.25177 | 123.5229 | -0.16022 | 61.3266 | 123.3719 | 123.3902 | -123.7061 | -123.6237
485.9844 | 123.5184 | -61.0977 | 62.1872 | 0.058086 | -0.0065042 | -0.05955 | -0.01581 | 0.035032 | -0.026142 | 0.069587 | -61.2671 | 62.3108 | -61.4182 | -61.3953 | 62.0087 | -0.009155 | -0.013733 | 0.15106 | 62.3428 | -61.409 | -0.32043 | 0.1236 | -0.16937 | -0.29755 | -0.17853 | -0.31128 | 0.15564 | 0.15106 | 61.084 | 61.2488 | 123.1064 | 123.4085 | -0.16937 | 123.4406 | 61.0886 | -0.31128 | 123.4085 | -0.16937 | 61.0886 | 123.1064 | 123.4406 | -123.6053 | -123.5962
486.9219 | 123.5092 | -61.0703 | 62.2055 | -0.3539 | -0.024662 | -0.028574 | -0.0051288 | 0.040372 | -0.017597 | 0.057838 | -61.2076 | 62.3428 | -61.3907 | -61.3449 | 62.0041 | 0.022888 | -0.009155 | 0.16937 | 62.3428 | -61.4136 | -0.32044 | 0.13733 | -0.13733 | -0.27466 | -0.20142 | -0.34332 | 0.13733 | 0.18311 | 61.0611 | 61.2396 | 123.0743 | 123.4131 | -0.13733 | 123.4131 | 61.0931 | -0.34332 | 123.4131 | -0.13733 | 61.0931 | 123.0743 | 123.4131 | -123.5962 | -123.6191
487.9219 | 123.4222 | -61.1114 | 62.2604 | -0.33864 | -0.0075722 | -0.033915 | 0.020506 | 0.055326 | -0.016529 | 0.061042 | -61.235 | 62.3703 | -61.4365 | -61.2625 | 62.1368 | 0.11902 | -0.13275 | 0.25177 | 62.3108 | -61.3861 | -0.32501 | 0.10986 | -0.1236 | -0.15106 | -0.1236 | -0.27466 | 0.050354 | 0.20142 | 60.9787 | 61.3632 | 123.2483 | 123.4818 | -0.1236 | 123.4222 | 61.2305 | -0.27466 | 123.4818 | -0.1236 | 61.2305 | 123.2483 | 123.4222 | -123.6969 | -123.6465
488.9844 | 123.5458 | -61.0977 | 62.2009 | 0.027569 | -0.019321 | -0.033915 | -0.0029928 | 0.040372 | -0.028278 | 0.066383 | -61.2946 | 62.3016 | -61.441 | -61.3998 | 62.0041 | -0.013733 | 0 | 0.14648 | 62.3154 | -61.3998 | -0.34332 | 0.10071 | -0.19684 | -0.30212 | -0.19684 | -0.30212 | 0.11444 | 0.14648 | 61.0977 | 61.2442 | 123.1018 | 123.3994 | -0.19684 | 123.4131 | 61.084 | -0.30212 | 123.3994 | -0.19684 | 61.084 | 123.1018 | 123.4131 | -123.642 | -123.6008
489.9219 | 123.4406 | -61.1023 | 62.2513 | -0.47597 | -0.011844 | -0.045664 | 0.013029 | 0.037168 | -0.020801 | 0.073859 | -61.2717 | 62.3978 | -61.441 | -61.2259 | 62.0956 | 0.1236 | -0.10986 | 0.24719 | 62.2925 | -61.3861 | -0.33875 | 0.14648 | -0.16937 | -0.1236 | -0.15564 | -0.28381 | 0.041198 | 0.16937 | 60.9924 | 61.3495 | 123.1979 | 123.5001 | -0.16937 | 123.3948 | 61.2259 | -0.28381 | 123.5001 | -0.16937 | 61.2259 | 123.1979 | 123.3948 | -123.6923 | -123.6374
490.9688 | 123.5458 | -61.1069 | 62.1689 | 0.1649 | -0.0097082 | -0.032847 | -0.0019248 | 0.040372 | -0.018665 | 0.061042 | -61.235 | 62.3016 | -61.409 | -61.409 | 61.9675 | -0.082397 | 0.032043 | 0.091553 | 62.2971 | -61.4182 | -0.30212 | 0.13275 | -0.12817 | -0.30212 | -0.20142 | -0.31128 | 0.12817 | 0.17395 | 61.1389 | 61.1984 | 123.0743 | 123.4085 | -0.12817 | 123.4039 | 61.0245 | -0.31128 | 123.4085 | -0.12817 | 61.0245 | 123.0743 | 123.4039 | -123.5779 | -123.587
491.9219 | 123.4634 | -61.1023 | 62.2467 | -0.41494 | -0.0011632 | -0.032847 | 0.00021117 | 0.044645 | -0.013325 | 0.068519 | -61.2396 | 62.3749 | -61.4319 | -61.2854 | 62.0728 | 0.082397 | -0.064087 | 0.20599 | 62.3154 | -61.3907 | -0.32959 | 0.12817 | -0.13733 | -0.18311 | -0.17395 | -0.28839 | 0.068665 | 0.19226 | 61.0382 | 61.3083 | 123.175 | 123.4772 | -0.13733 | 123.4177 | 61.1847 | -0.28839 | 123.4772 | -0.13733 | 61.1847 | 123.175 | 123.4177 | -123.6786 | -123.6374
492.9688 | 123.5504 | -61.0657 | 62.2009 | -0.018208 | -0.019321 | -0.052073 | -0.0051288 | 0.035032 | -0.022938 | 0.065314 | -61.2305 | 62.3383 | -61.409 | -61.409 | 61.9858 | -0.013733 | 0.013733 | 0.1236 | 62.3383 | -61.4136 | -0.34332 | 0.13733 | -0.16479 | -0.34332 | -0.21515 | -0.3479 | 0.13733 | 0.17853 | 61.0794 | 61.1893 | 123.0515 | 123.4039 | -0.16479 | 123.4039 | 61.0519 | -0.3479 | 123.4039 | -0.16479 | 61.0519 | 123.0515 | 123.4039 | -123.6099 | -123.6145
493.9219 | 123.4497 | -61.0519 | 62.1918 | -0.26235 | -0.020389 | -0.037119 | 0.0044842 | 0.032895 | -0.030414 | 0.071723 | -61.203 | 62.3154 | -61.4044 | -61.409 | 61.9629 | -0.032043 | -0.050354 | 0.059509 | 62.3978 | -61.4044 | -0.35248 | 0.1236 | -0.15106 | -0.35706 | -0.22888 | -0.35248 | 0.20599 | 0.20142 | 61.0016 | 61.1114 | 123.0148 | 123.3673 | -0.15106 | 123.4497 | 61.0199 | -0.35248 | 123.3673 | -0.15106 | 61.0199 | 123.0148 | 123.4497 | -123.5962 | -123.5962
494.9844 | 123.4406 | -61.1069 | 62.2284 | -0.32338 | 0.0031088 | -0.030711 | 0.010892 | 0.04144 | -0.017597 | 0.063178 | -61.2625 | 62.3932 | -61.4136 | -61.1847 | 62.0682 | 0.082397 | -0.11444 | 0.2655 | 62.3199 | -61.3495 | -0.3067 | 0.16479 | -0.15564 | -0.077819 | -0.16022 | -0.24261 | 0.091552 | 0.15106 | 60.9924 | 61.3724 | 123.175 | 123.5001 | -0.15564 | 123.4268 | 61.1893 | -0.24261 | 123.5001 | -0.15564 | 61.1893 | 123.175 | 123.4268 | -123.642 | -123.5779
495.9219 | 123.555 | -61.0657 | 62.2147 | -0.29287 | -0.026798 | -0.030711 | 0.0055522 | 0.037168 | -0.013325 | 0.05677 | -61.2076 | 62.3383 | -61.4227 | -61.4822 | 62.0819 | -0.032043 | 0.004578 | 0.14191 | 62.3474 | -61.3998 | -0.35705 | 0.1236 | -0.14191 | -0.41656 | -0.13275 | -0.33417 | 0.13275 | 0.21515 | 61.0703 | 61.2076 | 123.1476 | 123.4039 | -0.14191 | 123.4131 | 61.0336 | -0.33417 | 123.4039 | -0.14191 | 61.0336 | 123.1476 | 123.4131 | -123.6374 | -123.6145
496.9844 | 123.5413 | -61.0748 | 62.2192 | 0.042827 | -0.015048 | -0.041392 | -0.012606 | 0.028623 | -0.040028 | 0.064246 | -61.235 | 62.3291 | -61.4273 | -61.3998 | 61.9949 | -0.022888 | 0.027466 | 0.12817 | 62.3199 | -61.3861 | -0.35248 | 0.10986 | -0.16022 | -0.32501 | -0.2243 | -0.31128 | 0.10071 | 0.19226 | 61.1023 | 61.203 | 123.0698 | 123.4039 | -0.16022 | 123.3948 | 61.0519 | -0.31128 | 123.4039 | -0.16022 | 61.0519 | 123.0698 | 123.3948 | -123.6465 | -123.6053
497.9219 | 123.4818 | -61.0977 | 62.233 | -0.33864 | -0.012912 | -0.027506 | 0.010892 | 0.039304 | -0.014393 | 0.073859 | -61.2167 | 62.3428 | -61.3861 | -61.3083 | 62.0453 | 0.059509 | -0.036621 | 0.19226 | 62.3291 | -61.377 | -0.28839 | 0.10986 | -0.11902 | -0.21057 | -0.18768 | -0.27924 | 0.096131 | 0.16937 | 61.0611 | 61.29 | 123.143 | 123.4406 | -0.11902 | 123.4268 | 61.1572 | -0.27924 | 123.4406 | -0.11902 | 61.1572 | 123.143 | 123.4268 | -123.6191 | -123.6099
498.9844 | 123.6008 | -61.0611 | 62.1872 | -0.44545 | -0.010776 | -0.028574 | -0.0019248 | 0.043577 | -0.031483 | 0.06211 | -61.2213 | 62.2787 | -61.3907 | -61.4365 | 61.9446 | -0.045776 | 0.07782 | 0.082397 | 62.3383 | -61.3907 | -0.32959 | 0.091553 | -0.16022 | -0.37537 | -0.24262 | -0.32959 | 0.15106 | 0.16937 | 61.1389 | 61.1435 | 123.0057 | 123.3398 | -0.16022 | 123.3994 | 61.0153 | -0.32959 | 123.3398 | -0.16022 | 61.0153 | 123.0057 | 123.3994 | -123.5779 | -123.5779
499.9219 | 123.4726 | -61.1023 | 62.2055 | -0.18605 | 0.0063138 | -0.030711 | 0.02371 | 0.039304 | 0.0037646 | 0.057838 | -61.1893 | 62.4069 | -61.4044 | -61.2579 | 62.0453 | 0.054932 | -0.059509 | 0.18768 | 62.3016 | -61.3815 | -0.30212 | 0.20142 | -0.086975 | -0.15564 | -0.16022 | -0.27924 | 0.096131 | 0.21515 | 61.0428 | 61.29 | 123.1476 | 123.5092 | -0.086975 | 123.4039 | 61.1572 | -0.27924 | 123.5092 | -0.086975 | 61.1572 | 123.1476 | 123.4039 | -123.6099 | -123.587
500.9844 | 123.5367 | -61.0748 | 62.2147 | -0.018208 | -0.017185 | -0.046732 | -0.0040608 | 0.032895 | -0.050709 | 0.075996 | -61.2762 | 62.2787 | -61.441 | -61.3312 | 61.9949 | 0.018311 | 0.050354 | 0.13275 | 62.3337 | -61.3724 | -0.36621 | 0.064087 | -0.20142 | -0.25635 | -0.21973 | -0.29755 | 0.11902 | 0.16479 | 61.1252 | 61.2076 | 123.0698 | 123.3536 | -0.20142 | 123.4085 | 61.0931 | -0.29755 | 123.3536 | -0.20142 | 61.0931 | 123.0698 | 123.4085 | -123.6557 | -123.587
501.9219 | 123.5641 | -61.0565 | 62.2101 | -0.033467 | -0.021457 | -0.040324 | -0.0094018 | 0.035032 | -0.025074 | 0.066383 | -61.2259 | 62.3154 | -61.4319 | -61.409 | 61.9812 | -0.045776 | 0.027466 | 0.11902 | 62.3428 | -61.4044 | -0.37537 | 0.10529 | -0.16937 | -0.35248 | -0.22888 | -0.3479 | 0.13275 | 0.20599 | 61.084 | 61.1755 | 123.0377 | 123.3719 | -0.16937 | 123.3994 | 61.0107 | -0.3479 | 123.3719 | -0.16937 | 61.0107 | 123.0377 | 123.3994 | -123.642 | -123.6145
502.9844 | 123.5046 | -61.0657 | 62.1872 | 0.45481 | -0.0032992 | -0.0082804 | 0.0044842 | 0.033964 | -0.0079844 | 0.066383 | -61.2122 | 62.3291 | -61.4273 | -61.4044 | 61.9629 | -0.022888 | 0.064087 | -0.082397 | 62.2559 | -61.4639 | -0.36163 | 0.14191 | -0.14648 | -0.33874 | -0.2243 | -0.39825 | 0.068664 | 0.21515 | 61.1298 | 60.9833 | 123.0286 | 123.3948 | -0.14648 | 123.3215 | 61.0428 | -0.39825 | 123.3948 | -0.14648 | 61.0428 | 123.0286 | 123.3215 | -123.6145 | -123.6511
503.9219 | 123.5825 | -61.0519 | 62.178 | -0.12502 | -0.010776 | -0.029642 | -0.0019248 | 0.028623 | -0.028278 | 0.065314 | -61.2396 | 62.3337 | -61.4044 | -61.4044 | 61.9675 | -0.045776 | 0.050354 | 0.10529 | 62.3291 | -61.3907 | -0.35248 | 0.15564 | -0.18768 | -0.35248 | -0.21057 | -0.33875 | 0.15106 | 0.16479 | 61.1023 | 61.1572 | 123.0194 | 123.3856 | -0.18768 | 123.381 | 61.0062 | -0.33875 | 123.3856 | -0.18768 | 61.0062 | 123.0194 | 123.381 | -123.5825 | -123.5687
504.9844 | 123.5596 | -61.0611 | 62.178 | -0.10976 | -0.018253 | -0.021098 | -0.00085683 | 0.030759 | -0.02721 | 0.065314 | -61.2259 | 62.3428 | -61.4227 | -61.4044 | 61.9766 | -0.036621 | 0.022888 | 0.10986 | 62.3291 | -61.3907 | -0.36163 | 0.16479 | -0.16479 | -0.34332 | -0.20142 | -0.32959 | 0.15106 | 0.19684 | 61.084 | 61.171 | 123.0377 | 123.4039 | -0.16479 | 123.3902 | 61.0245 | -0.32959 | 123.4039 | -0.16479 | 61.0245 | 123.0377 | 123.3902 | -123.6008 | -123.5687
505.9219 | 123.555 | -61.0519 | 62.2009 | 0.058086 | -0.020389 | -0.054209 | 0.0034162 | 0.030759 | -0.026142 | 0.058906 | -61.2305 | 62.3383 | -61.4227 | -61.409 | 61.9583 | -0.032043 | 0.036621 | 0.10529 | 62.3383 | -61.3861 | -0.37079 | 0.13733 | -0.17853 | -0.35706 | -0.24262 | -0.33417 | 0.13733 | 0.19226 | 61.0886 | 61.1572 | 123.0103 | 123.3902 | -0.17853 | 123.3902 | 61.0199 | -0.33417 | 123.3902 | -0.17853 | 61.0199 | 123.0103 | 123.3902 | -123.6237 | -123.587
506.9844 | 123.5184 | -61.0794 | 62.1918 | 0.27171 | -0.019321 | -0.052073 | -0.0019248 | 0.04144 | -0.029346 | 0.058906 | -61.2534 | 62.3108 | -61.4502 | -61.3678 | 62.0041 | -0.013733 | -0.009155 | 0.14648 | 62.3245 | -61.3724 | -0.37079 | 0.11902 | -0.17395 | -0.28839 | -0.18768 | -0.29297 | 0.13275 | 0.19684 | 61.0703 | 61.2259 | 123.0835 | 123.3902 | -0.17395 | 123.4039 | 61.0657 | -0.29297 | 123.3902 | -0.17395 | 61.0657 | 123.0835 | 123.4039 | -123.642 | -123.5641
507.9219 | 123.5184 | -61.0794 | 62.1964 | 0.10386 | -0.0043672 | -0.043528 | 0.011961 | 0.038236 | -0.028278 | 0.074928 | -61.2808 | 62.3062 | -61.441 | -61.3541 | 62.0132 | 0 | -0.022888 | 0.14191 | 62.2879 | -61.3907 | -0.36163 | 0.10986 | -0.20142 | -0.27466 | -0.18311 | -0.31128 | 0.091553 | 0.16022 | 61.0565 | 61.2213 | 123.0927 | 123.3856 | -0.20142 | 123.3673 | 61.0794 | -0.31128 | 123.3856 | -0.20142 | 61.0794 | 123.0927 | 123.3673 | -123.6374 | -123.587
508.9844 | 123.5504 | -61.0886 | 62.1597 | 0.22593 | -0.0032992 | -0.037119 | 0.015165 | 0.035032 | -0.0079844 | 0.069587 | -61.2442 | 62.3474 | -61.4365 | -61.3586 | 61.9812 | -0.054932 | 0.041199 | 0.091553 | 62.3154 | -61.4365 | -0.3479 | 0.18768 | -0.15564 | -0.27008 | -0.17853 | -0.3479 | 0.15564 | 0.19226 | 61.1298 | 61.1801 | 123.0698 | 123.436 | -0.15564 | 123.4039 | 61.0336 | -0.3479 | 123.436 | -0.15564 | 61.0336 | 123.0698 | 123.4039 | -123.5962 | -123.5962
509.9219 | 123.4955 | -61.0519 | 62.2147 | -0.24709 | -0.0075722 | -0.036051 | 0.0012792 | 0.04144 | -0.016529 | 0.069587 | -61.1938 | 62.3428 | -61.4136 | -61.3632 | 61.9904 | 0.018311 | 0.013733 | 0.14648 | 62.3291 | -61.3953 | -0.36163 | 0.12817 | -0.14191 | -0.31128 | -0.22431 | -0.34332 | 0.11444 | 0.21973 | 61.0657 | 61.1984 | 123.0423 | 123.3948 | -0.14191 | 123.381 | 61.0703 | -0.34332 | 123.3948 | -0.14191 | 61.0703 | 123.0423 | 123.381 | -123.6282 | -123.6099
510.9844 | 123.381 | -61.0977 | 62.2467 | 0.33274 | -0.0011632 | -0.032847 | 0.022642 | 0.042508 | -0.0058484 | 0.066383 | -61.2808 | 62.4252 | -61.4548 | -61.2259 | 62.114 | 0.16022 | -0.032043 | 0.054932 | 62.1918 | -61.4136 | -0.35706 | 0.17853 | -0.18311 | -0.12817 | -0.13275 | -0.31586 | -0.054932 | 0.17395 | 61.0657 | 61.1526 | 123.2117 | 123.5229 | -0.18311 | 123.2895 | 61.2579 | -0.31586 | 123.5229 | -0.18311 | 61.2579 | 123.2117 | 123.2895 | -123.7015 | -123.6603
511.9219 | 123.5092 | -61.0794 | 62.2009 | 0.1649 | -0.010776 | -0.061686 | 0.0055522 | 0.038236 | -0.029346 | 0.071723 | -61.29 | 62.3016 | -61.4594 | -61.3541 | 62.0224 | 0 | -0.018311 | 0.15106 | 62.3108 | -61.4044 | -0.37994 | 0.10071 | -0.21057 | -0.27466 | -0.17853 | -0.32501 | 0.10986 | 0.16937 | 61.0611 | 61.2305 | 123.1018 | 123.381 | -0.21057 | 123.3902 | 61.0794 | -0.32501 | 123.381 | -0.21057 | 61.0794 | 123.1018 | 123.3902 | -123.6603 | -123.6053
512.9844 | 123.4497 | -61.1023 | 62.2101 | 0.36326 | 0.019131 | -0.032847 | 0.019437 | 0.037168 | -0.01012 | 0.052497 | -61.2946 | 62.4023 | -61.4365 | -61.1893 | 61.8622 | -0.054932 | -0.018311 | 0.37994 | 62.2696 | -61.3861 | -0.33417 | 0.19226 | -0.19226 | -0.086975 | -0.3479 | -0.28381 | 0.059509 | 0.14191 | 61.084 | 61.4822 | 122.9645 | 123.5046 | -0.19226 | 123.3719 | 61.0474 | -0.28381 | 123.5046 | -0.19226 | 61.0474 | 122.9645 | 123.3719 | -123.6465 | -123.5962
513.9219 | 123.5596 | -61.0886 | 62.1643 | 0.74473 | -0.0054352 | -0.057413 | 0.0076882 | 0.046781 | -0.022938 | 0.064246 | -61.1893 | 62.3474 | -61.4456 | -61.3861 | 61.9949 | -0.064087 | 0.041199 | 0.10071 | 62.2879 | -61.3998 | -0.35706 | 0.1831 | -0.10071 | -0.29755 | -0.16937 | -0.31128 | 0.1236 | 0.25635 | 61.1298 | 61.1893 | 123.0835 | 123.436 | -0.10071 | 123.3765 | 61.0245 | -0.31128 | 123.436 | -0.10071 | 61.0245 | 123.0835 | 123.3765 | -123.6099 | -123.5641
514.9844 | 123.4406 | -61.1114 | 62.2375 | -0.4302 | -0.0022312 | -0.027506 | 0.021574 | 0.049985 | -0.025074 | 0.081336 | -61.2854 | 62.4298 | -61.4502 | -61.3037 | 61.9537 | 0.11902 | -0.082397 | 0.22888 | 62.2925 | -61.3449 | -0.33875 | 0.19226 | -0.17395 | -0.19226 | -0.28381 | -0.23346 | 0.054931 | 0.16479 | 61.0291 | 61.3403 | 123.0652 | 123.5413 | -0.17395 | 123.4039 | 61.2305 | -0.23346 | 123.5413 | -0.17395 | 61.2305 | 123.0652 | 123.4039 | -123.6877 | -123.5825
515.9219 | 123.5229 | -61.0703 | 62.1643 | 0.33274 | -0.018253 | -0.018961 | -0.0029928 | 0.045713 | -0.020801 | 0.067451 | -61.2717 | 62.3383 | -61.4319 | -61.3678 | 62.027 | 0.013733 | -0.013733 | 0.12817 | 62.2833 | -61.3953 | -0.36163 | 0.17395 | -0.20142 | -0.29755 | -0.13733 | -0.32501 | 0.11902 | 0.16022 | 61.0565 | 61.1984 | 123.0972 | 123.4085 | -0.20142 | 123.3536 | 61.084 | -0.32501 | 123.4085 | -0.20142 | 61.084 | 123.0972 | 123.3536 | -123.5962 | -123.5596
516.9219 | 123.5596 | -61.0748 | 62.1735 | 1.4161 | -0.015048 | -0.0082804 | -0.011538 | 0.032895 | -0.026142 | 0.065314 | -61.0199 | 62.3154 | -61.3861 | -61.3724 | 61.9629 | -0.082397 | 0.041199 | 0.07782 | 62.3016 | -61.4319 | -0.31128 | 0.14191 | 0.054932 | -0.29755 | -0.21057 | -0.35706 | 0.12817 | 0.36621 | 61.116 | 61.1526 | 123.0377 | 123.3902 | 0.054932 | 123.3765 | 60.9924 | -0.35706 | 123.3902 | 0.054932 | 60.9924 | 123.0377 | 123.3765 | -123.5596 | -123.6053
517.9844 | 123.555 | -61.0748 | 62.1506 | 0.10386 | -0.0054352 | -0.018961 | 0.016233 | 0.040372 | -0.0015754 | 0.0792 | -61.1984 | 62.3474 | -61.4136 | -61.3861 | 61.9812 | -0.073242 | 0.036621 | 0.09613 | 62.2879 | -61.4319 | -0.33874 | 0.19684 | -0.1236 | -0.31128 | -0.16937 | -0.35706 | 0.13733 | 0.21515 | 61.1114 | 61.171 | 123.056 | 123.4222 | -0.1236 | 123.3627 | 61.0016 | -0.35706 | 123.4222 | -0.1236 | 61.0016 | 123.056 | 123.3627 | -123.5641 | -123.5825
518.9219 | 123.5321 | -61.084 | 62.1826 | -0.36916 | -0.011844 | -0.030711 | -0.0029928 | 0.048917 | -0.014393 | 0.070655 | -61.2259 | 62.3016 | -61.4227 | -61.3953 | 61.9675 | -0.068665 | 0.036621 | 0.10529 | 62.3016 | -61.4227 | -0.33874 | 0.11902 | -0.14191 | -0.31128 | -0.21515 | -0.33874 | 0.11902 | 0.19684 | 61.1206 | 61.1893 | 123.0515 | 123.3856 | -0.14191 | 123.3856 | 61.0153 | -0.33874 | 123.3856 | -0.14191 | 61.0153 | 123.0515 | 123.3856 | -123.6053 | -123.6053
519.9844 | 123.5184 | -61.084 | 62.1918 | -0.10976 | -0.0032992 | -0.038187 | 0.0034162 | 0.040372 | -0.020801 | 0.05677 | -61.2442 | 62.3566 | -61.4227 | -61.3953 | 61.9858 | -0.018311 | 0 | 0.13733 | 62.3199 | -61.4044 | -0.33874 | 0.16479 | -0.16022 | -0.31128 | -0.20599 | -0.32043 | 0.12817 | 0.17853 | 61.084 | 61.2213 | 123.0698 | 123.4406 | -0.16022 | 123.4039 | 61.0657 | -0.32043 | 123.4406 | -0.16022 | 61.0657 | 123.0698 | 123.4039 | -123.6145 | -123.5962
520.9219 | 123.5367 | -61.0748 | 62.1735 | 0.28697 | -0.01398 | -0.033915 | 0.0044842 | 0.046781 | -0.02187 | 0.068519 | -61.2122 | 62.3245 | -61.4227 | -61.409 | 61.9629 | -0.064087 | 0.032043 | 0.10071 | 62.2879 | -61.4182 | -0.3479 | 0.15106 | -0.13733 | -0.33417 | -0.21057 | -0.34332 | 0.11444 | 0.21057 | 61.1069 | 61.1755 | 123.0377 | 123.3994 | -0.13733 | 123.3627 | 61.0107 | -0.34332 | 123.3994 | -0.13733 | 61.0107 | 123.0377 | 123.3627 | -123.5962 | -123.5916
521.9844 | 123.4314 | -61.1298 | 62.1918 | 0.19541 | 0.010586 | -0.020029 | 0.02371 | 0.04144 | -0.017597 | 0.058906 | -61.2396 | 62.4298 | -61.4273 | -61.2305 | 62.0728 | 0.091553 | -0.09613 | 0.24261 | 62.2833 | -61.409 | -0.29755 | 0.23804 | -0.10986 | -0.10071 | -0.11902 | -0.27924 | 0.091553 | 0.18768 | 61.0336 | 61.3724 | 123.2025 | 123.5596 | -0.10986 | 123.4131 | 61.2213 | -0.27924 | 123.5596 | -0.10986 | 61.2213 | 123.2025 | 123.4131 | -123.6191 | -123.6008
522.9219 | 123.4589 | -61.0977 | 62.1872 | 0.50059 | 0.0020408 | -0.024302 | 0.013029 | 0.045713 | -0.0079844 | 0.064246 | -61.2762 | 62.3795 | -61.4639 | -61.2671 | 62.0682 | 0.050354 | -0.082397 | 0.18768 | 62.2833 | -61.4136 | -0.36621 | 0.19226 | -0.17853 | -0.16937 | -0.11902 | -0.31586 | 0.09613 | 0.18768 | 61.0153 | 61.2854 | 123.1659 | 123.4772 | -0.17853 | 123.381 | 61.1481 | -0.31586 | 123.4772 | -0.17853 | 61.1481 | 123.1659 | 123.381 | -123.6511 | -123.6008
523.9688 | 123.5779 | -61.0794 | 62.178 | -0.36916 | -0.015048 | -0.044596 | -0.0019248 | 0.046781 | -0.025074 | 0.049293 | -61.1847 | 62.3291 | -61.4136 | -61.2854 | 62.3474 | -0.041199 | -0.17395 | 0.10986 | 62.3199 | -61.3861 | -0.33417 | 0.15106 | -0.10528 | -0.20599 | 0.16937 | -0.3067 | 0.14191 | 0.22888 | 60.9055 | 61.1893 | 123.4268 | 123.4085 | -0.10528 | 123.3994 | 61.0382 | -0.3067 | 123.4085 | -0.10528 | 61.0382 | 123.4268 | 123.3994 | -123.5916 | -123.5641
524.9219 | 123.555 | -61.0657 | 62.1643 | 0.21067 | 0.010586 | -0.022166 | 0.013029 | 0.052121 | -0.019733 | 0.069587 | -61.2717 | 62.3337 | -61.4456 | -61.3998 | 61.9537 | -0.050354 | 0.045776 | 0.10071 | 62.3291 | -61.4227 | -0.37994 | 0.16937 | -0.20599 | -0.33417 | -0.21057 | -0.35705 | 0.16479 | 0.17395 | 61.1114 | 61.1664 | 123.0194 | 123.3994 | -0.20599 | 123.3948 | 61.0153 | -0.35705 | 123.3994 | -0.20599 | 61.0153 | 123.0194 | 123.3948 | -123.6099 | -123.587
525.9844 | 123.5367 | -61.1114 | 62.2284 | 0.30223 | 0.014859 | 0.0034686 | 0.0087562 | 0.049985 | -0.01012 | 0.065314 | -61.2991 | 62.3932 | -61.4822 | -61.2259 | 62.0956 | 0.091553 | -0.11902 | 0.31128 | 62.2284 | -61.3907 | -0.37079 | 0.16479 | -0.18768 | -0.11444 | -0.13275 | -0.27924 | 0 | 0.18311 | 60.9924 | 61.4227 | 123.2071 | 123.5046 | -0.18768 | 123.3398 | 61.203 | -0.27924 | 123.5046 | -0.18768 | 61.203 | 123.2071 | 123.3398 | -123.7106 | -123.6191
526.9219 | 123.4085 | -61.0977 | 62.2055 | 0.40904 | 0.0095178 | -0.024302 | -0.00085683 | 0.042508 | -0.01012 | 0.061042 | -61.29 | 62.4115 | -61.4594 | -61.1389 | 61.9904 | 0.091553 | -0.059509 | 0.21057 | 62.2604 | -61.3998 | -0.36163 | 0.20599 | -0.19226 | -0.041199 | -0.21515 | -0.30212 | 0.054932 | 0.16937 | 61.0382 | 61.3083 | 123.0881 | 123.5092 | -0.19226 | 123.3582 | 61.1893 | -0.30212 | 123.5092 | -0.19226 | 61.1893 | 123.0881 | 123.3582 | -123.6649 | -123.6053
527.9219 | 123.4268 | -61.1343 | 62.2101 | 0.21067 | 0.0084498 | -0.034983 | 0.015165 | 0.055326 | -0.00050737 | 0.065314 | -61.2625 | 62.4298 | -61.4548 | -61.2305 | 62.1048 | 0.10071 | -0.11902 | 0.2655 | 62.3199 | -61.3815 | -0.32044 | 0.21973 | -0.12817 | -0.096131 | -0.10529 | -0.24719 | 0.10986 | 0.19226 | 61.0153 | 61.3998 | 123.2391 | 123.5641 | -0.12817 | 123.4543 | 61.235 | -0.24719 | 123.5641 | -0.12817 | 61.235 | 123.2391 | 123.4543 | -123.6649 | -123.5916
528.9844 | 123.4909 | -61.0794 | 62.2192 | -0.33864 | 0.0041778 | -0.022166 | 0.011961 | 0.046781 | -0.0026434 | 0.071723 | -61.2213 | 62.4435 | -61.4365 | -61.2762 | 62.0682 | 0.064087 | -0.054932 | 0.1831 | 62.2925 | -61.4044 | -0.35705 | 0.2243 | -0.14191 | -0.19684 | -0.15106 | -0.32501 | 0.073242 | 0.21515 | 61.0245 | 61.2625 | 123.1476 | 123.5229 | -0.14191 | 123.3719 | 61.1435 | -0.32501 | 123.5229 | -0.14191 | 61.1435 | 123.1476 | 123.3719 | -123.6557 | -123.6237
529.9219 | 123.4268 | -61.1435 | 62.2101 | 0.22593 | -0.0043672 | -0.0082804 | 0.024778 | 0.059598 | -0.0026434 | 0.061042 | -61.2442 | 62.4435 | -61.441 | -61.2396 | 62.114 | 0.10986 | -0.11902 | 0.25635 | 62.2833 | -61.3815 | -0.29755 | 0.23346 | -0.10071 | -0.09613 | -0.09613 | -0.23804 | 0.073242 | 0.19684 | 61.0245 | 61.3998 | 123.2574 | 123.587 | -0.10071 | 123.4268 | 61.2534 | -0.23804 | 123.587 | -0.10071 | 61.2534 | 123.2574 | 123.4268 | -123.6511 | -123.5916
530.9844 | 123.4543 | -61.1252 | 62.2147 | -1.2084 | -0.0065042 | -0.031779 | 0.015165 | 0.052121 | -0.0058484 | 0.078132 | -61.4639 | 62.4435 | -61.4502 | -61.29 | 62.1048 | 0.15106 | -0.086975 | 0.2655 | 62.3291 | -61.3586 | -0.32501 | 0.22888 | -0.33875 | -0.16479 | -0.10986 | -0.23346 | 0.11444 | -0.013733 | 61.0382 | 61.3907 | 123.23 | 123.5687 | -0.33875 | 123.4543 | 61.2762 | -0.23346 | 123.5687 | -0.33875 | 61.2762 | 123.23 | 123.4543 | -123.6649 | -123.5733
531.9219 | 123.4268 | -61.1343 | 62.2101 | 0.33274 | -0.0022312 | -0.017893 | 0.0044842 | 0.051053 | -0.0058484 | 0.070655 | -61.3083 | 62.4207 | -61.4731 | -61.5738 | 62.0956 | 0.21515 | -0.064087 | 0.1831 | 62.3199 | -61.3907 | -0.33875 | 0.21057 | -0.17395 | -0.43945 | -0.11444 | -0.25635 | 0.10986 | 0.16479 | 61.0703 | 61.3174 | 123.23 | 123.555 | -0.17395 | 123.4543 | 61.3495 | -0.25635 | 123.555 | -0.17395 | 61.3495 | 123.23 | 123.4543 | -123.6832 | -123.6008
532.9844 | 123.436 | -61.1069 | 62.2421 | -1.1626 | 0.00097275 | -0.033915 | 0.0066202 | 0.052121 | -0.01012 | 0.072791 | -61.3037 | 62.4252 | -61.441 | -61.2671 | 62.0865 | 0.11444 | -0.091553 | 0.26093 | 62.3108 | -61.3953 | -0.33417 | 0.18311 | -0.19684 | -0.16022 | -0.15564 | -0.28839 | 0.068665 | 0.13733 | 61.0153 | 61.3678 | 123.1934 | 123.5321 | -0.19684 | 123.4177 | 61.2213 | -0.28839 | 123.5321 | -0.19684 | 61.2213 | 123.1934 | 123.4177 | -123.6832 | -123.6374
533.9219 | 123.4497 | -61.1114 | 62.1964 | 0.10386 | -0.0032992 | -0.022166 | 0.021574 | 0.048917 | 0.0059006 | 0.069587 | -61.2305 | 62.4481 | -61.4365 | -61.2488 | 62.0911 | 0.091553 | -0.10071 | 0.21515 | 62.2971 | -61.4044 | -0.32501 | 0.25177 | -0.11902 | -0.13733 | -0.10529 | -0.29297 | 0.10071 | 0.20599 | 61.0107 | 61.3266 | 123.2025 | 123.5596 | -0.11902 | 123.4085 | 61.203 | -0.29297 | 123.5596 | -0.11902 | 61.203 | 123.2025 | 123.4085 | -123.6328 | -123.6008
534.9219 | 123.4634 | -61.1252 | 62.2238 | -0.094502 | -0.0075722 | -0.023234 | 0.0023482 | 0.051053 | -0.012257 | 0.075996 | -61.2167 | 62.4252 | -61.441 | -61.29 | 62.0682 | 0.059509 | -0.050354 | 0.20142 | 62.3245 | -61.409 | -0.31586 | 0.20142 | -0.091553 | -0.16479 | -0.15564 | -0.28381 | 0.10071 | 0.2243 | 61.0748 | 61.3266 | 123.1934 | 123.5504 | -0.091553 | 123.4497 | 61.1847 | -0.28381 | 123.5504 | -0.091553 | 61.1847 | 123.1934 | 123.4497 | -123.6649 | -123.6328
535.9844 | 123.3902 | -61.1435 | 62.2192 | 0.058086 | 0.00097275 | -0.0072124 | 0.020506 | 0.049985 | 0.0048326 | 0.065314 | -61.2671 | 62.4573 | -61.4365 | -61.2534 | 62.1048 | 0.082397 | -0.09613 | 0.27924 | 62.2879 | -61.3998 | -0.29297 | 0.23804 | -0.1236 | -0.10986 | -0.11444 | -0.25635 | 0.068665 | 0.16937 | 61.0474 | 61.4227 | 123.2483 | 123.6008 | -0.1236 | 123.4314 | 61.2259 | -0.25635 | 123.6008 | -0.1236 | 61.2259 | 123.2483 | 123.4314 | -123.6557 | -123.6191
536.9219 | 123.4543 | -61.0977 | 62.2009 | -0.063984 | 0.0031088 | -0.021098 | 0.0098242 | 0.048917 | 0.0069696 | 0.084541 | -61.2259 | 62.4664 | -61.4182 | -61.3037 | 61.9904 | 0.059509 | -0.013733 | 0.15564 | 62.2925 | -61.409 | -0.32043 | 0.2655 | -0.12817 | -0.20599 | -0.21057 | -0.31128 | 0.091552 | 0.19226 | 61.084 | 61.2534 | 123.0881 | 123.5641 | -0.12817 | 123.3902 | 61.1572 | -0.31128 | 123.5641 | -0.12817 | 61.1572 | 123.0881 | 123.3902 | -123.6191 | -123.6099
537.9844 | 123.5229 | -61.0565 | 62.1872 | -0.41494 | -0.012912 | -0.028574 | -0.019015 | 0.046781 | -0.018665 | 0.074928 | -61.1847 | 62.3703 | -61.3953 | -61.409 | 61.9812 | 0.004578 | 0.032043 | 0.14191 | 62.3611 | -61.3907 | -0.33874 | 0.1831 | -0.12817 | -0.35248 | -0.20599 | -0.33417 | 0.17395 | 0.21057 | 61.0886 | 61.1984 | 123.0377 | 123.4268 | -0.12817 | 123.4177 | 61.0611 | -0.33417 | 123.4268 | -0.12817 | 61.0611 | 123.0377 | 123.4177 | -123.5825 | -123.5779
538.9219 | 123.436 | -61.1298 | 62.2101 | 0.39378 | -0.011844 | -0.032847 | 0.013029 | 0.055326 | -0.0069164 | 0.064246 | -61.3266 | 62.4344 | -61.4594 | -61.2579 | 62.1094 | 0.091553 | -0.13275 | 0.25635 | 62.2787 | -61.4044 | -0.32959 | 0.2243 | -0.19684 | -0.12817 | -0.10071 | -0.27466 | 0.068665 | 0.13275 | 60.997 | 61.3861 | 123.2391 | 123.5641 | -0.19684 | 123.4085 | 61.2213 | -0.27466 | 123.5641 | -0.19684 | 61.2213 | 123.2391 | 123.4085 | -123.6694 | -123.6145
539.9688 | 123.5504 | -61.0336 | 62.1872 | -0.20131 | -0.017185 | -0.032847 | -0.01047 | 0.044645 | -0.020801 | 0.074928 | -61.2122 | 62.3062 | -61.4456 | -61.4731 | 61.9171 | -0.050354 | 0.082397 | 0.09613 | 62.3566 | -61.4227 | -0.41199 | 0.11902 | -0.17853 | -0.43945 | -0.27008 | -0.3891 | 0.16937 | 0.23346 | 61.116 | 61.1298 | 122.9507 | 123.3398 | -0.17853 | 123.3902 | 60.9833 | -0.3891 | 123.3398 | -0.17853 | 60.9833 | 122.9507 | 123.3902 | -123.6328 | -123.6099
540.9219 | 123.5321 | -61.0611 | 62.2284 | -0.41494 | -0.010776 | -0.04246 | -0.0029928 | 0.045713 | -0.0079844 | 0.069587 | -61.203 | 62.384 | -61.4136 | -61.3861 | 61.9995 | 0.013733 | 0.004578 | 0.15564 | 62.3611 | -61.4136 | -0.35248 | 0.15564 | -0.14191 | -0.32501 | -0.22888 | -0.35248 | 0.13275 | 0.21057 | 61.0657 | 61.2167 | 123.0606 | 123.4451 | -0.14191 | 123.4222 | 61.0748 | -0.35248 | 123.4451 | -0.14191 | 61.0748 | 123.0606 | 123.4222 | -123.642 | -123.642
541.9844 | 123.4497 | -61.1023 | 62.2696 | -0.46071 | -0.0075722 | -0.011485 | 0.0076882 | 0.048917 | -0.024006 | 0.075996 | -61.2671 | 62.4161 | -61.4685 | -61.2534 | 62.0819 | 0.13275 | -0.10986 | 0.27466 | 62.2925 | -61.3678 | -0.36621 | 0.14648 | -0.1648 | -0.15106 | -0.18768 | -0.2655 | 0.022888 | 0.20142 | 60.9924 | 61.377 | 123.1842 | 123.5184 | -0.1648 | 123.3948 | 61.235 | -0.2655 | 123.5184 | -0.1648 | 61.235 | 123.1842 | 123.3948 | -123.7381 | -123.6374
542.9219 | 123.4039 | -61.1069 | 62.2284 | 0.1649 | 0.0041778 | -0.02537 | 0.019437 | 0.051053 | 0.0037646 | 0.069587 | -61.2488 | 62.4298 | -61.441 | -61.2488 | 62.0773 | 0.091553 | -0.10986 | 0.26093 | 62.2787 | -61.4044 | -0.33417 | 0.20142 | -0.14191 | -0.14191 | -0.15106 | -0.29755 | 0.050354 | 0.19226 | 60.997 | 61.3678 | 123.1842 | 123.5367 | -0.14191 | 123.3856 | 61.1984 | -0.29755 | 123.5367 | -0.14191 | 61.1984 | 123.1842 | 123.3856 | -123.6694 | -123.6328
543.9844 | 123.4543 | -61.0794 | 62.2192 | -0.36916 | 0.0041778 | -0.015757 | 0.025846 | 0.040372 | -0.0047804 | 0.067451 | -61.2442 | 62.4298 | -61.4502 | -61.2717 | 62.0544 | 0.068665 | -0.054932 | 0.21973 | 62.3108 | -61.4044 | -0.37079 | 0.21057 | -0.16479 | -0.19226 | -0.16479 | -0.32501 | 0.091553 | 0.20599 | 61.0245 | 61.2991 | 123.1338 | 123.5092 | -0.16479 | 123.3902 | 61.1481 | -0.32501 | 123.5092 | -0.16479 | 61.1481 | 123.1338 | 123.3902 | -123.6694 | -123.6237
544.9219 | 123.4909 | -61.116 | 62.2192 | -0.018208 | -0.0022312 | -0.016825 | 0.014097 | 0.037168 | -0.0079844 | 0.064246 | -61.1984 | 62.4527 | -61.4227 | -61.2625 | 62.0316 | 0.009155 | -0.050354 | 0.21515 | 62.3108 | -61.409 | -0.3067 | 0.23346 | -0.082397 | -0.14648 | -0.18768 | -0.29297 | 0.091553 | 0.2243 | 61.0657 | 61.3312 | 123.1476 | 123.5687 | -0.082397 | 123.4268 | 61.1252 | -0.29297 | 123.5687 | -0.082397 | 61.1252 | 123.1476 | 123.4268 | -123.642 | -123.6282
545.9531 | 123.4222 | -61.1206 | 62.2055 | 0.50059 | -9.5248e-05 | -0.033915 | 0.018369 | 0.049985 | -0.0015754 | 0.065314 | -61.2946 | 62.4252 | -61.4594 | -61.2488 | 62.1094 | 0.091553 | -0.13275 | 0.2655 | 62.2925 | -61.3724 | -0.33875 | 0.21973 | -0.17395 | -0.12817 | -0.09613 | -0.25177 | 0.086975 | 0.16479 | 60.9879 | 61.3861 | 123.23 | 123.5458 | -0.17395 | 123.4131 | 61.2122 | -0.25177 | 123.5458 | -0.17395 | 61.2122 | 123.23 | 123.4131 | -123.6649 | -123.5779
547.3594 | 123.5229 | -61.0886 | 62.2101 | -0.36916 | -0.0075722 | -0.051005 | -0.0029928 | 0.052121 | -0.0079844 | 0.061042 | -61.1938 | 62.3978 | -61.4044 | -61.3678 | 62.0178 | 0.041199 | -0.018311 | 0.17853 | 62.3383 | -61.3907 | -0.31586 | 0.18768 | -0.10529 | -0.27924 | -0.19226 | -0.30212 | 0.12817 | 0.21057 | 61.0703 | 61.2671 | 123.1064 | 123.4863 | -0.10529 | 123.4268 | 61.1298 | -0.30212 | 123.4863 | -0.10529 | 61.1298 | 123.1064 | 123.4268 | -123.6145 | -123.6008
547.9219 | 123.555 | -61.0703 | 62.1506 | 0.54637 | 0.0063138 | -0.034983 | 0.015165 | 0.043577 | -0.0047804 | 0.071723 | -61.2396 | 62.3886 | -61.4365 | -61.3632 | 61.9858 | -0.036621 | 0 | 0.15106 | 62.3062 | -61.4548 | -0.36621 | 0.23804 | -0.16937 | -0.29297 | -0.16479 | -0.38452 | 0.15564 | 0.19684 | 61.0703 | 61.2213 | 123.056 | 123.4589 | -0.16937 | 123.3765 | 61.0336 | -0.38452 | 123.4589 | -0.16937 | 61.0336 | 123.056 | 123.3765 | -123.587 | -123.6053
548.9219 | 123.4634 | -61.0886 | 62.2375 | -0.27761 | 0.0052458 | -0.032847 | 0.017301 | 0.042508 | -0.0015754 | 0.06211 | -61.2488 | 62.4664 | -61.4319 | -61.2488 | 62.1048 | 0.10071 | -0.10529 | 0.25177 | 62.3337 | -61.3998 | -0.34332 | 0.22888 | -0.16022 | -0.16022 | -0.13275 | -0.31128 | 0.09613 | 0.18311 | 60.9833 | 61.3403 | 123.1934 | 123.555 | -0.16022 | 123.4222 | 61.1893 | -0.31128 | 123.555 | -0.16022 | 61.1893 | 123.1934 | 123.4222 | -123.6694 | -123.6374
549.9219 | 123.4451 | -61.1206 | 62.2284 | 0.01231 | 0.00097275 | -0.012553 | 0.018369 | 0.054258 | 0.0016286 | 0.072791 | -61.2259 | 62.4344 | -61.4594 | -61.2625 | 62.0819 | 0.059509 | -0.086975 | 0.21973 | 62.2971 | -61.409 | -0.33875 | 0.20599 | -0.10529 | -0.14191 | -0.14648 | -0.28839 | 0.068664 | 0.23346 | 61.0336 | 61.3403 | 123.2025 | 123.555 | -0.10529 | 123.4177 | 61.1801 | -0.28839 | 123.555 | -0.10529 | 61.1801 | 123.2025 | 123.4177 | -123.6877 | -123.6374
551.0156 | 123.5413 | -61.0565 | 62.1918 | -0.27761 | -0.022525 | -0.020029 | 0.0023482 | 0.037168 | -0.018665 | 0.077064 | -61.1893 | 62.352 | -61.4182 | -61.6013 | 61.9171 | 0.009155 | 0.032043 | 0.07782 | 62.3611 | -61.4273 | -0.36163 | 0.16022 | -0.13275 | -0.54474 | -0.27466 | -0.37079 | 0.16937 | 0.22888 | 61.0886 | 61.1343 | 122.9736 | 123.4085 | -0.13275 | 123.4177 | 61.0657 | -0.37079 | 123.4085 | -0.13275 | 61.0657 | 122.9736 | 123.4177 | -123.6099 | -123.6191
551.9219 | 123.4589 | -61.1252 | 62.1964 | -0.21657 | -0.0043672 | -0.036051 | 0.016233 | 0.04144 | -0.011188 | 0.058906 | -61.29 | 62.4527 | -61.4456 | -61.2762 | 62.0682 | 0.059509 | -0.07782 | 0.21515 | 62.3016 | -61.3953 | -0.32044 | 0.25635 | -0.16479 | -0.15106 | -0.12817 | -0.27008 | 0.10529 | 0.15564 | 61.0474 | 61.3403 | 123.1934 | 123.5779 | -0.16479 | 123.4268 | 61.1847 | -0.27008 | 123.5779 | -0.16479 | 61.1847 | 123.1934 | 123.4268 | -123.642 | -123.5916
552.9844 | 123.4222 | -61.0977 | 62.233 | -0.44545 | 0.0063138 | -0.018961 | 0.025846 | 0.055326 | -0.016529 | 0.06211 | -61.2717 | 62.4115 | -61.4777 | -61.2122 | 62.0773 | 0.10071 | -0.082397 | 0.27466 | 62.3108 | -61.377 | -0.37994 | 0.17853 | -0.17395 | -0.11444 | -0.15564 | -0.27924 | 0.07782 | 0.20599 | 61.0153 | 61.3724 | 123.175 | 123.5092 | -0.17395 | 123.4085 | 61.1984 | -0.27924 | 123.5092 | -0.17395 | 61.1984 | 123.175 | 123.4085 | -123.7106 | -123.6099
553.9219 | 123.3994 | -61.1252 | 62.178 | 0.14964 | -9.5248e-05 | -0.026438 | 0.014097 | 0.051053 | 0.0037646 | 0.059974 | -61.2625 | 62.4298 | -61.441 | -61.2579 | 62.0911 | 0.09613 | -0.15106 | 0.24719 | 62.2879 | -61.4182 | -0.31586 | 0.25177 | -0.13733 | -0.13275 | -0.086976 | -0.29297 | 0.10986 | 0.17853 | 60.9741 | 61.3724 | 123.2162 | 123.555 | -0.13733 | 123.4131 | 61.2213 | -0.29297 | 123.555 | -0.13733 | 61.2213 | 123.2162 | 123.4131 | -123.6191 | -123.5962
554.9844 | 123.4634 | -61.1069 | 62.2238 | -0.50649 | 0.016995 | -0.049937 | 0.013029 | 0.048917 | -0.011188 | 0.064246 | -61.2488 | 62.4619 | -61.4548 | -61.2671 | 62.0911 | 0.10529 | -0.091553 | 0.25635 | 62.3474 | -61.3861 | -0.3479 | 0.23804 | -0.14191 | -0.16022 | -0.13275 | -0.27923 | 0.1236 | 0.20599 | 61.0153 | 61.3632 | 123.1979 | 123.5687 | -0.14191 | 123.4543 | 61.2122 | -0.27923 | 123.5687 | -0.14191 | 61.2122 | 123.1979 | 123.4543 | -123.6786 | -123.6099
555.9375 | 123.5367 | -61.0565 | 62.1597 | 0.33274 | -0.012912 | -0.030711 | 0.0012792 | 0.043577 | -0.0058484 | 0.064246 | -61.1847 | 62.3749 | -61.4319 | -61.3998 | 61.9675 | -0.059509 | 0.022888 | 0.10071 | 62.3062 | -61.4227 | -0.37537 | 0.21515 | -0.12817 | -0.34332 | -0.19226 | -0.36621 | 0.14648 | 0.24719 | 61.0794 | 61.1572 | 123.024 | 123.4314 | -0.12817 | 123.3627 | 60.997 | -0.36621 | 123.4314 | -0.12817 | 60.997 | 123.024 | 123.3627 | -123.5916 | -123.5825
556.9844 | 123.4589 | -61.0886 | 62.2238 | -0.23183 | -0.010776 | -0.030711 | 0.013029 | 0.044645 | 0.0016286 | 0.080268 | -61.2534 | 62.4252 | -61.4456 | -61.2762 | 62.0544 | 0.10986 | -0.073242 | 0.23346 | 62.3291 | -61.4044 | -0.35706 | 0.20142 | -0.16479 | -0.18768 | -0.16937 | -0.31586 | 0.10529 | 0.19226 | 61.0153 | 61.322 | 123.143 | 123.5138 | -0.16479 | 123.4177 | 61.1984 | -0.31586 | 123.5138 | -0.16479 | 61.1984 | 123.143 | 123.4177 | -123.6694 | -123.6282
557.9219 | 123.4406 | -61.116 | 62.2055 | -0.018208 | 0.0084498 | -0.010416 | 0.0055522 | 0.049985 | -0.0047804 | 0.066383 | -61.2534 | 62.4252 | -61.4365 | -61.2717 | 62.0819 | 0.073242 | -0.10071 | 0.2243 | 62.3062 | -61.3953 | -0.32043 | 0.21973 | -0.13733 | -0.15564 | -0.1236 | -0.27924 | 0.10071 | 0.1831 | 61.0153 | 61.3403 | 123.1979 | 123.5413 | -0.13733 | 123.4222 | 61.1893 | -0.27924 | 123.5413 | -0.13733 | 61.1893 | 123.1979 | 123.4222 | -123.642 | -123.6008
558.9844 | 123.468 | -61.0794 | 62.2467 | -0.78115 | -0.0011632 | -0.041392 | 0.0012792 | 0.05319 | -0.014393 | 0.064246 | -61.2488 | 62.4802 | -61.441 | -61.2534 | 62.0956 | 0.10986 | -0.11444 | 0.25635 | 62.3108 | -61.3861 | -0.36163 | 0.23346 | -0.16937 | -0.17395 | -0.15106 | -0.3067 | 0.064087 | 0.19226 | 60.965 | 61.3358 | 123.175 | 123.5596 | -0.16937 | 123.3902 | 61.1893 | -0.3067 | 123.5596 | -0.16937 | 61.1893 | 123.175 | 123.3902 | -123.6877 | -123.6328
559.9219 | 123.4222 | -61.0977 | 62.2238 | 0.058086 | 0.00097275 | -0.022166 | 0.011961 | 0.051053 | -0.0090524 | 0.069587 | -61.2488 | 62.4207 | -61.4456 | -61.235 | 62.1002 | 0.082397 | -0.11902 | 0.24261 | 62.3154 | -61.3953 | -0.3479 | 0.19684 | -0.15106 | -0.13733 | -0.1236 | -0.29755 | 0.091553 | 0.19684 | 60.9787 | 61.3403 | 123.1979 | 123.5184 | -0.15106 | 123.4131 | 61.1801 | -0.29755 | 123.5184 | -0.15106 | 61.1801 | 123.1979 | 123.4131 | -123.6694 | -123.6191
561.0156 | 123.5275 | -61.0336 | 62.2284 | -1.5593 | -0.016117 | -0.041392 | -0.0051288 | 0.048917 | -0.02721 | 0.083472 | -61.2534 | 62.3611 | -61.4182 | -61.4044 | 61.9812 | 0.004578 | 0.027466 | 0.1236 | 62.3474 | -61.4182 | -0.38452 | 0.13275 | -0.21973 | -0.37079 | -0.24719 | -0.38452 | 0.11902 | 0.16479 | 61.0611 | 61.1572 | 123.0148 | 123.3948 | -0.21973 | 123.381 | 61.0382 | -0.38452 | 123.3948 | -0.21973 | 61.0382 | 123.0148 | 123.381 | -123.6465 | -123.6465
561.9219 | 123.5001 | -61.1023 | 62.265 | -0.30813 | -0.011844 | -0.04246 | 0.0023482 | 0.051053 | -0.0047804 | 0.0792 | -61.2076 | 62.4664 | -61.441 | -61.29 | 62.0636 | 0.073242 | -0.059509 | 0.21973 | 62.3199 | -61.4227 | -0.33875 | 0.20142 | -0.10529 | -0.18768 | -0.20142 | -0.32043 | 0.054931 | 0.23346 | 61.0428 | 61.322 | 123.1659 | 123.5687 | -0.10529 | 123.4222 | 61.1755 | -0.32043 | 123.5687 | -0.10529 | 61.1755 | 123.1659 | 123.4222 | -123.7061 | -123.6877
562.9219 | 123.5001 | -61.1114 | 62.2238 | -0.079243 | 0.0073818 | -0.023234 | 0.0098242 | 0.044645 | 0.0091056 | 0.065314 | -61.203 | 62.4344 | -61.4365 | -61.3037 | 62.0544 | 0.045776 | -0.054932 | 0.21057 | 62.3154 | -61.3953 | -0.32501 | 0.21057 | -0.091553 | -0.19226 | -0.16937 | -0.28381 | 0.091553 | 0.23346 | 61.0565 | 61.322 | 123.1659 | 123.5458 | -0.091553 | 123.4268 | 61.1572 | -0.28381 | 123.5458 | -0.091553 | 61.1572 | 123.1659 | 123.4268 | -123.6603 | -123.6191
563.9219 | 123.4268 | -61.1206 | 62.2192 | 0.10386 | 0.0073818 | -0.027506 | 0.020506 | 0.048917 | -0.01012 | 0.071723 | -61.2488 | 62.439 | -61.4594 | -61.2579 | 62.0865 | 0.082397 | -0.082397 | 0.24261 | 62.3016 | -61.3998 | -0.33875 | 0.21973 | -0.12817 | -0.13733 | -0.13275 | -0.27924 | 0.082398 | 0.21057 | 61.0382 | 61.3632 | 123.2071 | 123.5596 | -0.12817 | 123.4222 | 61.203 | -0.27924 | 123.5596 | -0.12817 | 61.203 | 123.2071 | 123.4222 | -123.6786 | -123.6191
564.9688 | 123.5229 | -61.0977 | 62.178 | 0.31749 | -0.020389 | -0.033915 | -0.017947 | 0.051053 | -0.024006 | 0.073859 | -61.2625 | 62.3016 | -61.4365 | -61.4136 | 62.0041 | -0.032043 | -0.004578 | 0.14191 | 62.3474 | -61.4182 | -0.33874 | 0.1236 | -0.16479 | -0.31586 | -0.17395 | -0.32043 | 0.16937 | 0.17395 | 61.0931 | 61.2396 | 123.1018 | 123.3994 | -0.16479 | 123.4451 | 61.0657 | -0.32043 | 123.3994 | -0.16479 | 61.0657 | 123.1018 | 123.4451 | -123.6145 | -123.5962
565.9219 | 123.5413 | -61.0748 | 62.178 | 0.33274 | 0.0073818 | -0.014689 | 0.0012792 | 0.0361 | 0.0026966 | 0.064246 | -61.2122 | 62.352 | -61.4502 | -61.3907 | 61.9904 | -0.054932 | 0.018311 | 0.091553 | 62.352 | -61.4685 | -0.37537 | 0.17395 | -0.13733 | -0.31586 | -0.18768 | -0.39368 | 0.17395 | 0.23804 | 61.0931 | 61.1664 | 123.0652 | 123.4268 | -0.13733 | 123.4268 | 61.0199 | -0.39368 | 123.4268 | -0.13733 | 61.0199 | 123.0652 | 123.4268 | -123.6282 | -123.6465
566.9844 | 123.5229 | -61.0748 | 62.2238 | -0.41494 | -0.0065042 | -0.051005 | 0.0023482 | 0.048917 | -0.016529 | 0.066383 | -61.2213 | 62.384 | -61.4227 | -61.3403 | 62.0178 | 0.032043 | -0.018311 | 0.19684 | 62.3383 | -61.4182 | -0.3479 | 0.16022 | -0.14648 | -0.2655 | -0.20599 | -0.34332 | 0.11444 | 0.20142 | 61.0565 | 61.2717 | 123.0927 | 123.4589 | -0.14648 | 123.4131 | 61.1069 | -0.34332 | 123.4589 | -0.14648 | 61.1069 | 123.0927 | 123.4131 | -123.6465 | -123.642
567.9219 | 123.4634 | -61.0748 | 62.2513 | -0.15554 | 0.0041778 | -0.040324 | 0.014097 | 0.044645 | -0.0069164 | 0.070655 | -61.203 | 62.4344 | -61.441 | -61.2854 | 62.0453 | 0.004578 | -0.054932 | 0.15106 | 62.3016 | -61.3953 | -0.36621 | 0.1831 | -0.12817 | -0.21057 | -0.20599 | -0.32043 | 0.050354 | 0.23804 | 61.0199 | 61.2259 | 123.1201 | 123.5092 | -0.12817 | 123.3765 | 61.0794 | -0.32043 | 123.5092 | -0.12817 | 61.0794 | 123.1201 | 123.3765 | -123.6923 | -123.6465
568.9844 | 123.5458 | -61.0703 | 62.2055 | 0.50059 | -0.021457 | -0.018961 | -0.0061968 | 0.0361 | -0.020801 | 0.077064 | -61.171 | 62.3474 | -61.409 | -61.409 | 61.9766 | -0.009155 | 0.018311 | 0.13275 | 62.3611 | -61.4044 | -0.33875 | 0.14191 | -0.10071 | -0.33875 | -0.22888 | -0.33417 | 0.15564 | 0.23804 | 61.0886 | 61.203 | 123.0469 | 123.4177 | -0.10071 | 123.4314 | 61.0611 | -0.33417 | 123.4177 | -0.10071 | 61.0611 | 123.0469 | 123.4314 | -123.6145 | -123.6099
569.9219 | 123.3994 | -61.1069 | 62.265 | -0.4302 | 0.00097275 | -0.031779 | 0.010892 | 0.051053 | -0.0090524 | 0.075996 | -61.2579 | 62.439 | -61.4273 | -61.322 | 61.94 | 0.11444 | -0.07782 | 0.22888 | 62.3108 | -61.3724 | -0.32043 | 0.17395 | -0.15106 | -0.21515 | -0.32501 | -0.2655 | 0.045776 | 0.16937 | 61.0291 | 61.3358 | 123.0469 | 123.5458 | -0.15106 | 123.4177 | 61.2213 | -0.2655 | 123.5458 | -0.15106 | 61.2213 | 123.0469 | 123.4177 | -123.6923 | -123.6374
570.9844 | 123.4863 | -61.084 | 62.2467 | -0.33864 | -0.0011632 | -0.023234 | 0.0034162 | 0.042508 | -0.013325 | 0.063178 | -61.2396 | 62.4344 | -61.4502 | -61.2625 | 62.0773 | 0.064087 | -0.09613 | 0.21973 | 62.3291 | -61.4044 | -0.36621 | 0.18768 | -0.15564 | -0.17853 | -0.16937 | -0.32043 | 0.082398 | 0.21057 | 60.9879 | 61.3037 | 123.1613 | 123.5184 | -0.15564 | 123.4131 | 61.1481 | -0.32043 | 123.5184 | -0.15564 | 61.1481 | 123.1613 | 123.4131 | -123.6969 | -123.6511
571.9219 | 123.555 | -61.0931 | 62.2055 | -0.12502 | 0.0031088 | -0.015757 | 0.013029 | 0.042508 | -0.00050737 | 0.06211 | -61.2167 | 62.4481 | -61.4502 | -61.2762 | 62.027 | 0.054932 | -0.036621 | 0.20142 | 62.352 | -61.3815 | -0.35706 | 0.24262 | -0.1236 | -0.18311 | -0.17853 | -0.28839 | 0.14648 | 0.23346 | 61.0565 | 61.2946 | 123.1201 | 123.5413 | -0.1236 | 123.4451 | 61.1481 | -0.28839 | 123.5413 | -0.1236 | 61.1481 | 123.1201 | 123.4451 | -123.6557 | -123.587
572.9219 | 123.4726 | -61.1069 | 62.2055 | -0.10976 | -9.5248e-05 | -0.027506 | 0.0023482 | 0.046781 | -0.0047804 | 0.077064 | -61.1984 | 62.439 | -61.441 | -61.2762 | 62.0499 | 0.054932 | -0.045776 | 0.19684 | 62.3108 | -61.4227 | -0.33417 | 0.23346 | -0.091552 | -0.16937 | -0.15564 | -0.31586 | 0.10529 | 0.24262 | 61.0611 | 61.3037 | 123.1567 | 123.5458 | -0.091552 | 123.4177 | 61.1618 | -0.31586 | 123.5458 | -0.091552 | 61.1618 | 123.1567 | 123.4177 | -123.6465 | -123.6282
573.9219 | 123.4085 | -61.1389 | 62.1964 | -0.41494 | 0.00097275 | -0.034983 | 0.0012792 | 0.047849 | -0.0090524 | 0.06211 | -61.2808 | 62.4252 | -61.4685 | -61.2488 | 61.9583 | 0.21057 | 0.068665 | 0.29755 | 62.3291 | -61.377 | -0.32959 | 0.22888 | -0.14191 | -0.10986 | -0.23804 | -0.23804 | 0.13275 | 0.18768 | 61.2076 | 61.4365 | 123.0972 | 123.5641 | -0.14191 | 123.468 | 61.3495 | -0.23804 | 123.5641 | -0.14191 | 61.3495 | 123.0972 | 123.468 | -123.6649 | -123.5733
574.9219 | 123.4634 | -61.1069 | 62.233 | -0.44545 | -0.0043672 | -0.055277 | 0.016233 | 0.052121 | -0.018665 | 0.069587 | -61.29 | 62.4344 | -61.4548 | -61.2488 | 62.0819 | 0.10071 | -0.091553 | 0.25635 | 62.3428 | -61.377 | -0.3479 | 0.20142 | -0.1831 | -0.14191 | -0.15106 | -0.27008 | 0.10986 | 0.1648 | 61.0153 | 61.3632 | 123.1888 | 123.5413 | -0.1831 | 123.4497 | 61.2076 | -0.27008 | 123.5413 | -0.1831 | 61.2076 | 123.1888 | 123.4497 | -123.6877 | -123.6099
575.9375 | 123.5184 | -61.084 | 62.2192 | -0.58278 | -0.0097082 | -0.033915 | -0.0040608 | 0.052121 | -0.024006 | 0.066383 | -61.203 | 62.3657 | -61.4319 | -61.3998 | 61.9904 | -0.009155 | 0.013733 | 0.13275 | 62.352 | -61.3907 | -0.3479 | 0.14649 | -0.11902 | -0.31586 | -0.22888 | -0.3067 | 0.13275 | 0.22888 | 61.0977 | 61.2167 | 123.0743 | 123.4497 | -0.11902 | 123.436 | 61.0748 | -0.3067 | 123.4497 | -0.11902 | 61.0748 | 123.0743 | 123.436 | -123.6511 | -123.6099
576.9688 | 123.5504 | -61.0565 | 62.1689 | 0.57688 | -0.0022312 | -0.034983 | 0.0012792 | 0.040372 | -0.013325 | 0.053565 | -61.2259 | 62.3611 | -61.4319 | -61.4044 | 61.9766 | -0.050354 | 0.018311 | 0.10986 | 62.3199 | -61.4594 | -0.37537 | 0.19226 | -0.16937 | -0.3479 | -0.19226 | -0.40283 | 0.15106 | 0.20599 | 61.0748 | 61.1664 | 123.0331 | 123.4177 | -0.16937 | 123.3765 | 61.0062 | -0.40283 | 123.4177 | -0.16937 | 61.0062 | 123.0331 | 123.3765 | -123.6008 | -123.6282
577.9219 | 123.4177 | -61.0931 | 62.233 | -0.33864 | -0.017185 | -0.044596 | 0.0055522 | 0.047849 | -0.018665 | 0.06211 | -61.2762 | 62.4023 | -61.441 | -61.29 | 62.0636 | 0.10071 | -0.091553 | 0.23804 | 62.3291 | -61.3678 | -0.3479 | 0.16937 | -0.18311 | -0.19684 | -0.16937 | -0.27466 | 0.096131 | 0.16479 | 61.0016 | 61.3312 | 123.1567 | 123.4955 | -0.18311 | 123.4222 | 61.1938 | -0.27466 | 123.4955 | -0.18311 | 61.1938 | 123.1567 | 123.4222 | -123.674 | -123.6008
578.9844 | 123.5046 | -61.1023 | 62.2009 | 0.088604 | -0.011844 | -0.056345 | 0.00021117 | 0.035032 | -0.028278 | 0.070655 | -61.2762 | 62.3108 | -61.441 | -61.3953 | 62.0041 | -0.004578 | -0.022888 | 0.14648 | 62.3383 | -61.3953 | -0.33875 | 0.10986 | -0.17395 | -0.29297 | -0.19684 | -0.29297 | 0.13733 | 0.16479 | 61.0794 | 61.2488 | 123.1064 | 123.4131 | -0.17395 | 123.4406 | 61.0977 | -0.29297 | 123.4131 | -0.17395 | 61.0977 | 123.1064 | 123.4406 | -123.642 | -123.5962
579.9219 | 123.4543 | -61.0977 | 62.2467 | -0.41494 | -0.0075722 | -0.037119 | 0.022642 | 0.04144 | -0.011188 | 0.059974 | -61.2488 | 62.4344 | -61.4227 | -61.2534 | 62.0819 | 0.086975 | -0.10986 | 0.25635 | 62.3291 | -61.377 | -0.32501 | 0.18768 | -0.15106 | -0.15564 | -0.16479 | -0.27924 | 0.082398 | 0.17395 | 60.9879 | 61.3541 | 123.1796 | 123.5321 | -0.15106 | 123.4268 | 61.1847 | -0.27924 | 123.5321 | -0.15106 | 61.1847 | 123.1796 | 123.4268 | -123.6694 | -123.6237
580.9844 | 123.436 | -61.1023 | 62.2055 | 0.088604 | 0.0031088 | -0.012553 | 0.015165 | 0.046781 | 0.00056063 | 0.059974 | -61.235 | 62.4344 | -61.441 | -61.2396 | 62.0819 | 0.09613 | -0.10986 | 0.2243 | 62.3108 | -61.4044 | -0.33875 | 0.22888 | -0.13275 | -0.13733 | -0.1236 | -0.30212 | 0.10529 | 0.20599 | 60.9924 | 61.3266 | 123.1842 | 123.5367 | -0.13275 | 123.4131 | 61.1984 | -0.30212 | 123.5367 | -0.13275 | 61.1984 | 123.1842 | 123.4131 | -123.6465 | -123.6099
581.9219 | 123.4131 | -61.116 | 62.2421 | -0.4302 | -0.0065042 | -0.020029 | 0.013029 | 0.044645 | -0.016529 | 0.070655 | -61.2854 | 62.4069 | -61.441 | -61.2671 | 62.0911 | 0.11902 | -0.10986 | 0.27008 | 62.3383 | -61.3632 | -0.32501 | 0.16479 | -0.16937 | -0.15106 | -0.15106 | -0.24719 | 0.096131 | 0.15564 | 61.0062 | 61.3861 | 123.2071 | 123.5229 | -0.16937 | 123.4543 | 61.235 | -0.24719 | 123.5229 | -0.16937 | 61.235 | 123.2071 | 123.4543 | -123.6832 | -123.6053
582.9844 | 123.587 | -61.0474 | 62.2101 | 0.088604 | -0.012912 | -0.028574 | -0.013674 | 0.035032 | -0.032551 | 0.066383 | -61.1893 | 62.3108 | -61.3998 | -61.4502 | 61.9537 | -0.054932 | 0.073242 | 0.09613 | 62.3795 | -61.3953 | -0.35248 | 0.10071 | -0.14191 | -0.40283 | -0.25635 | -0.3479 | 0.16937 | 0.21057 | 61.1206 | 61.1435 | 123.0011 | 123.3582 | -0.14191 | 123.4268 | 60.9924 | -0.3479 | 123.3582 | -0.14191 | 60.9924 | 123.0011 | 123.4268 | -123.6099 | -123.6053
583.9219 | 123.4863 | -61.0794 | 62.2375 | -0.46071 | -0.010776 | -0.031779 | 0.013029 | 0.043577 | -0.013325 | 0.068519 | -61.2717 | 62.4435 | -61.4456 | -61.2534 | 62.0956 | 0.09613 | -0.10529 | 0.24261 | 62.3474 | -61.3632 | -0.36621 | 0.20599 | -0.19226 | -0.17395 | -0.14191 | -0.28381 | 0.10986 | 0.17395 | 60.9741 | 61.322 | 123.175 | 123.5229 | -0.19226 | 123.4268 | 61.1755 | -0.28381 | 123.5229 | -0.19226 | 61.1755 | 123.175 | 123.4268 | -123.6832 | -123.6008
584.9844 | 123.5321 | -61.0794 | 62.2009 | -0.063984 | -0.0065042 | -0.023234 | -0.011538 | 0.0361 | -0.024006 | 0.072791 | -61.2396 | 62.3291 | -61.4456 | -61.409 | 61.9995 | -0.009155 | 0 | 0.15564 | 62.3566 | -61.3907 | -0.36621 | 0.12817 | -0.16022 | -0.32959 | -0.20142 | -0.31128 | 0.15564 | 0.20599 | 61.0794 | 61.235 | 123.0789 | 123.4085 | -0.16022 | 123.436 | 61.0703 | -0.31128 | 123.4085 | -0.16022 | 61.0703 | 123.0789 | 123.436 | -123.6465 | -123.5916
585.9219 | 123.5367 | -61.1069 | 62.2192 | 0.073345 | -0.020389 | -0.014689 | -0.016879 | 0.030759 | -0.02187 | 0.078132 | -61.3083 | 62.3062 | -61.4365 | -61.3495 | 62.0132 | -0.009155 | -0.009155 | 0.14648 | 62.3383 | -61.4044 | -0.32959 | 0.086975 | -0.20142 | -0.24261 | -0.20599 | -0.29755 | 0.11902 | 0.12817 | 61.0977 | 61.2534 | 123.1201 | 123.4131 | -0.20142 | 123.4451 | 61.0977 | -0.29755 | 123.4131 | -0.20142 | 61.0977 | 123.1201 | 123.4451 | -123.6557 | -123.6237
586.9844 | 123.5458 | -61.0611 | 62.1918 | 0.042827 | -0.015048 | -0.039256 | -0.0051288 | 0.025419 | -0.033619 | 0.059974 | -61.2671 | 62.3016 | -61.4227 | -61.3953 | 61.9629 | -0.032043 | 0.013733 | 0.12817 | 62.3474 | -61.4182 | -0.36163 | 0.10986 | -0.20599 | -0.33417 | -0.22888 | -0.35706 | 0.15564 | 0.15564 | 61.0748 | 61.1893 | 123.024 | 123.3627 | -0.20599 | 123.4085 | 61.0291 | -0.35706 | 123.3627 | -0.20599 | 61.0291 | 123.024 | 123.4085 | -123.6145 | -123.6099
587.9219 | 123.4268 | -61.0977 | 62.2421 | -0.49123 | -0.0065042 | -0.020029 | 0.021574 | 0.043577 | -0.013325 | 0.057838 | -61.2762 | 62.4252 | -61.4594 | -61.2534 | 62.0911 | 0.11444 | -0.11902 | 0.25635 | 62.3245 | -61.3815 | -0.36163 | 0.18311 | -0.17853 | -0.15564 | -0.15106 | -0.28381 | 0.082398 | 0.18311 | 60.9787 | 61.3541 | 123.1888 | 123.5229 | -0.17853 | 123.4222 | 61.2122 | -0.28381 | 123.5229 | -0.17853 | 61.2122 | 123.1888 | 123.4222 | -123.7015 | -123.6237
588.9844 | 123.5138 | -61.0519 | 62.2147 | -0.048725 | -0.02573 | -0.039256 | 0.00021117 | 0.030759 | -0.026142 | 0.055701 | -61.2946 | 62.3337 | -61.4502 | -61.3998 | 61.972 | -0.032043 | -0.027466 | 0.13733 | 62.3383 | -61.3953 | -0.39825 | 0.11902 | -0.24262 | -0.3479 | -0.24262 | -0.34332 | 0.1236 | 0.15564 | 61.0245 | 61.1893 | 123.024 | 123.3856 | -0.24262 | 123.3902 | 61.0199 | -0.34332 | 123.3856 | -0.24262 | 61.0199 | 123.024 | 123.3902 | -123.6649 | -123.6099
589.9219 | 123.4543 | -61.0565 | 62.1826 | -0.4302 | -0.017185 | -0.045664 | -0.013674 | 0.039304 | -0.028278 | 0.071723 | -61.1755 | 62.352 | -61.4182 | -61.4136 | 61.972 | -0.036621 | 0.041199 | 0.036621 | 62.3978 | -61.4044 | -0.36163 | 0.16937 | -0.11902 | -0.35705 | -0.21057 | -0.3479 | 0.21515 | 0.24262 | 61.0977 | 61.0931 | 123.0286 | 123.4085 | -0.11902 | 123.4543 | 61.0199 | -0.3479 | 123.4085 | -0.11902 | 61.0199 | 123.0286 | 123.4543 | -123.6008 | -123.587
590.9219 | 123.555 | -61.0931 | 62.1735 | 0.47007 | -0.0054352 | -0.046732 | 0.0044842 | 0.037168 | -0.0090524 | 0.059974 | -61.1938 | 62.3749 | -61.409 | -61.3953 | 61.9675 | -0.082397 | 0.036621 | 0.07782 | 62.3154 | -61.4136 | -0.31586 | 0.20142 | -0.10071 | -0.30212 | -0.20599 | -0.32043 | 0.14191 | 0.21515 | 61.1298 | 61.171 | 123.0606 | 123.468 | -0.10071 | 123.4085 | 61.0107 | -0.32043 | 123.468 | -0.10071 | 61.0107 | 123.0606 | 123.4085 | -123.5825 | -123.587
591.9844 | 123.468 | -61.084 | 62.2375 | -0.36916 | -0.0054352 | -0.011485 | 0.017301 | 0.032895 | -0.01012 | 0.066383 | -61.2442 | 62.3611 | -61.4319 | -61.2671 | 62.0819 | 0.059509 | -0.10529 | 0.26093 | 62.3474 | -61.3586 | -0.3479 | 0.1236 | -0.16022 | -0.18311 | -0.15564 | -0.27466 | 0.10986 | 0.18768 | 60.9787 | 61.3449 | 123.1659 | 123.4451 | -0.16022 | 123.4314 | 61.1435 | -0.27466 | 123.4451 | -0.16022 | 61.1435 | 123.1659 | 123.4314 | -123.6694 | -123.5962
592.9219 | 123.436 | -61.0611 | 62.2787 | -0.3539 | 0.0073818 | -0.048869 | 0.020506 | 0.045713 | -0.0079844 | 0.059974 | -61.3632 | 62.4481 | -61.4182 | -61.2122 | 62.0361 | 0.13275 | -0.091553 | 0.24261 | 62.3108 | -61.3907 | -0.35706 | 0.16937 | -0.30212 | -0.15106 | -0.24262 | -0.32959 | 0.032043 | 0.054932 | 60.9695 | 61.3037 | 123.0972 | 123.5092 | -0.30212 | 123.3719 | 61.1938 | -0.32959 | 123.5092 | -0.30212 | 61.1938 | 123.0972 | 123.3719 | -123.6969 | -123.6694
593.9844 | 123.5229 | -61.0657 | 62.2101 | -0.033467 | -0.023593 | -0.012553 | -0.0051288 | 0.031827 | -0.026142 | 0.070655 | -61.2488 | 62.3337 | -61.4319 | -61.3861 | 61.9858 | -0.018311 | 0.009155 | 0.11444 | 62.3154 | -61.4182 | -0.36621 | 0.1236 | -0.1831 | -0.32043 | -0.2243 | -0.35248 | 0.10529 | 0.18311 | 61.0748 | 61.1801 | 123.0515 | 123.3994 | -0.1831 | 123.381 | 61.0474 | -0.35248 | 123.3994 | -0.1831 | 61.0474 | 123.0515 | 123.381 | -123.642 | -123.6282
594.9219 | 123.4314 | -61.0886 | 62.2421 | -0.41494 | -0.010776 | -0.026438 | 0.016233 | 0.035032 | -0.012257 | 0.073859 | -61.2808 | 62.439 | -61.4594 | -61.2305 | 62.1002 | 0.13275 | -0.1236 | 0.24719 | 62.3337 | -61.3815 | -0.37079 | 0.19684 | -0.19226 | -0.14191 | -0.14191 | -0.29297 | 0.091553 | 0.17853 | 60.965 | 61.3358 | 123.1888 | 123.5275 | -0.19226 | 123.4222 | 61.2213 | -0.29297 | 123.5275 | -0.19226 | 61.2213 | 123.1888 | 123.4222 | -123.7015 | -123.6237
595.9844 | 123.3902 | -61.1023 | 62.2284 | 0.24119 | 0.0073818 | -0.032847 | 0.0098242 | 0.040372 | -0.011188 | 0.072791 | -61.3037 | 62.3978 | -61.4594 | -61.203 | 62.114 | 0.086975 | -0.14648 | 0.2655 | 62.2971 | -61.3815 | -0.35706 | 0.16937 | -0.20142 | -0.10071 | -0.11444 | -0.27924 | 0.068664 | 0.15564 | 60.9558 | 61.3678 | 123.2162 | 123.5001 | -0.20142 | 123.3994 | 61.1893 | -0.27924 | 123.5001 | -0.20142 | 61.1893 | 123.2162 | 123.3994 | -123.6877 | -123.6099
596.9219 | 123.4406 | -61.0977 | 62.2467 | -0.41494 | -0.012912 | -0.017893 | 0.00021117 | 0.043577 | -0.026142 | 0.071723 | -61.2579 | 62.3978 | -61.4273 | -61.2717 | 62.0819 | 0.091553 | -0.09613 | 0.23346 | 62.3199 | -61.3586 | -0.32959 | 0.15106 | -0.16022 | -0.17395 | -0.16479 | -0.26093 | 0.073242 | 0.16937 | 61.0016 | 61.3312 | 123.1796 | 123.4955 | -0.16022 | 123.4177 | 61.1893 | -0.26093 | 123.4955 | -0.16022 | 61.1893 | 123.1796 | 123.4177 | -123.674 | -123.6053
597.9844 | 123.5687 | -61.0519 | 62.2009 | -0.079243 | -0.011844 | -0.0478 | -0.012606 | 0.0361 | -0.026142 | 0.072791 | -61.2305 | 62.352 | -61.4319 | -61.4365 | 61.9354 | -0.045776 | 0.073242 | 0.091553 | 62.3383 | -61.4273 | -0.37994 | 0.15106 | -0.17853 | -0.38452 | -0.2655 | -0.37537 | 0.13733 | 0.20142 | 61.1252 | 61.1435 | 122.9874 | 123.4039 | -0.17853 | 123.3902 | 61.0062 | -0.37537 | 123.4039 | -0.17853 | 61.0062 | 122.9874 | 123.3902 | -123.6328 | -123.6282
598.9219 | 123.5504 | -61.0657 | 62.2192 | -0.41494 | -0.017185 | -0.028574 | 0.019437 | 0.035032 | -0.022938 | 0.075996 | -61.3632 | 62.3474 | -61.3907 | -61.3495 | 61.9034 | 0 | 0.086975 | 0.059509 | 62.3428 | -61.4273 | -0.32501 | 0.12817 | -0.29755 | -0.28381 | -0.31586 | -0.36163 | 0.1236 | 0.027466 | 61.1526 | 61.1252 | 122.9691 | 123.4131 | -0.29755 | 123.4085 | 61.0657 | -0.36163 | 123.4131 | -0.29755 | 61.0657 | 122.9691 | 123.4085 | -123.6099 | -123.6465
599.9844 | 123.5687 | -61.0428 | 62.1826 | 0.45481 | 0.00097275 | -0.029642 | -0.00085683 | 0.031827 | -0.0090524 | 0.06211 | -61.203 | 62.3245 | -61.4365 | -61.4044 | 61.9675 | -0.082397 | 0.032043 | 0.082397 | 62.3245 | -61.4227 | -0.39368 | 0.14191 | -0.16022 | -0.36163 | -0.21515 | -0.37994 | 0.14191 | 0.23346 | 61.0748 | 61.1252 | 123.0103 | 123.3673 | -0.16022 | 123.3673 | 60.9604 | -0.37994 | 123.3673 | -0.16022 | 60.9604 | 123.0103 | 123.3673 | -123.6191 | -123.6053
600.9219 | 123.4314 | -61.1252 | 62.1826 | 0.39378 | -0.0043672 | -0.012553 | 0.017301 | 0.044645 | -0.0079844 | 0.067451 | -61.2717 | 62.384 | -61.4639 | -61.1893 | 62.0499 | 0.050354 | -0.07782 | 0.2655 | 62.2971 | -61.3815 | -0.33875 | 0.20142 | -0.14648 | -0.064087 | -0.13275 | -0.25635 | 0.11444 | 0.19226 | 61.0474 | 61.3907 | 123.175 | 123.5092 | -0.14648 | 123.4222 | 61.1755 | -0.25635 | 123.5092 | -0.14648 | 61.1755 | 123.175 | 123.4222 | -123.6465 | -123.5641
601.9844 | 123.4909 | -61.1023 | 62.2055 | 0.30223 | -0.0075722 | -0.030711 | 0.013029 | 0.035032 | -0.013325 | 0.066383 | -61.2854 | 62.3932 | -61.4548 | -61.2808 | 62.0728 | 0.032043 | -0.073242 | 0.19226 | 62.2696 | -61.3998 | -0.35248 | 0.18768 | -0.18311 | -0.17853 | -0.13275 | -0.29755 | 0.064087 | 0.16937 | 61.0291 | 61.2946 | 123.175 | 123.4955 | -0.18311 | 123.3719 | 61.1343 | -0.29755 | 123.4955 | -0.18311 | 61.1343 | 123.175 | 123.3719 | -123.6603 | -123.6053
602.9219 | 123.436 | -61.0291 | 62.1964 | -0.3539 | -0.01398 | -0.048869 | 0.00021117 | 0.040372 | -0.036823 | 0.054633 | -61.203 | 62.3383 | -61.4044 | -61.4182 | 61.9766 | -0.027466 | 0.041199 | 0.064087 | 62.3749 | -61.3861 | -0.37537 | 0.14191 | -0.17395 | -0.3891 | -0.21973 | -0.35706 | 0.17853 | 0.20142 | 61.0703 | 61.0931 | 123.0057 | 123.3673 | -0.17395 | 123.4039 | 61.0016 | -0.35706 | 123.3673 | -0.17395 | 61.0016 | 123.0057 | 123.4039 | -123.6008 | -123.5825
603.9219 | 123.555 | -61.0565 | 62.2147 | -0.20131 | -0.01398 | -0.046732 | -0.0072648 | 0.037168 | -0.029346 | 0.072791 | -61.1984 | 62.3474 | -61.4319 | -61.4227 | 61.972 | -0.036621 | 0.050354 | 0.091553 | 62.3383 | -61.409 | -0.37537 | 0.13275 | -0.14191 | -0.36621 | -0.24262 | -0.35248 | 0.1236 | 0.23346 | 61.1069 | 61.1481 | 123.0286 | 123.4039 | -0.14191 | 123.3948 | 61.0199 | -0.35248 | 123.4039 | -0.14191 | 61.0199 | 123.0286 | 123.3948 | -123.6465 | -123.6237
604.9844 | 123.5367 | -61.0748 | 62.1964 | 0.62266 | 0.00097275 | -0.02537 | 0.0066202 | 0.037168 | -0.018665 | 0.071723 | -61.2991 | 62.3291 | -61.441 | -61.3541 | 62.0041 | -0.018311 | -0.018311 | 0.15564 | 62.3154 | -61.409 | -0.36621 | 0.13275 | -0.2243 | -0.27924 | -0.19226 | -0.33417 | 0.11902 | 0.14191 | 61.0565 | 61.2305 | 123.0789 | 123.4039 | -0.2243 | 123.3902 | 61.0565 | -0.33417 | 123.4039 | -0.2243 | 61.0565 | 123.0789 | 123.3902 | -123.6374 | -123.6053
605.9219 | 123.4772 | -61.0886 | 62.2559 | -0.30813 | -0.0022312 | -0.056345 | 0.031187 | 0.047849 | -0.0047804 | 0.068519 | -61.2396 | 62.4344 | -61.441 | -61.2396 | 62.0682 | 0.086975 | -0.086975 | 0.22888 | 62.3154 | -61.3724 | -0.35248 | 0.17853 | -0.15106 | -0.15106 | -0.18768 | -0.28381 | 0.05951 | 0.20142 | 61.0016 | 61.3174 | 123.1567 | 123.5229 | -0.15106 | 123.4039 | 61.1755 | -0.28381 | 123.5229 | -0.15106 | 61.1755 | 123.1567 | 123.4039 | -123.6969 | -123.6282
606.9844 | 123.4863 | -61.1206 | 62.1918 | 0.47007 | -0.0065042 | -0.032847 | 0.016233 | 0.039304 | -0.0079844 | 0.063178 | -61.2625 | 62.3886 | -61.4685 | -61.3083 | 62.0407 | 0.013733 | -0.050354 | 0.16937 | 62.2971 | -61.4044 | -0.3479 | 0.19684 | -0.14191 | -0.18768 | -0.15106 | -0.28381 | 0.10529 | 0.20599 | 61.0703 | 61.29 | 123.1613 | 123.5092 | -0.14191 | 123.4177 | 61.1343 | -0.28381 | 123.5092 | -0.14191 | 61.1343 | 123.1613 | 123.4177 | -123.6603 | -123.5962
607.9219 | 123.5001 | -61.0931 | 62.2192 | -0.32338 | -0.010776 | -0.046732 | 0.0023482 | 0.040372 | -0.019733 | 0.06211 | -61.2122 | 62.3703 | -61.4273 | -61.3266 | 62.0132 | 0.050354 | -0.032043 | 0.16937 | 62.3474 | -61.3678 | -0.33417 | 0.15106 | -0.11902 | -0.23346 | -0.20599 | -0.27466 | 0.12817 | 0.21515 | 61.0611 | 61.2625 | 123.1064 | 123.4634 | -0.11902 | 123.4406 | 61.1435 | -0.27466 | 123.4634 | -0.11902 | 61.1435 | 123.1064 | 123.4406 | -123.6465 | -123.587
608.9219 | 123.6923 | -61.0382 | 62.265 | -0.3539 | -0.020389 | -0.044596 | 0.0034162 | 0.04144 | -0.022938 | 0.071723 | -61.1938 | 62.352 | -61.4182 | -61.4136 | 61.9629 | -0.013733 | 0.054932 | 0.07782 | 62.3703 | -61.3953 | -0.37994 | 0.086975 | -0.15564 | -0.37537 | -0.30212 | -0.35706 | 0.10529 | 0.2243 | 61.0931 | 61.116 | 123.0011 | 123.3902 | -0.15564 | 123.4085 | 61.0245 | -0.35706 | 123.3902 | -0.15564 | 61.0245 | 123.0011 | 123.4085 | -123.6832 | -123.6603
609.9844 | 123.5275 | -61.084 | 62.2055 | 0.058086 | -0.01398 | -0.039256 | 0.0034162 | 0.038236 | -0.022938 | 0.070655 | -61.2717 | 62.3108 | -61.4502 | -61.3907 | 62.0178 | -0.022888 | 0.013733 | 0.13733 | 62.3245 | -61.4044 | -0.36621 | 0.10529 | -0.18768 | -0.3067 | -0.18768 | -0.32043 | 0.11902 | 0.17853 | 61.0977 | 61.2213 | 123.1018 | 123.3948 | -0.18768 | 123.4085 | 61.0611 | -0.32043 | 123.3948 | -0.18768 | 61.0611 | 123.1018 | 123.4085 | -123.6557 | -123.6099
610.9219 | 123.4543 | -61.0931 | 62.2513 | -2.5817 | -0.0075722 | -0.037119 | 0.026914 | 0.042508 | -0.01012 | 0.061042 | -61.3358 | 62.4207 | -61.4685 | -61.1938 | 62.0956 | 0.11444 | -0.11444 | 0.23346 | 62.3199 | -61.3861 | -0.37537 | 0.16937 | -0.24261 | -0.10071 | -0.15564 | -0.29297 | 0.068664 | 0.13275 | 60.9787 | 61.3266 | 123.1888 | 123.5138 | -0.24261 | 123.4131 | 61.2076 | -0.29297 | 123.5138 | -0.24261 | 61.2076 | 123.1888 | 123.4131 | -123.7198 | -123.6374
611.9844 | 123.5321 | -61.0794 | 62.1918 | 0.53111 | 0.0020408 | -0.0061444 | 0.016233 | 0.047849 | -0.011188 | 0.053565 | -61.2534 | 62.3749 | -61.441 | -61.3449 | 62.0087 | -0.022888 | -0.013733 | 0.10986 | 62.3199 | -61.4182 | -0.36163 | 0.18311 | -0.17395 | -0.2655 | -0.1831 | -0.33874 | 0.12817 | 0.18768 | 61.0657 | 61.1893 | 123.0881 | 123.4543 | -0.17395 | 123.3994 | 61.0565 | -0.33874 | 123.4543 | -0.17395 | 61.0565 | 123.0881 | 123.3994 | -123.6328 | -123.6099
612.9219 | 123.5504 | -61.0474 | 62.2101 | -0.3539 | -0.012912 | -0.040324 | -0.0061968 | 0.043577 | -0.032551 | 0.066383 | -61.1664 | 62.3566 | -61.4227 | -61.4273 | 61.9583 | -0.036621 | 0.045776 | 0.09613 | 62.3566 | -61.4182 | -0.37537 | 0.14648 | -0.11902 | -0.37994 | -0.25177 | -0.37079 | 0.14648 | 0.25635 | 61.0931 | 61.1435 | 123.0057 | 123.4039 | -0.11902 | 123.4039 | 61.0107 | -0.37079 | 123.4039 | -0.11902 | 61.0107 | 123.0057 | 123.4039 | -123.6328 | -123.6282
613.9844 | 123.4634 | -61.1298 | 62.2009 | 0.36326 | 0.0031088 | -0.034983 | 0.019437 | 0.044645 | -0.011188 | 0.075996 | -61.2717 | 62.3795 | -61.4639 | -61.2808 | 62.0682 | 0.027466 | -0.073242 | 0.17853 | 62.2879 | -61.3998 | -0.33417 | 0.17853 | -0.14191 | -0.15106 | -0.13275 | -0.27008 | 0.086975 | 0.19226 | 61.0565 | 61.3083 | 123.1979 | 123.5092 | -0.14191 | 123.4177 | 61.1572 | -0.27008 | 123.5092 | -0.14191 | 61.1572 | 123.1979 | 123.4177 | -123.6649 | -123.6008
614.9219 | 123.4863 | -61.0657 | 62.2009 | 0.073345 | -0.0097082 | -0.02537 | -0.0019248 | 0.037168 | -0.029346 | 0.059974 | -61.2671 | 62.3245 | -61.4639 | -61.377 | 61.9995 | -0.013733 | -0.032043 | 0.14648 | 62.3062 | -61.3907 | -0.39825 | 0.1236 | -0.20142 | -0.31128 | -0.20142 | -0.32501 | 0.10529 | 0.19684 | 61.0336 | 61.2122 | 123.0652 | 123.3902 | -0.20142 | 123.3719 | 61.0519 | -0.32501 | 123.3902 | -0.20142 | 61.0519 | 123.0652 | 123.3719 | -123.6649 | -123.5916
615.9844 | 123.4863 | -61.084 | 62.2101 | 0.24119 | -0.016117 | -0.023234 | -0.00085683 | 0.0361 | -0.025074 | 0.075996 | -61.2762 | 62.3245 | -61.4319 | -61.3632 | 62.0178 | 0.004578 | -0.022888 | 0.13275 | 62.3383 | -61.409 | -0.3479 | 0.11444 | -0.19226 | -0.27924 | -0.19226 | -0.32501 | 0.12817 | 0.15564 | 61.0611 | 61.2167 | 123.1018 | 123.4085 | -0.19226 | 123.4222 | 61.0886 | -0.32501 | 123.4085 | -0.19226 | 61.0886 | 123.1018 | 123.4222 | -123.642 | -123.6191
616.9219 | 123.5367 | -61.0703 | 62.1918 | -0.033467 | -0.02573 | -0.028574 | -0.0029928 | 0.030759 | -0.024006 | 0.070655 | -61.2259 | 62.3383 | -61.4365 | -61.3907 | 61.9858 | -0.022888 | 0.032043 | 0.11902 | 62.3383 | -61.3953 | -0.36621 | 0.14648 | -0.15564 | -0.32044 | -0.20599 | -0.32501 | 0.14648 | 0.21057 | 61.1023 | 61.1893 | 123.056 | 123.4085 | -0.15564 | 123.4085 | 61.0474 | -0.32501 | 123.4085 | -0.15564 | 61.0474 | 123.056 | 123.4085 | -123.6282 | -123.587
617.9844 | 123.5596 | -61.0886 | 62.1872 | 0.54637 | -0.0011632 | -0.041392 | 0.0087562 | 0.029691 | -0.0047804 | 0.06211 | -61.1801 | 62.3566 | -61.4182 | -61.3953 | 61.9492 | -0.068665 | 0.16022 | 0.050354 | 62.2742 | -61.4594 | -0.32959 | 0.16937 | -0.091553 | -0.3067 | -0.23804 | -0.37079 | 0.086975 | 0.23804 | 61.2488 | 61.1389 | 123.0377 | 123.4451 | -0.091553 | 123.3627 | 61.0199 | -0.37079 | 123.4451 | -0.091553 | 61.0199 | 123.0377 | 123.3627 | -123.6053 | -123.6465
618.9219 | 123.5229 | -61.0703 | 62.1872 | 0.21067 | -0.0065042 | -0.039256 | 0.0087562 | 0.026487 | -0.024006 | 0.071723 | -61.2717 | 62.3154 | -61.4319 | -61.3541 | 62.0087 | 0 | -0.022888 | 0.1236 | 62.3291 | -61.409 | -0.36163 | 0.12817 | -0.20142 | -0.28381 | -0.17853 | -0.33875 | 0.14191 | 0.16022 | 61.0474 | 61.1938 | 123.0789 | 123.3856 | -0.20142 | 123.3994 | 61.0703 | -0.33875 | 123.3856 | -0.20142 | 61.0703 | 123.0789 | 123.3994 | -123.6191 | -123.5962
619.9844 | 123.4818 | -61.1023 | 62.2055 | 0.042827 | 0.010586 | -0.0093484 | 0.018369 | 0.042508 | -0.0037124 | 0.073859 | -61.1801 | 62.4298 | -61.441 | -61.2534 | 62.0544 | -0.022888 | -0.091553 | 0.14191 | 62.3016 | -61.3953 | -0.33875 | 0.22431 | -0.07782 | -0.15106 | -0.15106 | -0.29297 | 0.096131 | 0.26093 | 61.0107 | 61.2442 | 123.1567 | 123.5321 | -0.07782 | 123.4039 | 61.0794 | -0.29297 | 123.5321 | -0.07782 | 61.0794 | 123.1567 | 123.4039 | -123.6465 | -123.6008
620.9219 | 123.4772 | -61.0748 | 62.2238 | -0.44545 | -0.016117 | -0.031779 | 0.0055522 | 0.04144 | -0.020801 | 0.066383 | -61.2167 | 62.3611 | -61.4319 | -61.322 | 62.0499 | 0.059509 | -0.054932 | 0.1831 | 62.3566 | -61.3724 | -0.35706 | 0.13733 | -0.14191 | -0.24719 | -0.17395 | -0.29755 | 0.13275 | 0.21515 | 61.0199 | 61.2579 | 123.1247 | 123.436 | -0.14191 | 123.4314 | 61.1343 | -0.29755 | 123.436 | -0.14191 | 61.1343 | 123.1247 | 123.4314 | -123.6557 | -123.5962
621.9844 | 123.4634 | -61.0657 | 62.2192 | -0.1708 | 0.00097275 | -0.033915 | 0.026914 | 0.045713 | -0.0058484 | 0.073859 | -61.1938 | 62.439 | -61.4227 | -61.2488 | 62.0773 | 0.059509 | -0.073242 | 0.19684 | 62.3108 | -61.3998 | -0.35705 | 0.21973 | -0.12817 | -0.1831 | -0.14191 | -0.33417 | 0.091553 | 0.22888 | 60.9924 | 61.2625 | 123.143 | 123.5046 | -0.12817 | 123.3765 | 61.1252 | -0.33417 | 123.5046 | -0.12817 | 61.1252 | 123.143 | 123.3765 | -123.642 | -123.6191
622.9219 | 123.5046 | -61.0565 | 62.2147 | 0.13438 | -0.01398 | -0.027506 | -0.0019248 | 0.040372 | -0.029346 | 0.065314 | -61.2717 | 62.3474 | -61.4548 | -61.3632 | 62.027 | 0 | -0.022888 | 0.14191 | 62.3291 | -61.4182 | -0.39825 | 0.13275 | -0.21515 | -0.3067 | -0.18768 | -0.36163 | 0.11444 | 0.18311 | 61.0336 | 61.1984 | 123.0835 | 123.4039 | -0.21515 | 123.3856 | 61.0565 | -0.36163 | 123.4039 | -0.21515 | 61.0565 | 123.0835 | 123.3856 | -123.6694 | -123.6328
623.9844 | 123.5184 | -61.084 | 62.1735 | 1.0804 | -0.017185 | -0.041392 | -0.0083338 | 0.038236 | -0.015461 | 0.072791 | -61.1984 | 62.3337 | -61.4594 | -61.3998 | 61.9904 | -0.041199 | 0.032043 | 0.10986 | 62.3337 | -61.4136 | -0.37537 | 0.16022 | -0.11444 | -0.31586 | -0.18311 | -0.32959 | 0.16022 | 0.26093 | 61.116 | 61.1938 | 123.0743 | 123.4177 | -0.11444 | 123.4177 | 61.0428 | -0.32959 | 123.4177 | -0.11444 | 61.0428 | 123.0743 | 123.4177 | -123.6328 | -123.587
624.9219 | 123.5779 | -61.0565 | 62.1689 | 0.48533 | -0.012912 | -0.029642 | 0.00021117 | 0.030759 | -0.01012 | 0.082404 | -61.2167 | 62.3245 | -61.4319 | -61.3266 | 61.7798 | -0.17853 | 0.073242 | 0.21515 | 62.3383 | -61.3998 | -0.37537 | 0.15564 | -0.16022 | -0.27008 | -0.3891 | -0.34332 | 0.16937 | 0.21515 | 61.1298 | 61.2717 | 122.8363 | 123.381 | -0.16022 | 123.3948 | 60.878 | -0.34332 | 123.381 | -0.16022 | 60.878 | 122.8363 | 123.3948 | -123.6008 | -123.5687
625.9844 | 123.5641 | -61.0153 | 62.2055 | -0.29287 | -0.0065042 | -0.061686 | -0.0072648 | 0.031827 | -0.033619 | 0.064246 | -61.1893 | 62.3154 | -61.4365 | -61.3953 | 61.9675 | -0.022888 | 0.059509 | 0.086975 | 62.3611 | -61.4044 | -0.42114 | 0.10986 | -0.17395 | -0.37994 | -0.23804 | -0.3891 | 0.15564 | 0.24719 | 61.0748 | 61.1023 | 122.9828 | 123.3307 | -0.17395 | 123.3765 | 60.9924 | -0.3891 | 123.3307 | -0.17395 | 60.9924 | 122.9828 | 123.3765 | -123.642 | -123.6099
626.9219 | 123.468 | -61.0748 | 62.1964 | 0.22593 | -0.0086402 | -0.045664 | 0.0034162 | 0.028623 | -0.02721 | 0.082404 | -61.2808 | 62.3245 | -61.4594 | -61.3724 | 62.0041 | 0 | -0.036621 | 0.15106 | 62.3337 | -61.3907 | -0.38452 | 0.12817 | -0.20599 | -0.29755 | -0.19226 | -0.31586 | 0.13733 | 0.17853 | 61.0382 | 61.2259 | 123.0789 | 123.3994 | -0.20599 | 123.4085 | 61.0748 | -0.31586 | 123.3994 | -0.20599 | 61.0748 | 123.0789 | 123.4085 | -123.6557 | -123.587
627.9844 | 123.4451 | -61.116 | 62.2238 | 0.33274 | -0.0022312 | -0.024302 | 0.026914 | 0.025419 | 0.0016286 | 0.064246 | -61.2946 | 62.4298 | -61.4182 | -61.2076 | 62.0956 | 0.07782 | -0.13275 | 0.22888 | 62.2787 | -61.3907 | -0.30212 | 0.20599 | -0.17853 | -0.091553 | -0.12817 | -0.27466 | 0.054932 | 0.1236 | 60.9833 | 61.3449 | 123.2117 | 123.5458 | -0.17853 | 123.3948 | 61.1938 | -0.27466 | 123.5458 | -0.17853 | 61.1938 | 123.2117 | 123.3948 | -123.642 | -123.6145
628.9219 | 123.5825 | -61.0428 | 62.2009 | -0.12502 | -0.015048 | -0.04246 | -0.0019248 | 0.032895 | -0.02721 | 0.059974 | -61.2305 | 62.3428 | -61.441 | -61.4182 | 61.9766 | -0.032043 | 0.032043 | 0.10071 | 62.3657 | -61.3953 | -0.39825 | 0.14191 | -0.18768 | -0.37537 | -0.2243 | -0.35248 | 0.1648 | 0.21057 | 61.0748 | 61.1435 | 123.0194 | 123.3856 | -0.18768 | 123.4085 | 61.0107 | -0.35248 | 123.3856 | -0.18768 | 61.0107 | 123.0194 | 123.4085 | -123.642 | -123.5962
629.9219 | 123.5321 | -61.0611 | 62.2101 | 1.996 | -0.015048 | -0.048869 | -0.0029928 | 0.038236 | -0.025074 | 0.067451 | -61.2076 | 62.3474 | -61.4319 | -61.3907 | 61.9995 | -0.022888 | -0.032043 | 0.1236 | 62.3428 | -61.3907 | -0.37079 | 0.13733 | -0.14648 | -0.32959 | -0.21057 | -0.32959 | 0.13275 | 0.2243 | 61.0291 | 61.1847 | 123.0606 | 123.4085 | -0.14648 | 123.4039 | 61.0382 | -0.32959 | 123.4085 | -0.14648 | 61.0382 | 123.0606 | 123.4039 | -123.642 | -123.6008
630.9844 | 123.5367 | -61.0474 | 62.233 | -0.12502 | -0.010776 | -0.043528 | 0.0044842 | 0.032895 | -0.018665 | 0.064246 | -61.1755 | 62.352 | -61.4319 | -61.377 | 61.9858 | 0.013733 | 0.004578 | 0.12817 | 62.3337 | -61.3861 | -0.38452 | 0.11902 | -0.12817 | -0.32959 | -0.24719 | -0.33875 | 0.10071 | 0.25635 | 61.0519 | 61.1755 | 123.0331 | 123.3994 | -0.12817 | 123.381 | 61.0611 | -0.33875 | 123.3994 | -0.12817 | 61.0611 | 123.0331 | 123.381 | -123.6649 | -123.6191
631.9219 | 123.5275 | -61.0748 | 62.2147 | 0.30223 | -0.022525 | -0.054209 | 0.0034162 | 0.038236 | -0.019733 | 0.059974 | -61.2625 | 62.3245 | -61.4182 | -61.3541 | 62.0041 | -0.022888 | -0.009155 | 0.13733 | 62.3245 | -61.4182 | -0.34332 | 0.10986 | -0.18768 | -0.27924 | -0.21057 | -0.34332 | 0.10986 | 0.15564 | 61.0657 | 61.2122 | 123.0789 | 123.3994 | -0.18768 | 123.3994 | 61.0519 | -0.34332 | 123.3994 | -0.18768 | 61.0519 | 123.0789 | 123.3994 | -123.6328 | -123.6328
632.9844 | 123.4177 | -61.1252 | 62.2101 | 0.36326 | -9.5248e-05 | -0.022166 | 0.032255 | 0.035032 | -0.0037124 | 0.065314 | -61.2946 | 62.4344 | -61.4365 | -61.2259 | 62.1002 | 0.07782 | -0.12817 | 0.22888 | 62.2742 | -61.3907 | -0.31128 | 0.2243 | -0.16937 | -0.10071 | -0.10986 | -0.2655 | 0.064087 | 0.14191 | 60.997 | 61.3541 | 123.2254 | 123.5596 | -0.16937 | 123.3994 | 61.203 | -0.2655 | 123.5596 | -0.16937 | 61.203 | 123.2254 | 123.3994 | -123.6465 | -123.6008
633.9219 | 123.5321 | -61.0794 | 62.2055 | 0.19541 | -0.017185 | -0.052073 | 0.0066202 | 0.032895 | -0.020801 | 0.054633 | -61.2762 | 62.3474 | -61.4594 | -61.3907 | 62.0087 | -0.022888 | -0.013733 | 0.1236 | 62.3383 | -61.3907 | -0.37994 | 0.14191 | -0.19684 | -0.31128 | -0.19684 | -0.31128 | 0.13275 | 0.18311 | 61.0657 | 61.203 | 123.0881 | 123.4268 | -0.19684 | 123.4177 | 61.0565 | -0.31128 | 123.4268 | -0.19684 | 61.0565 | 123.0881 | 123.4177 | -123.6649 | -123.5962
634.9844 | 123.4863 | -61.1206 | 62.2238 | -0.063984 | 0.00097275 | -0.021098 | 0.026914 | 0.044645 | -0.0015754 | 0.080268 | -61.203 | 62.4527 | -61.4319 | -61.2579 | 62.0224 | 0.041199 | -0.091553 | 0.15564 | 62.2925 | -61.4044 | -0.31128 | 0.22888 | -0.082398 | -0.13733 | -0.20142 | -0.28381 | 0.068664 | 0.22888 | 61.0291 | 61.2762 | 123.143 | 123.5733 | -0.082398 | 123.4131 | 61.1618 | -0.28381 | 123.5733 | -0.082398 | 61.1618 | 123.143 | 123.4131 | -123.6557 | -123.6282
635.9219 | 123.4589 | -61.084 | 62.2559 | -0.15554 | -0.0097082 | -0.0072124 | 0.016233 | 0.042508 | -0.025074 | 0.063178 | -61.2534 | 62.471 | -61.4594 | -61.235 | 62.0956 | 0.10071 | -0.091553 | 0.24261 | 62.3199 | -61.3586 | -0.37537 | 0.21515 | -0.16937 | -0.15106 | -0.16022 | -0.27466 | 0.064087 | 0.20599 | 60.9924 | 61.3266 | 123.1796 | 123.555 | -0.16937 | 123.4039 | 61.1847 | -0.27466 | 123.555 | -0.16937 | 61.1847 | 123.1796 | 123.4039 | -123.7152 | -123.6145
636.9844 | 123.3902 | -61.116 | 62.2147 | 0.18016 | 0.0020408 | -0.014689 | 0.025846 | 0.047849 | -0.0037124 | 0.069587 | -61.2625 | 62.4435 | -61.4777 | -61.2122 | 62.1506 | 0.091553 | -0.15106 | 0.21973 | 62.2879 | -61.3815 | -0.36163 | 0.22888 | -0.14648 | -0.09613 | -0.064087 | -0.2655 | 0.073242 | 0.21515 | 60.965 | 61.3358 | 123.2666 | 123.5596 | -0.14648 | 123.4039 | 61.2076 | -0.2655 | 123.5596 | -0.14648 | 61.2076 | 123.2666 | 123.4039 | -123.6923 | -123.5962
637.9219 | 123.5367 | -61.0748 | 62.178 | 0.1649 | -0.012912 | -0.051005 | -0.0029928 | 0.033964 | -0.017597 | 0.064246 | -61.2442 | 62.3108 | -61.4548 | -61.4227 | 62.0041 | -0.059509 | 0.027466 | 0.068665 | 62.3154 | -61.441 | -0.37994 | 0.13275 | -0.16937 | -0.3479 | -0.17395 | -0.36621 | 0.13733 | 0.21057 | 61.1023 | 61.1435 | 123.0789 | 123.3856 | -0.16937 | 123.3902 | 61.0153 | -0.36621 | 123.3856 | -0.16937 | 61.0153 | 123.0789 | 123.3902 | -123.6328 | -123.6191
638.9219 | 123.5413 | -61.0886 | 62.178 | 0.21067 | -0.019321 | -0.031779 | -0.0040608 | 0.031827 | -0.017597 | 0.070655 | -61.203 | 62.3245 | -61.4548 | -61.3998 | 61.9904 | -0.064087 | 0.018311 | 0.082397 | 62.3154 | -61.4044 | -0.36621 | 0.14648 | -0.11444 | -0.31128 | -0.18768 | -0.31586 | 0.13733 | 0.25177 | 61.1069 | 61.171 | 123.0789 | 123.4131 | -0.11444 | 123.4039 | 61.0245 | -0.31586 | 123.4131 | -0.11444 | 61.0245 | 123.0789 | 123.4039 | -123.6328 | -123.5825
639.9844 | 123.5367 | -61.0886 | 62.2009 | 0.4243 | 0.0063138 | -0.018961 | 0.013029 | 0.035032 | -0.012257 | 0.063178 | -61.2534 | 62.384 | -61.4456 | -61.3449 | 62.0041 | -0.027466 | 0.004578 | 0.10986 | 62.2971 | -61.4273 | -0.35706 | 0.18311 | -0.16479 | -0.25635 | -0.19684 | -0.33874 | 0.09613 | 0.19226 | 61.0931 | 61.1984 | 123.0927 | 123.4726 | -0.16479 | 123.3856 | 61.0611 | -0.33874 | 123.4726 | -0.16479 | 61.0611 | 123.0927 | 123.3856 | -123.6465 | -123.6282
640.9219 | 123.4451 | -61.1114 | 62.2421 | -0.3539 | -0.015048 | -0.048869 | -0.00085683 | 0.047849 | -0.015461 | 0.077064 | -61.2534 | 62.4115 | -61.4456 | -61.2991 | 62.0178 | 0.11444 | -0.054932 | 0.25177 | 62.3474 | -61.3586 | -0.33417 | 0.16937 | -0.14191 | -0.18768 | -0.2243 | -0.24719 | 0.10529 | 0.19226 | 61.0565 | 61.3632 | 123.1293 | 123.5229 | -0.14191 | 123.4589 | 61.2259 | -0.24719 | 123.5229 | -0.14191 | 61.2259 | 123.1293 | 123.4589 | -123.6877 | -123.6008
641.9844 | 123.4451 | -61.1069 | 62.2147 | 0.073345 | 0.0020408 | -0.041392 | 0.021574 | 0.040372 | -0.0058484 | 0.068519 | -61.2213 | 62.4619 | -61.4548 | -61.2442 | 62.1002 | 0.07782 | -0.09613 | 0.19684 | 62.3108 | -61.3861 | -0.3479 | 0.24719 | -0.11444 | -0.13733 | -0.11444 | -0.27923 | 0.09613 | 0.23346 | 61.0107 | 61.3037 | 123.2071 | 123.5687 | -0.11444 | 123.4177 | 61.1847 | -0.27923 | 123.5687 | -0.11444 | 61.1847 | 123.2071 | 123.4177 | -123.6694 | -123.6008
642.9219 | 123.5138 | -61.084 | 62.1735 | 0.47007 | -0.012912 | -0.044596 | -0.0029928 | 0.038236 | -0.014393 | 0.067451 | -61.2305 | 62.3383 | -61.4456 | -61.3998 | 62.0132 | -0.050354 | 0.013733 | 0.073242 | 62.3337 | -61.409 | -0.36163 | 0.16479 | -0.14648 | -0.31586 | -0.16022 | -0.32501 | 0.16022 | 0.21515 | 61.0977 | 61.1572 | 123.0972 | 123.4222 | -0.14648 | 123.4177 | 61.0336 | -0.32501 | 123.4222 | -0.14648 | 61.0336 | 123.0972 | 123.4177 | -123.6191 | -123.5825
643.9844 | 123.4131 | -61.1435 | 62.2147 | 0.10386 | 0.0052458 | -0.013621 | 0.030119 | 0.042508 | -0.0015754 | 0.058906 | -61.2671 | 62.4481 | -61.4594 | -61.2213 | 62.0956 | 0.10986 | -0.11444 | 0.23804 | 62.3154 | -61.3998 | -0.31586 | 0.23346 | -0.1236 | -0.077819 | -0.11902 | -0.25635 | 0.10071 | 0.19226 | 61.0291 | 61.3815 | 123.2391 | 123.5916 | -0.1236 | 123.4589 | 61.2534 | -0.25635 | 123.5916 | -0.1236 | 61.2534 | 123.2391 | 123.4589 | -123.674 | -123.6145
644.9219 | 123.4863 | -61.0565 | 62.1872 | 0.088604 | -0.015048 | -0.054209 | -0.0040608 | 0.040372 | -0.02187 | 0.069587 | -61.2671 | 62.3428 | -61.4548 | -61.3678 | 62.0178 | -0.009155 | -0.027466 | 0.1236 | 62.3383 | -61.3907 | -0.39825 | 0.15564 | -0.21057 | -0.31128 | -0.16937 | -0.33417 | 0.15106 | 0.18768 | 61.0291 | 61.1801 | 123.0743 | 123.3994 | -0.21057 | 123.3948 | 61.0474 | -0.33417 | 123.3994 | -0.21057 | 61.0474 | 123.0743 | 123.3948 | -123.642 | -123.5779
645.9844 | 123.555 | -61.0977 | 62.1552 | 0.69895 | -0.01398 | -0.051005 | -0.0019248 | 0.043577 | -0.01012 | 0.063178 | -61.2167 | 62.3383 | -61.4227 | -61.409 | 61.9675 | -0.059509 | 0.027466 | 0.07782 | 62.3245 | -61.4227 | -0.32501 | 0.18311 | -0.11902 | -0.31128 | -0.18768 | -0.32501 | 0.16937 | 0.20599 | 61.1252 | 61.1755 | 123.0652 | 123.436 | -0.11902 | 123.4222 | 61.0382 | -0.32501 | 123.436 | -0.11902 | 61.0382 | 123.0652 | 123.4222 | -123.5779 | -123.5779
646.9219 | 123.5184 | -61.0748 | 62.1826 | 0.31749 | -0.0086402 | -0.033915 | 0.010892 | 0.030759 | -0.019733 | 0.061042 | -61.2442 | 62.3108 | -61.441 | -61.3907 | 61.9904 | -0.045776 | -0.004578 | 0.10071 | 62.3108 | -61.4136 | -0.36621 | 0.12817 | -0.16937 | -0.31586 | -0.19226 | -0.33874 | 0.12817 | 0.19684 | 61.0703 | 61.1755 | 123.0652 | 123.3856 | -0.16937 | 123.3856 | 61.0291 | -0.33874 | 123.3856 | -0.16937 | 61.0291 | 123.0652 | 123.3856 | -123.6237 | -123.5962
647.9844 | 123.5184 | -61.0748 | 62.1872 | 0.22593 | -0.012912 | -0.027506 | -0.01047 | 0.037168 | -0.014393 | 0.063178 | -61.2625 | 62.3474 | -61.4319 | -61.3724 | 62.0224 | -0.004578 | -0.022888 | 0.14648 | 62.3108 | -61.4182 | -0.35706 | 0.16022 | -0.18768 | -0.29755 | -0.1648 | -0.34332 | 0.1236 | 0.16937 | 61.0519 | 61.2213 | 123.0972 | 123.4222 | -0.18768 | 123.3856 | 61.0703 | -0.34332 | 123.4222 | -0.18768 | 61.0703 | 123.0972 | 123.3856 | -123.6191 | -123.6053
648.9219 | 123.5184 | -61.0703 | 62.2101 | 0.14964 | -0.020389 | -0.034983 | 0.00021117 | 0.025419 | -0.025074 | 0.069587 | -61.2579 | 62.3474 | -61.4502 | -61.3724 | 62.0224 | -0.013733 | -0.022888 | 0.13733 | 62.3383 | -61.4044 | -0.37994 | 0.13733 | -0.18768 | -0.30212 | -0.18768 | -0.33417 | 0.12817 | 0.19226 | 61.0474 | 61.2076 | 123.0927 | 123.4177 | -0.18768 | 123.4085 | 61.0565 | -0.33417 | 123.4177 | -0.18768 | 61.0565 | 123.0927 | 123.4085 | -123.6603 | -123.6145
649.9219 | 123.555 | -61.0703 | 62.1826 | 3.8575 | -0.020389 | -0.04246 | 0.0098242 | 0.039304 | -0.033619 | 0.074928 | -61.0291 | 62.3428 | -61.4227 | -61.3953 | 61.9949 | -0.086975 | 0.022888 | 0.054932 | 62.3337 | -61.4273 | -0.35248 | 0.16022 | 0.041198 | -0.32501 | -0.18768 | -0.35706 | 0.15106 | 0.39368 | 61.0931 | 61.1252 | 123.0652 | 123.4131 | 0.041198 | 123.4039 | 60.9833 | -0.35706 | 123.4131 | 0.041198 | 60.9833 | 123.0652 | 123.4039 | -123.6053 | -123.6099
650.9844 | 123.5001 | -61.0611 | 62.2284 | -0.14028 | -0.010776 | -0.030711 | 0.013029 | 0.025419 | -0.022938 | 0.064246 | -61.1938 | 62.3566 | -61.4136 | -61.3678 | 61.9904 | 0.004578 | -0.013733 | 0.10986 | 62.3749 | -61.3998 | -0.35248 | 0.12817 | -0.13275 | -0.3067 | -0.23804 | -0.33875 | 0.14648 | 0.21973 | 61.0474 | 61.171 | 123.0515 | 123.4177 | -0.13275 | 123.436 | 61.0657 | -0.33875 | 123.4177 | -0.13275 | 61.0657 | 123.0515 | 123.436 | -123.642 | -123.6282
651.9219 | 123.5367 | -61.0748 | 62.1689 | 0.24119 | -0.016117 | -0.015757 | 0.00021117 | 0.028623 | -0.017597 | 0.072791 | -61.2122 | 62.3245 | -61.4639 | -61.4044 | 61.9583 | -0.059509 | 0.022888 | 0.068665 | 62.3291 | -61.4136 | -0.3891 | 0.15564 | -0.13733 | -0.32959 | -0.21057 | -0.33874 | 0.16022 | 0.25177 | 61.0977 | 61.1435 | 123.0331 | 123.3994 | -0.13733 | 123.4039 | 61.0153 | -0.33874 | 123.3994 | -0.13733 | 61.0153 | 123.0331 | 123.4039 | -123.6328 | -123.5825
652.9844 | 123.5321 | -61.0657 | 62.178 | 0.47007 | -0.0075722 | -0.028574 | 0.020506 | 0.035032 | -0.0047804 | 0.059974 | -61.1847 | 62.3566 | -61.441 | -61.4044 | 61.9675 | -0.082397 | 0.022888 | 0.059509 | 62.3108 | -61.4548 | -0.37537 | 0.17853 | -0.11902 | -0.33874 | -0.21057 | -0.3891 | 0.13275 | 0.25635 | 61.0886 | 61.1252 | 123.0331 | 123.4222 | -0.11902 | 123.3765 | 60.9833 | -0.3891 | 123.4222 | -0.11902 | 60.9833 | 123.0331 | 123.3765 | -123.6191 | -123.6328
653.9219 | 123.5504 | -61.084 | 62.1826 | 0.37852 | -0.016117 | -0.0072124 | -0.0051288 | 0.031827 | -0.011188 | 0.064246 | -61.1984 | 62.3383 | -61.4227 | -61.4456 | 62.0224 | -0.09613 | 0.004578 | 0.073242 | 62.3337 | -61.4182 | -0.33874 | 0.15564 | -0.11444 | -0.36163 | -0.16022 | -0.33417 | 0.15106 | 0.2243 | 61.0886 | 61.1572 | 123.1064 | 123.4222 | -0.11444 | 123.4177 | 60.9879 | -0.33417 | 123.4222 | -0.11444 | 60.9879 | 123.1064 | 123.4177 | -123.6053 | -123.6008
654.9844 | 123.4818 | -61.1206 | 62.1689 | 0.45481 | -0.0054352 | -0.043528 | 0.014097 | 0.042508 | -0.0090524 | 0.053565 | -61.2579 | 62.4115 | -61.4548 | -61.2808 | 62.0499 | 0.022888 | -0.068665 | 0.15106 | 62.2925 | -61.4044 | -0.33417 | 0.24262 | -0.13733 | -0.16022 | -0.11902 | -0.28381 | 0.1236 | 0.19684 | 61.0519 | 61.2717 | 123.1705 | 123.5321 | -0.13733 | 123.4131 | 61.1435 | -0.28381 | 123.5321 | -0.13733 | 61.1435 | 123.1705 | 123.4131 | -123.6237 | -123.5733
655.9219 | 123.5504 | -61.0611 | 62.1826 | 0.073345 | -0.018253 | -0.043528 | -0.011538 | 0.030759 | -0.026142 | 0.070655 | -61.2442 | 62.3566 | -61.4365 | -61.3907 | 61.9904 | -0.022888 | 0.013733 | 0.09613 | 62.3703 | -61.4227 | -0.37537 | 0.17395 | -0.18311 | -0.32959 | -0.19226 | -0.36163 | 0.18768 | 0.19226 | 61.0748 | 61.1572 | 123.0515 | 123.4177 | -0.18311 | 123.4314 | 61.0382 | -0.36163 | 123.4177 | -0.18311 | 61.0382 | 123.0515 | 123.4314 | -123.6191 | -123.6053
656.9219 | 123.5458 | -61.084 | 62.1689 | 0.40904 | -0.023593 | -0.026438 | 0.0055522 | 0.038236 | -0.024006 | 0.068519 | -61.3998 | 62.3154 | -61.4502 | -61.4136 | 61.9263 | -0.059509 | 0.059509 | 0.036621 | 62.3291 | -61.4273 | -0.36621 | 0.14648 | -0.31586 | -0.32959 | -0.24261 | -0.34332 | 0.16022 | 0.050354 | 61.1435 | 61.1206 | 123.0103 | 123.3994 | -0.31586 | 123.4131 | 61.0245 | -0.34332 | 123.3994 | -0.31586 | 61.0245 | 123.0103 | 123.4131 | -123.6191 | -123.5962
657.9844 | 123.4039 | -61.1435 | 62.2284 | 0.14964 | 0.0020408 | -0.018961 | 0.020506 | 0.042508 | -0.0026434 | 0.052497 | -61.2762 | 62.4344 | -61.4685 | -61.203 | 62.0499 | 0.073242 | -0.11902 | 0.2243 | 62.2879 | -61.3861 | -0.32501 | 0.20599 | -0.13275 | -0.059509 | -0.17853 | -0.24261 | 0.059509 | 0.19226 | 61.0245 | 61.3678 | 123.1934 | 123.5779 | -0.13275 | 123.4314 | 61.2167 | -0.24261 | 123.5779 | -0.13275 | 61.2167 | 123.1934 | 123.4314 | -123.6969 | -123.6145
658.9219 | 123.5458 | -61.0611 | 62.1735 | 0.8668 | -0.0097082 | -0.04246 | -0.0051288 | 0.039304 | -0.026142 | 0.069587 | -61.2259 | 62.3291 | -61.4365 | -61.3907 | 61.9858 | -0.07782 | 0.022888 | 0.07782 | 62.3428 | -61.3998 | -0.37537 | 0.15564 | -0.16479 | -0.32959 | -0.18768 | -0.33875 | 0.16937 | 0.21057 | 61.084 | 61.1389 | 123.0469 | 123.3902 | -0.16479 | 123.4039 | 60.9833 | -0.33875 | 123.3902 | -0.16479 | 60.9833 | 123.0469 | 123.4039 | -123.6099 | -123.5733
659.9844 | 123.5596 | -61.0474 | 62.178 | 0.48533 | -0.0097082 | -0.034983 | 0.0066202 | 0.038236 | -0.012257 | 0.059974 | -61.1847 | 62.352 | -61.441 | -61.3998 | 61.9812 | -0.082397 | 0.032043 | 0.045776 | 62.3154 | -61.4182 | -0.39368 | 0.17395 | -0.13733 | -0.35248 | -0.19684 | -0.37079 | 0.13733 | 0.25635 | 61.0794 | 61.0931 | 123.0286 | 123.3994 | -0.13733 | 123.3627 | 60.965 | -0.37079 | 123.3994 | -0.13733 | 60.965 | 123.0286 | 123.3627 | -123.6191 | -123.5962
660.9219 | 123.5321 | -61.0794 | 62.1826 | 0.058086 | -0.020389 | -0.054209 | -0.011538 | 0.04144 | -0.036823 | 0.063178 | -61.2808 | 62.3199 | -61.4502 | -61.3403 | 61.9766 | -0.013733 | -0.004578 | 0.13733 | 62.3611 | -61.3953 | -0.37079 | 0.13733 | -0.20142 | -0.26092 | -0.20599 | -0.31586 | 0.17853 | 0.16937 | 61.0748 | 61.2167 | 123.056 | 123.3994 | -0.20142 | 123.4406 | 61.0657 | -0.31586 | 123.3994 | -0.20142 | 61.0657 | 123.056 | 123.4406 | -123.6328 | -123.5779
661.9844 | 123.5413 | -61.0748 | 62.1826 | 0.4243 | 0.00097275 | -0.037119 | 0.013029 | 0.027555 | -0.018665 | 0.066383 | -61.235 | 62.3932 | -61.4319 | -61.3632 | 61.9492 | -0.073242 | 0.018311 | 0.082397 | 62.2971 | -61.4319 | -0.35706 | 0.21057 | -0.16022 | -0.28839 | -0.23346 | -0.35706 | 0.11444 | 0.19684 | 61.0931 | 61.1572 | 123.024 | 123.468 | -0.16022 | 123.3719 | 61.0016 | -0.35706 | 123.468 | -0.16022 | 61.0016 | 123.024 | 123.3719 | -123.6145 | -123.6145
662.9219 | 123.468 | -61.0886 | 62.1826 | 0.43956 | 0.0063138 | -0.023234 | 0.010892 | 0.047849 | -0.014393 | 0.064246 | -61.2671 | 62.4115 | -61.4639 | -61.2854 | 62.059 | 0.018311 | -0.064087 | 0.13733 | 62.2879 | -61.3953 | -0.37537 | 0.22888 | -0.17853 | -0.19684 | -0.1236 | -0.3067 | 0.10529 | 0.19684 | 61.0245 | 61.2259 | 123.1476 | 123.5001 | -0.17853 | 123.3765 | 61.1069 | -0.3067 | 123.5001 | -0.17853 | 61.1069 | 123.1476 | 123.3765 | -123.6465 | -123.5779
663.9219 | 123.5367 | -61.0657 | 62.1643 | 0.47007 | -0.0075722 | -0.045664 | 0.015165 | 0.028623 | -0.011188 | 0.055701 | -61.2213 | 62.3886 | -61.4594 | -61.3861 | 62.0132 | -0.041199 | 0.004578 | 0.073242 | 62.3199 | -61.4227 | -0.39368 | 0.2243 | -0.15564 | -0.32043 | -0.15106 | -0.35705 | 0.15564 | 0.23804 | 61.0703 | 61.1389 | 123.0789 | 123.4543 | -0.15564 | 123.3856 | 61.0245 | -0.35705 | 123.4543 | -0.15564 | 61.0245 | 123.0789 | 123.3856 | -123.6237 | -123.587
664.9844 | 123.5092 | -61.084 | 62.1872 | 0.058086 | -0.023593 | -0.04246 | -0.0072648 | 0.031827 | -0.037891 | 0.063178 | -61.1755 | 62.3795 | -61.4502 | -61.3541 | 62.0407 | -0.009155 | -0.041199 | 0.10071 | 62.352 | -61.4136 | -0.36621 | 0.19226 | -0.091553 | -0.27008 | -0.14649 | -0.32959 | 0.16479 | 0.27466 | 61.0428 | 61.1847 | 123.1247 | 123.4634 | -0.091553 | 123.436 | 61.0748 | -0.32959 | 123.4634 | -0.091553 | 61.0748 | 123.1247 | 123.436 | -123.6374 | -123.6008
665.9219 | 123.4222 | -61.1252 | 62.2284 | 0.31749 | 0.0073818 | -0.046732 | 0.022642 | 0.035032 | -0.026142 | 0.06211 | -61.2671 | 62.4619 | -61.441 | -61.0611 | 61.9858 | 0.054932 | -0.082397 | 0.17853 | 62.2925 | -61.3861 | -0.31586 | 0.23346 | -0.14191 | 0.064087 | -0.24262 | -0.26093 | 0.064086 | 0.17395 | 61.0428 | 61.3037 | 123.111 | 123.587 | -0.14191 | 123.4177 | 61.1801 | -0.26093 | 123.587 | -0.14191 | 61.1801 | 123.111 | 123.4177 | -123.6694 | -123.6145
666.9219 | 123.5596 | -61.0519 | 62.2101 | -0.56752 | -0.0043672 | -0.028574 | -0.0029928 | 0.04144 | -0.026142 | 0.067451 | -61.1755 | 62.352 | -61.3861 | -61.4502 | 61.9492 | -0.041199 | 0.041199 | 0.068665 | 62.3383 | -61.4319 | -0.33417 | 0.14191 | -0.1236 | -0.39825 | -0.26093 | -0.37994 | 0.12817 | 0.21057 | 61.0931 | 61.1206 | 123.0011 | 123.4039 | -0.1236 | 123.3902 | 61.0107 | -0.37994 | 123.4039 | -0.1236 | 61.0107 | 123.0011 | 123.3902 | -123.5962 | -123.642
667.9844 | 123.5138 | -61.0748 | 62.2009 | 0.058086 | -0.021457 | -0.029642 | -0.0051288 | 0.0361 | -0.028278 | 0.072791 | -61.1664 | 62.384 | -61.4136 | -61.3632 | 62.0316 | 0.004578 | -0.032043 | 0.082397 | 62.3383 | -61.4182 | -0.33874 | 0.18311 | -0.091553 | -0.28839 | -0.16937 | -0.34332 | 0.13733 | 0.24719 | 61.0428 | 61.1572 | 123.1064 | 123.4589 | -0.091553 | 123.4131 | 61.0794 | -0.34332 | 123.4589 | -0.091553 | 61.0794 | 123.1064 | 123.4131 | -123.6145 | -123.6191
668.9219 | 123.5825 | -61.0611 | 62.1872 | 0.45481 | 0.0020408 | -0.033915 | 0.018369 | 0.026487 | -0.0047804 | 0.059974 | -61.1893 | 62.3566 | -61.4273 | -61.3953 | 61.9766 | -0.091553 | 0.041199 | 0.050354 | 62.3062 | -61.4319 | -0.36621 | 0.16937 | -0.12817 | -0.33417 | -0.21057 | -0.37079 | 0.11902 | 0.23804 | 61.1023 | 61.1114 | 123.0377 | 123.4177 | -0.12817 | 123.3673 | 60.9695 | -0.37079 | 123.4177 | -0.12817 | 60.9695 | 123.0377 | 123.3673 | -123.6145 | -123.6191
669.9844 | 123.4451 | -61.1069 | 62.2101 | -0.14028 | -0.0043672 | -0.030711 | 0.030119 | 0.04144 | -0.00050737 | 0.064246 | -61.1801 | 62.4573 | -61.441 | -61.2625 | 62.0544 | 0.036621 | -0.07782 | 0.11902 | 62.3154 | -61.3953 | -0.33417 | 0.24719 | -0.073242 | -0.15564 | -0.15564 | -0.28839 | 0.10529 | 0.26093 | 61.0291 | 61.2259 | 123.1613 | 123.5641 | -0.073242 | 123.4222 | 61.1435 | -0.28839 | 123.5641 | -0.073242 | 61.1435 | 123.1613 | 123.4222 | -123.6511 | -123.6053
670.9219 | 123.5413 | -61.0611 | 62.1826 | 0.54637 | -0.0032992 | -0.028574 | 0.010892 | 0.042508 | -0.012257 | 0.05677 | -61.2579 | 62.4023 | -61.4548 | -61.3495 | 62.0132 | -0.036621 | 0 | 0.091553 | 62.3383 | -61.4227 | -0.39368 | 0.21973 | -0.19684 | -0.28839 | -0.16937 | -0.36163 | 0.15564 | 0.19684 | 61.0611 | 61.1526 | 123.0743 | 123.4634 | -0.19684 | 123.3994 | 61.0245 | -0.36163 | 123.4634 | -0.19684 | 61.0245 | 123.0743 | 123.3994 | -123.6374 | -123.6053
671.9844 | 123.5229 | -61.0611 | 62.1964 | 0.28697 | -0.01398 | -0.044596 | 0.0055522 | 0.040372 | -0.024006 | 0.066383 | -61.2625 | 62.3337 | -61.4685 | -61.3907 | 61.9949 | -0.018311 | -0.036621 | 0.10986 | 62.3154 | -61.4182 | -0.40741 | 0.13733 | -0.20142 | -0.32959 | -0.20142 | -0.35706 | 0.11902 | 0.20599 | 61.0245 | 61.171 | 123.056 | 123.3948 | -0.20142 | 123.3765 | 61.0428 | -0.35706 | 123.3948 | -0.20142 | 61.0428 | 123.056 | 123.3765 | -123.6649 | -123.6145
672.9219 | 123.4131 | -61.1114 | 62.2055 | 0.28697 | -0.0011632 | -0.027506 | 0.014097 | 0.0361 | -0.0058484 | 0.058906 | -61.2625 | 62.4481 | -61.4685 | -61.2076 | 62.0865 | 0.09613 | -0.11902 | 0.21515 | 62.2833 | -61.3861 | -0.35706 | 0.24262 | -0.15106 | -0.096131 | -0.11902 | -0.27466 | 0.07782 | 0.20599 | 60.9924 | 61.3266 | 123.1979 | 123.5596 | -0.15106 | 123.3948 | 61.2076 | -0.27466 | 123.5596 | -0.15106 | 61.2076 | 123.1979 | 123.3948 | -123.674 | -123.5916
673.9844 | 123.4451 | -61.0748 | 62.2284 | 0.058086 | 0.00097275 | -0.014689 | 0.013029 | 0.046781 | 0.0059006 | 0.059974 | -61.2259 | 62.4756 | -61.4502 | -61.2396 | 62.0911 | 0.059509 | -0.10071 | 0.18768 | 62.3199 | -61.3953 | -0.37537 | 0.24719 | -0.15106 | -0.16479 | -0.13733 | -0.32043 | 0.091552 | 0.2243 | 60.9741 | 61.2625 | 123.1659 | 123.5504 | -0.15106 | 123.3948 | 61.1343 | -0.32043 | 123.5504 | -0.15106 | 61.1343 | 123.1659 | 123.3948 | -123.6786 | -123.6237
674.9219 | 123.5092 | -61.084 | 62.2055 | 0.50059 | -0.0075722 | -0.036051 | 0.015165 | 0.055326 | -0.0079844 | 0.066383 | -61.2442 | 62.4023 | -61.4639 | -61.3266 | 62.0224 | -0.022888 | -0.013733 | 0.10071 | 62.3291 | -61.4136 | -0.37994 | 0.19684 | -0.16022 | -0.24262 | -0.18311 | -0.32959 | 0.1236 | 0.21973 | 61.0703 | 61.1847 | 123.1064 | 123.4863 | -0.16022 | 123.4131 | 61.0611 | -0.32959 | 123.4863 | -0.16022 | 61.0611 | 123.1064 | 123.4131 | -123.6694 | -123.6191
675.9844 | 123.5092 | -61.084 | 62.2101 | 0.058086 | -0.015048 | -0.022166 | -0.01581 | 0.039304 | -0.032551 | 0.068519 | -61.2671 | 62.3428 | -61.441 | -61.3815 | 62.027 | -0.009155 | -0.022888 | 0.11902 | 62.3383 | -61.3953 | -0.35706 | 0.13275 | -0.18311 | -0.29755 | -0.1831 | -0.31128 | 0.12817 | 0.17395 | 61.0611 | 61.203 | 123.111 | 123.4268 | -0.18311 | 123.4222 | 61.0748 | -0.31128 | 123.4268 | -0.18311 | 61.0748 | 123.111 | 123.4222 | -123.6511 | -123.6053
676.9219 | 123.5413 | -61.0657 | 62.2101 | 1.7976 | -0.0097082 | -0.027506 | 0.0034162 | 0.038236 | -0.024006 | 0.070655 | -61.1481 | 62.3291 | -61.4319 | -61.3815 | 61.9766 | -0.036621 | 0.027466 | 0.07782 | 62.3749 | -61.4227 | -0.36621 | 0.11902 | -0.082397 | -0.31586 | -0.23346 | -0.35705 | 0.1648 | 0.28381 | 61.0931 | 61.1435 | 123.0423 | 123.3948 | -0.082397 | 123.4406 | 61.0291 | -0.35705 | 123.3948 | -0.082397 | 61.0291 | 123.0423 | 123.4406 | -123.642 | -123.6328
677.9844 | 123.4589 | -61.1114 | 62.2192 | 0.058086 | 0.0020408 | -0.015757 | 0.019437 | 0.031827 | -0.0079844 | 0.06211 | -61.2854 | 62.4481 | -61.4502 | -61.2579 | 62.0911 | 0.045776 | -0.091553 | 0.16479 | 62.2833 | -61.4273 | -0.33875 | 0.22888 | -0.17395 | -0.14649 | -0.12817 | -0.31586 | 0.064087 | 0.16479 | 61.0199 | 61.2762 | 123.2025 | 123.5596 | -0.17395 | 123.3948 | 61.1572 | -0.31586 | 123.5596 | -0.17395 | 61.1572 | 123.2025 | 123.3948 | -123.6694 | -123.6465
678.9219 | 123.4451 | -61.1069 | 62.2147 | -0.033467 | 0.014859 | -0.039256 | 0.021574 | 0.035032 | -0.013325 | 0.06211 | -61.1984 | 62.4435 | -61.4319 | -61.2808 | 62.0407 | 0.036621 | -0.059509 | 0.15106 | 62.3062 | -61.3861 | -0.32501 | 0.22888 | -0.091552 | -0.17395 | -0.17395 | -0.27923 | 0.091552 | 0.23346 | 61.0474 | 61.2579 | 123.1476 | 123.5504 | -0.091552 | 123.4131 | 61.1435 | -0.27923 | 123.5504 | -0.091552 | 61.1435 | 123.1476 | 123.4131 | -123.6465 | -123.6008
679.9844 | 123.4039 | -61.0977 | 62.2421 | 0.348 | -0.0022312 | -0.040324 | 0.021574 | 0.049985 | -0.0079844 | 0.066383 | -61.29 | 62.471 | -61.4685 | -61.2396 | 62.1002 | 0.054932 | -0.16022 | -0.041199 | 62.2467 | -61.4044 | -0.37079 | 0.22888 | -0.19226 | -0.14191 | -0.14191 | -0.3067 | 0.004578 | 0.17853 | 60.9375 | 61.0565 | 123.1979 | 123.5687 | -0.19226 | 123.3444 | 61.1526 | -0.3067 | 123.5687 | -0.19226 | 61.1526 | 123.1979 | 123.3444 | -123.7106 | -123.6465
680.9219 | 123.4497 | -61.1206 | 62.2284 | 0.45481 | 0.018063 | -0.0050764 | 0.010892 | 0.042508 | -0.011188 | 0.064246 | -61.5509 | 62.3886 | -61.5234 | -61.29 | 62.0682 | 0.10529 | -0.07782 | 0.19226 | 62.3016 | -61.3907 | -0.40283 | 0.16022 | -0.4303 | -0.16937 | -0.16022 | -0.27008 | 0.073242 | -0.027466 | 61.0428 | 61.3129 | 123.1888 | 123.5092 | -0.4303 | 123.4222 | 61.2259 | -0.27008 | 123.5092 | -0.4303 | 61.2259 | 123.1888 | 123.4222 | -123.7518 | -123.6191
681.9844 | 123.5321 | -61.0886 | 62.1918 | 0.36326 | -0.015048 | -0.02537 | -0.011538 | 0.042508 | -0.02187 | 0.063178 | -61.2534 | 62.3474 | -61.4685 | -61.3953 | 62.0041 | -0.027466 | -0.027466 | 0.10986 | 62.352 | -61.4182 | -0.37994 | 0.15564 | -0.16479 | -0.3067 | -0.18768 | -0.32959 | 0.16022 | 0.21515 | 61.0611 | 61.1984 | 123.0927 | 123.436 | -0.16479 | 123.4406 | 61.0611 | -0.32959 | 123.436 | -0.16479 | 61.0611 | 123.0927 | 123.4406 | -123.6603 | -123.6099
682.9219 | 123.4955 | -61.0977 | 62.2284 | -0.39968 | 0.0031088 | -0.021098 | 0.020506 | 0.029691 | -0.013325 | 0.072791 | -61.1801 | 62.4619 | -61.441 | -61.29 | 62.0499 | 0.041199 | -0.045776 | 0.14191 | 62.3154 | -61.4044 | -0.34332 | 0.23346 | -0.082398 | -0.19226 | -0.17853 | -0.3067 | 0.086975 | 0.26093 | 61.0519 | 61.2396 | 123.1476 | 123.5596 | -0.082398 | 123.4131 | 61.1389 | -0.3067 | 123.5596 | -0.082398 | 61.1389 | 123.1476 | 123.4131 | -123.6694 | -123.6328
683.9844 | 123.5458 | -61.0794 | 62.1964 | 0.48533 | -0.0065042 | -0.023234 | 0.00021117 | 0.045713 | -0.020801 | 0.069587 | -61.2579 | 62.4115 | -61.4502 | -61.3449 | 62.0178 | -0.027466 | -0.022888 | 0.073242 | 62.3291 | -61.4273 | -0.37079 | 0.21515 | -0.17853 | -0.2655 | -0.17853 | -0.3479 | 0.13275 | 0.19226 | 61.0565 | 61.1526 | 123.0972 | 123.4909 | -0.17853 | 123.4085 | 61.0519 | -0.3479 | 123.4909 | -0.17853 | 61.0519 | 123.0972 | 123.4085 | -123.6465 | -123.6237
684.9219 | 123.4818 | -61.1069 | 62.2421 | -0.033467 | -0.0043672 | -0.016825 | 0.0034162 | 0.04144 | -0.0015754 | 0.068519 | -61.2213 | 62.4527 | -61.4456 | -61.2579 | 62.0636 | 0.041199 | -0.09613 | 0.15106 | 62.3383 | -61.3953 | -0.33875 | 0.21057 | -0.11444 | -0.15106 | -0.17853 | -0.28839 | 0.096131 | 0.22431 | 61.0107 | 61.2579 | 123.1705 | 123.5596 | -0.11444 | 123.4451 | 61.1481 | -0.28839 | 123.5596 | -0.11444 | 61.1481 | 123.1705 | 123.4451 | -123.6877 | -123.6374
686 | 123.5046 | -61.0657 | 62.1918 | 0.073345 | -0.010776 | -0.026438 | -0.019015 | 0.047849 | -0.022938 | 0.073859 | -61.2808 | 62.3611 | -61.4456 | -61.409 | 62.0636 | 0 | -0.059509 | 0.10986 | 62.3566 | -61.409 | -0.37994 | 0.16937 | -0.21515 | -0.34332 | -0.12817 | -0.34332 | 0.16479 | 0.1648 | 61.0062 | 61.1755 | 123.1293 | 123.4268 | -0.21515 | 123.4222 | 61.0657 | -0.34332 | 123.4268 | -0.21515 | 61.0657 | 123.1293 | 123.4222 | -123.6374 | -123.6008
686.9219 | 123.4863 | -61.084 | 62.233 | -0.32338 | 0.0095178 | -0.048869 | 0.011961 | 0.049985 | -0.0037124 | 0.069587 | -61.203 | 62.4664 | -61.4227 | -61.2579 | 62.0361 | 0.045776 | -0.086975 | 0.15106 | 62.352 | -61.3907 | -0.33874 | 0.23346 | -0.11902 | -0.17395 | -0.19684 | -0.3067 | 0.11902 | 0.21973 | 60.997 | 61.235 | 123.1201 | 123.5504 | -0.11902 | 123.436 | 61.1298 | -0.3067 | 123.5504 | -0.11902 | 61.1298 | 123.1201 | 123.436 | -123.6557 | -123.6237
687.9844 | 123.4543 | -61.1069 | 62.2284 | -0.12502 | 0.0041778 | -0.02537 | 0.024778 | 0.05319 | 0.0059006 | 0.064246 | -61.235 | 62.4619 | -61.4319 | -61.2396 | 62.0911 | 0.050354 | -0.10986 | 0.16479 | 62.3016 | -61.3907 | -0.32501 | 0.23346 | -0.12817 | -0.13275 | -0.13733 | -0.28381 | 0.073242 | 0.19684 | 60.997 | 61.2717 | 123.1979 | 123.5687 | -0.12817 | 123.4085 | 61.1572 | -0.28381 | 123.5687 | -0.12817 | 61.1572 | 123.1979 | 123.4085 | -123.6603 | -123.6191
688.9219 | 123.4772 | -61.0794 | 62.233 | -0.0029495 | 0.0031088 | -0.030711 | 0.022642 | 0.0361 | -0.0037124 | 0.067451 | -61.2076 | 62.4527 | -61.4548 | -61.3266 | 62.0865 | 0.050354 | -0.073242 | 0.14191 | 62.3383 | -61.3998 | -0.37537 | 0.21973 | -0.12817 | -0.24719 | -0.14648 | -0.32043 | 0.10529 | 0.24719 | 61.0062 | 61.2213 | 123.1659 | 123.5321 | -0.12817 | 123.4177 | 61.1298 | -0.32043 | 123.5321 | -0.12817 | 61.1298 | 123.1659 | 123.4177 | -123.6877 | -123.6328
689.9844 | 123.3444 | -61.0931 | 62.233 | -0.44545 | -0.010776 | -0.039256 | 0.013029 | 0.0361 | -0.013325 | 0.066383 | -61.2717 | 62.4847 | -61.441 | -61.2396 | 62.1048 | 0.10986 | -0.13275 | 0.15564 | 62.352 | -61.3541 | -0.3479 | 0.25177 | -0.17853 | -0.14648 | -0.12817 | -0.26093 | 0.11902 | 0.16937 | 60.9604 | 61.2488 | 123.1979 | 123.5779 | -0.17853 | 123.4451 | 61.203 | -0.26093 | 123.5779 | -0.17853 | 61.203 | 123.1979 | 123.4451 | -123.674 | -123.587
690.9219 | 123.468 | -61.1023 | 62.233 | -0.079243 | -0.0075722 | -0.036051 | 0.019437 | 0.043577 | -0.011188 | 0.064246 | -61.203 | 62.4481 | -61.441 | -61.2946 | 62.0636 | 0.050354 | -0.073242 | 0.12817 | 62.3428 | -61.3724 | -0.33875 | 0.21515 | -0.10071 | -0.19226 | -0.16937 | -0.27008 | 0.10986 | 0.23804 | 61.0291 | 61.2305 | 123.1659 | 123.5504 | -0.10071 | 123.4451 | 61.1526 | -0.27008 | 123.5504 | -0.10071 | 61.1526 | 123.1659 | 123.4451 | -123.674 | -123.6053
691.9844 | 123.4451 | -61.0886 | 62.265 | -1.3305 | -0.0065042 | -0.037119 | -0.014742 | 0.045713 | -0.014393 | 0.065314 | -61.3037 | 62.4481 | -61.4502 | -61.2671 | 62.1002 | 0.10986 | -0.11444 | 0.20599 | 62.3474 | -61.3815 | -0.36163 | 0.18311 | -0.21515 | -0.17853 | -0.16479 | -0.29297 | 0.082397 | 0.14648 | 60.9741 | 61.2946 | 123.1888 | 123.5367 | -0.21515 | 123.436 | 61.1984 | -0.29297 | 123.5367 | -0.21515 | 61.1984 | 123.1888 | 123.436 | -123.7152 | -123.6465
692.9219 | 123.436 | -61.1023 | 62.2742 | -0.65908 | 0.0084498 | -0.036051 | 0.0066202 | 0.030759 | -0.016529 | 0.066383 | -61.2213 | 62.4802 | -61.4502 | -61.2488 | 62.1002 | 0.086975 | -0.1236 | 0.20142 | 62.352 | -61.3953 | -0.3479 | 0.20599 | -0.11902 | -0.14648 | -0.17395 | -0.29297 | 0.07782 | 0.22888 | 60.9787 | 61.3037 | 123.2025 | 123.5825 | -0.11902 | 123.4543 | 61.1893 | -0.29297 | 123.5825 | -0.11902 | 61.1893 | 123.2025 | 123.4543 | -123.7244 | -123.6694
693.9844 | 123.4863 | -61.1252 | 62.2147 | -0.033467 | -0.0032992 | -0.046732 | 0.014097 | 0.048917 | -0.0047804 | 0.057838 | -61.2076 | 62.4344 | -61.4456 | -61.2671 | 62.0682 | 0.041199 | -0.07782 | 0.13275 | 62.3337 | -61.3998 | -0.32044 | 0.21973 | -0.082398 | -0.14191 | -0.14648 | -0.27466 | 0.11902 | 0.23804 | 61.0474 | 61.2579 | 123.1934 | 123.5596 | -0.082398 | 123.4589 | 61.1664 | -0.27466 | 123.5596 | -0.082398 | 61.1664 | 123.1934 | 123.4589 | -123.6603 | -123.6145
694.9219 | 123.4177 | -61.1023 | 62.2467 | -0.46071 | -0.0022312 | -0.040324 | -0.0029928 | 0.05319 | -0.013325 | 0.071723 | -61.2671 | 62.439 | -61.4594 | -61.3174 | 62.3245 | 0.19226 | -0.21057 | 0.07782 | 62.3154 | -61.3953 | -0.35706 | 0.19226 | -0.1648 | -0.21515 | 0.07782 | -0.29297 | 0.068665 | 0.19226 | 60.8917 | 61.1801 | 123.4268 | 123.5413 | -0.1648 | 123.4177 | 61.2946 | -0.29297 | 123.5413 | -0.1648 | 61.2946 | 123.4268 | 123.4177 | -123.7061 | -123.642
696 | 123.5138 | -61.0794 | 62.2147 | 0.28697 | -0.019321 | -0.052073 | -0.0051288 | 0.032895 | -0.028278 | 0.063178 | -61.2579 | 62.3703 | -61.4548 | -61.3953 | 62.0041 | -0.032043 | -0.013733 | 0.09613 | 62.3474 | -61.409 | -0.37537 | 0.15564 | -0.17853 | -0.31586 | -0.21057 | -0.32959 | 0.13275 | 0.19684 | 61.0657 | 61.1755 | 123.0835 | 123.4497 | -0.17853 | 123.4268 | 61.0474 | -0.32959 | 123.4497 | -0.17853 | 61.0474 | 123.0835 | 123.4268 | -123.6694 | -123.6237
696.9219 | 123.4268 | -61.1114 | 62.2421 | -2.5512 | -0.0043672 | -0.045664 | 0.015165 | 0.033964 | -0.013325 | 0.071723 | -61.3403 | 62.4664 | -61.4594 | -61.235 | 62.0956 | 0.10529 | -0.12817 | 0.19226 | 62.3474 | -61.3998 | -0.3479 | 0.22431 | -0.22888 | -0.1236 | -0.14648 | -0.28839 | 0.10529 | 0.11902 | 60.9833 | 61.3037 | 123.2071 | 123.5779 | -0.22888 | 123.4589 | 61.2167 | -0.28839 | 123.5779 | -0.22888 | 61.2167 | 123.2071 | 123.4589 | -123.7015 | -123.642
697.9844 | 123.436 | -61.0657 | 62.2559 | -1.834 | -0.0097082 | -0.040324 | 0.010892 | 0.035032 | -0.014393 | 0.059974 | -61.3495 | 62.4069 | -61.496 | -61.235 | 62.1002 | 0.09613 | -0.13733 | 0.18768 | 62.3611 | -61.3815 | -0.4303 | 0.15106 | -0.28381 | -0.16937 | -0.15564 | -0.31586 | 0.10529 | 0.14648 | 60.9283 | 61.2534 | 123.1659 | 123.4726 | -0.28381 | 123.4268 | 61.1618 | -0.31586 | 123.4726 | -0.28381 | 61.1618 | 123.1659 | 123.4268 | -123.7518 | -123.6374
698.9219 | 123.4634 | -61.0657 | 62.265 | -0.41494 | -0.011844 | -0.04246 | 0.00021117 | 0.052121 | -0.020801 | 0.061042 | -61.2259 | 62.4115 | -61.4182 | -61.29 | 62.0728 | 0.064087 | -0.10071 | 0.13275 | 62.3703 | -61.3815 | -0.35248 | 0.14648 | -0.16022 | -0.2243 | -0.19226 | -0.31586 | 0.10529 | 0.19226 | 60.965 | 61.1984 | 123.1384 | 123.4772 | -0.16022 | 123.436 | 61.1298 | -0.31586 | 123.4772 | -0.16022 | 61.1298 | 123.1384 | 123.436 | -123.6832 | -123.6465
699.9844 | 123.5046 | -61.0611 | 62.2742 | -0.47597 | -0.0075722 | -0.038187 | 0.0076882 | 0.047849 | -0.0090524 | 0.065314 | -61.2671 | 62.4481 | -61.4639 | -61.2396 | 62.1048 | 0.091553 | -0.15106 | 0.20142 | 62.3657 | -61.3495 | -0.40283 | 0.17395 | -0.20599 | -0.17853 | -0.16937 | -0.28839 | 0.091553 | 0.19684 | 60.91 | 61.2625 | 123.1659 | 123.5092 | -0.20599 | 123.4268 | 61.1526 | -0.28839 | 123.5092 | -0.20599 | 61.1526 | 123.1659 | 123.4268 | -123.7381 | -123.6237
700.9219 | 123.4314 | -61.0794 | 62.2696 | -0.36916 | -0.015048 | -0.018961 | 0.0034162 | 0.046781 | -0.017597 | 0.065314 | -61.0245 | 62.4802 | -61.4182 | -61.2167 | 62.146 | 0.07782 | -0.16022 | 0.21057 | 62.352 | -61.3541 | -0.33874 | 0.21057 | 0.054932 | -0.13733 | -0.1236 | -0.27466 | 0.082398 | 0.39368 | 60.9192 | 61.29 | 123.2254 | 123.5596 | 0.054932 | 123.4314 | 61.1572 | -0.27466 | 123.5596 | 0.054932 | 61.1572 | 123.2254 | 123.4314 | -123.6877 | -123.6237
701.9219 | 123.4634 | -61.084 | 62.2421 | -0.33864 | -0.0065042 | -0.023234 | 0.017301 | 0.043577 | -0.012257 | 0.072791 | -61.235 | 62.4573 | -61.4456 | -61.2625 | 62.0773 | 0.073242 | -0.11902 | 0.17395 | 62.3703 | -61.3632 | -0.36163 | 0.21515 | -0.15106 | -0.17853 | -0.16479 | -0.27924 | 0.12817 | 0.21057 | 60.965 | 61.2579 | 123.1613 | 123.5413 | -0.15106 | 123.4543 | 61.1572 | -0.27924 | 123.5413 | -0.15106 | 61.1572 | 123.1613 | 123.4543 | -123.6877 | -123.6053
702.9844 | 123.4772 | -61.084 | 62.2467 | -0.063984 | 0.00097275 | -0.037119 | 0.017301 | 0.047849 | -0.012257 | 0.064246 | -61.1801 | 62.4481 | -61.4548 | -61.2762 | 62.0682 | 0.041199 | -0.09613 | 0.1236 | 62.3383 | -61.377 | -0.37079 | 0.20142 | -0.096131 | -0.19226 | -0.17853 | -0.29297 | 0.091553 | 0.27466 | 60.9879 | 61.2076 | 123.1522 | 123.5321 | -0.096131 | 123.4222 | 61.1252 | -0.29297 | 123.5321 | -0.096131 | 61.1252 | 123.1522 | 123.4222 | -123.7015 | -123.6237
703.9219 | 123.4177 | -61.084 | 62.2375 | -0.32338 | -0.0065042 | -0.041392 | 0.0023482 | 0.040372 | -0.019733 | 0.063178 | -61.2671 | 62.439 | -61.4273 | -61.2442 | 62.1094 | 0.091553 | -0.13275 | 0.19226 | 62.3428 | -61.3724 | -0.34332 | 0.20142 | -0.18311 | -0.16022 | -0.12817 | -0.28839 | 0.10529 | 0.16022 | 60.9512 | 61.2762 | 123.1934 | 123.5229 | -0.18311 | 123.4268 | 61.1755 | -0.28839 | 123.5229 | -0.18311 | 61.1755 | 123.1934 | 123.4268 | -123.6649 | -123.6099
704.9844 | 123.4589 | -61.0703 | 62.233 | -0.26235 | -0.011844 | -0.031779 | 0.010892 | 0.052121 | -0.011188 | 0.063178 | -61.2122 | 62.471 | -61.4319 | -61.2625 | 62.0544 | 0.050354 | -0.082397 | 0.13733 | 62.3428 | -61.4044 | -0.36163 | 0.23804 | -0.14191 | -0.19226 | -0.17853 | -0.33417 | 0.10986 | 0.21973 | 60.9879 | 61.2076 | 123.1247 | 123.5413 | -0.14191 | 123.4131 | 61.1206 | -0.33417 | 123.5413 | -0.14191 | 61.1206 | 123.1247 | 123.4131 | -123.6649 | -123.6374
705.9219 | 123.4909 | -61.116 | 62.2147 | -0.20131 | -0.0054352 | -0.045664 | 0.0055522 | 0.044645 | -0.0069164 | 0.071723 | -61.1893 | 62.4435 | -61.4548 | -61.2762 | 62.0682 | 0.027466 | -0.068665 | 0.11444 | 62.3566 | -61.409 | -0.33875 | 0.22888 | -0.073242 | -0.16022 | -0.14648 | -0.29297 | 0.14191 | 0.2655 | 61.0474 | 61.2305 | 123.1842 | 123.5596 | -0.073242 | 123.4726 | 61.1435 | -0.29297 | 123.5596 | -0.073242 | 61.1435 | 123.1842 | 123.4726 | -123.6694 | -123.6237
706.9844 | 123.4451 | -61.0794 | 62.2467 | -0.36916 | -0.0065042 | -0.034983 | 0.0055522 | 0.042508 | -0.026142 | 0.061042 | -61.2579 | 62.3978 | -61.4594 | -61.2076 | 62.0956 | 0.059509 | -0.12817 | 0.19226 | 62.3657 | -61.3815 | -0.37994 | 0.15106 | -0.17853 | -0.12817 | -0.15106 | -0.30212 | 0.11902 | 0.20142 | 60.9512 | 61.2717 | 123.175 | 123.4772 | -0.17853 | 123.4451 | 61.1389 | -0.30212 | 123.4772 | -0.17853 | 61.1389 | 123.175 | 123.4451 | -123.7061 | -123.6282
707.9219 | 123.4589 | -61.0474 | 62.2604 | -0.38442 | -0.020389 | -0.041392 | -0.0040608 | 0.04144 | -0.020801 | 0.072791 | -61.1984 | 62.3749 | -61.4136 | -61.3266 | 62.0407 | 0.027466 | -0.07782 | 0.12817 | 62.3611 | -61.3861 | -0.36621 | 0.11444 | -0.15106 | -0.27924 | -0.21973 | -0.33875 | 0.10071 | 0.21515 | 60.9695 | 61.1755 | 123.0881 | 123.4222 | -0.15106 | 123.4085 | 61.0748 | -0.33875 | 123.4222 | -0.15106 | 61.0748 | 123.0881 | 123.4085 | -123.674 | -123.6465
708.9844 | 123.5779 | -61.0565 | 62.2375 | -0.094502 | -0.012912 | -0.052073 | -0.0072648 | 0.0361 | -0.032551 | 0.070655 | -61.2305 | 62.3566 | -61.4136 | -61.409 | 61.9858 | -0.068665 | 0.009155 | 0.041199 | 62.3978 | -61.3907 | -0.35705 | 0.11902 | -0.17395 | -0.35248 | -0.25177 | -0.33417 | 0.16022 | 0.1831 | 61.0657 | 61.0977 | 123.0423 | 123.4131 | -0.17395 | 123.4543 | 60.9879 | -0.33417 | 123.4131 | -0.17395 | 60.9879 | 123.0423 | 123.4543 | -123.6511 | -123.6282
709.9219 | 123.4726 | -61.084 | 62.2467 | -0.44545 | -0.0097082 | -0.027506 | 0.014097 | 0.0361 | -0.022938 | 0.05677 | -61.235 | 62.4298 | -61.4639 | -61.2396 | 62.0773 | 0.068665 | -0.1236 | 0.15106 | 62.3474 | -61.3861 | -0.37994 | 0.18311 | -0.15106 | -0.15564 | -0.16937 | -0.30212 | 0.10071 | 0.22888 | 60.9604 | 61.235 | 123.1613 | 123.5138 | -0.15106 | 123.4314 | 61.1526 | -0.30212 | 123.5138 | -0.15106 | 61.1526 | 123.1613 | 123.4314 | -123.7106 | -123.6328
710.9844 | 123.5275 | -61.0291 | 62.2513 | -0.32338 | -0.022525 | -0.031779 | -0.0040608 | 0.024351 | -0.028278 | 0.063178 | -61.1801 | 62.3657 | -61.4044 | -61.4182 | 61.9583 | -0.073242 | 0.004578 | 0.022888 | 62.3978 | -61.3998 | -0.37537 | 0.11444 | -0.15106 | -0.3891 | -0.29297 | -0.37079 | 0.14648 | 0.2243 | 61.0336 | 61.0519 | 122.9874 | 123.3948 | -0.15106 | 123.4268 | 60.9558 | -0.37079 | 123.3948 | -0.15106 | 60.9558 | 122.9874 | 123.4268 | -123.6557 | -123.6511
711.9219 | 123.468 | -61.0565 | 62.2421 | -0.41494 | -0.018253 | -0.044596 | -0.0083338 | 0.043577 | -0.019733 | 0.071723 | -61.1984 | 62.4115 | -61.4044 | -61.3266 | 62.0178 | 0.009155 | -0.073242 | 0.10986 | 62.3703 | -61.3953 | -0.3479 | 0.16937 | -0.14191 | -0.27008 | -0.2243 | -0.33874 | 0.12817 | 0.20599 | 60.9833 | 61.1664 | 123.0743 | 123.468 | -0.14191 | 123.4268 | 61.0657 | -0.33874 | 123.468 | -0.14191 | 61.0657 | 123.0743 | 123.4268 | -123.6465 | -123.6374
712.9844 | 123.4863 | -61.0703 | 62.2238 | -0.12502 | 0.0063138 | -0.022166 | 0.010892 | 0.040372 | -0.017597 | 0.073859 | -61.1801 | 62.4344 | -61.441 | -61.2625 | 62.0682 | 0.022888 | -0.082397 | 0.10986 | 62.3428 | -61.3907 | -0.37079 | 0.21057 | -0.10986 | -0.19226 | -0.15564 | -0.32044 | 0.11902 | 0.26093 | 60.9879 | 61.1801 | 123.1384 | 123.5046 | -0.10986 | 123.4131 | 61.0931 | -0.32044 | 123.5046 | -0.10986 | 61.0931 | 123.1384 | 123.4131 | -123.6649 | -123.6145
713.9219 | 123.5413 | -61.0519 | 62.2009 | -0.44545 | -0.020389 | -0.021098 | -0.0072648 | 0.035032 | -0.02721 | 0.068519 | -61.171 | 62.3657 | -61.4319 | -61.4136 | 61.9675 | -0.073242 | 0.027466 | 0.013733 | 62.4023 | -61.3953 | -0.37994 | 0.1648 | -0.11902 | -0.36163 | -0.23346 | -0.34332 | 0.20142 | 0.26093 | 61.0794 | 61.0657 | 123.0194 | 123.4177 | -0.11902 | 123.4543 | 60.9787 | -0.34332 | 123.4177 | -0.11902 | 60.9787 | 123.0194 | 123.4543 | -123.6328 | -123.5962
714.9844 | 123.4634 | -61.0748 | 62.2696 | -0.50649 | -0.011844 | -0.043528 | 0.00021117 | 0.028623 | -0.024006 | 0.071723 | -61.2396 | 62.4069 | -61.4365 | -61.29 | 62.0224 | 0.050354 | -0.091553 | 0.19226 | 62.3932 | -61.3632 | -0.36163 | 0.13733 | -0.16479 | -0.21515 | -0.24719 | -0.28839 | 0.1236 | 0.19684 | 60.9833 | 61.2671 | 123.0972 | 123.4818 | -0.16479 | 123.468 | 61.1252 | -0.28839 | 123.4818 | -0.16479 | 61.1252 | 123.0972 | 123.468 | -123.7061 | -123.6328
715.9219 | 123.4818 | -61.0657 | 62.2284 | -0.32338 | -0.015048 | -0.039256 | 0.016233 | 0.043577 | -0.01012 | 0.064246 | -61.2305 | 62.439 | -61.4548 | -61.2579 | 62.0728 | 0.022888 | -0.11444 | 0.12817 | 62.352 | -61.3724 | -0.3891 | 0.21057 | -0.16479 | -0.19226 | -0.15564 | -0.3067 | 0.1236 | 0.2243 | 60.9512 | 61.1938 | 123.1384 | 123.5046 | -0.16479 | 123.4177 | 61.0886 | -0.3067 | 123.5046 | -0.16479 | 61.0886 | 123.1384 | 123.4177 | -123.6832 | -123.6008
716.9844 | 123.4818 | -61.0565 | 62.2284 | 0.073345 | -0.02573 | -0.065958 | -0.00085683 | 0.0361 | -0.02721 | 0.065314 | -61.2717 | 62.3566 | -61.4365 | -61.377 | 62.0087 | -0.064087 | -0.11444 | 0.059509 | 62.3566 | -61.3815 | -0.37994 | 0.12817 | -0.21515 | -0.32043 | -0.21973 | -0.32501 | 0.12817 | 0.16479 | 60.9421 | 61.116 | 123.0652 | 123.4131 | -0.21515 | 123.4131 | 60.9924 | -0.32501 | 123.4131 | -0.21515 | 60.9924 | 123.0652 | 123.4131 | -123.6649 | -123.6099
717.9219 | 123.4726 | -61.084 | 62.2833 | -0.44545 | -0.016117 | -0.052073 | 0.017301 | 0.04144 | -0.029346 | 0.059974 | -61.2213 | 62.4115 | -61.441 | -61.2671 | 62.0728 | 0.032043 | -0.10986 | 0.1236 | 62.3611 | -61.3449 | -0.35706 | 0.12817 | -0.13733 | -0.18311 | -0.21057 | -0.26093 | 0.07782 | 0.21973 | 60.9741 | 61.2076 | 123.1567 | 123.4955 | -0.13733 | 123.4451 | 61.116 | -0.26093 | 123.4955 | -0.13733 | 61.116 | 123.1567 | 123.4451 | -123.7244 | -123.6282
718.9844 | 123.4543 | -61.0794 | 62.2101 | 0.01231 | -0.0032992 | -0.04246 | 0.016233 | 0.048917 | -0.0090524 | 0.06211 | -61.1801 | 62.4481 | -61.4182 | -61.1984 | 62.027 | -0.027466 | -0.091553 | 0.07782 | 62.3108 | -61.3953 | -0.33874 | 0.23804 | -0.10071 | -0.11902 | -0.1831 | -0.31586 | 0.10071 | 0.23804 | 60.9879 | 61.1572 | 123.1064 | 123.5275 | -0.10071 | 123.3902 | 61.0519 | -0.31586 | 123.5275 | -0.10071 | 61.0519 | 123.1064 | 123.3902 | -123.6282 | -123.6053
719.9219 | 123.5321 | -61.0703 | 62.2101 | 0.058086 | -0.023593 | -0.048869 | -0.01047 | 0.025419 | -0.029346 | 0.067451 | -61.2488 | 62.3474 | -61.441 | -61.3953 | 62.0132 | -0.082397 | -0.036621 | 0.032043 | 62.3703 | -61.3907 | -0.37079 | 0.13733 | -0.17853 | -0.32501 | -0.19684 | -0.32044 | 0.16022 | 0.19226 | 61.0336 | 61.1023 | 123.0835 | 123.4177 | -0.17853 | 123.4406 | 60.9879 | -0.32044 | 123.4177 | -0.17853 | 60.9879 | 123.0835 | 123.4406 | -123.6511 | -123.6008
720.9844 | 123.4772 | -61.0886 | 62.2467 | -0.23183 | 0.0041778 | -0.0478 | 0.018369 | 0.037168 | -0.0069164 | 0.058906 | -61.1801 | 62.471 | -61.4227 | -61.2534 | 62.0453 | -0.013733 | -0.10529 | 0.091553 | 62.3657 | -61.3861 | -0.33417 | 0.2243 | -0.091553 | -0.16479 | -0.20142 | -0.29755 | 0.11902 | 0.24261 | 60.9833 | 61.1801 | 123.1338 | 123.5596 | -0.091553 | 123.4543 | 61.0748 | -0.29755 | 123.5596 | -0.091553 | 61.0748 | 123.1338 | 123.4543 | -123.6694 | -123.6328
721.9219 | 123.5138 | -61.0291 | 62.2421 | 1.645 | -0.019321 | -0.054209 | 0.00021117 | 0.043577 | -0.024006 | 0.067451 | -61.1389 | 62.3566 | -61.4182 | -61.3815 | 61.9995 | -0.082397 | -0.022888 | 0.018311 | 62.3978 | -61.409 | -0.3891 | 0.11444 | -0.10986 | -0.35248 | -0.24261 | -0.37994 | 0.15564 | 0.27924 | 61.0062 | 61.0474 | 123.0286 | 123.3856 | -0.10986 | 123.4268 | 60.9467 | -0.37994 | 123.3856 | -0.10986 | 60.9467 | 123.0286 | 123.4268 | -123.6603 | -123.6511
722.9844 | 123.5504 | -61.084 | 62.2009 | -0.1708 | -0.016117 | -0.057413 | -0.01047 | 0.0361 | -0.036823 | 0.05677 | -61.2122 | 62.3795 | -61.4319 | -61.4044 | 61.972 | -0.10071 | -0.036621 | -0.009155 | 62.3566 | -61.4182 | -0.3479 | 0.17853 | -0.12817 | -0.32043 | -0.22888 | -0.33417 | 0.15564 | 0.21973 | 61.0474 | 61.0748 | 123.056 | 123.4634 | -0.12817 | 123.4406 | 60.9833 | -0.33417 | 123.4634 | -0.12817 | 60.9833 | 123.056 | 123.4406 | -123.6328 | -123.6191
723.9219 | 123.4406 | -61.0977 | 62.2467 | -1.01 | -0.0086402 | -0.056345 | 0.0034162 | 0.035032 | -0.028278 | 0.059974 | -61.2076 | 62.4435 | -61.4365 | -61.2259 | 62.1002 | 0.036621 | -0.16022 | 0.13733 | 62.3474 | -61.3724 | -0.33874 | 0.19684 | -0.10986 | -0.12817 | -0.14648 | -0.27466 | 0.10071 | 0.22888 | 60.9375 | 61.235 | 123.1979 | 123.5413 | -0.10986 | 123.4451 | 61.1343 | -0.27466 | 123.5413 | -0.10986 | 61.1343 | 123.1979 | 123.4451 | -123.6832 | -123.6191
724.9844 | 123.5916 | -61.0886 | 62.2055 | 0.11912 | -0.021457 | -0.046732 | -0.011538 | 0.026487 | -0.025074 | 0.066383 | -61.2534 | 62.3383 | -61.4273 | -61.3632 | 62.027 | -0.054932 | -0.086975 | 0.045776 | 62.3566 | -61.377 | -0.33874 | 0.13275 | -0.16479 | -0.27466 | -0.17853 | -0.28839 | 0.15106 | 0.17395 | 61.0016 | 61.1343 | 123.1155 | 123.4268 | -0.16479 | 123.4451 | 61.0336 | -0.28839 | 123.4268 | -0.16479 | 61.0336 | 123.1155 | 123.4451 | -123.6328 | -123.5825
725.9219 | 123.4726 | -61.0428 | 62.2696 | -0.44545 | -0.01398 | -0.045664 | 0.0076882 | 0.04144 | -0.019733 | 0.055701 | -61.203 | 62.3978 | -61.4319 | -61.2625 | 62.0636 | 0.009155 | -0.13275 | 0.10986 | 62.3474 | -61.3678 | -0.3891 | 0.12817 | -0.16022 | -0.21973 | -0.20599 | -0.32501 | 0.07782 | 0.22888 | 60.91 | 61.1526 | 123.1064 | 123.4406 | -0.16022 | 123.3902 | 61.0519 | -0.32501 | 123.4406 | -0.16022 | 61.0519 | 123.1064 | 123.3902 | -123.7015 | -123.6374
726.9844 | 123.5367 | -61.0474 | 62.265 | -0.21657 | -0.028934 | -0.049937 | 0.0066202 | 0.030759 | -0.029346 | 0.063178 | -61.1618 | 62.3749 | -61.4044 | -61.3724 | 61.9949 | -0.10071 | -0.032043 | 0.004578 | 62.3566 | -61.3861 | -0.35706 | 0.10986 | -0.11444 | -0.32501 | -0.27008 | -0.33875 | 0.091552 | 0.24262 | 61.0153 | 61.0519 | 123.0423 | 123.4222 | -0.11444 | 123.4039 | 60.9467 | -0.33875 | 123.4222 | -0.11444 | 60.9467 | 123.0423 | 123.4039 | -123.6694 | -123.6511
727.9219 | 123.5596 | -61.0291 | 62.2375 | -0.1708 | -0.011844 | -0.037119 | -0.0019248 | 0.033964 | -0.041096 | 0.073859 | -61.1801 | 62.3383 | -61.4227 | -61.409 | 61.9629 | -0.14191 | 0.004578 | -0.041199 | 62.4023 | -61.4136 | -0.39368 | 0.10071 | -0.15106 | -0.37994 | -0.27466 | -0.38452 | 0.16479 | 0.24261 | 61.0336 | 60.9879 | 122.9919 | 123.3673 | -0.15106 | 123.4314 | 60.8871 | -0.38452 | 123.3673 | -0.15106 | 60.8871 | 122.9919 | 123.4314 | -123.6603 | -123.6511
728.9844 | 123.555 | -61.0565 | 62.233 | 0.088604 | -0.020389 | -0.0478 | 0.014097 | 0.028623 | -0.033619 | 0.052497 | -61.2488 | 62.352 | -61.4319 | -61.3632 | 62.0499 | -0.086975 | -0.032043 | 0.036621 | 62.3886 | -61.3861 | -0.37537 | 0.11902 | -0.19226 | -0.3067 | -0.1831 | -0.32959 | 0.15564 | 0.18311 | 61.0245 | 61.0931 | 123.1064 | 123.4085 | -0.19226 | 123.4451 | 60.9695 | -0.32959 | 123.4085 | -0.19226 | 60.9695 | 123.1064 | 123.4451 | -123.6649 | -123.6191
729.9219 | 123.4726 | -61.0199 | 62.2696 | -0.33864 | -0.023593 | -0.041392 | 0.0076882 | 0.027555 | -0.030414 | 0.067451 | -61.171 | 62.3566 | -61.4319 | -61.3953 | 62.0041 | -0.10529 | -0.027466 | -0.036621 | 62.3795 | -61.3724 | -0.41199 | 0.086975 | -0.15106 | -0.37537 | -0.2655 | -0.35248 | 0.10986 | 0.26093 | 60.9924 | 60.9833 | 123.024 | 123.3765 | -0.15106 | 123.3994 | 60.9146 | -0.35248 | 123.3765 | -0.15106 | 60.9146 | 123.024 | 123.3994 | -123.7015 | -123.642
730.9219 | 123.4772 | -61.0748 | 62.2604 | -0.048725 | -0.0086402 | -0.034983 | 0.015165 | 0.023282 | -0.0015754 | 0.077064 | -61.1801 | 62.4298 | -61.441 | -61.2579 | 62.0865 | -0.041199 | -0.17395 | 0.086975 | 62.3566 | -61.3632 | -0.36621 | 0.16937 | -0.10529 | -0.18311 | -0.17395 | -0.28839 | 0.09613 | 0.26093 | 60.9009 | 61.1618 | 123.1613 | 123.5046 | -0.10529 | 123.4314 | 61.0336 | -0.28839 | 123.5046 | -0.10529 | 61.0336 | 123.1613 | 123.4314 | -123.7015 | -123.6237
731.9844 | 123.4634 | -61.0336 | 62.2604 | -0.44545 | -0.011844 | -0.040324 | -0.0094018 | 0.031827 | -0.033619 | 0.071723 | -61.1755 | 62.3703 | -61.377 | -61.3724 | 61.9812 | -0.1236 | -0.013733 | -0.045776 | 62.3886 | -61.3953 | -0.34332 | 0.10986 | -0.14191 | -0.33874 | -0.27924 | -0.36163 | 0.12817 | 0.20142 | 61.0199 | 60.9879 | 123.0148 | 123.4039 | -0.14191 | 123.4222 | 60.91 | -0.36163 | 123.4039 | -0.14191 | 60.91 | 123.0148 | 123.4222 | -123.6374 | -123.6557
732.9219 | 123.5596 | -61.0474 | 62.2238 | -0.15554 | -0.019321 | -0.061686 | 0.0012792 | 0.01901 | -0.042164 | 0.064246 | -61.2213 | 62.352 | -61.4319 | -61.377 | 61.9858 | -0.11902 | -0.050354 | -0.018311 | 62.3703 | -61.3907 | -0.38452 | 0.12817 | -0.17395 | -0.32959 | -0.23804 | -0.34332 | 0.14648 | 0.21057 | 60.997 | 61.0291 | 123.0331 | 123.3994 | -0.17395 | 123.4177 | 60.9283 | -0.34332 | 123.3994 | -0.17395 | 60.9283 | 123.0331 | 123.4177 | -123.6557 | -123.6145
733.9844 | 123.5321 | -61.0611 | 62.2192 | 0.13438 | -0.020389 | -0.032847 | -0.0040608 | 0.027555 | -0.02721 | 0.06211 | -61.2579 | 62.3566 | -61.441 | -61.3449 | 62.0224 | -0.086975 | -0.09613 | 0.013733 | 62.352 | -61.377 | -0.37994 | 0.13733 | -0.19684 | -0.28381 | -0.19684 | -0.31586 | 0.13275 | 0.1831 | 60.965 | 61.0748 | 123.0835 | 123.4177 | -0.19684 | 123.4131 | 60.9741 | -0.31586 | 123.4177 | -0.19684 | 60.9741 | 123.0835 | 123.4131 | -123.6603 | -123.5962
734.9219 | 123.4772 | -61.0519 | 62.2421 | -0.36916 | -0.016117 | -0.041392 | 0.0066202 | 0.035032 | -0.030414 | 0.064246 | -61.1984 | 62.3795 | -61.4273 | -61.2991 | 62.0178 | -0.064087 | -0.10071 | 0.013733 | 62.3657 | -61.3632 | -0.37537 | 0.13733 | -0.14648 | -0.24719 | -0.2243 | -0.31128 | 0.1236 | 0.22888 | 60.9512 | 61.0657 | 123.0698 | 123.4314 | -0.14648 | 123.4177 | 60.9879 | -0.31128 | 123.4314 | -0.14648 | 60.9879 | 123.0698 | 123.4177 | -123.6694 | -123.6053
735.9844 | 123.5413 | -61.0336 | 62.2238 | -0.094502 | -0.021457 | -0.06489 | 0.0066202 | 0.028623 | -0.02721 | 0.065314 | -61.2305 | 62.3337 | -61.4319 | -61.3815 | 61.9949 | -0.11902 | -0.068665 | -0.032043 | 62.384 | -61.3907 | -0.39825 | 0.10986 | -0.19684 | -0.3479 | -0.22888 | -0.35706 | 0.16022 | 0.20142 | 60.965 | 61.0016 | 123.0286 | 123.3673 | -0.19684 | 123.4177 | 60.9146 | -0.35706 | 123.3673 | -0.19684 | 60.9146 | 123.0286 | 123.4177 | -123.6557 | -123.6145
736.9219 | 123.5779 | -61.0291 | 62.265 | -0.36916 | -0.01398 | -0.055277 | 0.0034162 | 0.027555 | -0.028278 | 0.074928 | -61.1847 | 62.352 | -61.3953 | -61.3724 | 61.9675 | -0.13275 | -0.022888 | -0.045776 | 62.3749 | -61.3907 | -0.36621 | 0.086975 | -0.15564 | -0.34332 | -0.29755 | -0.36163 | 0.10986 | 0.21057 | 61.0062 | 60.9833 | 122.9965 | 123.381 | -0.15564 | 123.4039 | 60.8963 | -0.36163 | 123.381 | -0.15564 | 60.8963 | 122.9965 | 123.4039 | -123.6603 | -123.6557
737.9844 | 123.5184 | -61.0565 | 62.1826 | -0.56752 | -0.0086402 | -0.051005 | 0.011961 | 0.024351 | -0.018665 | 0.059974 | -61.1893 | 62.3657 | -61.3998 | -61.377 | 61.9766 | -0.15106 | -0.027466 | -0.064087 | 62.3566 | -61.3907 | -0.34332 | 0.18311 | -0.13275 | -0.32043 | -0.20599 | -0.33417 | 0.17395 | 0.21057 | 61.0291 | 60.9924 | 123.0331 | 123.4222 | -0.13275 | 123.4131 | 60.9055 | -0.33417 | 123.4222 | -0.13275 | 60.9055 | 123.0331 | 123.4131 | -123.5825 | -123.5733
738.9219 | 123.4634 | -61.0703 | 62.2421 | -0.46071 | -0.0043672 | -0.049937 | 0.014097 | 0.027555 | -0.029346 | 0.066383 | -61.2076 | 62.4023 | -61.4319 | -61.2671 | 62.0682 | -0.045776 | -0.14648 | 0.059509 | 62.3566 | -61.3449 | -0.36163 | 0.16022 | -0.13733 | -0.19684 | -0.17395 | -0.27466 | 0.11444 | 0.2243 | 60.9238 | 61.1298 | 123.1384 | 123.4726 | -0.13733 | 123.4268 | 61.0245 | -0.27466 | 123.4726 | -0.13733 | 61.0245 | 123.1384 | 123.4268 | -123.674 | -123.587
739.9844 | 123.4772 | -61.0657 | 62.265 | -0.46071 | -0.020389 | -0.051005 | 0.02371 | 0.025419 | -0.02187 | 0.068519 | -61.2076 | 62.4252 | -61.4227 | -61.2579 | 62.0773 | -0.022888 | -0.16022 | 0.036621 | 62.3795 | -61.3678 | -0.35705 | 0.16022 | -0.14191 | -0.19226 | -0.18768 | -0.30212 | 0.11444 | 0.21515 | 60.9055 | 61.1023 | 123.143 | 123.4909 | -0.14191 | 123.4451 | 61.0428 | -0.30212 | 123.4909 | -0.14191 | 61.0428 | 123.143 | 123.4451 | -123.6877 | -123.6328
740.9219 | 123.4497 | -61.0657 | 62.2787 | -0.33864 | -0.011844 | -0.052073 | 0.033323 | 0.033964 | -0.028278 | 0.070655 | -61.2579 | 62.4252 | -61.4594 | -61.1664 | 62.1231 | -0.013733 | -0.19684 | 0.10529 | 62.3383 | -61.3266 | -0.39368 | 0.14648 | -0.19226 | -0.10071 | -0.15564 | -0.26093 | 0.059509 | 0.20142 | 60.8688 | 61.171 | 123.1888 | 123.4909 | -0.19226 | 123.4039 | 61.0519 | -0.26093 | 123.4909 | -0.19226 | 61.0519 | 123.1888 | 123.4039 | -123.7381 | -123.6053
741.9844 | 123.5825 | -61.0107 | 62.2192 | -0.18605 | -0.028934 | -0.071299 | -0.01047 | 0.037168 | -0.036823 | 0.067451 | -61.171 | 62.352 | -61.4273 | -61.3495 | 61.972 | -0.15106 | -0.013733 | -0.086975 | 62.3932 | -61.3953 | -0.41656 | 0.13275 | -0.16022 | -0.33875 | -0.24719 | -0.38452 | 0.17395 | 0.25635 | 60.997 | 60.9238 | 122.9828 | 123.3627 | -0.16022 | 123.4039 | 60.8597 | -0.38452 | 123.3627 | -0.16022 | 60.8597 | 122.9828 | 123.4039 | -123.6465 | -123.6145
742.9219 | 123.5413 | -61.0336 | 62.2192 | -0.64382 | -0.018253 | -0.051005 | 0.0044842 | 0.035032 | -0.031483 | 0.068519 | -61.1984 | 62.3383 | -61.4273 | -61.3724 | 61.9858 | -0.12817 | -0.064087 | -0.050354 | 62.3886 | -61.3495 | -0.39368 | 0.11902 | -0.16479 | -0.33874 | -0.23346 | -0.31586 | 0.16937 | 0.22888 | 60.9695 | 60.9833 | 123.0194 | 123.3719 | -0.16479 | 123.4222 | 60.9055 | -0.31586 | 123.3719 | -0.16479 | 60.9055 | 123.0194 | 123.4222 | -123.6465 | -123.5687
743.9844 | 123.5458 | -61.0657 | 62.1826 | 0.47007 | -0.012912 | -0.067027 | 0.011961 | 0.014737 | -0.02721 | 0.066383 | -61.1755 | 62.3566 | -61.409 | -61.3449 | 61.9125 | -0.16022 | -0.041199 | -0.12817 | 62.3474 | -61.3953 | -0.34332 | 0.17395 | -0.10986 | -0.27924 | -0.27008 | -0.32959 | 0.16479 | 0.23346 | 61.0245 | 60.9375 | 122.9782 | 123.4222 | -0.10986 | 123.4131 | 60.9055 | -0.32959 | 123.4222 | -0.10986 | 60.9055 | 122.9782 | 123.4131 | -123.5916 | -123.5779
744.9219 | 123.4497 | -61.0519 | 62.2833 | -0.38442 | -0.024662 | -0.06489 | 0.017301 | 0.040372 | -0.017597 | 0.065314 | -61.0428 | 62.4573 | -61.4227 | -61.171 | 62.1735 | -0.022888 | -0.23346 | 0.10071 | 62.3474 | -61.3403 | -0.37079 | 0.17395 | 0.009155 | -0.11902 | -0.10986 | -0.28839 | 0.064087 | 0.37994 | 60.8185 | 61.1526 | 123.2254 | 123.5092 | 0.009155 | 123.3994 | 61.0291 | -0.28839 | 123.5092 | 0.009155 | 61.0291 | 123.2254 | 123.3994 | -123.7061 | -123.6237
745.9844 | 123.4772 | -61.0565 | 62.1918 | 0.22593 | -0.0065042 | -0.048869 | -0.0061968 | 0.024351 | -0.024006 | 0.067451 | -61.2396 | 62.3383 | -61.4273 | -61.3586 | 62.0178 | -0.11902 | -0.11902 | -0.013733 | 62.3749 | -61.3449 | -0.37079 | 0.14648 | -0.1831 | -0.30212 | -0.17395 | -0.28839 | 0.18311 | 0.18768 | 60.9375 | 61.0428 | 123.0743 | 123.3948 | -0.1831 | 123.4314 | 60.9375 | -0.28839 | 123.3948 | -0.1831 | 60.9375 | 123.0743 | 123.4314 | -123.6191 | -123.5367
746.9219 | 123.5733 | -61.0107 | 62.2559 | -0.23183 | -0.0043672 | -0.04246 | -0.0051288 | 0.040372 | -0.043232 | 0.066383 | -61.1572 | 62.3749 | -61.409 | -61.3953 | 61.9812 | -0.15106 | -0.050354 | -0.073242 | 62.3657 | -61.377 | -0.39825 | 0.11902 | -0.14648 | -0.38452 | -0.27466 | -0.36621 | 0.10986 | 0.25177 | 60.9604 | 60.9375 | 122.9919 | 123.3856 | -0.14648 | 123.3765 | 60.8597 | -0.36621 | 123.3856 | -0.14648 | 60.8597 | 122.9919 | 123.3765 | -123.6649 | -123.6328
747.9844 | 123.5275 | -61.0199 | 62.2696 | -1.3762 | -0.022525 | -0.034983 | 0.0023482 | 0.022214 | -0.025074 | 0.068519 | -61.235 | 62.3566 | -61.4182 | -61.3586 | 62.0087 | -0.11444 | -0.086975 | -0.059509 | 62.3657 | -61.3541 | -0.39825 | 0.086975 | -0.21515 | -0.33875 | -0.26093 | -0.33417 | 0.096131 | 0.18311 | 60.9329 | 60.9604 | 123.0286 | 123.3765 | -0.21515 | 123.3856 | 60.9055 | -0.33417 | 123.3765 | -0.21515 | 60.9055 | 123.0286 | 123.3856 | -123.6877 | -123.6237
748.9219 | 123.555 | -61.0474 | 62.2284 | 0.073345 | -0.027866 | -0.073435 | 0.0066202 | 0.031827 | -0.031483 | 0.06211 | -61.2534 | 62.3657 | -61.441 | -61.3861 | 62.0087 | -0.16937 | -0.10986 | -0.050354 | 62.3428 | -61.3861 | -0.39368 | 0.13733 | -0.20599 | -0.33875 | -0.21973 | -0.33875 | 0.11444 | 0.18768 | 60.9375 | 60.997 | 123.056 | 123.4131 | -0.20599 | 123.3902 | 60.878 | -0.33875 | 123.4131 | -0.20599 | 60.878 | 123.056 | 123.3902 | -123.6694 | -123.6145
749.9219 | 123.5825 | -61.0519 | 62.2284 | 0.027569 | -0.0086402 | -0.052073 | 0.0076882 | 0.011533 | -0.043232 | 0.064246 | -61.1984 | 62.3657 | -61.4227 | -61.3724 | 61.9766 | -0.16022 | -0.082397 | -0.082397 | 62.3795 | -61.3815 | -0.37079 | 0.13733 | -0.14648 | -0.32043 | -0.25177 | -0.32959 | 0.15106 | 0.2243 | 60.9695 | 60.9695 | 123.0286 | 123.4177 | -0.14648 | 123.4314 | 60.8917 | -0.32959 | 123.4177 | -0.14648 | 60.8917 | 123.0286 | 123.4314 | -123.6511 | -123.6099
750.9844 | 123.5184 | -61.0336 | 62.2787 | 0.51585 | -0.017185 | -0.0478 | -0.011538 | 0.028623 | -0.02721 | 0.075996 | -61.2442 | 62.3886 | -61.4044 | -61.3632 | 62.0041 | -0.15106 | -0.12817 | -0.059509 | 62.3383 | -61.3541 | -0.37079 | 0.10986 | -0.21057 | -0.32959 | -0.27466 | -0.32043 | 0.059509 | 0.16022 | 60.9055 | 60.9741 | 123.0377 | 123.4222 | -0.21057 | 123.3719 | 60.8826 | -0.32043 | 123.4222 | -0.21057 | 60.8826 | 123.0377 | 123.3719 | -123.6832 | -123.6328
751.9219 | 123.5779 | -61.0336 | 62.2101 | -0.26235 | -0.023593 | -0.053141 | 0.010892 | 0.033964 | -0.035755 | 0.06211 | -61.1755 | 62.3795 | -61.3953 | -61.377 | 61.9812 | -0.23346 | -0.1236 | 0.14191 | 62.439 | -61.3449 | -0.36163 | 0.16937 | -0.14191 | -0.34332 | -0.22888 | -0.31128 | 0.22888 | 0.21973 | 60.91 | 61.1755 | 123.0148 | 123.4131 | -0.14191 | 123.4726 | 60.8002 | -0.31128 | 123.4131 | -0.14191 | 60.8002 | 123.0148 | 123.4726 | -123.6053 | -123.555
752.9844 | 123.4451 | -61.0611 | 62.2925 | -0.4302 | -0.015048 | -0.051005 | 0.018369 | 0.032895 | -0.034687 | 0.06211 | -61.2167 | 62.4298 | -61.4182 | -61.2167 | 62.1094 | -0.022888 | -0.2243 | 0.050354 | 62.3383 | -61.322 | -0.35706 | 0.13733 | -0.15564 | -0.15564 | -0.1831 | -0.26093 | 0.045777 | 0.20142 | 60.8368 | 61.1114 | 123.1705 | 123.4909 | -0.15564 | 123.3994 | 61.0382 | -0.26093 | 123.4909 | -0.15564 | 61.0382 | 123.1705 | 123.3994 | -123.7106 | -123.6145
753.9219 | 123.5046 | -61.0245 | 62.2421 | 0.13438 | -0.01398 | -0.022166 | -0.0061968 | 0.030759 | -0.036823 | 0.051429 | -61.235 | 62.3474 | -61.4044 | -61.3174 | 62.0544 | -0.15106 | -0.13275 | -0.009155 | 62.3886 | -61.3861 | -0.37994 | 0.10529 | -0.21057 | -0.29297 | -0.18768 | -0.36163 | 0.14648 | 0.16937 | 60.8917 | 61.0153 | 123.0789 | 123.3719 | -0.21057 | 123.4131 | 60.8734 | -0.36163 | 123.3719 | -0.21057 | 60.8734 | 123.0789 | 123.4131 | -123.6465 | -123.6282
754.9219 | 123.5321 | -61.0428 | 62.2238 | 0.1649 | -0.016117 | -0.049937 | 0.00021117 | 0.028623 | -0.024006 | 0.064246 | -61.2396 | 62.3611 | -61.4136 | -61.3495 | 62.0178 | -0.17395 | -0.13733 | -0.082397 | 62.3199 | -61.3815 | -0.37079 | 0.13733 | -0.19684 | -0.3067 | -0.20599 | -0.33875 | 0.09613 | 0.17395 | 60.9055 | 60.9604 | 123.0606 | 123.4039 | -0.19684 | 123.3627 | 60.8688 | -0.33875 | 123.4039 | -0.19684 | 60.8688 | 123.0606 | 123.3627 | -123.6374 | -123.6053
755.9844 | 123.5733 | -61.0519 | 62.2147 | 0.79051 | -0.015048 | -0.029642 | 0.0066202 | 0.023282 | -0.017597 | 0.058906 | -61.0291 | 62.3703 | -61.4136 | -61.3358 | 61.9583 | -0.23804 | -0.10071 | -0.11444 | 62.3566 | -61.3953 | -0.36163 | 0.15564 | 0.022888 | -0.28381 | -0.25635 | -0.34332 | 0.14191 | 0.38452 | 60.9512 | 60.9375 | 123.0103 | 123.4222 | 0.022888 | 123.4085 | 60.8139 | -0.34332 | 123.4222 | 0.022888 | 60.8139 | 123.0103 | 123.4085 | -123.6282 | -123.6099
756.9219 | 123.4863 | -61.0474 | 62.2238 | 0.058086 | -0.0043672 | -0.045664 | 0.0066202 | 0.035032 | -0.028278 | 0.057838 | -61.235 | 62.3795 | -61.4227 | -61.3174 | 62.0316 | -0.14648 | -0.16022 | -0.059509 | 62.3291 | -61.3678 | -0.37537 | 0.15564 | -0.18768 | -0.27008 | -0.19226 | -0.32044 | 0.10529 | 0.18768 | 60.8871 | 60.9879 | 123.0789 | 123.4268 | -0.18768 | 123.3765 | 60.9009 | -0.32044 | 123.4268 | -0.18768 | 60.9009 | 123.0789 | 123.3765 | -123.6465 | -123.5916
757.9844 | 123.5367 | -61.0382 | 62.2147 | 0.042827 | -0.016117 | -0.063822 | -0.0029928 | 0.028623 | -0.022938 | 0.068519 | -61.2259 | 62.3795 | -61.3907 | -61.3678 | 61.9995 | -0.17853 | -0.11444 | -0.07782 | 62.3611 | -61.4044 | -0.35248 | 0.16479 | -0.18768 | -0.32959 | -0.21515 | -0.36621 | 0.14648 | 0.1648 | 60.9238 | 60.9604 | 123.0377 | 123.4177 | -0.18768 | 123.3994 | 60.8597 | -0.36621 | 123.4177 | -0.18768 | 60.8597 | 123.0377 | 123.3994 | -123.6053 | -123.6191
758.9219 | 123.4818 | -61.0474 | 62.2192 | 0.25645 | -0.0086402 | -0.040324 | 0.010892 | 0.033964 | -0.031483 | 0.067451 | -61.2213 | 62.3703 | -61.4227 | -61.3312 | 62.0407 | -0.17395 | -0.16937 | -0.064087 | 62.3474 | -61.4044 | -0.37537 | 0.15106 | -0.17395 | -0.28381 | -0.17853 | -0.35706 | 0.12817 | 0.20142 | 60.878 | 60.9833 | 123.0881 | 123.4177 | -0.17395 | 123.3948 | 60.8734 | -0.35706 | 123.4177 | -0.17395 | 60.8734 | 123.0881 | 123.3948 | -123.642 | -123.6237
759.9844 | 123.5092 | -61.0336 | 62.2192 | 0.28697 | -0.0097082 | -0.052073 | 0.0044842 | 0.025419 | -0.030414 | 0.052497 | -61.235 | 62.352 | -61.4136 | -61.3129 | 62.0178 | -0.18768 | -0.16937 | -0.068665 | 62.3474 | -61.3861 | -0.37994 | 0.13275 | -0.20142 | -0.27924 | -0.20142 | -0.35248 | 0.12817 | 0.17853 | 60.8643 | 60.965 | 123.0515 | 123.3856 | -0.20142 | 123.381 | 60.8459 | -0.35248 | 123.3856 | -0.20142 | 60.8459 | 123.0515 | 123.381 | -123.6328 | -123.6053
760.9219 | 123.5184 | -61.0428 | 62.2009 | 0.71421 | -0.016117 | -0.031779 | 0.0044842 | 0.014737 | -0.020801 | 0.051429 | -61.2579 | 62.3566 | -61.4502 | -61.322 | 62.0453 | -0.16479 | -0.16937 | -0.073242 | 62.352 | -61.3815 | -0.40741 | 0.15564 | -0.21515 | -0.27923 | -0.15564 | -0.33875 | 0.15106 | 0.19226 | 60.8734 | 60.9695 | 123.0881 | 123.3994 | -0.21515 | 123.3948 | 60.878 | -0.33875 | 123.3994 | -0.21515 | 60.878 | 123.0881 | 123.3948 | -123.6511 | -123.5825
761.9844 | 123.4634 | -61.0748 | 62.2467 | -0.21657 | 0.0041778 | -0.041392 | 0.026914 | 0.032895 | -0.0047804 | 0.064246 | -61.1755 | 62.4573 | -61.4182 | -61.1938 | 62.1094 | -0.1236 | -0.23804 | -0.004578 | 62.3337 | -61.3724 | -0.34332 | 0.21057 | -0.10071 | -0.11902 | -0.13733 | -0.29755 | 0.086975 | 0.24262 | 60.8368 | 61.0703 | 123.1842 | 123.5321 | -0.10071 | 123.4085 | 60.9512 | -0.29755 | 123.5321 | -0.10071 | 60.9512 | 123.1842 | 123.4085 | -123.6649 | -123.6191
762.9219 | 123.436 | -61.084 | 62.2787 | -0.24709 | -0.021457 | -0.04246 | 0.033323 | 0.043577 | -0.0090524 | 0.064246 | -61.2213 | 62.4939 | -61.4502 | -61.203 | 62.1048 | -0.07782 | -0.28381 | 0.018311 | 62.3566 | -61.3403 | -0.36621 | 0.21515 | -0.13733 | -0.11902 | -0.17395 | -0.25635 | 0.077819 | 0.22888 | 60.8002 | 61.1023 | 123.1888 | 123.5779 | -0.13733 | 123.4406 | 61.0062 | -0.25635 | 123.5779 | -0.13733 | 61.0062 | 123.1888 | 123.4406 | -123.7289 | -123.6191
763.9844 | 123.4268 | -61.0931 | 62.2513 | 0.22593 | -0.0043672 | -0.033915 | 0.017301 | 0.042508 | -0.0090524 | 0.065314 | -61.2305 | 62.5031 | -61.4456 | -61.1618 | 62.1643 | -0.073242 | -0.28381 | 0.022888 | 62.3062 | -61.3495 | -0.35248 | 0.25177 | -0.13733 | -0.068664 | -0.086975 | -0.25635 | 0.054931 | 0.21515 | 60.8093 | 61.116 | 123.2574 | 123.5962 | -0.13733 | 123.3994 | 61.0199 | -0.25635 | 123.5962 | -0.13733 | 61.0199 | 123.2574 | 123.3994 | -123.6969 | -123.6008
764.9219 | 123.5458 | -61.0474 | 62.2101 | 0.57688 | -0.017185 | -0.0093484 | 0.0044842 | 0.039304 | -0.019733 | 0.071723 | -61.1526 | 62.3886 | -61.4136 | -61.3998 | 62.0224 | -0.25177 | -0.14191 | -0.11902 | 62.384 | -61.3861 | -0.36621 | 0.17853 | -0.10529 | -0.35248 | -0.18768 | -0.33875 | 0.17395 | 0.26093 | 60.9055 | 60.9283 | 123.0698 | 123.436 | -0.10529 | 123.4314 | 60.7956 | -0.33875 | 123.436 | -0.10529 | 60.7956 | 123.0698 | 123.4314 | -123.6237 | -123.5962
765.9844 | 123.4772 | -61.0657 | 62.2009 | 0.4243 | -0.0075722 | -0.039256 | 0.013029 | 0.030759 | -0.0079844 | 0.070655 | -61.235 | 62.4481 | -61.4822 | -61.2762 | 62.0728 | -0.17395 | -0.21515 | -0.064087 | 62.3291 | -61.3953 | -0.41656 | 0.24719 | -0.16937 | -0.21057 | -0.12817 | -0.32959 | 0.12817 | 0.24719 | 60.8505 | 61.0016 | 123.1384 | 123.5138 | -0.16937 | 123.3948 | 60.8917 | -0.32959 | 123.5138 | -0.16937 | 60.8917 | 123.1384 | 123.3948 | -123.6832 | -123.5962
766.9219 | 123.5092 | -61.0245 | 62.1918 | 0.27171 | -0.0054352 | -0.020029 | 0.010892 | 0.038236 | -0.018665 | 0.073859 | -61.1984 | 62.3886 | -61.4182 | -61.377 | 62.0087 | -0.23346 | -0.16022 | -0.14648 | 62.3566 | -61.4044 | -0.39368 | 0.19684 | -0.17395 | -0.35248 | -0.1831 | -0.37994 | 0.16479 | 0.21973 | 60.8643 | 60.878 | 123.0331 | 123.4131 | -0.17395 | 123.381 | 60.791 | -0.37994 | 123.4131 | -0.17395 | 60.791 | 123.0331 | 123.381 | -123.6099 | -123.5962
767.9844 | 123.4863 | -61.0519 | 62.2192 | 0.24119 | -0.020389 | -0.033915 | 0.0044842 | 0.035032 | -0.016529 | 0.066383 | -61.2213 | 62.384 | -61.4182 | -61.3266 | 62.0544 | -0.2243 | -0.21973 | -0.09613 | 62.3566 | -61.3724 | -0.36621 | 0.1648 | -0.16937 | -0.27466 | -0.16479 | -0.32043 | 0.13733 | 0.19684 | 60.8322 | 60.9558 | 123.1064 | 123.436 | -0.16937 | 123.4085 | 60.8276 | -0.32043 | 123.436 | -0.16937 | 60.8276 | 123.1064 | 123.4085 | -123.6374 | -123.5916
768.9219 | 123.5641 | -61.0474 | 62.1964 | 0.37852 | 0.0041778 | -0.041392 | 0.0098242 | 0.024351 | -0.0058484 | 0.065314 | -61.171 | 62.3978 | -61.4136 | -61.409 | 62.2055 | -0.20599 | -0.18768 | -0.11902 | 62.3932 | -61.3861 | -0.36621 | 0.20142 | -0.1236 | -0.36163 | 0.009155 | -0.33875 | 0.19684 | 0.24261 | 60.8597 | 60.9283 | 123.2529 | 123.4451 | -0.1236 | 123.4406 | 60.8414 | -0.33875 | 123.4451 | -0.1236 | 60.8414 | 123.2529 | 123.4406 | -123.6099 | -123.5825
769.9844 | 123.468 | -61.084 | 62.2375 | 0.348 | 0.0063138 | -0.030711 | 0.021574 | 0.039304 | -0.0079844 | 0.064246 | -61.2305 | 62.471 | -61.4319 | -61.2488 | 62.0911 | -0.16937 | -0.2655 | -0.059509 | 62.3383 | -61.3678 | -0.3479 | 0.23346 | -0.14648 | -0.16479 | -0.14648 | -0.28381 | 0.10071 | 0.20142 | 60.8185 | 61.0245 | 123.175 | 123.555 | -0.14648 | 123.4222 | 60.9146 | -0.28381 | 123.555 | -0.14648 | 60.9146 | 123.175 | 123.4222 | -123.6694 | -123.6053
770.9219 | 123.5413 | -61.0474 | 62.233 | 0.13438 | -0.026798 | -0.030711 | 0.0044842 | 0.038236 | -0.024006 | 0.071723 | -61.2396 | 62.3795 | -61.4273 | -61.3358 | 62.0544 | -0.20142 | -0.22888 | -0.09613 | 62.3795 | -61.3632 | -0.37994 | 0.14648 | -0.19226 | -0.28839 | -0.17853 | -0.31586 | 0.14648 | 0.18768 | 60.8185 | 60.9512 | 123.1018 | 123.4268 | -0.19226 | 123.4268 | 60.8459 | -0.31586 | 123.4268 | -0.19226 | 60.8459 | 123.1018 | 123.4268 | -123.6603 | -123.5962
771.9844 | 123.4543 | -61.0565 | 62.2421 | -0.033467 | 0.0020408 | -0.039256 | 0.016233 | 0.030759 | -0.017597 | 0.082404 | -61.1664 | 62.5214 | -61.4319 | -61.2167 | 62.0316 | -0.16022 | -0.23804 | -0.09613 | 62.3245 | -61.3907 | -0.37537 | 0.27924 | -0.10986 | -0.16022 | -0.21057 | -0.33417 | 0.082398 | 0.2655 | 60.8185 | 60.9604 | 123.0881 | 123.5779 | -0.10986 | 123.381 | 60.8963 | -0.33417 | 123.5779 | -0.10986 | 60.8963 | 123.0881 | 123.381 | -123.674 | -123.6328
772.9219 | 123.4177 | -61.0474 | 62.2696 | -1.0558 | 0.0052458 | -0.039256 | 0.019437 | 0.043577 | -0.015461 | 0.069587 | -61.2534 | 62.4802 | -61.4319 | -61.2213 | 62.114 | -0.10071 | -0.32959 | -0.013733 | 62.3657 | -61.3449 | -0.38452 | 0.21057 | -0.20599 | -0.17395 | -0.15564 | -0.29755 | 0.096131 | 0.17853 | 60.7178 | 61.0336 | 123.1613 | 123.5275 | -0.20599 | 123.4131 | 60.9467 | -0.29755 | 123.5275 | -0.20599 | 60.9467 | 123.1613 | 123.4131 | -123.7015 | -123.6145
773.9844 | 123.4909 | -61.0336 | 62.2696 | -0.32338 | -0.0011632 | -0.037119 | 0.015165 | 0.043577 | -0.013325 | 0.057838 | -61.1893 | 62.5122 | -61.4227 | -61.2305 | 62.1094 | -0.13275 | -0.29297 | -0.041199 | 62.3749 | -61.3266 | -0.3891 | 0.24261 | -0.15564 | -0.19684 | -0.16022 | -0.29297 | 0.10529 | 0.23346 | 60.7407 | 60.9924 | 123.143 | 123.5458 | -0.15564 | 123.4085 | 60.9009 | -0.29297 | 123.5458 | -0.15564 | 60.9009 | 123.143 | 123.4085 | -123.6923 | -123.5962
774.9219 | 123.4863 | -61.0657 | 62.2192 | 0.4243 | -0.0086402 | -0.029642 | 0.015165 | 0.038236 | -0.017597 | 0.059974 | -61.2305 | 62.471 | -61.4639 | -61.2717 | 62.0956 | -0.20142 | -0.28381 | -0.09613 | 62.352 | -61.3815 | -0.39825 | 0.25177 | -0.16479 | -0.20599 | -0.1236 | -0.31586 | 0.13275 | 0.23346 | 60.7819 | 60.9695 | 123.1613 | 123.5367 | -0.16479 | 123.4177 | 60.8643 | -0.31586 | 123.5367 | -0.16479 | 60.8643 | 123.1613 | 123.4177 | -123.6832 | -123.6008
775.9844 | 123.5321 | -61.0336 | 62.2192 | 0.37852 | -0.019321 | -0.048869 | -0.0061968 | 0.037168 | -0.024006 | 0.075996 | -61.2122 | 62.3611 | -61.4548 | -61.3632 | 62.0636 | -0.24719 | -0.21973 | -0.1236 | 62.3795 | -61.3586 | -0.42114 | 0.14191 | -0.17853 | -0.32959 | -0.15564 | -0.32501 | 0.16022 | 0.24262 | 60.8139 | 60.91 | 123.0972 | 123.3948 | -0.17853 | 123.4131 | 60.7864 | -0.32501 | 123.3948 | -0.17853 | 60.7864 | 123.0972 | 123.4131 | -123.674 | -123.5779
776.9219 | 123.4589 | -61.0794 | 62.233 | 1.4924 | 0.0073818 | -0.034983 | 0.018369 | 0.04144 | -0.011188 | 0.058906 | -61.1755 | 62.4756 | -61.4319 | -61.2259 | 62.1231 | -0.17853 | -0.33875 | -0.045776 | 62.352 | -61.3541 | -0.35248 | 0.24262 | -0.09613 | -0.14648 | -0.10986 | -0.27466 | 0.11902 | 0.25635 | 60.7407 | 61.0336 | 123.2025 | 123.555 | -0.09613 | 123.4314 | 60.9009 | -0.27466 | 123.555 | -0.09613 | 60.9009 | 123.2025 | 123.4314 | -123.6649 | -123.587
777.9219 | 123.5138 | -61.0657 | 62.2192 | 0.48533 | -0.0022312 | -0.028574 | 0.010892 | 0.04144 | -0.0037124 | 0.066383 | -61.2122 | 62.4435 | -61.441 | -61.29 | 62.0499 | -0.25177 | -0.2655 | -0.1236 | 62.3611 | -61.4044 | -0.37537 | 0.2243 | -0.14648 | -0.2243 | -0.16937 | -0.33874 | 0.14191 | 0.22888 | 60.8002 | 60.9421 | 123.1155 | 123.5092 | -0.14648 | 123.4268 | 60.8139 | -0.33874 | 123.5092 | -0.14648 | 60.8139 | 123.1155 | 123.4268 | -123.6603 | -123.6237
778.9844 | 123.3902 | -61.0565 | 62.2696 | 0.19541 | 0.0031088 | -0.011485 | 0.014097 | 0.040372 | -0.0058484 | 0.066383 | -61.2625 | 62.4985 | -61.4319 | -61.1618 | 62.1735 | -0.16479 | -0.37079 | -0.027466 | 62.352 | -61.3861 | -0.37537 | 0.22888 | -0.20599 | -0.10528 | -0.09613 | -0.32959 | 0.082398 | 0.16937 | 60.6857 | 61.0291 | 123.23 | 123.555 | -0.20599 | 123.4085 | 60.8917 | -0.32959 | 123.555 | -0.20599 | 60.8917 | 123.23 | 123.4085 | -123.7015 | -123.6557
779.9219 | 123.4451 | -61.0703 | 62.2467 | 0.43956 | 0.0063138 | -0.048869 | 0.0044842 | 0.039304 | -0.014393 | 0.06211 | -61.2305 | 62.4939 | -61.4502 | -61.2534 | 62.0956 | -0.2243 | -0.32959 | -0.082397 | 62.3291 | -61.3632 | -0.37994 | 0.24719 | -0.16022 | -0.18311 | -0.15106 | -0.29297 | 0.082398 | 0.21973 | 60.7407 | 60.9879 | 123.1659 | 123.5641 | -0.16022 | 123.3994 | 60.8459 | -0.29297 | 123.5641 | -0.16022 | 60.8459 | 123.1659 | 123.3994 | -123.6969 | -123.6099
780.9844 | 123.5458 | -61.0153 | 62.2284 | 0.073345 | -0.0022312 | -0.030711 | 0.0066202 | 0.039304 | -0.0047804 | 0.067451 | -61.1618 | 62.4756 | -61.4044 | -61.3586 | 61.9995 | -0.31586 | -0.20599 | -0.19226 | 62.3657 | -61.3998 | -0.3891 | 0.24719 | -0.14648 | -0.34332 | -0.22888 | -0.38452 | 0.13733 | 0.24262 | 60.8093 | 60.8231 | 123.0148 | 123.4909 | -0.14648 | 123.381 | 60.6995 | -0.38452 | 123.4909 | -0.14648 | 60.6995 | 123.0148 | 123.381 | -123.6328 | -123.6282
781.9219 | 123.3902 | -61.0748 | 62.2375 | 0.24119 | 0.0084498 | -0.034983 | 0.016233 | 0.042508 | -0.014393 | 0.055701 | -61.2625 | 62.5259 | -61.4365 | -61.171 | 62.1597 | -0.17853 | -0.39368 | -0.036621 | 62.352 | -61.3358 | -0.36163 | 0.28839 | -0.18768 | -0.09613 | -0.07782 | -0.26093 | 0.11444 | 0.17395 | 60.6812 | 61.0382 | 123.2346 | 123.6008 | -0.18768 | 123.4268 | 60.8963 | -0.26093 | 123.6008 | -0.18768 | 60.8963 | 123.2346 | 123.4268 | -123.674 | -123.5733
782.9844 | 123.4726 | -61.0474 | 62.2696 | -0.15554 | -0.0043672 | -0.039256 | 0.018369 | 0.039304 | -0.0079844 | 0.050361 | -61.1664 | 62.4802 | -61.409 | -61.235 | 62.0911 | -0.20599 | -0.32959 | -0.10529 | 62.3932 | -61.3403 | -0.36163 | 0.21057 | -0.11902 | -0.18768 | -0.17853 | -0.29297 | 0.1236 | 0.24262 | 60.7178 | 60.9421 | 123.1384 | 123.5275 | -0.11902 | 123.4406 | 60.8414 | -0.29297 | 123.5275 | -0.11902 | 60.8414 | 123.1384 | 123.4406 | -123.6786 | -123.6099
783.9219 | 123.4177 | -61.0611 | 62.2742 | 0.30223 | 0.0041778 | -0.05955 | 0.0076882 | 0.038236 | -0.0037124 | 0.053565 | -61.2579 | 62.5076 | -61.4365 | -61.2625 | 62.1002 | -0.18768 | -0.3891 | -0.09613 | 62.3566 | -61.3632 | -0.37537 | 0.23346 | -0.19684 | -0.20142 | -0.17395 | -0.30212 | 0.082397 | 0.17853 | 60.672 | 60.965 | 123.1613 | 123.5687 | -0.19684 | 123.4177 | 60.8734 | -0.30212 | 123.5687 | -0.19684 | 60.8734 | 123.1613 | 123.4177 | -123.7106 | -123.6374
784.9844 | 123.4497 | -61.0519 | 62.2513 | -0.048725 | -0.0022312 | -0.016825 | 0.0098242 | 0.01901 | -0.0015754 | 0.054633 | -61.1664 | 62.5214 | -61.4227 | -61.2488 | 62.1277 | -0.27008 | -0.32959 | -0.068665 | 62.384 | -61.3724 | -0.37079 | 0.27008 | -0.11444 | -0.19684 | -0.1236 | -0.32043 | 0.13275 | 0.25635 | 60.7224 | 60.9833 | 123.1796 | 123.5733 | -0.11444 | 123.436 | 60.7819 | -0.32043 | 123.5733 | -0.11444 | 60.7819 | 123.1796 | 123.436 | -123.674 | -123.6237
785.9219 | 123.5641 | -61.0382 | 62.2192 | 0.48533 | -0.0054352 | -0.044596 | -0.00085683 | 0.037168 | -0.014393 | 0.068519 | -61.1755 | 62.4619 | -61.4136 | -61.2991 | 62.0819 | -0.38452 | -0.32959 | -0.21057 | 62.3566 | -61.3907 | -0.37537 | 0.24262 | -0.13733 | -0.26093 | -0.13733 | -0.35248 | 0.13733 | 0.23804 | 60.7086 | 60.8276 | 123.1201 | 123.5001 | -0.13733 | 123.3948 | 60.6537 | -0.35248 | 123.5001 | -0.13733 | 60.6537 | 123.1201 | 123.3948 | -123.6328 | -123.6099
786.9844 | 123.4909 | -61.0382 | 62.2879 | -0.1708 | -0.0022312 | -0.02537 | 0.011961 | 0.037168 | -0.015461 | 0.068519 | -61.1664 | 62.5168 | -61.409 | -61.2213 | 62.114 | -0.23346 | -0.36163 | -0.10529 | 62.4023 | -61.3541 | -0.37079 | 0.22888 | -0.12817 | -0.18311 | -0.17395 | -0.31586 | 0.11444 | 0.24262 | 60.6766 | 60.9329 | 123.1522 | 123.555 | -0.12817 | 123.4406 | 60.8047 | -0.31586 | 123.555 | -0.12817 | 60.8047 | 123.1522 | 123.4406 | -123.6969 | -123.642
787.9219 | 123.4314 | -61.0703 | 62.265 | 0.25645 | 0.0052458 | -0.020029 | 0.018369 | 0.051053 | -0.0090524 | 0.06211 | -61.2671 | 62.4985 | -61.4273 | -61.2076 | 62.1506 | -0.2243 | -0.42572 | -0.054932 | 62.352 | -61.3495 | -0.35706 | 0.23346 | -0.19684 | -0.13733 | -0.11444 | -0.27924 | 0.086975 | 0.16022 | 60.6445 | 61.0153 | 123.2208 | 123.5687 | -0.19684 | 123.4222 | 60.8459 | -0.27924 | 123.5687 | -0.19684 | 60.8459 | 123.2208 | 123.4222 | -123.6923 | -123.6145
788.9844 | 123.5275 | -61.0657 | 62.2238 | 0.4243 | -0.0022312 | -0.040324 | 0.011961 | 0.037168 | 0.00056063 | 0.064246 | -61.1755 | 62.4664 | -61.4227 | -61.322 | 62.0407 | -0.33417 | -0.31128 | -0.19226 | 62.384 | -61.3998 | -0.35705 | 0.24262 | -0.10986 | -0.25635 | -0.18311 | -0.33417 | 0.16022 | 0.24719 | 60.7544 | 60.8734 | 123.1064 | 123.5321 | -0.10986 | 123.4497 | 60.7315 | -0.33417 | 123.5321 | -0.10986 | 60.7315 | 123.1064 | 123.4497 | -123.6465 | -123.6237
789.9219 | 123.4451 | -61.0382 | 62.2604 | 0.36326 | 0.0041778 | -0.029642 | 0.015165 | 0.042508 | -0.011188 | 0.06211 | -61.1801 | 62.4893 | -61.4456 | -61.2396 | 62.1826 | -0.27924 | -0.46234 | -0.045776 | 62.3795 | -61.3403 | -0.40741 | 0.22888 | -0.14191 | -0.20142 | -0.07782 | -0.30212 | 0.11902 | 0.2655 | 60.5759 | 60.9924 | 123.2208 | 123.5275 | -0.14191 | 123.4177 | 60.759 | -0.30212 | 123.5275 | -0.14191 | 60.759 | 123.2208 | 123.4177 | -123.7061 | -123.6008
790.9844 | 123.4314 | -61.0657 | 62.2604 | 0.18016 | -0.010776 | -0.023234 | 0.016233 | 0.045713 | -0.00050737 | 0.069587 | -61.2534 | 62.5122 | -61.4456 | -61.171 | 62.1735 | -0.23804 | -0.43488 | -0.091553 | 62.3566 | -61.3586 | -0.37994 | 0.25177 | -0.18768 | -0.10529 | -0.086975 | -0.29297 | 0.09613 | 0.19226 | 60.6308 | 60.9741 | 123.2391 | 123.5779 | -0.18768 | 123.4222 | 60.8276 | -0.29297 | 123.5779 | -0.18768 | 60.8276 | 123.2391 | 123.4222 | -123.7061 | -123.6191
791.9219 | 123.4818 | -61.0565 | 62.2375 | 0.30223 | 0.011654 | -0.049937 | 0.0012792 | 0.040372 | -0.0047804 | 0.061042 | -61.2213 | 62.5168 | -61.4182 | -61.2305 | 62.1185 | -0.29755 | -0.39368 | -0.14648 | 62.384 | -61.3815 | -0.36163 | 0.27924 | -0.16479 | -0.17395 | -0.11902 | -0.32501 | 0.14648 | 0.19684 | 60.6628 | 60.91 | 123.175 | 123.5733 | -0.16479 | 123.4406 | 60.759 | -0.32501 | 123.5733 | -0.16479 | 60.759 | 123.175 | 123.4406 | -123.6557 | -123.6191
792.9219 | 123.4634 | -61.0336 | 62.2467 | 0.25645 | 0.0031088 | -0.045664 | 0.0076882 | 0.037168 | 0.00056063 | 0.057838 | -61.2488 | 62.4893 | -61.4365 | -61.2213 | 62.1048 | -0.29297 | -0.42114 | -0.13275 | 62.3657 | -61.3586 | -0.40283 | 0.24262 | -0.21515 | -0.18768 | -0.14191 | -0.32501 | 0.11902 | 0.18768 | 60.6125 | 60.9009 | 123.1384 | 123.5229 | -0.21515 | 123.3994 | 60.7407 | -0.32501 | 123.5229 | -0.21515 | 60.7407 | 123.1384 | 123.3994 | -123.6832 | -123.6053
793.9844 | 123.4406 | -61.0382 | 62.2833 | 0.058086 | -0.0032992 | -0.039256 | 0.010892 | 0.039304 | -0.013325 | 0.068519 | -61.2076 | 62.5214 | -61.4182 | -61.1984 | 62.1185 | -0.22888 | -0.47607 | -0.091553 | 62.4161 | -61.3358 | -0.37994 | 0.23804 | -0.16937 | -0.16022 | -0.16479 | -0.29755 | 0.13275 | 0.21057 | 60.5621 | 60.9467 | 123.1567 | 123.5596 | -0.16937 | 123.4543 | 60.8093 | -0.29755 | 123.5596 | -0.16937 | 60.8093 | 123.1567 | 123.4543 | -123.7015 | -123.6191
794.9219 | 123.4222 | -61.0245 | 62.2971 | 0.4243 | 0.0020408 | -0.02537 | 0.011961 | 0.043577 | 0.00056063 | 0.067451 | -61.2305 | 62.5305 | -61.4365 | -61.171 | 62.1735 | -0.26093 | -0.48065 | -0.10071 | 62.384 | -61.3632 | -0.41199 | 0.23346 | -0.20599 | -0.14648 | -0.1236 | -0.33874 | 0.086975 | 0.20599 | 60.5438 | 60.9238 | 123.1979 | 123.555 | -0.20599 | 123.4085 | 60.7636 | -0.33874 | 123.555 | -0.20599 | 60.7636 | 123.1979 | 123.4085 | -123.7335 | -123.6603
795.9844 | 123.4634 | -61.0199 | 62.2833 | 0.6837 | -0.0086402 | -0.017893 | 0.016233 | 0.051053 | 0.0026966 | 0.069587 | -61.1069 | 62.5122 | -61.4273 | -61.2076 | 62.1368 | -0.28839 | -0.41657 | -0.15106 | 62.4207 | -61.3815 | -0.40741 | 0.22888 | -0.086976 | -0.18768 | -0.14648 | -0.36163 | 0.13733 | 0.32043 | 60.6033 | 60.8688 | 123.1567 | 123.5321 | -0.086976 | 123.4406 | 60.7315 | -0.36163 | 123.5321 | -0.086976 | 60.7315 | 123.1567 | 123.4406 | -123.7106 | -123.6649
796.9219 | 123.4131 | -61.0382 | 62.2833 | 0.4243 | -0.0011632 | -0.039256 | 0.036527 | 0.031827 | -0.020801 | 0.057838 | -61.2442 | 62.5259 | -61.4273 | -60.9924 | 62.1597 | -0.31128 | -0.44861 | -0.10986 | 62.4023 | -61.3678 | -0.3891 | 0.24262 | -0.20599 | 0.045776 | -0.1236 | -0.32959 | 0.11902 | 0.1831 | 60.5896 | 60.9283 | 123.1979 | 123.5641 | -0.20599 | 123.4406 | 60.7269 | -0.32959 | 123.5641 | -0.20599 | 60.7269 | 123.1979 | 123.4406 | -123.7106 | -123.6511
797.9844 | 123.5046 | -61.0107 | 62.2467 | 0.48533 | -0.0043672 | -0.020029 | 0.0012792 | 0.045713 | 0.00056063 | 0.054633 | -61.1938 | 62.4939 | -61.4273 | -61.2717 | 62.0911 | -0.37079 | -0.41199 | -0.21057 | 62.4115 | -61.3541 | -0.41656 | 0.24719 | -0.18311 | -0.26093 | -0.15564 | -0.34332 | 0.16479 | 0.23346 | 60.5988 | 60.8002 | 123.1018 | 123.5046 | -0.18311 | 123.4222 | 60.64 | -0.34332 | 123.5046 | -0.18311 | 60.64 | 123.1018 | 123.4222 | -123.674 | -123.6008
798.9219 | 123.4314 | -61.0428 | 62.2375 | 0.43956 | -0.0043672 | -0.026438 | 0.0087562 | 0.035032 | -0.0037124 | 0.066383 | -61.2122 | 62.5122 | -61.4456 | -61.2213 | 62.1277 | -0.32959 | -0.45776 | -0.16479 | 62.3795 | -61.3632 | -0.40283 | 0.27466 | -0.16937 | -0.17853 | -0.10986 | -0.32043 | 0.14191 | 0.23346 | 60.585 | 60.878 | 123.1705 | 123.555 | -0.16937 | 123.4222 | 60.7132 | -0.32043 | 123.555 | -0.16937 | 60.7132 | 123.1705 | 123.4222 | -123.6832 | -123.6008
799.9844 | 123.4818 | -61.0245 | 62.2925 | -0.033467 | -0.0022312 | -0.021098 | 0.015165 | 0.046781 | -0.0026434 | 0.059974 | -61.1389 | 62.5168 | -61.3953 | -61.2076 | 62.114 | -0.32044 | -0.44403 | -0.17853 | 62.4207 | -61.3495 | -0.37079 | 0.22431 | -0.11444 | -0.18311 | -0.17853 | -0.32501 | 0.12817 | 0.25635 | 60.5804 | 60.8459 | 123.1384 | 123.5413 | -0.11444 | 123.4451 | 60.704 | -0.32501 | 123.5413 | -0.11444 | 60.704 | 123.1384 | 123.4451 | -123.6877 | -123.642
800.9219 | 123.4497 | -61.0611 | 62.2833 | 0.39378 | 0.010586 | -0.010416 | 0.0044842 | 0.04144 | -0.013325 | 0.068519 | -61.5097 | 62.4573 | -61.4548 | -61.2396 | 62.1597 | -0.28381 | -0.48523 | -0.16937 | 62.3932 | -61.3403 | -0.39368 | 0.17395 | -0.44861 | -0.17853 | -0.1236 | -0.27924 | 0.10986 | -0.054932 | 60.5759 | 60.8917 | 123.2208 | 123.5184 | -0.44861 | 123.4543 | 60.7773 | -0.27924 | 123.5184 | -0.44861 | 60.7773 | 123.2208 | 123.4543 | -123.7381 | -123.6237
801.9844 | 123.3856 | -61.0428 | 62.2833 | 0.1649 | -0.0032992 | -0.018961 | 0.010892 | 0.039304 | -0.00050737 | 0.072791 | -61.2305 | 62.5442 | -61.4273 | -61.1481 | 62.1735 | -0.31128 | -0.52185 | -0.15106 | 62.3932 | -61.3586 | -0.38452 | 0.26093 | -0.18768 | -0.10529 | -0.10986 | -0.31586 | 0.10986 | 0.19684 | 60.5209 | 60.8917 | 123.2162 | 123.587 | -0.18768 | 123.436 | 60.7315 | -0.31586 | 123.587 | -0.18768 | 60.7315 | 123.2162 | 123.436 | -123.7106 | -123.642
802.9219 | 123.4131 | -61.0336 | 62.2284 | 0.37852 | 0.00097275 | -0.049937 | 0.0076882 | 0.052121 | 0.00056063 | 0.070655 | -61.2213 | 62.5305 | -61.4456 | -61.1893 | 62.1597 | -0.33417 | -0.53101 | -0.13275 | 62.3932 | -61.3403 | -0.41199 | 0.30212 | -0.18768 | -0.15564 | -0.068665 | -0.3067 | 0.16479 | 0.22431 | 60.5026 | 60.9009 | 123.1934 | 123.5641 | -0.18768 | 123.4268 | 60.6995 | -0.3067 | 123.5641 | -0.18768 | 60.6995 | 123.1934 | 123.4268 | -123.674 | -123.5687
803.9844 | 123.4589 | -61.0245 | 62.2787 | 0.348 | -0.0075722 | -0.031779 | 0.011961 | 0.04144 | -0.018665 | 0.069587 | -61.1984 | 62.5214 | -61.4273 | -61.2167 | 62.1414 | -0.36163 | -0.48981 | -0.19684 | 62.4115 | -61.3449 | -0.40283 | 0.24261 | -0.17395 | -0.19226 | -0.13733 | -0.32043 | 0.13275 | 0.22888 | 60.5347 | 60.8276 | 123.1659 | 123.5458 | -0.17395 | 123.436 | 60.6628 | -0.32043 | 123.5458 | -0.17395 | 60.6628 | 123.1659 | 123.436 | -123.7061 | -123.6237
804.9219 | 123.4131 | -61.0428 | 62.2833 | 0.10386 | -0.0032992 | -0.033915 | 0.0044842 | 0.051053 | -0.0079844 | 0.054633 | -61.2305 | 62.558 | -61.441 | -61.1618 | 62.1826 | -0.3067 | -0.55847 | -0.13275 | 62.4023 | -61.3495 | -0.39825 | 0.27466 | -0.18768 | -0.11902 | -0.10071 | -0.3067 | 0.11902 | 0.21057 | 60.4843 | 60.91 | 123.2254 | 123.6008 | -0.18768 | 123.4451 | 60.7361 | -0.3067 | 123.6008 | -0.18768 | 60.7361 | 123.2254 | 123.4451 | -123.7244 | -123.6328
805.9844 | 123.4039 | -61.0382 | 62.2925 | 0.30223 | -0.012912 | -0.015757 | 0.0098242 | 0.048917 | -0.0047804 | 0.059974 | -61.2167 | 62.5305 | -61.4319 | -61.1481 | 62.2055 | -0.31586 | -0.58136 | -0.15106 | 62.3932 | -61.3541 | -0.39368 | 0.23804 | -0.17853 | -0.10986 | -0.086975 | -0.31586 | 0.10071 | 0.21515 | 60.4568 | 60.8871 | 123.2437 | 123.5687 | -0.17853 | 123.4314 | 60.7224 | -0.31586 | 123.5687 | -0.17853 | 60.7224 | 123.2437 | 123.4314 | -123.7244 | -123.6465
806.9219 | 123.3948 | -61.0474 | 62.2787 | 0.28697 | 0.00097275 | -0.0082804 | 0.017301 | 0.0361 | -0.0047804 | 0.06211 | -61.2259 | 62.5488 | -61.3953 | -61.171 | 62.1735 | -0.33875 | -0.56305 | -0.16937 | 62.4115 | -61.3358 | -0.3479 | 0.27008 | -0.17853 | -0.1236 | -0.10529 | -0.28839 | 0.13275 | 0.16937 | 60.4843 | 60.878 | 123.2208 | 123.5962 | -0.17853 | 123.4589 | 60.7086 | -0.28839 | 123.5962 | -0.17853 | 60.7086 | 123.2208 | 123.4589 | -123.674 | -123.6145
807.9219 | 123.3948 | -61.0382 | 62.3016 | 0.59214 | 0.0041778 | -0.043528 | 0.011961 | 0.04144 | 0.0016286 | 0.064246 | -61.1893 | 62.558 | -61.4182 | -61.1526 | 62.2055 | -0.32959 | -0.56763 | -0.16479 | 62.4161 | -61.3449 | -0.37994 | 0.25635 | -0.15106 | -0.11444 | -0.096131 | -0.3067 | 0.11444 | 0.22888 | 60.4706 | 60.8734 | 123.2437 | 123.5962 | -0.15106 | 123.4543 | 60.7086 | -0.3067 | 123.5962 | -0.15106 | 60.7086 | 123.2437 | 123.4543 | -123.7198 | -123.6465
808.9844 | 123.4726 | -60.9741 | 62.3383 | -0.38442 | -0.016117 | -0.044596 | -0.011538 | 0.043577 | -0.022938 | 0.069587 | -61.1572 | 62.5076 | -61.3586 | -61.235 | 62.1552 | -0.3479 | -0.53101 | -0.20599 | 62.439 | -61.3174 | -0.38452 | 0.16937 | -0.18311 | -0.26093 | -0.18311 | -0.34332 | 0.10071 | 0.20142 | 60.4431 | 60.7681 | 123.1293 | 123.4818 | -0.18311 | 123.4131 | 60.6262 | -0.34332 | 123.4818 | -0.18311 | 60.6262 | 123.1293 | 123.4131 | -123.6969 | -123.6557
809.9219 | 123.4222 | -61.0382 | 62.3291 | 0.18016 | 0.0073818 | -0.043528 | 0.020506 | 0.039304 | -0.012257 | 0.074928 | -61.1618 | 62.5168 | -61.3907 | -61.1526 | 62.1689 | -0.35706 | -0.55847 | -0.17853 | 62.4344 | -61.3266 | -0.35248 | 0.18768 | -0.1236 | -0.11444 | -0.16022 | -0.28839 | 0.10529 | 0.22888 | 60.4797 | 60.8597 | 123.2071 | 123.555 | -0.1236 | 123.4726 | 60.6812 | -0.28839 | 123.555 | -0.1236 | 60.6812 | 123.2071 | 123.4726 | -123.7198 | -123.6557
810.9844 | 123.4497 | -61.0016 | 62.3383 | -0.38442 | 0.0052458 | -0.0478 | 0.0076882 | 0.043577 | -0.024006 | 0.067451 | -61.1755 | 62.5351 | -61.4182 | -61.1618 | 62.2055 | -0.35248 | -0.54932 | -0.15106 | 62.4252 | -61.3129 | -0.41656 | 0.19684 | -0.17395 | -0.16022 | -0.13275 | -0.31128 | 0.086975 | 0.24262 | 60.4523 | 60.8505 | 123.2071 | 123.5367 | -0.17395 | 123.4268 | 60.6491 | -0.31128 | 123.5367 | -0.17395 | 60.6491 | 123.2071 | 123.4268 | -123.7564 | -123.6511
811.9219 | 123.4222 | -61.0153 | 62.3474 | 0.37852 | 0.010586 | -0.036051 | 0.014097 | 0.040372 | -0.011188 | 0.064246 | -61.1893 | 62.5442 | -61.3815 | -61.1755 | 62.5122 | -0.41657 | -0.64545 | -0.43488 | 62.3703 | -61.3586 | -0.36621 | 0.19684 | -0.17395 | -0.16022 | 0.16479 | -0.34332 | 0.022888 | 0.19226 | 60.3699 | 60.5804 | 123.5275 | 123.5596 | -0.17395 | 123.3856 | 60.5988 | -0.34332 | 123.5596 | -0.17395 | 60.5988 | 123.5275 | 123.3856 | -123.7289 | -123.7061
812.9844 | 123.468 | -60.997 | 62.2742 | -0.094502 | 0.00097275 | -0.024302 | 0.0087562 | 0.033964 | -0.017597 | 0.067451 | -61.1114 | 62.5305 | -61.4182 | -61.2076 | 62.1185 | -0.4303 | -0.53101 | -0.2243 | 62.4481 | -61.3266 | -0.42114 | 0.25635 | -0.11444 | -0.21057 | -0.15564 | -0.32959 | 0.17395 | 0.3067 | 60.466 | 60.7727 | 123.1155 | 123.5275 | -0.11444 | 123.4451 | 60.5667 | -0.32959 | 123.5275 | -0.11444 | 60.5667 | 123.1155 | 123.4451 | -123.6923 | -123.6008
813.9219 | 123.3856 | -61.0382 | 62.3199 | 0.22593 | 0.00097275 | -0.040324 | 0.021574 | 0.031827 | -0.014393 | 0.069587 | -61.1984 | 62.5534 | -61.4136 | -61.1481 | 62.2055 | -0.36163 | -0.6134 | -0.20142 | 62.4252 | -61.3174 | -0.37537 | 0.23346 | -0.16022 | -0.10986 | -0.11444 | -0.27924 | 0.10529 | 0.21515 | 60.4248 | 60.8368 | 123.2437 | 123.5916 | -0.16022 | 123.4634 | 60.6766 | -0.27924 | 123.5916 | -0.16022 | 60.6766 | 123.2437 | 123.4634 | -123.7335 | -123.6374
814.9844 | 123.4726 | -60.9879 | 62.3886 | -0.46071 | -9.5248e-05 | -0.061686 | 0.0012792 | 0.038236 | -0.011188 | 0.068519 | -61.1755 | 62.5488 | -61.3953 | -61.171 | 62.1872 | -0.35706 | -0.59052 | -0.18768 | 62.471 | -61.2762 | -0.40741 | 0.16022 | -0.18768 | -0.18311 | -0.20142 | -0.28839 | 0.082397 | 0.21973 | 60.3973 | 60.8002 | 123.175 | 123.5367 | -0.18768 | 123.4589 | 60.6308 | -0.28839 | 123.5367 | -0.18768 | 60.6308 | 123.175 | 123.4589 | -123.7839 | -123.6649
815.9219 | 123.4589 | -60.9787 | 62.3199 | -0.12502 | 0.0073818 | -0.030711 | 0.0044842 | 0.037168 | -0.013325 | 0.064246 | -61.1069 | 62.558 | -61.3632 | -61.2122 | 62.1414 | -0.4303 | -0.54016 | -0.25635 | 62.4481 | -61.3403 | -0.38452 | 0.23804 | -0.12817 | -0.23346 | -0.17853 | -0.36163 | 0.12817 | 0.25635 | 60.4385 | 60.7224 | 123.1201 | 123.5367 | -0.12817 | 123.4268 | 60.5484 | -0.36163 | 123.5367 | -0.12817 | 60.5484 | 123.1201 | 123.4268 | -123.6832 | -123.6603
816.9844 | 123.4222 | -60.997 | 62.3291 | 0.39378 | -0.0022312 | -0.041392 | 0.0034162 | 0.042508 | -0.0037124 | 0.069587 | -61.2213 | 62.5259 | -61.3907 | -61.1435 | 62.1964 | -0.42114 | -0.61798 | -0.20142 | 62.4115 | -61.3129 | -0.39368 | 0.19684 | -0.2243 | -0.14648 | -0.13275 | -0.31586 | 0.082397 | 0.16937 | 60.379 | 60.7956 | 123.1934 | 123.5229 | -0.2243 | 123.4085 | 60.5759 | -0.31586 | 123.5229 | -0.2243 | 60.5759 | 123.1934 | 123.4085 | -123.7198 | -123.642
817.9219 | 123.4863 | -60.9833 | 62.3062 | -0.0029495 | -0.012912 | -0.055277 | 0.016233 | 0.045713 | -0.0090524 | 0.057838 | -61.0886 | 62.5671 | -61.3678 | -61.1801 | 62.1597 | -0.44403 | -0.55389 | -0.27008 | 62.4802 | -61.2991 | -0.38452 | 0.26093 | -0.10529 | -0.19684 | -0.14648 | -0.31586 | 0.17395 | 0.27924 | 60.4294 | 60.7132 | 123.143 | 123.5504 | -0.10529 | 123.4634 | 60.5392 | -0.31586 | 123.5504 | -0.10529 | 60.5392 | 123.143 | 123.4634 | -123.674 | -123.6053
818.9219 | 123.4543 | -60.9833 | 62.3291 | -0.44545 | 0.0041778 | -0.028574 | 0.018369 | 0.052121 | -0.0069164 | 0.064246 | -61.1069 | 62.5992 | -61.3358 | -61.1435 | 62.1872 | -0.4303 | -0.57678 | -0.2655 | 62.4664 | -61.3083 | -0.35248 | 0.27008 | -0.1236 | -0.16022 | -0.14191 | -0.32501 | 0.13733 | 0.22888 | 60.4065 | 60.7178 | 123.1705 | 123.5825 | -0.1236 | 123.4497 | 60.553 | -0.32501 | 123.5825 | -0.1236 | 60.553 | 123.1705 | 123.4497 | -123.6649 | -123.6374
819.9219 | 123.4634 | -60.9787 | 62.3611 | -0.10976 | 0.0041778 | -0.029642 | 0.0034162 | 0.062803 | -0.0069164 | 0.069587 | -61.0931 | 62.5763 | -61.3815 | -61.203 | 62.1414 | -0.43945 | -0.59052 | -0.29297 | 62.471 | -61.3129 | -0.40283 | 0.21515 | -0.11444 | -0.2243 | -0.21973 | -0.33417 | 0.10986 | 0.28839 | 60.3882 | 60.6857 | 123.1201 | 123.555 | -0.11444 | 123.4497 | 60.5392 | -0.33417 | 123.555 | -0.11444 | 60.5392 | 123.1201 | 123.4497 | -123.7427 | -123.674
820.9219 | 123.4406 | -60.9558 | 62.3703 | 0.11912 | 0.00097275 | -0.045664 | 0.011961 | 0.048917 | -0.0069164 | 0.067451 | -61.0977 | 62.6129 | -61.3174 | -61.1298 | 62.2055 | -0.42114 | -0.60883 | -0.25177 | 62.4939 | -61.2671 | -0.36163 | 0.24262 | -0.14191 | -0.17395 | -0.16479 | -0.31128 | 0.1236 | 0.21973 | 60.347 | 60.704 | 123.1613 | 123.5687 | -0.14191 | 123.4497 | 60.5347 | -0.31128 | 123.5687 | -0.14191 | 60.5347 | 123.1613 | 123.4497 | -123.6877 | -123.6374
821.9844 | 123.4589 | -60.9238 | 62.3749 | -0.41494 | -0.017185 | -0.028574 | -0.019015 | 0.040372 | -0.024006 | 0.071723 | -61.0931 | 62.5259 | -61.3586 | -61.1984 | 62.1826 | -0.45319 | -0.59509 | -0.27008 | 62.5397 | -61.2442 | -0.43488 | 0.15106 | -0.16937 | -0.27466 | -0.19226 | -0.32044 | 0.16479 | 0.2655 | 60.3287 | 60.6537 | 123.1064 | 123.4497 | -0.16937 | 123.4634 | 60.4706 | -0.32044 | 123.4497 | -0.16937 | 60.4706 | 123.1064 | 123.4634 | -123.7335 | -123.6191
822.9219 | 123.4634 | -60.9375 | 62.4023 | -0.36916 | -0.0097082 | -0.02537 | 0.0044842 | 0.044645 | -0.0047804 | 0.066383 | -61.1023 | 62.6358 | -61.3266 | -61.1069 | 62.2192 | -0.42114 | -0.62714 | -0.23804 | 62.5168 | -61.2488 | -0.3891 | 0.23346 | -0.16479 | -0.16937 | -0.18311 | -0.31128 | 0.11444 | 0.2243 | 60.3104 | 60.6995 | 123.1567 | 123.5733 | -0.16479 | 123.4543 | 60.5164 | -0.31128 | 123.5733 | -0.16479 | 60.5164 | 123.1567 | 123.4543 | -123.7289 | -123.6511
823.9844 | 123.4589 | -60.9283 | 62.4207 | -0.27761 | -0.0043672 | -0.028574 | 0.018369 | 0.040372 | -0.018665 | 0.050361 | -61.0931 | 62.59 | -61.3174 | -61.0931 | 62.2238 | -0.4303 | -0.63171 | -0.25177 | 62.5626 | -61.2442 | -0.3891 | 0.16937 | -0.16479 | -0.16479 | -0.19684 | -0.31586 | 0.14191 | 0.2243 | 60.2966 | 60.6766 | 123.1522 | 123.5184 | -0.16479 | 123.4909 | 60.498 | -0.31586 | 123.5184 | -0.16479 | 60.498 | 123.1522 | 123.4909 | -123.7381 | -123.6649
824.9219 | 123.4772 | -60.9192 | 62.439 | -0.33864 | -0.0011632 | -0.049937 | 0.015165 | 0.038236 | -0.0058484 | 0.072791 | -61.0611 | 62.645 | -61.2991 | -61.1252 | 62.2192 | -0.45776 | -0.61798 | -0.28381 | 62.5351 | -61.2442 | -0.37994 | 0.20599 | -0.14191 | -0.20599 | -0.21973 | -0.32501 | 0.09613 | 0.23804 | 60.3012 | 60.6354 | 123.1384 | 123.5641 | -0.14191 | 123.4543 | 60.4614 | -0.32501 | 123.5641 | -0.14191 | 60.4614 | 123.1384 | 123.4543 | -123.7381 | -123.6832
825.9844 | 123.4955 | -60.9558 | 62.3245 | 0.14964 | -0.019321 | -0.040324 | -0.0061968 | 0.033964 | -0.031483 | 0.061042 | -61.1343 | 62.5031 | -61.3541 | -61.2671 | 62.1323 | -0.54016 | -0.5722 | -0.3479 | 62.5076 | -61.2625 | -0.39825 | 0.17853 | -0.17853 | -0.31128 | -0.19226 | -0.3067 | 0.18311 | 0.21973 | 60.3836 | 60.6079 | 123.0881 | 123.4589 | -0.17853 | 123.4634 | 60.4156 | -0.3067 | 123.4589 | -0.17853 | 60.4156 | 123.0881 | 123.4634 | -123.6786 | -123.587
826.9219 | 123.4772 | -60.9741 | 62.3703 | -0.32338 | -0.0022312 | -0.028574 | 0.019437 | 0.043577 | -0.01012 | 0.067451 | -61.0611 | 62.6038 | -61.3312 | -61.1343 | 62.1735 | -0.48981 | -0.62256 | -0.31128 | 62.4893 | -61.2717 | -0.35706 | 0.23346 | -0.086975 | -0.16022 | -0.19684 | -0.29755 | 0.11902 | 0.27008 | 60.3516 | 60.6628 | 123.1476 | 123.5779 | -0.086975 | 123.4634 | 60.4843 | -0.29755 | 123.5779 | -0.086975 | 60.4843 | 123.1476 | 123.4634 | -123.7015 | -123.642
827.9844 | 123.5504 | -60.9467 | 62.3199 | -0.033467 | -0.023593 | -0.071299 | -0.01047 | 0.037168 | -0.030414 | 0.070655 | -61.1252 | 62.4619 | -61.3495 | -61.3083 | 62.0728 | -0.59509 | -0.54016 | -0.38452 | 62.5305 | -61.3174 | -0.40283 | 0.14191 | -0.17853 | -0.36163 | -0.24719 | -0.37079 | 0.21057 | 0.2243 | 60.4065 | 60.5621 | 123.0194 | 123.4085 | -0.17853 | 123.4772 | 60.3516 | -0.37079 | 123.4085 | -0.17853 | 60.3516 | 123.0194 | 123.4772 | -123.6694 | -123.6374
828.9219 | 123.4131 | -60.8871 | 62.4939 | -0.39968 | -0.0043672 | -0.034983 | 0.025846 | 0.031827 | -0.011188 | 0.064246 | -61.0245 | 62.709 | -61.235 | -61.0474 | 62.5259 | -0.37994 | -0.75531 | -0.3479 | 62.59 | -61.171 | -0.3479 | 0.21515 | -0.13733 | -0.16022 | 0.032044 | -0.28381 | 0.096131 | 0.21057 | 60.1318 | 60.5392 | 123.4131 | 123.5962 | -0.13733 | 123.4772 | 60.5072 | -0.28381 | 123.5962 | -0.13733 | 60.5072 | 123.4131 | 123.4772 | -123.7289 | -123.6649
829.9844 | 123.4772 | -60.8871 | 62.4344 | -0.27761 | -0.0043672 | -0.02537 | 0.015165 | 0.04144 | -0.013325 | 0.06211 | -61.0336 | 62.6678 | -61.2762 | -61.0611 | 62.2604 | -0.48523 | -0.66376 | -0.29297 | 62.5717 | -61.1938 | -0.3891 | 0.23346 | -0.14648 | -0.17395 | -0.17395 | -0.3067 | 0.13733 | 0.24262 | 60.2234 | 60.5942 | 123.1476 | 123.555 | -0.14648 | 123.4589 | 60.4019 | -0.3067 | 123.555 | -0.14648 | 60.4019 | 123.1476 | 123.4589 | -123.7106 | -123.6282
830.9219 | 123.4726 | -60.8459 | 62.4847 | -0.27761 | -0.0043672 | -0.010416 | 0.025846 | 0.039304 | -0.014393 | 0.070655 | -60.965 | 62.7045 | -61.2259 | -61.0382 | 62.2925 | -0.48981 | -0.65002 | -0.3067 | 62.6038 | -61.1755 | -0.37994 | 0.21973 | -0.11902 | -0.19226 | -0.19226 | -0.32959 | 0.11902 | 0.26093 | 60.1959 | 60.5392 | 123.1384 | 123.5504 | -0.11902 | 123.4497 | 60.3561 | -0.32959 | 123.5504 | -0.11902 | 60.3561 | 123.1384 | 123.4497 | -123.7106 | -123.6603
831.9688 | 123.587 | -60.8917 | 62.3566 | 0.4243 | -0.019321 | -0.018961 | 0.0055522 | 0.0361 | -0.017597 | 0.064246 | -60.8963 | 62.6587 | -61.1572 | -61.2442 | 62.1368 | -0.75073 | -0.62256 | -0.49896 | 62.5763 | -61.2396 | -0.2655 | 0.30212 | -0.004577 | -0.35248 | -0.21973 | -0.3479 | 0.21973 | 0.26093 | 60.2692 | 60.3928 | 123.0286 | 123.5504 | -0.004577 | 123.468 | 60.141 | -0.3479 | 123.5504 | -0.004577 | 60.141 | 123.0286 | 123.468 | -123.5138 | -123.5962
832.9219 | 123.4589 | -60.759 | 62.5763 | -0.0029495 | 0.0073818 | -0.0478 | 0.018369 | 0.033964 | -0.0037124 | 0.067451 | -60.8597 | 62.8006 | -61.1298 | -60.9879 | 62.4023 | -0.5127 | -0.67291 | -0.33875 | 62.6633 | -61.1206 | -0.37079 | 0.2243 | -0.10071 | -0.22888 | -0.17395 | -0.36163 | 0.086975 | 0.27008 | 60.0861 | 60.4202 | 123.1613 | 123.5596 | -0.10071 | 123.4222 | 60.2463 | -0.36163 | 123.5596 | -0.10071 | 60.2463 | 123.1613 | 123.4222 | -123.7061 | -123.6969
833.9844 | 123.5825 | -60.5759 | 62.6633 | -0.14028 | -0.0086402 | -0.062754 | 0.0066202 | 0.043577 | -0.034687 | 0.067451 | -60.7636 | 62.8098 | -60.9879 | -60.9879 | 62.4252 | -0.62714 | -0.58594 | -0.44403 | 62.8464 | -60.9512 | -0.41199 | 0.14648 | -0.18768 | -0.41199 | -0.23804 | -0.37537 | 0.18311 | 0.2243 | 59.9899 | 60.1318 | 123.0011 | 123.3856 | -0.18768 | 123.4222 | 59.9487 | -0.37537 | 123.3856 | -0.18768 | 59.9487 | 123.0011 | 123.4222 | -123.6511 | -123.6145
834.9219 | 123.4451 | -60.5392 | 62.8006 | -0.49123 | 0.0020408 | -0.040324 | 0.017301 | 0.035032 | -0.0079844 | 0.068519 | -60.7498 | 62.9883 | -60.9695 | -60.704 | 62.5946 | -0.48981 | -0.71869 | -0.28839 | 62.8601 | -60.8734 | -0.4303 | 0.18768 | -0.21057 | -0.16479 | -0.20599 | -0.33417 | 0.059509 | 0.21973 | 59.8206 | 60.2509 | 123.1338 | 123.5275 | -0.21057 | 123.3994 | 60.0494 | -0.33417 | 123.5275 | -0.21057 | 60.0494 | 123.1338 | 123.3994 | -123.7701 | -123.674
835.9844 | 123.5413 | -60.4431 | 62.8464 | -0.32338 | -0.026798 | -0.0478 | -0.0072648 | 0.039304 | -0.032551 | 0.066383 | -60.6033 | 62.9471 | -60.8505 | -60.7819 | 62.5809 | -0.61798 | -0.60425 | -0.41657 | 62.9791 | -60.8231 | -0.40741 | 0.10071 | -0.16022 | -0.33875 | -0.2655 | -0.37994 | 0.13275 | 0.24719 | 59.8389 | 60.0266 | 123.024 | 123.3902 | -0.16022 | 123.4222 | 59.8251 | -0.37994 | 123.3902 | -0.16022 | 59.8251 | 123.024 | 123.4222 | -123.6969 | -123.6694
836.9219 | 123.4222 | -60.3882 | 62.9425 | -0.76589 | -0.015048 | -0.046732 | 0.014097 | 0.039304 | -0.016529 | 0.070655 | -60.5576 | 63.1668 | -60.7636 | -60.5667 | 62.7686 | -0.50812 | -0.737 | -0.29755 | 63.0478 | -60.6674 | -0.37537 | 0.2243 | -0.16937 | -0.17853 | -0.17395 | -0.27923 | 0.10529 | 0.20599 | 59.6512 | 60.0906 | 123.1567 | 123.555 | -0.16937 | 123.436 | 59.8801 | -0.27923 | 123.555 | -0.16937 | 59.8801 | 123.1567 | 123.436 | -123.7061 | -123.6099
837.9844 | 123.5504 | -60.2783 | 62.9654 | -0.3539 | -0.017185 | -0.056345 | -0.0029928 | 0.031827 | -0.037891 | 0.068519 | -60.4431 | 63.0981 | -60.6995 | -60.3561 | 62.709 | -0.737 | -0.64087 | -0.39368 | 63.1073 | -60.6491 | -0.42114 | 0.13275 | -0.16479 | -0.07782 | -0.25635 | -0.37079 | 0.14191 | 0.25635 | 59.6375 | 59.8846 | 122.9874 | 123.3765 | -0.16479 | 123.3856 | 59.5413 | -0.37079 | 123.3765 | -0.16479 | 59.5413 | 122.9874 | 123.3856 | -123.6649 | -123.6145
838.9219 | 123.4955 | -60.3287 | 63.0844 | -0.38442 | -9.5248e-05 | -0.049937 | 0.014097 | 0.04144 | -0.025074 | 0.069587 | -60.498 | 63.2172 | -60.704 | -60.4752 | 62.8601 | -0.48981 | -0.75531 | -0.28839 | 63.1165 | -60.6216 | -0.37537 | 0.13275 | -0.16937 | -0.14648 | -0.22431 | -0.29297 | 0.032043 | 0.20599 | 59.5734 | 60.0403 | 123.1888 | 123.5458 | -0.16937 | 123.4451 | 59.8389 | -0.29297 | 123.5458 | -0.16937 | 59.8389 | 123.1888 | 123.4451 | -123.7885 | -123.7061
839.9844 | 123.5779 | -60.3378 | 62.9379 | -0.12502 | -0.0097082 | -0.062754 | 0.0055522 | 0.031827 | -0.042164 | 0.068519 | -60.4889 | 63.1073 | -60.7086 | -60.6995 | 62.677 | -0.6546 | -0.60883 | -0.45319 | 63.1073 | -60.6628 | -0.37079 | 0.16937 | -0.15106 | -0.36163 | -0.26093 | -0.32501 | 0.16937 | 0.21973 | 59.729 | 59.8846 | 123.0148 | 123.4451 | -0.15106 | 123.4451 | 59.6832 | -0.32501 | 123.4451 | -0.15106 | 59.6832 | 123.0148 | 123.4451 | -123.6465 | -123.6008
840.9219 | 123.4543 | -60.3745 | 63.0066 | 0.11912 | -0.012912 | -0.043528 | 0.019437 | 0.040372 | -0.01012 | 0.066383 | -60.4935 | 63.208 | -60.7269 | -60.5026 | 62.8052 | -0.53101 | -0.78735 | -0.31586 | 63.1027 | -60.64 | -0.35248 | 0.20142 | -0.11902 | -0.12817 | -0.20142 | -0.2655 | 0.09613 | 0.23346 | 59.5871 | 60.0586 | 123.1796 | 123.5825 | -0.11902 | 123.4772 | 59.8434 | -0.2655 | 123.5825 | -0.11902 | 59.8434 | 123.1796 | 123.4772 | -123.7335 | -123.6465
841.9219 | 123.4222 | -60.2554 | 63.0798 | -2.3986 | 0.0084498 | -0.037119 | 0.019437 | 0.039304 | -0.013325 | 0.078132 | -60.4843 | 63.2996 | -60.6308 | -60.3607 | 62.9288 | -0.52185 | -0.7782 | -0.33417 | 63.1989 | -60.5576 | -0.37537 | 0.21973 | -0.22888 | -0.10529 | -0.15106 | -0.30212 | 0.11902 | 0.14648 | 59.4772 | 59.9213 | 123.1842 | 123.555 | -0.22888 | 123.4543 | 59.7336 | -0.30212 | 123.555 | -0.22888 | 59.7336 | 123.1842 | 123.4543 | -123.7106 | -123.6374
842.9844 | 123.4543 | -60.3104 | 62.9883 | -0.4302 | -0.023593 | -0.045664 | 0.00021117 | 0.030759 | -0.026142 | 0.075996 | -60.466 | 63.1485 | -60.7178 | -60.5621 | 62.7823 | -0.5722 | -0.72784 | -0.36163 | 63.1485 | -60.6354 | -0.40741 | 0.16022 | -0.15564 | -0.25177 | -0.20599 | -0.32501 | 0.16022 | 0.25177 | 59.5825 | 59.9487 | 123.0927 | 123.4589 | -0.15564 | 123.4589 | 59.7382 | -0.32501 | 123.4589 | -0.15564 | 59.7382 | 123.0927 | 123.4589 | -123.7061 | -123.6237
843.9219 | 123.4222 | -60.2554 | 63.1027 | -0.41494 | -0.0086402 | -0.041392 | 0.010892 | 0.035032 | -0.032551 | 0.06211 | -60.3928 | 63.2629 | -60.5988 | -60.4065 | 62.9242 | -0.52185 | -0.78735 | -0.31586 | 63.208 | -60.498 | -0.34332 | 0.16022 | -0.13733 | -0.15106 | -0.17853 | -0.24262 | 0.10529 | 0.20599 | 59.4681 | 59.9396 | 123.1796 | 123.5184 | -0.13733 | 123.4634 | 59.7336 | -0.24262 | 123.5184 | -0.13733 | 59.7336 | 123.1796 | 123.4634 | -123.7015 | -123.6008
844.9844 | 123.5596 | -60.1913 | 63.0798 | -0.033467 | -0.019321 | -0.079844 | -0.0051288 | 0.029691 | -0.030414 | 0.070655 | -60.3699 | 63.2355 | -60.5713 | -60.5255 | 62.8418 | -0.66834 | -0.67749 | -0.43488 | 63.2492 | -60.5438 | -0.37994 | 0.15564 | -0.17853 | -0.33417 | -0.23804 | -0.35248 | 0.16937 | 0.20142 | 59.5139 | 59.7565 | 123.0331 | 123.4268 | -0.17853 | 123.4406 | 59.523 | -0.35248 | 123.4268 | -0.17853 | 59.523 | 123.0331 | 123.4406 | -123.6511 | -123.6237
845.9219 | 123.4497 | -60.0998 | 63.2492 | 0.01231 | 0.00097275 | -0.054209 | 0.033323 | 0.039304 | -0.0037124 | 0.065314 | -60.173 | 63.4827 | -60.4385 | -60.2783 | 63.0295 | -0.59967 | -0.70496 | -0.3891 | 63.3636 | -60.434 | -0.33875 | 0.23346 | -0.073243 | -0.17853 | -0.21973 | -0.33417 | 0.11444 | 0.2655 | 59.3948 | 59.7107 | 123.1293 | 123.5825 | -0.073243 | 123.4634 | 59.5001 | -0.33417 | 123.5825 | -0.073243 | 59.5001 | 123.1293 | 123.4634 | -123.6877 | -123.6832
846.9844 | 123.5092 | -60.0815 | 63.1943 | -0.048725 | -0.0054352 | -0.052073 | -0.01581 | 0.037168 | -0.029346 | 0.057838 | -60.2325 | 63.3774 | -60.4523 | -60.3973 | 62.9883 | -0.66834 | -0.6958 | -0.42114 | 63.3362 | -60.4248 | -0.37079 | 0.18311 | -0.15106 | -0.31586 | -0.20599 | -0.34332 | 0.14191 | 0.21973 | 59.3857 | 59.6603 | 123.0698 | 123.4589 | -0.15106 | 123.4177 | 59.4131 | -0.34332 | 123.4589 | -0.15106 | 59.4131 | 123.0698 | 123.4177 | -123.6465 | -123.6191
847.9219 | 123.468 | -60.0266 | 63.327 | -0.32338 | 0.0052458 | -0.043528 | 0.017301 | 0.044645 | -0.0026434 | 0.067451 | -60.141 | 63.5147 | -60.4111 | -60.2051 | 63.1073 | -0.62714 | -0.7782 | -0.36163 | 63.4186 | -60.347 | -0.38452 | 0.18768 | -0.11444 | -0.17853 | -0.21973 | -0.32043 | 0.091553 | 0.27008 | 59.2484 | 59.6649 | 123.1338 | 123.5413 | -0.11444 | 123.4451 | 59.3994 | -0.32043 | 123.5413 | -0.11444 | 59.3994 | 123.1338 | 123.4451 | -123.7381 | -123.674
848.9844 | 123.436 | -60.0769 | 63.2401 | -0.4302 | -0.0043672 | -0.043528 | 0.0066202 | 0.045713 | -0.020801 | 0.065314 | -60.2646 | 63.4415 | -60.466 | -60.2234 | 63.089 | -0.5722 | -0.83771 | -0.32044 | 63.3728 | -60.3928 | -0.3891 | 0.20142 | -0.18768 | -0.14648 | -0.15106 | -0.31586 | 0.13275 | 0.20142 | 59.2392 | 59.7565 | 123.1659 | 123.5184 | -0.18768 | 123.4497 | 59.5047 | -0.31586 | 123.5184 | -0.18768 | 59.5047 | 123.1659 | 123.4497 | -123.7061 | -123.6328
849.9219 | 123.3994 | -60.0128 | 63.3453 | -0.47597 | -0.0054352 | -0.037119 | 0.022642 | 0.05319 | -0.024006 | 0.070655 | -60.1547 | 63.5696 | -60.3836 | -60.1044 | 63.002 | -0.62714 | -0.78735 | -0.3479 | 63.4048 | -60.2875 | -0.37079 | 0.2243 | -0.14191 | -0.091553 | -0.34332 | -0.27466 | 0.059509 | 0.22888 | 59.2255 | 59.6649 | 123.0148 | 123.5825 | -0.14191 | 123.4177 | 59.3857 | -0.27466 | 123.5825 | -0.14191 | 59.3857 | 123.0148 | 123.4177 | -123.7289 | -123.6328
850.9844 | 123.5458 | -59.9167 | 63.3362 | -0.14028 | -0.023593 | -0.052073 | -0.0072648 | 0.024351 | -0.033619 | 0.067451 | -60.0861 | 63.4964 | -60.3378 | -60.2829 | 63.0524 | -0.73242 | -0.64087 | -0.49896 | 63.5147 | -60.2921 | -0.42114 | 0.16022 | -0.16937 | -0.36621 | -0.28381 | -0.37537 | 0.17853 | 0.25177 | 59.2758 | 59.4177 | 122.9691 | 123.4131 | -0.16937 | 123.4314 | 59.1843 | -0.37537 | 123.4131 | -0.16937 | 59.1843 | 122.9691 | 123.4314 | -123.674 | -123.6282
851.9219 | 123.4314 | -59.8434 | 63.4872 | -0.4302 | -0.0043672 | -0.0478 | 0.0087562 | 0.037168 | -0.017597 | 0.066383 | -60.0311 | 63.7115 | -60.2325 | -59.967 | 63.3316 | -0.56763 | -0.84686 | -0.32044 | 63.5925 | -60.141 | -0.3891 | 0.2243 | -0.18768 | -0.1236 | -0.15564 | -0.29755 | 0.10529 | 0.20142 | 58.9966 | 59.523 | 123.175 | 123.555 | -0.18768 | 123.436 | 59.2758 | -0.29755 | 123.555 | -0.18768 | 59.2758 | 123.175 | 123.436 | -123.7198 | -123.6282
852.9219 | 123.4406 | -59.848 | 63.4598 | -0.56752 | -0.0075722 | -0.037119 | 0.014097 | 0.04144 | -0.016529 | 0.050361 | -60.054 | 63.6887 | -60.2646 | -60.0128 | 63.2996 | -0.59509 | -0.85144 | -0.33417 | 63.5651 | -60.1685 | -0.41656 | 0.22888 | -0.20599 | -0.16479 | -0.16022 | -0.32043 | 0.10529 | 0.21057 | 58.9966 | 59.5139 | 123.1476 | 123.5367 | -0.20599 | 123.4131 | 59.2529 | -0.32043 | 123.5367 | -0.20599 | 59.2529 | 123.1476 | 123.4131 | -123.7244 | -123.6282
853.9844 | 123.4314 | -59.729 | 63.5925 | -0.49123 | -0.01398 | -0.056345 | 0.02371 | 0.044645 | -0.016529 | 0.063178 | -59.9258 | 63.8031 | -60.1135 | -59.8846 | 63.446 | -0.56763 | -0.84686 | -0.34332 | 63.7024 | -60.0403 | -0.38452 | 0.21057 | -0.19684 | -0.15564 | -0.14648 | -0.31128 | 0.10986 | 0.18768 | 58.8821 | 59.3857 | 123.175 | 123.5321 | -0.19684 | 123.4314 | 59.1614 | -0.31128 | 123.5321 | -0.19684 | 59.1614 | 123.175 | 123.4314 | -123.7061 | -123.6328
854.9219 | 123.4818 | -59.8068 | 63.5101 | -0.32338 | -0.0075722 | -0.049937 | 0.022642 | 0.039304 | -0.01012 | 0.057838 | -59.9625 | 63.7253 | -60.2142 | -59.9808 | 63.3362 | -0.60425 | -0.81024 | -0.37537 | 63.6429 | -60.1089 | -0.40741 | 0.21515 | -0.15564 | -0.17395 | -0.17395 | -0.30212 | 0.13275 | 0.25177 | 58.9966 | 59.4315 | 123.143 | 123.5321 | -0.15564 | 123.4497 | 59.2026 | -0.30212 | 123.5321 | -0.15564 | 59.2026 | 123.143 | 123.4497 | -123.7244 | -123.6191
855.9844 | 123.5733 | -59.5505 | 63.7024 | -0.18605 | -0.017185 | -0.057413 | -0.014742 | 0.028623 | -0.032551 | 0.051429 | -59.729 | 63.8626 | -59.9625 | -59.9579 | 63.4598 | -0.75531 | -0.70496 | -0.50812 | 63.8992 | -59.9213 | -0.41199 | 0.16022 | -0.17853 | -0.40741 | -0.24262 | -0.37079 | 0.19684 | 0.23346 | 58.8455 | 59.0424 | 123.0103 | 123.4131 | -0.17853 | 123.4497 | 58.7952 | -0.37079 | 123.4131 | -0.17853 | 58.7952 | 123.0103 | 123.4497 | -123.6649 | -123.6237
856.9219 | 123.4497 | -59.6603 | 63.6932 | -0.41494 | -0.0075722 | -0.031779 | 0.0023482 | 0.039304 | -0.029346 | 0.065314 | -59.8022 | 63.8535 | -60.0174 | -59.848 | 63.4827 | -0.63171 | -0.8606 | -0.37994 | 63.8077 | -59.9442 | -0.35706 | 0.16022 | -0.14191 | -0.18768 | -0.21057 | -0.28381 | 0.11444 | 0.21515 | 58.7997 | 59.2804 | 123.143 | 123.5138 | -0.14191 | 123.468 | 59.0286 | -0.28381 | 123.5138 | -0.14191 | 59.0286 | 123.143 | 123.468 | -123.7106 | -123.6374
857.9688 | 123.5596 | -59.4818 | 63.7939 | -0.12502 | -9.5248e-05 | -0.046732 | -0.0029928 | 0.029691 | -0.049641 | 0.064246 | -59.6512 | 63.945 | -59.8618 | -59.8251 | 63.5513 | -0.73242 | -0.71869 | -0.4715 | 63.9404 | -59.8251 | -0.37994 | 0.15106 | -0.16937 | -0.34332 | -0.24261 | -0.34332 | 0.14648 | 0.21057 | 58.7631 | 59.0103 | 123.0331 | 123.4268 | -0.16937 | 123.4222 | 58.7494 | -0.34332 | 123.4268 | -0.16937 | 58.7494 | 123.0331 | 123.4222 | -123.6557 | -123.6191
858.9219 | 123.4589 | -59.1751 | 64.1464 | 0.54637 | 0.0020408 | -0.038187 | 0.018369 | 0.027555 | -0.014393 | 0.06211 | -59.3399 | 64.3616 | -59.5871 | -59.3491 | 63.9725 | -0.67749 | -0.84686 | -0.38452 | 64.2151 | -59.4955 | -0.41199 | 0.21515 | -0.1648 | -0.17395 | -0.17395 | -0.32043 | 0.068665 | 0.24719 | 58.3282 | 58.7906 | 123.1476 | 123.5367 | -0.1648 | 123.3902 | 58.4976 | -0.32043 | 123.5367 | -0.1648 | 58.4976 | 123.1476 | 123.3902 | -123.7335 | -123.642
859.9219 | 123.436 | -59.1751 | 64.1693 | -0.39968 | -0.011844 | -0.032847 | 0.014097 | 0.038236 | -0.026142 | 0.05677 | -59.3353 | 64.3982 | -59.5505 | -59.2346 | 64.325 | -0.6134 | -1.0483 | -0.39368 | 64.2883 | -59.5184 | -0.37537 | 0.22888 | -0.16022 | -0.059509 | 0.15564 | -0.34332 | 0.11902 | 0.21515 | 58.1268 | 58.7814 | 123.5001 | 123.5733 | -0.16022 | 123.4634 | 58.5617 | -0.34332 | 123.5733 | -0.16022 | 58.5617 | 123.5001 | 123.4634 | -123.7198 | -123.6877
860.9844 | 123.5046 | -58.6945 | 64.5676 | 0.36326 | -0.0086402 | -0.022166 | 0.0044842 | 0.035032 | -0.035755 | 0.068519 | -58.9188 | 64.6957 | -59.1385 | -59.0103 | 64.3524 | -0.737 | -0.78735 | -0.43945 | 64.7186 | -59.0652 | -0.44403 | 0.12817 | -0.2243 | -0.31586 | -0.21515 | -0.37079 | 0.15106 | 0.21973 | 57.9071 | 58.255 | 123.0469 | 123.3902 | -0.2243 | 123.4131 | 57.9575 | -0.37079 | 123.3902 | -0.2243 | 57.9575 | 123.0469 | 123.4131 | -123.7061 | -123.6328
861.9219 | 123.4406 | -58.6624 | 64.7095 | 0.19541 | -0.0043672 | -0.063822 | 0.025846 | 0.0361 | -0.02187 | 0.059974 | -58.8043 | 64.92 | -59.0332 | -58.8043 | 64.5172 | -0.60883 | -0.87433 | -0.3479 | 64.7919 | -58.9279 | -0.37079 | 0.21057 | -0.14191 | -0.14191 | -0.19226 | -0.2655 | 0.082397 | 0.22888 | 57.7881 | 58.3145 | 123.1796 | 123.5825 | -0.14191 | 123.4543 | 58.0536 | -0.2655 | 123.5825 | -0.14191 | 58.0536 | 123.1796 | 123.4543 | -123.7427 | -123.6374
862.9844 | 123.5275 | -59.1431 | 64.1464 | -1.3305 | -0.02573 | -0.037119 | -0.0019248 | 0.031827 | -0.036823 | 0.063178 | -59.3445 | 64.2517 | -59.5459 | -59.4727 | 63.8535 | -0.75531 | -0.76904 | -0.49439 | 64.2975 | -59.4955 | -0.40283 | 0.10529 | -0.20142 | -0.32959 | -0.29297 | -0.35248 | 0.15106 | 0.20142 | 58.374 | 58.6487 | 122.9965 | 123.3948 | -0.20142 | 123.4406 | 58.3878 | -0.35248 | 123.3948 | -0.20142 | 58.3878 | 122.9965 | 123.4406 | -123.6923 | -123.642
863.9219 | 123.5321 | -58.6716 | 64.5859 | 0.48533 | -0.0032992 | -0.041392 | 0.018369 | 0.026487 | -0.016529 | 0.065314 | -58.8364 | 64.801 | -59.1019 | -58.96 | 64.3662 | -0.78735 | -0.77362 | -0.49896 | 64.7415 | -59.0286 | -0.4303 | 0.21515 | -0.16479 | -0.28839 | -0.21973 | -0.35705 | 0.15564 | 0.2655 | 57.8979 | 58.1726 | 123.0377 | 123.4726 | -0.16479 | 123.4131 | 57.8842 | -0.35705 | 123.4726 | -0.16479 | 57.8842 | 123.0377 | 123.4131 | -123.6877 | -123.6145
864.9844 | 123.4909 | -58.4702 | 64.8148 | 0.348 | -0.024662 | -0.026438 | -0.0019248 | 0.033964 | -0.041096 | 0.065314 | -58.6258 | 64.9796 | -58.8318 | -58.7494 | 64.6133 | -0.76446 | -0.8194 | -0.46234 | 64.9933 | -58.7906 | -0.36163 | 0.16479 | -0.15564 | -0.27924 | -0.20142 | -0.32043 | 0.17853 | 0.20599 | 57.6508 | 58.0078 | 123.0835 | 123.4497 | -0.15564 | 123.4634 | 57.7057 | -0.32043 | 123.4497 | -0.15564 | 57.7057 | 123.0835 | 123.4634 | -123.6465 | -123.6053
865.9219 | 123.4406 | -58.6121 | 64.7095 | -0.47597 | -0.012912 | -0.06489 | 0.0076882 | 0.032895 | -0.025074 | 0.066383 | -58.7448 | 64.8834 | -58.9828 | -58.8364 | 64.4943 | -0.65918 | -0.88806 | -0.42114 | 64.8148 | -58.9188 | -0.37079 | 0.17395 | -0.13275 | -0.2243 | -0.21515 | -0.3067 | 0.10528 | 0.23804 | 57.724 | 58.1909 | 123.1064 | 123.4955 | -0.13275 | 123.4268 | 57.9529 | -0.3067 | 123.4955 | -0.13275 | 57.9529 | 123.1064 | 123.4268 | -123.6923 | -123.6282
866.9219 | 123.436 | -58.1818 | 65.1855 | -0.52175 | -0.016117 | -0.036051 | 0.016233 | 0.045713 | -0.022938 | 0.066383 | -58.3694 | 65.3412 | -58.5892 | -58.3374 | 64.9841 | -0.6134 | -0.91095 | -0.35706 | 65.2679 | -58.4747 | -0.40741 | 0.15564 | -0.18768 | -0.15564 | -0.20142 | -0.29297 | 0.082397 | 0.21973 | 57.2708 | 57.8247 | 123.1659 | 123.523 | -0.18768 | 123.4497 | 57.5684 | -0.29297 | 123.523 | -0.18768 | 57.5684 | 123.1659 | 123.4497 | -123.7747 | -123.6603
867.9844 | 123.5413 | -58.4381 | 64.8056 | -0.033467 | -0.022525 | -0.068095 | 0.0044842 | 0.022214 | -0.032551 | 0.06211 | -58.6395 | 64.9704 | -58.8547 | -58.7906 | 64.595 | -0.81024 | -0.80566 | -0.50812 | 65.0162 | -58.7814 | -0.41656 | 0.16479 | -0.20142 | -0.35248 | -0.21057 | -0.34332 | 0.21057 | 0.21515 | 57.6324 | 57.93 | 123.0331 | 123.4085 | -0.20142 | 123.4543 | 57.6279 | -0.34332 | 123.4085 | -0.20142 | 57.6279 | 123.0331 | 123.4543 | -123.6603 | -123.587
868.9219 | 123.3994 | -58.3466 | 64.9979 | 0.6074 | -0.0097082 | -0.032847 | 0.0408 | 0.038236 | -0.0079844 | 0.055701 | -58.5342 | 65.2176 | -58.7311 | -58.4244 | 64.8697 | -0.67749 | -0.94299 | -0.36621 | 65.0848 | -58.6349 | -0.38452 | 0.21973 | -0.18768 | -0.077819 | -0.12817 | -0.28839 | 0.086975 | 0.19684 | 57.4036 | 57.9803 | 123.2162 | 123.5641 | -0.18768 | 123.4314 | 57.6691 | -0.28839 | 123.5641 | -0.18768 | 57.6691 | 123.2162 | 123.4314 | -123.7289 | -123.6328
869.9219 | 123.5321 | -58.1955 | 65.094 | 1.3703 | -0.021457 | -0.039256 | 0.0034162 | 0.029691 | -0.031483 | 0.061042 | -58.3237 | 65.2176 | -58.5938 | -58.5205 | 64.8193 | -0.78278 | -0.79651 | -0.52643 | 65.2588 | -58.5571 | -0.39825 | 0.1236 | -0.12817 | -0.32501 | -0.27466 | -0.36163 | 0.16479 | 0.27008 | 57.399 | 57.6691 | 123.0148 | 123.4131 | -0.12817 | 123.4543 | 57.4127 | -0.36163 | 123.4131 | -0.12817 | 57.4127 | 123.0148 | 123.4543 | -123.6877 | -123.6511
870.9844 | 123.5229 | -57.9758 | 65.2954 | -0.048725 | -0.024662 | -0.038187 | 0.0034162 | 0.035032 | -0.0443 | 0.064246 | -58.1635 | 65.4602 | -58.374 | -58.3191 | 65.0253 | -0.81482 | -0.81024 | -0.52185 | 65.4602 | -58.3374 | -0.39825 | 0.16479 | -0.18768 | -0.34332 | -0.27008 | -0.36163 | 0.16479 | 0.21057 | 57.1655 | 57.4539 | 123.0011 | 123.436 | -0.18768 | 123.436 | 57.1609 | -0.36163 | 123.436 | -0.18768 | 57.1609 | 123.0011 | 123.436 | -123.6694 | -123.6328
871.9219 | 123.5046 | -57.9025 | 65.3778 | -0.38442 | -0.015048 | -0.060618 | 0.010892 | 0.031827 | -0.033619 | 0.077064 | -58.0948 | 65.506 | -58.3145 | -58.2184 | 65.1077 | -0.75073 | -0.85144 | -0.48981 | 65.5014 | -58.2596 | -0.41199 | 0.12817 | -0.19226 | -0.31586 | -0.27008 | -0.35706 | 0.1236 | 0.21973 | 57.0511 | 57.4127 | 123.0103 | 123.4085 | -0.19226 | 123.4039 | 57.1518 | -0.35706 | 123.4085 | -0.19226 | 57.1518 | 123.0103 | 123.4039 | -123.6923 | -123.6374
872.9844 | 123.5046 | -58.0399 | 65.2267 | 0.21067 | -0.0097082 | -0.043528 | -0.00085683 | 0.025419 | -0.032551 | 0.06211 | -58.255 | 65.3961 | -58.4427 | -58.3603 | 65.007 | -0.80109 | -0.91553 | -0.49896 | 65.3778 | -58.374 | -0.40283 | 0.16937 | -0.21515 | -0.32043 | -0.21973 | -0.33417 | 0.15106 | 0.18768 | 57.1243 | 57.5409 | 123.0469 | 123.436 | -0.21515 | 123.4177 | 57.2388 | -0.33417 | 123.436 | -0.21515 | 57.2388 | 123.0469 | 123.4177 | -123.6694 | -123.6008
873.9219 | 123.4222 | -58.0353 | 65.3275 | -0.44545 | -0.011844 | -0.05955 | 0.022642 | 0.028623 | -0.024006 | 0.058906 | -58.2047 | 65.5014 | -58.4198 | -58.1818 | 65.1169 | -0.70953 | -1.0117 | -0.42114 | 65.3961 | -58.3008 | -0.38452 | 0.17395 | -0.16937 | -0.14648 | -0.21057 | -0.2655 | 0.068664 | 0.21515 | 57.0236 | 57.6141 | 123.1522 | 123.5367 | -0.16937 | 123.4314 | 57.3257 | -0.2655 | 123.5367 | -0.16937 | 57.3257 | 123.1522 | 123.4314 | -123.7473 | -123.6282
874.9844 | 123.5092 | -57.9071 | 65.3824 | 0.25645 | -0.0054352 | -0.055277 | 0.0098242 | 0.016874 | -0.033619 | 0.068519 | -58.0902 | 65.5197 | -58.3145 | -58.223 | 65.1535 | -0.8194 | -0.87891 | -0.49439 | 65.538 | -58.2367 | -0.40741 | 0.13733 | -0.18311 | -0.31586 | -0.22888 | -0.32959 | 0.15564 | 0.2243 | 57.0282 | 57.4127 | 123.0606 | 123.4268 | -0.18311 | 123.4451 | 57.0877 | -0.32959 | 123.4268 | -0.18311 | 57.0877 | 123.0606 | 123.4451 | -123.6969 | -123.6191
875.9219 | 123.5184 | -57.8201 | 65.4785 | -0.18605 | -0.011844 | -0.0478 | 0.0076882 | 0.033964 | -0.033619 | 0.064246 | -57.962 | 65.6387 | -58.2184 | -58.1451 | 65.2084 | -0.80109 | -0.86975 | -0.52643 | 65.6158 | -58.1818 | -0.39825 | 0.16022 | -0.14191 | -0.32501 | -0.27008 | -0.36163 | 0.13733 | 0.25635 | 56.9504 | 57.2937 | 123.0286 | 123.4589 | -0.14191 | 123.436 | 57.019 | -0.36163 | 123.4589 | -0.14191 | 57.019 | 123.0286 | 123.436 | -123.6969 | -123.6603
876.9844 | 123.4818 | -57.8705 | 65.419 | 0.21067 | -0.011844 | -0.0478 | -0.0019248 | 0.025419 | -0.031483 | 0.06211 | -58.049 | 65.5746 | -58.2596 | -58.1772 | 65.1672 | -0.85602 | -0.91553 | -0.50812 | 65.5655 | -58.2275 | -0.3891 | 0.15564 | -0.17853 | -0.3067 | -0.25177 | -0.35706 | 0.14648 | 0.21057 | 56.955 | 57.3624 | 123.0377 | 123.4451 | -0.17853 | 123.436 | 57.0145 | -0.35706 | 123.4451 | -0.17853 | 57.0145 | 123.0377 | 123.436 | -123.6786 | -123.6465
877.9219 | 123.5779 | -57.7423 | 65.5151 | -0.30813 | -0.020389 | -0.056345 | 0.0055522 | 0.014737 | -0.032551 | 0.058906 | -57.8934 | 65.6708 | -58.1497 | -58.1039 | 65.213 | -0.88806 | -0.83771 | -0.60425 | 65.6845 | -58.1131 | -0.40741 | 0.15564 | -0.15106 | -0.36163 | -0.30212 | -0.37079 | 0.16937 | 0.25635 | 56.9046 | 57.1381 | 122.9553 | 123.4131 | -0.15106 | 123.4268 | 56.8542 | -0.37079 | 123.4131 | -0.15106 | 56.8542 | 122.9553 | 123.4268 | -123.6649 | -123.6282
878.9844 | 123.5367 | -57.6233 | 65.6433 | 0.53111 | -0.011844 | -0.027506 | 0.017301 | 0.022214 | -0.020801 | 0.063178 | -57.7835 | 65.8218 | -57.9758 | -57.9254 | 65.4053 | -0.90637 | -0.86975 | -0.5722 | 65.8264 | -57.9712 | -0.35248 | 0.17853 | -0.16022 | -0.30212 | -0.23804 | -0.3479 | 0.1831 | 0.19226 | 56.7535 | 57.0511 | 123.0286 | 123.4451 | -0.16022 | 123.4497 | 56.7169 | -0.3479 | 123.4451 | -0.16022 | 56.7169 | 123.0286 | 123.4497 | -123.6191 | -123.6145
879.9219 | 123.5641 | -57.5821 | 65.7028 | -0.1708 | -0.02573 | -0.056345 | 0.017301 | 0.025419 | -0.034687 | 0.069587 | -57.7148 | 65.8127 | -57.9895 | -57.9666 | 65.3778 | -0.88806 | -0.86975 | -0.58594 | 65.8539 | -57.93 | -0.40741 | 0.10986 | -0.13275 | -0.38452 | -0.32501 | -0.3479 | 0.15106 | 0.27466 | 56.7123 | 56.9962 | 122.9599 | 123.3948 | -0.13275 | 123.436 | 56.694 | -0.3479 | 123.3948 | -0.13275 | 56.694 | 122.9599 | 123.436 | -123.6923 | -123.6328
880.9844 | 123.5184 | -57.8888 | 65.3641 | 0.13438 | -0.011844 | -0.048869 | -0.014742 | 0.031827 | -0.025074 | 0.066383 | -58.0902 | 65.5701 | -58.2504 | -58.1635 | 65.1581 | -0.93384 | -0.97046 | -0.56305 | 65.5151 | -58.2275 | -0.36163 | 0.20599 | -0.20142 | -0.27466 | -0.20599 | -0.33875 | 0.15106 | 0.16022 | 56.9183 | 57.3257 | 123.0469 | 123.4589 | -0.20142 | 123.4039 | 56.955 | -0.33875 | 123.4589 | -0.20142 | 56.955 | 123.0469 | 123.4039 | -123.6145 | -123.5916
881.9219 | 123.5687 | -57.4768 | 65.7715 | -0.4302 | -0.023593 | -0.0478 | 0.011961 | 0.021146 | -0.035755 | 0.067451 | -57.6324 | 65.918 | -57.8888 | -57.8522 | 65.4968 | -0.88348 | -0.85602 | -0.57678 | 65.95 | -57.8339 | -0.41199 | 0.14648 | -0.15564 | -0.37537 | -0.27466 | -0.35706 | 0.17853 | 0.25635 | 56.6208 | 56.9 | 122.9736 | 123.3948 | -0.15564 | 123.4268 | 56.5933 | -0.35706 | 123.3948 | -0.15564 | 56.5933 | 122.9736 | 123.4268 | -123.6603 | -123.6053
882.9844 | 123.5687 | -57.6736 | 65.5838 | -0.079243 | -0.02573 | -0.06489 | 0.0034162 | 0.015806 | -0.041096 | 0.066383 | -57.8293 | 65.7623 | -58.0353 | -58.0307 | 65.2954 | -0.9613 | -0.92926 | -0.62256 | 65.7578 | -58.0673 | -0.36163 | 0.17853 | -0.15564 | -0.35706 | -0.28839 | -0.39368 | 0.17395 | 0.20599 | 56.7444 | 57.0511 | 122.9691 | 123.436 | -0.15564 | 123.4314 | 56.7123 | -0.39368 | 123.436 | -0.15564 | 56.7123 | 122.9691 | 123.4314 | -123.6191 | -123.6511
883.9219 | 123.5504 | -57.6965 | 65.5701 | -0.14028 | -0.019321 | -0.049937 | 0.0012792 | 0.027555 | -0.042164 | 0.071723 | -57.8567 | 65.7028 | -58.1177 | -58.0582 | 65.2954 | -0.97046 | -0.87891 | -0.60883 | 65.7669 | -58.0673 | -0.42114 | 0.13275 | -0.16022 | -0.36163 | -0.27466 | -0.37079 | 0.19684 | 0.26093 | 56.8176 | 57.0877 | 122.9919 | 123.3994 | -0.16022 | 123.4634 | 56.7261 | -0.37079 | 123.3994 | -0.16022 | 56.7261 | 122.9919 | 123.4634 | -123.6877 | -123.6374
884.9844 | 123.5092 | -58.0032 | 65.2634 | 0.13438 | -0.018253 | -0.027506 | 0.011961 | 0.026487 | -0.042164 | 0.058906 | -58.2504 | 65.3503 | -58.4381 | -58.3008 | 65.0345 | -0.90637 | -0.97046 | -0.55389 | 65.4373 | -58.3466 | -0.43488 | 0.086975 | -0.24719 | -0.29755 | -0.22888 | -0.34332 | 0.17395 | 0.18768 | 57.0328 | 57.4493 | 123.0377 | 123.3536 | -0.24719 | 123.4406 | 57.0969 | -0.34332 | 123.3536 | -0.24719 | 57.0969 | 123.0377 | 123.4406 | -123.7015 | -123.6099
885.9219 | 123.5458 | -58.4152 | 64.8651 | 0.042827 | -0.0097082 | -0.057413 | -0.0019248 | 0.028623 | -0.033619 | 0.066383 | -58.5434 | 65.0574 | -58.7631 | -58.7265 | 64.6179 | -1.0208 | -0.99335 | -0.61798 | 65.007 | -58.7494 | -0.3479 | 0.19226 | -0.12817 | -0.31128 | -0.24719 | -0.33417 | 0.14191 | 0.21973 | 57.4219 | 57.7972 | 123.0331 | 123.4726 | -0.12817 | 123.4222 | 57.3944 | -0.33417 | 123.4726 | -0.12817 | 57.3944 | 123.0331 | 123.4222 | -123.6282 | -123.6145
886.9844 | 123.4406 | -58.4427 | 64.9063 | 2.6826 | -0.0022312 | -0.029642 | 0.032255 | 0.028623 | -0.015461 | 0.055701 | -58.5251 | 65.1077 | -58.8226 | -58.6395 | 64.6637 | -0.97046 | -1.1307 | -0.5127 | 64.9063 | -58.754 | -0.37994 | 0.20142 | -0.082397 | -0.19684 | -0.24262 | -0.31128 | 0 | 0.29755 | 57.312 | 57.93 | 123.1064 | 123.5504 | -0.082397 | 123.349 | 57.4722 | -0.31128 | 123.5504 | -0.082397 | 57.4722 | 123.1064 | 123.349 | -123.7289 | -123.6603
887.9219 | 123.5413 | -58.8501 | 64.4531 | -0.18605 | -0.020389 | -0.032847 | 0.0076882 | 0.01901 | -0.035755 | 0.071723 | -59.0195 | 64.5813 | -59.2117 | -59.1751 | 64.183 | -1.0574 | -1.0025 | -0.63629 | 64.5859 | -59.1934 | -0.36163 | 0.12817 | -0.16937 | -0.32501 | -0.27008 | -0.34332 | 0.13275 | 0.19226 | 57.8476 | 58.2138 | 123.0331 | 123.4314 | -0.16937 | 123.436 | 57.7927 | -0.34332 | 123.4314 | -0.16937 | 57.7927 | 123.0331 | 123.436 | -123.6649 | -123.6465
888.9844 | 123.642 | -58.8089 | 64.4623 | 0.50059 | -9.5248e-05 | -0.024302 | 0.0066202 | 0.026487 | -0.02187 | 0.053565 | -58.8959 | 64.6912 | -59.1568 | -59.0927 | 64.2334 | -1.1261 | -1.0071 | -0.63171 | 64.6454 | -59.1522 | -0.3479 | 0.22888 | -0.086975 | -0.28381 | -0.22888 | -0.34332 | 0.18311 | 0.26093 | 57.8018 | 58.1772 | 123.0423 | 123.5001 | -0.086975 | 123.4543 | 57.6828 | -0.34332 | 123.5001 | -0.086975 | 57.6828 | 123.0423 | 123.4543 | -123.6191 | -123.6145
889.9219 | 123.5229 | -59.1431 | 64.1098 | -0.29287 | -0.028934 | -0.028574 | 0.0044842 | 0.029691 | -0.031483 | 0.057838 | -59.3994 | 64.3158 | -59.5459 | -59.4269 | 63.9496 | -1.0483 | -1.0345 | -0.62714 | 64.27 | -59.4681 | -0.40283 | 0.20599 | -0.25635 | -0.28381 | -0.16022 | -0.32501 | 0.16022 | 0.14648 | 58.1085 | 58.5159 | 123.0927 | 123.4589 | -0.25635 | 123.4131 | 58.0948 | -0.32501 | 123.4589 | -0.25635 | 58.0948 | 123.0927 | 123.4131 | -123.6557 | -123.5779
890.9844 | 123.5504 | -59.7427 | 63.5376 | 0.37852 | 0.0084498 | -0.020029 | 0.018369 | 0.022214 | -0.0026434 | 0.073859 | -59.8343 | 63.739 | -60.1135 | -60.0357 | 63.2263 | -1.1353 | -0.98877 | -0.65918 | 63.6749 | -60.0723 | -0.37079 | 0.20142 | -0.091553 | -0.29297 | -0.31128 | -0.32959 | 0.13733 | 0.27923 | 58.754 | 59.0836 | 122.9691 | 123.4818 | -0.091553 | 123.4177 | 58.6075 | -0.32959 | 123.4818 | -0.091553 | 58.6075 | 122.9691 | 123.4177 | -123.6511 | -123.6099
891.9219 | 123.4955 | -60.2417 | 63.0157 | 0.4243 | -0.02573 | -0.021098 | -0.0019248 | 0.024351 | -0.029346 | 0.071723 | -60.4294 | 63.1805 | -60.6308 | -60.4843 | 62.9013 | -1.1078 | -1.1124 | -0.70038 | 63.1897 | -60.5804 | -0.3891 | 0.1648 | -0.18768 | -0.24262 | -0.11444 | -0.33875 | 0.17395 | 0.20142 | 59.1293 | 59.5413 | 123.143 | 123.4222 | -0.18768 | 123.4314 | 59.1339 | -0.33875 | 123.4222 | -0.18768 | 59.1339 | 123.143 | 123.4314 | -123.6465 | -123.5962
892.9844 | 123.5092 | -61.1389 | 62.114 | 0.27171 | -0.018253 | -0.036051 | 0.011961 | 0.022214 | -0.02721 | 0.061042 | -61.2396 | 62.3337 | -61.4594 | -61.4365 | 61.9217 | -1.1902 | -1.1169 | -0.70038 | 62.265 | -61.4822 | -0.32043 | 0.21973 | -0.10071 | -0.29755 | -0.19226 | -0.34332 | 0.15106 | 0.21973 | 60.022 | 60.4385 | 123.0606 | 123.4726 | -0.10071 | 123.4039 | 59.9487 | -0.34332 | 123.4726 | -0.10071 | 59.9487 | 123.0606 | 123.4039 | -123.5733 | -123.5962
893.9219 | 123.5275 | -62.4664 | 60.8002 | 0.11912 | -0.02573 | -0.032847 | 0.0034162 | 0.030759 | -0.022938 | 0.069587 | -62.6221 | 60.9695 | -62.8098 | -62.764 | 60.5804 | -1.2314 | -1.2131 | -0.72784 | 60.9055 | -62.8326 | -0.34332 | 0.16937 | -0.15564 | -0.29755 | -0.21973 | -0.36621 | 0.10529 | 0.18768 | 61.2534 | 61.7386 | 123.0469 | 123.436 | -0.15564 | 123.3719 | 61.235 | -0.36621 | 123.436 | -0.15564 | 61.235 | 123.0469 | 123.3719 | -123.6099 | -123.6328
894.9844 | 123.4314 | -62.352 | 60.9238 | 0.36326 | -0.0022312 | -0.02537 | 0.024778 | 0.022214 | -0.011188 | 0.058906 | -62.5214 | 61.1893 | -62.764 | -62.5397 | 60.8963 | -1.1353 | -1.3 | -0.6134 | 61.0611 | -62.645 | -0.41199 | 0.2655 | -0.16937 | -0.18768 | -0.027466 | -0.29297 | 0.13733 | 0.24261 | 61.0519 | 61.7386 | 123.2483 | 123.5413 | -0.16937 | 123.4131 | 61.2167 | -0.29297 | 123.5413 | -0.16937 | 61.2167 | 123.2483 | 123.4131 | -123.6877 | -123.5687
895.9219 | 123.4955 | -63.6566 | 59.5779 | 0.31749 | -0.0086402 | -0.030711 | -0.00085683 | 0.022214 | -0.026142 | 0.061042 | -63.9175 | 59.7061 | -64.1281 | -63.9633 | 59.404 | -1.2589 | -1.181 | -0.70038 | 59.7427 | -64.0457 | -0.4715 | 0.12817 | -0.26093 | -0.3067 | -0.17395 | -0.3891 | 0.16479 | 0.21057 | 62.4756 | 62.9562 | 123.0606 | 123.3627 | -0.26093 | 123.3994 | 62.3978 | -0.3891 | 123.3627 | -0.26093 | 62.3978 | 123.0606 | 123.3994 | -123.7061 | -123.6237
896.9844 | 123.4268 | -66.6779 | 56.6483 | 0.042827 | 0.0052458 | -0.014689 | 0.02905 | 0.037168 | 0.0026966 | 0.065314 | -66.8838 | 56.7947 | -67.1036 | -66.7786 | 56.543 | -0.9201 | -0.22888 | 56.8817 | 56.7352 | -66.9754 | -0.42572 | 0.14648 | -0.20599 | -0.10071 | -0.10529 | -0.29755 | 0.086975 | 0.21973 | 66.449 | 123.5596 | 123.2208 | 123.4726 | -0.20599 | 123.4131 | 65.7578 | -0.29755 | 123.4726 | -0.20599 | 65.7578 | 123.2208 | 123.4131 | -123.7518 | -123.6237
897.9219 | 94.9219 | -93.718 | 29.5395 | 0.45481 | -0.0011632 | -0.036051 | 0.020506 | 0.033964 | -0.015461 | 0.059974 | -93.8095 | 29.6631 | -94.1849 | -93.9789 | 29.4662 | -2.6459 | -1.6663 | 29.5258 | 29.6906 | -94.0887 | -0.46692 | 0.1236 | -0.091552 | -0.26093 | -0.073242 | -0.37079 | 0.15106 | 0.37537 | 92.0517 | 123.2437 | 123.1842 | 123.381 | -0.091552 | 123.4085 | 91.0721 | -0.37079 | 123.381 | -0.091552 | 91.0721 | 123.1842 | 123.4085 | -123.7244 | -123.6282
898.9844 | 123.4543 | -108.3344 | 15.0192 | 0.33274 | -0.0022312 | -0.030711 | 0.036527 | 0.035032 | -0.015461 | 0.063178 | -108.4167 | 15.1291 | -108.7784 | -108.3069 | 15.0604 | -2.6596 | -2.0599 | 15.2069 | 15.1978 | -108.6136 | -0.44403 | 0.10986 | -0.082397 | 0.027466 | 0.041199 | -0.27923 | 0.17853 | 0.36163 | 106.2744 | 123.5413 | 123.3948 | 123.4634 | -0.082397 | 123.5321 | 105.6747 | -0.27923 | 123.4634 | -0.082397 | 105.6747 | 123.3948 | 123.5321 | -123.7976 | -123.6328
899.9219 | 123.5092 | -107.2174 | 16.0309 | 0.4243 | -0.0086402 | -0.036051 | 0.015165 | 0.027555 | -0.033619 | 0.065314 | -107.6431 | 16.0584 | -107.753 | -107.1808 | 16.2872 | -2.7512 | -2.0691 | 15.889 | 16.1911 | -107.7347 | -0.53558 | 0.027466 | -0.42572 | 0.036621 | 0.25635 | -0.51727 | 0.16022 | 0.10986 | 105.1483 | 123.1064 | 123.5046 | 123.2758 | -0.42572 | 123.4085 | 104.4662 | -0.51727 | 123.2758 | -0.42572 | 104.4662 | 123.5046 | 123.4085 | -123.7839 | -123.7656
900.9844 | 123.3948 | -110.4721 | 12.9272 | 0.1649 | 0.0031088 | -0.030711 | 0.045072 | 0.035032 | -0.014393 | 0.05677 | -110.5087 | 13.1561 | -110.82 | -110.5499 | 12.8723 | -2.829 | -2.1927 | 13.1927 | 12.9776 | -110.7147 | -0.3479 | 0.22888 | -0.036621 | -0.07782 | -0.054932 | -0.24262 | 0.050354 | 0.31128 | 108.2794 | 123.6649 | 123.3444 | 123.6282 | -0.036621 | 123.4497 | 107.6431 | -0.24262 | 123.6282 | -0.036621 | 107.6431 | 123.3444 | 123.4497 | -123.7473 | -123.642
901.9219 | 109.1583 | -111.6943 | 11.5448 | 1.0499 | -0.0086402 | -0.054209 | 0.011961 | 0.040372 | -0.018665 | 0.066383 | -111.7081 | 11.7371 | -111.8454 | -112.001 | 11.4441 | -3.0304 | -2.3026 | 11.5494 | 11.7462 | -112.0926 | -0.15106 | 0.19226 | -0.013733 | -0.3067 | -0.10071 | -0.39825 | 0.20142 | 0.13733 | 109.3918 | 123.2437 | 123.1384 | 123.4314 | -0.013733 | 123.4406 | 108.6639 | -0.39825 | 123.4314 | -0.013733 | 108.6639 | 123.1384 | 123.4406 | -123.3902 | -123.6374
902.9844 | 123.5092 | -115.654 | 7.6859 | 0.31749 | -0.017185 | -0.04246 | 0.010892 | 0.024351 | -0.017597 | 0.072791 | -115.7776 | 7.6996 | -116.1026 | -115.9287 | 7.6126 | -3.0029 | -2.2751 | 7.7362 | 7.8323 | -116.0156 | -0.44861 | 0.013733 | -0.1236 | -0.27466 | -0.073242 | -0.36163 | 0.14648 | 0.32501 | 113.3789 | 123.3902 | 123.2666 | 123.3536 | -0.1236 | 123.4863 | 112.6511 | -0.36163 | 123.3536 | -0.1236 | 112.6511 | 123.2666 | 123.4863 | -123.7885 | -123.7015
903.9219 | 123.468 | -115.5533 | 7.7728 | 0.24119 | -0.010776 | -0.022166 | 0.027982 | 0.0361 | -0.025074 | 0.059974 | -115.155 | 8.4412 | -115.6311 | -114.0793 | 7.4936 | -2.9617 | -2.4353 | 7.489 | 8.6792 | -115.8737 | -0.07782 | 0.66833 | 0.39826 | 1.474 | -0.27924 | -0.32043 | 0.90637 | 0.47607 | 113.118 | 123.0423 | 123.0469 | 123.9944 | 0.39826 | 124.2325 | 112.5916 | -0.32043 | 123.9944 | 0.39826 | 112.5916 | 123.0469 | 124.2325 | -123.4039 | -123.6465
904.9844 | 123.3948 | -115.9378 | 7.4844 | 0.82103 | 0.010586 | -0.029642 | 0.030119 | 0.032895 | -0.015461 | 0.063178 | -115.9836 | 7.5073 | -116.3544 | -116.1301 | 7.3059 | -2.3621 | -2.2522 | 7.5531 | 7.5943 | -116.2399 | -0.41657 | 0.022888 | -0.045777 | -0.19226 | -0.17853 | -0.30212 | 0.10986 | 0.37079 | 113.6856 | 123.4909 | 123.2437 | 123.4451 | -0.045777 | 123.5321 | 113.5757 | -0.30212 | 123.4451 | -0.045777 | 113.5757 | 123.2437 | 123.5321 | -123.8388 | -123.7244
905.9219 | 123.5229 | -116.3315 | 6.8893 | 0.43956 | -0.01398 | -0.028574 | 0.02371 | 0.035032 | -0.019733 | 0.088813 | -116.5237 | 7.0129 | -116.7664 | -116.9083 | 6.3217 | -3.1357 | -2.2751 | 6.8253 | 6.9855 | -116.8259 | -0.43488 | 0.1236 | -0.19226 | -0.57678 | -0.56763 | -0.49439 | 0.096131 | 0.24261 | 114.0564 | 123.1567 | 122.6532 | 123.3444 | -0.19226 | 123.317 | 113.1958 | -0.49439 | 123.3444 | -0.19226 | 113.1958 | 122.6532 | 123.317 | -123.6557 | -123.7152
906.9844 | 123.5138 | -116.8716 | 6.5186 | -0.3539 | 0.00097275 | -0.017893 | 0.024778 | 0.044645 | -0.011188 | 0.057838 | -116.9037 | 6.5872 | -117.3431 | -117.0776 | 6.3446 | -2.9251 | -2.3438 | 6.72 | 6.601 | -117.1738 | -0.4715 | 0.068664 | -0.032044 | -0.20599 | -0.17395 | -0.30212 | 0.082397 | 0.43945 | 114.5279 | 123.5916 | 123.2162 | 123.4589 | -0.032044 | 123.4726 | 113.9465 | -0.30212 | 123.4589 | -0.032044 | 113.9465 | 123.2162 | 123.4726 | -123.8617 | -123.6923
907.9219 | 117.9794 | -116.9449 | 6.3171 | 0.24119 | -9.5248e-05 | -0.041392 | 0.036527 | 0.0361 | -0.017597 | 0.069587 | -117.1051 | 6.3354 | -117.5125 | -116.8808 | 6.3446 | -3.1494 | -2.5772 | 6.2164 | 6.601 | -117.3569 | -0.56763 | 0.01831 | -0.16022 | 0.064087 | 0.027465 | -0.41199 | 0.28381 | 0.40741 | 114.3677 | 123.1613 | 123.2895 | 123.2803 | -0.16022 | 123.5458 | 113.7955 | -0.41199 | 123.2803 | -0.16022 | 113.7955 | 123.2895 | 123.5458 | -123.8297 | -123.674
908.9844 | 123.4268 | -117.1051 | 6.2988 | 0.21067 | 0.0020408 | -0.024302 | 0.033323 | 0.040372 | -0.012257 | 0.057838 | -116.9678 | 6.5552 | -117.4026 | -116.9495 | 6.4133 | -2.8152 | -2.655 | 6.3629 | 6.5323 | -117.3569 | -0.29755 | 0.25635 | 0.13733 | 0.15564 | 0.11444 | -0.25177 | 0.23346 | 0.43488 | 114.4501 | 123.468 | 123.5184 | 123.6603 | 0.13733 | 123.6374 | 114.2899 | -0.25177 | 123.6603 | 0.13733 | 114.2899 | 123.5184 | 123.6374 | -123.7015 | -123.6557
909.9219 | 123.4955 | -117.4255 | 5.8136 | 0.48533 | 0.0031088 | -0.043528 | 0.039732 | 0.027555 | -0.016529 | 0.064246 | -117.3523 | 6.0059 | -117.6544 | -117.8604 | 5.5664 | -3.186 | -2.6642 | 5.9601 | 5.9921 | -117.7917 | -0.22888 | 0.19226 | 0.073242 | -0.43488 | -0.24719 | -0.36621 | 0.17853 | 0.30212 | 114.7614 | 123.3856 | 122.9919 | 123.4314 | 0.073242 | 123.4177 | 114.2395 | -0.36621 | 123.4314 | 0.073242 | 114.2395 | 122.9919 | 123.4177 | -123.468 | -123.6053
910.9844 | 123.3856 | -122.1451 | 1.2039 | -0.24709 | -0.0022312 | -0.017893 | 0.060026 | 0.028623 | -0.015461 | 0.064246 | -0.004578 | 1.355 | -0.41199 | -122.2916 | 1.1078 | -2.9022 | -2.4628 | 1.3092 | 1.3504 | -122.4747 | 121.7331 | 0.15106 | 122.1405 | -0.14648 | -0.09613 | -0.32959 | 0.14648 | 0.40741 | 119.6823 | 123.4543 | 123.2529 | 123.5001 | 122.1405 | 123.4955 | 119.2429 | -0.32959 | 123.5001 | 122.1405 | 119.2429 | 123.2529 | 123.4955 | -1.6159 | -123.6786
911.9219 | 123.4131 | -121.6232 | 1.7853 | 0.25645 | 0.010586 | -0.012553 | 0.068571 | 0.032895 | -0.019733 | 0.06211 | -0.15106 | 1.973 | -0.40741 | -121.6919 | 1.7532 | -3.0396 | -2.6642 | 1.973 | 1.8723 | -121.8613 | 121.2158 | 0.18768 | 121.4722 | -0.068665 | -0.032043 | -0.23804 | 0.086975 | 0.25635 | 118.959 | 123.5962 | 123.3765 | 123.5962 | 121.4722 | 123.4955 | 118.5837 | -0.23804 | 123.5962 | 121.4722 | 118.5837 | 123.3765 | 123.4955 | -2.1927 | -123.6465
912.9844 | 123.5596 | -121.7422 | 1.6205 | 0.48533 | -0.0022312 | 0.00026463 | 0.066434 | 0.038236 | -0.022938 | 0.055701 | -0.022888 | 1.8723 | -0.3891 | -121.9208 | 1.5472 | -3.1265 | -2.5818 | 1.68 | 1.7807 | -122.0901 | 121.3531 | 0.25177 | 121.7194 | -0.17853 | -0.073242 | -0.3479 | 0.16022 | 0.36621 | 119.1605 | 123.4222 | 123.2895 | 123.6145 | 121.7194 | 123.5229 | 118.6157 | -0.3479 | 123.6145 | 121.7194 | 118.6157 | 123.2895 | 123.5229 | -2.0096 | -123.7106
913.9219 | 122.9004 | -120.8542 | 2.0233 | 0.50059 | -0.0097082 | 0.0088096 | 0.067503 | -0.029055 | -0.0069164 | 0.03968 | -0.036621 | 2.1744 | -0.38452 | 1.8448 | 2.005 | -1.1948 | -0.65002 | 2.1835 | 2.1515 | -121.1655 | 120.4697 | 0.15106 | 120.8176 | 122.699 | -0.01831 | -0.31128 | 0.12817 | 0.3479 | 120.2042 | 123.0377 | 122.8592 | 123.0286 | 120.8176 | 123.0057 | 119.6594 | -0.31128 | 123.0286 | 120.8176 | 119.6594 | 122.8592 | 123.0057 | -2.4078 | -123.1888
914.9844 | 123.0927 | -120.7718 | 2.2476 | -0.26235 | -0.0022312 | 0.0024006 | 0.083524 | -0.027987 | -0.01012 | 0.03968 | -0.032043 | 2.4078 | -0.42114 | 2.1652 | 2.1606 | -1.355 | -0.09613 | 2.3529 | 2.3666 | -121.106 | 120.3506 | 0.16022 | 120.7397 | 122.937 | -0.086975 | -0.33417 | 0.11902 | 0.3891 | 120.6757 | 123.1247 | 122.9324 | 123.1796 | 120.7397 | 123.1384 | 119.4168 | -0.33417 | 123.1796 | 120.7397 | 119.4168 | 122.9324 | 123.1384 | -2.6688 | -123.3536
915.9219 | 123.0057 | -121.1105 | 1.9501 | 0.51585 | 0.0031088 | 0.022695 | 0.073911 | -0.036532 | -0.0026434 | 0.028999 | -0.027466 | 2.0691 | -0.40283 | 1.918 | 1.918 | -1.4557 | -0.10986 | 2.0828 | 2.0645 | -121.4218 | 120.7077 | 0.11902 | 121.0831 | 123.0286 | -0.032043 | -0.31128 | 0.11444 | 0.37537 | 121.0007 | 123.1934 | 123.0286 | 123.1796 | 121.0831 | 123.175 | 119.6548 | -0.31128 | 123.1796 | 121.0831 | 119.6548 | 123.0286 | 123.175 | -2.3529 | -123.3719
916.9844 | 123.1064 | -121.2982 | 1.8265 | -0.38442 | -0.0097082 | -0.017893 | 0.074979 | -0.0376 | -0.019733 | 0.040748 | -0.050354 | 1.9455 | -0.38452 | 1.7715 | 1.767 | -1.4236 | -0.13275 | 1.9684 | 1.9684 | -121.5775 | 120.9137 | 0.11902 | 121.2479 | 123.0698 | -0.059509 | -0.27924 | 0.14191 | 0.33417 | 121.1655 | 123.2666 | 123.0652 | 123.2437 | 121.2479 | 123.2666 | 119.8746 | -0.27924 | 123.2437 | 121.2479 | 119.8746 | 123.0652 | 123.2666 | -2.211 | -123.4039
917.9219 | 123.1476 | -121.3074 | 1.8219 | 0.027569 | -9.5248e-05 | 0.0056046 | 0.089933 | -0.029055 | -0.012257 | 0.030067 | 0.009155 | 1.9592 | -0.38452 | 1.7899 | 1.767 | -1.8127 | -0.11444 | 1.9318 | 1.9547 | -121.6141 | 120.9229 | 0.13733 | 121.3165 | 123.0972 | -0.054931 | -0.3067 | 0.13275 | 0.39368 | 121.1929 | 123.2391 | 123.0743 | 123.2666 | 121.3165 | 123.262 | 119.4946 | -0.3067 | 123.2666 | 121.3165 | 119.4946 | 123.0743 | 123.262 | -2.2064 | -123.436
918.9844 | 123.1659 | -121.2387 | 1.9226 | -1.1779 | 0.00097275 | 0.0056046 | 0.082456 | -0.022647 | -0.017597 | 0.042884 | -0.054932 | 2.1011 | -0.36163 | 1.8677 | 1.8494 | -1.8906 | -0.12817 | 2.0462 | 2.0462 | -121.5454 | 120.8771 | 0.17853 | 121.1838 | 123.1064 | -0.073242 | -0.3067 | 0.1236 | 0.3067 | 121.1105 | 123.2849 | 123.0881 | 123.3398 | 121.1838 | 123.2849 | 119.3481 | -0.3067 | 123.3398 | 121.1838 | 119.3481 | 123.0881 | 123.2849 | -2.2842 | -123.468
919.9219 | 123.1384 | -121.2936 | 1.8814 | 0.10386 | 0.0020408 | 0.0077416 | 0.086729 | -0.031191 | -0.01012 | 0.049293 | 0.004578 | 2.037 | -0.39368 | 1.8814 | 1.8585 | -1.9684 | -0.12817 | 2.0279 | 2.0416 | -121.5729 | 120.9 | 0.15564 | 121.2982 | 123.175 | -0.022888 | -0.27924 | 0.16022 | 0.39826 | 121.1655 | 123.3215 | 123.1522 | 123.3307 | 121.2982 | 123.3353 | 119.3253 | -0.27924 | 123.3307 | 121.2982 | 119.3253 | 123.1522 | 123.3353 | -2.2751 | -123.4543
920.9844 | 123.2254 | -121.2982 | 1.8631 | -0.21657 | -0.0032992 | -0.0029404 | 0.073911 | -0.036532 | -0.0069164 | 0.041816 | 0.018311 | 2.005 | -0.39368 | 1.8036 | 1.7944 | -2.0416 | -0.064087 | 1.973 | 2.005 | -121.6095 | 120.9045 | 0.14191 | 121.3165 | 123.1018 | -0.068664 | -0.31128 | 0.14191 | 0.41199 | 121.2341 | 123.2712 | 123.0927 | 123.3032 | 121.3165 | 123.3032 | 119.2566 | -0.31128 | 123.3032 | 121.3165 | 119.2566 | 123.0927 | 123.3032 | -2.2568 | -123.4726
921.9219 | 123.1842 | -121.3165 | 1.8631 | 0.14964 | 0.0084498 | -0.010416 | 0.092069 | -0.030123 | -0.0026434 | 0.035407 | -0.009155 | 1.9958 | -0.39825 | 1.8311 | 1.8036 | -2.0416 | -0.13275 | 1.9821 | 1.9821 | -121.6324 | 120.9183 | 0.13275 | 121.3074 | 123.1476 | -0.059509 | -0.31586 | 0.11902 | 0.3891 | 121.1838 | 123.2986 | 123.1201 | 123.3124 | 121.3074 | 123.2986 | 119.2749 | -0.31586 | 123.3124 | 121.3074 | 119.2749 | 123.1201 | 123.2986 | -2.2614 | -123.4955
922.9844 | 123.2025 | -121.3989 | 1.7944 | -0.33864 | -0.0075722 | -0.0082804 | 0.077116 | -0.022647 | -0.0058484 | 0.055701 | -0.022888 | 1.9272 | -0.41199 | 1.7395 | 1.7075 | -2.0782 | -0.1236 | 1.9226 | 1.9272 | -121.701 | 120.9869 | 0.13275 | 121.376 | 123.1384 | -0.086976 | -0.30212 | 0.13275 | 0.3891 | 121.2753 | 123.3215 | 123.1064 | 123.3261 | 121.376 | 123.3261 | 119.3207 | -0.30212 | 123.3261 | 121.376 | 119.3207 | 123.1064 | 123.3261 | -2.2064 | -123.4955
923.9219 | 123.2254 | -121.4859 | 1.6983 | -1.2389 | 0.0020408 | -0.013621 | 0.081388 | -0.029055 | 0.0026966 | 0.042884 | 0.032043 | 1.8906 | -0.31586 | 1.6525 | 1.6113 | -2.1927 | -0.082397 | 1.7899 | 1.8723 | -121.8613 | 121.17 | 0.19226 | 121.5179 | 123.1384 | -0.086975 | -0.37537 | 0.17395 | 0.3479 | 121.4035 | 123.2758 | 123.0972 | 123.3765 | 121.5179 | 123.3582 | 119.2932 | -0.37537 | 123.3765 | 121.5179 | 119.2932 | 123.0972 | 123.3582 | -2.0142 | -123.5596
924.9844 | 123.2025 | -121.6049 | 1.5976 | -0.39968 | -0.0075722 | 0.0034686 | 0.065366 | -0.040805 | -0.02721 | 0.04502 | -0.018311 | 1.7303 | -0.36621 | 1.5427 | 1.5381 | -2.1698 | -0.12817 | 1.7303 | 1.7441 | -121.8887 | 121.2387 | 0.13275 | 121.5866 | 123.1476 | -0.059509 | -0.28381 | 0.14648 | 0.3479 | 121.4767 | 123.3353 | 123.143 | 123.3353 | 121.5866 | 123.349 | 119.4351 | -0.28381 | 123.3353 | 121.5866 | 119.4351 | 123.143 | 123.349 | -1.9638 | -123.4863
925.9219 | 123.2529 | -121.7102 | 1.4923 | -0.36916 | -0.0054352 | 0.019491 | 0.074979 | -0.03226 | -0.014393 | 0.053565 | -0.004578 | 1.6342 | -0.39368 | 1.4282 | 1.4053 | -2.2476 | -0.091553 | 1.5976 | 1.6296 | -122.0215 | 121.3165 | 0.14191 | 121.7056 | 123.1384 | -0.086976 | -0.31128 | 0.13733 | 0.3891 | 121.6187 | 123.3078 | 123.1155 | 123.3444 | 121.7056 | 123.3398 | 119.4626 | -0.31128 | 123.3444 | 121.7056 | 119.4626 | 123.1155 | 123.3398 | -1.886 | -123.5138
926.9844 | 123.349 | -121.7239 | 1.3138 | 0.027569 | -0.024662 | -0.010416 | 0.049345 | -0.034396 | -0.025074 | 0.040748 | -0.13275 | 2.3575 | -0.32959 | 1.2039 | 1.2405 | -2.6093 | 0.050354 | 1.4328 | 1.5747 | -122.1085 | 121.3943 | 1.0437 | 121.5912 | 122.9279 | -0.073242 | -0.38452 | 0.26093 | 0.19684 | 121.7743 | 123.1567 | 122.9645 | 124.0814 | 121.5912 | 123.2986 | 119.1147 | -0.38452 | 124.0814 | 121.5912 | 119.1147 | 122.9645 | 123.2986 | -1.6434 | -123.4222
927.9219 | 123.2574 | -121.8292 | 1.3824 | -0.36916 | -0.0022312 | -0.011485 | 0.076048 | -0.027987 | -0.0058484 | 0.041816 | -0.004578 | 1.5198 | -0.39368 | 1.3367 | 1.2817 | -2.3483 | -0.10071 | 1.4969 | 1.5335 | -122.1451 | 121.4355 | 0.13733 | 121.8246 | 123.1659 | -0.10071 | -0.31586 | 0.15106 | 0.3891 | 121.7285 | 123.3261 | 123.111 | 123.349 | 121.8246 | 123.3627 | 119.4809 | -0.31586 | 123.349 | 121.8246 | 119.4809 | 123.111 | 123.3627 | -1.7761 | -123.5275
928.9844 | 123.3078 | -121.7743 | 1.3733 | -0.38442 | -0.022525 | -0.0018714 | 0.062162 | -0.041873 | -0.022938 | 0.048225 | 0.045776 | 1.474 | -0.33417 | 0.97504 | 1.236 | -2.4124 | 0.045776 | 1.2909 | 1.5564 | -122.1771 | 121.4401 | 0.10071 | 121.8201 | 122.7493 | -0.13733 | -0.40283 | 0.1831 | 0.37994 | 121.8201 | 123.0652 | 123.0103 | 123.2483 | 121.8201 | 123.3307 | 119.3619 | -0.40283 | 123.2483 | 121.8201 | 119.3619 | 123.0103 | 123.3307 | -1.7075 | -123.5504
929.9219 | 123.2529 | -121.8704 | 1.3412 | -0.36916 | -0.0054352 | -0.0093484 | 0.081388 | -0.036532 | -0.011188 | 0.050361 | 0.004578 | 1.5152 | -0.39825 | 1.2909 | 1.236 | -2.4719 | -0.07782 | 1.442 | 1.4832 | -122.1954 | 121.4722 | 0.17395 | 121.875 | 123.1613 | -0.10529 | -0.32501 | 0.14191 | 0.40283 | 121.7926 | 123.3124 | 123.1064 | 123.3856 | 121.875 | 123.3536 | 119.3985 | -0.32501 | 123.3856 | 121.875 | 119.3985 | 123.1064 | 123.3536 | -1.7395 | -123.5367
930.9844 | 123.3398 | -121.8887 | 1.2955 | -0.30813 | -0.0086402 | -0.014689 | 0.055753 | -0.038668 | -0.015461 | 0.043952 | 0.054932 | 1.3824 | -0.34332 | 1.0117 | 1.236 | -2.5909 | -0.041199 | 1.3 | 1.4694 | -122.2687 | 121.5454 | 0.086975 | 121.9437 | 122.9004 | -0.059509 | -0.37994 | 0.17395 | 0.39825 | 121.8475 | 123.1888 | 123.1247 | 123.2712 | 121.9437 | 123.3582 | 119.2978 | -0.37994 | 123.2712 | 121.9437 | 119.2978 | 123.1247 | 123.3582 | -1.6388 | -123.5641
931.9219 | 123.2391 | -121.9574 | 1.2726 | -0.24709 | -0.015048 | -0.0093484 | 0.088865 | -0.042941 | -0.011188 | 0.046088 | -0.013733 | 1.4099 | -0.38452 | 1.2131 | 1.1719 | -2.5543 | -0.1236 | 1.3962 | 1.3916 | -122.2733 | 121.5729 | 0.13733 | 121.9437 | 123.1705 | -0.10071 | -0.31586 | 0.11902 | 0.37079 | 121.8338 | 123.3536 | 123.1293 | 123.3673 | 121.9437 | 123.349 | 119.4031 | -0.31586 | 123.3673 | 121.9437 | 119.4031 | 123.1293 | 123.349 | -1.6571 | -123.5458
932.9219 | 123.2346 | -122.1268 | 1.1353 | -0.048725 | -0.0065042 | -0.013621 | 0.067503 | -0.030123 | -0.030414 | 0.037543 | -0.045776 | 1.2543 | -0.38452 | 1.0712 | 1.062 | -2.5772 | -0.13275 | 1.2497 | 1.2497 | -122.4243 | 121.7422 | 0.11902 | 122.081 | 123.1979 | -0.073242 | -0.29755 | 0.11444 | 0.33875 | 121.994 | 123.3765 | 123.1888 | 123.381 | 122.081 | 123.3765 | 119.5496 | -0.29755 | 123.381 | 122.081 | 119.5496 | 123.1888 | 123.3765 | -1.5198 | -123.5596
933.9844 | 123.3124 | -122.1405 | 1.0895 | -0.4302 | -0.022525 | -0.0093484 | 0.068571 | -0.046145 | -0.028278 | 0.054633 | 0.036621 | 1.1581 | -0.35706 | 0.95673 | 0.94299 | -2.7054 | -0.050354 | 1.1536 | 1.268 | -122.493 | 121.7834 | 0.068664 | 122.1771 | 123.0972 | -0.14648 | -0.35248 | 0.17853 | 0.39368 | 122.0901 | 123.2941 | 123.0835 | 123.2986 | 122.1771 | 123.4085 | 119.4351 | -0.35248 | 123.2986 | 122.1771 | 119.4351 | 123.0835 | 123.4085 | -1.4465 | -123.5825
934.9219 | 123.2391 | -122.1771 | 1.0757 | -0.47597 | -0.018253 | -0.030711 | 0.076048 | -0.046145 | -0.02187 | 0.040748 | -0.045776 | 1.181 | -0.39368 | 1.0254 | 1.0071 | -2.6367 | -0.13733 | 1.2085 | 1.1856 | -122.5113 | 121.7834 | 0.10529 | 122.1313 | 123.2025 | -0.068665 | -0.33417 | 0.10986 | 0.3479 | 122.0398 | 123.3856 | 123.1842 | 123.3582 | 122.1313 | 123.3627 | 119.5404 | -0.33417 | 123.3582 | 122.1313 | 119.5404 | 123.1842 | 123.3627 | -1.4694 | -123.587
935.9844 | 123.3398 | -122.1909 | 1.0025 | 0.088604 | -0.016117 | -0.0072124 | 0.051481 | -0.038668 | -0.02721 | 0.034339 | -0.027466 | 1.1444 | -0.34332 | 0.74616 | 0.87433 | -2.8198 | -0.004578 | 1.0803 | 1.1673 | -122.5342 | 121.8475 | 0.14191 | 122.1634 | 122.937 | -0.12817 | -0.34332 | 0.1648 | 0.31586 | 122.1863 | 123.2712 | 123.0652 | 123.3353 | 122.1634 | 123.3582 | 119.371 | -0.34332 | 123.3353 | 122.1634 | 119.371 | 123.0652 | 123.3582 | -1.3458 | -123.5367
936.9219 | 123.3444 | -122.1497 | 1.1078 | -0.41494 | 0.00097275 | -0.021098 | 0.076048 | -0.036532 | -0.02187 | 0.051429 | -0.045776 | 1.1627 | -0.37994 | 1.0162 | 0.97046 | -2.7466 | -0.15106 | 1.1856 | 1.1581 | -122.5067 | 121.7697 | 0.054932 | 122.1039 | 123.1659 | -0.13733 | -0.35706 | 0.050354 | 0.33417 | 121.9986 | 123.3353 | 123.1201 | 123.3124 | 122.1039 | 123.3078 | 119.4031 | -0.35706 | 123.3124 | 122.1039 | 119.4031 | 123.1201 | 123.3078 | -1.4877 | -123.6145
937.9219 | 123.2803 | -122.2549 | 1.0483 | -0.53701 | -0.0011632 | -0.012553 | 0.079252 | -0.040805 | -0.018665 | 0.038612 | -0.064087 | 1.1673 | -0.38452 | 0.98419 | 0.93842 | -2.8198 | -0.13733 | 1.1719 | 1.1307 | -122.5296 | 121.8704 | 0.11902 | 122.1909 | 123.2391 | -0.10986 | -0.27466 | 0.082397 | 0.32043 | 122.1176 | 123.4268 | 123.1934 | 123.4222 | 122.1909 | 123.3856 | 119.4351 | -0.27466 | 123.4222 | 122.1909 | 119.4351 | 123.1934 | 123.3856 | -1.4328 | -123.5779
938.9844 | 123.3948 | -122.1817 | 1.0025 | -0.063984 | -0.022525 | -0.024302 | 0.058958 | -0.051486 | -0.031483 | 0.04502 | 0.041199 | 1.0941 | -0.32501 | 0.7782 | 0.81482 | -3.0533 | 0.059509 | 0.97504 | 1.1856 | -122.5937 | 121.8567 | 0.091553 | 122.2229 | 122.9599 | -0.18768 | -0.41199 | 0.18311 | 0.36621 | 122.2412 | 123.1567 | 122.9965 | 123.2758 | 122.2229 | 123.3673 | 119.1284 | -0.41199 | 123.2758 | 122.2229 | 119.1284 | 122.9965 | 123.3673 | -1.3275 | -123.5962
939.9219 | 123.349 | -122.2458 | 1.0025 | -1.4831 | -0.023593 | -0.0018714 | 0.077116 | -0.044009 | -0.036823 | 0.036475 | 0.032043 | 1.062 | -0.3479 | 0.82398 | 0.80566 | -3.0258 | 0.013733 | 0.99792 | 1.1856 | -122.5983 | 121.8979 | 0.05951 | 122.2778 | 123.0698 | -0.19684 | -0.35248 | 0.18311 | 0.37994 | 122.2595 | 123.2437 | 123.0515 | 123.3078 | 122.2778 | 123.4314 | 119.22 | -0.35248 | 123.3078 | 122.2778 | 119.22 | 123.0515 | 123.4314 | -1.3504 | -123.6008
940.9844 | 123.3902 | -122.2 | 1.0025 | -0.55227 | -0.018253 | 0.0024006 | 0.069639 | -0.048281 | -0.028278 | 0.040748 | 0.073242 | 1.0895 | -0.33875 | 0.8194 | 0.82398 | -3.1036 | 0.027466 | 0.99792 | 1.1948 | -122.5845 | 121.8613 | 0.086976 | 122.2733 | 123.0194 | -0.17853 | -0.38452 | 0.19226 | 0.41199 | 122.2275 | 123.1979 | 123.024 | 123.2895 | 122.2733 | 123.3948 | 119.0964 | -0.38452 | 123.2895 | 122.2733 | 119.0964 | 123.024 | 123.3948 | -1.3412 | -123.587
941.9219 | 123.3078 | -122.2641 | 1.0254 | -0.27761 | 0.0020408 | -0.0082804 | 0.084592 | -0.042941 | -0.011188 | 0.048225 | -0.013733 | 1.1673 | -0.37994 | 0.97504 | 0.91095 | -3.0441 | -0.13275 | 1.0895 | 1.1444 | -122.5708 | 121.8842 | 0.14191 | 122.2504 | 123.2391 | -0.11444 | -0.3067 | 0.11902 | 0.36621 | 122.1313 | 123.3536 | 123.175 | 123.4314 | 122.2504 | 123.4085 | 119.22 | -0.3067 | 123.4314 | 122.2504 | 119.22 | 123.175 | 123.4085 | -1.4053 | -123.5962
942.9844 | 123.3536 | -122.2412 | 1.0254 | 0.24119 | -0.012912 | -0.031779 | 0.066434 | -0.048281 | -0.029346 | 0.034339 | -0.009155 | 1.1124 | -0.33875 | 0.87433 | 0.89264 | -3.1952 | -0.032043 | 1.0666 | 1.1581 | -122.5937 | 121.9025 | 0.086975 | 122.2321 | 123.1155 | -0.13275 | -0.35248 | 0.13275 | 0.32959 | 122.2092 | 123.3078 | 123.1339 | 123.3536 | 122.2321 | 123.3994 | 119.046 | -0.35248 | 123.3536 | 122.2321 | 119.046 | 123.1339 | 123.3994 | -1.3641 | -123.6191
943.9219 | 123.2986 | -122.2733 | 1.0117 | -0.44545 | -0.018253 | -0.0072124 | 0.081388 | -0.042941 | -0.024006 | 0.037543 | 0.018311 | 1.1124 | -0.33875 | 0.91095 | 0.89264 | -3.1769 | -0.068665 | 1.0712 | 1.149 | -122.5937 | 121.9345 | 0.10071 | 122.2916 | 123.1842 | -0.11902 | -0.32044 | 0.13733 | 0.35706 | 122.2046 | 123.3444 | 123.1659 | 123.3856 | 122.2916 | 123.4222 | 119.0964 | -0.32044 | 123.3856 | 122.2916 | 119.0964 | 123.1659 | 123.4222 | -1.3504 | -123.6053
944.9219 | 123.3032 | -122.2687 | 0.99335 | 0.10386 | -0.010776 | -0.017893 | 0.076048 | -0.047213 | -0.015461 | 0.036475 | -0.009155 | 1.1398 | -0.37994 | 0.98877 | 0.94757 | -3.2501 | -0.082397 | 1.1078 | 1.1307 | -122.58 | 121.8887 | 0.14648 | 122.2595 | 123.2574 | -0.045776 | -0.31128 | 0.13733 | 0.37079 | 122.1863 | 123.3765 | 123.2162 | 123.4085 | 122.2595 | 123.3994 | 119.0186 | -0.31128 | 123.4085 | 122.2595 | 119.0186 | 123.2162 | 123.3994 | -1.3733 | -123.5733
945.9219 | 123.3627 | -122.2229 | 1.0254 | -0.26235 | -0.018253 | -0.010416 | 0.065366 | -0.047213 | -0.025074 | 0.038612 | 0.036621 | 1.1124 | -0.35248 | 0.87891 | 0.87433 | -3.36 | -0.013733 | 1.0437 | 1.2039 | -122.5662 | 121.8704 | 0.086975 | 122.2595 | 123.1018 | -0.15106 | -0.34332 | 0.17853 | 0.3891 | 122.2092 | 123.2666 | 123.0972 | 123.3353 | 122.2595 | 123.4268 | 118.8629 | -0.34332 | 123.3353 | 122.2595 | 118.8629 | 123.0972 | 123.4268 | -1.3779 | -123.5916
946.9844 | 123.4039 | -122.2046 | 1.0071 | -3.7108 | -0.022525 | -0.0018714 | 0.065366 | -0.049349 | -0.026142 | 0.058906 | -0.041199 | 1.062 | -0.37994 | 0.84228 | 0.84228 | -3.5019 | 0.036621 | 1.0071 | 1.1765 | -122.6028 | 121.8246 | 0.054932 | 122.1634 | 123.0469 | -0.1648 | -0.39825 | 0.16937 | 0.33875 | 122.2412 | 123.2117 | 123.0469 | 123.2666 | 122.1634 | 123.381 | 118.7027 | -0.39825 | 123.2666 | 122.1634 | 118.7027 | 123.0469 | 123.381 | -1.387 | -123.6099
947.9219 | 123.381 | -122.2412 | 0.99335 | -0.30813 | -0.012912 | -0.0478 | 0.065366 | -0.048281 | -0.022938 | 0.050361 | 0.064087 | 1.0529 | -0.36163 | 0.77362 | 0.85144 | -3.5385 | 0 | 0.97961 | 1.1673 | -122.6074 | 121.8796 | 0.059509 | 122.3053 | 123.0148 | -0.14191 | -0.36621 | 0.17395 | 0.42572 | 122.2412 | 123.2208 | 123.0927 | 123.2941 | 122.3053 | 123.4085 | 118.7027 | -0.36621 | 123.2941 | 122.3053 | 118.7027 | 123.0927 | 123.4085 | -1.355 | -123.6008
948.9844 | 123.3627 | -122.2595 | 0.9613 | 0.33274 | -0.0075722 | -0.018961 | 0.072843 | -0.046145 | -0.025074 | 0.043952 | 0.041199 | 1.0529 | -0.32959 | 0.83313 | 0.83313 | -3.6667 | 0.041199 | 0.98877 | 1.1581 | -122.5891 | 121.9299 | 0.091552 | 122.3007 | 123.0927 | -0.12817 | -0.32959 | 0.19684 | 0.37079 | 122.3007 | 123.2483 | 123.0927 | 123.3124 | 122.3007 | 123.4177 | 118.5928 | -0.32959 | 123.3124 | 122.3007 | 118.5928 | 123.0927 | 123.4177 | -1.2909 | -123.5504
949.9219 | 123.3627 | -122.2595 | 0.97504 | 0.50059 | -0.0022312 | 0.0024006 | 0.073911 | -0.041873 | -0.014393 | 0.03968 | 0.027466 | 1.0803 | -0.37079 | 0.86975 | 0.85144 | -3.7262 | 0.009155 | 1.0025 | 1.1215 | -122.6166 | 121.8887 | 0.10528 | 122.287 | 123.1293 | -0.1236 | -0.35706 | 0.14648 | 0.39825 | 122.2687 | 123.262 | 123.111 | 123.3398 | 122.287 | 123.381 | 118.5333 | -0.35706 | 123.3398 | 122.287 | 118.5333 | 123.111 | 123.381 | -1.3458 | -123.5916
950.9844 | 123.3673 | -122.2733 | 0.97046 | 0.37852 | -0.011844 | -0.026438 | 0.077116 | -0.052554 | -0.02721 | 0.030067 | 0.004578 | 1.062 | -0.31586 | 0.84228 | 0.84686 | -3.8452 | -0.009155 | 1.0208 | 1.1398 | -122.6166 | 121.9574 | 0.091553 | 122.2778 | 123.1155 | -0.1236 | -0.34332 | 0.16937 | 0.32044 | 122.2641 | 123.2941 | 123.1201 | 123.3353 | 122.2778 | 123.4131 | 118.428 | -0.34332 | 123.3353 | 122.2778 | 118.428 | 123.1201 | 123.4131 | -1.2863 | -123.587
951.9219 | 123.3307 | -122.2778 | 0.97961 | -0.47597 | -0.017185 | -0.015757 | 0.06323 | -0.052554 | -0.024006 | 0.037543 | 0.018311 | 1.0757 | -0.33875 | 0.86975 | 0.85144 | -3.8315 | -0.073242 | 1.0574 | 1.1536 | -122.6257 | 121.9391 | 0.096131 | 122.2961 | 123.1476 | -0.12817 | -0.3479 | 0.17395 | 0.35706 | 122.2046 | 123.3353 | 123.1293 | 123.3536 | 122.2961 | 123.4314 | 118.4464 | -0.3479 | 123.3536 | 122.2961 | 118.4464 | 123.1293 | 123.4314 | -1.3184 | -123.6053
952.9844 | 123.3856 | -122.2504 | 0.99792 | -0.048725 | -0.015048 | -0.041392 | 0.072843 | -0.045077 | -0.032551 | 0.053565 | -0.004578 | 1.0849 | -0.33417 | 0.81024 | 0.83771 | -3.9505 | 0.018311 | 1.0208 | 1.1765 | -122.6028 | 121.9162 | 0.086975 | 122.2458 | 123.0606 | -0.16022 | -0.35248 | 0.17853 | 0.32959 | 122.2687 | 123.2712 | 123.0881 | 123.3353 | 122.2458 | 123.4268 | 118.2999 | -0.35248 | 123.3353 | 122.2458 | 118.2999 | 123.0881 | 123.4268 | -1.3321 | -123.6008
953.9219 | 123.4039 | -122.2916 | 0.95215 | -0.44545 | -0.021457 | -0.023234 | 0.076048 | -0.047213 | -0.040028 | 0.038612 | 0.036621 | 1.0529 | -0.33875 | 0.78278 | 0.78278 | -4.0146 | 0.027466 | 0.9613 | 1.1581 | -122.6669 | 121.9528 | 0.10071 | 122.3282 | 123.0743 | -0.16937 | -0.37537 | 0.20599 | 0.37537 | 122.319 | 123.2529 | 123.0743 | 123.3444 | 122.3282 | 123.4497 | 118.277 | -0.37537 | 123.3444 | 122.3282 | 118.277 | 123.0743 | 123.4497 | -1.2909 | -123.6191
954.9844 | 123.3307 | -122.2916 | 1.0391 | -0.079243 | -0.0022312 | -0.0072124 | 0.10596 | -0.045077 | -0.022938 | 0.036475 | 0.045776 | 1.1261 | -0.35706 | 0.99792 | 0.87891 | -3.9871 | -0.045776 | 1.0941 | 1.1765 | -122.5937 | 121.9345 | 0.086975 | 122.3373 | 123.2895 | -0.16022 | -0.30212 | 0.13733 | 0.40283 | 122.2458 | 123.3856 | 123.1705 | 123.4177 | 122.3373 | 123.468 | 118.3044 | -0.30212 | 123.4177 | 122.3373 | 118.3044 | 123.1705 | 123.468 | -1.3962 | -123.6328
955.9219 | 123.3032 | -122.2824 | 1.0345 | -0.33864 | -0.01398 | -0.020029 | 0.077116 | -0.041873 | -0.020801 | 0.041816 | -0.041199 | 1.1169 | -0.37079 | 0.97961 | 0.93842 | -3.9505 | -0.14648 | 1.1398 | 1.1353 | -122.5845 | 121.9116 | 0.082397 | 122.2412 | 123.262 | -0.09613 | -0.30212 | 0.10071 | 0.32959 | 122.1359 | 123.4222 | 123.2208 | 123.3994 | 122.2412 | 123.4177 | 118.3319 | -0.30212 | 123.3994 | 122.2412 | 118.3319 | 123.2208 | 123.4177 | -1.4053 | -123.6191
956.9844 | 123.4131 | -122.2275 | 0.97046 | 0.47007 | -0.016117 | 0.010946 | 0.076048 | -0.048281 | -0.0090524 | 0.049293 | 0.059509 | 1.0849 | -0.32501 | 0.82855 | 0.8606 | -4.1336 | 0.050354 | 0.99335 | 1.1444 | -122.6303 | 121.9025 | 0.11444 | 122.287 | 123.056 | -0.10986 | -0.40283 | 0.17395 | 0.38452 | 122.2778 | 123.2208 | 123.0881 | 123.3124 | 122.287 | 123.3719 | 118.0939 | -0.40283 | 123.3124 | 122.287 | 118.0939 | 123.0881 | 123.3719 | -1.2955 | -123.6008
957.9219 | 123.4589 | -122.2687 | 0.95215 | -0.063984 | -0.023593 | -0.041392 | 0.048277 | -0.058962 | -0.0443 | 0.041816 | 0.082397 | 1.0529 | -0.33875 | 0.75989 | 0.76904 | -4.1153 | 0.027466 | 0.98419 | 1.1536 | -122.6486 | 121.9299 | 0.10071 | 122.3511 | 123.0286 | -0.1831 | -0.37994 | 0.20142 | 0.42114 | 122.2961 | 123.2529 | 123.0377 | 123.3215 | 122.3511 | 123.4222 | 118.1534 | -0.37994 | 123.3215 | 122.3511 | 118.1534 | 123.0377 | 123.4222 | -1.2909 | -123.6008
958.9844 | 123.4177 | -122.2916 | 0.9613 | 0.53111 | -9.5248e-05 | 0.010946 | 0.088865 | -0.051486 | -0.016529 | 0.055701 | 0.027466 | 1.0895 | -0.35248 | 0.86975 | 0.87433 | -4.1153 | 0.018311 | 1.0071 | 1.1536 | -122.6166 | 121.9391 | 0.12817 | 122.319 | 123.1613 | -0.086975 | -0.32501 | 0.19226 | 0.37994 | 122.3099 | 123.2986 | 123.1659 | 123.381 | 122.319 | 123.4451 | 118.1763 | -0.32501 | 123.381 | 122.319 | 118.1763 | 123.1659 | 123.4451 | -1.3138 | -123.5779
959.9219 | 123.3261 | -122.3099 | 0.97046 | -0.24709 | -0.0086402 | -0.015757 | 0.076048 | -0.038668 | -0.0079844 | 0.053565 | 0.004578 | 1.0986 | -0.38452 | 0.94299 | 0.88806 | -3.9963 | -0.086975 | 1.0757 | 1.1169 | -122.612 | 121.9254 | 0.12817 | 122.3145 | 123.2529 | -0.082397 | -0.30212 | 0.14648 | 0.3891 | 122.2229 | 123.3856 | 123.1979 | 123.4085 | 122.3145 | 123.4268 | 118.3136 | -0.30212 | 123.4085 | 122.3145 | 118.3136 | 123.1979 | 123.4268 | -1.355 | -123.5825
960.9844 | 123.3444 | -122.2916 | 0.99792 | 0.53111 | -0.0032992 | -0.0061444 | 0.088865 | -0.03226 | -0.02187 | 0.033271 | -0.027466 | 1.1169 | -0.35706 | 0.96588 | 0.93384 | -3.9871 | -0.068665 | 1.1032 | 1.1307 | -122.6212 | 121.9345 | 0.11902 | 122.2641 | 123.2574 | -0.064087 | -0.32959 | 0.13275 | 0.32959 | 122.2229 | 123.3948 | 123.2254 | 123.4085 | 122.2641 | 123.4222 | 118.3044 | -0.32959 | 123.4085 | 122.2641 | 118.3044 | 123.2254 | 123.4222 | -1.355 | -123.6191
961.9219 | 123.4039 | -122.2687 | 0.97961 | -0.10976 | -0.024662 | -0.0072124 | 0.058958 | -0.046145 | -0.034687 | 0.05677 | 0.004578 | 1.0712 | -0.36163 | 0.81024 | 0.84228 | -4.0695 | 0.009155 | 1.0208 | 1.149 | -122.6395 | 121.907 | 0.091553 | 122.2733 | 123.0789 | -0.13733 | -0.37079 | 0.16937 | 0.36621 | 122.2778 | 123.2895 | 123.111 | 123.3398 | 122.2733 | 123.4177 | 118.1992 | -0.37079 | 123.3398 | 122.2733 | 118.1992 | 123.111 | 123.4177 | -1.3412 | -123.6191
962.9844 | 123.3948 | -122.2961 | 0.97961 | 0.37852 | -0.0086402 | -0.00080337 | 0.052549 | -0.051486 | -0.028278 | 0.037543 | 0.013733 | 1.0941 | -0.34332 | 0.86975 | 0.86975 | -3.8956 | 0.009155 | 1.0391 | 1.1581 | -122.6486 | 121.9528 | 0.11444 | 122.3099 | 123.1659 | -0.10986 | -0.35248 | 0.17853 | 0.35706 | 122.3053 | 123.3353 | 123.1659 | 123.3902 | 122.3099 | 123.4543 | 118.4006 | -0.35248 | 123.3902 | 122.3099 | 118.4006 | 123.1659 | 123.4543 | -1.3229 | -123.6282
963.9219 | 123.4131 | -122.2549 | 0.97504 | -0.094502 | -0.010776 | -0.028574 | 0.062162 | -0.053622 | -0.033619 | 0.048225 | 0 | 1.0757 | -0.3479 | 0.8194 | 0.81482 | -4.0329 | 0.013733 | 1.0117 | 1.1536 | -122.6486 | 121.907 | 0.10071 | 122.2549 | 123.0743 | -0.16022 | -0.39368 | 0.17853 | 0.3479 | 122.2687 | 123.2666 | 123.0698 | 123.3307 | 122.2549 | 123.4085 | 118.222 | -0.39368 | 123.3307 | 122.2549 | 118.222 | 123.0698 | 123.4085 | -1.3229 | -123.6237
964.9844 | 123.4314 | -122.2595 | 1.0071 | 0.073345 | -0.017185 | -0.013621 | 0.064298 | -0.051486 | -0.031483 | 0.03968 | 0.004578 | 1.1124 | -0.33417 | 0.8606 | 0.85144 | -4.1061 | 0.009155 | 1.0391 | 1.1673 | -122.6257 | 121.9254 | 0.10529 | 122.2641 | 123.1201 | -0.15564 | -0.36621 | 0.16022 | 0.33875 | 122.2687 | 123.2986 | 123.111 | 123.3719 | 122.2641 | 123.4268 | 118.1534 | -0.36621 | 123.3719 | 122.2641 | 118.1534 | 123.111 | 123.4268 | -1.3412 | -123.6328
965.9219 | 123.3765 | -122.2458 | 0.99792 | 0.10386 | -0.016117 | -0.0072124 | 0.079252 | -0.047213 | -0.029346 | 0.047157 | -0.004578 | 1.1032 | -0.33417 | 0.87891 | 0.88348 | -4.1748 | -0.009155 | 1.0712 | 1.1673 | -122.5937 | 121.9116 | 0.10529 | 122.2412 | 123.1247 | -0.11444 | -0.3479 | 0.16937 | 0.32959 | 122.2366 | 123.317 | 123.1293 | 123.349 | 122.2412 | 123.4131 | 118.071 | -0.3479 | 123.349 | 122.2412 | 118.071 | 123.1293 | 123.4131 | -1.3321 | -123.5916
966.9844 | 123.4222 | -122.2916 | 0.95673 | 0.4243 | -0.0065042 | -0.030711 | 0.09741 | -0.051486 | -0.019733 | 0.047157 | 0.032043 | 1.0941 | -0.34332 | 0.8606 | 0.82398 | -4.2618 | 0.041199 | 1.0071 | 1.1398 | -122.644 | 121.9482 | 0.13733 | 122.3236 | 123.1522 | -0.13275 | -0.35248 | 0.18311 | 0.37537 | 122.3328 | 123.2986 | 123.1155 | 123.3856 | 122.3236 | 123.4314 | 118.0298 | -0.35248 | 123.3856 | 122.3236 | 118.0298 | 123.1155 | 123.4314 | -1.3 | -123.6008
967.9219 | 123.3765 | -122.3373 | 0.97961 | 0.088604 | -0.012912 | -0.036051 | 0.058958 | -0.051486 | -0.031483 | 0.049293 | 0.004578 | 1.0803 | -0.3479 | 0.87433 | 0.85144 | -4.248 | -0.018311 | 1.03 | 1.1536 | -122.6532 | 121.9894 | 0.10071 | 122.3419 | 123.2117 | -0.12817 | -0.31586 | 0.17395 | 0.35248 | 122.319 | 123.3673 | 123.1888 | 123.4177 | 122.3419 | 123.4909 | 118.0893 | -0.31586 | 123.4177 | 122.3419 | 118.0893 | 123.1888 | 123.4909 | -1.3275 | -123.6328
968.9844 | 123.3719 | -122.3099 | 0.96588 | 0.43956 | -0.0043672 | -0.0029404 | 0.084592 | -0.057894 | -0.0026434 | 0.040748 | -0.018311 | 1.0895 | -0.37994 | 0.92926 | 0.89722 | -4.2664 | -0.050354 | 1.062 | 1.1215 | -122.6532 | 121.9299 | 0.1236 | 122.2916 | 123.2391 | -0.068664 | -0.34332 | 0.15564 | 0.36163 | 122.2595 | 123.3719 | 123.2071 | 123.3994 | 122.2916 | 123.4314 | 118.0435 | -0.34332 | 123.3994 | 122.2916 | 118.0435 | 123.2071 | 123.4314 | -1.3458 | -123.6191
969.9219 | 123.4497 | -122.3373 | 0.94757 | 0.14964 | -0.021457 | -0.036051 | 0.06323 | -0.051486 | -0.034687 | 0.042884 | -0.009155 | 1.062 | -0.33875 | 0.80109 | 0.81024 | -4.2526 | 0.009155 | 0.99335 | 1.1398 | -122.6761 | 121.9986 | 0.11444 | 122.3282 | 123.1384 | -0.13733 | -0.33875 | 0.19226 | 0.32959 | 122.3465 | 123.3307 | 123.1476 | 123.3994 | 122.3282 | 123.4772 | 118.0847 | -0.33875 | 123.3994 | 122.3282 | 118.0847 | 123.1476 | 123.4772 | -1.2863 | -123.6237
970.9844 | 123.3261 | -122.3923 | 0.95215 | -1.5288 | 0.0041778 | 0.0077416 | 0.08032 | -0.039736 | -0.013325 | 0.042884 | -0.032043 | 1.0849 | -0.35248 | 0.95215 | 0.88806 | -3.9047 | -0.09613 | 1.0712 | 1.062 | -122.6578 | 122.0398 | 0.13275 | 122.3602 | 123.3444 | -0.064086 | -0.2655 | 0.10986 | 0.32044 | 122.2961 | 123.4634 | 123.2803 | 123.4772 | 122.3602 | 123.4543 | 118.4875 | -0.2655 | 123.4772 | 122.3602 | 118.4875 | 123.2803 | 123.4543 | -1.3046 | -123.6099
971.9219 | 123.381 | -122.3419 | 0.93384 | 0.53111 | -0.021457 | -0.016825 | 0.060026 | -0.045077 | -0.025074 | 0.04502 | 0 | 1.0254 | -0.33417 | 0.79651 | 0.82398 | -4.2526 | -0.032043 | 1.0025 | 1.0986 | -122.699 | 122.0078 | 0.091553 | 122.3419 | 123.1384 | -0.10986 | -0.35706 | 0.1648 | 0.33417 | 122.3099 | 123.3444 | 123.1659 | 123.3673 | 122.3419 | 123.4406 | 118.0893 | -0.35706 | 123.3673 | 122.3419 | 118.0893 | 123.1659 | 123.4406 | -1.268 | -123.6328
972.9844 | 123.468 | -122.3694 | 0.89264 | 0.4243 | -0.0054352 | -0.034983 | 0.079252 | -0.046145 | -0.0090524 | 0.03968 | 0.064087 | 1.0117 | -0.32501 | 0.62714 | 0.88348 | -4.2984 | -0.022888 | 0.90637 | 1.0483 | -122.7585 | 122.0444 | 0.11902 | 122.4335 | 122.9965 | -0.009155 | -0.3891 | 0.15564 | 0.3891 | 122.3465 | 123.2758 | 123.2529 | 123.381 | 122.4335 | 123.4177 | 118.071 | -0.3891 | 123.381 | 122.4335 | 118.071 | 123.2529 | 123.4177 | -1.2177 | -123.6511
973.9219 | 123.4314 | -122.3648 | 0.9201 | 0.48533 | -0.020389 | -0.013621 | 0.066434 | -0.040805 | -0.034687 | 0.050361 | 0.027466 | 0.96588 | -0.37537 | 0.76446 | 0.75989 | -4.2755 | 0.050354 | 0.92926 | 1.0941 | -122.7448 | 121.9894 | 0.045776 | 122.3923 | 123.1293 | -0.16022 | -0.37994 | 0.17395 | 0.40283 | 122.4152 | 123.2941 | 123.1247 | 123.3307 | 122.3923 | 123.4589 | 118.0893 | -0.37994 | 123.3307 | 122.3923 | 118.0893 | 123.1247 | 123.4589 | -1.2955 | -123.6649
974.9844 | 123.3307 | -122.4335 | 0.92926 | 0.18016 | 0.0041778 | -0.0093484 | 0.096342 | -0.039736 | -0.011188 | 0.04502 | 0 | 1.0666 | -0.37994 | 0.93842 | 0.87433 | -4.2984 | -0.1236 | 1.0483 | 1.0574 | -122.731 | 122.0535 | 0.13733 | 122.4335 | 123.3719 | -0.054931 | -0.29755 | 0.12817 | 0.37994 | 122.3099 | 123.4818 | 123.3078 | 123.5001 | 122.4335 | 123.4909 | 118.1351 | -0.29755 | 123.5001 | 122.4335 | 118.1351 | 123.3078 | 123.4909 | -1.3092 | -123.6603
975.9219 | 123.4039 | -122.374 | 0.92926 | 0.088604 | -0.012912 | -0.014689 | 0.058958 | -0.050418 | -0.038959 | 0.053565 | -0.036621 | 1.0208 | -0.36621 | 0.76904 | 0.79193 | -4.6143 | -0.022888 | 0.97504 | 1.0391 | -122.7127 | 122.0078 | 0.091553 | 122.3373 | 123.143 | -0.13733 | -0.33875 | 0.10986 | 0.32959 | 122.3511 | 123.349 | 123.1659 | 123.3948 | 122.3373 | 123.4131 | 117.7597 | -0.33875 | 123.3948 | 122.3373 | 117.7597 | 123.1659 | 123.4131 | -1.2955 | -123.642
976.9688 | 123.3719 | -122.4197 | 0.92468 | -0.36916 | 0.010586 | -0.0082804 | 0.087797 | -0.042941 | -0.016529 | 0.047157 | -0.018311 | 1.0712 | -0.37994 | 0.89264 | 0.82855 | -4.0878 | -0.09613 | 1.0162 | 1.0666 | -122.7173 | 122.0398 | 0.14648 | 122.4014 | 123.3124 | -0.096131 | -0.29755 | 0.14191 | 0.36163 | 122.3236 | 123.436 | 123.2483 | 123.4909 | 122.4014 | 123.4863 | 118.3319 | -0.29755 | 123.4909 | 122.4014 | 118.3319 | 123.2483 | 123.4863 | -1.3046 | -123.642
977.9219 | 123.4222 | -122.3648 | 0.91553 | 0.31749 | -0.018253 | -0.0072124 | 0.072843 | -0.048281 | -0.030414 | 0.037543 | 0.009155 | 1.0162 | -0.34332 | 0.78735 | 0.81482 | -3.7445 | 0 | 0.98419 | 1.0986 | -122.7264 | 122.0215 | 0.10071 | 122.374 | 123.1522 | -0.10071 | -0.36163 | 0.18311 | 0.35248 | 122.3648 | 123.349 | 123.1796 | 123.381 | 122.374 | 123.4634 | 118.6203 | -0.36163 | 123.381 | 122.374 | 118.6203 | 123.1796 | 123.4634 | -1.2589 | -123.642
978.9844 | 123.4406 | -122.3373 | 0.9201 | 1.0652 | -0.0043672 | 0.012014 | 0.069639 | -0.052554 | -0.02187 | 0.03968 | 0.054932 | 0.99792 | -0.36621 | 0.75989 | 0.78278 | -3.7125 | 0.036621 | 0.92926 | 1.0803 | -122.7448 | 121.9711 | 0.07782 | 122.3923 | 123.0972 | -0.13733 | -0.40741 | 0.16022 | 0.42114 | 122.374 | 123.2666 | 123.1201 | 123.3353 | 122.3923 | 123.4177 | 118.6249 | -0.40741 | 123.3353 | 122.3923 | 118.6249 | 123.1201 | 123.4177 | -1.2863 | -123.6649
979.9219 | 123.5138 | -122.3877 | 0.86975 | 0.47007 | -0.011844 | -0.0040084 | 0.083524 | -0.050418 | -0.018665 | 0.042884 | 0.041199 | 1.0254 | -0.33875 | 0.79193 | 0.78278 | -3.6118 | 0.027466 | 0.81482 | 1.1078 | -122.7722 | 122.0489 | 0.15564 | 122.4289 | 123.1796 | -0.086975 | -0.38452 | 0.23804 | 0.37994 | 122.4152 | 123.2025 | 123.1705 | 123.4131 | 122.4289 | 123.4955 | 118.7759 | -0.38452 | 123.4131 | 122.4289 | 118.7759 | 123.1705 | 123.4955 | -1.2085 | -123.642
980.9844 | 123.3398 | -122.3969 | 0.9613 | 0.4243 | -0.0097082 | -0.020029 | 0.091001 | -0.039736 | -0.013325 | 0.043952 | -0.022888 | 1.0941 | -0.36163 | 0.97046 | 0.91553 | -3.2318 | -0.11902 | 1.1032 | 1.062 | -122.6761 | 122.0352 | 0.13275 | 122.374 | 123.3673 | -0.045777 | -0.27923 | 0.10071 | 0.33874 | 122.2778 | 123.5001 | 123.3124 | 123.4909 | 122.374 | 123.4589 | 119.165 | -0.27923 | 123.4909 | 122.374 | 119.165 | 123.3124 | 123.4589 | -1.3229 | -123.6374
981.9219 | 123.4589 | -122.3648 | 0.91095 | 0.69895 | -0.01398 | -0.012553 | 0.071775 | -0.05469 | -0.018665 | 0.034339 | 0.14648 | 0.96588 | -0.36621 | 0.80109 | 0.78278 | -3.4882 | 0.045776 | 0.95215 | 1.0941 | -122.7493 | 121.9986 | 0.054931 | 122.5113 | 123.1659 | -0.12817 | -0.38452 | 0.1831 | 0.5127 | 122.4106 | 123.317 | 123.1476 | 123.3307 | 122.5113 | 123.4589 | 118.8766 | -0.38452 | 123.3307 | 122.5113 | 118.8766 | 123.1476 | 123.4589 | -1.2772 | -123.6603
982.9844 | 123.3902 | -122.3969 | 0.93842 | 0.45481 | -0.0043672 | -0.0029404 | 0.073911 | -0.035464 | -0.011188 | 0.038612 | -0.013733 | 1.0666 | -0.37079 | 0.88348 | 0.85602 | -3.3005 | -0.045776 | 1.0162 | 1.0757 | -122.7264 | 122.0261 | 0.12817 | 122.3831 | 123.2803 | -0.082398 | -0.32959 | 0.13733 | 0.35706 | 122.3511 | 123.4131 | 123.2529 | 123.4634 | 122.3831 | 123.4726 | 119.0964 | -0.32959 | 123.4634 | 122.3831 | 119.0964 | 123.2529 | 123.4726 | -1.3092 | -123.6649
983.9219 | 123.4451 | -122.4289 | 0.85144 | 0.073345 | -0.021457 | -0.0093484 | 0.054685 | -0.051486 | -0.029346 | 0.047157 | -0.036621 | 1.0437 | -0.33417 | 0.79651 | 0.81024 | -3.3142 | -0.36163 | 0.82398 | 1.0529 | -122.7814 | 122.0947 | 0.19226 | 122.3923 | 123.2254 | -0.041198 | -0.35248 | 0.20142 | 0.29755 | 122.0673 | 123.2529 | 123.2391 | 123.4726 | 122.3923 | 123.4818 | 119.1147 | -0.35248 | 123.4726 | 122.3923 | 119.1147 | 123.2391 | 123.4818 | -1.1856 | -123.6328
984.9844 | 123.3307 | -122.4289 | 0.93384 | 0.1649 | -0.0086402 | -0.012553 | 0.095274 | -0.045077 | -0.0037124 | 0.040748 | 0 | 1.0712 | -0.37537 | 0.93384 | 0.87891 | -3.1311 | -0.11444 | 1.062 | 1.0483 | -122.7493 | 122.0535 | 0.13733 | 122.4289 | 123.3627 | -0.054932 | -0.32044 | 0.11444 | 0.37537 | 122.3145 | 123.4909 | 123.3078 | 123.5001 | 122.4289 | 123.4772 | 119.2978 | -0.32044 | 123.5001 | 122.4289 | 119.2978 | 123.3078 | 123.4772 | -1.3092 | -123.6832
985.9219 | 123.4268 | -122.3648 | 0.93384 | 0.4243 | -9.5248e-05 | -0.017893 | 0.066434 | -0.038668 | -0.0079844 | 0.052497 | 0.036621 | 1.0345 | -0.35706 | 0.82855 | 0.74616 | -3.273 | 0.045776 | 0.96588 | 1.0941 | -122.7356 | 122.0078 | 0.10071 | 122.4014 | 123.1934 | -0.18768 | -0.37079 | 0.16022 | 0.39368 | 122.4106 | 123.3307 | 123.111 | 123.3994 | 122.4014 | 123.4589 | 119.0918 | -0.37079 | 123.3994 | 122.4014 | 119.0918 | 123.111 | 123.4589 | -1.2909 | -123.6694
986.9844 | 123.3994 | -122.3923 | 0.95215 | -0.094502 | 0.0020408 | 0.0098776 | 0.079252 | -0.030123 | -0.0037124 | 0.041816 | 0.027466 | 1.0757 | -0.37079 | 0.89264 | 0.86517 | -3.2135 | -0.064087 | 1.0391 | 1.0895 | -122.7081 | 122.0215 | 0.1236 | 122.4197 | 123.2849 | -0.086975 | -0.31586 | 0.13733 | 0.39825 | 122.3282 | 123.4314 | 123.2574 | 123.468 | 122.4197 | 123.4818 | 119.1788 | -0.31586 | 123.468 | 122.4197 | 119.1788 | 123.2574 | 123.4818 | -1.3229 | -123.6603
987.9219 | 123.4772 | -122.3053 | 0.96588 | 0.54637 | -0.016117 | -0.0029404 | 0.071775 | -0.048281 | -0.018665 | 0.043952 | 0.059509 | 1.0757 | -0.33417 | 0.82855 | 0.82398 | -3.2959 | 0.050354 | 0.99792 | 1.1398 | -122.6852 | 121.9711 | 0.10986 | 122.3648 | 123.1338 | -0.14191 | -0.37994 | 0.17395 | 0.39368 | 122.3557 | 123.3032 | 123.1293 | 123.381 | 122.3648 | 123.4451 | 119.0094 | -0.37994 | 123.381 | 122.3648 | 119.0094 | 123.1293 | 123.4451 | -1.3 | -123.6511
988.9844 | 123.4268 | -122.3465 | 0.98877 | 0.45481 | -0.0032992 | -0.010416 | 0.084592 | -0.035464 | -0.01012 | 0.035407 | -0.018311 | 1.1032 | -0.36163 | 0.90637 | 0.90179 | -3.392 | -0.027466 | 1.0574 | 1.1353 | -122.699 | 121.9849 | 0.11444 | 122.3282 | 123.2529 | -0.086976 | -0.35248 | 0.14648 | 0.34332 | 122.319 | 123.4039 | 123.2483 | 123.4497 | 122.3282 | 123.4818 | 118.9545 | -0.35248 | 123.4497 | 122.3282 | 118.9545 | 123.2483 | 123.4818 | -1.3504 | -123.6877
989.9219 | 123.4039 | -122.3831 | 0.9201 | 0.51585 | -0.011844 | 0.0077416 | 0.06323 | -0.045077 | -0.022938 | 0.050361 | 0.045776 | 1.0849 | -0.32044 | 0.81024 | 0.8194 | -3.5934 | 0.059509 | 0.99335 | 1.1536 | -122.7539 | 122.0627 | 0.1648 | 122.4289 | 123.1934 | -0.10071 | -0.37079 | 0.23346 | 0.36621 | 122.4426 | 123.3765 | 123.2025 | 123.468 | 122.4289 | 123.5367 | 118.7897 | -0.37079 | 123.468 | 122.4289 | 118.7897 | 123.2025 | 123.5367 | -1.2405 | -123.674
990.9844 | 123.3765 | -122.3419 | 0.99792 | 0.13438 | -9.5248e-05 | -0.021098 | 0.08032 | -0.046145 | -0.012257 | 0.051429 | -0.041199 | 1.1215 | -0.35706 | 0.97504 | 0.93842 | -3.5477 | -0.082397 | 1.1169 | 1.1124 | -122.6761 | 121.9849 | 0.1236 | 122.3007 | 123.317 | -0.059509 | -0.33417 | 0.11444 | 0.31586 | 122.2595 | 123.4589 | 123.2803 | 123.4634 | 122.3007 | 123.4543 | 118.7943 | -0.33417 | 123.4634 | 122.3007 | 118.7943 | 123.2803 | 123.4543 | -1.355 | -123.674
991.9219 | 123.4634 | -122.3282 | 0.97961 | 1.4924 | -0.017185 | -0.0478 | 0.056821 | -0.049349 | -0.015461 | 0.051429 | 0.16937 | 1.0071 | -0.36621 | 0.83313 | 0.82855 | -3.5614 | 0.041199 | 0.99792 | 1.1398 | -122.7036 | 121.962 | 0.027466 | 122.4976 | 123.1613 | -0.15106 | -0.37537 | 0.16022 | 0.53558 | 122.3694 | 123.3261 | 123.1567 | 123.3353 | 122.4976 | 123.468 | 118.7668 | -0.37537 | 123.3353 | 122.4976 | 118.7668 | 123.1567 | 123.468 | -1.3458 | -123.6832
992.9844 | 123.3994 | -122.3923 | 0.97046 | -0.3539 | -0.0086402 | 0.010946 | 0.089933 | -0.041873 | -0.013325 | 0.042884 | 0.004578 | 1.0712 | -0.37994 | 0.91095 | 0.8606 | -3.447 | -0.07782 | 1.0666 | 1.1169 | -122.7264 | 122.0123 | 0.10071 | 122.3969 | 123.3032 | -0.10986 | -0.33417 | 0.14648 | 0.38452 | 122.3145 | 123.4589 | 123.2529 | 123.4634 | 122.3969 | 123.5092 | 118.9453 | -0.33417 | 123.4634 | 122.3969 | 118.9453 | 123.2529 | 123.5092 | -1.3504 | -123.6969
993.9219 | 123.3902 | -122.3785 | 0.9613 | 1.172 | 0.0020408 | 0.0066726 | 0.082456 | -0.046145 | -0.0079844 | 0.040748 | -0.009155 | 1.1078 | -0.35706 | 0.28839 | 0.91553 | -3.4973 | 0.073242 | 1.1032 | 1.1032 | -122.6807 | 122.0215 | 0.14648 | 122.3694 | 122.6669 | -0.045777 | -0.30212 | 0.14191 | 0.3479 | 122.4518 | 123.4818 | 123.2941 | 123.4863 | 122.3694 | 123.4818 | 118.8812 | -0.30212 | 123.4863 | 122.3694 | 118.8812 | 123.2941 | 123.4818 | -1.3184 | -123.642
994.9844 | 123.3215 | -122.3785 | 0.97504 | 0.22593 | 0.00097275 | 0.00026463 | 0.073911 | -0.034396 | -0.0037124 | 0.048225 | -0.022888 | 1.1032 | -0.37079 | 0.30212 | 0.90637 | -3.4332 | 0.036621 | 1.0986 | 1.0941 | -122.6807 | 122.0078 | 0.12817 | 122.3557 | 122.6807 | -0.068665 | -0.30212 | 0.11902 | 0.3479 | 122.4152 | 123.4772 | 123.2849 | 123.4818 | 122.3557 | 123.4726 | 118.9453 | -0.30212 | 123.4818 | 122.3557 | 118.9453 | 123.2849 | 123.4726 | -1.3458 | -123.6557
995.9219 | 123.4543 | -122.406 | 0.97504 | 0.33274 | 0.0041778 | -0.0072124 | 0.083524 | -0.047213 | 0.0037646 | 0.037543 | -0.068665 | 1.0849 | -0.3891 | 0.29755 | 0.92468 | -3.3691 | 0.073242 | 1.2909 | 1.0941 | -122.699 | 122.0169 | 0.10986 | 122.3373 | 122.7036 | -0.050354 | -0.29297 | 0.11902 | 0.32043 | 122.4792 | 123.6969 | 123.3307 | 123.4909 | 122.3373 | 123.5001 | 119.0369 | -0.29297 | 123.4909 | 122.3373 | 119.0369 | 123.3307 | 123.5001 | -1.3641 | -123.674
996.9219 | 123.587 | -122.4335 | 0.91095 | 0.4243 | -0.010776 | -0.015757 | 0.062162 | -0.0376 | -0.013325 | 0.050361 | 0.045776 | 1.0345 | -0.32044 | 0.11902 | 0.7782 | -3.5477 | 0.2243 | 0.93842 | 1.1124 | -122.7676 | 122.113 | 0.1236 | 122.4792 | 122.5525 | -0.13275 | -0.33417 | 0.20142 | 0.36621 | 122.6578 | 123.3719 | 123.2117 | 123.468 | 122.4792 | 123.5458 | 118.8858 | -0.33417 | 123.468 | 122.4792 | 118.8858 | 123.2117 | 123.5458 | -1.2314 | -123.6786
997.9844 | 123.3673 | -122.406 | 0.92926 | 0.33274 | -0.0075722 | -0.0093484 | 0.071775 | -0.038668 | -0.020801 | 0.041816 | -0.013733 | 1.0803 | -0.35706 | 0.27008 | 0.86517 | -3.5202 | 0.07782 | 1.0574 | 1.0483 | -122.7722 | 122.049 | 0.15106 | 122.3923 | 122.6761 | -0.064087 | -0.36621 | 0.11902 | 0.34332 | 122.4838 | 123.4634 | 123.2712 | 123.4863 | 122.3923 | 123.4543 | 118.8858 | -0.36621 | 123.4863 | 122.3923 | 118.8858 | 123.2712 | 123.4543 | -1.2863 | -123.7015
998.9219 | 123.468 | -122.3648 | 0.9201 | 0.19541 | -0.012912 | -0.017893 | 0.08032 | -0.036532 | -0.017597 | 0.04502 | 0.032043 | 1.0208 | -0.34332 | 0.14648 | 0.74616 | -3.7537 | 0.21057 | 0.94299 | 1.0941 | -122.7722 | 122.0215 | 0.10071 | 122.3969 | 122.5113 | -0.17395 | -0.40741 | 0.17395 | 0.37537 | 122.5754 | 123.3078 | 123.111 | 123.3856 | 122.3969 | 123.4589 | 118.6111 | -0.40741 | 123.3856 | 122.3969 | 118.6111 | 123.111 | 123.4589 | -1.2634 | -123.6923
999.9844 | 123.3856 | -122.4472 | 0.93384 | -2.185 | 0.0020408 | 0.0013326 | 0.074979 | -0.035464 | -0.028278 | 0.051429 | -0.10986 | 1.1078 | -0.35248 | 0.27466 | 0.84686 | -3.7308 | 0.050354 | 1.0712 | 1.0574 | -122.7402 | 122.0947 | 0.17395 | 122.3373 | 122.7219 | -0.086975 | -0.29297 | 0.1236 | 0.24262 | 122.4976 | 123.5184 | 123.2941 | 123.555 | 122.3373 | 123.5046 | 118.7164 | -0.29297 | 123.555 | 122.3373 | 118.7164 | 123.2941 | 123.5046 | -1.2863 | -123.674
1000.9219 | 123.3215 | -122.438 | 0.93842 | 0.14964 | -0.0043672 | -0.0093484 | 0.082456 | -0.042941 | -0.0090524 | 0.043952 | -0.054932 | 1.062 | -0.3891 | 0.39825 | 0.88806 | -3.8773 | 0.10071 | 1.0941 | 1.0574 | -122.731 | 122.049 | 0.1236 | 122.3831 | 122.8363 | -0.050354 | -0.29297 | 0.11902 | 0.33417 | 122.5388 | 123.5321 | 123.3261 | 123.5001 | 122.3831 | 123.4955 | 118.5608 | -0.29297 | 123.5001 | 122.3831 | 118.5608 | 123.3261 | 123.4955 | -1.3275 | -123.6694
1001.9688 | 123.4543 | -122.3923 | 0.9201 | 1.6297 | -0.01398 | -0.011485 | 0.060026 | -0.0376 | -0.018665 | 0.048225 | 0.082397 | 1.0071 | -0.36163 | 0.13275 | 0.74158 | -4.0878 | 0.19226 | 0.95673 | 1.0941 | -122.7722 | 122.0306 | 0.086975 | 122.4747 | 122.525 | -0.17853 | -0.37994 | 0.17395 | 0.44403 | 122.5845 | 123.349 | 123.1339 | 123.3994 | 122.4747 | 123.4863 | 118.3044 | -0.37994 | 123.3994 | 122.4747 | 118.3044 | 123.1339 | 123.4863 | -1.2817 | -123.6923
1002.9219 | 123.3307 | -122.4472 | 0.92468 | 0.62266 | -9.5248e-05 | 0.0013326 | 0.079252 | -0.048281 | -0.01012 | 0.032203 | -0.041199 | 1.062 | -0.37994 | 0.31586 | 0.86517 | -4.0283 | 0.045776 | 1.0849 | 1.0529 | -122.7631 | 122.0673 | 0.13733 | 122.406 | 122.7631 | -0.05951 | -0.31586 | 0.12817 | 0.33875 | 122.493 | 123.5321 | 123.3124 | 123.5092 | 122.406 | 123.5001 | 118.4189 | -0.31586 | 123.5092 | 122.406 | 118.4189 | 123.3124 | 123.5001 | -1.3046 | -123.6877
1003.9844 | 123.3627 | -122.4655 | 0.9201 | 0.11912 | 0.0073818 | -0.0072124 | 0.084592 | -0.040805 | 0.0026966 | 0.054633 | -0.004578 | 1.0437 | -0.37994 | 0.27008 | 0.85144 | -3.9047 | 0.041199 | 1.0483 | 1.0391 | -122.7859 | 122.0856 | 0.1236 | 122.4609 | 122.7356 | -0.068665 | -0.32044 | 0.11902 | 0.37537 | 122.5067 | 123.5138 | 123.317 | 123.5092 | 122.4609 | 123.5046 | 118.5608 | -0.32044 | 123.5092 | 122.4609 | 118.5608 | 123.317 | 123.5046 | -1.3 | -123.7061
1004.9219 | 123.3719 | -122.4197 | 0.92926 | 0.22593 | 0.0031088 | 0.0066726 | 0.08032 | -0.0376 | -0.014393 | 0.037543 | -0.027466 | 1.062 | -0.37079 | 0.26093 | 0.8606 | -4.0192 | 0.09613 | 1.0529 | 1.0757 | -122.7676 | 122.049 | 0.13275 | 122.3923 | 122.6807 | -0.068664 | -0.3479 | 0.14648 | 0.34332 | 122.5159 | 123.4726 | 123.2803 | 123.4818 | 122.3923 | 123.4955 | 118.4006 | -0.3479 | 123.4818 | 122.3923 | 118.4006 | 123.2803 | 123.4955 | -1.3 | -123.6969
1005.9844 | 123.3627 | -122.438 | 0.94757 | -3.0242 | -0.011844 | -0.023234 | 0.078184 | -0.035464 | -0.022938 | 0.052497 | 0.018311 | 1.1307 | -0.33875 | 0.30212 | 0.83313 | -4.0924 | 0.041199 | 1.0849 | 1.0803 | -122.7448 | 122.0993 | 0.1831 | 122.4564 | 122.7402 | -0.11444 | -0.3067 | 0.13275 | 0.35706 | 122.4792 | 123.5229 | 123.2712 | 123.5687 | 122.4564 | 123.5184 | 118.3456 | -0.3067 | 123.5687 | 122.4564 | 118.3456 | 123.2712 | 123.5184 | -1.2863 | -123.6923
1006.9219 | 123.3536 | -122.4564 | 0.91095 | -0.033467 | 0.0041778 | 0.0098776 | 0.08032 | -0.03226 | -0.01012 | 0.052497 | 0.013733 | 1.0529 | -0.37079 | 0.27008 | 0.84686 | -4.3076 | 0.059509 | 1.0391 | 1.0391 | -122.7997 | 122.0856 | 0.14191 | 122.4701 | 122.7264 | -0.064087 | -0.34332 | 0.12817 | 0.38452 | 122.5159 | 123.4955 | 123.3032 | 123.5092 | 122.4701 | 123.4955 | 118.1488 | -0.34332 | 123.5092 | 122.4701 | 118.1488 | 123.3032 | 123.4955 | -1.2817 | -123.7106
1007.9844 | 123.3994 | -122.438 | 0.9201 | -0.30813 | -0.0022312 | -0.0018714 | 0.079252 | -0.0376 | -0.012257 | 0.048225 | -0.022888 | 1.0345 | -0.39368 | 0.23346 | 0.71411 | -3.4515 | 0.082397 | 1.0208 | 1.0529 | -122.8043 | 122.0444 | 0.11444 | 122.4152 | 122.6715 | -0.20599 | -0.36621 | 0.13275 | 0.37079 | 122.5204 | 123.4589 | 123.1522 | 123.4726 | 122.4152 | 123.4909 | 118.9865 | -0.36621 | 123.4726 | 122.4152 | 118.9865 | 123.1522 | 123.4909 | -1.3138 | -123.7244
1008.9219 | 123.3627 | -122.4564 | 0.9201 | 0.22593 | 0.0052458 | 0.0045366 | 0.085661 | -0.024783 | -0.0069164 | 0.042884 | 0.009155 | 1.0666 | -0.36621 | 0.27924 | 0.85602 | -4.5136 | 0.045776 | 1.0529 | 1.0437 | -122.7905 | 122.0901 | 0.14648 | 122.4655 | 122.7356 | -0.064087 | -0.33417 | 0.1236 | 0.37537 | 122.5021 | 123.5092 | 123.3124 | 123.5229 | 122.4655 | 123.5001 | 117.9428 | -0.33417 | 123.5229 | 122.4655 | 117.9428 | 123.3124 | 123.5001 | -1.2863 | -123.7106
1009.9219 | 123.3765 | -122.4792 | 0.87891 | 0.11912 | -0.012912 | -0.0061444 | 0.073911 | -0.031191 | -0.011188 | 0.048225 | -0.004578 | 1.0254 | -0.35706 | 0.25177 | 0.75073 | -3.6072 | 0.073242 | 1.0162 | 1.0391 | -122.8134 | 122.1222 | 0.14648 | 122.4747 | 122.731 | -0.12817 | -0.33417 | 0.16022 | 0.35248 | 122.5525 | 123.4955 | 123.23 | 123.5046 | 122.4747 | 123.5184 | 118.8721 | -0.33417 | 123.5046 | 122.4747 | 118.8721 | 123.23 | 123.5184 | -1.236 | -123.6923
1010.9844 | 123.3582 | -122.4747 | 0.88806 | -0.3539 | -0.010776 | -0.0082804 | 0.068571 | -0.029055 | -0.022938 | 0.054633 | -0.068665 | 1.0162 | -0.37994 | 0.24719 | 0.8194 | -4.6646 | 0.009155 | 1.0391 | 1.03 | -122.8134 | 122.0947 | 0.12817 | 122.406 | 122.7219 | -0.068665 | -0.33875 | 0.14191 | 0.31128 | 122.4838 | 123.5138 | 123.2941 | 123.4909 | 122.406 | 123.5046 | 117.8101 | -0.33875 | 123.4909 | 122.406 | 117.8101 | 123.2941 | 123.5046 | -1.268 | -123.7015
1011.9219 | 123.3627 | -122.5159 | 0.82855 | -0.0029495 | 0.0020408 | -0.0018714 | 0.086729 | -0.033328 | 0.0048326 | 0.046088 | 0.013733 | 0.97961 | -0.37994 | 0.24261 | 0.7782 | -4.8798 | 0.036621 | 0.99335 | 0.98419 | -122.8546 | 122.1359 | 0.15106 | 122.5296 | 122.7585 | -0.050354 | -0.33875 | 0.15564 | 0.39368 | 122.5525 | 123.5092 | 123.2941 | 123.4955 | 122.5296 | 123.5001 | 117.6361 | -0.33875 | 123.4955 | 122.5296 | 117.6361 | 123.2941 | 123.5001 | -1.2085 | -123.6832
1012.9844 | 123.3353 | -122.4838 | 0.88806 | 0.058086 | 0.0020408 | -0.020029 | 0.082456 | -0.033328 | -0.0037124 | 0.057838 | -0.018311 | 1.0162 | -0.37994 | 0.30212 | 0.78735 | -4.1428 | 0.018311 | 1.0895 | 1.0162 | -122.7814 | 122.1039 | 0.12817 | 122.4655 | 122.7859 | -0.10071 | -0.29755 | 0.12817 | 0.36163 | 122.5021 | 123.5733 | 123.2712 | 123.5001 | 122.4655 | 123.5001 | 118.3411 | -0.29755 | 123.5001 | 122.4655 | 118.3411 | 123.2712 | 123.5001 | -1.268 | -123.6694
1013.9219 | 123.4222 | -122.58 | 0.82398 | -0.079243 | -0.0086402 | 0.0013326 | 0.079252 | -0.03226 | -0.0069164 | 0.042884 | 0.045776 | 0.94757 | -0.36163 | 0.63171 | 0.65918 | -4.2938 | 0.49439 | 0.91095 | 0.97961 | -122.9004 | 122.2183 | 0.1236 | 122.6257 | 123.2117 | -0.1648 | -0.32044 | 0.15564 | 0.40741 | 123.0743 | 123.4909 | 123.2391 | 123.5275 | 122.6257 | 123.5596 | 118.2861 | -0.32044 | 123.5275 | 122.6257 | 118.2861 | 123.2391 | 123.5596 | -1.1856 | -123.7244
1014.9219 | 123.3994 | -122.4518 | 0.92468 | -0.048725 | -0.0043672 | -0.0061444 | 0.087797 | -0.029055 | -0.0090524 | 0.04502 | 0.013733 | 1.0025 | -0.36621 | 0.21057 | 0.74158 | -4.454 | 0.07782 | 0.99335 | 1.0391 | -122.818 | 122.0856 | 0.077819 | 122.4655 | 122.6624 | -0.18311 | -0.36621 | 0.11444 | 0.37994 | 122.5296 | 123.4451 | 123.1934 | 123.4543 | 122.4655 | 123.4909 | 117.9977 | -0.36621 | 123.4543 | 122.4655 | 117.9977 | 123.1934 | 123.4909 | -1.2909 | -123.7427
1015.9844 | 123.5275 | -122.4564 | 0.85602 | -0.3539 | -0.015048 | -0.033915 | 0.062162 | -0.033328 | -0.022938 | 0.054633 | -0.09613 | 0.93842 | -0.37079 | 0.022888 | 0.59967 | -4.5914 | 0.15106 | 0.87891 | 1.0254 | -122.85 | 122.0856 | 0.082398 | 122.3602 | 122.4792 | -0.25635 | -0.39368 | 0.16937 | 0.27466 | 122.6074 | 123.3353 | 123.056 | 123.3948 | 122.3602 | 123.4818 | 117.865 | -0.39368 | 123.3948 | 122.3602 | 117.865 | 123.056 | 123.4818 | -1.2268 | -123.7061
1016.9219 | 123.4222 | -122.4518 | 0.96588 | -0.12502 | -0.0043672 | 0.0045366 | 0.083524 | -0.034396 | -0.0079844 | 0.03968 | -0.009155 | 0.98877 | -0.37537 | 0.23346 | 0.70953 | -4.4769 | 0.26093 | 1.0574 | 1.0666 | -122.7859 | 122.0764 | 0.022889 | 122.4426 | 122.6852 | -0.25635 | -0.33417 | 0.10071 | 0.36621 | 122.7127 | 123.5092 | 123.1613 | 123.4406 | 122.4426 | 123.5184 | 117.9749 | -0.33417 | 123.4406 | 122.4426 | 117.9749 | 123.1613 | 123.5184 | -1.3412 | -123.7518
1017.9844 | 123.3673 | -122.493 | 0.90179 | -0.4302 | -0.0043672 | -0.0072124 | 0.067503 | -0.034396 | -0.018665 | 0.047157 | -0.11902 | 0.99335 | -0.40741 | 0.23804 | 0.78735 | -5.5115 | 0 | 1.0437 | 0.99792 | -122.8317 | 122.0856 | 0.091553 | 122.374 | 122.731 | -0.11444 | -0.33875 | 0.096131 | 0.28839 | 122.493 | 123.5367 | 123.2803 | 123.4863 | 122.374 | 123.4909 | 116.9815 | -0.33875 | 123.4863 | 122.374 | 116.9815 | 123.2803 | 123.4909 | -1.3092 | -123.7335
1018.9219 | 123.4085 | -122.5021 | 0.88348 | -0.14028 | 0.0020408 | 0.018423 | 0.077116 | -0.039736 | -0.0079844 | 0.041816 | -0.009155 | 1.0025 | -0.37537 | 0.2243 | 0.69122 | -4.9622 | 0.064087 | 0.9613 | 1.0391 | -122.8363 | 122.1268 | 0.11902 | 122.493 | 122.7264 | -0.19226 | -0.33417 | 0.15564 | 0.36621 | 122.5662 | 123.4634 | 123.1934 | 123.5046 | 122.493 | 123.5413 | 117.54 | -0.33417 | 123.5046 | 122.493 | 117.54 | 123.1934 | 123.5413 | -1.2589 | -123.7198
1019.9844 | 123.5092 | -122.4472 | 0.85602 | -0.32338 | -0.01398 | -0.021098 | 0.051481 | -0.049349 | -0.026142 | 0.055701 | 0.054932 | 0.95215 | -0.35706 | 0.073242 | 0.6134 | -4.8843 | 0.17853 | 0.86517 | 1.0803 | -122.8775 | 122.0901 | 0.09613 | 122.5021 | 122.5204 | -0.24261 | -0.4303 | 0.2243 | 0.41199 | 122.6257 | 123.3124 | 123.0606 | 123.3994 | 122.5021 | 123.5275 | 117.5629 | -0.4303 | 123.3994 | 122.5021 | 117.5629 | 123.0606 | 123.5275 | -1.2131 | -123.7335
1020.9219 | 123.349 | -122.4518 | 0.9613 | -0.3539 | -0.0032992 | -0.0018714 | 0.083524 | -0.0376 | -0.012257 | 0.049293 | -0.050354 | 1.0071 | -0.39368 | 0.37537 | 0.9613 | -4.866 | -0.009155 | 1.0254 | 1.062 | -122.7905 | 122.0581 | 0.045776 | 122.4014 | 122.8271 | 0 | -0.33875 | 0.10071 | 0.34332 | 122.4426 | 123.4772 | 123.4131 | 123.4589 | 122.4014 | 123.5138 | 117.5858 | -0.33875 | 123.4589 | 122.4014 | 117.5858 | 123.4131 | 123.5138 | -1.355 | -123.7518
1021.9844 | 123.4909 | -122.4426 | 0.82855 | -0.50649 | -0.02573 | -0.010416 | 0.056821 | -0.040805 | -0.02721 | 0.049293 | 0.036621 | 0.93842 | -0.32959 | 0.068665 | 0.52185 | -5.1956 | 0.16937 | 0.93384 | 1.0574 | -122.8729 | 122.113 | 0.10986 | 122.4792 | 122.5113 | -0.3067 | -0.4303 | 0.22888 | 0.36621 | 122.612 | 123.3765 | 122.9645 | 123.381 | 122.4792 | 123.5001 | 117.247 | -0.4303 | 123.381 | 122.4792 | 117.247 | 122.9645 | 123.5001 | -1.1581 | -123.7015
1022.9219 | 123.381 | -122.5845 | 0.81482 | -0.47597 | -0.010776 | -0.037119 | 0.084592 | -0.049349 | -0.022938 | 0.043952 | 0.10529 | 0.93384 | -0.35248 | 0.64545 | 0.62714 | -5.159 | 0.41657 | 0.92926 | 0.94757 | -122.9187 | 122.2321 | 0.11902 | 122.6898 | 123.23 | -0.18768 | -0.33417 | 0.13275 | 0.45776 | 123.0011 | 123.5138 | 123.2117 | 123.5184 | 122.6898 | 123.5321 | 117.4255 | -0.33417 | 123.5184 | 122.6898 | 117.4255 | 123.2117 | 123.5321 | -1.1673 | -123.7335
1023.9844 | 123.4909 | -122.5571 | 0.78735 | 0.027569 | -0.02573 | -0.017893 | 0.069639 | -0.047213 | -0.0443 | 0.050361 | -0.050354 | 0.87433 | -0.37079 | 0.54016 | 0.52643 | -5.3284 | 0.52643 | 0.81482 | 0.98877 | -122.9233 | 122.1863 | 0.086975 | 122.5067 | 123.0972 | -0.26093 | -0.36621 | 0.20142 | 0.32043 | 123.0835 | 123.3719 | 123.0835 | 123.4314 | 122.5067 | 123.5458 | 117.2287 | -0.36621 | 123.4314 | 122.5067 | 117.2287 | 123.0835 | 123.5458 | -1.1581 | -123.7106
1024.9219 | 123.3627 | -122.6074 | 0.75989 | 0.073345 | -9.5248e-05 | -0.0082804 | 0.076048 | -0.046145 | -0.01012 | 0.040748 | -0.064087 | 0.95215 | -0.35706 | 0.73242 | 0.56763 | -5.3146 | 0.50354 | 0.91553 | 0.91095 | -122.9736 | 122.2504 | 0.19226 | 122.5433 | 123.3398 | -0.19226 | -0.36621 | 0.15106 | 0.29297 | 123.111 | 123.5229 | 123.175 | 123.5596 | 122.5433 | 123.5184 | 117.2928 | -0.36621 | 123.5596 | 122.5433 | 117.2928 | 123.175 | 123.5184 | -1.1169 | -123.7335
1025.9844 | 123.5001 | -122.5662 | 0.77362 | -0.29287 | -0.027866 | -0.026438 | 0.072843 | -0.045077 | -0.018665 | 0.036475 | 0.022888 | 0.85602 | -0.37537 | 0.63171 | 0.56763 | -3.7949 | 0.62714 | 0.8194 | 0.94757 | -122.937 | 122.1909 | 0.082397 | 122.5891 | 123.1979 | -0.20599 | -0.37079 | 0.17395 | 0.39825 | 123.1934 | 123.3856 | 123.1338 | 123.4222 | 122.5891 | 123.5138 | 118.7714 | -0.37079 | 123.4222 | 122.5891 | 118.7714 | 123.1338 | 123.5138 | -1.149 | -123.7106
1026.9219 | 123.4222 | -122.6257 | 0.79193 | -0.30813 | -0.012912 | -0.023234 | 0.091001 | -0.047213 | -0.0069164 | 0.043952 | -0.068665 | 0.92926 | -0.40283 | 0.75531 | 0.54474 | -3.8132 | 0.54016 | 0.92468 | 0.91553 | -122.9095 | 122.2229 | 0.13733 | 122.5571 | 123.381 | -0.24719 | -0.28381 | 0.1236 | 0.33417 | 123.1659 | 123.5504 | 123.1705 | 123.555 | 122.5571 | 123.5413 | 118.8126 | -0.28381 | 123.555 | 122.5571 | 118.8126 | 123.1705 | 123.5413 | -1.1948 | -123.7015
1027.9688 | 123.5046 | -122.58 | 0.76904 | -0.30813 | -0.010776 | -0.046732 | 0.064298 | -0.039736 | -0.029346 | 0.063178 | -0.068665 | 0.87891 | -0.44403 | 0.41657 | 0.55847 | -3.7857 | 0.6546 | 0.70038 | 0.97504 | -122.9462 | 122.1359 | 0.10986 | 122.5113 | 122.9965 | -0.21057 | -0.36621 | 0.20599 | 0.37537 | 123.2346 | 123.2803 | 123.1384 | 123.4589 | 122.5113 | 123.555 | 118.7942 | -0.36621 | 123.4589 | 122.5113 | 118.7942 | 123.1384 | 123.555 | -1.2131 | -123.7152
1028.9219 | 123.4726 | -122.5113 | 0.80566 | -0.70485 | -0.0075722 | -0.023234 | 0.055753 | -0.046145 | -0.02187 | 0.05677 | -0.004578 | 0.90637 | -0.38452 | 0.65002 | 0.54016 | -5.2689 | 0.68207 | 0.84228 | 1.0117 | -122.9233 | 122.1268 | 0.10071 | 122.5067 | 123.1613 | -0.2655 | -0.41199 | 0.20599 | 0.37994 | 123.1934 | 123.3536 | 123.0515 | 123.4177 | 122.5067 | 123.5229 | 117.2424 | -0.41199 | 123.4177 | 122.5067 | 117.2424 | 123.0515 | 123.5229 | -1.1902 | -123.7289
1029.9688 | 123.4909 | -122.5204 | 0.8194 | 0.25645 | -0.0097082 | -0.0018714 | 0.08032 | -0.051486 | -0.016529 | 0.047157 | -0.018311 | 0.91553 | -0.35706 | 0.71411 | 0.55847 | -5.7587 | 0.72784 | 0.87891 | 0.99792 | -122.8821 | 122.1634 | 0.09613 | 122.5021 | 123.2346 | -0.26093 | -0.36163 | 0.17853 | 0.33874 | 123.2483 | 123.3994 | 123.0789 | 123.436 | 122.5021 | 123.5184 | 116.7618 | -0.36163 | 123.436 | 122.5021 | 116.7618 | 123.0789 | 123.5184 | -1.1765 | -123.7015
1030.9219 | 123.3856 | -122.5433 | 0.8606 | -0.30813 | -0.010776 | -0.011485 | 0.077116 | -0.047213 | -0.020801 | 0.041816 | -0.068665 | 0.98877 | -0.39825 | 0.8606 | 0.63171 | -5.6488 | 0.59967 | 0.98419 | 0.98877 | -122.8455 | 122.1451 | 0.12817 | 122.4747 | 123.4039 | -0.22888 | -0.30212 | 0.12817 | 0.32959 | 123.143 | 123.5275 | 123.175 | 123.5321 | 122.4747 | 123.5321 | 116.8945 | -0.30212 | 123.5321 | 122.4747 | 116.8945 | 123.175 | 123.5321 | -1.2589 | -123.7061
1031.9844 | 123.5046 | -122.4609 | 0.82855 | 0.37852 | -0.0075722 | -0.027506 | 0.061094 | -0.052554 | -0.020801 | 0.052497 | -0.27008 | 0.91095 | -0.39825 | 0.66834 | 0.54016 | -5.603 | 0.78735 | 0.85602 | 1.0162 | -122.8958 | 122.0627 | 0.082398 | 122.1909 | 123.1293 | -0.28839 | -0.43488 | 0.18768 | 0.12817 | 123.2483 | 123.317 | 123.0011 | 123.3719 | 122.1909 | 123.4772 | 116.8579 | -0.43488 | 123.3719 | 122.1909 | 116.8579 | 123.0011 | 123.4772 | -1.2268 | -123.7244
1032.9219 | 123.3948 | -122.4472 | 1.0025 | -0.20131 | -0.0097082 | 0.00026463 | 0.068571 | -0.051486 | 0.035809 | 0.10484 | -0.10529 | 1.0712 | -0.39825 | 0.27924 | -122.3785 | -13.6826 | 0.027466 | 1.0941 | 1.0803 | -122.731 | 122.049 | 0.068665 | 122.3419 | 122.7264 | -123.381 | -0.28381 | 0.07782 | 0.29297 | 122.4747 | 123.5413 | 0.068665 | 123.5184 | 122.3419 | 123.5275 | 108.7646 | -0.28381 | 123.5184 | 122.3419 | 108.7646 | 0.068665 | 123.5275 | -1.4008 | -123.7335
1033.9844 | 123.4818 | -122.4792 | 0.91095 | 0.13438 | -0.019321 | -0.045664 | 0.06323 | -0.041873 | 0.031536 | 0.10804 | -0.050354 | 0.9201 | -0.3891 | 0.13275 | -122.5479 | -16.2827 | 0.14191 | 0.91095 | 1.0437 | -122.8363 | 122.0901 | 0.009155 | 122.4289 | 122.612 | -123.4589 | -0.35706 | 0.13275 | 0.33874 | 122.6212 | 123.3902 | -0.068665 | 123.3994 | 122.4289 | 123.5229 | 106.1966 | -0.35706 | 123.3994 | 122.4289 | 106.1966 | -0.068665 | 123.5229 | -1.3 | -123.7473
1034.9219 | 123.5138 | -122.4976 | 0.79651 | -0.15554 | -0.027866 | -0.02537 | 0.061094 | -0.048281 | 0.024059 | 0.099494 | 0.009155 | 0.92926 | -0.33875 | 0.39825 | -122.6486 | -17.0334 | 0.50812 | 0.81024 | 1.0025 | -122.8912 | 122.1588 | 0.13275 | 122.5067 | 122.8958 | -123.4451 | -0.39368 | 0.20599 | 0.3479 | 123.0057 | 123.3078 | -0.15106 | 123.4268 | 122.5067 | 123.5001 | 105.4642 | -0.39368 | 123.4268 | 122.5067 | 105.4642 | -0.15106 | 123.5001 | -1.1353 | -123.6877
1035.9219 | 123.4222 | -122.5296 | 0.86517 | -0.20131 | -0.0011632 | -0.0072124 | 0.089933 | -0.049349 | 0.064648 | 0.11338 | -0.004578 | 0.9613 | -0.40283 | 0.25177 | -122.5433 | -16.4795 | 0.045776 | 0.91553 | 0.99792 | -122.8821 | 122.1268 | 0.096131 | 122.525 | 122.7814 | -123.4085 | -0.35248 | 0.13275 | 0.39825 | 122.5754 | 123.4451 | -0.013733 | 123.4909 | 122.525 | 123.5275 | 106.0501 | -0.35248 | 123.4909 | 122.525 | 106.0501 | -0.013733 | 123.5275 | -1.268 | -123.7473
1036.9844 | 123.5687 | -122.525 | 0.80109 | 0.53111 | -0.0065042 | -0.017893 | 0.069639 | -0.052554 | 0.04649 | 0.10697 | 0.013733 | 0.95673 | -0.33875 | 0.13733 | -122.5571 | -14.9734 | 0.17853 | 0.72784 | 1.0391 | -122.9187 | 122.1863 | 0.15564 | 122.5388 | 122.6624 | -123.3582 | -0.39368 | 0.23804 | 0.35248 | 122.7036 | 123.2529 | -0.032044 | 123.4818 | 122.5388 | 123.5641 | 107.5516 | -0.39368 | 123.4818 | 122.5388 | 107.5516 | -0.032044 | 123.5641 | -1.1398 | -123.7198
1037.9219 | 123.5001 | -122.4884 | 0.82398 | -0.38442 | -0.018253 | -0.013621 | 0.055753 | -0.055758 | 0.036877 | 0.11979 | 0.009155 | 0.94299 | -0.36163 | 0.1236 | -122.6303 | -16.7999 | 0.22888 | 0.85602 | 1.0162 | -122.8683 | 122.1268 | 0.11902 | 122.4976 | 122.612 | -123.4543 | -0.37994 | 0.19226 | 0.37079 | 122.7173 | 123.3444 | -0.14191 | 123.4314 | 122.4976 | 123.5046 | 105.6885 | -0.37994 | 123.4314 | 122.4976 | 105.6885 | -0.14191 | 123.5046 | -1.1856 | -123.6923
1038.9844 | 123.4726 | -122.4564 | 0.83313 | 0.45481 | -0.0032992 | -0.026438 | 0.070707 | -0.051486 | 0.042217 | 0.10163 | -0.041199 | 0.91095 | -0.39825 | 0.16022 | -122.5067 | -17.1707 | 0.16479 | 0.85602 | 0.99792 | -122.85 | 122.0581 | 0.07782 | 122.4152 | 122.6166 | -123.3398 | -0.39368 | 0.16479 | 0.35706 | 122.6212 | 123.3124 | -0.050354 | 123.3673 | 122.4152 | 123.4543 | 105.2856 | -0.39368 | 123.3673 | 122.4152 | 105.2856 | -0.050354 | 123.4543 | -1.2314 | -123.6832
1039.9219 | 123.5092 | -122.4335 | 0.88348 | -0.048725 | -0.02573 | -0.018961 | 0.068571 | -0.045077 | 0.034741 | 0.11765 | -0.036621 | 0.98419 | -0.37994 | 0.66376 | -122.5342 | -17.601 | 0.013733 | 0.89722 | 1.0757 | -122.8226 | 122.0535 | 0.10071 | 122.3969 | 123.0972 | -123.4177 | -0.3891 | 0.19226 | 0.34332 | 122.4472 | 123.3307 | -0.10071 | 123.4177 | 122.3969 | 123.5092 | 104.8325 | -0.3891 | 123.4177 | 122.3969 | 104.8325 | -0.10071 | 123.5092 | -1.2634 | -123.7061
1040.9844 | 123.468 | -122.4243 | 0.93842 | -0.32338 | -0.027866 | -0.031779 | 0.073911 | -0.049349 | 0.035809 | 0.11231 | 0.18768 | 1.0254 | -0.39825 | 0.74616 | -122.5067 | -17.0975 | 0.013733 | 0.95215 | 1.1169 | -122.7631 | 122.0261 | 0.086975 | 122.612 | 123.1705 | -123.4451 | -0.33875 | 0.17853 | 0.58594 | 122.438 | 123.3765 | -0.082398 | 123.4497 | 122.612 | 123.5413 | 105.3268 | -0.33875 | 123.4497 | 122.612 | 105.3268 | -0.082398 | 123.5413 | -1.3367 | -123.7015
1041.9219 | 123.4451 | -122.4289 | 0.90637 | 0.19541 | -0.021457 | -0.0082804 | 0.070707 | -0.051486 | 0.033672 | 0.11658 | -0.15106 | 0.97504 | -0.4715 | 0.75073 | -122.4792 | -17.2714 | -0.041199 | 0.94299 | 1.0666 | -122.7951 | 121.9574 | 0.068665 | 122.2778 | 123.1796 | -123.3856 | -0.36621 | 0.16022 | 0.32044 | 122.3877 | 123.3719 | -0.050354 | 123.4039 | 122.2778 | 123.4955 | 105.1575 | -0.36621 | 123.4039 | 122.2778 | 105.1575 | -0.050354 | 123.4955 | -1.3779 | -123.7015
1042.9688 | 123.4406 | -122.4243 | 0.94299 | 0.45481 | -0.0032992 | -0.028574 | 0.087797 | -0.048281 | 0.05183 | 0.10697 | -0.054932 | 1.0666 | -0.4303 | 0.83313 | -122.4289 | -17.482 | -0.045776 | 1.0071 | 1.0803 | -122.7631 | 121.994 | 0.1236 | 122.3694 | 123.2574 | -123.3719 | -0.33875 | 0.13733 | 0.37537 | 122.3785 | 123.4314 | -0.004578 | 123.4909 | 122.3694 | 123.5046 | 104.9423 | -0.33875 | 123.4909 | 122.3694 | 104.9423 | -0.004578 | 123.5046 | -1.3733 | -123.7061
1043.9219 | 123.4589 | -122.3419 | 1.0071 | 0.47007 | -0.012912 | -0.0040084 | 0.077116 | -0.049349 | 0.024059 | 0.10484 | -0.045776 | 1.0757 | -0.36621 | 0.19226 | -122.3923 | -17.8253 | 0.16022 | 1.0666 | 1.1536 | -122.6807 | 121.9757 | 0.068665 | 122.2961 | 122.5342 | -123.3994 | -0.33874 | 0.14648 | 0.32044 | 122.5021 | 123.4085 | -0.050354 | 123.4177 | 122.2961 | 123.4955 | 104.5166 | -0.33874 | 123.4177 | 122.2961 | 104.5166 | -0.050354 | 123.4955 | -1.3733 | -123.6877
1044.9219 | 123.4406 | -122.3557 | 0.97046 | 0.19541 | -0.023593 | -0.030711 | 0.072843 | -0.049349 | 0.032604 | 0.11872 | -0.041199 | 1.0666 | -0.35706 | 0.16479 | -122.4243 | -17.189 | 0.14191 | 1.0208 | 1.1169 | -122.7173 | 121.9986 | 0.09613 | 122.3145 | 122.5204 | -123.3948 | -0.36163 | 0.14648 | 0.31586 | 122.4976 | 123.3765 | -0.068664 | 123.4222 | 122.3145 | 123.4726 | 105.1666 | -0.36163 | 123.4222 | 122.3145 | 105.1666 | -0.068664 | 123.4726 | -1.3275 | -123.6877
1045.9844 | 123.5046 | -122.4472 | 0.87433 | -0.39968 | -0.020389 | -0.022166 | 0.069639 | -0.05469 | 0.031536 | 0.12406 | 0.004578 | 0.97961 | -0.35248 | 0.70038 | -122.5708 | -17.7887 | 0.77362 | 0.87891 | 1.0574 | -122.8317 | 122.0947 | 0.10528 | 122.4518 | 123.1476 | -123.4451 | -0.38452 | 0.1831 | 0.35706 | 123.2208 | 123.3261 | -0.1236 | 123.4268 | 122.4518 | 123.5046 | 104.6585 | -0.38452 | 123.4268 | 122.4518 | 104.6585 | -0.1236 | 123.5046 | -1.2268 | -123.7061
1046.9219 | 123.4497 | -122.3465 | 0.99335 | 0.33274 | -0.015048 | -0.011485 | 0.066434 | -0.053622 | 0.028332 | 0.10804 | -0.004578 | 1.1261 | -0.35248 | 0.19684 | -122.3785 | -17.5598 | 0.17853 | 1.0574 | 1.1673 | -122.6669 | 121.994 | 0.13275 | 122.3419 | 122.5433 | -123.3719 | -0.32043 | 0.17395 | 0.3479 | 122.525 | 123.4039 | -0.032043 | 123.4726 | 122.3419 | 123.5138 | 104.7867 | -0.32043 | 123.4726 | 122.3419 | 104.7867 | -0.032043 | 123.5138 | -1.3458 | -123.6603
1047.9844 | 123.4863 | -122.3557 | 0.92926 | 0.45481 | -0.010776 | 0.00026463 | 0.082456 | -0.046145 | 0.064648 | 0.099494 | 0.036621 | 1.0254 | -0.34332 | 0.16937 | -122.4976 | -18.3884 | 0.18768 | 0.93842 | 1.0941 | -122.7722 | 122.0123 | 0.096131 | 122.3923 | 122.525 | -123.4268 | -0.41656 | 0.1648 | 0.37994 | 122.5433 | 123.2941 | -0.14191 | 123.381 | 122.3923 | 123.4497 | 103.9673 | -0.41656 | 123.381 | 122.3923 | 103.9673 | -0.14191 | 123.4497 | -1.2726 | -123.7015
1048.9219 | 123.4955 | -122.3602 | 0.93842 | 0.50059 | -0.0065042 | -0.0018714 | 0.083524 | -0.053622 | 0.042217 | 0.11018 | 0.045776 | 1.0437 | -0.34332 | 0.16022 | -122.4792 | -17.981 | 0.20599 | 0.96588 | 1.1124 | -122.7402 | 122.0169 | 0.10528 | 122.406 | 122.5204 | -123.4177 | -0.37994 | 0.17395 | 0.3891 | 122.5662 | 123.3261 | -0.11902 | 123.4039 | 122.406 | 123.4726 | 104.3793 | -0.37994 | 123.4039 | 122.406 | 104.3793 | -0.11902 | 123.4726 | -1.2817 | -123.6786
1049.9844 | 123.3353 | -122.4426 | 0.97504 | 0.28697 | -0.0065042 | 0.0077416 | 0.099546 | -0.047213 | 0.047558 | 0.097358 | -0.032043 | 1.0803 | -0.38452 | 0.35706 | -122.3282 | -18.0084 | 0.022888 | 1.1307 | 1.0849 | -122.7402 | 122.0581 | 0.10528 | 122.4106 | 122.7997 | -123.3032 | -0.29755 | 0.10986 | 0.35248 | 122.4655 | 123.5733 | 0.11444 | 123.5229 | 122.4106 | 123.5275 | 104.4342 | -0.29755 | 123.5229 | 122.4106 | 104.4342 | 0.11444 | 123.5275 | -1.3596 | -123.7152
1050.9219 | 123.5321 | -122.3969 | 0.9201 | -0.15554 | -0.0086402 | -0.023234 | 0.074979 | -0.051486 | 0.04649 | 0.10377 | 0.018311 | 1.0391 | -0.32959 | 0.082397 | -122.5021 | -22.2107 | 0.18768 | 0.9201 | 1.1032 | -122.7768 | 122.0673 | 0.11902 | 122.4152 | 122.4792 | -123.4222 | -0.37994 | 0.18311 | 0.3479 | 122.5845 | 123.317 | -0.10528 | 123.436 | 122.4152 | 123.5001 | 100.1862 | -0.37994 | 123.436 | 122.4152 | 100.1862 | -0.10528 | 123.5001 | -1.2497 | -123.6969
1051.9844 | 123.3673 | -122.4701 | 0.91553 | 0.01231 | 0.0020408 | 0.012014 | 0.10168 | -0.041873 | 0.050762 | 0.11872 | -0.009155 | 1.0437 | -0.37537 | 0.28381 | -122.4472 | -22.2748 | 0.032043 | 1.0162 | 1.0345 | -122.8088 | 122.0947 | 0.12817 | 122.4609 | 122.7539 | -123.3627 | -0.33874 | 0.11902 | 0.36621 | 122.5021 | 123.4863 | 0.022888 | 123.5138 | 122.4609 | 123.5046 | 100.1953 | -0.33874 | 123.5138 | 122.4609 | 100.1953 | 0.022888 | 123.5046 | -1.2909 | -123.7244
1052.9219 | 123.4909 | -122.4609 | 0.86975 | 0.4243 | -0.017185 | -0.00080337 | 0.071775 | -0.039736 | 0.047558 | 0.1294 | 0.032043 | 0.97504 | -0.3479 | 0.12817 | -122.5388 | -22.3434 | 0.17853 | 0.91095 | 1.0483 | -122.8455 | 122.113 | 0.10529 | 122.493 | 122.5891 | -123.4085 | -0.38452 | 0.17853 | 0.37994 | 122.6395 | 123.3719 | -0.07782 | 123.436 | 122.493 | 123.5092 | 100.1175 | -0.38452 | 123.436 | 122.493 | 100.1175 | -0.07782 | 123.5092 | -1.2177 | -123.7152
1053.9844 | 123.4406 | -122.4289 | 0.93384 | 0.43956 | -0.0022312 | -0.020029 | 0.079252 | -0.046145 | 0.060375 | 0.12406 | -0.022888 | 1.0574 | -0.38452 | 0.22888 | -122.4014 | -22.1924 | 0.11444 | 1.0162 | 1.0666 | -122.7493 | 122.0444 | 0.1236 | 122.406 | 122.6578 | -123.3353 | -0.32044 | 0.13275 | 0.36163 | 122.5433 | 123.4451 | 0.027466 | 123.4863 | 122.406 | 123.4955 | 100.2365 | -0.32044 | 123.4863 | 122.406 | 100.2365 | 0.027466 | 123.4955 | -1.3184 | -123.6832
1054.9219 | 123.4772 | -122.4152 | 0.94757 | 0.4243 | -0.0043672 | 0.00026463 | 0.077116 | -0.052554 | 0.04649 | 0.11231 | -0.022888 | 1.0483 | -0.35706 | 0.19226 | -122.4335 | -22.0917 | 0.15106 | 1.0071 | 1.0941 | -122.7219 | 122.0581 | 0.10071 | 122.3923 | 122.6074 | -123.381 | -0.3067 | 0.14648 | 0.33417 | 122.5662 | 123.4222 | -0.018311 | 123.4634 | 122.3923 | 123.5092 | 100.3235 | -0.3067 | 123.4634 | 122.3923 | 100.3235 | -0.018311 | 123.5092 | -1.3046 | -123.6694
1055.9844 | 123.436 | -122.4197 | 0.93384 | 0.14964 | -0.012912 | -0.010416 | 0.070707 | -0.053622 | 0.041149 | 0.1059 | -0.032043 | 1.0345 | -0.35248 | 0.14648 | -122.4426 | -27.5391 | 0.12817 | 1.0025 | 1.0941 | -122.7493 | 122.0673 | 0.10071 | 122.3877 | 122.5662 | -123.3765 | -0.32959 | 0.16022 | 0.32044 | 122.5479 | 123.4222 | -0.022888 | 123.4543 | 122.3877 | 123.5138 | 94.8807 | -0.32959 | 123.4543 | 122.3877 | 94.8807 | -0.022888 | 123.5138 | -1.2863 | -123.6832
1056.9219 | 123.3627 | -122.3145 | 1.062 | -3.6651 | -0.0022312 | -0.010416 | 0.087797 | -0.049349 | 0.05183 | 0.11658 | -0.064087 | 1.1948 | -0.35706 | 0.31128 | -122.287 | -28.1067 | 0.073242 | 1.1902 | 1.1581 | -122.6257 | 121.9574 | 0.13275 | 122.2504 | 122.6257 | -123.349 | -0.31128 | 0.09613 | 0.29297 | 122.3877 | 123.5046 | 0.027466 | 123.5092 | 122.2504 | 123.4726 | 94.2078 | -0.31128 | 123.5092 | 122.2504 | 94.2078 | 0.027466 | 123.4726 | -1.4191 | -123.6877
1057.9844 | 123.3765 | -122.3923 | 0.98419 | -0.0029495 | 0.0020408 | 0.0077416 | 0.093137 | -0.034396 | 0.052898 | 0.12299 | -0.027466 | 1.1261 | -0.36621 | 0.27924 | -122.3236 | -27.1271 | 0.054932 | 1.1215 | 1.1124 | -122.7173 | 122.0261 | 0.14191 | 122.3648 | 122.6715 | -123.3078 | -0.32501 | 0.12817 | 0.33875 | 122.4472 | 123.5138 | 0.068665 | 123.5184 | 122.3648 | 123.5046 | 95.2652 | -0.32501 | 123.5184 | 122.3648 | 95.2652 | 0.068665 | 123.5046 | -1.3504 | -123.7015
1058.9219 | 123.5092 | -122.2595 | 1.0483 | 0.48533 | -0.017185 | -0.023234 | 0.071775 | -0.0376 | 0.039013 | 0.10911 | 0.018311 | 1.149 | -0.35706 | 0.15106 | -122.3969 | -26.4175 | 0.23804 | 1.0437 | 1.1856 | -122.6715 | 121.9025 | 0.10071 | 122.2778 | 122.4106 | -123.4451 | -0.41199 | 0.13733 | 0.37537 | 122.4976 | 123.3032 | -0.13733 | 123.4085 | 122.2778 | 123.4451 | 95.842 | -0.41199 | 123.4085 | 122.2778 | 95.842 | -0.13733 | 123.4451 | -1.4053 | -123.7198
1059.9844 | 123.3994 | -122.3557 | 1.0391 | -0.23183 | 0.0095178 | -0.020029 | 0.085661 | -0.038668 | 0.05183 | 0.11658 | -0.054932 | 1.1581 | -0.38452 | 0.27466 | -122.3145 | -27.7359 | 0.036621 | 1.149 | 1.1536 | -122.6669 | 121.9711 | 0.11902 | 122.3007 | 122.6303 | -123.3536 | -0.31128 | 0.11444 | 0.32959 | 122.3923 | 123.5046 | 0.041199 | 123.5138 | 122.3007 | 123.5092 | 94.6198 | -0.31128 | 123.5138 | 122.3007 | 94.6198 | 0.041199 | 123.5092 | -1.4236 | -123.7061
1060.9219 | 123.3673 | -122.0947 | 1.2726 | 0.40904 | 0.00097275 | -0.0061444 | 0.087797 | -0.025851 | 0.049694 | 0.11552 | -0.091553 | 1.4008 | -0.3891 | 0.37079 | -122.0215 | -23.5565 | 0.10529 | 1.4191 | 1.3733 | -122.4289 | 121.7056 | 0.12817 | 122.0032 | 122.4655 | -123.2941 | -0.33417 | 0.10071 | 0.29755 | 122.2 | 123.5138 | 0.073243 | 123.4955 | 122.0032 | 123.468 | 98.5382 | -0.33417 | 123.4955 | 122.0032 | 98.5382 | 0.073243 | 123.468 | -1.6617 | -123.7015
1061.9844 | 123.3719 | -122.2275 | 1.1581 | 0.10386 | 0.012723 | -0.0040084 | 0.08032 | -0.041873 | 0.060375 | 0.11765 | -0.059509 | 1.3138 | -0.39825 | 0.3067 | -122.0901 | -22.9752 | 0.09613 | 1.2772 | 1.3 | -122.5342 | 121.8292 | 0.15564 | 122.168 | 122.5342 | -123.2483 | -0.3067 | 0.14191 | 0.33875 | 122.3236 | 123.5046 | 0.13733 | 123.5413 | 122.168 | 123.5275 | 99.2523 | -0.3067 | 123.5413 | 122.168 | 99.2523 | 0.13733 | 123.5275 | -1.5564 | -123.6923
1062.9219 | 123.4085 | -122.2321 | 1.1307 | -0.27761 | -0.0022312 | -0.00080337 | 0.091001 | -0.03226 | 0.055035 | 0.11124 | 0.027466 | 1.3229 | -0.34332 | 0.30212 | -122.2183 | -23.172 | 0.10986 | 1.2863 | 1.2634 | -122.5296 | 121.8887 | 0.19226 | 122.2595 | 122.5342 | -123.349 | -0.29755 | 0.13275 | 0.37079 | 122.3419 | 123.5184 | 0.013733 | 123.555 | 122.2595 | 123.4955 | 99.0601 | -0.29755 | 123.555 | 122.2595 | 99.0601 | 0.013733 | 123.4955 | -1.474 | -123.6603
1063.9844 | 123.3948 | -122.1405 | 1.268 | -0.36916 | 0.00097275 | -0.016825 | 0.072843 | -0.033328 | 0.04649 | 0.1027 | -0.10071 | 1.3412 | -0.40741 | 0.48981 | -121.8201 | -29.3976 | -0.041199 | 1.387 | 1.4008 | -122.4243 | 121.7331 | 0.073243 | 122.0398 | 122.6303 | -123.0881 | -0.28381 | 0.13275 | 0.3067 | 122.0993 | 123.5275 | 0.32043 | 123.4818 | 122.0398 | 123.5413 | 92.7429 | -0.28381 | 123.4818 | 122.0398 | 92.7429 | 0.32043 | 123.5413 | -1.6754 | -123.6923
1064.9219 | 123.3673 | -122.0947 | 1.2817 | 0.073345 | 0.0031088 | 0.0056046 | 0.087797 | -0.040805 | 0.061443 | 0.11979 | -0.073242 | 1.4099 | -0.40283 | 0.36163 | -122.049 | -26.976 | 0.10071 | 1.4465 | 1.4099 | -122.4335 | 121.6919 | 0.12817 | 122.0215 | 122.4564 | -123.3307 | -0.33874 | 0.12817 | 0.32959 | 122.1954 | 123.5413 | 0.045777 | 123.5046 | 122.0215 | 123.5046 | 95.1187 | -0.33874 | 123.5046 | 122.0215 | 95.1187 | 0.045777 | 123.5046 | -1.6846 | -123.7152
1065.9844 | 123.4589 | -122.2137 | 1.1261 | -0.30813 | -0.02573 | -0.020029 | 0.068571 | -0.035464 | 0.040081 | 0.11338 | -0.032043 | 1.2222 | -0.35706 | -0.09613 | -122.3053 | -27.2049 | 0.26093 | 1.0391 | 1.3 | -122.6074 | 121.8567 | 0.09613 | 122.1817 | 122.1176 | -123.4314 | -0.39368 | 0.17395 | 0.32501 | 122.4747 | 123.2529 | -0.091553 | 123.436 | 122.1817 | 123.5138 | 95.0088 | -0.39368 | 123.436 | 122.1817 | 95.0088 | -0.091553 | 123.5138 | -1.4832 | -123.7335
1066.9219 | 123.3536 | -122.3236 | 1.0757 | 0.25645 | -0.0011632 | -0.0040084 | 0.077116 | -0.042941 | 0.060375 | 0.12086 | -0.059509 | 1.1581 | -0.41199 | 0.93384 | -122.2275 | -27.6306 | 0.64087 | 1.2268 | 1.1673 | -122.6486 | 121.9116 | 0.082397 | 122.2641 | 123.2574 | -123.3032 | -0.32501 | 0.091552 | 0.35248 | 122.9645 | 123.5504 | 0.09613 | 123.4817 | 122.2641 | 123.4909 | 94.693 | -0.32501 | 123.4817 | 122.2641 | 94.693 | 0.09613 | 123.4909 | -1.4877 | -123.7244
1067.9844 | 123.4131 | -122.287 | 1.0895 | -0.12502 | -0.0086402 | -0.0050764 | 0.068571 | -0.038668 | 0.048626 | 0.11552 | -0.022888 | 1.2085 | -0.40283 | 1.0162 | -122.2824 | -27.2324 | 0.88348 | 1.181 | 1.2131 | -122.6166 | 121.8842 | 0.11902 | 122.2641 | 123.3032 | -123.3719 | -0.32959 | 0.1236 | 0.37994 | 123.1705 | 123.468 | 0.004577 | 123.4955 | 122.2641 | 123.5001 | 95.0546 | -0.32959 | 123.4955 | 122.2641 | 95.0546 | 0.004577 | 123.5001 | -1.4923 | -123.7061
1068.9219 | 123.3902 | -122.2458 | 1.1307 | -0.18605 | -0.0011632 | -0.014689 | 0.084592 | -0.025851 | 0.04649 | 0.12193 | -0.16937 | 1.593 | -0.45776 | 1.0757 | -122.1817 | -25.8087 | 0.94757 | 1.2497 | 1.2955 | -122.5571 | 121.788 | 0.46234 | 122.0764 | 123.3215 | -123.3124 | -0.31128 | 0.1648 | 0.28839 | 123.1934 | 123.4955 | 0.064087 | 123.8388 | 122.0764 | 123.5413 | 96.4371 | -0.31128 | 123.8388 | 122.0764 | 96.4371 | 0.064087 | 123.5413 | -1.5884 | -123.6877
1069.9219 | 123.3902 | -122.3557 | 1.0391 | -0.33864 | 0.0020408 | -0.034983 | 0.071775 | -0.036532 | 0.053967 | 0.11231 | -0.16937 | 1.181 | -0.52185 | 0.97504 | -122.3465 | -19.4641 | 0.79651 | 1.1581 | 1.1856 | -122.6898 | 121.8338 | 0.14191 | 122.1863 | 123.3307 | -123.3856 | -0.33417 | 0.14648 | 0.35248 | 123.1522 | 123.5138 | 0.009155 | 123.5367 | 122.1863 | 123.5413 | 102.8915 | -0.33417 | 123.5367 | 122.1863 | 102.8915 | 0.009155 | 123.5413 | -1.561 | -123.7289
1070.9844 | 123.3719 | -122.3877 | 1.0529 | -0.3539 | -0.0086402 | -0.0040084 | 0.072843 | -0.044009 | 0.05183 | 0.11124 | -0.27924 | 1.1398 | -0.58594 | 0.95215 | -122.2229 | -19.7205 | 0.72784 | 1.1902 | 1.1948 | -122.6852 | 121.8018 | 0.086976 | 122.1085 | 123.3398 | -123.2758 | -0.29755 | 0.14191 | 0.3067 | 123.1155 | 123.5779 | 0.16479 | 123.5275 | 122.1085 | 123.5825 | 102.6672 | -0.29755 | 123.5275 | 122.1085 | 102.6672 | 0.16479 | 123.5825 | -1.6388 | -123.7381
1071.9219 | 123.3719 | -122.3831 | 1.0162 | -0.079243 | 0.0063138 | -0.012553 | 0.091001 | -0.034396 | 0.061443 | 0.10911 | -0.24261 | 1.1673 | -0.66376 | 0.97504 | -122.3511 | -19.6518 | 0.81024 | 1.1353 | 1.149 | -122.7173 | 121.7194 | 0.15106 | 122.1405 | 123.3582 | -123.3673 | -0.33417 | 0.13275 | 0.42114 | 123.1934 | 123.5184 | 0.032044 | 123.5504 | 122.1405 | 123.5321 | 102.7313 | -0.33417 | 123.5504 | 122.1405 | 102.7313 | 0.032044 | 123.5321 | -1.68 | -123.7335
1072.9219 | 123.4131 | -122.3602 | 1.0208 | -0.41494 | -0.0054352 | 0.0045366 | 0.085661 | -0.033328 | 0.049694 | 0.11552 | -1.0666 | 1.1398 | -1.474 | 0.92468 | -122.3694 | -19.7067 | 0.80109 | 1.0895 | 1.1581 | -122.7264 | 120.8862 | 0.11902 | 121.2936 | 123.2849 | -123.3902 | -0.36621 | 0.13733 | 0.40741 | 123.1613 | 123.4497 | -0.009156 | 123.5001 | 121.2936 | 123.5184 | 102.6535 | -0.36621 | 123.5001 | 121.2936 | 102.6535 | -0.009156 | 123.5184 | -2.4948 | -123.7473
1073.9844 | 123.4634 | -122.2275 | 1.0941 | 0.74473 | -0.026798 | 0.0024006 | 0.052549 | -0.0376 | 0.033672 | 0.12513 | -1.2497 | 1.1032 | -1.5839 | 0.91095 | -122.319 | -19.8624 | 0.94299 | 1.1581 | 1.2589 | -122.612 | 120.6436 | 0.009155 | 120.9778 | 123.1384 | -123.4131 | -0.38452 | 0.1648 | 0.33417 | 123.1705 | 123.3856 | -0.091553 | 123.3307 | 120.9778 | 123.4863 | 102.3651 | -0.38452 | 123.3307 | 120.9778 | 102.3651 | -0.091553 | 123.4863 | -2.6779 | -123.7061
1074.9219 | 123.4085 | -122.2321 | 1.1444 | -0.32338 | -0.0043672 | -0.015757 | 0.064298 | -0.033328 | 0.048626 | 0.11765 | -0.2243 | 1.2497 | -0.58594 | 0.29755 | -122.2641 | -20.2927 | 0.09613 | 1.2405 | 1.2726 | -122.5845 | 121.6461 | 0.10529 | 122.0078 | 122.5296 | -123.4085 | -0.35248 | 0.12817 | 0.36163 | 122.3282 | 123.4726 | -0.032043 | 123.4818 | 122.0078 | 123.5046 | 101.9394 | -0.35248 | 123.4818 | 122.0078 | 101.9394 | -0.032043 | 123.5046 | -1.7303 | -123.7289
1075.9219 | 123.3536 | -122.3099 | 1.0895 | -0.38442 | -0.0032992 | -0.017893 | 0.071775 | -0.042941 | 0.057171 | 0.12299 | -0.18768 | 1.2177 | -0.50354 | 0.99792 | -122.2641 | -20.2606 | 0.77362 | 1.2314 | 1.2039 | -122.6303 | 121.8063 | 0.12817 | 122.1222 | 123.3078 | -123.3536 | -0.32043 | 0.11444 | 0.31586 | 123.0835 | 123.5413 | 0.045776 | 123.5275 | 122.1222 | 123.5138 | 102.0493 | -0.32043 | 123.5275 | 122.1222 | 102.0493 | 0.045776 | 123.5138 | -1.593 | -123.7198
1076.9219 | 123.3673 | -122.2504 | 1.1719 | -0.36916 | -0.015048 | -0.033915 | 0.069639 | -0.040805 | 0.04649 | 0.11231 | -0.16479 | 1.2726 | -0.53558 | 0.28839 | -122.2092 | -20.018 | 0.07782 | 1.3092 | 1.2909 | -122.5479 | 121.7148 | 0.10071 | 122.0856 | 122.5388 | -123.381 | -0.29755 | 0.11902 | 0.37079 | 122.3282 | 123.5596 | 0.041199 | 123.5229 | 122.0856 | 123.5413 | 102.2324 | -0.29755 | 123.5229 | 122.0856 | 102.2324 | 0.041199 | 123.5413 | -1.7075 | -123.7198
1077.9844 | 123.436 | -122.2549 | 1.0895 | -0.49123 | -0.02573 | -0.021098 | 0.049345 | -0.041873 | 0.036877 | 0.12086 | -0.14191 | 1.1902 | -0.49439 | 0.1831 | -122.3511 | -20.3705 | 0.15564 | 1.149 | 1.2497 | -122.6303 | 121.7606 | 0.10071 | 122.113 | 122.438 | -123.4406 | -0.37537 | 0.16022 | 0.35248 | 122.4106 | 123.4039 | -0.09613 | 123.4451 | 122.113 | 123.5046 | 101.8845 | -0.37537 | 123.4451 | 122.113 | 101.8845 | -0.09613 | 123.5046 | -1.5839 | -123.7198
1078.9219 | 123.4222 | -122.2229 | 1.1673 | -0.048725 | 0.0073818 | 0.0098776 | 0.095274 | -0.044009 | 0.062512 | 0.10804 | -0.13733 | 1.2589 | -0.53101 | 0.28839 | -122.2092 | -20.4941 | 0.15106 | 1.2314 | 1.2909 | -122.5891 | 121.6919 | 0.091553 | 122.0856 | 122.5113 | -123.3765 | -0.36621 | 0.1236 | 0.39368 | 122.374 | 123.4543 | 0.013733 | 123.4817 | 122.0856 | 123.5138 | 101.7288 | -0.36621 | 123.4817 | 122.0856 | 101.7288 | 0.013733 | 123.5138 | -1.6983 | -123.7564
1079.9844 | 123.4314 | -122.2183 | 1.149 | -0.44545 | -0.022525 | -0.021098 | 0.072843 | -0.027987 | 0.04649 | 0.11658 | -0.10529 | 1.2177 | -0.48523 | 0.2243 | -122.2824 | -20.4391 | 0.13733 | 1.2131 | 1.2955 | -122.5662 | 121.7331 | 0.068664 | 122.113 | 122.4426 | -123.4314 | -0.3479 | 0.14648 | 0.37994 | 122.3557 | 123.4314 | -0.064087 | 123.436 | 122.113 | 123.5138 | 101.7792 | -0.3479 | 123.436 | 122.113 | 101.7792 | -0.064087 | 123.5138 | -1.6342 | -123.7152
1080.9219 | 123.3582 | -122.2641 | 1.1398 | -0.4302 | -0.0086402 | -0.013621 | 0.089933 | -0.047213 | 0.045422 | 0.11872 | -0.1831 | 1.2634 | -0.50812 | 0.30212 | -122.2321 | -19.7845 | 0.050354 | 1.2726 | 1.2405 | -122.5891 | 121.756 | 0.1236 | 122.081 | 122.5662 | -123.3719 | -0.32501 | 0.10071 | 0.32501 | 122.3145 | 123.5367 | 0.032043 | 123.5275 | 122.081 | 123.5046 | 102.4796 | -0.32501 | 123.5275 | 122.081 | 102.4796 | 0.032043 | 123.5046 | -1.6479 | -123.7289
1081.9844 | 123.4451 | -122.2229 | 1.0712 | 0.37852 | -0.0097082 | -0.026438 | 0.06323 | -0.047213 | 0.037945 | 0.11338 | -0.10529 | 1.1627 | -0.44403 | 0.16937 | -122.3373 | -19.9493 | 0.23804 | 1.1124 | 1.2634 | -122.6257 | 121.7789 | 0.091553 | 122.1176 | 122.3923 | -123.4085 | -0.40283 | 0.19226 | 0.33875 | 122.4609 | 123.3353 | -0.11444 | 123.3856 | 122.1176 | 123.4863 | 102.2736 | -0.40283 | 123.3856 | 122.1176 | 102.2736 | -0.11444 | 123.4863 | -1.5152 | -123.6969
1082.9219 | 123.468 | -122.2733 | 1.0483 | -1.1626 | -0.012912 | -0.0093484 | 0.061094 | -0.044009 | 0.041149 | 0.1294 | -0.1236 | 1.1078 | -0.4715 | 0.16022 | -122.4289 | -19.899 | 0.19226 | 1.0574 | 1.2177 | -122.6898 | 121.8018 | 0.059509 | 122.1497 | 122.4335 | -123.4772 | -0.41657 | 0.16937 | 0.3479 | 122.4655 | 123.3307 | -0.15564 | 123.381 | 122.1497 | 123.4909 | 102.3743 | -0.41657 | 123.381 | 122.1497 | 102.3743 | -0.15564 | 123.4909 | -1.5198 | -123.7381
1083.9844 | 123.4955 | -122.2366 | 1.0529 | -0.20131 | -0.02573 | -0.028574 | 0.051481 | -0.05469 | 0.036877 | 0.11872 | -0.11444 | 1.1353 | -0.45776 | 0.11902 | -122.438 | -19.7845 | 0.2243 | 1.0574 | 1.2314 | -122.6486 | 121.7789 | 0.082398 | 122.1222 | 122.3557 | -123.4909 | -0.41199 | 0.17853 | 0.34332 | 122.4609 | 123.2941 | -0.20142 | 123.3719 | 122.1222 | 123.468 | 102.4521 | -0.41199 | 123.3719 | 122.1222 | 102.4521 | -0.20142 | 123.468 | -1.5106 | -123.7015
1084.9219 | 123.4497 | -122.3007 | 1.0345 | -0.24709 | -0.015048 | -0.017893 | 0.073911 | -0.05469 | 0.035809 | 0.11231 | -0.12817 | 1.1124 | -0.5127 | 0.16937 | -122.4152 | -20.0409 | 0.17395 | 1.0574 | 1.2039 | -122.6669 | 121.788 | 0.07782 | 122.1725 | 122.4701 | -123.4497 | -0.36621 | 0.16937 | 0.38452 | 122.4747 | 123.3582 | -0.11444 | 123.4131 | 122.1725 | 123.5046 | 102.2598 | -0.36621 | 123.4131 | 122.1725 | 102.2598 | -0.11444 | 123.5046 | -1.5472 | -123.7015
1085.9844 | 123.436 | -122.3511 | 0.98877 | 0.24119 | -0.022525 | -0.031779 | 0.061094 | -0.049349 | 0.031536 | 0.12406 | -0.20142 | 1.1124 | -0.5127 | 0.17853 | -122.4197 | -20.1141 | 0.15106 | 1.0483 | 1.1673 | -122.6898 | 121.8384 | 0.1236 | 122.1497 | 122.5296 | -123.4085 | -0.33875 | 0.17853 | 0.31128 | 122.5021 | 123.3994 | -0.068665 | 123.4634 | 122.1497 | 123.5184 | 102.2369 | -0.33875 | 123.4634 | 122.1497 | 102.2369 | -0.068665 | 123.5184 | -1.5015 | -123.6786
1086.9219 | 123.3673 | -122.3831 | 1.0162 | -0.33864 | -0.021457 | -0.026438 | 0.082456 | -0.058962 | 0.040081 | 0.097358 | -0.20142 | 1.1261 | -0.53558 | 0.29297 | -122.3602 | -19.6564 | 0.036621 | 1.1215 | 1.1353 | -122.6898 | 121.8475 | 0.10986 | 122.1817 | 122.6761 | -123.3765 | -0.3067 | 0.11902 | 0.33417 | 122.4197 | 123.5046 | 0.022889 | 123.5092 | 122.1817 | 123.5184 | 102.7267 | -0.3067 | 123.5092 | 122.1817 | 102.7267 | 0.022889 | 123.5184 | -1.5518 | -123.7061
1087.9844 | 123.436 | -122.2824 | 1.0391 | 0.39378 | -0.01398 | -0.0050764 | 0.078184 | -0.048281 | 0.041149 | 0.11445 | -0.13733 | 1.1078 | -0.46234 | 0.19226 | -122.3785 | -20.0684 | 0.19226 | 1.0849 | 1.1902 | -122.6624 | 121.8201 | 0.068664 | 122.1451 | 122.4747 | -123.4177 | -0.37994 | 0.15106 | 0.32501 | 122.4747 | 123.3673 | -0.09613 | 123.3902 | 122.1451 | 123.4726 | 102.2141 | -0.37994 | 123.3902 | 122.1451 | 102.2141 | -0.09613 | 123.4726 | -1.5015 | -123.7015
1088.9219 | 123.5092 | -122.2504 | 1.0529 | -0.15554 | -0.0054352 | -0.046732 | 0.072843 | -0.049349 | 0.035809 | 0.11124 | -0.20142 | 1.1215 | -0.51727 | 0.10529 | -122.4747 | -22.0505 | 0.20599 | 1.0117 | 1.1993 | -122.7036 | 121.7331 | 0.068665 | 122.049 | 122.3557 | -123.5275 | -0.45319 | 0.14648 | 0.31586 | 122.4564 | 123.262 | -0.2243 | 123.3719 | 122.049 | 123.4497 | 100.1999 | -0.45319 | 123.3719 | 122.049 | 100.1999 | -0.2243 | 123.4497 | -1.5701 | -123.7564
1089.9844 | 123.5138 | -122.3969 | 0.9201 | -0.079243 | -0.023593 | -0.010416 | 0.058958 | -0.050418 | 0.031536 | 0.10911 | -0.17853 | 1.03 | -0.52185 | 0.74616 | -122.5616 | -22.8653 | 0.82398 | 0.92926 | 1.1169 | -122.7905 | 121.875 | 0.10986 | 122.2183 | 123.143 | -123.4818 | -0.39368 | 0.19684 | 0.34332 | 123.2208 | 123.3261 | -0.16479 | 123.4268 | 122.2183 | 123.5138 | 99.5316 | -0.39368 | 123.4268 | 122.2183 | 99.5316 | -0.16479 | 123.5138 | -1.442 | -123.7106
1090.9219 | 123.5184 | -122.2458 | 1.03 | -0.048725 | -0.022525 | -0.018961 | 0.065366 | -0.056826 | 0.044354 | 0.11445 | -0.12817 | 1.149 | -0.47607 | 0.8606 | -122.4564 | -20.874 | 0.032043 | 0.99792 | 1.2177 | -122.6807 | 121.7697 | 0.11902 | 122.1176 | 123.1064 | -123.4863 | -0.43487 | 0.18768 | 0.3479 | 122.2778 | 123.2437 | -0.21057 | 123.3948 | 122.1176 | 123.4634 | 101.3718 | -0.43487 | 123.3948 | 122.1176 | 101.3718 | -0.21057 | 123.4634 | -1.506 | -123.7106
1091.9844 | 123.4909 | -122.4655 | 0.94757 | 0.25645 | -0.019321 | -0.022166 | 0.067503 | -0.057894 | 0.017651 | 0.10697 | -0.21515 | 1.0803 | -0.52643 | 0.86975 | -122.4289 | -20.7184 | 0.8194 | 1.0391 | 1.1536 | -122.7173 | 121.9391 | 0.13275 | 122.2504 | 123.3353 | -123.3765 | -0.25177 | 0.20599 | 0.31128 | 123.2849 | 123.5046 | 0.036621 | 123.5458 | 122.2504 | 123.6191 | 101.7471 | -0.25177 | 123.5458 | 122.2504 | 101.7471 | 0.036621 | 123.6191 | -1.474 | -123.6649
1092.9219 | 123.3948 | -122.3602 | 1.0162 | -0.44545 | -0.017185 | -0.00080337 | 0.082456 | -0.049349 | 0.040081 | 0.11872 | -0.17395 | 1.1078 | -0.5127 | 0.93842 | -122.4197 | -20.8557 | 0.79651 | 1.0895 | 1.1398 | -122.7081 | 121.8475 | 0.091553 | 122.1863 | 123.2986 | -123.436 | -0.3479 | 0.1236 | 0.33875 | 123.1567 | 123.4497 | -0.05951 | 123.468 | 122.1863 | 123.5001 | 101.5045 | -0.3479 | 123.468 | 122.1863 | 101.5045 | -0.05951 | 123.5001 | -1.5289 | -123.7244
1093.9844 | 123.4772 | -122.3694 | 0.9201 | 0.48533 | -0.024662 | -0.028574 | 0.082456 | -0.052554 | 0.047558 | 0.12299 | -0.10071 | 1.0391 | -0.49896 | 0.82398 | -122.5067 | -20.2698 | 0.86517 | 0.94757 | 1.1261 | -122.7493 | 121.8704 | 0.11902 | 122.2687 | 123.1934 | -123.4268 | -0.37994 | 0.20599 | 0.39825 | 123.2346 | 123.317 | -0.13733 | 123.4085 | 122.2687 | 123.4955 | 102.0996 | -0.37994 | 123.4085 | 122.2687 | 102.0996 | -0.13733 | 123.4955 | -1.4191 | -123.6694
1094.9219 | 123.5001 | -122.2641 | 1.062 | -0.063984 | -0.024662 | -0.039256 | 0.070707 | -0.055758 | 0.031536 | 0.11552 | -0.13275 | 1.1581 | -0.48065 | 0.90637 | -122.4014 | -20.6726 | 0.013733 | 1.0712 | 1.2131 | -122.6349 | 121.7834 | 0.09613 | 122.1313 | 123.1705 | -123.4634 | -0.37079 | 0.15106 | 0.3479 | 122.2778 | 123.3353 | -0.13733 | 123.4222 | 122.1313 | 123.4772 | 101.5915 | -0.37079 | 123.4222 | 122.1313 | 101.5915 | -0.13733 | 123.4772 | -1.5427 | -123.6969
1095.9844 | 123.5687 | -122.3785 | 0.94757 | 0.48533 | -0.015048 | -0.0040084 | 0.078184 | -0.055758 | 0.045422 | 0.1027 | -0.10986 | 1.0895 | -0.46692 | 0.87891 | -122.4152 | -20.8099 | 0.027466 | 0.94757 | 1.1856 | -122.731 | 121.9116 | 0.14191 | 122.2687 | 123.2574 | -123.3627 | -0.35248 | 0.23804 | 0.35706 | 122.406 | 123.3261 | -0.036621 | 123.468 | 122.2687 | 123.5641 | 101.5686 | -0.35248 | 123.468 | 122.2687 | 101.5686 | -0.036621 | 123.5641 | -1.4145 | -123.6786
1096.9219 | 123.4451 | -122.374 | 0.96588 | 0.13438 | -0.012912 | 0.0013326 | 0.067503 | -0.050418 | 0.036877 | 0.11552 | -0.17853 | 1.0895 | -0.48065 | 0.86517 | -122.4289 | -20.5765 | 0.80566 | 1.0208 | 1.1307 | -122.7081 | 121.8933 | 0.1236 | 122.1954 | 123.2391 | -123.3948 | -0.33417 | 0.1648 | 0.30212 | 123.1796 | 123.3948 | -0.054932 | 123.4634 | 122.1954 | 123.5046 | 101.7975 | -0.33417 | 123.4634 | 122.1954 | 101.7975 | -0.054932 | 123.5046 | -1.4465 | -123.674
1097.9844 | 123.4543 | -122.374 | 0.95673 | 0.10386 | -0.0086402 | -0.032847 | 0.082456 | -0.057894 | 0.048626 | 0.11445 | -0.36163 | 1.1032 | -0.55847 | 0.83771 | -122.4747 | -20.755 | 0.8194 | 1.0162 | 1.0803 | -122.7356 | 121.8155 | 0.14648 | 122.0123 | 123.2117 | -123.4314 | -0.36163 | 0.1236 | 0.19684 | 123.1934 | 123.3902 | -0.10071 | 123.4772 | 122.0123 | 123.4543 | 101.619 | -0.36163 | 123.4772 | 122.0123 | 101.619 | -0.10071 | 123.4543 | -1.5152 | -123.6923
1098.9219 | 123.4726 | -122.3785 | 0.97046 | -0.15554 | -0.019321 | -0.027506 | 0.072843 | -0.060031 | 0.027264 | 0.10056 | -0.2243 | 1.0071 | -0.55389 | 0.84228 | -122.4747 | -21.1853 | 0.82855 | 1.0071 | 1.1261 | -122.7173 | 121.8246 | 0.036621 | 122.1542 | 123.2208 | -123.4451 | -0.33875 | 0.15564 | 0.32959 | 123.2071 | 123.3856 | -0.09613 | 123.3856 | 122.1542 | 123.5046 | 101.1932 | -0.33875 | 123.3856 | 122.1542 | 101.1932 | -0.09613 | 123.5046 | -1.5244 | -123.6877
1099.9844 | 123.3444 | -122.4289 | 0.96588 | 0.27171 | -0.0075722 | -0.010416 | 0.10702 | -0.048281 | 0.050762 | 0.11445 | -0.19684 | 1.0849 | -0.54016 | 1.0071 | -122.3648 | -21.3089 | 0.70038 | 1.0986 | 1.0666 | -122.7448 | 121.8887 | 0.11902 | 122.2321 | 123.436 | -123.3307 | -0.31586 | 0.10071 | 0.34332 | 123.1293 | 123.5275 | 0.064087 | 123.5138 | 122.2321 | 123.4955 | 101.12 | -0.31586 | 123.5138 | 122.2321 | 101.12 | 0.064087 | 123.4955 | -1.506 | -123.7106
1100.9219 | 123.4543 | -122.3877 | 0.96588 | 0.042827 | -0.022525 | -0.034983 | 0.062162 | -0.046145 | 0.025128 | 0.10377 | -0.17395 | 1.0483 | -0.47607 | 0.84686 | -122.4335 | -21.5286 | 0.82398 | 1.0208 | 1.1215 | -122.7219 | 121.9116 | 0.082398 | 122.2137 | 123.2346 | -123.3994 | -0.33417 | 0.15564 | 0.30212 | 123.2117 | 123.4085 | -0.045777 | 123.436 | 122.2137 | 123.5092 | 100.8591 | -0.33417 | 123.436 | 122.2137 | 100.8591 | -0.045777 | 123.5092 | -1.442 | -123.6877
1101.9844 | 123.3673 | -122.0673 | 1.2955 | 0.4243 | -0.019321 | 0.0066726 | 0.06323 | -0.05469 | 0.037945 | 0.1262 | -0.13733 | 1.268 | -0.46692 | 1.0529 | -122.0856 | -22.2794 | 1.2405 | 1.4557 | 1.4648 | -122.4152 | 121.6003 | -0.027466 | 121.9299 | 123.1201 | -123.381 | -0.3479 | 0.16937 | 0.32959 | 123.3078 | 123.5229 | -0.01831 | 123.3353 | 121.9299 | 123.5321 | 99.7879 | -0.3479 | 123.3353 | 121.9299 | 99.7879 | -0.01831 | 123.5321 | -1.7624 | -123.7106
1102.9219 | 123.5001 | -122.2549 | 1.0666 | -0.079243 | -0.0011632 | -0.012553 | 0.083524 | -0.061099 | 0.04649 | 0.11445 | -0.17395 | 1.1169 | -0.50812 | 0.95215 | -122.3373 | -21.3455 | 0.99335 | 1.0666 | 1.2497 | -122.612 | 121.7468 | 0.050354 | 122.081 | 123.2071 | -123.4039 | -0.35706 | 0.18311 | 0.33417 | 123.2483 | 123.3215 | -0.082397 | 123.3719 | 122.081 | 123.5046 | 100.9094 | -0.35706 | 123.3719 | 122.081 | 100.9094 | -0.082397 | 123.5046 | -1.5747 | -123.6786
1103.9688 | 123.3765 | -122.2137 | 1.1856 | 0.18016 | 0.0041778 | -0.021098 | 0.10489 | -0.0376 | 0.064648 | 0.10377 | -0.18768 | 1.2909 | -0.53101 | 1.1993 | -122.1405 | -21.6888 | 0.90179 | 1.3138 | 1.2909 | -122.5342 | 121.6827 | 0.10529 | 122.0261 | 123.4131 | -123.3261 | -0.32044 | 0.10529 | 0.34332 | 123.1155 | 123.5275 | 0.073242 | 123.5046 | 122.0261 | 123.5046 | 100.5249 | -0.32044 | 123.5046 | 122.0261 | 100.5249 | 0.073242 | 123.5046 | -1.7166 | -123.7198
1104.9219 | 123.4634 | -122.0901 | 1.2314 | 2.118 | -0.010776 | -0.0018714 | 0.08032 | -0.049349 | 0.044354 | 0.12193 | -0.064087 | 1.2543 | -0.52643 | 1.0986 | -122.1817 | -21.1395 | 1.1536 | 1.2451 | 1.4008 | -122.4426 | 121.5637 | 0.022888 | 122.0261 | 123.1888 | -123.4131 | -0.35248 | 0.16937 | 0.46234 | 123.2437 | 123.3353 | -0.091553 | 123.3444 | 122.0261 | 123.4909 | 100.9506 | -0.35248 | 123.3444 | 122.0261 | 100.9506 | -0.091553 | 123.4909 | -1.7578 | -123.674
1105.9844 | 123.3719 | -122.0993 | 1.3 | 0.48533 | 0.0041778 | -0.022166 | 0.092069 | -0.035464 | 0.055035 | 0.10377 | -0.19684 | 1.3962 | -0.54474 | 1.4969 | -122.1497 | -21.6339 | 1.0941 | 1.4877 | 1.4099 | -122.3969 | 121.5546 | 0.09613 | 121.9025 | 123.5962 | -123.4497 | -0.29755 | 0.10986 | 0.3479 | 123.1934 | 123.587 | -0.050354 | 123.4955 | 121.9025 | 123.5092 | 100.4654 | -0.29755 | 123.4955 | 121.9025 | 100.4654 | -0.050354 | 123.5092 | -1.8448 | -123.6969
1106.9219 | 123.4177 | -122.0306 | 1.3046 | 0.348 | -0.0075722 | -0.0050764 | 0.062162 | -0.060031 | 0.034741 | 0.11765 | -0.22888 | 1.3458 | -0.55389 | 1.1581 | -122.081 | -21.73 | 1.1856 | 1.3687 | 1.442 | -122.3785 | 121.4767 | 0.041199 | 121.8018 | 123.1888 | -123.3856 | -0.3479 | 0.13733 | 0.32501 | 123.2162 | 123.3994 | -0.050354 | 123.3765 | 121.8018 | 123.4726 | 100.3006 | -0.3479 | 123.3765 | 121.8018 | 100.3006 | -0.050354 | 123.4726 | -1.8585 | -123.6832
1107.9844 | 123.3856 | -122.168 | 1.2268 | 0.073345 | 0.0031088 | 0.015218 | 0.087797 | -0.042941 | 0.066784 | 0.11445 | -0.20142 | 1.3733 | -0.53101 | 1.2543 | -122.0856 | -22.1695 | 0.99792 | 1.3458 | 1.3504 | -122.4564 | 121.637 | 0.14648 | 121.9666 | 123.4222 | -123.3124 | -0.28839 | 0.1236 | 0.32959 | 123.1659 | 123.5138 | 0.082398 | 123.5413 | 121.9666 | 123.5184 | 99.9985 | -0.28839 | 123.5413 | 121.9666 | 99.9985 | 0.082398 | 123.5184 | -1.7578 | -123.6832
1108.9219 | 123.5001 | -122.0947 | 1.1902 | 0.39378 | -0.0054352 | -0.021098 | 0.072843 | -0.040805 | 0.044354 | 0.11872 | -0.15106 | 1.268 | -0.49439 | 1.0666 | -122.2046 | -21.9177 | 1.1398 | 1.2222 | 1.3641 | -122.4792 | 121.6003 | 0.077819 | 121.9437 | 123.1613 | -123.3948 | -0.38452 | 0.17395 | 0.34332 | 123.2346 | 123.317 | -0.10986 | 123.3627 | 121.9437 | 123.4589 | 100.177 | -0.38452 | 123.3627 | 121.9437 | 100.177 | -0.10986 | 123.4589 | -1.6846 | -123.6694
1109.9219 | 123.4039 | -122.3145 | 1.0437 | 0.37852 | -0.0032992 | -0.013621 | 0.091001 | -0.040805 | 0.055035 | 0.10697 | -0.21515 | 1.1536 | -0.54474 | 1.03 | -122.3007 | -22.9248 | 0.83771 | 1.1719 | 1.149 | -122.6715 | 121.7697 | 0.10986 | 122.0993 | 123.3444 | -123.3444 | -0.35706 | 0.10529 | 0.32959 | 123.1522 | 123.4863 | 0.013733 | 123.468 | 122.0993 | 123.4634 | 99.3896 | -0.35706 | 123.468 | 122.0993 | 99.3896 | 0.013733 | 123.4634 | -1.5884 | -123.7152
1110.9219 | 123.381 | -122.3465 | 1.0757 | 0.39378 | -0.0011632 | 0.0056046 | 0.088865 | -0.042941 | 0.039013 | 0.11658 | 0.009155 | 1.1719 | -0.55389 | 1.0941 | -122.2275 | -22.4167 | 0.80566 | 1.1856 | 1.181 | -122.6395 | 121.7926 | 0.09613 | 122.3557 | 123.4406 | -123.3032 | -0.29297 | 0.10529 | 0.56305 | 123.1522 | 123.5321 | 0.11902 | 123.5184 | 122.3557 | 123.5275 | 99.9298 | -0.29297 | 123.5184 | 122.3557 | 99.9298 | 0.11902 | 123.5275 | -1.6296 | -123.7152
1111.9844 | 123.381 | -122.2504 | 1.1124 | -0.30813 | -0.0022312 | -0.021098 | 0.082456 | -0.038668 | 0.064648 | 0.11872 | -0.23804 | 1.2085 | -0.61798 | 1.0574 | -122.2595 | -22.7188 | 0.90637 | 1.2085 | 1.236 | -122.6028 | 121.6324 | 0.09613 | 122.0123 | 123.3078 | -123.3719 | -0.35248 | 0.1236 | 0.37994 | 123.1567 | 123.4589 | -0.009155 | 123.4589 | 122.0123 | 123.4863 | 99.5316 | -0.35248 | 123.4589 | 122.0123 | 99.5316 | -0.009155 | 123.4863 | -1.7303 | -123.7152
1112.9219 | 123.4863 | -122.1451 | 1.1353 | 0.40904 | -0.0022312 | -0.024302 | 0.06323 | -0.040805 | 0.04649 | 0.11979 | -0.18768 | 1.2543 | -0.54016 | 1.0071 | -122.2641 | -22.7783 | 1.0895 | 1.1719 | 1.3229 | -122.5571 | 121.6049 | 0.11902 | 121.9574 | 123.1522 | -123.3994 | -0.41199 | 0.18768 | 0.35248 | 123.2346 | 123.317 | -0.11902 | 123.3994 | 121.9574 | 123.468 | 99.3668 | -0.41199 | 123.3994 | 121.9574 | 99.3668 | -0.11902 | 123.468 | -1.6754 | -123.6923
1113.9844 | 123.3856 | -122.113 | 1.2726 | -0.063984 | 0.010586 | 0.010946 | 0.095274 | -0.044009 | 0.075329 | 0.10804 | -0.20599 | 1.3916 | -0.5722 | 1.2405 | -122.0947 | -22.8516 | 1.0345 | 1.3824 | 1.3733 | -122.438 | 121.5408 | 0.11902 | 121.907 | 123.3536 | -123.3673 | -0.32501 | 0.10071 | 0.36621 | 123.1476 | 123.4955 | 0.01831 | 123.5046 | 121.907 | 123.4863 | 99.2615 | -0.32501 | 123.5046 | 121.907 | 99.2615 | 0.01831 | 123.4863 | -1.8448 | -123.7106
1114.9219 | 123.381 | -122.2229 | 1.1856 | 0.36326 | -0.0065042 | -0.0018714 | 0.092069 | -0.034396 | 0.04649 | 0.1027 | -0.050354 | 1.2863 | -0.57678 | 1.2085 | -122.1176 | -23.085 | 0.91553 | 1.3367 | 1.3046 | -122.5296 | 121.6461 | 0.10071 | 122.1725 | 123.4314 | -123.3032 | -0.3067 | 0.11902 | 0.52643 | 123.1384 | 123.5596 | 0.10528 | 123.5092 | 122.1725 | 123.5275 | 99.1379 | -0.3067 | 123.5092 | 122.1725 | 99.1379 | 0.10528 | 123.5275 | -1.7624 | -123.7152
1115.9844 | 123.3398 | -122.1863 | 1.181 | 0.40904 | 0.0020408 | -0.020029 | 0.085661 | -0.036532 | 0.08601 | 0.11338 | -0.25635 | 1.3092 | -0.57678 | 1.0666 | -122.3053 | -23.3688 | 1.0391 | 1.2451 | 1.3092 | -122.5113 | 121.6095 | 0.12817 | 121.9299 | 123.2529 | -123.4863 | -0.32501 | 0.12817 | 0.32043 | 123.2254 | 123.4314 | -0.11902 | 123.4955 | 121.9299 | 123.4955 | 98.8174 | -0.32501 | 123.4955 | 121.9299 | 98.8174 | -0.11902 | 123.4955 | -1.7578 | -123.6923
1116.9219 | 123.3398 | -122.2229 | 1.1444 | 0.28697 | 0.00097275 | 0.0024006 | 0.083524 | -0.036532 | 0.066784 | 0.11765 | -0.2655 | 1.2955 | -0.5722 | 1.1902 | -122.1359 | -22.5723 | 0.91095 | 1.3 | 1.2726 | -122.5525 | 121.6507 | 0.15106 | 121.9574 | 123.4131 | -123.2803 | -0.32959 | 0.12817 | 0.3067 | 123.1338 | 123.5229 | 0.086975 | 123.5184 | 121.9574 | 123.4955 | 99.6506 | -0.32959 | 123.5184 | 121.9574 | 99.6506 | 0.086975 | 123.4955 | -1.7166 | -123.6969
1117.9688 | 123.381 | -122.1817 | 1.2039 | -1.8645 | 0.00097275 | -0.0093484 | 0.070707 | -0.031191 | 0.045422 | 0.11231 | -0.33417 | 1.3687 | -0.53558 | 1.1673 | -122.1405 | -22.6364 | 0.95215 | 1.3412 | 1.3275 | -122.5113 | 121.6461 | 0.1648 | 121.8475 | 123.349 | -123.3444 | -0.32959 | 0.1236 | 0.20142 | 123.1338 | 123.5229 | 0.041199 | 123.5504 | 121.8475 | 123.5092 | 99.5453 | -0.32959 | 123.5504 | 121.8475 | 99.5453 | 0.041199 | 123.5092 | -1.7395 | -123.7152
1118.9219 | 123.3719 | -122.1588 | 1.2039 | 0.18016 | 0.0073818 | -0.011485 | 0.084592 | -0.034396 | 0.061443 | 0.11765 | -0.23346 | 1.3275 | -0.59052 | 1.2039 | -122.1268 | -23.4695 | 0.95673 | 1.3321 | 1.3275 | -122.5113 | 121.5683 | 0.1236 | 121.9254 | 123.3627 | -123.3307 | -0.35248 | 0.1236 | 0.35706 | 123.1155 | 123.4909 | 0.032043 | 123.4863 | 121.9254 | 123.4863 | 98.6893 | -0.35248 | 123.4863 | 121.9254 | 98.6893 | 0.032043 | 123.4863 | -1.7944 | -123.7152
1119.9844 | 123.381 | -122.3969 | 0.98877 | -0.47597 | -0.012912 | -0.012553 | 0.068571 | -0.036532 | 0.044354 | 0.11018 | -0.21973 | 1.1169 | -0.54474 | 0.9201 | -122.4289 | -23.5336 | 0.75073 | 1.1398 | 1.1169 | -122.7127 | 121.8521 | 0.12817 | 122.1771 | 123.317 | -123.4177 | -0.31586 | 0.12817 | 0.32501 | 123.1476 | 123.5367 | -0.032043 | 123.5138 | 122.1771 | 123.5138 | 98.8632 | -0.31586 | 123.5138 | 122.1771 | 98.8632 | -0.032043 | 123.5138 | -1.5335 | -123.7015
1120.9219 | 123.3902 | -122.4106 | 0.99335 | 0.4243 | -0.0043672 | -0.016825 | 0.082456 | -0.033328 | 0.058239 | 0.10377 | -0.36621 | 1.1169 | -0.68665 | 0.94299 | -122.3694 | -23.7396 | 0.76446 | 1.1307 | 1.0986 | -122.7356 | 121.7239 | 0.1236 | 122.0444 | 123.3536 | -123.3627 | -0.32501 | 0.10529 | 0.32043 | 123.175 | 123.5413 | 0.041198 | 123.5275 | 122.0444 | 123.5092 | 98.671 | -0.32501 | 123.5275 | 122.0444 | 98.671 | 0.041198 | 123.5092 | -1.68 | -123.7289
1121.9844 | 123.0698 | -89.328 | 33.9569 | -0.094502 | -0.0011632 | -0.0018714 | 0.06323 | -0.03226 | 0.043285 | 0.12513 | 2.3209 | 7.8323 | -0.53101 | 20.0684 | -112.1201 | -12.6022 | 29.9561 | 50.7385 | 25.4608 | -97.6227 | 88.797 | -26.1246 | 91.6489 | 109.3964 | -146.077 | -8.2947 | -8.4961 | 2.8519 | 119.2841 | 140.0665 | -22.7921 | 97.1603 | 91.6489 | 114.7888 | 76.7258 | -8.2947 | 97.1603 | 91.6489 | 76.7258 | -22.7921 | 114.7888 | -34.4879 | -131.5796
1122.9219 | 123.3673 | -116.9632 | 6.2164 | 0.19541 | -0.0022312 | 0.0013326 | 0.09741 | -0.0376 | 0.06358 | 0.10484 | -1.1032 | 10.3134 | -0.43945 | 6.7932 | -116.3727 | -22.5632 | 6.3263 | 6.5964 | 6.7612 | -117.1005 | 116.5237 | 4.097 | 115.86 | 123.7564 | -122.5891 | -0.13733 | 0.54474 | -0.66376 | 123.2895 | 123.5596 | 0.59051 | 127.2766 | 115.86 | 123.7244 | 94.4 | -0.13733 | 127.2766 | 115.86 | 94.4 | 0.59051 | 123.7244 | -6.6559 | -123.317
1123.9844 | 123.5458 | -118.4372 | 4.7928 | -0.30813 | -0.018253 | -0.018961 | 0.053617 | -0.031191 | 0.04649 | 0.12833 | -0.082397 | 4.8752 | -0.44861 | 4.6326 | -118.5104 | -22.879 | 4.6829 | 4.8569 | 4.9896 | -118.8858 | 117.9886 | 0.082397 | 118.3548 | 123.0698 | -123.3032 | -0.44861 | 0.19684 | 0.36621 | 123.1201 | 123.2941 | -0.073242 | 123.3124 | 118.3548 | 123.4268 | 95.5582 | -0.44861 | 123.3124 | 118.3548 | 95.5582 | -0.073242 | 123.4268 | -5.2414 | -123.6786
1124.9219 | 123.3765 | -119.0094 | 4.3304 | -0.079243 | 0.0095178 | 0.0013326 | 0.089933 | -0.040805 | 0.064648 | 0.11658 | -0.09613 | 4.4907 | -0.4715 | 4.2938 | -119.0735 | -23.14 | 4.1382 | 4.6371 | 4.4312 | -119.3573 | 118.5379 | 0.16022 | 118.9133 | 123.3032 | -123.4039 | -0.3479 | 0.10071 | 0.37537 | 123.1476 | 123.6465 | -0.064087 | 123.5001 | 118.9133 | 123.4406 | 95.8694 | -0.3479 | 123.5001 | 118.9133 | 95.8694 | -0.064087 | 123.4406 | -4.8019 | -123.6877
1125.9844 | 123.4314 | -117.7963 | 5.4932 | -2.0019 | -0.01398 | -0.011485 | 0.06323 | -0.039736 | 0.024059 | 0.12086 | -0.050354 | 5.6717 | -0.48981 | 5.3558 | -117.9474 | -22.8241 | 5.4565 | 5.5527 | 5.6396 | -118.1854 | 117.3065 | 0.17853 | 117.746 | 123.1522 | -123.4406 | -0.3891 | 0.14648 | 0.43945 | 123.2529 | 123.349 | -0.15106 | 123.468 | 117.746 | 123.436 | 94.9722 | -0.3891 | 123.468 | 117.746 | 94.9722 | -0.15106 | 123.436 | -5.983 | -123.6786
1126.9219 | 123.5229 | -117.2928 | 5.9601 | 0.30223 | -0.017185 | -0.021098 | 0.060026 | -0.048281 | 0.033672 | 0.12086 | -0.72327 | 6.6193 | -0.44861 | 6.3171 | -117.0868 | -22.5449 | 5.8868 | 6.0196 | 6.5735 | -117.5583 | 116.8442 | 0.65918 | 116.5695 | 123.6099 | -123.0469 | -0.2655 | 0.6134 | -0.27466 | 123.1796 | 123.3124 | 0.20599 | 123.912 | 116.5695 | 123.8663 | 94.7479 | -0.2655 | 123.912 | 116.5695 | 94.7479 | 0.20599 | 123.8663 | -6.4087 | -123.5184
1127.9844 | 123.3994 | -120.1309 | 3.3142 | -0.41494 | -0.015048 | -0.034983 | 0.077116 | -0.046145 | 0.048626 | 0.1262 | -0.082397 | 3.4607 | -0.49896 | 3.4744 | -119.9203 | -24.7925 | 3.1677 | 3.4744 | 3.5751 | -120.3278 | 119.632 | 0.14648 | 120.0485 | 123.6053 | -123.2346 | -0.19684 | 0.26092 | 0.41657 | 123.2986 | 123.6053 | 0.21057 | 123.5916 | 120.0485 | 123.7061 | 95.3384 | -0.19684 | 123.5916 | 120.0485 | 95.3384 | 0.21057 | 123.7061 | -3.8132 | -123.642
1128.9219 | 123.3948 | -117.3935 | 5.8685 | -0.094502 | -0.0022312 | -0.014689 | 0.085661 | -0.041873 | 0.057171 | 0.10911 | -0.13733 | 6.0379 | -0.48065 | 5.8411 | -117.5171 | -22.1283 | 5.7129 | 5.9647 | 5.983 | -117.8513 | 116.9128 | 0.16937 | 117.2562 | 123.2346 | -123.3856 | -0.45776 | 0.11444 | 0.34332 | 123.1064 | 123.3582 | -0.1236 | 123.4314 | 117.2562 | 123.3765 | 95.2652 | -0.45776 | 123.4314 | 117.2562 | 95.2652 | -0.1236 | 123.3765 | -6.3492 | -123.7198
1129.9844 | 123.3353 | -119.7327 | 3.566 | -0.38442 | -0.0086402 | -0.015757 | 0.062162 | -0.047213 | 0.034741 | 0.12299 | -0.10529 | 3.6942 | -0.46234 | 3.4424 | -119.8517 | -22.4899 | 3.5248 | 3.4332 | 3.7537 | -120.1767 | 119.2703 | 0.12817 | 119.6274 | 123.175 | -123.4177 | -0.44403 | 0.18768 | 0.35706 | 123.2574 | 123.1659 | -0.11902 | 123.4268 | 119.6274 | 123.4863 | 97.2427 | -0.44403 | 123.4268 | 119.6274 | 97.2427 | -0.11902 | 123.4863 | -4.0283 | -123.7427
1130.9219 | 123.4039 | -119.7235 | 3.6987 | 2.0722 | -0.0054352 | -0.00080337 | 0.091001 | -0.049349 | 0.071056 | 0.12086 | 1.3321 | 4.1199 | -0.43945 | 3.6896 | -119.6548 | -22.7737 | 3.4195 | 3.8269 | 4.4037 | -119.8929 | 119.2841 | 0.42114 | 121.0556 | 123.4131 | -123.3536 | -0.16937 | 0.70496 | 1.7715 | 123.143 | 123.5504 | 0.068665 | 123.8434 | 121.0556 | 124.1272 | 96.9498 | -0.16937 | 123.8434 | 121.0556 | 96.9498 | 0.068665 | 124.1272 | -4.1382 | -123.5916
1131.9844 | 123.3902 | -116.7435 | 6.5369 | 0.14964 | -0.0011632 | -0.0093484 | 0.083524 | -0.041873 | 0.057171 | 0.11658 | -0.19684 | 7.3792 | -0.49439 | 6.7291 | -116.6748 | -20.668 | 6.395 | 6.8527 | 6.8024 | -117.009 | 116.2491 | 0.84229 | 116.5466 | 123.4726 | -123.2117 | -0.2655 | 0.2655 | 0.29755 | 123.1384 | 123.5962 | 0.068664 | 124.1226 | 116.5466 | 123.5458 | 96.0754 | -0.2655 | 124.1226 | 116.5466 | 96.0754 | 0.068664 | 123.5458 | -7.0312 | -123.5458
1132.9219 | 123.4085 | -118.3228 | 5.0034 | -0.27761 | -0.0075722 | -0.015757 | 0.08032 | -0.03226 | 0.053967 | 0.12086 | -0.15564 | 5.1224 | -0.52185 | 4.9988 | -118.3365 | -21.3272 | 4.7974 | 5.0995 | 5.127 | -118.689 | 117.8009 | 0.11902 | 118.1671 | 123.3215 | -123.3398 | -0.36621 | 0.1236 | 0.36621 | 123.1201 | 123.4222 | -0.013733 | 123.4451 | 118.1671 | 123.4497 | 96.9955 | -0.36621 | 123.4451 | 118.1671 | 96.9955 | -0.013733 | 123.4497 | -5.5252 | -123.6923
1133.9844 | 123.5138 | -118.364 | 4.9393 | -0.12502 | -0.022525 | -0.014689 | 0.055753 | -0.051486 | 0.034741 | 0.12086 | -0.073242 | 5.0491 | -0.44861 | 4.747 | -118.483 | -22.0963 | 4.9255 | 4.9255 | 5.1315 | -118.7393 | 117.9153 | 0.10986 | 118.2907 | 123.111 | -123.4222 | -0.37537 | 0.19226 | 0.37537 | 123.2895 | 123.2895 | -0.11902 | 123.4131 | 118.2907 | 123.4955 | 96.2677 | -0.37537 | 123.4131 | 118.2907 | 96.2677 | -0.11902 | 123.4955 | -5.3879 | -123.6786
1134.9219 | 123.4222 | -118.4097 | 4.8889 | -0.27761 | -0.0065042 | -0.0029404 | 0.077116 | -0.03226 | 0.061443 | 0.11872 | -0.086975 | 5.4108 | -0.53558 | 4.9438 | -118.4372 | -22.4899 | 4.7607 | 5.04 | 5.072 | -118.7439 | 117.8741 | 0.52185 | 118.3228 | 123.3536 | -123.3261 | -0.33417 | 0.18311 | 0.44861 | 123.1705 | 123.4497 | -0.027466 | 123.8205 | 118.3228 | 123.4818 | 95.9198 | -0.33417 | 123.8205 | 118.3228 | 95.9198 | -0.027466 | 123.4818 | -5.4245 | -123.6328
1135.9219 | 123.3353 | -118.7622 | 4.5959 | -0.38442 | -0.0032992 | -0.020029 | 0.078184 | -0.036532 | 0.036877 | 0.11231 | -0.21515 | 4.66 | -0.51727 | 4.6097 | -118.6478 | -22.3618 | 4.422 | 4.6555 | 4.7424 | -119.1101 | 118.2449 | 0.064087 | 118.5471 | 123.3719 | -123.2437 | -0.3479 | 0.14649 | 0.30212 | 123.1842 | 123.4177 | 0.11444 | 123.4222 | 118.5471 | 123.5046 | 96.4005 | -0.3479 | 123.4222 | 118.5471 | 96.4005 | 0.11444 | 123.5046 | -5.1132 | -123.7061
1137 | 123.4451 | -118.1854 | 5.0995 | 0.33274 | -0.016117 | -0.052073 | 0.054685 | -0.041873 | 0.042217 | 0.11124 | -0.16022 | 5.1315 | -0.45319 | 4.9667 | -118.2678 | -21.8536 | 5.0949 | 5.1453 | 5.2689 | -118.5516 | 117.7322 | 0.032044 | 118.0252 | 123.1522 | -123.3673 | -0.36621 | 0.16937 | 0.29297 | 123.2803 | 123.3307 | -0.082397 | 123.317 | 118.0252 | 123.4543 | 96.3318 | -0.36621 | 123.317 | 118.0252 | 96.3318 | -0.082397 | 123.4543 | -5.5527 | -123.6511
1137.9219 | 123.4543 | -119.7556 | 3.5385 | -0.1708 | -0.026798 | 0.0024006 | 0.06323 | -0.042941 | 0.049694 | 0.1059 | -0.10986 | 3.6301 | -0.45776 | 3.4103 | -119.8883 | -23.0896 | 3.4424 | 3.653 | 3.6987 | -120.1538 | 119.2978 | 0.091553 | 119.6457 | 123.1659 | -123.4268 | -0.39825 | 0.16022 | 0.3479 | 123.1979 | 123.4085 | -0.13275 | 123.3856 | 119.6457 | 123.4543 | 96.666 | -0.39825 | 123.3856 | 119.6457 | 96.666 | -0.13275 | 123.4543 | -3.9963 | -123.6923
1138.9844 | 123.111 | -119.3939 | 3.5202 | -0.048725 | -0.015048 | -0.021098 | 0.055753 | -0.058962 | 0.040081 | 0.10484 | -0.18768 | 3.5889 | -0.50812 | 3.3371 | -119.5724 | -22.2748 | 3.4378 | 3.5156 | 3.685 | -119.783 | 118.8858 | 0.068664 | 119.2062 | 122.731 | -123.0927 | -0.3891 | 0.1648 | 0.32043 | 122.8317 | 122.9095 | -0.17853 | 122.9828 | 119.2062 | 123.0789 | 97.1191 | -0.3891 | 122.9828 | 119.2062 | 97.1191 | -0.17853 | 123.0789 | -4.0283 | -123.3032
1139.9219 | 123.1018 | -119.7464 | 3.3417 | -0.46071 | -0.018253 | -0.033915 | 0.068571 | -0.051486 | 0.040081 | 0.10484 | -0.17395 | 3.4515 | -0.48523 | 3.3188 | -119.7281 | -21.6522 | 3.0991 | 3.4561 | 3.4653 | -120.0302 | 119.2612 | 0.10986 | 119.5724 | 123.0652 | -123.0698 | -0.28381 | 0.1236 | 0.31128 | 122.8455 | 123.2025 | 0.018311 | 123.1979 | 119.5724 | 123.2117 | 98.0942 | -0.28381 | 123.1979 | 119.5724 | 98.0942 | 0.018311 | 123.2117 | -3.8269 | -123.3719
1140.9219 | 123.1705 | -116.7572 | 6.2439 | -0.44545 | -0.021457 | -0.028574 | 0.060026 | -0.038668 | 0.041149 | 0.1027 | -0.11902 | 6.2714 | -0.45319 | 6.1661 | -116.9312 | -20.7001 | 6.0928 | 6.3492 | 6.3629 | -117.1967 | 116.304 | 0.027466 | 116.6382 | 122.9233 | -123.175 | -0.43945 | 0.11902 | 0.33417 | 122.85 | 123.1064 | -0.17395 | 123.0286 | 116.6382 | 123.1201 | 96.0571 | -0.43945 | 123.0286 | 116.6382 | 96.0571 | -0.17395 | 123.1201 | -6.6971 | -123.4406
1141.9844 | 123.175 | -118.9728 | 4.097 | -0.52175 | -0.015048 | -0.010416 | 0.078184 | -0.049349 | 0.048626 | 0.11445 | -0.16937 | 4.2389 | -0.48981 | 4.1245 | -119.0002 | -22.7371 | 3.8773 | 4.2572 | 4.2435 | -119.3207 | 118.483 | 0.14191 | 118.8034 | 123.0972 | -123.0972 | -0.3479 | 0.14648 | 0.32043 | 122.85 | 123.23 | -0.027466 | 123.2117 | 118.8034 | 123.2162 | 96.2357 | -0.3479 | 123.2117 | 118.8034 | 96.2357 | -0.027466 | 123.2162 | -4.5868 | -123.4177
1142.9219 | 123.175 | -120.2774 | 2.8748 | -0.41494 | -0.0065042 | -0.0050764 | 0.084592 | -0.041873 | 0.049694 | 0.10056 | -0.20599 | 2.9709 | -0.49896 | 2.8748 | -120.2682 | -23.6755 | 2.623 | 3.0258 | 2.9938 | -120.5704 | 119.7784 | 0.09613 | 120.0714 | 123.1522 | -123.143 | -0.29297 | 0.11902 | 0.29297 | 122.9004 | 123.3032 | 0.009155 | 123.2483 | 120.0714 | 123.2712 | 96.6019 | -0.29297 | 123.2483 | 120.0714 | 96.6019 | 0.009155 | 123.2712 | -3.3737 | -123.4451
1143.9844 | 123.2483 | -120.5017 | 2.6688 | 0.48533 | -0.0011632 | -0.024302 | 0.084592 | -0.047213 | 0.056103 | 0.10911 | -0.23346 | 2.7832 | -0.55847 | 2.6413 | -120.5109 | -23.7625 | 2.504 | 2.742 | 2.8061 | -120.8359 | 119.9432 | 0.11444 | 120.2683 | 123.143 | -123.1796 | -0.33417 | 0.13733 | 0.32501 | 123.0057 | 123.2437 | -0.009155 | 123.2849 | 120.2683 | 123.3078 | 96.7392 | -0.33417 | 123.2849 | 120.2683 | 96.7392 | -0.009155 | 123.3078 | -3.2272 | -123.5046
1144.9219 | 122.937 | -121.1563 | 1.5793 | -0.018208 | 0.02554 | -0.017893 | 0.054685 | -0.050418 | 0.031536 | 0.1059 | -0.41199 | 0.20599 | -0.71411 | 1.4282 | -121.3257 | -23.4055 | 1.474 | 1.6388 | 1.767 | -121.5683 | 120.4422 | -1.3733 | 120.7443 | 122.5845 | -122.905 | -0.41199 | 0.18768 | 0.30212 | 122.6303 | 122.7951 | -0.16937 | 121.3623 | 120.7443 | 122.9233 | 97.7509 | -0.41199 | 121.3623 | 120.7443 | 97.7509 | -0.16937 | 122.9233 | -2.2934 | -123.1476
1145.9844 | 123.0377 | -121.3074 | 1.6296 | 0.39378 | 0.023404 | 0.012014 | 0.065366 | -0.052554 | 0.031536 | 0.10163 | -0.48065 | 0.21057 | -0.79651 | 1.5381 | -121.3486 | -20.5032 | 1.5289 | 1.7075 | 1.8356 | -121.6415 | 120.5109 | -1.4191 | 120.8267 | 122.8455 | -122.9782 | -0.33417 | 0.20599 | 0.31586 | 122.8363 | 123.0148 | -0.041199 | 121.5179 | 120.8267 | 123.143 | 100.8041 | -0.33417 | 121.5179 | 120.8267 | 100.8041 | -0.041199 | 123.143 | -2.4261 | -123.2712
1146.9219 | 123.1522 | -121.2067 | 1.7487 | -0.10976 | 0.023404 | -0.012553 | 0.05789 | -0.060031 | 0.042217 | 0.10911 | -0.4715 | 0.21057 | -0.82398 | 1.5747 | -121.3669 | -22.5311 | 1.6983 | 1.7349 | 1.9501 | -121.5866 | 120.3827 | -1.5381 | 120.7352 | 122.7814 | -123.1155 | -0.37994 | 0.20142 | 0.35248 | 122.905 | 122.9416 | -0.16022 | 121.4172 | 120.7352 | 123.1567 | 98.6755 | -0.37994 | 121.4172 | 120.7352 | 98.6755 | -0.16022 | 123.1567 | -2.5726 | -123.3353
1147.9844 | 123.1842 | -121.2662 | 1.7395 | -0.21657 | 0.026608 | -0.012553 | 0.054685 | -0.051486 | 0.031536 | 0.10056 | -0.20142 | 0.2243 | -0.54932 | 1.5884 | -121.4035 | -22.6318 | 1.6754 | 1.7578 | 1.9409 | -121.6095 | 120.7169 | -1.5152 | 121.0648 | 122.8546 | -123.143 | -0.34332 | 0.20142 | 0.3479 | 122.9416 | 123.024 | -0.13733 | 121.4905 | 121.0648 | 123.2071 | 98.6343 | -0.34332 | 121.4905 | 121.0648 | 98.6343 | -0.13733 | 123.2071 | -2.2888 | -123.349
1148.9219 | 123.1567 | -121.376 | 1.6479 | 0.088604 | 0.026608 | -0.014689 | 0.069639 | -0.060031 | 0.031536 | 0.10697 | -1.918 | 0.18768 | -2.2064 | 1.5015 | -121.4767 | -23.2635 | 1.5152 | 1.6617 | 1.8127 | -121.7377 | 119.1696 | -1.4603 | 119.458 | 122.8775 | -123.1247 | -0.36163 | 0.16479 | 0.28839 | 122.8912 | 123.0377 | -0.10071 | 121.5637 | 119.458 | 123.1888 | 98.1125 | -0.36163 | 121.5637 | 119.458 | 98.1125 | -0.10071 | 123.1888 | -3.8544 | -123.3856
1149.9844 | 123.1247 | -121.5134 | 1.5427 | 0.50059 | 0.04263 | -0.030711 | 0.083524 | -0.050418 | 0.057171 | 0.099494 | -2.2247 | 0.23804 | -2.5497 | 1.5381 | -121.5225 | -22.9111 | 1.3687 | 1.6251 | 1.6846 | -121.843 | 118.9636 | -1.3046 | 119.2886 | 123.0515 | -123.0652 | -0.32959 | 0.14191 | 0.32501 | 122.8821 | 123.1384 | -0.009155 | 121.7514 | 119.2886 | 123.1979 | 98.6023 | -0.32959 | 121.7514 | 119.2886 | 98.6023 | -0.009155 | 123.1979 | -4.0924 | -123.3856
1150.9219 | 123.1888 | -121.4676 | 1.5656 | 0.13438 | 0.028744 | -0.029642 | 0.06323 | -0.051486 | 0.026196 | 0.11124 | -2.2476 | 0.16937 | -2.5497 | 1.4511 | -121.5591 | -23.0576 | 1.4511 | 1.6251 | 1.7578 | -121.8246 | 118.9178 | -1.3962 | 119.22 | 122.9187 | -123.1247 | -0.35706 | 0.19226 | 0.30212 | 122.9187 | 123.0927 | -0.091553 | 121.637 | 119.22 | 123.2254 | 98.41 | -0.35706 | 121.637 | 119.22 | 98.41 | -0.091553 | 123.2254 | -4.1153 | -123.3902
1152 | 123.175 | -121.5363 | 1.5472 | -0.39968 | 0.03088 | -0.039256 | 0.081388 | -0.05469 | 0.042217 | 0.1027 | -2.1927 | 0.21973 | -2.5131 | 1.4557 | -121.6049 | -23.4192 | 1.3733 | 1.6022 | 1.6891 | -121.8979 | 119.0231 | -1.3275 | 119.3436 | 122.9919 | -123.1522 | -0.36163 | 0.14191 | 0.32044 | 122.9095 | 123.1384 | -0.068664 | 121.756 | 119.3436 | 123.2254 | 98.1171 | -0.36163 | 121.756 | 119.3436 | 98.1171 | -0.068664 | 123.2254 | -4.0604 | -123.4451
1152.9219 | 123.1796 | -121.5637 | 1.4832 | 0.19541 | 0.028744 | -0.027506 | 0.072843 | -0.057894 | 0.020855 | 0.10056 | -2.2705 | 0.20599 | -2.5635 | 1.3779 | -121.6415 | -23.9365 | 1.3321 | 1.5427 | 1.6388 | -121.9345 | 119.0002 | -1.2772 | 119.2932 | 122.9416 | -123.1247 | -0.37079 | 0.15564 | 0.29297 | 122.8958 | 123.1064 | -0.07782 | 121.7697 | 119.2932 | 123.2025 | 97.6273 | -0.37079 | 121.7697 | 119.2932 | 97.6273 | -0.07782 | 123.2025 | -4.0466 | -123.4177
1154.3438 | 123.2346 | -121.4813 | 1.5564 | -0.063984 | 0.028744 | -0.0082804 | 0.065366 | -0.053622 | 0.039013 | 0.11338 | -2.2705 | 0.2243 | -2.6047 | 1.4099 | -121.6415 | -24.8383 | 1.474 | 1.5564 | 1.7258 | -121.8796 | 118.8766 | -1.3321 | 119.2108 | 122.8912 | -123.1979 | -0.39825 | 0.16937 | 0.33417 | 122.9553 | 123.0377 | -0.16022 | 121.7056 | 119.2108 | 123.2071 | 96.6431 | -0.39825 | 121.7056 | 119.2108 | 96.6431 | -0.16022 | 123.2071 | -4.1611 | -123.436
1154.9219 | 123.2574 | -121.5408 | 1.5015 | -0.063984 | 0.02554 | -0.02537 | 0.064298 | -0.061099 | 0.030468 | 0.11338 | -2.2247 | 0.21515 | -2.5955 | 1.3596 | -121.701 | -24.7467 | 1.4511 | 1.5015 | 1.6846 | -121.9299 | 118.9453 | -1.2863 | 119.3161 | 122.9004 | -123.2025 | -0.3891 | 0.1831 | 0.37079 | 122.9919 | 123.0423 | -0.16022 | 121.756 | 119.3161 | 123.2254 | 96.7941 | -0.3891 | 121.756 | 119.3161 | 96.7941 | -0.16022 | 123.2254 | -4.097 | -123.4314
1155.9219 | 123.2346 | -121.5134 | 1.4786 | 0.54637 | 0.026608 | -0.010416 | 0.08032 | -0.046145 | 0.058239 | 0.10804 | -2.2842 | 0.21057 | -2.6321 | 1.1948 | -121.788 | -24.5499 | 1.4969 | 1.4557 | 1.6525 | -121.962 | 118.8812 | -1.268 | 119.2291 | 122.7081 | -123.2666 | -0.44861 | 0.17395 | 0.3479 | 123.0103 | 122.9691 | -0.27466 | 121.7239 | 119.2291 | 123.1659 | 96.9635 | -0.44861 | 121.7239 | 119.2291 | 96.9635 | -0.27466 | 123.1659 | -4.1107 | -123.4406
1156.9219 | 123.2162 | -121.582 | 1.4648 | 0.80577 | 0.03088 | -0.0072124 | 0.073911 | -0.063235 | 0.048626 | 0.10911 | -2.2797 | 0.19684 | -2.6459 | 1.355 | -121.6965 | -25.0534 | 1.4191 | 1.4969 | 1.6571 | -121.9574 | 118.9362 | -1.268 | 119.3024 | 122.937 | -123.1613 | -0.37537 | 0.19226 | 0.36621 | 123.0011 | 123.0789 | -0.11444 | 121.7789 | 119.3024 | 123.2391 | 96.5286 | -0.37537 | 121.7789 | 119.3024 | 96.5286 | -0.11444 | 123.2391 | -4.1107 | -123.4222
1158 | 123.1522 | -121.6415 | 1.4786 | -0.39968 | 0.037289 | -0.017893 | 0.074979 | -0.047213 | 0.032604 | 0.11445 | -1.8127 | 0.2243 | -2.1378 | 1.387 | -121.6782 | -24.9985 | 1.2634 | 1.5518 | 1.5976 | -121.9803 | 119.5038 | -1.2543 | 119.8288 | 123.0286 | -123.1567 | -0.33875 | 0.11902 | 0.32501 | 122.905 | 123.1934 | -0.036621 | 121.8658 | 119.8288 | 123.2391 | 96.6431 | -0.33875 | 121.8658 | 119.8288 | 96.6431 | -0.036621 | 123.2391 | -3.6163 | -123.4589
1158.9219 | 123.1979 | -121.6507 | 1.4374 | 0.19541 | 0.023404 | -0.014689 | 0.056821 | -0.051486 | 0.042217 | 0.10377 | -1.6067 | 0.20599 | -1.8723 | 1.3229 | -121.701 | -24.7787 | 1.3 | 1.5015 | 1.5976 | -121.9894 | 119.7784 | -1.2314 | 120.0439 | 122.9736 | -123.1384 | -0.33875 | 0.16022 | 0.2655 | 122.9507 | 123.1522 | -0.050354 | 121.8567 | 120.0439 | 123.2483 | 96.8719 | -0.33875 | 121.8567 | 120.0439 | 96.8719 | -0.050354 | 123.2483 | -3.3096 | -123.4268
1159.9844 | 123.1522 | -121.8567 | 1.2955 | -1.5136 | 0.049038 | -0.010416 | 0.1113 | -0.044009 | 0.059307 | 0.10056 | -1.7578 | 0.26093 | -1.973 | 1.3 | -121.8063 | -24.4766 | 1.0712 | 1.4145 | 1.4145 | -122.1497 | 119.8837 | -1.0345 | 120.0989 | 123.1567 | -123.1018 | -0.29297 | 0.11902 | 0.21515 | 122.9279 | 123.2712 | 0.050354 | 122.1176 | 120.0989 | 123.2712 | 97.3801 | -0.29297 | 122.1176 | 120.0989 | 97.3801 | 0.050354 | 123.2712 | -3.2684 | -123.4451
1160.9219 | 123.23 | -121.8018 | 1.2634 | 0.36326 | 0.040494 | -0.0082804 | 0.069639 | -0.041873 | 0.034741 | 0.10697 | -1.0162 | 0.21973 | -1.3412 | 1.1581 | -121.875 | -24.7467 | 1.1856 | 1.3229 | 1.4465 | -122.2 | 120.4605 | -1.0437 | 120.7855 | 122.9599 | -123.1384 | -0.39825 | 0.18311 | 0.32501 | 122.9874 | 123.1247 | -0.073242 | 122.0215 | 120.7855 | 123.2483 | 97.0551 | -0.39825 | 122.0215 | 120.7855 | 97.0551 | -0.073242 | 123.2483 | -2.6047 | -123.4634
1161.9844 | 123.1934 | -121.8338 | 1.3229 | -0.32338 | 0.052243 | -0.0029404 | 0.084592 | -0.042941 | 0.062512 | 0.11979 | -1.1261 | 0.26093 | -1.4191 | 1.3229 | -121.8063 | -24.3256 | 1.0986 | 1.4282 | 1.4511 | -122.1588 | 120.4147 | -1.062 | 120.7077 | 123.1567 | -123.1293 | -0.32501 | 0.12817 | 0.29297 | 122.9324 | 123.262 | 0.027466 | 122.0947 | 120.7077 | 123.2849 | 97.5082 | -0.32501 | 122.0947 | 120.7077 | 97.5082 | 0.027466 | 123.2849 | -2.742 | -123.4817
1162.9219 | 123.2666 | -121.8704 | 1.2268 | 0.31749 | 0.04797 | 0.020559 | 0.077116 | -0.050418 | 0.055035 | 0.1059 | -0.71411 | 0.21057 | -1.0941 | 1.1581 | -121.9437 | -24.9802 | 1.181 | 1.2955 | 1.4328 | -122.2275 | 120.7764 | -1.0162 | 121.1563 | 123.0286 | -123.1705 | -0.35706 | 0.20599 | 0.37994 | 123.0515 | 123.1659 | -0.073243 | 122.081 | 121.1563 | 123.3032 | 96.8903 | -0.35706 | 122.081 | 121.1563 | 96.8903 | -0.073243 | 123.3032 | -2.3209 | -123.4543
1163.9844 | 123.1613 | -121.7102 | 1.4603 | 0.1649 | 0.034085 | -0.013621 | 0.088865 | -0.040805 | 0.062512 | 0.10697 | -0.59509 | 0.2655 | -0.94299 | 1.4786 | -121.637 | -24.7833 | 1.1948 | 1.6113 | 1.5701 | -122.0444 | 120.7672 | -1.1948 | 121.1151 | 123.1888 | -123.0972 | -0.33417 | 0.10986 | 0.3479 | 122.905 | 123.3215 | 0.073242 | 121.9757 | 121.1151 | 123.2803 | 96.9269 | -0.33417 | 121.9757 | 121.1151 | 96.9269 | 0.073242 | 123.2803 | -2.4033 | -123.5046
1164.9219 | 123.1201 | -121.8338 | 1.3504 | 0.31749 | 0.050107 | 0.0077416 | 0.083524 | -0.033328 | 0.056103 | 0.11979 | -0.63629 | 0.26093 | -0.93842 | 1.3275 | -121.6644 | -24.6506 | 1.1032 | 1.3138 | 1.4374 | -122.1405 | 120.8954 | -1.0895 | 121.1975 | 123.1613 | -123.0148 | -0.3067 | 0.086975 | 0.30212 | 122.937 | 123.1476 | 0.16937 | 122.0947 | 121.1975 | 123.2712 | 97.1832 | -0.3067 | 122.0947 | 121.1975 | 97.1832 | 0.16937 | 123.2712 | -2.2888 | -123.4909
1165.9688 | 123.1934 | -121.6553 | 1.5244 | -0.33864 | 0.044766 | -0.036051 | 0.071775 | -0.045077 | 0.050762 | 0.12406 | -0.98877 | 0.24261 | -1.2817 | 1.4969 | -121.637 | -24.6918 | 1.2726 | 1.6388 | 1.6434 | -121.9528 | 120.3735 | -1.2817 | 120.6665 | 123.1522 | -123.1613 | -0.29755 | 0.11902 | 0.29297 | 122.9279 | 123.2941 | 0.01831 | 121.8979 | 120.6665 | 123.2986 | 96.9635 | -0.29755 | 121.8979 | 120.6665 | 96.9635 | 0.01831 | 123.2986 | -2.8061 | -123.4772
1166.9219 | 123.2208 | -121.6461 | 1.4557 | 0.51585 | 0.036221 | -0.0082804 | 0.072843 | -0.048281 | 0.06358 | 0.10697 | -1.1902 | 0.23346 | -1.5106 | 1.4328 | -121.6644 | -25.177 | 1.3092 | 1.5701 | 1.6205 | -121.9986 | 120.1355 | -1.2222 | 120.4559 | 123.0789 | -123.1201 | -0.35248 | 0.16479 | 0.32043 | 122.9553 | 123.2162 | -0.018311 | 121.8796 | 120.4559 | 123.2666 | 96.4691 | -0.35248 | 121.8796 | 120.4559 | 96.4691 | -0.018311 | 123.2666 | -2.9663 | -123.4543
1167.9219 | 123.1888 | -121.7239 | 1.4328 | 0.027569 | 0.054379 | -0.017893 | 0.086729 | -0.046145 | 0.056103 | 0.11445 | -1.3184 | 0.26093 | -1.6067 | 1.4328 | -121.6736 | -24.9161 | 1.2405 | 1.5793 | 1.5472 | -122.0581 | 120.1172 | -1.1719 | 120.4056 | 123.1567 | -123.1064 | -0.33417 | 0.11444 | 0.28839 | 122.9645 | 123.3032 | 0.050354 | 121.9849 | 120.4056 | 123.2712 | 96.8079 | -0.33417 | 121.9849 | 120.4056 | 96.8079 | 0.050354 | 123.2712 | -3.0396 | -123.4909
1168.9844 | 123.2071 | -121.7514 | 1.442 | -0.33864 | 0.04797 | -0.0040084 | 0.08032 | -0.047213 | 0.057171 | 0.10804 | -1.5152 | 0.23804 | -1.8539 | 1.3962 | -121.7194 | -25.6348 | 1.1993 | 1.5518 | 1.5656 | -122.0673 | 119.8975 | -1.2039 | 120.2362 | 123.1476 | -123.1613 | -0.31586 | 0.1236 | 0.33874 | 122.9507 | 123.3032 | 0.032044 | 121.9894 | 120.2362 | 123.317 | 96.1166 | -0.31586 | 121.9894 | 120.2362 | 96.1166 | 0.032044 | 123.317 | -3.2959 | -123.5092
1169.9219 | 123.1567 | -121.7422 | 1.4374 | 0.25645 | 0.045834 | -0.020029 | 0.078184 | -0.035464 | 0.053967 | 0.10377 | -1.5106 | 0.2655 | -1.8219 | 1.4511 | -121.6507 | -25.2365 | 1.1948 | 1.593 | 1.561 | -122.0673 | 119.9203 | -1.1719 | 120.2316 | 123.1934 | -123.0881 | -0.32501 | 0.1236 | 0.31128 | 122.937 | 123.3353 | 0.091553 | 122.0078 | 120.2316 | 123.3032 | 96.5057 | -0.32501 | 122.0078 | 120.2316 | 96.5057 | 0.091553 | 123.3032 | -3.2593 | -123.5046
1170.9844 | 123.175 | -121.7743 | 1.4465 | -0.3539 | 0.040494 | -0.016825 | 0.073911 | -0.034396 | 0.061443 | 0.11979 | -1.2085 | 0.26093 | -1.5198 | 1.3092 | -121.669 | -24.9481 | 1.1307 | 1.5564 | 1.5793 | -122.0627 | 120.2545 | -1.1856 | 120.5658 | 123.0835 | -123.1155 | -0.28839 | 0.13275 | 0.31128 | 122.905 | 123.3307 | 0.10529 | 122.0352 | 120.5658 | 123.3536 | 96.8262 | -0.28839 | 122.0352 | 120.5658 | 96.8262 | 0.10529 | 123.3536 | -2.9663 | -123.5092
1171.9219 | 123.1796 | -121.8155 | 1.355 | -0.048725 | 0.043698 | 0.0056046 | 0.084592 | -0.045077 | 0.059307 | 0.10911 | -1.1215 | 0.27466 | -1.4557 | 1.3596 | -121.7789 | -25.2731 | 1.1536 | 1.4923 | 1.4786 | -122.1313 | 120.3598 | -1.0803 | 120.694 | 123.175 | -123.1338 | -0.31586 | 0.1236 | 0.33417 | 122.9691 | 123.3078 | 0.036621 | 122.0901 | 120.694 | 123.2941 | 96.5424 | -0.31586 | 122.0901 | 120.694 | 96.5424 | 0.036621 | 123.2941 | -2.8107 | -123.4863
1172.9844 | 123.1842 | -121.8796 | 1.3092 | 0.40904 | 0.044766 | -0.0061444 | 0.085661 | -0.038668 | 0.058239 | 0.10377 | -0.7782 | 0.25635 | -1.0895 | 1.3092 | -121.7972 | -24.9619 | 1.0849 | 1.474 | 1.4282 | -122.1909 | 120.7901 | -1.0529 | 121.1014 | 123.1888 | -123.1064 | -0.31128 | 0.11902 | 0.31128 | 122.9645 | 123.3536 | 0.082398 | 122.1359 | 121.1014 | 123.3078 | 96.9177 | -0.31128 | 122.1359 | 121.1014 | 96.9177 | 0.082398 | 123.3078 | -2.3987 | -123.5001
1173.9219 | 123.1888 | -121.8979 | 1.2726 | 0.042827 | 0.050107 | -0.0082804 | 0.084592 | -0.03226 | 0.064648 | 0.11552 | -0.97504 | 0.27008 | -1.3275 | 1.2543 | -121.8613 | -23.9136 | 1.0757 | 1.4053 | 1.3962 | -122.2229 | 120.5704 | -1.0025 | 120.9229 | 123.1522 | -123.1338 | -0.32501 | 0.1236 | 0.35248 | 122.9736 | 123.3032 | 0.036621 | 122.168 | 120.9229 | 123.2941 | 97.9843 | -0.32501 | 122.168 | 120.9229 | 97.9843 | 0.036621 | 123.2941 | -2.6001 | -123.4955
1174.9219 | 123.1888 | -121.9208 | 1.268 | 0.19541 | 0.055447 | -0.0018714 | 0.083524 | -0.040805 | 0.056103 | 0.11124 | -0.72784 | 0.25635 | -1.0666 | 1.2772 | -121.8338 | -23.3322 | 1.0345 | 1.4191 | 1.3962 | -122.2366 | 120.8542 | -1.0117 | 121.1929 | 123.1979 | -123.1018 | -0.31586 | 0.12817 | 0.33874 | 122.9553 | 123.3398 | 0.086975 | 122.1771 | 121.1929 | 123.317 | 98.5886 | -0.31586 | 122.1771 | 121.1929 | 98.5886 | 0.086975 | 123.317 | -2.3346 | -123.5046
1175.9844 | 123.2025 | -121.9299 | 1.2405 | -0.063984 | 0.041562 | -0.0040084 | 0.08032 | -0.034396 | 0.058239 | 0.1059 | -0.89264 | 0.26093 | -1.2451 | 1.1948 | -121.907 | -24.0921 | 1.0437 | 1.3504 | 1.3824 | -122.2916 | 120.6848 | -0.97961 | 121.0373 | 123.1247 | -123.1476 | -0.36163 | 0.14191 | 0.35248 | 122.9736 | 123.2803 | 0.022889 | 122.1909 | 121.0373 | 123.3124 | 97.8378 | -0.36163 | 122.1909 | 121.0373 | 97.8378 | 0.022889 | 123.3124 | -2.4857 | -123.5321
1176.9219 | 123.1659 | -122.0581 | 1.1261 | 0.1649 | 0.041562 | 0.0013326 | 0.089933 | -0.031191 | 0.053967 | 0.1059 | -1.0895 | 0.27008 | -1.3916 | 1.1307 | -121.9162 | -24.0143 | 0.89722 | 1.3138 | 1.2726 | -122.3969 | 120.6665 | -0.85602 | 120.9686 | 123.1888 | -123.0423 | -0.33875 | 0.14648 | 0.30212 | 122.9553 | 123.3719 | 0.14191 | 122.3282 | 120.9686 | 123.3307 | 98.0438 | -0.33875 | 122.3282 | 120.9686 | 98.0438 | 0.14191 | 123.3307 | -2.5177 | -123.5229
1177.9844 | 123.2208 | -122.113 | 1.0529 | -0.30813 | 0.051175 | -0.023234 | 0.070707 | -0.033328 | -0.022938 | 0.040748 | -0.38452 | 0.23804 | -0.37994 | 0.98419 | 0.66834 | -4.7424 | 0.83313 | 1.1536 | 1.1902 | -122.5479 | 121.7331 | -0.81482 | 121.7285 | 123.0972 | -0.38452 | -0.43488 | 0.13733 | -0.004577 | 122.9462 | 123.2666 | 122.7814 | 122.3511 | 121.7285 | 123.3032 | 117.3706 | -0.43488 | 122.3511 | 121.7285 | 117.3706 | 122.7814 | 123.3032 | -1.4328 | -123.6008
1178.9219 | 123.2346 | -122.1268 | 1.0437 | -0.24709 | 0.037289 | -0.010416 | 0.067503 | -0.036532 | -0.0079844 | 0.041816 | -0.81024 | 0.2655 | -1.1581 | 0.96588 | 0.68665 | -4.7058 | 0.83313 | 1.1627 | 1.1673 | -122.5021 | 120.9686 | -0.7782 | 121.3165 | 123.0927 | -0.35706 | -0.37537 | 0.1236 | 0.3479 | 122.9599 | 123.2895 | 122.8134 | 122.3923 | 121.3165 | 123.2941 | 117.421 | -0.37537 | 122.3923 | 121.3165 | 117.421 | 122.8134 | 123.2941 | -2.2018 | -123.5458
1179.9844 | 123.2437 | -122.1542 | 1.0391 | -0.079243 | 0.037289 | -0.0050764 | 0.085661 | -0.03226 | -0.014393 | 0.043952 | -0.6546 | 0.23804 | -0.35248 | 0.97961 | 0.66376 | -4.8203 | 0.83771 | 1.1353 | 1.1581 | -122.5525 | 121.8018 | -0.80109 | 121.4996 | 123.1338 | -0.37537 | -0.39825 | 0.11902 | -0.30212 | 122.9919 | 123.2895 | 122.818 | 122.3923 | 121.4996 | 123.3124 | 117.334 | -0.39825 | 122.3923 | 121.4996 | 117.334 | 122.818 | 123.3124 | -1.3916 | -123.5916
1180.9219 | 123.2666 | -122.0901 | 1.0666 | -0.15554 | 0.044766 | 0.0024006 | 0.08032 | -0.031191 | -0.01012 | 0.03968 | -0.53558 | 0.2655 | -0.92926 | 0.93842 | 0.60425 | -5.1636 | 0.81482 | 1.3046 | 1.1353 | -122.4609 | 121.1609 | -0.80109 | 121.5546 | 123.0286 | -0.46234 | -0.37079 | 0.068665 | 0.39368 | 122.905 | 123.3948 | 122.6944 | 122.3557 | 121.5546 | 123.2254 | 116.9266 | -0.37079 | 122.3557 | 121.5546 | 116.9266 | 122.6944 | 123.2254 | -1.9958 | -123.5275
1181.9219 | 123.2391 | -122.2046 | 0.99335 | -0.10976 | 0.045834 | -0.0050764 | 0.077116 | -0.033328 | -0.012257 | 0.03968 | -0.48981 | 0.24261 | -0.85602 | 0.95215 | 0.66834 | -5.2048 | 0.81024 | 1.1169 | 1.1398 | -122.5662 | 121.3486 | -0.75073 | 121.7148 | 123.1567 | -0.32501 | -0.36163 | 0.14648 | 0.36621 | 123.0148 | 123.3215 | 122.8729 | 122.4472 | 121.7148 | 123.3444 | 116.9998 | -0.36163 | 122.4472 | 121.7148 | 116.9998 | 122.8729 | 123.3444 | -1.8494 | -123.5596
1182.9844 | 123.2803 | -122.168 | 0.97961 | -0.29287 | 0.018063 | -0.033915 | 0.058958 | -0.041873 | -0.035755 | 0.041816 | -0.61798 | 0.21057 | -0.97046 | 0.82398 | 0.5722 | -5.1178 | 0.84686 | 1.062 | 1.1673 | -122.5571 | 121.1975 | -0.76904 | 121.55 | 122.9919 | -0.40741 | -0.3891 | 0.18768 | 0.35248 | 123.0148 | 123.23 | 122.7402 | 122.3785 | 121.55 | 123.3353 | 117.0502 | -0.3891 | 122.3785 | 121.55 | 117.0502 | 122.7402 | 123.3353 | -1.9501 | -123.5367
1183.9219 | 123.23 | -122.0947 | 0.98419 | -0.079243 | 0.04797 | -0.0082804 | 0.071775 | -0.038668 | -0.0015754 | 0.040748 | -0.60425 | 0.2655 | -3.0258 | 0.93842 | 0.62256 | -5.7037 | 0.80566 | 1.0941 | 1.1307 | -120.7077 | 119.0689 | -0.71869 | 121.4905 | 123.0331 | -0.36163 | 1.387 | 0.14648 | 2.4216 | 122.9004 | 123.1888 | 122.7173 | 122.3602 | 121.4905 | 123.2254 | 116.391 | 1.387 | 122.3602 | 121.4905 | 116.391 | 122.7173 | 123.2254 | -4.01 | -121.6919
1184.9844 | 123.317 | -122.0947 | 1.0208 | -0.14028 | 0.03088 | -0.0029404 | 0.047208 | -0.042941 | 0.025128 | 0.11231 | -0.84686 | 0.21973 | -1.1856 | 0.82398 | -120.6528 | -24.527 | 0.95215 | 1.03 | 1.2177 | -122.5204 | 120.9091 | -0.80109 | 121.2479 | 122.9187 | -121.6736 | -0.42572 | 0.19684 | 0.33874 | 123.0469 | 123.1247 | 1.442 | 122.3145 | 121.2479 | 123.3124 | 97.5677 | -0.42572 | 122.3145 | 121.2479 | 97.5677 | 1.442 | 123.3124 | -2.2064 | -123.5413
1185.9219 | 123.2208 | -122.168 | 1.0345 | -0.30813 | 0.033017 | -0.032847 | 0.079252 | -0.049349 | 0.056103 | 0.1059 | -2.0462 | 0.24719 | -2.3392 | 0.99335 | -121.1288 | -21.0205 | 0.75073 | 1.1856 | 1.1627 | -122.5433 | 119.8288 | -0.78735 | 120.1218 | 123.1613 | -122.1634 | -0.37537 | 0.12817 | 0.29297 | 122.9187 | 123.3536 | 1.0391 | 122.4152 | 120.1218 | 123.3307 | 101.1475 | -0.37537 | 122.4152 | 120.1218 | 101.1475 | 1.0391 | 123.3307 | -3.3737 | -123.5779
1186.9844 | 123.3032 | -122.168 | 0.98419 | -0.3539 | 0.023404 | -0.010416 | 0.067503 | -0.033328 | 0.018719 | 0.11765 | -0.7782 | 0.19684 | -1.1307 | 0.94299 | -121.6553 | -25.0534 | 0.97504 | 1.0208 | 1.1719 | -122.5662 | 121.0373 | -0.78735 | 121.3898 | 123.111 | -122.6395 | -0.39825 | 0.18768 | 0.35248 | 123.143 | 123.1888 | 0.5127 | 122.3648 | 121.3898 | 123.3398 | 97.1146 | -0.39825 | 122.3648 | 121.3898 | 97.1146 | 0.5127 | 123.3398 | -2.1149 | -123.5504
1187.9219 | 123.2254 | -122.1542 | 1.0712 | -0.4302 | 0.04263 | -0.024302 | 0.084592 | -0.046145 | 0.042217 | 0.11018 | -0.97046 | 0.27924 | -1.3046 | 1.0529 | -121.8109 | -24.8337 | 0.78735 | 1.1948 | 1.1719 | -122.5204 | 120.8496 | -0.79193 | 121.1838 | 123.2071 | -122.8821 | -0.36621 | 0.10071 | 0.33417 | 122.9416 | 123.349 | 0.34332 | 122.4335 | 121.1838 | 123.3261 | 97.3206 | -0.36621 | 122.4335 | 121.1838 | 97.3206 | 0.34332 | 123.3261 | -2.3758 | -123.5916
1188.9844 | 123.2895 | -122.0947 | 1.0391 | 0.11912 | 0.043698 | -0.022166 | 0.051481 | -0.067507 | 0.027264 | 0.11658 | -0.87891 | 0.21515 | -1.181 | 0.86517 | -122.0306 | -24.9115 | 0.9613 | 1.1124 | 1.1856 | -122.4884 | 120.9137 | -0.82397 | 121.2158 | 122.9599 | -123.0698 | -0.39368 | 0.14648 | 0.30212 | 123.056 | 123.2071 | 0.064087 | 122.3099 | 121.2158 | 123.2803 | 97.1832 | -0.39368 | 122.3099 | 121.2158 | 97.1832 | 0.064087 | 123.2803 | -2.2202 | -123.5275
1189.9219 | 123.2346 | -122.1588 | 1.0757 | -0.15554 | 0.045834 | -0.039256 | 0.095274 | -0.052554 | 0.043285 | 0.11124 | -1.0574 | 0.27008 | -1.4053 | 1.0345 | -121.8475 | -24.7742 | 0.80566 | 1.1993 | 1.1948 | -122.4792 | 120.7535 | -0.80566 | 121.1014 | 123.1934 | -122.9233 | -0.32044 | 0.11902 | 0.3479 | 122.9645 | 123.3582 | 0.31128 | 122.4289 | 121.1014 | 123.3536 | 97.3846 | -0.32044 | 122.4289 | 121.1014 | 97.3846 | 0.31128 | 123.3536 | -2.4811 | -123.555
1190.9844 | 123.23 | -122.1085 | 1.1124 | -0.4302 | 0.033017 | -0.016825 | 0.079252 | -0.051486 | 0.052898 | 0.10804 | -1.3458 | 0.23804 | -1.6617 | 0.99792 | -121.1746 | -24.6002 | 0.85602 | 1.2039 | 1.2451 | -122.4701 | 120.4468 | -0.87433 | 120.7626 | 123.1064 | -122.287 | -0.36163 | 0.13275 | 0.31586 | 122.9645 | 123.3124 | 0.93384 | 122.3465 | 120.7626 | 123.3536 | 97.5082 | -0.36163 | 122.3465 | 120.7626 | 97.5082 | 0.93384 | 123.3536 | -2.774 | -123.5825
1191.9219 | 123.2941 | -122.1268 | 1.0345 | -0.1708 | 0.014859 | -0.029642 | 0.065366 | -0.042941 | 0.043285 | 0.097358 | -1.7303 | 0.21057 | -2.1057 | 0.90179 | -121.8384 | -25.1678 | 0.92468 | 1.0757 | 1.2222 | -122.5113 | 120.0211 | -0.82397 | 120.3964 | 123.0286 | -122.8729 | -0.38452 | 0.18768 | 0.37537 | 123.0515 | 123.2025 | 0.28839 | 122.3373 | 120.3964 | 123.349 | 96.9589 | -0.38452 | 122.3373 | 120.3964 | 96.9589 | 0.28839 | 123.349 | -3.1403 | -123.5458
1192.9844 | 123.3307 | -122.113 | 1.0437 | -0.094502 | 0.015927 | -0.030711 | 0.058958 | -0.052554 | 0.035809 | 0.10484 | -1.6937 | 0.21057 | -2.0096 | 0.87433 | -121.9849 | -24.9115 | 0.95673 | 1.0666 | 1.2405 | -122.525 | 120.1035 | -0.83313 | 120.4193 | 122.9874 | -123.0286 | -0.41199 | 0.19684 | 0.31586 | 123.0698 | 123.1796 | 0.12817 | 122.3236 | 120.4193 | 123.3536 | 97.2015 | -0.41199 | 122.3236 | 120.4193 | 97.2015 | 0.12817 | 123.3536 | -3.0533 | -123.5687
1193.9219 | 123.3032 | -122.1405 | 1.0208 | -0.39968 | 0.022336 | -0.015757 | 0.060026 | -0.05469 | 0.042217 | 0.10377 | -1.9455 | 0.20142 | -2.2659 | 0.91553 | -121.9849 | -25.0214 | 0.90179 | 1.0941 | 1.1993 | -122.5296 | 119.8746 | -0.8194 | 120.195 | 123.056 | -123.0057 | -0.3891 | 0.17853 | 0.32043 | 123.0423 | 123.2346 | 0.15564 | 122.3419 | 120.195 | 123.3398 | 97.1191 | -0.3891 | 122.3419 | 120.195 | 97.1191 | 0.15564 | 123.3398 | -3.2867 | -123.5504
1194.9844 | 123.3353 | -122.1268 | 1.03 | -0.4302 | 0.020199 | 0.0077416 | 0.05789 | -0.060031 | 0.035809 | 0.11552 | -2.9251 | 0.19226 | -3.2639 | 0.86975 | -121.9162 | -24.9847 | 0.93842 | 1.0437 | 1.2177 | -122.5616 | 118.8629 | -0.83771 | 119.2017 | 122.9965 | -122.9462 | -0.43488 | 0.18768 | 0.33874 | 123.0652 | 123.1705 | 0.21057 | 122.319 | 119.2017 | 123.3444 | 97.142 | -0.43488 | 122.319 | 119.2017 | 97.142 | 0.21057 | 123.3444 | -4.2938 | -123.5916
1195.9219 | 123.2758 | -122.1725 | 1.0162 | -0.30813 | 0.02554 | -0.016825 | 0.081388 | -0.050418 | 0.042217 | 0.11018 | -2.8976 | 0.20599 | -3.2455 | 0.90637 | -120.7031 | -24.5911 | 0.86975 | 1.062 | 1.1948 | -122.5433 | 118.927 | -0.81024 | 119.2749 | 123.0789 | -121.7194 | -0.37079 | 0.17853 | 0.3479 | 123.0423 | 123.2346 | 1.4694 | 122.3785 | 119.2749 | 123.3673 | 97.5815 | -0.37079 | 122.3785 | 119.2749 | 97.5815 | 1.4694 | 123.3673 | -4.2618 | -123.5596
1196.9219 | 123.2117 | -122.2046 | 1.03 | -0.36916 | 0.045834 | -0.0061444 | 0.081388 | -0.048281 | 0.04649 | 0.10911 | -2.7649 | 0.23804 | -3.0396 | 1.0071 | -120.4514 | -24.3713 | 0.737 | 1.1673 | 1.1398 | -122.5342 | 119.165 | -0.79193 | 119.4397 | 123.2117 | -121.4813 | -0.32959 | 0.10986 | 0.27466 | 122.9416 | 123.3719 | 1.7532 | 122.4426 | 119.4397 | 123.3444 | 97.8333 | -0.32959 | 122.4426 | 119.4397 | 97.8333 | 1.7532 | 123.3444 | -4.0695 | -123.5641
1197.9844 | 123.3398 | -122.1909 | 0.99792 | -0.4302 | 0.033017 | -0.046732 | 0.067503 | -0.05469 | 0.033672 | 0.11124 | -2.5909 | 0.19684 | -2.829 | 0.7782 | -121.0648 | -24.6323 | 0.88806 | 0.98419 | 1.1581 | -122.5616 | 119.3619 | -0.80109 | 119.5999 | 122.9691 | -122.0627 | -0.37079 | 0.16022 | 0.23804 | 123.0789 | 123.175 | 1.1261 | 122.3877 | 119.5999 | 123.349 | 97.5586 | -0.37079 | 122.3877 | 119.5999 | 97.5586 | 1.1261 | 123.349 | -3.8269 | -123.5596
1198.9219 | 123.3353 | -122.1863 | 1.0025 | -0.079243 | 0.018063 | -0.012553 | 0.071775 | -0.050418 | 0.042217 | 0.1059 | -2.3026 | 0.21515 | -2.6321 | 0.84686 | -120.6985 | -25.1541 | 0.90179 | 1.0254 | 1.1902 | -122.5342 | 119.5541 | -0.78735 | 119.8837 | 123.0331 | -121.701 | -0.3479 | 0.18768 | 0.32959 | 123.0881 | 123.2117 | 1.4877 | 122.4014 | 119.8837 | 123.3765 | 97.0322 | -0.3479 | 122.4014 | 119.8837 | 97.0322 | 1.4877 | 123.3765 | -3.6346 | -123.5367
1199.9844 | 123.3032 | -122.1634 | 0.98877 | 0.30223 | 0.016995 | -0.036051 | 0.068571 | -0.049349 | 0.037945 | 0.10804 | -2.3117 | 0.20142 | -2.5772 | 0.89264 | -121.5637 | -24.6597 | 0.8606 | 1.062 | 1.1627 | -122.5525 | 119.5862 | -0.78735 | 119.8517 | 123.056 | -122.5525 | -0.3891 | 0.17395 | 0.2655 | 123.024 | 123.2254 | 0.59967 | 122.3648 | 119.8517 | 123.3261 | 97.5037 | -0.3891 | 122.3648 | 119.8517 | 97.5037 | 0.59967 | 123.3261 | -3.566 | -123.5413
1200.9219 | 123.349 | -122.1725 | 0.98419 | -0.12502 | 0.031949 | -0.02537 | 0.068571 | -0.065371 | 0.030468 | 0.099494 | -2.1973 | 0.21973 | -2.5131 | 0.85144 | -121.138 | -24.733 | 0.89722 | 1.0117 | 1.1627 | -122.5708 | 119.6594 | -0.76446 | 119.9753 | 123.024 | -122.1222 | -0.39826 | 0.17853 | 0.31586 | 123.0698 | 123.1842 | 1.0345 | 122.3923 | 119.9753 | 123.3353 | 97.4396 | -0.39826 | 122.3923 | 119.9753 | 97.4396 | 1.0345 | 123.3353 | -3.4973 | -123.555
1201.9844 | 123.2437 | -122.2458 | 0.98877 | 0.31749 | 0.04263 | -0.010416 | 0.084592 | -0.052554 | 0.056103 | 0.089881 | -2.0462 | 0.25635 | -2.3392 | 0.99335 | -120.5017 | -24.5316 | 0.76904 | 1.1078 | 1.1078 | -122.5571 | 119.9066 | -0.73242 | 120.1996 | 123.2391 | -121.4905 | -0.31128 | 0.11902 | 0.29297 | 123.0148 | 123.3536 | 1.7441 | 122.5021 | 120.1996 | 123.3536 | 97.7142 | -0.31128 | 122.5021 | 120.1996 | 97.7142 | 1.7441 | 123.3536 | -3.3279 | -123.5458
1202.9219 | 123.3215 | -122.2321 | 0.97046 | 0.43956 | 0.038357 | -0.0040084 | 0.098478 | -0.056826 | 0.049694 | 0.11124 | -1.8723 | 0.21973 | -2.2064 | 0.92926 | -120.2866 | -23.3047 | 0.84228 | 1.0345 | 1.1261 | -122.5616 | 120.0256 | -0.75073 | 120.3598 | 123.1613 | -121.257 | -0.32959 | 0.15564 | 0.33417 | 123.0743 | 123.2666 | 1.9455 | 122.4518 | 120.3598 | 123.3582 | 98.9273 | -0.32959 | 122.4518 | 120.3598 | 98.9273 | 1.9455 | 123.3582 | -3.1769 | -123.5321
1203.9844 | 123.1522 | -122.1954 | 1.0071 | 0.30223 | 0.046902 | -0.0018714 | 0.091001 | -0.040805 | 0.059307 | 0.10697 | -1.9455 | 0.24719 | -2.2614 | 1.0162 | -120.3049 | -23.6252 | 0.72784 | 1.1398 | 1.1032 | -122.5662 | 119.9341 | -0.75989 | 120.2499 | 123.2117 | -121.312 | -0.37079 | 0.09613 | 0.31586 | 122.9233 | 123.3353 | 1.8906 | 122.4426 | 120.2499 | 123.2986 | 98.5703 | -0.37079 | 122.4426 | 120.2499 | 98.5703 | 1.8906 | 123.2986 | -3.2684 | -123.5733
1204.9219 | 123.3353 | -122.2046 | 0.99335 | -0.12502 | 0.027676 | -0.038187 | 0.062162 | -0.047213 | 0.034741 | 0.10804 | -1.7075 | 0.15564 | -2.0004 | 0.83771 | -120.4514 | -22.8287 | 0.85144 | 1.03 | 1.1581 | -122.5754 | 120.2042 | -0.83771 | 120.4971 | 123.0423 | -121.4447 | -0.37079 | 0.1648 | 0.29297 | 123.056 | 123.2346 | 1.7532 | 122.3602 | 120.4971 | 123.3627 | 99.3759 | -0.37079 | 122.3602 | 120.4971 | 99.3759 | 1.7532 | 123.3627 | -2.9938 | -123.5687
1205.9844 | 123.3398 | -122.2137 | 0.95673 | 0.24119 | 0.04797 | -0.0093484 | 0.083524 | -0.058962 | 0.059307 | 0.11979 | -1.6388 | 0.20599 | -1.9684 | 0.86975 | -120.6299 | -23.941 | 0.91095 | 0.98877 | 1.1444 | -122.5937 | 120.2454 | -0.75073 | 120.575 | 123.0835 | -121.5866 | -0.37994 | 0.18768 | 0.32959 | 123.1247 | 123.2025 | 1.5839 | 122.4197 | 120.575 | 123.3582 | 98.2727 | -0.37994 | 122.4197 | 120.575 | 98.2727 | 1.5839 | 123.3582 | -2.9251 | -123.5504
1206.9219 | 123.3353 | -122.1909 | 0.9613 | -0.079243 | 0.026608 | -0.030711 | 0.052549 | -0.055758 | 0.030468 | 0.10804 | -1.5656 | 0.20142 | -1.8585 | 0.83771 | -121.5775 | -24.1608 | 0.86975 | 1.0254 | 1.149 | -122.5754 | 120.3323 | -0.75989 | 120.6253 | 123.0286 | -122.5388 | -0.38452 | 0.18768 | 0.29297 | 123.0606 | 123.2162 | 0.6134 | 122.3923 | 120.6253 | 123.3398 | 98.0301 | -0.38452 | 122.3923 | 120.6253 | 98.0301 | 0.6134 | 123.3398 | -2.8198 | -123.5367
1207.9844 | 123.3719 | -122.2321 | 0.97504 | -0.12502 | 0.023404 | -0.02537 | 0.070707 | -0.050418 | 0.028332 | 0.11124 | -1.3962 | 0.19684 | -1.7395 | 0.8194 | -121.6507 | -25.3143 | 0.90179 | 0.9613 | 1.1719 | -122.5754 | 120.4926 | -0.7782 | 120.8359 | 123.0515 | -122.6257 | -0.34332 | 0.19684 | 0.34332 | 123.1338 | 123.1934 | 0.58136 | 122.4289 | 120.8359 | 123.4039 | 96.9177 | -0.34332 | 122.4289 | 120.8359 | 96.9177 | 0.58136 | 123.4039 | -2.7145 | -123.5504
1208.9219 | 123.3353 | -122.2824 | 0.89264 | 0.1649 | 0.034085 | -0.022166 | 0.070707 | -0.062167 | 0.027264 | 0.10911 | -1.5884 | 0.21973 | -1.9089 | 0.84686 | -121.7331 | -24.408 | 0.53558 | 0.78278 | 1.1032 | -122.699 | 120.3735 | -0.67291 | 120.694 | 123.1293 | -122.6257 | -0.41657 | 0.21057 | 0.32044 | 122.818 | 123.0652 | 0.54932 | 122.5021 | 120.694 | 123.3856 | 97.8745 | -0.41657 | 122.5021 | 120.694 | 97.8745 | 0.54932 | 123.3856 | -2.8015 | -123.5916
1209.9844 | 123.2666 | -122.2549 | 0.97046 | 0.71421 | 0.056515 | -0.031779 | 0.091001 | -0.052554 | 0.058239 | 0.099494 | -1.5015 | 0.27008 | -1.8585 | 0.99792 | -121.7422 | -24.4629 | 0.75073 | 1.1169 | 1.1032 | -122.5754 | 120.3964 | -0.70038 | 120.7535 | 123.2529 | -122.7127 | -0.32043 | 0.13275 | 0.35706 | 123.0057 | 123.3719 | 0.51269 | 122.525 | 120.7535 | 123.3582 | 97.7921 | -0.32043 | 122.525 | 120.7535 | 97.7921 | 0.51269 | 123.3582 | -2.829 | -123.5458
1210.9219 | 123.2803 | -122.2275 | 0.97961 | 0.042827 | 0.031949 | -0.02537 | 0.055753 | -0.047213 | 0.027264 | 0.11231 | -1.2451 | 0.20599 | -1.5244 | 0.8606 | -121.8292 | -24.2065 | 0.85144 | 1.0345 | 1.1215 | -122.5708 | 120.7031 | -0.77362 | 120.9824 | 123.0881 | -122.8088 | -0.34332 | 0.14191 | 0.27924 | 123.0789 | 123.262 | 0.39825 | 122.4335 | 120.9824 | 123.349 | 98.0209 | -0.34332 | 122.4335 | 120.9824 | 98.0209 | 0.39825 | 123.349 | -2.504 | -123.5504
1211.9844 | 123.3398 | -122.2183 | 0.95215 | 0.47007 | 0.037289 | 0.012014 | 0.086729 | -0.048281 | 0.052898 | 0.10804 | -0.74158 | 0.21057 | -1.0941 | 0.86975 | -121.8704 | -24.8566 | 0.88806 | 1.0071 | 1.1215 | -122.6395 | 121.1243 | -0.74158 | 121.4767 | 123.0881 | -122.8226 | -0.42114 | 0.16937 | 0.35248 | 123.1064 | 123.2254 | 0.3479 | 122.4289 | 121.4767 | 123.3398 | 97.3618 | -0.42114 | 122.4289 | 121.4767 | 97.3618 | 0.3479 | 123.3398 | -2.0462 | -123.5916
1212.9219 | 123.3536 | -122.2458 | 0.95215 | -0.23183 | 0.027676 | -0.027506 | 0.071775 | -0.046145 | 0.033672 | 0.11658 | -1.6296 | 0.21515 | -1.9821 | 0.79651 | -120.5704 | -24.2294 | 0.86517 | 0.94299 | 1.1398 | -122.6028 | 120.2637 | -0.737 | 120.6162 | 123.0423 | -121.5225 | -0.35706 | 0.18768 | 0.35248 | 123.111 | 123.1888 | 1.6754 | 122.4609 | 120.6162 | 123.3856 | 98.0164 | -0.35706 | 122.4609 | 120.6162 | 98.0164 | 1.6754 | 123.3856 | -2.9343 | -123.555
1213.9219 | 123.3353 | -122.2412 | 0.9613 | 0.37852 | 0.043698 | -0.015757 | 0.071775 | -0.052554 | 0.035809 | 0.1059 | -1.4648 | 0.20142 | -1.7807 | 0.83313 | -120.5887 | -23.6343 | 0.88348 | 0.97504 | 1.1169 | -122.6028 | 120.4605 | -0.75989 | 120.7764 | 123.0743 | -121.55 | -0.36163 | 0.15564 | 0.31586 | 123.1247 | 123.2162 | 1.6525 | 122.4426 | 120.7764 | 123.3582 | 98.6069 | -0.36163 | 122.4426 | 120.7764 | 98.6069 | 1.6525 | 123.3582 | -2.742 | -123.5641
1214.9844 | 123.2666 | -122.2778 | 0.9613 | 2.8504 | 0.044766 | -0.014689 | 0.089933 | -0.051486 | 0.060375 | 0.10377 | -1.4786 | 0.29297 | -1.8585 | 0.95673 | -120.6436 | -22.998 | 0.75073 | 1.0437 | 1.1078 | -122.6349 | 120.4193 | -0.66834 | 120.7993 | 123.2346 | -121.6049 | -0.35706 | 0.14648 | 0.37994 | 123.0286 | 123.3215 | 1.6342 | 122.5708 | 120.7993 | 123.3856 | 99.2798 | -0.35706 | 122.5708 | 120.7993 | 99.2798 | 1.6342 | 123.3856 | -2.8198 | -123.5962
1215.9219 | 123.3124 | -122.2504 | 0.95215 | 0.13438 | 0.03088 | -0.015757 | 0.062162 | -0.05469 | 0.034741 | 0.11338 | -1.4832 | 0.19684 | -1.7761 | 0.82855 | -121.4996 | -23.5245 | 0.80109 | 1.0117 | 1.0895 | -122.6074 | 120.4742 | -0.75531 | 120.7672 | 123.0789 | -122.4518 | -0.35706 | 0.13733 | 0.29297 | 123.0515 | 123.262 | 0.75073 | 122.4472 | 120.7672 | 123.3398 | 98.7259 | -0.35706 | 122.4472 | 120.7672 | 98.7259 | 0.75073 | 123.3398 | -2.7283 | -123.5596
1216.9219 | 123.3444 | -122.2321 | 0.95673 | 0.72947 | 0.035153 | -0.024302 | 0.073911 | -0.051486 | 0.047558 | 0.10911 | -1.3779 | 0.17395 | -1.7532 | 0.81482 | -121.0098 | -23.7991 | 0.8606 | 0.97504 | 1.1307 | -122.6532 | 120.4788 | -0.78278 | 120.8542 | 123.0469 | -121.9666 | -0.42114 | 0.17395 | 0.37537 | 123.0927 | 123.2071 | 1.2222 | 122.406 | 120.8542 | 123.3627 | 98.4329 | -0.42114 | 122.406 | 120.8542 | 98.4329 | 1.2222 | 123.3627 | -2.71 | -123.6099
1217.9844 | 123.2941 | -122.3099 | 0.95673 | -0.20131 | 0.026608 | -0.0061444 | 0.073911 | -0.050418 | 0.036877 | 0.11231 | -1.5747 | 0.21515 | -1.9363 | 0.90637 | -121.0236 | -23.465 | 0.74158 | 1.0391 | 1.0803 | -122.6303 | 120.3735 | -0.74158 | 120.7352 | 123.2162 | -121.9803 | -0.32043 | 0.1236 | 0.36163 | 123.0515 | 123.349 | 1.2863 | 122.525 | 120.7352 | 123.3902 | 98.8449 | -0.32043 | 122.525 | 120.7352 | 98.8449 | 1.2863 | 123.3902 | -2.8931 | -123.587
1218.9219 | 123.3261 | -122.2778 | 0.90179 | 0.43956 | 0.04263 | 0.0013326 | 0.072843 | -0.048281 | 0.047558 | 0.11872 | -1.5381 | 0.2243 | -1.8814 | 0.81024 | -120.6162 | -23.3047 | 0.79193 | 0.99335 | 1.0757 | -122.6624 | 120.3964 | -0.67749 | 120.7397 | 123.0881 | -121.5179 | -0.38452 | 0.17395 | 0.34332 | 123.0698 | 123.2712 | 1.6617 | 122.5021 | 120.7397 | 123.3536 | 98.9731 | -0.38452 | 122.5021 | 120.7397 | 98.9731 | 1.6617 | 123.3536 | -2.7832 | -123.5641
1219.9844 | 123.2483 | -122.3373 | 0.90637 | 0.13438 | 0.041562 | -0.038187 | 0.087797 | -0.047213 | 0.053967 | 0.10804 | -1.3458 | 0.24719 | -1.6846 | 0.90179 | -120.6985 | -23.3185 | 0.66376 | 1.0483 | 1.0162 | -122.6761 | 120.6528 | -0.65918 | 120.9915 | 123.2391 | -121.6049 | -0.33875 | 0.10986 | 0.33874 | 123.0011 | 123.3856 | 1.6388 | 122.5845 | 120.9915 | 123.3536 | 99.0189 | -0.33875 | 122.5845 | 120.9915 | 99.0189 | 1.6388 | 123.3536 | -2.5909 | -123.5825
1220.9219 | 123.3124 | -122.374 | 0.84686 | 0.57688 | 0.037289 | -0.018961 | 0.070707 | -0.039736 | 0.060375 | 0.10484 | -1.5747 | 0.21057 | -1.9272 | 0.75073 | -120.9137 | -23.3505 | 0.8194 | 0.91553 | 1.0666 | -122.731 | 120.4468 | -0.63629 | 120.7993 | 123.1247 | -121.7606 | -0.35706 | 0.21973 | 0.35248 | 123.1934 | 123.2895 | 1.4603 | 122.5845 | 120.7993 | 123.4406 | 99.0234 | -0.35706 | 122.5845 | 120.7993 | 99.0234 | 1.4603 | 123.4406 | -2.774 | -123.5779
1221.9844 | 123.2162 | -122.3648 | 0.89722 | 0.36326 | 0.041562 | -0.014689 | 0.091001 | -0.039736 | 0.052898 | 0.10911 | -1.4923 | 0.27924 | -1.8036 | 0.94757 | -120.8954 | -22.9843 | 0.65918 | 1.0529 | 1.0162 | -122.6898 | 120.5612 | -0.61798 | 120.8725 | 123.3124 | -121.7926 | -0.32501 | 0.11902 | 0.31128 | 123.024 | 123.4177 | 1.4694 | 122.644 | 120.8725 | 123.381 | 99.3805 | -0.32501 | 122.644 | 120.8725 | 99.3805 | 1.4694 | 123.381 | -2.7008 | -123.587
1222.9219 | 123.349 | -122.3511 | 0.8606 | 0.39378 | 0.041562 | -0.0029404 | 0.066434 | -0.05469 | 0.057171 | 0.10804 | -1.4648 | 0.19684 | -1.8219 | 0.73242 | -120.6162 | -22.4899 | 0.82398 | 0.90637 | 1.0483 | -122.731 | 120.5292 | -0.66376 | 120.8862 | 123.0835 | -121.4767 | -0.37994 | 0.18768 | 0.35705 | 123.175 | 123.2574 | 1.7349 | 122.5479 | 120.8862 | 123.3994 | 99.8611 | -0.37994 | 122.5479 | 120.8862 | 99.8611 | 1.7349 | 123.3994 | -2.6825 | -123.5916
1223.9844 | 123.3261 | -122.2778 | 0.95215 | -0.39968 | 0.036221 | -0.013621 | 0.078184 | -0.05469 | 0.043285 | 0.11552 | -1.506 | 0.25635 | -1.8311 | 0.87891 | -120.2774 | -22.9431 | 0.63171 | 1.0529 | 1.0162 | -122.6303 | 120.4468 | -0.6958 | 120.7718 | 123.1567 | -121.2296 | -0.35248 | 0.064087 | 0.32501 | 122.9095 | 123.3307 | 2.0004 | 122.5342 | 120.7718 | 123.2941 | 99.3347 | -0.35248 | 122.5342 | 120.7718 | 99.3347 | 2.0004 | 123.2941 | -2.7832 | -123.5825
1224.9219 | 123.2391 | -122.3648 | 0.88806 | 1.5229 | 0.049038 | -0.031779 | 0.073911 | -0.048281 | 0.058239 | 0.10697 | -1.3962 | 0.26093 | -1.712 | 0.87891 | -120.5063 | -23.3505 | 0.65918 | 1.0254 | 1.0025 | -122.7036 | 120.6528 | -0.62714 | 120.9686 | 123.2437 | -121.3943 | -0.33875 | 0.11444 | 0.31586 | 123.024 | 123.3902 | 1.8585 | 122.6257 | 120.9686 | 123.3673 | 99.0143 | -0.33875 | 122.6257 | 120.9686 | 99.0143 | 1.8585 | 123.3673 | -2.6001 | -123.5916
1225.9844 | 123.23 | -122.374 | 0.89722 | -0.10976 | 0.04263 | -0.0018714 | 0.091001 | -0.038668 | 0.067852 | 0.10804 | -1.1215 | 0.26093 | -1.442 | 0.93384 | -120.2637 | -22.8973 | 0.62256 | 1.0757 | 1.0117 | -122.6761 | 120.932 | -0.63629 | 121.2524 | 123.3078 | -121.1609 | -0.30212 | 0.11444 | 0.32044 | 122.9965 | 123.4497 | 2.1103 | 122.6349 | 121.2524 | 123.3856 | 99.4766 | -0.30212 | 122.6349 | 121.2524 | 99.4766 | 2.1103 | 123.3856 | -2.3392 | -123.5733
1226.9219 | 123.2529 | -122.3694 | 0.88806 | 0.073345 | 0.046902 | -0.011485 | 0.093137 | -0.036532 | 0.056103 | 0.10804 | -1.593 | 0.23346 | -1.9592 | 0.88806 | -120.3461 | -23.0576 | 0.67291 | 1.0162 | 1.0391 | -122.7081 | 120.4102 | -0.6546 | 120.7764 | 123.2574 | -121.2341 | -0.33875 | 0.15106 | 0.36621 | 123.0423 | 123.3856 | 2.0233 | 122.6028 | 120.7764 | 123.4085 | 99.3118 | -0.33875 | 122.6028 | 120.7764 | 99.3118 | 2.0233 | 123.4085 | -2.8473 | -123.5962
1227.9844 | 123.2437 | -122.3648 | 0.89722 | -0.033467 | 0.039425 | -0.030711 | 0.089933 | -0.033328 | 0.062512 | 0.10056 | -1.5839 | 0.23804 | -1.9501 | 0.87891 | -120.6619 | -22.9385 | 0.66834 | 1.0254 | 1.0254 | -122.699 | 120.4147 | -0.65918 | 120.7809 | 123.2437 | -121.5591 | -0.33417 | 0.12817 | 0.36621 | 123.0331 | 123.3902 | 1.7029 | 122.6028 | 120.7809 | 123.3902 | 99.4263 | -0.33417 | 122.6028 | 120.7809 | 99.4263 | 1.7029 | 123.3902 | -2.8473 | -123.5962
1228.9219 | 123.2437 | -122.3785 | 0.87433 | -0.0029495 | 0.041562 | 0.00026463 | 0.081388 | -0.041873 | 0.055035 | 0.11018 | -1.4282 | 0.25177 | -1.767 | 0.86517 | -120.4788 | -22.6456 | 0.66376 | 1.0162 | 1.0071 | -122.7036 | 120.6116 | -0.62256 | 120.9503 | 123.2437 | -121.3531 | -0.32501 | 0.13275 | 0.33875 | 123.0423 | 123.3948 | 1.8997 | 122.6303 | 120.9503 | 123.3856 | 99.733 | -0.32501 | 122.6303 | 120.9503 | 99.733 | 1.8997 | 123.3856 | -2.6413 | -123.5779
1229.9844 | 123.2391 | -122.3648 | 0.89722 | -0.41494 | 0.044766 | -0.013621 | 0.064298 | -0.042941 | 0.05183 | 0.10911 | -1.4328 | 0.24719 | -1.7258 | 0.85144 | -120.195 | -22.5449 | 0.63171 | 1.0483 | 1.0483 | -122.6944 | 120.639 | -0.65003 | 120.932 | 123.2162 | -121.0922 | -0.32959 | 0.15106 | 0.29297 | 122.9965 | 123.4131 | 2.1698 | 122.612 | 120.932 | 123.4131 | 99.8199 | -0.32959 | 122.612 | 120.932 | 99.8199 | 2.1698 | 123.4131 | -2.623 | -123.5916
1230.9219 | 123.2666 | -122.3969 | 0.89264 | -0.018208 | 0.053311 | -0.0018714 | 0.076048 | -0.038668 | 0.060375 | 0.1262 | -1.767 | 0.26093 | -2.1423 | 0.86975 | -120.2774 | -22.5815 | 0.65918 | 1.0071 | 1.0025 | -122.731 | 120.2545 | -0.63171 | 120.6299 | 123.2666 | -121.17 | -0.33417 | 0.10986 | 0.37537 | 123.056 | 123.4039 | 2.1194 | 122.6578 | 120.6299 | 123.3994 | 99.8154 | -0.33417 | 122.6578 | 120.6299 | 99.8154 | 2.1194 | 123.3994 | -3.035 | -123.6237
1231.9219 | 123.2758 | -122.4106 | 0.87433 | -2.0171 | 0.054379 | -0.014689 | 0.081388 | -0.0376 | 0.061443 | 0.10377 | -1.9501 | 0.29755 | -2.1973 | 0.82855 | -120.0119 | -22.5998 | 0.66834 | 0.97046 | 1.03 | -122.7356 | 120.2133 | -0.57678 | 120.4605 | 123.2391 | -120.8862 | -0.32501 | 0.15564 | 0.24719 | 123.0789 | 123.381 | 2.3987 | 122.7081 | 120.4605 | 123.4406 | 99.8108 | -0.32501 | 122.7081 | 120.4605 | 99.8108 | 2.3987 | 123.4406 | -3.0716 | -123.6099
1232.9688 | 123.2529 | -122.3923 | 0.87433 | -0.39968 | 0.037289 | -0.020029 | 0.069639 | -0.039736 | 0.042217 | 0.12406 | -0.80109 | 0.25177 | -1.0941 | 0.8194 | -120.9915 | -22.5082 | 0.60425 | 1.03 | 1.0162 | -122.699 | 121.2982 | -0.62256 | 121.5912 | 123.2117 | -121.8658 | -0.3067 | 0.14191 | 0.29297 | 122.9965 | 123.4222 | 1.4008 | 122.644 | 121.5912 | 123.4085 | 99.884 | -0.3067 | 122.644 | 121.5912 | 99.884 | 1.4008 | 123.4085 | -1.9684 | -123.5733
1233.9219 | 123.2803 | -122.4197 | 0.88348 | -0.27761 | 0.041562 | -0.0093484 | 0.074979 | -0.040805 | 0.055035 | 0.1059 | -0.9613 | 0.26093 | -1.2726 | 0.82855 | -120.5658 | -22.6273 | 0.62256 | 1.0071 | 0.99792 | -122.7448 | 121.1472 | -0.62256 | 121.4584 | 123.2483 | -121.4493 | -0.32501 | 0.11444 | 0.31128 | 123.0423 | 123.4268 | 1.8539 | 122.6807 | 121.4584 | 123.4177 | 99.7925 | -0.32501 | 122.6807 | 121.4584 | 99.7925 | 1.8539 | 123.4177 | -2.1561 | -123.6282
1234.9688 | 123.4131 | -122.3465 | 0.8606 | -0.24709 | 0.028744 | -0.039256 | 0.050413 | -0.042941 | 0.034741 | 0.10056 | -0.50812 | 0.20142 | -0.86517 | 0.64087 | -121.2387 | -22.7829 | 0.8194 | 0.86517 | 1.0437 | -122.7722 | 121.4813 | -0.65918 | 121.8384 | 122.9874 | -122.0993 | -0.42572 | 0.1831 | 0.35706 | 123.1659 | 123.2117 | 1.1078 | 122.5479 | 121.8384 | 123.3902 | 99.5636 | -0.42572 | 122.5479 | 121.8384 | 99.5636 | 1.1078 | 123.3902 | -1.7258 | -123.6328
1235.9219 | 123.3078 | -122.3785 | 0.88348 | 0.027569 | 0.033017 | -0.0072124 | 0.081388 | -0.050418 | 0.052898 | 0.11018 | -0.32044 | 0.25177 | -0.6958 | 0.82398 | -120.7626 | -21.8353 | 0.67749 | 0.97504 | 1.0071 | -122.7448 | 121.6827 | -0.63171 | 122.0581 | 123.2025 | -121.6461 | -0.36621 | 0.1236 | 0.37537 | 123.056 | 123.3536 | 1.6159 | 122.6303 | 122.0581 | 123.3856 | 100.5432 | -0.36621 | 122.6303 | 122.0581 | 100.5432 | 1.6159 | 123.3856 | -1.5793 | -123.6282
1236.9688 | 123.349 | -122.3373 | 0.86975 | 0.37852 | 0.019131 | -0.012553 | 0.053617 | -0.055758 | 0.034741 | 0.11018 | -0.20142 | 0.21973 | -0.51727 | 0.73242 | -120.8588 | -22.5632 | 0.79651 | 0.93384 | 1.0712 | -122.7219 | 121.8201 | -0.65002 | 122.1359 | 123.0698 | -121.7285 | -0.38452 | 0.20142 | 0.31586 | 123.1338 | 123.2712 | 1.4786 | 122.5571 | 122.1359 | 123.4085 | 99.7742 | -0.38452 | 122.5571 | 122.1359 | 99.7742 | 1.4786 | 123.4085 | -1.387 | -123.5916
1237.9219 | 123.2758 | -122.3694 | 0.89722 | -0.063984 | 0.044766 | 0.00026463 | 0.079252 | -0.044009 | 0.056103 | 0.10484 | -0.18768 | 0.23804 | -0.55847 | 0.84228 | -120.1126 | -22.4579 | 0.68665 | 0.98877 | 1.0437 | -122.7356 | 121.8109 | -0.65918 | 122.1817 | 123.2117 | -121.0098 | -0.36621 | 0.14648 | 0.37079 | 123.056 | 123.3582 | 2.2568 | 122.6074 | 122.1817 | 123.4131 | 99.9115 | -0.36621 | 122.6074 | 122.1817 | 99.9115 | 2.2568 | 123.4131 | -1.4557 | -123.6328
1238.9844 | 123.2483 | -122.3923 | 0.91095 | -0.4302 | 0.04263 | -0.0018714 | 0.066434 | -0.044009 | 0.04649 | 0.10911 | -0.24261 | 0.25177 | -0.53101 | 0.8606 | -120.6528 | -22.3434 | 0.63171 | 1.0529 | 1.0437 | -122.699 | 121.8613 | -0.65918 | 122.1497 | 123.2529 | -121.5637 | -0.3067 | 0.13275 | 0.28839 | 123.024 | 123.4451 | 1.7395 | 122.644 | 122.1497 | 123.436 | 100.0488 | -0.3067 | 122.644 | 122.1497 | 100.0488 | 1.7395 | 123.436 | -1.442 | -123.6099
1239.9219 | 123.2483 | -122.374 | 0.91095 | -0.47597 | 0.043698 | -0.020029 | 0.066434 | -0.040805 | 0.040081 | 0.11445 | -0.30212 | 0.24719 | -0.62256 | 0.83771 | -120.4514 | -21.9635 | 0.68207 | 1.0025 | 1.0254 | -122.7036 | 121.7514 | -0.66376 | 122.0718 | 123.2117 | -121.3623 | -0.32959 | 0.11444 | 0.32043 | 123.056 | 123.3765 | 1.9226 | 122.6212 | 122.0718 | 123.3994 | 100.4105 | -0.32959 | 122.6212 | 122.0718 | 100.4105 | 1.9226 | 123.3994 | -1.5335 | -123.6145
1240.9844 | 123.2941 | -122.3373 | 0.90637 | 0.40904 | 0.027676 | -0.02537 | 0.068571 | -0.053622 | 0.041149 | 0.11338 | -0.80566 | 0.21057 | -1.0941 | 0.76446 | -121.4035 | -21.7667 | 0.75073 | 0.9613 | 1.0529 | -122.7081 | 121.2433 | -0.6958 | 121.5317 | 123.1018 | -122.3099 | -0.37079 | 0.14648 | 0.28839 | 123.0881 | 123.2986 | 0.93384 | 122.5479 | 121.5317 | 123.3902 | 100.5707 | -0.37079 | 122.5479 | 121.5317 | 100.5707 | 0.93384 | 123.3902 | -2.0004 | -123.6145
1241.9219 | 123.2758 | -122.3648 | 0.91095 | -0.41494 | 0.043698 | -0.021098 | 0.06323 | -0.052554 | 0.037945 | 0.10163 | -0.39368 | 0.23804 | -0.70953 | 0.82855 | -121.4172 | -21.9315 | 0.67749 | 0.99792 | 1.0345 | -122.731 | 121.6553 | -0.67291 | 121.9711 | 123.1934 | -122.3282 | -0.36621 | 0.1236 | 0.31586 | 123.0423 | 123.3627 | 0.94757 | 122.6028 | 121.9711 | 123.3994 | 100.4333 | -0.36621 | 122.6028 | 121.9711 | 100.4333 | 0.94757 | 123.3994 | -1.6205 | -123.642
1242.9844 | 123.3994 | -122.3053 | 0.86517 | -0.36916 | 0.028744 | -0.036051 | 0.061094 | -0.055758 | 0.026196 | 0.11231 | -0.58136 | 0.20142 | -0.97961 | 0.67291 | -121.4767 | -22.2336 | 0.78278 | 0.89722 | 1.062 | -122.731 | 121.3257 | -0.66376 | 121.7239 | 122.9782 | -122.3419 | -0.42572 | 0.19684 | 0.39825 | 123.0881 | 123.2025 | 0.82855 | 122.5067 | 121.7239 | 123.3673 | 100.0717 | -0.42572 | 122.5067 | 121.7239 | 100.0717 | 0.82855 | 123.3673 | -1.8448 | -123.5962
1243.9219 | 123.2758 | -122.3831 | 0.89722 | -0.47597 | 0.039425 | -0.0050764 | 0.076048 | -0.057894 | 0.047558 | 0.11124 | -1.062 | 0.2243 | -1.3962 | 0.80566 | -121.3074 | -22.522 | 0.66376 | 0.99792 | 1.03 | -122.7081 | 120.9869 | -0.67291 | 121.3211 | 123.1888 | -122.2046 | -0.32501 | 0.13275 | 0.33417 | 123.0469 | 123.381 | 1.0757 | 122.6074 | 121.3211 | 123.4131 | 99.8611 | -0.32501 | 122.6074 | 121.3211 | 99.8611 | 1.0757 | 123.4131 | -2.2934 | -123.6053
1244.9844 | 123.3444 | -122.3282 | 0.88348 | 0.50059 | 0.021267 | -0.018961 | 0.066434 | -0.053622 | 0.049694 | 0.1027 | -0.56305 | 0.19684 | -0.91095 | 0.72784 | -121.1792 | -22.4808 | 0.81024 | 0.90179 | 1.0666 | -122.7264 | 121.4172 | -0.68665 | 121.7651 | 123.056 | -122.0627 | -0.39825 | 0.1831 | 0.3479 | 123.1384 | 123.23 | 1.149 | 122.525 | 121.7651 | 123.3948 | 99.8474 | -0.39825 | 122.525 | 121.7651 | 99.8474 | 1.149 | 123.3948 | -1.7944 | -123.6099
1245.9219 | 123.3673 | -122.3648 | 0.85602 | 0.073345 | 0.02554 | -0.014689 | 0.065366 | -0.049349 | 0.041149 | 0.10911 | -0.74158 | 0.18768 | -0.94757 | 0.67749 | -121.8338 | -21.9452 | 0.73242 | 0.88348 | 1.0529 | -122.7676 | 121.4172 | -0.66833 | 121.6232 | 123.0423 | -122.6898 | -0.40283 | 0.19684 | 0.20599 | 123.0972 | 123.2483 | 0.53101 | 122.5525 | 121.6232 | 123.4177 | 100.4196 | -0.40283 | 122.5525 | 121.6232 | 100.4196 | 0.53101 | 123.4177 | -1.8036 | -123.6237
1246.9844 | 123.3627 | -122.3557 | 0.83771 | 0.77525 | 0.045834 | 0.016286 | 0.083524 | -0.052554 | 0.045422 | 0.10056 | -1.0162 | 0.1831 | -1.3916 | 0.72327 | -121.7422 | -22.3343 | 0.7782 | 0.88348 | 1.0208 | -122.7631 | 120.9641 | -0.6546 | 121.3394 | 123.0789 | -122.58 | -0.40741 | 0.1831 | 0.37537 | 123.1339 | 123.2391 | 0.6134 | 122.5388 | 121.3394 | 123.3765 | 100.0214 | -0.40741 | 122.5388 | 121.3394 | 100.0214 | 0.6134 | 123.3765 | -2.2293 | -123.6008
1247.9219 | 123.3765 | -122.3785 | 0.82855 | -0.063984 | 0.021267 | -0.020029 | 0.068571 | -0.050418 | 0.033672 | 0.10377 | -1.1993 | 0.21515 | -1.4923 | 0.70496 | -121.4859 | -22.229 | 0.74616 | 0.88348 | 1.0162 | -122.7631 | 120.8862 | -0.6134 | 121.1792 | 123.0835 | -122.3145 | -0.38452 | 0.18768 | 0.29297 | 123.1247 | 123.262 | 0.89264 | 122.5937 | 121.1792 | 123.3948 | 100.1495 | -0.38452 | 122.5937 | 121.1792 | 100.1495 | 0.89264 | 123.3948 | -2.3209 | -123.5916
1248.9844 | 123.3856 | -122.4106 | 0.81024 | 0.47007 | 0.03088 | -0.031779 | 0.083524 | -0.05469 | 0.04649 | 0.11445 | -1.3412 | 0.19226 | -1.712 | 0.70038 | -121.6415 | -21.9727 | 0.76904 | 0.85144 | 1.0025 | -122.7859 | 120.6985 | -0.61798 | 121.0693 | 123.111 | -122.4518 | -0.37537 | 0.19226 | 0.37079 | 123.1796 | 123.262 | 0.76904 | 122.6028 | 121.0693 | 123.4131 | 100.4379 | -0.37537 | 122.6028 | 121.0693 | 100.4379 | 0.76904 | 123.4131 | -2.5223 | -123.5962
1249.9219 | 123.4085 | -122.374 | 0.81024 | -0.10976 | 0.020199 | -0.027506 | 0.054685 | -0.058962 | 0.019787 | 0.10377 | -1.68 | 0.21057 | -2.037 | 0.64087 | -121.6827 | -22.0276 | 0.75073 | 0.82855 | 1.0117 | -122.7997 | 120.3369 | -0.59967 | 120.694 | 123.0148 | -122.493 | -0.42572 | 0.20142 | 0.35705 | 123.1247 | 123.2025 | 0.69122 | 122.5845 | 120.694 | 123.3856 | 100.3464 | -0.42572 | 122.5845 | 120.694 | 100.3464 | 0.69122 | 123.3856 | -2.8473 | -123.6099
1250.9844 | 123.2986 | -122.4197 | 0.83771 | 0.40904 | 0.029812 | -0.015757 | 0.093137 | -0.052554 | 0.057171 | 0.098426 | -2.6505 | 0.22888 | -2.9617 | 0.80566 | -120.4697 | -21.8445 | 0.65918 | 0.9201 | 0.97504 | -122.7905 | 119.458 | -0.60883 | 119.7693 | 123.2254 | -121.3074 | -0.37079 | 0.13733 | 0.31128 | 123.0789 | 123.3398 | 1.9501 | 122.6486 | 119.7693 | 123.3948 | 100.5753 | -0.37079 | 122.6486 | 119.7693 | 100.5753 | 1.9501 | 123.3948 | -3.7994 | -123.6282
1251.9219 | 123.4085 | -122.3877 | 0.81482 | -0.048725 | 0.014859 | -0.055277 | 0.062162 | -0.063235 | 0.024059 | 0.1059 | -1.4832 | 0.21973 | -1.8036 | 0.63171 | -120.4788 | -21.8353 | 0.74158 | 0.8194 | 1.0208 | -122.7676 | 120.5841 | -0.59509 | 120.9045 | 123.0194 | -121.2936 | -0.37994 | 0.20599 | 0.32044 | 123.1293 | 123.2071 | 1.9089 | 122.6074 | 120.9045 | 123.4085 | 100.5524 | -0.37994 | 122.6074 | 120.9045 | 100.5524 | 1.9089 | 123.4085 | -2.6184 | -123.5825
1252.9844 | 123.2483 | -122.438 | 0.85602 | 0.28697 | 0.04263 | 0.00026463 | 0.092069 | -0.060031 | 0.055035 | 0.1027 | -1.3504 | 0.25635 | -1.6754 | 0.88806 | -120.4422 | -21.048 | 0.55389 | 0.99792 | 0.96588 | -122.7905 | 120.7626 | -0.59967 | 121.0876 | 123.3261 | -121.2982 | -0.35248 | 0.10986 | 0.32501 | 122.9919 | 123.436 | 1.9958 | 122.6944 | 121.0876 | 123.4039 | 101.3901 | -0.35248 | 122.6944 | 121.0876 | 101.3901 | 1.9958 | 123.4039 | -2.5314 | -123.6465
1253.9219 | 123.3444 | -122.3969 | 0.83771 | 0.31749 | 0.031949 | -0.012553 | 0.072843 | -0.056826 | 0.039013 | 0.12193 | -0.89264 | 0.21057 | -1.2314 | 0.70496 | -120.4056 | -21.0754 | 0.71411 | 0.89264 | 1.0025 | -122.7585 | 121.1655 | -0.62714 | 121.5042 | 123.1018 | -121.2433 | -0.36163 | 0.16479 | 0.33875 | 123.111 | 123.2895 | 1.9913 | 122.6074 | 121.5042 | 123.3994 | 101.3214 | -0.36163 | 122.6074 | 121.5042 | 101.3214 | 1.9913 | 123.3994 | -2.0691 | -123.5962
1254.9844 | 123.2574 | -122.4655 | 0.83313 | 0.36326 | 0.050107 | -0.029642 | 0.098478 | -0.045077 | 0.04649 | 0.099494 | -0.80109 | 0.23346 | -1.1124 | 0.84686 | -120.5475 | -20.5582 | 0.5722 | 0.95673 | 0.92468 | -122.8088 | 121.3531 | -0.59967 | 121.6644 | 123.3124 | -121.3806 | -0.34332 | 0.091553 | 0.31128 | 123.0377 | 123.4222 | 1.918 | 122.699 | 121.6644 | 123.3902 | 101.9073 | -0.34332 | 122.699 | 121.6644 | 101.9073 | 1.918 | 123.3902 | -1.9455 | -123.642
1255.9219 | 123.3444 | -122.4335 | 0.81482 | 0.36326 | 0.03088 | -0.015757 | 0.074979 | -0.051486 | 0.039013 | 0.095222 | -0.48065 | 0.21515 | -0.83771 | 0.67291 | -120.7214 | -20.5902 | 0.70496 | 0.83771 | 0.98877 | -122.7951 | 121.5958 | -0.59967 | 121.9528 | 123.1064 | -121.5363 | -0.36163 | 0.17395 | 0.35706 | 123.1384 | 123.2712 | 1.712 | 122.6486 | 121.9528 | 123.4222 | 101.8433 | -0.36163 | 122.6486 | 121.9528 | 101.8433 | 1.712 | 123.4222 | -1.6525 | -123.6099
1256.9844 | 123.317 | -122.4518 | 0.81024 | -0.6133 | 0.053311 | -0.0072124 | 0.10916 | -0.046145 | 0.055035 | 0.10377 | -0.22888 | 0.28839 | -0.62714 | 0.82855 | -120.6436 | -20.8466 | 0.59509 | 0.90637 | 0.97046 | -122.8134 | 121.8246 | -0.52185 | 122.2229 | 123.2803 | -121.4539 | -0.36163 | 0.16022 | 0.39825 | 123.0469 | 123.3582 | 1.8082 | 122.7402 | 122.2229 | 123.4222 | 101.6052 | -0.36163 | 122.7402 | 122.2229 | 101.6052 | 1.8082 | 123.4222 | -1.4374 | -123.6237
1257.9219 | 123.3627 | -122.4472 | 0.75531 | 0.088604 | 0.012723 | -0.021098 | 0.061094 | -0.053622 | 0.033672 | 0.093085 | -0.33417 | 0.21057 | -0.64087 | 0.58594 | -120.3735 | -20.7092 | 0.6958 | 0.84228 | 0.90637 | -122.8409 | 121.8063 | -0.54474 | 122.113 | 123.0331 | -121.1288 | -0.39368 | 0.15106 | 0.3067 | 123.143 | 123.2895 | 2.0737 | 122.6578 | 122.113 | 123.3536 | 101.738 | -0.39368 | 122.6578 | 122.113 | 101.738 | 2.0737 | 123.3536 | -1.3962 | -123.5962
1258.9844 | 123.2483 | -122.4884 | 0.8194 | 0.27171 | 0.045834 | 0.0024006 | 0.087797 | -0.040805 | 0.065716 | 0.099494 | -0.33417 | 0.27466 | -0.65002 | 0.84228 | -120.1584 | -20.3705 | 0.55847 | 0.99335 | 0.93842 | -122.7905 | 121.8384 | -0.54474 | 122.1542 | 123.3307 | -120.9778 | -0.30212 | 0.11902 | 0.31586 | 123.0469 | 123.4818 | 2.33 | 122.7631 | 122.1542 | 123.4268 | 102.1179 | -0.30212 | 122.7631 | 122.1542 | 102.1179 | 2.33 | 123.4268 | -1.4694 | -123.6099
1259.9219 | 123.3902 | -122.4152 | 0.78735 | 0.47007 | 0.036221 | 0.0045366 | 0.076048 | -0.045077 | 0.039013 | 0.11338 | -0.19226 | 0.19684 | -0.55847 | 0.6546 | -120.1355 | -20.9198 | 0.737 | 0.81024 | 0.97504 | -122.8592 | 121.8567 | -0.59052 | 122.2229 | 123.0698 | -120.9229 | -0.44403 | 0.18768 | 0.36621 | 123.1522 | 123.2254 | 2.2797 | 122.612 | 122.2229 | 123.3902 | 101.4954 | -0.44403 | 122.612 | 122.2229 | 101.4954 | 2.2797 | 123.3902 | -1.3458 | -123.6465
1260.9844 | 123.3994 | -122.438 | 0.74616 | 0.59214 | 0.039425 | 0.0024006 | 0.08032 | -0.044009 | -0.013325 | 0.048225 | -0.073242 | 0.21057 | -0.46234 | 0.63629 | 0.36621 | -5.2643 | 0.70496 | 0.79193 | 0.94757 | -122.85 | 121.9757 | -0.53558 | 122.3648 | 123.0743 | -0.37994 | -0.41199 | 0.20142 | 0.3891 | 123.143 | 123.23 | 122.8043 | 122.6486 | 122.3648 | 123.3856 | 117.1738 | -0.41199 | 122.6486 | 122.3648 | 117.1738 | 122.8043 | 123.3856 | -1.2085 | -123.5962
1261.9219 | 123.349 | -122.4747 | 0.75989 | 0.43956 | 0.04263 | -0.010416 | 0.082456 | -0.062167 | -0.0069164 | 0.046088 | -1.3138 | 0.24261 | -1.6205 | 0.72784 | 0.41199 | -5.3513 | 0.63629 | 0.83313 | 0.92926 | -122.8683 | 120.8542 | -0.51727 | 121.1609 | 123.2025 | -0.3479 | -0.39368 | 0.16937 | 0.3067 | 123.111 | 123.3078 | 122.8867 | 122.7173 | 121.1609 | 123.4039 | 117.1234 | -0.39368 | 122.7173 | 121.1609 | 117.1234 | 122.8867 | 123.4039 | -2.3804 | -123.6282
1262.9844 | 123.317 | -122.4014 | 0.81482 | -0.12502 | 0.039425 | 0.01415 | 0.091001 | -0.047213 | -0.011188 | 0.043952 | -1.1124 | 0.25177 | -1.4832 | 0.76446 | 0.43488 | -5.2414 | 0.59052 | 0.89722 | 0.92926 | -122.8409 | 120.9183 | -0.56305 | 121.2891 | 123.1659 | -0.37994 | -0.43945 | 0.11444 | 0.37079 | 122.9919 | 123.2986 | 122.8363 | 122.6532 | 121.2891 | 123.3307 | 117.16 | -0.43945 | 122.6532 | 121.2891 | 117.16 | 122.8363 | 123.3307 | -2.298 | -123.6557
1263.9219 | 123.4085 | -122.4564 | 0.75073 | 0.77525 | 0.044766 | -0.02537 | 0.066434 | -0.051486 | -0.018665 | 0.043952 | -0.96588 | 0.20599 | -1.3367 | 0.62256 | 0.37537 | -5.0949 | 0.70496 | 0.79193 | 0.94299 | -122.8638 | 121.1197 | -0.54474 | 121.4905 | 123.0789 | -0.37537 | -0.40741 | 0.19226 | 0.37079 | 123.1613 | 123.2483 | 122.8317 | 122.6624 | 121.4905 | 123.3994 | 117.3615 | -0.40741 | 122.6624 | 121.4905 | 117.3615 | 122.8317 | 123.3994 | -2.0874 | -123.6145
1264.9844 | 123.2712 | -122.5204 | 0.7782 | 0.1649 | 0.036221 | -0.014689 | 0.083524 | -0.047213 | -0.016529 | 0.036475 | -1.3412 | 0.24261 | -1.6891 | 0.81482 | 0.53558 | -5.1498 | 0.50354 | 0.9613 | 0.92468 | -122.8409 | 120.8313 | -0.53558 | 121.1792 | 123.3353 | -0.24261 | -0.32043 | 0.14649 | 0.3479 | 123.024 | 123.4818 | 123.056 | 122.7631 | 121.1792 | 123.4451 | 117.3706 | -0.32043 | 122.7631 | 121.1792 | 117.3706 | 123.056 | 123.4451 | -2.4673 | -123.6191
1265.9219 | 123.3398 | -122.5021 | 0.76904 | 0.45481 | 0.045834 | -0.024302 | 0.084592 | -0.039736 | -0.0090524 | 0.032203 | -1.2543 | 0.23804 | -1.593 | 0.73242 | 0.43488 | -5.4016 | 0.61798 | 0.87891 | 0.92468 | -122.8683 | 120.9091 | -0.53101 | 121.2479 | 123.2346 | -0.33417 | -0.36621 | 0.15564 | 0.33875 | 123.1201 | 123.381 | 122.937 | 122.7402 | 121.2479 | 123.4268 | 117.1005 | -0.36621 | 122.7402 | 121.2479 | 117.1005 | 122.937 | 123.4268 | -2.3621 | -123.6374
1266.9844 | 123.3215 | -122.525 | 0.7782 | -0.033467 | 0.040494 | 0.0045366 | 0.06323 | -0.038668 | -0.0037124 | 0.03968 | -1.3092 | 0.24261 | -1.6754 | 0.75531 | 0.41657 | -4.9072 | 0.59509 | 0.88806 | 0.92468 | -122.8958 | 120.8496 | -0.53558 | 121.2158 | 123.2803 | -0.36163 | -0.37079 | 0.14649 | 0.36621 | 123.1201 | 123.4131 | 122.9416 | 122.7676 | 121.2158 | 123.4497 | 117.6178 | -0.37079 | 122.7676 | 121.2158 | 117.6178 | 122.9416 | 123.4497 | -2.4536 | -123.674
1267.9219 | 123.2895 | -122.5342 | 0.7782 | -0.12502 | 0.045834 | 0.013082 | 0.08032 | -0.044009 | -0.0058484 | 0.054633 | -1.3321 | 0.27008 | -1.6754 | 0.75073 | 0.3479 | -4.8157 | 0.56763 | 0.89722 | 0.91553 | -122.8729 | 120.8588 | -0.50812 | 121.2021 | 123.2849 | -0.4303 | -0.33874 | 0.13733 | 0.34332 | 123.1018 | 123.4314 | 122.8821 | 122.8043 | 121.2021 | 123.4497 | 117.7185 | -0.33874 | 122.8043 | 121.2021 | 117.7185 | 122.8821 | 123.4497 | -2.4536 | -123.6511
1268.9844 | 123.262 | -122.5159 | 0.80566 | -0.39968 | 0.02554 | -0.033915 | 0.073911 | -0.040805 | -0.031483 | 0.04502 | -1.2726 | 0.26093 | -1.5793 | 0.70496 | 0.39825 | -4.953 | 0.54474 | 0.90179 | 0.94299 | -122.8363 | 120.9366 | -0.54474 | 121.2433 | 123.2208 | -0.40741 | -0.32044 | 0.13733 | 0.3067 | 123.0606 | 123.4177 | 122.9141 | 122.7768 | 121.2433 | 123.4589 | 117.5629 | -0.32044 | 122.7768 | 121.2433 | 117.5629 | 122.9141 | 123.4589 | -2.3849 | -123.642
1269.9219 | 123.2712 | -122.5388 | 0.76904 | 0.1649 | 0.036221 | -0.0072124 | 0.078184 | -0.040805 | -0.016529 | 0.049293 | -1.5015 | 0.25635 | -1.8173 | 0.76446 | 0.45319 | -5.0308 | 0.51727 | 0.93842 | 0.88806 | -122.8958 | 120.7214 | -0.5127 | 121.0373 | 123.3032 | -0.31586 | -0.35706 | 0.11902 | 0.31586 | 123.056 | 123.4772 | 122.9919 | 122.7951 | 121.0373 | 123.4268 | 117.5079 | -0.35706 | 122.7951 | 121.0373 | 117.5079 | 122.9919 | 123.4268 | -2.5864 | -123.6649
1270.9844 | 123.3261 | -122.5342 | 0.83313 | -0.44545 | 0.038357 | -0.012553 | 0.067503 | -0.044009 | -0.025074 | 0.037543 | -1.3916 | 0.27466 | -1.7029 | 0.74158 | 0.44403 | -4.5639 | 0.59052 | 1.1124 | 0.90637 | -122.8088 | 120.8313 | -0.55847 | 121.1426 | 123.2758 | -0.3891 | -0.27466 | 0.073242 | 0.31128 | 123.1247 | 123.6465 | 122.9782 | 122.8088 | 121.1426 | 123.4406 | 117.9703 | -0.27466 | 122.8088 | 121.1426 | 117.9703 | 122.9782 | 123.4406 | -2.536 | -123.642
1271.9219 | 123.3215 | -122.5479 | 0.75073 | 0.027569 | 0.039425 | -0.0029404 | 0.078184 | -0.030123 | -0.0047804 | 0.040748 | -1.3 | 0.28839 | -1.6525 | 0.71411 | 0.4303 | -4.7836 | 0.55847 | 0.86975 | 0.93384 | -122.9141 | 120.8954 | -0.46234 | 121.2479 | 123.262 | -0.32043 | -0.36621 | 0.18311 | 0.35248 | 123.1064 | 123.4177 | 122.9782 | 122.8363 | 121.2479 | 123.4818 | 117.7643 | -0.36621 | 122.8363 | 121.2479 | 117.7643 | 122.9782 | 123.4818 | -2.4033 | -123.6649
1272.9219 | 123.3444 | -122.5708 | 0.75531 | -0.14028 | 0.049038 | -0.041392 | 0.073911 | -0.041873 | -0.013325 | 0.042884 | -1.5427 | 0.27008 | -1.9318 | 0.71411 | 0.33875 | -4.9164 | 0.56305 | 0.86517 | 0.90637 | -122.8958 | 120.639 | -0.48523 | 121.0281 | 123.2849 | -0.41657 | -0.32501 | 0.15106 | 0.3891 | 123.1339 | 123.436 | 122.9095 | 122.8409 | 121.0281 | 123.4772 | 117.6544 | -0.32501 | 122.8409 | 121.0281 | 117.6544 | 122.9095 | 123.4772 | -2.6871 | -123.6511
1273.9688 | 123.4177 | -122.5388 | 0.71869 | -0.20131 | 0.019131 | -0.029642 | 0.051481 | -0.044009 | -0.036823 | 0.050361 | -1.4877 | 0.20142 | -1.8494 | 0.53101 | 0.3067 | -4.7333 | 0.6546 | 0.75073 | 0.92926 | -122.9187 | 120.6894 | -0.51727 | 121.051 | 123.0698 | -0.41199 | -0.37994 | 0.21057 | 0.36163 | 123.1934 | 123.2895 | 122.8455 | 122.7402 | 121.051 | 123.468 | 117.8055 | -0.37994 | 122.7402 | 121.051 | 117.8055 | 122.8455 | 123.468 | -2.5681 | -123.6374
1274.9219 | 123.317 | -122.612 | 0.73242 | -0.33864 | 0.039425 | -0.011485 | 0.081388 | -0.042941 | -0.013325 | 0.036475 | -1.1169 | 0.27008 | -1.4786 | 0.68665 | 0.36163 | -4.6692 | 0.51727 | 0.84686 | 0.8606 | -122.937 | 121.1334 | -0.46234 | 121.4951 | 123.2986 | -0.37079 | -0.32501 | 0.12817 | 0.36163 | 123.1293 | 123.4589 | 122.9736 | 122.8821 | 121.4951 | 123.4726 | 117.9428 | -0.32501 | 122.8821 | 121.4951 | 117.9428 | 122.9736 | 123.4726 | -2.211 | -123.6694
1275.9844 | 123.317 | -122.5845 | 0.79651 | -0.41494 | 0.039425 | -0.010416 | 0.074979 | -0.045077 | -0.0079844 | 0.046088 | -0.97046 | 0.2655 | -1.2863 | 0.70496 | 0.27466 | -4.4403 | 0.54932 | 1.0895 | 0.88348 | -122.8638 | 121.2982 | -0.53101 | 121.6141 | 123.2895 | -0.52185 | -0.27924 | 0.086975 | 0.31586 | 123.1339 | 123.674 | 122.8592 | 122.85 | 121.6141 | 123.468 | 118.1442 | -0.27924 | 122.85 | 121.6141 | 118.1442 | 122.8592 | 123.468 | -2.0828 | -123.6603
1276.9219 | 123.3353 | -122.6028 | 0.72784 | -0.3539 | 0.036221 | -0.0029404 | 0.089933 | -0.045077 | -0.017597 | 0.037543 | -1.474 | 0.26093 | -1.8219 | 0.68665 | 0.39368 | -4.6829 | 0.50354 | 0.85144 | 0.8606 | -122.937 | 120.7809 | -0.46692 | 121.1288 | 123.2895 | -0.33417 | -0.33417 | 0.13275 | 0.3479 | 123.1064 | 123.4543 | 122.9965 | 122.8638 | 121.1288 | 123.4634 | 117.9199 | -0.33417 | 122.8638 | 121.1288 | 117.9199 | 122.9965 | 123.4634 | -2.5497 | -123.6649
1277.9844 | 123.2529 | -122.58 | 0.75531 | -0.46071 | 0.046902 | -0.028574 | 0.077116 | -0.034396 | -0.029346 | 0.04502 | -0.24719 | 0.24261 | -0.5722 | 0.70496 | 0.42114 | -4.6509 | 0.47607 | 0.90179 | 0.87433 | -122.9095 | 122.0078 | -0.5127 | 122.3328 | 123.2849 | -0.33417 | -0.32959 | 0.11902 | 0.32501 | 123.056 | 123.4817 | 123.0011 | 122.8226 | 122.3328 | 123.4543 | 117.9291 | -0.32959 | 122.8226 | 122.3328 | 117.9291 | 123.0011 | 123.4543 | -1.3275 | -123.6649
1278.9219 | 123.3627 | -122.525 | 0.77362 | -0.44545 | 0.039425 | -0.027506 | 0.064298 | -0.047213 | -0.029346 | 0.035407 | -0.24261 | 0.2655 | -0.57678 | 0.70953 | 0.41199 | -4.4632 | 0.4715 | 0.91095 | 0.84228 | -122.8958 | 121.9482 | -0.50812 | 122.2824 | 123.2346 | -0.36163 | -0.37079 | 0.068664 | 0.33417 | 122.9965 | 123.436 | 122.937 | 122.7905 | 122.2824 | 123.3673 | 118.0618 | -0.37079 | 122.7905 | 122.2824 | 118.0618 | 122.937 | 123.3673 | -1.3504 | -123.6694
1279.9844 | 123.3124 | -122.6028 | 0.72784 | -0.49123 | 0.034085 | -0.0050764 | 0.071775 | -0.0376 | -0.02721 | 0.04502 | -0.13275 | 0.23346 | -0.47607 | 0.63629 | 0.35248 | -4.4449 | 0.51727 | 0.83771 | 0.87891 | -122.937 | 122.1268 | -0.49439 | 122.4701 | 123.2391 | -0.37537 | -0.33417 | 0.15106 | 0.34332 | 123.1201 | 123.4406 | 122.9553 | 122.8363 | 122.4701 | 123.4818 | 118.158 | -0.33417 | 122.8363 | 122.4701 | 118.158 | 122.9553 | 123.4818 | -1.2039 | -123.6649
1280.9219 | 123.3215 | -122.6212 | 0.71869 | -0.47597 | 0.024472 | -0.015757 | 0.066434 | -0.042941 | -0.022938 | 0.042884 | -0.15106 | 0.22888 | -0.48523 | 0.6546 | 0.37994 | -4.2892 | 0.50354 | 0.83771 | 0.86975 | -122.9462 | 122.1359 | -0.48981 | 122.4701 | 123.2758 | -0.33875 | -0.32501 | 0.15106 | 0.33417 | 123.1247 | 123.4589 | 123.0011 | 122.85 | 122.4701 | 123.4909 | 118.3319 | -0.32501 | 122.85 | 122.4701 | 118.3319 | 123.0011 | 123.4909 | -1.2039 | -123.6649
1281.9844 | 123.4131 | -122.58 | 0.70953 | -0.018208 | 0.013791 | -0.0082804 | 0.064298 | -0.052554 | -0.040028 | 0.03968 | -0.14648 | 0.21973 | -0.48065 | 0.54474 | 0.29297 | -4.3991 | 0.6134 | 0.75073 | 0.89264 | -122.9599 | 122.0993 | -0.48981 | 122.4335 | 123.1247 | -0.41657 | -0.37994 | 0.1831 | 0.33417 | 123.1934 | 123.3307 | 122.8729 | 122.7997 | 122.4335 | 123.4726 | 118.1808 | -0.37994 | 122.7997 | 122.4335 | 118.1808 | 122.8729 | 123.4726 | -1.1902 | -123.6694
1282.9219 | 123.349 | -122.6257 | 0.71411 | -0.4302 | 0.037289 | -0.033915 | 0.071775 | -0.05469 | -0.028278 | 0.038612 | -0.14191 | 0.2243 | -0.50354 | 0.63171 | 0.32044 | -4.4266 | 0.5127 | 0.81482 | 0.87433 | -122.9599 | 122.1222 | -0.48981 | 122.4838 | 123.2574 | -0.39368 | -0.33417 | 0.16022 | 0.36163 | 123.1384 | 123.4406 | 122.9462 | 122.85 | 122.4838 | 123.5001 | 118.1992 | -0.33417 | 122.85 | 122.4838 | 118.1992 | 122.9462 | 123.5001 | -1.2177 | -123.674
1283.9688 | 123.317 | -122.6486 | 0.70038 | -0.38442 | 0.040494 | -0.046732 | 0.091001 | -0.047213 | -0.02187 | 0.032203 | -0.059509 | 0.2655 | -0.49896 | 0.73242 | 0.38452 | -4.39 | 0.48065 | 0.84686 | 0.82855 | -122.9507 | 122.1497 | -0.43487 | 122.5891 | 123.381 | -0.31586 | -0.30212 | 0.12817 | 0.43945 | 123.1293 | 123.4955 | 123.0331 | 122.9141 | 122.5891 | 123.4772 | 118.2587 | -0.30212 | 122.9141 | 122.5891 | 118.2587 | 123.0331 | 123.4772 | -1.1993 | -123.6511
1284.9219 | 123.3627 | -122.6028 | 0.71411 | -0.3539 | 0.023404 | -0.027506 | 0.071775 | -0.045077 | -0.02721 | 0.038612 | -0.11902 | 0.20142 | -0.48065 | 0.60883 | 0.32959 | -4.5273 | 0.53101 | 0.80109 | 0.87891 | -122.9416 | 122.1222 | -0.5127 | 122.4838 | 123.2117 | -0.38452 | -0.33874 | 0.16479 | 0.36163 | 123.1339 | 123.4039 | 122.9324 | 122.8043 | 122.4838 | 123.4818 | 118.0756 | -0.33874 | 122.8043 | 122.4838 | 118.0756 | 122.9324 | 123.4818 | -1.1948 | -123.6557
1285.9844 | 123.381 | -122.5662 | 0.70496 | 0.14964 | 0.02554 | -0.027506 | 0.051481 | -0.058962 | -0.048572 | 0.03968 | -0.20599 | 0.21057 | -0.51727 | 0.57678 | 0.33417 | -4.6692 | 0.55389 | 0.78735 | 0.87891 | -122.9416 | 122.0489 | -0.49439 | 122.3602 | 123.143 | -0.37079 | -0.37537 | 0.17395 | 0.31128 | 123.1201 | 123.3536 | 122.9004 | 122.7768 | 122.3602 | 123.4451 | 117.897 | -0.37537 | 122.7768 | 122.3602 | 117.897 | 122.9004 | 123.4451 | -1.2222 | -123.6465
1286.9219 | 123.4589 | -122.5342 | 0.70953 | -0.12502 | 0.038357 | -0.028574 | 0.070707 | -0.060031 | -0.035755 | 0.040748 | -0.14191 | 0.21057 | -0.48981 | 0.51727 | 0.21515 | -4.8157 | 0.66376 | 0.70038 | 0.90637 | -122.9874 | 122.0444 | -0.49896 | 122.3923 | 123.0515 | -0.49438 | -0.45319 | 0.19684 | 0.3479 | 123.1979 | 123.2346 | 122.7493 | 122.7448 | 122.3923 | 123.4406 | 117.7185 | -0.45319 | 122.7448 | 122.3923 | 117.7185 | 122.7493 | 123.4406 | -1.1993 | -123.6969
1287.9219 | 123.3902 | -122.5845 | 0.71411 | 0.10386 | 0.015927 | -0.039256 | 0.06323 | -0.062167 | -0.034687 | 0.033271 | -0.24719 | 0.17395 | -0.53101 | 0.5722 | 0.25635 | -4.7562 | 0.57678 | 0.76904 | 0.85144 | -122.9279 | 122.0535 | -0.54016 | 122.3373 | 123.1567 | -0.45776 | -0.34332 | 0.13733 | 0.28381 | 123.1613 | 123.3536 | 122.8409 | 122.7585 | 122.3373 | 123.436 | 117.8284 | -0.34332 | 122.7585 | 122.3373 | 117.8284 | 122.8409 | 123.436 | -1.2451 | -123.642
1288.9688 | 123.4085 | -122.612 | 0.71411 | 0.53111 | 0.040494 | -0.010416 | 0.084592 | -0.056826 | -0.024006 | 0.036475 | -0.16937 | 0.2243 | -0.53101 | 0.67291 | 0.3891 | -4.5456 | 0.57678 | 0.78735 | 0.86517 | -122.9919 | 122.081 | -0.48981 | 122.4426 | 123.2849 | -0.32501 | -0.37994 | 0.15106 | 0.36163 | 123.1888 | 123.3994 | 123.0011 | 122.8363 | 122.4426 | 123.4772 | 118.0664 | -0.37994 | 122.8363 | 122.4426 | 118.0664 | 123.0011 | 123.4772 | -1.2451 | -123.7061
1289.9219 | 123.3902 | -122.5571 | 0.70953 | 0.058086 | 0.02554 | -0.027506 | 0.078184 | -0.048281 | -0.047504 | 0.03968 | -0.2243 | 0.21973 | -0.51727 | 0.6134 | 0.33875 | -4.3121 | 0.5722 | 0.77362 | 0.87433 | -122.9324 | 122.0398 | -0.48981 | 122.3328 | 123.1705 | -0.37079 | -0.37537 | 0.1648 | 0.29297 | 123.1293 | 123.3307 | 122.8958 | 122.7768 | 122.3328 | 123.4314 | 118.2449 | -0.37537 | 122.7768 | 122.3328 | 118.2449 | 122.8958 | 123.4314 | -1.2268 | -123.642
1290.9844 | 123.3032 | -122.5845 | 0.73242 | 0.56163 | 0.039425 | -0.02537 | 0.088865 | -0.052554 | -0.017597 | 0.038612 | -0.23346 | 0.2655 | -0.56305 | 0.78278 | 0.47607 | -4.3579 | 0.49896 | 0.90637 | 0.8606 | -122.9462 | 122.0215 | -0.46692 | 122.3511 | 123.3673 | -0.25635 | -0.36163 | 0.12817 | 0.32959 | 123.0835 | 123.4909 | 123.0606 | 122.85 | 122.3511 | 123.4451 | 118.2266 | -0.36163 | 122.85 | 122.3511 | 118.2266 | 123.0606 | 123.4451 | -1.2955 | -123.6786
1291.9219 | 123.4589 | -122.5479 | 0.67749 | -0.033467 | 0.021267 | -0.036051 | 0.055753 | -0.057894 | -0.031483 | 0.036475 | -0.11902 | 0.21057 | -0.50812 | 0.51727 | 0.27466 | -4.5731 | 0.65002 | 0.72784 | 0.90179 | -122.9645 | 122.0398 | -0.46692 | 122.4289 | 123.0652 | -0.40283 | -0.41657 | 0.2243 | 0.3891 | 123.1979 | 123.2758 | 122.8226 | 122.7585 | 122.4289 | 123.4497 | 117.9749 | -0.41657 | 122.7585 | 122.4289 | 117.9749 | 122.8226 | 123.4497 | -1.1856 | -123.642
1292.9844 | 123.3948 | -122.5708 | 0.71869 | 0.57688 | 0.023404 | -0.017893 | 0.074979 | -0.058962 | -0.034687 | 0.02793 | -0.17853 | 0.19226 | -0.54016 | 0.59509 | 0.33875 | -4.3442 | 0.64545 | 0.75073 | 0.90637 | -122.9462 | 122.0306 | -0.52643 | 122.3923 | 123.1659 | -0.37994 | -0.37537 | 0.18768 | 0.36163 | 123.2162 | 123.3215 | 122.9095 | 122.7631 | 122.3923 | 123.4772 | 118.2266 | -0.37537 | 122.7631 | 122.3923 | 118.2266 | 122.9095 | 123.4772 | -1.2589 | -123.6649
1293.9219 | 123.317 | -122.6212 | 0.74158 | -0.44545 | 0.039425 | -0.022166 | 0.073911 | -0.053622 | -0.020801 | 0.03968 | -0.26093 | 0.26093 | -0.5722 | 0.71411 | 0.44861 | -4.2801 | 0.45776 | 0.8606 | 0.84686 | -122.9279 | 122.049 | -0.48065 | 122.3602 | 123.3353 | -0.29297 | -0.3067 | 0.10529 | 0.31128 | 123.0789 | 123.4818 | 123.0698 | 122.8821 | 122.3602 | 123.468 | 118.3411 | -0.3067 | 122.8821 | 122.3602 | 118.3411 | 123.0698 | 123.468 | -1.3138 | -123.6694
1294.9844 | 123.4085 | -122.612 | 0.68207 | 0.47007 | 0.057583 | -0.016825 | 0.076048 | -0.052554 | -0.011188 | 0.031135 | -0.16022 | 0.23346 | -0.52185 | 0.64087 | 0.36621 | -4.3076 | 0.57678 | 0.74158 | 0.83771 | -122.9782 | 122.0901 | -0.44861 | 122.4518 | 123.2529 | -0.31586 | -0.36621 | 0.15564 | 0.36163 | 123.1888 | 123.3536 | 122.9782 | 122.8455 | 122.4518 | 123.4497 | 118.3044 | -0.36621 | 122.8455 | 122.4518 | 118.3044 | 122.9782 | 123.4497 | -1.2039 | -123.6603
1295.9219 | 123.4039 | -122.5937 | 0.70953 | 0.19541 | 0.029812 | -0.014689 | 0.067503 | -0.058962 | -0.034687 | 0.034339 | -0.14191 | 0.20599 | -0.49439 | 0.5722 | 0.31586 | -4.3259 | 0.63171 | 0.73242 | 0.89722 | -122.9736 | 122.0993 | -0.50354 | 122.4518 | 123.1659 | -0.39368 | -0.37994 | 0.18768 | 0.35248 | 123.2254 | 123.3261 | 122.9095 | 122.7997 | 122.4518 | 123.4909 | 118.2678 | -0.37994 | 122.7997 | 122.4518 | 118.2678 | 122.9095 | 123.4909 | -1.2039 | -123.6832
1296.9844 | 123.2986 | -122.6349 | 0.70038 | -4.016 | 0.053311 | -0.0018714 | 0.089933 | -0.057894 | -0.01012 | 0.032203 | -0.25635 | 0.27008 | -0.50812 | 0.71869 | 0.41657 | -4.0833 | 0.47607 | 0.84228 | 0.84228 | -122.9691 | 122.1268 | -0.4303 | 122.3785 | 123.3536 | -0.28381 | -0.33417 | 0.14191 | 0.25177 | 123.111 | 123.4772 | 123.0515 | 122.905 | 122.3785 | 123.4772 | 118.5516 | -0.33417 | 122.905 | 122.3785 | 118.5516 | 123.0515 | 123.4772 | -1.2085 | -123.6694
1297.9219 | 123.3948 | -122.5845 | 0.70953 | 0.27171 | 0.02554 | -0.014689 | 0.061094 | -0.060031 | -0.034687 | 0.040748 | -0.18768 | 0.21057 | -0.48523 | 0.60425 | 0.33417 | -4.1611 | 0.56305 | 0.7782 | 0.88348 | -122.937 | 122.0993 | -0.49896 | 122.3969 | 123.1888 | -0.37537 | -0.35248 | 0.17395 | 0.29755 | 123.1476 | 123.3627 | 122.9187 | 122.7951 | 122.3969 | 123.468 | 118.4235 | -0.35248 | 122.7951 | 122.3969 | 118.4235 | 122.9187 | 123.468 | -1.1948 | -123.6465
1298.9844 | 123.3353 | -122.6074 | 0.72784 | -0.64382 | 0.041562 | -0.041392 | 0.085661 | -0.047213 | -0.02187 | 0.038612 | -0.35248 | 0.29297 | -0.64545 | 0.70038 | 0.50812 | -4.0558 | 0.49896 | 0.85144 | 0.85602 | -122.937 | 121.962 | -0.43488 | 122.2549 | 123.3078 | -0.21973 | -0.32959 | 0.12817 | 0.29297 | 123.1064 | 123.4589 | 123.1155 | 122.9004 | 122.2549 | 123.4634 | 118.5516 | -0.32959 | 122.9004 | 122.2549 | 118.5516 | 123.1155 | 123.4634 | -1.3733 | -123.6649
1299.9219 | 123.4543 | -122.5891 | 0.67291 | 0.50059 | 0.044766 | -0.031779 | 0.070707 | -0.061099 | -0.018665 | 0.03968 | -1.3916 | 0.19684 | -1.7715 | 0.59052 | 0.35706 | -4.2435 | 0.65002 | 0.73242 | 0.88806 | -122.9736 | 120.8176 | -0.47607 | 121.1975 | 123.1796 | -0.31586 | -0.38452 | 0.21515 | 0.37994 | 123.2391 | 123.3215 | 122.9462 | 122.7859 | 121.1975 | 123.4772 | 118.3456 | -0.38452 | 122.7859 | 121.1975 | 118.3456 | 122.9462 | 123.4772 | -2.4445 | -123.6465
1300.9844 | 123.3582 | -122.612 | 0.73242 | -0.39968 | 0.043698 | -0.0040084 | 0.082456 | -0.044009 | -0.0090524 | 0.036475 | -0.16479 | 0.2655 | -0.5127 | 0.72784 | 0.44861 | -4.0192 | 0.47607 | 0.87433 | 0.87891 | -122.9599 | 122.0993 | -0.46692 | 122.4472 | 123.3398 | -0.28381 | -0.3479 | 0.14648 | 0.3479 | 123.0881 | 123.4863 | 123.0606 | 122.8775 | 122.4472 | 123.4909 | 118.5928 | -0.3479 | 122.8775 | 122.4472 | 118.5928 | 123.0606 | 123.4909 | -1.2451 | -123.6923
1301.9219 | 123.3398 | -122.58 | 0.74616 | -0.018208 | 0.053311 | -0.021098 | 0.083524 | -0.053622 | -0.014393 | 0.037543 | -0.1831 | 0.26093 | -0.48981 | 0.71869 | 0.50354 | -3.9093 | 0.54474 | 0.87891 | 0.86517 | -122.9187 | 122.0901 | -0.48523 | 122.3969 | 123.2986 | -0.24262 | -0.33875 | 0.11902 | 0.3067 | 123.1247 | 123.4589 | 123.0835 | 122.8409 | 122.3969 | 123.4451 | 118.6707 | -0.33875 | 122.8409 | 122.3969 | 118.6707 | 123.0835 | 123.4451 | -1.236 | -123.6649
1302.9688 | 123.3673 | -122.5937 | 0.73242 | -0.27761 | 0.045834 | -0.00080337 | 0.086729 | -0.045077 | -0.025074 | 0.050361 | -0.14191 | 0.2243 | -0.48981 | 0.6958 | 0.44403 | -3.8818 | 0.54016 | 0.84228 | 0.87891 | -122.9462 | 122.1039 | -0.50812 | 122.4518 | 123.2895 | -0.28839 | -0.35248 | 0.14648 | 0.3479 | 123.1338 | 123.436 | 123.0377 | 122.818 | 122.4518 | 123.4726 | 118.7119 | -0.35248 | 122.818 | 122.4518 | 118.7119 | 123.0377 | 123.4726 | -1.2222 | -123.6786
1303.9219 | 123.4222 | -122.58 | 0.71411 | -0.048725 | 0.024472 | -0.024302 | 0.056821 | -0.036532 | -0.041096 | 0.035407 | -0.11444 | 0.22888 | -0.44861 | 0.55389 | 0.36621 | -3.9276 | 0.60883 | 0.76904 | 0.89722 | -122.937 | 122.1313 | -0.48523 | 122.4655 | 123.1338 | -0.3479 | -0.35706 | 0.18311 | 0.33417 | 123.1888 | 123.349 | 122.9462 | 122.8088 | 122.4655 | 123.4772 | 118.6523 | -0.35706 | 122.8088 | 122.4655 | 118.6523 | 122.9462 | 123.4772 | -1.1627 | -123.6511
1304.9844 | 123.2758 | -122.5937 | 0.7782 | -0.47597 | 0.044766 | -0.020029 | 0.08032 | -0.031191 | -0.036823 | 0.036475 | -0.15564 | 0.23804 | -0.49439 | 0.75989 | 0.59967 | -3.5889 | 0.59052 | 0.8194 | 0.88806 | -122.9233 | 122.0993 | -0.54016 | 122.438 | 123.3536 | -0.17853 | -0.32959 | 0.10986 | 0.33875 | 123.1842 | 123.4131 | 123.1934 | 122.8317 | 122.438 | 123.4818 | 119.0048 | -0.32959 | 122.8317 | 122.438 | 119.0048 | 123.1934 | 123.4818 | -1.2726 | -123.7015
1305.9219 | 123.4497 | -122.5845 | 0.67749 | 0.40904 | 0.04263 | -0.0082804 | 0.081388 | -0.048281 | -0.026142 | 0.048225 | -0.09613 | 0.23346 | -0.50354 | 0.58136 | 0.37079 | -3.8727 | 0.60883 | 0.78278 | 0.86975 | -122.9874 | 122.081 | -0.44403 | 122.4884 | 123.1659 | -0.3067 | -0.40283 | 0.19226 | 0.40741 | 123.1934 | 123.3673 | 122.9553 | 122.818 | 122.4884 | 123.4543 | 118.7119 | -0.40283 | 122.818 | 122.4884 | 118.7119 | 122.9553 | 123.4543 | -1.181 | -123.6649
1306.9844 | 123.3582 | -122.6257 | 0.72327 | 0.36326 | 0.034085 | -0.024302 | 0.081388 | -0.047213 | -0.0026434 | 0.037543 | -0.050354 | 0.32044 | -0.39825 | 0.70038 | 0.43488 | -3.9185 | 0.50354 | 0.82398 | 0.88806 | -122.9507 | 122.2275 | -0.40283 | 122.5754 | 123.3261 | -0.28839 | -0.32501 | 0.1648 | 0.3479 | 123.1293 | 123.4497 | 123.0606 | 122.9462 | 122.5754 | 123.5138 | 118.7073 | -0.32501 | 122.9462 | 122.5754 | 118.7073 | 123.0606 | 123.5138 | -1.1215 | -123.674
1307.9219 | 123.3261 | -122.6349 | 0.71411 | 0.18016 | 0.053311 | -0.013621 | 0.069639 | -0.049349 | -0.0069164 | 0.043952 | -0.15106 | 0.25177 | -0.48981 | 0.72327 | 0.49439 | -3.9413 | 0.46692 | 0.90179 | 0.82398 | -122.9599 | 122.1451 | -0.46234 | 122.4838 | 123.3582 | -0.21973 | -0.32501 | 0.10986 | 0.33874 | 123.1018 | 123.5367 | 123.1293 | 122.8867 | 122.4838 | 123.4589 | 118.6935 | -0.32501 | 122.8867 | 122.4838 | 118.6935 | 123.1293 | 123.4589 | -1.2039 | -123.674
1309 | 123.4314 | -122.5388 | 0.71411 | 0.40904 | 0.049038 | -0.027506 | 0.05789 | -0.053622 | -0.040028 | 0.034339 | -0.21973 | 0.21057 | -0.46234 | 0.54016 | 0.35706 | -4.0558 | 0.72327 | 0.77362 | 0.92468 | -132.28 | 122.0764 | -0.50354 | 122.319 | 123.0789 | -0.35706 | -9.7412 | 0.21057 | 0.24261 | 123.262 | 123.3124 | 122.8958 | 122.7493 | 122.319 | 123.4634 | 118.483 | -9.7412 | 122.7493 | 122.319 | 118.483 | 122.8958 | 123.4634 | -1.1765 | -132.9941
1309.9219 | 123.3353 | -122.5937 | 0.74158 | 0.19541 | 0.043698 | 0.0034686 | 0.076048 | -0.044009 | -0.0079844 | 0.034339 | -0.14648 | 0.27008 | -0.48523 | 0.78278 | 0.5127 | -3.9459 | 0.47607 | 0.93384 | 0.85602 | -122.9324 | 122.1085 | -0.4715 | 122.4472 | 123.3765 | -0.22888 | -0.33875 | 0.11444 | 0.33875 | 123.0698 | 123.5275 | 123.1064 | 122.8638 | 122.4472 | 123.4497 | 118.6478 | -0.33875 | 122.8638 | 122.4472 | 118.6478 | 123.1064 | 123.4497 | -1.2268 | -123.674
1310.9844 | 123.3627 | -122.612 | 0.72784 | -0.36916 | 0.039425 | -0.016825 | 0.081388 | -0.041873 | -0.02187 | 0.033271 | -0.12817 | 0.24719 | -0.48065 | 0.6958 | 0.43488 | -3.9871 | 0.52185 | 0.84228 | 0.87891 | -122.9691 | 122.1313 | -0.48065 | 122.4838 | 123.3078 | -0.29297 | -0.35706 | 0.15106 | 0.35248 | 123.1339 | 123.4543 | 123.0469 | 122.8592 | 122.4838 | 123.4909 | 118.6249 | -0.35706 | 122.8592 | 122.4838 | 118.6249 | 123.0469 | 123.4909 | -1.2085 | -123.6969
1311.9219 | 123.3307 | -122.5891 | 0.737 | 0.28697 | 0.04797 | -0.0082804 | 0.10489 | -0.048281 | -0.033619 | 0.035407 | -0.14191 | 0.24719 | -0.48981 | 0.84686 | 0.43945 | -4.0192 | 0.52643 | 0.90637 | 0.86975 | -122.9462 | 122.0993 | -0.48981 | 122.4472 | 123.436 | -0.29755 | -0.35706 | 0.13275 | 0.3479 | 123.1155 | 123.4955 | 123.0286 | 122.8363 | 122.4472 | 123.4589 | 118.5699 | -0.35706 | 122.8363 | 122.4472 | 118.5699 | 123.0286 | 123.4589 | -1.2268 | -123.6832
1312.9844 | 123.3261 | -122.5754 | 0.78735 | -0.52175 | 0.024472 | -0.020029 | 0.077116 | -0.03226 | -0.036823 | 0.042884 | -0.1831 | 0.25635 | -0.48065 | 0.73242 | 0.49439 | -4.0649 | 0.49439 | 0.92468 | 0.88348 | -122.905 | 122.0947 | -0.53101 | 122.3923 | 123.3078 | -0.29297 | -0.32959 | 0.09613 | 0.29755 | 123.0698 | 123.5001 | 123.0698 | 122.8317 | 122.3923 | 123.4589 | 118.5104 | -0.32959 | 122.8317 | 122.3923 | 118.5104 | 123.0698 | 123.4589 | -1.268 | -123.6923
1313.9219 | 123.3261 | -122.6166 | 0.74616 | 0.058086 | 0.039425 | -0.0050764 | 0.089933 | -0.046145 | -0.013325 | 0.040748 | -0.10529 | 0.25635 | -0.47607 | 0.737 | 0.48523 | -3.9185 | 0.48981 | 0.87433 | 0.87891 | -122.9507 | 122.1405 | -0.48981 | 122.5113 | 123.3536 | -0.26093 | -0.33417 | 0.13275 | 0.37079 | 123.1064 | 123.4909 | 123.1018 | 122.8729 | 122.5113 | 123.4955 | 118.6981 | -0.33417 | 122.8729 | 122.5113 | 118.6981 | 123.1018 | 123.4955 | -1.2222 | -123.6969
1314.9844 | 123.3582 | -122.6028 | 0.78735 | 0.027569 | 0.051175 | 0.0066726 | 0.08032 | -0.041873 | -0.01012 | 0.040748 | -0.09613 | 0.23346 | -0.46692 | 1.0025 | 0.6134 | -3.9963 | 0.58136 | 0.8606 | 0.9201 | -122.937 | 122.1359 | -0.5539 | 122.5067 | 123.6053 | -0.17395 | -0.33417 | 0.13275 | 0.37079 | 123.1842 | 123.4634 | 123.2162 | 122.8363 | 122.5067 | 123.5229 | 118.6066 | -0.33417 | 122.8363 | 122.5067 | 118.6066 | 123.2162 | 123.5229 | -1.2543 | -123.7244
1315.9219 | 123.3719 | -122.5937 | 0.72784 | -0.18605 | 0.04263 | 0.0024006 | 0.076048 | -0.041873 | -0.018665 | 0.040748 | -0.082397 | 0.26093 | -0.47607 | 0.67291 | 0.4303 | -4.1107 | 0.53101 | 0.84228 | 0.88348 | -122.9828 | 122.1176 | -0.46692 | 122.5113 | 123.2666 | -0.29755 | -0.3891 | 0.15564 | 0.39368 | 123.1247 | 123.436 | 123.024 | 122.8546 | 122.5113 | 123.4772 | 118.483 | -0.3891 | 122.8546 | 122.5113 | 118.483 | 123.024 | 123.4772 | -1.2039 | -123.7106
1316.9844 | 123.3215 | -122.6212 | 0.78735 | -0.3539 | 0.038357 | -0.0040084 | 0.068571 | -0.048281 | -0.033619 | 0.02259 | -0.16937 | 0.27008 | -0.48065 | 0.7782 | 0.61798 | -4.0237 | 0.49439 | 0.80109 | 0.9201 | -122.9416 | 122.1405 | -0.51727 | 122.4518 | 123.3994 | -0.16937 | -0.32043 | 0.13275 | 0.31128 | 123.1155 | 123.4222 | 123.2391 | 122.8912 | 122.4518 | 123.5413 | 118.5974 | -0.32043 | 122.8912 | 122.4518 | 118.5974 | 123.2391 | 123.5413 | -1.268 | -123.7289
1317.9219 | 123.3673 | -122.6395 | 0.71869 | -0.29287 | 0.040494 | -0.0082804 | 0.065366 | -0.039736 | -0.0047804 | 0.028999 | -0.086975 | 0.29755 | -0.42114 | 0.70496 | 0.44861 | -3.8773 | 0.52643 | 0.8606 | 0.8606 | -122.9782 | 122.2183 | -0.42114 | 122.5525 | 123.3444 | -0.27008 | -0.33875 | 0.14191 | 0.33417 | 123.1659 | 123.5001 | 123.0881 | 122.937 | 122.5525 | 123.5001 | 118.7622 | -0.33875 | 122.937 | 122.5525 | 118.7622 | 123.0881 | 123.5001 | -1.1398 | -123.6969
1318.9844 | 123.381 | -122.6624 | 0.72327 | -0.3539 | 0.034085 | -0.0061444 | 0.071775 | -0.036532 | -0.017597 | 0.046088 | -0.14648 | 0.25635 | -0.52185 | 0.66834 | 0.39368 | -4.248 | 0.50812 | 0.86517 | 0.8606 | -122.9874 | 122.1405 | -0.46692 | 122.5159 | 123.3307 | -0.32959 | -0.32501 | 0.13733 | 0.37537 | 123.1705 | 123.5275 | 123.056 | 122.9187 | 122.5159 | 123.5229 | 118.4143 | -0.32501 | 122.9187 | 122.5159 | 118.4143 | 123.056 | 123.5229 | -1.2451 | -123.7106
1319.9219 | 123.3536 | -122.6669 | 0.70496 | 0.042827 | 0.043698 | -0.017893 | 0.089933 | -0.053622 | -0.011188 | 0.037543 | -0.1236 | 0.27466 | -0.46692 | 0.68207 | 0.44861 | -4.4357 | 0.49896 | 0.84228 | 0.8606 | -122.9919 | 122.2 | -0.4303 | 122.5433 | 123.349 | -0.25635 | -0.32501 | 0.15564 | 0.34332 | 123.1659 | 123.5092 | 123.1155 | 122.9416 | 122.5433 | 123.5275 | 118.2312 | -0.32501 | 122.9416 | 122.5433 | 118.2312 | 123.1155 | 123.5275 | -1.1719 | -123.6969
1320.9844 | 123.381 | -122.6852 | 0.71869 | -0.29287 | 0.039425 | -0.013621 | 0.076048 | -0.040805 | -0.024006 | 0.040748 | -0.15564 | 0.24719 | -0.50812 | 0.65918 | 0.39368 | -4.5502 | 0.49439 | 0.82855 | 0.8606 | -123.0057 | 122.1771 | -0.4715 | 122.5296 | 123.3444 | -0.32501 | -0.32043 | 0.14191 | 0.35248 | 123.1796 | 123.5138 | 123.0789 | 122.9324 | 122.5296 | 123.5458 | 118.1351 | -0.32043 | 122.9324 | 122.5296 | 118.1351 | 123.0789 | 123.5458 | -1.2268 | -123.7244
1321.9219 | 123.3444 | -122.6578 | 0.69122 | -0.47597 | 0.037289 | -0.024302 | 0.070707 | -0.045077 | -0.025074 | 0.031135 | -0.15564 | 0.29297 | -0.47607 | 0.67291 | 0.4303 | -4.0649 | 0.44861 | 0.87433 | 0.85144 | -122.9736 | 122.1817 | -0.39825 | 122.5021 | 123.3307 | -0.26093 | -0.31586 | 0.16022 | 0.32043 | 123.1064 | 123.5321 | 123.0881 | 122.9507 | 122.5021 | 123.5092 | 118.5928 | -0.31586 | 122.9507 | 122.5021 | 118.5928 | 123.0881 | 123.5092 | -1.1673 | -123.6649
1322.9844 | 123.3582 | -122.6761 | 0.69122 | -0.46071 | 0.020199 | -0.028574 | 0.065366 | -0.0376 | -0.038959 | 0.034339 | -0.11444 | 0.21057 | -0.45776 | 0.59509 | 0.36621 | -4.3121 | 0.51727 | 0.81024 | 0.86975 | -123.0011 | 122.2183 | -0.48065 | 122.5616 | 123.2712 | -0.32501 | -0.32501 | 0.17853 | 0.34332 | 123.1934 | 123.4863 | 123.0423 | 122.8867 | 122.5616 | 123.5458 | 118.364 | -0.32501 | 122.8867 | 122.5616 | 118.364 | 123.0423 | 123.5458 | -1.149 | -123.6923
1323.9219 | 123.3673 | -122.7585 | 0.70953 | -0.20131 | 0.034085 | -0.027506 | 0.073911 | -0.047213 | -0.017597 | 0.041816 | -0.14191 | 0.2655 | -0.48981 | 0.66376 | 0.40283 | -4.1794 | 0.4303 | 0.83313 | 0.83313 | -123.0011 | 122.2687 | -0.44403 | 122.6166 | 123.4222 | -0.3067 | -0.24262 | 0.1236 | 0.3479 | 123.1888 | 123.5916 | 123.1613 | 123.024 | 122.6166 | 123.5916 | 118.5791 | -0.24262 | 123.024 | 122.6166 | 118.5791 | 123.1613 | 123.5916 | -1.1993 | -123.7106
1324.9844 | 123.3627 | -122.7173 | 0.69122 | -0.41494 | 0.029812 | -0.0061444 | 0.077116 | -0.036532 | -0.02187 | 0.031135 | -0.11444 | 0.22888 | -0.46234 | 0.59967 | 0.37994 | -4.0329 | 0.48523 | 0.8194 | 0.86975 | -122.9965 | 122.2549 | -0.46234 | 122.6028 | 123.317 | -0.31128 | -0.27924 | 0.17853 | 0.3479 | 123.2025 | 123.5367 | 123.0972 | 122.9462 | 122.6028 | 123.587 | 118.6844 | -0.27924 | 122.9462 | 122.6028 | 118.6844 | 123.0972 | 123.587 | -1.1536 | -123.6877
1325.9219 | 123.3627 | -122.7127 | 0.69122 | -0.3539 | 0.043698 | -0.011485 | 0.079252 | -0.036532 | -0.011188 | 0.034339 | -0.14648 | 0.27008 | -0.47607 | 0.65002 | 0.41657 | -3.9505 | 0.43945 | 0.83313 | 0.82855 | -123.0148 | 122.2366 | -0.42114 | 122.5662 | 123.3627 | -0.27466 | -0.30212 | 0.13733 | 0.32959 | 123.1522 | 123.5458 | 123.1293 | 122.9828 | 122.5662 | 123.5413 | 118.7622 | -0.30212 | 122.9828 | 122.5662 | 118.7622 | 123.1293 | 123.5413 | -1.1673 | -123.7061
1326.9844 | 123.3765 | -122.7081 | 0.69122 | -0.4302 | 0.035153 | -0.04246 | 0.066434 | -0.0376 | -0.017597 | 0.034339 | -0.13733 | 0.26093 | -0.47607 | 0.65002 | 0.39825 | -3.5065 | 0.44403 | 0.82855 | 0.8194 | -123.0377 | 122.2321 | -0.4303 | 122.5708 | 123.3582 | -0.29297 | -0.32959 | 0.12817 | 0.33874 | 123.1522 | 123.5367 | 123.1064 | 122.9691 | 122.5708 | 123.5275 | 119.2017 | -0.32959 | 122.9691 | 122.5708 | 119.2017 | 123.1064 | 123.5275 | -1.1673 | -123.7289
1327.9219 | 123.3673 | -122.7356 | 0.68665 | -0.3539 | 0.04797 | -0.026438 | 0.08032 | -0.038668 | -0.018665 | 0.034339 | -0.13733 | 0.24719 | -0.48523 | 0.64545 | 0.36621 | -3.6621 | 0.43945 | 0.83313 | 0.81482 | -123.024 | 122.2504 | -0.43945 | 122.5983 | 123.381 | -0.32043 | -0.28839 | 0.12817 | 0.3479 | 123.175 | 123.5687 | 123.1018 | 122.9828 | 122.5983 | 123.5504 | 119.0735 | -0.28839 | 122.9828 | 122.5983 | 119.0735 | 123.1018 | 123.5504 | -1.1719 | -123.7106
1328.9844 | 123.468 | -122.6624 | 0.66376 | -0.14028 | 0.028744 | -0.033915 | 0.051481 | -0.046145 | -0.047504 | 0.040748 | -0.10071 | 0.21057 | -0.44861 | 0.49439 | 0.27924 | -3.8544 | 0.60883 | 0.71411 | 0.89264 | -123.0286 | 122.2137 | -0.45319 | 122.5616 | 123.1567 | -0.38452 | -0.36621 | 0.22888 | 0.3479 | 123.2712 | 123.3765 | 122.9416 | 122.8729 | 122.5616 | 123.555 | 118.808 | -0.36621 | 122.8729 | 122.5616 | 118.808 | 122.9416 | 123.555 | -1.1124 | -123.6923
1329.9219 | 123.4085 | -122.6578 | 0.70496 | -0.36916 | 0.022336 | -0.032847 | 0.071775 | -0.039736 | -0.02721 | 0.042884 | -0.091553 | 0.20599 | -0.43488 | 0.57678 | 0.33875 | -3.7216 | 0.53101 | 0.76446 | 0.87891 | -123.0331 | 122.2229 | -0.49896 | 122.5662 | 123.2346 | -0.36621 | -0.37537 | 0.17395 | 0.34332 | 123.1888 | 123.4222 | 122.9965 | 122.8638 | 122.5662 | 123.5367 | 118.9362 | -0.37537 | 122.8638 | 122.5662 | 118.9362 | 122.9965 | 123.5367 | -1.1398 | -123.7381
1330.9688 | 123.4131 | -122.6761 | 0.6958 | 0.042827 | 0.021267 | 0.0024006 | 0.065366 | -0.051486 | -0.02721 | 0.048225 | -0.11902 | 0.20142 | -0.43945 | 0.54016 | 0.34332 | -3.6621 | 0.54016 | 0.76904 | 0.84228 | -123.0148 | 122.2366 | -0.49438 | 122.5571 | 123.2162 | -0.35248 | -0.33875 | 0.14648 | 0.32043 | 123.2162 | 123.4451 | 123.0194 | 122.8775 | 122.5571 | 123.5184 | 119.014 | -0.33875 | 122.8775 | 122.5571 | 119.014 | 123.0194 | 123.5184 | -1.1353 | -123.7106
1331.9219 | 123.3353 | -122.6852 | 0.6958 | -0.50649 | 0.029812 | -0.033915 | 0.085661 | -0.050418 | -0.035755 | 0.050361 | -0.16022 | 0.27008 | -0.48065 | 0.67291 | 0.44861 | -3.5385 | 0.42572 | 0.8606 | 0.84686 | -122.9965 | 122.2046 | -0.42572 | 122.525 | 123.3582 | -0.24719 | -0.31128 | 0.15106 | 0.32044 | 123.111 | 123.5458 | 123.1338 | 122.9553 | 122.525 | 123.5321 | 119.1467 | -0.31128 | 122.9553 | 122.525 | 119.1467 | 123.1338 | 123.5321 | -1.1765 | -123.6923
1332.9219 | 123.3398 | -122.7036 | 0.68665 | -0.44545 | 0.036221 | -0.038187 | 0.082456 | -0.046145 | -0.020801 | 0.034339 | -0.13275 | 0.23804 | -0.44403 | 0.65002 | 0.44861 | -4.0146 | 0.41657 | 0.81482 | 0.84686 | -123.024 | 122.2595 | -0.44861 | 122.5708 | 123.3536 | -0.23804 | -0.32044 | 0.16022 | 0.31128 | 123.1201 | 123.5184 | 123.1522 | 122.9416 | 122.5708 | 123.5504 | 118.689 | -0.32044 | 122.9416 | 122.5708 | 118.689 | 123.1522 | 123.5504 | -1.1307 | -123.7106
1333.9844 | 123.4222 | -122.6349 | 0.68207 | 0.30223 | 0.024472 | -0.030711 | 0.064298 | -0.049349 | -0.036823 | 0.043952 | -0.082397 | 0.20599 | -0.44861 | 0.54016 | 0.3479 | -3.7949 | 0.57678 | 0.74616 | 0.87891 | -123.0286 | 122.1863 | -0.47607 | 122.5525 | 123.175 | -0.33417 | -0.39368 | 0.19684 | 0.36621 | 123.2117 | 123.381 | 122.9828 | 122.8409 | 122.5525 | 123.5138 | 118.84 | -0.39368 | 122.8409 | 122.5525 | 118.84 | 122.9828 | 123.5138 | -1.1307 | -123.7106
1334.9219 | 123.4039 | -122.6669 | 0.68665 | -0.36916 | 0.015927 | -0.026438 | 0.066434 | -0.060031 | -0.022938 | 0.035407 | -0.091553 | 0.23804 | -0.46234 | 0.5722 | 0.34332 | -3.653 | 0.50812 | 0.75989 | 0.85144 | -123.0423 | 122.2046 | -0.44861 | 122.5754 | 123.2391 | -0.34332 | -0.37537 | 0.16479 | 0.37079 | 123.175 | 123.4268 | 123.0103 | 122.905 | 122.5754 | 123.5184 | 119.014 | -0.37537 | 122.905 | 122.5754 | 119.014 | 123.0103 | 123.5184 | -1.149 | -123.7289
1335.9219 | 123.4772 | -122.6624 | 0.66376 | -0.29287 | 0.034085 | -0.044596 | 0.068571 | -0.055758 | -0.037891 | 0.035407 | -0.073242 | 0.19226 | -0.42114 | 0.5127 | 0.31128 | -3.772 | 0.5722 | 0.68665 | 0.85144 | -123.0515 | 122.2412 | -0.4715 | 122.5891 | 123.175 | -0.35248 | -0.3891 | 0.18768 | 0.3479 | 123.2346 | 123.349 | 122.9736 | 122.8546 | 122.5891 | 123.5138 | 118.8904 | -0.3891 | 122.8546 | 122.5891 | 118.8904 | 122.9736 | 123.5138 | -1.0849 | -123.7152
1336.9219 | 123.4497 | -122.6807 | 0.64087 | 1.2025 | 0.022336 | -0.024302 | 0.073911 | -0.050418 | -0.035755 | 0.046088 | -0.1831 | 0.1831 | -0.47607 | 0.46692 | 0.3067 | -3.8727 | 0.53558 | 0.66834 | 0.83771 | -123.0606 | 122.2046 | -0.45776 | 122.4976 | 123.1476 | -0.33417 | -0.37994 | 0.19684 | 0.29297 | 123.2162 | 123.349 | 122.9874 | 122.8638 | 122.4976 | 123.5184 | 118.808 | -0.37994 | 122.8638 | 122.4976 | 118.808 | 122.9874 | 123.5184 | -1.1169 | -123.7015
1337.9844 | 123.4085 | -122.7356 | 0.6134 | 0.4243 | 0.035153 | 0.0056046 | 0.088865 | -0.058962 | -0.015461 | 0.026862 | -0.054932 | 0.2243 | -0.44403 | 0.54932 | 0.32501 | -3.8177 | 0.59052 | 0.68665 | 0.82855 | -123.0698 | 122.2916 | -0.3891 | 122.6807 | 123.2849 | -0.28839 | -0.33417 | 0.21515 | 0.3891 | 123.3261 | 123.4222 | 123.0606 | 122.9599 | 122.6807 | 123.5641 | 118.9178 | -0.33417 | 122.9599 | 122.6807 | 118.9178 | 123.0606 | 123.5641 | -1.0574 | -123.6832
1338.9219 | 123.3765 | -122.7036 | 0.67749 | -0.44545 | 0.02554 | -0.033915 | 0.079252 | -0.041873 | -0.015461 | 0.033271 | -0.11902 | 0.24261 | -0.45319 | 0.62714 | 0.43488 | -3.7857 | 0.45776 | 0.78735 | 0.81024 | -123.0148 | 122.2504 | -0.43488 | 122.5845 | 123.3307 | -0.24262 | -0.31128 | 0.13275 | 0.33417 | 123.1613 | 123.4909 | 123.1384 | 122.9462 | 122.5845 | 123.5138 | 118.9178 | -0.31128 | 122.9462 | 122.5845 | 118.9178 | 123.1384 | 123.5138 | -1.1307 | -123.6923
1339.9844 | 123.381 | -122.6715 | 0.64545 | 0.43956 | 0.049038 | 0.0034686 | 0.093137 | -0.062167 | -0.013325 | 0.03968 | -0.14191 | 0.25177 | -0.46692 | 0.6546 | 0.43945 | -3.8544 | 0.46692 | 0.78278 | 0.81024 | -123.0286 | 122.2046 | -0.39368 | 122.5296 | 123.3261 | -0.20599 | -0.35706 | 0.1648 | 0.32501 | 123.1384 | 123.4543 | 123.111 | 122.9233 | 122.5296 | 123.4818 | 118.8171 | -0.35706 | 122.9233 | 122.5296 | 118.8171 | 123.111 | 123.4818 | -1.1124 | -123.674
1340.9219 | 123.5641 | -122.6944 | 0.65002 | -0.32338 | 0.029812 | -0.015757 | 0.06323 | -0.042941 | -0.036823 | 0.050361 | -0.064087 | 0.20599 | -0.45319 | 0.50354 | 0.32959 | -3.7354 | 0.57678 | 0.69122 | 0.87433 | -123.0606 | 122.2412 | -0.44403 | 122.6303 | 123.1979 | -0.32043 | -0.36621 | 0.2243 | 0.3891 | 123.2712 | 123.3856 | 123.024 | 122.9004 | 122.6303 | 123.5687 | 118.959 | -0.36621 | 122.9004 | 122.6303 | 118.959 | 123.024 | 123.5687 | -1.1032 | -123.7106
1341.9844 | 123.4406 | -122.6624 | 0.63171 | 3.0335 | 0.023404 | -0.032847 | 0.073911 | -0.05469 | -0.038959 | 0.040748 | 0.036621 | 0.17395 | -0.46234 | 0.52643 | 0.36163 | -3.9047 | 0.58136 | 0.6958 | 0.83313 | -123.0789 | 122.2 | -0.45776 | 122.699 | 123.1888 | -0.27008 | -0.41656 | 0.20142 | 0.49896 | 123.2437 | 123.3582 | 123.024 | 122.8363 | 122.699 | 123.4955 | 118.7576 | -0.41656 | 122.8363 | 122.699 | 118.7576 | 123.024 | 123.4955 | -1.0941 | -123.7106
1342.9219 | 123.5001 | -122.6532 | 0.64545 | -0.23183 | 0.016995 | -0.0093484 | 0.064298 | -0.053622 | -0.032551 | 0.038612 | -0.054932 | 0.21515 | -0.41657 | 0.4715 | 0.27466 | -3.8223 | 0.58594 | 0.65002 | 0.82855 | -123.0743 | 122.2366 | -0.4303 | 122.5983 | 123.1247 | -0.37079 | -0.42114 | 0.1831 | 0.36163 | 123.2391 | 123.3032 | 122.9279 | 122.8683 | 122.5983 | 123.4818 | 118.8309 | -0.42114 | 122.8683 | 122.5983 | 118.8309 | 122.9279 | 123.4818 | -1.062 | -123.7198
1343.9844 | 123.4268 | -122.6807 | 0.6546 | 0.19541 | 0.031949 | -0.0029404 | 0.060026 | -0.066439 | -0.041096 | 0.038612 | -0.11902 | 0.22888 | -0.45319 | 0.54016 | 0.36621 | -3.7033 | 0.50812 | 0.72327 | 0.82855 | -123.0331 | 122.2275 | -0.42572 | 122.5616 | 123.2208 | -0.28839 | -0.35248 | 0.17395 | 0.33417 | 123.1888 | 123.4039 | 123.0469 | 122.9095 | 122.5616 | 123.5092 | 118.9774 | -0.35248 | 122.9095 | 122.5616 | 118.9774 | 123.0469 | 123.5092 | -1.1078 | -123.6877
1344.9219 | 123.4634 | -122.6669 | 0.67291 | -0.39968 | 0.034085 | -0.033915 | 0.071775 | -0.061099 | -0.037891 | 0.040748 | 0.15106 | 0.1831 | -0.43488 | 0.56763 | 0.32959 | -3.7765 | 0.55389 | 0.70038 | 0.82855 | -123.0423 | 122.2321 | -0.48981 | 122.818 | 123.2346 | -0.34332 | -0.37537 | 0.15564 | 0.58594 | 123.2208 | 123.3673 | 122.9965 | 122.85 | 122.818 | 123.4955 | 118.8904 | -0.37537 | 122.85 | 122.818 | 118.8904 | 122.9965 | 123.4955 | -1.1078 | -123.7152
1345.9688 | 123.349 | -122.7264 | 0.65918 | 0.1649 | 0.04263 | -0.0082804 | 0.092069 | -0.049349 | -0.017597 | 0.035407 | -0.11444 | 0.24261 | -0.4715 | 0.68207 | 0.42114 | -3.7628 | 0.39825 | 0.78735 | 0.79193 | -123.0698 | 122.2549 | -0.41656 | 122.612 | 123.4085 | -0.23804 | -0.34332 | 0.13275 | 0.35706 | 123.1247 | 123.5138 | 123.1476 | 122.9691 | 122.612 | 123.5184 | 118.9636 | -0.34332 | 122.9691 | 122.612 | 118.9636 | 123.1476 | 123.5184 | -1.1307 | -123.7289
1346.9219 | 123.4863 | -122.6395 | 0.65002 | -0.21657 | 0.022336 | -0.044596 | 0.062162 | -0.057894 | -0.036823 | 0.03968 | -0.086975 | 0.21973 | -0.4303 | 0.48981 | 0.28381 | -4.0054 | 0.55847 | 0.67291 | 0.82398 | -123.0469 | 122.2092 | -0.4303 | 122.5525 | 123.1293 | -0.36621 | -0.40741 | 0.17395 | 0.34332 | 123.1979 | 123.3124 | 122.9233 | 122.8592 | 122.5525 | 123.4634 | 118.634 | -0.40741 | 122.8592 | 122.5525 | 118.634 | 122.9233 | 123.4634 | -1.0803 | -123.6969
1347.9844 | 123.4268 | -122.6669 | 0.61798 | 0.10386 | 0.027676 | -0.043528 | 0.076048 | -0.070712 | -0.037891 | 0.03968 | -0.12817 | 0.2243 | -0.44861 | 0.52643 | 0.2655 | -3.9963 | 0.50354 | 0.6958 | 0.7782 | -123.0972 | 122.2183 | -0.39368 | 122.5388 | 123.1934 | -0.35248 | -0.4303 | 0.16022 | 0.32043 | 123.1705 | 123.3627 | 122.9324 | 122.8912 | 122.5388 | 123.4451 | 118.6707 | -0.4303 | 122.8912 | 122.5388 | 118.6707 | 122.9324 | 123.4451 | -1.0666 | -123.7152
1348.9219 | 123.436 | -122.6715 | 0.67291 | 0.28697 | 0.027676 | -0.034983 | 0.077116 | -0.057894 | -0.032551 | 0.040748 | -0.12817 | 0.17395 | -0.46234 | 0.52185 | 0.3067 | -3.8269 | 0.53101 | 0.70038 | 0.83313 | -123.0606 | 122.2092 | -0.49896 | 122.5433 | 123.1934 | -0.36621 | -0.3891 | 0.16022 | 0.33417 | 123.2025 | 123.3719 | 122.9782 | 122.8455 | 122.5433 | 123.5046 | 118.8446 | -0.3891 | 122.8455 | 122.5433 | 118.8446 | 122.9782 | 123.5046 | -1.1353 | -123.7335
1349.9844 | 123.4451 | -122.6624 | 0.66834 | 0.51585 | 0.028744 | -0.0061444 | 0.077116 | -0.060031 | -0.046436 | 0.030067 | -0.12817 | 0.1831 | -0.46692 | 0.52643 | 0.31586 | -3.7994 | 0.53101 | 0.70496 | 0.79651 | -123.0515 | 122.1954 | -0.48523 | 122.5342 | 123.1888 | -0.35248 | -0.3891 | 0.12817 | 0.33874 | 123.1934 | 123.3673 | 122.9782 | 122.8455 | 122.5342 | 123.4589 | 118.8629 | -0.3891 | 122.8455 | 122.5342 | 118.8629 | 122.9782 | 123.4589 | -1.1353 | -123.7198
1350.9219 | 123.436 | -122.6807 | 0.65918 | 0.073345 | 0.033017 | -0.028574 | 0.069639 | -0.062167 | -0.035755 | 0.03968 | -0.10529 | 0.20599 | -0.41657 | 0.54474 | 0.31586 | -3.9185 | 0.49896 | 0.72327 | 0.79651 | -123.0469 | 122.2641 | -0.45319 | 122.5754 | 123.2254 | -0.34332 | -0.36621 | 0.13733 | 0.31128 | 123.1796 | 123.4039 | 122.9965 | 122.8867 | 122.5754 | 123.4772 | 118.7622 | -0.36621 | 122.8867 | 122.5754 | 118.7622 | 122.9965 | 123.4772 | -1.0757 | -123.7061
1351.9844 | 123.3307 | -122.7448 | 0.6546 | -0.018208 | 0.052243 | -0.00080337 | 0.10489 | -0.058962 | -0.011188 | 0.02793 | -0.11444 | 0.23804 | -0.4715 | 0.71411 | 0.42572 | -4.216 | 0.38452 | 0.82398 | 0.7782 | -123.0606 | 122.2733 | -0.41657 | 122.6303 | 123.4589 | -0.22888 | -0.31586 | 0.1236 | 0.35706 | 123.1293 | 123.5687 | 123.1705 | 122.9828 | 122.6303 | 123.5229 | 118.5287 | -0.31586 | 122.9828 | 122.6303 | 118.5287 | 123.1705 | 123.5229 | -1.1261 | -123.7152
1352.9219 | 123.4451 | -122.6807 | 0.66834 | -0.048725 | 0.038357 | -0.043528 | 0.076048 | -0.055758 | -0.036823 | 0.036475 | -0.10529 | 0.21515 | -0.42572 | 0.51727 | 0.32044 | -4.0146 | 0.54016 | 0.70496 | 0.81482 | -123.0423 | 122.2549 | -0.45319 | 122.5754 | 123.1979 | -0.3479 | -0.36163 | 0.14648 | 0.32043 | 123.2208 | 123.3856 | 123.0011 | 122.8958 | 122.5754 | 123.4955 | 118.6661 | -0.36163 | 122.8958 | 122.5754 | 118.6661 | 123.0011 | 123.4955 | -1.0941 | -123.7106
1353.9844 | 123.3261 | -122.7264 | 0.6546 | 0.13438 | 0.039425 | 0.013082 | 0.10489 | -0.045077 | -0.020801 | 0.034339 | -0.16937 | 0.26093 | -0.48065 | 0.72327 | 0.45319 | -3.9322 | 0.37079 | 0.82855 | 0.7782 | -123.0698 | 122.2458 | -0.39368 | 122.5571 | 123.4497 | -0.20142 | -0.34332 | 0.1236 | 0.31128 | 123.0972 | 123.555 | 123.1796 | 122.9874 | 122.5571 | 123.5046 | 118.7942 | -0.34332 | 122.9874 | 122.5571 | 118.7942 | 123.1796 | 123.5046 | -1.1353 | -123.7244
1354.9219 | 123.4268 | -122.7081 | 0.63629 | 0.24119 | 0.021267 | -0.038187 | 0.062162 | -0.044009 | -0.035755 | 0.031135 | -0.1236 | 0.21973 | -0.44403 | 0.52185 | 0.32501 | -4.4312 | 0.49896 | 0.6958 | 0.81482 | -123.0652 | 122.2641 | -0.41656 | 122.5845 | 123.23 | -0.31128 | -0.35706 | 0.17853 | 0.32044 | 123.2071 | 123.4039 | 123.0331 | 122.9279 | 122.5845 | 123.5229 | 118.277 | -0.35706 | 122.9279 | 122.5845 | 118.277 | 123.0331 | 123.5229 | -1.0803 | -123.7015
1355.9844 | 123.3902 | -122.7173 | 0.64087 | 0.37852 | 0.040494 | -0.0018714 | 0.091001 | -0.062167 | -0.01012 | 0.031135 | -0.33417 | 0.26093 | -0.46234 | 0.63171 | 0.41657 | -4.3991 | 0.41657 | 0.77362 | 0.79193 | -123.0469 | 122.2549 | -0.37994 | 122.3831 | 123.349 | -0.2243 | -0.32959 | 0.15106 | 0.12817 | 123.1339 | 123.4909 | 123.1339 | 122.9782 | 122.3831 | 123.5092 | 118.3182 | -0.32959 | 122.9782 | 122.3831 | 118.3182 | 123.1339 | 123.5092 | -1.1032 | -123.6877
1356.9219 | 123.4772 | -122.7219 | 0.6134 | 0.50059 | 0.029812 | -0.026438 | 0.079252 | -0.061099 | -0.022938 | 0.032203 | -0.054932 | 0.21515 | -0.45319 | 0.48981 | 0.28381 | -4.5776 | 0.5722 | 0.64545 | 0.80109 | -123.0881 | 122.2687 | -0.39825 | 122.6669 | 123.2117 | -0.32959 | -0.36621 | 0.18768 | 0.39825 | 123.2941 | 123.3673 | 123.0057 | 122.937 | 122.6669 | 123.5229 | 118.1442 | -0.36621 | 122.937 | 122.6669 | 118.1442 | 123.0057 | 123.5229 | -1.0666 | -123.7015
1357.9844 | 123.4726 | -122.6715 | 0.64545 | 0.43956 | 0.043698 | -0.010416 | 0.074979 | -0.052554 | -0.013325 | 0.031135 | -0.054932 | 0.21515 | -0.44861 | 0.52185 | 0.25177 | -4.5868 | 0.58594 | 0.67749 | 0.84686 | -123.0972 | 122.2229 | -0.4303 | 122.6166 | 123.1934 | -0.39368 | -0.42572 | 0.20142 | 0.39368 | 123.2574 | 123.349 | 122.9233 | 122.8867 | 122.6166 | 123.5184 | 118.0847 | -0.42572 | 122.8867 | 122.6166 | 118.0847 | 122.9233 | 123.5184 | -1.0941 | -123.7427
1358.9219 | 123.4406 | -122.6898 | 0.63171 | 0.30223 | 0.029812 | -0.010416 | 0.072843 | -0.055758 | -0.022938 | 0.047157 | -0.10071 | 0.21057 | -0.45776 | 0.50812 | 0.27466 | -4.6738 | 0.55389 | 0.68207 | 0.81482 | -123.0652 | 122.2321 | -0.42114 | 122.5891 | 123.1979 | -0.35706 | -0.37537 | 0.1831 | 0.35706 | 123.2437 | 123.3719 | 122.9645 | 122.9004 | 122.5891 | 123.5046 | 118.0161 | -0.37537 | 122.9004 | 122.5891 | 118.0161 | 122.9645 | 123.5046 | -1.0895 | -123.6969
1359.9844 | 123.4543 | -122.699 | 0.65002 | 0.48533 | 0.038357 | -0.013621 | 0.078184 | -0.051486 | -0.025074 | 0.04502 | -0.091553 | 0.23804 | -0.46692 | 0.58594 | 0.30212 | -4.5822 | 0.52643 | 0.71411 | 0.80109 | -123.0606 | 122.2321 | -0.41199 | 122.6074 | 123.2849 | -0.3479 | -0.36163 | 0.15106 | 0.37537 | 123.2254 | 123.4131 | 123.0011 | 122.937 | 122.6074 | 123.5001 | 118.1168 | -0.36163 | 122.937 | 122.6074 | 118.1168 | 123.0011 | 123.5001 | -1.1169 | -123.7106
1360.9219 | 123.4268 | -122.7127 | 0.63629 | 0.33274 | 0.03088 | -0.0082804 | 0.084592 | -0.053622 | -0.031483 | 0.033271 | -0.086975 | 0.20599 | -0.44403 | 0.49439 | 0.24719 | -4.6646 | 0.55389 | 0.68665 | 0.8194 | -123.0835 | 122.2687 | -0.4303 | 122.6257 | 123.2071 | -0.3891 | -0.37079 | 0.18311 | 0.35706 | 123.2666 | 123.3994 | 122.9599 | 122.9187 | 122.6257 | 123.5321 | 118.0481 | -0.37079 | 122.9187 | 122.6257 | 118.0481 | 122.9599 | 123.5321 | -1.0803 | -123.7198
1361.9844 | 123.3856 | -122.7356 | 0.64087 | -0.36916 | 0.044766 | -0.013621 | 0.086729 | -0.05469 | -0.015461 | 0.025794 | -0.15106 | 0.2655 | -0.45319 | 0.64087 | 0.36621 | -4.3945 | 0.42114 | 0.7782 | 0.77362 | -123.0743 | 122.2824 | -0.37537 | 122.5845 | 123.3765 | -0.27466 | -0.33875 | 0.13275 | 0.30212 | 123.1567 | 123.5138 | 123.1018 | 123.0011 | 122.5845 | 123.5092 | 118.3411 | -0.33875 | 123.0011 | 122.5845 | 118.3411 | 123.1018 | 123.5092 | -1.0941 | -123.7152
1362.9219 | 123.4818 | -122.6624 | 0.62256 | 0.51585 | 0.035153 | 0.0259 | 0.084592 | -0.055758 | -0.0090524 | 0.041816 | -0.073242 | 0.20599 | -0.44861 | 0.50812 | 0.24719 | -4.5273 | 0.56763 | 0.66834 | 0.8194 | -123.0927 | 122.2137 | -0.41656 | 122.5891 | 123.1705 | -0.37537 | -0.4303 | 0.19684 | 0.37537 | 123.23 | 123.3307 | 122.9095 | 122.8683 | 122.5891 | 123.4818 | 118.1351 | -0.4303 | 122.8683 | 122.5891 | 118.1351 | 122.9095 | 123.4818 | -1.0712 | -123.7152
1363.9844 | 123.3627 | -122.7127 | 0.6546 | 0.18016 | 0.050107 | -0.0040084 | 0.095274 | -0.044009 | -0.0026434 | 0.037543 | -0.12817 | 0.24261 | -0.48523 | 0.68207 | 0.37079 | -4.5136 | 0.42114 | 0.81024 | 0.78735 | -123.0606 | 122.2275 | -0.41199 | 122.5845 | 123.3948 | -0.28381 | -0.3479 | 0.13275 | 0.35706 | 123.1339 | 123.523 | 123.0835 | 122.9553 | 122.5845 | 123.5001 | 118.1992 | -0.3479 | 122.9553 | 122.5845 | 118.1992 | 123.0835 | 123.5001 | -1.1398 | -123.7152
1364.9219 | 123.3994 | -122.7081 | 0.64545 | 0.348 | 0.040494 | -0.033915 | 0.070707 | -0.035464 | -0.019733 | 0.034339 | -0.14191 | 0.24719 | -0.49439 | 0.61798 | 0.27466 | -4.6326 | 0.45776 | 0.75989 | 0.80109 | -123.0789 | 122.2137 | -0.39826 | 122.5662 | 123.3261 | -0.37079 | -0.37079 | 0.15564 | 0.35248 | 123.1659 | 123.468 | 122.9828 | 122.9553 | 122.5662 | 123.5092 | 118.0756 | -0.37079 | 122.9553 | 122.5662 | 118.0756 | 122.9828 | 123.5092 | -1.1398 | -123.7244
1365.9844 | 123.3444 | -122.7036 | 0.68665 | 0.22593 | 0.04797 | -0.013621 | 0.084592 | -0.05469 | -0.00050737 | 0.032203 | -0.15106 | 0.24719 | 0.71869 | 0.68665 | 0.37537 | -4.5868 | 0.41657 | 0.85602 | 0.78735 | -123.0423 | 123.4222 | -0.43945 | 122.5525 | 123.3902 | -0.31128 | -0.33875 | 0.10071 | -0.86975 | 123.1201 | 123.5596 | 123.0789 | 122.9507 | 122.5525 | 123.4909 | 118.1168 | -0.33875 | 122.9507 | 122.5525 | 118.1168 | 123.0789 | 123.4909 | 0.032043 | -123.7289
1366.9219 | 123.4863 | -122.6807 | 0.65002 | 0.63792 | 0.04263 | -0.011485 | 0.079252 | -0.047213 | -0.026142 | 0.041816 | -0.059509 | 0.2243 | -0.43945 | 0.5127 | 0.29755 | -4.6143 | 0.59509 | 0.69122 | 0.84228 | -123.056 | 122.2412 | -0.42572 | 122.6212 | 123.1934 | -0.35248 | -0.37537 | 0.19226 | 0.37994 | 123.2758 | 123.3719 | 122.9782 | 122.905 | 122.6212 | 123.5229 | 118.0664 | -0.37537 | 122.905 | 122.6212 | 118.0664 | 122.9782 | 123.5229 | -1.0895 | -123.7061
1367.9844 | 123.3765 | -122.6944 | 0.70496 | 0.39378 | 0.04263 | -0.021098 | 0.088865 | -0.055758 | -0.0058484 | 0.061042 | -0.14191 | 0.27466 | -0.4715 | 0.87433 | 0.31586 | -4.7104 | 0.45319 | 0.91095 | 0.81482 | -123.0515 | 122.2229 | -0.4303 | 122.5525 | 123.5687 | -0.3891 | -0.35706 | 0.10986 | 0.32959 | 123.1476 | 123.6053 | 123.0103 | 122.9691 | 122.5525 | 123.5092 | 117.984 | -0.35706 | 122.9691 | 122.5525 | 117.984 | 123.0103 | 123.5092 | -1.1765 | -123.7564
1368.9219 | 123.3673 | -122.7402 | 0.66834 | 0.19541 | 0.039425 | -0.02537 | 0.078184 | -0.045077 | -0.014393 | 0.037543 | -0.022888 | 0.27008 | -0.46692 | 0.67749 | 0.39825 | -4.6143 | 0.44403 | 0.8194 | 0.80109 | -123.0743 | 122.2733 | -0.39825 | 122.7173 | 123.4177 | -0.27008 | -0.33417 | 0.13275 | 0.44403 | 123.1842 | 123.5596 | 123.1384 | 123.0103 | 122.7173 | 123.5413 | 118.1259 | -0.33417 | 123.0103 | 122.7173 | 118.1259 | 123.1384 | 123.5413 | -1.1353 | -123.7427
1369.9844 | 123.4177 | -122.7219 | 0.65918 | 0.027569 | 0.046902 | -0.0072124 | 0.094205 | -0.042941 | -0.01012 | 0.032203 | -0.1236 | 0.27466 | -0.48981 | 0.62714 | 0.35706 | -4.747 | 0.45776 | 0.77362 | 0.81482 | -123.0743 | 122.2321 | -0.38452 | 122.5983 | 123.349 | -0.30212 | -0.35248 | 0.15564 | 0.36621 | 123.1796 | 123.4955 | 123.0789 | 122.9965 | 122.5983 | 123.5367 | 117.9749 | -0.35248 | 122.9965 | 122.5983 | 117.9749 | 123.0789 | 123.5367 | -1.149 | -123.7335
1370.9219 | 123.3444 | -122.731 | 0.68665 | 0.31749 | 0.04797 | -0.018961 | 0.082456 | -0.0376 | -0.011188 | 0.030067 | -0.15106 | 0.27466 | -0.50354 | 0.67291 | 0.41657 | -4.8706 | 0.4303 | 0.85144 | 0.80109 | -123.0286 | 122.2275 | -0.41199 | 122.58 | 123.4039 | -0.27008 | -0.29755 | 0.11444 | 0.35248 | 123.1613 | 123.5825 | 123.1476 | 123.0057 | 122.58 | 123.5321 | 117.8604 | -0.29755 | 123.0057 | 122.58 | 117.8604 | 123.1476 | 123.5321 | -1.1902 | -123.7152
1371.9844 | 123.3719 | -122.7356 | 0.66376 | 0.31749 | 0.040494 | -0.0061444 | 0.070707 | -0.039736 | -0.022938 | 0.04502 | -0.15106 | 0.25635 | -0.48981 | 0.61798 | 0.36621 | -4.8798 | 0.40283 | 0.83771 | 0.79193 | -123.0606 | 122.2458 | -0.40741 | 122.5845 | 123.3536 | -0.29755 | -0.32501 | 0.12817 | 0.33874 | 123.1384 | 123.5733 | 123.1018 | 122.9919 | 122.5845 | 123.5275 | 117.8558 | -0.32501 | 122.9919 | 122.5845 | 117.8558 | 123.1018 | 123.5275 | -1.1536 | -123.7244
1372.9219 | 123.3948 | -122.7402 | 0.66834 | 0.37852 | 0.053311 | -0.00080337 | 0.083524 | -0.025851 | -0.016529 | 0.036475 | -0.13275 | 0.24719 | -0.48981 | 0.50354 | 0.51727 | -4.6646 | 0.35248 | 0.80566 | 0.80566 | -123.0835 | 122.2504 | -0.42114 | 122.6074 | 123.2437 | -0.15106 | -0.34332 | 0.13733 | 0.35706 | 123.0927 | 123.5458 | 123.2574 | 122.9874 | 122.6074 | 123.5458 | 118.0756 | -0.34332 | 122.9874 | 122.6074 | 118.0756 | 123.2574 | 123.5458 | -1.1581 | -123.7518
1373.9844 | 123.381 | -122.7356 | 0.65002 | -0.14028 | 0.046902 | -0.020029 | 0.077116 | -0.049349 | -0.0069164 | 0.040748 | -0.15564 | 0.28839 | -0.48981 | 0.64087 | 0.37079 | -4.6875 | 0.40741 | 0.80109 | 0.80566 | -123.0835 | 122.2458 | -0.36163 | 122.58 | 123.3765 | -0.27924 | -0.3479 | 0.15564 | 0.33417 | 123.143 | 123.5367 | 123.1064 | 123.024 | 122.58 | 123.5413 | 118.0481 | -0.3479 | 123.024 | 122.58 | 118.0481 | 123.1064 | 123.5413 | -1.1398 | -123.7335
1374.9219 | 123.349 | -122.7722 | 0.66376 | 0.25645 | 0.056515 | 0.0024006 | 0.094205 | -0.041873 | -0.014393 | 0.03968 | -0.16479 | 0.26093 | -0.5127 | 0.66834 | 0.39368 | -4.7699 | 0.41199 | 0.82855 | 0.75989 | -123.0789 | 122.2595 | -0.40283 | 122.6074 | 123.4406 | -0.27008 | -0.3067 | 0.096131 | 0.3479 | 123.1842 | 123.6008 | 123.1659 | 123.0331 | 122.6074 | 123.5321 | 118.0023 | -0.3067 | 123.0331 | 122.6074 | 118.0023 | 123.1659 | 123.5321 | -1.1765 | -123.7427
1375.9844 | 123.3719 | -122.7448 | 0.66376 | 0.33274 | 0.039425 | 0.0034686 | 0.077116 | -0.044009 | -0.022938 | 0.02793 | -0.16022 | 0.25635 | -0.50812 | 0.6546 | 0.40741 | -4.7882 | 0.41199 | 0.84686 | 0.81024 | -123.0789 | 122.2366 | -0.40741 | 122.5845 | 123.3994 | -0.25635 | -0.33417 | 0.14648 | 0.3479 | 123.1567 | 123.5916 | 123.1522 | 123.0011 | 122.5845 | 123.555 | 117.9565 | -0.33417 | 123.0011 | 122.5845 | 117.9565 | 123.1522 | 123.555 | -1.1719 | -123.7427
1376.9219 | 123.3856 | -122.7631 | 0.63171 | -0.033467 | 0.041562 | -0.020029 | 0.083524 | -0.03226 | -0.0069164 | 0.037543 | -0.1236 | 0.25177 | -0.49896 | 0.62714 | 0.3479 | -5.0491 | 0.41199 | 0.7782 | 0.77362 | -123.1155 | 122.2641 | -0.37994 | 122.6395 | 123.3902 | -0.28381 | -0.35248 | 0.14191 | 0.37537 | 123.175 | 123.5413 | 123.111 | 123.0148 | 122.6395 | 123.5367 | 117.7139 | -0.35248 | 123.0148 | 122.6395 | 117.7139 | 123.111 | 123.5367 | -1.1307 | -123.7473
1377.9844 | 123.3994 | -122.7173 | 0.6546 | -0.26235 | 0.044766 | -0.018961 | 0.08032 | -0.041873 | -0.02187 | 0.051429 | -0.13275 | 0.24719 | -0.50354 | 0.59052 | 0.34332 | -4.9942 | 0.44403 | 0.7782 | 0.80566 | -123.0789 | 122.2137 | -0.40741 | 122.5845 | 123.3078 | -0.31128 | -0.36163 | 0.15106 | 0.37079 | 123.1613 | 123.4955 | 123.0606 | 122.9645 | 122.5845 | 123.5229 | 117.7231 | -0.36163 | 122.9645 | 122.5845 | 117.7231 | 123.0606 | 123.5229 | -1.1581 | -123.7335
1378.9219 | 123.3719 | -122.6578 | 0.74616 | 0.36326 | 0.049038 | -0.0050764 | 0.081388 | -0.044009 | -0.015461 | 0.033271 | -0.16479 | 0.27466 | -0.48981 | 0.73242 | 0.47607 | -4.8294 | 0.48981 | 0.91095 | 0.86975 | -123.0057 | 122.168 | -0.4715 | 122.493 | 123.3902 | -0.27008 | -0.3479 | 0.1236 | 0.32501 | 123.1476 | 123.5687 | 123.1338 | 122.9324 | 122.493 | 123.5275 | 117.8284 | -0.3479 | 122.9324 | 122.493 | 117.8284 | 123.1338 | 123.5275 | -1.236 | -123.7518
1379.9844 | 123.4726 | -122.6257 | 0.73242 | 0.54637 | 0.04263 | -0.021098 | 0.067503 | -0.038668 | -0.0069164 | 0.040748 | -0.11444 | 0.23346 | -0.48523 | 0.62256 | 0.41199 | -4.6463 | 0.62256 | 0.81482 | 0.90637 | -122.9965 | 122.1405 | -0.49896 | 122.5113 | 123.2483 | -0.32044 | -0.37079 | 0.17395 | 0.37079 | 123.2483 | 123.4406 | 123.0377 | 122.8592 | 122.5113 | 123.5321 | 117.9794 | -0.37079 | 122.8592 | 122.5113 | 117.9794 | 123.0377 | 123.5321 | -1.2177 | -123.7289
1380.9219 | 123.3627 | -122.644 | 0.75073 | 0.24119 | 0.057583 | -0.011485 | 0.088865 | -0.046145 | -0.0079844 | 0.03968 | -0.14191 | 0.27466 | -0.49896 | 0.76904 | 0.5127 | -4.5959 | 0.50354 | 0.93384 | 0.87433 | -122.9645 | 122.1451 | -0.47607 | 122.5021 | 123.4131 | -0.23804 | -0.32044 | 0.1236 | 0.35706 | 123.1476 | 123.5779 | 123.1567 | 122.9187 | 122.5021 | 123.5184 | 118.0481 | -0.32044 | 122.9187 | 122.5021 | 118.0481 | 123.1567 | 123.5184 | -1.2497 | -123.7152
1381.9844 | 123.4177 | -122.6349 | 0.75531 | -0.38442 | 0.027676 | -0.016825 | 0.065366 | -0.042941 | -0.020801 | 0.049293 | -0.12817 | 0.25177 | -0.49439 | 0.64087 | 0.41199 | -4.5593 | 0.58136 | 0.87433 | 0.93384 | -122.9691 | 122.1405 | -0.50354 | 122.5067 | 123.2758 | -0.34332 | -0.33417 | 0.17853 | 0.36621 | 123.2162 | 123.5092 | 123.0469 | 122.8867 | 122.5067 | 123.5687 | 118.0756 | -0.33417 | 122.8867 | 122.5067 | 118.0756 | 123.0469 | 123.5687 | -1.2497 | -123.7244
1382.9219 | 123.3673 | -122.6624 | 0.76446 | 0.073345 | 0.04263 | -0.013621 | 0.091001 | -0.047213 | -0.00050737 | 0.034339 | -0.11444 | 0.26093 | -0.50354 | 0.75989 | 0.5127 | -4.4037 | 0.53101 | 0.91095 | 0.90637 | -122.9828 | 122.1588 | -0.50354 | 122.5479 | 123.4222 | -0.25177 | -0.32043 | 0.14191 | 0.3891 | 123.1934 | 123.5733 | 123.175 | 122.9233 | 122.5479 | 123.5687 | 118.2587 | -0.32043 | 122.9233 | 122.5479 | 118.2587 | 123.175 | 123.5687 | -1.268 | -123.7473
1383.9844 | 123.3948 | -122.7356 | 0.68207 | 0.042827 | 0.051175 | -0.015757 | 0.093137 | -0.038668 | -0.014393 | 0.03968 | -0.11902 | 0.26093 | -0.47607 | 0.6546 | 0.39368 | -4.3945 | 0.4303 | 0.8194 | 0.80109 | -123.1064 | 122.2595 | -0.42114 | 122.6166 | 123.3902 | -0.28839 | -0.37079 | 0.11902 | 0.35706 | 123.1659 | 123.555 | 123.1293 | 122.9965 | 122.6166 | 123.5367 | 118.3411 | -0.37079 | 122.9965 | 122.6166 | 118.3411 | 123.1293 | 123.5367 | -1.1581 | -123.7885
1384.9219 | 123.468 | -122.6532 | 0.67749 | 0.13438 | 0.015927 | -0.051005 | 0.058958 | -0.039736 | -0.032551 | 0.046088 | -0.16022 | 0.21515 | -0.45776 | 0.59052 | 0.42114 | -4.6143 | 0.32501 | 0.73242 | 0.91553 | -123.0698 | 122.1954 | -0.46234 | 122.493 | 123.2437 | -0.25635 | -0.41656 | 0.23804 | 0.29755 | 122.9782 | 123.3856 | 123.0743 | 122.8683 | 122.493 | 123.5687 | 118.0389 | -0.41656 | 122.8683 | 122.493 | 118.0389 | 123.0743 | 123.5687 | -1.1353 | -123.7473
1385.9844 | 123.3719 | -122.6395 | 0.77362 | -0.38442 | 0.02554 | -0.028574 | 0.077116 | -0.049349 | -0.029346 | 0.034339 | -0.14648 | 0.25635 | -0.47607 | 0.66376 | 0.5127 | -4.1519 | 0.49896 | 0.88348 | 0.88348 | -122.9782 | 122.1634 | -0.51727 | 122.493 | 123.3032 | -0.26093 | -0.33875 | 0.10986 | 0.32959 | 123.1384 | 123.5229 | 123.1522 | 122.8958 | 122.493 | 123.5229 | 118.4875 | -0.33875 | 122.8958 | 122.493 | 118.4875 | 123.1522 | 123.5229 | -1.2497 | -123.7518
1386.9219 | 123.3444 | -122.6166 | 0.76904 | 0.10386 | 0.040494 | -0.023234 | 0.093137 | -0.046145 | -0.0015754 | 0.036475 | -0.12817 | 0.24719 | -0.46692 | 0.7782 | 0.49439 | -4.0421 | 0.50354 | 0.93842 | 0.88806 | -122.9965 | 122.1497 | -0.52185 | 122.4884 | 123.3948 | -0.27466 | -0.37994 | 0.11902 | 0.33874 | 123.1201 | 123.555 | 123.111 | 122.8638 | 122.4884 | 123.5046 | 118.5745 | -0.37994 | 122.8638 | 122.4884 | 118.5745 | 123.111 | 123.5046 | -1.236 | -123.7656
1387.9844 | 123.4177 | -122.6395 | 0.74158 | -0.20131 | 0.04263 | -0.028574 | 0.081388 | -0.052554 | -0.019733 | 0.038612 | -0.13733 | 0.24719 | -0.50354 | 0.6958 | 0.43945 | -4.2389 | 0.52643 | 0.87891 | 0.89264 | -122.9965 | 122.1359 | -0.49439 | 122.5021 | 123.3353 | -0.30212 | -0.35706 | 0.15106 | 0.36621 | 123.1659 | 123.5184 | 123.0789 | 122.8867 | 122.5021 | 123.5321 | 118.4006 | -0.35706 | 122.8867 | 122.5021 | 118.4006 | 123.0789 | 123.5321 | -1.2451 | -123.7381
1388.9219 | 123.4222 | -122.6257 | 0.74616 | -0.12502 | 0.043698 | -0.014689 | 0.089933 | -0.048281 | -0.019733 | 0.031135 | -0.086975 | 0.26093 | -0.48523 | 0.71411 | 0.48065 | -4.3213 | 0.55389 | 0.86975 | 0.9201 | -123.0057 | 122.1405 | -0.48523 | 122.5388 | 123.3398 | -0.2655 | -0.37994 | 0.17395 | 0.39825 | 123.1796 | 123.4955 | 123.1064 | 122.8867 | 122.5388 | 123.5458 | 118.3044 | -0.37994 | 122.8867 | 122.5388 | 118.3044 | 123.1064 | 123.5458 | -1.2314 | -123.7518
1389.9844 | 123.3627 | -122.6624 | 0.76904 | 0.22593 | 0.037289 | -0.0029404 | 0.083524 | -0.048281 | -0.0090524 | 0.033271 | -0.13733 | 0.2655 | -0.48523 | 0.76446 | 0.5127 | -4.216 | 0.53558 | 0.93384 | 0.90179 | -122.9919 | 122.1771 | -0.50354 | 122.525 | 123.4268 | -0.25635 | -0.32959 | 0.13275 | 0.3479 | 123.1979 | 123.5962 | 123.175 | 122.9279 | 122.525 | 123.5641 | 118.4464 | -0.32959 | 122.9279 | 122.525 | 118.4464 | 123.175 | 123.5641 | -1.2543 | -123.761
1390.9219 | 123.4085 | -122.6395 | 0.77362 | -0.21657 | 0.051175 | -0.027506 | 0.072843 | -0.041873 | -0.016529 | 0.035407 | -0.11444 | 0.2655 | -0.50812 | 0.70038 | 0.48523 | -4.3259 | 0.56763 | 0.89264 | 0.91095 | -123.0011 | 122.1313 | -0.50812 | 122.525 | 123.3398 | -0.28839 | -0.36163 | 0.13733 | 0.39368 | 123.2071 | 123.5321 | 123.1247 | 122.905 | 122.525 | 123.5504 | 118.3136 | -0.36163 | 122.905 | 122.525 | 118.3136 | 123.1247 | 123.5504 | -1.2817 | -123.7747
1391.9844 | 123.3948 | -122.6166 | 0.77362 | -0.39968 | 0.020199 | -0.022166 | 0.062162 | -0.042941 | -0.028278 | 0.040748 | -0.12817 | 0.24719 | -0.48065 | 0.65918 | 0.45319 | -4.2435 | 0.56305 | 0.87433 | 0.94299 | -122.9599 | 122.1359 | -0.52643 | 122.4884 | 123.2758 | -0.32044 | -0.34332 | 0.16937 | 0.35248 | 123.1796 | 123.4909 | 123.0698 | 122.8638 | 122.4884 | 123.5596 | 118.3731 | -0.34332 | 122.8638 | 122.4884 | 118.3731 | 123.0698 | 123.5596 | -1.2543 | -123.7335
1392.9219 | 123.3765 | -122.6486 | 0.74158 | 0.058086 | 0.04263 | -0.028574 | 0.081388 | -0.045077 | -0.013325 | 0.031135 | -0.11444 | 0.24261 | -0.49439 | 0.75531 | 0.50354 | -4.3121 | 0.52185 | 0.89264 | 0.89264 | -123.024 | 122.1542 | -0.49896 | 122.5342 | 123.4039 | -0.23804 | -0.37537 | 0.15106 | 0.37994 | 123.1705 | 123.5413 | 123.1522 | 122.8912 | 122.5342 | 123.5413 | 118.3365 | -0.37537 | 122.8912 | 122.5342 | 118.3365 | 123.1522 | 123.5413 | -1.236 | -123.7656
1393.9844 | 123.3719 | -122.6898 | 0.74616 | -0.32338 | 0.038357 | -0.029642 | 0.084592 | -0.036532 | -0.020801 | 0.040748 | -0.14191 | 0.2655 | -0.4715 | 0.71869 | 0.4715 | -4.303 | 0.48981 | 0.91095 | 0.90637 | -122.9965 | 122.2183 | -0.48065 | 122.5479 | 123.4085 | -0.27466 | -0.3067 | 0.16022 | 0.32959 | 123.1796 | 123.6008 | 123.1613 | 122.9553 | 122.5479 | 123.5962 | 118.3868 | -0.3067 | 122.9553 | 122.5479 | 118.3868 | 123.1613 | 123.5962 | -1.2177 | -123.7427
1394.9219 | 123.5687 | -122.6486 | 0.737 | 0.22593 | 0.033017 | -0.0093484 | 0.04614 | -0.045077 | -0.032551 | 0.033271 | -0.19226 | 0.21057 | -0.5127 | 0.6134 | 0.41657 | -4.5364 | 0.59967 | 0.81482 | 0.91095 | -123.024 | 122.1359 | -0.52643 | 122.4564 | 123.262 | -0.32043 | -0.37537 | 0.17395 | 0.32043 | 123.2483 | 123.4634 | 123.0652 | 122.8592 | 122.4564 | 123.5596 | 118.1122 | -0.37537 | 122.8592 | 122.4564 | 118.1122 | 123.0652 | 123.5596 | -1.2497 | -123.761
1395.9844 | 123.4772 | -122.6028 | 0.737 | -0.32338 | 0.024472 | -0.027506 | 0.053617 | -0.060031 | -0.034687 | 0.04502 | -0.27008 | 0.20142 | -0.63629 | 0.58136 | 0.37994 | -4.2343 | 0.61798 | 0.77362 | 0.94299 | -123.0103 | 121.9666 | -0.53558 | 122.3328 | 123.1842 | -0.35706 | -0.40741 | 0.20599 | 0.36621 | 123.2208 | 123.3765 | 122.9828 | 122.8043 | 122.3328 | 123.5458 | 118.3685 | -0.40741 | 122.8043 | 122.3328 | 118.3685 | 122.9828 | 123.5458 | -1.3733 | -123.7473
1396.9219 | 123.3765 | -122.6624 | 0.7782 | -0.29287 | 0.028744 | -0.022166 | 0.066434 | -0.047213 | -0.030414 | 0.036475 | -0.63171 | 0.25635 | -0.97504 | 0.71411 | 0.46692 | -4.0329 | 0.5127 | 0.91553 | 0.90637 | -122.9828 | 121.6873 | -0.52185 | 122.0306 | 123.3765 | -0.31128 | -0.32043 | 0.12817 | 0.34332 | 123.175 | 123.5779 | 123.1293 | 122.9187 | 122.0306 | 123.5687 | 118.6295 | -0.32043 | 122.9187 | 122.0306 | 118.6295 | 123.1293 | 123.5687 | -1.7532 | -123.761
1397.9844 | 123.349 | -122.6578 | 0.76446 | 0.83628 | 0.045834 | -0.015757 | 0.089933 | -0.047213 | -0.00050737 | 0.032203 | -1.4328 | 0.27008 | -1.7761 | 0.78278 | 0.18768 | -4.216 | 0.5127 | 0.90637 | 0.90637 | -122.9874 | 120.8817 | -0.49438 | 121.225 | 123.4406 | -0.57678 | -0.32959 | 0.14191 | 0.34332 | 123.1705 | 123.5641 | 122.8455 | 122.9279 | 121.225 | 123.5641 | 118.4418 | -0.32959 | 122.9279 | 121.225 | 118.4418 | 122.8455 | 123.5641 | -2.5406 | -123.7518
1398.9219 | 123.3765 | -122.6807 | 0.75531 | -0.36916 | 0.031949 | -0.038187 | 0.077116 | -0.044009 | -0.018665 | 0.035407 | -1.4282 | 0.27008 | -1.7441 | 0.71411 | 0.45776 | -4.1977 | 0.49896 | 0.90179 | 0.9201 | -122.9874 | 120.9366 | -0.48523 | 121.2524 | 123.3948 | -0.29755 | -0.3067 | 0.16479 | 0.31586 | 123.1796 | 123.5825 | 123.1384 | 122.9507 | 121.2524 | 123.6008 | 118.483 | -0.3067 | 122.9507 | 121.2524 | 118.483 | 123.1384 | 123.6008 | -2.4994 | -123.7427
1399.9844 | 123.5138 | -122.6303 | 0.75989 | -0.12502 | 0.012723 | -0.029642 | 0.049345 | -0.053622 | -0.041096 | 0.043952 | -1.3687 | 0.24261 | -1.7075 | 0.57678 | 0.37994 | -4.2435 | 0.65002 | 0.76446 | 0.97961 | -122.9828 | 120.9229 | -0.51727 | 121.2616 | 123.2071 | -0.37994 | -0.35248 | 0.21973 | 0.33874 | 123.2803 | 123.3948 | 123.0103 | 122.8729 | 121.2616 | 123.6099 | 118.3868 | -0.35248 | 122.8729 | 121.2616 | 118.3868 | 123.0103 | 123.6099 | -2.4673 | -123.7427
1400.9219 | 123.3765 | -122.6898 | 0.77362 | -0.46071 | 0.036221 | -0.023234 | 0.083524 | -0.048281 | -0.025074 | 0.036475 | -1.4282 | 0.25635 | -1.7212 | 0.72327 | 0.47607 | -4.1611 | 0.48981 | 0.91553 | 0.87433 | -123.0103 | 120.9686 | -0.51727 | 121.2616 | 123.4131 | -0.29755 | -0.32044 | 0.10071 | 0.29297 | 123.1796 | 123.6053 | 123.1659 | 122.9462 | 121.2616 | 123.5641 | 118.5287 | -0.32044 | 122.9462 | 121.2616 | 118.5287 | 123.1659 | 123.5641 | -2.4948 | -123.7839
1401.9844 | 123.4634 | -122.6303 | 0.74616 | 0.33274 | 0.023404 | -0.0040084 | 0.062162 | -0.051486 | -0.032551 | 0.035407 | -1.3596 | 0.2243 | -1.7166 | 0.59967 | 0.39368 | -4.0375 | 0.58594 | 0.80109 | 0.90637 | -123.0148 | 120.9137 | -0.52185 | 121.2708 | 123.23 | -0.35248 | -0.38452 | 0.16022 | 0.35706 | 123.2162 | 123.4314 | 123.024 | 122.8546 | 121.2708 | 123.5367 | 118.5928 | -0.38452 | 122.8546 | 121.2708 | 118.5928 | 123.024 | 123.5367 | -2.4628 | -123.761
1402.9219 | 123.4268 | -122.6303 | 0.76446 | -0.39968 | 0.02554 | -0.021098 | 0.078184 | -0.050418 | -0.033619 | 0.041816 | -1.2726 | 0.21973 | -1.6388 | 0.65002 | 0.42114 | -3.9917 | 0.52643 | 0.83771 | 0.90637 | -123.0103 | 120.9915 | -0.54474 | 121.3577 | 123.2803 | -0.34332 | -0.37994 | 0.14191 | 0.36621 | 123.1567 | 123.468 | 123.0515 | 122.85 | 121.3577 | 123.5367 | 118.6386 | -0.37994 | 122.85 | 121.3577 | 118.6386 | 123.0515 | 123.5367 | -2.4033 | -123.7747
1403.9844 | 123.5046 | -122.612 | 0.74616 | -0.033467 | 0.016995 | -0.041392 | 0.05789 | -0.057894 | -0.033619 | 0.053565 | -1.3458 | 0.22888 | -1.6937 | 0.59967 | 0.38452 | -4.3396 | 0.6546 | 0.79651 | 0.93842 | -122.9828 | 120.9183 | -0.51727 | 121.2662 | 123.2117 | -0.36163 | -0.37079 | 0.19226 | 0.3479 | 123.2666 | 123.4085 | 122.9965 | 122.8409 | 121.2662 | 123.5504 | 118.2724 | -0.37079 | 122.8409 | 121.2662 | 118.2724 | 122.9965 | 123.5504 | -2.4399 | -123.7289
1404.9219 | 123.4909 | -122.6257 | 0.74158 | -1.4983 | 0.029812 | -0.013621 | 0.065366 | -0.062167 | -0.031483 | 0.038612 | -1.4145 | 0.19684 | -1.7441 | 0.5722 | 0.37079 | -4.5044 | 0.62714 | 0.76904 | 0.9201 | -123.056 | 120.8817 | -0.54474 | 121.2112 | 123.1979 | -0.37079 | -0.4303 | 0.17853 | 0.32959 | 123.2529 | 123.3948 | 122.9965 | 122.8226 | 121.2112 | 123.5458 | 118.1213 | -0.4303 | 122.8226 | 121.2112 | 118.1213 | 122.9965 | 123.5458 | -2.4857 | -123.7976
1405.9844 | 123.5046 | -122.6486 | 0.71411 | -0.079243 | 0.021267 | -0.032847 | 0.050413 | -0.062167 | -0.036823 | 0.035407 | -1.3824 | 0.21973 | -1.7212 | 0.56305 | 0.35248 | -4.2938 | 0.6134 | 0.74616 | 0.90179 | -123.0103 | 120.9274 | -0.49438 | 121.2662 | 123.2117 | -0.36163 | -0.36163 | 0.18768 | 0.33874 | 123.262 | 123.3948 | 123.0011 | 122.8683 | 121.2662 | 123.5504 | 118.3548 | -0.36163 | 122.8683 | 121.2662 | 118.3548 | 123.0011 | 123.5504 | -2.4353 | -123.7244
1406.9219 | 123.4863 | -122.6486 | 0.70496 | -0.3539 | 0.016995 | -0.026438 | 0.078184 | -0.062167 | -0.038959 | 0.038612 | -0.64545 | 0.21057 | -1.0345 | 0.58136 | 0.3479 | -4.3076 | 0.58136 | 0.75531 | 0.89264 | -123.0515 | 121.6141 | -0.49439 | 122.0032 | 123.23 | -0.35706 | -0.40283 | 0.18768 | 0.3891 | 123.23 | 123.4039 | 122.9965 | 122.8592 | 122.0032 | 123.5413 | 118.3411 | -0.40283 | 122.8592 | 122.0032 | 118.3411 | 122.9965 | 123.5413 | -1.7395 | -123.7564
1407.9844 | 123.4955 | -122.6761 | 0.67291 | 0.43956 | 0.028744 | -0.021098 | 0.08032 | -0.061099 | -0.02721 | 0.033271 | -1.4008 | 0.21973 | -1.767 | 0.5722 | 0.26093 | -4.3488 | 0.65002 | 0.68207 | 0.85144 | -123.0835 | 120.9091 | -0.45319 | 121.2753 | 123.2483 | -0.41199 | -0.40741 | 0.17853 | 0.36621 | 123.3261 | 123.3582 | 122.937 | 122.8958 | 121.2753 | 123.5275 | 118.3273 | -0.40741 | 122.8958 | 121.2753 | 118.3273 | 122.937 | 123.5275 | -2.4399 | -123.7564
1408.9219 | 123.3994 | -122.7081 | 0.74616 | -0.38442 | 0.024472 | -0.037119 | 0.076048 | -0.056826 | -0.036823 | 0.02793 | -1.442 | 0.24261 | -1.7853 | 0.71411 | 0.46234 | -4.2572 | 0.45319 | 0.84228 | 0.86975 | -123.0148 | 120.9229 | -0.50354 | 121.2662 | 123.4222 | -0.28381 | -0.3067 | 0.1236 | 0.34332 | 123.1613 | 123.5504 | 123.1705 | 122.9507 | 121.2662 | 123.5779 | 118.4509 | -0.3067 | 122.9507 | 121.2662 | 118.4509 | 123.1705 | 123.5779 | -2.5314 | -123.761
1409.9844 | 123.5229 | -122.6395 | 0.70038 | -0.048725 | 0.018063 | -0.033915 | 0.05789 | -0.067507 | -0.040028 | 0.030067 | -1.3504 | 0.22888 | -1.6754 | 0.54474 | 0.36621 | -4.3442 | 0.61798 | 0.72784 | 0.89722 | -123.024 | 120.9641 | -0.4715 | 121.2891 | 123.1842 | -0.33417 | -0.38452 | 0.19684 | 0.32501 | 123.2574 | 123.3673 | 123.0057 | 122.8683 | 121.2891 | 123.5367 | 118.2953 | -0.38452 | 122.8683 | 121.2891 | 118.2953 | 123.0057 | 123.5367 | -2.3758 | -123.7244
1410.9219 | 123.5138 | -122.644 | 0.72327 | -0.14028 | 0.022336 | -0.023234 | 0.073911 | -0.052554 | -0.049641 | 0.030067 | -1.0529 | 0.21973 | -1.3824 | 0.54016 | 0.34332 | -4.4312 | 0.6134 | 0.71411 | 0.89264 | -123.024 | 121.2616 | -0.50354 | 121.5912 | 123.1842 | -0.37994 | -0.37994 | 0.16937 | 0.32959 | 123.2574 | 123.3582 | 122.9874 | 122.8638 | 121.5912 | 123.5367 | 118.2129 | -0.37994 | 122.8638 | 121.5912 | 118.2129 | 122.9874 | 123.5367 | -2.1057 | -123.7473
1411.9844 | 123.4818 | -122.6486 | 0.6958 | 0.43956 | 0.031949 | -0.013621 | 0.081388 | -0.057894 | -0.02721 | 0.032203 | -1.4145 | 0.19684 | -1.8127 | 0.51727 | 0.34332 | -4.4952 | 0.63171 | 0.71411 | 0.86975 | -123.056 | 120.8359 | -0.49896 | 121.2341 | 123.1659 | -0.35248 | -0.40741 | 0.17395 | 0.39825 | 123.2803 | 123.3627 | 122.9919 | 122.8455 | 121.2341 | 123.5184 | 118.1534 | -0.40741 | 122.8455 | 121.2341 | 118.1534 | 122.9919 | 123.5184 | -2.5085 | -123.7518
1412.9219 | 123.4955 | -122.6212 | 0.75989 | 0.24119 | 0.028744 | -0.031779 | 0.067503 | -0.053622 | -0.038959 | 0.03968 | -1.593 | 0.1831 | -1.918 | 0.62256 | 0.39825 | -4.8523 | 0.62714 | 0.80109 | 0.94299 | -122.9965 | 120.7031 | -0.57678 | 121.0281 | 123.2437 | -0.36163 | -0.37537 | 0.1831 | 0.32501 | 123.2483 | 123.4222 | 123.0194 | 122.8043 | 121.0281 | 123.5641 | 117.7689 | -0.37537 | 122.8043 | 121.0281 | 117.7689 | 123.0194 | 123.5641 | -2.6779 | -123.7564
1413.9219 | 123.5413 | -122.6074 | 0.75531 | -0.018208 | 0.029812 | -0.015757 | 0.08032 | -0.069644 | -0.038959 | 0.04502 | -1.4374 | 0.21057 | -1.8082 | 0.57678 | 0.32959 | -4.9622 | 0.6958 | 0.76904 | 0.95673 | -123.0194 | 120.7993 | -0.54474 | 121.17 | 123.1842 | -0.42572 | -0.41199 | 0.20142 | 0.37079 | 123.3032 | 123.3765 | 122.937 | 122.818 | 121.17 | 123.5641 | 117.6453 | -0.41199 | 122.818 | 121.17 | 117.6453 | 122.937 | 123.5641 | -2.5635 | -123.7747
1414.9844 | 123.3856 | -122.6349 | 0.76904 | 0.21067 | 0.038357 | -0.024302 | 0.096342 | -0.049349 | -0.019733 | 0.032203 | -1.5335 | 0.24261 | -1.8951 | 0.8194 | 0.48981 | -4.9301 | 0.53558 | 0.91095 | 0.90637 | -122.9507 | 120.7397 | -0.52643 | 121.1014 | 123.4543 | -0.27924 | -0.31586 | 0.13733 | 0.36163 | 123.1705 | 123.5458 | 123.1247 | 122.8775 | 121.1014 | 123.5413 | 117.7048 | -0.31586 | 122.8775 | 121.1014 | 117.7048 | 123.1247 | 123.5413 | -2.6642 | -123.7198
1415.9219 | 123.4634 | -122.6349 | 0.67749 | 0.088604 | 0.027676 | -0.021098 | 0.066434 | -0.068576 | -0.033619 | 0.034339 | -1.5976 | 0.21973 | -1.886 | 0.62256 | 0.41199 | -5.2368 | 0.39368 | 0.737 | 0.88348 | -123.0789 | 120.7489 | -0.45776 | 121.0373 | 123.2574 | -0.2655 | -0.44403 | 0.20599 | 0.28839 | 123.0286 | 123.3719 | 123.0469 | 122.8546 | 121.0373 | 123.5184 | 117.3981 | -0.44403 | 122.8546 | 121.0373 | 117.3981 | 123.0469 | 123.5184 | -2.5635 | -123.7564
1416.9219 | 123.4497 | -122.6395 | 0.75073 | 0.18016 | 0.033017 | -0.02537 | 0.069639 | -0.052554 | -0.036823 | 0.047157 | -1.5518 | 0.2243 | -1.8585 | 0.62714 | 0.40283 | -4.9438 | 0.59509 | 0.78278 | 0.90637 | -123.0148 | 120.7809 | -0.52643 | 121.0876 | 123.2666 | -0.3479 | -0.37537 | 0.15564 | 0.3067 | 123.2346 | 123.4222 | 123.0423 | 122.8638 | 121.0876 | 123.5458 | 117.6956 | -0.37537 | 122.8638 | 121.0876 | 117.6956 | 123.0423 | 123.5458 | -2.6093 | -123.7656
1417.9844 | 123.5413 | -122.644 | 0.7782 | 0.28697 | 0.045834 | -0.011485 | 0.093137 | -0.05469 | -0.018665 | 0.024726 | -1.5656 | 0.26093 | -1.9089 | 0.77362 | 0.50812 | -4.8431 | 0.48981 | 1.0345 | 0.87891 | -122.9416 | 120.7352 | -0.51727 | 121.0785 | 123.4177 | -0.27008 | -0.29755 | 0.10071 | 0.34332 | 123.1338 | 123.6786 | 123.1522 | 122.905 | 121.0785 | 123.5229 | 117.8009 | -0.29755 | 122.905 | 121.0785 | 117.8009 | 123.1522 | 123.5229 | -2.6871 | -123.7198
1418.9219 | 123.4909 | -122.6303 | 0.72784 | -1.8798 | 0.02554 | -0.026438 | 0.072843 | -0.053622 | -0.028278 | 0.040748 | -1.506 | 0.16937 | -1.8677 | 0.60425 | 0.37994 | -4.8065 | 0.64545 | 0.74616 | 0.90179 | -123.024 | 120.7626 | -0.55847 | 121.1243 | 123.2346 | -0.3479 | -0.39368 | 0.17395 | 0.36163 | 123.2758 | 123.3765 | 123.0103 | 122.7997 | 121.1243 | 123.5321 | 117.8238 | -0.39368 | 122.7997 | 121.1243 | 117.8238 | 123.0103 | 123.5321 | -2.5955 | -123.7518
1419.9219 | 123.4772 | -122.6257 | 0.69122 | 0.348 | 0.028744 | -0.0093484 | 0.066434 | -0.053622 | -0.025074 | 0.040748 | -1.474 | 0.21515 | -1.8265 | 0.59509 | 0.37994 | -4.8386 | 0.63171 | 0.75531 | 0.88348 | -123.0377 | 120.7993 | -0.47607 | 121.1517 | 123.2208 | -0.31128 | -0.41199 | 0.19226 | 0.35248 | 123.2574 | 123.381 | 123.0057 | 122.8409 | 121.1517 | 123.5092 | 117.7872 | -0.41199 | 122.8409 | 121.1517 | 117.7872 | 123.0057 | 123.5092 | -2.5177 | -123.7289
1420.9844 | 123.4268 | -122.7081 | 0.70496 | 0.25645 | 0.038357 | -0.0072124 | 0.084592 | -0.061099 | -0.012257 | 0.031135 | -1.4694 | 0.29755 | -1.7944 | 0.70953 | 0.43945 | -4.7974 | 0.49439 | 0.81482 | 0.85602 | -123.0469 | 120.9137 | -0.40741 | 121.2387 | 123.4177 | -0.2655 | -0.33875 | 0.15106 | 0.32501 | 123.2025 | 123.5229 | 123.1476 | 123.0057 | 121.2387 | 123.5641 | 117.9108 | -0.33875 | 123.0057 | 121.2387 | 117.9108 | 123.1476 | 123.5641 | -2.4994 | -123.7518
1421.9219 | 123.4863 | -122.6166 | 0.72327 | 0.36326 | 0.040494 | -0.012553 | 0.06323 | -0.050418 | -0.040028 | 0.032203 | -1.5427 | 0.21973 | -1.8677 | 0.60883 | 0.42572 | -4.8843 | 0.63629 | 0.78278 | 0.90179 | -123.0148 | 120.7489 | -0.50354 | 121.0739 | 123.2254 | -0.29755 | -0.39825 | 0.17853 | 0.32501 | 123.2529 | 123.3994 | 123.0423 | 122.8363 | 121.0739 | 123.5184 | 117.7322 | -0.39825 | 122.8363 | 121.0739 | 117.7322 | 123.0423 | 123.5184 | -2.5909 | -123.7381
1422.9844 | 123.4222 | -122.6715 | 0.70953 | 0.21067 | 0.049038 | -0.010416 | 0.082456 | -0.049349 | -0.013325 | 0.028999 | -1.5701 | 0.26093 | -1.9226 | 0.72327 | 0.47607 | -5.0629 | 0.5127 | 0.85144 | 0.8606 | -123.0515 | 120.7489 | -0.44861 | 121.1014 | 123.3948 | -0.23346 | -0.37994 | 0.15106 | 0.35248 | 123.1842 | 123.5229 | 123.1476 | 122.9324 | 121.1014 | 123.5321 | 117.6086 | -0.37994 | 122.9324 | 121.1014 | 117.6086 | 123.1476 | 123.5321 | -2.6321 | -123.761
1423.9219 | 123.5458 | -122.6532 | 0.68665 | 0.50059 | 0.034085 | 0.00026463 | 0.074979 | -0.042941 | -0.01012 | 0.037543 | -1.3733 | 0.20142 | -1.7624 | 0.45776 | 0.50812 | -4.6967 | 0.57678 | 0.75073 | 0.86975 | -123.056 | 120.8908 | -0.48523 | 121.2799 | 123.111 | -0.17853 | -0.40283 | 0.18311 | 0.3891 | 123.23 | 123.4039 | 123.1613 | 122.8546 | 121.2799 | 123.5229 | 117.9565 | -0.40283 | 122.8546 | 121.2799 | 117.9565 | 123.1613 | 123.5229 | -2.449 | -123.7427
1424.9844 | 123.4268 | -122.6669 | 0.73242 | -0.048725 | 0.049038 | -0.024302 | 0.088865 | -0.041873 | -0.0037124 | 0.042884 | -1.3458 | 0.27008 | -1.7212 | 0.69122 | 0.4303 | -4.3808 | 0.52185 | 0.82398 | 0.86517 | -123.024 | 120.9457 | -0.46234 | 121.3211 | 123.3582 | -0.30212 | -0.35706 | 0.13275 | 0.37537 | 123.1888 | 123.4909 | 123.0972 | 122.937 | 121.3211 | 123.5321 | 118.2861 | -0.35706 | 122.937 | 121.3211 | 118.2861 | 123.0972 | 123.5321 | -2.4536 | -123.7564
1425.9219 | 123.5138 | -122.6349 | 0.70038 | 0.027569 | 0.033017 | -0.024302 | 0.077116 | -0.048281 | -0.014393 | 0.036475 | -1.4648 | 0.21057 | -1.8311 | 0.59509 | 0.3479 | -4.422 | 0.65002 | 0.75531 | 0.91553 | -123.056 | 120.8038 | -0.48981 | 121.17 | 123.23 | -0.35248 | -0.42114 | 0.21515 | 0.36621 | 123.2849 | 123.3902 | 122.9828 | 122.8455 | 121.17 | 123.5504 | 118.2129 | -0.42114 | 122.8455 | 121.17 | 118.2129 | 122.9828 | 123.5504 | -2.5314 | -123.7564
1426.9844 | 123.436 | -122.6486 | 0.737 | 0.37852 | 0.037289 | -0.010416 | 0.085661 | -0.046145 | -0.01012 | 0.033271 | -1.5015 | 0.23804 | -1.8402 | 0.70496 | 0.46234 | -4.5547 | 0.55389 | 0.8606 | 0.88806 | -123.0148 | 120.8084 | -0.49896 | 121.1472 | 123.3536 | -0.27466 | -0.36621 | 0.15106 | 0.33874 | 123.2025 | 123.5092 | 123.111 | 122.8867 | 121.1472 | 123.5367 | 118.0939 | -0.36621 | 122.8867 | 121.1472 | 118.0939 | 123.111 | 123.5367 | -2.5772 | -123.7518
1427.9219 | 123.5275 | -122.5937 | 0.72784 | 0.36326 | 0.03088 | -0.0061444 | 0.071775 | -0.050418 | -0.026142 | 0.03968 | -1.506 | 0.21973 | -1.8768 | 0.60425 | 0.37994 | -4.7424 | 0.68207 | 0.76904 | 0.92468 | -123.0331 | 120.7169 | -0.50812 | 121.0876 | 123.1979 | -0.3479 | -0.43945 | 0.19684 | 0.37079 | 123.2758 | 123.3627 | 122.9736 | 122.8134 | 121.0876 | 123.5184 | 117.8513 | -0.43945 | 122.8134 | 121.0876 | 117.8513 | 122.9736 | 123.5184 | -2.6047 | -123.761
1428.9844 | 123.3398 | -122.644 | 0.7782 | 0.36326 | 0.046902 | 0.01415 | 0.087797 | -0.047213 | -0.0069164 | 0.03968 | -1.5198 | 0.2655 | -1.8539 | 0.76446 | 0.52185 | -4.2618 | 0.70496 | 0.83313 | 0.90179 | -122.9691 | 120.7901 | -0.51269 | 121.1243 | 123.4085 | -0.25635 | -0.32501 | 0.1236 | 0.33417 | 123.349 | 123.4772 | 123.1659 | 122.9095 | 121.1243 | 123.5458 | 118.3823 | -0.32501 | 122.9095 | 121.1243 | 118.3823 | 123.1659 | 123.5458 | -2.6321 | -123.7473
1429.9219 | 123.4818 | -122.6624 | 0.75989 | 0.45481 | 0.044766 | 0.0013326 | 0.084592 | -0.055758 | -0.0047804 | 0.028999 | -1.5427 | 0.21515 | -1.8677 | 0.69122 | 0.46692 | -4.4266 | 0.60425 | 0.84686 | 0.90637 | -123.0148 | 120.7947 | -0.54474 | 121.1197 | 123.3536 | -0.29297 | -0.35248 | 0.14648 | 0.32501 | 123.2666 | 123.5092 | 123.1293 | 122.8775 | 121.1197 | 123.5687 | 118.2358 | -0.35248 | 122.8775 | 121.1197 | 118.2358 | 123.1293 | 123.5687 | -2.6276 | -123.7747
1430.9844 | 123.4085 | -122.6761 | 0.75073 | 0.042827 | 0.036221 | -0.022166 | 0.092069 | -0.047213 | -0.018665 | 0.035407 | -1.4786 | 0.27466 | -1.8494 | 0.737 | 0.44861 | -4.6143 | 0.52185 | 0.87433 | 0.89264 | -123.0057 | 120.8267 | -0.47607 | 121.1975 | 123.4131 | -0.30212 | -0.32959 | 0.14191 | 0.37079 | 123.1979 | 123.5504 | 123.1247 | 122.9507 | 121.1975 | 123.5687 | 118.0618 | -0.32959 | 122.9507 | 121.1975 | 118.0618 | 123.1247 | 123.5687 | -2.6001 | -123.7564
1431.9219 | 123.436 | -122.699 | 0.737 | 4.8493 | 0.033017 | -0.018961 | 0.073911 | -0.047213 | -0.0047804 | 0.033271 | -1.7624 | 0.28381 | -1.9501 | 0.69122 | 0.4715 | -4.9484 | 0.49896 | 0.88806 | 0.88806 | -123.0469 | 120.7489 | -0.45319 | 120.9366 | 123.3902 | -0.2655 | -0.3479 | 0.15106 | 0.18768 | 123.1979 | 123.587 | 123.1705 | 122.9828 | 120.9366 | 123.587 | 117.7506 | -0.3479 | 122.9828 | 120.9366 | 117.7506 | 123.1705 | 123.587 | -2.6871 | -123.7839
1432.9844 | 123.3719 | -122.7219 | 0.737 | 0.71421 | 0.044766 | -0.012553 | 0.08032 | -0.035464 | -0.0047804 | 0.038612 | -1.5289 | 0.25635 | -1.8814 | 0.75073 | 0.49439 | -5.0079 | 0.45319 | 0.91095 | 0.87433 | -123.0331 | 120.8405 | -0.48065 | 121.1929 | 123.4726 | -0.24261 | -0.31128 | 0.13733 | 0.35248 | 123.175 | 123.6328 | 123.2162 | 122.9782 | 121.1929 | 123.5962 | 117.7139 | -0.31128 | 122.9782 | 121.1929 | 117.7139 | 123.2162 | 123.5962 | -2.6184 | -123.7701
1433.9219 | 123.5184 | -122.5937 | 0.75531 | 0.47007 | 0.031949 | -0.021098 | 0.066434 | -0.049349 | -0.014393 | 0.038612 | -1.5198 | 0.19226 | -1.8814 | 0.61798 | 0.40741 | -5.0858 | 0.72327 | 0.79651 | 0.93842 | -123.0011 | 120.7123 | -0.56305 | 121.0739 | 123.2117 | -0.3479 | -0.40741 | 0.18311 | 0.36163 | 123.317 | 123.3902 | 123.0011 | 122.7859 | 121.0739 | 123.5321 | 117.5079 | -0.40741 | 122.7859 | 121.0739 | 117.5079 | 123.0011 | 123.5321 | -2.6367 | -123.7564
1434.9844 | 123.3902 | -122.6028 | 0.83313 | 0.47007 | 0.053311 | -0.013621 | 0.084592 | -0.048281 | -0.00050737 | 0.03968 | -1.5198 | 0.28839 | -1.8494 | 0.8194 | 0.49896 | -4.953 | 0.58594 | 0.98877 | 0.94299 | -122.9462 | 120.7535 | -0.54474 | 121.0831 | 123.4222 | -0.33417 | -0.34332 | 0.10986 | 0.32959 | 123.1888 | 123.5916 | 123.1018 | 122.8912 | 121.0831 | 123.5458 | 117.6498 | -0.34332 | 122.8912 | 121.0831 | 117.6498 | 123.1018 | 123.5458 | -2.6825 | -123.7793
1435.9219 | 123.4039 | -122.6578 | 0.78735 | 0.40904 | 0.049038 | -0.0029404 | 0.085661 | -0.046145 | -0.016529 | 0.042884 | -1.5839 | 0.27924 | -1.9272 | 0.80109 | 0.49896 | -4.9667 | 0.53558 | 0.9613 | 0.91553 | -122.9965 | 120.7306 | -0.50812 | 121.0739 | 123.4589 | -0.28839 | -0.33875 | 0.12817 | 0.34332 | 123.1934 | 123.6191 | 123.1567 | 122.937 | 121.0739 | 123.5733 | 117.691 | -0.33875 | 122.937 | 121.0739 | 117.691 | 123.1567 | 123.5733 | -2.7145 | -123.7839
1436.9844 | 123.4406 | -122.644 | 0.76904 | -0.36916 | 0.034085 | -0.014689 | 0.087797 | -0.048281 | -0.02187 | 0.037543 | -1.5381 | 0.26093 | -1.886 | 0.75073 | 0.49439 | -4.8614 | 0.54932 | 0.93384 | 0.92468 | -122.9874 | 120.7581 | -0.50812 | 121.106 | 123.3948 | -0.27466 | -0.34332 | 0.15564 | 0.3479 | 123.1934 | 123.5779 | 123.1384 | 122.905 | 121.106 | 123.5687 | 117.7826 | -0.34332 | 122.905 | 121.106 | 117.7826 | 123.1384 | 123.5687 | -2.655 | -123.7564
1437.9219 | 123.4314 | -122.612 | 0.81482 | 0.36326 | 0.04797 | -0.0061444 | 0.079252 | -0.048281 | -0.020801 | 0.03968 | -1.5427 | 0.27008 | -1.2909 | 0.77362 | 0.54016 | -4.8248 | 0.54474 | 0.95673 | 0.90179 | -122.9645 | 121.3211 | -0.54474 | 121.0693 | 123.3856 | -0.27466 | -0.35248 | 0.086975 | -0.25177 | 123.1567 | 123.5687 | 123.1522 | 122.8821 | 121.0693 | 123.5138 | 117.7872 | -0.35248 | 122.8821 | 121.0693 | 117.7872 | 123.1522 | 123.5138 | -2.1057 | -123.7793
1438.9688 | 123.4131 | -122.6395 | 0.78735 | -0.41494 | 0.028744 | -0.0093484 | 0.068571 | -0.049349 | -0.0443 | 0.043952 | -1.4557 | 0.26093 | -1.7899 | 0.71869 | 0.45776 | -4.8843 | 0.53101 | 0.92468 | 0.93842 | -122.9691 | 120.8496 | -0.52643 | 121.1838 | 123.3582 | -0.32959 | -0.32959 | 0.15106 | 0.33417 | 123.1705 | 123.5641 | 123.0972 | 122.9004 | 121.1838 | 123.5779 | 117.7551 | -0.32959 | 122.9004 | 121.1838 | 117.7551 | 123.0972 | 123.5779 | -2.5772 | -123.7564
1439.9219 | 123.4039 | -122.6212 | 0.79651 | -0.018208 | 0.051175 | 0.0077416 | 0.079252 | -0.049349 | -0.0079844 | 0.041816 | -1.5015 | 0.25635 | -1.886 | 0.76904 | 0.48523 | -5.1178 | 0.56763 | 0.92926 | 0.93384 | -122.9919 | 120.7352 | -0.54016 | 121.1197 | 123.3902 | -0.31128 | -0.37079 | 0.13733 | 0.38452 | 123.1888 | 123.5504 | 123.1064 | 122.8775 | 121.1197 | 123.555 | 117.5034 | -0.37079 | 122.8775 | 121.1197 | 117.5034 | 123.1064 | 123.555 | -2.6825 | -123.7885
1440.9844 | 123.4406 | -122.3831 | 0.97961 | -0.079243 | 0.051175 | -0.0050764 | 0.079252 | -0.036532 | -0.018665 | 0.047157 | -1.4832 | 0.26093 | -1.8631 | 0.88348 | 0.62256 | -5.1224 | 0.73242 | 1.0483 | 1.0803 | -122.8455 | 120.52 | -0.71869 | 120.9 | 123.2666 | -0.35706 | -0.46234 | 0.10071 | 0.37994 | 123.1155 | 123.4314 | 123.0057 | 122.644 | 120.9 | 123.4634 | 117.2607 | -0.46234 | 122.644 | 120.9 | 117.2607 | 123.0057 | 123.4634 | -2.8427 | -123.8251
1441.9219 | 123.4039 | -122.6395 | 0.78278 | 0.11912 | 0.045834 | 0.0088096 | 0.086729 | -0.033328 | -0.012257 | 0.03968 | -1.4511 | 0.25635 | -1.8311 | 0.76904 | 0.54932 | -4.9164 | 0.54932 | 0.94299 | 0.93842 | -122.9919 | 120.8084 | -0.52643 | 121.1884 | 123.4085 | -0.23346 | -0.35248 | 0.15564 | 0.37994 | 123.1888 | 123.5825 | 123.1888 | 122.8958 | 121.1884 | 123.5779 | 117.7231 | -0.35248 | 122.8958 | 121.1884 | 117.7231 | 123.1888 | 123.5779 | -2.6138 | -123.7747
1442.9844 | 123.4222 | -122.6715 | 0.78735 | -0.21657 | 0.027676 | -0.032847 | 0.072843 | -0.052554 | -0.031483 | 0.031135 | -1.4694 | 0.25635 | -1.799 | 0.74158 | 0.5127 | -4.9988 | 0.51727 | 0.92926 | 0.90179 | -122.9919 | 120.8725 | -0.53101 | 121.2021 | 123.4131 | -0.27466 | -0.32043 | 0.11444 | 0.32959 | 123.1888 | 123.6008 | 123.1842 | 122.9279 | 121.2021 | 123.5733 | 117.6727 | -0.32043 | 122.9279 | 121.2021 | 117.6727 | 123.1842 | 123.5733 | -2.5864 | -123.7793
1443.9219 | 123.4085 | -122.6761 | 0.74158 | 0.088604 | 0.050107 | -0.00080337 | 0.081388 | -0.046145 | -0.0037124 | 0.035407 | -1.4648 | 0.24719 | -1.8082 | 0.74616 | 0.5127 | -5.0583 | 0.5127 | 0.9201 | 0.89264 | -123.0331 | 120.8679 | -0.49439 | 121.2112 | 123.4222 | -0.22888 | -0.35706 | 0.15106 | 0.34332 | 123.1888 | 123.5962 | 123.1888 | 122.9233 | 121.2112 | 123.5687 | 117.6178 | -0.35706 | 122.9233 | 121.2112 | 117.6178 | 123.1888 | 123.5687 | -2.5497 | -123.7747
1444.9844 | 123.4543 | -122.5067 | 0.93842 | -0.033467 | 0.04263 | -0.022166 | 0.08032 | -0.040805 | -0.013325 | 0.03968 | -1.387 | 0.27924 | -1.7899 | 0.87891 | 0.63629 | -4.9896 | 0.73242 | 1.0574 | 1.1124 | -122.8455 | 120.7169 | -0.65918 | 121.1197 | 123.3856 | -0.30212 | -0.33875 | 0.17395 | 0.40283 | 123.2391 | 123.5641 | 123.143 | 122.7859 | 121.1197 | 123.6191 | 117.5171 | -0.33875 | 122.7859 | 121.1197 | 117.5171 | 123.143 | 123.6191 | -2.7283 | -123.7839
1445.9219 | 123.4314 | -122.4838 | 0.92926 | -0.32338 | 0.027676 | 0.0013326 | 0.068571 | -0.0376 | -0.017597 | 0.028999 | -1.442 | 0.25177 | -1.7899 | 0.87891 | 0.64087 | -4.8203 | 0.6958 | 1.0574 | 1.0666 | -122.8592 | 120.694 | -0.67749 | 121.0419 | 123.3627 | -0.28839 | -0.37537 | 0.13733 | 0.3479 | 123.1796 | 123.5413 | 123.1247 | 122.7356 | 121.0419 | 123.5504 | 117.6636 | -0.37537 | 122.7356 | 121.0419 | 117.6636 | 123.1247 | 123.5504 | -2.7191 | -123.7885
1446.9688 | 123.5367 | -122.4609 | 0.93384 | -0.23183 | 0.021267 | -0.029642 | 0.039732 | -0.046145 | -0.036823 | 0.049293 | -1.4145 | 0.19684 | -1.767 | 0.70496 | 0.5127 | -5.159 | 0.8194 | 0.94299 | 1.1169 | -122.8683 | 120.694 | -0.737 | 121.0464 | 123.1659 | -0.42114 | -0.40741 | 0.18311 | 0.35248 | 123.2803 | 123.4039 | 122.9736 | 122.6578 | 121.0464 | 123.5779 | 117.3019 | -0.40741 | 122.6578 | 121.0464 | 117.3019 | 122.9736 | 123.5779 | -2.7008 | -123.8022
1447.9219 | 123.3765 | -122.4838 | 0.93842 | 0.21067 | 0.04263 | -0.0018714 | 0.092069 | -0.036532 | -0.011188 | 0.048225 | -1.5381 | 0.26093 | -1.8951 | 0.93842 | 0.71411 | -4.8981 | 0.64545 | 1.1215 | 1.0574 | -122.85 | 120.5887 | -0.67749 | 120.9457 | 123.4222 | -0.2243 | -0.36621 | 0.11902 | 0.35706 | 123.1293 | 123.6053 | 123.1979 | 122.7448 | 120.9457 | 123.5413 | 117.5858 | -0.36621 | 122.7448 | 120.9457 | 117.5858 | 123.1979 | 123.5413 | -2.8336 | -123.7885
1448.9844 | 123.3948 | -122.5525 | 0.9201 | -1.5441 | 0.035153 | -0.014689 | 0.066434 | -0.044009 | -0.016529 | 0.036475 | -1.5427 | 0.27924 | -1.8677 | 0.85602 | 0.6134 | -4.7745 | 0.6546 | 1.0712 | 1.0529 | -122.8409 | 120.6848 | -0.64087 | 121.0098 | 123.4085 | -0.3067 | -0.28839 | 0.13275 | 0.32501 | 123.2071 | 123.6237 | 123.1659 | 122.8317 | 121.0098 | 123.6053 | 117.778 | -0.28839 | 122.8317 | 121.0098 | 117.778 | 123.1659 | 123.6053 | -2.7878 | -123.761
1449.9219 | 123.4039 | -122.6074 | 0.8194 | -0.094502 | 0.044766 | -0.017893 | 0.091001 | -0.042941 | -0.017597 | 0.031135 | -1.474 | 0.25177 | -1.8677 | 0.81482 | 0.54016 | -4.9576 | 0.60425 | 0.97504 | 0.95215 | -122.9599 | 120.7397 | -0.56763 | 121.1334 | 123.4222 | -0.27924 | -0.35248 | 0.13275 | 0.39368 | 123.2117 | 123.5825 | 123.1476 | 122.8592 | 121.1334 | 123.5596 | 117.6498 | -0.35248 | 122.8592 | 121.1334 | 117.6498 | 123.1476 | 123.5596 | -2.6871 | -123.7793
1450.9844 | 123.4268 | -122.5388 | 0.89722 | 0.13438 | 0.043698 | -0.041392 | 0.067503 | -0.029055 | -0.018665 | 0.033271 | -1.4694 | 0.31128 | -1.7532 | 0.86517 | 0.59052 | -4.9255 | 0.62714 | 1.0437 | 1.0391 | -122.9004 | 120.7855 | -0.58594 | 121.0693 | 123.4039 | -0.3067 | -0.36163 | 0.14191 | 0.28381 | 123.1659 | 123.5825 | 123.1293 | 122.85 | 121.0693 | 123.5779 | 117.6132 | -0.36163 | 122.85 | 121.0693 | 117.6132 | 123.1293 | 123.5779 | -2.6505 | -123.7976
1451.9219 | 123.4131 | -122.5433 | 0.91553 | -0.4302 | 0.039425 | -0.029642 | 0.076048 | -0.048281 | -0.030414 | 0.038612 | -1.4877 | 0.2655 | -1.8127 | 0.87891 | 0.63629 | -5.0674 | 0.63629 | 1.0757 | 1.062 | -122.8729 | 120.7306 | -0.65002 | 121.0556 | 123.4222 | -0.27924 | -0.32959 | 0.14648 | 0.32501 | 123.1796 | 123.6191 | 123.1796 | 122.8088 | 121.0556 | 123.6053 | 117.4759 | -0.32959 | 122.8088 | 121.0556 | 117.4759 | 123.1796 | 123.6053 | -2.7283 | -123.7885
1452.9844 | 123.4039 | -122.5342 | 0.9201 | -0.36916 | 0.031949 | -0.014689 | 0.067503 | -0.045077 | -0.029346 | 0.038612 | -1.593 | 0.25635 | -1.8951 | 0.86975 | 0.62256 | -5.3238 | 0.63629 | 1.0712 | 1.0437 | -122.8546 | 120.639 | -0.66376 | 120.9412 | 123.4039 | -0.29755 | -0.32043 | 0.1236 | 0.30212 | 123.1705 | 123.6053 | 123.1567 | 122.7905 | 120.9412 | 123.5779 | 117.2104 | -0.32043 | 122.7905 | 120.9412 | 117.2104 | 123.1567 | 123.5779 | -2.8152 | -123.7747
1453.9219 | 123.349 | -122.5159 | 0.93842 | -0.41494 | 0.041562 | -0.026438 | 0.074979 | -0.048281 | -0.026142 | 0.035407 | -1.5106 | 0.26093 | -1.8127 | 0.81024 | 0.71411 | -5.0034 | 0.83313 | 1.0437 | 1.062 | -122.8455 | 120.7031 | -0.67749 | 121.0052 | 123.3261 | -0.2243 | -0.32959 | 0.1236 | 0.30212 | 123.349 | 123.5596 | 123.23 | 122.7768 | 121.0052 | 123.5779 | 117.5125 | -0.32959 | 122.7768 | 121.0052 | 117.5125 | 123.23 | 123.5779 | -2.7512 | -123.7839
1454.9844 | 123.4451 | -122.612 | 0.81024 | -0.3539 | 0.038357 | -0.013621 | 0.091001 | -0.047213 | -0.02721 | 0.034339 | -1.474 | 0.24261 | -1.8356 | 0.77362 | 0.53101 | -5.1727 | 0.56305 | 0.94757 | 0.93384 | -122.9919 | 120.7764 | -0.56763 | 121.138 | 123.3856 | -0.27924 | -0.37994 | 0.1236 | 0.36163 | 123.175 | 123.5596 | 123.143 | 122.8546 | 121.138 | 123.5458 | 117.4393 | -0.37994 | 122.8546 | 121.138 | 117.4393 | 123.143 | 123.5458 | -2.6459 | -123.8022
1455.9219 | 123.3856 | -122.6212 | 0.8194 | -3.0547 | 0.04263 | -0.0072124 | 0.081388 | -0.044009 | -0.034687 | 0.046088 | -1.6113 | 0.28839 | -1.7761 | 0.7782 | 0.52185 | -5.0491 | 0.54932 | 0.9613 | 0.97504 | -122.9599 | 120.845 | -0.53101 | 121.0098 | 123.3994 | -0.29755 | -0.33875 | 0.15564 | 0.16479 | 123.1705 | 123.5825 | 123.143 | 122.9095 | 121.0098 | 123.5962 | 117.572 | -0.33875 | 122.9095 | 121.0098 | 117.572 | 123.143 | 123.5962 | -2.5955 | -123.7793
1456.9844 | 123.4772 | -122.5662 | 0.8194 | -0.46071 | 0.04263 | -0.022166 | 0.056821 | -0.051486 | -0.034687 | 0.04502 | -1.4832 | 0.23346 | -1.8494 | 0.69122 | 0.46692 | -4.9942 | 0.63629 | 0.89722 | 1.0025 | -122.9919 | 120.7169 | -0.58594 | 121.0831 | 123.2574 | -0.35248 | -0.42572 | 0.1831 | 0.36621 | 123.2025 | 123.4634 | 123.0331 | 122.7997 | 121.0831 | 123.5687 | 117.572 | -0.42572 | 122.7997 | 121.0831 | 117.572 | 123.0331 | 123.5687 | -2.6688 | -123.8113
1457.9219 | 123.3994 | -122.6212 | 0.84228 | -0.41494 | 0.038357 | -0.018961 | 0.072843 | -0.051486 | -0.034687 | 0.046088 | -1.5472 | 0.27466 | -1.8677 | 0.80566 | 0.54932 | -5.0171 | 0.54016 | 0.98877 | 1.0025 | -122.9416 | 120.7535 | -0.56763 | 121.0739 | 123.4268 | -0.29297 | -0.32043 | 0.16022 | 0.32043 | 123.1613 | 123.6099 | 123.1705 | 122.8958 | 121.0739 | 123.6237 | 117.6041 | -0.32043 | 122.8958 | 121.0739 | 117.6041 | 123.1705 | 123.6237 | -2.71 | -123.7839
1458.9844 | 123.4909 | -122.5937 | 0.8194 | 0.073345 | 0.027676 | -0.036051 | 0.05789 | -0.055758 | -0.041096 | 0.033271 | -1.8173 | 0.21057 | -1.918 | 0.6546 | 0.48065 | -5.2048 | 0.68665 | 0.88348 | 0.95673 | -122.9507 | 120.6757 | -0.60883 | 120.7764 | 123.2483 | -0.33875 | -0.35706 | 0.13733 | 0.10071 | 123.2803 | 123.4772 | 123.0743 | 122.8043 | 120.7764 | 123.5504 | 117.3889 | -0.35706 | 122.8043 | 120.7764 | 117.3889 | 123.0743 | 123.5504 | -2.7374 | -123.7701
1459.9219 | 123.4726 | -122.5845 | 0.80109 | -0.41494 | 0.023404 | -0.024302 | 0.067503 | -0.063235 | -0.028278 | 0.031135 | -1.5381 | 0.2243 | -1.9135 | 0.66834 | 0.44403 | -5.2963 | 0.6546 | 0.87891 | 0.97504 | -122.9919 | 120.6711 | -0.57678 | 121.0464 | 123.2529 | -0.35705 | -0.40741 | 0.17395 | 0.37537 | 123.2391 | 123.4634 | 123.0286 | 122.8088 | 121.0464 | 123.5596 | 117.2882 | -0.40741 | 122.8088 | 121.0464 | 117.2882 | 123.0286 | 123.5596 | -2.7145 | -123.793
1460.9844 | 123.5275 | -122.5937 | 0.79193 | -0.063984 | 0.02554 | -0.040324 | 0.062162 | -0.066439 | -0.038959 | 0.036475 | -1.593 | 0.23804 | -1.9455 | 0.60425 | 0.39825 | -5.4794 | 0.69122 | 0.79651 | 0.98877 | -123.0148 | 120.6482 | -0.55389 | 121.0007 | 123.1979 | -0.39368 | -0.42114 | 0.19684 | 0.35248 | 123.2849 | 123.3902 | 122.9919 | 122.8317 | 121.0007 | 123.5825 | 117.1143 | -0.42114 | 122.8317 | 121.0007 | 117.1143 | 122.9919 | 123.5825 | -2.7374 | -123.8068
1461.9219 | 123.4085 | -122.644 | 0.80109 | -0.52175 | 0.026608 | -0.036051 | 0.083524 | -0.046145 | -0.026142 | 0.036475 | -1.6159 | 0.24261 | -1.9409 | 0.77362 | 0.48981 | -5.2826 | 0.5127 | 0.94757 | 0.93384 | -122.9919 | 120.7031 | -0.55847 | 121.0281 | 123.4177 | -0.31128 | -0.3479 | 0.13275 | 0.32501 | 123.1567 | 123.5916 | 123.1338 | 122.8867 | 121.0281 | 123.5779 | 117.3614 | -0.3479 | 122.8867 | 121.0281 | 117.3614 | 123.1338 | 123.5779 | -2.742 | -123.793
1462.9688 | 123.5092 | -122.6074 | 0.79651 | 0.11912 | 0.03088 | -0.015757 | 0.072843 | -0.053622 | -0.032551 | 0.040748 | -1.6205 | 0.20142 | -1.9592 | 0.63629 | 0.39368 | -5.3879 | 0.64087 | 0.83771 | 0.9613 | -122.9828 | 120.6482 | -0.59509 | 120.9869 | 123.2437 | -0.40283 | -0.37537 | 0.1648 | 0.33875 | 123.2483 | 123.4451 | 123.0011 | 122.8088 | 120.9869 | 123.5687 | 117.2195 | -0.37537 | 122.8088 | 120.9869 | 117.2195 | 123.0011 | 123.5687 | -2.7557 | -123.7793
1463.9219 | 123.4451 | -122.6624 | 0.79193 | -0.26235 | 0.039425 | -0.018961 | 0.085661 | -0.044009 | -0.015461 | 0.02259 | -1.5839 | 0.2655 | -1.9363 | 0.7782 | 0.46234 | -5.2322 | 0.52185 | 0.92926 | 0.91095 | -123.0011 | 120.726 | -0.52643 | 121.0785 | 123.4406 | -0.32959 | -0.33875 | 0.11902 | 0.35248 | 123.1842 | 123.5916 | 123.1247 | 122.9279 | 121.0785 | 123.5733 | 117.4301 | -0.33875 | 122.9279 | 121.0785 | 117.4301 | 123.1247 | 123.5733 | -2.7283 | -123.793
1464.9844 | 123.5413 | -122.5662 | 0.81482 | -0.15554 | 0.016995 | -0.036051 | 0.060026 | -0.05469 | -0.054981 | 0.025794 | -1.593 | 0.21973 | -1.9455 | 0.6546 | 0.35248 | -5.3925 | 0.71411 | 0.84228 | 1.0117 | -122.9416 | 120.6207 | -0.59509 | 120.9732 | 123.2208 | -0.46234 | -0.37537 | 0.19684 | 0.35248 | 123.2803 | 123.4085 | 122.9187 | 122.7859 | 120.9732 | 123.5779 | 117.1738 | -0.37537 | 122.7859 | 120.9732 | 117.1738 | 122.9187 | 123.5779 | -2.7603 | -123.7564
1465.9219 | 123.3902 | -122.5296 | 0.86975 | -0.39968 | 0.020199 | -0.028574 | 0.071775 | -0.053622 | -0.034687 | 0.035407 | -1.5518 | 0.20142 | -1.8997 | 0.72784 | 0.47607 | -5.2917 | 0.80109 | 0.78278 | 1.1078 | -122.9736 | 120.6299 | -0.66834 | 120.9778 | 123.2574 | -0.39368 | -0.44403 | 0.23804 | 0.3479 | 123.3307 | 123.3124 | 123.0057 | 122.731 | 120.9778 | 123.6374 | 117.2379 | -0.44403 | 122.731 | 120.9778 | 117.2379 | 123.0057 | 123.6374 | -2.7695 | -123.8434
1466.9688 | 123.4726 | -122.525 | 0.87433 | 0.57688 | 0.037289 | -0.014689 | 0.086729 | -0.058962 | -0.017597 | 0.033271 | -1.6388 | 0.24261 | -1.9958 | 0.84686 | 0.57678 | -5.3055 | 0.72327 | 0.97961 | 1.0254 | -122.8867 | 120.5292 | -0.63171 | 120.8862 | 123.3719 | -0.29755 | -0.36163 | 0.15106 | 0.35706 | 123.2483 | 123.5046 | 123.1018 | 122.7676 | 120.8862 | 123.5504 | 117.2195 | -0.36163 | 122.7676 | 120.8862 | 117.2195 | 123.1018 | 123.5504 | -2.8702 | -123.761
1467.9219 | 123.5321 | -122.6257 | 0.75531 | -0.38442 | 0.016995 | -0.038187 | 0.055753 | -0.048281 | -0.02721 | 0.041816 | -1.6296 | 0.21057 | -1.9867 | 0.48981 | 0.46234 | -5.2277 | 0.59967 | 0.76446 | 0.93384 | -123.0148 | 120.639 | -0.54474 | 120.9961 | 123.1155 | -0.29297 | -0.3891 | 0.17853 | 0.35705 | 123.2254 | 123.3902 | 123.0881 | 122.8363 | 120.9961 | 123.5596 | 117.3981 | -0.3891 | 122.8363 | 120.9961 | 117.3981 | 123.0881 | 123.5596 | -2.742 | -123.7701
1468.9844 | 123.5504 | -122.6532 | 0.72784 | -0.36916 | 0.02554 | -0.016825 | 0.068571 | -0.055758 | -0.011188 | 0.024726 | -1.6937 | 0.21057 | -2.0416 | 0.63629 | 0.56763 | -5.4245 | 0.52643 | 0.83313 | 0.92468 | -123.024 | 120.6116 | -0.51727 | 120.9595 | 123.2895 | -0.16022 | -0.37079 | 0.19684 | 0.3479 | 123.1796 | 123.4863 | 123.2208 | 122.8638 | 120.9595 | 123.5779 | 117.2287 | -0.37079 | 122.8638 | 120.9595 | 117.2287 | 123.2208 | 123.5779 | -2.7695 | -123.7518
1469.9219 | 123.4497 | -122.6532 | 0.79651 | -0.50649 | 0.023404 | -0.017893 | 0.084592 | -0.056826 | -0.043232 | 0.032203 | -1.6983 | 0.25177 | -2.0554 | 0.69122 | 0.36621 | -5.5069 | 0.55847 | 0.87891 | 0.93384 | -123.0011 | 120.5978 | -0.54474 | 120.9549 | 123.3444 | -0.4303 | -0.3479 | 0.13733 | 0.35706 | 123.2117 | 123.5321 | 123.0194 | 122.905 | 120.9549 | 123.587 | 117.1463 | -0.3479 | 122.905 | 120.9549 | 117.1463 | 123.0194 | 123.587 | -2.8519 | -123.7976
1470.9844 | 123.5687 | -122.5845 | 0.76446 | -0.58278 | 0.027676 | -0.017893 | 0.061094 | -0.058962 | -0.0443 | 0.035407 | -1.7075 | 0.21973 | -2.0874 | 0.58136 | 0.31586 | -5.5664 | 0.71411 | 0.76446 | 0.97504 | -123.0103 | 120.4971 | -0.54474 | 120.8771 | 123.1659 | -0.44861 | -0.42572 | 0.21057 | 0.37994 | 123.2986 | 123.349 | 122.9004 | 122.8043 | 120.8771 | 123.5596 | 117.0181 | -0.42572 | 122.8043 | 120.8771 | 117.0181 | 122.9004 | 123.5596 | -2.8519 | -123.7747
1471.9219 | 123.5367 | -122.5021 | 0.89722 | -0.033467 | 0.018063 | -0.038187 | 0.076048 | -0.057894 | -0.036823 | 0.032203 | -1.6525 | 0.19684 | -2.0325 | 0.76446 | 0.51727 | -5.1407 | 0.83313 | 0.95215 | 1.1169 | -122.8638 | 120.4697 | -0.70038 | 120.8496 | 123.2666 | -0.37994 | -0.36163 | 0.21973 | 0.37994 | 123.3353 | 123.4543 | 123.0194 | 122.699 | 120.8496 | 123.6191 | 117.3614 | -0.36163 | 122.699 | 120.8496 | 117.3614 | 123.0194 | 123.6191 | -2.9297 | -123.761
1472.9844 | 123.555 | -122.4701 | 0.90637 | -0.65908 | 0.012723 | -0.029642 | 0.078184 | -0.064303 | -0.035755 | 0.038612 | -1.593 | 0.21973 | -2.0004 | 0.71411 | 0.45776 | -4.9484 | 0.80566 | 0.92926 | 1.1124 | -122.8638 | 120.4697 | -0.68664 | 120.8771 | 123.1842 | -0.44861 | -0.39368 | 0.20599 | 0.40741 | 123.2758 | 123.3994 | 122.9279 | 122.6898 | 120.8771 | 123.5825 | 117.5217 | -0.39368 | 122.6898 | 120.8771 | 117.5217 | 122.9279 | 123.5825 | -2.9068 | -123.7701
1473.9219 | 123.5413 | -122.4792 | 0.93384 | -0.063984 | 0.028744 | -0.02537 | 0.060026 | -0.061099 | -0.034687 | 0.03968 | -1.6708 | 0.21973 | -2.0142 | 0.75989 | 0.49439 | -5.0446 | 0.83313 | 0.95215 | 1.1078 | -122.8317 | 120.4651 | -0.71411 | 120.8084 | 123.2391 | -0.43945 | -0.35248 | 0.17395 | 0.34332 | 123.3124 | 123.4314 | 122.9736 | 122.699 | 120.8084 | 123.587 | 117.4347 | -0.35248 | 122.699 | 120.8084 | 117.4347 | 122.9736 | 123.587 | -2.948 | -123.7656
1474.9844 | 123.4451 | -122.5525 | 0.89722 | 0.45481 | 0.037289 | 0.0034686 | 0.094205 | -0.053622 | -0.022938 | 0.037543 | -1.6846 | 0.25177 | -2.0416 | 0.91095 | 0.61798 | -5.0125 | 0.6958 | 1.0208 | 1.03 | -122.8729 | 120.5109 | -0.64545 | 120.8679 | 123.4634 | -0.27924 | -0.32043 | 0.13275 | 0.35706 | 123.2483 | 123.5733 | 123.1705 | 122.8043 | 120.8679 | 123.5825 | 117.54 | -0.32043 | 122.8043 | 120.8679 | 117.54 | 123.1705 | 123.5825 | -2.9388 | -123.7701
1475.9219 | 123.4497 | -122.5937 | 0.89264 | 0.348 | 0.040494 | -0.014689 | 0.078184 | -0.050418 | -0.018665 | 0.028999 | -1.5518 | 0.27008 | -2.0645 | 0.93384 | 0.62714 | -5.1727 | 0.62256 | 1.0391 | 1.0117 | -122.8821 | 120.5292 | -0.62256 | 121.0419 | 123.5275 | -0.2655 | -0.28839 | 0.11902 | 0.51269 | 123.2162 | 123.6328 | 123.2208 | 122.8638 | 121.0419 | 123.6053 | 117.421 | -0.28839 | 122.8638 | 121.0419 | 117.421 | 123.2208 | 123.6053 | -2.9572 | -123.7747
1476.9844 | 123.5046 | -122.5021 | 0.88348 | 0.43956 | 0.031949 | -0.020029 | 0.066434 | -0.051486 | -0.035755 | 0.043952 | -1.7349 | 0.21057 | -2.0691 | 0.73242 | 0.49439 | -5.278 | 0.80109 | 0.9201 | 1.0574 | -122.8546 | 120.433 | -0.67291 | 120.7672 | 123.2346 | -0.3891 | -0.35248 | 0.17395 | 0.33417 | 123.3032 | 123.4222 | 122.9965 | 122.7127 | 120.7672 | 123.5596 | 117.2241 | -0.35248 | 122.7127 | 120.7672 | 117.2241 | 122.9965 | 123.5596 | -2.9526 | -123.7381
1477.9219 | 123.5138 | -122.5388 | 0.8606 | 0.01231 | 0.024472 | -0.040324 | 0.072843 | -0.063235 | -0.036823 | 0.03968 | -1.7578 | 0.16479 | -2.1057 | 0.737 | 0.51727 | -5.127 | 0.75531 | 0.94299 | 1.0391 | -122.8821 | 120.433 | -0.6958 | 120.7809 | 123.2758 | -0.34332 | -0.34332 | 0.17853 | 0.3479 | 123.2941 | 123.4818 | 123.056 | 122.7036 | 120.7809 | 123.5779 | 117.4118 | -0.34332 | 122.7036 | 120.7809 | 117.4118 | 123.056 | 123.5779 | -2.9663 | -123.7427
1478.9844 | 123.468 | -122.5388 | 0.91095 | 0.33274 | 0.046902 | -0.0029404 | 0.096342 | -0.051486 | -0.012257 | 0.032203 | -1.767 | 0.2655 | -2.1103 | 0.91553 | 0.58136 | -5.1315 | 0.63171 | 1.0483 | 1.0162 | -122.9141 | 120.4285 | -0.64545 | 120.7718 | 123.4543 | -0.32959 | -0.37537 | 0.10528 | 0.34332 | 123.1705 | 123.587 | 123.1201 | 122.8043 | 120.7718 | 123.555 | 117.4072 | -0.37537 | 122.8043 | 120.7718 | 117.4072 | 123.1201 | 123.555 | -3.0212 | -123.8251
1479.9219 | 123.4863 | -122.5296 | 0.90179 | 0.088604 | 0.024472 | -0.026438 | 0.069639 | -0.062167 | -0.048572 | 0.041816 | -1.7715 | 0.2243 | -2.0874 | 0.78278 | 0.49896 | -5.1636 | 0.75073 | 0.97504 | 1.0757 | -122.8821 | 120.4422 | -0.67749 | 120.7581 | 123.3124 | -0.40283 | -0.35248 | 0.17395 | 0.31586 | 123.2803 | 123.5046 | 123.0286 | 122.7539 | 120.7581 | 123.6053 | 117.366 | -0.35248 | 122.7539 | 120.7581 | 117.366 | 123.0286 | 123.6053 | -2.9892 | -123.7839
1480.9844 | 123.5504 | -122.493 | 0.89264 | -0.033467 | 0.026608 | -0.022166 | 0.068571 | -0.066439 | -0.036823 | 0.040748 | -1.7624 | 0.2243 | -2.0874 | 0.72327 | 0.46234 | -5.1773 | 0.78735 | 0.91553 | 1.0757 | -122.8867 | 120.4056 | -0.66833 | 120.7306 | 123.2162 | -0.4303 | -0.39368 | 0.18311 | 0.32501 | 123.2803 | 123.4085 | 122.9553 | 122.7173 | 120.7306 | 123.5687 | 117.3157 | -0.39368 | 122.7173 | 120.7306 | 117.3157 | 122.9553 | 123.5687 | -2.98 | -123.7793
1481.9219 | 123.4909 | -122.525 | 0.88348 | 0.14964 | 0.035153 | -0.012553 | 0.065366 | -0.055758 | -0.047504 | 0.032203 | -1.8127 | 0.22888 | -2.1194 | 0.7782 | 0.56305 | -5.0858 | 0.75531 | 0.95673 | 1.0666 | -122.8958 | 120.4056 | -0.6546 | 120.7123 | 123.3032 | -0.32044 | -0.37079 | 0.1831 | 0.3067 | 123.2803 | 123.4818 | 123.0881 | 122.7539 | 120.7123 | 123.5916 | 117.4393 | -0.37079 | 122.7539 | 120.7123 | 117.4393 | 123.0881 | 123.5916 | -3.0029 | -123.7793
1482.9844 | 123.5092 | -122.5204 | 0.89264 | -0.41494 | 0.028744 | -0.031779 | 0.073911 | -0.062167 | -0.034687 | 0.036475 | -1.767 | 0.17853 | -2.0691 | 0.7782 | 0.54474 | -5.191 | 0.78278 | 0.95215 | 1.0803 | -122.8729 | 120.4514 | -0.71411 | 120.7535 | 123.2986 | -0.3479 | -0.35248 | 0.18768 | 0.30212 | 123.3032 | 123.4726 | 123.0652 | 122.699 | 120.7535 | 123.6008 | 117.3294 | -0.35248 | 122.699 | 120.7535 | 117.3294 | 123.0652 | 123.6008 | -2.9617 | -123.7656
1483.9219 | 123.4955 | -122.5159 | 0.89722 | 0.39378 | 0.024472 | -0.027506 | 0.066434 | -0.062167 | -0.041096 | 0.025794 | -1.8539 | 0.22888 | -2.1973 | 0.80109 | 0.55389 | -5.2185 | 0.7782 | 0.95673 | 1.0803 | -122.8455 | 120.3186 | -0.66834 | 120.6619 | 123.317 | -0.34332 | -0.32959 | 0.1831 | 0.34332 | 123.2941 | 123.4726 | 123.0698 | 122.7448 | 120.6619 | 123.5962 | 117.2974 | -0.32959 | 122.7448 | 120.6619 | 117.2974 | 123.0698 | 123.5962 | -3.0945 | -123.7427
1484.9688 | 123.4543 | -122.5342 | 0.88806 | -0.27761 | 0.037289 | -0.017893 | 0.094205 | -0.057894 | -0.0079844 | 0.030067 | -1.6846 | 0.25635 | -2.0874 | 0.86975 | 0.56305 | -5.1819 | 0.70038 | 0.99335 | 1.0437 | -122.8912 | 120.4468 | -0.63171 | 120.8496 | 123.4039 | -0.32501 | -0.35705 | 0.15564 | 0.40283 | 123.2346 | 123.5275 | 123.0972 | 122.7905 | 120.8496 | 123.5779 | 117.3523 | -0.35705 | 122.7905 | 120.8496 | 117.3523 | 123.0972 | 123.5779 | -2.9755 | -123.7793
1485.9219 | 123.4131 | -122.5388 | 0.91095 | -0.3539 | 0.035153 | -0.051005 | 0.078184 | -0.042941 | -0.017597 | 0.033271 | -1.4511 | 0.27924 | -2.0096 | 0.93842 | 0.64087 | -5.0537 | 0.6134 | 1.0712 | 1.0529 | -122.8592 | 120.5292 | -0.63171 | 121.0876 | 123.4772 | -0.27008 | -0.32043 | 0.14191 | 0.55847 | 123.1522 | 123.6099 | 123.1796 | 122.818 | 121.0876 | 123.5916 | 117.485 | -0.32043 | 122.818 | 121.0876 | 117.485 | 123.1796 | 123.5916 | -2.9205 | -123.7701
1486.9844 | 123.4406 | -122.5479 | 0.92468 | 0.1649 | 0.044766 | -0.020029 | 0.10061 | -0.047213 | -0.0015754 | 0.030067 | -1.8219 | 0.24261 | -2.1973 | 0.93384 | 0.63171 | -5.2139 | 0.6546 | 1.062 | 1.03 | -122.8683 | 120.3506 | -0.68207 | 120.726 | 123.4818 | -0.29297 | -0.32043 | 0.10528 | 0.37537 | 123.2025 | 123.6099 | 123.1796 | 122.7905 | 120.726 | 123.5779 | 117.334 | -0.32043 | 122.7905 | 120.726 | 117.334 | 123.1796 | 123.5779 | -3.1219 | -123.793
1487.9219 | 123.4497 | -122.612 | 0.84228 | 0.40904 | 0.035153 | -0.016825 | 0.074979 | -0.053622 | -0.02187 | 0.038612 | -1.7532 | 0.21515 | -2.1149 | 0.73242 | 0.51727 | -5.3238 | 0.81024 | 0.91553 | 1.0849 | -122.9507 | 120.4971 | -0.62714 | 120.8588 | 123.3444 | -0.32501 | -0.33875 | 0.24262 | 0.36163 | 123.4222 | 123.5275 | 123.1293 | 122.8271 | 120.8588 | 123.6969 | 117.2882 | -0.33875 | 122.8271 | 120.8588 | 117.2882 | 123.1293 | 123.6969 | -2.9572 | -123.793
1488.9844 | 123.4543 | -122.5159 | 0.92468 | -1.3457 | 0.058651 | -0.014689 | 0.085661 | -0.046145 | -0.017597 | 0.041816 | -1.8127 | 0.26093 | -2.1149 | 0.92468 | 0.67749 | -5.3513 | 0.68665 | 1.0757 | 1.0574 | -122.8317 | 120.401 | -0.66376 | 120.7031 | 123.4406 | -0.24719 | -0.31586 | 0.13275 | 0.30212 | 123.2025 | 123.5916 | 123.1934 | 122.7768 | 120.7031 | 123.5733 | 117.1646 | -0.31586 | 122.7768 | 120.7031 | 117.1646 | 123.1934 | 123.5733 | -3.0396 | -123.7564
1489.9219 | 123.4955 | -122.4472 | 0.95673 | 0.25645 | 0.018063 | -0.017893 | 0.05789 | -0.042941 | -0.032551 | 0.046088 | -1.7578 | 0.22888 | -2.0645 | 0.83313 | 0.62714 | -5.2826 | 0.82855 | 1.0391 | 1.1169 | -122.818 | 120.3827 | -0.72784 | 120.6894 | 123.2803 | -0.32959 | -0.37079 | 0.16022 | 0.3067 | 123.2758 | 123.4863 | 123.0743 | 122.6761 | 120.6894 | 123.5641 | 117.1646 | -0.37079 | 122.6761 | 120.6894 | 117.1646 | 123.0743 | 123.5641 | -3.0212 | -123.7747
1490.9688 | 123.4314 | -122.5159 | 0.94757 | -0.36916 | 0.034085 | -0.024302 | 0.081388 | -0.050418 | -0.030414 | 0.026862 | -1.5015 | 0.28839 | -1.9501 | 0.90637 | 0.71411 | -5.1041 | 0.66376 | 1.0803 | 1.1078 | -122.8134 | 120.5658 | -0.65918 | 121.0144 | 123.4222 | -0.23346 | -0.29755 | 0.16022 | 0.44861 | 123.1796 | 123.5962 | 123.23 | 122.8043 | 121.0144 | 123.6237 | 117.4118 | -0.29755 | 122.8043 | 121.0144 | 117.4118 | 123.23 | 123.6237 | -2.8976 | -123.761
1491.9219 | 123.5367 | -122.2275 | 1.1215 | 0.073345 | 0.034085 | -0.014689 | 0.066434 | -0.057894 | -0.030414 | 0.043952 | -1.6708 | 0.21515 | -2.0966 | 1.0391 | 0.80566 | -4.953 | 1.0666 | 1.1719 | 1.3138 | -122.6715 | 120.1309 | -0.90637 | 120.5566 | 123.2666 | -0.31586 | -0.44403 | 0.19226 | 0.42572 | 123.2941 | 123.3994 | 123.0331 | 122.4426 | 120.5566 | 123.5413 | 117.2745 | -0.44403 | 122.4426 | 120.5566 | 117.2745 | 123.0331 | 123.5413 | -3.2181 | -123.793
1492.9844 | 123.5001 | -122.4884 | 0.92468 | 0.348 | 0.035153 | -0.022166 | 0.068571 | -0.052554 | -0.043232 | 0.031135 | -1.6891 | 0.22888 | -2.0508 | 0.77362 | 0.58594 | -5.0995 | 0.83771 | 0.97961 | 1.0986 | -122.8683 | 120.4376 | -0.6958 | 120.7993 | 123.262 | -0.33875 | -0.37994 | 0.17395 | 0.36163 | 123.3261 | 123.468 | 123.0743 | 122.7173 | 120.7993 | 123.587 | 117.3889 | -0.37994 | 122.7173 | 120.7993 | 117.3889 | 123.0743 | 123.587 | -2.9755 | -123.793
1493.9219 | 123.468 | -122.3282 | 1.0849 | 0.45481 | 0.031949 | -0.012553 | 0.084592 | -0.053622 | -0.020801 | 0.032203 | -1.712 | 0.24261 | -2.0599 | 1.0529 | 0.79651 | -4.9576 | 0.93842 | 1.2085 | 1.2451 | -122.6852 | 120.2682 | -0.84228 | 120.6162 | 123.381 | -0.28839 | -0.35706 | 0.16022 | 0.3479 | 123.2666 | 123.5367 | 123.1247 | 122.5708 | 120.6162 | 123.5733 | 117.3706 | -0.35706 | 122.5708 | 120.6162 | 117.3706 | 123.1247 | 123.5733 | -3.1448 | -123.7701
1494.9844 | 123.4177 | -122.5159 | 0.91095 | 0.11912 | 0.04797 | 0.00026463 | 0.087797 | -0.052554 | -0.0079844 | 0.026862 | -1.6891 | 0.27924 | -2.0737 | 0.91095 | 0.63171 | -4.9393 | 0.68207 | 1.0483 | 1.0483 | -122.8867 | 120.4422 | -0.63171 | 120.8267 | 123.4268 | -0.27924 | -0.37079 | 0.13733 | 0.38452 | 123.1979 | 123.5641 | 123.1476 | 122.7951 | 120.8267 | 123.5641 | 117.5766 | -0.37079 | 122.7951 | 120.8267 | 117.5766 | 123.1476 | 123.5641 | -2.9846 | -123.7976
1495.9219 | 123.5184 | -122.3053 | 1.1032 | 0.47007 | 0.049038 | -0.038187 | 0.082456 | -0.045077 | -0.017597 | 0.031135 | -1.7532 | 0.23804 | -2.092 | 1.0345 | 0.79651 | -4.9667 | 0.98877 | 1.1948 | 1.2497 | -122.6578 | 120.2133 | -0.86517 | 120.5521 | 123.3398 | -0.3067 | -0.35248 | 0.14648 | 0.33874 | 123.2941 | 123.5001 | 123.1018 | 122.5433 | 120.5521 | 123.555 | 117.3386 | -0.35248 | 122.5433 | 120.5521 | 117.3386 | 123.1018 | 123.555 | -3.1952 | -123.761
1496.9844 | 123.4634 | -122.5021 | 0.97046 | -0.063984 | 0.045834 | -0.0050764 | 0.086729 | -0.052554 | -0.017597 | 0.046088 | -1.6067 | 0.2655 | -1.9821 | 1.1948 | 0.76904 | -4.5959 | 0.77362 | 1.0574 | 1.1444 | -122.8409 | 120.52 | -0.70496 | 120.8954 | 123.6969 | -0.20142 | -0.33875 | 0.17395 | 0.37537 | 123.2758 | 123.5596 | 123.2712 | 122.7676 | 120.8954 | 123.6465 | 117.9062 | -0.33875 | 122.7676 | 120.8954 | 117.9062 | 123.2712 | 123.6465 | -2.9526 | -123.8113
1497.9219 | 123.4406 | -122.493 | 0.93384 | 1.3246 | 0.044766 | 0.0013326 | 0.084592 | -0.050418 | -0.015461 | 0.036475 | -1.6754 | 0.28839 | -2.0462 | 0.92468 | 0.65002 | -4.7882 | 0.71411 | 1.0941 | 1.0712 | -122.8683 | 120.4468 | -0.64545 | 120.8176 | 123.4177 | -0.28381 | -0.37537 | 0.13733 | 0.37079 | 123.2071 | 123.587 | 123.143 | 122.7814 | 120.8176 | 123.5641 | 117.7048 | -0.37537 | 122.7814 | 120.8176 | 117.7048 | 123.143 | 123.5641 | -2.98 | -123.8022
1498.9844 | 123.4634 | -122.5342 | 0.91095 | -0.23183 | 0.040494 | -0.011485 | 0.082456 | -0.036532 | -0.012257 | 0.049293 | -1.5793 | 0.27008 | -1.973 | 0.87891 | 0.62256 | -4.3945 | 0.66834 | 1.0345 | 1.0391 | -122.905 | 120.5612 | -0.64087 | 120.9549 | 123.4131 | -0.28839 | -0.37079 | 0.12817 | 0.39368 | 123.2025 | 123.5687 | 123.1567 | 122.8043 | 120.9549 | 123.5733 | 118.1396 | -0.37079 | 122.8043 | 120.9549 | 118.1396 | 123.1567 | 123.5733 | -2.8839 | -123.8159
1499.9219 | 123.4039 | -122.5159 | 0.91095 | 0.14964 | 0.046902 | -0.012553 | 0.094205 | -0.038668 | -0.0090524 | 0.037543 | -1.6296 | 0.2655 | -1.9913 | 0.90637 | 0.63629 | -4.3808 | 0.66376 | 1.0895 | 1.0483 | -122.8683 | 120.5246 | -0.64545 | 120.8862 | 123.4222 | -0.27466 | -0.35248 | 0.13733 | 0.36163 | 123.1796 | 123.6053 | 123.1522 | 122.7814 | 120.8862 | 123.5641 | 118.1351 | -0.35248 | 122.7814 | 120.8862 | 118.1351 | 123.1522 | 123.5641 | -2.9022 | -123.7793
1500.9688 | 123.5046 | -122.4335 | 0.97961 | -0.44545 | 0.039425 | -0.027506 | 0.083524 | -0.038668 | -0.038959 | 0.042884 | -1.6434 | 0.27466 | -1.9363 | 0.88806 | 0.64087 | -4.5181 | 0.6546 | 1.0986 | 1.0483 | -122.8317 | 120.4971 | -0.70496 | 120.7901 | 123.3215 | -0.33874 | -0.39825 | 0.068665 | 0.29297 | 123.0881 | 123.5321 | 123.0743 | 122.7081 | 120.7901 | 123.4818 | 117.9153 | -0.39825 | 122.7081 | 120.7901 | 117.9153 | 123.0743 | 123.4818 | -2.916 | -123.8113
1501.9219 | 123.4268 | -122.5113 | 0.95215 | 0.30223 | 0.041562 | -0.026438 | 0.078184 | -0.040805 | -0.014393 | 0.033271 | -1.6571 | 0.26093 | -2.0233 | 0.91553 | 0.64087 | -4.5044 | 0.95673 | 1.1719 | 1.0391 | -122.8455 | 120.488 | -0.69122 | 120.8542 | 123.4268 | -0.31128 | -0.33417 | 0.086976 | 0.36621 | 123.468 | 123.6832 | 123.1522 | 122.7722 | 120.8542 | 123.5504 | 118.0069 | -0.33417 | 122.7722 | 120.8542 | 118.0069 | 123.1522 | 123.5504 | -2.9755 | -123.7976
1502.9688 | 123.4634 | -122.493 | 0.94299 | -0.10976 | 0.036221 | 0.0013326 | 0.084592 | -0.0376 | -0.025074 | 0.038612 | -1.6159 | 0.26093 | -1.973 | 0.91095 | 0.63171 | -4.5776 | 0.75531 | 1.0712 | 1.0941 | -122.8546 | 120.52 | -0.68207 | 120.8771 | 123.4039 | -0.31128 | -0.36163 | 0.15106 | 0.35705 | 123.2483 | 123.5641 | 123.1247 | 122.7539 | 120.8771 | 123.587 | 117.9153 | -0.36163 | 122.7539 | 120.8771 | 117.9153 | 123.1247 | 123.587 | -2.916 | -123.7976
1503.9219 | 123.3994 | -122.3465 | 1.1169 | -0.018208 | 0.033017 | -0.024302 | 0.074979 | -0.051486 | 0.00056063 | 0.026862 | -1.6983 | 0.27466 | -2.0691 | 1.1261 | 0.79193 | -4.6509 | 0.84686 | 1.3229 | 1.2405 | -122.6761 | 120.2774 | -0.84228 | 120.6482 | 123.4726 | -0.32501 | -0.32959 | 0.1236 | 0.37079 | 123.1934 | 123.6694 | 123.1384 | 122.6212 | 120.6482 | 123.587 | 117.6956 | -0.32959 | 122.6212 | 120.6482 | 117.6956 | 123.1384 | 123.587 | -3.186 | -123.793
1504.9844 | 123.4726 | -122.4609 | 0.96588 | -0.32338 | 0.043698 | 0.0056046 | 0.078184 | -0.045077 | -0.024006 | 0.043952 | -1.5793 | 0.25177 | -1.9547 | 0.91095 | 0.66834 | -4.6326 | 0.75989 | 1.0803 | 1.1124 | -122.8455 | 120.5063 | -0.71411 | 120.8817 | 123.3719 | -0.29755 | -0.38452 | 0.14648 | 0.37537 | 123.2208 | 123.5413 | 123.1293 | 122.7127 | 120.8817 | 123.5733 | 117.8284 | -0.38452 | 122.7127 | 120.8817 | 117.8284 | 123.1293 | 123.5733 | -2.9205 | -123.8113
1505.9219 | 123.4314 | -122.3373 | 1.0941 | 0.073345 | 0.039425 | -0.018961 | 0.081388 | -0.044009 | -0.013325 | 0.028999 | -1.593 | 0.27924 | -1.9547 | 1.1032 | 0.82855 | -4.6417 | 0.86517 | 1.2543 | 1.2634 | -122.6898 | 120.3827 | -0.81482 | 120.7443 | 123.4406 | -0.2655 | -0.35248 | 0.16937 | 0.36163 | 123.2025 | 123.5916 | 123.1659 | 122.6166 | 120.7443 | 123.6008 | 117.6956 | -0.35248 | 122.6166 | 120.7443 | 117.6956 | 123.1659 | 123.6008 | -3.0487 | -123.7839
1506.9844 | 123.3627 | -122.2595 | 1.1765 | -0.38442 | 0.027676 | -0.02537 | 0.065366 | -0.038668 | -0.022938 | 0.036475 | -1.5152 | 0.28839 | -1.8219 | 1.0895 | 0.81024 | -4.5502 | 0.85602 | 1.3229 | 1.2634 | -122.6212 | 120.4376 | -0.88806 | 120.7443 | 123.349 | -0.36621 | -0.36163 | 0.086975 | 0.3067 | 123.1155 | 123.5825 | 123.0698 | 122.5479 | 120.7443 | 123.5229 | 117.7094 | -0.36163 | 122.5479 | 120.7443 | 117.7094 | 123.0698 | 123.5229 | -2.9984 | -123.7976
1507.9219 | 123.4497 | -122.3328 | 1.1124 | -0.55227 | 0.044766 | -0.020029 | 0.079252 | -0.040805 | -0.013325 | 0.02793 | -1.5015 | 0.32501 | -1.8768 | 1.0803 | 0.81024 | -4.5685 | 0.90179 | 1.236 | 1.2634 | -122.699 | 120.4559 | -0.78735 | 120.8313 | 123.4131 | -0.30212 | -0.36621 | 0.15106 | 0.37537 | 123.2346 | 123.5687 | 123.143 | 122.6578 | 120.8313 | 123.5962 | 117.7643 | -0.36621 | 122.6578 | 120.8313 | 117.7643 | 123.143 | 123.5962 | -2.9892 | -123.8113
1508.9844 | 123.4589 | -122.3648 | 1.0803 | -0.75063 | 0.046902 | -0.0061444 | 0.082456 | -0.039736 | -0.015461 | 0.041816 | -1.5335 | 0.32501 | -1.8677 | 1.0666 | 0.78278 | -4.747 | 0.87433 | 1.2314 | 1.2543 | -122.7219 | 120.4971 | -0.75531 | 120.8313 | 123.4314 | -0.29755 | -0.35706 | 0.17395 | 0.33417 | 123.2391 | 123.5962 | 123.1476 | 122.6898 | 120.8313 | 123.6191 | 117.6178 | -0.35706 | 122.6898 | 120.8313 | 117.6178 | 123.1476 | 123.6191 | -2.948 | -123.8022
1509.9219 | 123.4497 | -122.3511 | 1.0666 | 0.042827 | 0.043698 | -0.022166 | 0.078184 | -0.041873 | -0.00050737 | 0.03968 | -1.561 | 0.2655 | -1.9455 | 1.0666 | 0.80109 | -4.8935 | 0.8606 | 1.236 | 1.2314 | -122.7448 | 120.4056 | -0.80109 | 120.7901 | 123.4177 | -0.2655 | -0.39368 | 0.1648 | 0.38452 | 123.2117 | 123.587 | 123.1522 | 122.6166 | 120.7901 | 123.5825 | 117.4576 | -0.39368 | 122.6166 | 120.7901 | 117.4576 | 123.1522 | 123.5825 | -3.0121 | -123.8113
1510.9844 | 123.5413 | -122.2961 | 1.1169 | 4.7883 | 0.021267 | -0.026438 | 0.048277 | -0.048281 | -0.02721 | 0.038612 | -1.3367 | 0.20599 | -1.8082 | 0.9201 | 0.73242 | -4.4952 | 0.98419 | 1.1627 | 1.3092 | -122.6898 | 120.488 | -0.91095 | 120.9595 | 123.2162 | -0.38452 | -0.39368 | 0.19226 | 0.4715 | 123.2803 | 123.4589 | 123.0286 | 122.5021 | 120.9595 | 123.6053 | 117.8009 | -0.39368 | 122.5021 | 120.9595 | 117.8009 | 123.0286 | 123.6053 | -2.9251 | -123.8068
1511.9219 | 123.468 | -122.319 | 1.1536 | 0.01231 | 0.04263 | -0.027506 | 0.083524 | -0.042941 | -0.0079844 | 0.031135 | -1.4008 | 0.2655 | -1.7899 | 1.1215 | 0.84686 | -4.3533 | 0.94299 | 1.2589 | 1.3046 | -122.6761 | 120.5292 | -0.88806 | 120.9183 | 123.4406 | -0.3067 | -0.35706 | 0.15106 | 0.3891 | 123.262 | 123.5779 | 123.1659 | 122.5845 | 120.9183 | 123.6237 | 117.9657 | -0.35706 | 122.5845 | 120.9183 | 117.9657 | 123.1659 | 123.6237 | -2.9434 | -123.8297
1512.9844 | 123.4451 | -122.2778 | 1.1536 | -0.39968 | 0.040494 | -0.020029 | 0.071775 | -0.046145 | -0.02187 | 0.038612 | -1.4786 | 0.25635 | -1.8402 | 1.1215 | 0.85144 | -4.184 | 0.88806 | 1.3 | 1.2909 | -122.6349 | 120.4376 | -0.89722 | 120.7993 | 123.3994 | -0.30212 | -0.35706 | 0.13733 | 0.36163 | 123.1659 | 123.5779 | 123.1293 | 122.5342 | 120.7993 | 123.5687 | 118.0939 | -0.35706 | 122.5342 | 120.7993 | 118.0939 | 123.1293 | 123.5687 | -2.9938 | -123.7885
1513.9219 | 123.4543 | -122.1085 | 1.3275 | -0.26235 | 0.035153 | -0.00080337 | 0.072843 | -0.035464 | -0.02187 | 0.041816 | -1.3916 | 0.25635 | -1.7487 | 1.2817 | 0.98419 | -4.0009 | 1.1032 | 1.4603 | 1.4923 | -122.4838 | 120.3598 | -1.0712 | 120.7169 | 123.3902 | -0.34332 | -0.37537 | 0.1648 | 0.35705 | 123.2117 | 123.5687 | 123.0927 | 122.3648 | 120.7169 | 123.6008 | 118.1076 | -0.37537 | 122.3648 | 120.7169 | 118.1076 | 123.0927 | 123.6008 | -3.0762 | -123.8113
1514.9844 | 123.4085 | -122.2687 | 1.2314 | -0.58278 | 0.034085 | -0.02537 | 0.062162 | -0.040805 | -0.029346 | 0.048225 | -1.4328 | 0.27008 | -1.767 | 1.1673 | 0.88806 | -3.9459 | 0.96588 | 1.4053 | 1.3779 | -122.5708 | 120.5017 | -0.9613 | 120.8359 | 123.436 | -0.34332 | -0.30212 | 0.14648 | 0.33417 | 123.2346 | 123.674 | 123.1567 | 122.5388 | 120.8359 | 123.6465 | 118.3228 | -0.30212 | 122.5388 | 120.8359 | 118.3228 | 123.1567 | 123.6465 | -2.9984 | -123.8022
1515.9219 | 123.4314 | -122.3648 | 1.1444 | 0.11912 | 0.041562 | -0.014689 | 0.077116 | -0.044009 | -0.013325 | 0.033271 | -1.4603 | 0.24261 | -1.8494 | 1.1353 | 0.83313 | -4.1473 | 0.93384 | 1.3046 | 1.3092 | -122.6761 | 120.5154 | -0.90179 | 120.9045 | 123.5001 | -0.31128 | -0.31128 | 0.1648 | 0.3891 | 123.2986 | 123.6694 | 123.1979 | 122.6074 | 120.9045 | 123.674 | 118.2175 | -0.31128 | 122.6074 | 120.9045 | 118.2175 | 123.1979 | 123.674 | -2.9938 | -123.8205
1516.9844 | 123.5367 | -122.1909 | 1.2222 | 0.027569 | 0.044766 | -0.024302 | 0.055753 | -0.050418 | -0.026142 | 0.042884 | -1.3916 | 0.20599 | -1.7487 | 1.0529 | 0.81024 | -4.1519 | 1.0986 | 1.2817 | 1.4053 | -122.5983 | 120.4422 | -1.0162 | 120.7993 | 123.2437 | -0.41199 | -0.40741 | 0.18311 | 0.35705 | 123.2895 | 123.4726 | 123.0011 | 122.3969 | 120.7993 | 123.5962 | 118.0389 | -0.40741 | 122.3969 | 120.7993 | 118.0389 | 123.0011 | 123.5962 | -2.9709 | -123.8205
1517.9219 | 123.4451 | -120.7443 | 2.7008 | -0.32338 | 0.04797 | -0.021098 | 0.084592 | -0.042941 | -0.022938 | 0.032203 | -1.3367 | 0.27924 | -1.7075 | 2.7191 | 2.33 | -3.2867 | 2.4948 | 2.8839 | 2.8564 | -121.0739 | 119.0369 | -2.4216 | 119.4077 | 123.4634 | -0.37079 | -0.32959 | 0.15564 | 0.37079 | 123.2391 | 123.6282 | 123.0743 | 121.0236 | 119.4077 | 123.6008 | 117.4576 | -0.32959 | 121.0236 | 119.4077 | 117.4576 | 123.0743 | 123.6008 | -4.4083 | -123.7747
1518.9844 | 123.5641 | -121.0144 | 2.3849 | -0.24709 | 0.029812 | -0.036051 | 0.051481 | -0.070712 | -0.042164 | 0.040748 | -1.3138 | 0.21515 | -1.6617 | 2.2156 | 1.9547 | -3.4561 | 2.3254 | 2.4033 | 2.6093 | -121.4081 | 119.3527 | -2.1698 | 119.7006 | 123.23 | -0.4303 | -0.39368 | 0.2243 | 0.3479 | 123.3398 | 123.4177 | 122.9691 | 121.2296 | 119.7006 | 123.6237 | 117.5583 | -0.39368 | 121.2296 | 119.7006 | 117.5583 | 122.9691 | 123.6237 | -4.0466 | -123.793
1519.9219 | 123.468 | -122.1863 | 1.2772 | -0.38442 | 0.039425 | -0.026438 | 0.095274 | -0.046145 | -0.019733 | 0.036475 | -1.4191 | 0.25177 | -1.8082 | 1.2589 | 0.91553 | -3.9871 | 1.0574 | 1.4008 | 1.4328 | -122.525 | 120.3781 | -1.0254 | 120.7672 | 123.4451 | -0.36163 | -0.33875 | 0.15564 | 0.3891 | 123.2437 | 123.587 | 123.1018 | 122.438 | 120.7672 | 123.6191 | 118.1992 | -0.33875 | 122.438 | 120.7672 | 118.1992 | 123.1018 | 123.6191 | -3.0853 | -123.8022
1520.9844 | 123.4772 | -121.1563 | 2.3666 | -0.3539 | 0.037289 | -0.016825 | 0.08032 | -0.038668 | -0.017597 | 0.043952 | -1.3275 | 0.25177 | -1.6983 | 2.3163 | 1.9821 | -3.4607 | 2.1286 | 2.4673 | 2.4948 | -121.431 | 119.458 | -2.1149 | 119.8288 | 123.4726 | -0.38452 | -0.27466 | 0.12817 | 0.37079 | 123.2849 | 123.6237 | 123.1384 | 121.4081 | 119.8288 | 123.6511 | 117.6956 | -0.27466 | 121.4081 | 119.8288 | 117.6956 | 123.1384 | 123.6511 | -4.0649 | -123.7976
1521.9219 | 123.4406 | -121.2662 | 2.211 | -0.4302 | 0.050107 | -0.029642 | 0.08032 | -0.041873 | -0.022938 | 0.025794 | -1.3824 | 0.29755 | -1.7075 | 2.2018 | 1.8814 | -3.5706 | 1.9592 | 2.3758 | 2.3529 | -121.582 | 119.5587 | -1.9135 | 119.8837 | 123.468 | -0.32959 | -0.31586 | 0.14191 | 0.32501 | 123.2254 | 123.642 | 123.1476 | 121.5637 | 119.8837 | 123.6191 | 117.6956 | -0.31586 | 121.5637 | 119.8837 | 117.6956 | 123.1476 | 123.6191 | -3.9185 | -123.793
1522.9844 | 123.4634 | -122.2641 | 1.236 | -0.4302 | 0.016995 | -0.021098 | 0.067503 | -0.048281 | -0.045368 | 0.042884 | -1.3229 | 0.2243 | -1.68 | 1.1124 | 0.86975 | -3.9276 | 1.0162 | 1.3367 | 1.387 | -122.5845 | 120.5841 | -1.0117 | 120.9412 | 123.3765 | -0.36621 | -0.32044 | 0.15106 | 0.35706 | 123.2803 | 123.6008 | 123.1338 | 122.4884 | 120.9412 | 123.6511 | 118.3365 | -0.32044 | 122.4884 | 120.9412 | 118.3365 | 123.1338 | 123.6511 | -2.916 | -123.8205
1523.9219 | 123.4497 | -121.1792 | 2.2934 | -0.32338 | 0.041562 | -0.045664 | 0.069639 | -0.039736 | -0.02721 | 0.030067 | -1.1765 | 0.25635 | -1.5381 | 2.2705 | 1.8906 | -3.2272 | 2.0142 | 2.4353 | 2.417 | -121.5317 | 119.6411 | -2.037 | 120.0027 | 123.4497 | -0.40283 | -0.35248 | 0.1236 | 0.36163 | 123.1934 | 123.6145 | 123.0698 | 121.4355 | 120.0027 | 123.5962 | 117.952 | -0.35248 | 121.4355 | 120.0027 | 117.952 | 123.0698 | 123.5962 | -3.8315 | -123.8251
1524.9844 | 123.5504 | -122.2321 | 1.2405 | 0.11912 | 0.035153 | -0.015757 | 0.060026 | -0.051486 | -0.046436 | 0.043952 | -1.4465 | 0.16937 | -1.7761 | 1.0666 | 0.81024 | -3.7811 | 1.0941 | 1.3138 | 1.4236 | -122.5754 | 120.4559 | -1.0712 | 120.7855 | 123.2986 | -0.4303 | -0.34332 | 0.18311 | 0.32959 | 123.3261 | 123.5458 | 123.0423 | 122.4014 | 120.7855 | 123.6557 | 118.4509 | -0.34332 | 122.4014 | 120.7855 | 118.4509 | 123.0423 | 123.6557 | -3.0167 | -123.8159
1525.9219 | 123.4222 | -121.2891 | 2.2018 | -0.0029495 | 0.041562 | -0.014689 | 0.091001 | -0.049349 | -0.011188 | 0.031135 | -1.2863 | 0.25177 | -1.6708 | 2.2064 | 1.8494 | -3.2776 | 1.9272 | 2.3529 | 2.3346 | -121.6324 | 119.6182 | -1.9501 | 120.0027 | 123.4955 | -0.35248 | -0.34332 | 0.13275 | 0.38452 | 123.2162 | 123.642 | 123.1384 | 121.5408 | 120.0027 | 123.6237 | 118.0115 | -0.34332 | 121.5408 | 120.0027 | 118.0115 | 123.1384 | 123.6237 | -3.8727 | -123.8342
1526.9844 | 123.5641 | -121.4127 | 1.9775 | -0.14028 | 0.021267 | -0.0082804 | 0.06323 | -0.042941 | -0.037891 | 0.043952 | -1.2589 | 0.2243 | -1.6251 | 1.8127 | 1.5472 | -3.7354 | 1.9135 | 2.0142 | 2.1973 | -121.7972 | 119.7876 | -1.7532 | 120.1538 | 123.2254 | -0.4303 | -0.38452 | 0.21973 | 0.36621 | 123.3261 | 123.4268 | 122.9599 | 121.637 | 120.1538 | 123.6099 | 117.6773 | -0.38452 | 121.637 | 120.1538 | 117.6773 | 122.9599 | 123.6099 | -3.6026 | -123.7747
1527.9219 | 123.4818 | -121.4996 | 1.9821 | -0.44545 | 0.029812 | -0.022166 | 0.072843 | -0.05469 | -0.024006 | 0.037543 | -1.2955 | 0.23804 | -1.6525 | 1.8494 | 1.5198 | -3.7857 | 1.7624 | 2.0599 | 2.1103 | -121.875 | 119.8471 | -1.7441 | 120.2042 | 123.349 | -0.46234 | -0.37537 | 0.12817 | 0.35706 | 123.262 | 123.5596 | 123.0194 | 121.7377 | 120.2042 | 123.6099 | 117.7139 | -0.37537 | 121.7377 | 120.2042 | 117.7139 | 123.0194 | 123.6099 | -3.6346 | -123.8571
1528.9688 | 123.5138 | -121.3943 | 1.9913 | 0.11912 | 0.016995 | -0.015757 | 0.06323 | -0.053622 | -0.033619 | 0.036475 | -1.3412 | 0.20599 | -1.6571 | 1.8906 | 1.6434 | -3.8635 | 1.8768 | 2.092 | 2.211 | -121.8018 | 119.7372 | -1.7853 | 120.0531 | 123.2849 | -0.3479 | -0.40741 | 0.21973 | 0.31586 | 123.2712 | 123.4863 | 123.0377 | 121.6003 | 120.0531 | 123.6053 | 117.5308 | -0.40741 | 121.6003 | 120.0531 | 117.5308 | 123.0377 | 123.6053 | -3.6484 | -123.793
1529.9219 | 123.4634 | -122.0306 | 1.3962 | -0.23183 | 0.034085 | -0.016825 | 0.093137 | -0.051486 | -0.018665 | 0.030067 | -1.3275 | 0.2655 | -1.7258 | 1.3824 | 1.0391 | -4.39 | 1.1856 | 1.5198 | 1.5427 | -122.4106 | 120.3049 | -1.1307 | 120.7031 | 123.4131 | -0.35706 | -0.37994 | 0.14648 | 0.39825 | 123.2162 | 123.5504 | 123.0698 | 122.2961 | 120.7031 | 123.5733 | 117.6407 | -0.37994 | 122.2961 | 120.7031 | 117.6407 | 123.0698 | 123.5733 | -3.1219 | -123.8068
1530.9844 | 123.5825 | -122.2 | 1.2131 | 0.10386 | 0.019131 | -0.028574 | 0.058958 | -0.052554 | -0.036823 | 0.041816 | -1.2177 | 0.20599 | -1.6113 | 1.03 | 0.81482 | -4.3625 | 1.1215 | 1.2589 | 1.4053 | -122.5891 | 120.5887 | -1.0071 | 120.9824 | 123.23 | -0.39826 | -0.3891 | 0.19226 | 0.39368 | 123.3215 | 123.4589 | 123.0148 | 122.406 | 120.9824 | 123.6053 | 117.8375 | -0.3891 | 122.406 | 120.9824 | 117.8375 | 123.0148 | 123.6053 | -2.8244 | -123.8022
1531.9219 | 123.436 | -122.1954 | 1.2726 | -0.41494 | 0.019131 | -0.015757 | 0.08032 | -0.045077 | -0.015461 | 0.04502 | -1.2772 | 0.24719 | -1.6159 | 1.2131 | 0.94299 | -4.3625 | 1.0437 | 1.3779 | 1.4191 | -122.5433 | 120.5795 | -1.0254 | 120.9183 | 123.4085 | -0.32959 | -0.3479 | 0.14648 | 0.33875 | 123.2391 | 123.5733 | 123.1384 | 122.4426 | 120.9183 | 123.6145 | 117.8329 | -0.3479 | 122.4426 | 120.9183 | 117.8329 | 123.1384 | 123.6145 | -2.8885 | -123.8159
1532.9844 | 123.4039 | -122.3007 | 1.2131 | -0.33864 | 0.028744 | -0.05955 | 0.066434 | -0.051486 | -0.043232 | 0.040748 | -1.2909 | 0.25177 | -1.6113 | 1.1902 | 0.90179 | -4.3945 | 0.93384 | 1.3596 | 1.3458 | -122.5983 | 120.6894 | -0.9613 | 121.0098 | 123.4909 | -0.31128 | -0.29755 | 0.13275 | 0.32043 | 123.2346 | 123.6603 | 123.2025 | 122.5525 | 121.0098 | 123.6465 | 117.9062 | -0.29755 | 122.5525 | 121.0098 | 117.9062 | 123.2025 | 123.6465 | -2.8244 | -123.8113
1533.9219 | 123.555 | -122.2275 | 1.1993 | -0.30813 | 0.022336 | -0.016825 | 0.060026 | -0.052554 | -0.040028 | 0.041816 | -1.3 | 0.21973 | -1.6525 | 1.0437 | 0.75989 | -4.7104 | 1.0986 | 1.2222 | 1.3962 | -122.6212 | 120.575 | -0.97961 | 120.9274 | 123.2712 | -0.43945 | -0.39368 | 0.19684 | 0.35248 | 123.3261 | 123.4497 | 122.9874 | 122.4472 | 120.9274 | 123.6237 | 117.5171 | -0.39368 | 122.4472 | 120.9274 | 117.5171 | 122.9874 | 123.6237 | -2.8519 | -123.8205
1534.9844 | 123.5733 | -122.2 | 1.2131 | -0.21657 | 0.021267 | -0.045664 | 0.061094 | -0.061099 | -0.037891 | 0.032203 | -1.3733 | 0.24261 | -1.7349 | 1.0483 | 0.79651 | -4.6463 | 1.1353 | 1.2405 | 1.4191 | -122.5754 | 120.4651 | -0.97046 | 120.8267 | 123.2483 | -0.41656 | -0.37537 | 0.20599 | 0.36163 | 123.3353 | 123.4406 | 122.9965 | 122.4426 | 120.8267 | 123.6191 | 117.5537 | -0.37537 | 122.4426 | 120.8267 | 117.5537 | 122.9965 | 123.6191 | -2.948 | -123.7885
1535.9219 | 123.4634 | -122.2961 | 1.2085 | -0.64382 | 0.046902 | -0.010416 | 0.094205 | -0.045077 | -0.0058484 | 0.031135 | -1.3458 | 0.3067 | -1.7258 | 1.2177 | 0.84228 | -4.8569 | 0.98419 | 1.3321 | 1.355 | -122.6074 | 120.5704 | -0.90179 | 120.9503 | 123.5138 | -0.36621 | -0.31128 | 0.14648 | 0.37994 | 123.2803 | 123.6282 | 123.1384 | 122.6028 | 120.9503 | 123.6511 | 117.4393 | -0.31128 | 122.6028 | 120.9503 | 117.4393 | 123.1384 | 123.6511 | -2.9343 | -123.8159
1536.9844 | 123.5504 | -122.2733 | 1.1627 | -0.55227 | 0.036221 | -0.028574 | 0.072843 | -0.051486 | -0.017597 | 0.037543 | -1.4786 | 0.16937 | -1.8631 | 1.03 | 0.7782 | -4.9164 | 1.0895 | 1.2177 | 1.3596 | -122.6212 | 120.4102 | -0.99335 | 120.7947 | 123.3032 | -0.38452 | -0.3479 | 0.19684 | 0.38452 | 123.3627 | 123.4909 | 123.0515 | 122.4426 | 120.7947 | 123.6328 | 117.3569 | -0.3479 | 122.4426 | 120.7947 | 117.3569 | 123.0515 | 123.6328 | -3.0258 | -123.7839
1537.9219 | 123.5504 | -122.2733 | 1.149 | -0.3539 | 0.021267 | -0.029642 | 0.072843 | -0.055758 | -0.024006 | 0.043952 | -1.5656 | 0.21057 | -1.7761 | 0.99792 | 0.66834 | -4.8843 | 1.0941 | 1.1902 | 1.3596 | -122.6349 | 120.4971 | -0.93842 | 120.7077 | 123.2712 | -0.48065 | -0.36163 | 0.21057 | 0.21057 | 123.3673 | 123.4634 | 122.9416 | 122.4838 | 120.7077 | 123.6328 | 117.3889 | -0.36163 | 122.4838 | 120.7077 | 117.3889 | 122.9416 | 123.6328 | -2.9251 | -123.7839
1538.9219 | 123.642 | -122.2778 | 1.1536 | -0.36916 | 0.019131 | -0.020029 | 0.064298 | -0.05469 | -0.029346 | 0.036475 | -1.4008 | 0.21973 | -1.7349 | 1.0117 | 0.69122 | -4.747 | 1.0757 | 1.2039 | 1.3824 | -122.5754 | 120.5429 | -0.93384 | 120.8771 | 123.2895 | -0.46234 | -0.29755 | 0.22888 | 0.33417 | 123.3536 | 123.4818 | 122.9691 | 122.4976 | 120.8771 | 123.6603 | 117.5308 | -0.29755 | 122.4976 | 120.8771 | 117.5308 | 122.9691 | 123.6603 | -2.8885 | -123.7289
1539.9844 | 123.5275 | -121.5179 | 1.9089 | 0.22593 | 0.020199 | -0.029642 | 0.058958 | -0.061099 | -0.043232 | 0.036475 | -1.4557 | 0.17853 | -1.7899 | 1.7624 | 1.442 | -4.2938 | 1.7899 | 1.9638 | 2.0828 | -121.8933 | 119.7281 | -1.7303 | 120.0623 | 123.2803 | -0.46692 | -0.37537 | 0.17395 | 0.33417 | 123.3078 | 123.4818 | 122.9599 | 121.6965 | 120.0623 | 123.6008 | 117.2241 | -0.37537 | 121.6965 | 120.0623 | 117.2241 | 122.9599 | 123.6008 | -3.6987 | -123.8022
1540.9219 | 123.5641 | -122.3145 | 1.1124 | 0.43956 | 0.036221 | -0.016825 | 0.076048 | -0.051486 | -0.026142 | 0.036475 | -1.4923 | 0.21515 | -1.8951 | 0.98877 | 0.68207 | -4.5181 | 1.0162 | 1.1353 | 1.2772 | -122.7264 | 120.4193 | -0.89722 | 120.8221 | 123.3032 | -0.4303 | -0.41199 | 0.1648 | 0.40283 | 123.3307 | 123.4497 | 122.9965 | 122.5296 | 120.8221 | 123.5916 | 117.7963 | -0.41199 | 122.5296 | 120.8221 | 117.7963 | 122.9965 | 123.5916 | -3.0075 | -123.8388
1541.9844 | 123.5001 | -122.2595 | 1.1536 | 0.25645 | 0.031949 | -0.0050764 | 0.070707 | -0.056826 | -0.025074 | 0.036475 | -1.5198 | 0.23804 | -1.8494 | 1.0529 | 0.75989 | -4.4769 | 1.03 | 1.236 | 1.3229 | -122.6486 | 120.4102 | -0.91553 | 120.7397 | 123.3124 | -0.39368 | -0.3891 | 0.16937 | 0.32959 | 123.2895 | 123.4955 | 123.0194 | 122.4976 | 120.7397 | 123.5825 | 117.7826 | -0.3891 | 122.4976 | 120.7397 | 117.7826 | 123.0194 | 123.5825 | -3.0029 | -123.8022
1542.9219 | 123.5825 | -122.1359 | 1.2177 | -0.79641 | 0.021267 | -0.028574 | 0.056821 | -0.072848 | -0.033619 | 0.035407 | -1.4374 | 0.21515 | -1.799 | 1.0345 | 0.73242 | -4.4266 | 1.149 | 1.2314 | 1.4236 | -122.5616 | 120.3369 | -1.0025 | 120.6985 | 123.1705 | -0.48523 | -0.42572 | 0.20599 | 0.36163 | 123.2849 | 123.3673 | 122.8683 | 122.3511 | 120.6985 | 123.5596 | 117.7094 | -0.42572 | 122.3511 | 120.6985 | 117.7094 | 122.8683 | 123.5596 | -3.0167 | -123.7793
1543.9844 | 123.5413 | -121.3165 | 1.1719 | -0.0029495 | 0.022336 | -0.032847 | 0.071775 | -0.065371 | -0.037891 | 0.037543 | -1.4969 | 0.22888 | 0.28839 | 1.0117 | 0.68665 | -6.1066 | 1.0895 | 1.2039 | 1.3596 | -137.0178 | 121.6049 | -0.94299 | 119.8196 | 122.3282 | -0.48523 | -15.7013 | 0.18768 | -1.7853 | 122.406 | 122.5204 | 122.0032 | 121.5454 | 119.8196 | 122.6761 | 115.21 | -15.7013 | 121.5454 | 119.8196 | 115.21 | 122.0032 | 122.6761 | -0.88348 | -138.1897
1544.9219 | 123.5367 | -122.2183 | 1.1581 | -0.36916 | 0.0084498 | -0.028574 | 0.074979 | -0.057894 | -0.033619 | 0.036475 | -1.1581 | 0.19226 | -1.7761 | 1.0529 | 0.6546 | -4.4632 | 1.062 | 1.1902 | 1.3367 | -122.6395 | 120.4422 | -0.96588 | 121.0602 | 123.2712 | -0.50354 | -0.42114 | 0.17853 | 0.61798 | 123.2803 | 123.4085 | 122.8729 | 122.4106 | 121.0602 | 123.555 | 117.7551 | -0.42114 | 122.4106 | 121.0602 | 117.7551 | 122.8729 | 123.555 | -2.9343 | -123.7976
1545.9375 | 123.5458 | -119.696 | 1.4282 | 0.11912 | 0.035153 | -0.021098 | 0.071775 | -0.062167 | -0.02721 | 0.031135 | -1.3962 | 0.23346 | 2.2659 | 1.3824 | 1.3367 | -5.2322 | 1.3 | 1.3046 | 1.6479 | -149.9954 | 121.962 | -1.1948 | 118.2999 | 121.0785 | -0.091553 | -30.2994 | 0.21973 | -3.6621 | 120.9961 | 121.0007 | 121.0327 | 119.9295 | 118.2999 | 121.344 | 114.4638 | -30.2994 | 119.9295 | 118.2999 | 114.4638 | 121.0327 | 121.344 | 0.83771 | -151.4236
1546.9844 | 123.5779 | -122.0581 | 1.7258 | 0.39378 | 0.027676 | -0.049937 | 0.072843 | -0.066439 | -0.028278 | 0.035407 | -1.474 | 0.20599 | -1.3687 | 1.5747 | 1.0391 | -3.3737 | 1.6342 | 1.7624 | 1.8768 | -120.7352 | 120.6894 | -1.5198 | 120.5841 | 123.6328 | -0.68665 | 1.3229 | 0.15106 | -0.10529 | 123.6923 | 123.8205 | 123.0972 | 122.2641 | 120.5841 | 123.9349 | 118.6844 | 1.3229 | 122.2641 | 120.5841 | 118.6844 | 123.0972 | 123.9349 | -3.0945 | -122.4609
1547.9219 | 123.555 | -119.8334 | 2.037 | 0.27171 | 0.020199 | -0.011485 | 0.071775 | -0.053622 | -0.042164 | 0.028999 | -1.3779 | 0.18768 | 2.298 | 1.9455 | -9.1873 | -4.7058 | 1.8906 | 2.0691 | 2.1698 | -149.9954 | 122.1313 | -1.8494 | 118.4555 | 121.7789 | -11.2244 | -30.162 | 0.13275 | -3.6758 | 121.7239 | 121.9025 | 110.6461 | 120.0211 | 118.4555 | 122.0032 | 115.1276 | -30.162 | 120.0211 | 118.4555 | 115.1276 | 110.6461 | 122.0032 | 0.26093 | -152.0325
1548.9688 | 123.2162 | -117.8284 | 1.9089 | -0.033467 | 0.046902 | -0.032847 | 0.094205 | -0.053622 | -0.015461 | 0.033271 | -1.4053 | 0.26093 | 1.7258 | 1.9089 | 1.7441 | -3.1723 | 1.7303 | 2.037 | 2.0691 | -130.632 | 119.5541 | -1.648 | 116.423 | 119.7372 | -0.1648 | -12.8037 | 0.16022 | -3.1311 | 119.5587 | 119.8654 | 119.5724 | 118.0893 | 116.423 | 119.8975 | 114.6561 | -12.8037 | 118.0893 | 116.423 | 114.6561 | 119.5724 | 119.8975 | -0.18311 | -132.5409
1549.9219 | 123.5046 | -115.654 | 1.9409 | 0.30223 | 0.02554 | -0.027506 | 0.073911 | -0.060031 | -0.035755 | 0.03968 | -1.68 | 0.21515 | 0.62714 | 1.9363 | -23.5062 | -7.4982 | 1.8082 | 1.9913 | 2.092 | -149.9954 | 116.2811 | -1.7258 | 113.974 | 117.5903 | -25.4471 | -34.3414 | 0.15106 | -2.3071 | 117.4622 | 117.6453 | 92.1478 | 115.8691 | 113.974 | 117.746 | 108.1558 | -34.3414 | 115.8691 | 113.974 | 108.1558 | 92.1478 | 117.746 | -1.3138 | -151.9363
1551 | 123.4177 | -121.5363 | 1.8082 | -0.27761 | 0.023404 | -0.037119 | 0.070707 | -0.066439 | -0.036823 | 0.034339 | -1.3184 | 0.20142 | 2.2247 | 1.6754 | 1.2863 | -4.0237 | 1.7303 | 1.68 | 2.005 | -120.7352 | 123.761 | -1.6068 | 120.2179 | 123.2117 | -0.52185 | 0.80109 | 0.19684 | -3.5431 | 123.2666 | 123.2162 | 122.8226 | 121.7377 | 120.2179 | 123.5413 | 117.5125 | 0.80109 | 121.7377 | 120.2179 | 117.5125 | 122.8226 | 123.5413 | 0.41656 | -122.5433
1551.9219 | 123.5687 | -120.195 | 1.9363 | -0.079243 | 0.018063 | -0.040324 | 0.067503 | -0.051486 | -0.037891 | 0.040748 | -1.2177 | 0.23346 | 0.86517 | 1.7899 | 1.3962 | -3.6896 | 1.9821 | 2.0325 | 2.1378 | -138.6246 | 121.0602 | -1.7029 | 118.9774 | 121.9849 | -0.54016 | -18.4296 | 0.20142 | -2.0828 | 122.1771 | 122.2275 | 121.5912 | 120.4285 | 118.9774 | 122.3328 | 116.5054 | -18.4296 | 120.4285 | 118.9774 | 116.5054 | 121.5912 | 122.3328 | -1.0712 | -140.5609
1552.9844 | 123.5687 | -117.6956 | 1.9226 | 0.348 | 0.034085 | -0.023234 | 0.089933 | -0.060031 | -0.019733 | 0.037543 | -1.5289 | 0.2243 | -0.93842 | 1.8127 | 0.97046 | -5.0995 | 1.886 | 2.0462 | 2.1057 | -144.223 | 116.7572 | -1.6983 | 116.1667 | 119.5084 | -0.95215 | -26.5274 | 0.18311 | -0.59052 | 119.5816 | 119.7418 | 118.6661 | 117.9199 | 116.1667 | 119.8013 | 112.5961 | -26.5274 | 117.9199 | 116.1667 | 112.5961 | 118.6661 | 119.8013 | -2.861 | -146.1456
1553.9219 | 123.4955 | -121.5088 | 1.8356 | 0.14964 | 0.020199 | -0.037119 | 0.070707 | -0.067507 | -0.034687 | 0.036475 | -1.4053 | 0.2243 | -1.7075 | 1.7075 | 1.3641 | -3.923 | 1.6983 | 1.9135 | 1.9867 | -121.9894 | 119.8013 | -1.6113 | 120.1035 | 123.2162 | -0.4715 | -0.48065 | 0.15106 | 0.30212 | 123.2071 | 123.4222 | 122.8729 | 121.7331 | 120.1035 | 123.4955 | 117.5858 | -0.48065 | 121.7331 | 120.1035 | 117.5858 | 122.8729 | 123.4955 | -3.5431 | -123.8251
1554.9844 | 123.5184 | -121.225 | 2.1378 | 0.4243 | 0.031949 | -0.018961 | 0.074979 | -0.066439 | -0.047504 | 0.033271 | -1.3138 | 0.23804 | -1.6617 | 2.0279 | 1.5976 | -3.7628 | 2.0187 | 2.1881 | 2.2934 | -121.6599 | 119.5633 | -1.8997 | 119.9112 | 123.2529 | -0.54016 | -0.43488 | 0.15564 | 0.3479 | 123.2437 | 123.4131 | 122.8226 | 121.463 | 119.9112 | 123.5184 | 117.4622 | -0.43488 | 121.463 | 119.9112 | 117.4622 | 122.8226 | 123.5184 | -3.7994 | -123.7976
1555.9375 | 123.5367 | -121.5363 | 1.8356 | 0.027569 | 0.03088 | -0.040324 | 0.070707 | -0.058962 | -0.030414 | 0.035407 | -1.3367 | 0.23346 | -1.6251 | 1.8036 | 1.3916 | -3.8361 | 1.4282 | 1.7944 | 2.0416 | -121.9711 | 119.9112 | -1.6022 | 120.1996 | 123.3398 | -0.44403 | -0.43488 | 0.20599 | 0.28839 | 122.9645 | 123.3307 | 122.9279 | 121.7697 | 120.1996 | 123.5779 | 117.7002 | -0.43488 | 121.7697 | 120.1996 | 117.7002 | 122.9279 | 123.5779 | -3.4607 | -123.8068
1556.9844 | 123.5367 | -121.463 | 1.9592 | -0.079243 | 0.019131 | -0.018961 | 0.069639 | -0.062167 | -0.043232 | 0.035407 | -1.2634 | 0.17395 | -1.5701 | 1.8265 | 1.4374 | -3.6758 | 1.8265 | 2.0096 | 2.124 | -121.8155 | 119.8929 | -1.7853 | 120.1996 | 123.2895 | -0.52185 | -0.35248 | 0.16479 | 0.3067 | 123.2895 | 123.4726 | 122.9004 | 121.637 | 120.1996 | 123.587 | 117.7872 | -0.35248 | 121.637 | 120.1996 | 117.7872 | 122.9004 | 123.587 | -3.5294 | -123.7747
1557.9219 | 123.5458 | -121.5179 | 1.9043 | 0.48533 | 0.052243 | -0.0040084 | 0.093137 | -0.069644 | -0.030414 | 0.034339 | -1.3184 | 0.23804 | -1.6937 | 1.8723 | 1.3916 | -3.8361 | 1.7853 | 1.9775 | 2.0645 | -121.8842 | 119.8242 | -1.6663 | 120.1996 | 123.3902 | -0.51269 | -0.36621 | 0.16022 | 0.37537 | 123.3032 | 123.4955 | 122.9095 | 121.756 | 120.1996 | 123.5825 | 117.6819 | -0.36621 | 121.756 | 120.1996 | 117.6819 | 122.9095 | 123.5825 | -3.598 | -123.7885
1558.9844 | 123.4772 | -121.8109 | 1.6525 | -0.23183 | 0.051175 | -0.02537 | 0.092069 | -0.051486 | -0.0037124 | 0.037543 | -1.2222 | 0.2655 | -1.6388 | 1.6342 | 1.2497 | -3.8452 | 1.4557 | 1.767 | 1.7853 | -122.1725 | 120.1721 | -1.387 | 120.5887 | 123.4451 | -0.40283 | -0.36163 | 0.13275 | 0.41657 | 123.2666 | 123.5779 | 123.0606 | 122.0764 | 120.5887 | 123.5962 | 117.9657 | -0.36163 | 122.0764 | 120.5887 | 117.9657 | 123.0606 | 123.5962 | -3.2913 | -123.8251
1559.9219 | 123.5367 | -121.7972 | 1.5701 | 0.25645 | 0.036221 | 0.0013326 | 0.067503 | -0.044009 | -0.031483 | 0.031135 | -1.2817 | 0.20142 | -1.6388 | 1.4603 | 1.149 | -4.1794 | 1.4923 | 1.6296 | 1.7487 | -122.2183 | 120.1584 | -1.3687 | 120.5154 | 123.2574 | -0.42114 | -0.42114 | 0.17853 | 0.35706 | 123.2895 | 123.4268 | 122.9462 | 121.9986 | 120.5154 | 123.5458 | 117.6178 | -0.42114 | 121.9986 | 120.5154 | 117.6178 | 122.9462 | 123.5458 | -3.2089 | -123.7885
1561 | 123.4497 | -121.7697 | 1.6846 | 3.9338 | 0.043698 | -0.010416 | 0.091001 | -0.0376 | -0.024006 | 0.037543 | -1.1444 | 0.30212 | -1.5518 | 1.6983 | 1.3504 | -3.9185 | 1.4145 | 1.8356 | 1.8265 | -122.0993 | 120.2179 | -1.3824 | 120.6253 | 123.468 | -0.33417 | -0.32959 | 0.14191 | 0.40741 | 123.1842 | 123.6053 | 123.1201 | 122.0718 | 120.6253 | 123.5962 | 117.8513 | -0.32959 | 122.0718 | 120.6253 | 117.8513 | 123.1201 | 123.5962 | -3.2364 | -123.7839
1561.9219 | 123.5641 | -121.7834 | 1.6022 | -0.12502 | 0.021267 | -0.031779 | 0.061094 | -0.05469 | -0.0443 | 0.033271 | -1.3275 | 0.23804 | -1.68 | 1.4099 | 0.97046 | -4.1473 | 1.4969 | 1.6067 | 1.7807 | -122.2183 | 120.1035 | -1.3641 | 120.4559 | 123.1934 | -0.63171 | -0.43488 | 0.17853 | 0.35248 | 123.2803 | 123.3902 | 122.7539 | 122.0215 | 120.4559 | 123.5641 | 117.6361 | -0.43488 | 122.0215 | 120.4559 | 117.6361 | 122.7539 | 123.5641 | -3.2822 | -123.8205
1562.9844 | 123.4772 | -121.0327 | 2.3163 | 0.48533 | 0.04797 | 0.00026463 | 0.084592 | -0.057894 | -0.013325 | 0.030067 | -1.3092 | 0.24719 | 0.56763 | 2.3209 | 1.6937 | -3.5248 | 2.1469 | 2.4582 | 2.4307 | -121.582 | 121.6003 | -2.0691 | 119.7235 | 123.3536 | -0.62256 | -0.54932 | 0.11444 | -1.8768 | 123.1796 | 123.4909 | 122.7264 | 121.2799 | 119.7235 | 123.4634 | 117.5079 | -0.54932 | 121.2799 | 119.7235 | 117.5079 | 122.7264 | 123.4634 | -1.7487 | -123.8983
1563.9219 | 123.5321 | -119.3253 | 2.3254 | 0.348 | 0.035153 | -0.023234 | 0.062162 | -0.057894 | -0.028278 | 0.036475 | -1.3458 | 0.2243 | 1.0162 | 2.2293 | 1.8448 | -3.2684 | 2.211 | 2.5406 | 2.5177 | -149.1806 | 120.3415 | -2.1011 | 117.9794 | 121.5546 | -0.48065 | -29.8553 | 0.19226 | -2.3621 | 121.5363 | 121.8658 | 121.17 | 119.5496 | 117.9794 | 121.843 | 116.0568 | -29.8553 | 119.5496 | 117.9794 | 116.0568 | 121.17 | 121.843 | -1.3092 | -151.506
1564.9844 | 123.5641 | -120.9915 | 2.3346 | -0.1708 | 0.034085 | -0.0040084 | 0.072843 | -0.056826 | -0.024006 | 0.038612 | -1.4053 | 0.21515 | 0.42114 | 2.2064 | 1.5656 | -3.8269 | 2.2568 | 2.3438 | 2.5085 | -121.4584 | 121.4127 | -2.1194 | 119.5862 | 123.1979 | -0.76904 | -0.46692 | 0.17395 | -1.8265 | 123.2483 | 123.3353 | 122.5571 | 121.2067 | 119.5862 | 123.5001 | 117.1646 | -0.46692 | 121.2067 | 119.5862 | 117.1646 | 122.5571 | 123.5001 | -1.9135 | -123.793
1565.9219 | 123.5184 | -121.0281 | 2.3849 | 0.13438 | 0.020199 | -0.026438 | 0.056821 | -0.057894 | -0.038959 | 0.038612 | -1.4328 | 0.21057 | -1.7258 | 2.2934 | 1.8311 | -4.184 | 2.0554 | 2.417 | 2.5223 | -121.4401 | 119.3024 | -2.1744 | 119.5953 | 123.3215 | -0.55389 | -0.41199 | 0.13733 | 0.29297 | 123.0835 | 123.4451 | 122.8592 | 121.2387 | 119.5953 | 123.5504 | 116.8442 | -0.41199 | 121.2387 | 119.5953 | 116.8442 | 122.8592 | 123.5504 | -4.1107 | -123.8251
1566.9844 | 123.5458 | -120.6894 | 2.6779 | 0.48533 | 0.045834 | -0.021098 | 0.081388 | -0.061099 | 0.048626 | 0.099494 | -3.0533 | 0.23804 | -3.4103 | 2.6413 | -119.4214 | -25.1862 | 2.5909 | 2.7649 | 2.8519 | -121.0968 | 117.2791 | -2.4399 | 117.6361 | 123.3307 | -122.0993 | -0.40741 | 0.17395 | 0.35705 | 123.2803 | 123.4543 | 1.268 | 120.9274 | 117.6361 | 123.5413 | 95.5032 | -0.40741 | 120.9274 | 117.6361 | 95.5032 | 1.268 | 123.5413 | -6.0883 | -123.7747
1567.9219 | 123.5825 | -120.433 | 2.8976 | 0.43956 | 0.028744 | -0.0029404 | 0.061094 | -0.052554 | 0.036877 | 0.1027 | -2.9068 | 0.21057 | -3.273 | 2.8473 | -118.3777 | -24.5682 | 2.742 | 2.8702 | 3.1082 | -120.8725 | 117.16 | -2.6871 | 117.5262 | 123.2803 | -121.2753 | -0.43945 | 0.21057 | 0.36621 | 123.175 | 123.3032 | 2.0554 | 120.6436 | 117.5262 | 123.5413 | 95.8649 | -0.43945 | 120.6436 | 117.5262 | 95.8649 | 2.0554 | 123.5413 | -6.1707 | -123.7701
1568.9844 | 123.4497 | -120.3415 | 3.1448 | -0.23183 | 0.028744 | -0.0093484 | 0.085661 | -0.062167 | 0.030468 | 0.11018 | -2.8885 | 0.24719 | -3.2455 | 3.1128 | -118.103 | -24.234 | 2.8702 | 3.2959 | 3.2639 | -120.6528 | 117.0959 | -2.8976 | 117.453 | 123.4543 | -121.2479 | -0.31128 | 0.11902 | 0.35706 | 123.2117 | 123.6374 | 2.2385 | 120.5887 | 117.453 | 123.6053 | 96.1075 | -0.31128 | 120.5887 | 117.453 | 96.1075 | 2.2385 | 123.6053 | -6.3904 | -123.7976
1569.9219 | 123.4131 | -120.6619 | 2.829 | 0.348 | 0.049038 | 0.0066726 | 0.091001 | -0.051486 | 0.052898 | 0.094154 | -2.9205 | 0.2655 | -3.2547 | 2.8564 | -118.4097 | -24.2294 | 2.5635 | 2.9755 | 2.9205 | -120.9732 | 117.4072 | -2.5635 | 117.7414 | 123.5184 | -121.2387 | -0.31128 | 0.091553 | 0.33417 | 123.2254 | 123.6374 | 2.2522 | 120.9274 | 117.7414 | 123.5825 | 96.4325 | -0.31128 | 120.9274 | 117.7414 | 96.4325 | 2.2522 | 123.5825 | -6.0837 | -123.8022
1570.9844 | 123.468 | -119.8151 | 3.598 | -0.079243 | 0.049038 | -0.032847 | 0.086729 | -0.047213 | 0.044354 | 0.10377 | -2.7878 | 0.27008 | -3.186 | 3.5889 | -117.6086 | -23.5611 | 3.4149 | 3.7262 | 3.7491 | -120.1904 | 116.629 | -3.3279 | 117.0273 | 123.4039 | -121.2067 | -0.37537 | 0.15106 | 0.39825 | 123.23 | 123.5413 | 2.2064 | 120.0851 | 117.0273 | 123.5641 | 96.254 | -0.37537 | 120.0851 | 117.0273 | 96.254 | 2.2064 | 123.5641 | -6.7841 | -123.7885
1571.9219 | 123.4406 | -121.2936 | 2.179 | 0.47007 | 0.044766 | -0.016825 | 0.076048 | -0.05469 | 0.052898 | 0.099494 | -3.0441 | 0.26093 | -3.3691 | 2.0691 | -119.5908 | -24.1058 | 1.8951 | 2.3026 | 2.3026 | -121.6324 | 117.9245 | -1.918 | 118.2495 | 123.3627 | -121.7697 | -0.33875 | 0.1236 | 0.32501 | 123.1888 | 123.5962 | 1.7029 | 121.5546 | 118.2495 | 123.5962 | 97.1878 | -0.33875 | 121.5546 | 118.2495 | 97.1878 | 1.7029 | 123.5962 | -5.5481 | -123.8113
1572.9844 | 123.4726 | -121.3989 | 2.037 | -0.36916 | 0.043698 | -0.037119 | 0.08032 | -0.044009 | 0.04649 | 0.11018 | -3.0258 | 0.24261 | -3.3783 | 2.0096 | -120.1721 | -23.9822 | 1.8127 | 2.1515 | 2.1744 | -121.7468 | 118.0206 | -1.7944 | 118.3731 | 123.4085 | -122.2092 | -0.3479 | 0.13733 | 0.35248 | 123.2117 | 123.5504 | 1.2268 | 121.6415 | 118.3731 | 123.5733 | 97.4167 | -0.3479 | 121.6415 | 118.3731 | 97.4167 | 1.2268 | 123.5733 | -5.4153 | -123.7839
1573.9219 | 123.4543 | -121.0831 | 2.3529 | 0.13438 | 0.041562 | -0.016825 | 0.086729 | -0.046145 | 0.062512 | 0.098426 | -2.9572 | 0.2655 | -3.3325 | 2.3666 | -118.6981 | -23.2956 | 2.124 | 2.5177 | 2.4994 | -121.4081 | 117.7505 | -2.0874 | 118.1259 | 123.4497 | -121.051 | -0.32501 | 0.14649 | 0.37537 | 123.2071 | 123.6008 | 2.3849 | 121.3486 | 118.1259 | 123.5825 | 97.7875 | -0.32501 | 121.3486 | 118.1259 | 97.7875 | 2.3849 | 123.5825 | -5.6854 | -123.761
1574.9844 | 123.587 | -120.8817 | 2.5131 | -0.18605 | 0.029812 | -0.0072124 | 0.051481 | -0.050418 | 0.034741 | 0.11445 | -2.8564 | 0.21057 | -3.1998 | 2.2797 | -118.84 | -23.1262 | 2.4216 | 2.5497 | 2.6962 | -121.2799 | 117.6819 | -2.3026 | 118.0252 | 123.1613 | -121.3531 | -0.39825 | 0.1831 | 0.34332 | 123.3032 | 123.4314 | 2.0416 | 121.0922 | 118.0252 | 123.5779 | 97.7554 | -0.39825 | 121.0922 | 118.0252 | 97.7554 | 2.0416 | 123.5779 | -5.7129 | -123.793
1575.9219 | 123.5458 | -120.7489 | 2.6093 | 2.3316 | 0.031949 | -0.017893 | 0.065366 | -0.045077 | 0.031536 | 0.10484 | -2.9297 | 0.1831 | -3.4058 | 2.4765 | -118.2175 | -22.9202 | 2.5543 | 2.6642 | 2.7924 | -121.17 | 117.3431 | -2.4261 | 117.8192 | 123.2254 | -120.8267 | -0.42114 | 0.18311 | 0.47608 | 123.3032 | 123.4131 | 2.5314 | 120.932 | 117.8192 | 123.5413 | 97.8287 | -0.42114 | 120.932 | 117.8192 | 97.8287 | 2.5314 | 123.5413 | -6.015 | -123.7793
1576.9844 | 123.4772 | -120.3827 | 3.0624 | -0.26235 | 0.040494 | -0.023234 | 0.078184 | -0.05469 | 0.048626 | 0.099494 | -2.9297 | 0.25635 | -3.2822 | 3.0624 | -118.4143 | -22.1008 | 2.8748 | 3.1815 | 3.2272 | -120.7123 | 117.1005 | -2.8061 | 117.453 | 123.4451 | -121.4767 | -0.32959 | 0.1648 | 0.35248 | 123.2574 | 123.5641 | 1.9684 | 120.639 | 117.453 | 123.6099 | 98.2819 | -0.32959 | 120.639 | 117.453 | 98.2819 | 1.9684 | 123.6099 | -6.3446 | -123.7747
1577.9219 | 123.4726 | -120.401 | 3.0212 | -0.063984 | 0.036221 | 0.0024006 | 0.086729 | -0.048281 | -0.0090524 | 0.035407 | -1.387 | 0.25635 | -1.8036 | 3.2043 | 1.5884 | -3.5385 | 2.8152 | 3.1174 | 3.1677 | -120.7809 | 118.5974 | -2.7649 | 119.014 | 123.6053 | -1.4328 | -0.37994 | 0.14648 | 0.41657 | 123.2162 | 123.5184 | 121.9894 | 120.6573 | 119.014 | 123.5687 | 116.8625 | -0.37994 | 120.6573 | 119.014 | 116.8625 | 121.9894 | 123.5687 | -4.8248 | -123.8022
1578.9844 | 123.4589 | -120.369 | 3.0487 | -0.73537 | 0.037289 | -0.026438 | 0.074979 | -0.048281 | -0.018665 | 0.042884 | -1.3596 | 0.31586 | -1.6937 | 3.035 | 2.6321 | -3.1311 | 2.8152 | 3.2089 | 3.1998 | -120.7306 | 118.6752 | -2.7328 | 119.0094 | 123.4039 | -0.41657 | -0.36163 | 0.15106 | 0.33417 | 123.1842 | 123.5779 | 123.0011 | 120.6848 | 119.0094 | 123.5687 | 117.2379 | -0.36163 | 120.6848 | 119.0094 | 117.2379 | 123.0011 | 123.5687 | -4.7424 | -123.7793
1579.9219 | 123.4039 | -120.2866 | 3.1448 | 0.77525 | 0.046902 | -0.0093484 | 0.089933 | -0.047213 | -0.013325 | 0.031135 | -1.3916 | 0.27924 | -1.7395 | 3.186 | 2.8107 | -2.9526 | 2.8793 | 3.3508 | 3.2684 | -120.607 | 118.5471 | -2.8656 | 118.895 | 123.4726 | -0.33417 | -0.32044 | 0.1236 | 0.3479 | 123.1659 | 123.6374 | 123.0972 | 120.5658 | 118.895 | 123.555 | 117.334 | -0.32044 | 120.5658 | 118.895 | 117.334 | 123.0972 | 123.555 | -4.8843 | -123.7518
1580.9844 | 123.4497 | -120.6024 | 2.8427 | -0.033467 | 0.036221 | -0.010416 | 0.074979 | -0.046145 | -0.017597 | 0.038612 | -1.3916 | 0.28381 | -0.36621 | 2.8061 | 2.3666 | -3.0808 | 2.5772 | 2.98 | 2.9572 | -120.9457 | 120.2362 | -2.5589 | 119.2108 | 123.4085 | -0.47607 | -0.34332 | 0.11444 | -1.0254 | 123.1796 | 123.5825 | 122.9691 | 120.8862 | 119.2108 | 123.5596 | 117.5217 | -0.34332 | 120.8862 | 119.2108 | 117.5217 | 122.9691 | 123.5596 | -3.2089 | -123.7885
1581.9219 | 123.4543 | -120.5566 | 2.8839 | -0.033467 | 0.045834 | 0.0034686 | 0.073911 | -0.040805 | 0.04649 | 0.095222 | -3.0212 | 0.23804 | -3.4012 | 3.0121 | -118.5883 | -22.76 | 2.6413 | 2.9526 | 3.0075 | -120.932 | 117.1555 | -2.6459 | 117.5354 | 123.5687 | -121.4722 | -0.37537 | 0.1236 | 0.37994 | 123.1979 | 123.5092 | 1.9684 | 120.7947 | 117.5354 | 123.5641 | 97.7966 | -0.37537 | 120.7947 | 117.5354 | 97.7966 | 1.9684 | 123.5641 | -6.2851 | -123.8159
1582.9844 | 123.5733 | -120.314 | 3.0716 | -0.30813 | 0.018063 | -0.011485 | 0.064298 | -0.053622 | 0.027264 | 0.11445 | -2.8793 | 0.21057 | -3.1952 | 2.8793 | -119.0369 | -22.0825 | 2.9892 | 3.0991 | 3.2547 | -120.7169 | 117.1188 | -2.861 | 117.4347 | 123.1934 | -122.1085 | -0.40283 | 0.18311 | 0.31586 | 123.3032 | 123.4131 | 1.2772 | 120.5246 | 117.4347 | 123.5687 | 98.2315 | -0.40283 | 120.5246 | 117.4347 | 98.2315 | 1.2772 | 123.5687 | -6.2668 | -123.7885
1583.9219 | 123.468 | -120.3918 | 3.0441 | -0.27761 | 0.046902 | -0.033915 | 0.08032 | -0.046145 | 0.044354 | 0.10911 | -2.8381 | 0.2655 | -3.2089 | 3.0121 | -118.6249 | -21.9955 | 2.8336 | 3.1723 | 3.1815 | -120.7489 | 117.1829 | -2.7786 | 117.5537 | 123.4039 | -121.669 | -0.35706 | 0.13733 | 0.37079 | 123.2254 | 123.5641 | 1.767 | 120.6573 | 117.5537 | 123.5733 | 98.3963 | -0.35706 | 120.6573 | 117.5537 | 98.3963 | 1.767 | 123.5733 | -6.2531 | -123.793
1584.9844 | 123.5687 | -120.5475 | 2.8107 | -0.26235 | 0.018063 | -0.015757 | 0.05789 | -0.056826 | 0.020855 | 0.10697 | -2.861 | 0.21973 | -3.2089 | 2.623 | -118.5974 | -22.1741 | 2.7191 | 2.8427 | 2.9846 | -120.9686 | 117.3386 | -2.5909 | 117.6865 | 123.1705 | -121.4081 | -0.42114 | 0.17395 | 0.3479 | 123.2666 | 123.3902 | 1.9501 | 120.7672 | 117.6865 | 123.5321 | 98.3734 | -0.42114 | 120.7672 | 117.6865 | 98.3734 | 1.9501 | 123.5321 | -6.0196 | -123.7793
1585.9375 | 123.5046 | -120.2728 | 3.0808 | 0.39378 | 0.026608 | -0.023234 | 0.070707 | -0.058962 | 0.033672 | 0.094154 | -2.9068 | 0.21057 | -3.2501 | 2.9388 | -118.4555 | -21.9086 | 2.9938 | 3.1494 | 3.2593 | -120.694 | 117.0227 | -2.8702 | 117.366 | 123.2117 | -121.5363 | -0.42114 | 0.17853 | 0.34332 | 123.2666 | 123.4222 | 1.8173 | 120.4834 | 117.366 | 123.5321 | 98.3643 | -0.42114 | 120.4834 | 117.366 | 98.3643 | 1.8173 | 123.5321 | -6.3309 | -123.7747
1586.9844 | 123.5229 | -120.5887 | 2.7924 | -0.38442 | 0.024472 | -0.012553 | 0.073911 | -0.056826 | 0.027264 | 0.098426 | -2.8976 | 0.21515 | -3.2776 | 2.6459 | -119.4031 | -22.3114 | 2.6779 | 2.8519 | 2.9938 | -121.0052 | 117.3111 | -2.5772 | 117.691 | 123.2346 | -122.1954 | -0.41657 | 0.20142 | 0.37994 | 123.2666 | 123.4406 | 1.1856 | 120.8038 | 117.691 | 123.5825 | 98.2773 | -0.41657 | 120.8038 | 117.691 | 98.2773 | 1.1856 | 123.5825 | -6.0699 | -123.7976
1587.9219 | 123.4543 | -120.5338 | 2.9617 | -0.38442 | 0.03088 | -0.011485 | 0.084592 | -0.051486 | 0.034741 | 0.10484 | -2.9388 | 0.25177 | -3.2776 | 3.1265 | -118.7897 | -21.8948 | 2.5864 | 3.1357 | 3.0853 | -120.8267 | 117.2562 | -2.71 | 117.5949 | 123.6603 | -121.7514 | -0.29297 | 0.1236 | 0.33875 | 123.1201 | 123.6694 | 1.7441 | 120.7855 | 117.5949 | 123.6191 | 98.6389 | -0.29297 | 120.7855 | 117.5949 | 98.6389 | 1.7441 | 123.6191 | -6.2393 | -123.7885
1588.9219 | 123.4726 | -120.4742 | 2.9617 | -0.23183 | 0.034085 | -0.016825 | 0.085661 | -0.055758 | 0.055035 | 0.1027 | -2.8656 | 0.24719 | -3.2364 | 2.9205 | -118.4601 | -21.5469 | 2.7237 | 3.0487 | 3.0808 | -120.845 | 117.2379 | -2.7145 | 117.6086 | 123.3948 | -121.4218 | -0.37079 | 0.11902 | 0.37079 | 123.1979 | 123.5229 | 2.0142 | 120.7214 | 117.6086 | 123.555 | 98.9273 | -0.37079 | 120.7214 | 117.6086 | 98.9273 | 2.0142 | 123.555 | -6.1981 | -123.8068
1589.9844 | 123.5046 | -120.2545 | 3.1265 | 0.30223 | 0.010586 | -0.0040084 | 0.047208 | -0.055758 | 0.024059 | 0.098426 | -2.8793 | 0.23804 | -3.1723 | 3.0212 | -117.9428 | -21.4874 | 3.0029 | 3.2181 | 3.3142 | -120.6345 | 117.0822 | -2.8885 | 117.3752 | 123.2758 | -121.0693 | -0.37994 | 0.18768 | 0.29297 | 123.2574 | 123.4726 | 2.3117 | 120.4926 | 117.3752 | 123.5687 | 98.7671 | -0.37994 | 120.4926 | 117.3752 | 98.7671 | 2.3117 | 123.5687 | -6.2988 | -123.761
1590.9219 | 123.4589 | -120.3232 | 3.1082 | -0.30813 | 0.046902 | -0.015757 | 0.092069 | -0.049349 | 0.05183 | 0.11018 | -2.8015 | 0.2655 | -3.1952 | 3.0808 | -118.2495 | -20.7504 | 2.9022 | 3.2089 | 3.241 | -120.6848 | 117.128 | -2.8427 | 117.5217 | 123.4039 | -121.3577 | -0.36163 | 0.13275 | 0.39368 | 123.2254 | 123.5321 | 2.0737 | 120.5887 | 117.5217 | 123.5641 | 99.5728 | -0.36163 | 120.5887 | 117.5217 | 99.5728 | 2.0737 | 123.5641 | -6.3034 | -123.793
1591.9844 | 123.5229 | -119.577 | 3.7537 | 0.1649 | 0.026608 | -0.036051 | 0.06323 | -0.051486 | -0.034687 | 0.040748 | -1.2955 | 0.1831 | -1.6663 | 3.6301 | 3.2547 | -2.8519 | 3.685 | 3.7949 | 3.9322 | -120.0211 | 117.9108 | -3.5706 | 118.2816 | 123.2071 | -0.49896 | -0.44403 | 0.17853 | 0.37079 | 123.262 | 123.3719 | 122.8317 | 119.7601 | 118.2816 | 123.5092 | 116.7252 | -0.44403 | 119.7601 | 118.2816 | 116.7252 | 122.8317 | 123.5092 | -5.4199 | -123.7747
1592.9219 | 123.4497 | -119.2108 | 4.1428 | -1.3152 | 0.041562 | -0.020029 | 0.082456 | -0.051486 | -0.031483 | 0.037543 | -1.2817 | 0.31128 | -1.5518 | 4.1794 | 3.7079 | -2.2476 | 3.9093 | 4.3167 | 4.3076 | -119.6091 | 117.659 | -3.8315 | 117.9291 | 123.3902 | -0.43488 | -0.39826 | 0.16479 | 0.27008 | 123.1201 | 123.5275 | 122.9187 | 119.5221 | 117.9291 | 123.5184 | 116.9632 | -0.39826 | 119.5221 | 117.9291 | 116.9632 | 122.9187 | 123.5184 | -5.6946 | -123.7518
1593.9844 | 123.5184 | -120.3369 | 3.0212 | 0.24119 | 0.027676 | -0.046732 | 0.066434 | -0.056826 | -0.037891 | 0.042884 | -1.387 | 0.23346 | -1.7166 | 2.8839 | 2.5635 | -2.9572 | 2.8931 | 3.0945 | 3.1723 | -120.7947 | 118.6203 | -2.7878 | 118.9499 | 123.2208 | -0.45776 | -0.45776 | 0.15106 | 0.32959 | 123.23 | 123.4314 | 122.9004 | 120.5704 | 118.9499 | 123.5092 | 117.3798 | -0.45776 | 120.5704 | 118.9499 | 117.3798 | 122.9004 | 123.5092 | -4.7379 | -123.8159
1594.9219 | 123.5962 | -119.9615 | 3.4058 | -0.49123 | 0.018063 | -0.031779 | 0.058958 | -0.052554 | -0.036823 | 0.036475 | -1.1444 | 0.21515 | -1.5289 | 3.2272 | 2.9068 | -2.5681 | 3.3188 | 3.4378 | 3.6026 | -120.3918 | 118.4326 | -3.1906 | 118.8171 | 123.1888 | -0.49896 | -0.4303 | 0.19684 | 0.38452 | 123.2803 | 123.3994 | 122.8683 | 120.1767 | 118.8171 | 123.5641 | 117.3935 | -0.4303 | 120.1767 | 118.8171 | 117.3935 | 122.8683 | 123.5641 | -4.9347 | -123.7976
1595.9844 | 123.5321 | -120.2362 | 3.0899 | -0.32338 | 0.014859 | -0.034983 | 0.069639 | -0.066439 | -0.052845 | 0.015113 | -1.2314 | 0.21515 | -1.6296 | 2.7145 | 2.6733 | -2.6917 | 2.9984 | 3.0762 | 3.2822 | -120.694 | 118.6066 | -2.8748 | 119.0048 | 122.9507 | -0.41656 | -0.45776 | 0.19226 | 0.39826 | 123.2346 | 123.3124 | 122.9095 | 120.4514 | 119.0048 | 123.5184 | 117.5446 | -0.45776 | 120.4514 | 119.0048 | 117.5446 | 122.9095 | 123.5184 | -4.7195 | -123.7839
1596.9219 | 123.5641 | -120.2133 | 3.1494 | -0.32338 | 0.020199 | -0.032847 | 0.068571 | -0.049349 | -0.033619 | 0.031135 | -0.79193 | 0.21515 | -1.181 | 3.0808 | 2.8198 | -2.7512 | 3.0441 | 3.2455 | 3.3554 | -120.6207 | 119.0323 | -2.9343 | 119.4214 | 123.2941 | -0.32959 | -0.40741 | 0.20599 | 0.3891 | 123.2574 | 123.4589 | 123.0331 | 120.4285 | 119.4214 | 123.5687 | 117.4622 | -0.40741 | 120.4285 | 119.4214 | 117.4622 | 123.0331 | 123.5687 | -4.3304 | -123.7701
1597.9688 | 123.4955 | -119.957 | 3.4698 | 0.47007 | 0.04263 | -0.011485 | 0.079252 | -0.055758 | -0.020801 | 0.033271 | -0.79651 | 0.2655 | -1.1765 | 3.447 | 3.0853 | -2.449 | 3.3096 | 3.566 | 3.6163 | -120.3369 | 118.7805 | -3.2043 | 119.1605 | 123.4039 | -0.38452 | -0.37994 | 0.14648 | 0.37994 | 123.2666 | 123.5229 | 123.0423 | 120.2225 | 119.1605 | 123.5733 | 117.5079 | -0.37994 | 120.2225 | 119.1605 | 117.5079 | 123.0423 | 123.5733 | -4.6463 | -123.8068
1598.9219 | 123.587 | -119.7235 | 3.5934 | -0.063984 | 0.028744 | -0.028574 | 0.055753 | -0.052554 | -0.034687 | 0.041816 | -0.80109 | 0.23804 | -1.1902 | 3.4515 | 3.0991 | -2.4673 | 3.566 | 3.6209 | 3.7994 | -120.1675 | 118.5333 | -3.3554 | 118.9224 | 123.175 | -0.49438 | -0.44403 | 0.20599 | 0.3891 | 123.2895 | 123.3444 | 122.8226 | 119.9615 | 118.9224 | 123.5229 | 117.2562 | -0.44403 | 119.9615 | 118.9224 | 117.2562 | 122.8226 | 123.5229 | -4.7836 | -123.761
1599.9844 | 123.555 | -119.7876 | 3.5202 | 0.39378 | 0.024472 | -0.0050764 | 0.079252 | -0.058962 | -0.026142 | 0.035407 | -0.8606 | 0.21057 | -1.2543 | 3.4241 | 3.0716 | -2.5589 | 3.479 | 3.5706 | 3.6987 | -120.2682 | 118.5333 | -3.3096 | 118.927 | 123.2117 | -0.44861 | -0.48065 | 0.17853 | 0.39368 | 123.2666 | 123.3582 | 122.8592 | 119.9982 | 118.927 | 123.4863 | 117.2287 | -0.48065 | 119.9982 | 118.927 | 117.2287 | 122.8592 | 123.4863 | -4.7745 | -123.7885
1600.9219 | 123.4726 | -119.7647 | 3.6072 | -0.4302 | 0.022336 | -0.011485 | 0.082456 | -0.064303 | -0.032551 | 0.032203 | -0.89722 | 0.24261 | -1.2634 | 3.5339 | 3.1677 | -2.6413 | 3.4287 | 3.7125 | 3.7811 | -120.1675 | 118.5013 | -3.3646 | 118.8675 | 123.2986 | -0.43945 | -0.40283 | 0.17395 | 0.36621 | 123.1934 | 123.4772 | 122.9324 | 120.0073 | 118.8675 | 123.5458 | 117.1234 | -0.40283 | 120.0073 | 118.8675 | 117.1234 | 122.9324 | 123.5458 | -4.8706 | -123.7747
1601.9844 | 123.5504 | -119.9295 | 3.4103 | 0.47007 | 0.031949 | -0.015757 | 0.065366 | -0.049349 | -0.036823 | 0.036475 | -0.81482 | 0.1831 | -1.1993 | 3.2867 | 2.9434 | -2.7969 | 3.3051 | 3.447 | 3.5706 | -120.3964 | 118.7302 | -3.2272 | 119.1147 | 123.2162 | -0.46692 | -0.46692 | 0.16022 | 0.38452 | 123.2346 | 123.3765 | 122.8729 | 120.1126 | 119.1147 | 123.5001 | 117.1326 | -0.46692 | 120.1126 | 119.1147 | 117.1326 | 122.8729 | 123.5001 | -4.6097 | -123.8068
1602.9219 | 123.5367 | -119.0094 | 4.2847 | 0.073345 | 0.021267 | -0.017893 | 0.064298 | -0.058962 | -0.056049 | 0.038612 | -0.86975 | 0.23346 | -1.2039 | 4.0649 | 3.7857 | -2.1973 | 4.216 | 4.4128 | 4.4403 | -119.4763 | 117.8055 | -4.0512 | 118.1396 | 123.0743 | -0.49896 | -0.46692 | 0.15564 | 0.33417 | 123.2254 | 123.4222 | 122.7951 | 119.2429 | 118.1396 | 123.4497 | 116.8121 | -0.46692 | 119.2429 | 118.1396 | 116.8121 | 122.7951 | 123.4497 | -5.4886 | -123.761
1603.9844 | 123.5641 | -118.959 | 4.3396 | 0.39378 | 0.038357 | -0.016825 | 0.077116 | -0.060031 | -0.029346 | 0.034339 | -0.73242 | 0.21057 | -1.1307 | 4.2435 | 3.8452 | -2.1332 | 4.2847 | 4.3762 | 4.5319 | -119.4534 | 117.8284 | -4.129 | 118.2266 | 123.2025 | -0.49438 | -0.49438 | 0.19226 | 0.39825 | 123.2437 | 123.3353 | 122.8043 | 119.1696 | 118.2266 | 123.4909 | 116.8259 | -0.49438 | 119.1696 | 118.2266 | 116.8259 | 122.8043 | 123.4909 | -5.4703 | -123.793
1604.9219 | 123.5779 | -119.0552 | 4.2709 | -0.26235 | 0.029812 | -0.040324 | 0.065366 | -0.058962 | -0.038959 | 0.031135 | -0.8194 | 0.21973 | -1.1856 | 4.1611 | 3.7399 | -2.1194 | 4.2206 | 4.3304 | 4.4724 | -119.4946 | 117.8696 | -4.0512 | 118.2358 | 123.2162 | -0.53101 | -0.43945 | 0.20142 | 0.36621 | 123.2758 | 123.3856 | 122.7951 | 119.2749 | 118.2358 | 123.5275 | 116.9357 | -0.43945 | 119.2749 | 118.2358 | 116.9357 | 122.7951 | 123.5275 | -5.4565 | -123.7656
1605.9844 | 123.5641 | -117.5766 | 4.1473 | 0.50059 | 0.038357 | -0.024302 | 0.070707 | -0.064303 | -0.020801 | 0.026862 | -0.737 | 0.20599 | -1.1215 | 4.0924 | 3.9551 | -2.0782 | 4.1382 | 4.248 | 4.39 | -138.0569 | 116.4551 | -3.9413 | 116.8396 | 121.669 | -0.19226 | -20.4803 | 0.24262 | 0.38452 | 121.7148 | 121.8246 | 121.5317 | 117.7826 | 116.8396 | 121.9666 | 115.4984 | -20.4803 | 117.7826 | 116.8396 | 115.4984 | 121.5317 | 121.9666 | -5.2689 | -142.2043
1606.9219 | 123.5229 | -118.6066 | 4.6829 | 0.37852 | 0.022336 | -0.023234 | 0.06323 | -0.062167 | -0.034687 | 0.035407 | -0.71411 | 0.21515 | -0.87433 | 4.6005 | 4.1794 | -1.7624 | 4.5868 | 4.7562 | 4.8569 | -119.0918 | 117.7322 | -4.4678 | 117.8925 | 123.2071 | -0.50354 | -0.48523 | 0.17395 | 0.16022 | 123.1934 | 123.3627 | 122.7859 | 118.8217 | 117.8925 | 123.4634 | 116.8442 | -0.48523 | 118.8217 | 117.8925 | 116.8442 | 122.7859 | 123.4634 | -5.5573 | -123.7747
1607.9844 | 123.5641 | -118.895 | 4.4769 | 0.31749 | 0.040494 | -0.012553 | 0.089933 | -0.066439 | 0.056103 | 0.1027 | -2.1011 | 0.21057 | -2.4902 | 4.4357 | -116.2262 | -23.3231 | 4.4083 | 4.5273 | 4.6509 | -119.3161 | 116.4047 | -4.2664 | 116.7938 | 123.3307 | -120.7031 | -0.42114 | 0.17395 | 0.3891 | 123.3032 | 123.4222 | 2.6688 | 119.1055 | 116.7938 | 123.5458 | 95.5719 | -0.42114 | 119.1055 | 116.7938 | 95.5719 | 2.6688 | 123.5458 | -6.9672 | -123.793
1608.9219 | 123.5321 | -118.5837 | 4.7836 | -0.018208 | 0.019131 | -0.012553 | 0.060026 | -0.058962 | 0.028332 | 0.090949 | -2.5864 | 0.19226 | -2.9068 | 4.6692 | -116.3635 | -21.6614 | 4.66 | 4.8431 | 4.953 | -118.9728 | 115.6769 | -4.5914 | 115.9973 | 123.2529 | -121.1472 | -0.3891 | 0.16937 | 0.32043 | 123.2437 | 123.4268 | 2.2202 | 118.7759 | 115.9973 | 123.5367 | 96.9223 | -0.3891 | 118.7759 | 115.9973 | 96.9223 | 2.2202 | 123.5367 | -7.6904 | -123.7564
1609.9844 | 123.4451 | -118.5654 | 4.7974 | -0.094502 | 0.051175 | -0.020029 | 0.095274 | -0.052554 | 0.053967 | 0.10697 | -2.5543 | 0.27466 | -2.9343 | 4.7882 | -116.2445 | -20.5261 | 4.5593 | 4.8614 | 4.8569 | -119.0598 | 115.6311 | -4.5227 | 116.011 | 123.3536 | -121.0419 | -0.49438 | 0.05951 | 0.37994 | 123.1247 | 123.4268 | 2.3209 | 118.84 | 116.011 | 123.4222 | 98.0392 | -0.49438 | 118.84 | 116.011 | 98.0392 | 2.3209 | 123.4222 | -7.7316 | -123.8571
1610.9219 | 123.5458 | -118.5608 | 4.8065 | -0.3539 | 0.020199 | -0.021098 | 0.070707 | -0.047213 | 0.025128 | 0.085609 | -2.2385 | 0.23804 | -2.6138 | 4.4586 | -116.6199 | -20.4666 | 4.7058 | 4.7791 | 4.9576 | -118.9453 | 115.947 | -4.5685 | 116.3223 | 123.0194 | -121.4264 | -0.38452 | 0.15106 | 0.37537 | 123.2666 | 123.3398 | 1.9409 | 118.7988 | 116.3223 | 123.5184 | 98.0942 | -0.38452 | 118.7988 | 116.3223 | 98.0942 | 1.9409 | 123.5184 | -7.4203 | -123.7518
1611.9844 | 123.4222 | -118.4967 | 4.9576 | 0.073345 | 0.055447 | -0.024302 | 0.096342 | -0.048281 | 0.042217 | 0.10804 | -2.5452 | 0.23804 | -2.9251 | 5.0217 | -116.478 | -20.2057 | 4.6967 | 5.0858 | 5.0674 | -118.8629 | 115.5716 | -4.7195 | 115.9515 | 123.5184 | -121.4355 | -0.36621 | 0.10986 | 0.37994 | 123.1934 | 123.5825 | 2.0187 | 118.7347 | 115.9515 | 123.5641 | 98.291 | -0.36621 | 118.7347 | 115.9515 | 98.291 | 2.0187 | 123.5641 | -7.8827 | -123.8205
1612.9219 | 123.5184 | -118.7256 | 4.6463 | 0.30223 | 0.03088 | -0.04246 | 0.065366 | -0.052554 | 0.031536 | 0.09629 | -2.4857 | 0.23346 | -2.7832 | 4.5319 | -117.2195 | -20.4849 | 4.4998 | 4.7012 | 4.7928 | -119.1055 | 115.9424 | -4.4128 | 116.2399 | 123.2574 | -121.8658 | -0.37994 | 0.14649 | 0.29755 | 123.2254 | 123.4268 | 1.506 | 118.959 | 116.2399 | 123.5184 | 98.2407 | -0.37994 | 118.959 | 116.2399 | 98.2407 | 1.506 | 123.5184 | -7.4295 | -123.7518
1613.9844 | 123.4543 | -118.5791 | 4.8248 | 0.088604 | 0.053311 | 0.017355 | 0.086729 | -0.050418 | 0.053967 | 0.10697 | -2.504 | 0.2655 | -2.9068 | 4.866 | -117.2333 | -20.2515 | 4.6509 | 4.9576 | 4.9713 | -118.9453 | 115.6723 | -4.5593 | 116.0751 | 123.4451 | -122.0581 | -0.36621 | 0.14648 | 0.40283 | 123.23 | 123.5367 | 1.3458 | 118.8446 | 116.0751 | 123.5504 | 98.3276 | -0.36621 | 118.8446 | 116.0751 | 98.3276 | 1.3458 | 123.5504 | -7.7316 | -123.7701
1614.9219 | 123.5367 | -118.5837 | 4.7607 | 0.1649 | 0.043698 | -0.022166 | 0.078184 | -0.056826 | 0.043285 | 0.1059 | -2.6184 | 0.22888 | -2.9572 | 4.6829 | -116.5741 | -20.0043 | 4.7058 | 4.8157 | 4.9622 | -118.9957 | 115.6265 | -4.5319 | 115.9653 | 123.2666 | -121.3348 | -0.41199 | 0.20142 | 0.33874 | 123.2895 | 123.3994 | 2.0096 | 118.8126 | 115.9653 | 123.5458 | 98.5794 | -0.41199 | 118.8126 | 115.9653 | 98.5794 | 2.0096 | 123.5458 | -7.7179 | -123.7564
1615.9219 | 123.5184 | -118.515 | 4.8203 | 0.073345 | 0.03088 | -0.024302 | 0.053617 | -0.069644 | 0.021923 | 0.11552 | -2.5314 | 0.21515 | -2.8336 | 4.6967 | -117.0685 | -19.7525 | 4.7424 | 4.9301 | 4.9576 | -118.9224 | 115.6815 | -4.6051 | 115.9836 | 123.2117 | -121.8887 | -0.40741 | 0.13733 | 0.30212 | 123.2574 | 123.4451 | 1.4465 | 118.7302 | 115.9836 | 123.4726 | 98.7625 | -0.40741 | 118.7302 | 115.9836 | 98.7625 | 1.4465 | 123.4726 | -7.6538 | -123.7427
1616.9844 | 123.436 | -118.364 | 5.0858 | 0.042827 | 0.044766 | 0.01415 | 0.088865 | -0.052554 | 0.059307 | 0.10804 | -2.4628 | 0.27466 | -2.8152 | 5.1407 | -116.2674 | -19.2719 | 4.8706 | 5.2689 | 5.2231 | -118.7027 | 115.5487 | -4.8111 | 115.9012 | 123.5046 | -121.3531 | -0.33875 | 0.13733 | 0.35248 | 123.2346 | 123.6328 | 2.0966 | 118.6386 | 115.9012 | 123.587 | 99.0921 | -0.33875 | 118.6386 | 115.9012 | 99.0921 | 2.0966 | 123.587 | -7.901 | -123.7885
1617.9219 | 123.4818 | -118.0435 | 5.3238 | 0.45481 | 0.041562 | -0.015757 | 0.08032 | -0.05469 | 0.057171 | 0.10056 | -2.504 | 0.26093 | -2.861 | 5.3329 | -116.2354 | -19.0384 | 5.1773 | 5.4611 | 5.4657 | -118.4509 | 115.1825 | -5.0629 | 115.5396 | 123.3765 | -121.5591 | -0.40741 | 0.14191 | 0.35706 | 123.2208 | 123.5046 | 1.8082 | 118.3044 | 115.5396 | 123.5092 | 99.0051 | -0.40741 | 118.3044 | 115.5396 | 99.0051 | 1.8082 | 123.5092 | -8.1848 | -123.7747
1618.9219 | 123.5458 | -118.103 | 5.2185 | 0.37852 | 0.031949 | -0.010416 | 0.085661 | -0.05469 | 0.049694 | 0.09629 | -2.4582 | 0.22888 | -2.8244 | 5.1453 | -116.9724 | -19.7708 | 5.1544 | 5.2643 | 5.3879 | -118.5333 | 115.2786 | -4.9896 | 115.6448 | 123.2483 | -122.1909 | -0.4303 | 0.16937 | 0.36621 | 123.2574 | 123.3673 | 1.1307 | 118.3319 | 115.6448 | 123.4909 | 98.3322 | -0.4303 | 118.3319 | 115.6448 | 98.3322 | 1.1307 | 123.4909 | -8.0429 | -123.7518
1619.9688 | 123.4909 | -118.103 | 5.3101 | -0.44545 | 0.023404 | -0.030711 | 0.067503 | -0.050418 | 0.039013 | 0.10911 | -2.3026 | 0.25635 | -2.655 | 5.2277 | -115.9698 | -19.0338 | 5.1453 | 5.4199 | 5.4657 | -118.4647 | 115.448 | -5.0537 | 115.8005 | 123.3307 | -121.2799 | -0.36163 | 0.15564 | 0.35248 | 123.2483 | 123.5229 | 2.1332 | 118.3594 | 115.8005 | 123.5687 | 99.0692 | -0.36163 | 118.3594 | 115.8005 | 99.0692 | 2.1332 | 123.5687 | -7.9651 | -123.7747
1620.9219 | 123.5229 | -117.9337 | 5.4245 | -0.3539 | 0.027676 | -0.046732 | 0.060026 | -0.051486 | 0.027264 | 0.11124 | -2.2797 | 0.2243 | -2.6413 | 5.3741 | -115.9424 | -19.1895 | 5.3146 | 5.5069 | 5.6213 | -118.3411 | 115.2924 | -5.2002 | 115.654 | 123.3078 | -121.3669 | -0.40741 | 0.19684 | 0.36163 | 123.2483 | 123.4406 | 1.9913 | 118.158 | 115.654 | 123.555 | 98.7442 | -0.40741 | 118.158 | 115.654 | 98.7442 | 1.9913 | 123.555 | -8.0658 | -123.7656
1621.9844 | 123.4268 | -118.1076 | 5.2826 | 3.766 | 0.043698 | -0.037119 | 0.083524 | -0.051486 | 0.047558 | 0.090949 | -2.2522 | 0.27466 | -2.7695 | 5.3055 | -116.4185 | -19.249 | 5.0446 | 5.4382 | 5.3696 | -118.5059 | 115.3381 | -5.0079 | 115.8554 | 123.4131 | -121.7011 | -0.39825 | 0.086975 | 0.51727 | 123.1522 | 123.5458 | 1.6891 | 118.3823 | 115.8554 | 123.4772 | 98.8586 | -0.39825 | 118.3823 | 115.8554 | 98.8586 | 1.6891 | 123.4772 | -8.0521 | -123.7885
1622.9219 | 123.4131 | -118.5104 | 4.9301 | 0.40904 | 0.04263 | -0.024302 | 0.084592 | -0.042941 | 0.052898 | 0.10056 | -2.3666 | 0.27008 | -2.71 | 4.9988 | -116.3177 | -19.3497 | 4.6509 | 5.0766 | 5.0858 | -118.8629 | 115.8005 | -4.66 | 116.1438 | 123.5092 | -121.2479 | -0.35248 | 0.15564 | 0.34332 | 123.1613 | 123.587 | 2.1927 | 118.7805 | 116.1438 | 123.5962 | 99.1608 | -0.35248 | 118.7805 | 116.1438 | 99.1608 | 2.1927 | 123.5962 | -7.6401 | -123.793
1623.9844 | 123.4726 | -118.2404 | 5.1819 | 0.30223 | 0.040494 | -0.024302 | 0.078184 | -0.048281 | -0.0015754 | 0.031135 | -1.0254 | 0.27466 | -1.387 | 5.2689 | 4.8431 | -1.6891 | 4.9393 | 5.3696 | 5.3101 | -118.5883 | 116.8533 | -4.9072 | 117.215 | 123.5092 | -0.33875 | -0.3479 | 0.12817 | 0.36163 | 123.1796 | 123.6099 | 123.0835 | 118.515 | 117.215 | 123.5504 | 116.5512 | -0.3479 | 118.515 | 117.215 | 116.5512 | 123.0835 | 123.5504 | -6.5689 | -123.7701
1624.9219 | 123.5367 | -117.7505 | 5.571 | 1.6908 | 0.027676 | -0.024302 | 0.06323 | -0.05469 | -0.024006 | 0.031135 | -0.91553 | 0.19226 | -1.4008 | 5.4657 | 5.04 | -1.4511 | 5.5161 | 5.6396 | 5.7632 | -118.2175 | 116.3498 | -5.3787 | 116.835 | 123.2162 | -0.53101 | -0.46692 | 0.19226 | 0.48523 | 123.2666 | 123.3902 | 122.7905 | 117.9428 | 116.835 | 123.5138 | 116.2994 | -0.46692 | 117.9428 | 116.835 | 116.2994 | 122.7905 | 123.5138 | -6.9717 | -123.7885
1625.9844 | 123.5413 | -118.1488 | 5.2048 | -0.018208 | 0.020199 | -0.023234 | 0.060026 | -0.067507 | 0.024059 | 0.11658 | -2.5269 | 0.21973 | -2.8244 | 5.0949 | -116.4413 | -20.0272 | 5.0995 | 5.2551 | 5.3833 | -118.5516 | 115.3244 | -4.985 | 115.6219 | 123.2437 | -121.6461 | -0.40283 | 0.17853 | 0.29755 | 123.2483 | 123.4039 | 1.7075 | 118.3685 | 115.6219 | 123.5321 | 98.1216 | -0.40283 | 118.3685 | 115.6219 | 98.1216 | 1.7075 | 123.5321 | -8.0292 | -123.7564
1626.9219 | 123.4314 | -118.2678 | 5.1636 | 0.40904 | 0.052243 | -0.016825 | 0.077116 | -0.047213 | 0.049694 | 0.1059 | -2.504 | 0.25635 | -2.8564 | 5.191 | -116.5009 | -19.313 | 4.9164 | 5.3467 | 5.2643 | -118.6203 | 115.4114 | -4.9072 | 115.7639 | 123.4589 | -121.6644 | -0.35248 | 0.10071 | 0.35248 | 123.1842 | 123.6145 | 1.767 | 118.5242 | 115.7639 | 123.5321 | 98.9548 | -0.35248 | 118.5242 | 115.7639 | 98.9548 | 1.767 | 123.5321 | -8.02 | -123.7839
1627.9844 | 123.6099 | -118.1625 | 5.191 | 0.51585 | 0.039425 | -0.015757 | 0.087797 | -0.060031 | 0.049694 | 0.10056 | -2.4261 | 0.21057 | -2.8152 | 5.2139 | -117.4393 | -19.5923 | 5.2185 | 5.1727 | 5.3925 | -118.6111 | 115.3473 | -4.9805 | 115.7364 | 123.3765 | -122.6303 | -0.44861 | 0.20142 | 0.3891 | 123.381 | 123.3353 | 0.72327 | 118.3731 | 115.7364 | 123.555 | 98.5703 | -0.44861 | 118.3731 | 115.7364 | 98.5703 | 0.72327 | 123.555 | -8.0063 | -123.8022
1628.9219 | 123.5641 | -117.9474 | 5.3787 | 1.3551 | 0.026608 | -0.023234 | 0.072843 | -0.050418 | 0.044354 | 0.10377 | -2.4078 | 0.21973 | -2.7969 | 5.3055 | -116.9952 | -19.5145 | 5.3467 | 5.452 | 5.5618 | -118.3777 | 115.1505 | -5.159 | 115.5396 | 123.2529 | -122.374 | -0.4303 | 0.18311 | 0.3891 | 123.2941 | 123.3994 | 0.95215 | 118.1671 | 115.5396 | 123.5092 | 98.4329 | -0.4303 | 118.1671 | 115.5396 | 98.4329 | 0.95215 | 123.5092 | -8.1757 | -123.7564
1629.9844 | 123.4451 | -117.9565 | 5.4703 | -0.49123 | 0.035153 | -0.033915 | 0.074979 | -0.055758 | 0.042217 | 0.10377 | -2.3987 | 0.2655 | -2.7145 | 5.452 | -116.8625 | -19.0475 | 5.2002 | 5.6442 | 5.5481 | -118.3228 | 115.242 | -5.2048 | 115.5579 | 123.4085 | -122.3328 | -0.36621 | 0.07782 | 0.31586 | 123.1567 | 123.6008 | 1.0941 | 118.222 | 115.5579 | 123.5046 | 98.909 | -0.36621 | 118.222 | 115.5579 | 98.909 | 1.0941 | 123.5046 | -8.1848 | -123.793
1630.9219 | 123.5275 | -118.1213 | 5.2597 | -0.0029495 | 0.036221 | -0.041392 | 0.055753 | -0.063235 | 0.034741 | 0.11552 | -2.4216 | 0.21515 | -2.7328 | 5.2368 | -117.8146 | -19.3451 | 4.8889 | 5.2322 | 5.4428 | -118.5608 | 115.3885 | -5.0446 | 115.6998 | 123.3582 | -123.0743 | -0.43945 | 0.1831 | 0.31128 | 123.0103 | 123.3536 | 0.3067 | 118.3365 | 115.6998 | 123.5641 | 98.7762 | -0.43945 | 118.3365 | 115.6998 | 98.7762 | 0.3067 | 123.5641 | -7.9926 | -123.8205
1631.9844 | 123.4451 | -118.3044 | 5.1086 | -0.32338 | 0.036221 | -0.012553 | 0.084592 | -0.049349 | 0.04649 | 0.11018 | -2.3438 | 0.25635 | -2.7191 | 5.1224 | -117.952 | -19.4092 | 4.866 | 5.2505 | 5.2277 | -118.6844 | 115.5853 | -4.8523 | 115.9607 | 123.4268 | -123.0606 | -0.37994 | 0.11902 | 0.37537 | 123.1705 | 123.555 | 0.35248 | 118.5608 | 115.9607 | 123.5321 | 98.8953 | -0.37994 | 118.5608 | 115.9607 | 98.8953 | 0.35248 | 123.5321 | -7.8278 | -123.793
1632.9219 | 123.5458 | -118.2816 | 5.0537 | 0.36326 | 0.027676 | -0.028574 | 0.084592 | -0.050418 | 0.048626 | 0.10377 | -2.3987 | 0.24261 | -2.7695 | 5.0034 | -117.778 | -19.6564 | 5.0217 | 5.1178 | 5.2551 | -118.6798 | 115.5121 | -4.8111 | 115.8829 | 123.2849 | -122.8317 | -0.39826 | 0.20142 | 0.37079 | 123.3032 | 123.3994 | 0.50354 | 118.5242 | 115.8829 | 123.5367 | 98.6252 | -0.39826 | 118.5242 | 115.8829 | 98.6252 | 0.50354 | 123.5367 | -7.8232 | -123.7335
1633.9844 | 123.4543 | -118.4097 | 4.9942 | -0.27761 | 0.046902 | -0.017893 | 0.082456 | -0.055758 | 0.04649 | 0.095222 | -2.3849 | 0.27008 | -2.7786 | 4.9896 | -118.1305 | -19.4229 | 4.7699 | 5.127 | 5.127 | -118.7943 | 115.6311 | -4.7241 | 116.0248 | 123.3994 | -123.1247 | -0.38452 | 0.13275 | 0.39368 | 123.1796 | 123.5367 | 0.27924 | 118.6798 | 116.0248 | 123.5367 | 98.9868 | -0.38452 | 118.6798 | 116.0248 | 98.9868 | 0.27924 | 123.5367 | -7.7728 | -123.7885
1634.9219 | 123.4406 | -118.2724 | 5.159 | 0.39378 | 0.027676 | -0.020029 | 0.077116 | -0.05469 | 0.056103 | 0.099494 | -2.6779 | 0.27466 | -2.7603 | 5.1315 | -117.9565 | -19.2947 | 4.8935 | 5.2917 | 5.2597 | -118.6203 | 115.5121 | -4.8843 | 115.5945 | 123.4039 | -123.1155 | -0.3479 | 0.10071 | 0.082398 | 123.1659 | 123.5641 | 0.31586 | 118.5471 | 115.5945 | 123.5321 | 98.9777 | -0.3479 | 118.5471 | 115.5945 | 98.9777 | 0.31586 | 123.5321 | -7.9193 | -123.7793
1635.9844 | 123.4177 | -118.4692 | 4.9484 | 0.13438 | 0.038357 | -0.012553 | 0.077116 | -0.040805 | 0.044354 | 0.090949 | -2.2659 | 0.28839 | -2.7512 | 5.0217 | -117.3294 | -19.0475 | 4.7653 | 5.127 | 5.0903 | -118.8171 | 115.7181 | -4.66 | 116.2033 | 123.4909 | -122.2778 | -0.3479 | 0.14191 | 0.48523 | 123.2346 | 123.5962 | 1.1398 | 118.7576 | 116.2033 | 123.5596 | 99.4217 | -0.3479 | 118.7576 | 116.2033 | 99.4217 | 1.1398 | 123.5596 | -7.6996 | -123.7656
1636.9219 | 123.4543 | -118.5196 | 4.8935 | 0.51585 | 0.046902 | 0.020559 | 0.089933 | -0.049349 | 0.055035 | 0.10804 | -2.4445 | 0.26093 | -2.8061 | 4.8752 | -117.5812 | -19.0933 | 4.6738 | 5.0125 | 4.9988 | -118.8766 | 115.7135 | -4.6326 | 116.0751 | 123.3948 | -122.4747 | -0.35706 | 0.10529 | 0.36163 | 123.1934 | 123.5321 | 0.93842 | 118.7805 | 116.0751 | 123.5184 | 99.4263 | -0.35706 | 118.7805 | 116.0751 | 99.4263 | 0.93842 | 123.5184 | -7.6996 | -123.7701
1637.9844 | 123.5687 | -118.6478 | 4.66 | 0.48533 | 0.035153 | -0.00080337 | 0.068571 | -0.049349 | 0.04649 | 0.10484 | -2.4765 | 0.2243 | -2.8427 | 4.5868 | -118.4463 | -19.8029 | 4.4998 | 4.8248 | 4.8431 | -119.1101 | 115.8051 | -4.4357 | 116.1713 | 123.2346 | -123.1064 | -0.46234 | 0.18311 | 0.36621 | 123.1476 | 123.4726 | 0.20142 | 118.8721 | 116.1713 | 123.4909 | 98.8449 | -0.46234 | 118.8721 | 116.1713 | 98.8449 | 0.20142 | 123.4909 | -7.5027 | -123.7701
1638.9219 | 123.3856 | -118.634 | 4.8065 | 0.33274 | 0.049038 | -0.013621 | 0.081388 | -0.055758 | 0.053967 | 0.11231 | -2.6596 | 0.26093 | -2.98 | 4.8569 | -116.5466 | -19.487 | 4.5044 | 5.0079 | 4.8935 | -118.9957 | 115.654 | -4.5456 | 115.9744 | 123.4909 | -121.3531 | -0.36163 | 0.086975 | 0.32044 | 123.1384 | 123.642 | 2.0874 | 118.895 | 115.9744 | 123.5275 | 99.147 | -0.36163 | 118.895 | 115.9744 | 99.147 | 2.0874 | 123.5275 | -7.7866 | -123.8022
1639.9844 | 123.4451 | -118.5333 | 4.8798 | -0.3539 | 0.029812 | -0.032847 | 0.081388 | -0.052554 | 0.048626 | 0.10484 | -2.4994 | 0.27008 | -2.8427 | 4.9118 | -116.5649 | -19.2993 | 4.6646 | 5.0583 | 5.0079 | -118.8812 | 115.6906 | -4.6097 | 116.0339 | 123.4451 | -121.4447 | -0.3479 | 0.12817 | 0.34332 | 123.1979 | 123.5916 | 1.9684 | 118.8034 | 116.0339 | 123.5413 | 99.234 | -0.3479 | 118.8034 | 116.0339 | 99.234 | 1.9684 | 123.5413 | -7.7225 | -123.761
1640.9219 | 123.5001 | -118.8309 | 4.5502 | 0.27171 | 0.024472 | -0.016825 | 0.052549 | -0.040805 | 0.027264 | 0.11338 | -2.6001 | 0.24261 | -2.9068 | 4.4495 | -117.5354 | -19.8074 | 4.4312 | 4.6555 | 4.7287 | -119.22 | 115.9241 | -4.3076 | 116.2308 | 123.2803 | -122.0856 | -0.3891 | 0.17853 | 0.3067 | 123.262 | 123.4863 | 1.2955 | 119.0735 | 116.2308 | 123.5596 | 99.0234 | -0.3891 | 119.0735 | 116.2308 | 99.0234 | 1.2955 | 123.5596 | -7.457 | -123.7701
1641.9844 | 123.4634 | -118.9362 | 4.5136 | -0.39968 | 0.046902 | -0.0082804 | 0.079252 | -0.05469 | 0.053967 | 0.10804 | -2.4353 | 0.26093 | -2.7832 | 4.5136 | -117.3111 | -19.8074 | 4.2709 | 4.6097 | 4.6463 | -119.3069 | 116.153 | -4.2526 | 116.5009 | 123.4497 | -121.8246 | -0.37079 | 0.13275 | 0.3479 | 123.2071 | 123.5458 | 1.6251 | 119.1971 | 116.5009 | 123.5825 | 99.1287 | -0.37079 | 119.1971 | 116.5009 | 99.1287 | 1.6251 | 123.5825 | -7.2968 | -123.8205
1642.9219 | 123.4177 | -119.0643 | 4.3762 | 0.073345 | 0.043698 | -0.016825 | 0.084592 | -0.047213 | 0.057171 | 0.10911 | -2.4536 | 0.27008 | -2.8336 | 4.4083 | -117.4988 | -19.8074 | 4.1336 | 4.5227 | 4.4769 | -119.4168 | 116.2308 | -4.1061 | 116.6107 | 123.4726 | -121.875 | -0.35248 | 0.10071 | 0.37994 | 123.1979 | 123.587 | 1.5656 | 119.3344 | 116.6107 | 123.5413 | 99.2569 | -0.35248 | 119.3344 | 116.6107 | 99.2569 | 1.5656 | 123.5413 | -7.2098 | -123.793
1643.9844 | 123.4222 | -118.8217 | 4.6143 | -0.41494 | 0.036221 | -0.0072124 | 0.056821 | -0.042941 | 0.034741 | 0.10377 | -2.5543 | 0.23804 | -2.8793 | 4.5044 | -117.8055 | -19.8532 | 4.4174 | 4.7607 | 4.715 | -119.1696 | 115.9424 | -4.3762 | 116.2674 | 123.3261 | -122.4197 | -0.3479 | 0.10071 | 0.32501 | 123.2391 | 123.5825 | 1.0162 | 119.0598 | 116.2674 | 123.5367 | 98.9685 | -0.3479 | 119.0598 | 116.2674 | 98.9685 | 1.0162 | 123.5367 | -7.4936 | -123.7839
1644.9219 | 123.4451 | -119.0826 | 4.3167 | -0.55227 | 0.039425 | -0.020029 | 0.087797 | -0.047213 | 0.048626 | 0.097358 | -2.4536 | 0.32044 | -2.7878 | 4.3304 | -118.0664 | -20.0226 | 4.129 | 4.454 | 4.4815 | -119.4672 | 116.2949 | -3.9963 | 116.629 | 123.4131 | -122.3831 | -0.38452 | 0.1648 | 0.33417 | 123.2117 | 123.5367 | 1.0162 | 119.4031 | 116.629 | 123.5641 | 99.0601 | -0.38452 | 119.4031 | 116.629 | 99.0601 | 1.0162 | 123.5641 | -7.1045 | -123.7839
1645.9844 | 123.4955 | -119.0964 | 4.3076 | 0.14964 | 0.022336 | -0.0061444 | 0.041868 | -0.050418 | 0.028332 | 0.10804 | -2.4582 | 0.2243 | -2.7695 | 4.1794 | -117.1463 | -19.9951 | 4.1794 | 4.3945 | 4.4403 | -119.4626 | 116.3269 | -4.0833 | 116.6382 | 123.2758 | -121.4539 | -0.36621 | 0.13275 | 0.31128 | 123.2758 | 123.4909 | 1.9501 | 119.3207 | 116.6382 | 123.5367 | 99.1013 | -0.36621 | 119.3207 | 116.6382 | 99.1013 | 1.9501 | 123.5367 | -7.077 | -123.7701
1646.9219 | 123.4177 | -119.1971 | 4.2297 | 0.042827 | 0.053311 | -0.011485 | 0.091001 | -0.055758 | 0.056103 | 0.10484 | -2.4628 | 0.24719 | -2.8564 | 4.2526 | -118.5745 | -20.3018 | 4.0009 | 4.4037 | 4.3854 | -119.5587 | 116.3406 | -3.9825 | 116.7343 | 123.4497 | -122.8043 | -0.36163 | 0.15564 | 0.39368 | 123.1979 | 123.6008 | 0.62256 | 119.4443 | 116.7343 | 123.5825 | 98.8953 | -0.36163 | 119.4443 | 116.7343 | 98.8953 | 0.62256 | 123.5825 | -7.0862 | -123.7885
1647.9844 | 123.5275 | -118.808 | 4.5731 | 0.4243 | 0.039425 | -0.02537 | 0.064298 | -0.057894 | 0.033672 | 0.10377 | -2.7969 | 0.19226 | -2.9251 | 4.3304 | -118.4097 | -20.05 | 4.5731 | 4.6097 | 4.6829 | -119.2429 | 115.8829 | -4.3808 | 116.011 | 123.1384 | -122.9828 | -0.43488 | 0.10986 | 0.12817 | 123.381 | 123.4177 | 0.39825 | 119.0002 | 116.011 | 123.4909 | 98.7579 | -0.43488 | 119.0002 | 116.011 | 98.7579 | 0.39825 | 123.4909 | -7.4982 | -123.8159
1648.9219 | 123.4222 | -119.0277 | 4.4037 | 0.1649 | 0.031949 | -0.026438 | 0.076048 | -0.046145 | 0.043285 | 0.1027 | -2.6001 | 0.28839 | -2.9343 | 4.4495 | -118.2999 | -20.1553 | 4.1611 | 4.5731 | 4.541 | -119.371 | 116.0934 | -4.1153 | 116.4276 | 123.4772 | -122.7036 | -0.34332 | 0.13733 | 0.33417 | 123.1888 | 123.6008 | 0.72784 | 119.3161 | 116.4276 | 123.5687 | 98.8724 | -0.34332 | 119.3161 | 116.4276 | 98.8724 | 0.72784 | 123.5687 | -7.338 | -123.7747
1649.9844 | 123.4268 | -118.9087 | 4.4815 | -0.10976 | 0.049038 | -0.014689 | 0.079252 | -0.050418 | 0.056103 | 0.1059 | -2.3346 | 0.27466 | -2.829 | 4.4861 | -118.3228 | -20.2011 | 4.2709 | 4.6005 | 4.6555 | -119.2795 | 116.0797 | -4.2068 | 116.5741 | 123.3948 | -122.8043 | -0.37079 | 0.17395 | 0.49438 | 123.1796 | 123.5092 | 0.58594 | 119.1833 | 116.5741 | 123.5641 | 98.7076 | -0.37079 | 119.1833 | 116.5741 | 98.7076 | 0.58594 | 123.5641 | -7.3105 | -123.761
1650.9219 | 123.436 | -118.9819 | 4.422 | -0.18605 | 0.04797 | -0.020029 | 0.08032 | -0.063235 | 0.059307 | 0.098426 | -2.5085 | 0.28381 | -2.8702 | 4.4403 | -118.3548 | -20.3522 | 4.2343 | 4.5868 | 4.5868 | -119.339 | 116.1118 | -4.1382 | 116.4734 | 123.4222 | -122.7768 | -0.35706 | 0.16479 | 0.36163 | 123.2162 | 123.5687 | 0.62714 | 119.2657 | 116.4734 | 123.5687 | 98.6298 | -0.35706 | 119.2657 | 116.4734 | 98.6298 | 0.62714 | 123.5687 | -7.2922 | -123.761
1651.9219 | 123.4634 | -118.8995 | 4.5319 | -0.24709 | 0.029812 | -0.034983 | 0.08032 | -0.047213 | 0.05183 | 0.095222 | -2.449 | 0.27466 | -2.8336 | 4.5502 | -118.1122 | -20.2011 | 4.3121 | 4.66 | 4.6875 | -119.2245 | 116.066 | -4.2572 | 116.4505 | 123.4497 | -122.644 | -0.32501 | 0.15564 | 0.38452 | 123.2117 | 123.5596 | 0.78735 | 119.1742 | 116.4505 | 123.587 | 98.6984 | -0.32501 | 119.1742 | 116.4505 | 98.6984 | 0.78735 | 123.587 | -7.3654 | -123.7564
1652.9844 | 123.5321 | -119.0735 | 4.2755 | 0.40904 | 0.039425 | -0.024302 | 0.071775 | -0.052554 | 0.045422 | 0.10804 | -2.5177 | 0.21515 | -2.8976 | 4.1565 | -117.4393 | -20.2423 | 4.2206 | 4.3259 | 4.4815 | -119.4946 | 116.1758 | -4.0604 | 116.5558 | 123.23 | -121.7148 | -0.42114 | 0.20599 | 0.37994 | 123.2941 | 123.3994 | 1.6342 | 119.2886 | 116.5558 | 123.555 | 98.8312 | -0.42114 | 119.2886 | 116.5558 | 98.8312 | 1.6342 | 123.555 | -7.1732 | -123.7701
1653.9219 | 123.5001 | -118.9774 | 4.4632 | 0.37852 | 0.043698 | -0.0082804 | 0.076048 | -0.046145 | 0.055035 | 0.099494 | -2.5314 | 0.28839 | -2.8427 | 4.4586 | -118.1808 | -20.1553 | 4.2984 | 4.7333 | 4.5639 | -119.3069 | 116.1346 | -4.1748 | 116.4459 | 123.436 | -122.644 | -0.32959 | 0.10071 | 0.31128 | 123.2758 | 123.7106 | 0.79651 | 119.2657 | 116.4459 | 123.5413 | 98.822 | -0.32959 | 119.2657 | 116.4459 | 98.822 | 0.79651 | 123.5413 | -7.3059 | -123.7701
1654.9844 | 123.468 | -118.927 | 4.4952 | -0.079243 | 0.044766 | -0.010416 | 0.084592 | -0.053622 | 0.044354 | 0.1059 | -2.4078 | 0.27008 | -2.7832 | 4.5822 | -117.1234 | -19.9997 | 4.2572 | 4.509 | 4.6692 | -119.3298 | 116.1438 | -4.2252 | 116.5192 | 123.5092 | -121.6187 | -0.40283 | 0.17395 | 0.37537 | 123.1842 | 123.436 | 1.8036 | 119.1971 | 116.5192 | 123.5962 | 98.9273 | -0.40283 | 119.1971 | 116.5192 | 98.9273 | 1.8036 | 123.5962 | -7.2784 | -123.8251
1655.9219 | 123.5046 | -118.8995 | 4.4861 | 0.47007 | 0.034085 | 0.0077416 | 0.065366 | -0.048281 | 0.056103 | 0.1059 | -2.5177 | 0.2655 | -2.8976 | 4.5181 | -117.5491 | -19.7617 | 4.3213 | 4.5456 | 4.6738 | -119.3069 | 116.0019 | -4.2206 | 116.3818 | 123.4177 | -122.0352 | -0.40741 | 0.18768 | 0.37994 | 123.2208 | 123.4451 | 1.3504 | 119.165 | 116.3818 | 123.5733 | 99.1379 | -0.40741 | 119.165 | 116.3818 | 99.1379 | 1.3504 | 123.5733 | -7.3837 | -123.793
1656.9844 | 123.4451 | -118.7943 | 4.6463 | -0.3539 | 0.039425 | -0.024302 | 0.082456 | -0.041873 | 0.048626 | 0.10911 | -2.5406 | 0.25635 | -2.9526 | 4.6646 | -117.4164 | -19.9631 | 4.4403 | 4.8248 | 4.8431 | -119.1376 | 115.8417 | -4.39 | 116.2537 | 123.4589 | -122.0627 | -0.34332 | 0.19684 | 0.41199 | 123.2346 | 123.6191 | 1.3779 | 119.0506 | 116.2537 | 123.6374 | 98.8312 | -0.34332 | 119.0506 | 116.2537 | 98.8312 | 1.3779 | 123.6374 | -7.5989 | -123.7839
1657.9219 | 123.4955 | -118.7073 | 4.6829 | 0.22593 | 0.018063 | -0.02537 | 0.053617 | -0.041873 | 0.037945 | 0.10056 | -2.6047 | 0.23346 | -2.9251 | 4.5547 | -116.7343 | -20.0088 | 4.5547 | 4.7791 | 4.8523 | -119.0964 | 115.7822 | -4.4495 | 116.1026 | 123.262 | -121.4172 | -0.3891 | 0.16937 | 0.32044 | 123.262 | 123.4863 | 1.973 | 118.9407 | 116.1026 | 123.5596 | 98.6984 | -0.3891 | 118.9407 | 116.1026 | 98.6984 | 1.973 | 123.5596 | -7.608 | -123.7793
1658.9219 | 123.4543 | -118.7988 | 4.5914 | -0.24709 | 0.037289 | -0.010416 | 0.085661 | -0.058962 | 0.056103 | 0.10377 | -2.243 | 0.25635 | -2.6138 | 4.5639 | -116.8625 | -19.3085 | 4.3579 | 4.7287 | 4.7012 | -119.2245 | 116.185 | -4.335 | 116.5558 | 123.3627 | -121.4539 | -0.42572 | 0.10986 | 0.37079 | 123.1567 | 123.5275 | 1.9363 | 119.0552 | 116.5558 | 123.5001 | 99.4904 | -0.42572 | 119.0552 | 116.5558 | 99.4904 | 1.9363 | 123.5001 | -7.2052 | -123.8159
1659.9844 | 123.436 | -118.5562 | 4.8981 | 1.7518 | 0.037289 | -0.017893 | 0.070707 | -0.053622 | 0.047558 | 0.10056 | -2.3758 | 0.29297 | -2.8381 | 5.0308 | -116.9678 | -19.6976 | 4.6921 | 5.0125 | 5.1315 | -118.8721 | 115.7181 | -4.6051 | 116.1804 | 123.587 | -121.8658 | -0.31586 | 0.23346 | 0.46234 | 123.2483 | 123.5687 | 1.5884 | 118.8492 | 116.1804 | 123.6877 | 98.8586 | -0.31586 | 118.8492 | 116.1804 | 98.8586 | 1.5884 | 123.6877 | -7.7362 | -123.7701
1660.9219 | 123.436 | -119.0277 | 4.39 | -0.094502 | 0.038357 | -0.023234 | 0.086729 | -0.034396 | 0.061443 | 0.097358 | -2.243 | 0.30212 | -2.6184 | 4.3671 | -118.3365 | -19.7754 | 4.1656 | 4.5136 | 4.4998 | -119.4122 | 116.4093 | -4.0878 | 116.7847 | 123.3948 | -122.7264 | -0.38452 | 0.10986 | 0.37537 | 123.1934 | 123.5413 | 0.69122 | 119.3298 | 116.7847 | 123.5275 | 99.2523 | -0.38452 | 119.3298 | 116.7847 | 99.2523 | 0.69122 | 123.5275 | -7.0084 | -123.8022
1661.9844 | 123.4543 | -118.9819 | 4.3808 | -0.39968 | 0.021267 | -0.027506 | 0.053617 | -0.05469 | 0.033672 | 0.11445 | -2.2018 | 0.23346 | -2.5497 | 4.2709 | -118.071 | -19.4733 | 4.2023 | 4.4724 | 4.5319 | -119.4168 | 116.4322 | -4.1473 | 116.7801 | 123.2529 | -122.4518 | -0.43488 | 0.15106 | 0.3479 | 123.1842 | 123.4543 | 0.91095 | 119.2154 | 116.7801 | 123.5138 | 99.5087 | -0.43488 | 119.2154 | 116.7801 | 99.5087 | 0.91095 | 123.5138 | -6.9305 | -123.7976
1662.9219 | 123.4726 | -118.9041 | 4.4724 | 0.14964 | 0.031949 | -0.031779 | 0.061094 | -0.065371 | 0.037945 | 0.10911 | -2.2614 | 0.2243 | -2.5635 | 4.3625 | -117.7734 | -19.6381 | 4.303 | 4.5319 | 4.6555 | -119.3161 | 116.3406 | -4.248 | 116.6428 | 123.2666 | -122.2458 | -0.41199 | 0.18311 | 0.30212 | 123.2071 | 123.436 | 1.1307 | 119.1284 | 116.6428 | 123.5596 | 99.2661 | -0.41199 | 119.1284 | 116.6428 | 99.2661 | 1.1307 | 123.5596 | -7.0358 | -123.7885
1663.9844 | 123.4268 | -118.8675 | 4.5364 | 0.1649 | 0.033017 | -0.0050764 | 0.094205 | -0.050418 | 0.055035 | 0.094154 | -2.2247 | 0.24261 | -2.5955 | 4.5593 | -117.4301 | -19.6655 | 4.3396 | 4.7058 | 4.6921 | -119.2474 | 116.272 | -4.2938 | 116.6428 | 123.4268 | -121.9666 | -0.37994 | 0.15564 | 0.37079 | 123.2071 | 123.5733 | 1.4374 | 119.1101 | 116.6428 | 123.5596 | 99.202 | -0.37994 | 119.1101 | 116.6428 | 99.202 | 1.4374 | 123.5596 | -7.132 | -123.7839
1664.9219 | 123.4085 | -119.2245 | 4.2252 | -0.41494 | 0.04263 | -0.014689 | 0.082456 | -0.052554 | 0.056103 | 0.10377 | -2.2064 | 0.25177 | -2.5681 | 4.2709 | -118.483 | -19.7342 | 3.9093 | 4.3167 | 4.39 | -119.5724 | 116.6565 | -3.9734 | 117.0181 | 123.4955 | -122.7081 | -0.3479 | 0.1648 | 0.36163 | 123.1338 | 123.5413 | 0.74158 | 119.4763 | 117.0181 | 123.6145 | 99.4904 | -0.3479 | 119.4763 | 117.0181 | 99.4904 | 0.74158 | 123.6145 | -6.7932 | -123.7976
1666 | 123.5504 | -119.1971 | 4.184 | -0.53701 | 0.026608 | -0.030711 | 0.050413 | -0.062167 | 0.021923 | 0.10377 | -2.8061 | 0.21973 | -3.1631 | 3.9917 | -118.0023 | -19.1528 | 4.1016 | 4.2068 | 4.3762 | -119.6045 | 116.0339 | -3.9642 | 116.391 | 123.1888 | -122.1863 | -0.40741 | 0.19226 | 0.35706 | 123.2986 | 123.4039 | 1.1948 | 119.4168 | 116.391 | 123.5733 | 100.0443 | -0.40741 | 119.4168 | 116.391 | 100.0443 | 1.1948 | 123.5733 | -7.3471 | -123.7885
1666.9219 | 123.4177 | -119.2108 | 4.2114 | 0.058086 | 0.037289 | -0.0029404 | 0.083524 | -0.058962 | 0.050762 | 0.10484 | -2.8152 | 0.25177 | -3.1677 | 4.2114 | -118.3823 | -19.1574 | 3.9688 | 4.3488 | 4.303 | -119.5953 | 116.0431 | -3.9597 | 116.3956 | 123.4222 | -122.5937 | -0.38452 | 0.091553 | 0.35248 | 123.1796 | 123.5596 | 0.82855 | 119.4626 | 116.3956 | 123.5138 | 100.0534 | -0.38452 | 119.4626 | 116.3956 | 100.0534 | 0.82855 | 123.5138 | -7.3792 | -123.8068
1667.9844 | 123.4634 | -119.2932 | 4.1565 | -0.079243 | 0.022336 | -0.017893 | 0.084592 | -0.046145 | 0.048626 | 0.10377 | -2.7695 | 0.25177 | -3.1769 | 4.0604 | -118.6981 | -18.956 | 4.1565 | 4.3121 | 4.2572 | -119.5999 | 116.1163 | -3.9047 | 116.5237 | 123.3536 | -122.8546 | -0.3067 | 0.10071 | 0.40741 | 123.4497 | 123.6053 | 0.59509 | 119.545 | 116.5237 | 123.5504 | 100.3372 | -0.3067 | 119.545 | 116.5237 | 100.3372 | 0.59509 | 123.5504 | -7.3334 | -123.7564
1668.9219 | 123.4589 | -119.0598 | 4.3671 | -0.3539 | 0.041562 | -0.015757 | 0.077116 | -0.048281 | 0.049694 | 0.11018 | -3.0487 | 0.25635 | -3.4149 | 4.3671 | -118.5059 | -19.4092 | 4.097 | 4.4495 | 4.5044 | -119.4443 | 115.6448 | -4.1107 | 116.011 | 123.4268 | -122.8729 | -0.38452 | 0.13733 | 0.36621 | 123.1567 | 123.5092 | 0.55389 | 119.3161 | 116.011 | 123.5641 | 99.6506 | -0.38452 | 119.3161 | 116.011 | 99.6506 | 0.55389 | 123.5641 | -7.782 | -123.8113
1669.9844 | 123.468 | -119.2429 | 4.1611 | -0.46071 | 0.022336 | -0.032847 | 0.056821 | -0.052554 | 0.033672 | 0.11124 | -2.7924 | 0.24261 | -3.1494 | 4.0146 | -118.84 | -19.0613 | 3.9825 | 4.2343 | 4.2938 | -119.6548 | 116.0934 | -3.9185 | 116.4505 | 123.2574 | -123.0011 | -0.41199 | 0.13275 | 0.35706 | 123.2254 | 123.4772 | 0.40283 | 119.4855 | 116.4505 | 123.5367 | 100.1816 | -0.41199 | 119.4855 | 116.4505 | 100.1816 | 0.40283 | 123.5367 | -7.3105 | -123.8159
1670.9219 | 123.4085 | -119.3527 | 4.0878 | -0.29287 | 0.028744 | -0.030711 | 0.08032 | -0.055758 | 0.041149 | 0.098426 | -2.8015 | 0.29297 | -3.1448 | 4.0512 | -117.4988 | -18.9056 | 3.7994 | 4.2618 | 4.1748 | -119.696 | 116.2079 | -3.7949 | 116.5512 | 123.4039 | -121.5866 | -0.34332 | 0.086975 | 0.34332 | 123.1522 | 123.6145 | 1.8539 | 119.6457 | 116.5512 | 123.5275 | 100.4471 | -0.34332 | 119.6457 | 116.5512 | 100.4471 | 1.8539 | 123.5275 | -7.2327 | -123.7839
1671.9844 | 123.3902 | -119.3481 | 4.0649 | 0.1649 | 0.046902 | -0.022166 | 0.084592 | -0.049349 | 0.060375 | 0.10377 | -2.8381 | 0.26093 | -3.1815 | 4.1428 | -117.6682 | -18.9514 | 3.8452 | 4.2755 | 4.1702 | -119.6823 | 116.1667 | -3.804 | 116.51 | 123.4909 | -121.7331 | -0.33417 | 0.10529 | 0.34332 | 123.1934 | 123.6237 | 1.68 | 119.6091 | 116.51 | 123.5184 | 100.3967 | -0.33417 | 119.6091 | 116.51 | 100.3967 | 1.68 | 123.5184 | -7.2464 | -123.7473
1672.9219 | 123.3673 | -119.2795 | 4.1565 | -0.49123 | 0.037289 | -0.024302 | 0.069639 | -0.050418 | 0.04649 | 0.10484 | -2.8015 | 0.26093 | -3.1448 | 4.0695 | -117.8421 | -18.924 | 3.8223 | 4.3854 | 4.2618 | -119.6228 | 116.1346 | -3.8956 | 116.478 | 123.349 | -121.9986 | -0.34332 | 0.10529 | 0.34332 | 123.1018 | 123.6649 | 1.4374 | 119.5404 | 116.478 | 123.5413 | 100.3555 | -0.34332 | 119.5404 | 116.478 | 100.3555 | 1.4374 | 123.5413 | -7.3013 | -123.7793
1673.9844 | 123.5046 | -119.2703 | 4.0878 | 0.50059 | 0.037289 | 0.00026463 | 0.08032 | -0.060031 | 0.048626 | 0.10377 | -2.9892 | 0.23346 | -3.3234 | 4.0649 | -118.7714 | -19.3314 | 3.9963 | 4.1794 | 4.2618 | -119.664 | 115.947 | -3.8544 | 116.2811 | 123.3353 | -122.8592 | -0.39368 | 0.17395 | 0.33417 | 123.2666 | 123.4497 | 0.49896 | 119.5038 | 116.2811 | 123.5321 | 99.939 | -0.39368 | 119.5038 | 116.2811 | 99.939 | 0.49896 | 123.5321 | -7.4112 | -123.7518
1674.9219 | 123.4772 | -119.3298 | 4.0878 | -0.39968 | 0.033017 | -0.012553 | 0.085661 | -0.040805 | 0.045422 | 0.10804 | -2.829 | 0.2655 | -3.2181 | 4.1702 | -118.7531 | -19.574 | 3.8589 | 4.1931 | 4.3076 | -119.7052 | 116.1118 | -3.8223 | 116.5009 | 123.5001 | -122.8409 | -0.37537 | 0.21973 | 0.3891 | 123.1888 | 123.5229 | 0.57678 | 119.5953 | 116.5009 | 123.6374 | 99.7559 | -0.37537 | 119.5953 | 116.5009 | 99.7559 | 0.57678 | 123.6374 | -7.3059 | -123.793
1675.9844 | 123.4085 | -118.9636 | 4.4952 | -0.26235 | 0.034085 | -0.030711 | 0.073911 | -0.048281 | 0.04649 | 0.11445 | -2.9617 | 0.2655 | -3.2822 | 4.422 | -118.4418 | -19.5511 | 4.1611 | 4.6188 | 4.5639 | -119.2841 | 115.6815 | -4.2297 | 116.0019 | 123.3856 | -122.937 | -0.32044 | 0.068665 | 0.32044 | 123.1247 | 123.5825 | 0.52185 | 119.2291 | 116.0019 | 123.5275 | 99.4125 | -0.32044 | 119.2291 | 116.0019 | 99.4125 | 0.52185 | 123.5275 | -7.7774 | -123.7793
1676.9219 | 123.4085 | -119.3619 | 4.0833 | -0.46071 | 0.039425 | -0.043528 | 0.066434 | -0.051486 | 0.036877 | 0.10911 | -2.9892 | 0.27008 | -3.3096 | 4.0329 | -118.7256 | -19.9036 | 3.8132 | 4.2618 | 4.1885 | -119.6732 | 116.0522 | -3.8132 | 116.3727 | 123.3948 | -122.8088 | -0.31128 | 0.10529 | 0.32043 | 123.175 | 123.6237 | 0.63629 | 119.632 | 116.3727 | 123.5504 | 99.4583 | -0.31128 | 119.632 | 116.3727 | 99.4583 | 0.63629 | 123.5504 | -7.3929 | -123.7564
1677.9844 | 123.4085 | -119.2429 | 4.1931 | 0.073345 | 0.043698 | -0.024302 | 0.078184 | -0.051486 | 0.050762 | 0.10163 | -3.0075 | 0.30212 | -3.3737 | 4.216 | -118.8904 | -19.9356 | 3.9688 | 4.335 | 4.3304 | -119.5816 | 115.8691 | -3.891 | 116.2354 | 123.4589 | -123.0835 | -0.33875 | 0.13733 | 0.36621 | 123.2117 | 123.5779 | 0.35248 | 119.545 | 116.2354 | 123.5733 | 99.3073 | -0.33875 | 119.545 | 116.2354 | 99.3073 | 0.35248 | 123.5733 | -7.5668 | -123.7747
1678.9219 | 123.5504 | -119.1879 | 4.1794 | -0.39968 | 0.029812 | -0.018961 | 0.05789 | -0.052554 | 0.036877 | 0.11018 | -2.98 | 0.21515 | -3.3463 | 4.01 | -119.0964 | -19.9493 | 4.1061 | 4.2023 | 4.3671 | -119.6091 | 115.8417 | -3.9642 | 116.2079 | 123.1979 | -123.2758 | -0.42114 | 0.18768 | 0.36621 | 123.2941 | 123.3902 | 0.091552 | 119.4031 | 116.2079 | 123.555 | 99.2386 | -0.42114 | 119.4031 | 116.2079 | 99.2386 | 0.091552 | 123.555 | -7.5256 | -123.7885
1679.9219 | 123.4085 | -118.9682 | 4.4495 | -0.39968 | 0.026608 | -0.027506 | 0.078184 | -0.049349 | 0.042217 | 0.097358 | -3.0075 | 0.27924 | -3.3188 | 4.4495 | -118.689 | -19.6976 | 4.2343 | 4.6646 | 4.6463 | -119.2612 | 115.6494 | -4.1702 | 115.9607 | 123.4177 | -123.1384 | -0.29297 | 0.19684 | 0.31128 | 123.2025 | 123.6328 | 0.27924 | 119.2474 | 115.9607 | 123.6145 | 99.2706 | -0.29297 | 119.2474 | 115.9607 | 99.2706 | 0.27924 | 123.6145 | -7.7683 | -123.7106
1680.9844 | 123.4131 | -119.1101 | 4.3488 | 0.30223 | 0.038357 | -0.012553 | 0.096342 | -0.062167 | 0.052898 | 0.099494 | -3.0121 | 0.2655 | -3.3691 | 4.4815 | -118.6981 | -19.3497 | 4.1519 | 4.4632 | 4.4952 | -119.4168 | 115.741 | -4.0833 | 116.098 | 123.5916 | -123.0469 | -0.3067 | 0.14648 | 0.35706 | 123.262 | 123.5733 | 0.41199 | 119.3756 | 116.098 | 123.6053 | 99.7604 | -0.3067 | 119.3756 | 116.098 | 99.7604 | 0.41199 | 123.6053 | -7.7179 | -123.7656
1681.9219 | 123.4497 | -119.0552 | 4.3808 | -0.50649 | 0.018063 | -0.023234 | 0.065366 | -0.047213 | 0.026196 | 0.11231 | -2.98 | 0.23346 | -3.3188 | 4.2847 | -118.7164 | -19.7159 | 4.1565 | 4.5273 | 4.5044 | -119.4031 | 115.7364 | -4.1473 | 116.0751 | 123.3398 | -123.0972 | -0.3479 | 0.1236 | 0.33874 | 123.2117 | 123.5825 | 0.33875 | 119.2886 | 116.0751 | 123.5596 | 99.3393 | -0.3479 | 119.2886 | 116.0751 | 99.3393 | 0.33875 | 123.5596 | -7.6996 | -123.7839
1682.9219 | 123.5458 | -119.101 | 4.2435 | -0.38442 | 0.010586 | -0.032847 | 0.054685 | -0.061099 | -0.011188 | 0.11338 | -2.8793 | 0.21057 | -3.2501 | 4.2435 | -117.5217 | -19.7296 | 4.0878 | 4.3716 | 4.4449 | -119.4992 | 115.8508 | -4.0329 | 116.2216 | 123.3444 | -121.7651 | -0.39825 | 0.20142 | 0.37079 | 123.1888 | 123.4726 | 1.5793 | 119.3115 | 116.2216 | 123.5458 | 99.3713 | -0.39825 | 119.3115 | 116.2216 | 99.3713 | 1.5793 | 123.5458 | -7.4936 | -123.7427
1683.9844 | 123.4085 | -118.9911 | 4.509 | -0.1708 | 0.033017 | -0.015757 | 0.091001 | -0.049349 | 0.039013 | 0.1059 | -2.7969 | 0.25177 | -3.1448 | 4.715 | -118.5471 | -19.78 | 4.1382 | 4.8523 | 4.6188 | -119.22 | 115.8463 | -4.2572 | 116.1942 | 123.7061 | -123.056 | -0.22888 | 0.10986 | 0.3479 | 123.1293 | 123.8434 | 0.44403 | 119.2429 | 116.1942 | 123.6099 | 99.2111 | -0.22888 | 119.2429 | 116.1942 | 99.2111 | 0.44403 | 123.6099 | -7.6538 | -123.7289
1684.9219 | 123.5275 | -118.6478 | 4.6509 | -0.15554 | 0.014859 | -0.023234 | 0.05789 | -0.063235 | 0.018719 | 0.099494 | -2.6825 | 0.21973 | -3.0624 | 4.5364 | -118.5562 | -19.7891 | 4.6097 | 4.7058 | 4.8843 | -119.101 | 115.5853 | -4.4312 | 115.9653 | 123.1842 | -123.2071 | -0.45319 | 0.23346 | 0.37994 | 123.2574 | 123.3536 | 0.091553 | 118.8675 | 115.9653 | 123.5321 | 98.8586 | -0.45319 | 118.8675 | 115.9653 | 98.8586 | 0.091553 | 123.5321 | -7.7133 | -123.7518
1685.9844 | 123.4268 | -119.2337 | 4.1702 | -0.55227 | 0.022336 | -0.023234 | 0.083524 | -0.047213 | 0.040081 | 0.097358 | -2.7924 | 0.25635 | -3.1082 | 4.1748 | -118.9362 | -19.6701 | 3.9001 | 4.3167 | 4.3076 | -119.5953 | 116.1255 | -3.9139 | 116.4413 | 123.4085 | -123.1064 | -0.36163 | 0.13733 | 0.31586 | 123.1339 | 123.5504 | 0.29755 | 119.4901 | 116.4413 | 123.5413 | 99.5636 | -0.36163 | 119.4901 | 116.4413 | 99.5636 | 0.29755 | 123.5413 | -7.2784 | -123.7656
1686.9219 | 123.4314 | -119.0643 | 4.3488 | -0.3539 | 0.033017 | -0.031779 | 0.069639 | -0.060031 | 0.031536 | 0.10484 | -2.7695 | 0.23346 | -3.1219 | 4.2847 | -118.7531 | -19.3588 | 4.1519 | 4.4815 | 4.4815 | -119.426 | 115.9424 | -4.1153 | 116.2949 | 123.349 | -123.1018 | -0.36163 | 0.13275 | 0.35248 | 123.2162 | 123.5458 | 0.31128 | 119.2978 | 116.2949 | 123.5458 | 99.7055 | -0.36163 | 119.2978 | 116.2949 | 99.7055 | 0.31128 | 123.5458 | -7.4707 | -123.7747
1687.9844 | 123.5275 | -119.1559 | 4.2297 | -2.5817 | 0.021267 | -0.043528 | 0.067503 | -0.066439 | 0.034741 | 0.090949 | -2.8015 | 0.20142 | -3.0716 | 4.0878 | -118.895 | -19.3588 | 4.1199 | 4.2755 | 4.39 | -119.5587 | 116.0843 | -4.0283 | 116.3544 | 123.2437 | -123.1247 | -0.40283 | 0.16022 | 0.27008 | 123.2758 | 123.4314 | 0.26093 | 119.3573 | 116.3544 | 123.5458 | 99.7971 | -0.40283 | 119.3573 | 116.3544 | 99.7971 | 0.26093 | 123.5458 | -7.3013 | -123.7885
1688.9219 | 123.555 | -118.8263 | 4.5273 | -0.23183 | 0.011654 | -0.023234 | 0.066434 | -0.060031 | 0.024059 | 0.10377 | -2.7054 | 0.21973 | -3.0808 | 4.2892 | -118.6798 | -19.162 | 4.4174 | 4.6188 | 4.66 | -119.2657 | 115.7455 | -4.3076 | 116.1209 | 123.1155 | -123.2071 | -0.43945 | 0.13275 | 0.37537 | 123.2437 | 123.4451 | 0.14648 | 119.046 | 116.1209 | 123.4863 | 99.6643 | -0.43945 | 119.046 | 116.1209 | 99.6643 | 0.14648 | 123.4863 | -7.608 | -123.793
1689.9844 | 123.4818 | -118.9133 | 4.422 | 0.13438 | 0.026608 | -0.048869 | 0.069639 | -0.055758 | 0.027264 | 0.10056 | -2.8244 | 0.23346 | -3.1128 | 4.2709 | -118.7119 | -19.368 | 4.2389 | 4.4495 | 4.6005 | -119.3344 | 115.8005 | -4.1885 | 116.0889 | 123.1842 | -123.1339 | -0.42114 | 0.17853 | 0.28839 | 123.1522 | 123.3627 | 0.20142 | 119.1467 | 116.0889 | 123.5138 | 99.5453 | -0.42114 | 119.1467 | 116.0889 | 99.5453 | 0.20142 | 123.5138 | -7.5348 | -123.7564
1690.9219 | 123.5458 | -118.6249 | 4.6783 | -0.18605 | 0.026608 | -0.02537 | 0.064298 | -0.066439 | 0.033672 | 0.10911 | -2.6825 | 0.23346 | -3.0487 | 4.4815 | -118.5471 | -19.1116 | 4.6463 | 4.7424 | 4.8614 | -119.0643 | 115.5762 | -4.4449 | 115.9424 | 123.1064 | -123.2254 | -0.43945 | 0.1831 | 0.36621 | 123.2712 | 123.3673 | 0.07782 | 118.8583 | 115.9424 | 123.4863 | 99.5132 | -0.43945 | 118.8583 | 115.9424 | 99.5132 | 0.07782 | 123.4863 | -7.7271 | -123.7427
1691.9844 | 123.4818 | -119.1467 | 4.2068 | 0.348 | 0.028744 | -0.04246 | 0.071775 | -0.064303 | 0.031536 | 0.099494 | -2.7603 | 0.21057 | -3.1174 | 4.1153 | -119.0552 | -19.4321 | 4.0924 | 4.2526 | 4.39 | -119.5496 | 116.0294 | -3.9963 | 116.3864 | 123.262 | -123.262 | -0.40283 | 0.18311 | 0.35706 | 123.2391 | 123.3994 | 0.091553 | 119.3573 | 116.3864 | 123.5367 | 99.7147 | -0.40283 | 119.3573 | 116.3864 | 99.7147 | 0.091553 | 123.5367 | -7.3242 | -123.7564
1692.9219 | 123.5092 | -119.2795 | 4.0787 | -0.033467 | 0.021267 | -0.020029 | 0.062162 | -0.066439 | 0.019787 | 0.11231 | -2.742 | 0.21515 | -3.0853 | 3.9597 | -119.1834 | -19.2719 | 3.9825 | 4.1565 | 4.2618 | -119.6686 | 116.1942 | -3.8635 | 116.5375 | 123.2391 | -123.262 | -0.3891 | 0.18311 | 0.34332 | 123.262 | 123.436 | 0.09613 | 119.4946 | 116.5375 | 123.5413 | 100.0076 | -0.3891 | 119.4946 | 116.5375 | 100.0076 | 0.09613 | 123.5413 | -7.164 | -123.7473
1693.9219 | 123.5229 | -118.5196 | 4.8111 | -0.079243 | 0.010586 | -0.041392 | 0.073911 | -0.064303 | 0.0294 | 0.10377 | -2.6962 | 0.21973 | -3.0533 | 4.6646 | -118.5287 | -19.162 | 4.7012 | 4.8477 | 4.9759 | -118.959 | 115.4663 | -4.5914 | 115.8234 | 123.1842 | -123.3398 | -0.43945 | 0.16479 | 0.35706 | 123.2208 | 123.3673 | -0.009156 | 118.7393 | 115.8234 | 123.4955 | 99.3576 | -0.43945 | 118.7393 | 115.8234 | 99.3576 | -0.009156 | 123.4955 | -7.8644 | -123.7701
1694.9844 | 123.5001 | -118.7073 | 4.6051 | 0.36326 | 0.034085 | -0.030711 | 0.089933 | -0.064303 | 0.042217 | 0.095222 | -2.7512 | 0.23346 | -3.1311 | 4.5685 | -118.6203 | -19.0796 | 4.541 | 4.6875 | 4.7882 | -119.1284 | 115.5762 | -4.3716 | 115.9561 | 123.2758 | -123.2254 | -0.42114 | 0.18311 | 0.37994 | 123.2483 | 123.3948 | 0.086975 | 118.9407 | 115.9561 | 123.4955 | 99.6277 | -0.42114 | 118.9407 | 115.9561 | 99.6277 | 0.086975 | 123.4955 | -7.7362 | -123.7335
1695.9219 | 123.4909 | -119.3069 | 4.0695 | 0.088604 | 0.022336 | -0.045664 | 0.067503 | -0.060031 | 0.021923 | 0.10377 | -2.9526 | 0.21973 | -3.186 | 3.9368 | -119.1879 | -19.5053 | 3.9093 | 4.1245 | 4.2068 | -119.6686 | 116.1209 | -3.8498 | 116.3544 | 123.2437 | -123.2574 | -0.36163 | 0.13733 | 0.23346 | 123.2162 | 123.4314 | 0.11902 | 119.5267 | 116.3544 | 123.5138 | 99.8016 | -0.36163 | 119.5267 | 116.3544 | 99.8016 | 0.11902 | 123.5138 | -7.2556 | -123.7381
1696.9844 | 123.5046 | -118.8583 | 4.454 | 0.01231 | 0.019131 | -0.011485 | 0.071775 | -0.063235 | 0.041149 | 0.095222 | -2.8198 | 0.2243 | -3.1357 | 4.1107 | -118.8217 | -19.1116 | 4.3854 | 4.6005 | 4.4907 | -119.2978 | 115.7227 | -4.2297 | 116.0385 | 122.9691 | -123.2758 | -0.43945 | 0.036621 | 0.31586 | 123.2437 | 123.4589 | 0.036621 | 119.0826 | 116.0385 | 123.349 | 99.7467 | -0.43945 | 119.0826 | 116.0385 | 99.7467 | 0.036621 | 123.349 | -7.5897 | -123.7518
1697.9219 | 123.4863 | -118.2587 | 5.1453 | 0.11912 | 0.023404 | -0.04246 | 0.065366 | -0.073916 | 0.032604 | 0.10911 | -2.7695 | 0.21973 | -3.0716 | 5.0858 | -117.984 | -18.9972 | 4.9988 | 5.2734 | 5.3055 | -118.5745 | 115.1871 | -4.9255 | 115.4892 | 123.3444 | -123.1293 | -0.31586 | 0.16022 | 0.30212 | 123.2574 | 123.5321 | 0.27466 | 118.4784 | 115.4892 | 123.5641 | 99.2615 | -0.31586 | 118.4784 | 115.4892 | 99.2615 | 0.27466 | 123.5641 | -8.2169 | -123.7198
1698.9844 | 123.5596 | -118.515 | 4.7928 | -0.72011 | 0.03088 | -0.045664 | 0.072843 | -0.063235 | 0.021923 | 0.1027 | -2.6733 | 0.21973 | -3.0212 | 4.7195 | -118.0527 | -19.2261 | 4.8019 | 4.7974 | 4.9713 | -118.9682 | 115.4938 | -4.5731 | 115.8417 | 123.2346 | -122.8455 | -0.45319 | 0.17853 | 0.3479 | 123.317 | 123.3124 | 0.46234 | 118.7347 | 115.8417 | 123.4863 | 99.2889 | -0.45319 | 118.7347 | 115.8417 | 99.2889 | 0.46234 | 123.4863 | -7.814 | -123.761
1699.9219 | 123.5504 | -118.6432 | 4.6967 | 0.39378 | 0.036221 | -0.026438 | 0.088865 | -0.067507 | 0.037945 | 0.090949 | -2.8427 | 0.21973 | -3.2364 | 4.6463 | -118.5745 | -19.6655 | 4.5456 | 4.8523 | 4.8294 | -119.0369 | 115.4068 | -4.4769 | 115.8005 | 123.2895 | -123.2712 | -0.39368 | 0.13275 | 0.39368 | 123.1888 | 123.4955 | 0.068664 | 118.8629 | 115.8005 | 123.4726 | 98.9777 | -0.39368 | 118.8629 | 115.8005 | 98.9777 | 0.068664 | 123.4726 | -7.933 | -123.7335
1700.9844 | 123.4131 | -118.5928 | 4.8111 | -0.50649 | 0.044766 | -0.018961 | 0.085661 | -0.057894 | 0.032604 | 0.098426 | -2.6825 | 0.28381 | -2.9663 | 4.8019 | -118.3777 | -18.8873 | 4.5639 | 4.9347 | 4.9118 | -118.9453 | 115.6265 | -4.5273 | 115.9103 | 123.3948 | -123.1888 | -0.35248 | 0.10071 | 0.28381 | 123.1567 | 123.5275 | 0.21515 | 118.8766 | 115.9103 | 123.5046 | 99.7055 | -0.35248 | 118.8766 | 115.9103 | 99.7055 | 0.21515 | 123.5046 | -7.7774 | -123.7564
1701.9219 | 123.5138 | -117.7368 | 5.5756 | 0.1649 | 0.034085 | -0.0478 | 0.066434 | -0.060031 | 0.025128 | 0.1027 | -2.5726 | 0.23346 | -2.8885 | 5.5481 | -117.5766 | -18.6127 | 5.397 | 5.6305 | 5.7587 | -118.1808 | 114.8483 | -5.3421 | 115.1642 | 123.2849 | -123.1522 | -0.44403 | 0.18311 | 0.31586 | 123.1339 | 123.3673 | 0.16022 | 117.9703 | 115.1642 | 123.4955 | 99.1241 | -0.44403 | 117.9703 | 115.1642 | 99.1241 | 0.16022 | 123.4955 | -8.4641 | -123.7564
1702.9844 | 123.5138 | -117.9062 | 5.4016 | 0.6074 | 0.037289 | -0.017893 | 0.078184 | -0.066439 | 0.041149 | 0.10163 | -2.5406 | 0.21515 | -2.9434 | 5.3513 | -117.7917 | -18.9056 | 5.4108 | 5.5069 | 5.6396 | -118.3044 | 114.9628 | -5.1865 | 115.3656 | 123.2574 | -123.1934 | -0.39825 | 0.23804 | 0.40283 | 123.317 | 123.4131 | 0.11444 | 118.1213 | 115.3656 | 123.5458 | 99.0005 | -0.39825 | 118.1213 | 115.3656 | 99.0005 | 0.11444 | 123.5458 | -8.345 | -123.7061
1703.9219 | 123.4909 | -118.5745 | 4.7516 | 0.36326 | 0.033017 | -0.022166 | 0.076048 | -0.062167 | 0.034741 | 0.099494 | -2.6367 | 0.23804 | -3.0075 | 4.6829 | -118.4784 | -18.8919 | 4.6829 | 4.8111 | 4.9576 | -118.9865 | 115.567 | -4.5135 | 115.9378 | 123.2574 | -123.23 | -0.41199 | 0.20599 | 0.37079 | 123.2574 | 123.3856 | 0.09613 | 118.8126 | 115.9378 | 123.5321 | 99.6826 | -0.41199 | 118.8126 | 115.9378 | 99.6826 | 0.09613 | 123.5321 | -7.7591 | -123.7381
1704.9844 | 123.3948 | -118.689 | 4.7287 | 0.19541 | 0.04797 | -0.015757 | 0.092069 | -0.057894 | 0.05183 | 0.088813 | -2.7237 | 0.27924 | -3.0579 | 4.7836 | -118.4372 | -19.0384 | 4.4861 | 4.8981 | 4.8477 | -119.0002 | 115.6311 | -4.4495 | 115.9653 | 123.4726 | -123.1659 | -0.31128 | 0.11902 | 0.33417 | 123.175 | 123.587 | 0.25177 | 118.9682 | 115.9653 | 123.5367 | 99.6506 | -0.31128 | 118.9682 | 115.9653 | 99.6506 | 0.25177 | 123.5367 | -7.7866 | -123.7289
1705.9219 | 123.4863 | -118.1076 | 5.2505 | 0.43956 | 0.02554 | -0.034983 | 0.062162 | -0.066439 | 0.040081 | 0.10804 | -2.6779 | 0.21973 | -3.0487 | 5.1636 | -118.0252 | -18.8599 | 5.2002 | 5.3375 | 5.4245 | -118.4601 | 115.0589 | -5.0308 | 115.4297 | 123.2712 | -123.2758 | -0.35248 | 0.17395 | 0.37079 | 123.3078 | 123.4451 | 0.082397 | 118.3273 | 115.4297 | 123.5321 | 99.2477 | -0.35248 | 118.3273 | 115.4297 | 99.2477 | 0.082397 | 123.5321 | -8.2993 | -123.7106
1706.9219 | 123.4177 | -118.8538 | 4.5136 | 0.39378 | 0.052243 | 0.0056046 | 0.096342 | -0.049349 | 0.052898 | 0.10056 | -2.9892 | 0.27466 | -3.1586 | 4.5868 | -118.4647 | -19.1116 | 4.335 | 4.6829 | 4.6646 | -119.22 | 115.6952 | -4.2389 | 115.8646 | 123.4406 | -122.9782 | -0.36621 | 0.15106 | 0.16937 | 123.1888 | 123.5367 | 0.3891 | 119.1284 | 115.8646 | 123.5184 | 99.7421 | -0.36621 | 119.1284 | 115.8646 | 99.7421 | 0.3891 | 123.5184 | -7.6721 | -123.7335
1708 | 123.4589 | -117.5446 | 5.8594 | -0.033467 | 0.04797 | -0.0061444 | 0.087797 | -0.047213 | 0.05183 | 0.10163 | -2.4582 | 0.27466 | -2.98 | 5.8228 | -117.2882 | -18.5211 | 5.6763 | 6.015 | 5.9601 | -117.8879 | 114.5645 | -5.5847 | 115.0864 | 123.3673 | -123.1476 | -0.34332 | 0.10071 | 0.52185 | 123.2208 | 123.5596 | 0.25635 | 117.8192 | 115.0864 | 123.5046 | 99.0234 | -0.34332 | 117.8192 | 115.0864 | 99.0234 | 0.25635 | 123.5046 | -8.8394 | -123.7473
1708.9219 | 123.4726 | -118.4692 | 4.8798 | 0.348 | 0.027676 | -0.018961 | 0.062162 | -0.041873 | 0.035809 | 0.10911 | -2.7969 | 0.23346 | -3.0991 | 4.7607 | -118.4738 | -19.2352 | 4.747 | 4.953 | 5.0354 | -118.8858 | 115.3702 | -4.6463 | 115.6723 | 123.23 | -123.3536 | -0.41656 | 0.15564 | 0.30212 | 123.2162 | 123.4222 | -0.004578 | 118.7027 | 115.6723 | 123.5046 | 99.234 | -0.41656 | 118.7027 | 115.6723 | 99.234 | -0.004578 | 123.5046 | -7.9788 | -123.7656
1709.9844 | 123.3902 | -118.6523 | 4.7699 | 0.4243 | 0.045834 | -0.0072124 | 0.089933 | -0.05469 | 0.04649 | 0.086677 | -2.8519 | 0.27924 | -3.1769 | 4.834 | -118.4647 | -19.1437 | 4.5273 | 4.9347 | 4.8706 | -119.014 | 115.4755 | -4.4907 | 115.8005 | 123.4863 | -123.2346 | -0.36163 | 0.10071 | 0.32501 | 123.1796 | 123.587 | 0.18768 | 118.9316 | 115.8005 | 123.5229 | 99.5087 | -0.36163 | 118.9316 | 115.8005 | 99.5087 | 0.18768 | 123.5229 | -7.9468 | -123.7839
1710.9219 | 123.4909 | -118.3502 | 5.0308 | 0.348 | 0.033017 | -0.018961 | 0.066434 | -0.057894 | 0.028332 | 0.1059 | -2.6642 | 0.22888 | -2.9709 | 4.8157 | -118.396 | -18.9468 | 4.9301 | 5.127 | 5.1224 | -118.7073 | 115.3793 | -4.8019 | 115.686 | 123.1659 | -123.4268 | -0.35706 | 0.091552 | 0.3067 | 123.2803 | 123.4772 | -0.045776 | 118.5791 | 115.686 | 123.4726 | 99.4034 | -0.35706 | 118.5791 | 115.686 | 99.4034 | -0.045776 | 123.4726 | -8.0017 | -123.7381
1711.9844 | 123.3856 | -118.19 | 5.2643 | 0.36326 | 0.044766 | -0.011485 | 0.096342 | -0.053622 | 0.053967 | 0.10377 | -2.7191 | 0.27466 | -3.0624 | 5.4382 | -117.9794 | -18.9056 | 4.9988 | 5.3787 | 5.4199 | -118.4875 | 115.1276 | -4.9896 | 115.4709 | 123.6282 | -123.2437 | -0.29755 | 0.15564 | 0.34332 | 123.1888 | 123.5687 | 0.21057 | 118.4647 | 115.4709 | 123.6099 | 99.2844 | -0.29755 | 118.4647 | 115.4709 | 99.2844 | 0.21057 | 123.6099 | -8.3267 | -123.7518
1712.9219 | 123.4314 | -118.3411 | 5.0583 | 0.39378 | 0.044766 | -0.031779 | 0.094205 | -0.048281 | 0.066784 | 0.10697 | -2.5955 | 0.2655 | -2.9205 | 5.072 | -118.2953 | -19.0155 | 4.8248 | 5.2002 | 5.1544 | -118.7256 | 115.4205 | -4.7928 | 115.7455 | 123.4131 | -123.3536 | -0.38452 | 0.09613 | 0.32501 | 123.1659 | 123.5413 | 0.045776 | 118.6066 | 115.7455 | 123.4955 | 99.3256 | -0.38452 | 118.6066 | 115.7455 | 99.3256 | 0.045776 | 123.4955 | -7.9788 | -123.7839
1713.9844 | 123.3902 | -118.7897 | 4.6692 | 0.13438 | 0.055447 | -0.020029 | 0.084592 | -0.036532 | 0.055035 | 0.10056 | -2.5772 | 0.28381 | -2.9205 | 4.7012 | -118.6295 | -19.0796 | 4.4174 | 4.8431 | 4.7791 | -119.1101 | 115.8691 | -4.3854 | 116.2125 | 123.4909 | -123.2986 | -0.32043 | 0.10986 | 0.34332 | 123.2071 | 123.6328 | 0.16022 | 119.0735 | 116.2125 | 123.5687 | 99.7101 | -0.32043 | 119.0735 | 116.2125 | 99.7101 | 0.16022 | 123.5687 | -7.5897 | -123.7793
1714.9219 | 123.468 | -118.6157 | 4.7241 | 0.45481 | 0.046902 | -0.028574 | 0.078184 | -0.046145 | 0.053967 | 0.10484 | -2.7145 | 0.25635 | -3.0762 | 4.7195 | -118.5608 | -19.1803 | 4.5593 | 4.8706 | 4.9301 | -118.9957 | 115.5396 | -4.4678 | 115.9012 | 123.3353 | -123.2849 | -0.37994 | 0.20599 | 0.36163 | 123.175 | 123.4863 | 0.054932 | 118.8721 | 115.9012 | 123.5458 | 99.4354 | -0.37994 | 118.8721 | 115.9012 | 99.4354 | 0.054932 | 123.5458 | -7.8003 | -123.7198
1715.9844 | 123.5321 | -118.5333 | 4.7882 | 0.53111 | 0.034085 | -0.021098 | 0.064298 | -0.051486 | 0.055035 | 0.11018 | -2.6825 | 0.23804 | -3.0396 | 4.6692 | -118.5562 | -19.0018 | 4.7379 | 4.866 | 4.9713 | -118.9453 | 115.4938 | -4.5502 | 115.8508 | 123.2025 | -123.3444 | -0.41199 | 0.18311 | 0.35706 | 123.2712 | 123.3994 | -0.022888 | 118.7714 | 115.8508 | 123.5046 | 99.5316 | -0.41199 | 118.7714 | 115.8508 | 99.5316 | -0.022888 | 123.5046 | -7.8278 | -123.7335
1716.9219 | 123.4268 | -118.6935 | 4.6738 | -0.0029495 | 0.045834 | 0.020559 | 0.083524 | -0.049349 | 0.062512 | 0.10163 | -2.6596 | 0.2655 | -3.0533 | 4.7333 | -118.6295 | -19.075 | 4.4861 | 4.866 | 4.8157 | -119.0552 | 115.6403 | -4.4083 | 116.0339 | 123.4268 | -123.3032 | -0.36163 | 0.14191 | 0.39368 | 123.1796 | 123.5596 | 0.064086 | 118.959 | 116.0339 | 123.5092 | 99.6185 | -0.36163 | 118.959 | 116.0339 | 99.6185 | 0.064086 | 123.5092 | -7.7271 | -123.7289
1717.9844 | 123.4177 | -118.6432 | 4.7699 | 0.073345 | 0.04263 | -0.0093484 | 0.077116 | -0.042941 | 0.052898 | 0.1059 | -2.7237 | 0.26093 | -3.0487 | 4.8157 | -118.5287 | -18.9514 | 4.5136 | 4.9484 | 4.8752 | -118.9728 | 115.5945 | -4.509 | 115.9195 | 123.4589 | -123.2986 | -0.32959 | 0.10529 | 0.32501 | 123.1567 | 123.5916 | 0.11444 | 118.9041 | 115.9195 | 123.5184 | 99.6918 | -0.32959 | 118.9041 | 115.9195 | 99.6918 | 0.11444 | 123.5184 | -7.8186 | -123.7427
1718.9219 | 123.3994 | -118.7668 | 4.6463 | 0.33274 | 0.035153 | -0.037119 | 0.085661 | -0.051486 | 0.057171 | 0.098426 | -2.6733 | 0.27008 | -3.0212 | 4.715 | -118.6295 | -18.9972 | 4.4083 | 4.866 | 4.7882 | -119.0781 | 115.7455 | -4.3762 | 116.0934 | 123.4818 | -123.2758 | -0.31128 | 0.14191 | 0.3479 | 123.175 | 123.6328 | 0.13733 | 119.0369 | 116.0934 | 123.555 | 99.7696 | -0.31128 | 119.0369 | 116.0934 | 99.7696 | 0.13733 | 123.555 | -7.6675 | -123.7244
1719.9844 | 123.4314 | -118.6478 | 4.7745 | -0.14028 | 0.039425 | -0.027506 | 0.072843 | -0.047213 | 0.049694 | 0.098426 | -1.9913 | 0.28839 | -2.3849 | 4.715 | -118.6111 | -19.4138 | 4.5502 | 4.8523 | 4.8889 | -119.046 | 116.2628 | -4.4861 | 116.6565 | 123.3627 | -123.3856 | -0.39825 | 0.11444 | 0.39368 | 123.1979 | 123.5001 | 0.036621 | 118.9362 | 116.6565 | 123.5367 | 99.234 | -0.39825 | 118.9362 | 116.6565 | 99.234 | 0.036621 | 123.5367 | -7.1594 | -123.8205
1720.9219 | 123.3948 | -118.6615 | 4.747 | 0.43956 | 0.043698 | -0.0018714 | 0.086729 | -0.036532 | 0.050762 | 0.10377 | -2.6459 | 0.2655 | -2.9938 | 4.7745 | -118.5425 | -19.1299 | 4.4769 | 4.9164 | 4.8386 | -119.0277 | 115.6677 | -4.4815 | 116.0156 | 123.436 | -123.2895 | -0.36621 | 0.091553 | 0.3479 | 123.1384 | 123.5779 | 0.11902 | 118.927 | 116.0156 | 123.5001 | 99.5316 | -0.36621 | 118.927 | 116.0156 | 99.5316 | 0.11902 | 123.5001 | -7.7408 | -123.7747
1721.9844 | 123.4497 | -118.4692 | 4.9118 | -0.1708 | 0.051175 | -0.016825 | 0.08032 | -0.046145 | 0.058239 | 0.10484 | -2.623 | 0.26093 | -2.9984 | 4.8752 | -118.396 | -19.1299 | 4.7241 | 5.0766 | 5.0583 | -118.84 | 115.4709 | -4.6509 | 115.8463 | 123.3444 | -123.3078 | -0.37079 | 0.14649 | 0.37537 | 123.1934 | 123.5458 | 0.073242 | 118.7302 | 115.8463 | 123.5275 | 99.3393 | -0.37079 | 118.7302 | 115.8463 | 99.3393 | 0.073242 | 123.5275 | -7.9102 | -123.7518
1722.9219 | 123.4268 | -118.634 | 4.7745 | 0.088604 | 0.041562 | -0.027506 | 0.081388 | -0.0376 | 0.052898 | 0.099494 | -2.7237 | 0.27008 | -3.0945 | 4.7928 | -118.5196 | -19.4504 | 4.541 | 4.9301 | 4.9026 | -118.9957 | 115.5396 | -4.5044 | 115.9103 | 123.4268 | -123.2941 | -0.36163 | 0.12817 | 0.37079 | 123.175 | 123.5641 | 0.11444 | 118.9041 | 115.9103 | 123.5367 | 99.1837 | -0.36163 | 118.9041 | 115.9103 | 99.1837 | 0.11444 | 123.5367 | -7.869 | -123.7701
1723.9844 | 123.5229 | -118.396 | 4.953 | -0.79641 | 0.02554 | -0.038187 | 0.066434 | -0.052554 | 0.040081 | 0.11338 | -2.6184 | 0.2243 | -2.9755 | 4.7791 | -118.4738 | -19.5877 | 4.834 | 5.0262 | 5.1361 | -118.8171 | 115.4205 | -4.7287 | 115.7776 | 123.175 | -123.4268 | -0.42114 | 0.18311 | 0.35706 | 123.23 | 123.4222 | -0.07782 | 118.6203 | 115.7776 | 123.5321 | 98.8083 | -0.42114 | 118.6203 | 115.7776 | 98.8083 | -0.07782 | 123.5321 | -7.9285 | -123.7701
1724.9219 | 123.4451 | -118.5837 | 4.8111 | 0.92784 | 0.043698 | -0.015757 | 0.077116 | -0.039736 | 0.044354 | 0.10377 | -2.6321 | 0.29297 | -2.9755 | 4.8386 | -118.5104 | -19.7662 | 4.6646 | 4.9759 | 4.9942 | -118.9316 | 115.6082 | -4.5181 | 115.9515 | 123.4222 | -123.3215 | -0.3479 | 0.18311 | 0.34332 | 123.2483 | 123.5596 | 0.073242 | 118.8766 | 115.9515 | 123.5779 | 98.8174 | -0.3479 | 118.8766 | 115.9515 | 98.8174 | 0.073242 | 123.5779 | -7.7866 | -123.7427
1726 | 123.5092 | -118.6249 | 4.7195 | 0.18016 | 0.02554 | 0.0056046 | 0.05789 | -0.053622 | 0.041149 | 0.10804 | -2.8152 | 0.21515 | -3.1631 | 4.5914 | -118.6981 | -20.0317 | 4.6509 | 4.7836 | 4.9072 | -119.0369 | 115.4617 | -4.5044 | 115.8096 | 123.2162 | -123.4177 | -0.41199 | 0.18768 | 0.3479 | 123.2758 | 123.4085 | -0.073242 | 118.84 | 115.8096 | 123.5321 | 98.5931 | -0.41199 | 118.84 | 115.8096 | 98.5931 | -0.073242 | 123.5321 | -7.8827 | -123.7564
1726.9219 | 123.4497 | -118.8171 | 4.6051 | -0.33864 | 0.036221 | -0.027506 | 0.073911 | -0.051486 | 0.055035 | 0.093085 | -2.742 | 0.26093 | -3.1128 | 4.5822 | -118.7668 | -19.9768 | 4.4037 | 4.7379 | 4.7379 | -119.1834 | 115.7043 | -4.3442 | 116.0751 | 123.3994 | -123.3719 | -0.36621 | 0.13275 | 0.37079 | 123.2208 | 123.555 | 0.050354 | 119.0781 | 116.0751 | 123.555 | 98.8403 | -0.36621 | 119.0781 | 116.0751 | 98.8403 | 0.050354 | 123.555 | -7.7179 | -123.7885
1727.9219 | 123.4268 | -118.7576 | 4.6555 | -0.3539 | 0.04263 | -0.012553 | 0.077116 | -0.048281 | 0.047558 | 0.1027 | -2.7512 | 0.27008 | -3.0945 | 4.6417 | -118.721 | -20.0867 | 4.4083 | 4.8157 | 4.7882 | -119.1055 | 115.6631 | -4.3854 | 116.0065 | 123.3994 | -123.3765 | -0.3479 | 0.13275 | 0.34332 | 123.1659 | 123.5733 | 0.036621 | 119.0277 | 116.0065 | 123.5458 | 98.671 | -0.3479 | 119.0277 | 116.0065 | 98.671 | 0.036621 | 123.5458 | -7.7499 | -123.761
1728.9844 | 123.5413 | -118.6798 | 4.6509 | -0.15554 | 0.03088 | -0.021098 | 0.049345 | -0.063235 | 0.0294 | 0.1027 | -2.7695 | 0.22888 | -3.1219 | 4.5181 | -118.7851 | -20.1782 | 4.6143 | 4.715 | 4.8843 | -119.0918 | 115.5579 | -4.422 | 115.9103 | 123.1979 | -123.436 | -0.41199 | 0.23346 | 0.35248 | 123.2941 | 123.3948 | -0.10528 | 118.9087 | 115.9103 | 123.5641 | 98.5016 | -0.41199 | 118.9087 | 115.9103 | 98.5016 | -0.10528 | 123.5641 | -7.7728 | -123.7427
1729.9219 | 123.4451 | -118.6386 | 4.7607 | -0.72011 | 0.037289 | -0.020029 | 0.084592 | -0.055758 | 0.041149 | 0.10056 | -2.7603 | 0.31586 | -3.0533 | 4.7607 | -118.5883 | -19.7571 | 4.5776 | 4.9118 | 4.921 | -119.014 | 115.5853 | -4.4449 | 115.8783 | 123.3994 | -123.349 | -0.37537 | 0.16022 | 0.29297 | 123.2162 | 123.5504 | 0.050354 | 118.9545 | 115.8783 | 123.5596 | 98.8815 | -0.37537 | 118.9545 | 115.8783 | 98.8815 | 0.050354 | 123.5596 | -7.814 | -123.7747
1730.9844 | 123.4314 | -118.6249 | 4.7653 | 1.3551 | 0.052243 | -0.033915 | 0.086729 | -0.049349 | 0.055035 | 0.099494 | -2.6138 | 0.32501 | -2.9663 | 4.7653 | -118.4875 | -19.6289 | 4.541 | 4.8981 | 4.9072 | -119.046 | 115.6586 | -4.4403 | 116.011 | 123.3902 | -123.2529 | -0.42114 | 0.14191 | 0.35248 | 123.1659 | 123.5229 | 0.13733 | 118.9499 | 116.011 | 123.5321 | 98.996 | -0.42114 | 118.9499 | 116.011 | 98.996 | 0.13733 | 123.5321 | -7.7316 | -123.8113
1731.9219 | 123.4543 | -118.5013 | 4.8935 | -0.41494 | 0.023404 | -0.039256 | 0.067503 | -0.053622 | 0.021923 | 0.10911 | -2.7008 | 0.24261 | -3.0624 | 4.8065 | -118.4875 | -19.6518 | 4.7241 | 4.9759 | 5.0949 | -118.8812 | 115.4388 | -4.6509 | 115.8005 | 123.3078 | -123.381 | -0.37994 | 0.20142 | 0.36163 | 123.2254 | 123.4772 | 0.013733 | 118.7439 | 115.8005 | 123.5962 | 98.8495 | -0.37994 | 118.7439 | 115.8005 | 98.8495 | 0.013733 | 123.5962 | -7.9559 | -123.7747
1732.9688 | 123.5184 | -118.3594 | 4.985 | 0.18016 | 0.019131 | -0.049937 | 0.051481 | -0.056826 | 0.035809 | 0.10697 | -2.6093 | 0.18768 | -2.9434 | 4.7791 | -118.4418 | -19.3405 | 4.8706 | 5.0217 | 5.1361 | -118.7988 | 115.416 | -4.7974 | 115.7501 | 123.1384 | -123.4268 | -0.43945 | 0.15106 | 0.33417 | 123.23 | 123.381 | -0.082397 | 118.5471 | 115.7501 | 123.4955 | 99.0189 | -0.43945 | 118.5471 | 115.7501 | 99.0189 | -0.082397 | 123.4955 | -7.9285 | -123.7839
1733.9219 | 123.4222 | -118.5928 | 4.7882 | 0.042827 | 0.043698 | -0.0072124 | 0.10168 | -0.053622 | 0.065716 | 0.095222 | -2.5818 | 0.25635 | -2.9709 | 4.866 | -118.5379 | -19.3497 | 4.6097 | 4.9713 | 4.9942 | -118.9819 | 115.6219 | -4.5319 | 116.011 | 123.4589 | -123.3261 | -0.3891 | 0.20599 | 0.3891 | 123.2025 | 123.5641 | 0.054931 | 118.8492 | 116.011 | 123.587 | 99.2432 | -0.3891 | 118.8492 | 116.011 | 99.2432 | 0.054931 | 123.587 | -7.7591 | -123.7701
1734.9844 | 123.5046 | -118.2129 | 5.1819 | 0.19541 | 0.0095178 | -0.038187 | 0.054685 | -0.061099 | 0.0294 | 0.10697 | -2.5955 | 0.24719 | -2.8931 | 4.9576 | -118.3594 | -19.043 | 5.1819 | 5.246 | 5.2963 | -118.5883 | 115.3198 | -4.9347 | 115.6174 | 123.1705 | -123.5413 | -0.37537 | 0.11444 | 0.29755 | 123.3948 | 123.4589 | -0.14648 | 118.4601 | 115.6174 | 123.5092 | 99.1699 | -0.37537 | 118.4601 | 115.6174 | 99.1699 | -0.14648 | 123.5092 | -8.075 | -123.7701
1735.9219 | 123.4726 | -118.6569 | 4.7607 | -0.26235 | 0.031949 | -0.036051 | 0.074979 | -0.05469 | 0.045422 | 0.10056 | -2.7145 | 0.23804 | -3.1174 | 4.7607 | -118.6478 | -19.5923 | 4.5593 | 4.8889 | 4.8935 | -118.9957 | 115.5395 | -4.5227 | 115.9424 | 123.4177 | -123.4085 | -0.33875 | 0.13275 | 0.40283 | 123.2162 | 123.5458 | 0.009155 | 118.895 | 115.9424 | 123.5504 | 99.0646 | -0.33875 | 118.895 | 115.9424 | 99.0646 | 0.009155 | 123.5504 | -7.8781 | -123.7564
1736.9844 | 123.4543 | -118.6066 | 4.834 | -0.4302 | 0.041562 | -0.036051 | 0.078184 | -0.05469 | 0.052898 | 0.10056 | -2.7512 | 0.27466 | -3.0945 | 4.8248 | -118.5562 | -19.4046 | 4.5731 | 4.9667 | 4.9255 | -118.9499 | 115.5121 | -4.5593 | 115.8554 | 123.4314 | -123.3902 | -0.34332 | 0.091553 | 0.34332 | 123.1796 | 123.5733 | 0.050354 | 118.8812 | 115.8554 | 123.5321 | 99.202 | -0.34332 | 118.8812 | 115.8554 | 99.202 | 0.050354 | 123.5321 | -7.9285 | -123.7839
1737.9219 | 123.4909 | -118.7164 | 4.6783 | -0.27761 | 0.02554 | -0.043528 | 0.06323 | -0.057894 | 0.037945 | 0.10056 | -2.6459 | 0.22888 | -2.9984 | 4.5502 | -118.7668 | -19.6564 | 4.5364 | 4.747 | 4.8294 | -119.0964 | 115.7181 | -4.4495 | 116.0706 | 123.2666 | -123.4451 | -0.37994 | 0.15106 | 0.35248 | 123.2529 | 123.4634 | -0.050354 | 118.9453 | 116.0706 | 123.5458 | 99.0601 | -0.37994 | 118.9453 | 116.0706 | 99.0601 | -0.050354 | 123.5458 | -7.6767 | -123.7747
1738.9844 | 123.4497 | -118.6295 | 4.7836 | -0.49123 | 0.049038 | -0.014689 | 0.087797 | -0.048281 | 0.045422 | 0.10377 | -2.449 | 0.26093 | -2.8107 | 4.7745 | -118.5379 | -19.0155 | 4.5822 | 4.8981 | 4.9118 | -118.9774 | 115.8188 | -4.5227 | 116.1804 | 123.4039 | -123.3215 | -0.3479 | 0.12817 | 0.36163 | 123.2117 | 123.5275 | 0.091553 | 118.8904 | 116.1804 | 123.5413 | 99.614 | -0.3479 | 118.8904 | 116.1804 | 99.614 | 0.091553 | 123.5413 | -7.5943 | -123.761
1739.9219 | 123.5184 | -118.6798 | 4.6967 | 0.01231 | 0.014859 | -0.043528 | 0.052549 | -0.05469 | 0.020855 | 0.10804 | -2.4765 | 0.23804 | -2.8244 | 4.541 | -118.7302 | -18.988 | 4.5822 | 4.7424 | 4.8798 | -119.0872 | 115.8554 | -4.4586 | 116.2033 | 123.2208 | -123.4268 | -0.40741 | 0.18311 | 0.3479 | 123.262 | 123.4222 | -0.050354 | 118.9178 | 116.2033 | 123.5596 | 99.6918 | -0.40741 | 118.9178 | 116.2033 | 99.6918 | -0.050354 | 123.5596 | -7.5211 | -123.7839
1740.9844 | 123.4909 | -118.5242 | 4.8111 | -0.3539 | 0.026608 | -0.045664 | 0.058958 | -0.066439 | 0.025128 | 0.10911 | -2.4353 | 0.21057 | -2.8152 | 4.4724 | -118.602 | -18.7134 | 4.7333 | 4.747 | 4.9713 | -118.9636 | 115.7089 | -4.6005 | 116.0889 | 122.9965 | -123.4131 | -0.43945 | 0.16022 | 0.37994 | 123.2574 | 123.2712 | -0.07782 | 118.7347 | 116.0889 | 123.4955 | 99.8108 | -0.43945 | 118.7347 | 116.0889 | 99.8108 | -0.07782 | 123.4955 | -7.6263 | -123.7747
1741.9219 | 123.5092 | -118.2312 | 5.0766 | -3.6956 | 0.022336 | -0.017893 | 0.069639 | -0.053622 | 0.026196 | 0.098426 | -2.5452 | 0.21973 | -2.948 | 4.9759 | -118.3823 | -19.0338 | 4.9942 | 5.1453 | 5.2597 | -118.6615 | 115.2832 | -4.8569 | 115.686 | 123.2071 | -123.4589 | -0.4303 | 0.18311 | 0.40283 | 123.2254 | 123.3765 | -0.15106 | 118.4509 | 115.686 | 123.4909 | 99.1974 | -0.4303 | 118.4509 | 115.686 | 99.1974 | -0.15106 | 123.4909 | -8.0246 | -123.7381
1742.9844 | 123.4726 | -117.8925 | 5.4932 | -0.4302 | 0.021267 | -0.021098 | 0.076048 | -0.066439 | 0.027264 | 0.11124 | -2.6093 | 0.25635 | -2.9572 | 5.4291 | -117.9245 | -18.7408 | 5.365 | 5.5664 | 5.658 | -118.2816 | 114.9353 | -5.2368 | 115.2832 | 123.3215 | -123.4177 | -0.3891 | 0.16479 | 0.3479 | 123.2574 | 123.4589 | -0.032044 | 118.1488 | 115.2832 | 123.5504 | 99.1516 | -0.3891 | 118.1488 | 115.2832 | 99.1516 | -0.032044 | 123.5504 | -8.4503 | -123.7747
1743.9219 | 123.4726 | -118.1076 | 5.2551 | 0.43956 | 0.036221 | -0.0029404 | 0.082456 | -0.062167 | 0.047558 | 0.09629 | -2.6825 | 0.24719 | -3.067 | 5.3421 | -118.1442 | -19.1162 | 4.9942 | 5.2505 | 5.3558 | -118.5471 | 115.0406 | -5.0079 | 115.4251 | 123.4497 | -123.3994 | -0.43945 | 0.10071 | 0.38452 | 123.1018 | 123.3582 | -0.036621 | 118.3548 | 115.4251 | 123.4634 | 98.9914 | -0.43945 | 118.3548 | 115.4251 | 98.9914 | -0.036621 | 123.4634 | -8.3221 | -123.8022
1744.9844 | 123.468 | -118.7851 | 4.6097 | 0.4243 | 0.02554 | -0.052073 | 0.065366 | -0.049349 | 0.024059 | 0.10163 | -2.6871 | 0.22888 | -3.0258 | 4.4998 | -118.808 | -19.2947 | 4.509 | 4.6555 | 4.7836 | -119.1696 | 115.7593 | -4.3808 | 116.098 | 123.2849 | -123.4177 | -0.38452 | 0.17395 | 0.33875 | 123.2941 | 123.4406 | -0.022888 | 119.014 | 116.098 | 123.5687 | 99.4904 | -0.38452 | 119.014 | 116.098 | 99.4904 | -0.022888 | 123.5687 | -7.6355 | -123.7793
1745.9219 | 123.5046 | -118.7073 | 4.6234 | -0.3539 | 0.029812 | -0.027506 | 0.068571 | -0.066439 | 0.028332 | 0.10163 | -2.4857 | 0.21973 | -2.8427 | 4.5502 | -118.8171 | -18.8965 | 4.509 | 4.715 | 4.866 | -119.0964 | 115.8646 | -4.4037 | 116.2216 | 123.2574 | -123.4406 | -0.3891 | 0.24261 | 0.35706 | 123.2162 | 123.4222 | -0.10986 | 118.927 | 116.2216 | 123.5733 | 99.8108 | -0.3891 | 118.927 | 116.2216 | 99.8108 | -0.10986 | 123.5733 | -7.4661 | -123.7198
1746.9844 | 123.5458 | -118.7347 | 4.6326 | -0.048725 | 0.019131 | -0.044596 | 0.051481 | -0.055758 | 0.025128 | 0.10056 | -2.4353 | 0.25177 | -2.7786 | 4.4678 | -118.8492 | -18.7271 | 4.5227 | 4.6509 | 4.7928 | -119.1605 | 115.9561 | -4.3808 | 116.2994 | 123.2025 | -123.4818 | -0.42572 | 0.16022 | 0.34332 | 123.2574 | 123.3856 | -0.11444 | 118.9865 | 116.2994 | 123.5275 | 100.0076 | -0.42572 | 118.9865 | 116.2994 | 100.0076 | -0.11444 | 123.5275 | -7.4112 | -123.793
1747.9219 | 123.5229 | -117.9886 | 5.3879 | -0.048725 | 0.021267 | -0.031779 | 0.065366 | -0.069644 | 0.043285 | 0.10697 | -2.3529 | 0.2243 | -2.655 | 5.4291 | -118.0939 | -18.0496 | 5.4657 | 5.4428 | 5.6992 | -118.3273 | 115.3336 | -5.1636 | 115.6357 | 123.4177 | -123.4818 | -0.33875 | 0.31128 | 0.30212 | 123.4543 | 123.4314 | -0.10529 | 118.2129 | 115.6357 | 123.6877 | 99.939 | -0.33875 | 118.2129 | 115.6357 | 99.939 | -0.10529 | 123.6877 | -8.0429 | -123.7152
1749 | 123.4268 | -118.5471 | 4.8523 | 1.645 | 0.049038 | -0.048869 | 0.081388 | -0.063235 | 0.048626 | 0.097358 | -2.6093 | 0.27008 | -2.9709 | 4.8935 | -118.515 | -18.8049 | 4.6005 | 4.9942 | 4.953 | -118.9316 | 115.5762 | -4.5822 | 115.9378 | 123.4406 | -123.3673 | -0.38452 | 0.10071 | 0.36163 | 123.1476 | 123.5413 | 0.032043 | 118.8171 | 115.9378 | 123.5001 | 99.7421 | -0.38452 | 118.8171 | 115.9378 | 99.7421 | 0.032043 | 123.5001 | -7.8232 | -123.7839
1749.9219 | 123.5138 | -118.4647 | 4.9026 | 0.088604 | 0.021267 | -0.010416 | 0.061094 | -0.060031 | 0.026196 | 0.1027 | -2.6093 | 0.21515 | -2.9205 | 4.7562 | -118.5287 | -18.75 | 4.7836 | 4.9347 | 5.0583 | -118.8812 | 115.5441 | -4.6875 | 115.8554 | 123.2208 | -123.4314 | -0.41656 | 0.15564 | 0.31128 | 123.2483 | 123.3994 | -0.064087 | 118.6798 | 115.8554 | 123.523 | 99.7147 | -0.41656 | 118.6798 | 115.8554 | 99.7147 | -0.064087 | 123.523 | -7.8232 | -123.7839
1750.9844 | 123.5504 | -118.6615 | 4.6738 | -0.12502 | 0.022336 | -0.037119 | 0.072843 | -0.067507 | 0.034741 | 0.1059 | -2.449 | 0.2243 | -2.7969 | 4.5044 | -118.7988 | -18.837 | 4.6005 | 4.6921 | 4.8431 | -119.0872 | 115.8646 | -4.4495 | 116.2125 | 123.1659 | -123.4726 | -0.42572 | 0.16937 | 0.3479 | 123.262 | 123.3536 | -0.13733 | 118.8858 | 116.2125 | 123.5046 | 99.8245 | -0.42572 | 118.8858 | 116.2125 | 99.8245 | -0.13733 | 123.5046 | -7.4707 | -123.761
1751.9219 | 123.5458 | -118.2587 | 5.072 | -0.27761 | 0.014859 | -0.045664 | 0.06323 | -0.076052 | 0.017651 | 0.10484 | -2.3621 | 0.21973 | -2.7466 | 4.9164 | -118.4235 | -18.5806 | 5.0125 | 5.0995 | 5.2597 | -118.6798 | 115.5121 | -4.8523 | 115.8966 | 123.175 | -123.4955 | -0.42114 | 0.18768 | 0.38452 | 123.2712 | 123.3582 | -0.16479 | 118.4784 | 115.8966 | 123.5184 | 99.678 | -0.42114 | 118.4784 | 115.8966 | 99.678 | -0.16479 | 123.5184 | -7.8186 | -123.7518
1752.9844 | 123.4818 | -118.5425 | 4.8065 | 0.85154 | 0.038357 | -0.041392 | 0.086729 | -0.060031 | 0.043285 | 0.10163 | -2.3849 | 0.19226 | -2.7969 | 4.7287 | -118.5425 | -18.4982 | 4.7195 | 4.8523 | 4.9622 | -118.9682 | 115.7455 | -4.6143 | 116.1575 | 123.2712 | -123.349 | -0.42572 | 0.15564 | 0.41199 | 123.262 | 123.3948 | 0 | 118.7347 | 116.1575 | 123.5046 | 100.0443 | -0.42572 | 118.7347 | 116.1575 | 100.0443 | 0 | 123.5046 | -7.6035 | -123.7747
1753.9219 | 123.4955 | -118.6615 | 4.6829 | 0.11912 | 0.029812 | -0.02537 | 0.078184 | -0.064303 | 0.030468 | 0.10056 | -2.6413 | 0.25177 | -2.9022 | 4.6143 | -118.6066 | -18.7454 | 4.5502 | 4.7699 | 4.8569 | -119.0598 | 115.7593 | -4.4312 | 116.0202 | 123.2758 | -123.2895 | -0.39825 | 0.17395 | 0.26093 | 123.2117 | 123.4314 | 0.054932 | 118.9133 | 116.0202 | 123.5184 | 99.9161 | -0.39825 | 118.9133 | 116.0202 | 99.9161 | 0.054932 | 123.5184 | -7.5851 | -123.7427
1754.9844 | 123.4543 | -118.0115 | 5.3192 | 0.4243 | 0.03088 | -0.039256 | 0.088865 | -0.065371 | 0.035809 | 0.09629 | -2.5314 | 0.21057 | -2.9343 | 5.3879 | -117.9199 | -18.3609 | 5.2689 | 5.3787 | 5.5893 | -118.4189 | 115.0772 | -5.1086 | 115.48 | 123.3994 | -123.2391 | -0.40741 | 0.27008 | 0.40283 | 123.2803 | 123.3902 | 0.091553 | 118.222 | 115.48 | 123.6008 | 99.6506 | -0.40741 | 118.222 | 115.48 | 99.6506 | 0.091553 | 123.6008 | -8.2535 | -123.7381
1755.9219 | 123.5184 | -118.1168 | 5.246 | -0.24709 | 0.023404 | -0.041392 | 0.064298 | -0.058962 | 0.036877 | 0.10484 | -2.3483 | 0.22888 | -2.7649 | 5.1132 | -118.1625 | -18.3426 | 5.1498 | 5.2597 | 5.4153 | -118.5471 | 115.3519 | -5.0171 | 115.7684 | 123.23 | -123.4085 | -0.4303 | 0.16937 | 0.41656 | 123.2666 | 123.3765 | -0.045777 | 118.3456 | 115.7684 | 123.5321 | 99.7742 | -0.4303 | 118.3456 | 115.7684 | 99.7742 | -0.045777 | 123.5321 | -8.0109 | -123.793
1756.9219 | 123.4818 | -118.1259 | 5.2368 | 0.30223 | 0.027676 | -0.036051 | 0.082456 | -0.057894 | 0.034741 | 0.093085 | -2.4673 | 0.23804 | -2.7786 | 5.1727 | -118.0527 | -18.3517 | 5.1178 | 5.3238 | 5.4199 | -118.483 | 115.3473 | -4.9988 | 115.6586 | 123.2986 | -123.2895 | -0.35706 | 0.18311 | 0.31128 | 123.2437 | 123.4497 | 0.073243 | 118.364 | 115.6586 | 123.5458 | 99.7742 | -0.35706 | 118.364 | 115.6586 | 99.7742 | 0.073243 | 123.5458 | -8.0154 | -123.7198
1757.9844 | 123.5001 | -117.5491 | 5.809 | 0.19541 | 0.039425 | -0.024302 | 0.082456 | -0.063235 | 0.04649 | 0.095222 | -2.5131 | 0.22888 | -2.8564 | 5.3146 | -118.0344 | -18.4799 | 5.7312 | 6.0425 | 5.8136 | -118.0069 | 114.6927 | -5.5801 | 115.036 | 122.8638 | -123.8434 | -0.45776 | 0.004578 | 0.34332 | 123.2803 | 123.5916 | -0.48523 | 117.778 | 115.036 | 123.3627 | 99.0692 | -0.45776 | 117.778 | 115.036 | 99.0692 | -0.48523 | 123.3627 | -8.6655 | -123.8159
1758.9219 | 123.5138 | -118.0069 | 5.3238 | 0.37852 | 0.020199 | -0.015757 | 0.072843 | -0.060031 | 0.034741 | 0.098426 | -2.6733 | 0.21973 | -3.035 | 5.2322 | -118.0618 | -18.5165 | 5.2368 | 5.4153 | 5.4474 | -118.4006 | 114.9719 | -5.1041 | 115.3336 | 123.2391 | -123.3856 | -0.39368 | 0.1236 | 0.36163 | 123.2437 | 123.4222 | -0.054932 | 118.2266 | 115.3336 | 123.4543 | 99.4904 | -0.39368 | 118.2266 | 115.3336 | 99.4904 | -0.054932 | 123.4543 | -8.3588 | -123.7244
1759.9844 | 123.6374 | -118.5928 | 4.715 | 0.48533 | 0.035153 | -0.038187 | 0.083524 | -0.060031 | 0.044354 | 0.099494 | -2.5177 | 0.21973 | -2.8885 | 4.7104 | -118.6249 | -18.4662 | 4.715 | 4.7424 | 4.9622 | -119.0186 | 115.7043 | -4.4952 | 116.0751 | 123.3032 | -123.3398 | -0.42572 | 0.24719 | 0.37079 | 123.3078 | 123.3353 | -0.032044 | 118.8126 | 116.0751 | 123.555 | 100.1266 | -0.42572 | 118.8126 | 116.0751 | 100.1266 | -0.032044 | 123.555 | -7.6035 | -123.7335
1761.25 | 123.5138 | -117.9016 | 5.4153 | -0.36916 | 0.020199 | -0.014689 | 0.087797 | -0.065371 | 0.033672 | 0.10377 | -2.5818 | 0.2243 | -2.8015 | 5.3879 | -118.0664 | -18.1046 | 5.3833 | 5.4611 | 5.5847 | -118.3319 | 115.1001 | -5.191 | 115.3198 | 123.2895 | -123.4818 | -0.4303 | 0.16937 | 0.21973 | 123.2849 | 123.3627 | -0.16479 | 118.1259 | 115.3198 | 123.4863 | 99.7971 | -0.4303 | 118.1259 | 115.3198 | 99.7971 | -0.16479 | 123.4863 | -8.2169 | -123.7473
1761.9219 | 123.4772 | -118.2129 | 5.0949 | 0.37852 | 0.029812 | -0.02537 | 0.076048 | -0.058962 | 0.037945 | 0.10056 | -2.5314 | 0.22888 | -2.8656 | 5.0171 | -118.2587 | -18.4479 | 5.0354 | 5.1727 | 5.2826 | -118.6432 | 115.3473 | -4.866 | 115.6815 | 123.23 | -123.3536 | -0.4303 | 0.18768 | 0.33417 | 123.2483 | 123.3856 | -0.045776 | 118.4418 | 115.6815 | 123.4955 | 99.765 | -0.4303 | 118.4418 | 115.6815 | 99.765 | -0.045776 | 123.4955 | -7.9605 | -123.7381
1762.9219 | 123.5138 | -118.3685 | 4.9393 | -1.1321 | 0.033017 | -0.0061444 | 0.073911 | -0.056826 | 0.033672 | 0.10484 | -2.4673 | 0.17395 | -2.8519 | 4.8523 | -118.4509 | -7.5256 | 4.9026 | 4.9942 | 5.1544 | -118.8034 | 115.5167 | -4.7653 | 115.9012 | 123.2208 | -123.3902 | -0.43488 | 0.21515 | 0.38452 | 123.2712 | 123.3627 | -0.082398 | 118.5425 | 115.9012 | 123.5229 | 110.8429 | -0.43488 | 118.5425 | 115.9012 | 110.8429 | -0.082398 | 123.5229 | -7.7911 | -123.7427
1763.9375 | 123.4222 | -118.2083 | 5.2048 | 0.39378 | 0.056515 | -0.00080337 | 0.074979 | -0.066439 | 0.045422 | 0.10377 | -2.5772 | 0.27466 | -2.655 | 5.2231 | -118.0939 | 4.6143 | 4.9805 | 5.3741 | 5.3238 | -118.5379 | 115.5533 | -4.9301 | 115.6311 | 123.4314 | -123.2986 | -0.32959 | 0.11902 | 0.07782 | 123.1888 | 123.5825 | 0.11444 | 118.483 | 115.6311 | 123.5321 | 122.8226 | -0.32959 | 118.483 | 115.6311 | 122.8226 | 0.11444 | 123.5321 | -7.8598 | -123.7427
1764.9688 | 123.4177 | -118.4555 | 4.9759 | -1.2999 | 0.050107 | -0.024302 | 0.086729 | -0.051486 | 0.048626 | 0.099494 | -2.33 | 0.31586 | -2.6276 | 5.2826 | -118.1305 | 4.5547 | 4.6692 | 5.0812 | 5.2139 | -118.7622 | 115.8279 | -4.66 | 116.1255 | 123.7381 | -123.1064 | -0.3067 | 0.23804 | 0.29755 | 123.1247 | 123.5367 | 0.32501 | 118.7714 | 116.1255 | 123.6694 | 123.0103 | -0.3067 | 118.7714 | 116.1255 | 123.0103 | 0.32501 | 123.6694 | -7.6035 | -123.7381
1765.9219 | 123.5092 | -118.3548 | 4.9942 | 0.47007 | 0.033017 | -0.020029 | 0.072843 | -0.055758 | 0.042217 | 0.09629 | -2.3529 | 0.25177 | -2.7512 | 4.9805 | -118.3456 | 4.6143 | 4.8798 | 5.0812 | 5.1636 | -118.7485 | 115.6036 | -4.7424 | 116.0019 | 123.3353 | -123.3398 | -0.39368 | 0.16937 | 0.39826 | 123.2346 | 123.436 | 0.009155 | 118.6066 | 116.0019 | 123.5184 | 122.9691 | -0.39368 | 118.6066 | 116.0019 | 122.9691 | 0.009155 | 123.5184 | -7.7454 | -123.7427
1766.9844 | 123.4497 | -117.9337 | 5.4291 | -0.24709 | 0.053311 | -0.015757 | 0.085661 | -0.048281 | 0.044354 | 0.10163 | -2.179 | 0.27466 | -2.5589 | 5.4382 | -117.9749 | 5.2597 | 5.2094 | 5.5206 | 5.5298 | -118.3456 | 115.3748 | -5.1544 | 115.7547 | 123.3719 | -123.4039 | -0.41199 | 0.10071 | 0.37994 | 123.143 | 123.4543 | -0.041199 | 118.2083 | 115.7547 | 123.4634 | 123.1934 | -0.41199 | 118.2083 | 115.7547 | 123.1934 | -0.041199 | 123.4634 | -7.988 | -123.7747
1767.9219 | 123.4451 | -118.4967 | 4.9026 | 0.22593 | 0.044766 | -0.02537 | 0.089933 | -0.045077 | 0.04649 | 0.099494 | -2.298 | 0.2655 | -2.6413 | 4.9301 | -118.4097 | 4.7607 | 4.7333 | 5.0674 | 5.0308 | -118.8675 | 115.8554 | -4.6371 | 116.1987 | 123.4268 | -123.3124 | -0.37079 | 0.12817 | 0.34332 | 123.23 | 123.5641 | 0.086975 | 118.7622 | 116.1987 | 123.5275 | 123.2574 | -0.37079 | 118.7622 | 116.1987 | 123.2574 | 0.086975 | 123.5275 | -7.5439 | -123.7701
1768.9844 | 123.4406 | -118.4235 | 4.9759 | 0.33274 | 0.043698 | -0.0018714 | 0.077116 | -0.052554 | 0.053967 | 0.093085 | -2.3117 | 0.27008 | -2.6596 | 4.9942 | -118.364 | 4.7516 | 4.7287 | 5.1498 | 5.0903 | -118.7668 | 115.7639 | -4.7058 | 116.1118 | 123.4177 | -123.3398 | -0.34332 | 0.11444 | 0.3479 | 123.1522 | 123.5733 | 0.059509 | 118.6935 | 116.1118 | 123.5138 | 123.175 | -0.34332 | 118.6935 | 116.1118 | 123.175 | 0.059509 | 123.5138 | -7.6355 | -123.7427
1769.9219 | 123.5504 | -118.3777 | 4.9484 | 0.33274 | 0.036221 | -0.0018714 | 0.061094 | -0.055758 | 0.044354 | 0.1059 | -2.2247 | 0.2243 | -2.623 | 4.8706 | -118.4372 | 4.7104 | 4.9301 | 5.0354 | 5.1453 | -118.7988 | 115.7547 | -4.7241 | 116.153 | 123.2483 | -123.3856 | -0.42114 | 0.19684 | 0.39826 | 123.3078 | 123.4131 | -0.059509 | 118.602 | 116.153 | 123.5229 | 123.0881 | -0.42114 | 118.602 | 116.153 | 123.0881 | -0.059509 | 123.5229 | -7.5714 | -123.7473
1770.9844 | 123.436 | -118.3319 | 5.0903 | -0.36916 | 0.037289 | -0.020029 | 0.079252 | -0.049349 | 0.042217 | 0.10484 | -2.2018 | 0.26093 | -2.5726 | 5.1041 | -118.2724 | 4.834 | 4.8614 | 5.2414 | 5.2322 | -118.6844 | 115.7593 | -4.8294 | 116.1301 | 123.436 | -123.3627 | -0.35248 | 0.14191 | 0.37079 | 123.1934 | 123.5733 | 0.059509 | 118.5928 | 116.1301 | 123.5641 | 123.1659 | -0.35248 | 118.5928 | 116.1301 | 123.1659 | 0.059509 | 123.5641 | -7.663 | -123.7747
1771.9219 | 123.4589 | -118.2449 | 5.0949 | 0.31749 | 0.044766 | -0.020029 | 0.091001 | -0.053622 | 0.044354 | 0.10911 | -2.2522 | 0.24719 | -2.6047 | 5.0583 | -118.2907 | 4.866 | 4.9255 | 5.2597 | 5.2002 | -118.6615 | 115.6403 | -4.8477 | 115.9927 | 123.3032 | -123.3856 | -0.41657 | 0.10529 | 0.35248 | 123.1705 | 123.5046 | -0.045776 | 118.4921 | 115.9927 | 123.4451 | 123.111 | -0.41657 | 118.4921 | 115.9927 | 123.111 | -0.045776 | 123.4451 | -7.6996 | -123.7564
1772.9219 | 123.5138 | -118.4875 | 4.8203 | 0.43956 | 0.045834 | -0.0040084 | 0.082456 | -0.058962 | 0.04649 | 0.098426 | -2.2339 | 0.22888 | -2.6138 | 4.747 | -118.5013 | 4.6188 | 4.7516 | 4.8752 | 5.0217 | -118.9499 | 115.8737 | -4.5914 | 116.2537 | 123.2346 | -123.3215 | -0.46234 | 0.20142 | 0.37994 | 123.2391 | 123.3627 | -0.013733 | 118.7164 | 116.2537 | 123.5092 | 123.1064 | -0.46234 | 118.7164 | 116.2537 | 123.1064 | -0.013733 | 123.5092 | -7.4341 | -123.7701
1773.9844 | 123.2895 | -118.5471 | 4.8248 | 0.39378 | 0.049038 | -0.0072124 | 0.078184 | -0.052554 | 0.040081 | 0.1059 | -2.2797 | 0.27466 | -2.6367 | 4.8752 | -118.4875 | 4.6738 | 4.5959 | 5.0308 | 4.9576 | -118.895 | 115.9103 | -4.5502 | 116.2674 | 123.4222 | -123.3124 | -0.3479 | 0.13275 | 0.35706 | 123.143 | 123.5779 | 0.059509 | 118.8217 | 116.2674 | 123.5046 | 123.2208 | -0.3479 | 118.8217 | 116.2674 | 123.2208 | 0.059509 | 123.5046 | -7.4615 | -123.7198
1774.9219 | 123.4314 | -118.2404 | 5.1544 | 5.6123 | 0.040494 | -0.026438 | 0.082456 | -0.055758 | 0.04649 | 0.10056 | -2.0828 | 0.29755 | -2.5909 | 5.1865 | -118.158 | 4.9759 | 4.9026 | 5.3101 | 5.3101 | -118.6203 | 115.6494 | -4.8569 | 116.1575 | 123.4268 | -123.3124 | -0.37994 | 0.15564 | 0.50812 | 123.143 | 123.5504 | 0.082397 | 118.5379 | 116.1575 | 123.5504 | 123.2162 | -0.37994 | 118.5379 | 116.1575 | 123.2162 | 0.082397 | 123.5504 | -7.7454 | -123.7747
1775.9844 | 123.4634 | -118.0801 | 5.3101 | -0.094502 | 0.046902 | -0.015757 | 0.092069 | -0.058962 | 0.061443 | 0.1027 | -2.0966 | 0.2655 | -2.5131 | 5.278 | -118.0893 | 5.0583 | 5.0903 | 5.4657 | 5.4382 | -118.4601 | 115.567 | -5.0446 | 115.9836 | 123.3582 | -123.3994 | -0.37994 | 0.12817 | 0.41657 | 123.1705 | 123.5458 | -0.009155 | 118.3456 | 115.9836 | 123.5184 | 123.1384 | -0.37994 | 118.3456 | 115.9836 | 123.1384 | -0.009155 | 123.5184 | -7.8232 | -123.7701
1776.9219 | 123.468 | -117.9382 | 5.4611 | 0.45481 | 0.043698 | -0.023234 | 0.078184 | -0.046145 | 0.05183 | 0.10697 | -2.2064 | 0.27008 | -2.5406 | 5.4565 | -117.9062 | 5.3238 | 5.2597 | 5.5847 | 5.6213 | -118.3228 | 115.3976 | -5.191 | 115.7318 | 123.3948 | -123.3673 | -0.38452 | 0.16022 | 0.33417 | 123.1979 | 123.5229 | 0.032043 | 118.2083 | 115.7318 | 123.5596 | 123.262 | -0.38452 | 118.2083 | 115.7318 | 123.262 | 0.032043 | 123.5596 | -8.0017 | -123.7839
1777.9844 | 123.4589 | -118.2037 | 5.1865 | -0.18605 | 0.031949 | 0.00026463 | 0.074979 | -0.051486 | 0.05183 | 0.10697 | -2.0874 | 0.25635 | -2.4582 | 5.1956 | -118.1992 | 5.1132 | 4.985 | 5.3238 | 5.3421 | -118.5791 | 115.7455 | -4.9301 | 116.1163 | 123.3994 | -123.3856 | -0.37537 | 0.15564 | 0.37079 | 123.1888 | 123.5275 | 0.004577 | 118.4601 | 116.1163 | 123.5458 | 123.317 | -0.37537 | 118.4601 | 116.1163 | 123.317 | 0.004577 | 123.5458 | -7.6447 | -123.7656
1778.9219 | 123.4314 | -118.6523 | 4.7516 | -0.15554 | 0.04797 | -0.022166 | 0.078184 | -0.050418 | 0.043285 | 0.1027 | -2.2064 | 0.27924 | -2.5543 | 4.7104 | -118.6249 | 4.6463 | 4.509 | 4.8752 | 4.8386 | -119.0369 | 116.098 | -4.4724 | 116.4459 | 123.3627 | -123.3765 | -0.38452 | 0.086975 | 0.3479 | 123.1613 | 123.5275 | 0.027466 | 118.9316 | 116.4459 | 123.4909 | 123.2986 | -0.38452 | 118.9316 | 116.4459 | 123.2986 | 0.027466 | 123.4909 | -7.3059 | -123.7885
1779.9844 | 123.4406 | -117.8513 | 5.5115 | 0.1649 | 0.041562 | 0.015218 | 0.077116 | -0.046145 | 0.073193 | 0.10056 | -2.0645 | 0.31586 | -2.4307 | 5.6717 | -117.7231 | 5.4565 | 5.2734 | 5.6168 | 5.6946 | -118.2541 | 115.4205 | -5.1956 | 115.7867 | 123.5229 | -123.2346 | -0.40283 | 0.18311 | 0.36621 | 123.1247 | 123.468 | 0.12817 | 118.1671 | 115.7867 | 123.5458 | 123.3078 | -0.40283 | 118.1671 | 115.7867 | 123.3078 | 0.12817 | 123.5458 | -7.9422 | -123.7656
1780.9219 | 123.3719 | -117.3294 | 6.1157 | 0.027569 | 0.040494 | -0.0082804 | 0.082456 | -0.03226 | 0.05183 | 0.10484 | -2.0691 | 0.27008 | -2.4078 | 6.1295 | -117.1783 | 5.9418 | 5.8273 | 6.2714 | 6.189 | -117.6956 | 114.9216 | -5.8456 | 115.2603 | 123.4589 | -123.2941 | -0.36621 | 0.073242 | 0.33874 | 123.1567 | 123.6008 | 0.15106 | 117.5995 | 115.2603 | 123.5184 | 123.2712 | -0.36621 | 117.5995 | 115.2603 | 123.2712 | 0.15106 | 123.5184 | -8.5236 | -123.8113
1781.9844 | 123.4451 | -118.5928 | 4.834 | -0.23183 | 0.035153 | -0.0040084 | 0.074979 | -0.053622 | 0.042217 | 0.10163 | -2.2293 | 0.2655 | -2.5726 | 4.7974 | -118.5608 | 4.7653 | 4.5639 | 4.9896 | 4.9713 | -118.9682 | 116.0202 | -4.5685 | 116.3635 | 123.3902 | -123.3948 | -0.37537 | 0.13733 | 0.34332 | 123.1567 | 123.5825 | 0.032043 | 118.8583 | 116.3635 | 123.5641 | 123.3582 | -0.37537 | 118.8583 | 116.3635 | 123.3582 | 0.032043 | 123.5641 | -7.4066 | -123.8022
1782.9219 | 123.4543 | -118.5196 | 4.8431 | 0.47007 | 0.040494 | 0.0066726 | 0.072843 | -0.053622 | 0.048626 | 0.10056 | -2.2842 | 0.26093 | -2.6321 | 4.8203 | -118.5013 | 4.7745 | 4.66 | 4.9896 | 4.9759 | -118.9133 | 115.8875 | -4.5822 | 116.2354 | 123.3398 | -123.3444 | -0.39368 | 0.13275 | 0.3479 | 123.1796 | 123.5092 | 0.01831 | 118.7805 | 116.2354 | 123.4955 | 123.2941 | -0.39368 | 118.7805 | 116.2354 | 123.2941 | 0.01831 | 123.4955 | -7.4753 | -123.7564
1783.9844 | 123.3856 | -118.3365 | 5.0995 | 0.1649 | 0.044766 | -0.014689 | 0.096342 | -0.045077 | 0.055035 | 0.095222 | -2.2659 | 0.2655 | -2.6138 | 5.1315 | -118.222 | 5.0674 | 4.8248 | 5.3009 | 5.2002 | -118.6661 | 115.7227 | -4.834 | 116.0706 | 123.468 | -123.3215 | -0.32959 | 0.10071 | 0.3479 | 123.1613 | 123.6374 | 0.11444 | 118.602 | 116.0706 | 123.5367 | 123.4039 | -0.32959 | 118.602 | 116.0706 | 123.4039 | 0.11444 | 123.5367 | -7.7133 | -123.7656
1784.9219 | 123.4222 | -117.9337 | 5.4749 | 1.6145 | 0.049038 | -0.015757 | 0.079252 | -0.051486 | 0.056103 | 0.099494 | -2.1881 | 0.28839 | -2.5818 | 5.4062 | -117.952 | 5.397 | 5.2826 | 5.658 | 5.5618 | -118.3319 | 115.3519 | -5.1865 | 115.7455 | 123.3398 | -123.4268 | -0.39825 | 0.086975 | 0.39368 | 123.2162 | 123.5916 | -0.01831 | 118.222 | 115.7455 | 123.4955 | 123.3307 | -0.39825 | 118.222 | 115.7455 | 123.3307 | -0.01831 | 123.4955 | -8.0566 | -123.8068
1785.9219 | 123.4131 | -118.5242 | 4.8935 | -5.2062 | 0.045834 | -0.017893 | 0.079252 | -0.052554 | 0.057171 | 0.11231 | -2.3987 | 0.27924 | -2.6276 | 4.8752 | -118.4738 | 4.834 | 4.6646 | 5.0446 | 4.9988 | -118.8675 | 115.8966 | -4.6143 | 116.1255 | 123.3994 | -123.3673 | -0.34332 | 0.10529 | 0.22888 | 123.1888 | 123.5687 | 0.050354 | 118.8034 | 116.1255 | 123.5229 | 123.3582 | -0.34332 | 118.8034 | 116.1255 | 123.3582 | 0.050354 | 123.5229 | -7.5211 | -123.761
1786.9219 | 123.4177 | -118.6844 | 4.7424 | 0.37852 | 0.04797 | -0.017893 | 0.068571 | -0.057894 | 0.055035 | 0.094154 | -2.0874 | 0.27008 | -2.6367 | 4.747 | -118.5562 | 4.6692 | 4.4907 | 4.9255 | 4.8981 | -119.0369 | 116.0477 | -4.4724 | 116.597 | 123.4314 | -123.2986 | -0.35248 | 0.15564 | 0.54932 | 123.175 | 123.6099 | 0.12817 | 118.9545 | 116.597 | 123.5825 | 123.3536 | -0.35248 | 118.9545 | 116.597 | 123.3536 | 0.12817 | 123.5825 | -7.3792 | -123.7793
1787.9844 | 123.4634 | -117.7094 | 5.5984 | -0.29287 | 0.040494 | -0.010416 | 0.085661 | -0.055758 | 0.05183 | 0.099494 | -2.0874 | 0.26093 | -2.4811 | 5.246 | -118.1122 | 5.1819 | 5.0949 | 5.4291 | 5.3925 | -118.3914 | 115.2283 | -5.3375 | 115.6219 | 122.9553 | -123.7106 | -0.68207 | -0.20599 | 0.39368 | 122.8043 | 123.1384 | -0.40283 | 117.9703 | 115.6219 | 123.1018 | 122.8912 | -0.68207 | 117.9703 | 115.6219 | 122.8912 | -0.40283 | 123.1018 | -8.0795 | -123.9899
1788.9219 | 123.2986 | -117.6544 | 5.7358 | 0.43956 | 0.056515 | 0.0045366 | 0.08032 | -0.039736 | 0.05183 | 0.097358 | -2.1149 | 0.28381 | -2.4902 | 5.7449 | -117.6041 | 5.6946 | 5.484 | 5.983 | 5.8044 | -118.0206 | 115.1642 | -5.452 | 115.5396 | 123.3994 | -123.3398 | -0.36621 | 0.068664 | 0.37537 | 123.1384 | 123.6374 | 0.050354 | 117.9382 | 115.5396 | 123.4589 | 123.349 | -0.36621 | 117.9382 | 115.5396 | 123.349 | 0.050354 | 123.4589 | -8.226 | -123.7564
1789.9688 | 123.3994 | -117.778 | 5.6671 | 0.36326 | 0.04263 | -0.0029404 | 0.085661 | -0.051486 | 0.055035 | 0.10697 | -2.179 | 0.27008 | -2.4994 | 5.69 | -117.6773 | 5.603 | 5.4337 | 5.8731 | 5.777 | -118.0939 | 115.2786 | -5.397 | 115.5991 | 123.468 | -123.3444 | -0.31586 | 0.10986 | 0.32043 | 123.2117 | 123.6511 | 0.10071 | 118.0481 | 115.5991 | 123.555 | 123.381 | -0.31586 | 118.0481 | 115.5991 | 123.381 | 0.10071 | 123.555 | -8.1665 | -123.761
1790.9219 | 123.4085 | -118.6295 | 4.7928 | 1.7823 | 0.046902 | -0.041392 | 0.067503 | -0.049349 | 0.049694 | 0.10377 | -2.1194 | 0.28839 | -2.5589 | 4.8248 | -118.5562 | 4.7379 | 4.5914 | 4.9805 | 4.9347 | -118.9819 | 116.0706 | -4.5044 | 116.51 | 123.4543 | -123.349 | -0.35248 | 0.14191 | 0.43945 | 123.2208 | 123.6099 | 0.073243 | 118.9178 | 116.51 | 123.5641 | 123.3673 | -0.35248 | 118.9178 | 116.51 | 123.3673 | 0.073243 | 123.5641 | -7.3517 | -123.7747
1791.9844 | 123.3994 | -118.9224 | 4.4861 | 0.088604 | 0.040494 | -0.0018714 | 0.081388 | -0.055758 | 0.05183 | 0.10163 | -2.2202 | 0.27466 | -2.5818 | 4.5136 | -118.84 | 4.4449 | 4.2526 | 4.6692 | 4.6417 | -119.2886 | 116.3406 | -4.2114 | 116.7023 | 123.436 | -123.3261 | -0.36621 | 0.15564 | 0.36163 | 123.175 | 123.5916 | 0.082397 | 119.1971 | 116.7023 | 123.5641 | 123.3673 | -0.36621 | 119.1971 | 116.7023 | 123.3673 | 0.082397 | 123.5641 | -7.0679 | -123.7747
1792.9219 | 123.468 | -118.8446 | 4.5319 | 0.40904 | 0.04797 | 0.0066726 | 0.078184 | -0.047213 | 0.071056 | 0.10163 | -2.2614 | 0.27466 | -2.6001 | 4.454 | -118.895 | 4.3762 | 4.3671 | 4.7516 | 4.5639 | -119.252 | 116.2445 | -4.2572 | 116.5833 | 123.2986 | -123.4268 | -0.40741 | 0.032044 | 0.33874 | 123.2117 | 123.5962 | -0.050354 | 119.1193 | 116.5833 | 123.4085 | 123.2208 | -0.40741 | 119.1193 | 116.5833 | 123.2208 | -0.050354 | 123.4085 | -7.132 | -123.7839
1793.9844 | 123.4314 | -119.0002 | 4.422 | 0.073345 | 0.040494 | -0.02537 | 0.081388 | -0.045077 | 0.048626 | 0.10056 | -2.1744 | 0.30212 | -2.504 | 4.3991 | -118.9499 | 4.3533 | 4.1611 | 4.5959 | 4.5502 | -119.3756 | 116.4963 | -4.1199 | 116.8259 | 123.3994 | -123.3719 | -0.37537 | 0.12817 | 0.32959 | 123.1613 | 123.5962 | 0.050354 | 119.3024 | 116.8259 | 123.5504 | 123.3536 | -0.37537 | 119.3024 | 116.8259 | 123.3536 | 0.050354 | 123.5504 | -6.926 | -123.7976
1794.9219 | 123.4222 | -118.959 | 4.4495 | -0.033467 | 0.045834 | 0.0088096 | 0.069639 | -0.057894 | 0.055035 | 0.10484 | -2.1469 | 0.27008 | -2.536 | 4.4495 | -118.8995 | 4.3716 | 4.1977 | 4.6051 | 4.5914 | -119.3573 | 116.423 | -4.1794 | 116.8121 | 123.4085 | -123.349 | -0.39825 | 0.14191 | 0.3891 | 123.1567 | 123.5641 | 0.059509 | 119.2291 | 116.8121 | 123.5504 | 123.3307 | -0.39825 | 119.2291 | 116.8121 | 123.3307 | 0.059509 | 123.5504 | -6.9855 | -123.8068
1795.9844 | 123.4406 | -118.7988 | 4.6371 | -0.27761 | 0.045834 | -0.049937 | 0.066434 | -0.048281 | 0.055035 | 0.1027 | -2.1515 | 0.27466 | -2.4994 | 4.6188 | -118.7393 | 4.5593 | 4.3533 | 4.7836 | 4.7562 | -119.1605 | 116.2994 | -4.3625 | 116.6473 | 123.4177 | -123.3765 | -0.36163 | 0.11902 | 0.3479 | 123.1522 | 123.5825 | 0.059509 | 119.0735 | 116.6473 | 123.555 | 123.3582 | -0.36163 | 119.0735 | 116.6473 | 123.3582 | 0.059509 | 123.555 | -7.1365 | -123.7976
1796.9219 | 123.4039 | -118.9316 | 4.4861 | 0.39378 | 0.054379 | -0.034983 | 0.077116 | -0.042941 | 0.048626 | 0.1027 | -2.2568 | 0.27466 | -2.6276 | 4.4952 | -118.8492 | 4.4266 | 4.2206 | 4.66 | 4.6005 | -119.3161 | 116.304 | -4.2114 | 116.6748 | 123.4268 | -123.3353 | -0.38452 | 0.11444 | 0.37079 | 123.1522 | 123.5916 | 0.082398 | 119.2062 | 116.6748 | 123.5321 | 123.3582 | -0.38452 | 119.2062 | 116.6748 | 123.3582 | 0.082398 | 123.5321 | -7.1136 | -123.8022
1797.9688 | 123.4772 | -119.0186 | 4.3533 | -0.36916 | 0.037289 | -0.054209 | 0.058958 | -0.047213 | 0.030468 | 0.10697 | -2.1835 | 0.24261 | -2.536 | 4.2114 | -119.0735 | 4.2068 | 4.184 | 4.4403 | 4.5364 | -119.4489 | 116.4825 | -4.1107 | 116.835 | 123.23 | -123.4268 | -0.4303 | 0.18311 | 0.35248 | 123.2025 | 123.4589 | -0.054931 | 119.2612 | 116.835 | 123.555 | 123.2254 | -0.4303 | 119.2612 | 116.835 | 123.2254 | -0.054931 | 123.555 | -6.8893 | -123.8022
1798.9219 | 123.3765 | -118.6935 | 4.7333 | 0.10386 | 0.04263 | -0.033915 | 0.082456 | -0.051486 | 0.055035 | 0.1027 | -2.2888 | 0.26093 | -2.6596 | 4.7607 | -118.602 | 4.6967 | 4.5044 | 4.8981 | 4.8477 | -119.0781 | 116.0339 | -4.4724 | 116.4047 | 123.4543 | -123.3353 | -0.38452 | 0.11444 | 0.37079 | 123.1979 | 123.5916 | 0.091552 | 118.9545 | 116.4047 | 123.5413 | 123.3902 | -0.38452 | 118.9545 | 116.4047 | 123.3902 | 0.091552 | 123.5413 | -7.3929 | -123.8113
1799.9844 | 123.4222 | -118.7897 | 4.6509 | -0.24709 | 0.028744 | -0.036051 | 0.058958 | -0.052554 | 0.035809 | 0.11231 | -2.2568 | 0.27466 | -2.5589 | 4.628 | -118.721 | 4.6005 | 4.3945 | 4.8386 | 4.7928 | -119.101 | 116.2308 | -4.3762 | 116.5329 | 123.4177 | -123.3719 | -0.31128 | 0.14191 | 0.30212 | 123.1842 | 123.6282 | 0.068665 | 119.0643 | 116.5329 | 123.5825 | 123.3902 | -0.31128 | 119.0643 | 116.5329 | 123.3902 | 0.068665 | 123.5825 | -7.2098 | -123.7518
1800.9219 | 123.436 | -118.3685 | 5.0446 | 0.48533 | 0.043698 | -0.028574 | 0.072843 | -0.053622 | 0.072125 | 0.097358 | -2.2247 | 0.26093 | -2.5772 | 4.8569 | -118.2037 | 4.985 | 4.6967 | 5.1682 | 5.1865 | -118.7393 | 115.7913 | -4.7836 | 116.1438 | 123.2254 | -123.2483 | -0.37079 | 0.14191 | 0.35248 | 123.0652 | 123.5367 | 0.1648 | 118.6295 | 116.1438 | 123.555 | 123.3536 | -0.37079 | 118.6295 | 116.1438 | 123.3536 | 0.1648 | 123.555 | -7.6218 | -123.7839
1801.9844 | 123.4497 | -118.9911 | 4.3991 | -0.15554 | 0.033017 | -0.040324 | 0.078184 | -0.052554 | 0.047558 | 0.10911 | -2.1881 | 0.26093 | -2.5909 | 4.3762 | -118.9865 | 4.2938 | 4.1931 | 4.5227 | 4.5639 | -119.4077 | 116.4001 | -4.1382 | 116.803 | 123.3673 | -123.3856 | -0.41656 | 0.16479 | 0.40283 | 123.1842 | 123.5138 | 0.004578 | 119.252 | 116.803 | 123.555 | 123.2849 | -0.41656 | 119.252 | 116.803 | 123.2849 | 0.004578 | 123.555 | -6.9901 | -123.8068
1802.9219 | 123.3765 | -118.808 | 4.5959 | 0.22593 | 0.056515 | -0.012553 | 0.077116 | -0.041873 | 0.06358 | 0.1059 | -2.211 | 0.28839 | -2.5772 | 4.6509 | -118.6981 | 4.5593 | 4.3121 | 4.8019 | 4.7287 | -119.1879 | 116.2308 | -4.3076 | 116.597 | 123.4589 | -123.2941 | -0.37994 | 0.13275 | 0.36621 | 123.1201 | 123.6099 | 0.10986 | 119.0964 | 116.597 | 123.5367 | 123.3673 | -0.37994 | 119.0964 | 116.597 | 123.3673 | 0.10986 | 123.5367 | -7.1732 | -123.7839
1803.9844 | 123.4177 | -118.9819 | 4.4312 | 0.042827 | 0.050107 | -0.012553 | 0.083524 | -0.047213 | 0.052898 | 0.11231 | -2.2064 | 0.28839 | -2.6047 | 4.4312 | -118.9682 | 4.3304 | 4.1885 | 4.5639 | 4.5364 | -119.3985 | 116.3773 | -4.1428 | 116.7755 | 123.4131 | -123.3994 | -0.41657 | 0.10529 | 0.39825 | 123.1705 | 123.5458 | 0.013733 | 119.2703 | 116.7755 | 123.5184 | 123.3124 | -0.41657 | 119.2703 | 116.7755 | 123.3124 | 0.013733 | 123.5184 | -7.0358 | -123.8297
1804.9219 | 123.4268 | -117.8604 | 5.5527 | 0.088604 | 0.052243 | -0.010416 | 0.094205 | -0.044009 | 0.057171 | 0.10484 | -2.0966 | 0.26093 | -2.4628 | 5.6351 | -117.746 | 5.5756 | 5.3696 | 5.7404 | 5.7266 | -118.2129 | 115.3976 | -5.2917 | 115.7639 | 123.4955 | -123.2986 | -0.35248 | 0.17395 | 0.36621 | 123.23 | 123.6008 | 0.11444 | 118.1213 | 115.7639 | 123.587 | 123.436 | -0.35248 | 118.1213 | 115.7639 | 123.436 | 0.11444 | 123.587 | -8.0154 | -123.7656
1805.9844 | 123.4406 | -118.6844 | 4.715 | -0.24709 | 0.027676 | -0.031779 | 0.079252 | -0.051486 | 0.043285 | 0.11124 | -2.2934 | 0.29755 | -2.5681 | 4.6921 | -118.6615 | 4.6646 | 4.4403 | 4.8752 | 4.8477 | -119.0689 | 116.1163 | -4.4174 | 116.391 | 123.3765 | -123.3765 | -0.38452 | 0.13275 | 0.27466 | 123.1247 | 123.5596 | 0.022888 | 118.9819 | 116.391 | 123.5321 | 123.349 | -0.38452 | 118.9819 | 116.391 | 123.349 | 0.022888 | 123.5321 | -7.283 | -123.7839
1806.9219 | 123.4039 | -119.0323 | 4.3625 | 0.073345 | 0.052243 | -0.023234 | 0.088865 | -0.041873 | 0.057171 | 0.1027 | -2.3071 | 0.27466 | -2.6917 | 4.3945 | -118.9957 | 4.303 | 4.1245 | 4.5273 | 4.4907 | -119.4397 | 116.3406 | -4.0878 | 116.7252 | 123.4268 | -123.3582 | -0.40741 | 0.12817 | 0.38452 | 123.1567 | 123.5596 | 0.036621 | 119.3069 | 116.7252 | 123.5229 | 123.3353 | -0.40741 | 119.3069 | 116.7252 | 123.3353 | 0.036621 | 123.5229 | -7.0541 | -123.8022
1807.9688 | 123.4497 | -118.7851 | 4.6463 | -0.33864 | 0.029812 | -0.039256 | 0.070707 | -0.048281 | 0.035809 | 0.10911 | -2.2751 | 0.24261 | -2.6276 | 4.5868 | -118.7622 | 4.541 | 4.4083 | 4.7699 | 4.7699 | -119.1376 | 116.1575 | -4.4037 | 116.51 | 123.3719 | -123.4085 | -0.35248 | 0.1236 | 0.35248 | 123.1934 | 123.555 | 0.022888 | 119.0277 | 116.51 | 123.555 | 123.3261 | -0.35248 | 119.0277 | 116.51 | 123.3261 | 0.022888 | 123.555 | -7.2739 | -123.7839
1808.9219 | 123.436 | -118.8538 | 4.5776 | -0.32338 | 0.029812 | -0.030711 | 0.072843 | -0.038668 | 0.05183 | 0.10056 | -2.2659 | 0.28381 | -2.6276 | 4.5639 | -118.8126 | 4.5044 | 4.3396 | 4.7333 | 4.7104 | -119.2108 | 116.2262 | -4.2938 | 116.5878 | 123.4177 | -123.3902 | -0.35706 | 0.13275 | 0.36163 | 123.1934 | 123.587 | 0.041199 | 119.1376 | 116.5878 | 123.5641 | 123.3582 | -0.35706 | 119.1376 | 116.5878 | 123.3582 | 0.041199 | 123.5641 | -7.2052 | -123.7885
1809.9844 | 123.4085 | -118.5059 | 4.9026 | -0.44545 | 0.023404 | -0.052073 | 0.062162 | -0.044009 | 0.033672 | 0.11018 | -2.2888 | 0.2655 | -2.6138 | 4.9072 | -118.4555 | 4.8614 | 4.6097 | 5.0858 | 5.0537 | -118.8629 | 115.892 | -4.6371 | 116.217 | 123.4131 | -123.3582 | -0.35706 | 0.15106 | 0.32501 | 123.1155 | 123.5916 | 0.050354 | 118.7714 | 116.217 | 123.5596 | 123.3673 | -0.35706 | 118.7714 | 116.217 | 123.3673 | 0.050354 | 123.5596 | -7.5165 | -123.7656
1810.9219 | 123.4543 | -117.9199 | 5.484 | -0.14028 | 0.040494 | -0.0082804 | 0.082456 | -0.055758 | 0.056103 | 0.10377 | -2.1378 | 0.27466 | -2.5223 | 5.452 | -117.9382 | 5.3787 | 5.278 | 5.6076 | 5.5984 | -118.3136 | 115.3976 | -5.2094 | 115.7822 | 123.3719 | -123.4222 | -0.39368 | 0.11444 | 0.38452 | 123.1979 | 123.5275 | -0.01831 | 118.1946 | 115.7822 | 123.5184 | 123.2986 | -0.39368 | 118.1946 | 115.7822 | 123.2986 | -0.01831 | 123.5184 | -8.0063 | -123.7976
1811.9844 | 123.5779 | -116.5649 | 6.7749 | -0.36916 | 0.024472 | -0.041392 | 0.054685 | -0.042941 | 0.026196 | 0.11338 | -1.9501 | 0.2243 | -2.3575 | 6.6238 | -116.7206 | 6.6284 | 6.7245 | 6.839 | 6.9992 | -116.9586 | 114.2075 | -6.5506 | 114.6149 | 123.1888 | -123.4955 | -0.39368 | 0.22431 | 0.40741 | 123.2895 | 123.4039 | -0.15564 | 116.7892 | 114.6149 | 123.5641 | 123.1934 | -0.39368 | 116.7892 | 114.6149 | 123.1934 | -0.15564 | 123.5641 | -9.1324 | -123.7335
1812.9219 | 123.4543 | -118.0527 | 5.3741 | -0.59804 | 0.028744 | -0.024302 | 0.072843 | -0.053622 | 0.056103 | 0.10056 | -2.1332 | 0.29755 | -2.4673 | 5.3925 | -117.9977 | 5.3146 | 5.1224 | 5.5435 | 5.4977 | -118.4235 | 115.5853 | -5.0766 | 115.9195 | 123.4451 | -123.3719 | -0.37079 | 0.1236 | 0.33417 | 123.175 | 123.5962 | 0.054931 | 118.3502 | 115.9195 | 123.5504 | 123.3673 | -0.37079 | 118.3502 | 115.9195 | 123.3673 | 0.054931 | 123.5504 | -7.8415 | -123.7976
1813.9844 | 123.468 | -118.3411 | 5.0583 | -0.4302 | 0.033017 | -0.017893 | 0.06323 | -0.052554 | 0.035809 | 0.10911 | -2.1378 | 0.23346 | -2.5314 | 4.9896 | -118.3456 | 5.0171 | 4.8935 | 5.2094 | 5.2185 | -118.7073 | 115.8096 | -4.8248 | 116.2033 | 123.3307 | -123.4039 | -0.36621 | 0.16022 | 0.39368 | 123.2346 | 123.5504 | -0.004578 | 118.5745 | 116.2033 | 123.5596 | 123.3582 | -0.36621 | 118.5745 | 116.2033 | 123.3582 | -0.004578 | 123.5596 | -7.5897 | -123.7656
1814.9219 | 123.4406 | -118.4143 | 4.9759 | 0.47007 | 0.050107 | -0.04246 | 0.079252 | -0.038668 | 0.071056 | 0.089881 | -2.211 | 0.27466 | -2.6001 | 4.8614 | -118.2312 | 4.9576 | 4.6692 | 5.1224 | 5.1086 | -118.808 | 115.8142 | -4.7012 | 116.2033 | 123.2758 | -123.2071 | -0.39368 | 0.13275 | 0.3891 | 123.0835 | 123.5367 | 0.18311 | 118.689 | 116.2033 | 123.5229 | 123.3719 | -0.39368 | 118.689 | 116.2033 | 123.3719 | 0.18311 | 123.5229 | -7.576 | -123.7839
1815.9844 | 123.5138 | -118.1076 | 5.2322 | -0.10976 | 0.02554 | -0.031779 | 0.055753 | -0.062167 | 0.026196 | 0.10911 | -2.1744 | 0.23346 | -2.5177 | 5.1132 | -118.2358 | 5.0858 | 5.1315 | 5.2963 | 5.4291 | -118.5242 | 115.5899 | -4.9988 | 115.9332 | 123.2208 | -123.468 | -0.41656 | 0.19684 | 0.34332 | 123.2391 | 123.4039 | -0.12817 | 118.3411 | 115.9332 | 123.5367 | 123.1934 | -0.41656 | 118.3411 | 115.9332 | 123.1934 | -0.12817 | 123.5367 | -7.7499 | -123.7564
1816.9219 | 123.4131 | -115.9058 | 7.5256 | -0.38442 | 0.038357 | -0.036051 | 0.077116 | -0.057894 | 0.049694 | 0.10697 | -1.8723 | 0.2655 | -2.1744 | 7.6218 | -115.8279 | 7.5256 | 7.2784 | 7.7042 | 7.7087 | -116.2308 | 113.7314 | -7.2601 | 114.0335 | 123.5275 | -123.3536 | -0.32501 | 0.1831 | 0.30212 | 123.1842 | 123.6099 | 0.07782 | 116.1713 | 114.0335 | 123.6145 | 123.4314 | -0.32501 | 116.1713 | 114.0335 | 123.4314 | 0.07782 | 123.6145 | -9.7 | -123.7564
1817.9844 | 123.4497 | -116.4642 | 6.9489 | -0.39968 | 0.036221 | -0.031779 | 0.060026 | -0.057894 | 0.041149 | 0.10484 | -1.8997 | 0.22888 | -2.2751 | 6.8848 | -116.597 | 6.7703 | 6.7566 | 7.0633 | 7.077 | -116.8396 | 114.1891 | -6.72 | 114.5645 | 123.349 | -123.5458 | -0.37537 | 0.12817 | 0.37537 | 123.2208 | 123.5275 | -0.13275 | 116.6931 | 114.5645 | 123.5413 | 123.2346 | -0.37537 | 116.6931 | 114.5645 | 123.2346 | -0.13275 | 123.5413 | -9.2239 | -123.7885
1818.9219 | 123.4085 | -117.7505 | 5.6488 | -0.56752 | 0.023404 | -0.031779 | 0.071775 | -0.051486 | 0.033672 | 0.10697 | -2.0279 | 0.28381 | -2.3758 | 5.6625 | -117.7231 | 5.5847 | 5.4108 | 5.864 | 5.7724 | -118.0756 | 115.3748 | -5.365 | 115.7227 | 123.4131 | -123.3719 | -0.32501 | 0.1236 | 0.3479 | 123.1613 | 123.6145 | 0.027466 | 118.0344 | 115.7227 | 123.5229 | 123.3353 | -0.32501 | 118.0344 | 115.7227 | 123.3353 | 0.027466 | 123.5229 | -8.0246 | -123.7244
1819.9844 | 123.5092 | -118.158 | 5.2368 | 0.10386 | 0.049038 | -0.033915 | 0.087797 | -0.051486 | 0.043285 | 0.1027 | -2.0187 | 0.24261 | -2.4307 | 5.2505 | -118.1717 | 5.1132 | 5.0125 | 5.3604 | 5.3604 | -118.5333 | 115.7272 | -4.9942 | 116.1392 | 123.4085 | -123.4085 | -0.37537 | 0.1236 | 0.41199 | 123.1705 | 123.5184 | -0.013733 | 118.4006 | 116.1392 | 123.5184 | 123.2712 | -0.37537 | 118.4006 | 116.1392 | 123.2712 | -0.013733 | 123.5184 | -7.6675 | -123.7701
1820.9219 | 123.4589 | -116.4368 | 6.9305 | -0.39968 | 0.033017 | -0.016825 | 0.064298 | -0.049349 | 0.034741 | 0.10697 | -1.8127 | 0.24261 | -2.1561 | 6.9717 | -116.4093 | 6.8848 | 6.7429 | 7.0587 | 7.1732 | -116.7892 | 114.2807 | -6.6879 | 114.624 | 123.4085 | -123.3398 | -0.35248 | 0.24261 | 0.34332 | 123.1796 | 123.4955 | 0.027466 | 116.6794 | 114.624 | 123.6099 | 123.3215 | -0.35248 | 116.6794 | 114.624 | 123.3215 | 0.027466 | 123.6099 | -9.0866 | -123.7198
1821.9688 | 123.4222 | -117.7002 | 5.722 | 1.1262 | 0.037289 | -0.040324 | 0.08032 | -0.057894 | 0.045422 | 0.10056 | -2.0233 | 0.2655 | -2.4261 | 5.6717 | -117.6544 | 5.6442 | 5.603 | 5.9372 | 5.809 | -118.0573 | 115.274 | -5.4565 | 115.6769 | 123.3719 | -123.3765 | -0.35706 | 0.086975 | 0.40283 | 123.3032 | 123.6374 | 0.045776 | 117.9657 | 115.6769 | 123.5092 | 123.3444 | -0.35706 | 117.9657 | 115.6769 | 123.3444 | 0.045776 | 123.5092 | -8.1482 | -123.7793
1822.9219 | 123.5367 | -117.9657 | 5.3467 | -0.14028 | 0.018063 | -0.037119 | 0.054685 | -0.061099 | 0.033672 | 0.10377 | -2.0004 | 0.21973 | -2.3941 | 5.2231 | -118.1168 | 5.2094 | 5.3192 | 5.4108 | 5.5527 | -118.3868 | 115.5716 | -5.127 | 115.9653 | 123.1888 | -123.4634 | -0.42114 | 0.20599 | 0.39368 | 123.2849 | 123.3765 | -0.15106 | 118.1854 | 115.9653 | 123.5184 | 123.175 | -0.42114 | 118.1854 | 115.9653 | 123.175 | -0.15106 | 123.5184 | -7.7408 | -123.7335
1823.9844 | 123.5229 | -116.5283 | 6.8069 | 0.47007 | 0.037289 | -0.033915 | 0.082456 | -0.062167 | 0.030468 | 0.099494 | -1.9592 | 0.22888 | -2.3392 | 6.8298 | -116.5604 | 6.7108 | 6.8253 | 6.9214 | 7.0587 | -116.9495 | 114.1891 | -6.5781 | 114.5691 | 123.3582 | -123.3673 | -0.42114 | 0.25177 | 0.37994 | 123.3536 | 123.4497 | -0.032044 | 116.7572 | 114.5691 | 123.587 | 123.2391 | -0.42114 | 116.7572 | 114.5691 | 123.2391 | -0.032044 | 123.587 | -9.1461 | -123.7564
1824.9219 | 123.4177 | -117.7048 | 5.7037 | 0.088604 | 0.043698 | -0.037119 | 0.088865 | -0.061099 | 0.057171 | 0.090949 | -2.0416 | 0.2655 | -2.4033 | 5.7678 | -117.6178 | 5.658 | 5.4794 | 5.864 | 5.8502 | -118.0664 | 115.3015 | -5.4382 | 115.6631 | 123.4726 | -123.3215 | -0.36163 | 0.14649 | 0.36163 | 123.1842 | 123.5687 | 0.086975 | 117.9703 | 115.6631 | 123.555 | 123.3627 | -0.36163 | 117.9703 | 115.6631 | 123.3627 | 0.086975 | 123.555 | -8.107 | -123.7701
1825.9844 | 123.4955 | -117.9199 | 5.4153 | -0.0029495 | 0.020199 | -0.02537 | 0.067503 | -0.05469 | 0.024059 | 0.095222 | -2.1011 | 0.2243 | -2.4216 | 5.3421 | -118.0206 | 5.3421 | 5.3192 | 5.5161 | 5.5801 | -118.3594 | 115.4984 | -5.191 | 115.8188 | 123.262 | -123.436 | -0.43945 | 0.16479 | 0.32043 | 123.2391 | 123.436 | -0.10071 | 118.1442 | 115.8188 | 123.5001 | 123.262 | -0.43945 | 118.1442 | 115.8188 | 123.262 | -0.10071 | 123.5001 | -7.8369 | -123.7747
1826.9219 | 123.5825 | -117.0135 | 6.3309 | -0.10976 | 0.019131 | -0.023234 | 0.065366 | -0.057894 | 0.027264 | 0.10484 | -1.9409 | 0.23804 | -2.2888 | 6.1798 | -117.1555 | 6.1752 | 6.2622 | 6.3904 | 6.4957 | -117.4438 | 114.7247 | -6.0928 | 115.0726 | 123.1934 | -123.4863 | -0.4303 | 0.16479 | 0.3479 | 123.2758 | 123.4039 | -0.14191 | 117.2516 | 115.0726 | 123.5092 | 123.1888 | -0.4303 | 117.2516 | 115.0726 | 123.1888 | -0.14191 | 123.5092 | -8.6197 | -123.7747
1827.9844 | 123.5184 | -117.1829 | 6.1935 | 0.10386 | 0.026608 | -0.0093484 | 0.055753 | -0.057894 | 0.037945 | 0.10697 | -2.1561 | 0.21973 | -2.3804 | 6.0791 | -117.2516 | 6.0425 | 6.0608 | 6.2759 | 6.3354 | -117.5674 | 114.8026 | -5.9738 | 115.0269 | 123.262 | -123.4451 | -0.38452 | 0.14191 | 0.2243 | 123.2437 | 123.4589 | -0.068665 | 117.4026 | 115.0269 | 123.5184 | 123.2254 | -0.38452 | 117.4026 | 115.0269 | 123.2254 | -0.068665 | 123.5184 | -8.5739 | -123.761
1828.9219 | 123.4955 | -117.8787 | 5.4749 | 0.042827 | 0.022336 | -0.0029404 | 0.072843 | -0.065371 | 0.025128 | 0.10484 | -2.1194 | 0.24261 | -2.449 | 5.3925 | -117.9657 | 5.3329 | 5.3467 | 5.5664 | 5.6534 | -118.2724 | 115.4297 | -5.2322 | 115.7593 | 123.2712 | -123.4406 | -0.39368 | 0.17853 | 0.32959 | 123.2254 | 123.4451 | -0.086975 | 118.1213 | 115.7593 | 123.5321 | 123.2117 | -0.39368 | 118.1213 | 115.7593 | 123.2117 | -0.086975 | 123.5321 | -7.9239 | -123.7473
1829.9844 | 123.436 | -117.8513 | 5.5344 | -0.3539 | 0.033017 | -0.055277 | 0.077116 | -0.060031 | 0.028332 | 0.097358 | -2.092 | 0.27008 | -2.4261 | 5.5939 | -117.7963 | 5.5298 | 5.3009 | 5.7404 | 5.6625 | -118.2312 | 115.4251 | -5.2643 | 115.7593 | 123.4451 | -123.3307 | -0.37994 | 0.12817 | 0.33417 | 123.1522 | 123.5916 | 0.054931 | 118.1213 | 115.7593 | 123.5138 | 123.381 | -0.37994 | 118.1213 | 115.7593 | 123.381 | 0.054931 | 123.5138 | -7.9605 | -123.7656
1830.9219 | 123.5413 | -117.7139 | 5.6442 | 0.24119 | 0.010586 | -0.026438 | 0.060026 | -0.055758 | 0.024059 | 0.10056 | -2.1103 | 0.21057 | -2.4307 | 5.5939 | -117.8192 | 5.5023 | 5.5252 | 5.7083 | 5.8365 | -118.0801 | 115.2832 | -5.4337 | 115.6036 | 123.3078 | -123.4634 | -0.36621 | 0.19226 | 0.32043 | 123.2391 | 123.4222 | -0.10529 | 117.9245 | 115.6036 | 123.5504 | 123.2162 | -0.36621 | 117.9245 | 115.6036 | 123.2162 | -0.10529 | 123.5504 | -8.075 | -123.7244
1831.9844 | 123.4772 | -117.5034 | 5.8502 | 0.48533 | 0.051175 | -0.010416 | 0.085661 | -0.064303 | 0.045422 | 0.10163 | -2.092 | 0.2655 | -2.449 | 5.896 | -117.5125 | 5.7724 | 5.7083 | 5.9784 | 6.015 | -117.8879 | 115.0543 | -5.5847 | 115.4114 | 123.3994 | -123.3627 | -0.38452 | 0.16479 | 0.35706 | 123.2117 | 123.4818 | -0.009155 | 117.7689 | 115.4114 | 123.5184 | 123.2758 | -0.38452 | 117.7689 | 115.4114 | 123.2758 | -0.009155 | 123.5184 | -8.2993 | -123.7381
1832.9219 | 123.5046 | -117.0639 | 6.2942 | 0.13438 | 0.027676 | -0.023234 | 0.068571 | -0.058962 | 0.040081 | 0.097358 | -2.0782 | 0.23346 | -2.4033 | 6.1752 | -117.1738 | 6.1752 | 6.1752 | 6.3995 | 6.4407 | -117.4301 | 114.6606 | -6.0608 | 114.9857 | 123.2391 | -123.468 | -0.36621 | 0.14649 | 0.32501 | 123.2391 | 123.4634 | -0.10986 | 117.2974 | 114.9857 | 123.5046 | 123.2391 | -0.36621 | 117.2974 | 114.9857 | 123.2391 | -0.10986 | 123.5046 | -8.6975 | -123.7244
1833.9844 | 123.5413 | -117.0731 | 6.2759 | 0.31749 | 0.031949 | -0.027506 | 0.066434 | -0.060031 | 0.043285 | 0.085609 | -2.0233 | 0.24719 | -2.3987 | 6.2073 | -117.1555 | 6.1569 | 6.1935 | 6.3583 | 6.4453 | -117.5079 | 114.6744 | -6.0287 | 115.0497 | 123.2803 | -123.4314 | -0.43488 | 0.16937 | 0.37537 | 123.2666 | 123.4314 | -0.082398 | 117.3203 | 115.0497 | 123.5184 | 123.23 | -0.43488 | 117.3203 | 115.0497 | 123.23 | -0.082398 | 123.5184 | -8.6746 | -123.7839
1834.9219 | 123.5001 | -117.16 | 6.189 | 0.042827 | 0.028744 | -0.036051 | 0.08032 | -0.062167 | 0.027264 | 0.09629 | -2.0554 | 0.24719 | -2.4033 | 6.1203 | -117.2195 | 6.0883 | 6.0654 | 6.2897 | 6.3583 | -117.5446 | 114.7568 | -5.9418 | 115.1047 | 123.2803 | -123.4085 | -0.38452 | 0.16937 | 0.3479 | 123.2254 | 123.4497 | -0.059509 | 117.4072 | 115.1047 | 123.5184 | 123.2483 | -0.38452 | 117.4072 | 115.1047 | 123.2483 | -0.059509 | 123.5184 | -8.5922 | -123.7335
1835.9844 | 123.4222 | -117.9291 | 5.5023 | 0.11912 | 0.038357 | -0.022166 | 0.096342 | -0.066439 | 0.048626 | 0.092017 | -2.1332 | 0.26093 | -2.5223 | 5.5435 | -117.8925 | 5.3925 | 5.2643 | 5.6625 | 5.6168 | -118.2999 | 115.4068 | -5.2414 | 115.7959 | 123.4726 | -123.3948 | -0.37079 | 0.11444 | 0.3891 | 123.1934 | 123.5916 | 0.036621 | 118.19 | 115.7959 | 123.5458 | 123.3215 | -0.37079 | 118.19 | 115.7959 | 123.3215 | 0.036621 | 123.5458 | -8.0246 | -123.8022
1836.9219 | 123.5092 | -117.9199 | 5.4108 | -0.41494 | 0.031949 | -0.016825 | 0.069639 | -0.057894 | 0.052898 | 0.10911 | -2.1286 | 0.18768 | -2.536 | 5.3238 | -118.0023 | 5.2597 | 5.3558 | 5.4657 | 5.5893 | -118.3365 | 115.3839 | -5.2231 | 115.7913 | 123.2437 | -123.4131 | -0.41657 | 0.17853 | 0.40741 | 123.2758 | 123.3856 | -0.082397 | 118.1076 | 115.7913 | 123.5092 | 123.1796 | -0.41657 | 118.1076 | 115.7913 | 123.1796 | -0.082397 | 123.5092 | -7.9468 | -123.7473
1837.9844 | 123.3719 | -117.6407 | 5.7861 | 0.4243 | 0.039425 | -0.028574 | 0.096342 | -0.053622 | 0.055035 | 0.097358 | -2.1469 | 0.28381 | -2.4811 | 5.896 | -117.5308 | 5.7541 | 5.5206 | 5.983 | 5.8731 | -117.984 | 115.1596 | -5.5023 | 115.4938 | 123.5367 | -123.317 | -0.34332 | 0.086975 | 0.33417 | 123.1613 | 123.6237 | 0.10986 | 117.9245 | 115.4938 | 123.5138 | 123.3948 | -0.34332 | 117.9245 | 115.4938 | 123.3948 | 0.10986 | 123.5138 | -8.2672 | -123.7701
1838.9219 | 123.4955 | -117.2287 | 6.0928 | 0.27171 | 0.023404 | -0.02537 | 0.058958 | -0.057894 | 0.039013 | 0.098426 | -2.0782 | 0.21973 | -2.4216 | 6.0196 | -117.3065 | 5.9555 | 6.0425 | 6.1752 | 6.3034 | -117.6407 | 114.8071 | -5.8731 | 115.1505 | 123.2483 | -123.3994 | -0.41199 | 0.21057 | 0.34332 | 123.2712 | 123.4039 | -0.07782 | 117.4484 | 115.1505 | 123.5321 | 123.1842 | -0.41199 | 117.4484 | 115.1505 | 123.1842 | -0.07782 | 123.5321 | -8.5144 | -123.7335
1839.9844 | 123.4589 | -116.9403 | 6.4499 | 1.0652 | 0.037289 | -0.031779 | 0.095274 | -0.053622 | 0.066784 | 0.09629 | -1.9821 | 0.30212 | -2.3209 | 6.514 | -116.9037 | 6.3538 | 6.308 | 6.633 | 6.5689 | -117.3065 | 114.6194 | -6.1478 | 114.9582 | 123.4543 | -123.3536 | -0.36621 | 0.11902 | 0.33875 | 123.2483 | 123.5733 | 0.036621 | 117.2424 | 114.9582 | 123.5092 | 123.2941 | -0.36621 | 117.2424 | 114.9582 | 123.2941 | 0.036621 | 123.5092 | -8.7708 | -123.7564
1840.9219 | 123.6603 | -117.6361 | 5.6992 | 0.4243 | 0.024472 | -0.0050764 | 0.066434 | -0.069644 | 0.036877 | 0.11124 | -2.1332 | 0.2243 | -2.5177 | 5.5847 | -117.7917 | 5.571 | 5.7083 | 5.7449 | 5.8685 | -118.0801 | 115.1184 | -5.4749 | 115.5029 | 123.2208 | -123.4909 | -0.44403 | 0.16937 | 0.38452 | 123.3444 | 123.381 | -0.15564 | 117.8604 | 115.5029 | 123.5046 | 123.2071 | -0.44403 | 117.8604 | 115.5029 | 123.2071 | -0.15564 | 123.5046 | -8.2169 | -123.7793
1841.9844 | 123.5229 | -117.421 | 5.9692 | -0.094502 | 0.046902 | -0.0093484 | 0.087797 | -0.053622 | 0.057171 | 0.10484 | -2.0874 | 0.27924 | -2.4994 | 5.7083 | -117.4667 | 5.8044 | 5.7724 | 6.1066 | 5.9189 | -117.9062 | 114.9216 | -5.69 | 115.3336 | 123.1293 | -123.436 | -0.48523 | -0.050354 | 0.41199 | 123.1934 | 123.5275 | -0.045777 | 117.7002 | 115.3336 | 123.3398 | 123.2254 | -0.48523 | 117.7002 | 115.3336 | 123.2254 | -0.045777 | 123.3398 | -8.4686 | -123.8754
1842.9219 | 123.5275 | -118.5104 | 4.7974 | 0.54637 | 0.033017 | 0.00026463 | 0.081388 | -0.051486 | 0.037945 | 0.10163 | -2.2293 | 0.23346 | -2.6093 | 4.6921 | -118.6157 | 4.6371 | 4.7699 | 4.8569 | 4.9896 | -118.9453 | 115.9012 | -4.5639 | 116.2811 | 123.2025 | -123.4131 | -0.43488 | 0.19226 | 0.37994 | 123.2803 | 123.3673 | -0.10529 | 118.7439 | 116.2811 | 123.5001 | 123.1476 | -0.43488 | 118.7439 | 116.2811 | 123.1476 | -0.10529 | 123.5001 | -7.4066 | -123.7427
1843.9844 | 123.3994 | -118.7027 | 4.6829 | 0.088604 | 0.039425 | -0.017893 | 0.088865 | -0.047213 | 0.05183 | 0.099494 | -2.179 | 0.27008 | -2.5497 | 4.7379 | -118.6432 | 4.6371 | 4.4449 | 4.8523 | 4.8157 | -119.0872 | 116.153 | -4.4128 | 116.5237 | 123.4406 | -123.3261 | -0.38452 | 0.13275 | 0.37079 | 123.1476 | 123.555 | 0.05951 | 118.9728 | 116.5237 | 123.5184 | 123.3398 | -0.38452 | 118.9728 | 116.5237 | 123.3398 | 0.05951 | 123.5184 | -7.2327 | -123.7701
1844.9219 | 123.5229 | -118.927 | 4.3762 | 0.45481 | 0.034085 | -0.029642 | 0.06323 | -0.058962 | 0.043285 | 0.1027 | -2.2018 | 0.21973 | -2.5864 | 4.216 | -119.0826 | 4.2389 | 4.3259 | 4.4357 | 4.5593 | -119.3893 | 116.3406 | -4.1565 | 116.7252 | 123.143 | -123.4589 | -0.46234 | 0.18311 | 0.38452 | 123.2529 | 123.3627 | -0.15564 | 119.1467 | 116.7252 | 123.4863 | 123.1659 | -0.46234 | 119.1467 | 116.7252 | 123.1659 | -0.15564 | 123.4863 | -6.9626 | -123.7656
1845.9219 | 123.5046 | -117.9657 | 5.3467 | 0.37852 | 0.034085 | -0.022166 | 0.056821 | -0.061099 | 0.036877 | 0.10163 | -2.1515 | 0.23346 | -2.4857 | 5.2643 | -118.0206 | 5.2277 | 5.2231 | 5.4382 | 5.5573 | -118.4006 | 115.48 | -5.1132 | 115.8142 | 123.23 | -123.3673 | -0.43488 | 0.21057 | 0.33417 | 123.1888 | 123.4039 | -0.054932 | 118.1992 | 115.8142 | 123.5229 | 123.1934 | -0.43488 | 118.1992 | 115.8142 | 123.1934 | -0.054932 | 123.5229 | -7.8323 | -123.7473
1846.9844 | 123.4314 | -118.3594 | 5.0217 | 0.073345 | 0.040494 | -0.031779 | 0.083524 | -0.046145 | 0.06358 | 0.10056 | -2.1149 | 0.28381 | -2.5131 | 5.0583 | -118.3319 | 4.9484 | 4.8065 | 5.1819 | 5.1682 | -118.7759 | 115.8463 | -4.7379 | 116.2445 | 123.4177 | -123.3536 | -0.41657 | 0.14649 | 0.39826 | 123.1659 | 123.5413 | 0.027466 | 118.6432 | 116.2445 | 123.5275 | 123.3078 | -0.41657 | 118.6432 | 116.2445 | 123.3078 | 0.027466 | 123.5275 | -7.5348 | -123.7976
1847.9219 | 123.5413 | -117.7414 | 5.5939 | 0.57688 | 0.043698 | -0.02537 | 0.064298 | -0.056826 | 0.037945 | 0.10056 | -2.1057 | 0.23346 | -2.4902 | 5.5298 | -117.7963 | 5.4794 | 5.5573 | 5.6534 | 5.8044 | -118.1763 | 115.2512 | -5.3604 | 115.6357 | 123.2712 | -123.3902 | -0.43488 | 0.21057 | 0.38452 | 123.2986 | 123.3948 | -0.054932 | 117.9749 | 115.6357 | 123.5458 | 123.2208 | -0.43488 | 117.9749 | 115.6357 | 123.2208 | -0.054932 | 123.5458 | -8.0841 | -123.7701
1848.9844 | 123.3719 | -117.6224 | 5.7816 | 0.28697 | 0.041562 | -0.018961 | 0.08032 | -0.049349 | 0.053967 | 0.10377 | -2.1835 | 0.29755 | -2.5085 | 5.8502 | -117.5217 | 5.7449 | 5.5435 | 5.9601 | 5.8914 | -118.0069 | 115.1138 | -5.484 | 115.4388 | 123.4726 | -123.3032 | -0.38452 | 0.10986 | 0.32501 | 123.1659 | 123.5825 | 0.10071 | 117.9199 | 115.4388 | 123.5138 | 123.3673 | -0.38452 | 117.9199 | 115.4388 | 123.3673 | 0.10071 | 123.5138 | -8.2901 | -123.7885
1849.9219 | 123.4451 | -118.7714 | 4.6234 | 0.36326 | 0.043698 | -0.020029 | 0.08032 | -0.060031 | 0.043285 | 0.11338 | -2.2797 | 0.27008 | -2.6276 | 4.6234 | -118.7302 | 4.5364 | 4.4495 | 4.7607 | 4.747 | -119.1605 | 116.1438 | -4.3533 | 116.4917 | 123.3948 | -123.3536 | -0.3891 | 0.1236 | 0.3479 | 123.2208 | 123.5321 | 0.041198 | 119.0414 | 116.4917 | 123.5184 | 123.3078 | -0.3891 | 119.0414 | 116.4917 | 123.3078 | 0.041198 | 123.5184 | -7.251 | -123.7839
1850.9844 | 123.4451 | -119.0231 | 4.3762 | 0.28697 | 0.04263 | -0.018961 | 0.079252 | -0.049349 | 0.043285 | 0.1027 | -2.3483 | 0.27008 | -2.6871 | 4.3442 | -119.0048 | 4.2892 | 4.2206 | 4.5364 | 4.5227 | -119.3939 | 116.3361 | -4.1061 | 116.6748 | 123.3673 | -123.381 | -0.37079 | 0.14648 | 0.33874 | 123.2437 | 123.5596 | 0.01831 | 119.2932 | 116.6748 | 123.5458 | 123.3124 | -0.37079 | 119.2932 | 116.6748 | 123.3124 | 0.01831 | 123.5458 | -7.0633 | -123.7701
1851.9219 | 123.5275 | -117.6727 | 5.6717 | 0.31749 | 0.041562 | -0.034983 | 0.062162 | -0.05469 | 0.056103 | 0.10056 | -2.1652 | 0.22888 | -2.5269 | 5.5618 | -117.7505 | 5.5161 | 5.6305 | 5.7449 | 5.8548 | -118.1213 | 115.1459 | -5.4428 | 115.5075 | 123.2346 | -123.4222 | -0.44861 | 0.1831 | 0.36163 | 123.3032 | 123.4177 | -0.07782 | 117.9016 | 115.5075 | 123.5275 | 123.1888 | -0.44861 | 117.9016 | 115.5075 | 123.1888 | -0.07782 | 123.5275 | -8.1985 | -123.793
1852.9844 | 123.4543 | -118.0115 | 5.4153 | -0.39968 | 0.041562 | -0.020029 | 0.083524 | -0.05469 | 0.057171 | 0.1059 | -2.0416 | 0.28839 | -2.4033 | 5.4153 | -117.9657 | 5.3467 | 5.1773 | 5.5664 | 5.5389 | -118.396 | 115.6082 | -5.127 | 115.9698 | 123.4268 | -123.381 | -0.38452 | 0.1236 | 0.36163 | 123.1888 | 123.5779 | 0.045777 | 118.2999 | 115.9698 | 123.5504 | 123.3582 | -0.38452 | 118.2999 | 115.9698 | 123.3582 | 0.045777 | 123.5504 | -7.8186 | -123.8113
1853.9219 | 123.5229 | -118.84 | 4.4769 | 0.47007 | 0.029812 | -0.029642 | 0.069639 | -0.060031 | 0.06358 | 0.10377 | -2.1606 | 0.21515 | -2.5543 | 4.1565 | -118.9545 | 4.3808 | 4.4449 | 4.5273 | 4.66 | -119.2978 | 116.2857 | -4.2618 | 116.6794 | 122.9965 | -123.4314 | -0.45776 | 0.1831 | 0.39368 | 123.2849 | 123.3673 | -0.11444 | 119.0552 | 116.6794 | 123.5001 | 123.2208 | -0.45776 | 119.0552 | 116.6794 | 123.2208 | -0.11444 | 123.5001 | -7.0312 | -123.7747
1854.9844 | 123.4314 | -118.3914 | 5.0217 | 0.058086 | 0.035153 | -0.0061444 | 0.093137 | -0.047213 | 0.049694 | 0.10697 | -2.0737 | 0.29297 | -2.4673 | 5.0537 | -118.3365 | 4.953 | 4.8065 | 5.1727 | 5.1544 | -118.7805 | 115.9241 | -4.7287 | 116.3177 | 123.4451 | -123.3582 | -0.3891 | 0.13275 | 0.39368 | 123.1979 | 123.5641 | 0.054931 | 118.6844 | 116.3177 | 123.5458 | 123.3444 | -0.3891 | 118.6844 | 116.3177 | 123.3444 | 0.054931 | 123.5458 | -7.489 | -123.8022
1855.9219 | 123.4085 | -118.3731 | 5.0491 | -2.4138 | 0.034085 | -0.011485 | 0.077116 | -0.051486 | 0.042217 | 0.098426 | -2.1469 | 0.28381 | -2.5131 | 4.9896 | -118.3777 | 4.9576 | 4.834 | 5.2048 | 5.1315 | -118.721 | 115.86 | -4.7653 | 116.2262 | 123.3627 | -123.4268 | -0.3479 | 0.082398 | 0.36621 | 123.2071 | 123.5779 | -0.004578 | 118.6569 | 116.2262 | 123.5046 | 123.3307 | -0.3479 | 118.6569 | 116.2262 | 123.3307 | -0.004578 | 123.5046 | -7.5623 | -123.7701
1856.9844 | 123.4406 | -117.9062 | 5.4794 | -0.0029495 | 0.037289 | -0.011485 | 0.078184 | -0.049349 | 0.05183 | 0.10697 | -1.9226 | 0.28839 | -2.417 | 5.5161 | -117.8879 | 5.3879 | 5.2826 | 5.6396 | 5.6488 | -118.3044 | 115.4892 | -5.191 | 115.9836 | 123.4222 | -123.3673 | -0.39825 | 0.16937 | 0.49439 | 123.1888 | 123.5458 | 0.018311 | 118.1946 | 115.9836 | 123.555 | 123.2941 | -0.39825 | 118.1946 | 115.9836 | 123.2941 | 0.018311 | 123.555 | -7.8964 | -123.7839
1857.9219 | 123.5138 | -118.7714 | 4.5731 | 0.22593 | 0.046902 | -0.026438 | 0.074979 | -0.049349 | 0.044354 | 0.098426 | -2.1378 | 0.25177 | -2.5085 | 4.4952 | -118.8675 | 4.422 | 4.5181 | 4.6509 | 4.7516 | -119.22 | 116.2628 | -4.3213 | 116.6336 | 123.2666 | -123.4406 | -0.44861 | 0.17853 | 0.37079 | 123.2895 | 123.4222 | -0.096131 | 119.0231 | 116.6336 | 123.5229 | 123.1934 | -0.44861 | 119.0231 | 116.6336 | 123.1934 | -0.096131 | 123.5229 | -7.0816 | -123.793
1858.9844 | 123.3948 | -118.7347 | 4.7104 | 0.088604 | 0.043698 | -0.014689 | 0.079252 | -0.053622 | 0.057171 | 0.10804 | -2.0966 | 0.27466 | -2.4353 | 4.7516 | -118.6295 | 4.6555 | 4.4449 | 4.8843 | 4.8019 | -119.0643 | 116.2994 | -4.4357 | 116.6382 | 123.4863 | -123.3398 | -0.32959 | 0.091553 | 0.33875 | 123.1796 | 123.6191 | 0.10528 | 119.0094 | 116.6382 | 123.5367 | 123.3902 | -0.32959 | 119.0094 | 116.6382 | 123.3902 | 0.10528 | 123.5367 | -7.1457 | -123.7747
1859.9219 | 123.5046 | -117.627 | 5.722 | 0.45481 | 0.045834 | -0.033915 | 0.070707 | -0.057894 | 0.062512 | 0.10804 | -2.0004 | 0.25635 | -2.3392 | 5.7037 | -117.6544 | 5.6305 | 5.6488 | 5.8182 | 5.896 | -118.0481 | 115.2878 | -5.4657 | 115.6265 | 123.3307 | -123.3765 | -0.42114 | 0.17395 | 0.33874 | 123.2758 | 123.4451 | -0.027466 | 117.8833 | 115.6265 | 123.5229 | 123.2574 | -0.42114 | 117.8833 | 115.6265 | 123.2574 | -0.027466 | 123.5229 | -8.0612 | -123.7701
1860.9844 | 123.4726 | -118.8583 | 4.541 | -0.4302 | 0.046902 | -0.0072124 | 0.085661 | -0.046145 | 0.04649 | 0.090949 | -1.9867 | 0.25635 | -2.3575 | 4.5273 | -118.8446 | 4.4449 | 4.3579 | 4.6738 | 4.6967 | -119.252 | 116.5009 | -4.2847 | 116.8716 | 123.3856 | -123.3856 | -0.39368 | 0.15564 | 0.37079 | 123.2162 | 123.5321 | 0.013733 | 119.1147 | 116.8716 | 123.555 | 123.3032 | -0.39368 | 119.1147 | 116.8716 | 123.3032 | 0.013733 | 123.555 | -6.8985 | -123.793
1861.9219 | 123.5275 | -118.9362 | 4.4083 | 0.45481 | 0.035153 | -0.0050764 | 0.064298 | -0.051486 | 0.057171 | 0.10697 | -2.0782 | 0.22888 | -2.4719 | 4.0741 | -118.9957 | 4.2984 | 4.3488 | 4.4312 | 4.5639 | -119.3619 | 116.4642 | -4.1794 | 116.8579 | 123.0103 | -123.4039 | -0.42572 | 0.15564 | 0.39368 | 123.2849 | 123.3673 | -0.05951 | 119.165 | 116.8579 | 123.5001 | 123.2346 | -0.42572 | 119.165 | 116.8579 | 123.2346 | -0.05951 | 123.5001 | -6.8802 | -123.7701
1862.9844 | 123.4726 | -118.6478 | 4.747 | -0.3539 | 0.028744 | -0.021098 | 0.076048 | -0.0376 | 0.053967 | 0.10163 | -2.0142 | 0.27466 | -2.4124 | 4.7379 | -118.6478 | 4.6463 | 4.5456 | 4.866 | 4.8706 | -119.0781 | 116.2354 | -4.4724 | 116.6336 | 123.3856 | -123.3948 | -0.4303 | 0.1236 | 0.39826 | 123.1934 | 123.5138 | 0 | 118.9224 | 116.6336 | 123.5184 | 123.2941 | -0.4303 | 118.9224 | 116.6336 | 123.2941 | 0 | 123.5184 | -7.1594 | -123.8251
1863.9219 | 123.3719 | -117.7185 | 5.6946 | 0.31749 | 0.046902 | -0.015757 | 0.08032 | -0.055758 | 0.060375 | 0.10484 | -2.0599 | 0.27466 | -2.3849 | 5.8411 | -117.5446 | 5.6854 | 5.4062 | 5.8868 | 5.8594 | -118.0481 | 115.3336 | -5.4199 | 115.6586 | 123.5596 | -123.2391 | -0.32959 | 0.16479 | 0.32501 | 123.1247 | 123.6053 | 0.17395 | 117.9932 | 115.6586 | 123.5779 | 123.4039 | -0.32959 | 117.9932 | 115.6586 | 123.4039 | 0.17395 | 123.5779 | -8.0795 | -123.7427
1864.9844 | 123.4268 | -117.6956 | 5.7358 | -0.079243 | 0.049038 | -0.0072124 | 0.088865 | -0.050418 | 0.058239 | 0.1027 | -1.8173 | 0.28381 | -2.3575 | 5.7587 | -117.6544 | 5.6488 | 5.5435 | 5.8685 | 5.9097 | -118.0801 | 115.3381 | -5.452 | 115.8783 | 123.4543 | -123.3902 | -0.38452 | 0.17395 | 0.54016 | 123.2391 | 123.5641 | 0.041199 | 117.9794 | 115.8783 | 123.6053 | 123.3444 | -0.38452 | 117.9794 | 115.8783 | 123.3444 | 0.041199 | 123.6053 | -8.0933 | -123.8159
1865.9219 | 123.4406 | -118.1442 | 5.2734 | 0.36326 | 0.037289 | 0.0077416 | 0.076048 | -0.047213 | 0.053967 | 0.09629 | -2.0462 | 0.2655 | -2.4124 | 5.2689 | -118.0939 | 5.1865 | 5.1041 | 5.4108 | 5.4199 | -118.5059 | 115.7318 | -5.0079 | 116.098 | 123.4131 | -123.3673 | -0.36163 | 0.14648 | 0.36621 | 123.2483 | 123.555 | 0.050354 | 118.4097 | 116.098 | 123.5641 | 123.3307 | -0.36163 | 118.4097 | 116.098 | 123.3307 | 0.050354 | 123.5641 | -7.6859 | -123.7793
1866.9844 | 123.4589 | -118.309 | 5.0858 | -0.23183 | 0.037289 | -0.012553 | 0.088865 | -0.05469 | 0.049694 | 0.10911 | -2.0096 | 0.27008 | -2.3941 | 5.0858 | -118.2999 | 4.9988 | 4.8935 | 5.2368 | 5.2597 | -118.7027 | 115.9149 | -4.8157 | 116.2994 | 123.3948 | -123.3856 | -0.39368 | 0.17395 | 0.38452 | 123.2025 | 123.5458 | 0.009155 | 118.5791 | 116.2994 | 123.5687 | 123.3078 | -0.39368 | 118.5791 | 116.2994 | 123.3078 | 0.009155 | 123.5687 | -7.4799 | -123.7885
1867.9219 | 123.4131 | -117.4667 | 5.928 | 2.2248 | 0.041562 | -0.011485 | 0.074979 | -0.042941 | 0.057171 | 0.09629 | -1.9363 | 0.29297 | -2.3575 | 5.9509 | -117.4255 | 5.8777 | 5.7037 | 6.0974 | 6.0333 | -117.8696 | 115.1093 | -5.6351 | 115.5304 | 123.4177 | -123.3536 | -0.40283 | 0.10528 | 0.42114 | 123.1705 | 123.5641 | 0.041199 | 117.7597 | 115.5304 | 123.5001 | 123.3444 | -0.40283 | 117.7597 | 115.5304 | 123.3444 | 0.041199 | 123.5001 | -8.2855 | -123.7976
1868.9844 | 123.4772 | -118.1854 | 5.1956 | -0.24709 | 0.043698 | -0.026438 | 0.079252 | -0.046145 | 0.048626 | 0.097358 | -1.973 | 0.27008 | -2.3529 | 5.1865 | -118.2083 | 5.1041 | 4.9622 | 5.3558 | 5.3329 | -118.5791 | 115.8325 | -4.9255 | 116.2125 | 123.3719 | -123.4039 | -0.39368 | 0.13733 | 0.37994 | 123.1476 | 123.5413 | -0.022888 | 118.4555 | 116.2125 | 123.5184 | 123.2895 | -0.39368 | 118.4555 | 116.2125 | 123.2895 | -0.022888 | 123.5184 | -7.5485 | -123.7747
1869.9219 | 123.3902 | -117.2745 | 6.1386 | 0.36326 | 0.046902 | -0.0018714 | 0.085661 | -0.05469 | 0.056103 | 0.10911 | -2.037 | 0.27008 | -2.3849 | 6.1615 | -117.5308 | 6.0516 | 6.0379 | 6.2988 | 6.2164 | -117.6773 | 114.8895 | -5.8685 | 115.2374 | 123.436 | -123.6694 | -0.40283 | 0.07782 | 0.3479 | 123.3124 | 123.5733 | -0.25635 | 117.5446 | 115.2374 | 123.4909 | 123.3261 | -0.40283 | 117.5446 | 115.2374 | 123.3261 | -0.25635 | 123.4909 | -8.5236 | -123.8159
1870.9844 | 123.4406 | -117.3569 | 6.0654 | -0.23183 | 0.045834 | -0.0018714 | 0.071775 | -0.046145 | 0.055035 | 0.098426 | -1.9775 | 0.28839 | -2.3712 | 6.0562 | -117.3386 | 5.9647 | 5.8594 | 6.1981 | 6.1981 | -117.7368 | 114.9857 | -5.777 | 115.3793 | 123.4131 | -123.4039 | -0.37994 | 0.13275 | 0.39368 | 123.2162 | 123.555 | 0.018311 | 117.6453 | 115.3793 | 123.555 | 123.3215 | -0.37994 | 117.6453 | 115.3793 | 123.3215 | 0.018311 | 123.555 | -8.4366 | -123.8022
1871.9219 | 123.4406 | -117.9291 | 5.4474 | 0.058086 | 0.041562 | 0.0056046 | 0.074979 | -0.041873 | 0.053967 | 0.11018 | -2.0554 | 0.28839 | -2.4261 | 5.4199 | -117.9382 | 5.3604 | 5.278 | 5.6488 | 5.603 | -118.3182 | 115.5029 | -5.159 | 115.8737 | 123.349 | -123.3856 | -0.3891 | 0.15564 | 0.37079 | 123.2071 | 123.5779 | -0.009155 | 118.2175 | 115.8737 | 123.5321 | 123.2895 | -0.3891 | 118.2175 | 115.8737 | 123.2895 | -0.009155 | 123.5321 | -7.8735 | -123.7656
1872.9844 | 123.4314 | -117.2653 | 6.1523 | 2.2401 | 0.041562 | -0.011485 | 0.074979 | -0.05469 | 0.055035 | 0.1027 | -1.8356 | 0.32044 | -2.2293 | 6.1707 | -117.215 | 6.1066 | 5.9052 | 6.34 | 6.2759 | -117.6407 | 115.036 | -5.8319 | 115.4297 | 123.436 | -123.3673 | -0.37537 | 0.1236 | 0.39368 | 123.1705 | 123.6053 | 0.050354 | 117.5858 | 115.4297 | 123.5413 | 123.3719 | -0.37537 | 117.5858 | 115.4297 | 123.3719 | 0.050354 | 123.5413 | -8.3817 | -123.793
1873.9219 | 123.4268 | -117.3935 | 5.9509 | -3.2378 | 0.037289 | -0.020029 | 0.087797 | -0.052554 | 0.058239 | 0.098426 | -2.0187 | 0.29297 | -2.3666 | 6.015 | -117.3843 | 5.9418 | 5.777 | 6.1478 | 6.0974 | -117.8101 | 115.0269 | -5.658 | 115.3748 | 123.4085 | -123.3353 | -0.41656 | 0.14648 | 0.3479 | 123.1705 | 123.5413 | 0.009156 | 117.6865 | 115.3748 | 123.4909 | 123.3353 | -0.41656 | 117.6865 | 115.3748 | 123.3353 | 0.009156 | 123.4909 | -8.3176 | -123.761
1874.9844 | 123.4634 | -118.0527 | 5.3741 | -0.30813 | 0.022336 | -0.018961 | 0.078184 | -0.045077 | 0.053967 | 0.10804 | -1.9913 | 0.27924 | -2.3849 | 5.3604 | -118.0206 | 5.3101 | 5.1498 | 5.5252 | 5.5206 | -118.428 | 115.6677 | -5.0949 | 116.0614 | 123.4131 | -123.3948 | -0.37537 | 0.14648 | 0.39368 | 123.2025 | 123.5779 | 0.032043 | 118.3319 | 116.0614 | 123.5733 | 123.3627 | -0.37537 | 118.3319 | 116.0614 | 123.3627 | 0.032043 | 123.5733 | -7.7591 | -123.8022
1875.9219 | 123.3719 | -117.8146 | 5.6122 | 0.21067 | 0.043698 | -0.023234 | 0.072843 | -0.046145 | 0.050762 | 0.098426 | -2.0187 | 0.26093 | -2.3758 | 5.6671 | -117.7231 | 5.5801 | 5.3604 | 5.8136 | 5.7358 | -118.158 | 115.4388 | -5.3513 | 115.7959 | 123.4817 | -123.3353 | -0.34332 | 0.1236 | 0.35705 | 123.175 | 123.6282 | 0.091553 | 118.0756 | 115.7959 | 123.5504 | 123.3948 | -0.34332 | 118.0756 | 115.7959 | 123.3948 | 0.091553 | 123.5504 | -7.988 | -123.7701
1876.9844 | 123.4268 | -117.8604 | 5.5756 | -0.21657 | 0.044766 | -0.02537 | 0.081388 | -0.048281 | 0.043285 | 0.098426 | -1.9638 | 0.28839 | -2.3117 | 5.5573 | -117.8329 | 5.4886 | 5.3192 | 5.7587 | 5.6808 | -118.2129 | 115.5487 | -5.2872 | 115.8966 | 123.4177 | -123.4085 | -0.35248 | 0.10529 | 0.3479 | 123.1796 | 123.6191 | 0.027466 | 118.1488 | 115.8966 | 123.5413 | 123.349 | -0.35248 | 118.1488 | 115.8966 | 123.349 | 0.027466 | 123.5413 | -7.8873 | -123.7885
1877.9219 | 123.4451 | -117.7414 | 5.658 | 0.43956 | 0.037289 | 0.0056046 | 0.069639 | -0.042941 | 0.055035 | 0.11552 | -2.005 | 0.27924 | -2.3575 | 5.7541 | -117.7231 | 5.5664 | 5.5618 | 5.8456 | 5.8319 | -118.1351 | 115.3839 | -5.3787 | 115.7364 | 123.4955 | -123.381 | -0.39368 | 0.17395 | 0.35248 | 123.3032 | 123.587 | 0.018311 | 118.0206 | 115.7364 | 123.5733 | 123.3078 | -0.39368 | 118.0206 | 115.7364 | 123.3078 | 0.018311 | 123.5733 | -8.0154 | -123.793
1878.9844 | 123.436 | -117.659 | 5.7358 | -0.14028 | 0.035153 | -0.014689 | 0.079252 | -0.046145 | 0.058239 | 0.098426 | -1.9135 | 0.27466 | -2.3026 | 5.722 | -117.6544 | 5.6351 | 5.5298 | 5.8731 | 5.8594 | -118.0801 | 115.3564 | -5.4611 | 115.7455 | 123.381 | -123.3902 | -0.42114 | 0.1236 | 0.3891 | 123.1888 | 123.5321 | 0.004578 | 117.9337 | 115.7455 | 123.5184 | 123.2941 | -0.42114 | 117.9337 | 115.7455 | 123.2941 | 0.004578 | 123.5184 | -8.0383 | -123.8159
1879.9219 | 123.4222 | -116.7709 | 6.6284 | -1.6204 | 0.035153 | -0.021098 | 0.082456 | -0.048281 | 0.055035 | 0.084541 | -1.9638 | 0.29297 | -2.3026 | 6.6605 | -116.7297 | 6.5826 | 6.4545 | 6.8069 | 6.7749 | -117.1326 | 114.4684 | -6.3354 | 114.8071 | 123.4314 | -123.3582 | -0.36163 | 0.14648 | 0.33874 | 123.2254 | 123.5779 | 0.041199 | 117.0639 | 114.8071 | 123.5458 | 123.3536 | -0.36163 | 117.0639 | 114.8071 | 123.3536 | 0.041199 | 123.5458 | -8.931 | -123.761
1880.9844 | 123.4131 | -117.2882 | 6.1523 | -0.41494 | 0.044766 | -0.033915 | 0.086729 | -0.046145 | 0.040081 | 0.099494 | -1.8539 | 0.27924 | -2.179 | 6.2073 | -117.2928 | 6.0883 | 5.928 | 6.3126 | 6.2714 | -117.6727 | 115.1093 | -5.8731 | 115.4343 | 123.4955 | -123.4451 | -0.38452 | 0.11902 | 0.32501 | 123.2162 | 123.6008 | -0.004578 | 117.5674 | 115.4343 | 123.5596 | 123.3765 | -0.38452 | 117.5674 | 115.4343 | 123.3765 | -0.004578 | 123.5596 | -8.3313 | -123.8251
1881.9219 | 123.4177 | -117.4896 | 5.9097 | 0.50059 | 0.041562 | -0.017893 | 0.076048 | -0.055758 | 0.043285 | 0.10484 | -1.5289 | 0.26093 | -1.9135 | 5.896 | -117.4942 | 5.8777 | 5.6854 | 6.0471 | 6.0425 | -117.9016 | 115.5762 | -5.6488 | 115.9607 | 123.3856 | -123.4039 | -0.41199 | 0.13275 | 0.38452 | 123.175 | 123.5367 | -0.004578 | 117.7505 | 115.9607 | 123.5321 | 123.3673 | -0.41199 | 117.7505 | 115.9607 | 123.3673 | -0.004578 | 123.5321 | -7.8232 | -123.8113
1882.9844 | 123.4222 | -117.0822 | 6.3126 | -0.033467 | 0.037289 | -0.0082804 | 0.084592 | -0.048281 | 0.052898 | 0.1027 | -1.442 | 0.27466 | -1.8677 | 6.2393 | -117.1783 | 6.0654 | 5.9647 | 6.4316 | 6.3629 | -117.5308 | 115.2145 | -6.0379 | 115.6403 | 123.3215 | -123.4909 | -0.44861 | 0.050354 | 0.42572 | 123.0469 | 123.5138 | -0.096131 | 117.3569 | 115.6403 | 123.4451 | 123.1476 | -0.44861 | 117.3569 | 115.6403 | 123.1476 | -0.096131 | 123.4451 | -8.1802 | -123.8434
1883.9219 | 123.4177 | -117.9428 | 5.4794 | 0.31749 | 0.044766 | -0.011485 | 0.078184 | -0.049349 | 0.06892 | 0.11552 | -1.6205 | 0.28839 | -1.9775 | 5.484 | -117.8879 | 5.4108 | 5.2322 | 5.658 | 5.603 | -118.3273 | 115.9653 | -5.191 | 116.3223 | 123.4268 | -123.3673 | -0.38452 | 0.1236 | 0.35706 | 123.175 | 123.6008 | 0.054932 | 118.2312 | 116.3223 | 123.5458 | 123.3536 | -0.38452 | 118.2312 | 116.3223 | 123.3536 | 0.054932 | 123.5458 | -7.457 | -123.8068
1884.9844 | 123.4726 | -117.2836 | 6.0837 | -0.32338 | 0.044766 | -0.021098 | 0.08032 | -0.050418 | 0.047558 | 0.11124 | -1.4786 | 0.27924 | -1.886 | 6.0654 | -117.3019 | 6.0059 | 5.9052 | 6.2164 | 6.2256 | -117.7139 | 115.3976 | -5.8044 | 115.8051 | 123.349 | -123.3856 | -0.4303 | 0.14191 | 0.40741 | 123.1888 | 123.5001 | -0.018311 | 117.5629 | 115.8051 | 123.5092 | 123.2895 | -0.4303 | 117.5629 | 115.8051 | 123.2895 | -0.018311 | 123.5092 | -7.9697 | -123.7976
1885.9219 | 123.5046 | -117.2745 | 6.0379 | 0.47007 | 0.044766 | 0.00026463 | 0.074979 | -0.047213 | 0.050762 | 0.10056 | -1.5427 | 0.25177 | -1.918 | 5.983 | -117.3615 | 5.9006 | 5.9463 | 6.1432 | 6.2119 | -117.7414 | 115.3564 | -5.7861 | 115.7318 | 123.2574 | -123.3994 | -0.46692 | 0.17395 | 0.37537 | 123.2208 | 123.4177 | -0.086975 | 117.5262 | 115.7318 | 123.4863 | 123.175 | -0.46692 | 117.5262 | 115.7318 | 123.175 | -0.086975 | 123.4863 | -7.9559 | -123.7793
1886.9844 | 123.4222 | -117.746 | 5.6717 | -0.38442 | 0.035153 | -0.023234 | 0.061094 | -0.042941 | 0.052898 | 0.10697 | -1.506 | 0.28381 | -1.8677 | 5.6396 | -117.5949 | 5.6442 | 5.365 | 5.8502 | 5.8456 | -118.1396 | 115.8783 | -5.3879 | 116.2399 | 123.3856 | -123.2666 | -0.39368 | 0.17395 | 0.36163 | 123.111 | 123.5962 | 0.15106 | 118.0298 | 116.2399 | 123.5916 | 123.3902 | -0.39368 | 118.0298 | 116.2399 | 123.3902 | 0.15106 | 123.5916 | -7.5394 | -123.8113
1887.9219 | 123.3856 | -117.572 | 5.8182 | 0.31749 | 0.049038 | -0.0093484 | 0.086729 | -0.044009 | 0.060375 | 0.11872 | -1.9638 | 0.29297 | -2.33 | 5.6946 | -117.6086 | 5.8273 | 5.6351 | 5.9052 | 5.9601 | -117.9932 | 115.242 | -5.5252 | 115.6082 | 123.2666 | -123.4268 | -0.42114 | 0.14191 | 0.36621 | 123.2071 | 123.4772 | -0.036622 | 117.865 | 115.6082 | 123.5321 | 123.3994 | -0.42114 | 117.865 | 115.6082 | 123.3994 | -0.036622 | 123.5321 | -8.1482 | -123.8113
1888.9844 | 123.4085 | -117.3615 | 6.0745 | 0.19541 | 0.049038 | -0.013621 | 0.079252 | -0.061099 | 0.056103 | 0.11231 | -1.9501 | 0.27924 | -2.2751 | 6.1661 | -117.2241 | 6.0516 | 5.809 | 6.2805 | 6.2119 | -117.7002 | 115.0864 | -5.7953 | 115.4114 | 123.5275 | -123.2986 | -0.33874 | 0.13733 | 0.32501 | 123.1705 | 123.642 | 0.13733 | 117.6407 | 115.4114 | 123.5733 | 123.4131 | -0.33874 | 117.6407 | 115.4114 | 123.4131 | 0.13733 | 123.5733 | -8.3496 | -123.7747
1889.9219 | 123.3948 | -118.1763 | 5.2231 | 0.088604 | 0.04263 | -0.020029 | 0.078184 | -0.046145 | 0.065716 | 0.099494 | -1.9867 | 0.25635 | -2.3575 | 5.2551 | -118.0847 | 5.1865 | 4.9622 | 5.397 | 5.3421 | -118.5654 | 115.8188 | -4.9667 | 116.1896 | 123.4314 | -123.3078 | -0.3891 | 0.11902 | 0.37079 | 123.1384 | 123.5733 | 0.091553 | 118.4326 | 116.1896 | 123.5184 | 123.3627 | -0.3891 | 118.4326 | 116.1896 | 123.3627 | 0.091553 | 123.5184 | -7.5806 | -123.7885
1890.9688 | 123.4085 | -117.2791 | 6.0928 | -0.29287 | 0.029812 | -0.022166 | 0.05789 | -0.049349 | 0.034741 | 0.1059 | -1.9867 | 0.27466 | -2.3117 | 6.308 | -117.3386 | 6.015 | 5.9143 | 6.2988 | 6.2622 | -117.6682 | 114.9673 | -5.8182 | 115.2924 | 123.587 | -123.4314 | -0.3891 | 0.16937 | 0.32501 | 123.1934 | 123.5779 | -0.059509 | 117.5537 | 115.2924 | 123.5413 | 123.2941 | -0.3891 | 117.5537 | 115.2924 | 123.2941 | -0.059509 | 123.5413 | -8.4045 | -123.761
1891.9219 | 123.4863 | -117.3157 | 6.0791 | 0.45481 | 0.037289 | -0.027506 | 0.071775 | -0.049349 | 0.043285 | 0.094154 | -2.0004 | 0.26093 | -2.3666 | 5.8365 | -117.334 | 5.9738 | 5.9784 | 6.1752 | 6.1752 | -117.746 | 114.949 | -5.8182 | 115.3152 | 123.1522 | -123.4131 | -0.4303 | 0.09613 | 0.36621 | 123.2941 | 123.4909 | -0.01831 | 117.5766 | 115.3152 | 123.4909 | 123.2895 | -0.4303 | 117.5766 | 115.3152 | 123.2895 | -0.01831 | 123.4909 | -8.4457 | -123.8251
1892.9844 | 123.4451 | -117.6041 | 5.8044 | -0.23183 | 0.050107 | -0.026438 | 0.076048 | -0.049349 | 0.04649 | 0.09629 | -1.8723 | 0.27008 | -2.2614 | 5.7999 | -117.5766 | 5.7129 | 5.603 | 5.9418 | 5.9509 | -118.0069 | 115.3427 | -5.5344 | 115.7318 | 123.4039 | -123.381 | -0.40283 | 0.14649 | 0.3891 | 123.2071 | 123.5458 | 0.027466 | 117.8741 | 115.7318 | 123.555 | 123.317 | -0.40283 | 117.8741 | 115.7318 | 123.317 | 0.027466 | 123.555 | -8.0658 | -123.8113
1893.9219 | 123.436 | -118.2632 | 5.1498 | 0.40904 | 0.040494 | -0.012553 | 0.06323 | -0.039736 | 0.056103 | 0.10163 | -2.0416 | 0.29297 | -2.3849 | 5.2322 | -118.0984 | 5.0583 | 4.8431 | 5.365 | 5.3055 | -118.6295 | 115.8783 | -4.8569 | 116.2216 | 123.4955 | -123.2483 | -0.36621 | 0.15564 | 0.34332 | 123.1064 | 123.6282 | 0.16479 | 118.5562 | 116.2216 | 123.5687 | 123.3215 | -0.36621 | 118.5562 | 116.2216 | 123.3215 | 0.16479 | 123.5687 | -7.5348 | -123.7793
1894.9844 | 123.4451 | -117.8375 | 5.571 | -0.24709 | 0.039425 | -0.015757 | 0.069639 | -0.039736 | 0.052898 | 0.098426 | -1.9363 | 0.27466 | -2.2888 | 5.5893 | -117.8146 | 5.5161 | 5.3238 | 5.7541 | 5.7266 | -118.2037 | 115.5487 | -5.2963 | 115.9012 | 123.4268 | -123.3856 | -0.36621 | 0.15564 | 0.35248 | 123.1613 | 123.5916 | 0.022888 | 118.1122 | 115.9012 | 123.5641 | 123.3536 | -0.36621 | 118.1122 | 115.9012 | 123.3536 | 0.022888 | 123.5641 | -7.8598 | -123.7747
1895.9219 | 123.3398 | -117.0502 | 6.3721 | 0.348 | 0.037289 | -0.014689 | 0.078184 | -0.042941 | 0.045422 | 0.10911 | -1.9318 | 0.27466 | -2.2888 | 6.3721 | -117.009 | 6.4362 | 6.2759 | 6.3995 | 6.4728 | -117.4118 | 114.7614 | -6.0974 | 115.1184 | 123.4222 | -123.381 | -0.36163 | 0.10071 | 0.35706 | 123.3261 | 123.4497 | 0.041199 | 117.3248 | 115.1184 | 123.5229 | 123.4863 | -0.36163 | 117.3248 | 115.1184 | 123.4863 | 0.041199 | 123.5229 | -8.6609 | -123.7839
1896.9688 | 123.5001 | -116.8442 | 6.4728 | -1.1474 | 0.028744 | -0.017893 | 0.058958 | -0.048281 | 0.032604 | 0.11018 | -1.8448 | 0.21515 | -2.1927 | 6.3538 | -116.9815 | 6.3492 | 6.3766 | 6.5598 | 6.6559 | -117.334 | 114.6515 | -6.2576 | 114.9994 | 123.1979 | -123.4543 | -0.48981 | 0.18311 | 0.3479 | 123.2208 | 123.4039 | -0.13733 | 117.0593 | 114.9994 | 123.5001 | 123.1934 | -0.48981 | 117.0593 | 114.9994 | 123.1934 | -0.13733 | 123.5001 | -8.6655 | -123.8068
1897.9219 | 123.3902 | -116.9632 | 6.4728 | 0.21067 | 0.046902 | -0.013621 | 0.088865 | -0.05469 | 0.059307 | 0.093085 | -1.9135 | 0.2655 | -2.2751 | 6.5094 | -116.9174 | 6.4133 | 6.189 | 6.6513 | 6.5598 | -117.3523 | 114.6881 | -6.2073 | 115.0497 | 123.4726 | -123.3902 | -0.3891 | 0.086975 | 0.36163 | 123.1522 | 123.6145 | 0.045777 | 117.2287 | 115.0497 | 123.5229 | 123.3765 | -0.3891 | 117.2287 | 115.0497 | 123.3765 | 0.045777 | 123.5229 | -8.7479 | -123.8251
1898.9844 | 123.4451 | -116.9815 | 6.4178 | -0.26235 | 0.043698 | -0.044596 | 0.085661 | -0.050418 | 0.050762 | 0.097358 | -1.7944 | 0.2655 | -2.1881 | 6.4041 | -116.9769 | 6.308 | 6.1798 | 6.5369 | 6.546 | -117.3843 | 114.7934 | -6.1523 | 115.1871 | 123.3856 | -123.3948 | -0.40283 | 0.12817 | 0.39368 | 123.1613 | 123.5184 | 0.004577 | 117.247 | 115.1871 | 123.5275 | 123.2895 | -0.40283 | 117.247 | 115.1871 | 123.2895 | 0.004577 | 123.5275 | -8.606 | -123.8022
1899.9219 | 123.5092 | -116.8854 | 6.459 | 0.43956 | 0.04263 | -0.010416 | 0.071775 | -0.064303 | 0.058239 | 0.099494 | -1.8723 | 0.24719 | -2.2568 | 6.4041 | -116.8625 | 6.3492 | 6.3995 | 6.5277 | 6.6559 | -117.3019 | 114.6286 | -6.2119 | 115.0131 | 123.2895 | -123.3215 | -0.41657 | 0.19684 | 0.38452 | 123.2849 | 123.4131 | 0.022888 | 117.1326 | 115.0131 | 123.5413 | 123.2346 | -0.41657 | 117.1326 | 115.0131 | 123.2346 | 0.022888 | 123.5413 | -8.7158 | -123.761
1900.9844 | 123.5275 | -117.5537 | 5.7587 | 1.2788 | 0.037289 | -0.0093484 | 0.058958 | -0.056826 | 0.043285 | 0.10163 | -2.0279 | 0.23346 | -2.3758 | 5.6671 | -117.6727 | 5.5893 | 5.7129 | 5.8228 | 5.9463 | -117.9977 | 115.1779 | -5.5252 | 115.5258 | 123.2208 | -123.4314 | -0.44403 | 0.18768 | 0.3479 | 123.2666 | 123.3765 | -0.11902 | 117.7872 | 115.5258 | 123.5001 | 123.143 | -0.44403 | 117.7872 | 115.5258 | 123.143 | -0.11902 | 123.5001 | -8.1345 | -123.7564
1901.9219 | 123.436 | -117.6865 | 5.7083 | 0.19541 | 0.036221 | -0.011485 | 0.077116 | -0.053622 | 0.048626 | 0.099494 | -2.0462 | 0.29297 | -2.3895 | 5.7358 | -117.6361 | 5.6442 | 5.5389 | 5.8868 | 5.8548 | -118.0847 | 115.2969 | -5.4153 | 115.6403 | 123.4222 | -123.3444 | -0.39825 | 0.14648 | 0.34332 | 123.2254 | 123.5733 | 0.050354 | 117.9794 | 115.6403 | 123.5413 | 123.3307 | -0.39825 | 117.9794 | 115.6403 | 123.3307 | 0.050354 | 123.5413 | -8.0978 | -123.793
1902.9844 | 123.4131 | -117.6682 | 5.7678 | 0.43956 | 0.036221 | -0.044596 | 0.078184 | -0.056826 | 0.049694 | 0.094154 | -1.973 | 0.31586 | -2.3026 | 5.7678 | -117.6178 | 5.7129 | 5.5069 | 5.9463 | 5.9235 | -118.0298 | 115.3656 | -5.452 | 115.6952 | 123.436 | -123.3856 | -0.36163 | 0.15564 | 0.32959 | 123.175 | 123.6145 | 0.050354 | 117.984 | 115.6952 | 123.5916 | 123.381 | -0.36163 | 117.984 | 115.6952 | 123.381 | 0.050354 | 123.5916 | -8.0704 | -123.7976
1903.9219 | 123.4131 | -117.5034 | 5.9463 | 0.43956 | 0.038357 | -0.026438 | 0.086729 | -0.049349 | 0.055035 | 0.097358 | -1.973 | 0.28381 | -2.3483 | 5.9601 | -117.4118 | 5.8914 | 5.6854 | 6.1157 | 6.0516 | -117.8421 | 115.155 | -5.6625 | 115.5304 | 123.4634 | -123.3582 | -0.33875 | 0.10529 | 0.37537 | 123.1888 | 123.6191 | 0.091553 | 117.7872 | 115.5304 | 123.555 | 123.3948 | -0.33875 | 117.7872 | 115.5304 | 123.3948 | 0.091553 | 123.555 | -8.2947 | -123.7885
1904.9844 | 123.4451 | -116.89 | 6.514 | -0.30813 | 0.045834 | -0.022166 | 0.076048 | -0.049349 | 0.05183 | 0.092017 | -1.8265 | 0.27924 | -2.2247 | 6.5186 | -116.8808 | 6.4407 | 6.3171 | 6.6605 | 6.6559 | -117.2836 | 114.6652 | -6.2347 | 115.0635 | 123.4085 | -123.3948 | -0.39368 | 0.14191 | 0.39825 | 123.2071 | 123.5504 | 0.009156 | 117.1692 | 115.0635 | 123.5458 | 123.3307 | -0.39368 | 117.1692 | 115.0635 | 123.3307 | 0.009156 | 123.5458 | -8.7387 | -123.7976
1905.9219 | 123.5504 | -116.7618 | 6.5735 | -0.29287 | 0.02554 | -0.038187 | 0.058958 | -0.056826 | 0.022991 | 0.10163 | -1.8448 | 0.22888 | -2.2156 | 6.427 | -116.9174 | 6.395 | 6.5186 | 6.6238 | 6.7657 | -117.2058 | 114.5462 | -6.3446 | 114.917 | 123.1888 | -123.4909 | -0.44403 | 0.19226 | 0.37079 | 123.2803 | 123.3856 | -0.15564 | 116.9907 | 114.917 | 123.5275 | 123.1567 | -0.44403 | 116.9907 | 114.917 | 123.1567 | -0.15564 | 123.5275 | -8.7891 | -123.7793
1906.9844 | 123.4634 | -117.4164 | 5.9784 | -0.094502 | 0.044766 | -0.011485 | 0.08032 | -0.048281 | 0.062512 | 0.098426 | -1.8677 | 0.27466 | -2.2888 | 5.9738 | -117.4072 | 5.8594 | 5.7816 | 6.102 | 6.1157 | -117.8558 | 115.1276 | -5.7037 | 115.5487 | 123.3902 | -123.3856 | -0.43945 | 0.13733 | 0.42114 | 123.1979 | 123.5184 | 0.009155 | 117.691 | 115.5487 | 123.5321 | 123.2758 | -0.43945 | 117.691 | 115.5487 | 123.2758 | 0.009155 | 123.5321 | -8.2672 | -123.8342
1907.9219 | 123.468 | -117.3706 | 5.9967 | 0.48533 | 0.045834 | -0.015757 | 0.061094 | -0.064303 | 0.048626 | 0.1059 | -1.9318 | 0.22888 | -2.3026 | 5.9509 | -117.3889 | 5.8914 | 6.0059 | 6.1111 | 6.2531 | -117.7368 | 115.0681 | -5.7678 | 115.4388 | 123.3215 | -123.3856 | -0.36621 | 0.25635 | 0.37079 | 123.3765 | 123.4817 | -0.018311 | 117.5995 | 115.4388 | 123.6237 | 123.262 | -0.36621 | 117.5995 | 115.4388 | 123.262 | -0.018311 | 123.6237 | -8.2993 | -123.7335
1908.9844 | 123.4543 | -116.272 | 7.1228 | -0.33864 | 0.039425 | -0.0093484 | 0.081388 | -0.049349 | 0.061443 | 0.099494 | -1.7532 | 0.25635 | -2.1469 | 7.1457 | -116.2766 | 7.0267 | 6.9077 | 7.2876 | 7.2647 | -116.6748 | 114.1251 | -6.8665 | 114.5187 | 123.4177 | -123.3994 | -0.40283 | 0.14191 | 0.39368 | 123.1796 | 123.5596 | -0.004577 | 116.5283 | 114.5187 | 123.5367 | 123.2986 | -0.40283 | 116.5283 | 114.5187 | 123.2986 | -0.004577 | 123.5367 | -9.2697 | -123.7976
1909.9219 | 123.4955 | -115.9103 | 7.4249 | 0.40904 | 0.03088 | -0.0018714 | 0.068571 | -0.051486 | 0.044354 | 0.11338 | -1.7807 | 0.21057 | -2.1423 | 7.3288 | -116.0202 | 7.2739 | 7.37 | 7.4936 | 7.608 | -116.3635 | 113.768 | -7.2144 | 114.1296 | 123.2391 | -123.4451 | -0.45319 | 0.1831 | 0.36163 | 123.2803 | 123.4039 | -0.10986 | 116.1209 | 114.1296 | 123.5184 | 123.1842 | -0.45319 | 116.1209 | 114.1296 | 123.1842 | -0.10986 | 123.5184 | -9.5673 | -123.7885
1910.9844 | 123.5001 | -116.0934 | 7.2327 | 0.36326 | 0.034085 | -0.028574 | 0.055753 | -0.062167 | 0.035809 | 0.10377 | -1.8448 | 0.22888 | -2.2202 | 7.1548 | -116.1758 | 7.1091 | 7.1823 | 7.338 | 7.4341 | -116.5466 | 113.8733 | -7.0038 | 114.2487 | 123.2483 | -123.4085 | -0.45319 | 0.20142 | 0.37537 | 123.2758 | 123.4314 | -0.082397 | 116.3223 | 114.2487 | 123.5275 | 123.2025 | -0.45319 | 116.3223 | 114.2487 | 123.2025 | -0.082397 | 123.5275 | -9.4528 | -123.7793
1911.9219 | 123.5092 | -115.9836 | 7.3883 | 0.47007 | 0.038357 | -0.032847 | 0.094205 | -0.066439 | 0.060375 | 0.092017 | -1.8219 | 0.25635 | -2.2018 | 7.4066 | -116.0019 | 7.2968 | 7.3105 | 7.5165 | 7.5577 | -116.3864 | 113.7817 | -7.132 | 114.1617 | 123.3902 | -123.3902 | -0.40283 | 0.16937 | 0.37994 | 123.2941 | 123.5001 | -0.01831 | 116.2399 | 114.1617 | 123.5413 | 123.2803 | -0.40283 | 116.2399 | 114.1617 | 123.2803 | -0.01831 | 123.5413 | -9.5901 | -123.7747
1912.9844 | 123.4451 | -116.0934 | 7.283 | -0.0029495 | 0.045834 | -0.020029 | 0.08032 | -0.053622 | 0.061443 | 0.10697 | -1.7487 | 0.27008 | -2.179 | 7.338 | -116.0797 | 7.2189 | 7.1365 | 7.4432 | 7.4661 | -116.4963 | 113.9145 | -7.0129 | 114.3448 | 123.4314 | -123.3627 | -0.40283 | 0.18311 | 0.4303 | 123.23 | 123.5367 | 0.013733 | 116.3635 | 114.3448 | 123.5596 | 123.3124 | -0.40283 | 116.3635 | 114.3448 | 123.3124 | 0.013733 | 123.5596 | -9.462 | -123.7793
1913.9219 | 123.5458 | -116.0522 | 7.2601 | 0.57688 | 0.038357 | -0.030711 | 0.071775 | -0.061099 | 0.05183 | 0.090949 | -1.8539 | 0.24261 | -2.2568 | 7.2098 | -116.1621 | 7.1274 | 7.2327 | 7.3517 | 7.4661 | -116.5009 | 113.7955 | -7.0175 | 114.1983 | 123.262 | -123.4222 | -0.44861 | 0.20599 | 0.40283 | 123.2849 | 123.4039 | -0.10986 | 116.2949 | 114.1983 | 123.5184 | 123.1796 | -0.44861 | 116.2949 | 114.1983 | 123.1796 | -0.10986 | 123.5184 | -9.5169 | -123.761
1914.9844 | 123.4451 | -116.2125 | 7.1823 | -0.36916 | 0.034085 | -0.020029 | 0.08032 | -0.051486 | 0.049694 | 0.10163 | -1.7853 | 0.27466 | -2.1835 | 7.1732 | -116.2491 | 7.1091 | 6.9717 | 7.3746 | 7.3196 | -116.5878 | 114.0289 | -6.9077 | 114.4272 | 123.3856 | -123.4314 | -0.37537 | 0.13733 | 0.39826 | 123.1842 | 123.587 | -0.036621 | 116.4871 | 114.4272 | 123.5321 | 123.3215 | -0.37537 | 116.4871 | 114.4272 | 123.3215 | -0.036621 | 123.5321 | -9.3658 | -123.7701
1915.9219 | 123.5001 | -117.1234 | 6.221 | -0.38442 | 0.029812 | -0.037119 | 0.049345 | -0.055758 | 0.042217 | 0.1027 | -1.6479 | 0.24261 | -2.0645 | 6.1249 | -117.2012 | 6.0883 | 6.1157 | 6.2942 | 6.4087 | -117.5537 | 115.0589 | -5.9784 | 115.4755 | 123.2483 | -123.4222 | -0.4303 | 0.18768 | 0.41656 | 123.2391 | 123.4177 | -0.07782 | 117.366 | 115.4755 | 123.5321 | 123.2117 | -0.4303 | 117.366 | 115.4755 | 123.2117 | -0.07782 | 123.5321 | -8.2855 | -123.7747
1916.9688 | 123.4039 | -116.1713 | 7.251 | -0.44545 | 0.039425 | -0.02537 | 0.081388 | -0.053622 | 0.044354 | 0.093085 | -1.6251 | 0.29755 | -1.9867 | 7.283 | -116.1484 | 7.2052 | 6.9717 | 7.4249 | 7.3746 | -116.5283 | 114.1846 | -6.9534 | 114.5462 | 123.4543 | -123.3994 | -0.35705 | 0.1236 | 0.36163 | 123.143 | 123.5962 | 0.022889 | 116.4688 | 114.5462 | 123.5458 | 123.3765 | -0.35705 | 116.4688 | 114.5462 | 123.3765 | 0.022889 | 123.5458 | -9.2377 | -123.7793
1917.9219 | 123.4543 | -115.9698 | 7.4203 | 0.13438 | 0.036221 | -0.046732 | 0.070707 | -0.052554 | 0.04649 | 0.099494 | -1.7487 | 0.29297 | -2.1149 | 7.5119 | -115.9332 | 7.3517 | 7.2876 | 7.5806 | 7.6035 | -116.3498 | 113.855 | -7.1274 | 114.2212 | 123.4818 | -123.3536 | -0.37994 | 0.18311 | 0.36621 | 123.2574 | 123.5504 | 0.036621 | 116.2628 | 114.2212 | 123.5733 | 123.3215 | -0.37994 | 116.2628 | 114.2212 | 123.3215 | 0.036621 | 123.5733 | -9.5352 | -123.7701
1918.9688 | 123.3856 | -116.0202 | 7.37 | 0.11912 | 0.045834 | 0.0034686 | 0.092069 | -0.061099 | 0.057171 | 0.10377 | -1.7349 | 0.2655 | -2.1103 | 7.4432 | -116.0385 | 7.3196 | 7.1594 | 7.576 | 7.489 | -116.4047 | 113.9099 | -7.1045 | 114.2853 | 123.4634 | -123.4085 | -0.38452 | 0.11902 | 0.37537 | 123.1796 | 123.5962 | -0.01831 | 116.2857 | 114.2853 | 123.5092 | 123.3398 | -0.38452 | 116.2857 | 114.2853 | 123.3398 | -0.01831 | 123.5092 | -9.4803 | -123.7747
1919.9219 | 123.5321 | -116.3086 | 6.9946 | 0.13438 | 0.031949 | -0.0029404 | 0.065366 | -0.055758 | 0.037945 | 0.10804 | -1.7715 | 0.20142 | -2.1698 | 6.9168 | -116.4093 | 6.8802 | 6.9626 | 7.0816 | 7.2235 | -116.7526 | 114.1388 | -6.7932 | 114.537 | 123.2254 | -123.4039 | -0.44403 | 0.22888 | 0.39826 | 123.2712 | 123.3902 | -0.10071 | 116.51 | 114.537 | 123.5321 | 123.1888 | -0.44403 | 116.51 | 114.537 | 123.1888 | -0.10071 | 123.5321 | -9.1644 | -123.7473
1920.9844 | 123.5092 | -116.4917 | 6.8161 | 0.28697 | 0.037289 | -0.033915 | 0.058958 | -0.062167 | 0.044354 | 0.09629 | -1.7624 | 0.22888 | -2.1286 | 6.7383 | -116.6107 | 6.6833 | 6.7657 | 6.8893 | 7.0129 | -116.9632 | 114.3631 | -6.5872 | 114.7293 | 123.23 | -123.4268 | -0.4715 | 0.19684 | 0.36621 | 123.2574 | 123.381 | -0.11902 | 116.7206 | 114.7293 | 123.5046 | 123.175 | -0.4715 | 116.7206 | 114.7293 | 123.175 | -0.11902 | 123.5046 | -8.9447 | -123.7793
1921.9219 | 123.5321 | -115.6357 | 7.6721 | 0.4243 | 0.034085 | -0.014689 | 0.072843 | -0.056826 | 0.047558 | 0.098426 | -1.6571 | 0.21515 | -2.0737 | 7.3608 | -115.6998 | 7.5714 | 7.6447 | 7.7957 | 7.8049 | -116.1118 | 113.562 | -7.457 | 113.9786 | 122.9965 | -123.3719 | -0.47607 | 0.13275 | 0.41657 | 123.2803 | 123.4314 | -0.064087 | 115.8508 | 113.9786 | 123.4406 | 123.2071 | -0.47607 | 115.8508 | 113.9786 | 123.2071 | -0.064087 | 123.4406 | -9.7458 | -123.7839
1922.9844 | 123.436 | -116.5833 | 6.8161 | 0.01231 | 0.04263 | -0.027506 | 0.085661 | -0.03226 | 0.049694 | 0.090949 | -1.6891 | 0.27466 | -2.1057 | 6.9077 | -116.5375 | 6.72 | 6.5964 | 6.9534 | 6.9992 | -116.9907 | 114.4775 | -6.5414 | 114.8941 | 123.4909 | -123.3536 | -0.40741 | 0.18311 | 0.41657 | 123.1796 | 123.5367 | 0.045776 | 116.8579 | 114.8941 | 123.5825 | 123.3032 | -0.40741 | 116.8579 | 114.8941 | 123.3032 | 0.045776 | 123.5825 | -8.9218 | -123.8068
1923.9219 | 123.4497 | -116.3498 | 7.0038 | 0.4243 | 0.040494 | -0.016825 | 0.08032 | -0.050418 | 0.036877 | 0.10484 | -1.712 | 0.2655 | -2.0874 | 6.9946 | -116.3589 | 6.9214 | 6.8253 | 7.1548 | 7.1136 | -116.7664 | 114.2624 | -6.7383 | 114.6378 | 123.3444 | -123.3627 | -0.41657 | 0.10986 | 0.37537 | 123.175 | 123.5046 | -0.009156 | 116.6153 | 114.6378 | 123.4634 | 123.2712 | -0.41657 | 116.6153 | 114.6378 | 123.2712 | -0.009156 | 123.4634 | -9.0912 | -123.7701
1924.9844 | 123.4314 | -115.1962 | 8.1848 | 0.073345 | 0.04797 | -0.011485 | 0.081388 | -0.044009 | 0.059307 | 0.10163 | -1.5152 | 0.27466 | -1.9318 | 8.2901 | -115.1779 | 8.1253 | 8.0063 | 8.4091 | 8.3221 | -115.6036 | 113.2645 | -7.9102 | 113.681 | 123.4863 | -123.3627 | -0.40741 | 0.13733 | 0.41656 | 123.2025 | 123.6053 | 0.018311 | 115.4709 | 113.681 | 123.5184 | 123.3215 | -0.40741 | 115.4709 | 113.681 | 123.3215 | 0.018311 | 123.5184 | -10.1166 | -123.7885
1925.9219 | 123.5641 | -116.4688 | 6.8436 | 0.51585 | 0.03088 | -0.023234 | 0.064298 | -0.062167 | 0.043285 | 0.10484 | -1.7349 | 0.21973 | -2.1378 | 6.8069 | -116.5375 | 6.7429 | 6.8527 | 6.9672 | 7.0908 | -116.8854 | 114.3311 | -6.6238 | 114.7339 | 123.2758 | -123.381 | -0.41656 | 0.24719 | 0.40283 | 123.3215 | 123.436 | -0.068665 | 116.6885 | 114.7339 | 123.5596 | 123.2117 | -0.41656 | 116.6885 | 114.7339 | 123.2117 | -0.068665 | 123.5596 | -8.9813 | -123.7289
1926.9844 | 123.4222 | -116.5604 | 6.8436 | -0.41494 | 0.036221 | -0.026438 | 0.072843 | -0.051486 | 0.041149 | 0.1059 | -1.4099 | 0.30212 | -2.0187 | 6.9031 | -116.5054 | 6.7978 | 6.5689 | 7.0175 | 6.9763 | -116.9312 | 114.5416 | -6.5414 | 115.1505 | 123.4634 | -123.349 | -0.37079 | 0.13275 | 0.60883 | 123.1293 | 123.5779 | 0.054932 | 116.8625 | 115.1505 | 123.5367 | 123.3582 | -0.37079 | 116.8625 | 115.1505 | 123.3582 | 0.054932 | 123.5367 | -8.8623 | -123.7747
1927.9219 | 123.5413 | -117.1921 | 6.1111 | -0.53701 | 0.029812 | -0.012553 | 0.051481 | -0.061099 | 0.039013 | 0.11445 | -1.9043 | 0.18768 | -2.2842 | 6.0104 | -117.3065 | 5.9692 | 6.0654 | 6.1981 | 6.3171 | -117.6407 | 114.9078 | -5.9235 | 115.2878 | 123.2025 | -123.4177 | -0.44861 | 0.20599 | 0.37994 | 123.2574 | 123.3902 | -0.11444 | 117.3798 | 115.2878 | 123.5092 | 123.1613 | -0.44861 | 117.3798 | 115.2878 | 123.1613 | -0.11444 | 123.5092 | -8.3954 | -123.7518
1928.9844 | 123.3902 | -116.423 | 6.9809 | 0.57688 | 0.050107 | -0.041392 | 0.08032 | -0.048281 | 0.056103 | 0.10056 | -1.7487 | 0.28381 | -2.1378 | 7.0587 | -116.3589 | 6.9489 | 6.7429 | 7.1869 | 7.077 | -116.8213 | 114.2853 | -6.6971 | 114.6744 | 123.4818 | -123.3398 | -0.39825 | 0.09613 | 0.3891 | 123.1659 | 123.6099 | 0.064087 | 116.7068 | 114.6744 | 123.5001 | 123.3719 | -0.39825 | 116.7068 | 114.6744 | 123.3719 | 0.064087 | 123.5001 | -9.1187 | -123.8022
1929.9219 | 123.5229 | -115.9882 | 7.3517 | 0.4243 | 0.04263 | -0.015757 | 0.074979 | -0.052554 | 0.050762 | 0.11124 | -1.6846 | 0.26093 | -2.1011 | 7.3242 | -116.0614 | 7.251 | 7.3654 | 7.4707 | 7.5439 | -116.4139 | 113.887 | -7.0908 | 114.3036 | 123.3124 | -123.4131 | -0.42572 | 0.19226 | 0.41657 | 123.3536 | 123.4589 | -0.073242 | 116.2491 | 114.3036 | 123.5321 | 123.2391 | -0.42572 | 116.2491 | 114.3036 | 123.2391 | -0.073242 | 123.5321 | -9.4528 | -123.7656
1930.9688 | 123.4451 | -116.0843 | 7.2968 | -0.18605 | 0.041562 | -0.0061444 | 0.082456 | -0.049349 | 0.056103 | 0.10911 | -1.6205 | 0.27466 | -2.0416 | 7.2693 | -116.1072 | 7.2144 | 7.1136 | 7.4387 | 7.402 | -116.4917 | 114.0427 | -7.0221 | 114.4638 | 123.3536 | -123.4039 | -0.40741 | 0.10529 | 0.42114 | 123.1979 | 123.5229 | -0.022888 | 116.3589 | 114.4638 | 123.4863 | 123.2986 | -0.40741 | 116.3589 | 114.4638 | 123.2986 | -0.022888 | 123.4863 | -9.3384 | -123.7885
1931.9219 | 123.4955 | -116.5237 | 6.8024 | 0.50059 | 0.041562 | -0.0040084 | 0.067503 | -0.066439 | 0.047558 | 0.089881 | -1.6754 | 0.26093 | -2.0416 | 6.8161 | -116.5512 | 6.6971 | 6.7245 | 6.9122 | 7.0129 | -116.9815 | 114.4821 | -6.5414 | 114.8483 | 123.3398 | -123.3536 | -0.45776 | 0.21057 | 0.36621 | 123.2483 | 123.436 | -0.027465 | 116.7847 | 114.8483 | 123.5367 | 123.2208 | -0.45776 | 116.7847 | 114.8483 | 123.2208 | -0.027465 | 123.5367 | -8.844 | -123.7839
1932.9844 | 123.4131 | -117.3248 | 6.1111 | 0.10386 | 0.049038 | -0.013621 | 0.076048 | -0.053622 | 0.058239 | 0.10163 | -1.7029 | 0.27924 | -2.0966 | 6.1432 | -117.2516 | 6.0425 | 5.864 | 6.2759 | 6.2393 | -117.7277 | 115.2283 | -5.8319 | 115.6219 | 123.468 | -123.3627 | -0.40283 | 0.12817 | 0.39368 | 123.1888 | 123.6008 | 0.073242 | 117.6041 | 115.6219 | 123.5641 | 123.3673 | -0.40283 | 117.6041 | 115.6219 | 123.3673 | 0.073242 | 123.5641 | -8.2077 | -123.8388
1933.9219 | 123.5367 | -117.334 | 5.983 | 0.37852 | 0.039425 | -0.022166 | 0.068571 | -0.062167 | 0.055035 | 0.095222 | -1.8677 | 0.21973 | -2.2797 | 5.9143 | -117.4255 | 5.8456 | 5.9372 | 6.0562 | 6.189 | -117.8009 | 115.0543 | -5.7632 | 115.4663 | 123.2483 | -123.4085 | -0.46692 | 0.20599 | 0.41199 | 123.2712 | 123.3902 | -0.091553 | 117.5537 | 115.4663 | 123.5229 | 123.1796 | -0.46692 | 117.5537 | 115.4663 | 123.1796 | -0.091553 | 123.5229 | -8.2626 | -123.7839
1934.9844 | 123.4497 | -116.6336 | 6.7337 | -0.24709 | 0.045834 | -0.014689 | 0.079252 | -0.050418 | 0.059307 | 0.088813 | -1.7441 | 0.27008 | -2.1332 | 6.752 | -116.6656 | 6.6696 | 6.5414 | 6.8848 | 6.8756 | -117.0731 | 114.5004 | -6.4636 | 114.8895 | 123.3856 | -123.3994 | -0.43945 | 0.14191 | 0.3891 | 123.175 | 123.5184 | -0.032043 | 116.9037 | 114.8895 | 123.5092 | 123.3032 | -0.43945 | 116.9037 | 114.8895 | 123.3032 | -0.032043 | 123.5092 | -8.8669 | -123.8068
1935.9219 | 123.5321 | -116.2811 | 7.0358 | 0.43956 | 0.037289 | -0.017893 | 0.064298 | -0.060031 | 0.030468 | 0.10163 | -1.767 | 0.2243 | -2.1515 | 7.0175 | -116.3223 | 6.9214 | 6.9946 | 7.1045 | 7.2647 | -116.6931 | 114.1296 | -6.8115 | 114.5142 | 123.2986 | -123.3582 | -0.41199 | 0.22888 | 0.38452 | 123.2758 | 123.3856 | -0.041199 | 116.5054 | 114.5142 | 123.5458 | 123.2025 | -0.41199 | 116.5054 | 114.5142 | 123.2025 | -0.041199 | 123.5458 | -9.1873 | -123.7289
1936.9844 | 123.4177 | -116.716 | 6.6696 | -1.2847 | 0.049038 | -0.010416 | 0.068571 | -0.056826 | 0.056103 | 0.10377 | -1.7761 | 0.33875 | -2.0874 | 6.72 | -116.6931 | 6.5826 | 6.4865 | 6.8298 | 6.8161 | -117.1234 | 114.6286 | -6.3309 | 114.9399 | 123.436 | -123.3627 | -0.40741 | 0.14648 | 0.31128 | 123.2025 | 123.5458 | 0.022888 | 117.0547 | 114.9399 | 123.5321 | 123.2986 | -0.40741 | 117.0547 | 114.9399 | 123.2986 | 0.022888 | 123.5321 | -8.757 | -123.793
1937.9219 | 123.3948 | -116.7206 | 6.6971 | 0.30223 | 0.039425 | -0.010416 | 0.076048 | -0.067507 | 0.083874 | 0.1027 | -1.8356 | 0.29297 | -2.2064 | 6.5186 | -116.6473 | 6.6742 | 6.4178 | 6.7749 | 6.8207 | -117.1051 | 114.5142 | -6.4041 | 114.8849 | 123.2391 | -123.3444 | -0.38452 | 0.1236 | 0.37079 | 123.1384 | 123.4955 | 0.073242 | 117.0135 | 114.8849 | 123.5413 | 123.3948 | -0.38452 | 117.0135 | 114.8849 | 123.3948 | 0.073242 | 123.5413 | -8.9035 | -123.8022
1938.9688 | 123.4222 | -116.4459 | 6.9901 | -0.048725 | 0.040494 | -0.020029 | 0.091001 | -0.056826 | 0.044354 | 0.10484 | -1.7349 | 0.29755 | -2.0966 | 7.0358 | -116.3544 | 6.926 | 6.7703 | 7.1548 | 7.1365 | -116.7801 | 114.3494 | -6.6925 | 114.711 | 123.4818 | -123.3444 | -0.33417 | 0.14649 | 0.36163 | 123.2162 | 123.6008 | 0.091553 | 116.7435 | 114.711 | 123.5825 | 123.3719 | -0.33417 | 116.7435 | 114.711 | 123.3719 | 0.091553 | 123.5825 | -9.0866 | -123.7701
1939.9219 | 123.5046 | -116.7435 | 6.5826 | 0.4243 | 0.037289 | -0.024302 | 0.066434 | -0.051486 | 0.048626 | 0.10804 | -1.5701 | 0.25177 | -1.9592 | 6.5552 | -116.7755 | 6.4819 | 6.5781 | 6.7154 | 6.7886 | -117.16 | 114.7842 | -6.3309 | 115.1733 | 123.2986 | -123.3582 | -0.41656 | 0.20599 | 0.3891 | 123.3215 | 123.4589 | -0.032044 | 116.9952 | 115.1733 | 123.5321 | 123.2254 | -0.41656 | 116.9952 | 115.1733 | 123.2254 | -0.032044 | 123.5321 | -8.5419 | -123.7427
1940.9844 | 123.468 | -116.6199 | 6.7612 | -0.32338 | 0.046902 | -0.0082804 | 0.073911 | -0.057894 | 0.047558 | 0.099494 | -1.5381 | 0.27466 | -1.9089 | 6.7657 | -116.6199 | 6.6833 | 6.5781 | 6.926 | 6.9122 | -117.041 | 114.711 | -6.4865 | 115.0818 | 123.3856 | -123.381 | -0.42114 | 0.15106 | 0.37079 | 123.1979 | 123.5458 | 0 | 116.8945 | 115.0818 | 123.5321 | 123.3032 | -0.42114 | 116.8945 | 115.0818 | 123.3032 | 0 | 123.5321 | -8.67 | -123.8022
1941.9219 | 123.5184 | -117.0181 | 6.3171 | 0.47007 | 0.037289 | -0.015757 | 0.067503 | -0.055758 | 0.047558 | 0.09629 | -1.6251 | 0.23804 | -1.9958 | 6.2851 | -117.0776 | 6.2027 | 6.2668 | 6.4178 | 6.5048 | -117.4393 | 115.0223 | -6.0791 | 115.3931 | 123.3032 | -123.3948 | -0.42114 | 0.18768 | 0.37079 | 123.2849 | 123.436 | -0.05951 | 117.2562 | 115.3931 | 123.5229 | 123.2208 | -0.42114 | 117.2562 | 115.3931 | 123.2208 | -0.05951 | 123.5229 | -8.313 | -123.7564
1942.9844 | 123.4451 | -117.0135 | 6.3675 | -0.29287 | 0.043698 | -0.024302 | 0.077116 | -0.061099 | 0.042217 | 0.094154 | -1.4877 | 0.28839 | -1.886 | 6.3766 | -117.0364 | 6.2897 | 6.1661 | 6.5186 | 6.5048 | -117.4347 | 115.1276 | -6.0791 | 115.5258 | 123.3902 | -123.4039 | -0.42114 | 0.13733 | 0.39825 | 123.1796 | 123.5321 | -0.022888 | 117.3019 | 115.5258 | 123.5184 | 123.3032 | -0.42114 | 117.3019 | 115.5258 | 123.3032 | -0.022888 | 123.5184 | -8.2535 | -123.8022
1943.9219 | 123.5229 | -116.2537 | 7.0587 | 0.48533 | 0.036221 | 0.0056046 | 0.05789 | -0.056826 | 0.045422 | 0.10804 | -1.4557 | 0.21973 | -1.8539 | 6.9901 | -116.3452 | 6.9351 | 7.0496 | 7.1457 | 7.2601 | -116.7206 | 114.3997 | -6.839 | 114.798 | 123.2437 | -123.4039 | -0.46692 | 0.20142 | 0.39825 | 123.3032 | 123.3994 | -0.091553 | 116.4734 | 114.798 | 123.5138 | 123.1888 | -0.46692 | 116.4734 | 114.798 | 123.1888 | -0.091553 | 123.5138 | -8.9127 | -123.7793
1944.9688 | 123.4497 | -116.2857 | 7.1182 | -0.0029495 | 0.033017 | -0.0082804 | 0.077116 | -0.056826 | 0.052898 | 0.10056 | -1.4786 | 0.26093 | -1.8494 | 7.132 | -116.2766 | 7.0175 | 6.9168 | 7.2601 | 7.2556 | -116.7068 | 114.4363 | -6.8573 | 114.8071 | 123.4177 | -123.3948 | -0.42114 | 0.13733 | 0.37079 | 123.2025 | 123.5458 | 0.009156 | 116.5466 | 114.8071 | 123.5413 | 123.3032 | -0.42114 | 116.5466 | 114.8071 | 123.3032 | 0.009156 | 123.5413 | -8.9676 | -123.8251
1945.9219 | 123.4909 | -116.4825 | 6.8527 | 0.4243 | 0.049038 | 0.0066726 | 0.073911 | -0.056826 | 0.053967 | 0.099494 | -1.5564 | 0.25177 | -1.9318 | 6.8573 | -116.5009 | 6.752 | 6.7383 | 6.9626 | 7.0496 | -116.8945 | 114.5508 | -6.601 | 114.9261 | 123.3398 | -123.3536 | -0.41199 | 0.19684 | 0.37537 | 123.2208 | 123.4451 | -0.01831 | 116.7343 | 114.9261 | 123.5321 | 123.2346 | -0.41199 | 116.7343 | 114.9261 | 123.2346 | -0.01831 | 123.5321 | -8.7845 | -123.7473
1946.9844 | 123.4543 | -116.1118 | 7.2647 | -0.12502 | 0.040494 | -0.032847 | 0.089933 | -0.051486 | 0.053967 | 0.09629 | -1.4648 | 0.28381 | -1.8768 | 7.2464 | -116.1667 | 7.1411 | 7.0679 | 7.4387 | 7.3608 | -116.5237 | 114.2349 | -6.9809 | 114.6469 | 123.3582 | -123.4314 | -0.41199 | 0.096131 | 0.41199 | 123.1796 | 123.5504 | -0.054932 | 116.3956 | 114.6469 | 123.4726 | 123.2529 | -0.41199 | 116.3956 | 114.6469 | 123.2529 | -0.054932 | 123.4726 | -9.1415 | -123.7885
1947.9219 | 123.5046 | -116.1392 | 7.2098 | 2.2706 | 0.029812 | -0.016825 | 0.060026 | -0.05469 | 0.034741 | 0.09629 | -1.5244 | 0.20599 | -2.0233 | 7.132 | -116.1987 | 7.0587 | 7.1686 | 7.2556 | 7.4341 | -116.5649 | 114.1159 | -7.0038 | 114.6149 | 123.2712 | -123.4085 | -0.42572 | 0.2243 | 0.49896 | 123.3078 | 123.3948 | -0.059509 | 116.3452 | 114.6149 | 123.5733 | 123.1979 | -0.42572 | 116.3452 | 114.6149 | 123.1979 | -0.059509 | 123.5733 | -9.2331 | -123.7747
1948.9844 | 123.3994 | -116.5009 | 6.9214 | 0.48533 | 0.041562 | -0.0050764 | 0.087797 | -0.055758 | 0.053967 | 0.10377 | -1.6525 | 0.29755 | -2.005 | 6.9763 | -116.4001 | 6.8756 | 6.6742 | 7.1091 | 7.045 | -116.8716 | 114.4958 | -6.6238 | 114.8483 | 123.4772 | -123.3215 | -0.37079 | 0.1236 | 0.35248 | 123.175 | 123.6099 | 0.10071 | 116.7984 | 114.8483 | 123.5458 | 123.3765 | -0.37079 | 116.7984 | 114.8483 | 123.3765 | 0.10071 | 123.5458 | -8.9264 | -123.793
1949.9219 | 123.5184 | -116.6656 | 6.665 | 0.40904 | 0.033017 | -0.04246 | 0.058958 | -0.05469 | 0.040081 | 0.088813 | -1.593 | 0.20599 | -2.0416 | 6.5506 | -116.716 | 6.514 | 6.6147 | 6.7566 | 6.8481 | -117.1143 | 114.624 | -6.459 | 115.0726 | 123.2162 | -123.381 | -0.44861 | 0.18311 | 0.44861 | 123.2803 | 123.4222 | -0.050354 | 116.8716 | 115.0726 | 123.5138 | 123.1796 | -0.44861 | 116.8716 | 115.0726 | 123.1796 | -0.050354 | 123.5138 | -8.7067 | -123.7793
1950.9844 | 123.4451 | -116.0751 | 7.3425 | -0.36916 | 0.044766 | -0.020029 | 0.08032 | -0.064303 | 0.039013 | 0.099494 | -1.5656 | 0.29297 | -1.9409 | 7.3746 | -116.066 | 7.283 | 7.0953 | 7.5302 | 7.4799 | -116.4688 | 114.1342 | -7.0496 | 114.5096 | 123.4497 | -123.4085 | -0.39368 | 0.13733 | 0.37537 | 123.1705 | 123.6053 | 0.009155 | 116.3681 | 114.5096 | 123.555 | 123.3582 | -0.39368 | 116.3681 | 114.5096 | 123.3582 | 0.009155 | 123.555 | -9.2834 | -123.8113
1951.9219 | 123.4497 | -115.4755 | 7.9147 | 0.57688 | 0.038357 | -0.027506 | 0.079252 | -0.060031 | 0.048626 | 0.093085 | -1.5564 | 0.28381 | -1.9089 | 7.9468 | -115.4572 | 7.8552 | 7.7454 | 8.0887 | 8.0246 | -115.8646 | 113.5666 | -7.6309 | 113.9191 | 123.4222 | -123.3719 | -0.3891 | 0.10986 | 0.35248 | 123.2208 | 123.5641 | 0.018311 | 115.7593 | 113.9191 | 123.5001 | 123.3307 | -0.3891 | 115.7593 | 113.9191 | 123.3307 | 0.018311 | 123.5001 | -9.8236 | -123.7793
1952.9844 | 123.4314 | -115.3976 | 7.9788 | 0.01231 | 0.035153 | -0.020029 | 0.084592 | -0.053622 | 0.059307 | 0.10911 | -1.506 | 0.3067 | -1.9135 | 8.0658 | -115.3702 | 7.9559 | 7.8278 | 8.2077 | 8.139 | -115.7776 | 113.4842 | -7.6721 | 113.8916 | 123.4634 | -123.349 | -0.37994 | 0.16022 | 0.40741 | 123.2254 | 123.6053 | 0.027466 | 115.7043 | 113.8916 | 123.5367 | 123.3536 | -0.37994 | 115.7043 | 113.8916 | 123.3536 | 0.027466 | 123.5367 | -9.8923 | -123.7564
1953.9219 | 123.5321 | -115.892 | 7.4158 | 0.45481 | 0.029812 | -0.018961 | 0.065366 | -0.055758 | 0.043285 | 0.1059 | -1.7532 | 0.21515 | -2.1698 | 7.3792 | -115.9836 | 7.2784 | 7.3929 | 7.5027 | 7.6126 | -116.3406 | 113.7222 | -7.2006 | 114.1388 | 123.2712 | -123.3994 | -0.44861 | 0.19684 | 0.41656 | 123.2849 | 123.3948 | -0.091553 | 116.1072 | 114.1388 | 123.5046 | 123.1705 | -0.44861 | 116.1072 | 114.1388 | 123.1705 | -0.091553 | 123.5046 | -9.5856 | -123.7564
1954.9844 | 123.4268 | -115.4709 | 7.9056 | -0.063984 | 0.036221 | -0.0093484 | 0.087797 | -0.05469 | 0.053967 | 0.099494 | -1.4877 | 0.29755 | -2.0187 | 7.9514 | -115.4755 | 7.8049 | 7.6813 | 8.0292 | 8.0338 | -115.9149 | 113.4521 | -7.608 | 113.9832 | 123.4222 | -123.381 | -0.44403 | 0.12817 | 0.53101 | 123.1522 | 123.5001 | -0.004578 | 115.7684 | 113.9832 | 123.5046 | 123.2758 | -0.44403 | 115.7684 | 113.9832 | 123.2758 | -0.004578 | 123.5046 | -9.9243 | -123.8205
1955.9219 | 123.5275 | -115.8691 | 7.457 | 0.4243 | 0.035153 | -0.017893 | 0.072843 | -0.062167 | 0.041149 | 0.10056 | -1.712 | 0.23346 | -2.1011 | 7.4203 | -115.9378 | 7.3196 | 7.4203 | 7.5394 | 7.6492 | -116.3177 | 113.768 | -7.2235 | 114.1571 | 123.2895 | -123.3948 | -0.44861 | 0.19226 | 0.3891 | 123.2895 | 123.4085 | -0.068664 | 116.1026 | 114.1571 | 123.5184 | 123.1888 | -0.44861 | 116.1026 | 114.1571 | 123.1888 | -0.068664 | 123.5184 | -9.5581 | -123.7747
1956.9844 | 123.4268 | -116.1072 | 7.3013 | 0.088604 | 0.045834 | -0.063822 | 0.088865 | -0.046145 | 0.052898 | 0.09629 | -1.5335 | 0.28381 | -1.9409 | 7.3425 | -116.0614 | 7.2189 | 7.0862 | 7.4753 | 7.4341 | -116.5054 | 114.1663 | -7.0175 | 114.5737 | 123.4497 | -123.3627 | -0.39825 | 0.13275 | 0.40741 | 123.1934 | 123.5825 | 0.045777 | 116.391 | 114.5737 | 123.5413 | 123.3261 | -0.39825 | 116.391 | 114.5737 | 123.3261 | 0.045777 | 123.5413 | -9.2422 | -123.8068
1957.9219 | 123.5046 | -115.7318 | 7.6126 | 0.48533 | 0.039425 | -0.024302 | 0.073911 | -0.049349 | 0.055035 | 0.097358 | -1.2268 | 0.24261 | -1.5747 | 7.5897 | -115.8051 | 7.4844 | 7.5073 | 7.7179 | 7.7866 | -116.1667 | 114.1571 | -7.37 | 114.505 | 123.3215 | -123.4177 | -0.43487 | 0.17395 | 0.3479 | 123.2391 | 123.4497 | -0.073242 | 115.9744 | 114.505 | 123.5184 | 123.2162 | -0.43487 | 115.9744 | 114.505 | 123.2162 | -0.073242 | 123.5184 | -9.1873 | -123.7793
1958.9688 | 123.4406 | -115.8646 | 7.5302 | -0.033467 | 0.028744 | -0.012553 | 0.08032 | -0.051486 | 0.04649 | 0.10911 | -1.5244 | 0.27466 | -1.9592 | 7.4982 | -115.9012 | 7.3883 | 7.2922 | 7.8369 | 7.6126 | -116.2308 | 113.9053 | -7.2556 | 114.3402 | 123.3627 | -123.4314 | -0.36621 | 0.082398 | 0.43488 | 123.1567 | 123.7015 | -0.036621 | 116.1392 | 114.3402 | 123.4772 | 123.2529 | -0.36621 | 116.1392 | 114.3402 | 123.2529 | -0.036621 | 123.4772 | -9.4894 | -123.761
1959.9219 | 123.5046 | -115.86 | 7.4753 | 0.43956 | 0.043698 | -0.018961 | 0.066434 | -0.057894 | 0.05183 | 0.10163 | -1.6159 | 0.24261 | -2.0096 | 7.4112 | -115.9424 | 7.3334 | 7.4112 | 7.5623 | 7.6538 | -116.3086 | 113.8504 | -7.2327 | 114.2441 | 123.2712 | -123.4177 | -0.44861 | 0.17853 | 0.39368 | 123.2712 | 123.4222 | -0.082398 | 116.1026 | 114.2441 | 123.5138 | 123.1934 | -0.44861 | 116.1026 | 114.2441 | 123.1934 | -0.082398 | 123.5138 | -9.4849 | -123.7839
1960.9844 | 123.3673 | -115.6403 | 7.7545 | 0.37852 | 0.044766 | -0.037119 | 0.077116 | -0.042941 | 0.059307 | 0.10484 | -1.6296 | 0.27466 | -1.9867 | 7.8186 | -115.5945 | 7.6996 | 7.5119 | 7.9376 | 7.8506 | -116.0385 | 113.6536 | -7.4799 | 114.0106 | 123.4589 | -123.349 | -0.39825 | 0.09613 | 0.35705 | 123.1522 | 123.5779 | 0.045777 | 115.9149 | 114.0106 | 123.4909 | 123.3398 | -0.39825 | 115.9149 | 114.0106 | 123.3398 | 0.045777 | 123.4909 | -9.7412 | -123.793
1961.9219 | 123.5367 | -115.6403 | 7.6859 | 0.53111 | 0.035153 | -0.014689 | 0.055753 | -0.070712 | 0.047558 | 0.098426 | -1.5564 | 0.23804 | -1.9409 | 7.4524 | -115.8325 | 7.4753 | 7.6401 | 7.7774 | 7.7774 | -116.1301 | 113.6993 | -7.4478 | 114.0839 | 123.0927 | -123.5184 | -0.48981 | 0.091553 | 0.38452 | 123.2803 | 123.4177 | -0.19226 | 115.8783 | 114.0839 | 123.4177 | 123.1155 | -0.48981 | 115.8783 | 114.0839 | 123.1155 | -0.19226 | 123.4177 | -9.6268 | -123.8159
1962.9844 | 123.3994 | -116.1026 | 7.2968 | -0.44545 | 0.036221 | -0.013621 | 0.064298 | -0.062167 | 0.047558 | 0.09629 | -1.6159 | 0.29297 | -1.9455 | 7.3288 | -116.0477 | 7.2784 | 7.0587 | 7.5211 | 7.4203 | -116.4825 | 114.1571 | -7.0038 | 114.4867 | 123.4314 | -123.3444 | -0.37994 | 0.1236 | 0.32959 | 123.1613 | 123.6237 | 0.054932 | 116.3956 | 114.4867 | 123.5229 | 123.381 | -0.37994 | 116.3956 | 114.4867 | 123.381 | 0.054932 | 123.5229 | -9.2422 | -123.7793
1963.9219 | 123.5046 | -115.8417 | 7.4844 | 0.47007 | 0.043698 | -0.022166 | 0.082456 | -0.060031 | 0.042217 | 0.10056 | -1.5518 | 0.26093 | -1.9409 | 7.4844 | -115.9103 | 7.3792 | 7.4112 | 7.5943 | 7.6767 | -116.3223 | 113.9008 | -7.2235 | 114.2899 | 123.3261 | -123.3948 | -0.48065 | 0.19226 | 0.3891 | 123.2529 | 123.436 | -0.068664 | 116.1026 | 114.2899 | 123.5184 | 123.2208 | -0.48065 | 116.1026 | 114.2899 | 123.2208 | -0.068664 | 123.5184 | -9.4254 | -123.8068
1964.9844 | 123.436 | -115.8966 | 7.5256 | -0.33864 | 0.039425 | -0.043528 | 0.081388 | -0.060031 | 0.021923 | 0.10163 | -1.5106 | 0.29755 | -1.8677 | 7.7545 | -115.6998 | 7.4432 | 7.1915 | 7.7499 | 7.6767 | -116.2766 | 114.0289 | -7.2281 | 114.386 | 123.6511 | -123.2254 | -0.37994 | 0.15106 | 0.35706 | 123.0881 | 123.6465 | 0.19684 | 116.1942 | 114.386 | 123.5733 | 123.3398 | -0.37994 | 116.1942 | 114.386 | 123.3398 | 0.19684 | 123.5733 | -9.3933 | -123.8022
1965.9219 | 123.3902 | -115.6586 | 7.7225 | 0.10386 | 0.049038 | -0.020029 | 0.089933 | -0.058962 | 0.06358 | 0.10056 | -1.6983 | 0.2655 | -2.0737 | 7.8003 | -115.6494 | 7.6767 | 7.5073 | 7.9422 | 7.8323 | -116.0843 | 113.5849 | -7.457 | 113.9603 | 123.4589 | -123.3719 | -0.42572 | 0.10986 | 0.37537 | 123.1659 | 123.6008 | 0.009155 | 115.9241 | 113.9603 | 123.4909 | 123.3353 | -0.42572 | 115.9241 | 113.9603 | 123.3353 | 0.009155 | 123.4909 | -9.7961 | -123.8068
1966.9844 | 123.4497 | -115.7364 | 7.6447 | -0.29287 | 0.04263 | -0.029642 | 0.070707 | -0.050418 | 0.058239 | 0.1027 | -1.593 | 0.28381 | -1.9913 | 7.6584 | -115.741 | 7.576 | 7.4478 | 7.7957 | 7.7957 | -116.1346 | 113.7451 | -7.3608 | 114.1434 | 123.3948 | -123.3856 | -0.39825 | 0.15106 | 0.39825 | 123.1842 | 123.5321 | -0.004578 | 116.0202 | 114.1434 | 123.5321 | 123.3124 | -0.39825 | 116.0202 | 114.1434 | 123.3124 | -0.004578 | 123.5321 | -9.6359 | -123.7793
1967.9219 | 123.468 | -115.8508 | 7.5531 | 0.50059 | 0.044766 | -0.013621 | 0.069639 | -0.045077 | 0.052898 | 0.1059 | -1.5656 | 0.27924 | -1.9226 | 7.5577 | -115.7547 | 7.4478 | 7.3975 | 7.6767 | 7.6904 | -116.272 | 113.9282 | -7.2739 | 114.2853 | 123.4085 | -123.3078 | -0.42114 | 0.13733 | 0.35705 | 123.2483 | 123.5275 | 0.09613 | 116.1301 | 114.2853 | 123.5413 | 123.2986 | -0.42114 | 116.1301 | 114.2853 | 123.2986 | 0.09613 | 123.5413 | -9.4757 | -123.8251
1968.9844 | 123.4268 | -115.6952 | 7.6538 | -0.12502 | 0.035153 | -0.043528 | 0.084592 | -0.041873 | 0.053967 | 0.10377 | -1.4786 | 0.28381 | -1.8951 | 7.6355 | -115.773 | 7.5211 | 7.4387 | 7.7728 | 7.7499 | -116.1942 | 113.8 | -7.37 | 114.2166 | 123.3307 | -123.4268 | -0.49896 | 0.09613 | 0.41657 | 123.1338 | 123.468 | -0.07782 | 115.979 | 114.2166 | 123.4451 | 123.2162 | -0.49896 | 115.979 | 114.2166 | 123.2162 | -0.07782 | 123.4451 | -9.549 | -123.848
1969.9219 | 123.3902 | -115.6723 | 7.7362 | 0.13438 | 0.044766 | -0.013621 | 0.087797 | -0.052554 | 0.043285 | 0.10163 | -1.5427 | 0.27924 | -1.886 | 7.8735 | -115.5441 | 7.7042 | 7.5256 | 7.9697 | 7.8827 | -116.0385 | 113.7863 | -7.457 | 114.1296 | 123.5458 | -123.2803 | -0.36621 | 0.14648 | 0.34332 | 123.1979 | 123.642 | 0.12817 | 115.9515 | 114.1296 | 123.555 | 123.3765 | -0.36621 | 115.9515 | 114.1296 | 123.3765 | 0.12817 | 123.555 | -9.6222 | -123.7747
1970.9844 | 123.5001 | -115.6265 | 7.7225 | -0.97951 | 0.034085 | -0.037119 | 0.061094 | -0.058962 | 0.037945 | 0.11018 | -1.3779 | 0.22888 | -1.7349 | 7.6492 | -115.7364 | 7.608 | 7.6355 | 7.8323 | 7.9193 | -116.0477 | 113.8916 | -7.4936 | 114.2487 | 123.2758 | -123.4589 | -0.42114 | 0.19684 | 0.35705 | 123.262 | 123.4589 | -0.10986 | 115.8554 | 114.2487 | 123.5458 | 123.2346 | -0.42114 | 115.8554 | 114.2487 | 123.2346 | -0.10986 | 123.5458 | -9.4574 | -123.7701
1971.9219 | 123.4451 | -115.3564 | 8.0612 | 0.45481 | 0.035153 | -0.031779 | 0.076048 | -0.053622 | 0.050762 | 0.09629 | -1.3916 | 0.25635 | -1.7761 | 8.0704 | -115.3381 | 8.0109 | 7.8552 | 8.226 | 8.1711 | -115.7364 | 113.5803 | -7.8049 | 113.9648 | 123.4268 | -123.3994 | -0.37994 | 0.10986 | 0.38452 | 123.2117 | 123.5825 | 0.01831 | 115.6128 | 113.9648 | 123.5275 | 123.3673 | -0.37994 | 115.6128 | 113.9648 | 123.3673 | 0.01831 | 123.5275 | -9.8373 | -123.7976
1972.9844 | 123.4863 | -115.4709 | 7.8827 | -0.36916 | 0.021267 | -0.02537 | 0.058958 | -0.051486 | 0.034741 | 0.10697 | -1.3367 | 0.25177 | -1.7349 | 7.8369 | -115.5579 | 7.7911 | 7.7728 | 8.0017 | 8.0795 | -115.892 | 113.736 | -7.6309 | 114.1342 | 123.3078 | -123.4406 | -0.42114 | 0.19684 | 0.39825 | 123.2437 | 123.4726 | -0.086975 | 115.7227 | 114.1342 | 123.5504 | 123.262 | -0.42114 | 115.7227 | 114.1342 | 123.262 | -0.086975 | 123.5504 | -9.6176 | -123.7747
1973.9219 | 123.3994 | -114.6835 | 8.7341 | 0.10386 | 0.04797 | -0.026438 | 0.078184 | -0.066439 | 0.04649 | 0.1027 | -1.4236 | 0.27924 | -1.7578 | 8.9127 | -114.5142 | 8.7021 | 8.4595 | 8.8486 | 8.8257 | -115.0726 | 112.9257 | -8.4549 | 113.2599 | 123.5962 | -123.2483 | -0.3891 | 0.091553 | 0.33417 | 123.143 | 123.5321 | 0.16937 | 114.9628 | 113.2599 | 123.5092 | 123.3856 | -0.3891 | 114.9628 | 113.2599 | 123.3856 | 0.16937 | 123.5092 | -10.4919 | -123.8068
1974.9844 | 123.5275 | -114.8254 | 8.5236 | -0.30813 | 0.037289 | -0.053141 | 0.052549 | -0.064303 | 0.028332 | 0.095222 | -1.0941 | 0.23346 | -1.7075 | 8.4137 | -114.917 | 8.3588 | 8.4274 | 8.6151 | 8.7021 | -115.2649 | 113.118 | -8.2901 | 113.7314 | 123.2391 | -123.4406 | -0.43945 | 0.17853 | 0.6134 | 123.2529 | 123.4406 | -0.091553 | 115.0589 | 113.7314 | 123.5275 | 123.1842 | -0.43945 | 115.0589 | 113.7314 | 123.1842 | -0.091553 | 123.5275 | -10.231 | -123.7885
1975.9219 | 123.3902 | -114.4501 | 8.9264 | 0.11912 | 0.038357 | 0.013082 | 0.08032 | -0.048281 | 0.05183 | 0.097358 | -1.3504 | 0.28381 | -1.7029 | 9.0225 | -114.3906 | 8.9264 | 8.6884 | 9.1507 | 9.0729 | -114.8483 | 112.7472 | -8.6426 | 113.0997 | 123.4726 | -123.317 | -0.39825 | 0.14648 | 0.35248 | 123.1384 | 123.6008 | 0.059509 | 114.7339 | 113.0997 | 123.5229 | 123.3765 | -0.39825 | 114.7339 | 113.0997 | 123.3765 | 0.059509 | 123.5229 | -10.6293 | -123.7747
1976.9844 | 123.555 | -114.6378 | 8.6792 | -0.29287 | 0.022336 | -0.034983 | 0.050413 | -0.052554 | 0.024059 | 0.10163 | -1.236 | 0.22888 | -1.6434 | 8.4778 | -114.9033 | 8.4732 | 8.5785 | 8.7112 | 8.7936 | -115.1138 | 112.9944 | -8.4503 | 113.4018 | 123.1155 | -123.5825 | -0.47608 | 0.11444 | 0.40741 | 123.2162 | 123.349 | -0.2655 | 114.8666 | 113.4018 | 123.4314 | 123.111 | -0.47608 | 114.8666 | 113.4018 | 123.111 | -0.2655 | 123.4314 | -10.3226 | -123.793
1977.9219 | 123.4085 | -115.1001 | 8.2993 | 0.39378 | 0.037289 | -0.034983 | 0.086729 | -0.047213 | 0.045422 | 0.099494 | -1.3367 | 0.27466 | -1.7212 | 8.4091 | -114.9994 | 8.2626 | 8.0841 | 8.5007 | 8.4229 | -115.48 | 113.3789 | -8.0246 | 113.7634 | 123.5092 | -123.2986 | -0.37994 | 0.1236 | 0.38452 | 123.1842 | 123.6008 | 0.10071 | 115.3748 | 113.7634 | 123.523 | 123.3627 | -0.37994 | 115.3748 | 113.7634 | 123.3627 | 0.10071 | 123.523 | -10.0204 | -123.7793
1978.9688 | 123.436 | -115.6723 | 7.7225 | -0.46071 | 0.038357 | -0.046732 | 0.064298 | -0.060031 | 0.018719 | 0.097358 | -1.387 | 0.2655 | -1.7807 | 7.7042 | -115.6906 | 7.6447 | 7.5302 | 7.8827 | 7.8644 | -116.0431 | 113.8916 | -7.457 | 114.2853 | 123.3765 | -123.4131 | -0.37079 | 0.14191 | 0.39368 | 123.2025 | 123.555 | -0.018311 | 115.9378 | 114.2853 | 123.5367 | 123.317 | -0.37079 | 115.9378 | 114.2853 | 123.317 | -0.018311 | 123.5367 | -9.5032 | -123.7656
1979.9219 | 123.4589 | -112.9623 | 10.4233 | -0.29287 | 0.033017 | -0.011485 | 0.091001 | -0.057894 | 0.052898 | 0.099494 | -1.062 | 0.28839 | -1.4923 | 10.4645 | -112.9486 | 10.4279 | 10.3226 | 10.6155 | 10.5606 | -113.3606 | 111.47 | -10.1349 | 111.9003 | 123.4268 | -123.3719 | -0.39826 | 0.13733 | 0.4303 | 123.2849 | 123.5779 | 0.013733 | 113.2507 | 111.9003 | 123.5229 | 123.3902 | -0.39826 | 113.2507 | 111.9003 | 123.3902 | 0.013733 | 123.5229 | -11.9156 | -123.7839
1980.9844 | 123.3948 | -116.1163 | 7.3059 | 0.31749 | 0.036221 | -0.036051 | 0.061094 | -0.048281 | 0.028332 | 0.1027 | -1.5152 | 0.27466 | -1.9318 | 7.3883 | -116.066 | 7.2739 | 7.0541 | 7.4799 | 7.457 | -116.4825 | 114.1846 | -7.0312 | 114.6011 | 123.5046 | -123.3719 | -0.36621 | 0.15106 | 0.41656 | 123.1705 | 123.5962 | 0.050354 | 116.391 | 114.6011 | 123.5733 | 123.3902 | -0.36621 | 116.391 | 114.6011 | 123.3902 | 0.050354 | 123.5733 | -9.2377 | -123.7885
1981.9219 | 123.436 | -113.2004 | 10.2036 | -0.094502 | 0.034085 | -0.016825 | 0.089933 | -0.033328 | 0.050762 | 0.095222 | -1.0986 | 0.28839 | -1.5244 | 10.2585 | -113.2736 | 10.0204 | 10.0983 | 10.4141 | 10.3043 | -113.5803 | 111.676 | -9.9152 | 112.1017 | 123.4589 | -123.4772 | -0.37994 | 0.10071 | 0.42572 | 123.2986 | 123.6145 | -0.073243 | 113.4888 | 112.1017 | 123.5046 | 123.2208 | -0.37994 | 113.4888 | 112.1017 | 123.2208 | -0.073243 | 123.5046 | -11.7279 | -123.7839
1982.9844 | 123.5046 | -115.9012 | 7.4432 | -0.018208 | 0.016995 | -0.0093484 | 0.052549 | -0.058962 | 0.018719 | 0.1027 | -1.6708 | 0.23346 | -1.799 | 7.2876 | -116.0385 | 7.2876 | 7.3151 | 7.5119 | 7.5485 | -116.3635 | 114.1022 | -7.2098 | 114.2303 | 123.1888 | -123.4817 | -0.46234 | 0.10529 | 0.12817 | 123.2162 | 123.4131 | -0.13733 | 116.1346 | 114.2303 | 123.4497 | 123.1888 | -0.46234 | 116.1346 | 114.2303 | 123.1888 | -0.13733 | 123.4497 | -9.2422 | -123.8068
1983.9219 | 123.4497 | -113.8 | 9.581 | -0.033467 | 0.053311 | -0.010416 | 0.087797 | -0.038668 | 0.04649 | 0.10697 | -1.062 | 0.27924 | -1.5839 | 9.6725 | -113.7817 | 9.5169 | 9.3842 | 9.7458 | 9.7092 | -114.2166 | 112.2162 | -9.3018 | 112.738 | 123.4726 | -123.3627 | -0.41657 | 0.12817 | 0.52185 | 123.1842 | 123.5458 | 0.018311 | 114.0793 | 112.738 | 123.5092 | 123.317 | -0.41657 | 114.0793 | 112.738 | 123.317 | 0.018311 | 123.5092 | -11.1649 | -123.7976
1984.9688 | 123.4955 | -113.9374 | 9.4162 | 0.088604 | 0.023404 | -0.024302 | 0.060026 | -0.058962 | 0.032604 | 0.099494 | -1.2863 | 0.23346 | -1.6296 | 9.4482 | -113.9374 | 9.3292 | 9.3063 | 9.5169 | 9.6405 | -114.3448 | 112.3077 | -9.1827 | 112.6511 | 123.3856 | -123.3536 | -0.40741 | 0.2243 | 0.34332 | 123.2437 | 123.4543 | 0 | 114.1708 | 112.6511 | 123.5779 | 123.2666 | -0.40741 | 114.1708 | 112.6511 | 123.2666 | 0 | 123.5779 | -11.0458 | -123.761
1985.9219 | 123.4451 | -113.8916 | 9.4711 | -0.32338 | 0.039425 | -0.037119 | 0.082456 | -0.055758 | 0.047558 | 0.10377 | -1.236 | 0.27924 | -1.5976 | 9.3246 | -114.0472 | 9.3979 | 9.3338 | 9.7 | 9.5306 | -114.3311 | 112.294 | -9.1919 | 112.6556 | 123.2162 | -123.5184 | -0.43945 | 0.05951 | 0.36163 | 123.2254 | 123.5916 | -0.15564 | 114.1708 | 112.6556 | 123.4222 | 123.2895 | -0.43945 | 114.1708 | 112.6556 | 123.2895 | -0.15564 | 123.4222 | -11.0687 | -123.8022
1986.9688 | 123.5321 | -113.8962 | 9.4391 | -0.12502 | 0.016995 | -0.022166 | 0.056821 | -0.060031 | 0.022991 | 0.10484 | -1.2268 | 0.23346 | -1.5564 | 9.4849 | -113.8641 | 9.4528 | 9.4849 | 9.5352 | 9.7229 | -114.2715 | 112.3398 | -9.2056 | 112.6694 | 123.381 | -123.3032 | -0.37537 | 0.28381 | 0.32959 | 123.381 | 123.4314 | 0.032043 | 114.1296 | 112.6694 | 123.6191 | 123.349 | -0.37537 | 114.1296 | 112.6694 | 123.349 | 0.032043 | 123.6191 | -10.9955 | -123.7106
1987.9219 | 123.3902 | -113.7314 | 9.6085 | -0.10976 | 0.035153 | -0.00080337 | 0.077116 | -0.062167 | 0.056103 | 0.098426 | -0.91095 | 0.28839 | -1.3458 | 9.6542 | -113.8321 | 9.4711 | 9.4025 | 9.6817 | 9.7046 | -114.2303 | 112.3856 | -9.3201 | 112.8204 | 123.3856 | -123.4406 | -0.49896 | 0.096131 | 0.43488 | 123.1339 | 123.4131 | -0.10071 | 114.0198 | 112.8204 | 123.436 | 123.2025 | -0.49896 | 114.0198 | 112.8204 | 123.2025 | -0.10071 | 123.436 | -10.9543 | -123.8388
1988.9844 | 123.5321 | -114.3356 | 8.9722 | -0.32338 | 0.0073818 | -0.034983 | 0.05789 | -0.062167 | 0.040081 | 0.1059 | -0.92926 | 0.2243 | -1.3641 | 8.9081 | -114.473 | 8.8531 | 8.8852 | 9.0729 | 9.1461 | -114.7797 | 112.9715 | -8.7479 | 113.4064 | 123.2437 | -123.4451 | -0.44403 | 0.17395 | 0.43488 | 123.2208 | 123.4085 | -0.13733 | 114.5599 | 113.4064 | 123.4818 | 123.1888 | -0.44403 | 114.5599 | 113.4064 | 123.1888 | -0.13733 | 123.4818 | -10.3363 | -123.7518
1989.9219 | 123.4589 | -115.329 | 8.0841 | -0.0029495 | 0.051175 | 0.00026463 | 0.073911 | -0.051486 | 0.049694 | 0.10697 | -1.03 | 0.28381 | -1.4465 | 8.107 | -115.2969 | 8.0292 | 7.9102 | 8.2352 | 8.2489 | -115.6998 | 113.8824 | -7.8003 | 114.299 | 123.436 | -123.381 | -0.37079 | 0.16479 | 0.41657 | 123.2391 | 123.5641 | 0.032043 | 115.6128 | 114.299 | 123.5779 | 123.3582 | -0.37079 | 115.6128 | 114.299 | 123.3582 | 0.032043 | 123.5779 | -9.5306 | -123.7839
1990.9844 | 123.587 | -112.8113 | 10.6339 | -0.30813 | 0.0041778 | -0.06489 | 0.053617 | -0.048281 | 0.028332 | 0.095222 | -0.88806 | 0.21973 | -1.355 | 8.9447 | -113.681 | 10.5011 | 10.7712 | 10.8673 | 9.9747 | -113.4109 | 111.4563 | -10.4141 | 111.9232 | 121.756 | -124.3149 | -0.59967 | -0.65918 | 0.46692 | 123.5825 | 123.6786 | -0.86975 | 113.031 | 111.9232 | 122.7859 | 123.3124 | -0.59967 | 113.031 | 111.9232 | 123.3124 | -0.86975 | 122.7859 | -11.9888 | -124.0448
1991.9219 | 123.5184 | -114.9261 | 8.4137 | 0.39378 | 0.03088 | -0.011485 | 0.060026 | -0.05469 | 0.021923 | 0.09629 | -1.0345 | 0.23346 | -1.4511 | 8.3633 | -115.0726 | 8.2993 | 8.3908 | 8.432 | 8.6151 | -115.3931 | 113.475 | -8.1802 | 113.8916 | 123.2895 | -123.4863 | -0.46692 | 0.20142 | 0.41657 | 123.317 | 123.3582 | -0.14648 | 115.1596 | 113.8916 | 123.5413 | 123.2254 | -0.46692 | 115.1596 | 113.8916 | 123.2254 | -0.14648 | 123.5413 | -9.8648 | -123.8068
1992.9844 | 123.5413 | -114.3356 | 9.0042 | -0.46071 | 0.011654 | -0.026438 | 0.056821 | -0.050418 | 0.026196 | 0.10056 | -0.90637 | 0.23804 | -1.3367 | 8.7891 | -114.5554 | 8.8394 | 8.9539 | 9.0775 | 9.1415 | -114.7842 | 112.999 | -8.7662 | 113.4293 | 123.1247 | -123.5596 | -0.44861 | 0.13733 | 0.4303 | 123.2895 | 123.4131 | -0.21973 | 114.5737 | 113.4293 | 123.4772 | 123.175 | -0.44861 | 114.5737 | 113.4293 | 123.175 | -0.21973 | 123.4772 | -10.3409 | -123.7885
1993.9219 | 123.4222 | -113.7772 | 9.5993 | -0.32338 | 0.04263 | -0.036051 | 0.084592 | -0.057894 | 0.033672 | 0.1027 | -1.1353 | 0.27924 | -1.5106 | 9.8785 | -113.5849 | 9.5535 | 9.2514 | 9.8465 | 9.7321 | -114.1434 | 112.2665 | -9.3201 | 112.6419 | 123.6557 | -123.1842 | -0.36621 | 0.13275 | 0.37537 | 123.0286 | 123.6237 | 0.19226 | 114.0564 | 112.6419 | 123.5092 | 123.3307 | -0.36621 | 114.0564 | 112.6419 | 123.3307 | 0.19226 | 123.5092 | -11.1099 | -123.7427
1994.9844 | 123.5641 | -114.9902 | 8.3313 | -0.063984 | 0.0095178 | -0.041392 | 0.062162 | -0.068576 | 0.017651 | 0.098426 | -1.268 | 0.25177 | -1.6388 | 8.2214 | -115.123 | 8.1894 | 8.2947 | 8.4091 | 8.5373 | -115.4022 | 113.3514 | -8.0795 | 113.7222 | 123.2117 | -123.4543 | -0.41199 | 0.20599 | 0.37079 | 123.2849 | 123.3994 | -0.13275 | 115.242 | 113.7222 | 123.5275 | 123.1796 | -0.41199 | 115.242 | 113.7222 | 123.1796 | -0.13275 | 123.5275 | -9.9701 | -123.7335
1995.9219 | 123.4543 | -114.2441 | 9.1553 | -0.29287 | 0.028744 | -0.027506 | 0.085661 | -0.055758 | 0.043285 | 0.090949 | -1.2589 | 0.27008 | -1.6571 | 9.2468 | -114.2441 | 9.0683 | 8.9447 | 9.2972 | 9.2972 | -114.6149 | 112.587 | -8.8852 | 112.9852 | 123.4909 | -123.3994 | -0.37079 | 0.14191 | 0.39825 | 123.1888 | 123.5413 | 0 | 114.5142 | 112.9852 | 123.5413 | 123.3124 | -0.37079 | 114.5142 | 112.9852 | 123.3124 | 0 | 123.5413 | -10.8124 | -123.7701
1996.9844 | 123.4039 | -115.1871 | 8.2443 | -0.38442 | 0.036221 | -0.032847 | 0.081388 | -0.049349 | 0.0294 | 0.094154 | -1.3504 | 0.28839 | -1.7029 | 8.2993 | -115.1047 | 8.2123 | 7.988 | 8.432 | 8.3679 | -115.5258 | 113.4842 | -7.9559 | 113.8367 | 123.4863 | -123.349 | -0.33875 | 0.1236 | 0.35248 | 123.175 | 123.6191 | 0.082398 | 115.4755 | 113.8367 | 123.555 | 123.3994 | -0.33875 | 115.4755 | 113.8367 | 123.3994 | 0.082398 | 123.555 | -9.9472 | -123.7701
1997.9219 | 123.4039 | -114.9948 | 8.4457 | -0.33864 | 0.039425 | -0.036051 | 0.069639 | -0.049349 | 0.05183 | 0.10697 | -1.3275 | 0.28381 | -1.6754 | 8.3908 | -114.9307 | 8.4457 | 8.1802 | 8.6014 | 8.5602 | -115.3107 | 113.3194 | -8.1619 | 113.6673 | 123.3856 | -123.3765 | -0.31586 | 0.11444 | 0.3479 | 123.175 | 123.5962 | 0.064087 | 115.2786 | 113.6673 | 123.555 | 123.4406 | -0.31586 | 115.2786 | 113.6673 | 123.4406 | 0.064087 | 123.555 | -10.1212 | -123.7564
1998.9844 | 123.4772 | -114.4775 | 8.876 | 0.37852 | 0.024472 | -0.034983 | 0.06323 | -0.056826 | 0.030468 | 0.1027 | -1.3504 | 0.25177 | -1.7212 | 8.8898 | -114.5096 | 8.7662 | 8.7616 | 8.9813 | 9.082 | -114.8804 | 112.7563 | -8.6243 | 113.1271 | 123.3673 | -123.3856 | -0.40283 | 0.20599 | 0.37079 | 123.2391 | 123.4589 | -0.032044 | 114.7293 | 113.1271 | 123.5596 | 123.2437 | -0.40283 | 114.7293 | 113.1271 | 123.2437 | -0.032044 | 123.5596 | -10.5972 | -123.7564
1999.9219 | 123.3994 | -113.562 | 9.8373 | -0.44545 | 0.026608 | -0.031779 | 0.083524 | -0.055758 | 0.035809 | 0.10163 | -1.1215 | 0.27924 | -1.4832 | 9.819 | -113.5941 | 9.7321 | 9.5581 | 10.0388 | 9.8877 | -113.942 | 112.0789 | -9.5581 | 112.4405 | 123.381 | -123.4314 | -0.37994 | 0.050354 | 0.36163 | 123.1201 | 123.6008 | -0.032043 | 113.8412 | 112.4405 | 123.4497 | 123.2941 | -0.37994 | 113.8412 | 112.4405 | 123.2941 | -0.032043 | 123.4497 | -11.3205 | -123.7793
2000.9688 | 123.4818 | -114.624 | 8.7021 | 0.10386 | 0.022336 | -0.033915 | 0.056821 | -0.062167 | 0.026196 | 0.088813 | -1.3275 | 0.2243 | -1.6434 | 8.4778 | -114.83 | 8.5693 | 8.6197 | 8.8852 | 8.8623 | -115.0177 | 112.9807 | -8.4778 | 113.2965 | 123.1018 | -123.5321 | -0.39368 | 0.16022 | 0.31586 | 123.2437 | 123.5092 | -0.20599 | 114.8483 | 113.2965 | 123.4863 | 123.1934 | -0.39368 | 114.8483 | 113.2965 | 123.1934 | -0.20599 | 123.4863 | -10.3455 | -123.7198
2001.9219 | 123.4543 | -113.3789 | 9.9976 | 0.042827 | 0.051175 | -0.010416 | 0.087797 | -0.066439 | 0.050762 | 0.093085 | -1.1856 | 0.27466 | -1.5747 | 10.1669 | -113.2919 | 9.993 | 9.8282 | 10.1852 | 10.1669 | -113.7634 | 111.8042 | -9.7229 | 112.1933 | 123.5458 | -123.2895 | -0.38452 | 0.16937 | 0.3891 | 123.2071 | 123.5641 | 0.086975 | 113.6536 | 112.1933 | 123.5458 | 123.3719 | -0.38452 | 113.6536 | 112.1933 | 123.3719 | 0.086975 | 123.5458 | -11.5723 | -123.761
2002.9844 | 123.5275 | -114.5645 | 8.757 | 0.027569 | 0.026608 | -0.037119 | 0.062162 | -0.072848 | 0.021923 | 0.092017 | -1.2909 | 0.24719 | -1.6525 | 8.7158 | -114.679 | 8.6609 | 8.6929 | 8.8577 | 8.9722 | -114.9628 | 112.912 | -8.5098 | 113.2736 | 123.2803 | -123.436 | -0.39825 | 0.21515 | 0.36163 | 123.2574 | 123.4222 | -0.11444 | 114.8117 | 113.2736 | 123.5367 | 123.2254 | -0.39825 | 114.8117 | 113.2736 | 123.2254 | -0.11444 | 123.5367 | -10.4095 | -123.7198
2003.9219 | 122.937 | -109.3185 | 13.678 | -0.3539 | 0.022336 | -0.028574 | 0.065366 | -0.053622 | 0.045422 | 0.099494 | -0.70953 | 0.26093 | -1.0712 | 13.6185 | -109.1995 | 13.5406 | 13.3759 | 13.916 | 13.6505 | -109.7443 | 108.2474 | -13.4171 | 108.609 | 122.937 | -122.8775 | -0.42572 | -0.027466 | 0.36163 | 122.6944 | 123.2346 | 0.11902 | 109.5795 | 108.609 | 122.9691 | 122.8592 | -0.42572 | 109.5795 | 108.609 | 122.8592 | 0.11902 | 122.9691 | -14.7491 | -123.4222
2004.9844 | 123.2712 | -112.2711 | 10.7941 | 0.18016 | 0.014859 | -0.024302 | 0.050413 | -0.057894 | 0.015514 | 0.085609 | -0.84686 | 0.21057 | -1.181 | 10.7391 | -112.3718 | 10.7117 | 10.73 | 10.881 | 10.9863 | -112.6785 | 111.0901 | -10.5835 | 111.4243 | 123.0103 | -123.1659 | -0.40741 | 0.19226 | 0.33417 | 123.0011 | 123.1522 | -0.10071 | 112.4817 | 111.4243 | 123.2574 | 122.9828 | -0.40741 | 112.4817 | 111.4243 | 122.9828 | -0.10071 | 123.2574 | -11.9751 | -123.4726
2005.9219 | 123.2346 | -110.2066 | 12.9456 | -0.4302 | 0.029812 | -0.021098 | 0.065366 | -0.057894 | 0.028332 | 0.083472 | -0.68665 | 0.27008 | -1.0941 | 11.1099 | -110.408 | 12.8265 | 10.9451 | 13.1058 | 12.9776 | -110.6232 | 109.1125 | -12.6755 | 109.52 | 121.3165 | -123.3536 | -0.41657 | 0.032043 | 0.40741 | 121.1517 | 123.3124 | -0.20142 | 110.4767 | 109.52 | 123.1842 | 123.0331 | -0.41657 | 110.4767 | 109.52 | 123.0331 | -0.20142 | 123.1842 | -14.0396 | -123.5687
2006.9844 | 123.23 | -108.5083 | 14.6393 | 0.042827 | 0.038357 | -0.011485 | 0.085661 | -0.055758 | 0.058239 | 0.082404 | -0.5722 | 0.26093 | -1.0071 | 12.0255 | -108.4808 | 14.6576 | 11.673 | 14.9048 | 14.7858 | -108.9157 | 107.5012 | -14.3784 | 107.9361 | 120.5338 | -123.1201 | -0.40741 | 0.14649 | 0.43488 | 120.1813 | 123.4131 | 0.027466 | 108.7692 | 107.9361 | 123.2941 | 123.1659 | -0.40741 | 108.7692 | 107.9361 | 123.1659 | 0.027466 | 123.2941 | -15.6464 | -123.555
2007.9219 | 123.23 | -111.8683 | 11.3388 | -0.3539 | 0.043698 | -0.0478 | 0.085661 | -0.063235 | 0.053967 | 0.085609 | -0.64087 | 0.28381 | -1.1032 | 11.4166 | -111.8134 | 11.3388 | 11.1191 | 11.554 | 11.4807 | -112.2208 | 110.7651 | -11.055 | 111.2274 | 123.2849 | -123.1522 | -0.35248 | 0.14191 | 0.46234 | 122.9874 | 123.4222 | 0.054932 | 112.1521 | 111.2274 | 123.349 | 123.2071 | -0.35248 | 112.1521 | 111.2274 | 123.2071 | 0.054932 | 123.349 | -12.442 | -123.5596
2008.9844 | 123.2986 | -111.9873 | 11.2061 | -0.46071 | 0.013791 | -0.037119 | 0.054685 | -0.064303 | 0.022991 | 0.093085 | -0.73242 | 0.25177 | -1.1032 | 11.2061 | -112.0743 | 11.1145 | 11.0367 | 11.3434 | 11.3525 | -112.4039 | 110.8841 | -10.9543 | 111.2549 | 123.1934 | -123.2803 | -0.41656 | 0.14648 | 0.37079 | 123.024 | 123.3307 | -0.086975 | 112.2391 | 111.2549 | 123.3398 | 123.1018 | -0.41656 | 112.2391 | 111.2549 | 123.1018 | -0.086975 | 123.3398 | -12.3093 | -123.6099
2009.9219 | 123.2758 | -112.1887 | 11.0367 | -0.39968 | 0.039425 | -0.034983 | 0.069639 | -0.058962 | 0.036877 | 0.097358 | -0.75989 | 0.27924 | -1.1261 | 11.1694 | -111.8729 | 11.0458 | 10.8536 | 11.2518 | 11.2061 | -112.5504 | 111.0626 | -10.7574 | 111.4288 | 123.3582 | -122.9095 | -0.36163 | 0.16937 | 0.36621 | 123.0423 | 123.4406 | 0.31586 | 112.468 | 111.4288 | 123.3948 | 123.2346 | -0.36163 | 112.468 | 111.4288 | 123.2346 | 0.31586 | 123.3948 | -12.1628 | -123.587
2010.9844 | 123.3444 | -111.0031 | 12.2086 | 0.22593 | 0.022336 | -0.024302 | 0.049345 | -0.070712 | 0.039013 | 0.098426 | -0.6958 | 0.22888 | -1.0574 | 12.1536 | -111.0672 | 12.1399 | 12.0895 | 12.355 | 12.3734 | -111.3785 | 109.9457 | -11.9797 | 110.3073 | 123.1567 | -123.2758 | -0.37537 | 0.16479 | 0.36163 | 123.0927 | 123.3582 | -0.064087 | 111.232 | 110.3073 | 123.3765 | 123.143 | -0.37537 | 111.232 | 110.3073 | 123.143 | -0.064087 | 123.3765 | -13.266 | -123.587
2011.9219 | 123.2758 | -111.2091 | 12.0438 | -0.30813 | 0.03088 | -0.045664 | 0.077116 | -0.062167 | 0.0294 | 0.09629 | -0.65002 | 0.27008 | -1.0391 | 12.1445 | -111.1588 | 12.0621 | 11.8195 | 12.2818 | 12.1628 | -111.557 | 110.17 | -11.7737 | 110.5591 | 123.3536 | -123.2025 | -0.3479 | 0.11902 | 0.3891 | 123.0286 | 123.4909 | 0.050354 | 111.4792 | 110.5591 | 123.3719 | 123.2712 | -0.3479 | 111.4792 | 110.5591 | 123.2712 | 0.050354 | 123.3719 | -13.0829 | -123.6008
2012.9688 | 123.3948 | -111.4197 | 11.7645 | 0.348 | 0.033017 | -0.026438 | 0.069639 | -0.053622 | 0.039013 | 0.088813 | -0.69122 | 0.22888 | -1.1032 | 11.8378 | -111.4609 | 11.6409 | 11.7325 | 11.8927 | 11.9385 | -111.8546 | 110.3165 | -11.5356 | 110.7285 | 123.2574 | -123.2254 | -0.43487 | 0.17395 | 0.41199 | 123.1522 | 123.3124 | -0.041198 | 111.6486 | 110.7285 | 123.3582 | 123.0606 | -0.43487 | 111.6486 | 110.7285 | 123.0606 | -0.041198 | 123.3582 | -12.8677 | -123.6191
2013.9219 | 123.2758 | -112.4268 | 10.8673 | 0.30223 | 0.033017 | -0.021098 | 0.084592 | -0.061099 | 0.042217 | 0.095222 | -0.85602 | 0.27466 | -1.2497 | 10.9222 | -112.3718 | 10.8673 | 10.6293 | 11.0687 | 10.968 | -112.7838 | 111.1771 | -10.5927 | 111.5707 | 123.349 | -123.2391 | -0.35705 | 0.10071 | 0.39368 | 123.056 | 123.4955 | 0.054932 | 112.7014 | 111.5707 | 123.3948 | 123.2941 | -0.35705 | 112.7014 | 111.5707 | 123.2941 | 0.054932 | 123.3948 | -12.117 | -123.6511
2014.9844 | 123.4039 | -111.8179 | 11.4212 | -0.048725 | 0.02554 | -0.052073 | 0.067503 | -0.074984 | 0.027264 | 0.098426 | -0.63629 | 0.24261 | -0.99335 | 11.3709 | -111.9141 | 11.261 | 11.3846 | 11.5128 | 11.5952 | -112.2025 | 110.8246 | -11.1786 | 111.1816 | 123.1888 | -123.3353 | -0.38452 | 0.17395 | 0.35706 | 123.2025 | 123.3307 | -0.09613 | 112.0605 | 111.1816 | 123.4131 | 123.0789 | -0.38452 | 112.0605 | 111.1816 | 123.0789 | -0.09613 | 123.4131 | -12.4146 | -123.6237
2015.9219 | 123.2574 | -111.2091 | 12.0895 | -0.4302 | 0.026608 | -0.024302 | 0.082456 | -0.069644 | 0.034741 | 0.098426 | -0.45776 | 0.28381 | -0.81024 | 12.117 | -111.2457 | 12.0255 | 11.7874 | 12.3871 | 12.1674 | -111.5479 | 110.3989 | -11.8057 | 110.7513 | 123.3261 | -123.3353 | -0.33875 | 0.077819 | 0.35248 | 122.9965 | 123.5962 | -0.036622 | 111.4929 | 110.7513 | 123.3765 | 123.2346 | -0.33875 | 111.4929 | 110.7513 | 123.2346 | -0.036622 | 123.3765 | -12.8998 | -123.6374
2016.9844 | 123.3994 | -110.7376 | 12.4786 | 0.74473 | 0.015927 | -0.041392 | 0.062162 | -0.067507 | 0.032604 | 0.085609 | -0.37994 | 0.18768 | -0.92468 | 12.5015 | -110.8658 | 12.3642 | 12.4741 | 12.5931 | 12.6617 | -111.1725 | 109.8129 | -12.291 | 110.3577 | 123.2391 | -123.3444 | -0.43487 | 0.1831 | 0.54474 | 123.2117 | 123.3307 | -0.12817 | 110.9253 | 110.3577 | 123.3994 | 123.1018 | -0.43487 | 110.9253 | 110.3577 | 123.1018 | -0.12817 | 123.3994 | -13.4033 | -123.6511
2017.9219 | 123.2986 | -110.9894 | 12.291 | -0.56752 | 0.031949 | -0.016825 | 0.070707 | -0.052554 | 0.033672 | 0.088813 | -0.41657 | 0.2655 | -0.76904 | 12.4054 | -110.9665 | 12.291 | 12.0895 | 12.5198 | 12.4237 | -111.319 | 110.2203 | -12.0255 | 110.5728 | 123.3948 | -123.2574 | -0.32959 | 0.13275 | 0.35248 | 123.0789 | 123.5092 | 0.022888 | 111.2549 | 110.5728 | 123.4131 | 123.2803 | -0.32959 | 111.2549 | 110.5728 | 123.2803 | 0.022888 | 123.4131 | -13.06 | -123.6099
2018.9844 | 123.4131 | -98.0347 | 25.145 | -4.8552 | 0.012723 | -0.022166 | 0.054685 | -0.05469 | 0.021923 | 0.095222 | -0.16479 | 0.20142 | -0.42572 | 9.5123 | -98.1812 | 25.1266 | 9.4803 | 25.3052 | 25.3464 | -98.4421 | 97.6089 | -24.9435 | 97.8699 | 107.547 | -123.3261 | -0.40741 | 0.20142 | 0.26092 | 107.515 | 123.3398 | -0.14648 | 98.2361 | 97.8699 | 123.381 | 123.1613 | -0.40741 | 98.2361 | 97.8699 | 123.1613 | -0.14648 | 123.381 | -25.5707 | -123.587
2019.9219 | 123.3078 | -97.998 | 25.2777 | -0.44545 | 0.028744 | -0.026438 | 0.061094 | -0.051486 | 0.0294 | 0.095222 | -0.054932 | 0.27008 | -0.42114 | 9.7137 | -97.998 | 25.3052 | 9.407 | 25.5157 | 25.351 | -98.3597 | 97.5769 | -25.0076 | 97.9431 | 107.7118 | -123.2758 | -0.36163 | 0.073242 | 0.36621 | 107.4051 | 123.5138 | 0 | 98.2681 | 97.9431 | 123.349 | 123.3032 | -0.36163 | 98.2681 | 97.9431 | 123.3032 | 0 | 123.349 | -25.6989 | -123.6374
2020.9844 | 123.4039 | -97.4533 | 25.7309 | 0.33274 | 0.033017 | -0.021098 | 0.055753 | -0.062167 | 0.030468 | 0.10697 | -0.07782 | 0.23804 | -0.46692 | 10.3455 | -97.5311 | 25.7355 | 10.2631 | 25.9323 | 25.8911 | -97.8882 | 96.9864 | -25.4929 | 97.3755 | 107.7988 | -123.262 | -0.43488 | 0.16022 | 0.3891 | 107.7164 | 123.3856 | -0.07782 | 97.6913 | 97.3755 | 123.3444 | 123.1888 | -0.43488 | 97.6913 | 97.3755 | 123.1888 | -0.07782 | 123.3444 | -26.1978 | -123.6191
2021.9219 | 123.3215 | -96.0846 | 27.1866 | -2.2155 | 0.044766 | -0.027506 | 0.083524 | -0.05469 | 0.039013 | 0.094154 | 0.082397 | 0.31128 | -0.19684 | 12.4924 | -96.0571 | 27.2324 | 12.1719 | 27.4292 | 27.2873 | -96.4554 | 95.8878 | -26.8753 | 96.167 | 108.577 | -123.2437 | -0.37079 | 0.10071 | 0.27924 | 108.2565 | 123.5138 | 0.027466 | 96.3959 | 96.167 | 123.3719 | 123.317 | -0.37079 | 96.3959 | 96.167 | 123.317 | 0.027466 | 123.3719 | -27.3834 | -123.642
2022.9844 | 123.4268 | -97.3068 | 25.8499 | -0.079243 | 0.015927 | -0.046732 | 0.052549 | -0.053622 | 0.022991 | 0.11018 | -0.091553 | 0.2655 | -0.45776 | 10.437 | -97.467 | 25.8087 | 10.4599 | 26.0147 | 26.0376 | -97.7783 | 96.8491 | -25.5844 | 97.2153 | 107.7438 | -123.317 | -0.4715 | 0.18768 | 0.36621 | 107.7667 | 123.3215 | -0.16022 | 97.5723 | 97.2153 | 123.3444 | 123.1155 | -0.4715 | 97.5723 | 97.2153 | 123.1155 | -0.16022 | 123.3444 | -26.3077 | -123.6282
2023.9219 | 123.3307 | -97.467 | 25.7812 | -0.46071 | 0.031949 | -0.0093484 | 0.067503 | -0.058962 | 0.0294 | 0.09629 | -0.036621 | 0.27466 | -0.4303 | 10.4553 | -97.5266 | 25.8591 | 10.1944 | 26.0513 | 25.9094 | -97.8607 | 97.0367 | -25.5066 | 97.4304 | 107.9224 | -123.3078 | -0.39368 | 0.12817 | 0.39368 | 107.6614 | 123.5184 | -0.059509 | 97.7417 | 97.4304 | 123.3765 | 123.3261 | -0.39368 | 97.7417 | 97.4304 | 123.3261 | -0.059509 | 123.3765 | -26.2115 | -123.642
2024.9844 | 123.3994 | -97.4899 | 25.7172 | 0.19541 | 0.011654 | -0.054209 | 0.051481 | -0.061099 | 0.024059 | 0.092017 | -0.11902 | 0.25177 | -0.48981 | 10.2722 | -97.5952 | 25.7034 | 10.2036 | 25.8957 | 25.8728 | -97.8973 | 97.0001 | -25.4654 | 97.3709 | 107.7621 | -123.3124 | -0.40741 | 0.15564 | 0.37079 | 107.6935 | 123.3856 | -0.10529 | 97.7417 | 97.3709 | 123.3627 | 123.1934 | -0.40741 | 97.7417 | 97.3709 | 123.1934 | -0.10529 | 123.3627 | -26.207 | -123.6145
2025.9219 | 123.349 | -97.4579 | 25.827 | -0.33864 | 0.036221 | -0.02537 | 0.08032 | -0.057894 | 0.043285 | 0.090949 | -0.036621 | 0.28381 | -0.42572 | 10.524 | -97.4899 | 25.8362 | 10.2585 | 26.0422 | 25.9323 | -97.8333 | 97.0322 | -25.5432 | 97.4213 | 107.9819 | -123.317 | -0.37537 | 0.10529 | 0.3891 | 107.7164 | 123.5001 | -0.032043 | 97.7417 | 97.4213 | 123.3902 | 123.2941 | -0.37537 | 97.7417 | 97.4213 | 123.2941 | -0.032043 | 123.3902 | -26.2527 | -123.6603
2026.9844 | 123.4131 | -96.8307 | 26.3855 | 0.19541 | 0.028744 | -0.018961 | 0.056821 | -0.062167 | 0.019787 | 0.094154 | -0.16937 | 0.24719 | -0.52643 | 11.3068 | -96.8903 | 26.3901 | 11.174 | 26.564 | 26.5549 | -97.2382 | 96.3043 | -26.1383 | 96.6614 | 108.1375 | -123.2758 | -0.40741 | 0.16937 | 0.35706 | 108.0048 | 123.3948 | -0.059509 | 97.0779 | 96.6614 | 123.3856 | 123.2208 | -0.40741 | 97.0779 | 96.6614 | 123.2208 | -0.059509 | 123.3856 | -26.9119 | -123.6237
2027.9219 | 123.4268 | -96.2082 | 26.976 | -2.5206 | 0.024472 | -0.016825 | 0.055753 | -0.060031 | 0.034741 | 0.099494 | -0.064087 | 0.21973 | -0.39368 | 12.1033 | -96.3455 | 26.9485 | 12.0758 | 27.1545 | 27.1454 | -96.6614 | 95.8145 | -26.7563 | 96.1441 | 108.3115 | -123.3215 | -0.45319 | 0.16937 | 0.32959 | 108.284 | 123.3627 | -0.13733 | 96.4279 | 96.1441 | 123.3536 | 123.1567 | -0.45319 | 96.4279 | 96.1441 | 123.1567 | -0.13733 | 123.3536 | -27.3697 | -123.6374
2028.9844 | 123.4406 | -96.7987 | 26.4175 | -0.27761 | 0.023404 | -0.043528 | 0.058958 | -0.051486 | 0.025128 | 0.10377 | -0.032043 | 0.23346 | -0.4303 | 11.2656 | -96.9452 | 26.358 | 11.2656 | 26.564 | 26.5778 | -97.229 | 96.3684 | -26.1841 | 96.7667 | 108.0643 | -123.3627 | -0.4303 | 0.16022 | 0.39826 | 108.0643 | 123.3627 | -0.14648 | 97.0322 | 96.7667 | 123.3765 | 123.1567 | -0.4303 | 97.0322 | 96.7667 | 123.1567 | -0.14648 | 123.3765 | -26.8478 | -123.6465
2029.9219 | 123.4085 | -95.9656 | 27.2415 | -0.3539 | 0.018063 | -0.039256 | 0.055753 | -0.061099 | 0.016583 | 0.098426 | 0.041199 | 0.23804 | -0.37994 | 12.5015 | -96.0938 | 27.2461 | 12.3917 | 27.4338 | 27.3834 | -96.3776 | 95.5856 | -27.0035 | 96.0068 | 108.4671 | -123.3353 | -0.41199 | 0.14191 | 0.42114 | 108.3572 | 123.3994 | -0.12817 | 96.2036 | 96.0068 | 123.349 | 123.2117 | -0.41199 | 96.2036 | 96.0068 | 123.2117 | -0.12817 | 123.349 | -27.6215 | -123.6191
2030.9844 | 123.4634 | -97.0139 | 26.1795 | 0.43956 | 0.02554 | -0.048869 | 0.05789 | -0.052554 | 0.040081 | 0.099494 | -0.11444 | 0.22888 | -0.54932 | 11.0046 | -97.1283 | 26.1383 | 11.0184 | 26.3351 | 26.3626 | -97.4716 | 96.4645 | -25.9506 | 96.8994 | 108.0185 | -123.3078 | -0.45776 | 0.18311 | 0.43488 | 108.0322 | 123.349 | -0.11444 | 97.2427 | 96.8994 | 123.3765 | 123.1522 | -0.45776 | 97.2427 | 96.8994 | 123.1522 | -0.11444 | 123.3765 | -26.7288 | -123.6511
2031.9219 | 123.4406 | -97.2748 | 25.9277 | -1.1626 | 0.013791 | -0.04246 | 0.050413 | -0.056826 | 0.035809 | 0.09629 | -0.022888 | 0.21057 | -0.40283 | 10.6018 | -97.4258 | 25.8911 | 10.5515 | 26.1017 | 26.1154 | -97.7142 | 96.8719 | -25.7172 | 97.2519 | 107.8766 | -123.3536 | -0.43945 | 0.18768 | 0.37994 | 107.8262 | 123.3765 | -0.15106 | 97.4854 | 97.2519 | 123.3902 | 123.1659 | -0.43945 | 97.4854 | 97.2519 | 123.1659 | -0.15106 | 123.3902 | -26.3306 | -123.642
2032.9844 | 123.4222 | -97.6227 | 25.6027 | 0.39378 | 0.02554 | -0.014689 | 0.048277 | -0.060031 | 0.052898 | 0.092017 | -0.17395 | 0.22888 | -0.58594 | 9.9106 | -97.8424 | 25.6073 | 10.199 | 25.6943 | 25.7767 | -98.053 | 97.0367 | -25.3738 | 97.4487 | 107.5333 | -123.4451 | -0.4303 | 0.17395 | 0.41199 | 107.8217 | 123.317 | -0.21973 | 97.8516 | 97.4487 | 123.3994 | 123.23 | -0.4303 | 97.8516 | 97.4487 | 123.23 | -0.21973 | 123.3994 | -26.1887 | -123.6557
2033.9219 | 123.4726 | -97.6639 | 25.5157 | -0.079243 | 0.020199 | -0.037119 | 0.050413 | -0.064303 | 0.036877 | 0.093085 | -0.14191 | 0.24719 | -0.53558 | 9.9792 | -97.8378 | 25.4791 | 10.0159 | 25.6577 | 25.708 | -98.1216 | 97.1283 | -25.2686 | 97.522 | 107.6431 | -123.3536 | -0.45776 | 0.19226 | 0.39368 | 107.6797 | 123.3215 | -0.17395 | 97.9111 | 97.522 | 123.3719 | 123.143 | -0.45776 | 97.9111 | 97.522 | 123.143 | -0.17395 | 123.3719 | -26.0513 | -123.6374
2034.9844 | 123.3948 | -96.2631 | 26.9577 | 0.31749 | 0.016995 | -0.044596 | 0.06323 | -0.061099 | 0.028332 | 0.085609 | -0.09613 | 0.23346 | -0.46234 | 12.117 | -96.3593 | 26.9348 | 12.0071 | 27.1454 | 27.0859 | -96.6705 | 95.8008 | -26.7242 | 96.167 | 108.3801 | -123.317 | -0.40741 | 0.12817 | 0.36621 | 108.2703 | 123.4085 | -0.09613 | 96.4966 | 96.167 | 123.349 | 123.1979 | -0.40741 | 96.4966 | 96.167 | 123.1979 | -0.09613 | 123.349 | -27.42 | -123.6282
2035.9219 | 123.436 | -97.3938 | 25.8133 | 1.7213 | 0.020199 | -0.052073 | 0.069639 | -0.069644 | 0.036877 | 0.098426 | -0.073242 | 0.22888 | -0.50354 | 10.4416 | -97.5082 | 25.7858 | 10.4004 | 25.9872 | 25.9964 | -97.8058 | 96.8903 | -25.5844 | 97.3206 | 107.8354 | -123.3215 | -0.41199 | 0.18311 | 0.4303 | 107.7942 | 123.381 | -0.11444 | 97.6227 | 97.3206 | 123.3902 | 123.1796 | -0.41199 | 97.6227 | 97.3206 | 123.1796 | -0.11444 | 123.3902 | -26.3168 | -123.6191
2036.9844 | 123.381 | -96.8857 | 26.3763 | 0.31749 | 0.041562 | -0.036051 | 0.081388 | -0.056826 | 0.047558 | 0.087745 | -0.064087 | 0.2655 | -0.47607 | 11.4212 | -96.8582 | 26.4267 | 11.1008 | 26.5778 | 26.4954 | -97.2565 | 96.4096 | -26.1108 | 96.8216 | 108.3069 | -123.2346 | -0.37079 | 0.11902 | 0.41199 | 107.9865 | 123.4634 | 0.027466 | 97.1512 | 96.8216 | 123.381 | 123.3124 | -0.37079 | 97.1512 | 96.8216 | 123.3124 | 0.027466 | 123.381 | -26.8524 | -123.6328
2037.9219 | 123.4451 | -96.6248 | 26.5915 | -0.33864 | 0.014859 | -0.041392 | 0.052549 | -0.066439 | 0.026196 | 0.093085 | -0.036621 | 0.2243 | -0.41657 | 11.467 | -96.6156 | 26.6876 | 11.618 | 26.6144 | 26.8021 | -97.0413 | 96.2082 | -26.3672 | 96.5881 | 108.0917 | -123.2071 | -0.41656 | 0.21057 | 0.37994 | 108.2428 | 123.2391 | 0.009155 | 96.8491 | 96.5881 | 123.4268 | 123.3124 | -0.41656 | 96.8491 | 96.5881 | 123.3124 | 0.009155 | 123.4268 | -27.0081 | -123.6328
2038.9844 | 123.4451 | -96.9498 | 26.2756 | -0.0029495 | 0.027676 | -0.023234 | 0.051481 | -0.061099 | 0.027264 | 0.098426 | -0.11902 | 0.24719 | -0.49439 | 11.0916 | -97.1054 | 26.207 | 11.0413 | 26.4175 | 26.4313 | -97.3892 | 96.4554 | -26.0284 | 96.8307 | 108.0414 | -123.381 | -0.43945 | 0.15564 | 0.37537 | 107.991 | 123.3673 | -0.15564 | 97.197 | 96.8307 | 123.381 | 123.1567 | -0.43945 | 97.197 | 96.8307 | 123.1567 | -0.15564 | 123.381 | -26.77 | -123.6649
2039.9219 | 123.3536 | -97.522 | 25.7629 | -0.46071 | 0.027676 | -0.0072124 | 0.066434 | -0.056826 | 0.032604 | 0.10163 | -0.10071 | 0.26093 | -0.48065 | 10.3683 | -97.6044 | 25.7401 | 10.1395 | 26.001 | 25.8362 | -97.9111 | 97.0413 | -25.502 | 97.4213 | 107.8903 | -123.3673 | -0.3891 | 0.073243 | 0.37994 | 107.6614 | 123.523 | -0.082397 | 97.7829 | 97.4213 | 123.3582 | 123.262 | -0.3891 | 97.7829 | 97.4213 | 123.262 | -0.082397 | 123.3582 | -26.2436 | -123.674
2040.9844 | 123.4039 | -98.0209 | 25.1999 | 0.45481 | 0.035153 | -0.036051 | 0.065366 | -0.063235 | 0.031536 | 0.073859 | -0.20142 | 0.2243 | -0.57678 | 9.5627 | -98.1033 | 25.1816 | 9.5261 | 25.3738 | 25.3464 | -98.4421 | 97.4442 | -24.9756 | 97.8195 | 107.5836 | -123.3032 | -0.42114 | 0.14648 | 0.37537 | 107.547 | 123.3948 | -0.082398 | 98.2452 | 97.8195 | 123.3673 | 123.2025 | -0.42114 | 98.2452 | 97.8195 | 123.2025 | -0.082398 | 123.3673 | -25.7767 | -123.642
2041.9219 | 123.4543 | -97.673 | 25.5203 | -0.32338 | 0.024472 | -0.041392 | 0.061094 | -0.051486 | 0.034741 | 0.093085 | -0.10071 | 0.22888 | -0.48981 | 10.0845 | -97.6913 | 25.4974 | 9.9976 | 25.7309 | 25.7126 | -98.1262 | 97.1832 | -25.2914 | 97.5723 | 107.7576 | -123.2117 | -0.45319 | 0.19226 | 0.3891 | 107.6706 | 123.4039 | -0.01831 | 97.9019 | 97.5723 | 123.3856 | 123.1705 | -0.45319 | 97.9019 | 97.5723 | 123.1705 | -0.01831 | 123.3856 | -26.0101 | -123.6465
2042.9844 | 123.3719 | -98.0209 | 25.1724 | 0.48533 | 0.026608 | -0.020029 | 0.062162 | -0.066439 | 0.047558 | 0.086677 | -0.10529 | 0.21973 | -0.55847 | 9.6725 | -98.0759 | 25.2045 | 9.6451 | 25.3647 | 25.4379 | -98.4146 | 97.4625 | -24.9527 | 97.9156 | 107.6935 | -123.2483 | -0.39368 | 0.2655 | 0.45319 | 107.666 | 123.3856 | -0.054932 | 98.2407 | 97.9156 | 123.4589 | 123.2254 | -0.39368 | 98.2407 | 97.9156 | 123.2254 | -0.054932 | 123.4589 | -25.7309 | -123.587
2043.9219 | 123.4772 | -98.4329 | 24.7787 | -0.20131 | 0.028744 | -0.030711 | 0.036527 | -0.062167 | 0.021923 | 0.1027 | -0.23346 | 0.22888 | -0.65002 | 8.9584 | -98.5519 | 24.7696 | 8.963 | 24.9664 | 24.9985 | -98.8403 | 97.7829 | -24.5499 | 98.1995 | 107.3914 | -123.3307 | -0.40741 | 0.21973 | 0.41657 | 107.3959 | 123.3994 | -0.11902 | 98.6618 | 98.1995 | 123.4314 | 123.2025 | -0.40741 | 98.6618 | 98.1995 | 123.2025 | -0.11902 | 123.4314 | -25.4288 | -123.6191
2044.9844 | 123.3994 | -97.8012 | 25.4654 | 0.47007 | 0.024472 | -0.0082804 | 0.073911 | -0.068576 | 0.049694 | 0.085609 | -0.1236 | 0.27008 | -0.54016 | 10.025 | -97.8516 | 25.4425 | 9.7412 | 25.6165 | 25.5432 | -98.2269 | 97.261 | -25.1953 | 97.6776 | 107.8262 | -123.317 | -0.42572 | 0.07782 | 0.41657 | 107.5424 | 123.4177 | -0.050354 | 98.0713 | 97.6776 | 123.3444 | 123.2437 | -0.42572 | 98.0713 | 97.6776 | 123.2437 | -0.050354 | 123.3444 | -26.0056 | -123.6923
2045.9219 | 123.4955 | -98.0942 | 25.1175 | -0.0029495 | 0.02554 | -0.040324 | 0.048277 | -0.062167 | 0.027264 | 0.097358 | -0.082397 | 0.23804 | -0.49439 | 9.375 | -97.6227 | 25.0534 | 9.4528 | 25.2411 | 25.3098 | -98.5245 | 97.5998 | -24.8795 | 98.0118 | 107.4692 | -122.7402 | -0.4303 | 0.19226 | 0.41199 | 107.547 | 123.3353 | 0.4715 | 98.3322 | 98.0118 | 123.4039 | 123.1476 | -0.4303 | 98.3322 | 98.0118 | 123.1476 | 0.4715 | 123.4039 | -25.6119 | -123.642
2046.9844 | 123.4085 | -99.3896 | 23.8724 | 0.19541 | 0.019131 | -0.068095 | 0.062162 | -0.065371 | 0.025128 | 0.084541 | -0.48065 | 0.25177 | -0.81482 | 7.6218 | -98.2361 | 23.8495 | 7.576 | 24.0372 | 24.0143 | -99.7879 | 98.5748 | -23.6206 | 98.909 | 107.0114 | -122.1085 | -0.39826 | 0.14191 | 0.33417 | 106.9656 | 123.4268 | 1.1536 | 99.6414 | 98.909 | 123.4039 | 123.2391 | -0.39826 | 99.6414 | 98.909 | 123.2391 | 1.1536 | 123.4039 | -24.6872 | -123.6603
2047.9219 | 123.4222 | -98.465 | 24.7696 | 0.21067 | 0.018063 | -0.038187 | 0.052549 | -0.065371 | 0.021923 | 0.086677 | -0.22888 | 0.19226 | -0.58136 | 8.9218 | -97.1558 | 24.7604 | 8.8898 | 24.9481 | 24.9023 | -98.8724 | 97.8836 | -24.5773 | 98.2361 | 107.3868 | -121.9254 | -0.40741 | 0.13275 | 0.35248 | 107.3547 | 123.4131 | 1.3092 | 98.6572 | 98.2361 | 123.3673 | 123.2254 | -0.40741 | 98.6572 | 98.2361 | 123.2254 | 1.3092 | 123.3673 | -25.351 | -123.642
2048.9844 | 123.4634 | -97.9477 | 25.2457 | -0.33864 | 0.018063 | -0.021098 | 0.051481 | -0.065371 | 0.0294 | 0.10163 | -0.054932 | 0.22888 | -0.45776 | 9.6359 | -96.8811 | 25.2319 | 9.6634 | 25.4105 | 25.4562 | -98.3826 | 97.4899 | -25.0168 | 97.8928 | 107.5836 | -122.1268 | -0.43488 | 0.21057 | 0.40283 | 107.6111 | 123.3582 | 1.0666 | 98.1766 | 97.8928 | 123.4039 | 123.1796 | -0.43488 | 98.1766 | 97.8928 | 123.1796 | 1.0666 | 123.4039 | -25.7034 | -123.6282
2049.9219 | 123.4955 | -98.0713 | 25.1541 | 0.01231 | 0.012723 | -0.037119 | 0.054685 | -0.065371 | 0.017651 | 0.090949 | -0.091553 | 0.24719 | -0.44403 | 9.4666 | -97.5082 | 25.1175 | 9.5398 | 25.2914 | 25.3372 | -98.5107 | 97.6273 | -24.9069 | 97.9797 | 107.5378 | -122.6624 | -0.43945 | 0.18311 | 0.35248 | 107.6111 | 123.3627 | 0.56305 | 98.3185 | 97.9797 | 123.4085 | 123.1888 | -0.43945 | 98.3185 | 97.9797 | 123.1888 | 0.56305 | 123.4085 | -25.5981 | -123.6649
2050.9844 | 123.4543 | -99.0555 | 24.1837 | 0.47007 | 0.034085 | -0.026438 | 0.077116 | -0.060031 | 0.039013 | 0.095222 | -0.30212 | 0.27466 | -0.71411 | 8.1436 | -98.5016 | 24.1379 | 8.0704 | 24.353 | 24.3164 | -99.4675 | 98.3414 | -23.909 | 98.7534 | 107.1991 | -122.6852 | -0.41199 | 0.13275 | 0.41199 | 107.1259 | 123.4085 | 0.55389 | 99.3301 | 98.7534 | 123.3719 | 123.1934 | -0.41199 | 99.3301 | 98.7534 | 123.1934 | 0.55389 | 123.3719 | -24.8978 | -123.6511
2051.9219 | 123.4634 | -99.028 | 24.1745 | -0.23183 | 0.023404 | -0.012553 | 0.052549 | -0.065371 | 0.017651 | 0.10056 | -0.21973 | 0.23346 | -0.6134 | 8.0383 | -98.1583 | 24.1104 | 8.075 | 24.3164 | 24.3393 | -99.4858 | 98.4146 | -23.941 | 98.8083 | 107.0663 | -122.3328 | -0.45776 | 0.16479 | 0.39368 | 107.103 | 123.3444 | 0.86975 | 99.2615 | 98.8083 | 123.3673 | 123.1384 | -0.45776 | 99.2615 | 98.8083 | 123.1384 | 0.86975 | 123.3673 | -24.7879 | -123.6603
2052.9844 | 123.4268 | -98.9639 | 24.2661 | 0.37852 | 0.026608 | -0.028574 | 0.054685 | -0.062167 | 0.030468 | 0.094154 | -0.3067 | 0.23346 | -0.70953 | 8.2169 | -97.6822 | 24.2203 | 8.1665 | 24.4217 | 24.4034 | -99.3759 | 98.2544 | -24.0326 | 98.6572 | 107.1808 | -121.9482 | -0.41199 | 0.13733 | 0.40283 | 107.1304 | 123.3856 | 1.2817 | 99.1974 | 98.6572 | 123.3673 | 123.1842 | -0.41199 | 99.1974 | 98.6572 | 123.1842 | 1.2817 | 123.3673 | -24.9756 | -123.642
2053.9219 | 123.4772 | -99.321 | 23.8998 | -0.21657 | 0.023404 | -0.031779 | 0.056821 | -0.058962 | 0.025128 | 0.084541 | -0.13275 | 0.23804 | -0.54932 | 7.6767 | -97.0596 | 23.8449 | 7.6492 | 24.2203 | 24.0921 | -99.765 | 98.7717 | -23.6618 | 99.1882 | 106.9977 | -120.9595 | -0.44403 | 0.19226 | 0.41657 | 106.9702 | 123.5413 | 2.2614 | 99.559 | 99.1882 | 123.4131 | 123.1659 | -0.44403 | 99.559 | 99.1882 | 123.1659 | 2.2614 | 123.4131 | -24.4492 | -123.6649
2054.9844 | 123.4772 | -99.2523 | 23.9822 | 0.36326 | 0.019131 | -0.0061444 | 0.070707 | -0.065371 | 0.033672 | 0.088813 | -0.18768 | 0.2243 | -0.63629 | 7.8552 | -97.0596 | 23.909 | 7.8094 | 24.1104 | 24.1241 | -99.6872 | 98.616 | -23.7579 | 99.0646 | 107.1075 | -121.0419 | -0.43488 | 0.14191 | 0.44861 | 107.0618 | 123.3627 | 2.1927 | 99.4766 | 99.0646 | 123.3765 | 123.1613 | -0.43488 | 99.4766 | 99.0646 | 123.1613 | 2.1927 | 123.3765 | -24.6185 | -123.6694
2055.9219 | 123.468 | -99.4308 | 23.7854 | -0.14028 | 0.022336 | -0.02537 | 0.047208 | -0.064303 | 0.031536 | 0.094154 | -0.3479 | 0.25177 | -0.66834 | 7.5485 | -97.7646 | 23.7213 | 7.5073 | 23.9639 | 23.9639 | -99.852 | 98.7625 | -23.5336 | 99.0829 | 106.9794 | -121.55 | -0.42114 | 0.17853 | 0.32044 | 106.9382 | 123.3948 | 1.6663 | 99.6826 | 99.0829 | 123.3948 | 123.1522 | -0.42114 | 99.6826 | 99.0829 | 123.1522 | 1.6663 | 123.3948 | -24.4537 | -123.6374
2056.9844 | 123.4955 | -99.9344 | 23.3002 | 0.43956 | 0.031949 | 0.01415 | 0.062162 | -0.065371 | 0.047558 | 0.09629 | -0.41199 | 0.24261 | -0.82398 | 6.8802 | -100.0397 | 23.2498 | 6.839 | 23.4741 | 23.4512 | -100.3647 | 99.1104 | -23.0576 | 99.5224 | 106.8146 | -123.3398 | -0.4303 | 0.15106 | 0.41199 | 106.7734 | 123.4085 | -0.10529 | 100.177 | 99.5224 | 123.3856 | 123.1842 | -0.4303 | 100.177 | 99.5224 | 123.1842 | -0.10529 | 123.3856 | -24.1241 | -123.6649
2057.9219 | 123.4543 | -99.8886 | 23.3185 | 0.28697 | 0.015927 | -0.044596 | 0.047208 | -0.07178 | 0.032604 | 0.093085 | -0.4303 | 0.21515 | -0.79193 | 6.8481 | -100.0214 | 23.2956 | 6.8298 | 23.497 | 23.5016 | -100.3235 | 99.0967 | -23.1033 | 99.4583 | 106.7368 | -123.3398 | -0.43488 | 0.18311 | 0.36163 | 106.7184 | 123.3856 | -0.13275 | 100.1038 | 99.4583 | 123.3902 | 123.1842 | -0.43488 | 100.1038 | 99.4583 | 123.1842 | -0.13275 | 123.3902 | -24.1104 | -123.642
2058.9844 | 123.4955 | -99.8154 | 23.3917 | 3.3082 | 0.040494 | -0.031779 | 0.065366 | -0.068576 | 0.049694 | 0.090949 | -0.54016 | 0.19684 | -0.89722 | 6.9855 | -99.8932 | 23.378 | 6.9901 | 23.5519 | 23.5703 | -100.2457 | 98.9182 | -23.1949 | 99.2752 | 106.8008 | -123.2849 | -0.4303 | 0.17853 | 0.35706 | 106.8054 | 123.3673 | -0.077819 | 100.0122 | 99.2752 | 123.3856 | 123.1934 | -0.4303 | 100.0122 | 99.2752 | 123.1934 | -0.077819 | 123.3856 | -24.2889 | -123.6374
2059.9219 | 123.5001 | -99.1699 | 24.0463 | -0.0029495 | 0.021267 | -0.04246 | 0.056821 | -0.067507 | 0.032604 | 0.09629 | -0.33875 | 0.24719 | -0.74158 | 7.8552 | -99.3484 | 23.9822 | 7.9239 | 24.1608 | 24.2203 | -99.6277 | 98.4283 | -23.7991 | 98.8312 | 107.0251 | -123.3948 | -0.45776 | 0.17395 | 0.40283 | 107.0938 | 123.3307 | -0.17853 | 99.4171 | 98.8312 | 123.3902 | 123.1522 | -0.45776 | 99.4171 | 98.8312 | 123.1522 | -0.17853 | 123.3902 | -24.7879 | -123.674
2060.9688 | 123.3902 | -99.4446 | 23.8312 | 0.042827 | 0.051175 | -0.0082804 | 0.08032 | -0.056826 | 0.05183 | 0.089881 | -0.19684 | 0.28381 | -0.78735 | 7.7545 | -99.4034 | 23.8998 | 7.4799 | 24.1013 | 23.9822 | -99.8337 | 98.6572 | -23.5474 | 99.2477 | 107.1991 | -123.2346 | -0.3891 | 0.15106 | 0.59052 | 106.9244 | 123.5458 | 0.041199 | 99.7284 | 99.2477 | 123.4268 | 123.3444 | -0.3891 | 99.7284 | 99.2477 | 123.3444 | 0.041199 | 123.4268 | -24.6185 | -123.6649
2061.9219 | 123.4497 | -99.4629 | 23.7671 | 0.01231 | 0.02554 | -0.049937 | 0.041868 | -0.060031 | 0.028332 | 0.10163 | -0.62256 | 0.21973 | -0.82855 | 7.5256 | -99.5728 | 23.7534 | 7.5119 | 23.9319 | 23.9365 | -99.8795 | 98.6343 | -23.5474 | 98.8403 | 106.9885 | -123.3398 | -0.41657 | 0.16937 | 0.20599 | 106.9748 | 123.3948 | -0.10986 | 99.6826 | 98.8403 | 123.3994 | 123.2162 | -0.41657 | 99.6826 | 98.8403 | 123.2162 | -0.10986 | 123.3994 | -24.5956 | -123.6465
2062.9844 | 123.4772 | -111.2549 | 11.9843 | 0.63792 | 0.033017 | -0.0082804 | 0.081388 | -0.070712 | 0.039013 | 0.094154 | -0.89722 | 0.25177 | -1.3138 | 8.67 | -111.232 | 11.9339 | 8.5236 | 12.0529 | 12.2452 | -111.7081 | 109.9411 | -11.7325 | 110.3577 | 119.9249 | -123.2162 | -0.45319 | 0.26092 | 0.41656 | 119.7784 | 123.3078 | 0.022888 | 111.5067 | 110.3577 | 123.5001 | 123.1888 | -0.45319 | 111.5067 | 110.3577 | 123.1888 | 0.022888 | 123.5001 | -13.298 | -123.6923
2063.9219 | 123.436 | -114.4455 | 8.8394 | 0.18016 | 0.026608 | -0.033915 | 0.069639 | -0.072848 | 0.020855 | 0.09629 | -1.1032 | 0.21057 | -1.4511 | 8.8257 | -114.5279 | 8.7341 | 8.7479 | 8.9676 | 9.05 | -114.83 | 112.9944 | -8.6288 | 113.3423 | 123.2712 | -123.3673 | -0.38452 | 0.21057 | 0.3479 | 123.1934 | 123.4131 | -0.082397 | 114.6561 | 113.3423 | 123.4955 | 123.1796 | -0.38452 | 114.6561 | 113.3423 | 123.1796 | -0.082397 | 123.4955 | -10.2905 | -123.6694
2064.9844 | 123.3582 | -114.4913 | 8.8303 | 0.01231 | 0.04797 | -0.015757 | 0.093137 | -0.064303 | 0.060375 | 0.086677 | -1.0529 | 0.28839 | -1.4694 | 8.9035 | -114.4592 | 8.7799 | 8.6014 | 9.0134 | 8.9355 | -114.8849 | 113.0219 | -8.5419 | 113.4384 | 123.3948 | -123.2895 | -0.39368 | 0.10529 | 0.41657 | 123.0927 | 123.5046 | 0.032043 | 114.7797 | 113.4384 | 123.4268 | 123.2712 | -0.39368 | 114.7797 | 113.4384 | 123.2712 | 0.032043 | 123.4268 | -10.2997 | -123.7152
2065.9219 | 123.436 | -114.8758 | 8.4183 | 0.27171 | 0.027676 | -0.028574 | 0.066434 | -0.065371 | 0.016583 | 0.089881 | -1.1124 | 0.24719 | -1.474 | 8.4229 | -114.3219 | 8.3313 | 8.3359 | 8.5556 | 8.606 | -115.2603 | 113.4018 | -8.1711 | 113.7634 | 123.2986 | -122.7402 | -0.38452 | 0.18768 | 0.36163 | 123.2117 | 123.4314 | 0.55389 | 115.123 | 113.7634 | 123.4818 | 123.2071 | -0.38452 | 115.123 | 113.7634 | 123.2071 | 0.55389 | 123.4818 | -9.8923 | -123.6786
2066.9688 | 123.4039 | -114.8712 | 8.4824 | -0.52175 | 0.03088 | -0.011485 | 0.081388 | -0.065371 | 0.05183 | 0.094154 | -1.0025 | 0.28839 | -1.4282 | 8.638 | -114.7751 | 8.4732 | 8.3267 | 8.6609 | 8.6014 | -115.21 | 113.443 | -8.194 | 113.8687 | 123.5092 | -123.2574 | -0.33875 | 0.11902 | 0.42572 | 123.1979 | 123.5321 | 0.096131 | 115.1596 | 113.8687 | 123.4726 | 123.3444 | -0.33875 | 115.1596 | 113.8687 | 123.3444 | 0.096131 | 123.4726 | -9.9106 | -123.6923
2067.9219 | 123.4818 | -114.7797 | 8.4641 | 0.47007 | 0.03088 | -0.038187 | 0.060026 | -0.066439 | 0.043285 | 0.10377 | -0.89264 | 0.25177 | -1.3412 | 8.4412 | -114.3539 | 8.3633 | 8.4412 | 8.5464 | 8.6838 | -115.2191 | 113.4384 | -8.2123 | 113.887 | 123.2208 | -122.818 | -0.43945 | 0.21973 | 0.44861 | 123.2208 | 123.3261 | 0.42572 | 115.0314 | 113.887 | 123.4634 | 123.143 | -0.43945 | 115.0314 | 113.887 | 123.143 | 0.42572 | 123.4634 | -9.8053 | -123.6832
2068.9844 | 123.3902 | -112.1063 | 11.1832 | -0.65908 | 0.038357 | -0.014689 | 0.092069 | -0.042941 | 0.056103 | 0.092017 | -0.99792 | 0.27008 | -1.4282 | 8.6609 | -112.0468 | 11.261 | 8.432 | 11.4487 | 11.3846 | -112.4771 | 110.6781 | -10.9131 | 111.1084 | 120.7672 | -123.23 | -0.37079 | 0.20142 | 0.4303 | 120.5383 | 123.555 | 0.059509 | 112.3764 | 111.1084 | 123.4909 | 123.3673 | -0.37079 | 112.3764 | 111.1084 | 123.3673 | 0.059509 | 123.4909 | -12.6114 | -123.6603
2069.9219 | 123.4177 | -112.2025 | 11.1053 | 0.37852 | 0.020199 | -0.04246 | 0.062162 | -0.058962 | 0.027264 | 0.089881 | -1.1948 | 0.24261 | -1.5472 | 8.075 | -111.2595 | 11.0367 | 8.0612 | 11.293 | 11.2976 | -112.5595 | 110.6552 | -10.8627 | 111.0077 | 120.2774 | -122.3648 | -0.35706 | 0.19226 | 0.35248 | 120.2637 | 123.4955 | 0.94299 | 112.4451 | 111.0077 | 123.5001 | 123.2391 | -0.35706 | 112.4451 | 111.0077 | 123.2391 | 0.94299 | 123.5001 | -12.6526 | -123.6649
2070.9844 | 123.3856 | -112.8662 | 10.4599 | -0.15554 | 0.041562 | -0.012553 | 0.086729 | -0.060031 | 0.055035 | 0.084541 | -1.1124 | 0.28839 | -1.5335 | 7.7591 | -111.438 | 10.3912 | 7.5302 | 10.6201 | 10.5927 | -113.2919 | 111.3327 | -10.1715 | 111.7538 | 120.6253 | -121.8979 | -0.42572 | 0.13275 | 0.42114 | 120.3964 | 123.4863 | 1.4282 | 113.1546 | 111.7538 | 123.4589 | 123.2574 | -0.42572 | 113.1546 | 111.7538 | 123.2574 | 1.4282 | 123.4589 | -11.9934 | -123.7518
2071.9219 | 123.4589 | -112.5641 | 10.7025 | 2.3316 | 0.028744 | -0.0093484 | 0.06323 | -0.063235 | 0.033672 | 0.092017 | -1.2131 | 0.21973 | -1.5747 | 8.0658 | -110.5087 | 10.5606 | 8.0566 | 10.7986 | 10.8444 | -112.999 | 110.9894 | -10.4828 | 111.351 | 120.6299 | -121.2112 | -0.43488 | 0.14191 | 0.36163 | 120.6207 | 123.3627 | 2.0554 | 112.7838 | 111.351 | 123.4085 | 123.1247 | -0.43488 | 112.7838 | 111.351 | 123.1247 | 2.0554 | 123.4085 | -12.2772 | -123.7015
2072.9844 | 123.4497 | -112.6556 | 10.6064 | 0.40904 | 0.040494 | -0.041392 | 0.081388 | -0.063235 | 0.043285 | 0.089881 | -1.1627 | 0.27008 | -1.5518 | 7.9285 | -111.1908 | 10.5331 | 7.8552 | 10.7574 | 10.762 | -113.0722 | 111.1038 | -10.3363 | 111.4929 | 120.5841 | -121.7972 | -0.41656 | 0.15564 | 0.3891 | 120.5109 | 123.4131 | 1.4648 | 112.9257 | 111.4929 | 123.4177 | 123.1888 | -0.41656 | 112.9257 | 111.4929 | 123.1888 | 1.4648 | 123.4177 | -12.1582 | -123.6786
2073.9219 | 123.4589 | -112.2299 | 11.0229 | 0.4243 | 0.021267 | -0.028574 | 0.064298 | -0.068576 | 0.049694 | 0.089881 | -1.0941 | 0.24261 | -1.5015 | 8.194 | -111.2457 | 10.9497 | 8.2443 | 11.1649 | 11.2381 | -112.6511 | 110.7285 | -10.7803 | 111.1359 | 120.4239 | -122.2687 | -0.42114 | 0.21515 | 0.40741 | 120.4742 | 123.3948 | 0.98419 | 112.4725 | 111.1359 | 123.468 | 123.1796 | -0.42114 | 112.4725 | 111.1359 | 123.1796 | 0.98419 | 123.468 | -12.5244 | -123.674
2074.9688 | 123.3994 | -112.326 | 10.9909 | -0.033467 | 0.036221 | -0.013621 | 0.088865 | -0.063235 | 0.055035 | 0.093085 | -0.99792 | 0.27924 | -1.4236 | 8.3267 | -111.3464 | 10.9039 | 8.3313 | 11.2427 | 11.0825 | -112.7335 | 110.9024 | -10.7117 | 111.3281 | 120.6528 | -122.3373 | -0.40741 | 0.091552 | 0.42572 | 120.6573 | 123.5687 | 0.97961 | 112.6053 | 111.3281 | 123.4085 | 123.23 | -0.40741 | 112.6053 | 111.3281 | 123.23 | 0.97961 | 123.4085 | -12.4146 | -123.7244
2075.9219 | 123.4909 | -112.262 | 10.9863 | 0.57688 | 0.03088 | -0.013621 | 0.065366 | -0.053622 | 0.047558 | 0.097358 | -1.1581 | 0.23346 | -1.5884 | 8.2077 | -112.3901 | 10.849 | 8.2352 | 11.0825 | 11.1786 | -112.7106 | 110.6735 | -10.7529 | 111.1038 | 120.4697 | -123.3765 | -0.44861 | 0.19226 | 0.4303 | 120.4971 | 123.3444 | -0.12817 | 112.4954 | 111.1038 | 123.4406 | 123.111 | -0.44861 | 112.4954 | 111.1038 | 123.111 | -0.12817 | 123.4406 | -12.5748 | -123.6969
2076.9844 | 123.3353 | -112.8204 | 10.5377 | 0.24119 | 0.045834 | -0.020029 | 0.074979 | -0.05469 | 0.055035 | 0.092017 | -1.2909 | 0.29755 | -1.6434 | 8.0475 | -112.7197 | 10.5286 | 7.7545 | 10.7483 | 10.6339 | -113.1866 | 111.1771 | -10.2402 | 111.5295 | 120.8679 | -123.2574 | -0.36621 | 0.09613 | 0.35248 | 120.575 | 123.5687 | 0.10071 | 113.118 | 111.5295 | 123.4543 | 123.349 | -0.36621 | 113.118 | 111.5295 | 123.349 | 0.10071 | 123.4543 | -12.1811 | -123.7244
2077.9219 | 123.4818 | -112.9257 | 10.3226 | 0.43956 | 0.034085 | -0.016825 | 0.062162 | -0.060031 | 0.043285 | 0.093085 | -1.2589 | 0.24261 | -1.6525 | 7.869 | -113.0402 | 10.199 | 7.901 | 10.4279 | 10.524 | -113.4064 | 111.2732 | -10.08 | 111.6669 | 120.7947 | -123.3627 | -0.48065 | 0.20142 | 0.39368 | 120.8267 | 123.3536 | -0.11444 | 113.1683 | 111.6669 | 123.4497 | 123.1247 | -0.48065 | 113.1683 | 111.6669 | 123.1247 | -0.11444 | 123.4497 | -11.9751 | -123.7289
2078.9844 | 123.3856 | -113.031 | 10.2722 | -3.9702 | 0.038357 | -0.028574 | 0.079252 | -0.055758 | 0.048626 | 0.090949 | -1.3275 | 0.3067 | -1.6251 | 8.2397 | -113.0585 | 10.2402 | 8.0521 | 10.4645 | 10.4004 | -113.4659 | 111.4059 | -9.9655 | 111.7035 | 121.2708 | -123.3307 | -0.43487 | 0.12817 | 0.29755 | 121.0831 | 123.4955 | -0.027466 | 113.3377 | 111.7035 | 123.4314 | 123.2712 | -0.43487 | 113.3377 | 111.7035 | 123.2712 | -0.027466 | 123.4314 | -11.8973 | -123.7381
2079.9219 | 123.4634 | -113.1409 | 10.1212 | 0.33274 | 0.026608 | -0.041392 | 0.061094 | -0.066439 | 0.039013 | 0.090949 | -1.2543 | 0.2243 | -1.6479 | 7.8186 | -113.2233 | 9.9014 | 7.6767 | 10.2448 | 10.3043 | -113.5574 | 111.4929 | -9.8969 | 111.8866 | 120.9595 | -123.3444 | -0.41657 | 0.1831 | 0.39368 | 120.8176 | 123.3856 | -0.082398 | 113.3652 | 111.8866 | 123.4451 | 123.0423 | -0.41657 | 113.3652 | 111.8866 | 123.0423 | -0.082398 | 123.4451 | -11.7691 | -123.6786
2080.9844 | 123.381 | -100.0214 | 23.3002 | -0.36916 | 0.054379 | -0.016825 | 0.072843 | -0.051486 | 0.05183 | 0.1027 | -0.60425 | 0.29755 | -0.99792 | 6.9305 | -99.3027 | 23.3368 | 6.6467 | 23.5428 | 23.3917 | -100.4059 | 99.0234 | -23.0026 | 99.4171 | 106.9519 | -122.6028 | -0.38452 | 0.091553 | 0.39368 | 106.6681 | 123.5641 | 0.71869 | 100.3189 | 99.4171 | 123.4131 | 123.3582 | -0.38452 | 100.3189 | 99.4171 | 123.3582 | 0.71869 | 123.4131 | -24.2981 | -123.7061
2081.9219 | 123.5001 | -99.8291 | 23.3688 | 0.43956 | 0.024472 | -0.032847 | 0.052549 | -0.052554 | 0.040081 | 0.098426 | -0.58594 | 0.2243 | -1.0071 | 6.9397 | -99.9847 | 23.3368 | 6.9992 | 23.5382 | 23.5474 | -100.3052 | 98.822 | -23.1445 | 99.2432 | 106.7688 | -123.3536 | -0.47607 | 0.17853 | 0.42114 | 106.8283 | 123.3673 | -0.15564 | 100.0534 | 99.2432 | 123.3765 | 123.1659 | -0.47607 | 100.0534 | 99.2432 | 123.1659 | -0.15564 | 123.3765 | -24.3759 | -123.674
2082.9844 | 123.4497 | -99.9756 | 23.291 | -0.14028 | 0.012723 | -0.04246 | 0.045072 | -0.042941 | 0.040081 | 0.089881 | -0.6546 | 0.23346 | -0.97504 | 6.8115 | -100.0626 | 23.2819 | 6.7841 | 23.465 | 23.4467 | -100.3967 | 99.0005 | -23.0576 | 99.321 | 106.7871 | -123.3536 | -0.42114 | 0.15564 | 0.32044 | 106.7596 | 123.4406 | -0.086975 | 100.209 | 99.321 | 123.4222 | 123.2574 | -0.42114 | 100.209 | 99.321 | 123.2574 | -0.086975 | 123.4222 | -24.2661 | -123.6877
2083.9219 | 123.4909 | -113.0676 | 10.1761 | 0.6837 | 0.031949 | -0.015757 | 0.081388 | -0.067507 | 0.048626 | 0.095222 | -1.1765 | 0.2243 | -1.6022 | 7.8644 | -113.1775 | 10.0525 | 7.9102 | 10.2768 | 10.3867 | -113.5208 | 111.4655 | -9.9518 | 111.8912 | 120.932 | -123.3536 | -0.45319 | 0.21057 | 0.42572 | 120.9778 | 123.3444 | -0.10986 | 113.2919 | 111.8912 | 123.4543 | 123.1201 | -0.45319 | 113.2919 | 111.8912 | 123.1201 | -0.10986 | 123.4543 | -11.7783 | -123.6969
2084.9844 | 123.3719 | -113.2141 | 10.1395 | -0.33864 | 0.044766 | -0.028574 | 0.069639 | -0.060031 | 0.04649 | 0.088813 | -1.2131 | 0.30212 | -1.5793 | 7.8918 | -113.2141 | 10.1257 | 7.5806 | 10.3455 | 10.2539 | -113.5849 | 111.6348 | -9.8373 | 112.001 | 121.106 | -123.3536 | -0.37079 | 0.11444 | 0.36621 | 120.7947 | 123.5596 | 0 | 113.5162 | 112.001 | 123.468 | 123.3398 | -0.37079 | 113.5162 | 112.001 | 123.3398 | 0 | 123.468 | -11.7188 | -123.7244
2085.9219 | 123.4818 | -100.2365 | 23.0118 | 0.348 | 0.029812 | -0.041392 | 0.064298 | -0.053622 | 0.044354 | 0.092017 | -0.6546 | 0.23804 | -1.0757 | 6.3812 | -100.3418 | 22.9431 | 6.427 | 23.172 | 23.2178 | -100.6851 | 99.1608 | -22.7737 | 99.5819 | 106.6177 | -123.3536 | -0.44861 | 0.20599 | 0.42114 | 106.6635 | 123.4085 | -0.10529 | 100.4745 | 99.5819 | 123.4543 | 123.1796 | -0.44861 | 100.4745 | 99.5819 | 123.1796 | -0.10529 | 123.4543 | -24.0875 | -123.6969
2086.9844 | 123.4222 | -100.177 | 23.1445 | -0.12502 | 0.051175 | -0.0050764 | 0.076048 | -0.045077 | 0.052898 | 0.090949 | -0.60425 | 0.27466 | -1.0254 | 6.6513 | -100.1816 | 23.14 | 6.4224 | 23.3688 | 23.2727 | -100.5936 | 99.1516 | -22.8699 | 99.5728 | 106.8283 | -123.3261 | -0.41656 | 0.12817 | 0.42114 | 106.5994 | 123.5458 | -0.004578 | 100.4517 | 99.5728 | 123.4497 | 123.317 | -0.41656 | 100.4517 | 99.5728 | 123.317 | -0.004578 | 123.4497 | -24.1699 | -123.7381
2087.9219 | 123.5275 | -100.058 | 23.1766 | 0.027569 | 0.029812 | -0.037119 | 0.039732 | -0.057894 | 0.025128 | 0.097358 | -0.59967 | 0.22888 | -0.99335 | 6.5552 | -100.2274 | 23.1125 | 6.6422 | 23.3047 | 23.3871 | -100.502 | 99.0646 | -22.9477 | 99.4583 | 106.6132 | -123.4039 | -0.44403 | 0.21057 | 0.39368 | 106.7001 | 123.3627 | -0.16937 | 100.2869 | 99.4583 | 123.4451 | 123.1705 | -0.44403 | 100.2869 | 99.4583 | 123.1705 | -0.16937 | 123.4451 | -24.1699 | -123.6786
2088.9844 | 123.4818 | -100.0305 | 23.2452 | 0.348 | 0.04263 | -0.014689 | 0.070707 | -0.060031 | 0.052898 | 0.087745 | -0.67749 | 0.25635 | -1.0757 | 6.8024 | -100.0443 | 23.2864 | 6.5826 | 23.5153 | 23.3551 | -100.4425 | 98.9548 | -22.9889 | 99.353 | 106.8329 | -123.2895 | -0.41199 | 0.10986 | 0.39825 | 106.6132 | 123.5458 | -0.013732 | 100.2869 | 99.353 | 123.3856 | 123.317 | -0.41199 | 100.2869 | 99.353 | 123.317 | -0.013732 | 123.3856 | -24.321 | -123.6877
2089.9219 | 123.4909 | -100.0488 | 23.1766 | 1.584 | 0.045834 | -0.031779 | 0.06323 | -0.056826 | 0.049694 | 0.10804 | -0.66376 | 0.25177 | -1.0529 | 6.6284 | -100.1541 | 23.14 | 6.665 | 23.3459 | 23.3551 | -100.5203 | 98.996 | -22.9248 | 99.3851 | 106.6772 | -123.3307 | -0.4715 | 0.17853 | 0.3891 | 106.7139 | 123.3948 | -0.10529 | 100.3006 | 99.3851 | 123.4039 | 123.1888 | -0.4715 | 100.3006 | 99.3851 | 123.1888 | -0.10529 | 123.4039 | -24.2294 | -123.6969
2090.9844 | 123.3948 | -100.0534 | 23.2498 | -0.30813 | 0.034085 | -0.037119 | 0.068571 | -0.053622 | 0.035809 | 0.10056 | -0.53101 | 0.29755 | -0.94757 | 6.7978 | -100.0214 | 23.4009 | 6.6605 | 23.5153 | 23.4055 | -100.4334 | 99.1058 | -22.9523 | 99.5224 | 106.8512 | -123.2712 | -0.37994 | 0.15564 | 0.41657 | 106.7139 | 123.5687 | 0.032044 | 100.351 | 99.5224 | 123.4589 | 123.4543 | -0.37994 | 100.351 | 99.5224 | 123.4543 | 0.032044 | 123.4589 | -24.1974 | -123.6832
2091.9219 | 123.5138 | -99.9664 | 23.2635 | 0.51585 | 0.03088 | -0.0093484 | 0.06323 | -0.052554 | 0.037945 | 0.09629 | -0.5722 | 0.24261 | -0.99335 | 6.7657 | -100.0671 | 23.2361 | 6.7017 | 23.4741 | 23.4283 | -100.4562 | 98.9731 | -23.0209 | 99.3942 | 106.7322 | -123.3307 | -0.48981 | 0.1648 | 0.42114 | 106.6681 | 123.4406 | -0.10071 | 100.209 | 99.3942 | 123.3948 | 123.2025 | -0.48981 | 100.209 | 99.3942 | 123.2025 | -0.10071 | 123.3948 | -24.2569 | -123.7198
2092.9844 | 123.436 | -99.9847 | 23.2773 | 0.18016 | 0.026608 | -0.051005 | 0.04614 | -0.057894 | 0.033672 | 0.098426 | -0.58136 | 0.25177 | -0.92926 | 6.7566 | -100.09 | 23.2452 | 6.7245 | 23.4558 | 23.4467 | -100.4013 | 99.0555 | -23.0255 | 99.4034 | 106.7413 | -123.3673 | -0.41657 | 0.16937 | 0.3479 | 106.7093 | 123.4406 | -0.10529 | 100.2365 | 99.4034 | 123.4314 | 123.23 | -0.41657 | 100.2365 | 99.4034 | 123.23 | -0.10529 | 123.4314 | -24.2065 | -123.6786
2093.9219 | 123.4634 | -99.9573 | 23.3002 | 0.37852 | 0.024472 | -0.022166 | 0.065366 | -0.067507 | 0.042217 | 0.10804 | -0.43488 | 0.23346 | -0.84686 | 6.7841 | -100.0534 | 23.2452 | 6.7703 | 23.4329 | 23.4787 | -100.4105 | 99.1104 | -23.0667 | 99.5224 | 106.7413 | -123.3536 | -0.45319 | 0.17853 | 0.41199 | 106.7276 | 123.3902 | -0.096131 | 100.1907 | 99.5224 | 123.436 | 123.2025 | -0.45319 | 100.1907 | 99.5224 | 123.2025 | -0.096131 | 123.436 | -24.147 | -123.7106
2094.9844 | 123.3856 | -100.0443 | 23.3093 | -0.41494 | 0.038357 | -0.013621 | 0.058958 | -0.061099 | 0.042217 | 0.093085 | -0.39368 | 0.28381 | -0.79193 | 6.8344 | -100.0259 | 23.3322 | 6.5506 | 23.5519 | 23.4055 | -100.4334 | 99.2523 | -23.0255 | 99.6506 | 106.8787 | -123.3353 | -0.3891 | 0.096131 | 0.39825 | 106.5948 | 123.5962 | 0.01831 | 100.3281 | 99.6506 | 123.4497 | 123.3765 | -0.3891 | 100.3281 | 99.6506 | 123.3765 | 0.01831 | 123.4497 | -24.1013 | -123.7427
2095.9219 | 123.3765 | -100.0488 | 23.2773 | 0.43956 | 0.038357 | -0.010416 | 0.078184 | -0.045077 | 0.059307 | 0.093085 | -0.4303 | 0.28839 | -0.8194 | 6.8802 | -100.0122 | 23.3139 | 6.5826 | 23.5336 | 23.3643 | -100.4425 | 99.2294 | -22.9889 | 99.6185 | 106.929 | -123.2895 | -0.39368 | 0.086975 | 0.3891 | 106.6315 | 123.5825 | 0.036621 | 100.3372 | 99.6185 | 123.4131 | 123.3627 | -0.39368 | 100.3372 | 99.6185 | 123.3627 | 0.036621 | 123.4131 | -24.0967 | -123.7198
2096.9844 | 123.3994 | -100.0671 | 23.2224 | -0.079243 | 0.04797 | -0.031779 | 0.071775 | -0.042941 | 0.056103 | 0.090949 | -0.3067 | 0.29297 | -0.75989 | 6.8161 | -100.0809 | 23.2315 | 6.5826 | 23.4604 | 23.3871 | -100.4929 | 99.3073 | -22.9294 | 99.7604 | 106.8832 | -123.3032 | -0.42572 | 0.1648 | 0.45319 | 106.6498 | 123.5275 | -0.013733 | 100.3601 | 99.7604 | 123.4543 | 123.2986 | -0.42572 | 100.3601 | 99.7604 | 123.2986 | -0.013733 | 123.4543 | -23.9822 | -123.7152
2097.9219 | 123.4818 | -99.9847 | 23.2544 | 0.348 | 0.036221 | -0.017893 | 0.053617 | -0.047213 | 0.034741 | 0.085609 | -0.37079 | 0.2655 | -0.7782 | 6.8207 | -100.0717 | 23.2224 | 6.7474 | 23.465 | 23.4558 | -100.4242 | 99.2065 | -22.9889 | 99.614 | 106.8054 | -123.3261 | -0.43945 | 0.20142 | 0.40741 | 106.7322 | 123.4497 | -0.086975 | 100.2502 | 99.614 | 123.4406 | 123.2071 | -0.43945 | 100.2502 | 99.614 | 123.2071 | -0.086975 | 123.4406 | -24.0326 | -123.6786
2098.9844 | 123.3673 | -99.9939 | 23.3368 | -0.38442 | 0.034085 | -0.032847 | 0.073911 | -0.046145 | 0.036877 | 0.09629 | -0.33417 | 0.28839 | -0.6958 | 6.9397 | -99.9847 | 23.3917 | 6.6422 | 23.6069 | 23.4375 | -100.3922 | 99.2981 | -23.0484 | 99.6597 | 106.9336 | -123.3215 | -0.39825 | 0.10071 | 0.36163 | 106.636 | 123.6008 | 0.009155 | 100.2823 | 99.6597 | 123.4314 | 123.3856 | -0.39825 | 100.2823 | 99.6597 | 123.3856 | 0.009155 | 123.4314 | -24.0326 | -123.7289
2099.9219 | 123.4909 | -99.9481 | 23.2956 | -0.29287 | 0.033017 | -0.00080337 | 0.06323 | -0.061099 | 0.034741 | 0.095222 | -0.3891 | 0.22888 | -0.79193 | 6.7612 | -100.0717 | 23.2361 | 6.7978 | 23.4558 | 23.4741 | -100.3967 | 99.1562 | -23.0667 | 99.559 | 106.7093 | -123.3673 | -0.44861 | 0.17853 | 0.40283 | 106.7459 | 123.4039 | -0.1236 | 100.177 | 99.559 | 123.4222 | 123.1842 | -0.44861 | 100.177 | 99.559 | 123.1842 | -0.1236 | 123.4222 | -24.0875 | -123.6923
2100.9219 | 123.4177 | -99.9619 | 23.3047 | 0.348 | 0.033017 | -0.017893 | 0.054685 | -0.053622 | 0.071056 | 0.081336 | -0.37994 | 0.27924 | -0.74158 | 6.7291 | -99.9619 | 23.4055 | 6.6742 | 23.5107 | 23.4787 | -100.383 | 99.2203 | -23.0255 | 99.5819 | 106.691 | -123.2666 | -0.42114 | 0.17395 | 0.36163 | 106.636 | 123.4726 | 0 | 100.2411 | 99.5819 | 123.4406 | 123.3673 | -0.42114 | 100.2411 | 99.5819 | 123.3673 | 0 | 123.4406 | -24.0463 | -123.6877
2101.9219 | 123.4818 | -99.8154 | 23.4375 | 0.4243 | 0.024472 | -0.032847 | 0.062162 | -0.055758 | 0.047558 | 0.093085 | -0.32044 | 0.26093 | -0.71869 | 6.9672 | -99.9298 | 23.4146 | 6.9397 | 23.6115 | 23.6023 | -100.2411 | 99.0967 | -23.1766 | 99.4949 | 106.7825 | -123.3673 | -0.42572 | 0.1648 | 0.39825 | 106.7551 | 123.4268 | -0.11444 | 100.0763 | 99.4949 | 123.4177 | 123.23 | -0.42572 | 100.0763 | 99.4949 | 123.23 | -0.11444 | 123.4177 | -24.1562 | -123.6786
2102.9844 | 123.4131 | -100.0534 | 23.2269 | -0.18605 | 0.046902 | -0.029642 | 0.071775 | -0.049349 | 0.05183 | 0.10484 | -0.25177 | 0.29297 | -0.6958 | 6.7749 | -100.0626 | 23.259 | 6.5552 | 23.4924 | 23.3917 | -100.4745 | 99.3576 | -22.934 | 99.8016 | 106.8283 | -123.2895 | -0.42114 | 0.1648 | 0.44403 | 106.6086 | 123.5458 | -0.009155 | 100.3464 | 99.8016 | 123.4451 | 123.3124 | -0.42114 | 100.3464 | 99.8016 | 123.3124 | -0.009155 | 123.4451 | -23.9227 | -123.7015
2103.9219 | 123.4268 | -100.0488 | 23.2132 | 1.2483 | 0.038357 | -0.013621 | 0.065366 | -0.05469 | 0.04649 | 0.099494 | -0.2655 | 0.29297 | -0.74616 | 6.7612 | -100.0763 | 23.2407 | 6.5918 | 23.465 | 23.4055 | -100.4745 | 99.3027 | -22.9202 | 99.7833 | 106.81 | -123.2895 | -0.42572 | 0.19226 | 0.48065 | 106.6406 | 123.5138 | -0.027466 | 100.3418 | 99.7833 | 123.4543 | 123.2895 | -0.42572 | 100.3418 | 99.7833 | 123.2895 | -0.027466 | 123.4543 | -23.9594 | -123.6877
2104.9844 | 123.4177 | -100.0717 | 23.2361 | -0.24709 | 0.039425 | -0.046732 | 0.068571 | -0.055758 | 0.044354 | 0.086677 | -0.28381 | 0.27924 | -0.70038 | 6.7612 | -100.0626 | 23.2635 | 6.5598 | 23.465 | 23.3643 | -100.47 | 99.3713 | -22.9568 | 99.7879 | 106.8329 | -123.2986 | -0.39826 | 0.12817 | 0.41656 | 106.6315 | 123.5367 | 0.009155 | 100.351 | 99.7879 | 123.436 | 123.3353 | -0.39826 | 100.351 | 99.7879 | 123.3353 | 0.009155 | 123.436 | -23.9365 | -123.7061
2105.9219 | 123.3994 | -100.1495 | 23.1812 | 0.39378 | 0.041562 | -0.0082804 | 0.05789 | -0.046145 | 0.048626 | 0.098426 | -0.35248 | 0.27466 | -0.75073 | 6.6742 | -100.1175 | 23.2224 | 6.4499 | 23.4421 | 23.3185 | -100.5249 | 99.3988 | -22.9065 | 99.7971 | 106.8237 | -123.2986 | -0.37537 | 0.13733 | 0.39825 | 106.5994 | 123.5916 | 0.032043 | 100.4242 | 99.7971 | 123.468 | 123.3719 | -0.37537 | 100.4242 | 99.7971 | 123.3719 | 0.032043 | 123.468 | -23.9319 | -123.7061
2106.9844 | 123.4268 | -100.1404 | 23.1766 | -0.23183 | 0.04263 | -0.017893 | 0.076048 | -0.055758 | 0.055035 | 0.089881 | -0.2655 | 0.29755 | -0.69122 | 6.6513 | -100.1404 | 23.204 | 6.4499 | 23.4055 | 23.3231 | -100.5386 | 99.4492 | -22.879 | 99.8749 | 106.7917 | -123.317 | -0.39825 | 0.14648 | 0.42572 | 106.5903 | 123.5458 | 0 | 100.4379 | 99.8749 | 123.4634 | 123.3444 | -0.39825 | 100.4379 | 99.8749 | 123.3444 | 0 | 123.4634 | -23.8678 | -123.7152
2107.9219 | 123.4909 | -99.9847 | 23.2498 | 0.24119 | 0.019131 | -0.015757 | 0.04614 | -0.052554 | 0.044354 | 0.081336 | -0.3067 | 0.24261 | -0.74616 | 6.7474 | -100.0717 | 23.2315 | 6.7612 | 23.4329 | 23.4604 | -100.4242 | 99.2386 | -23.0072 | 99.678 | 106.7322 | -123.3215 | -0.43945 | 0.21057 | 0.43945 | 106.7459 | 123.4177 | -0.086975 | 100.2274 | 99.678 | 123.4451 | 123.2162 | -0.43945 | 100.2274 | 99.678 | 123.2162 | -0.086975 | 123.4451 | -23.996 | -123.674
2108.9844 | 123.4222 | -100.0717 | 23.2452 | -0.24709 | 0.049038 | -0.010416 | 0.078184 | -0.050418 | 0.040081 | 0.098426 | -0.1831 | 0.28381 | -0.6134 | 6.752 | -100.0946 | 23.2681 | 6.546 | 23.4787 | 23.3963 | -100.4791 | 99.4583 | -22.9614 | 99.8886 | 106.8237 | -123.3398 | -0.40741 | 0.15106 | 0.4303 | 106.6177 | 123.5504 | -0.022888 | 100.3555 | 99.8886 | 123.468 | 123.3398 | -0.40741 | 100.3555 | 99.8886 | 123.3398 | -0.022888 | 123.468 | -23.8586 | -123.7244
2109.9219 | 123.381 | -100.145 | 23.1857 | 0.48533 | 0.044766 | 0.0045366 | 0.072843 | -0.048281 | 0.049694 | 0.092017 | -0.19226 | 0.32959 | -0.59967 | 6.8069 | -100.1129 | 23.2315 | 6.5277 | 23.4467 | 23.3139 | -100.5524 | 99.5453 | -22.8561 | 99.9527 | 106.9519 | -123.2986 | -0.40741 | 0.12817 | 0.40741 | 106.6727 | 123.5916 | 0.032043 | 100.4745 | 99.9527 | 123.4589 | 123.3765 | -0.40741 | 100.4745 | 99.9527 | 123.3765 | 0.032043 | 123.4589 | -23.7854 | -123.7381
2110.9844 | 123.381 | -99.971 | 23.3368 | -0.39968 | 0.02554 | -0.013621 | 0.045072 | -0.047213 | 0.037945 | 0.093085 | -0.16937 | 0.2655 | -0.55389 | 6.8298 | -100.0076 | 23.3505 | 6.6284 | 23.5428 | 23.4741 | -100.3967 | 99.4171 | -23.0713 | 99.8016 | 106.8008 | -123.3444 | -0.42572 | 0.13733 | 0.38452 | 106.5994 | 123.5138 | -0.036621 | 100.2365 | 99.8016 | 123.4451 | 123.3215 | -0.42572 | 100.2365 | 99.8016 | 123.3215 | -0.036621 | 123.4451 | -23.8907 | -123.7335
2111.9219 | 123.3856 | -100.0488 | 23.259 | 0.33274 | 0.037289 | -0.026438 | 0.08032 | -0.038668 | 0.042217 | 0.098426 | -0.22888 | 0.29297 | -0.60425 | 6.9351 | -100.0076 | 23.3276 | 6.633 | 23.5382 | 23.3917 | -100.4608 | 99.4446 | -22.966 | 99.8199 | 106.9839 | -123.2666 | -0.41199 | 0.13275 | 0.37537 | 106.6818 | 123.587 | 0.041199 | 100.3418 | 99.8199 | 123.4406 | 123.3765 | -0.41199 | 100.3418 | 99.8199 | 123.3765 | 0.041199 | 123.4406 | -23.8632 | -123.7198
2112.9844 | 123.3673 | -100.0992 | 23.2681 | -0.12502 | 0.036221 | -0.037119 | 0.051481 | -0.050418 | 0.033672 | 0.090949 | -0.19684 | 0.28381 | -0.49439 | 6.8893 | -100.0854 | 23.3185 | 6.6467 | 23.5107 | 23.3917 | -100.4517 | 99.6048 | -22.9843 | 99.9023 | 106.9885 | -123.3536 | -0.35248 | 0.1236 | 0.29755 | 106.7459 | 123.6099 | 0.013733 | 100.383 | 99.9023 | 123.4909 | 123.4177 | -0.35248 | 100.383 | 99.9023 | 123.4177 | 0.013733 | 123.4909 | -23.7625 | -123.7198
2113.9219 | 123.3856 | -100.0397 | 23.2681 | 0.19541 | 0.043698 | -0.015757 | 0.078184 | -0.047213 | 0.050762 | 0.095222 | -0.15106 | 0.2655 | -0.60425 | 6.9214 | -99.9573 | 23.3551 | 6.5598 | 23.6115 | 23.41 | -100.4471 | 99.4354 | -23.0026 | 99.8886 | 106.9611 | -123.2254 | -0.40741 | 0.14191 | 0.45319 | 106.5994 | 123.6511 | 0.082398 | 100.3052 | 99.8886 | 123.4497 | 123.3948 | -0.40741 | 100.3052 | 99.8886 | 123.3948 | 0.082398 | 123.4497 | -23.8724 | -123.7152
2114.9844 | 123.4497 | -100.0443 | 23.2727 | -0.44545 | 0.041562 | -0.0093484 | 0.06323 | -0.049349 | 0.039013 | 0.092017 | -0.12817 | 0.29297 | -0.50354 | 6.9305 | -100.058 | 23.3002 | 6.6422 | 23.5199 | 23.378 | -100.4608 | 99.5407 | -22.9797 | 99.9161 | 106.9748 | -123.3307 | -0.41656 | 0.10529 | 0.37537 | 106.6864 | 123.5641 | -0.013733 | 100.3372 | 99.9161 | 123.4222 | 123.3444 | -0.41656 | 100.3372 | 99.9161 | 123.3444 | -0.013733 | 123.4222 | -23.7762 | -123.7335
2115.9219 | 123.349 | -100.1175 | 23.1857 | 0.43956 | 0.041562 | -0.012553 | 0.070707 | -0.052554 | 0.053967 | 0.098426 | -0.19684 | 0.29755 | -0.57678 | 6.9305 | -100.0763 | 23.2773 | 6.5826 | 23.4741 | 23.2956 | -100.5295 | 99.5407 | -22.8882 | 99.9207 | 107.048 | -123.262 | -0.41199 | 0.10986 | 0.37994 | 106.7001 | 123.5916 | 0.041199 | 100.415 | 99.9207 | 123.4131 | 123.3948 | -0.41199 | 100.415 | 99.9207 | 123.3948 | 0.041199 | 123.4131 | -23.7625 | -123.7152
2116.9844 | 123.3994 | -100.209 | 23.1033 | -0.30813 | 0.034085 | -0.010416 | 0.069639 | -0.045077 | 0.037945 | 0.09629 | -0.091553 | 0.31128 | -0.44861 | 6.7612 | -100.1999 | 23.1262 | 6.4774 | 23.3688 | 23.2178 | -100.6302 | 99.7604 | -22.7921 | 100.1175 | 106.9702 | -123.3032 | -0.42114 | 0.11444 | 0.35706 | 106.6864 | 123.5779 | 0.009155 | 100.5203 | 100.1175 | 123.4268 | 123.3353 | -0.42114 | 100.5203 | 100.1175 | 123.3353 | 0.009155 | 123.4268 | -23.5519 | -123.7335
2117.9219 | 123.3582 | -100.1999 | 23.14 | 0.19541 | 0.055447 | -0.022166 | 0.072843 | -0.038668 | 0.053967 | 0.089881 | -0.11902 | 0.27924 | -0.54016 | 6.6971 | -100.1221 | 23.204 | 6.4087 | 23.4329 | 23.2773 | -100.5707 | 99.6597 | -22.8607 | 100.0809 | 106.897 | -123.262 | -0.37079 | 0.13733 | 0.42114 | 106.6086 | 123.6328 | 0.07782 | 100.4791 | 100.0809 | 123.4772 | 123.4039 | -0.37079 | 100.4791 | 100.0809 | 123.4039 | 0.07782 | 123.4772 | -23.6801 | -123.7106
2118.9844 | 123.4131 | -100.0305 | 23.2635 | 0.042827 | 0.039425 | -0.033915 | 0.067503 | -0.048281 | 0.043285 | 0.090949 | -0.045776 | 0.29297 | -0.41657 | 6.7841 | -100.09 | 23.2956 | 6.5689 | 23.497 | 23.3963 | -100.4837 | 99.614 | -22.9706 | 99.9847 | 106.8146 | -123.3536 | -0.45319 | 0.13275 | 0.37079 | 106.5994 | 123.5275 | -0.059509 | 100.3235 | 99.9847 | 123.4268 | 123.3261 | -0.45319 | 100.3235 | 99.9847 | 123.3261 | -0.059509 | 123.4268 | -23.6801 | -123.7473
2119.9219 | 123.3994 | -100.209 | 23.0576 | 0.10386 | 0.04263 | -0.015757 | 0.069639 | -0.034396 | 0.052898 | 0.097358 | -0.041199 | 0.31128 | -0.45319 | 6.7474 | -100.2548 | 23.1262 | 6.4819 | 23.3505 | 23.2452 | -100.6256 | 99.7559 | -22.7463 | 100.1678 | 106.9565 | -123.3124 | -0.41656 | 0.18768 | 0.41199 | 106.691 | 123.5596 | -0.045777 | 100.5203 | 100.1678 | 123.4543 | 123.3353 | -0.41656 | 100.5203 | 100.1678 | 123.3353 | -0.045777 | 123.4543 | -23.5107 | -123.6832
2120.9844 | 123.3536 | -100.2365 | 23.0988 | -0.30813 | 0.039425 | -0.040324 | 0.06323 | -0.048281 | 0.037945 | 0.097358 | -0.027466 | 0.28839 | -0.41199 | 6.633 | -100.2457 | 23.1125 | 6.3812 | 23.3093 | 23.204 | -100.5981 | 99.8245 | -22.8104 | 100.209 | 106.8695 | -123.3444 | -0.36163 | 0.10529 | 0.38452 | 106.6177 | 123.5458 | -0.009156 | 100.5249 | 100.209 | 123.4406 | 123.349 | -0.36163 | 100.5249 | 100.209 | 123.349 | -0.009156 | 123.4406 | -23.5107 | -123.6969
2121.9219 | 123.4039 | -100.2502 | 23.0667 | -0.079243 | 0.056515 | -0.018961 | 0.064298 | -0.045077 | 0.04649 | 0.093085 | 0.009155 | 0.28839 | -0.42572 | 6.7017 | -100.2457 | 23.1033 | 6.4865 | 23.3047 | 23.2132 | -100.6714 | 99.8245 | -22.7783 | 100.2594 | 106.9519 | -123.3124 | -0.42114 | 0.14648 | 0.43488 | 106.7368 | 123.555 | 0.004577 | 100.5386 | 100.2594 | 123.4634 | 123.3536 | -0.42114 | 100.5386 | 100.2594 | 123.3536 | 0.004577 | 123.4634 | -23.4924 | -123.7381
2122.9844 | 123.4451 | -99.9939 | 23.2773 | -0.3539 | 0.022336 | -0.043528 | 0.047208 | -0.046145 | 0.025128 | 0.099494 | 0.045776 | 0.2243 | -0.36163 | 6.8665 | -100.264 | 23.2452 | 6.8756 | 23.465 | 23.4604 | -100.4196 | 99.6323 | -23.053 | 100.0397 | 106.8604 | -123.5413 | -0.42572 | 0.1831 | 0.40741 | 106.8695 | 123.4589 | -0.27008 | 100.2182 | 100.0397 | 123.4543 | 123.2391 | -0.42572 | 100.2182 | 100.0397 | 123.2391 | -0.27008 | 123.4543 | -23.6389 | -123.6969
2123.9219 | 123.4222 | -100.2274 | 23.0804 | -0.063984 | 0.038357 | -0.0029404 | 0.060026 | -0.047213 | 0.044354 | 0.095222 | 0.041199 | 0.27924 | -0.38452 | 6.6238 | -100.2594 | 23.085 | 6.427 | 23.3047 | 23.2086 | -100.6622 | 99.8428 | -22.8012 | 100.2686 | 106.8512 | -123.3398 | -0.43488 | 0.12817 | 0.42572 | 106.6544 | 123.5321 | -0.032043 | 100.5066 | 100.2686 | 123.436 | 123.3124 | -0.43488 | 100.5066 | 100.2686 | 123.3124 | -0.032043 | 123.436 | -23.465 | -123.7427
2124.9844 | 123.3765 | -100.145 | 23.2132 | -0.38442 | 0.027676 | -0.048869 | 0.05789 | -0.053622 | 0.045422 | 0.1059 | 0.004578 | 0.29755 | -0.36163 | 6.7703 | -100.1221 | 23.2361 | 6.4957 | 23.4695 | 23.3414 | -100.5157 | 99.7833 | -22.9156 | 100.1495 | 106.9153 | -123.3353 | -0.37079 | 0.12817 | 0.36621 | 106.6406 | 123.6145 | 0.022888 | 100.4425 | 100.1495 | 123.4863 | 123.381 | -0.37079 | 100.4425 | 100.1495 | 123.381 | 0.022888 | 123.4863 | -23.5748 | -123.7289
2125.9219 | 123.4131 | -100.2411 | 23.0759 | 0.01231 | 0.031949 | -0.027506 | 0.070707 | -0.050418 | 0.049694 | 0.092017 | 0.059509 | 0.26093 | -0.38452 | 6.6422 | -100.2274 | 23.0988 | 6.4041 | 23.3047 | 23.2361 | -100.6577 | 99.8566 | -22.8149 | 100.3006 | 106.8832 | -123.3032 | -0.41656 | 0.16022 | 0.44403 | 106.6452 | 123.5458 | 0.013733 | 100.502 | 100.3006 | 123.4772 | 123.3398 | -0.41656 | 100.502 | 100.3006 | 123.3398 | 0.013733 | 123.4772 | -23.4604 | -123.7335
2126.9844 | 123.4451 | -100.2823 | 23.0026 | -0.39968 | 0.031949 | -0.048869 | 0.045072 | -0.040805 | 0.026196 | 0.09629 | 0.086975 | 0.24261 | -0.33417 | 6.308 | -100.2411 | 23.0026 | 6.4178 | 23.0621 | 23.1812 | -100.7446 | 99.9481 | -22.76 | 100.3693 | 106.5903 | -123.2437 | -0.46234 | 0.17853 | 0.42114 | 106.7001 | 123.3444 | 0.041199 | 100.5249 | 100.3693 | 123.4634 | 123.2849 | -0.46234 | 100.5249 | 100.3693 | 123.2849 | 0.041199 | 123.4634 | -23.3368 | -123.7473
2127.9219 | 123.4222 | -100.3143 | 22.998 | -0.1708 | 0.031949 | -0.022166 | 0.069639 | -0.044009 | 0.045422 | 0.099494 | 0.027466 | 0.29755 | -0.42114 | 6.5781 | -100.3326 | 23.0118 | 6.3583 | 23.2315 | 23.1445 | -100.7355 | 99.8932 | -22.7005 | 100.3418 | 106.8924 | -123.3307 | -0.42114 | 0.14648 | 0.44861 | 106.6727 | 123.5458 | -0.018311 | 100.6119 | 100.3418 | 123.4589 | 123.3261 | -0.42114 | 100.6119 | 100.3418 | 123.3261 | -0.018311 | 123.4589 | -23.4192 | -123.7335
2128.9844 | 123.4314 | -100.1999 | 23.0896 | -0.23183 | 0.014859 | -0.029642 | 0.04614 | -0.044009 | 0.028332 | 0.098426 | 0.027466 | 0.26093 | -0.36621 | 6.5186 | -100.2823 | 23.0804 | 6.4224 | 23.3139 | 23.2498 | -100.6348 | 99.8337 | -22.8287 | 100.2274 | 106.7184 | -123.3719 | -0.43488 | 0.16022 | 0.39368 | 106.6223 | 123.5138 | -0.082398 | 100.4608 | 100.2274 | 123.4497 | 123.2803 | -0.43488 | 100.4608 | 100.2274 | 123.2803 | -0.082398 | 123.4497 | -23.4558 | -123.7244
2129.9219 | 123.4085 | -100.2823 | 23.0621 | 1.8281 | 0.035153 | -0.055277 | 0.069639 | -0.041873 | 0.044354 | 0.089881 | 0.11444 | 0.31128 | -0.31128 | 6.5872 | -100.2914 | 23.0804 | 6.2851 | 23.2864 | 23.1537 | -100.6943 | 99.971 | -22.7509 | 100.3967 | 106.8695 | -123.3536 | -0.41199 | 0.091553 | 0.42572 | 106.5674 | 123.5687 | -0.009155 | 100.5936 | 100.3967 | 123.436 | 123.3627 | -0.41199 | 100.5936 | 100.3967 | 123.3627 | -0.009155 | 123.436 | -23.3734 | -123.7564
2130.9844 | 123.3627 | -100.5249 | 22.8241 | -0.41494 | 0.044766 | -0.029642 | 0.061094 | -0.044009 | 0.034741 | 0.092017 | 0.027466 | 0.29297 | -0.35706 | 6.34 | -100.5066 | 22.8653 | 6.0562 | 23.0667 | 22.9477 | -100.8728 | 100.1678 | -22.5311 | 100.5524 | 106.8649 | -123.3307 | -0.3479 | 0.1236 | 0.38452 | 106.5811 | 123.5916 | 0.01831 | 100.8179 | 100.5524 | 123.4726 | 123.3902 | -0.3479 | 100.8179 | 100.5524 | 123.3902 | 0.01831 | 123.4726 | -23.1812 | -123.6969
2131.9219 | 123.4222 | -100.4837 | 22.8195 | -0.10976 | 0.043698 | -0.029642 | 0.066434 | -0.047213 | 0.056103 | 0.094154 | 0.045776 | 0.28381 | -0.39825 | 6.3995 | -100.5112 | 22.8333 | 6.1798 | 23.0484 | 22.9752 | -100.9094 | 100.0855 | -22.5357 | 100.5295 | 106.8832 | -123.3307 | -0.42572 | 0.15564 | 0.44403 | 106.6635 | 123.5321 | -0.027465 | 100.7675 | 100.5295 | 123.4589 | 123.317 | -0.42572 | 100.7675 | 100.5295 | 123.317 | -0.027465 | 123.4589 | -23.2178 | -123.7289
2132.9844 | 123.3765 | -100.5707 | 22.7646 | -0.38442 | 0.026608 | -0.053141 | 0.054685 | -0.045077 | 0.042217 | 0.088813 | -0.018311 | 0.29297 | -0.3891 | 6.2256 | -100.5753 | 22.8012 | 5.9463 | 23.0164 | 22.8928 | -100.9598 | 100.1816 | -22.4716 | 100.5524 | 106.7963 | -123.3398 | -0.3891 | 0.12817 | 0.37079 | 106.517 | 123.587 | -0.004577 | 100.8636 | 100.5524 | 123.4634 | 123.3719 | -0.3891 | 100.8636 | 100.5524 | 123.3719 | -0.004577 | 123.4634 | -23.1537 | -123.7244
2133.9219 | 123.4268 | -100.4791 | 22.8241 | -0.15554 | 0.034085 | -0.037119 | 0.062162 | -0.051486 | 0.050762 | 0.093085 | 0.018311 | 0.27924 | -0.41657 | 6.3492 | -100.4791 | 22.8424 | 6.1432 | 23.0576 | 22.9706 | -100.8728 | 100.0626 | -22.5449 | 100.4974 | 106.8283 | -123.3032 | -0.39368 | 0.14648 | 0.43488 | 106.6223 | 123.5367 | 0 | 100.7584 | 100.4974 | 123.4497 | 123.3215 | -0.39368 | 100.7584 | 100.4974 | 123.3215 | 0 | 123.4497 | -23.2407 | -123.6969
2134.9844 | 123.4955 | -100.4654 | 22.7692 | -0.36916 | 0.028744 | -0.0478 | 0.049345 | -0.051486 | 0.039013 | 0.095222 | -0.018311 | 0.23804 | -0.44403 | 6.1523 | -100.621 | 22.7325 | 6.1981 | 22.934 | 22.9752 | -100.9232 | 100.0214 | -22.5311 | 100.4471 | 106.6177 | -123.3902 | -0.45776 | 0.20599 | 0.42572 | 106.6635 | 123.3994 | -0.15564 | 100.7034 | 100.4471 | 123.4406 | 123.1979 | -0.45776 | 100.7034 | 100.4471 | 123.1979 | -0.15564 | 123.4406 | -23.2132 | -123.6923
2135.9219 | 123.4177 | -100.6531 | 22.6593 | -0.063984 | 0.028744 | -0.04246 | 0.066434 | -0.048281 | 0.05183 | 0.093085 | -0.032043 | 0.27924 | -0.48981 | 6.0928 | -100.6668 | 22.6639 | 5.8594 | 22.8836 | 22.7966 | -101.0925 | 100.1633 | -22.3801 | 100.621 | 106.7459 | -123.3261 | -0.43945 | 0.13733 | 0.45776 | 106.5125 | 123.5367 | -0.013733 | 100.9323 | 100.621 | 123.4497 | 123.317 | -0.43945 | 100.9323 | 100.621 | 123.317 | -0.013733 | 123.4497 | -23.1491 | -123.7518
2136.9844 | 123.3948 | -100.5661 | 22.7737 | -0.41494 | 0.023404 | -0.030711 | 0.048277 | -0.055758 | 0.032604 | 0.099494 | -0.036621 | 0.28839 | -0.4303 | 6.2164 | -100.5569 | 22.7966 | 5.9921 | 22.998 | 22.8882 | -100.9415 | 100.1358 | -22.4854 | 100.5295 | 106.7825 | -123.3307 | -0.37537 | 0.11444 | 0.39368 | 106.5582 | 123.5641 | 0.009155 | 100.8545 | 100.5295 | 123.4543 | 123.3627 | -0.37537 | 100.8545 | 100.5295 | 123.3627 | 0.009155 | 123.4543 | -23.204 | -123.7152
2137.9219 | 123.4268 | -100.5844 | 22.7417 | -0.094502 | 0.036221 | -0.037119 | 0.06323 | -0.051486 | 0.05183 | 0.095222 | -0.041199 | 0.27924 | -0.46692 | 6.2347 | -100.6027 | 22.7325 | 6.0333 | 22.9614 | 22.8928 | -101.0056 | 100.1175 | -22.4625 | 100.5432 | 106.8192 | -123.3444 | -0.42114 | 0.15106 | 0.42572 | 106.6177 | 123.5458 | -0.01831 | 100.8636 | 100.5432 | 123.4772 | 123.317 | -0.42114 | 100.8636 | 100.5432 | 123.317 | -0.01831 | 123.4772 | -23.2086 | -123.7473
2138.9844 | 123.4772 | -100.5341 | 22.728 | -0.47597 | 0.0095178 | -0.030711 | 0.041868 | -0.053622 | 0.027264 | 0.10484 | -0.064087 | 0.21973 | -0.47607 | 6.0013 | -100.6897 | 22.6639 | 6.0242 | 22.8699 | 22.934 | -100.9781 | 100.058 | -22.5082 | 100.47 | 106.5353 | -123.4177 | -0.44403 | 0.20599 | 0.41199 | 106.5582 | 123.4039 | -0.15564 | 100.7538 | 100.47 | 123.468 | 123.1979 | -0.44403 | 100.7538 | 100.47 | 123.1979 | -0.15564 | 123.468 | -23.204 | -123.7061
2139.9219 | 123.4177 | -100.5798 | 22.7097 | -0.063984 | 0.044766 | -0.02537 | 0.076048 | -0.042941 | 0.050762 | 0.082404 | -0.086975 | 0.28381 | -0.50812 | 6.1661 | -100.5981 | 22.7371 | 5.9235 | 22.9523 | 22.8699 | -101.0239 | 100.0717 | -22.4258 | 100.4929 | 106.7459 | -123.3078 | -0.44403 | 0.16022 | 0.42114 | 106.5033 | 123.5321 | -0.018311 | 100.8636 | 100.4929 | 123.4497 | 123.317 | -0.44403 | 100.8636 | 100.4929 | 123.317 | -0.018311 | 123.4497 | -23.2178 | -123.7335
2140.9844 | 123.5001 | -100.5112 | 22.7188 | -0.29287 | 0.018063 | -0.041392 | 0.048277 | -0.053622 | 0.032604 | 0.10377 | -0.059509 | 0.24261 | -0.46234 | 5.8777 | -100.6897 | 22.6501 | 5.9235 | 22.8607 | 22.8928 | -100.9872 | 100.0488 | -22.4762 | 100.4517 | 106.3889 | -123.4085 | -0.47608 | 0.17395 | 0.40283 | 106.4346 | 123.3719 | -0.17853 | 100.7538 | 100.4517 | 123.4039 | 123.1613 | -0.47608 | 100.7538 | 100.4517 | 123.1613 | -0.17853 | 123.4039 | -23.1812 | -123.7061
2141.9219 | 123.4268 | -100.5432 | 22.8104 | -0.20131 | 0.037289 | -0.026438 | 0.069639 | -0.056826 | 0.058239 | 0.087745 | -0.045776 | 0.28381 | -0.50354 | 6.0928 | -100.5478 | 22.7966 | 5.8594 | 23.0347 | 22.9202 | -100.9277 | 100.0397 | -22.5266 | 100.4974 | 106.636 | -123.3582 | -0.38452 | 0.10986 | 0.45776 | 106.4026 | 123.5779 | -0.004578 | 100.827 | 100.4974 | 123.4634 | 123.3398 | -0.38452 | 100.827 | 100.4974 | 123.3398 | -0.004578 | 123.4634 | -23.3139 | -123.7381
2142.9844 | 123.5092 | -100.589 | 22.673 | -0.063984 | 0.013791 | -0.036051 | 0.047208 | -0.053622 | 0.0294 | 0.10163 | -0.15106 | 0.27466 | -0.54474 | 5.7587 | -100.7492 | 22.6089 | 5.809 | 22.8012 | 22.8699 | -101.0605 | 100.0442 | -22.3984 | 100.4379 | 106.3477 | -123.4222 | -0.4715 | 0.19684 | 0.39368 | 106.398 | 123.3902 | -0.16022 | 100.8636 | 100.4379 | 123.4589 | 123.1979 | -0.4715 | 100.8636 | 100.4379 | 123.1979 | -0.16022 | 123.4589 | -23.2178 | -123.7335
2143.9219 | 123.3948 | -102.1225 | 21.2128 | -0.32338 | 0.024472 | -0.045664 | 0.073911 | -0.055758 | 0.048626 | 0.083472 | -0.22888 | 0.30212 | -0.62256 | 3.7216 | -102.1408 | 21.2311 | 3.4378 | 21.4462 | 21.3135 | -102.5253 | 101.4999 | -20.9106 | 101.8936 | 105.8441 | -123.3536 | -0.40283 | 0.10071 | 0.39368 | 105.5603 | 123.5687 | -0.01831 | 102.4246 | 101.8936 | 123.436 | 123.3536 | -0.40283 | 102.4246 | 101.8936 | 123.3536 | -0.01831 | 123.436 | -21.8353 | -123.7381
2144.9844 | 123.4863 | -102.4429 | 20.8328 | -0.0029495 | 0.014859 | -0.037119 | 0.049345 | -0.064303 | 0.0294 | 0.099494 | -0.33417 | 0.19226 | -0.70496 | 2.623 | -102.594 | 20.7687 | 2.6505 | 20.9793 | 21.0114 | -102.8961 | 101.738 | -20.6406 | 102.1088 | 105.0659 | -123.4268 | -0.45319 | 0.17853 | 0.37079 | 105.0934 | 123.4222 | -0.15106 | 102.6352 | 102.1088 | 123.4543 | 123.2117 | -0.45319 | 102.6352 | 102.1088 | 123.2117 | -0.15106 | 123.4543 | -21.5378 | -123.7289
2145.9219 | 123.4177 | -102.4246 | 20.9061 | -0.50649 | 0.039425 | -0.026438 | 0.074979 | -0.060031 | 0.042217 | 0.095222 | -0.27008 | 0.2655 | -0.71869 | 2.7695 | -102.4429 | 20.9015 | 2.5772 | 21.1121 | 21.0571 | -102.8275 | 101.7059 | -20.6406 | 102.1545 | 105.1941 | -123.349 | -0.40283 | 0.15106 | 0.44861 | 105.0018 | 123.5367 | -0.01831 | 102.6901 | 102.1545 | 123.4818 | 123.3261 | -0.40283 | 102.6901 | 102.1545 | 123.3261 | -0.01831 | 123.4818 | -21.6248 | -123.7335
2146.9844 | 123.4726 | -102.2049 | 21.0846 | 0.042827 | 0.019131 | -0.015757 | 0.053617 | -0.051486 | 0.017651 | 0.092017 | -0.39368 | 0.24719 | -0.74158 | 2.9526 | -102.3239 | 21.0388 | 2.9343 | 21.2219 | 21.2448 | -102.6031 | 101.4633 | -20.8374 | 101.8112 | 105.1575 | -123.4085 | -0.39825 | 0.16022 | 0.3479 | 105.1392 | 123.4268 | -0.11902 | 102.4521 | 101.8112 | 123.4497 | 123.2437 | -0.39825 | 102.4521 | 101.8112 | 123.2437 | -0.11902 | 123.4497 | -21.8262 | -123.6877
2147.9219 | 123.4268 | -103.0518 | 20.2606 | -0.033467 | 0.039425 | -0.024302 | 0.077116 | -0.046145 | 0.06358 | 0.10377 | -0.38452 | 0.27924 | -0.81024 | 2.1469 | -103.0426 | 20.2652 | 1.9363 | 20.4941 | 20.4071 | -103.4729 | 102.2415 | -19.9814 | 102.6672 | 105.1987 | -123.3032 | -0.42114 | 0.14648 | 0.42572 | 104.9881 | 123.5458 | 0.009155 | 103.331 | 102.6672 | 123.4589 | 123.317 | -0.42114 | 103.331 | 102.6672 | 123.317 | 0.009155 | 123.4589 | -21.0709 | -123.7335
2148.9844 | 123.4909 | -103.0609 | 20.1874 | -0.20131 | 0.016995 | -0.04246 | 0.042936 | -0.057894 | 0.032604 | 0.094154 | -0.39825 | 0.24719 | -0.78278 | 1.9455 | -103.2166 | 20.1416 | 2.0279 | 20.3293 | 20.4254 | -103.4958 | 102.2781 | -19.9402 | 102.6627 | 105.0064 | -123.4039 | -0.43488 | 0.23804 | 0.38452 | 105.0888 | 123.3902 | -0.15564 | 103.3081 | 102.6627 | 123.4863 | 123.2025 | -0.43488 | 103.3081 | 102.6627 | 123.2025 | -0.15564 | 123.4863 | -20.9702 | -123.6832
2149.9219 | 123.3948 | -103.2166 | 20.1187 | -0.26235 | 0.038357 | -0.041392 | 0.058958 | -0.049349 | 0.053967 | 0.093085 | -0.37537 | 0.27466 | -0.82398 | 1.9135 | -103.244 | 20.0775 | 1.6708 | 20.3156 | 20.2469 | -103.6285 | 102.3926 | -19.8441 | 102.8412 | 105.13 | -123.3627 | -0.41199 | 0.12817 | 0.44861 | 104.8874 | 123.5321 | -0.027466 | 103.4912 | 102.8412 | 123.4634 | 123.2941 | -0.41199 | 103.4912 | 102.8412 | 123.2941 | -0.027466 | 123.4634 | -20.9427 | -123.7473
2150.9688 | 123.5321 | -103.6469 | 19.5923 | -0.20131 | 0.024472 | -0.038187 | 0.036527 | -0.064303 | 0.017651 | 0.10056 | -0.42114 | 0.23804 | -0.78735 | 1.1581 | -103.8025 | 19.5007 | 1.2634 | 19.7342 | 19.7983 | -104.1092 | 102.8595 | -19.3542 | 103.2257 | 104.805 | -123.3948 | -0.46234 | 0.20599 | 0.36621 | 104.9103 | 123.381 | -0.15564 | 103.8849 | 103.2257 | 123.4451 | 123.1476 | -0.46234 | 103.8849 | 103.2257 | 123.1476 | -0.15564 | 123.4451 | -20.3796 | -123.7015
2151.9219 | 123.3948 | -103.7201 | 19.5923 | -0.0029495 | 0.050107 | -0.015757 | 0.079252 | -0.048281 | 0.05183 | 0.095222 | -0.40741 | 0.27466 | -0.8606 | 1.2497 | -103.7476 | 19.5557 | 0.96588 | 19.7662 | 19.693 | -104.1504 | 102.8595 | -19.3176 | 103.3127 | 104.9698 | -123.3398 | -0.4303 | 0.10071 | 0.45319 | 104.686 | 123.4863 | -0.027466 | 103.9948 | 103.3127 | 123.4131 | 123.2758 | -0.4303 | 103.9948 | 103.3127 | 123.2758 | -0.027466 | 123.4131 | -20.4529 | -123.7427
2152.9844 | 123.436 | -104.0039 | 19.3268 | -0.56752 | 0.022336 | -0.027506 | 0.058958 | -0.07178 | 0.030468 | 0.09629 | -0.42114 | 0.25177 | -0.81482 | 0.76904 | -104.0634 | 19.3039 | 0.67749 | 19.5236 | 19.4778 | -104.4113 | 103.1891 | -19.075 | 103.5828 | 104.7729 | -123.3902 | -0.40741 | 0.15106 | 0.39368 | 104.6814 | 123.5275 | -0.05951 | 104.2557 | 103.5828 | 123.4818 | 123.3078 | -0.40741 | 104.2557 | 103.5828 | 123.3078 | -0.05951 | 123.4818 | -20.1416 | -123.7381
2153.9219 | 123.4131 | -104.2328 | 19.0933 | -0.0029495 | 0.044766 | -0.010416 | 0.071775 | -0.056826 | 0.04649 | 0.099494 | -0.40283 | 0.29755 | -0.85602 | 0.71869 | -104.2053 | 19.1116 | 0.50354 | 19.3314 | 19.2398 | -104.6082 | 103.3768 | -18.7958 | 103.83 | 104.9515 | -123.2986 | -0.37537 | 0.14648 | 0.45319 | 104.7363 | 123.5641 | 0.027466 | 104.5303 | 103.83 | 123.4726 | 123.3444 | -0.37537 | 104.5303 | 103.83 | 123.3444 | 0.027466 | 123.4726 | -19.9493 | -123.7015
2154.9844 | 123.5229 | -104.2877 | 18.9972 | -0.094502 | 0.022336 | -0.028574 | 0.049345 | -0.068576 | 0.0059006 | 0.092017 | -0.45319 | 0.25635 | -0.82398 | 0.49896 | -104.4479 | 18.9102 | 0.61798 | 19.1254 | 19.194 | -104.7134 | 103.4637 | -18.7408 | 103.8345 | 104.7867 | -123.4451 | -0.42572 | 0.19684 | 0.37079 | 104.9057 | 123.4131 | -0.16022 | 104.5441 | 103.8345 | 123.4818 | 123.1979 | -0.42572 | 104.5441 | 103.8345 | 123.1979 | -0.16022 | 123.4818 | -19.8212 | -123.7106
2155.9219 | 123.4039 | -104.3198 | 19.0018 | -0.094502 | 0.041562 | -0.032847 | 0.073911 | -0.049349 | 0.053967 | 0.095222 | -0.43945 | 0.31128 | -0.87433 | 0.64545 | -104.3198 | 19.0201 | 0.42114 | 19.2215 | 19.1574 | -104.7226 | 103.4454 | -18.6905 | 103.8803 | 104.9652 | -123.3215 | -0.40283 | 0.15564 | 0.43488 | 104.7409 | 123.5413 | 0 | 104.631 | 103.8803 | 123.4772 | 123.3398 | -0.40283 | 104.631 | 103.8803 | 123.3398 | 0 | 123.4772 | -19.8761 | -123.7244
2156.9844 | 123.4955 | -104.3198 | 18.9331 | -0.33864 | 0.026608 | -0.041392 | 0.052549 | -0.056826 | 0.028332 | 0.097358 | -0.44861 | 0.24719 | -0.89722 | 0.36163 | -104.4617 | 18.869 | 0.41657 | 19.0659 | 19.1116 | -104.7501 | 103.4225 | -18.6859 | 103.8712 | 104.6814 | -123.3948 | -0.4303 | 0.17853 | 0.44861 | 104.7363 | 123.3856 | -0.14191 | 104.567 | 103.8712 | 123.4314 | 123.1888 | -0.4303 | 104.567 | 103.8712 | 123.1888 | -0.14191 | 123.4314 | -19.8303 | -123.6832
2157.9219 | 123.4314 | -104.3976 | 18.9285 | -0.24709 | 0.036221 | -0.017893 | 0.073911 | -0.050418 | 0.049694 | 0.093085 | -0.44403 | 0.29297 | -0.88806 | 0.5722 | -104.4159 | 18.9194 | 0.37537 | 19.1345 | 19.0475 | -104.8187 | 103.5095 | -18.6356 | 103.9536 | 104.9698 | -123.3444 | -0.42114 | 0.11902 | 0.44403 | 104.7729 | 123.5321 | -0.018311 | 104.6906 | 103.9536 | 123.4451 | 123.317 | -0.42114 | 104.6906 | 103.9536 | 123.317 | -0.018311 | 123.4451 | -19.8166 | -123.7473
2158.9844 | 123.3765 | -104.2328 | 19.1071 | -0.30813 | 0.034085 | -0.036051 | 0.061094 | -0.048281 | 0.031536 | 0.097358 | -0.6958 | 0.29297 | -1.1032 | 0.52643 | -104.2374 | -4.422 | 0.27008 | 19.3359 | 19.2123 | -104.6173 | 103.1296 | -18.8141 | 103.537 | 104.7592 | -123.3444 | -0.38452 | 0.10528 | 0.40741 | 104.5029 | 123.5687 | -0.004578 | 104.5258 | 103.537 | 123.4451 | 99.8108 | -0.38452 | 104.5258 | 103.537 | 99.8108 | -0.004578 | 123.4451 | -20.2103 | -123.7244
2159.9219 | 123.436 | -104.393 | 18.9377 | -0.21657 | 0.052243 | -0.013621 | 0.071775 | -0.050418 | 0.047558 | 0.10377 | -0.68665 | 0.27008 | -1.1124 | 0.4715 | -104.4067 | -11.2885 | 0.3067 | 19.1483 | 19.0659 | -104.7821 | 103.2806 | -18.6676 | 103.7064 | 104.8645 | -123.3444 | -0.3891 | 0.12817 | 0.42572 | 104.6997 | 123.5413 | -0.013733 | 104.6631 | 103.7064 | 123.4589 | 93.1046 | -0.3891 | 104.6631 | 103.7064 | 93.1046 | -0.013733 | 123.4589 | -20.05 | -123.7198
2160.9844 | 123.5092 | -104.3793 | 18.869 | -0.21657 | 0.012723 | -0.040324 | 0.0408 | -0.057894 | 0.020855 | 0.10697 | -0.7782 | 0.24719 | -1.1719 | 0.32044 | -104.5349 | -11.8149 | 0.41657 | 19.0338 | 19.075 | -104.805 | 103.2074 | -18.6218 | 103.6011 | 104.6997 | -123.4039 | -0.42572 | 0.20599 | 0.39368 | 104.7958 | 123.4131 | -0.15564 | 104.6265 | 103.6011 | 123.4543 | 92.5644 | -0.42572 | 104.6265 | 103.6011 | 92.5644 | -0.15564 | 123.4543 | -20.0409 | -123.674
2161.9219 | 123.4222 | -104.393 | 18.9011 | -0.20131 | 0.038357 | -0.021098 | 0.073911 | -0.045077 | 0.060375 | 0.085609 | -0.71869 | 0.27466 | -1.1581 | 0.47607 | -104.4113 | -11.5723 | 0.27466 | 19.1116 | 19.0384 | -104.8279 | 103.2349 | -18.6264 | 103.6743 | 104.8691 | -123.3124 | -0.43488 | 0.13733 | 0.43945 | 104.6677 | 123.5046 | -0.018311 | 104.6677 | 103.6743 | 123.4314 | 92.8207 | -0.43488 | 104.6677 | 103.6743 | 92.8207 | -0.018311 | 123.4314 | -20.0592 | -123.7289
2162.9844 | 123.4955 | -104.4708 | 18.7637 | -0.30813 | 0.023404 | -0.026438 | 0.054685 | -0.05469 | 0.020855 | 0.10377 | -0.72327 | 0.24719 | -1.1398 | 0.29755 | -104.6082 | -11.6318 | 0.35706 | 18.9423 | 18.9972 | -104.9103 | 103.331 | -18.5165 | 103.7476 | 104.7684 | -123.3719 | -0.43945 | 0.23346 | 0.41656 | 104.8279 | 123.4131 | -0.13733 | 104.718 | 103.7476 | 123.468 | 92.8391 | -0.43945 | 104.718 | 103.7476 | 92.8391 | -0.13733 | 123.468 | -19.9036 | -123.674
2163.9219 | 123.436 | -104.6494 | 18.6722 | -0.18605 | 0.039425 | -0.029642 | 0.072843 | -0.047213 | 0.045422 | 0.085609 | -0.47607 | 0.27924 | -0.91095 | 0.46234 | -104.6677 | 18.6676 | 0.27924 | 18.8873 | 18.8187 | -105.043 | 103.7384 | -18.3929 | 104.1733 | 105.1117 | -123.3398 | -0.39368 | 0.14648 | 0.43488 | 104.9286 | 123.5367 | -0.018311 | 104.9286 | 104.1733 | 123.468 | 123.317 | -0.39368 | 104.9286 | 104.1733 | 123.317 | -0.018311 | 123.468 | -19.5831 | -123.7152
2164.9844 | 123.4177 | -104.6951 | 18.6447 | -0.10976 | 0.03088 | -0.017893 | 0.074979 | -0.046145 | 0.056103 | 0.092017 | -0.47607 | 0.27008 | -0.9201 | 0.44403 | -104.6997 | 18.631 | 0.25635 | 18.8461 | 18.7592 | -105.1071 | 103.775 | -18.3746 | 104.2191 | 105.1392 | -123.3444 | -0.41199 | 0.11444 | 0.44403 | 104.9515 | 123.5413 | -0.004578 | 104.9652 | 104.2191 | 123.4543 | 123.3261 | -0.41199 | 104.9652 | 104.2191 | 123.3261 | -0.004578 | 123.4543 | -19.5648 | -123.7518
2165.9219 | 123.4268 | -104.6814 | 18.6356 | -0.079243 | 0.043698 | -0.022166 | 0.078184 | -0.039736 | 0.061443 | 0.087745 | -0.50812 | 0.31128 | -0.93384 | 0.45319 | -104.686 | 18.6356 | 0.27924 | 18.8507 | 18.7958 | -105.098 | 103.7476 | -18.3243 | 104.1733 | 105.1346 | -123.3215 | -0.41656 | 0.16022 | 0.42572 | 104.9606 | 123.5321 | -0.004578 | 104.9927 | 104.1733 | 123.4772 | 123.317 | -0.41656 | 104.9927 | 104.1733 | 123.317 | -0.004578 | 123.4772 | -19.5694 | -123.7335
2166.9219 | 123.4268 | -104.6768 | 18.663 | -0.32338 | 0.03088 | -0.029642 | 0.06323 | -0.045077 | 0.040081 | 0.093085 | -0.50812 | 0.28839 | -0.88806 | 0.5127 | -104.6494 | 18.7088 | 0.24719 | 18.9194 | 18.8004 | -105.0201 | 103.7888 | -18.3746 | 104.1687 | 105.1895 | -123.3124 | -0.34332 | 0.13733 | 0.37994 | 104.924 | 123.5962 | 0.027466 | 104.9652 | 104.1687 | 123.4772 | 123.3856 | -0.34332 | 104.9652 | 104.1687 | 123.3856 | 0.027466 | 123.4772 | -19.5511 | -123.6832
2167.9219 | 123.4772 | -104.7638 | 18.6264 | -0.27761 | 0.022336 | -0.038187 | 0.067503 | -0.038668 | 0.048626 | 0.093085 | -0.54016 | 0.27466 | -0.92926 | 0.45776 | -104.7226 | 18.6127 | 0.2243 | 18.8324 | 18.6996 | -105.1346 | 103.8345 | -18.3517 | 104.2236 | 105.2216 | -123.349 | -0.37079 | 0.073242 | 0.3891 | 104.9881 | 123.5962 | 0.041199 | 105.0385 | 104.2236 | 123.4634 | 123.3765 | -0.37079 | 105.0385 | 104.2236 | 123.3765 | 0.041199 | 123.4634 | -19.5557 | -123.761
2168.9844 | 123.4039 | -104.7592 | 18.6035 | -0.38442 | 0.029812 | -0.037119 | 0.073911 | -0.049349 | 0.041149 | 0.10056 | -0.54016 | 0.28381 | -0.92468 | 0.4715 | -104.7363 | 18.6172 | 0.20599 | 18.8232 | 18.7134 | -105.1483 | 103.8345 | -18.3197 | 104.2191 | 105.2307 | -123.3398 | -0.3891 | 0.10986 | 0.38452 | 104.9652 | 123.5825 | 0.022888 | 105.043 | 104.2191 | 123.4726 | 123.3765 | -0.3891 | 105.043 | 104.2191 | 123.3765 | 0.022888 | 123.4726 | -19.5282 | -123.7518
2169.9219 | 123.3856 | -104.837 | 18.5394 | -0.38442 | 0.024472 | -0.028574 | 0.06323 | -0.047213 | 0.036877 | 0.099494 | -0.55389 | 0.29755 | -0.90637 | 0.46692 | -104.8141 | 18.5532 | 0.21057 | 18.782 | 18.6539 | -105.2032 | 103.9307 | -18.2419 | 104.2831 | 105.304 | -123.3536 | -0.36621 | 0.11444 | 0.35248 | 105.0476 | 123.6191 | 0.022888 | 105.1346 | 104.2831 | 123.4909 | 123.3902 | -0.36621 | 105.1346 | 104.2831 | 123.3902 | 0.022888 | 123.4909 | -19.4458 | -123.7427
2170.9688 | 123.468 | -104.8096 | 18.4982 | 0.088604 | 0.021267 | -0.014689 | 0.038663 | -0.063235 | 0.025128 | 0.094154 | -0.59509 | 0.25177 | -0.94299 | 0.3067 | -104.892 | 18.4525 | 0.3479 | 18.6539 | 18.6813 | -105.249 | 103.8666 | -18.2465 | 104.2145 | 105.1163 | -123.3902 | -0.43945 | 0.18311 | 0.3479 | 105.1575 | 123.4634 | -0.082398 | 105.0613 | 104.2145 | 123.4909 | 123.262 | -0.43945 | 105.0613 | 104.2145 | 123.262 | -0.082398 | 123.4909 | -19.4412 | -123.7473
2171.9219 | 123.3948 | -104.9103 | 18.4387 | -0.36916 | 0.034085 | -0.056345 | 0.056821 | -0.064303 | 0.04649 | 0.098426 | -0.47607 | 0.28839 | -0.84686 | 0.46692 | -104.9057 | 18.4845 | 0.20142 | 18.6813 | 18.5577 | -105.3131 | 104.0634 | -18.1503 | 104.4342 | 105.3772 | -123.3444 | -0.40283 | 0.11902 | 0.37079 | 105.1117 | 123.5916 | 0.004577 | 105.1987 | 104.4342 | 123.468 | 123.3948 | -0.40283 | 105.1987 | 104.4342 | 123.3948 | 0.004577 | 123.468 | -19.2856 | -123.7518
2172.9844 | 123.4634 | -104.8187 | 18.4982 | 0.1649 | 0.0052458 | -0.013621 | 0.053617 | -0.063235 | 0.019787 | 0.094154 | -0.54474 | 0.23804 | -0.86517 | 0.32044 | -104.9011 | 18.4662 | 0.32959 | 18.6584 | 18.663 | -105.2124 | 103.9536 | -18.2602 | 104.274 | 105.1392 | -123.3994 | -0.39368 | 0.1648 | 0.32043 | 105.1483 | 123.4772 | -0.082397 | 105.0568 | 104.274 | 123.4818 | 123.2849 | -0.39368 | 105.0568 | 104.274 | 123.2849 | -0.082397 | 123.4818 | -19.3634 | -123.7106
2173.9219 | 123.4863 | -104.7134 | 18.576 | 0.47007 | 0.035153 | -0.044596 | 0.065366 | -0.060031 | 0.056103 | 0.095222 | -0.4715 | 0.24261 | -0.87891 | 0.37994 | -104.8233 | 18.4937 | 0.43488 | 18.7042 | 18.7637 | -105.1529 | 103.8345 | -18.3334 | 104.2419 | 105.0934 | -123.3994 | -0.43945 | 0.18768 | 0.40741 | 105.1483 | 123.4177 | -0.10986 | 104.9561 | 104.2419 | 123.4772 | 123.2071 | -0.43945 | 104.9561 | 104.2419 | 123.2071 | -0.10986 | 123.4772 | -19.455 | -123.7289
2174.9844 | 123.4589 | -104.6951 | 18.5989 | 0.14964 | 0.022336 | -0.038187 | 0.051481 | -0.062167 | 0.0294 | 0.09629 | -0.48065 | 0.24719 | -0.90179 | 0.40283 | -104.7867 | 18.5623 | 0.3891 | 18.7866 | 18.7775 | -105.1254 | 103.7933 | -18.3517 | 104.2145 | 105.098 | -123.3856 | -0.4303 | 0.17853 | 0.42114 | 105.0842 | 123.4817 | -0.091553 | 104.9423 | 104.2145 | 123.4726 | 123.2574 | -0.4303 | 104.9423 | 104.2145 | 123.2574 | -0.091553 | 123.4726 | -19.5007 | -123.7244
2175.9219 | 123.381 | -104.7455 | 18.6172 | -0.64382 | 0.022336 | -0.04246 | 0.070707 | -0.058962 | 0.037945 | 0.088813 | -0.46234 | 0.2655 | -0.83313 | 0.59967 | -104.7363 | 18.6127 | 0.38452 | 18.837 | 18.7592 | -105.1209 | 103.9124 | -18.3517 | 104.2831 | 105.3452 | -123.3536 | -0.37537 | 0.14191 | 0.37079 | 105.13 | 123.5825 | 0.009155 | 105.011 | 104.2831 | 123.5046 | 123.3582 | -0.37537 | 105.011 | 104.2831 | 123.3582 | 0.009155 | 123.5046 | -19.4504 | -123.7381
2176.9844 | 123.4909 | -104.6494 | 18.6081 | 0.40904 | 0.029812 | -0.029642 | 0.062162 | -0.057894 | 0.041149 | 0.10377 | -0.55389 | 0.23804 | -0.98877 | 0.56763 | -104.7958 | 18.5349 | 0.60883 | 18.75 | 18.7958 | -105.1071 | 103.6606 | -18.3701 | 104.0955 | 105.217 | -123.4039 | -0.45776 | 0.18768 | 0.43488 | 105.2582 | 123.3994 | -0.14648 | 104.8874 | 104.0955 | 123.4451 | 123.1842 | -0.45776 | 104.8874 | 104.0955 | 123.1842 | -0.14648 | 123.4451 | -19.5969 | -123.7152
2177.9219 | 123.4634 | -104.6448 | 18.6401 | -0.39968 | 0.021267 | -0.046732 | 0.054685 | -0.055758 | 0.0294 | 0.10484 | -0.44861 | 0.24719 | -0.82855 | 0.58594 | -104.7409 | 18.6356 | 0.53101 | 18.837 | 18.8049 | -105.0613 | 103.8162 | -18.3929 | 104.1962 | 105.2307 | -123.381 | -0.41657 | 0.1648 | 0.37994 | 105.1758 | 123.4817 | -0.096131 | 104.892 | 104.1962 | 123.4497 | 123.2803 | -0.41657 | 104.892 | 104.1962 | 123.2803 | -0.096131 | 123.4497 | -19.4687 | -123.7015
2178.9844 | 123.4039 | -104.4662 | 18.869 | -0.0029495 | 0.036221 | -0.0082804 | 0.084592 | -0.060031 | 0.053967 | 0.090949 | -0.42572 | 0.28839 | -0.86975 | 0.74158 | -104.4479 | 18.869 | 0.49439 | 19.0933 | 19.0018 | -104.8691 | 103.5965 | -18.5806 | 104.0405 | 105.2078 | -123.317 | -0.40283 | 0.13275 | 0.44403 | 104.9606 | 123.5596 | 0.018311 | 104.7546 | 104.0405 | 123.468 | 123.3353 | -0.40283 | 104.7546 | 104.0405 | 123.3353 | 0.018311 | 123.468 | -19.7388 | -123.7381
2179.9219 | 123.4909 | -104.4525 | 18.8416 | -0.30813 | 0.02554 | -0.04246 | 0.052549 | -0.065371 | 0.025128 | 0.092017 | -0.37994 | 0.23346 | -0.79651 | 0.5722 | -104.6173 | 18.7454 | 0.60425 | 18.9423 | 18.988 | -104.892 | 103.656 | -18.6081 | 104.0726 | 105.0247 | -123.4589 | -0.43945 | 0.14648 | 0.41657 | 105.0568 | 123.3948 | -0.16479 | 104.686 | 104.0726 | 123.4406 | 123.1979 | -0.43945 | 104.686 | 104.0726 | 123.1979 | -0.16479 | 123.4406 | -19.6381 | -123.7335
2180.9844 | 123.4726 | -121.6324 | 1.6754 | 0.33274 | 0.015927 | -0.027506 | 0.069639 | -0.082461 | 0.033672 | 0.097358 | -0.9613 | 0.2243 | -1.3504 | 0.88348 | -121.7697 | -9.6634 | 0.93842 | 1.7166 | 1.8677 | -122.1176 | 120.282 | -1.4511 | 120.6711 | 122.5159 | -123.4451 | -0.48523 | 0.19226 | 0.3891 | 122.5708 | 123.349 | -0.13733 | 121.8567 | 120.6711 | 123.5001 | 111.969 | -0.48523 | 121.8567 | 120.6711 | 111.969 | -0.13733 | 123.5001 | -3.0258 | -123.793
2181.9219 | 123.4818 | -122.2549 | 1.1124 | -0.36916 | 0.027676 | -0.032847 | 0.076048 | -0.073916 | 0.018719 | 0.098426 | -0.81024 | 0.21973 | -1.2268 | 0.84686 | -122.374 | -16.3879 | 0.86517 | 1.1719 | 1.3275 | -122.699 | 121.0281 | -0.89264 | 121.4447 | 123.1018 | -123.4863 | -0.44403 | 0.21515 | 0.41656 | 123.1201 | 123.4268 | -0.11902 | 122.4747 | 121.4447 | 123.5825 | 105.867 | -0.44403 | 122.4747 | 121.4447 | 105.867 | -0.11902 | 123.5825 | -2.3392 | -123.8113
2182.9844 | 123.4726 | -122.0078 | 1.3733 | 0.01231 | 0.018063 | -0.032847 | 0.067503 | -0.069644 | 0.035809 | 0.094154 | -0.90637 | 0.24261 | -1.2497 | 1.1673 | -122.081 | -14.2456 | 1.1444 | 1.4511 | 1.5564 | -122.3831 | 120.7581 | -1.1307 | 121.1014 | 123.175 | -123.4543 | -0.37537 | 0.1831 | 0.34332 | 123.1522 | 123.4589 | -0.073243 | 122.2504 | 121.1014 | 123.5641 | 107.7621 | -0.37537 | 122.2504 | 121.1014 | 107.7621 | -0.073243 | 123.5641 | -2.623 | -123.7564
2183.9219 | 123.4039 | -104.2923 | 19.075 | 0.40904 | 0.028744 | -0.0082804 | 0.084592 | -0.056826 | 0.035809 | 0.095222 | -0.62714 | 0.26093 | -1.0025 | 0.98877 | -104.2648 | -10.8261 | 0.737 | 19.2947 | 19.1666 | -104.6448 | 103.2898 | -18.8141 | 103.6652 | 105.2811 | -123.3398 | -0.35248 | 0.091553 | 0.37537 | 105.0293 | 123.587 | 0.027465 | 104.5532 | 103.6652 | 123.4589 | 93.4662 | -0.35248 | 104.5532 | 103.6652 | 93.4662 | 0.027465 | 123.4589 | -20.0775 | -123.7198
2184.9844 | 123.4543 | -104.2328 | 19.0567 | 0.348 | 0.039425 | -0.04246 | 0.058958 | -0.058962 | 0.026196 | 0.092017 | -0.64087 | 0.23804 | -1.0345 | 0.82398 | -104.3198 | -10.7895 | 0.83771 | 19.2215 | 19.249 | -104.631 | 103.1982 | -18.8187 | 103.5919 | 105.0568 | -123.3765 | -0.39825 | 0.19226 | 0.39368 | 105.0705 | 123.4543 | -0.086975 | 104.4708 | 103.5919 | 123.4818 | 93.4433 | -0.39825 | 104.4708 | 103.5919 | 93.4433 | -0.086975 | 123.4818 | -20.0912 | -123.6877
2185.9219 | 106.398 | -105.4001 | 17.8391 | -0.32338 | 0.022336 | -0.02537 | 0.060026 | -0.066439 | 0.025128 | 0.09629 | -0.58136 | 0.22888 | -1.0162 | 0.71869 | -105.5832 | -11.7188 | 0.77362 | 17.9489 | 18.0176 | -105.9311 | 104.3839 | -17.6102 | 104.8187 | 106.1188 | -123.4222 | -0.53101 | 0.17853 | 0.43488 | 106.1737 | 123.349 | -0.18311 | 105.629 | 104.8187 | 123.4177 | 93.6813 | -0.53101 | 105.629 | 104.8187 | 93.6813 | -0.18311 | 123.4177 | -18.8553 | -123.7701
2186.9844 | 123.4909 | -106.5399 | 16.7267 | 0.4243 | 0.026608 | -0.037119 | 0.060026 | -0.064303 | 0.036877 | 0.10163 | -0.6546 | 0.2243 | -1.0757 | 0.73242 | -106.6772 | -11.4853 | 0.78735 | 16.8503 | 16.9144 | -107.0023 | 105.4642 | -16.5024 | 105.8853 | 107.2723 | -123.4039 | -0.46234 | 0.18768 | 0.42114 | 107.3273 | 123.3902 | -0.13733 | 106.7642 | 105.8853 | 123.4543 | 95.0546 | -0.46234 | 106.7642 | 105.8853 | 95.0546 | -0.13733 | 123.4543 | -17.8024 | -123.7289
2187.9219 | 122.8546 | -93.4662 | 31.1737 | 0.073345 | 0.024472 | -0.037119 | 0.053617 | -0.064303 | 0.032604 | 0.10163 | -0.54016 | 0.24261 | -0.92926 | 1.2085 | -96.4142 | -9.5306 | 1.2268 | 33.7143 | 27.063 | -95.462 | 92.5369 | -30.9311 | 92.926 | 94.6747 | -127.5879 | -1.9958 | -4.1107 | 0.3891 | 94.693 | 127.1805 | -2.948 | 93.7088 | 92.926 | 120.5292 | 83.9355 | -1.9958 | 93.7088 | 92.926 | 83.9355 | -2.948 | 120.5292 | -32.103 | -126.6357
2188.9844 | 123.6191 | -106.7825 | 16.3147 | 0.073345 | 0.049038 | -0.039256 | 0.084592 | -0.064303 | 0.049694 | 0.09629 | -0.69122 | 0.27924 | -1.0803 | 0.92926 | -108.1192 | -11.0458 | 0.6546 | 15.3992 | 15.3397 | -108.1421 | 105.7022 | -16.0355 | 106.0913 | 107.7118 | -124.4339 | -1.3596 | -0.97504 | 0.3891 | 107.4371 | 122.1817 | -1.3367 | 107.0618 | 106.0913 | 122.1222 | 95.7367 | -1.3596 | 107.0618 | 106.0913 | 95.7367 | -1.3367 | 122.1222 | -17.395 | -124.4568
2189.9219 | 123.5229 | -108.3069 | 14.9734 | 0.01231 | 0.013791 | -0.032847 | 0.051481 | -0.058962 | 0.019787 | 0.089881 | -0.66834 | 0.24719 | -1.0757 | 0.71869 | -108.4442 | -11.2564 | 0.79193 | 15.065 | 15.1566 | -108.7601 | 107.2311 | -14.7263 | 107.6385 | 109.0256 | -123.4177 | -0.45319 | 0.18311 | 0.40741 | 109.0988 | 123.3719 | -0.13733 | 108.5541 | 107.6385 | 123.4634 | 97.0505 | -0.45319 | 108.5541 | 107.6385 | 97.0505 | -0.13733 | 123.4634 | -16.0492 | -123.7335
2190.9844 | 123.4497 | -104.599 | 18.663 | 0.39378 | 0.024472 | -0.049937 | 0.053617 | -0.065371 | 0.035809 | 0.089881 | -0.71411 | 0.23804 | -1.1169 | 0.46692 | -104.686 | -10.437 | 0.46692 | 18.8416 | 18.8461 | -105.011 | 103.4821 | -18.425 | 103.8849 | 105.0659 | -123.349 | -0.41199 | 0.1831 | 0.40283 | 105.0659 | 123.4406 | -0.086975 | 104.837 | 103.8849 | 123.4451 | 94.162 | -0.41199 | 104.837 | 103.8849 | 94.162 | -0.086975 | 123.4451 | -19.78 | -123.674
2191.9219 | 113.6124 | -112.0514 | 11.087 | -0.094502 | 0.023404 | -0.052073 | 0.055753 | -0.076052 | 0.020855 | 0.089881 | -0.77362 | 0.25635 | -1.181 | 0.25177 | -112.2849 | -12.7945 | 0.3479 | 11.1145 | 11.3159 | -112.6648 | 110.8704 | -10.8307 | 111.2778 | 112.3032 | -123.3719 | -0.6134 | 0.22888 | 0.40741 | 112.3993 | 123.1659 | -0.23346 | 112.3077 | 111.2778 | 123.3673 | 99.2569 | -0.6134 | 112.3077 | 111.2778 | 99.2569 | -0.23346 | 123.3673 | -12.2681 | -123.7518
2192.9844 | 123.3902 | -104.0497 | 18.9423 | 0.39378 | 0.049038 | -0.0082804 | 0.074979 | -0.052554 | 0.05183 | 0.086677 | -0.74158 | 0.28381 | -1.1353 | 0.65002 | -104.0634 | -11.4624 | 0.38452 | 19.5099 | 19.3909 | -104.4296 | 102.9144 | -18.6584 | 103.3081 | 104.6997 | -123.0057 | -0.37994 | 0.44861 | 0.39368 | 104.4342 | 123.5596 | -0.013733 | 104.3335 | 103.3081 | 123.4406 | 92.5873 | -0.37994 | 104.3335 | 103.3081 | 92.5873 | -0.013733 | 123.4406 | -20.0775 | -123.3719
2193.9219 | 123.5229 | -110.8154 | 12.4008 | -0.033467 | 0.013791 | -0.051005 | 0.058958 | -0.068576 | 0.027264 | 0.10163 | -0.84228 | 0.23804 | -1.2177 | 0.30212 | -111.0168 | -18.7088 | 0.36163 | 12.529 | 12.561 | -111.3235 | 109.5978 | -12.1628 | 109.9731 | 111.1176 | -123.4177 | -0.50812 | 0.16022 | 0.37537 | 111.1771 | 123.3444 | -0.20142 | 111.0535 | 109.9731 | 123.3765 | 92.1066 | -0.50812 | 111.0535 | 109.9731 | 92.1066 | -0.20142 | 123.3765 | -13.6185 | -123.7244
2194.9844 | 123.4222 | -103.7247 | 19.5145 | 0.45481 | 0.038357 | -0.0082804 | 0.082456 | -0.057894 | 0.044354 | 0.092017 | -0.79651 | 0.3067 | -1.2039 | 0.63171 | -103.6743 | -11.4258 | 0.42572 | 19.7754 | 19.693 | -104.1412 | 102.5208 | -19.2078 | 102.9282 | 104.3564 | -123.1888 | -0.41656 | 0.17853 | 0.40741 | 104.1504 | 123.5001 | 0.050354 | 104.0314 | 102.9282 | 123.4177 | 92.2989 | -0.41656 | 104.0314 | 102.9282 | 92.2989 | 0.050354 | 123.4177 | -20.7184 | -123.6557
2195.9219 | 123.5458 | -112.468 | 10.8353 | -0.079243 | 0.020199 | -0.038187 | 0.053617 | -0.068576 | 0.014446 | 0.1059 | -0.86975 | 0.24261 | -1.2589 | 0.27466 | -112.5961 | -13.884 | 0.33875 | 10.9634 | 11.0184 | -112.8937 | 111.2091 | -10.5927 | 111.5982 | 112.7426 | -123.4314 | -0.42572 | 0.18311 | 0.3891 | 112.8067 | 123.4314 | -0.12817 | 112.7106 | 111.5982 | 123.4863 | 98.584 | -0.42572 | 112.7106 | 111.5982 | 98.584 | -0.12817 | 123.4863 | -12.0941 | -123.7289
2196.9844 | 123.3582 | -104.155 | 19.0704 | 0.63792 | 0.03088 | -0.044596 | 0.081388 | -0.053622 | 0.042217 | 0.087745 | -0.80109 | 0.29297 | -1.2085 | 0.66834 | -103.9764 | -11.7874 | 0.31128 | 19.3359 | 19.3588 | -104.5898 | 102.9465 | -18.7775 | 103.3539 | 104.8233 | -123.0469 | -0.43488 | 0.28839 | 0.40741 | 104.4662 | 123.4909 | 0.17853 | 104.4479 | 103.3539 | 123.5138 | 92.3676 | -0.43488 | 104.4479 | 103.3539 | 92.3676 | 0.17853 | 123.5138 | -20.2789 | -123.6603
2197.9219 | 123.468 | -108.0826 | 15.152 | 0.19541 | 0.013791 | -0.036051 | 0.06323 | -0.061099 | 0.033672 | 0.090949 | -0.95673 | 0.23346 | -1.3 | 0.39368 | -108.197 | -13.7192 | 0.35706 | 15.3671 | 15.358 | -108.5312 | 106.7825 | -14.9185 | 107.1259 | 108.4763 | -123.349 | -0.44861 | 0.20599 | 0.34332 | 108.4396 | 123.4497 | -0.11444 | 108.316 | 107.1259 | 123.4406 | 94.3634 | -0.44861 | 108.316 | 107.1259 | 94.3634 | -0.11444 | 123.4406 | -16.452 | -123.6832
2198.9844 | 123.4863 | -119.6091 | 3.7399 | 0.14964 | 0.018063 | -0.036051 | 0.061094 | -0.07178 | 0.025128 | 0.089881 | -1.1948 | 0.27008 | -1.5472 | 0.60425 | -119.751 | -15.6967 | 0.58594 | 3.7491 | 3.8727 | -120.0851 | 118.0618 | -3.4698 | 118.4143 | 120.2133 | -123.4909 | -0.47607 | 0.13275 | 0.35248 | 120.195 | 123.3582 | -0.14191 | 119.8792 | 118.4143 | 123.4818 | 103.9124 | -0.47607 | 119.8792 | 118.4143 | 103.9124 | -0.14191 | 123.4818 | -5.2872 | -123.8251
2199.9219 | 123.5184 | -112.6328 | 10.6018 | -0.20131 | 0.026608 | -0.031779 | 0.055753 | -0.067507 | 0.022991 | 0.093085 | -0.95673 | 0.26093 | -1.3596 | 0.23346 | -112.8113 | -14.0167 | 0.32959 | 10.7254 | 10.8261 | -113.0676 | 111.2732 | -10.3409 | 111.676 | 112.8662 | -123.4131 | -0.43488 | 0.2243 | 0.40283 | 112.9623 | 123.3582 | -0.17853 | 112.8937 | 111.676 | 123.4589 | 98.616 | -0.43488 | 112.8937 | 111.676 | 98.616 | -0.17853 | 123.4589 | -11.9614 | -123.6694
2200.9844 | 123.4451 | -114.5187 | 8.7021 | 0.43956 | 0.038357 | -0.045664 | 0.082456 | -0.066439 | 0.04649 | 0.080268 | -1.2909 | 0.2655 | -1.6937 | 0.33875 | -114.5554 | -26.9714 | 0.18768 | 8.8531 | 8.9172 | -114.9857 | 112.825 | -8.4366 | 113.2278 | 114.8575 | -123.2574 | -0.46692 | 0.21515 | 0.40283 | 114.7064 | 123.3719 | -0.036621 | 114.7842 | 113.2278 | 123.436 | 87.5473 | -0.46692 | 114.7842 | 113.2278 | 87.5473 | -0.036621 | 123.436 | -10.3958 | -123.6877
2201.9219 | 123.4543 | -114.3814 | 8.9447 | 0.073345 | 0.03088 | -0.060618 | 0.05789 | -0.078189 | 0.021923 | 0.1027 | -1.1536 | 0.24719 | -1.4694 | 0.21973 | -114.4592 | -15.9943 | 0.21057 | 9.0546 | 9.1187 | -114.7659 | 112.912 | -8.6975 | 113.2278 | 114.6011 | -123.4039 | -0.38452 | 0.17395 | 0.31586 | 114.592 | 123.436 | -0.07782 | 114.6286 | 113.2278 | 123.5001 | 98.3871 | -0.38452 | 114.6286 | 113.2278 | 98.3871 | -0.07782 | 123.5001 | -10.4141 | -123.7106
2202.9844 | 123.4818 | -114.4043 | 8.8211 | 0.48533 | 0.040494 | -0.016825 | 0.085661 | -0.069644 | 0.045422 | 0.086677 | -1.2177 | 0.25177 | -1.6251 | 0.29755 | -114.5508 | -29.6677 | 0.21057 | 8.963 | 9.0088 | -114.917 | 112.7792 | -8.5693 | 113.1866 | 114.7018 | -123.3719 | -0.51269 | 0.18768 | 0.40741 | 114.6149 | 123.3673 | -0.14648 | 114.6561 | 113.1866 | 123.4131 | 84.7366 | -0.51269 | 114.6561 | 113.1866 | 84.7366 | -0.14648 | 123.4131 | -10.4462 | -123.7381
2203.9219 | 123.4634 | -119.0826 | 4.2206 | 0.19541 | 0.021267 | -0.02537 | 0.067503 | -0.065371 | 0.0294 | 0.097358 | -1.3733 | 0.23804 | -1.7212 | 0.11902 | -119.22 | -25.0351 | 0.091553 | 4.3121 | 4.4083 | -119.4946 | 117.3615 | -3.9825 | 117.7094 | 119.2017 | -123.4406 | -0.41199 | 0.18768 | 0.3479 | 119.1742 | 123.3948 | -0.13733 | 119.3207 | 117.7094 | 123.4909 | 94.0475 | -0.41199 | 119.3207 | 117.7094 | 94.0475 | -0.13733 | 123.4909 | -5.9418 | -123.7152
2204.9688 | 123.3627 | -122.2549 | 1.1261 | 0.50059 | 0.044766 | -0.017893 | 0.089933 | -0.073916 | 0.044354 | 0.090949 | -1.4786 | 0.28381 | -1.8539 | 0.21515 | -122.2137 | -25.946 | -0.082397 | 1.3 | 1.2772 | -122.6349 | 120.401 | -0.84229 | 120.7764 | 122.4701 | -123.3398 | -0.37994 | 0.15106 | 0.37537 | 122.1725 | 123.555 | 0.041199 | 122.5388 | 120.7764 | 123.5321 | 96.3089 | -0.37994 | 122.5388 | 120.7764 | 96.3089 | 0.041199 | 123.5321 | -2.98 | -123.761
2205.9219 | 123.4543 | -122.4609 | 0.9201 | 0.348 | 0.022336 | -0.033915 | 0.073911 | -0.07178 | 0.032604 | 0.10056 | -1.5335 | 0.23346 | -1.886 | 0.036621 | -122.5296 | -30.1163 | 0.022888 | 0.98877 | 1.1078 | -122.8683 | 120.575 | -0.68665 | 120.9274 | 122.4976 | -123.4497 | -0.40741 | 0.18768 | 0.35248 | 122.4838 | 123.4497 | -0.068665 | 122.6944 | 120.9274 | 123.5687 | 92.3447 | -0.40741 | 122.6944 | 120.9274 | 92.3447 | -0.068665 | 123.5687 | -2.8061 | -123.7885
2206.9844 | 123.4039 | -122.5571 | 0.90637 | 0.11912 | 0.045834 | -0.015757 | 0.085661 | -0.066439 | 0.060375 | 0.094154 | -1.3687 | 0.29297 | -1.7761 | 0.20599 | -122.4747 | -26.8707 | -0.064087 | 1.0574 | 1.0391 | -122.9279 | 120.7809 | -0.6134 | 121.1884 | 122.7631 | -123.381 | -0.37079 | 0.13275 | 0.40741 | 122.493 | 123.6145 | 0.082398 | 122.85 | 121.1884 | 123.5962 | 95.6863 | -0.37079 | 122.85 | 121.1884 | 95.6863 | 0.082398 | 123.5962 | -2.6825 | -123.8342
2207.9219 | 123.468 | -122.5845 | 0.79651 | 0.13438 | 0.015927 | -0.02537 | 0.05789 | -0.064303 | 0.017651 | 0.090949 | -1.4648 | 0.25635 | -1.799 | 0.027466 | -122.6486 | -24.7742 | 0.022888 | 0.87433 | 0.98419 | -123.0057 | 120.7855 | -0.54016 | 121.1197 | 122.612 | -123.4451 | -0.42114 | 0.18768 | 0.33417 | 122.6074 | 123.4589 | -0.064087 | 122.8409 | 121.1197 | 123.5687 | 97.8104 | -0.42114 | 122.8409 | 121.1197 | 97.8104 | -0.064087 | 123.5687 | -2.5955 | -123.8022
2208.9844 | 123.1476 | -122.644 | 0.79193 | 0.10386 | 0.041562 | -0.030711 | 0.098478 | -0.066439 | 0.053967 | 0.097358 | -1.3962 | 0.28839 | -1.8082 | 0.19684 | -122.58 | -24.3851 | -0.10071 | 0.95215 | 0.9201 | -123.0103 | 120.8359 | -0.50354 | 121.2479 | 122.8409 | -123.3719 | -0.36621 | 0.12817 | 0.41199 | 122.5433 | 123.5962 | 0.064087 | 122.9324 | 121.2479 | 123.5641 | 98.259 | -0.36621 | 122.9324 | 121.2479 | 98.259 | 0.064087 | 123.5641 | -2.6001 | -123.8022
2209.9219 | 123.4451 | -122.6395 | 0.74158 | 0.1649 | 0.015927 | -0.037119 | 0.065366 | -0.07178 | 0.026196 | 0.10484 | -1.5427 | 0.25177 | -1.8906 | 0.013733 | -122.7127 | -29.2694 | -0.009155 | 0.83313 | 0.94757 | -123.0377 | 120.7489 | -0.48981 | 121.0968 | 122.6532 | -123.4543 | -0.39825 | 0.20599 | 0.3479 | 122.6303 | 123.4726 | -0.073243 | 122.8912 | 121.0968 | 123.587 | 93.3701 | -0.39825 | 122.8912 | 121.0968 | 93.3701 | -0.073243 | 123.587 | -2.6321 | -123.7793
2210.9688 | 123.4177 | -122.5845 | 0.75073 | -0.27761 | 0.04797 | -0.04246 | 0.082456 | -0.067507 | 0.034741 | 0.089881 | -1.4099 | 0.28381 | -1.7899 | 0.16022 | -122.6624 | -26.532 | -0.068665 | 0.89264 | 0.90637 | -123.056 | 120.7947 | -0.46692 | 121.1746 | 122.7448 | -123.4131 | -0.4715 | 0.15564 | 0.37994 | 122.5159 | 123.4772 | -0.07782 | 122.8683 | 121.1746 | 123.4909 | 96.0526 | -0.4715 | 122.8683 | 121.1746 | 96.0526 | -0.07782 | 123.4909 | -2.5406 | -123.8068
2211.9219 | 123.5092 | -122.5067 | 0.81024 | 0.6074 | 0.026608 | -0.015757 | 0.077116 | -0.063235 | 0.034741 | 0.097358 | -1.5884 | 0.24719 | -1.9821 | 0.013733 | -122.6395 | -24.6597 | 0.07782 | 0.8606 | 1.0162 | -122.9507 | 120.5246 | -0.56305 | 120.9183 | 122.5204 | -123.4497 | -0.44403 | 0.20599 | 0.39368 | 122.5845 | 123.3673 | -0.13275 | 122.7539 | 120.9183 | 123.5229 | 97.847 | -0.44403 | 122.7539 | 120.9183 | 97.847 | -0.13275 | 123.5229 | -2.7924 | -123.761
2212.9844 | 123.3673 | -122.6212 | 0.82398 | 0.51585 | 0.036221 | -0.011485 | 0.085661 | -0.064303 | 0.056103 | 0.09629 | -1.5198 | 0.30212 | -1.9043 | 0.21057 | -122.5388 | -21.666 | -0.10986 | 0.98877 | 0.96588 | -122.9828 | 120.7169 | -0.52185 | 121.1014 | 122.8317 | -123.3627 | -0.36163 | 0.14191 | 0.38452 | 122.5113 | 123.6099 | 0.082398 | 122.9233 | 121.1014 | 123.587 | 100.9552 | -0.36163 | 122.9233 | 121.1014 | 100.9552 | 0.082398 | 123.587 | -2.7283 | -123.8068
2213.9219 | 123.4863 | -122.6212 | 0.75531 | 0.37852 | 0.029812 | -0.024302 | 0.069639 | -0.066439 | 0.0294 | 0.097358 | -1.6251 | 0.23804 | -2.005 | 0 | -122.6898 | -26.5549 | 0.050354 | 0.80566 | 0.93842 | -123.0057 | 120.6162 | -0.51727 | 120.9961 | 122.6212 | -123.4451 | -0.38452 | 0.18311 | 0.37994 | 122.6715 | 123.4268 | -0.068664 | 122.8592 | 120.9961 | 123.5596 | 96.0663 | -0.38452 | 122.8592 | 120.9961 | 96.0663 | -0.068664 | 123.5596 | -2.7603 | -123.761
2215.0938 | 123.4406 | -122.6624 | 0.72784 | 0.01231 | 0.028744 | -0.018961 | 0.085661 | -0.060031 | 0.037945 | 0.099494 | -1.4786 | 0.27466 | -1.9135 | 0.15106 | -122.6852 | -21.698 | -0.054932 | 0.86517 | 0.88348 | -123.0652 | 120.7489 | -0.45319 | 121.1838 | 122.8134 | -123.4131 | -0.40283 | 0.15564 | 0.43487 | 122.6074 | 123.5275 | -0.022888 | 122.937 | 121.1838 | 123.5458 | 100.9644 | -0.40283 | 122.937 | 121.1838 | 100.9644 | -0.022888 | 123.5458 | -2.6413 | -123.793
2216.3438 | 123.4818 | -122.438 | 0.97504 | -0.0029495 | 0.028744 | -0.033915 | 0.058958 | -0.066439 | 0.040081 | 0.093085 | -1.5381 | 0.2655 | -1.8906 | -0.018311 | -121.9162 | -22.4625 | 0.022888 | 0.93842 | 1.1765 | -122.8455 | 120.5475 | -0.70953 | 120.9 | 122.4197 | -122.8912 | -0.40741 | 0.20142 | 0.35248 | 122.4609 | 123.3765 | 0.52185 | 122.7036 | 120.9 | 123.6145 | 99.9756 | -0.40741 | 122.7036 | 120.9 | 99.9756 | 0.52185 | 123.6145 | -2.8656 | -123.8205
2217.0938 | 123.4451 | -122.5159 | 0.87433 | -0.018208 | 0.03088 | -0.022166 | 0.095274 | -0.062167 | 0.039013 | 0.094154 | -1.506 | 0.28839 | -1.9272 | 0.15106 | -122.5433 | -23.6023 | -0.045776 | 0.98877 | 1.0391 | -122.9187 | 120.5887 | -0.58594 | 121.0098 | 122.6669 | -123.4177 | -0.40283 | 0.16479 | 0.42114 | 122.4701 | 123.5046 | -0.027466 | 122.8043 | 121.0098 | 123.555 | 98.9136 | -0.40283 | 122.8043 | 121.0098 | 98.9136 | -0.027466 | 123.555 | -2.8015 | -123.793
2218.4375 | 123.4222 | -122.6257 | 0.82855 | -0.094502 | 0.04797 | -0.0061444 | 0.084592 | -0.057894 | 0.057171 | 0.099494 | -1.4557 | 0.27924 | -1.9043 | 0.16479 | -122.5708 | -24.0967 | -0.068665 | 0.95215 | 0.99335 | -122.9874 | 120.7214 | -0.54932 | 121.17 | 122.7905 | -123.3994 | -0.36163 | 0.1648 | 0.44861 | 122.5571 | 123.5779 | 0.054931 | 122.905 | 121.17 | 123.6191 | 98.5291 | -0.36163 | 122.905 | 121.17 | 98.5291 | 0.054931 | 123.6191 | -2.7328 | -123.8159
2218.9688 | 123.3948 | -122.6486 | 0.81024 | 0.14964 | 0.040494 | -0.029642 | 0.084592 | -0.063235 | 0.045422 | 0.095222 | -1.5427 | 0.29297 | -1.9455 | 0.1831 | -122.5845 | -24.1379 | -0.086975 | 0.94757 | 0.92468 | -123.0057 | 120.7031 | -0.51727 | 121.106 | 122.8317 | -123.3948 | -0.35705 | 0.11444 | 0.40283 | 122.5616 | 123.5962 | 0.064087 | 122.9416 | 121.106 | 123.5733 | 98.5107 | -0.35705 | 122.9416 | 121.106 | 98.5107 | 0.064087 | 123.5733 | -2.7557 | -123.8159
2220.6406 | 123.3536 | -122.7493 | 0.71411 | 0.27171 | 0.033017 | -0.030711 | 0.082456 | -0.064303 | 0.048626 | 0.10163 | -1.6205 | 0.29297 | -1.9958 | 0.15564 | -122.7036 | -25.9689 | -0.10986 | 0.90179 | 0.82398 | -123.0606 | 120.7535 | -0.42114 | 121.1288 | 122.905 | -123.4177 | -0.31128 | 0.10986 | 0.37537 | 122.6395 | 123.6511 | 0.045777 | 123.0423 | 121.1288 | 123.5733 | 96.7804 | -0.31128 | 123.0423 | 121.1288 | 96.7804 | 0.045777 | 123.5733 | -2.71 | -123.7747
2221.6094 | 122.5296 | -122.2504 | 0.15106 | 0.45481 | 0.035153 | -0.022166 | 0.10275 | -0.066439 | 0.050762 | 0.12299 | -0.39368 | 0.23346 | -0.83771 | -0.068665 | -122.3557 | -0.059509 | 0.041199 | 0.19226 | 0.33875 | -122.7036 | 121.4127 | 0.082397 | 121.8567 | 122.1817 | -122.5067 | -0.45319 | 0.18768 | 0.44403 | 122.2916 | 122.4426 | -0.10529 | 122.4838 | 121.8567 | 122.5891 | 122.1909 | -0.45319 | 122.4838 | 121.8567 | 122.1909 | -0.10529 | 122.5891 | -0.98877 | -122.8546
2222.1094 | 122.6395 | -122.4976 | 0.16479 | -0.4302 | 0.023404 | -0.036051 | 0.10382 | -0.069644 | -0.02721 | 0.05677 | -0.20142 | 0.25635 | -0.61798 | 0.013733 | -0.027466 | -0.737 | -0.073242 | 0.27008 | 0.3479 | -122.8638 | 121.8796 | 0.091553 | 122.2961 | 122.5113 | -0.19226 | -0.36621 | 0.1831 | 0.41656 | 122.4243 | 122.7676 | 122.4701 | 122.7539 | 122.2961 | 122.8455 | 121.7606 | -0.36621 | 122.7539 | 122.2961 | 121.7606 | 122.4701 | 122.8455 | -0.78278 | -123.0286
2223.5156 | 122.7264 | -122.58 | 0.1831 | 0.24119 | 0.046902 | -0.028574 | 0.12411 | -0.056826 | -0.017597 | 0.058906 | -0.31128 | 0.29297 | -0.6958 | 0.13733 | -0.041199 | 0.041199 | -0.12817 | 0.34332 | 0.31128 | -122.9828 | 121.8842 | 0.10986 | 122.2687 | 122.7173 | -0.2243 | -0.40283 | 0.12817 | 0.38452 | 122.4518 | 122.9233 | 122.5388 | 122.8729 | 122.2687 | 122.8912 | 122.6212 | -0.40283 | 122.8729 | 122.2687 | 122.6212 | 122.5388 | 122.8912 | -0.87891 | -123.1659
2227.2656 | 122.9141 | -122.6624 | 0.15106 | 0.042827 | 0.016995 | -0.022166 | 0.082456 | -0.07712 | -0.045368 | 0.05677 | -0.25635 | 0.2655 | -0.6134 | -0.054932 | -0.19684 | -0.082397 | -0.018311 | 0.23346 | 0.33417 | -123.0972 | 122.049 | 0.11444 | 122.406 | 122.6074 | -0.3479 | -0.43488 | 0.1831 | 0.35706 | 122.644 | 122.8958 | 122.4655 | 122.9279 | 122.406 | 122.9965 | 122.58 | -0.43488 | 122.9279 | 122.406 | 122.58 | 122.4655 | 122.9965 | -0.76447 | -123.2483
2227.9219 | 122.9416 | -122.6669 | 0.13733 | 0.48533 | 0.020199 | -0.028574 | 0.11664 | -0.07178 | -0.022938 | 0.057838 | -0.23346 | 0.24719 | -0.65918 | -0.022888 | -0.17395 | -0.14648 | 0.050354 | 0.18768 | 0.36163 | -123.1338 | 122.0078 | 0.10986 | 122.4335 | 122.644 | -0.31128 | -0.46692 | 0.2243 | 0.42572 | 122.7173 | 122.8546 | 122.493 | 122.9141 | 122.4335 | 123.0286 | 122.5204 | -0.46692 | 122.9141 | 122.4335 | 122.5204 | 122.493 | 123.0286 | -0.79651 | -123.2712
2228.9219 | 122.9782 | -122.644 | 0.13733 | 0.48533 | 0.043698 | -0.0082804 | 0.1145 | -0.073916 | -0.028278 | 0.057838 | -0.21057 | 0.23346 | -0.65002 | -0.004578 | -0.20599 | -0.15106 | 0.045776 | 0.17395 | 0.36163 | -123.1247 | 121.994 | 0.09613 | 122.4335 | 122.6395 | -0.34332 | -0.48065 | 0.2243 | 0.43945 | 122.6898 | 122.818 | 122.438 | 122.8775 | 122.4335 | 123.0057 | 122.493 | -0.48065 | 122.8775 | 122.4335 | 122.493 | 122.438 | 123.0057 | -0.78735 | -123.262
2229.9844 | 122.8867 | -122.7173 | 0.17395 | -0.32338 | 0.033017 | -0.015757 | 0.12091 | -0.060031 | -0.030414 | 0.058906 | -0.19226 | 0.29755 | -0.58594 | 0.14648 | -0.082397 | -0.027466 | -0.10986 | 0.30212 | 0.32959 | -123.1338 | 122.1313 | 0.1236 | 122.525 | 122.8638 | -0.25635 | -0.41656 | 0.15564 | 0.39368 | 122.6074 | 123.0194 | 122.6349 | 123.0148 | 122.525 | 123.0469 | 122.6898 | -0.41656 | 123.0148 | 122.525 | 122.6898 | 122.6349 | 123.0469 | -0.75989 | -123.3078
2230.9219 | 122.9691 | -122.6761 | 0.15106 | 0.31749 | 0.028744 | -0.031779 | 0.11343 | -0.060031 | -0.02187 | 0.058906 | -0.2243 | 0.25177 | -0.66376 | -0.004578 | -0.16022 | -0.13275 | 0.036621 | 0.20142 | 0.36163 | -123.1522 | 122.0123 | 0.10071 | 122.4518 | 122.6715 | -0.31128 | -0.47608 | 0.21057 | 0.43945 | 122.7127 | 122.8775 | 122.5159 | 122.9279 | 122.4518 | 123.0377 | 122.5433 | -0.47608 | 122.9279 | 122.4518 | 122.5433 | 122.5159 | 123.0377 | -0.81482 | -123.3032
2231.9219 | 122.9004 | -122.731 | 0.16479 | 0.40904 | 0.033017 | -0.039256 | 0.1177 | -0.056826 | -0.020801 | 0.052497 | -0.25635 | 0.29297 | -0.66834 | 0.11444 | -0.086975 | 0.013733 | -0.064087 | 0.28381 | 0.32044 | -123.1247 | 122.0627 | 0.12817 | 122.4747 | 122.8455 | -0.25177 | -0.39368 | 0.15564 | 0.41199 | 122.6669 | 123.0148 | 122.644 | 123.024 | 122.4747 | 123.0515 | 122.7448 | -0.39368 | 123.024 | 122.4747 | 122.7448 | 122.644 | 123.0515 | -0.83313 | -123.2895
2232.9844 | 122.9141 | -122.7219 | 0.16937 | -0.0029495 | 0.04263 | -0.014689 | 0.12945 | -0.065371 | -0.017597 | 0.051429 | -0.17395 | 0.28381 | -0.59967 | 0.16479 | -0.10986 | -0.07782 | -0.10529 | 0.31586 | 0.33875 | -123.1522 | 122.1222 | 0.11444 | 122.5479 | 122.8867 | -0.27924 | -0.4303 | 0.16937 | 0.42572 | 122.6166 | 123.0377 | 122.612 | 123.0057 | 122.5479 | 123.0606 | 122.644 | -0.4303 | 123.0057 | 122.5479 | 122.644 | 122.612 | 123.0606 | -0.76904 | -123.3215
2233.9219 | 123.0103 | -122.7219 | 0.14191 | 0.50059 | 0.036221 | -0.024302 | 0.099546 | -0.067507 | -0.02187 | 0.05677 | -0.19226 | 0.22888 | -0.64087 | -0.022888 | -0.23346 | -0.07782 | 0.045776 | 0.18768 | 0.3479 | -123.2025 | 122.081 | 0.086975 | 122.5296 | 122.699 | -0.37537 | -0.48065 | 0.20599 | 0.44861 | 122.7676 | 122.9095 | 122.4884 | 122.9507 | 122.5296 | 123.0698 | 122.644 | -0.48065 | 122.9507 | 122.5296 | 122.644 | 122.4884 | 123.0698 | -0.78278 | -123.3444
2234.9844 | 122.937 | -122.7859 | 0.17395 | -0.079243 | 0.038357 | -0.0072124 | 0.12091 | -0.062167 | -0.016529 | 0.057838 | -0.14648 | 0.30212 | -0.5722 | 0.11902 | -0.14648 | 0.041199 | -0.064087 | 0.28839 | 0.33417 | -123.1796 | 122.2137 | 0.12817 | 122.6395 | 122.905 | -0.32043 | -0.39368 | 0.16022 | 0.42572 | 122.7219 | 123.0743 | 122.6395 | 123.0881 | 122.6395 | 123.1201 | 122.8271 | -0.39368 | 123.0881 | 122.6395 | 122.8271 | 122.6395 | 123.1201 | -0.74615 | -123.3536
2235.9219 | 122.9919 | -122.7585 | 0.16022 | -0.32338 | 0.015927 | -0.034983 | 0.095274 | -0.068576 | -0.035755 | 0.053565 | -0.12817 | 0.24261 | -0.50812 | -0.022888 | -0.28839 | -0.041199 | -0.027466 | 0.2243 | 0.33875 | -123.1796 | 122.2504 | 0.082398 | 122.6303 | 122.7356 | -0.44861 | -0.42114 | 0.17853 | 0.37994 | 122.731 | 122.9828 | 122.4701 | 123.0011 | 122.6303 | 123.0972 | 122.7173 | -0.42114 | 123.0011 | 122.6303 | 122.7173 | 122.4701 | 123.0972 | -0.66833 | -123.3398
2236.9219 | 123.024 | -122.7219 | 0.14191 | 0.50059 | 0.024472 | -0.024302 | 0.10702 | -0.074984 | -0.019733 | 0.064246 | -0.10529 | 0.27008 | -0.53558 | 0.013733 | -0.28839 | -0.050354 | 0.041199 | 0.19684 | 0.3479 | -123.1934 | 122.1863 | 0.12817 | 122.6166 | 122.7356 | -0.4303 | -0.4715 | 0.20599 | 0.4303 | 122.7631 | 122.9187 | 122.4335 | 122.9919 | 122.6166 | 123.0698 | 122.6715 | -0.4715 | 122.9919 | 122.6166 | 122.6715 | 122.4335 | 123.0698 | -0.67749 | -123.3353
2237.9219 | 123.0469 | -122.7585 | 0.14648 | 0.50059 | 0.033017 | -0.022166 | 0.10916 | -0.065371 | -0.029346 | 0.046088 | -0.11444 | 0.26093 | -0.55389 | 0.018311 | -0.32501 | -0.054932 | 0.018311 | 0.21057 | 0.3479 | -123.2346 | 122.2046 | 0.11444 | 122.644 | 122.7768 | -0.4715 | -0.47607 | 0.20142 | 0.43945 | 122.7768 | 122.9691 | 122.4335 | 123.0194 | 122.644 | 123.1064 | 122.7036 | -0.47607 | 123.0194 | 122.644 | 122.7036 | 122.4335 | 123.1064 | -0.70038 | -123.381
2238.9219 | 122.9507 | -122.8134 | 0.16479 | 0.348 | 0.037289 | -0.040324 | 0.10489 | -0.065371 | -0.026142 | 0.059974 | -0.17853 | 0.28839 | -0.58594 | 0.14191 | -0.24261 | 0.050354 | -0.086975 | 0.31586 | 0.33417 | -123.2025 | 122.2275 | 0.1236 | 122.6349 | 122.9553 | -0.40741 | -0.3891 | 0.16937 | 0.40741 | 122.7264 | 123.1293 | 122.5708 | 123.1018 | 122.6349 | 123.1476 | 122.8638 | -0.3891 | 123.1018 | 122.6349 | 122.8638 | 122.5708 | 123.1476 | -0.75073 | -123.3673
2239.9219 | 123.0469 | -122.7402 | 0.15106 | 0.51585 | 0.03088 | -0.032847 | 0.10489 | -0.060031 | -0.028278 | 0.065314 | -0.07782 | 0.24261 | -0.52185 | -0.022888 | -0.37994 | -0.068665 | 0.041199 | 0.17853 | 0.36621 | -123.2071 | 122.2183 | 0.091553 | 122.6624 | 122.7173 | -0.53101 | -0.46692 | 0.21515 | 0.44403 | 122.7814 | 122.9187 | 122.3602 | 122.9828 | 122.6624 | 123.1064 | 122.6715 | -0.46692 | 122.9828 | 122.6624 | 122.6715 | 122.3602 | 123.1064 | -0.67291 | -123.3582
2240.9219 | 123.0103 | -122.7585 | 0.16022 | 0.14964 | 0.027676 | -0.0478 | 0.091001 | -0.070712 | -0.048572 | 0.070655 | -0.12817 | 0.26093 | -0.48523 | -0.018311 | -0.3479 | -0.009155 | -0.022888 | 0.21057 | 0.35706 | -123.2071 | 122.2733 | 0.10071 | 122.6303 | 122.7402 | -0.50812 | -0.44861 | 0.19684 | 0.35706 | 122.7356 | 122.9691 | 122.4106 | 123.0194 | 122.6303 | 123.1155 | 122.7493 | -0.44861 | 123.0194 | 122.6303 | 122.7493 | 122.4106 | 123.1155 | -0.64545 | -123.3673
2241.9219 | 123.0698 | -122.7539 | 0.15106 | 0.36326 | 0.04797 | -0.0082804 | 0.10702 | -0.07178 | -0.028278 | 0.048225 | -0.036621 | 0.24719 | -0.49439 | -0.004578 | -0.33875 | -0.064087 | 0.050354 | 0.19226 | 0.34332 | -123.2437 | 122.2595 | 0.09613 | 122.7173 | 122.7493 | -0.48981 | -0.48981 | 0.19226 | 0.45776 | 122.8043 | 122.9462 | 122.4152 | 123.0011 | 122.7173 | 123.0972 | 122.6898 | -0.48981 | 123.0011 | 122.7173 | 122.6898 | 122.4152 | 123.0972 | -0.64545 | -123.3948
2242.9844 | 122.9874 | -122.7905 | 0.16937 | -0.14028 | 0.038357 | -0.023234 | 0.12839 | -0.063235 | -0.013325 | 0.052497 | -0.082397 | 0.28839 | -0.51727 | 0.13275 | -0.3067 | 0.032043 | -0.082397 | 0.28839 | 0.32959 | -123.2346 | 122.2733 | 0.11902 | 122.7081 | 122.9233 | -0.47607 | -0.44403 | 0.16022 | 0.43488 | 122.7081 | 123.0789 | 122.4838 | 123.0789 | 122.7081 | 123.1201 | 122.8226 | -0.44403 | 123.0789 | 122.7081 | 122.8226 | 122.4838 | 123.1201 | -0.68665 | -123.4039
2243.9219 | 123.0423 | -122.7905 | 0.14648 | 0.45481 | 0.036221 | -0.018961 | 0.11023 | -0.063235 | -0.020801 | 0.065314 | -0.16022 | 0.25635 | -0.56305 | 0.022888 | -0.32501 | -0.022888 | 0.022888 | 0.2243 | 0.34332 | -123.2391 | 122.2275 | 0.10986 | 122.6303 | 122.8134 | -0.4715 | -0.44861 | 0.19684 | 0.40283 | 122.8134 | 123.0148 | 122.4655 | 123.0469 | 122.6303 | 123.1338 | 122.7676 | -0.44861 | 123.0469 | 122.6303 | 122.7676 | 122.4655 | 123.1338 | -0.70953 | -123.3856
2244.9844 | 123.0057 | -122.8271 | 0.16022 | -0.23183 | 0.036221 | -0.033915 | 0.11984 | -0.065371 | -0.016529 | 0.06211 | -0.14191 | 0.28381 | -0.54932 | 0.10986 | -0.2655 | 0.050354 | -0.10071 | 0.30212 | 0.32501 | -123.2208 | 122.2778 | 0.1236 | 122.6852 | 122.937 | -0.42572 | -0.39368 | 0.1648 | 0.40741 | 122.7264 | 123.1293 | 122.5616 | 123.111 | 122.6852 | 123.1522 | 122.8775 | -0.39368 | 123.111 | 122.6852 | 122.8775 | 122.5616 | 123.1522 | -0.70953 | -123.381
2245.9219 | 122.9782 | -122.8455 | 0.17853 | -0.3539 | 0.034085 | -0.032847 | 0.094205 | -0.055758 | -0.034687 | 0.067451 | -0.16937 | 0.27466 | -0.54016 | 0.07782 | -0.27924 | 0.068665 | -0.12817 | 0.31128 | 0.32959 | -123.23 | 122.3053 | 0.09613 | 122.6761 | 122.9233 | -0.45776 | -0.38452 | 0.15106 | 0.37079 | 122.7173 | 123.1567 | 122.5662 | 123.1201 | 122.6761 | 123.175 | 122.9141 | -0.38452 | 123.1201 | 122.6761 | 122.9141 | 122.5662 | 123.175 | -0.71869 | -123.4085
2246.9844 | 123.0103 | -122.85 | 0.17395 | -0.063984 | 0.043698 | -0.016825 | 0.12091 | -0.062167 | -0.02721 | 0.06211 | -0.12817 | 0.28839 | -0.58594 | 0.1236 | -0.24719 | 0.027466 | -0.07782 | 0.29755 | 0.32501 | -123.2346 | 122.2641 | 0.11444 | 122.7219 | 122.9736 | -0.42114 | -0.38452 | 0.15106 | 0.45776 | 122.7722 | 123.1476 | 122.6028 | 123.1384 | 122.7219 | 123.175 | 122.8775 | -0.38452 | 123.1384 | 122.7219 | 122.8775 | 122.6028 | 123.175 | -0.75989 | -123.4085
2247.9219 | 123.0652 | -122.7951 | 0.13733 | 0.45481 | 0.036221 | -0.029642 | 0.10809 | -0.062167 | -0.013325 | 0.063178 | -0.1831 | 0.24719 | -0.60425 | 0.032043 | -0.31128 | -0.050354 | 0.022888 | 0.2243 | 0.35248 | -123.2483 | 122.1909 | 0.10986 | 122.612 | 122.8271 | -0.44861 | -0.45319 | 0.21515 | 0.42114 | 122.818 | 123.0194 | 122.4838 | 123.0423 | 122.612 | 123.1476 | 122.7448 | -0.45319 | 123.0423 | 122.612 | 122.7448 | 122.4838 | 123.1476 | -0.74158 | -123.3856
2248.9219 | 123.0377 | -122.7905 | 0.14648 | 0.48533 | 0.041562 | -0.04246 | 0.11664 | -0.074984 | -0.015461 | 0.058906 | -0.18768 | 0.28381 | -0.59052 | 0.032043 | -0.39825 | -0.032043 | -0.004578 | 0.2243 | 0.34332 | -123.2574 | 122.2 | 0.13733 | 122.6028 | 122.8226 | -0.54474 | -0.46692 | 0.19684 | 0.40283 | 122.7859 | 123.0148 | 122.3923 | 123.0743 | 122.6028 | 123.1338 | 122.7585 | -0.46692 | 123.0743 | 122.6028 | 122.7585 | 122.3923 | 123.1338 | -0.737 | -123.4039
2249.9844 | 122.9736 | -122.8729 | 0.16937 | -0.3539 | 0.028744 | -0.036051 | 0.10168 | -0.067507 | -0.031483 | 0.065314 | -0.2243 | 0.28381 | -0.59967 | 0.09613 | -0.33875 | 0.073242 | -0.11444 | 0.32044 | 0.32044 | -123.1979 | 122.2733 | 0.11444 | 122.6486 | 122.9691 | -0.50812 | -0.32501 | 0.15106 | 0.37537 | 122.7585 | 123.1934 | 122.5342 | 123.1567 | 122.6486 | 123.1934 | 122.9462 | -0.32501 | 123.1567 | 122.6486 | 122.9462 | 122.5342 | 123.1934 | -0.76904 | -123.3673
2250.9219 | 123.056 | -122.818 | 0.15564 | 0.30223 | 0.031949 | -0.027506 | 0.10489 | -0.069644 | -0.047504 | 0.052497 | -0.22888 | 0.23804 | -0.62256 | -0.013733 | -0.49896 | -0.036621 | 0.004578 | 0.21973 | 0.32501 | -123.2529 | 122.1954 | 0.082397 | 122.5891 | 122.8043 | -0.6546 | -0.43488 | 0.16937 | 0.39368 | 122.8226 | 123.0377 | 122.319 | 123.056 | 122.5891 | 123.143 | 122.7814 | -0.43488 | 123.056 | 122.5891 | 122.7814 | 122.319 | 123.143 | -0.7782 | -123.4085
2251.9844 | 122.9874 | -122.8638 | 0.18768 | -0.33864 | 0.031949 | -0.031779 | 0.1177 | -0.063235 | -0.029346 | 0.064246 | -0.19226 | 0.32044 | -0.60425 | 0.11444 | -0.4303 | 0.064087 | -0.12817 | 0.32959 | 0.31128 | -123.2437 | 122.2595 | 0.13275 | 122.6715 | 122.9782 | -0.61798 | -0.37994 | 0.1236 | 0.41199 | 122.7356 | 123.1934 | 122.4335 | 123.1842 | 122.6715 | 123.175 | 122.9279 | -0.37994 | 123.1842 | 122.6715 | 122.9279 | 122.4335 | 123.175 | -0.79193 | -123.4314
2252.9219 | 122.9874 | -122.85 | 0.16937 | 0.36326 | 0.049038 | -0.0029404 | 0.12518 | -0.063235 | -0.01012 | 0.055701 | -0.24261 | 0.3067 | -0.63629 | 0.16022 | -0.41657 | 0.073242 | -0.11902 | 0.33417 | 0.3067 | -123.2529 | 122.2137 | 0.13733 | 122.6074 | 123.0103 | -0.58594 | -0.40283 | 0.13733 | 0.39368 | 122.731 | 123.1842 | 122.4335 | 123.1567 | 122.6074 | 123.1567 | 122.9233 | -0.40283 | 123.1567 | 122.6074 | 122.9233 | 122.4335 | 123.1567 | -0.80566 | -123.4222
2253.9844 | 123.0103 | -122.85 | 0.15564 | -0.1708 | 0.045834 | -0.028574 | 0.12198 | -0.065371 | -0.018665 | 0.051429 | -0.15106 | 0.28839 | -0.59967 | 0.10071 | -0.3891 | 0.036621 | -0.086975 | 0.28381 | 0.32044 | -123.2574 | 122.2504 | 0.13275 | 122.699 | 122.9507 | -0.54474 | -0.40741 | 0.1648 | 0.44861 | 122.7631 | 123.1338 | 122.4609 | 123.1384 | 122.699 | 123.1705 | 122.8867 | -0.40741 | 123.1384 | 122.699 | 122.8867 | 122.4609 | 123.1705 | -0.75531 | -123.4131
2254.9219 | 123.0377 | -122.8271 | 0.15564 | 0.40904 | 0.046902 | -0.028574 | 0.11236 | -0.05469 | -0.012257 | 0.064246 | -0.27924 | 0.29297 | -0.66834 | 0.091553 | -0.48981 | 0.032043 | -0.054932 | 0.27924 | 0.31586 | -123.2437 | 122.1588 | 0.13733 | 122.5479 | 122.9187 | -0.64545 | -0.41657 | 0.16022 | 0.3891 | 122.7722 | 123.1064 | 122.3373 | 123.1201 | 122.5479 | 123.143 | 122.8592 | -0.41657 | 123.1201 | 122.5479 | 122.8592 | 122.3373 | 123.143 | -0.82398 | -123.3994
2255.9844 | 122.9874 | -122.8683 | 0.16479 | 0.33274 | 0.056515 | -0.027506 | 0.11877 | -0.064303 | -0.025074 | 0.068519 | -0.27008 | 0.31128 | -0.67291 | 0.14648 | -0.36163 | 0.086975 | -0.11444 | 0.32501 | 0.31128 | -123.2483 | 122.1954 | 0.14648 | 122.5983 | 123.0148 | -0.52643 | -0.37994 | 0.14648 | 0.40283 | 122.7539 | 123.1934 | 122.5067 | 123.1796 | 122.5983 | 123.1796 | 122.9553 | -0.37994 | 123.1796 | 122.5983 | 122.9553 | 122.5067 | 123.1796 | -0.83771 | -123.4131
2256.9219 | 123.0148 | -122.8775 | 0.17853 | 0.43956 | 0.029812 | -0.029642 | 0.11557 | -0.057894 | -0.02721 | 0.058906 | -0.30212 | 0.28839 | -0.68207 | 0.12817 | -0.42114 | 0.045776 | -0.086975 | 0.32959 | 0.32501 | -123.2758 | 122.1954 | 0.10986 | 122.5754 | 123.0057 | -0.59967 | -0.39825 | 0.14648 | 0.37994 | 122.7905 | 123.2071 | 122.4564 | 123.1659 | 122.5754 | 123.2025 | 122.9233 | -0.39825 | 123.1659 | 122.5754 | 122.9233 | 122.4564 | 123.2025 | -0.8606 | -123.4543
2257.9844 | 123.024 | -122.8729 | 0.18768 | -0.33864 | 0.03088 | -0.022166 | 0.11664 | -0.057894 | -0.014393 | 0.058906 | -0.25177 | 0.29297 | -0.64545 | 0.10986 | -0.32959 | 0.073242 | -0.11902 | 0.32044 | 0.3479 | -123.262 | 122.2275 | 0.10529 | 122.6212 | 122.9828 | -0.51727 | -0.3891 | 0.16022 | 0.39368 | 122.7539 | 123.1934 | 122.5433 | 123.1659 | 122.6212 | 123.2208 | 122.9462 | -0.3891 | 123.1659 | 122.6212 | 122.9462 | 122.5433 | 123.2208 | -0.83313 | -123.4497
2258.9219 | 122.9919 | -122.8683 | 0.17395 | 0.22593 | 0.039425 | -0.010416 | 0.12625 | -0.057894 | -0.012257 | 0.064246 | -0.26093 | 0.3067 | -0.67749 | 0.15564 | -0.40283 | 0.07782 | -0.11902 | 0.34332 | 0.31586 | -123.2849 | 122.1909 | 0.13275 | 122.6074 | 123.024 | -0.57678 | -0.41657 | 0.14191 | 0.41657 | 122.7493 | 123.2117 | 122.4655 | 123.175 | 122.6074 | 123.1842 | 122.9462 | -0.41657 | 123.175 | 122.6074 | 122.9462 | 122.4655 | 123.1842 | -0.85144 | -123.4589
2259.9844 | 123.0423 | -122.8775 | 0.17853 | -0.32338 | 0.036221 | -0.031779 | 0.1145 | -0.055758 | -0.025074 | 0.053565 | -0.23346 | 0.30212 | -0.63629 | 0.10529 | -0.44861 | 0.064087 | -0.10071 | 0.31586 | 0.33417 | -123.2758 | 122.2412 | 0.1236 | 122.644 | 122.9828 | -0.62714 | -0.39825 | 0.15564 | 0.40283 | 122.7768 | 123.1934 | 122.4289 | 123.1796 | 122.644 | 123.2117 | 122.9416 | -0.39825 | 123.1796 | 122.644 | 122.9416 | 122.4289 | 123.2117 | -0.81482 | -123.4543
2260.9219 | 123.0103 | -122.8958 | 0.16937 | 0.31749 | 0.037289 | -0.028574 | 0.12198 | -0.061099 | -0.016529 | 0.06211 | -0.27466 | 0.30212 | -0.67291 | 0.13733 | -0.40741 | 0.086975 | -0.11902 | 0.34332 | 0.32501 | -123.2849 | 122.2229 | 0.13275 | 122.6212 | 123.0331 | -0.57678 | -0.3891 | 0.15564 | 0.39825 | 122.7768 | 123.2391 | 122.4884 | 123.1979 | 122.6212 | 123.2208 | 122.9828 | -0.3891 | 123.1979 | 122.6212 | 122.9828 | 122.4884 | 123.2208 | -0.84229 | -123.4543
2261.9844 | 123.0377 | -122.9004 | 0.17395 | -0.3539 | 0.04263 | -0.028574 | 0.11557 | -0.062167 | -0.017597 | 0.064246 | -0.20142 | 0.3067 | -0.63171 | 0.09613 | -0.43488 | 0.036621 | -0.082397 | 0.29755 | 0.3479 | -123.2895 | 122.2687 | 0.13275 | 122.699 | 122.9965 | -0.60882 | -0.3891 | 0.17395 | 0.4303 | 122.818 | 123.1979 | 122.4655 | 123.2071 | 122.699 | 123.2483 | 122.937 | -0.3891 | 123.2071 | 122.699 | 122.937 | 122.4655 | 123.2483 | -0.80566 | -123.4634
2262.9219 | 123.0011 | -122.9004 | 0.16022 | 0.10386 | 0.04263 | -0.0061444 | 0.11877 | -0.067507 | -0.0047804 | 0.065314 | -0.24719 | 0.29755 | -0.62714 | 0.16937 | -0.40741 | 0.09613 | -0.1236 | 0.36621 | 0.3067 | -123.3032 | 122.2733 | 0.13733 | 122.6532 | 123.0698 | -0.56763 | -0.40283 | 0.14648 | 0.37994 | 122.7768 | 123.2666 | 122.493 | 123.1979 | 122.6532 | 123.2071 | 122.9965 | -0.40283 | 123.1979 | 122.6532 | 122.9965 | 122.493 | 123.2071 | -0.78735 | -123.4634
2263.9844 | 123.0286 | -122.8775 | 0.15564 | -0.29287 | 0.046902 | -0.011485 | 0.10489 | -0.056826 | -0.0079844 | 0.063178 | -0.21057 | 0.29297 | -0.61798 | 0.09613 | -0.42572 | 0.041199 | -0.073242 | 0.31128 | 0.33417 | -123.2941 | 122.2595 | 0.13733 | 122.6669 | 122.9736 | -0.58136 | -0.41656 | 0.17853 | 0.40741 | 122.8043 | 123.1888 | 122.4518 | 123.1705 | 122.6669 | 123.2117 | 122.9187 | -0.41656 | 123.1705 | 122.6669 | 122.9187 | 122.4518 | 123.2117 | -0.77362 | -123.4497
2264.9219 | 123.0148 | -122.905 | 0.16479 | 0.073345 | 0.045834 | -0.031779 | 0.11343 | -0.066439 | -0.011188 | 0.053565 | -0.21057 | 0.29755 | -0.62256 | 0.14648 | -0.36163 | 0.073242 | -0.09613 | 0.32959 | 0.34332 | -123.2803 | 122.2824 | 0.13275 | 122.6944 | 123.0515 | -0.52643 | -0.37537 | 0.17853 | 0.41199 | 122.8088 | 123.2346 | 122.5433 | 123.2025 | 122.6944 | 123.2483 | 122.9782 | -0.37537 | 123.2025 | 122.6944 | 122.9782 | 122.5433 | 123.2483 | -0.78735 | -123.4451
2265.9844 | 123.0331 | -122.8775 | 0.16479 | -0.36916 | 0.029812 | -0.031779 | 0.1113 | -0.049349 | -0.030414 | 0.057838 | -0.21973 | 0.3067 | -0.6134 | 0.10071 | -0.40741 | 0.068665 | -0.10986 | 0.33417 | 0.32959 | -123.2712 | 122.2641 | 0.14191 | 122.6578 | 122.9782 | -0.5722 | -0.39368 | 0.16479 | 0.39368 | 122.7676 | 123.2117 | 122.4701 | 123.1842 | 122.6578 | 123.2071 | 122.9462 | -0.39368 | 123.1842 | 122.6578 | 122.9462 | 122.4701 | 123.2071 | -0.7782 | -123.436
2266.9219 | 123.0286 | -122.8912 | 0.18768 | 0.042827 | 0.045834 | -0.018961 | 0.11557 | -0.055758 | -0.012257 | 0.064246 | -0.16937 | 0.29755 | -0.58136 | 0.13733 | -0.32501 | 0.064087 | -0.11444 | 0.32959 | 0.32044 | -123.2895 | 122.3099 | 0.10986 | 122.7219 | 123.0286 | -0.5127 | -0.39826 | 0.13275 | 0.41199 | 122.7768 | 123.2208 | 122.5662 | 123.1888 | 122.7219 | 123.2117 | 122.9553 | -0.39826 | 123.1888 | 122.7219 | 122.9553 | 122.5662 | 123.2117 | -0.76904 | -123.4772
2267.9844 | 123.1522 | -122.8729 | 0.16022 | -0.29287 | 0.013791 | -0.02537 | 0.096342 | -0.067507 | -0.0443 | 0.066383 | -0.16479 | 0.25177 | -0.55389 | -0.09613 | -0.55389 | -0.14191 | 0.022888 | 0.1831 | 0.35706 | -123.3078 | 122.319 | 0.091553 | 122.7081 | 122.7768 | -0.71411 | -0.43488 | 0.19684 | 0.3891 | 122.8958 | 123.056 | 122.319 | 123.1247 | 122.7081 | 123.23 | 122.731 | -0.43488 | 123.1247 | 122.7081 | 122.731 | 122.319 | 123.23 | -0.71411 | -123.468
2268.9219 | 123.0194 | -122.905 | 0.17395 | 0.14964 | 0.037289 | -0.023234 | 0.13052 | -0.064303 | -0.012257 | 0.06211 | 0.018311 | 0.28839 | -0.40283 | 0.16022 | -0.40741 | -0.032043 | -0.1236 | 0.34332 | 0.32044 | -123.3215 | 122.5021 | 0.11444 | 122.9233 | 123.0652 | -0.58136 | -0.41657 | 0.14649 | 0.42114 | 122.7814 | 123.2483 | 122.4976 | 123.1934 | 122.9233 | 123.2254 | 122.8729 | -0.41657 | 123.1934 | 122.9233 | 122.8729 | 122.4976 | 123.2254 | -0.57678 | -123.4955
2269.9844 | 123.024 | -122.9324 | 0.19226 | 0.30223 | 0.031949 | -0.045664 | 0.10382 | -0.060031 | -0.018665 | 0.057838 | -0.032043 | 0.2655 | -0.42114 | 0.091553 | -0.36163 | -0.013733 | -0.13275 | 0.34332 | 0.32959 | -123.3032 | 122.5113 | 0.073242 | 122.9004 | 123.024 | -0.55389 | -0.37079 | 0.13733 | 0.3891 | 122.7997 | 123.2758 | 122.5708 | 123.1979 | 122.9004 | 123.262 | 122.9187 | -0.37079 | 123.1979 | 122.9004 | 122.9187 | 122.5708 | 123.262 | -0.6134 | -123.4955
2270.9219 | 123.056 | -122.9004 | 0.15564 | -0.0029495 | 0.044766 | -0.031779 | 0.12091 | -0.058962 | -0.016529 | 0.063178 | 0.064087 | 0.28381 | -0.38452 | 0.1236 | -0.38452 | 0.018311 | -0.07782 | 0.29755 | 0.33417 | -123.3353 | 122.5159 | 0.12817 | 122.9645 | 123.024 | -0.54016 | -0.43488 | 0.17853 | 0.44861 | 122.8226 | 123.1979 | 122.5159 | 123.1842 | 122.9645 | 123.2346 | 122.9187 | -0.43488 | 123.1842 | 122.9645 | 122.9187 | 122.5159 | 123.2346 | -0.54016 | -123.4909
2271.9844 | 123.1613 | -122.8683 | 0.15564 | -0.21657 | 0.020199 | -0.028574 | 0.091001 | -0.073916 | -0.045368 | 0.067451 | 0.054932 | 0.24719 | -0.39368 | -0.086975 | -0.52643 | -0.1236 | 0.009155 | 0.17395 | 0.37994 | -123.3307 | 122.4747 | 0.091552 | 122.9233 | 122.7814 | -0.68207 | -0.46234 | 0.2243 | 0.44861 | 122.8775 | 123.0423 | 122.3419 | 123.1155 | 122.9233 | 123.2483 | 122.7448 | -0.46234 | 123.1155 | 122.9233 | 122.7448 | 122.3419 | 123.2483 | -0.54932 | -123.4863
2272.9219 | 123.0835 | -122.9187 | 0.16937 | -0.033467 | 0.043698 | -0.016825 | 0.11984 | -0.062167 | -0.014393 | 0.071723 | 0.045776 | 0.28381 | -0.39825 | 0.10986 | -0.46234 | 0.013733 | -0.073242 | 0.27924 | 0.32501 | -123.2986 | 122.5204 | 0.11444 | 122.9645 | 123.0286 | -0.63171 | -0.37994 | 0.15564 | 0.44403 | 122.8455 | 123.1979 | 122.4564 | 123.2025 | 122.9645 | 123.2437 | 122.9324 | -0.37994 | 123.2025 | 122.9645 | 122.9324 | 122.4564 | 123.2437 | -0.56763 | -123.468
2273.9844 | 123.1522 | -122.8683 | 0.16937 | -0.21657 | 0.021267 | -0.020029 | 0.089933 | -0.07712 | -0.042164 | 0.054633 | 0.041199 | 0.23804 | -0.37079 | -0.068665 | -0.55389 | -0.068665 | 0.027466 | 0.18768 | 0.37079 | -123.317 | 122.4976 | 0.068664 | 122.9095 | 122.7997 | -0.72327 | -0.44861 | 0.20142 | 0.41199 | 122.8958 | 123.056 | 122.3145 | 123.1064 | 122.9095 | 123.2391 | 122.7997 | -0.44861 | 123.1064 | 122.9095 | 122.7997 | 122.3145 | 123.2391 | -0.54016 | -123.4863
2274.9219 | 123.056 | -122.9324 | 0.17395 | 0.058086 | 0.03088 | -0.037119 | 0.11984 | -0.069644 | -0.025074 | 0.05677 | 0.032043 | 0.29297 | -0.39825 | 0.15106 | -0.4303 | 0.027466 | -0.091553 | 0.31128 | 0.3479 | -123.3215 | 122.5342 | 0.11902 | 122.9645 | 123.0835 | -0.60425 | -0.3891 | 0.17395 | 0.4303 | 122.8409 | 123.2437 | 122.5021 | 123.2254 | 122.9645 | 123.2803 | 122.9599 | -0.3891 | 123.2254 | 122.9645 | 122.9599 | 122.5021 | 123.2803 | -0.5722 | -123.4955
2275.9844 | 123.0652 | -122.9187 | 0.16022 | -0.29287 | 0.035153 | -0.026438 | 0.1113 | -0.058962 | -0.025074 | 0.059974 | 0.004578 | 0.29755 | -0.40741 | 0.10071 | -0.37079 | 0.032043 | -0.10071 | 0.29297 | 0.32044 | -123.3261 | 122.5113 | 0.13733 | 122.9233 | 123.0194 | -0.53101 | -0.40741 | 0.16022 | 0.41199 | 122.818 | 123.2117 | 122.5479 | 123.2162 | 122.9233 | 123.2391 | 122.9507 | -0.40741 | 123.2162 | 122.9233 | 122.9507 | 122.5479 | 123.2391 | -0.56763 | -123.4863
2276.9219 | 123.0698 | -122.937 | 0.16479 | -0.38442 | 0.028744 | -0.053141 | 0.098478 | -0.063235 | -0.026142 | 0.050361 | -0.027466 | 0.30212 | -0.42572 | 0.11444 | -0.44861 | 0.036621 | -0.11444 | 0.31586 | 0.32959 | -123.3215 | 122.5113 | 0.13733 | 122.9095 | 123.0515 | -0.6134 | -0.38452 | 0.16479 | 0.39825 | 122.8226 | 123.2529 | 122.4884 | 123.2391 | 122.9095 | 123.2666 | 122.9736 | -0.38452 | 123.2391 | 122.9095 | 122.9736 | 122.4884 | 123.2666 | -0.59052 | -123.4863
2277.9844 | 123.1705 | -122.8912 | 0.13733 | -0.32338 | 0.012723 | -0.030711 | 0.073911 | -0.064303 | -0.049641 | 0.061042 | 0.041199 | 0.24261 | -0.37994 | -0.059509 | -0.52643 | -0.07782 | 0.022888 | 0.17853 | 0.37537 | -123.3398 | 122.5113 | 0.10529 | 122.9324 | 122.8317 | -0.66376 | -0.44861 | 0.23804 | 0.42114 | 122.9141 | 123.0698 | 122.3648 | 123.1338 | 122.9324 | 123.2666 | 122.8134 | -0.44861 | 123.1338 | 122.9324 | 122.8134 | 122.3648 | 123.2666 | -0.51727 | -123.4772
2278.9219 | 123.1018 | -122.9324 | 0.18768 | -0.33864 | 0.039425 | -0.011485 | 0.11664 | -0.066439 | -0.026142 | 0.058906 | 0.009155 | 0.3067 | -0.41657 | 0.11902 | -0.46234 | 0.036621 | -0.10529 | 0.3067 | 0.3067 | -123.3307 | 122.5159 | 0.11902 | 122.9416 | 123.0515 | -0.65002 | -0.39825 | 0.11902 | 0.42572 | 122.8271 | 123.2391 | 122.4701 | 123.2391 | 122.9416 | 123.2391 | 122.9691 | -0.39825 | 123.2391 | 122.9416 | 122.9691 | 122.4701 | 123.2391 | -0.60425 | -123.5184
2279.9688 | 123.1796 | -122.9004 | 0.14191 | -0.094502 | 0.014859 | -0.02537 | 0.085661 | -0.079257 | -0.045368 | 0.051429 | 0 | 0.26093 | -0.36163 | -0.068665 | -0.59052 | -0.082397 | 0.036621 | 0.17853 | 0.36163 | -123.317 | 122.5388 | 0.11902 | 122.9004 | 122.8317 | -0.73242 | -0.41657 | 0.21973 | 0.36163 | 122.937 | 123.0789 | 122.3099 | 123.1613 | 122.9004 | 123.262 | 122.818 | -0.41657 | 123.1613 | 122.9004 | 122.818 | 122.3099 | 123.262 | -0.50354 | -123.4589
2280.9219 | 123.0652 | -122.937 | 0.17853 | -0.36916 | 0.039425 | -0.033915 | 0.12091 | -0.057894 | -0.025074 | 0.065314 | -0.013733 | 0.3067 | -0.42572 | 0.13275 | -0.49439 | 0.050354 | -0.1236 | 0.32959 | 0.33417 | -123.3307 | 122.5113 | 0.12817 | 122.9233 | 123.0698 | -0.67291 | -0.39368 | 0.15564 | 0.41199 | 122.8134 | 123.2666 | 122.4426 | 123.2437 | 122.9233 | 123.2712 | 122.9874 | -0.39368 | 123.2437 | 122.9233 | 122.9874 | 122.4426 | 123.2712 | -0.60425 | -123.5092
2281.9844 | 123.1522 | -122.905 | 0.14191 | -0.3539 | 0.015927 | -0.029642 | 0.089933 | -0.068576 | -0.033619 | 0.059974 | 0.041199 | 0.23804 | -0.3891 | -0.032043 | -0.60425 | -0.068665 | 0.018311 | 0.20599 | 0.36163 | -123.3261 | 122.5159 | 0.09613 | 122.9462 | 122.8729 | -0.74616 | -0.42114 | 0.21973 | 0.4303 | 122.9233 | 123.111 | 122.3007 | 123.143 | 122.9462 | 123.2666 | 122.8363 | -0.42114 | 123.143 | 122.9462 | 122.8363 | 122.3007 | 123.2666 | -0.53101 | -123.468
2282.9219 | 123.0972 | -122.9095 | 0.17395 | -0.079243 | 0.02554 | -0.038187 | 0.12625 | -0.069644 | -0.0079844 | 0.053565 | 0.045776 | 0.30212 | -0.39825 | 0.11444 | -0.49439 | 0.013733 | -0.068665 | 0.28381 | 0.34332 | -123.3353 | 122.5113 | 0.12817 | 122.9553 | 123.024 | -0.66834 | -0.42572 | 0.16937 | 0.44403 | 122.8409 | 123.1934 | 122.4152 | 123.2117 | 122.9553 | 123.2529 | 122.9233 | -0.42572 | 123.2117 | 122.9553 | 122.9233 | 122.4152 | 123.2529 | -0.5722 | -123.5092
2283.9844 | 123.1888 | -122.8867 | 0.13733 | -0.26235 | 0.021267 | -0.055277 | 0.088865 | -0.07712 | -0.042164 | 0.06211 | 0.022888 | 0.24261 | -0.36163 | -0.064087 | -0.64087 | -0.073242 | 0.050354 | 0.17853 | 0.37537 | -123.3261 | 122.525 | 0.10529 | 122.9095 | 122.8226 | -0.7782 | -0.43945 | 0.23804 | 0.38452 | 122.937 | 123.0652 | 122.2458 | 123.1293 | 122.9095 | 123.262 | 122.8134 | -0.43945 | 123.1293 | 122.9095 | 122.8134 | 122.2458 | 123.262 | -0.49896 | -123.4634
2284.9219 | 123.1018 | -122.9507 | 0.16937 | -0.29287 | 0.045834 | -0.015757 | 0.11023 | -0.07178 | -0.02721 | 0.063178 | 0.022888 | 0.29755 | -0.39368 | 0.12817 | -0.48523 | 0.032043 | -0.10529 | 0.31128 | 0.32959 | -123.3627 | 122.5571 | 0.12817 | 122.9736 | 123.0789 | -0.6546 | -0.41199 | 0.16022 | 0.41657 | 122.8455 | 123.262 | 122.4655 | 123.2483 | 122.9736 | 123.2803 | 122.9828 | -0.41199 | 123.2483 | 122.9736 | 122.9828 | 122.4655 | 123.2803 | -0.56305 | -123.5321
2285.9844 | 123.1796 | -122.9004 | 0.13733 | -0.20131 | 0.019131 | -0.05955 | 0.086729 | -0.069644 | -0.0443 | 0.053565 | -0.009155 | 0.25635 | -0.37994 | -0.050354 | -0.60425 | -0.050354 | 0 | 0.19226 | 0.36163 | -123.3124 | 122.5204 | 0.11902 | 122.8912 | 122.85 | -0.74158 | -0.41199 | 0.2243 | 0.37079 | 122.9004 | 123.0927 | 122.2961 | 123.1567 | 122.8912 | 123.262 | 122.85 | -0.41199 | 123.1567 | 122.8912 | 122.85 | 122.2961 | 123.262 | -0.51727 | -123.4497
2286.9219 | 123.0972 | -122.9416 | 0.1831 | -0.47597 | 0.036221 | -0.037119 | 0.10916 | -0.063235 | -0.041096 | 0.059974 | -0.004578 | 0.2655 | -0.40741 | 0.086975 | -0.51727 | 0.036621 | -0.09613 | 0.27466 | 0.34332 | -123.3261 | 122.5342 | 0.082398 | 122.937 | 123.0286 | -0.70038 | -0.38452 | 0.16022 | 0.40283 | 122.8455 | 123.2162 | 122.4243 | 123.2071 | 122.937 | 123.2849 | 122.9782 | -0.38452 | 123.2071 | 122.937 | 122.9782 | 122.4243 | 123.2849 | -0.59052 | -123.5092
2287.9844 | 123.1247 | -122.9187 | 0.14191 | 0.25645 | 0.021267 | -0.053141 | 0.09741 | -0.080325 | -0.045368 | 0.05677 | -0.009155 | 0.24719 | -0.37994 | 0.009155 | -0.57678 | -0.036621 | -0.022888 | 0.23346 | 0.34332 | -123.3536 | 122.5388 | 0.10528 | 122.9095 | 122.9279 | -0.71869 | -0.43488 | 0.20142 | 0.37079 | 122.8958 | 123.1522 | 122.3419 | 123.1659 | 122.9095 | 123.262 | 122.8821 | -0.43488 | 123.1659 | 122.9095 | 122.8821 | 122.3419 | 123.262 | -0.52185 | -123.4955
2288.9219 | 123.0652 | -122.9324 | 0.1831 | -0.41494 | 0.04263 | -0.034983 | 0.12625 | -0.070712 | -0.016529 | 0.053565 | -0.050354 | 0.29755 | -0.44403 | 0.13733 | -0.52185 | 0.068665 | -0.1236 | 0.32959 | 0.32501 | -123.3261 | 122.4884 | 0.11444 | 122.8821 | 123.0698 | -0.70496 | -0.39368 | 0.14191 | 0.39368 | 122.8088 | 123.262 | 122.4106 | 123.23 | 122.8821 | 123.2574 | 123.0011 | -0.39368 | 123.23 | 122.8821 | 123.0011 | 122.4106 | 123.2574 | -0.62714 | -123.5092
2289.9844 | 123.1338 | -122.9279 | 0.15106 | 0.37852 | 0.014859 | -0.02537 | 0.096342 | -0.084597 | -0.033619 | 0.065314 | 0.009155 | 0.23804 | -0.37079 | -0.009155 | -0.59967 | -0.022888 | -0.018311 | 0.2243 | 0.35248 | -123.3124 | 122.5571 | 0.086975 | 122.937 | 122.9187 | -0.75073 | -0.38452 | 0.20142 | 0.37994 | 122.9095 | 123.1522 | 122.3282 | 123.1659 | 122.937 | 123.2803 | 122.905 | -0.38452 | 123.1659 | 122.937 | 122.905 | 122.3282 | 123.2803 | -0.52185 | -123.4634
2290.9219 | 123.0789 | -122.9736 | 0.1831 | -0.55227 | 0.015927 | -0.039256 | 0.12198 | -0.066439 | -0.030414 | 0.05677 | -0.059509 | 0.28839 | -0.42114 | 0.1236 | -0.59052 | 0.068665 | -0.15106 | 0.32959 | 0.32044 | -123.3261 | 122.5525 | 0.10529 | 122.9141 | 123.0972 | -0.77362 | -0.35248 | 0.13733 | 0.36163 | 122.8226 | 123.3032 | 122.3831 | 123.262 | 122.9141 | 123.2941 | 123.0423 | -0.35248 | 123.262 | 122.9141 | 123.0423 | 122.3831 | 123.2941 | -0.60425 | -123.5092
2291.9844 | 123.1934 | -122.9004 | 0.15564 | -0.12502 | 0.023404 | -0.058482 | 0.093137 | -0.074984 | -0.047504 | 0.057838 | 0.004578 | 0.24261 | -0.37994 | -0.054932 | -0.75073 | -0.068665 | 0.004578 | 0.17853 | 0.3479 | -123.3398 | 122.5204 | 0.086975 | 122.905 | 122.8455 | -0.90637 | -0.43945 | 0.19226 | 0.38452 | 122.905 | 123.0789 | 122.1497 | 123.143 | 122.905 | 123.2483 | 122.8317 | -0.43945 | 123.143 | 122.905 | 122.8317 | 122.1497 | 123.2483 | -0.53558 | -123.4955
2292.9219 | 123.0789 | -122.9874 | 0.17395 | -0.094502 | 0.029812 | -0.036051 | 0.10596 | -0.079257 | -0.047504 | 0.052497 | -0.018311 | 0.27924 | -0.42114 | 0.10986 | -0.60883 | 0.068665 | -0.1236 | 0.31586 | 0.31586 | -123.3307 | 122.5662 | 0.10529 | 122.9691 | 123.0972 | -0.78278 | -0.34332 | 0.14191 | 0.40283 | 122.8638 | 123.3032 | 122.3785 | 123.2666 | 122.9691 | 123.3032 | 123.056 | -0.34332 | 123.2666 | 122.9691 | 123.056 | 122.3785 | 123.3032 | -0.59509 | -123.5046
2293.9844 | 123.143 | -122.9095 | 0.16479 | 0.33274 | 0.021267 | -0.039256 | 0.095274 | -0.068576 | -0.053913 | 0.055701 | 0.004578 | 0.23804 | -0.38452 | 0.018311 | -0.65918 | -0.032043 | -0.009155 | 0.2243 | 0.34332 | -123.3673 | 122.525 | 0.073242 | 122.9141 | 122.9279 | -0.82398 | -0.45776 | 0.17853 | 0.3891 | 122.9004 | 123.1339 | 122.2504 | 123.1476 | 122.9141 | 123.2529 | 122.8775 | -0.45776 | 123.1476 | 122.9141 | 122.8775 | 122.2504 | 123.2529 | -0.54932 | -123.5321
2294.9219 | 123.0652 | -122.9691 | 0.16937 | -0.56752 | 0.034085 | -0.04246 | 0.1113 | -0.07178 | -0.015461 | 0.058906 | -0.041199 | 0.28381 | -0.43945 | 0.12817 | -0.59509 | 0.086975 | -0.13733 | 0.33417 | 0.32501 | -123.3536 | 122.5296 | 0.11444 | 122.9279 | 123.0972 | -0.76447 | -0.38452 | 0.15564 | 0.39825 | 122.8317 | 123.3032 | 122.374 | 123.2529 | 122.9279 | 123.2941 | 123.056 | -0.38452 | 123.2529 | 122.9279 | 123.056 | 122.374 | 123.2941 | -0.60883 | -123.5229
2295.9844 | 123.2162 | -122.937 | 0.14648 | -0.15554 | 0.011654 | -0.022166 | 0.092069 | -0.074984 | -0.046436 | 0.06211 | 0.041199 | 0.21515 | -0.3891 | -0.041199 | -0.70953 | -0.07782 | 0.018311 | 0.17853 | 0.36163 | -123.3444 | 122.5479 | 0.068665 | 122.9782 | 122.8958 | -0.85602 | -0.40741 | 0.21515 | 0.4303 | 122.9553 | 123.1155 | 122.2275 | 123.1522 | 122.9782 | 123.2986 | 122.8592 | -0.40741 | 123.1522 | 122.9782 | 122.8592 | 122.2275 | 123.2986 | -0.53558 | -123.4909
2296.9219 | 123.0789 | -122.9782 | 0.15564 | -0.47597 | 0.04263 | -0.037119 | 0.12732 | -0.067507 | -0.02721 | 0.063178 | -0.032043 | 0.28839 | -0.41657 | 0.14191 | -0.57678 | 0.073242 | -0.14191 | 0.32044 | 0.32044 | -123.3444 | 122.5616 | 0.13275 | 122.9462 | 123.1201 | -0.73242 | -0.36621 | 0.1648 | 0.38452 | 122.8363 | 123.2986 | 122.4014 | 123.2666 | 122.9462 | 123.2986 | 123.0515 | -0.36621 | 123.2666 | 122.9462 | 123.0515 | 122.4014 | 123.2986 | -0.57221 | -123.5001
2297.9844 | 123.1567 | -122.937 | 0.14648 | 0.37852 | 0.020199 | -0.041392 | 0.096342 | -0.080325 | -0.037891 | 0.055701 | 0.009155 | 0.2655 | -0.40283 | 0 | -0.6546 | -0.045776 | -0.004578 | 0.22888 | 0.33417 | -123.3627 | 122.5342 | 0.11902 | 122.9462 | 122.937 | -0.80109 | -0.42572 | 0.18768 | 0.41199 | 122.9324 | 123.1659 | 122.2824 | 123.2025 | 122.9462 | 123.2712 | 122.8912 | -0.42572 | 123.2025 | 122.9462 | 122.8912 | 122.2824 | 123.2712 | -0.54932 | -123.5092
2298.9219 | 123.1064 | -122.9553 | 0.17853 | -0.4302 | 0.016995 | -0.027506 | 0.10168 | -0.072848 | -0.029346 | 0.067451 | 0.009155 | 0.26093 | -0.40741 | 0.086975 | -0.6134 | 0.032043 | -0.091553 | 0.2655 | 0.32501 | -123.3444 | 122.5479 | 0.082397 | 122.9645 | 123.0423 | -0.79193 | -0.3891 | 0.14648 | 0.41657 | 122.8638 | 123.2208 | 122.3419 | 123.2162 | 122.9645 | 123.2803 | 122.9874 | -0.3891 | 123.2162 | 122.9645 | 122.9874 | 122.3419 | 123.2803 | -0.58594 | -123.5229
2299.9844 | 123.1613 | -122.9233 | 0.12817 | 0.10386 | 0.024472 | -0.055277 | 0.093137 | -0.081393 | -0.043232 | 0.054633 | -0.032043 | 0.27008 | -0.3891 | -0.009155 | -0.63629 | -0.032043 | 0 | 0.19684 | 0.35706 | -123.349 | 122.5342 | 0.14191 | 122.8912 | 122.9141 | -0.76447 | -0.42572 | 0.22888 | 0.35706 | 122.9233 | 123.1201 | 122.287 | 123.1934 | 122.8912 | 123.2803 | 122.8912 | -0.42572 | 123.1934 | 122.8912 | 122.8912 | 122.287 | 123.2803 | -0.51727 | -123.4772
2300.9219 | 123.2208 | -122.9279 | 0.16479 | -0.3539 | 0.013791 | -0.020029 | 0.10061 | -0.073916 | -0.040028 | 0.055701 | 0.054932 | 0.23804 | -0.37994 | -0.032043 | -0.66376 | -0.068665 | 0.027466 | 0.1831 | 0.36163 | -123.3765 | 122.5479 | 0.073242 | 122.9828 | 122.8958 | -0.82855 | -0.44861 | 0.19684 | 0.43488 | 122.9553 | 123.111 | 122.2641 | 123.1659 | 122.9828 | 123.2895 | 122.8592 | -0.44861 | 123.1659 | 122.9828 | 122.8592 | 122.2641 | 123.2895 | -0.54474 | -123.5413
2301.9844 | 123.1705 | -122.9187 | 0.13733 | 0.14964 | 0.015927 | -0.031779 | 0.093137 | -0.079257 | -0.050709 | 0.051429 | -0.022888 | 0.25635 | -0.40283 | 0.009155 | -0.62256 | -0.027466 | -0.022888 | 0.21973 | 0.3479 | -123.3582 | 122.5159 | 0.11902 | 122.8958 | 122.9279 | -0.75989 | -0.43945 | 0.21057 | 0.37994 | 122.8958 | 123.1384 | 122.2961 | 123.175 | 122.8958 | 123.2666 | 122.8912 | -0.43945 | 123.175 | 122.8958 | 122.8912 | 122.2961 | 123.2666 | -0.54016 | -123.4955
2302.9219 | 123.1247 | -122.9645 | 0.16937 | -0.46071 | 0.022336 | -0.031779 | 0.11984 | -0.064303 | -0.035755 | 0.055701 | -0.004578 | 0.24261 | -0.38452 | 0.068665 | -0.60425 | 0.018311 | -0.07782 | 0.28839 | 0.34332 | -123.349 | 122.58 | 0.073242 | 122.9599 | 123.0331 | -0.77362 | -0.38452 | 0.17395 | 0.37994 | 122.8867 | 123.2529 | 122.3602 | 123.2071 | 122.9599 | 123.3078 | 122.9828 | -0.38452 | 123.2071 | 122.9599 | 122.9828 | 122.3602 | 123.3078 | -0.55389 | -123.5184
2303.9844 | 123.1705 | -122.9324 | 0.14648 | 0.43956 | 0.023404 | -0.051005 | 0.10809 | -0.080325 | -0.038959 | 0.047157 | 0.032043 | 0.22888 | -0.40283 | 0 | -0.6546 | -0.054932 | 0.013733 | 0.19226 | 0.34332 | -123.349 | 122.5296 | 0.082398 | 122.9645 | 122.9324 | -0.80109 | -0.41657 | 0.19684 | 0.43488 | 122.9462 | 123.1247 | 122.2778 | 123.1613 | 122.9645 | 123.2758 | 122.8775 | -0.41657 | 123.1613 | 122.9645 | 122.8775 | 122.2778 | 123.2758 | -0.54932 | -123.4955
2304.9219 | 123.1659 | -122.9416 | 0.14648 | -0.39968 | 0.014859 | -0.027506 | 0.09741 | -0.080325 | -0.035755 | 0.053565 | 0.027466 | 0.25177 | -0.39825 | 0.018311 | -0.62714 | -0.027466 | -0.036621 | 0.23346 | 0.33417 | -123.3627 | 122.5433 | 0.10529 | 122.9691 | 122.9599 | -0.77362 | -0.42114 | 0.18768 | 0.42572 | 122.905 | 123.175 | 122.3145 | 123.1934 | 122.9691 | 123.2758 | 122.9141 | -0.42114 | 123.1934 | 122.9691 | 122.9141 | 122.3145 | 123.2758 | -0.54474 | -123.5092
2305.9688 | 123.1842 | -122.9416 | 0.13733 | 0.13438 | 0.029812 | -0.027506 | 0.10275 | -0.080325 | -0.041096 | 0.047157 | -0.009155 | 0.25177 | -0.38452 | 0.018311 | -0.58594 | -0.018311 | -0.022888 | 0.22888 | 0.34332 | -123.349 | 122.5571 | 0.11444 | 122.9324 | 122.9599 | -0.72327 | -0.40741 | 0.20599 | 0.37537 | 122.9187 | 123.1705 | 122.3557 | 123.1934 | 122.9324 | 123.2849 | 122.9233 | -0.40741 | 123.1934 | 122.9324 | 122.9233 | 122.3557 | 123.2849 | -0.52185 | -123.4863
2306.9219 | 123.1293 | -122.9828 | 0.17395 | -0.36916 | 0.028744 | -0.032847 | 0.12091 | -0.079257 | -0.0443 | 0.061042 | 0.018311 | 0.25635 | -0.40283 | 0.07782 | -0.57678 | 0.013733 | -0.07782 | 0.27008 | 0.32959 | -123.3719 | 122.58 | 0.082398 | 123.0011 | 123.0606 | -0.75073 | -0.3891 | 0.15564 | 0.42114 | 122.905 | 123.2529 | 122.406 | 123.2391 | 123.0011 | 123.3124 | 122.9965 | -0.3891 | 123.2391 | 123.0011 | 122.9965 | 122.406 | 123.3124 | -0.57678 | -123.5458
2307.9844 | 123.1796 | -122.9324 | 0.14191 | 0.1649 | 0.027676 | -0.039256 | 0.10168 | -0.081393 | -0.056049 | 0.052497 | -0.027466 | 0.24261 | -0.37079 | 0.013733 | -0.60883 | -0.027466 | -0.004578 | 0.23804 | 0.33417 | -123.349 | 122.5616 | 0.10071 | 122.905 | 122.9462 | -0.75073 | -0.41657 | 0.19226 | 0.34332 | 122.9279 | 123.1705 | 122.3236 | 123.175 | 122.905 | 123.2666 | 122.905 | -0.41657 | 123.175 | 122.905 | 122.905 | 122.3236 | 123.2666 | -0.5127 | -123.4909
2308.9219 | 123.1934 | -122.9324 | 0.15106 | -0.38442 | 0.015927 | -0.033915 | 0.11023 | -0.083529 | -0.043232 | 0.052497 | 0.027466 | 0.25635 | -0.3891 | 0.018311 | -0.72784 | -0.050354 | -0.004578 | 0.21057 | 0.35706 | -123.3582 | 122.5433 | 0.10529 | 122.9599 | 122.9507 | -0.87891 | -0.42572 | 0.20599 | 0.41656 | 122.9279 | 123.143 | 122.2046 | 123.1888 | 122.9599 | 123.2895 | 122.8821 | -0.42572 | 123.1888 | 122.9599 | 122.8821 | 122.2046 | 123.2895 | -0.54016 | -123.5092
2309.9844 | 123.1613 | -122.9507 | 0.15106 | 0.39378 | 0.045834 | -0.024302 | 0.12198 | -0.069644 | -0.029346 | 0.059974 | -0.009155 | 0.29755 | -0.40741 | 0.12817 | -0.6134 | 0.009155 | -0.050354 | 0.27008 | 0.32501 | -123.3536 | 122.5433 | 0.14648 | 122.9416 | 123.0789 | -0.76447 | -0.40283 | 0.17395 | 0.39825 | 122.9004 | 123.2208 | 122.3373 | 123.2483 | 122.9416 | 123.2758 | 122.9599 | -0.40283 | 123.2483 | 122.9416 | 122.9599 | 122.3373 | 123.2758 | -0.55847 | -123.5046
2310.9219 | 123.143 | -122.9553 | 0.15106 | -0.32338 | 0.018063 | -0.034983 | 0.1145 | -0.07178 | -0.047504 | 0.065314 | 0.018311 | 0.25635 | -0.39825 | 0.022888 | -0.73242 | 0.004578 | -0.054932 | 0.25177 | 0.3479 | -123.3582 | 122.5571 | 0.10529 | 122.9736 | 122.9782 | -0.88348 | -0.40283 | 0.19684 | 0.41657 | 122.9004 | 123.2071 | 122.2229 | 123.2117 | 122.9736 | 123.3032 | 122.9599 | -0.40283 | 123.2117 | 122.9736 | 122.9599 | 122.2229 | 123.3032 | -0.54932 | -123.5092
2311.9844 | 123.1934 | -122.9187 | 0.13733 | 0.39378 | 0.024472 | -0.048869 | 0.10916 | -0.067507 | -0.037891 | 0.071723 | 0.050354 | 0.24719 | -0.37994 | 0.013733 | -0.69122 | -0.054932 | 0.036621 | 0.19226 | 0.3479 | -123.3673 | 122.5388 | 0.10986 | 122.9691 | 122.9324 | -0.82855 | -0.44861 | 0.21057 | 0.4303 | 122.9553 | 123.111 | 122.2275 | 123.1659 | 122.9691 | 123.2666 | 122.8638 | -0.44861 | 123.1659 | 122.9691 | 122.8638 | 122.2275 | 123.2666 | -0.51727 | -123.5046
2312.9219 | 123.2483 | -122.9416 | 0.15106 | -0.12502 | 0.012723 | -0.032847 | 0.10596 | -0.084597 | -0.049641 | 0.050361 | 0.045776 | 0.24261 | -0.39368 | -0.045776 | -0.73242 | -0.064087 | 0.018311 | 0.17395 | 0.36621 | -123.3994 | 122.5479 | 0.091553 | 122.9874 | 122.8958 | -0.88348 | -0.45776 | 0.21515 | 0.43945 | 122.9599 | 123.1155 | 122.2092 | 123.1842 | 122.9874 | 123.3078 | 122.8775 | -0.45776 | 123.1842 | 122.9874 | 122.8775 | 122.2092 | 123.3078 | -0.54474 | -123.5504
2313.9688 | 123.1979 | -122.9553 | 0.1236 | 0.54637 | 0.027676 | -0.021098 | 0.1145 | -0.07178 | -0.019733 | 0.059974 | 0.07782 | 0.23804 | -0.37537 | 0 | -0.67749 | -0.068665 | 0.050354 | 0.18768 | 0.3479 | -123.3994 | 122.58 | 0.11444 | 123.0331 | 122.9553 | -0.80109 | -0.44403 | 0.2243 | 0.45319 | 123.0057 | 123.143 | 122.2778 | 123.1934 | 123.0331 | 123.3032 | 122.8867 | -0.44403 | 123.1934 | 123.0331 | 122.8867 | 122.2778 | 123.3032 | -0.49896 | -123.5229
2314.9219 | 123.2712 | -122.9462 | 0.14191 | -0.048725 | 0.024472 | -0.036051 | 0.098478 | -0.066439 | -0.0443 | 0.061042 | 0.045776 | 0.23346 | -0.35706 | -0.050354 | -0.66834 | -0.082397 | 0.036621 | 0.17395 | 0.34332 | -123.3765 | 122.5891 | 0.091552 | 122.9919 | 122.8958 | -0.81024 | -0.4303 | 0.20142 | 0.40283 | 122.9828 | 123.1201 | 122.2778 | 123.1796 | 122.9919 | 123.2895 | 122.8638 | -0.4303 | 123.1796 | 122.9919 | 122.8638 | 122.2778 | 123.2895 | -0.49896 | -123.5184
2315.9844 | 123.1934 | -122.9736 | 0.15564 | 0.13438 | 0.026608 | -0.043528 | 0.10702 | -0.066439 | -0.041096 | 0.066383 | -0.018311 | 0.27008 | -0.3891 | 0 | -0.58136 | -0.013733 | -0.009155 | 0.2243 | 0.32501 | -123.3765 | 122.5845 | 0.11444 | 122.9553 | 122.9736 | -0.737 | -0.40283 | 0.16937 | 0.37079 | 122.9645 | 123.1979 | 122.3923 | 123.2437 | 122.9553 | 123.2986 | 122.9599 | -0.40283 | 123.2437 | 122.9553 | 122.9599 | 122.3923 | 123.2986 | -0.54474 | -123.5321
2316.9219 | 123.1934 | -122.9691 | 0.14191 | -0.39968 | 0.026608 | -0.028574 | 0.10489 | -0.065371 | -0.040028 | 0.054633 | 0.027466 | 0.26093 | -0.37994 | 0 | -0.62256 | -0.054932 | -0.004578 | 0.20142 | 0.35706 | -123.381 | 122.5891 | 0.11902 | 122.9965 | 122.9691 | -0.76447 | -0.41199 | 0.21515 | 0.40741 | 122.9645 | 123.1705 | 122.3465 | 123.23 | 122.9965 | 123.3261 | 122.9141 | -0.41199 | 123.23 | 122.9965 | 122.9141 | 122.3465 | 123.3261 | -0.52185 | -123.5229
2317.9844 | 123.2254 | -122.9553 | 0.14648 | 0.4243 | 0.03088 | -0.038187 | 0.10809 | -0.070712 | -0.031483 | 0.068519 | 0.059509 | 0.23346 | -0.3891 | 0.009155 | -7.782 | -0.068665 | 0.045776 | 0.16937 | 0.34332 | -123.3856 | 122.5662 | 0.086975 | 123.0148 | 122.9645 | -7.9285 | -0.4303 | 0.19684 | 0.44861 | 123.0011 | 123.1247 | 115.1733 | 123.1888 | 123.0148 | 123.2986 | 122.8867 | -0.4303 | 123.1888 | 123.0148 | 122.8867 | 115.1733 | 123.2986 | -0.53558 | -123.5321
2318.9219 | 123.2529 | -122.9187 | 0.14191 | -0.18605 | 0.024472 | -0.043528 | 0.099546 | -0.07712 | -0.045368 | 0.073859 | 0.032043 | 0.23804 | -0.36621 | -0.054932 | -9.0088 | -0.068665 | 0.064087 | 0.15106 | 0.35706 | -123.3719 | 122.5525 | 0.09613 | 122.9507 | 122.8638 | -9.1507 | -0.45319 | 0.21515 | 0.39825 | 122.9828 | 123.0698 | 113.9099 | 123.1567 | 122.9507 | 123.2758 | 122.85 | -0.45319 | 123.1567 | 122.9507 | 122.85 | 113.9099 | 123.2758 | -0.50812 | -123.5138
2319.9844 | 123.2071 | -122.9691 | 0.14648 | 0.21067 | 0.019131 | -0.034983 | 0.1113 | -0.07178 | -0.030414 | 0.06211 | -0.018311 | 0.24261 | -0.37537 | 0.027466 | -8.8943 | -0.022888 | -0.018311 | 0.2243 | 0.33417 | -123.3719 | 122.5937 | 0.096131 | 122.9507 | 122.9965 | -9.0408 | -0.40283 | 0.18768 | 0.35705 | 122.9507 | 123.1934 | 114.0747 | 123.2117 | 122.9507 | 123.3032 | 122.9462 | -0.40283 | 123.2117 | 122.9507 | 122.9462 | 114.0747 | 123.3032 | -0.52185 | -123.5184
2320.9219 | 123.23 | -122.9416 | 0.14191 | -0.094502 | 0.026608 | -0.052073 | 0.11343 | -0.080325 | -0.050709 | 0.055701 | 0.009155 | 0.25635 | -0.37994 | -0.027466 | -1.7761 | -0.073242 | 0.036621 | 0.1831 | 0.33875 | -123.3856 | 122.5616 | 0.11444 | 122.9507 | 122.9141 | -1.918 | -0.44403 | 0.19684 | 0.3891 | 122.9782 | 123.1247 | 121.1655 | 123.1979 | 122.9507 | 123.2803 | 122.8683 | -0.44403 | 123.1979 | 122.9507 | 122.8683 | 121.1655 | 123.2803 | -0.52185 | -123.5275
2321.9844 | 123.2391 | -122.9645 | 0.14648 | 0.40904 | 0.031949 | -0.021098 | 0.12411 | -0.073916 | -0.02187 | 0.054633 | 0.073242 | 0.24261 | -0.37994 | 0.041199 | -1.5976 | -0.064087 | 0.050354 | 0.1831 | 0.34332 | -123.4177 | 122.5845 | 0.096131 | 123.0377 | 123.0057 | -1.7441 | -0.45319 | 0.19684 | 0.45319 | 123.0148 | 123.1476 | 121.3669 | 123.2071 | 123.0377 | 123.3078 | 122.9004 | -0.45319 | 123.2071 | 123.0377 | 122.9004 | 121.3669 | 123.3078 | -0.52643 | -123.5641
2322.9219 | 123.2666 | -122.9736 | 0.13275 | -0.018208 | 0.018063 | -0.053141 | 0.10061 | -0.07712 | -0.047504 | 0.05677 | 0.054932 | 0.23804 | -0.37079 | -0.054932 | -1.6617 | -0.091553 | 0.045776 | 0.16937 | 0.35706 | -123.4177 | 122.6028 | 0.10529 | 123.0286 | 122.9187 | -1.7944 | -0.44403 | 0.2243 | 0.42572 | 123.0194 | 123.143 | 121.312 | 123.2117 | 123.0286 | 123.3307 | 122.8821 | -0.44403 | 123.2117 | 123.0286 | 122.8821 | 121.312 | 123.3307 | -0.50354 | -123.5504
2323.9844 | 123.111 | -123.0103 | 0.17853 | 0.40904 | 0.040494 | -0.024302 | 0.12732 | -0.076052 | -0.025074 | 0.059974 | -0.013733 | 0.29755 | -0.42114 | 0.16937 | -1.4008 | 0.082397 | -0.11444 | 0.33417 | 0.31586 | -123.3627 | 122.5891 | 0.11902 | 122.9965 | 123.1796 | -1.5793 | -0.35248 | 0.13733 | 0.40741 | 122.8958 | 123.3444 | 121.6095 | 123.3078 | 122.9965 | 123.3261 | 123.0927 | -0.35248 | 123.3078 | 122.9965 | 123.0927 | 121.6095 | 123.3261 | -0.59967 | -123.5413
2324.9219 | 123.3398 | -122.9233 | 0.15106 | -0.21657 | 0.013791 | -0.053141 | 0.10916 | -0.072848 | -0.040028 | 0.071723 | 0.009155 | 0.22888 | -0.37079 | -0.036621 | -3.5889 | -0.068665 | 0.054932 | 0.16479 | 0.36163 | -123.3902 | 122.5525 | 0.07782 | 122.9324 | 122.8867 | -3.7399 | -0.46692 | 0.21057 | 0.37994 | 122.9782 | 123.0881 | 119.3344 | 123.1522 | 122.9324 | 123.2849 | 122.8546 | -0.46692 | 123.1522 | 122.9324 | 122.8546 | 119.3344 | 123.2849 | -0.52185 | -123.5413
2325.9844 | 123.23 | -122.9553 | 0.15106 | 0.36326 | 0.050107 | -0.038187 | 0.12839 | -0.080325 | -0.019733 | 0.059974 | 0.022888 | 0.27924 | -0.40283 | 0.059509 | -1.3596 | -0.041199 | 0.009155 | 0.22888 | 0.33417 | -123.436 | 122.5525 | 0.12817 | 122.9782 | 123.0148 | -1.5106 | -0.48065 | 0.1831 | 0.42572 | 122.9645 | 123.1842 | 121.5958 | 123.2346 | 122.9782 | 123.2895 | 122.9141 | -0.48065 | 123.2346 | 122.9782 | 122.9141 | 121.5958 | 123.2895 | -0.55389 | -123.587
2326.9219 | 123.2254 | -122.9736 | 0.14191 | -0.36916 | 0.026608 | -0.017893 | 0.11236 | -0.067507 | -0.042164 | 0.068519 | 0.013733 | 0.24719 | -0.38452 | 0 | -1.3962 | -0.022888 | -0.013733 | 0.21973 | 0.35248 | -123.3902 | 122.5891 | 0.10528 | 122.9874 | 122.9736 | -1.5381 | -0.41656 | 0.21057 | 0.39825 | 122.9599 | 123.1934 | 121.5775 | 123.2208 | 122.9874 | 123.3261 | 122.9507 | -0.41656 | 123.2208 | 122.9874 | 122.9507 | 121.5775 | 123.3261 | -0.52643 | -123.5321
2327.9844 | 123.2529 | -122.9462 | 0.14191 | 0.45481 | 0.037289 | -0.04246 | 0.1113 | -0.085665 | -0.029346 | 0.054633 | 0.064087 | 0.24261 | -0.36163 | 0.004578 | -1.4099 | -0.054932 | 0.050354 | 0.16937 | 0.32501 | -123.4268 | 122.5845 | 0.10071 | 123.0103 | 122.9507 | -1.5518 | -0.48065 | 0.18311 | 0.42572 | 122.9965 | 123.1155 | 121.5363 | 123.1888 | 123.0103 | 123.2712 | 122.8912 | -0.48065 | 123.1888 | 123.0103 | 122.8912 | 121.5363 | 123.2712 | -0.50354 | -123.5687
2328.9219 | 123.2529 | -122.9828 | 0.15564 | 0.01231 | 0.010586 | -0.031779 | 0.11236 | -0.079257 | -0.054981 | 0.065314 | -0.009155 | 0.24719 | -0.38452 | -0.050354 | -1.4923 | -0.068665 | 0.036621 | 0.19684 | 0.36163 | -123.4177 | 122.5983 | 0.091552 | 122.9736 | 122.9324 | -1.648 | -0.43488 | 0.20599 | 0.37537 | 123.0194 | 123.1796 | 121.4905 | 123.23 | 122.9736 | 123.3444 | 122.9141 | -0.43488 | 123.23 | 122.9736 | 122.9141 | 121.4905 | 123.3444 | -0.54016 | -123.5733
2329.9844 | 123.2574 | -122.9691 | 0.14191 | 0.37852 | 0.024472 | -0.031779 | 0.10916 | -0.073916 | -0.035755 | 0.061042 | 0.045776 | 0.23346 | -0.3891 | 0.004578 | -1.2131 | -0.068665 | 0.054932 | 0.18768 | 0.34332 | -123.4039 | 122.58 | 0.091552 | 123.0148 | 122.9736 | -1.355 | -0.43488 | 0.20142 | 0.43487 | 123.024 | 123.1567 | 121.756 | 123.2025 | 123.0148 | 123.3124 | 122.9004 | -0.43488 | 123.2025 | 123.0148 | 122.9004 | 121.756 | 123.3124 | -0.53101 | -123.5458
2330.9219 | 123.2162 | -122.9965 | 0.14191 | -0.41494 | 0.013791 | -0.048869 | 0.10809 | -0.084597 | -0.046436 | 0.055701 | 0.045776 | 0.25177 | -0.38452 | -0.004578 | -1.1398 | -0.036621 | 0.018311 | 0.18768 | 0.35706 | -123.4085 | 122.612 | 0.10986 | 123.0423 | 122.9919 | -1.2817 | -0.41199 | 0.21515 | 0.4303 | 123.0148 | 123.1842 | 121.8567 | 123.2483 | 123.0423 | 123.3536 | 122.9599 | -0.41199 | 123.2483 | 123.0423 | 122.9599 | 121.8567 | 123.3536 | -0.52643 | -123.5504
2331.9844 | 123.1613 | -123.0057 | 0.1831 | -0.55227 | 0.012723 | -0.043528 | 0.1145 | -0.065371 | -0.040028 | 0.063178 | -0.009155 | 0.27008 | -0.41199 | 0.10529 | -1.0208 | 0.059509 | -0.10986 | 0.31586 | 0.32501 | -123.3856 | 122.5937 | 0.086976 | 122.9965 | 123.111 | -1.2039 | -0.37994 | 0.14191 | 0.40283 | 122.8958 | 123.3215 | 121.9849 | 123.2758 | 122.9965 | 123.3307 | 123.0652 | -0.37994 | 123.2758 | 122.9965 | 123.0652 | 121.9849 | 123.3307 | -0.59509 | -123.5687
2332.9219 | 123.2712 | -123.0103 | 0.14648 | -0.8727 | 0.018063 | -0.040324 | 0.099546 | -0.07178 | -0.043232 | 0.064246 | 0.027466 | 0.22888 | -0.38452 | -0.073242 | -1.2314 | -0.086975 | 0.050354 | 0.16022 | 0.35248 | -123.3948 | 122.6257 | 0.082398 | 123.0377 | 122.937 | -1.3779 | -0.38452 | 0.20599 | 0.41199 | 123.0606 | 123.1705 | 121.7789 | 123.2391 | 123.0377 | 123.3627 | 122.9233 | -0.38452 | 123.2391 | 123.0377 | 122.9233 | 121.7789 | 123.3627 | -0.531 | -123.5413
2333.9844 | 123.2391 | -122.9599 | 0.16022 | 0.45481 | 0.029812 | -0.028574 | 0.11343 | -0.084597 | -0.028278 | 0.059974 | 0.059509 | 0.23804 | -0.37537 | 0 | -0.76446 | -0.073242 | 0.050354 | 0.1831 | 0.35706 | -123.4177 | 122.5845 | 0.07782 | 123.0194 | 122.9599 | -0.92468 | -0.45776 | 0.19684 | 0.43487 | 123.0103 | 123.143 | 122.1954 | 123.1979 | 123.0194 | 123.317 | 122.8867 | -0.45776 | 123.1979 | 123.0194 | 122.8867 | 122.1954 | 123.317 | -0.53558 | -123.5779
2334.9219 | 123.2574 | -122.9691 | 0.13733 | -0.32338 | 0.016995 | -0.05955 | 0.11984 | -0.073916 | -0.035755 | 0.053565 | 0.050354 | 0.22888 | -0.3891 | -0.022888 | -0.74158 | -0.045776 | 0.013733 | 0.17395 | 0.36163 | -123.4131 | 122.58 | 0.091553 | 123.0194 | 122.9462 | -0.87891 | -0.44403 | 0.2243 | 0.43945 | 122.9828 | 123.143 | 122.2275 | 123.1979 | 123.0194 | 123.3307 | 122.9233 | -0.44403 | 123.1979 | 123.0194 | 122.9233 | 122.2275 | 123.3307 | -0.52643 | -123.5504
2335.9844 | 123.2208 | -122.9874 | 0.14191 | 0.1649 | 0.027676 | -0.032847 | 0.10596 | -0.080325 | -0.038959 | 0.05677 | -0.018311 | 0.25635 | -0.38452 | 0.018311 | -0.68665 | -0.027466 | -0.004578 | 0.22888 | 0.3479 | -123.3902 | 122.6028 | 0.11444 | 122.9691 | 123.0057 | -0.82855 | -0.40283 | 0.20599 | 0.36621 | 122.9828 | 123.2162 | 122.3007 | 123.2437 | 122.9691 | 123.3353 | 122.9599 | -0.40283 | 123.2437 | 122.9691 | 122.9599 | 122.3007 | 123.3353 | -0.52643 | -123.5321
2336.9219 | 123.1567 | -123.0194 | 0.15106 | -0.018208 | 0.034085 | -0.044596 | 0.13586 | -0.07712 | -0.024006 | 0.047157 | 0.054932 | 0.3067 | -0.39368 | 0.1831 | -1.2131 | 0.045776 | -0.086975 | 0.31586 | 0.31586 | -123.4131 | 122.6257 | 0.15564 | 123.0743 | 123.2025 | -1.3641 | -0.39368 | 0.16479 | 0.44861 | 122.9324 | 123.3353 | 121.8063 | 123.3261 | 123.0743 | 123.3353 | 123.0652 | -0.39368 | 123.3261 | 123.0743 | 123.0652 | 121.8063 | 123.3353 | -0.54474 | -123.5641
2337.9844 | 123.2666 | -122.9645 | 0.12817 | 0.43956 | 0.023404 | -0.037119 | 0.12305 | -0.067507 | -0.028278 | 0.053565 | 0.064087 | 0.25177 | -0.37537 | -0.004578 | -0.32501 | -0.068665 | 0.054932 | 0.19226 | 0.36621 | -123.3948 | 122.5891 | 0.1236 | 123.0286 | 122.9599 | -0.45319 | -0.4303 | 0.23804 | 0.43945 | 123.0194 | 123.1567 | 122.6395 | 123.2162 | 123.0286 | 123.3307 | 122.8958 | -0.4303 | 123.2162 | 123.0286 | 122.8958 | 122.6395 | 123.3307 | -0.50354 | -123.5229
2338.9219 | 123.2712 | -122.9645 | 0.15106 | -0.32338 | 0.012723 | -0.037119 | 0.095274 | -0.07712 | -0.056049 | 0.061042 | 0.027466 | 0.23346 | -0.37994 | -0.036621 | -0.32959 | -0.050354 | 0.032043 | 0.18768 | 0.3479 | -123.4085 | 122.5845 | 0.082397 | 122.9919 | 122.9279 | -0.48065 | -0.44403 | 0.19684 | 0.40741 | 122.9965 | 123.1522 | 122.6349 | 123.1979 | 122.9919 | 123.3124 | 122.9141 | -0.44403 | 123.1979 | 122.9919 | 122.9141 | 122.6349 | 123.3124 | -0.53101 | -123.5596
2339.9844 | 123.2529 | -122.9645 | 0.15106 | 0.43956 | 0.028744 | -0.030711 | 0.10809 | -0.083529 | -0.032551 | 0.061042 | 0.041199 | 0.23346 | -0.36621 | -0.013733 | -0.48065 | -0.059509 | 0.036621 | 0.19226 | 0.32501 | -123.4131 | 122.5983 | 0.082397 | 123.0057 | 122.9507 | -0.63171 | -0.44861 | 0.17395 | 0.40741 | 123.0011 | 123.1567 | 122.4838 | 123.1979 | 123.0057 | 123.2895 | 122.905 | -0.44861 | 123.1979 | 123.0057 | 122.905 | 122.4838 | 123.2895 | -0.51727 | -123.5641
2340.9219 | 123.1613 | -123.024 | 0.1831 | -0.38442 | 0.016995 | -0.028574 | 0.11023 | -0.079257 | -0.036823 | 0.050361 | 0 | 0.27466 | -0.39368 | 0.10529 | -0.45776 | 0.059509 | -0.082397 | 0.30212 | 0.32959 | -123.3948 | 122.6303 | 0.091553 | 123.024 | 123.1293 | -0.64087 | -0.37079 | 0.14649 | 0.39368 | 122.9416 | 123.3261 | 122.5662 | 123.2986 | 123.024 | 123.3536 | 123.0835 | -0.37079 | 123.2986 | 123.024 | 123.0835 | 122.5662 | 123.3536 | -0.57678 | -123.5779
2341.9844 | 123.1888 | -123.0148 | 0.17395 | -0.4302 | 0.027676 | -0.046732 | 0.11343 | -0.074984 | -0.032551 | 0.064246 | -0.009155 | 0.3067 | -0.43945 | 0.14648 | -0.32044 | 0.064087 | -0.11444 | 0.31586 | 0.32959 | -123.4085 | 122.5754 | 0.13275 | 123.0057 | 123.1613 | -0.49439 | -0.39368 | 0.15564 | 0.4303 | 122.9004 | 123.3307 | 122.6944 | 123.3215 | 123.0057 | 123.3444 | 123.0789 | -0.39368 | 123.3215 | 123.0057 | 123.0789 | 122.6944 | 123.3444 | -0.6134 | -123.5825
2342.9219 | 123.2666 | -122.9599 | 0.15106 | -0.39968 | 0.029812 | -0.024302 | 0.094205 | -0.070712 | -0.040028 | 0.05677 | 0.032043 | 0.25177 | -0.36163 | -0.022888 | -0.40283 | -0.054932 | 0.032043 | 0.19226 | 0.36621 | -123.4314 | 122.5983 | 0.10071 | 122.9919 | 122.937 | -0.55389 | -0.4715 | 0.21515 | 0.39368 | 122.9919 | 123.1522 | 122.5571 | 123.2117 | 122.9919 | 123.3261 | 122.905 | -0.4715 | 123.2117 | 122.9919 | 122.905 | 122.5571 | 123.3261 | -0.5127 | -123.5825
2343.9844 | 123.23 | -123.0011 | 0.15106 | 0.37852 | 0.019131 | -0.048869 | 0.099546 | -0.079257 | -0.047504 | 0.046088 | -0.013733 | 0.24261 | -0.37994 | 0 | -0.35706 | -0.022888 | -0.018311 | 0.2243 | 0.33875 | -123.4131 | 122.6212 | 0.091553 | 122.9874 | 123.0011 | -0.50812 | -0.41199 | 0.18768 | 0.36621 | 122.9828 | 123.2254 | 122.644 | 123.2437 | 122.9874 | 123.3398 | 122.9782 | -0.41199 | 123.2437 | 122.9874 | 122.9782 | 122.644 | 123.3398 | -0.53101 | -123.5641
2344.9219 | 123.2895 | -122.9919 | 0.15564 | -0.4302 | 0.015927 | -0.086253 | 0.10168 | -0.067507 | -0.045368 | 0.055701 | 0.036621 | 0.25177 | -0.3891 | -0.022888 | -0.42572 | -0.050354 | 0.027466 | 0.18768 | 0.36621 | -123.4451 | 122.6028 | 0.09613 | 123.0286 | 122.9691 | -0.58136 | -0.45319 | 0.21057 | 0.42572 | 123.0194 | 123.1796 | 122.5662 | 123.2437 | 123.0286 | 123.3582 | 122.9416 | -0.45319 | 123.2437 | 123.0286 | 122.9416 | 122.5662 | 123.3582 | -0.54474 | -123.6008
2345.9219 | 123.3078 | -122.9782 | 0.13733 | -0.64382 | 0.022336 | -0.024302 | 0.10916 | -0.079257 | -0.051777 | 0.064246 | 0.045776 | 0.23804 | -0.38452 | -0.054932 | -0.43945 | -0.064087 | 0.032043 | 0.17395 | 0.35706 | -123.4406 | 122.5937 | 0.10071 | 123.024 | 122.9233 | -0.57678 | -0.46234 | 0.21973 | 0.4303 | 123.0103 | 123.1522 | 122.5388 | 123.2162 | 123.024 | 123.3353 | 122.9141 | -0.46234 | 123.2162 | 123.024 | 122.9141 | 122.5388 | 123.3353 | -0.52185 | -123.5779
2346.9219 | 123.2849 | -122.9736 | 0.13733 | -0.38442 | 0.028744 | -0.060618 | 0.10382 | -0.079257 | -0.042164 | 0.057838 | 0.054932 | 0.25635 | -0.37994 | -0.022888 | -0.5127 | -0.064087 | 0.018311 | 0.1831 | 0.35706 | -123.4543 | 122.5937 | 0.11902 | 123.0286 | 122.9507 | -0.65002 | -0.48065 | 0.21973 | 0.43488 | 122.9919 | 123.1567 | 122.4609 | 123.23 | 123.0286 | 123.3307 | 122.9095 | -0.48065 | 123.23 | 123.0286 | 122.9095 | 122.4609 | 123.3307 | -0.51727 | -123.5916
2347.9844 | 123.2162 | -122.9828 | 0.13733 | 0.25645 | 0.027676 | -0.029642 | 0.10702 | -0.080325 | -0.054981 | 0.061042 | 0.004578 | 0.25177 | -0.38452 | 0.018311 | -0.42114 | -0.018311 | -0.004578 | 0.22888 | 0.33875 | -123.4131 | 122.5983 | 0.11444 | 122.9874 | 123.0011 | -0.55847 | -0.4303 | 0.20142 | 0.3891 | 122.9782 | 123.2117 | 122.5616 | 123.2346 | 122.9874 | 123.3215 | 122.9645 | -0.4303 | 123.2346 | 122.9874 | 122.9645 | 122.5616 | 123.3215 | -0.52185 | -123.5504
2348.9219 | 123.2208 | -123.024 | 0.16022 | 0.18016 | 0.029812 | -0.02537 | 0.10809 | -0.078189 | -0.054981 | 0.058906 | -0.013733 | 0.25177 | -0.39368 | 0 | -0.41657 | -0.018311 | 0 | 0.2243 | 0.32959 | -123.4177 | 122.6303 | 0.091553 | 123.0103 | 123.024 | -0.57678 | -0.39368 | 0.16937 | 0.37994 | 123.024 | 123.2483 | 122.6074 | 123.2758 | 123.0103 | 123.3536 | 123.0057 | -0.39368 | 123.2758 | 123.0103 | 123.0057 | 122.6074 | 123.3536 | -0.55389 | -123.5779
2349.9844 | 123.1888 | -123.024 | 0.15564 | 0.37852 | 0.037289 | -0.029642 | 0.13266 | -0.07712 | -0.030414 | 0.052497 | -0.009155 | 0.29297 | -0.40283 | 0.16479 | -0.68207 | 0.041199 | -0.086975 | 0.3067 | 0.31128 | -123.4085 | 122.6212 | 0.13733 | 123.0148 | 123.1888 | -0.83771 | -0.38452 | 0.15564 | 0.39368 | 122.937 | 123.3307 | 122.3419 | 123.317 | 123.0148 | 123.3353 | 123.0652 | -0.38452 | 123.317 | 123.0148 | 123.0652 | 122.3419 | 123.3353 | -0.55847 | -123.5641
2350.9219 | 123.2849 | -122.9874 | 0.14648 | -0.38442 | 0.013791 | -0.062754 | 0.11343 | -0.082461 | -0.050709 | 0.063178 | 0.032043 | 0.24261 | -0.3891 | -0.045776 | -0.53558 | -0.073242 | 0.013733 | 0.19226 | 0.37079 | -123.4268 | 122.5983 | 0.096131 | 123.0194 | 122.9416 | -0.68207 | -0.43945 | 0.2243 | 0.42114 | 123.0011 | 123.1796 | 122.4518 | 123.23 | 123.0194 | 123.3582 | 122.9141 | -0.43945 | 123.23 | 123.0194 | 122.9141 | 122.4518 | 123.3582 | -0.53558 | -123.5733
2351.9844 | 123.2071 | -123.024 | 0.16937 | 0.40904 | 0.041562 | -0.021098 | 0.12945 | -0.080325 | -0.017597 | 0.048225 | 0 | 0.28839 | -0.4303 | 0.13275 | -0.27924 | 0.022888 | -0.059509 | 0.28839 | 0.31586 | -123.436 | 122.5937 | 0.11902 | 123.024 | 123.1567 | -0.44861 | -0.41199 | 0.14648 | 0.4303 | 122.9645 | 123.3124 | 122.7448 | 123.3124 | 123.024 | 123.3398 | 123.0469 | -0.41199 | 123.3124 | 123.024 | 123.0469 | 122.7448 | 123.3398 | -0.59967 | -123.6053
2352.9219 | 123.2483 | -122.9965 | 0.14191 | 0.01231 | 0.016995 | -0.029642 | 0.096342 | -0.076052 | -0.047504 | 0.06211 | -0.032043 | 0.25635 | -0.37994 | -0.022888 | -0.35248 | -0.041199 | 0.013733 | 0.20142 | 0.33417 | -123.4085 | 122.6166 | 0.11444 | 122.9645 | 122.9736 | -0.49439 | -0.41199 | 0.19226 | 0.3479 | 123.0103 | 123.1979 | 122.644 | 123.2529 | 122.9645 | 123.3307 | 122.9553 | -0.41199 | 123.2529 | 122.9645 | 122.9553 | 122.644 | 123.3307 | -0.52185 | -123.5504
2353.9844 | 123.2025 | -123.024 | 0.15106 | 0.45481 | 0.034085 | -0.039256 | 0.12625 | -0.078189 | -0.037891 | 0.057838 | 0 | 0.28381 | -0.42572 | 0.12817 | -0.31586 | 0.027466 | -0.050354 | 0.2655 | 0.3067 | -123.436 | 122.5983 | 0.13275 | 123.024 | 123.1522 | -0.46692 | -0.41199 | 0.15564 | 0.42572 | 122.9736 | 123.2895 | 122.7081 | 123.3078 | 123.024 | 123.3307 | 123.0515 | -0.41199 | 123.3078 | 123.024 | 123.0515 | 122.7081 | 123.3307 | -0.57678 | -123.587
2354.9219 | 123.3124 | -123.0011 | 0.11902 | -0.079243 | 0.0095178 | -0.05955 | 0.11023 | -0.069644 | -0.050709 | 0.064246 | 0.027466 | 0.23346 | -0.37537 | -0.045776 | -0.56763 | -0.082397 | 0.004578 | 0.17853 | 0.32959 | -123.4451 | 122.6257 | 0.11444 | 123.0286 | 122.9553 | -0.68665 | -0.44403 | 0.21057 | 0.40283 | 123.0057 | 123.1796 | 122.4335 | 123.2346 | 123.0286 | 123.3307 | 122.9187 | -0.44403 | 123.2346 | 123.0286 | 122.9187 | 122.4335 | 123.3307 | -0.49438 | -123.5641
2355.9844 | 123.2666 | -122.9965 | 0.12817 | 0.47007 | 0.038357 | -0.018961 | 0.1145 | -0.07178 | -0.032551 | 0.055701 | 0.082397 | 0.26093 | -0.39368 | 0.041199 | -0.27466 | -0.068665 | 0.032043 | 0.19226 | 0.35706 | -123.4634 | 122.6028 | 0.13275 | 123.0789 | 123.0377 | -0.40283 | -0.46692 | 0.22888 | 0.47607 | 123.0286 | 123.1888 | 122.7219 | 123.2574 | 123.0789 | 123.3536 | 122.9279 | -0.46692 | 123.2574 | 123.0789 | 122.9279 | 122.7219 | 123.3536 | -0.52185 | -123.5916
2356.9219 | 123.2254 | -122.9965 | 0.15564 | 0.10386 | 0.020199 | -0.02537 | 0.099546 | -0.076052 | -0.0443 | 0.068519 | -0.027466 | 0.26093 | -0.3891 | -0.009155 | -0.27008 | -0.018311 | -0.013733 | 0.22888 | 0.33417 | -123.4406 | 122.6074 | 0.10529 | 122.9691 | 122.9874 | -0.42572 | -0.44403 | 0.17853 | 0.36163 | 122.9828 | 123.2254 | 122.7264 | 123.2574 | 122.9691 | 123.3307 | 122.9782 | -0.44403 | 123.2574 | 122.9691 | 122.9782 | 122.7264 | 123.3307 | -0.54474 | -123.5962
2357.9219 | 123.2437 | -123.0286 | 0.16022 | 0.10386 | 0.02554 | -0.051005 | 0.10382 | -0.073916 | -0.051777 | 0.054633 | 0.022888 | 0.24719 | -0.37994 | 0.009155 | -0.25635 | -0.018311 | -0.009155 | 0.23346 | 0.33875 | -123.4177 | 122.6486 | 0.086975 | 123.0515 | 123.0377 | -0.41657 | -0.3891 | 0.17853 | 0.40283 | 123.0194 | 123.262 | 122.7722 | 123.2758 | 123.0515 | 123.3673 | 123.0103 | -0.3891 | 123.2758 | 123.0515 | 123.0103 | 122.7722 | 123.3673 | -0.54016 | -123.5779
2358.9844 | 123.1476 | -123.0423 | 0.1831 | 0.058086 | 0.046902 | -0.017893 | 0.1412 | -0.074984 | -0.018665 | 0.061042 | 0.022888 | 0.29755 | -0.40741 | 0.17853 | -0.15564 | 0.082397 | -0.10986 | 0.32959 | 0.31128 | -123.4451 | 122.6349 | 0.11444 | 123.0652 | 123.2208 | -0.33874 | -0.40283 | 0.12817 | 0.4303 | 122.9324 | 123.3719 | 122.8867 | 123.3398 | 123.0652 | 123.3536 | 123.1247 | -0.40283 | 123.3398 | 123.0652 | 123.1247 | 122.8867 | 123.3536 | -0.59052 | -123.6282
2359.9219 | 123.2346 | -123.0011 | 0.14191 | 0.28697 | 0.029812 | -0.030711 | 0.10916 | -0.064303 | -0.047504 | 0.052497 | 0.032043 | 0.25177 | -0.37994 | -0.004578 | -0.24261 | -0.045776 | 0.027466 | 0.19684 | 0.35248 | -123.436 | 122.6212 | 0.10986 | 123.0331 | 122.9965 | -0.38452 | -0.43488 | 0.21057 | 0.41199 | 123.0286 | 123.1979 | 122.7585 | 123.2529 | 123.0331 | 123.3536 | 122.9553 | -0.43488 | 123.2529 | 123.0331 | 122.9553 | 122.7585 | 123.3536 | -0.52185 | -123.5779
2360.9688 | 123.1842 | -123.0652 | 0.16937 | -0.36916 | 0.027676 | -0.031779 | 0.12945 | -0.073916 | -0.022938 | 0.051429 | -0.009155 | 0.30212 | -0.4303 | 0.15106 | -0.16937 | 0.054932 | -0.10986 | 0.31128 | 0.3067 | -123.4406 | 122.6349 | 0.13275 | 123.056 | 123.2162 | -0.33875 | -0.37537 | 0.13733 | 0.42114 | 122.9553 | 123.3765 | 122.8958 | 123.3673 | 123.056 | 123.3719 | 123.1201 | -0.37537 | 123.3673 | 123.056 | 123.1201 | 122.8958 | 123.3719 | -0.59967 | -123.6099
2361.9219 | 123.2758 | -122.9965 | 0.14648 | 0.47007 | 0.026608 | -0.028574 | 0.12732 | -0.07712 | -0.028278 | 0.059974 | 0.041199 | 0.27924 | -0.38452 | 0.054932 | -0.21515 | -0.009155 | 0.050354 | 0.1831 | 0.32959 | -123.4726 | 122.612 | 0.13275 | 123.0377 | 123.0515 | -0.36163 | -0.47607 | 0.18311 | 0.42572 | 123.0469 | 123.1796 | 122.7814 | 123.2758 | 123.0377 | 123.3261 | 122.9874 | -0.47607 | 123.2758 | 123.0377 | 122.9874 | 122.7814 | 123.3261 | -0.531 | -123.6191
2362.9844 | 123.1979 | -123.0835 | 0.16937 | -0.094502 | 0.033017 | -0.041392 | 0.11664 | -0.061099 | -0.016529 | 0.072791 | 0.050354 | 0.29755 | -0.40741 | 0.14648 | -0.11902 | 0.036621 | -0.07782 | 0.30212 | 0.32044 | -123.4818 | 122.6761 | 0.12817 | 123.1338 | 123.23 | -0.28839 | -0.39825 | 0.15106 | 0.45776 | 123.0057 | 123.3856 | 122.9645 | 123.381 | 123.1338 | 123.4039 | 123.1201 | -0.39825 | 123.381 | 123.1338 | 123.1201 | 122.9645 | 123.4039 | -0.57678 | -123.6511
2363.9219 | 123.3078 | -122.9782 | 0.13733 | 0.48533 | 0.024472 | -0.040324 | 0.10596 | -0.069644 | -0.033619 | 0.053565 | 0.068665 | 0.24719 | -0.37079 | -0.004578 | -0.21973 | -0.068665 | 0.050354 | 0.20142 | 0.34332 | -123.468 | 122.6074 | 0.10986 | 123.0469 | 122.9736 | -0.35706 | -0.48981 | 0.20599 | 0.43945 | 123.0286 | 123.1796 | 122.7585 | 123.2254 | 123.0469 | 123.3215 | 122.9095 | -0.48981 | 123.2254 | 123.0469 | 122.9095 | 122.7585 | 123.3215 | -0.50812 | -123.6053
2364.9844 | 123.175 | -123.0469 | 0.19226 | 0.28697 | 0.037289 | -0.022166 | 0.12198 | -0.068576 | -0.011188 | 0.063178 | -0.022888 | 0.32044 | -0.42114 | 0.16479 | -0.13733 | 0.07782 | -0.1236 | 0.33417 | 0.3067 | -123.4497 | 122.6257 | 0.12817 | 123.024 | 123.2117 | -0.32959 | -0.40283 | 0.11444 | 0.39825 | 122.9233 | 123.381 | 122.9095 | 123.3673 | 123.024 | 123.3536 | 123.1247 | -0.40283 | 123.3673 | 123.024 | 123.1247 | 122.9095 | 123.3536 | -0.6134 | -123.642
2365.9219 | 123.2895 | -122.9965 | 0.13733 | 0.4243 | 0.044766 | -0.028574 | 0.12839 | -0.072848 | -0.026142 | 0.059974 | 0.059509 | 0.2655 | -0.39825 | 0.045776 | -0.1831 | -0.022888 | 0.004578 | 0.21515 | 0.33875 | -123.468 | 122.5983 | 0.12817 | 123.056 | 123.0423 | -0.32043 | -0.4715 | 0.20142 | 0.45776 | 123.0011 | 123.2117 | 122.8134 | 123.262 | 123.056 | 123.3353 | 122.9736 | -0.4715 | 123.262 | 123.056 | 122.9736 | 122.8134 | 123.3353 | -0.53558 | -123.6053
2366.9844 | 123.23 | -123.0835 | 0.17395 | -0.36916 | 0.037289 | -0.020029 | 0.12198 | -0.070712 | -0.030414 | 0.057838 | -0.009155 | 0.31586 | -0.41657 | 0.13733 | -0.19684 | 0.059509 | -0.082397 | 0.31128 | 0.32501 | -123.468 | 122.6669 | 0.14191 | 123.0743 | 123.2208 | -0.37079 | -0.38452 | 0.15106 | 0.40741 | 123.0011 | 123.3948 | 122.8867 | 123.3994 | 123.0743 | 123.4085 | 123.143 | -0.38452 | 123.3994 | 123.0743 | 123.143 | 122.8867 | 123.4085 | -0.59052 | -123.642
2367.9219 | 123.2117 | -123.0469 | 0.15564 | 0.40904 | 0.045834 | -0.024302 | 0.10702 | -0.069644 | -0.020801 | 0.053565 | -0.036621 | 0.29297 | -0.40741 | 0.10986 | -0.16022 | 0.036621 | -0.064087 | 0.28381 | 0.32959 | -123.4589 | 122.6395 | 0.13733 | 123.0103 | 123.1567 | -0.31586 | -0.41199 | 0.17395 | 0.37079 | 122.9828 | 123.3307 | 122.8867 | 123.3398 | 123.0103 | 123.3765 | 123.0835 | -0.41199 | 123.3398 | 123.0103 | 123.0835 | 122.8867 | 123.3765 | -0.56305 | -123.6145
2368.9844 | 123.2437 | -123.0606 | 0.17853 | -0.39968 | 0.041562 | -0.041392 | 0.12091 | -0.065371 | -0.022938 | 0.063178 | 0.004578 | 0.31586 | -0.4303 | 0.11902 | -0.19226 | 0.059509 | -0.086975 | 0.29755 | 0.33417 | -123.468 | 122.6303 | 0.13733 | 123.0652 | 123.1796 | -0.37079 | -0.40741 | 0.15564 | 0.43488 | 122.9736 | 123.3582 | 122.8683 | 123.3765 | 123.0652 | 123.3948 | 123.1201 | -0.40741 | 123.3765 | 123.0652 | 123.1201 | 122.8683 | 123.3948 | -0.60883 | -123.6465
2369.9219 | 123.1888 | -123.0652 | 0.1831 | 0.33274 | 0.029812 | 0.0013326 | 0.11236 | -0.066439 | -0.016529 | 0.071723 | -0.018311 | 0.28839 | -0.41657 | 0.15106 | -0.16937 | 0.073242 | -0.10986 | 0.3479 | 0.3067 | -123.436 | 122.6486 | 0.10529 | 123.0469 | 123.2162 | -0.35248 | -0.37079 | 0.1236 | 0.39825 | 122.9553 | 123.4131 | 122.8958 | 123.3536 | 123.0469 | 123.3719 | 123.1384 | -0.37079 | 123.3536 | 123.0469 | 123.1384 | 122.8958 | 123.3719 | -0.59967 | -123.6191
2370.9844 | 123.2025 | -123.0698 | 0.16937 | -0.41494 | 0.041562 | -0.015757 | 0.11236 | -0.055758 | -0.022938 | 0.047157 | -0.022888 | 0.31128 | -0.43945 | 0.10529 | -0.17853 | 0.082397 | -0.1236 | 0.34332 | 0.29755 | -123.4451 | 122.6303 | 0.14191 | 123.0469 | 123.175 | -0.3479 | -0.37537 | 0.12817 | 0.41656 | 122.9462 | 123.4131 | 122.8912 | 123.381 | 123.0469 | 123.3673 | 123.1522 | -0.37537 | 123.381 | 123.0469 | 123.1522 | 122.8912 | 123.3673 | -0.60883 | -123.6145
2371.9219 | 123.1705 | -123.0606 | 0.16937 | 0.75999 | 0.04263 | -0.015757 | 0.1177 | -0.063235 | -0.022938 | 0.063178 | 0.013733 | 0.3067 | -0.41199 | 0.16937 | -1.0529 | 0.09613 | -0.13275 | 0.37537 | 0.32501 | -123.4634 | 122.6486 | 0.13733 | 123.0743 | 123.23 | -1.2222 | -0.40283 | 0.15564 | 0.42572 | 122.9279 | 123.436 | 122.0078 | 123.3673 | 123.0743 | 123.3856 | 123.1567 | -0.40283 | 123.3673 | 123.0743 | 123.1567 | 122.0078 | 123.3856 | -0.58136 | -123.6328
2372.9688 | 123.2986 | -123.0469 | 0.13733 | -0.048725 | 0.018063 | -0.0478 | 0.086729 | -0.061099 | -0.037891 | 0.073859 | 0.036621 | 0.24719 | -0.37994 | -0.068665 | -0.51727 | -0.050354 | 0.032043 | 0.18768 | 0.35706 | -123.4863 | 122.6669 | 0.10986 | 123.0835 | 122.9782 | -0.6546 | -0.43945 | 0.21973 | 0.41657 | 123.0789 | 123.2346 | 122.5296 | 123.2941 | 123.0835 | 123.4039 | 122.9965 | -0.43945 | 123.2941 | 123.0835 | 122.9965 | 122.5296 | 123.4039 | -0.51727 | -123.6237
2373.9219 | 123.2071 | -123.0743 | 0.16937 | 0.10386 | 0.036221 | -0.015757 | 0.11984 | -0.057894 | -0.018665 | 0.051429 | 0.018311 | 0.31128 | -0.39368 | 0.16479 | -0.52643 | 0.073242 | -0.12817 | 0.3479 | 0.31128 | -123.4955 | 122.6807 | 0.14191 | 123.0927 | 123.2391 | -0.6958 | -0.42114 | 0.14191 | 0.41199 | 122.9462 | 123.4222 | 122.5479 | 123.3856 | 123.0927 | 123.3856 | 123.1476 | -0.42114 | 123.3856 | 123.0927 | 123.1476 | 122.5479 | 123.3856 | -0.56305 | -123.6649
2374.9219 | 123.23 | -123.0606 | 0.1831 | 0.14964 | 0.050107 | -0.014689 | 0.1113 | -0.067507 | -0.014393 | 0.061042 | 0.036621 | 0.29297 | -0.42114 | 0.14191 | -0.58594 | 0.064087 | -0.10071 | 0.3479 | 0.32959 | -123.4726 | 122.6395 | 0.10986 | 123.0972 | 123.2025 | -0.76904 | -0.41199 | 0.14649 | 0.45776 | 122.9599 | 123.4085 | 122.4747 | 123.3536 | 123.0972 | 123.3902 | 123.1247 | -0.41199 | 123.3536 | 123.0972 | 123.1247 | 122.4747 | 123.3902 | -0.60425 | -123.6557
2375.9844 | 123.2346 | -123.0377 | 0.16022 | -0.10976 | 0.036221 | -0.0040084 | 0.1145 | -0.057894 | -0.025074 | 0.061042 | 0.027466 | 0.29755 | -0.40283 | 0.1236 | -0.72784 | 0.045776 | -0.073242 | 0.32501 | 0.33417 | -123.4863 | 122.6349 | 0.13733 | 123.0652 | 123.1613 | -0.88806 | -0.44861 | 0.17395 | 0.4303 | 122.9645 | 123.3627 | 122.3099 | 123.3353 | 123.0652 | 123.3719 | 123.0835 | -0.44861 | 123.3353 | 123.0652 | 123.0835 | 122.3099 | 123.3719 | -0.56305 | -123.6465
2376.9219 | 123.1979 | -123.0743 | 0.17395 | 0.13438 | 0.039425 | -0.031779 | 0.1177 | -0.057894 | -0.015461 | 0.058906 | 0.018311 | 0.32044 | -0.40741 | 0.13733 | -0.54016 | 0.07782 | -0.10071 | 0.33875 | 0.33417 | -123.4818 | 122.6669 | 0.14649 | 123.0927 | 123.2117 | -0.71411 | -0.40741 | 0.16022 | 0.42572 | 122.9736 | 123.4131 | 122.5342 | 123.3948 | 123.0927 | 123.4085 | 123.1522 | -0.40741 | 123.3948 | 123.0927 | 123.1522 | 122.5342 | 123.4085 | -0.58136 | -123.6557
2377.9844 | 116.2262 | -78.2822 | 37.9944 | -0.4302 | 0.022336 | -0.037119 | 34.5698 | 0.016874 | -0.032551 | 35.0877 | -0.018311 | 0.31128 | -0.43945 | 0.45319 | -19.5831 | 0.059509 | 0.10529 | 0.28381 | 15.8249 | -56.8634 | 77.8427 | -37.6831 | 78.2639 | 78.7354 | -57.5775 | 21.4188 | -22.1695 | 0.42114 | 78.3875 | 78.566 | 58.699 | 78.5934 | 78.2639 | 94.1071 | 78.3417 | 21.4188 | 78.5934 | 78.2639 | 78.3417 | 58.699 | 94.1071 | -38.4338 | -94.8578
2378.9219 | 121.8475 | -63.9725 | 57.399 | 0.058086 | 0.046902 | -0.016825 | 0.80664 | -0.066439 | -0.0069164 | 0.75639 | 0.050354 | 0.31128 | -0.39368 | 57.9849 | 32.3044 | 55.9113 | 57.5821 | 57.9391 | 57.8293 | -64.389 | 63.5788 | -57.0877 | 64.0228 | 121.9574 | -25.0946 | -0.41656 | 0.4303 | 0.44403 | 121.5546 | 121.9116 | 96.2769 | 64.2838 | 64.0228 | 121.8018 | 119.8837 | -0.41656 | 64.2838 | 64.0228 | 119.8837 | 96.2769 | 121.8018 | -57.7927 | -121.788
2379.9844 | 122.319 | -64.2563 | 57.7606 | -0.26235 | 0.0095178 | -0.034983 | 0.067503 | -0.065371 | -0.050709 | 0.050361 | 0.041199 | 0.24261 | -0.38452 | 57.9666 | 57.7515 | 57.7057 | 57.8476 | 57.9895 | 58.0032 | -64.7369 | 63.8718 | -57.518 | 64.2975 | 122.2229 | -0.009155 | -0.48065 | 0.24261 | 0.42572 | 122.1039 | 122.2458 | 122.0078 | 64.4989 | 64.2975 | 122.2595 | 121.962 | -0.48065 | 64.4989 | 64.2975 | 121.962 | 122.0078 | 122.2595 | -58.1451 | -122.4976
2380.9219 | 122.2778 | -64.2838 | 57.8888 | -0.10976 | 0.035153 | -0.040324 | 0.094205 | -0.073916 | -0.018665 | 0.041816 | 0.064087 | 0.29755 | -0.3891 | 58.2138 | 57.9208 | 57.8567 | 57.8339 | 58.1589 | 58.0215 | -64.7232 | 63.8947 | -57.5912 | 64.3478 | 122.4976 | 0.032043 | -0.43945 | 0.13275 | 0.45319 | 122.1176 | 122.4426 | 122.2046 | 64.5813 | 64.3478 | 122.3053 | 122.1405 | -0.43945 | 64.5813 | 64.3478 | 122.1405 | 122.2046 | 122.3053 | -58.2779 | -122.612
2381.9688 | 122.406 | -64.3112 | 57.8247 | -0.15554 | 0.019131 | -0.033915 | 0.076048 | -0.07712 | -0.034687 | 0.064246 | 0.004578 | 0.24719 | -0.35248 | 58.0124 | 57.4631 | 57.7652 | 57.9163 | 58.0307 | 58.0261 | -64.7644 | 63.9587 | -57.5775 | 64.3158 | 122.3236 | -0.36163 | -0.45319 | 0.20142 | 0.35706 | 122.2275 | 122.3419 | 121.7743 | 64.5584 | 64.3158 | 122.3373 | 122.0764 | -0.45319 | 64.5584 | 64.3158 | 122.0764 | 121.7743 | 122.3373 | -58.1772 | -122.5891
2382.9219 | 122.3785 | -64.3662 | 57.8613 | -0.21657 | 0.045834 | -0.029642 | 0.10168 | -0.079257 | -0.012257 | 0.042884 | 0.045776 | 0.29755 | -0.39368 | 58.2047 | 57.4905 | 57.843 | 57.811 | 58.1268 | 57.9895 | -64.8285 | 63.9725 | -57.5638 | 64.4119 | 122.5708 | -0.37079 | -0.46234 | 0.12817 | 0.43945 | 122.1771 | 122.493 | 121.8567 | 64.6637 | 64.4119 | 122.3557 | 122.2092 | -0.46234 | 64.6637 | 64.4119 | 122.2092 | 121.8567 | 122.3557 | -58.255 | -122.6898
2383.9219 | 122.4014 | -64.3524 | 57.8934 | -0.048725 | 0.040494 | -0.021098 | 0.099546 | -0.067507 | -0.019733 | 0.055701 | 0.064087 | 0.29755 | -0.38452 | 58.2504 | 57.7057 | 57.8659 | 57.8384 | 58.1726 | 58.0353 | -64.8102 | 63.9679 | -57.5958 | 64.4165 | 122.6028 | -0.18768 | -0.45776 | 0.14191 | 0.44861 | 122.1909 | 122.525 | 122.0581 | 64.65 | 64.4165 | 122.3877 | 122.2183 | -0.45776 | 64.65 | 64.4165 | 122.2183 | 122.0581 | 122.3877 | -58.2779 | -122.7036
2385.1406 | 122.4976 | -64.27 | 57.9529 | -0.12502 | 0.02554 | -0.041392 | 0.079252 | -0.078189 | -0.049641 | 0.055701 | 0.027466 | 0.25177 | -0.36163 | 58.1177 | 57.6599 | 57.8522 | 57.6828 | 58.1223 | 58.1497 | -64.7644 | 63.9084 | -57.7011 | 64.2975 | 122.3877 | -0.29297 | -0.49438 | 0.19684 | 0.3891 | 121.9528 | 122.3923 | 121.9299 | 64.5218 | 64.2975 | 122.4197 | 122.1222 | -0.49438 | 64.5218 | 64.2975 | 122.1222 | 121.9299 | 122.4197 | -58.3145 | -122.7173
2385.9219 | 122.4335 | -64.2151 | 58.0902 | -0.38442 | 0.052243 | -0.043528 | 0.10596 | -0.074984 | -0.024006 | 0.054633 | 0.050354 | 0.3067 | -0.38452 | 58.429 | 57.8613 | 58.0673 | 57.7606 | 58.342 | 58.2275 | -64.6591 | 63.8306 | -57.7835 | 64.2654 | 122.644 | -0.22888 | -0.44403 | 0.13733 | 0.43488 | 121.9757 | 122.5571 | 122.0764 | 64.5218 | 64.2654 | 122.4426 | 122.2824 | -0.44403 | 64.5218 | 64.2654 | 122.2824 | 122.0764 | 122.4426 | -58.4747 | -122.7493
2386.9219 | 122.4609 | -64.2609 | 58.0673 | -0.24709 | 0.039425 | -0.045664 | 0.096342 | -0.064303 | -0.015461 | 0.053565 | 0.036621 | 0.3067 | -0.39825 | 58.4015 | 57.8247 | 58.0582 | 57.7515 | 58.3282 | 58.2275 | -64.6683 | 63.8626 | -57.7606 | 64.2975 | 122.6624 | -0.24262 | -0.40741 | 0.16022 | 0.43488 | 122.0123 | 122.5891 | 122.0856 | 64.5676 | 64.2975 | 122.4884 | 122.319 | -0.40741 | 64.5676 | 64.2975 | 122.319 | 122.0856 | 122.4884 | -58.4656 | -122.7356
2387.9844 | 122.4518 | -64.2609 | 58.0673 | -0.44545 | 0.015927 | -0.034983 | 0.091001 | -0.078189 | -0.040028 | 0.074928 | -0.004578 | 0.2655 | -0.40741 | 58.342 | 57.1655 | 58.0444 | 57.8247 | 58.3328 | 58.2275 | -64.6683 | 63.8535 | -57.8018 | 64.2563 | 122.6028 | -0.90179 | -0.40741 | 0.16022 | 0.40283 | 122.0856 | 122.5937 | 121.4264 | 64.5264 | 64.2563 | 122.4884 | 122.3053 | -0.40741 | 64.5264 | 64.2563 | 122.3053 | 121.4264 | 122.4884 | -58.4747 | -122.7356
2388.9219 | 122.4335 | -64.2975 | 58.0765 | 0.088604 | 0.045834 | -0.0093484 | 0.12305 | -0.070712 | -0.0090524 | 0.065314 | 0.027466 | 0.29297 | -0.38452 | 58.4564 | 57.843 | 58.0673 | 57.962 | 58.3511 | 58.168 | -64.6957 | 63.913 | -57.7835 | 64.325 | 122.7539 | -0.23346 | -0.39826 | 0.091553 | 0.41199 | 122.2595 | 122.6486 | 122.1405 | 64.5905 | 64.325 | 122.4655 | 122.3648 | -0.39826 | 64.5905 | 64.325 | 122.3648 | 122.1405 | 122.4655 | -58.461 | -122.7722
2389.9844 | 122.4518 | -64.2792 | 58.1085 | -0.4302 | 0.03088 | -0.029642 | 0.10702 | -0.07712 | -0.019733 | 0.066383 | -0.032043 | 0.30212 | -0.41199 | 58.4518 | 54.0482 | 58.1223 | 57.9025 | 58.4106 | 58.2642 | -64.65 | 63.8672 | -57.8064 | 64.2471 | 122.731 | -4.0604 | -0.37079 | 0.15564 | 0.37994 | 122.1817 | 122.6898 | 118.3273 | 64.5813 | 64.2471 | 122.5433 | 122.4014 | -0.37079 | 64.5813 | 64.2471 | 122.4014 | 118.3273 | 122.5433 | -58.5205 | -122.7585
2390.9219 | 122.5021 | -64.1327 | 58.223 | -0.18605 | 0.04263 | -0.034983 | 0.11023 | -0.062167 | -0.01012 | 0.077064 | 0.059509 | 0.3067 | -0.3891 | 58.5617 | 44.8425 | 58.1863 | 58.1635 | 58.4747 | 58.342 | -64.595 | 63.7436 | -57.9163 | 64.1922 | 122.6944 | -13.3804 | -0.46234 | 0.11902 | 0.44861 | 122.2961 | 122.6074 | 108.9752 | 64.4394 | 64.1922 | 122.4747 | 122.319 | -0.46234 | 64.4394 | 64.1922 | 122.319 | 108.9752 | 122.4747 | -58.6121 | -122.818
2391.9844 | 122.4747 | -64.2471 | 58.1451 | -0.38442 | 0.02554 | -0.05955 | 0.10489 | -0.070712 | -0.028278 | 0.0792 | -0.054932 | 0.29755 | -0.41657 | 58.4839 | 52.7252 | 58.1085 | 58.0261 | 58.4473 | 58.2962 | -64.65 | 63.8306 | -57.8476 | 64.1922 | 122.731 | -5.4199 | -0.40283 | 0.15106 | 0.36163 | 122.2733 | 122.6944 | 116.9724 | 64.5447 | 64.1922 | 122.5433 | 122.3557 | -0.40283 | 64.5447 | 64.1922 | 122.3557 | 116.9724 | 122.5433 | -58.5617 | -122.7951
2392.9219 | 117.4255 | -52.8671 | 64.6362 | -0.62856 | 0.031949 | -0.034983 | 34.5698 | -0.027987 | -0.013325 | 35.0877 | 0.054932 | 0.29755 | -0.38452 | 38.2828 | 7.0084 | 7.4524 | 38.1317 | 17.5461 | 49.1501 | -37.9944 | 52.4826 | -64.3387 | 52.9221 | 91.1499 | -57.6279 | 14.8727 | -15.4861 | 0.43945 | 90.9988 | 70.4132 | 59.8755 | 53.1647 | 52.9221 | 102.0172 | 60.3195 | 14.8727 | 53.1647 | 52.9221 | 60.3195 | 59.8755 | 102.0172 | -65.0208 | -102.6306
2393.9219 | 122.1634 | -64.1281 | 57.8934 | -0.21657 | 0.037289 | -0.0072124 | 0.10809 | -0.067507 | -0.011188 | 0.05677 | 0.032043 | 0.30212 | -0.39825 | 58.2138 | 57.9895 | 57.8934 | 57.8567 | 58.1635 | 58.0856 | -64.5584 | 63.7299 | -57.5912 | 64.1602 | 122.3419 | 0.09613 | -0.4303 | 0.19226 | 0.4303 | 121.9849 | 122.2916 | 122.1176 | 64.4302 | 64.1602 | 122.2137 | 122.0215 | -0.4303 | 64.4302 | 64.1602 | 122.0215 | 122.1176 | 122.2137 | -58.2916 | -122.4518
2394.9219 | 122.2412 | -64.2014 | 57.9254 | -0.30813 | 0.039425 | -0.026438 | 0.098478 | -0.057894 | -0.024006 | 0.052497 | 0.013733 | 0.29297 | -0.42572 | 58.2413 | 57.9987 | 57.9071 | 57.8751 | 58.2138 | 58.0719 | -64.5996 | 63.7756 | -57.6324 | 64.2151 | 122.4426 | 0.073242 | -0.39825 | 0.14648 | 0.43945 | 122.0764 | 122.4152 | 122.2 | 64.4943 | 64.2151 | 122.2733 | 122.1085 | -0.39825 | 64.4943 | 64.2151 | 122.1085 | 122.2 | 122.2733 | -58.3511 | -122.525
2395.9219 | 122.2824 | -64.2288 | 57.9391 | -0.33864 | 0.034085 | -0.033915 | 0.099546 | -0.066439 | -0.018665 | 0.055701 | -0.018311 | 0.30212 | -0.41199 | 58.2733 | 57.9895 | 57.93 | 57.8613 | 58.223 | 58.0948 | -64.6271 | 63.8168 | -57.637 | 64.2105 | 122.5021 | 0.050354 | -0.39825 | 0.15564 | 0.39368 | 122.0901 | 122.4518 | 122.2183 | 64.5309 | 64.2105 | 122.3236 | 122.1588 | -0.39825 | 64.5309 | 64.2105 | 122.1588 | 122.2183 | 122.3236 | -58.3511 | -122.5662
2396.9844 | 122.2641 | -64.2426 | 57.9529 | -0.33864 | 0.041562 | -0.039256 | 0.10489 | -0.068576 | -0.029346 | 0.068519 | -0.050354 | 0.3067 | -0.42572 | 58.2596 | 58.0124 | 57.9529 | 57.8293 | 58.2413 | 58.0673 | -64.6729 | 63.8168 | -57.6462 | 64.1922 | 122.5021 | 0.059509 | -0.4303 | 0.11444 | 0.37537 | 122.0718 | 122.4838 | 122.2549 | 64.5493 | 64.1922 | 122.3099 | 122.1954 | -0.4303 | 64.5493 | 64.1922 | 122.1954 | 122.2549 | 122.3099 | -58.3786 | -122.6257
2397.9219 | 122.3328 | -64.2563 | 57.9254 | -0.26235 | 0.034085 | -0.039256 | 0.10596 | -0.07178 | -0.024006 | 0.064246 | 0.027466 | 0.32501 | -0.41657 | 58.2596 | 58.0078 | 57.9391 | 57.8979 | 58.2138 | 58.1039 | -64.6774 | 63.8397 | -57.6004 | 64.2838 | 122.5159 | 0.082397 | -0.42114 | 0.17853 | 0.44403 | 122.1542 | 122.4701 | 122.2641 | 64.5813 | 64.2838 | 122.3602 | 122.1954 | -0.42114 | 64.5813 | 64.2838 | 122.1954 | 122.2641 | 122.3602 | -58.342 | -122.6028
2398.9844 | 122.4564 | -64.2563 | 57.9163 | -0.23183 | 0.011654 | -0.037119 | 0.077116 | -0.070712 | -0.041096 | 0.064246 | 0.068665 | 0.24719 | -0.37994 | 58.1039 | 57.9071 | 57.8201 | 57.9941 | 58.0948 | 58.136 | -64.7232 | 63.8763 | -57.6691 | 64.325 | 122.3602 | -0.009156 | -0.46692 | 0.21973 | 0.44861 | 122.2504 | 122.3511 | 122.1634 | 64.5035 | 64.325 | 122.3923 | 122.0764 | -0.46692 | 64.5035 | 64.325 | 122.0764 | 122.1634 | 122.3923 | -58.2962 | -122.6395
2399.9219 | 122.3648 | -64.2746 | 57.93 | -0.033467 | 0.04797 | -0.033915 | 0.11877 | -0.070712 | -0.020801 | 0.063178 | 0.059509 | 0.29755 | -0.40283 | 58.2916 | 57.9803 | 57.8934 | 57.8751 | 58.2001 | 58.0902 | -64.7598 | 63.8718 | -57.6324 | 64.3341 | 122.5662 | 0.050354 | -0.48523 | 0.16022 | 0.46234 | 122.1497 | 122.4747 | 122.2549 | 64.5721 | 64.3341 | 122.3648 | 122.168 | -0.48523 | 64.5721 | 64.3341 | 122.168 | 122.2549 | 122.3648 | -58.3328 | -122.6898
2400.9844 | 122.3877 | -64.3021 | 57.9575 | -0.15554 | 0.036221 | -0.032847 | 0.10809 | -0.07178 | -0.026142 | 0.070655 | 0.036621 | 0.3067 | -0.40741 | 58.3054 | 57.9758 | 57.8888 | 57.8751 | 58.1955 | 58.0902 | -64.7186 | 63.8947 | -57.6508 | 64.3387 | 122.6074 | 0.018311 | -0.41656 | 0.13275 | 0.44403 | 122.1771 | 122.4976 | 122.2778 | 64.6088 | 64.3387 | 122.3923 | 122.1909 | -0.41656 | 64.6088 | 64.3387 | 122.1909 | 122.2778 | 122.3923 | -58.3649 | -122.6761
2401.9219 | 122.3648 | -64.3433 | 57.93 | -0.3539 | 0.036221 | -0.02537 | 0.1113 | -0.067507 | -0.025074 | 0.06211 | -0.022888 | 0.27924 | -0.42572 | 58.2596 | 58.0078 | 57.9346 | 57.8247 | 58.2184 | 58.0948 | -64.7415 | 63.9175 | -57.6508 | 64.3204 | 122.6028 | 0.077819 | -0.39825 | 0.16479 | 0.40283 | 122.168 | 122.5616 | 122.3511 | 64.6225 | 64.3204 | 122.4381 | 122.2778 | -0.39825 | 64.6225 | 64.3204 | 122.2778 | 122.3511 | 122.4381 | -58.3557 | -122.6715
2402.9844 | 122.4335 | -64.3524 | 57.9025 | -0.0029495 | 0.031949 | -0.017893 | 0.1113 | -0.064303 | -0.014393 | 0.068519 | 0.032043 | 0.29755 | -0.39825 | 58.2504 | 57.9849 | 57.8796 | 57.8339 | 58.1497 | 58.0673 | -64.7873 | 63.9542 | -57.605 | 64.3845 | 122.6028 | 0.082397 | -0.43487 | 0.16479 | 0.4303 | 122.1863 | 122.5021 | 122.3373 | 64.65 | 64.3845 | 122.4197 | 122.2321 | -0.43487 | 64.65 | 64.3845 | 122.2321 | 122.3373 | 122.4197 | -58.3008 | -122.6898
2403.9219 | 122.3602 | -64.3982 | 57.8842 | -0.44545 | 0.028744 | -0.036051 | 0.1113 | -0.068576 | -0.022938 | 0.061042 | -0.022888 | 0.3067 | -0.42114 | 58.2321 | 57.9529 | 57.8979 | 57.7332 | 58.1909 | 58.0261 | -64.8056 | 63.9771 | -57.5775 | 64.3753 | 122.6303 | 0.068665 | -0.40741 | 0.14191 | 0.39825 | 122.1313 | 122.5891 | 122.3511 | 64.7049 | 64.3753 | 122.4243 | 122.2961 | -0.40741 | 64.7049 | 64.3753 | 122.2961 | 122.3511 | 122.4243 | -58.3054 | -122.6898
2404.9844 | 122.5113 | -64.357 | 57.8751 | -0.68959 | 0.0095178 | -0.044596 | 0.069639 | -0.072848 | -0.040028 | 0.074928 | 0.004578 | 0.23804 | -0.36621 | 58.0078 | 57.7927 | 57.7515 | 57.9391 | 58.017 | 58.0856 | -64.8331 | 63.9908 | -57.637 | 64.3616 | 122.3648 | -0.082397 | -0.47607 | 0.21057 | 0.37079 | 122.2961 | 122.374 | 122.1497 | 64.595 | 64.3616 | 122.4426 | 122.1085 | -0.47607 | 64.595 | 64.3616 | 122.1085 | 122.1497 | 122.4426 | -58.2413 | -122.7081
2405.9219 | 122.4106 | -64.3753 | 57.9208 | -0.32338 | 0.03088 | -0.034983 | 0.1145 | -0.067507 | -0.031483 | 0.065314 | -0.009155 | 0.31128 | -0.40283 | 58.2642 | 57.9575 | 57.8796 | 57.8156 | 58.1909 | 58.0582 | -64.801 | 63.9725 | -57.6096 | 64.3661 | 122.6395 | 0.036621 | -0.42572 | 0.13733 | 0.39368 | 122.1909 | 122.5662 | 122.3328 | 64.6866 | 64.3661 | 122.4335 | 122.2549 | -0.42572 | 64.6866 | 64.3661 | 122.2549 | 122.3328 | 122.4335 | -58.3237 | -122.7219
2406.9844 | 122.5296 | -64.4165 | 57.8613 | -0.26235 | 0.014859 | -0.062754 | 0.087797 | -0.07712 | -0.029346 | 0.065314 | 0.064087 | 0.24719 | -0.40741 | 58.0444 | 57.8064 | 57.7103 | 57.8796 | 58.0124 | 58.0582 | -64.8697 | 64.0091 | -57.6141 | 64.4806 | 122.4609 | -0.054932 | -0.45319 | 0.19684 | 0.4715 | 122.2961 | 122.4289 | 122.2229 | 64.6637 | 64.4806 | 122.4747 | 122.1268 | -0.45319 | 64.6637 | 64.4806 | 122.1268 | 122.2229 | 122.4747 | -58.2687 | -122.731
2407.9219 | 122.525 | -64.4028 | 57.8384 | 0.348 | 0.028744 | -0.038187 | 0.11023 | -0.07178 | -0.02187 | 0.052497 | 0.068665 | 0.26093 | -0.38452 | 58.0811 | 57.7881 | 57.692 | 57.8567 | 58.0032 | 58.0444 | -64.8926 | 64.0182 | -57.5775 | 64.4714 | 122.4838 | -0.050354 | -0.48981 | 0.20599 | 0.45319 | 122.2595 | 122.406 | 122.1909 | 64.6637 | 64.4714 | 122.4472 | 122.0947 | -0.48981 | 64.6637 | 64.4714 | 122.0947 | 122.1909 | 122.4472 | -58.223 | -122.731
2408.9844 | 122.5433 | -64.4165 | 57.8567 | -0.1708 | 0.022336 | -0.055277 | 0.081388 | -0.070712 | -0.042164 | 0.067451 | 0.050354 | 0.24719 | -0.38452 | 58.0307 | 57.7744 | 57.6965 | 57.8751 | 58.0215 | 58.0627 | -64.8697 | 64.032 | -57.6096 | 64.4669 | 122.4472 | -0.082397 | -0.45319 | 0.20599 | 0.43488 | 122.2916 | 122.438 | 122.1909 | 64.6637 | 64.4669 | 122.4792 | 122.113 | -0.45319 | 64.6637 | 64.4669 | 122.113 | 122.1909 | 122.4792 | -58.2413 | -122.7264
2409.9219 | 122.4106 | -64.4257 | 57.9346 | -0.36916 | 0.033017 | -0.0478 | 0.10916 | -0.084597 | -0.033619 | 0.059974 | -0.022888 | 0.31128 | -0.4303 | 58.2779 | 57.9483 | 57.8934 | 57.7606 | 58.2047 | 58.0582 | -64.8285 | 63.9954 | -57.6233 | 64.4028 | 122.7036 | 0.013733 | -0.40283 | 0.1236 | 0.40741 | 122.1863 | 122.6303 | 122.374 | 64.7369 | 64.4028 | 122.4838 | 122.319 | -0.40283 | 64.7369 | 64.4028 | 122.319 | 122.374 | 122.4838 | -58.3649 | -122.7631
2410.9844 | 122.525 | -64.4165 | 57.8888 | -0.079243 | 0.016995 | -0.043528 | 0.089933 | -0.070712 | -0.042164 | 0.071723 | -0.018311 | 0.25177 | -0.37994 | 58.0856 | 57.8339 | 57.7606 | 57.8979 | 58.0765 | 58.0765 | -64.8468 | 64.0366 | -57.637 | 64.3982 | 122.5021 | -0.054932 | -0.4303 | 0.18768 | 0.36163 | 122.3145 | 122.493 | 122.2504 | 64.6683 | 64.3982 | 122.493 | 122.1771 | -0.4303 | 64.6683 | 64.3982 | 122.1771 | 122.2504 | 122.493 | -58.2687 | -122.7356
2411.9219 | 122.4518 | -64.4119 | 57.9483 | -0.36916 | 0.036221 | -0.022166 | 0.11557 | -0.073916 | -0.026142 | 0.064246 | 0.009155 | 0.31128 | -0.42572 | 58.3237 | 57.9712 | 57.9025 | 57.811 | 58.223 | 58.0719 | -64.8148 | 63.9862 | -57.637 | 64.4211 | 122.7356 | 0.022888 | -0.40283 | 0.1236 | 0.43488 | 122.2229 | 122.6349 | 122.3831 | 64.7232 | 64.4211 | 122.4838 | 122.3145 | -0.40283 | 64.7232 | 64.4211 | 122.3145 | 122.3831 | 122.4838 | -58.374 | -122.7631
2412.9844 | 122.5571 | -64.3066 | 58.0078 | -0.39968 | 0.027676 | -0.056345 | 0.098478 | -0.080325 | -0.025074 | 0.066383 | 0.041199 | 0.25635 | -0.3891 | 58.2367 | 57.9346 | 57.8659 | 57.9803 | 58.2138 | 58.2047 | -64.7598 | 63.9175 | -57.7515 | 64.3478 | 122.5433 | -0.073242 | -0.45319 | 0.19684 | 0.4303 | 122.287 | 122.5204 | 122.2412 | 64.563 | 64.3478 | 122.5113 | 122.1725 | -0.45319 | 64.563 | 64.3478 | 122.1725 | 122.2412 | 122.5113 | -58.3969 | -122.7676
2413.9219 | 118.7622 | -59.2255 | 59.1888 | -0.36916 | 0.027676 | -0.049937 | 34.5698 | -0.041873 | -0.014393 | 35.0877 | -0.036621 | 0.30212 | -0.47607 | 37.0285 | -15.3625 | 34.4055 | 36.525 | 7.2372 | 46.0052 | -46.4584 | 58.7494 | -58.8867 | 59.1888 | 96.254 | -74.5514 | 12.767 | -13.1836 | 0.43945 | 95.7504 | 66.4627 | 43.8629 | 59.5276 | 59.1888 | 105.2307 | 93.631 | 12.767 | 59.5276 | 59.1888 | 93.631 | 43.8629 | 105.2307 | -59.6649 | -105.6473
2414.9844 | 122.0718 | -64.1602 | 57.6874 | 0.088604 | 0.02554 | -0.04246 | 0.073911 | -0.067507 | -0.038959 | 0.054633 | -0.018311 | 0.26093 | -0.37079 | 57.8842 | 57.5912 | 57.6141 | 57.6965 | 57.8064 | 57.8751 | -64.5996 | 63.7894 | -57.4265 | 64.1418 | 122.0444 | -0.09613 | -0.43945 | 0.18768 | 0.35248 | 121.8567 | 121.9666 | 121.7514 | 64.4211 | 64.1418 | 122.0352 | 121.7743 | -0.43945 | 64.4211 | 64.1418 | 121.7743 | 121.7514 | 122.0352 | -58.0582 | -122.287
2415.9219 | 122.113 | -64.2151 | 57.7835 | -0.10976 | 0.039425 | -0.038187 | 0.10489 | -0.073916 | -0.02187 | 0.048225 | 0.054932 | 0.27924 | -0.41657 | 58.1268 | 57.6508 | 57.7515 | 57.7103 | 57.8476 | 57.93 | -64.5996 | 63.7985 | -57.5043 | 64.27 | 122.3419 | -0.13275 | -0.38452 | 0.14649 | 0.4715 | 121.9254 | 122.0627 | 121.8658 | 64.4943 | 64.27 | 122.1451 | 121.9666 | -0.38452 | 64.4943 | 64.27 | 121.9666 | 121.8658 | 122.1451 | -58.2001 | -122.3831
2416.9688 | 122.2687 | -64.2197 | 57.7515 | 0.37852 | 0.031949 | -0.048869 | 0.089933 | -0.079257 | -0.040028 | 0.051429 | 0.059509 | 0.24719 | -0.37994 | 57.9987 | 57.6782 | 57.6553 | 57.8384 | 57.8384 | 57.9666 | -64.6866 | 63.8397 | -57.5043 | 64.2792 | 122.2183 | -0.073242 | -0.46692 | 0.21515 | 0.43945 | 122.0581 | 122.0581 | 121.8979 | 64.4669 | 64.2792 | 122.1863 | 121.875 | -0.46692 | 64.4669 | 64.2792 | 121.875 | 121.8979 | 122.1863 | -58.1314 | -122.438
2417.9219 | 122.1817 | -64.2975 | 57.7606 | 0.37852 | 0.036221 | -0.037119 | 0.1113 | -0.070712 | -0.022938 | 0.047157 | 0 | 0.29755 | -0.41657 | 58.1451 | 57.8156 | 57.756 | 57.724 | 57.9987 | 57.8888 | -64.6912 | 63.8809 | -57.4631 | 64.2975 | 122.4426 | 0.054932 | -0.39368 | 0.12817 | 0.41657 | 122.0215 | 122.2961 | 122.113 | 64.595 | 64.2975 | 122.1863 | 122.0535 | -0.39368 | 64.595 | 64.2975 | 122.0535 | 122.113 | 122.1863 | -58.1772 | -122.4518
2418.9844 | 122.1863 | -64.3066 | 57.8247 | -0.33864 | 0.024472 | -0.032847 | 0.10061 | -0.072848 | -0.02721 | 0.052497 | -0.032043 | 0.30212 | -0.4303 | 58.1818 | 57.8705 | 57.8156 | 57.692 | 58.0856 | 57.9437 | -64.7003 | 63.8763 | -57.5226 | 64.2746 | 122.4884 | 0.045776 | -0.39368 | 0.11902 | 0.39826 | 121.9986 | 122.3923 | 122.1771 | 64.6088 | 64.2746 | 122.2504 | 122.1222 | -0.39368 | 64.6088 | 64.2746 | 122.1222 | 122.1771 | 122.2504 | -58.255 | -122.525
2419.9219 | 122.2046 | -64.3021 | 57.8384 | -0.55227 | 0.029812 | -0.024302 | 0.095274 | -0.069644 | -0.031483 | 0.053565 | -0.045776 | 0.3067 | -0.43488 | 58.1818 | 57.8842 | 57.8567 | 57.7057 | 58.1039 | 57.9803 | -64.6683 | 63.8672 | -57.5317 | 64.2563 | 122.4838 | 0.045776 | -0.36621 | 0.14191 | 0.3891 | 122.0078 | 122.406 | 122.1863 | 64.6088 | 64.2563 | 122.2824 | 122.1588 | -0.36621 | 64.6088 | 64.2563 | 122.1588 | 122.1863 | 122.2824 | -58.2733 | -122.5067
2420.9844 | 122.3511 | -64.27 | 57.8293 | -0.033467 | 0.019131 | -0.011485 | 0.083524 | -0.081393 | -0.051777 | 0.063178 | 0.013733 | 0.26093 | -0.37079 | 58.0307 | 57.7515 | 57.7286 | 57.8979 | 57.9849 | 58.0261 | -64.7003 | 63.8992 | -57.5684 | 64.2838 | 122.3007 | -0.07782 | -0.4303 | 0.19684 | 0.38452 | 122.168 | 122.2549 | 122.0215 | 64.5309 | 64.2838 | 122.2961 | 121.9986 | -0.4303 | 64.5309 | 64.2838 | 121.9986 | 122.0215 | 122.2961 | -58.2001 | -122.5296
2421.9219 | 122.2733 | -64.3295 | 57.8522 | -0.30813 | 0.028744 | -0.048869 | 0.098478 | -0.067507 | -0.033619 | 0.055701 | -0.013733 | 0.2655 | -0.41657 | 58.1497 | 57.8979 | 57.843 | 57.7377 | 58.0994 | 57.9849 | -64.7095 | 63.913 | -57.5867 | 64.3158 | 122.4792 | 0.045776 | -0.37994 | 0.13275 | 0.40283 | 122.0673 | 122.4289 | 122.2275 | 64.595 | 64.3158 | 122.3145 | 122.1725 | -0.37994 | 64.595 | 64.3158 | 122.1725 | 122.2275 | 122.3145 | -58.2687 | -122.5616
2422.9844 | 122.3511 | -64.2197 | 57.8888 | -0.033467 | 0.020199 | -0.0478 | 0.083524 | -0.078189 | -0.0443 | 0.055701 | 0 | 0.2655 | -0.37537 | 58.1451 | 57.8567 | 57.8339 | 57.9437 | 58.0536 | 58.1177 | -64.6454 | 63.8443 | -57.6233 | 64.2197 | 122.3648 | -0.032044 | -0.42572 | 0.22888 | 0.37537 | 122.1634 | 122.2733 | 122.0764 | 64.4852 | 64.2197 | 122.3373 | 122.0535 | -0.42572 | 64.4852 | 64.2197 | 122.0535 | 122.0764 | 122.3373 | -58.2642 | -122.5342
2423.9219 | 122.3373 | -64.2059 | 57.9437 | -0.46071 | 0.023404 | -0.058482 | 0.095274 | -0.081393 | -0.034687 | 0.061042 | 0.036621 | 0.27924 | -0.3891 | 58.2092 | 57.9346 | 57.8705 | 57.9208 | 58.1451 | 58.1223 | -64.6591 | 63.8168 | -57.6645 | 64.2426 | 122.4152 | -0.009156 | -0.45319 | 0.17853 | 0.42572 | 122.1268 | 122.3511 | 122.1405 | 64.4852 | 64.2426 | 122.3282 | 122.0764 | -0.45319 | 64.4852 | 64.2426 | 122.0764 | 122.1405 | 122.3282 | -58.3328 | -122.6028
2424.9844 | 122.3373 | -64.2654 | 57.8613 | 0.21067 | 0.021267 | -0.0478 | 0.093137 | -0.092074 | -0.041096 | 0.066383 | -0.009155 | 0.24719 | -0.39368 | 58.1039 | 57.8567 | 57.811 | 57.8979 | 58.0444 | 58.0673 | -64.7186 | 63.8718 | -57.6141 | 64.2563 | 122.3694 | -0.004578 | -0.45319 | 0.20599 | 0.38452 | 122.1634 | 122.3099 | 122.1222 | 64.5126 | 64.2563 | 122.3328 | 122.0764 | -0.45319 | 64.5126 | 64.2563 | 122.0764 | 122.1222 | 122.3328 | -58.255 | -122.58
2425.9219 | 122.3602 | -64.2792 | 57.9163 | -0.4302 | 0.012723 | -0.054209 | 0.10489 | -0.081393 | -0.049641 | 0.059974 | 0.022888 | 0.26093 | -0.40741 | 58.1863 | 57.8476 | 57.8659 | 57.8339 | 58.0902 | 58.0582 | -64.7003 | 63.8718 | -57.6553 | 64.3021 | 122.4655 | -0.068665 | -0.42114 | 0.14191 | 0.4303 | 122.113 | 122.3694 | 122.1268 | 64.5401 | 64.3021 | 122.3373 | 122.1451 | -0.42114 | 64.5401 | 64.3021 | 122.1451 | 122.1268 | 122.3373 | -58.3237 | -122.6166
2426.9844 | 122.3648 | -64.4073 | 57.7515 | 0.48533 | 0.028744 | -0.030711 | 0.10489 | -0.086733 | -0.026142 | 0.051429 | 0.027466 | 0.2655 | -0.3891 | 58.0719 | 57.7744 | 57.7011 | 57.8201 | 57.9849 | 57.9575 | -64.8514 | 64.0182 | -57.486 | 64.4348 | 122.4792 | 0.022888 | -0.44403 | 0.20599 | 0.41656 | 122.2275 | 122.3923 | 122.1817 | 64.6729 | 64.4348 | 122.3648 | 122.1085 | -0.44403 | 64.6729 | 64.4348 | 122.1085 | 122.1817 | 122.3648 | -58.1406 | -122.6028
2427.9219 | 122.3282 | -64.4714 | 57.7789 | -0.44545 | 0.027676 | -0.048869 | 0.093137 | -0.079257 | -0.032551 | 0.052497 | 0 | 0.27008 | -0.41199 | 58.0811 | 57.8156 | 57.7423 | 57.692 | 58.0078 | 57.8796 | -64.8651 | 64.0594 | -57.5089 | 64.4714 | 122.5525 | 0.036621 | -0.39368 | 0.10071 | 0.41199 | 122.1634 | 122.4792 | 122.287 | 64.7415 | 64.4714 | 122.3511 | 122.2137 | -0.39368 | 64.7415 | 64.4714 | 122.2137 | 122.287 | 122.3511 | -58.1909 | -122.644
2428.9844 | 122.081 | -64.3158 | 57.4722 | 0.47007 | 0.037289 | -0.046732 | 0.099546 | -0.07178 | -0.019733 | 0.054633 | 0.07782 | 0.25635 | -0.37079 | 57.6828 | 57.1106 | 57.3624 | 57.5409 | 57.2983 | 57.6416 | -64.8239 | 63.945 | -57.2159 | 64.3936 | 121.9986 | -0.36163 | -0.50812 | 0.16937 | 0.44861 | 121.8567 | 121.6141 | 121.4264 | 64.5721 | 64.3936 | 121.9574 | 121.6782 | -0.50812 | 64.5721 | 64.3936 | 121.6782 | 121.4264 | 121.9574 | -57.843 | -122.2961
2429.9219 | 122.2504 | -64.444 | 57.7057 | -0.32338 | 0.023404 | -0.027506 | 0.09741 | -0.067507 | -0.031483 | 0.066383 | -0.022888 | 0.28381 | -0.42114 | 58.0582 | 57.5409 | 57.692 | 57.5546 | 57.7194 | 57.8339 | -64.8239 | 64.0228 | -57.4219 | 64.4211 | 122.5021 | -0.16479 | -0.37994 | 0.12817 | 0.39825 | 121.9986 | 122.1634 | 121.9849 | 64.7278 | 64.4211 | 122.2778 | 122.1359 | -0.37994 | 64.7278 | 64.4211 | 122.1359 | 121.9849 | 122.2778 | -58.1268 | -122.5296
2430.9844 | 122.4197 | -64.4714 | 57.6279 | -0.048725 | 0.020199 | -0.049937 | 0.083524 | -0.082461 | -0.051777 | 0.063178 | 0.032043 | 0.25177 | -0.39368 | 57.8384 | 57.3853 | 57.5592 | 57.7332 | 57.605 | 57.8567 | -64.9246 | 64.0778 | -57.3761 | 64.5035 | 122.3099 | -0.24261 | -0.45319 | 0.22888 | 0.42572 | 122.2046 | 122.0764 | 121.8567 | 64.7232 | 64.5035 | 122.3282 | 122.0306 | -0.45319 | 64.7232 | 64.5035 | 122.0306 | 121.8567 | 122.3282 | -58.0215 | -122.5525
2431.9219 | 122.4243 | -64.4623 | 57.6599 | -0.30813 | 0.014859 | -0.054209 | 0.096342 | -0.080325 | -0.030414 | 0.063178 | 0.045776 | 0.2655 | -0.3891 | 57.8888 | 57.3761 | 57.5638 | 57.6965 | 57.5912 | 57.8613 | -64.9292 | 64.0732 | -57.3944 | 64.5081 | 122.3511 | -0.28381 | -0.46692 | 0.20142 | 0.43487 | 122.1588 | 122.0535 | 121.8384 | 64.7278 | 64.5081 | 122.3236 | 122.0261 | -0.46692 | 64.7278 | 64.5081 | 122.0261 | 121.8384 | 122.3236 | -58.049 | -122.5891
2432.9844 | 122.4152 | -64.5081 | 57.6508 | 0.51585 | 0.041562 | -0.033915 | 0.1145 | -0.080325 | -0.020801 | 0.054633 | 0.032043 | 0.28839 | -0.42572 | 57.9803 | 57.2937 | 57.5775 | 57.6736 | 57.4585 | 57.8247 | -64.9796 | 64.0823 | -57.3624 | 64.5401 | 122.4884 | -0.35706 | -0.4715 | 0.17395 | 0.45776 | 122.1817 | 121.9666 | 121.8018 | 64.7964 | 64.5401 | 122.3328 | 122.0856 | -0.4715 | 64.7964 | 64.5401 | 122.0856 | 121.8018 | 122.3328 | -58.0765 | -122.6303
2433.9219 | 122.4335 | -64.5218 | 57.6599 | -0.29287 | 0.028744 | -0.04246 | 0.089933 | -0.083529 | -0.036823 | 0.070655 | 0.018311 | 0.25635 | -0.40741 | 57.8934 | 57.3944 | 57.5775 | 57.6828 | 57.6004 | 57.8567 | -64.9567 | 64.1144 | -57.4036 | 64.5401 | 122.4152 | -0.2655 | -0.43488 | 0.19684 | 0.42572 | 122.2046 | 122.1222 | 121.9162 | 64.7781 | 64.5401 | 122.3785 | 122.0993 | -0.43488 | 64.7781 | 64.5401 | 122.0993 | 121.9162 | 122.3785 | -58.0673 | -122.6166
2434.9844 | 122.4472 | -64.5584 | 57.6096 | 0.66844 | 0.035153 | -0.040324 | 0.10275 | -0.079257 | -0.037891 | 0.055701 | 0.059509 | 0.24719 | -0.36621 | 57.8796 | 57.3349 | 57.518 | 57.6828 | 57.5134 | 57.8018 | -65.0253 | 64.1922 | -57.3624 | 64.6179 | 122.4381 | -0.27466 | -0.46692 | 0.19226 | 0.42572 | 122.2412 | 122.0718 | 121.8933 | 64.8056 | 64.6179 | 122.3602 | 122.0764 | -0.46692 | 64.8056 | 64.6179 | 122.0764 | 121.8933 | 122.3602 | -57.9758 | -122.6349
2435.9219 | 122.4701 | -64.5584 | 57.6279 | -0.38442 | 0.018063 | -0.048869 | 0.093137 | -0.093142 | -0.031483 | 0.061042 | 0.032043 | 0.23346 | -0.39825 | 57.8613 | 57.1472 | 57.5409 | 57.7103 | 57.3486 | 57.8384 | -65.0162 | 64.1602 | -57.3944 | 64.5905 | 122.4197 | -0.48065 | -0.45776 | 0.21057 | 0.4303 | 122.2687 | 121.907 | 121.7056 | 64.7919 | 64.5905 | 122.3969 | 122.0993 | -0.45776 | 64.7919 | 64.5905 | 122.0993 | 121.7056 | 122.3969 | -58.0261 | -122.644
2436.9844 | 122.4518 | -64.5813 | 57.5912 | 0.47007 | 0.026608 | -0.032847 | 0.096342 | -0.091006 | -0.031483 | 0.068519 | 0.064087 | 0.24719 | -0.36163 | 57.8567 | 57.2983 | 57.4768 | 57.6645 | 57.4585 | 57.7698 | -65.0665 | 64.2197 | -57.3441 | 64.6454 | 122.438 | -0.29297 | -0.48523 | 0.17853 | 0.42572 | 122.2458 | 122.0398 | 121.8796 | 64.8285 | 64.6454 | 122.3511 | 122.0581 | -0.48523 | 64.8285 | 64.6454 | 122.0581 | 121.8796 | 122.3511 | -57.9529 | -122.6578
2437.9219 | 122.4747 | -64.6317 | 57.5638 | -0.048725 | 0.026608 | -0.026438 | 0.093137 | -0.081393 | -0.053913 | 0.066383 | 0 | 0.24261 | -0.3891 | 57.7972 | 57.2754 | 57.486 | 57.6508 | 57.4539 | 57.7972 | -65.0665 | 64.2426 | -57.3212 | 64.6317 | 122.4289 | -0.28839 | -0.43488 | 0.23346 | 0.3891 | 122.2824 | 122.0856 | 121.907 | 64.8743 | 64.6317 | 122.4289 | 122.1176 | -0.43488 | 64.8743 | 64.6317 | 122.1176 | 121.907 | 122.4289 | -57.9529 | -122.6303
2438.9844 | 122.4792 | -64.6408 | 57.5729 | 0.48533 | 0.026608 | -0.027506 | 0.11557 | -0.078189 | -0.026142 | 0.052497 | 0.082397 | 0.2655 | -0.36163 | 57.8201 | 57.2525 | 57.4402 | 57.6553 | 57.4173 | 57.7469 | -65.1123 | 64.2792 | -57.3074 | 64.7232 | 122.4609 | -0.32044 | -0.4715 | 0.17395 | 0.44403 | 122.2961 | 122.0581 | 121.8933 | 64.9063 | 64.7232 | 122.3877 | 122.081 | -0.4715 | 64.9063 | 64.7232 | 122.081 | 121.8933 | 122.3877 | -57.9346 | -122.6852
2439.9219 | 122.4884 | -64.6362 | 57.5592 | -0.15554 | 0.028744 | -0.049937 | 0.098478 | -0.074984 | -0.049641 | 0.067451 | 0.022888 | 0.27008 | -0.36163 | 57.8018 | 57.2983 | 57.4905 | 57.6736 | 57.4951 | 57.7789 | -65.062 | 64.2746 | -57.2891 | 64.6591 | 122.438 | -0.26093 | -0.42572 | 0.21973 | 0.38452 | 122.3099 | 122.1313 | 121.9345 | 64.9063 | 64.6591 | 122.4152 | 122.1268 | -0.42572 | 64.9063 | 64.6591 | 122.1268 | 121.9345 | 122.4152 | -57.9208 | -122.6212
2440.9844 | 122.4701 | -64.6866 | 57.5455 | 0.24119 | 0.024472 | -0.045664 | 0.095274 | -0.096347 | -0.036823 | 0.064246 | 0.022888 | 0.25635 | -0.38452 | 57.8247 | 57.2754 | 57.4905 | 57.5958 | 57.4631 | 57.7332 | -65.1077 | 64.3021 | -57.2891 | 64.7095 | 122.5113 | -0.27008 | -0.42114 | 0.18768 | 0.40741 | 122.2824 | 122.1497 | 121.962 | 64.9429 | 64.7095 | 122.4197 | 122.1771 | -0.42114 | 64.9429 | 64.7095 | 122.1771 | 121.962 | 122.4197 | -57.93 | -122.6532
2441.9219 | 122.5204 | -64.6637 | 57.5592 | -0.094502 | 0.027676 | -0.044596 | 0.096342 | -0.084597 | -0.048572 | 0.061042 | 0.013733 | 0.23804 | -0.37537 | 57.7881 | 57.1976 | 57.4677 | 57.6187 | 57.4173 | 57.7515 | -65.1215 | 64.2883 | -57.3212 | 64.6774 | 122.4518 | -0.36163 | -0.45776 | 0.19226 | 0.3891 | 122.2824 | 122.081 | 121.8613 | 64.9017 | 64.6774 | 122.4152 | 122.1313 | -0.45776 | 64.9017 | 64.6774 | 122.1313 | 121.8613 | 122.4152 | -57.9346 | -122.6807
2442.9844 | 122.4518 | -64.7049 | 57.55 | 0.40904 | 0.033017 | -0.033915 | 0.12411 | -0.072848 | -0.029346 | 0.05677 | 0 | 0.28839 | -0.40283 | 57.9575 | 57.28 | 57.55 | 57.5317 | 57.4631 | 57.724 | -65.1443 | 64.3021 | -57.2617 | 64.7049 | 122.6624 | -0.27008 | -0.43945 | 0.17395 | 0.40283 | 122.2366 | 122.168 | 121.9849 | 64.9933 | 64.7049 | 122.4289 | 122.2549 | -0.43945 | 64.9933 | 64.7049 | 122.2549 | 121.9849 | 122.4289 | -57.9529 | -122.6944
2443.9219 | 122.5479 | -64.563 | 57.6691 | -0.10976 | 0.021267 | -0.032847 | 0.089933 | -0.081393 | -0.034687 | 0.06211 | 0.041199 | 0.25635 | -0.37537 | 57.8705 | 57.2845 | 57.5684 | 57.7469 | 57.4402 | 57.8751 | -65.0436 | 64.1876 | -57.4127 | 64.6042 | 122.4335 | -0.38452 | -0.48065 | 0.20599 | 0.41656 | 122.3099 | 122.0032 | 121.8475 | 64.8193 | 64.6042 | 122.438 | 122.1313 | -0.48065 | 64.8193 | 64.6042 | 122.1313 | 121.8475 | 122.438 | -58.0444 | -122.7127
2444.9844 | 122.4884 | -64.6088 | 57.6691 | 0.59214 | 0.039425 | -0.034983 | 0.11023 | -0.085665 | -0.017597 | 0.067451 | 0.027466 | 0.28839 | -0.3891 | 57.9849 | 57.2662 | 57.5775 | 57.6599 | 57.4265 | 57.7972 | -65.0528 | 64.2197 | -57.3807 | 64.6362 | 122.5937 | -0.40283 | -0.44403 | 0.12817 | 0.41656 | 122.2687 | 122.0352 | 121.875 | 64.8972 | 64.6362 | 122.406 | 122.1863 | -0.44403 | 64.8972 | 64.6362 | 122.1863 | 121.875 | 122.406 | -58.0582 | -122.7219
2445.9219 | 122.5296 | -64.6408 | 57.605 | -0.094502 | 0.0084498 | -0.032847 | 0.10916 | -0.084597 | -0.046436 | 0.061042 | 0.009155 | 0.26093 | -0.37537 | 57.8201 | 57.312 | 57.5363 | 57.7011 | 57.5272 | 57.8156 | -65.0803 | 64.2654 | -57.3441 | 64.65 | 122.4609 | -0.29297 | -0.43945 | 0.21057 | 0.38452 | 122.3419 | 122.168 | 121.9528 | 64.9017 | 64.65 | 122.4564 | 122.1771 | -0.43945 | 64.9017 | 64.65 | 122.1771 | 121.9528 | 122.4564 | -57.9803 | -122.6852
2446.9844 | 122.5342 | -64.6179 | 57.6187 | 0.43956 | 0.029812 | -0.045664 | 0.10809 | -0.086733 | -0.025074 | 0.072791 | 0.064087 | 0.29755 | -0.37079 | 57.8934 | 57.2708 | 57.518 | 57.7286 | 57.518 | 57.7972 | -65.1077 | 64.2471 | -57.3212 | 64.682 | 122.5113 | -0.3479 | -0.48981 | 0.17853 | 0.43488 | 122.3465 | 122.1359 | 121.8887 | 64.9155 | 64.682 | 122.4152 | 122.1359 | -0.48981 | 64.9155 | 64.682 | 122.1359 | 121.8887 | 122.4152 | -57.9895 | -122.7264
2447.9219 | 122.525 | -64.6225 | 57.6508 | -0.0029495 | 0.014859 | -0.055277 | 0.095274 | -0.086733 | -0.051777 | 0.058906 | 0 | 0.25177 | -0.37079 | 57.8567 | 57.3624 | 57.5684 | 57.6782 | 57.5409 | 57.8384 | -65.062 | 64.2517 | -57.399 | 64.6225 | 122.4792 | -0.28839 | -0.43945 | 0.18768 | 0.37079 | 122.3007 | 122.1634 | 121.9849 | 64.8743 | 64.6225 | 122.4609 | 122.1909 | -0.43945 | 64.8743 | 64.6225 | 122.1909 | 121.9849 | 122.4609 | -58.0215 | -122.7127
2448.9844 | 122.5708 | -64.6545 | 57.605 | 0.18016 | 0.029812 | -0.028574 | 0.10489 | -0.085665 | -0.031483 | 0.055701 | 0.07782 | 0.24719 | -0.37079 | 57.8934 | 57.3257 | 57.5409 | 57.7148 | 57.5043 | 57.7927 | -65.1077 | 64.2838 | -57.3578 | 64.7324 | 122.5479 | -0.27923 | -0.45319 | 0.18768 | 0.44861 | 122.3694 | 122.1588 | 121.9803 | 64.9017 | 64.7324 | 122.4472 | 122.1954 | -0.45319 | 64.9017 | 64.7324 | 122.1954 | 121.9803 | 122.4472 | -57.9758 | -122.7127
2449.9219 | 122.5204 | -64.7003 | 57.5912 | 0.11912 | 0.015927 | -0.060618 | 0.098478 | -0.081393 | -0.041096 | 0.072791 | -0.013733 | 0.25177 | -0.37537 | 57.8293 | 57.0511 | 57.5455 | 57.6004 | 57.2571 | 57.7469 | -65.1352 | 64.325 | -57.3395 | 64.6866 | 122.5296 | -0.54016 | -0.43488 | 0.15564 | 0.36163 | 122.3007 | 121.9574 | 121.7514 | 64.9521 | 64.6866 | 122.4472 | 122.2458 | -0.43488 | 64.9521 | 64.6866 | 122.2458 | 121.7514 | 122.4472 | -57.9666 | -122.7264
2450.9844 | 122.5754 | -64.6729 | 57.5775 | 0.51585 | 0.031949 | -0.021098 | 0.11236 | -0.08887 | -0.020801 | 0.070655 | 0.073242 | 0.24719 | -0.37537 | 57.8613 | 57.0236 | 57.486 | 57.692 | 57.1838 | 57.7744 | -65.1535 | 64.2975 | -57.3303 | 64.7461 | 122.5342 | -0.55389 | -0.48065 | 0.19684 | 0.44861 | 122.3648 | 121.8567 | 121.6965 | 64.92 | 64.7461 | 122.4472 | 122.1588 | -0.48065 | 64.92 | 64.7461 | 122.1588 | 121.6965 | 122.4472 | -57.9529 | -122.731
2451.9219 | 122.5113 | -64.7095 | 57.605 | 0.10386 | 0.016995 | -0.02537 | 0.098478 | -0.087802 | -0.046436 | 0.06211 | -0.013733 | 0.25635 | -0.39368 | 57.8247 | 57.225 | 57.5317 | 57.6141 | 57.4173 | 57.7652 | -65.1443 | 64.3158 | -57.3486 | 64.6957 | 122.5342 | -0.37994 | -0.43487 | 0.16022 | 0.37994 | 122.3236 | 122.1268 | 121.9345 | 64.9658 | 64.6957 | 122.4747 | 122.2412 | -0.43487 | 64.9658 | 64.6957 | 122.2412 | 121.9345 | 122.4747 | -57.9987 | -122.7493
2452.9844 | 122.4976 | -64.769 | 57.5958 | 0.39378 | 0.035153 | -0.029642 | 0.11877 | -0.085665 | -0.028278 | 0.065314 | 0.004578 | 0.30212 | -0.40741 | 57.9437 | 57.2433 | 57.5684 | 57.5684 | 57.4173 | 57.7194 | -65.1764 | 64.3616 | -57.2937 | 64.7736 | 122.7127 | -0.35248 | -0.40741 | 0.1236 | 0.41199 | 122.3373 | 122.1863 | 122.0123 | 65.0711 | 64.7736 | 122.4884 | 122.3373 | -0.40741 | 65.0711 | 64.7736 | 122.3373 | 122.0123 | 122.4884 | -58.0032 | -122.7722
2453.9219 | 122.5433 | -64.7278 | 57.5638 | 0.027569 | 0.03088 | -0.049937 | 0.096342 | -0.083529 | -0.049641 | 0.070655 | -0.018311 | 0.27008 | -0.38452 | 57.8018 | 57.1335 | 57.5089 | 57.6279 | 57.3441 | 57.7652 | -65.1489 | 64.3433 | -57.2937 | 64.7095 | 122.5296 | -0.4303 | -0.42114 | 0.20142 | 0.36621 | 122.3557 | 122.0718 | 121.8613 | 64.9979 | 64.7095 | 122.493 | 122.2366 | -0.42114 | 64.9979 | 64.7095 | 122.2366 | 121.8613 | 122.493 | -57.9483 | -122.7127
2454.9844 | 122.4426 | -64.7781 | 57.5912 | 0.088604 | 0.052243 | -0.018961 | 0.12198 | -0.078189 | -0.015461 | 0.067451 | -0.022888 | 0.30212 | -0.42114 | 58.0215 | 57.2891 | 57.6187 | 57.4677 | 57.5089 | 57.7148 | -65.1581 | 64.357 | -57.2891 | 64.7552 | 122.7997 | -0.30212 | -0.37994 | 0.1236 | 0.39825 | 122.2458 | 122.287 | 122.0673 | 65.0803 | 64.7552 | 122.493 | 122.3969 | -0.37994 | 65.0803 | 64.7552 | 122.3969 | 122.0673 | 122.493 | -58.0124 | -122.7493
2455.9219 | 122.5571 | -64.7095 | 57.5912 | 0.18016 | 0.020199 | -0.037119 | 0.094205 | -0.081393 | -0.049641 | 0.05677 | -0.032043 | 0.25635 | -0.39825 | 57.8293 | 57.1838 | 57.5546 | 57.637 | 57.3761 | 57.7606 | -65.1627 | 64.3112 | -57.3349 | 64.6774 | 122.5388 | -0.40741 | -0.45319 | 0.16937 | 0.36621 | 122.3465 | 122.0856 | 121.8933 | 64.9658 | 64.6774 | 122.4701 | 122.2641 | -0.45319 | 64.9658 | 64.6774 | 122.2641 | 121.8933 | 122.4701 | -57.9895 | -122.7539
2456.9844 | 122.4976 | -64.7598 | 57.6096 | -0.033467 | 0.037289 | -0.020029 | 0.12305 | -0.078189 | -0.014393 | 0.059974 | 0.059509 | 0.31128 | -0.40283 | 57.9803 | 57.2113 | 57.5775 | 57.5317 | 57.4036 | 57.7286 | -65.2084 | 64.357 | -57.2983 | 64.8193 | 122.7402 | -0.39825 | -0.44861 | 0.11902 | 0.46234 | 122.2916 | 122.1634 | 121.9711 | 65.0711 | 64.8193 | 122.4884 | 122.3373 | -0.44861 | 65.0711 | 64.8193 | 122.3373 | 121.9711 | 122.4884 | -58.0124 | -122.818
2457.9219 | 122.58 | -64.7415 | 57.5546 | 0.47007 | 0.027676 | -0.027506 | 0.10809 | -0.070712 | -0.046436 | 0.063178 | 0.059509 | 0.24261 | -0.37079 | 57.811 | 57.0969 | 57.4677 | 57.6462 | 57.2983 | 57.7789 | -65.2222 | 64.3707 | -57.312 | 64.801 | 122.5525 | -0.45776 | -0.48065 | 0.22431 | 0.4303 | 122.3877 | 122.0398 | 121.8384 | 64.9841 | 64.801 | 122.5204 | 122.2092 | -0.48065 | 64.9841 | 64.801 | 122.2092 | 121.8384 | 122.5204 | -57.9254 | -122.7768
2458.9844 | 122.4747 | -64.7964 | 57.5729 | 0.14964 | 0.054379 | -0.026438 | 0.12839 | -0.078189 | -0.016529 | 0.068519 | 0.018311 | 0.31128 | -0.41199 | 57.9987 | 57.193 | 57.6141 | 57.4997 | 57.3944 | 57.7286 | -65.1764 | 64.3845 | -57.2617 | 64.8148 | 122.7951 | -0.37994 | -0.37994 | 0.15564 | 0.4303 | 122.2961 | 122.1909 | 121.9894 | 65.1077 | 64.8148 | 122.525 | 122.4106 | -0.37994 | 65.1077 | 64.8148 | 122.4106 | 121.9894 | 122.525 | -57.9849 | -122.7493
2459.9219 | 122.5708 | -64.7598 | 57.5592 | 0.10386 | 0.024472 | -0.0478 | 0.094205 | -0.074984 | -0.053913 | 0.065314 | -0.018311 | 0.24261 | -0.39368 | 57.811 | 57.0648 | 57.5363 | 57.6004 | 57.2571 | 57.7698 | -65.1901 | 64.3662 | -57.3166 | 64.7415 | 122.5708 | -0.49439 | -0.4303 | 0.21057 | 0.37537 | 122.3602 | 122.0169 | 121.8246 | 65.0024 | 64.7415 | 122.5296 | 122.2961 | -0.4303 | 65.0024 | 64.7415 | 122.2961 | 121.8246 | 122.5296 | -57.9529 | -122.7493
2460.9844 | 122.5571 | -64.7964 | 57.5684 | 0.51585 | 0.041562 | -0.02537 | 0.12305 | -0.079257 | -0.024006 | 0.050361 | 0.018311 | 0.28839 | -0.40283 | 57.8979 | 57.0145 | 57.5455 | 57.5821 | 57.2113 | 57.7057 | -65.213 | 64.3936 | -57.28 | 64.8148 | 122.6944 | -0.55389 | -0.41657 | 0.13733 | 0.42114 | 122.3785 | 122.0078 | 121.8109 | 65.0848 | 64.8148 | 122.5021 | 122.3419 | -0.41657 | 65.0848 | 64.8148 | 122.3419 | 121.8109 | 122.5021 | -57.9712 | -122.7814
2461.9219 | 122.5662 | -64.769 | 57.55 | 0.31749 | 0.023404 | -0.036051 | 0.092069 | -0.076052 | -0.056049 | 0.058906 | -0.018311 | 0.2655 | -0.3891 | 57.8247 | 56.9092 | 57.5089 | 57.605 | 57.1243 | 57.7698 | -65.2359 | 64.3799 | -57.2845 | 64.7507 | 122.5937 | -0.64087 | -0.46692 | 0.21973 | 0.37079 | 122.374 | 121.8933 | 121.6782 | 65.0345 | 64.7507 | 122.5388 | 122.2778 | -0.46692 | 65.0345 | 64.7507 | 122.2778 | 121.6782 | 122.5388 | -57.9391 | -122.7859
2462.9844 | 122.5021 | -64.8056 | 57.6233 | 0.14964 | 0.036221 | -0.0082804 | 0.12198 | -0.073916 | -0.02187 | 0.066383 | 0.013733 | 0.31128 | -0.41657 | 58.0215 | 56.9778 | 57.6279 | 57.5134 | 57.1884 | 57.7377 | -65.2222 | 64.389 | -57.312 | 64.8193 | 122.8271 | -0.64545 | -0.41656 | 0.11444 | 0.4303 | 122.319 | 121.994 | 121.7834 | 65.1169 | 64.8193 | 122.5433 | 122.4335 | -0.41656 | 65.1169 | 64.8193 | 122.4335 | 121.7834 | 122.5433 | -58.0399 | -122.8455
2463.9219 | 122.5845 | -64.7598 | 57.5867 | 0.40904 | 0.018063 | -0.031779 | 0.10168 | -0.076052 | -0.036823 | 0.069587 | 0.027466 | 0.25635 | -0.37994 | 57.8293 | 56.8085 | 57.5272 | 57.6508 | 57.0053 | 57.7698 | -65.2039 | 64.3799 | -57.3303 | 64.7873 | 122.5891 | -0.7782 | -0.44403 | 0.18311 | 0.40741 | 122.4106 | 121.7651 | 121.5683 | 65.0162 | 64.7873 | 122.5296 | 122.287 | -0.44403 | 65.0162 | 64.7873 | 122.287 | 121.5683 | 122.5296 | -57.9666 | -122.7905
2464.9844 | 122.525 | -64.7736 | 57.6599 | 0.36326 | 0.049038 | -0.037119 | 0.11557 | -0.080325 | -0.011188 | 0.063178 | -0.013733 | 0.3067 | -0.43488 | 58.0353 | 56.8497 | 57.6599 | 57.5409 | 57.0602 | 57.7606 | -65.181 | 64.3387 | -57.3532 | 64.7598 | 122.8088 | -0.81024 | -0.40741 | 0.10071 | 0.42114 | 122.3145 | 121.8338 | 121.6232 | 65.0803 | 64.7598 | 122.5342 | 122.4335 | -0.40741 | 65.0803 | 64.7598 | 122.4335 | 121.6232 | 122.5342 | -58.0948 | -122.8409
2465.9219 | 122.612 | -64.7369 | 57.5912 | 0.31749 | 0.020199 | -0.028574 | 0.099546 | -0.085665 | -0.032551 | 0.063178 | 0.032043 | 0.24261 | -0.3891 | 57.8476 | 56.6299 | 57.518 | 57.6828 | 56.8222 | 57.8156 | -65.1901 | 64.3478 | -57.3486 | 64.769 | 122.5845 | -0.9613 | -0.45319 | 0.2243 | 0.42114 | 122.4197 | 121.5591 | 121.3669 | 64.9796 | 64.769 | 122.5525 | 122.2549 | -0.45319 | 64.9796 | 64.769 | 122.2549 | 121.3669 | 122.5525 | -57.9803 | -122.7814

## Thermal Data
Fire Time | South 11 C | Cable 1 | Cable 2
-0.3083 | 23.9442 | 23.0421 | 23.2269
0.6917 | 23.9578 | 23.0403 | 23.226
1.6917 | 23.9467 | 23.0326 | 23.2245
2.6917 | 23.9497 | 23.0332 | 23.2341
3.6917 | 23.9993 | 23.0262 | 23.2282
4.6917 | 24.3474 | 23.0305 | 23.2214
5.6917 | 25.2647 | 23.0322 | 23.2245
6.6917 | 26.7846 | 23.0331 | 23.2257
7.6917 | 28.8372 | 23.0376 | 23.238
8.6917 | 31.3605 | 23.0397 | 23.2292
9.6917 | 34.286 | 23.0413 | 23.232
10.6917 | 37.5504 | 23.0542 | 23.2392
11.6917 | 41.0974 | 23.0668 | 23.2579
12.6917 | 44.922 | 23.0752 | 23.2557
13.6917 | 48.9771 | 23.0839 | 23.2703
14.6917 | 53.2102 | 23.1046 | 23.2901
15.6917 | 57.6401 | 23.133 | 23.3068
16.6917 | 62.2341 | 23.1586 | 23.3391
17.6917 | 66.9518 | 23.195 | 23.3703
18.6917 | 71.828 | 23.2315 | 23.4046
19.6917 | 76.8172 | 23.2853 | 23.4544
20.6917 | 81.9076 | 23.3395 | 23.5035
21.6917 | 87.0719 | 23.404 | 23.5665
22.6917 | 92.3057 | 23.4697 | 23.6314
23.6917 | 97.594 | 23.5702 | 23.7102
24.6917 | 103.0404 | 23.6555 | 23.7726
25.6917 | 108.6025 | 23.748 | 23.8646
26.6917 | 114.2252 | 23.855 | 23.9546
27.6917 | 119.8641 | 23.9724 | 24.0569
28.6917 | 125.589 | 24.1094 | 24.1763
29.6917 | 131.3665 | 24.237 | 24.2924
30.6917 | 137.211 | 24.377 | 24.4241
31.6917 | 143.086 | 24.5376 | 24.5672
32.6917 | 149.0013 | 24.7069 | 24.7167
33.6917 | 154.8583 | 24.8939 | 24.8836
34.6917 | 160.746 | 25.0987 | 25.0634
35.6917 | 166.5701 | 25.3092 | 25.2444
36.6917 | 172.4574 | 25.5436 | 25.4394
37.6917 | 178.4183 | 25.7792 | 25.6535
38.6917 | 184.3915 | 26.0338 | 25.8888
39.6917 | 190.2767 | 26.3015 | 26.14
40.6917 | 196.2231 | 26.5884 | 26.399
41.6917 | 202.1693 | 26.8867 | 26.6671
42.6917 | 208.0611 | 27.2062 | 26.962
43.6917 | 213.8959 | 27.535 | 27.2553
44.6917 | 219.6944 | 27.8947 | 27.5753
45.6917 | 225.5317 | 28.2602 | 27.9162
46.6917 | 231.3764 | 28.6311 | 28.2766
47.6917 | 237.1217 | 29.0375 | 28.6357
48.6917 | 242.8126 | 29.4523 | 29.0181
49.6917 | 248.573 | 29.895 | 29.4185
50.6917 | 254.3009 | 30.3601 | 29.8395
51.6917 | 259.9486 | 30.8442 | 30.2744
52.6917 | 265.5628 | 31.3459 | 30.7271
53.6917 | 271.1667 | 31.8559 | 31.1994
54.6917 | 276.8354 | 32.3879 | 31.6895
55.6917 | 282.4273 | 32.9539 | 32.1923
56.6917 | 287.719 | 33.5407 | 32.7194
57.6917 | 292.6141 | 34.1287 | 33.2743
58.6917 | 297.2021 | 34.7389 | 33.83
59.6917 | 301.5889 | 35.3542 | 34.4009
60.6917 | 305.7144 | 35.9893 | 34.9753
61.6917 | 309.6103 | 36.6317 | 35.5649
62.6917 | 313.3161 | 37.2941 | 36.1744
63.6917 | 316.9728 | 37.9605 | 36.8009
64.6917 | 320.3624 | 38.6304 | 37.4258
65.6917 | 323.4336 | 39.3085 | 38.0568
66.6917 | 326.1392 | 39.9977 | 38.689
67.6917 | 328.6247 | 40.699 | 39.3436
68.6917 | 330.7644 | 41.4102 | 39.9977
69.6917 | 332.6041 | 42.1383 | 40.6669
70.6917 | 334.2253 | 42.8618 | 41.3409
71.6917 | 335.5988 | 43.6049 | 42.0106
72.6917 | 336.7276 | 44.3318 | 42.6899
73.6917 | 337.7294 | 45.0753 | 43.3696
74.6917 | 338.5543 | 45.8228 | 44.0504
75.6917 | 339.1608 | 46.5804 | 44.7328
76.6917 | 339.5472 | 47.337 | 45.4152
77.6917 | 339.9448 | 48.0931 | 46.1094
78.6917 | 340.3197 | 48.8619 | 46.7827
79.6917 | 340.5863 | 49.6282 | 47.469
80.6917 | 340.5836 | 50.4117 | 48.1495
81.6917 | 340.5153 | 51.1928 | 48.8345
82.6917 | 340.5096 | 51.9735 | 49.5187
83.6917 | 340.4911 | 52.7867 | 50.2029
84.6917 | 340.4665 | 53.5701 | 50.8941
85.6917 | 340.3503 | 54.3581 | 51.5731
86.6917 | 340.1274 | 55.1583 | 52.2616
87.6917 | 339.8004 | 55.9467 | 52.9386
88.6917 | 339.6077 | 56.7499 | 53.6073
89.6917 | 339.2757 | 57.5311 | 54.2825
90.6917 | 338.9673 | 58.331 | 54.9607
91.6917 | 338.6587 | 59.1104 | 55.6357
92.6917 | 338.2933 | 59.9109 | 56.3112
93.6917 | 337.9214 | 60.7058 | 56.9795
94.6917 | 337.5067 | 61.4967 | 57.6484
95.6917 | 337.072 | 62.2835 | 58.3035
96.6917 | 336.5933 | 63.0651 | 58.9687
97.6917 | 336.1745 | 63.8293 | 59.618
98.6917 | 335.7255 | 64.6106 | 60.2611
99.6917 | 335.3044 | 65.3682 | 60.8934
100.6917 | 334.8026 | 66.1199 | 61.5304
101.6917 | 334.3158 | 66.8646 | 62.1646
102.6917 | 333.8276 | 67.6007 | 62.7833
103.6917 | 333.2494 | 68.3335 | 63.3956
104.6917 | 332.7687 | 69.0604 | 64.0084
105.6917 | 332.2981 | 69.7732 | 64.6073
106.6917 | 331.7308 | 70.4861 | 65.2008
107.6917 | 331.2215 | 71.1993 | 65.7918
108.6917 | 330.7241 | 71.9062 | 66.3755
109.6917 | 330.1393 | 72.6221 | 66.9459
110.6917 | 329.5628 | 73.3127 | 67.5183
111.6917 | 329.055 | 74.0128 | 68.0791
112.6917 | 328.5568 | 74.6931 | 68.6401
113.6917 | 328.0477 | 75.3523 | 69.1985
114.6917 | 327.5704 | 76.0048 | 69.7403
115.6917 | 327.1086 | 76.6502 | 70.2856
116.6917 | 326.5861 | 77.2898 | 70.8123
117.6917 | 326.0226 | 77.9167 | 71.3562
118.6917 | 325.4983 | 78.5383 | 71.8724
119.6917 | 324.9773 | 79.1635 | 72.389
120.6917 | 324.4388 | 79.759 | 72.906
121.6917 | 324.0194 | 80.3604 | 73.4124
122.6917 | 323.6351 | 80.9599 | 73.9198
123.6917 | 323.2298 | 81.5447 | 74.4095
124.7073 | 322.8076 | 82.1211 | 74.9032
125.6917 | 322.3727 | 82.7055 | 75.3841
126.6917 | 322.0565 | 83.2633 | 75.8564
127.6917 | 321.7854 | 83.8217 | 76.3234
128.6917 | 321.5362 | 84.3829 | 76.7972
129.6917 | 321.3524 | 84.9325 | 77.2454
130.6917 | 321.2706 | 85.4581 | 77.721
131.6917 | 321.1857 | 85.9996 | 78.1789
132.6917 | 321.1806 | 86.5439 | 78.6288
133.6917 | 321.2854 | 87.0731 | 79.0833
134.6917 | 321.4376 | 87.6017 | 79.5296
135.6917 | 321.6326 | 88.1275 | 79.9793
136.6917 | 321.8501 | 88.6508 | 80.4277
137.6917 | 322.1243 | 89.1706 | 80.8849
138.6917 | 322.4193 | 89.6925 | 81.3287
139.6917 | 322.8483 | 90.2192 | 81.7695
140.6917 | 323.2164 | 90.7242 | 82.2106
141.6917 | 323.5015 | 91.2415 | 82.6475
142.6917 | 323.8368 | 91.7604 | 83.0943
143.6917 | 324.2026 | 92.2715 | 83.5394
144.6917 | 324.5833 | 92.7779 | 83.9758
145.6917 | 325.0176 | 93.2908 | 84.4208
146.6917 | 325.3946 | 93.8027 | 84.8689
147.6917 | 325.8206 | 94.3154 | 85.3068
148.6917 | 326.1897 | 94.8237 | 85.7546
149.6917 | 326.564 | 95.3347 | 86.1988
150.6917 | 326.9984 | 95.8451 | 86.6412
151.6917 | 327.4531 | 96.3552 | 87.0847
152.6917 | 327.809 | 96.864 | 87.539
153.6917 | 328.1323 | 97.3711 | 87.98
154.6917 | 328.4663 | 97.8751 | 88.426
155.6917 | 328.8185 | 98.3932 | 88.8746
156.6917 | 329.1128 | 98.8942 | 89.332
157.6917 | 329.3735 | 99.4219 | 89.7888
158.6917 | 329.5997 | 99.9274 | 90.2417
159.6917 | 329.8327 | 100.4305 | 90.6899
160.6917 | 330.0748 | 100.9481 | 91.1372
161.6917 | 330.2616 | 101.4553 | 91.5814
162.6917 | 330.3654 | 101.9565 | 92.0348
163.6917 | 330.5176 | 102.4634 | 92.4851
164.6917 | 330.642 | 102.9625 | 92.9379
165.6917 | 330.7006 | 103.4733 | 93.3834
166.6917 | 330.7626 | 103.9749 | 93.8354
167.6917 | 330.8387 | 104.4859 | 94.2783
168.6917 | 330.8935 | 104.9815 | 94.7338
169.6917 | 330.9773 | 105.4854 | 95.1764
170.6917 | 331.1021 | 105.978 | 95.6162
171.6917 | 331.1761 | 106.4829 | 96.0558
172.6917 | 331.2052 | 106.9698 | 96.5048
173.6917 | 331.2079 | 107.4631 | 96.9438
174.6917 | 331.2477 | 107.9453 | 97.3798
175.6917 | 331.3653 | 108.4718 | 97.8196
176.6917 | 331.4725 | 108.9779 | 98.262
177.6917 | 331.5294 | 109.4767 | 98.7044
178.6917 | 331.4893 | 109.9753 | 99.1382
179.6917 | 331.4748 | 110.4675 | 99.5791
180.6917 | 331.4309 | 110.9624 | 100.0129
181.6917 | 331.3962 | 111.4517 | 100.4405
182.6917 | 331.3514 | 111.9464 | 100.8687
183.6917 | 331.2698 | 112.4428 | 101.297
184.6917 | 331.2508 | 112.9311 | 101.7157
185.6917 | 331.319 | 113.4092 | 102.1397
186.6917 | 331.3931 | 113.8992 | 102.5632
187.6917 | 331.4115 | 114.3827 | 102.9909
188.6917 | 331.4189 | 114.8597 | 103.4032
189.6917 | 331.3479 | 115.3336 | 103.8176
190.6917 | 331.2806 | 115.8054 | 104.2382
191.6917 | 331.2535 | 116.2831 | 104.6631
192.6917 | 331.1829 | 116.7642 | 105.0704
193.6917 | 331.0862 | 117.2274 | 105.4769
194.6917 | 330.9867 | 117.7003 | 105.8838
195.6917 | 330.9311 | 118.1637 | 106.2975
196.6917 | 330.8801 | 118.6438 | 106.6999
197.6917 | 330.8125 | 119.1096 | 107.1014
198.6917 | 330.708 | 119.5585 | 107.501
199.6917 | 330.6654 | 120.02 | 107.9094
200.6917 | 330.6228 | 120.4849 | 108.3025
201.6917 | 330.5856 | 120.9607 | 108.7023
202.6917 | 330.5359 | 121.4099 | 109.1001
203.6917 | 330.5182 | 121.8767 | 109.4896
204.6917 | 330.5116 | 122.3295 | 109.8858
205.6917 | 330.52 | 122.7916 | 110.2735
206.6917 | 330.4954 | 123.2334 | 110.6694
207.6917 | 330.4691 | 123.6875 | 111.0567
208.6917 | 330.4711 | 124.1441 | 111.4469
209.6917 | 330.4596 | 124.5939 | 111.8268
210.6917 | 330.4527 | 125.0384 | 112.2149
211.6917 | 330.4641 | 125.4824 | 112.5908
212.6917 | 330.4683 | 125.9251 | 112.9711
213.6917 | 330.4319 | 126.3601 | 113.3517
214.6917 | 330.4678 | 126.8194 | 113.7256
215.6917 | 330.5539 | 127.2652 | 114.1041
216.6917 | 330.5793 | 127.7049 | 114.4724
217.6917 | 330.5811 | 128.1597 | 114.8473
218.6917 | 330.6455 | 128.5892 | 115.216
219.6917 | 330.6195 | 129.0459 | 115.5901
220.6917 | 330.6244 | 129.4838 | 115.9488
221.6917 | 330.5992 | 129.9245 | 116.3175
222.6917 | 330.6194 | 130.3522 | 116.679
223.6917 | 330.5945 | 130.7874 | 117.0361
224.6917 | 330.5753 | 131.2306 | 117.4062
225.6917 | 330.6174 | 131.6525 | 117.7617
226.6917 | 330.5793 | 132.0912 | 118.1219
227.6917 | 330.6167 | 132.5235 | 118.4776
228.6917 | 330.6906 | 132.956 | 118.8414
229.6917 | 330.7833 | 133.3835 | 119.1886
230.6917 | 330.7962 | 133.8123 | 119.5333
231.6917 | 330.7765 | 134.2384 | 119.883
232.6917 | 330.8409 | 134.6672 | 120.2314
233.6917 | 330.9373 | 135.0937 | 120.5763
234.6917 | 331.0055 | 135.5167 | 120.919
235.6917 | 331.0355 | 135.9422 | 121.2571
236.6917 | 331.0336 | 136.3609 | 121.5885
237.6917 | 331.0265 | 136.792 | 121.9316
238.6917 | 331.0442 | 137.2115 | 122.2596
239.6917 | 331.0677 | 137.6423 | 122.5889
240.6917 | 331.1324 | 138.0598 | 122.9213
241.6917 | 331.1036 | 138.4655 | 123.2374
242.6917 | 331.061 | 138.899 | 123.5654
243.6917 | 331.0716 | 139.3086 | 123.8881
244.6917 | 331.1204 | 139.7219 | 124.203
245.6917 | 331.156 | 140.1414 | 124.5152
246.6917 | 331.1525 | 140.5518 | 124.8265
247.6917 | 331.1358 | 140.958 | 125.1404
248.6917 | 331.0757 | 141.3586 | 125.4403
249.6917 | 331.1021 | 141.7696 | 125.7459
250.6917 | 331.0398 | 142.1658 | 126.0468
251.6917 | 330.9276 | 142.5422 | 126.3474
252.6917 | 330.8436 | 142.9505 | 126.6354
253.6917 | 330.7622 | 143.3414 | 126.9375
254.6917 | 330.6622 | 143.723 | 127.2333
255.6917 | 330.58 | 144.1036 | 127.5198
256.6917 | 330.5523 | 144.4846 | 127.8055
257.6917 | 330.5433 | 144.8589 | 128.1022
258.6917 | 330.5004 | 145.2286 | 128.3883
259.6917 | 330.4703 | 145.5934 | 128.6799
260.6917 | 330.4071 | 145.9498 | 128.9643
261.6917 | 330.3333 | 146.3088 | 129.2452
262.6917 | 330.2776 | 146.6546 | 129.5221
263.6917 | 330.2746 | 146.9856 | 129.7933
264.6917 | 330.2996 | 147.3206 | 130.0775
265.6917 | 330.3516 | 147.6513 | 130.343
266.6917 | 330.3425 | 147.9752 | 130.6282
267.6917 | 330.2961 | 148.2926 | 130.8964
268.6917 | 330.2605 | 148.612 | 131.1793
269.6917 | 330.2361 | 148.9203 | 131.454
270.6917 | 330.2129 | 149.2224 | 131.7201
271.6917 | 330.1629 | 149.5363 | 131.9981
272.6917 | 330.1212 | 149.8404 | 132.2712
273.6917 | 330.1081 | 150.1293 | 132.5482
274.6917 | 330.0938 | 150.4079 | 132.8218
275.6917 | 330.1005 | 150.6939 | 133.0928
276.6917 | 330.1096 | 150.971 | 133.3668
277.6917 | 330.1454 | 151.2336 | 133.6459
278.6917 | 330.0911 | 151.5018 | 133.9236
279.6917 | 330.0731 | 151.7591 | 134.199
280.6917 | 330.0822 | 152.0251 | 134.4795
281.6917 | 330.106 | 152.2808 | 134.7583
282.6917 | 330.1389 | 152.5255 | 135.0459
283.6917 | 330.1459 | 152.7778 | 135.3279
284.6917 | 330.0979 | 153.0316 | 135.6141
285.6917 | 330.0909 | 153.2809 | 135.9161
286.6917 | 330.1028 | 153.5245 | 136.2095
287.6917 | 330.13 | 153.779 | 136.5082
288.6917 | 330.1632 | 154.0364 | 136.8114
289.6917 | 330.1923 | 154.2855 | 137.1216
290.6917 | 330.2199 | 154.538 | 137.4344
291.6917 | 330.2592 | 154.7977 | 137.7567
292.6917 | 330.2616 | 155.0613 | 138.0697
293.6917 | 330.2859 | 155.3205 | 138.3857
294.6917 | 330.2994 | 155.5909 | 138.7015
295.6917 | 330.2831 | 155.8679 | 139.0236
296.6917 | 330.2957 | 156.129 | 139.3533
297.6917 | 330.3092 | 156.4181 | 139.6656
298.6917 | 330.3672 | 156.6879 | 139.9957
299.6917 | 330.4338 | 156.9837 | 140.3218
300.6917 | 330.4586 | 157.2762 | 140.6512
301.6917 | 330.4714 | 157.5557 | 140.9838
302.6917 | 330.4877 | 157.8502 | 141.3079
303.6917 | 330.4807 | 158.1467 | 141.63
304.6917 | 330.4887 | 158.4436 | 141.9687
305.6917 | 330.462 | 158.7355 | 142.2907
306.6917 | 330.4552 | 159.0278 | 142.6215
307.6917 | 330.4471 | 159.3375 | 142.9559
308.6917 | 330.3861 | 159.6441 | 143.2891
309.6917 | 330.3533 | 159.9425 | 143.6265
310.6917 | 330.3341 | 160.243 | 143.9594
311.6917 | 330.3391 | 160.5581 | 144.2869
312.6917 | 330.427 | 160.8415 | 144.6237
313.6917 | 330.4642 | 161.1602 | 144.9612
314.6917 | 330.4664 | 161.4709 | 145.2863
315.6917 | 330.4801 | 161.769 | 145.6241
316.6917 | 330.4894 | 162.0626 | 145.9543
317.6917 | 330.4859 | 162.3661 | 146.2867
318.6917 | 330.4325 | 162.662 | 146.6136
319.6917 | 330.4751 | 162.9725 | 146.9446
320.6917 | 330.5224 | 163.2767 | 147.2833
321.6917 | 330.4995 | 163.588 | 147.6115
322.6917 | 330.4695 | 163.8857 | 147.9417
323.6917 | 330.4581 | 164.198 | 148.2677
324.6917 | 330.4153 | 164.5119 | 148.5894
325.6917 | 330.3628 | 164.8152 | 148.9204
326.6917 | 330.3806 | 165.1177 | 149.2408
327.6917 | 330.3362 | 165.4199 | 149.5674
328.6917 | 330.3107 | 165.7193 | 149.8937
329.6917 | 330.2895 | 166.0399 | 150.2097
330.6917 | 330.3118 | 166.3374 | 150.53
331.6917 | 330.3515 | 166.649 | 150.8534
332.6917 | 330.3328 | 166.9645 | 151.178
333.6917 | 330.3096 | 167.2749 | 151.493
334.6917 | 330.302 | 167.5781 | 151.8124
335.6917 | 330.2876 | 167.8743 | 152.1278
336.6917 | 330.2692 | 168.1925 | 152.445
337.6917 | 330.2623 | 168.4957 | 152.7608
338.6917 | 330.273 | 168.8095 | 153.076
339.6917 | 330.2837 | 169.1112 | 153.4045
340.6917 | 330.2719 | 169.4065 | 153.7169
341.6917 | 330.2745 | 169.7264 | 154.0278
342.6917 | 330.2675 | 170.0315 | 154.3389
343.6917 | 330.2553 | 170.3294 | 154.661
344.6917 | 330.2916 | 170.6418 | 154.968
345.6917 | 330.3153 | 170.9432 | 155.2782
346.6917 | 330.3001 | 171.264 | 155.5938
347.6917 | 330.2969 | 171.5587 | 155.9095
348.6917 | 330.317 | 171.8709 | 156.2249
349.6917 | 330.3264 | 172.1757 | 156.5256
350.6917 | 330.3426 | 172.494 | 156.8377
351.6917 | 330.3664 | 172.7994 | 157.1534
352.6917 | 330.3745 | 173.1052 | 157.463
353.6917 | 330.4283 | 173.4176 | 157.771
354.6917 | 330.3987 | 173.7225 | 158.0726
355.6917 | 330.3491 | 174.0292 | 158.383
356.6917 | 330.2673 | 174.346 | 158.6856
357.6917 | 330.2489 | 174.6463 | 158.9984
358.6917 | 330.268 | 174.9598 | 159.3006
359.6917 | 330.2579 | 175.2616 | 159.6045
360.6917 | 330.2493 | 175.5673 | 159.9068
361.6917 | 330.2556 | 175.8761 | 160.2141
362.6917 | 330.2687 | 176.1782 | 160.5157
363.6917 | 330.2955 | 176.4821 | 160.8206
364.6917 | 330.3592 | 176.7852 | 161.1187
365.6917 | 330.3755 | 177.09 | 161.4226
366.6917 | 330.3577 | 177.3942 | 161.7298
367.6917 | 330.3556 | 177.6861 | 162.0243
368.6917 | 330.3239 | 177.9943 | 162.3181
369.6917 | 330.3474 | 178.2879 | 162.6197
370.6917 | 330.3495 | 178.5887 | 162.9127
371.6917 | 330.3463 | 178.8882 | 163.2147
372.6917 | 330.3551 | 179.1925 | 163.51
373.6917 | 330.3557 | 179.4778 | 163.7995
374.6917 | 330.3275 | 179.768 | 164.0913
375.6917 | 330.3029 | 180.0642 | 164.3866
376.6917 | 330.2816 | 180.3559 | 164.6806
377.6917 | 330.2735 | 180.6516 | 164.9752
378.6917 | 330.274 | 180.9265 | 165.2659
379.6917 | 330.2073 | 181.2248 | 165.5597
380.6917 | 330.1853 | 181.511 | 165.8534
381.6917 | 330.142 | 181.8084 | 166.1427
382.6917 | 330.1465 | 182.0863 | 166.4339
383.6917 | 330.1298 | 182.3737 | 166.7277
384.6917 | 330.0728 | 182.6595 | 167.0133
385.6917 | 330.0087 | 182.945 | 167.2883
386.6917 | 329.9587 | 183.2188 | 167.5693
387.6917 | 329.8878 | 183.4874 | 167.844
388.6917 | 329.9113 | 183.7654 | 168.1334
389.6917 | 329.9156 | 184.0426 | 168.3999
390.6917 | 329.9211 | 184.3133 | 168.6849
391.6917 | 329.9372 | 184.5923 | 168.9542
392.6917 | 329.9749 | 184.8631 | 169.2222
393.6917 | 330.0006 | 185.1335 | 169.4955
394.6917 | 330.0331 | 185.4171 | 169.7684
395.6917 | 330.056 | 185.6627 | 170.0373
396.6917 | 330.0556 | 185.9449 | 170.31
397.6917 | 330.0386 | 186.205 | 170.5779
398.6917 | 329.9928 | 186.4824 | 170.8544
399.6917 | 330.0041 | 186.7334 | 171.1149
400.6917 | 330.0541 | 186.9899 | 171.3859
401.6917 | 330.0914 | 187.259 | 171.6547
402.6917 | 330.1313 | 187.5162 | 171.9197
403.6917 | 330.158 | 187.7728 | 172.1835
404.6917 | 330.1472 | 188.0348 | 172.4485
405.6917 | 330.1533 | 188.294 | 172.7142
406.6917 | 330.1812 | 188.555 | 172.974
407.6917 | 330.2194 | 188.8091 | 173.2369
408.6917 | 330.2188 | 189.0615 | 173.4994
409.6917 | 330.2391 | 189.3228 | 173.7583
410.6917 | 330.2486 | 189.5733 | 174.014
411.6917 | 330.2656 | 189.831 | 174.2667
412.6917 | 330.274 | 190.0819 | 174.5289
413.6917 | 330.2174 | 190.3262 | 174.7692
414.6917 | 330.2192 | 190.581 | 175.0268
415.6917 | 330.2533 | 190.848 | 175.2875
416.6917 | 330.2539 | 191.1007 | 175.5307
417.6917 | 330.2572 | 191.3521 | 175.7768
418.6917 | 330.265 | 191.5991 | 176.0178
419.6917 | 330.2951 | 191.842 | 176.2604
420.6917 | 330.3457 | 192.1049 | 176.5093
421.6917 | 330.3703 | 192.3532 | 176.7419
422.6917 | 330.4125 | 192.611 | 176.9767
423.6917 | 330.4169 | 192.8642 | 177.2048
424.6917 | 330.3797 | 193.1146 | 177.4323
425.6917 | 330.3406 | 193.3722 | 177.6488
426.6917 | 330.3466 | 193.6172 | 177.864
427.6917 | 330.3567 | 193.8743 | 178.0672
428.6917 | 330.3563 | 194.1204 | 178.2446
429.6917 | 330.3932 | 194.3823 | 178.402
430.6917 | 330.3859 | 194.6411 | 178.5465
431.6917 | 330.3534 | 194.8839 | 178.7281
432.6917 | 330.2999 | 195.1357 | 178.9219
433.6917 | 330.2845 | 195.3949 | 179.1187
434.6917 | 330.244 | 195.6472 | 179.3467
435.6917 | 330.2165 | 195.8882 | 179.5787
436.6917 | 330.2271 | 196.1418 | 179.8251
437.6917 | 330.2515 | 196.3966 | 180.0638
438.6917 | 330.2434 | 196.6407 | 180.3142
439.6917 | 330.1934 | 196.901 | 180.5591
440.6917 | 330.1525 | 197.1346 | 180.8067
441.6917 | 330.141 | 197.4004 | 181.0698
442.6917 | 330.1371 | 197.6455 | 181.316
443.6917 | 330.1631 | 197.9009 | 181.5704
444.6917 | 330.1464 | 198.1506 | 181.827
445.6917 | 330.1383 | 198.4047 | 182.0887
446.6917 | 330.1125 | 198.6485 | 182.3497
447.6917 | 330.1513 | 198.9041 | 182.6094
448.6917 | 330.1878 | 199.1689 | 182.8732
449.6917 | 330.2244 | 199.4309 | 183.1396
450.6917 | 330.2109 | 199.6917 | 183.3987
451.6917 | 330.1671 | 199.9499 | 183.6674
452.6917 | 330.1074 | 200.1882 | 183.9277
453.6917 | 330.1168 | 200.4517 | 184.1875
454.6917 | 330.1043 | 200.7055 | 184.451
455.6917 | 330.1201 | 200.961 | 184.7122
456.6917 | 330.1238 | 201.2101 | 184.983
457.6917 | 330.1147 | 201.4526 | 185.2496
458.6917 | 330.1 | 201.7018 | 185.5009
459.6917 | 330.0786 | 201.9454 | 185.7663
460.6917 | 330.0531 | 202.1884 | 186.0331
461.6917 | 330.0609 | 202.4452 | 186.3112
462.6917 | 330.0861 | 202.6837 | 186.5683
463.6917 | 330.0552 | 202.9224 | 186.8282
464.6917 | 330.007 | 203.1626 | 187.0914
465.6917 | 330.0185 | 203.4051 | 187.3632
466.6917 | 329.9999 | 203.6307 | 187.6231
467.6917 | 330.0351 | 203.8597 | 187.8859
468.6917 | 330.0218 | 204.0958 | 188.1513
469.6917 | 330.1124 | 204.3224 | 188.4207
470.6917 | 330.1783 | 204.5548 | 188.6828
471.6917 | 330.1756 | 204.7935 | 188.9583
472.6917 | 330.1662 | 205.023 | 189.2252
473.6917 | 330.1849 | 205.2607 | 189.4828
474.6917 | 330.1967 | 205.4921 | 189.7499
475.6917 | 330.183 | 205.7154 | 190.0067
476.6917 | 330.1779 | 205.953 | 190.2755
477.6917 | 330.2228 | 206.1743 | 190.5429
478.6917 | 330.2791 | 206.4102 | 190.8082
479.6917 | 330.3164 | 206.6261 | 191.0711
480.6917 | 330.3239 | 206.858 | 191.3269
481.6917 | 330.3674 | 207.0857 | 191.5888
482.6917 | 330.4562 | 207.3011 | 191.8508
483.6917 | 330.4891 | 207.5272 | 192.1111
484.6917 | 330.5132 | 207.7662 | 192.3709
485.6917 | 330.5032 | 207.9956 | 192.6364
486.6917 | 330.5613 | 208.2371 | 192.8967
487.6917 | 330.574 | 208.4698 | 193.1535
488.6917 | 330.579 | 208.7022 | 193.4259
489.6917 | 330.5885 | 208.928 | 193.6766
490.6917 | 330.6198 | 209.1784 | 193.9422
491.6917 | 330.6281 | 209.3989 | 194.1953
492.6917 | 330.6468 | 209.6279 | 194.4561
493.6917 | 330.6537 | 209.8633 | 194.7181
494.6917 | 330.6719 | 210.1027 | 194.9849
495.6917 | 330.7052 | 210.3288 | 195.2427
496.6917 | 330.6494 | 210.541 | 195.4938
497.6917 | 330.5936 | 210.767 | 195.7541
498.6917 | 330.5985 | 210.994 | 196.0176
499.6917 | 330.5676 | 211.2237 | 196.2858
500.6917 | 330.5403 | 211.4432 | 196.5378
501.6917 | 330.5251 | 211.6813 | 196.7917
502.6917 | 330.5339 | 211.8923 | 197.0478
503.6917 | 330.5538 | 212.1178 | 197.3097
504.6917 | 330.5845 | 212.3425 | 197.5661
505.6917 | 330.6175 | 212.5582 | 197.8106
506.6917 | 330.6064 | 212.7911 | 198.0604
507.6917 | 330.5279 | 213.0071 | 198.3112
508.6917 | 330.4478 | 213.2212 | 198.5649
509.6917 | 330.4241 | 213.4378 | 198.8172
510.6917 | 330.4182 | 213.6475 | 199.0564
511.6917 | 330.4088 | 213.8688 | 199.301
512.6917 | 330.3867 | 214.0828 | 199.5472
513.6917 | 330.392 | 214.3022 | 199.7926
514.6917 | 330.3542 | 214.5064 | 200.0368
515.6917 | 330.2535 | 214.717 | 200.2857
516.6917 | 330.1919 | 214.9336 | 200.5267
517.6917 | 330.1667 | 215.1536 | 200.7682
518.6917 | 330.106 | 215.4167 | 201.008
519.6917 | 330.0511 | 215.6954 | 201.2488
520.6917 | 330.0271 | 215.9517 | 201.4821
521.6917 | 330.0093 | 216.2246 | 201.7118
522.6917 | 329.9924 | 216.4732 | 201.9561
523.6917 | 329.9624 | 216.7261 | 202.1891
524.6917 | 329.9281 | 216.9719 | 202.4213
525.6917 | 329.8998 | 217.2164 | 202.6467
526.6917 | 329.9336 | 217.4628 | 202.8815
527.6917 | 329.9665 | 217.7195 | 203.1177
528.6917 | 329.9465 | 217.9557 | 203.3479
529.6917 | 329.9474 | 218.1753 | 203.5821
530.6917 | 329.9475 | 218.4141 | 203.8125
531.6917 | 329.9549 | 218.6534 | 204.0508
532.6917 | 329.9144 | 218.86 | 204.2811
533.6917 | 329.9213 | 219.0723 | 204.5051
534.6917 | 329.9134 | 219.2929 | 204.7416
535.6917 | 329.9277 | 219.5064 | 204.9664
536.6917 | 329.9327 | 219.7354 | 205.1922
537.6917 | 329.9753 | 219.9438 | 205.4186
538.6917 | 329.9872 | 220.1718 | 205.6379
539.6917 | 330.0089 | 220.3864 | 205.8746
540.6917 | 330.0259 | 220.5981 | 206.1029
541.6917 | 330.0379 | 220.8016 | 206.321
542.6917 | 330.0983 | 221.0074 | 206.5414
543.6917 | 330.0958 | 221.2233 | 206.7687
544.6917 | 330.1423 | 221.4339 | 206.992
545.6917 | 330.2214 | 221.6382 | 207.2171
546.6917 | 330.304 | 221.8634 | 207.4366
547.6917 | 330.3496 | 222.0818 | 207.6545
548.6917 | 330.3273 | 222.2932 | 207.8789
549.6917 | 330.3007 | 222.5208 | 208.1015
550.6917 | 330.3135 | 222.7559 | 208.3273
551.6917 | 330.3287 | 222.9995 | 208.5405
552.6917 | 330.3456 | 223.2709 | 208.766
553.6917 | 330.3858 | 223.5267 | 208.9862
554.6917 | 330.4358 | 223.785 | 209.203
555.6917 | 330.4753 | 224.0553 | 209.4214
556.6917 | 330.524 | 224.3239 | 209.6436
557.6917 | 330.5559 | 224.5934 | 209.8588
558.6917 | 330.5339 | 224.853 | 210.075
559.6917 | 330.5292 | 225.1354 | 210.2881
560.6917 | 330.5133 | 225.4192 | 210.5048
561.6917 | 330.4774 | 225.6889 | 210.7239
562.6917 | 330.4557 | 225.9575 | 210.9401
563.6917 | 330.3586 | 226.2495 | 211.1485
564.6917 | 330.3173 | 226.5348 | 211.359
565.6917 | 330.2633 | 226.8023 | 211.5683
566.6917 | 330.1587 | 227.1037 | 211.775
567.6917 | 330.1208 | 227.4025 | 211.9845
568.6917 | 330.0627 | 227.7324 | 212.1852
569.6917 | 330.0306 | 228.0598 | 212.395
570.6917 | 330.0015 | 228.3754 | 212.5993
571.6917 | 330.0142 | 228.7066 | 212.8104
572.6917 | 329.997 | 229.0194 | 213.0091
573.6917 | 330.0047 | 229.351 | 213.2218
574.6917 | 330.0194 | 229.6884 | 213.4226
575.6917 | 329.9712 | 230.0025 | 213.6157
576.6917 | 329.9492 | 230.339 | 213.8198
577.6917 | 329.9432 | 230.6972 | 214.0243
578.6917 | 329.9294 | 231.0356 | 214.2264
579.6917 | 329.9312 | 231.363 | 214.4423
580.6917 | 329.9581 | 231.6918 | 214.6798
581.6917 | 329.9537 | 232.0146 | 214.8972
582.6917 | 329.9974 | 232.3386 | 215.1079
583.6917 | 330.0421 | 232.6105 | 215.3304
584.6917 | 330.0496 | 232.918 | 215.5392
585.6917 | 330.0846 | 233.2481 | 215.7583
586.6917 | 330.0468 | 233.5726 | 215.9552
587.6917 | 330.0339 | 233.8972 | 216.1615
588.6917 | 330.0284 | 234.2004 | 216.3633
589.6917 | 329.9924 | 234.4655 | 216.5766
590.6917 | 329.9595 | 234.699 | 216.7819
591.6917 | 329.956 | 234.9648 | 216.9625
592.6917 | 329.974 | 235.2707 | 217.1429
593.6917 | 329.9347 | 235.56 | 217.3244
594.6917 | 329.8907 | 235.8557 | 217.5226
595.6917 | 329.9308 | 236.1426 | 217.7164
596.6917 | 329.9561 | 236.3883 | 217.9087
597.6917 | 329.9984 | 236.6454 | 218.1045
598.6917 | 329.9995 | 236.8944 | 218.293
599.6917 | 330.0075 | 237.1404 | 218.4866
600.6917 | 329.9951 | 237.3926 | 218.6825
601.6917 | 329.9798 | 237.6413 | 218.8598
602.6917 | 329.9325 | 237.8926 | 219.0514
603.6917 | 329.9146 | 238.1174 | 219.2457
604.6917 | 329.9246 | 238.3457 | 219.4291
605.6917 | 329.9337 | 238.5602 | 219.6249
606.6917 | 329.9553 | 238.7751 | 219.8067
607.6917 | 329.9954 | 239.0079 | 220.0045
608.6917 | 330.0483 | 239.2314 | 220.1825
609.6917 | 330.0433 | 239.4099 | 220.3658
610.6917 | 329.9784 | 239.6213 | 220.5412
611.6917 | 329.9598 | 239.7489 | 220.7241
612.6917 | 329.9643 | 239.9371 | 220.9136
613.6917 | 329.9911 | 240.1494 | 221.0895
614.6917 | 330.0389 | 240.3526 | 221.26
615.6917 | 330.0979 | 240.5631 | 221.4419
616.6917 | 330.1895 | 240.7521 | 221.6217
617.6917 | 330.2636 | 240.9755 | 221.7935
618.6917 | 330.2787 | 241.1757 | 221.9724
619.6917 | 330.3139 | 241.3947 | 222.1523
620.6917 | 330.3621 | 241.6097 | 222.3312
621.6917 | 330.3851 | 241.7646 | 222.5067
622.6917 | 330.3923 | 241.9249 | 222.6912
623.6917 | 330.4617 | 242.0842 | 222.8725
624.6917 | 330.537 | 242.1825 | 223.051
625.6917 | 330.581 | 242.3077 | 223.2394
626.6917 | 330.5825 | 242.4196 | 223.4179
627.6917 | 330.6061 | 242.5909 | 223.6011
628.6917 | 330.5954 | 242.7408 | 223.7716
629.6917 | 330.5497 | 242.9183 | 223.9482
630.6917 | 330.5007 | 243.0841 | 224.1212
631.6917 | 330.4709 | 243.2804 | 224.2893
632.6917 | 330.4695 | 243.495 | 224.4565
633.6917 | 330.4832 | 243.6646 | 224.6233
634.6917 | 330.454 | 243.8398 | 224.7899
635.6917 | 330.3882 | 243.9808 | 224.9575
636.6917 | 330.3611 | 244.1558 | 225.122
637.6917 | 330.3356 | 244.3013 | 225.3075
638.6917 | 330.3381 | 244.4529 | 225.4904
639.6917 | 330.3292 | 244.6014 | 225.6502
640.6917 | 330.3015 | 244.791 | 225.8338
641.6917 | 330.2831 | 244.9681 | 226.004
642.6917 | 330.2387 | 245.1248 | 226.1701
643.6917 | 330.1894 | 245.2792 | 226.3376
644.6917 | 330.1791 | 245.4501 | 226.5067
645.6917 | 330.1657 | 245.6342 | 226.678
646.6917 | 330.1576 | 245.7653 | 226.8418
647.6917 | 330.1467 | 245.902 | 227.017
648.6917 | 330.1286 | 246.0031 | 227.1729
649.6917 | 330.1139 | 246.0842 | 227.3395
650.6917 | 330.0974 | 246.1765 | 227.499
651.6917 | 330.1265 | 246.2725 | 227.6594
652.6917 | 330.1554 | 246.4079 | 227.8167
653.6917 | 330.093 | 246.5692 | 227.9806
654.6917 | 330.0801 | 246.7166 | 228.1346
655.6917 | 330.0621 | 246.8414 | 228.2973
656.6917 | 330.0066 | 246.9623 | 228.4557
657.6917 | 329.9589 | 247.0464 | 228.6174
658.6917 | 329.9134 | 247.1188 | 228.7812
659.6917 | 329.9089 | 247.2351 | 228.9356
660.6917 | 329.9499 | 247.3468 | 229.0939
661.6917 | 329.959 | 247.4979 | 229.2443
662.6917 | 329.9388 | 247.6337 | 229.401
663.6917 | 329.9543 | 247.7687 | 229.5531
664.6917 | 329.9698 | 247.8419 | 229.7061
665.6917 | 329.9901 | 247.9562 | 229.848
666.6917 | 330.0222 | 248.1053 | 229.9967
667.6917 | 330.0031 | 248.1926 | 230.1429
668.6917 | 330.0052 | 248.2993 | 230.2872
669.6917 | 329.9894 | 248.3544 | 230.4324
670.6917 | 329.9789 | 248.4961 | 230.5844
671.6917 | 329.9394 | 248.6581 | 230.7327
672.6917 | 329.9242 | 248.8479 | 230.8818
673.6917 | 329.9604 | 248.9084 | 231.0271
674.6917 | 329.9392 | 249.0138 | 231.1783
675.6917 | 329.967 | 249.0858 | 231.3307
676.6917 | 330.031 | 249.1518 | 231.474
677.6917 | 330.0295 | 249.1423 | 231.6173
678.6917 | 330.0103 | 249.2399 | 231.7651
679.6917 | 330.0592 | 249.3918 | 231.9096
680.6917 | 330.0665 | 249.5227 | 232.0712
681.6917 | 330.0859 | 249.6373 | 232.2152
682.6917 | 330.1591 | 249.7699 | 232.3576
683.6917 | 330.2219 | 249.958 | 232.503
684.6917 | 330.2783 | 250.1249 | 232.6473
685.6917 | 330.35 | 250.2048 | 232.7855
686.6917 | 330.3905 | 250.2413 | 232.9269
687.6917 | 330.3987 | 250.3375 | 233.0753
688.6917 | 330.3954 | 250.4768 | 233.2109
689.6917 | 330.3905 | 250.6192 | 233.3514
690.6917 | 330.3641 | 250.6907 | 233.4989
691.6917 | 330.349 | 250.7498 | 233.6399
692.6917 | 330.3552 | 250.8607 | 233.7884
693.6917 | 330.3666 | 250.9666 | 233.9388
694.6917 | 330.3789 | 251.112 | 234.085
695.6917 | 330.3934 | 251.2363 | 234.2217
696.6917 | 330.4181 | 251.4037 | 234.3594
697.6917 | 330.3877 | 251.5356 | 234.4961
698.6917 | 330.3499 | 251.6032 | 234.6232
699.6917 | 330.339 | 251.7145 | 234.7576
700.6917 | 330.346 | 251.8472 | 234.8803
701.6917 | 330.3666 | 251.9788 | 235.0189
702.6917 | 330.3719 | 252.0664 | 235.1518
703.6917 | 330.3741 | 252.1857 | 235.2773
704.6917 | 330.3898 | 252.3233 | 235.3987
705.6917 | 330.4506 | 252.406 | 235.5221
706.6917 | 330.4331 | 252.4894 | 235.6439
707.6917 | 330.4647 | 252.5789 | 235.7744
708.6917 | 330.5147 | 252.7106 | 235.8974
709.6917 | 330.5384 | 252.7953 | 236.0258
710.6917 | 330.4915 | 252.8703 | 236.1434
711.6917 | 330.4637 | 252.9486 | 236.2838
712.6917 | 330.4378 | 253.0816 | 236.4059
713.6917 | 330.3783 | 253.1509 | 236.5333
714.6917 | 330.3483 | 253.2119 | 236.6495
715.6917 | 330.3634 | 253.2456 | 236.7777
716.6917 | 330.3527 | 253.3252 | 236.9067
717.6917 | 330.3126 | 253.4355 | 237.0365
718.6917 | 330.3352 | 253.5457 | 237.1578
719.6917 | 330.3613 | 253.581 | 237.2818
720.6917 | 330.349 | 253.6553 | 237.4064
721.6917 | 330.3328 | 253.7776 | 237.5255
722.6917 | 330.2795 | 253.826 | 237.6474
723.6917 | 330.2935 | 253.9243 | 237.7725
724.6917 | 330.2896 | 253.9679 | 237.8942
725.6917 | 330.2855 | 254.0373 | 238.0169
726.6917 | 330.305 | 254.1128 | 238.1316
727.6917 | 330.2824 | 254.1708 | 238.2576
728.6917 | 330.273 | 254.2567 | 238.3769
729.6917 | 330.2978 | 254.3235 | 238.4967
730.6917 | 330.2749 | 254.3775 | 238.6164
731.6917 | 330.3079 | 254.4599 | 238.7262
732.6917 | 330.3311 | 254.5369 | 238.8525
733.6917 | 330.3614 | 254.6286 | 238.9696
734.6917 | 330.3207 | 254.7048 | 239.0819
735.6917 | 330.2897 | 254.768 | 239.1957
736.6917 | 330.2838 | 254.7762 | 239.3145
737.6917 | 330.2578 | 254.7941 | 239.439
738.6917 | 330.2507 | 254.8431 | 239.5564
739.6917 | 330.2104 | 254.9361 | 239.6649
740.6917 | 330.1767 | 255.0173 | 239.7916
741.6917 | 330.167 | 255.0796 | 239.9007
742.6917 | 330.1817 | 255.1671 | 240.0173
743.6917 | 330.2319 | 255.2846 | 240.1333
744.6917 | 330.2595 | 255.3695 | 240.2373
745.6917 | 330.3101 | 255.3921 | 240.3517
746.6917 | 330.3544 | 255.4129 | 240.4548
747.6917 | 330.3599 | 255.4715 | 240.5668
748.6917 | 330.3018 | 255.5687 | 240.6754
749.6917 | 330.3167 | 255.6735 | 240.779
750.6917 | 330.3443 | 255.7205 | 240.8831
751.6917 | 330.3739 | 255.7826 | 240.9923
752.6917 | 330.3769 | 255.8684 | 241.0994
753.6917 | 330.3733 | 255.9652 | 241.1983
754.6917 | 330.3823 | 256.0534 | 241.3091
755.6917 | 330.3841 | 256.0761 | 241.4223
756.6917 | 330.3692 | 256.1317 | 241.5293
757.6917 | 330.339 | 256.1849 | 241.6319
758.6917 | 330.3556 | 256.2706 | 241.7452
759.6917 | 330.36 | 256.3341 | 241.8519
760.6917 | 330.3596 | 256.3981 | 241.9584
761.6917 | 330.3416 | 256.4576 | 242.0755
762.6917 | 330.3663 | 256.5287 | 242.1816
763.6917 | 330.3344 | 256.5941 | 242.2896
764.6917 | 330.3211 | 256.7299 | 242.4023
765.6917 | 330.3521 | 256.8084 | 242.5043
766.6917 | 330.4086 | 256.8573 | 242.6167
767.6917 | 330.3936 | 256.9593 | 242.7248
768.6917 | 330.3808 | 257.075 | 242.8259
769.6917 | 330.2808 | 257.1138 | 242.9353
770.6917 | 330.2489 | 257.1553 | 243.0329
771.6917 | 330.2494 | 257.2294 | 243.1354
772.6917 | 330.2382 | 257.3417 | 243.24
773.6917 | 330.1753 | 257.4181 | 243.3404
774.6917 | 330.1521 | 257.5166 | 243.4467
775.6917 | 330.1289 | 257.6002 | 243.5456
776.6917 | 330.1732 | 257.6723 | 243.6462
777.6917 | 330.1911 | 257.7252 | 243.7361
778.6917 | 330.1939 | 257.7801 | 243.841
779.6917 | 330.1593 | 257.8263 | 243.931
780.6917 | 330.1045 | 257.8888 | 244.0376
781.6917 | 330.0777 | 257.9531 | 244.13
782.6917 | 330.043 | 257.9811 | 244.2241
783.6917 | 330.0068 | 258.0253 | 244.3207
784.6917 | 330.0152 | 258.0797 | 244.4154
785.6917 | 330.0128 | 258.1222 | 244.5078
786.6917 | 330.0029 | 258.144 | 244.6043
787.6917 | 330.0267 | 258.1763 | 244.6969
788.6917 | 330.0428 | 258.2192 | 244.7972
789.6917 | 330.0358 | 258.287 | 244.8797
790.6917 | 330.0583 | 258.3413 | 244.9741
791.6917 | 330.0768 | 258.3877 | 245.0727
792.6917 | 330.1087 | 258.4273 | 245.1572
793.6917 | 330.1252 | 258.4736 | 245.2496
794.6917 | 330.1811 | 258.5465 | 245.3394
795.6917 | 330.222 | 258.6054 | 245.4317
796.6917 | 330.2131 | 258.6795 | 245.5214
797.6917 | 330.2245 | 258.7246 | 245.6109
798.6917 | 330.2463 | 258.764 | 245.7017
799.6917 | 330.2688 | 258.8214 | 245.8048
800.6917 | 330.3063 | 258.8333 | 245.9005
801.6917 | 330.2955 | 258.8767 | 245.9857
802.6917 | 330.3119 | 258.9139 | 246.0828
803.6917 | 330.3429 | 258.9678 | 246.1654
804.6917 | 330.4049 | 259.0264 | 246.2596
805.6917 | 330.4204 | 259.0787 | 246.3604
806.6917 | 330.4793 | 259.1309 | 246.4537
807.6917 | 330.5075 | 259.1674 | 246.5459
808.6917 | 330.5791 | 259.2147 | 246.6379
809.6917 | 330.6132 | 259.2913 | 246.7292
810.6917 | 330.6368 | 259.3581 | 246.8088
811.6917 | 330.648 | 259.4256 | 246.9015
812.6917 | 330.6679 | 259.4725 | 246.9854
813.6917 | 330.6938 | 259.5235 | 247.0749
814.6917 | 330.7079 | 259.5634 | 247.1714
815.6917 | 330.6758 | 259.6176 | 247.2506
816.6917 | 330.674 | 259.6594 | 247.3459
817.6917 | 330.6999 | 259.7053 | 247.4275
818.6917 | 330.7072 | 259.7317 | 247.5154
819.6917 | 330.6962 | 259.8024 | 247.6092
820.6917 | 330.7066 | 259.8327 | 247.6951
821.6917 | 330.718 | 259.8775 | 247.7914
822.6917 | 330.7781 | 259.9486 | 247.8722
823.6917 | 330.8416 | 259.9725 | 247.9639
824.6917 | 330.8462 | 259.986 | 248.0542
825.6917 | 330.817 | 260.0346 | 248.142
826.6917 | 330.8218 | 260.0883 | 248.2341
827.6917 | 330.802 | 260.1602 | 248.3167
828.6917 | 330.7749 | 260.2221 | 248.4103
829.6917 | 330.7585 | 260.2886 | 248.4986
830.6917 | 330.7208 | 260.3393 | 248.5866
831.6917 | 330.6612 | 260.3994 | 248.6716
832.6917 | 330.6537 | 260.4818 | 248.7671
833.6917 | 330.6921 | 260.5542 | 248.8528
834.6917 | 330.6711 | 260.6232 | 248.9398
835.6917 | 330.6506 | 260.6985 | 249.0232
836.6917 | 330.6075 | 260.7718 | 249.1112
837.6917 | 330.5361 | 260.8471 | 249.1986
838.6917 | 330.5126 | 260.9339 | 249.2905
839.6917 | 330.4667 | 261.04 | 249.3754
840.6917 | 330.426 | 261.1144 | 249.4499
841.6917 | 330.4215 | 261.2148 | 249.5464
842.6917 | 330.4072 | 261.2984 | 249.6325
843.6917 | 330.4084 | 261.388 | 249.719
844.6917 | 330.3923 | 261.4804 | 249.8049
845.6917 | 330.3611 | 261.5757 | 249.8875
846.6917 | 330.3236 | 261.6563 | 249.962
847.6917 | 330.2764 | 261.7605 | 250.0437
848.6917 | 330.251 | 261.8514 | 250.1225
849.6917 | 330.2582 | 261.936 | 250.2014
850.6917 | 330.2494 | 262.0248 | 250.274
851.6917 | 330.246 | 262.0904 | 250.3542
852.6917 | 330.267 | 262.1365 | 250.4329
853.6917 | 330.3068 | 262.2156 | 250.5151
854.6917 | 330.3559 | 262.2775 | 250.6004
855.6917 | 330.3726 | 262.3584 | 250.6729
856.6917 | 330.336 | 262.4283 | 250.7551
857.6917 | 330.2977 | 262.5071 | 250.8289
858.6917 | 330.2878 | 262.6186 | 250.9042
859.6917 | 330.2043 | 262.6703 | 250.9828
860.6917 | 330.2029 | 262.7346 | 251.0648
861.6917 | 330.2285 | 262.7796 | 251.1356
862.6917 | 330.2171 | 262.8474 | 251.208
863.6917 | 330.2122 | 262.9092 | 251.2819
864.6917 | 330.2071 | 262.9769 | 251.3574
865.6917 | 330.1706 | 263.0444 | 251.4257
866.6917 | 330.1781 | 263.089 | 251.5113
867.6917 | 330.2106 | 263.1558 | 251.5843
868.6917 | 330.224 | 263.1974 | 251.6538
869.6917 | 330.204 | 263.2382 | 251.7341
870.6917 | 330.1969 | 263.2995 | 251.8091
871.6917 | 330.1366 | 263.3408 | 251.8914
872.6917 | 330.1243 | 263.3616 | 251.971
873.6917 | 330.0892 | 263.4172 | 252.0439
874.6917 | 330.0231 | 263.464 | 252.1276
875.6917 | 330.0326 | 263.507 | 252.1987
876.6917 | 330.0273 | 263.5448 | 252.2816
877.6917 | 330.0031 | 263.5734 | 252.3481
878.6917 | 330.0149 | 263.6357 | 252.4163
879.6917 | 329.9909 | 263.6978 | 252.4799
880.6917 | 329.9716 | 263.7851 | 252.5339
881.6917 | 329.9732 | 263.8531 | 252.5823
882.6917 | 329.9789 | 263.8949 | 252.6343
883.6917 | 329.9871 | 263.9471 | 252.6835
884.6917 | 329.9923 | 264.0152 | 252.7365
885.6917 | 330.019 | 264.0755 | 252.8011
886.6917 | 330.0173 | 264.1518 | 252.875
887.6917 | 330.0506 | 264.201 | 252.9478
888.6917 | 330.0883 | 264.2452 | 253.0072
889.6917 | 330.0914 | 264.2874 | 253.0658
890.6917 | 330.1048 | 264.3343 | 253.1285
891.6917 | 330.0879 | 264.3736 | 253.1998
892.6917 | 330.0397 | 264.4278 | 253.2535
893.6917 | 330.0445 | 264.5042 | 253.3179
894.6917 | 330.0179 | 264.5658 | 253.3655
895.6917 | 329.9907 | 264.6067 | 253.4069
896.6917 | 330.0402 | 264.6461 | 253.4589
897.6917 | 330.048 | 264.7168 | 253.5084
898.6917 | 330.0599 | 264.8033 | 253.5682
899.6917 | 330.0795 | 264.8963 | 253.6215
900.6917 | 330.0881 | 264.9729 | 253.6791
901.6917 | 330.1112 | 265.0452 | 253.7318
902.6917 | 330.1404 | 265.0967 | 253.8001
903.6917 | 330.1798 | 265.1724 | 253.854
904.6917 | 330.1973 | 265.2276 | 253.9097
905.6917 | 330.2125 | 265.2989 | 253.9659
906.6917 | 330.2258 | 265.379 | 254.0389
907.6917 | 330.1868 | 265.4283 | 254.0972
908.6917 | 330.1893 | 265.4934 | 254.1682
909.6917 | 330.2121 | 265.5563 | 254.2286
910.6917 | 330.2114 | 265.6194 | 254.2986
911.6917 | 330.2338 | 265.6756 | 254.367
912.6917 | 330.302 | 265.7513 | 254.4374
913.6917 | 330.3437 | 265.8893 | 254.5019
914.6917 | 330.3687 | 265.987 | 254.562
915.6917 | 330.4078 | 266.0779 | 254.6458
916.6917 | 330.479 | 266.2172 | 254.7198
917.6917 | 330.5416 | 266.3257 | 254.7862
918.6917 | 330.6019 | 266.4312 | 254.8515
919.6917 | 330.642 | 266.5207 | 254.9235
920.6917 | 330.6421 | 266.6156 | 254.9931
921.6917 | 330.6287 | 266.6751 | 255.0604
922.6917 | 330.6682 | 266.7537 | 255.1314
923.6917 | 330.6692 | 266.7984 | 255.1888
924.6917 | 330.6556 | 266.8626 | 255.2676
925.6917 | 330.6212 | 266.8989 | 255.3253
926.6917 | 330.5415 | 266.9586 | 255.3958
927.6917 | 330.5012 | 267.0332 | 255.4678
928.6917 | 330.49 | 267.1053 | 255.5331
929.6917 | 330.5047 | 267.1602 | 255.5962
930.6917 | 330.4997 | 267.2191 | 255.6712
931.6917 | 330.4586 | 267.2586 | 255.7414
932.6917 | 330.4455 | 267.2877 | 255.8109
933.6917 | 330.4218 | 267.3073 | 255.8769
934.6917 | 330.3843 | 267.3326 | 255.9453
935.6917 | 330.2951 | 267.356 | 256.04
936.6917 | 330.2456 | 267.3855 | 256.1113
937.6917 | 330.1939 | 267.4161 | 256.1713
938.6917 | 330.1283 | 267.4554 | 256.2513
939.6917 | 330.0258 | 267.5115 | 256.3215
940.6917 | 329.964 | 267.5424 | 256.3876
941.6917 | 329.9477 | 267.5578 | 256.4697
942.6917 | 329.9294 | 267.5768 | 256.5428
943.6917 | 329.8907 | 267.6073 | 256.6067
944.6917 | 329.8765 | 267.6626 | 256.6794
945.6917 | 329.8879 | 267.7143 | 256.7496
946.6917 | 329.8829 | 267.7721 | 256.8219
947.6917 | 329.9026 | 267.8667 | 256.88
948.6917 | 329.8693 | 267.9528 | 256.9447
949.6917 | 329.8607 | 268.0197 | 257.0106
950.6917 | 329.8819 | 268.0492 | 257.0675
951.6917 | 329.8299 | 268.1316 | 257.1349
952.6917 | 329.822 | 268.2152 | 257.1972
953.6917 | 329.7904 | 268.2859 | 257.262
954.6917 | 329.7381 | 268.3267 | 257.327
955.6917 | 329.726 | 268.37 | 257.3927
956.6917 | 329.7274 | 268.3743 | 257.4607
957.6917 | 329.7909 | 268.3688 | 257.5301
958.6917 | 329.7993 | 268.3806 | 257.5902
959.6917 | 329.793 | 268.389 | 257.6503
960.6917 | 329.7415 | 268.414 | 257.7243
961.6917 | 329.7089 | 268.4376 | 257.7802
962.6917 | 329.7219 | 268.4712 | 257.8519
963.6917 | 329.7308 | 268.4515 | 257.9118
964.6917 | 329.7037 | 268.4744 | 257.9833
965.6917 | 329.7026 | 268.5117 | 258.0497
966.6917 | 329.6656 | 268.5701 | 258.1077
967.6917 | 329.6177 | 268.5804 | 258.1802
968.6917 | 329.5925 | 268.6054 | 258.2455
969.6917 | 329.6082 | 268.6482 | 258.3061
970.6917 | 329.614 | 268.693 | 258.3716
971.6917 | 329.6206 | 268.726 | 258.4394
972.6917 | 329.6549 | 268.7862 | 258.5037
973.6917 | 329.6886 | 268.8517 | 258.5586
974.6917 | 329.7378 | 268.9017 | 258.6172
975.6917 | 329.7537 | 268.9419 | 258.6866
976.6917 | 329.7533 | 268.9649 | 258.7513
977.6917 | 329.7515 | 268.9994 | 258.8018
978.6917 | 329.7132 | 269.058 | 258.8726
979.6917 | 329.7816 | 269.1177 | 258.9291
980.6917 | 329.8283 | 269.1602 | 258.9878
981.6917 | 329.8498 | 269.2157 | 259.0534
982.6917 | 329.8158 | 269.2933 | 259.1169
983.6917 | 329.7827 | 269.3417 | 259.1825
984.6917 | 329.78 | 269.3921 | 259.2593
985.6917 | 329.7963 | 269.4474 | 259.3188
986.6917 | 329.8374 | 269.5019 | 259.3897
987.6917 | 329.8363 | 269.5554 | 259.4521
988.6917 | 329.9045 | 269.5919 | 259.507
989.6917 | 329.98 | 269.6493 | 259.5653
990.6917 | 329.9749 | 269.6792 | 259.6094
991.6917 | 329.9364 | 269.6926 | 259.6544
992.6917 | 329.9061 | 269.7192 | 259.7087
993.6917 | 329.8827 | 269.7527 | 259.7525
994.6917 | 329.9139 | 269.7842 | 259.7959
995.6917 | 329.9397 | 269.8229 | 259.8481
996.6917 | 329.954 | 269.8761 | 259.9048
997.6917 | 329.9636 | 269.9058 | 259.9642
998.6917 | 329.9239 | 269.9579 | 260.015
999.6917 | 329.8932 | 270.0237 | 260.0672
1000.6917 | 329.8634 | 270.0802 | 260.121
1001.6917 | 329.9384 | 270.1192 | 260.179
1002.6917 | 330.0205 | 270.1593 | 260.2275
1003.6917 | 330.0746 | 270.1713 | 260.2823
1004.6917 | 330.1066 | 270.1822 | 260.3316
1005.6917 | 330.0637 | 270.1967 | 260.3854
1006.6917 | 330.0378 | 270.2383 | 260.4348
1007.6917 | 330.0665 | 270.3065 | 260.4937
1008.6917 | 330.0909 | 270.385 | 260.5431
1009.6917 | 330.0883 | 270.4786 | 260.5961
1010.6917 | 330.1287 | 270.5809 | 260.6474
1011.6917 | 330.1503 | 270.6683 | 260.7118
1012.6917 | 330.192 | 270.7091 | 260.7747
1013.6917 | 330.245 | 270.7314 | 260.8514
1014.6917 | 330.2635 | 270.7925 | 260.9048
1015.6917 | 330.2729 | 270.8748 | 260.9578
1016.6917 | 330.2948 | 270.9479 | 261.0094
1017.6917 | 330.2846 | 271.0076 | 261.0636
1018.6917 | 330.2539 | 271.0725 | 261.1229
1019.6917 | 330.1974 | 271.1371 | 261.1791
1020.6917 | 330.1591 | 271.2009 | 261.226
1021.6917 | 330.1624 | 271.2992 | 261.282
1022.6917 | 330.1542 | 271.3804 | 261.3479
1023.6917 | 330.14 | 271.4459 | 261.4038
1024.6917 | 330.1354 | 271.4442 | 261.457
1025.6917 | 330.1038 | 271.4825 | 261.5111
1026.6917 | 330.0794 | 271.5511 | 261.5581
1027.6917 | 330.0933 | 271.6381 | 261.6179
1028.6917 | 330.0886 | 271.7125 | 261.6688
1029.6917 | 330.0696 | 271.7676 | 261.7212
1030.6917 | 330.0348 | 271.8383 | 261.7739
1031.6917 | 329.9907 | 271.9119 | 261.8222
1032.6917 | 329.9121 | 271.9724 | 261.8759
1033.6917 | 329.8609 | 272.0622 | 261.9416
1034.6917 | 329.84 | 272.1372 | 261.9861
1035.6917 | 329.8132 | 272.1974 | 262.042
1036.6917 | 329.8256 | 272.2622 | 262.0984
1037.6917 | 329.7927 | 272.3346 | 262.1569
1038.6917 | 329.7717 | 272.3608 | 262.2058
1039.6917 | 329.7469 | 272.3714 | 262.2585
1040.6917 | 329.7536 | 272.3732 | 262.3113
1041.6917 | 329.7337 | 272.3609 | 262.3666
1042.6917 | 329.7313 | 272.3685 | 262.4105
1043.6917 | 329.6698 | 272.382 | 262.4667
1044.6917 | 329.5938 | 272.4016 | 262.5193
1045.6917 | 329.527 | 272.4168 | 262.5658
1046.6917 | 329.4971 | 272.4567 | 262.6238
1047.6917 | 329.4667 | 272.5037 | 262.6706
1048.6917 | 329.438 | 272.5642 | 262.7204
1049.6917 | 329.4283 | 272.5978 | 262.7768
1050.6917 | 329.3748 | 272.626 | 262.8342
1051.6917 | 329.3946 | 272.7017 | 262.9019
1052.6917 | 329.4636 | 272.7777 | 262.9572
1053.6917 | 329.4804 | 272.8121 | 263.0109
1054.6917 | 329.4757 | 272.8445 | 263.0637
1055.6917 | 329.4645 | 272.8842 | 263.1129
1056.6917 | 329.4882 | 272.9 | 263.1656
1057.6917 | 329.4818 | 272.8433 | 263.2036
1058.6917 | 329.4866 | 272.8211 | 263.2489
1059.6917 | 329.4879 | 272.8108 | 263.3057
1060.6917 | 329.4701 | 272.8149 | 263.3433
1061.6917 | 329.4536 | 272.8089 | 263.3907
1062.6917 | 329.4759 | 272.8245 | 263.4359
1063.6917 | 329.4971 | 272.8494 | 263.4906
1064.6917 | 329.508 | 272.9125 | 263.535
1065.6917 | 329.4863 | 272.9377 | 263.586
1066.6917 | 329.5109 | 272.952 | 263.6279
1067.6917 | 329.5109 | 272.9886 | 263.6772
1068.6917 | 329.4797 | 273.0021 | 263.7281
1069.6917 | 329.4865 | 273.0448 | 263.7692
1070.6917 | 329.493 | 273.0762 | 263.8204
1071.6917 | 329.5263 | 273.0982 | 263.876
1072.6917 | 329.5019 | 273.1485 | 263.9228
1073.6917 | 329.4882 | 273.1988 | 263.968
1074.6917 | 329.5062 | 273.1977 | 264.0145
1075.6917 | 329.5172 | 273.2232 | 264.0708
1076.6917 | 329.5338 | 273.2222 | 264.1167
1077.6917 | 329.5334 | 273.2284 | 264.1679
1078.6917 | 329.563 | 273.2336 | 264.2225
1079.6917 | 329.5911 | 273.2249 | 264.2919
1080.6917 | 329.5979 | 273.2513 | 264.3454
1081.6917 | 329.583 | 273.2615 | 264.3956
1082.6917 | 329.6555 | 273.2881 | 264.4619
1083.6917 | 329.6897 | 273.3049 | 264.5081
1084.6917 | 329.7115 | 273.3323 | 264.5648
1085.6917 | 329.7271 | 273.3917 | 264.6235
1086.6917 | 329.7697 | 273.4242 | 264.6706
1087.6917 | 329.816 | 273.461 | 264.714
1088.6917 | 329.8894 | 273.5106 | 264.7668
1089.6917 | 329.9287 | 273.5453 | 264.8182
1090.6917 | 329.9802 | 273.6017 | 264.8599
1091.6917 | 330.0448 | 273.6362 | 264.9143
1092.6917 | 330.102 | 273.6794 | 264.9754
1093.6917 | 330.1503 | 273.727 | 265.0239
1094.6917 | 330.2097 | 273.7797 | 265.0847
1095.6917 | 330.2671 | 273.8369 | 265.1298
1096.6917 | 330.2757 | 273.8316 | 265.1909
1097.6917 | 330.2803 | 273.8185 | 265.2343
1098.6917 | 330.2322 | 273.8293 | 265.2748
1099.6917 | 330.1133 | 273.859 | 265.3139
1100.6917 | 330.0699 | 273.885 | 265.3526
1101.6917 | 330.0513 | 273.925 | 265.3958
1102.6917 | 330.0373 | 273.9575 | 265.4377
1103.6917 | 330.0091 | 273.9915 | 265.4946
1104.6917 | 330.0378 | 274.0246 | 265.549
1105.6917 | 330.0482 | 274.0779 | 265.5886
1106.6917 | 330.0365 | 274.1335 | 265.6293
1107.6917 | 330.0513 | 274.1495 | 265.6609
1108.6917 | 330.0367 | 274.1469 | 265.6982
1109.6917 | 329.9727 | 274.1568 | 265.7439
1110.6917 | 329.9419 | 274.2035 | 265.7906
1111.6917 | 329.9529 | 274.2549 | 265.8401
1112.6917 | 329.9626 | 274.2877 | 265.8891
1113.6917 | 329.9266 | 274.2807 | 265.931
1114.6917 | 329.8416 | 274.3038 | 265.9544
1115.6917 | 329.7742 | 274.3252 | 266.0164
1116.6917 | 329.8148 | 274.3739 | 266.0653
1117.6917 | 329.8656 | 274.4031 | 266.1221
1118.6917 | 329.8334 | 274.4284 | 266.1547
1119.6917 | 329.7748 | 274.4554 | 266.192
1120.6917 | 329.7791 | 274.4763 | 266.2302
1121.6917 | 329.7908 | 274.4907 | 266.2705
1122.6917 | 329.777 | 274.529 | 266.3146
1123.6917 | 329.7494 | 274.5436 | 266.3662
1124.6917 | 329.7325 | 274.5481 | 266.4159
1125.6917 | 329.7384 | 274.5599 | 266.4625
1126.6917 | 329.7786 | 274.621 | 266.4972
1127.6917 | 329.849 | 274.6267 | 266.5356
1128.6917 | 329.8811 | 274.6444 | 266.5713
1129.6917 | 329.9333 | 274.6578 | 266.6102
1130.6917 | 329.9582 | 274.6846 | 266.6578
1131.6917 | 330.0022 | 274.7086 | 266.6972
1132.6917 | 330.0383 | 274.7315 | 266.7449
1133.6917 | 330.0383 | 274.7326 | 266.7877
1134.6917 | 330.0227 | 274.7094 | 266.8208
1135.6917 | 330.0526 | 274.7141 | 266.8607
1136.6917 | 330.1524 | 274.7443 | 266.9039
1137.6917 | 330.1957 | 274.7838 | 266.9343
1138.6917 | 330.1459 | 274.8054 | 266.9825
1139.6917 | 330.1238 | 274.8288 | 267.0263
1140.6917 | 330.1514 | 274.8823 | 267.0606
1141.6917 | 330.1873 | 275.1531 | 267.1006
1142.6917 | 330.2892 | 275.3553 | 267.1517
1143.6917 | 330.4172 | 275.5401 | 267.1878
1144.6917 | 330.4759 | 275.7327 | 267.2202
1145.6917 | 330.4572 | 275.909 | 267.264
1146.6917 | 330.487 | 276.1519 | 267.2391
1147.6917 | 330.5432 | 277.3141 | 267.3521
1148.6917 | 330.6562 | 277.772 | 267.3985
1149.6917 | 330.6589 | 278.1159 | 267.4387
1150.6917 | 330.5547 | 278.3594 | 267.494
1151.6917 | 330.464 | 278.5753 | 267.536
1152.6917 | 330.4277 | 278.7394 | 267.5828
1153.6917 | 330.386 | 278.8419 | 267.6237
1154.6917 | 330.3909 | 278.9211 | 267.6825
1155.6917 | 330.3525 | 278.9288 | 267.7284
1156.6917 | 330.2753 | 278.8657 | 267.7794
1157.6917 | 330.1688 | 278.8476 | 267.8291
1158.6917 | 330.1082 | 278.7808 | 267.8713
1159.6917 | 330.0652 | 278.7024 | 267.9214
1160.6917 | 330.0384 | 278.6169 | 267.9757
1161.6917 | 329.9807 | 278.5297 | 268.0262
1162.6917 | 329.9237 | 278.4666 | 268.0787
1163.6917 | 329.915 | 278.3901 | 268.1244
1164.6917 | 329.9469 | 278.2547 | 268.1706
1165.6917 | 329.961 | 278.1367 | 268.2136
1166.6917 | 329.9552 | 278.0145 | 268.2674
1167.6917 | 329.9908 | 277.9062 | 268.3071
1168.6917 | 330.0228 | 277.8272 | 268.3526
1169.6917 | 330.0081 | 277.749 | 268.4077
1170.6917 | 329.9777 | 277.6559 | 268.4546
1171.6917 | 329.9863 | 277.5737 | 268.4995
1172.6917 | 330.0218 | 277.4772 | 268.5537
1173.6917 | 330.0123 | 277.3923 | 268.5916
1174.6917 | 330.0465 | 277.3278 | 268.6372
1175.6917 | 330.0771 | 277.2869 | 268.6762
1176.6917 | 330.0962 | 277.2557 | 268.7229
1177.6917 | 330.064 | 277.2277 | 268.7683
1178.6917 | 329.9968 | 277.1475 | 268.8095
1179.6917 | 329.925 | 277.0888 | 268.8436
1180.6917 | 329.8824 | 277.0387 | 268.8832
1181.6917 | 329.8337 | 276.9982 | 268.9317
1182.6917 | 329.8658 | 276.9504 | 268.9705
1183.6917 | 329.884 | 276.9237 | 269.0068
1184.6917 | 329.8813 | 276.8895 | 269.0572
1185.6917 | 329.8529 | 276.8735 | 269.093
1186.6917 | 329.8627 | 276.8531 | 269.1457
1187.6917 | 329.8025 | 276.8305 | 269.1755
1188.6917 | 329.8303 | 276.8394 | 269.2089
1189.6917 | 329.8546 | 276.8331 | 269.2532
1190.6917 | 329.8131 | 276.8126 | 269.2899
1191.6917 | 329.8027 | 276.7947 | 269.3055
1192.6917 | 329.8218 | 276.7715 | 269.3515
1193.6917 | 329.8185 | 276.7805 | 269.3918
1194.6917 | 329.7719 | 276.7942 | 269.429
1195.6917 | 329.7247 | 276.7909 | 269.4643
1196.6917 | 329.7387 | 276.8026 | 269.4931
1197.6917 | 329.7588 | 276.7802 | 269.5259
1198.6917 | 329.8197 | 276.737 | 269.5596
1199.6917 | 329.8506 | 276.7158 | 269.5916
1200.6917 | 329.8184 | 276.7102 | 269.6083
1201.6917 | 329.8131 | 276.6892 | 269.6626
1202.6917 | 329.8638 | 276.6905 | 269.6967
1203.6917 | 329.8699 | 276.6671 | 269.7319
1204.6917 | 329.8172 | 276.6565 | 269.7761
1205.6917 | 329.7558 | 276.6199 | 269.8041
1206.6917 | 329.7207 | 276.571 | 269.836
1207.6917 | 329.7617 | 276.5347 | 269.8768
1208.6917 | 329.8436 | 276.5016 | 269.9104
1209.6917 | 329.911 | 276.5083 | 269.9466
1210.6917 | 329.9744 | 276.4985 | 269.9718
1211.6917 | 330.0228 | 276.4998 | 270.0068
1212.6917 | 330.0079 | 276.5141 | 270.0347
1213.6917 | 329.9939 | 276.5023 | 270.065
1214.6917 | 329.9795 | 276.4635 | 270.0911
1215.6917 | 329.9698 | 276.4642 | 270.125
1216.6917 | 329.975 | 276.4693 | 270.1654
1217.6917 | 329.9903 | 276.4592 | 270.1949
1218.6917 | 329.9712 | 276.4618 | 270.2279
1219.6917 | 330.0519 | 276.4483 | 270.2782
1220.6917 | 330.1128 | 276.4481 | 270.3033
1221.6917 | 330.1367 | 276.4855 | 270.3419
1222.6917 | 330.1495 | 276.5075 | 270.3695
1223.6917 | 330.1676 | 276.5449 | 270.3994
1224.6917 | 330.1677 | 276.587 | 270.427
1225.6917 | 330.2177 | 276.6221 | 270.4552
1226.6917 | 330.2402 | 276.6351 | 270.4868
1227.6917 | 330.2207 | 276.6081 | 270.5081
1228.6917 | 330.2041 | 276.6327 | 270.5421
1229.6917 | 330.2076 | 276.6668 | 270.5751
1230.6917 | 330.2137 | 276.7161 | 270.6197
1231.6917 | 330.2022 | 276.7778 | 270.6529
1232.6917 | 330.2395 | 276.7723 | 270.6786
1233.6917 | 330.2357 | 276.7459 | 270.7098
1234.6917 | 330.237 | 276.7434 | 270.7363
1235.6917 | 330.2849 | 276.7471 | 270.7644
1236.6917 | 330.2735 | 276.7213 | 270.796
1237.6917 | 330.2712 | 276.6715 | 270.8212
1238.6917 | 330.2843 | 276.6617 | 270.8508
1239.6917 | 330.2726 | 276.656 | 270.8791
1240.6917 | 330.2618 | 276.6794 | 270.9039
1241.6917 | 330.2908 | 276.6646 | 270.9391
1242.6917 | 330.3148 | 276.6355 | 270.9727
1243.6917 | 330.321 | 276.6244 | 271.0011
1244.6917 | 330.3734 | 276.6479 | 271.0294
1245.6917 | 330.3597 | 276.6661 | 271.0638
1246.6917 | 330.3641 | 276.7026 | 271.1034
1247.6917 | 330.3337 | 276.7096 | 271.1268
1248.6917 | 330.3225 | 276.6955 | 271.154
1249.6917 | 330.3076 | 276.6128 | 271.1857
1250.6917 | 330.3105 | 276.5799 | 271.2129
1251.6917 | 330.3489 | 276.5531 | 271.2337
1252.6917 | 330.3733 | 276.5735 | 271.2653
1253.6917 | 330.4179 | 276.61 | 271.2924
1254.6917 | 330.4521 | 276.5936 | 271.3143
1255.6917 | 330.475 | 276.5431 | 271.3445
1256.6917 | 330.4321 | 276.5295 | 271.3725
1257.6917 | 330.3975 | 276.5159 | 271.3917
1258.6917 | 330.352 | 276.5203 | 271.4189
1259.6917 | 330.3259 | 276.546 | 271.443
1260.6917 | 330.2867 | 276.525 | 271.4729
1261.6917 | 330.2565 | 276.4987 | 271.4988
1262.6917 | 330.2281 | 276.4858 | 271.528
1263.6917 | 330.2192 | 276.4869 | 271.5456
1264.6917 | 330.2126 | 276.4996 | 271.5709
1265.6917 | 330.2361 | 276.5475 | 271.6021
1266.6917 | 330.2044 | 276.5272 | 271.6311
1267.6917 | 330.1766 | 276.5258 | 271.657
1268.6917 | 330.136 | 276.545 | 271.6884
1269.6917 | 330.1754 | 276.5499 | 271.7073
1270.6917 | 330.1607 | 276.5402 | 271.7336
1271.6917 | 330.1732 | 276.5256 | 271.7598
1272.6917 | 330.1753 | 276.5172 | 271.783
1273.6917 | 330.1623 | 276.5095 | 271.8102
1274.6917 | 330.1442 | 276.5483 | 271.8421
1275.6917 | 330.0966 | 276.5453 | 271.8614
1276.6917 | 330.0312 | 276.5453 | 271.8886
1277.6917 | 329.9599 | 276.5951 | 271.909
1278.6917 | 329.8993 | 276.6021 | 271.9267
1279.6917 | 329.8773 | 276.6006 | 271.9598
1280.6917 | 329.8449 | 276.5956 | 271.9857
1281.6917 | 329.8118 | 276.601 | 272.0255
1282.6917 | 329.8117 | 276.5888 | 272.0432
1283.6917 | 329.8428 | 276.577 | 272.0774
1284.6917 | 329.801 | 276.535 | 272.1086
1285.6917 | 329.7225 | 276.5199 | 272.1341
1286.6917 | 329.6587 | 276.5563 | 272.1664
1287.6917 | 329.6723 | 276.5737 | 272.2071
1288.6917 | 329.6904 | 276.6046 | 272.2245
1289.6917 | 329.6436 | 276.5905 | 272.2406
1290.6917 | 329.5279 | 276.5666 | 272.2636
1291.6917 | 329.3852 | 276.5241 | 272.2928
1292.6917 | 329.3259 | 276.4914 | 272.315
1293.6917 | 329.3603 | 276.4641 | 272.3417
1294.6917 | 329.354 | 276.4133 | 272.367
1295.6917 | 329.3112 | 276.3812 | 272.3893
1296.6917 | 329.3092 | 276.3772 | 272.4292
1297.6917 | 329.3074 | 276.4043 | 272.4423
1298.6917 | 329.3138 | 276.4176 | 272.4631
1299.6917 | 329.3351 | 276.4143 | 272.4814
1300.6917 | 329.3358 | 276.3923 | 272.5068
1301.6917 | 329.3697 | 276.4101 | 272.536
1302.6917 | 329.4687 | 276.4615 | 272.5624
1303.6917 | 329.4949 | 276.5025 | 272.5774
1304.6917 | 329.5226 | 276.4649 | 272.6051
1305.6917 | 329.4954 | 276.4384 | 272.6177
1306.6917 | 329.4251 | 276.4375 | 272.6345
1307.6917 | 329.4126 | 276.4469 | 272.6511
1308.6917 | 329.419 | 276.4753 | 272.6783
1309.6917 | 329.4303 | 276.4694 | 272.7073
1310.6917 | 329.4482 | 276.4869 | 272.7318
1311.6917 | 329.468 | 276.506 | 272.7543
1312.6917 | 329.5665 | 276.5192 | 272.7784
1313.6917 | 329.5886 | 276.5496 | 272.8012
1314.6917 | 329.5788 | 276.5934 | 272.8165
1315.6917 | 329.5734 | 276.5801 | 272.8426
1316.6917 | 329.5752 | 276.5642 | 272.8591
1317.6917 | 329.5579 | 276.5434 | 272.8767
1318.6917 | 329.5294 | 276.5521 | 272.8883
1319.6917 | 329.5152 | 276.5698 | 272.9169
1320.6917 | 329.5663 | 276.5718 | 272.9435
1321.6917 | 329.5921 | 276.5826 | 272.9463
1322.6917 | 329.563 | 276.5831 | 272.9825
1323.6917 | 329.4962 | 276.5919 | 272.9999
1324.6917 | 329.4901 | 276.6092 | 273.017
1325.9573 | 329.5279 | 276.6663 | 273.0537
1326.6917 | 329.5384 | 276.6206 | 273.0779
1327.6917 | 329.5544 | 276.5828 | 273.0923
1328.6917 | 329.5858 | 276.5688 | 273.1105
1329.7229 | 329.5664 | 276.5927 | 273.1263
1330.6917 | 329.5839 | 276.6039 | 273.1592
1331.6917 | 329.5689 | 276.6341 | 273.1878
1332.6917 | 329.583 | 276.6506 | 273.2089
1333.6917 | 329.6775 | 276.6614 | 273.2219
1334.6917 | 329.7431 | 276.6361 | 273.24
1335.6917 | 329.8229 | 276.6514 | 273.2567
1336.6917 | 329.8622 | 276.6773 | 273.2841
1337.6917 | 329.8737 | 276.6925 | 273.3141
1338.6917 | 329.8612 | 276.6924 | 273.3229
1339.6917 | 329.9125 | 276.702 | 273.3381
1340.6917 | 329.9558 | 276.7264 | 273.3696
1341.6917 | 330.0358 | 276.7598 | 273.3869
1342.6917 | 330.0576 | 276.7563 | 273.405
1343.6917 | 330.0233 | 276.7786 | 273.424
1344.6917 | 330.0265 | 276.8326 | 273.4461
1345.6917 | 330.0758 | 276.8701 | 273.4722
1346.6917 | 330.1245 | 276.8994 | 273.4872
1347.6917 | 330.2126 | 276.9149 | 273.5241
1348.6917 | 330.2374 | 276.9301 | 273.5451
1349.6917 | 330.2592 | 276.9805 | 273.5487
1350.6917 | 330.2735 | 276.9893 | 273.5751
1351.6917 | 330.2942 | 276.9806 | 273.6096
1352.6917 | 330.346 | 276.9936 | 273.6289
1353.6917 | 330.3997 | 277.0319 | 273.6366
1354.6917 | 330.4581 | 277.0251 | 273.6627
1355.6917 | 330.48 | 277.0886 | 273.698
1356.6917 | 330.4604 | 277.1318 | 273.7108
1357.6917 | 330.4518 | 277.157 | 273.7461
1358.6917 | 330.4159 | 277.2002 | 273.764
1359.6917 | 330.4175 | 277.2747 | 273.7692
1360.6917 | 330.3598 | 277.3307 | 273.7983
1361.6917 | 330.3462 | 277.3614 | 273.8254
1362.6917 | 330.3109 | 277.3498 | 273.8484
1363.6917 | 330.2068 | 277.3513 | 273.865
1364.6917 | 330.1389 | 277.3593 | 273.8974
1365.6917 | 330.1559 | 277.4062 | 273.9116
1366.6917 | 330.1668 | 277.4043 | 273.9408
1367.6917 | 330.1974 | 277.3714 | 273.9576
1368.6917 | 330.1996 | 277.3291 | 273.9744
1369.6917 | 330.1982 | 277.322 | 273.9874
1370.6917 | 330.1329 | 277.3196 | 274.0102
1371.6917 | 330.1257 | 277.3275 | 274.035
1372.6917 | 330.1722 | 277.3533 | 274.0595
1373.6917 | 330.1951 | 277.3357 | 274.0704
1374.6917 | 330.1873 | 277.3675 | 274.0913
1375.6917 | 330.172 | 277.4057 | 274.1073
1376.6917 | 330.1483 | 277.4612 | 274.1246
1377.6917 | 330.1042 | 277.4937 | 274.1499
1378.6917 | 330.0608 | 277.5161 | 274.1665
1379.6917 | 329.9997 | 277.5406 | 274.185
1380.6917 | 329.9585 | 277.5411 | 274.2069
1381.6917 | 329.9125 | 277.5568 | 274.2273
1382.6917 | 329.8308 | 277.5874 | 274.243
1383.6917 | 329.8359 | 277.5905 | 274.2619
1384.6917 | 329.8128 | 277.5856 | 274.2766
1385.6917 | 329.8284 | 277.6117 | 274.2985
1386.6917 | 329.8097 | 277.6187 | 274.3246
1387.6917 | 329.8209 | 277.6151 | 274.3402
1388.6917 | 329.8501 | 277.6437 | 274.354
1389.6917 | 329.8523 | 277.6532 | 274.3677
1390.6917 | 329.857 | 277.6742 | 274.3809
1391.6917 | 329.8553 | 277.7005 | 274.4078
1392.6917 | 329.8675 | 277.7081 | 274.412
1393.6917 | 329.8799 | 277.7171 | 274.4391
1394.6917 | 329.9343 | 277.6528 | 274.4548
1395.6917 | 329.943 | 277.6316 | 274.4779
1396.6917 | 329.9007 | 277.6638 | 274.5013
1397.6917 | 329.9029 | 277.6855 | 274.5119
1398.6917 | 329.9099 | 277.6756 | 274.531
1399.6917 | 329.9195 | 277.69 | 274.558
1400.6917 | 329.9338 | 277.6788 | 274.5681
1401.6917 | 329.8908 | 277.7317 | 274.5998
1402.6917 | 329.8512 | 277.7536 | 274.6116
1403.6917 | 329.8488 | 277.7554 | 274.6288
1404.6917 | 329.8006 | 277.7566 | 274.6533
1405.6917 | 329.7798 | 277.7328 | 274.6644
1406.6917 | 329.7854 | 277.7518 | 274.6842
1407.6917 | 329.7826 | 277.789 | 274.6947
1408.6917 | 329.7981 | 277.823 | 274.7146
1409.6917 | 329.8274 | 277.8493 | 274.7252
1410.6917 | 329.8789 | 277.8525 | 274.7481
1411.6917 | 329.9528 | 277.9028 | 274.7606
1412.6917 | 330.0207 | 277.9426 | 274.7707
1413.6917 | 330.0528 | 277.9695 | 274.7868
1414.6917 | 330.0498 | 278.0184 | 274.803
1415.6917 | 330.0676 | 278.0723 | 274.8238
1416.6917 | 330.0994 | 278.1223 | 274.8441
1417.6917 | 330.0843 | 278.1444 | 274.8538
1418.6917 | 330.0915 | 278.1714 | 274.8725
1419.6917 | 330.1023 | 278.1454 | 274.8824
1420.6917 | 330.1466 | 278.1446 | 274.8981
1421.6917 | 330.1867 | 278.1529 | 274.9219
1422.6917 | 330.1726 | 278.1761 | 274.9382
1423.6917 | 330.1731 | 278.1667 | 274.9562
1424.6917 | 330.1484 | 278.1909 | 274.9762
1425.6917 | 330.1614 | 278.2107 | 274.9967
1426.6917 | 330.1902 | 278.2513 | 275.0152
1427.6917 | 330.2273 | 278.2914 | 275.0288
1428.6917 | 330.2443 | 278.3062 | 275.0499
1429.6917 | 330.2316 | 278.3513 | 275.0702
1430.6917 | 330.2259 | 278.3986 | 275.0977
1431.6917 | 330.2312 | 278.4441 | 275.1162
1432.6917 | 330.164 | 278.4794 | 275.1412
1433.6917 | 330.1273 | 278.5215 | 275.1608
1434.6917 | 330.1077 | 278.5492 | 275.1733
1435.6917 | 330.1111 | 278.5764 | 275.1935
1436.6917 | 330.1309 | 278.6048 | 275.2178
1437.6917 | 330.1437 | 278.5743 | 275.2351
1438.6917 | 330.1179 | 278.5435 | 275.2571
1439.6917 | 330.0954 | 278.5404 | 275.278
1440.6917 | 330.0458 | 278.5072 | 275.2885
1441.6917 | 330.0157 | 278.4975 | 275.3111
1442.6917 | 330.0172 | 278.4798 | 275.3266
1443.6917 | 330.0172 | 278.4572 | 275.3374
1444.6917 | 330.0079 | 278.4471 | 275.3534
1445.6917 | 330.006 | 278.4413 | 275.3758
1446.6917 | 329.9656 | 278.427 | 275.396
1447.6917 | 329.8604 | 278.4329 | 275.4081
1448.6917 | 329.8012 | 278.4365 | 275.4336
1449.6917 | 329.7754 | 278.4067 | 275.4534
1450.6917 | 329.7664 | 278.4158 | 275.4695
1451.6917 | 329.7284 | 278.4506 | 275.4878
1452.6917 | 329.7308 | 278.4681 | 275.5054
1453.6917 | 329.7279 | 278.4593 | 275.5172
1454.6917 | 329.7036 | 278.4261 | 275.5364
1455.6917 | 329.6898 | 278.4152 | 275.5605
1456.6917 | 329.6934 | 278.4412 | 275.5829
1457.6917 | 329.7129 | 278.4663 | 275.5973
1458.6917 | 329.6504 | 278.4746 | 275.6073
1459.6917 | 329.5954 | 278.4699 | 275.6244
1460.6917 | 329.5424 | 278.4483 | 275.6419
1461.6917 | 329.5232 | 278.4689 | 275.6656
1462.6917 | 329.5235 | 278.5232 | 275.6884
1463.6917 | 329.5972 | 278.5796 | 275.7073
1464.6917 | 329.6559 | 278.6165 | 275.7199
1465.6917 | 329.6781 | 278.6008 | 275.7354
1466.6917 | 329.6929 | 278.6484 | 275.7495
1467.6917 | 329.7126 | 278.7015 | 275.7739
1468.6917 | 329.7591 | 278.7535 | 275.7921
1469.6917 | 329.7166 | 278.7647 | 275.8133
1470.6917 | 329.7046 | 278.7495 | 275.8278
1471.6917 | 329.7034 | 278.7529 | 275.8415
1472.6917 | 329.7005 | 278.8072 | 275.8623
1473.6917 | 329.6807 | 278.8468 | 275.8804
1474.6917 | 329.6416 | 278.8976 | 275.8989
1475.6917 | 329.6174 | 278.9225 | 275.9151
1476.6917 | 329.5519 | 278.9392 | 275.9267
1477.6917 | 329.4906 | 278.9559 | 275.9474
1478.6917 | 329.483 | 278.9643 | 275.9621
1479.6917 | 329.5265 | 278.9397 | 275.9834
1480.6917 | 329.4786 | 278.9431 | 276.0014
1481.6917 | 329.4427 | 278.9436 | 276.0125
1482.6917 | 329.3737 | 278.9528 | 276.0385
1483.6917 | 329.3429 | 278.9718 | 276.0549
1484.6917 | 329.3502 | 278.9644 | 276.0603
1485.6917 | 329.3918 | 278.9728 | 276.078
1486.6917 | 329.4157 | 278.9835 | 276.0896
1487.6917 | 329.3928 | 279.0335 | 276.1075
1488.6917 | 329.3522 | 279.0747 | 276.119
1489.6917 | 329.299 | 279.0851 | 276.1373
1490.6917 | 329.3167 | 279.0999 | 276.1554
1491.6917 | 329.3011 | 279.094 | 276.1631
1492.6917 | 329.3348 | 279.0735 | 276.1719
1493.6917 | 329.3466 | 279.1005 | 276.1912
1494.6917 | 329.327 | 279.1317 | 276.2088
1495.6917 | 329.3009 | 279.1497 | 276.2219
1496.6917 | 329.2634 | 279.187 | 276.2382
1497.6917 | 329.2864 | 279.1613 | 276.2509
1498.6917 | 329.2957 | 279.1954 | 276.2708
1499.6917 | 329.2949 | 279.2215 | 276.2824
1500.6917 | 329.3583 | 279.2192 | 276.2943
1501.6917 | 329.4176 | 279.293 | 276.3123
1502.6917 | 329.4836 | 279.345 | 276.3324
1503.6917 | 329.5526 | 279.3794 | 276.3482
1504.6917 | 329.5591 | 279.3997 | 276.3602
1505.6917 | 329.6297 | 279.4072 | 276.377
1506.6917 | 329.6839 | 279.4466 | 276.3904
1507.6917 | 329.7083 | 279.4922 | 276.4067
1508.6917 | 329.7113 | 279.5399 | 276.4257
1509.6917 | 329.7052 | 279.5616 | 276.4388
1510.6917 | 329.6622 | 279.5717 | 276.4594
1511.6917 | 329.6399 | 279.5866 | 276.4759
1512.6917 | 329.6475 | 279.6082 | 276.4934
1513.6917 | 329.6706 | 279.6444 | 276.5048
1514.6917 | 329.6866 | 279.6789 | 276.5268
1515.6917 | 329.7016 | 279.7194 | 276.5393
1516.6917 | 329.706 | 279.7124 | 276.5557
1517.6917 | 329.6923 | 279.7048 | 276.5748
1518.6917 | 329.7514 | 279.7323 | 276.5825
1519.6917 | 329.7797 | 279.7721 | 276.5934
1520.6917 | 329.83 | 279.7869 | 276.6149
1521.6917 | 329.8826 | 279.8017 | 276.6289
1522.6917 | 329.9224 | 279.8232 | 276.6367
1523.6917 | 329.9197 | 279.8323 | 276.6523
1524.6917 | 329.9533 | 279.8639 | 276.6772
1525.6917 | 330.0128 | 279.8987 | 276.694
1526.6917 | 330.0643 | 279.9208 | 276.7022
1527.6917 | 330.0798 | 279.9398 | 276.7233
1528.6917 | 330.081 | 279.9234 | 276.7411
1529.6917 | 330.0671 | 279.9434 | 276.7541
1530.6917 | 330.0549 | 279.9403 | 276.7675
1531.6917 | 329.9723 | 279.9408 | 276.7923
1532.6917 | 329.966 | 279.9633 | 276.809
1533.6917 | 329.967 | 280.0137 | 276.8191
1534.6917 | 330.003 | 280.0241 | 276.8372
1535.6917 | 330.0481 | 280.0052 | 276.851
1536.6917 | 330.0574 | 280.022 | 276.8637
1537.6917 | 330.0564 | 280.0422 | 276.8732
1538.6917 | 330.0817 | 280.0806 | 276.8947
1539.6917 | 330.1296 | 280.1669 | 276.9071
1540.6917 | 330.159 | 280.1641 | 276.9177
1541.6917 | 330.1746 | 280.1525 | 276.9329
1542.6917 | 330.153 | 280.162 | 276.9482
1543.6917 | 330.1463 | 280.2041 | 276.9639
1544.6917 | 330.1235 | 280.2788 | 276.9856
1545.6917 | 330.0868 | 280.3051 | 277.0066
1546.6917 | 330.0627 | 280.3113 | 277.0204
1547.6917 | 330.0748 | 280.3414 | 277.0411
1548.6917 | 330.0518 | 280.3968 | 277.0568
1549.6917 | 330.0277 | 280.4541 | 277.073
1550.6917 | 330.0072 | 280.4627 | 277.0962
1551.6917 | 329.9896 | 280.4456 | 277.1118
1552.6917 | 329.9585 | 280.442 | 277.1177
1553.6917 | 329.8893 | 280.4719 | 277.1395
1554.6917 | 329.88 | 280.4945 | 277.1633
1555.6917 | 329.8805 | 280.5036 | 277.1795
1556.6917 | 329.8802 | 280.497 | 277.1997
1557.6917 | 329.8614 | 280.5109 | 277.2203
1558.6917 | 329.8698 | 280.5265 | 277.2315
1559.6917 | 329.8491 | 280.5385 | 277.2556
1560.6917 | 329.8348 | 280.5729 | 277.274
1561.6917 | 329.807 | 280.6007 | 277.2882
1562.6917 | 329.784 | 280.6341 | 277.3007
1563.6917 | 329.7574 | 280.646 | 277.3129
1564.6917 | 329.6633 | 280.6416 | 277.3359
1565.6917 | 329.5577 | 280.6736 | 277.3447
1566.6917 | 329.5032 | 280.729 | 277.3622
1567.6917 | 329.4838 | 280.7625 | 277.3753
1568.6917 | 329.416 | 280.8123 | 277.3915
1569.6917 | 329.4336 | 280.7923 | 277.3988
1570.6917 | 329.4381 | 280.797 | 277.4195
1571.6917 | 329.401 | 280.8246 | 277.4259
1572.6917 | 329.3652 | 280.8436 | 277.4443
1573.6917 | 329.3446 | 280.8432 | 277.4601
1574.6917 | 329.3669 | 280.8802 | 277.4682
1575.6917 | 329.4182 | 280.9028 | 277.4845
1576.6917 | 329.4872 | 280.9269 | 277.4994
1577.6917 | 329.5353 | 280.9593 | 277.5175
1578.6917 | 329.5632 | 281.0168 | 277.5347
1579.6917 | 329.5679 | 281.0784 | 277.5469
1580.6917 | 329.5062 | 281.1216 | 277.5719
1581.6917 | 329.4972 | 281.1525 | 277.5801
1582.6917 | 329.5094 | 281.1864 | 277.5995
1583.6917 | 329.5114 | 281.2366 | 277.618
1584.6917 | 329.5223 | 281.2574 | 277.6428
1585.6917 | 329.5375 | 281.2867 | 277.6519
1586.6917 | 329.5316 | 281.3111 | 277.6657
1587.6917 | 329.5462 | 281.3099 | 277.6844
1588.6917 | 329.5507 | 281.2966 | 277.6933
1589.6917 | 329.517 | 281.3022 | 277.7141
1590.6917 | 329.4828 | 281.3885 | 277.7377
1591.6917 | 329.4709 | 281.4585 | 277.7438
1592.6917 | 329.4886 | 281.5111 | 277.7563
1593.6917 | 329.5078 | 281.5358 | 277.7662
1594.6917 | 329.5517 | 281.5217 | 277.7821
1595.6917 | 329.6095 | 281.5805 | 277.7973
1596.6917 | 329.6479 | 281.6399 | 277.8121
1597.6917 | 329.6992 | 281.6731 | 277.8249
1598.6917 | 329.7708 | 281.6753 | 277.8459
1599.6917 | 329.7769 | 281.6452 | 277.8561
1600.6917 | 329.7901 | 281.6411 | 277.8678
1601.6917 | 329.8268 | 281.6207 | 277.8854
1602.6917 | 329.8389 | 281.6243 | 277.9068
1603.6917 | 329.8005 | 281.6661 | 277.9178
1604.6917 | 329.8114 | 281.6591 | 277.932
1605.6917 | 329.8021 | 281.6753 | 277.9474
1606.6917 | 329.7337 | 281.6979 | 277.9636
1607.6917 | 329.665 | 281.7243 | 277.9758
1608.6917 | 329.6829 | 281.7328 | 277.9962
1609.6917 | 329.6823 | 281.73 | 278.0073
1610.6917 | 329.6567 | 281.7217 | 278.022
1611.6917 | 329.6032 | 281.7104 | 278.0397
1612.6917 | 329.6148 | 281.738 | 278.0518
1613.6917 | 329.6232 | 281.7425 | 278.0734
1614.6917 | 329.6231 | 281.7757 | 278.0888
1615.6917 | 329.6217 | 281.766 | 278.1036
1616.6917 | 329.6314 | 281.7329 | 278.1227
1617.6917 | 329.5596 | 281.7066 | 278.1402
1618.6917 | 329.5352 | 281.7017 | 278.1517
1619.6917 | 329.5526 | 281.6855 | 278.1709
1620.6917 | 329.5503 | 281.679 | 278.1842
1621.6917 | 329.5867 | 281.7056 | 278.2015
1622.6917 | 329.6197 | 281.7574 | 278.2133
1623.6917 | 329.6431 | 281.8008 | 278.2322
1624.6917 | 329.6557 | 281.8339 | 278.2535
1625.6917 | 329.6428 | 281.8312 | 278.2575
1626.6917 | 329.6413 | 281.8136 | 278.2804
1627.6917 | 329.66 | 281.7833 | 278.2935
1628.6917 | 329.6931 | 281.7685 | 278.3067
1629.6917 | 329.6877 | 281.784 | 278.3229
1630.6917 | 329.6963 | 281.8062 | 278.3338
1631.6917 | 329.7784 | 281.8332 | 278.3524
1632.6917 | 329.7908 | 281.8464 | 278.3701
1633.6917 | 329.797 | 281.8332 | 278.384
1634.6917 | 329.8301 | 281.8465 | 278.4031
1635.6917 | 329.8838 | 281.8923 | 278.4186
1636.6917 | 329.9193 | 281.928 | 278.4277
1637.6917 | 329.8533 | 281.9574 | 278.45
1638.6917 | 329.8025 | 281.955 | 278.4612
1639.6917 | 329.8113 | 281.8809 | 278.467
1640.6917 | 329.845 | 281.9 | 278.4829
1641.6917 | 329.868 | 281.8882 | 278.4901
1642.6917 | 329.9273 | 281.865 | 278.5108
1643.6917 | 329.9631 | 281.9046 | 278.5176
1644.6917 | 330.0027 | 281.9402 | 278.5324
1645.6917 | 330.0486 | 281.961 | 278.5415
1646.6917 | 330.0984 | 282.0193 | 278.5615
1647.6917 | 330.1225 | 282.0151 | 278.5756
1648.6917 | 330.1924 | 282.0102 | 278.5877
1649.6917 | 330.221 | 282.0426 | 278.6051
1650.6917 | 330.2759 | 282.0892 | 278.6216
1651.6917 | 330.341 | 282.0888 | 278.6286
1652.6917 | 330.3344 | 282.0645 | 278.6434
1653.6917 | 330.3334 | 282.0122 | 278.6597
1654.6917 | 330.381 | 282.0122 | 278.6703
1655.6917 | 330.4403 | 282.0432 | 278.6817
1656.6917 | 330.4892 | 282.0693 | 278.6986
1657.6917 | 330.5035 | 282.1184 | 278.7113
1658.6917 | 330.4681 | 282.103 | 278.7235
1659.6917 | 330.4314 | 282.0968 | 278.742
1660.6917 | 330.3738 | 282.1047 | 278.7493
1661.6917 | 330.3791 | 282.1341 | 278.7685
1662.6917 | 330.3508 | 282.1487 | 278.7764
1663.6917 | 330.3428 | 282.1641 | 278.7853
1664.6917 | 330.3355 | 282.1485 | 278.799
1665.6917 | 330.3323 | 282.1319 | 278.8094
1666.6917 | 330.2749 | 282.1462 | 278.814
1667.6917 | 330.1838 | 282.1751 | 278.8357
1668.6917 | 330.1687 | 282.1849 | 278.8539
1669.6917 | 330.1576 | 282.1533 | 278.8612
1670.6917 | 330.18 | 282.1809 | 278.8768
1671.6917 | 330.1791 | 282.201 | 278.8858
1672.6917 | 330.1942 | 282.2603 | 278.9047
1673.6917 | 330.2055 | 282.2985 | 278.9237
1674.6917 | 330.1528 | 282.3073 | 278.9415
1675.6917 | 330.0799 | 282.3144 | 278.9572
1676.6917 | 330.0139 | 282.3278 | 278.9687
1677.6917 | 329.9697 | 282.3272 | 278.9763
1678.6917 | 329.9867 | 282.3493 | 278.9929
1679.6917 | 330.0351 | 282.3732 | 279.0117
1680.6917 | 330.083 | 282.3877 | 279.0306
1681.6917 | 330.0472 | 282.3843 | 279.0468
1682.6917 | 330.0108 | 282.4133 | 279.0601
1683.6917 | 329.9882 | 282.4248 | 279.0701
1684.6917 | 329.9 | 282.4566 | 279.0759
1685.6917 | 329.8181 | 282.4755 | 279.0949
1686.6917 | 329.809 | 282.4657 | 279.0985
1687.6917 | 329.7949 | 282.5018 | 279.1138
1688.6917 | 329.7578 | 282.5441 | 279.1269
1689.6917 | 329.7224 | 282.5357 | 279.1403
1690.6917 | 329.6446 | 282.555 | 279.1509
1691.6917 | 329.6234 | 282.5788 | 279.1577
1692.6917 | 329.5793 | 282.6175 | 279.1681
1693.6917 | 329.5311 | 282.6612 | 279.1844
1694.6917 | 329.4887 | 282.6966 | 279.1881
1695.6917 | 329.4696 | 282.7218 | 279.2062
1696.6917 | 329.4672 | 282.7252 | 279.2061
1697.6917 | 329.4909 | 282.7432 | 279.214
1698.6917 | 329.5319 | 282.7364 | 279.2349
1699.6917 | 329.5631 | 282.7585 | 279.245
1700.6917 | 329.5049 | 282.7571 | 279.2554
1701.6917 | 329.4528 | 282.797 | 279.2667
1702.6917 | 329.448 | 282.8477 | 279.2734
1703.6917 | 329.4351 | 282.8835 | 279.2817
1704.6917 | 329.3963 | 282.8797 | 279.2972
1705.6917 | 329.3156 | 282.8571 | 279.3086
1706.6917 | 329.266 | 282.8392 | 279.317
1707.6917 | 329.2849 | 282.8597 | 279.326
1708.6917 | 329.2998 | 282.8542 | 279.3318
1709.6917 | 329.2753 | 282.8951 | 279.3394
1710.6917 | 329.2594 | 282.9368 | 279.3511
1711.6917 | 329.2595 | 282.999 | 279.3545
1712.6917 | 329.2358 | 283.058 | 279.3742
1713.6917 | 329.232 | 283.1166 | 279.381
1714.6917 | 329.1933 | 283.1425 | 279.3802
1715.6917 | 329.2527 | 283.151 | 279.4031
1716.6917 | 329.2949 | 283.1085 | 279.412
1717.6917 | 329.3168 | 283.0539 | 279.425
1718.6917 | 329.3222 | 283.0224 | 279.4282
1719.6917 | 329.3469 | 283.0422 | 279.4404
1720.6917 | 329.3972 | 283.0637 | 279.4508
1721.6917 | 329.4415 | 283.0742 | 279.4571
1722.6917 | 329.4846 | 283.0443 | 279.468
1723.6917 | 329.5064 | 283.0041 | 279.4689
1724.6917 | 329.4988 | 282.9954 | 279.4836
1725.6917 | 329.5508 | 282.9855 | 279.4932
1726.6917 | 329.6327 | 282.9775 | 279.5104
1727.6917 | 329.6481 | 282.9482 | 279.521
1728.6917 | 329.6948 | 282.9647 | 279.5315
1729.6917 | 329.7248 | 282.9722 | 279.5433
1730.6917 | 329.6906 | 282.9885 | 279.5599
1731.6917 | 329.6943 | 283.0008 | 279.5741
1732.6917 | 329.7161 | 283.0173 | 279.5786
1733.6917 | 329.6967 | 283.0322 | 279.596
1734.6917 | 329.7001 | 283.072 | 279.6044
1735.6917 | 329.687 | 283.0985 | 279.615
1736.6917 | 329.6994 | 283.1608 | 279.6219
1737.6917 | 329.7396 | 283.1606 | 279.6401
1738.6917 | 329.8025 | 283.181 | 279.6461
1739.6917 | 329.8438 | 283.1562 | 279.6663
1740.6917 | 329.809 | 283.1447 | 279.6772
1741.6917 | 329.8127 | 283.1595 | 279.6857
1742.6917 | 329.7875 | 283.1606 | 279.7015
1743.6917 | 329.8198 | 283.1779 | 279.7059
1744.6917 | 329.8508 | 283.1952 | 279.7169
1745.6917 | 329.89 | 283.1922 | 279.7254
1746.6917 | 329.9489 | 283.2001 | 279.7431
1747.6917 | 329.9011 | 283.225 | 279.7546
1748.6917 | 329.9377 | 283.24 | 279.7692
1749.6917 | 329.9634 | 283.2487 | 279.7798
1750.6917 | 329.9707 | 283.226 | 279.7975
1751.6917 | 329.9669 | 283.2257 | 279.7993
1752.6917 | 329.9193 | 283.2368 | 279.8197
1753.6917 | 329.9247 | 283.2537 | 279.8384
1754.6917 | 329.9691 | 283.2863 | 279.8438
1755.6917 | 329.955 | 283.2796 | 279.8547
1756.6917 | 329.9077 | 283.2714 | 279.8703
1757.6917 | 329.8707 | 283.281 | 279.8811
1758.6917 | 329.7933 | 283.2413 | 279.8942
1759.6917 | 329.7565 | 283.2376 | 279.906
1760.6917 | 329.7166 | 283.2257 | 279.9197
1761.6917 | 329.7107 | 283.2584 | 279.9335
1762.6917 | 329.7011 | 283.254 | 279.9412
1763.6917 | 329.6789 | 283.2695 | 279.9553
1764.6917 | 329.6965 | 283.2378 | 279.9613
1765.6917 | 329.7273 | 283.2293 | 279.9794
1766.6917 | 329.6938 | 283.2165 | 279.9824
1767.6917 | 329.6726 | 283.2234 | 279.9962
1768.6917 | 329.7161 | 283.2333 | 280.0122
1769.6917 | 329.7474 | 283.2466 | 280.0176
1770.6917 | 329.7861 | 283.2685 | 280.034
1771.6917 | 329.7473 | 283.2908 | 280.0438
1772.6917 | 329.7232 | 283.2739 | 280.0526
1773.6917 | 329.7407 | 283.2442 | 280.0658
1774.6917 | 329.7097 | 283.2339 | 280.0802
1775.6917 | 329.6314 | 283.2431 | 280.0882
1776.6917 | 329.6168 | 283.3066 | 280.1023
1777.6917 | 329.5947 | 283.3288 | 280.1191
1778.6917 | 329.5765 | 283.3881 | 280.1262
1779.6917 | 329.5363 | 283.4165 | 280.1352
1780.6917 | 329.5395 | 283.4514 | 280.1502
1781.6917 | 329.5305 | 283.507 | 280.1465
1782.6917 | 329.5221 | 283.5396 | 280.159
1783.6917 | 329.5556 | 283.5595 | 280.175
1784.6917 | 329.5511 | 283.5882 | 280.1973
1785.6917 | 329.5418 | 283.6195 | 280.2043
1786.6917 | 329.4968 | 283.6293 | 280.2118
1787.6917 | 329.4885 | 283.6645 | 280.2304
1788.6917 | 329.5104 | 283.7049 | 280.2433
1789.6917 | 329.531 | 283.7466 | 280.2554
1790.6917 | 329.5087 | 283.7762 | 280.2632
1791.6917 | 329.4764 | 283.7496 | 280.2719
1792.6917 | 329.4681 | 283.7971 | 280.28
1793.6917 | 329.5264 | 283.8423 | 280.3005
1794.6917 | 329.5663 | 283.8824 | 280.3177
1795.6917 | 329.6407 | 283.8844 | 280.3221
1796.6917 | 329.6798 | 283.8826 | 280.3399
1797.6917 | 329.6797 | 283.929 | 280.35
1798.6917 | 329.7069 | 283.9878 | 280.3598
1799.6917 | 329.7627 | 284.0351 | 280.3727
1800.6917 | 329.7765 | 284.0458 | 280.3783
1801.6917 | 329.8 | 284.0319 | 280.3917
1802.6917 | 329.8157 | 284.0374 | 280.403
1803.6917 | 329.8416 | 284.0511 | 280.4237
1804.6917 | 329.8288 | 284.0369 | 280.4349
1805.6917 | 329.8693 | 284.0197 | 280.4476
1806.6917 | 329.9025 | 284.0074 | 280.4529
1807.6917 | 329.9423 | 283.9863 | 280.4635
1808.6917 | 329.9382 | 283.9765 | 280.4782
1809.6917 | 329.9314 | 283.9638 | 280.4882
1810.6917 | 329.9405 | 283.9714 | 280.4981
1811.6917 | 329.9625 | 283.9719 | 280.5025
1812.6917 | 329.9659 | 283.9685 | 280.5183
1813.6917 | 329.9777 | 283.965 | 280.5234
1814.6917 | 329.9902 | 283.9407 | 280.5331
1815.6917 | 329.957 | 283.9491 | 280.5439
1816.6917 | 329.9561 | 283.9709 | 280.5539
1817.6917 | 329.981 | 284.0057 | 280.5631
1818.6917 | 329.9961 | 284.036 | 280.576
1819.6917 | 329.9912 | 284.071 | 280.5865
1820.6917 | 330.0128 | 284.1076 | 280.5887
1821.6917 | 330.0099 | 284.1149 | 280.6098
1822.6917 | 329.9938 | 284.1075 | 280.6101
1823.6917 | 330.0119 | 284.1203 | 280.6284
1824.6917 | 329.9965 | 284.1354 | 280.6403
1825.6917 | 329.9677 | 284.1444 | 280.6519
1826.6917 | 329.9113 | 284.1726 | 280.666
1827.6917 | 329.8956 | 284.1731 | 280.6825
1828.6917 | 329.8961 | 284.1846 | 280.6838
1829.6917 | 329.8731 | 284.2075 | 280.6959
1830.6917 | 329.9042 | 284.2475 | 280.707
1831.6917 | 329.9044 | 284.2566 | 280.7172
1832.6917 | 329.8653 | 284.2401 | 280.7313
1833.6917 | 329.8471 | 284.2143 | 280.7432
1834.6917 | 329.7751 | 284.2047 | 280.7489
1835.6917 | 329.7122 | 284.2281 | 280.7721
1836.6917 | 329.6703 | 284.258 | 280.7765
1837.6917 | 329.6329 | 284.2786 | 280.7872
1838.6917 | 329.5904 | 284.3096 | 280.7981
1839.6917 | 329.5705 | 284.3066 | 280.8118
1840.6917 | 329.5876 | 284.3014 | 280.8191
1841.6917 | 329.6093 | 284.3058 | 280.8198
1842.6917 | 329.5895 | 284.2855 | 280.8328
1843.6917 | 329.5593 | 284.263 | 280.8376
1844.6917 | 329.5436 | 284.1736 | 280.8472
1845.6917 | 329.5254 | 284.1232 | 280.8579
1846.6917 | 329.5351 | 284.1149 | 280.8687
1847.6917 | 329.5741 | 284.0474 | 280.8808
1848.6917 | 329.5822 | 284.0302 | 280.8888
1849.6917 | 329.6014 | 284.0131 | 280.8938
1850.6917 | 329.5701 | 284.0344 | 280.903
1851.6917 | 329.5917 | 284.0283 | 280.9155
1852.6917 | 329.6468 | 284.0553 | 280.9327
1853.6917 | 329.688 | 284.1028 | 280.9349
1854.6917 | 329.7255 | 284.1568 | 280.9498
1855.6917 | 329.7435 | 284.1723 | 280.9625
1856.6917 | 329.7208 | 284.2111 | 280.9764
1857.6917 | 329.715 | 284.2633 | 280.988
1858.6917 | 329.6985 | 284.3131 | 280.9957
1859.6917 | 329.7168 | 284.3746 | 281.008
1860.6917 | 329.7198 | 284.4071 | 281.0169
1861.6917 | 329.6609 | 284.4398 | 281.0288
1862.6917 | 329.6388 | 284.4629 | 281.0389
1863.6917 | 329.6261 | 284.4843 | 281.0465
1864.6917 | 329.5773 | 284.5204 | 281.0576
1865.6917 | 329.4947 | 284.5554 | 281.0736
1866.6917 | 329.4322 | 284.5671 | 281.0791
1867.6917 | 329.4084 | 284.6102 | 281.0869
1868.6917 | 329.36 | 284.6476 | 281.0944
1869.6917 | 329.3597 | 284.6349 | 281.1095
1870.6917 | 329.3554 | 284.5994 | 281.1205
1871.6917 | 329.3662 | 284.5835 | 281.1356
1872.6917 | 329.3926 | 284.5524 | 281.1399
1873.6917 | 329.3974 | 284.548 | 281.1434
1874.6917 | 329.4275 | 284.5358 | 281.1538
1875.6917 | 329.4353 | 284.5344 | 281.1649
1876.6917 | 329.4858 | 284.5479 | 281.1736
1877.6917 | 329.505 | 284.5617 | 281.1751
1878.6917 | 329.4977 | 284.5559 | 281.1862
1879.6917 | 329.4552 | 284.5545 | 281.2031
1880.6917 | 329.3945 | 284.5364 | 281.2063
1881.6917 | 329.3447 | 284.5088 | 281.2183
1882.6917 | 329.3215 | 284.4668 | 281.2218
1883.6917 | 329.2767 | 284.47 | 281.2291
1884.6917 | 329.2277 | 284.4883 | 281.2431
1885.6917 | 329.1919 | 284.5005 | 281.2475
1886.6917 | 329.1848 | 284.5221 | 281.2572
1887.6917 | 329.1665 | 284.5408 | 281.2635
1888.6917 | 329.1516 | 284.5504 | 281.2687
1889.6917 | 329.1877 | 284.5478 | 281.2827
1890.6917 | 329.1874 | 284.572 | 281.2859
1891.6917 | 329.1816 | 284.5761 | 281.2986
1892.6917 | 329.1411 | 284.5808 | 281.298
1893.6917 | 329.1333 | 284.5389 | 281.3086
1894.6917 | 329.1374 | 284.505 | 281.3135
1895.6917 | 329.164 | 284.4694 | 281.3205
1896.6917 | 329.1845 | 284.4481 | 281.3226
1897.6917 | 329.1848 | 284.4008 | 281.3239
1898.6917 | 329.1884 | 284.3722 | 281.3382
1899.6917 | 329.2605 | 284.3621 | 281.3474
1900.6917 | 329.286 | 284.3429 | 281.3524
1901.6917 | 329.2834 | 284.3382 | 281.3603
1902.6917 | 329.2265 | 284.3159 | 281.3692
1903.6917 | 329.2137 | 284.3002 | 281.3756
1904.6917 | 329.1913 | 284.2803 | 281.3841
1905.6917 | 329.1381 | 284.2404 | 281.3858
1906.6917 | 329.1468 | 284.2447 | 281.3898
1907.6917 | 329.2232 | 284.2409 | 281.4055
1908.6917 | 329.2625 | 284.2378 | 281.4119
1909.6917 | 329.2684 | 284.231 | 281.4257
1910.6917 | 329.26 | 284.2239 | 281.4317
1911.6917 | 329.2764 | 284.2394 | 281.4359
1912.6917 | 329.317 | 284.2525 | 281.4509
1913.6917 | 329.3626 | 284.2854 | 281.46
1914.6917 | 329.4297 | 284.3106 | 281.4696
1915.6917 | 329.4125 | 284.2965 | 281.4762
1916.6917 | 329.4326 | 284.318 | 281.4917
1917.6917 | 329.4706 | 284.3363 | 281.4931
1918.6917 | 329.5062 | 284.3807 | 281.503
1919.6917 | 329.5559 | 284.4086 | 281.5177
1920.6917 | 329.604 | 284.4449 | 281.5194
1921.6917 | 329.6221 | 284.4652 | 281.5296
1922.6917 | 329.6208 | 284.4757 | 281.5375
1923.6917 | 329.6499 | 284.4974 | 281.5479
1924.6917 | 329.6453 | 284.5248 | 281.5515
1925.6917 | 329.6062 | 284.548 | 281.5615
1926.6917 | 329.5419 | 284.5735 | 281.5706
1927.6917 | 329.5058 | 284.618 | 281.5802
1928.6917 | 329.4918 | 284.6841 | 281.586
1929.6917 | 329.5417 | 284.7286 | 281.5961
1930.6917 | 329.6048 | 284.765 | 281.5925
1931.6917 | 329.6183 | 284.7827 | 281.6048
1932.6917 | 329.6643 | 284.7911 | 281.6102
1933.6917 | 329.7199 | 284.7664 | 281.627
1934.6917 | 329.6962 | 284.7563 | 281.6323
1935.6917 | 329.6458 | 284.7755 | 281.6416
1936.6917 | 329.584 | 284.7892 | 281.6567
1937.6917 | 329.5542 | 284.7912 | 281.6603
1938.6917 | 329.5994 | 284.7862 | 281.672
1939.6917 | 329.6116 | 284.7666 | 281.6785
1940.6917 | 329.5574 | 284.7576 | 281.6938
1941.6917 | 329.5423 | 284.7627 | 281.7001
1942.6917 | 329.5543 | 284.7694 | 281.7056
1943.6917 | 329.5909 | 284.7764 | 281.7208
1944.6917 | 329.5536 | 284.7488 | 281.7313
1945.6917 | 329.4981 | 284.7183 | 281.742
1946.6917 | 329.4858 | 284.7134 | 281.7514
1947.6917 | 329.5046 | 284.6999 | 281.7581
1948.6917 | 329.5141 | 284.6916 | 281.7713
1949.6917 | 329.5213 | 284.7346 | 281.7829
1950.6917 | 329.4322 | 284.7423 | 281.7947
1951.6917 | 329.3425 | 284.7423 | 281.8044
1952.6917 | 329.3134 | 284.721 | 281.8097
1953.6917 | 329.3027 | 284.7189 | 281.8167
1954.6917 | 329.2797 | 284.7339 | 281.8259
1955.6917 | 329.2479 | 284.7777 | 281.8336
1956.6917 | 329.2589 | 284.8144 | 281.8446
1957.6917 | 329.2737 | 284.8204 | 281.8555
1958.6917 | 329.2211 | 284.8362 | 281.8625
1959.6917 | 329.1762 | 284.8403 | 281.8607
1960.6917 | 329.2336 | 284.8471 | 281.8689
1961.6917 | 329.3127 | 284.8364 | 281.8838
1962.6917 | 329.4022 | 284.8357 | 281.885
1963.6917 | 329.4781 | 284.8119 | 281.8954
1964.6917 | 329.5314 | 284.78 | 281.9058
1965.6917 | 329.593 | 284.805 | 281.91
1966.6917 | 329.6634 | 284.8189 | 281.9216
1967.6917 | 329.7296 | 284.8149 | 281.9285
1968.6917 | 329.8126 | 284.8273 | 281.937
1969.6917 | 329.8519 | 284.8341 | 281.9398
1970.6917 | 329.846 | 284.8637 | 281.9519
1971.6917 | 329.7834 | 284.8798 | 281.971
1972.6917 | 329.7742 | 284.9095 | 281.9656
1973.6917 | 329.7992 | 284.9276 | 281.9802
1974.6917 | 329.8077 | 284.9391 | 281.9855
1975.6917 | 329.828 | 284.9436 | 281.9995
1976.6917 | 329.8598 | 284.9154 | 282.0044
1977.6917 | 329.8196 | 284.9044 | 282.0075
1978.6917 | 329.7734 | 284.8964 | 282.0159
1979.6917 | 329.7499 | 284.8635 | 282.0176
1980.6917 | 329.7839 | 284.8804 | 282.0278
1981.6917 | 329.847 | 284.894 | 282.0401
1982.6917 | 329.8586 | 284.8851 | 282.0469
1983.6917 | 329.8682 | 284.8756 | 282.0423
1984.6917 | 329.845 | 284.8534 | 282.0536
1985.6917 | 329.8474 | 284.8429 | 282.0653
1986.6917 | 329.8354 | 284.8717 | 282.0685
1987.6917 | 329.8251 | 284.88 | 282.0761
1988.6917 | 329.8016 | 284.8862 | 282.0816
1989.6917 | 329.8138 | 284.9129 | 282.0865
1990.6917 | 329.8254 | 284.9373 | 282.1011
1991.6917 | 329.865 | 284.9799 | 282.1079
1992.6917 | 329.8684 | 285.0276 | 282.1125
1993.6917 | 329.8525 | 285.0514 | 282.1273
1994.6917 | 329.8325 | 285.0461 | 282.1266
1995.6917 | 329.7666 | 285.0312 | 282.1326
1996.6917 | 329.6933 | 285.0234 | 282.1382
1997.6917 | 329.6562 | 285.0018 | 282.1461
1998.6917 | 329.6342 | 285.0055 | 282.1501
1999.6917 | 329.6149 | 284.9859 | 282.1552
2000.6917 | 329.587 | 284.9834 | 282.1653
2001.6917 | 329.5644 | 284.9821 | 282.1649
2002.6917 | 329.5464 | 284.9688 | 282.1743
2003.6917 | 329.5742 | 284.9678 | 282.1737
2004.6917 | 329.5782 | 284.9348 | 282.1816
2005.6917 | 329.5786 | 284.9218 | 282.1943
2006.6917 | 329.5732 | 285.0136 | 282.1922
2007.6917 | 329.5741 | 285.0466 | 282.1991
2008.6917 | 329.5781 | 285.0912 | 282.2083
2009.6917 | 329.5637 | 285.1215 | 282.2097
2010.6917 | 329.5379 | 285.1496 | 282.2166
2011.6917 | 329.5438 | 285.1755 | 282.2257
2012.6917 | 329.5417 | 285.2092 | 282.2381
2013.6917 | 329.5779 | 285.231 | 282.2451
2014.6917 | 329.6071 | 285.2504 | 282.2516
2015.6917 | 329.6536 | 285.2454 | 282.2632
2016.6917 | 329.5729 | 285.2556 | 282.2695
2017.6917 | 329.5041 | 285.247 | 282.2803
2018.6917 | 329.5446 | 285.3077 | 282.2906
2019.6917 | 329.6002 | 285.3613 | 282.297
2020.6917 | 329.6675 | 285.3988 | 282.3074
2021.6917 | 329.6781 | 285.3947 | 282.3204
2022.6917 | 329.6755 | 285.4187 | 282.331
2023.6917 | 329.6397 | 285.4406 | 282.3471
2024.6917 | 329.612 | 285.5062 | 282.3461
2025.6917 | 329.6332 | 285.5931 | 282.3641
2026.6917 | 329.602 | 285.6568 | 282.3751
2027.6917 | 329.5577 | 285.7393 | 282.3884
2028.6917 | 329.5047 | 285.8008 | 282.399
2029.6917 | 329.5355 | 285.8792 | 282.4194
2030.6917 | 329.5667 | 285.9728 | 282.4215
2031.6917 | 329.5623 | 286.0303 | 282.4368
2032.6917 | 329.5201 | 286.0925 | 282.4581
2033.6917 | 329.4969 | 286.1615 | 282.4651
2034.6917 | 329.4627 | 286.2294 | 282.4778
2035.6917 | 329.3699 | 286.3018 | 282.4851
2036.6917 | 329.2766 | 286.3875 | 282.5022
2037.6917 | 329.2296 | 286.4541 | 282.5161
2038.6917 | 329.2481 | 286.5114 | 282.5316
2039.6917 | 329.2416 | 286.5928 | 282.5382
2040.6917 | 329.1442 | 286.6702 | 282.5594
2041.6917 | 329.0764 | 286.7264 | 282.5741
2042.6917 | 328.9791 | 286.8403 | 282.5932
2043.6917 | 328.9476 | 286.9208 | 282.6026
2044.6917 | 328.9158 | 286.9983 | 282.6254
2045.6917 | 328.8893 | 287.0875 | 282.6448
2046.6917 | 328.9215 | 287.1585 | 282.6626
2047.6917 | 329.0023 | 287.2788 | 282.6808
2048.6917 | 329.0631 | 287.4454 | 282.6989
2049.6917 | 329.1184 | 287.605 | 282.7185
2050.6917 | 329.1946 | 287.8086 | 282.7454
2051.6917 | 329.3294 | 288.0255 | 282.7594
2052.6917 | 329.4364 | 288.2376 | 282.784
2053.6917 | 329.4912 | 288.4864 | 282.8121
2054.6917 | 329.5085 | 288.7866 | 282.823
2055.6917 | 329.5739 | 289.122 | 282.8484
2056.6917 | 329.6535 | 289.5625 | 282.8728
2057.6917 | 329.7424 | 290.0835 | 282.9078
2058.6917 | 329.7861 | 290.7323 | 282.9379
2059.6917 | 329.8402 | 291.4628 | 282.9606
2060.6917 | 329.8506 | 292.294 | 282.9987
2061.6917 | 329.857 | 293.2098 | 283.0217
2062.6917 | 329.8943 | 294.2605 | 283.0617
2063.6917 | 329.9007 | 295.4278 | 283.0993
2064.6917 | 329.885 | 296.6979 | 283.1464
2065.6917 | 329.899 | 298.0346 | 283.1842
2066.6917 | 329.9611 | 299.4911 | 283.2481
2067.6917 | 330.0475 | 301.0323 | 283.2979
2068.6917 | 330.1158 | 302.6989 | 283.3594
2069.6917 | 330.1599 | 304.4539 | 283.4306
2070.6917 | 330.2018 | 306.2761 | 283.5077
2071.6917 | 330.2725 | 308.4117 | 283.6009
2072.6917 | 330.3678 | 310.5828 | 283.691
2073.6917 | 330.4033 | 313.2224 | 283.7846
2074.6917 | 330.4162 | 317.4625 | 283.8975
2075.6917 | 330.4574 | 325.9565 | 284.0296
2076.6917 | 330.4764 | 339.3789 | 284.1709
2077.6917 | 330.5275 | 354.3836 | 284.3131
2078.6917 | 330.585 | 367.9384 | 284.4909
2079.6917 | 330.6173 | 380.8577 | 284.6894
2080.6917 | 330.6076 | 393.3743 | 284.9655
2081.6917 | 330.6018 | 404.0496 | 285.2475
2082.6917 | 330.6239 | 413.2287 | 285.6379
2083.6917 | 330.6397 | 421.4553 | 286.0912
2084.6917 | 330.6651 | 428.3455 | 286.5992
2085.6917 | 330.6276 | 433.6659 | 287.1343
2086.6917 | 330.6077 | 437.8568 | 287.7654
2087.6917 | 330.6352 | 442.2301 | 288.4717
2088.6917 | 330.6612 | 446.7364 | 289.1941
2089.6917 | 330.668 | 451.6493 | 289.9722
2090.6917 | 330.5779 | 456.1515 | 290.7717
2091.6917 | 330.6534 | 460.0086 | 291.6252
2092.6917 | 330.5854 | 463.7746 | 292.5313
2093.6917 | 330.5342 | 465.1674 | 293.4974
2094.6917 | 330.4368 | 466.2671 | 294.5198
2095.6917 | 330.2842 | 467.1621 | 295.6337
2096.6917 | 330.1551 | 467.6334 | 296.8409
2097.6917 | 330.1353 | 467.9662 | 298.1588
2098.6917 | 330.0893 | 468.2952 | 299.5581
2099.6917 | 330.0206 | 468.8095 | 301.0736
2100.6917 | 329.915 | 469.6869 | 302.6996
2101.6917 | 329.7798 | 471.3612 | 304.3672
2102.6917 | 329.5863 | 472.6875 | 306.1763
2103.6917 | 329.3593 | 475.0905 | 308.0365
2104.6917 | 329.1294 | 477.0352 | 309.8796
2105.6917 | 329.0158 | 478.3413 | 311.7924
2106.6917 | 328.9355 | 480.9508 | 313.7636
2107.6917 | 328.7959 | 480.7612 | 315.7773
2108.6917 | 328.6023 | 481.0392 | 317.7311
2109.6917 | 328.4548 | 481.8237 | 319.7066
2110.6917 | 328.2511 | 482.3078 | 321.585
2111.6917 | 328.0712 | 482.3027 | 323.5671
2112.6917 | 327.9317 | 483.5233 | 325.2655
2113.6917 | 327.7994 | 484.6079 | 326.8918
2114.6917 | 327.6526 | 485.0149 | 328.7639
2115.6917 | 327.5977 | 484.904 | 330.735
2116.6917 | 327.5036 | 486.4466 | 332.6984
2117.6917 | 327.3321 | 487.7967 | 334.7276
2118.6917 | 327.1541 | 490.0918 | 336.7946
2119.6917 | 327.0087 | 491.2015 | 338.7484
2120.6917 | 326.8645 | 492.2745 | 340.815
2121.6917 | 326.7496 | 493.9615 | 342.84
2122.6917 | 326.6184 | 494.6627 | 344.8773
2123.6917 | 326.4785 | 496.179 | 346.9531
2124.6917 | 326.3548 | 498.0345 | 349.0362
2125.6917 | 326.2648 | 499.2026 | 351.0669
2126.6917 | 326.2373 | 498.6616 | 353.0484
2127.6917 | 326.1994 | 497.8528 | 355.0216
2128.6917 | 326.1483 | 498.6823 | 357.0238
2129.6917 | 326.0259 | 498.6027 | 359.059
2130.6917 | 325.9154 | 500.2437 | 361.0783
2131.6917 | 325.8913 | 499.5399 | 363.1135
2132.6917 | 325.791 | 500.7445 | 365.1388
2133.6917 | 325.7222 | 501.1228 | 367.1845
2134.6917 | 325.7532 | 501.1128 | 369.1984
2135.6917 | 325.8082 | 502.5714 | 371.2239
2136.6917 | 325.8221 | 504.0628 | 373.2281
2137.6917 | 325.84 | 503.6193 | 375.1879
2138.6917 | 325.8086 | 505.0689 | 377.1268
2139.6917 | 325.7929 | 506.8095 | 378.9887
2140.6917 | 325.6869 | 507.2355 | 380.8304
2141.6917 | 325.7016 | 507.3807 | 382.6674
2142.6917 | 325.7575 | 507.9144 | 384.4623
2143.6917 | 325.7523 | 508.3877 | 386.2193
2144.6917 | 325.7697 | 508.5086 | 388.0193
2145.6917 | 325.8563 | 507.8087 | 389.8342
2146.6917 | 325.8189 | 508.9744 | 391.6272
2147.6917 | 325.7953 | 510.4291 | 393.4046
2148.6917 | 325.7133 | 510.703 | 395.1575
2149.6917 | 325.6631 | 510.4034 | 396.9306
2150.6917 | 325.6807 | 510.7899 | 398.6916
2151.6917 | 325.7877 | 510.7263 | 400.3262
2152.6917 | 325.8624 | 511.3323 | 401.9992
2153.6917 | 325.8486 | 512.8016 | 403.6589
2154.6917 | 325.8292 | 512.9301 | 405.4034
2155.6917 | 325.766 | 513.083 | 407.1429
2156.6917 | 325.6979 | 514.6046 | 408.8654
2157.6917 | 325.7689 | 515.3139 | 410.6284
2158.6917 | 325.9064 | 514.6924 | 412.377
2159.6917 | 325.8778 | 514.5418 | 414.1051
2160.6917 | 325.909 | 514.6547 | 415.738
2161.6917 | 325.8989 | 514.8184 | 417.4223
2162.6917 | 325.9668 | 516.1049 | 419.0283
2163.6917 | 326.0044 | 517.7592 | 420.6571
2164.6917 | 326.0415 | 517.3947 | 422.1574
2165.6917 | 326.1176 | 518.5822 | 423.6314
2166.6917 | 326.2378 | 520.3711 | 425.1207
2167.6917 | 326.4631 | 523.1506 | 426.5669
2168.6917 | 326.6013 | 524.3378 | 428.0485
2169.6917 | 326.7753 | 522.3937 | 429.5352
2170.6917 | 327.0248 | 523.154 | 431.1187
2171.6917 | 327.1438 | 522.2003 | 432.6907
2172.6917 | 327.387 | 522.3646 | 434.2492
2173.6917 | 327.4841 | 523.8241 | 435.815
2174.6917 | 327.5223 | 524.3632 | 437.3318
2175.6917 | 327.5945 | 522.2 | 438.9909
2176.6917 | 327.738 | 524.7354 | 440.5099
2177.6917 | 327.8216 | 526.4349 | 442.1476
2178.6917 | 327.8926 | 526.835 | 443.6522
2179.6917 | 327.9749 | 529.2553 | 445.4234
2180.6917 | 328.1392 | 531.0706 | 446.9896
2181.6917 | 328.2002 | 531.702 | 448.5209
2182.6917 | 328.1913 | 530.809 | 449.972
2183.6917 | 328.3628 | 531.5534 | 451.4397
2184.6917 | 328.7133 | 532.3696 | 452.9065
2185.6917 | 328.9573 | 532.6357 | 454.3299
2186.6917 | 329.0596 | 531.6779 | 455.5734
2187.6917 | 329.1267 | 531.3253 | 457.0363
2188.6917 | 329.2203 | 530.6585 | 458.2592
2189.6917 | 329.2988 | 529.1239 | 459.448
2190.6917 | 329.354 | 529.1276 | 460.7719
2191.6917 | 329.6232 | 529.8414 | 462.0291
2192.6917 | 329.7735 | 530.1792 | 463.1391
2193.6917 | 329.7551 | 530.2763 | 464.2504
2194.6917 | 329.7544 | 530.4138 | 465.4306
2195.6917 | 329.768 | 533.2842 | 466.4675
2196.6917 | 329.6789 | 536.2571 | 467.3326
2197.6917 | 329.6266 | 539.3971 | 468.2662
2198.6917 | 329.6555 | 539.5774 | 469.0325
2199.6917 | 329.6304 | 540.8515 | 469.9344
2200.6917 | 329.571 | 541.1455 | 470.7989
2201.6917 | 329.6847 | 541.5454 | 471.6448
2202.6917 | 329.73 | 545.9329 | 472.4806
2203.6917 | 329.8057 | 550.2577 | 473.2699
2204.6917 | 329.8025 | 551.0517 | 474.0216
2205.6917 | 329.9516 | 552.2642 | 474.7789
2206.6917 | 330.1527 | 552.396 | 475.6336
2207.6917 | 330.2696 | 553.9678 | 476.4752
2208.6917 | 330.2533 | 558.6109 | 477.3189
2209.6917 | 330.0931 | 562.8966 | 478.1277
2210.6917 | 329.9094 | 565.0976 | 478.9746
2211.6917 | 329.8692 | 565.588 | 479.8347
2212.6917 | 329.9913 | 568.8418 | 480.6472
2213.6917 | 330.1577 | 569.8685 | 481.4021
2214.6917 | 330.2162 | 572.9903 | 482.1851
2215.6917 | 330.3804 | 574.3934 | 482.9775
2216.6917 | 330.2639 | 576.94 | 483.6981
2217.6917 | 330.2424 | 579.6598 | 484.4341
2218.6917 | 330.29 | 578.6512 | 485.1473
2219.6917 | 330.4983 | 579.6445 | 485.8534
2220.6917 | 330.6153 | 580.4164 | 486.5708
2221.6917 | 330.6401 | 581.2613 | 487.3039
2222.6917 | 330.7575 | 582.3238 | 488.0294
2223.6917 | 330.802 | 584.3595 | 488.8061
2224.6917 | 331.3016 | 584.672 | 489.5494
2225.6917 | 331.5729 | 582.4513 | 490.2758
2226.6917 | 331.758 | 582.5135 | 490.8972
2227.6917 | 331.9991 | 581.9453 | 491.5608
2228.6917 | 332.2102 | 580.5432 | 492.3106
2229.6917 | 332.4156 | 578.345 | 493.0957
2230.6917 | 332.616 | 579.9507 | 494.01
2231.6917 | 332.8371 | 581.1645 | 494.8047
2232.6917 | 333.0677 | 580.9494 | 495.6563
2233.6917 | 333.2871 | 581.1026 | 496.4308
2234.6917 | 333.5825 | 582.2737 | 497.1471
2235.6917 | 333.843 | 584.1831 | 497.9628
2236.6917 | 333.9322 | 585.163 | 498.7497
2237.6917 | 334.1262 | 586.3586 | 499.7787
2238.6917 | 334.1295 | 587.6638 | 500.5909
2239.6917 | 334.1432 | 590.0219 | 501.6714
2240.6917 | 334.1189 | 593.2637 | 502.6504
2241.6917 | 334.0547 | 596.1502 | 503.5901
2242.6917 | 334.0833 | 597.3545 | 504.5537
2243.6917 | 334.0361 | 599.7729 | 505.4295
2244.6917 | 334.082 | 601.2262 | 506.4037
2245.6917 | 334.1625 | 603.628 | 507.2682
2246.6917 | 334.2623 | 605.5176 | 508.1285
2247.6917 | 334.3004 | 607.4547 | 509.0505
2248.6917 | 334.2195 | 608.2901 | 510.0307
2249.6917 | 334.2225 | 608.7819 | 511.062
2250.6917 | 334.3564 | 608.7339 | 512.0216
2251.6917 | 334.4615 | 609.1837 | 512.9543
2252.6917 | 334.5439 | 609.239 | 513.8606
2253.6917 | 334.5999 | 609.7398 | 514.7431
2254.6917 | 334.5936 | 609.5531 | 515.6123
2255.6917 | 334.6617 | 608.7791 | 516.5691
2256.6917 | 334.8167 | 607.7658 | 517.4697
2257.6917 | 334.9493 | 606.7316 | 518.4405
2258.6917 | 335.1086 | 605.8158 | 519.3283
2259.6917 | 335.2133 | 604.9259 | 520.2456
2260.6917 | 335.3473 | 603.872 | 521.161
2261.6917 | 335.4143 | 602.6315 | 522.0548
2262.6917 | 335.4619 | 601.3104 | 522.9254
2263.6917 | 335.4624 | 599.8068 | 523.7419
2264.6917 | 335.4922 | 598.0031 | 524.5117
2265.6917 | 335.4745 | 596.0293 | 525.1869
2266.6917 | 335.3979 | 594.0528 | 525.8722
2267.6917 | 335.4611 | 592.2476 | 526.5502
2268.6917 | 335.542 | 590.4624 | 527.2776
2269.6917 | 335.6799 | 588.7062 | 527.9752
2270.6917 | 335.8753 | 586.6791 | 528.6726
2271.6917 | 335.9321 | 584.5664 | 529.278
2272.6917 | 335.9517 | 582.3296 | 529.8632
2273.6917 | 336.0475 | 580.0106 | 530.3616
2274.6917 | 336.1156 | 577.9372 | 530.8381
2275.6917 | 336.223 | 575.9701 | 531.3666
2276.6917 | 336.3615 | 574.1165 | 531.8937
2277.6917 | 336.5693 | 572.1154 | 532.413
2278.6917 | 336.71 | 569.834 | 532.7955
2279.6917 | 336.6913 | 567.5678 | 533.2557
2280.6917 | 336.7351 | 565.3917 | 533.5882
2281.6917 | 336.8573 | 562.8819 | 533.8013
2282.6917 | 336.837 | 560.449 | 534.0439
2283.6917 | 336.7514 | 558.1483 | 534.2661
2284.6917 | 336.6932 | 555.6849 | 534.3249
2285.6917 | 336.6212 | 553.2888 | 534.423
2286.6917 | 336.5541 | 550.7994 | 534.5524
2287.6917 | 336.5535 | 548.4501 | 534.6762
2288.6917 | 336.4601 | 546.1512 | 534.8416
2289.6917 | 336.3751 | 543.9379 | 534.9926
2290.6917 | 336.3042 | 541.8185 | 535.1631
2291.6917 | 336.2738 | 539.5772 | 535.2934
2292.6917 | 336.1739 | 537.6411 | 535.4281
2293.6917 | 336.0917 | 535.5509 | 535.5422
2294.6917 | 335.965 | 533.1958 | 535.5808
2295.6917 | 335.8778 | 531.0692 | 535.6001
2296.6917 | 335.791 | 529.1528 | 535.44
2297.6917 | 335.7657 | 527.1686 | 535.1393
2298.6917 | 335.7532 | 524.9117 | 534.8822
2299.6917 | 335.7069 | 522.7559 | 534.7901
2300.6917 | 335.6396 | 520.4507 | 534.7418
2301.6917 | 335.4772 | 518.4716 | 534.7648
2302.6917 | 335.3284 | 516.6032 | 534.6869
2303.6917 | 335.2208 | 514.96 | 534.5705
2304.6917 | 335.2058 | 513.0507 | 534.3815
2305.6917 | 335.2582 | 511.219 | 534.1693
2306.6917 | 335.2692 | 509.3242 | 533.986
2307.6917 | 335.1974 | 507.7331 | 533.8166
2308.6917 | 335.1982 | 506.0499 | 533.6635
2309.6917 | 335.1494 | 504.4554 | 533.4477
2310.6917 | 335.1356 | 502.9556 | 533.3546
2311.6917 | 335.0869 | 501.4537 | 533.2169
2312.6917 | 335.0008 | 500.0508 | 533.1908
2313.6917 | 334.8687 | 498.5026 | 533.136
2314.6917 | 334.7708 | 497.0777 | 532.9854
2315.6917 | 334.7566 | 495.7917 | 532.693
2316.6917 | 334.6683 | 494.4653 | 532.499
2317.6917 | 334.5959 | 493.3204 | 532.349
2318.6917 | 334.5011 | 492.0441 | 532.0078
2319.6917 | 334.4194 | 490.9279 | 531.4469
2320.6917 | 334.3512 | 489.7256 | 531.1286
2321.6917 | 334.2437 | 488.4344 | 530.6426
2322.6917 | 334.1868 | 487.3337 | 530.5223
2323.6917 | 334.0778 | 486.2061 | 530.0989
2324.6917 | 334.0351 | 485.0513 | 529.8513
2325.6917 | 333.9567 | 483.7926 | 529.9172
2326.6917 | 333.8295 | 482.6312 | 529.8889
2327.6917 | 333.7582 | 481.5691 | 529.9786
2328.6917 | 333.635 | 480.6217 | 529.7673
2329.6917 | 333.5011 | 479.6511 | 529.4312
2330.6917 | 333.3948 | 478.7243 | 529.2872
2331.6917 | 333.2967 | 477.9107 | 528.8818
2332.6917 | 333.1424 | 477.1883 | 528.6807
2333.6917 | 332.9753 | 476.3387 | 528.425
2334.6917 | 332.8371 | 475.3538 | 528.1847
2335.6917 | 332.7582 | 474.4266 | 527.9743
2336.6917 | 332.6214 | 473.6414 | 527.5487
2337.6917 | 332.4393 | 472.9763 | 527.0161
2338.6917 | 332.3126 | 472.2665 | 526.6453
2339.6917 | 332.1998 | 471.4895 | 526.4508
2340.6917 | 332.0557 | 470.8323 | 526.3407
2341.6917 | 331.9707 | 470.015 | 526.0017
2342.6917 | 331.8274 | 469.2965 | 525.5724
2343.6917 | 331.6149 | 468.5577 | 525.2429
2344.6917 | 331.3978 | 467.8752 | 524.919
2345.6917 | 331.255 | 467.1968 | 524.3486
2346.6917 | 331.1071 | 466.4552 | 524.0036
2347.6917 | 330.9686 | 465.7568 | 523.6786
2348.6917 | 330.8241 | 464.942 | 523.5467
2349.6917 | 330.6676 | 464.2135 | 523.5404
2350.6917 | 330.5247 | 463.6735 | 523.3551
2351.6917 | 330.3632 | 463.028 | 523.0649
2352.6917 | 330.1445 | 462.4621 | 522.8275
2353.6917 | 329.9481 | 461.989 | 522.5733
2354.6917 | 329.8278 | 461.5184 | 522.2057
2355.6917 | 329.7129 | 460.9644 | 521.9376
2356.6917 | 329.5658 | 460.5229 | 521.7069
2357.6917 | 329.3986 | 460.1196 | 521.3936
2358.6917 | 329.2115 | 459.5589 | 521.1393
2359.6917 | 329.0542 | 459.1813 | 520.8732
2360.6917 | 328.8957 | 458.5389 | 520.5538
2361.6917 | 328.7508 | 457.9764 | 520.4486
2362.6917 | 328.581 | 457.2975 | 520.1677
2363.6917 | 328.4247 | 456.8001 | 519.9406
2364.6917 | 328.2636 | 456.4241 | 519.8092
2365.6917 | 328.1301 | 455.3523 | 519.6289
2366.6917 | 327.9893 | 454.3491 | 519.3484
2367.6917 | 327.8851 | 453.1883 | 519.0351
2368.6917 | 327.7549 | 452.3352 | 518.707
2369.6917 | 327.6292 | 451.7568 | 518.5972
2370.6917 | 327.469 | 451.0226 | 518.5534
2371.6917 | 327.351 | 450.1104 | 518.4312
2372.6917 | 327.1644 | 449.7732 | 518.322
2373.6917 | 326.9705 | 449.5562 | 518.2155
2374.6917 | 326.8575 | 449.277 | 518.2302
2375.6917 | 326.7264 | 449.9368 | 518.2416
2376.6917 | 326.5552 | 449.7755 | 518.0997
2377.6917 | 326.4213 | 449.0761 | 518.0304
2378.6917 | 326.3219 | 448.7181 | 518.0149
2379.6917 | 326.2314 | 448.4297 | 518.0146
2380.6917 | 326.1174 | 449.0882 | 517.9233
2381.6917 | 326.28 | 449.7484 | 517.8511
2382.6917 | 326.3767 | 449.7496 | 517.8184
2383.6917 | 326.2434 | 449.2429 | 517.8367
2384.6917 | 326.0766 | 449.1147 | 517.971
2385.6917 | 325.9123 | 449.0312 | 518.0837
2386.6917 | 325.7674 | 448.5691 | 518.1546
2387.6917 | 325.666 | 448.0821 | 518.1442
2388.6917 | 325.5565 | 447.998 | 518.1421
2389.6917 | 325.4153 | 447.9233 | 518.1624
2390.6917 | 325.273 | 447.93 | 518.186
2391.6917 | 325.1081 | 447.6838 | 518.1208
2392.6917 | 324.9467 | 447.7119 | 517.9568
2393.6917 | 324.767 | 447.6428 | 517.7525
2394.6917 | 324.6468 | 448.8703 | 518.5753
2395.6917 | 324.5649 | 447.6463 | 517.6018
2396.6917 | 324.5807 | 447.534 | 517.5911
2397.6917 | 324.4919 | 447.7746 | 517.5067
2398.6917 | 324.3377 | 447.5806 | 517.2131
2399.6917 | 324.2078 | 447.4618 | 517.1501
2400.6917 | 324.0667 | 447.5191 | 516.9549
2401.6917 | 323.9504 | 447.2037 | 516.8074
2402.6917 | 323.8741 | 446.8933 | 516.7056
2403.6917 | 323.744 | 446.5906 | 516.6445
2404.6917 | 323.6202 | 446.3605 | 516.5673
2405.6917 | 323.5107 | 446.4437 | 516.4852
2406.6917 | 323.3203 | 446.5329 | 516.2787
2407.6917 | 323.1445 | 446.1932 | 516.0635
2408.6917 | 322.9717 | 446.1528 | 515.9433
2409.6917 | 322.8191 | 446.0129 | 515.7675
2410.6917 | 322.7031 | 445.9983 | 515.6005
2411.6917 | 322.5775 | 445.4763 | 515.3619
2412.6917 | 322.4435 | 445.1859 | 515.2262
2413.6917 | 322.2579 | 445.0862 | 515.1406
2414.6917 | 322.1 | 444.8081 | 514.9294
2415.6917 | 321.9107 | 444.5108 | 514.8986
2416.6917 | 321.7105 | 445.1725 | 515.1276
2417.6917 | 321.5813 | 444.6433 | 514.6138
2418.6917 | 321.4839 | 444.5183 | 514.508
2419.6917 | 321.3739 | 444.3048 | 514.3767
2420.6917 | 321.1987 | 444.0028 | 514.1679
2421.6917 | 320.9503 | 443.6874 | 513.9131
2422.6917 | 320.7132 | 443.1846 | 513.6993
2423.6917 | 320.4801 | 442.6625 | 513.5377
2424.6917 | 320.2522 | 442.3788 | 513.365
2425.6917 | 320.0167 | 442.1528 | 513.2116
2426.6917 | 319.794 | 442.0483 | 513.0141
2427.6917 | 319.6136 | 441.9657 | 512.7865
2428.6917 | 319.4487 | 442.0283 | 512.5064
2429.6917 | 319.2675 | 441.8834 | 512.3033
2430.6917 | 319.0684 | 441.7959 | 512.0102
2431.6917 | 318.8555 | 441.8701 | 511.7608
2432.6917 | 318.6558 | 442.08 | 511.5401
2433.6917 | 318.4523 | 442.1061 | 511.3113
2434.6917 | 318.2746 | 442.0213 | 511.026
2435.6917 | 318.1241 | 441.9379 | 510.7537
2436.6917 | 317.9543 | 441.825 | 510.4849
2437.6917 | 317.7336 | 441.4839 | 510.2735
2438.6917 | 317.547 | 441.2618 | 510.1287
2439.6917 | 317.3418 | 440.9631 | 509.9568
2440.6917 | 317.1423 | 440.7325 | 509.8751
2441.6917 | 316.9233 | 440.5766 | 509.6899
2442.6917 | 316.7017 | 440.3669 | 509.4928
2443.6917 | 316.4988 | 440.1297 | 509.2727
2444.6917 | 316.2871 | 439.9896 | 509.06
2445.6917 | 316.0453 | 439.9018 | 508.868
2446.6917 | 315.8271 | 439.6695 | 508.7218
2447.6917 | 315.6272 | 439.403 | 508.596
2448.6917 | 315.3867 | 439.131 | 508.4593
2449.6917 | 315.1336 | 438.8985 | 508.3867
2450.6917 | 314.9342 | 438.5262 | 508.2587
2451.6917 | 314.7162 | 438.3808 | 508.1999
2452.6917 | 314.5171 | 438.3299 | 508.0505
2453.6917 | 314.3439 | 438.1047 | 507.9454
2454.6917 | 314.1753 | 437.9062 | 507.8575
2455.6917 | 313.9707 | 437.7313 | 507.7367
2456.6917 | 313.769 | 437.5377 | 507.6218
2457.6917 | 313.6177 | 437.5059 | 507.4992
2458.6917 | 313.4473 | 437.4809 | 507.3993
2459.6917 | 313.2695 | 437.3185 | 507.2666
2460.6917 | 313.0951 | 437.1947 | 507.1334
2461.6917 | 312.9304 | 437.1184 | 506.9547
2462.6917 | 312.763 | 437.062 | 506.806
2463.6917 | 312.5554 | 437.0073 | 506.7049
2464.6917 | 312.3389 | 437.0647 | 506.581
2465.6917 | 312.1506 | 437.0099 | 506.463