## Test Conditions
DESIREE-FIRE Test Number 7 - Circuit Simulator Data Only
Test Date: | 2009-07-20
DCSim DAQ Start Time | 10:58
DCSim Time for Synchronization | 11:07
Heat Source Synchronization | 1:15 | minutes:seconds
Heat Source DAQ Start Time | 11:06
Fire Time | 11:08
Offset | 0:10 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 600 | seconds
Heat Source Offset | 0:02 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 149 | seconds
Heat Source Stop Time | 11:20
Test Duration | 0:12 | minutes:seconds
| 720 | seconds
CT500 turns | 1 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1
Pre-Test Baseline: | Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.0625 | 124.498 | -60.1456 | 64.0366 | 0.039098 | 0.0061468 | 0.064915 | 0.059291 | -0.0093096 | -0.0086702 | 0.00027221 | 0.097669 | -0.010985 | 0.077291 | 0.062192 | -0.005089 | -0.0015599 | -0.018567 | -0.041199 | 63.8672 | -60.2234 | 64.1602 | -60.141 | -60.4843 | -60.498 | 0.009155 | 63.9084 | -60.1913 | 64.238 | -60.173 | -60.2783 | -60.2234 | -0.07782 | -0.16937 | 0.1236 | 0.004578 | -0.35248 | -0.33874 | -0.27466 | -0.26093 | -0.045776 | -0.12817 | 0.20142 | -0.027466 | -0.07782 | -0.13275 | -0.032044 | -0.086975 | 0.082398 | 124.3835 | 0.01831 | 124.4293 | 124.0906 | 124.0997 | 124.0128 | 124.054 | -124.2599 | -124.2279 | 124.3057 | 124.3835 | 60.1044 | 60.1547
0.9375 | 124.4385 | -60.1501 | 64.0457 | 0.039098 | -0.0034662 | 0.071323 | 0.059291 | -0.0050366 | 0.0041468 | 0.0045452 | -0.0091433 | 0.0039692 | 0.06661 | 0.055783 | -0.00081695 | -0.0079689 | -0.0036126 | -0.09613 | 63.9313 | -60.228 | 64.2151 | -60.0677 | -60.3607 | -60.4019 | -0.082397 | 63.9359 | -60.2051 | 64.2105 | -60.2188 | -60.3241 | -60.2783 | -0.07782 | -0.11444 | 0.16937 | 0.082397 | -0.25177 | -0.21057 | -0.17395 | -0.13275 | -0.054932 | -0.10986 | 0.16479 | -0.068665 | -0.12817 | -0.17395 | -0.073242 | -0.11902 | 0.16022 | 124.4431 | -0.013733 | 124.4156 | 124.1592 | 124.1409 | 124.0814 | 124.086 | -124.2737 | -124.2508 | 124.3652 | 124.3607 | 60.054 | 60.0677
1.9375 | 124.5071 | -60.141 | 64.0228 | 0.023839 | -0.0034662 | 0.053165 | 0.061427 | -0.013582 | -0.031101 | -0.0018638 | 0.051892 | -0.0035078 | 0.055929 | 0.058987 | 0.00666 | -0.00049194 | 0.0081364 | -0.045776 | 63.8809 | -60.2005 | 64.1556 | -60.1501 | -60.4568 | -60.4843 | 0.009155 | 63.9175 | -60.1685 | 64.2426 | -60.1593 | -60.2921 | -60.228 | -0.059509 | -0.14191 | 0.13275 | -0.009155 | -0.34332 | -0.31586 | -0.28381 | -0.25635 | -0.027466 | -0.10529 | 0.21973 | -0.018311 | -0.086975 | -0.15106 | -0.059509 | -0.1236 | 0.050354 | 124.3561 | 0.009155 | 124.411 | 124.0814 | 124.086 | 124.0219 | 124.0585 | -124.2233 | -124.1913 | 124.2966 | 124.3835 | 60.0952 | 60.1501
2.9375 | 124.5071 | -60.1501 | 64.0411 | 0.084874 | 0.0029428 | 0.070255 | 0.061427 | -0.0082416 | -0.0033302 | 0.0088172 | 0.067151 | 0.00076419 | 0.060202 | 0.069668 | -0.00081695 | 0.0048481 | -0.014294 | -0.022888 | 63.8809 | -60.1959 | 64.1739 | -60.141 | -60.4752 | -60.498 | -0.022888 | 63.9313 | -60.2097 | 64.2563 | -60.1868 | -60.2829 | -60.228 | -0.045777 | -0.16022 | 0.13275 | 0.009155 | -0.3479 | -0.32501 | -0.30212 | -0.27924 | -0.05951 | -0.10986 | 0.21515 | -0.036622 | -0.07782 | -0.13275 | -0.01831 | -0.073242 | 0.054932 | 124.3698 | 0.022888 | 124.4659 | 124.0768 | 124.1409 | 124.0311 | 124.0814 | -124.2371 | -124.2508 | 124.324 | 124.4064 | 60.1273 | 60.1273
3.9375 | 124.5071 | -60.1639 | 63.9999 | 0.039098 | -0.0023982 | 0.069187 | 0.055018 | -0.00076463 | -0.0011942 | 0.0045452 | 0.0061157 | -0.00030381 | 0.064474 | 0.053647 | 0.004524 | 0.0059161 | 0.0060004 | -0.064087 | 63.8672 | -60.1913 | 64.1785 | -60.1273 | -60.4797 | -60.4752 | 0 | 63.8992 | -60.1822 | 64.2426 | -60.1822 | -60.2921 | -60.2234 | -0.027466 | -0.13275 | 0.17853 | 0.036621 | -0.31128 | -0.31586 | -0.28381 | -0.28839 | -0.018311 | -0.10071 | 0.24262 | -0.018311 | -0.05951 | -0.12817 | -0.041199 | -0.10986 | 0.064087 | 124.3698 | 0 | 124.4247 | 124.0585 | 124.0814 | 124.0311 | 124.0631 | -124.1913 | -124.1821 | 124.3423 | 124.4064 | 60.0998 | 60.1639
4.9688 | 124.411 | -60.1685 | 64.0182 | 0.084874 | 0.00080677 | 0.071323 | 0.062495 | -0.024263 | 0.0062828 | -0.0072048 | 0.021375 | -0.0013718 | 0.058065 | 0.072873 | -0.002953 | -0.0069009 | 0.0081364 | -0.082397 | 63.9267 | -60.228 | 64.2838 | -60.0311 | -60.3653 | -60.4019 | -0.082397 | 63.9542 | -60.2097 | 64.1968 | -60.2325 | -60.347 | -60.3104 | -0.059509 | -0.091553 | 0.2655 | 0.13733 | -0.23346 | -0.19684 | -0.17395 | -0.13733 | -0.041199 | -0.064087 | 0.17853 | -0.064087 | -0.14191 | -0.17853 | -0.10071 | -0.13733 | 0.19684 | 124.5117 | -0.022888 | 124.4064 | 124.1547 | 124.1638 | 124.0952 | 124.1226 | -124.2462 | -124.2279 | 124.4522 | 124.3652 | 60.0861 | 60.0861
5.9375 | 124.4843 | -60.141 | 64.0411 | 0.0085801 | 0.0050788 | 0.076664 | 0.04861 | -0.0061046 | -0.022556 | -0.0072048 | 0.17396 | 0.0018322 | 0.062338 | 0.02374 | 0.007728 | -0.0015599 | -0.0057486 | -0.027466 | 63.8855 | -60.2005 | 64.1693 | -60.1639 | -60.4889 | -60.5026 | 0.018311 | 63.9221 | -60.173 | 64.2426 | -60.1685 | -60.2783 | -60.228 | -0.059509 | -0.15564 | 0.12817 | -0.022888 | -0.36163 | -0.3479 | -0.30213 | -0.28839 | -0.032044 | -0.11902 | 0.20142 | -0.027466 | -0.086975 | -0.13733 | -0.054931 | -0.10529 | 0.036621 | 124.3698 | 0.004578 | 124.4156 | 124.086 | 124.0952 | 124.0265 | 124.0631 | -124.2416 | -124.2142 | 124.3103 | 124.3835 | 60.1135 | 60.1593
6.9375 | 124.4843 | -60.141 | 64.0549 | 0.17643 | 0.0072148 | 0.068119 | 0.055018 | 0.0035084 | -0.010807 | 0.0013402 | -0.0091433 | 0.00076419 | 0.076223 | 0.069668 | -0.00081695 | 0.0091211 | -0.0068176 | -0.082397 | 63.8947 | -60.2188 | 64.183 | -60.1089 | -60.4523 | -60.5072 | -0.013733 | 63.9175 | -60.173 | 64.238 | -60.173 | -60.2829 | -60.2325 | -0.07782 | -0.16022 | 0.12817 | 0.032043 | -0.36621 | -0.31128 | -0.28839 | -0.23346 | -0.032044 | -0.13733 | 0.1831 | -0.032044 | -0.091553 | -0.14191 | -0.059509 | -0.10986 | 0.10986 | 124.4019 | 0 | 124.411 | 124.1135 | 124.0906 | 124.0356 | 124.0585 | -124.2737 | -124.2279 | 124.324 | 124.379 | 60.0586 | 60.1273
7.9375 | 124.4568 | -60.1456 | 64.0366 | -0.12875 | -0.00026223 | 0.059574 | 0.057155 | -0.01465 | -0.0065342 | -0.01575 | 0.051892 | -0.0056438 | 0.06127 | 0.062192 | 0.00666 | 0.0080531 | 0.030567 | -0.054932 | 63.913 | -60.2188 | 64.2014 | -60.1135 | -60.4431 | -60.4523 | -0.004578 | 63.9221 | -60.1913 | 64.2426 | -60.1868 | -60.2966 | -60.2325 | -0.073242 | -0.1236 | 0.1648 | 0.032044 | -0.3067 | -0.29755 | -0.23346 | -0.2243 | -0.045776 | -0.11444 | 0.20599 | -0.041199 | -0.086975 | -0.15106 | -0.041199 | -0.10529 | 0.10529 | 124.4202 | 0.004577 | 124.4339 | 124.1318 | 124.1135 | 124.0585 | 124.0677 | -124.2554 | -124.2279 | 124.3469 | 124.3881 | 60.0906 | 60.141
8.9375 | 124.4888 | -60.1456 | 64.032 | 0.0085801 | 0.0072148 | 0.069187 | 0.056086 | -0.0050366 | -0.010807 | 0.0013402 | -0.0091433 | -0.0035078 | 0.056997 | 0.052579 | -0.011498 | 0.0027121 | -0.014294 | -0.022888 | 63.858 | -60.2005 | 64.1602 | -60.1593 | -60.4843 | -60.498 | 0.013733 | 63.9175 | -60.173 | 64.2609 | -60.1685 | -60.2737 | -60.228 | -0.054931 | -0.17395 | 0.12817 | -0.013733 | -0.35248 | -0.33874 | -0.29755 | -0.28381 | -0.027466 | -0.11444 | 0.22888 | -0.022888 | -0.082397 | -0.12817 | -0.054931 | -0.10071 | 0.041198 | 124.3607 | 0.004578 | 124.4339 | 124.0585 | 124.0906 | 124.0036 | 124.0631 | -124.2325 | -124.205 | 124.3057 | 124.4064 | 60.1227 | 60.1593
9.9375 | 124.4659 | -60.1547 | 64.0045 | 0.084874 | 0.0050788 | 0.064915 | 0.064631 | 0.0077804 | -0.021488 | -0.0093408 | 0.14344 | -0.0013718 | 0.064474 | 0.061124 | 0.003456 | -0.0036969 | -0.021771 | -0.027466 | 63.8672 | -60.2051 | 64.1647 | -60.1685 | -60.4752 | -60.4935 | 0.009155 | 63.913 | -60.1822 | 64.2334 | -60.1685 | -60.2737 | -60.2142 | -0.050354 | -0.13733 | 0.16022 | -0.013733 | -0.33874 | -0.32043 | -0.28839 | -0.27008 | -0.027466 | -0.091553 | 0.22888 | -0.013733 | -0.059509 | -0.11902 | -0.032043 | -0.091553 | 0.036621 | 124.3698 | 0.013733 | 124.4156 | 124.0723 | 124.0952 | 124.0219 | 124.0677 | -124.2096 | -124.1867 | 124.3195 | 124.3881 | 60.1273 | 60.1639
10.9375 | 124.4705 | -60.141 | 64.0182 | 0.023839 | -0.00026223 | 0.067051 | 0.060359 | -0.0061046 | 0.0041468 | 0.015226 | 0.1587 | -0.00030381 | 0.051657 | 0.032284 | -0.001885 | -0.00049194 | -0.018567 | -0.022888 | 63.8718 | -60.2051 | 64.1602 | -60.173 | -60.4889 | -60.5026 | -0.009155 | 63.9175 | -60.1913 | 64.2471 | -60.1593 | -60.2783 | -60.2463 | -0.064087 | -0.14648 | 0.14191 | -0.032044 | -0.36163 | -0.3479 | -0.29755 | -0.28381 | -0.050354 | -0.10071 | 0.22888 | -0.018311 | -0.10529 | -0.13733 | -0.054932 | -0.086975 | 0.032043 | 124.3652 | 0.032043 | 124.4385 | 124.0768 | 124.1089 | 124.0128 | 124.0585 | -124.2233 | -124.2096 | 124.3011 | 124.3881 | 60.1181 | 60.1318
11.9375 | 124.5026 | -60.173 | 64.0091 | -0.037196 | -0.0056022 | 0.075596 | 0.066768 | -0.0039686 | -0.0097382 | -0.014682 | -0.024402 | -0.0099168 | 0.063406 | 0.066464 | -0.002953 | -0.0069009 | -0.0004086 | -0.032043 | 63.8672 | -60.2097 | 64.151 | -60.1547 | -60.466 | -60.4935 | 0.004578 | 63.9084 | -60.1959 | 64.2471 | -60.1639 | -60.2966 | -60.2234 | -0.036621 | -0.14191 | 0.14191 | 0.018311 | -0.32043 | -0.29297 | -0.28381 | -0.25635 | -0.022888 | -0.10071 | 0.23804 | 0.009156 | -0.050354 | -0.1236 | -0.027466 | -0.10071 | 0.054932 | 124.3607 | 0.032044 | 124.4431 | 124.0768 | 124.1043 | 124.0402 | 124.0814 | -124.2188 | -124.205 | 124.324 | 124.4202 | 60.141 | 60.1776
12.9375 | 124.4797 | -60.1364 | 64.0228 | 0.023839 | -0.00026223 | 0.059574 | 0.060359 | 0.012053 | 0.0030788 | 0.0045452 | 0.11293 | -0.0056438 | 0.055929 | 0.058987 | -0.009362 | -0.0015599 | -0.0057486 | -0.032043 | 63.8809 | -60.1868 | 64.1647 | -60.1639 | -60.4797 | -60.498 | 0.018311 | 63.8992 | -60.1639 | 64.2426 | -60.173 | -60.2875 | -60.2509 | -0.050354 | -0.14191 | 0.14191 | -0.027465 | -0.36163 | -0.34332 | -0.31128 | -0.29297 | -0.027465 | -0.1236 | 0.21973 | -0.036621 | -0.11444 | -0.15106 | -0.086975 | -0.1236 | 0.022889 | 124.3515 | -0.009156 | 124.4064 | 124.0677 | 124.0631 | 124.0173 | 124.0356 | -124.2096 | -124.1867 | 124.3011 | 124.379 | 60.1044 | 60.1547
13.9375 | 124.4522 | -60.1501 | 64.0366 | 0.0085801 | 0.0082828 | 0.063847 | 0.051814 | -0.00076463 | -0.0022622 | 0.0013402 | -0.070178 | -0.0067128 | 0.060202 | 0.082486 | 0.003456 | 0.0048481 | 0.0049324 | -0.036621 | 63.8901 | -60.2051 | 64.1785 | -60.1364 | -60.466 | -60.4797 | -0.013733 | 63.9587 | -60.1776 | 64.2426 | -60.173 | -60.2921 | -60.228 | -0.054932 | -0.14648 | 0.14191 | 0.013732 | -0.32959 | -0.31586 | -0.27466 | -0.26093 | -0.027466 | -0.07782 | 0.20599 | -0.022889 | -0.07782 | -0.14191 | -0.050354 | -0.11444 | 0.068664 | 124.3835 | 0.004577 | 124.4202 | 124.0952 | 124.1364 | 124.0402 | 124.1089 | -124.2416 | -124.2142 | 124.3286 | 124.3927 | 60.1135 | 60.1364
14.9375 | 124.4843 | -60.1364 | 64.0366 | 0.039098 | -0.0023982 | 0.062778 | 0.066768 | -0.011446 | 0.0073508 | -0.0018638 | 0.08241 | 0.00076419 | 0.055929 | 0.082486 | -0.004021 | -0.010105 | -0.0036126 | -0.073242 | 63.8672 | -60.2051 | 64.1876 | -60.0998 | -60.4523 | -60.4843 | -0.027466 | 63.9313 | -60.1868 | 64.2242 | -60.1822 | -60.2875 | -60.2325 | -0.068664 | -0.16937 | 0.15106 | 0.036622 | -0.3479 | -0.31586 | -0.27924 | -0.24719 | -0.050354 | -0.10529 | 0.18768 | -0.045776 | -0.09613 | -0.15106 | -0.045776 | -0.10071 | 0.10529 | 124.3927 | 0.004578 | 124.411 | 124.0723 | 124.118 | 124.0036 | 124.0677 | -124.2416 | -124.2233 | 124.324 | 124.3607 | 60.0632 | 60.1089
15.9688 | 124.4293 | -60.1273 | 64.0503 | 0.10013 | -0.0066702 | 0.059574 | 0.049678 | 0.0035084 | 0.0020108 | -0.0050688 | 0.28077 | -0.0013718 | 0.06661 | 0.053647 | 0.003456 | -0.0047649 | 0.0049324 | -0.032043 | 63.8855 | -60.2188 | 64.2242 | -60.0632 | -60.4156 | -60.4431 | -0.032043 | 63.9496 | -60.1593 | 64.2059 | -60.1868 | -60.2829 | -60.26 | -0.091553 | -0.16479 | 0.17395 | 0.064087 | -0.31586 | -0.28839 | -0.2243 | -0.19684 | -0.032044 | -0.10071 | 0.15564 | -0.05951 | -0.13275 | -0.15564 | -0.10071 | -0.1236 | 0.15564 | 124.4431 | -0.027466 | 124.3652 | 124.1043 | 124.1089 | 124.0128 | 124.0768 | -124.2691 | -124.2096 | 124.3515 | 124.3332 | 60.0952 | 60.0952
16.9375 | 124.4705 | -60.1318 | 64.0182 | -0.0066789 | 0.0050788 | 0.065983 | 0.059291 | -0.0050366 | 0.029782 | -0.0029318 | 0.021375 | -0.0024398 | 0.054861 | 0.050442 | -0.00081695 | -0.00049194 | 0.013477 | -0.009155 | 63.8718 | -60.1639 | 64.1693 | -60.1639 | -60.4935 | -60.5072 | -0.004578 | 63.9221 | -60.1685 | 64.2471 | -60.1593 | -60.2737 | -60.2142 | -0.032043 | -0.14648 | 0.15106 | -0.032043 | -0.37537 | -0.36163 | -0.34332 | -0.32959 | -0.036621 | -0.096131 | 0.22888 | -0.027466 | -0.082397 | -0.14191 | -0.045776 | -0.10529 | 0 | 124.3332 | 0.009155 | 124.4156 | 124.0356 | 124.0906 | 124.0036 | 124.054 | -124.1821 | -124.1867 | 124.3011 | 124.379 | 60.1227 | 60.1273
17.9531 | 124.3652 | -60.1959 | 64.0732 | 0.14591 | -0.00026223 | 0.072392 | 0.063563 | -0.0039686 | -0.00012524 | -0.0093408 | -0.11595 | -0.0024398 | 0.070883 | 0.095303 | 0.00025105 | -0.0047649 | 0.010272 | 0 | 63.9221 | -60.2142 | 64.2929 | -60.0174 | -60.3561 | -60.3561 | -0.064087 | 63.9587 | -60.1913 | 64.1464 | -60.2554 | -60.3928 | -60.3378 | -0.01831 | -0.15106 | 0.21973 | 0.17853 | -0.16022 | -0.16022 | -0.14191 | -0.14191 | 0.004578 | -0.11444 | 0.073242 | -0.059509 | -0.14191 | -0.19684 | -0.14648 | -0.20142 | 0.19684 | 124.5071 | -0.064087 | 124.3378 | 124.1364 | 124.1501 | 124.118 | 124.1547 | -124.2874 | -124.2645 | 124.4888 | 124.3423 | 60.1959 | 60.1318
18.9375 | 124.4476 | -60.1181 | 64.0182 | 0.14591 | -0.0066702 | 0.068119 | 0.059291 | 0.00030337 | -0.00012524 | -0.00079579 | 0.036633 | 0.0018322 | 0.064474 | 0.079282 | 0.001319 | -0.0058329 | 0.0070684 | -0.054932 | 63.8718 | -60.2051 | 64.1785 | -60.1593 | -60.4797 | -60.466 | 0 | 63.9175 | -60.173 | 64.2471 | -60.173 | -60.2875 | -60.228 | -0.086975 | -0.14648 | 0.16022 | -0.041199 | -0.3479 | -0.36163 | -0.26093 | -0.27466 | -0.054932 | -0.10071 | 0.22888 | -0.054932 | -0.10986 | -0.16937 | -0.054931 | -0.11444 | 0.045776 | 124.3835 | 0 | 124.4202 | 124.0768 | 124.0906 | 123.9899 | 124.0356 | -124.2233 | -124.1913 | 124.2966 | 124.3652 | 60.0632 | 60.1181
19.9375 | 124.4751 | -60.1318 | 63.9999 | 0.023839 | 0.00080677 | 0.071323 | 0.060359 | 0.0024404 | -0.016147 | 0.0013402 | 0.1587 | -0.012053 | 0.058065 | 0.052579 | 0.003456 | -0.0026279 | 0.0017274 | -0.027466 | 63.8809 | -60.1959 | 64.1464 | -60.1501 | -60.4889 | -60.4935 | 0.013733 | 63.913 | -60.173 | 64.2288 | -60.1639 | -60.2875 | -60.2325 | -0.064087 | -0.11902 | 0.14648 | -0.01831 | -0.36163 | -0.35706 | -0.29755 | -0.29297 | -0.041199 | -0.086975 | 0.22888 | -0.032043 | -0.10071 | -0.15564 | -0.059509 | -0.11444 | 0.045777 | 124.3423 | 0.009156 | 124.4019 | 124.0768 | 124.086 | 124.0128 | 124.0448 | -124.1959 | -124.173 | 124.2783 | 124.3607 | 60.1044 | 60.1456
20.9688 | 124.3927 | -60.1822 | 64.0411 | -0.037196 | -0.0066702 | 0.076664 | 0.068904 | 0.0088484 | 0.015896 | 0.015226 | 0.0061157 | -0.0013718 | 0.059133 | 0.053647 | 0.00025105 | -0.010105 | 0.0081364 | -0.09613 | 63.9175 | -60.2188 | 64.2975 | -60.0174 | -60.3561 | -60.3836 | -0.10529 | 63.945 | -60.2097 | 64.1785 | -60.2234 | -60.4111 | -60.3653 | -0.036621 | -0.1236 | 0.25635 | 0.16479 | -0.20142 | -0.17395 | -0.16479 | -0.13733 | -0.027466 | -0.096131 | 0.13733 | -0.041199 | -0.18311 | -0.22888 | -0.15564 | -0.20142 | 0.20142 | 124.5163 | -0.013733 | 124.3881 | 124.1364 | 124.1547 | 124.0997 | 124.1272 | -124.2599 | -124.2508 | 124.4797 | 124.3607 | 60.0861 | 60.0769
21.9375 | 124.4843 | -60.1318 | 64.032 | 0.14591 | 0.0061468 | 0.064915 | 0.059291 | 0.0035084 | 0.028714 | 0.0045452 | 0.021375 | 0.0039692 | 0.067678 | 0.049374 | 0.00025105 | -0.00049194 | -0.0078856 | -0.07782 | 63.8901 | -60.2371 | 64.2105 | -60.1044 | -60.4294 | -60.4523 | -0.032043 | 63.913 | -60.1822 | 64.238 | -60.1868 | -60.3104 | -60.2371 | -0.10529 | -0.14191 | 0.17853 | 0.027466 | -0.32044 | -0.29755 | -0.21515 | -0.19226 | -0.050354 | -0.11902 | 0.20599 | -0.054932 | -0.10529 | -0.17853 | -0.054932 | -0.12817 | 0.13275 | 124.4476 | -0.004578 | 124.4202 | 124.1272 | 124.0952 | 124.0219 | 124.0448 | -124.2691 | -124.2142 | 124.3423 | 124.3698 | 60.054 | 60.0998
22.9688 | 124.4705 | -60.1227 | 64.032 | 0.069615 | -0.0013302 | 0.064915 | 0.059291 | -0.0082416 | 0.03085 | -0.0050688 | 0.235 | -0.0024398 | 0.051657 | 0.082486 | 0.00025105 | 0.0016441 | -0.0046806 | -0.032043 | 63.8763 | -60.2097 | 64.1556 | -60.1593 | -60.4706 | -60.4889 | 0.018311 | 63.8855 | -60.173 | 64.238 | -60.173 | -60.2921 | -60.1639 | -0.086975 | -0.15564 | 0.1236 | -0.036621 | -0.36621 | -0.3479 | -0.27924 | -0.26093 | -0.050354 | -0.14648 | 0.20599 | -0.050354 | -0.041198 | -0.16937 | 0.009156 | -0.11902 | 0.050354 | 124.3652 | 0 | 124.411 | 124.086 | 124.0585 | 123.999 | 124.0082 | -124.2416 | -124.205 | 124.2783 | 124.3607 | 60.0906 | 60.141
23.9375 | 124.4843 | -60.1318 | 64.0274 | 0.084874 | 0.0093518 | 0.069187 | 0.061427 | -0.011446 | -0.0097382 | 0.0024082 | 0.021375 | -0.012053 | 0.071951 | 0.044034 | 0.00025105 | -0.014378 | -0.0057486 | -0.027466 | 63.8718 | -60.2097 | 64.1556 | -60.1501 | -60.4706 | -60.5072 | 0.004578 | 63.9313 | -60.1685 | 64.2563 | -60.1685 | -60.2783 | -60.228 | -0.07782 | -0.15564 | 0.12817 | -0.01831 | -0.37537 | -0.33875 | -0.29755 | -0.26093 | -0.036621 | -0.096131 | 0.22888 | -0.036621 | -0.09613 | -0.14648 | -0.059509 | -0.10986 | 0.05951 | 124.3652 | 0 | 124.4247 | 124.0814 | 124.0997 | 124.0036 | 124.0631 | -124.2371 | -124.1959 | 124.2874 | 124.3881 | 60.1044 | 60.1364
24.9375 | 124.498 | -60.1135 | 64.0228 | -0.0066789 | 0.0061468 | 0.060642 | 0.057155 | -0.0071726 | -0.018283 | 0.0077492 | 0.036633 | -0.0024398 | 0.074087 | 0.082486 | 0.003456 | 0.00057606 | -0.017499 | -0.036621 | 63.8809 | -60.2142 | 64.1602 | -60.1547 | -60.4706 | -60.4889 | 0.004578 | 63.913 | -60.1822 | 64.2563 | -60.1639 | -60.2875 | -60.2142 | -0.10071 | -0.14191 | 0.13733 | -0.041199 | -0.37537 | -0.35706 | -0.27466 | -0.25635 | -0.068665 | -0.10986 | 0.23346 | -0.050354 | -0.10071 | -0.17395 | -0.032043 | -0.10529 | 0.059509 | 124.3744 | 0.018311 | 124.4385 | 124.0952 | 124.0952 | 123.9944 | 124.0265 | -124.2371 | -124.205 | 124.2737 | 124.3698 | 60.0769 | 60.1181
25.9531 | 124.3881 | -60.2005 | 64.0366 | 0.14591 | 0.0082828 | 0.055302 | 0.065699 | 0.016325 | 0.018033 | 0.00027221 | 0.0061157 | 0.010377 | 0.060202 | 0.086758 | -0.002953 | -0.0026279 | -0.0025446 | -0.009155 | 63.9496 | -60.1959 | 64.2883 | -60.0403 | -60.3561 | -60.3561 | -0.068665 | 63.9679 | -60.1959 | 64.1556 | -60.2554 | -60.4111 | -60.3287 | 0.004577 | -0.086975 | 0.25177 | 0.16022 | -0.15564 | -0.15564 | -0.16022 | -0.16022 | 0.004577 | -0.068664 | 0.11902 | -0.054932 | -0.12817 | -0.21057 | -0.13275 | -0.21515 | 0.15564 | 124.4843 | -0.059509 | 124.3515 | 124.1455 | 124.1638 | 124.1501 | 124.1684 | -124.2325 | -124.2325 | 124.4888 | 124.3561 | 60.1913 | 60.1318
26.9375 | 124.4705 | -60.141 | 64.0045 | 0.0085801 | -0.0013302 | 0.059574 | 0.059291 | -0.0018326 | 0.0020108 | 0.0088172 | 0.20448 | 0.0029002 | 0.075155 | 0.054715 | -0.001885 | 0.0048481 | -0.0078856 | -0.036621 | 63.8763 | -60.1913 | 64.1464 | -60.173 | -60.4797 | -60.4935 | 0.018311 | 63.9267 | -60.1959 | 64.2288 | -60.1593 | -60.2875 | -60.2325 | -0.050354 | -0.12817 | 0.14191 | -0.032044 | -0.35248 | -0.33875 | -0.30212 | -0.28839 | -0.054932 | -0.07782 | 0.2243 | -0.018311 | -0.091553 | -0.14648 | -0.036621 | -0.091553 | 0.01831 | 124.3378 | 0.036621 | 124.4247 | 124.0677 | 124.1226 | 124.0173 | 124.0677 | -124.1959 | -124.2004 | 124.2874 | 124.3698 | 60.1044 | 60.1593
27.9375 | 124.3881 | -60.1822 | 64.0457 | -0.0066789 | 0.0072148 | 0.069187 | 0.064631 | -0.0029006 | -0.0054662 | -0.0093408 | -0.054919 | 0.011445 | 0.065542 | 0.094235 | 0.004524 | 0.0027121 | 0.012409 | -0.07782 | 63.9267 | -60.2325 | 64.3295 | -59.9808 | -60.3333 | -60.3516 | -0.15106 | 63.9862 | -60.2051 | 64.1281 | -60.3012 | -60.434 | -60.3424 | -0.050354 | -0.11902 | 0.28381 | 0.20142 | -0.16937 | -0.15106 | -0.11902 | -0.10071 | -0.022888 | -0.059509 | 0.082398 | -0.11902 | -0.16022 | -0.25177 | -0.13733 | -0.22888 | 0.25177 | 124.5621 | -0.09613 | 124.3332 | 124.1592 | 124.1913 | 124.1089 | 124.1684 | -124.2783 | -124.2508 | 124.5117 | 124.3103 | 60.1044 | 60.0311
28.9375 | 124.4888 | -60.1364 | 63.9999 | -0.0066789 | 0.01042 | 0.062778 | 0.062495 | -0.0061046 | 0.0052148 | -0.00079579 | 0.036633 | -0.0035078 | 0.06127 | 0.087826 | -0.009362 | 0.0091211 | 0.0027964 | -0.032043 | 63.9084 | -60.2005 | 64.1693 | -60.1364 | -60.4889 | -60.5026 | 0 | 63.9221 | -60.2051 | 64.2334 | -60.173 | -60.2875 | -60.228 | -0.064086 | -0.091553 | 0.16937 | 0 | -0.36621 | -0.35248 | -0.30213 | -0.28839 | -0.068664 | -0.07782 | 0.23346 | -0.036621 | -0.091552 | -0.15106 | -0.022888 | -0.082398 | 0.064086 | 124.3698 | 0.032043 | 124.4385 | 124.1089 | 124.1272 | 124.0448 | 124.0585 | -124.2004 | -124.205 | 124.3057 | 124.3698 | 60.1044 | 60.1364
29.9688 | 124.4476 | -60.1227 | 64.0411 | -0.0066789 | -0.0013302 | 0.057438 | 0.051814 | 0.016325 | -0.0022622 | 0.0077492 | 0.18922 | 0.0018322 | 0.078359 | 0.039761 | 0.00025105 | -0.012242 | 0.0006594 | -0.013733 | 63.9084 | -60.1776 | 64.2197 | -60.0952 | -60.4111 | -60.4248 | -0.004578 | 63.9359 | -60.1639 | 64.2197 | -60.1868 | -60.2646 | -60.228 | -0.054931 | -0.13275 | 0.17853 | 0.027466 | -0.30212 | -0.28839 | -0.24719 | -0.23346 | -0.041198 | -0.10529 | 0.17853 | -0.064087 | -0.10529 | -0.14191 | -0.064087 | -0.10071 | 0.082397 | 124.3973 | -0.022889 | 124.3835 | 124.086 | 124.0997 | 124.0311 | 124.0585 | -124.2188 | -124.205 | 124.3423 | 124.3423 | 60.1089 | 60.1181
30.9375 | 124.4614 | -60.1456 | 64.0366 | 0.084874 | 0.0093518 | 0.062778 | 0.064631 | -0.01465 | 0.0094878 | 0.0024082 | 0.1587 | 0.00076419 | 0.075155 | 0.050442 | 0.004524 | 0.0048481 | 0.0070684 | -0.036621 | 63.9038 | -60.1959 | 64.151 | -60.141 | -60.4752 | -60.4843 | 0.009155 | 63.9084 | -60.1593 | 64.2426 | -60.1685 | -60.2737 | -60.2234 | -0.050354 | -0.13275 | 0.11444 | 0.004578 | -0.33874 | -0.32959 | -0.28839 | -0.27924 | -0.013733 | -0.12817 | 0.20599 | -0.022888 | -0.07782 | -0.12817 | -0.064087 | -0.11444 | 0.054932 | 124.3469 | -0.009155 | 124.4019 | 124.0997 | 124.0677 | 124.0494 | 124.054 | -124.2325 | -124.1959 | 124.2966 | 124.3881 | 60.1089 | 60.1547
31.9531 | 124.3195 | -60.1868 | 64.064 | 0.11539 | 0.0029428 | 0.067051 | 0.063563 | -0.0093096 | 0.00094276 | 0.0045452 | -0.054919 | 0.0039692 | 0.058065 | 0.087826 | -0.004021 | -0.0069009 | 0.0070684 | -0.027466 | 63.9313 | -60.228 | 64.3158 | -59.9808 | -60.3333 | -60.3378 | -0.12817 | 63.9771 | -60.2188 | 64.119 | -60.3058 | -60.4202 | -60.3561 | -0.041198 | -0.13275 | 0.25177 | 0.20599 | -0.15106 | -0.14648 | -0.10986 | -0.10529 | -0.032043 | -0.086975 | 0.054932 | -0.11902 | -0.16937 | -0.23346 | -0.13733 | -0.20142 | 0.24719 | 124.5438 | -0.086975 | 124.3378 | 124.1592 | 124.1959 | 124.118 | 124.1638 | -124.292 | -124.2828 | 124.5026 | 124.3057 | 60.1593 | 60.0586
32.9375 | 124.4934 | -60.1547 | 64.032 | -0.067714 | 0.0029428 | 0.062778 | 0.055018 | 0.0013714 | -0.0086702 | 0.0098852 | 0.12819 | -0.0067128 | 0.056997 | 0.015195 | -0.002953 | -0.0069009 | -0.0089536 | -0.013733 | 63.8763 | -60.1868 | 64.1373 | -60.1593 | -60.4797 | -60.498 | 0.013733 | 63.9221 | -60.1501 | 64.238 | -60.1593 | -60.2921 | -60.2325 | -0.032044 | -0.15564 | 0.10529 | -0.004578 | -0.34332 | -0.32501 | -0.31128 | -0.29297 | 0.004578 | -0.10986 | 0.20599 | -0.004578 | -0.07782 | -0.13733 | -0.082398 | -0.14191 | 0.027466 | 124.324 | -0.009156 | 124.3881 | 124.0631 | 124.0723 | 124.0311 | 124.0768 | -124.2188 | -124.1821 | 124.292 | 124.3927 | 60.141 | 60.1685
33.9375 | 124.4293 | -60.1456 | 64.032 | -0.037196 | 0.0061468 | 0.055302 | 0.062495 | 0.0045764 | 0.016964 | 0.013089 | 0.28077 | -0.0077808 | 0.068746 | 0.053647 | 0.004524 | -0.0036969 | 0.0006594 | -0.032043 | 63.8763 | -60.1776 | 64.151 | -60.1547 | -60.466 | -60.4935 | 0.018311 | 63.9175 | -60.173 | 64.2059 | -60.2234 | -60.2921 | -60.2463 | -0.032043 | -0.15564 | 0.11902 | -0.009155 | -0.3479 | -0.32043 | -0.31586 | -0.28839 | -0.027466 | -0.11444 | 0.17395 | -0.07782 | -0.10071 | -0.14648 | -0.073242 | -0.11902 | 0.022888 | 124.3286 | -0.050354 | 124.379 | 124.054 | 124.0906 | 124.0219 | 124.0631 | -124.2096 | -124.205 | 124.2966 | 124.3515 | 60.1135 | 60.1639
34.9375 | 124.4385 | -60.1273 | 64.032 | -0.0066789 | -0.0066702 | 0.07346 | 0.069972 | 0.0077804 | -0.0054662 | -0.0061368 | -0.0091433 | -0.0024398 | 0.062338 | 0.076077 | -0.004021 | 0.0080531 | -0.013226 | -0.018311 | 63.8901 | -60.1776 | 64.1464 | -60.1364 | -60.4843 | -60.5026 | 0.009155 | 63.9359 | -60.1776 | 64.2288 | -60.173 | -60.2829 | -60.2005 | -0.050354 | -0.14191 | 0.11444 | -0.009156 | -0.37537 | -0.35706 | -0.32501 | -0.3067 | -0.050354 | -0.09613 | 0.19684 | -0.045777 | -0.073242 | -0.15564 | -0.022888 | -0.10529 | 0.041198 | 124.324 | 0.004577 | 124.4064 | 124.0677 | 124.1135 | 124.0173 | 124.0631 | -124.2096 | -124.2096 | 124.2737 | 124.3561 | 60.1089 | 60.1364
35.9375 | 124.5117 | -60.1273 | 64.0549 | 0.0085801 | 0.0029428 | 0.067051 | 0.063563 | 0.0056444 | -0.0086702 | 0.0077492 | 0.097669 | -0.0077808 | 0.063406 | 0.028012 | -0.001885 | 0.0016441 | -0.0089536 | -0.018311 | 63.8763 | -60.2051 | 64.1647 | -60.1547 | -60.4843 | -60.5026 | 0.009155 | 63.8901 | -60.1822 | 64.2426 | -60.173 | -60.2875 | -60.2142 | -0.07782 | -0.17853 | 0.10986 | -0.027466 | -0.37537 | -0.35706 | -0.29755 | -0.27924 | -0.054932 | -0.1648 | 0.18768 | -0.045777 | -0.086975 | -0.16022 | -0.032043 | -0.10529 | 0.050354 | 124.3698 | 0.009155 | 124.4247 | 124.0814 | 124.0723 | 124.0036 | 124.0173 | -124.2599 | -124.2371 | 124.292 | 124.3698 | 60.1089 | 60.1364
36.9375 | 124.4797 | -60.1593 | 64.0274 | -0.037196 | -0.00026223 | 0.062778 | 0.058223 | -0.013582 | 0.020169 | 0.0013402 | 0.17396 | -0.0056438 | 0.060202 | 0.062192 | 0.002387 | -0.0069009 | 0.0081364 | -0.036621 | 63.8626 | -60.1868 | 64.1464 | -60.1456 | -60.466 | -60.4843 | 0.009155 | 63.9084 | -60.1547 | 64.238 | -60.1639 | -60.2737 | -60.2188 | -0.027466 | -0.1648 | 0.11902 | 0.013733 | -0.32501 | -0.3067 | -0.29755 | -0.27923 | 0.004578 | -0.11902 | 0.21057 | -0.004577 | -0.059509 | -0.11444 | -0.064087 | -0.11902 | 0.041199 | 124.3332 | -0.009155 | 124.3927 | 124.0494 | 124.0631 | 124.0219 | 124.0677 | -124.2142 | -124.1821 | 124.3057 | 124.3973 | 60.1227 | 60.1685
37.9375 | 124.4751 | -60.1318 | 63.9999 | 0.10013 | 0.0040108 | 0.070255 | 0.063563 | -0.0082416 | -0.010807 | 0.0066812 | 0.08241 | 0.0061052 | 0.047384 | 0.061124 | 0.005592 | 0.0027121 | -0.0057486 | -0.022888 | 63.858 | -60.2142 | 64.1281 | -60.1593 | -60.4752 | -60.5072 | 0.022888 | 63.913 | -60.1593 | 64.2334 | -60.1547 | -60.2692 | -60.2142 | -0.082397 | -0.14191 | 0.12817 | -0.027466 | -0.37537 | -0.34332 | -0.29297 | -0.26093 | -0.027466 | -0.086975 | 0.23346 | -0.022888 | -0.082397 | -0.13733 | -0.054931 | -0.10986 | 0.054931 | 124.3423 | 0.004578 | 124.3927 | 124.0723 | 124.0723 | 123.9899 | 124.0448 | -124.2142 | -124.1592 | 124.2599 | 124.3652 | 60.1089 | 60.1547
38.9375 | 124.4705 | -60.1273 | 64.0182 | -0.021937 | -0.0045342 | 0.069187 | 0.058223 | 0.0045764 | -0.012943 | 0.0066812 | 0.08241 | -0.0035078 | 0.075155 | 0.047238 | 0.003456 | 0.0027121 | 0.012409 | -0.027466 | 63.8718 | -60.1822 | 64.1373 | -60.1639 | -60.4797 | -60.5026 | 0.018311 | 63.9084 | -60.1776 | 64.2563 | -60.1501 | -60.2554 | -60.2325 | -0.054932 | -0.14648 | 0.11902 | -0.036621 | -0.37537 | -0.35248 | -0.32044 | -0.29755 | -0.050354 | -0.10986 | 0.23804 | -0.022888 | -0.10529 | -0.12817 | -0.054932 | -0.07782 | 0.018311 | 124.3195 | 0.027466 | 124.4339 | 124.054 | 124.086 | 123.999 | 124.0356 | -124.2004 | -124.1959 | 124.2645 | 124.3835 | 60.0998 | 60.1456
39.9375 | 124.4797 | -60.1501 | 64.0366 | 0.084874 | 0.0061468 | 0.072392 | 0.064631 | -0.0029006 | -0.0011942 | 0.017362 | 0.08241 | 0.00076419 | 0.062338 | 0.06326 | -0.005089 | 0.0037801 | -0.014294 | -0.027466 | 63.8809 | -60.2188 | 64.1602 | -60.1547 | -60.4752 | -60.4889 | -0.004578 | 63.9084 | -60.1776 | 64.2471 | -60.1501 | -60.2783 | -60.2188 | -0.068665 | -0.15564 | 0.1236 | -0.004578 | -0.33875 | -0.32501 | -0.27008 | -0.25635 | -0.027466 | -0.12817 | 0.21057 | 0 | -0.068665 | -0.12817 | -0.041199 | -0.10071 | 0.064087 | 124.379 | 0.027466 | 124.4247 | 124.0997 | 124.086 | 124.0311 | 124.0585 | -124.2554 | -124.2142 | 124.3103 | 124.3973 | 60.1227 | 60.1456
40.9375 | 124.4568 | -60.1318 | 64.0137 | 0.054357 | 0.0018748 | 0.068119 | 0.058223 | 0.0056444 | -0.0043982 | 0.010953 | 0.12819 | -0.0045758 | 0.067678 | 0.06326 | 0.002387 | 0.0091211 | 0.0027964 | -0.022888 | 63.8626 | -60.2005 | 64.151 | -60.1593 | -60.4797 | -60.4843 | 0.022888 | 63.9404 | -60.1639 | 64.2426 | -60.1593 | -60.2829 | -60.2097 | -0.068664 | -0.15106 | 0.13733 | -0.027466 | -0.35248 | -0.3479 | -0.28381 | -0.27924 | -0.032043 | -0.073242 | 0.22888 | -0.027466 | -0.07782 | -0.15106 | -0.045777 | -0.11902 | 0.041198 | 124.3515 | 0.004577 | 124.4064 | 124.0631 | 124.1043 | 123.9944 | 124.0723 | -124.2142 | -124.1776 | 124.2828 | 124.3744 | 60.1089 | 60.1547
41.9375 | 124.4522 | -60.1456 | 64.0228 | 0.10013 | -0.0088062 | 0.059574 | 0.061427 | 0.017393 | -0.0043982 | -0.0018638 | 0.036633 | 0.0039692 | 0.048452 | 0.066464 | -0.00081695 | -0.010105 | -0.022839 | -0.064087 | 63.8992 | -60.2234 | 64.2059 | -60.0952 | -60.4156 | -60.4477 | -0.022888 | 63.913 | -60.1822 | 64.2288 | -60.1868 | -60.3012 | -60.2097 | -0.07782 | -0.1236 | 0.18311 | 0.050354 | -0.30212 | -0.27008 | -0.2243 | -0.19226 | -0.036621 | -0.10986 | 0.20599 | -0.041199 | -0.064087 | -0.15564 | -0.027466 | -0.11902 | 0.12817 | 124.4293 | -0.004578 | 124.411 | 124.1226 | 124.0952 | 124.0448 | 124.0585 | -124.2462 | -124.205 | 124.3515 | 124.3744 | 60.0815 | 60.1227
42.9375 | 124.4476 | -60.1456 | 63.9954 | 0.054357 | 0.00080677 | 0.05637 | 0.064631 | -0.022127 | -0.00012524 | -0.0050688 | 0.14344 | 0.00076419 | 0.067678 | 0.054715 | -0.005089 | -0.0015599 | -0.013226 | -0.032043 | 63.9496 | -60.26 | 64.238 | -60.0677 | -60.3928 | -60.4156 | -0.073242 | 63.9267 | -60.1959 | 64.2151 | -60.2005 | -60.3012 | -60.2188 | -0.11444 | -0.045776 | 0.24262 | 0.07782 | -0.27008 | -0.24719 | -0.15564 | -0.13275 | -0.050354 | -0.068664 | 0.21973 | -0.054931 | -0.073242 | -0.15564 | -0.022888 | -0.10529 | 0.19226 | 124.498 | -0.004577 | 124.411 | 124.2096 | 124.1226 | 124.0952 | 124.0723 | -124.2554 | -124.1913 | 124.3835 | 124.3607 | 60.1135 | 60.0723
43.9375 | 124.4431 | -60.1273 | 64.0045 | 0.10013 | -0.00026223 | 0.064915 | 0.056086 | -0.0061046 | 0.010556 | -0.012545 | 0.021375 | -0.0035078 | 0.067678 | 0.031216 | 0.005592 | -0.0090369 | -0.0036126 | -0.045776 | 63.8763 | -60.2051 | 64.1556 | -60.1227 | -60.466 | -60.4797 | -0.004578 | 63.9175 | -60.1639 | 64.2426 | -60.1593 | -60.2783 | -60.2142 | -0.07782 | -0.12817 | 0.15106 | 0.004577 | -0.35248 | -0.33875 | -0.27466 | -0.26093 | -0.036621 | -0.086975 | 0.23804 | -0.032044 | -0.086975 | -0.15106 | -0.050354 | -0.11444 | 0.082397 | 124.3607 | 0.004577 | 124.4064 | 124.0814 | 124.0814 | 124.0036 | 124.0448 | -124.2096 | -124.1684 | 124.2828 | 124.3698 | 60.0815 | 60.1227
44.9375 | 124.4659 | -60.141 | 64.0182 | -0.021937 | 0.0029428 | 0.057438 | 0.060359 | 0.010984 | -0.0065342 | 0.0077492 | 0.036633 | -0.0045758 | 0.059133 | 0.037625 | 0.004524 | 0.0069851 | 0.0006594 | -0.068665 | 63.8809 | -60.2051 | 64.1785 | -60.1089 | -60.4431 | -60.4797 | -0.022888 | 63.9267 | -60.1776 | 64.2242 | -60.1639 | -60.2692 | -60.2051 | -0.064087 | -0.13733 | 0.16022 | 0.032043 | -0.33875 | -0.30212 | -0.27466 | -0.23804 | -0.036621 | -0.091553 | 0.20599 | -0.022888 | -0.064087 | -0.12817 | -0.027466 | -0.091553 | 0.09613 | 124.3835 | 0.013733 | 124.4019 | 124.086 | 124.1043 | 124.0219 | 124.0677 | -124.2233 | -124.1959 | 124.3195 | 124.3652 | 60.0723 | 60.1181
45.9375 | 124.4888 | -60.1547 | 64.0182 | 0.17643 | -0.00026223 | 0.062778 | 0.060359 | -0.0018326 | 0.0084198 | -0.0018638 | 0.036633 | -0.0045758 | 0.071951 | 0.079282 | -0.006157 | 0.0069851 | 0.0017274 | -0.086975 | 63.913 | -60.2188 | 64.2288 | -60.0906 | -60.434 | -60.4431 | -0.036621 | 63.9313 | -60.1868 | 64.2242 | -60.1639 | -60.3104 | -60.2188 | -0.064087 | -0.10529 | 0.21057 | 0.064087 | -0.28839 | -0.27924 | -0.2243 | -0.21515 | -0.032044 | -0.086976 | 0.20599 | -0.009155 | -0.064087 | -0.15564 | -0.032043 | -0.1236 | 0.12817 | 124.4476 | 0.022889 | 124.411 | 124.1318 | 124.118 | 124.0677 | 124.086 | -124.2371 | -124.205 | 124.3835 | 124.379 | 60.0677 | 60.1181
46.9375 | 124.4339 | -60.141 | 64.032 | 0.11539 | -0.0056022 | 0.051029 | 0.057155 | 0.0013714 | -0.00012524 | -0.012545 | 0.11293 | -0.0045758 | 0.080496 | 0.091031 | -0.008294 | 0.0027121 | -0.0036126 | -0.091553 | 63.8947 | -60.2188 | 64.238 | -60.0494 | -60.3836 | -60.4156 | -0.07782 | 63.9359 | -60.1822 | 64.2105 | -60.1959 | -60.3195 | -60.228 | -0.07782 | -0.13733 | 0.20599 | 0.091553 | -0.27466 | -0.24262 | -0.19684 | -0.16479 | -0.041199 | -0.09613 | 0.17853 | -0.054932 | -0.086975 | -0.17853 | -0.045776 | -0.13733 | 0.16937 | 124.4568 | -0.013733 | 124.3927 | 124.1135 | 124.118 | 124.0356 | 124.0768 | -124.2508 | -124.2142 | 124.379 | 124.3515 | 60.0494 | 60.0632
47.9375 | 124.4888 | -60.141 | 64.0091 | 0.054357 | 0.0061468 | 0.064915 | 0.067836 | 0.0045764 | -0.0033302 | -0.014682 | -0.024402 | -0.00030381 | 0.070883 | 0.064328 | -0.005089 | -0.0047649 | -0.019635 | -0.068665 | 63.8763 | -60.2097 | 64.1418 | -60.141 | -60.4797 | -60.4706 | -0.013733 | 63.9221 | -60.173 | 64.2288 | -60.1547 | -60.26 | -60.2142 | -0.068665 | -0.13275 | 0.13275 | 0 | -0.32959 | -0.33875 | -0.26093 | -0.27008 | -0.032044 | -0.086975 | 0.21973 | -0.013733 | -0.073242 | -0.11902 | -0.041198 | -0.086975 | 0.068665 | 124.3515 | 0.018311 | 124.4019 | 124.086 | 124.0952 | 124.0173 | 124.0631 | -124.2188 | -124.1821 | 124.2828 | 124.3698 | 60.0723 | 60.1273
48.9375 | 124.4293 | -60.1593 | 64.0274 | -0.0066789 | -0.0066702 | 0.060642 | 0.066768 | 0.0099164 | -0.015079 | -0.0039998 | -0.29906 | 0.0039692 | 0.06127 | 0.018399 | -0.004021 | 0.0080531 | 0.0081364 | -0.10986 | 63.9267 | -60.228 | 64.2792 | -60.022 | -60.3653 | -60.3882 | -0.16022 | 63.913 | -60.2005 | 64.1876 | -60.2417 | -60.3378 | -60.2875 | -0.068664 | -0.10071 | 0.25177 | 0.13733 | -0.22888 | -0.20599 | -0.16022 | -0.13733 | -0.041198 | -0.11444 | 0.16022 | -0.082397 | -0.12817 | -0.17853 | -0.086976 | -0.13733 | 0.20599 | 124.5071 | -0.041199 | 124.3881 | 124.1547 | 124.1135 | 124.086 | 124.0723 | -124.2554 | -124.2279 | 124.4385 | 124.3469 | 60.0494 | 59.9991
49.9375 | 124.4202 | -60.1639 | 64.0366 | 0.14591 | 0.0018748 | 0.077732 | 0.064631 | -0.0071726 | 0.010556 | -0.0093408 | 0.021375 | 0.010377 | 0.059133 | 0.066464 | -0.00081695 | 0.0059161 | 0.0017274 | -0.10071 | 63.9404 | -60.2417 | 64.2883 | -60.0174 | -60.3516 | -60.3516 | -0.12817 | 63.9542 | -60.1913 | 64.1739 | -60.1089 | -60.379 | -60.3195 | -0.07782 | -0.09613 | 0.25177 | 0.14648 | -0.18768 | -0.18768 | -0.10986 | -0.10986 | -0.027466 | -0.082397 | 0.13733 | 0.054931 | -0.15564 | -0.21515 | -0.12817 | -0.18768 | 0.2243 | 124.53 | 0.082397 | 124.3652 | 124.1821 | 124.1455 | 124.1043 | 124.118 | -124.2783 | -124.2279 | 124.4522 | 124.3378 | 60.0632 | 60.0357
50.9375 | 124.4614 | -60.1364 | 64.0091 | 0.11539 | 0.0061468 | 0.064915 | 0.062495 | 0.010984 | 0.010556 | -0.0093408 | 0.067151 | -0.00030381 | 0.064474 | 0.056851 | 0.002387 | 0.0027121 | -0.0057486 | -0.09613 | 63.8947 | -60.228 | 64.2059 | -60.0723 | -60.4111 | -60.4294 | -0.050354 | 63.9084 | -60.1913 | 64.2288 | -60.1868 | -60.2829 | -60.2097 | -0.091552 | -0.11444 | 0.19684 | 0.064087 | -0.29297 | -0.27466 | -0.20142 | -0.18311 | -0.054931 | -0.10071 | 0.21973 | -0.050354 | -0.073242 | -0.14648 | -0.018311 | -0.091553 | 0.15564 | 124.4339 | 0.004577 | 124.4202 | 124.1226 | 124.0997 | 124.0311 | 124.0448 | -124.2371 | -124.2004 | 124.3423 | 124.3652 | 60.0403 | 60.0861
51.9375 | 124.4431 | -60.1501 | 64.032 | 0.26798 | -0.0045342 | 0.07346 | 0.05395 | 0.00030337 | 0.00094276 | -0.010409 | -0.070178 | -0.0024398 | 0.06661 | 0.032284 | -0.005089 | 0.0016441 | -0.015362 | -0.10529 | 63.9221 | -60.2325 | 64.1968 | -60.1089 | -60.4111 | -60.4111 | -0.054932 | 63.945 | -60.1868 | 64.2242 | -60.2097 | -60.3333 | -60.2325 | -0.082398 | -0.10986 | 0.16479 | 0.041198 | -0.26093 | -0.26093 | -0.17853 | -0.17853 | -0.036622 | -0.086975 | 0.19226 | -0.05951 | -0.082398 | -0.18311 | -0.045776 | -0.14648 | 0.1236 | 124.4293 | -0.022888 | 124.411 | 124.1547 | 124.1318 | 124.0723 | 124.0952 | -124.2645 | -124.2188 | 124.3469 | 124.3744 | 60.0449 | 60.0952
52.9375 | 124.4293 | -60.1318 | 64.0137 | 0.0085801 | -0.0023982 | 0.074528 | 0.064631 | 0.0013714 | -0.0011942 | 0.0056132 | 0.0061157 | 0.0050372 | 0.065542 | 0.082486 | -0.005089 | -0.0026279 | 0.019885 | -0.20599 | 63.8763 | -60.2463 | 64.238 | -60.0632 | -60.4111 | -60.4065 | -0.082397 | 63.9175 | -60.1822 | 64.2059 | -60.2051 | -60.3378 | -60.2554 | -0.11444 | -0.13733 | 0.2243 | 0.068665 | -0.27466 | -0.27924 | -0.16022 | -0.16479 | -0.050354 | -0.09613 | 0.19226 | -0.073242 | -0.1236 | -0.20599 | -0.073242 | -0.15564 | 0.18311 | 124.4843 | -0.022888 | 124.3881 | 124.1226 | 124.0997 | 124.0082 | 124.0494 | -124.2599 | -124.1959 | 124.3698 | 124.3378 | 59.9258 | 60.0494
53.9375 | 124.4568 | -60.1639 | 64.0045 | 0.069615 | -0.0077382 | 0.071323 | 0.065699 | -0.0018326 | -0.0022622 | -0.017886 | 0.067151 | -0.0067128 | 0.051657 | 0.052579 | 0.001319 | 0.0016441 | 0.015613 | -0.036621 | 63.8855 | -60.2097 | 64.1556 | -60.1273 | -60.466 | -60.4797 | 0 | 63.9175 | -60.1776 | 64.2334 | -60.1547 | -60.2829 | -60.2005 | -0.045777 | -0.11902 | 0.15106 | 0.036621 | -0.31586 | -0.30212 | -0.27008 | -0.25635 | -0.013733 | -0.086975 | 0.22888 | 0.009155 | -0.036621 | -0.11902 | -0.022888 | -0.10529 | 0.082398 | 124.3652 | 0.022888 | 124.411 | 124.0952 | 124.0952 | 124.0494 | 124.0814 | -124.2142 | -124.1821 | 124.3195 | 124.3973 | 60.1273 | 60.1639
54.9375 | 124.4476 | -60.1501 | 64.0182 | 0.023839 | -0.00026223 | 0.064915 | 0.063563 | -0.011446 | -0.018283 | -0.0039998 | 0.0061157 | -0.0013718 | 0.06661 | 0.089963 | -0.00081695 | 0.0016441 | -0.016431 | -0.059509 | 63.8809 | -60.1959 | 64.183 | -60.0815 | -60.4523 | -60.498 | -0.009155 | 63.9267 | -60.1639 | 64.2334 | -60.1776 | -60.2829 | -60.2097 | -0.045777 | -0.13733 | 0.16479 | 0.068664 | -0.3479 | -0.30213 | -0.30212 | -0.25635 | -0.013733 | -0.091553 | 0.21515 | -0.027466 | -0.05951 | -0.13275 | -0.045777 | -0.11902 | 0.11444 | 124.379 | -0.013733 | 124.3973 | 124.0768 | 124.0906 | 124.0311 | 124.0768 | -124.2142 | -124.1821 | 124.3332 | 124.3835 | 60.0906 | 60.141
55.9375 | 124.3835 | -60.1318 | 64.0594 | 0.13065 | -0.0056022 | 0.062778 | 0.063563 | -0.016787 | 0.011624 | 0.012021 | 0.0061157 | 0.011445 | 0.067678 | 0.064328 | 0.007728 | 0.0037801 | -0.0004086 | -0.09613 | 63.9359 | -60.228 | 64.2929 | -60.0037 | -60.3561 | -60.3516 | -0.1236 | 63.9587 | -60.2051 | 64.1464 | -60.2005 | -60.228 | -60.2463 | -0.09613 | -0.1236 | 0.23346 | 0.12817 | -0.21973 | -0.2243 | -0.1236 | -0.12817 | -0.073242 | -0.10071 | 0.086975 | -0.068664 | -0.11444 | -0.09613 | -0.041199 | -0.022888 | 0.2243 | 124.5209 | 0.004578 | 124.3515 | 124.1638 | 124.1638 | 124.0677 | 124.0906 | -124.2874 | -124.2645 | 124.4247 | 124.2783 | 60.0357 | 60.0082
56.9375 | 124.3881 | -60.1547 | 64.0549 | 0.039098 | -0.0077382 | 0.067051 | 0.059291 | 0.0088484 | 0.0094878 | 0.021634 | 0.0061157 | 0.0029002 | 0.064474 | 0.047238 | 0.004524 | 0.0016441 | 0.0006594 | -0.082397 | 63.913 | -60.2097 | 64.2975 | -59.9762 | -60.3333 | -60.3561 | -0.12817 | 63.9542 | -60.2097 | 64.1418 | -60.2875 | -60.3928 | -60.3058 | -0.054932 | -0.14191 | 0.24261 | 0.17853 | -0.20142 | -0.17853 | -0.14648 | -0.1236 | -0.054932 | -0.10071 | 0.086975 | -0.13275 | -0.15106 | -0.23804 | -0.09613 | -0.1831 | 0.23346 | 124.5071 | -0.07782 | 124.3515 | 124.1226 | 124.1638 | 124.0677 | 124.1089 | -124.2645 | -124.2645 | 124.4522 | 124.2966 | 60.0723 | 60.0266
57.9375 | 124.4339 | -60.1639 | 64.0457 | 0.069615 | -0.0034662 | 0.06171 | 0.059291 | 0.015257 | 0.0020108 | 0.013089 | 0.14344 | 0.0050372 | 0.070883 | 0.067532 | 0.009864 | 0.0080531 | -0.0025446 | -0.10071 | 63.8947 | -60.2142 | 64.238 | -60.0449 | -60.3928 | -60.3973 | -0.064087 | 63.9267 | -60.2097 | 64.2014 | -60.2371 | -60.3607 | -60.2371 | -0.050354 | -0.15106 | 0.19226 | 0.11902 | -0.23346 | -0.22888 | -0.18311 | -0.17853 | -0.045777 | -0.11902 | 0.15564 | -0.073243 | -0.073243 | -0.19684 | -0.027466 | -0.15106 | 0.16937 | 124.4522 | -0.027466 | 124.411 | 124.1089 | 124.1364 | 124.0585 | 124.0906 | -124.2599 | -124.2554 | 124.4019 | 124.3652 | 60.0632 | 60.0998
58.9375 | 124.4247 | -60.141 | 64.0274 | 0.11539 | -0.00026223 | 0.062778 | 0.058223 | -0.017855 | 0.010556 | 0.0077492 | 0.11293 | 0.0018322 | 0.080496 | 0.10598 | -0.014702 | -0.0090369 | 0.0092044 | -0.10529 | 63.8992 | -60.228 | 64.2517 | -60.0357 | -60.3836 | -60.379 | -0.086975 | 63.9313 | -60.2051 | 64.1602 | -60.2097 | -60.347 | -60.2737 | -0.086975 | -0.12817 | 0.2243 | 0.10529 | -0.23804 | -0.24262 | -0.15106 | -0.15564 | -0.064087 | -0.096131 | 0.13275 | -0.068665 | -0.13275 | -0.20599 | -0.068665 | -0.14191 | 0.19226 | 124.4797 | -0.004578 | 124.3652 | 124.1272 | 124.1364 | 124.0402 | 124.0723 | -124.2554 | -124.2325 | 124.3927 | 124.3011 | 60.0357 | 60.054
59.9375 | 124.3927 | -60.1456 | 64.032 | 0.084874 | -0.0098752 | 0.069187 | 0.062495 | 0.0024404 | -0.0043982 | -0.0072048 | -0.024402 | 0.0039692 | 0.067678 | 0.042966 | 0.002387 | 0.0016441 | -0.013226 | -0.10986 | 63.913 | -60.228 | 64.2792 | -60.0128 | -60.3516 | -60.3836 | -0.10986 | 63.9496 | -60.2005 | 64.1556 | -60.2509 | -60.3882 | -60.2875 | -0.082397 | -0.11902 | 0.24719 | 0.13275 | -0.23804 | -0.20599 | -0.15564 | -0.1236 | -0.054931 | -0.082397 | 0.1236 | -0.10528 | -0.14191 | -0.24262 | -0.086976 | -0.18768 | 0.21515 | 124.5071 | -0.050354 | 124.3561 | 124.1409 | 124.1501 | 124.0585 | 124.0952 | -124.2599 | -124.2325 | 124.4247 | 124.3011 | 60.0357 | 60.0357
60.9375 | 124.3744 | -60.1685 | 64.0549 | 0.069615 | -0.00026223 | 0.059574 | 0.068904 | 0.0045764 | -0.0022622 | -0.0072048 | 0.036633 | -0.0024398 | 0.069815 | 0.064328 | 0.00025105 | -0.0069009 | -0.0036126 | -0.09613 | 63.9084 | -60.2234 | 64.2883 | -59.9945 | -60.3424 | -60.3607 | -0.12817 | 63.9313 | -60.1959 | 64.1556 | -60.2646 | -60.3836 | -60.3058 | -0.054932 | -0.14649 | 0.23346 | 0.17395 | -0.19226 | -0.17395 | -0.13733 | -0.11902 | -0.027466 | -0.1236 | 0.10071 | -0.09613 | -0.13733 | -0.21515 | -0.10986 | -0.18768 | 0.22888 | 124.5117 | -0.068664 | 124.3515 | 124.1318 | 124.1272 | 124.0768 | 124.0997 | -124.2783 | -124.2508 | 124.4568 | 124.324 | 60.0723 | 60.0403
61.9375 | 124.4156 | -60.1318 | 64.0182 | 0.084874 | 0.01042 | 0.060642 | 0.058223 | 0.010984 | -0.0033302 | 0.01843 | 0.036633 | -0.0013718 | 0.062338 | 0.082486 | 0.001319 | 0.00057606 | 0.0049324 | -0.086975 | 63.9084 | -60.2325 | 64.2242 | -60.0403 | -60.4019 | -60.4019 | -0.07782 | 63.9267 | -60.1913 | 64.2059 | -60.1913 | -60.2875 | -60.2142 | -0.10071 | -0.10986 | 0.20599 | 0.091553 | -0.27008 | -0.27008 | -0.16937 | -0.16937 | -0.059509 | -0.091553 | 0.18768 | -0.059509 | -0.082397 | -0.15564 | -0.022888 | -0.096131 | 0.19226 | 124.4568 | 0 | 124.3973 | 124.1409 | 124.118 | 124.0402 | 124.0585 | -124.2508 | -124.2096 | 124.3561 | 124.3378 | 60.0449 | 60.054
62.9375 | 124.3744 | -60.173 | 64.0778 | 0.16117 | -0.0013302 | 0.05637 | 0.056086 | 0.013121 | -0.0043982 | -0.0072048 | -0.024402 | 0.0061052 | 0.06661 | 0.081418 | 0.00025105 | -0.00049194 | 0.0092044 | -0.07782 | 63.9359 | -60.2371 | 64.2929 | -59.9762 | -60.3241 | -60.347 | -0.16937 | 63.945 | -60.2005 | 64.1098 | -60.3012 | -60.4111 | -60.3333 | -0.064087 | -0.14191 | 0.21515 | 0.19684 | -0.17395 | -0.15106 | -0.10986 | -0.086975 | -0.027465 | -0.13275 | 0.032043 | -0.12817 | -0.16022 | -0.23804 | -0.13275 | -0.21057 | 0.26093 | 124.53 | -0.10071 | 124.3103 | 124.173 | 124.1455 | 124.1089 | 124.118 | -124.3149 | -124.2783 | 124.4659 | 124.2828 | 60.0952 | 60.0037
63.9375 | 124.3698 | -60.1822 | 64.0366 | -0.0066789 | -0.0045342 | 0.072392 | 0.062495 | -0.0050366 | 0.0041468 | 0.0024082 | 0.14344 | 0.0029002 | 0.078359 | 0.040829 | -0.006157 | -0.0036969 | 0.0038644 | 0.10986 | 63.9267 | -60.2051 | 64.3158 | -59.9625 | -60.3378 | -60.3516 | -0.14648 | 63.9587 | -60.2142 | 64.1052 | -60.2829 | -60.4248 | -60.3424 | -0.022888 | -0.10986 | 0.27924 | 0.21973 | -0.16937 | -0.15564 | -0.14648 | -0.13275 | -0.032043 | -0.07782 | 0.068665 | -0.10071 | -0.16022 | -0.24262 | -0.12817 | -0.21057 | 0.24262 | 124.5209 | -0.068665 | 124.3195 | 124.1318 | 124.173 | 124.1089 | 124.1409 | -124.2416 | -124.2508 | 124.498 | 124.2874 | 60.2921 | 60.0357
64.9375 | 124.3698 | -60.1501 | 64.032 | 0.039098 | -0.0013302 | 0.059574 | 0.059291 | 0.0099164 | 0.025509 | 0.014158 | 0.08241 | 0.0050372 | 0.073019 | 0.091031 | 0.00025105 | -0.010105 | 0.0027964 | -0.10071 | 63.9267 | -60.228 | 64.2838 | -60.0128 | -60.3333 | -60.3561 | -0.12817 | 63.9404 | -60.1913 | 64.1464 | -60.2509 | -60.3699 | -60.2783 | -0.07782 | -0.10529 | 0.25177 | 0.13733 | -0.20599 | -0.18311 | -0.12817 | -0.10529 | -0.041199 | -0.091552 | 0.11444 | -0.10071 | -0.12817 | -0.21973 | -0.086975 | -0.17853 | 0.21515 | 124.5117 | -0.059509 | 124.3378 | 124.1547 | 124.1318 | 124.0768 | 124.0906 | -124.2599 | -124.2233 | 124.4339 | 124.2966 | 60.0494 | 60.022
65.9375 | 124.3744 | -60.1776 | 64.0411 | 0.14591 | -0.0023982 | 0.06171 | 0.07104 | 0.0013714 | -0.0011942 | -0.0018638 | -0.054919 | 0.0082412 | 0.078359 | 0.06326 | -0.005089 | -0.0036969 | -0.018567 | -0.086975 | 63.9313 | -60.2463 | 64.2746 | -59.9991 | -60.3333 | -60.3653 | -0.1236 | 63.9404 | -60.2051 | 64.1373 | -60.2692 | -60.3836 | -60.2875 | -0.068665 | -0.10986 | 0.23346 | 0.17853 | -0.18768 | -0.15564 | -0.11902 | -0.086975 | -0.027466 | -0.10071 | 0.09613 | -0.091553 | -0.10986 | -0.20599 | -0.082398 | -0.17853 | 0.24719 | 124.5209 | -0.064087 | 124.3423 | 124.1776 | 124.1455 | 124.1089 | 124.118 | -124.2874 | -124.2462 | 124.4522 | 124.3149 | 60.0906 | 60.054
66.9375 | 124.4431 | -60.1273 | 64.0594 | 0.17643 | -0.0088062 | 0.063847 | 0.059291 | 0.0024404 | -0.0022622 | -0.0072048 | 0.29603 | -0.0045758 | 0.073019 | 0.058987 | 0.015205 | -0.00049194 | 0.0060004 | 0 | 63.9221 | -60.1776 | 64.1785 | -60.0906 | -60.4156 | -60.4477 | 0.032043 | 63.9267 | -60.1639 | 64.2059 | -60.1501 | -60.2417 | -60.1913 | -0.050354 | -0.13733 | 0.11902 | 0.036621 | -0.32044 | -0.28839 | -0.27008 | -0.23804 | -0.036621 | -0.13275 | 0.14648 | -0.022888 | -0.064087 | -0.11444 | -0.027466 | -0.07782 | 0.086975 | 124.3561 | 0.013733 | 124.3698 | 124.0997 | 124.0906 | 124.0494 | 124.054 | -124.2371 | -124.2233 | 124.3057 | 124.3332 | 60.1273 | 60.1593
67.9375 | 124.3607 | -60.1776 | 64.064 | -0.0066789 | -0.010943 | 0.068119 | 0.064631 | 0.0056444 | -0.014011 | -0.0050688 | -0.1007 | 0.0039692 | 0.067678 | 0.047238 | 0.001319 | -0.0047649 | -0.0046806 | -0.07782 | 63.9359 | -60.2371 | 64.2883 | -59.9945 | -60.3104 | -60.3333 | -0.12817 | 63.9542 | -60.1822 | 64.151 | -60.2783 | -60.4156 | -60.3058 | -0.05951 | -0.12817 | 0.2243 | 0.18311 | -0.15564 | -0.13275 | -0.09613 | -0.073242 | -0.004578 | -0.10986 | 0.086975 | -0.10071 | -0.12817 | -0.23804 | -0.1236 | -0.23346 | 0.24262 | 124.5255 | -0.09613 | 124.3332 | 124.173 | 124.1364 | 124.1135 | 124.1318 | -124.3011 | -124.2462 | 124.4659 | 124.3286 | 60.0998 | 60.0494
68.9375 | 124.4293 | -60.1456 | 64.0594 | 0.16117 | -0.0056022 | 0.067051 | 0.059291 | 0.0013714 | -0.016147 | -0.0039998 | -0.024402 | 0.0093092 | 0.06127 | 0.036557 | 0.00025105 | -0.0015599 | 0.012409 | -0.07782 | 63.9175 | -60.2371 | 64.2334 | -60.0311 | -60.3653 | -60.4019 | -0.086975 | 63.945 | -60.1685 | 64.1693 | -60.2188 | -60.3424 | -60.26 | -0.091553 | -0.14191 | 0.17395 | 0.11444 | -0.25635 | -0.21973 | -0.16479 | -0.12817 | -0.022888 | -0.11444 | 0.10986 | -0.073242 | -0.11444 | -0.19684 | -0.091553 | -0.17395 | 0.20599 | 124.4705 | -0.050354 | 124.3378 | 124.1547 | 124.1135 | 124.0631 | 124.0906 | -124.2966 | -124.2279 | 124.379 | 124.3149 | 60.0677 | 60.0586
69.9375 | 124.3607 | -60.1593 | 64.0457 | 0.039098 | 0.00080677 | 0.064915 | 0.07104 | 0.019529 | 0.016964 | 0.0056132 | -0.070178 | -0.0024398 | 0.06127 | 0.055783 | -0.006157 | 0.00057606 | 0.0017274 | -0.091553 | 63.9221 | -60.2554 | 64.2792 | -59.8068 | -60.2371 | -60.3378 | -0.1236 | 63.9862 | -60.2051 | 64.1235 | -60.2921 | -60.4156 | -60.3378 | -0.09613 | -0.1236 | 0.23346 | 0.35248 | -0.17853 | -0.07782 | -0.082398 | 0.01831 | -0.045776 | -0.059509 | 0.07782 | -0.13275 | -0.17853 | -0.25635 | -0.13275 | -0.21057 | 0.44861 | 124.5346 | -0.086975 | 124.3286 | 124.1776 | 124.1913 | 124.0814 | 124.1455 | -124.3011 | -124.2508 | 124.4385 | 124.2828 | 60.0677 | 60.0357
70.9375 | 124.3561 | -60.1685 | 64.0686 | 0.023839 | 0.00080677 | 0.054234 | 0.065699 | 0.0067124 | -0.0054662 | -0.0061368 | 0.54017 | -0.00030381 | 0.067678 | 0.062192 | 0.007728 | 0.0059161 | 0.016681 | -0.082397 | 63.9175 | -60.2371 | 64.2975 | -59.8572 | -60.3836 | -60.5896 | -0.073242 | 63.9954 | -60.2005 | 64.1052 | -60.3012 | -60.3973 | -60.3149 | -0.068665 | -0.15106 | 0.22888 | 0.31128 | -0.42114 | -0.21515 | -0.35248 | -0.14648 | -0.032043 | -0.073243 | 0.036621 | -0.13275 | -0.14648 | -0.22888 | -0.11444 | -0.19684 | 0.37994 | 124.5346 | -0.10071 | 124.3057 | 124.1547 | 124.1959 | 124.086 | 124.1638 | -124.3057 | -124.2691 | 124.4659 | 124.2737 | 60.0861 | 60.0952
71.9375 | 124.4888 | -60.0998 | 64.0366 | 0.023839 | -0.0013302 | 0.06171 | 0.056086 | 0.0088484 | 0.0062828 | 0.0066812 | 0.40284 | -0.0067128 | 0.068746 | 0.031216 | 0.00666 | -0.0090369 | 0.027362 | 0 | 63.9084 | -60.1776 | 64.1785 | -60.0952 | -60.4111 | -60.4385 | 0.064087 | 63.9496 | -60.1776 | 64.2334 | -60.1273 | -60.228 | -60.1913 | -0.07782 | -0.12817 | 0.14191 | 0.004577 | -0.33875 | -0.31128 | -0.26093 | -0.23346 | -0.07782 | -0.086975 | 0.19684 | -0.027466 | -0.091553 | -0.12817 | -0.013733 | -0.050354 | 0.082397 | 124.3561 | 0.050354 | 124.411 | 124.086 | 124.1272 | 124.0082 | 124.0494 | -124.2142 | -124.2142 | 124.2783 | 124.3332 | 60.0998 | 60.1639
72.9375 | 124.3698 | -60.1456 | 64.0411 | 0.11539 | 0.00080677 | 0.06171 | 0.072108 | 0.022734 | 0.01376 | 0.012021 | -0.054919 | 0.0050372 | 0.077291 | 0.076077 | -0.009362 | 0.0016441 | 0.012409 | -0.091553 | 63.8901 | -60.2325 | 64.2838 | -59.9945 | -60.3287 | -60.3424 | -0.1236 | 63.9404 | -60.1868 | 64.1418 | -60.2646 | -60.379 | -60.3012 | -0.086975 | -0.15106 | 0.24261 | 0.15106 | -0.19684 | -0.1831 | -0.10986 | -0.09613 | -0.041199 | -0.10071 | 0.10071 | -0.11902 | -0.15564 | -0.23346 | -0.11444 | -0.19226 | 0.23804 | 124.5163 | -0.077819 | 124.3286 | 124.1226 | 124.1272 | 124.0356 | 124.086 | -124.2737 | -124.2279 | 124.4293 | 124.2874 | 60.054 | 60.022
73.9375 | 124.3652 | -60.1547 | 64.0594 | 0.084874 | -0.0045342 | 0.068119 | 0.064631 | 0.00030337 | 0.024441 | -0.011477 | 0.021375 | 0.0071732 | 0.067678 | 0.062192 | 0.002387 | -0.0090369 | 0.010272 | -0.091553 | 63.9267 | -60.2142 | 64.2838 | -59.9854 | -60.3333 | -60.3241 | -0.11444 | 63.945 | -60.1959 | 64.1327 | -60.2875 | -60.3882 | -60.3287 | -0.059509 | -0.13275 | 0.2243 | 0.16937 | -0.16937 | -0.17853 | -0.10986 | -0.11902 | -0.041199 | -0.11444 | 0.073242 | -0.13275 | -0.17395 | -0.23346 | -0.13275 | -0.19226 | 0.22888 | 124.498 | -0.091553 | 124.3286 | 124.1409 | 124.1409 | 124.0814 | 124.0997 | -124.2737 | -124.2554 | 124.4385 | 124.2874 | 60.0632 | 60.0403
74.9375 | 124.4431 | -60.1318 | 64.0366 | 0.023839 | -0.0098752 | 0.05637 | 0.065699 | -0.0050366 | 0.0020108 | -0.0082728 | 0.021375 | 0.0029002 | 0.069815 | 0.053647 | 0.008796 | -0.0036969 | 0.0027964 | -0.086975 | 63.9038 | -60.2142 | 64.2197 | -60.0494 | -60.3973 | -60.4111 | -0.059509 | 63.9404 | -60.1776 | 64.1922 | -60.1822 | -60.3104 | -60.228 | -0.082397 | -0.13275 | 0.18311 | 0.082398 | -0.27924 | -0.2655 | -0.19684 | -0.18311 | -0.045776 | -0.09613 | 0.15564 | -0.050354 | -0.09613 | -0.17853 | -0.050354 | -0.13275 | 0.16479 | 124.4339 | -0.004578 | 124.3698 | 124.118 | 124.118 | 124.0356 | 124.0723 | -124.2508 | -124.2142 | 124.3515 | 124.324 | 60.0449 | 60.0723
75.9375 | 124.4247 | -60.1456 | 64.0366 | 0.039098 | -0.0088062 | 0.065983 | 0.068904 | 0.0024404 | 0.0041468 | -0.0018638 | 0.067151 | -0.0013718 | 0.080496 | 0.0686 | 0.005592 | 0.00057606 | 0.02309 | -0.09613 | 63.8901 | -60.2417 | 64.2426 | -60.0449 | -60.379 | -60.3928 | -0.07782 | 63.9221 | -60.1822 | 64.183 | -60.2097 | -60.3287 | -60.2737 | -0.09613 | -0.14648 | 0.20599 | 0.10071 | -0.24719 | -0.23346 | -0.15106 | -0.13733 | -0.036621 | -0.11444 | 0.14648 | -0.064087 | -0.12817 | -0.1831 | -0.091553 | -0.14648 | 0.19684 | 124.4843 | -0.027466 | 124.3652 | 124.1318 | 124.1043 | 124.0356 | 124.0677 | -124.2783 | -124.2188 | 124.3881 | 124.3286 | 60.0494 | 60.0677
76.9375 | 124.4934 | -60.1318 | 64.0274 | 0.17643 | -0.0023982 | 0.062778 | 0.065699 | -0.0082416 | 0.0084198 | -0.0029318 | 0.28077 | 0.0050372 | 0.070883 | 0.050442 | -0.004021 | -0.0058329 | 0.01134 | 0.032043 | 63.9313 | -60.1547 | 64.1922 | -60.0998 | -60.4568 | -60.4523 | 0.082397 | 63.9359 | -60.1456 | 64.2517 | -60.0906 | -60.1913 | -60.1822 | -0.022888 | -0.096131 | 0.16479 | 0.032044 | -0.32044 | -0.32501 | -0.29755 | -0.30212 | -0.013733 | -0.091553 | 0.2243 | 0.041199 | -0.050354 | -0.059509 | -0.036621 | -0.045776 | 0.054932 | 124.3469 | 0.054932 | 124.3973 | 124.086 | 124.0814 | 124.0631 | 124.0677 | -124.1821 | -124.173 | 124.324 | 124.3835 | 60.1639 | 60.2142
77.9375 | 124.3469 | -60.1501 | 64.0549 | 0.054357 | -0.00026223 | 0.063847 | 0.057155 | -0.0039686 | 0.011624 | 0.031247 | -0.070178 | 0.0061052 | 0.053793 | 0.066464 | -0.00081695 | 0.0037801 | -0.023907 | -0.09613 | 63.9084 | -60.2325 | 64.2746 | -60.2142 | -60.5621 | -60.1456 | -0.19684 | 63.9633 | -60.1913 | 64.1052 | -60.2829 | -60.4156 | -60.3333 | -0.082398 | -0.14649 | 0.21973 | -0.064087 | 0.004577 | -0.41199 | 0.086975 | -0.32959 | -0.041199 | -0.091553 | 0.050354 | -0.13275 | -0.18311 | -0.2655 | -0.14191 | -0.2243 | 0.018311 | 124.5071 | -0.091553 | 124.2966 | 124.1409 | 124.1547 | 124.0585 | 124.1135 | -124.2874 | -124.2462 | 124.4247 | 124.2554 | 60.054 | 59.9533
78.9375 | 124.3698 | -60.1501 | 64.0549 | 0.17643 | 0.0029428 | 0.064915 | 0.059291 | -0.0018326 | -0.00012524 | 0.017362 | 0.036633 | 0.015718 | 0.075155 | 0.052579 | 0.001319 | -0.00049194 | 0.0070684 | -0.068665 | 63.9267 | -60.2417 | 64.2792 | -60.0128 | -60.347 | -60.3561 | -0.1236 | 63.9542 | -60.1822 | 64.1602 | -60.2646 | -60.3561 | -60.3012 | -0.091553 | -0.12817 | 0.2243 | 0.13733 | -0.20599 | -0.19684 | -0.11444 | -0.10529 | -0.032044 | -0.10071 | 0.10528 | -0.11444 | -0.15106 | -0.20599 | -0.11902 | -0.17395 | 0.22888 | 124.5209 | -0.082397 | 124.3423 | 124.1684 | 124.1364 | 124.0768 | 124.1043 | -124.2966 | -124.2371 | 124.4293 | 124.3103 | 60.0815 | 60.0266
79.9375 | 124.3515 | -60.1593 | 64.0594 | 0.0085801 | -0.00026223 | 0.058506 | 0.052882 | 0.00030337 | 0.015896 | 0.014158 | -0.054919 | -0.0056438 | 0.067678 | 0.064328 | 0.012001 | 0.0027121 | -0.0025446 | -0.09613 | 63.9084 | -60.228 | 64.2792 | -59.9899 | -60.3424 | -60.347 | -0.13275 | 63.9542 | -60.1913 | 64.1418 | -60.2646 | -60.3882 | -60.3058 | -0.068664 | -0.15106 | 0.21973 | 0.16937 | -0.18768 | -0.18311 | -0.11902 | -0.11444 | -0.032043 | -0.10529 | 0.082398 | -0.10529 | -0.14648 | -0.22888 | -0.11444 | -0.19684 | 0.23804 | 124.5071 | -0.073242 | 124.3332 | 124.1364 | 124.1455 | 124.0677 | 124.1135 | -124.2874 | -124.2508 | 124.4385 | 124.3011 | 60.0632 | 60.0266
80.9688 | 124.4156 | -60.1135 | 64.0274 | 0.10013 | -0.0023982 | 0.062778 | 0.061427 | 0.016325 | -0.0043982 | -0.0093408 | 0.25026 | 0.00076419 | 0.065542 | 0.054715 | -0.004021 | 0.0048481 | -0.0046806 | -0.054932 | 63.8763 | -60.2051 | 64.1418 | -60.0677 | -60.3378 | -60.3882 | -0.054932 | 63.9175 | -60.1959 | 64.1876 | -60.1776 | -60.2692 | -60.2463 | -0.091553 | -0.15106 | 0.11444 | 0.045776 | -0.27466 | -0.2243 | -0.18311 | -0.13275 | -0.082398 | -0.10986 | 0.16022 | -0.064087 | -0.13275 | -0.15564 | -0.050354 | -0.073242 | 0.13733 | 124.3469 | 0.018311 | 124.3835 | 124.0814 | 124.1135 | 123.9899 | 124.0311 | -124.2325 | -124.2233 | 124.2554 | 124.3011 | 60.0586 | 60.0586
81.9375 | 124.4064 | -60.1181 | 64.0869 | 0.10013 | 0.0072148 | 0.058506 | 0.063563 | -0.0039686 | -0.012943 | -0.020022 | 0.21974 | -0.0088488 | 0.070883 | 0.075009 | 0.002387 | -0.012242 | -0.0004086 | 0.086975 | 63.9175 | -60.1639 | 64.2059 | -60.0861 | -60.4156 | -60.4065 | 0.07782 | 63.9496 | -60.1501 | 64.2014 | -60.1501 | -60.26 | -60.2325 | -0.045776 | -0.16937 | 0.11902 | 0.032043 | -0.28839 | -0.29755 | -0.24262 | -0.25177 | -0.032043 | -0.13733 | 0.11444 | -0.032043 | -0.11444 | -0.14191 | -0.082398 | -0.10986 | 0.077819 | 124.3698 | 0 | 124.3515 | 124.0814 | 124.0997 | 124.0356 | 124.0677 | -124.2508 | -124.2371 | 124.324 | 124.3195 | 60.2051 | 60.1959
82.9375 | 124.4156 | -60.1547 | 64.0503 | 0.2222 | 0.0029428 | 0.065983 | 0.067836 | -0.019991 | 0.0030788 | 0.0045452 | -0.0091433 | -0.0013718 | 0.062338 | 0.065396 | -0.004021 | 0.0037801 | -0.010022 | -0.09613 | 63.9038 | -60.2463 | 64.2242 | -60.0403 | -60.379 | -60.3745 | -0.073242 | 63.9542 | -60.1822 | 64.1785 | -60.2005 | -60.3333 | -60.2417 | -0.091553 | -0.14648 | 0.17395 | 0.11444 | -0.21973 | -0.2243 | -0.12817 | -0.13275 | -0.027466 | -0.09613 | 0.12817 | -0.045776 | -0.086975 | -0.17853 | -0.059509 | -0.15106 | 0.20599 | 124.4705 | -0.01831 | 124.3607 | 124.1501 | 124.1364 | 124.0585 | 124.1089 | -124.2966 | -124.2325 | 124.379 | 124.3332 | 60.0586 | 60.0815
83.9375 | 124.3332 | -60.1776 | 64.0778 | 0.25272 | -0.0056022 | 0.063847 | 0.07104 | 0.0035084 | -0.0011942 | 0.0045452 | 0.036633 | 0.0050372 | 0.074087 | 0.10278 | -0.00081695 | 0.0027121 | 0.013477 | -0.054932 | 63.9359 | -60.2097 | 64.2975 | -59.9762 | -60.3378 | -60.3378 | -0.1236 | 63.9725 | -60.1959 | 64.1281 | -60.2966 | -60.379 | -60.3058 | -0.032044 | -0.14191 | 0.21973 | 0.20142 | -0.16022 | -0.16022 | -0.12817 | -0.12817 | -0.018311 | -0.10529 | 0.050354 | -0.11902 | -0.12817 | -0.20142 | -0.10986 | -0.1831 | 0.23346 | 124.5071 | -0.10071 | 124.324 | 124.1455 | 124.1684 | 124.1135 | 124.1501 | -124.2874 | -124.2737 | 124.4751 | 124.3057 | 60.1227 | 60.054
84.9375 | 124.3607 | -60.1685 | 64.0594 | 0.054357 | -0.0045342 | 0.062778 | 0.073176 | 0.02487 | -0.0043982 | -0.0029318 | -0.03966 | 0.0029002 | 0.077291 | 0.08569 | 0.00666 | 0.0048481 | 0.0070684 | -0.086975 | 63.9359 | -60.2325 | 64.2746 | -59.9762 | -60.3058 | -60.3149 | -0.13733 | 63.9496 | -60.1913 | 64.1235 | -60.3012 | -60.4202 | -60.3104 | -0.064087 | -0.1236 | 0.21515 | 0.19226 | -0.14648 | -0.13733 | -0.082397 | -0.073242 | -0.022888 | -0.10986 | 0.064087 | -0.13275 | -0.14191 | -0.25177 | -0.11902 | -0.22888 | 0.25635 | 124.5071 | -0.10986 | 124.3149 | 124.1684 | 124.1409 | 124.1043 | 124.118 | -124.292 | -124.2508 | 124.4431 | 124.292 | 60.0815 | 60.0311
85.9375 | 124.4019 | -60.1456 | 64.032 | 0.023839 | -0.010943 | 0.062778 | 0.056086 | -0.00076463 | -0.0086702 | -0.00079579 | -0.024402 | 0.0050372 | 0.059133 | 0.079282 | 0.003456 | 0.016598 | 0.017749 | -0.086975 | 63.9175 | -60.2325 | 64.2609 | -60.0037 | -60.3516 | -60.3745 | -0.10529 | 63.9313 | -60.173 | 64.151 | -60.2371 | -60.3653 | -60.2783 | -0.086975 | -0.11444 | 0.22888 | 0.14191 | -0.22888 | -0.20599 | -0.14191 | -0.11902 | -0.027466 | -0.10071 | 0.11902 | -0.091553 | -0.13275 | -0.21973 | -0.10529 | -0.19226 | 0.22888 | 124.4934 | -0.064087 | 124.324 | 124.1501 | 124.1043 | 124.0631 | 124.0768 | -124.2645 | -124.205 | 124.4064 | 124.2966 | 60.0586 | 60.0403
86.9375 | 124.411 | -60.0906 | 64.0594 | -0.0066789 | 0.0018748 | 0.070255 | 0.061427 | -0.0018326 | -0.016147 | 0.00027221 | 0.28077 | -0.0067128 | 0.065542 | 0.054715 | -0.001885 | -0.00049194 | 0.016681 | 0.07782 | 63.9084 | -60.1593 | 64.1602 | -60.1089 | -60.4248 | -60.4111 | 0.091553 | 63.9587 | -60.1273 | 64.2334 | -60.1089 | -60.228 | -60.1913 | -0.068665 | -0.15106 | 0.10071 | -0.018311 | -0.32043 | -0.33417 | -0.25177 | -0.2655 | -0.036621 | -0.10071 | 0.17395 | -0.018311 | -0.10071 | -0.13733 | -0.064087 | -0.10071 | 0.050354 | 124.3195 | 0.01831 | 124.3607 | 124.0677 | 124.086 | 123.999 | 124.0494 | -124.2188 | -124.1867 | 124.2508 | 124.324 | 60.1685 | 60.1822
87.9375 | 124.3652 | -60.1227 | 64.0411 | 0.10013 | 0.0018748 | 0.060642 | 0.061427 | -0.0039686 | -0.0076022 | -0.0061368 | -0.0091433 | -0.0077808 | 0.06661 | 0.064328 | -0.004021 | 0.00057606 | 0.01134 | -0.09613 | 63.9038 | -60.2371 | 64.27 | -60.0082 | -60.3241 | -60.3607 | -0.11444 | 63.945 | -60.1959 | 64.1464 | -60.2371 | -60.3561 | -60.2829 | -0.11444 | -0.13733 | 0.22888 | 0.11444 | -0.23804 | -0.20142 | -0.1236 | -0.086975 | -0.073242 | -0.096131 | 0.10528 | -0.11444 | -0.16022 | -0.23346 | -0.086975 | -0.16022 | 0.22888 | 124.5071 | -0.041199 | 124.3423 | 124.1409 | 124.1409 | 124.0265 | 124.0677 | -124.2783 | -124.2371 | 124.3927 | 124.2691 | 60.0266 | 60.0082
88.9375 | 124.4385 | -60.1181 | 64.0045 | 0.039098 | -0.0023982 | 0.06171 | 0.061427 | -0.0093096 | -0.012943 | -0.013613 | 0.021375 | -0.0024398 | 0.065542 | 0.064328 | 0.002387 | 0.015529 | 0.0081364 | -0.073242 | 63.8947 | -60.228 | 64.183 | -60.0906 | -60.4294 | -60.4385 | -0.050354 | 63.8855 | -60.1685 | 64.2197 | -60.1913 | -60.2829 | -60.2005 | -0.10986 | -0.10986 | 0.17853 | 0.027466 | -0.32044 | -0.31128 | -0.21057 | -0.20142 | -0.050354 | -0.11902 | 0.21515 | -0.073242 | -0.082397 | -0.1648 | -0.032043 | -0.11444 | 0.13733 | 124.411 | -0.022888 | 124.3881 | 124.1226 | 124.054 | 124.0128 | 124.0036 | -124.2325 | -124.173 | 124.3011 | 124.3378 | 60.0449 | 60.0677
89.9375 | 124.4339 | -60.1044 | 63.9954 | 0.054357 | -0.0023982 | 0.06171 | 0.064631 | 0.0045764 | -0.0065342 | -0.0093408 | 0.12819 | -0.00030381 | 0.064474 | 0.066464 | 0.003456 | 0.010189 | -0.0089536 | -0.036621 | 63.8809 | -60.1639 | 64.119 | -60.1547 | -60.4614 | -60.466 | 0.009155 | 63.9038 | -60.1547 | 64.1968 | -60.1593 | -60.2783 | -60.2234 | -0.059509 | -0.11444 | 0.1236 | -0.050354 | -0.36163 | -0.35706 | -0.30212 | -0.29755 | -0.050354 | -0.091552 | 0.20142 | -0.054932 | -0.11902 | -0.17395 | -0.068665 | -0.1236 | 0.009155 | 124.2828 | -0.004578 | 124.3515 | 124.0448 | 124.0585 | 123.9853 | 124.0082 | -124.1592 | -124.1501 | 124.2233 | 124.3011 | 60.0677 | 60.1135
90.9375 | 124.3652 | -60.141 | 64.0274 | 0.023839 | 0.0029428 | 0.059574 | 0.061427 | 0.0077804 | -0.0033302 | -0.014682 | -0.054919 | 0.0039692 | 0.076223 | 0.06326 | -0.008294 | 0.0091211 | 0.0027964 | -0.091553 | 63.9175 | -60.2234 | 64.2609 | -59.9854 | -60.347 | -60.3516 | -0.11444 | 63.9816 | -60.2051 | 64.1464 | -60.26 | -60.3699 | -60.2966 | -0.082398 | -0.10986 | 0.23346 | 0.15564 | -0.21057 | -0.20599 | -0.12817 | -0.1236 | -0.064087 | -0.045777 | 0.11902 | -0.11902 | -0.15564 | -0.22888 | -0.091553 | -0.16479 | 0.23804 | 124.4843 | -0.054932 | 124.3515 | 124.1409 | 124.1867 | 124.0585 | 124.1226 | -124.2508 | -124.2325 | 124.4019 | 124.2874 | 60.0494 | 60.0266
91.9844 | 124.4568 | -60.0998 | 64.0594 | 0.11539 | -0.0034662 | 0.057438 | 0.059291 | -0.0093096 | 0.026577 | -0.014682 | 0.26551 | -0.0035078 | 0.069815 | 0.065396 | -0.004021 | 0.00057606 | -0.010022 | 0.054932 | 63.9084 | -60.1776 | 64.1556 | -60.1089 | -60.4431 | -60.434 | 0.10071 | 63.9633 | -60.1135 | 64.2242 | -60.0952 | -60.2188 | -60.1685 | -0.07782 | -0.15106 | 0.096131 | -0.009156 | -0.33417 | -0.34332 | -0.25635 | -0.2655 | -0.013733 | -0.09613 | 0.16479 | 0.004577 | -0.068665 | -0.11902 | -0.054932 | -0.10529 | 0.068664 | 124.3332 | 0.01831 | 124.3378 | 124.086 | 124.0768 | 124.0082 | 124.0631 | -124.2371 | -124.173 | 124.2554 | 124.324 | 60.1547 | 60.2005
92.9688 | 124.4614 | -60.1227 | 64.0228 | -0.082972 | 0.020033 | 0.075596 | 0.061427 | -0.0050366 | 0.015896 | -0.0039998 | 0.1587 | 0.0082412 | 0.064474 | 0.045102 | -0.001885 | 0.010189 | -0.0057486 | -0.10529 | 63.8123 | -60.2142 | 64.1327 | -60.1227 | -60.4614 | -60.5209 | 0.022888 | 63.8809 | -60.1593 | 64.2334 | -60.1501 | -60.2646 | -60.2188 | -0.091552 | -0.21057 | 0.10986 | 0 | -0.39825 | -0.33875 | -0.3067 | -0.24719 | -0.036621 | -0.14191 | 0.21057 | -0.027465 | -0.09613 | -0.14191 | -0.059509 | -0.10529 | 0.091552 | 124.3469 | 0.009156 | 124.3927 | 124.0265 | 124.0402 | 123.9349 | 124.0036 | -124.2371 | -124.1821 | 124.2554 | 124.3561 | 60.0174 | 60.1456
93.9375 | 124.4247 | -60.141 | 64.0274 | 0.039098 | 0.0029428 | 0.063847 | 0.065699 | -0.0029006 | 0.00094276 | 0.00027221 | -0.024402 | 0.0039692 | 0.068746 | 0.050442 | 0.00025105 | 0.0016441 | -0.0046806 | -0.086975 | 63.8901 | -60.2325 | 64.1968 | -60.0494 | -60.3745 | -60.4019 | -0.041199 | 63.9084 | -60.1776 | 64.2014 | -60.2005 | -60.3195 | -60.2142 | -0.091553 | -0.13733 | 0.16937 | 0.091553 | -0.26093 | -0.23346 | -0.16937 | -0.14191 | -0.036621 | -0.11902 | 0.17395 | -0.059509 | -0.073242 | -0.17853 | -0.036621 | -0.14191 | 0.18311 | 124.4293 | -0.022888 | 124.379 | 124.1226 | 124.086 | 124.0311 | 124.0494 | -124.2599 | -124.205 | 124.3378 | 124.3423 | 60.054 | 60.0998
94.9375 | 124.411 | -60.1135 | 64.0366 | 0.0085801 | 0.0061468 | 0.071323 | 0.063563 | -0.0039686 | 0.0030788 | -0.014682 | 0.235 | -0.00030381 | 0.068746 | 0.065396 | 0.012001 | -0.0036969 | -0.0068176 | -0.027466 | 63.9313 | -60.2005 | 64.1693 | -60.0769 | -60.4156 | -60.4202 | -0.022888 | 63.9313 | -60.1364 | 64.1556 | -60.1868 | -60.3104 | -60.2325 | -0.086975 | -0.10529 | 0.13275 | 0.036621 | -0.3067 | -0.30212 | -0.21973 | -0.21515 | -0.022889 | -0.10529 | 0.11902 | -0.073243 | -0.11902 | -0.19684 | -0.09613 | -0.17395 | 0.1236 | 124.3698 | -0.050354 | 124.292 | 124.1318 | 124.0677 | 124.0448 | 124.0448 | -124.2371 | -124.173 | 124.2828 | 124.2691 | 60.0861 | 60.0906
96 | 124.4476 | -60.1364 | 63.9954 | 0.16117 | -0.0023982 | 0.058506 | 0.07104 | -0.0018326 | 0.00094276 | 0.0013402 | -0.0091433 | -0.00030381 | 0.085836 | 0.072873 | -0.00081695 | 0.0091211 | -0.010022 | 0.11902 | 63.8855 | -60.1639 | 64.1373 | -60.1639 | -60.5072 | -60.498 | 0.004578 | 63.8992 | -60.1685 | 64.238 | -60.173 | -60.2737 | -60.2097 | -0.027465 | -0.10986 | 0.14191 | -0.027465 | -0.36163 | -0.37079 | -0.33417 | -0.34332 | -0.032043 | -0.09613 | 0.24262 | -0.036621 | -0.073242 | -0.13733 | -0.041199 | -0.10529 | 0 | 124.3011 | -0.004578 | 124.4064 | 124.0494 | 124.0677 | 124.0219 | 124.0356 | -124.1592 | -124.1638 | 124.2737 | 124.3744 | 60.2554 | 60.141
96.9688 | 124.3195 | -60.1547 | 64.0823 | -0.0066789 | -0.0023982 | 0.069187 | 0.075312 | 0.0099164 | -0.012943 | 0.0066812 | -0.054919 | 0.0039692 | 0.062338 | 0.094235 | -0.00081695 | 0.0091211 | -0.0036126 | -0.036621 | 63.9359 | -60.2142 | 64.2746 | -59.9945 | -60.3195 | -60.3104 | -0.12817 | 63.9542 | -60.1868 | 64.1098 | -60.3149 | -60.4385 | -60.3241 | -0.059509 | -0.14648 | 0.19226 | 0.16022 | -0.15564 | -0.16479 | -0.096131 | -0.10529 | -0.032044 | -0.12817 | 0.027466 | -0.16022 | -0.16937 | -0.28381 | -0.13733 | -0.25177 | 0.21973 | 124.4888 | -0.12817 | 124.2966 | 124.1501 | 124.1409 | 124.0906 | 124.1089 | -124.2966 | -124.2691 | 124.4293 | 124.2645 | 60.1181 | 60.0266
97.9375 | 124.3607 | -60.1547 | 64.0503 | 0.11539 | 0.00080677 | 0.063847 | 0.061427 | 0.010984 | 0.025509 | 0.010953 | -0.085437 | -0.0013718 | 0.059133 | 0.10278 | -0.001885 | 0.00057606 | -0.018567 | -0.086975 | 63.9267 | -60.2371 | 64.2883 | -59.9808 | -60.3149 | -60.3195 | -0.13275 | 63.9404 | -60.2051 | 64.1098 | -60.2737 | -60.4111 | -60.3195 | -0.082398 | -0.1236 | 0.23804 | 0.17395 | -0.16479 | -0.16022 | -0.082397 | -0.077819 | -0.050354 | -0.10986 | 0.059509 | -0.11902 | -0.16479 | -0.25635 | -0.11444 | -0.20599 | 0.25635 | 124.5255 | -0.068665 | 124.3149 | 124.1638 | 124.1455 | 124.0814 | 124.0952 | -124.2874 | -124.2554 | 124.4431 | 124.2645 | 60.0677 | 60.022
98.9375 | 124.3835 | -60.1593 | 64.0457 | 0.14591 | 0.0029428 | 0.068119 | 0.067836 | 0.0035084 | -0.0043982 | -0.010409 | 0.0061157 | -0.0013718 | 0.059133 | 0.067532 | -0.005089 | -0.00049194 | 0.0092044 | -0.10071 | 63.9084 | -60.2371 | 64.2654 | -60.0082 | -60.3561 | -60.3836 | -0.10071 | 63.9267 | -60.1685 | 64.1556 | -60.228 | -60.3516 | -60.2692 | -0.07782 | -0.13733 | 0.21973 | 0.15106 | -0.2243 | -0.19684 | -0.14648 | -0.11902 | -0.009155 | -0.11902 | 0.10986 | -0.068664 | -0.10986 | -0.19226 | -0.10071 | -0.18311 | 0.22888 | 124.5026 | -0.059509 | 124.324 | 124.1455 | 124.0952 | 124.0677 | 124.086 | -124.2828 | -124.2142 | 124.4247 | 124.3149 | 60.0586 | 60.0586
99.9375 | 124.498 | -60.1089 | 64.0503 | 0.10013 | 0.0040108 | 0.048893 | 0.061427 | -0.0082416 | -0.038578 | 0.0013402 | 0.18922 | 0.0029002 | 0.074087 | 0.087826 | 0.00666 | -0.020786 | 0.017749 | 0.082397 | 63.9038 | -60.1547 | 64.3295 | -59.9991 | -60.6354 | -60.5576 | 0.10529 | 63.9496 | -60.1501 | 64.238 | -60.0815 | -60.1776 | -60.1593 | -0.045776 | -0.14648 | 0.27924 | 0.10986 | -0.44861 | -0.52643 | -0.40283 | -0.48065 | -0.041198 | -0.10071 | 0.18768 | 0.027466 | -0.050354 | -0.068664 | -0.009156 | -0.027466 | 0.15564 | 124.4843 | 0.068664 | 124.3881 | 124.0585 | 124.0997 | 124.0128 | 124.0585 | -124.205 | -124.2004 | 124.4385 | 124.3469 | 60.1913 | 60.2142
100.9375 | 124.379 | -60.1593 | 64.0411 | -0.0066789 | -0.0034662 | 0.059574 | 0.07104 | 0.0056444 | -0.017215 | 0.0013402 | 0.097669 | -0.00030381 | 0.060202 | 0.048306 | -0.013634 | 0.0027121 | -0.0068176 | -0.10071 | 63.9175 | -60.2234 | 64.2792 | -60.0082 | -60.3561 | -60.3561 | -0.10986 | 63.9267 | -60.1776 | 64.1464 | -60.2509 | -60.3653 | -60.2875 | -0.064087 | -0.1236 | 0.23804 | 0.15106 | -0.19684 | -0.19684 | -0.13275 | -0.13275 | -0.01831 | -0.11444 | 0.10528 | -0.091552 | -0.12817 | -0.20599 | -0.10986 | -0.18768 | 0.21515 | 124.5026 | -0.073242 | 124.324 | 124.1409 | 124.1043 | 124.0768 | 124.086 | -124.2645 | -124.2188 | 124.4385 | 124.3057 | 60.0586 | 60.0494
101.9219 | 124.4476 | -60.1273 | 64.0182 | 0.11539 | 0.0050788 | 0.062778 | 0.061427 | -0.0039686 | -0.021488 | 0.0066812 | 0.37233 | 0.0029002 | 0.076223 | 0.082486 | -0.002953 | 0.0027121 | 0.0060004 | -0.022888 | 63.8489 | -60.2051 | 64.1373 | -60.0632 | -60.5942 | -60.6354 | 0 | 63.9313 | -60.1456 | 64.1876 | -60.1685 | -60.2554 | -60.1913 | -0.07782 | -0.16937 | 0.11902 | 0.064087 | -0.50812 | -0.46692 | -0.4303 | -0.3891 | -0.018311 | -0.086976 | 0.16937 | -0.041199 | -0.064087 | -0.12817 | -0.045776 | -0.10986 | 0.14191 | 124.3423 | -0.022888 | 124.3332 | 124.054 | 124.0768 | 123.9761 | 124.0585 | -124.2233 | -124.1638 | 124.2645 | 124.3149 | 60.1044 | 60.1273
102.9375 | 124.4614 | -60.141 | 64.0091 | 0.054357 | 0.0072148 | 0.060642 | 0.056086 | 0.0056444 | -0.017215 | 0.0024082 | -0.054919 | 0.0039692 | 0.070883 | 0.048306 | -0.006157 | 0.0080531 | -0.0089536 | -0.10071 | 63.8763 | -60.2188 | 64.2014 | -60.054 | -60.3882 | -60.4111 | -0.064087 | 63.9221 | -60.141 | 64.2151 | -60.173 | -60.3561 | -60.2509 | -0.07782 | -0.13275 | 0.19226 | 0.086975 | -0.27008 | -0.24719 | -0.19226 | -0.16937 | 0 | -0.086975 | 0.20599 | -0.032044 | -0.10986 | -0.21515 | -0.10986 | -0.21515 | 0.1648 | 124.4202 | -0.032044 | 124.3561 | 124.0952 | 124.0631 | 124.0173 | 124.0631 | -124.2279 | -124.1501 | 124.3423 | 124.3561 | 60.0403 | 60.0769
103.9375 | 124.3607 | -60.1318 | 64.0457 | 0.054357 | -0.0034662 | 0.062778 | 0.069972 | 0.0067124 | -0.0076022 | 0.012021 | 0.021375 | 0.0050372 | 0.063406 | 0.037625 | 0.008796 | 0.0059161 | 0.019885 | -0.091553 | 63.9267 | -60.2097 | 64.2838 | -59.9854 | -60.347 | -60.3516 | -0.12817 | 63.9496 | -60.1868 | 64.1373 | -60.2829 | -60.379 | -60.3058 | -0.07782 | -0.11902 | 0.23804 | 0.14648 | -0.21973 | -0.21515 | -0.14191 | -0.13733 | -0.054932 | -0.09613 | 0.091553 | -0.15106 | -0.17395 | -0.24719 | -0.11902 | -0.19226 | 0.2243 | 124.4934 | -0.09613 | 124.324 | 124.1364 | 124.1364 | 124.0585 | 124.0814 | -124.2554 | -124.2325 | 124.4156 | 124.2691 | 60.0403 | 60.0037
104.9375 | 124.3835 | -60.1181 | 64.064 | 0.16117 | 0.0040108 | 0.063847 | 0.061427 | 0.022734 | 0.011624 | -0.00079579 | -0.085437 | -0.0056438 | 0.068746 | 0.050442 | -0.002953 | 0.012325 | -0.0046806 | 0.041199 | 63.945 | -60.1959 | 64.2288 | -60.0174 | -60.3653 | -60.3561 | -0.20599 | 63.945 | -60.2051 | 64.151 | -60.1913 | -60.3012 | -60.228 | -0.07782 | -0.11902 | 0.16479 | 0.10071 | -0.23804 | -0.24719 | -0.16022 | -0.16937 | -0.086975 | -0.11902 | 0.086975 | -0.073242 | -0.10986 | -0.18311 | -0.022888 | -0.09613 | 0.17853 | 124.4247 | 0.013733 | 124.3561 | 124.1409 | 124.1501 | 124.0631 | 124.0631 | -124.2599 | -124.2691 | 124.3469 | 124.2691 | 60.1593 | 59.9121
105.9375 | 124.3195 | -60.173 | 64.0732 | 0.11539 | 0.012556 | 0.059574 | 0.07104 | 0.022734 | -0.016147 | -0.0061368 | -0.03966 | -0.0013718 | 0.06661 | 0.049374 | -0.004021 | 0.012325 | -0.010022 | -0.027466 | 63.913 | -60.2188 | 64.2929 | -59.9808 | -60.2966 | -60.3333 | -0.11902 | 63.9816 | -60.1959 | 64.1052 | -60.2646 | -60.4065 | -60.3058 | -0.045776 | -0.16022 | 0.21973 | 0.19226 | -0.16022 | -0.1236 | -0.11444 | -0.07782 | -0.022888 | -0.091553 | 0.032044 | -0.091552 | -0.13275 | -0.23346 | -0.10986 | -0.21057 | 0.23804 | 124.5117 | -0.068664 | 124.3011 | 124.1318 | 124.1776 | 124.086 | 124.1547 | -124.292 | -124.2691 | 124.4659 | 124.2783 | 60.1456 | 60.054
106.9375 | 124.3973 | -60.141 | 64.0503 | 0.10013 | -0.0023982 | 0.069187 | 0.066768 | 0.0099164 | -0.014011 | -0.00079579 | 0.08241 | -0.0099168 | 0.063406 | 0.064328 | -0.001885 | -0.0036969 | -0.0004086 | -0.091553 | 63.913 | -60.2234 | 64.2471 | -60.0082 | -60.3561 | -60.3699 | -0.09613 | 63.9404 | -60.1822 | 64.1693 | -60.228 | -60.3378 | -60.2737 | -0.082398 | -0.13733 | 0.19684 | 0.13275 | -0.22888 | -0.21515 | -0.14648 | -0.13275 | -0.041199 | -0.10986 | 0.11902 | -0.086975 | -0.13275 | -0.19684 | -0.091553 | -0.15564 | 0.21515 | 124.4705 | -0.045776 | 124.3515 | 124.1364 | 124.1226 | 124.054 | 124.0814 | -124.2737 | -124.2325 | 124.3881 | 124.3103 | 60.0494 | 60.0449
107.9375 | 124.379 | -60.1547 | 64.0549 | 0.14591 | 0.0050788 | 0.057438 | 0.063563 | -0.0050366 | -0.0022622 | -0.0061368 | 0.0061157 | 0.0071732 | 0.064474 | 0.050442 | -0.001885 | -0.0058329 | 0.0017274 | -0.09613 | 63.8947 | -60.2234 | 64.2563 | -60.0037 | -60.3241 | -60.3607 | -0.11444 | 63.9404 | -60.1593 | 64.1556 | -60.2234 | -60.3287 | -60.2554 | -0.068665 | -0.16022 | 0.20142 | 0.15106 | -0.20599 | -0.16937 | -0.13733 | -0.10071 | -0.004578 | -0.11444 | 0.10071 | -0.068665 | -0.10071 | -0.17395 | -0.09613 | -0.16937 | 0.21973 | 124.4797 | -0.064087 | 124.3149 | 124.118 | 124.0997 | 124.0494 | 124.0952 | -124.2783 | -124.2142 | 124.411 | 124.3103 | 60.0586 | 60.0403
108.9219 | 124.4568 | -60.1135 | 64.0091 | 0.023839 | -0.0066702 | 0.069187 | 0.059291 | -0.00076463 | 0.014828 | -0.014682 | 0.12819 | -0.0035078 | 0.074087 | 0.055783 | 0.002387 | 0.0059161 | -0.0068176 | -0.027466 | 63.8718 | -60.1822 | 64.1235 | -60.141 | -60.498 | -60.4843 | -0.018311 | 63.8947 | -60.1776 | 64.2242 | -60.1227 | -60.228 | -60.173 | -0.068665 | -0.13733 | 0.11444 | -0.027466 | -0.37079 | -0.38452 | -0.30212 | -0.31586 | -0.064087 | -0.11444 | 0.21515 | -0.009156 | -0.05951 | -0.11444 | 0.004577 | -0.050354 | 0.041199 | 124.3057 | 0.054931 | 124.4019 | 124.054 | 124.0723 | 123.9853 | 124.0082 | -124.1913 | -124.1867 | 124.2371 | 124.3378 | 60.0861 | 60.0952
109.9531 | 124.4339 | -60.1135 | 64.0091 | -0.037196 | 0.0072148 | 0.067051 | 0.065699 | -0.010378 | -0.0097382 | -0.013613 | -0.0091433 | -0.0045758 | 0.065542 | 0.072873 | -0.007226 | -0.0079689 | -0.0078856 | -0.050354 | 63.8901 | -60.2051 | 64.151 | -60.1044 | -60.4431 | -60.4523 | -0.009155 | 63.9038 | -60.1547 | 64.3524 | -60.1593 | -60.2325 | -60.2325 | -0.091553 | -0.11902 | 0.14191 | 0.009155 | -0.33875 | -0.32959 | -0.24719 | -0.23804 | -0.041199 | -0.10529 | 0.34332 | -0.045777 | -0.11902 | -0.11902 | -0.07782 | -0.07782 | 0.10071 | 124.3561 | -0.004578 | 124.5071 | 124.0952 | 124.0585 | 124.0036 | 124.0173 | -124.2142 | -124.1638 | 124.2645 | 124.4659 | 60.0632 | 60.1044
110.9375 | 124.4476 | -60.1227 | 64.0045 | -0.052455 | 0.0040108 | 0.071323 | 0.057155 | 0.0013714 | -0.0011942 | -0.0029318 | -0.0091433 | 0.0061052 | 0.070883 | 0.031216 | -0.007226 | 0.013393 | 0.0081364 | -0.07782 | 63.8763 | -60.2325 | 64.1922 | -60.054 | -60.3973 | -60.4065 | -0.045776 | 63.913 | -60.173 | 64.1876 | -60.1776 | -60.2509 | -60.1868 | -0.10986 | -0.12817 | 0.18768 | 0.068665 | -0.28381 | -0.27466 | -0.17395 | -0.1648 | -0.050354 | -0.091553 | 0.1831 | -0.054931 | -0.064087 | -0.12817 | -0.013733 | -0.077819 | 0.17853 | 124.4247 | -0.004577 | 124.3607 | 124.1089 | 124.086 | 123.999 | 124.0356 | -124.2371 | -124.1776 | 124.3149 | 124.3103 | 60.0449 | 60.0769
111.9375 | 124.4339 | -60.1135 | 63.9954 | 0.054357 | 0.01042 | 0.067051 | 0.065699 | 0.0099164 | 0.012692 | -0.00079579 | 0.067151 | -0.013121 | 0.068746 | 0.066464 | -0.002953 | -0.0036969 | 0.0038644 | -0.041199 | 63.8855 | -60.173 | 64.1235 | -60.1364 | -60.4568 | -60.4706 | 0.018311 | 63.8992 | -60.1501 | 64.2105 | -60.1593 | -60.2829 | -60.1913 | -0.05951 | -0.10986 | 0.12817 | -0.022889 | -0.35706 | -0.34332 | -0.29755 | -0.28381 | -0.036621 | -0.09613 | 0.21515 | -0.045777 | -0.07782 | -0.16937 | -0.041199 | -0.13275 | 0.036621 | 124.2966 | -0.009156 | 124.3607 | 124.0585 | 124.0494 | 123.999 | 124.0128 | -124.1684 | -124.1455 | 124.2371 | 124.324 | 60.0723 | 60.1318
112.9375 | 124.4385 | -60.1364 | 64.0137 | 0.069615 | 0.00080677 | 0.069187 | 0.068904 | 0.0013714 | -0.0097382 | 0.010953 | 0.051892 | -0.0024398 | 0.065542 | 0.050442 | -0.001885 | -0.012242 | 0.0060004 | -0.018311 | 63.8672 | -60.1868 | 64.1281 | -60.1501 | -60.4523 | -60.4752 | 0.018311 | 63.9038 | -60.1639 | 64.2105 | -60.1593 | -60.2737 | -60.2097 | -0.050354 | -0.14648 | 0.11444 | -0.013732 | -0.33874 | -0.31586 | -0.28839 | -0.2655 | -0.027465 | -0.10986 | 0.19684 | -0.022888 | -0.073242 | -0.13733 | -0.045777 | -0.10986 | 0.036622 | 124.3149 | 0.004577 | 124.3744 | 124.054 | 124.0677 | 124.0036 | 124.0402 | -124.2004 | -124.1776 | 124.2645 | 124.3469 | 60.1181 | 60.1547
113.9375 | 124.4019 | -60.1273 | 64.0228 | 0.084874 | -0.00026223 | 0.065983 | 0.052882 | -0.0018326 | -0.012943 | 0.0077492 | 0.12819 | 0.0029002 | 0.079428 | 0.077145 | 0.002387 | 0.0048481 | 0.0070684 | -0.045776 | 63.8855 | -60.1593 | 64.1418 | -60.0952 | -60.4294 | -60.4385 | -0.022888 | 63.913 | -60.1501 | 64.1647 | -60.1776 | -60.2783 | -60.2463 | -0.032044 | -0.13733 | 0.11902 | 0.032043 | -0.31128 | -0.30212 | -0.27924 | -0.27008 | -0.022888 | -0.10986 | 0.14191 | -0.050354 | -0.11902 | -0.15106 | -0.096131 | -0.12817 | 0.064087 | 124.3011 | -0.027466 | 124.3149 | 124.0448 | 124.0631 | 124.0128 | 124.0402 | -124.1821 | -124.173 | 124.2691 | 124.292 | 60.0815 | 60.1044
114.9531 | 124.4293 | -60.1273 | 64.0274 | 0.13065 | 0.01042 | 0.070255 | 0.061427 | 0.018461 | 0.0041468 | -0.0061368 | 0.31129 | -0.015257 | 0.063406 | 0.071805 | -0.005089 | 0.00057606 | -0.0078856 | -0.027466 | 63.8672 | -60.2097 | 63.9862 | -60.1456 | -60.3058 | -60.4019 | 0.004578 | 63.8947 | -60.1501 | 64.2334 | -60.141 | -60.2783 | -60.173 | -0.082398 | -0.16022 | -0.041199 | -0.018311 | -0.27466 | -0.17853 | -0.19226 | -0.09613 | -0.022888 | -0.13275 | 0.20599 | -0.013733 | -0.045777 | -0.15106 | -0.022889 | -0.12817 | 0.064087 | 124.1959 | 0.009155 | 124.3835 | 124.0768 | 124.0448 | 123.9944 | 124.0219 | -124.2371 | -124.1776 | 124.1135 | 124.3607 | 60.0998 | 60.1318
115.9375 | 124.4522 | -60.0861 | 64.0274 | 0.084874 | -0.0023982 | 0.06171 | 0.061427 | -0.0082416 | -0.0033302 | 0.0013402 | 0.11293 | -0.0013718 | 0.067678 | 0.062192 | 0.012001 | 0.012325 | -0.010022 | -0.041199 | 63.9038 | -60.2005 | 64.1418 | -60.1318 | -60.4477 | -60.4752 | -0.004578 | 63.9038 | -60.1639 | 64.1968 | -60.0266 | -60.1044 | -60.1364 | -0.11444 | -0.1236 | 0.11444 | -0.045776 | -0.3891 | -0.36163 | -0.27466 | -0.24719 | -0.077819 | -0.1236 | 0.16937 | 0.05951 | -0.050354 | -0.01831 | 0.027465 | 0.059509 | 0.068664 | 124.3423 | 0.13733 | 124.3607 | 124.1043 | 124.0677 | 123.9899 | 123.9899 | -124.2279 | -124.1913 | 124.2279 | 124.2828 | 60.0449 | 60.0815
116.9375 | 124.4385 | -60.0998 | 64.0137 | 0.10013 | -0.0023982 | 0.059574 | 0.062495 | -0.0093096 | -0.0022622 | -0.017886 | 0.17396 | -0.0067128 | 0.063406 | 0.066464 | 0.00025105 | 0.0037801 | 0.0038644 | -0.050354 | 63.8535 | -60.1959 | 64.1327 | -60.1273 | -60.4385 | -60.4752 | 0.004578 | 63.9038 | -60.1639 | 64.2151 | -60.141 | -60.2554 | -60.1913 | -0.096131 | -0.16022 | 0.11902 | -0.027466 | -0.37537 | -0.33875 | -0.27924 | -0.24262 | -0.064087 | -0.10986 | 0.20142 | -0.041199 | -0.091553 | -0.15564 | -0.027466 | -0.091553 | 0.068665 | 124.3286 | 0.022888 | 124.379 | 124.0494 | 124.0677 | 123.9532 | 124.0036 | -124.2096 | -124.1776 | 124.2325 | 124.3149 | 60.0494 | 60.1044
117.9375 | 124.4156 | -60.1089 | 64.0137 | -0.0066789 | 0.0029428 | 0.05637 | 0.064631 | 0.0035084 | 0.0094878 | 0.010953 | 0.08241 | -0.0024398 | 0.063406 | 0.040829 | -0.001885 | -0.0069009 | -0.0057486 | -0.036621 | 63.8626 | -60.1822 | 64.1418 | -60.1227 | -60.434 | -60.4477 | 0 | 63.9175 | -60.1639 | 64.183 | -60.2005 | -60.2921 | -60.228 | -0.073242 | -0.15106 | 0.12817 | -0.013733 | -0.33875 | -0.32501 | -0.2655 | -0.25177 | -0.054931 | -0.09613 | 0.16937 | -0.091552 | -0.11902 | -0.18311 | -0.064087 | -0.12817 | 0.059509 | 124.324 | -0.036621 | 124.3469 | 124.0448 | 124.0814 | 123.9716 | 124.0265 | -124.1959 | -124.1776 | 124.2508 | 124.292 | 60.0723 | 60.1089
118.9375 | 124.4339 | -60.1318 | 64.0137 | 0.10013 | 0.01042 | 0.067051 | 0.061427 | -0.0050366 | 0.015896 | 0.01843 | 0.08241 | -0.0099168 | 0.084768 | 0.077145 | -0.00081695 | -0.0036969 | -0.014294 | -0.050354 | 63.8763 | -60.173 | 64.1464 | -60.1135 | -60.4248 | -60.4477 | -0.009155 | 63.9084 | -60.173 | 64.1922 | -60.1776 | -60.2875 | -60.2188 | -0.041199 | -0.13733 | 0.13275 | 0.018311 | -0.31586 | -0.29297 | -0.27466 | -0.25177 | -0.041199 | -0.10529 | 0.17853 | -0.045776 | -0.086975 | -0.15564 | -0.045776 | -0.11444 | 0.05951 | 124.3195 | -0.004577 | 124.3652 | 124.0494 | 124.0814 | 124.0082 | 124.0402 | -124.1867 | -124.1867 | 124.2783 | 124.324 | 60.0815 | 60.1227
119.9375 | 124.4522 | -60.0952 | 64.032 | 0.039098 | 0.0029428 | 0.057438 | 0.07104 | -0.00076463 | -0.0076022 | 0.0045452 | 0.0061157 | -0.0056438 | 0.078359 | 0.072873 | -0.016839 | 0.0048481 | -0.015362 | -0.041199 | 63.8626 | -60.1913 | 64.1602 | -60.1456 | -60.4614 | -60.4568 | -0.004578 | 63.9175 | -60.1639 | 64.1464 | -59.9991 | -60.0906 | -60.1044 | -0.09613 | -0.16937 | 0.12817 | -0.050354 | -0.36163 | -0.36621 | -0.2655 | -0.27008 | -0.068664 | -0.11444 | 0.11444 | 0.096131 | -0.009155 | 0.004578 | 0.059509 | 0.073242 | 0.045776 | 124.3515 | 0.16479 | 124.3103 | 124.054 | 124.0814 | 123.9578 | 124.0128 | -124.2233 | -124.1959 | 124.2554 | 124.2416 | 60.054 | 60.0906
120.9375 | 124.4019 | -60.1273 | 64.0228 | 0.069615 | 0.0050788 | 0.065983 | 0.064631 | 0.018461 | -0.0033302 | 0.016294 | 0.1587 | -0.0045758 | 0.070883 | 0.042966 | -0.005089 | -0.0026279 | -0.0014766 | -0.045776 | 63.8809 | -60.1822 | 64.151 | -60.1044 | -60.4248 | -60.4523 | -0.009155 | 63.913 | -60.173 | 64.1968 | -60.1913 | -60.2783 | -60.2188 | -0.054932 | -0.14191 | 0.12817 | 0.022888 | -0.32501 | -0.29755 | -0.27008 | -0.24262 | -0.045777 | -0.10986 | 0.17395 | -0.064087 | -0.091553 | -0.15106 | -0.045776 | -0.10529 | 0.07782 | 124.3332 | -0.01831 | 124.3698 | 124.0631 | 124.086 | 124.0082 | 124.0402 | -124.205 | -124.1959 | 124.2783 | 124.324 | 60.0815 | 60.1181
121.9375 | 124.411 | -60.1044 | 64.0594 | 0.069615 | -0.0098752 | 0.068119 | 0.050746 | 0.0024404 | -0.0011942 | -0.011477 | 0.26551 | -0.0024398 | 0.076223 | 0.076077 | -0.009362 | 0.00057606 | -0.012158 | -0.018311 | 63.8901 | -60.1868 | 64.1693 | -60.0677 | -60.3882 | -60.4111 | 0.009155 | 63.945 | -60.1456 | 64.2014 | -60.1501 | -60.2417 | -60.1959 | -0.082398 | -0.16937 | 0.10986 | 0.036621 | -0.3067 | -0.28381 | -0.2243 | -0.20142 | -0.041199 | -0.11444 | 0.14191 | -0.045776 | -0.091553 | -0.13733 | -0.050354 | -0.09613 | 0.11902 | 124.3561 | -0.004577 | 124.3469 | 124.0768 | 124.0906 | 123.9944 | 124.0494 | -124.2462 | -124.205 | 124.2737 | 124.3057 | 60.0861 | 60.1135
122.9375 | 124.4247 | -60.1318 | 64.032 | 0.023839 | 0.0040108 | 0.05637 | 0.058223 | -0.0018326 | 0.0062828 | -0.0018638 | 0.14344 | -0.0077808 | 0.069815 | 0.056851 | 0.00025105 | 0.00057606 | 0.0006594 | -0.041199 | 63.8535 | -60.1776 | 64.1464 | -60.1044 | -60.4202 | -60.4477 | -0.013733 | 63.913 | -60.1593 | 64.1739 | -60.1913 | -60.2875 | -60.2188 | -0.045776 | -0.17853 | 0.11444 | 0.027466 | -0.31586 | -0.28839 | -0.27008 | -0.24261 | -0.027466 | -0.11902 | 0.14191 | -0.059509 | -0.086975 | -0.15564 | -0.059509 | -0.12817 | 0.073242 | 124.324 | -0.032043 | 124.3332 | 124.0311 | 124.0723 | 123.9853 | 124.0448 | -124.2096 | -124.1913 | 124.2783 | 124.3057 | 60.0906 | 60.1181
123.9375 | 124.3927 | -60.1273 | 64.0457 | 0.0085801 | 0.0093518 | 0.063847 | 0.062495 | -0.010378 | -0.022556 | 0.00027221 | 0.067151 | 0.0050372 | 0.043112 | 0.0686 | 0.00025105 | -0.00049194 | -0.0046806 | -0.041199 | 63.8809 | -60.1868 | 64.151 | -60.1227 | -60.4294 | -60.4385 | -0.004578 | 63.913 | -60.1822 | 64.1647 | -60.1868 | -60.2921 | -60.2325 | -0.05951 | -0.16479 | 0.10529 | 0.004577 | -0.31128 | -0.30212 | -0.25177 | -0.24261 | -0.054932 | -0.13275 | 0.11902 | -0.05951 | -0.10529 | -0.1648 | -0.050354 | -0.10986 | 0.064087 | 124.3378 | -0.004578 | 124.3469 | 124.0677 | 124.0952 | 124.0082 | 124.0402 | -124.2325 | -124.2279 | 124.2783 | 124.292 | 60.0861 | 60.1227
124.9375 | 124.2874 | -60.1456 | 64.064 | 0.11539 | -0.0056022 | 0.068119 | 0.065699 | 0.0088484 | 0.014828 | 0.0056132 | -0.20751 | 0.0018322 | 0.06661 | 0.08569 | -0.002953 | -0.0069009 | -0.0046806 | -0.027466 | 63.9267 | -60.2097 | 64.2563 | -60.0128 | -60.3378 | -60.3149 | -0.059509 | 63.9725 | -60.1639 | 64.1373 | -60.2646 | -60.3973 | -60.2921 | -0.064087 | -0.13733 | 0.19226 | 0.13275 | -0.16937 | -0.19226 | -0.10528 | -0.12817 | -0.01831 | -0.091553 | 0.073242 | -0.11902 | -0.14648 | -0.25177 | -0.12817 | -0.23346 | 0.19684 | 124.4659 | -0.10071 | 124.3011 | 124.1364 | 124.1364 | 124.0723 | 124.118 | -124.2737 | -124.2279 | 124.4019 | 124.2828 | 60.1181 | 60.0861
125.9375 | 124.4064 | -60.1227 | 64.0182 | 0.20695 | -0.0023982 | 0.055302 | 0.056086 | 0.0045764 | -0.015079 | 0.0056132 | 0.20448 | -0.00030381 | 0.053793 | 0.039761 | 0.003456 | 0.0091211 | -0.0014766 | -0.018311 | 63.9038 | -60.1776 | 64.1602 | -60.0677 | -60.3973 | -60.4156 | -0.009155 | 63.9496 | -60.1593 | 64.1922 | -60.1456 | -60.2463 | -60.1913 | -0.054931 | -0.11444 | 0.14191 | 0.054932 | -0.29297 | -0.27466 | -0.23804 | -0.21973 | -0.036621 | -0.068665 | 0.17395 | -0.022888 | -0.068664 | -0.1236 | -0.032043 | -0.086975 | 0.10986 | 124.3378 | 0.013733 | 124.3515 | 124.0814 | 124.1089 | 124.0265 | 124.0723 | -124.1959 | -124.1776 | 124.2828 | 124.3149 | 60.1044 | 60.1135
126.9375 | 124.4522 | -60.1044 | 64.0366 | 0.11539 | 0.011488 | 0.058506 | 0.061427 | 0.00030337 | -0.0011942 | -0.0061368 | 0.21974 | 0.0039692 | 0.065542 | 0.061124 | 0.007728 | -0.0036969 | -0.0046806 | 0.018311 | 63.8809 | -60.173 | 64.1556 | -60.1181 | -60.4385 | -60.4248 | 0.07782 | 63.9359 | -60.1501 | 64.2609 | -60.0586 | -60.1639 | -60.1822 | -0.068665 | -0.15564 | 0.11902 | -0.013733 | -0.32043 | -0.33417 | -0.25177 | -0.2655 | -0.045776 | -0.10071 | 0.2243 | 0.045776 | -0.07782 | -0.059509 | -0.032044 | -0.013733 | 0.054932 | 124.3286 | 0.091552 | 124.411 | 124.054 | 124.086 | 123.9853 | 124.0402 | -124.2096 | -124.1867 | 124.2599 | 124.3652 | 60.1227 | 60.1822
127.9375 | 124.379 | -60.1135 | 64.0137 | 0.023839 | 0.0029428 | 0.062778 | 0.062495 | 0.013121 | 0.012692 | -0.0061368 | 0.17396 | 0.0018322 | 0.069815 | 0.06326 | -0.002953 | 0.0069851 | 0.0027964 | -0.041199 | 63.8855 | -60.2051 | 64.1281 | -60.1227 | -60.4294 | -60.4614 | 0.004578 | 63.8855 | -60.1501 | 64.1968 | -60.1685 | -60.2783 | -60.2234 | -0.091553 | -0.12817 | 0.11444 | -0.009156 | -0.3479 | -0.31586 | -0.25635 | -0.2243 | -0.036621 | -0.12817 | 0.1831 | -0.054932 | -0.10986 | -0.16479 | -0.073243 | -0.12817 | 0.082397 | 124.3332 | -0.018311 | 124.3469 | 124.0906 | 124.0356 | 123.999 | 123.999 | -124.2188 | -124.1638 | 124.2416 | 124.3103 | 60.0723 | 60.1181
128.9375 | 124.3652 | -60.1273 | 64.032 | 0.17643 | 0.0050788 | 0.067051 | 0.055018 | -0.0082416 | -0.0043982 | -0.0029318 | 0.14344 | -0.0067128 | 0.078359 | 0.024808 | -0.00081695 | -0.014378 | -0.024975 | -0.054932 | 63.858 | -60.1913 | 64.1876 | -60.0586 | -60.3928 | -60.4065 | -0.032043 | 63.9359 | -60.1639 | 64.2654 | -60.2509 | -60.2829 | -60.2325 | -0.064087 | -0.17395 | 0.15564 | 0.068664 | -0.27924 | -0.2655 | -0.21515 | -0.20142 | -0.036621 | -0.09613 | 0.23346 | -0.1236 | -0.10529 | -0.15564 | -0.068665 | -0.11902 | 0.13275 | 124.379 | -0.086975 | 124.4293 | 124.0494 | 124.0997 | 123.9853 | 124.0631 | -124.2233 | -124.1959 | 124.3149 | 124.3927 | 60.0723 | 60.0952
129.9375 | 124.4247 | -60.0861 | 64.0549 | 0.11539 | -0.00026223 | 0.063847 | 0.074244 | -0.0061046 | 0.0041468 | -0.011477 | 0.097669 | -0.0035078 | 0.059133 | 0.070737 | -0.00081695 | 0.0080531 | 0.0027964 | 0.091553 | 63.9221 | -60.1639 | 64.1602 | -60.1044 | -60.4202 | -60.4065 | 0.11444 | 63.9633 | -60.1273 | 64.2197 | -60.1044 | -60.2097 | -60.1685 | -0.077819 | -0.13275 | 0.10528 | -0.01831 | -0.32043 | -0.33417 | -0.24262 | -0.25635 | -0.041198 | -0.091553 | 0.16479 | -0.01831 | -0.082397 | -0.1236 | -0.041199 | -0.082398 | 0.059509 | 124.324 | 0.022888 | 124.3469 | 124.086 | 124.0906 | 124.0082 | 124.0494 | -124.2188 | -124.1821 | 124.2462 | 124.3057 | 60.1776 | 60.2005
130.9375 | 124.4202 | -60.1273 | 64.0411 | 0.0085801 | 0.0029428 | 0.057438 | 0.065699 | 0.020598 | 0.020169 | -0.0018638 | 0.14344 | -0.0056438 | 0.04952 | 0.10171 | 0.003456 | 0.0069851 | 0.0060004 | -0.059509 | 63.8992 | -60.2051 | 64.1968 | -60.0311 | -60.3745 | -60.4111 | -0.022888 | 63.9313 | -60.141 | 64.2105 | -60.1501 | -60.2509 | -60.2051 | -0.07782 | -0.14191 | 0.15564 | 0.09613 | -0.28381 | -0.24719 | -0.20599 | -0.16937 | -0.013733 | -0.10986 | 0.16937 | -0.022888 | -0.07782 | -0.1236 | -0.064087 | -0.10986 | 0.17395 | 124.4019 | -0.009155 | 124.3515 | 124.1043 | 124.0723 | 124.0265 | 124.0585 | -124.2462 | -124.1821 | 124.324 | 124.3378 | 60.0677 | 60.1044
131.9375 | 124.4019 | -60.1135 | 64.0091 | -0.0066789 | 0.0072148 | 0.064915 | 0.067836 | -0.0029006 | 0.0084198 | -0.0018638 | 0.097669 | -0.0045758 | 0.058065 | 0.069668 | -0.004021 | 0.0069851 | -0.016431 | -0.027466 | 63.8855 | -60.1776 | 64.1235 | -60.1181 | -60.4477 | -60.4523 | 0.018311 | 63.913 | -60.1639 | 64.2014 | -60.1639 | -60.2692 | -60.2097 | -0.064087 | -0.1236 | 0.11444 | -0.004578 | -0.33875 | -0.33417 | -0.27466 | -0.27008 | -0.050354 | -0.09613 | 0.19226 | -0.050354 | -0.096131 | -0.15564 | -0.045777 | -0.10529 | 0.059509 | 124.3011 | 0 | 124.3652 | 124.0631 | 124.0768 | 123.999 | 124.0265 | -124.1867 | -124.173 | 124.2371 | 124.3149 | 60.0861 | 60.1318
132.9375 | 124.3835 | -60.1364 | 64.0274 | 0.023839 | 0.0072148 | 0.059574 | 0.063563 | -0.00076463 | 0.026577 | -0.01575 | 0.021375 | -0.00030381 | 0.06127 | 0.041897 | -0.008294 | 0.0048481 | 0.0006594 | -0.032043 | 63.8535 | -60.173 | 64.1235 | -60.1181 | -60.4477 | -60.466 | 0.013733 | 63.913 | -60.1318 | 64.2014 | -60.1776 | -60.2646 | -60.2097 | -0.036621 | -0.17395 | 0.09613 | 0.018311 | -0.32959 | -0.31128 | -0.29297 | -0.27466 | 0.004578 | -0.11444 | 0.17395 | -0.041198 | -0.073242 | -0.12817 | -0.07782 | -0.13275 | 0.054932 | 124.2966 | -0.045776 | 124.3332 | 124.0265 | 124.0448 | 123.9899 | 124.0494 | -124.2004 | -124.1592 | 124.2599 | 124.3378 | 60.1044 | 60.1501
133.9375 | 124.4064 | -60.1273 | 64.0228 | 0.11539 | -0.0013302 | 0.059574 | 0.060359 | -0.010378 | 0.0020108 | 0.00027221 | 0.097669 | -0.0035078 | 0.055929 | 0.069668 | -0.00081695 | -0.0047649 | -0.0036126 | 0.068665 | 63.9175 | -60.1776 | 64.2197 | -60.054 | -60.3973 | -60.4294 | -0.059509 | 63.9175 | -60.1501 | 64.1922 | -60.173 | -60.2692 | -60.2234 | -0.050354 | -0.10529 | 0.19684 | 0.073242 | -0.30212 | -0.27008 | -0.25177 | -0.21973 | -0.022888 | -0.10529 | 0.16937 | -0.045777 | -0.096131 | -0.14191 | -0.073243 | -0.11902 | 0.1236 | 124.3973 | -0.022889 | 124.3423 | 124.0952 | 124.0677 | 124.0448 | 124.0448 | -124.2004 | -124.173 | 124.3469 | 124.3195 | 60.1959 | 60.0677
134.9375 | 124.4751 | -60.0723 | 64.0411 | 0.13065 | 0.0050788 | 0.055302 | 0.065699 | -0.013582 | 0.0062828 | -0.020022 | 0.21974 | 0.0082412 | 0.071951 | 0.083554 | -0.005089 | 0.00057606 | -0.01109 | 0.045776 | 63.8992 | -60.1776 | 64.1418 | -60.1273 | -60.4431 | -60.4202 | 0.12817 | 63.9313 | -60.1273 | 64.2654 | -60.0632 | -60.1822 | -60.141 | -0.10529 | -0.14191 | 0.10071 | -0.054931 | -0.3479 | -0.37079 | -0.24261 | -0.2655 | -0.054931 | -0.10986 | 0.2243 | 0.009156 | -0.068664 | -0.10986 | -0.013733 | -0.054932 | 0.050354 | 124.3195 | 0.064087 | 124.3927 | 124.0768 | 124.0585 | 123.9716 | 124.0036 | -124.2188 | -124.1684 | 124.2142 | 124.3378 | 60.1181 | 60.2005
135.9375 | 124.3973 | -60.141 | 64.0228 | 0.13065 | 0.0050788 | 0.063847 | 0.069972 | 0.0067124 | -0.0022622 | 0.0013402 | 0.0061157 | 0.0029002 | 0.052725 | 0.052579 | -0.006157 | 0.0069851 | 0.0060004 | -0.027466 | 63.9038 | -60.1913 | 64.2014 | -60.0494 | -60.3195 | -60.434 | 0 | 63.9404 | -60.141 | 64.1556 | -60.1913 | -60.2829 | -60.2142 | -0.050354 | -0.11902 | 0.17853 | 0.091553 | -0.29297 | -0.17853 | -0.24262 | -0.12817 | 0 | -0.082397 | 0.13275 | -0.050354 | -0.073242 | -0.14191 | -0.073242 | -0.14191 | 0.14191 | 124.3927 | -0.050354 | 124.2966 | 124.0952 | 124.0814 | 124.0448 | 124.0814 | -124.2142 | -124.1638 | 124.3423 | 124.2966 | 60.1135 | 60.141
136.9375 | 124.4019 | -60.0952 | 64.0228 | 0.039098 | 0.0029428 | 0.05637 | 0.073176 | -0.0050366 | -0.0033302 | 0.0024082 | 0.036633 | -0.0013718 | 0.077291 | 0.081418 | 0.001319 | 0.010189 | -0.0068176 | -0.032043 | 63.8763 | -60.2097 | 64.1327 | -60.1181 | -60.4111 | -60.4477 | 0.004578 | 63.9267 | -60.1685 | 64.1739 | -60.1776 | -60.2783 | -60.228 | -0.11444 | -0.14648 | 0.10986 | -0.022888 | -0.35248 | -0.31586 | -0.23804 | -0.20142 | -0.073242 | -0.09613 | 0.15106 | -0.082397 | -0.13275 | -0.1831 | -0.059509 | -0.10986 | 0.091553 | 124.3423 | -0.009155 | 124.3423 | 124.086 | 124.0952 | 123.9716 | 124.0219 | -124.2325 | -124.1913 | 124.2279 | 124.2691 | 60.0632 | 60.0998
137.9375 | 124.3881 | -60.1273 | 64.0549 | 0.054357 | 0.0029428 | 0.063847 | 0.061427 | -0.0061046 | 0.021237 | 0.013089 | 0.021375 | 0.0061052 | 0.06127 | 0.034421 | -0.005089 | 0.0037801 | -0.012158 | -0.032043 | 63.8809 | -60.1959 | 64.1739 | -60.0586 | -60.3973 | -60.4019 | -0.041199 | 63.9267 | -60.1868 | 64.2426 | -60.1913 | -60.3287 | -60.2234 | -0.068665 | -0.17395 | 0.11902 | 0.068664 | -0.27466 | -0.27008 | -0.20599 | -0.20142 | -0.05951 | -0.12817 | 0.18768 | -0.064087 | -0.096131 | -0.20142 | -0.036621 | -0.14191 | 0.13733 | 124.3698 | -0.004577 | 124.4293 | 124.0768 | 124.1135 | 124.0082 | 124.054 | -124.2508 | -124.2416 | 124.3011 | 124.3698 | 60.0952 | 60.0861
138.9375 | 124.379 | -60.0998 | 64.0457 | 0.054357 | 0.013624 | 0.059574 | 0.066768 | 0.0099164 | -0.0054662 | 0.017362 | 0.097669 | -0.0024398 | 0.077291 | 0.058987 | -0.009362 | 0.00057606 | -0.0014766 | -0.064087 | 63.8763 | -60.1868 | 64.183 | -60.0494 | -60.3882 | -60.4156 | -0.045776 | 63.9359 | -60.1593 | 64.183 | -60.1868 | -60.054 | -60.0998 | -0.086976 | -0.16937 | 0.13733 | 0.050354 | -0.31586 | -0.28839 | -0.22888 | -0.20142 | -0.05951 | -0.10986 | 0.13733 | -0.086976 | 0 | 0.045776 | 0.05951 | 0.10529 | 0.13733 | 124.3698 | -0.027466 | 124.3423 | 124.0631 | 124.0952 | 123.9761 | 124.0356 | -124.2325 | -124.205 | 124.2828 | 124.2828 | 60.0357 | 60.054
139.9375 | 124.4247 | -60.1181 | 64.0137 | 0.023839 | -0.0013302 | 0.062778 | 0.061427 | 0.0099164 | -0.0076022 | -0.00079579 | 0.20448 | 0.0039692 | 0.063406 | 0.037625 | 0.00025105 | -0.0015599 | 0.0027964 | -0.086975 | 63.8855 | -60.1868 | 64.1602 | -60.0494 | -60.4065 | -60.4019 | -0.004578 | 63.9313 | -60.1501 | 64.1876 | -60.1639 | -60.2737 | -60.2097 | -0.068665 | -0.12817 | 0.14648 | 0.068665 | -0.28381 | -0.28839 | -0.21515 | -0.21973 | -0.032043 | -0.082398 | 0.17395 | -0.045776 | -0.091553 | -0.15564 | -0.05951 | -0.1236 | 0.13733 | 124.3469 | -0.013733 | 124.3378 | 124.0723 | 124.0814 | 124.0036 | 124.0494 | -124.2004 | -124.1638 | 124.2783 | 124.3057 | 60.0311 | 60.1135
140.9375 | 124.3835 | -60.1181 | 64.0228 | 0.16117 | 0.0050788 | 0.059574 | 0.058223 | -0.011446 | 0.012692 | 0.0088172 | -0.024402 | -0.010985 | 0.056997 | 0.034421 | -0.009362 | 0.0069851 | 0.0038644 | -0.064087 | 63.8901 | -60.1593 | 64.1693 | -60.0677 | -60.4019 | -60.4156 | -0.041199 | 63.945 | -60.173 | 64.1876 | -60.1639 | -60.2646 | -60.2188 | -0.041199 | -0.13275 | 0.14648 | 0.050354 | -0.29755 | -0.28381 | -0.25635 | -0.24262 | -0.054932 | -0.07782 | 0.16479 | -0.045776 | -0.10071 | -0.14648 | -0.045776 | -0.091552 | 0.091553 | 124.3286 | 0.009156 | 124.3607 | 124.0494 | 124.118 | 124.0082 | 124.0631 | -124.1821 | -124.1959 | 124.2874 | 124.3057 | 60.054 | 60.0769
141.9375 | 124.4019 | -60.141 | 64.0274 | 0.069615 | -0.0034662 | 0.053165 | 0.059291 | -0.010378 | -0.023624 | 0.0024082 | -0.03966 | 0.0029002 | 0.063406 | 0.050442 | -0.004021 | 0.0016441 | -0.013226 | -0.032043 | 63.8809 | -60.1822 | 64.1876 | -60.054 | -60.4202 | -60.3378 | -0.045776 | 63.9404 | -60.1639 | 64.1327 | -60.2051 | -60.3104 | -60.2463 | -0.041199 | -0.14648 | 0.16022 | 0.086975 | -0.19684 | -0.27924 | -0.15564 | -0.23804 | -0.022888 | -0.086975 | 0.10528 | -0.064087 | -0.10529 | -0.16937 | -0.082398 | -0.14648 | 0.12817 | 124.3698 | -0.041199 | 124.2966 | 124.0631 | 124.1043 | 124.0219 | 124.0814 | -124.2096 | -124.1913 | 124.3286 | 124.2737 | 60.1089 | 60.0952
142.9375 | 124.4064 | -60.1227 | 64.0411 | 0.16117 | -0.0066702 | 0.065983 | 0.060359 | 0.015257 | 0.015896 | 0.016294 | 0.17396 | 0.0061052 | 0.04952 | 0.066464 | -0.004021 | 0.0080531 | -0.0036126 | -0.018311 | 63.8947 | -60.2097 | 64.1876 | -60.0494 | -60.4019 | -60.3973 | -0.004578 | 63.9359 | -60.1501 | 64.2059 | -60.1456 | -60.2463 | -60.2188 | -0.086975 | -0.14649 | 0.14648 | 0.073243 | -0.27466 | -0.27924 | -0.18768 | -0.19226 | -0.027465 | -0.10529 | 0.16479 | -0.022888 | -0.09613 | -0.1236 | -0.068665 | -0.096131 | 0.16022 | 124.3973 | 0.004577 | 124.3561 | 124.1043 | 124.086 | 124.0173 | 124.0585 | -124.2508 | -124.1913 | 124.3103 | 124.3286 | 60.1044 | 60.1181
143.9844 | 124.2691 | -60.1639 | 64.0411 | 0.023839 | -0.0013302 | 0.064915 | 0.066768 | 0.0013714 | 0.011624 | -0.013613 | -0.17699 | 0.0061052 | 0.077291 | 0.054715 | -0.008294 | 0.0048481 | -0.0004086 | -0.091553 | 63.913 | -60.2325 | 64.2471 | -60.2005 | -60.5255 | -60.1181 | -0.21057 | 63.9771 | -60.1959 | 64.1098 | -60.2829 | -60.3882 | -60.3104 | -0.068665 | -0.12817 | 0.20599 | -0.036621 | 0.045776 | -0.36163 | 0.11444 | -0.29297 | -0.032044 | -0.064087 | 0.068664 | -0.11902 | -0.14648 | -0.22431 | -0.11444 | -0.19226 | 0.032044 | 124.4797 | -0.086975 | 124.3057 | 124.1455 | 124.173 | 124.0768 | 124.1409 | -124.2737 | -124.2371 | 124.411 | 124.2737 | 60.0723 | 59.9533
144.9375 | 124.4247 | -60.0815 | 64.0594 | 0.069615 | 0.0018748 | 0.063847 | 0.056086 | 0.018461 | 0.014828 | -0.013613 | 0.14344 | -0.0056438 | 0.056997 | 0.02374 | 0.00025105 | -0.0036969 | -0.010022 | 0.11444 | 63.8947 | -60.1456 | 64.1556 | -60.1227 | -60.434 | -60.434 | 0.10529 | 63.9496 | -60.1364 | 64.2426 | -60.0861 | -60.1959 | -60.173 | -0.064087 | -0.1648 | 0.096131 | -0.041199 | -0.35248 | -0.35248 | -0.28839 | -0.28839 | -0.054932 | -0.10986 | 0.18311 | -0.004578 | -0.091553 | -0.11444 | -0.036621 | -0.059509 | 0.022888 | 124.3011 | 0.050354 | 124.379 | 124.0402 | 124.086 | 123.9761 | 124.0311 | -124.205 | -124.1959 | 124.2371 | 124.324 | 60.1959 | 60.1868
145.9688 | 124.3973 | -60.1273 | 64.0228 | -0.0066789 | 0.0061468 | 0.075596 | 0.061427 | 0.014189 | -0.010807 | -0.018954 | 0.08241 | -0.00030381 | 0.070883 | 0.066464 | -0.00081695 | 0.010189 | 0.010272 | -0.013733 | 63.8443 | -60.1868 | 64.1098 | -60.1273 | -60.4431 | -60.466 | 0.032043 | 63.8992 | -60.1593 | 64.2059 | -60.1364 | -60.2509 | -60.1868 | -0.05951 | -0.17853 | 0.086975 | 0 | -0.33875 | -0.31586 | -0.27923 | -0.25635 | -0.032044 | -0.1236 | 0.18311 | -0.009156 | -0.05951 | -0.1236 | -0.027466 | -0.091552 | 0.05951 | 124.2966 | 0.022888 | 124.3652 | 124.0311 | 124.0585 | 123.9716 | 124.0265 | -124.2096 | -124.1821 | 124.2371 | 124.3332 | 60.1135 | 60.1593
146.9375 | 124.3973 | -60.1044 | 64.0228 | 0.13065 | 0.0082828 | 0.074528 | 0.068904 | -0.0071726 | -0.0054662 | 0.0045452 | -0.085437 | -0.0067128 | 0.062338 | 0.052579 | 0.00025105 | -0.0036969 | 0.0017274 | -0.032043 | 63.8397 | -60.1776 | 64.1373 | -60.1181 | -60.4294 | -60.4523 | 0.004578 | 63.9038 | -60.1639 | 64.183 | -60.1639 | -60.2783 | -60.2097 | -0.073242 | -0.18311 | 0.11444 | -0.013733 | -0.3479 | -0.32501 | -0.27466 | -0.25177 | -0.059509 | -0.11902 | 0.16022 | -0.059509 | -0.10529 | -0.17395 | -0.045777 | -0.11444 | 0.059509 | 124.3149 | 0 | 124.3469 | 124.0173 | 124.0677 | 123.9441 | 124.0082 | -124.2004 | -124.1867 | 124.2416 | 124.2874 | 60.0723 | 60.1089
147.9375 | 124.4064 | -60.1273 | 64.0091 | 0.054357 | 0.0040108 | 0.072392 | 0.059291 | 0.012053 | -0.0065342 | 0.0088172 | 0.051892 | 0.0082412 | 0.070883 | 0.067532 | 0.014137 | 0.0091211 | 0.0049324 | -0.045776 | 63.8626 | -60.1868 | 64.1006 | -60.1318 | -60.4477 | -60.4706 | 0.018311 | 63.8763 | -60.1593 | 64.2151 | -60.1685 | -60.2646 | -60.1913 | -0.05951 | -0.14648 | 0.091553 | -0.004578 | -0.34332 | -0.32044 | -0.28381 | -0.26093 | -0.032044 | -0.13275 | 0.20599 | -0.041199 | -0.064087 | -0.13733 | -0.032043 | -0.10529 | 0.054932 | 124.2874 | -0.009155 | 124.3744 | 124.0494 | 124.0356 | 123.9899 | 124.0036 | -124.1959 | -124.1684 | 124.2279 | 124.3423 | 60.0815 | 60.1456
148.9375 | 124.4522 | -60.0906 | 63.9862 | -0.067714 | 0.0018748 | 0.065983 | 0.064631 | -0.00076463 | -0.0043982 | -0.0029318 | 0.08241 | 0.00076419 | 0.074087 | 0.064328 | -0.001885 | 0.0069851 | -0.0014766 | -0.009155 | 63.8763 | -60.1822 | 64.1144 | -60.1227 | -60.4477 | -60.4706 | 0.022888 | 63.9084 | -60.1364 | 64.238 | -60.141 | -60.2692 | -60.2005 | -0.091553 | -0.10986 | 0.12817 | -0.032044 | -0.37994 | -0.35706 | -0.28839 | -0.2655 | -0.045777 | -0.07782 | 0.25177 | -0.050354 | -0.10986 | -0.17853 | -0.064086 | -0.13275 | 0.059509 | 124.2966 | -0.004577 | 124.3744 | 124.0585 | 124.0448 | 123.967 | 123.999 | -124.1684 | -124.1226 | 124.205 | 124.3286 | 60.0815 | 60.1135
149.9375 | 124.4064 | -60.141 | 64.0228 | 0.0085801 | 0.014692 | 0.064915 | 0.062495 | -0.0050366 | -0.030033 | 0.0066812 | 0.28077 | 0.0029002 | 0.059133 | 0.11773 | 0.008796 | 0.0059161 | -0.0004086 | -0.027466 | 63.8992 | -60.1868 | 64.1693 | -60.054 | -60.3928 | -60.4202 | -0.009155 | 63.945 | -60.1639 | 64.2014 | -60.1456 | -60.2463 | -60.1959 | -0.045777 | -0.1236 | 0.14648 | 0.086975 | -0.27924 | -0.25177 | -0.23346 | -0.20599 | -0.022888 | -0.07782 | 0.17853 | -0.004578 | -0.054932 | -0.10529 | -0.032044 | -0.082398 | 0.13275 | 124.3561 | 0.01831 | 124.3652 | 124.086 | 124.1089 | 124.0402 | 124.086 | -124.2096 | -124.1867 | 124.3103 | 124.3423 | 60.1135 | 60.1318
150.9375 | 124.4064 | -60.1135 | 63.9999 | 0.039098 | 0.013624 | 0.060642 | 0.062495 | -0.0029006 | -0.010807 | -0.0082728 | 0.11293 | -0.0013718 | 0.062338 | 0.015195 | -0.009362 | 0.0048481 | -0.01109 | -0.059509 | 63.8718 | -60.2051 | 64.1739 | -60.0586 | -60.3973 | -60.4202 | -0.041199 | 63.9221 | -60.1639 | 64.1693 | -60.173 | -60.2737 | -60.228 | -0.091553 | -0.12817 | 0.17395 | 0.054931 | -0.3067 | -0.28381 | -0.21515 | -0.19226 | -0.050354 | -0.07782 | 0.16937 | -0.05951 | -0.11444 | -0.16022 | -0.064087 | -0.10986 | 0.14648 | 124.379 | -0.009156 | 124.3332 | 124.0768 | 124.086 | 123.9853 | 124.0356 | -124.205 | -124.1638 | 124.2874 | 124.2828 | 60.054 | 60.0723
151.9375 | 124.292 | -60.1273 | 64.0732 | -0.052455 | -0.00026223 | 0.068119 | 0.073176 | 0.010984 | 0.0073508 | 0.015226 | -0.13121 | 0.00076419 | 0.060202 | 0.087826 | -0.004021 | -0.0015599 | 0.013477 | -0.022888 | 63.9084 | -60.2051 | 64.2654 | -59.9716 | -60.3104 | -60.3241 | -0.086975 | 63.9679 | -60.1639 | 64.1235 | -60.2692 | -60.3882 | -60.3012 | -0.07782 | -0.1648 | 0.19226 | 0.15564 | -0.19684 | -0.18311 | -0.11902 | -0.10529 | -0.036621 | -0.10529 | 0.050354 | -0.14191 | -0.17395 | -0.26093 | -0.13733 | -0.22431 | 0.23346 | 124.4705 | -0.10529 | 124.2874 | 124.1135 | 124.1318 | 124.0356 | 124.0952 | -124.2783 | -124.2371 | 124.3927 | 124.2508 | 60.1044 | 60.0403
152.9375 | 124.498 | -60.1227 | 64.0045 | 0.039098 | 0.01042 | 0.057438 | 0.058223 | 0.0056444 | 0.0084198 | -0.013613 | -0.070178 | -0.0035078 | 0.071951 | 0.092099 | -0.005089 | 0.012325 | -0.0036126 | -0.036621 | 63.8718 | -60.228 | 64.1373 | -60.1227 | -60.4523 | -60.4568 | -0.004578 | 63.9038 | -60.1639 | 64.2242 | -60.1135 | -60.5072 | -60.3333 | -0.10529 | -0.13275 | 0.13275 | 0 | -0.33417 | -0.32959 | -0.22888 | -0.22431 | -0.041198 | -0.10071 | 0.21973 | 0.009156 | -0.21057 | -0.38452 | -0.16937 | -0.34332 | 0.10529 | 124.3652 | 0.050354 | 124.3881 | 124.0997 | 124.0677 | 123.9944 | 124.0265 | -124.2325 | -124.1684 | 124.2599 | 124.3469 | 60.0861 | 60.1181
153.9375 | 124.4156 | -60.1181 | 63.9862 | 0.10013 | -0.0023982 | 0.063847 | 0.076381 | -0.015718 | 0.0094878 | -0.0050688 | -0.054919 | -0.0024398 | 0.077291 | 0.0686 | 0.00666 | 0.00057606 | -0.0036126 | -0.091553 | 63.9084 | -60.2142 | 64.1602 | -60.0769 | -60.4111 | -60.4248 | -0.013733 | 63.9267 | -60.1776 | 64.2105 | -60.1501 | -60.2783 | -60.1776 | -0.09613 | -0.07782 | 0.17395 | 0.041199 | -0.3067 | -0.29297 | -0.21057 | -0.19684 | -0.059509 | -0.059509 | 0.2243 | -0.032043 | -0.059509 | -0.16022 | 0 | -0.10071 | 0.13733 | 124.3744 | 0.027466 | 124.3881 | 124.1226 | 124.1043 | 124.0265 | 124.0448 | -124.2004 | -124.1638 | 124.2783 | 124.3286 | 60.0266 | 60.1044
154.9375 | 124.4339 | -60.0998 | 64.0366 | 0.45109 | 0.00080677 | 0.068119 | 0.049678 | 0.020598 | 0.0041468 | 0.00027221 | 0.20448 | 0.0018322 | 0.075155 | 0.082486 | 0.00666 | 0.0059161 | 0.0070684 | -0.14191 | 63.9404 | -60.2051 | 64.0869 | -60.1273 | -60.4248 | -60.4019 | 0.09613 | 63.9313 | -60.1089 | 64.2426 | -60.0723 | -60.1868 | -60.1364 | -0.10529 | -0.09613 | 0.050354 | -0.027466 | -0.30212 | -0.32501 | -0.19684 | -0.21973 | -0.009156 | -0.10529 | 0.20599 | 0.027465 | -0.036622 | -0.086976 | -0.027466 | -0.07782 | 0.07782 | 124.292 | 0.036621 | 124.3515 | 124.1455 | 124.0402 | 124.0402 | 124.0311 | -124.2416 | -124.1455 | 124.1867 | 124.3423 | 59.9579 | 60.1959
155.9688 | 124.3286 | -60.1273 | 64.0549 | -0.021937 | -0.0013302 | 0.069187 | 0.059291 | -0.0018326 | -0.022556 | -0.030703 | -0.13121 | 0.0018322 | 0.070883 | 0.039761 | 0.00025105 | 0.00057606 | -0.01109 | 0.082397 | 63.945 | -60.1685 | 64.3112 | -59.9396 | -60.3104 | -60.3287 | -0.12817 | 63.9404 | -60.1776 | 64.1052 | -60.2692 | -60.3928 | -60.2875 | -0.041199 | -0.10986 | 0.25635 | 0.18768 | -0.20142 | -0.18311 | -0.16022 | -0.14191 | -0.050354 | -0.11444 | 0.050354 | -0.14191 | -0.16022 | -0.2655 | -0.10986 | -0.21515 | 0.22888 | 124.4797 | -0.091553 | 124.2828 | 124.1135 | 124.118 | 124.0723 | 124.0677 | -124.2233 | -124.2325 | 124.4385 | 124.2325 | 60.2097 | 59.9991
156.9375 | 124.4385 | -60.1227 | 64.0228 | -0.037196 | -0.0066702 | 0.065983 | 0.064631 | 0.0077804 | -0.0086702 | 0.0013402 | -0.03966 | 0.010377 | 0.069815 | 0.041897 | -0.008294 | 0.014461 | -0.0025446 | -0.073242 | 63.8901 | -60.2097 | 64.151 | -60.0769 | -60.4248 | -60.434 | -0.013733 | 63.8901 | -60.1501 | 64.2105 | -60.141 | -60.2737 | -60.1685 | -0.086975 | -0.13275 | 0.12817 | 0.045777 | -0.31128 | -0.30212 | -0.2243 | -0.21515 | -0.027465 | -0.13275 | 0.18768 | -0.01831 | -0.045776 | -0.15106 | -0.018311 | -0.1236 | 0.13275 | 124.3607 | 0.009155 | 124.3607 | 124.0997 | 124.0402 | 124.0128 | 124.0128 | -124.2325 | -124.173 | 124.2737 | 124.3332 | 60.0494 | 60.1089
157.9375 | 124.4247 | -60.0861 | 64.0137 | -0.037196 | 0.012556 | 0.072392 | 0.061427 | -0.011446 | -0.0011942 | -0.0061368 | 0.12819 | -0.0035078 | 0.06661 | 0.035489 | -0.001885 | 0.0080531 | 0.0049324 | -0.036621 | 63.8718 | -60.1959 | 64.119 | -60.1318 | -60.6537 | -60.5026 | 0.013733 | 63.9313 | -60.1135 | 64.1968 | -60.1547 | -60.2463 | -60.1685 | -0.10986 | -0.14191 | 0.10529 | -0.045776 | -0.41656 | -0.56763 | -0.3067 | -0.45776 | -0.027465 | -0.082398 | 0.1831 | -0.068664 | -0.082397 | -0.16022 | -0.054932 | -0.13275 | 0.064087 | 124.3149 | -0.041199 | 124.3103 | 124.0677 | 124.0448 | 123.9578 | 124.0173 | -124.2096 | -124.1272 | 124.205 | 124.2828 | 60.0494 | 60.0998
158.9375 | 124.4202 | -60.1227 | 64.0137 | 0.023839 | -0.0098752 | 0.070255 | 0.057155 | -0.0071726 | -0.0065342 | 0.0013402 | 0.14344 | -0.0045758 | 0.059133 | 0.069668 | -0.013634 | 0.0037801 | 0.0017274 | -0.022888 | 63.8672 | -60.1776 | 64.1098 | -60.1364 | -60.4706 | -60.4477 | 0.013733 | 63.8947 | -60.1547 | 64.2105 | -60.141 | -60.26 | -60.1868 | -0.054931 | -0.14648 | 0.09613 | -0.013733 | -0.32501 | -0.3479 | -0.27008 | -0.29297 | -0.032043 | -0.11902 | 0.19684 | -0.01831 | -0.064087 | -0.13733 | -0.032044 | -0.10529 | 0.041198 | 124.2874 | 0.013733 | 124.3652 | 124.0448 | 124.0494 | 123.9899 | 124.0173 | -124.1913 | -124.1684 | 124.2325 | 124.3332 | 60.0998 | 60.1364
159.9375 | 124.4339 | -60.0769 | 64.0549 | 0.0085801 | 0.0040108 | 0.060642 | 0.072108 | 0.020598 | -0.0011942 | -0.0061368 | 0.25026 | 0.00076419 | 0.073019 | 0.052579 | -0.002953 | 0.0016441 | -0.0004086 | 0.07782 | 63.9084 | -60.1639 | 64.1373 | -60.0861 | -60.4111 | -60.3882 | 0.09613 | 63.9587 | -60.1227 | 64.2059 | -60.1044 | -60.2051 | -60.173 | -0.086975 | -0.14649 | 0.082397 | -0.009156 | -0.31128 | -0.33417 | -0.22431 | -0.24719 | -0.045777 | -0.096131 | 0.15106 | -0.027466 | -0.096131 | -0.12817 | -0.050354 | -0.082397 | 0.077819 | 124.3011 | 0.018311 | 124.3286 | 124.0723 | 124.0814 | 123.9853 | 124.0356 | -124.2188 | -124.1776 | 124.2142 | 124.2828 | 60.1547 | 60.173
160.9375 | 124.411 | -60.1318 | 64.0182 | 0.0085801 | 0.0029428 | 0.05637 | 0.068904 | -0.023195 | -0.0054662 | -0.0039998 | 0.08241 | 0.0029002 | 0.073019 | 0.073941 | -0.007226 | 0.0048481 | -0.016431 | -0.07782 | 63.8855 | -60.2463 | 64.1602 | -60.0861 | -60.434 | -60.4156 | -0.045776 | 63.9038 | -60.1639 | 64.2059 | -60.1593 | -60.26 | -60.1639 | -0.11444 | -0.13275 | 0.14191 | 0.045776 | -0.28381 | -0.30212 | -0.16937 | -0.18768 | -0.032043 | -0.11444 | 0.18768 | -0.027466 | -0.032043 | -0.12817 | 0 | -0.096131 | 0.16022 | 124.4064 | 0.004577 | 124.3698 | 124.1318 | 124.0677 | 124.0173 | 124.0356 | -124.2645 | -124.1821 | 124.292 | 124.3378 | 60.054 | 60.0861
161.9375 | 124.4064 | -60.1089 | 64.0274 | 0.039098 | 0.00080677 | 0.058506 | 0.066768 | 0.0024404 | 0.0094878 | 0.0013402 | 0.12819 | -0.0024398 | 0.075155 | 0.066464 | 0.003456 | 0.016598 | 0.0092044 | -0.07782 | 63.8855 | -60.2097 | 64.1968 | -60.0494 | -60.3882 | -60.3928 | -0.054932 | 63.9175 | -60.173 | 64.1876 | -60.1639 | -60.2554 | -60.173 | -0.10071 | -0.14191 | 0.16937 | 0.05951 | -0.28381 | -0.27924 | -0.1831 | -0.17853 | -0.064087 | -0.10986 | 0.16022 | -0.054931 | -0.064087 | -0.14648 | 0 | -0.082397 | 0.16022 | 124.4064 | 0.009156 | 124.3607 | 124.0952 | 124.0906 | 123.9944 | 124.0265 | -124.2371 | -124.2004 | 124.3057 | 124.2966 | 60.0311 | 60.054
162.9375 | 124.4476 | -60.0906 | 64.0045 | 0.10013 | 0.0040108 | 0.069187 | 0.074244 | -0.0050366 | -0.014011 | 0.0056132 | 0.051892 | -0.0067128 | 0.070883 | 0.042966 | 0.002387 | 0.0069851 | -0.0014766 | -0.041199 | 63.858 | -60.1913 | 64.1235 | -60.1318 | -60.4477 | -60.4523 | 0.073242 | 63.8901 | -60.1959 | 64.2334 | -60.1227 | -60.2829 | -60.1959 | -0.10071 | -0.14649 | 0.11902 | -0.041199 | -0.36163 | -0.35706 | -0.26093 | -0.25635 | -0.10529 | -0.11444 | 0.22888 | -0.032044 | -0.10529 | -0.19226 | 0 | -0.086975 | 0.059509 | 124.3149 | 0.073242 | 124.4293 | 124.0494 | 124.086 | 123.9487 | 123.9807 | -124.1959 | -124.2004 | 124.2142 | 124.324 | 60.0494 | 60.1639
163.9375 | 124.379 | -60.1456 | 64.032 | 0.11539 | 0.0029428 | 0.06171 | 0.055018 | 0.016325 | -0.0043982 | -0.0082728 | 0.021375 | 0.00076419 | 0.078359 | 0.067532 | -0.005089 | 0.0037801 | -0.0089536 | -0.10071 | 63.8901 | -60.2371 | 64.238 | -60.0128 | -60.3424 | -60.3607 | -0.086975 | 63.9313 | -60.173 | 64.1647 | -60.2097 | -60.3287 | -60.228 | -0.091553 | -0.14191 | 0.20599 | 0.13275 | -0.21515 | -0.19684 | -0.1236 | -0.10529 | -0.027466 | -0.10071 | 0.13275 | -0.064087 | -0.082397 | -0.1831 | -0.054931 | -0.15564 | 0.22431 | 124.4751 | -0.036621 | 124.3378 | 124.1272 | 124.1043 | 124.0356 | 124.0768 | -124.2691 | -124.205 | 124.3835 | 124.3103 | 60.0449 | 60.0586
164.9375 | 124.4431 | -60.1273 | 63.9816 | 0.054357 | -0.0034662 | 0.068119 | 0.061427 | -0.017855 | 0.0073508 | 0.0077492 | 0.11293 | 0.012514 | 0.060202 | 0.072873 | -0.002953 | 0.011257 | 0.0092044 | -0.059509 | 63.8763 | -60.1868 | 64.1464 | -60.0952 | -60.4614 | -60.4568 | -0.022888 | 63.8901 | -60.1593 | 64.2151 | -60.1547 | -60.2417 | -60.1593 | -0.05951 | -0.10529 | 0.16479 | 0.032043 | -0.32959 | -0.33417 | -0.27008 | -0.27466 | -0.032044 | -0.091552 | 0.23346 | -0.027466 | -0.032044 | -0.11444 | 0 | -0.082397 | 0.091553 | 124.3332 | 0.004578 | 124.3744 | 124.0631 | 124.0494 | 124.0036 | 124.0173 | -124.1684 | -124.1409 | 124.2737 | 124.3423 | 60.0677 | 60.1044
165.9375 | 124.4247 | -60.1227 | 64.0137 | 0.11539 | 0.0018748 | 0.065983 | 0.064631 | 0.015257 | -0.022556 | -0.0050688 | 0.11293 | -0.00030381 | 0.076223 | 0.055783 | -0.007226 | -0.0015599 | 0.0038644 | -0.07782 | 63.8763 | -60.2051 | 64.151 | -60.0586 | -60.4156 | -60.434 | -0.004578 | 63.913 | -60.1547 | 64.2105 | -60.1364 | -60.2692 | -60.1639 | -0.082397 | -0.13733 | 0.13733 | 0.064087 | -0.31128 | -0.29297 | -0.22888 | -0.21057 | -0.032043 | -0.10071 | 0.19684 | -0.013733 | -0.041198 | -0.14648 | -0.009155 | -0.11444 | 0.14648 | 124.3561 | 0.01831 | 124.3652 | 124.0814 | 124.0677 | 123.999 | 124.0356 | -124.2188 | -124.1684 | 124.2737 | 124.3332 | 60.0449 | 60.1181
166.9375 | 124.3973 | -60.1273 | 63.9816 | 0.14591 | 0.0050788 | 0.064915 | 0.076381 | -0.0039686 | 0.019101 | -0.0061368 | -0.0091433 | 0.011445 | 0.052725 | 0.069668 | 0.003456 | 0.015529 | -0.0004086 | -0.091553 | 63.8901 | -60.2371 | 64.1739 | -60.0494 | -60.3882 | -60.3928 | -0.054932 | 63.9084 | -60.1685 | 64.1693 | -60.1456 | -60.26 | -60.1822 | -0.10986 | -0.091552 | 0.19226 | 0.07782 | -0.2655 | -0.26093 | -0.15564 | -0.15106 | -0.041199 | -0.073242 | 0.18768 | -0.018311 | -0.054932 | -0.13275 | -0.013733 | -0.091553 | 0.18768 | 124.411 | 0.022888 | 124.3378 | 124.1272 | 124.0768 | 124.0173 | 124.0356 | -124.2188 | -124.1501 | 124.3011 | 124.2966 | 60.0357 | 60.0723
167.9375 | 124.4202 | -60.1364 | 63.9725 | 0.10013 | 0.0029428 | 0.068119 | 0.063563 | 0.0088484 | -0.0022622 | -0.0072048 | 0.12819 | -0.0035078 | 0.056997 | 0.056851 | -0.012566 | 0.0048481 | -0.027112 | -0.045776 | 63.8626 | -60.1822 | 64.1052 | -60.1227 | -60.4706 | -60.4706 | -0.068665 | 63.858 | -60.1776 | 64.2151 | -60.1227 | -60.2509 | -60.1639 | -0.045776 | -0.10986 | 0.13275 | 0.013733 | -0.33417 | -0.33417 | -0.28839 | -0.28839 | -0.041198 | -0.11444 | 0.24261 | 0.013733 | -0.027465 | -0.11444 | 0.013733 | -0.073242 | 0.059509 | 124.2874 | 0.054931 | 124.3927 | 124.0448 | 124.0356 | 123.999 | 123.9944 | -124.1547 | -124.1501 | 124.2416 | 124.3515 | 60.0906 | 60.0677
168.9375 | 124.3927 | -60.1135 | 63.9908 | -0.0066789 | 0.0093518 | 0.060642 | 0.063563 | 0.010984 | -0.022556 | -0.0093408 | -0.024402 | 0.0071732 | 0.068746 | 0.044034 | 0.005592 | 0.0069851 | 0.0092044 | -0.082397 | 63.9175 | -60.2097 | 64.2105 | -60.0128 | -60.3699 | -60.3516 | -0.086975 | 63.945 | -60.1822 | 64.183 | -60.1913 | -60.2966 | -60.2097 | -0.096131 | -0.073242 | 0.21973 | 0.10071 | -0.23804 | -0.25635 | -0.14191 | -0.16022 | -0.068665 | -0.045777 | 0.19226 | -0.07782 | -0.096131 | -0.18311 | -0.027466 | -0.11444 | 0.19684 | 124.4202 | -0.009155 | 124.3652 | 124.1272 | 124.1272 | 124.0311 | 124.0585 | -124.2004 | -124.173 | 124.324 | 124.2966 | 60.0311 | 60.0266
169.9375 | 124.4339 | -60.1135 | 63.9771 | 0.069615 | -0.0066702 | 0.063847 | 0.067836 | 0.013121 | 0.0020108 | -0.0029318 | 0.097669 | -0.0067128 | 0.069815 | 0.033353 | 0.003456 | 0.014461 | -0.014294 | -0.041199 | 63.8626 | -60.1913 | 64.1052 | -60.1044 | -60.4294 | -60.4523 | 0.022888 | 63.913 | -60.1318 | 64.2105 | -60.1273 | -60.2554 | -60.1593 | -0.07782 | -0.11444 | 0.12817 | 0.009155 | -0.33875 | -0.31586 | -0.26093 | -0.23804 | -0.018311 | -0.064087 | 0.23346 | -0.013733 | -0.045777 | -0.14191 | -0.027466 | -0.1236 | 0.086975 | 124.2966 | 0.004578 | 124.3423 | 124.054 | 124.0448 | 123.9761 | 124.0265 | -124.1684 | -124.1089 | 124.2188 | 124.324 | 60.0723 | 60.1364
170.9375 | 124.4705 | -60.1181 | 63.9999 | 0.054357 | 0.0061468 | 0.064915 | 0.060359 | 0.0077804 | 0.019101 | -0.013613 | 0.14344 | -0.0099168 | 0.064474 | 0.017331 | -0.011498 | 0.016598 | 0.0006594 | -0.036621 | 63.8763 | -60.2097 | 64.119 | -60.1044 | -60.4431 | -60.4477 | 0.009155 | 63.9221 | -60.1685 | 64.2242 | -60.2463 | -60.5072 | -60.1456 | -0.091553 | -0.1236 | 0.11902 | 0.013733 | -0.32959 | -0.32501 | -0.23804 | -0.23346 | -0.050354 | -0.07782 | 0.2243 | -0.12817 | -0.027466 | -0.3891 | 0.022888 | -0.33875 | 0.10529 | 124.3286 | -0.07782 | 124.3927 | 124.086 | 124.0906 | 123.9944 | 124.0402 | -124.2096 | -124.1684 | 124.2371 | 124.3423 | 60.0815 | 60.1273
171.9375 | 124.4019 | -60.1227 | 63.9999 | 0.10013 | -0.00026223 | 0.065983 | 0.058223 | 0.0013714 | -0.0086702 | 0.0034762 | 0.12819 | -0.0024398 | 0.058065 | 0.071805 | -0.009362 | 0.0016441 | -0.0046806 | -0.059509 | 63.8809 | -60.173 | 64.1006 | -60.1044 | -60.4568 | -60.4477 | 0.032043 | 63.9084 | -60.1181 | 64.2014 | -60.1364 | -60.2509 | -60.1822 | -0.050354 | -0.11902 | 0.10071 | 0.018311 | -0.32501 | -0.33417 | -0.27466 | -0.28381 | 0.004578 | -0.091553 | 0.20142 | -0.013733 | -0.059509 | -0.12817 | -0.064087 | -0.13275 | 0.068665 | 124.2737 | -0.018311 | 124.3195 | 124.054 | 124.0265 | 124.0036 | 124.0311 | -124.173 | -124.118 | 124.2233 | 124.324 | 60.0632 | 60.1547
172.9375 | 124.379 | -60.0769 | 64.0411 | 0.25272 | 0.0040108 | 0.064915 | 0.060359 | -0.0050366 | 0.0052148 | -0.0018638 | 0.29603 | 0.011445 | 0.068746 | 0.067532 | 0.004524 | 0.00057606 | 0.0017274 | 0.091553 | 63.9175 | -60.1593 | 64.151 | -60.0861 | -60.4065 | -60.4111 | 0.09613 | 63.9542 | -60.0998 | 64.2105 | -60.1044 | -60.2097 | -60.1685 | -0.082398 | -0.1236 | 0.10986 | -0.009156 | -0.33417 | -0.32959 | -0.25177 | -0.24719 | -0.022888 | -0.086975 | 0.16937 | -0.027466 | -0.091553 | -0.13275 | -0.068665 | -0.10986 | 0.073242 | 124.3103 | -0.004578 | 124.3103 | 124.0768 | 124.054 | 123.9944 | 124.0311 | -124.2004 | -124.1409 | 124.2279 | 124.2874 | 60.1685 | 60.173
173.9375 | 124.3378 | -60.1318 | 64.0366 | 0.069615 | 0.0061468 | 0.060642 | 0.060359 | 0.012053 | -0.011875 | -0.0072048 | -0.024402 | 0.0018322 | 0.059133 | 0.047238 | -0.013634 | 0.0048481 | -0.032452 | -0.082397 | 63.9175 | -60.2234 | 64.2426 | -59.9854 | -60.347 | -60.3424 | -0.09613 | 63.9587 | -60.173 | 64.1373 | -60.2234 | -60.3378 | -60.2417 | -0.091553 | -0.11902 | 0.20599 | 0.14648 | -0.21057 | -0.21515 | -0.11902 | -0.1236 | -0.041199 | -0.07782 | 0.10071 | -0.091553 | -0.10986 | -0.20599 | -0.068664 | -0.16479 | 0.23804 | 124.4659 | -0.050354 | 124.3103 | 124.1409 | 124.1318 | 124.0494 | 124.0906 | -124.2599 | -124.2096 | 124.3744 | 124.2691 | 60.0494 | 60.0357
174.9375 | 124.4339 | -60.1089 | 64.0411 | 0.19169 | -0.00026223 | 0.067051 | 0.049678 | 0.020598 | -0.0033302 | 0.00027221 | 0.34181 | -0.0056438 | 0.081564 | 0.061124 | -0.002953 | -0.00049194 | -0.024975 | 0.004578 | 63.9084 | -60.1501 | 64.151 | -60.0861 | -60.4202 | -60.4065 | 0.059509 | 63.9313 | -60.1364 | 64.2242 | -60.1135 | -60.1913 | -60.1456 | -0.041198 | -0.13275 | 0.10986 | 0.022888 | -0.29755 | -0.31128 | -0.25635 | -0.27008 | -0.027466 | -0.10986 | 0.1831 | -0.004577 | -0.036621 | -0.082397 | -0.009155 | -0.054931 | 0.064086 | 124.3011 | 0.022889 | 124.3607 | 124.0585 | 124.0677 | 124.0173 | 124.0402 | -124.1913 | -124.1776 | 124.2599 | 124.3332 | 60.1135 | 60.1685
175.9375 | 124.4156 | -60.1135 | 64.032 | 0.069615 | 0.013624 | 0.072392 | 0.068904 | 0.0077804 | -0.0033302 | 0.0098852 | 0.11293 | -0.0056438 | 0.054861 | 0.079282 | -0.005089 | -0.00049194 | -0.0057486 | -0.027466 | 63.8626 | -60.1776 | 64.1144 | -60.1273 | -60.4431 | -60.434 | 0.004578 | 63.8992 | -60.1593 | 64.1876 | -60.1501 | -60.2646 | -60.1822 | -0.064087 | -0.16937 | 0.082398 | -0.013733 | -0.32043 | -0.32959 | -0.25635 | -0.2655 | -0.045777 | -0.13275 | 0.15564 | -0.036621 | -0.068665 | -0.15106 | -0.022888 | -0.10529 | 0.050354 | 124.292 | 0.009156 | 124.3469 | 124.0402 | 124.0585 | 123.9761 | 124.0128 | -124.2096 | -124.1913 | 124.2279 | 124.3011 | 60.0861 | 60.1181
176.9375 | 124.4293 | -60.1273 | 64.0182 | -0.0066789 | 0.0029428 | 0.058506 | 0.069972 | 0.0056444 | 0.0062828 | -0.00079579 | -0.024402 | 0.0050372 | 0.073019 | 0.057919 | -0.013634 | 0.0059161 | -0.013226 | -0.086975 | 63.8947 | -60.2188 | 64.1785 | -60.0677 | -60.4111 | -60.4065 | -0.022888 | 63.9175 | -60.1593 | 64.2151 | -60.1547 | -60.26 | -60.1685 | -0.091553 | -0.1236 | 0.16022 | 0.059509 | -0.27924 | -0.28381 | -0.18768 | -0.19226 | -0.032044 | -0.10071 | 0.19684 | -0.027466 | -0.041199 | -0.13275 | -0.009155 | -0.10071 | 0.15106 | 124.3973 | 0.004578 | 124.3744 | 124.1135 | 124.0768 | 124.0219 | 124.0448 | -124.2371 | -124.1776 | 124.3057 | 124.3423 | 60.0403 | 60.1044
177.9375 | 124.3881 | -60.0906 | 64.0228 | 0.17643 | -0.010943 | 0.069187 | 0.062495 | -0.0029006 | 0.01376 | 0.0066812 | 0.21974 | -0.0056438 | 0.075155 | 0.077145 | -0.006157 | 0.0048481 | -0.0014766 | -0.022888 | 63.9084 | -60.1547 | 64.1968 | -60.0449 | -60.4248 | -60.4111 | -0.050354 | 63.913 | -60.1593 | 64.1602 | -60.1685 | -60.2646 | -60.2097 | -0.064087 | -0.11444 | 0.17395 | 0.045776 | -0.32043 | -0.33417 | -0.25635 | -0.27008 | -0.068665 | -0.10986 | 0.13733 | -0.07782 | -0.11902 | -0.17395 | -0.050354 | -0.10529 | 0.10986 | 124.3515 | -0.009155 | 124.3195 | 124.0631 | 124.0723 | 123.999 | 124.0036 | -124.1776 | -124.1821 | 124.2874 | 124.2508 | 60.0677 | 60.0403
178.9375 | 124.4202 | -60.1135 | 64.0228 | 0.19169 | 0.012556 | 0.067051 | 0.077449 | -0.00076463 | 0.021237 | -0.0082728 | 0.051892 | -0.0035078 | 0.080496 | 0.048306 | -0.007226 | 0.021938 | 0.012409 | -0.022888 | 63.8626 | -60.1913 | 64.1418 | -60.2829 | -60.6445 | -60.4202 | 0.022888 | 63.9404 | -60.141 | 64.1968 | -60.1456 | -60.2463 | -60.1639 | -0.07782 | -0.16022 | 0.11902 | -0.16937 | -0.3067 | -0.53101 | -0.22888 | -0.45319 | -0.027466 | -0.082397 | 0.17395 | -0.032044 | -0.050354 | -0.13275 | -0.022888 | -0.10529 | -0.091553 | 124.3332 | -0.004578 | 124.3378 | 124.054 | 124.0814 | 123.9761 | 124.054 | -124.2142 | -124.1638 | 124.2554 | 124.3103 | 60.0906 | 60.1364
179.9375 | 124.4614 | -60.0952 | 64.0182 | -0.037196 | -0.00026223 | 0.059574 | 0.05395 | 0.0035084 | 0.018033 | -0.0039998 | 0.29603 | 0.0029002 | 0.065542 | 0.037625 | -0.008294 | 0.0069851 | -0.013226 | 0.032043 | 63.9038 | -60.173 | 64.1373 | -60.0998 | -60.4385 | -60.4202 | 0.10986 | 63.9221 | -60.1135 | 64.2471 | -60.0494 | -60.173 | -60.1044 | -0.07782 | -0.11444 | 0.11902 | -0.004577 | -0.32501 | -0.34332 | -0.24719 | -0.2655 | -0.01831 | -0.096131 | 0.22888 | 0.045777 | -0.009155 | -0.07782 | 0.009155 | -0.05951 | 0.073243 | 124.3103 | 0.064087 | 124.3607 | 124.0768 | 124.0356 | 123.999 | 124.0173 | -124.1913 | -124.1318 | 124.2325 | 124.3423 | 60.1273 | 60.2051
180.9375 | 124.3881 | -60.1318 | 64.0091 | 0.084874 | -0.00026223 | 0.06171 | 0.079585 | -0.013582 | -0.018283 | 0.0045452 | 0.036633 | -0.0088488 | 0.084768 | 0.058987 | -0.009362 | 0.0059161 | -0.0057486 | -0.091553 | 63.9038 | -60.2234 | 64.2014 | -60.0266 | -60.3607 | -60.3699 | -0.07782 | 63.9175 | -60.173 | 64.1647 | -60.1868 | -60.2966 | -60.2097 | -0.091553 | -0.10529 | 0.19226 | 0.10529 | -0.23804 | -0.22888 | -0.14648 | -0.13733 | -0.041199 | -0.091552 | 0.15564 | -0.054932 | -0.07782 | -0.16479 | -0.036621 | -0.1236 | 0.19684 | 124.4247 | -0.013733 | 124.3378 | 124.1272 | 124.0906 | 124.0356 | 124.0494 | -124.2325 | -124.1821 | 124.3332 | 124.2966 | 60.0403 | 60.054
181.9375 | 124.3652 | -60.1456 | 64.0182 | 0.11539 | -0.0013302 | 0.060642 | 0.064631 | -0.011446 | 0.0041468 | 0.0013402 | 0.021375 | 0.0082412 | 0.068746 | 0.044034 | 0.002387 | 0.0048481 | -0.0025446 | -0.091553 | 63.9038 | -60.2142 | 64.2059 | -60.0128 | -60.347 | -60.3699 | -0.10071 | 63.9404 | -60.1639 | 64.1693 | -60.2051 | -60.3149 | -60.2142 | -0.068664 | -0.11444 | 0.18768 | 0.13275 | -0.2243 | -0.20142 | -0.15564 | -0.13275 | -0.01831 | -0.07782 | 0.15106 | -0.059509 | -0.068664 | -0.16937 | -0.050354 | -0.15106 | 0.20142 | 124.4202 | -0.041199 | 124.3332 | 124.118 | 124.1043 | 124.0494 | 124.086 | -124.2325 | -124.1821 | 124.3515 | 124.3149 | 60.054 | 60.0449
182.9375 | 124.3195 | -60.1181 | 64.0778 | 0.25272 | -0.0056022 | 0.052097 | 0.064631 | 0.017393 | 0.0084198 | 0.012021 | 0.08241 | 0.0050372 | 0.0837 | 0.057919 | 0.001319 | 0.00057606 | -0.0057486 | 0.068665 | 63.9496 | -60.1639 | 64.2242 | -59.9808 | -60.3195 | -60.3195 | -0.013733 | 63.9679 | -60.1547 | 64.1373 | -60.2051 | -60.3058 | -60.2417 | -0.045776 | -0.12817 | 0.14648 | 0.13733 | -0.20142 | -0.20142 | -0.15564 | -0.15564 | -0.036621 | -0.10986 | 0.059509 | -0.086975 | -0.1236 | -0.18768 | -0.086975 | -0.15106 | 0.18311 | 124.3881 | -0.050354 | 124.292 | 124.1135 | 124.1226 | 124.0677 | 124.086 | -124.2416 | -124.2325 | 124.3423 | 124.2554 | 60.1868 | 60.1044
183.9375 | 124.4064 | -60.0906 | 64.0045 | -0.0066789 | -0.0034662 | 0.067051 | 0.064631 | 0.0045764 | 0.010556 | -0.00079579 | 0.17396 | -0.0077808 | 0.063406 | 0.079282 | 0.004524 | 0.019802 | -0.0068176 | -0.041199 | 63.8672 | -60.1913 | 64.119 | -60.1181 | -60.434 | -60.4477 | 0.004578 | 63.8901 | -60.141 | 64.1922 | -60.1593 | -60.2509 | -60.1959 | -0.10071 | -0.13733 | 0.11444 | -0.027466 | -0.35706 | -0.34332 | -0.25635 | -0.24262 | -0.050354 | -0.11444 | 0.18768 | -0.068665 | -0.10529 | -0.16022 | -0.054932 | -0.10986 | 0.073242 | 124.3103 | -0.018311 | 124.3332 | 124.0585 | 124.0311 | 123.9578 | 123.9807 | -124.1959 | -124.1455 | 124.2096 | 124.2828 | 60.0494 | 60.0952
184.9375 | 124.4293 | -60.1181 | 63.9908 | 0.084874 | 0.01576 | 0.064915 | 0.07104 | 0.0088484 | -0.019351 | -0.0093408 | 0.036633 | -0.0067128 | 0.062338 | 0.024808 | -0.001885 | 0.0048481 | -0.0078856 | -0.041199 | 63.8397 | -60.173 | 64.1144 | -60.141 | -60.4385 | -60.4614 | 0.027466 | 63.8901 | -60.1822 | 64.2014 | -60.1593 | -60.2417 | -60.173 | -0.054932 | -0.15106 | 0.1236 | -0.022888 | -0.34332 | -0.32044 | -0.28839 | -0.2655 | -0.064087 | -0.10071 | 0.21057 | -0.041199 | -0.054932 | -0.1236 | 0.009155 | -0.059509 | 0.032044 | 124.2874 | 0.022888 | 124.3835 | 124.0128 | 124.0723 | 123.9578 | 124.0082 | -124.1638 | -124.173 | 124.2325 | 124.3195 | 60.0769 | 60.1456
185.9375 | 124.4385 | -60.0952 | 64.0091 | 0.023839 | 0.00080677 | 0.067051 | 0.067836 | 0.0067124 | -0.00012524 | -0.012545 | 0.31129 | 0.0018322 | 0.047384 | 0.088895 | -0.00081695 | 0.0091211 | -0.016431 | -0.027466 | 63.8672 | -60.1959 | 64.1006 | -60.1273 | -60.4111 | -60.6903 | 0.073242 | 63.9175 | -60.1089 | 64.183 | -60.1547 | -60.2509 | -60.1593 | -0.10071 | -0.14191 | 0.091553 | -0.032043 | -0.59509 | -0.31586 | -0.49439 | -0.21515 | -0.013733 | -0.091552 | 0.17395 | -0.059509 | -0.064087 | -0.15564 | -0.050354 | -0.14191 | 0.068665 | 124.2966 | -0.045776 | 124.292 | 124.0631 | 124.0265 | 123.9624 | 124.0128 | -124.205 | -124.118 | 124.1959 | 124.2783 | 60.0677 | 60.1685
186.9375 | 124.4064 | -60.1089 | 64.0137 | 0.054357 | 0.0082828 | 0.063847 | 0.065699 | -0.0061046 | -0.012943 | -0.013613 | 0.14344 | -0.0024398 | 0.062338 | 0.062192 | -0.00081695 | 0.010189 | -0.012158 | -0.036621 | 63.8763 | -60.1868 | 64.1098 | -60.1181 | -60.4477 | -60.4477 | -0.009155 | 63.9221 | -60.1364 | 64.3616 | -60.1227 | -60.1959 | -60.1776 | -0.07782 | -0.13733 | 0.09613 | -0.009155 | -0.33875 | -0.33875 | -0.26093 | -0.26093 | -0.027466 | -0.091553 | 0.3479 | -0.013733 | -0.068664 | -0.086975 | -0.041198 | -0.059509 | 0.068665 | 124.2966 | 0.013733 | 124.498 | 124.0631 | 124.0585 | 123.9853 | 124.0311 | -124.2004 | -124.1501 | 124.2188 | 124.4705 | 60.0723 | 60.0998
187.9375 | 124.4019 | -60.0952 | 64.0457 | 0.17643 | 0.0061468 | 0.062778 | 0.077449 | -0.0071726 | 0.0073508 | 0.00027221 | 0.25026 | -0.010985 | 0.075155 | 0.035489 | 0.004524 | 0.0037801 | -0.0046806 | 0.068665 | 63.8855 | -60.1318 | 64.1327 | -60.0861 | -60.4065 | -60.3836 | 0.10529 | 63.9542 | -60.1318 | 64.2059 | -60.1044 | -60.2142 | -60.1501 | -0.036621 | -0.16022 | 0.086975 | 0.009155 | -0.28839 | -0.31128 | -0.25177 | -0.27466 | -0.036621 | -0.091552 | 0.16022 | -0.009155 | -0.054931 | -0.11902 | -0.01831 | -0.082397 | 0.045776 | 124.2645 | 0.027466 | 124.3378 | 124.0173 | 124.086 | 123.9807 | 124.0494 | -124.1776 | -124.1776 | 124.2279 | 124.3011 | 60.1639 | 60.2005
188.9375 | 124.3378 | -60.1364 | 64.0045 | 0.069615 | -0.0098752 | 0.062778 | 0.075312 | 0.020598 | -0.00012524 | -0.0061368 | -0.11595 | 0.011445 | 0.067678 | 0.062192 | -0.005089 | 0.019802 | 0.0092044 | -0.091553 | 63.9038 | -60.2371 | 64.2334 | -59.9808 | -60.3104 | -60.3424 | -0.1236 | 63.9359 | -60.1913 | 64.1418 | -60.2463 | -60.3561 | -60.26 | -0.10071 | -0.10071 | 0.22888 | 0.15564 | -0.20599 | -0.17395 | -0.10529 | -0.073242 | -0.054931 | -0.068665 | 0.13733 | -0.10986 | -0.1236 | -0.21973 | -0.068665 | -0.1648 | 0.25635 | 124.4705 | -0.054932 | 124.3332 | 124.1409 | 124.1272 | 124.0402 | 124.0723 | -124.2416 | -124.1959 | 124.3698 | 124.2783 | 60.0449 | 60.0128
189.9375 | 124.411 | -60.1227 | 64.0045 | 0.10013 | -0.0045342 | 0.071323 | 0.057155 | -0.0050366 | 0.0094878 | -0.0029318 | 0.40284 | -0.0013718 | 0.067678 | 0.033353 | 0.002387 | 0.010189 | 0.010272 | -0.032043 | 63.8718 | -60.2097 | 64.0915 | -60.1456 | -60.4019 | -60.6766 | 0.064087 | 63.9221 | -60.1501 | 64.1968 | -60.141 | -60.2417 | -60.1685 | -0.086975 | -0.13275 | 0.086975 | -0.022888 | -0.55389 | -0.27924 | -0.46692 | -0.19226 | -0.027465 | -0.082398 | 0.19226 | -0.01831 | -0.045776 | -0.11902 | -0.018311 | -0.091553 | 0.064087 | 124.3011 | 0.009155 | 124.3469 | 124.0814 | 124.0723 | 123.9944 | 124.0448 | -124.2142 | -124.1547 | 124.2142 | 124.3195 | 60.0906 | 60.1868
190.9688 | 124.3744 | -60.1044 | 64.0137 | -0.021937 | 0.00080677 | 0.06171 | 0.061427 | 0.0013714 | 0.0030788 | -0.0072048 | 0.14344 | -0.0035078 | 0.068746 | 0.040829 | -0.00081695 | -0.0015599 | -0.015362 | -0.054932 | 63.8443 | -60.1822 | 64.1373 | -60.0998 | -60.4065 | -60.4248 | -0.009155 | 63.9084 | -60.1501 | 64.1785 | -60.1639 | -60.2829 | -60.1913 | -0.07782 | -0.16937 | 0.1236 | 0.004578 | -0.32043 | -0.30212 | -0.24262 | -0.2243 | -0.045776 | -0.10529 | 0.16479 | -0.059509 | -0.086975 | -0.17853 | -0.041199 | -0.13275 | 0.082398 | 124.3195 | -0.013733 | 124.3286 | 124.0265 | 124.0585 | 123.9487 | 124.0128 | -124.1959 | -124.1638 | 124.2416 | 124.2828 | 60.0494 | 60.0952
191.9375 | 124.4202 | -60.1044 | 64.0182 | 0.069615 | 0.0061468 | 0.067051 | 0.066768 | -0.013582 | 0.016964 | -0.0072048 | 0.11293 | -0.0088488 | 0.082632 | 0.062192 | -0.01043 | 0.012325 | -0.0068176 | -0.009155 | 63.8718 | -60.1547 | 64.064 | -60.1273 | -60.4477 | -60.4477 | 0.018311 | 63.9084 | -60.1364 | 64.2105 | -60.1318 | -60.2509 | -60.1593 | -0.050354 | -0.14648 | 0.045776 | -0.022888 | -0.34332 | -0.34332 | -0.29297 | -0.29297 | -0.032044 | -0.10986 | 0.19226 | -0.027466 | -0.054932 | -0.14648 | -0.022888 | -0.11444 | 0.027466 | 124.2188 | 0.004578 | 124.3469 | 124.0265 | 124.0448 | 123.9761 | 124.0128 | -124.173 | -124.1547 | 124.1684 | 124.3149 | 60.0952 | 60.1227
192.9688 | 124.379 | -60.1044 | 64.0503 | -0.021937 | -0.0045342 | 0.06171 | 0.057155 | -0.010378 | 0.0030788 | 0.0056132 | 0.29603 | -0.0024398 | 0.058065 | 0.095303 | -0.00081695 | 0.00057606 | -0.0046806 | -0.091553 | 63.8626 | -60.1913 | 64.1647 | -60.0311 | -60.3928 | -60.4065 | -0.018311 | 63.9496 | -60.1639 | 64.1693 | -60.1547 | -60.2554 | -60.1959 | -0.086975 | -0.18768 | 0.11444 | 0.073242 | -0.30212 | -0.28839 | -0.21515 | -0.20142 | -0.059509 | -0.10071 | 0.11902 | -0.050354 | -0.091553 | -0.15106 | -0.032044 | -0.091553 | 0.16022 | 124.3561 | 0.009155 | 124.3332 | 124.054 | 124.1135 | 123.967 | 124.054 | -124.2416 | -124.2142 | 124.2691 | 124.2737 | 60.0128 | 60.0861
193.9375 | 124.292 | -60.141 | 64.0457 | 0.023839 | 0.01042 | 0.069187 | 0.068904 | 0.0067124 | -0.010807 | -0.01575 | -0.054919 | 0.0050372 | 0.064474 | 0.069668 | 0.004524 | -0.0015599 | 0.015613 | -0.059509 | 63.913 | -60.2325 | 64.27 | -59.9304 | -60.2875 | -60.2783 | -0.12817 | 63.9587 | -60.1913 | 64.2746 | -60.1868 | -60.3104 | -60.2966 | -0.091553 | -0.13275 | 0.22431 | 0.21057 | -0.13733 | -0.14648 | -0.045776 | -0.054932 | -0.050354 | -0.086975 | 0.22888 | -0.045777 | -0.15564 | -0.16937 | -0.10529 | -0.11902 | 0.30212 | 124.5026 | 0.004577 | 124.4659 | 124.1455 | 124.1501 | 124.054 | 124.0997 | -124.2783 | -124.2371 | 124.411 | 124.4156 | 60.0815 | 60.0128
194.9844 | 124.3011 | -60.1456 | 64.0411 | 0.054357 | 0.0050788 | 0.055302 | 0.074244 | 0.014189 | 0.0084198 | -0.0039998 | -0.054919 | 0.0093092 | 0.069815 | 0.019467 | -0.002953 | 0.0037801 | -0.0068176 | -0.07782 | 63.9496 | -60.228 | 64.2609 | -59.9487 | -60.2966 | -60.3012 | -0.13275 | 63.945 | -60.1776 | 64.1098 | -60.2509 | -60.3836 | -60.2646 | -0.082397 | -0.091553 | 0.21973 | 0.19684 | -0.15564 | -0.15106 | -0.073242 | -0.068665 | -0.032043 | -0.096131 | 0.068664 | -0.10528 | -0.11902 | -0.23804 | -0.086975 | -0.20599 | 0.27924 | 124.4888 | -0.073242 | 124.2874 | 124.1776 | 124.1226 | 124.0952 | 124.0906 | -124.2691 | -124.2188 | 124.4064 | 124.2554 | 60.0677 | 60.0128
195.9375 | 124.3423 | -60.1456 | 64.0274 | 0.0085801 | -0.0013302 | 0.067051 | 0.062495 | 0.0088484 | -0.010807 | 0.0045452 | -0.024402 | 0.0029002 | 0.068746 | 0.075009 | 0.002387 | 0.011257 | 0.012409 | -0.082397 | 63.9084 | -60.2142 | 64.2334 | -59.9945 | -60.3287 | -60.3516 | -0.07782 | 63.9313 | -60.1776 | 64.1327 | -60.2005 | -60.3287 | -60.2325 | -0.068664 | -0.11902 | 0.20599 | 0.15106 | -0.20599 | -0.1831 | -0.13733 | -0.11444 | -0.032043 | -0.096131 | 0.10528 | -0.054931 | -0.086975 | -0.1831 | -0.054932 | -0.15106 | 0.21973 | 124.4476 | -0.022888 | 124.3103 | 124.1226 | 124.1089 | 124.054 | 124.0768 | -124.2416 | -124.205 | 124.379 | 124.2783 | 60.0632 | 60.0677
196.9688 | 124.2645 | -60.1273 | 64.0411 | 0.054357 | 0.01042 | 0.068119 | 0.064631 | 0.018461 | -0.0043982 | 0.0013402 | -0.16173 | 0.0029002 | 0.069815 | 0.073941 | 0.00025105 | 0.0037801 | -0.01109 | -0.091553 | 63.9267 | -60.2142 | 64.2883 | -59.9167 | -60.2783 | -60.3012 | -0.27924 | 63.9267 | -60.2463 | 64.064 | -60.2463 | -60.4019 | -60.2737 | -0.086975 | -0.11444 | 0.24719 | 0.21057 | -0.17395 | -0.15106 | -0.086975 | -0.064087 | -0.11902 | -0.11444 | 0.022888 | -0.11902 | -0.14649 | -0.27466 | -0.027466 | -0.15564 | 0.29755 | 124.5026 | 0 | 124.3103 | 124.1409 | 124.173 | 124.054 | 124.054 | -124.2554 | -124.2874 | 124.4156 | 124.1913 | 60.0357 | 59.848
197.9375 | 124.3744 | -60.1273 | 63.9999 | 0.069615 | 0.012556 | 0.058506 | 0.068904 | 0.0088484 | 0.010556 | 0.0013402 | -0.03966 | -0.00030381 | 0.076223 | 0.0686 | -0.006157 | 0.015529 | -0.016431 | -0.086975 | 63.8947 | -60.2142 | 64.1968 | -60.022 | -60.3699 | -60.3745 | -0.086975 | 63.9038 | -60.1822 | 64.1876 | -60.173 | -60.2829 | -60.1959 | -0.086975 | -0.10529 | 0.19684 | 0.10528 | -0.24719 | -0.24262 | -0.16022 | -0.15564 | -0.054932 | -0.09613 | 0.18768 | -0.045777 | -0.068665 | -0.15564 | -0.013733 | -0.10071 | 0.19226 | 124.411 | 0.009155 | 124.3698 | 124.1089 | 124.086 | 124.0219 | 124.0311 | -124.2142 | -124.1821 | 124.324 | 124.3149 | 60.0403 | 60.0403
198.9688 | 124.3149 | -60.1364 | 64.0228 | 0.13065 | 0.00080677 | 0.058506 | 0.08813 | -0.0050366 | 0.0030788 | 0.00027221 | -0.024402 | 0.0029002 | 0.065542 | 0.067532 | 0.003456 | 0.0069851 | 0.0038644 | -0.036621 | 63.8992 | -60.2463 | 64.2563 | -59.9854 | -60.3149 | -60.2829 | -0.15106 | 63.9542 | -60.1868 | 64.1006 | -60.2646 | -60.3607 | -60.26 | -0.10986 | -0.1236 | 0.23346 | 0.15106 | -0.14648 | -0.17853 | -0.036621 | -0.068664 | -0.050354 | -0.068664 | 0.07782 | -0.12817 | -0.1236 | -0.2243 | -0.073242 | -0.17395 | 0.26093 | 124.5026 | -0.077819 | 124.2874 | 124.1455 | 124.1409 | 124.0356 | 124.0906 | -124.2691 | -124.2096 | 124.3927 | 124.2371 | 60.0998 | 59.9854
199.9375 | 124.4247 | -60.1089 | 64.032 | 0.19169 | 0.0082828 | 0.060642 | 0.055018 | 0.0024404 | 0.0094878 | -0.0018638 | 0.26551 | -0.0045758 | 0.074087 | 0.060055 | -0.002953 | 0.0091211 | -0.013226 | 0.018311 | 63.8947 | -60.173 | 64.1556 | -60.054 | -60.4065 | -60.4156 | 0.036621 | 63.913 | -60.1501 | 64.2059 | -60.0998 | -60.2097 | -60.141 | -0.064087 | -0.13733 | 0.1236 | 0.054932 | -0.3067 | -0.29755 | -0.24261 | -0.23346 | -0.041198 | -0.11902 | 0.17395 | 0.009156 | -0.032043 | -0.10071 | 0.009155 | -0.05951 | 0.11902 | 124.3286 | 0.050354 | 124.3561 | 124.0677 | 124.0631 | 124.0036 | 124.0219 | -124.205 | -124.1821 | 124.2645 | 124.3149 | 60.1273 | 60.1456
200.9688 | 124.3835 | -60.1227 | 64.0045 | 0.084874 | 0.0082828 | 0.05637 | 0.067836 | 0.0067124 | -0.02042 | 0.0066812 | -0.024402 | -0.0024398 | 0.067678 | 0.060055 | -0.007226 | 0.0027121 | -0.0057486 | -0.082397 | 63.8992 | -60.2097 | 64.1876 | -60.0266 | -60.3561 | -60.3745 | -0.068665 | 63.9175 | -60.1501 | 64.1602 | -60.1685 | -60.2737 | -60.2005 | -0.086975 | -0.10529 | 0.1831 | 0.096131 | -0.25177 | -0.23346 | -0.16479 | -0.14648 | -0.027465 | -0.086975 | 0.15564 | -0.045776 | -0.077819 | -0.15106 | -0.050354 | -0.1236 | 0.18311 | 124.3973 | -0.018311 | 124.3103 | 124.1089 | 124.0677 | 124.0219 | 124.0402 | -124.2142 | -124.1547 | 124.3103 | 124.2828 | 60.0403 | 60.054
201.9375 | 124.2645 | -60.1227 | 64.0366 | -0.0066789 | 0.00080677 | 0.070255 | 0.073176 | -0.0029006 | 0.021237 | 0.0034762 | -0.11595 | 0.0018322 | 0.067678 | 0.070737 | -0.008294 | 0.0037801 | -0.0025446 | -0.050354 | 63.9221 | -60.2188 | 64.2609 | -59.9487 | -60.2829 | -60.3149 | -0.17395 | 63.9359 | -60.1959 | 64.0778 | -60.2646 | -60.4019 | -60.2829 | -0.09613 | -0.11444 | 0.2243 | 0.17395 | -0.19226 | -0.16022 | -0.09613 | -0.064087 | -0.073242 | -0.10071 | 0.041199 | -0.14191 | -0.16022 | -0.27924 | -0.086975 | -0.20599 | 0.27008 | 124.4797 | -0.068664 | 124.2737 | 124.1409 | 124.1318 | 124.0448 | 124.0585 | -124.2554 | -124.2325 | 124.3835 | 124.2004 | 60.0723 | 59.9487
202.9844 | 124.3286 | -60.1181 | 64.0686 | 0.37479 | 0.012556 | 0.062778 | 0.067836 | 0.0056444 | -0.021488 | -0.013613 | 0.14344 | -0.00030381 | 0.069815 | 0.057919 | -0.016839 | 0.012325 | -0.0068176 | -0.07782 | 63.9679 | -60.2097 | 64.2838 | -59.9258 | -60.2371 | -60.228 | -0.041199 | 63.9816 | -60.141 | 64.1098 | -60.1868 | -60.3012 | -60.228 | -0.091553 | -0.10071 | 0.21515 | 0.19226 | -0.10986 | -0.11902 | -0.01831 | -0.027466 | -0.022888 | -0.086976 | 0.041198 | -0.068665 | -0.10986 | -0.18311 | -0.086975 | -0.16022 | 0.28381 | 124.4934 | -0.045777 | 124.2508 | 124.1776 | 124.1226 | 124.086 | 124.0997 | -124.2783 | -124.2096 | 124.4019 | 124.2279 | 60.0403 | 60.0769
203.9375 | 124.3057 | -60.173 | 64.0549 | -0.021937 | 0.0050788 | 0.067051 | 0.072108 | 0.0077804 | 0.0020108 | 0.0013402 | -0.054919 | 0.0093092 | 0.074087 | 0.034421 | -0.005089 | 0.0069851 | 0.0017274 | -0.041199 | 63.9313 | -60.2097 | 64.2609 | -59.9716 | -60.2783 | -60.3287 | -0.14191 | 63.945 | -60.1822 | 64.0915 | -60.2509 | -60.3745 | -60.2646 | -0.036621 | -0.1236 | 0.20599 | 0.20142 | -0.15564 | -0.10529 | -0.11902 | -0.068664 | -0.009155 | -0.10986 | 0.036621 | -0.077819 | -0.091552 | -0.20142 | -0.082397 | -0.19226 | 0.23804 | 124.4705 | -0.068664 | 124.2737 | 124.1409 | 124.1272 | 124.1043 | 124.118 | -124.2645 | -124.2371 | 124.4339 | 124.2645 | 60.1318 | 60.0311
204.9688 | 124.3286 | -60.0952 | 64.0686 | 0.023839 | 0.0050788 | 0.064915 | 0.073176 | 0.018461 | 0.0041468 | -0.0093408 | 0.097669 | -0.00030381 | 0.069815 | 0.071805 | -0.005089 | 0.0080531 | 0.01134 | 0.027466 | 63.9725 | -60.1547 | 64.2563 | -59.9121 | -60.2921 | -60.2692 | -0.045776 | 63.9862 | -60.1456 | 64.1464 | -60.1776 | -60.3012 | -60.2188 | -0.059509 | -0.096131 | 0.18768 | 0.18311 | -0.17395 | -0.19684 | -0.11444 | -0.13733 | -0.050354 | -0.082398 | 0.077819 | -0.082397 | -0.1236 | -0.20599 | -0.073242 | -0.15564 | 0.24262 | 124.411 | -0.032043 | 124.292 | 124.1272 | 124.1318 | 124.0677 | 124.0814 | -124.2233 | -124.2142 | 124.3515 | 124.2416 | 60.1227 | 60.0494
205.9375 | 124.3378 | -60.1593 | 64.0274 | 0.10013 | 0.011488 | 0.064915 | 0.069972 | 0.0088484 | -0.0065342 | -0.0061368 | -0.03966 | 0.0061052 | 0.076223 | 0.035489 | -0.002953 | 0.0027121 | 0.0038644 | -0.068665 | 63.9221 | -60.2463 | 64.2471 | -59.9716 | -60.3104 | -60.3149 | -0.13275 | 63.9496 | -60.1776 | 64.1052 | -60.2417 | -60.3653 | -60.2509 | -0.086975 | -0.10529 | 0.21973 | 0.18768 | -0.15564 | -0.15106 | -0.068664 | -0.064087 | -0.01831 | -0.07782 | 0.07782 | -0.082397 | -0.091552 | -0.20599 | -0.073242 | -0.18768 | 0.27466 | 124.4934 | -0.064087 | 124.2828 | 124.1684 | 124.1272 | 124.0814 | 124.1089 | -124.2737 | -124.205 | 124.4064 | 124.2645 | 60.0906 | 60.0266
206.9531 | 124.2462 | -60.1318 | 64.0778 | 0.20695 | -0.010943 | 0.062778 | 0.055018 | -0.0029006 | 0.0030788 | 0.0024082 | 0.28077 | -0.0024398 | 0.067678 | 0.062192 | -0.002953 | -0.00049194 | -0.0068176 | 0.013733 | 63.945 | -60.1685 | 64.27 | -59.935 | -60.2783 | -60.26 | -0.027466 | 63.9999 | -60.141 | 64.1006 | -60.3287 | -60.4111 | -60.2417 | -0.036621 | -0.13275 | 0.19226 | 0.19684 | -0.12817 | -0.14648 | -0.091553 | -0.10986 | -0.009155 | -0.07782 | 0.022888 | -0.19684 | -0.10986 | -0.27924 | -0.10071 | -0.27008 | 0.23346 | 124.4385 | -0.18768 | 124.2416 | 124.1135 | 124.1409 | 124.0768 | 124.1318 | -124.2462 | -124.2188 | 124.4019 | 124.2325 | 60.1456 | 60.1044
207.9375 | 124.3195 | -60.1318 | 64.0366 | 0.17643 | 0.0040108 | 0.057438 | 0.067836 | -0.0029006 | -0.012943 | -0.0050688 | -0.054919 | 0.0018322 | 0.064474 | 0.056851 | -0.005089 | 0.0069851 | 0.010272 | -0.086975 | 63.9359 | -60.2325 | 64.2426 | -59.967 | -60.3058 | -60.3378 | -0.11444 | 63.9633 | -60.1868 | 64.1144 | -60.2463 | -60.3561 | -60.2371 | -0.10071 | -0.10071 | 0.20599 | 0.16479 | -0.20599 | -0.17395 | -0.10529 | -0.073242 | -0.054932 | -0.073242 | 0.07782 | -0.11444 | -0.10529 | -0.2243 | -0.050354 | -0.16937 | 0.2655 | 124.4751 | -0.059509 | 124.3011 | 124.1684 | 124.1501 | 124.0677 | 124.0952 | -124.2691 | -124.2233 | 124.3744 | 124.2462 | 60.0449 | 60.0174
208.9688 | 124.3332 | -60.1089 | 64.064 | 0.14591 | 0.00080677 | 0.053165 | 0.066768 | 0.0099164 | -0.02042 | -0.0061368 | 0.11293 | -0.0024398 | 0.075155 | 0.06326 | -0.009362 | 0.013393 | -0.01109 | 0.036621 | 63.9175 | -60.1913 | 64.238 | -59.9854 | -60.3241 | -60.3058 | -0.004578 | 63.9633 | -60.141 | 64.1602 | -60.1639 | -60.2921 | -60.2051 | -0.082397 | -0.14648 | 0.17395 | 0.1236 | -0.19684 | -0.21515 | -0.11444 | -0.13275 | -0.032043 | -0.10071 | 0.09613 | -0.054931 | -0.09613 | -0.18311 | -0.064087 | -0.15106 | 0.20599 | 124.4293 | -0.022888 | 124.3011 | 124.1089 | 124.1043 | 124.0265 | 124.0723 | -124.2554 | -124.205 | 124.3469 | 124.2691 | 60.1456 | 60.1044
209.9375 | 124.3286 | -60.1089 | 64.0182 | 0.14591 | 0.0018748 | 0.059574 | 0.059291 | 0.0045764 | -0.00012524 | -0.0061368 | 0.11293 | 0.00076419 | 0.079428 | 0.051511 | -0.016839 | 0.015529 | -0.012158 | -0.086975 | 63.8992 | -60.1959 | 64.2288 | -59.9716 | -60.3058 | -60.3424 | -0.11444 | 63.9542 | -60.1822 | 64.1281 | -60.2097 | -60.3333 | -60.2417 | -0.086975 | -0.11902 | 0.21057 | 0.13733 | -0.23346 | -0.19684 | -0.14648 | -0.10986 | -0.073242 | -0.064087 | 0.10986 | -0.10071 | -0.13275 | -0.2243 | -0.059509 | -0.15106 | 0.2243 | 124.4247 | -0.027466 | 124.3103 | 124.0952 | 124.1364 | 124.0082 | 124.0631 | -124.2142 | -124.2004 | 124.3378 | 124.2371 | 60.022 | 59.9945
210.9688 | 124.3515 | -60.1089 | 64.0823 | 0.14591 | 0.012556 | 0.068119 | 0.064631 | -0.0061046 | 0.016964 | -0.01575 | 0.021375 | 0.0018322 | 0.069815 | 0.08035 | 0.001319 | 0.0016441 | -0.0025446 | -0.086975 | 63.9267 | -60.2097 | 64.2654 | -59.9442 | -60.2692 | -60.2692 | -0.15564 | 63.9679 | -60.1913 | 64.2654 | -60.6171 | -60.5209 | -60.1135 | -0.10071 | -0.15564 | 0.18311 | 0.16479 | -0.16022 | -0.16022 | -0.059509 | -0.059509 | -0.082397 | -0.11444 | 0.18311 | -0.50812 | -0.004577 | -0.41199 | 0.07782 | -0.32959 | 0.2655 | 124.4751 | -0.42572 | 124.4568 | 124.1364 | 124.1592 | 124.0356 | 124.0768 | -124.292 | -124.2737 | 124.3744 | 124.3744 | 60.022 | 59.9533
211.9375 | 124.2966 | -60.141 | 64.0411 | 0.14591 | 0.0072148 | 0.068119 | 0.065699 | 0.020598 | -0.0011942 | 0.0013402 | 0.0061157 | 0.01465 | 0.076223 | 0.062192 | 0.001319 | 0.0069851 | -0.012158 | -0.004578 | 63.9313 | -60.1959 | 64.2197 | -59.9899 | -60.3287 | -60.3104 | -0.045776 | 63.9633 | -60.141 | 64.119 | -60.2005 | -60.3333 | -60.2417 | -0.054932 | -0.10986 | 0.17853 | 0.15106 | -0.16937 | -0.18768 | -0.11444 | -0.13275 | 0 | -0.07782 | 0.07782 | -0.059509 | -0.10071 | -0.19226 | -0.10071 | -0.19226 | 0.20599 | 124.4156 | -0.059509 | 124.2599 | 124.1272 | 124.1043 | 124.0723 | 124.1043 | -124.2371 | -124.1821 | 124.3607 | 124.2599 | 60.1364 | 60.0952
212.9375 | 124.2783 | -60.141 | 64.0457 | 0.023839 | -0.0023982 | 0.062778 | 0.067836 | 0.02487 | -0.0022622 | -0.0072048 | -0.0091433 | -0.0013718 | 0.078359 | 0.051511 | 0.009864 | 0.0069851 | 0.010272 | -0.09613 | 63.9267 | -60.2005 | 64.1968 | -60.1456 | -60.5804 | -60.1501 | -0.16479 | 63.9542 | -60.173 | 64.0869 | -60.2463 | -60.3516 | -60.2509 | -0.059509 | -0.11902 | 0.15106 | -0.004578 | -0.009155 | -0.43945 | 0.050354 | -0.37994 | -0.032044 | -0.091552 | 0.041199 | -0.10529 | -0.10986 | -0.21057 | -0.077819 | -0.17853 | 0.054931 | 124.3973 | -0.073242 | 124.2599 | 124.1272 | 124.1272 | 124.0677 | 124.0952 | -124.2462 | -124.2188 | 124.3378 | 124.2279 | 60.0449 | 59.9762
213.9531 | 124.3881 | -60.0861 | 64.0411 | 0.10013 | -0.0045342 | 0.064915 | 0.047541 | -0.0029006 | -0.0097382 | 0.012021 | 0.4181 | 0.00076419 | 0.067678 | 0.036557 | 0.007728 | 0.0069851 | -0.0036126 | 0.082397 | 63.9084 | -60.1318 | 64.1281 | -60.0677 | -60.4019 | -60.3882 | 0.068665 | 63.9587 | -60.1181 | 64.1739 | -60.1135 | -60.2188 | -60.1685 | -0.045776 | -0.13275 | 0.086975 | 0.018311 | -0.30212 | -0.31586 | -0.25635 | -0.27008 | -0.032043 | -0.082398 | 0.13275 | -0.027465 | -0.082397 | -0.13275 | -0.050354 | -0.10071 | 0.064087 | 124.2599 | 0.004578 | 124.292 | 124.0402 | 124.0768 | 123.9944 | 124.0448 | -124.173 | -124.1592 | 124.2142 | 124.2599 | 60.1685 | 60.1547
214.9375 | 124.3103 | -60.1135 | 64.0594 | 0.069615 | 0.0029428 | 0.053165 | 0.066768 | 0.0013714 | -0.021488 | -0.014682 | 0.067151 | 0.0039692 | 0.060202 | 0.0686 | 0.00025105 | -0.0026279 | 0.0006594 | 0.009155 | 63.9221 | -60.173 | 64.2242 | -59.9899 | -60.2966 | -60.3287 | -0.064087 | 63.9725 | -60.1456 | 64.0915 | -60.2234 | -60.3424 | -60.26 | -0.05951 | -0.13733 | 0.16479 | 0.1236 | -0.21515 | -0.18311 | -0.15564 | -0.1236 | -0.032044 | -0.086975 | 0.032044 | -0.10986 | -0.14648 | -0.22888 | -0.11444 | -0.19684 | 0.18311 | 124.3973 | -0.07782 | 124.2371 | 124.0952 | 124.118 | 124.0356 | 124.086 | -124.2325 | -124.205 | 124.3378 | 124.205 | 60.1227 | 60.0494
215.9375 | 124.3423 | -60.1044 | 64.0503 | 0.20695 | -0.0034662 | 0.064915 | 0.073176 | 0.0056444 | -0.015079 | 0.0013402 | 0.21974 | 0.0029002 | 0.065542 | 0.047238 | 0.004524 | 0.0069851 | -0.0078856 | 0.032043 | 63.913 | -60.1913 | 64.2197 | -60.0037 | -60.3287 | -60.3973 | 0.013733 | 63.9359 | -60.1456 | 64.1968 | -60.1501 | -60.26 | -60.173 | -0.086975 | -0.13733 | 0.16937 | 0.10071 | -0.29297 | -0.2243 | -0.20599 | -0.13733 | -0.041199 | -0.11444 | 0.14648 | -0.045776 | -0.068665 | -0.15564 | -0.027466 | -0.11444 | 0.18768 | 124.411 | -0.004577 | 124.3423 | 124.1043 | 124.0814 | 124.0173 | 124.0402 | -124.2416 | -124.1959 | 124.324 | 124.3011 | 60.1364 | 60.1181
216.9375 | 124.3195 | -60.1181 | 64.032 | 0.084874 | 0.01042 | 0.065983 | 0.063563 | 0.022734 | -0.0033302 | 0.0034762 | -0.0091433 | 0.0093092 | 0.063406 | 0.045102 | -0.002953 | 0.0016441 | 0.025226 | 0.045776 | 63.9542 | -60.1593 | 64.1968 | -60.0082 | -60.3333 | -60.3104 | -0.027466 | 63.9679 | -60.1547 | 64.1281 | -60.1868 | -60.3378 | -60.2234 | -0.041199 | -0.077819 | 0.16479 | 0.10986 | -0.19226 | -0.21515 | -0.15106 | -0.17395 | -0.036621 | -0.064086 | 0.096131 | -0.068665 | -0.10529 | -0.21973 | -0.068665 | -0.18311 | 0.15106 | 124.3561 | -0.032044 | 124.2828 | 124.1135 | 124.1226 | 124.0723 | 124.086 | -124.1913 | -124.1867 | 124.3149 | 124.2462 | 60.1639 | 60.0906
217.9375 | 124.3515 | -60.1181 | 64.064 | 0.20695 | -0.0077382 | 0.062778 | 0.07104 | -0.0093096 | 0.011624 | -0.017886 | 0.08241 | 0.010377 | 0.062338 | 0.057919 | -0.01043 | 0.0048481 | -0.023907 | 0.050354 | 63.9496 | -60.173 | 64.2059 | -59.9899 | -60.3104 | -60.3149 | 0.027466 | 63.9542 | -60.141 | 64.1556 | -60.1501 | -60.3058 | -60.2051 | -0.054932 | -0.11444 | 0.14191 | 0.12817 | -0.19684 | -0.19226 | -0.14191 | -0.13733 | -0.022888 | -0.10986 | 0.091553 | -0.032043 | -0.086975 | -0.18768 | -0.064087 | -0.16479 | 0.18311 | 124.379 | -0.009155 | 124.2966 | 124.1226 | 124.0952 | 124.0677 | 124.0723 | -124.2371 | -124.205 | 124.324 | 124.2737 | 60.1685 | 60.1456
218.9375 | 124.3423 | -60.1135 | 64.032 | 0.11539 | -0.00026223 | 0.064915 | 0.069972 | 0.012053 | -0.0086702 | -0.0093408 | 0.08241 | 0.013582 | 0.064474 | 0.064328 | -0.006157 | 0.012325 | -0.0036126 | 0.032043 | 63.9221 | -60.1913 | 64.1876 | -59.9808 | -60.2966 | -60.3333 | 0.050354 | 63.9679 | -60.141 | 64.1464 | -60.1913 | -60.3058 | -60.2188 | -0.07782 | -0.10986 | 0.15564 | 0.13275 | -0.21973 | -0.18311 | -0.14191 | -0.10529 | -0.027466 | -0.064086 | 0.11444 | -0.07782 | -0.10529 | -0.19226 | -0.07782 | -0.16479 | 0.21057 | 124.379 | -0.050354 | 124.2874 | 124.1135 | 124.1089 | 124.0356 | 124.0814 | -124.2233 | -124.173 | 124.3011 | 124.2599 | 60.1456 | 60.1639
219.9375 | 124.411 | -60.1181 | 63.9954 | 0.28324 | 0.0093518 | 0.060642 | 0.076381 | -0.0093096 | -0.0065342 | -0.0072048 | 0.20448 | -0.010985 | 0.071951 | 0.065396 | 0.001319 | 0.012325 | -0.021771 | 0.045776 | 63.8992 | -60.141 | 64.0823 | -60.1501 | -60.4477 | -60.4523 | 0.022888 | 63.8947 | -60.1456 | 64.1876 | -60.1456 | -60.2463 | -60.141 | -0.022888 | -0.09613 | 0.086975 | -0.032043 | -0.33417 | -0.32959 | -0.31128 | -0.3067 | -0.027466 | -0.10071 | 0.19226 | -0.027466 | -0.022888 | -0.12817 | 0.004578 | -0.10071 | -0.009155 | 124.2233 | 0 | 124.3332 | 124.0402 | 124.0402 | 124.0173 | 124.0128 | -124.1364 | -124.1409 | 124.2004 | 124.3057 | 60.1639 | 60.141
220.9375 | 124.2874 | -60.1547 | 64.0457 | 0.10013 | 0.0082828 | 0.063847 | 0.072108 | -0.0039686 | -0.0076022 | -0.0039998 | 0.097669 | 0.0018322 | 0.068746 | 0.086758 | -0.00081695 | 0.0016441 | -0.016431 | -0.036621 | 63.9175 | -60.1913 | 64.2471 | -59.9716 | -60.3149 | -60.3012 | -0.10071 | 63.9542 | -60.1456 | 64.0823 | -60.2737 | -60.4156 | -60.2829 | -0.036621 | -0.12817 | 0.20142 | 0.18311 | -0.14648 | -0.16022 | -0.10986 | -0.1236 | 0.009155 | -0.091552 | 0.036621 | -0.11902 | -0.12817 | -0.26093 | -0.13733 | -0.27008 | 0.21973 | 124.4385 | -0.12817 | 124.2279 | 124.1089 | 124.0997 | 124.0723 | 124.1089 | -124.2371 | -124.1913 | 124.4019 | 124.2371 | 60.1181 | 60.054
221.9375 | 124.3378 | -60.1181 | 64.0823 | 0.13065 | 0.0029428 | 0.052097 | 0.067836 | 0.013121 | -0.0043982 | 0.0045452 | 0.12819 | 0.0018322 | 0.06661 | 0.045102 | -0.007226 | 0.015529 | 0.0049324 | 0.027466 | 63.9725 | -60.173 | 64.2609 | -59.9304 | -60.2966 | -60.26 | -0.032043 | 64.0045 | -60.1364 | 64.1327 | -60.1685 | -60.3012 | -60.2051 | -0.054932 | -0.10986 | 0.17853 | 0.18768 | -0.14191 | -0.17853 | -0.086975 | -0.1236 | -0.018311 | -0.077819 | 0.050354 | -0.050354 | -0.086975 | -0.18311 | -0.068664 | -0.16479 | 0.24262 | 124.4339 | -0.032043 | 124.2691 | 124.1455 | 124.1409 | 124.0906 | 124.1226 | -124.2554 | -124.2188 | 124.379 | 124.2508 | 60.1456 | 60.0861
222.9375 | 124.3149 | -60.0952 | 64.0823 | 0.20695 | -0.0034662 | 0.057438 | 0.064631 | 0.013121 | 0.0062828 | 0.014158 | 0.18922 | 0.0018322 | 0.086904 | 0.0087855 | 0.002387 | 0.0016441 | 0.013477 | 0.032043 | 63.9725 | -60.1959 | 64.27 | -59.9258 | -60.2783 | -60.2737 | -0.032043 | 63.9862 | -60.1501 | 64.1144 | -60.1776 | -60.2966 | -60.2188 | -0.10071 | -0.10986 | 0.18768 | 0.16937 | -0.17853 | -0.1831 | -0.07782 | -0.082397 | -0.054931 | -0.09613 | 0.032044 | -0.082397 | -0.1236 | -0.20142 | -0.068665 | -0.14648 | 0.27008 | 124.4659 | -0.027466 | 124.2645 | 124.1684 | 124.1364 | 124.0677 | 124.0814 | -124.2783 | -124.2325 | 124.3652 | 124.2096 | 60.1273 | 60.0632
223.9375 | 124.3332 | -60.1044 | 64.0366 | 0.10013 | -0.0056022 | 0.058506 | 0.067836 | 0.0056444 | 0.0020108 | -0.0018638 | 0.11293 | 0.00076419 | 0.081564 | 0.064328 | -0.008294 | 0.0069851 | -0.0046806 | 0.036621 | 63.9313 | -60.1776 | 64.1739 | -60.0357 | -60.3149 | -60.347 | 0.027466 | 63.9862 | -60.1501 | 64.151 | -60.1364 | -60.2875 | -60.2142 | -0.073242 | -0.10529 | 0.13733 | 0.068664 | -0.24261 | -0.21057 | -0.16937 | -0.13733 | -0.045776 | -0.050354 | 0.11444 | -0.032044 | -0.10986 | -0.18311 | -0.064087 | -0.13733 | 0.14191 | 124.3515 | 0.013732 | 124.3011 | 124.1089 | 124.1364 | 124.0356 | 124.0906 | -124.2142 | -124.1867 | 124.2783 | 124.2554 | 60.141 | 60.1318
224.9375 | 124.3103 | -60.1318 | 64.0549 | 0.17643 | -0.00026223 | 0.064915 | 0.055018 | -0.0029006 | 0.0052148 | 0.017362 | 0.1587 | -0.0067128 | 0.065542 | 0.078213 | 0.001319 | 0.015529 | 0.013477 | -0.086975 | 63.9175 | -60.2234 | 64.1052 | -60.2417 | -60.3973 | -60.1227 | -0.19226 | 63.9587 | -60.1776 | 64.0823 | -60.2646 | -60.3836 | -60.26 | -0.091553 | -0.13733 | 0.050354 | -0.10986 | 0.009155 | -0.2655 | 0.10071 | -0.17395 | -0.045776 | -0.096131 | 0.027465 | -0.13275 | -0.12817 | -0.25177 | -0.082398 | -0.20599 | -0.01831 | 124.3286 | -0.086975 | 124.2599 | 124.1409 | 124.1364 | 124.0494 | 124.0906 | -124.2783 | -124.2325 | 124.2371 | 124.2142 | 60.0449 | 59.9396
225.9375 | 124.3332 | -60.1181 | 64.0732 | 0.17643 | 0.0040108 | 0.062778 | 0.066768 | -0.023195 | 0.0020108 | 0.0024082 | 0.097669 | 0.0071732 | 0.092245 | 0.036557 | 0.001319 | 0.0059161 | -0.0025446 | 0.036621 | 63.9542 | -60.1822 | 64.2563 | -59.9304 | -60.2921 | -60.26 | -0.032043 | 63.9954 | -60.1501 | 64.1327 | -60.1639 | -60.2829 | -60.2005 | -0.064087 | -0.11902 | 0.18311 | 0.18768 | -0.14191 | -0.17395 | -0.07782 | -0.10986 | -0.032043 | -0.07782 | 0.059509 | -0.045776 | -0.082397 | -0.1648 | -0.050354 | -0.13275 | 0.25177 | 124.4385 | -0.013733 | 124.2828 | 124.1364 | 124.1455 | 124.0723 | 124.1135 | -124.2554 | -124.2233 | 124.3744 | 124.2508 | 60.1547 | 60.0861
226.9375 | 124.3378 | -60.1181 | 64.0549 | 0.16117 | 0.0029428 | 0.070255 | 0.062495 | -0.010378 | -0.0076022 | -0.0093408 | 0.11293 | 0.0061052 | 0.067678 | 0.061124 | -0.014702 | 0.013393 | -0.0089536 | 0.036621 | 63.9313 | -60.1776 | 64.2151 | -60.0128 | -60.3287 | -60.3241 | 0.018311 | 63.9587 | -60.1547 | 64.151 | -60.1685 | -60.3058 | -60.2234 | -0.059509 | -0.1236 | 0.16022 | 0.10529 | -0.20599 | -0.21057 | -0.14648 | -0.15106 | -0.036621 | -0.096131 | 0.09613 | -0.050354 | -0.10529 | -0.18768 | -0.068665 | -0.15106 | 0.1648 | 124.3927 | -0.013733 | 124.3057 | 124.1089 | 124.1135 | 124.0494 | 124.0768 | -124.2325 | -124.2096 | 124.3332 | 124.2691 | 60.1547 | 60.1364
227.9375 | 124.3195 | -60.1227 | 64.0457 | 0.17643 | 0.0082828 | 0.052097 | 0.07104 | 0.015257 | -0.0043982 | -0.013613 | 0.067151 | 0.012514 | 0.063406 | 0.06326 | -0.007226 | 0.014461 | -0.0089536 | -0.036621 | 63.9038 | -60.1959 | 64.1922 | -60.0357 | -60.3653 | -60.3241 | 0.022888 | 63.9725 | -60.1318 | 64.1418 | -60.173 | -60.2921 | -60.2051 | -0.073242 | -0.14191 | 0.14648 | 0.086975 | -0.20142 | -0.24261 | -0.12817 | -0.16937 | -0.009155 | -0.073242 | 0.096131 | -0.050354 | -0.082397 | -0.16937 | -0.073242 | -0.16022 | 0.16022 | 124.3881 | -0.041199 | 124.2737 | 124.0997 | 124.1043 | 124.0265 | 124.0952 | -124.2416 | -124.1776 | 124.3149 | 124.2645 | 60.0861 | 60.1456
228.9375 | 124.3286 | -60.0861 | 64.0732 | 0.14591 | -0.0045342 | 0.064915 | 0.07104 | 0.0013714 | -0.021488 | -0.0039998 | 0.20448 | 0.017854 | 0.071951 | 0.048306 | -0.004021 | 0.0080531 | 0.014545 | 0.050354 | 63.9404 | -60.1593 | 64.2197 | -59.9762 | -60.3287 | -60.3012 | 0.022888 | 63.9633 | -60.1227 | 64.151 | -60.1501 | -60.2783 | -60.2005 | -0.073242 | -0.13275 | 0.14648 | 0.10986 | -0.21515 | -0.24261 | -0.14191 | -0.16937 | -0.036621 | -0.10986 | 0.07782 | -0.064086 | -0.11444 | -0.19226 | -0.077819 | -0.15564 | 0.18311 | 124.379 | -0.027465 | 124.2737 | 124.0997 | 124.086 | 124.0265 | 124.0494 | -124.2325 | -124.1959 | 124.3057 | 124.2371 | 60.1364 | 60.1089
229.9688 | 124.2828 | -60.1364 | 64.0503 | 0.19169 | 0.0072148 | 0.060642 | 0.077449 | -0.0039686 | -0.015079 | 0.0024082 | 0.12819 | 0.010377 | 0.079428 | 0.070737 | -0.009362 | 0.017666 | -0.016431 | 0.018311 | 63.913 | -60.2005 | 64.2334 | -59.9945 | -60.3195 | -60.3195 | -0.009155 | 63.9542 | -60.1547 | 64.1006 | -60.2005 | -60.3333 | -60.2371 | -0.064086 | -0.13733 | 0.1831 | 0.14191 | -0.1831 | -0.1831 | -0.11902 | -0.11902 | -0.01831 | -0.09613 | 0.050354 | -0.064086 | -0.10071 | -0.19684 | -0.082398 | -0.17853 | 0.20599 | 124.4339 | -0.045776 | 124.2554 | 124.1135 | 124.1089 | 124.0494 | 124.0906 | -124.2508 | -124.205 | 124.3698 | 124.2371 | 60.1547 | 60.1273
230.9375 | 124.3149 | -60.1227 | 64.0686 | 0.069615 | 0.00080677 | 0.068119 | 0.07104 | 0.010984 | 0.0062828 | -0.010409 | 0.14344 | 0.0061052 | 0.086904 | 0.056851 | -0.009362 | 0.011257 | 0.010272 | 0.041199 | 63.9313 | -60.1868 | 64.2105 | -59.9899 | -60.3378 | -60.3287 | -0.022888 | 63.9267 | -60.1501 | 64.1464 | -60.1501 | -60.3424 | -60.2005 | -0.064087 | -0.13733 | 0.14191 | 0.13275 | -0.20599 | -0.21515 | -0.14191 | -0.15106 | -0.027465 | -0.14191 | 0.077819 | -0.027465 | -0.077819 | -0.21973 | -0.050354 | -0.19226 | 0.19684 | 124.3973 | 0 | 124.2966 | 124.118 | 124.0768 | 124.054 | 124.0494 | -124.2554 | -124.2188 | 124.3332 | 124.2691 | 60.1639 | 60.0998
231.9375 | 124.3515 | -60.1181 | 64.0594 | 0.13065 | 0.00080677 | 0.059574 | 0.076381 | 0.016325 | -0.0086702 | -0.0050688 | 0.1587 | 0.0071732 | 0.075155 | 0.052579 | -0.001885 | 0.013393 | 0.0006594 | 0.041199 | 63.9313 | -60.1639 | 64.1968 | -59.9991 | -60.3241 | -60.3058 | 0.013733 | 63.9587 | -60.141 | 64.0869 | -60.141 | -60.2371 | -60.2097 | -0.045776 | -0.12817 | 0.13733 | 0.11902 | -0.18768 | -0.20599 | -0.14191 | -0.16022 | -0.022888 | -0.10071 | 0.027466 | -0.022888 | -0.091553 | -0.11902 | -0.068665 | -0.096131 | 0.16479 | 124.3607 | 0 | 124.2279 | 124.0952 | 124.0997 | 124.0494 | 124.0768 | -124.2233 | -124.2004 | 124.3149 | 124.205 | 60.1593 | 60.1318
232.9375 | 124.3149 | -60.1227 | 64.064 | 0.11539 | 0.0029428 | 0.063847 | 0.073176 | 0.0045764 | -0.017215 | -0.0018638 | 0.067151 | -0.00030381 | 0.056997 | 0.036557 | -0.005089 | 0.0016441 | -0.020703 | 0.036621 | 63.913 | -60.1639 | 64.2059 | -60.0128 | -60.3378 | -60.3378 | -0.009155 | 63.9725 | -60.141 | 64.1418 | -60.1913 | -60.3241 | -60.2188 | -0.041198 | -0.15106 | 0.14191 | 0.10986 | -0.21515 | -0.21515 | -0.17395 | -0.17395 | -0.01831 | -0.091553 | 0.07782 | -0.068664 | -0.09613 | -0.20142 | -0.07782 | -0.18311 | 0.15106 | 124.3698 | -0.050354 | 124.2828 | 124.0768 | 124.1135 | 124.0356 | 124.0952 | -124.2279 | -124.205 | 124.3286 | 124.2645 | 60.1593 | 60.1135
233.9375 | 124.2874 | -60.1181 | 64.0411 | 0.11539 | -0.00026223 | 0.060642 | 0.064631 | -0.01465 | -0.019351 | -0.0039998 | 0.051892 | 0.0093092 | 0.063406 | 0.037625 | -0.00081695 | 0.0016441 | -0.0004086 | -0.018311 | 63.913 | -60.173 | 64.2105 | -59.9991 | -60.2966 | -60.2966 | -0.073242 | 63.9404 | -60.173 | 64.0823 | -60.228 | -60.3836 | -60.2692 | -0.054932 | -0.12817 | 0.16937 | 0.11902 | -0.17853 | -0.17853 | -0.1236 | -0.1236 | -0.054932 | -0.10071 | 0.041198 | -0.10986 | -0.15106 | -0.2655 | -0.09613 | -0.21057 | 0.17395 | 124.3835 | -0.054931 | 124.2554 | 124.086 | 124.1135 | 124.0311 | 124.0585 | -124.2142 | -124.2142 | 124.3286 | 124.2004 | 60.0998 | 60.0449
234.9375 | 124.2828 | -60.1501 | 64.0366 | 0.17643 | 0.0061468 | 0.064915 | 0.064631 | 0.012053 | -0.014011 | 0.00027221 | 0.1587 | 0.0082412 | 0.071951 | 0.049374 | -0.008294 | 0.013393 | 0.020953 | -0.032043 | 63.8992 | -60.1913 | 64.2334 | -59.9854 | -60.3241 | -60.3104 | -0.082397 | 63.9816 | -60.1227 | 64.0869 | -60.2142 | -60.3745 | -60.26 | -0.041199 | -0.13733 | 0.19684 | 0.16479 | -0.16022 | -0.17395 | -0.11902 | -0.13275 | 0.027465 | -0.054932 | 0.050354 | -0.064087 | -0.10986 | -0.22431 | -0.13733 | -0.25177 | 0.20599 | 124.4247 | -0.091552 | 124.2096 | 124.0906 | 124.1043 | 124.0494 | 124.1318 | -124.2279 | -124.1592 | 124.3835 | 124.2371 | 60.1181 | 60.0677
235.9375 | 124.3378 | -60.0998 | 64.0778 | 0.2222 | 0.0093518 | 0.059574 | 0.062495 | 0.017393 | 0.03085 | -0.012545 | 0.26551 | 0.017854 | 0.079428 | 0.038693 | -0.009362 | 0.0080531 | -0.017499 | 0.032043 | 63.9496 | -60.1639 | 64.2288 | -59.9167 | -60.3012 | -60.2829 | -0.041199 | 63.9771 | -60.1456 | 64.1373 | -60.1776 | -60.2875 | -60.2142 | -0.064087 | -0.12817 | 0.15106 | 0.1831 | -0.18311 | -0.20142 | -0.11902 | -0.13733 | -0.045777 | -0.10071 | 0.059509 | -0.07782 | -0.11444 | -0.18768 | -0.068664 | -0.14191 | 0.24719 | 124.3927 | -0.032043 | 124.2828 | 124.1135 | 124.1226 | 124.0494 | 124.0768 | -124.2416 | -124.2233 | 124.3286 | 124.2371 | 60.1318 | 60.0586
236.9375 | 124.3378 | -60.0998 | 64.0594 | 0.10013 | 0.00080677 | 0.059574 | 0.063563 | 0.0056444 | -0.00012524 | 0.00027221 | 0.20448 | 0.0050372 | 0.062338 | 0.055783 | -0.011498 | 0.015529 | -0.0014766 | 0.054932 | 63.9175 | -60.173 | 64.1693 | -60.0128 | -60.3561 | -60.3104 | 0.004578 | 63.9771 | -60.1273 | 64.1418 | -60.1822 | -60.3058 | -60.2188 | -0.073243 | -0.14191 | 0.10986 | 0.086975 | -0.21057 | -0.25635 | -0.13733 | -0.18311 | -0.027466 | -0.082397 | 0.082398 | -0.082398 | -0.11902 | -0.20599 | -0.091553 | -0.17853 | 0.16022 | 124.3423 | -0.054932 | 124.2691 | 124.0906 | 124.1043 | 124.0173 | 124.0768 | -124.2325 | -124.1867 | 124.2691 | 124.2416 | 60.1547 | 60.1044
237.9375 | 124.3881 | -60.1227 | 64.0778 | 0.13065 | 0.0018748 | 0.067051 | 0.075312 | 0.0099164 | -0.0076022 | 0.010953 | 0.08241 | 0.0039692 | 0.069815 | 0.060055 | -0.004021 | 0.010189 | -0.0089536 | 0.050354 | 63.9359 | -60.1776 | 64.2105 | -59.9899 | -60.3241 | -60.3241 | 0.022888 | 63.9496 | -60.1364 | 64.1327 | -60.2142 | -60.4248 | -60.3012 | -0.054931 | -0.14191 | 0.13275 | 0.13275 | -0.20142 | -0.20142 | -0.14648 | -0.14648 | -0.013733 | -0.12817 | 0.054931 | -0.091552 | -0.17853 | -0.30212 | -0.16479 | -0.28839 | 0.18768 | 124.3881 | -0.077819 | 124.2691 | 124.1135 | 124.086 | 124.0585 | 124.0723 | -124.2554 | -124.2142 | 124.3332 | 124.2554 | 60.173 | 60.1456
238.9375 | 124.3469 | -60.1273 | 64.0549 | 0.10013 | 0.0061468 | 0.060642 | 0.07104 | -0.0082416 | -0.015079 | -0.00079579 | 0.12819 | 0.013582 | 0.075155 | 0.053647 | -0.009362 | 0.0048481 | 0.012409 | 0.054932 | 63.9084 | -60.1822 | 64.2059 | -60.0128 | -60.3195 | -60.3195 | 0.009155 | 63.9542 | -60.1364 | 64.151 | -60.1181 | -60.5209 | -60.2921 | -0.054932 | -0.14649 | 0.15106 | 0.11444 | -0.19226 | -0.19226 | -0.13733 | -0.13733 | -0.009156 | -0.10071 | 0.09613 | 0.009155 | -0.1648 | -0.39368 | -0.15564 | -0.38452 | 0.16937 | 124.3881 | 0.018311 | 124.2874 | 124.0906 | 124.0906 | 124.0356 | 124.0814 | -124.2371 | -124.1913 | 124.3332 | 124.2783 | 60.1822 | 60.1364
239.9375 | 124.3744 | -60.1273 | 63.9908 | 0.054357 | 0.0061468 | 0.060642 | 0.068904 | -0.0029006 | 0.019101 | 0.0056132 | 0.21974 | 0.0050372 | 0.081564 | 0.036557 | -0.014702 | 0.0048481 | -0.0078856 | -0.082397 | 63.9175 | -60.2051 | 64.1693 | -60.0403 | -60.3745 | -60.3836 | -0.050354 | 63.9084 | -60.1547 | 64.1785 | -60.1776 | -60.2783 | -60.1639 | -0.07782 | -0.073242 | 0.17853 | 0.086975 | -0.25635 | -0.24719 | -0.17853 | -0.16937 | -0.027466 | -0.082398 | 0.18768 | -0.050354 | -0.036621 | -0.15106 | -0.009155 | -0.1236 | 0.16479 | 124.3744 | -0.022888 | 124.3332 | 124.1226 | 124.0631 | 124.0448 | 124.0356 | -124.1959 | -124.1455 | 124.2966 | 124.3057 | 60.0449 | 60.0769
240.9375 | 124.3011 | -60.1318 | 64.064 | 0.14591 | -0.010943 | 0.068119 | 0.064631 | 0.0077804 | 0.00094276 | -0.0061368 | 0.036633 | 0.013582 | 0.062338 | 0.078213 | 0.001319 | 0.0048481 | 0.0027964 | -0.004578 | 63.9038 | -60.1868 | 64.2151 | -59.9808 | -60.3149 | -60.2921 | -0.086975 | 63.9496 | -60.1822 | 64.0915 | -60.2234 | -60.3561 | -60.2509 | -0.054932 | -0.16022 | 0.15106 | 0.15106 | -0.16022 | -0.1831 | -0.10529 | -0.12817 | -0.050354 | -0.11444 | 0.027466 | -0.091553 | -0.11902 | -0.2243 | -0.068664 | -0.17395 | 0.20599 | 124.4019 | -0.041199 | 124.2737 | 124.0906 | 124.1318 | 124.0356 | 124.0814 | -124.2508 | -124.2462 | 124.3469 | 124.2233 | 60.1273 | 60.0449
241.9375 | 124.2691 | -60.141 | 64.0549 | 0.084874 | 0.0040108 | 0.063847 | 0.072108 | 0.0035084 | -0.0033302 | -0.0082728 | 0.08241 | -0.0035078 | 0.076223 | 0.040829 | -0.005089 | 0.0037801 | -0.0046806 | -0.064087 | 63.9084 | -60.2005 | 64.27 | -59.9213 | -60.2921 | -60.2875 | -0.16479 | 63.9725 | -60.1959 | 63.9954 | -60.5484 | -60.1593 | -60.0677 | -0.059509 | -0.14649 | 0.21515 | 0.21973 | -0.14648 | -0.15106 | -0.086976 | -0.091553 | -0.054932 | -0.082398 | -0.05951 | -0.40741 | 0.073242 | -0.018311 | 0.12817 | 0.036621 | 0.27923 | 124.4705 | -0.35248 | 124.1913 | 124.1089 | 124.1684 | 124.0494 | 124.1135 | -124.2554 | -124.2508 | 124.411 | 124.1364 | 60.0769 | 59.9762
242.9375 | 124.3103 | -60.1089 | 64.0457 | 0.11539 | 0.0072148 | 0.068119 | 0.064631 | 0.0088484 | 0.0062828 | 0.015226 | 0.12819 | 0.0018322 | 0.069815 | 0.051511 | -0.001885 | 0.00057606 | -0.0004086 | 0.032043 | 63.9496 | -60.1913 | 64.2105 | -59.9899 | -60.3287 | -60.3149 | 0.004578 | 63.9633 | -60.1364 | 64.1464 | -60.141 | -60.2966 | -60.1959 | -0.082397 | -0.09613 | 0.16479 | 0.11902 | -0.20599 | -0.21973 | -0.1236 | -0.13733 | -0.027466 | -0.082397 | 0.10071 | -0.032043 | -0.086975 | -0.18768 | -0.059509 | -0.16022 | 0.20142 | 124.4019 | -0.004577 | 124.2828 | 124.1409 | 124.0997 | 124.0585 | 124.0723 | -124.2371 | -124.1821 | 124.3195 | 124.2554 | 60.141 | 60.1135
243.9375 | 124.3515 | -60.1227 | 64.0549 | 0.084874 | 0.0018748 | 0.063847 | 0.065699 | -0.0029006 | -0.010807 | -0.0039998 | 0.17396 | 0.012514 | 0.06127 | 0.050442 | -0.011498 | 0.0048481 | -0.0004086 | -0.12817 | 63.913 | -60.1822 | 64.1876 | -60.0449 | -60.3561 | -60.3104 | 0.022888 | 63.9679 | -60.1181 | 64.1327 | -60.1776 | -60.2921 | -60.1959 | -0.059509 | -0.14191 | 0.13275 | 0.07782 | -0.18768 | -0.23346 | -0.12817 | -0.17395 | 0.004578 | -0.086975 | 0.077819 | -0.054931 | -0.073242 | -0.16937 | -0.07782 | -0.17395 | 0.13733 | 124.3698 | -0.059509 | 124.2508 | 124.0952 | 124.086 | 124.0356 | 124.0906 | -124.2371 | -124.173 | 124.3103 | 124.2554 | 59.9945 | 60.1456
244.9688 | 124.3378 | -60.1044 | 64.0503 | 0.11539 | -0.0034662 | 0.06171 | 0.065699 | 0.017393 | -0.016147 | -0.014682 | 0.051892 | 0.00076419 | 0.076223 | 0.06326 | -0.002953 | 0.0059161 | 0.0027964 | 0.045776 | 63.945 | -60.1685 | 64.2288 | -59.9762 | -60.3104 | -60.3012 | 0.004578 | 63.9542 | -60.1639 | 64.1373 | -60.1501 | -60.2875 | -60.1913 | -0.064087 | -0.10529 | 0.17853 | 0.12817 | -0.19684 | -0.20599 | -0.13275 | -0.14191 | -0.059509 | -0.09613 | 0.086975 | -0.045776 | -0.086975 | -0.18311 | -0.027466 | -0.1236 | 0.19226 | 124.3973 | 0.013733 | 124.3011 | 124.1135 | 124.118 | 124.0494 | 124.0585 | -124.2188 | -124.2142 | 124.3332 | 124.2416 | 60.1501 | 60.1089
245.9375 | 124.3149 | -60.1181 | 64.0457 | 0.13065 | -0.019488 | 0.089481 | 0.056086 | 0.0099164 | -0.011875 | -0.010409 | 0.11293 | -0.0013718 | 0.084768 | 0.037625 | 0.002387 | 0.0048481 | 0.024158 | -0.41657 | 63.8626 | -60.26 | 64.2242 | -59.9258 | -60.2829 | -60.3012 | -0.1236 | 63.9313 | -60.1547 | 64.0594 | -60.2509 | -60.3699 | -60.2509 | -0.14191 | -0.18311 | 0.17853 | 0.19226 | -0.18311 | -0.1648 | -0.041198 | -0.022888 | -0.036621 | -0.11444 | 0.013733 | -0.13275 | -0.13275 | -0.25177 | -0.09613 | -0.21515 | 0.33417 | 124.4843 | -0.09613 | 124.2142 | 124.1226 | 124.086 | 123.9807 | 124.0494 | -124.3057 | -124.2004 | 124.3423 | 124.1776 | 59.7015 | 59.9945
246.9375 | 124.2783 | -60.1089 | 64.0274 | 0.16117 | 0.0018748 | 0.067051 | 0.065699 | -0.0093096 | 0.0052148 | -0.0082728 | -0.03966 | 0.0050372 | 0.060202 | 0.04617 | 0.00025105 | 0.00057606 | -0.0068176 | 0 | 63.9267 | -60.1685 | 64.2105 | -59.9899 | -60.3195 | -60.3104 | -0.045776 | 63.9542 | -60.141 | 64.1006 | -60.2005 | -60.3287 | -60.2463 | -0.059509 | -0.10071 | 0.1831 | 0.11902 | -0.20142 | -0.21057 | -0.14191 | -0.15106 | -0.032043 | -0.073242 | 0.073242 | -0.091552 | -0.13733 | -0.21973 | -0.10529 | -0.18768 | 0.17853 | 124.379 | -0.059509 | 124.2416 | 124.0952 | 124.0952 | 124.0356 | 124.0631 | -124.1959 | -124.1684 | 124.3195 | 124.2096 | 60.1089 | 60.0632
247.9375 | 124.2874 | -60.1089 | 64.0274 | 0.20695 | 0.0029428 | 0.062778 | 0.067836 | 0.013121 | 0.0030788 | 0.00027221 | 0.067151 | 0.010377 | 0.06661 | 0.061124 | -0.006157 | 0.0069851 | -0.029248 | -0.009155 | 63.9267 | -60.2051 | 64.2105 | -59.9854 | -60.3149 | -60.3241 | -0.018311 | 63.9404 | -60.1456 | 64.119 | -60.1868 | -60.3287 | -60.2188 | -0.09613 | -0.10071 | 0.1831 | 0.1236 | -0.21515 | -0.20599 | -0.11902 | -0.10986 | -0.036621 | -0.086975 | 0.091553 | -0.07782 | -0.10986 | -0.21973 | -0.073242 | -0.1831 | 0.21973 | 124.4156 | -0.041199 | 124.2645 | 124.1318 | 124.086 | 124.0356 | 124.0494 | -124.2325 | -124.173 | 124.3195 | 124.2279 | 60.0998 | 60.0906
248.9375 | 124.3195 | -60.1089 | 64.0594 | 0.11539 | 0.0050788 | 0.070255 | 0.068904 | -0.00076463 | 0.0041468 | -0.0082728 | 0.0061157 | 0.00076419 | 0.065542 | 0.049374 | -0.001885 | -0.0026279 | 0.0017274 | 0.032043 | 63.945 | -60.1593 | 64.1922 | -59.9945 | -60.347 | -60.3104 | -0.009155 | 63.945 | -60.1547 | 64.119 | -60.1913 | -60.3241 | -60.2051 | -0.050354 | -0.11444 | 0.13275 | 0.11444 | -0.20142 | -0.23804 | -0.15106 | -0.18768 | -0.045776 | -0.11444 | 0.05951 | -0.082397 | -0.09613 | -0.21515 | -0.050354 | -0.16937 | 0.16479 | 124.3515 | -0.036621 | 124.2737 | 124.1043 | 124.0997 | 124.054 | 124.054 | -124.2188 | -124.2142 | 124.3011 | 124.2279 | 60.141 | 60.0998
249.9844 | 124.3195 | -60.1135 | 64.0823 | 0.20695 | 0.011488 | 0.064915 | 0.073176 | 0.00030337 | -0.0022622 | 0.015226 | 0.14344 | 0.0039692 | 0.076223 | 0.052579 | -0.007226 | -0.0036969 | -0.0046806 | 0.018311 | 63.9221 | -60.173 | 64.2517 | -59.9121 | -60.2554 | -60.2646 | -0.032043 | 63.9771 | -60.1318 | 64.1327 | -60.1593 | -60.2875 | -60.1959 | -0.05951 | -0.16022 | 0.16937 | 0.20142 | -0.15106 | -0.14191 | -0.091552 | -0.082397 | -0.018311 | -0.10528 | 0.050354 | -0.045777 | -0.082398 | -0.17395 | -0.064087 | -0.15564 | 0.26093 | 124.4247 | -0.027466 | 124.2645 | 124.0952 | 124.1089 | 124.0356 | 124.0906 | -124.2554 | -124.2142 | 124.3652 | 124.2462 | 60.1318 | 60.0815
250.9375 | 124.2874 | -60.0998 | 64.0594 | 0.23746 | -0.0023982 | 0.063847 | 0.061427 | -0.0071726 | -0.012943 | -0.0050688 | 0.21974 | -0.00030381 | 0.070883 | 0.048306 | -0.002953 | 0.0069851 | 0.0017274 | 0.050354 | 63.945 | -60.1776 | 64.2151 | -59.9899 | -60.3241 | -60.2966 | 0 | 63.945 | -60.1456 | 64.1373 | -60.141 | -60.2829 | -60.1776 | -0.07782 | -0.11444 | 0.15564 | 0.10986 | -0.19684 | -0.22431 | -0.11902 | -0.14648 | -0.045777 | -0.11444 | 0.07782 | -0.041199 | -0.07782 | -0.18311 | -0.032043 | -0.13733 | 0.18768 | 124.3927 | 0.004578 | 124.2828 | 124.1226 | 124.0906 | 124.0448 | 124.0448 | -124.2371 | -124.205 | 124.3149 | 124.2371 | 60.1501 | 60.0998
251.9375 | 124.3286 | -60.0998 | 64.0686 | 0.069615 | 0.0029428 | 0.051029 | 0.064631 | 0.0067124 | 0.0052148 | 0.0034762 | 0.11293 | 0.0050372 | 0.065542 | 0.041897 | 0.00666 | 0.016598 | -0.0089536 | 0.018311 | 63.9359 | -60.1639 | 64.183 | -60.0174 | -60.3378 | -60.3195 | 0.013733 | 63.9542 | -60.1364 | 64.1281 | -60.2005 | -60.2966 | -60.1547 | -0.064087 | -0.13275 | 0.11444 | 0.082397 | -0.21973 | -0.23804 | -0.15564 | -0.17395 | -0.036622 | -0.11444 | 0.059509 | -0.10071 | -0.054932 | -0.19684 | -0.01831 | -0.16022 | 0.14648 | 124.3469 | -0.064086 | 124.2645 | 124.0997 | 124.0906 | 124.0356 | 124.054 | -124.2325 | -124.205 | 124.2828 | 124.2279 | 60.1181 | 60.1135
252.9375 | 124.2599 | -60.1227 | 64.0137 | 0.054357 | 0.0029428 | 0.065983 | 0.075312 | 0.0067124 | 0.0094878 | -0.0072048 | 0.14344 | 0.0082412 | 0.082632 | 0.02374 | 0.005592 | 0.0069851 | -0.015362 | -0.036621 | 63.9221 | -60.2188 | 64.238 | -59.9396 | -60.2875 | -60.2829 | -0.15564 | 63.9542 | -60.1685 | 64.0594 | -60.26 | -60.3836 | -60.2829 | -0.09613 | -0.091553 | 0.2243 | 0.18311 | -0.16022 | -0.16479 | -0.064087 | -0.068665 | -0.045776 | -0.059509 | 0.045776 | -0.13733 | -0.16022 | -0.26093 | -0.11444 | -0.21515 | 0.27924 | 124.4568 | -0.091553 | 124.2279 | 124.1409 | 124.1226 | 124.0448 | 124.0768 | -124.2325 | -124.1821 | 124.3607 | 124.1821 | 60.0861 | 59.967
253.9375 | 124.2599 | -60.1364 | 64.0503 | 0.13065 | -0.0045342 | 0.060642 | 0.063563 | 0.027006 | 0.0052148 | -0.011477 | 0.12819 | 0.011445 | 0.073019 | 0.052579 | 0.001319 | 0.0037801 | 0.0092044 | -0.10071 | 63.8947 | -60.2325 | 64.2609 | -59.9075 | -60.2921 | -60.2921 | -0.15564 | 63.9313 | -60.1822 | 64.0778 | -60.2646 | -60.3836 | -60.26 | -0.09613 | -0.15564 | 0.21057 | 0.22888 | -0.15564 | -0.15564 | -0.059509 | -0.059509 | -0.045776 | -0.11902 | 0.027466 | -0.12817 | -0.1236 | -0.24719 | -0.07782 | -0.20142 | 0.32501 | 124.4934 | -0.082397 | 124.2599 | 124.1272 | 124.1135 | 124.0311 | 124.0677 | -124.2828 | -124.2325 | 124.3973 | 124.2142 | 60.0357 | 59.9808
254.9375 | 124.3011 | -60.1318 | 64.0457 | 0.14591 | -0.0045342 | 0.058506 | 0.07104 | 0.014189 | 0.014828 | 0.0098852 | -0.03966 | -0.0024398 | 0.081564 | 0.036557 | 0.004524 | 0.0091211 | -0.018567 | -0.091553 | 63.9038 | -60.2142 | 64.2563 | -59.9121 | -60.2737 | -60.2921 | -0.1831 | 63.9679 | -60.1822 | 64.0732 | -60.2646 | -60.3836 | -60.26 | -0.082397 | -0.14191 | 0.21057 | 0.21973 | -0.16022 | -0.14191 | -0.07782 | -0.05951 | -0.050354 | -0.077819 | 0.027466 | -0.13275 | -0.12817 | -0.25177 | -0.07782 | -0.20142 | 0.30212 | 124.4705 | -0.082397 | 124.2554 | 124.118 | 124.1501 | 124.0356 | 124.0997 | -124.2599 | -124.2279 | 124.3881 | 124.205 | 60.0403 | 59.9487
255.9375 | 124.3149 | -60.1044 | 64.0366 | 0.023839 | -0.0013302 | 0.065983 | 0.067836 | 0.015257 | -0.0043982 | 0.012021 | 0.12819 | 0.00076419 | 0.071951 | 0.10064 | -0.01043 | 0.012325 | 0.0060004 | 0.022888 | 63.9084 | -60.1822 | 64.1922 | -59.9899 | -60.3241 | -60.3195 | 0 | 63.9496 | -60.1456 | 64.151 | -60.1639 | -60.2875 | -60.2005 | -0.07782 | -0.12817 | 0.15564 | 0.11444 | -0.21515 | -0.21973 | -0.13733 | -0.14191 | -0.041199 | -0.086975 | 0.11444 | -0.059509 | -0.09613 | -0.18311 | -0.054931 | -0.14191 | 0.19226 | 124.3744 | -0.01831 | 124.2966 | 124.0906 | 124.0952 | 124.0128 | 124.054 | -124.2188 | -124.1821 | 124.2966 | 124.2554 | 60.1273 | 60.1044
256.9375 | 124.3423 | -60.1181 | 64.0594 | 0.16117 | -0.0056022 | 0.072392 | 0.066768 | 0.02487 | 0.0084198 | -0.0093408 | 0.11293 | 0.010377 | 0.079428 | 0.064328 | -0.006157 | 0.012325 | -0.018567 | 0.036621 | 63.9359 | -60.1685 | 64.2151 | -60.0082 | -60.3516 | -60.3058 | 0.013733 | 63.9633 | -60.1318 | 64.1418 | -60.1456 | -60.2737 | -60.1868 | -0.050354 | -0.1236 | 0.15564 | 0.10986 | -0.18768 | -0.23346 | -0.13733 | -0.18311 | -0.013733 | -0.09613 | 0.082398 | -0.027466 | -0.068665 | -0.15564 | -0.054932 | -0.14191 | 0.16022 | 124.3835 | -0.013733 | 124.2737 | 124.1043 | 124.0952 | 124.054 | 124.0814 | -124.2279 | -124.1913 | 124.3332 | 124.2599 | 60.1547 | 60.1318
257.9375 | 124.3286 | -60.1135 | 64.0549 | 0.17643 | -0.0045342 | 0.068119 | 0.057155 | 0.0077804 | -0.012943 | -0.0050688 | 0.14344 | 0.0071732 | 0.076223 | 0.076077 | -0.013634 | 0.014461 | -0.0014766 | 0.022888 | 63.9359 | -60.1868 | 64.1968 | -60.0037 | -60.3424 | -60.3241 | 0 | 63.9587 | -60.1501 | 64.0915 | -60.1593 | -60.2921 | -60.1822 | -0.073243 | -0.11902 | 0.14191 | 0.10986 | -0.21057 | -0.22888 | -0.13733 | -0.15564 | -0.036621 | -0.096131 | 0.036621 | -0.045777 | -0.068665 | -0.17853 | -0.032044 | -0.14191 | 0.18311 | 124.3835 | -0.009156 | 124.2416 | 124.1226 | 124.1089 | 124.0494 | 124.0723 | -124.2416 | -124.205 | 124.3103 | 124.205 | 60.1364 | 60.1135
258.9375 | 124.324 | -60.0998 | 64.0686 | 0.17643 | 0.00080677 | 0.068119 | 0.066768 | 0.0024404 | 0.0041468 | -0.010409 | 0.18922 | 0.0050372 | 0.064474 | 0.051511 | -0.004021 | 0.0091211 | -0.0025446 | 0.032043 | 63.9404 | -60.1639 | 64.2242 | -59.9716 | -60.3149 | -60.2921 | 0.013733 | 63.9542 | -60.1227 | 64.1418 | -60.1639 | -60.2692 | -60.1868 | -0.064087 | -0.12817 | 0.15564 | 0.12817 | -0.19226 | -0.21515 | -0.12817 | -0.15106 | -0.022889 | -0.11444 | 0.073242 | -0.064087 | -0.086976 | -0.16937 | -0.064087 | -0.14648 | 0.19226 | 124.3881 | -0.041198 | 124.2645 | 124.1043 | 124.0768 | 124.0402 | 124.054 | -124.2325 | -124.1913 | 124.324 | 124.2416 | 60.1318 | 60.1135
259.9844 | 124.324 | -60.1135 | 64.0732 | 0.11539 | 0.0082828 | 0.059574 | 0.057155 | 0.016325 | 0.01376 | 0.00027221 | 0.32655 | 0.013582 | 0.074087 | 0.041897 | -0.01043 | 0.017666 | -0.0068176 | 0 | 63.9587 | -60.173 | 64.2563 | -59.9167 | -60.2783 | -60.26 | -0.027466 | 64.0091 | -60.1135 | 64.0549 | -60.2554 | -60.3973 | -60.2325 | -0.05951 | -0.11444 | 0.18311 | 0.19684 | -0.14648 | -0.16479 | -0.086975 | -0.10529 | 0 | -0.064087 | -0.01831 | -0.14191 | -0.11902 | -0.28381 | -0.11902 | -0.28381 | 0.25635 | 124.4293 | -0.14191 | 124.1684 | 124.1318 | 124.1226 | 124.0723 | 124.1226 | -124.2462 | -124.1867 | 124.3698 | 124.1684 | 60.1135 | 60.0861
260.9375 | 124.3561 | -60.0952 | 64.032 | 0.14591 | 0.0050788 | 0.06171 | 0.067836 | 0.00030337 | -0.0033302 | -0.0039998 | 0.08241 | 0.01465 | 0.074087 | 0.069668 | -0.012566 | 0.0016441 | -0.0089536 | 0.045776 | 63.9221 | -60.1685 | 64.2242 | -59.9854 | -60.3333 | -60.3058 | 0.013733 | 63.9679 | -60.1318 | 64.1418 | -60.1547 | -60.2783 | -60.1685 | -0.073242 | -0.10986 | 0.19226 | 0.10986 | -0.21057 | -0.23804 | -0.13733 | -0.1648 | -0.036621 | -0.064086 | 0.10986 | -0.059509 | -0.073242 | -0.1831 | -0.036621 | -0.14648 | 0.1831 | 124.3927 | -0.022888 | 124.2737 | 124.0906 | 124.0997 | 124.0173 | 124.0631 | -124.2004 | -124.1638 | 124.3195 | 124.2371 | 60.141 | 60.1089
261.9375 | 124.2554 | -60.0998 | 64.0549 | 0.19169 | -0.0077382 | 0.063847 | 0.072108 | -0.0071726 | -0.0086702 | 0.0066812 | 0.036633 | 0.010377 | 0.076223 | 0.044034 | 0.005592 | 0.0048481 | -0.0025446 | 0.018311 | 63.9084 | -60.1913 | 64.183 | -59.9991 | -60.3378 | -60.2966 | -0.013733 | 63.9313 | -60.1181 | 64.0869 | -60.2097 | -60.3378 | -60.2051 | -0.091553 | -0.14649 | 0.12817 | 0.10071 | -0.19684 | -0.23804 | -0.10529 | -0.14648 | -0.018311 | -0.1236 | 0.032043 | -0.10986 | -0.10529 | -0.23804 | -0.086975 | -0.21973 | 0.19226 | 124.3744 | -0.091553 | 124.205 | 124.0997 | 124.0494 | 124.0082 | 124.0311 | -124.2462 | -124.173 | 124.2828 | 124.1867 | 60.1181 | 60.0861
262.9375 | 124.324 | -60.0769 | 64.0778 | 0.16117 | -0.0013302 | 0.06171 | 0.079585 | 0.0077804 | -0.0022622 | -0.0029318 | 0.17396 | 0.0050372 | 0.068746 | 0.057919 | -0.008294 | 0.0016441 | 0.012409 | 0.036621 | 63.9404 | -60.1685 | 64.2517 | -59.9442 | -60.2921 | -60.3058 | -0.032043 | 63.9679 | -60.1456 | 64.1235 | -60.1501 | -60.2737 | -60.173 | -0.091553 | -0.13733 | 0.17395 | 0.13275 | -0.22888 | -0.21515 | -0.13733 | -0.1236 | -0.068665 | -0.10986 | 0.045776 | -0.073242 | -0.096131 | -0.19684 | -0.027466 | -0.12817 | 0.2243 | 124.4202 | -0.004577 | 124.2691 | 124.1089 | 124.1135 | 124.0173 | 124.0448 | -124.2462 | -124.2233 | 124.3286 | 124.2004 | 60.1135 | 60.0449
263.9375 | 124.2737 | -60.1135 | 64.0961 | 0.084874 | -0.0098752 | 0.05637 | 0.067836 | 0.012053 | 0.0052148 | 0.00027221 | 0.40284 | 0.010377 | 0.078359 | 0.02908 | -0.007226 | 0.010189 | -0.0025446 | 0.013733 | 63.9496 | -60.141 | 64.2838 | -59.903 | -60.26 | -60.2417 | -0.041199 | 63.9862 | -60.141 | 64.0961 | -60.1959 | -60.2875 | -60.2188 | -0.027466 | -0.14648 | 0.18768 | 0.21057 | -0.12817 | -0.14648 | -0.10071 | -0.11902 | -0.027466 | -0.10986 | 0 | -0.082398 | -0.10529 | -0.17395 | -0.07782 | -0.14648 | 0.23804 | 124.4247 | -0.054932 | 124.2371 | 124.0906 | 124.1272 | 124.0631 | 124.0997 | -124.2371 | -124.2371 | 124.3973 | 124.2096 | 60.1273 | 60.0723
264.9375 | 124.3011 | -60.1181 | 64.0732 | 0.14591 | -0.012011 | 0.057438 | 0.061427 | 0.015257 | 0.0052148 | -0.016818 | 0.235 | -0.0077808 | 0.075155 | 0.052579 | -0.01043 | 0.023006 | 0.01134 | 0.013733 | 63.9496 | -60.1959 | 64.2609 | -59.9121 | -60.2692 | -60.2509 | -0.050354 | 63.9679 | -60.1364 | 64.0594 | -60.2554 | -60.347 | -60.2097 | -0.07782 | -0.1236 | 0.18768 | 0.20599 | -0.13275 | -0.15106 | -0.054931 | -0.073242 | -0.018311 | -0.10529 | -0.013733 | -0.13733 | -0.091553 | -0.22888 | -0.073242 | -0.21057 | 0.28381 | 124.4568 | -0.11902 | 124.1959 | 124.1455 | 124.1043 | 124.0677 | 124.086 | -124.2691 | -124.2096 | 124.379 | 124.1776 | 60.1318 | 60.0677
265.9375 | 124.3286 | -60.0906 | 64.0549 | 0.14591 | 0.0029428 | 0.062778 | 0.064631 | 0.0013714 | -0.0043982 | -0.0061368 | 0.051892 | -0.0067128 | 0.062338 | 0.045102 | -0.011498 | 0.010189 | -0.013226 | 0.045776 | 63.9359 | -60.1547 | 64.2105 | -59.9945 | -60.3149 | -60.3149 | 0.018311 | 63.9679 | -60.1273 | 64.1373 | -60.1547 | -60.2737 | -60.1913 | -0.064087 | -0.11902 | 0.15564 | 0.09613 | -0.2243 | -0.2243 | -0.16022 | -0.16022 | -0.036621 | -0.086975 | 0.082397 | -0.064087 | -0.10071 | -0.18311 | -0.064087 | -0.14649 | 0.16022 | 124.3652 | -0.027466 | 124.2645 | 124.0906 | 124.0952 | 124.0265 | 124.0585 | -124.2096 | -124.1821 | 124.3011 | 124.2279 | 60.1364 | 60.1089
266.9375 | 124.3103 | -60.0815 | 64.0869 | 0.19169 | 0.0040108 | 0.060642 | 0.064631 | -0.0029006 | -0.02042 | 0.00027221 | 0.47914 | -0.0013718 | 0.0837 | 0.065396 | 0.001319 | 0.012325 | 0.0038644 | 0.022888 | 63.9359 | -60.1822 | 64.2654 | -59.9304 | -60.2646 | -60.2692 | -0.09613 | 63.9954 | -60.1456 | 64.1098 | -60.1776 | -60.2875 | -60.2051 | -0.10071 | -0.15106 | 0.17853 | 0.15106 | -0.18768 | -0.1831 | -0.086975 | -0.082397 | -0.064087 | -0.091553 | 0.022888 | -0.09613 | -0.1236 | -0.20599 | -0.059509 | -0.14191 | 0.25177 | 124.4476 | -0.032043 | 124.2554 | 124.118 | 124.1409 | 124.0173 | 124.0768 | -124.2691 | -124.2325 | 124.3469 | 124.1913 | 60.1044 | 59.9854
267.9375 | 124.2691 | -60.1089 | 64.0823 | 0.16117 | -0.0066702 | 0.067051 | 0.065699 | -0.019991 | 0.0094878 | -0.013613 | 0.34181 | -0.0024398 | 0.069815 | 0.022671 | -0.005089 | -0.011173 | -0.016431 | 0.050354 | 63.9359 | -60.1501 | 64.2151 | -59.9167 | -60.2005 | -60.26 | -0.032043 | 63.9725 | -60.141 | 64.1006 | -60.1913 | -60.3012 | -60.2417 | -0.041198 | -0.14648 | 0.13275 | 0.19226 | -0.15106 | -0.091552 | -0.10986 | -0.050354 | -0.032043 | -0.10986 | 0.018311 | -0.082397 | -0.13275 | -0.19226 | -0.10071 | -0.16022 | 0.23346 | 124.3652 | -0.050354 | 124.2416 | 124.086 | 124.1135 | 124.0448 | 124.0814 | -124.2325 | -124.2233 | 124.324 | 124.2096 | 60.1593 | 60.0769
268.9375 | 124.292 | -60.1135 | 64.0869 | 0.11539 | -0.0023982 | 0.059574 | 0.065699 | 0.016325 | -0.015079 | 0.0013402 | 0.21974 | 0.012514 | 0.071951 | 0.099576 | -0.006157 | 0.0091211 | 0.0017274 | 0.15106 | 63.9771 | -60.1318 | 64.27 | -59.8938 | -60.2737 | -60.26 | -0.027466 | 63.9771 | -60.1227 | 64.1144 | -60.1593 | -60.3012 | -60.1913 | -0.018311 | -0.10986 | 0.18311 | 0.21973 | -0.14648 | -0.16022 | -0.12817 | -0.14191 | -0.009156 | -0.10986 | 0.027466 | -0.045777 | -0.07782 | -0.18768 | -0.068664 | -0.17853 | 0.23804 | 124.4019 | -0.036621 | 124.2371 | 124.1089 | 124.0997 | 124.0906 | 124.0906 | -124.2188 | -124.2096 | 124.3835 | 124.2279 | 60.2646 | 60.0861
269.9688 | 124.324 | -60.1044 | 64.0686 | 0.13065 | -0.0023982 | 0.072392 | 0.064631 | 0.022734 | -0.023624 | -0.0093408 | 0.11293 | 0.0061052 | 0.055929 | 0.061124 | -0.005089 | 0.0037801 | -0.0046806 | 0.032043 | 63.9221 | -60.1868 | 64.2288 | -59.9396 | -60.3058 | -60.2829 | 0 | 63.9816 | -60.1227 | 64.1556 | -60.141 | -60.2783 | -60.1685 | -0.082398 | -0.14648 | 0.16022 | 0.1648 | -0.17853 | -0.20142 | -0.09613 | -0.11902 | -0.018311 | -0.086976 | 0.086975 | -0.036621 | -0.064087 | -0.17395 | -0.045776 | -0.15564 | 0.24719 | 124.4156 | -0.01831 | 124.2783 | 124.1089 | 124.1043 | 124.0265 | 124.086 | -124.2554 | -124.1913 | 124.3332 | 124.2599 | 60.1364 | 60.1044
270.9375 | 124.3469 | -60.0815 | 64.0594 | 0.25272 | 0.0082828 | 0.067051 | 0.060359 | 0.0045764 | -0.014011 | -0.012545 | 0.37233 | -0.0056438 | 0.069815 | 0.017331 | -0.002953 | 0.0016441 | -0.0057486 | 0.045776 | 63.9038 | -60.1227 | 64.1373 | -60.0266 | -60.3516 | -60.3516 | 0.064087 | 63.945 | -60.1181 | 64.1556 | -60.1135 | -60.2371 | -60.1685 | -0.041199 | -0.15564 | 0.07782 | 0.054932 | -0.27008 | -0.27008 | -0.22888 | -0.22888 | -0.036621 | -0.11444 | 0.096131 | -0.032043 | -0.086975 | -0.15564 | -0.050354 | -0.11902 | 0.096131 | 124.2599 | 0.004578 | 124.2737 | 124.0265 | 124.0631 | 123.9853 | 124.0265 | -124.1821 | -124.1776 | 124.2188 | 124.2371 | 60.1273 | 60.1456
271.9375 | 124.3378 | -60.0723 | 64.0549 | 0.46634 | 0.0018748 | 0.060642 | 0.062495 | 0.0077804 | -0.018283 | 0.0045452 | 0.31129 | 0.0039692 | 0.079428 | 0.04617 | -0.004021 | 0.014461 | -0.019635 | 0.050354 | 63.9496 | -60.1456 | 64.119 | -60.0632 | -60.3653 | -60.3745 | 0.073242 | 63.945 | -60.1181 | 64.1739 | -60.0998 | -60.2097 | -60.1364 | -0.073242 | -0.10529 | 0.064087 | 0.009156 | -0.30212 | -0.29297 | -0.22888 | -0.21973 | -0.045776 | -0.10986 | 0.11902 | -0.027465 | -0.064087 | -0.13733 | -0.018311 | -0.091553 | 0.082398 | 124.2645 | 0.018311 | 124.292 | 124.0952 | 124.0631 | 124.0219 | 124.0173 | -124.2004 | -124.173 | 124.1913 | 124.2462 | 60.1227 | 60.1456
272.9375 | 124.2737 | -60.0769 | 64.0869 | 0.14591 | -0.0013302 | 0.072392 | 0.062495 | -0.0050366 | 0.0052148 | -0.0018638 | 0.235 | -0.0024398 | 0.079428 | 0.047238 | 0.002387 | -0.0069009 | -0.0014766 | 0.059509 | 63.9084 | -60.1318 | 64.1876 | -59.9945 | -60.3058 | -60.3149 | 0.013733 | 63.9725 | -60.1273 | 64.1006 | -60.1639 | -60.2966 | -60.2142 | -0.054932 | -0.17853 | 0.10071 | 0.082397 | -0.23804 | -0.22888 | -0.1831 | -0.17395 | -0.050354 | -0.11444 | 0.013733 | -0.086975 | -0.13733 | -0.21973 | -0.086975 | -0.16937 | 0.13733 | 124.3195 | -0.036621 | 124.2279 | 124.0402 | 124.0997 | 123.9853 | 124.0494 | -124.2188 | -124.2142 | 124.2645 | 124.1776 | 60.1364 | 60.0906
273.9375 | 124.3057 | -60.1181 | 64.064 | 0.023839 | 0.0029428 | 0.063847 | 0.082789 | 0.0077804 | 0.018033 | -0.0082728 | 0.021375 | 0.022127 | 0.077291 | 0.082486 | -0.01043 | 0.017666 | -0.021771 | -0.091553 | 63.8855 | -60.2234 | 64.2426 | -59.935 | -60.2921 | -60.2921 | -0.12817 | 63.9679 | -60.1685 | 64.1785 | -60.466 | -60.4019 | -60.1044 | -0.10529 | -0.17853 | 0.17853 | 0.1831 | -0.17395 | -0.17395 | -0.068664 | -0.068664 | -0.050354 | -0.09613 | 0.11444 | -0.3479 | 0.013733 | -0.28381 | 0.064087 | -0.23346 | 0.28839 | 124.4659 | -0.29755 | 124.3469 | 124.1089 | 124.1364 | 124.0036 | 124.086 | -124.2874 | -124.2325 | 124.3607 | 124.2966 | 60.0266 | 59.9899
274.9375 | 124.3332 | -60.0998 | 64.0411 | 0.084874 | 0.0050788 | 0.057438 | 0.072108 | 0.0024404 | 0.0084198 | 0.00027221 | 0.097669 | -0.00030381 | 0.070883 | 0.055783 | -0.014702 | 0.0080531 | -0.01109 | 0.050354 | 63.9496 | -60.2005 | 64.2242 | -59.9533 | -60.3012 | -60.2783 | 0.022888 | 63.9725 | -60.1273 | 64.1373 | -60.1227 | -60.2463 | -60.173 | -0.10071 | -0.091553 | 0.1831 | 0.14648 | -0.17853 | -0.20142 | -0.07782 | -0.10071 | -0.027466 | -0.068665 | 0.09613 | -0.022889 | -0.073243 | -0.14648 | -0.045777 | -0.11902 | 0.24719 | 124.4247 | 0.004577 | 124.2645 | 124.1501 | 124.0997 | 124.0494 | 124.0723 | -124.2416 | -124.1684 | 124.324 | 124.2371 | 60.1501 | 60.1227
275.9375 | 124.2737 | -60.0998 | 64.0594 | 0.2222 | 0.0072148 | 0.055302 | 0.068904 | 0.013121 | 0.00094276 | 0.0056132 | 0.17396 | 0.0050372 | 0.06127 | 0.093167 | 0.004524 | 0.0027121 | -0.0014766 | 0.064087 | 63.9633 | -60.1593 | 64.2563 | -59.9167 | -60.2554 | -60.26 | -0.022888 | 63.9908 | -60.141 | 64.1006 | -60.1913 | -60.3104 | -60.2234 | -0.05951 | -0.09613 | 0.19684 | 0.1831 | -0.16022 | -0.15564 | -0.10071 | -0.09613 | -0.041199 | -0.068664 | 0.041199 | -0.091553 | -0.1236 | -0.21057 | -0.082398 | -0.16937 | 0.24261 | 124.4156 | -0.050354 | 124.2416 | 124.1226 | 124.1318 | 124.0631 | 124.0906 | -124.2188 | -124.2004 | 124.3561 | 124.2004 | 60.1639 | 60.0769
276.9375 | 124.2554 | -60.0861 | 64.1052 | 0.13065 | 0.0018748 | 0.058506 | 0.063563 | 0.0024404 | -0.0043982 | -0.0039998 | 0.11293 | -0.00030381 | 0.077291 | 0.062192 | -0.00081695 | -0.00049194 | 0.0060004 | 0.027466 | 63.9359 | -60.1685 | 64.2517 | -59.9167 | -60.2692 | -60.26 | -0.027466 | 63.9954 | -60.1135 | 64.1006 | -60.173 | -60.2875 | -60.2188 | -0.082397 | -0.16937 | 0.14648 | 0.16937 | -0.17395 | -0.1831 | -0.091553 | -0.10071 | -0.027465 | -0.10986 | -0.004578 | -0.086975 | -0.13275 | -0.20142 | -0.10529 | -0.17395 | 0.25177 | 124.4202 | -0.05951 | 124.2142 | 124.1043 | 124.1089 | 124.0219 | 124.0814 | -124.2737 | -124.2188 | 124.3378 | 124.1867 | 60.1135 | 60.0586
277.9375 | 124.2737 | -60.0952 | 64.0778 | 0.16117 | 0.00080677 | 0.054234 | 0.063563 | 0.020598 | -0.0022622 | -0.0072048 | 0.28077 | -0.0099168 | 0.085836 | 0.091031 | -0.006157 | 0.0069851 | -0.015362 | 0.045776 | 63.9359 | -60.1685 | 64.238 | -59.9258 | -60.2646 | -60.2554 | -0.013733 | 63.9679 | -60.1089 | 64.0869 | -60.1776 | -60.2921 | -60.2234 | -0.073242 | -0.14191 | 0.16022 | 0.16937 | -0.16022 | -0.16937 | -0.086975 | -0.09613 | -0.013733 | -0.10986 | 0.009155 | -0.082397 | -0.12817 | -0.19684 | -0.11444 | -0.18311 | 0.24261 | 124.4064 | -0.068664 | 124.1959 | 124.1043 | 124.0768 | 124.0311 | 124.0631 | -124.2462 | -124.1867 | 124.3332 | 124.1821 | 60.141 | 60.0815
278.9375 | 124.2462 | -60.1089 | 64.0778 | 0.11539 | 0.0061468 | 0.067051 | 0.080653 | 0.0056444 | -0.016147 | 0.013089 | -0.054919 | 0.00076419 | 0.076223 | 0.065396 | 0.001319 | 0.0069851 | -0.0025446 | -0.027466 | 63.8855 | -60.1868 | 64.1968 | -59.9579 | -60.2875 | -60.2829 | -0.10071 | 63.945 | -60.1501 | 64.0778 | -60.228 | -60.4019 | -60.2509 | -0.07782 | -0.19226 | 0.11902 | 0.15106 | -0.17395 | -0.17853 | -0.09613 | -0.10071 | -0.041198 | -0.13275 | 0 | -0.11902 | -0.14191 | -0.29297 | -0.10071 | -0.25177 | 0.22888 | 124.3835 | -0.07782 | 124.2279 | 124.0723 | 124.0952 | 123.9944 | 124.054 | -124.2645 | -124.2279 | 124.3057 | 124.1867 | 60.0815 | 60.0082
279.9375 | 124.3149 | -60.0815 | 64.0549 | 0.2222 | 0.0093518 | 0.059574 | 0.067836 | -0.0039686 | 0.0041468 | 0.00027221 | 0.17396 | 0.0061052 | 0.067678 | 0.081418 | -0.002953 | 0.0048481 | -0.010022 | 0.022888 | 63.9587 | -60.1822 | 64.2426 | -59.9167 | -60.2783 | -60.2646 | -0.022888 | 63.9771 | -60.1135 | 64.1327 | -60.1593 | -60.2692 | -60.1685 | -0.10071 | -0.096131 | 0.18768 | 0.16479 | -0.1831 | -0.19684 | -0.082397 | -0.09613 | -0.032043 | -0.07782 | 0.077819 | -0.07782 | -0.086975 | -0.18768 | -0.054932 | -0.15564 | 0.2655 | 124.4247 | -0.045777 | 124.2462 | 124.1409 | 124.0906 | 124.0402 | 124.0585 | -124.2371 | -124.1684 | 124.324 | 124.2142 | 60.1044 | 60.0586
280.9375 | 124.2691 | -60.1227 | 64.0778 | 0.20695 | 0.0018748 | 0.070255 | 0.063563 | 0.0045764 | -0.012943 | -0.00079579 | 0.29603 | 0.011445 | 0.071951 | 0.091031 | -0.001885 | 0.013393 | -0.010022 | 0.032043 | 63.9496 | -60.1639 | 64.2334 | -59.9075 | -60.26 | -60.2417 | -0.027466 | 63.9771 | -60.141 | 64.1006 | -60.1685 | -60.3012 | -60.2234 | -0.041198 | -0.12817 | 0.15564 | 0.21515 | -0.11902 | -0.13733 | -0.07782 | -0.096131 | -0.01831 | -0.10071 | 0.022888 | -0.045776 | -0.10071 | -0.17853 | -0.082398 | -0.16022 | 0.25635 | 124.3973 | -0.027466 | 124.2416 | 124.1135 | 124.118 | 124.0723 | 124.0997 | -124.2416 | -124.2188 | 124.3561 | 124.2233 | 60.1547 | 60.0952
281.9375 | 124.3057 | -60.0861 | 64.0915 | 0.054357 | -0.0077382 | 0.055302 | 0.080653 | 0.0088484 | 0.0062828 | -0.0061368 | 0.036633 | 0.0029002 | 0.063406 | 0.035489 | -0.022179 | 0.013393 | 0.0092044 | 0.027466 | 63.9175 | -60.1959 | 64.2334 | -59.9396 | -60.3012 | -60.2875 | -0.004578 | 63.9771 | -60.1273 | 64.1418 | -60.1456 | -60.2692 | -60.173 | -0.10986 | -0.17395 | 0.14191 | 0.14649 | -0.20142 | -0.21515 | -0.091553 | -0.10529 | -0.041198 | -0.11444 | 0.050354 | -0.059509 | -0.086975 | -0.1831 | -0.045777 | -0.14191 | 0.25635 | 124.4293 | -0.018311 | 124.2691 | 124.1135 | 124.1043 | 124.0036 | 124.0631 | -124.2874 | -124.2188 | 124.3195 | 124.2279 | 60.1135 | 60.0815
282.9688 | 124.2874 | -60.0906 | 64.0869 | 0.084874 | -0.0034662 | 0.063847 | 0.069972 | 0.0067124 | -0.015079 | -0.0029318 | 0.26551 | 0.00076419 | 0.069815 | 0.042966 | -0.001885 | 0.0016441 | 0.0070684 | 0.045776 | 63.9313 | -60.1685 | 64.2471 | -59.9304 | -60.2554 | -60.2554 | -0.041199 | 63.9679 | -60.1044 | 64.1052 | -60.1822 | -60.3104 | -60.2188 | -0.07782 | -0.15564 | 0.16022 | 0.16022 | -0.16479 | -0.16479 | -0.086975 | -0.086975 | -0.013733 | -0.11902 | 0.018311 | -0.091553 | -0.12817 | -0.21973 | -0.11444 | -0.20599 | 0.23804 | 124.4156 | -0.07782 | 124.2096 | 124.0997 | 124.0723 | 124.0219 | 124.0585 | -124.2554 | -124.1913 | 124.3378 | 124.1959 | 60.1364 | 60.0494
283.9375 | 124.3927 | -60.0815 | 63.9954 | 0.023839 | 0.0029428 | 0.07346 | 0.072108 | 0.0067124 | 0.021237 | 0.0045452 | 0.25026 | -0.0035078 | 0.071951 | 0.030148 | -0.017907 | 0.013393 | 0.0049324 | -0.041199 | 63.8672 | -60.1593 | 64.0594 | -60.1135 | -60.4431 | -60.4385 | 0.004578 | 63.8992 | -60.1273 | 64.2929 | -60.0403 | -60.1593 | -60.1318 | -0.07782 | -0.12817 | 0.064087 | -0.032043 | -0.35706 | -0.36163 | -0.27924 | -0.28381 | -0.045776 | -0.09613 | 0.29755 | 0.041199 | -0.050354 | -0.07782 | -0.004578 | -0.032044 | 0.045777 | 124.2188 | 0.086975 | 124.4202 | 124.0265 | 124.0265 | 123.9487 | 123.9807 | -124.1547 | -124.1226 | 124.1409 | 124.3744 | 60.0403 | 60.0861
284.9375 | 124.292 | -60.1135 | 64.064 | 0.28324 | 0.0040108 | 0.063847 | 0.072108 | -0.0029006 | -0.0086702 | 0.010953 | -0.085437 | -0.0056438 | 0.065542 | 0.032284 | -0.013634 | 0.013393 | -0.010022 | -0.013733 | 63.9221 | -60.2005 | 64.2059 | -59.967 | -60.2921 | -60.2966 | -0.041199 | 63.9542 | -60.1318 | 64.119 | -60.1959 | -60.2921 | -60.1913 | -0.086975 | -0.14191 | 0.14191 | 0.14648 | -0.18311 | -0.17853 | -0.096131 | -0.091553 | -0.018311 | -0.10986 | 0.054932 | -0.082398 | -0.07782 | -0.17853 | -0.059509 | -0.16022 | 0.23346 | 124.4064 | -0.064087 | 124.2508 | 124.1226 | 124.086 | 124.0356 | 124.0677 | -124.2645 | -124.1959 | 124.3195 | 124.2325 | 60.0998 | 60.0723
285.9375 | 124.324 | -60.0998 | 64.0503 | 0.20695 | -0.00026223 | 0.054234 | 0.069972 | 0.0056444 | -0.0097382 | 0.0013402 | 0.14344 | -0.0099168 | 0.0837 | 0.06326 | -0.011498 | 0.00057606 | -0.0004086 | 0.013733 | 63.9542 | -60.1685 | 64.2746 | -59.9716 | -60.3561 | -60.2875 | -0.050354 | 63.9725 | -60.1501 | 64.1006 | -60.2005 | -60.2829 | -60.2188 | -0.068665 | -0.09613 | 0.2243 | 0.12817 | -0.18768 | -0.25635 | -0.11902 | -0.18768 | -0.050354 | -0.07782 | 0.050354 | -0.10071 | -0.11902 | -0.18311 | -0.068665 | -0.13275 | 0.19684 | 124.4431 | -0.050354 | 124.2508 | 124.1226 | 124.1226 | 124.054 | 124.0723 | -124.2188 | -124.2004 | 124.3744 | 124.2004 | 60.1135 | 60.0494
286.9375 | 124.3103 | -60.0815 | 64.0778 | 0.11539 | -0.0013302 | 0.067051 | 0.072108 | -0.0029006 | -0.0065342 | -0.022158 | 0.051892 | 0.0029002 | 0.0837 | 0.033353 | -0.004021 | 0.0069851 | -0.0057486 | 0.041199 | 63.9313 | -60.2005 | 64.1785 | -59.9945 | -60.3241 | -60.3058 | 0.018311 | 63.9587 | -60.1273 | 64.1556 | -60.1364 | -60.2692 | -60.1776 | -0.11902 | -0.14648 | 0.10071 | 0.086975 | -0.2243 | -0.24262 | -0.10529 | -0.1236 | -0.045776 | -0.11902 | 0.07782 | -0.054932 | -0.09613 | -0.18768 | -0.050354 | -0.14191 | 0.20599 | 124.379 | -0.009156 | 124.2828 | 124.1318 | 124.086 | 124.0128 | 124.0402 | -124.2783 | -124.205 | 124.2599 | 124.2371 | 60.1227 | 60.0998
287.9375 | 124.3057 | -60.1135 | 64.0778 | 0.17643 | -0.0013302 | 0.05637 | 0.072108 | 0.015257 | 0.0030788 | 0.0066812 | 0.036633 | 0.0039692 | 0.068746 | 0.051511 | 0.002387 | 0.013393 | 0.0006594 | 0.018311 | 63.9542 | -60.1685 | 64.2151 | -59.9121 | -60.2554 | -60.2417 | -0.045776 | 64.0091 | -60.1273 | 64.1006 | -60.1868 | -60.3104 | -60.2051 | -0.054932 | -0.1236 | 0.13733 | 0.20142 | -0.12817 | -0.14191 | -0.073242 | -0.086975 | -0.013733 | -0.068665 | 0.022888 | -0.073243 | -0.091553 | -0.19684 | -0.07782 | -0.18311 | 0.25635 | 124.3835 | -0.05951 | 124.2279 | 124.1226 | 124.1364 | 124.0677 | 124.1226 | -124.2462 | -124.205 | 124.3286 | 124.2142 | 60.1318 | 60.0677
288.9375 | 124.4019 | -60.0952 | 63.9816 | 0.084874 | 0.0061468 | 0.067051 | 0.065699 | 0.013121 | -0.0022622 | 0.0034762 | 0.20448 | -0.0077808 | 0.076223 | 0.054715 | -0.002953 | 0.015529 | 0.0017274 | -0.059509 | 63.8901 | -60.141 | 64.0686 | -60.0998 | -60.4385 | -60.4248 | -0.009155 | 63.8672 | -60.1318 | 64.183 | -60.0998 | -60.2142 | -60.1318 | -0.045776 | -0.091552 | 0.086976 | -0.004577 | -0.32959 | -0.34332 | -0.28381 | -0.29755 | -0.036621 | -0.11444 | 0.20142 | -0.004577 | -0.036621 | -0.11902 | 0 | -0.082397 | 0.041199 | 124.2096 | 0.032044 | 124.3149 | 124.0311 | 123.999 | 123.9853 | 123.9624 | -124.1226 | -124.1135 | 124.1638 | 124.2783 | 60.0357 | 60.0861
289.9375 | 124.3652 | -60.0723 | 64.0366 | 0.084874 | -0.0066702 | 0.070255 | 0.058223 | 0.0067124 | 0.00094276 | 0.0034762 | 0.34181 | -0.0024398 | 0.06661 | 0.049374 | -0.018975 | -0.0026279 | -0.013226 | 0.036621 | 63.9038 | -60.1364 | 64.0869 | -60.0723 | -60.3973 | -60.3745 | 0.10986 | 63.9313 | -60.0861 | 64.3387 | -60.2829 | -60.2509 | -60.1776 | -0.064087 | -0.13275 | 0.050354 | 0 | -0.30212 | -0.32501 | -0.23804 | -0.26093 | -0.013733 | -0.10529 | 0.30212 | -0.21057 | -0.10529 | -0.17853 | -0.091552 | -0.16479 | 0.064087 | 124.2233 | -0.19684 | 124.4247 | 124.0402 | 124.0173 | 123.9761 | 124.0036 | -124.173 | -124.1226 | 124.1592 | 124.411 | 60.1089 | 60.1822
290.9375 | 124.2737 | -60.1044 | 64.0457 | 0.13065 | 0.00080677 | 0.068119 | 0.072108 | -0.012514 | 0.024441 | -0.0082728 | -0.0091433 | 0.011445 | 0.06661 | 0.064328 | -0.011498 | 0.010189 | -0.0068176 | -0.022888 | 63.9175 | -60.1868 | 64.2151 | -59.9625 | -60.3058 | -60.3104 | -0.041199 | 63.9725 | -60.1501 | 64.1098 | -60.1868 | -60.3195 | -60.1959 | -0.082398 | -0.12817 | 0.16937 | 0.14191 | -0.20599 | -0.20142 | -0.1236 | -0.11902 | -0.045776 | -0.073242 | 0.064087 | -0.082398 | -0.091553 | -0.21515 | -0.045777 | -0.16937 | 0.22431 | 124.4019 | -0.036622 | 124.2599 | 124.1043 | 124.1226 | 124.0219 | 124.0768 | -124.2325 | -124.1959 | 124.3195 | 124.2142 | 60.0815 | 60.0632
291.9375 | 124.2966 | -60.1089 | 64.0686 | 0.25272 | -0.0023982 | 0.049961 | 0.063563 | 0.0099164 | -0.0065342 | -0.0039998 | 0.14344 | 0.0071732 | 0.064474 | 0.087826 | 0.00025105 | 0.011257 | 0.0038644 | 0.20142 | 63.9771 | -60.1456 | 64.2746 | -59.9075 | -60.2463 | -60.2554 | -0.041199 | 63.9954 | -60.1318 | 64.1098 | -60.1776 | -60.2921 | -60.1776 | -0.036621 | -0.091553 | 0.20599 | 0.20142 | -0.14648 | -0.13733 | -0.10986 | -0.10071 | -0.022888 | -0.073243 | 0.041198 | -0.068664 | -0.068664 | -0.18311 | -0.045776 | -0.16022 | 0.23804 | 124.4202 | -0.045776 | 124.2416 | 124.1226 | 124.1272 | 124.086 | 124.1043 | -124.2142 | -124.2004 | 124.3835 | 124.2188 | 60.3104 | 60.0677
292.9375 | 124.3103 | -60.0769 | 64.0549 | 0.14591 | -0.0077382 | 0.059574 | 0.073176 | 0.010984 | -0.0065342 | 0.015226 | 0.067151 | 0.00076419 | 0.079428 | 0.066464 | -0.007226 | 0.0048481 | -0.0025446 | 0.041199 | 63.9496 | -60.1501 | 64.2059 | -59.967 | -60.3012 | -60.2875 | 0 | 63.9771 | -60.1044 | 64.151 | -60.1318 | -60.2509 | -60.1639 | -0.073242 | -0.10529 | 0.15106 | 0.10986 | -0.21057 | -0.2243 | -0.13733 | -0.15106 | -0.027466 | -0.07782 | 0.09613 | -0.054932 | -0.086975 | -0.17395 | -0.059509 | -0.14648 | 0.1831 | 124.3561 | -0.027466 | 124.2554 | 124.0997 | 124.0814 | 124.0265 | 124.054 | -124.205 | -124.1592 | 124.2828 | 124.2279 | 60.1181 | 60.0769
293.9375 | 124.3881 | -60.0906 | 63.9816 | 0.054357 | -0.0023982 | 0.075596 | 0.069972 | -0.00076463 | -0.027896 | -0.012545 | 0.14344 | 0.0061052 | 0.063406 | 0.049374 | -0.017907 | -0.0026279 | -0.0014766 | -0.054932 | 63.8992 | -60.1776 | 64.1052 | -60.0861 | -60.4294 | -60.4111 | -0.013733 | 63.9038 | -60.141 | 64.1876 | -60.1089 | -60.228 | -60.1089 | -0.086975 | -0.082397 | 0.1236 | 0.004577 | -0.32043 | -0.33874 | -0.23346 | -0.25177 | -0.050354 | -0.077819 | 0.20599 | -0.018311 | -0.018311 | -0.13733 | 0.032043 | -0.086975 | 0.091552 | 124.2828 | 0.032043 | 124.3286 | 124.0768 | 124.0448 | 123.9899 | 123.9944 | -124.1592 | -124.1226 | 124.1959 | 124.2783 | 60.0357 | 60.0769
294.9688 | 124.2737 | -60.1273 | 64.0594 | 0.023839 | 0.011488 | 0.06171 | 0.075312 | -0.00076463 | 0.014828 | -0.0082728 | -0.0091433 | 0.0061052 | 0.080496 | 0.030148 | -0.00081695 | 0.016598 | 0.0027964 | -0.004578 | 63.9267 | -60.173 | 64.2151 | -59.9808 | -60.3149 | -60.2921 | -0.050354 | 63.9542 | -60.1364 | 64.1098 | -60.1913 | -60.3241 | -60.2097 | -0.045777 | -0.13275 | 0.15564 | 0.14648 | -0.1648 | -0.18768 | -0.11902 | -0.14191 | -0.009156 | -0.10529 | 0.050354 | -0.064087 | -0.082398 | -0.19684 | -0.073242 | -0.18768 | 0.19226 | 124.3881 | -0.054931 | 124.2462 | 124.0997 | 124.0906 | 124.054 | 124.0814 | -124.2325 | -124.1959 | 124.3423 | 124.2371 | 60.1227 | 60.0769
295.9375 | 124.3103 | -60.0906 | 64.0594 | 0.11539 | 0.0093518 | 0.062778 | 0.072108 | 0.0024404 | -0.0043982 | 0.010953 | 0.051892 | 0.011445 | 0.073019 | 0.0087855 | -0.005089 | 0.0080531 | 0.0017274 | 0.013733 | 63.9267 | -60.1685 | 64.183 | -59.9991 | -60.3104 | -60.3058 | 0.018311 | 63.9725 | -60.1135 | 64.1373 | -60.1364 | -60.2829 | -60.2692 | -0.07782 | -0.13275 | 0.1236 | 0.091553 | -0.21515 | -0.21973 | -0.13733 | -0.14191 | -0.022888 | -0.086975 | 0.07782 | -0.045777 | -0.17853 | -0.19226 | -0.15564 | -0.16937 | 0.16937 | 124.3515 | -0.022889 | 124.2508 | 124.0952 | 124.086 | 124.0173 | 124.0631 | -124.2279 | -124.173 | 124.2737 | 124.2279 | 60.1044 | 60.1089
296.9375 | 124.2508 | -60.0906 | 64.0366 | 0.20695 | -0.00026223 | 0.068119 | 0.072108 | 0.0099164 | 0.026577 | 0.0098852 | 0.11293 | 0.0093092 | 0.067678 | 0.053647 | -0.004021 | 0.015529 | 0.0092044 | 0.013733 | 63.9359 | -60.1913 | 64.1693 | -59.9854 | -60.3195 | -60.3012 | 0.009155 | 63.9725 | -60.1364 | 64.1602 | -60.1364 | -60.228 | -60.2371 | -0.10071 | -0.10071 | 0.13275 | 0.10529 | -0.21057 | -0.22888 | -0.10986 | -0.12817 | -0.045777 | -0.064087 | 0.1236 | -0.045777 | -0.14648 | -0.13733 | -0.10071 | -0.091552 | 0.20599 | 124.3607 | 0 | 124.2966 | 124.1272 | 124.1089 | 124.0265 | 124.0631 | -124.2279 | -124.173 | 124.2599 | 124.2508 | 60.1044 | 60.0998
297.9375 | 124.3469 | -60.0677 | 64.0411 | 0.084874 | 0.011488 | 0.06171 | 0.066768 | 0.0077804 | 0.0020108 | -0.010409 | 0.08241 | -0.0013718 | 0.0837 | 0.057919 | -0.004021 | 0.012325 | 0.016681 | 0.027466 | 63.9221 | -60.1822 | 64.1922 | -59.9899 | -60.3195 | -60.3149 | -0.004578 | 63.9542 | -60.1181 | 64.1602 | -60.1273 | -60.2783 | -60.1776 | -0.11444 | -0.11902 | 0.15106 | 0.07782 | -0.24719 | -0.25177 | -0.13275 | -0.13733 | -0.050354 | -0.086975 | 0.11902 | -0.059509 | -0.10986 | -0.21057 | -0.059509 | -0.16022 | 0.19226 | 124.3744 | -0.009155 | 124.2783 | 124.1043 | 124.0723 | 123.9899 | 124.0219 | -124.2233 | -124.1592 | 124.2599 | 124.2279 | 60.0952 | 60.0632
298.9375 | 124.2645 | -60.1181 | 64.0549 | 0.13065 | 0.0061468 | 0.05637 | 0.066768 | 0.023802 | -0.012943 | -0.020022 | 0.067151 | -0.0024398 | 0.06127 | 0.02374 | -0.001885 | 0.0037801 | 0.0027964 | -0.022888 | 63.9038 | -60.1822 | 64.2059 | -59.9808 | -60.2921 | -60.3058 | -0.045776 | 63.9587 | -60.1364 | 64.1235 | -60.1913 | -60.3058 | -60.2051 | -0.064087 | -0.15106 | 0.15106 | 0.13733 | -0.18768 | -0.17395 | -0.1236 | -0.10986 | -0.018311 | -0.096131 | 0.068664 | -0.073242 | -0.086975 | -0.18768 | -0.068664 | -0.16937 | 0.20142 | 124.3881 | -0.054931 | 124.2599 | 124.086 | 124.0952 | 124.0219 | 124.0768 | -124.2371 | -124.1913 | 124.324 | 124.2416 | 60.0952 | 60.0723
299.9375 | 124.3149 | -60.0998 | 64.0732 | 0.023839 | 0.0061468 | 0.062778 | 0.063563 | 0.0088484 | 0.035122 | 0.0066812 | 0.08241 | 0.0018322 | 0.070883 | 0.032284 | -0.013634 | 0.016598 | -0.0078856 | -0.013733 | 63.9359 | -60.1822 | 64.2059 | -59.9762 | -60.2966 | -60.3012 | -0.036621 | 63.9313 | -60.141 | 64.1327 | -60.173 | -60.3195 | -60.2005 | -0.082398 | -0.13733 | 0.13275 | 0.1236 | -0.20142 | -0.19684 | -0.11902 | -0.11444 | -0.041199 | -0.14191 | 0.059509 | -0.073243 | -0.10071 | -0.21973 | -0.059509 | -0.17853 | 0.20599 | 124.3881 | -0.032044 | 124.2737 | 124.118 | 124.0723 | 124.0356 | 124.0311 | -124.2554 | -124.2142 | 124.3057 | 124.2325 | 60.0861 | 60.0632
300.9375 | 124.3103 | -60.0769 | 64.0411 | 0.2222 | 0.0050788 | 0.058506 | 0.067836 | 0.0077804 | -0.0086702 | 0.0077492 | 0.067151 | 0.0039692 | 0.062338 | 0.048306 | -0.005089 | 0.017666 | 0.0017274 | 0.027466 | 63.9313 | -60.141 | 64.1968 | -59.9854 | -60.3012 | -60.2921 | 0.018311 | 63.9542 | -60.1273 | 64.1602 | -60.1456 | -60.2646 | -60.173 | -0.064087 | -0.10986 | 0.15564 | 0.091552 | -0.21515 | -0.2243 | -0.15106 | -0.16022 | -0.050354 | -0.086975 | 0.11902 | -0.068665 | -0.096131 | -0.18768 | -0.045777 | -0.13733 | 0.15564 | 124.3378 | -0.018311 | 124.2874 | 124.0723 | 124.0814 | 124.0082 | 124.0311 | -124.1821 | -124.1684 | 124.2737 | 124.2371 | 60.1044 | 60.0952
301.9375 | 124.2874 | -60.0861 | 64.032 | 0.054357 | -0.00026223 | 0.047825 | 0.074244 | -0.011446 | -0.014011 | 0.0034762 | 0.051892 | 0.0018322 | 0.069815 | 0.056851 | -0.004021 | 0.016598 | -0.0014766 | -0.041199 | 63.9221 | -60.1913 | 64.2105 | -59.9579 | -60.2921 | -60.2921 | -0.036621 | 63.9679 | -60.1456 | 64.1373 | -60.1593 | -60.2783 | -60.1822 | -0.10528 | -0.10986 | 0.17853 | 0.12817 | -0.20599 | -0.20599 | -0.10071 | -0.10071 | -0.059509 | -0.064086 | 0.10529 | -0.073242 | -0.09613 | -0.19226 | -0.036621 | -0.13275 | 0.23346 | 124.4019 | -0.013733 | 124.2828 | 124.1135 | 124.1135 | 124.0082 | 124.054 | -124.2233 | -124.1776 | 124.2966 | 124.2233 | 60.0449 | 60.0494
302.9375 | 124.2599 | -60.0861 | 64.0411 | 0.14591 | 0.0040108 | 0.070255 | 0.072108 | 0.012053 | 0.00094276 | -0.0061368 | 0.067151 | -0.0056438 | 0.071951 | 0.057919 | 0.001319 | -0.0026279 | 0.0038644 | -0.032043 | 63.9267 | -60.1959 | 64.2334 | -59.9533 | -60.2829 | -60.2921 | -0.082397 | 63.9496 | -60.1364 | 64.0732 | -60.2142 | -60.347 | -60.228 | -0.10986 | -0.11444 | 0.19226 | 0.13275 | -0.20599 | -0.19684 | -0.09613 | -0.086975 | -0.050354 | -0.091553 | 0.032043 | -0.12817 | -0.14191 | -0.26092 | -0.091552 | -0.21057 | 0.24262 | 124.4293 | -0.077819 | 124.2096 | 124.1226 | 124.086 | 124.0128 | 124.0356 | -124.2371 | -124.1776 | 124.3195 | 124.1592 | 60.054 | 60.0037
303.9375 | 124.2508 | -60.1273 | 64.0366 | 0.069615 | 0.0029428 | 0.070255 | 0.078517 | 0.012053 | -0.014011 | -0.0018638 | -0.024402 | -0.0099168 | 0.071951 | 0.031216 | -0.013634 | 0.013393 | 0.0092044 | -0.086975 | 63.9359 | -60.1822 | 64.2517 | -59.8984 | -60.2692 | -60.2692 | -0.16479 | 63.9587 | -60.1456 | 64.064 | -60.2463 | -60.3607 | -60.2234 | -0.054932 | -0.10071 | 0.21515 | 0.22888 | -0.14191 | -0.14191 | -0.086975 | -0.086975 | -0.018311 | -0.07782 | 0.027466 | -0.11902 | -0.096131 | -0.23346 | -0.07782 | -0.21515 | 0.28381 | 124.4339 | -0.10071 | 124.2096 | 124.118 | 124.1043 | 124.0631 | 124.086 | -124.2188 | -124.1821 | 124.379 | 124.1913 | 60.0403 | 59.9625
304.9375 | 124.2828 | -60.0952 | 64.0503 | 0.16117 | -0.0056022 | 0.058506 | 0.07104 | 0.029142 | -0.0054662 | 0.015226 | 0.036633 | 0.0071732 | 0.063406 | 0.037625 | -0.009362 | 0.012325 | 0.0006594 | 0.009155 | 63.9038 | -60.1547 | 64.1785 | -59.9808 | -60.3104 | -60.2966 | 0.013733 | 63.9679 | -60.1456 | 64.1647 | -60.141 | -60.2509 | -60.1501 | -0.059509 | -0.14648 | 0.12817 | 0.11444 | -0.20142 | -0.21515 | -0.14191 | -0.15564 | -0.050354 | -0.082397 | 0.11444 | -0.045776 | -0.054931 | -0.15564 | -0.004577 | -0.10528 | 0.17395 | 124.3332 | 0.004578 | 124.3103 | 124.0585 | 124.1135 | 123.999 | 124.0631 | -124.205 | -124.1959 | 124.2737 | 124.2599 | 60.1044 | 60.1089
305.9375 | 124.324 | -60.0632 | 64.0686 | 0.10013 | -0.0077382 | 0.060642 | 0.064631 | 0.00030337 | -0.0076022 | 0.0013402 | 0.11293 | -0.0013718 | 0.082632 | 0.079282 | -0.01577 | 0.010189 | -0.018567 | 0.032043 | 63.9359 | -60.1547 | 64.2014 | -59.9762 | -60.3104 | -60.2783 | 0.022888 | 63.9908 | -60.0952 | 64.1235 | -60.1273 | -60.2737 | -60.1593 | -0.091553 | -0.13275 | 0.13275 | 0.086975 | -0.21515 | -0.24719 | -0.1236 | -0.15564 | -0.032044 | -0.07782 | 0.054931 | -0.064087 | -0.096131 | -0.21057 | -0.064087 | -0.17853 | 0.17853 | 124.3561 | -0.032043 | 124.2188 | 124.0906 | 124.086 | 123.999 | 124.054 | -124.2233 | -124.1638 | 124.2645 | 124.1867 | 60.0952 | 60.0861
306.9375 | 124.2645 | -60.1089 | 64.0549 | 0.14591 | 0.0029428 | 0.067051 | 0.069972 | -0.0039686 | -0.016147 | 0.0034762 | 0.11293 | 0.0061052 | 0.063406 | 0.06326 | 0.00025105 | 0.016598 | 0.0038644 | 0.009155 | 63.9313 | -60.1685 | 64.2059 | -59.967 | -60.3104 | -60.2783 | -0.050354 | 63.9679 | -60.1227 | 64.119 | -60.1913 | -60.3333 | -60.2051 | -0.059509 | -0.1236 | 0.15106 | 0.14191 | -0.16937 | -0.20142 | -0.10986 | -0.14191 | -0.013733 | -0.086975 | 0.064087 | -0.082397 | -0.09613 | -0.2243 | -0.082397 | -0.21057 | 0.20142 | 124.3744 | -0.068664 | 124.2416 | 124.0997 | 124.0906 | 124.0402 | 124.0768 | -124.2233 | -124.1776 | 124.3149 | 124.2279 | 60.1181 | 60.0586
307.9688 | 124.2599 | -60.1044 | 64.0686 | 0.10013 | 0.0093518 | 0.069187 | 0.064631 | -0.0039686 | -0.02042 | -0.0061368 | 0.14344 | 0.0061052 | 0.06127 | 0.025876 | -0.016839 | 0.0069851 | 0.0006594 | -0.041199 | 63.913 | -60.1593 | 64.2014 | -59.9854 | -60.3058 | -60.3149 | -0.050354 | 63.9542 | -60.1364 | 64.1052 | -60.1959 | -60.3195 | -60.2005 | -0.054932 | -0.15564 | 0.13275 | 0.11902 | -0.21057 | -0.20142 | -0.15564 | -0.14648 | -0.032044 | -0.11444 | 0.036621 | -0.091553 | -0.09613 | -0.21515 | -0.064086 | -0.1831 | 0.17395 | 124.3607 | -0.059509 | 124.2416 | 124.0723 | 124.0906 | 124.0173 | 124.0585 | -124.2279 | -124.205 | 124.3057 | 124.2096 | 60.0632 | 60.054
308.9375 | 124.3149 | -60.0677 | 64.0457 | 0.069615 | 0.0072148 | 0.072392 | 0.075312 | 0.0045764 | 0.0052148 | -0.013613 | 0.11293 | 0.0029002 | 0.056997 | 0.035489 | -0.009362 | 0.0091211 | 0.013477 | -0.073242 | 63.9267 | -60.173 | 64.2197 | -59.967 | -60.2783 | -60.2737 | -0.068665 | 63.9542 | -60.1364 | 64.1281 | -60.1593 | -60.2921 | -60.1822 | -0.10529 | -0.11902 | 0.17395 | 0.10071 | -0.20599 | -0.21057 | -0.10071 | -0.10529 | -0.068665 | -0.091552 | 0.082398 | -0.091553 | -0.11444 | -0.2243 | -0.045776 | -0.15564 | 0.20599 | 124.3927 | -0.022888 | 124.2645 | 124.0997 | 124.0906 | 123.9944 | 124.0219 | -124.2188 | -124.1821 | 124.2874 | 124.1959 | 59.9945 | 59.9991
309.9375 | 124.2508 | -60.1089 | 64.0411 | -0.0066789 | 0.0072148 | 0.064915 | 0.064631 | 0.0056444 | -0.0011942 | -0.0039998 | 0.067151 | -0.0056438 | 0.076223 | 0.08035 | -0.006157 | 0.015529 | 0.0092044 | -0.11444 | 63.9038 | -60.1913 | 64.2426 | -59.8938 | -60.228 | -60.2554 | -0.16937 | 63.9542 | -60.1822 | 64.1006 | -60.2097 | -60.3561 | -60.228 | -0.082397 | -0.13733 | 0.20142 | 0.21515 | -0.14648 | -0.11902 | -0.064087 | -0.036621 | -0.073242 | -0.086975 | 0.059509 | -0.10071 | -0.11902 | -0.24719 | -0.045776 | -0.17395 | 0.29755 | 124.4339 | -0.027466 | 124.2828 | 124.0952 | 124.1364 | 124.0128 | 124.0631 | -124.2325 | -124.2233 | 124.3515 | 124.2096 | 59.9945 | 59.9396
310.9375 | 124.2599 | -60.1089 | 64.0366 | 0.023839 | 0.0082828 | 0.058506 | 0.066768 | 0.0067124 | -0.016147 | -0.020022 | 0.14344 | 0.0018322 | 0.077291 | 0.055783 | -0.009362 | 0.016598 | -0.0068176 | -0.032043 | 63.9175 | -60.1593 | 64.2014 | -59.967 | -60.2829 | -60.2829 | -0.09613 | 63.9587 | -60.1089 | 64.119 | -60.2005 | -60.3241 | -60.2142 | -0.050354 | -0.11902 | 0.1648 | 0.14191 | -0.17395 | -0.17395 | -0.1236 | -0.1236 | 0 | -0.07782 | 0.082398 | -0.091552 | -0.10529 | -0.21515 | -0.10529 | -0.21515 | 0.19226 | 124.3607 | -0.091552 | 124.2279 | 124.0768 | 124.0677 | 124.0265 | 124.0677 | -124.1959 | -124.1455 | 124.3103 | 124.2279 | 60.0769 | 60.0128
311.9375 | 124.2142 | -60.1044 | 64.0411 | -0.021937 | 0.0061468 | 0.064915 | 0.074244 | -0.0050366 | -0.00012524 | 0.013089 | 0.08241 | 0.0071732 | 0.079428 | 0.082486 | -0.005089 | 0.0069851 | 0.0038644 | -0.091553 | 63.945 | -60.1593 | 64.2426 | -59.903 | -60.26 | -60.2646 | -0.16937 | 63.9633 | -60.1639 | 64.0869 | -60.2371 | -60.3836 | -60.2325 | -0.054932 | -0.096131 | 0.20142 | 0.20142 | -0.16022 | -0.15564 | -0.10529 | -0.10071 | -0.059509 | -0.07782 | 0.045776 | -0.13275 | -0.12817 | -0.27924 | -0.068665 | -0.21973 | 0.25635 | 124.4019 | -0.073243 | 124.2508 | 124.1043 | 124.1272 | 124.0494 | 124.0677 | -124.2004 | -124.205 | 124.3469 | 124.1913 | 60.0128 | 59.935
312.9375 | 124.3057 | -60.0952 | 64.0366 | 0.28324 | -0.00026223 | 0.05637 | 0.075312 | -0.0039686 | -0.0043982 | 0.0034762 | 0.21974 | 0.0029002 | 0.068746 | 0.033353 | -0.012566 | 0.012325 | 0.020953 | 0.004578 | 63.9725 | -60.173 | 64.238 | -59.9213 | -60.2875 | -60.2463 | -0.032043 | 63.9999 | -60.1273 | 64.1556 | -60.1273 | -60.26 | -60.1822 | -0.07782 | -0.064087 | 0.20142 | 0.17395 | -0.15106 | -0.19226 | -0.073242 | -0.11444 | -0.032043 | -0.036621 | 0.11902 | -0.032043 | -0.086975 | -0.16479 | -0.054932 | -0.13275 | 0.25177 | 124.411 | 0 | 124.2828 | 124.1455 | 124.1272 | 124.0677 | 124.0952 | -124.2096 | -124.1638 | 124.3332 | 124.2508 | 60.0998 | 60.0632
313.9375 | 124.3011 | -60.0769 | 64.0137 | 0.13065 | 0.0040108 | 0.058506 | 0.073176 | -0.0039686 | -0.0022622 | -0.0039998 | 0.11293 | -0.00030381 | 0.075155 | 0.042966 | -0.01043 | 0.016598 | 0.0006594 | 0.022888 | 63.9679 | -60.1639 | 64.1968 | -59.9808 | -60.3195 | -60.2921 | -0.013733 | 63.945 | -60.1181 | 64.1464 | -60.1227 | -60.2554 | -60.1593 | -0.086975 | -0.045776 | 0.1831 | 0.09613 | -0.21515 | -0.24262 | -0.12817 | -0.15564 | -0.041199 | -0.068665 | 0.13275 | -0.045777 | -0.082398 | -0.17853 | -0.041199 | -0.13733 | 0.18311 | 124.3607 | -0.004578 | 124.2645 | 124.1318 | 124.0631 | 124.0448 | 124.0219 | -124.1776 | -124.1318 | 124.2737 | 124.2233 | 60.0998 | 60.0632
314.9375 | 124.3744 | -60.0998 | 64.032 | 0.10013 | -0.0013302 | 0.055302 | 0.073176 | 0.010984 | 0.0030788 | -0.0039998 | 0.12819 | 0.0018322 | 0.076223 | 0.0686 | 0.001319 | 0.0080531 | 0.0081364 | -0.1236 | 63.8992 | -60.1913 | 64.183 | -59.967 | -60.3195 | -60.3287 | -0.11444 | 63.9267 | -60.1364 | 64.1556 | -60.1501 | -60.2554 | -60.1639 | -0.091553 | -0.13275 | 0.15106 | 0.13275 | -0.22888 | -0.21973 | -0.13733 | -0.12817 | -0.036622 | -0.10529 | 0.1236 | -0.050354 | -0.064087 | -0.15564 | -0.027465 | -0.11902 | 0.2243 | 124.3744 | -0.013732 | 124.292 | 124.0906 | 124.0631 | 123.999 | 124.0265 | -124.2233 | -124.1684 | 124.2828 | 124.2554 | 59.9762 | 59.9854
315.9375 | 124.3057 | -60.1181 | 64.032 | 0.13065 | -0.0056022 | 0.062778 | 0.068904 | 0.0067124 | -0.0033302 | -0.013613 | 0.12819 | -0.0035078 | 0.075155 | 0.069668 | -0.009362 | 0.014461 | 0.0027964 | 0.004578 | 63.945 | -60.1639 | 64.2242 | -59.935 | -60.2921 | -60.2646 | -0.018311 | 63.9862 | -60.1273 | 64.1464 | -60.1044 | -60.2417 | -60.1593 | -0.045776 | -0.086975 | 0.19226 | 0.1831 | -0.14648 | -0.17395 | -0.10071 | -0.12817 | -0.009155 | -0.045776 | 0.11444 | 0.013733 | -0.041199 | -0.1236 | -0.032044 | -0.11444 | 0.22888 | 124.3881 | 0.022888 | 124.2737 | 124.1089 | 124.1135 | 124.0631 | 124.1043 | -124.1959 | -124.1592 | 124.3423 | 124.2645 | 60.1227 | 60.0998
316.9375 | 124.3011 | -60.1089 | 64.0594 | 0.16117 | -0.0034662 | 0.067051 | 0.066768 | -0.0061046 | 0.0073508 | -0.020022 | 0.235 | 0.012514 | 0.080496 | 0.067532 | -0.016839 | 0.011257 | -0.0057486 | 0.009155 | 63.9542 | -60.1547 | 64.2014 | -59.9808 | -60.2921 | -60.2737 | -0.022888 | 63.9587 | -60.1364 | 64.1556 | -60.1273 | -60.2554 | -60.1456 | -0.045776 | -0.10529 | 0.14191 | 0.12817 | -0.1648 | -0.18311 | -0.11902 | -0.13733 | -0.027466 | -0.10071 | 0.096131 | -0.01831 | -0.036621 | -0.14648 | -0.009155 | -0.11902 | 0.17395 | 124.3561 | 0.009156 | 124.292 | 124.1089 | 124.0952 | 124.0631 | 124.0677 | -124.2142 | -124.1959 | 124.3103 | 124.2645 | 60.1181 | 60.0861
317.9375 | 124.2874 | -60.0723 | 64.0503 | 0.054357 | -0.0066702 | 0.065983 | 0.068904 | -0.00076463 | -0.012943 | 0.0024082 | 0.11293 | 0.0029002 | 0.064474 | 0.030148 | -0.01043 | 0.0091211 | 0.020953 | -0.013733 | 63.9404 | -60.1547 | 64.2151 | -59.9854 | -60.2921 | -60.2829 | -0.036621 | 63.9679 | -60.1273 | 64.1373 | -60.1089 | -60.2509 | -60.1639 | -0.082397 | -0.10986 | 0.16479 | 0.086975 | -0.21057 | -0.21973 | -0.12817 | -0.13733 | -0.054931 | -0.082397 | 0.086975 | -0.036621 | -0.091552 | -0.17853 | -0.036621 | -0.1236 | 0.16937 | 124.3698 | 0.01831 | 124.2645 | 124.0952 | 124.0952 | 124.0128 | 124.0402 | -124.205 | -124.1776 | 124.2874 | 124.2096 | 60.0586 | 60.0357
318.9688 | 124.2828 | -60.0815 | 64.0457 | 0.16117 | -0.0013302 | 0.064915 | 0.07104 | 0.00030337 | -0.00012524 | 0.0013402 | 0.08241 | 0.0071732 | 0.078359 | 0.025876 | -0.013634 | 0.018734 | -0.0025446 | -0.027466 | 63.9359 | -60.1776 | 64.2105 | -59.967 | -60.3058 | -60.2829 | -0.064087 | 63.9908 | -60.1089 | 64.1052 | -60.173 | -60.3058 | -60.173 | -0.09613 | -0.10986 | 0.16479 | 0.11444 | -0.20142 | -0.2243 | -0.10529 | -0.12817 | -0.027466 | -0.054931 | 0.05951 | -0.091553 | -0.091553 | -0.2243 | -0.064087 | -0.19684 | 0.21057 | 124.3881 | -0.064087 | 124.2142 | 124.1135 | 124.0997 | 124.0173 | 124.0723 | -124.2233 | -124.1547 | 124.292 | 124.1867 | 60.054 | 60.0174
319.9375 | 124.2599 | -60.0861 | 64.0549 | 0.11539 | 0.0018748 | 0.067051 | 0.067836 | -0.0039686 | -0.0022622 | -0.0093408 | 0.08241 | 0.0093092 | 0.062338 | 0.048306 | -0.004021 | 0.0080531 | -0.0057486 | -0.07782 | 63.9221 | -60.1822 | 64.2151 | -59.9304 | -60.2463 | -60.2692 | -0.15106 | 63.9679 | -60.1364 | 64.0915 | -60.2051 | -60.3699 | -60.2325 | -0.09613 | -0.13275 | 0.16022 | 0.15564 | -0.1831 | -0.16022 | -0.086975 | -0.064087 | -0.050354 | -0.086975 | 0.036621 | -0.11902 | -0.14648 | -0.28381 | -0.09613 | -0.23346 | 0.25177 | 124.3973 | -0.068664 | 124.2279 | 124.1043 | 124.1043 | 124.0082 | 124.054 | -124.2371 | -124.1913 | 124.3011 | 124.1776 | 60.0082 | 59.935
320.9375 | 124.3195 | -60.0723 | 64.1098 | 0.20695 | -0.0013302 | 0.064915 | 0.075312 | 0.0099164 | -0.018283 | -0.0039998 | 0.12819 | 0.0018322 | 0.067678 | 0.051511 | 0.00025105 | 0.010189 | 0.02309 | -0.022888 | 63.9542 | -60.141 | 64.2563 | -59.8755 | -60.2371 | -60.228 | -0.073242 | 63.9954 | -60.1227 | 64.119 | -60.141 | -60.2692 | -60.1593 | -0.068664 | -0.15564 | 0.14648 | 0.19684 | -0.15564 | -0.16479 | -0.086975 | -0.096131 | -0.050354 | -0.11444 | 0.009156 | -0.068664 | -0.086975 | -0.19684 | -0.036621 | -0.14648 | 0.2655 | 124.3973 | -0.01831 | 124.2416 | 124.0952 | 124.118 | 124.0265 | 124.0677 | -124.2508 | -124.2325 | 124.3286 | 124.1913 | 60.0494 | 59.9991
321.9375 | 124.292 | -60.0952 | 64.0594 | 0.084874 | -0.0098752 | 0.05637 | 0.069972 | 0.0045764 | -0.0022622 | -0.0029318 | 0.21974 | 0.0018322 | 0.077291 | 0.042966 | -0.009362 | 0.019802 | -0.012158 | -0.013733 | 63.9587 | -60.1547 | 64.2288 | -59.9396 | -60.2829 | -60.2646 | -0.032043 | 63.9679 | -60.1044 | 64.1418 | -60.1273 | -60.2646 | -60.1456 | -0.059509 | -0.10071 | 0.16937 | 0.15564 | -0.16937 | -0.18768 | -0.10986 | -0.12817 | -0.009155 | -0.091552 | 0.082398 | -0.032043 | -0.050354 | -0.16937 | -0.041199 | -0.16022 | 0.21515 | 124.3835 | -0.022888 | 124.2462 | 124.1135 | 124.0723 | 124.054 | 124.0631 | -124.2142 | -124.1638 | 124.324 | 124.2371 | 60.0815 | 60.0632
322.9375 | 124.2828 | -60.0815 | 64.0594 | 0.2222 | 0.00080677 | 0.064915 | 0.07104 | 0.012053 | -0.021488 | -0.016818 | 0.20448 | 0.0050372 | 0.062338 | 0.069668 | -0.007226 | 0.0059161 | -0.026044 | -0.018311 | 63.9725 | -60.1456 | 64.2517 | -59.9075 | -60.26 | -60.2371 | -0.059509 | 63.9816 | -60.1135 | 64.151 | -60.1318 | -60.2646 | -60.141 | -0.064087 | -0.086975 | 0.19226 | 0.17395 | -0.15564 | -0.17853 | -0.091553 | -0.11444 | -0.032043 | -0.07782 | 0.091553 | -0.050354 | -0.059509 | -0.1831 | -0.027466 | -0.15106 | 0.23804 | 124.3973 | -0.018311 | 124.2645 | 124.118 | 124.0952 | 124.054 | 124.0631 | -124.205 | -124.173 | 124.3332 | 124.2325 | 60.0632 | 60.022
323.9375 | 124.2966 | -60.0906 | 64.0594 | 0.084874 | 0.0093518 | 0.06171 | 0.055018 | 0.010984 | -0.0011942 | -0.0018638 | -0.03966 | -0.0056438 | 0.076223 | 0.01199 | -0.006157 | 0.0080531 | -0.0025446 | -0.032043 | 63.9359 | -60.1593 | 64.1556 | -59.935 | -60.2966 | -60.2966 | -0.027466 | 63.9771 | -60.1273 | 64.1144 | -60.1456 | -60.2921 | -60.1822 | -0.068665 | -0.1236 | 0.096131 | 0.15564 | -0.20599 | -0.20599 | -0.13733 | -0.13733 | -0.036621 | -0.082397 | 0.054932 | -0.054932 | -0.091553 | -0.20142 | -0.054932 | -0.1648 | 0.2243 | 124.3149 | -0.018311 | 124.2416 | 124.0952 | 124.1043 | 124.0265 | 124.0677 | -124.2188 | -124.1867 | 124.2462 | 124.205 | 60.0586 | 60.0632
324.9375 | 124.2874 | -60.0677 | 64.064 | 0.069615 | -0.00026223 | 0.06171 | 0.077449 | 0.016325 | -0.021488 | -0.0061368 | -0.054919 | 0.0071732 | 0.059133 | 0.049374 | -0.006157 | 0.0048481 | -0.0089536 | -0.013733 | 63.9587 | -60.1456 | 64.1922 | -59.9762 | -60.3012 | -60.2829 | -0.013733 | 63.9771 | -60.1089 | 64.1373 | -60.1135 | -60.2509 | -60.1456 | -0.07782 | -0.10529 | 0.12817 | 0.091553 | -0.21515 | -0.23346 | -0.13733 | -0.15564 | -0.041199 | -0.086975 | 0.073242 | -0.045776 | -0.07782 | -0.1831 | -0.036621 | -0.14191 | 0.16937 | 124.3378 | -0.004577 | 124.2462 | 124.1043 | 124.086 | 124.0265 | 124.0448 | -124.2096 | -124.173 | 124.2599 | 124.205 | 60.054 | 60.054
325.9375 | 124.2508 | -60.0494 | 64.0869 | 0.084874 | -0.00026223 | 0.057438 | 0.068904 | -0.010378 | -0.0086702 | 0.014158 | 0.29603 | 0.01465 | 0.075155 | 0.049374 | -0.009362 | 0.013393 | 0.0038644 | -0.041199 | 63.945 | -60.1227 | 64.2609 | -59.8892 | -60.2325 | -60.2097 | -0.07782 | 63.9908 | -60.1044 | 64.1052 | -60.141 | -60.2692 | -60.1959 | -0.073243 | -0.14191 | 0.17395 | 0.16022 | -0.16022 | -0.18311 | -0.086975 | -0.10986 | -0.054932 | -0.09613 | 0.018311 | -0.091553 | -0.14648 | -0.21973 | -0.091553 | -0.16479 | 0.23346 | 124.3835 | -0.036621 | 124.2096 | 124.0677 | 124.0952 | 123.9944 | 124.0402 | -124.2096 | -124.1913 | 124.3103 | 124.1547 | 60.0082 | 59.9716
326.9375 | 124.2554 | -60.0861 | 64.0869 | 0.16117 | -0.0013302 | 0.058506 | 0.064631 | -0.00076463 | -0.011875 | -0.0082728 | 0.11293 | -0.0045758 | 0.068746 | 0.06326 | -0.012566 | 0.015529 | 0.016681 | -0.027466 | 63.9725 | -60.1456 | 64.238 | -59.9854 | -60.2921 | -60.2371 | -0.086975 | 63.9862 | -60.1135 | 64.0915 | -60.173 | -60.2875 | -60.1868 | -0.059509 | -0.11444 | 0.15106 | 0.10071 | -0.15106 | -0.20599 | -0.091553 | -0.14648 | -0.027465 | -0.10071 | 0.004578 | -0.086975 | -0.10071 | -0.20142 | -0.073243 | -0.17395 | 0.16022 | 124.3835 | -0.05951 | 124.205 | 124.118 | 124.0997 | 124.0585 | 124.0723 | -124.2325 | -124.2004 | 124.324 | 124.1776 | 60.0586 | 59.9991
327.9375 | 124.2828 | -60.0815 | 64.0686 | 0.20695 | -0.00026223 | 0.064915 | 0.073176 | -0.0018326 | 0.010556 | -0.0050688 | 0.20448 | 0.011445 | 0.069815 | 0.0686 | -0.009362 | 0.0080531 | -0.0078856 | 0.013733 | 63.9587 | -60.1364 | 64.2151 | -59.9579 | -60.2921 | -60.2875 | -0.032043 | 63.9771 | -60.1089 | 64.1602 | -60.1273 | -60.2417 | -60.1456 | -0.054932 | -0.10986 | 0.14648 | 0.1236 | -0.20599 | -0.21057 | -0.15106 | -0.15564 | -0.027466 | -0.091553 | 0.091552 | -0.045776 | -0.064087 | -0.16022 | -0.036621 | -0.13275 | 0.17853 | 124.3515 | -0.01831 | 124.2691 | 124.0952 | 124.086 | 124.0402 | 124.0585 | -124.205 | -124.1776 | 124.2966 | 124.2416 | 60.0952 | 60.0494
328.9375 | 124.3057 | -60.0632 | 64.0823 | 0.2222 | 0.00080677 | 0.063847 | 0.075312 | -0.0018326 | -0.0033302 | -0.013613 | 0.21974 | 0.011445 | 0.073019 | 0.025876 | -0.014702 | 0.0091211 | 0.0027964 | -0.004578 | 63.9633 | -60.1318 | 64.2563 | -59.8846 | -60.2509 | -60.2234 | -0.07782 | 64.0091 | -60.0906 | 64.1144 | -60.1364 | -60.2646 | -60.1593 | -0.068665 | -0.11902 | 0.17395 | 0.17853 | -0.16022 | -0.18768 | -0.091553 | -0.11902 | -0.027466 | -0.073242 | 0.032044 | -0.073243 | -0.096131 | -0.20142 | -0.068665 | -0.17395 | 0.24719 | 124.3881 | -0.045777 | 124.205 | 124.0952 | 124.0997 | 124.0265 | 124.0723 | -124.2142 | -124.173 | 124.3195 | 124.1776 | 60.0586 | 59.9854
329.9375 | 124.324 | -60.0861 | 64.0732 | 0.16117 | 0.0050788 | 0.06171 | 0.062495 | 0.0024404 | -0.0011942 | -0.011477 | 0.18922 | 0.0039692 | 0.073019 | 0.039761 | -0.009362 | 0.0016441 | -0.0046806 | -0.013733 | 63.9725 | -60.1456 | 64.238 | -59.9121 | -60.2783 | -60.2463 | -0.059509 | 63.9816 | -60.0998 | 64.1602 | -60.1089 | -60.2371 | -60.1364 | -0.059509 | -0.10071 | 0.16479 | 0.17395 | -0.16022 | -0.19226 | -0.10071 | -0.13275 | -0.013732 | -0.091553 | 0.086975 | -0.022888 | -0.050354 | -0.15106 | -0.036622 | -0.13733 | 0.23346 | 124.3835 | -0.009156 | 124.2599 | 124.118 | 124.0814 | 124.0585 | 124.0677 | -124.2188 | -124.173 | 124.324 | 124.2462 | 60.0723 | 60.0266
330.9375 | 124.2645 | -60.0769 | 64.0915 | 0.32902 | -0.0056022 | 0.054234 | 0.067836 | -0.0061046 | -0.0086702 | 0.010953 | 0.17396 | 0.0018322 | 0.071951 | 0.079282 | 0.003456 | 0.0048481 | -0.0089536 | -0.032043 | 63.9725 | -60.1501 | 64.3112 | -59.9258 | -60.3653 | -60.26 | -0.082397 | 63.9954 | -60.1181 | 64.1006 | -60.1913 | -60.2829 | -60.1776 | -0.073242 | -0.11902 | 0.21973 | 0.15106 | -0.18311 | -0.28839 | -0.10986 | -0.21515 | -0.041199 | -0.096131 | 0.009155 | -0.11444 | -0.10071 | -0.20599 | -0.059509 | -0.1648 | 0.2243 | 124.4614 | -0.073242 | 124.2188 | 124.1226 | 124.1135 | 124.0494 | 124.0723 | -124.2416 | -124.2096 | 124.3881 | 124.1776 | 60.0449 | 59.9945
331.9375 | 124.2966 | -60.0677 | 64.0732 | 0.11539 | 0.00080677 | 0.069187 | 0.077449 | 0.0024404 | 0.011624 | -0.0061368 | 0.12819 | 0.010377 | 0.067678 | 0.049374 | -0.006157 | 0.017666 | -0.01109 | -0.018311 | 63.9404 | -60.173 | 64.2242 | -59.9625 | -60.2875 | -60.2463 | -0.045776 | 63.9954 | -60.0998 | 64.151 | -60.1181 | -60.2463 | -60.1364 | -0.10529 | -0.13275 | 0.15106 | 0.10529 | -0.17853 | -0.21973 | -0.073242 | -0.11444 | -0.032043 | -0.07782 | 0.07782 | -0.050354 | -0.068665 | -0.17853 | -0.036622 | -0.14648 | 0.21057 | 124.3973 | -0.018311 | 124.2508 | 124.1135 | 124.0952 | 124.0082 | 124.0631 | -124.2462 | -124.173 | 124.292 | 124.2188 | 60.0494 | 60.022
332.9375 | 124.2828 | -60.0632 | 64.0869 | 0.14591 | -0.0056022 | 0.060642 | 0.069972 | 0.019529 | 0.010556 | -0.020022 | 0.32655 | 0.00076419 | 0.067678 | 0.083554 | -0.008294 | 0.0048481 | -0.023907 | 0.018311 | 63.9359 | -60.1135 | 64.1739 | -59.9762 | -60.3058 | -60.2875 | -0.018311 | 63.9679 | -60.0998 | 64.1373 | -60.1135 | -60.26 | -60.1547 | -0.050354 | -0.15106 | 0.086975 | 0.086975 | -0.22431 | -0.24262 | -0.17395 | -0.19226 | -0.036621 | -0.11902 | 0.050354 | -0.050354 | -0.091553 | -0.19684 | -0.054932 | -0.16022 | 0.13733 | 124.2874 | -0.013733 | 124.2371 | 124.0494 | 124.0677 | 123.999 | 124.0311 | -124.2004 | -124.1867 | 124.2371 | 124.2004 | 60.0815 | 60.0449
333.9375 | 124.2416 | -60.0586 | 64.0961 | 0.17643 | 0.0029428 | 0.058506 | 0.061427 | 0.020598 | 0.0073508 | -0.027499 | 0.1587 | -0.0013718 | 0.071951 | 0.082486 | -0.007226 | -0.00049194 | -0.017499 | -0.009155 | 63.9679 | -60.141 | 64.2609 | -59.8938 | -60.2371 | -60.228 | -0.07782 | 63.9999 | -60.1135 | 64.1144 | -60.1501 | -60.2646 | -60.1822 | -0.082397 | -0.12817 | 0.16479 | 0.16479 | -0.16937 | -0.17853 | -0.086975 | -0.096131 | -0.054931 | -0.09613 | 0.018311 | -0.091552 | -0.1236 | -0.20599 | -0.068665 | -0.15106 | 0.24719 | 124.4019 | -0.036621 | 124.2279 | 124.1089 | 124.1135 | 124.0265 | 124.0585 | -124.2371 | -124.2096 | 124.3195 | 124.173 | 60.0494 | 59.9808
334.9375 | 124.2691 | -60.0494 | 64.0686 | 0.16117 | 0.0061468 | 0.067051 | 0.082789 | 0.00030337 | 0.0041468 | -0.0082728 | 0.0061157 | 0.0039692 | 0.081564 | 0.052579 | -0.01043 | 0.0080531 | -0.0089536 | -0.091553 | 63.9633 | -60.1547 | 64.2334 | -59.9487 | -60.2646 | -60.2737 | -0.082397 | 63.9633 | -60.1227 | 64.1464 | -60.1318 | -60.26 | -60.1547 | -0.10529 | -0.10529 | 0.16479 | 0.10071 | -0.22431 | -0.21515 | -0.11902 | -0.10986 | -0.073243 | -0.10529 | 0.077819 | -0.082398 | -0.10529 | -0.21057 | -0.032043 | -0.13733 | 0.20599 | 124.3881 | -0.009155 | 124.2691 | 124.118 | 124.086 | 124.0128 | 124.0128 | -124.2233 | -124.1913 | 124.2828 | 124.1959 | 59.9579 | 59.967
335.9375 | 124.292 | -60.0723 | 64.0869 | 0.11539 | 0.0029428 | 0.055302 | 0.073176 | 0.016325 | 0.00094276 | -0.0082728 | 0.17396 | 0.0082412 | 0.078359 | 0.065396 | -0.005089 | 0.0069851 | -0.0057486 | -0.041199 | 63.9679 | -60.1547 | 64.2609 | -59.8801 | -60.2325 | -60.2234 | -0.082397 | 63.9771 | -60.0952 | 64.1418 | -60.1318 | -60.26 | -60.1593 | -0.082397 | -0.11902 | 0.17395 | 0.19226 | -0.15106 | -0.16022 | -0.068665 | -0.07782 | -0.022888 | -0.10986 | 0.054932 | -0.059509 | -0.086975 | -0.18768 | -0.064087 | -0.16479 | 0.27466 | 124.4156 | -0.036621 | 124.2371 | 124.1226 | 124.0723 | 124.0402 | 124.0494 | -124.2416 | -124.1821 | 124.3332 | 124.2142 | 60.0311 | 59.9899
336.9375 | 124.292 | -60.0861 | 64.0778 | 0.17643 | -0.0034662 | 0.065983 | 0.074244 | 0.0099164 | -0.019351 | 0.0045452 | 0.21974 | 0.0071732 | 0.068746 | 0.052579 | -0.004021 | 0.0069851 | -0.0068176 | -0.050354 | 63.9542 | -60.1456 | 64.27 | -59.8755 | -60.2234 | -60.2005 | -0.086975 | 63.9954 | -60.0998 | 64.1281 | -60.1318 | -60.2737 | -60.1639 | -0.059509 | -0.1236 | 0.19226 | 0.21057 | -0.11444 | -0.13733 | -0.054931 | -0.07782 | -0.013732 | -0.082398 | 0.050354 | -0.045776 | -0.077819 | -0.18768 | -0.064087 | -0.17395 | 0.27008 | 124.4156 | -0.032044 | 124.2279 | 124.0997 | 124.0952 | 124.0402 | 124.0814 | -124.2233 | -124.1776 | 124.3561 | 124.2142 | 60.0357 | 59.9991
337.9375 | 124.2828 | -60.0449 | 64.0778 | 0.069615 | -0.0034662 | 0.059574 | 0.077449 | 0.0045764 | -0.018283 | -0.0039998 | -0.0091433 | 0.011445 | 0.062338 | 0.082486 | -0.013634 | 0.0091211 | -0.0078856 | -0.045776 | 63.945 | -60.1639 | 64.2426 | -59.9075 | -60.2692 | -60.2417 | -0.068665 | 64.0045 | -60.1135 | 64.1602 | -60.1044 | -60.2234 | -60.1273 | -0.11902 | -0.13275 | 0.16479 | 0.13733 | -0.19684 | -0.2243 | -0.07782 | -0.10529 | -0.068664 | -0.073242 | 0.082397 | -0.059509 | -0.082397 | -0.17853 | -0.013733 | -0.10986 | 0.25635 | 124.4064 | 0.009155 | 124.2737 | 124.1089 | 124.118 | 123.9899 | 124.0494 | -124.2416 | -124.1913 | 124.2874 | 124.205 | 59.9991 | 59.9762
338.9844 | 124.379 | -60.0128 | 64.0594 | 0.17643 | 0.0018748 | 0.064915 | 0.062495 | 0.012053 | -0.024692 | -0.017886 | 0.235 | 0.0018322 | 0.06127 | 0.042966 | -0.013634 | 0.0080531 | -0.017499 | -0.004578 | 63.913 | -60.0906 | 64.3387 | -59.8389 | -60.4523 | -60.5072 | 0.073242 | 63.945 | -60.0586 | 64.2151 | -60.022 | -60.1227 | -60.0357 | -0.07782 | -0.14648 | 0.27924 | 0.17395 | -0.49439 | -0.43945 | -0.41656 | -0.36163 | -0.045777 | -0.11444 | 0.15564 | -0.009156 | -0.022889 | -0.10986 | 0.022888 | -0.064087 | 0.25177 | 124.4293 | 0.036621 | 124.2737 | 124.0036 | 124.0036 | 123.9258 | 123.9578 | -124.1501 | -124.118 | 124.3515 | 124.2279 | 60.0082 | 60.0861
339.9375 | 124.2737 | -60.1089 | 64.032 | 0.069615 | 0.0029428 | 0.063847 | 0.081721 | -0.019991 | 0.0094878 | -0.0072048 | 0.051892 | 0.0061052 | 0.069815 | 0.04617 | -0.014702 | 0.013393 | 0.0006594 | -0.14191 | 63.9542 | -60.1685 | 64.2517 | -59.9167 | -60.2737 | -60.2509 | -0.18768 | 63.9725 | -60.1456 | 64.1052 | -60.1822 | -60.3149 | -60.2005 | -0.059509 | -0.077819 | 0.21973 | 0.19226 | -0.14191 | -0.1648 | -0.082397 | -0.10529 | -0.036621 | -0.059509 | 0.073243 | -0.073242 | -0.091552 | -0.20599 | -0.054931 | -0.16937 | 0.25177 | 124.4202 | -0.036621 | 124.2508 | 124.1226 | 124.118 | 124.0631 | 124.0814 | -124.2004 | -124.1776 | 124.3607 | 124.2142 | 59.967 | 59.9213
340.9375 | 124.3652 | -60.0403 | 64.0411 | 0.13065 | 0.0029428 | 0.060642 | 0.065699 | 0.0067124 | -0.010807 | -0.0082728 | 0.32655 | 0.0050372 | 0.074087 | 0.050442 | -0.012566 | -0.0058329 | -0.010022 | 0.009155 | 63.9633 | -60.0998 | 64.1144 | -60.022 | -60.347 | -60.3333 | 0.032043 | 63.9679 | -60.0632 | 64.2059 | -60.0449 | -60.141 | -60.0861 | -0.059509 | -0.07782 | 0.073242 | 0.01831 | -0.29297 | -0.3067 | -0.23346 | -0.24719 | -0.022888 | -0.073242 | 0.16479 | -0.004578 | -0.045777 | -0.10071 | -0.022889 | -0.07782 | 0.077819 | 124.2142 | 0.01831 | 124.2691 | 124.0631 | 124.0311 | 124.0036 | 124.0082 | -124.1409 | -124.1043 | 124.1547 | 124.2462 | 60.0494 | 60.0723
341.9375 | 124.2874 | -60.0449 | 64.1006 | 0.023839 | 0.0040108 | 0.06171 | 0.077449 | -0.0082416 | -0.0097382 | -0.0018638 | 0.32655 | 0.0061052 | 0.078359 | 0.044034 | -0.012566 | 0.012325 | -0.0057486 | 0.004578 | 63.9404 | -60.1089 | 64.1785 | -59.967 | -60.2875 | -60.3012 | -0.032043 | 63.9771 | -60.054 | 64.1556 | -60.1089 | -60.2509 | -60.173 | -0.064087 | -0.16022 | 0.07782 | 0.07782 | -0.25635 | -0.24262 | -0.19226 | -0.17853 | -0.009155 | -0.1236 | 0.054932 | -0.064087 | -0.12817 | -0.20599 | -0.11902 | -0.19684 | 0.14191 | 124.2874 | -0.054932 | 124.2096 | 124.0494 | 124.0311 | 123.9853 | 124.0219 | -124.2096 | -124.1547 | 124.2233 | 124.2004 | 60.0494 | 60.0128
342.9375 | 124.2645 | -60.0357 | 64.1556 | 0.14591 | 0.0061468 | 0.05637 | 0.07104 | -0.0018326 | -0.014011 | 0.0066812 | 0.235 | 0.0050372 | 0.073019 | 0.069668 | -0.011498 | 0.0016441 | -0.0036126 | -0.050354 | 63.9771 | -60.1456 | 64.2609 | -59.8984 | -60.2051 | -60.2188 | -0.082397 | 64.0366 | -60.0952 | 64.1144 | -60.1456 | -60.26 | -60.1868 | -0.10986 | -0.17853 | 0.10528 | 0.13733 | -0.18311 | -0.16937 | -0.073242 | -0.059509 | -0.059509 | -0.11902 | -0.041199 | -0.10986 | -0.15106 | -0.2243 | -0.091553 | -0.16479 | 0.24719 | 124.4064 | -0.050354 | 124.2096 | 124.1226 | 124.1318 | 124.0128 | 124.0723 | -124.3011 | -124.2508 | 124.2966 | 124.1501 | 59.9854 | 59.9533
343.9375 | 124.2416 | -60.0586 | 64.0961 | 0.16117 | -0.0034662 | 0.057438 | 0.077449 | 0.025938 | -0.021488 | -0.0061368 | 0.14344 | 0.0039692 | 0.065542 | 0.083554 | -0.006157 | 0.0048481 | 0.013477 | 0.16937 | 64.0228 | -60.0815 | 64.2792 | -59.8618 | -60.2097 | -60.2234 | -0.091553 | 64.0274 | -60.0861 | 64.1006 | -60.1593 | -60.2692 | -60.1593 | -0.022888 | -0.073242 | 0.18311 | 0.19684 | -0.16479 | -0.15106 | -0.14191 | -0.12817 | -0.027466 | -0.068664 | 0.004578 | -0.10071 | -0.10071 | -0.21057 | -0.073242 | -0.1831 | 0.21973 | 124.3607 | -0.073242 | 124.1867 | 124.1043 | 124.1135 | 124.0814 | 124.086 | -124.1776 | -124.1821 | 124.3378 | 124.1592 | 60.228 | 59.967
344.9375 | 124.3011 | -60.0449 | 64.0732 | 0.084874 | 0.0072148 | 0.069187 | 0.07104 | 0.00030337 | 0.0041468 | -0.0050688 | 0.021375 | 0.0061052 | 0.070883 | 0.060055 | -0.017907 | 0.0069851 | -0.0004086 | -0.009155 | 63.9816 | -60.1456 | 64.2197 | -59.9487 | -60.2921 | -60.2692 | -0.045776 | 63.9908 | -60.0861 | 64.1739 | -60.1089 | -60.2325 | -60.1364 | -0.10071 | -0.091553 | 0.14648 | 0.096131 | -0.2243 | -0.24719 | -0.1236 | -0.14648 | -0.041199 | -0.082397 | 0.10071 | -0.064087 | -0.091553 | -0.18768 | -0.050354 | -0.14648 | 0.19684 | 124.3652 | -0.022888 | 124.2599 | 124.1272 | 124.0768 | 124.0265 | 124.0356 | -124.2188 | -124.1592 | 124.2645 | 124.2188 | 60.0357 | 59.9991
345.9375 | 124.2554 | -60.0769 | 64.1006 | 0.13065 | 0.0050788 | 0.07346 | 0.069972 | 0.00030337 | 0.0084198 | 0.010953 | 0.18922 | -0.0099168 | 0.063406 | 0.073941 | 0.005592 | 0.013393 | -0.012158 | -0.059509 | 63.9816 | -60.1364 | 64.2792 | -59.8755 | -60.2142 | -60.2097 | 0.12817 | 64.0686 | -60.0403 | 64.1327 | -60.1456 | -60.2692 | -60.173 | -0.05951 | -0.11902 | 0.17853 | 0.20142 | -0.13275 | -0.13733 | -0.073242 | -0.077819 | 0.036621 | -0.032043 | 0.032043 | -0.068665 | -0.096131 | -0.19226 | -0.13275 | -0.22888 | 0.26093 | 124.4156 | -0.10529 | 124.173 | 124.118 | 124.1089 | 124.0585 | 124.1455 | -124.2371 | -124.1409 | 124.3561 | 124.2096 | 60.0174 | 60.2051
346.9375 | 124.3698 | -59.9991 | 64.0549 | 0.20695 | 0.00080677 | 0.071323 | 0.062495 | -0.0082416 | -0.0097382 | -0.014682 | 0.32655 | -0.013121 | 0.06661 | 0.058987 | -0.009362 | -0.00049194 | -0.0036126 | -0.022888 | 63.9038 | -60.0906 | 64.1373 | -60.0266 | -60.3561 | -60.3516 | 0.027466 | 63.9496 | -60.0677 | 64.2151 | -60.022 | -60.1181 | -60.054 | -0.091553 | -0.15106 | 0.082397 | -0.027466 | -0.35248 | -0.35706 | -0.26093 | -0.2655 | -0.068665 | -0.10529 | 0.16022 | -0.022889 | -0.054932 | -0.11902 | 0.013733 | -0.050354 | 0.064087 | 124.2279 | 0.045776 | 124.2828 | 123.9944 | 124.0173 | 123.9029 | 123.9487 | -124.1455 | -124.1226 | 124.1364 | 124.2142 | 59.9762 | 60.0266
347.9375 | 124.2874 | -60.0449 | 64.0961 | 0.084874 | 0.0072148 | 0.063847 | 0.068904 | 0.0024404 | -0.010807 | -0.0082728 | 0.32655 | 0.0050372 | 0.069815 | 0.032284 | -0.002953 | 0.012325 | -0.0089536 | 0.018311 | 63.945 | -60.1135 | 64.1693 | -59.9854 | -60.3104 | -60.2966 | -0.009155 | 63.9771 | -60.0906 | 64.1602 | -60.0861 | -60.2005 | -60.1135 | -0.068664 | -0.15106 | 0.073243 | 0.059509 | -0.25177 | -0.2655 | -0.18311 | -0.19684 | -0.045776 | -0.11902 | 0.064087 | -0.041199 | -0.068664 | -0.15564 | -0.022888 | -0.10986 | 0.12817 | 124.2828 | 0.004577 | 124.2508 | 124.0585 | 124.0677 | 123.9899 | 124.0219 | -124.2096 | -124.1867 | 124.2142 | 124.205 | 60.0632 | 60.0357
348.9531 | 124.324 | -60.0677 | 64.0503 | 0.084874 | 0.0061468 | 0.055302 | 0.067836 | -0.0050366 | -0.0054662 | -0.0061368 | 0.35707 | 0.0039692 | 0.064474 | 0.056851 | -0.001885 | -0.0047649 | -0.0025446 | -0.11902 | 63.9084 | -60.1181 | 64.1785 | -59.9899 | -60.3012 | -60.3195 | -0.10071 | 63.9862 | -60.1044 | 64.1739 | -60.0723 | -60.1776 | -60.1227 | -0.050354 | -0.14191 | 0.12817 | 0.07782 | -0.25177 | -0.23346 | -0.20142 | -0.18311 | -0.036621 | -0.064087 | 0.1236 | -0.004578 | -0.054932 | -0.10986 | -0.018311 | -0.073242 | 0.12817 | 124.2966 | 0.032043 | 124.2783 | 124.0265 | 124.0906 | 123.9761 | 124.054 | -124.1684 | -124.1547 | 124.2462 | 124.2416 | 59.9487 | 59.967
349.9375 | 124.2462 | -60.0632 | 64.1144 | 0.11539 | -0.0045342 | 0.059574 | 0.083857 | 0.0077804 | 0.0020108 | -0.01575 | 0.12819 | -0.00030381 | 0.073019 | 0.061124 | -0.01043 | 0.0059161 | -0.0014766 | -0.004578 | 63.9587 | -60.1181 | 64.2334 | -59.9121 | -60.2463 | -60.2142 | -0.082397 | 64.0137 | -60.0998 | 64.1052 | -60.1318 | -60.2463 | -60.1685 | -0.054932 | -0.15564 | 0.11902 | 0.15106 | -0.15106 | -0.18311 | -0.09613 | -0.12817 | -0.036621 | -0.10071 | -0.009155 | -0.068665 | -0.10529 | -0.18311 | -0.068665 | -0.14648 | 0.20599 | 124.3515 | -0.032044 | 124.205 | 124.0768 | 124.1135 | 124.0219 | 124.0768 | -124.2325 | -124.2142 | 124.2966 | 124.1684 | 60.0586 | 59.9808
350.9375 | 124.2599 | -60.054 | 64.119 | 0.16117 | -0.0034662 | 0.058506 | 0.067836 | 0.019529 | -0.0097382 | -0.0039998 | 0.17396 | 0.0061052 | 0.06127 | 0.052579 | -0.009362 | 0.010189 | 0.0027964 | -0.013733 | 63.9542 | -60.1089 | 64.2105 | -59.935 | -60.26 | -60.26 | -0.064087 | 64.0091 | -60.0677 | 64.1052 | -60.0952 | -60.26 | -60.1685 | -0.054932 | -0.1648 | 0.091552 | 0.11902 | -0.20599 | -0.20599 | -0.15106 | -0.15106 | -0.013733 | -0.10986 | -0.013733 | -0.041199 | -0.11444 | -0.20599 | -0.10071 | -0.19226 | 0.17395 | 124.3195 | -0.027466 | 124.173 | 124.0631 | 124.0768 | 124.0082 | 124.0631 | -124.2279 | -124.1867 | 124.2645 | 124.1592 | 60.0403 | 59.9899
351.9375 | 124.2554 | -60.0906 | 64.0869 | 0.2222 | 0.0018748 | 0.053165 | 0.07104 | -0.012514 | 0.0062828 | -0.01575 | 0.097669 | 0.010377 | 0.078359 | 0.032284 | -0.002953 | -0.0015599 | -0.012158 | -0.041199 | 63.9862 | -60.1364 | 64.2838 | -59.8618 | -60.2097 | -60.1868 | -0.10071 | 64.0274 | -60.0998 | 64.27 | -60.2509 | -60.4065 | -60.2646 | -0.045777 | -0.10071 | 0.19684 | 0.22888 | -0.096131 | -0.11902 | -0.050354 | -0.073242 | -0.009155 | -0.059509 | 0.18311 | -0.16022 | -0.17395 | -0.31586 | -0.16479 | -0.3067 | 0.27466 | 124.4202 | -0.15106 | 124.3698 | 124.1226 | 124.1272 | 124.0768 | 124.118 | -124.2233 | -124.1867 | 124.3744 | 124.3607 | 60.0494 | 59.9899
352.9375 | 124.3195 | -60.0403 | 64.0778 | 0.13065 | 0.0040108 | 0.069187 | 0.075312 | 0.012053 | -0.00012524 | -0.01575 | 0.1587 | 0.0018322 | 0.080496 | 0.036557 | -0.01043 | 0.014461 | -0.0046806 | -0.027466 | 63.9954 | -60.141 | 64.2609 | -59.9121 | -60.2371 | -60.2371 | -0.064087 | 64.0091 | -60.0906 | 64.2014 | -60.0906 | -60.2325 | -60.1318 | -0.10071 | -0.082398 | 0.1831 | 0.12817 | -0.19684 | -0.19684 | -0.096131 | -0.096131 | -0.050354 | -0.068665 | 0.1236 | -0.050354 | -0.091553 | -0.19226 | -0.041199 | -0.14191 | 0.22888 | 124.4019 | 0 | 124.292 | 124.1364 | 124.0997 | 124.0356 | 124.0494 | -124.2188 | -124.1684 | 124.3011 | 124.2416 | 60.0128 | 59.9762
353.9375 | 124.3469 | -60.0128 | 64.032 | 0.023839 | 0.00080677 | 0.059574 | 0.078517 | 0.0013714 | -0.032169 | -0.018954 | 0.1587 | -0.0067128 | 0.078359 | 0.0087855 | -0.007226 | 0.0080531 | -0.015362 | 0.004578 | 63.9679 | -60.1044 | 64.2242 | -59.7931 | -60.1959 | -60.5072 | 0.068665 | 63.9542 | -60.0632 | 64.238 | -59.9854 | -60.1273 | -60.0494 | -0.091553 | -0.064086 | 0.19226 | 0.21973 | -0.49439 | -0.18311 | -0.40283 | -0.091553 | -0.050354 | -0.077819 | 0.20599 | 0.027465 | -0.036621 | -0.11444 | 0.013733 | -0.064087 | 0.31128 | 124.3286 | 0.077819 | 124.3011 | 124.0723 | 124.0173 | 123.9807 | 123.967 | -124.1364 | -124.0952 | 124.2371 | 124.2508 | 60.0174 | 60.0815
354.9688 | 124.3561 | -60.0494 | 64.0228 | -0.052455 | 0.013624 | 0.067051 | 0.076381 | -0.00076463 | -0.0022622 | -0.01575 | 0.051892 | 0.011445 | 0.063406 | 0.070737 | -0.011498 | -0.00049194 | -0.010022 | -0.10529 | 63.9038 | -60.1227 | 64.1052 | -60.0586 | -60.3745 | -60.3836 | -0.073242 | 63.9267 | -60.0861 | 64.3433 | -59.9762 | -60.1181 | -60.0586 | -0.073243 | -0.11902 | 0.082398 | -0.009156 | -0.33417 | -0.32501 | -0.26093 | -0.25177 | -0.036622 | -0.09613 | 0.32043 | 0.073242 | -0.009156 | -0.068665 | 0.027466 | -0.032043 | 0.064087 | 124.2279 | 0.10986 | 124.4293 | 124.0265 | 124.0128 | 123.9532 | 123.9761 | -124.1455 | -124.1089 | 124.1547 | 124.3927 | 59.9442 | 59.9762
355.9375 | 124.3103 | -60.0174 | 64.0823 | 0.084874 | 0.00080677 | 0.074528 | 0.067836 | 0.0099164 | 0.0084198 | 0.00027221 | 0.18922 | 0.00076419 | 0.0837 | 0.024808 | -0.007226 | 0.010189 | -0.0068176 | 0 | 63.9404 | -60.0906 | 64.1373 | -59.9945 | -60.3058 | -60.3195 | -0.004578 | 63.9771 | -60.0632 | 64.2288 | -60.0266 | -60.1456 | -60.0586 | -0.073242 | -0.14191 | 0.054932 | 0.022888 | -0.30212 | -0.28839 | -0.22888 | -0.21515 | -0.045776 | -0.10528 | 0.14648 | -0.009155 | -0.041199 | -0.12817 | 0.004577 | -0.082398 | 0.09613 | 124.2279 | 0.036621 | 124.292 | 124.0311 | 124.0402 | 123.9578 | 123.9944 | -124.173 | -124.1455 | 124.1547 | 124.2462 | 60.0174 | 60.0128
356.9375 | 124.3469 | -60.0174 | 64.1052 | 0.054357 | -0.0023982 | 0.065983 | 0.07104 | 0.0035084 | 0.0062828 | -0.0082728 | 0.235 | 0.00076419 | 0.053793 | 0.040829 | -0.007226 | 0.011257 | -0.024975 | 0.004578 | 63.9267 | -60.0998 | 64.1418 | -60.0082 | -60.3516 | -60.3241 | -0.009155 | 63.9908 | -60.0632 | 64.2242 | -59.9991 | -60.1273 | -60.0449 | -0.082397 | -0.17853 | 0.036621 | 0.009155 | -0.3067 | -0.33417 | -0.22431 | -0.25177 | -0.045776 | -0.11444 | 0.11902 | 0.018311 | -0.027466 | -0.10986 | 0.01831 | -0.064087 | 0.091552 | 124.2416 | 0.064087 | 124.2874 | 124.0265 | 124.054 | 123.9441 | 124.0082 | -124.205 | -124.1684 | 124.1592 | 124.2416 | 60.022 | 60.0082
357.9375 | 124.3378 | -59.9991 | 64.0503 | 0.039098 | -0.0034662 | 0.052097 | 0.07104 | 0.0035084 | -0.0022622 | -0.0029318 | 0.40284 | 0.0018322 | 0.065542 | 0.079282 | -0.006157 | 0.0016441 | 0.0017274 | 0.23804 | 64.0091 | -60.0403 | 64.1739 | -59.9899 | -60.3653 | -60.3333 | 0.004578 | 63.9908 | -60.0449 | 64.2517 | -60.0037 | -60.1181 | -60.0311 | -0.041199 | -0.041199 | 0.1236 | 0.009155 | -0.33417 | -0.36621 | -0.29297 | -0.32501 | -0.045777 | -0.059509 | 0.20142 | -0.004578 | -0.032044 | -0.11902 | 0.013733 | -0.073242 | 0.050354 | 124.2142 | 0.041199 | 124.2966 | 124.0494 | 124.0356 | 124.0082 | 123.9899 | -124.0906 | -124.0952 | 124.173 | 124.2508 | 60.2371 | 60.0037
358.9375 | 124.2966 | -59.9991 | 64.1235 | 0.20695 | 0.011488 | 0.063847 | 0.079585 | 0.016325 | -0.012943 | -0.0039998 | 0.11293 | -0.00030381 | 0.079428 | 0.11346 | -0.001885 | 0.0080531 | -0.02818 | -0.018311 | 63.945 | -60.0906 | 64.183 | -59.9487 | -60.2921 | -60.2829 | -0.059509 | 64.0091 | -60.0403 | 64.2151 | -60.0449 | -60.173 | -60.0861 | -0.091553 | -0.17853 | 0.059509 | 0.050354 | -0.28381 | -0.29297 | -0.19226 | -0.20142 | -0.041199 | -0.11444 | 0.091553 | -0.045777 | -0.086976 | -0.17395 | -0.045777 | -0.13275 | 0.14191 | 124.2737 | -0.004578 | 124.2554 | 124.0356 | 124.0494 | 123.9441 | 124.0082 | -124.2142 | -124.1638 | 124.1821 | 124.2142 | 59.9808 | 59.9396
359.9531 | 124.3423 | -60.0174 | 64.0366 | -0.021937 | 0.0061468 | 0.068119 | 0.082789 | -0.00076463 | -0.0065342 | -0.0039998 | 0.21974 | -0.010985 | 0.078359 | 0.045102 | -0.007226 | 0.0027121 | -0.014294 | -0.16479 | 63.9221 | -60.1089 | 64.1602 | -59.9991 | -60.3195 | -60.3424 | -0.15564 | 63.9816 | -60.0449 | 64.183 | -60.0861 | -60.1639 | -60.0586 | -0.091553 | -0.11444 | 0.1236 | 0.018311 | -0.32501 | -0.30212 | -0.23346 | -0.21057 | -0.027466 | -0.054932 | 0.14648 | -0.068665 | -0.041199 | -0.14648 | -0.013733 | -0.11902 | 0.10986 | 124.2691 | -0.041199 | 124.2279 | 124.0311 | 124.0265 | 123.9395 | 123.999 | -124.1455 | -124.0814 | 124.1776 | 124.2004 | 59.8526 | 59.8618
360.9375 | 124.379 | -60.0037 | 64.0686 | 0.084874 | -0.00026223 | 0.062778 | 0.077449 | 0.0067124 | -0.0011942 | -0.016818 | 0.32655 | 0.00076419 | 0.080496 | 0.062192 | -0.020043 | 0.0080531 | -0.0046806 | -0.041199 | 63.9496 | -60.0632 | 64.1418 | -60.0082 | -60.3287 | -60.3287 | -0.036621 | 63.9771 | -60.0266 | 64.1968 | -60.1089 | -60.1776 | -60.054 | -0.059509 | -0.11902 | 0.073242 | -0.004578 | -0.32501 | -0.32501 | -0.2655 | -0.2655 | -0.022888 | -0.091553 | 0.12817 | -0.10529 | -0.050354 | -0.17395 | -0.027466 | -0.15106 | 0.054931 | 124.205 | -0.082398 | 124.2233 | 124.0128 | 124.0036 | 123.9532 | 123.9807 | -124.1318 | -124.0952 | 124.1455 | 124.2004 | 59.9625 | 59.967
361.9375 | 124.379 | -59.9625 | 64.1052 | 0.10013 | 0.0040108 | 0.062778 | 0.072108 | 0.0077804 | -0.016147 | -0.00079579 | 0.31129 | -0.0035078 | 0.078359 | 0.036557 | -0.007226 | 0.00057606 | -0.01109 | -0.11902 | 63.9496 | -60.0677 | 64.1602 | -59.967 | -60.3104 | -60.2966 | -0.068665 | 64.0137 | -60.0494 | 64.2609 | -59.9899 | -60.1089 | -60.0357 | -0.10529 | -0.15564 | 0.054931 | -0.004578 | -0.33417 | -0.3479 | -0.22888 | -0.24262 | -0.086975 | -0.091553 | 0.15564 | -0.027466 | -0.073243 | -0.14648 | 0.013732 | -0.05951 | 0.10071 | 124.2279 | 0.059509 | 124.3103 | 124.0173 | 124.0631 | 123.912 | 123.9761 | -124.173 | -124.1547 | 124.1226 | 124.2233 | 59.8434 | 59.8938
362.9375 | 124.3423 | -59.967 | 64.0961 | 0.45109 | -0.0023982 | 0.06171 | 0.072108 | -0.0093096 | 0.0094878 | 0.0045452 | 0.14344 | -0.00030381 | 0.064474 | 0.058987 | -0.009362 | 0.0059161 | -0.017499 | -0.10529 | 64.0366 | -60.054 | 64.1464 | -60.0128 | -60.2921 | -60.2875 | -0.091553 | 63.9954 | -59.9854 | 64.2746 | -59.9808 | -60.0952 | -60.0082 | -0.086975 | -0.059509 | 0.050354 | -0.045776 | -0.32043 | -0.32501 | -0.23346 | -0.23804 | -0.018311 | -0.10071 | 0.17853 | -0.013733 | -0.041199 | -0.12817 | -0.022888 | -0.10986 | 0.041199 | 124.2004 | 0.004578 | 124.2599 | 124.0906 | 123.9807 | 124.0036 | 123.9624 | -124.1501 | -124.0814 | 124.1135 | 124.2416 | 59.8618 | 59.8755
363.9375 | 124.3286 | -59.9762 | 64.1052 | 0.13065 | 0.0029428 | 0.067051 | 0.081721 | -0.0093096 | 0.031918 | 0.0066812 | 0.20448 | 0.00076419 | 0.064474 | 0.031216 | -0.01043 | 0.014461 | -0.0014766 | -0.16937 | 63.9816 | -60.0357 | 64.0915 | -60.1501 | -60.3241 | -60.3058 | -0.14191 | 64.0274 | -60.0449 | 64.2883 | -59.9396 | -60.054 | -59.9762 | -0.05951 | -0.1236 | -0.013733 | -0.17395 | -0.32959 | -0.3479 | -0.27008 | -0.28839 | -0.068665 | -0.07782 | 0.1831 | 0.036621 | 0 | -0.07782 | 0.068665 | -0.009155 | -0.11444 | 124.1272 | 0.10529 | 124.3332 | 124.0173 | 124.0723 | 123.9578 | 124.0036 | -124.1409 | -124.1501 | 124.0677 | 124.2645 | 59.8068 | 59.8343
364.9375 | 124.2966 | -59.9625 | 64.1373 | 0.16117 | 0.013624 | 0.067051 | 0.07104 | 0.0035084 | -0.0011942 | -0.0039998 | 0.17396 | -0.0056438 | 0.067678 | 0.055783 | -0.011498 | 0.0091211 | 0.0027964 | -0.20599 | 63.9816 | -60.0449 | 64.2014 | -59.9396 | -60.26 | -60.26 | -0.18768 | 64.0411 | -60.0037 | 64.2654 | -59.9899 | -60.0998 | -60.0311 | -0.082398 | -0.15564 | 0.064087 | 0.022888 | -0.29755 | -0.29755 | -0.21515 | -0.21515 | -0.041199 | -0.09613 | 0.12817 | -0.027466 | -0.068665 | -0.13733 | -0.027466 | -0.09613 | 0.10529 | 124.2462 | 0.013733 | 124.2691 | 124.0265 | 124.0448 | 123.9441 | 124.0036 | -124.1821 | -124.1409 | 124.1638 | 124.2279 | 59.7565 | 59.7748
365.9375 | 124.3149 | -59.9487 | 64.1556 | 0.084874 | 0.0061468 | 0.051029 | 0.066768 | -0.013582 | -0.0043982 | 0.00027221 | 0.08241 | 0.0039692 | 0.064474 | 0.055783 | -0.002953 | -0.0015599 | -0.012158 | -0.29297 | 64.0045 | -60.0449 | 64.2014 | -59.9213 | -60.2783 | -60.2463 | -0.21057 | 64.0457 | -59.967 | 64.2792 | -59.9625 | -60.0677 | -60.0082 | -0.096131 | -0.15106 | 0.045776 | 0.027465 | -0.29755 | -0.32959 | -0.20142 | -0.23346 | -0.018311 | -0.10986 | 0.1236 | -0.013733 | -0.05951 | -0.11902 | -0.041199 | -0.10071 | 0.1236 | 124.2462 | 0.004578 | 124.2462 | 124.0494 | 124.0128 | 123.9532 | 123.9944 | -124.2004 | -124.1226 | 124.1501 | 124.2279 | 59.6558 | 59.7382
366.9375 | 124.324 | -59.935 | 64.1373 | 0.0085801 | 0.0082828 | 0.05637 | 0.075312 | 0.0035084 | 0.00094276 | 0.0066812 | 0.1587 | 0.0039692 | 0.082632 | 0.038693 | -0.017907 | 0.012325 | -0.0078856 | -0.39368 | 63.9862 | -60.054 | 64.2014 | -59.935 | -60.2692 | -60.2463 | -0.27466 | 64.0503 | -59.9945 | 64.3066 | -59.9396 | -60.0449 | -59.9854 | -0.11902 | -0.15106 | 0.064087 | 0 | -0.31128 | -0.33417 | -0.19226 | -0.21515 | -0.059509 | -0.086975 | 0.16937 | -0.004577 | -0.050354 | -0.10986 | 0.009155 | -0.050354 | 0.11902 | 124.2554 | 0.054932 | 124.3011 | 124.0402 | 124.0448 | 123.9212 | 123.9853 | -124.1913 | -124.1318 | 124.1364 | 124.2416 | 59.5413 | 59.6603
367.9375 | 124.2783 | -59.9533 | 64.1922 | 0.19169 | 0.00080677 | 0.062778 | 0.068904 | 0.0045764 | -0.0043982 | 0.0077492 | 0.14344 | 0.0029002 | 0.063406 | 0.067532 | 0.005592 | 0.0048481 | 0.0070684 | -0.46234 | 64.0182 | -60.0266 | 64.2654 | -59.8618 | -60.1959 | -60.1868 | -0.38452 | 64.0778 | -59.9854 | 64.2654 | -59.9899 | -60.1135 | -60.0174 | -0.073242 | -0.17395 | 0.073242 | 0.091553 | -0.23346 | -0.24262 | -0.16022 | -0.16937 | -0.032044 | -0.11444 | 0.073242 | -0.036621 | -0.064087 | -0.16022 | -0.032043 | -0.12817 | 0.16479 | 124.292 | -0.004577 | 124.2508 | 124.0448 | 124.0631 | 123.9716 | 124.0311 | -124.2188 | -124.1776 | 124.2188 | 124.2188 | 59.491 | 59.5688
368.9375 | 124.4247 | -59.9213 | 64.1418 | 0.14591 | -0.0066702 | 0.057438 | 0.075312 | -0.0029006 | 0.0094878 | -0.0093408 | 0.28077 | -0.0077808 | 0.067678 | 0.050442 | -0.005089 | 0.010189 | -0.012158 | -0.62256 | 64.0274 | -59.9899 | 64.2288 | -59.9487 | -60.2646 | -60.2554 | -0.3891 | 64.0594 | -59.9625 | 64.3707 | -59.8755 | -59.9808 | -59.935 | -0.068664 | -0.11444 | 0.086975 | -0.027465 | -0.33417 | -0.34332 | -0.2655 | -0.27466 | -0.041198 | -0.082398 | 0.22888 | 0.045777 | -0.013733 | -0.059509 | 0.027465 | -0.018311 | 0.041199 | 124.2188 | 0.086975 | 124.3332 | 124.0173 | 124.0219 | 123.9487 | 123.9807 | -124.1318 | -124.1043 | 124.1501 | 124.292 | 59.2987 | 59.5322
369.9688 | 124.2828 | -59.9442 | 64.2151 | 0.20695 | -0.0077382 | 0.068119 | 0.077449 | 0.013121 | -0.021488 | 0.0034762 | -0.024402 | 0.0082412 | 0.070883 | 0.062192 | -0.011498 | 0.0037801 | 0.017749 | -0.75073 | 64.064 | -59.9991 | 64.3707 | -59.7473 | -60.1089 | -60.1044 | -0.65002 | 64.1281 | -59.9854 | 64.2792 | -59.9808 | -60.1135 | -60.0037 | -0.054931 | -0.15106 | 0.15564 | 0.19684 | -0.16022 | -0.16479 | -0.10529 | -0.10986 | -0.041199 | -0.086975 | 0.064087 | -0.036621 | -0.059509 | -0.16937 | -0.01831 | -0.12817 | 0.25177 | 124.3698 | 0.004578 | 124.2645 | 124.0631 | 124.1135 | 124.0082 | 124.0723 | -124.2142 | -124.2004 | 124.3149 | 124.2233 | 59.1934 | 59.2941
370.9375 | 124.3378 | -59.9121 | 64.1739 | 0.10013 | -0.0013302 | 0.063847 | 0.081721 | 0.0045764 | 0.0062828 | -0.013613 | 0.25026 | -0.0024398 | 0.073019 | 0.047238 | -0.011498 | -0.0026279 | -0.018567 | -0.81024 | 64.0549 | -59.9625 | 64.2105 | -59.935 | -60.2417 | -60.2188 | -0.62714 | 64.0823 | -59.9487 | 64.595 | -60.1639 | -60.0769 | -59.9762 | -0.050354 | -0.11902 | 0.036621 | -0.022889 | -0.3067 | -0.32959 | -0.25635 | -0.27924 | -0.036621 | -0.091553 | 0.42114 | -0.25177 | -0.064087 | -0.16479 | -0.027466 | -0.12817 | 0.027465 | 124.173 | -0.21515 | 124.5438 | 124.0173 | 124.0311 | 123.967 | 123.9944 | -124.1364 | -124.1226 | 124.1226 | 124.5071 | 59.1019 | 59.285
371.9844 | 124.2828 | -59.903 | 64.2517 | 0.054357 | -0.0034662 | 0.075596 | 0.081721 | 0.00030337 | -0.030033 | 0.013089 | 0.14344 | 0.0039692 | 0.054861 | 0.054715 | -0.004021 | 0.013393 | -0.01109 | -0.97046 | 64.1006 | -59.9716 | 64.3341 | -59.8068 | -60.1593 | -60.1364 | -0.84228 | 64.1464 | -59.9487 | 64.2929 | -59.9533 | -60.1089 | -60.0128 | -0.068665 | -0.15106 | 0.082397 | 0.09613 | -0.23346 | -0.25635 | -0.1648 | -0.18768 | -0.045776 | -0.10529 | 0.041199 | -0.050354 | -0.10986 | -0.20599 | -0.064087 | -0.16022 | 0.16479 | 124.3057 | -0.004578 | 124.2416 | 124.0723 | 124.0952 | 124.0036 | 124.0494 | -124.2233 | -124.2004 | 124.2371 | 124.1959 | 58.9325 | 59.0607
372.9375 | 124.3332 | -59.8755 | 64.2242 | -0.021937 | 0.0061468 | 0.07346 | 0.07104 | 0.010984 | 0.00094276 | -0.0050688 | 0.21974 | 0.00076419 | 0.074087 | 0.024808 | -0.007226 | 0.00057606 | 0.0038644 | -1.1627 | 64.1006 | -59.9121 | 64.27 | -59.8297 | -60.1868 | -60.2417 | -0.91095 | 64.0961 | -59.9121 | 64.3799 | -59.8618 | -59.9579 | -59.9121 | -0.036621 | -0.1236 | 0.045777 | 0.045776 | -0.36621 | -0.31128 | -0.32959 | -0.27466 | -0.036621 | -0.12817 | 0.15564 | 0.013733 | -0.036621 | -0.082398 | 0 | -0.045777 | 0.082397 | 124.1821 | 0.050354 | 124.292 | 124.0128 | 124.0082 | 123.9761 | 123.9716 | -124.1364 | -124.1364 | 124.1455 | 124.2554 | 58.7128 | 58.9645
373.9375 | 124.3698 | -59.8389 | 64.2242 | 0.10013 | 0.0018748 | 0.055302 | 0.076381 | -0.0082416 | -0.0097382 | -0.0061368 | -0.03966 | 0.0018322 | 0.067678 | 0.06326 | -0.016839 | 0.010189 | 0.010272 | -1.2863 | 64.0961 | -59.9442 | 64.2746 | -59.9991 | -60.1089 | -59.9442 | -1.1353 | 64.1098 | -59.903 | 64.4073 | -59.8114 | -59.967 | -59.8984 | -0.10529 | -0.12817 | 0.050354 | -0.16022 | -0.10529 | -0.27008 | 0 | -0.16479 | -0.064087 | -0.11444 | 0.18311 | 0.027466 | -0.059509 | -0.12817 | 0.004578 | -0.064087 | -0.054931 | 124.2188 | 0.091553 | 124.3103 | 124.0402 | 124.0128 | 123.9349 | 123.9487 | -124.1684 | -124.1272 | 124.1135 | 124.2462 | 58.5526 | 58.7036
374.9375 | 124.3515 | -59.8389 | 64.2334 | -0.0066789 | 0.0082828 | 0.06171 | 0.081721 | 0.0077804 | -0.02576 | -0.00079579 | 0.036633 | 0.0039692 | 0.059133 | 0.053647 | -0.001885 | 0.015529 | -0.016431 | -1.5564 | 64.0503 | -59.9533 | 64.27 | -59.8709 | -60.1959 | -60.2142 | -1.3687 | 64.1006 | -59.903 | 64.3478 | -60.054 | -59.8251 | -59.7748 | -0.11444 | -0.1831 | 0.036622 | -0.032044 | -0.37537 | -0.35706 | -0.26093 | -0.24262 | -0.064087 | -0.13275 | 0.11444 | -0.21515 | 0.064087 | 0.013733 | 0.12817 | 0.07782 | 0.082397 | 124.2233 | -0.15106 | 124.2508 | 124.0036 | 124.0036 | 123.8892 | 123.9395 | -124.1867 | -124.1364 | 124.1089 | 124.1867 | 58.2825 | 58.4702
375.9375 | 124.3698 | -59.8297 | 64.2197 | 0.13065 | 0.0040108 | 0.071323 | 0.078517 | 0.0024404 | 0.010556 | -0.017886 | 0.28077 | 0.0093092 | 0.068746 | 0.062192 | -0.009362 | 0.011257 | 0.0070684 | -1.7075 | 64.1235 | -59.935 | 64.3387 | -59.7885 | -60.1547 | -60.1501 | -1.5381 | 64.1647 | -59.8892 | 64.4302 | -59.8068 | -59.9167 | -59.8389 | -0.10529 | -0.096131 | 0.11902 | 0.041199 | -0.32043 | -0.32501 | -0.21515 | -0.21973 | -0.059509 | -0.054932 | 0.21057 | 0.022888 | -0.009155 | -0.086975 | 0.050354 | -0.027466 | 0.14648 | 124.2737 | 0.082397 | 124.3195 | 124.0585 | 124.054 | 123.9532 | 123.9944 | -124.1547 | -124.1089 | 124.1684 | 124.2599 | 58.1223 | 58.2916
376.9375 | 124.3835 | -59.8114 | 64.2654 | 0.084874 | 0.0029428 | 0.065983 | 0.067836 | 0.00030337 | 0.00094276 | -0.017886 | 0.21974 | -0.0045758 | 0.087973 | 0.025876 | -0.016839 | 0.0080531 | 0.0049324 | -1.8997 | 64.119 | -59.8984 | 64.3341 | -59.8206 | -60.173 | -60.1685 | -1.6113 | 64.1922 | -59.8526 | 64.4806 | -59.7519 | -59.8709 | -59.8068 | -0.086975 | -0.14648 | 0.068664 | -0.009156 | -0.35706 | -0.36163 | -0.27008 | -0.27466 | -0.041199 | -0.073242 | 0.21515 | 0.059509 | 0.004577 | -0.05951 | 0.045776 | -0.018311 | 0.077819 | 124.2325 | 0.10071 | 124.3332 | 124.0173 | 124.0448 | 123.9304 | 124.0036 | -124.1638 | -124.118 | 124.1455 | 124.292 | 57.9117 | 58.2001
377.9375 | 124.3698 | -59.7748 | 64.2609 | 0.10013 | -0.0034662 | 0.065983 | 0.078517 | 0.0088484 | 0.00094276 | 0.0056132 | 0.20448 | 0.0093092 | 0.063406 | 0.060055 | -0.01043 | 0.014461 | 0.022022 | -2.0966 | 64.1647 | -59.8663 | 64.3478 | -59.7885 | -60.1273 | -60.1364 | -1.8723 | 64.1922 | -59.8297 | 64.5081 | -59.7107 | -59.8434 | -59.7977 | -0.091553 | -0.09613 | 0.086975 | -0.013733 | -0.36163 | -0.35248 | -0.27008 | -0.26093 | -0.054932 | -0.068664 | 0.24719 | 0.064087 | -0.022888 | -0.068665 | 0.032044 | -0.013733 | 0.07782 | 124.2142 | 0.11902 | 124.3378 | 124.0311 | 124.0219 | 123.9395 | 123.967 | -124.1272 | -124.0906 | 124.1226 | 124.2828 | 57.6782 | 57.9025
378.9375 | 124.379 | -59.7702 | 64.27 | 0.14591 | 0.0050788 | 0.058506 | 0.082789 | 0.0024404 | -0.02042 | -0.01575 | 0.18922 | -0.0035078 | 0.06127 | 0.053647 | -0.01577 | 0.010189 | -0.012158 | -2.2705 | 64.1739 | -59.8663 | 64.3295 | -59.816 | -60.1227 | -60.1227 | -2.0325 | 64.2151 | -59.8114 | 64.4669 | -59.4223 | -60.022 | -59.9899 | -0.09613 | -0.096131 | 0.059509 | -0.045776 | -0.35248 | -0.35248 | -0.25635 | -0.25635 | -0.041198 | -0.054932 | 0.19684 | 0.3479 | -0.21973 | -0.25177 | -0.17853 | -0.21057 | 0.050354 | 124.1959 | 0.3891 | 124.2783 | 124.0402 | 124.0265 | 123.9441 | 123.9853 | -124.1364 | -124.0814 | 124.0997 | 124.2371 | 57.4997 | 57.7377
379.9375 | 124.2645 | -59.816 | 64.3295 | 0.16117 | 0.0018748 | 0.072392 | 0.089198 | -0.0029006 | 0.012692 | 0.0045452 | -0.13121 | 0.010377 | 0.064474 | 0.038693 | -0.012566 | 0.0091211 | -0.0025446 | -2.5589 | 64.2059 | -59.8938 | 64.4577 | -59.6695 | -60.022 | -59.9945 | -2.3621 | 64.2517 | -59.8572 | 64.4806 | -59.8206 | -59.9854 | -59.8801 | -0.07782 | -0.1236 | 0.12817 | 0.14648 | -0.17853 | -0.20599 | -0.10071 | -0.12817 | -0.041199 | -0.07782 | 0.15106 | -0.004578 | -0.064087 | -0.16937 | -0.022888 | -0.12817 | 0.2243 | 124.3515 | 0.036621 | 124.3378 | 124.0997 | 124.1089 | 124.0219 | 124.0677 | -124.2233 | -124.1867 | 124.2737 | 124.2966 | 57.2571 | 57.4539
380.9375 | 124.3881 | -59.7427 | 64.3204 | 0.19169 | 0.0040108 | 0.057438 | 0.074244 | -0.024263 | -0.0086702 | -0.0018638 | 0.28077 | 0.0061052 | 0.078359 | 0.048306 | -0.008294 | 0.0059161 | -0.021771 | -2.8336 | 64.2151 | -59.8297 | 64.3753 | -59.7519 | -60.0723 | -60.0861 | -2.4582 | 64.2151 | -59.7656 | 64.5401 | -59.697 | -59.8206 | -59.7565 | -0.086975 | -0.10529 | 0.054931 | -0.009155 | -0.34332 | -0.32959 | -0.25635 | -0.24262 | -0.022888 | -0.10529 | 0.21973 | 0.045777 | -0.013733 | -0.07782 | 0.009155 | -0.054932 | 0.07782 | 124.205 | 0.068665 | 124.3057 | 124.0448 | 123.9807 | 123.9578 | 123.9578 | -124.1501 | -124.086 | 124.118 | 124.2828 | 56.9092 | 57.2845
381.9375 | 124.3515 | -59.7382 | 64.3158 | 0.0085801 | -0.0013302 | 0.051029 | 0.07104 | 0.0088484 | -0.010807 | -0.0061368 | 0.14344 | -0.0067128 | 0.062338 | 0.036557 | -0.002953 | 0.0059161 | -0.0057486 | -3.1357 | 64.2197 | -59.8434 | 64.4302 | -59.6741 | -60.0494 | -60.0082 | -2.8107 | 64.2471 | -59.7885 | 64.476 | -59.7473 | -59.8709 | -59.7794 | -0.10529 | -0.09613 | 0.11444 | 0.064087 | -0.27008 | -0.31128 | -0.16479 | -0.20599 | -0.050354 | -0.068665 | 0.16022 | -0.009155 | -0.041199 | -0.13275 | 0.009155 | -0.082398 | 0.16937 | 124.2737 | 0.041199 | 124.2645 | 124.0631 | 124.0356 | 123.9578 | 123.9853 | -124.1592 | -124.1043 | 124.1684 | 124.2142 | 56.6025 | 56.9275
382.9375 | 124.3195 | -59.7336 | 64.3753 | 0.10013 | 0.0040108 | 0.064915 | 0.080653 | -0.017855 | -0.0011942 | 0.0045452 | 0.12819 | 0.00076419 | 0.070883 | 0.04617 | -0.002953 | 0.010189 | -0.0036126 | -3.4561 | 64.2059 | -59.7931 | 64.4897 | -59.6741 | -60.0037 | -59.9899 | -3.0899 | 64.2426 | -59.7748 | 64.4943 | -59.729 | -59.8572 | -59.7839 | -0.059509 | -0.16937 | 0.11444 | 0.05951 | -0.25635 | -0.27008 | -0.19684 | -0.21057 | -0.041198 | -0.13275 | 0.11902 | 0.004578 | -0.050354 | -0.1236 | -0.009156 | -0.082398 | 0.11902 | 124.2828 | 0.045776 | 124.2691 | 123.999 | 124.0173 | 123.9395 | 123.9761 | -124.1684 | -124.1501 | 124.2233 | 124.2279 | 56.2775 | 56.6437
383.9688 | 124.2416 | -59.761 | 64.4211 | 0.11539 | 0.00080677 | 0.059574 | 0.073176 | -0.0039686 | 0.0041468 | 0.0088172 | 0.036633 | 0.0029002 | 0.069815 | 0.086758 | -0.006157 | 0.014461 | -0.0014766 | -3.685 | 64.3021 | -59.7885 | 64.5721 | -59.5276 | -59.903 | -59.8938 | -3.2455 | 64.3341 | -59.7473 | 64.4623 | -59.7702 | -59.9167 | -59.8434 | -0.027466 | -0.11902 | 0.15106 | 0.23346 | -0.13275 | -0.14191 | -0.10529 | -0.11444 | 0.013733 | -0.086976 | 0.041198 | -0.009156 | -0.082398 | -0.15564 | -0.096131 | -0.16937 | 0.26093 | 124.3607 | -0.022889 | 124.2096 | 124.0906 | 124.0814 | 124.0631 | 124.0952 | -124.2096 | -124.1684 | 124.3332 | 124.2233 | 56.076 | 56.5155
384.9375 | 124.2737 | -59.7061 | 64.3936 | 0.084874 | 0.0061468 | 0.064915 | 0.082789 | 0.0088484 | 0.00094276 | -0.0039998 | -0.070178 | 0.0018322 | 0.062338 | 0.064328 | -0.005089 | 0.0080531 | -0.01109 | -3.9505 | 64.2838 | -59.8343 | 64.5813 | -59.5825 | -59.9579 | -59.9487 | -3.3966 | 64.3341 | -59.761 | 64.4943 | -59.7565 | -59.9121 | -59.7794 | -0.12817 | -0.10986 | 0.18768 | 0.1236 | -0.24261 | -0.25177 | -0.11444 | -0.1236 | -0.054931 | -0.05951 | 0.10071 | -0.050354 | -0.073242 | -0.20599 | -0.018311 | -0.15106 | 0.25177 | 124.4156 | 0.004577 | 124.2554 | 124.118 | 124.0952 | 123.9899 | 124.0402 | -124.2279 | -124.1547 | 124.2874 | 124.2004 | 55.7556 | 56.3095
385.9375 | 124.3744 | -59.6832 | 64.4028 | 0.13065 | 0.0029428 | 0.062778 | 0.072108 | 0.0099164 | -0.0022622 | -0.020022 | 0.26551 | -0.0056438 | 0.075155 | 0.039761 | 0.00025105 | 0.0048481 | -0.0025446 | -4.2343 | 64.27 | -59.7702 | 64.4806 | -59.6329 | -59.9808 | -59.967 | -3.6163 | 64.3112 | -59.7519 | 64.5721 | -59.6558 | -59.7656 | -59.6878 | -0.086975 | -0.13275 | 0.07782 | 0.050354 | -0.28381 | -0.29755 | -0.19684 | -0.21057 | -0.068664 | -0.091553 | 0.16937 | 0.027466 | -0.004577 | -0.082397 | 0.064087 | -0.013733 | 0.13733 | 124.2508 | 0.09613 | 124.324 | 124.0402 | 124.0631 | 123.9532 | 123.9944 | -124.173 | -124.1547 | 124.1638 | 124.2554 | 55.4489 | 56.0669
386.9375 | 124.3469 | -59.6741 | 64.4165 | 0.039098 | 0.0018748 | 0.060642 | 0.081721 | 0.0056444 | 0.0073508 | -0.012545 | 0.1587 | 0.0050372 | 0.075155 | 0.041897 | -0.011498 | 0.0069851 | -0.022839 | -4.5273 | 64.3021 | -59.729 | 64.4989 | -59.5963 | -59.9625 | -59.9716 | -3.8177 | 64.3066 | -59.7198 | 64.5859 | -59.6283 | -59.7702 | -59.6878 | -0.054932 | -0.11444 | 0.082397 | 0.07782 | -0.29755 | -0.28839 | -0.24261 | -0.23346 | -0.045777 | -0.10986 | 0.16937 | 0.045776 | -0.013733 | -0.096131 | 0.032044 | -0.050354 | 0.13275 | 124.2279 | 0.091553 | 124.3057 | 124.0311 | 124.0265 | 123.9761 | 123.9807 | -124.1455 | -124.1364 | 124.173 | 124.2599 | 55.1468 | 55.8563
387.9375 | 124.3469 | -59.6558 | 64.4348 | 0.20695 | -0.0034662 | 0.052097 | 0.076381 | 0.0013714 | -0.0097382 | -0.011477 | 0.17396 | -0.0088488 | 0.071951 | 0.056851 | -0.01043 | 0.0059161 | -0.0014766 | -4.7653 | 64.3158 | -59.7107 | 64.5218 | -59.5596 | -59.9121 | -59.9213 | -4.2526 | 64.3707 | -59.6741 | 64.5813 | -59.6512 | -59.7794 | -59.6741 | -0.054931 | -0.11902 | 0.086976 | 0.096131 | -0.2655 | -0.25635 | -0.21057 | -0.20142 | -0.01831 | -0.064086 | 0.14648 | 0.004578 | -0.01831 | -0.1236 | 0 | -0.10529 | 0.15106 | 124.2325 | 0.022888 | 124.2554 | 124.0265 | 124.0448 | 123.9716 | 124.0265 | -124.1455 | -124.1089 | 124.1776 | 124.2371 | 54.8904 | 55.4031
388.9375 | 124.3332 | -59.6375 | 64.444 | 0.023839 | 0.0093518 | 0.059574 | 0.077449 | -0.00076463 | 0.0084198 | 0.0013402 | 0.18922 | -0.00030381 | 0.069815 | 0.067532 | -0.005089 | -0.00049194 | 0.017749 | -5.0674 | 64.3066 | -59.7153 | 64.5493 | -59.5505 | -59.9121 | -59.935 | -4.5731 | 64.3433 | -59.7015 | 64.5813 | -59.6512 | -59.7794 | -59.7015 | -0.07782 | -0.13733 | 0.10529 | 0.086975 | -0.29755 | -0.27466 | -0.21973 | -0.19684 | -0.064087 | -0.10071 | 0.13733 | -0.013733 | -0.064087 | -0.14191 | 0 | -0.07782 | 0.16479 | 124.2645 | 0.050354 | 124.2828 | 124.0219 | 124.0448 | 123.9441 | 123.9807 | -124.1592 | -124.1455 | 124.1867 | 124.2188 | 54.57 | 55.0644
389.9375 | 124.3561 | -59.5688 | 64.4806 | 0.10013 | 0.0061468 | 0.065983 | 0.063563 | -0.0093096 | -0.00012524 | 0.0045452 | 0.14344 | 0.0029002 | 0.059133 | 0.030148 | -0.007226 | 0.0048481 | -0.0078856 | -5.2002 | 64.357 | -59.6695 | 64.5309 | -59.5779 | -59.9304 | -59.8526 | -4.7699 | 64.3753 | -59.6786 | 64.6454 | -59.5322 | -59.6741 | -59.6191 | -0.10071 | -0.1236 | 0.050354 | -0.009155 | -0.28381 | -0.36163 | -0.18311 | -0.26093 | -0.10986 | -0.10529 | 0.16479 | 0.036621 | -0.050354 | -0.10529 | 0.059509 | 0.004578 | 0.091553 | 124.2004 | 0.14648 | 124.324 | 124.0265 | 124.054 | 123.9258 | 123.9441 | -124.1501 | -124.1592 | 124.0997 | 124.2142 | 54.3686 | 54.7989
390.9375 | 124.3195 | -59.61 | 64.5081 | 0.069615 | 0.0018748 | 0.065983 | 0.079585 | 0.010984 | -0.0065342 | -0.014682 | 0.18922 | 0.00076419 | 0.077291 | 0.060055 | -0.01043 | 0.013393 | -0.0057486 | -5.5756 | 64.3662 | -59.6741 | 64.5859 | -59.491 | -59.8526 | -59.8663 | -5.0629 | 64.389 | -59.6283 | 64.6454 | -59.6054 | -59.7473 | -59.6558 | -0.064087 | -0.14191 | 0.077819 | 0.11902 | -0.25635 | -0.24262 | -0.19226 | -0.17853 | -0.018311 | -0.11902 | 0.13733 | 0.004577 | -0.045777 | -0.13733 | -0.027466 | -0.11902 | 0.18311 | 124.2599 | 0.022888 | 124.2737 | 124.0402 | 124.0173 | 123.9761 | 123.999 | -124.1821 | -124.1364 | 124.1959 | 124.2554 | 54.0344 | 54.5471
391.9375 | 124.292 | -59.5871 | 64.4669 | 0.10013 | -0.00026223 | 0.068119 | 0.073176 | -0.0082416 | -0.0065342 | 0.0056132 | 0.1587 | 0.0050372 | 0.065542 | 0.056851 | -0.017907 | 0.0048481 | -0.012158 | -5.8319 | 64.3707 | -59.6603 | 64.6271 | -59.4681 | -59.8434 | -59.8389 | -5.2643 | 64.4119 | -59.6054 | 64.65 | -59.5596 | -59.7427 | -59.6649 | -0.073242 | -0.09613 | 0.16022 | 0.11902 | -0.25177 | -0.25635 | -0.17853 | -0.18311 | -0.018311 | -0.054932 | 0.1831 | 0.027466 | -0.07782 | -0.15564 | -0.059509 | -0.13733 | 0.19226 | 124.2874 | 0.045777 | 124.2554 | 124.0311 | 124.0173 | 123.9578 | 123.999 | -124.1272 | -124.0723 | 124.2142 | 124.2371 | 53.7552 | 54.3228
392.9375 | 124.3286 | -59.5505 | 64.5218 | 0.054357 | 0.0029428 | 0.058506 | 0.076381 | 0.019529 | -0.026828 | -0.016818 | -0.024402 | 0.0061052 | 0.091177 | 0.033353 | -0.008294 | 0.011257 | -0.017499 | -6.1295 | 64.389 | -59.642 | 64.6454 | -59.4589 | -59.8434 | -59.8297 | -5.6168 | 64.4257 | -59.6146 | 64.6454 | -59.5688 | -59.7153 | -59.6191 | -0.091553 | -0.13275 | 0.1236 | 0.091553 | -0.27924 | -0.29297 | -0.18768 | -0.20142 | -0.064087 | -0.096131 | 0.1236 | -0.018311 | -0.068665 | -0.16479 | -0.004578 | -0.10071 | 0.18311 | 124.2874 | 0.045776 | 124.2599 | 124.0311 | 124.0402 | 123.9395 | 123.9761 | -124.1638 | -124.1364 | 124.1959 | 124.1959 | 53.421 | 53.9337
393.9375 | 124.2966 | -59.5596 | 64.5264 | 0.084874 | 0.012556 | 0.065983 | 0.077449 | 0.020598 | 0.018033 | -0.014682 | 0.036633 | -0.0045758 | 0.06661 | 0.060055 | -0.009362 | 0.011257 | -0.0068176 | -6.3629 | 64.4211 | -59.6329 | 64.6774 | -59.4406 | -59.7977 | -59.8572 | -5.8914 | 64.4714 | -59.5871 | 64.6545 | -59.5642 | -59.697 | -59.6008 | -0.073243 | -0.10528 | 0.15106 | 0.11902 | -0.29755 | -0.23804 | -0.2243 | -0.16479 | -0.027466 | -0.054931 | 0.12817 | -0.004578 | -0.041199 | -0.13733 | -0.013733 | -0.10986 | 0.19226 | 124.3103 | 0.022888 | 124.2416 | 124.054 | 124.0585 | 123.9807 | 124.0311 | -124.1592 | -124.1135 | 124.2371 | 124.2142 | 53.1967 | 53.6682
394.9375 | 124.3835 | -59.5001 | 64.5538 | 0.10013 | -0.010943 | 0.052097 | 0.078517 | 0.00030337 | 0.01376 | -0.0039998 | 0.08241 | 0.0039692 | 0.063406 | 0.048306 | -0.018975 | 0.012325 | -0.0014766 | -6.5872 | 64.4302 | -59.5963 | 64.6362 | -59.4681 | -59.8343 | -59.8251 | -6.0745 | 64.4852 | -59.5642 | 64.769 | -59.4498 | -59.5825 | -59.5001 | -0.09613 | -0.1236 | 0.082397 | 0.032043 | -0.32501 | -0.33417 | -0.22888 | -0.23804 | -0.064087 | -0.068665 | 0.21515 | 0.050354 | 0 | -0.082398 | 0.064087 | -0.018311 | 0.12817 | 124.2325 | 0.11444 | 124.3332 | 124.0265 | 124.0494 | 123.9304 | 123.9853 | -124.1501 | -124.118 | 124.1364 | 124.2691 | 52.9129 | 53.4256
395.9375 | 124.3469 | -59.5276 | 64.5401 | 0.0085801 | 0.00080677 | 0.064915 | 0.078517 | 0.0035084 | -0.014011 | -0.0029318 | 0.29603 | -0.0099168 | 0.078359 | 0.038693 | -0.005089 | 0.012325 | -0.018567 | -6.9214 | 64.4394 | -59.5871 | 64.595 | -59.4864 | -59.7885 | -60.0128 | -6.3492 | 64.4714 | -59.523 | 64.7461 | -59.5001 | -59.6466 | -59.5551 | -0.059509 | -0.10071 | 0.054932 | 0.041199 | -0.48523 | -0.26093 | -0.42572 | -0.20142 | 0.004578 | -0.068664 | 0.20599 | 0.027466 | -0.027466 | -0.11902 | -0.032044 | -0.1236 | 0.10071 | 124.1821 | 0.022888 | 124.2691 | 124.0265 | 123.9944 | 123.967 | 123.999 | -124.1272 | -124.0631 | 124.1226 | 124.2737 | 52.6062 | 53.1784
396.9375 | 124.3469 | -59.4772 | 64.5584 | 0.054357 | 0.012556 | 0.060642 | 0.083857 | 0.0099164 | -0.015079 | -0.017886 | 0.0061157 | -0.0056438 | 0.067678 | 0.050442 | -0.007226 | 0.014461 | -0.0014766 | -7.1915 | 64.4211 | -59.5734 | 64.65 | -59.4543 | -59.7977 | -59.8114 | -6.7932 | 64.5126 | -59.5322 | 64.7781 | -59.4681 | -59.61 | -59.5276 | -0.09613 | -0.13733 | 0.091552 | 0.022888 | -0.33417 | -0.32043 | -0.23804 | -0.2243 | -0.054932 | -0.045777 | 0.21973 | 0.009155 | -0.050354 | -0.13275 | 0.004578 | -0.077819 | 0.11902 | 124.2233 | 0.064087 | 124.3103 | 123.9944 | 124.0448 | 123.8983 | 123.9899 | -124.1318 | -124.0906 | 124.1272 | 124.2554 | 52.2858 | 52.684
397.9375 | 124.3378 | -59.4452 | 64.5996 | 0.14591 | 0.01042 | 0.060642 | 0.083857 | 0.013121 | 0.0041468 | -0.0050688 | -0.03966 | 0.0029002 | 0.073019 | 0.078213 | -0.014702 | 0.010189 | -0.010022 | -7.4844 | 64.4531 | -59.5322 | 64.7049 | -59.4269 | -59.7931 | -59.8114 | -7.0953 | 64.5035 | -59.5276 | 64.8102 | -59.4177 | -59.5688 | -59.4589 | -0.086976 | -0.14648 | 0.10529 | 0.01831 | -0.36621 | -0.3479 | -0.27923 | -0.26093 | -0.082398 | -0.09613 | 0.21057 | 0.027465 | -0.013733 | -0.1236 | 0.068665 | -0.041199 | 0.10529 | 124.2371 | 0.10986 | 124.3378 | 123.9853 | 124.0311 | 123.8983 | 123.9487 | -124.1318 | -124.1272 | 124.1501 | 124.2554 | 51.9608 | 52.3499
398.9375 | 124.3423 | -59.4177 | 64.5996 | -0.0066789 | -0.0034662 | 0.069187 | 0.077449 | -0.01465 | -0.0076022 | 0.0034762 | -0.070178 | -0.013121 | 0.073019 | 0.075009 | -0.012566 | 0.010189 | -0.021771 | -7.7316 | 64.4989 | -59.5276 | 64.6866 | -59.3994 | -59.761 | -59.7656 | -7.6172 | 64.5401 | -59.4864 | 64.8697 | -59.3445 | -59.5505 | -59.4543 | -0.10986 | -0.10071 | 0.086975 | 0.018311 | -0.3479 | -0.34332 | -0.23804 | -0.23346 | -0.068664 | -0.059509 | 0.27008 | 0.073243 | -0.036621 | -0.13275 | 0.032043 | -0.064087 | 0.12817 | 124.2142 | 0.14191 | 124.3561 | 124.0265 | 124.0265 | 123.9166 | 123.9578 | -124.1272 | -124.086 | 124.1043 | 124.2874 | 51.6861 | 51.8005
399.9375 | 124.3286 | -59.4131 | 64.6362 | 0.16117 | 0.0029428 | 0.067051 | 0.078517 | 0.00030337 | -0.012943 | 0.0013402 | 0.021375 | -0.00030381 | 0.070883 | 0.073941 | -0.01577 | 0.0048481 | 0.013477 | -7.901 | 64.5309 | -59.4772 | 64.682 | -59.3857 | -59.7427 | -59.7473 | -7.9422 | 64.5676 | -59.4498 | 64.8514 | -59.3765 | -59.5459 | -59.436 | -0.064087 | -0.10528 | 0.045777 | 0.027466 | -0.33417 | -0.32959 | -0.27008 | -0.2655 | -0.036621 | -0.068664 | 0.21515 | 0.036621 | -0.022888 | -0.13275 | 0.013733 | -0.09613 | 0.091553 | 124.1592 | 0.073242 | 124.3011 | 124.0082 | 124.0173 | 123.9441 | 123.9807 | -124.1135 | -124.086 | 124.0952 | 124.2645 | 51.5121 | 51.4709
400.9375 | 124.3103 | -59.3628 | 64.6957 | 0.023839 | -0.0013302 | 0.072392 | 0.081721 | -0.01465 | -0.010807 | -0.014682 | -0.03966 | 0.0018322 | 0.060202 | 0.062192 | -0.018975 | 0.026211 | -0.0078856 | -8.5052 | 64.5447 | -59.436 | 64.7415 | -59.4589 | -59.8251 | -59.6512 | -8.3313 | 64.6179 | -59.3903 | 64.8651 | -59.3124 | -59.4818 | -59.3536 | -0.073242 | -0.15106 | 0.045776 | -0.09613 | -0.28839 | -0.46234 | -0.21515 | -0.3891 | -0.027466 | -0.07782 | 0.16937 | 0.050354 | 0.009155 | -0.11902 | 0.036621 | -0.091553 | -0.022888 | 124.1776 | 0.07782 | 124.2554 | 123.9807 | 124.0082 | 123.9075 | 123.9807 | -124.1318 | -124.086 | 124.1043 | 124.2279 | 50.8575 | 51.0315
401.9375 | 124.3561 | -59.2941 | 64.7324 | 0.0085801 | 0.00080677 | 0.067051 | 0.079585 | -0.010378 | -0.016147 | -0.024295 | 0.036633 | 0.0039692 | 0.073019 | 0.073941 | -0.01043 | 0.018734 | 0.0038644 | -9.0729 | 64.563 | -59.4315 | 64.7873 | -59.2758 | -59.6741 | -59.6603 | -8.6838 | 64.6271 | -59.3719 | 64.9292 | -59.1476 | -59.3353 | -59.3124 | -0.13733 | -0.16937 | 0.054931 | 0.01831 | -0.36621 | -0.37994 | -0.22888 | -0.24261 | -0.07782 | -0.10529 | 0.19684 | 0.14648 | -0.018311 | -0.041199 | 0.059509 | 0.036621 | 0.15564 | 124.2188 | 0.2243 | 124.3011 | 123.9944 | 123.999 | 123.8571 | 123.9212 | -124.1638 | -124.1043 | 124.0814 | 124.2233 | 50.2213 | 50.6104
402.9375 | 124.3103 | -59.3079 | 64.7598 | 0.039098 | 0.0018748 | 0.053165 | 0.084926 | 0.0035084 | -0.017215 | -0.013613 | -0.070178 | -0.0045758 | 0.071951 | 0.021603 | -0.008294 | 0.0059161 | -0.0004086 | -9.4437 | 64.6774 | -59.4177 | 64.9292 | -59.1385 | -59.5459 | -59.5505 | -9.0225 | 64.6957 | -59.3765 | 64.92 | -59.2987 | -59.4635 | -59.3445 | -0.10986 | -0.082398 | 0.16937 | 0.16937 | -0.24262 | -0.23804 | -0.13275 | -0.12817 | -0.068665 | -0.064087 | 0.16022 | 0.009155 | -0.036621 | -0.15564 | 0.032044 | -0.086975 | 0.27924 | 124.3469 | 0.07782 | 124.2966 | 124.0952 | 124.0723 | 123.9853 | 124.0036 | -124.1776 | -124.1364 | 124.2371 | 124.2279 | 49.8642 | 50.2853
403.9375 | 124.324 | -59.2575 | 64.7552 | 0.0085801 | 0.0018748 | 0.069187 | 0.076381 | -0.021059 | -0.0097382 | 0.0013402 | -0.03966 | -0.0088488 | 0.070883 | 0.039761 | -0.012566 | 0.018734 | 0.0027964 | -9.6268 | 64.6683 | -59.3674 | 64.8331 | -59.1888 | -59.5596 | -59.5825 | -9.2011 | 64.7095 | -59.3262 | 64.9979 | -59.2117 | -59.404 | -59.2804 | -0.10986 | -0.086975 | 0.07782 | 0.068664 | -0.32501 | -0.30212 | -0.21515 | -0.19226 | -0.068665 | -0.045776 | 0.24262 | 0.045776 | -0.022889 | -0.14649 | 0.045776 | -0.07782 | 0.17853 | 124.2004 | 0.11444 | 124.324 | 124.0356 | 124.0356 | 123.9258 | 123.967 | -124.1226 | -124.0814 | 124.0906 | 124.2554 | 49.6307 | 50.0565
404.9375 | 124.3469 | -59.2438 | 64.801 | 0.10013 | 0.0029428 | 0.063847 | 0.073176 | 0.0056444 | 0.0084198 | -0.0050688 | -0.14647 | -0.0067128 | 0.065542 | 0.070737 | -0.016839 | 0.015529 | -0.015362 | -9.8602 | 64.7232 | -59.3536 | 64.9338 | -59.1248 | -59.5139 | -59.5367 | -9.5078 | 64.7369 | -59.2896 | 65.0208 | -59.198 | -59.3765 | -59.2529 | -0.10986 | -0.077819 | 0.13275 | 0.11902 | -0.29297 | -0.27008 | -0.18311 | -0.16022 | -0.045777 | -0.064087 | 0.21973 | 0.045776 | -0.009156 | -0.13275 | 0.036621 | -0.086975 | 0.22888 | 124.2874 | 0.091553 | 124.3103 | 124.0768 | 124.0265 | 123.967 | 123.9807 | -124.1547 | -124.0906 | 124.1776 | 124.2645 | 49.3835 | 49.736
405.9375 | 124.3103 | -59.2117 | 64.8331 | 0.13065 | -0.0066702 | 0.063847 | 0.080653 | 0.0067124 | -0.0011942 | -0.013613 | 0.0061157 | 0.0082412 | 0.074087 | 0.079282 | 0.00025105 | 0.011257 | -0.0057486 | -10.0983 | 64.7415 | -59.3079 | 65.007 | -59.0378 | -59.4498 | -59.4681 | -9.8053 | 64.769 | -59.2758 | 65.0299 | -59.1751 | -59.3353 | -59.2072 | -0.09613 | -0.091553 | 0.17395 | 0.17395 | -0.25635 | -0.23804 | -0.16022 | -0.14191 | -0.064087 | -0.064087 | 0.19684 | 0.036621 | 0.004578 | -0.1236 | 0.068665 | -0.059509 | 0.27008 | 124.3149 | 0.10071 | 124.3057 | 124.0494 | 124.0448 | 123.9532 | 123.9807 | -124.1409 | -124.1089 | 124.2188 | 124.2416 | 49.1135 | 49.4064
406.9375 | 124.3469 | -59.1888 | 64.8651 | -0.021937 | 0.0050788 | 0.064915 | 0.079585 | 0.0035084 | -0.0011942 | -0.0072048 | 0.051892 | -0.0099168 | 0.063406 | 0.086758 | -0.012566 | 0.010189 | -0.016431 | -10.2859 | 64.7598 | -59.2621 | 64.9612 | -59.0881 | -59.5047 | -59.4955 | -10.0388 | 64.7827 | -59.2346 | 65.0757 | -59.1156 | -59.3033 | -59.1751 | -0.073242 | -0.10528 | 0.096131 | 0.10071 | -0.3067 | -0.31586 | -0.23346 | -0.24262 | -0.045776 | -0.082397 | 0.21057 | 0.073242 | 0.013733 | -0.11444 | 0.059509 | -0.068665 | 0.17395 | 124.2233 | 0.11902 | 124.3103 | 124.0219 | 124.0173 | 123.9487 | 123.9716 | -124.1272 | -124.0997 | 124.1501 | 124.2645 | 48.9029 | 49.1501
407.9688 | 124.3607 | -59.1476 | 64.9338 | 0.11539 | -0.0045342 | 0.064915 | 0.084926 | 0.00030337 | -0.0065342 | -0.0039998 | 0.31129 | -0.00030381 | 0.082632 | 0.026944 | -0.008294 | 0.0037801 | -0.0089536 | -10.4095 | 64.7919 | -59.2026 | 65.0253 | -59.0286 | -59.4406 | -59.4498 | -10.2264 | 64.8605 | -59.1751 | 65.1306 | -59.0515 | -59.2346 | -59.1248 | -0.054932 | -0.14191 | 0.091553 | 0.11902 | -0.30212 | -0.29297 | -0.24719 | -0.23804 | -0.027466 | -0.073242 | 0.19684 | 0.09613 | 0.022888 | -0.086975 | 0.050354 | -0.059509 | 0.17395 | 124.2279 | 0.1236 | 124.3057 | 123.9944 | 124.0356 | 123.9395 | 124.0082 | -124.1364 | -124.1089 | 124.173 | 124.2783 | 48.7381 | 48.9212
408.9375 | 124.2599 | -59.1431 | 64.9475 | 0.054357 | -0.0013302 | 0.06171 | 0.082789 | 0.0024404 | 0.011624 | -0.0082728 | -0.16173 | 0.012514 | 0.069815 | 0.045102 | -0.007226 | 0.019802 | 0.01134 | -10.5972 | 64.8514 | -59.2209 | 65.1535 | -58.8913 | -59.3216 | -59.3216 | -10.556 | 64.9063 | -59.1797 | 65.0482 | -59.1614 | -59.3445 | -59.2072 | -0.07782 | -0.096131 | 0.20599 | 0.25177 | -0.17853 | -0.17853 | -0.10071 | -0.10071 | -0.036621 | -0.041199 | 0.10071 | -0.018311 | -0.064087 | -0.20142 | -0.027466 | -0.16479 | 0.32959 | 124.3744 | 0.01831 | 124.2279 | 124.0723 | 124.086 | 123.9944 | 124.0494 | -124.1684 | -124.1272 | 124.2966 | 124.1913 | 48.5458 | 48.587
409.9844 | 124.3423 | -59.0332 | 65.0116 | 0.054357 | -0.0013302 | 0.044621 | 0.087062 | -0.0039686 | 0.0084198 | -0.0039998 | 0.70802 | 0.00076419 | 0.085836 | 0.064328 | -0.011498 | 0.012325 | -0.015362 | -10.7391 | 64.8788 | -59.1019 | 65.0711 | -58.96 | -59.3719 | -59.3582 | -10.7941 | 64.9063 | -59.0973 | 65.1672 | -58.992 | -59.1156 | -59.0424 | -0.068665 | -0.13275 | 0.059509 | 0.073242 | -0.32501 | -0.33875 | -0.25635 | -0.27008 | -0.064087 | -0.10529 | 0.15564 | 0.041199 | -0.009155 | -0.082398 | 0.054932 | -0.018311 | 0.14191 | 124.173 | 0.10529 | 124.2645 | 123.9807 | 124.0036 | 123.912 | 123.9395 | -124.1135 | -124.1089 | 124.1043 | 124.2004 | 48.2941 | 48.2391
410.9375 | 124.2691 | -59.0515 | 65.0528 | 0.11539 | 0.0061468 | 0.06171 | 0.073176 | 0.0045764 | 0.0062828 | -0.0093408 | -0.1007 | 0.00076419 | 0.076223 | 0.050442 | -0.004021 | 0.015529 | -0.017499 | -11.0184 | 64.8972 | -59.1934 | 65.1947 | -58.8409 | -59.2621 | -59.285 | -10.9085 | 64.9338 | -59.111 | 65.1672 | -59.0378 | -59.2163 | -59.1156 | -0.14191 | -0.15564 | 0.14191 | 0.21057 | -0.23346 | -0.21057 | -0.091553 | -0.068665 | -0.059509 | -0.11902 | 0.11444 | 0.013733 | -0.064087 | -0.1648 | -0.004578 | -0.10529 | 0.35248 | 124.3881 | 0.073242 | 124.2783 | 124.0906 | 124.0448 | 123.9487 | 123.9853 | -124.2462 | -124.1638 | 124.2462 | 124.2188 | 48.0331 | 48.143
411.9375 | 124.2828 | -58.9966 | 65.0848 | 0.11539 | -0.0056022 | 0.059574 | 0.082789 | 0.0045764 | -0.0011942 | -0.01575 | 0.021375 | 0.0093092 | 0.064474 | 0.071805 | -0.009362 | 0.023006 | -0.01109 | -11.4487 | 65.007 | -59.0973 | 65.2771 | -58.7448 | -59.1614 | -59.1751 | -11.1008 | 65.007 | -59.0607 | 65.213 | -58.9828 | -59.1934 | -59.0561 | -0.10071 | -0.07782 | 0.19226 | 0.25177 | -0.17853 | -0.1648 | -0.07782 | -0.064087 | -0.064087 | -0.07782 | 0.12817 | 0.013733 | -0.059509 | -0.19684 | 0.004578 | -0.13275 | 0.35248 | 124.3744 | 0.07782 | 124.2737 | 124.1043 | 124.0677 | 124.0036 | 124.0036 | -124.1821 | -124.1455 | 124.2737 | 124.2096 | 47.5479 | 47.8958
412.9375 | 124.2462 | -58.9371 | 65.1306 | 0.19169 | 0.0040108 | 0.065983 | 0.079585 | -0.0018326 | -0.012943 | -0.016818 | -0.070178 | -0.0013718 | 0.086904 | 0.048306 | -0.01043 | 0.014461 | 0.0092044 | -11.673 | 65.0528 | -59.0286 | 65.3366 | -58.6578 | -59.111 | -59.1248 | -11.3068 | 65.0757 | -58.9828 | 65.2451 | -58.9417 | -59.1385 | -59.024 | -0.091552 | -0.07782 | 0.20599 | 0.27924 | -0.18768 | -0.17395 | -0.096131 | -0.082398 | -0.045776 | -0.054931 | 0.11444 | -0.004577 | -0.086975 | -0.20142 | -0.041199 | -0.15564 | 0.37079 | 124.3652 | 0.041199 | 124.2279 | 124.0814 | 124.0585 | 123.9899 | 124.0128 | -124.1592 | -124.1135 | 124.2737 | 124.1821 | 47.2641 | 47.6303
413.9375 | 124.3286 | -58.9096 | 65.1672 | -0.0066789 | 0.00080677 | 0.065983 | 0.090266 | 0.0056444 | -0.012943 | 0.0088172 | 0.0061157 | -0.0013718 | 0.073019 | 0.038693 | -0.007226 | 0.016598 | 0.0017274 | -11.8561 | 65.0757 | -59.0057 | 65.3366 | -58.6624 | -59.1248 | -59.1248 | -11.4304 | 65.1031 | -58.9371 | 65.3366 | -58.8409 | -59.0561 | -58.9279 | -0.09613 | -0.091552 | 0.16937 | 0.24719 | -0.21515 | -0.21515 | -0.11902 | -0.11902 | -0.027466 | -0.064087 | 0.16937 | 0.068665 | -0.01831 | -0.14648 | 0.009156 | -0.11902 | 0.34332 | 124.3423 | 0.096131 | 124.2737 | 124.0814 | 124.0402 | 123.9853 | 124.0128 | -124.173 | -124.1043 | 124.2462 | 124.2462 | 47.0535 | 47.4792
414.9375 | 124.3103 | -58.8776 | 65.213 | 0.17643 | -0.0056022 | 0.060642 | 0.079585 | 0.0088484 | -0.0054662 | -0.0093408 | 0.021375 | -0.00030381 | 0.086904 | 0.083554 | -0.004021 | 0.0048481 | 0.0006594 | -12.1078 | 65.1169 | -58.9691 | 65.4007 | -58.5983 | -59.0561 | -59.0607 | -11.6272 | 65.1443 | -58.8913 | 65.3458 | -58.8181 | -59.0424 | -58.9142 | -0.091553 | -0.096131 | 0.18768 | 0.27923 | -0.18311 | -0.17853 | -0.091553 | -0.086975 | -0.013733 | -0.068665 | 0.13275 | 0.059509 | -0.036622 | -0.16479 | -0.022889 | -0.15106 | 0.37079 | 124.3698 | 0.073242 | 124.2371 | 124.086 | 124.0356 | 123.9944 | 124.0219 | -124.1821 | -124.1043 | 124.2783 | 124.2233 | 46.7697 | 47.2504
415.9844 | 124.2828 | -58.8226 | 65.3 | 0.13065 | -0.0013302 | 0.057438 | 0.065699 | -0.018923 | 0.0020108 | -0.012545 | -0.024402 | 0.0082412 | 0.067678 | 0.065396 | -0.011498 | 0.0037801 | 0.014545 | -12.2543 | 65.1947 | -58.8913 | 65.4602 | -58.5205 | -58.9874 | -58.9783 | -11.7783 | 65.2313 | -58.8684 | 65.3915 | -58.7402 | -59.0012 | -58.8776 | -0.068664 | -0.10529 | 0.16022 | 0.30212 | -0.15564 | -0.16479 | -0.086975 | -0.096131 | -0.045776 | -0.068665 | 0.091553 | 0.082398 | -0.054931 | -0.17853 | -0.009155 | -0.13275 | 0.37079 | 124.3515 | 0.12817 | 124.2599 | 124.086 | 124.0997 | 124.0173 | 124.054 | -124.1913 | -124.1684 | 124.2828 | 124.2142 | 46.5683 | 47.0444
416.9375 | 124.2142 | -58.8089 | 65.3366 | 0.10013 | -0.0023982 | 0.060642 | 0.077449 | 0.0099164 | 0.0062828 | -0.00079579 | -0.11595 | -0.00030381 | 0.081564 | 0.066464 | -0.011498 | 0.014461 | 0.015613 | -12.4832 | 65.1993 | -58.8913 | 65.5334 | -58.4564 | -58.9279 | -58.9188 | -12.0712 | 65.2542 | -58.8593 | 65.3687 | -58.8043 | -59.0012 | -58.8776 | -0.082397 | -0.13733 | 0.19684 | 0.35248 | -0.10986 | -0.11902 | -0.027466 | -0.036621 | -0.050354 | -0.082398 | 0.032043 | 0.004578 | -0.068664 | -0.19226 | -0.01831 | -0.14191 | 0.43487 | 124.4247 | 0.054932 | 124.2279 | 124.0906 | 124.1135 | 124.0082 | 124.0631 | -124.2279 | -124.1959 | 124.3423 | 124.1776 | 46.3257 | 46.7377
417.9375 | 124.2508 | -58.7448 | 65.3687 | -0.021937 | -0.012011 | 0.055302 | 0.068904 | -0.0039686 | -0.0065342 | -0.011477 | -0.0091433 | -0.00030381 | 0.068746 | 0.053647 | -0.011498 | 0.021938 | -0.0004086 | -12.6709 | 65.2496 | -58.8547 | 65.6845 | -58.3008 | -58.9096 | -58.8913 | -12.3138 | 65.3091 | -58.7997 | 65.4282 | -58.7585 | -58.9783 | -58.8455 | -0.10986 | -0.11902 | 0.31586 | 0.44403 | -0.14648 | -0.16479 | -0.036621 | -0.054932 | -0.054932 | -0.059509 | 0.05951 | -0.013733 | -0.10071 | -0.23346 | -0.045776 | -0.17853 | 0.55389 | 124.5392 | 0.041199 | 124.2279 | 124.1043 | 124.1089 | 123.9944 | 124.054 | -124.2233 | -124.1684 | 124.4293 | 124.173 | 46.0739 | 46.431
418.9375 | 124.2325 | -58.7265 | 65.3778 | 0.10013 | 0.0018748 | 0.068119 | 0.075312 | -0.0039686 | 0.011624 | 0.0077492 | -0.070178 | 0.0018322 | 0.06127 | 0.061124 | -0.007226 | 0.011257 | 0.014545 | -12.886 | 65.2863 | -58.8043 | 65.6067 | -58.3878 | -58.8593 | -58.8684 | -12.9364 | 65.2542 | -58.7952 | 65.4648 | -58.6807 | -58.9142 | -58.8043 | -0.07782 | -0.091553 | 0.22888 | 0.33874 | -0.14191 | -0.13275 | -0.064087 | -0.054932 | -0.068665 | -0.1236 | 0.086975 | 0.045776 | -0.07782 | -0.18768 | -0.009155 | -0.11902 | 0.41656 | 124.411 | 0.11444 | 124.2599 | 124.0906 | 124.0494 | 124.0128 | 123.9807 | -124.1821 | -124.173 | 124.3332 | 124.1913 | 45.8405 | 45.7901
419.9375 | 124.2416 | -58.6578 | 65.4602 | 0.10013 | 0.00080677 | 0.069187 | 0.076381 | -0.00076463 | -0.012943 | -0.020022 | 0.021375 | -0.0024398 | 0.068746 | 0.069668 | -0.01043 | 0.011257 | 0.0038644 | -13.2751 | 65.3412 | -58.7906 | 65.625 | -58.3237 | -58.8181 | -58.8181 | -12.9959 | 65.3915 | -58.7265 | 65.3229 | -58.6761 | -58.6761 | -58.6075 | -0.13275 | -0.11902 | 0.16479 | 0.33417 | -0.16022 | -0.16022 | -0.027466 | -0.027466 | -0.068664 | -0.068664 | -0.13733 | -0.01831 | 0.050354 | -0.01831 | 0.11902 | 0.050354 | 0.46692 | 124.4156 | 0.050354 | 124.0494 | 124.1318 | 124.118 | 123.999 | 124.0494 | -124.2508 | -124.1867 | 124.2828 | 123.9807 | 45.3827 | 45.6619
420.9688 | 124.3515 | -58.5846 | 65.4556 | 0.054357 | -0.0066702 | 0.071323 | 0.066768 | -0.0029006 | -0.00012524 | -0.0061368 | 0.1587 | 0.0082412 | 0.078359 | 0.040829 | -0.007226 | 0.0069851 | 0.0081364 | -13.4354 | 65.3046 | -58.6853 | 65.5243 | -58.4473 | -58.8776 | -58.9233 | -12.8906 | 65.3595 | -58.6624 | 65.6479 | -58.461 | -58.7173 | -58.6258 | -0.10071 | -0.15106 | 0.068665 | 0.13733 | -0.33875 | -0.29297 | -0.23804 | -0.19226 | -0.07782 | -0.09613 | 0.19226 | 0.1236 | -0.041198 | -0.13275 | 0.036622 | -0.054931 | 0.23804 | 124.2096 | 0.20142 | 124.3103 | 123.9899 | 124.0219 | 123.8892 | 123.9441 | -124.1409 | -124.118 | 124.1089 | 124.2325 | 45.1492 | 45.694
421.9375 | 124.2599 | -58.5663 | 65.5289 | 0.054357 | 0.0018748 | 0.068119 | 0.076381 | 0.0013714 | -0.026828 | -0.00079579 | 0.067151 | 0.0050372 | 0.062338 | 0.0686 | -0.01043 | 0.0048481 | 0.01134 | -13.6871 | 65.4282 | -58.6807 | 65.7303 | -58.2413 | -58.7769 | -58.7265 | -13.4354 | 65.4694 | -58.6258 | 65.593 | -58.5342 | -58.786 | -58.6533 | -0.11444 | -0.10071 | 0.20142 | 0.32501 | -0.16022 | -0.21057 | -0.045776 | -0.09613 | -0.059509 | -0.05951 | 0.064087 | 0.032043 | -0.086975 | -0.21973 | -0.027466 | -0.16022 | 0.43945 | 124.411 | 0.091552 | 124.2188 | 124.1089 | 124.0952 | 123.9944 | 124.0356 | -124.2096 | -124.1547 | 124.2966 | 124.1592 | 44.8792 | 45.1309
422.9375 | 124.1913 | -58.5114 | 65.5701 | 0.10013 | 0.012556 | 0.062778 | 0.087062 | -0.015718 | -0.015079 | -0.010409 | -0.0091433 | 0.0071732 | 0.078359 | 0.034421 | -0.011498 | 0.0091211 | -0.0014766 | -13.8382 | 65.4785 | -58.6075 | 65.7715 | -58.1635 | -58.667 | -58.6533 | -13.623 | 65.506 | -58.5754 | 65.6113 | -58.5205 | -58.7448 | -58.6304 | -0.09613 | -0.091552 | 0.20142 | 0.3479 | -0.14191 | -0.15564 | -0.045776 | -0.059509 | -0.064086 | -0.064087 | 0.041199 | -0.009155 | -0.11902 | -0.23346 | -0.054932 | -0.16937 | 0.44403 | 124.379 | 0.054931 | 124.1867 | 124.086 | 124.0814 | 123.9899 | 124.0173 | -124.1776 | -124.1455 | 124.2828 | 124.1226 | 44.6732 | 44.8883
423.9375 | 124.2279 | -58.4564 | 65.6662 | 0.069615 | -0.010943 | 0.069187 | 0.07104 | 0.0088484 | -0.018283 | -0.010409 | 0.0061157 | 0.0061052 | 0.076223 | 0.025876 | -0.013634 | 0.0037801 | -0.010022 | -14.003 | 65.5289 | -58.5617 | 65.8173 | -58.1131 | -58.5938 | -58.6075 | -13.8107 | 65.5746 | -58.5251 | 65.712 | -58.3969 | -58.7311 | -58.5709 | -0.10529 | -0.13733 | 0.15106 | 0.34332 | -0.15106 | -0.13733 | -0.045776 | -0.032043 | -0.068664 | -0.091553 | 0.045776 | 0.059509 | -0.11444 | -0.27466 | -0.045777 | -0.20599 | 0.44861 | 124.379 | 0.12817 | 124.2371 | 124.0906 | 124.0997 | 123.9853 | 124.0311 | -124.2279 | -124.1913 | 124.2737 | 124.1684 | 44.4534 | 44.6457
424.9375 | 124.3561 | -58.4518 | 65.712 | 0.069615 | 0.017896 | 0.064915 | 0.078517 | 0.010984 | 0.0062828 | -0.0050688 | 0.067151 | 0.0039692 | 0.063406 | 0.057919 | -0.005089 | 0.010189 | -0.0078856 | -14.209 | 65.6204 | -58.5159 | 65.918 | -58.0399 | -58.5571 | -58.5526 | -14.0808 | 65.6158 | -58.4656 | 65.7303 | -58.3832 | -58.9005 | -58.7448 | -0.064087 | -0.091553 | 0.20599 | 0.41199 | -0.10071 | -0.10529 | -0.036621 | -0.041199 | -0.013733 | -0.09613 | 0.018311 | 0.068664 | -0.29297 | -0.44861 | -0.27924 | -0.43488 | 0.47607 | 124.4339 | 0.082397 | 124.1959 | 124.1364 | 124.0814 | 124.0723 | 124.0677 | -124.2279 | -124.1776 | 124.3698 | 124.1821 | 44.2429 | 44.371
425.9844 | 124.2828 | -58.3374 | 65.8173 | 0.20695 | -0.0077382 | 0.057438 | 0.083857 | 0.0024404 | -0.0086702 | 0.0024082 | 0.021375 | -0.0024398 | 0.078359 | 0.064328 | -0.01043 | 0.015529 | -0.013226 | -14.3005 | 65.6662 | -58.4061 | 65.9683 | -57.9712 | -58.461 | -58.4702 | -14.3829 | 65.7211 | -58.3511 | 65.8447 | -58.223 | -58.4839 | -58.3923 | -0.068665 | -0.15106 | 0.15106 | 0.36621 | -0.13275 | -0.1236 | -0.064087 | -0.054932 | -0.013733 | -0.096131 | 0.027466 | 0.11444 | -0.054932 | -0.14649 | -0.041199 | -0.13275 | 0.43488 | 124.3744 | 0.12817 | 124.1959 | 124.0723 | 124.0723 | 124.0036 | 124.0585 | -124.2233 | -124.1684 | 124.3057 | 124.1821 | 44.0369 | 43.9545
426.9375 | 124.1959 | -58.287 | 65.8218 | 0.084874 | 0.0040108 | 0.065983 | 0.082789 | -0.010378 | -0.00012524 | -0.0029318 | -0.054919 | 0.0029002 | 0.064474 | 0.078213 | -0.001885 | 0.016598 | -0.017499 | -14.5386 | 65.7166 | -58.4015 | 65.9912 | -57.9071 | -58.4244 | -58.4335 | -14.6713 | 65.744 | -58.3603 | 65.8447 | -58.2367 | -58.5205 | -58.3832 | -0.11444 | -0.10528 | 0.16937 | 0.37994 | -0.14648 | -0.13733 | -0.032044 | -0.022888 | -0.073243 | -0.077819 | 0.022889 | 0.050354 | -0.096131 | -0.23346 | -0.022888 | -0.16022 | 0.49439 | 124.3927 | 0.1236 | 124.205 | 124.118 | 124.1043 | 124.0036 | 124.0311 | -124.2233 | -124.1821 | 124.2783 | 124.1318 | 43.7485 | 43.6157
427.9375 | 124.2371 | -58.2504 | 65.8722 | 0.10013 | -0.0013302 | 0.062778 | 0.078517 | -0.0029006 | -0.0097382 | 0.00027221 | 0.44862 | 0.0050372 | 0.076223 | 0.0686 | 0.001319 | 0.019802 | -0.0014766 | -14.8407 | 65.7532 | -58.342 | 66.0507 | -57.8705 | -58.3191 | -58.5297 | -15.0513 | 65.8356 | -58.2642 | 65.9363 | -58.1863 | -58.4656 | -58.3191 | -0.091553 | -0.11902 | 0.17853 | 0.37994 | -0.27924 | -0.068665 | -0.18768 | 0.022888 | -0.013733 | -0.036621 | 0.064087 | 0.064087 | -0.068665 | -0.21515 | -0.054932 | -0.20142 | 0.4715 | 124.3927 | 0.07782 | 124.2004 | 124.0952 | 124.0997 | 124.0036 | 124.086 | -124.2142 | -124.1364 | 124.3011 | 124.1867 | 43.4097 | 43.1992
428.9375 | 124.2188 | -58.168 | 65.95 | 0.10013 | -0.0077382 | 0.067051 | 0.082789 | 0.0067124 | 0.0030788 | 0.0013402 | 0.051892 | 0.00076419 | 0.068746 | 0.026944 | -0.01043 | 0.019802 | -0.0025446 | -15.0879 | 65.8264 | -58.2642 | 66.124 | -57.7698 | -58.3008 | -58.3145 | -15.3305 | 65.863 | -58.2367 | 66.0141 | -58.0902 | -58.4244 | -58.2596 | -0.09613 | -0.1236 | 0.17395 | 0.39825 | -0.14648 | -0.13275 | -0.050354 | -0.036621 | -0.068664 | -0.086975 | 0.064087 | 0.07782 | -0.091553 | -0.25635 | -0.022889 | -0.18768 | 0.49438 | 124.3881 | 0.14648 | 124.2508 | 124.0906 | 124.0997 | 123.9944 | 124.0311 | -124.2142 | -124.1867 | 124.292 | 124.1821 | 43.0801 | 42.8375
429.9375 | 124.2004 | -58.0948 | 66.0187 | 0.023839 | 0.0018748 | 0.059574 | 0.074244 | 0.014189 | -0.038578 | 0.0013402 | -0.054919 | 0.0061052 | 0.067678 | 0.049374 | -0.017907 | 0.014461 | -0.014294 | -15.2573 | 65.9088 | -58.1955 | 66.1926 | -57.7103 | -58.2413 | -58.2413 | -15.6326 | 65.9271 | -58.1543 | 66.0278 | -58.0353 | -58.3008 | -58.1818 | -0.10071 | -0.10986 | 0.17395 | 0.38452 | -0.14648 | -0.14648 | -0.045776 | -0.045776 | -0.059509 | -0.091553 | 0.009155 | 0.05951 | -0.086975 | -0.20599 | -0.027466 | -0.14648 | 0.48523 | 124.3881 | 0.11902 | 124.1821 | 124.1043 | 124.0814 | 124.0036 | 124.0219 | -124.2142 | -124.173 | 124.2874 | 124.1226 | 42.8375 | 42.4622
430.9375 | 124.2142 | -58.0353 | 66.0965 | 0.17643 | 0.0018748 | 0.065983 | 0.064631 | 0.010984 | -0.00012524 | -0.010409 | -0.070178 | 0.010377 | 0.062338 | 0.057919 | -0.002953 | 0.012325 | -0.0004086 | -15.4861 | 65.9958 | -58.1039 | 66.2476 | -57.6553 | -58.1589 | -58.1543 | -15.8844 | 66.0233 | -58.0582 | 66.1285 | -57.9254 | -58.2184 | -58.0948 | -0.068665 | -0.10071 | 0.15106 | 0.37994 | -0.11902 | -0.1236 | -0.050354 | -0.054932 | -0.022889 | -0.073243 | 0.032043 | 0.10986 | -0.05951 | -0.18311 | -0.036621 | -0.16022 | 0.44861 | 124.3515 | 0.13275 | 124.1867 | 124.0997 | 124.0814 | 124.0311 | 124.0585 | -124.2004 | -124.1547 | 124.2828 | 124.1638 | 42.5491 | 42.1509
431.9375 | 124.2325 | -57.9163 | 66.1835 | 0.16117 | 0.0061468 | 0.067051 | 0.066768 | 0.010984 | -0.026828 | -0.0061368 | 0.0061157 | 0.012514 | 0.069815 | 0.072873 | -0.00081695 | 0.011257 | -0.0025446 | -15.9622 | 66.0233 | -58.0399 | 66.3712 | -57.4905 | -58.0627 | -58.0765 | -16.2781 | 66.1148 | -57.962 | 66.2384 | -57.811 | -58.1314 | -57.9941 | -0.1236 | -0.16022 | 0.18768 | 0.42572 | -0.16022 | -0.14648 | -0.036621 | -0.022888 | -0.045776 | -0.068665 | 0.054931 | 0.10529 | -0.07782 | -0.21515 | -0.032044 | -0.16937 | 0.54932 | 124.411 | 0.15106 | 124.2004 | 124.0631 | 124.0768 | 123.9395 | 124.0311 | -124.2233 | -124.1455 | 124.2874 | 124.1547 | 41.954 | 41.6382
432.9375 | 124.1867 | -57.8705 | 66.2933 | 0.13065 | 0.0018748 | 0.064915 | 0.078517 | 0.025938 | -0.02042 | -0.0093408 | -0.13121 | 0.0071732 | 0.073019 | 0.060055 | -0.014702 | 0.014461 | -0.0014766 | -15.9302 | 66.1926 | -57.9117 | 66.4902 | -57.3669 | -57.93 | -57.962 | -16.5482 | 66.1972 | -57.8979 | 66.3071 | -57.7835 | -58.0627 | -57.9346 | -0.041199 | -0.10071 | 0.19684 | 0.50354 | -0.091553 | -0.05951 | -0.050354 | -0.018311 | -0.027466 | -0.09613 | 0.013733 | 0.086975 | -0.064087 | -0.19226 | -0.036621 | -0.1648 | 0.54474 | 124.4019 | 0.11444 | 124.205 | 124.1043 | 124.0952 | 124.0631 | 124.0677 | -124.205 | -124.1913 | 124.3607 | 124.1776 | 41.9403 | 41.3223
433.9688 | 124.2462 | -57.7011 | 66.4032 | 0.10013 | 0.011488 | 0.060642 | 0.080653 | 0.010984 | -0.012943 | -0.0018638 | -0.0091433 | 0.01465 | 0.067678 | 0.044034 | -0.008294 | 0.015529 | -0.0036126 | -16.4108 | 66.3116 | -57.7789 | 66.5314 | -57.3166 | -57.8705 | -57.8613 | -16.8457 | 66.33 | -57.7469 | 66.4627 | -57.5775 | -57.8888 | -57.7698 | -0.07782 | -0.091552 | 0.12817 | 0.38452 | -0.16022 | -0.16937 | -0.082397 | -0.091552 | -0.045776 | -0.073242 | 0.05951 | 0.1236 | -0.068664 | -0.18768 | -0.022888 | -0.14191 | 0.46234 | 124.3103 | 0.16937 | 124.2096 | 124.0906 | 124.0768 | 124.0128 | 124.0311 | -124.1821 | -124.1501 | 124.2325 | 124.1638 | 41.2903 | 40.8554
434.9375 | 124.2004 | -57.6279 | 66.5085 | -0.021937 | 0.00080677 | 0.063847 | 0.073176 | 0.0035084 | -0.00012524 | -0.011477 | 0.0061157 | 0.0071732 | 0.079428 | 0.054715 | -0.013634 | 0.0059161 | 0.0038644 | -16.7358 | 66.3803 | -57.7103 | 66.6916 | -57.1793 | -57.7469 | -57.7606 | -17.189 | 66.4032 | -57.6691 | 66.6687 | -57.486 | -57.7332 | -57.7011 | -0.082397 | -0.12817 | 0.1831 | 0.44861 | -0.13275 | -0.11902 | -0.050354 | -0.036621 | -0.041198 | -0.10529 | 0.16022 | 0.14191 | -0.073242 | -0.10529 | -0.032044 | -0.064087 | 0.53101 | 124.4019 | 0.1831 | 124.3378 | 124.0906 | 124.0723 | 124.0082 | 124.0311 | -124.2188 | -124.1776 | 124.3195 | 124.2966 | 40.892 | 40.4388
435.9375 | 124.0952 | -57.5638 | 66.5497 | 0.054357 | 0.0082828 | 0.058506 | 0.072108 | 0.030211 | 0.0030788 | 0.00027221 | 0.036633 | 0.012514 | 0.077291 | 0.035489 | -0.007226 | 0.013393 | 0.0017274 | -16.8365 | 66.4902 | -57.6141 | 66.8015 | -57.0282 | -57.6279 | -57.6553 | -17.6514 | 66.5176 | -57.5684 | 66.6275 | -57.4402 | -57.7194 | -57.4448 | -0.050354 | -0.05951 | 0.25177 | 0.53558 | -0.091552 | -0.064087 | -0.041198 | -0.013733 | -0.004577 | -0.032044 | 0.077819 | 0.1236 | 0.11902 | -0.15564 | 0.1236 | -0.15106 | 0.58594 | 124.4156 | 0.12817 | 124.1959 | 124.1043 | 124.086 | 124.054 | 124.0814 | -124.1638 | -124.118 | 124.3652 | 124.1913 | 40.7272 | 39.9124
436.9375 | 124.2416 | -57.431 | 66.6824 | 0.11539 | 0.0040108 | 0.057438 | 0.072108 | 0.012053 | -0.0043982 | -0.012545 | 0.0061157 | 0.0093092 | 0.071951 | 0.024808 | -0.007226 | 0.0080531 | 0.010272 | -17.2348 | 66.5451 | -57.5272 | 66.8381 | -57.0099 | -57.5592 | -57.5867 | -18.1915 | 66.6 | -57.4539 | 66.7236 | -57.2937 | -57.6233 | -57.518 | -0.096131 | -0.13733 | 0.15564 | 0.42114 | -0.15564 | -0.12817 | -0.059509 | -0.032043 | -0.022888 | -0.082397 | 0.041199 | 0.13733 | -0.086975 | -0.19226 | -0.064087 | -0.16937 | 0.51727 | 124.3652 | 0.16022 | 124.1776 | 124.0723 | 124.054 | 123.9761 | 124.0311 | -124.2096 | -124.1364 | 124.2691 | 124.1547 | 40.1962 | 39.2395
437.9375 | 124.2462 | -57.3303 | 66.7603 | 0.19169 | 0.013624 | 0.071323 | 0.075312 | 0.0067124 | -0.032169 | -0.0072048 | -0.03966 | 0.0093092 | 0.082632 | 0.040829 | -0.012566 | 0.018734 | -0.012158 | -17.5049 | 66.6595 | -57.4219 | 66.9159 | -56.8954 | -57.4814 | -57.4814 | -18.3014 | 66.6824 | -57.3532 | 66.806 | -57.1793 | -57.518 | -57.4127 | -0.091553 | -0.10071 | 0.15564 | 0.43488 | -0.15106 | -0.15106 | -0.059509 | -0.059509 | -0.022888 | -0.07782 | 0.045776 | 0.15106 | -0.082398 | -0.18768 | -0.05951 | -0.1648 | 0.52643 | 124.3378 | 0.17395 | 124.1592 | 124.0814 | 124.0356 | 123.9899 | 124.0128 | -124.1821 | -124.1135 | 124.2462 | 124.1364 | 39.8254 | 39.0289
438.9375 | 124.1776 | -57.2342 | 66.9067 | 0.14591 | 0.0082828 | 0.072392 | 0.081721 | 0.0099164 | -0.0054662 | -0.0061368 | -0.03966 | -0.0067128 | 0.077291 | 0.061124 | -0.007226 | 0.014461 | 0.0038644 | -17.7338 | 66.774 | -57.312 | 67.067 | -56.7261 | -57.3395 | -57.3532 | -18.8004 | 66.8152 | -57.2754 | 66.8793 | -57.1472 | -57.4493 | -57.3349 | -0.07782 | -0.13275 | 0.16022 | 0.50812 | -0.11902 | -0.10529 | -0.041198 | -0.027466 | -0.041199 | -0.091552 | -0.027466 | 0.086975 | -0.10071 | -0.21515 | -0.059509 | -0.17395 | 0.58594 | 124.379 | 0.12817 | 124.1547 | 124.086 | 124.0906 | 124.0082 | 124.0494 | -124.2188 | -124.1821 | 124.3011 | 124.1135 | 39.5004 | 38.4338
439.9375 | 124.2416 | -57.1518 | 66.9617 | 0.14591 | 0.0093518 | 0.068119 | 0.063563 | -0.0082416 | -0.0076022 | -0.010409 | 0.08241 | -0.00030381 | 0.073019 | 0.040829 | -0.018975 | 0.010189 | -0.0057486 | -18.0405 | 66.8472 | -57.2433 | 67.1265 | -56.6391 | -57.2525 | -57.2845 | -19.8257 | 66.8106 | -57.2159 | 66.9846 | -56.9824 | -57.3303 | -57.2296 | -0.091553 | -0.11444 | 0.16479 | 0.5127 | -0.13275 | -0.10071 | -0.041199 | -0.009155 | -0.064087 | -0.15106 | 0.022888 | 0.16937 | -0.07782 | -0.17853 | -0.013733 | -0.11444 | 0.60425 | 124.3698 | 0.23346 | 124.2004 | 124.0906 | 124.0265 | 123.999 | 123.9624 | -124.205 | -124.1776 | 124.2783 | 124.1364 | 39.1113 | 37.326
440.9375 | 124.2188 | -56.9962 | 67.1402 | -0.0066789 | 0.0072148 | 0.071323 | 0.080653 | 0.010984 | 0.015896 | -0.03284 | 0.067151 | 0.0093092 | 0.068746 | 0.052579 | -0.004021 | 0.0059161 | -0.012158 | -18.2327 | 66.9937 | -57.0923 | 67.2592 | -56.4972 | -57.1106 | -57.1243 | -19.6701 | 67.0303 | -57.0511 | 67.131 | -56.8817 | -57.2113 | -57.0877 | -0.09613 | -0.14648 | 0.11902 | 0.49896 | -0.12817 | -0.11444 | -0.032044 | -0.018311 | -0.054931 | -0.10986 | -0.009156 | 0.11444 | -0.091553 | -0.21515 | -0.036622 | -0.16022 | 0.59509 | 124.3515 | 0.16937 | 124.1821 | 124.086 | 124.0814 | 123.9899 | 124.0265 | -124.2325 | -124.1913 | 124.2554 | 124.1272 | 38.7634 | 37.3261
441.9375 | 124.2554 | -56.8863 | 67.1951 | 0.054357 | 0.0029428 | 0.069187 | 0.076381 | 0.016325 | 0.012692 | -0.0072048 | 0.1587 | 0.00076419 | 0.063406 | 0.051511 | -0.005089 | 0.013393 | -0.0046806 | -18.5074 | 67.1494 | -56.9595 | 67.4057 | -56.3919 | -57.0099 | -57.0282 | -19.9631 | 67.131 | -56.955 | 67.2867 | -56.7078 | -57.0328 | -56.9366 | -0.073242 | -0.045776 | 0.21057 | 0.49438 | -0.14191 | -0.1236 | -0.068664 | -0.050354 | -0.068664 | -0.064087 | 0.091553 | 0.17853 | -0.050354 | -0.14648 | 0.01831 | -0.07782 | 0.56763 | 124.3652 | 0.24719 | 124.2416 | 124.1089 | 124.086 | 124.0356 | 124.0173 | -124.1547 | -124.1501 | 124.292 | 124.173 | 38.3789 | 36.9232
442.9375 | 124.1959 | -56.7719 | 67.3691 | 0.13065 | -0.0034662 | 0.068119 | 0.077449 | 0.0013714 | -0.015079 | -0.010409 | 0.021375 | 0.0018322 | 0.081564 | 0.084622 | -0.004021 | 0.00057606 | 0.014545 | -18.7134 | 67.2501 | -56.8542 | 67.5659 | -56.1996 | -56.8314 | -56.8634 | -20.1874 | 67.305 | -56.7856 | 67.392 | -56.6208 | -56.9504 | -56.8451 | -0.082397 | -0.11902 | 0.19684 | 0.5722 | -0.091552 | -0.059509 | -0.009155 | 0.022888 | -0.013732 | -0.064087 | 0.022888 | 0.15106 | -0.073242 | -0.17853 | -0.05951 | -0.16479 | 0.6546 | 124.4202 | 0.16479 | 124.1776 | 124.1043 | 124.0906 | 124.0219 | 124.0768 | -124.2233 | -124.1547 | 124.3378 | 124.1638 | 38.0585 | 36.5845
443.9375 | 124.2599 | -56.662 | 67.4286 | 0.084874 | -0.0023982 | 0.071323 | 0.074244 | 0.0056444 | 0.0052148 | 0.00027221 | 0.067151 | 0.0071732 | 0.062338 | 0.078213 | -0.014702 | 0.0091211 | 0.0070684 | -18.8873 | 67.3233 | -56.7535 | 67.5751 | -56.1768 | -56.781 | -56.7993 | -20.7367 | 67.3508 | -56.7215 | 67.4789 | -56.4697 | -56.8405 | -56.7398 | -0.091553 | -0.10529 | 0.14648 | 0.48523 | -0.13733 | -0.11902 | -0.045776 | -0.027466 | -0.05951 | -0.07782 | 0.050354 | 0.19226 | -0.07782 | -0.17853 | -0.01831 | -0.11902 | 0.57678 | 124.3286 | 0.25177 | 124.2004 | 124.0768 | 124.0723 | 123.9853 | 124.0128 | -124.1821 | -124.1501 | 124.2371 | 124.1409 | 37.7747 | 35.9253
444.9375 | 124.2279 | -56.5659 | 67.5476 | 0.20695 | 0.0040108 | 0.063847 | 0.081721 | -0.011446 | 0.0052148 | -0.0039998 | 0.08241 | -0.0035078 | 0.073019 | 0.040829 | -0.007226 | 0.0037801 | -0.0025446 | -19.1345 | 67.4606 | -56.6574 | 67.6895 | -56.0394 | -56.6711 | -56.6803 | -21.1716 | 67.4835 | -56.5842 | 67.6071 | -56.3644 | -56.7123 | -56.6254 | -0.091553 | -0.086975 | 0.14191 | 0.52643 | -0.11444 | -0.10529 | -0.022888 | -0.013733 | -0.01831 | -0.064086 | 0.05951 | 0.20142 | -0.059509 | -0.14648 | -0.041199 | -0.12817 | 0.61798 | 124.3469 | 0.21973 | 124.1913 | 124.118 | 124.0677 | 124.0265 | 124.0494 | -124.205 | -124.1318 | 124.2554 | 124.173 | 37.4313 | 35.3943
445.9375 | 124.1959 | -56.4606 | 67.6804 | 0.11539 | 0.014692 | 0.068119 | 0.078517 | 0.0024404 | 0.00094276 | -0.022158 | 0.08241 | 0.0029002 | 0.073019 | 0.056851 | -0.005089 | 0.0091211 | 0.0038644 | -19.3634 | 67.5613 | -56.4972 | 67.8314 | -55.8609 | -56.5155 | -56.5475 | -21.4188 | 67.5934 | -56.4789 | 67.6758 | -56.2683 | -56.6483 | -56.5384 | -0.036621 | -0.11902 | 0.15106 | 0.59967 | -0.086975 | -0.054932 | -0.050354 | -0.018311 | -0.018311 | -0.086975 | -0.004578 | 0.19226 | -0.07782 | -0.18768 | -0.059509 | -0.16937 | 0.63629 | 124.3286 | 0.21057 | 124.1547 | 124.0585 | 124.0723 | 124.0219 | 124.054 | -124.1776 | -124.1592 | 124.292 | 124.1364 | 37.0972 | 35.0418
446.9375 | 124.2188 | -56.3141 | 67.8085 | 0.10013 | -0.0034662 | 0.057438 | 0.079585 | 0.0077804 | -0.0086702 | -0.011477 | 0.051892 | 0.0082412 | 0.073019 | 0.036557 | -0.014702 | 0.013393 | -0.0078856 | -19.6976 | 67.662 | -56.3828 | 67.9504 | -55.7236 | -56.3873 | -56.4056 | -21.524 | 67.7124 | -56.3278 | 67.7994 | -56.163 | -56.5109 | -56.4194 | -0.068664 | -0.14648 | 0.14191 | 0.59052 | -0.091553 | -0.073242 | -0.022889 | -0.004578 | -0.013733 | -0.096131 | -0.009156 | 0.15106 | -0.10529 | -0.19684 | -0.091553 | -0.1831 | 0.65918 | 124.3332 | 0.1648 | 124.1272 | 124.0448 | 124.0402 | 123.9761 | 124.0265 | -124.1913 | -124.1364 | 124.2645 | 124.1135 | 36.6165 | 34.79
447.9375 | 124.173 | -56.2225 | 67.9138 | 0.16117 | -0.010943 | 0.068119 | 0.077449 | 0.0013714 | -0.019351 | 0.0013402 | 0.08241 | 0.010377 | 0.074087 | 0.084622 | -0.002953 | 0.014461 | -0.0046806 | -19.8898 | 67.8131 | -56.282 | 68.1335 | -55.5771 | -56.2637 | -56.2866 | -21.9727 | 67.8497 | -56.2408 | 67.955 | -55.9891 | -56.3965 | -56.4651 | -0.059509 | -0.10071 | 0.21973 | 0.64545 | -0.064087 | -0.041199 | -0.004578 | 0.01831 | -0.018311 | -0.064087 | 0.041199 | 0.23346 | -0.24261 | -0.17395 | -0.2243 | -0.15564 | 0.70496 | 124.4156 | 0.25177 | 124.1959 | 124.0952 | 124.0906 | 124.0356 | 124.0723 | -124.1959 | -124.1547 | 124.3561 | 124.1776 | 36.3327 | 34.2499
448.9375 | 124.2371 | -56.0944 | 68.042 | 0.0085801 | 0.01042 | 0.063847 | 0.075312 | 0.0013714 | 0.0020108 | 0.012021 | 0.08241 | 0.00076419 | 0.060202 | 0.031216 | -0.008294 | 0.0080531 | 0.010272 | -20.018 | 67.9321 | -56.1584 | 68.2434 | -55.3894 | -56.1264 | -56.1493 | -22.2198 | 67.9916 | -56.1035 | 68.074 | -55.8655 | -56.2408 | -56.1584 | -0.064087 | -0.10986 | 0.20142 | 0.70496 | -0.054932 | -0.032044 | 0.009155 | 0.032043 | -0.009156 | -0.050354 | 0.032044 | 0.22888 | -0.064087 | -0.14648 | -0.054931 | -0.13733 | 0.76904 | 124.4019 | 0.23804 | 124.1776 | 124.0906 | 124.0952 | 124.0265 | 124.086 | -124.2004 | -124.1455 | 124.3378 | 124.1684 | 36.0764 | 33.8745
449.9375 | 124.2554 | -55.925 | 68.1656 | -0.43392 | -0.0023982 | 0.068119 | 0.076381 | 0.014189 | -0.02042 | -0.0072048 | 0.067151 | 0.010377 | 0.092245 | 0.061124 | -0.014702 | 0.0069851 | 0.0070684 | -20.0043 | 68.0557 | -56.0257 | 68.3716 | -55.2658 | -56.0211 | -56.0898 | -22.5266 | 68.0695 | -55.9753 | 68.2114 | -55.7236 | -56.0944 | -55.9982 | -0.10071 | -0.10986 | 0.20599 | 0.65918 | -0.16479 | -0.09613 | -0.064087 | 0.004578 | -0.050354 | -0.09613 | 0.045777 | 0.20142 | -0.073242 | -0.16937 | -0.022888 | -0.11902 | 0.75989 | 124.3973 | 0.25177 | 124.1867 | 124.0814 | 124.0448 | 123.9807 | 123.9944 | -124.1913 | -124.1409 | 124.2966 | 124.1364 | 35.9207 | 33.3984
450.9375 | 124.2325 | -55.7968 | 68.2892 | -0.067714 | 0.0040108 | 0.068119 | 0.075312 | 0.014189 | -0.015079 | -0.010409 | 0.11293 | 0.0071732 | 0.069815 | 0.060055 | -0.016839 | 0.012325 | -0.023907 | -20.43 | 68.1931 | -55.8655 | 68.454 | -55.1788 | -55.8929 | -55.9158 | -22.8104 | 68.2114 | -55.8197 | 68.3533 | -55.5679 | -55.9662 | -55.8701 | -0.068665 | -0.096131 | 0.16479 | 0.61798 | -0.11902 | -0.09613 | -0.050354 | -0.027465 | -0.022888 | -0.07782 | 0.064086 | 0.22888 | -0.073242 | -0.16937 | -0.050354 | -0.14648 | 0.68665 | 124.3195 | 0.25177 | 124.173 | 124.0585 | 124.0311 | 123.9899 | 124.0082 | -124.1547 | -124.1089 | 124.2508 | 124.1501 | 35.3668 | 32.9864
451.9375 | 124.2233 | -55.6732 | 68.4448 | 0.25272 | 0.0029428 | 0.06171 | 0.074244 | 0.0045764 | 0.0062828 | 0.0056132 | 0.021375 | -0.0035078 | 0.079428 | 0.030148 | -0.016839 | 0.012325 | 0.010272 | -20.6726 | 68.3304 | -55.7693 | 68.5776 | -55.0415 | -55.7465 | -55.7785 | -23.2773 | 68.3441 | -55.719 | 68.4677 | -55.4123 | -55.8243 | -55.7419 | -0.09613 | -0.11444 | 0.13275 | 0.63171 | -0.10529 | -0.073242 | -0.009155 | 0.022888 | -0.045776 | -0.10071 | 0.022888 | 0.26093 | -0.068664 | -0.15106 | -0.022888 | -0.10529 | 0.72784 | 124.3469 | 0.3067 | 124.1867 | 124.0997 | 124.0631 | 124.0036 | 124.0173 | -124.2142 | -124.1638 | 124.2508 | 124.1409 | 35.0006 | 32.3959
452.9375 | 124.2096 | -55.5634 | 68.5638 | 0.054357 | 0.011488 | 0.059574 | 0.081721 | -0.00076463 | -0.010807 | -0.0082728 | -0.0091433 | 0.00076419 | 0.082632 | 0.040829 | -0.01043 | 0.025143 | -0.0089536 | -20.9473 | 68.4494 | -55.6274 | 68.7195 | -54.8218 | -55.6 | -55.6046 | -23.9227 | 68.4814 | -55.6 | 68.5684 | -55.3391 | -55.7236 | -55.6366 | -0.064087 | -0.11444 | 0.15564 | 0.74158 | -0.041199 | -0.036622 | 0.022888 | 0.027465 | -0.036622 | -0.082398 | 0.004577 | 0.2243 | -0.073243 | -0.16022 | -0.036621 | -0.1236 | 0.80566 | 124.3469 | 0.26093 | 124.1684 | 124.0768 | 124.0814 | 124.0128 | 124.0448 | -124.1913 | -124.1638 | 124.2828 | 124.1318 | 34.6161 | 31.6406
453.9375 | 124.2142 | -55.3894 | 68.7057 | 0.13065 | 0.0029428 | 0.068119 | 0.076381 | 0.0067124 | -0.0022622 | 0.0066812 | 0.097669 | 0.00076419 | 0.068746 | 0.054715 | -0.009362 | 0.011257 | 0.012409 | -21.1761 | 68.6188 | -55.4855 | 68.8705 | -54.6707 | -55.4352 | -55.4672 | -24.2844 | 68.6554 | -55.4352 | 68.7378 | -55.1514 | -55.5817 | -55.4901 | -0.096131 | -0.086976 | 0.16479 | 0.71869 | -0.07782 | -0.045777 | 0.018311 | 0.050354 | -0.045777 | -0.050354 | 0.032043 | 0.23804 | -0.10071 | -0.19226 | -0.054931 | -0.14648 | 0.81482 | 124.3561 | 0.28381 | 124.173 | 124.1043 | 124.0906 | 124.0082 | 124.0448 | -124.1913 | -124.1409 | 124.2599 | 124.1272 | 34.2133 | 31.105
454.9375 | 124.2325 | -55.275 | 68.8477 | 0.10013 | -0.0023982 | 0.067051 | 0.077449 | 0.0056444 | 0.0041468 | 0.0024082 | -0.0091433 | 0.00076419 | 0.077291 | 0.052579 | -0.01577 | 0.012325 | 0.0049324 | -21.3913 | 68.7149 | -55.3574 | 69.0262 | -54.5288 | -55.2979 | -55.3482 | -24.7009 | 68.779 | -55.3436 | 68.9117 | -54.9774 | -55.4764 | -55.3528 | -0.082398 | -0.13275 | 0.17853 | 0.74615 | -0.073243 | -0.022889 | 0.009155 | 0.059509 | -0.068665 | -0.068664 | 0.064087 | 0.29755 | -0.07782 | -0.20142 | -0.009155 | -0.13275 | 0.82855 | 124.3835 | 0.36621 | 124.2554 | 124.0723 | 124.1226 | 123.9899 | 124.054 | -124.205 | -124.1913 | 124.3011 | 124.1867 | 33.8837 | 30.574
455.9375 | 124.1913 | -55.1331 | 69.017 | 0.14591 | 0.00080677 | 0.063847 | 0.083857 | 0.0099164 | 0.0052148 | -0.0018638 | 0.12819 | 0.0061052 | 0.081564 | 0.067532 | -0.013634 | 0.019802 | 0.01134 | -21.3821 | 68.8614 | -55.22 | 69.1406 | -54.364 | -55.1788 | -55.2155 | -25.1587 | 68.8751 | -55.188 | 68.9026 | -55.101 | -54.9774 | -55.0415 | -0.086975 | -0.15564 | 0.1236 | 0.76904 | -0.082397 | -0.045776 | 0.004578 | 0.041199 | -0.054931 | -0.14191 | -0.11444 | 0.032044 | 0.091553 | 0.15564 | 0.14648 | 0.21057 | 0.85602 | 124.3607 | 0.086975 | 124.0906 | 124.0814 | 124.0631 | 123.9944 | 124.0082 | -124.2371 | -124.205 | 124.2737 | 124.0356 | 33.7509 | 29.9744
456.9375 | 124.0906 | -55.0415 | 69.0125 | 0.023839 | 0.0050788 | 0.075596 | 0.089198 | 0.016325 | 0.0041468 | -0.016818 | -0.0091433 | -0.00030381 | 0.0837 | 0.070737 | 0.00025105 | 0.0091211 | -0.01109 | -21.3318 | 68.9987 | -55.1376 | 69.2642 | -54.213 | -55.0323 | -55.0827 | -25.6119 | 69.0125 | -55.1147 | 69.0857 | -54.7852 | -55.2017 | -55.0598 | -0.09613 | -0.013733 | 0.25177 | 0.82855 | -0.041199 | 0.009155 | 0.054931 | 0.10528 | -0.073242 | 0 | 0.073242 | 0.25635 | -0.01831 | -0.16022 | 0.054932 | -0.086975 | 0.92468 | 124.4019 | 0.32959 | 124.2004 | 124.1364 | 124.1272 | 124.0402 | 124.054 | -124.1501 | -124.1272 | 124.3057 | 124.1272 | 33.7097 | 29.4296
457.9375 | 124.1913 | -54.8767 | 69.2276 | 0.054357 | 0.0061468 | 0.065983 | 0.077449 | 0.0024404 | 0.0020108 | -0.010409 | -0.0091433 | -0.0013718 | 0.084768 | 0.049374 | -0.01577 | 0.018734 | -0.0014766 | -21.4691 | 69.1452 | -54.9591 | 69.4153 | -54.0344 | -54.8447 | -54.9133 | -25.6348 | 69.1544 | -54.9179 | 69.2505 | -54.5746 | -55.0049 | -54.9408 | -0.082397 | -0.082397 | 0.18768 | 0.84228 | -0.036621 | 0.032043 | 0.045776 | 0.11444 | -0.041199 | -0.073242 | 0.022888 | 0.30212 | -0.064087 | -0.12817 | -0.022888 | -0.086975 | 0.92468 | 124.3744 | 0.34332 | 124.1684 | 124.1043 | 124.0723 | 124.0219 | 124.0311 | -124.1867 | -124.1455 | 124.292 | 124.1272 | 33.4076 | 29.2419
458.9375 | 124.2004 | -54.7211 | 69.3832 | 0.039098 | -0.0045342 | 0.070255 | 0.076381 | -0.013582 | -0.0097382 | -0.010409 | 0.097669 | 0.0061052 | 0.075155 | 0.072873 | -0.004021 | 0.011257 | -0.017499 | -21.6064 | 69.2551 | -54.8126 | 69.5023 | -53.9566 | -54.7668 | -54.8218 | -25.9415 | 69.3054 | -54.7668 | 69.4153 | -54.3961 | -54.8492 | -54.7897 | -0.091553 | -0.12817 | 0.11902 | 0.76447 | -0.10071 | -0.045777 | -0.009155 | 0.045776 | -0.045777 | -0.07782 | 0.032043 | 0.32501 | -0.068665 | -0.12817 | -0.022888 | -0.082397 | 0.85602 | 124.3149 | 0.37079 | 124.1821 | 124.0677 | 124.0723 | 123.9761 | 124.0265 | -124.1959 | -124.1501 | 124.2233 | 124.1364 | 33.1146 | 28.7796
459.9375 | 124.205 | -54.5288 | 69.5709 | 0.14591 | 0.0050788 | 0.063847 | 0.084926 | 0.0056444 | -0.031101 | 0.0045452 | -0.03966 | 0.0029002 | 0.058065 | 0.030148 | -0.009362 | 0.019802 | 0.0006594 | -21.8079 | 69.4748 | -54.6112 | 69.7495 | -53.6774 | -54.5425 | -54.57 | -25.8316 | 69.5068 | -54.57 | 69.5984 | -54.2038 | -54.689 | -54.6021 | -0.082397 | -0.096131 | 0.17853 | 0.85144 | -0.041198 | -0.013733 | 0.041199 | 0.068664 | -0.041198 | -0.064087 | 0.027466 | 0.32501 | -0.073242 | -0.16022 | -0.032044 | -0.11902 | 0.93384 | 124.3607 | 0.36621 | 124.1684 | 124.086 | 124.0768 | 124.0036 | 124.0356 | -124.1821 | -124.1409 | 124.2783 | 124.1272 | 32.7209 | 28.6972
460.9375 | 124.1913 | -54.3457 | 69.7861 | 0.2222 | 0.00080677 | 0.063847 | 0.085994 | 0.0045764 | -0.012943 | -0.023226 | 0.021375 | 0.0071732 | 0.084768 | 0.095303 | -0.012566 | 0.010189 | -0.0089536 | -21.8491 | 69.6991 | -54.3961 | 69.9554 | -53.4576 | -54.3091 | -54.3549 | -25.9964 | 69.7266 | -54.3594 | 69.7998 | -53.9932 | -54.4693 | -54.3869 | -0.050354 | -0.086975 | 0.16937 | 0.88806 | -0.009155 | 0.036621 | 0.041199 | 0.086975 | -0.013733 | -0.05951 | 0.013733 | 0.35248 | -0.041199 | -0.1236 | -0.027466 | -0.10986 | 0.93841 | 124.3515 | 0.36621 | 124.1592 | 124.0952 | 124.086 | 124.0448 | 124.0723 | -124.1821 | -124.1455 | 124.3011 | 124.1455 | 32.4966 | 28.3493
461.9375 | 124.1959 | -54.1763 | 69.9371 | 0.069615 | 0.0082828 | 0.059574 | 0.082789 | -0.018923 | 0.011624 | -0.0018638 | -0.0091433 | 0.010377 | 0.058065 | 0.048306 | -0.008294 | 0.0091211 | -0.0036126 | -22.0734 | 69.8181 | -54.2358 | 70.0699 | -53.3112 | -54.1809 | -54.2221 | -26.239 | 69.8502 | -54.2221 | 69.9463 | -53.8467 | -54.3228 | -54.2358 | -0.059509 | -0.11902 | 0.13275 | 0.86517 | -0.045776 | -0.004577 | 0.013733 | 0.054932 | -0.045776 | -0.086975 | 0.009155 | 0.32959 | -0.059509 | -0.14648 | -0.013733 | -0.10071 | 0.92468 | 124.3057 | 0.37537 | 124.1684 | 124.054 | 124.0723 | 123.9944 | 124.0265 | -124.173 | -124.1592 | 124.2462 | 124.1226 | 32.103 | 27.9373
462.9375 | 124.2096 | -53.952 | 70.1752 | 0.069615 | 0.0040108 | 0.064915 | 0.077449 | -0.0018326 | 0.0084198 | -0.018954 | 0.051892 | 0.0039692 | 0.080496 | 0.061124 | -0.013634 | 0.0037801 | 0.0070684 | -22.0505 | 70.0424 | -54.0436 | 70.3308 | -52.9999 | -53.8971 | -53.9703 | -26.6785 | 70.0836 | -53.9886 | 70.1797 | -53.6179 | -54.0985 | -54.007 | -0.091553 | -0.13275 | 0.15564 | 0.95215 | -0.018311 | 0.054931 | 0.073242 | 0.14648 | -0.036621 | -0.091553 | 0.004578 | 0.33417 | -0.054932 | -0.14649 | -0.018311 | -0.10986 | 1.0437 | 124.3744 | 0.37079 | 124.1684 | 124.086 | 124.0723 | 123.9944 | 124.0356 | -124.2188 | -124.1638 | 124.2828 | 124.1318 | 31.9015 | 27.2736
463.9375 | 124.1867 | -53.8101 | 70.3125 | 0.054357 | 0.0050788 | 0.062778 | 0.083857 | 0.0077804 | -0.026828 | 0.0013402 | 0.08241 | -0.0088488 | 0.076223 | 0.045102 | -0.001885 | 0.028347 | 0.0049324 | -22.11 | 70.1935 | -53.9062 | 70.459 | -52.8305 | -53.7369 | -53.833 | -26.8433 | 70.2301 | -53.8376 | 70.3033 | -53.4622 | -53.9612 | -53.8788 | -0.09613 | -0.11902 | 0.14648 | 0.97961 | -0.022888 | 0.073243 | 0.073242 | 0.16937 | -0.027465 | -0.082397 | -0.009155 | 0.3479 | -0.068664 | -0.15106 | -0.041199 | -0.1236 | 1.0757 | 124.3652 | 0.37537 | 124.1409 | 124.0997 | 124.0677 | 124.0036 | 124.0402 | -124.2188 | -124.1501 | 124.2691 | 124.1135 | 31.7001 | 26.9669
464.9375 | 124.2279 | -53.6499 | 70.4636 | 0.16117 | 0.0072148 | 0.071323 | 0.073176 | 0.015257 | -0.015079 | -0.0018638 | 0.051892 | 0.00076419 | 0.068746 | 0.08035 | -0.01577 | 0.018734 | -0.023907 | -22.0779 | 70.3537 | -53.7231 | 70.5505 | -52.7481 | -53.6545 | -53.7003 | -26.9989 | 70.3583 | -53.6911 | 70.5093 | -53.2425 | -53.7506 | -53.6819 | -0.073243 | -0.10986 | 0.086975 | 0.90179 | -0.050354 | -0.004578 | 0.022889 | 0.068665 | -0.041199 | -0.10529 | 0.045776 | 0.40741 | -0.032044 | -0.10071 | 0.009155 | -0.059509 | 0.97504 | 124.2737 | 0.44861 | 124.2004 | 124.0768 | 124.0494 | 124.0036 | 124.0082 | -124.1867 | -124.1547 | 124.2004 | 124.1592 | 31.572 | 26.651
465.9375 | 124.2004 | -53.4256 | 70.6924 | 0.16117 | 0.0072148 | 0.064915 | 0.085994 | 0.0013714 | -0.0033302 | 0.0066812 | 0.067151 | -0.0013718 | 0.069815 | 0.050442 | -0.005089 | 0.0059161 | -0.010022 | -22.0642 | 70.6055 | -53.4851 | 70.8618 | -52.4002 | -53.3569 | -53.4119 | -26.9577 | 70.6284 | -53.4576 | 70.7062 | -53.009 | -53.5126 | -53.4439 | -0.059509 | -0.086975 | 0.16937 | 1.0254 | 0.013733 | 0.068664 | 0.073242 | 0.12817 | -0.032044 | -0.064087 | 0.013733 | 0.41656 | -0.018311 | -0.086975 | 0.013733 | -0.054931 | 1.0849 | 124.3469 | 0.44861 | 124.1638 | 124.0906 | 124.086 | 124.0311 | 124.054 | -124.1776 | -124.1501 | 124.2874 | 124.1318 | 31.3614 | 26.4679
466.9375 | 124.2142 | -53.2196 | 70.903 | 0.069615 | 0.0029428 | 0.060642 | 0.085994 | 0.0067124 | -0.00012524 | -0.016818 | 0.051892 | 0.0061052 | 0.068746 | 0.040829 | -0.009362 | 0.011257 | 0.0006594 | -21.9727 | 70.7657 | -53.3112 | 71.0266 | -52.2034 | -53.1738 | -53.2562 | -27.2232 | 70.8115 | -53.2654 | 70.9122 | -52.8076 | -53.3066 | -53.2562 | -0.091553 | -0.13733 | 0.1236 | 1.0162 | -0.036622 | 0.045776 | 0.054931 | 0.13733 | -0.045777 | -0.091553 | 0.009155 | 0.41199 | -0.036622 | -0.086976 | 0.009155 | -0.041199 | 1.1078 | 124.3378 | 0.45776 | 124.1776 | 124.0768 | 124.0768 | 123.9853 | 124.0311 | -124.2142 | -124.1684 | 124.2462 | 124.1318 | 31.2469 | 25.9964
467.9375 | 124.205 | -52.9633 | 71.1227 | 0.10013 | -0.0034662 | 0.06171 | 0.075312 | 0.020598 | 0.0073508 | -0.0061368 | -0.024402 | 0.011445 | 0.064474 | 0.058987 | -0.008294 | 0.0069851 | -0.018567 | -21.73 | 70.9991 | -53.0823 | 71.2601 | -51.9333 | -52.9221 | -52.9953 | -26.9028 | 71.0358 | -53.0319 | 71.1502 | -52.5284 | -53.0457 | -52.9999 | -0.11902 | -0.1236 | 0.13733 | 1.03 | -0.032043 | 0.041199 | 0.086975 | 0.16022 | -0.068664 | -0.086975 | 0.027466 | 0.43488 | -0.036621 | -0.082397 | 0.032043 | -0.013733 | 1.149 | 124.3423 | 0.50354 | 124.1821 | 124.0814 | 124.0677 | 123.9624 | 123.999 | -124.205 | -124.1547 | 124.2233 | 124.1135 | 31.2332 | 26.0605
468.9375 | 124.1867 | -52.803 | 71.3013 | 0.039098 | -0.0045342 | 0.065983 | 0.084926 | 0.0099164 | -0.0065342 | -0.025363 | 0.051892 | 0.0061052 | 0.078359 | 0.073941 | -0.012566 | 0.019802 | -0.019635 | -21.8857 | 71.1777 | -52.9129 | 71.4523 | -51.709 | -52.7252 | -52.803 | -27.1225 | 71.2372 | -52.8534 | 71.3287 | -52.359 | -52.9083 | -52.89 | -0.10986 | -0.1236 | 0.15106 | 1.0941 | 0 | 0.07782 | 0.10986 | 0.18768 | -0.050354 | -0.064087 | 0.027465 | 0.44403 | -0.086975 | -0.10528 | -0.036621 | -0.054931 | 1.2039 | 124.3652 | 0.49439 | 124.1821 | 124.0906 | 124.0906 | 123.9807 | 124.0402 | -124.2142 | -124.1547 | 124.2554 | 124.1318 | 30.9174 | 25.6805
469.9375 | 124.2279 | -52.5742 | 71.5393 | 0.084874 | 0.0018748 | 0.065983 | 0.077449 | 0.010984 | -0.0022622 | -0.011477 | 0.051892 | 0.0029002 | 0.087973 | 0.038693 | -0.012566 | 0.021938 | -0.0046806 | -21.4508 | 71.4294 | -52.6474 | 71.6583 | -51.4435 | -52.478 | -52.5696 | -27.0676 | 71.4432 | -52.6154 | 71.553 | -52.0981 | -52.652 | -52.6154 | -0.073242 | -0.10986 | 0.11902 | 1.1307 | 0.004578 | 0.096131 | 0.07782 | 0.16937 | -0.041198 | -0.096131 | 0.013733 | 0.47607 | -0.041198 | -0.07782 | 0 | -0.036622 | 1.2039 | 124.3057 | 0.51727 | 124.1684 | 124.0768 | 124.0585 | 124.0036 | 124.0173 | -124.1867 | -124.1547 | 124.2325 | 124.1272 | 31.1234 | 25.5066
470.9688 | 124.2508 | -52.4002 | 71.7087 | 0.19169 | 0.00080677 | 0.06171 | 0.082789 | 0.0013714 | 0.0073508 | -0.011477 | 0.17396 | 0.0039692 | 0.071951 | 0.052579 | -0.01043 | 0.014461 | 0.0049324 | -21.4737 | 71.608 | -52.4734 | 71.8506 | -51.2375 | -52.2949 | -52.3773 | -27.2186 | 71.64 | -52.4277 | 71.7865 | -51.8372 | -52.4048 | -52.3727 | -0.073242 | -0.10071 | 0.14191 | 1.1627 | 0.022889 | 0.10529 | 0.096131 | 0.17853 | -0.027465 | -0.068664 | 0.07782 | 0.56305 | 0.027466 | -0.004577 | 0.054931 | 0.022888 | 1.236 | 124.324 | 0.59051 | 124.2142 | 124.0814 | 124.0677 | 124.0082 | 124.0402 | -124.1821 | -124.1364 | 124.2508 | 124.1867 | 30.9265 | 25.1816
471.9375 | 124.2737 | -52.153 | 71.9467 | 0.13065 | 0.0082828 | 0.058506 | 0.081721 | -0.0039686 | -0.016147 | -0.00079579 | 0.067151 | 0.0029002 | 0.067678 | 0.069668 | -0.014702 | 0.013393 | -0.015362 | -21.1899 | 71.8369 | -52.2446 | 72.0474 | -50.9949 | -52.0935 | -52.153 | -27.2324 | 71.846 | -52.1988 | 72.0245 | -51.5625 | -52.1622 | -52.1347 | -0.091553 | -0.10986 | 0.10071 | 1.1581 | 0 | 0.059509 | 0.091553 | 0.15106 | -0.045777 | -0.10071 | 0.07782 | 0.59052 | 0.01831 | -0.009155 | 0.064087 | 0.036622 | 1.2497 | 124.292 | 0.63629 | 124.2233 | 124.0814 | 124.0448 | 123.9899 | 123.999 | -124.1913 | -124.1455 | 124.2004 | 124.1776 | 30.9631 | 24.9207
472.9375 | 124.2508 | -52.0294 | 72.084 | 0.084874 | -0.0013302 | 0.055302 | 0.084926 | -0.01465 | 0.0020108 | -0.0050688 | 0.18922 | 0.016786 | 0.060202 | 0.060055 | -0.012566 | 0.012325 | -0.019635 | -21.08 | 71.9742 | -52.0935 | 72.1893 | -50.8026 | -51.9196 | -51.9928 | -27.5757 | 72.0154 | -52.066 | 72.1573 | -51.4114 | -52.0203 | -51.9928 | -0.064087 | -0.10986 | 0.10529 | 1.2268 | 0.036621 | 0.10986 | 0.10071 | 0.17395 | -0.036621 | -0.068664 | 0.073243 | 0.61798 | 0.036621 | 0.009155 | 0.073242 | 0.045776 | 1.2909 | 124.2828 | 0.6546 | 124.2233 | 124.0677 | 124.0814 | 124.0036 | 124.0448 | -124.1776 | -124.1501 | 124.2188 | 124.1867 | 30.9494 | 24.4537
473.9375 | 124.2371 | -51.796 | 72.3129 | 0.2222 | 0.012556 | 0.062778 | 0.082789 | 0.00030337 | -0.0076022 | -0.0093408 | 0.097669 | 0.0071732 | 0.075155 | 0.066464 | -0.020043 | 0.017666 | -0.0068176 | -20.9106 | 72.171 | -51.8738 | 72.3862 | -50.5417 | -51.6769 | -51.7548 | -27.2964 | 72.1756 | -51.8326 | 72.3358 | -51.2192 | -51.8234 | -51.828 | -0.07782 | -0.14191 | 0.073242 | 1.2543 | 0.041198 | 0.11902 | 0.11902 | 0.19684 | -0.036622 | -0.13733 | 0.022888 | 0.57678 | -0.032044 | -0.027466 | 0.004578 | 0.009156 | 1.3321 | 124.2599 | 0.6134 | 124.1684 | 124.0448 | 124.0082 | 123.967 | 123.9716 | -124.1867 | -124.1455 | 124.1821 | 124.1318 | 30.8853 | 24.4995
474.9375 | 124.2233 | -51.4847 | 72.6105 | 0.20695 | 0.0050788 | 0.070255 | 0.081721 | 0.0013714 | -0.0043982 | 0.0077492 | 0.17396 | -0.00030381 | 0.080496 | 0.026944 | -0.005089 | 0.018734 | 0.015613 | -21.0434 | 72.5006 | -51.5625 | 72.7158 | -50.1801 | -51.3428 | -51.4435 | -27.2736 | 72.5327 | -51.5167 | 72.6837 | -50.8347 | -51.4709 | -51.4481 | -0.07782 | -0.10986 | 0.10529 | 1.3046 | 0.041199 | 0.14191 | 0.11902 | 0.21973 | -0.032044 | -0.07782 | 0.073242 | 0.65002 | 0.036621 | 0.013733 | 0.068665 | 0.045777 | 1.3824 | 124.2783 | 0.68207 | 124.2004 | 124.0631 | 124.0494 | 123.9853 | 124.0173 | -124.173 | -124.1272 | 124.2004 | 124.1684 | 30.4413 | 24.2111
475.9375 | 124.2325 | -50.8392 | 73.2605 | 0.054357 | 0.0072148 | 0.067051 | 0.078517 | 0.0067124 | -0.0054662 | 0.00027221 | 0.11293 | 0.011445 | 0.0837 | 0.06326 | -0.017907 | 0.013393 | -0.0004086 | -22.3206 | 73.1644 | -50.9216 | 73.3429 | -49.4934 | -50.6516 | -50.7935 | -26.9348 | 73.1918 | -50.8621 | 73.32 | -50.1617 | -50.8118 | -50.7889 | -0.082398 | -0.09613 | 0.082398 | 1.3458 | 0.045776 | 0.18768 | 0.12817 | 0.27008 | -0.022889 | -0.068665 | 0.059509 | 0.67749 | 0.050354 | 0.027465 | 0.073243 | 0.050354 | 1.4282 | 124.2645 | 0.70038 | 124.1821 | 124.086 | 124.054 | 124.0036 | 124.0311 | -124.1821 | -124.1226 | 124.1821 | 124.1592 | 28.5187 | 23.9044
476.9375 | 124.2599 | -50.4913 | 73.6176 | 0.069615 | 0.0040108 | 0.068119 | 0.08813 | -0.0071726 | -0.012943 | -0.0082728 | 0.036633 | 0.01999 | 0.06127 | 0.030148 | -0.024315 | 0.017666 | 0.0070684 | -22.8287 | 73.4436 | -50.6195 | 73.6908 | -49.1226 | -50.2899 | -50.4501 | -27.0721 | 73.4802 | -50.5417 | 73.6725 | -49.8138 | -50.4684 | -50.4776 | -0.12817 | -0.17395 | 0.073242 | 1.3687 | 0.041199 | 0.20142 | 0.16937 | 0.32959 | -0.050354 | -0.13733 | 0.054931 | 0.67749 | 0.013733 | 0.022888 | 0.064087 | 0.073242 | 1.4969 | 124.3103 | 0.72784 | 124.2142 | 124.0631 | 124.0219 | 123.9349 | 123.9716 | -124.2371 | -124.1592 | 124.1821 | 124.1638 | 27.6627 | 23.4192
477.9375 | 124.2554 | -50.2441 | 73.851 | 0.17643 | 0.0018748 | 0.063847 | 0.074244 | -0.0029006 | -0.0076022 | 0.0024082 | 0.14344 | 0.0029002 | 0.090109 | 0.034421 | -0.012566 | 0.012325 | 0.0049324 | -22.9889 | 73.7274 | -50.3403 | 73.97 | -48.7885 | -49.9695 | -50.1526 | -26.8158 | 73.7823 | -50.2625 | 73.9151 | -49.53 | -50.2121 | -50.2075 | -0.09613 | -0.1236 | 0.11902 | 1.4557 | 0.091553 | 0.27466 | 0.18768 | 0.37079 | -0.01831 | -0.068664 | 0.064087 | 0.71411 | 0.036621 | 0.032044 | 0.054931 | 0.050354 | 1.5518 | 124.3103 | 0.73242 | 124.1776 | 124.0677 | 124.0448 | 123.9716 | 124.0265 | -124.1913 | -124.1135 | 124.2142 | 124.1592 | 27.2552 | 23.4283
478.9375 | 124.2279 | -49.8734 | 74.2493 | 0.023839 | 0.0072148 | 0.05637 | 0.072108 | 0.0045764 | -0.0022622 | -0.010409 | 0.067151 | 0.00076419 | 0.071951 | 0.049374 | 0.001319 | 0.0048481 | 0.0017274 | -23.3185 | 74.1394 | -49.942 | 74.4415 | -48.2437 | -49.53 | -49.7177 | -26.6876 | 74.1852 | -49.9146 | 74.2447 | -49.1364 | -49.855 | -49.855 | -0.068665 | -0.10986 | 0.19226 | 1.6296 | 0.15564 | 0.34332 | 0.22431 | 0.41199 | -0.041199 | -0.064087 | -0.004578 | 0.737 | 0.01831 | 0.01831 | 0.059509 | 0.059509 | 1.6983 | 124.3835 | 0.7782 | 124.1592 | 124.0814 | 124.0997 | 124.0128 | 124.0585 | -124.1913 | -124.1638 | 124.3149 | 124.118 | 26.5549 | 23.1857
479.9375 | 124.205 | -49.736 | 74.3774 | 0.20695 | -0.0098752 | 0.063847 | 0.072108 | 0.0067124 | -0.017215 | -0.014682 | 0.25026 | 0.0093092 | 0.076223 | 0.035489 | -0.009362 | 0.0059161 | -0.0068176 | -23.085 | 74.2538 | -49.8276 | 74.707 | -47.9462 | -49.3378 | -49.6628 | -26.8982 | 74.3134 | -49.7543 | 74.382 | -48.9761 | -49.7086 | -49.736 | -0.091553 | -0.1236 | 0.32959 | 1.7899 | 0.073242 | 0.39825 | 0.16479 | 0.48981 | -0.01831 | -0.064087 | 0.004578 | 0.75989 | 0 | 0.027466 | 0.01831 | 0.045776 | 1.8814 | 124.5346 | 0.7782 | 124.1364 | 124.0814 | 124.0677 | 123.9899 | 124.0494 | -124.205 | -124.1318 | 124.4431 | 124.118 | 26.651 | 22.8378
480.9375 | 124.2096 | -49.3515 | 74.7849 | 0.11539 | 0.0029428 | 0.060642 | 0.080653 | 0.0088484 | 0.0073508 | 0.0066812 | 0.11293 | 0.00076419 | 0.082632 | 0.066464 | -0.011498 | 0.010189 | -0.0068176 | -23.671 | 74.6658 | -49.4064 | 74.7803 | -47.6715 | -48.7839 | -49.1776 | -26.6785 | 74.7116 | -49.3515 | 74.8077 | -48.5779 | -49.324 | -49.3149 | -0.054932 | -0.11902 | -0.004578 | 1.68 | 0.17395 | 0.56763 | 0.22888 | 0.62256 | 0 | -0.073242 | 0.022888 | 0.77362 | 0.036621 | 0.027465 | 0.036621 | 0.027465 | 1.7349 | 124.1867 | 0.77362 | 124.1592 | 124.0723 | 124.0631 | 124.0173 | 124.0631 | -124.1913 | -124.1364 | 124.1318 | 124.1592 | 25.6805 | 22.673
481.9375 | 124.2004 | -48.349 | 75.7965 | 0.10013 | -0.0013302 | 0.057438 | 0.077449 | -0.0018326 | -0.021488 | -0.0061368 | 0.35707 | 0.0039692 | 0.073019 | 0.060055 | -0.013634 | 0.014461 | 0.0038644 | -22.879 | 75.65 | -48.4268 | 75.8606 | -46.6095 | -47.9233 | -48.2071 | -31.1462 | 75.6546 | -48.4314 | 75.7874 | -47.6578 | -48.3215 | -48.3215 | -0.07782 | -0.14648 | 0.064087 | 1.7395 | 0.14191 | 0.42572 | 0.21973 | 0.50354 | -0.082397 | -0.14191 | -0.009155 | 0.69122 | 0.027466 | 0.027466 | 0.10986 | 0.10986 | 1.8173 | 124.2874 | 0.77362 | 124.2188 | 124.0768 | 124.086 | 123.999 | 124.0036 | -124.2233 | -124.2279 | 124.2096 | 124.1364 | 25.47 | 17.2028
482.9375 | 124.2233 | -48.0469 | 76.0712 | 0.14591 | 0.00080677 | 0.063847 | 0.085994 | 0.0045764 | 0.010556 | -0.0039998 | 0.18922 | 0.013582 | 0.076223 | 0.057919 | -0.014702 | 0.026211 | 0.0038644 | -22.9248 | 75.975 | -48.1247 | 76.1993 | -46.2341 | -47.5342 | -47.8638 | -31.4987 | 75.9659 | -48.0881 | 76.0803 | -47.2824 | -48.024 | -48.024 | -0.07782 | -0.09613 | 0.12817 | 1.8127 | 0.1831 | 0.5127 | 0.26093 | 0.59052 | -0.041199 | -0.10529 | 0.009155 | 0.76447 | 0.022888 | 0.022888 | 0.064087 | 0.064087 | 1.8906 | 124.324 | 0.80566 | 124.1684 | 124.0997 | 124.054 | 124.0219 | 124.0128 | -124.1959 | -124.1592 | 124.2462 | 124.1272 | 25.1221 | 16.5482
483.9844 | 124.2188 | -47.2687 | 76.8768 | 0.11539 | -0.0013302 | 0.057438 | 0.08813 | 0.012053 | -0.0033302 | 0.0013402 | 0.235 | 0.0093092 | 0.077291 | 0.044034 | -0.014702 | 0.015529 | -0.0089536 | -25.1404 | 76.7212 | -47.3785 | 77.0279 | -45.3781 | -46.6049 | -47.0627 | -32.2769 | 76.767 | -47.3007 | 76.8814 | -46.4676 | -47.2229 | -47.2366 | -0.10986 | -0.15564 | 0.15106 | 1.8906 | 0.20599 | 0.66376 | 0.31586 | 0.77362 | -0.032043 | -0.10986 | 0.004578 | 0.80109 | 0.032044 | 0.045777 | 0.064087 | 0.07782 | 2.0004 | 124.4064 | 0.83313 | 124.1821 | 124.0997 | 124.0677 | 123.9899 | 124.0356 | -124.2554 | -124.1776 | 124.2966 | 124.1501 | 22.1283 | 14.9918
484.9375 | 124.2096 | -47.0901 | 77.0142 | 0.14591 | 0.012556 | 0.06171 | 0.083857 | 0.0035084 | 0.0052148 | -0.0061368 | 0.14344 | 0.0029002 | 0.076223 | 0.041897 | -0.014702 | 0.015529 | -0.0057486 | -24.852 | 76.918 | -47.1725 | 77.3575 | -45.0302 | -46.3669 | -46.9345 | -32.5287 | 76.9501 | -47.1405 | 77.0233 | -46.2616 | -47.0673 | -47.081 | -0.082397 | -0.09613 | 0.34332 | 2.0599 | 0.15564 | 0.72327 | 0.23804 | 0.80566 | -0.050354 | -0.064087 | 0.009155 | 0.82855 | 0.009155 | 0.022888 | 0.059509 | 0.073242 | 2.1423 | 124.53 | 0.87891 | 124.1638 | 124.0906 | 124.0906 | 124.0082 | 124.0402 | -124.1867 | -124.1547 | 124.4476 | 124.1135 | 22.2382 | 14.5615
485.9375 | 124.3332 | -47.7631 | 76.2451 | 0.054357 | 0.0050788 | 0.080936 | 0.078517 | -0.0071726 | -0.0076022 | 0.00027221 | 0.12819 | 0.00076419 | 0.067678 | 0.082486 | -0.012566 | 0.027279 | 0.022022 | -25.1266 | 76.1307 | -47.8821 | 76.2909 | -45.8908 | -47.1725 | -47.6715 | -27.4292 | 76.1765 | -47.8043 | 76.442 | -46.6965 | -47.6212 | -47.644 | -0.11902 | -0.11444 | 0.045777 | 1.8723 | 0.091553 | 0.59052 | 0.21057 | 0.70953 | -0.041198 | -0.068664 | 0.19684 | 1.0666 | 0.11902 | 0.14191 | 0.16022 | 0.1831 | 1.9913 | 124.173 | 1.1078 | 124.2462 | 124.0128 | 123.9807 | 123.8937 | 123.9395 | -124.1272 | -124.0494 | 124.054 | 124.205 | 22.6364 | 20.3339
486.9375 | 124.2371 | -47.5113 | 76.5747 | 0.10013 | 0.011488 | 0.059574 | 0.083857 | -0.0071726 | 0.010556 | -0.012545 | 0.37233 | 0.012514 | 0.065542 | 0.052579 | -0.005089 | 0.0048481 | -0.01109 | -25.6256 | 76.4923 | -47.5159 | 76.6205 | -45.4788 | -46.8933 | -47.2961 | -27.0264 | 76.4603 | -47.5571 | 76.6113 | -46.4401 | -47.3648 | -47.4289 | -0.004577 | -0.082397 | 0.045776 | 2.0325 | 0.21515 | 0.61798 | 0.21973 | 0.62256 | -0.045776 | -0.11444 | 0.036621 | 1.0712 | 0.082398 | 0.14648 | 0.12817 | 0.19226 | 2.037 | 124.1364 | 1.1169 | 124.1684 | 124.0082 | 124.0173 | 124.0036 | 123.9716 | -124.0906 | -124.1318 | 124.1318 | 124.1226 | 21.8857 | 20.4849
487.9375 | 124.2279 | -47.5616 | 76.5701 | 0.17643 | -0.0023982 | 0.062778 | 0.090266 | 0.0056444 | -0.0022622 | -0.010409 | 0.28077 | 0.0082412 | 0.069815 | 0.02374 | -0.018975 | 0.019802 | -0.0089536 | -21.9772 | 76.5472 | -47.4884 | 76.9409 | -45.1126 | -48.143 | -47.0535 | -30.4047 | 76.5747 | -47.5021 | 76.5106 | -46.5591 | -47.4655 | -47.5479 | 0.073243 | -0.022888 | 0.37079 | 2.449 | 0.50812 | -0.58136 | 0.43487 | -0.6546 | 0.05951 | 0.004578 | -0.059509 | 1.0025 | 0.013733 | 0.096131 | -0.045777 | 0.036621 | 2.3758 | 124.4293 | 0.94299 | 124.0128 | 124.0356 | 124.0768 | 124.1089 | 124.1364 | -124.0585 | -124.0723 | 124.5026 | 124.0723 | 25.5844 | 17.157
488.9375 | 124.2508 | -47.4472 | 76.6342 | 0.2222 | 0.0050788 | 0.058506 | 0.080653 | 0.0088484 | 0.010556 | -0.0093408 | 0.235 | 0.0061052 | 0.06127 | 0.030148 | -0.01577 | 0.024074 | -0.0046806 | -18.8873 | 76.5015 | -47.525 | 76.6708 | -45.2774 | -46.7468 | -47.1863 | -27.3743 | 76.5472 | -47.4838 | 76.6754 | -46.2662 | -47.2778 | -47.3602 | -0.077819 | -0.13275 | 0.036621 | 2.1698 | 0.26093 | 0.70038 | 0.33875 | 0.7782 | -0.036621 | -0.086975 | 0.041199 | 1.181 | 0.086976 | 0.16937 | 0.1236 | 0.20599 | 2.2476 | 124.1959 | 1.2177 | 124.1592 | 124.0265 | 124.0311 | 123.9487 | 123.9944 | -124.1592 | -124.118 | 124.118 | 124.1226 | 28.5599 | 20.0729
489.9375 | 124.1913 | -46.7972 | 77.3392 | 0.14591 | 0.011488 | 0.063847 | 0.095607 | 0.025938 | -0.010807 | 0.0045452 | 0.20448 | 0.0029002 | 0.078359 | 0.060055 | -0.011498 | 0.017666 | -0.022839 | -18.2281 | 77.1561 | -46.9025 | 77.4399 | -44.4534 | -45.7535 | -46.4127 | -31.6406 | 77.243 | -46.8109 | 77.3621 | -45.6757 | -46.6644 | -46.7606 | -0.10529 | -0.18311 | 0.10071 | 2.3438 | 0.38452 | 1.0437 | 0.48981 | 1.149 | -0.013733 | -0.09613 | 0.022889 | 1.1215 | 0.036621 | 0.13275 | 0.050354 | 0.14648 | 2.449 | 124.3423 | 1.1353 | 124.173 | 124.0585 | 124.054 | 123.9532 | 124.0402 | -124.2416 | -124.1501 | 124.2371 | 124.1592 | 28.569 | 15.1566
490.9375 | 124.2096 | -46.2387 | 77.8519 | 0.16117 | 0.012556 | 0.068119 | 0.092402 | -0.0264 | 0.0041468 | -0.024295 | 0.35707 | 0.013582 | 0.063406 | 0.0686 | -0.020043 | 0.011257 | -0.023907 | -18.1824 | 77.6871 | -46.4218 | 77.9343 | -43.7347 | -45.1447 | -45.9183 | -30.9906 | 77.71 | -46.3531 | 77.9022 | -45.0851 | -46.106 | -46.138 | -0.18311 | -0.16479 | 0.082397 | 2.504 | 0.32043 | 1.0941 | 0.50354 | 1.2772 | -0.11444 | -0.14191 | 0.050354 | 1.1536 | 0.10071 | 0.13275 | 0.21515 | 0.24719 | 2.6871 | 124.3561 | 1.268 | 124.2554 | 124.1089 | 124.0631 | 123.9258 | 123.9487 | -124.2737 | -124.205 | 124.173 | 124.1409 | 28.0563 | 15.2481
491.9375 | 124.2966 | -45.5795 | 78.5294 | 0.13065 | 0.01042 | 0.06171 | 0.087062 | 0.0088484 | -0.0097382 | 0.0034762 | 0.32655 | 0.0018322 | 0.06661 | 0.064328 | -0.01043 | 0.0027121 | -0.0089536 | -22.9523 | 78.0716 | -45.8771 | 78.4607 | -43.2724 | -43.6066 | -45.3186 | -30.9036 | 78.3691 | -45.6345 | 78.598 | -44.3161 | -45.3644 | -45.433 | -0.29755 | -0.45776 | -0.068665 | 2.3071 | 0.26093 | 1.973 | 0.55847 | 2.2705 | -0.054931 | -0.16022 | 0.068664 | 1.2634 | 0.14648 | 0.21515 | 0.20142 | 0.27008 | 2.6047 | 124.3378 | 1.3184 | 124.2325 | 123.9487 | 124.0036 | 123.6511 | 123.9487 | -124.4064 | -124.1638 | 124.0402 | 124.1776 | 22.6273 | 14.6759
492.9375 | 124.2279 | -45.1584 | 78.923 | 0.20695 | -0.0034662 | 0.065983 | 0.094539 | 0.0067124 | -0.024692 | 0.0098852 | 0.29603 | 0.0071732 | 0.0837 | 0.0686 | -0.020043 | 0.017666 | -0.0057486 | -24.5499 | 78.7674 | -45.2271 | 78.8635 | -42.778 | -43.9957 | -44.838 | -30.3955 | 78.7628 | -45.2225 | 79.0375 | -43.808 | -44.9112 | -44.9936 | -0.068665 | -0.15564 | -0.05951 | 2.3804 | 0.32043 | 1.1627 | 0.3891 | 1.2314 | -0.064087 | -0.16022 | 0.11444 | 1.3504 | 0.16479 | 0.24719 | 0.22888 | 0.31128 | 2.449 | 124.0906 | 1.4145 | 124.2599 | 123.9944 | 123.9853 | 123.9258 | 123.9212 | -124.1501 | -124.1455 | 124.0219 | 124.1959 | 20.6085 | 14.7629
493.9375 | 124.3149 | -44.6457 | 79.4174 | 0.20695 | -0.00026223 | 0.063847 | 0.09347 | -0.0018326 | 0.0041468 | -0.0039998 | 0.12819 | -0.00030381 | 0.078359 | 0.078213 | -0.011498 | 0.0091211 | -0.0014766 | -22.5769 | 79.2664 | -44.7098 | 79.5639 | -41.9907 | -43.364 | -44.2978 | -29.5807 | 79.3121 | -44.7006 | 79.5685 | -43.2266 | -44.3756 | -44.4763 | -0.064087 | -0.15106 | 0.14648 | 2.655 | 0.3479 | 1.2817 | 0.41199 | 1.3458 | -0.054932 | -0.10528 | 0.15106 | 1.4191 | 0.16937 | 0.27008 | 0.22431 | 0.32501 | 2.7191 | 124.2737 | 1.474 | 124.2691 | 123.9761 | 124.0128 | 123.912 | 123.9578 | -124.1272 | -124.118 | 124.2096 | 124.2142 | 22.0688 | 15.065
494.9375 | 124.3057 | -44.133 | 79.9347 | 0.054357 | -0.0013302 | 0.062778 | 0.10095 | -0.01465 | -0.0033302 | -0.0029318 | 0.29603 | 0.0018322 | 0.074087 | 0.073941 | -0.021111 | 0.00057606 | -0.027112 | -24.2844 | 79.8294 | -44.1788 | 79.9576 | -41.5649 | -42.3523 | -43.7119 | -29.1733 | 79.8294 | -44.1513 | 80.1544 | -42.9108 | -43.8492 | -43.9774 | -0.045776 | -0.10528 | 0.022889 | 2.5681 | 0.42114 | 1.7807 | 0.46692 | 1.8265 | -0.01831 | -0.10528 | 0.21973 | 1.2222 | 0.15564 | 0.28381 | 0.17395 | 0.30212 | 2.6138 | 124.1364 | 1.2405 | 124.3057 | 124.0082 | 123.9807 | 123.9624 | 123.9624 | -124.1135 | -124.086 | 124.0906 | 124.2874 | 19.8486 | 14.9597
495.9375 | 124.2416 | -43.7576 | 80.3513 | 0.10013 | 0.00080677 | 0.063847 | 0.095607 | -0.0061046 | 0.018033 | 0.00027221 | -0.024402 | 0.0039692 | 0.076223 | 0.086758 | -0.030724 | 0.012325 | -0.014294 | -25.0671 | 80.2094 | -43.8492 | 80.4199 | -40.9653 | -42.485 | -43.1534 | -29.2145 | 80.2505 | -43.8034 | 80.4108 | -42.2653 | -43.5699 | -43.6295 | -0.091553 | -0.14191 | 0.068665 | 2.7924 | 0.60425 | 1.2726 | 0.6958 | 1.3641 | -0.045777 | -0.10071 | 0.05951 | 1.4923 | 0.12817 | 0.18768 | 0.17395 | 0.23346 | 2.8839 | 124.2691 | 1.5381 | 124.2142 | 124.0585 | 124.054 | 123.967 | 124.0082 | -124.2004 | -124.1547 | 124.1776 | 124.1684 | 18.6905 | 14.5432
496.9375 | 124.2966 | -43.277 | 80.7587 | 0.10013 | 0.0029428 | 0.064915 | 0.095607 | 0.00030337 | 0.00094276 | -0.014682 | -0.37535 | -0.00030381 | 0.064474 | 0.050442 | -0.009362 | 0.012325 | -0.0057486 | -25.2914 | 80.5298 | -43.4601 | 80.7449 | -39.9857 | -41.2766 | -42.7414 | -28.949 | 80.6442 | -43.3502 | 80.9235 | -41.6611 | -42.984 | -43.0756 | -0.1831 | -0.22888 | -0.013733 | 3.2913 | 0.53558 | 2.0004 | 0.71869 | 2.1835 | -0.073242 | -0.11444 | 0.16479 | 1.6159 | 0.20142 | 0.29297 | 0.27466 | 0.36621 | 3.4744 | 124.205 | 1.6891 | 124.2737 | 123.9899 | 123.9944 | 123.8068 | 123.9212 | -124.2188 | -124.1089 | 124.0219 | 124.2004 | 17.9855 | 14.328
497.9375 | 124.3057 | -43.19 | 80.8411 | 0.054357 | 0.0093518 | 0.063847 | 0.099879 | 0.015257 | -0.015079 | 0.0088172 | 0.31129 | 0.0071732 | 0.084768 | 0.094235 | -0.021111 | -0.0036969 | -0.027112 | -27.6764 | 80.8502 | -43.1213 | 80.9921 | -39.5142 | -41.0889 | -42.5125 | -29.4205 | 80.8044 | -43.1946 | 81.1661 | -41.6153 | -43.0756 | -43.0573 | 0.068664 | 0.009156 | 0.15106 | 3.6758 | 0.67749 | 2.1011 | 0.60883 | 2.0325 | -0.004578 | -0.036621 | 0.32501 | 1.5747 | 0.13275 | 0.11444 | 0.13733 | 0.11902 | 3.6072 | 124.1135 | 1.5793 | 124.3607 | 123.9716 | 123.999 | 124.0402 | 123.9944 | -123.9624 | -124.0356 | 124.1821 | 124.3561 | 15.5136 | 13.7695
498.9375 | 124.3286 | -42.984 | 81.0471 | -0.037196 | 0.0040108 | 0.062778 | 0.10522 | -0.0071726 | -0.0033302 | -0.013613 | 0.35707 | 0.0018322 | 0.085836 | 0.052579 | -0.016839 | 0.012325 | 0.0049324 | -25.6851 | 80.9143 | -43.0801 | 81.0699 | -38.7909 | -41.0889 | -42.4393 | -30.8395 | 80.9784 | -43.0389 | 81.1981 | -41.3361 | -42.6407 | -42.7689 | -0.09613 | -0.13275 | 0.022888 | 4.1931 | 0.54474 | 1.8951 | 0.64087 | 1.9913 | -0.054931 | -0.068664 | 0.15106 | 1.6479 | 0.21515 | 0.34332 | 0.27008 | 0.39825 | 4.2892 | 124.1501 | 1.7029 | 124.2371 | 123.9944 | 124.0173 | 123.8983 | 123.9624 | -124.1272 | -124.086 | 124.054 | 124.1821 | 17.2989 | 12.1445
499.9375 | 124.292 | -42.9062 | 81.1203 | 0.084874 | 0.01042 | 0.067051 | 0.10949 | 0.0045764 | -0.0011942 | 0.00027221 | 0.35707 | -0.0035078 | 0.06661 | 0.056851 | -0.009362 | 0.016598 | -0.01109 | -24.1241 | 81.0471 | -42.9794 | 81.1981 | -39.7293 | -40.6586 | -42.0959 | -31.0043 | 81.0654 | -42.9749 | 81.2714 | -41.2262 | -42.5766 | -42.7094 | -0.073242 | -0.073242 | 0.07782 | 3.1769 | 0.81024 | 2.2476 | 0.88348 | 2.3209 | -0.068665 | -0.054931 | 0.15106 | 1.68 | 0.19684 | 0.32959 | 0.2655 | 0.39825 | 3.2501 | 124.1776 | 1.7487 | 124.2462 | 124.0265 | 124.0402 | 123.9532 | 123.9716 | -124.0997 | -124.0952 | 124.1043 | 124.1776 | 18.782 | 11.9019
500.9375 | 124.2096 | -42.3157 | 81.8344 | 0.16117 | 0.0082828 | 0.057438 | 0.10842 | 0.0013714 | 0.020169 | 0.00027221 | 0.20448 | 0.013582 | 0.064474 | 0.039761 | -0.012566 | 0.02087 | -0.016431 | -23.053 | 81.8756 | -42.1646 | 82.0953 | -38.8687 | -39.5966 | -41.0889 | -32.2815 | 81.8756 | -42.2287 | 81.8298 | -40.6265 | -42.0364 | -42.16 | 0.15106 | 0.041198 | 0.26093 | 3.447 | 1.2268 | 2.7191 | 1.0757 | 2.5681 | 0.086975 | 0.041198 | -0.004578 | 1.6891 | 0.15564 | 0.27924 | 0.068665 | 0.19226 | 3.2959 | 124.2599 | 1.6022 | 124.0585 | 124.0402 | 124.1043 | 124.1913 | 124.1913 | -123.999 | -124.0631 | 124.411 | 124.1455 | 19.2627 | 10.0342
501.9375 | 124.3103 | -41.803 | 82.2556 | 0.13065 | 0.0040108 | 0.06171 | 0.11377 | -0.0093096 | 0.0094878 | 0.0024082 | 0.29603 | 0.015718 | 0.082632 | 0.0087855 | -0.009362 | 0.0091211 | -0.020703 | -25.7446 | 82.0175 | -41.9907 | 82.1869 | -38.7177 | -38.9648 | -40.9378 | -30.8533 | 82.0724 | -41.9449 | 82.3517 | -39.9765 | -41.4413 | -41.5695 | -0.18768 | -0.23804 | -0.068664 | 3.0853 | 0.86517 | 2.8381 | 1.0529 | 3.0258 | -0.14191 | -0.1831 | 0.096131 | 1.8265 | 0.23346 | 0.36163 | 0.37537 | 0.50354 | 3.273 | 124.1776 | 1.9684 | 124.2966 | 124.0082 | 124.0173 | 123.8205 | 123.8754 | -124.2462 | -124.2004 | 123.9899 | 124.1547 | 16.0584 | 10.9497
502.9375 | 124.3011 | -41.1392 | 82.9056 | 0.054357 | 0.0029428 | 0.075596 | 0.11483 | -0.010378 | 0.03085 | -0.0082728 | 0.11293 | -0.00030381 | 0.055929 | 0.073941 | -0.008294 | 0.019802 | -0.015362 | -23.6801 | 82.7728 | -41.2537 | 82.9376 | -37.9807 | -37.8479 | -39.9582 | -31.5674 | 82.8003 | -41.1942 | 83.0475 | -39.2578 | -40.7639 | -40.9241 | -0.11444 | -0.13275 | 0.032043 | 3.1586 | 1.181 | 3.2913 | 1.2955 | 3.4058 | -0.054932 | -0.10529 | 0.14191 | 1.8814 | 0.21515 | 0.37537 | 0.27008 | 0.4303 | 3.273 | 124.1913 | 1.9363 | 124.2416 | 124.0265 | 123.9944 | 123.912 | 123.9395 | -124.1592 | -124.0997 | 124.0768 | 124.1867 | 17.4591 | 9.5718
503.9375 | 124.3423 | -41.0248 | 83.0017 | -0.037196 | 0.011488 | 0.068119 | 0.1127 | -0.0082416 | 0.031918 | 0.0066812 | 0.235 | 0.0029002 | 0.069815 | 0.035489 | -0.007226 | 0.013393 | 0.0038644 | -23.5382 | 82.933 | -41.0934 | 83.0383 | -37.8204 | -37.7106 | -39.8346 | -31.778 | 82.933 | -41.0431 | 83.1802 | -39.061 | -40.5853 | -40.7867 | -0.068665 | -0.068665 | 0.036621 | 3.2043 | 1.1902 | 3.3142 | 1.2589 | 3.3829 | -0.018311 | -0.068665 | 0.17853 | 1.9638 | 0.23804 | 0.43945 | 0.25635 | 0.45776 | 3.273 | 124.1318 | 1.9821 | 124.2233 | 124.0265 | 123.9761 | 123.9578 | 123.9578 | -124.0952 | -124.0448 | 124.0631 | 124.205 | 17.4866 | 9.2468
504.9375 | 124.3332 | -40.2054 | 83.844 | -0.0066789 | 0.0093518 | 0.071323 | 0.11911 | 0.0099164 | 0.026577 | -0.0050688 | 0.25026 | -0.00030381 | 0.063406 | 0.031216 | -0.017907 | 0.016598 | -0.0078856 | -25.2228 | 83.7204 | -40.2557 | 83.8898 | -36.85 | -35.8246 | -38.7817 | -29.1962 | 83.7616 | -40.242 | 83.9996 | -38.1775 | -39.7751 | -39.9353 | -0.050354 | -0.1236 | 0.045777 | 3.3554 | 1.4236 | 4.3808 | 1.474 | 4.4312 | -0.036621 | -0.082397 | 0.15564 | 2.0279 | 0.27008 | 0.4303 | 0.3067 | 0.46692 | 3.4058 | 124.1455 | 2.0645 | 124.2416 | 123.9761 | 124.0036 | 123.9258 | 123.967 | -124.0997 | -124.086 | 124.0952 | 124.205 | 14.9826 | 11.0092
505.9375 | 124.2828 | -40.1917 | 83.8669 | 0.039098 | -0.0013302 | 0.062778 | 0.1159 | -0.013582 | 0.019101 | 0.0066812 | 0.235 | 0.0029002 | 0.085836 | 0.045102 | -0.01577 | 0.014461 | 0.010272 | -25.0031 | 83.7433 | -40.3107 | 83.9081 | -36.6028 | -35.5042 | -38.649 | -30.2353 | 83.7616 | -40.2466 | 83.9722 | -38.1729 | -39.7705 | -39.949 | -0.11902 | -0.1236 | 0.041199 | 3.5889 | 1.5427 | 4.6875 | 1.6617 | 4.8065 | -0.054932 | -0.10529 | 0.10529 | 2.0187 | 0.24261 | 0.42114 | 0.29755 | 0.47607 | 3.7079 | 124.2188 | 2.0737 | 124.2188 | 124.054 | 124.0082 | 123.9349 | 123.9532 | -124.1776 | -124.1135 | 124.0997 | 124.1638 | 15.1886 | 9.9564
506.9375 | 124.2371 | -40.1596 | 83.9172 | -0.0066789 | 0.01042 | 0.060642 | 0.14047 | -0.0029006 | 0.039395 | -0.0029318 | 0.021375 | 0.015718 | 0.068746 | 0.06326 | -0.00081695 | 0.011257 | -0.0004086 | -24.884 | 83.7753 | -40.2512 | 83.9218 | -33.5037 | -35.3714 | -38.9465 | -29.9652 | 83.812 | -40.1917 | 83.9905 | -38.0905 | -39.7888 | -39.9307 | -0.091553 | -0.14191 | 0.004578 | 6.6559 | 1.2131 | 4.7882 | 1.3046 | 4.8798 | -0.032043 | -0.10529 | 0.073243 | 2.0691 | 0.22888 | 0.37079 | 0.26093 | 0.40283 | 6.7474 | 124.173 | 2.1011 | 124.1821 | 124.0265 | 124.0036 | 123.9349 | 123.9716 | -124.1684 | -124.1089 | 124.0814 | 124.1501 | 15.2756 | 10.1944
507.9375 | 124.2828 | -39.9078 | 84.0546 | -0.052455 | 0.0018748 | 0.072392 | 0.12551 | 0.017393 | 0.020169 | 0.0024082 | 0.18922 | 0.0018322 | 0.071951 | 0.073941 | -0.011498 | 0.014461 | -0.0025446 | -26.6922 | 83.5236 | -40.4755 | 83.8257 | -33.6136 | -35.2844 | -38.8733 | -29.8874 | 83.9127 | -40.0406 | 84.4437 | -37.6053 | -39.3265 | -39.2578 | -0.56763 | -0.531 | -0.22888 | 6.2943 | 1.0345 | 4.6234 | 1.6022 | 5.191 | -0.13275 | -0.14191 | 0.3891 | 2.3026 | 0.65002 | 0.58136 | 0.78278 | 0.71411 | 6.8619 | 124.3011 | 2.4353 | 124.4843 | 123.999 | 123.9532 | 123.4314 | 123.8205 | -124.53 | -124.0952 | 123.7335 | 124.3515 | 13.2156 | 10.0204
508.9375 | 124.2966 | -39.1434 | 84.9243 | -0.052455 | 0.0029428 | 0.069187 | 0.1362 | 0.013121 | 0.019101 | 0.0056132 | 0.17396 | 0.0061052 | 0.071951 | 0.045102 | -0.007226 | 0.017666 | 0.0006594 | -26.6327 | 84.7275 | -39.2853 | 84.8648 | -34.3689 | -33.7555 | -37.3718 | -30.0568 | 84.7504 | -39.2487 | 85.0433 | -36.937 | -38.5437 | -38.855 | -0.14191 | -0.19684 | -0.059509 | 4.7745 | 1.7715 | 5.3879 | 1.9135 | 5.5298 | -0.10529 | -0.17395 | 0.11902 | 2.2064 | 0.28839 | 0.59967 | 0.39368 | 0.70496 | 4.9164 | 124.1501 | 2.3117 | 124.292 | 124.0128 | 123.999 | 123.8709 | 123.8937 | -124.2096 | -124.173 | 124.0082 | 124.1867 | 12.5107 | 9.0866
509.9375 | 124.3057 | -39.4135 | 84.6085 | 0.11539 | 0.00080677 | 0.057438 | 0.12445 | 0.0045764 | 0.043667 | 0.010953 | 0.20448 | 0.0093092 | 0.079428 | 0.036557 | -0.01043 | 0.013393 | -0.014294 | -25.9277 | 84.5123 | -39.473 | 84.6634 | -34.3414 | -33.7646 | -37.532 | -28.8849 | 84.5398 | -39.4638 | 84.7641 | -37.1384 | -38.5162 | -39.1159 | -0.059509 | -0.09613 | 0.054932 | 5.072 | 1.8814 | 5.6488 | 1.9409 | 5.7083 | -0.050354 | -0.068664 | 0.15564 | 2.2751 | 0.29755 | 0.89722 | 0.3479 | 0.94757 | 5.1315 | 124.1364 | 2.3254 | 124.2279 | 123.9853 | 124.0036 | 123.9258 | 123.9532 | -124.0814 | -124.0723 | 124.0768 | 124.1776 | 13.4857 | 10.5286
510.9375 | 124.292 | -39.2258 | 84.9106 | 0.023839 | 0.0072148 | 0.063847 | 0.14367 | -0.0071726 | 0.079983 | 0.01843 | 0.12819 | 0.011445 | 0.064474 | 0.051511 | -0.006157 | 0.017666 | -0.012158 | -28.1616 | 82.8552 | -40.6494 | 85.1074 | -34.8633 | -35.9894 | -38.205 | -27.8458 | 84.4574 | -39.4363 | 84.343 | -37.1841 | -38.4705 | -38.6673 | -1.4236 | -2.0554 | 0.19684 | 4.3625 | 1.0208 | 3.2364 | 2.4445 | 4.66 | -0.21057 | -0.45319 | -0.56763 | 2.0416 | 0.55847 | 0.75531 | 0.76904 | 0.96588 | 5.7861 | 125.7568 | 2.2522 | 123.7793 | 123.5046 | 123.8937 | 122.081 | 123.6832 | -125.56 | -124.3469 | 124.3332 | 123.5687 | 11.0641 | 11.38
511.9375 | 124.3378 | -39.6561 | 84.4025 | -0.052455 | 0.0018748 | 0.080936 | 0.17572 | 0.0013714 | 0.05328 | 0.013089 | 0.11293 | 0.010377 | 0.070883 | 0.08569 | -0.018975 | 0.010189 | 0.0006594 | -21.0388 | 84.3842 | -39.5737 | 84.5306 | -33.5358 | -31.4667 | -37.1475 | -26.7975 | 84.3979 | -39.6011 | 84.4116 | -37.4817 | -39.4547 | -39.3173 | 0.082398 | -0.018311 | 0.12817 | 6.1203 | 2.5085 | 8.1894 | 2.4261 | 8.107 | 0.054932 | -0.004578 | 0.009155 | 2.1744 | 0.33875 | 0.20142 | 0.28381 | 0.14648 | 6.0379 | 124.1043 | 2.1194 | 124.0128 | 123.9578 | 123.999 | 124.0402 | 124.054 | -123.9761 | -124.0036 | 124.1867 | 124.0677 | 18.6172 | 12.8586
512.9375 | 124.3835 | -29.8553 | 94.0933 | 0.023839 | 0.0093518 | 0.014713 | 0.082789 | 0.012053 | -0.0033302 | 0.01843 | 0.0061157 | 0.0093092 | 0.074087 | 0.081418 | 0.001319 | 0.02087 | 0.01134 | -27.9099 | 94.3909 | -29.7226 | -29.8508 | -25.9415 | -33.9203 | -23.0576 | -20.8694 | 94.1208 | -29.892 | 94.2627 | -27.6901 | -29.4113 | -29.686 | 0.13275 | 0.29755 | -123.9441 | 3.9139 | 6.7978 | -4.0649 | 6.665 | -4.1977 | -0.036621 | 0.027466 | 0.16937 | 2.1652 | 0.16937 | 0.44403 | 0.20599 | 0.48065 | 3.7811 | -0.12817 | 2.2018 | 124.1547 | 124.1135 | 124.0128 | 124.2462 | 123.9761 | -123.8159 | -123.9853 | 0.004578 | 124.118 | 1.9455 | 8.9859
513.9375 | 124.3057 | -43.1625 | 80.777 | -0.14401 | 0.00080677 | 0.090549 | 0.36904 | 0.0077804 | 0.18679 | 0.034452 | 0.036633 | 0.011445 | 0.065542 | 0.015195 | -0.009362 | 0.017666 | 0.0038644 | -5.5344 | 81.0379 | -42.8833 | 81.2347 | -35.8795 | 12.5336 | -39.7751 | -31.8695 | 80.3192 | -43.6066 | 81.1432 | -40.6769 | -42.8558 | -42.9474 | 0.27924 | 0.26093 | 0.45776 | 7.283 | 3.3875 | 55.6961 | 3.1082 | 55.4169 | -0.44403 | -0.45776 | 0.36621 | 2.4857 | 0.21515 | 0.3067 | 0.65918 | 0.75073 | 7.0038 | 124.118 | 2.9297 | 124.7498 | 123.9212 | 123.9258 | 124.2004 | 123.4818 | -123.6603 | -124.3835 | 124.3973 | 124.3057 | 37.6282 | 11.293
514.9375 | 124.2691 | -38.1592 | 86.0596 | 0.13065 | 0.00080677 | 0.074528 | 0.1896 | -0.016787 | 0.03085 | 0.019498 | 0.0061157 | -0.0013718 | 0.053793 | 0.045102 | -0.036065 | 0.024074 | -0.027112 | -24.5316 | 86.8973 | -37.0285 | 87.4237 | -31.4072 | -32.5195 | -34.5886 | -27.5528 | 86.7599 | -37.2025 | 85.5331 | -35.994 | -37.706 | -37.9532 | 1.1307 | 0.83771 | 1.3641 | 6.752 | 3.5706 | 5.6396 | 2.4399 | 4.509 | 0.95673 | 0.70038 | -0.52643 | 2.1652 | 0.20599 | 0.45319 | -0.75073 | -0.50354 | 5.6213 | 124.4522 | 1.2085 | 122.7356 | 123.9258 | 123.9624 | 125.0565 | 124.9191 | -123.0881 | -123.262 | 125.5829 | 123.6923 | 13.6276 | 10.6064
515.9375 | 124.3057 | -36.2411 | 87.6022 | 0.039098 | 0.0061468 | 0.071323 | 0.1896 | -0.013582 | 0.032986 | 0.020566 | 0.067151 | 0.0093092 | 0.051657 | 0.045102 | -0.005089 | 0.017666 | -0.0014766 | -24.971 | 87.1033 | -36.8958 | 86.6547 | -31.398 | -22.0139 | -34.0256 | -26.8936 | 87.1994 | -36.644 | 88.3163 | -33.4259 | -35.4904 | -35.9802 | -0.6546 | -0.49896 | -0.94757 | 4.8431 | 2.2156 | 14.2273 | 2.8702 | 14.8819 | -0.40283 | -0.40283 | 0.71411 | 2.8152 | 0.26093 | 0.75073 | 0.66376 | 1.1536 | 5.4977 | 123.5504 | 3.2181 | 124.9603 | 123.999 | 123.8434 | 123.3444 | 123.4406 | -124.498 | -124.2462 | 122.8958 | 124.5575 | 11.2701 | 9.3475
516.9375 | 124.2691 | -37.4771 | 86.4716 | -0.021937 | 0.00080677 | 0.070255 | 0.20242 | -0.013582 | 0.049008 | 0.01843 | 0.067151 | 0.013582 | 0.075155 | 0.057919 | -0.004021 | 0.023006 | 0.0070684 | -19.4321 | 86.673 | -37.2299 | 86.9019 | -30.9952 | -14.859 | -34.6024 | -28.5828 | 86.9064 | -37.056 | 86.8927 | -34.8587 | -36.7264 | -37.3947 | 0.24719 | 0.20142 | 0.4303 | 6.4819 | 2.8748 | 22.6181 | 2.6276 | 22.3709 | 0.42114 | 0.43488 | 0.42114 | 2.6184 | 0.082398 | 0.75073 | -0.33875 | 0.32959 | 6.2347 | 124.1318 | 2.1973 | 123.9487 | 123.9029 | 123.9624 | 124.1501 | 124.3835 | -123.7015 | -123.5275 | 124.379 | 124.3698 | 18.045 | 8.8943
517.9375 | 124.2783 | -41.8808 | 82.1365 | -0.052455 | 0.036054 | 0.0788 | 0.37973 | 0.0088484 | 0.23379 | 0.017362 | -0.03966 | 0.010377 | 0.060202 | 0.11132 | -0.006157 | 0.017666 | 0.0006594 | -30.3726 | 87.3276 | -36.5433 | 82.9742 | -33.1284 | 30.2399 | -35.733 | -33.1558 | 82.3196 | -41.7023 | 82.2601 | -39.1983 | -40.892 | -41.4597 | 5.3375 | 5.191 | 0.83771 | 8.7524 | 6.1478 | 72.1207 | 0.81024 | 66.7831 | 0.17853 | 0.1831 | 0.1236 | 2.6825 | 0.42114 | 0.98877 | 0.24262 | 0.81024 | 3.4149 | 119.5175 | 2.504 | 123.9624 | 123.8708 | 124.0219 | 129.2084 | 124.2004 | -118.6798 | -123.8388 | 124.855 | 124.1409 | 11.5082 | 8.725
518.9375 | 124.2783 | -41.9449 | 82.1136 | -0.29659 | 0.00080677 | 0.098026 | 0.49081 | 0.0035084 | 0.32458 | 0.031247 | 0.11293 | 0.0018322 | 0.077291 | 0.065396 | 0.002387 | 0.018734 | -0.0004086 | -6.0974 | 81.9397 | -42.128 | 81.8481 | -34.0439 | 31.8512 | -37.5687 | -31.9794 | 81.8481 | -42.0685 | 82.1274 | -39.2258 | -41.2399 | -41.5604 | -0.18311 | -0.17395 | -0.2655 | 7.901 | 4.3762 | 73.7961 | 4.5593 | 73.9792 | -0.1236 | -0.2655 | 0.013733 | 2.7191 | 0.38452 | 0.70496 | 0.50812 | 0.82855 | 8.0841 | 123.9761 | 2.8427 | 124.1959 | 124.0677 | 123.9166 | 123.8846 | 123.793 | -124.2416 | -124.1821 | 123.793 | 124.0723 | 35.8475 | 9.9655
519.9375 | 124.3652 | -41.3177 | 81.6559 | 0.23746 | 0.014692 | 0.015781 | 0.080653 | 0.021666 | 0.040463 | 0.024839 | 5.835 | 0.29663 | 0.14885 | 0.087826 | -0.004021 | 0.015529 | 0.086109 | -31.7047 | 100.4974 | -23.6572 | -42.5583 | -23.0759 | -42.4026 | -10.8032 | -34.2865 | 87.822 | -34.7626 | 81.2668 | -39.83 | -39.7751 | -41.8854 | 17.6605 | 18.8416 | -124.2142 | 18.2419 | 30.5145 | -1.0849 | 12.854 | -18.7454 | 6.5552 | 6.1661 | -0.3891 | 1.4877 | -0.56763 | 1.5427 | -7.1228 | -5.0125 | 0.58136 | -18.9011 | -5.0674 | 116.0294 | 124.1547 | 122.5845 | 141.8152 | 129.1397 | -105.3131 | -116.4185 | -1.2405 | 122.5845 | 9.613 | 7.0312
520.9375 | 124.3561 | -45.2316 | 78.6255 | -0.89169 | 0.021101 | 0.12793 | 0.76959 | -0.0061046 | 0.54354 | 0.033384 | -0.23803 | 0.0018322 | 0.075155 | 0.062192 | -0.011498 | 0.019802 | 0.0027964 | 14.8453 | 78.3096 | -45.5109 | 78.5019 | -34.8541 | 61.5921 | -41.5466 | -40.9698 | 78.1357 | -45.4422 | 78.8177 | -42.3477 | -44.3436 | -44.7556 | -0.27924 | -0.31586 | -0.1236 | 10.3775 | 3.685 | 106.8237 | 3.9642 | 107.103 | -0.21057 | -0.48981 | 0.19226 | 2.8839 | 0.47607 | 0.88806 | 0.68665 | 1.0986 | 10.6567 | 124.0128 | 3.0945 | 124.2599 | 123.8205 | 123.5779 | 123.5413 | 123.3673 | -124.1364 | -124.0677 | 123.7335 | 124.0494 | 60.0769 | 4.2618
521.9375 | 124.3378 | 3.1311 | 147.0016 | -0.37289 | -0.017351 | 0.098026 | 0.7023 | -0.0061046 | 0.54568 | -0.011477 | -0.42113 | 0.01465 | 0.086904 | 0.064328 | 0.018409 | 0.027279 | 0.02309 | -1.0391 | 80.0217 | -29.5074 | 47.4152 | -22.6273 | 31.8832 | -0.19226 | 0.1236 | 79.7379 | -0.013733 | 149.9954 | 42.16 | 22.8195 | 24.5728 | -32.6386 | -66.98 | -99.5865 | -25.7584 | -3.3234 | 28.7521 | 29.3152 | 61.3907 | -3.1448 | -67.2638 | 2.9938 | 39.0289 | 21.4416 | 19.6884 | 24.5865 | 22.8333 | 6.8802 | 76.9226 | 42.1738 | 150.0092 | 109.5291 | 79.7516 | 76.8906 | 76.6068 | -176.5091 | -147.0154 | 44.2841 | 146.8643 | -4.1702 | -3.0075
522.9375 | 124.3332 | -47.1634 | 76.7258 | -0.43392 | 0.0018748 | 0.1493 | 0.72686 | -0.0050366 | 0.52218 | 0.0024082 | -0.14647 | -0.0024398 | 0.082632 | 0.032284 | -0.01043 | 0.014461 | 0.0081364 | 12.1948 | 73.9105 | -49.9054 | 73.8968 | -21.0663 | 47.7402 | 6.9855 | -46.1975 | 73.4116 | -50.0656 | 77.5314 | -44.1376 | -45.6619 | -46.6049 | -2.742 | -2.8152 | -2.829 | 26.0971 | 54.1489 | 94.9036 | 56.8909 | 97.6456 | -2.9022 | -3.3142 | 0.80566 | 3.0258 | 0.55847 | 1.5015 | 3.4607 | 4.4037 | 28.8391 | 123.8022 | 5.928 | 127.597 | 123.8159 | 123.4772 | 121.0739 | 120.575 | -126.6312 | -126.7914 | 121.0602 | 124.6948 | 59.3582 | 0.96588
523.9375 | 124.3881 | -27.1408 | 96.785 | 0.0085801 | 0.0072148 | 0.023258 | 0.060359 | 0.016325 | 0.0062828 | -0.0018638 | -0.085437 | 0.010377 | 0.079428 | 0.060055 | -0.002953 | 0.014461 | 0.015613 | -23.1491 | 96.6293 | -27.3056 | -26.413 | -22.5815 | -26.5274 | -19.9997 | -23.8815 | 96.3272 | -27.2873 | 96.9177 | -24.8566 | -26.1017 | -26.7838 | -0.1648 | -0.15564 | -123.1979 | 4.5593 | 7.1411 | 0.6134 | 7.3059 | 0.7782 | -0.14648 | -0.45776 | 0.13275 | 2.2842 | 0.35706 | 1.0391 | 0.50354 | 1.1856 | 4.7241 | 0.89264 | 2.4307 | 124.205 | 123.9349 | 123.6145 | 123.7701 | 123.468 | -124.0906 | -124.0723 | 0.72784 | 124.0585 | 3.9917 | 3.2593
524.9375 | 124.3286 | -27.3834 | 96.5927 | 0.11539 | 0.0072148 | 0.0061675 | 0.057155 | -0.0039686 | 0.0094878 | 0.014158 | -0.024402 | 0.0039692 | 0.064474 | 0.051511 | 0.002387 | 0.027279 | 0.018817 | -23.9365 | 96.524 | -27.4887 | -26.5137 | -22.7371 | -26.6464 | -20.1324 | -23.703 | 96.5012 | -27.4475 | 96.7255 | -25.058 | -26.3718 | -26.9348 | -0.10528 | -0.068664 | -123.1064 | 4.6463 | 7.251 | 0.737 | 7.3563 | 0.84229 | -0.064087 | -0.091552 | 0.13275 | 2.3254 | 0.44861 | 1.0117 | 0.5127 | 1.0757 | 4.7516 | 0.97504 | 2.3895 | 124.173 | 124.0128 | 123.9487 | 123.9075 | 123.8846 | -124.0814 | -124.0402 | 0.86975 | 124.1089 | 3.447 | 3.6804
525.9375 | 124.3195 | -27.2461 | 96.7163 | 0.023839 | 0.016828 | 0.0050995 | 0.051814 | 0.015257 | -0.030033 | -0.0018638 | -0.024402 | 0.015718 | 0.069815 | 0.058987 | -0.004021 | 0.033687 | 0.0092044 | -23.5519 | 96.6156 | -27.3468 | -26.3123 | -22.554 | -26.4359 | -20.3018 | -23.1949 | 96.6385 | -27.301 | 96.9223 | -25.1221 | -26.2848 | -26.7517 | -0.10071 | -0.10071 | -123.0286 | 4.6921 | 6.9443 | 0.81024 | 7.045 | 0.91095 | -0.054931 | -0.07782 | 0.20599 | 2.124 | 0.49438 | 0.9613 | 0.54932 | 1.0162 | 4.7928 | 1.0345 | 2.179 | 124.2233 | 123.9624 | 123.9395 | 123.8617 | 123.8846 | -124.0631 | -124.0173 | 0.93384 | 124.1684 | 3.6942 | 4.0512
526.9375 | 124.3286 | -26.8478 | 97.1603 | 0.039098 | 0.013624 | 0.013645 | 0.051814 | -0.00076463 | -0.0022622 | 0.010953 | -0.085437 | 0.0039692 | 0.064474 | 0.087826 | -0.016839 | 0.016598 | -0.0004086 | -23.172 | 97.0825 | -26.9485 | -25.8728 | -22.1008 | -26.0284 | -20.3201 | -24.4629 | 97.0505 | -26.8936 | 97.3389 | -24.7101 | -25.4379 | -26.2985 | -0.10071 | -0.077819 | -123.0331 | 4.747 | 6.5277 | 0.8194 | 6.6284 | 0.92011 | -0.045777 | -0.10986 | 0.17853 | 2.1378 | 0.54932 | 1.4099 | 0.59509 | 1.4557 | 4.8477 | 1.0757 | 2.1835 | 124.2325 | 124.0311 | 123.9441 | 123.9304 | 123.8983 | -124.1089 | -124.054 | 0.97504 | 124.1867 | 3.6758 | 2.3849
527.9375 | 124.3149 | -26.825 | 97.2015 | 0.14591 | 0.01042 | -0.00024048 | 0.047541 | -0.0082416 | -0.016147 | -0.0061368 | -0.14647 | 0.017854 | 0.070883 | 0.10919 | -0.008294 | 0.023006 | -0.0078856 | -24.7513 | 97.1054 | -26.9073 | -25.7767 | -21.8445 | -25.914 | -20.2789 | -25.0488 | 97.1283 | -26.8616 | 97.3846 | -24.7009 | -25.3738 | -26.2161 | -0.082398 | -0.09613 | -122.9782 | 4.9805 | 6.546 | 0.91095 | 6.6284 | 0.99335 | -0.036621 | -0.073242 | 0.18311 | 2.124 | 0.60883 | 1.4511 | 0.64545 | 1.4877 | 5.0629 | 1.1307 | 2.1606 | 124.2462 | 124.0128 | 123.9899 | 123.9304 | 123.9532 | -124.1089 | -124.0631 | 1.0483 | 124.2096 | 2.0737 | 1.7761
528.9375 | 124.3515 | -26.4679 | 97.5632 | 0.10013 | 0.021101 | -0.00024048 | 0.049678 | -0.0071726 | 0.0041468 | -0.0082728 | -0.16173 | 0.017854 | 0.062338 | 0.070737 | -0.021111 | 0.032619 | 0.0006594 | -24.4125 | 97.5082 | -26.5182 | -25.3189 | -22.0505 | -25.4837 | -20.6863 | -24.4446 | 97.5128 | -26.4542 | 97.8149 | -24.4171 | -25.1358 | -25.8545 | -0.050354 | -0.054931 | -122.8821 | 4.4174 | 5.7816 | 0.98419 | 5.8319 | 1.0345 | 0.013733 | -0.050354 | 0.25177 | 2.0508 | 0.6134 | 1.3321 | 0.59967 | 1.3184 | 4.4678 | 1.1993 | 2.037 | 124.2691 | 124.0265 | 123.967 | 123.9761 | 123.9807 | -124.0814 | -124.0173 | 1.149 | 124.2828 | 2.0554 | 2.0233
529.9375 | 124.3149 | -26.0422 | 97.9797 | 0.084874 | 0.011488 | 0.013645 | 0.047541 | 0.0035084 | 0.015896 | -0.014682 | 0.051892 | 0.0029002 | 0.068746 | 0.070737 | -0.009362 | 0.02087 | 0.0038644 | -24.5407 | 97.8378 | -26.1429 | -25.0214 | -21.7896 | -25.1724 | -20.8603 | -23.3231 | 97.8745 | -26.0925 | 98.1491 | -23.9822 | -24.5865 | -25.3922 | -0.10071 | -0.14191 | -123.0011 | 4.2526 | 5.1819 | 0.86975 | 5.2826 | 0.97046 | -0.050354 | -0.10529 | 0.16937 | 2.0599 | 0.65002 | 1.4557 | 0.70038 | 1.506 | 4.3533 | 1.1215 | 2.1103 | 124.2416 | 123.9807 | 123.967 | 123.88 | 123.9166 | -124.1226 | -124.0723 | 1.0208 | 124.1913 | 1.5015 | 2.7191
530.9375 | 124.3103 | -26.207 | 97.8424 | 0.069615 | 0.014692 | 0.0083045 | 0.04861 | -0.01465 | 0.023373 | 0.0088172 | -0.03966 | 0.0061052 | 0.070883 | 0.076077 | -0.013634 | 0.023006 | -0.016431 | -24.4995 | 97.7692 | -26.2619 | -25.1404 | -22.0367 | -25.2777 | -21.167 | -23.0347 | 97.8287 | -26.1978 | 98.0347 | -24.0509 | -24.7238 | -25.4883 | -0.054932 | -0.073242 | -122.9828 | 4.1702 | 5.04 | 0.92926 | 5.0949 | 0.98419 | 0.009155 | -0.013733 | 0.19226 | 2.1561 | 0.71869 | 1.4832 | 0.70953 | 1.474 | 4.2252 | 1.1215 | 2.1469 | 124.2325 | 124.0311 | 124.0265 | 123.9761 | 124.0356 | -124.1043 | -124.0402 | 1.0666 | 124.2416 | 1.7075 | 3.1723
531.9375 | 124.2828 | -25.8408 | 98.1995 | 0.069615 | 0.012556 | 0.0050995 | 0.052882 | 0.0024404 | -0.0076022 | 0.00027221 | 0.12819 | 0.010377 | 0.076223 | 0.036557 | -0.013634 | 0.03796 | -0.0014766 | -23.7625 | 98.1033 | -25.9048 | -24.8062 | -22.1283 | -24.9893 | -20.1828 | -23.0392 | 98.1262 | -25.8774 | 98.3414 | -23.8083 | -24.2935 | -25.0076 | -0.064087 | -0.09613 | -123.0057 | 3.7125 | 5.658 | 0.85144 | 5.722 | 0.91553 | -0.036621 | -0.073242 | 0.14191 | 2.0325 | 0.83313 | 1.5472 | 0.86975 | 1.5839 | 3.7766 | 1.0986 | 2.0691 | 124.2188 | 124.0082 | 124.0036 | 123.9441 | 123.967 | -124.1043 | -124.0768 | 1.0345 | 124.1821 | 2.0782 | 2.8015
532.9375 | 124.3149 | -25.7721 | 98.2819 | 0.10013 | 0.0061468 | -0.0023775 | 0.052882 | -0.011446 | -0.0043982 | -0.0082728 | -0.13121 | 0.0071732 | 0.071951 | 0.057919 | -0.014702 | 0.014461 | -0.014294 | -23.2407 | 98.2407 | -25.8133 | -24.5361 | -21.7804 | -24.7421 | -19.7571 | -21.9498 | 98.1857 | -25.7996 | 98.4375 | -23.7122 | -24.2249 | -24.7787 | -0.041198 | -0.041198 | -122.818 | 3.9917 | 6.015 | 1.03 | 6.0562 | 1.0712 | -0.027466 | -0.09613 | 0.15564 | 2.0599 | 0.99335 | 1.5472 | 1.0208 | 1.5747 | 4.0329 | 1.2772 | 2.0874 | 124.2371 | 124.054 | 123.9853 | 124.0128 | 123.9578 | -124.0952 | -124.0814 | 1.236 | 124.2096 | 2.5314 | 3.8223
533.9531 | 124.1913 | -25.708 | 98.41 | 0.25272 | 0.017896 | 0.0040315 | 0.044337 | 0.0024404 | 0.011624 | -0.0018638 | -0.2838 | 0.0039692 | 0.094381 | 0.049374 | -0.037133 | -0.029331 | -0.039929 | -23.0026 | 98.3047 | -25.7721 | -24.4629 | -21.611 | -24.6597 | -19.7571 | -22.0917 | 98.2727 | -25.7584 | 98.4421 | -23.7488 | -24.1516 | -24.9893 | -0.064087 | -0.10528 | -122.8729 | 4.097 | 5.9509 | 1.0483 | 6.015 | 1.1124 | -0.050354 | -0.13733 | 0.032044 | 1.9592 | 0.71869 | 1.5564 | 0.76904 | 1.6068 | 4.1611 | 1.3092 | 2.0096 | 124.2004 | 124.0768 | 124.0311 | 124.0128 | 123.9807 | -124.1821 | -124.1684 | 1.2451 | 124.1501 | 2.7054 | 3.6163
534.9375 | 124.2416 | -25.7172 | 98.3871 | 0.49686 | 0.0050788 | 0.0050995 | 0.042201 | 0.012053 | 0.00094276 | 0.0024082 | -0.054919 | 0.013582 | 0.084768 | 0.064328 | -0.01043 | 0.031551 | -0.0004086 | -23.6481 | 98.3185 | -25.7858 | -24.3668 | -21.6156 | -24.5544 | -20.4163 | -22.0642 | 98.3002 | -25.7538 | 98.4192 | -23.7854 | -24.2523 | -24.8703 | -0.068665 | -0.068665 | -122.7539 | 4.1016 | 5.3009 | 1.1627 | 5.3696 | 1.2314 | -0.036621 | -0.086975 | 0.032043 | 1.9318 | 0.84686 | 1.4648 | 0.88348 | 1.5015 | 4.1702 | 1.4191 | 1.9684 | 124.173 | 124.1043 | 124.054 | 124.0356 | 124.0173 | -124.173 | -124.1409 | 1.3504 | 124.1364 | 2.0691 | 3.653
535.9375 | 124.2737 | -25.5386 | 98.5016 | 0.10013 | 0.0040108 | -0.0013085 | 0.050746 | -0.0082416 | -0.0086702 | -0.00079579 | -0.024402 | 0.0061052 | 0.068746 | 0.06326 | -0.007226 | 0.036892 | 0.012409 | -22.6547 | 98.4283 | -25.6485 | -24.1928 | -21.2814 | -24.4995 | -20.2286 | -22.0917 | 98.4421 | -25.5936 | 98.6252 | -23.5245 | -23.877 | -24.6689 | -0.10986 | -0.073242 | -122.6944 | 4.2572 | 5.3101 | 1.0391 | 5.4199 | 1.149 | -0.054932 | -0.059509 | 0.1236 | 2.0142 | 0.86975 | 1.6617 | 0.92468 | 1.7166 | 4.3671 | 1.4557 | 2.0691 | 124.2188 | 124.0768 | 124.0356 | 123.967 | 123.9807 | -124.1501 | -124.0952 | 1.3458 | 124.1638 | 2.8839 | 3.447
536.9375 | 124.2416 | -25.1724 | 98.9365 | 0.16117 | 0.016828 | -0.0013085 | 0.046473 | 0.0035084 | 0.0062828 | -0.00079579 | -0.070178 | 0.017854 | 0.075155 | 0.051511 | -0.007226 | 0.039028 | -0.0046806 | -22.5906 | 98.7488 | -25.3555 | -23.4467 | -20.7459 | -24.2477 | -21.0297 | -22.6959 | 98.8724 | -25.1999 | 98.9868 | -23.3414 | -23.4787 | -24.2935 | -0.18311 | -0.18768 | -122.3831 | 4.4266 | 4.1428 | 0.92468 | 4.3259 | 1.1078 | -0.027466 | -0.064087 | 0.050354 | 1.8311 | 0.87891 | 1.6937 | 0.90637 | 1.7212 | 4.6097 | 1.9089 | 1.8585 | 124.1867 | 124.1043 | 124.0723 | 123.9212 | 124.0448 | -124.292 | -124.1364 | 1.7258 | 124.1592 | 2.5818 | 2.4765
537.9375 | 124.3011 | -24.614 | 99.3439 | 0.0085801 | 0.021101 | -0.00024048 | 0.03686 | 0.0035084 | 0.020169 | 0.0056132 | -0.1007 | 0.013582 | 0.071951 | 0.075009 | -0.012566 | 0.031551 | 0.0027964 | -23.5748 | 99.3164 | -24.7284 | -24.5682 | -21.8216 | -24.321 | -20.8786 | -22.0551 | 99.2661 | -24.6643 | 99.5636 | -22.7692 | -23.0988 | -24.0829 | -0.11444 | -0.027466 | -123.912 | 2.7924 | 3.7354 | 0.29297 | 3.8498 | 0.40741 | -0.050354 | -0.07782 | 0.21973 | 1.8448 | 0.53101 | 1.5152 | 0.58136 | 1.5656 | 2.9068 | 0.16022 | 1.8951 | 124.2279 | 124.0448 | 123.9304 | 123.9304 | 123.88 | -124.0723 | -124.0082 | 0.045777 | 124.1776 | 1.0391 | 2.5589
538.9844 | 124.3652 | -52.8854 | 70.9763 | -0.75436 | 0.94716 | 0.13968 | 0.069972 | 0.013121 | 0.80951 | 0.00027221 | 0.34181 | 0.0039692 | 0.099722 | 0.050442 | -0.005089 | 0.023006 | 0.020953 | 18.8187 | 70.8115 | -52.9861 | 64.4943 | -8.7753 | 70.7748 | 17.1707 | -49.4247 | 70.9213 | -53.0136 | 71.1044 | -50.4318 | -50.8575 | -51.7868 | -0.10071 | -0.16479 | -6.4819 | 44.1101 | 70.0562 | 123.6603 | 70.1569 | 123.761 | -0.12817 | -0.054931 | 0.12817 | 2.4536 | 1.0986 | 2.0279 | 1.2268 | 2.1561 | 44.2108 | 117.4805 | 2.5818 | 124.118 | 123.7976 | 123.9349 | 123.6969 | 123.8068 | -123.9624 | -123.9899 | 117.3798 | 123.9899 | 71.7041 | 3.4607
539.9844 | 124.3103 | -51.1459 | 72.7158 | -0.83065 | 0.93541 | 0.13327 | 0.077449 | -0.010378 | 0.80203 | -0.0061368 | 0.235 | 0.0082412 | 0.0837 | 0.032284 | -0.009362 | 0.019802 | -0.0025446 | 19.9677 | 72.5464 | -51.2421 | 66.1377 | -20.1782 | 72.3953 | 19.9539 | -48.1796 | 72.551 | -51.3062 | 72.908 | -48.761 | -49.0448 | -49.8917 | -0.09613 | -0.16937 | -6.5781 | 30.9677 | 71.0999 | 123.5413 | 71.196 | 123.6374 | -0.16022 | -0.1648 | 0.19226 | 2.3849 | 1.2543 | 2.1011 | 1.4145 | 2.2614 | 31.0638 | 117.3798 | 2.5452 | 124.2142 | 123.7885 | 123.8571 | 123.6923 | 123.6969 | -123.9578 | -124.0219 | 117.2836 | 124.054 | 71.1136 | 2.9663
540.9531 | 124.1501 | -50.5783 | 73.3566 | -0.75436 | 0.93113 | 0.13648 | 0.076381 | 0.014189 | 0.8031 | 0.010953 | -0.070178 | 0.0018322 | 0.085836 | 0.066464 | -0.00081695 | 0.031551 | 0.0070684 | 19.4046 | 73.2101 | -50.6607 | 66.9159 | -17.0013 | 73.1323 | 14.6164 | -48.1293 | 73.3246 | -50.6561 | 73.4116 | -47.9324 | -48.6511 | -49.4156 | -0.082398 | -0.14648 | -6.4407 | 33.577 | 65.1947 | 123.7106 | 65.2771 | 123.793 | -0.07782 | -0.032043 | 0.054932 | 2.6459 | 1.1627 | 1.9272 | 1.2405 | 2.005 | 33.6594 | 117.5766 | 2.7237 | 124.0677 | 123.8708 | 123.9807 | 123.7885 | 123.9029 | -124.0173 | -124.0128 | 117.4942 | 123.9899 | 69.9829 | 2.449
541.9375 | 124.1318 | -50.9171 | 73.0545 | -0.83065 | 0.91404 | 0.12366 | 0.069972 | 0.0088484 | 0.76358 | 0.0066812 | -0.83312 | -0.047301 | 0.076223 | 0.060055 | -0.045678 | -0.048557 | -0.040997 | 22.4213 | 72.8714 | -50.9491 | 65.7669 | -19.8532 | 72.6654 | 15.6372 | -48.3719 | 73.0087 | -50.9628 | 73.1323 | -48.3444 | -48.9716 | -49.5941 | -0.032044 | -0.1831 | -7.2876 | 31.0638 | 66.5543 | 123.5825 | 66.5863 | 123.6145 | -0.045777 | -0.045776 | 0.07782 | 2.5726 | 1.3229 | 1.9455 | 1.3687 | 1.9913 | 31.0959 | 116.716 | 2.6184 | 124.0952 | 123.8205 | 123.9716 | 123.7885 | 123.9258 | -124.0036 | -124.0173 | 116.684 | 124.0494 | 73.3383 | 2.5452
542.9375 | 124.0906 | -51.6403 | 72.3633 | -0.76962 | 0.91939 | 0.129 | 0.066768 | 0.032347 | 0.7796 | 0.010953 | -0.11595 | 0.01999 | 0.075155 | 0.050442 | -0.014702 | 0.033687 | 0.017749 | 21.1349 | 72.2076 | -51.6403 | 64.6088 | -18.4982 | 72.0749 | 15.6281 | -49.6262 | 72.2122 | -51.7364 | 72.2763 | -49.5026 | -49.704 | -50.2853 | 0 | -0.15564 | -7.7545 | 33.1421 | 67.2684 | 123.7152 | 67.2684 | 123.7152 | -0.09613 | -0.15106 | -0.086975 | 2.1378 | 1.355 | 1.9363 | 1.4511 | 2.0325 | 33.1421 | 116.2491 | 2.2339 | 124.0128 | 123.848 | 123.9487 | 123.848 | 123.8525 | -124.0036 | -124.0997 | 116.2491 | 123.9166 | 72.7753 | 2.0142
544.1094 | 124.1638 | -51.6632 | 72.2855 | -0.67806 | 0.92045 | 0.13007 | 0.062495 | 0.012053 | 0.79776 | 0.012021 | 0.26551 | 0.0082412 | 0.095449 | 0.075009 | 0.002387 | 0.025143 | 0.0027964 | 22.8653 | 72.1985 | -51.5854 | 64.801 | -17.6147 | 71.9788 | 11.6821 | -49.7452 | 72.1161 | -51.741 | 72.3587 | -49.823 | -49.5621 | -50.1297 | 0.07782 | -0.086975 | -7.4844 | 34.0485 | 63.3453 | 123.642 | 63.2675 | 123.5641 | -0.07782 | -0.16937 | 0.073243 | 1.8402 | 1.5335 | 2.1011 | 1.6113 | 2.179 | 33.9706 | 116.3864 | 1.918 | 124.0997 | 123.7839 | 123.8571 | 123.8617 | 123.7793 | -123.8708 | -124.0265 | 116.4642 | 124.0219 | 74.5285 | 1.918
544.9375 | 124.1043 | -51.915 | 72.0245 | -0.54074 | 0.92366 | 0.14182 | 0.079585 | 0.012053 | 0.76037 | 0.016294 | -0.085437 | 0.017854 | 0.071951 | 0.058987 | -0.011498 | 0.026211 | -0.0025446 | 22.6364 | 71.933 | -51.8555 | 64.5081 | -16.5802 | 71.9009 | 10.9406 | -50.0061 | 71.9925 | -51.9196 | 72.0932 | -50.1389 | -49.7635 | -50.4272 | 0.059509 | -0.091553 | -7.5165 | 35.3348 | 62.8555 | 123.8159 | 62.796 | 123.7564 | -0.004578 | -0.032043 | 0.068665 | 1.7761 | 1.4877 | 2.1515 | 1.4923 | 2.1561 | 35.2753 | 116.3635 | 1.7807 | 124.0128 | 123.7885 | 123.912 | 123.848 | 123.9075 | -123.88 | -123.9441 | 116.423 | 124.0082 | 74.5514 | 1.9089
545.9531 | 124.0768 | -52.2858 | 71.6583 | -0.72384 | 0.91618 | 0.13755 | 0.07104 | 0.032347 | 0.7796 | 0.025907 | 0.021375 | 0.0093092 | 0.089041 | 0.067532 | -0.006157 | 0.033687 | 0.027362 | 25.1633 | 71.5393 | -52.2491 | 63.5834 | -19.5923 | 71.5256 | 11.9202 | -50.4227 | 71.6492 | -52.2812 | 71.7087 | -50.1984 | -50.0519 | -50.5188 | 0.036621 | -0.11902 | -8.075 | 32.6935 | 64.2059 | 123.8113 | 64.1693 | 123.7747 | 0.004578 | -0.009155 | 0.050354 | 2.0874 | 1.767 | 2.2339 | 1.7624 | 2.2293 | 32.6569 | 115.8325 | 2.0828 | 123.9899 | 123.7885 | 123.9304 | 123.8251 | 123.9349 | -123.9075 | -123.9395 | 115.8691 | 123.9944 | 77.449 | 1.8631
546.9375 | 124.086 | -51.8784 | 72.0795 | -0.78488 | 0.92259 | 0.1557 | 0.069972 | 0.013121 | 0.74328 | 0.010953 | -0.024402 | 0.01465 | 0.092245 | 0.095303 | -0.006157 | 0.036892 | 0.025226 | 28.1891 | 71.9559 | -51.8555 | 64.0182 | -19.1895 | 71.9604 | 11.3113 | -50.0107 | 72.02 | -51.9012 | 71.965 | -49.173 | -49.7177 | -50.2396 | 0.022888 | -0.1236 | -8.0612 | 32.6889 | 63.1897 | 123.8388 | 63.1668 | 123.8159 | -0.022888 | -0.05951 | -0.11444 | 2.7054 | 1.6388 | 2.1606 | 1.6617 | 2.1835 | 32.666 | 115.8737 | 2.7283 | 123.8663 | 123.8113 | 123.9212 | 123.8342 | 123.8983 | -123.9349 | -123.9807 | 115.8966 | 123.8434 | 80.0674 | 1.8677
547.9688 | 124.1043 | -52.1301 | 71.7682 | -0.57125 | 0.90336 | 0.15143 | 0.076381 | 0.00030337 | 0.75824 | -0.00079579 | -0.054919 | 0.010377 | 0.096517 | 0.079282 | -0.005089 | 0.030483 | 0.0070684 | 27.9419 | 71.5759 | -52.1988 | 63.6887 | -17.8345 | 71.5851 | 9.7961 | -50.1938 | 71.6263 | -52.2354 | 71.9101 | -49.6811 | -49.8734 | -50.2625 | -0.068665 | -0.19226 | -8.0795 | 34.2957 | 61.9263 | 123.7152 | 61.9949 | 123.7839 | -0.10529 | -0.14191 | 0.14191 | 2.449 | 1.8677 | 2.2568 | 1.973 | 2.3621 | 34.3643 | 115.8875 | 2.5543 | 124.1455 | 123.7747 | 123.8617 | 123.7061 | 123.7564 | -123.967 | -124.0036 | 115.8188 | 124.0402 | 80.072 | 1.9363
548.9375 | 124.054 | -50.9399 | 72.9858 | -0.76962 | 0.92259 | 0.15036 | 0.062495 | 0.0077804 | 0.77319 | 0.022702 | -0.22277 | 0.01999 | 0.095449 | 0.094235 | -0.008294 | 0.0048481 | -0.0025446 | 25.7996 | 72.8394 | -50.9171 | 65.2725 | -18.1961 | 72.8485 | 6.752 | -49.1135 | 72.9538 | -50.9583 | 73.082 | -48.3627 | -48.6603 | -48.9578 | 0.022888 | -0.14648 | -7.7133 | 32.7438 | 57.692 | 123.7885 | 57.6691 | 123.7656 | -0.018311 | -0.032044 | 0.09613 | 2.5772 | 1.9821 | 2.2797 | 2.0004 | 2.298 | 32.7209 | 116.1896 | 2.5955 | 124.0402 | 123.7564 | 123.912 | 123.7793 | 123.8937 | -123.9029 | -123.9441 | 116.2125 | 124.0219 | 76.7395 | 1.8265
549.9688 | 123.3261 | -45.7947 | 78.1631 | -0.60177 | 0.87025 | 0.11298 | 0.066768 | 0.018461 | 0.7561 | 0.0077492 | -0.16173 | 0.012514 | 0.096517 | 0.12307 | -0.002953 | 0.0059161 | -0.031384 | 27.8824 | 77.98 | -45.8221 | -3.186 | -23.2132 | 77.948 | -4.985 | -44.0781 | 77.9892 | -45.8908 | 78.2181 | -42.6224 | -43.4692 | -43.9865 | -0.027466 | -0.1831 | -81.3492 | 22.5815 | 40.8096 | 123.7427 | 40.8371 | 123.7701 | -0.09613 | -0.17395 | 0.054932 | 3.1723 | 1.8082 | 2.3254 | 1.9043 | 2.4216 | 22.6089 | 42.6361 | 3.2684 | 124.1089 | 123.8022 | 123.88 | 123.7747 | 123.7839 | -123.9853 | -124.054 | 42.6086 | 124.0128 | 73.6771 | 1.7166
550.9375 | 124.0356 | -47.8638 | 76.1124 | -0.67806 | 0.88948 | 0.13861 | 0.079585 | 0.027006 | 0.77639 | 0.0045452 | -0.085437 | 0.015718 | 0.097586 | 0.091031 | -0.014702 | 0.026211 | 0.02309 | 26.7197 | 76.1444 | -47.7264 | 32.8125 | -22.3938 | 75.8926 | -2.5909 | -45.8817 | 75.8926 | -48.0103 | 76.0437 | -43.4052 | -45.4102 | -45.9183 | 0.13733 | 0.032043 | -43.2999 | 25.47 | 45.2728 | 123.7564 | 45.1355 | 123.6191 | -0.14648 | -0.21973 | -0.068665 | 4.4586 | 1.9455 | 2.4536 | 2.092 | 2.6001 | 25.3326 | 80.5389 | 4.6051 | 124.054 | 123.8708 | 123.9029 | 124.0082 | 123.7564 | -123.8388 | -124.1226 | 80.6763 | 123.9075 | 74.5834 | 1.9821
551.9688 | 124.1226 | -51.1871 | 72.6974 | -0.70858 | 0.91511 | 0.14716 | 0.063563 | -0.00076463 | 0.74862 | 0.00027221 | 0.051892 | 0.012514 | 0.090109 | 0.14123 | 0.00025105 | 0.026211 | 0.0060004 | 26.358 | 72.3587 | -51.3886 | 63.4232 | -17.2485 | 72.3495 | 3.3554 | -48.6099 | 72.4503 | -51.4069 | 72.789 | -46.637 | -48.1247 | -49.3652 | -0.20142 | -0.33875 | -9.2743 | 33.9386 | 54.5425 | 123.5367 | 54.744 | 123.7381 | -0.21973 | -0.24719 | 0.091552 | 4.5502 | 1.8219 | 3.0624 | 2.0416 | 3.2822 | 34.14 | 114.8117 | 4.7699 | 124.1959 | 123.7473 | 123.8571 | 123.5458 | 123.6374 | -124.086 | -124.1043 | 114.6103 | 123.9761 | 77.5452 | 2.5772
552.9375 | 123.9944 | -52.272 | 71.6263 | -0.70858 | 0.92152 | 0.15998 | 0.066768 | 0.0067124 | 0.76144 | 0.00027221 | -0.16173 | 0.021058 | 0.091177 | 0.071805 | -0.009362 | 0.030483 | 0.016681 | 29.6494 | 71.402 | -52.3407 | 62.7182 | -14.4516 | 71.521 | 4.7287 | -49.8413 | 71.5988 | -52.3361 | 71.6217 | -49.7818 | -49.8505 | -50.386 | -0.068664 | -0.2243 | -8.9081 | 37.8204 | 57.0007 | 123.793 | 57.0694 | 123.8617 | -0.064087 | -0.027466 | -0.004578 | 2.4902 | 1.886 | 2.4216 | 1.9501 | 2.4857 | 37.8891 | 115.0589 | 2.5543 | 123.9578 | 123.7427 | 123.9349 | 123.674 | 123.8708 | -123.967 | -123.9624 | 114.9902 | 123.8937 | 81.9214 | 2.4307
553.9531 | 124.0265 | -52.327 | 71.6034 | -0.66281 | 0.91618 | 0.15677 | 0.055018 | 0.0056444 | 0.76999 | -0.0072048 | 0.26551 | 0.025331 | 0.10399 | 0.032284 | -0.007226 | 0.028347 | 0.016681 | 29.5029 | 71.4294 | -52.3041 | 62.8235 | -12.7533 | 71.4569 | 3.3875 | -49.7726 | 71.5393 | -52.359 | 71.5942 | -50.1709 | -49.5758 | -50.4318 | 0.022888 | -0.17395 | -8.7799 | 39.5737 | 55.7144 | 123.7839 | 55.6915 | 123.761 | -0.032044 | -0.064087 | -0.009156 | 2.1561 | 1.8951 | 2.7512 | 1.9272 | 2.7832 | 39.5508 | 115.1276 | 2.1881 | 123.9532 | 123.7335 | 123.8983 | 123.7564 | 123.8663 | -123.9075 | -123.9624 | 115.1505 | 123.9212 | 81.8298 | 2.5543
554.9375 | 124.0997 | -52.4597 | 71.4569 | -0.69332 | 0.91618 | 0.16852 | 0.067836 | 0.0056444 | 0.73367 | -0.0018638 | 0.021375 | 0.021058 | 0.10079 | 0.089963 | -0.014702 | 0.03796 | 0.019885 | 25.209 | 71.3058 | -52.4139 | 62.9929 | -10.3958 | 71.2372 | 2.1057 | -49.7269 | 71.3425 | -52.5513 | 71.7041 | -50.1617 | -49.6857 | -50.5325 | 0.045777 | -0.15106 | -8.464 | 42.0639 | 54.5654 | 123.6969 | 54.5197 | 123.6511 | -0.091553 | -0.11444 | 0.24719 | 2.298 | 1.9272 | 2.774 | 2.0187 | 2.8656 | 42.0181 | 115.4068 | 2.3895 | 124.2554 | 123.7198 | 123.8937 | 123.7656 | 123.8022 | -123.8708 | -124.0082 | 115.4526 | 124.1638 | 77.6688 | 2.7328
555.9375 | 124.0814 | -52.1347 | 71.7636 | -0.66281 | 0.92473 | 0.16852 | 0.07104 | 0.017393 | 0.74008 | 0.016294 | 0.021375 | 0.024263 | 0.085836 | 0.079282 | -0.007226 | 0.039028 | 0.0092044 | 26.9348 | 71.6446 | -52.0569 | 63.5788 | -7.7454 | 71.6217 | -2.7145 | -47.4747 | 71.7499 | -52.0935 | 71.7041 | -49.6216 | -49.2599 | -50.0977 | 0.07782 | -0.11902 | -8.1848 | 44.3893 | 49.4202 | 123.7564 | 49.3423 | 123.6786 | 0.041199 | -0.013733 | -0.059509 | 2.5131 | 2.037 | 2.8748 | 1.9958 | 2.8336 | 44.3115 | 115.6357 | 2.4719 | 123.7976 | 123.7015 | 123.8434 | 123.7793 | 123.8846 | -123.8205 | -123.8571 | 115.7135 | 123.8388 | 79.0695 | 4.66
556.9688 | 124.0219 | -52.739 | 71.1914 | -0.69332 | 0.91832 | 0.17066 | 0.063563 | 0.017393 | 0.75076 | 0.0024082 | 0.0061157 | 0.018922 | 0.10613 | 0.073941 | -0.016839 | 0.035824 | 0.0081364 | 26.0925 | 70.9396 | -52.8305 | 62.5946 | -4.9713 | 71.0175 | -2.7374 | -46.4081 | 71.2051 | -52.7069 | 71.2143 | -49.7955 | -49.9191 | -50.766 | -0.091552 | -0.25177 | -8.5968 | 47.7676 | 50.0015 | 123.7564 | 50.0931 | 123.848 | 0.032044 | 0.013733 | 0.022888 | 2.9434 | 1.973 | 2.8198 | 1.9409 | 2.7878 | 47.8592 | 115.4251 | 2.9114 | 123.9212 | 123.7701 | 123.912 | 123.6786 | 123.9441 | -124.0219 | -123.8983 | 115.3336 | 123.9532 | 78.8315 | 6.3309
557.9375 | 124.0311 | -51.6632 | 72.2305 | -0.70858 | 0.92793 | 0.17386 | 0.074244 | 0.0099164 | 0.75183 | 0.012021 | 0.036633 | 0.01999 | 0.092245 | 0.087826 | -0.00081695 | 0.036892 | 0.012409 | 22.966 | 71.9742 | -51.7273 | 63.5605 | -5.0583 | 71.9284 | -3.3737 | -43.6935 | 72.0932 | -51.7776 | 72.2672 | -47.6395 | -48.6099 | -49.5255 | -0.064087 | -0.25635 | -8.67 | 46.6049 | 48.2895 | 123.5916 | 48.3536 | 123.6557 | -0.11444 | -0.13733 | 0.036621 | 4.0237 | 2.1378 | 3.0533 | 2.2522 | 3.1677 | 46.669 | 115.2878 | 4.1382 | 124.0448 | 123.7015 | 123.8708 | 123.6374 | 123.7564 | -123.9578 | -124.0082 | 115.2237 | 123.9304 | 74.6292 | 7.9697
558.9844 | 124.0173 | -51.6357 | 72.258 | -0.69332 | 0.92152 | 0.16959 | 0.061427 | -0.0039686 | 0.73687 | 0.012021 | -0.03966 | 0.024263 | 0.089041 | 0.10278 | -0.017907 | 0.026211 | 0.01134 | 25.3281 | 71.7316 | -51.9928 | 63.3774 | -3.9688 | 71.727 | -2.5772 | -44.2657 | 71.8552 | -51.9424 | 72.2397 | -47.8226 | -49.2737 | -49.4293 | -0.35706 | -0.52643 | -8.8806 | 47.6669 | 49.0585 | 123.3627 | 49.4156 | 123.7198 | -0.3067 | -0.40283 | -0.018311 | 3.8132 | 2.2064 | 2.3621 | 2.5131 | 2.6688 | 48.024 | 115.3702 | 4.1199 | 124.1821 | 123.7244 | 123.7976 | 123.3673 | 123.4909 | -124.2508 | -124.2004 | 115.0131 | 123.8754 | 76.9638 | 7.37
559.9375 | 123.9578 | -51.1414 | 72.7524 | -0.63229 | 0.92579 | 0.16532 | 0.061427 | 0.013121 | 0.75503 | -0.0039998 | 0.1587 | 0.016786 | 0.10186 | 0.072873 | -0.002953 | 0.034756 | -0.0036126 | 24.7513 | 72.5418 | -51.2146 | 64.238 | -5.278 | 72.5601 | -4.0375 | -41.7938 | 72.6883 | -51.1642 | 72.789 | -46.3348 | -48.2986 | -48.6603 | -0.073243 | -0.21057 | -8.5144 | 45.8633 | 47.1039 | 123.7015 | 47.1771 | 123.7747 | -0.022889 | -0.064087 | 0.036621 | 4.8065 | 2.4811 | 2.8427 | 2.504 | 2.8656 | 45.9366 | 115.4526 | 4.8294 | 123.9532 | 123.7564 | 123.8525 | 123.6832 | 123.8297 | -123.967 | -123.9166 | 115.3793 | 123.9304 | 75.8926 | 9.3475
560.9688 | 124.0723 | -51.828 | 72.0062 | -0.67806 | 0.91191 | 0.15677 | 0.067836 | 0.022734 | 0.73581 | 0.0056132 | 0.097669 | 0.016786 | 0.095449 | 0.091031 | -0.012566 | 0.03796 | 0.0092044 | 23.1216 | 71.8826 | -51.8738 | 63.446 | -4.9713 | 71.8506 | -3.7262 | -44.5862 | 72.0016 | -51.7136 | 72.1024 | -48.1705 | -48.3032 | -49.4431 | -0.045776 | -0.1236 | -8.5602 | 46.8567 | 48.1018 | 123.6786 | 48.1476 | 123.7244 | 0.11444 | -0.004578 | 0.09613 | 3.6575 | 2.3849 | 3.5248 | 2.2705 | 3.4103 | 46.9025 | 115.3198 | 3.5431 | 123.8159 | 123.7564 | 123.7152 | 123.7106 | 123.8297 | -123.88 | -123.7198 | 115.274 | 123.9304 | 74.9496 | 7.2418
561.9375 | 124.0128 | -50.9445 | 72.8897 | -0.66281 | 0.92793 | 0.17707 | 0.057155 | 0.025938 | 0.73474 | 0.01843 | 0.067151 | 0.024263 | 0.091177 | 0.075009 | -0.013634 | 0.0433 | -0.0014766 | 31.1417 | 72.6288 | -51.0864 | 63.327 | -4.8203 | 72.7432 | -5.658 | -47.7402 | 72.7982 | -51.0132 | 73.0774 | -47.4152 | -47.2916 | -48.5962 | -0.14191 | -0.26093 | -9.5627 | 46.1243 | 45.2866 | 123.6877 | 45.4285 | 123.8297 | -0.068665 | -0.091552 | 0.18768 | 3.5294 | 2.3483 | 3.653 | 2.417 | 3.7216 | 46.2662 | 114.4135 | 3.598 | 124.0906 | 123.7152 | 123.8113 | 123.5733 | 123.7427 | -123.9761 | -123.9029 | 114.2715 | 124.0219 | 82.0862 | 3.2043
562.9844 | 123.9624 | -49.8138 | 74.0616 | -0.67806 | 0.92045 | 0.17279 | 0.066768 | 0.015257 | 0.73153 | -0.01575 | -0.03966 | 0.041353 | 0.10079 | 0.0686 | -0.01043 | 0.041164 | 0.017749 | 23.3459 | 73.8281 | -49.8642 | 64.8331 | -5.6625 | 73.8831 | -4.66 | -41.7435 | 73.97 | -49.8688 | 74.0707 | -46.6278 | -46.1838 | -47.5479 | -0.050354 | -0.23346 | -9.2285 | 44.1513 | 45.1538 | 123.6969 | 45.2042 | 123.7473 | -0.054931 | -0.091552 | 0.009156 | 3.186 | 2.2659 | 3.6301 | 2.3209 | 3.685 | 44.2017 | 114.6973 | 3.241 | 123.9395 | 123.6923 | 123.8388 | 123.642 | 123.7839 | -123.9258 | -123.9304 | 114.6469 | 123.8846 | 73.1598 | 8.0704
563.9375 | 123.9807 | -51.2924 | 72.5601 | -0.7391 | 0.95784 | 0.20591 | 0.074244 | 0.010984 | 0.74115 | -0.012545 | -0.024402 | 0.01999 | 0.081564 | 0.096371 | -0.011498 | 0.03796 | 0.015613 | 65.9088 | 72.4136 | -51.2512 | 63.8535 | -5.9875 | 72.3312 | -4.8477 | -44.3848 | 72.4365 | -51.3611 | 72.5601 | -47.4197 | -47.9828 | -48.6557 | 0.041198 | -0.14648 | -8.7067 | 45.3049 | 46.4447 | 123.6237 | 46.4035 | 123.5825 | -0.068665 | -0.1236 | 0 | 3.8727 | 2.6367 | 3.3096 | 2.7054 | 3.3783 | 45.2637 | 115.1047 | 3.9413 | 123.9212 | 123.6649 | 123.7976 | 123.7061 | 123.7289 | -123.8113 | -123.9212 | 115.1459 | 123.8525 | 117.2012 | 6.9077
564.9531 | 124.118 | -67.2409 | 56.5567 | -0.70858 | 0.96745 | 0.22727 | 0.065699 | 0.022734 | 0.72085 | 0.013089 | 0.32655 | 0.038148 | 0.029226 | -0.041416 | -0.006157 | 0.0069851 | 0.0070684 | 52.2491 | 56.1722 | -67.511 | 47.4197 | -19.3817 | 56.1768 | -18.0405 | -0.11444 | 0.12817 | -0.082397 | -0.022888 | -0.050354 | -0.027466 | -0.027466 | -0.27008 | -0.38452 | -9.137 | 47.8592 | 49.2004 | 123.4177 | 49.4705 | 123.6877 | 67.1585 | -56.4285 | -56.5796 | 67.1906 | 67.2134 | 67.2134 | 0.054931 | 0.054931 | 48.1293 | 114.9307 | 0.032043 | 0.059509 | 123.6832 | 0.21057 | 123.4131 | 67.3691 | -124.0677 | -56.6391 | 114.6606 | 67.218 | 119.4901 | 67.1265
565.9375 | 123.967 | -67.1173 | 56.7352 | -0.89169 | 0.96852 | 0.2497 | 0.062495 | 0.0088484 | 0.7294 | 0.0056132 | 0.051892 | 0.030671 | 0.040975 | 0.00024052 | -0.021111 | 0.010189 | 0.0006594 | 51.6174 | 56.4743 | -67.1951 | 47.5479 | -18.0725 | 56.575 | -16.6626 | -0.091553 | 0.091553 | -0.082397 | -0.027466 | -0.064087 | -0.07782 | -0.032043 | -0.077819 | -0.26093 | -9.1873 | 49.0448 | 50.4547 | 123.6923 | 50.5325 | 123.7701 | 67.0349 | -56.6437 | -56.7627 | 67.0532 | 67.0853 | 67.0395 | 0.050354 | 0.004577 | 49.1226 | 114.743 | 0.01831 | 0.054931 | 123.6694 | 0.17395 | 123.5916 | 67.2089 | -123.9304 | -56.8176 | 114.6652 | 67.0898 | 118.7347 | 67.0258
566.9688 | 123.9761 | -64.7049 | 59.1339 | -0.86117 | 0.95891 | 0.22513 | 0.076381 | -0.0039686 | 0.72299 | 0.0045452 | 0.17396 | 0.039216 | 0.018545 | -0.038211 | -0.011498 | 0.016598 | 0.0070684 | 53.1509 | 58.8089 | -64.8422 | 50.1114 | -19.1803 | 58.9417 | -18.2602 | -0.082397 | 0.09613 | -0.07782 | -0.022888 | -0.045776 | -0.064087 | -0.018311 | -0.13733 | -0.32501 | -9.0225 | 45.5246 | 46.4447 | 123.6465 | 46.582 | 123.7839 | 64.6271 | -59.0378 | -59.1568 | 64.6591 | 64.6866 | 64.6408 | 0.059509 | 0.013733 | 45.6619 | 114.9536 | 0.032044 | 0.054932 | 123.6511 | 0.17395 | 123.5138 | 64.801 | -123.9761 | -59.2117 | 114.8163 | 64.682 | 117.8558 | 64.6225
567.9375 | 123.912 | -67.4423 | 56.3965 | -0.84591 | 0.97493 | 0.24756 | 0.060359 | -0.00076463 | 0.71124 | 0.0013402 | 0.0061157 | 0.033876 | 0.032431 | -0.012576 | -0.008294 | 0.0037801 | 0.0049324 | 52.0706 | 56.2088 | -67.511 | 47.3145 | -20.7413 | 56.25 | -19.6198 | -0.14191 | 0.10071 | -0.082397 | -0.018311 | -0.082397 | -0.073242 | -0.009155 | -0.068664 | -0.18768 | -9.082 | 46.7011 | 47.8226 | 123.6923 | 47.8912 | 123.761 | 67.3599 | -56.2958 | -56.4148 | 67.3599 | 67.4332 | 67.3691 | 0.073242 | 0.009155 | 46.7697 | 114.8254 | 0 | 0.064086 | 123.7198 | 0.18311 | 123.6511 | 67.543 | -123.9075 | -56.4789 | 114.7568 | 67.424 | 119.5129 | 67.3004
568.9844 | 123.9578 | -66.5039 | 57.3212 | -0.78488 | 1.0016 | 0.26892 | 0.057155 | 0.0056444 | 0.73474 | 0.0034762 | 0.051892 | 0.052034 | 0.058065 | -0.017917 | -0.01577 | 0.017666 | 0.01134 | 52.272 | 57.2479 | -66.449 | 47.9599 | -20.2606 | 57.2388 | -18.9972 | -0.1236 | 0.07782 | -0.059509 | -0.036621 | -0.068665 | -0.086975 | -0.036621 | 0.054931 | -0.073242 | -9.3613 | 46.2433 | 47.5067 | 123.7427 | 47.4518 | 123.6877 | 66.4444 | -57.2433 | -57.3578 | 66.4352 | 66.4673 | 66.4169 | 0.022888 | -0.027466 | 46.1884 | 114.4089 | -0.009156 | 0.022888 | 123.6969 | 0.13733 | 123.7518 | 66.5817 | -123.7701 | -57.3807 | 114.4638 | 66.4673 | 118.7759 | 66.3803
569.9375 | 123.9624 | -65.918 | 57.9437 | -0.67806 | 0.97279 | 0.24543 | 0.061427 | -0.0039686 | 0.72085 | 0.013089 | 0.021375 | 0.050966 | 0.020681 | -0.0029635 | -0.007226 | 0.018734 | 0.012409 | 53.8284 | 57.7744 | -65.9225 | 48.6008 | -20.5444 | 57.843 | -19.5831 | -0.12817 | 0.091553 | -0.073242 | -0.045776 | -0.073242 | -0.086975 | -0.022888 | -0.004577 | -0.16937 | -9.343 | 45.3735 | 46.3348 | 123.761 | 46.3394 | 123.7656 | 65.8447 | -57.8522 | -57.9895 | 65.8447 | 65.8951 | 65.831 | 0.050354 | -0.013733 | 45.3781 | 114.5233 | 0 | 0.027466 | 123.6969 | 0.16479 | 123.6923 | 66.0095 | -123.8663 | -58.017 | 114.5187 | 65.8722 | 119.7464 | 65.7898
570.9688 | 124.2462 | -63.8626 | 59.9121 | -0.90695 | 1.0219 | 0.35117 | 0.062495 | 0.018461 | 0.71338 | 0.0098852 | 0.17396 | 0.041353 | 0.038839 | -0.04996 | -0.016839 | 0.02087 | 0.015613 | 54.2542 | 59.6878 | -63.8947 | 50.2029 | -20.929 | 59.5322 | -19.8715 | 0.064087 | 0.045776 | -0.032043 | 0.10071 | 0.091553 | 0.086975 | 0.11444 | -0.032043 | -0.2243 | -9.7092 | 42.9337 | 43.9911 | 123.3948 | 44.0231 | 123.4268 | 63.8306 | -59.8663 | -59.8114 | 63.9542 | 63.9771 | 63.9496 | 0.14648 | 0.11902 | 42.9657 | 114.0976 | 0.1236 | 0.13275 | 123.5825 | 0.077819 | 123.5504 | 63.9084 | -123.8068 | -59.9442 | 114.0656 | 63.9633 | 118.1168 | 63.9267
571.9375 | 123.8709 | -70.4544 | 53.2288 | -1.0748 | 1.1116 | 0.35117 | 0.050746 | 0.017393 | 0.73794 | 0.012021 | 0.40284 | 0.032808 | 0.028158 | -0.017917 | -0.017907 | 0.00057606 | -0.0004086 | 51.0544 | 53.0548 | -70.4269 | 51.3474 | -20.5902 | 53.0182 | -19.5831 | 0.004578 | 0.064087 | -0.036621 | 0.018311 | 0.054932 | 0.041199 | 0.054932 | 0.027466 | -0.17395 | -1.8814 | 49.8642 | 50.8713 | 123.4726 | 50.8438 | 123.4451 | 70.4178 | -53.1647 | -53.2104 | 70.5093 | 70.5093 | 70.4956 | 0.091553 | 0.07782 | 49.8367 | 121.7743 | 0.091553 | 0.054932 | 123.4818 | 0.10071 | 123.5092 | 70.5185 | -123.6557 | -53.2654 | 121.8018 | 70.4727 | 121.5088 | 70.459
572.9531 | 123.9853 | -61.7844 | 62.0544 | 0.2985 | 0.013624 | 0.0050995 | 0.046473 | 0.018461 | -0.0054662 | 0.015226 | 0.34181 | 0.039216 | 0.022818 | -0.013645 | -0.007226 | 0.014461 | 0.017749 | 0.041199 | 0.045776 | -0.045776 | 0.082397 | 0.09613 | 0.059509 | 0.064087 | -0.064087 | 0.10986 | -0.059509 | -0.032043 | -0.013733 | -0.009155 | -0.004578 | 61.7386 | -62.0087 | -61.972 | 61.8805 | 61.8484 | 61.8439 | 0.10986 | 0.10528 | 61.7249 | -61.9446 | -62.0865 | 61.7706 | 61.7798 | 61.7752 | 0.054931 | 0.050354 | 0.14191 | 0.12817 | 0.045776 | 0.027466 | 0.091552 | 0.16937 | 61.8301 | 61.8942 | -62.1002 | -62.114 | 61.8668 | 61.7523 | 61.8256 | 61.7203
573.9375 | 123.9944 | -61.853 | 62.0407 | 0.26798 | 0.0050788 | 0.01685 | 0.042201 | 0.017393 | 0.024441 | 0.0024082 | 0.051892 | 0.034944 | 0.021749 | -0.0051005 | -0.017907 | 0.024074 | 0.0006594 | 0.009155 | 0.027466 | -0.050354 | 0.068665 | 0.09613 | 0.059509 | 0.045776 | -0.086975 | 0.082397 | -0.054932 | -0.032043 | -0.054932 | -0.054932 | -0.009155 | 61.8027 | -62.0132 | -61.972 | 61.9492 | 61.8988 | 61.9125 | 0.09613 | 0.10986 | 61.7981 | -61.9583 | -62.0728 | 61.7981 | 61.8439 | 61.7981 | 0.045777 | 0 | 0.14648 | 0.11902 | 0 | 0.022889 | 0.07782 | 0.13733 | 61.8805 | 61.9354 | -62.0911 | -62.0956 | 61.9217 | 61.821 | 61.8622 | 61.7661
574.9531 | 124.0128 | -61.8439 | 62.0728 | 0.2222 | 0.00080677 | 0.0093725 | 0.03686 | -0.017855 | 0.0041468 | -0.01575 | 0.25026 | 0.047761 | 0.035635 | -0.039279 | -0.005089 | 0.0091211 | -0.0025446 | 0.009155 | 0.022888 | -0.018311 | 0.082397 | 0.11444 | 0.054932 | 0.068665 | -0.059509 | 0.10071 | -0.054932 | -0.041199 | 0.009155 | 0.009155 | -0.009155 | 61.8256 | -62.0499 | -61.9904 | 61.9583 | 61.9125 | 61.8988 | 0.086976 | 0.073243 | 61.7889 | -61.972 | -62.114 | 61.853 | 61.8347 | 61.853 | 0.045777 | 0.064087 | 0.13275 | 0.10071 | 0.064087 | 0.013733 | 0.041199 | 0.15564 | 61.8668 | 61.9446 | -62.0911 | -62.1277 | 61.9263 | 61.8027 | 61.853 | 61.7844
575.9375 | 124.0219 | -61.8576 | 62.0407 | 0.13065 | 0.018965 | 0.01685 | 0.038997 | 0.0013714 | 0.0084198 | 0.0034762 | -0.024402 | 0.046693 | 0.031362 | -0.022189 | -0.004021 | 0.030483 | 0.010272 | 0 | 0.009155 | -0.032043 | 0.059509 | 0.09613 | 0.045776 | 0.045776 | -0.064087 | 0.091553 | -0.064087 | -0.032043 | -0.050354 | -0.059509 | -0.032043 | 61.8256 | -62.0316 | -61.9812 | 61.9537 | 61.9034 | 61.9034 | 0.077819 | 0.077819 | 61.7935 | -61.9492 | -62.0728 | 61.8073 | 61.8256 | 61.7981 | 0.032044 | 0.004578 | 0.12817 | 0.091552 | 0.013733 | 0.032044 | 0.041198 | 0.15564 | 61.8668 | 61.9492 | -62.0728 | -62.1048 | 61.9171 | 61.8256 | 61.8576 | 61.7935
576.9844 | 124.0311 | -61.8622 | 62.0361 | 0.16117 | 0.01576 | 0.010441 | 0.041133 | -0.010378 | 0.015896 | 0.0088172 | -0.085437 | 0.041353 | 0.039907 | 0.019467 | -0.013634 | 0.014461 | 0.0049324 | -0.018311 | 0.013733 | -0.059509 | 0.10071 | 0.15564 | 0.07782 | 0.082397 | -0.11902 | 0.082397 | -0.068665 | -0.009155 | -0.054932 | -0.064087 | -0.004578 | 61.8027 | -62.0224 | -61.9354 | 62.0178 | 61.9446 | 61.94 | 0.14191 | 0.13733 | 61.7935 | -61.9537 | -62.0453 | 61.8073 | 61.8576 | 61.7981 | 0.064087 | 0.004578 | 0.21515 | 0.16022 | 0.013733 | 0.05951 | 0.073242 | 0.15106 | 61.8759 | 61.9446 | -62.0956 | -62.1048 | 61.9629 | 61.853 | 61.8439 | 61.7432
577.9375 | 124.0402 | -61.8805 | 62.0544 | 0.17643 | -0.0066702 | 0.0050995 | 0.047541 | 0.012053 | -0.014011 | 0.0066812 | -0.0091433 | 0.046693 | 0.024954 | -0.020053 | -0.005089 | 0.025143 | -0.017499 | 0 | 0.054932 | -0.009155 | 0.059509 | 0.091553 | 0.027466 | 0.050354 | -0.032043 | 0.10529 | -0.041199 | -0.018311 | -0.013733 | -0.018311 | -0.018311 | 61.8713 | -61.9995 | -61.9949 | 61.972 | 61.9308 | 61.908 | 0.059509 | 0.036621 | 61.8393 | -61.9492 | -62.0728 | 61.8668 | 61.8622 | 61.8622 | 0.022888 | 0.022888 | 0.10071 | 0.068664 | 0.027466 | 0.022888 | 0.064087 | 0.14649 | 61.9354 | 61.9858 | -62.0636 | -62.0956 | 61.94 | 61.8622 | 61.8805 | 61.8484
578.9688 | 124.0631 | -61.8759 | 62.059 | 0.28324 | -0.0098752 | 0.0050995 | 0.03686 | 0.014189 | 0.0094878 | -0.0029318 | 0.097669 | 0.041353 | 0.026022 | -0.040347 | -0.012566 | 0.017666 | -0.0014766 | -0.059509 | 0.032043 | -0.036621 | 0.10986 | 0.15106 | 0.064087 | 0.073242 | -0.064087 | 0.10986 | -0.050354 | -0.022888 | -0.009155 | -0.004578 | -0.004578 | 61.8393 | -62.027 | -61.9492 | 62.027 | 61.9492 | 61.94 | 0.10986 | 0.10071 | 61.8256 | -61.9492 | -62.0819 | 61.8668 | 61.8713 | 61.8713 | 0.045776 | 0.045776 | 0.18768 | 0.14648 | 0.041199 | 0.027466 | 0.068664 | 0.16022 | 61.908 | 61.9858 | -62.0956 | -62.1094 | 61.9858 | 61.853 | 61.8164 | 61.8118
579.9375 | 124.0082 | -61.8713 | 62.0499 | 0.16117 | 0.011488 | 0.011509 | 0.042201 | -0.0029006 | 0.0084198 | 0.0066812 | 0.08241 | 0.043489 | 0.018545 | -0.036075 | -0.020043 | 0.02087 | -0.0068176 | -0.036621 | 0.013733 | -0.045776 | 0.064087 | 0.11444 | 0.054932 | 0.054932 | -0.10529 | 0.07782 | -0.054932 | -0.050354 | -0.073242 | -0.050354 | 0.004578 | 61.8256 | -62.0361 | -61.9858 | 61.9858 | 61.9263 | 61.9263 | 0.10071 | 0.10071 | 61.8164 | -61.972 | -62.1002 | 61.7981 | 61.8759 | 61.821 | 0.05951 | 0.004578 | 0.16022 | 0.10986 | -0.01831 | 0.004578 | 0.059509 | 0.13275 | 61.8851 | 61.9492 | -62.0956 | -62.1048 | 61.9354 | 61.821 | 61.8347 | 61.7661
580.9688 | 124.0173 | -61.8668 | 62.0544 | 0.28324 | 0.01042 | 0.0061675 | 0.050746 | 0.017393 | 0.0030788 | -0.0050688 | -0.0091433 | 0.044557 | 0.023886 | 0.0023765 | -0.008294 | 0.02087 | 0.015613 | -0.022888 | -0.004578 | -0.032043 | 0.064087 | 0.10529 | 0.041199 | 0.068665 | -0.073242 | 0.086975 | -0.050354 | -0.036621 | -0.045776 | -0.050354 | -0.018311 | 61.8347 | -62.059 | -61.9904 | 61.972 | 61.9354 | 61.908 | 0.10071 | 0.073242 | 61.8164 | -61.9675 | -62.0911 | 61.821 | 61.8484 | 61.8164 | 0.032043 | 0 | 0.13733 | 0.09613 | 0.004578 | 0.013733 | 0.027465 | 0.13733 | 61.8622 | 61.9537 | -62.0865 | -62.1048 | 61.9308 | 61.8301 | 61.8439 | 61.7935
581.9375 | 124.1867 | -61.8484 | 62.0132 | 0.17643 | 0.016828 | -0.0013085 | 0.03152 | 0.020598 | -0.0097382 | -0.0072048 | 0.43336 | 0.038148 | 0.032431 | -0.037143 | -0.009362 | 0.012325 | -0.0036126 | 0 | 0.004578 | -0.013733 | -0.009155 | 0.041199 | -0.009155 | -0.018311 | -0.018311 | 0.07782 | -0.032043 | 0.041199 | 0.068665 | 0.064087 | 0.050354 | 61.8347 | -62.0087 | -62.0224 | 61.8896 | 61.8301 | 61.8393 | -0.004578 | 0.004578 | 61.8164 | -61.9354 | -61.972 | 61.9171 | 61.8988 | 61.9125 | 0.082397 | 0.09613 | 0.054932 | 0.004578 | 0.10071 | 0.073242 | 0.018311 | 0.10986 | 61.853 | 61.9263 | -62.027 | -62.0453 | 61.8393 | 61.8896 | 61.8484 | 61.8301
582.9688 | 124.054 | -61.8851 | 62.0544 | 0.16117 | -0.0013302 | 0.0072355 | 0.044337 | 0.017393 | -0.0097382 | 0.0045452 | 0.0061157 | 0.045625 | 0.032431 | 0.0066495 | -0.012566 | 0.021938 | -0.015362 | -0.027466 | 0.004578 | -0.041199 | 0.082397 | 0.13275 | 0.064087 | 0.064087 | -0.16479 | 0.091553 | -0.032043 | -0.013733 | 0 | -0.050354 | -0.004578 | 61.8439 | -62.0499 | -61.972 | 62.0178 | 61.9492 | 61.9492 | 0.10529 | 0.10529 | 61.853 | -61.9629 | -62.0682 | 61.8851 | 61.8805 | 61.8347 | 0.027465 | -0.018311 | 0.17395 | 0.1236 | 0.032043 | 0.01831 | 0.045777 | 0.1236 | 61.8896 | 61.9766 | -62.0956 | -62.0865 | 61.9675 | 61.8713 | 61.8576 | 61.7203
583.9375 | 124.0677 | -61.8713 | 62.0865 | 0.25272 | 0.024305 | 0.018986 | 0.025111 | 0.010984 | -0.00012524 | -0.0072048 | -0.0091433 | 0.040285 | 0.028158 | -0.02753 | -0.01577 | 0.031551 | -0.013226 | 0.022888 | 0.054932 | 0.018311 | 0.045776 | 0.086975 | 0.027466 | 0.045776 | -0.022888 | 0.091553 | -0.041199 | -0.004578 | -0.009155 | -0.027466 | -0.009155 | 61.8896 | -62.0316 | -62.0407 | 61.9583 | 61.9171 | 61.8988 | 0.027465 | 0.009155 | 61.8301 | -61.9949 | -62.0911 | 61.8622 | 61.8622 | 61.8439 | 0.032044 | 0.013733 | 0.068664 | 0.027465 | 0.032044 | 0.036621 | 0.036621 | 0.13275 | 61.9263 | 61.9629 | -62.0682 | -62.1277 | 61.9171 | 61.8668 | 61.8942 | 61.8484
584.9844 | 124.0723 | -61.8942 | 62.0682 | 0.19169 | 0.0050788 | 0.0072355 | 0.028315 | 0.015257 | 0.00094276 | -0.0072048 | 0.21974 | 0.039216 | 0.043112 | -0.046756 | -0.002953 | 0.011257 | 0.01134 | -0.018311 | 0.041199 | -0.018311 | 0.10071 | 0.11444 | 0.073242 | 0.082397 | -0.054932 | 0.091553 | -0.054932 | -0.036621 | 0.004578 | 0 | 0 | 61.8759 | -62.027 | -61.9675 | 62.0087 | 61.9766 | 61.9675 | 0.10071 | 0.091553 | 61.8393 | -61.9766 | -62.1048 | 61.8988 | 61.8942 | 61.8942 | 0.054932 | 0.054932 | 0.13275 | 0.11902 | 0.05951 | 0.018311 | 0.05951 | 0.14649 | 61.9354 | 61.9858 | -62.0865 | -62.1231 | 61.9949 | 61.8576 | 61.8759 | 61.8393
585.9375 | 124.086 | -61.8805 | 62.059 | 0.16117 | 0.0029428 | 0.0072355 | 0.029384 | 0.010984 | 0.00094276 | -0.0039998 | 0.1587 | 0.041353 | 0.029226 | -0.040347 | -0.013634 | 0.021938 | 0.0049324 | 0.018311 | 0.013733 | -0.032043 | 0.086975 | 0.30212 | 0.15106 | 0.11444 | 0 | 0.15106 | 0.027466 | 0.009155 | 0.022888 | 0.004578 | 0.018311 | 61.8484 | -62.0453 | -61.972 | 62.1826 | 61.9949 | 62.0316 | 0.14648 | 0.18311 | 61.908 | -61.908 | -62.0499 | 61.9034 | 61.8988 | 61.8851 | -0.009155 | -0.022888 | 0.33417 | 0.11902 | -0.004578 | -0.018311 | 0.045776 | 0.1236 | 61.8942 | 62.0316 | -62.0911 | -62.0316 | 61.9675 | 61.8896 | 61.8988 | 61.8805
586.9844 | 124.086 | -61.8896 | 62.0407 | 0.23746 | 0.014692 | 0.021122 | 0.028315 | 0.015257 | 0.015896 | -0.0093408 | 0.036633 | 0.049898 | 0.035635 | 0.0023765 | -0.007226 | 0.025143 | -0.014294 | -0.018311 | 0.009155 | -0.045776 | 0.1831 | 0.068665 | -0.064087 | 0.13275 | -0.07782 | 0.11444 | -0.032043 | -0.013733 | -0.027466 | -0.013733 | 0.009155 | 61.8439 | -62.0316 | -61.8576 | 61.9583 | 62.0224 | 61.8256 | 0.17853 | -0.018311 | 61.8576 | -61.9263 | -62.0544 | 61.8622 | 61.8988 | 61.8759 | 0.041198 | 0.01831 | 0.11444 | 0.22888 | 0.004577 | 0.01831 | 0.054931 | 0.14648 | 61.8988 | 62.0041 | -62.0865 | -62.0728 | 62.0728 | 61.8759 | 61.8713 | 61.8118
587.9375 | 124.0768 | -61.8942 | 62.0773 | 0.19169 | -0.00026223 | 0.01685 | 0.040065 | 0.030211 | 0.014828 | -0.011477 | 0.235 | 0.047761 | 0.029226 | 0.00024052 | -0.01043 | 0.025143 | 0.0006594 | 0 | 0.045776 | -0.009155 | 0.054932 | 0.082397 | 0.022888 | 0.041199 | -0.041199 | 0.068665 | -0.036621 | -0.018311 | 0 | -0.013733 | 0.004578 | 61.8851 | -62.0316 | -62.0224 | 61.9766 | 61.9354 | 61.9171 | 0.050354 | 0.032043 | 61.8576 | -62.0087 | -62.0956 | 61.8942 | 61.8988 | 61.8805 | 0.041199 | 0.022888 | 0.091552 | 0.064087 | 0.036621 | 0.01831 | 0.054931 | 0.10529 | 61.94 | 61.9629 | -62.0865 | -62.114 | 61.9492 | 61.8759 | 61.8942 | 61.853
588.9531 | 124.1043 | -61.8759 | 62.0728 | 0.19169 | 0.01576 | -0.0013085 | 0.022975 | 0.0056444 | -0.0065342 | 0.00027221 | 0.35707 | 0.045625 | 0.039907 | -0.046756 | -0.004021 | 0.0059161 | -0.014294 | 0.032043 | -0.013733 | -0.022888 | 0.004578 | 0.032043 | -0.009155 | 0.013733 | 0.013733 | 0.091553 | -0.032043 | 0 | 0.054932 | 0.041199 | 0.041199 | 61.853 | -62.0865 | -62.0682 | 61.908 | 61.8896 | 61.8668 | 0.036621 | 0.013733 | 61.8439 | -61.9812 | -62.0728 | 61.9308 | 61.9171 | 61.9171 | 0.073242 | 0.073242 | 0.054931 | 0.027466 | 0.086975 | 0.032043 | 0.009155 | 0.1236 | 61.8622 | 61.9675 | -62.0956 | -62.1048 | 61.8805 | 61.8759 | 61.908 | 61.8896
589.9375 | 124.1089 | -61.8576 | 62.0865 | 0.10013 | 0.0082828 | 0.0061675 | 0.041133 | 0.0024404 | 0.0030788 | -0.0039998 | 0.08241 | 0.046693 | 0.030294 | -0.0093725 | -0.014702 | 0.025143 | 0.0017274 | 0.032043 | 0.009155 | -0.050354 | 0.036621 | 0.073242 | 0 | 0.041199 | 0.004578 | 0.10529 | -0.032043 | 0.036621 | 0.054932 | 0.054932 | 0.045776 | 61.8073 | -62.0773 | -62.0499 | 61.9308 | 61.8988 | 61.8576 | 0.091553 | 0.050354 | 61.8256 | -61.9812 | -62.0499 | 61.9125 | 61.9034 | 61.9125 | 0.077819 | 0.086975 | 0.1236 | 0.086975 | 0.086975 | 0.068664 | 0.059509 | 0.13733 | 61.8668 | 61.9629 | -62.1368 | -62.1185 | 61.8942 | 61.8942 | 61.8896 | 61.8622
590.9844 | 124.1272 | -61.8622 | 62.0728 | 0.25272 | 0.0040108 | 0.010441 | 0.038997 | 0.0024404 | -0.0022622 | 0.0066812 | 0.1587 | 0.043489 | 0.035635 | -0.02753 | -0.016839 | 0.011257 | -0.0004086 | -0.013733 | 0.009155 | -0.041199 | 0.082397 | 0.13275 | 0.045776 | 0.086975 | -0.059509 | 0.10529 | -0.054932 | -0.018311 | 0.027466 | 0.018311 | 0.041199 | 61.821 | -62.0636 | -61.9904 | 61.9949 | 61.9492 | 61.908 | 0.12817 | 0.086975 | 61.8073 | -61.9675 | -62.0911 | 61.8896 | 61.9034 | 61.8805 | 0.096131 | 0.073243 | 0.17395 | 0.1236 | 0.082398 | 0.036621 | 0.050354 | 0.16022 | 61.8713 | 61.9675 | -62.114 | -62.1277 | 61.9446 | 61.8439 | 61.8484 | 61.8027
591.9375 | 124.1364 | -61.8668 | 62.0361 | 0.054357 | 0.0072148 | 0.0061675 | 0.030452 | 0.02487 | -0.017215 | -0.014682 | 0.37233 | 0.048829 | 0.038839 | -0.058505 | -0.005089 | 0.014461 | -0.0046806 | 0.027466 | -0.018311 | 0 | -0.022888 | 0.018311 | -0.013733 | -0.018311 | 0.027466 | 0.064087 | -0.018311 | 0.041199 | 0.059509 | 0.064087 | 0.064087 | 61.8668 | -62.0544 | -62.059 | 61.8851 | 61.8484 | 61.853 | -0.018311 | -0.013733 | 61.8484 | -61.972 | -61.9949 | 61.9263 | 61.9308 | 61.9308 | 0.082398 | 0.082398 | 0.018311 | -0.022888 | 0.07782 | 0.05951 | -0.018311 | 0.082398 | 61.8484 | 61.9308 | -62.0361 | -62.0544 | 61.8439 | 61.908 | 61.8942 | 61.8942
592.9688 | 124.1638 | -61.8484 | 62.1002 | 0.20695 | 0.0072148 | 0.0029635 | 0.035792 | -0.016787 | 0.0041468 | -0.0018638 | 0.37233 | 0.025331 | 0.037771 | -0.022189 | -0.020043 | 0.0080531 | -0.0036126 | 0.041199 | -0.036621 | -0.004578 | -0.064087 | -0.036621 | -0.073242 | -0.032043 | 0.09613 | 0.064087 | 0 | 0.086975 | 0.13733 | 0.13733 | 0.11902 | 61.8439 | -62.1368 | -62.1643 | 61.8118 | 61.8164 | 61.7752 | -0.027465 | -0.068664 | 61.8484 | -62.0361 | -62.0132 | 61.9858 | 61.9675 | 61.9858 | 0.11902 | 0.13733 | -0.032043 | -0.059509 | 0.13733 | 0.086975 | -0.032043 | 0.064087 | 61.8118 | 61.9125 | -62.1048 | -62.1002 | 61.7844 | 61.9354 | 61.8896 | 61.9446
593.9375 | 124.0952 | -61.8622 | 62.0682 | 0.28324 | 0.0072148 | 0.010441 | 0.037928 | -0.012514 | 0.0062828 | -0.01575 | -0.03966 | 0.047761 | 0.037771 | -0.0018955 | -0.020043 | 0.023006 | -0.0025446 | 0.032043 | 0.045776 | 0.009155 | 0.032043 | 0.07782 | 0.013733 | 0.050354 | -0.027466 | 0.082397 | -0.045776 | -0.027466 | -0.009155 | -0.009155 | 0.018311 | 61.8713 | -62.0224 | -62.0361 | 61.94 | 61.9125 | 61.8759 | 0.041199 | 0.004578 | 61.8164 | -61.9858 | -62.0956 | 61.853 | 61.8805 | 61.853 | 0.064087 | 0.036621 | 0.068665 | 0.022888 | 0.036621 | 0.01831 | 0.036621 | 0.12817 | 61.908 | 61.9446 | -62.059 | -62.114 | 61.8942 | 61.8347 | 61.8942 | 61.8347
594.9375 | 124.054 | -61.8851 | 62.0636 | 0.23746 | 0.01576 | 0.01685 | 0.041133 | 0.0035084 | -0.0086702 | -0.0050688 | 0.051892 | 0.048829 | 0.029226 | 0.0098535 | -0.013634 | 0.0091211 | 0.0027964 | -0.036621 | 0 | -0.073242 | 0.082397 | 0.1236 | 0.027466 | 0.068665 | -0.091553 | 0.10071 | -0.054932 | -0.032043 | -0.073242 | -0.050354 | -0.013733 | 61.8118 | -62.0636 | -61.9812 | 62.0087 | 61.9537 | 61.9125 | 0.14191 | 0.10071 | 61.8301 | -61.9629 | -62.0956 | 61.8118 | 61.8713 | 61.8347 | 0.041199 | 0.004578 | 0.19684 | 0.15564 | -0.01831 | 0.022889 | 0.073242 | 0.15564 | 61.8851 | 61.9858 | -62.1368 | -62.1185 | 61.9675 | 61.853 | 61.8485 | 61.7935
595.9375 | 124.1135 | -61.8988 | 62.0453 | -0.037196 | 0.00080677 | -0.0023775 | 0.037928 | 0.014189 | -0.0033302 | -0.01575 | 0.1587 | 0.047761 | 0.033499 | 0.0045125 | -0.00081695 | 0.0069851 | 0.029498 | 0.013733 | 0.022888 | -0.027466 | 0.07782 | 0.10071 | 0.054932 | 0.045776 | -0.045776 | 0.068665 | -0.068665 | 0.013733 | 0.018311 | -0.004578 | 0.022888 | 61.8713 | -62.0224 | -61.9675 | 61.9995 | 61.9446 | 61.9537 | 0.073242 | 0.082398 | 61.8301 | -61.9766 | -62.0316 | 61.9171 | 61.9217 | 61.8942 | 0.091553 | 0.064087 | 0.12817 | 0.10529 | 0.086976 | 0.082398 | 0.050354 | 0.13733 | 61.9217 | 61.9675 | -62.0728 | -62.114 | 61.9766 | 61.9125 | 61.9125 | 61.853
596.9844 | 124.1089 | -61.8759 | 62.0544 | 0.13065 | 0.0061468 | 0.01685 | 0.040065 | 0.010984 | -0.024692 | 0.0066812 | 0.08241 | 0.050966 | 0.034567 | -0.00082748 | -0.014702 | 0.02087 | -0.0014766 | -0.073242 | 0.032043 | -0.022888 | 0.064087 | 0.09613 | 0.059509 | 0.032043 | -0.036621 | 0.086975 | -0.036621 | 0.009155 | 0 | 0 | 0.032043 | 61.853 | -62.0224 | -61.9904 | 61.972 | 61.908 | 61.9354 | 0.054931 | 0.082397 | 61.8393 | -61.9675 | -62.0453 | 61.8759 | 61.908 | 61.8759 | 0.068664 | 0.036621 | 0.11902 | 0.086975 | 0.036621 | 0.045776 | 0.054931 | 0.1236 | 61.908 | 61.9629 | -62.0773 | -62.0911 | 61.94 | 61.8851 | 61.8027 | 61.8393
598.0469 | 124.1272 | -61.8622 | 62.0911 | 0.32902 | 0.0050788 | 0.014713 | 0.032588 | -0.0071726 | -0.019351 | -0.0082728 | 0.097669 | 0.048829 | 0.030294 | -0.043552 | -0.01577 | 0.019802 | -0.024975 | -0.018311 | 0.013733 | -0.041199 | 0.054932 | 0.086975 | 0.022888 | 0.041199 | -0.022888 | 0.064087 | -0.045776 | 0.036621 | 0.045776 | 0.032043 | 0.054932 | 61.821 | -62.0773 | -62.0361 | 61.9492 | 61.9034 | 61.8851 | 0.082398 | 0.064087 | 61.8164 | -62.027 | -62.0544 | 61.908 | 61.9171 | 61.8942 | 0.10071 | 0.077819 | 0.12817 | 0.096131 | 0.091552 | 0.082397 | 0.054932 | 0.10986 | 61.8759 | 61.9263 | -62.1323 | -62.1368 | 61.9171 | 61.8988 | 61.8439 | 61.8393
598.9531 | 124.0814 | -61.8896 | 62.0911 | 0.20695 | -0.00026223 | -0.00024048 | 0.028315 | 0.021666 | 0.010556 | 0.0045452 | 0.32655 | 0.039216 | 0.037771 | -0.016849 | -0.009362 | -0.00049194 | 0.010272 | -0.004578 | 0.018311 | -0.013733 | 0.064087 | 0.14191 | 0.050354 | 0.068665 | -0.050354 | 0.10529 | -0.045776 | -0.027466 | 0.013733 | 0.004578 | 0.013733 | 61.8759 | -62.0728 | -62.027 | 62.0316 | 61.9583 | 61.94 | 0.082398 | 0.064087 | 61.8439 | -61.9858 | -62.1185 | 61.9034 | 61.9034 | 61.8942 | 0.059509 | 0.050354 | 0.15564 | 0.07782 | 0.059509 | 0.01831 | 0.032044 | 0.15106 | 61.908 | 61.9949 | -62.1048 | -62.1368 | 61.9537 | 61.8622 | 61.8851 | 61.8393
599.9375 | 124.0768 | -61.8896 | 62.0956 | 0.13065 | 0.012556 | 0.013645 | 0.032588 | 0.0035084 | 0.011624 | 0.00027221 | 0.051892 | 0.048829 | 0.022818 | 0.01199 | -0.011498 | 0.023006 | -0.020703 | -0.013733 | -0.009155 | -0.07782 | 0.07782 | 0.091553 | 0.045776 | 0.054932 | -0.068665 | 0.082397 | -0.050354 | -0.027466 | -0.032043 | -0.059509 | -0.009155 | 61.8118 | -62.1048 | -62.0178 | 61.9812 | 61.9446 | 61.9354 | 0.13275 | 0.1236 | 61.8393 | -62.0132 | -62.1231 | 61.8576 | 61.8805 | 61.8301 | 0.041199 | -0.009155 | 0.16937 | 0.15564 | 0.018311 | 0.022888 | 0.068665 | 0.13275 | 61.8805 | 61.972 | -62.1735 | -62.146 | 61.9675 | 61.8622 | 61.8759 | 61.821
600.9844 | 124.0814 | -61.8805 | 62.0682 | 0.31376 | 0.0018748 | 0.013645 | 0.021907 | 0.014189 | 0.00094276 | -0.010409 | 0.31129 | 0.039216 | 0.043112 | -0.041416 | -0.005089 | 0.011257 | 0.0017274 | 0.022888 | 0 | -0.027466 | 0.050354 | 0.091553 | 0.032043 | 0.082397 | -0.045776 | 0.086975 | -0.041199 | -0.036621 | 0.009155 | 0.013733 | -0.009155 | 61.853 | -62.0682 | -62.0178 | 61.972 | 61.9629 | 61.9125 | 0.10986 | 0.059509 | 61.8393 | -61.9812 | -62.1048 | 61.8896 | 61.8713 | 61.8942 | 0.032044 | 0.054932 | 0.11902 | 0.07782 | 0.050354 | 0.004578 | 0.027466 | 0.12817 | 61.8805 | 61.9675 | -62.0956 | -62.1094 | 61.9308 | 61.8439 | 61.9034 | 61.8347
601.9375 | 124.0723 | -61.8942 | 62.0865 | 0.069615 | 0.011488 | 0.010441 | 0.044337 | -0.0029006 | -0.0097382 | 0.0045452 | -0.0091433 | 0.041353 | 0.033499 | -0.0072365 | -0.008294 | 0.021938 | -0.0025446 | -0.009155 | -0.009155 | -0.032043 | 0.059509 | 0.091553 | 0.032043 | 0.059509 | -0.064087 | 0.07782 | -0.045776 | -0.022888 | -0.022888 | -0.036621 | -0.004578 | 61.8622 | -62.0956 | -62.027 | 61.9858 | 61.9537 | 61.9263 | 0.091552 | 0.064086 | 61.8485 | -62.0087 | -62.1094 | 61.8713 | 61.8896 | 61.8576 | 0.041198 | 0.009155 | 0.1236 | 0.091552 | 0.022888 | 0.022888 | 0.022888 | 0.1236 | 61.8851 | 61.972 | -62.1185 | -62.1323 | 61.9537 | 61.8713 | 61.8851 | 61.8301
602.9688 | 124.118 | -61.8759 | 62.0911 | 0.17643 | -0.00026223 | 0.0050995 | 0.034724 | 0.010984 | 0.0030788 | 0.0034762 | 0.067151 | 0.039216 | 0.018545 | -0.0051005 | -0.007226 | 0.018734 | -0.012158 | 0.004578 | -0.013733 | -0.036621 | 0.027466 | 0.064087 | 0.018311 | 0.041199 | 0.009155 | 0.091553 | -0.032043 | 0.027466 | 0.054932 | 0.041199 | 0.045776 | 61.8393 | -62.1048 | -62.0636 | 61.94 | 61.9171 | 61.8942 | 0.07782 | 0.054932 | 61.8439 | -61.9995 | -62.0636 | 61.9308 | 61.9217 | 61.9171 | 0.077819 | 0.073242 | 0.10071 | 0.064087 | 0.086975 | 0.059509 | 0.022888 | 0.1236 | 61.8622 | 61.9675 | -62.1277 | -62.1231 | 61.9034 | 61.9034 | 61.8805 | 61.8851
603.9375 | 124.1135 | -61.8988 | 62.059 | 0.23746 | 0.0050788 | 0.0018955 | 0.033656 | 0.018461 | 0.0020108 | 0.012021 | 0.12819 | 0.038148 | 0.031362 | -0.033939 | -0.008294 | 0.0069851 | -0.014294 | 0.013733 | -0.009155 | -0.036621 | 0.032043 | 0.054932 | 0.009155 | 0.041199 | 0.013733 | 0.07782 | -0.041199 | 0.027466 | 0.054932 | 0.022888 | 0.054932 | 61.8622 | -62.0682 | -62.027 | 61.9537 | 61.94 | 61.908 | 0.07782 | 0.045776 | 61.8576 | -61.9812 | -62.0316 | 61.9537 | 61.9537 | 61.9217 | 0.096131 | 0.064087 | 0.091553 | 0.068664 | 0.096131 | 0.068665 | 0.027466 | 0.11902 | 61.8896 | 61.9766 | -62.0956 | -62.1002 | 61.9308 | 61.9263 | 61.9125 | 61.9125
604.9375 | 124.0906 | -61.8805 | 62.0865 | 0.2222 | 0.013624 | 0.014713 | 0.041133 | -0.0039686 | 0.0084198 | 0.0034762 | 0.14344 | 0.056306 | 0.026022 | -0.0051005 | 0.00025105 | 0.025143 | 0.015613 | -0.004578 | 0.018311 | -0.022888 | 0.054932 | 0.07782 | 0.036621 | 0.036621 | -0.041199 | 0.086975 | -0.050354 | -0.032043 | -0.022888 | -0.041199 | -0.004578 | 61.8576 | -62.0682 | -62.0316 | 61.9583 | 61.9171 | 61.9171 | 0.059509 | 0.059509 | 61.8301 | -61.9995 | -62.1185 | 61.8576 | 61.8759 | 61.8393 | 0.045776 | 0.009155 | 0.10071 | 0.07782 | 0.027466 | 0.018311 | 0.041199 | 0.13733 | 61.8988 | 61.9675 | -62.1094 | -62.1368 | 61.9354 | 61.8484 | 61.8759 | 61.8393
605.9688 | 124.1821 | -61.8713 | 62.0636 | 0.11539 | 0.01042 | 0.0040315 | 0.027247 | 0.0056444 | -0.0086702 | 0.0013402 | 0.25026 | 0.036012 | 0.035635 | 0.0066495 | -0.008294 | 0.012325 | 0.0081364 | -0.027466 | 0.004578 | -0.032043 | 0.032043 | 0.07782 | 0.013733 | 0.032043 | -0.009155 | 0.068665 | -0.032043 | 0.027466 | 0.059509 | 0.050354 | 0.068665 | 61.8393 | -62.059 | -62.0316 | 61.9492 | 61.9034 | 61.8851 | 0.064086 | 0.045776 | 61.8393 | -61.9949 | -62.0361 | 61.9308 | 61.94 | 61.9217 | 0.10071 | 0.082397 | 0.10986 | 0.064086 | 0.091552 | 0.059509 | 0.036621 | 0.10071 | 61.8759 | 61.94 | -62.0956 | -62.0956 | 61.9034 | 61.8988 | 61.8439 | 61.8622
606.9375 | 124.1089 | -61.8942 | 62.0865 | 0.17643 | 0.0050788 | 0.013645 | 0.025111 | 0.018461 | 0.0084198 | 0.0066812 | 0.25026 | 0.048829 | 0.033499 | 0.0013085 | -0.021111 | 0.012325 | -0.0025446 | 0.032043 | 0.045776 | 0.018311 | 0.054932 | 0.07782 | 0.018311 | 0.054932 | -0.018311 | 0.07782 | -0.036621 | -0.022888 | -0.009155 | -0.013733 | 0 | 61.9125 | -62.0407 | -62.0316 | 61.972 | 61.9492 | 61.9125 | 0.036621 | 0 | 61.8576 | -62.0087 | -62.1094 | 61.8851 | 61.8942 | 61.8805 | 0.036621 | 0.022888 | 0.059509 | 0.036621 | 0.027466 | 0.013733 | 0.027465 | 0.11444 | 61.94 | 61.972 | -62.0682 | -62.1231 | 61.9492 | 61.8713 | 61.9263 | 61.8759
607.9844 | 124.1089 | -61.8896 | 62.0911 | 0.084874 | 0.0072148 | 0.018986 | 0.038997 | 0.0088484 | 0.020169 | -0.0029318 | 0.051892 | 0.049898 | 0.039907 | -0.053165 | -0.009362 | 0.015529 | -0.0068176 | 0.041199 | 0.041199 | 0.036621 | 0.041199 | 0.07782 | 0.009155 | 0.045776 | -0.018311 | 0.082397 | -0.041199 | 0 | 0 | -0.013733 | 0.027466 | 61.9263 | -62.0499 | -62.0499 | 61.9675 | 61.9354 | 61.8988 | 0.009155 | -0.027466 | 61.8484 | -62.0087 | -62.0911 | 61.8896 | 61.9171 | 61.8759 | 0.068665 | 0.027466 | 0.041199 | 0.004578 | 0.041199 | 0.041199 | 0.004578 | 0.1236 | 61.9308 | 61.972 | -62.0544 | -62.1323 | 61.9308 | 61.8896 | 61.9308 | 61.8713
608.9375 | 124.0952 | -61.9171 | 62.0956 | 0.17643 | 0.018965 | 0.018986 | 0.032588 | 0.023802 | -0.00012524 | -0.0050688 | -0.0091433 | 0.046693 | 0.034567 | -0.028598 | -0.005089 | 0.019802 | 0.0017274 | -0.027466 | -0.004578 | -0.050354 | 0.064087 | 0.10529 | 0.041199 | 0.064087 | -0.10986 | 0.07782 | -0.068665 | -0.027466 | -0.041199 | -0.054932 | -0.009155 | 61.8668 | -62.1002 | -62.0316 | 62.0224 | 61.9812 | 61.9583 | 0.11444 | 0.091553 | 61.8484 | -62.0178 | -62.1231 | 61.8759 | 61.908 | 61.8622 | 0.05951 | 0.013733 | 0.15564 | 0.11444 | 0.027466 | 0.041199 | 0.045776 | 0.14649 | 61.9125 | 61.9949 | -62.146 | -62.1643 | 61.9812 | 61.8896 | 61.8896 | 61.8073
609.9844 | 124.2096 | -61.8439 | 62.059 | 0.13065 | 0.0050788 | 0.012577 | 0.029384 | 0.015257 | -0.014011 | 0.0013402 | 0.29603 | 0.048829 | 0.036703 | -0.017917 | -0.016839 | 0.019802 | 0.0006594 | -0.022888 | -0.013733 | -0.018311 | -0.013733 | 0.036621 | -0.036621 | -0.027466 | 0.045776 | 0.045776 | -0.009155 | 0.091553 | 0.10529 | 0.091553 | 0.11444 | 61.8256 | -62.0728 | -62.0728 | 61.8805 | 61.8164 | 61.8073 | -0.009155 | -0.01831 | 61.8347 | -62.0132 | -61.9675 | 61.9492 | 61.9583 | 61.9354 | 0.1236 | 0.10071 | 0.054932 | 0.004578 | 0.11444 | 0.10071 | 0.004578 | 0.054931 | 61.8301 | 61.8896 | -62.0773 | -62.0682 | 61.8301 | 61.9354 | 61.821 | 61.8896
610.9375 | 124.1409 | -61.8988 | 62.0956 | 0.13065 | 0.01576 | 0.011509 | 0.037928 | 0.0077804 | 0.0084198 | 0.0013402 | 0.12819 | 0.039216 | 0.031362 | -0.015781 | -0.007226 | 0.011257 | -0.015362 | 0.018311 | 0 | -0.045776 | 0.036621 | 0.073242 | 0.009155 | 0.036621 | 0.022888 | 0.09613 | -0.027466 | 0.022888 | 0.045776 | 0.032043 | 0.050354 | 61.853 | -62.0956 | -62.059 | 61.972 | 61.9354 | 61.908 | 0.082397 | 0.054931 | 61.8713 | -61.9995 | -62.0728 | 61.9446 | 61.9492 | 61.9308 | 0.07782 | 0.059509 | 0.11902 | 0.082397 | 0.073242 | 0.050354 | 0.045776 | 0.1236 | 61.8988 | 61.9949 | -62.1414 | -62.1231 | 61.9354 | 61.9217 | 61.9171 | 61.9217
611.9531 | 124.0952 | -61.908 | 62.0865 | 0.19169 | 0.0072148 | 0.012577 | 0.026179 | -0.0029006 | -0.0065342 | -0.0061368 | 0.34181 | 0.046693 | 0.039907 | -0.031802 | 0.002387 | 0.0080531 | -0.0078856 | 0.013733 | -0.004578 | -0.009155 | 0.009155 | 0.07782 | 0.009155 | 0.036621 | -0.004578 | 0.09613 | -0.022888 | -0.009155 | 0.004578 | 0.045776 | 0.027466 | 61.8988 | -62.0911 | -62.0773 | 61.9858 | 61.9446 | 61.9171 | 0.045776 | 0.01831 | 61.8851 | -61.9904 | -62.0956 | 61.9125 | 61.9354 | 61.9537 | 0.050354 | 0.068664 | 0.086975 | 0.01831 | 0.027466 | 0.013733 | 0.004577 | 0.11902 | 61.9034 | 62.0041 | -62.0956 | -62.1094 | 61.9171 | 61.8988 | 61.9217 | 61.9034
612.9375 | 124.1318 | -61.8713 | 62.0636 | 0.17643 | 0.011488 | 0.0083045 | 0.037928 | 0.0077804 | 0.0030788 | -0.0039998 | 0.08241 | 0.048829 | 0.029226 | -0.040347 | -0.020043 | 0.0091211 | -0.012158 | 0.041199 | 0.032043 | 0.018311 | 0.064087 | 0.07782 | 0.027466 | 0.045776 | -0.022888 | 0.10529 | -0.027466 | -0.027466 | -0.013733 | -0.022888 | 0.013733 | 61.8896 | -62.0316 | -61.9995 | 61.9492 | 61.9171 | 61.8988 | 0.027465 | 0.009155 | 61.8439 | -61.9583 | -62.0911 | 61.8576 | 61.8851 | 61.8484 | 0.041199 | 0.004578 | 0.059509 | 0.045776 | 0.013733 | 0 | 0.013732 | 0.13275 | 61.9034 | 61.9766 | -62.0453 | -62.0911 | 61.9354 | 61.8439 | 61.9125 | 61.8484
613.9375 | 124.118 | -61.8896 | 62.0773 | 0.2222 | 0.01042 | 0.01685 | 0.030452 | 0.0099164 | -0.014011 | -0.010409 | 0.067151 | 0.044557 | 0.024954 | -0.043552 | -0.014702 | 0.016598 | 0.0027964 | 0 | -0.009155 | -0.018311 | 0.050354 | 0.091553 | 0.041199 | 0.064087 | 0.009155 | 0.11902 | -0.013733 | -0.004578 | 0.022888 | 0 | 0.022888 | 61.8713 | -62.0865 | -62.027 | 61.9812 | 61.9537 | 61.9308 | 0.082398 | 0.05951 | 61.8759 | -61.9583 | -62.0819 | 61.9125 | 61.9125 | 61.8896 | 0.036621 | 0.013733 | 0.10986 | 0.068665 | 0.036621 | 0.009155 | 0.009156 | 0.13275 | 61.8805 | 62.0087 | -62.0956 | -62.0911 | 61.94 | 61.8851 | 61.8896 | 61.8988
614.9375 | 124.0723 | -61.9217 | 62.0865 | 0.084874 | 0.0018748 | 0.0083045 | 0.03152 | 0.013121 | -0.00012524 | -0.0061368 | -0.03966 | 0.034944 | 0.043112 | -0.0083045 | -0.007226 | 0.024074 | 0.0006594 | -0.022888 | -0.032043 | -0.032043 | 0.064087 | 0.086975 | 0.045776 | 0.064087 | -0.073242 | 0.091553 | -0.036621 | -0.036621 | -0.041199 | -0.054932 | -0.009155 | 61.8896 | -62.1185 | -62.0224 | 62.0087 | 61.9858 | 61.9675 | 0.09613 | 0.077819 | 61.8851 | -61.9949 | -62.1231 | 61.8805 | 61.9125 | 61.8668 | 0.027466 | -0.018311 | 0.11902 | 0.09613 | -0.004578 | 0 | 0 | 0.12817 | 61.8896 | 62.0132 | -62.1185 | -62.1231 | 61.9858 | 61.8851 | 61.8988 | 61.8484
615.9375 | 124.0997 | -61.8896 | 62.0956 | 0.19169 | -0.0013302 | 0.015781 | 0.038997 | 0.0013714 | 0.011624 | -0.014682 | 0.14344 | 0.044557 | 0.029226 | 0.0034445 | -0.022179 | 0.016598 | 0.0038644 | 0 | 0.013733 | -0.022888 | 0.059509 | 0.091553 | 0.027466 | 0.054932 | -0.045776 | 0.082397 | -0.050354 | -0.041199 | -0.013733 | -0.027466 | -0.004578 | 61.8668 | -62.0819 | -62.0361 | 61.9812 | 61.9446 | 61.9171 | 0.07782 | 0.050354 | 61.8393 | -62.0132 | -62.1368 | 61.8759 | 61.8851 | 61.8622 | 0.045776 | 0.022888 | 0.11444 | 0.082397 | 0.036621 | 0.009155 | 0.036621 | 0.13275 | 61.9034 | 61.972 | -62.1185 | -62.146 | 61.9492 | 61.8484 | 61.8896 | 61.8439
616.9375 | 124.1684 | -61.908 | 62.0865 | 0.17643 | 0.0082828 | 0.0018955 | 0.043269 | -0.0061046 | 0.0041468 | -0.0061368 | 0.021375 | 0.041353 | 0.030294 | -0.02753 | -0.009362 | 0.014461 | -0.012158 | 0.018311 | 0.004578 | -0.027466 | 0.036621 | 0.064087 | 0.009155 | 0.032043 | 0.022888 | 0.082397 | -0.027466 | 0.036621 | 0.050354 | 0.045776 | 0.045776 | 61.8805 | -62.0819 | -62.0499 | 61.972 | 61.94 | 61.9171 | 0.059509 | 0.036621 | 61.8805 | -62.0041 | -62.0499 | 61.9583 | 61.9537 | 61.9537 | 0.073242 | 0.073242 | 0.091553 | 0.064087 | 0.07782 | 0.064087 | 0.032044 | 0.10986 | 61.9125 | 61.9904 | -62.114 | -62.114 | 61.9446 | 61.9446 | 61.9263 | 61.9308
617.9688 | 124.1501 | -61.8988 | 62.0682 | 0.11539 | 0.0050788 | 0.013645 | 0.03686 | 0.0013714 | -0.0054662 | -0.0018638 | 0.18922 | 0.040285 | 0.033499 | 0.014126 | -0.008294 | 0.012325 | -0.0025446 | 0.027466 | -0.004578 | -0.032043 | 0.022888 | 0.068665 | -0.004578 | 0.036621 | 0.018311 | 0.091553 | -0.027466 | 0.032043 | 0.059509 | 0.041199 | 0.059509 | 61.8668 | -62.0728 | -62.0453 | 61.9675 | 61.9354 | 61.8942 | 0.068664 | 0.027465 | 61.8713 | -61.9766 | -62.0361 | 61.9583 | 61.9583 | 61.94 | 0.086975 | 0.068665 | 0.10071 | 0.054931 | 0.086975 | 0.059509 | 0.027465 | 0.11902 | 61.8942 | 61.9904 | -62.1002 | -62.0956 | 61.9217 | 61.9308 | 61.9263 | 61.9171
618.9375 | 124.1318 | -61.9171 | 62.1002 | 0.17643 | 0.014692 | 0.011509 | 0.037928 | 0.0024404 | -0.0086702 | 0.0013402 | 0.25026 | 0.034944 | 0.035635 | -0.028598 | -0.01043 | 0.0080531 | 0.019885 | 0.022888 | -0.022888 | -0.022888 | 0.036621 | 0.073242 | 0.068665 | 0.25635 | 0.018311 | 0.13275 | 0.036621 | 0.032043 | 0.032043 | 0.009155 | 0.036621 | 61.8942 | -62.1231 | -62.0636 | 61.9904 | 62.1735 | 61.9858 | 0.27924 | 0.091553 | 61.9537 | -61.9675 | -62.0682 | 61.9492 | 61.9537 | 61.9263 | 0 | -0.027466 | 0.09613 | 0.059509 | -0.004578 | -0.004578 | 0 | 0.09613 | 61.8942 | 62.0499 | -62.1231 | -62.0636 | 61.9537 | 61.9492 | 61.94 | 61.9354
619.9688 | 124.1226 | -61.8942 | 62.0956 | 0.19169 | 0.0082828 | 0.010441 | 0.037928 | 0.022734 | 0.012692 | 0.0045452 | 0.12819 | 0.033876 | 0.037771 | -0.0093725 | -0.01043 | 0.019802 | -0.0036126 | 0 | 0.013733 | -0.013733 | 0.050354 | 0.09613 | 0.036621 | 0.045776 | -0.036621 | 0.073242 | -0.050354 | -0.022888 | -0.036621 | -0.045776 | -0.004578 | 61.8805 | -62.0819 | -62.0453 | 61.9904 | 61.94 | 61.9308 | 0.059509 | 0.050354 | 61.8439 | -62.0224 | -62.1185 | 61.8576 | 61.8896 | 61.8485 | 0.045776 | 0.004578 | 0.10986 | 0.064087 | 0.013733 | 0.027466 | 0.027466 | 0.1236 | 61.908 | 61.9675 | -62.1094 | -62.146 | 61.9446 | 61.8713 | 61.8942 | 61.8576
620.9375 | 124.1501 | -61.8988 | 62.0956 | 0.10013 | 0.014692 | 0.012577 | 0.034724 | 0.020598 | -0.017215 | -0.0082728 | 0.097669 | 0.040285 | 0.031362 | -0.031802 | -0.011498 | 0.023006 | -0.0068176 | 0.009155 | 0.036621 | 0.022888 | 0.045776 | 0.082397 | 0.013733 | 0.050354 | -0.022888 | 0.086975 | -0.036621 | -0.009155 | 0.004578 | -0.013733 | 0.013733 | 61.9217 | -62.059 | -62.0499 | 61.9812 | 61.9492 | 61.9125 | 0.027466 | -0.009155 | 61.8622 | -62.0087 | -62.1048 | 61.9034 | 61.9125 | 61.8851 | 0.050354 | 0.022888 | 0.059509 | 0.022888 | 0.041199 | 0.027466 | 0.013733 | 0.1236 | 61.9354 | 61.9858 | -62.0728 | -62.1323 | 61.9446 | 61.8896 | 61.908 | 61.8759
621.9844 | 124.2325 | -61.8896 | 62.0682 | 0.17643 | -0.0013302 | 0.011509 | 0.032588 | -0.0061046 | -0.012943 | 0.0056132 | 0.54017 | 0.039216 | 0.021749 | -0.041416 | -0.001885 | 0.011257 | 0.0017274 | 0.018311 | -0.032043 | 0.004578 | -0.032043 | 0.022888 | -0.045776 | -0.027466 | 0.059509 | 0.068665 | 0.004578 | 0.082397 | 0.13275 | 0.13733 | 0.12817 | 61.8942 | -62.1002 | -62.1002 | 61.9125 | 61.8622 | 61.8439 | -0.032044 | -0.050354 | 61.8942 | -61.9995 | -61.9858 | 62.0224 | 62.0178 | 62.027 | 0.1236 | 0.13275 | 0.01831 | -0.036621 | 0.12817 | 0.077819 | -0.036621 | 0.064087 | 61.8576 | 61.9583 | -62.0636 | -62.0636 | 61.8576 | 61.972 | 61.908 | 61.9492
622.9375 | 124.1547 | -61.8988 | 62.0911 | 0.17643 | 0.0050788 | 0.012577 | 0.027247 | 0.010984 | 0.012692 | -0.0050688 | 0.021375 | 0.044557 | 0.031362 | -0.014713 | -0.020043 | 0.017666 | 0.0006594 | 0.022888 | -0.009155 | -0.032043 | 0.027466 | 0.050354 | 0.018311 | 0.050354 | 0.082397 | 0.086975 | -0.004578 | 0.032043 | 0.054932 | 0.054932 | 0.050354 | 61.8668 | -62.1002 | -62.0636 | 61.9492 | 61.9492 | 61.9171 | 0.082397 | 0.050354 | 61.8942 | -62.0041 | -62.059 | 61.9537 | 61.9492 | 61.9537 | 0.054932 | 0.05951 | 0.082397 | 0.059509 | 0.05951 | 0.036621 | 0.022888 | 0.091553 | 61.8896 | 61.9858 | -62.1231 | -62.0956 | 61.9263 | 61.9308 | 61.9217 | 61.9812
623.9531 | 124.205 | -61.8805 | 62.0956 | 0.20695 | 0.0093518 | 0.01685 | 0.025111 | 0.0088484 | -0.00012524 | 0.014158 | 0.57069 | 0.043489 | 0.030294 | -0.059573 | -0.021111 | 0.021938 | -0.0014766 | 0.036621 | -0.041199 | 0.018311 | -0.13733 | -0.041199 | 0.086975 | -0.082397 | 0.050354 | 0.045776 | -0.022888 | 0.086975 | 0.1236 | 0.11444 | 0.10529 | 61.8988 | -62.1368 | -62.233 | 61.8393 | 61.7981 | 61.9675 | -0.10071 | 0.068664 | 61.8576 | -62.0499 | -62.0087 | 62.0041 | 61.9858 | 61.9949 | 0.12817 | 0.13733 | -0.05951 | -0.15564 | 0.14648 | 0.10986 | -0.05951 | 0.068664 | 61.8393 | 61.9263 | -62.0773 | -62.1185 | 61.7432 | 61.9675 | 61.9171 | 61.9308
624.9375 | 124.1638 | -61.9034 | 62.0911 | 0.25272 | 0.0093518 | 0.0061675 | 0.044337 | 0.0024404 | -0.0097382 | -0.0029318 | 0.18922 | 0.040285 | 0.031362 | -0.0072365 | -0.020043 | 0.015529 | -0.0089536 | 0.004578 | -0.009155 | -0.050354 | 0.073242 | 0.10529 | 0.018311 | 0.050354 | -0.036621 | 0.091553 | -0.027466 | 0 | 0.032043 | 0.022888 | 0.032043 | 61.853 | -62.1002 | -62.0178 | 62.0087 | 61.9537 | 61.9217 | 0.10071 | 0.068665 | 61.8759 | -61.9995 | -62.0911 | 61.9354 | 61.9354 | 61.9263 | 0.059509 | 0.050354 | 0.15564 | 0.1236 | 0.059509 | 0.027466 | 0.041199 | 0.11902 | 61.8942 | 61.9949 | -62.1414 | -62.1185 | 61.9766 | 61.9034 | 61.908 | 61.8668
625.9688 | 124.1547 | -61.8805 | 62.1002 | 0.25272 | 0.0093518 | 0.0018955 | 0.030452 | -0.0039686 | -0.0076022 | 0.0013402 | 0.11293 | 0.073396 | 0.035635 | 0.00024052 | -0.014702 | 0.017666 | -0.0057486 | 0.018311 | -0.009155 | -0.032043 | 0.032043 | 0.064087 | 0 | 0.041199 | 0.13275 | 0.10529 | 0.013733 | 0.032043 | 0.036621 | 0.018311 | 0.050354 | 61.8484 | -62.1094 | -62.0682 | 61.9446 | 61.9217 | 61.8805 | 0.073242 | 0.032043 | 61.8942 | -61.9949 | -62.0682 | 61.9171 | 61.9308 | 61.8988 | 0.036621 | 0.004578 | 0.09613 | 0.064086 | 0.022888 | 0.01831 | 0.022888 | 0.091553 | 61.8713 | 61.9858 | -62.1323 | -62.0865 | 61.9125 | 61.9125 | 61.8988 | 62.0132
626.9375 | 124.1638 | -61.8942 | 62.1002 | 0.20695 | 0.0093518 | 0.015781 | 0.03152 | -0.010378 | -0.0086702 | -0.016818 | 0.17396 | 0.048829 | 0.034567 | -0.021121 | -0.014702 | 0.014461 | -0.0057486 | 0 | -0.013733 | -0.013733 | 0.036621 | 0.064087 | -0.009155 | 0.036621 | 0.018311 | 0.082397 | -0.041199 | 0.018311 | 0.059509 | 0.041199 | 0.050354 | 61.8805 | -62.114 | -62.0636 | 61.9583 | 61.9308 | 61.8851 | 0.050354 | 0.004578 | 61.853 | -62.0178 | -62.0819 | 61.9537 | 61.9446 | 61.9354 | 0.091553 | 0.082398 | 0.07782 | 0.050354 | 0.10071 | 0.05951 | 0 | 0.1236 | 61.8805 | 61.9766 | -62.114 | -62.1414 | 61.9308 | 61.9125 | 61.8942 | 61.9125
627.9375 | 124.1547 | -61.908 | 62.1094 | 0.26798 | 0.01042 | 0.013645 | 0.034724 | -0.00076463 | -0.0011942 | -0.0072048 | 0.17396 | 0.036012 | 0.021749 | 0.0013085 | -0.00081695 | 0.015529 | -0.010022 | 0.022888 | 0 | -0.022888 | 0.032043 | 0.050354 | 0.004578 | 0.032043 | 0.022888 | 0.082397 | -0.018311 | 0.013733 | 0.050354 | 0.036621 | 0.041199 | 61.8851 | -62.1094 | -62.0773 | 61.9583 | 61.94 | 61.9125 | 0.054931 | 0.027466 | 61.8896 | -62.027 | -62.0956 | 61.9583 | 61.9492 | 61.9446 | 0.05951 | 0.054932 | 0.073242 | 0.054931 | 0.068665 | 0.032044 | 0.022888 | 0.10071 | 61.908 | 61.9904 | -62.1323 | -62.1277 | 61.94 | 61.9217 | 61.9308 | 61.9308
628.9375 | 124.1592 | -61.908 | 62.1277 | 0.2222 | 0.0093518 | 0.0093725 | 0.032588 | -0.0061046 | 0.0084198 | -0.00079579 | 0.20448 | 0.041353 | 0.036703 | -0.021121 | -0.012566 | 0.019802 | 0.0017274 | 0.032043 | -0.013733 | -0.041199 | 0.036621 | 0.068665 | 0.022888 | 0.022888 | 0.018311 | 0.09613 | -0.032043 | 0.032043 | 0.054932 | 0.032043 | 0.050354 | 61.8668 | -62.1414 | -62.0911 | 61.9766 | 61.9308 | 61.9308 | 0.064087 | 0.064087 | 61.8759 | -62.0316 | -62.0956 | 61.9629 | 61.9583 | 61.94 | 0.082397 | 0.064086 | 0.10986 | 0.07782 | 0.086975 | 0.064086 | 0.027466 | 0.12817 | 61.8942 | 62.0041 | -62.1689 | -62.1597 | 61.9446 | 61.94 | 61.94 | 61.9263
629.9375 | 124.1592 | -61.8988 | 62.1048 | 0.23746 | 0.013624 | 0.013645 | 0.032588 | 0.0099164 | 0.016964 | 0.0024082 | 0.235 | 0.041353 | 0.033499 | -0.020053 | -0.009362 | 0.013393 | 0.01134 | 0.027466 | 0.009155 | -0.027466 | 0.054932 | 0.073242 | 0.013733 | 0.036621 | 0.018311 | 0.091553 | -0.018311 | 0.027466 | 0.050354 | 0.041199 | 0.059509 | 61.8713 | -62.0956 | -62.0499 | 61.972 | 61.9354 | 61.9125 | 0.064087 | 0.041199 | 61.8805 | -62.0132 | -62.0773 | 61.9492 | 61.9583 | 61.94 | 0.07782 | 0.05951 | 0.10071 | 0.082398 | 0.068665 | 0.045777 | 0.036621 | 0.10986 | 61.908 | 61.9904 | -62.1323 | -62.1231 | 61.9537 | 61.9263 | 61.9263 | 61.9171
630.9375 | 124.1409 | -61.908 | 62.1185 | 0.2222 | -0.00026223 | 0.015781 | 0.030452 | -0.0050366 | 0.010556 | 0.0045452 | 0.18922 | 0.042421 | 0.040975 | -0.014713 | -0.021111 | 0.015529 | -0.0089536 | -0.022888 | 0.009155 | -0.009155 | 0.073242 | 0.13733 | 0.045776 | 0.086975 | -0.07782 | 0.086975 | -0.054932 | -0.036621 | 0 | 0.004578 | 0.013733 | 61.8988 | -62.1094 | -62.0453 | 62.0453 | 61.9949 | 61.9537 | 0.09613 | 0.054931 | 61.853 | -62.0316 | -62.1552 | 61.908 | 61.9217 | 61.9125 | 0.068665 | 0.05951 | 0.14648 | 0.082397 | 0.054932 | 0.018311 | 0.01831 | 0.14191 | 61.9171 | 61.9949 | -62.1277 | -62.1735 | 61.9812 | 61.8713 | 61.8851 | 61.8301
631.9375 | 124.1272 | -61.9263 | 62.0956 | 0.23746 | 0.0029428 | 0.0083045 | 0.024043 | 0.0067124 | -0.0033302 | -0.00079579 | 0.34181 | 0.050966 | 0.045248 | -0.042484 | -0.014702 | 0.011257 | 0.0070684 | -0.036621 | 0.009155 | -0.045776 | 0.086975 | 0.13733 | 0.064087 | 0.082397 | -0.064087 | 0.09613 | -0.041199 | -0.036621 | 0.004578 | -0.004578 | -0.009155 | 61.8805 | -62.0865 | -62.0087 | 62.0636 | 62.0087 | 61.9904 | 0.12817 | 0.10986 | 61.8851 | -61.9995 | -62.1323 | 61.9308 | 61.9171 | 61.9217 | 0.032044 | 0.036621 | 0.18311 | 0.13275 | 0.045777 | 0.004578 | 0.054931 | 0.13733 | 61.9354 | 62.0224 | -62.1414 | -62.1368 | 62.0132 | 61.8896 | 61.8896 | 61.8622
632.9375 | 124.1455 | -61.8759 | 62.1368 | 0.28324 | 0.0018748 | 0.01685 | 0.029384 | 0.021666 | -0.0033302 | -0.013613 | 0.21974 | 0.040285 | 0.036703 | -0.029666 | -0.006157 | 0.017666 | 0.010272 | -0.013733 | -0.004578 | -0.041199 | 0.091553 | 0.14191 | 0.050354 | 0.082397 | -0.059509 | 0.09613 | -0.041199 | -0.018311 | 0.013733 | 0.004578 | 0.018311 | 61.8347 | -62.1414 | -62.0453 | 62.0178 | 61.9583 | 61.9263 | 0.1236 | 0.091553 | 61.8347 | -62.0407 | -62.1552 | 61.8896 | 61.8942 | 61.8805 | 0.05951 | 0.045777 | 0.18311 | 0.13275 | 0.054932 | 0.022888 | 0.036621 | 0.13733 | 61.8713 | 61.972 | -62.178 | -62.178 | 61.9675 | 61.8576 | 61.8622 | 61.8164
633.9375 | 124.1638 | -61.8942 | 62.1002 | 0.13065 | 0.0050788 | 0.0050995 | 0.044337 | -0.0018326 | -0.02042 | -0.0018638 | 0.14344 | 0.044557 | 0.023886 | -0.0018955 | -0.013634 | 0.012325 | -0.012158 | 0.009155 | 0.004578 | -0.032043 | 0.064087 | 0.1236 | 0.032043 | 0.054932 | -0.018311 | 0.09613 | -0.027466 | 0.009155 | 0.054932 | 0.041199 | 0.050354 | 61.8622 | -62.0956 | -62.0361 | 62.0178 | 61.9492 | 61.9263 | 0.086975 | 0.064086 | 61.8668 | -62.0041 | -62.0911 | 61.9492 | 61.9446 | 61.9354 | 0.07782 | 0.068665 | 0.15564 | 0.09613 | 0.082398 | 0.036621 | 0.036621 | 0.1236 | 61.8988 | 61.9904 | -62.1323 | -62.1277 | 61.9583 | 61.9034 | 61.9034 | 61.8759
634.9375 | 124.1638 | -61.9171 | 62.1323 | 0.20695 | 0.018965 | 0.0072355 | 0.03686 | 0.0045764 | -0.010807 | 0.0034762 | 0.17396 | 0.045625 | 0.02709 | -0.028598 | -0.017907 | 0.016598 | -0.0068176 | -0.004578 | 0.013733 | -0.027466 | 0.07782 | 0.13275 | 0.041199 | 0.073242 | -0.064087 | 0.09613 | -0.036621 | -0.009155 | 0.032043 | 0.027466 | 0.032043 | 61.8896 | -62.1185 | -62.0544 | 62.0499 | 61.9904 | 61.9583 | 0.10071 | 0.068665 | 61.8805 | -62.0361 | -62.1414 | 61.9492 | 61.9492 | 61.9446 | 0.068664 | 0.064087 | 0.16022 | 0.10529 | 0.068664 | 0.027466 | 0.041199 | 0.13275 | 61.9308 | 62.0132 | -62.1597 | -62.1689 | 61.9949 | 61.908 | 61.9125 | 61.853
635.9375 | 124.1638 | -61.9263 | 62.1002 | 0.34427 | -0.00026223 | 0.015781 | 0.03152 | 0.012053 | 0.011624 | 0.0066812 | 0.235 | 0.049898 | 0.031362 | -0.016849 | -0.008294 | 0.014461 | -0.0025446 | -0.018311 | 0.027466 | -0.041199 | 0.091553 | 0.12817 | 0.054932 | 0.07782 | -0.054932 | 0.091553 | -0.036621 | -0.022888 | 0.009155 | 0.013733 | 0.018311 | 61.8851 | -62.0728 | -62.0087 | 62.0544 | 62.0041 | 61.9812 | 0.11902 | 0.096131 | 61.8896 | -62.0087 | -62.1231 | 61.9354 | 61.9446 | 61.94 | 0.054932 | 0.050354 | 0.16937 | 0.13275 | 0.045776 | 0.013733 | 0.068665 | 0.12817 | 61.9537 | 62.0178 | -62.1414 | -62.1368 | 62.0178 | 61.9034 | 61.908 | 61.8713
636.9375 | 124.1226 | -61.9171 | 62.1277 | 0.17643 | 0.017896 | 0.012577 | 0.029384 | 0.016325 | -0.017215 | -0.016818 | 0.28077 | 0.042421 | 0.030294 | -0.028598 | -0.014702 | 0.0027121 | -0.015362 | -0.022888 | -0.004578 | -0.032043 | 0.10071 | 0.13733 | 0.054932 | 0.073242 | -0.050354 | 0.11444 | -0.054932 | -0.022888 | 0.004578 | 0.009155 | 0.013733 | 61.8851 | -62.1323 | -62.027 | 62.0544 | 61.9904 | 61.972 | 0.10529 | 0.086975 | 61.8622 | -62.0132 | -62.1506 | 61.9217 | 61.9308 | 61.9263 | 0.068665 | 0.064087 | 0.16937 | 0.13275 | 0.05951 | 0.032044 | 0.027465 | 0.16937 | 61.9125 | 62.0316 | -62.1597 | -62.1826 | 62.0178 | 61.8942 | 61.8942 | 61.8668
637.9688 | 124.1226 | -61.9171 | 62.1185 | 0.19169 | 0.01042 | 0.015781 | 0.027247 | 0.0035084 | 0.0062828 | 0.0045452 | 0.40284 | 0.042421 | 0.039907 | -0.013645 | -0.014702 | 0.0048481 | 0.0049324 | 0.022888 | -0.009155 | -0.022888 | 0.050354 | 0.091553 | 0.041199 | 0.054932 | -0.032043 | 0.073242 | -0.018311 | -0.022888 | 0 | 0.022888 | 0.004578 | 61.8942 | -62.1277 | -62.0682 | 62.0087 | 61.972 | 61.9583 | 0.07782 | 0.064087 | 61.8988 | -62.0453 | -62.1414 | 61.9171 | 61.9217 | 61.94 | 0.022889 | 0.041199 | 0.11444 | 0.073242 | 0.018311 | -0.004577 | 0.013733 | 0.091553 | 61.908 | 61.9904 | -62.1414 | -62.1368 | 61.9675 | 61.8942 | 61.94 | 61.8851
638.9375 | 124.1547 | -61.9125 | 62.1185 | 0.16117 | -0.00026223 | 0.00082752 | 0.038997 | 0.0099164 | 0.022305 | 0.0045452 | 0.44862 | 0.036012 | 0.036703 | -0.0061685 | -0.014702 | 0.015529 | -0.0025446 | 0.045776 | -0.036621 | -0.004578 | 0 | 0.050354 | -0.004578 | 0.013733 | 0.009155 | 0.07782 | -0.032043 | -0.013733 | 0.036621 | 0.009155 | 0.027466 | 61.908 | -62.1552 | -62.1185 | 61.9629 | 61.9263 | 61.908 | 0.018311 | 0 | 61.8805 | -62.0407 | -62.1323 | 61.9492 | 61.94 | 61.9217 | 0.059509 | 0.041198 | 0.054932 | 0.004578 | 0.068664 | 0.01831 | -0.032043 | 0.10986 | 61.8759 | 61.9904 | -62.1231 | -62.1506 | 61.9125 | 61.8988 | 61.9583 | 61.9217
638.8125 | 124.1226 | -61.9308 | 62.1277 | 0.32902 | 0.01576 | 0.01685 | 0.033656 | 0.0056444 | -0.023624 | 0.00027221 | 0.37233 | 0.040285 | 0.037771 | -0.014713 | -0.016839 | 0.00057606 | -0.0089536 | -0.022888 | -0.004578 | -0.027466 | 0.07782 | 0.12817 | 0.036621 | 0.086975 | -0.045776 | 0.09613 | -0.041199 | -0.050354 | 0.009155 | 0.009155 | -0.004578 | 61.9034 | -62.1323 | -62.0499 | 62.059 | 62.0178 | 61.9675 | 0.11444 | 0.064087 | 61.8896 | -62.0316 | -62.178 | 61.94 | 61.9263 | 61.94 | 0.036621 | 0.050354 | 0.15564 | 0.10529 | 0.050354 | -0.009155 | 0.022888 | 0.13733 | 61.9263 | 62.027 | -62.1552 | -62.1689 | 62.0087 | 61.8805 | 61.908 | 61.8851
639.8125 | 124.1409 | -61.9125 | 62.1414 | 0.16117 | 0.017896 | 0.011509 | 0.040065 | 0.00030337 | 0.021237 | -0.0039998 | 0.26551 | 0.03174 | 0.029226 | -0.017917 | -0.012566 | 0.0016441 | -0.027112 | 0.013733 | 0 | -0.018311 | 0.032043 | 0.086975 | 0.027466 | 0.050354 | -0.013733 | 0.09613 | -0.004578 | -0.027466 | 0.013733 | 0.013733 | 0.009155 | 61.8942 | -62.1414 | -62.1094 | 61.9995 | 61.9629 | 61.94 | 0.068665 | 0.045777 | 61.908 | -62.0453 | -62.1689 | 61.9263 | 61.9217 | 61.9263 | 0.013733 | 0.018311 | 0.10529 | 0.050354 | 0.018311 | -0.022888 | 0.018311 | 0.10071 | 61.9125 | 62.0087 | -62.1597 | -62.146 | 61.9446 | 61.8851 | 61.9263 | 61.8988
640.8125 | 124.1364 | -61.9308 | 62.1094 | 0.2985 | 0.0050788 | 0.0050995 | 0.030452 | 0.0024404 | -0.00012524 | -0.0061368 | 0.18922 | 0.03708 | 0.038839 | -0.0072365 | -0.025384 | 0.0069851 | -0.0068176 | -0.032043 | -0.013733 | -0.032043 | 0.082397 | 0.11444 | 0.050354 | 0.09613 | -0.050354 | 0.10071 | -0.032043 | -0.059509 | -0.004578 | 0.004578 | 0.009155 | 61.8988 | -62.1231 | -62.027 | 62.0453 | 62.027 | 61.9812 | 0.12817 | 0.082397 | 61.8988 | -62.0087 | -62.1689 | 61.9263 | 61.94 | 61.9354 | 0.041198 | 0.036621 | 0.14648 | 0.11444 | 0.027465 | -0.027466 | 0.01831 | 0.13275 | 61.9171 | 62.0316 | -62.1414 | -62.1414 | 62.0132 | 61.8713 | 61.8988 | 61.8805
641.8281 | 124.2462 | -61.8759 | 62.0636 | 0.023839 | 0.01042 | 0.013645 | 0.033656 | -0.00076463 | 0.0020108 | -0.0039998 | 0.21974 | 0.033876 | 0.029226 | -0.018985 | -0.021111 | 0.011257 | 0.014545 | 0.041199 | -0.059509 | 0 | -0.064087 | -0.036621 | -0.068665 | -0.068665 | 0.091553 | 0.041199 | -0.004578 | 0.082397 | 0.11444 | 0.091553 | 0.10529 | 61.8759 | -62.1231 | -62.1277 | 61.8393 | 61.8073 | 61.8073 | -0.068665 | -0.068665 | 61.8713 | -62.0224 | -61.9812 | 61.9904 | 61.9812 | 61.9675 | 0.10986 | 0.096131 | -0.036621 | -0.064087 | 0.11902 | 0.086975 | -0.059509 | 0.045777 | 61.8164 | 61.9171 | -62.0636 | -62.0682 | 61.8118 | 61.9583 | 61.9171 | 61.9675
642.8438 | 124.1364 | -61.908 | 62.114 | 0.16117 | 0.00080677 | 0.0029635 | 0.037928 | -0.0018326 | -0.012943 | 0.0045452 | 0.20448 | 0.047761 | 0.030294 | 0.021603 | -0.016839 | 0.023006 | -0.0014766 | -0.013733 | 0 | -0.032043 | 0.082397 | 0.13275 | 0.050354 | 0.07782 | -0.054932 | 0.10529 | -0.032043 | -0.018311 | 0.004578 | 0.009155 | 0.036621 | 61.8759 | -62.114 | -62.0316 | 62.0407 | 61.9858 | 61.9583 | 0.10986 | 0.082397 | 61.8759 | -62.0087 | -62.1323 | 61.9125 | 61.9446 | 61.9171 | 0.068664 | 0.041198 | 0.16479 | 0.11444 | 0.036621 | 0.013732 | 0.032043 | 0.13733 | 61.908 | 62.0132 | -62.146 | -62.146 | 61.9904 | 61.8896 | 61.8942 | 61.853
643.8125 | 124.2416 | -61.8668 | 62.1002 | 0.26798 | 0.0040108 | 0.011509 | 0.032588 | 0.015257 | -0.021488 | -0.0093408 | 0.32655 | 0.043489 | 0.019613 | -0.023258 | -0.01043 | 0.0080531 | -0.0025446 | 0.050354 | -0.045776 | -0.004578 | -0.059509 | -0.009155 | -0.059509 | -0.027466 | 0.082397 | 0.050354 | -0.009155 | 0.064087 | 0.11444 | 0.10071 | 0.091553 | 61.8622 | -62.146 | -62.1597 | 61.8576 | 61.8393 | 61.8073 | -0.022888 | -0.054931 | 61.8576 | -62.0499 | -62.0361 | 61.9812 | 61.9583 | 61.9675 | 0.10071 | 0.10986 | -0.004577 | -0.054931 | 0.1236 | 0.073242 | -0.041198 | 0.059509 | 61.821 | 61.9171 | -62.1048 | -62.1094 | 61.8073 | 61.9308 | 61.9171 | 61.9492
644.8125 | 124.2599 | -61.8805 | 62.1002 | 0.2222 | 0.012556 | 0.0050995 | 0.035792 | -0.010378 | -0.00012524 | -0.01575 | 0.35707 | 0.047761 | 0.029226 | -0.039279 | -0.01043 | 0.011257 | -0.0089536 | 0.054932 | -0.036621 | 0.018311 | -0.068665 | -0.027466 | -0.086975 | -0.041199 | 0.09613 | 0.059509 | -0.004578 | 0.082397 | 0.11444 | 0.11902 | 0.09613 | 61.8988 | -62.1368 | -62.1689 | 61.853 | 61.8393 | 61.7935 | -0.05951 | -0.10529 | 61.8759 | -62.0407 | -62.0178 | 61.9949 | 61.9766 | 61.9995 | 0.10071 | 0.1236 | -0.045777 | -0.086976 | 0.11902 | 0.086975 | -0.054932 | 0.064087 | 61.8439 | 61.94 | -62.0819 | -62.1048 | 61.8118 | 61.9629 | 61.9354 | 61.9766
645.8125 | 124.1913 | -61.908 | 62.114 | 0.17643 | 0.014692 | 0.010441 | 0.026179 | -0.0018326 | -0.0033302 | -0.016818 | 0.34181 | 0.032808 | 0.030294 | 0.025876 | -0.01043 | 0.0069851 | -0.018567 | 0.050354 | -0.041199 | 0.009155 | -0.041199 | 0.009155 | -0.036621 | -0.013733 | 0.054932 | 0.073242 | -0.013733 | 0.032043 | 0.073242 | 0.059509 | 0.068665 | 61.9171 | -62.1552 | -62.1552 | 61.9171 | 61.8942 | 61.8713 | -0.022888 | -0.045776 | 61.8942 | -62.0407 | -62.0819 | 61.9812 | 61.9766 | 61.9675 | 0.082398 | 0.073242 | 0 | -0.050354 | 0.086975 | 0.045776 | -0.050354 | 0.086975 | 61.8668 | 61.9812 | -62.1048 | -62.1277 | 61.8668 | 61.94 | 61.9583 | 61.9629
646.8125 | 124.1684 | -61.908 | 62.0956 | 0.14591 | 0.0061468 | 0.0050995 | 0.034724 | 0.0088484 | 0.0062828 | -0.011477 | -0.070178 | 0.053102 | 0.042044 | -0.01044 | -0.016839 | 0.021938 | -0.012158 | -0.032043 | -0.018311 | -0.032043 | 0.091553 | 0.13275 | 0.054932 | 0.054932 | -0.059509 | 0.10529 | -0.022888 | -0.013733 | -0.027466 | -0.022888 | 0.018311 | 61.8759 | -62.114 | -62.0041 | 62.0407 | 61.9629 | 61.9629 | 0.086975 | 0.086975 | 61.8851 | -61.9904 | -62.1094 | 61.8805 | 61.9263 | 61.8851 | 0.041199 | 0 | 0.16479 | 0.1236 | -0.004578 | 0.009155 | 0.013732 | 0.12817 | 61.8896 | 62.0132 | -62.1277 | -62.1185 | 61.9995 | 61.8942 | 61.8759 | 61.8484
647.8125 | 124.1501 | -61.908 | 62.114 | 0.10013 | 0.0072148 | 0.0040315 | 0.037928 | 0.018461 | 0.018033 | -0.012545 | 0.28077 | 0.040285 | 0.031362 | 0.0034445 | -0.013634 | 0.013393 | -0.0004086 | 0.036621 | -0.027466 | -0.009155 | -0.018311 | 0.036621 | -0.013733 | 0.009155 | 0.027466 | 0.059509 | -0.022888 | 0 | 0.045776 | 0.036621 | 0.032043 | 61.8988 | -62.1414 | -62.1323 | 61.9446 | 61.9171 | 61.8942 | 0.01831 | -0.004578 | 61.8851 | -62.0544 | -62.114 | 61.9537 | 61.94 | 61.9446 | 0.054931 | 0.059509 | 0.045776 | -0.009156 | 0.068664 | 0.022888 | -0.018311 | 0.082397 | 61.8805 | 61.9675 | -62.1231 | -62.1368 | 61.8896 | 61.908 | 61.9446 | 61.9354
648.8125 | 124.205 | -61.8759 | 62.0911 | 0.2222 | 0.022169 | 0.0072355 | 0.03686 | -0.0018326 | 0.00094276 | -0.0050688 | 0.34181 | 0.038148 | 0.036703 | -0.030734 | -0.011498 | 0.014461 | -0.021771 | 0.054932 | -0.041199 | 0.018311 | -0.045776 | 0.018311 | -0.045776 | -0.018311 | 0.059509 | 0.068665 | -0.018311 | 0.041199 | 0.086975 | 0.082397 | 0.059509 | 61.8942 | -62.1323 | -62.1368 | 61.8942 | 61.8576 | 61.8301 | -0.036622 | -0.064087 | 61.8576 | -62.0224 | -62.0499 | 61.9629 | 61.9354 | 61.9583 | 0.07782 | 0.10071 | 0 | -0.064087 | 0.10529 | 0.05951 | -0.05951 | 0.086976 | 61.8347 | 61.9446 | -62.0728 | -62.1094 | 61.8301 | 61.9171 | 61.9308 | 61.9354
649.8125 | 124.2142 | -61.8805 | 62.1185 | 0.19169 | 0.012556 | 0.017918 | 0.033656 | -0.0061046 | 0.00094276 | 0.0066812 | 0.18922 | 0.032808 | 0.024954 | -0.036075 | -0.024315 | 0.014461 | -0.0078856 | 0.059509 | -0.054932 | 0.013733 | -0.054932 | -0.022888 | -0.073242 | -0.027466 | 0.091553 | 0.073242 | -0.004578 | 0.064087 | 0.11444 | 0.10529 | 0.082397 | 61.8942 | -62.1735 | -62.1735 | 61.8576 | 61.853 | 61.8073 | -0.041199 | -0.086975 | 61.8759 | -62.0453 | -62.0544 | 61.9949 | 61.9629 | 61.9858 | 0.086975 | 0.10986 | -0.036621 | -0.068665 | 0.11902 | 0.068665 | -0.068665 | 0.07782 | 61.8256 | 61.9537 | -62.1048 | -62.1231 | 61.8256 | 61.9446 | 61.94 | 61.972
650.8125 | 124.2783 | -61.8851 | 62.0911 | 0.20695 | 0.0061468 | 0.012577 | 0.029384 | -0.0071726 | -0.017215 | -0.0050688 | 0.38759 | 0.038148 | 0.023886 | -0.015781 | -0.011498 | 0.013393 | -0.0089536 | 0.032043 | -0.041199 | -0.004578 | -0.082397 | -0.050354 | -0.091553 | -0.059509 | 0.11902 | 0.045776 | 0 | 0.09613 | 0.14648 | 0.13275 | 0.10986 | 61.8805 | -62.1323 | -62.1735 | 61.8347 | 61.8256 | 61.7935 | -0.054931 | -0.086975 | 61.8851 | -62.0453 | -61.9949 | 62.0316 | 61.9949 | 62.0178 | 0.10986 | 0.13275 | -0.045776 | -0.077819 | 0.14648 | 0.09613 | -0.036621 | 0.045776 | 61.8439 | 61.9308 | -62.0956 | -62.0911 | 61.8027 | 61.9812 | 61.9171 | 62.0041
651.8125 | 124.2783 | -61.8759 | 62.0773 | 0.16117 | 0.012556 | 0.0050995 | 0.033656 | -0.015718 | 0.0030788 | -0.0072048 | 0.21974 | 0.044557 | 0.033499 | -0.0029635 | -0.01577 | 0.0069851 | 0.0027964 | 0.041199 | -0.027466 | -0.004578 | -0.059509 | -0.027466 | -0.082397 | -0.045776 | 0.13733 | 0.041199 | -0.013733 | 0.091553 | 0.15106 | 0.17395 | 0.11902 | 61.8713 | -62.1048 | -62.1368 | 61.8484 | 61.8301 | 61.7935 | -0.041198 | -0.077819 | 61.8622 | -62.0361 | -61.9858 | 62.027 | 61.9949 | 62.0499 | 0.13275 | 0.18768 | -0.022888 | -0.054931 | 0.16479 | 0.10529 | -0.022888 | 0.054932 | 61.8484 | 61.9171 | -62.0819 | -62.0911 | 61.8164 | 61.9675 | 61.9171 | 62.0132
652.8125 | 124.2783 | -61.8759 | 62.0819 | 0.20695 | 0.0029428 | 0.0040315 | 0.035792 | 0.010984 | -0.016147 | -0.0093408 | 0.40284 | 0.033876 | 0.029226 | -0.032871 | -0.016839 | 0.016598 | -0.010022 | 0.059509 | -0.036621 | 0.004578 | -0.086975 | -0.041199 | -0.073242 | -0.050354 | 0.10529 | 0.054932 | -0.013733 | 0.09613 | 0.14648 | 0.14648 | 0.09613 | 61.8805 | -62.1185 | -62.1689 | 61.8347 | 61.8256 | 61.8027 | -0.054932 | -0.07782 | 61.8622 | -62.027 | -61.9858 | 62.0224 | 61.972 | 62.0224 | 0.10986 | 0.16022 | -0.045777 | -0.091553 | 0.16022 | 0.10986 | -0.041199 | 0.068665 | 61.8393 | 61.9308 | -62.0773 | -62.0956 | 61.7889 | 61.972 | 61.9354 | 61.9812
653.8125 | 124.2508 | -61.9034 | 62.0911 | 0.039098 | 0.011488 | 0.014713 | 0.035792 | 0.012053 | -0.0043982 | 0.0098852 | 0.31129 | 0.038148 | 0.030294 | -0.040347 | -0.01577 | 0.02087 | -0.0078856 | 0.036621 | -0.050354 | 0.018311 | -0.091553 | -0.059509 | -0.10529 | -0.073242 | 0.13733 | 0.082397 | 0.004578 | 0.10071 | 0.14648 | 0.13733 | 0.10529 | 61.9217 | -62.1414 | -62.1826 | 61.8439 | 61.8301 | 61.7981 | -0.091553 | -0.1236 | 61.908 | -62.0087 | -61.9904 | 62.0499 | 62.0087 | 62.0407 | 0.10071 | 0.13275 | -0.07782 | -0.10986 | 0.14191 | 0.09613 | -0.068665 | 0.077819 | 61.853 | 61.9858 | -62.0728 | -62.0865 | 61.8118 | 62.0041 | 61.94 | 62.0407
654.8125 | 124.2462 | -61.8622 | 62.0911 | 0.20695 | 0.01042 | 0.010441 | 0.034724 | 0.0056444 | 0.00094276 | -0.0050688 | 0.31129 | 0.045625 | 0.040975 | -0.0061685 | -0.020043 | 0.017666 | -0.012158 | 0.041199 | -0.036621 | 0.009155 | -0.068665 | -0.027466 | -0.086975 | -0.050354 | 0.10071 | 0.059509 | -0.009155 | 0.07782 | 0.13275 | 0.12817 | 0.10529 | 61.8713 | -62.1277 | -62.1597 | 61.8347 | 61.8118 | 61.7752 | -0.059509 | -0.09613 | 61.853 | -62.0316 | -62.0132 | 61.9949 | 61.9675 | 61.9904 | 0.11444 | 0.13733 | -0.036621 | -0.07782 | 0.14191 | 0.086975 | -0.045776 | 0.068664 | 61.8256 | 61.9217 | -62.0819 | -62.1002 | 61.7935 | 61.94 | 61.9034 | 61.9629
655.8125 | 124.2737 | -61.8805 | 62.0865 | 0.19169 | 0.0050788 | 0.0083045 | 0.038997 | 0.00030337 | 0.0020108 | -0.00079579 | 0.37233 | 0.042421 | 0.030294 | -0.023258 | -0.011498 | 0.014461 | -0.0014766 | 0.07782 | -0.036621 | 0.009155 | -0.064087 | -0.032043 | -0.07782 | -0.041199 | 0.10529 | 0.050354 | 0.004578 | 0.10986 | 0.14191 | 0.14648 | 0.11902 | 61.8896 | -62.1231 | -62.1506 | 61.8484 | 61.8393 | 61.8027 | -0.050354 | -0.086975 | 61.8851 | -62.0361 | -61.9766 | 62.0224 | 61.9995 | 62.027 | 0.11444 | 0.14191 | -0.041198 | -0.073242 | 0.13733 | 0.10529 | -0.045776 | 0.045776 | 61.8439 | 61.9308 | -62.0773 | -62.0819 | 61.8164 | 61.9904 | 61.9583 | 61.9858
656.8125 | 124.2691 | -61.8805 | 62.0682 | 0.25272 | 0.0082828 | 0.0061675 | 0.037928 | 0.0077804 | 0.011624 | -0.010409 | 0.235 | 0.034944 | 0.039907 | -0.028598 | -0.020043 | 0.017666 | -0.015362 | 0.054932 | -0.032043 | 0 | -0.091553 | -0.068665 | -0.10529 | -0.073242 | 0.11444 | 0.054932 | -0.013733 | 0.10071 | 0.15106 | 0.12817 | 0.10071 | 61.8805 | -62.1002 | -62.1597 | 61.8118 | 61.8073 | 61.7752 | -0.073242 | -0.10529 | 61.8668 | -62.0132 | -61.9675 | 62.0316 | 61.9812 | 62.0087 | 0.11444 | 0.14191 | -0.068665 | -0.091553 | 0.16479 | 0.11444 | -0.032043 | 0.068665 | 61.8484 | 61.9354 | -62.0682 | -62.0819 | 61.7889 | 61.9812 | 61.9354 | 61.9949
657.8125 | 124.2599 | -61.8896 | 62.0819 | 0.19169 | 0.011488 | 0.023258 | 0.026179 | 0.0088484 | -0.0086702 | -0.012545 | 0.235 | 0.046693 | 0.024954 | -0.016849 | -0.013634 | 0.016598 | 0.010272 | 0.027466 | -0.036621 | 0.004578 | -0.045776 | 0.009155 | -0.050354 | -0.045776 | 0.054932 | 0.054932 | -0.018311 | 0.07782 | 0.11902 | 0.10529 | 0.10071 | 61.8942 | -62.1185 | -62.1277 | 61.8988 | 61.8439 | 61.8393 | -0.050354 | -0.054932 | 61.8713 | -62.027 | -62.0041 | 62.0087 | 61.9904 | 61.9949 | 0.11902 | 0.1236 | 0.004577 | -0.050354 | 0.13733 | 0.096131 | -0.041199 | 0.073243 | 61.853 | 61.9446 | -62.0773 | -62.1002 | 61.8439 | 61.9675 | 61.9171 | 61.9446
658.8125 | 124.2783 | -61.8942 | 62.0819 | 0.023839 | 0.014692 | 0.012577 | 0.041133 | -0.0050366 | -0.024692 | -0.00079579 | 0.21974 | 0.040285 | 0.028158 | -0.011508 | -0.013634 | 0.015529 | 0.0027964 | -0.004578 | -0.036621 | -0.018311 | -0.018311 | 0.018311 | -0.041199 | -0.032043 | 0.041199 | 0.050354 | -0.004578 | 0.082397 | 0.10529 | 0.10986 | 0.086975 | 61.8759 | -62.1185 | -62.1002 | 61.9125 | 61.8622 | 61.853 | -0.013732 | -0.022888 | 61.8896 | -62.0316 | -61.9995 | 61.9995 | 61.9812 | 62.0041 | 0.091553 | 0.11444 | 0.036622 | 0 | 0.10986 | 0.086975 | -0.01831 | 0.054932 | 61.8576 | 61.9446 | -62.1002 | -62.0865 | 61.8759 | 61.9766 | 61.8896 | 61.9354
659.8125 | 124.2874 | -61.8759 | 62.0773 | 0.13065 | 0.0082828 | 0.0018955 | 0.041133 | 0.0024404 | -0.015079 | -0.0082728 | 0.25026 | 0.03708 | 0.024954 | 0.00024052 | -0.01043 | 0.011257 | -0.013226 | 0.027466 | -0.050354 | 0.004578 | -0.045776 | -0.022888 | -0.073242 | -0.059509 | 0.10071 | 0.045776 | -0.018311 | 0.10071 | 0.13733 | 0.13733 | 0.10071 | 61.8805 | -62.1277 | -62.1231 | 61.853 | 61.8164 | 61.8027 | -0.064087 | -0.07782 | 61.8576 | -62.0316 | -61.9766 | 62.0132 | 61.9766 | 62.0132 | 0.11902 | 0.15564 | -0.027466 | -0.050354 | 0.15564 | 0.11902 | -0.054932 | 0.064087 | 61.8256 | 61.9217 | -62.0728 | -62.0956 | 61.8301 | 61.9766 | 61.9034 | 61.9766
660.8125 | 124.2737 | -61.8851 | 62.0544 | 0.16117 | 0.011488 | 0.0029635 | 0.045405 | 0.021666 | -0.0097382 | -0.010409 | 0.235 | 0.041353 | 0.031362 | 0.0055815 | -0.01043 | 0.010189 | -0.017499 | 0.027466 | -0.045776 | -0.013733 | -0.050354 | -0.004578 | -0.068665 | -0.045776 | 0.068665 | 0.045776 | -0.013733 | 0.11444 | 0.11444 | 0.1236 | 0.10986 | 61.8713 | -62.1002 | -62.1048 | 61.8805 | 61.8393 | 61.8164 | -0.032043 | -0.054932 | 61.8713 | -62.0087 | -61.94 | 61.9995 | 61.9949 | 62.0087 | 0.1236 | 0.13733 | 0.009155 | -0.036621 | 0.12817 | 0.12817 | -0.032043 | 0.059509 | 61.8393 | 61.9308 | -62.0682 | -62.0682 | 61.8347 | 61.9995 | 61.9125 | 61.9537
661.8125 | 124.2737 | -61.8988 | 62.0865 | 0.13065 | 0.00080677 | 0.0050995 | 0.027247 | 0.0045764 | 0.016964 | 0.013089 | 0.21974 | 0.03174 | 0.029226 | -0.024326 | -0.018975 | 0.014461 | -0.0036126 | 0.045776 | -0.041199 | 0.009155 | -0.082397 | -0.054932 | -0.10071 | -0.068665 | 0.13733 | 0.032043 | 0 | 0.10071 | 0.14648 | 0.14191 | 0.10529 | 61.908 | -62.1277 | -62.1689 | 61.8439 | 61.8301 | 61.7981 | -0.07782 | -0.10986 | 61.8988 | -62.0544 | -61.9858 | 62.0453 | 62.0041 | 62.0407 | 0.10529 | 0.14191 | -0.064087 | -0.091552 | 0.14648 | 0.10071 | -0.050354 | 0.032043 | 61.8576 | 61.9308 | -62.0773 | -62.0865 | 61.8164 | 61.9995 | 61.9446 | 62.0361
662.8125 | 124.292 | -61.8896 | 62.0865 | 0.17643 | -0.0034662 | 0.0093725 | 0.021907 | -0.015718 | -0.0022622 | 0.0024082 | 0.26551 | 0.026399 | 0.048452 | -0.062778 | -0.023247 | 0.0091211 | -0.0036126 | 0.041199 | -0.036621 | 0 | -0.068665 | -0.032043 | -0.086975 | -0.054932 | 0.12817 | 0.064087 | -0.009155 | 0.12817 | 0.16479 | 0.14648 | 0.10986 | 61.8896 | -62.1231 | -62.1552 | 61.8576 | 61.8347 | 61.8027 | -0.054932 | -0.086975 | 61.8805 | -62.0224 | -61.9583 | 62.0544 | 61.9995 | 62.0361 | 0.11902 | 0.15564 | -0.032043 | -0.068665 | 0.17395 | 0.13733 | -0.036621 | 0.073242 | 61.853 | 61.9537 | -62.0865 | -62.0956 | 61.821 | 62.0178 | 61.9308 | 62.0178
663.8125 | 124.2874 | -61.8805 | 62.1048 | 0.16117 | 0.011488 | 0.0029635 | 0.040065 | 0.027006 | -0.02042 | -0.010409 | 0.26551 | 0.03708 | 0.026022 | -0.030734 | -0.013634 | 0.016598 | 0.0038644 | 0.027466 | -0.045776 | -0.009155 | -0.059509 | -0.027466 | -0.07782 | -0.050354 | 0.1236 | 0.045776 | -0.018311 | 0.11902 | 0.16479 | 0.14191 | 0.10071 | 61.8713 | -62.1506 | -62.1643 | 61.853 | 61.8301 | 61.8027 | -0.041199 | -0.068665 | 61.8622 | -62.059 | -61.9858 | 62.0453 | 61.9812 | 62.0224 | 0.11902 | 0.16022 | -0.018311 | -0.050354 | 0.18311 | 0.13733 | -0.036621 | 0.064087 | 61.8347 | 61.9263 | -62.114 | -62.1231 | 61.821 | 61.9995 | 61.908 | 62.0041
664.8125 | 124.2508 | -61.908 | 62.0819 | 0.11539 | 0.0061468 | 0.0083045 | 0.043269 | -0.0018326 | -0.0065342 | -0.0039998 | 0.14344 | 0.040285 | 0.037771 | 0.0098535 | -0.013634 | 0.017666 | 0.0092044 | 0 | -0.041199 | -0.004578 | -0.027466 | 0.027466 | -0.041199 | -0.032043 | 0.027466 | 0.068665 | -0.027466 | 0.059509 | 0.10071 | 0.10986 | 0.086975 | 61.9034 | -62.1231 | -62.1094 | 61.9354 | 61.8759 | 61.8668 | -0.027465 | -0.036621 | 61.8805 | -62.0132 | -62.0224 | 62.0087 | 61.9949 | 62.0178 | 0.11444 | 0.13733 | 0.032044 | -0.022888 | 0.12817 | 0.086975 | -0.036621 | 0.096131 | 61.8668 | 61.9766 | -62.0865 | -62.1094 | 61.8805 | 61.9675 | 61.908 | 61.9354
665.8125 | 124.2645 | -61.8896 | 62.0682 | 0.039098 | 0.012556 | 0.0040315 | 0.028315 | 0.00030337 | -0.00012524 | -0.010409 | 0.235 | 0.039216 | 0.038839 | -0.030734 | -0.020043 | 0.016598 | -0.0025446 | 0.009155 | -0.036621 | -0.018311 | -0.018311 | 0.036621 | -0.032043 | -0.013733 | 0.022888 | 0.064087 | -0.009155 | 0.073242 | 0.09613 | 0.086975 | 0.073242 | 61.8713 | -62.1048 | -62.0865 | 61.9263 | 61.8759 | 61.8576 | 0.004578 | -0.013732 | 61.8805 | -62.0041 | -61.9949 | 61.9858 | 61.9629 | 61.9766 | 0.082397 | 0.09613 | 0.054932 | 0 | 0.10528 | 0.082397 | -0.01831 | 0.073242 | 61.853 | 61.9537 | -62.0865 | -62.0773 | 61.8713 | 61.9629 | 61.8988 | 61.9125
666.8125 | 124.2737 | -61.9125 | 62.0682 | 0.11539 | 0.00080677 | -0.0045135 | 0.027247 | -0.0018326 | -0.0065342 | 0.0066812 | 0.17396 | 0.046693 | 0.024954 | -0.029666 | -0.020043 | 0.026211 | -0.0068176 | 0.050354 | -0.064087 | 0.013733 | -0.10071 | -0.082397 | -0.10071 | -0.07782 | 0.10071 | 0.041199 | 0.004578 | 0.091553 | 0.14648 | 0.1236 | 0.10071 | 61.9263 | -62.1323 | -62.1689 | 61.8301 | 61.8347 | 61.8118 | -0.091553 | -0.11444 | 61.9171 | -62.027 | -61.9766 | 62.059 | 62.0132 | 62.0361 | 0.09613 | 0.11902 | -0.09613 | -0.11444 | 0.14191 | 0.086975 | -0.07782 | 0.036621 | 61.8484 | 61.9537 | -62.0544 | -62.0636 | 61.8118 | 62.0041 | 61.9629 | 62.0132
667.8125 | 124.2599 | -61.9034 | 62.1002 | 0.28324 | 0.021101 | 0.0083045 | 0.032588 | 0.0045764 | 0.0041468 | -0.016818 | 0.1587 | 0.029603 | 0.018545 | -0.01044 | -0.016839 | 0.014461 | -0.021771 | 0.013733 | -0.041199 | -0.009155 | -0.041199 | 0 | -0.064087 | -0.045776 | 0.059509 | 0.059509 | -0.013733 | 0.086975 | 0.11902 | 0.12817 | 0.09613 | 61.8942 | -62.1414 | -62.1414 | 61.9034 | 61.8576 | 61.8393 | -0.036621 | -0.054932 | 61.8896 | -62.0407 | -62.0132 | 62.0224 | 61.9995 | 62.0316 | 0.10986 | 0.14191 | 0.009155 | -0.032044 | 0.13275 | 0.10071 | -0.032044 | 0.073242 | 61.8622 | 61.9629 | -62.1094 | -62.114 | 61.8622 | 61.9904 | 61.9171 | 61.9629
668.8125 | 124.2828 | -61.9034 | 62.0865 | 0.20695 | 0.0061468 | 0.0061675 | 0.03686 | -0.0029006 | -0.010807 | -0.020022 | 0.1587 | 0.03174 | 0.028158 | -0.023258 | -0.024315 | 0.0069851 | -0.01109 | 0.027466 | -0.045776 | 0 | -0.073242 | -0.059509 | -0.09613 | -0.064087 | 0.11902 | 0.068665 | -0.004578 | 0.11444 | 0.16479 | 0.16022 | 0.10986 | 61.9034 | -62.1323 | -62.1597 | 61.8439 | 61.8393 | 61.8073 | -0.064087 | -0.09613 | 61.8988 | -62.0178 | -61.972 | 62.0682 | 62.0132 | 62.0636 | 0.11444 | 0.16479 | -0.059509 | -0.073242 | 0.16937 | 0.11902 | -0.045776 | 0.073243 | 61.8576 | 61.972 | -62.0865 | -62.0911 | 61.8301 | 62.0178 | 61.9308 | 62.0224
669.8125 | 124.292 | -61.8668 | 62.0773 | 0.11539 | 0.011488 | 0.012577 | 0.038997 | 0.0035084 | 0.011624 | -0.0072048 | 0.28077 | 0.040285 | 0.024954 | -0.033939 | -0.006157 | 0.013393 | -0.0036126 | 0.045776 | -0.032043 | -0.013733 | -0.054932 | -0.018311 | -0.064087 | -0.068665 | 0.10986 | 0.050354 | -0.027466 | 0.11902 | 0.15564 | 0.15564 | 0.1236 | 61.853 | -62.1094 | -62.1323 | 61.8484 | 61.7981 | 61.8027 | -0.054932 | -0.050354 | 61.8393 | -62.027 | -61.9583 | 62.0224 | 61.9904 | 62.0224 | 0.15106 | 0.18311 | -0.004578 | -0.041199 | 0.18311 | 0.14649 | -0.01831 | 0.07782 | 61.8347 | 61.9171 | -62.0911 | -62.1048 | 61.8118 | 61.9858 | 61.9125 | 61.9766
670.8125 | 124.2783 | -61.8759 | 62.0865 | 0.13065 | 0.0082828 | 0.00082752 | 0.032588 | 0.0024404 | 0.0052148 | 0.010953 | 0.21974 | 0.028535 | 0.024954 | -0.02753 | -0.020043 | 0.012325 | -0.0068176 | 0.032043 | -0.041199 | -0.009155 | -0.045776 | -0.009155 | -0.086975 | -0.050354 | 0.091553 | 0.045776 | 0.004578 | 0.10986 | 0.14191 | 0.14191 | 0.10529 | 61.8668 | -62.1277 | -62.1323 | 61.8668 | 61.8256 | 61.7889 | -0.041199 | -0.07782 | 61.8805 | -62.0407 | -61.9766 | 62.0178 | 61.9812 | 62.0178 | 0.10071 | 0.13733 | 0 | -0.036621 | 0.13733 | 0.10529 | -0.032044 | 0.041198 | 61.8347 | 61.9217 | -62.0956 | -62.0819 | 61.8301 | 61.9858 | 61.908 | 61.9675
671.8125 | 124.2416 | -61.908 | 62.059 | 0.14591 | 0.0050788 | 0.00082752 | 0.033656 | 0.0077804 | -0.012943 | -0.02109 | 0.235 | 0.03174 | 0.034567 | 0.0098535 | -0.020043 | 0.013393 | -0.0068176 | 0.013733 | -0.036621 | 0 | -0.018311 | 0.032043 | -0.032043 | -0.018311 | 0.018311 | 0.068665 | -0.032043 | 0.059509 | 0.073242 | 0.10071 | 0.082397 | 61.908 | -62.0956 | -62.0773 | 61.94 | 61.8896 | 61.8759 | -0.018311 | -0.032043 | 61.8759 | -61.9904 | -61.9995 | 61.9812 | 61.9904 | 62.0087 | 0.11444 | 0.13275 | 0.032043 | -0.018311 | 0.10529 | 0.091552 | -0.036621 | 0.10071 | 61.8713 | 61.9766 | -62.059 | -62.0911 | 61.8896 | 61.9675 | 61.9217 | 61.9263
672.8125 | 124.1821 | -61.9308 | 62.1506 | 0.2222 | 0.0072148 | 0.011509 | 0.025111 | -0.0082416 | -0.0097382 | -0.022158 | -0.0091433 | 0.042421 | 0.037771 | -0.0072365 | -0.013634 | 0.026211 | -0.017499 | -0.032043 | -0.022888 | -0.045776 | 0.082397 | 0.1236 | 0.050354 | 0.064087 | -0.050354 | 0.10071 | -0.054932 | -0.009155 | 0.018311 | 0 | 0.013733 | 61.8851 | -62.1735 | -62.0682 | 62.0544 | 61.9949 | 61.9812 | 0.10986 | 0.09613 | 61.8759 | -62.0499 | -62.1597 | 61.9492 | 61.9446 | 61.9308 | 0.068665 | 0.054932 | 0.16937 | 0.12817 | 0.073243 | 0.045777 | 0.022888 | 0.15564 | 61.908 | 62.0316 | -62.1963 | -62.2055 | 62.0132 | 61.9217 | 61.8988 | 61.8805
673.8125 | 124.2645 | -61.8805 | 62.0728 | 0.2222 | 0.01042 | -0.00024048 | 0.024043 | -0.011446 | 0.0052148 | 0.0013402 | 0.12819 | 0.039216 | 0.030294 | 0.0055815 | -0.008294 | 0.010189 | -0.0025446 | 0.009155 | -0.064087 | 0.004578 | -0.022888 | 0.013733 | -0.054932 | -0.032043 | 0.036621 | 0.054932 | -0.022888 | 0.073242 | 0.11444 | 0.11444 | 0.10071 | 61.8851 | -62.1368 | -62.0956 | 61.8942 | 61.8484 | 61.8256 | -0.036621 | -0.05951 | 61.8576 | -62.0178 | -61.9995 | 61.9949 | 61.9812 | 61.9949 | 0.1236 | 0.13733 | 0.009155 | -0.027466 | 0.13733 | 0.09613 | -0.068665 | 0.07782 | 61.8164 | 61.9354 | -62.0682 | -62.0956 | 61.8576 | 61.9537 | 61.8896 | 61.9171
674.8125 | 124.2554 | -61.9263 | 62.0865 | 0.26798 | 0.0029428 | 0.0093725 | 0.030452 | -0.0029006 | -0.012943 | -0.00079579 | 0.28077 | 0.047761 | 0.032431 | -0.015781 | -0.01043 | 0.02087 | -0.0036126 | 0.018311 | -0.045776 | -0.004578 | -0.013733 | 0.027466 | -0.059509 | -0.036621 | 0.041199 | 0.045776 | -0.018311 | 0.082397 | 0.10986 | 0.09613 | 0.073242 | 61.9217 | -62.1323 | -62.1002 | 61.9537 | 61.8896 | 61.8668 | -0.032043 | -0.054931 | 61.908 | -62.0407 | -62.0041 | 62.0361 | 61.9995 | 62.0224 | 0.091553 | 0.11444 | 0.032044 | -0.009155 | 0.12817 | 0.10071 | -0.041198 | 0.064087 | 61.8805 | 61.972 | -62.0911 | -62.1048 | 61.9125 | 62.0087 | 61.9446 | 61.9675
675.8125 | 124.292 | -61.9171 | 62.0773 | 0.14591 | -0.0023982 | 0.020054 | 0.034724 | -0.0050366 | 0.0084198 | -0.0061368 | 0.28077 | 0.040285 | 0.026022 | 0.034421 | -0.009362 | 0.0080531 | 0.015613 | 0.022888 | -0.036621 | -0.009155 | -0.045776 | -0.013733 | -0.082397 | -0.054932 | 0.09613 | 0.050354 | -0.009155 | 0.11444 | 0.15106 | 0.13733 | 0.11444 | 61.908 | -62.114 | -62.1231 | 61.9034 | 61.8622 | 61.8347 | -0.045777 | -0.073242 | 61.908 | -62.027 | -61.9629 | 62.0682 | 62.0316 | 62.0544 | 0.1236 | 0.14648 | -0.004578 | -0.036621 | 0.16022 | 0.1236 | -0.027466 | 0.059509 | 61.8805 | 61.9675 | -62.0865 | -62.0865 | 61.8713 | 62.0316 | 61.94 | 62.0132
676.8125 | 124.2783 | -61.9034 | 62.0499 | 0.14591 | 0.011488 | 0.0093725 | 0.030452 | 0.021666 | 0.0020108 | 0.0056132 | 0.17396 | 0.03708 | 0.034567 | -0.042484 | -0.012566 | 0.0080531 | -0.027112 | 0.013733 | -0.032043 | -0.022888 | -0.059509 | 0.009155 | -0.068665 | -0.045776 | 0.07782 | 0.045776 | -0.009155 | 0.10529 | 0.1236 | 0.1236 | 0.09613 | 61.8805 | -62.0819 | -62.1094 | 61.9125 | 61.8576 | 61.8347 | -0.022888 | -0.045777 | 61.8942 | -62.0041 | -61.9446 | 62.027 | 61.9995 | 62.027 | 0.10528 | 0.13275 | 0.032043 | -0.036621 | 0.13275 | 0.11444 | -0.009155 | 0.054931 | 61.8713 | 61.9492 | -62.0728 | -62.059 | 61.8439 | 62.0087 | 61.9171 | 61.9812
677.8125 | 124.2828 | -61.9171 | 62.059 | 0.25272 | 0.016828 | 0.010441 | 0.038997 | -0.013582 | -0.015079 | -0.010409 | 0.12819 | 0.038148 | 0.026022 | -0.030734 | -0.016839 | 0.012325 | -0.0089536 | 0 | -0.036621 | 0 | -0.050354 | 0.018311 | -0.064087 | -0.041199 | 0.059509 | 0.041199 | -0.013733 | 0.082397 | 0.11444 | 0.10986 | 0.09613 | 61.9171 | -62.0956 | -62.1094 | 61.9354 | 61.8759 | 61.853 | -0.041199 | -0.064087 | 61.9034 | -62.0178 | -61.9766 | 62.0316 | 62.0132 | 62.027 | 0.10986 | 0.1236 | 0.018311 | -0.050354 | 0.12817 | 0.09613 | -0.036621 | 0.054932 | 61.8805 | 61.9583 | -62.059 | -62.0728 | 61.8668 | 61.9995 | 61.9171 | 61.9766
678.8125 | 124.2371 | -61.9354 | 62.0911 | 0.084874 | 0.0093518 | -0.0023775 | 0.034724 | 0.0013714 | 0.0020108 | 0.0013402 | 0.11293 | 0.030671 | 0.033499 | 0.00024052 | -0.01577 | 0.0037801 | 0.019885 | -0.013733 | -0.050354 | -0.018311 | -0.009155 | 0.045776 | -0.032043 | -0.009155 | 0.004578 | 0.050354 | -0.041199 | 0.045776 | 0.064087 | 0.068665 | 0.050354 | 61.9171 | -62.1414 | -62.1002 | 61.9812 | 61.9263 | 61.9034 | 0.009156 | -0.013732 | 61.8942 | -62.0407 | -62.0453 | 61.9995 | 61.9858 | 62.0041 | 0.091553 | 0.10986 | 0.064087 | 0.009156 | 0.10529 | 0.086975 | -0.032043 | 0.091553 | 61.8851 | 61.9858 | -62.1094 | -62.1323 | 61.9263 | 61.9812 | 61.9217 | 61.94
679.8125 | 124.2279 | -61.9217 | 62.0728 | 0.19169 | 0.0050788 | 0.011509 | 0.030452 | 0.022734 | -0.012943 | -0.014682 | 0.18922 | 0.045625 | 0.030294 | 0.0087855 | -0.006157 | 0.029415 | 0.0006594 | -0.013733 | -0.036621 | 0.009155 | -0.013733 | 0.032043 | -0.036621 | -0.013733 | 0.009155 | 0.059509 | -0.009155 | 0.045776 | 0.064087 | 0.054932 | 0.064087 | 61.9308 | -62.1094 | -62.0865 | 61.9537 | 61.908 | 61.8851 | -0.022888 | -0.045776 | 61.9125 | -62.0132 | -62.027 | 61.9858 | 61.9858 | 61.9766 | 0.073242 | 0.064087 | 0.022888 | -0.022888 | 0.073242 | 0.054931 | -0.045776 | 0.068664 | 61.8851 | 61.9812 | -62.0636 | -62.0819 | 61.908 | 61.9675 | 61.908 | 61.9308
680.8125 | 124.2462 | -61.8988 | 62.0956 | 0.11539 | 0.0061468 | 0.0040315 | 0.037928 | 0.00030337 | 0.0020108 | 0.0045452 | 0.18922 | 0.027467 | 0.030294 | -0.0029635 | -0.008294 | 0.015529 | -0.0068176 | 0 | -0.032043 | -0.009155 | -0.004578 | 0.022888 | -0.050354 | -0.027466 | 0.032043 | 0.064087 | -0.022888 | 0.059509 | 0.10071 | 0.11444 | 0.082397 | 61.8896 | -62.1277 | -62.1002 | 61.9217 | 61.8713 | 61.8484 | -0.018311 | -0.041199 | 61.8759 | -62.0316 | -62.0361 | 61.9995 | 61.9812 | 62.0132 | 0.10528 | 0.13733 | 0.032043 | 0.004577 | 0.1236 | 0.082397 | -0.022888 | 0.086975 | 61.8668 | 61.9629 | -62.1048 | -62.1185 | 61.8942 | 61.9583 | 61.8988 | 61.9308
681.8125 | 124.2599 | -61.9217 | 62.059 | 0.19169 | 0.014692 | 0.0029635 | 0.03152 | -0.00076463 | -0.0076022 | 0.0077492 | 0.18922 | 0.036012 | 0.036703 | -0.016849 | -0.023247 | 0.011257 | -0.012158 | 0 | -0.050354 | -0.018311 | -0.013733 | 0.050354 | -0.041199 | -0.018311 | 0.009155 | 0.073242 | -0.022888 | 0.059509 | 0.086975 | 0.091553 | 0.064087 | 61.9034 | -62.1094 | -62.0728 | 61.972 | 61.9034 | 61.8805 | 0 | -0.022888 | 61.8988 | -61.9858 | -61.9995 | 62.0087 | 61.9858 | 62.0132 | 0.086975 | 0.11444 | 0.068665 | 0.004578 | 0.10986 | 0.082397 | -0.032043 | 0.09613 | 61.8713 | 61.9949 | -62.0773 | -62.0819 | 61.908 | 61.9812 | 61.9217 | 61.9308
682.8125 | 124.2737 | -61.8759 | 62.0819 | 0.31376 | 0.01042 | 0.0029635 | 0.027247 | -0.0061046 | 0.014828 | 0.010953 | 0.26551 | 0.038148 | 0.040975 | -0.0040315 | -0.018975 | 0.017666 | 0.0017274 | 0.004578 | -0.036621 | -0.022888 | -0.036621 | 0.004578 | -0.073242 | -0.050354 | 0.054932 | 0.064087 | -0.018311 | 0.073242 | 0.11902 | 0.13275 | 0.091553 | 61.853 | -62.1185 | -62.1185 | 61.8805 | 61.8256 | 61.8027 | -0.027466 | -0.050354 | 61.8576 | -62.0178 | -62.0087 | 61.9949 | 61.9675 | 62.0087 | 0.10986 | 0.15106 | 0.027466 | -0.013733 | 0.13733 | 0.091553 | -0.013733 | 0.082398 | 61.8393 | 61.94 | -62.1048 | -62.1002 | 61.8393 | 61.9492 | 61.8805 | 61.9308
683.8125 | 124.2737 | -61.9034 | 62.059 | 0.084874 | 0.0061468 | 0.020054 | 0.044337 | -0.013582 | 0.0030788 | -0.0082728 | 0.12819 | 0.032808 | 0.031362 | -0.016849 | 0.001319 | 0.023006 | -0.012158 | 0 | -0.036621 | 0.004578 | -0.022888 | 0.004578 | -0.045776 | -0.032043 | 0.045776 | 0.054932 | -0.018311 | 0.07782 | 0.11902 | 0.10986 | 0.086975 | 61.908 | -62.0956 | -62.0819 | 61.908 | 61.8713 | 61.8576 | -0.036621 | -0.050354 | 61.8851 | -62.0041 | -61.9812 | 62.0224 | 61.9904 | 62.0132 | 0.10529 | 0.12817 | 0 | -0.027466 | 0.13733 | 0.096131 | -0.041199 | 0.073243 | 61.8668 | 61.9583 | -62.0544 | -62.0773 | 61.8805 | 61.9812 | 61.9034 | 61.9492
684.8125 | 124.2691 | -61.908 | 62.1094 | 0.17643 | 0.0029428 | 0.0083045 | 0.040065 | -0.013582 | -0.0065342 | -0.0029318 | 0.11293 | 0.042421 | 0.031362 | 0.017331 | -0.022179 | 0.017666 | -0.01109 | 0.018311 | -0.036621 | 0.004578 | -0.018311 | 0.018311 | -0.045776 | -0.013733 | 0.032043 | 0.064087 | -0.018311 | 0.073242 | 0.086975 | 0.09613 | 0.10071 | 61.9125 | -62.146 | -62.1277 | 61.9263 | 61.8942 | 61.8622 | -0.018311 | -0.050354 | 61.8896 | -62.0453 | -62.0361 | 61.9949 | 62.0087 | 62.0041 | 0.11902 | 0.11444 | 0.013733 | -0.022889 | 0.10529 | 0.091553 | -0.041199 | 0.082398 | 61.8713 | 61.972 | -62.1048 | -62.1277 | 61.8896 | 61.9812 | 61.9263 | 61.94
685.8125 | 124.2462 | -61.94 | 62.0361 | 0.11539 | 0.012556 | 0.015781 | 0.026179 | -0.0018326 | 0.0041468 | 0.0024082 | 0.036633 | 0.036012 | 0.026022 | -0.022189 | -0.016839 | 0.0016441 | -0.014294 | -0.018311 | -0.032043 | 0 | -0.009155 | 0.032043 | -0.022888 | -0.036621 | -0.004578 | 0.050354 | -0.022888 | 0.045776 | 0.064087 | 0.064087 | 0.045776 | 61.94 | -62.0682 | -62.0453 | 61.972 | 61.9034 | 61.9171 | -0.036621 | -0.022888 | 61.9171 | -61.9858 | -61.9904 | 62.0041 | 61.9858 | 62.0041 | 0.068664 | 0.086975 | 0.032043 | -0.009155 | 0.086975 | 0.068664 | -0.032043 | 0.073242 | 61.908 | 61.9904 | -62.0361 | -62.059 | 61.9308 | 61.9858 | 61.9217 | 61.9354
686.8125 | 124.2599 | -61.9034 | 62.0865 | 0.16117 | 0.0050788 | 0.0040315 | 0.024043 | -0.0093096 | 0.018033 | -0.0093408 | 0.14344 | 0.039216 | 0.039907 | 0.00024052 | -0.012566 | 0.024074 | -0.016431 | -0.018311 | -0.045776 | -0.009155 | -0.004578 | 0.032043 | -0.036621 | -0.027466 | 0.013733 | 0.050354 | -0.036621 | 0.050354 | 0.086975 | 0.07782 | 0.082397 | 61.8942 | -62.1323 | -62.0911 | 61.9354 | 61.8759 | 61.8668 | -0.018311 | -0.027466 | 61.8668 | -62.0361 | -62.0361 | 61.9904 | 61.9858 | 61.9812 | 0.11902 | 0.11444 | 0.041198 | 0.004577 | 0.1236 | 0.086975 | -0.036621 | 0.086975 | 61.8576 | 61.9537 | -62.0956 | -62.1231 | 61.8988 | 61.9537 | 61.8851 | 61.9171
687.8125 | 124.2462 | -61.9308 | 62.0728 | 0.16117 | 0.012556 | 0.0083045 | 0.041133 | -0.0061046 | 0.022305 | -0.0029318 | 0.14344 | 0.036012 | 0.030294 | 0.021603 | -0.018975 | 0.0091211 | -0.0025446 | 0.004578 | -0.041199 | 0 | -0.009155 | 0.041199 | -0.041199 | -0.018311 | 0.004578 | 0.073242 | -0.027466 | 0.045776 | 0.086975 | 0.073242 | 0.068665 | 61.9308 | -62.114 | -62.0819 | 61.972 | 61.9125 | 61.8896 | -0.018311 | -0.041199 | 61.9034 | -61.9995 | -62.027 | 62.0178 | 61.9995 | 62.0041 | 0.096131 | 0.10071 | 0.041199 | -0.009155 | 0.11444 | 0.073242 | -0.041199 | 0.10071 | 61.8896 | 62.0041 | -62.0728 | -62.1002 | 61.9217 | 61.9766 | 61.9354 | 61.9354
688.8125 | 124.2371 | -61.9308 | 62.0865 | 0.17643 | 0.012556 | 0.0083045 | 0.033656 | -0.013582 | -0.016147 | -0.0039998 | 0.1587 | 0.036012 | 0.02709 | 0.0077175 | -0.012566 | 0.016598 | -0.0078856 | -0.013733 | -0.041199 | -0.009155 | -0.013733 | 0.045776 | -0.032043 | -0.022888 | -0.004578 | 0.073242 | -0.022888 | 0.045776 | 0.064087 | 0.054932 | 0.064087 | 61.9217 | -62.1277 | -62.1002 | 61.9766 | 61.908 | 61.8988 | -0.013733 | -0.022888 | 61.908 | -62.0132 | -62.0407 | 61.9949 | 61.9949 | 61.9858 | 0.086975 | 0.07782 | 0.054931 | -0.004578 | 0.086975 | 0.068664 | -0.032044 | 0.09613 | 61.8896 | 62.0041 | -62.0956 | -62.1094 | 61.9171 | 61.9766 | 61.9171 | 61.9263
689.8125 | 124.2645 | -61.8896 | 62.0911 | 0.28324 | 0.013624 | 0.017918 | 0.042201 | -0.0039686 | -0.0054662 | -0.018954 | 0.12819 | 0.043489 | 0.02709 | -0.015781 | -0.016839 | 0.015529 | -0.024975 | -0.009155 | -0.041199 | -0.018311 | -0.027466 | 0.018311 | -0.041199 | -0.022888 | 0.036621 | 0.036621 | -0.009155 | 0.068665 | 0.091553 | 0.10071 | 0.09613 | 61.8713 | -62.1323 | -62.1185 | 61.908 | 61.8668 | 61.8484 | -0.004577 | -0.022888 | 61.8805 | -62.0544 | -62.0224 | 61.9812 | 61.9858 | 61.9904 | 0.10528 | 0.10986 | 0.036622 | -0.009155 | 0.10071 | 0.07782 | -0.022888 | 0.045776 | 61.8484 | 61.9263 | -62.1094 | -62.1002 | 61.8622 | 61.9583 | 61.8805 | 61.9263
690.8125 | 124.2691 | -61.9263 | 62.0682 | 0.13065 | 0.0018748 | 0.0029635 | 0.032588 | -0.0039686 | -0.0033302 | 0.0045452 | 0.18922 | 0.047761 | 0.020681 | 0.01199 | -0.014702 | 0.019802 | -0.0004086 | 0 | -0.050354 | 0 | 0 | 0.036621 | -0.050354 | -0.018311 | 0.022888 | 0.050354 | -0.022888 | 0.064087 | 0.09613 | 0.091553 | 0.086975 | 61.9263 | -62.1185 | -62.0682 | 61.9629 | 61.908 | 61.8759 | -0.018311 | -0.050354 | 61.9034 | -62.0178 | -62.0041 | 62.0224 | 62.0132 | 62.0178 | 0.10986 | 0.11444 | 0.036621 | 0 | 0.11902 | 0.086975 | -0.050354 | 0.073242 | 61.8759 | 61.9766 | -62.0682 | -62.0911 | 61.9263 | 61.9904 | 61.9263 | 61.9492
691.8125 | 124.2371 | -61.9125 | 62.1002 | 0.14591 | 0.017896 | 0.013645 | 0.029384 | 0.0013714 | 0.0030788 | -0.0050688 | 0.29603 | 0.03174 | 0.028158 | -0.021121 | -0.021111 | 0.023006 | -0.0004086 | 0.013733 | -0.036621 | -0.022888 | -0.013733 | 0.032043 | -0.036621 | -0.004578 | 0.018311 | 0.054932 | -0.009155 | 0.064087 | 0.059509 | 0.068665 | 0.064087 | 61.8896 | -62.1368 | -62.114 | 61.9446 | 61.908 | 61.8759 | 0.01831 | -0.013733 | 61.9034 | -62.0453 | -62.0361 | 61.972 | 61.9766 | 61.9812 | 0.073242 | 0.07782 | 0.054931 | 0.009155 | 0.068664 | 0.073242 | -0.013733 | 0.064087 | 61.8759 | 61.9675 | -62.1231 | -62.1094 | 61.8988 | 61.9766 | 61.9263 | 61.9308
692.8125 | 124.2371 | -61.9263 | 62.1185 | 0.039098 | 0.012556 | 0.012577 | 0.026179 | 0.010984 | -0.0033302 | -0.011477 | 0.036633 | 0.045625 | 0.023886 | -0.059573 | -0.023247 | 0.02087 | -0.0025446 | -0.004578 | -0.059509 | -0.018311 | -0.013733 | 0.018311 | -0.032043 | -0.027466 | 0.027466 | 0.059509 | -0.018311 | 0.059509 | 0.068665 | 0.054932 | 0.064087 | 61.908 | -62.178 | -62.1323 | 61.9446 | 61.8988 | 61.8942 | -0.009155 | -0.013732 | 61.908 | -62.059 | -62.059 | 61.9949 | 61.9904 | 61.9812 | 0.082398 | 0.073243 | 0.036622 | 0.004578 | 0.086976 | 0.07782 | -0.041198 | 0.07782 | 61.8668 | 61.9858 | -62.1368 | -62.1368 | 61.9125 | 61.9858 | 61.9217 | 61.9537
693.8125 | 124.2508 | -61.9217 | 62.0773 | 0.11539 | 0.0050788 | 0.0072355 | 0.030452 | 0.0056444 | -0.0054662 | -0.0029318 | 0.12819 | 0.038148 | 0.033499 | -0.0051005 | 0.00025105 | 0.023006 | -0.019635 | -0.022888 | -0.045776 | -0.018311 | -0.018311 | 0.036621 | -0.041199 | -0.018311 | 0 | 0.064087 | -0.027466 | 0.036621 | 0.064087 | 0.073242 | 0.068665 | 61.9034 | -62.1231 | -62.0956 | 61.9583 | 61.9034 | 61.8805 | 0 | -0.022888 | 61.8942 | -62.0132 | -62.0407 | 61.9858 | 61.9904 | 61.9949 | 0.096131 | 0.10071 | 0.054932 | 0 | 0.091553 | 0.064087 | -0.027465 | 0.091553 | 61.8759 | 61.9858 | -62.0956 | -62.1048 | 61.9034 | 61.9583 | 61.8988 | 61.9217
694.8125 | 124.2279 | -61.9263 | 62.0682 | 0.10013 | 0.027509 | 0.0029635 | 0.030452 | 0.0045764 | -0.0065342 | 0.012021 | 0.067151 | 0.043489 | 0.040975 | -0.013645 | -0.023247 | 0.011257 | 0.0027964 | -0.009155 | -0.036621 | -0.013733 | -0.022888 | 0.045776 | -0.036621 | -0.022888 | 0.004578 | 0.068665 | -0.018311 | 0.050354 | 0.054932 | 0.064087 | 0.068665 | 61.9125 | -62.1048 | -62.0911 | 61.972 | 61.9034 | 61.8896 | -0.009155 | -0.022888 | 61.908 | -61.9995 | -62.0178 | 61.9812 | 61.9949 | 61.9904 | 0.086976 | 0.082398 | 0.059509 | -0.009155 | 0.073243 | 0.068665 | -0.022888 | 0.086976 | 61.8896 | 61.9949 | -62.0819 | -62.0865 | 61.9034 | 61.9766 | 61.9171 | 61.9308
695.8125 | 124.2691 | -61.908 | 62.0911 | 0.17643 | 0.0093518 | 0.0083045 | 0.034724 | 0.0035084 | -0.0033302 | 0.0045452 | 0.097669 | 0.044557 | 0.020681 | 0.0087855 | -0.006157 | 0.019802 | -0.0089536 | 0 | -0.036621 | -0.022888 | -0.022888 | 0.022888 | -0.036621 | -0.027466 | 0 | 0.050354 | -0.009155 | 0.068665 | 0.086975 | 0.10071 | 0.086975 | 61.8851 | -62.1277 | -62.114 | 61.9308 | 61.8805 | 61.8713 | -0.004578 | -0.013733 | 61.8988 | -62.0407 | -62.0224 | 61.9949 | 61.9949 | 62.0087 | 0.09613 | 0.10986 | 0.045776 | 0 | 0.09613 | 0.07782 | -0.013733 | 0.059509 | 61.8713 | 61.9583 | -62.114 | -62.1002 | 61.8851 | 61.9766 | 61.908 | 61.908
696.8125 | 124.2325 | -61.9263 | 62.0728 | 0.20695 | -0.0013302 | 0.0050995 | 0.027247 | 0.0045764 | -0.016147 | 0.0098852 | 0.17396 | 0.038148 | 0.011068 | -0.014713 | -0.013634 | 0.017666 | -0.0004086 | 0.009155 | -0.041199 | -0.009155 | -0.018311 | 0.032043 | -0.032043 | -0.022888 | 0.004578 | 0.059509 | -0.018311 | 0.064087 | 0.073242 | 0.073242 | 0.073242 | 61.9171 | -62.114 | -62.0911 | 61.9583 | 61.9034 | 61.8942 | -0.013733 | -0.022888 | 61.908 | -62.0132 | -62.0087 | 61.9995 | 61.9995 | 61.9995 | 0.091553 | 0.091553 | 0.041198 | -0.009156 | 0.091553 | 0.082398 | -0.032044 | 0.07782 | 61.8851 | 61.9858 | -62.0819 | -62.0911 | 61.908 | 61.9904 | 61.9354 | 61.9308
697.8125 | 124.2508 | -61.9263 | 62.0682 | 0.16117 | 0.011488 | 0.0018955 | 0.038997 | -0.0029006 | -0.00012524 | -0.0093408 | 0.036633 | 0.039216 | 0.016409 | -0.0051005 | -0.014702 | 0.017666 | -0.015362 | 0 | -0.045776 | -0.004578 | -0.013733 | 0.045776 | -0.036621 | -0.018311 | 0 | 0.064087 | -0.018311 | 0.045776 | 0.068665 | 0.064087 | 0.064087 | 61.9217 | -62.114 | -62.0819 | 61.972 | 61.908 | 61.8896 | -0.013733 | -0.032043 | 61.908 | -62.0041 | -62.0224 | 61.9949 | 61.9904 | 61.9904 | 0.082398 | 0.082398 | 0.050354 | -0.009155 | 0.086976 | 0.064087 | -0.041198 | 0.082398 | 61.8805 | 61.9904 | -62.0728 | -62.0865 | 61.9125 | 61.972 | 61.9263 | 61.9263
698.8125 | 124.2462 | -61.9217 | 62.0865 | 0.11539 | 0.011488 | 0.017918 | 0.037928 | -0.00076463 | -0.021488 | 0.00027221 | -0.0091433 | 0.032808 | 0.036703 | -0.014713 | -0.01577 | 0.025143 | 0.0092044 | 0 | -0.050354 | -0.004578 | -0.059509 | 0.004578 | -0.050354 | -0.018311 | 0.045776 | 0.050354 | -0.022888 | 0.07782 | 0.050354 | 0.064087 | 0.059509 | 61.9171 | -62.1368 | -62.146 | 61.9263 | 61.9034 | 61.8713 | -0.013733 | -0.045776 | 61.8988 | -62.0361 | -62.0087 | 61.972 | 61.9812 | 61.9858 | 0.082397 | 0.086975 | 0.009156 | -0.054931 | 0.073242 | 0.10071 | -0.045776 | 0.073242 | 61.8713 | 61.972 | -62.0911 | -62.1094 | 61.8622 | 61.9995 | 61.9217 | 61.9675
699.8125 | 124.2416 | -61.9354 | 62.059 | 0.10013 | 0.021101 | 0.01685 | 0.040065 | 0.0067124 | -0.0043982 | 0.0034762 | -0.03966 | 0.046693 | 0.018545 | -0.0051005 | -0.014702 | 0.02087 | -0.019635 | 0.022888 | -0.050354 | -0.009155 | -0.045776 | -0.027466 | -0.059509 | -0.064087 | 0.059509 | 0.050354 | -0.004578 | 0.07782 | 0.068665 | 0.073242 | 0.064087 | 61.9263 | -62.1094 | -62.1048 | 61.908 | 61.8713 | 61.8759 | -0.054932 | -0.050354 | 61.9308 | -62.0087 | -61.9812 | 62.0041 | 61.9995 | 62.0087 | 0.068665 | 0.07782 | -0.018311 | -0.036621 | 0.073243 | 0.082398 | -0.041199 | 0.054932 | 61.8851 | 61.9858 | -62.0682 | -62.0636 | 61.8896 | 62.0132 | 61.9583 | 61.9949
700.8125 | 124.2508 | -61.9263 | 62.0865 | 0.13065 | 0.012556 | 0.0029635 | 0.030452 | -0.0082416 | -0.0022622 | -0.0029318 | 0.067151 | 0.030671 | 0.022818 | -0.017917 | -0.008294 | 0.014461 | -0.0057486 | -0.018311 | -0.050354 | -0.004578 | -0.018311 | 0.022888 | -0.036621 | -0.027466 | -0.009155 | 0.036621 | -0.032043 | 0.050354 | 0.068665 | 0.073242 | 0.054932 | 61.9217 | -62.1368 | -62.1048 | 61.9492 | 61.8988 | 61.8896 | -0.022888 | -0.032043 | 61.8942 | -62.0499 | -62.0361 | 61.9949 | 61.9812 | 61.9995 | 0.086975 | 0.10529 | 0.027466 | -0.013733 | 0.10071 | 0.082397 | -0.045776 | 0.068664 | 61.8759 | 61.9629 | -62.0911 | -62.1185 | 61.908 | 61.9766 | 61.908 | 61.9171
701.8125 | 124.2416 | -61.9034 | 62.0773 | 0.13065 | 0.020033 | 0.0072355 | 0.037928 | 0.0013714 | -0.0076022 | -0.0018638 | 0.097669 | 0.041353 | 0.020681 | -0.0018955 | -0.012566 | 0.018734 | -0.0078856 | 0.009155 | -0.050354 | -0.018311 | -0.027466 | 0.009155 | -0.041199 | -0.027466 | 0.018311 | 0.054932 | -0.004578 | 0.054932 | 0.064087 | 0.068665 | 0.059509 | 61.8851 | -62.1277 | -62.1048 | 61.9125 | 61.8759 | 61.8622 | -0.009155 | -0.022888 | 61.8988 | -62.0224 | -62.0224 | 61.9675 | 61.9629 | 61.972 | 0.064087 | 0.073243 | 0.027466 | -0.009155 | 0.068665 | 0.05951 | -0.032043 | 0.05951 | 61.853 | 61.9583 | -62.0956 | -62.0819 | 61.8759 | 61.9583 | 61.9125 | 61.9217
702.8125 | 124.2599 | -61.9171 | 62.0911 | 0.17643 | 0.0040108 | 0.013645 | 0.032588 | -0.0071726 | 0.0062828 | -0.00079579 | 0.14344 | 0.050966 | 0.017477 | 0.00024052 | -0.007226 | 0.017666 | 0.0006594 | -0.004578 | -0.036621 | -0.009155 | -0.027466 | 0.041199 | -0.032043 | -0.018311 | 0.009155 | 0.041199 | -0.041199 | 0.041199 | 0.059509 | 0.054932 | 0.073242 | 61.908 | -62.1277 | -62.1185 | 61.9583 | 61.8988 | 61.8851 | -0.009156 | -0.022888 | 61.8759 | -62.0499 | -62.0499 | 61.9766 | 61.9904 | 61.972 | 0.11444 | 0.096131 | 0.050354 | -0.018311 | 0.10071 | 0.082398 | -0.027466 | 0.082398 | 61.8805 | 61.9583 | -62.1002 | -62.1323 | 61.8896 | 61.9583 | 61.9125 | 61.9263
703.8125 | 124.2691 | -61.9263 | 62.059 | 0.11539 | 0.01576 | 0.0083045 | 0.035792 | -0.0029006 | 0.012692 | 0.0066812 | 0.08241 | 0.041353 | 0.030294 | 0.0098535 | -0.01577 | 0.014461 | 0.0081364 | -0.013733 | -0.064087 | -0.022888 | -0.022888 | 0.022888 | -0.032043 | -0.013733 | 0.009155 | 0.068665 | -0.022888 | 0.045776 | 0.068665 | 0.054932 | 0.068665 | 61.9034 | -62.1231 | -62.0819 | 61.9492 | 61.9125 | 61.8942 | 0.009155 | -0.009155 | 61.9034 | -61.9904 | -62.0132 | 61.9949 | 61.9949 | 61.9812 | 0.091553 | 0.07782 | 0.045776 | 0 | 0.091553 | 0.068664 | -0.041199 | 0.091553 | 61.8622 | 61.9949 | -62.0819 | -62.0819 | 61.9034 | 61.972 | 61.9125 | 61.9354
704.8125 | 124.2599 | -61.94 | 62.0865 | 0.054357 | 0.012556 | 0.015781 | 0.035792 | 0.022734 | -0.0043982 | -0.010409 | 0.036633 | 0.034944 | 0.032431 | -0.045688 | -0.013634 | 0.026211 | -0.0068176 | 0.009155 | -0.050354 | -0.004578 | -0.041199 | 0.004578 | -0.032043 | -0.032043 | 0.027466 | 0.059509 | -0.022888 | 0.041199 | 0.054932 | 0.064087 | 0.073242 | 61.9354 | -62.1368 | -62.1277 | 61.9446 | 61.908 | 61.908 | -0.027465 | -0.027465 | 61.9171 | -62.027 | -62.0453 | 61.9949 | 62.0132 | 62.0041 | 0.09613 | 0.086975 | 0.009156 | -0.036621 | 0.07782 | 0.064087 | -0.045776 | 0.082397 | 61.8896 | 61.9995 | -62.0911 | -62.1094 | 61.8988 | 61.9812 | 61.9492 | 61.9675
705.8125 | 124.2966 | -61.9171 | 62.0682 | 0.084874 | 0.018965 | 0.013645 | 0.038997 | -0.010378 | -0.0065342 | -0.013613 | 0.08241 | 0.027467 | 0.029226 | -0.012576 | -0.022179 | 0.021938 | -0.022839 | 0.041199 | -0.064087 | -0.004578 | -0.073242 | -0.022888 | -0.073242 | -0.068665 | 0.07782 | 0.041199 | -0.004578 | 0.10986 | 0.1236 | 0.10071 | 0.10529 | 61.9125 | -62.1323 | -62.1414 | 61.8942 | 61.8484 | 61.8439 | -0.064087 | -0.068664 | 61.9125 | -62.027 | -61.9583 | 62.0407 | 62.0224 | 62.0178 | 0.10986 | 0.10529 | -0.01831 | -0.068664 | 0.12817 | 0.11444 | -0.059509 | 0.045777 | 61.853 | 61.9583 | -62.0728 | -62.0728 | 61.8439 | 62.027 | 61.9583 | 61.9949
706.8125 | 124.292 | -61.8896 | 62.0453 | 0.10013 | 0.014692 | 0.018986 | 0.042201 | -0.012514 | -0.0054662 | -0.013613 | 0.036633 | 0.032808 | 0.030294 | -0.0093725 | -0.01043 | 0.011257 | 0.0070684 | 0.045776 | -0.064087 | 0.004578 | -0.068665 | -0.032043 | -0.09613 | -0.07782 | 0.07782 | 0.036621 | -0.004578 | 0.10529 | 0.11902 | 0.11444 | 0.11902 | 61.8942 | -62.1094 | -62.114 | 61.8576 | 61.8118 | 61.7935 | -0.082398 | -0.10071 | 61.8851 | -62.0087 | -61.94 | 62.0087 | 62.0087 | 62.0041 | 0.1236 | 0.11902 | -0.036621 | -0.073243 | 0.1236 | 0.10986 | -0.068665 | 0.041199 | 61.8256 | 61.9263 | -62.0407 | -62.0499 | 61.821 | 61.9949 | 61.9354 | 61.9675
707.8125 | 124.2828 | -61.9171 | 62.0636 | 0.16117 | 0.0072148 | 0.00082752 | 0.042201 | -0.012514 | -0.00012524 | -0.016818 | 0.11293 | 0.033876 | 0.021749 | -0.0083045 | -0.007226 | 0.014461 | 0.0081364 | 0.027466 | -0.068665 | 0.004578 | -0.064087 | -0.032043 | -0.07782 | -0.073242 | 0.09613 | 0.041199 | -0.027466 | 0.10071 | 0.10986 | 0.10529 | 0.091553 | 61.9217 | -62.1323 | -62.1277 | 61.8851 | 61.8439 | 61.8393 | -0.07782 | -0.082398 | 61.8896 | -62.0224 | -61.9629 | 62.027 | 62.0087 | 62.0224 | 0.11902 | 0.13275 | -0.036621 | -0.068665 | 0.13733 | 0.12817 | -0.073243 | 0.068665 | 61.8484 | 61.9583 | -62.059 | -62.0911 | 61.853 | 62.0178 | 61.9446 | 62.0132
708.8125 | 124.2783 | -61.9217 | 62.0819 | 0.13065 | 0.0040108 | 0.0040315 | 0.042201 | 0.0088484 | -0.02042 | 0.0024082 | -0.070178 | 0.030671 | 0.030294 | -0.028598 | -0.011498 | 0.015529 | -0.013226 | 0.032043 | -0.064087 | 0.004578 | -0.082397 | -0.041199 | -0.082397 | -0.064087 | 0.082397 | 0.041199 | -0.004578 | 0.10529 | 0.12817 | 0.10529 | 0.09613 | 61.9263 | -62.146 | -62.1643 | 61.8805 | 61.8576 | 61.8393 | -0.068665 | -0.086975 | 61.9171 | -62.0407 | -61.9766 | 62.0499 | 62.0178 | 62.027 | 0.10071 | 0.10986 | -0.045777 | -0.086975 | 0.13275 | 0.10986 | -0.068665 | 0.045777 | 61.8576 | 61.9629 | -62.0773 | -62.0865 | 61.8393 | 62.027 | 61.9537 | 62.0041
709.8125 | 124.2599 | -61.8896 | 62.0544 | 0.14591 | 0.00080677 | 0.0093725 | 0.035792 | -0.0082416 | -0.010807 | 0.0066812 | 0.08241 | 0.041353 | 0.02709 | -0.033939 | -0.009362 | 0.013393 | -0.013226 | 0.022888 | -0.064087 | 0 | -0.064087 | -0.032043 | -0.073242 | -0.068665 | 0.086975 | 0.045776 | -0.009155 | 0.091553 | 0.09613 | 0.086975 | 0.091553 | 61.8896 | -62.1185 | -62.1185 | 61.8576 | 61.821 | 61.8164 | -0.068665 | -0.073242 | 61.8805 | -62.0087 | -61.9629 | 61.9858 | 61.9812 | 61.9766 | 0.10071 | 0.09613 | -0.032043 | -0.064087 | 0.10528 | 0.10071 | -0.064087 | 0.054931 | 61.8256 | 61.9354 | -62.0544 | -62.0636 | 61.8256 | 61.9812 | 61.9125 | 61.9766
710.8125 | 124.2691 | -61.9125 | 62.0636 | 0.13065 | 0.017896 | 0.011509 | 0.041133 | 0.0024404 | 0.0030788 | -0.00079579 | 0.08241 | 0.033876 | 0.020681 | 0.0066495 | -0.008294 | 0.015529 | 0.0092044 | 0.027466 | -0.068665 | -0.009155 | -0.073242 | -0.050354 | -0.073242 | -0.064087 | 0.068665 | 0.036621 | -0.009155 | 0.09613 | 0.10071 | 0.091553 | 0.086975 | 61.9034 | -62.1323 | -62.1368 | 61.8622 | 61.8484 | 61.8393 | -0.054932 | -0.064087 | 61.9034 | -62.027 | -61.9675 | 62.0132 | 61.9995 | 62.0041 | 0.09613 | 0.10071 | -0.041199 | -0.064087 | 0.10986 | 0.10528 | -0.05951 | 0.045776 | 61.8439 | 61.9492 | -62.0728 | -62.0728 | 61.8393 | 62.0087 | 61.94 | 61.9812
711.8125 | 124.2828 | -61.908 | 62.0544 | 0.084874 | 0.0050788 | 0.0072355 | 0.037928 | 0.022734 | 0.0030788 | -0.010409 | -0.085437 | 0.032808 | 0.0089315 | -0.022189 | -0.021111 | 0.014461 | 0.0038644 | 0.045776 | -0.045776 | 0 | -0.07782 | -0.027466 | -0.10986 | -0.059509 | 0.07782 | 0.045776 | 0.004578 | 0.10529 | 0.1236 | 0.10529 | 0.10986 | 61.908 | -62.1002 | -62.1323 | 61.8805 | 61.8484 | 61.7981 | -0.059509 | -0.10986 | 61.9125 | -62.0087 | -61.9492 | 62.0316 | 62.0178 | 62.0132 | 0.10529 | 0.10071 | -0.027466 | -0.07782 | 0.11902 | 0.10071 | -0.045776 | 0.041198 | 61.8622 | 61.9537 | -62.0544 | -62.0499 | 61.8301 | 62.0132 | 61.9537 | 61.9858
712.8125 | 124.2828 | -61.908 | 62.0682 | 0.16117 | 0.0061468 | 0.0018955 | 0.034724 | 0.010984 | -0.0043982 | -0.011477 | -0.070178 | 0.045625 | 0.019613 | 0.0066495 | -0.013634 | 0.019802 | -0.0014766 | -0.027466 | -0.022888 | -0.041199 | 0.009155 | 0.045776 | -0.018311 | 0.004578 | 0.013733 | 0.045776 | -0.022888 | 0.086975 | 0.09613 | 0.082397 | 0.10071 | 61.8668 | -62.0911 | -62.059 | 61.9537 | 61.9125 | 61.8896 | 0.045777 | 0.022888 | 61.8851 | -62.0224 | -61.9812 | 62.0041 | 62.0087 | 61.9904 | 0.1236 | 0.10528 | 0.086975 | 0.050354 | 0.11902 | 0.10986 | 0.018311 | 0.068664 | 61.8851 | 61.9537 | -62.1094 | -62.0911 | 61.9171 | 61.9949 | 61.8805 | 61.9217
713.8125 | 124.2508 | -61.9537 | 62.0682 | 0.069615 | 0.0040108 | 0.012577 | 0.03686 | 0.0088484 | -0.012943 | -0.0093408 | -0.070178 | 0.036012 | 0.034567 | -0.024326 | -0.01043 | 0.012325 | 0.0049324 | -0.045776 | -0.013733 | -0.045776 | 0.045776 | 0.07782 | 0 | 0.022888 | -0.027466 | 0.064087 | -0.027466 | 0.032043 | 0.041199 | 0.036621 | 0.050354 | 61.908 | -62.0819 | -62.0224 | 62.0316 | 61.9766 | 61.9537 | 0.068664 | 0.045776 | 61.9263 | -62.0041 | -62.0361 | 61.9949 | 62.0041 | 61.9904 | 0.07782 | 0.064087 | 0.1236 | 0.091552 | 0.068665 | 0.059509 | 0.032043 | 0.091553 | 61.94 | 62.0178 | -62.114 | -62.0956 | 61.9995 | 61.9858 | 61.908 | 61.9263
714.8125 | 124.2966 | -61.9125 | 62.0773 | 0.10013 | 0.0072148 | 0.00082752 | 0.042201 | 0.0045764 | -0.0076022 | -0.0082728 | 0.051892 | 0.039216 | 0.029226 | 0.0087855 | -0.020043 | 0.018734 | -0.0025446 | -0.013733 | -0.041199 | -0.036621 | -0.009155 | 0.036621 | -0.041199 | -0.032043 | 0.027466 | 0.064087 | -0.004578 | 0.09613 | 0.10071 | 0.091553 | 0.10986 | 61.8759 | -62.1185 | -62.0865 | 61.9492 | 61.8805 | 61.8713 | 0.004578 | -0.004578 | 61.908 | -62.0132 | -61.9812 | 62.0132 | 62.0224 | 62.0041 | 0.11444 | 0.096131 | 0.073242 | 0.027466 | 0.10529 | 0.10071 | -0.004578 | 0.068665 | 61.8713 | 61.9766 | -62.114 | -62.0819 | 61.9034 | 62.0087 | 61.8988 | 61.94
715.8125 | 124.2599 | -61.9446 | 62.0407 | 0.20695 | 0.011488 | 0.0040315 | 0.026179 | 0.0045764 | -0.0076022 | -0.0072048 | 0.0061157 | 0.03174 | 0.021749 | -0.0018955 | -0.014702 | 0.018734 | 0.0006594 | -0.041199 | -0.022888 | -0.045776 | 0.027466 | 0.082397 | 0.009155 | 0.004578 | -0.022888 | 0.082397 | -0.022888 | 0.050354 | 0.068665 | 0.054932 | 0.082397 | 61.8988 | -62.0636 | -62.0132 | 62.027 | 61.9492 | 61.9537 | 0.050354 | 0.054931 | 61.9217 | -61.9583 | -61.9904 | 62.0132 | 62.027 | 61.9995 | 0.10528 | 0.07782 | 0.12817 | 0.073242 | 0.091553 | 0.073242 | 0.022888 | 0.10528 | 61.9217 | 62.027 | -62.0865 | -62.0636 | 61.972 | 61.9949 | 61.9034 | 61.9217
716.8125 | 124.2783 | -61.9034 | 62.059 | 0.084874 | -0.00026223 | 0.0072355 | 0.041133 | 0.00030337 | -0.00012524 | -0.0082728 | 0.0061157 | 0.038148 | 0.033499 | 0.017331 | -0.024315 | 0.028347 | -0.020703 | -0.004578 | -0.041199 | -0.018311 | -0.032043 | -0.004578 | -0.054932 | -0.041199 | 0.054932 | 0.050354 | -0.013733 | 0.10529 | 0.091553 | 0.091553 | 0.10529 | 61.8851 | -62.1002 | -62.0911 | 61.8988 | 61.8622 | 61.8484 | -0.022888 | -0.036621 | 61.8896 | -62.0087 | -61.9537 | 61.9949 | 62.0087 | 61.9949 | 0.11902 | 0.10529 | 0.013733 | -0.013732 | 0.10529 | 0.11902 | -0.022888 | 0.064087 | 61.8622 | 61.9537 | -62.0773 | -62.0728 | 61.8713 | 62.0087 | 61.8988 | 61.9583
717.8125 | 124.2874 | -61.9537 | 62.059 | 0.13065 | 0.0018748 | 0.0072355 | 0.03152 | -0.0071726 | 0.0020108 | -0.0018638 | -0.03966 | 0.038148 | 0.024954 | 0.028012 | -0.018975 | 0.018734 | -0.014294 | -0.036621 | -0.022888 | -0.036621 | 0.009155 | 0.041199 | -0.004578 | -0.004578 | 0.009155 | 0.059509 | -0.027466 | 0.07782 | 0.10071 | 0.045776 | 0.073242 | 61.9171 | -62.0819 | -62.0499 | 61.9949 | 61.9492 | 61.9492 | 0.032043 | 0.032043 | 61.9263 | -61.9995 | -61.9812 | 62.0544 | 62.027 | 61.9995 | 0.10071 | 0.073242 | 0.07782 | 0.045776 | 0.12817 | 0.10529 | 0.013733 | 0.086975 | 61.9308 | 62.0132 | -62.0956 | -62.0865 | 61.9629 | 62.0316 | 61.9171 | 61.9629
718.8125 | 124.2325 | -61.94 | 62.0636 | 0.023839 | 0.01576 | 0.0083045 | 0.042201 | 0.016325 | -0.019351 | -0.0093408 | 0.067151 | 0.039216 | 0.036703 | 0.0055815 | -0.014702 | 0.030483 | 0.0038644 | -0.050354 | -0.032043 | -0.041199 | 0.041199 | 0.068665 | 0.013733 | 0.013733 | -0.018311 | 0.068665 | -0.027466 | 0.045776 | 0.050354 | 0.027466 | 0.064087 | 61.8988 | -62.0956 | -62.0224 | 62.0087 | 61.9537 | 61.9537 | 0.054932 | 0.054932 | 61.9125 | -61.9949 | -62.0178 | 61.9904 | 62.0041 | 61.9675 | 0.091553 | 0.054932 | 0.10986 | 0.082398 | 0.07782 | 0.073242 | 0.009156 | 0.096131 | 61.908 | 62.0087 | -62.1048 | -62.0911 | 61.9812 | 61.9858 | 61.8896 | 61.9217
719.8125 | 124.1821 | -61.9583 | 62.1048 | 0.054357 | 0.01042 | -0.0023775 | 0.026179 | 0.0077804 | -0.0086702 | -0.0082728 | -0.070178 | 0.040285 | 0.019613 | -0.025394 | -0.008294 | 0.018734 | -0.018567 | -0.050354 | -0.009155 | -0.045776 | 0.082397 | 0.13275 | 0.045776 | 0.059509 | -0.09613 | 0.082397 | -0.054932 | -0.018311 | -0.022888 | -0.050354 | -0.004578 | 61.9125 | -62.114 | -62.0224 | 62.0911 | 62.0178 | 62.0041 | 0.10528 | 0.091552 | 61.9034 | -62.0224 | -62.1231 | 61.9354 | 61.9537 | 61.908 | 0.050354 | 0.004578 | 0.17853 | 0.12817 | 0.032044 | 0.036621 | 0.036621 | 0.13733 | 61.9492 | 62.0407 | -62.1506 | -62.1597 | 62.0407 | 61.94 | 61.908 | 61.8622
720.8125 | 124.173 | -61.972 | 62.0911 | 0.10013 | 0.014692 | 0.012577 | 0.038997 | -0.0061046 | 0.0073508 | -0.010409 | -0.14647 | 0.043489 | 0.028158 | -0.023258 | -0.012566 | 0.017666 | 0.0049324 | -0.041199 | -0.032043 | -0.041199 | 0.10071 | 0.15106 | 0.073242 | 0.07782 | -0.11444 | 0.086975 | -0.045776 | -0.022888 | -0.032043 | -0.041199 | 0.004578 | 61.9308 | -62.1231 | -61.9904 | 62.1231 | 62.0499 | 62.0453 | 0.11902 | 0.11444 | 61.9263 | -62.0041 | -62.114 | 61.94 | 61.9766 | 61.9308 | 0.050354 | 0.004577 | 0.19226 | 0.14191 | 0.013733 | 0.022888 | 0.009156 | 0.13275 | 61.94 | 62.059 | -62.1323 | -62.1368 | 62.0728 | 61.9492 | 61.9308 | 61.8576

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.8396 | 21.7861 | 20.4878 | 20.6755
0.1604 | 22.7016 | 20.4893 | 20.6782
1.1604 | 24.3205 | 20.4808 | 20.6749
2.1604 | 26.6133 | 20.4813 | 20.6728
3.1604 | 29.4455 | 20.493 | 20.6792
4.1604 | 32.717 | 20.4916 | 20.6819
5.1604 | 36.4123 | 20.4972 | 20.6944
6.1604 | 40.4293 | 20.5077 | 20.6994
7.1604 | 44.729 | 20.5052 | 20.7041
8.1604 | 49.2835 | 20.5085 | 20.7145
9.1604 | 54.077 | 20.5225 | 20.7372
10.1604 | 58.9366 | 20.5367 | 20.758
11.1604 | 63.9947 | 20.5555 | 20.7851
12.1604 | 69.221 | 20.5685 | 20.8219
13.1604 | 74.5926 | 20.6001 | 20.8611
14.1604 | 80.1068 | 20.6275 | 20.9098
15.1604 | 85.7426 | 20.6618 | 20.9702
16.1604 | 91.4358 | 20.6877 | 21.0231
17.1604 | 97.1524 | 20.7409 | 21.0941
18.1604 | 102.9731 | 20.7913 | 21.1784
19.1604 | 108.8628 | 20.8438 | 21.2621
20.1604 | 114.7453 | 20.9043 | 21.3622
21.1604 | 120.7234 | 20.9714 | 21.4746
22.1604 | 126.7537 | 21.0474 | 21.5987
23.1604 | 132.7654 | 21.1367 | 21.727
24.1604 | 138.7527 | 21.2268 | 21.8739
25.1604 | 144.6381 | 21.3273 | 22.0341
26.1604 | 150.6143 | 21.4263 | 22.219
27.1604 | 156.673 | 21.5467 | 22.4045
28.1604 | 162.7395 | 21.671 | 22.6168
29.1604 | 168.8355 | 21.806 | 22.8277
30.1604 | 174.9409 | 21.9507 | 23.0665
31.1604 | 181.0833 | 22.1082 | 23.3086
32.1604 | 187.1151 | 22.2759 | 23.5745
33.1604 | 193.1589 | 22.4612 | 23.8554
34.1604 | 199.1344 | 22.6555 | 24.1434
35.1604 | 204.8934 | 22.8667 | 24.4561
36.1604 | 210.7904 | 23.0967 | 24.7766
37.1604 | 216.6585 | 23.3305 | 25.114
38.1604 | 222.5801 | 23.5895 | 25.4781
39.1604 | 228.6511 | 23.8649 | 25.8563
40.1604 | 234.5508 | 24.1541 | 26.2453
41.1604 | 240.4037 | 24.4573 | 26.6763
42.1604 | 246.0936 | 24.7663 | 27.1097
43.1604 | 251.8559 | 25.1096 | 27.5795
44.1604 | 257.6127 | 25.447 | 28.0439
45.1604 | 263.4425 | 25.8127 | 28.5444
46.1604 | 269.0276 | 26.1914 | 29.0495
47.1604 | 274.6574 | 26.599 | 29.5816
48.1604 | 280.4058 | 27.0178 | 30.1313
49.1604 | 286.1868 | 27.4414 | 30.7118
50.1604 | 291.8735 | 27.876 | 31.306
51.1604 | 297.4726 | 28.3428 | 31.9246
52.1604 | 302.8914 | 28.8239 | 32.5815
53.1604 | 308.3439 | 29.3214 | 33.2432
54.1604 | 313.8608 | 29.8377 | 33.9294
55.1604 | 319.3917 | 30.381 | 34.6323
56.1604 | 324.8854 | 30.9349 | 35.3681
57.1604 | 330.3269 | 31.4997 | 36.1161
58.1604 | 335.7835 | 32.0751 | 36.8896
59.1604 | 341.107 | 32.6743 | 37.6883
60.1604 | 346.3725 | 33.294 | 38.5077
61.1604 | 351.5636 | 33.9427 | 39.3453
62.1604 | 356.734 | 34.5843 | 40.211
63.1604 | 361.9738 | 35.2479 | 41.0734
64.1604 | 367.2917 | 35.9356 | 41.9811
65.1604 | 372.5825 | 36.6569 | 42.8918
66.1604 | 377.7409 | 37.3721 | 43.8408
67.1604 | 382.8872 | 38.1068 | 44.808
68.1604 | 387.9022 | 38.8606 | 45.7926
69.1604 | 392.9385 | 39.6394 | 46.8033
70.1604 | 397.8729 | 40.4305 | 47.8243
71.1604 | 402.805 | 41.2437 | 48.8633
72.1604 | 407.6238 | 42.0857 | 49.9178
73.1604 | 412.5489 | 42.9421 | 51.002
74.1604 | 417.6162 | 43.8432 | 52.1258
75.1604 | 422.6069 | 44.7592 | 53.2795
76.1604 | 427.5596 | 45.7253 | 54.48
77.1604 | 432.4148 | 46.6947 | 55.7361
78.1604 | 436.556 | 47.696 | 57.0228
79.1604 | 440.2181 | 48.733 | 58.3571
80.1604 | 443.6424 | 49.7816 | 59.721
81.1604 | 446.6469 | 50.8621 | 61.1038
82.1604 | 449.4851 | 51.9605 | 62.5175
83.1604 | 452.4537 | 53.0894 | 63.9407
84.1604 | 455.3294 | 54.2186 | 65.3872
85.1604 | 458.2774 | 55.3868 | 66.8501
86.1604 | 460.9117 | 56.5393 | 68.3135
87.1604 | 463.3689 | 57.7212 | 69.7948
88.1604 | 465.7333 | 58.8905 | 71.2829
89.1604 | 467.9065 | 60.082 | 72.7815
90.1604 | 469.7677 | 61.2779 | 74.2961
91.1604 | 471.1906 | 62.4866 | 75.8151
92.1604 | 472.4798 | 63.7068 | 77.3173
93.1604 | 473.8113 | 64.9362 | 78.8354
94.1604 | 474.6507 | 66.1685 | 80.3569
95.1604 | 475.2559 | 67.4048 | 81.8706
96.1604 | 475.7264 | 68.6442 | 83.4001
97.1604 | 476.0731 | 69.8811 | 84.9143
98.1604 | 476.2535 | 71.1277 | 86.4182
99.1604 | 476.2989 | 72.3542 | 87.9134
100.1604 | 476.2746 | 73.6087 | 89.3867
101.1604 | 476.1863 | 74.854 | 90.8455
102.1604 | 476.1438 | 76.0875 | 92.3116
103.1604 | 475.8986 | 77.3174 | 93.7968
104.1604 | 475.6459 | 78.5393 | 95.2656
105.1604 | 475.5083 | 79.7548 | 96.7182
106.1604 | 475.3516 | 80.9619 | 98.1707
107.1604 | 475.1205 | 82.1466 | 99.6005
108.1604 | 474.8757 | 83.3456 | 101.0171
109.1604 | 474.4882 | 84.5281 | 102.4419
110.1604 | 474.1965 | 85.7111 | 103.8428
111.1604 | 473.9161 | 86.8837 | 105.2232
112.1604 | 473.7899 | 88.0519 | 106.6028
113.1604 | 473.6663 | 89.216 | 107.9734
114.1604 | 473.5317 | 90.3791 | 109.3372
115.1604 | 473.6129 | 91.5355 | 110.6813
116.1604 | 473.4451 | 92.6909 | 112.032
117.1604 | 473.3521 | 93.8446 | 113.3482
118.1604 | 473.2934 | 94.9813 | 114.6687
119.1604 | 473.3459 | 96.1141 | 115.9716
120.1604 | 473.3759 | 97.2429 | 117.263
121.1604 | 473.3551 | 98.3745 | 118.5628
122.1604 | 473.4447 | 99.4818 | 119.8421
123.1604 | 473.6345 | 100.5912 | 121.1367
124.1604 | 473.7036 | 101.6938 | 122.444
125.1604 | 473.8691 | 102.8013 | 123.7242
126.1604 | 473.9748 | 103.8915 | 124.9701
127.1604 | 474.0743 | 104.9666 | 126.2238
128.1604 | 474.2285 | 106.0384 | 127.4703
129.1604 | 474.3632 | 107.0981 | 128.7037
130.1604 | 474.4809 | 108.1652 | 129.9306
131.1604 | 474.7384 | 109.2095 | 131.1586
132.1604 | 474.8514 | 110.2577 | 132.3757
133.1604 | 475.0326 | 111.3016 | 133.5901
134.1604 | 475.2559 | 112.353 | 134.7799
135.1604 | 475.3288 | 113.3817 | 135.9516
136.1604 | 475.4906 | 114.4174 | 137.1748
137.1604 | 475.5747 | 115.424 | 138.3527
138.1604 | 475.7288 | 116.4337 | 139.5463
139.1604 | 475.9944 | 117.4377 | 140.7157
140.1604 | 476.1503 | 118.4203 | 141.8865
141.1604 | 476.245 | 119.4069 | 143.0321
142.1604 | 476.3349 | 120.3845 | 144.1746
143.1604 | 476.4839 | 121.3558 | 145.3289
144.1604 | 476.6794 | 122.2903 | 146.4779
145.1604 | 476.8725 | 123.2283 | 147.611
146.1604 | 476.9568 | 124.1377 | 148.7415
147.1604 | 477.167 | 125.0504 | 149.8635
148.1604 | 477.343 | 125.9439 | 150.9967
149.1604 | 477.4801 | 126.8137 | 152.0978
150.1604 | 477.5415 | 127.6926 | 153.2149
151.1604 | 477.5744 | 128.5595 | 154.3205
152.1604 | 477.4934 | 129.4201 | 155.4181
153.1604 | 477.4272 | 130.2653 | 156.5083
154.1604 | 477.4165 | 131.1169 | 157.5987
155.1604 | 477.3932 | 131.9436 | 158.6736
156.1604 | 477.4871 | 132.7699 | 159.7667
157.1604 | 477.5158 | 133.5931 | 160.8468
158.1604 | 477.4385 | 134.4155 | 161.9143
159.1604 | 477.4193 | 135.2237 | 162.9675
160.1604 | 477.3557 | 136.0235 | 164.0351
161.1604 | 477.2767 | 136.8293 | 165.0973
162.1604 | 477.2059 | 137.6438 | 166.1605
163.1604 | 477.1614 | 138.4398 | 167.2219
164.1604 | 477.217 | 139.2486 | 168.2494
165.1604 | 477.2172 | 140.0352 | 169.2757
166.1604 | 477.2259 | 140.8378 | 170.3077
167.1604 | 477.2483 | 141.6111 | 171.3333
168.1604 | 477.099 | 142.3846 | 172.3491
169.1604 | 477.1037 | 143.159 | 173.3548
170.1604 | 477.0464 | 143.9178 | 174.3624
171.1604 | 476.9871 | 144.7026 | 175.3516
172.1604 | 476.9538 | 145.4816 | 176.344
173.1604 | 476.8773 | 146.2757 | 177.3376
174.1604 | 476.9467 | 147.0639 | 178.3203
175.1604 | 476.8957 | 147.8598 | 179.3078
176.1604 | 476.8219 | 148.6595 | 180.2912
177.1604 | 476.7951 | 149.4538 | 181.2686
178.1604 | 476.6908 | 150.2687 | 182.2618
179.1604 | 476.6254 | 151.0691 | 183.2823
180.1604 | 476.552 | 151.8854 | 184.2827
181.1604 | 476.5865 | 152.6963 | 185.2575
182.1604 | 476.5785 | 153.5111 | 186.2344
183.1604 | 476.5049 | 154.3313 | 187.2095
184.1604 | 476.549 | 155.1613 | 188.1861
185.1604 | 476.4437 | 155.9901 | 189.1732
186.1604 | 476.2971 | 156.8368 | 190.157
187.1604 | 476.1963 | 157.68 | 191.1294
188.1604 | 476.2378 | 158.5244 | 192.1046
189.1604 | 476.1609 | 159.3828 | 193.0771
190.1604 | 476.0396 | 160.254 | 194.0666
191.1604 | 476.0335 | 161.1185 | 195.0397
192.1604 | 476.0887 | 161.991 | 196.0192
193.1604 | 476.0611 | 162.8662 | 196.9917
194.1604 | 476.0447 | 163.7526 | 197.9745
195.1604 | 476.0482 | 164.6406 | 198.9661
196.1604 | 475.9762 | 165.5406 | 200.0005
197.1604 | 475.8452 | 166.4335 | 200.9923
198.1604 | 475.8744 | 167.3261 | 201.9821
199.1604 | 475.8122 | 168.2343 | 202.9632
200.1604 | 475.7508 | 169.1307 | 203.9503
201.1604 | 475.8493 | 170.0505 | 204.9324
202.1604 | 475.8605 | 170.9581 | 205.9172
203.1604 | 475.9047 | 171.8602 | 206.8908
204.1604 | 476.0019 | 172.7662 | 207.866
205.1604 | 475.8859 | 173.6737 | 208.8451
206.1604 | 475.7856 | 174.5797 | 209.8039
207.1604 | 475.7553 | 175.4767 | 210.7704
208.1604 | 475.6299 | 176.3783 | 211.7395
209.1604 | 475.6502 | 177.2817 | 212.7059
210.1604 | 475.6433 | 178.1846 | 213.6621
211.1604 | 475.7568 | 179.0851 | 214.6185
212.1604 | 475.841 | 179.9816 | 215.5808
213.1604 | 475.9329 | 180.8787 | 216.5416
214.1604 | 476.0059 | 181.781 | 217.5
215.1604 | 476.0397 | 182.6651 | 218.4913
216.1604 | 476.0029 | 183.5529 | 219.4616
217.1604 | 476.0719 | 184.425 | 220.423
218.1604 | 476.1061 | 185.3093 | 221.3833
219.1604 | 476.1695 | 186.2008 | 222.3446
220.1604 | 476.1828 | 187.0505 | 223.3078
221.1604 | 476.2051 | 187.8934 | 224.271
222.1604 | 476.334 | 188.7403 | 225.2449
223.1604 | 476.3813 | 189.6003 | 226.2394
224.1604 | 476.3281 | 190.4626 | 227.2362
225.1604 | 476.4304 | 191.3231 | 228.2674
226.1604 | 476.399 | 192.1746 | 229.2817
227.1604 | 476.4848 | 193.0315 | 230.3583
228.1604 | 476.5088 | 193.8894 | 231.4319
229.1604 | 476.4299 | 194.7425 | 232.5021
230.1604 | 476.3736 | 195.5853 | 233.5618
231.1604 | 476.41 | 196.4903 | 234.6783
232.1604 | 476.4496 | 197.3835 | 235.7825
233.1604 | 476.4826 | 198.2642 | 236.7898
234.1604 | 476.3429 | 199.1417 | 237.7696
235.1604 | 476.1963 | 200.0084 | 238.8315
236.1604 | 476.1003 | 200.8712 | 239.868
237.1604 | 476.0774 | 201.7156 | 240.938
238.1604 | 475.9587 | 202.5544 | 242.082
239.1604 | 475.795 | 203.3752 | 243.3257
240.1604 | 475.8059 | 204.1865 | 244.6343
241.1604 | 475.6871 | 204.9949 | 245.9831
242.1604 | 475.6006 | 205.7917 | 247.3804
243.1604 | 475.6014 | 206.5936 | 248.749
244.1604 | 475.5792 | 207.3817 | 250.0869
245.1604 | 475.5835 | 208.182 | 251.4913
246.1604 | 475.5081 | 208.9738 | 252.8816
247.1604 | 475.4353 | 209.7539 | 254.1978
248.1604 | 475.3378 | 210.5242 | 255.4877
249.1604 | 475.2662 | 211.2833 | 256.7133
250.1604 | 475.2879 | 212.0437 | 257.9157
251.1604 | 475.2295 | 212.8004 | 259.0622
252.1604 | 475.1903 | 213.5876 | 260.1258
253.1604 | 475.1528 | 214.395 | 261.0705
254.1604 | 475.1784 | 215.1849 | 262.0359
255.1604 | 475.1481 | 215.9515 | 263.0154
256.1604 | 475.1848 | 216.7255 | 264.016
257.1604 | 475.1666 | 217.5128 | 265.0488
258.1604 | 475.0984 | 218.2671 | 266.0139
259.1604 | 474.9881 | 218.9912 | 266.9649
260.1604 | 474.9494 | 219.6767 | 267.9042
261.1604 | 474.8655 | 220.2629 | 268.7939
262.1604 | 474.8798 | 220.7342 | 269.6359
263.1604 | 474.777 | 221.2566 | 270.4374
264.1604 | 474.6218 | 221.6942 | 271.1835
265.1604 | 474.6497 | 222.0796 | 271.8925
266.1604 | 474.5818 | 222.5096 | 272.5883
267.1604 | 474.5328 | 223.1092 | 273.3163
268.1604 | 474.4869 | 223.9139 | 274.046
269.1604 | 474.4965 | 224.8916 | 274.7369
270.1604 | 474.473 | 225.8763 | 275.3908
271.1604 | 474.4377 | 226.8379 | 276.0133
272.1604 | 474.4218 | 227.9073 | 276.6561
273.1604 | 474.376 | 228.9913 | 277.2703
274.1604 | 474.3615 | 230.0553 | 277.8441
275.1604 | 474.4111 | 231.0548 | 278.6713
276.1604 | 474.7158 | 231.8903 | 279.2891
277.1604 | 475.0292 | 232.7834 | 279.8595
278.1604 | 475.7362 | 233.6076 | 280.4096
279.1604 | 476.4226 | 234.4409 | 280.9024
280.1604 | 477.048 | 235.6515 | 281.4906
281.1604 | 477.418 | 236.9364 | 281.9249
282.1604 | 477.5403 | 238.4838 | 282.2658
283.1604 | 477.5534 | 239.7163 | 282.5819
284.1604 | 477.493 | 241.171 | 282.7845
285.1604 | 477.4088 | 242.5389 | 283.0457
286.1604 | 477.1496 | 244.0274 | 283.2859
287.1604 | 476.9175 | 245.6322 | 284.2615
288.1604 | 476.5972 | 247.4206 | 285.1581
289.1604 | 476.2746 | 249.9803 | 285.8536
290.1604 | 475.921 | 253.7931 | 287.0978
291.1604 | 475.5659 | 254.4507 | 286.7263
292.1604 | 475.2429 | 256.3653 | 285.7744
293.1604 | 474.9025 | 255.9325 | 284.8085
294.1604 | 474.5662 | 256.5168 | 283.9474
295.1604 | 474.2745 | 257.7072 | 283.1761
296.1604 | 473.9666 | 260.039 | 282.1732
297.1604 | 473.5485 | 263.0534 | 281.5816
298.1604 | 473.0666 | 266.2951 | 281.1701
299.1604 | 472.6494 | 268.3227 | 280.8389
300.1604 | 472.3153 | 269.7623 | 280.7587
301.1604 | 471.9777 | 271.6297 | 281.0506
302.1604 | 471.5309 | 272.6322 | 281.3056
303.1604 | 471.1647 | 273.5701 | 281.3644
304.1604 | 470.7842 | 273.399 | 281.8501
305.1604 | 470.3977 | 274.9746 | 282.1926
306.1604 | 470.0772 | 275.3329 | 282.8138
307.1604 | 469.6637 | 277.1358 | 283.3565
308.1604 | 469.3623 | 280.4298 | 283.6851
309.1604 | 468.9671 | 281.9648 | 283.9606
310.1604 | 468.7242 | 285.8428 | 284.3625
311.1604 | 468.3802 | 290.6594 | 284.8522
312.1604 | 468.1115 | 295.2121 | 285.6155
313.1604 | 467.8699 | 297.8597 | 286.3367
314.1604 | 467.6579 | 298.2787 | 287.0474
315.1604 | 467.4153 | 302.9532 | 287.8604
316.1604 | 467.1766 | 304.148 | 288.7778
317.1604 | 466.9094 | 306.0091 | 289.7512
318.1604 | 466.6486 | 308.9213 | 290.6919
319.1604 | 466.4283 | 308.9112 | 291.7013
320.1604 | 466.1487 | 311.6508 | 292.848
321.1604 | 465.9797 | 313.4075 | 293.8753
322.1604 | 465.8431 | 314.7531 | 295.0532
323.1604 | 465.7757 | 318.3286 | 296.2012
324.1604 | 465.8314 | 320.3114 | 297.6412
325.1604 | 465.8801 | 324.1481 | 299.2004
326.1604 | 465.8076 | 327.645 | 300.6375
327.1604 | 465.7901 | 330.0492 | 302.0909
328.1604 | 465.7909 | 330.9718 | 303.7255
329.1604 | 465.7633 | 333.2277 | 305.4074
330.1604 | 465.785 | 334.1808 | 307.1736
331.1604 | 465.8561 | 336.7284 | 309.0173
332.1604 | 466.0512 | 336.8417 | 311.0299
333.1604 | 466.2591 | 340.1046 | 313.139
334.1604 | 466.4477 | 347.1361 | 315.2146
335.1604 | 466.5583 | 347.5515 | 317.2896
336.1604 | 466.6591 | 351.7515 | 319.4649
337.1604 | 466.7313 | 354.5018 | 321.5254
338.1604 | 466.8836 | 356.6828 | 323.6225
339.1604 | 467.1039 | 359.3536 | 325.5344
340.1604 | 467.1271 | 361.9879 | 327.4259
341.1604 | 467.2502 | 363.6139 | 329.4833
342.1604 | 467.2334 | 365.3108 | 331.5628
343.1604 | 467.2308 | 368.1009 | 333.4495
344.1604 | 467.2421 | 369.9366 | 335.6389
345.1604 | 467.2419 | 371.6895 | 337.8006
346.1604 | 467.1187 | 373.7661 | 339.7991
347.1604 | 467.1315 | 374.3028 | 341.8257
348.1604 | 467.1675 | 376.4599 | 343.8598
349.1604 | 467.0918 | 378.8691 | 345.8981
350.1604 | 466.9769 | 379.7269 | 347.7733
351.1604 | 466.8777 | 381.1305 | 349.652
352.1604 | 466.6966 | 385.1698 | 351.482
353.1604 | 466.5876 | 386.8679 | 353.0055
354.1604 | 466.4953 | 386.4323 | 354.4538
355.1604 | 466.4302 | 389.0368 | 355.9029
356.1604 | 466.3684 | 391.1647 | 357.3447
357.1604 | 466.2671 | 393.1076 | 358.6518
358.1604 | 466.1299 | 394.7158 | 359.9139
359.1604 | 466.0782 | 396.3336 | 361.2601
360.1604 | 465.9767 | 397.8675 | 362.4868
361.1604 | 465.9264 | 400.0193 | 363.738
362.1604 | 465.9041 | 400.9788 | 364.9134
363.1604 | 465.9646 | 402.7105 | 366.0597
364.1604 | 466.0212 | 403.7812 | 367.2089
365.1604 | 466.0417 | 404.5209 | 368.3558
366.1604 | 466.0249 | 407.6621 | 369.4711
367.1604 | 466.0392 | 408.8492 | 370.6254
368.1604 | 466.1126 | 408.3045 | 371.687
369.1604 | 466.1502 | 410.2424 | 372.7087
370.1604 | 466.1687 | 412.2396 | 373.7044
371.1604 | 466.2544 | 413.2587 | 374.6566
372.1604 | 466.3401 | 414.644 | 375.6134
373.1604 | 466.4807 | 415.119 | 376.5605
374.1604 | 466.6273 | 417.5086 | 377.5315
375.1604 | 466.7239 | 418.6312 | 378.5052
376.1604 | 466.7859 | 420.0008 | 379.4482
377.1604 | 466.857 | 420.2088 | 380.3712
378.1604 | 466.982 | 420.0457 | 381.3712
379.1604 | 467.0463 | 419.3238 | 382.3413
380.1604 | 467.1127 | 420.2742 | 383.277
381.1604 | 467.2412 | 422.3099 | 384.2055
382.1604 | 467.317 | 421.1811 | 385.1361
383.1604 | 467.3762 | 421.4939 | 386.0793
384.1604 | 467.4513 | 423.3052 | 387.0534
385.1604 | 467.5769 | 424.2468 | 387.9514
386.1604 | 467.6226 | 424.6492 | 388.8286
387.1604 | 467.731 | 424.484 | 389.7876
388.1604 | 467.8337 | 425.4936 | 390.7602
389.1604 | 467.877 | 425.3434 | 391.6427
390.1604 | 467.8519 | 426.6951 | 392.4983
391.1604 | 467.8404 | 426.7374 | 393.3845
392.1604 | 467.8205 | 427.6603 | 394.2666
393.1604 | 467.8087 | 428.9269 | 395.1325
394.1604 | 467.7852 | 428.0251 | 395.9893
395.1604 | 467.8308 | 428.2188 | 396.7964
396.1604 | 467.8575 | 431.0743 | 397.5647
397.1604 | 467.9006 | 431.371 | 398.2894
398.1604 | 467.9703 | 429.3169 | 398.9817
399.1604 | 468.0364 | 432.7834 | 399.7091
400.1604 | 468.1093 | 432.3034 | 400.4035
401.1604 | 468.0972 | 432.9044 | 401.0008
402.1604 | 468.1064 | 433.3803 | 401.6145
403.1604 | 468.1346 | 433.8606 | 402.1744
404.1604 | 468.2347 | 433.89 | 402.7183
405.1604 | 468.3165 | 434.3747 | 403.2217
406.1604 | 468.3301 | 434.5655 | 403.7367
407.1604 | 468.3785 | 435.7386 | 404.3024
408.1604 | 468.4524 | 436.3578 | 404.9007
409.1604 | 468.5486 | 436.6685 | 405.405
410.1604 | 468.6244 | 437.2519 | 405.8725
411.1604 | 468.6914 | 437.7858 | 406.4582
412.1604 | 468.7677 | 437.9694 | 406.8377
413.1604 | 468.8785 | 438.0959 | 407.1406
414.1604 | 468.9451 | 438.2759 | 407.5511
415.1604 | 469.0188 | 438.6874 | 407.7942
416.1604 | 469.0155 | 438.7656 | 408.0513
417.1604 | 468.9762 | 439.1688 | 408.608
418.1604 | 469.0378 | 439.7453 | 409.3441
419.1604 | 469.17 | 439.9205 | 410.0343
420.1604 | 469.1896 | 440.176 | 410.6293
421.1604 | 469.2122 | 440.7415 | 411.3365
422.1604 | 469.3193 | 441.1519 | 412.0395
423.1604 | 469.3259 | 441.4683 | 412.7576
424.1604 | 469.3393 | 442.1078 | 413.568
425.1604 | 469.3879 | 442.2354 | 414.3623
426.1604 | 469.506 | 443.2509 | 415.2118
427.1604 | 469.6111 | 444.0163 | 416.0604
428.1604 | 469.692 | 445.0544 | 416.8889
429.1604 | 469.7455 | 446.1281 | 417.369
430.1604 | 469.8133 | 447.4106 | 417.8676
431.1604 | 469.8605 | 448.7432 | 418.5477
432.1604 | 469.903 | 450.2136 | 419.2698
433.1604 | 469.9224 | 451.5644 | 420.0142
434.1604 | 469.8559 | 452.7341 | 420.7846
435.1604 | 469.8805 | 454.1106 | 421.6037
436.1604 | 469.8448 | 455.2588 | 422.5376
437.1604 | 469.8763 | 456.7277 | 423.5084
438.1604 | 469.9623 | 458.2885 | 424.5072
439.1604 | 469.8761 | 459.5839 | 425.4978
440.1604 | 469.7915 | 461.1558 | 426.4936
441.1604 | 469.7488 | 462.8583 | 427.463
442.1604 | 469.8196 | 464.2595 | 428.4593
443.1604 | 469.8582 | 465.7879 | 429.4454
444.1604 | 469.7558 | 469.9976 | 430.4233
445.1604 | 469.6565 | 474.9342 | 431.4302
446.1604 | 469.6813 | 480.5036 | 432.4709
447.1604 | 469.6101 | 485.7304 | 433.5127
448.1604 | 469.6449 | 490.9923 | 434.5555
449.1604 | 469.6765 | 495.7791 | 435.671
450.1604 | 469.6565 | 500.2562 | 436.8191
451.1604 | 469.6653 | 504.2449 | 437.9053
452.1604 | 469.571 | 507.8828 | 438.9469
453.1604 | 469.4386 | 511.6911 | 440.0164
454.1604 | 469.4511 | 514.6822 | 441.1323
455.1604 | 469.3859 | 518.1063 | 442.1242
456.1604 | 469.4238 | 521.2658 | 443.1643
457.1604 | 469.3884 | 524.0085 | 444.1524
458.1604 | 469.386 | 526.8796 | 445.0715
459.1604 | 469.3124 | 530.0696 | 446.0302
460.1604 | 469.3364 | 532.9023 | 446.9839
461.1604 | 469.3664 | 535.223 | 447.867
462.1604 | 469.3472 | 537.7854 | 448.6519
463.1604 | 469.3781 | 540.4161 | 449.458
464.1604 | 469.3228 | 542.8471 | 450.3022
465.1604 | 469.287 | 545.6539 | 451.1233
466.1604 | 469.2925 | 548.2084 | 452.026
467.1604 | 469.385 | 550.7835 | 452.7325
468.1604 | 469.364 | 553.0958 | 453.6429
469.1604 | 469.3325 | 555.8119 | 454.3992
470.1604 | 469.2701 | 558.1754 | 455.42
471.1604 | 469.2451 | 560.2186 | 456.4107
472.1604 | 469.1844 | 562.6613 | 457.3637
473.1604 | 469.1937 | 565.7755 | 458.4318
474.1604 | 469.2315 | 567.7926 | 459.5249
475.1604 | 469.2673 | 570.076 | 460.7787
476.1604 | 469.2568 | 572.4165 | 461.9285
477.1604 | 469.2889 | 574.6445 | 463.0783
478.1604 | 469.2841 | 576.3162 | 464.2011
479.1604 | 469.3465 | 577.4626 | 465.3028
480.1604 | 469.3369 | 578.3984 | 466.4921
481.1604 | 469.2914 | 579.3208 | 467.7475
482.1604 | 469.2441 | 579.7784 | 469.0422
483.1604 | 469.1871 | 580.9353 | 470.5321
484.1604 | 469.0805 | 581.2565 | 472.3853
485.1604 | 469.0289 | 581.4687 | 474.2666
486.1604 | 468.9927 | 581.7911 | 476.0564
487.1604 | 468.9684 | 582.2123 | 477.775
488.1604 | 468.9919 | 582.8303 | 479.7736
489.1604 | 468.9741 | 583.7737 | 483.6464
490.1604 | 469.0514 | 584.7802 | 489.2583
491.1604 | 469.1395 | 585.2717 | 494.9655
492.1604 | 469.2184 | 585.9085 | 500.1336
493.1604 | 469.2851 | 586.4912 | 504.9542
494.1604 | 469.4288 | 588.0768 | 510.3563
495.1604 | 469.521 | 588.5145 | 515.6457
496.1604 | 469.6037 | 589.6592 | 521.0906
497.1604 | 469.5983 | 590.4751 | 525.8648
498.1604 | 469.7282 | 590.6502 | 530.4166
499.1604 | 469.7716 | 591.278 | 536.1638
500.1604 | 469.752 | 591.2599 | 542.8358
501.1604 | 469.6518 | 591.789 | 551.028
502.1604 | 469.6142 | 592.7458 | 555.4199
503.1604 | 469.7053 | 592.4543 | 561.6702
504.1604 | 469.7642 | 592.9229 | 563.1145
505.1604 | 469.7415 | 593.669 | 565.7571
506.1604 | 469.7664 | 594.6122 | 566.4263
507.1604 | 469.7789 | 595.9345 | 567.3821
508.1604 | 469.7711 | 597.0918 | 569.8823
509.1604 | 469.72 | 598.179 | 569.6273
510.1604 | 469.6768 | 598.8198 | 572.4397
511.1604 | 469.6613 | 598.8818 | 580.4178
512.1604 | 469.7202 | 599.8327 | 584.6633
513.1604 | 469.7605 | 600.8877 | 588.1772
514.1604 | 469.7581 | 601.3186 | 592.935
515.1604 | 469.5915 | 600.5535 | 593.7708
516.1604 | 469.4566 | 600.4612 | 596.9441
517.1604 | 469.4002 | 599.8055 | 598.6242
518.1604 | 469.3611 | 598.7904 | 598.8066
519.1604 | 469.302 | 598.996 | 599.5965
520.1604 | 469.2916 | 600.2666 | 602.4805
521.1604 | 469.4013 | 601.4567 | 606.8005
522.1604 | 469.4706 | 602.1192 | 607.2271
523.1604 | 469.5565 | 602.8888 | 609.1947
524.1604 | 469.6577 | 603.0868 | 612.9711
525.1604 | 469.706 | 603.0638 | 617.1454
526.1604 | 469.6652 | 603.5742 | 619.919
527.1604 | 469.6373 | 604.6765 | 620.0139
528.1604 | 469.727 | 605.6311 | 624.5775
529.1604 | 469.7662 | 606.5579 | 626.3802
530.1604 | 469.7682 | 607.0474 | 626.476
531.1604 | 469.7553 | 607.1104 | 628.5351
532.1604 | 469.7687 | 606.9487 | 630.4042
533.1604 | 469.7182 | 606.5387 | 629.5383
534.1604 | 469.7041 | 606.1614 | 634.6506
535.1604 | 469.7222 | 606.3082 | 635.3184
536.1604 | 469.8051 | 606.8065 | 637.0215
537.1604 | 469.8402 | 606.7528 | 640.8843
538.1604 | 469.8925 | 606.8829 | 643.8538
539.1604 | 469.924 | 607.6586 | 645.4356
540.1604 | 469.9429 | 607.6123 | 650.3687
541.1604 | 470.0513 | 607.4321 | 652.066
542.1604 | 470.0487 | 607.9501 | 651.9619
543.1604 | 470.0358 | 609.2082 | 658.0961
544.1604 | 470.0614 | 610.0485 | 660.4447
545.1604 | 470.2129 | 609.8443 | 661.5967
546.1604 | 470.2332 | 610.0006 | 667.5384
547.1604 | 470.2557 | 611.0535 | 673.8288
548.1604 | 470.3075 | 612.835 | 665.7678
549.1604 | 470.2937 | 613.6194 | 666.3651
550.1604 | 470.3042 | 614.4438 | 665.9647
551.1604 | 470.3329 | 614.6122 | 667.4851
552.1604 | 470.3112 | 616.4891 | 667.188
553.1604 | 470.2934 | 616.7804 | 665.1128
554.1604 | 470.2632 | 617.295 | 668.6915
555.1604 | 470.2334 | 618.3217 | 676.0236
556.1604 | 470.1996 | 618.7192 | 680.6515
557.1604 | 470.1452 | 618.1451 | 684.7342
558.1604 | 470.0537 | 617.8156 | 685.5951
559.1604 | 469.9606 | 617.6778 | 684.2436
560.1604 | 469.9165 | 617.3088 | 688.3574
561.1604 | 469.9197 | 617.2558 | 690.6337
562.1604 | 469.8495 | 617.006 | 691.4654
563.1604 | 469.7906 | 616.3319 | 691.322
564.1604 | 469.7376 | 616.457 | 695.9941
565.1604 | 469.6934 | 615.9832 | 693.7664
566.1604 | 469.7261 | 615.1303 | 690.452
567.1604 | 469.7112 | 606.0018 | 682.1463
568.1604 | 469.5811 | 603.4399 | 681.8383
569.1604 | 469.4699 | 602.3091 | 679.3106
570.1604 | 469.3793 | 601.1197 | 687.7389
571.1604 | 469.3102 | 607.8759 | 691.0545
572.1604 | 469.2485 | 607.0876 | 688.2269
573.1604 | 469.2073 | 608.012 | 693.0527
574.1604 | 469.1657 | 607.6224 | 688.8675
575.1604 | 469.1202 | 607.2879 | 687.9496
576.1604 | 469.1032 | 606.7398 | 683.3765
577.1604 | 469.0962 | 606.5661 | 675.6523
578.1604 | 469.0601 | 607.7517 | 674.6827
579.1604 | 469.0145 | 607.487 | 680.1821
580.1604 | 468.9494 | 606.1258 | 678.2748
581.1604 | 468.9248 | 605.6704 | 680.4439
582.1604 | 468.8853 | 605.5901 | 682.8669
583.1604 | 468.8202 | 605.0734 | 683.7361
584.1604 | 468.7798 | 605.8305 | 688.9099
585.1604 | 468.7844 | 605.2635 | 688.6756
586.1604 | 468.7844 | 604.8436 | 689.5592
587.1604 | 468.8149 | 603.6026 | 691.2791
588.1604 | 468.8359 | 603.7277 | 691.2633
589.1604 | 468.7617 | 603.1099 | 685.4021
590.1604 | 468.7682 | 604.2783 | 683.3825
591.1604 | 468.8234 | 605.2408 | 680.0342
592.1604 | 468.8211 | 604.2738 | 675.3532
593.1604 | 468.7625 | 615.8052 | 690.5937
594.1604 | 468.6935 | 617.1477 | 690.7923
595.1604 | 468.7886 | 616.81 | 681.5299
596.1604 | 468.7518 | 616.1976 | 675.6206
597.1604 | 468.6991 | 616.3075 | 674.3453
598.1604 | 468.7306 | 616.9877 | 669.0892
599.1604 | 468.7519 | 617.1558 | 665.134
600.1604 | 468.7639 | 617.6025 | 663.3294
601.1604 | 468.7559 | 617.0468 | 666.9977
602.1604 | 468.7536 | 617.4812 | 663.6464
603.1604 | 468.8125 | 616.9261 | 663.0789
604.1604 | 468.8546 | 618.1685 | 665.2702
605.1604 | 468.9076 | 618.011 | 661.3397
606.1604 | 468.8923 | 618.0912 | 658.4113
607.1604 | 468.9155 | 617.6706 | 655.6713
608.1604 | 468.8606 | 617.814 | 652.5487
609.1604 | 468.778 | 618.4045 | 655.0493
610.1604 | 468.7414 | 619.2038 | 656.2897
611.1604 | 468.8109 | 620.7262 | 661.2809
612.1604 | 468.8946 | 622.6177 | 662.8894
613.1604 | 468.9304 | 623.8525 | 664.1383
614.1604 | 468.9697 | 625.3846 | 666.7912
615.1604 | 469.0316 | 625.4618 | 661.5364
616.1604 | 469.0353 | 625.6053 | 658.4407
617.1604 | 469.0208 | 625.5733 | 662.1354
618.1604 | 469.0728 | 626.2455 | 662.777
619.1604 | 469.194 | 625.9954 | 659.1009
620.1604 | 469.2785 | 626.0686 | 655.6261
621.1604 | 469.4391 | 626.6076 | 656.9207
622.1604 | 469.6177 | 626.7445 | 660.315
623.1604 | 469.7728 | 627.3346 | 660.1115
624.1604 | 469.8902 | 627.1695 | 656.2688
625.1604 | 469.9669 | 627.3086 | 659.6082
626.1604 | 470.1713 | 627.4417 | 657.9001
627.1604 | 470.3386 | 627.2928 | 654.9943
628.1604 | 470.4639 | 626.8893 | 659.2201
629.1604 | 470.4823 | 626.4144 | 659.1734
630.1604 | 470.442 | 625.8484 | 655.3576
631.1604 | 470.5935 | 625.7242 | 655.7511
632.1604 | 470.7335 | 625.2723 | 652.8672
633.1604 | 470.8198 | 624.7403 | 654.2116
634.1604 | 470.7574 | 624.7371 | 658.0182
635.1604 | 470.7843 | 624.684 | 657.2684
636.1604 | 470.9125 | 624.3953 | 657.2849
637.1604 | 471.037 | 623.5413 | 656.2127
638.1604 | 471.0562 | 622.8483 | 654.8481
639.1604 | 471.1228 | 621.73 | 650.1584
640.1604 | 471.1152 | 621.0207 | 647.6961
641.1604 | 471.1 | 620.321 | 650.7249
642.1604 | 471.0409 | 619.5455 | 650.5282
643.1604 | 470.8771 | 618.4419 | 647.5347
644.1604 | 470.8173 | 617.1175 | 643.5037
645.1604 | 470.8313 | 616.2041 | 643.8636
646.1604 | 470.7914 | 615.6893 | 641.5895
647.1604 | 470.6866 | 616.246 | 642.5137
648.1604 | 470.6796 | 616.2986 | 643.4479
649.1604 | 470.8382 | 616.464 | 645.1095
650.1604 | 470.8904 | 615.9379 | 640.2306
651.1604 | 470.8758 | 615.4616 | 637.2884
652.1604 | 470.8882 | 614.9971 | 637.1302
653.1604 | 470.8515 | 614.8027 | 638.5414
654.1604 | 470.946 | 615.5121 | 644.8285
655.1604 | 470.8611 | 615.4489 | 645.1969
656.1604 | 470.7632 | 616.0207 | 649.168
657.1604 | 470.8023 | 616.3942 | 650.3538
658.1604 | 470.8597 | 616.5718 | 648.0656
659.1604 | 470.8246 | 616.4651 | 646.8688
660.1604 | 470.6938 | 617.2571 | 651.9104
661.1604 | 470.6146 | 616.8865 | 650.0514
662.1604 | 470.5081 | 616.3982 | 645.4664
663.1604 | 470.4352 | 615.8313 | 643.2196
664.1604 | 470.2787 | 615.1293 | 641.2793
665.1604 | 470.1389 | 615.0623 | 644.4652
666.1604 | 470.0064 | 615.4813 | 646.4654
667.1604 | 469.8509 | 615.1899 | 644.9454
668.1604 | 469.5326 | 614.8362 | 645.155
669.1604 | 469.209 | 615.0672 | 649.3834
670.1604 | 469.043 | 615.0189 | 648.8381
671.1604 | 468.717 | 614.9217 | 650.0645
672.1604 | 468.4155 | 615.0756 | 653.5974
673.1604 | 468.1989 | 615.1623 | 654.1803
674.1604 | 467.9228 | 615.0919 | 655.3093
675.1604 | 467.4929 | 614.9211 | 661.1806
676.1604 | 467.0908 | 615.4107 | 662.8865
677.1604 | 466.8371 | 614.5477 | 656.6765
678.1604 | 466.7057 | 613.9335 | 658.2814
679.1604 | 466.3634 | 613.8976 | 661.8333
680.1604 | 465.8903 | 613.772 | 662.2768
681.1604 | 465.5007 | 614.2582 | 670.5185
682.1604 | 465.2539 | 615.0272 | 668.673
683.1604 | 464.9411 | 614.0532 | 661.8009
684.1604 | 464.5933 | 613.3424 | 658.0281
685.1604 | 464.3251 | 612.3262 | 655.3894
686.1604 | 464.1077 | 611.8653 | 659.2503
687.1604 | 463.7894 | 610.7435 | 655.4393
688.1604 | 463.3922 | 610.0918 | 652.6711
689.1604 | 463.0258 | 609.614 | 654.1045
690.1604 | 462.707 | 609.1048 | 650.829
691.1604 | 462.3698 | 608.9373 | 653.2195
692.1604 | 461.9696 | 608.5382 | 650.3154
693.1604 | 461.5617 | 607.1021 | 648.8471
694.1604 | 461.2569 | 606.6981 | 648.9152
695.1604 | 460.9092 | 605.9504 | 649.6833
696.1604 | 460.5337 | 605.7141 | 648.4876
697.1604 | 460.0932 | 605.5437 | 649.8225
698.1604 | 459.7121 | 605.7402 | 651.8113
699.1604 | 459.3636 | 605.5982 | 647.3682
700.1604 | 458.9765 | 604.9424 | 644.5516
701.1604 | 458.5271 | 604.4122 | 641.5029
702.1604 | 458.0694 | 604.407 | 640.4657
703.1604 | 457.6158 | 604.133 | 641.5085
704.1604 | 457.2432 | 604.0605 | 642.1582
705.1604 | 456.9207 | 603.4118 | 639.6237
706.1604 | 456.5099 | 602.5892 | 638.8222
707.1604 | 456.0606 | 601.5711 | 637.7047
708.1604 | 455.6168 | 601.4044 | 635.0262
709.1604 | 455.1735 | 600.6728 | 632.2901
710.1604 | 454.7292 | 600.1936 | 629.0672
711.1604 | 454.2816 | 599.2941 | 627.1862
712.1604 | 453.8192 | 598.5425 | 625.2659
713.1604 | 453.3926 | 597.3628 | 623.7435
714.1604 | 452.9446 | 596.8617 | 625.3464
715.1604 | 452.4699 | 596.8877 | 624.1462
716.1604 | 451.9596 | 596.1688 | 623.4085
717.1604 | 451.4565 | 595.3177 | 622.6466
718.1604 | 451.0583 | 593.9595 | 620.5391
719.1604 | 450.5742 | 593.6126 | 621.3449
720.1604 | 450.1204 | 592.9111 | 619.2552