## Test Conditions
DESIREE-FIRE Test Number 8 - Circuit Simulator Data Only
Test Date: | 2009-07-20
DCSim DAQ Start Time | 3:23
DCSim Time for Synchronization
Heat Source Synchronization |  | minutes:seconds
Heat Source DAQ Start Time
Fire Time | 3:29
Offset | 0:06 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 360 | seconds
Heat Source Offset | 3:29 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 212 | seconds
Heat Source Stop Time | 3:42
Test Duration | 0:13 | minutes:seconds
| 780 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.51562 | 123.8342 | -60.3149 | 63.2538 | 0.094845 | -0.00034947 | 0.072743 | 0.054463 | -0.010078 | 0.0013638 | 0.0067786 | 0.023818 | 0.0012264 | 0.058208 | 0.075805 | -0.012563 | 0.0042299 | 0.0068215 | -0.050354 | 63.176 | -60.4156 | 63.3362 | -60.3149 | -60.6308 | -0.086975 | 0.009155 | 63.2126 | -60.3699 | 63.4369 | -60.3516 | -60.4477 | -60.3287 | -0.10071 | -0.07782 | 0.082398 | 0 | 60.228 | -0.31586 | 60.3287 | -0.21515 | -0.054932 | -0.041199 | 0.18311 | -0.036621 | -0.013733 | -0.13275 | 0.041199 | -0.07782 | 0.10071 | 123.7518 | 0.018311 | 123.8068 | 123.5916 | 123.5825 | 123.4909 | 123.5275 | -123.6694 | -123.6237 | 123.6511 | 123.7518 | 60.2646 | 60.3241
0.48438 | 123.8617 | -60.3012 | 63.2675 | 0.079586 | 0.0028555 | 0.068471 | 0.058736 | 0.016624 | 0.0099088 | -0.0028344 | 0.069594 | -0.011591 | 0.068889 | 0.072601 | 0.0045258 | -0.0011101 | 0.00041246 | -0.027466 | 63.1668 | -60.4431 | 63.2263 | -60.2554 | -60.4523 | -0.09613 | -0.018311 | 63.2172 | -60.347 | 63.4644 | -60.3058 | -60.4431 | -60.3241 | -0.14191 | -0.10071 | -0.041199 | 0.045776 | 60.2051 | -0.15106 | 60.347 | -0.009156 | -0.045777 | -0.050354 | 0.19684 | -0.004578 | -0.022889 | -0.14191 | 0.022888 | -0.09613 | 0.18768 | 123.6694 | 0.041199 | 123.8113 | 123.6099 | 123.5641 | 123.468 | 123.5184 | -123.7106 | -123.6145 | 123.5275 | 123.7656 | 60.2737 | 60.2829
1.4844 | 123.8754 | -60.3333 | 63.2584 | -0.10352 | -0.0035535 | 0.065267 | 0.064076 | 0.018761 | 0.00029581 | 0.011052 | -0.5255 | 0.0012264 | 0.052867 | 0.059784 | 0.0034578 | -0.0064511 | 0.00041246 | -0.027466 | 63.2034 | -60.4523 | 63.3224 | -60.3241 | -60.6537 | -0.10071 | 0.16479 | 63.1714 | -60.3607 | 63.5056 | -60.3058 | -60.466 | -60.347 | -0.11902 | -0.054932 | 0.064087 | 0.009155 | 60.2325 | -0.32043 | 60.3516 | -0.20142 | -0.027466 | -0.086975 | 0.24719 | 0.027466 | -0.013733 | -0.13275 | 0.013733 | -0.10529 | 0.12817 | 123.7747 | 0.054932 | 123.8663 | 123.6557 | 123.5321 | 123.5367 | 123.5046 | -123.7106 | -123.6191 | 123.6557 | 123.8388 | 60.3058 | 60.498
2.4844 | 123.848 | -60.2875 | 63.295 | 0.17114 | 0.0017875 | 0.059926 | 0.054463 | 0.011284 | -0.0029082 | -0.0071064 | 0.20692 | -0.0073186 | 0.063548 | 0.038421 | 0.0087988 | -0.0085871 | -0.0059965 | -0.027466 | 63.2217 | -60.4294 | 63.3682 | -60.2463 | -60.585 | -0.018311 | -0.004578 | 63.2309 | -60.3607 | 63.4506 | -60.3287 | -60.4248 | -60.3378 | -0.14191 | -0.073242 | 0.073242 | 0.041199 | 60.2692 | -0.29755 | 60.4111 | -0.15564 | -0.073242 | -0.064087 | 0.15564 | -0.041198 | -0.050354 | -0.13733 | 0.022888 | -0.064087 | 0.1831 | 123.7976 | 0.032044 | 123.8113 | 123.6511 | 123.5916 | 123.5092 | 123.5184 | -123.7244 | -123.6557 | 123.6557 | 123.7381 | 60.26 | 60.2829
3.4844 | 123.8663 | -60.3149 | 63.2721 | 0.0032924 | -0.00034947 | 0.064198 | 0.070485 | -0.016487 | 0.00029581 | 0.0046426 | 0.084853 | -0.010523 | 0.065685 | 0.055511 | -0.00081422 | 0.0052979 | -0.0038605 | -0.054932 | 63.1531 | -60.434 | 63.3362 | -60.3195 | -60.64 | -0.091553 | 0.004578 | 63.208 | -60.3516 | 63.4735 | -60.3378 | -60.4431 | -60.3287 | -0.11902 | -0.11902 | 0.064087 | -0.004578 | 60.2234 | -0.32501 | 60.3424 | -0.20599 | -0.036621 | -0.064087 | 0.20142 | -0.022889 | -0.013733 | -0.12817 | 0.022888 | -0.091553 | 0.11444 | 123.7701 | 0.013732 | 123.8251 | 123.587 | 123.5596 | 123.468 | 123.5229 | -123.7061 | -123.6237 | 123.6511 | 123.7885 | 60.26 | 60.3195
4.4844 | 123.8571 | -60.3104 | 63.2355 | 0.03381 | -0.0046215 | 0.059926 | 0.065144 | -0.017555 | -0.0050442 | -0.010311 | 0.069594 | 0.0033634 | 0.068889 | 0.032013 | -0.0061552 | 0.0020939 | 0.0014805 | -0.013733 | 63.1577 | -60.434 | 63.3224 | -60.3195 | -60.6491 | -0.082397 | 0.018311 | 63.2309 | -60.3699 | 63.4689 | -60.3195 | -60.4294 | -60.3104 | -0.1236 | -0.07782 | 0.086975 | -0.009155 | 60.228 | -0.33875 | 60.3516 | -0.21515 | -0.059509 | -0.004578 | 0.23346 | -0.009155 | 0 | -0.11902 | 0.059509 | -0.059509 | 0.11444 | 123.7564 | 0.050354 | 123.8388 | 123.5916 | 123.6008 | 123.468 | 123.5413 | -123.6694 | -123.6053 | 123.6328 | 123.7793 | 60.2966 | 60.3287
5.4844 | 123.8709 | -60.3058 | 63.2446 | 0.30847 | -0.012098 | 0.069539 | 0.072621 | 0.0080791 | 0.0056368 | 0.0099836 | -0.0066996 | 0.0044314 | 0.060344 | 0.035217 | -0.00081422 | -4.2099e-05 | 0.00041246 | 0.050354 | 63.208 | -60.4248 | 63.295 | -60.3745 | -60.6812 | -0.10071 | 0 | 63.2126 | -60.3287 | 63.4644 | -60.3104 | -60.4614 | -60.3149 | -0.11902 | -0.036621 | 0.050354 | -0.068665 | 60.2051 | -0.37537 | 60.3241 | -0.25635 | -0.022888 | -0.032044 | 0.21973 | -0.004578 | -0.009155 | -0.15564 | 0.013733 | -0.13275 | 0.050354 | 123.7198 | 0.01831 | 123.793 | 123.6328 | 123.5413 | 123.5138 | 123.5184 | -123.6694 | -123.5733 | 123.6008 | 123.7701 | 60.3561 | 60.3058
6.4844 | 123.8297 | -60.3195 | 63.2629 | 0.064327 | -0.0024855 | 0.067403 | 0.058736 | -0.02076 | -0.0029082 | 0.0078466 | 0.16115 | -0.00090962 | 0.059276 | 0.04483 | 0.0098668 | -0.0085871 | -0.0017235 | -0.054932 | 63.1897 | -60.4202 | 63.3133 | -60.3149 | -60.6354 | -0.082397 | 0.013733 | 63.2034 | -60.3607 | 63.4735 | -60.3287 | -60.4523 | -60.3516 | -0.10071 | -0.073242 | 0.050354 | 0.004578 | 60.2371 | -0.31586 | 60.3378 | -0.21515 | -0.041199 | -0.059509 | 0.21057 | -0.009155 | -0.032043 | -0.13275 | 0.009156 | -0.091553 | 0.10529 | 123.7335 | 0.032044 | 123.8342 | 123.6099 | 123.5641 | 123.5092 | 123.5229 | -123.6832 | -123.6237 | 123.6328 | 123.793 | 60.2646 | 60.3333
7.4844 | 123.8251 | -60.3241 | 63.2675 | 0.1101 | -0.014234 | 0.052449 | 0.055531 | 0.018761 | 0.0045688 | 0.0025066 | 0.11537 | -0.00090962 | 0.063548 | 0.051239 | 0.0045258 | 0.0020939 | 0.0046845 | 0.13733 | 63.2309 | -60.4065 | 63.3911 | -60.1959 | -60.5713 | -0.022888 | -0.059509 | 63.208 | -60.3836 | 63.4323 | -60.3516 | -60.4843 | -60.3699 | -0.082397 | -0.036621 | 0.1236 | 0.12817 | 60.3012 | -0.24719 | 60.3836 | -0.16479 | -0.059509 | -0.059509 | 0.1648 | -0.027465 | -0.045776 | -0.16022 | 0.013733 | -0.10071 | 0.21057 | 123.7976 | 0.032044 | 123.8159 | 123.6374 | 123.5916 | 123.555 | 123.5321 | -123.674 | -123.6511 | 123.7152 | 123.7564 | 60.4614 | 60.2646
8.4844 | 123.8754 | -60.3149 | 63.2217 | 0.079586 | 0.0017875 | 0.072743 | 0.075825 | 0.0038071 | 0.022727 | 0.0057106 | -0.021958 | 0.0022944 | 0.068889 | 0.069397 | -0.0061552 | -0.0075191 | 0.0036165 | -0.086975 | 63.1668 | -60.466 | 63.3179 | -60.3195 | -60.6354 | -0.10071 | -0.21515 | 63.1668 | -60.3973 | 63.4506 | -60.2921 | -60.434 | -60.3104 | -0.15106 | -0.054932 | 0.09613 | -0.004578 | 60.2142 | -0.32044 | 60.3653 | -0.16937 | -0.082398 | -0.054932 | 0.22888 | 0.022888 | 0.004577 | -0.11902 | 0.086975 | -0.036621 | 0.14648 | 123.7839 | 0.10529 | 123.848 | 123.6328 | 123.5641 | 123.4818 | 123.4818 | -123.6877 | -123.6191 | 123.6328 | 123.7656 | 60.228 | 60.0998
9.4844 | 123.8663 | -60.3149 | 63.2355 | 0.064327 | 0.0017875 | 0.068471 | 0.065144 | 0.0038071 | -0.0050442 | -0.0028344 | -0.021958 | 0.0044314 | 0.056072 | 0.085418 | 0.0013218 | -0.0075191 | 0.0078895 | -0.059509 | 63.1851 | -60.4431 | 63.327 | -60.3149 | -60.6354 | -0.086975 | 0.004578 | 63.2034 | -60.3516 | 63.4735 | -60.3333 | -60.4523 | -60.3195 | -0.12817 | -0.050354 | 0.091552 | 0 | 60.228 | -0.32044 | 60.3561 | -0.19226 | -0.036621 | -0.032044 | 0.23804 | -0.018311 | -0.004578 | -0.13733 | 0.032043 | -0.10071 | 0.12817 | 123.7701 | 0.01831 | 123.8251 | 123.6282 | 123.555 | 123.5001 | 123.5184 | -123.6786 | -123.587 | 123.642 | 123.7885 | 60.2554 | 60.3195
10.4844 | 123.8571 | -60.3149 | 63.2584 | -0.088261 | -0.0067575 | 0.075948 | 0.06194 | 0.0027391 | -0.013589 | -0.00069841 | 0.069594 | -0.0019776 | 0.050731 | 0.03949 | -0.0093592 | 0.0042299 | 0.0057535 | 0.009155 | 63.1897 | -60.4248 | 63.2767 | -60.3195 | -60.6491 | -0.086975 | 0.018311 | 63.2217 | -60.3561 | 63.4689 | -60.3195 | -60.434 | -60.3195 | -0.10986 | -0.068665 | 0.01831 | -0.004578 | 60.228 | -0.33417 | 60.3378 | -0.2243 | -0.041199 | -0.036621 | 0.21057 | -0.004578 | -0.004578 | -0.11902 | 0.036621 | -0.07782 | 0.10529 | 123.7015 | 0.036621 | 123.8251 | 123.6145 | 123.5779 | 123.5046 | 123.5367 | -123.6832 | -123.6145 | 123.5916 | 123.7839 | 60.3241 | 60.3333
11.4844 | 123.8754 | -60.2966 | 63.2492 | 0.094845 | -0.0024855 | 0.070607 | 0.057667 | -0.0079419 | -0.0018402 | 0.0078466 | 0.0085594 | -0.0030456 | 0.07423 | 0.076874 | 0.0013218 | -0.0096551 | 0.0036165 | -0.15106 | 63.1393 | -60.4706 | 63.3087 | -60.3561 | -60.6812 | -0.07782 | 0.004578 | 63.1851 | -60.3836 | 63.5101 | -60.3195 | -60.4294 | -60.3195 | -0.17395 | -0.10986 | 0.059509 | -0.059509 | 60.2188 | -0.38452 | 60.3928 | -0.21057 | -0.086975 | -0.064087 | 0.26093 | -0.022888 | -0.022888 | -0.13275 | 0.064087 | -0.045776 | 0.11444 | 123.7793 | 0.064087 | 123.8937 | 123.6099 | 123.5687 | 123.436 | 123.4818 | -123.7198 | -123.6328 | 123.6053 | 123.8068 | 60.1456 | 60.3012
12.4844 | 124.0814 | -60.2371 | 63.3499 | 0.1101 | 0.00071953 | 0.059926 | 0.059804 | -0.015419 | -0.017862 | -0.0060384 | 0.10011 | -0.0041136 | 0.052867 | 0.070465 | -0.00081422 | -0.0053831 | 0.0014805 | 0.045776 | 63.2217 | -60.4065 | 63.3362 | -60.3058 | -60.6537 | -0.059509 | 0.17395 | 63.2492 | -60.2966 | 63.5284 | -60.2371 | -60.3516 | -60.466 | -0.16937 | -0.12817 | -0.013733 | -0.068664 | 60.1776 | -0.41656 | 60.347 | -0.24719 | -0.059509 | -0.10071 | 0.17853 | 0 | -0.22888 | -0.11444 | -0.16937 | -0.054931 | 0.10071 | 123.7427 | 0.059509 | 123.8251 | 123.6282 | 123.5458 | 123.4589 | 123.4863 | -123.7564 | -123.6465 | 123.5733 | 123.7656 | 60.2829 | 60.4111
13.4844 | 123.8754 | -60.3287 | 63.2675 | 0.0032924 | 0.00071953 | 0.072743 | 0.065144 | -0.0036699 | -0.0061122 | 0.0089146 | 0.11537 | -0.0062496 | 0.068889 | 0.050171 | 0.00025378 | -0.0064511 | -0.0027915 | -0.036621 | 63.2217 | -60.4202 | 63.3041 | -60.3287 | -60.6583 | -0.09613 | 0.018311 | 63.1943 | -60.3378 | 63.4552 | -60.3287 | -60.4568 | -60.3149 | -0.091553 | -0.045776 | 0.036621 | 0 | 60.2325 | -0.32959 | 60.3241 | -0.23804 | -0.009156 | -0.073242 | 0.18768 | 0 | 0.013733 | -0.12817 | 0.022889 | -0.11902 | 0.091553 | 123.7244 | 0.009156 | 123.793 | 123.642 | 123.5321 | 123.5504 | 123.5229 | -123.6877 | -123.6053 | 123.6328 | 123.7839 | 60.2921 | 60.347
14.4844 | 123.912 | -60.2966 | 63.2629 | 0.064327 | 0.00071953 | 0.064198 | 0.060872 | 0.0038071 | -0.0082492 | -0.0060384 | -0.067735 | 0.0022944 | 0.06248 | 0.071533 | 0.0087988 | -4.2099e-05 | 0.0046845 | -0.032043 | 63.1943 | -60.4202 | 63.3453 | -60.3058 | -60.6445 | -0.09613 | 0 | 63.2217 | -60.3561 | 63.4186 | -60.0906 | -60.3653 | -60.3058 | -0.1236 | -0.068664 | 0.082398 | -0.009155 | 60.2005 | -0.3479 | 60.3241 | -0.2243 | -0.059509 | -0.041198 | 0.15564 | 0.20599 | -0.009155 | -0.068664 | 0.050354 | -0.009155 | 0.11444 | 123.7656 | 0.2655 | 123.7747 | 123.6145 | 123.5779 | 123.4909 | 123.5184 | -123.6832 | -123.6191 | 123.642 | 123.7152 | 60.2646 | 60.2966
15.4844 | 123.9304 | -60.2875 | 63.1897 | 0.17114 | -0.0078255 | 0.055654 | 0.06194 | -0.015419 | -0.0018402 | 0.0057106 | -0.037217 | 0.0054994 | 0.076366 | 0.095032 | -0.00081422 | 0.0063669 | 0.0089575 | -0.064087 | 63.208 | -60.4385 | 63.3545 | -60.2554 | -60.5988 | -0.082397 | 0.004578 | 63.2126 | -60.379 | 63.4918 | -60.3378 | -60.4385 | -60.3058 | -0.15106 | 0.018311 | 0.16479 | 0.032044 | 60.2051 | -0.31128 | 60.3561 | -0.16022 | -0.091552 | 0.022888 | 0.30212 | -0.050354 | -0.01831 | -0.15106 | 0.073242 | -0.05951 | 0.18311 | 123.793 | 0.041198 | 123.8708 | 123.6465 | 123.5916 | 123.4955 | 123.5001 | -123.6282 | -123.5687 | 123.642 | 123.7793 | 60.2234 | 60.2921
16.4844 | 123.8846 | -60.2966 | 63.2309 | 0.018551 | 0.0039235 | 0.071675 | 0.052327 | -0.0047379 | 0.010977 | -0.0017664 | -0.067735 | -0.0041136 | 0.060344 | 0.072601 | 0.0077308 | 0.0085029 | 0.016434 | -0.17853 | 63.1348 | -60.498 | 63.3041 | -60.347 | -60.6812 | -0.064087 | 0.009155 | 63.1943 | -60.3882 | 63.4872 | -60.3104 | -60.434 | -60.3195 | -0.20142 | -0.09613 | 0.073242 | -0.050354 | 60.2325 | -0.38452 | 60.434 | -0.1831 | -0.091553 | -0.036621 | 0.25635 | -0.013733 | -0.022888 | -0.13733 | 0.068665 | -0.045776 | 0.15106 | 123.8022 | 0.07782 | 123.8754 | 123.6328 | 123.5825 | 123.4314 | 123.4909 | -123.7289 | -123.6191 | 123.6008 | 123.7839 | 60.1181 | 60.3058
17.4844 | 123.8571 | -60.2921 | 63.295 | 0.15588 | 0.0071275 | 0.05779 | 0.052327 | 0.0027391 | 0.01525 | -0.011379 | 0.10011 | 0.0022944 | 0.066753 | 0.018127 | -0.0061552 | -0.0053831 | -0.014542 | -0.009155 | 63.2217 | -60.4065 | 63.3545 | -60.2509 | -60.6125 | -0.022888 | 0.041199 | 63.2172 | -60.3516 | 63.4872 | -60.2829 | -60.4019 | -60.2966 | -0.11444 | -0.073242 | 0.059509 | 0.041199 | 60.2692 | -0.32043 | 60.3836 | -0.20599 | -0.059509 | -0.07782 | 0.19226 | 0.009155 | -0.004578 | -0.10986 | 0.054931 | -0.050355 | 0.15564 | 123.761 | 0.068664 | 123.8388 | 123.6282 | 123.5687 | 123.5138 | 123.5092 | -123.7015 | -123.6465 | 123.6465 | 123.7793 | 60.2829 | 60.3333
18.4844 | 123.8571 | -60.3333 | 63.2538 | 0.03381 | -0.0035535 | 0.064198 | 0.06728 | 0.0070111 | 0.019522 | 0.0035746 | -0.021958 | 0.00015838 | 0.063548 | 0.082214 | -0.00081422 | -0.0011101 | 0.014297 | -0.022888 | 63.1622 | -60.4614 | 63.327 | -60.3195 | -60.6583 | -0.09613 | -0.16479 | 63.1531 | -60.379 | 63.4598 | -60.2783 | -60.4431 | -60.3195 | -0.12817 | -0.091553 | 0.073242 | 0.013733 | 60.2371 | -0.32501 | 60.3653 | -0.19684 | -0.045776 | -0.10071 | 0.20599 | 0.054932 | 0.013733 | -0.10986 | 0.059509 | -0.064087 | 0.14191 | 123.7885 | 0.10071 | 123.8388 | 123.6237 | 123.5321 | 123.4955 | 123.4863 | -123.7152 | -123.6328 | 123.6603 | 123.793 | 60.3104 | 60.1685
19.4844 | 123.8983 | -60.2646 | 63.2767 | 0.0032924 | -0.0046215 | 0.071675 | 0.06194 | 0.0027391 | 0.0013638 | 0.013188 | 0.023818 | 0.0033634 | 0.060344 | 0.065124 | -0.0040182 | 0.0095709 | 0.017502 | -0.032043 | 63.208 | -60.434 | 63.3408 | -60.3241 | -60.6491 | -0.09613 | -0.009155 | 63.1897 | -60.3928 | 63.446 | -60.1044 | -60.3745 | -60.3058 | -0.16937 | -0.068664 | 0.064087 | -0.05951 | 60.1685 | -0.38452 | 60.3378 | -0.21515 | -0.12817 | -0.086975 | 0.16937 | 0.16022 | -0.041199 | -0.10986 | 0.086975 | 0.01831 | 0.10986 | 123.7747 | 0.28839 | 123.8388 | 123.642 | 123.5825 | 123.4726 | 123.4543 | -123.7106 | -123.6694 | 123.6053 | 123.7106 | 60.2325 | 60.2554
20.4844 | 123.8434 | -60.3104 | 63.2263 | -0.073002 | -0.0014175 | 0.068471 | 0.052327 | 0.0006031 | 0.0088408 | -0.0028344 | 0.069594 | 0.0044314 | 0.068889 | 0.050171 | -0.0029502 | -0.0053831 | 0.0025485 | -0.050354 | 63.1714 | -60.4294 | 63.2996 | -60.3195 | -60.6445 | -0.082397 | 0.013733 | 63.2172 | -60.3333 | 63.4689 | -60.3287 | -60.4294 | -60.3149 | -0.11902 | -0.054931 | 0.073243 | -0.009155 | 60.228 | -0.33417 | 60.347 | -0.21515 | -0.022888 | -0.009155 | 0.24262 | -0.01831 | -0.004577 | -0.11902 | 0.018311 | -0.09613 | 0.10986 | 123.7289 | 0.004578 | 123.8022 | 123.6008 | 123.5504 | 123.4818 | 123.5275 | -123.6557 | -123.5596 | 123.6099 | 123.7793 | 60.26 | 60.3241
21.4844 | 123.8617 | -60.3012 | 63.2401 | -0.057743 | -0.0035535 | 0.06313 | 0.055531 | 0.010216 | 0.0067048 | -0.0092424 | 0.0085594 | 0.0044314 | 0.060344 | 0.075805 | -0.00081422 | 0.0052979 | -0.010269 | -0.07782 | 63.2126 | -60.4614 | 63.3499 | -60.2829 | -60.6216 | -0.064087 | -0.013733 | 63.2355 | -60.3699 | 63.4644 | -60.3424 | -60.466 | -60.3195 | -0.16022 | -0.027466 | 0.10986 | 0.01831 | 60.2371 | -0.32043 | 60.3973 | -0.16022 | -0.068665 | -0.004577 | 0.2243 | -0.041199 | -0.018311 | -0.16479 | 0.050354 | -0.09613 | 0.17853 | 123.8113 | 0.027466 | 123.8342 | 123.674 | 123.6053 | 123.5138 | 123.5367 | -123.7015 | -123.6099 | 123.6511 | 123.7656 | 60.2234 | 60.2875
22.4844 | 123.8297 | -60.3149 | 63.2629 | 0.1101 | 0.0017875 | 0.066335 | 0.059804 | -0.0004649 | -0.00077219 | 0.0089146 | 0.054336 | -0.0051816 | 0.068889 | 0.050171 | 0.0034578 | -4.2099e-05 | 0.012161 | -0.045776 | 63.1622 | -60.4294 | 63.3224 | -60.3287 | -60.64 | -0.091553 | 0.022888 | 63.1943 | -60.3607 | 63.446 | -60.3287 | -60.466 | -60.3378 | -0.11444 | -0.10071 | 0.05951 | -0.013733 | 60.2234 | -0.32501 | 60.3378 | -0.21057 | -0.045777 | -0.068664 | 0.18311 | -0.013733 | -0.022889 | -0.15106 | 0.022888 | -0.10529 | 0.10071 | 123.7518 | 0.032044 | 123.8068 | 123.5916 | 123.555 | 123.4772 | 123.5092 | -123.6923 | -123.6237 | 123.6374 | 123.761 | 60.2692 | 60.3378
23.4844 | 123.88 | -60.3241 | 63.2446 | 0.018551 | 0.0049915 | 0.072743 | 0.056599 | -0.0090099 | -0.0029082 | -0.0060384 | 0.40529 | 0.0012264 | 0.069957 | 0.085418 | -0.0061552 | -0.0064511 | 0.0068215 | -0.050354 | 63.1805 | -60.4614 | 63.3087 | -60.2463 | -60.7819 | -0.31586 | -0.009155 | 63.2126 | -60.3195 | 63.4323 | -60.347 | -60.4294 | -60.3058 | -0.13733 | -0.064087 | 0.064087 | 0.07782 | 60.0082 | -0.45776 | 60.1456 | -0.32043 | 0.004578 | -0.032044 | 0.18768 | -0.022888 | 0.018311 | -0.10528 | 0.013733 | -0.10986 | 0.21515 | 123.7701 | -0.027466 | 123.7518 | 123.642 | 123.5321 | 123.5046 | 123.5367 | -123.7061 | -123.5641 | 123.6328 | 123.7564 | 60.2737 | 60.3149
24.4844 | 123.8297 | -60.3149 | 63.2126 | 0.03381 | 0.0039235 | 0.077016 | 0.060872 | 0.012352 | 0.0067048 | 0.0025066 | -0.037217 | 0.0076354 | 0.068889 | 0.083282 | 0.0013218 | 0.0052979 | 0.013229 | -0.086975 | 63.176 | -60.4568 | 63.3087 | -60.3195 | -60.6583 | -0.086975 | -0.32044 | 63.1393 | -60.4111 | 63.4644 | -60.3104 | -60.4111 | -60.2829 | -0.14191 | -0.036621 | 0.096131 | -0.004578 | 60.228 | -0.34332 | 60.3699 | -0.20142 | -0.096131 | -0.073242 | 0.25177 | 0.004577 | 0.032043 | -0.096131 | 0.12817 | 0 | 0.13733 | 123.7656 | 0.10071 | 123.8754 | 123.6328 | 123.5504 | 123.4909 | 123.4543 | -123.6694 | -123.6237 | 123.6237 | 123.7793 | 60.228 | 59.9945
25.4844 | 123.8388 | -60.2966 | 63.2584 | 0.1101 | -0.00034947 | 0.065267 | 0.072621 | 0.010216 | -0.015725 | -0.0060384 | 0.023818 | -0.0019776 | 0.056072 | 0.068329 | -0.0082912 | -0.016064 | 0.0057535 | -0.054932 | 63.176 | -60.4248 | 63.3316 | -60.2875 | -60.64 | -0.10071 | -0.009155 | 63.1989 | -60.3561 | 63.6108 | -60.3333 | -60.379 | -60.3012 | -0.12817 | -0.082398 | 0.073242 | 0.009155 | 60.1959 | -0.34332 | 60.3241 | -0.21515 | -0.059509 | -0.059509 | 0.35248 | -0.036621 | -0.004577 | -0.082397 | 0.054932 | -0.022888 | 0.13733 | 123.7564 | 0.022888 | 123.967 | 123.6008 | 123.555 | 123.4726 | 123.4955 | -123.6832 | -123.6145 | 123.6282 | 123.9075 | 60.2417 | 60.2875
26.4844 | 123.8709 | -60.3149 | 63.2675 | 0.018551 | 0.0039235 | 0.059926 | 0.069417 | -0.014351 | -0.0029082 | -0.0060384 | 0.054336 | 0.0033634 | 0.063548 | 0.070465 | -0.0040182 | -0.0043151 | 0.016434 | -0.086975 | 63.1622 | -60.4385 | 63.3224 | -60.3104 | -60.6262 | -0.10071 | 0.009155 | 63.2126 | -60.3836 | 63.4644 | -60.3195 | -60.4431 | -60.3104 | -0.1236 | -0.10529 | 0.054932 | 0.004577 | 60.2142 | -0.31128 | 60.3378 | -0.18768 | -0.068665 | -0.054932 | 0.19684 | -0.004578 | 0.004577 | -0.12817 | 0.073242 | -0.059509 | 0.12817 | 123.761 | 0.064087 | 123.848 | 123.6008 | 123.5962 | 123.4772 | 123.5275 | -123.7061 | -123.6511 | 123.6374 | 123.7793 | 60.228 | 60.3241
27.4844 | 123.8205 | -60.3104 | 63.2812 | 0.049069 | 0.0049915 | 0.056722 | 0.057667 | -0.012215 | 0.0056368 | 0.0078466 | 0.22218 | -0.0030456 | 0.063548 | 0.03949 | 0.0034578 | -0.0011101 | 0.0089575 | -0.064087 | 63.2034 | -60.434 | 63.3682 | -60.2325 | -60.585 | -0.041199 | -0.054932 | 63.2217 | -60.3561 | 63.4323 | -60.4477 | -60.4523 | -60.3241 | -0.1236 | -0.07782 | 0.086975 | 0.07782 | 60.2692 | -0.27466 | 60.3928 | -0.15106 | -0.045776 | -0.059509 | 0.15106 | -0.13733 | -0.013733 | -0.14191 | 0.032043 | -0.096131 | 0.20142 | 123.8022 | -0.091553 | 123.7885 | 123.6374 | 123.5779 | 123.5138 | 123.5321 | -123.7152 | -123.6374 | 123.6786 | 123.7427 | 60.2463 | 60.2554
28.4844 | 123.8617 | -60.3241 | 63.1989 | 0.03381 | 0.0028555 | 0.064198 | 0.06194 | 0.0080791 | 0.0077728 | -0.013515 | -0.082994 | 0.0012264 | 0.067821 | 0.08435 | 0.0013218 | -0.0032471 | 0.0078895 | -0.086975 | 63.1897 | -60.4523 | 63.3591 | -60.2737 | -60.6033 | -0.068665 | -0.022888 | 63.1989 | -60.3516 | 63.4781 | -60.3378 | -60.4385 | -60.3104 | -0.12817 | -0.009156 | 0.16022 | 0.050354 | 60.2554 | -0.27924 | 60.3836 | -0.15106 | -0.027465 | 0 | 0.27923 | -0.013733 | 0.013733 | -0.11444 | 0.041198 | -0.086976 | 0.17853 | 123.8113 | 0.013732 | 123.8297 | 123.642 | 123.5504 | 123.5138 | 123.523 | -123.6511 | -123.5504 | 123.6832 | 123.8022 | 60.2371 | 60.3012
29.4844 | 123.8571 | -60.3149 | 63.2446 | -0.45447 | 0.0039235 | 0.060994 | 0.054463 | -0.013283 | 0.0056368 | -0.0049704 | 0.084853 | 0.00015838 | 0.05714 | 0.048034 | 0.0034578 | -0.0053831 | -0.0017235 | 0.09613 | 63.1622 | -60.4111 | 63.3224 | -60.3012 | -60.6628 | -0.15106 | 0.013733 | 63.2034 | -60.3653 | 63.4827 | -60.3241 | -60.434 | -60.3195 | -0.096131 | -0.082398 | 0.07782 | 0.013733 | 60.1639 | -0.3479 | 60.26 | -0.25177 | -0.050354 | -0.041199 | 0.23804 | -0.009156 | -0.004578 | -0.11902 | 0.045776 | -0.068665 | 0.10986 | 123.7335 | 0.041198 | 123.848 | 123.5733 | 123.5687 | 123.4772 | 123.5184 | -123.6557 | -123.6099 | 123.6374 | 123.7976 | 60.4111 | 60.3287
30.4844 | 123.8571 | -60.3058 | 63.2584 | -0.027225 | 0.0039235 | 0.060994 | 0.06728 | -0.0015339 | -0.0061122 | -0.00069841 | 0.10011 | 0.0012264 | 0.066753 | 0.097168 | -0.0050872 | -0.0032471 | -0.027359 | -0.018311 | 63.1851 | -60.4477 | 63.4277 | -60.3699 | -60.6491 | -0.11444 | -0.022888 | 63.1989 | -60.379 | 63.4872 | -60.3058 | -60.4156 | -60.2646 | -0.14191 | -0.073242 | 0.16937 | -0.064087 | 60.1913 | -0.34332 | 60.3333 | -0.20142 | -0.073242 | -0.059509 | 0.22888 | 0 | 0.041199 | -0.10986 | 0.11444 | -0.036621 | 0.07782 | 123.8754 | 0.073242 | 123.8663 | 123.6328 | 123.5779 | 123.4909 | 123.5046 | -123.7061 | -123.6374 | 123.7335 | 123.793 | 60.2875 | 60.2829
31.4844 | 123.8892 | -60.3149 | 63.2538 | 0.24743 | -0.0067575 | 0.068471 | 0.070485 | -0.015419 | 0.014182 | -0.0028344 | -0.22032 | -0.0062496 | 0.060344 | 0.067261 | 0.0077308 | -0.0053831 | -0.012405 | -0.041199 | 63.1485 | -60.4385 | 63.3408 | -60.498 | -60.9009 | -0.036621 | 0.036621 | 63.2355 | -60.3653 | 63.446 | -60.3195 | -60.4248 | -60.2921 | -0.1236 | -0.10529 | 0.086975 | -0.18311 | 60.2783 | -0.58594 | 60.4019 | -0.46234 | -0.050354 | -0.01831 | 0.19226 | -0.004578 | 0.022888 | -0.10986 | 0.073242 | -0.05951 | -0.059509 | 123.7793 | 0.045776 | 123.8113 | 123.587 | 123.6008 | 123.4634 | 123.5504 | -123.6923 | -123.6191 | 123.6557 | 123.761 | 60.2737 | 60.3516
32.4844 | 123.8205 | -60.3149 | 63.2767 | -0.027225 | -0.014234 | 0.066335 | 0.072621 | -0.0026019 | 0.023795 | 0.0014386 | 0.14589 | -0.0019776 | 0.051799 | 0.014923 | 0.0055948 | -0.0053831 | 0.012161 | -0.059509 | 63.2217 | -60.434 | 63.3499 | -60.2875 | -60.6033 | 0.013733 | -0.041199 | 63.2263 | -60.3561 | 63.3957 | -60.379 | -60.434 | -60.3378 | -0.11902 | -0.054931 | 0.073243 | 0.027465 | 60.3287 | -0.28839 | 60.4477 | -0.16937 | -0.041199 | -0.050354 | 0.11902 | -0.064087 | -0.022889 | -0.11902 | 0.01831 | -0.07782 | 0.14648 | 123.7839 | -0.022888 | 123.7518 | 123.6557 | 123.5825 | 123.5367 | 123.5413 | -123.7106 | -123.6328 | 123.6649 | 123.7106 | 60.2554 | 60.2737
33.4844 | 123.8251 | -60.2966 | 63.2721 | 0.064327 | 0.0017875 | 0.069539 | 0.058736 | 0.012352 | 0.012046 | -0.0049704 | 0.054336 | -0.0051816 | 0.05714 | 0.080078 | 0.0055948 | 0.0042299 | -0.012405 | -0.054932 | 63.176 | -60.4568 | 63.327 | -60.3012 | -60.6262 | -0.068665 | -0.004578 | 63.2263 | -60.379 | 63.4415 | -60.3607 | -60.466 | -60.3424 | -0.16022 | -0.096131 | 0.054931 | -0.004577 | 60.228 | -0.32959 | 60.3882 | -0.16937 | -0.082397 | -0.045777 | 0.16937 | -0.064087 | -0.045776 | -0.16937 | 0.036621 | -0.086975 | 0.15564 | 123.7839 | 0.01831 | 123.8205 | 123.6328 | 123.6053 | 123.4726 | 123.5229 | -123.7289 | -123.6511 | 123.6237 | 123.7381 | 60.2417 | 60.2921
34.4844 | 123.7656 | -60.3058 | 63.327 | 0.14062 | -0.0046215 | 0.060994 | 0.065144 | -0.0079419 | 0.00029581 | 0.0014386 | 0.16115 | -0.0051816 | 0.071025 | 0.058716 | 0.010935 | -0.0011101 | 0.0078895 | 0.059509 | 63.2217 | -60.4156 | 63.414 | -60.2142 | -60.5484 | 0.050354 | 0.013733 | 63.2675 | -60.3516 | 63.382 | -60.379 | -60.3973 | -60.3241 | -0.10986 | -0.10528 | 0.086975 | 0.091553 | 60.3561 | -0.24262 | 60.466 | -0.13275 | -0.045776 | -0.059509 | 0.054932 | -0.073242 | -0.018311 | -0.091553 | 0.027465 | -0.045777 | 0.20142 | 123.8297 | -0.027466 | 123.7335 | 123.6374 | 123.6191 | 123.5275 | 123.5733 | -123.7427 | -123.6786 | 123.7198 | 123.6877 | 60.3653 | 60.3195
35.4844 | 123.8617 | -60.2921 | 63.2584 | 0.0032924 | 0.00071953 | 0.056722 | 0.066212 | 0.0006031 | -0.019998 | 0.016392 | -0.021958 | -0.0083866 | 0.060344 | 0.057647 | 0.0013218 | 0.0074349 | -0.0081325 | -0.086975 | 63.2034 | -60.4523 | 63.3774 | -60.2554 | -60.6033 | -0.073242 | -0.032043 | 63.2217 | -60.347 | 63.4506 | -60.3287 | -60.4477 | -60.3104 | -0.16022 | -0.054932 | 0.11902 | 0.036621 | 60.2188 | -0.31128 | 60.379 | -0.15106 | -0.054932 | -0.036621 | 0.19226 | -0.036621 | -0.018311 | -0.15564 | 0.036621 | -0.10071 | 0.19684 | 123.8297 | 0.018311 | 123.7976 | 123.6557 | 123.5687 | 123.4955 | 123.5138 | -123.7106 | -123.6053 | 123.6694 | 123.7427 | 60.2051 | 60.26
36.4844 | 123.8754 | -60.3058 | 63.2629 | 0.094845 | 0.00071953 | 0.062062 | 0.052327 | 0.0048751 | 0.0013638 | 0.0078466 | -0.082994 | -0.0051816 | 0.067821 | 0.059784 | 0.00025378 | 0.0020939 | -0.00065554 | -0.036621 | 63.1577 | -60.4202 | 63.2675 | -60.553 | -60.791 | 0.041199 | 0.022888 | 63.2172 | -60.3561 | 63.4644 | -60.3058 | -60.4294 | -60.2921 | -0.11444 | -0.10529 | 0.004578 | -0.24719 | 60.347 | -0.48523 | 60.4614 | -0.37079 | -0.050354 | -0.045776 | 0.20142 | 0 | 0.013733 | -0.1236 | 0.064087 | -0.073242 | -0.13275 | 123.6877 | 0.050354 | 123.8205 | 123.5779 | 123.5733 | 123.4634 | 123.5229 | -123.6832 | -123.6191 | 123.5733 | 123.7701 | 60.2692 | 60.3287
37.4844 | 123.8571 | -60.3012 | 63.2904 | 0.12536 | -0.00034947 | 0.05779 | 0.058736 | 0.018761 | 0.0088408 | 0.0014386 | 0.20692 | 0.0097714 | 0.069957 | 0.048034 | -0.00081422 | 0.0042299 | 0.0057535 | 0.018311 | 63.2309 | -60.3836 | 63.3362 | -60.3012 | -60.6171 | -0.054932 | 0.10986 | 63.2538 | -60.347 | 63.5147 | -60.2463 | -60.3653 | -60.2829 | -0.082398 | -0.059509 | 0.045777 | 0 | 60.2463 | -0.31586 | 60.3287 | -0.23346 | -0.045777 | -0.036621 | 0.2243 | 0.054931 | 0.01831 | -0.064087 | 0.064087 | -0.01831 | 0.082398 | 123.7198 | 0.10071 | 123.8617 | 123.6145 | 123.6008 | 123.5321 | 123.555 | -123.674 | -123.6374 | 123.6374 | 123.8159 | 60.3195 | 60.4111
38.4844 | 123.8709 | -60.3561 | 63.2629 | 0.1101 | -0.0024855 | 0.06313 | 0.065144 | -0.0090099 | -0.013589 | -0.0081744 | 0.084853 | 0.0054994 | 0.053935 | 0.076874 | 0.0034578 | 0.0052979 | -0.011337 | -0.073242 | 63.1943 | -60.4248 | 63.2675 | -60.3333 | -60.6491 | -0.07782 | -0.009155 | 63.208 | -60.379 | 63.4598 | -60.3104 | -60.5484 | -60.5621 | -0.068665 | -0.068664 | 0.004578 | 0.022888 | 60.2783 | -0.29297 | 60.347 | -0.2243 | -0.022888 | -0.054931 | 0.19684 | 0.045776 | -0.20599 | -0.19226 | -0.18311 | -0.16937 | 0.091553 | 123.6923 | 0.068664 | 123.8388 | 123.6191 | 123.587 | 123.5504 | 123.5641 | -123.6877 | -123.642 | 123.6237 | 123.8159 | 60.2829 | 60.347
39.4844 | 123.8342 | -60.2829 | 63.3179 | 0.20166 | -0.0035535 | 0.06313 | 0.063008 | 0.012352 | 0.0035008 | -0.0039024 | 0.20692 | 0.0054994 | 0.065685 | 0.068329 | 0.0055948 | 0.0010259 | -0.011337 | 0.064087 | 63.1989 | -60.3836 | 63.3316 | -60.2875 | -60.6125 | -0.013733 | 0.09613 | 63.2538 | -60.3378 | 63.4781 | -60.2737 | -60.3928 | -60.2875 | -0.10071 | -0.11902 | 0.013733 | -0.004578 | 60.2692 | -0.32959 | 60.3699 | -0.22888 | -0.054932 | -0.064087 | 0.16022 | 0.009155 | -0.004578 | -0.10986 | 0.050354 | -0.054931 | 0.09613 | 123.7152 | 0.064087 | 123.8159 | 123.5825 | 123.5916 | 123.4818 | 123.5367 | -123.7015 | -123.6557 | 123.6145 | 123.761 | 60.347 | 60.379
40.4844 | 123.8617 | -60.3058 | 63.2538 | 0.064327 | 0.0049915 | 0.062062 | 0.059804 | 0.0016711 | -0.010385 | -0.0049704 | 0.54262 | -0.0019776 | 0.061412 | 0.059784 | -0.0029502 | 0.011707 | -0.0081325 | -0.022888 | 63.1714 | -60.4202 | 63.2996 | -60.3241 | -60.6033 | -0.3067 | 0.004578 | 63.2309 | -60.3607 | 63.4323 | -60.3516 | -60.434 | -60.3058 | -0.11444 | -0.082397 | 0.045777 | -0.018311 | 59.9991 | -0.29755 | 60.1135 | -0.18311 | -0.054932 | -0.022888 | 0.17853 | -0.045776 | 0 | -0.12817 | 0.054932 | -0.073242 | 0.09613 | 123.7198 | 0.009156 | 123.793 | 123.5916 | 123.5916 | 123.4772 | 123.5367 | -123.674 | -123.6145 | 123.6053 | 123.7381 | 60.2829 | 60.3104
41.4844 | 123.8617 | -60.3012 | 63.2629 | 0.0032924 | 0.0039235 | 0.062062 | 0.064076 | -0.015419 | 0.0099088 | -0.00069841 | 0.039077 | 0.00015838 | 0.072093 | 0.06192 | -0.011495 | -0.0085871 | -0.012405 | -0.050354 | 63.1668 | -60.4477 | 63.3041 | -60.3012 | -60.6491 | -0.11444 | -0.004578 | 63.1989 | -60.3516 | 63.6292 | -60.3104 | -60.3653 | -60.2554 | -0.14648 | -0.09613 | 0.041199 | 0 | 60.1868 | -0.3479 | 60.3333 | -0.20142 | -0.050354 | -0.064086 | 0.36621 | -0.009156 | 0.045776 | -0.064087 | 0.09613 | -0.013733 | 0.14648 | 123.7518 | 0.041198 | 123.9807 | 123.6145 | 123.5504 | 123.468 | 123.5001 | -123.7106 | -123.6145 | 123.6053 | 123.9304 | 60.2509 | 60.2966
42.4844 | 123.848 | -60.2966 | 63.2675 | 0.24743 | 0.0071275 | 0.06313 | 0.060872 | -0.0036699 | 0.0056368 | 0.013188 | 0.22218 | -0.00090962 | 0.05714 | 0.052307 | 0.010935 | -0.0032471 | 0.0057535 | -0.041199 | 63.208 | -60.4294 | 63.382 | -60.2234 | -60.5804 | -0.027466 | -0.018311 | 63.2355 | -60.3561 | 63.4415 | -60.3241 | -60.4248 | -60.3378 | -0.13275 | -0.059509 | 0.11444 | 0.073242 | 60.2692 | -0.28381 | 60.4019 | -0.15106 | -0.059509 | -0.032043 | 0.17395 | -0.027466 | -0.041199 | -0.12817 | 0.01831 | -0.068665 | 0.20599 | 123.8113 | 0.032043 | 123.7976 | 123.6374 | 123.5916 | 123.5046 | 123.5321 | -123.6969 | -123.6237 | 123.6786 | 123.7381 | 60.2554 | 60.2783
43.4844 | 123.8709 | -60.3149 | 63.2584 | 0.0032924 | 0.0049915 | 0.068471 | 0.059804 | 0.012352 | -0.0061122 | -0.010311 | -0.1898 | 0.0012264 | 0.05714 | 0.049103 | -0.0029502 | 0.0020939 | -0.0081325 | -0.07782 | 63.1943 | -60.4431 | 63.3316 | -60.2737 | -60.6079 | -0.041199 | -0.004578 | 63.1989 | -60.3882 | 63.4781 | -60.3149 | -60.4523 | -60.2966 | -0.12817 | -0.064087 | 0.073242 | 0.041198 | 60.2737 | -0.29297 | 60.4019 | -0.16479 | -0.073243 | -0.059509 | 0.21973 | 0 | 0.01831 | -0.13733 | 0.091553 | -0.064087 | 0.16937 | 123.7747 | 0.073243 | 123.8663 | 123.6374 | 123.587 | 123.5092 | 123.5138 | -123.7015 | -123.6465 | 123.6465 | 123.793 | 60.2371 | 60.3104
44.4844 | 123.848 | -60.228 | 63.3087 | 0.079586 | 0.00071953 | 0.056722 | 0.049123 | -0.010078 | 0.0077728 | -0.0081744 | 0.28322 | -0.0073186 | 0.082775 | 0.077942 | 0.0023898 | -0.0011101 | -0.0070645 | 0.045776 | 63.2172 | -60.4019 | 63.3545 | -60.3058 | -60.6491 | -0.059509 | 0.15564 | 63.2446 | -60.3287 | 63.501 | -60.2509 | -60.0037 | -59.9167 | -0.17395 | -0.091553 | 0.045776 | -0.07782 | 60.1685 | -0.42114 | 60.3424 | -0.24719 | -0.10071 | -0.064087 | 0.19226 | -0.022888 | 0.31128 | 0.2243 | 0.41199 | 0.32501 | 0.096131 | 123.7564 | 0.07782 | 123.8297 | 123.6191 | 123.5733 | 123.4451 | 123.4726 | -123.7106 | -123.6374 | 123.5825 | 123.7289 | 60.2737 | 60.3836
45.4844 | 123.8205 | -60.3287 | 63.2629 | 0.20166 | 0.0049915 | 0.067403 | 0.072621 | 0.019829 | -0.0018402 | 0.01212 | -0.11351 | 0.0022944 | 0.053935 | 0.065124 | 0.00025378 | 0.0052979 | -0.0017235 | -0.086975 | 63.1805 | -60.4797 | 63.3911 | -60.2142 | -60.5667 | -0.036621 | -0.07782 | 63.2217 | -60.3882 | 63.4415 | -60.3378 | -60.4614 | -60.2737 | -0.15106 | -0.082397 | 0.12817 | 0.11444 | 60.2921 | -0.23804 | 60.4431 | -0.086975 | -0.05951 | -0.041198 | 0.17853 | -0.009156 | 0.054931 | -0.13275 | 0.11444 | -0.073242 | 0.2655 | 123.8708 | 0.050354 | 123.8297 | 123.6603 | 123.6099 | 123.5092 | 123.5504 | -123.7427 | -123.6511 | 123.7198 | 123.7701 | 60.2417 | 60.2509
46.4844 | 123.8297 | -60.3149 | 63.2721 | 0.049069 | 0.0028555 | 0.065267 | 0.053395 | 0.0091481 | 0.0088408 | 0.0025066 | -0.082994 | 0.0065674 | 0.064617 | 0.082214 | -0.00081422 | -0.0011101 | -0.0049285 | -0.11902 | 63.2172 | -60.4477 | 63.4186 | -60.2188 | -60.5759 | -0.018311 | -0.082397 | 63.2401 | -60.379 | 63.4232 | -60.379 | -60.4752 | -60.3378 | -0.13275 | -0.054932 | 0.14648 | 0.09613 | 60.2966 | -0.26093 | 60.4294 | -0.12817 | -0.064087 | -0.032044 | 0.15106 | -0.064087 | -0.022889 | -0.16022 | 0.041198 | -0.096131 | 0.22888 | 123.8663 | 0 | 123.8022 | 123.6649 | 123.6191 | 123.5321 | 123.555 | -123.7198 | -123.6511 | 123.7335 | 123.7381 | 60.1959 | 60.2325
47.4844 | 123.848 | -60.3195 | 63.2721 | 0.1101 | 0.0017875 | 0.06313 | 0.06194 | 0.015556 | -0.0082492 | -0.0081744 | 0.23744 | 0.0033634 | 0.064617 | 0.057647 | 0.01414 | -0.0075191 | -0.0038605 | -0.027466 | 63.2217 | -60.3973 | 63.3682 | -60.2509 | -60.5759 | -0.027466 | -0.022888 | 63.1989 | -60.3607 | 63.4369 | -60.3333 | -60.4202 | -60.3287 | -0.07782 | -0.050354 | 0.09613 | 0.068665 | 60.2921 | -0.25635 | 60.3699 | -0.17853 | -0.041199 | -0.073242 | 0.16479 | -0.013733 | -0.009155 | -0.10071 | 0.032044 | -0.059509 | 0.14649 | 123.7656 | 0.027466 | 123.7976 | 123.6191 | 123.5596 | 123.5413 | 123.5184 | -123.6694 | -123.6328 | 123.6877 | 123.7564 | 60.2921 | 60.2966
48.4844 | 123.7564 | -60.3378 | 63.2721 | 0.03381 | -0.0014175 | 0.06313 | 0.065144 | -0.011147 | -0.0061122 | 0.0025066 | -0.15929 | 0.0097714 | 0.068889 | 0.097168 | 0.0034578 | 0.0085029 | 0.011093 | -0.10071 | 63.2126 | -60.4706 | 63.4186 | -60.1776 | -60.5301 | 0.004578 | -0.091553 | 63.2309 | -60.379 | 63.382 | -60.4019 | -60.5301 | -60.3745 | -0.13275 | -0.05951 | 0.14648 | 0.16022 | 60.3424 | -0.19226 | 60.4752 | -0.059509 | -0.041198 | -0.041199 | 0.10986 | -0.064087 | -0.036621 | -0.19226 | 0.004577 | -0.15106 | 0.29297 | 123.8892 | -0.022889 | 123.761 | 123.6832 | 123.6099 | 123.5504 | 123.5687 | -123.7427 | -123.6511 | 123.7564 | 123.7198 | 60.2371 | 60.2463
49.4844 | 123.9075 | -60.2829 | 63.2812 | 0.1101 | -0.0035535 | 0.06313 | 0.052327 | -0.014351 | -0.01893 | 0.013188 | 0.29848 | -0.0019776 | 0.068889 | 0.0085137 | -0.0040182 | 0.020252 | 0.0046845 | 0.022888 | 63.2172 | -60.4111 | 63.3041 | -60.3104 | -60.6354 | -0.050354 | 0.1236 | 63.2629 | -60.3333 | 63.2538 | -60.2188 | -60.4706 | -60.3378 | -0.12817 | -0.064087 | 0.022888 | -0.027466 | 60.2325 | -0.35248 | 60.3607 | -0.2243 | -0.050354 | -0.018311 | -0.027466 | 0.064087 | -0.054932 | -0.18768 | -0.004578 | -0.13733 | 0.10071 | 123.7152 | 0.11444 | 123.587 | 123.6282 | 123.5962 | 123.5001 | 123.5458 | -123.6923 | -123.6145 | 123.587 | 123.5367 | 60.3058 | 60.4065
50.4844 | 123.8297 | -60.3241 | 63.2721 | 0.018551 | -0.0067575 | 0.06313 | 0.060872 | -0.0047379 | -0.017862 | 0.011052 | -0.052476 | 0.0033634 | 0.080638 | 0.073669 | -0.011495 | 0.0042299 | 0.0057535 | -0.10071 | 63.2034 | -60.4706 | 63.3728 | -60.2371 | -60.5942 | -0.064087 | -0.032043 | 63.2172 | -60.3699 | 63.3957 | -60.3607 | -60.4385 | -60.3012 | -0.14648 | -0.068665 | 0.10071 | 0.086975 | 60.26 | -0.27008 | 60.4065 | -0.1236 | -0.045776 | -0.054932 | 0.1236 | -0.036621 | 0.022889 | -0.11444 | 0.068665 | -0.068665 | 0.23346 | 123.8434 | 0.009155 | 123.7656 | 123.674 | 123.587 | 123.5275 | 123.5413 | -123.7427 | -123.642 | 123.6969 | 123.7198 | 60.2234 | 60.2921
51.4844 | 123.7976 | -60.2921 | 63.2492 | 0.018551 | 0.015673 | 0.069539 | 0.064076 | 0.0080791 | 0.016318 | 0.00037059 | -0.11351 | -0.0062496 | 0.067821 | 0.065124 | -0.0018822 | 0.0010259 | -0.012405 | -0.082397 | 63.2034 | -60.4477 | 63.3911 | -60.228 | -60.585 | -0.050354 | -0.059509 | 63.2172 | -60.3607 | 63.446 | -60.3424 | -60.4477 | -60.2966 | -0.15564 | -0.045777 | 0.14191 | 0.064087 | 60.2417 | -0.29297 | 60.3973 | -0.13733 | -0.068665 | -0.032044 | 0.19684 | -0.050354 | -0.004578 | -0.15564 | 0.064087 | -0.086975 | 0.21973 | 123.8388 | 0.018311 | 123.8068 | 123.6511 | 123.5779 | 123.4955 | 123.5092 | -123.6969 | -123.6099 | 123.6832 | 123.7381 | 60.2097 | 60.2325
52.4844 | 123.8251 | -60.3104 | 63.295 | 0.14062 | -0.0099625 | 0.052449 | 0.059804 | -0.0068739 | 0.0035008 | 0.013188 | -0.0066996 | -0.0019776 | 0.053935 | 0.054443 | 0.0045258 | 0.0010259 | -0.00065554 | -0.059509 | 63.2401 | -60.4065 | 63.382 | -60.2051 | -60.6628 | 0.027466 | -0.027466 | 63.2401 | -60.3653 | 63.4094 | -60.3653 | -60.4568 | -60.3287 | -0.09613 | -0.054932 | 0.086975 | 0.10529 | 60.3378 | -0.35248 | 60.434 | -0.25635 | -0.054931 | -0.054932 | 0.11444 | -0.054931 | -0.01831 | -0.14648 | 0.036621 | -0.091553 | 0.20142 | 123.7885 | 0 | 123.7747 | 123.6465 | 123.6053 | 123.5504 | 123.5504 | -123.7015 | -123.6603 | 123.6923 | 123.7198 | 60.2509 | 60.2829
53.4844 | 123.793 | -60.3333 | 63.2629 | 0.079586 | 0.0017875 | 0.05779 | 0.056599 | 0.0091481 | 0.0024328 | -0.0017664 | -0.067735 | 0.012976 | 0.068889 | 0.037353 | -0.0061552 | 0.0042299 | 0.0036165 | -0.10071 | 63.2263 | -60.4706 | 63.4048 | -60.2097 | -60.553 | -0.027466 | -0.082397 | 63.2355 | -60.3699 | 63.4369 | -60.3745 | -60.4843 | -60.3516 | -0.13733 | -0.036621 | 0.14191 | 0.1236 | 60.3058 | -0.21973 | 60.4431 | -0.082398 | -0.036621 | -0.027465 | 0.17395 | -0.041199 | -0.01831 | -0.15106 | 0.018311 | -0.11444 | 0.26093 | 123.8754 | -0.004578 | 123.8068 | 123.6969 | 123.6053 | 123.5596 | 123.5687 | -123.7335 | -123.6328 | 123.7381 | 123.7701 | 60.2325 | 60.2509
54.4844 | 123.7198 | -60.3104 | 63.327 | 0.14062 | -0.0088935 | 0.04604 | 0.059804 | -0.022896 | 0.013114 | 0.0067786 | 0.084853 | -0.0094546 | 0.068889 | 0.075805 | -0.0061552 | -0.0032471 | -0.0081325 | 0.050354 | 63.2401 | -60.4111 | 63.446 | -60.1593 | -60.5255 | 0.064087 | 0.027466 | 63.295 | -60.3653 | 63.382 | -60.3653 | -60.5072 | -60.4111 | -0.10071 | -0.086975 | 0.11902 | 0.15106 | 60.3745 | -0.21515 | 60.4752 | -0.11444 | -0.054931 | -0.032043 | 0.054932 | -0.054931 | -0.10071 | -0.19684 | -0.045777 | -0.14191 | 0.25177 | 123.8571 | 0 | 123.7473 | 123.6511 | 123.6603 | 123.5504 | 123.6053 | -123.7381 | -123.6923 | 123.7564 | 123.6923 | 60.3607 | 60.3378
55.4844 | 123.8022 | -60.3287 | 63.2858 | 0.094845 | 0.0039235 | 0.077016 | 0.063008 | 0.0048751 | 0.0067048 | 0.00037059 | -0.098252 | 0.010839 | 0.07423 | 0.082214 | -0.0050872 | -0.0011101 | 0.00041246 | -0.086975 | 63.2355 | -60.4843 | 63.4323 | -60.2051 | -60.5347 | 0 | -0.10986 | 63.2675 | -60.379 | 63.4048 | -60.3699 | -60.5072 | -60.3745 | -0.15564 | -0.050354 | 0.14648 | 0.1236 | 60.3287 | -0.20599 | 60.4843 | -0.050354 | -0.050354 | -0.018311 | 0.11902 | -0.041199 | -0.045777 | -0.17853 | 0.004577 | -0.12817 | 0.27924 | 123.9166 | 0.009155 | 123.7839 | 123.7198 | 123.6465 | 123.5641 | 123.5962 | -123.7701 | -123.6649 | 123.761 | 123.7335 | 60.2417 | 60.2188
56.4844 | 123.7976 | -60.3333 | 63.2721 | 0.14062 | -0.00034947 | 0.064198 | 0.073689 | 0.0080791 | -0.010385 | -0.016719 | -0.098252 | -0.0083866 | 0.060344 | 0.069397 | 0.0013218 | 0.0074349 | 0.0057535 | -0.10071 | 63.2034 | -60.4752 | 63.4186 | -60.1913 | -60.5255 | 0.018311 | -0.10529 | 63.2355 | -60.3653 | 63.4094 | -60.3973 | -60.5255 | -60.3745 | -0.14191 | -0.068665 | 0.14648 | 0.14191 | 60.3516 | -0.19226 | 60.4935 | -0.050354 | -0.032043 | -0.036621 | 0.13733 | -0.064087 | -0.041199 | -0.19226 | -0.009156 | -0.16022 | 0.28381 | 123.8937 | -0.032044 | 123.7747 | 123.6786 | 123.6008 | 123.5367 | 123.5687 | -123.7473 | -123.6374 | 123.7518 | 123.7427 | 60.2325 | 60.228
57.4844 | 123.8113 | -60.3241 | 63.2675 | 0.018551 | -0.0046215 | 0.068471 | 0.06194 | 0.010216 | -0.027475 | 0.0089146 | 0.0085594 | 0.0012264 | 0.080638 | 0.052307 | 0.0045258 | 0.0020939 | 0.00041246 | -0.041199 | 63.2172 | -60.434 | 63.3041 | -60.3149 | -60.6216 | -0.086975 | -0.004578 | 63.1714 | -60.3699 | 63.4415 | -60.3561 | -60.4523 | -60.3287 | -0.10986 | -0.050354 | 0.036621 | 0.009156 | 60.2371 | -0.29755 | 60.347 | -0.18768 | -0.045776 | -0.09613 | 0.17395 | -0.032043 | -0.004577 | -0.12817 | 0.041199 | -0.082398 | 0.11902 | 123.7381 | 0.013733 | 123.8113 | 123.6511 | 123.5413 | 123.5413 | 123.4955 | -123.7015 | -123.6374 | 123.6282 | 123.7656 | 60.2829 | 60.3195
58.4844 | 123.8251 | -60.3058 | 63.2446 | 0.094845 | -0.00034947 | 0.068471 | 0.069417 | 0.0048751 | -0.00077219 | 0.0025066 | 0.054336 | 0.00015838 | 0.06248 | 0.055511 | -0.0018822 | -4.2099e-05 | 0.0068215 | -0.086975 | 63.1851 | -60.466 | 63.3453 | -60.2921 | -60.5988 | -0.050354 | -0.050354 | 63.1989 | -60.379 | 63.4598 | -60.3424 | -60.4431 | -60.2737 | -0.16022 | -0.059509 | 0.10071 | 0.013733 | 60.2554 | -0.29297 | 60.4156 | -0.13275 | -0.073242 | -0.045776 | 0.21515 | -0.036621 | 0.032043 | -0.13733 | 0.10528 | -0.064087 | 0.17395 | 123.8113 | 0.036621 | 123.8388 | 123.6511 | 123.5779 | 123.4909 | 123.5046 | -123.7106 | -123.6237 | 123.6511 | 123.7656 | 60.2188 | 60.2554
59.4844 | 123.8388 | -60.3012 | 63.2446 | 0.079586 | 0.0017875 | 0.064198 | 0.058736 | -0.0068739 | -0.0018402 | -0.00069841 | 0.054336 | 0.0054994 | 0.082775 | 0.069397 | -0.00081422 | -0.0021781 | -0.0092005 | -0.10071 | 63.2126 | -60.4706 | 63.3636 | -60.26 | -60.6033 | -0.059509 | -0.018311 | 63.2355 | -60.3607 | 63.4598 | -60.3424 | -60.4477 | -60.2921 | -0.16937 | -0.032044 | 0.11902 | 0.041198 | 60.2417 | -0.30212 | 60.4111 | -0.13275 | -0.05951 | -0.009155 | 0.21515 | -0.041199 | 0.009155 | -0.14648 | 0.068665 | -0.086975 | 0.21057 | 123.8342 | 0.018311 | 123.8205 | 123.6832 | 123.5962 | 123.5138 | 123.5367 | -123.7152 | -123.6053 | 123.6649 | 123.761 | 60.2005 | 60.2829
60.4844 | 123.8571 | -60.3333 | 63.2538 | 0.018551 | 0.00071953 | 0.070607 | 0.064076 | 0.0080791 | 0.0077728 | -0.00069841 | -0.0066996 | -0.0041136 | 0.067821 | 0.050171 | 0.0055948 | -0.0011101 | -0.0059965 | -0.082397 | 63.2172 | -60.466 | 63.3636 | -60.2417 | -60.5804 | -0.050354 | -0.036621 | 63.2309 | -60.3561 | 63.4552 | -60.3928 | -60.5438 | -60.3241 | -0.13275 | -0.036621 | 0.10986 | 0.091553 | 60.2829 | -0.24719 | 60.4156 | -0.11444 | -0.022888 | -0.022888 | 0.20142 | -0.059509 | 0.009155 | -0.21057 | 0.032043 | -0.18768 | 0.2243 | 123.8297 | -0.036621 | 123.8113 | 123.6832 | 123.587 | 123.5504 | 123.5641 | -123.7198 | -123.6099 | 123.6969 | 123.7885 | 60.2509 | 60.2966
61.4844 | 123.8663 | -60.3333 | 63.2538 | 0.0032924 | -0.00034947 | 0.066335 | 0.058736 | -0.0058059 | 0.022727 | -0.0049704 | 0.43581 | -0.011591 | 0.069957 | 0.062988 | -0.0029502 | -0.0021781 | 0.0014805 | -0.027466 | 63.1668 | -60.434 | 63.295 | -60.3058 | -60.6033 | -0.24719 | 0.068665 | 63.2309 | -60.3104 | 63.4598 | -60.379 | -60.434 | -60.2966 | -0.10071 | -0.086975 | 0.041199 | 0.027466 | 60.0861 | -0.27008 | 60.1868 | -0.16937 | 0.022888 | -0.022888 | 0.20599 | -0.045776 | 0.036621 | -0.10071 | 0.013733 | -0.1236 | 0.12817 | 123.7289 | -0.068664 | 123.7701 | 123.6008 | 123.5413 | 123.5001 | 123.5641 | -123.6877 | -123.5641 | 123.6282 | 123.793 | 60.3058 | 60.4019
62.4844 | 123.8068 | -60.3104 | 63.2721 | 0.12536 | -0.0024855 | 0.060994 | 0.049123 | 0.0038071 | 0.022727 | 0.021733 | 0.20692 | -0.0051816 | 0.064617 | 0.053375 | 0.0034578 | 0.0031619 | -0.0038605 | -0.050354 | 63.1851 | -60.4065 | 63.3362 | -60.2646 | -60.5942 | -0.059509 | -0.022888 | 63.2263 | -60.3928 | 63.4048 | -60.3607 | -60.4431 | -60.3195 | -0.09613 | -0.086975 | 0.064087 | 0.045777 | 60.2509 | -0.28381 | 60.347 | -0.18768 | -0.082397 | -0.045777 | 0.13275 | -0.050354 | -0.009155 | -0.13275 | 0.073242 | -0.050354 | 0.14191 | 123.7427 | 0.032043 | 123.7976 | 123.5916 | 123.6191 | 123.4955 | 123.5367 | -123.6786 | -123.6649 | 123.6465 | 123.7152 | 60.26 | 60.2875
63.4844 | 123.8388 | -60.3149 | 63.2629 | 0.14062 | 0.010333 | 0.05779 | 0.06194 | -0.0015339 | 0.0099088 | -0.0039024 | 0.11537 | -0.00090962 | 0.06248 | 0.060852 | -0.00081422 | -0.0021781 | 0.017502 | -0.10986 | 63.1989 | -60.4477 | 63.4048 | -60.2142 | -60.5438 | -0.022888 | -0.073242 | 63.2309 | -60.3699 | 63.4186 | -60.3699 | -60.4797 | -60.3241 | -0.13275 | -0.064086 | 0.14191 | 0.10071 | 60.2921 | -0.22888 | 60.4248 | -0.09613 | -0.054932 | -0.032043 | 0.15564 | -0.054932 | -0.009156 | -0.1648 | 0.045776 | -0.10986 | 0.23346 | 123.8525 | 0 | 123.7885 | 123.6465 | 123.6008 | 123.5138 | 123.5458 | -123.7106 | -123.6328 | 123.7198 | 123.7335 | 60.2051 | 60.2417
64.4844 | 123.8892 | -60.2921 | 63.2629 | 0.049069 | -0.0099625 | 0.070607 | 0.070485 | 0.014488 | -0.0061122 | 0.0067786 | -0.021958 | -0.0019776 | 0.068889 | 0.052307 | -0.0040182 | -0.0021781 | -0.0070645 | -0.041199 | 63.2126 | -60.4294 | 63.3408 | -60.2692 | -60.6491 | -0.10529 | 0 | 63.1851 | -60.3378 | 63.5834 | -60.5942 | -60.4614 | -60.1181 | -0.13733 | -0.050354 | 0.07782 | 0.022888 | 60.1868 | -0.35706 | 60.3241 | -0.21973 | -0.045777 | -0.077819 | 0.32043 | -0.30212 | 0.17395 | -0.16937 | 0.21973 | -0.1236 | 0.16022 | 123.7701 | -0.25635 | 123.9212 | 123.642 | 123.5229 | 123.5046 | 123.4772 | -123.6923 | -123.6008 | 123.6328 | 123.8754 | 60.2509 | 60.2921
65.4844 | 123.848 | -60.3012 | 63.2401 | -0.027225 | -0.0046215 | 0.073811 | 0.070485 | -0.0004649 | 0.0013638 | -0.0039024 | 0.10011 | -0.0019776 | 0.068889 | 0.065124 | -0.00081422 | 0.0095709 | 0.011093 | -0.082397 | 63.1714 | -60.4202 | 63.2996 | -60.3058 | -60.6491 | -0.082397 | 0.027466 | 63.2034 | -60.379 | 63.4552 | -60.3149 | -60.4294 | -60.2921 | -0.11902 | -0.068664 | 0.05951 | -0.004578 | 60.2188 | -0.3479 | 60.3378 | -0.22888 | -0.07782 | -0.036621 | 0.21515 | -0.013733 | 0.009155 | -0.12817 | 0.086975 | -0.050354 | 0.11444 | 123.7198 | 0.064087 | 123.8342 | 123.5916 | 123.5825 | 123.4726 | 123.5046 | -123.6603 | -123.6191 | 123.6008 | 123.7564 | 60.2188 | 60.3287
66.4844 | 123.8754 | -60.3241 | 63.2446 | 0.17114 | -0.0035535 | 0.068471 | 0.059804 | -0.0090099 | -0.021066 | -0.0071064 | 0.084853 | 0.0097714 | 0.077434 | 0.033081 | 0.0077308 | -0.0032471 | 0.0014805 | -0.068665 | 63.1714 | -60.4614 | 63.3362 | -60.2737 | -60.6125 | -0.059509 | -0.086975 | 63.1943 | -60.379 | 63.4598 | -60.3241 | -60.4294 | -60.2921 | -0.13733 | -0.073242 | 0.091553 | 0.050354 | 60.2646 | -0.28839 | 60.4019 | -0.15106 | -0.054931 | -0.050354 | 0.21515 | 0 | 0.032044 | -0.10528 | 0.086975 | -0.050354 | 0.18768 | 123.7976 | 0.054931 | 123.8388 | 123.6328 | 123.5733 | 123.4955 | 123.5184 | -123.7061 | -123.6237 | 123.6603 | 123.7839 | 60.2554 | 60.2371
67.4844 | 123.8113 | -60.2966 | 63.2721 | 0.1101 | 0.0017875 | 0.067403 | 0.054463 | 0.016624 | 0.0056368 | -0.0049704 | 0.11537 | 0.0087034 | 0.067821 | 0.075805 | 0.0034578 | 0.0095709 | 0.014297 | -0.064087 | 63.1851 | -60.4202 | 63.3499 | -60.2509 | -60.585 | -0.036621 | -0.041199 | 63.2263 | -60.3653 | 63.414 | -60.3516 | -60.4431 | -60.3241 | -0.1236 | -0.086975 | 0.07782 | 0.045777 | 60.26 | -0.28839 | 60.3836 | -0.1648 | -0.068664 | -0.045777 | 0.14191 | -0.054931 | -0.027466 | -0.14648 | 0.041198 | -0.07782 | 0.16937 | 123.7701 | 0.013733 | 123.7793 | 123.6053 | 123.5916 | 123.4818 | 123.5229 | -123.6923 | -123.6374 | 123.6465 | 123.7106 | 60.2325 | 60.2554
68.4844 | 123.8342 | -60.3149 | 63.2767 | 0.12536 | -0.0078255 | 0.067403 | 0.063008 | 0.017693 | -0.0093172 | 0.014256 | -0.067735 | -0.0083866 | 0.077434 | 0.060852 | 0.00025378 | 0.0031619 | -0.033768 | -0.022888 | 63.1851 | -60.434 | 63.2996 | -60.5392 | -60.8139 | 0.004578 | 0.027466 | 63.2263 | -60.3424 | 63.4506 | -60.3195 | -60.4156 | -60.2829 | -0.11902 | -0.091552 | 0.022889 | -0.22431 | 60.3195 | -0.49896 | 60.4385 | -0.37994 | -0.027466 | -0.050354 | 0.17395 | -0.004578 | 0.032043 | -0.10071 | 0.059509 | -0.073242 | -0.10529 | 123.7335 | 0.022888 | 123.793 | 123.6191 | 123.5687 | 123.5001 | 123.5413 | -123.7106 | -123.6191 | 123.6145 | 123.7656 | 60.2921 | 60.3424
69.4844 | 123.8388 | -60.2921 | 63.2629 | 0.14062 | -0.00034947 | 0.06313 | 0.057667 | -0.017555 | 0.0045688 | -0.0049704 | 0.054336 | 0.00015838 | 0.055004 | 0.074737 | -0.0061552 | 0.0020939 | 0.00041246 | -0.10071 | 63.208 | -60.4797 | 63.382 | -60.2142 | -60.5759 | -0.041199 | -0.054932 | 63.2263 | -60.3516 | 63.4323 | -60.3516 | -60.4385 | -60.2966 | -0.18768 | -0.054931 | 0.11902 | 0.07782 | 60.2509 | -0.28381 | 60.4385 | -0.096131 | -0.059509 | -0.036621 | 0.16937 | -0.059509 | -0.004578 | -0.14648 | 0.054931 | -0.086976 | 0.2655 | 123.8617 | 0 | 123.7839 | 123.6877 | 123.5779 | 123.5001 | 123.5184 | -123.7427 | -123.6145 | 123.674 | 123.7244 | 60.1913 | 60.2371
70.4844 | 123.7885 | -60.3149 | 63.2767 | 0.03381 | -0.0035535 | 0.064198 | 0.059804 | 0.0006031 | 0.0013638 | -0.013515 | -0.11351 | -0.0051816 | 0.069957 | 0.076874 | -0.0029502 | -0.0011101 | 0.0014805 | -0.10529 | 63.1989 | -60.466 | 63.4003 | -60.2142 | -60.5576 | -0.041199 | -0.091553 | 63.2263 | -60.3928 | 63.4415 | -60.3745 | -60.466 | -60.3333 | -0.15106 | -0.077819 | 0.1236 | 0.10071 | 60.2737 | -0.24262 | 60.4248 | -0.091553 | -0.07782 | -0.050354 | 0.1648 | -0.05951 | -0.018311 | -0.15106 | 0.059509 | -0.073242 | 0.25177 | 123.8663 | 0.01831 | 123.8342 | 123.6649 | 123.6191 | 123.5138 | 123.5413 | -123.7427 | -123.6694 | 123.7152 | 123.7564 | 60.2097 | 60.2234
71.4844 | 123.8937 | -60.3012 | 63.2858 | 0.049069 | 0.0017875 | 0.051381 | 0.065144 | -0.0026019 | 0.0099088 | -0.0028344 | 0.039077 | 0.0097714 | 0.072093 | 0.069397 | 0.0087988 | 0.0042299 | 0.013229 | -0.032043 | 63.1989 | -60.4156 | 63.327 | -60.3012 | -60.6674 | -0.082397 | 0 | 63.1989 | -60.3699 | 63.5422 | -60.5209 | -60.6079 | -60.1913 | -0.11444 | -0.086975 | 0.041198 | 0 | 60.2188 | -0.36621 | 60.3333 | -0.25177 | -0.068665 | -0.086975 | 0.25635 | -0.21973 | 0.10986 | -0.3067 | 0.17853 | -0.23804 | 0.11444 | 123.7427 | -0.15106 | 123.912 | 123.6145 | 123.5687 | 123.5001 | 123.5001 | -123.7015 | -123.6557 | 123.6282 | 123.8434 | 60.2692 | 60.3012
72.4844 | 123.8709 | -60.3012 | 63.2812 | 0.1864 | 0.0060595 | 0.054585 | 0.055531 | -0.0047379 | -0.014657 | -0.0049704 | 0.19167 | 0.0033634 | 0.082775 | 0.064056 | -0.00081422 | 0.0031619 | 0.0078895 | 0.036621 | 63.2263 | -60.379 | 63.3408 | -60.2554 | -60.6125 | -0.050354 | 0.073242 | 63.2355 | -60.3195 | 63.4964 | -60.2875 | -60.3653 | -60.2463 | -0.07782 | -0.054932 | 0.059509 | 0.045776 | 60.2509 | -0.31128 | 60.3287 | -0.23346 | -0.018311 | -0.045776 | 0.21515 | 0.013732 | 0.054931 | -0.064087 | 0.073242 | -0.045776 | 0.1236 | 123.7198 | 0.032043 | 123.8159 | 123.6053 | 123.555 | 123.5275 | 123.5367 | -123.6603 | -123.6008 | 123.642 | 123.7976 | 60.3378 | 60.3745
73.4844 | 123.8617 | -60.3058 | 63.2675 | 0.03381 | 0.010333 | 0.071675 | 0.066212 | 0.0027391 | -0.0050442 | -0.0049704 | 0.039077 | -0.0041136 | 0.061412 | 0.046966 | 0.0013218 | -0.0021781 | -0.012405 | -0.045776 | 63.1348 | -60.4706 | 63.2721 | -60.2829 | -60.64 | -0.14648 | 0.018311 | 63.1989 | -60.3607 | 63.4735 | -60.3012 | -60.4385 | -60.3149 | -0.1648 | -0.13275 | 0.004578 | 0.022888 | 60.1593 | -0.33417 | 60.3241 | -0.16937 | -0.054932 | -0.068664 | 0.20599 | 0.004578 | -0.009155 | -0.13275 | 0.045777 | -0.07782 | 0.18768 | 123.7427 | 0.05951 | 123.8342 | 123.6053 | 123.5596 | 123.4406 | 123.5046 | -123.7381 | -123.6282 | 123.5779 | 123.7793 | 60.26 | 60.3241
74.4844 | 123.8251 | -60.2737 | 63.2401 | 0.03381 | 0.0081955 | 0.067403 | 0.057667 | -0.017555 | -0.010385 | 0.00037059 | 0.054336 | 0.0044314 | 0.05714 | 0.071533 | -0.0061552 | 0.0031619 | -0.0059965 | 0.013733 | 63.1897 | -60.4752 | 63.2996 | -60.2966 | -60.6766 | -0.10986 | -0.004578 | 63.1897 | -60.3607 | 63.4689 | -60.3012 | -60.4156 | -60.2921 | -0.20142 | -0.050354 | 0.05951 | -0.022888 | 60.1639 | -0.40283 | 60.3653 | -0.20142 | -0.086975 | -0.050354 | 0.22888 | -0.027465 | -0.01831 | -0.14191 | 0.068665 | -0.054931 | 0.17853 | 123.7747 | 0.05951 | 123.8297 | 123.6649 | 123.5504 | 123.4634 | 123.4634 | -123.7152 | -123.6008 | 123.5733 | 123.7427 | 60.2875 | 60.2692
75.4844 | 123.8571 | -60.2875 | 63.2629 | 0.14062 | 0.0060595 | 0.069539 | 0.065144 | -0.0058059 | 0.0045688 | 0.0089146 | -0.0066996 | -0.0062496 | 0.064617 | 0.066192 | -0.0072232 | 0.0031619 | 0.0068215 | -0.041199 | 63.2126 | -60.4385 | 63.3728 | -60.1593 | -60.6079 | -0.11444 | 0.032043 | 63.2172 | -60.347 | 63.4735 | -60.2829 | -60.434 | -60.2737 | -0.15106 | -0.050354 | 0.10986 | 0.12817 | 60.173 | -0.32043 | 60.3241 | -0.16937 | -0.059509 | -0.045776 | 0.21057 | 0.004578 | 0.013733 | -0.14648 | 0.073242 | -0.086975 | 0.27924 | 123.8113 | 0.064087 | 123.8205 | 123.6511 | 123.5641 | 123.5001 | 123.5046 | -123.7015 | -123.6099 | 123.6603 | 123.761 | 60.2463 | 60.3195
76.4844 | 123.8571 | -60.3012 | 63.2401 | -0.027225 | -0.00034947 | 0.05779 | 0.074757 | -0.0004649 | -0.0093172 | -0.0071064 | 0.023818 | 0.0012264 | 0.072093 | 0.060852 | -0.0029502 | 0.0010259 | 0.0025485 | -0.10071 | 63.2217 | -60.4523 | 63.3591 | -60.2417 | -60.5896 | -0.064087 | -0.032043 | 63.2446 | -60.379 | 63.4781 | -60.4111 | -60.5255 | -60.3058 | -0.15106 | -0.01831 | 0.11902 | 0.059509 | 60.2371 | -0.28839 | 60.3882 | -0.13733 | -0.07782 | 0.004578 | 0.23804 | -0.10986 | -0.004578 | -0.2243 | 0.073242 | -0.14648 | 0.21057 | 123.8113 | -0.032044 | 123.8571 | 123.674 | 123.6237 | 123.5229 | 123.5458 | -123.6923 | -123.6191 | 123.6603 | 123.7793 | 60.2005 | 60.2692
77.4844 | 123.8342 | -60.3195 | 63.2584 | 0.079586 | -0.0014175 | 0.069539 | 0.056599 | 0.0038071 | 0.0056368 | -0.014583 | 0.31374 | 0.0033634 | 0.069957 | 0.086487 | -0.0040182 | -0.0011101 | -0.013474 | -0.022888 | 63.2217 | -60.434 | 63.3636 | -60.2509 | -60.6079 | -0.032043 | 0.041199 | 63.2217 | -60.3378 | 63.4689 | -60.2875 | -60.3745 | -60.2783 | -0.11444 | -0.036621 | 0.10529 | 0.068665 | 60.2875 | -0.28839 | 60.4019 | -0.17395 | -0.018311 | -0.036621 | 0.21057 | 0.032043 | 0.041199 | -0.054932 | 0.05951 | -0.036621 | 0.18311 | 123.7976 | 0.050354 | 123.8068 | 123.6557 | 123.5596 | 123.5413 | 123.5413 | -123.6923 | -123.5962 | 123.6832 | 123.7885 | 60.2966 | 60.3607
78.4844 | 123.848 | -60.3012 | 63.2446 | -0.011967 | 0.0071275 | 0.06313 | 0.068349 | 0.0027391 | -0.0061122 | 0.0057106 | 0.28322 | 0.00015838 | 0.059276 | 0.067261 | -0.0018822 | 0.0031619 | 0.0036165 | -0.018311 | 63.1485 | -60.4568 | 63.2767 | -60.3195 | -60.5804 | -0.18768 | 0.10529 | 63.2172 | -60.3287 | 63.4735 | -60.3561 | -60.4294 | -60.3012 | -0.15564 | -0.09613 | 0.032043 | -0.018311 | 60.1135 | -0.27924 | 60.2692 | -0.1236 | -0.027466 | -0.027466 | 0.22888 | -0.054932 | 0 | -0.12817 | 0.027466 | -0.10071 | 0.13733 | 123.7335 | -0.027466 | 123.8022 | 123.6053 | 123.5458 | 123.4497 | 123.5184 | -123.7015 | -123.5733 | 123.5779 | 123.7747 | 60.2829 | 60.4065
79.4844 | 123.88 | -60.3104 | 63.2172 | -0.057743 | -0.0024855 | 0.069539 | 0.064076 | -0.012215 | 0.014182 | 0.0099836 | -0.46446 | -0.0083866 | 0.059276 | 0.067261 | -0.0082912 | 0.0042299 | -0.0049285 | -0.027466 | 63.1714 | -60.4202 | 63.2858 | -60.3195 | -60.6445 | -0.10986 | 0.16937 | 63.208 | -60.3516 | 63.4872 | -60.2875 | -60.4568 | -60.3195 | -0.10986 | -0.045776 | 0.068665 | -0.009155 | 60.2005 | -0.33417 | 60.3104 | -0.2243 | -0.041198 | -0.009155 | 0.27008 | 0.022888 | -0.009155 | -0.14648 | 0.032043 | -0.10529 | 0.10071 | 123.7061 | 0.064086 | 123.8388 | 123.5916 | 123.5596 | 123.4818 | 123.5184 | -123.6374 | -123.5687 | 123.5962 | 123.7976 | 60.2829 | 60.4797
80.4844 | 123.8571 | -60.3058 | 63.2126 | 0.094845 | 0.0049915 | 0.067403 | 0.050191 | -0.012215 | 0.0035008 | -0.0039024 | -0.0066996 | 0.015112 | 0.069957 | 0.074737 | -0.0029502 | -0.0032471 | -0.02095 | -0.027466 | 63.1851 | -60.4248 | 63.2904 | -60.3149 | -60.64 | -0.09613 | -0.1236 | 63.1393 | -60.3836 | 63.446 | -60.2737 | -60.434 | -60.3012 | -0.11902 | -0.027465 | 0.07782 | -0.009155 | 60.2097 | -0.33417 | 60.3287 | -0.21515 | -0.07782 | -0.073242 | 0.23346 | 0.032043 | 0.004578 | -0.12817 | 0.082398 | -0.050354 | 0.10986 | 123.7152 | 0.10986 | 123.8297 | 123.6099 | 123.5229 | 123.4909 | 123.4451 | -123.6374 | -123.5962 | 123.5962 | 123.7518 | 60.2783 | 60.1822
81.4844 | 123.8251 | -60.3012 | 63.2538 | -0.011967 | 0.0017875 | 0.064198 | 0.06194 | -0.0015339 | 0.0067048 | 0.0099836 | 0.16115 | -0.00090962 | 0.058208 | 0.064056 | 0.0066628 | -4.2099e-05 | 0.0057535 | -0.022888 | 63.176 | -60.4065 | 63.2767 | -60.3287 | -60.64 | -0.10986 | 0.013733 | 63.1897 | -60.3699 | 63.4506 | -60.3149 | -60.4248 | -60.2875 | -0.10529 | -0.07782 | 0.022888 | -0.027466 | 60.1913 | -0.33875 | 60.2966 | -0.23346 | -0.068665 | -0.064087 | 0.19684 | -0.013733 | 0.013732 | -0.1236 | 0.082397 | -0.054932 | 0.07782 | 123.6832 | 0.054932 | 123.8205 | 123.5825 | 123.5596 | 123.4772 | 123.4909 | -123.6603 | -123.6237 | 123.5779 | 123.7518 | 60.2783 | 60.3149
82.4844 | 123.8251 | -60.3012 | 63.2904 | 0.1864 | -0.0067575 | 0.05779 | 0.057667 | -0.0047379 | -0.025338 | -0.010311 | 0.10011 | -0.0041136 | 0.078502 | 0.051239 | -0.00081422 | -4.2099e-05 | 0.011093 | -0.050354 | 63.2126 | -60.434 | 63.4003 | -60.2463 | -60.6354 | 0.027466 | -0.036621 | 63.2172 | -60.3516 | 63.4048 | -60.3378 | -60.434 | -60.3058 | -0.13275 | -0.07782 | 0.10986 | 0.054931 | 60.3287 | -0.33417 | 60.4614 | -0.20142 | -0.050354 | -0.073242 | 0.11444 | -0.036622 | -0.004578 | -0.13275 | 0.045776 | -0.082398 | 0.18768 | 123.8342 | 0.013732 | 123.7564 | 123.6465 | 123.5687 | 123.5138 | 123.5184 | -123.7244 | -123.642 | 123.7015 | 123.7061 | 60.2509 | 60.2646
83.4844 | 123.8297 | -60.2783 | 63.1897 | -0.011967 | -0.0035535 | 0.068471 | 0.073689 | -0.0068739 | 0.0056368 | -0.0028344 | -0.021958 | 0.0033634 | 0.066753 | 0.088623 | -0.0061552 | 0.010639 | 0.015366 | -0.009155 | 63.1805 | -60.4614 | 63.3087 | -60.3012 | -60.6537 | -0.10071 | -0.28381 | 63.1577 | -60.4111 | 63.4415 | -60.2966 | -60.3973 | -60.2737 | -0.18311 | -0.009155 | 0.11902 | -0.022888 | 60.1776 | -0.37537 | 60.3607 | -0.19226 | -0.13275 | -0.032043 | 0.25177 | -0.018311 | 0.004577 | -0.11902 | 0.13733 | 0.013733 | 0.16022 | 123.7701 | 0.11444 | 123.8525 | 123.642 | 123.5687 | 123.4589 | 123.436 | -123.6511 | -123.6008 | 123.587 | 123.7198 | 60.2692 | 59.9945
84.4844 | 123.8251 | -60.2783 | 63.2492 | -0.011967 | 0.010333 | 0.066335 | 0.069417 | -0.0036699 | -0.016794 | 0.014256 | 0.0085594 | -0.0062496 | 0.066753 | 0.037353 | 0.0055948 | -0.0043151 | -0.0059965 | -0.022888 | 63.1943 | -60.4431 | 63.2904 | -60.3241 | -60.64 | -0.07782 | 0.018311 | 63.2126 | -60.3516 | 63.4598 | -60.3149 | -60.434 | -60.2966 | -0.16479 | -0.054932 | 0.041198 | -0.045777 | 60.2005 | -0.36163 | 60.3653 | -0.19684 | -0.073242 | -0.036622 | 0.21057 | -0.036621 | -0.018311 | -0.15564 | 0.054931 | -0.082398 | 0.11902 | 123.7335 | 0.036621 | 123.8113 | 123.6374 | 123.5641 | 123.4726 | 123.4909 | -123.6923 | -123.6008 | 123.5687 | 123.7381 | 60.2554 | 60.2966
85.4844 | 123.8388 | -60.3012 | 63.2355 | -0.011967 | -0.01103 | 0.068471 | 0.068349 | -0.016487 | -0.031747 | 0.00037059 | 0.11537 | -0.0051816 | 0.065685 | 0.048034 | -0.0029502 | -0.0053831 | -0.0027915 | -0.032043 | 63.1851 | -60.4156 | 63.295 | -60.3149 | -60.6537 | -0.09613 | 0.022888 | 63.2172 | -60.3699 | 63.4506 | -60.3287 | -60.434 | -60.3195 | -0.11444 | -0.050354 | 0.059509 | -0.013733 | 60.2051 | -0.35248 | 60.3195 | -0.23804 | -0.068665 | -0.018311 | 0.21515 | -0.027466 | -0.018311 | -0.13275 | 0.050354 | -0.064087 | 0.10071 | 123.7106 | 0.041199 | 123.8205 | 123.6008 | 123.587 | 123.4863 | 123.5184 | -123.6511 | -123.6053 | 123.5962 | 123.7518 | 60.2692 | 60.3241
86.4844 | 123.8251 | -60.2966 | 63.2401 | 0.049069 | 0.0028555 | 0.068471 | 0.057667 | 0.0006031 | -0.013589 | -0.0028344 | 0.13063 | 0.0087034 | 0.075298 | 0.08435 | -0.00081422 | -4.2099e-05 | -0.0081325 | -0.022888 | 63.1943 | -60.4111 | 63.2812 | -60.3195 | -60.6354 | -0.10071 | 0.013733 | 63.2217 | -60.3653 | 63.4506 | -60.3195 | -60.434 | -60.3058 | -0.11444 | -0.045776 | 0.041199 | -0.022888 | 60.1959 | -0.33875 | 60.3104 | -0.2243 | -0.068664 | -0.01831 | 0.21057 | -0.022888 | -0.009155 | -0.13733 | 0.059509 | -0.068665 | 0.091553 | 123.6923 | 0.045776 | 123.8159 | 123.6053 | 123.587 | 123.4909 | 123.5184 | -123.6511 | -123.6053 | 123.5779 | 123.7473 | 60.2737 | 60.3104
87.4844 | 123.8983 | -60.26 | 63.2767 | 0.064327 | 0.0049915 | 0.065267 | 0.055531 | 0.0048751 | -0.0061122 | -0.0060384 | 0.20692 | 0.00015838 | 0.068889 | 0.060852 | 0.0013218 | -0.0043151 | 0.0068215 | 0.045776 | 63.2126 | -60.3882 | 63.3179 | -60.2966 | -60.6216 | -0.036621 | 0.10986 | 63.2355 | -60.3287 | 63.5056 | -60.2463 | -60.3424 | -60.2325 | -0.12817 | -0.064087 | 0.041199 | -0.036621 | 60.2234 | -0.36163 | 60.3516 | -0.23346 | -0.068664 | -0.041198 | 0.22888 | 0.013733 | 0.027466 | -0.082397 | 0.09613 | -0.013733 | 0.091553 | 123.7061 | 0.082397 | 123.8342 | 123.6008 | 123.5641 | 123.4726 | 123.4955 | -123.6649 | -123.6053 | 123.5779 | 123.7656 | 60.3058 | 60.3699
88.4844 | 123.8022 | -60.3012 | 63.2675 | -0.011967 | -0.0088935 | 0.06313 | 0.055531 | 0.0091481 | 0.017386 | -0.0060384 | 0.10011 | 0.0054994 | 0.080638 | 0.064056 | 0.00025378 | -0.0032471 | -0.0017235 | -0.054932 | 63.1897 | -60.4294 | 63.327 | -60.2692 | -60.5988 | -0.059509 | -0.018311 | 63.2263 | -60.3516 | 63.4232 | -60.3973 | -60.4706 | -60.3333 | -0.12817 | -0.07782 | 0.059509 | 0.032043 | 60.2417 | -0.29755 | 60.3699 | -0.16937 | -0.050354 | -0.041199 | 0.15564 | -0.096131 | -0.032044 | -0.16937 | 0.01831 | -0.11902 | 0.16022 | 123.7564 | -0.045777 | 123.7747 | 123.6191 | 123.5779 | 123.4909 | 123.5275 | -123.6969 | -123.6191 | 123.6282 | 123.7244 | 60.2463 | 60.2829
89.4844 | 123.8159 | -60.3058 | 63.2401 | 0.1101 | 0.0017875 | 0.069539 | 0.055531 | 0.01342 | -0.0029082 | -0.00069841 | 0.11537 | -0.0051816 | 0.058208 | 0.088623 | 0.0077308 | -0.0011101 | 0.022842 | -0.068665 | 63.1897 | -60.434 | 63.3362 | -60.2737 | -60.6033 | -0.059509 | -0.036621 | 63.2263 | -60.3516 | 63.4277 | -60.3699 | -60.4843 | -60.347 | -0.12817 | -0.050354 | 0.096131 | 0.032043 | 60.2463 | -0.29755 | 60.3745 | -0.16937 | -0.045776 | -0.013733 | 0.18768 | -0.064087 | -0.041199 | -0.17853 | 0.004577 | -0.13275 | 0.16022 | 123.7701 | -0.018311 | 123.7793 | 123.6237 | 123.5779 | 123.4955 | 123.5321 | -123.674 | -123.5916 | 123.642 | 123.7335 | 60.2371 | 60.2692
90.4844 | 123.8388 | -60.3012 | 63.2629 | -0.011967 | 0.0092645 | 0.065267 | 0.068349 | 0.0006031 | -0.00077219 | 0.0014386 | 0.023818 | -0.0019776 | 0.068889 | 0.08435 | 0.0013218 | 0.0074349 | 0.015366 | -0.032043 | 63.1851 | -60.4019 | 63.2812 | -60.3241 | -60.6445 | -0.086975 | 0.018311 | 63.2217 | -60.347 | 63.4598 | -60.3195 | -60.434 | -60.2921 | -0.10071 | -0.077819 | 0.018311 | -0.022889 | 60.2142 | -0.34332 | 60.3149 | -0.24261 | -0.045777 | -0.041198 | 0.19684 | -0.018311 | 0.009155 | -0.13275 | 0.054932 | -0.086975 | 0.07782 | 123.6832 | 0.027466 | 123.8068 | 123.587 | 123.5687 | 123.4863 | 123.5229 | -123.6649 | -123.6099 | 123.5825 | 123.761 | 60.2692 | 60.3195
91.4844 | 123.7885 | -60.2966 | 63.2629 | 0.1101 | 0.011401 | 0.058858 | 0.069417 | -0.018623 | 0.018454 | -0.0039024 | 0.10011 | -0.0051816 | 0.066753 | 0.056579 | -0.0018822 | -0.0096551 | -0.017746 | -0.050354 | 63.1714 | -60.4523 | 63.3316 | -60.2829 | -60.5988 | -0.064087 | -0.022888 | 63.2446 | -60.3561 | 63.4186 | -60.347 | -60.4568 | -60.3607 | -0.15564 | -0.091552 | 0.068665 | 0.013733 | 60.2325 | -0.30212 | 60.3882 | -0.14648 | -0.059509 | -0.01831 | 0.15564 | -0.050354 | -0.064087 | -0.16022 | -0.004578 | -0.10071 | 0.16937 | 123.7839 | 0.009155 | 123.7747 | 123.6237 | 123.6008 | 123.468 | 123.5413 | -123.7152 | -123.6191 | 123.6282 | 123.7152 | 60.2463 | 60.2737
92.4844 | 123.8388 | -60.2737 | 63.2767 | 0.018551 | -0.01103 | 0.058858 | 0.058736 | 0.014488 | -0.011453 | 0.0014386 | 0.22218 | -0.00090962 | 0.072093 | 0.033081 | 0.0023898 | -0.0053831 | -0.023087 | -0.041199 | 63.2217 | -60.434 | 63.3591 | -60.2371 | -60.585 | -0.041199 | 0.004578 | 63.2584 | -60.347 | 63.4598 | -60.2966 | -60.4019 | -60.2737 | -0.16022 | -0.054931 | 0.082398 | 0.036621 | 60.2325 | -0.31128 | 60.3928 | -0.15106 | -0.073242 | -0.01831 | 0.18311 | -0.022888 | 0 | -0.12817 | 0.073242 | -0.054932 | 0.19684 | 123.793 | 0.050354 | 123.8068 | 123.6557 | 123.6053 | 123.4955 | 123.5321 | -123.7106 | -123.6237 | 123.6328 | 123.7335 | 60.2325 | 60.2783
93.4844 | 123.7885 | -60.2783 | 63.2767 | 0.094845 | 0.0071275 | 0.065267 | 0.057667 | 0.0091481 | -0.0018402 | -0.016719 | 0.13063 | 0.0054994 | 0.069957 | 0.04483 | -0.00081422 | -0.0064511 | -0.0049285 | -0.045776 | 63.1805 | -60.434 | 63.327 | -60.2737 | -60.5942 | -0.073242 | -0.027466 | 63.2126 | -60.3745 | 63.4186 | -60.3561 | -60.4294 | -60.2921 | -0.15564 | -0.09613 | 0.050354 | 0.004577 | 60.2051 | -0.31586 | 60.3607 | -0.16022 | -0.096131 | -0.064087 | 0.14191 | -0.07782 | -0.013733 | -0.15106 | 0.082398 | -0.054931 | 0.16022 | 123.761 | 0.018311 | 123.793 | 123.6145 | 123.587 | 123.4589 | 123.4909 | -123.7106 | -123.6511 | 123.6053 | 123.6969 | 60.2325 | 60.2509
94.4844 | 123.7976 | -60.2783 | 63.2629 | 0.0032924 | 0.0028555 | 0.066335 | 0.063008 | 0.0059431 | -0.019998 | 0.011052 | -0.037217 | -0.00090962 | 0.071025 | 0.088623 | -0.0018822 | 0.0063669 | -0.012405 | -0.050354 | 63.1851 | -60.4431 | 63.327 | -60.2783 | -60.6171 | -0.073242 | -0.027466 | 63.208 | -60.3516 | 63.4232 | -60.3424 | -60.4294 | -60.2966 | -0.16479 | -0.077819 | 0.064087 | 0 | 60.2051 | -0.33874 | 60.3699 | -0.17395 | -0.073242 | -0.054931 | 0.16022 | -0.064087 | -0.018311 | -0.15106 | 0.054931 | -0.07782 | 0.16479 | 123.7701 | 0.009155 | 123.7747 | 123.6282 | 123.5596 | 123.4634 | 123.4863 | -123.7061 | -123.6145 | 123.6053 | 123.7015 | 60.228 | 60.2509
95.4844 | 123.7976 | -60.3378 | 63.2904 | 0.049069 | -0.0088935 | 0.06313 | 0.064076 | -0.0015339 | 0.0013638 | -0.00069841 | 0.72572 | 0.0054994 | 0.068889 | 0.057647 | 0.0023898 | -0.0021781 | -0.011337 | -0.045776 | 63.1897 | -60.4156 | 63.3682 | -60.2417 | -60.5621 | -0.050354 | -0.17853 | 63.2126 | -60.3516 | 63.4094 | -60.4065 | -60.4843 | -60.3516 | -0.077819 | -0.10071 | 0.07782 | 0.096131 | 60.2875 | -0.2243 | 60.3653 | -0.14648 | -0.013732 | -0.07782 | 0.11902 | -0.068664 | -0.013732 | -0.14648 | 0 | -0.13275 | 0.17395 | 123.7839 | -0.054932 | 123.761 | 123.6053 | 123.5641 | 123.5275 | 123.5504 | -123.7061 | -123.642 | 123.7061 | 123.7473 | 60.2921 | 60.1593
96.4844 | 123.7976 | -60.3058 | 63.2538 | 0.12536 | 0.0028555 | 0.060994 | 0.074757 | -0.0004649 | -0.0029082 | -0.0039024 | 0.023818 | -0.0019776 | 0.072093 | 0.053375 | -0.0029502 | 0.0031619 | -0.013474 | -0.045776 | 63.1897 | -60.4294 | 63.2996 | -60.2737 | -60.6033 | -0.073242 | -0.013733 | 63.2401 | -60.3745 | 63.414 | -60.3561 | -60.4477 | -60.3241 | -0.1236 | -0.064087 | 0.045777 | 0.032043 | 60.2325 | -0.29755 | 60.3561 | -0.17395 | -0.068665 | -0.013733 | 0.16022 | -0.050354 | -0.018311 | -0.14191 | 0.050354 | -0.073242 | 0.15564 | 123.7289 | 0.018311 | 123.7885 | 123.6191 | 123.6145 | 123.4955 | 123.5458 | -123.6832 | -123.6282 | 123.6053 | 123.7198 | 60.26 | 60.2921
97.4844 | 123.8525 | -60.2554 | 63.2584 | 0.094845 | 0.0060595 | 0.05779 | 0.063008 | 0.0016711 | 0.0045688 | -0.0017664 | 0.14589 | 0.00015838 | 0.059276 | 0.073669 | 0.0034578 | 0.0042299 | 0.0014805 | 0.018311 | 63.2126 | -60.4019 | 63.327 | -60.2692 | -60.6216 | -0.054932 | 0.091553 | 63.2309 | -60.3333 | 63.4781 | -60.2371 | -60.347 | -60.2554 | -0.14648 | -0.045777 | 0.068664 | -0.013733 | 60.2005 | -0.36621 | 60.347 | -0.21973 | -0.07782 | -0.027466 | 0.21973 | 0.01831 | 0 | -0.091553 | 0.07782 | -0.013733 | 0.13275 | 123.7289 | 0.09613 | 123.8113 | 123.6145 | 123.5641 | 123.468 | 123.4863 | -123.6603 | -123.5916 | 123.5825 | 123.7335 | 60.2737 | 60.347
98.4844 | 123.7976 | -60.3104 | 63.295 | 0.079586 | -0.0024855 | 0.049245 | 0.064076 | 0.0080791 | 0.010977 | -0.012447 | 0.069594 | -0.0062496 | 0.067821 | 0.083282 | -0.00081422 | -0.0032471 | 0.015366 | -0.036621 | 63.2126 | -60.4202 | 63.3545 | -60.2097 | -60.5759 | -0.018311 | -0.036621 | 63.2446 | -60.3607 | 63.4735 | -60.434 | -60.434 | -60.2829 | -0.10986 | -0.082398 | 0.059509 | 0.10071 | 60.2921 | -0.2655 | 60.4019 | -0.15564 | -0.050354 | -0.050354 | 0.17853 | -0.1236 | 0.027466 | -0.1236 | 0.07782 | -0.073242 | 0.21057 | 123.7747 | -0.073242 | 123.8342 | 123.6328 | 123.6053 | 123.5229 | 123.555 | -123.7152 | -123.6557 | 123.6649 | 123.7839 | 60.2737 | 60.2737
99.4844 | 123.8113 | -60.3012 | 63.2629 | 0.14062 | -0.0024855 | 0.073811 | 0.065144 | 0.0048751 | 0.0024328 | -0.0081744 | 0.16115 | 0.010839 | 0.066753 | 0.057647 | -0.0040182 | -0.0096551 | -0.0070645 | -0.036621 | 63.2172 | -60.434 | 63.3636 | -60.228 | -60.5713 | -0.045776 | -0.045776 | 63.2401 | -60.347 | 63.3545 | -60.2921 | -60.4065 | -60.3882 | -0.13275 | -0.045776 | 0.10071 | 0.073242 | 60.2554 | -0.27008 | 60.3882 | -0.13733 | -0.045777 | -0.022888 | 0.091553 | 0.009155 | -0.086976 | -0.10529 | -0.041199 | -0.059509 | 0.20599 | 123.7976 | 0.054932 | 123.7015 | 123.6511 | 123.587 | 123.5184 | 123.5413 | -123.6969 | -123.6099 | 123.6649 | 123.6557 | 60.2646 | 60.2554
100.4844 | 123.8434 | -60.2829 | 63.2858 | 0.064327 | -0.0014175 | 0.070607 | 0.063008 | 0.014488 | 0.019522 | -0.010311 | 0.069594 | -0.011591 | 0.067821 | 0.028808 | -0.0029502 | -0.0011101 | 0.012161 | -0.064087 | 63.2034 | -60.4202 | 63.3087 | -60.2509 | -60.5942 | -0.022888 | -0.041199 | 63.2309 | -60.3653 | 63.446 | -60.2051 | -60.6171 | -60.3699 | -0.13733 | -0.082398 | 0.022888 | 0.032044 | 60.26 | -0.31128 | 60.3973 | -0.17395 | -0.082397 | -0.054932 | 0.16022 | 0.07782 | -0.086975 | -0.33417 | -0.004578 | -0.25177 | 0.16937 | 123.7289 | 0.16022 | 123.8113 | 123.6237 | 123.5962 | 123.4863 | 123.5138 | -123.7061 | -123.6511 | 123.5916 | 123.7289 | 60.2188 | 60.2417
101.4844 | 123.8663 | -60.2875 | 63.2538 | 0.1101 | -0.00034947 | 0.069539 | 0.060872 | -0.0090099 | 0.0088408 | -0.0081744 | 0.16115 | -0.00090962 | 0.080638 | 0.07901 | -0.0050872 | 0.0063669 | 0.024979 | -0.064087 | 63.1897 | -60.4294 | 63.3316 | -60.2371 | -60.6125 | -0.059509 | -0.022888 | 63.2217 | -60.3607 | 63.4094 | -60.347 | -60.4248 | -60.1639 | -0.14191 | -0.064087 | 0.07782 | 0.050354 | 60.228 | -0.32501 | 60.3699 | -0.18311 | -0.073242 | -0.032043 | 0.15564 | -0.059509 | 0.1236 | -0.13733 | 0.19684 | -0.064087 | 0.19226 | 123.761 | 0.013733 | 123.7701 | 123.6191 | 123.5825 | 123.4772 | 123.5092 | -123.6832 | -123.6145 | 123.6191 | 123.6969 | 60.2234 | 60.2646
102.4844 | 123.8022 | -60.3058 | 63.2584 | 0.1864 | -0.0056895 | 0.056722 | 0.050191 | -0.0047379 | 0.012046 | 0.01212 | 0.13063 | 0.0087034 | 0.077434 | 0.042694 | -0.025381 | -0.0043151 | 0.0078895 | 0.041199 | 63.2217 | -60.4111 | 63.3041 | -60.3241 | -60.6262 | -0.059509 | 0.16022 | 63.2401 | -60.3241 | 63.652 | -60.6216 | -60.3928 | -60.2371 | -0.10529 | -0.036621 | 0.045776 | -0.018311 | 60.2463 | -0.32044 | 60.3516 | -0.21515 | -0.018311 | -0.018311 | 0.39368 | -0.31586 | 0.068664 | -0.086975 | 0.086975 | -0.068664 | 0.086975 | 123.7152 | -0.29755 | 123.9761 | 123.6328 | 123.5641 | 123.5275 | 123.5458 | -123.6694 | -123.5825 | 123.6099 | 123.9578 | 60.347 | 60.466
103.4844 | 123.8205 | -60.2875 | 63.2629 | 0.094845 | 0.0060595 | 0.055654 | 0.058736 | 0.0091481 | 0.017386 | 0.0035746 | 0.054336 | 0.0076354 | 0.063548 | 0.064056 | 0.0066628 | -0.0075191 | -0.0017235 | -0.059509 | 63.1989 | -60.4385 | 63.3362 | -60.2554 | -60.5804 | -0.018311 | -0.032043 | 63.2309 | -60.3699 | 63.414 | -60.3333 | -60.4523 | -60.3104 | -0.15106 | -0.064086 | 0.073243 | 0.032044 | 60.2692 | -0.29297 | 60.4202 | -0.14191 | -0.082397 | -0.032043 | 0.15106 | -0.045776 | -0.022888 | -0.1648 | 0.059509 | -0.082398 | 0.18311 | 123.7747 | 0.036621 | 123.7839 | 123.6374 | 123.6008 | 123.4863 | 123.5184 | -123.7015 | -123.6328 | 123.6237 | 123.7015 | 60.228 | 60.2554
104.4844 | 123.7701 | -60.3104 | 63.2767 | 0.14062 | 0.011401 | 0.06313 | 0.054463 | 0.0016711 | 0.017386 | 0.0025066 | 0.10011 | 0.0012264 | 0.061412 | 0.085418 | -0.0050872 | -0.0053831 | -0.042313 | -0.059509 | 63.2034 | -60.4385 | 63.3362 | -60.2692 | -60.5804 | -0.059509 | -0.013733 | 63.2355 | -60.3424 | 63.4369 | -60.3516 | -60.4477 | -60.3012 | -0.12817 | -0.073242 | 0.05951 | 0.041199 | 60.2509 | -0.27008 | 60.379 | -0.14191 | -0.032043 | -0.041198 | 0.16022 | -0.041198 | 0.009156 | -0.13733 | 0.041199 | -0.10529 | 0.16937 | 123.7747 | -0.009155 | 123.7793 | 123.642 | 123.5779 | 123.5138 | 123.5458 | -123.7152 | -123.6191 | 123.6465 | 123.7473 | 60.2509 | 60.2966
105.4844 | 123.8113 | -60.2829 | 63.2904 | 0.049069 | 0.00071953 | 0.056722 | 0.070485 | 0.012352 | 0.0067048 | -0.010311 | 0.16115 | -0.0073186 | 0.06248 | 0.064056 | 0.0013218 | 0.0031619 | -0.0027915 | -0.045776 | 63.2172 | -60.4019 | 63.4232 | -60.2463 | -60.6216 | -0.009155 | -0.086975 | 63.2355 | -60.3745 | 63.4277 | -60.3241 | -60.4431 | -60.3149 | -0.11902 | -0.073242 | 0.13275 | 0.036621 | 60.2737 | -0.33874 | 60.3928 | -0.21973 | -0.091553 | -0.054931 | 0.13733 | -0.041199 | -0.032043 | -0.16022 | 0.05951 | -0.068664 | 0.15564 | 123.8251 | 0.050354 | 123.8022 | 123.6191 | 123.6099 | 123.5001 | 123.5184 | -123.6923 | -123.6649 | 123.7061 | 123.7106 | 60.2371 | 60.1959
106.4844 | 123.7885 | -60.3195 | 63.2858 | 0.079586 | -0.0035535 | 0.062062 | 0.054463 | 0.019829 | 0.012046 | 0.0014386 | 0.054336 | 0.0054994 | 0.064617 | 0.060852 | 0.0045258 | -0.0032471 | 0.011093 | -0.059509 | 63.208 | -60.4385 | 63.3865 | -60.1776 | -60.5576 | -0.073242 | -0.027466 | 63.208 | -60.347 | 63.3957 | -60.3516 | -60.4385 | -60.3104 | -0.11902 | -0.07782 | 0.10071 | 0.14191 | 60.2463 | -0.23804 | 60.3653 | -0.11902 | -0.027466 | -0.07782 | 0.10986 | -0.032043 | 0.009155 | -0.11902 | 0.036621 | -0.091553 | 0.26093 | 123.8251 | -0.004577 | 123.7427 | 123.6465 | 123.555 | 123.5275 | 123.5275 | -123.7244 | -123.6328 | 123.7061 | 123.7152 | 60.26 | 60.2921
107.4844 | 123.7152 | -60.3241 | 63.327 | 0.03381 | -0.0067575 | 0.066335 | 0.059804 | 0.0006031 | -0.025338 | -0.0028344 | 0.023818 | -0.0094546 | 0.075298 | 0.057647 | 0.0013218 | 0.0010259 | 0.0014805 | 0.045776 | 63.2446 | -60.434 | 63.4323 | -60.1547 | -60.4752 | 0.091553 | -0.004578 | 63.3041 | -60.3561 | 63.382 | -60.3928 | -60.5026 | -60.3745 | -0.10986 | -0.082397 | 0.10529 | 0.16937 | 60.4156 | -0.15106 | 60.5255 | -0.041199 | -0.032043 | -0.022888 | 0.054932 | -0.068664 | -0.050354 | -0.17853 | -0.018311 | -0.14648 | 0.27924 | 123.8663 | -0.036621 | 123.7381 | 123.6786 | 123.6603 | 123.5687 | 123.6282 | -123.761 | -123.6832 | 123.7564 | 123.7061 | 60.3699 | 60.3195
108.4844 | 123.7839 | -60.3104 | 63.2767 | 0.12536 | 0.0092645 | 0.056722 | 0.065144 | 0.014488 | 0.0088408 | -0.0039024 | 0.13063 | -0.0041136 | 0.07957 | 0.04483 | 0.0098668 | -0.0021781 | 0.0025485 | -0.082397 | 63.1989 | -60.434 | 63.382 | -60.2234 | -60.5667 | -0.032043 | -0.032043 | 63.2126 | -60.3699 | 63.501 | -60.4248 | -60.4706 | -60.3012 | -0.1236 | -0.077819 | 0.10529 | 0.086975 | 60.2783 | -0.25635 | 60.4019 | -0.13275 | -0.059509 | -0.064087 | 0.22431 | -0.11444 | 0.009156 | -0.16022 | 0.068665 | -0.10071 | 0.21057 | 123.8159 | -0.054932 | 123.8708 | 123.6328 | 123.5825 | 123.5092 | 123.5229 | -123.7106 | -123.6465 | 123.6923 | 123.8113 | 60.228 | 60.2783
109.4844 | 123.8205 | -60.2875 | 63.2858 | 0.03381 | 0.00071953 | 0.062062 | 0.066212 | 0.0070111 | 0.010977 | -0.016719 | 0.11537 | 0.0012264 | 0.059276 | 0.058716 | 0.0023898 | -4.2099e-05 | -0.0027915 | -0.050354 | 63.1851 | -60.4523 | 63.3865 | -60.2142 | -60.5804 | -0.018311 | -0.027466 | 63.2217 | -60.3516 | 63.4232 | -60.3287 | -60.4294 | -60.2966 | -0.1648 | -0.10071 | 0.10071 | 0.073243 | 60.2692 | -0.29297 | 60.434 | -0.12817 | -0.064086 | -0.064087 | 0.13733 | -0.041198 | -0.009155 | -0.14191 | 0.054931 | -0.07782 | 0.23804 | 123.8388 | 0.022888 | 123.7747 | 123.6374 | 123.5733 | 123.4726 | 123.5092 | -123.7381 | -123.6374 | 123.674 | 123.7106 | 60.2371 | 60.26
110.4844 | 123.8663 | -60.2966 | 63.2675 | 0.12536 | -0.0088935 | 0.060994 | 0.065144 | -0.0068739 | 0.00029581 | -0.0092424 | 0.023818 | -0.0030456 | 0.072093 | 0.098236 | 0.0055948 | -0.0011101 | -0.0070645 | -0.050354 | 63.1989 | -60.4294 | 63.3408 | -60.2554 | -60.585 | -0.045776 | -0.041199 | 63.2401 | -60.3561 | 63.4232 | -60.3561 | -60.4431 | -60.3058 | -0.13275 | -0.068664 | 0.073242 | 0.041199 | 60.2509 | -0.28839 | 60.3836 | -0.15564 | -0.059509 | -0.027466 | 0.15564 | -0.059509 | -0.009155 | -0.14648 | 0.050354 | -0.086975 | 0.17395 | 123.7701 | 0 | 123.7793 | 123.6282 | 123.5962 | 123.4955 | 123.5367 | -123.6969 | -123.6237 | 123.6374 | 123.7198 | 60.2463 | 60.2554
111.4844 | 123.7885 | -60.3058 | 63.3041 | 0.079586 | 0.0039235 | 0.069539 | 0.056599 | 0.0070111 | 0.0077728 | 0.0078466 | -0.037217 | 0.00015838 | 0.060344 | 0.064056 | 0.0013218 | 0.0010259 | 0.0025485 | -0.059509 | 63.176 | -60.434 | 63.3499 | -60.2325 | -60.5896 | -0.054932 | -0.036621 | 63.2217 | -60.3607 | 63.414 | -60.3378 | -60.4568 | -60.3195 | -0.12817 | -0.12817 | 0.045777 | 0.073242 | 60.2509 | -0.28381 | 60.379 | -0.15564 | -0.054932 | -0.082397 | 0.10986 | -0.032044 | -0.013733 | -0.15106 | 0.041199 | -0.09613 | 0.20142 | 123.7839 | 0.022888 | 123.7747 | 123.6099 | 123.5825 | 123.4818 | 123.5275 | -123.7381 | -123.6649 | 123.6557 | 123.7198 | 60.2463 | 60.2692
112.4844 | 123.848 | -60.2737 | 63.327 | 0.12536 | -0.0024855 | 0.072743 | 0.064076 | -0.0036699 | -0.022134 | -0.0039024 | 0.13063 | -0.00090962 | 0.065685 | 0.052307 | -0.0029502 | -0.0032471 | 0.0025485 | 0.091553 | 63.2217 | -60.3973 | 63.3087 | -60.26 | -60.6216 | -0.041199 | 0.11444 | 63.2767 | -60.3195 | 63.4735 | -60.2692 | -60.3561 | -60.26 | -0.1236 | -0.10528 | -0.01831 | 0.013733 | 60.2325 | -0.3479 | 60.3561 | -0.2243 | -0.045776 | -0.050354 | 0.14649 | 0.004578 | 0.013733 | -0.082397 | 0.059509 | -0.036621 | 0.13733 | 123.7061 | 0.050354 | 123.793 | 123.6191 | 123.5962 | 123.4955 | 123.5504 | -123.7244 | -123.6465 | 123.5825 | 123.7473 | 60.3653 | 60.3882
113.4844 | 123.8068 | -60.3104 | 63.295 | 0.14062 | -0.0056895 | 0.070607 | 0.055531 | -0.0036699 | -0.0029082 | -0.0081744 | 0.023818 | 0.0054994 | 0.067821 | 0.056579 | 0.0013218 | 0.0042299 | -0.019882 | -0.050354 | 63.2217 | -60.4294 | 63.3774 | -60.1547 | -60.6079 | -0.059509 | -0.082397 | 63.2263 | -60.3836 | 63.4186 | -60.3333 | -60.4385 | -60.2921 | -0.11902 | -0.073242 | 0.082397 | 0.15564 | 60.2509 | -0.29755 | 60.3699 | -0.17853 | -0.073242 | -0.068665 | 0.1236 | -0.022888 | 0.018311 | -0.12817 | 0.091553 | -0.054932 | 0.27466 | 123.8068 | 0.050354 | 123.8022 | 123.6511 | 123.6099 | 123.5321 | 123.5367 | -123.7244 | -123.6786 | 123.6877 | 123.7289 | 60.26 | 60.228
114.4844 | 123.7885 | -60.3058 | 63.295 | 0.14062 | -0.00034947 | 0.064198 | 0.058736 | 0.0080791 | 0.013114 | -0.0071064 | 0.16115 | 0.0065674 | 0.066753 | 0.073669 | -0.00081422 | 0.0010259 | 0.0078895 | -0.050354 | 63.2217 | -60.4202 | 63.3133 | -60.2097 | -60.5072 | -0.07782 | -0.10071 | 63.2309 | -60.3653 | 63.3957 | -60.3699 | -60.4752 | -60.3333 | -0.11444 | -0.073242 | 0.01831 | 0.09613 | 60.228 | -0.20142 | 60.3424 | -0.086975 | -0.059509 | -0.064087 | 0.10071 | -0.064087 | -0.027466 | -0.16937 | 0.032043 | -0.10986 | 0.21057 | 123.7335 | -0.004578 | 123.761 | 123.642 | 123.5962 | 123.5275 | 123.5367 | -123.7152 | -123.6603 | 123.6191 | 123.7015 | 60.2554 | 60.2051
115.4844 | 123.7976 | -60.3149 | 63.2675 | 0.049069 | -0.0024855 | 0.06313 | 0.066212 | -0.0004649 | -0.0071802 | -0.0081744 | 0.58839 | 0.0044314 | 0.056072 | 0.073669 | 0.0045258 | -0.0032471 | -0.016678 | -0.050354 | 63.2126 | -60.434 | 63.3545 | -60.228 | -60.5667 | -0.059509 | -0.10986 | 63.2629 | -60.3333 | 63.3911 | -60.4065 | -60.4477 | -60.3424 | -0.11902 | -0.054932 | 0.086975 | 0.086975 | 60.2554 | -0.25177 | 60.3745 | -0.13275 | -0.018311 | -0.004578 | 0.1236 | -0.091553 | -0.027466 | -0.13275 | -0.009155 | -0.11444 | 0.20599 | 123.7885 | -0.073242 | 123.7244 | 123.6465 | 123.5962 | 123.5275 | 123.5779 | -123.7015 | -123.6008 | 123.6694 | 123.7061 | 60.2646 | 60.2051
116.4844 | 123.8525 | -60.2692 | 63.295 | 0.049069 | -0.00034947 | 0.068471 | 0.066212 | -0.010078 | 0.014182 | 0.0099836 | 0.16115 | -0.0019776 | 0.075298 | 0.069397 | 0.0066628 | 0.0042299 | -0.02095 | -0.013733 | 63.2217 | -60.4248 | 63.3591 | -60.2371 | -60.5759 | -0.022888 | 0 | 63.2126 | -60.3424 | 63.4415 | -60.3104 | -60.4065 | -60.2966 | -0.15564 | -0.073242 | 0.064087 | 0.032043 | 60.2463 | -0.3067 | 60.4019 | -0.15106 | -0.073242 | -0.082398 | 0.14648 | -0.041199 | -0.027466 | -0.13733 | 0.045776 | -0.064087 | 0.18768 | 123.7839 | 0.032043 | 123.7839 | 123.6465 | 123.555 | 123.4909 | 123.4818 | -123.7198 | -123.6374 | 123.6282 | 123.7106 | 60.2554 | 60.2692
117.4844 | 123.8434 | -60.2692 | 63.2904 | 0.15588 | 0.0017875 | 0.055654 | 0.06194 | 0.0038071 | 0.0013638 | 0.0014386 | -0.23558 | 0.0022944 | 0.061412 | 0.071533 | -0.0029502 | -0.0032471 | -0.014542 | 0.086975 | 63.2309 | -60.3928 | 63.2858 | -60.2829 | -60.672 | 0.10986 | 0.082397 | 63.2217 | -60.3516 | 63.5101 | -60.2417 | -60.379 | -60.2554 | -0.1236 | -0.059509 | -0.004577 | -0.013733 | 60.379 | -0.40283 | 60.5026 | -0.27924 | -0.082397 | -0.068664 | 0.21973 | 0.027466 | 0.013733 | -0.10986 | 0.09613 | -0.027466 | 0.10986 | 123.6786 | 0.10986 | 123.8617 | 123.6237 | 123.5733 | 123.5001 | 123.4909 | -123.6832 | -123.642 | 123.555 | 123.7793 | 60.3561 | 60.3516
118.4844 | 123.8297 | -60.3012 | 63.3041 | 0.079586 | -0.0067575 | 0.06313 | 0.064076 | 0.020897 | 0.0024328 | 0.00037059 | 0.084853 | 0.0044314 | 0.06248 | 0.085418 | -0.0072232 | 0.017048 | 0.011093 | -0.041199 | 63.1943 | -60.4385 | 63.3453 | -60.2188 | -60.5804 | -0.036621 | -0.036621 | 63.2263 | -60.379 | 63.3774 | -60.173 | -60.5392 | -60.3928 | -0.13733 | -0.10986 | 0.041199 | 0.082397 | 60.2646 | -0.27924 | 60.4019 | -0.14191 | -0.07782 | -0.07782 | 0.073242 | 0.12817 | -0.091553 | -0.23804 | -0.013733 | -0.16022 | 0.21973 | 123.7839 | 0.20599 | 123.7564 | 123.6328 | 123.6053 | 123.4955 | 123.5275 | -123.7427 | -123.6832 | 123.6465 | 123.6786 | 60.26 | 60.2646
119.4844 | 123.8251 | -60.3104 | 63.2721 | -0.042484 | -0.00034947 | 0.066335 | 0.058736 | -0.0026019 | 0.0067048 | -0.0049704 | 0.10011 | 0.0076354 | 0.073162 | 0.074737 | -0.0061552 | 0.0074349 | -0.0027915 | -0.027466 | 63.208 | -60.4202 | 63.3408 | -60.2234 | -60.5667 | -0.004578 | -0.032043 | 63.2446 | -60.3241 | 63.4552 | -60.3287 | -60.4202 | -60.2966 | -0.10986 | -0.064087 | 0.068664 | 0.086975 | 60.3058 | -0.25635 | 60.4156 | -0.14648 | -0.013733 | -0.027466 | 0.1831 | -0.01831 | 0.013733 | -0.10986 | 0.027466 | -0.09613 | 0.19684 | 123.761 | -0.004577 | 123.7793 | 123.6282 | 123.5687 | 123.5184 | 123.555 | -123.6923 | -123.5962 | 123.6511 | 123.7656 | 60.2829 | 60.2783
120.4844 | 123.7885 | -60.2921 | 63.295 | 0.15588 | -0.0024855 | 0.064198 | 0.056599 | 0.0048751 | 0.0056368 | -0.0081744 | 0.19167 | 0.00015838 | 0.073162 | 0.097168 | 0.0034578 | -0.0043151 | 0.0036165 | -0.10071 | 63.2126 | -60.4202 | 63.3453 | -60.228 | -60.585 | -0.041199 | -0.009155 | 63.2584 | -60.3607 | 63.4369 | -60.3241 | -60.434 | -60.2966 | -0.12817 | -0.082398 | 0.050354 | 0.064087 | 60.2509 | -0.29297 | 60.379 | -0.1648 | -0.068665 | -0.036621 | 0.14191 | -0.032044 | -0.004578 | -0.14191 | 0.064087 | -0.073242 | 0.19226 | 123.7656 | 0.036621 | 123.7976 | 123.6328 | 123.6191 | 123.5046 | 123.5504 | -123.7152 | -123.6557 | 123.6374 | 123.7289 | 60.1913 | 60.2829
121.4844 | 123.7976 | -60.3195 | 63.2584 | 0.27795 | 0.015673 | 0.059926 | 0.057667 | -0.0036699 | 0.013114 | -0.0274 | 0.039077 | -0.010523 | 0.077434 | 0.062988 | 0.0045258 | -0.0053831 | -0.00065554 | -0.064087 | 63.208 | -60.3928 | 63.3408 | -60.2417 | -60.585 | -0.027466 | -0.045776 | 63.2217 | -60.3607 | 63.4232 | -60.3378 | -60.4431 | -60.3012 | -0.073242 | -0.050354 | 0.082397 | 0.07782 | 60.2921 | -0.2655 | 60.3653 | -0.19226 | -0.041199 | -0.036621 | 0.1648 | -0.018311 | 0.018311 | -0.1236 | 0.05951 | -0.082397 | 0.15106 | 123.7335 | 0.022888 | 123.7839 | 123.6008 | 123.5825 | 123.5275 | 123.5413 | -123.6511 | -123.6191 | 123.6603 | 123.7427 | 60.2554 | 60.2737
122.4844 | 123.7747 | -60.2737 | 63.3179 | 0.14062 | 0.0039235 | 0.050313 | 0.068349 | 0.0006031 | 0.018454 | 0.020665 | 0.054336 | 0.0033634 | 0.076366 | 0.050171 | 0.00025378 | 0.010639 | -0.0070645 | 0.086975 | 63.2355 | -60.4019 | 63.3408 | -60.2234 | -60.5621 | 0.013733 | 0.059509 | 63.2721 | -60.3241 | 63.4323 | -60.3104 | -60.4294 | -60.3149 | -0.12817 | -0.082397 | 0.022888 | 0.050354 | 60.2875 | -0.28839 | 60.4156 | -0.16022 | -0.050354 | -0.045776 | 0.11444 | -0.036621 | -0.041198 | -0.15564 | 0.009156 | -0.10528 | 0.17853 | 123.7427 | 0.013733 | 123.7564 | 123.6374 | 123.5962 | 123.5092 | 123.5458 | -123.7198 | -123.642 | 123.6145 | 123.7061 | 60.3607 | 60.3333
123.4844 | 123.8113 | -60.2783 | 63.2721 | 0.0032924 | -0.0056895 | 0.060994 | 0.060872 | 0.028374 | -0.0061122 | 0.0025066 | 0.039077 | -0.0094546 | 0.067821 | 0.10251 | 0.0066628 | -0.0064511 | -0.01561 | -0.032043 | 63.2172 | -60.4111 | 63.3362 | -60.2325 | -60.585 | -0.027466 | 0.009155 | 63.2355 | -60.3653 | 63.4506 | -60.3195 | -60.3928 | -60.2737 | -0.13275 | -0.054932 | 0.064087 | 0.045776 | 60.2509 | -0.3067 | 60.3836 | -0.17395 | -0.086975 | -0.036621 | 0.17853 | -0.041199 | 0.004577 | -0.11444 | 0.091552 | -0.027466 | 0.17853 | 123.7473 | 0.045776 | 123.8159 | 123.6282 | 123.6008 | 123.4955 | 123.5138 | -123.6832 | -123.6374 | 123.6145 | 123.7289 | 60.2463 | 60.2875
124.4844 | 123.7839 | -60.2829 | 63.3087 | 0.094845 | 0.0017875 | 0.068471 | 0.072621 | 0.023033 | -0.010385 | -0.013515 | -0.082994 | 0.0022944 | 0.061412 | 0.076874 | -0.0050872 | -0.0021781 | 0.0014805 | -0.032043 | 63.2126 | -60.4156 | 63.3682 | -60.1639 | -60.5896 | -0.027466 | -0.009155 | 63.2263 | -60.3333 | 63.3957 | -60.3516 | -60.4523 | -60.2921 | -0.13275 | -0.096131 | 0.059509 | 0.11902 | 60.2554 | -0.3067 | 60.3882 | -0.17395 | -0.050354 | -0.082398 | 0.086975 | -0.068664 | -0.009155 | -0.16937 | 0.041199 | -0.11902 | 0.25177 | 123.7839 | -0.01831 | 123.7289 | 123.6282 | 123.5596 | 123.4955 | 123.5092 | -123.7244 | -123.642 | 123.6511 | 123.6786 | 60.2509 | 60.2737
125.4844 | 123.8113 | -60.2966 | 63.2767 | 0.094845 | 0.011401 | 0.062062 | 0.073689 | 0.0006031 | 0.017386 | 0.0025066 | 0.16115 | -0.0062496 | 0.071025 | 0.10678 | 0.00025378 | 0.0010259 | -0.0049285 | -0.022888 | 63.2126 | -60.4248 | 63.3408 | -60.2371 | -60.5942 | -0.036621 | 0.022888 | 63.2446 | -60.3333 | 63.4689 | -60.2966 | -60.4156 | -60.2875 | -0.12817 | -0.064087 | 0.064087 | 0.059509 | 60.26 | -0.29755 | 60.3882 | -0.16937 | -0.036621 | -0.032043 | 0.19226 | 0 | 0.009155 | -0.11902 | 0.045776 | -0.082397 | 0.18768 | 123.7656 | 0.036621 | 123.8022 | 123.6374 | 123.5779 | 123.5092 | 123.5413 | -123.7015 | -123.6099 | 123.6374 | 123.7656 | 60.2737 | 60.3195
126.4844 | 123.8068 | -60.2646 | 63.2767 | 0.094845 | 0.0017875 | 0.060994 | 0.065144 | 0.0059431 | 0.0077728 | -0.0028344 | 0.10011 | 0.0044314 | 0.064617 | 0.070465 | 0.0034578 | 0.0095709 | 0.016434 | -0.013733 | 63.2401 | -60.4065 | 63.3316 | -60.2234 | -60.5713 | -0.045776 | 0.009155 | 63.2217 | -60.347 | 63.4506 | -60.3012 | -60.3882 | -60.2783 | -0.14191 | -0.036621 | 0.054932 | 0.041198 | 60.2188 | -0.3067 | 60.3607 | -0.16479 | -0.082398 | -0.054931 | 0.17395 | -0.036621 | -0.013733 | -0.1236 | 0.068665 | -0.041199 | 0.18311 | 123.7381 | 0.045777 | 123.7976 | 123.6465 | 123.5687 | 123.5046 | 123.4863 | -123.6832 | -123.6237 | 123.5962 | 123.7152 | 60.2509 | 60.2737
127.4844 | 123.7015 | -60.3058 | 63.3408 | 0.15588 | 0.0049915 | 0.065267 | 0.071553 | 0.0080791 | 0.0077728 | -0.016719 | 0.069594 | 0.0076354 | 0.078502 | 0.080078 | -0.0072232 | 0.010639 | 0.0025485 | 0.059509 | 63.2401 | -60.434 | 63.4415 | -60.1364 | -60.5072 | 0.082397 | -0.009155 | 63.295 | -60.3424 | 63.3774 | -60.3745 | -60.498 | -60.3745 | -0.12817 | -0.10071 | 0.10071 | 0.16937 | 60.3882 | -0.20142 | 60.5164 | -0.073242 | -0.036621 | -0.045776 | 0.036621 | -0.068665 | -0.068665 | -0.19226 | -0.032044 | -0.15564 | 0.29755 | 123.8754 | -0.032044 | 123.7198 | 123.674 | 123.6374 | 123.5458 | 123.6008 | -123.7747 | -123.6832 | 123.7473 | 123.6832 | 60.3653 | 60.2966
128.4844 | 123.8022 | -60.2692 | 63.2812 | 0.17114 | 0.0049915 | 0.054585 | 0.06194 | 0.0070111 | -0.0039762 | 0.0035746 | 0.20692 | -0.0019776 | 0.083843 | 0.041626 | 0.0013218 | -0.0011101 | 0.0014805 | -0.018311 | 63.2126 | -60.4385 | 63.3408 | -60.2097 | -60.5621 | -0.027466 | -0.009155 | 63.2034 | -60.3378 | 63.4415 | -60.3104 | -60.4019 | -60.2829 | -0.16937 | -0.068665 | 0.059509 | 0.059509 | 60.2417 | -0.29297 | 60.4111 | -0.1236 | -0.068665 | -0.07782 | 0.16022 | -0.041199 | -0.013733 | -0.13275 | 0.054932 | -0.064087 | 0.22888 | 123.7793 | 0.027466 | 123.7793 | 123.6511 | 123.5413 | 123.4818 | 123.4726 | -123.7198 | -123.6191 | 123.6099 | 123.7106 | 60.2509 | 60.26
129.4844 | 123.8525 | -60.2554 | 63.2812 | 0.1101 | -0.0024855 | 0.052449 | 0.054463 | 0.0016711 | 0.0035008 | -0.014583 | 0.17641 | 0.00015838 | 0.067821 | 0.087555 | 0.0023898 | 0.0031619 | -0.0092005 | 0.009155 | 63.1989 | -60.4294 | 63.3133 | -60.2646 | -60.5988 | -0.045776 | 0.091553 | 63.2309 | -60.3424 | 63.4735 | -60.2692 | -60.3195 | -60.1959 | -0.17395 | -0.082397 | 0.032043 | -0.009155 | 60.2097 | -0.34332 | 60.3836 | -0.16937 | -0.086975 | -0.050354 | 0.19226 | -0.013733 | 0.059509 | -0.064087 | 0.14648 | 0.022888 | 0.16479 | 123.7427 | 0.073242 | 123.8159 | 123.6282 | 123.5733 | 123.4543 | 123.4863 | -123.7106 | -123.6237 | 123.5687 | 123.7289 | 60.2646 | 60.347
130.4844 | 123.8571 | -60.2875 | 63.2812 | 0.20166 | -0.0067575 | 0.064198 | 0.076894 | 0.017693 | -0.022134 | 0.0078466 | 0.13063 | 0.0022944 | 0.068889 | 0.072601 | -0.00081422 | 0.0042299 | -0.0059965 | 0.018311 | 63.208 | -60.4202 | 63.3041 | -60.2783 | -60.6171 | -0.059509 | 0.091553 | 63.2355 | -60.3424 | 63.4872 | -60.2371 | -60.3149 | -60.2371 | -0.13275 | -0.073242 | 0.022888 | 0.009156 | 60.228 | -0.32959 | 60.3607 | -0.19684 | -0.054931 | -0.045776 | 0.20599 | 0.050354 | 0.050354 | -0.027465 | 0.10529 | 0.027466 | 0.14191 | 123.7244 | 0.10529 | 123.8297 | 123.6282 | 123.5779 | 123.4955 | 123.523 | -123.7015 | -123.6237 | 123.5916 | 123.7747 | 60.3058 | 60.379
131.4844 | 123.8113 | -60.2829 | 63.2584 | 0.03381 | 0.0017875 | 0.065267 | 0.068349 | 0.0070111 | -0.021066 | 0.00037059 | 0.19167 | 0.0033634 | 0.073162 | 0.11746 | -0.012563 | -4.2099e-05 | 0.0025485 | -0.013733 | 63.2309 | -60.4111 | 63.3545 | -60.2234 | -60.5667 | -0.022888 | 0 | 63.2263 | -60.3607 | 63.4506 | -60.3195 | -60.4065 | -60.2921 | -0.12817 | -0.027466 | 0.09613 | 0.059509 | 60.26 | -0.28381 | 60.3882 | -0.15564 | -0.07782 | -0.032044 | 0.19226 | -0.036621 | -0.009155 | -0.1236 | 0.068665 | -0.045776 | 0.18768 | 123.7656 | 0.041199 | 123.8113 | 123.642 | 123.587 | 123.5138 | 123.5092 | -123.6694 | -123.6191 | 123.6374 | 123.7335 | 60.2692 | 60.2829
132.4844 | 123.8159 | -60.2921 | 63.2996 | 0.15588 | 0.0081955 | 0.060994 | 0.069417 | 0.0048751 | 0.0035008 | -0.0049704 | 0.054336 | -0.0083866 | 0.07423 | 0.058716 | -0.00081422 | -0.0021781 | -0.0049285 | 0.082397 | 63.2492 | -60.4202 | 63.3362 | -60.2554 | -60.5988 | -0.027466 | 0.09613 | 63.2629 | -60.3287 | 63.4506 | -60.2783 | -60.3836 | -60.2646 | -0.12817 | -0.050354 | 0.036621 | 0.036621 | 60.2646 | -0.3067 | 60.3928 | -0.17853 | -0.036621 | -0.036622 | 0.15106 | 0.013733 | 0.027466 | -0.091553 | 0.064087 | -0.054932 | 0.16479 | 123.7564 | 0.050354 | 123.7793 | 123.6694 | 123.5916 | 123.5413 | 123.555 | -123.7198 | -123.6282 | 123.6282 | 123.7427 | 60.3745 | 60.3882
133.4844 | 123.8846 | -60.2646 | 63.2812 | 0.1101 | -0.0046215 | 0.052449 | 0.06194 | 0.0048751 | -0.01893 | 0.01212 | 0.13063 | 0.0022944 | 0.073162 | 0.071533 | -0.0029502 | -4.2099e-05 | -0.016678 | 0.022888 | 63.2401 | -60.4019 | 63.3499 | -60.2783 | -60.6171 | -0.036621 | 0.082397 | 63.2401 | -60.3516 | 63.501 | -60.2554 | -60.3699 | -60.2829 | -0.13733 | -0.041199 | 0.068665 | -0.013733 | 60.228 | -0.35248 | 60.3653 | -0.21515 | -0.086975 | -0.041199 | 0.21973 | 0.009155 | -0.018311 | -0.10529 | 0.068664 | -0.018311 | 0.1236 | 123.7518 | 0.09613 | 123.8525 | 123.642 | 123.5916 | 123.5046 | 123.5046 | -123.6832 | -123.6328 | 123.6145 | 123.7656 | 60.2875 | 60.347
134.4844 | 123.8525 | -60.2463 | 63.2904 | 0.14062 | -0.0088935 | 0.058858 | 0.06194 | 0.0048751 | -0.01893 | 0.0089146 | 0.10011 | 0.0012264 | 0.075298 | 0.080078 | 0.0066628 | 0.0052979 | 0.0025485 | 0.027466 | 63.2126 | -60.3973 | 63.3224 | -60.2646 | -60.6079 | -0.041199 | 0.068665 | 63.2401 | -60.3333 | 63.4735 | -60.2783 | -60.3882 | -60.2554 | -0.15106 | -0.07782 | 0.032044 | -0.01831 | 60.2051 | -0.36163 | 60.3561 | -0.21057 | -0.086975 | -0.050354 | 0.18311 | -0.032043 | -0.009155 | -0.14191 | 0.07782 | -0.054932 | 0.13275 | 123.7198 | 0.054932 | 123.8068 | 123.6099 | 123.5733 | 123.4589 | 123.4863 | -123.6877 | -123.6237 | 123.5687 | 123.7198 | 60.2737 | 60.3149
135.4844 | 123.7701 | -60.3058 | 63.3087 | -0.073002 | 0.0049915 | 0.056722 | 0.075825 | -0.0047379 | 0.0099088 | -0.0017664 | -0.1898 | 0.0097714 | 0.063548 | 0.085418 | -0.012563 | 0.013843 | 0.014297 | 0.068665 | 63.2263 | -60.4614 | 63.4094 | -60.1685 | -60.5209 | 0.041199 | 0 | 63.2675 | -60.3607 | 63.4277 | -60.3561 | -60.4935 | -60.3287 | -0.15564 | -0.082398 | 0.10071 | 0.13733 | 60.347 | -0.21515 | 60.5026 | -0.059509 | -0.054932 | -0.041199 | 0.11902 | -0.050354 | -0.022888 | -0.18768 | 0.032044 | -0.13275 | 0.29297 | 123.8709 | 0.004578 | 123.7885 | 123.6877 | 123.6282 | 123.5321 | 123.5733 | -123.7701 | -123.6694 | 123.7152 | 123.7335 | 60.3745 | 60.3058
136.4844 | 123.8525 | -60.26 | 63.2812 | 0.049069 | 0.0028555 | 0.06313 | 0.064076 | 0.020897 | -0.026407 | -0.0028344 | 0.16115 | -0.015863 | 0.066753 | 0.077942 | 0.0055948 | 0.013843 | -0.0027915 | 0.064087 | 63.2217 | -60.4019 | 63.2629 | -60.3149 | -60.6262 | -0.032043 | 0.47607 | 63.3133 | -60.3012 | 63.5376 | -60.3104 | -60.3653 | -60.228 | -0.14191 | -0.059509 | -0.018311 | -0.054931 | 60.228 | -0.36621 | 60.3699 | -0.2243 | -0.041198 | 0.032043 | 0.25635 | -0.050354 | 0.032044 | -0.10529 | 0.073242 | -0.064087 | 0.086976 | 123.6649 | -0.009156 | 123.8388 | 123.6237 | 123.6145 | 123.4818 | 123.5733 | -123.6832 | -123.5825 | 123.5229 | 123.7976 | 60.3241 | 60.7361
137.4844 | 123.7289 | -60.2875 | 63.3316 | 0.20166 | -0.0014175 | 0.056722 | 0.06728 | 0.014488 | 0.017386 | -0.012447 | -0.052476 | 0.00015838 | 0.083843 | 0.073669 | 0.00025378 | 0.0052979 | 0.0068215 | 0.004578 | 63.2584 | -60.466 | 63.4277 | -60.1227 | -60.2417 | 0.17395 | -0.073242 | 63.2584 | -60.379 | 63.4094 | -60.3653 | -60.498 | -60.347 | -0.17853 | -0.073242 | 0.09613 | 0.16479 | 60.4614 | 0.045777 | 60.64 | 0.2243 | -0.091552 | -0.073242 | 0.07782 | -0.077819 | -0.059509 | -0.21057 | 0.032043 | -0.11902 | 0.34332 | 123.8937 | 0.013733 | 123.7885 | 123.7244 | 123.6374 | 123.5458 | 123.5458 | -123.7976 | -123.7106 | 123.7152 | 123.6969 | 60.2921 | 60.2142
138.4844 | 123.8342 | -60.2829 | 63.2767 | 0.03381 | 0.0039235 | 0.060994 | 0.059804 | 0.01342 | 0.0045688 | 0.0025066 | 0.19167 | 0.0087034 | 0.066753 | 0.045898 | -0.0050872 | -0.0021781 | 0.00041246 | -0.009155 | 63.208 | -60.4156 | 63.3224 | -60.26 | -60.6033 | -0.064087 | 0.064087 | 63.2355 | -60.3287 | 63.4598 | -60.2554 | -60.3745 | -60.2463 | -0.13275 | -0.068664 | 0.045777 | 0.022888 | 60.2188 | -0.32043 | 60.3516 | -0.18768 | -0.045776 | -0.041198 | 0.18311 | 0.027466 | 0.036621 | -0.091553 | 0.082397 | -0.045777 | 0.15564 | 123.7381 | 0.073242 | 123.7885 | 123.6237 | 123.5641 | 123.4909 | 123.5184 | -123.6923 | -123.6053 | 123.6053 | 123.7427 | 60.2737 | 60.347
139.4844 | 123.7381 | -60.2554 | 63.2584 | 0.03381 | 0.0039235 | 0.053517 | 0.065144 | 0.0070111 | 0.023795 | -0.014583 | 0.22218 | 0.0033634 | 0.053935 | 0.052307 | 0.00025378 | 0.0031619 | 0.017502 | 0.027466 | 63.2126 | -60.4156 | 63.2858 | -60.3287 | -60.6445 | -0.045776 | 0.16022 | 63.2446 | -60.3195 | 63.3224 | -60.0266 | -60.0815 | -60.2005 | -0.16022 | -0.045777 | 0.027466 | -0.073242 | 60.2097 | -0.3891 | 60.3699 | -0.22888 | -0.064087 | -0.013733 | 0.064087 | 0.22888 | 0.054932 | 0.17395 | 0.11902 | 0.23804 | 0.086975 | 123.7015 | 0.29297 | 123.642 | 123.6282 | 123.5641 | 123.468 | 123.5001 | -123.674 | -123.5779 | 123.5413 | 123.5779 | 60.2829 | 60.4156
140.4844 | 123.7152 | -60.3333 | 63.295 | 0.1864 | 0.0060595 | 0.052449 | 0.076894 | -0.0068739 | 0.025931 | -0.0028344 | -0.11351 | 0.012976 | 0.075298 | 0.057647 | -0.0018822 | 0.018116 | 0.0046845 | -0.009155 | 63.2492 | -60.466 | 63.4094 | -60.1868 | -60.5164 | 0.032043 | -0.032043 | 63.2721 | -60.3516 | 63.3728 | -60.4019 | -60.5438 | -60.3424 | -0.13275 | -0.045776 | 0.11444 | 0.14648 | 60.3653 | -0.1831 | 60.498 | -0.050354 | -0.01831 | -0.022888 | 0.07782 | -0.068665 | -0.009155 | -0.21057 | 0.009155 | -0.19226 | 0.27923 | 123.8754 | -0.050355 | 123.7244 | 123.7152 | 123.6237 | 123.5825 | 123.6053 | -123.761 | -123.6465 | 123.7427 | 123.7061 | 60.3241 | 60.3012
141.4844 | 123.8846 | -60.2371 | 63.2858 | 0.094845 | -0.0035535 | 0.065267 | 0.064076 | -0.011147 | 0.023795 | -0.014583 | 0.17641 | 0.0054994 | 0.065685 | 0.069397 | 0.0066628 | -4.2099e-05 | 0.014297 | 0.036621 | 63.2401 | -60.4202 | 63.2904 | -60.2829 | -60.6354 | -0.07782 | 0.15106 | 63.2584 | -60.3058 | 63.4918 | -60.2051 | -60.3287 | -60.2188 | -0.1831 | -0.045777 | 0.004577 | -0.045776 | 60.1593 | -0.39825 | 60.3424 | -0.21515 | -0.068664 | -0.027466 | 0.20599 | 0.032044 | 0.018311 | -0.091552 | 0.086975 | -0.022888 | 0.13733 | 123.7106 | 0.10071 | 123.7976 | 123.6603 | 123.5641 | 123.4772 | 123.4955 | -123.7061 | -123.5916 | 123.5275 | 123.7289 | 60.2737 | 60.3882
142.4844 | 123.761 | -60.3012 | 63.3224 | 0.049069 | -0.0035535 | 0.062062 | 0.073689 | 0.010216 | -0.021066 | -0.0071064 | -0.021958 | 0.0076354 | 0.078502 | 0.050171 | -0.0072232 | 0.0042299 | -0.0017235 | 0.036621 | 63.2584 | -60.4477 | 63.4415 | -60.1318 | -60.4568 | 0.086975 | -0.027466 | 63.2996 | -60.3653 | 63.3957 | -60.3378 | -60.4614 | -60.3195 | -0.14648 | -0.064087 | 0.11902 | 0.16937 | 60.3882 | -0.15564 | 60.5347 | -0.009155 | -0.064087 | -0.022888 | 0.073242 | -0.036622 | -0.018311 | -0.16022 | 0.045776 | -0.096131 | 0.31586 | 123.8892 | 0.027465 | 123.761 | 123.7061 | 123.6649 | 123.5596 | 123.6008 | -123.7701 | -123.6877 | 123.7427 | 123.6969 | 60.3378 | 60.2737
143.4844 | 123.8571 | -60.2371 | 63.2721 | 0.12536 | -0.0056895 | 0.053517 | 0.08437 | 0.010216 | 0.016318 | 0.0035746 | 0.34425 | 0.0054994 | 0.071025 | 0.049103 | -0.0050872 | 0.0085029 | -0.022018 | 0.07782 | 63.2355 | -60.3836 | 63.295 | -60.1089 | -60.2692 | -0.17853 | 0.013733 | 63.2034 | -60.3424 | 63.4872 | -60.2234 | -60.3653 | -60.2417 | -0.14648 | -0.036621 | 0.022888 | 0.12817 | 60.0586 | -0.032043 | 60.2051 | 0.11444 | -0.10529 | -0.068665 | 0.21515 | 0.013733 | -0.004577 | -0.12817 | 0.10071 | -0.022888 | 0.27466 | 123.6786 | 0.11902 | 123.8297 | 123.6191 | 123.5458 | 123.4726 | 123.4406 | -123.6557 | -123.6145 | 123.5321 | 123.7244 | 60.3149 | 60.2509
144.4844 | 123.8434 | -60.2737 | 63.2767 | 0.20166 | 0.0039235 | 0.062062 | 0.06194 | 0.024101 | 0.021659 | -0.0049704 | 0.23744 | 0.0097714 | 0.076366 | 0.073669 | -0.0147 | -0.0043151 | 0.0014805 | 0.018311 | 63.2309 | -60.4156 | 63.2996 | -60.2554 | -60.5804 | -0.041199 | 0.086975 | 63.208 | -60.347 | 63.4827 | -60.2509 | -60.379 | -60.2509 | -0.14191 | -0.045776 | 0.022889 | 0.018311 | 60.2325 | -0.3067 | 60.3745 | -0.16479 | -0.073242 | -0.068664 | 0.20599 | 0.022889 | 0.022889 | -0.10528 | 0.096131 | -0.032043 | 0.16022 | 123.7152 | 0.096131 | 123.8297 | 123.6465 | 123.555 | 123.5046 | 123.4818 | -123.6923 | -123.6237 | 123.5733 | 123.7564 | 60.2921 | 60.3607
145.4844 | 123.7518 | -60.2875 | 63.327 | 0.29321 | -0.0014175 | 0.05779 | 0.06728 | 0.0027391 | 0.0067048 | 0.0046426 | -0.0066996 | 0.00015838 | 0.063548 | 0.068329 | -0.0061552 | -0.0075191 | 0.011093 | 0.013733 | 63.2584 | -60.4568 | 63.4781 | -60.0998 | -60.4523 | 0.091553 | -0.045776 | 63.3041 | -60.3516 | 63.3728 | -60.3653 | -60.4935 | -60.3333 | -0.16937 | -0.068664 | 0.15106 | 0.18768 | 60.379 | -0.1648 | 60.5484 | 0.004577 | -0.064086 | -0.022888 | 0.045777 | -0.077819 | -0.045776 | -0.20599 | 0.01831 | -0.14191 | 0.35706 | 123.9349 | -0.013733 | 123.7244 | 123.7152 | 123.6557 | 123.5458 | 123.5916 | -123.7839 | -123.6786 | 123.7656 | 123.6603 | 60.3012 | 60.2417
146.4844 | 123.8434 | -60.2692 | 63.2812 | 0.14062 | -0.012098 | 0.055654 | 0.060872 | -0.012215 | 0.0067048 | -0.0039024 | 0.23744 | 0.0044314 | 0.066753 | 0.041626 | -0.0050872 | 0.0085029 | -0.0092005 | 0.041199 | 63.2126 | -60.4156 | 63.295 | -60.3149 | -60.6445 | -0.054932 | 0.14191 | 63.2446 | -60.3241 | 63.501 | -60.2325 | -60.3241 | -60.2142 | -0.14648 | -0.068665 | 0.013733 | -0.045776 | 60.2142 | -0.37537 | 60.3607 | -0.22888 | -0.054932 | -0.036621 | 0.21973 | 0.036621 | 0.054932 | -0.054932 | 0.10986 | 0 | 0.10071 | 123.7106 | 0.091553 | 123.8251 | 123.6282 | 123.5687 | 123.4818 | 123.5138 | -123.6969 | -123.6053 | 123.5641 | 123.7701 | 60.3104 | 60.4111
147.4844 | 123.7152 | -60.2966 | 63.3453 | 0.079586 | -0.0014175 | 0.058858 | 0.065144 | -0.0004649 | -0.01893 | -0.0028344 | 0.069594 | 0.0065674 | 0.075298 | 0.091827 | 0.0013218 | 0.0095709 | 0.0057535 | -0.064087 | 63.2812 | -60.4797 | 63.4552 | -60.0677 | -60.4248 | 0.10986 | -0.045776 | 63.2904 | -60.3561 | 63.3774 | -60.3745 | -60.4843 | -60.3424 | -0.18311 | -0.064087 | 0.10986 | 0.22888 | 60.4065 | -0.12817 | 60.5896 | 0.054931 | -0.059509 | -0.054932 | 0.032043 | -0.07782 | -0.045776 | -0.18768 | 0.013733 | -0.12817 | 0.41199 | 123.9349 | -0.018311 | 123.7335 | 123.761 | 123.6465 | 123.5779 | 123.587 | -123.8251 | -123.7015 | 123.7518 | 123.674 | 60.2325 | 60.2509
148.4844 | 123.8709 | -60.2737 | 63.2675 | 0.094845 | 0.0060595 | 0.070607 | 0.069417 | 0.012352 | 0.0035008 | -0.0017664 | 0.20692 | 0.0044314 | 0.076366 | 0.049103 | 0.00025378 | 0.012775 | 0.011093 | 0.018311 | 63.2034 | -60.3973 | 63.327 | -60.2554 | -60.6079 | -0.059509 | 0.086975 | 63.2538 | -60.3241 | 63.4781 | -60.2692 | -60.347 | -60.26 | -0.1236 | -0.064087 | 0.059509 | 0.018311 | 60.2142 | -0.33417 | 60.3378 | -0.21057 | -0.050354 | -0.013733 | 0.21057 | 0.004578 | 0.013733 | -0.073242 | 0.064087 | -0.022888 | 0.14191 | 123.7244 | 0.054932 | 123.8022 | 123.6008 | 123.5779 | 123.4772 | 123.5275 | -123.6649 | -123.5916 | 123.6008 | 123.7518 | 60.2921 | 60.3607
149.4844 | 123.8388 | -60.2692 | 63.2767 | 0.079586 | -0.0067575 | 0.060994 | 0.069417 | -0.0026019 | 0.026999 | 0.01746 | 0.23744 | 0.0065674 | 0.078502 | 0.040558 | -0.0018822 | 0.011707 | -0.0017235 | 0.009155 | 63.2172 | -60.3928 | 63.3179 | -60.2371 | -60.5942 | -0.032043 | 0.045776 | 63.2172 | -60.3561 | 63.4598 | -60.2646 | -60.3745 | -60.2509 | -0.1236 | -0.059509 | 0.041199 | 0.032043 | 60.2371 | -0.32501 | 60.3607 | -0.20142 | -0.086975 | -0.059509 | 0.18311 | 0.004578 | 0.018311 | -0.10529 | 0.10529 | -0.018311 | 0.15564 | 123.7106 | 0.091553 | 123.8159 | 123.6099 | 123.5733 | 123.4863 | 123.4863 | -123.6694 | -123.6328 | 123.587 | 123.7289 | 60.2783 | 60.3149
150.4844 | 123.674 | -60.3333 | 63.3179 | 0.018551 | -0.0014175 | 0.053517 | 0.069417 | 0.0059431 | -0.0018402 | -0.024196 | -0.12877 | 0.010839 | 0.078502 | 0.040558 | -0.0072232 | 0.0052979 | -0.0017235 | -0.054932 | 63.2355 | -60.4706 | 63.4323 | -60.1227 | -60.498 | 0.050354 | -0.10986 | 63.2858 | -60.3928 | 63.3087 | -60.4889 | -60.5804 | -60.3836 | -0.13733 | -0.082397 | 0.11444 | 0.21057 | 60.3836 | -0.16479 | 60.5209 | -0.027466 | -0.059509 | -0.032043 | -0.009155 | -0.15564 | -0.050354 | -0.24719 | 0.009155 | -0.18768 | 0.3479 | 123.9029 | -0.096131 | 123.7015 | 123.7061 | 123.6786 | 123.5687 | 123.6191 | -123.7885 | -123.7106 | 123.7656 | 123.642 | 60.2783 | 60.2234
151.4844 | 123.8434 | -60.2829 | 63.295 | 0.064327 | 0.00071953 | 0.058858 | 0.059804 | 0.0070111 | 0.0035008 | -0.0092424 | 0.26796 | -0.0051816 | 0.076366 | 0.042694 | -0.0029502 | 0.0085029 | 0.016434 | -0.027466 | 63.2401 | -60.3928 | 63.3453 | -60.228 | -60.5759 | -0.032043 | 0.004578 | 63.2126 | -60.3287 | 63.4552 | -60.2921 | -60.3882 | -60.2646 | -0.10986 | -0.054932 | 0.050354 | 0.054932 | 60.2509 | -0.29297 | 60.3607 | -0.18311 | -0.045776 | -0.082398 | 0.16022 | -0.009155 | 0.018311 | -0.10529 | 0.064087 | -0.05951 | 0.16479 | 123.7381 | 0.036621 | 123.7839 | 123.6328 | 123.5413 | 123.5229 | 123.4955 | -123.6877 | -123.6237 | 123.6282 | 123.7381 | 60.2554 | 60.2875
152.4844 | 123.793 | -60.2829 | 63.2904 | 0.079586 | 0.0092645 | 0.068471 | 0.06728 | 0.0070111 | 0.0024328 | -0.00069841 | 0.20692 | 0.00015838 | 0.06248 | 0.066192 | -0.0147 | 0.0010259 | 0.013229 | 0.073242 | 63.2263 | -60.4248 | 63.3133 | -60.2554 | -60.5896 | -0.013733 | 0.10529 | 63.2675 | -60.3058 | 63.4689 | -60.2829 | -60.379 | -60.2509 | -0.14191 | -0.064087 | 0.022888 | 0.027466 | 60.2692 | -0.3067 | 60.4111 | -0.16479 | -0.022888 | -0.022888 | 0.17853 | 0 | 0.032044 | -0.09613 | 0.054932 | -0.073242 | 0.16937 | 123.7381 | 0.022888 | 123.7747 | 123.6511 | 123.5733 | 123.5092 | 123.5504 | -123.7152 | -123.5962 | 123.5962 | 123.7518 | 60.3561 | 60.3882
153.4844 | 123.8159 | -60.2829 | 63.2858 | 0.03381 | 0.0071275 | 0.054585 | 0.069417 | 0.0027391 | 0.016318 | 0.00037059 | 0.13063 | 0.0065674 | 0.055004 | 0.037353 | -0.0040182 | -0.0075191 | 0.0046845 | 0.004578 | 63.2263 | -60.4431 | 63.3224 | -60.228 | -60.5804 | -0.045776 | 0.050354 | 63.2492 | -60.3287 | 63.446 | -60.2692 | -60.3653 | -60.2509 | -0.16022 | -0.05951 | 0.036621 | 0.054932 | 60.2371 | -0.29755 | 60.3973 | -0.13733 | -0.045776 | -0.036621 | 0.16022 | 0.013733 | 0.032044 | -0.082397 | 0.07782 | -0.036621 | 0.21515 | 123.7656 | 0.059509 | 123.7747 | 123.6694 | 123.5779 | 123.5092 | 123.5321 | -123.7289 | -123.6145 | 123.6053 | 123.7289 | 60.2875 | 60.3333
154.4844 | 123.8159 | -60.2966 | 63.2812 | 0.1864 | -0.0067575 | 0.065267 | 0.056599 | -0.0026019 | -0.00077219 | -0.0092424 | 0.19167 | -0.0030456 | 0.072093 | 0.040558 | -0.0029502 | -0.0043151 | 0.015366 | -0.022888 | 63.2126 | -60.4248 | 63.3362 | -60.2371 | -60.5759 | -0.036621 | 0.032043 | 63.2263 | -60.3333 | 63.4689 | -60.2737 | -60.3653 | -60.2646 | -0.12817 | -0.068665 | 0.054932 | 0.059509 | 60.26 | -0.27924 | 60.3882 | -0.15106 | -0.036621 | -0.054932 | 0.18768 | 0.022888 | 0.032044 | -0.068664 | 0.068665 | -0.032043 | 0.18768 | 123.761 | 0.059509 | 123.8022 | 123.6374 | 123.5596 | 123.5092 | 123.5229 | -123.7061 | -123.6145 | 123.6328 | 123.7656 | 60.2737 | 60.3287
155.4844 | 123.7061 | -60.2829 | 63.3133 | 0.46106 | 0.0071275 | 0.064198 | 0.064076 | -0.013283 | -0.019998 | 0.016392 | 0.023818 | 0.010839 | 0.076366 | 0.069397 | -0.0050872 | 0.0063669 | 0.0014805 | -0.068665 | 63.2996 | -60.434 | 63.4644 | -60.1273 | -60.4568 | 0.12817 | -0.045776 | 63.2996 | -60.347 | 63.3636 | -60.3882 | -60.4889 | -60.3333 | -0.15106 | -0.013732 | 0.15106 | 0.15564 | 60.4111 | -0.17395 | 60.5621 | -0.022888 | -0.064087 | -0.013732 | 0.050354 | -0.10529 | -0.050354 | -0.20599 | 0.013733 | -0.14191 | 0.3067 | 123.8983 | -0.041199 | 123.7106 | 123.7335 | 123.6465 | 123.5825 | 123.5825 | -123.7473 | -123.6603 | 123.7473 | 123.6465 | 60.2142 | 60.2371
156.4844 | 123.8113 | -60.2783 | 63.2767 | 0.12536 | 0.0039235 | 0.062062 | 0.058736 | 0.0006031 | 0.0056368 | -0.019924 | 0.23744 | -0.0051816 | 0.066753 | 0.074737 | 0.0023898 | 0.0031619 | -0.017746 | -0.068665 | 63.1989 | -60.4523 | 63.3728 | -60.2234 | -60.5438 | -0.027466 | -0.022888 | 63.2309 | -60.3424 | 63.414 | -60.3149 | -60.4156 | -60.2737 | -0.17395 | -0.077819 | 0.096131 | 0.054931 | 60.2509 | -0.2655 | 60.4248 | -0.091552 | -0.064087 | -0.045776 | 0.13733 | -0.036621 | 0.004577 | -0.13733 | 0.068664 | -0.073242 | 0.22888 | 123.8251 | 0.027466 | 123.7564 | 123.6511 | 123.5733 | 123.4772 | 123.5092 | -123.7289 | -123.6191 | 123.6511 | 123.6923 | 60.2097 | 60.2554
157.4844 | 123.7244 | -60.3195 | 63.3362 | 0.1864 | -0.0024855 | 0.05779 | 0.064076 | -0.0090099 | -0.016794 | -0.012447 | 0.14589 | 0.0033634 | 0.066753 | 0.089691 | -0.0018822 | -0.0021781 | 0.01857 | 0.018311 | 63.2584 | -60.434 | 63.4506 | -60.1135 | -60.4523 | 0.09613 | -0.09613 | 63.2996 | -60.3241 | 63.3316 | -60.379 | -60.4111 | -60.3333 | -0.11444 | -0.07782 | 0.11444 | 0.20599 | 60.4156 | -0.13275 | 60.5301 | -0.018311 | -0.004578 | -0.036621 | -0.004578 | -0.059509 | -0.013733 | -0.091553 | -0.009155 | -0.086975 | 0.32043 | 123.8846 | -0.054931 | 123.6557 | 123.6923 | 123.6237 | 123.5779 | 123.6191 | -123.7701 | -123.6603 | 123.7701 | 123.6511 | 60.3378 | 60.2234
158.4844 | 123.7747 | -60.2921 | 63.2812 | 0.17114 | 0.0049915 | 0.05779 | 0.070485 | 0.023033 | 0.014182 | 0.0025066 | 0.17641 | 0.0044314 | 0.072093 | 0.058716 | -0.011495 | 0.0095709 | -0.0081325 | -0.041199 | 63.2034 | -60.434 | 63.3224 | -60.2509 | -60.5484 | 0.004578 | -0.022888 | 63.2492 | -60.3561 | 63.3865 | -60.3241 | -60.4202 | -60.2829 | -0.14191 | -0.07782 | 0.041199 | 0.041199 | 60.2966 | -0.25635 | 60.4385 | -0.11444 | -0.064087 | -0.032043 | 0.10529 | -0.032044 | 0.009155 | -0.12817 | 0.073242 | -0.064087 | 0.18311 | 123.7564 | 0.032043 | 123.7427 | 123.6374 | 123.6053 | 123.4955 | 123.5413 | -123.7152 | -123.6374 | 123.6145 | 123.6786 | 60.2509 | 60.2692
159.4844 | 123.7701 | -60.2875 | 63.2767 | 0.094845 | 0.0081955 | 0.06313 | 0.066212 | -0.0026019 | -0.0071802 | 0.01746 | 0.20692 | -0.0094546 | 0.069957 | 0.069397 | 0.0034578 | -0.0032471 | 0.015366 | -0.059509 | 63.2263 | -60.4156 | 63.3499 | -60.2188 | -60.5667 | -0.022888 | -0.032043 | 63.2446 | -60.3195 | 63.4186 | -60.4111 | -60.4111 | -60.2783 | -0.12817 | -0.050354 | 0.073243 | 0.068665 | 60.2646 | -0.27923 | 60.3928 | -0.15106 | -0.032043 | -0.032043 | 0.14191 | -0.1236 | 0.009156 | -0.1236 | 0.041199 | -0.091553 | 0.19684 | 123.7656 | -0.091553 | 123.7381 | 123.642 | 123.5641 | 123.5138 | 123.5321 | -123.6923 | -123.5962 | 123.6374 | 123.7061 | 60.228 | 60.2554
160.4844 | 123.7839 | -60.2966 | 63.295 | 0.094845 | -0.0046215 | 0.064198 | 0.069417 | -0.0047379 | 0.019522 | -0.013515 | 0.13063 | 0.0044314 | 0.073162 | 0.032013 | -0.0050872 | -0.011791 | -0.0092005 | -0.068665 | 63.2263 | -60.4202 | 63.327 | -60.2234 | -60.5804 | -0.036621 | -0.022888 | 63.2401 | -60.3378 | 63.4277 | -60.3287 | -60.4156 | -60.2829 | -0.1236 | -0.068665 | 0.032043 | 0.073242 | 60.26 | -0.28381 | 60.3836 | -0.16022 | -0.041199 | -0.054932 | 0.13275 | -0.032043 | 0.013733 | -0.11902 | 0.054932 | -0.077819 | 0.19684 | 123.7473 | 0.009156 | 123.7656 | 123.6465 | 123.5779 | 123.5229 | 123.5367 | -123.7152 | -123.6328 | 123.6237 | 123.7244 | 60.228 | 60.2737
161.4844 | 123.7976 | -60.2783 | 63.2721 | 0.079586 | -0.00034947 | 0.058858 | 0.075825 | -0.010078 | -0.019998 | 0.0057106 | 0.084853 | -0.0030456 | 0.056072 | 0.089691 | -0.0029502 | -0.0096551 | -0.010269 | -0.041199 | 63.2217 | -60.4431 | 63.3179 | -60.2234 | -60.5301 | -0.032043 | -0.022888 | 63.2355 | -60.3378 | 63.4232 | -60.3149 | -60.4111 | -60.2737 | -0.16479 | -0.050354 | 0.045776 | 0.054931 | 60.2463 | -0.25177 | 60.4111 | -0.086975 | -0.05951 | -0.036621 | 0.15106 | -0.036621 | 0.004577 | -0.13275 | 0.064087 | -0.073242 | 0.21973 | 123.761 | 0.022889 | 123.761 | 123.6649 | 123.5733 | 123.5001 | 123.5138 | -123.7152 | -123.6099 | 123.5962 | 123.7015 | 60.2371 | 60.2554
162.4844 | 123.7518 | -60.2646 | 63.3316 | 0.1101 | 0.0071275 | 0.062062 | 0.070485 | 0.0080791 | 0.014182 | -0.0028344 | 0.14589 | 0.00015838 | 0.063548 | 0.064056 | -0.0072232 | -0.0043151 | 0.00041246 | 0.082397 | 63.2584 | -60.4019 | 63.3362 | -60.2325 | -60.5759 | 0.013733 | 0.073242 | 63.2584 | -60.347 | 63.4323 | -60.3149 | -60.4111 | -60.2783 | -0.13733 | -0.073242 | 0.004578 | 0.032043 | 60.2783 | -0.31128 | 60.4156 | -0.17395 | -0.082398 | -0.073242 | 0.10071 | -0.050354 | -0.013733 | -0.14648 | 0.068665 | -0.064087 | 0.16937 | 123.7381 | 0.032044 | 123.7793 | 123.6603 | 123.6053 | 123.5229 | 123.5229 | -123.7335 | -123.6786 | 123.6008 | 123.6969 | 60.347 | 60.3378
163.4844 | 123.8663 | -60.2875 | 63.2584 | 0.094845 | -0.0067575 | 0.058858 | 0.071553 | -0.0004649 | 0.013114 | 0.00037059 | 0.11537 | 0.0087034 | 0.073162 | 0.06192 | -0.0040182 | 0.0042299 | -0.0017235 | -0.059509 | 63.1805 | -60.4294 | 63.3362 | -60.2325 | -60.5621 | -0.027466 | -0.050354 | 63.2355 | -60.3653 | 63.4048 | -60.3424 | -60.4385 | -60.2966 | -0.14191 | -0.07782 | 0.07782 | 0.054932 | 60.26 | -0.27466 | 60.4019 | -0.13275 | -0.077819 | -0.022888 | 0.14648 | -0.054931 | -0.009155 | -0.15106 | 0.068664 | -0.073243 | 0.19684 | 123.7656 | 0.022888 | 123.7701 | 123.6099 | 123.6008 | 123.468 | 123.523 | -123.6877 | -123.6237 | 123.6237 | 123.6923 | 60.228 | 60.2371
164.4844 | 123.8113 | -60.2692 | 63.2767 | 0.049069 | 0.0028555 | 0.062062 | 0.065144 | 0.0091481 | -0.013589 | 0.0025066 | 0.23744 | -0.0030456 | 0.063548 | 0.046966 | -0.0082912 | 0.0010259 | -0.0059965 | 0.054932 | 63.2309 | -60.4248 | 63.3591 | -60.1913 | -60.5713 | -0.054932 | -0.027466 | 63.2309 | -60.3516 | 63.446 | -60.3287 | -60.4156 | -60.2875 | -0.15564 | -0.045776 | 0.082398 | 0.07782 | 60.2142 | -0.30212 | 60.3699 | -0.14648 | -0.082397 | -0.045776 | 0.16937 | -0.059509 | -0.018311 | -0.14648 | 0.064086 | -0.064087 | 0.23346 | 123.7839 | 0.022888 | 123.7976 | 123.6557 | 123.5825 | 123.5001 | 123.5001 | -123.7015 | -123.6282 | 123.6282 | 123.7152 | 60.3241 | 60.2417
165.4844 | 123.7701 | -60.2783 | 63.2584 | 0.018551 | 0.0028555 | 0.070607 | 0.065144 | 0.018761 | 0.012046 | -0.0081744 | 0.084853 | -0.0062496 | 0.076366 | 0.07901 | -0.0050872 | -0.0011101 | -0.017746 | -0.068665 | 63.2126 | -60.4065 | 63.327 | -60.228 | -60.5667 | -0.045776 | -0.050354 | 63.2401 | -60.3561 | 63.414 | -60.3149 | -60.4431 | -60.3012 | -0.12817 | -0.045777 | 0.068664 | 0.050354 | 60.2325 | -0.28839 | 60.3607 | -0.16022 | -0.07782 | -0.018311 | 0.15564 | -0.036621 | -0.022888 | -0.16479 | 0.054932 | -0.086975 | 0.17853 | 123.7335 | 0.041199 | 123.7701 | 123.6191 | 123.5962 | 123.4909 | 123.5184 | -123.6649 | -123.6145 | 123.6053 | 123.6923 | 60.2097 | 60.228
166.4844 | 123.7701 | -60.2875 | 63.2767 | 0.14062 | -0.0046215 | 0.064198 | 0.06194 | -0.0015339 | -0.0093172 | -0.0017664 | 0.11537 | -0.010523 | 0.05714 | 0.026672 | -0.0040182 | 0.0074349 | -0.030563 | -0.07782 | 63.1989 | -60.4248 | 63.3224 | -60.228 | -60.5667 | -0.050354 | -0.032043 | 63.2355 | -60.3836 | 63.4048 | -60.3195 | -60.4431 | -60.2875 | -0.13733 | -0.077819 | 0.045777 | 0.05951 | 60.2371 | -0.27923 | 60.3745 | -0.14191 | -0.09613 | -0.041198 | 0.12817 | -0.032043 | 0 | -0.15564 | 0.09613 | -0.059509 | 0.19684 | 123.7473 | 0.064087 | 123.7885 | 123.6237 | 123.6191 | 123.4863 | 123.523 | -123.7015 | -123.6603 | 123.6099 | 123.6923 | 60.2097 | 60.2554
167.4844 | 123.8525 | -60.26 | 63.2812 | 0.12536 | 0.00071953 | 0.048177 | 0.059804 | -0.012215 | -0.021066 | 0.016392 | 0.16115 | 0.0012264 | 0.068889 | 0.071533 | -0.0082912 | 0.0010259 | -0.031632 | 0.032043 | 63.1989 | -60.4065 | 63.2858 | -60.2829 | -60.6354 | -0.068665 | 0.13733 | 63.2492 | -60.3195 | 63.5056 | -60.2142 | -60.3104 | -60.2188 | -0.14648 | -0.082397 | 0.004578 | -0.022888 | 60.1913 | -0.37537 | 60.3378 | -0.22888 | -0.059509 | -0.032043 | 0.2243 | 0.045777 | 0.041199 | -0.050354 | 0.10071 | 0.009155 | 0.1236 | 123.6923 | 0.10529 | 123.8251 | 123.6053 | 123.5687 | 123.4589 | 123.5092 | -123.6877 | -123.6008 | 123.5458 | 123.7656 | 60.2921 | 60.3973
168.4844 | 123.7885 | -60.2875 | 63.2629 | 0.14062 | 0.0049915 | 0.058858 | 0.055531 | -0.0026019 | 0.0067048 | -0.00069841 | 0.069594 | 0.010839 | 0.071025 | 0.038421 | -0.0093592 | -0.0011101 | 0.0014805 | -0.059509 | 63.1943 | -60.4431 | 63.3453 | -60.2142 | -60.5576 | -0.027466 | -0.050354 | 63.2446 | -60.3561 | 63.4094 | -60.3516 | -60.434 | -60.2966 | -0.15564 | -0.068664 | 0.082398 | 0.073243 | 60.26 | -0.27008 | 60.4156 | -0.11444 | -0.068664 | -0.01831 | 0.14648 | -0.064086 | -0.009155 | -0.14648 | 0.059509 | -0.07782 | 0.22888 | 123.7885 | 0.004578 | 123.7656 | 123.6374 | 123.6008 | 123.4818 | 123.5321 | -123.7061 | -123.6191 | 123.6328 | 123.6969 | 60.228 | 60.2371
169.4688 | 123.7747 | -60.2921 | 63.2492 | 0.12536 | 0.0017875 | 0.062062 | 0.064076 | 0.0006031 | -0.0082492 | -0.00069841 | 0.10011 | -0.0030456 | 0.066753 | 0.053375 | -0.0050872 | 0.0042299 | 0.010025 | -0.054932 | 63.2217 | -60.4431 | 63.3408 | -60.2097 | -60.5621 | -0.027466 | -0.036621 | 63.2446 | -60.347 | 63.4186 | -60.347 | -60.3973 | -60.2646 | -0.15106 | -0.027466 | 0.091552 | 0.082397 | 60.2646 | -0.27008 | 60.4156 | -0.11902 | -0.054932 | -0.004578 | 0.16937 | -0.054932 | 0.027466 | -0.10529 | 0.082398 | -0.050354 | 0.23346 | 123.7839 | 0 | 123.7656 | 123.6649 | 123.5916 | 123.5138 | 123.5367 | -123.6923 | -123.5962 | 123.6328 | 123.7106 | 60.2371 | 60.2554
170.4844 | 123.7701 | -60.3012 | 63.2492 | 0.018551 | 0.0049915 | 0.06313 | 0.065144 | 0.015556 | -0.0039762 | 0.0025066 | 0.10011 | -0.0019776 | 0.075298 | 0.056579 | -0.0050872 | -0.0011101 | -0.0017235 | -0.068665 | 63.176 | -60.4065 | 63.327 | -60.2188 | -60.5759 | -0.036621 | -0.050354 | 63.2401 | -60.3378 | 63.3957 | -60.3241 | -60.4568 | -60.3104 | -0.10529 | -0.073243 | 0.077819 | 0.082397 | 60.2646 | -0.27466 | 60.3699 | -0.16937 | -0.036622 | -0.009156 | 0.14648 | -0.022889 | -0.009156 | -0.15564 | 0.027466 | -0.11902 | 0.18768 | 123.7335 | 0.013733 | 123.7335 | 123.5825 | 123.5779 | 123.4772 | 123.5413 | -123.6557 | -123.587 | 123.6282 | 123.6969 | 60.2325 | 60.2509
171.4844 | 123.8022 | -60.2692 | 63.2767 | 0.14062 | -0.00034947 | 0.062062 | 0.075825 | -0.0079419 | 0.0067048 | -0.0081744 | 0.069594 | 0.011908 | 0.069957 | 0.060852 | -0.0040182 | 0.0020939 | -0.019882 | -0.036621 | 63.2263 | -60.4431 | 63.3499 | -60.228 | -60.5713 | -0.027466 | -0.022888 | 63.2309 | -60.3516 | 63.4644 | -60.347 | -60.3973 | -60.2829 | -0.17395 | -0.050354 | 0.073243 | 0.041199 | 60.2417 | -0.30212 | 60.4156 | -0.12817 | -0.082397 | -0.045776 | 0.18768 | -0.07782 | -0.013733 | -0.12817 | 0.068664 | -0.045777 | 0.21515 | 123.793 | 0.004577 | 123.8159 | 123.6694 | 123.5825 | 123.4955 | 123.5001 | -123.7198 | -123.6282 | 123.6191 | 123.7335 | 60.2325 | 60.2463
172.4844 | 123.8434 | -60.2646 | 63.2538 | 0.094845 | 0.0017875 | 0.054585 | 0.064076 | -0.0079419 | 0.0024328 | 0.0035746 | 0.10011 | 0.012976 | 0.060344 | 0.075805 | -0.0029502 | 0.0010259 | -0.013474 | -0.041199 | 63.2126 | -60.4294 | 63.327 | -60.2371 | -60.5804 | -0.032043 | 0.022888 | 63.2401 | -60.3333 | 63.4781 | -60.2554 | -60.3928 | -60.2554 | -0.16479 | -0.041199 | 0.073242 | 0.027465 | 60.2325 | -0.31586 | 60.3973 | -0.15106 | -0.068665 | -0.013733 | 0.2243 | 0.009155 | 0.009155 | -0.12817 | 0.07782 | -0.059509 | 0.19226 | 123.7564 | 0.07782 | 123.8113 | 123.642 | 123.5733 | 123.4772 | 123.5046 | -123.6832 | -123.587 | 123.5916 | 123.7427 | 60.2234 | 60.2875
173.4844 | 123.7656 | -60.2829 | 63.2629 | 0.17114 | -0.0056895 | 0.06313 | 0.065144 | -0.010078 | 0.016318 | -0.0060384 | 0.22218 | -0.0041136 | 0.059276 | 0.049103 | 0.0098668 | -0.0053831 | -0.017746 | -0.050354 | 63.2034 | -60.4431 | 63.3545 | -60.2097 | -60.5713 | -0.027466 | -0.054932 | 63.2584 | -60.3561 | 63.4003 | -60.3424 | -60.4431 | -60.2829 | -0.16022 | -0.059509 | 0.091553 | 0.073242 | 60.2554 | -0.28839 | 60.4156 | -0.12817 | -0.073242 | -0.004577 | 0.13733 | -0.059509 | 0 | -0.16022 | 0.073242 | -0.086975 | 0.23346 | 123.7976 | 0.013733 | 123.7564 | 123.6465 | 123.6145 | 123.4863 | 123.5413 | -123.7061 | -123.6191 | 123.6374 | 123.6832 | 60.2325 | 60.228
174.4844 | 123.7747 | -60.3058 | 63.2721 | 0.1101 | 0.015673 | 0.060994 | 0.070485 | 0.0059431 | -0.0050442 | -0.011379 | 0.069594 | 0.011908 | 0.05714 | 0.072601 | 0.0013218 | 0.010639 | -0.0070645 | -0.050354 | 63.1989 | -60.4156 | 63.3316 | -60.2005 | -60.5667 | -0.022888 | -0.045776 | 63.2309 | -60.347 | 63.414 | -60.3516 | -60.4477 | -60.3149 | -0.10986 | -0.073242 | 0.059509 | 0.10529 | 60.2829 | -0.26093 | 60.3928 | -0.15106 | -0.041199 | -0.041199 | 0.14191 | -0.045776 | -0.009155 | -0.14191 | 0.032044 | -0.10071 | 0.21515 | 123.7473 | -0.004577 | 123.761 | 123.6145 | 123.5779 | 123.5046 | 123.5367 | -123.6877 | -123.6191 | 123.6374 | 123.7198 | 60.2554 | 60.26
175.4844 | 123.7747 | -60.2783 | 63.2538 | 0.14062 | 0.0028555 | 0.052449 | 0.066212 | -0.011147 | -0.0029082 | -0.0081744 | 0.13063 | 0.0033634 | 0.078502 | 0.069397 | -0.0018822 | 0.0063669 | -0.0017235 | -0.07782 | 63.2034 | -60.4568 | 63.3453 | -60.2234 | -60.5621 | -0.041199 | -0.041199 | 63.2172 | -60.3516 | 63.4094 | -60.3378 | -60.4294 | -60.2966 | -0.17853 | -0.050354 | 0.091553 | 0.054931 | 60.2371 | -0.28381 | 60.4156 | -0.10529 | -0.073242 | -0.036621 | 0.15564 | -0.05951 | -0.018311 | -0.15106 | 0.054931 | -0.07782 | 0.23346 | 123.8022 | 0.013732 | 123.761 | 123.6603 | 123.5687 | 123.4818 | 123.4955 | -123.7106 | -123.6053 | 123.6237 | 123.6877 | 60.2005 | 60.2371
176.4844 | 123.7839 | -60.2966 | 63.2767 | -0.042484 | 0.00071953 | 0.055654 | 0.06728 | -0.0047379 | 0.00029581 | -0.0017664 | 0.13063 | 0.0012264 | 0.075298 | 0.048034 | 0.0013218 | 0.0063669 | 0.016434 | -0.07782 | 63.1989 | -60.4202 | 63.327 | -60.2234 | -60.585 | -0.041199 | -0.041199 | 63.2355 | -60.3745 | 63.414 | -60.3378 | -60.4202 | -60.2875 | -0.1236 | -0.077819 | 0.050354 | 0.073242 | 60.2554 | -0.28839 | 60.379 | -0.1648 | -0.07782 | -0.041198 | 0.13733 | -0.041199 | 0.009155 | -0.1236 | 0.086975 | -0.045776 | 0.19684 | 123.7473 | 0.036621 | 123.7885 | 123.6191 | 123.6099 | 123.4955 | 123.5321 | -123.6969 | -123.6511 | 123.6237 | 123.7106 | 60.2188 | 60.2554
177.4844 | 123.7564 | -60.2829 | 63.2767 | 0.17114 | 0.0071275 | 0.06313 | 0.065144 | 0.0016711 | 0.0024328 | 0.0014386 | 0.11537 | -0.0030456 | 0.068889 | 0.088623 | 0.0055948 | 0.0063669 | -0.0038605 | 0.064087 | 63.2355 | -60.4065 | 63.3453 | -60.2188 | -60.5621 | 0.013733 | 0.054932 | 63.2858 | -60.3424 | 63.4277 | -60.3195 | -60.4294 | -60.2921 | -0.1236 | -0.041198 | 0.068665 | 0.064087 | 60.2966 | -0.27924 | 60.4202 | -0.15564 | -0.059509 | 0.009156 | 0.15106 | -0.036621 | -0.009155 | -0.14648 | 0.050354 | -0.086975 | 0.18768 | 123.7518 | 0.022888 | 123.7701 | 123.642 | 123.6282 | 123.5184 | 123.5687 | -123.6832 | -123.6191 | 123.6282 | 123.7106 | 60.347 | 60.3378
178.4844 | 123.7793 | -60.2966 | 63.2584 | 0.064327 | -0.0014175 | 0.054585 | 0.069417 | 0.0038071 | 0.00029581 | 0.0099836 | 0.084853 | 0.0033634 | 0.058208 | 0.08435 | 0.0013218 | -0.0021781 | -0.0038605 | -0.054932 | 63.2034 | -60.4202 | 63.3362 | -60.2142 | -60.553 | -0.022888 | -0.041199 | 63.2355 | -60.347 | 63.4186 | -60.3333 | -60.4477 | -60.2875 | -0.1236 | -0.054932 | 0.07782 | 0.082398 | 60.2737 | -0.25635 | 60.3973 | -0.13275 | -0.050354 | -0.022888 | 0.16022 | -0.036621 | 0.009155 | -0.15106 | 0.059509 | -0.10071 | 0.20599 | 123.7564 | 0.013733 | 123.7656 | 123.6237 | 123.5825 | 123.5001 | 123.5321 | -123.6786 | -123.6053 | 123.6328 | 123.7152 | 60.2417 | 60.2554
179.4844 | 123.7885 | -60.2921 | 63.2446 | 0.15588 | 0.011401 | 0.06313 | 0.063008 | -0.0079419 | 0.0067048 | -0.011379 | 0.0085594 | -0.0041136 | 0.060344 | 0.043762 | -0.0061552 | 0.0052979 | -0.0038605 | -0.050354 | 63.2126 | -60.4202 | 63.2996 | -60.2783 | -60.5896 | -0.07782 | -0.022888 | 63.2126 | -60.347 | 63.4277 | -60.3378 | -60.4111 | -60.2829 | -0.12817 | -0.032044 | 0.054932 | 0.013733 | 60.2142 | -0.29755 | 60.3424 | -0.16937 | -0.054932 | -0.032044 | 0.1831 | -0.045777 | 0.009155 | -0.11902 | 0.064087 | -0.064087 | 0.14191 | 123.7198 | 0.009155 | 123.7747 | 123.6328 | 123.5596 | 123.5046 | 123.5046 | -123.6649 | -123.5916 | 123.5916 | 123.7198 | 60.2417 | 60.2692
180.4844 | 123.7885 | -60.2783 | 63.2401 | 0.049069 | 0.018878 | 0.056722 | 0.063008 | 0.010216 | 0.0056368 | -0.0039024 | -0.0066996 | -0.00090962 | 0.059276 | 0.068329 | 0.0034578 | -0.0043151 | 0.00041246 | -0.050354 | 63.1714 | -60.4202 | 63.295 | -60.2737 | -60.5804 | -0.086975 | 0.009155 | 63.2492 | -60.3516 | 63.4232 | -60.3241 | -60.4431 | -60.2875 | -0.14191 | -0.068664 | 0.054932 | 0.004577 | 60.1913 | -0.30212 | 60.3333 | -0.16022 | -0.073242 | 0.009156 | 0.18311 | -0.045777 | -0.009156 | -0.16479 | 0.064086 | -0.091553 | 0.14648 | 123.7152 | 0.027465 | 123.7747 | 123.5916 | 123.6008 | 123.4497 | 123.5275 | -123.6603 | -123.5916 | 123.5733 | 123.7015 | 60.228 | 60.2875
181.4844 | 123.7656 | -60.2737 | 63.2904 | 0.14062 | 0.0049915 | 0.070607 | 0.057667 | -0.0036699 | -0.0029082 | -0.0049704 | 0.069594 | -0.0051816 | 0.077434 | 0.052307 | -0.0072232 | 0.0020939 | -0.0038605 | -0.068665 | 63.208 | -60.4385 | 63.3224 | -60.228 | -60.5804 | -0.036621 | -0.045776 | 63.2126 | -60.3424 | 63.4232 | -60.3378 | -60.4202 | -60.2966 | -0.16479 | -0.082397 | 0.032044 | 0.045777 | 60.2371 | -0.3067 | 60.4019 | -0.14191 | -0.068664 | -0.07782 | 0.13275 | -0.064087 | -0.022888 | -0.14648 | 0.045776 | -0.07782 | 0.21057 | 123.761 | 0.004577 | 123.7656 | 123.6465 | 123.555 | 123.4818 | 123.4863 | -123.7289 | -123.6328 | 123.5962 | 123.6969 | 60.2051 | 60.228
182.4844 | 123.7885 | -60.2875 | 63.2767 | 0.094845 | 0.0039235 | 0.071675 | 0.065144 | -0.0015339 | 0.0045688 | -0.0092424 | 0.16115 | 0.00015838 | 0.088115 | 0.10571 | -0.010427 | 0.011707 | 0.010025 | 0.068665 | 63.2538 | -60.3836 | 63.295 | -60.2737 | -60.6079 | -0.032043 | 0.10071 | 63.2309 | -60.3012 | 63.5056 | -60.347 | -60.2966 | -60.1822 | -0.09613 | -0.022888 | 0.018311 | 0.013733 | 60.2554 | -0.32043 | 60.3516 | -0.2243 | -0.013732 | -0.045776 | 0.22888 | -0.059509 | 0.10529 | -0.009155 | 0.11902 | 0.004577 | 0.10986 | 123.6786 | -0.045777 | 123.8068 | 123.6374 | 123.5321 | 123.5413 | 123.5184 | -123.6603 | -123.5779 | 123.5825 | 123.793 | 60.3561 | 60.3882
183.4844 | 123.7701 | -60.3012 | 63.2492 | 0.079586 | 0.0017875 | 0.053517 | 0.065144 | -0.0079419 | -0.015725 | -0.0092424 | 0.16115 | -0.0030456 | 0.059276 | 0.056579 | 0.0055948 | -4.2099e-05 | 0.00041246 | -0.059509 | 63.208 | -60.434 | 63.295 | -60.2463 | -60.5804 | -0.064087 | -0.027466 | 63.2309 | -60.3378 | 63.4232 | -60.3378 | -60.4385 | -60.3058 | -0.13275 | -0.041199 | 0.045776 | 0.054931 | 60.2371 | -0.27924 | 60.3699 | -0.14648 | -0.036622 | -0.018311 | 0.17395 | -0.036622 | -0.004578 | -0.13733 | 0.032044 | -0.10071 | 0.18768 | 123.7289 | 0 | 123.761 | 123.642 | 123.5687 | 123.5092 | 123.5321 | -123.6832 | -123.587 | 123.5962 | 123.7244 | 60.2417 | 60.2737
184.4844 | 123.761 | -60.3104 | 63.2675 | 0.018551 | -0.0067575 | 0.060994 | 0.069417 | 0.011284 | -0.017862 | 0.0067786 | 0.069594 | 0.0033634 | 0.076366 | 0.059784 | 0.0013218 | 0.0063669 | -0.01561 | -0.064087 | 63.1897 | -60.4568 | 63.3545 | -60.2234 | -60.5621 | -0.036621 | -0.041199 | 63.2355 | -60.347 | 63.3957 | -60.3149 | -60.4477 | -60.2966 | -0.14648 | -0.07782 | 0.086975 | 0.086975 | 60.2737 | -0.25177 | 60.4202 | -0.10529 | -0.036621 | -0.032043 | 0.12817 | -0.004577 | 0.013733 | -0.13733 | 0.050354 | -0.10071 | 0.23346 | 123.8113 | 0.032044 | 123.7427 | 123.6465 | 123.5825 | 123.5001 | 123.5458 | -123.7244 | -123.6145 | 123.6649 | 123.7061 | 60.2463 | 60.2692
185.4844 | 123.7747 | -60.2921 | 63.2767 | 0.049069 | -0.00034947 | 0.05779 | 0.064076 | -0.0036699 | 0.00029581 | -0.00069841 | 0.084853 | 0.0044314 | 0.065685 | 0.066192 | -0.00081422 | 0.0020939 | 0.0078895 | -0.068665 | 63.1851 | -60.4385 | 63.327 | -60.2142 | -60.5804 | -0.036621 | -0.050354 | 63.2263 | -60.3607 | 63.414 | -60.3607 | -60.434 | -60.2829 | -0.14648 | -0.091552 | 0.050354 | 0.07782 | 60.2554 | -0.28839 | 60.4019 | -0.14191 | -0.068665 | -0.050354 | 0.13733 | -0.068665 | 0.009155 | -0.14191 | 0.07782 | -0.073242 | 0.22431 | 123.7656 | 0 | 123.7747 | 123.6237 | 123.587 | 123.4772 | 123.5184 | -123.7152 | -123.6374 | 123.6191 | 123.7061 | 60.2234 | 60.2417
186.4844 | 123.7976 | -60.2783 | 63.2721 | 0.094845 | 0.0028555 | 0.067403 | 0.076894 | -0.0090099 | 0.0077728 | -0.011379 | 0.023818 | 0.0033634 | 0.06248 | 0.059784 | -0.0072232 | 0.0063669 | -0.0070645 | -0.032043 | 63.176 | -60.3928 | 63.2858 | -60.2829 | -60.6125 | -0.07782 | 0.013733 | 63.2217 | -60.3424 | 63.4277 | -60.3333 | -60.4202 | -60.2692 | -0.11444 | -0.096131 | 0.013733 | -0.004578 | 60.2005 | -0.33417 | 60.3149 | -0.21973 | -0.064087 | -0.050354 | 0.15564 | -0.054932 | 0.009155 | -0.14191 | 0.073242 | -0.07782 | 0.10986 | 123.6786 | 0.009155 | 123.7701 | 123.5687 | 123.5641 | 123.4543 | 123.5001 | -123.6649 | -123.6145 | 123.5641 | 123.7061 | 60.2463 | 60.2921
187.4844 | 123.8388 | -60.2829 | 63.2721 | -0.027225 | 0.010333 | 0.060994 | 0.06728 | -0.0058059 | 0.00029581 | 0.0046426 | 0.22218 | 0.00015838 | 0.071025 | 0.062988 | 0.0013218 | -0.0011101 | -0.011337 | -0.050354 | 63.2355 | -60.4385 | 63.3408 | -60.2188 | -60.5759 | -0.050354 | 0.009155 | 63.2217 | -60.3516 | 63.4369 | -60.2875 | -60.3561 | -60.2463 | -0.15564 | -0.036621 | 0.068664 | 0.064087 | 60.2325 | -0.29297 | 60.3882 | -0.13733 | -0.068664 | -0.050354 | 0.16479 | -0.004578 | 0.036621 | -0.073242 | 0.10529 | -0.004578 | 0.21973 | 123.7793 | 0.064086 | 123.7885 | 123.674 | 123.5733 | 123.5184 | 123.5046 | -123.7106 | -123.6237 | 123.6237 | 123.7198 | 60.2325 | 60.2921
188.4844 | 123.793 | -60.2966 | 63.2538 | 0.049069 | 0.0060595 | 0.06313 | 0.066212 | 0.0006031 | -0.00077219 | 0.013188 | -0.021958 | -0.00090962 | 0.060344 | 0.051239 | -0.010427 | 0.011707 | -0.022018 | -0.064087 | 63.1897 | -60.4385 | 63.3133 | -60.2554 | -60.5942 | -0.064087 | -0.041199 | 63.2538 | -60.3516 | 63.4415 | -60.3333 | -60.4477 | -60.3058 | -0.14191 | -0.064087 | 0.059509 | 0.041199 | 60.2325 | -0.29755 | 60.3745 | -0.15564 | -0.054931 | 0 | 0.18768 | -0.036621 | -0.009155 | -0.15106 | 0.045776 | -0.096131 | 0.18311 | 123.7518 | 0.01831 | 123.793 | 123.6282 | 123.6053 | 123.4863 | 123.5504 | -123.6923 | -123.6053 | 123.6099 | 123.7381 | 60.2325 | 60.2554
189.4844 | 123.7747 | -60.2966 | 63.2675 | 0.0032924 | 0.011401 | 0.062062 | 0.071553 | -0.0090099 | -0.012521 | 0.00037059 | -0.037217 | -0.0019776 | 0.058208 | 0.042694 | -0.0029502 | 0.013843 | 0.0014805 | -0.064087 | 63.2034 | -60.4248 | 63.2904 | -60.2783 | -60.5942 | -0.091553 | -0.009155 | 63.2355 | -60.3424 | 63.4186 | -60.3333 | -60.4202 | -60.2692 | -0.12817 | -0.064087 | 0.022888 | 0.018311 | 60.2051 | -0.29755 | 60.3333 | -0.16937 | -0.045776 | -0.032043 | 0.15106 | -0.036621 | 0.027466 | -0.1236 | 0.073242 | -0.07782 | 0.14648 | 123.7152 | 0.009155 | 123.761 | 123.6282 | 123.5779 | 123.5001 | 123.5321 | -123.6923 | -123.6099 | 123.587 | 123.7152 | 60.2325 | 60.2875
190.4844 | 123.7839 | -60.2829 | 63.2538 | 0.15588 | 0.0017875 | 0.055654 | 0.069417 | 0.014488 | 0.0099088 | 0.023869 | -0.082994 | 0.0022944 | 0.067821 | 0.058716 | 0.0023898 | 0.0052979 | -0.0049285 | -0.050354 | 63.2126 | -60.4156 | 63.2629 | -60.2966 | -60.6216 | -0.082397 | -0.009155 | 63.2126 | -60.3516 | 63.4415 | -60.3516 | -60.4202 | -60.2921 | -0.13275 | -0.041199 | 0.009155 | -0.013733 | 60.2005 | -0.33874 | 60.3333 | -0.20599 | -0.068664 | -0.041199 | 0.18768 | -0.068664 | -0.009155 | -0.13733 | 0.059509 | -0.068665 | 0.11902 | 123.6786 | 0 | 123.793 | 123.6282 | 123.5641 | 123.4955 | 123.4955 | -123.6694 | -123.6053 | 123.5458 | 123.7244 | 60.2325 | 60.2737
191.4844 | 123.7656 | -60.2966 | 63.2492 | 0.018551 | 0.0060595 | 0.062062 | 0.069417 | 0.0038071 | 0.00029581 | -0.013515 | 0.084853 | -0.00090962 | 0.071025 | 0.052307 | -0.010427 | -0.0043151 | 0.0014805 | -0.068665 | 63.2126 | -60.4294 | 63.3224 | -60.2234 | -60.5804 | -0.054932 | -0.045776 | 63.2309 | -60.3561 | 63.4048 | -60.3378 | -60.4431 | -60.2966 | -0.13275 | -0.036622 | 0.073242 | 0.073242 | 60.2417 | -0.28381 | 60.3744 | -0.15106 | -0.059509 | -0.018311 | 0.15564 | -0.041199 | 0 | -0.14648 | 0.059509 | -0.086975 | 0.20599 | 123.7518 | 0.01831 | 123.761 | 123.642 | 123.587 | 123.5092 | 123.5275 | -123.6786 | -123.6053 | 123.6191 | 123.7015 | 60.228 | 60.2509
192.4844 | 123.8663 | -60.26 | 63.2721 | 0.094845 | 0.012469 | 0.060994 | 0.072621 | 0.0016711 | -0.012521 | -0.0092424 | 0.13063 | -0.00090962 | 0.083843 | 0.049103 | -0.0040182 | -4.2099e-05 | 0.0036165 | 0.036621 | 63.2355 | -60.3973 | 63.295 | -60.2692 | -60.585 | -0.082397 | 0.14191 | 63.2538 | -60.347 | 63.5239 | -60.2005 | -60.347 | -60.228 | -0.13733 | -0.036621 | 0.022888 | -0.009155 | 60.1776 | -0.32501 | 60.3149 | -0.18768 | -0.086975 | -0.018311 | 0.25177 | 0.05951 | 0.032044 | -0.086975 | 0.11902 | 0 | 0.12817 | 123.6923 | 0.14648 | 123.8708 | 123.6328 | 123.6008 | 123.4955 | 123.5138 | -123.6694 | -123.6191 | 123.555 | 123.7839 | 60.2966 | 60.4019
193.4844 | 123.7839 | -60.2783 | 63.2309 | -0.042484 | 0.0049915 | 0.071675 | 0.06728 | -0.010078 | 0.0024328 | -0.0039024 | -0.0066996 | -0.0019776 | 0.06248 | 0.085418 | -0.0072232 | 0.0074349 | -0.0017235 | -0.059509 | 63.1805 | -60.434 | 63.2538 | -60.2966 | -60.6125 | -0.059509 | 0.013733 | 63.2309 | -60.3424 | 63.446 | -60.3012 | -60.4156 | -60.2554 | -0.15564 | -0.050354 | 0.022888 | -0.018311 | 60.2188 | -0.33417 | 60.3745 | -0.17853 | -0.064087 | 0 | 0.21515 | -0.022888 | 0.022888 | -0.13733 | 0.086975 | -0.073242 | 0.13733 | 123.6877 | 0.041199 | 123.7885 | 123.6145 | 123.5733 | 123.4589 | 123.5092 | -123.6649 | -123.5733 | 123.5321 | 123.7244 | 60.2188 | 60.2921
194.4844 | 123.7473 | -60.2921 | 63.2584 | 0.094845 | 0.0092645 | 0.067403 | 0.065144 | 0.015556 | 0.0067048 | -0.0039024 | -0.0066996 | -0.0041136 | 0.066753 | 0.067261 | -0.00081422 | -4.2099e-05 | 0.0014805 | -0.068665 | 63.1851 | -60.4385 | 63.3133 | -60.2646 | -60.5988 | -0.059509 | -0.027466 | 63.2401 | -60.3561 | 63.414 | -60.3424 | -60.434 | -60.2783 | -0.14648 | -0.073242 | 0.054931 | 0.027466 | 60.2325 | -0.3067 | 60.379 | -0.16022 | -0.064087 | -0.018311 | 0.15564 | -0.050354 | 0.013733 | -0.14191 | 0.07782 | -0.07782 | 0.17395 | 123.7518 | 0.013733 | 123.7701 | 123.6237 | 123.5962 | 123.4772 | 123.5321 | -123.6969 | -123.6145 | 123.6053 | 123.7061 | 60.2234 | 60.2646
195.4844 | 123.7701 | -60.2783 | 63.2629 | 0.094845 | 0.011401 | 0.056722 | 0.069417 | 0.017693 | 0.0045688 | -0.0071064 | 0.023818 | 0.0065674 | 0.081706 | 0.085418 | -0.0029502 | -0.0011101 | 0.00041246 | -0.045776 | 63.1897 | -60.4248 | 63.2858 | -60.2692 | -60.585 | -0.068665 | -0.022888 | 63.2217 | -60.347 | 63.4277 | -60.3333 | -60.4156 | -60.2875 | -0.14648 | -0.073242 | 0.022889 | 0.009155 | 60.2097 | -0.3067 | 60.3561 | -0.16022 | -0.068665 | -0.041198 | 0.16479 | -0.054932 | -0.009156 | -0.13733 | 0.059509 | -0.068664 | 0.15564 | 123.7106 | 0.013733 | 123.7747 | 123.6145 | 123.5687 | 123.468 | 123.5001 | -123.6877 | -123.6099 | 123.5641 | 123.7061 | 60.2325 | 60.2554
196.5 | 123.6923 | -60.2966 | 63.2996 | 0.064327 | 0.0039235 | 0.054585 | 0.065144 | 0.0080791 | -0.0029082 | -0.0071064 | 0.039077 | 0.0044314 | 0.083843 | 0.074737 | -0.0093592 | -0.0021781 | 0.011093 | 0.027466 | 63.2858 | -60.4431 | 63.3499 | -60.2051 | -60.4156 | 0.041199 | -0.073242 | 63.3041 | -60.3287 | 63.3545 | -60.3882 | -60.4843 | -60.3287 | -0.14648 | -0.013733 | 0.050354 | 0.091553 | 60.3378 | -0.11902 | 60.4843 | 0.027466 | -0.032043 | 0.004577 | 0.054931 | -0.091553 | -0.032043 | -0.18768 | 0 | -0.15564 | 0.23804 | 123.793 | -0.05951 | 123.6832 | 123.7289 | 123.6328 | 123.5825 | 123.6008 | -123.7427 | -123.6282 | 123.6465 | 123.6511 | 60.3241 | 60.2234
198.1094 | 123.8709 | -60.2783 | 63.2584 | 0.094845 | 0.00071953 | 0.052449 | 0.069417 | -0.0004649 | -0.0029082 | -0.010311 | 0.32899 | -0.0019776 | 0.064617 | 0.058716 | -0.0040182 | -0.0021781 | -0.0049285 | 0.032043 | 63.2034 | -60.4202 | 63.2812 | -60.3012 | -60.6033 | -0.050354 | 0.10986 | 63.2263 | -60.3012 | 63.501 | -60.1868 | -60.3058 | -60.2142 | -0.14191 | -0.054932 | 0.022888 | -0.022888 | 60.228 | -0.32501 | 60.3699 | -0.18311 | -0.022888 | -0.032044 | 0.24262 | 0.091552 | 0.064087 | -0.027466 | 0.086975 | -0.004578 | 0.11902 | 123.7015 | 0.11444 | 123.8022 | 123.6237 | 123.5275 | 123.4818 | 123.5046 | -123.6786 | -123.5596 | 123.5596 | 123.7793 | 60.3104 | 60.3882
199.1719 | 123.7152 | -60.2783 | 63.3087 | 0.14062 | 0.0071275 | 0.072743 | 0.070485 | -0.0036699 | 0.00029581 | 0.0078466 | -0.1898 | 0.0012264 | 0.063548 | 0.08435 | -0.0072232 | 0.011707 | 0.0036165 | -0.018311 | 63.2584 | -60.466 | 63.4003 | -60.1685 | -60.4843 | 0.018311 | -0.036621 | 63.2584 | -60.3745 | 63.3957 | -60.3516 | -60.4935 | -60.3241 | -0.18768 | -0.050354 | 0.091553 | 0.10986 | 60.2966 | -0.20599 | 60.4843 | -0.018311 | -0.096131 | -0.050354 | 0.086975 | -0.073242 | -0.045777 | -0.21515 | 0.050354 | -0.11902 | 0.29755 | 123.8663 | 0.022889 | 123.7701 | 123.7244 | 123.6328 | 123.5367 | 123.5367 | -123.7747 | -123.6832 | 123.6786 | 123.674 | 60.26 | 60.2417
200.2344 | 123.8342 | -60.2371 | 63.2675 | 0.14062 | -0.01103 | 0.050313 | 0.06194 | 0.016624 | -0.012521 | 0.0057106 | 0.20692 | -0.0051816 | 0.069957 | 0.045898 | -0.0072232 | 0.0031619 | -0.014542 | 0.027466 | 63.2309 | -60.4065 | 63.3133 | -60.2966 | -60.6308 | -0.064087 | 0.14648 | 63.2172 | -60.3195 | 63.4964 | -60.2371 | -60.3378 | -60.2051 | -0.16937 | -0.036621 | 0.045776 | -0.059509 | 60.173 | -0.39368 | 60.3424 | -0.2243 | -0.082397 | -0.050354 | 0.22888 | 0 | 0.032044 | -0.10071 | 0.11444 | -0.018311 | 0.10986 | 123.7198 | 0.082397 | 123.8159 | 123.6374 | 123.5367 | 123.468 | 123.4543 | -123.674 | -123.587 | 123.5504 | 123.7335 | 60.2646 | 60.3836
201.9219 | 123.7701 | -60.2829 | 63.2401 | 0.079586 | -0.0014175 | 0.062062 | 0.068349 | -0.0015339 | 0.00029581 | 0.0046426 | -0.11351 | 0.0065674 | 0.071025 | 0.048034 | -0.0061552 | -0.0011101 | 0.0014805 | -0.10529 | 63.2172 | -60.466 | 63.3591 | -60.1913 | -60.5392 | -0.027466 | -0.07782 | 63.2217 | -60.347 | 63.4277 | -60.3195 | -60.4111 | -60.2509 | -0.1831 | -0.022888 | 0.11902 | 0.091553 | 60.2554 | -0.25635 | 60.4385 | -0.073243 | -0.064087 | -0.01831 | 0.18768 | -0.036621 | 0.032044 | -0.12817 | 0.096131 | -0.064087 | 0.27466 | 123.8251 | 0.027466 | 123.7747 | 123.6832 | 123.5687 | 123.5001 | 123.5046 | -123.7061 | -123.587 | 123.642 | 123.7106 | 60.1776 | 60.2051
203.0625 | 123.8846 | -60.2234 | 63.3591 | 0.23217 | -0.0014175 | 0.053517 | 0.06728 | 0.011284 | -0.013589 | -0.0028344 | 0.26796 | 0.0012264 | 0.072093 | 0.033081 | 0.0023898 | 0.0052979 | 0.0014805 | 0.068665 | 63.2446 | -60.3699 | 63.295 | -60.2966 | -60.6216 | -0.041199 | 0.10986 | 63.2263 | -60.3333 | 63.4918 | -60.2188 | -60.3333 | -60.3561 | -0.14648 | -0.11444 | -0.064087 | -0.073242 | 60.1822 | -0.39825 | 60.3287 | -0.25177 | -0.10986 | -0.13275 | 0.13275 | 0.004578 | -0.13275 | -0.10986 | -0.022888 | 0 | 0.073242 | 123.6649 | 0.11444 | 123.8251 | 123.6145 | 123.5596 | 123.468 | 123.4497 | -123.7289 | -123.6923 | 123.5184 | 123.7152 | 60.2921 | 60.3333
203.6719 | 123.848 | -60.2829 | 63.2675 | 0.094845 | -0.0088935 | 0.066335 | 0.064076 | -0.0047379 | -0.0050442 | -0.00069841 | 0.14589 | 0.0044314 | 0.063548 | 0.037353 | 0.012003 | 0.0031619 | 0.0046845 | -0.07782 | 63.208 | -60.4431 | 63.3316 | -60.2234 | -60.5621 | -0.054932 | -0.068665 | 63.2126 | -60.3333 | 63.3957 | -60.3241 | -60.4431 | -60.2829 | -0.16022 | -0.059509 | 0.064087 | 0.059509 | 60.228 | -0.27924 | 60.3882 | -0.11902 | -0.050354 | -0.054932 | 0.12817 | -0.041199 | 0 | -0.16022 | 0.050354 | -0.10986 | 0.21973 | 123.7747 | 0.009155 | 123.7289 | 123.6511 | 123.5458 | 123.4909 | 123.4955 | -123.7106 | -123.6008 | 123.6145 | 123.6786 | 60.2051 | 60.2142
207.7969 | 123.7518 | -60.3012 | 63.295 | 0.21692 | 0.015673 | 0.054585 | 0.073689 | 0.016624 | -0.0029082 | 0.0046426 | -0.052476 | -0.0030456 | 0.078502 | 0.065124 | -0.0082912 | 0.0031619 | -0.013474 | 0.027466 | 63.2858 | -60.4111 | 63.3865 | -60.1776 | -60.5072 | 0.041199 | -0.004578 | 63.2584 | -60.3516 | 63.4094 | -60.3241 | -60.4523 | -60.2737 | -0.10986 | -0.009155 | 0.091553 | 0.1236 | 60.3424 | -0.20599 | 60.4523 | -0.09613 | -0.050354 | -0.036621 | 0.11444 | -0.022889 | 0.027465 | -0.15106 | 0.077819 | -0.10071 | 0.23346 | 123.7976 | 0.027465 | 123.761 | 123.6969 | 123.6099 | 123.587 | 123.5596 | -123.7061 | -123.6465 | 123.6877 | 123.7106 | 60.3287 | 60.2966
208.7812 | 123.7793 | -60.2783 | 63.2355 | 0.03381 | 0.0071275 | 0.066335 | 0.069417 | 0.0070111 | 0.014182 | -0.00069841 | -0.037217 | -0.0041136 | 0.068889 | 0.052307 | 0.0034578 | 0.020252 | -0.016678 | -0.082397 | 63.1989 | -60.4477 | 63.2767 | -60.2829 | -60.5988 | -0.09613 | -0.004578 | 63.2034 | -60.3561 | 63.4277 | -60.2966 | -60.4065 | -60.2463 | -0.16937 | -0.036621 | 0.041198 | -0.004578 | 60.1822 | -0.32043 | 60.3516 | -0.15106 | -0.07782 | -0.032044 | 0.19226 | -0.018311 | 0.032043 | -0.12817 | 0.10986 | -0.050354 | 0.16479 | 123.7244 | 0.059509 | 123.7839 | 123.6465 | 123.5596 | 123.4772 | 123.4818 | -123.6832 | -123.5916 | 123.555 | 123.7061 | 60.1959 | 60.2737
209.4844 | 123.7747 | -60.2829 | 63.2904 | 0.049069 | 0.00071953 | 0.066335 | 0.071553 | 0.0048751 | -0.00077219 | 0.0046426 | 0.19167 | -0.0073186 | 0.080638 | 0.032013 | 0.0013218 | 0.0052979 | 0.0036165 | -0.059509 | 63.1897 | -60.4156 | 63.3133 | -60.2463 | -60.5713 | -0.045776 | -0.036621 | 63.2355 | -60.3378 | 63.3865 | -60.3195 | -60.4385 | -60.2509 | -0.13275 | -0.10071 | 0.022888 | 0.036621 | 60.2371 | -0.28839 | 60.3699 | -0.15564 | -0.054932 | -0.054931 | 0.096131 | -0.036621 | 0.032044 | -0.15564 | 0.086976 | -0.10071 | 0.16937 | 123.7289 | 0.018311 | 123.7244 | 123.6053 | 123.5733 | 123.4726 | 123.5184 | -123.7061 | -123.6282 | 123.5962 | 123.6694 | 60.2234 | 60.2463
210.4844 | 123.8068 | -60.2509 | 63.2858 | 0.21692 | -0.0014175 | 0.056722 | 0.066212 | -0.012215 | -0.01893 | -0.0028344 | 0.22218 | 0.012976 | 0.056072 | 0.064056 | -0.0040182 | -0.0064511 | -0.0081325 | 0.050354 | 63.2126 | -60.3836 | 63.2904 | -60.2692 | -60.585 | -0.036621 | 0.41657 | 63.3087 | -60.2783 | 63.5284 | -60.2875 | -60.3607 | -60.2142 | -0.13275 | -0.073243 | 0.004577 | -0.018311 | 60.2142 | -0.33417 | 60.347 | -0.20142 | -0.027466 | 0.022888 | 0.24261 | -0.036622 | 0.036621 | -0.10986 | 0.064087 | -0.082398 | 0.11444 | 123.674 | -0.009156 | 123.8068 | 123.5962 | 123.587 | 123.4634 | 123.5596 | -123.6694 | -123.5641 | 123.5413 | 123.7793 | 60.3012 | 60.6674
211.4844 | 123.7701 | -60.2966 | 63.2629 | 0.094845 | 0.0028555 | 0.058858 | 0.069417 | 0.0016711 | 0.0045688 | -0.011379 | 0.039077 | 0.0022944 | 0.069957 | 0.071533 | -0.010427 | 0.011707 | -0.00065554 | -0.059509 | 63.2034 | -60.4477 | 63.3041 | -60.2646 | -60.5896 | -0.059509 | -0.032043 | 63.2401 | -60.3516 | 63.4277 | -60.3149 | -60.4156 | -60.2646 | -0.15106 | -0.059509 | 0.041199 | 0.032044 | 60.2371 | -0.29297 | 60.3882 | -0.14191 | -0.054931 | -0.022888 | 0.16479 | -0.01831 | 0.032044 | -0.11902 | 0.086975 | -0.064087 | 0.18311 | 123.7518 | 0.036621 | 123.7793 | 123.6511 | 123.5916 | 123.5001 | 123.5367 | -123.7106 | -123.6145 | 123.6008 | 123.7244 | 60.2371 | 60.2646
212.4844 | 123.6832 | -60.2737 | 63.3453 | 0.14062 | -0.0024855 | 0.055654 | 0.069417 | -0.028236 | -0.0071802 | -0.00069841 | 0.11537 | 0.014044 | 0.068889 | 0.068329 | -0.0050872 | 0.017048 | 0.01857 | -0.004578 | 63.2996 | -60.4019 | 63.4552 | -60.0769 | -60.434 | 0.09613 | 0.054932 | 63.3545 | -60.3058 | 63.3499 | -60.3104 | -60.498 | -60.347 | -0.12817 | -0.045776 | 0.10986 | 0.19684 | 60.3699 | -0.16022 | 60.498 | -0.032043 | -0.032043 | 0.009155 | 0.004578 | -0.036621 | -0.073242 | -0.2243 | -0.041199 | -0.19226 | 0.32501 | 123.8571 | -0.004578 | 123.6557 | 123.7015 | 123.6603 | 123.5733 | 123.6282 | -123.7473 | -123.6511 | 123.7289 | 123.6237 | 60.2692 | 60.3287
213.4844 | 123.7793 | -60.2966 | 63.2629 | -0.057743 | -0.0014175 | 0.067403 | 0.072621 | 0.0080791 | -0.013589 | -0.0060384 | 0.084853 | 0.0054994 | 0.064617 | 0.012787 | -0.0072232 | -4.2099e-05 | -0.0017235 | -0.054932 | 63.208 | -60.4385 | 63.2584 | -60.2921 | -60.6033 | -0.07782 | 0 | 63.2263 | -60.3149 | 63.4186 | -60.3104 | -60.4202 | -60.2692 | -0.14191 | -0.054931 | -0.004577 | 0.004578 | 60.2188 | -0.3067 | 60.3607 | -0.16479 | -0.01831 | -0.036621 | 0.15564 | -0.013733 | 0.027466 | -0.1236 | 0.045776 | -0.10529 | 0.14648 | 123.6969 | 0.004577 | 123.7335 | 123.6465 | 123.5413 | 123.5046 | 123.5229 | -123.7015 | -123.5779 | 123.555 | 123.7152 | 60.2417 | 60.2966
214.4844 | 123.7793 | -60.2829 | 63.2355 | 0.049069 | 0.0060595 | 0.060994 | 0.070485 | -0.0004649 | 0.019522 | -0.0039024 | 0.17641 | 0.00015838 | 0.071025 | 0.068329 | -0.011495 | 0.013843 | -0.012405 | -0.050354 | 63.2309 | -60.3973 | 63.2584 | -60.2783 | -60.6079 | -0.086975 | 0.013733 | 63.2355 | -60.3241 | 63.4415 | -60.3058 | -60.434 | -60.2646 | -0.11444 | -0.004578 | 0.022888 | 0.004578 | 60.1959 | -0.32501 | 60.3104 | -0.21057 | -0.041199 | 0 | 0.20599 | -0.022888 | 0.018311 | -0.15106 | 0.05951 | -0.10986 | 0.11902 | 123.6557 | 0.018311 | 123.7656 | 123.6282 | 123.5596 | 123.5138 | 123.5184 | -123.6328 | -123.5596 | 123.5413 | 123.7244 | 60.2325 | 60.2966
215.4844 | 123.8617 | -60.2463 | 63.2812 | 0.049069 | 0.0060595 | 0.04604 | 0.069417 | 0.0091481 | -0.0050442 | 0.00037059 | 0.23744 | -0.0030456 | 0.07957 | 0.056579 | -0.0029502 | -0.0075191 | -0.0059965 | 0.013733 | 63.2584 | -60.3882 | 63.2767 | -60.2921 | -60.5667 | -0.068665 | 0.10071 | 63.2401 | -60.3012 | 63.5056 | -60.2051 | -60.3104 | -60.1959 | -0.14191 | -0.022888 | -0.004578 | -0.045776 | 60.1776 | -0.32043 | 60.3195 | -0.17853 | -0.054931 | -0.041199 | 0.2243 | 0.041199 | 0.050354 | -0.064087 | 0.10529 | -0.009156 | 0.096131 | 123.6649 | 0.09613 | 123.8068 | 123.6465 | 123.5413 | 123.5046 | 123.4863 | -123.6694 | -123.5825 | 123.5229 | 123.7518 | 60.26 | 60.347
216.4844 | 123.7793 | -60.2737 | 63.295 | 0.1101 | 0.0028555 | 0.056722 | 0.054463 | 0.0016711 | -0.0018402 | -0.0092424 | 0.0085594 | 0.0076354 | 0.077434 | 0.024536 | -0.00081422 | 0.0074349 | 0.0014805 | -0.07782 | 63.2217 | -60.4202 | 63.3224 | -60.2325 | -60.5576 | -0.045776 | -0.032043 | 63.2446 | -60.3287 | 63.4186 | -60.3333 | -60.4156 | -60.2783 | -0.14648 | -0.073242 | 0.027466 | 0.041199 | 60.228 | -0.28381 | 60.3745 | -0.13733 | -0.054931 | -0.050354 | 0.1236 | -0.059509 | -0.004577 | -0.14191 | 0.050354 | -0.086975 | 0.18768 | 123.7427 | -0.004578 | 123.7473 | 123.642 | 123.5733 | 123.4955 | 123.5184 | -123.7152 | -123.6237 | 123.5962 | 123.6923 | 60.1959 | 60.2417
217.4844 | 123.8251 | -60.2509 | 63.2904 | 0.12536 | 0.0060595 | 0.05779 | 0.072621 | -0.02076 | 0.0035008 | -0.0092424 | 0.11537 | 0.010839 | 0.066753 | 0.075805 | -0.0040182 | 0.0052979 | -0.0092005 | 0.050354 | 63.2263 | -60.3882 | 63.2904 | -60.2692 | -60.6674 | 0.064087 | 0.004578 | 63.2401 | -60.3287 | 63.4598 | -60.1822 | -60.347 | -60.2051 | -0.13733 | -0.064087 | 0 | -0.018311 | 60.3149 | -0.41657 | 60.4523 | -0.27923 | -0.07782 | -0.050354 | 0.16937 | 0.068664 | 0.045776 | -0.096131 | 0.1236 | -0.018311 | 0.11902 | 123.6786 | 0.14648 | 123.7885 | 123.6145 | 123.5687 | 123.4772 | 123.4909 | -123.6786 | -123.6191 | 123.5413 | 123.7106 | 60.3012 | 60.2554
218.4844 | 123.7289 | -60.2966 | 63.3133 | 0.049069 | 0.0060595 | 0.054585 | 0.072621 | -0.0079419 | -0.0018402 | -0.014583 | 0.19167 | -0.00090962 | 0.066753 | 0.075805 | -0.0082912 | 0.0031619 | -0.0049285 | -0.073242 | 63.2217 | -60.434 | 63.3408 | -60.2051 | -60.5392 | -0.045776 | -0.064087 | 63.2217 | -60.3561 | 63.3911 | -60.2188 | -60.3516 | -60.2829 | -0.13733 | -0.091552 | 0.027466 | 0.091553 | 60.2509 | -0.24262 | 60.3882 | -0.10529 | -0.059509 | -0.091552 | 0.07782 | 0.07782 | 0.013733 | -0.054931 | 0.073242 | 0.004578 | 0.22888 | 123.7747 | 0.13733 | 123.7473 | 123.6557 | 123.5779 | 123.5184 | 123.5184 | -123.7473 | -123.6694 | 123.6374 | 123.6877 | 60.2234 | 60.2325
219.4844 | 123.7473 | -60.2737 | 63.2721 | -0.011967 | 0.0071275 | 0.055654 | 0.058736 | -0.013283 | -0.014657 | 0.0067786 | 0.054336 | -0.00090962 | 0.066753 | 0.095032 | -0.0147 | 0.0010259 | -0.0027915 | -0.07782 | 63.2126 | -60.4294 | 63.3362 | -60.2005 | -60.553 | -0.032043 | -0.054932 | 63.2401 | -60.3241 | 63.4232 | -60.3195 | -60.4065 | -60.2737 | -0.15564 | -0.05951 | 0.064087 | 0.073243 | 60.2417 | -0.27924 | 60.3973 | -0.1236 | -0.050354 | -0.032044 | 0.15106 | -0.045776 | 0 | -0.13275 | 0.050354 | -0.082397 | 0.22888 | 123.7656 | 0.004578 | 123.7473 | 123.642 | 123.5641 | 123.4863 | 123.5138 | -123.7015 | -123.5962 | 123.6099 | 123.6969 | 60.1959 | 60.2188
220.4844 | 123.8205 | -60.2463 | 63.2629 | 0.1864 | 0.00071953 | 0.056722 | 0.072621 | -0.0058059 | 0.012046 | 0.0025066 | 0.20692 | 0.0076354 | 0.067821 | 0.090759 | -0.018972 | 0.010639 | -0.012405 | -0.009155 | 63.2309 | -60.4019 | 63.3179 | -60.2142 | -60.5576 | -0.036621 | 0.045776 | 63.2538 | -60.3424 | 63.4872 | -60.2417 | -60.3516 | -60.2097 | -0.15564 | -0.032043 | 0.054932 | 0.032044 | 60.2097 | -0.31128 | 60.3653 | -0.15564 | -0.09613 | -0.009155 | 0.2243 | 0.004578 | 0.036621 | -0.10529 | 0.13275 | -0.009155 | 0.18768 | 123.7198 | 0.10071 | 123.8297 | 123.6328 | 123.5962 | 123.4772 | 123.5001 | -123.6649 | -123.6053 | 123.5641 | 123.7335 | 60.2371 | 60.2921
221.4844 | 123.8022 | -60.2875 | 63.2492 | 0.094845 | 0.0028555 | 0.05779 | 0.068349 | -0.0004649 | -0.010385 | 0.00037059 | 0.039077 | -0.0019776 | 0.059276 | 0.075805 | -0.0050872 | 0.0052979 | 0.016434 | -0.041199 | 63.1989 | -60.4294 | 63.2858 | -60.2921 | -60.6171 | -0.09613 | 0.004578 | 63.2126 | -60.3424 | 63.4598 | -60.3104 | -60.4111 | -60.2554 | -0.14191 | -0.050354 | 0.036621 | -0.004577 | 60.1913 | -0.32959 | 60.3333 | -0.18768 | -0.054931 | -0.036622 | 0.21057 | -0.022888 | 0.032044 | -0.1236 | 0.086975 | -0.068665 | 0.13733 | 123.7152 | 0.032043 | 123.8022 | 123.6282 | 123.555 | 123.4863 | 123.5001 | -123.6786 | -123.5916 | 123.5733 | 123.7473 | 60.2463 | 60.2921
222.4844 | 123.7244 | -60.2829 | 63.3499 | 0.30847 | -0.0067575 | 0.065267 | 0.06728 | 0.010216 | -0.011453 | 0.0014386 | -0.021958 | 0.0087034 | 0.072093 | 0.091827 | -0.0040182 | 0.010639 | -0.0070645 | -0.14191 | 63.2996 | -60.434 | 63.4369 | -60.1227 | -60.4156 | 0.12817 | -0.073242 | 63.3041 | -60.347 | 63.3682 | -60.347 | -60.466 | -60.3104 | -0.15106 | -0.050354 | 0.086975 | 0.16022 | 60.4111 | -0.13275 | 60.5621 | 0.018311 | -0.064087 | -0.045777 | 0.01831 | -0.064087 | -0.027466 | -0.1831 | 0.036621 | -0.11902 | 0.31128 | 123.8708 | 0 | 123.7152 | 123.7335 | 123.6511 | 123.5825 | 123.587 | -123.7839 | -123.6969 | 123.7198 | 123.6511 | 60.141 | 60.2097
223.4844 | 123.7701 | -60.2783 | 63.2858 | 0.049069 | -0.0088935 | 0.059926 | 0.070485 | -0.0015339 | -0.0082492 | -0.018856 | 0.14589 | 0.0054994 | 0.072093 | 0.066192 | -0.0061552 | 0.0074349 | -0.00065554 | -0.073242 | 63.1989 | -60.4156 | 63.3179 | -60.2417 | -60.5759 | -0.050354 | -0.045776 | 63.2355 | -60.3333 | 63.414 | -60.3241 | -60.4065 | -60.2646 | -0.13733 | -0.086975 | 0.032043 | 0.036621 | 60.228 | -0.29755 | 60.3653 | -0.16022 | -0.054932 | -0.050354 | 0.12817 | -0.045777 | 0.013733 | -0.12817 | 0.068665 | -0.073242 | 0.17395 | 123.7335 | 0.009155 | 123.7473 | 123.6145 | 123.5687 | 123.4772 | 123.5138 | -123.7015 | -123.6191 | 123.5962 | 123.6923 | 60.2051 | 60.2325
224.4844 | 123.7518 | -60.2875 | 63.2629 | 0.018551 | 0.0017875 | 0.065267 | 0.06194 | 0.014488 | -0.014657 | -0.00069841 | 0.13063 | 0.0033634 | 0.076366 | 0.048034 | -0.013631 | 0.012775 | -0.018814 | -0.059509 | 63.176 | -60.4065 | 63.2904 | -60.2646 | -60.5804 | -0.064087 | -0.045776 | 63.2401 | -60.3378 | 63.4277 | -60.3104 | -60.4294 | -60.2554 | -0.11902 | -0.086975 | 0.027466 | 0.022889 | 60.2234 | -0.29297 | 60.3424 | -0.17395 | -0.050354 | -0.022888 | 0.16479 | -0.022888 | 0.032044 | -0.14191 | 0.082398 | -0.091552 | 0.14191 | 123.6969 | 0.027466 | 123.7656 | 123.5825 | 123.5779 | 123.4634 | 123.5275 | -123.6694 | -123.6008 | 123.5779 | 123.7152 | 60.228 | 60.2417
225.4844 | 123.8113 | -60.2509 | 63.2812 | 0.1864 | 0.0049915 | 0.059926 | 0.070485 | 0.0070111 | -0.0082492 | -0.0092424 | 0.2527 | 0.0033634 | 0.073162 | 0.025604 | -0.0029502 | 0.0031619 | 0.0068215 | 0 | 63.2263 | -60.3973 | 63.3087 | -60.2188 | -60.5667 | -0.054932 | 0.050354 | 63.2584 | -60.3058 | 63.4918 | -60.2371 | -60.3424 | -60.2097 | -0.14649 | -0.054932 | 0.027466 | 0.032043 | 60.1959 | -0.31586 | 60.3424 | -0.16937 | -0.054932 | -0.022888 | 0.21057 | 0.013732 | 0.041198 | -0.091553 | 0.09613 | -0.036621 | 0.17853 | 123.7061 | 0.068664 | 123.7976 | 123.6237 | 123.5641 | 123.4772 | 123.5092 | -123.6786 | -123.587 | 123.5596 | 123.7427 | 60.2509 | 60.3012
226.4844 | 123.7793 | -60.2737 | 63.2858 | 0.12536 | 0.014605 | 0.060994 | 0.072621 | -0.028236 | 0.014182 | -0.012447 | 0.14589 | 0.0087034 | 0.077434 | 0.026672 | -0.010427 | 0.0085029 | -0.00065554 | -0.082397 | 63.2172 | -60.4294 | 63.3133 | -60.2097 | -60.5484 | -0.050354 | -0.068665 | 63.2492 | -60.3607 | 63.4232 | -60.3195 | -60.4156 | -60.2692 | -0.15564 | -0.068665 | 0.027465 | 0.064087 | 60.2234 | -0.27466 | 60.379 | -0.11902 | -0.086975 | -0.036621 | 0.13733 | -0.045776 | 0.004578 | -0.14191 | 0.091553 | -0.054931 | 0.21973 | 123.7427 | 0.041199 | 123.7839 | 123.6465 | 123.6099 | 123.4909 | 123.523 | -123.7152 | -123.6465 | 123.587 | 123.6969 | 60.1913 | 60.2051
227.4844 | 123.6923 | -60.2737 | 63.3133 | 0.12536 | -0.0014175 | 0.056722 | 0.073689 | 0.01342 | -0.0029082 | 0.0099836 | -0.0066996 | -0.00090962 | 0.077434 | 0.067261 | -0.0040182 | -0.0011101 | 0.0014805 | 0.054932 | 63.2584 | -60.379 | 63.3636 | -60.1822 | -60.5164 | 0.032043 | 0.022888 | 63.327 | -60.3241 | 63.4003 | -60.3149 | -60.4294 | -60.2783 | -0.10528 | -0.054931 | 0.050354 | 0.091553 | 60.3058 | -0.24261 | 60.4111 | -0.13733 | -0.050354 | 0.013733 | 0.086976 | -0.041198 | -0.004577 | -0.15564 | 0.045777 | -0.10528 | 0.19684 | 123.7427 | 0.009156 | 123.7244 | 123.6374 | 123.6511 | 123.5321 | 123.6008 | -123.6923 | -123.6374 | 123.6374 | 123.674 | 60.3287 | 60.2966
228.4844 | 123.7885 | -60.2692 | 63.2538 | 0.079586 | 0.0049915 | 0.056722 | 0.074757 | -0.0090099 | -0.012521 | -0.0081744 | 0.0085594 | 0.0012264 | 0.073162 | 0.065124 | -0.012563 | 0.0063669 | 0.0046845 | -0.050354 | 63.1989 | -60.4156 | 63.2767 | -60.2921 | -60.6216 | -0.09613 | -0.004578 | 63.2309 | -60.3424 | 63.4598 | -60.2875 | -60.3973 | -60.2142 | -0.14648 | -0.054931 | 0.022888 | -0.022888 | 60.173 | -0.35248 | 60.3195 | -0.20599 | -0.073242 | -0.022888 | 0.20599 | -0.018311 | 0.054932 | -0.12817 | 0.12817 | -0.054932 | 0.1236 | 123.6923 | 0.054931 | 123.8022 | 123.6145 | 123.5733 | 123.468 | 123.5001 | -123.6694 | -123.5962 | 123.5458 | 123.7289 | 60.2188 | 60.2646
229.4844 | 123.761 | -60.2692 | 63.2538 | 0.079586 | 0.00071953 | 0.071675 | 0.06728 | 0.0070111 | 0.010977 | -0.00069841 | 0.17641 | 0.0054994 | 0.060344 | 0.067261 | -0.0029502 | 0.0095709 | 0.0068215 | -0.082397 | 63.1989 | -60.4156 | 63.3087 | -60.2371 | -60.5621 | -0.050354 | -0.064087 | 63.2401 | -60.3241 | 63.4369 | -60.3195 | -60.4111 | -60.26 | -0.14648 | -0.054931 | 0.054932 | 0.032043 | 60.2188 | -0.29297 | 60.3653 | -0.14648 | -0.054932 | -0.013733 | 0.18311 | -0.050354 | 0.009155 | -0.14191 | 0.064087 | -0.086975 | 0.17853 | 123.7244 | 0.004578 | 123.761 | 123.6145 | 123.5641 | 123.468 | 123.5092 | -123.6694 | -123.5779 | 123.5779 | 123.7061 | 60.1868 | 60.2051
230.4844 | 123.8617 | -60.2463 | 63.2767 | 0.17114 | -0.0078255 | 0.064198 | 0.066212 | -0.0026019 | 0.00029581 | -0.0017664 | 0.34425 | 0.0012264 | 0.084911 | 0.045898 | 0.0013218 | 0.0020939 | 0.017502 | 0.013733 | 63.2446 | -60.3836 | 63.3179 | -60.2646 | -60.5896 | -0.059509 | 0.073242 | 63.2401 | -60.2921 | 63.5147 | -60.1639 | -60.3104 | -60.2142 | -0.13733 | -0.032043 | 0.041199 | -0.01831 | 60.1868 | -0.34332 | 60.3241 | -0.20599 | -0.045776 | -0.036621 | 0.23804 | 0.082398 | 0.032044 | -0.064087 | 0.07782 | -0.018311 | 0.11902 | 123.7015 | 0.12817 | 123.8068 | 123.6282 | 123.5321 | 123.4909 | 123.4863 | -123.6603 | -123.5687 | 123.5641 | 123.761 | 60.26 | 60.3195
231.4844 | 123.7656 | -60.2783 | 63.2767 | 0.094845 | -0.0024855 | 0.065267 | 0.071553 | -0.012215 | -0.0061122 | -0.0081744 | 0.13063 | 0.0087034 | 0.068889 | 0.053375 | -0.00081422 | -0.0021781 | -0.030563 | -0.068665 | 63.208 | -60.4156 | 63.295 | -60.2554 | -60.585 | -0.07782 | -0.050354 | 63.2309 | -60.3516 | 63.4186 | -60.3012 | -60.4111 | -60.2509 | -0.13733 | -0.068664 | 0.018311 | 0.022888 | 60.2005 | -0.3067 | 60.3378 | -0.16937 | -0.073242 | -0.045776 | 0.14191 | -0.022888 | 0.027466 | -0.13275 | 0.10071 | -0.05951 | 0.16022 | 123.7106 | 0.050354 | 123.7701 | 123.6237 | 123.5825 | 123.4863 | 123.5092 | -123.6923 | -123.6282 | 123.5733 | 123.6969 | 60.2097 | 60.228
232.4844 | 123.7564 | -60.2509 | 63.2767 | 0.1101 | 0.0060595 | 0.056722 | 0.065144 | -0.014351 | 0.013114 | 0.0025066 | 0.10011 | 0.0033634 | 0.066753 | 0.10571 | -0.0147 | 0.0063669 | 0.00041246 | -0.09613 | 63.2309 | -60.4477 | 63.3224 | -60.2005 | -60.553 | -0.045776 | -0.07782 | 63.2355 | -60.3287 | 63.4277 | -60.3149 | -60.4111 | -60.2646 | -0.19684 | -0.045776 | 0.045777 | 0.050354 | 60.2051 | -0.30213 | 60.4019 | -0.10529 | -0.07782 | -0.041198 | 0.15106 | -0.064087 | -0.013733 | -0.16022 | 0.064087 | -0.082398 | 0.24719 | 123.7701 | 0.013733 | 123.7564 | 123.6786 | 123.5641 | 123.4818 | 123.4863 | -123.7244 | -123.6053 | 123.5733 | 123.6786 | 60.1547 | 60.173
233.4844 | 123.7518 | -60.26 | 63.2675 | 0.1101 | 0.0017875 | 0.058858 | 0.069417 | 0.0016711 | 0.0013638 | 0.0025066 | 0.039077 | -0.0041136 | 0.07957 | 0.087555 | -0.0040182 | 0.012775 | -0.013474 | -0.10071 | 63.2034 | -60.4111 | 63.3362 | -60.2051 | -60.5438 | -0.036621 | -0.07782 | 63.2492 | -60.347 | 63.4232 | -60.3241 | -60.4065 | -60.2509 | -0.15106 | -0.064087 | 0.068665 | 0.054932 | 60.2234 | -0.28381 | 60.3745 | -0.13275 | -0.086975 | -0.01831 | 0.15564 | -0.064087 | 0.009156 | -0.14648 | 0.096131 | -0.059509 | 0.20599 | 123.7473 | 0.022888 | 123.7701 | 123.6145 | 123.5962 | 123.4634 | 123.5092 | -123.6786 | -123.6145 | 123.5962 | 123.6832 | 60.1593 | 60.1822
234.4844 | 123.7839 | -60.2646 | 63.2675 | 0.1101 | 0.010333 | 0.05779 | 0.071553 | -0.0004649 | -0.0018402 | 0.0067786 | 0.0085594 | 0.0012264 | 0.056072 | 0.057647 | -0.010427 | 0.0010259 | 0.0025485 | -0.054932 | 63.1943 | -60.3928 | 63.2721 | -60.2783 | -60.6216 | -0.10071 | -0.009155 | 63.1989 | -60.3378 | 63.4598 | -60.2737 | -60.4065 | -60.2463 | -0.12817 | -0.073242 | 0.004578 | -0.013733 | 60.1639 | -0.35706 | 60.2921 | -0.22888 | -0.073243 | -0.068664 | 0.19226 | -0.009156 | 0.01831 | -0.14191 | 0.091553 | -0.068664 | 0.11444 | 123.6649 | 0.064087 | 123.7976 | 123.587 | 123.5367 | 123.4589 | 123.4634 | -123.6603 | -123.6053 | 123.5367 | 123.7244 | 60.2097 | 60.2554
235.4844 | 123.7701 | -60.2554 | 63.2675 | 0.03381 | 0.00071953 | 0.065267 | 0.064076 | 0.014488 | 0.0056368 | -0.010311 | 0.22218 | 0.0022944 | 0.068889 | 0.066192 | -0.0061552 | -0.0011101 | -0.017746 | -0.07782 | 63.2309 | -60.4111 | 63.3499 | -60.173 | -60.5301 | -0.022888 | -0.07782 | 63.2538 | -60.3424 | 63.3682 | -60.3012 | -60.3882 | -60.2463 | -0.15564 | -0.036621 | 0.082398 | 0.082397 | 60.2325 | -0.27466 | 60.3882 | -0.11902 | -0.086975 | -0.013733 | 0.10071 | -0.045776 | 0.009155 | -0.13275 | 0.09613 | -0.045777 | 0.23804 | 123.761 | 0.041199 | 123.7106 | 123.642 | 123.5962 | 123.4863 | 123.5092 | -123.6786 | -123.6099 | 123.6053 | 123.6237 | 60.1776 | 60.1776
236.4844 | 123.7747 | -60.2646 | 63.2812 | 0.1864 | -0.0046215 | 0.054585 | 0.069417 | -0.02076 | -0.015725 | -0.0028344 | 0.069594 | -0.0062496 | 0.07423 | 0.055511 | 0.00025378 | 0.0052979 | 0.0046845 | -0.073242 | 63.1989 | -60.4111 | 63.3041 | -60.2325 | -60.5667 | -0.064087 | -0.068665 | 63.2355 | -60.3333 | 63.4277 | -60.3104 | -60.4156 | -60.26 | -0.14648 | -0.082397 | 0.022888 | 0.032043 | 60.2005 | -0.30212 | 60.347 | -0.15564 | -0.068665 | -0.045776 | 0.14648 | -0.045777 | 0.004577 | -0.15106 | 0.073242 | -0.082397 | 0.17853 | 123.7152 | 0.022888 | 123.761 | 123.6099 | 123.5687 | 123.4634 | 123.5001 | -123.6923 | -123.6145 | 123.5687 | 123.6923 | 60.1913 | 60.1959
237.4844 | 123.7701 | -60.2829 | 63.2538 | 0.12536 | 0.0028555 | 0.069539 | 0.068349 | 0.0027391 | 0.016318 | 0.0025066 | 0.023818 | -0.0030456 | 0.067821 | 0.068329 | -0.0050872 | 0.01598 | 0.0036165 | -0.07782 | 63.2034 | -60.4202 | 63.2904 | -60.2509 | -60.5804 | -0.073242 | -0.054932 | 63.2263 | -60.3378 | 63.4415 | -60.2966 | -60.4065 | -60.26 | -0.13733 | -0.050354 | 0.036621 | 0.032044 | 60.2097 | -0.29755 | 60.347 | -0.16022 | -0.054932 | -0.027466 | 0.18768 | -0.013733 | 0.022888 | -0.1236 | 0.07782 | -0.068664 | 0.16937 | 123.7106 | 0.041199 | 123.7793 | 123.6237 | 123.5641 | 123.4863 | 123.5092 | -123.674 | -123.5916 | 123.5733 | 123.7244 | 60.2051 | 60.228
238.4844 | 123.7518 | -60.2417 | 63.2812 | 0.03381 | 0.0060595 | 0.056722 | 0.073689 | -0.0026019 | 0.010977 | -0.0081744 | 0.023818 | 0.0012264 | 0.061412 | 0.090759 | -0.0029502 | 0.0085029 | -0.0027915 | -0.091553 | 63.2172 | -60.4065 | 63.2812 | -60.2463 | -60.5896 | -0.068665 | -0.045776 | 63.2309 | -60.3195 | 63.4415 | -60.3149 | -60.4019 | -60.2554 | -0.1648 | -0.064087 | 0 | -0.004578 | 60.173 | -0.3479 | 60.3378 | -0.18311 | -0.07782 | -0.050354 | 0.16022 | -0.073242 | -0.013733 | -0.16022 | 0.064087 | -0.082398 | 0.16022 | 123.6877 | 0.004578 | 123.761 | 123.6237 | 123.5504 | 123.4589 | 123.4726 | -123.6877 | -123.6008 | 123.5229 | 123.6832 | 60.1501 | 60.1959
239.4844 | 123.7793 | -60.2692 | 63.2904 | 0.018551 | 0.0039235 | 0.060994 | 0.074757 | -0.012215 | -0.0039762 | 0.00037059 | 0.039077 | -0.011591 | 0.067821 | 0.080078 | 0.0055948 | 0.012775 | -0.0049285 | -0.091553 | 63.2309 | -60.4202 | 63.3316 | -60.2051 | -60.5484 | -0.050354 | -0.082397 | 63.2446 | -60.3012 | 63.4277 | -60.3104 | -60.4065 | -60.2509 | -0.15106 | -0.059509 | 0.041199 | 0.064087 | 60.2188 | -0.27924 | 60.3699 | -0.12817 | -0.032043 | -0.045776 | 0.13733 | -0.041199 | 0.018311 | -0.13733 | 0.050354 | -0.10529 | 0.21515 | 123.7518 | -0.009156 | 123.7289 | 123.6511 | 123.5458 | 123.5001 | 123.5138 | -123.7106 | -123.5916 | 123.6008 | 123.6969 | 60.1776 | 60.1868
240.4844 | 123.7061 | -60.2463 | 63.3224 | 0.12536 | -0.0056895 | 0.066335 | 0.075825 | -0.0004649 | -0.0061122 | -0.0071064 | 0.17641 | -0.00090962 | 0.068889 | 0.057647 | -0.0029502 | -0.0021781 | -0.016678 | 0.032043 | 63.2584 | -60.3699 | 63.3682 | -60.1959 | -60.5118 | 0.036621 | 0.004578 | 63.3087 | -60.2829 | 63.4186 | -60.2966 | -60.4111 | -60.2554 | -0.1236 | -0.064087 | 0.045776 | 0.050354 | 60.2829 | -0.2655 | 60.4065 | -0.14191 | -0.036621 | -0.013733 | 0.09613 | -0.050354 | -0.009155 | -0.16479 | 0.027466 | -0.12817 | 0.17395 | 123.7381 | -0.013733 | 123.7015 | 123.6282 | 123.5916 | 123.5046 | 123.555 | -123.6923 | -123.6053 | 123.6145 | 123.6649 | 60.2783 | 60.2509
241.4844 | 123.7793 | -60.2509 | 63.2812 | 0.1101 | 0.0060595 | 0.04604 | 0.063008 | 0.0080791 | 0.0035008 | -0.0092424 | -0.021958 | 0.00015838 | 0.063548 | 0.092895 | -0.0018822 | 0.0063669 | -0.0059965 | -0.059509 | 63.2172 | -60.4019 | 63.3087 | -60.2554 | -60.585 | -0.07782 | -0.027466 | 63.2492 | -60.3241 | 63.4735 | -60.2829 | -60.3973 | -60.2234 | -0.15106 | -0.064087 | 0.027466 | -0.004578 | 60.173 | -0.33417 | 60.3241 | -0.18311 | -0.073243 | -0.032043 | 0.19226 | -0.032044 | 0.027465 | -0.14649 | 0.10071 | -0.073242 | 0.14648 | 123.7106 | 0.041199 | 123.7976 | 123.6191 | 123.5733 | 123.468 | 123.5001 | -123.6832 | -123.6053 | 123.5596 | 123.7244 | 60.1913 | 60.2234
242.4844 | 123.7656 | -60.2692 | 63.2858 | 0.0032924 | 0.0039235 | 0.064198 | 0.066212 | -0.0090099 | -0.017862 | -0.0092424 | 0.039077 | 0.0022944 | 0.063548 | 0.08435 | -0.0040182 | 0.0063669 | -0.010269 | -0.07782 | 63.2309 | -60.3928 | 63.3087 | -60.2234 | -60.5576 | -0.064087 | -0.082397 | 63.2401 | -60.3287 | 63.4415 | -60.3241 | -60.4156 | -60.2554 | -0.1236 | -0.054932 | 0.022888 | 0.045776 | 60.2051 | -0.28839 | 60.3287 | -0.16479 | -0.059509 | -0.045777 | 0.15564 | -0.054932 | 0.013733 | -0.14648 | 0.073242 | -0.086975 | 0.16937 | 123.7015 | 0.004577 | 123.7701 | 123.6237 | 123.5687 | 123.5001 | 123.5092 | -123.6786 | -123.6145 | 123.5779 | 123.7106 | 60.1913 | 60.1868
243.4844 | 123.7701 | -60.26 | 63.2721 | 0.094845 | -0.0024855 | 0.059926 | 0.07903 | 0.0027391 | -0.019998 | -0.0039024 | 0.0085594 | 0.0033634 | 0.078502 | 0.043762 | 0.0098668 | 0.0095709 | -0.0070645 | -0.09613 | 63.2034 | -60.4248 | 63.2904 | -60.2509 | -60.5576 | -0.086975 | -0.050354 | 63.2584 | -60.3424 | 63.4277 | -60.3058 | -60.3928 | -60.2325 | -0.16479 | -0.068665 | 0.01831 | 0.009156 | 60.173 | -0.29755 | 60.3378 | -0.13275 | -0.082397 | -0.013733 | 0.15564 | -0.045776 | 0.027466 | -0.13275 | 0.10986 | -0.050354 | 0.17395 | 123.7152 | 0.036621 | 123.7701 | 123.6282 | 123.6008 | 123.4634 | 123.5184 | -123.6969 | -123.6145 | 123.5504 | 123.6877 | 60.1639 | 60.2097
244.4844 | 123.7518 | -60.2646 | 63.2812 | 0.14062 | 0.0039235 | 0.066335 | 0.066212 | 0.011284 | -0.010385 | -0.0017664 | -0.021958 | 0.0022944 | 0.077434 | 0.0961 | -0.0061552 | 0.019184 | -0.01561 | -0.082397 | 63.2126 | -60.4248 | 63.2767 | -60.2692 | -60.585 | -0.082397 | -0.050354 | 63.2446 | -60.3333 | 63.4415 | -60.3012 | -60.4065 | -60.2371 | -0.16022 | -0.068665 | -0.004578 | -0.004578 | 60.1822 | -0.32044 | 60.3424 | -0.16022 | -0.068665 | -0.036621 | 0.16022 | -0.036621 | 0.027465 | -0.14191 | 0.09613 | -0.073242 | 0.15564 | 123.7015 | 0.032044 | 123.7747 | 123.6374 | 123.5779 | 123.4772 | 123.5092 | -123.7061 | -123.6145 | 123.5413 | 123.7061 | 60.1822 | 60.2142
245.4844 | 123.8113 | -60.2371 | 63.3133 | 0.1864 | 0.0071275 | 0.051381 | 0.06728 | -0.0090099 | -0.0082492 | 0.00037059 | 0.26796 | 0.0022944 | 0.06248 | 0.081146 | 0.0023898 | 0.0042299 | -0.0070645 | 0.15106 | 63.3041 | -60.3424 | 63.2996 | -60.2097 | -60.5438 | -0.082397 | 0.036621 | 63.2584 | -60.3149 | 63.4827 | -60.2142 | -60.3424 | -60.1959 | -0.10529 | -0.009155 | -0.013732 | 0.027466 | 60.1547 | -0.3067 | 60.26 | -0.20142 | -0.077819 | -0.054931 | 0.16937 | 0.022889 | 0.041199 | -0.10529 | 0.11902 | -0.027466 | 0.13275 | 123.642 | 0.10071 | 123.7976 | 123.6465 | 123.5733 | 123.5413 | 123.4955 | -123.6557 | -123.6282 | 123.5367 | 123.7198 | 60.3882 | 60.2737
246.4844 | 123.7656 | -60.2875 | 63.2858 | 0.018551 | 0.0017875 | 0.062062 | 0.069417 | 0.0016711 | -0.0071802 | 0.0078466 | -0.0066996 | 0.0044314 | 0.07423 | 0.064056 | -0.0018822 | 0.0063669 | -0.00065554 | -0.10071 | 63.2217 | -60.4019 | 63.3224 | -60.2142 | -60.5484 | -0.041199 | -0.10071 | 63.2584 | -60.3378 | 63.4323 | -60.3012 | -60.4019 | -60.2371 | -0.11444 | -0.064087 | 0.036621 | 0.073243 | 60.2463 | -0.26093 | 60.3607 | -0.14648 | -0.050354 | -0.027466 | 0.14648 | -0.013732 | 0.050354 | -0.11444 | 0.10071 | -0.064087 | 0.18768 | 123.7244 | 0.036622 | 123.7701 | 123.6237 | 123.5962 | 123.5092 | 123.5458 | -123.6877 | -123.6237 | 123.6099 | 123.7198 | 60.1868 | 60.1868
247.4844 | 123.8113 | -60.2875 | 63.2584 | 0.32373 | 0.011401 | 0.06313 | 0.074757 | -0.0058059 | 0.0077728 | 0.00037059 | -0.037217 | -0.0041136 | 0.069957 | 0.077942 | -0.0082912 | 0.0042299 | -0.0017235 | -0.068665 | 63.2446 | -60.3561 | 63.2538 | -60.3058 | -60.5988 | -0.07782 | -0.036621 | 63.2492 | -60.3149 | 63.4689 | -60.2829 | -60.3653 | -60.2234 | -0.068664 | -0.013733 | -0.004578 | -0.01831 | 60.2097 | -0.31128 | 60.2783 | -0.24261 | -0.027465 | -0.009155 | 0.21057 | 0.004578 | 0.064087 | -0.077819 | 0.091552 | -0.050354 | 0.050354 | 123.6099 | 0.032043 | 123.7839 | 123.6008 | 123.5641 | 123.5321 | 123.5367 | -123.6145 | -123.5733 | 123.5413 | 123.7564 | 60.2188 | 60.2509
248.4844 | 123.8251 | -60.2554 | 63.2767 | 0.03381 | -0.00034947 | 0.065267 | 0.071553 | -0.0026019 | -0.0018402 | -0.0028344 | -0.067735 | -0.0030456 | 0.061412 | 0.06192 | 0.0055948 | 0.014911 | 0.0078895 | -0.045776 | 63.208 | -60.4431 | 63.3041 | -60.2509 | -60.6216 | -0.082397 | -0.059509 | 63.2126 | -60.347 | 63.4735 | -60.2417 | -60.347 | -60.1959 | -0.18768 | -0.068664 | 0.027466 | 0.004578 | 60.173 | -0.36621 | 60.3607 | -0.17853 | -0.091553 | -0.064087 | 0.19684 | 0.013733 | 0.059509 | -0.091553 | 0.15106 | 0 | 0.19226 | 123.7473 | 0.10529 | 123.8205 | 123.6511 | 123.5596 | 123.4634 | 123.468 | -123.7198 | -123.6237 | 123.5596 | 123.7289 | 60.2097 | 60.1959
249.4844 | 123.7656 | -60.2509 | 63.2492 | 0.018551 | 0.0071275 | 0.056722 | 0.073689 | -0.0004649 | 0.0024328 | 0.0025066 | 0.054336 | 0.0044314 | 0.07423 | 0.053375 | -0.00081422 | -0.0021781 | 0.011093 | -0.10071 | 63.1989 | -60.3928 | 63.2812 | -60.2646 | -60.585 | -0.082397 | -0.059509 | 63.2355 | -60.3149 | 63.4552 | -60.2921 | -60.3973 | -60.2463 | -0.14191 | -0.050354 | 0.032043 | -0.013733 | 60.1685 | -0.33417 | 60.3104 | -0.19226 | -0.064087 | -0.013733 | 0.20599 | -0.041199 | 0.004577 | -0.14649 | 0.068664 | -0.082398 | 0.12817 | 123.674 | 0.022888 | 123.7701 | 123.5916 | 123.5504 | 123.4497 | 123.4863 | -123.642 | -123.5641 | 123.5321 | 123.7061 | 60.1501 | 60.1913
250.4844 | 123.8068 | -60.2417 | 63.295 | 0.15588 | -0.0056895 | 0.055654 | 0.074757 | -0.018623 | 0.0035008 | -0.0049704 | 0.23744 | 0.0012264 | 0.072093 | 0.057647 | -0.0040182 | -0.0011101 | 0.0025485 | -0.059509 | 63.2492 | -60.3882 | 63.3453 | -60.2005 | -60.5438 | -0.032043 | -0.018311 | 63.2538 | -60.3058 | 63.4872 | -60.2325 | -60.3516 | -60.2005 | -0.14649 | -0.045776 | 0.050354 | 0.041199 | 60.2097 | -0.30212 | 60.3561 | -0.15564 | -0.064087 | -0.041199 | 0.19226 | 0.009155 | 0.041199 | -0.10986 | 0.10529 | -0.045776 | 0.18768 | 123.7335 | 0.073242 | 123.793 | 123.6374 | 123.5596 | 123.4909 | 123.4955 | -123.6832 | -123.6008 | 123.587 | 123.7289 | 60.1822 | 60.2234
251.4844 | 123.8022 | -60.2554 | 63.2492 | 0.094845 | 0.0049915 | 0.060994 | 0.06728 | -0.0068739 | -0.0029082 | 0.0014386 | 0.023818 | -0.010523 | 0.064617 | 0.056579 | -0.0061552 | 0.0074349 | 0.0036165 | -0.059509 | 63.2126 | -60.3973 | 63.295 | -60.2371 | -60.585 | -0.091553 | -0.054932 | 63.2309 | -60.3333 | 63.4598 | -60.2783 | -60.3699 | -60.2371 | -0.14191 | -0.036622 | 0.045776 | 0.01831 | 60.1639 | -0.32959 | 60.3058 | -0.18768 | -0.07782 | -0.018311 | 0.21057 | -0.022888 | 0.01831 | -0.11444 | 0.09613 | -0.036621 | 0.16022 | 123.6923 | 0.054932 | 123.793 | 123.6099 | 123.5641 | 123.468 | 123.4863 | -123.6465 | -123.5825 | 123.5504 | 123.7152 | 60.1959 | 60.2005
252.4844 | 123.8022 | -60.2646 | 63.2675 | -0.11878 | 0.012469 | 0.050313 | 0.074757 | 0.0006031 | 0.0013638 | -0.014583 | 0.023818 | 0.0033634 | 0.059276 | 0.083282 | -0.0061552 | 0.017048 | 0.00041246 | 0.050354 | 63.1851 | -60.3653 | 63.295 | -60.2875 | -60.6308 | -0.11902 | -0.032043 | 63.2217 | -60.3104 | 63.4689 | -60.2692 | -60.379 | -60.2234 | -0.10071 | -0.082397 | 0.027466 | -0.022889 | 60.1456 | -0.36621 | 60.2463 | -0.2655 | -0.045777 | -0.045776 | 0.20142 | -0.004578 | 0.041198 | -0.11444 | 0.086975 | -0.068664 | 0.077819 | 123.6603 | 0.041199 | 123.7793 | 123.5504 | 123.5321 | 123.4497 | 123.4863 | -123.6328 | -123.5779 | 123.5596 | 123.7335 | 60.3149 | 60.2325
253.4844 | 123.7793 | -60.2875 | 63.2767 | 0.17114 | 0.0028555 | 0.056722 | 0.06728 | 0.019829 | -0.0061122 | -0.0071064 | 0.054336 | 0.0044314 | 0.060344 | 0.081146 | -0.0040182 | -4.2099e-05 | 0.0057535 | -0.10071 | 63.208 | -60.3836 | 63.2996 | -60.2463 | -60.5713 | -0.068665 | -0.082397 | 63.2492 | -60.3195 | 63.4369 | -60.2921 | -60.3973 | -60.2371 | -0.09613 | -0.068664 | 0.022889 | 0.041199 | 60.2188 | -0.28381 | 60.3149 | -0.18768 | -0.032043 | -0.027465 | 0.16022 | -0.004577 | 0.050354 | -0.10986 | 0.082397 | -0.07782 | 0.13733 | 123.6832 | 0.027466 | 123.7564 | 123.5916 | 123.5687 | 123.4955 | 123.5367 | -123.6603 | -123.5962 | 123.587 | 123.7244 | 60.1868 | 60.2051
254.4844 | 123.8159 | -60.2463 | 63.2675 | 0.15588 | 0.0081955 | 0.070607 | 0.076894 | 0.0059431 | 0.0056368 | -0.0081744 | 0.39003 | 0.0012264 | 0.07957 | 0.057647 | -0.012563 | 0.0052979 | 0.00041246 | -0.086975 | 63.2126 | -60.4019 | 63.2629 | -60.1959 | -60.5988 | -0.29297 | -0.068665 | 63.2675 | -60.3058 | 63.4415 | -60.2966 | -60.3653 | -60.2142 | -0.15564 | -0.054932 | -0.004578 | 0.050354 | 59.9533 | -0.35248 | 60.1089 | -0.19684 | -0.059509 | 0 | 0.17395 | -0.050354 | 0.032044 | -0.11902 | 0.091553 | -0.059509 | 0.20599 | 123.6649 | 0.009155 | 123.7473 | 123.6145 | 123.5733 | 123.4589 | 123.5138 | -123.6694 | -123.5733 | 123.5092 | 123.6877 | 60.1593 | 60.1776
255.4844 | 123.7381 | -60.2692 | 63.2858 | 0.018551 | 0.0049915 | 0.056722 | 0.073689 | 0.0070111 | -0.012521 | -0.017787 | 0.039077 | -0.010523 | 0.069957 | 0.073669 | 0.0034578 | -0.0032471 | -0.0070645 | -0.11902 | 63.208 | -60.3928 | 63.327 | -60.2005 | -60.5438 | -0.041199 | -0.09613 | 63.2629 | -60.3424 | 63.4323 | -60.2875 | -60.3882 | -60.2417 | -0.1236 | -0.07782 | 0.041198 | 0.068665 | 60.228 | -0.27466 | 60.3516 | -0.15106 | -0.073242 | -0.022889 | 0.14648 | -0.018311 | 0.027466 | -0.11902 | 0.10071 | -0.045777 | 0.19226 | 123.7198 | 0.054931 | 123.7747 | 123.6008 | 123.6053 | 123.4772 | 123.5321 | -123.6786 | -123.6282 | 123.5962 | 123.7015 | 60.1501 | 60.173
256.4844 | 123.8022 | -60.2463 | 63.2675 | 0.0032924 | 0.00071953 | 0.05779 | 0.075825 | -0.0036699 | 0.0035008 | -0.0028344 | -0.052476 | 0.0087034 | 0.073162 | 0.060852 | -0.0082912 | 0.0095709 | -0.0059965 | -0.082397 | 63.2034 | -60.4111 | 63.3133 | -60.2417 | -60.5804 | -0.073242 | -0.068665 | 63.2446 | -60.3058 | 63.4552 | -60.2692 | -60.3745 | -60.2097 | -0.16479 | -0.064087 | 0.045776 | 0.004578 | 60.173 | -0.33417 | 60.3378 | -0.16937 | -0.059509 | -0.022888 | 0.18768 | -0.022888 | 0.036621 | -0.12817 | 0.09613 | -0.068665 | 0.16937 | 123.7244 | 0.036621 | 123.761 | 123.6145 | 123.5504 | 123.4497 | 123.4909 | -123.6786 | -123.5733 | 123.5596 | 123.7015 | 60.1639 | 60.1776
257.4844 | 123.8251 | -60.2371 | 63.2492 | 0.1864 | -0.0024855 | 0.065267 | 0.06728 | -0.0026019 | -0.011453 | -0.010311 | -0.037217 | -0.0062496 | 0.06248 | 0.055511 | -0.0061552 | 0.0042299 | 0.00041246 | -0.013733 | 63.208 | -60.3607 | 63.3041 | -60.3104 | -60.6308 | -0.10529 | -0.027466 | 63.2355 | -60.2921 | 63.4735 | -60.26 | -60.3699 | -60.2188 | -0.1236 | -0.041199 | 0.054931 | -0.073242 | 60.1318 | -0.39368 | 60.2554 | -0.27008 | -0.054931 | -0.013733 | 0.2243 | -0.022888 | 0.018311 | -0.13275 | 0.073242 | -0.07782 | 0.050354 | 123.6649 | 0.032043 | 123.7656 | 123.5687 | 123.5275 | 123.4451 | 123.4726 | -123.6099 | -123.5413 | 123.5413 | 123.7106 | 60.2234 | 60.2097
258.4844 | 123.8113 | -60.2554 | 63.2675 | 0.1101 | 0.0081955 | 0.055654 | 0.069417 | -0.0079419 | -0.019998 | 0.01746 | 0.11537 | 0.0012264 | 0.067821 | 0.032013 | -0.010427 | 0.0031619 | -0.013474 | -0.091553 | 63.2172 | -60.4019 | 63.2584 | -60.2371 | -60.5804 | -0.11444 | -0.10986 | 63.2217 | -60.3195 | 63.4781 | -60.2463 | -60.3287 | -60.1822 | -0.14648 | -0.050354 | -0.009155 | 0.01831 | 60.141 | -0.32501 | 60.2875 | -0.17853 | -0.064087 | -0.045776 | 0.21057 | 0.009155 | 0.073242 | -0.073242 | 0.13733 | -0.009155 | 0.16479 | 123.6603 | 0.073242 | 123.7976 | 123.6191 | 123.5413 | 123.4726 | 123.4772 | -123.6694 | -123.587 | 123.5138 | 123.7335 | 60.1639 | 60.1456
259.4844 | 123.8251 | -60.2371 | 63.2721 | 0.064327 | 0.014605 | 0.064198 | 0.071553 | 0.0048751 | 0.0099088 | -0.0092424 | -0.052476 | 0.0065674 | 0.073162 | 0.065124 | -0.0082912 | 0.0063669 | -0.016678 | -0.10071 | 63.2263 | -60.4019 | 63.3224 | -60.2921 | -60.791 | -0.11444 | -0.018311 | 63.2492 | -60.3149 | 63.4552 | -60.2646 | -60.3699 | -60.2097 | -0.16479 | -0.045777 | 0.050354 | -0.054931 | 60.1227 | -0.55389 | 60.2875 | -0.3891 | -0.077819 | -0.022888 | 0.1831 | -0.027465 | 0.027466 | -0.13275 | 0.10528 | -0.054932 | 0.10986 | 123.7244 | 0.050354 | 123.7701 | 123.6282 | 123.5641 | 123.4634 | 123.4863 | -123.674 | -123.587 | 123.5596 | 123.6923 | 60.1364 | 60.2188
260.4844 | 123.7701 | -60.2463 | 63.2858 | 0.0032924 | -0.0067575 | 0.054585 | 0.068349 | 0.023033 | -0.0082492 | -0.016719 | 0.0085594 | -0.0083866 | 0.067821 | 0.083282 | -0.010427 | 0.0095709 | -0.0059965 | -0.09613 | 63.2492 | -60.3745 | 63.3591 | -60.1593 | -60.5438 | -0.009155 | -0.10529 | 63.2858 | -60.3058 | 63.414 | -60.2966 | -60.3928 | -60.228 | -0.12817 | -0.036621 | 0.073242 | 0.086975 | 60.2371 | -0.29755 | 60.3653 | -0.16937 | -0.059509 | 0 | 0.12817 | -0.050354 | 0.018311 | -0.14648 | 0.07782 | -0.086975 | 0.21515 | 123.7335 | 0.009155 | 123.7198 | 123.6237 | 123.5916 | 123.4955 | 123.5321 | -123.6603 | -123.5916 | 123.6053 | 123.6603 | 60.1501 | 60.141
261.4844 | 123.7793 | -60.2051 | 63.2858 | 0.1101 | 0.012469 | 0.058858 | 0.075825 | -0.0004649 | 0.0067048 | -0.010311 | -0.037217 | 0.0033634 | 0.069957 | 0.032013 | -0.011495 | 0.011707 | -0.013474 | -0.09613 | 63.2172 | -60.4202 | 63.2767 | -60.2509 | -60.585 | -0.09613 | -0.082397 | 63.2355 | -60.2921 | 63.2858 | -60.1685 | -60.1547 | -60.0769 | -0.21515 | -0.068665 | -0.009156 | -0.045776 | 60.1089 | -0.37994 | 60.3241 | -0.1648 | -0.086975 | -0.050354 | 0 | 0.036621 | 0.12817 | 0.050354 | 0.21515 | 0.13733 | 0.16937 | 123.6969 | 0.1236 | 123.5779 | 123.6374 | 123.5275 | 123.4222 | 123.4406 | -123.7061 | -123.5779 | 123.4818 | 123.4909 | 60.1089 | 60.1227
262.4844 | 123.8388 | -60.2371 | 63.2263 | 0.12536 | 0.0028555 | 0.050313 | 0.074757 | 0.0006031 | -0.0093172 | -0.0049704 | -0.082994 | 0.0044314 | 0.073162 | 0.050171 | -0.0072232 | 0.013843 | 0.01857 | -0.14191 | 63.1989 | -60.4248 | 63.2858 | -60.2509 | -60.5759 | -0.09613 | -0.068665 | 63.2309 | -60.3195 | 63.4872 | -60.2554 | -60.3561 | -60.1868 | -0.18768 | -0.027465 | 0.05951 | -0.013732 | 60.141 | -0.33875 | 60.3287 | -0.15106 | -0.082397 | 0.004578 | 0.26093 | -0.01831 | 0.050354 | -0.11902 | 0.13275 | -0.036621 | 0.17395 | 123.7106 | 0.064087 | 123.8068 | 123.6237 | 123.5504 | 123.436 | 123.468 | -123.6511 | -123.5458 | 123.523 | 123.7244 | 60.0952 | 60.1685
263.4844 | 123.7793 | -60.2463 | 63.2767 | -0.088261 | 0.0017875 | 0.056722 | 0.071553 | 0.0059431 | -0.013589 | 0.00037059 | 0.11537 | -0.0030456 | 0.058208 | 0.035217 | -0.0040182 | 0.0074349 | -0.0059965 | 0.050354 | 63.2034 | -60.3745 | 63.2904 | -60.2463 | -60.6216 | -0.11902 | -0.050354 | 63.2584 | -60.2829 | 63.4689 | -60.2554 | -60.379 | -60.2142 | -0.12817 | -0.073242 | 0.013733 | 0 | 60.1273 | -0.37537 | 60.2554 | -0.24719 | -0.036621 | -0.01831 | 0.19226 | -0.009155 | 0.032044 | -0.13275 | 0.068665 | -0.09613 | 0.12817 | 123.6649 | 0.027466 | 123.7518 | 123.5779 | 123.5413 | 123.4497 | 123.5046 | -123.6511 | -123.5596 | 123.5367 | 123.7152 | 60.2966 | 60.1959
264.4844 | 123.8022 | -60.2463 | 63.295 | 0.14062 | 0.0081955 | 0.060994 | 0.058736 | 0.0016711 | 0.0056368 | -0.0028344 | 0.069594 | 0.0044314 | 0.068889 | 0.083282 | -0.0050872 | 0.0085029 | -0.0017235 | -0.11902 | 63.2217 | -60.4202 | 63.2812 | -60.2646 | -60.5621 | -0.10529 | -0.09613 | 63.2263 | -60.3287 | 63.4872 | -60.2463 | -60.3516 | -60.1776 | -0.17395 | -0.073242 | -0.013733 | -0.01831 | 60.141 | -0.31586 | 60.3149 | -0.14191 | -0.082397 | -0.068665 | 0.19226 | 0 | 0.068665 | -0.10529 | 0.15106 | -0.022888 | 0.15564 | 123.7015 | 0.082397 | 123.8159 | 123.642 | 123.555 | 123.468 | 123.4726 | -123.7152 | -123.6237 | 123.5275 | 123.7335 | 60.1273 | 60.1501
265.4844 | 123.7564 | -60.228 | 63.295 | 0.12536 | 0.0039235 | 0.053517 | 0.06728 | 0.0027391 | 0.0056368 | -0.014583 | 0.2527 | -0.0041136 | 0.049663 | 0.011719 | -0.0018822 | 0.01598 | 0.0068215 | -0.022888 | 63.2629 | -60.379 | 63.382 | -60.1456 | -60.5484 | -0.032043 | -0.10071 | 63.2629 | -60.3287 | 63.4644 | -60.2829 | -60.3745 | -60.2463 | -0.15106 | -0.032044 | 0.086975 | 0.082397 | 60.1959 | -0.32043 | 60.347 | -0.16937 | -0.10071 | -0.032044 | 0.16937 | -0.054932 | -0.018311 | -0.14648 | 0.082397 | -0.045777 | 0.23346 | 123.761 | 0.045776 | 123.793 | 123.642 | 123.5916 | 123.4909 | 123.4909 | -123.674 | -123.6237 | 123.6099 | 123.6923 | 60.2051 | 60.1273
266.4844 | 123.793 | -60.2463 | 63.2584 | 0.03381 | 0.0039235 | 0.06313 | 0.077962 | 0.0006031 | -0.0029082 | -0.013515 | 0.17641 | 0.0087034 | 0.072093 | 0.052307 | -0.012563 | 0.013843 | 0.0036165 | -0.10071 | 63.2034 | -60.3928 | 63.2721 | -60.2463 | -60.5896 | -0.07782 | -0.1831 | 63.1897 | -60.3378 | 63.4689 | -60.2005 | -60.3699 | -60.2005 | -0.14648 | -0.054932 | 0.013733 | 0 | 60.1685 | -0.34332 | 60.3149 | -0.19684 | -0.091553 | -0.068665 | 0.21057 | 0.045777 | 0.045777 | -0.1236 | 0.13733 | -0.032043 | 0.14648 | 123.6649 | 0.13733 | 123.8068 | 123.5962 | 123.5275 | 123.4497 | 123.436 | -123.6511 | -123.5962 | 123.5184 | 123.7152 | 60.1456 | 60.0632
267.4844 | 123.761 | -60.2554 | 63.2584 | 0.14062 | -0.0024855 | 0.05779 | 0.073689 | -0.0036699 | 0.0013638 | 0.0014386 | 0.084853 | 0.0044314 | 0.067821 | 0.089691 | -0.0061552 | 0.019184 | 0.0078895 | -0.086975 | 63.2355 | -60.3745 | 63.2858 | -60.26 | -60.5896 | -0.068665 | -0.068665 | 63.2492 | -60.3333 | 63.4872 | -60.26 | -60.3653 | -60.2188 | -0.11902 | -0.022888 | 0.027466 | -0.004578 | 60.1868 | -0.33417 | 60.3058 | -0.21515 | -0.07782 | -0.009155 | 0.22888 | -0.004578 | 0.036621 | -0.10986 | 0.11444 | -0.032043 | 0.11444 | 123.6603 | 0.073242 | 123.8205 | 123.6099 | 123.5825 | 123.4909 | 123.5046 | -123.6328 | -123.5916 | 123.5413 | 123.7427 | 60.1685 | 60.1868
268.4844 | 123.7747 | -60.2325 | 63.295 | 0.094845 | 0.013537 | 0.065267 | 0.075825 | -0.0026019 | 0.021659 | 0.011052 | -0.067735 | -0.0041136 | 0.058208 | 0.06192 | 0.0023898 | 0.01598 | 0.0068215 | -0.09613 | 63.2355 | -60.3928 | 63.2767 | -60.2463 | -60.5896 | -0.07782 | -0.07782 | 63.2584 | -60.3104 | 63.4232 | -60.4568 | -60.1181 | -60.0082 | -0.16022 | -0.059509 | -0.018311 | -0.013733 | 60.1547 | -0.35706 | 60.3149 | -0.19684 | -0.07782 | -0.036621 | 0.12817 | -0.2243 | 0.2243 | 0.11444 | 0.30212 | 0.19226 | 0.14648 | 123.6694 | -0.14648 | 123.7335 | 123.6282 | 123.5687 | 123.468 | 123.4909 | -123.6877 | -123.6053 | 123.5092 | 123.6557 | 60.1364 | 60.1547
269.4844 | 123.7656 | -60.2783 | 63.2217 | -0.011967 | 0.0049915 | 0.054585 | 0.071553 | 0.010216 | -0.0050442 | 0.0078466 | -0.021958 | -0.0019776 | 0.065685 | 0.086487 | -0.011495 | 0.017048 | -0.010269 | -0.086975 | 63.2355 | -60.4248 | 63.295 | -60.2371 | -60.5804 | -0.082397 | -0.07782 | 63.2492 | -60.2966 | 63.4781 | -60.2463 | -60.3607 | -60.1776 | -0.14648 | 0.013733 | 0.073242 | 0.041198 | 60.1959 | -0.30212 | 60.3424 | -0.15564 | -0.018311 | 0.027466 | 0.25635 | 0.032043 | 0.10071 | -0.082398 | 0.11902 | -0.064087 | 0.18768 | 123.7198 | 0.050354 | 123.7747 | 123.6603 | 123.5458 | 123.5138 | 123.5275 | -123.6465 | -123.5184 | 123.5733 | 123.7564 | 60.1913 | 60.2005
270.4844 | 123.7518 | -60.2234 | 63.3041 | 0.15588 | -0.0067575 | 0.054585 | 0.068349 | 0.0091481 | -0.0082492 | 0.0057106 | 0.069594 | -0.00090962 | 0.075298 | 0.030945 | -0.0061552 | -0.0043151 | 0.0068215 | -0.10986 | 63.2492 | -60.3882 | 63.3453 | -60.1593 | -60.5118 | -0.022888 | -0.1236 | 63.2675 | -60.3012 | 63.4964 | -60.3699 | -60.347 | -60.1456 | -0.1648 | -0.054931 | 0.041199 | 0.064087 | 60.2005 | -0.28839 | 60.3653 | -0.1236 | -0.077819 | -0.036621 | 0.19226 | -0.14648 | 0.07782 | -0.1236 | 0.15564 | -0.045777 | 0.22888 | 123.7335 | -0.068665 | 123.7976 | 123.6374 | 123.5687 | 123.4726 | 123.4909 | -123.6923 | -123.6053 | 123.5687 | 123.7198 | 60.1135 | 60.0998
271.4844 | 123.8251 | -60.2463 | 63.2767 | -0.088261 | 0.011401 | 0.049245 | 0.085438 | 0.0048751 | 0.0045688 | -0.010311 | 0.054336 | -0.0019776 | 0.077434 | 0.082214 | -0.0050872 | 0.011707 | 0.014297 | 0.041199 | 63.208 | -60.379 | 63.2996 | -60.228 | -60.6125 | -0.09613 | -0.041199 | 63.2584 | -60.3104 | 63.4918 | -60.2417 | -60.3561 | -60.2051 | -0.13275 | -0.068664 | 0.022889 | 0.018311 | 60.1501 | -0.36621 | 60.2829 | -0.23346 | -0.064087 | -0.01831 | 0.21515 | 0.004578 | 0.041199 | -0.10986 | 0.10529 | -0.045776 | 0.15106 | 123.6786 | 0.068665 | 123.8022 | 123.587 | 123.5687 | 123.4543 | 123.5046 | -123.6557 | -123.587 | 123.5458 | 123.7381 | 60.2875 | 60.2051
272.4844 | 123.7885 | -60.2417 | 63.2584 | 0.079586 | 0.0092645 | 0.053517 | 0.075825 | -0.0058059 | -0.015725 | -0.0092424 | -0.021958 | -0.0030456 | 0.065685 | 0.091827 | -0.015768 | 0.013843 | -0.025223 | -0.3067 | 63.1897 | -60.4477 | 63.2767 | -60.2737 | -60.585 | -0.054932 | -0.07782 | 63.2401 | -60.3287 | 63.4964 | -60.2371 | -60.347 | -60.1959 | -0.20599 | -0.068665 | 0.01831 | -0.032044 | 60.1868 | -0.34332 | 60.3928 | -0.13733 | -0.086975 | -0.018311 | 0.23804 | 0.004577 | 0.045776 | -0.10529 | 0.13275 | -0.018311 | 0.17395 | 123.7244 | 0.091552 | 123.8251 | 123.6374 | 123.5687 | 123.4314 | 123.4818 | -123.7061 | -123.587 | 123.5184 | 123.7381 | 59.935 | 60.1639
273.4844 | 123.7747 | -60.2646 | 63.295 | 0.1101 | -0.0024855 | 0.064198 | 0.071553 | 0.0038071 | 0.0013638 | -0.0039024 | 0.084853 | 0.0033634 | 0.067821 | 0.086487 | -0.015768 | 0.0063669 | -0.0017235 | -0.11444 | 63.2401 | -60.3745 | 63.3041 | -60.228 | -60.5438 | -0.050354 | -0.086975 | 63.2584 | -60.3104 | 63.4277 | -60.2829 | -60.3699 | -60.2234 | -0.10986 | -0.054932 | 0.009155 | 0.036621 | 60.2142 | -0.27924 | 60.3241 | -0.16937 | -0.045777 | -0.036621 | 0.13275 | -0.018311 | 0.041198 | -0.10529 | 0.086975 | -0.059509 | 0.14648 | 123.6786 | 0.027466 | 123.7381 | 123.6145 | 123.5687 | 123.5046 | 123.5229 | -123.6694 | -123.6053 | 123.5687 | 123.6923 | 60.1501 | 60.1776
274.4844 | 123.7839 | -60.2325 | 63.2904 | 0.094845 | 0.0060595 | 0.067403 | 0.058736 | 0.018761 | -0.010385 | 0.0078466 | -0.0066996 | 0.0012264 | 0.064617 | 0.030945 | -0.016836 | 0.020252 | 0.011093 | -0.1236 | 63.2263 | -60.3928 | 63.295 | -60.2234 | -60.5484 | -0.059509 | -0.068665 | 63.2309 | -60.3058 | 63.4598 | -60.2875 | -60.379 | -60.2051 | -0.16022 | -0.064087 | 0.004578 | 0.009155 | 60.173 | -0.31586 | 60.3333 | -0.15564 | -0.073242 | -0.059509 | 0.16937 | -0.054932 | 0.027466 | -0.14648 | 0.10071 | -0.073242 | 0.16937 | 123.6877 | 0.01831 | 123.7656 | 123.6191 | 123.5367 | 123.4589 | 123.4634 | -123.6832 | -123.5962 | 123.5275 | 123.6923 | 60.1089 | 60.1639
275.4844 | 123.7747 | -60.2463 | 63.2996 | 0.15588 | 0.011401 | 0.059926 | 0.072621 | -0.0079419 | -0.0071802 | -0.014583 | 0.11537 | 0.0097714 | 0.068889 | 0.038421 | -0.012563 | 0.0063669 | 0.00041246 | -0.11444 | 63.2858 | -60.3653 | 63.3087 | -60.1593 | -60.4706 | -0.004578 | -0.13275 | 63.2858 | -60.3012 | 63.4781 | -60.2509 | -60.3561 | -60.2097 | -0.11902 | -0.013733 | 0.009155 | 0.086975 | 60.2417 | -0.2243 | 60.3607 | -0.10529 | -0.054931 | -0.013733 | 0.17853 | -0.004577 | 0.036621 | -0.10986 | 0.091552 | -0.054932 | 0.20599 | 123.674 | 0.050354 | 123.7793 | 123.6511 | 123.587 | 123.5321 | 123.5321 | -123.6649 | -123.6008 | 123.555 | 123.7244 | 60.1318 | 60.1135
276.4844 | 123.7793 | -60.2234 | 63.2538 | 0.079586 | 0.00071953 | 0.059926 | 0.066212 | -0.0026019 | 0.0067048 | -0.020992 | 0.10011 | 0.0044314 | 0.053935 | 0.051239 | -0.017904 | 0.0095709 | 0.0089575 | -0.091553 | 63.2309 | -60.4202 | 63.2904 | -60.26 | -60.5896 | -0.086975 | -0.32959 | 63.208 | -60.3424 | 63.4781 | -60.2188 | -60.3378 | -60.1776 | -0.19684 | -0.022888 | 0.036621 | -0.036621 | 60.1364 | -0.36621 | 60.3333 | -0.16937 | -0.11902 | -0.045776 | 0.2243 | 0.004578 | 0.045777 | -0.11444 | 0.16479 | 0.004577 | 0.16022 | 123.7106 | 0.1236 | 123.8205 | 123.6511 | 123.5504 | 123.4543 | 123.4314 | -123.674 | -123.5962 | 123.5138 | 123.7015 | 60.1318 | 59.8938
277.4844 | 123.7839 | -60.2051 | 63.2767 | 0.14062 | 0.0060595 | 0.068471 | 0.064076 | -0.0015339 | -0.0082492 | 0.00037059 | 0.14589 | 0.00015838 | 0.076366 | 0.10571 | -0.015768 | 0.0085029 | 0.0046845 | -0.091553 | 63.2217 | -60.3653 | 63.3041 | -60.2234 | -60.5713 | -0.059509 | -0.07782 | 63.2721 | -60.2737 | 63.4781 | -60.2463 | -60.3607 | -60.1913 | -0.16022 | -0.054931 | 0.027466 | -0.018311 | 60.1456 | -0.36621 | 60.3058 | -0.20599 | -0.068665 | -0.004577 | 0.20142 | -0.041199 | 0.013733 | -0.15564 | 0.082398 | -0.086975 | 0.14191 | 123.6694 | 0.027466 | 123.7518 | 123.587 | 123.5458 | 123.4268 | 123.4772 | -123.642 | -123.5504 | 123.5092 | 123.6832 | 60.1135 | 60.1273
278.4844 | 123.7747 | -60.2371 | 63.2996 | 0.064327 | -0.0024855 | 0.058858 | 0.071553 | -0.0015339 | 0.010977 | 0.0046426 | 0.069594 | -0.0019776 | 0.063548 | 0.037353 | -0.013631 | 0.012775 | 0.0036165 | -0.15106 | 63.2446 | -60.3882 | 63.2904 | -60.2234 | -60.5576 | -0.068665 | -0.082397 | 63.2629 | -60.2921 | 63.4827 | -60.2463 | -60.3516 | -60.1913 | -0.15106 | -0.054932 | -0.009156 | 0.013733 | 60.1685 | -0.32043 | 60.3195 | -0.16937 | -0.054931 | -0.036622 | 0.18311 | -0.009155 | 0.045777 | -0.11444 | 0.10071 | -0.059509 | 0.1648 | 123.6786 | 0.045776 | 123.7747 | 123.6328 | 123.555 | 123.4818 | 123.5001 | -123.6877 | -123.5916 | 123.5275 | 123.7198 | 60.0861 | 60.1547
279.4844 | 123.7885 | -60.2005 | 63.2858 | 0.14062 | 0.021014 | 0.064198 | 0.075825 | 0.011284 | 0.012046 | -0.00069841 | 0.084853 | -0.0062496 | 0.073162 | 0.059784 | -0.010427 | 0.0095709 | -0.012405 | -0.1236 | 63.2538 | -60.379 | 63.3041 | -60.2051 | -60.5255 | -0.054932 | -0.082397 | 63.2721 | -60.2921 | 63.501 | -60.2371 | -60.3424 | -60.1868 | -0.17853 | -0.032044 | 0.01831 | -0.004578 | 60.1456 | -0.32501 | 60.3241 | -0.14648 | -0.091553 | -0.013733 | 0.21515 | -0.036622 | 0.013732 | -0.14191 | 0.10529 | -0.050354 | 0.17395 | 123.6832 | 0.054931 | 123.793 | 123.6328 | 123.5641 | 123.4543 | 123.4726 | -123.6649 | -123.5779 | 123.5046 | 123.7015 | 60.0769 | 60.1181
280.4844 | 123.7289 | -60.2097 | 63.3499 | 0.12536 | -0.00034947 | 0.053517 | 0.070485 | 0.0027391 | -0.0050442 | 0.01746 | 0.084853 | 0.01618 | 0.068889 | 0.024536 | -0.0029502 | 0.0052979 | -0.0038605 | -0.12817 | 63.2538 | -60.347 | 63.3682 | -60.141 | -60.498 | -0.013733 | -0.14648 | 63.3224 | -60.3012 | 63.4598 | -60.1822 | -60.2921 | -60.2005 | -0.13733 | -0.096131 | 0.01831 | 0.068665 | 60.1959 | -0.28839 | 60.3333 | -0.15106 | -0.091552 | -0.027466 | 0.10986 | 0.027466 | 0.009156 | -0.082397 | 0.10071 | 0.009155 | 0.20599 | 123.7152 | 0.11902 | 123.761 | 123.6008 | 123.6237 | 123.4634 | 123.5321 | -123.6969 | -123.6511 | 123.5779 | 123.6694 | 60.0815 | 60.0632
281.4844 | 123.7564 | -60.2417 | 63.327 | 0.079586 | -0.0035535 | 0.04604 | 0.06728 | 0.012352 | -0.0082492 | 0.0014386 | 0.039077 | 0.00015838 | 0.073162 | 0.082214 | -0.0029502 | 0.0095709 | 0.0036165 | -0.13275 | 63.2812 | -60.3882 | 63.3316 | -60.1959 | -60.5347 | -0.068665 | -0.1236 | 63.295 | -60.2966 | 63.4781 | -60.2692 | -60.3287 | -60.1913 | -0.14649 | -0.045776 | 0.004578 | 0.045776 | 60.173 | -0.29297 | 60.3195 | -0.14648 | -0.054932 | -0.032043 | 0.15106 | -0.027466 | 0.050354 | -0.086975 | 0.10529 | -0.032043 | 0.19226 | 123.7198 | 0.027466 | 123.7747 | 123.6694 | 123.5916 | 123.5229 | 123.5367 | -123.7152 | -123.6237 | 123.5733 | 123.7198 | 60.1089 | 60.1181
282.4844 | 123.7976 | -60.1913 | 63.3041 | 0.018551 | 0.012469 | 0.073811 | 0.06728 | 0.016624 | 0.0056368 | -0.023128 | 0.054336 | 0.0022944 | 0.059276 | 0.041626 | -0.0147 | 0.012775 | -0.0038605 | -0.10071 | 63.2217 | -60.3516 | 63.3087 | -60.0723 | -60.4797 | -0.09613 | -0.10071 | 63.2996 | -60.2875 | 63.5239 | -60.1776 | -60.3104 | -60.1547 | -0.16022 | -0.082397 | 0.004578 | 0.11902 | 60.0952 | -0.28839 | 60.2554 | -0.12817 | -0.096131 | -0.004577 | 0.21973 | 0.013733 | 0.036621 | -0.11902 | 0.13275 | -0.022888 | 0.27923 | 123.6603 | 0.10986 | 123.8113 | 123.5733 | 123.587 | 123.4131 | 123.4909 | -123.6557 | -123.5916 | 123.5001 | 123.7152 | 60.0906 | 60.0906
283.4844 | 123.7518 | -60.2005 | 63.3179 | -0.027225 | 0.0039235 | 0.058858 | 0.068349 | -0.0047379 | -0.0039762 | 0.0099836 | 0.023818 | 0.0033634 | 0.064617 | 0.060852 | -0.0147 | 0.014911 | 0.010025 | -0.11902 | 63.2721 | -60.3561 | 63.3087 | -60.1959 | -60.5347 | -0.086975 | -0.13275 | 63.3041 | -60.2737 | 63.4918 | -60.2463 | -60.3424 | -60.1913 | -0.15564 | -0.045776 | -0.009155 | 0.004577 | 60.1135 | -0.33417 | 60.2692 | -0.17853 | -0.073243 | -0.013733 | 0.17395 | -0.045777 | 0.009155 | -0.14191 | 0.082398 | -0.068664 | 0.16022 | 123.6649 | 0.027466 | 123.7656 | 123.6282 | 123.5779 | 123.4726 | 123.5046 | -123.674 | -123.5916 | 123.5092 | 123.6923 | 60.0815 | 60.0677
284.4844 | 123.7701 | -60.2097 | 63.2996 | 0.1101 | 0.0028555 | 0.060994 | 0.072621 | -0.011147 | 0.0056368 | -0.0028344 | 0.039077 | -0.010523 | 0.059276 | 0.081146 | -0.0018822 | 0.012775 | -0.033768 | -0.11444 | 63.2812 | -60.3424 | 63.3179 | -60.2142 | -60.5484 | -0.082397 | -0.15106 | 63.295 | -60.2875 | 63.501 | -60.228 | -60.3378 | -60.1639 | -0.13275 | -0.018311 | 0.01831 | -0.004577 | 60.1273 | -0.33874 | 60.26 | -0.20599 | -0.07782 | -0.004578 | 0.20142 | -0.01831 | 0.045777 | -0.12817 | 0.1236 | -0.050354 | 0.12817 | 123.6603 | 0.05951 | 123.7885 | 123.6237 | 123.5825 | 123.4909 | 123.5046 | -123.642 | -123.587 | 123.5275 | 123.7106 | 60.0952 | 60.0586
285.4844 | 123.8297 | -60.1593 | 63.327 | 0.064327 | -0.00034947 | 0.064198 | 0.071553 | 0.015556 | -0.019998 | 0.01212 | 0.16115 | -0.0073186 | 0.067821 | 0.07901 | -0.0093592 | -0.0021781 | -0.01561 | -0.041199 | 63.295 | -60.2966 | 63.3362 | -60.1639 | -60.5347 | -0.10529 | -0.036621 | 63.3362 | -60.2234 | 63.5742 | -60.1273 | -60.2325 | -60.0906 | -0.13733 | -0.032043 | 0.009156 | -0.004577 | 60.054 | -0.37537 | 60.1913 | -0.23804 | -0.064087 | 0.009156 | 0.24719 | 0.032044 | 0.068665 | -0.073242 | 0.13275 | -0.009155 | 0.13275 | 123.6328 | 0.096131 | 123.7976 | 123.5916 | 123.5596 | 123.4543 | 123.4955 | -123.6237 | -123.5504 | 123.4955 | 123.7335 | 60.1181 | 60.1227
286.4844 | 123.7518 | -60.1868 | 63.3499 | 0.064327 | 0.0071275 | 0.064198 | 0.064076 | 0.0091481 | -0.0061122 | 0.0046426 | -0.0066996 | -0.0030456 | 0.07957 | 0.030945 | -0.0061552 | 0.01598 | 0.0046845 | -0.13733 | 63.2858 | -60.347 | 63.3636 | -60.1547 | -60.498 | -0.082397 | -0.25635 | 63.3224 | -60.2646 | 63.501 | -60.2325 | -60.3287 | -60.1685 | -0.16022 | -0.064087 | 0.013732 | 0.032044 | 60.1044 | -0.31128 | 60.2646 | -0.15106 | -0.077819 | -0.027466 | 0.15106 | -0.045776 | 0.018311 | -0.14191 | 0.09613 | -0.064087 | 0.19226 | 123.7106 | 0.032043 | 123.7656 | 123.6328 | 123.587 | 123.4726 | 123.5092 | -123.6969 | -123.6145 | 123.5504 | 123.6877 | 60.0494 | 59.9304
287.4844 | 123.7701 | -60.2142 | 63.3408 | 0.12536 | 0.0017875 | 0.07488 | 0.075825 | -0.0068739 | 0.0056368 | -0.018856 | -0.037217 | 0.0044314 | 0.075298 | 0.025604 | -0.010427 | 0.0042299 | -0.019882 | -0.13733 | 63.2904 | -60.3653 | 63.3545 | -60.1501 | -60.4889 | -0.086975 | -0.26093 | 63.3041 | -60.26 | 63.4964 | -60.2371 | -60.3561 | -60.173 | -0.15106 | -0.050354 | 0.013733 | 0.064087 | 60.1273 | -0.27466 | 60.2783 | -0.1236 | -0.045777 | -0.036621 | 0.15564 | -0.022889 | 0.041198 | -0.14191 | 0.086975 | -0.09613 | 0.21515 | 123.7198 | 0.022888 | 123.7564 | 123.6557 | 123.5641 | 123.5046 | 123.5184 | -123.7061 | -123.6008 | 123.5687 | 123.7106 | 60.0769 | 59.9533
288.4844 | 123.7839 | -60.1868 | 63.3224 | 0.0032924 | 0.0039235 | 0.06313 | 0.063008 | 0.0091481 | -0.011453 | -0.0092424 | -0.021958 | 0.0065674 | 0.06248 | 0.03949 | -0.011495 | 0.010639 | -0.02095 | -0.14648 | 63.2858 | -60.3333 | 63.3545 | -60.1547 | -60.4935 | -0.11444 | -0.27924 | 63.2904 | -60.2554 | 63.4964 | -60.2234 | -60.3287 | -60.1547 | -0.14648 | -0.036621 | 0.032043 | 0.032044 | 60.0723 | -0.3067 | 60.2188 | -0.16022 | -0.068664 | -0.032044 | 0.17395 | -0.036621 | 0.032044 | -0.14191 | 0.10071 | -0.073242 | 0.17853 | 123.6877 | 0.032043 | 123.7518 | 123.6191 | 123.5458 | 123.4726 | 123.4772 | -123.6557 | -123.5779 | 123.5413 | 123.6832 | 60.0403 | 59.9075
289.4844 | 123.8022 | -60.173 | 63.3453 | 0.018551 | 0.014605 | 0.068471 | 0.07903 | -0.0068739 | -0.011453 | -0.0071064 | 0.023818 | -0.0030456 | 0.056072 | 0.036285 | -0.0072232 | 0.0085029 | -0.016678 | -0.13733 | 63.2996 | -60.3378 | 63.2904 | -60.0906 | -60.379 | -0.17395 | -0.28381 | 63.3224 | -60.2417 | 63.5468 | -60.141 | -60.2875 | -60.1181 | -0.16479 | -0.045776 | -0.054932 | 0.082398 | 59.9991 | -0.20599 | 60.1639 | -0.041198 | -0.068664 | -0.022888 | 0.20142 | 0.032044 | 0.054932 | -0.11444 | 0.1236 | -0.045777 | 0.24719 | 123.6282 | 0.10071 | 123.7885 | 123.6374 | 123.5641 | 123.4726 | 123.4955 | -123.6832 | -123.587 | 123.4634 | 123.7198 | 60.0357 | 59.8892
290.4844 | 123.8113 | -60.141 | 63.3545 | 0.15588 | 0.0081955 | 0.06313 | 0.075825 | -0.011147 | 0.0056368 | 0.0035746 | 0.14589 | 0.0022944 | 0.053935 | 0.069397 | -0.012563 | 0.0063669 | -0.024155 | -0.054932 | 63.3408 | -60.2921 | 63.3499 | -60.1822 | -60.4935 | -0.14191 | -0.22888 | 63.382 | -60.2051 | 63.5788 | -60.0998 | -60.2142 | -60.0998 | -0.15106 | -0.013733 | -0.004577 | -0.041199 | 59.9991 | -0.35248 | 60.1501 | -0.20142 | -0.064087 | 0.027466 | 0.2243 | 0.041199 | 0.041199 | -0.073242 | 0.10529 | -0.009155 | 0.10986 | 123.642 | 0.10529 | 123.7839 | 123.6328 | 123.587 | 123.4818 | 123.5229 | -123.6465 | -123.5596 | 123.4909 | 123.7198 | 60.0861 | 59.9121
291.4844 | 123.7518 | -60.1685 | 63.3545 | 0.1101 | 0.0028555 | 0.059926 | 0.068349 | -0.0079419 | -0.00077219 | 0.0046426 | 0.054336 | 0.00015838 | 0.069957 | 0.058716 | -0.02004 | 0.014911 | 0.0046845 | -0.19684 | 63.3224 | -60.3104 | 63.4186 | -60.0906 | -60.4431 | -0.13733 | -0.4303 | 63.3362 | -60.2188 | 63.5101 | -60.2005 | -60.2966 | -60.1456 | -0.14191 | -0.032043 | 0.064087 | 0.07782 | 60.0311 | -0.27466 | 60.173 | -0.13275 | -0.050354 | -0.01831 | 0.15564 | -0.032043 | 0.022888 | -0.12817 | 0.073242 | -0.07782 | 0.21973 | 123.7289 | 0.018311 | 123.7289 | 123.6328 | 123.555 | 123.4909 | 123.5046 | -123.6649 | -123.5733 | 123.587 | 123.6786 | 59.9716 | 59.7382
292.4844 | 123.7564 | -60.1593 | 63.3316 | 0.0032924 | 0.011401 | 0.055654 | 0.077962 | -0.0047379 | -0.00077219 | 0.0046426 | -0.0066996 | 0.0065674 | 0.067821 | 0.056579 | -0.013631 | 0.010639 | -0.0092005 | -0.19684 | 63.3133 | -60.3287 | 63.3865 | -60.141 | -60.4889 | -0.19684 | -0.40283 | 63.3591 | -60.2097 | 63.5651 | -60.1639 | -60.2737 | -60.1089 | -0.16937 | -0.018311 | 0.054932 | 0.018311 | 59.9625 | -0.32959 | 60.1318 | -0.16022 | -0.050354 | 0.027466 | 0.23346 | -0.004577 | 0.050354 | -0.11444 | 0.10071 | -0.064087 | 0.18768 | 123.7152 | 0.045777 | 123.7747 | 123.642 | 123.5687 | 123.4726 | 123.5184 | -123.6603 | -123.5413 | 123.5458 | 123.7244 | 59.9625 | 59.7565
293.4844 | 123.7564 | -60.1501 | 63.3865 | -0.057743 | -0.0067575 | 0.062062 | 0.066212 | 0.018761 | -0.0039762 | -0.0092424 | 0.054336 | 0.0044314 | 0.07423 | 0.062988 | -0.0082912 | 0.0020939 | -0.011337 | -0.21515 | 63.3545 | -60.2875 | 63.4232 | -60.0998 | -60.4431 | -0.17853 | -0.49896 | 63.3636 | -60.2097 | 63.5468 | -60.1685 | -60.2692 | -60.1089 | -0.13733 | -0.032044 | 0.036621 | 0.050354 | 59.9716 | -0.29297 | 60.1089 | -0.15564 | -0.05951 | -0.022889 | 0.16022 | -0.018311 | 0.041198 | -0.11902 | 0.10071 | -0.059509 | 0.18768 | 123.7106 | 0.041199 | 123.7564 | 123.642 | 123.5733 | 123.5046 | 123.5138 | -123.674 | -123.5962 | 123.5733 | 123.6969 | 59.935 | 59.6512
294.4844 | 123.7427 | -60.1273 | 63.4094 | 0.1101 | -0.0014175 | 0.064198 | 0.070485 | 0.0080791 | 0.0056368 | -0.010311 | 0.039077 | -0.00090962 | 0.061412 | 0.03949 | 0.0023898 | 0.010639 | -0.02095 | -0.24719 | 63.3316 | -60.2737 | 63.414 | -60.0952 | -60.434 | -0.20599 | -0.55389 | 63.3774 | -60.2142 | 63.5605 | -60.1685 | -60.2692 | -60.0998 | -0.14649 | -0.07782 | 0.004577 | 0.032043 | 59.9213 | -0.3067 | 60.0677 | -0.16022 | -0.086975 | -0.032044 | 0.15106 | -0.041199 | 0.027466 | -0.14191 | 0.11444 | -0.054932 | 0.17853 | 123.6877 | 0.045776 | 123.7747 | 123.6053 | 123.5916 | 123.4589 | 123.5046 | -123.6832 | -123.6237 | 123.5413 | 123.6877 | 59.8801 | 59.5734
295.4844 | 123.7564 | -60.1273 | 63.4232 | 0.15588 | 0.00071953 | 0.064198 | 0.077962 | -0.0068739 | -0.013589 | -0.0071064 | 0.32899 | -0.00090962 | 0.063548 | 0.024536 | -0.013631 | 0.012775 | 0.0036165 | -0.15106 | 63.4094 | -60.2371 | 63.4232 | -60.0998 | -60.4294 | -0.23804 | -0.46692 | 63.4048 | -60.1547 | 63.5147 | -60.1639 | -60.1868 | -60.054 | -0.10986 | -0.013733 | 0 | 0.027466 | 59.8892 | -0.30212 | 59.9991 | -0.19226 | -0.027466 | -0.018311 | 0.091552 | -0.036621 | 0.073242 | -0.05951 | 0.10071 | -0.032044 | 0.13733 | 123.6603 | -0.009155 | 123.6694 | 123.6465 | 123.5596 | 123.5367 | 123.5321 | -123.6603 | -123.5779 | 123.5504 | 123.642 | 59.9762 | 59.6603
296.4844 | 123.7839 | -60.0861 | 63.414 | -0.088261 | -0.00034947 | 0.065267 | 0.066212 | -0.0004649 | 0.0067048 | 0.0078466 | -0.052476 | 0.00015838 | 0.064617 | 0.030945 | -0.0147 | 0.017048 | 0.0025485 | -0.29297 | 63.3591 | -60.2646 | 63.5056 | -59.9808 | -60.4797 | -0.27466 | -0.6134 | 63.4094 | -60.1593 | 63.6429 | -60.054 | -60.2142 | -60.0357 | -0.17853 | -0.054931 | 0.091553 | 0.10529 | 59.8114 | -0.39368 | 59.9899 | -0.21515 | -0.073242 | -0.004577 | 0.22888 | 0.032044 | 0.050354 | -0.12817 | 0.1236 | -0.054931 | 0.28381 | 123.7701 | 0.10529 | 123.8022 | 123.6237 | 123.5687 | 123.4451 | 123.4955 | -123.6786 | -123.5733 | 123.5916 | 123.7289 | 59.7931 | 59.4727
297.4844 | 123.7518 | -60.0861 | 63.446 | 0.049069 | 0.0060595 | 0.05779 | 0.087575 | -0.0058059 | -0.010385 | 0.016392 | -0.021958 | -0.0019776 | 0.07423 | 0.069397 | -0.0082912 | 0.0085029 | 0.015366 | -0.34332 | 63.3682 | -60.2142 | 63.4323 | -60.0952 | -60.4156 | -0.35248 | -0.737 | 63.4277 | -60.173 | 63.5925 | -60.1089 | -60.2188 | -60.0586 | -0.12817 | -0.07782 | -0.013733 | -0.009155 | 59.7336 | -0.32959 | 59.8618 | -0.20142 | -0.086975 | -0.018311 | 0.14648 | -0.022888 | 0.027466 | -0.13275 | 0.11444 | -0.045776 | 0.11902 | 123.6465 | 0.064087 | 123.7656 | 123.5825 | 123.6008 | 123.4543 | 123.5138 | -123.6603 | -123.6191 | 123.5184 | 123.6786 | 59.7427 | 59.3491
298.4844 | 123.761 | -60.0677 | 63.4277 | 0.03381 | 0.0081955 | 0.049245 | 0.071553 | 0.014488 | 0.0088408 | -0.0028344 | -0.037217 | -0.0030456 | 0.071025 | 0.042694 | 0.00025378 | 0.0095709 | -0.0081325 | -0.37994 | 63.3865 | -60.2142 | 63.446 | -60.0769 | -60.434 | -0.3891 | -0.84228 | 63.414 | -60.1593 | 63.6108 | -60.0769 | -60.1913 | -60.0357 | -0.14648 | -0.041198 | 0.018311 | -0.009155 | 59.6786 | -0.36621 | 59.8251 | -0.21973 | -0.091553 | -0.013733 | 0.18311 | -0.009155 | 0.032043 | -0.1236 | 0.1236 | -0.032043 | 0.13733 | 123.6603 | 0.082398 | 123.7701 | 123.6008 | 123.5733 | 123.4543 | 123.4818 | -123.642 | -123.587 | 123.5138 | 123.6786 | 59.6878 | 59.2255
299.4844 | 123.7839 | -60.0769 | 63.4415 | -0.042484 | 0.011401 | 0.060994 | 0.064076 | -0.017555 | -0.0061122 | -0.020992 | 0.13063 | 0.0044314 | 0.061412 | 0.053375 | -0.0029502 | 0.011707 | -0.0059965 | -0.45319 | 63.3911 | -60.2051 | 63.4552 | -60.0449 | -60.4019 | -0.44861 | -0.95215 | 63.414 | -60.1318 | 63.6429 | -60.054 | -60.1776 | -60.0174 | -0.12817 | -0.050354 | 0.013733 | 0.032043 | 59.6283 | -0.32501 | 59.7565 | -0.19684 | -0.054932 | -0.027466 | 0.20142 | 0.022888 | 0.059509 | -0.10071 | 0.11444 | -0.045776 | 0.16022 | 123.6603 | 0.07782 | 123.7747 | 123.5962 | 123.5458 | 123.468 | 123.4909 | -123.6465 | -123.5733 | 123.5321 | 123.7198 | 59.6237 | 59.1248
300.4844 | 123.8388 | -60.022 | 63.4781 | 0.094845 | 0.012469 | 0.054585 | 0.071553 | -0.0026019 | 0.0035008 | -0.0092424 | 0.20692 | 0.0012264 | 0.067821 | 0.065124 | -0.0050872 | 0.0074349 | -0.0017235 | -0.44403 | 63.4506 | -60.2051 | 63.4872 | -60.0311 | -60.379 | -0.48065 | -0.97961 | 63.4552 | -60.1044 | 63.707 | -59.9579 | -60.0723 | -59.9304 | -0.1831 | -0.027465 | 0.009156 | -0.009155 | 59.5413 | -0.35705 | 59.7244 | -0.17395 | -0.082397 | -0.022888 | 0.22888 | 0.064087 | 0.091553 | -0.050354 | 0.17395 | 0.032043 | 0.17395 | 123.6923 | 0.14648 | 123.8113 | 123.6557 | 123.5596 | 123.4726 | 123.4772 | -123.6832 | -123.5825 | 123.5092 | 123.7289 | 59.5779 | 59.0424
301.4844 | 123.7793 | -60.0174 | 63.5101 | -0.042484 | 0.0092645 | 0.050313 | 0.071553 | 0.0038071 | -0.0061122 | -0.0039024 | 0.084853 | 0.0076354 | 0.071025 | 0.065124 | -0.0093592 | 0.012775 | -0.0059965 | -0.58594 | 63.4506 | -60.1822 | 63.5193 | -59.9854 | -60.3287 | -0.54932 | -1.2726 | 63.4689 | -60.0998 | 63.6612 | -60.054 | -60.1776 | -60.0128 | -0.16479 | -0.059509 | 0.009155 | 0.032043 | 59.4681 | -0.31128 | 59.6329 | -0.14648 | -0.082397 | -0.041199 | 0.15106 | -0.036621 | 0.004578 | -0.16022 | 0.086975 | -0.07782 | 0.19684 | 123.7015 | 0.045776 | 123.761 | 123.6328 | 123.5687 | 123.468 | 123.4863 | -123.6923 | -123.6099 | 123.5367 | 123.6786 | 59.4315 | 58.7448
302.4844 | 123.7885 | -59.9991 | 63.5101 | -0.40869 | 0.025286 | 0.066335 | 0.068349 | -0.013283 | -0.0082492 | -0.0081744 | -0.082994 | 0.0054994 | 0.076366 | 0.082214 | -0.0040182 | 0.013843 | -0.0027915 | -0.6134 | 63.4186 | -60.2051 | 63.4964 | -59.9808 | -60.3607 | -0.71411 | -1.3687 | 63.4506 | -60.0632 | 63.7207 | -59.9854 | -60.1273 | -59.967 | -0.20599 | -0.091553 | -0.013733 | 0.01831 | 59.285 | -0.36163 | 59.491 | -0.15564 | -0.064087 | -0.059509 | 0.21057 | 0.013732 | 0.032043 | -0.12817 | 0.09613 | -0.064087 | 0.2243 | 123.7015 | 0.077819 | 123.7839 | 123.6237 | 123.5138 | 123.4177 | 123.4497 | -123.7152 | -123.5733 | 123.4955 | 123.7198 | 59.3857 | 58.6304
303.4844 | 123.7198 | -59.9945 | 63.588 | 0.17114 | -0.0035535 | 0.04604 | 0.066212 | 0.012352 | 0.0056368 | -0.0060384 | -0.052476 | 0.0054994 | 0.066753 | 0.091827 | 0.00025378 | 0.017048 | -0.011337 | -0.72327 | 63.5513 | -60.1547 | 63.7024 | -59.7748 | -60.1593 | -0.56763 | -1.6022 | 63.588 | -60.0632 | 63.652 | -60.0128 | -60.173 | -59.9854 | -0.16022 | -0.036621 | 0.11444 | 0.21973 | 59.4269 | -0.16479 | 59.5871 | -0.004578 | -0.068664 | 0 | 0.064087 | -0.01831 | 0.009155 | -0.17853 | 0.077819 | -0.10986 | 0.37994 | 123.8571 | 0.050354 | 123.7152 | 123.7061 | 123.6511 | 123.5458 | 123.5825 | -123.7427 | -123.6511 | 123.6969 | 123.6465 | 59.2712 | 58.3923
304.4844 | 123.7518 | -59.9625 | 63.5239 | 0.15588 | 0.0049915 | 0.052449 | 0.06728 | -0.023964 | -0.016794 | -0.0092424 | 0.10011 | -0.00090962 | 0.049663 | 0.062988 | 0.0013218 | 0.018116 | -0.017746 | -0.86517 | 63.4964 | -60.1181 | 63.5422 | -59.9304 | -60.2829 | -0.83313 | -1.7303 | 63.5101 | -60.0403 | 63.7024 | -59.9854 | -60.0998 | -59.9579 | -0.15564 | -0.027466 | 0.01831 | 0.032043 | 59.1293 | -0.32044 | 59.285 | -0.1648 | -0.07782 | -0.013733 | 0.17853 | -0.022889 | 0.004577 | -0.13733 | 0.082397 | -0.059509 | 0.18768 | 123.6603 | 0.054931 | 123.7427 | 123.6145 | 123.5504 | 123.4589 | 123.4726 | -123.642 | -123.5641 | 123.5046 | 123.6649 | 59.0973 | 58.2321
305.4844 | 123.7701 | -59.935 | 63.588 | 0.17114 | -0.0088935 | 0.050313 | 0.06728 | -0.0079419 | 0.0013638 | -0.0071064 | 0.14589 | -0.0041136 | 0.078502 | 0.052307 | -0.0093592 | 0.017048 | -0.019882 | -0.95673 | 63.5559 | -60.0998 | 63.6017 | -59.8938 | -60.2783 | -0.88806 | -1.8814 | 63.5696 | -60.0174 | 63.7619 | -59.8984 | -60.0266 | -59.8709 | -0.16479 | -0.032044 | 0.013733 | 0.041199 | 59.0469 | -0.34332 | 59.2117 | -0.17853 | -0.082397 | -0.018311 | 0.17395 | 0.036622 | 0.064087 | -0.091552 | 0.14648 | -0.009155 | 0.20599 | 123.7015 | 0.11902 | 123.7793 | 123.6557 | 123.587 | 123.4909 | 123.5046 | -123.6877 | -123.6053 | 123.5367 | 123.6969 | 58.9783 | 58.0536
306.4844 | 123.7564 | -59.9533 | 63.5559 | 0.0032924 | 0.00071953 | 0.055654 | 0.077962 | -0.0026019 | -0.0071802 | -0.02206 | 0.084853 | -0.0030456 | 0.066753 | 0.06192 | -0.0082912 | 0.0074349 | 0.0014805 | -1.1078 | 63.533 | -60.0677 | 63.5696 | -59.9213 | -60.2737 | -1.0071 | -2.1423 | 63.5605 | -60.0082 | 63.7482 | -59.9167 | -60.0769 | -59.8984 | -0.11444 | -0.022888 | 0.013733 | 0.032043 | 58.9462 | -0.32044 | 59.0607 | -0.20599 | -0.054932 | 0.004578 | 0.19226 | 0.036621 | 0.054932 | -0.1236 | 0.10986 | -0.068664 | 0.14648 | 123.6374 | 0.091553 | 123.7564 | 123.6008 | 123.5687 | 123.4863 | 123.5138 | -123.6237 | -123.5641 | 123.5229 | 123.7015 | 58.8455 | 57.811
307.4844 | 123.7656 | -59.935 | 63.5834 | 0.03381 | 0.0081955 | 0.073811 | 0.073689 | 0.010216 | 0.00029581 | -0.017787 | 0.10011 | 0.0022944 | 0.076366 | 0.052307 | -0.0040182 | 0.013843 | -0.0092005 | -1.1993 | 63.5513 | -60.0632 | 63.588 | -59.8938 | -60.26 | -1.0895 | -2.33 | 63.5651 | -60.0037 | 63.7894 | -59.903 | -60.0494 | -59.8801 | -0.12817 | -0.032043 | 0.004578 | 0.041199 | 58.8455 | -0.32501 | 58.9737 | -0.19684 | -0.068664 | -0.018311 | 0.20599 | 0.032044 | 0.054932 | -0.11444 | 0.1236 | -0.045776 | 0.16937 | 123.6511 | 0.10071 | 123.793 | 123.6145 | 123.5687 | 123.4863 | 123.5001 | -123.6465 | -123.587 | 123.523 | 123.7244 | 58.7357 | 57.605
308.4844 | 123.6923 | -59.9167 | 63.7024 | 0.094845 | -0.0024855 | 0.049245 | 0.071553 | 0.012352 | -0.0039762 | -0.0081744 | 0.10011 | 0.012976 | 0.076366 | 0.076874 | -0.0050872 | 0.0074349 | -0.013474 | -1.3412 | 63.6475 | -60.0769 | 63.7756 | -59.7244 | -60.0815 | -1.0208 | -2.6001 | 63.6795 | -59.9533 | 63.7253 | -59.9396 | -60.0769 | -59.935 | -0.16022 | -0.054932 | 0.073242 | 0.19226 | 58.8959 | -0.16479 | 59.0561 | -0.004578 | -0.036621 | -0.022889 | 0.022888 | -0.022888 | -0.018311 | -0.16022 | 0.01831 | -0.1236 | 0.35248 | 123.8525 | 0.013733 | 123.6786 | 123.7244 | 123.6328 | 123.5641 | 123.5962 | -123.7793 | -123.6557 | 123.6923 | 123.642 | 58.5754 | 57.3166
309.4844 | 123.7885 | -59.8892 | 63.6108 | 0.079586 | 0.015673 | 0.059926 | 0.077962 | -0.0026019 | 0.0024328 | 0.00037059 | -0.052476 | 0.0076354 | 0.064617 | 0.060852 | -0.0093592 | 0.0074349 | 0.0078895 | -1.5015 | 63.5742 | -60.0449 | 63.6566 | -59.8297 | -60.1913 | -1.2634 | -2.7237 | 63.6154 | -59.9304 | 63.826 | -59.8618 | -60.0037 | -59.8343 | -0.15564 | -0.036621 | 0.045776 | 0.059509 | 58.6258 | -0.30212 | 58.7814 | -0.14648 | -0.041199 | 0.004577 | 0.21515 | 0.027466 | 0.054931 | -0.11444 | 0.09613 | -0.073242 | 0.21515 | 123.7015 | 0.068665 | 123.7564 | 123.6191 | 123.5458 | 123.4634 | 123.5046 | -123.6557 | -123.5413 | 123.5458 | 123.7152 | 58.3878 | 57.1655
310.4844 | 123.7976 | -59.8251 | 63.6932 | 0.064327 | 0.0060595 | 0.056722 | 0.071553 | 0.0027391 | -0.0071802 | -0.0049704 | 0.37477 | 0.0044314 | 0.077434 | 0.057647 | -0.026449 | 0.017048 | -0.0038605 | -1.5747 | 63.6383 | -59.9762 | 63.6658 | -59.7977 | -60.1776 | -1.3229 | -3.1723 | 63.6703 | -59.9304 | 63.8168 | -59.7382 | -59.8892 | -59.7839 | -0.15106 | -0.054931 | -0.027466 | 0.027466 | 58.5022 | -0.35248 | 58.6533 | -0.20142 | -0.10529 | -0.022888 | 0.1236 | 0.086975 | 0.041198 | -0.064087 | 0.14648 | 0.041199 | 0.17853 | 123.642 | 0.19226 | 123.7473 | 123.6145 | 123.6008 | 123.4634 | 123.4955 | -123.6694 | -123.6237 | 123.4909 | 123.642 | 58.2504 | 56.6528
311.4844 | 123.7885 | -59.8389 | 63.6841 | 0.049069 | -0.00034947 | 0.05779 | 0.076894 | 0.0016711 | 0.0045688 | 0.0014386 | 0.11537 | 0.0044314 | 0.073162 | 0.043762 | -0.0029502 | 0.0052979 | -0.00065554 | -1.8311 | 63.62 | -60.0037 | 63.6978 | -59.7748 | -60.141 | -1.3962 | -3.2639 | 63.6566 | -59.9396 | 63.8306 | -59.8251 | -59.9854 | -59.8068 | -0.16479 | -0.064087 | 0.013733 | 0.064087 | 58.4427 | -0.30212 | 58.6075 | -0.13733 | -0.10071 | -0.027466 | 0.14648 | 0.013733 | 0.032043 | -0.14648 | 0.13275 | -0.045777 | 0.22888 | 123.7015 | 0.11444 | 123.7701 | 123.6237 | 123.5962 | 123.4589 | 123.4955 | -123.6877 | -123.6237 | 123.5367 | 123.6694 | 58.0078 | 56.575
312.4844 | 123.8022 | -59.7977 | 63.6932 | -0.22559 | 0.015673 | 0.056722 | 0.081166 | -0.0068739 | -0.0039762 | -0.00069841 | 0.023818 | 0.00015838 | 0.053935 | 0.051239 | -0.018972 | 0.013843 | -0.0027915 | -1.9272 | 63.62 | -59.9899 | 63.7024 | -59.7473 | -60.1776 | -1.5289 | -3.4882 | 63.6749 | -59.8709 | 63.9084 | -59.7748 | -59.9396 | -59.7656 | -0.19226 | -0.073242 | 0.009156 | 0.050354 | 58.2687 | -0.37994 | 58.461 | -0.18768 | -0.073243 | -0.01831 | 0.21515 | 0.022888 | 0.032043 | -0.14191 | 0.10529 | -0.068664 | 0.24261 | 123.6923 | 0.096131 | 123.7793 | 123.6099 | 123.5458 | 123.4177 | 123.4726 | -123.6832 | -123.5641 | 123.5001 | 123.7061 | 57.8705 | 56.3095
313.4844 | 123.6649 | -59.7977 | 63.8077 | 0.14062 | -0.0014175 | 0.055654 | 0.080098 | 0.014488 | 0.0024328 | -0.0092424 | 0.16115 | -0.0030456 | 0.056072 | 0.059784 | 0.0023898 | 0.0020939 | 0.017502 | -2.1286 | 63.7207 | -59.9167 | 63.8443 | -59.6191 | -59.9991 | -1.474 | -3.8269 | 63.7619 | -59.848 | 63.8947 | -59.7794 | -59.9945 | -59.8297 | -0.11902 | -0.086975 | 0.036621 | 0.17853 | 58.3237 | -0.20142 | 58.4427 | -0.082397 | -0.050354 | -0.045776 | 0.086975 | 0.01831 | -0.032044 | -0.19684 | 0.01831 | -0.14648 | 0.29755 | 123.761 | 0.068664 | 123.7427 | 123.6374 | 123.6099 | 123.5184 | 123.5596 | -123.7244 | -123.6557 | 123.642 | 123.6923 | 57.6691 | 55.9708
314.4844 | 123.7564 | -59.7839 | 63.7573 | -0.011967 | -0.0024855 | 0.062062 | 0.076894 | 0.0027391 | -0.011453 | -0.011379 | 0.16115 | 0.0097714 | 0.064617 | 0.054443 | -0.016836 | 0.013843 | 0.0057535 | -2.4216 | 63.7253 | -59.935 | 63.7894 | -59.6558 | -60.0586 | -1.6159 | -4.1519 | 63.7344 | -59.8526 | 63.8809 | -59.7565 | -59.9075 | -59.7519 | -0.15106 | -0.032043 | 0.032044 | 0.12817 | 58.168 | -0.27466 | 58.3191 | -0.1236 | -0.068664 | -0.022888 | 0.1236 | 0.027466 | 0.032044 | -0.1236 | 0.10071 | -0.054932 | 0.27924 | 123.7244 | 0.09613 | 123.7335 | 123.6603 | 123.587 | 123.5092 | 123.5184 | -123.6923 | -123.6099 | 123.5733 | 123.6649 | 57.3624 | 55.632
315.4844 | 123.793 | -59.7336 | 63.8031 | 0.12536 | 0.0071275 | 0.071675 | 0.080098 | 0.0048751 | 0.0067048 | 0.011052 | 0.11537 | -0.0073186 | 0.07423 | 0.057647 | -0.0072232 | 0.012775 | -0.0027915 | -2.6505 | 63.7482 | -59.903 | 63.7802 | -59.6466 | -60.0586 | -1.7303 | -4.3762 | 63.7711 | -59.8022 | 63.9771 | -59.6649 | -59.8297 | -59.6832 | -0.16937 | -0.054932 | -0.022889 | 0.086976 | 58.0032 | -0.32501 | 58.1726 | -0.15564 | -0.068664 | -0.032044 | 0.17395 | 0.068665 | 0.050354 | -0.09613 | 0.11902 | -0.027466 | 0.25635 | 123.6832 | 0.13733 | 123.7793 | 123.6511 | 123.5733 | 123.4818 | 123.5046 | -123.7061 | -123.6053 | 123.5138 | 123.7106 | 57.0831 | 55.3574
316.4844 | 123.7656 | -59.729 | 63.7848 | -0.011967 | 0.0092645 | 0.05779 | 0.06728 | 0.01342 | 0.0035008 | -0.010311 | 0.10011 | -0.0051816 | 0.051799 | 0.074737 | -0.015768 | 0.014911 | -0.00065554 | -2.9114 | 63.7436 | -59.8755 | 63.8031 | -59.6603 | -60.0403 | -1.8723 | -4.7928 | 63.7573 | -59.7885 | 63.9771 | -59.7061 | -59.8572 | -59.697 | -0.14648 | -0.041199 | 0.018311 | 0.068665 | 57.8568 | -0.31128 | 58.0032 | -0.1648 | -0.059509 | -0.027466 | 0.19226 | 0.022888 | 0.032044 | -0.12817 | 0.091553 | -0.068665 | 0.21515 | 123.6786 | 0.082397 | 123.7656 | 123.6191 | 123.5458 | 123.4726 | 123.4863 | -123.6603 | -123.5733 | 123.5321 | 123.7061 | 56.8176 | 54.9362
317.4844 | 123.761 | -59.7015 | 63.7939 | 0.12536 | 0.010333 | 0.05779 | 0.068349 | 0.0048751 | 0.0035008 | -0.019924 | 0.023818 | 0.0087034 | 0.073162 | 0.069397 | -0.0072232 | 0.010639 | -0.014542 | -3.154 | 63.7756 | -59.8618 | 63.7985 | -59.642 | -60.0311 | -1.9821 | -5.127 | 63.7939 | -59.7931 | 63.9862 | -59.6695 | -59.8434 | -59.6466 | -0.16022 | -0.01831 | 0.004578 | 0.059509 | 57.7194 | -0.32959 | 57.8796 | -0.16937 | -0.091553 | 0 | 0.19226 | 0.032043 | 0.054932 | -0.14191 | 0.14648 | -0.050354 | 0.21973 | 123.6603 | 0.1236 | 123.7793 | 123.6374 | 123.587 | 123.4772 | 123.4955 | -123.6557 | -123.587 | 123.5001 | 123.6877 | 56.5475 | 54.5746
318.4844 | 123.7885 | -59.6741 | 63.8718 | 0.1101 | -0.022779 | 0.044972 | 0.073689 | -0.0036699 | 0.0035008 | -0.0081744 | 0.084853 | -0.00090962 | 0.069957 | 0.030945 | -0.024313 | 0.014911 | -0.013474 | -2.9892 | 63.8901 | -59.7794 | 63.8992 | -59.5505 | -60.0266 | -2.0691 | -5.3879 | 63.8397 | -59.7473 | 64.0366 | -59.5596 | -59.729 | -59.6146 | -0.10529 | 0.018311 | 0.027466 | 0.1236 | 57.605 | -0.35248 | 57.7103 | -0.24719 | -0.073242 | -0.032043 | 0.16479 | 0.11444 | 0.059509 | -0.054932 | 0.13275 | 0.01831 | 0.22888 | 123.6786 | 0.18768 | 123.7839 | 123.6694 | 123.587 | 123.5641 | 123.5138 | -123.6511 | -123.6191 | 123.5733 | 123.7106 | 56.6849 | 54.2862
319.4844 | 123.7564 | -59.6558 | 63.8763 | 0.018551 | -0.0078255 | 0.059926 | 0.074757 | 0.0091481 | 0.00029581 | 0.01212 | 0.11537 | 0.015112 | 0.068889 | 0.048034 | -0.012563 | 0.0042299 | -0.011337 | -3.6942 | 63.8214 | -59.8114 | 63.8947 | -59.5184 | -59.9396 | -2.1378 | -5.9052 | 63.8489 | -59.7198 | 64.0182 | -59.6329 | -59.8022 | -59.6146 | -0.15564 | -0.054932 | 0.01831 | 0.13733 | 57.518 | -0.28381 | 57.6736 | -0.12817 | -0.064087 | -0.027466 | 0.14191 | 0.022888 | 0.041199 | -0.14648 | 0.10529 | -0.082397 | 0.29297 | 123.7061 | 0.086975 | 123.7381 | 123.6328 | 123.5687 | 123.4772 | 123.5046 | -123.6877 | -123.5962 | 123.5504 | 123.674 | 55.9616 | 53.7506
320.4844 | 123.8251 | -59.6054 | 63.8901 | 0.079586 | -0.0014175 | 0.060994 | 0.073689 | 0.0038071 | -0.0018402 | -0.012447 | 0.19167 | -0.0041136 | 0.068889 | 0.045898 | -0.012563 | 0.012775 | -0.0027915 | -3.891 | 63.8718 | -59.7748 | 63.8901 | -59.5413 | -59.9487 | -2.2476 | -6.102 | 63.8992 | -59.7015 | 64.1098 | -59.491 | -59.6603 | -59.5367 | -0.16937 | -0.018311 | 0 | 0.064087 | 57.3578 | -0.34332 | 57.5272 | -0.17395 | -0.09613 | 0.009155 | 0.21973 | 0.11444 | 0.068665 | -0.054931 | 0.16479 | 0.041199 | 0.23346 | 123.6649 | 0.21057 | 123.8113 | 123.6465 | 123.6008 | 123.4772 | 123.5046 | -123.6649 | -123.5916 | 123.4955 | 123.7152 | 55.7144 | 53.5034
321.4844 | 123.7381 | -59.6375 | 63.9359 | 0.15588 | 0.00071953 | 0.05779 | 0.074757 | 0.0059431 | -0.00077219 | -0.0028344 | 0.084853 | 0.0033634 | 0.05714 | 0.069397 | -0.0147 | 0.012775 | -0.013474 | -4.2389 | 63.8901 | -59.7702 | 63.945 | -59.4589 | -59.903 | -2.2888 | -6.8253 | 63.9038 | -59.6878 | 64.0457 | -59.5871 | -59.7519 | -59.6008 | -0.13275 | -0.045776 | 0.009155 | 0.17853 | 57.3486 | -0.2655 | 57.4814 | -0.13275 | -0.050354 | -0.032043 | 0.10986 | 0.050354 | 0.036621 | -0.11444 | 0.086975 | -0.064087 | 0.31128 | 123.7152 | 0.10071 | 123.7335 | 123.6603 | 123.5916 | 123.5275 | 123.5413 | -123.7061 | -123.6237 | 123.5825 | 123.6832 | 55.3986 | 52.8122
322.4844 | 123.7289 | -59.6054 | 63.9404 | 0.03381 | 0.0017875 | 0.054585 | 0.081166 | 0.0048751 | -0.015725 | 0.0046426 | 0.13063 | 0.0054994 | 0.067821 | 0.0224 | -0.0050872 | 0.017048 | 0.0046845 | -4.5181 | 63.9038 | -59.761 | 63.9633 | -59.4452 | -59.8892 | -2.3712 | -7.2693 | 63.9313 | -59.6878 | 64.1281 | -59.5779 | -59.7885 | -59.5642 | -0.15564 | -0.036621 | 0.022888 | 0.16022 | 57.2342 | -0.28381 | 57.3898 | -0.12817 | -0.082397 | -0.009156 | 0.18768 | 0.027466 | 0.041199 | -0.18311 | 0.1236 | -0.10071 | 0.31586 | 123.7244 | 0.10986 | 123.8159 | 123.6649 | 123.6191 | 123.5092 | 123.5367 | -123.7015 | -123.6282 | 123.5687 | 123.7335 | 55.0873 | 52.3361
323.4844 | 123.7335 | -59.5734 | 64.0137 | 0.1864 | 0.0060595 | 0.056722 | 0.083302 | -0.0068739 | 0.0056368 | -0.0028344 | -0.11351 | 0.015112 | 0.063548 | 0.069397 | -0.016836 | 0.019184 | -0.018814 | -4.747 | 63.9725 | -59.729 | 64.0778 | -59.3628 | -59.7931 | -2.4124 | -7.6218 | 63.9862 | -59.6649 | 64.0961 | -59.5322 | -59.7427 | -59.5596 | -0.15564 | -0.041199 | 0.064087 | 0.21057 | 57.1609 | -0.21973 | 57.3166 | -0.064087 | -0.091553 | -0.027466 | 0.082397 | 0.041198 | 0.013733 | -0.16937 | 0.10529 | -0.07782 | 0.36621 | 123.8068 | 0.13275 | 123.761 | 123.7015 | 123.6511 | 123.5458 | 123.5596 | -123.7427 | -123.6786 | 123.6511 | 123.6694 | 54.8264 | 51.9516
324.4844 | 123.7564 | -59.5779 | 63.9679 | 0.064327 | -0.0067575 | 0.06313 | 0.068349 | 0.0048751 | -0.00077219 | -0.012447 | 0.039077 | 0.0012264 | 0.06248 | 0.054443 | -0.010427 | 0.011707 | -0.030563 | -5.1361 | 63.913 | -59.7107 | 63.9679 | -59.4498 | -59.8663 | -2.5772 | -8.0154 | 63.9175 | -59.642 | 64.1144 | -59.523 | -59.7107 | -59.5139 | -0.13275 | -0.054932 | 0 | 0.12817 | 57.0007 | -0.28839 | 57.1335 | -0.15564 | -0.064087 | -0.050354 | 0.14648 | 0.054932 | 0.064087 | -0.13275 | 0.12817 | -0.068664 | 0.26093 | 123.6786 | 0.11902 | 123.7564 | 123.6237 | 123.5596 | 123.4909 | 123.4955 | -123.6786 | -123.6099 | 123.5458 | 123.6923 | 54.4418 | 51.5625
325.4844 | 123.8297 | -59.5322 | 63.9633 | 0.15588 | 0.0049915 | 0.060994 | 0.075825 | 0.012352 | -0.010385 | -0.0071064 | 0.16115 | 0.0012264 | 0.071025 | 0.053375 | -0.012563 | 0.013843 | -0.0081325 | -5.3696 | 63.9542 | -59.6512 | 63.9679 | -59.4635 | -59.8846 | -2.5955 | -8.2169 | 63.9816 | -59.5642 | 64.3066 | -59.2255 | -59.9258 | -59.6603 | -0.11902 | -0.009155 | 0.004578 | 0.068665 | 56.9366 | -0.35248 | 57.0557 | -0.23346 | -0.032043 | 0.01831 | 0.34332 | 0.3067 | -0.12817 | -0.39368 | -0.09613 | -0.36163 | 0.18768 | 123.6191 | 0.33874 | 123.8708 | 123.6053 | 123.5458 | 123.4863 | 123.5138 | -123.6145 | -123.5275 | 123.5001 | 123.8388 | 54.1626 | 51.3153
326.4844 | 123.7701 | -59.5047 | 64.032 | 0.0032924 | 0.0028555 | 0.059926 | 0.072621 | 0.0059431 | -0.012521 | 0.0067786 | 0.069594 | 0.0065674 | 0.07957 | 0.040558 | -0.011495 | 0.0095709 | -0.0049285 | -5.777 | 63.9496 | -59.697 | 63.9999 | -59.3582 | -59.8022 | -2.6276 | -8.638 | 63.9908 | -59.5505 | 64.1556 | -59.4772 | -59.6741 | -59.4864 | -0.19226 | -0.082397 | -0.032043 | 0.14648 | 56.8771 | -0.29755 | 57.0694 | -0.10529 | -0.045776 | -0.041198 | 0.1236 | 0.027466 | 0.018311 | -0.16937 | 0.064087 | -0.1236 | 0.33874 | 123.6969 | 0.073242 | 123.7061 | 123.6465 | 123.5413 | 123.4543 | 123.4955 | -123.7289 | -123.5825 | 123.5046 | 123.6603 | 53.7277 | 50.8667
327.4844 | 123.7381 | -59.5139 | 64.0228 | 0.15588 | 0.0060595 | 0.064198 | 0.07903 | 0.0070111 | -0.0093172 | 0.0014386 | 0.054336 | 0.0033634 | 0.071025 | 0.030945 | -0.00081422 | 0.0020939 | 0.0025485 | -6.1249 | 63.9587 | -59.6649 | 64.0686 | -59.3308 | -59.7702 | -2.7603 | -9.0546 | 63.9999 | -59.6054 | 64.151 | -59.4727 | -59.6603 | -59.4818 | -0.15106 | -0.064087 | 0.045777 | 0.1831 | 56.7535 | -0.25635 | 56.9046 | -0.10529 | -0.091553 | -0.022888 | 0.12817 | 0.041199 | 0.032043 | -0.14648 | 0.1236 | -0.054931 | 0.33417 | 123.7335 | 0.13275 | 123.7564 | 123.6237 | 123.6053 | 123.4726 | 123.5138 | -123.6877 | -123.6282 | 123.5825 | 123.6649 | 53.389 | 50.4593
328.4844 | 123.7839 | -59.5093 | 64.0366 | 0.0032924 | -0.017438 | 0.052449 | 0.069417 | 0.0038071 | -0.0029082 | -0.011379 | 0.20692 | -0.0083866 | 0.076366 | 0.057647 | -0.010427 | -4.2099e-05 | -0.0038605 | -6.4499 | 63.9999 | -59.6375 | 64.0823 | -59.3216 | -59.7839 | -2.8427 | -9.3887 | 64.032 | -59.5505 | 64.1556 | -59.4681 | -59.6329 | -59.4589 | -0.12817 | -0.036621 | 0.045776 | 0.18768 | 56.6666 | -0.27466 | 56.7947 | -0.14648 | -0.041199 | -0.004578 | 0.11902 | 0.041198 | 0.050354 | -0.1236 | 0.091553 | -0.082398 | 0.31586 | 123.7198 | 0.082397 | 123.7061 | 123.6374 | 123.5825 | 123.5092 | 123.5413 | -123.674 | -123.587 | 123.5916 | 123.6649 | 53.0594 | 50.1205
329.4844 | 123.7427 | -59.4864 | 64.0594 | 0.14062 | 0.0028555 | 0.053517 | 0.06728 | -0.0026019 | 0.0099088 | -0.0028344 | 0.20692 | 0.0054994 | 0.085979 | 0.0961 | -0.012563 | 0.0052979 | -0.0070645 | -6.8069 | 64.0137 | -59.6329 | 64.1144 | -59.285 | -59.7473 | -2.8839 | -9.6359 | 64.032 | -59.5367 | 64.2197 | -59.4406 | -59.6329 | -59.4406 | -0.14648 | -0.045776 | 0.054932 | 0.20142 | 56.6025 | -0.26093 | 56.749 | -0.11444 | -0.050354 | -0.027466 | 0.16022 | 0.045776 | 0.045776 | -0.14648 | 0.09613 | -0.096131 | 0.3479 | 123.7473 | 0.09613 | 123.7564 | 123.6465 | 123.5687 | 123.5001 | 123.5184 | -123.6923 | -123.5962 | 123.6008 | 123.7061 | 52.6794 | 49.8505
330.4844 | 123.7335 | -59.4452 | 64.1327 | 0.15588 | 0.0028555 | 0.068471 | 0.075825 | -0.0079419 | -0.0029082 | 0.0099836 | 0.0085594 | 0.0065674 | 0.082775 | 0.089691 | -0.0029502 | 0.0052979 | 0.0089575 | -7.0221 | 64.064 | -59.5871 | 64.1144 | -59.2712 | -59.7061 | -2.9617 | -9.9747 | 64.0778 | -59.4955 | 64.2288 | -59.3674 | -59.5551 | -59.3811 | -0.14191 | -0.068664 | -0.01831 | 0.17395 | 56.4835 | -0.26093 | 56.6254 | -0.11902 | -0.050354 | -0.054931 | 0.096131 | 0.077819 | 0.064086 | -0.10986 | 0.11444 | -0.05951 | 0.31586 | 123.7015 | 0.12817 | 123.7244 | 123.6511 | 123.5733 | 123.5092 | 123.5229 | -123.7198 | -123.6282 | 123.5596 | 123.674 | 52.4231 | 49.4705
331.4844 | 123.761 | -59.4086 | 64.1144 | 0.12536 | 0.0081955 | 0.064198 | 0.066212 | 0.012352 | -0.011453 | -0.0092424 | 0.069594 | 0.0054994 | 0.076366 | 0.067261 | -0.0093592 | 0.013843 | -0.033768 | -7.4661 | 64.0549 | -59.5688 | 64.119 | -59.2804 | -59.7244 | -3.0945 | -10.318 | 64.0823 | -59.4818 | 64.2517 | -59.3445 | -59.5459 | -59.3628 | -0.16022 | -0.059509 | 0.004578 | 0.12817 | 56.3141 | -0.31586 | 56.4743 | -0.15564 | -0.073243 | -0.032044 | 0.13733 | 0.064087 | 0.045776 | -0.13733 | 0.11902 | -0.064086 | 0.28839 | 123.6877 | 0.13733 | 123.7335 | 123.6237 | 123.5641 | 123.4634 | 123.4909 | -123.6832 | -123.5962 | 123.5275 | 123.6603 | 51.9424 | 49.0906
332.4844 | 123.8342 | -59.4086 | 64.1144 | 0.094845 | 0.0039235 | 0.051381 | 0.07903 | 0.015556 | 0.0045688 | -0.0060384 | 0.13063 | 0.0087034 | 0.064617 | 0.050171 | -0.0072232 | 0.019184 | 0.0014805 | -7.8918 | 64.0778 | -59.5551 | 64.1922 | -59.1934 | -59.6649 | -3.1357 | -10.5423 | 64.119 | -59.4772 | 64.2609 | -59.3399 | -59.5413 | -59.4589 | -0.14648 | -0.036621 | 0.07782 | 0.21515 | 56.2729 | -0.25635 | 56.4194 | -0.10986 | -0.068665 | 0.004578 | 0.14648 | 0.068664 | -0.050354 | -0.13275 | 0.018311 | -0.064087 | 0.36163 | 123.7473 | 0.13733 | 123.7381 | 123.6328 | 123.5962 | 123.4863 | 123.5275 | -123.6694 | -123.5916 | 123.6008 | 123.6694 | 51.5167 | 48.8663
333.4844 | 123.7427 | -59.3903 | 64.1418 | 0.1101 | 0.0060595 | 0.067403 | 0.072621 | -0.015419 | 0.0056368 | -0.0049704 | 0.054336 | 0.0076354 | 0.07957 | 0.060852 | -0.0147 | 0.02132 | -0.019882 | -8.1665 | 64.0869 | -59.5413 | 64.183 | -59.1843 | -59.6558 | -3.1403 | -10.7758 | 64.1327 | -59.4452 | 64.2746 | -59.3491 | -59.5139 | -59.3399 | -0.15106 | -0.054932 | 0.041198 | 0.20599 | 56.25 | -0.2655 | 56.4011 | -0.11444 | -0.054931 | -0.009156 | 0.13275 | 0.041199 | 0.050354 | -0.1236 | 0.10528 | -0.068665 | 0.35706 | 123.7244 | 0.09613 | 123.7198 | 123.6282 | 123.5779 | 123.4772 | 123.5229 | -123.6832 | -123.587 | 123.5733 | 123.6649 | 51.2238 | 48.6145
334.4844 | 123.7381 | -59.3719 | 64.1602 | 0.079586 | -0.0046215 | 0.04604 | 0.066212 | 0.0070111 | 0.0024328 | 0.00037059 | 0.17641 | -0.0062496 | 0.068889 | 0.095032 | -0.016836 | 0.0042299 | -0.0081325 | -8.4457 | 64.1144 | -59.5184 | 64.1876 | -59.1614 | -59.642 | -3.186 | -11.0046 | 64.1556 | -59.4406 | 64.2929 | -59.3262 | -59.523 | -59.3353 | -0.14648 | -0.045776 | 0.027466 | 0.21057 | 56.1859 | -0.27008 | 56.3324 | -0.1236 | -0.068665 | -0.004577 | 0.13275 | 0.045776 | 0.036621 | -0.15106 | 0.10529 | -0.082397 | 0.35706 | 123.7061 | 0.11444 | 123.7335 | 123.6328 | 123.5962 | 123.4863 | 123.5275 | -123.6786 | -123.6008 | 123.5596 | 123.6649 | 50.9262 | 48.3673
335.4844 | 123.7747 | -59.3491 | 64.2105 | 0.30847 | 0.0071275 | 0.065267 | 0.070485 | -0.019692 | -0.029611 | 0.0014386 | 0.039077 | -0.00090962 | 0.075298 | 0.058716 | -0.0040182 | 0.014911 | 0.0025485 | -8.6609 | 64.1281 | -59.4727 | 64.183 | -59.1843 | -59.6558 | -3.2043 | -11.0458 | 64.1693 | -59.3994 | 64.357 | -59.2163 | -59.4177 | -59.2575 | -0.1236 | -0.082397 | -0.027466 | 0.16479 | 56.1447 | -0.3067 | 56.2683 | -0.18311 | -0.050354 | -0.041198 | 0.14648 | 0.13275 | 0.091553 | -0.068665 | 0.14191 | -0.018311 | 0.28839 | 123.6557 | 0.1831 | 123.7564 | 123.6008 | 123.5687 | 123.4772 | 123.5184 | -123.6832 | -123.6099 | 123.5321 | 123.7061 | 50.6882 | 48.3032
336.4844 | 123.7518 | -59.3536 | 64.2014 | 0.12536 | -0.0046215 | 0.052449 | 0.08437 | 0.0027391 | -0.0029082 | -0.0060384 | 0.023818 | 0.00015838 | 0.080638 | 0.059784 | -0.0050872 | 0.014911 | 0.020706 | -9.0363 | 64.1373 | -59.491 | 64.1876 | -59.1064 | -59.5779 | -3.2227 | -11.3434 | 64.1556 | -59.4086 | 64.3616 | -59.2438 | -59.436 | -59.2758 | -0.13733 | -0.064087 | -0.013733 | 0.24719 | 56.131 | -0.2243 | 56.2683 | -0.086975 | -0.054931 | -0.045776 | 0.16022 | 0.10986 | 0.07782 | -0.082397 | 0.13275 | -0.027466 | 0.38452 | 123.6786 | 0.16479 | 123.7701 | 123.6282 | 123.5641 | 123.4909 | 123.5092 | -123.6923 | -123.6099 | 123.5413 | 123.7152 | 50.3174 | 48.0103
337.4844 | 123.7564 | -59.3216 | 64.2105 | 0.018551 | 0.0071275 | 0.05779 | 0.07903 | 0.0080791 | -0.014657 | -0.014583 | 0.10011 | 0.0044314 | 0.071025 | 0.10571 | -0.013631 | 0.01598 | 0.0025485 | -9.2743 | 64.1785 | -59.4727 | 64.2654 | -59.1019 | -59.6237 | -3.2547 | -11.4761 | 64.1922 | -59.404 | 64.3387 | -59.2575 | -59.4681 | -59.2896 | -0.15106 | -0.032043 | 0.054932 | 0.21973 | 56.0669 | -0.30212 | 56.218 | -0.15106 | -0.082398 | -0.01831 | 0.12817 | 0.064087 | 0.032043 | -0.14649 | 0.11444 | -0.064087 | 0.37079 | 123.7381 | 0.14649 | 123.7427 | 123.6511 | 123.5962 | 123.5001 | 123.5138 | -123.6832 | -123.6145 | 123.587 | 123.6603 | 50.0473 | 47.8455
338.4844 | 123.7473 | -59.3308 | 64.1876 | 0.094845 | 0.0017875 | 0.062062 | 0.076894 | -0.0004649 | 0.0024328 | -0.0039024 | 0.11537 | 0.0012264 | 0.072093 | 0.060852 | 0.0023898 | -0.0075191 | 0.00041246 | -9.4757 | 64.1464 | -59.4864 | 64.2609 | -59.0927 | -59.6054 | -3.3005 | -11.6638 | 64.1739 | -59.3903 | 64.3478 | -59.2484 | -59.4589 | -59.285 | -0.15564 | -0.041199 | 0.073242 | 0.23804 | 56.0303 | -0.27466 | 56.1859 | -0.11902 | -0.059509 | -0.013733 | 0.16022 | 0.082398 | 0.045777 | -0.12817 | 0.10529 | -0.068664 | 0.39368 | 123.7473 | 0.14191 | 123.7381 | 123.6328 | 123.5641 | 123.4772 | 123.5046 | -123.674 | -123.5779 | 123.5916 | 123.6786 | 49.855 | 47.6669
339.4844 | 123.7747 | -59.2758 | 64.2426 | 0.094845 | -0.00034947 | 0.054585 | 0.065144 | -0.0058059 | -0.0061122 | 0.015324 | 0.039077 | 0.0044314 | 0.072093 | 0.056579 | -0.02004 | 0.011707 | -0.0059965 | -9.6497 | 64.1968 | -59.4498 | 64.2471 | -59.0927 | -59.5276 | -3.2822 | -11.8607 | 64.1693 | -59.3765 | 64.3845 | -59.2072 | -59.4086 | -59.2346 | -0.17395 | -0.045777 | 0.004577 | 0.18311 | 55.9937 | -0.25177 | 56.1676 | -0.07782 | -0.10071 | -0.073242 | 0.14191 | 0.068665 | 0.041199 | -0.13275 | 0.14191 | -0.032043 | 0.35706 | 123.6969 | 0.16937 | 123.761 | 123.6465 | 123.5458 | 123.4726 | 123.4451 | -123.6923 | -123.6191 | 123.5229 | 123.6603 | 49.6262 | 47.4152
340.4844 | 123.6969 | -59.285 | 64.3021 | 0.15588 | 0.0028555 | 0.06313 | 0.082234 | 0.0038071 | -0.023202 | -0.0028344 | 0.069594 | 0.0076354 | 0.077434 | 0.052307 | 0.0013218 | 0.022388 | 0.026047 | -9.7229 | 64.2151 | -59.4177 | 64.3112 | -59.0149 | -59.5139 | -3.2135 | -11.9476 | 64.2609 | -59.3262 | 64.3616 | -59.2346 | -59.4177 | -59.2484 | -0.13275 | -0.086975 | 0.009155 | 0.27008 | 56.0715 | -0.22888 | 56.2042 | -0.09613 | -0.041199 | -0.041199 | 0.059509 | 0.050354 | 0.036621 | -0.13275 | 0.07782 | -0.091553 | 0.40283 | 123.7289 | 0.091553 | 123.6877 | 123.6328 | 123.587 | 123.5001 | 123.5458 | -123.7198 | -123.6282 | 123.5962 | 123.6465 | 49.5621 | 47.3373
341.4844 | 123.7289 | -59.2575 | 64.2471 | -0.042484 | 0.0060595 | 0.050313 | 0.06728 | -0.0058059 | -0.016794 | 0.0078466 | 0.14589 | 0.00015838 | 0.073162 | 0.069397 | -0.0072232 | 0.0085029 | -0.010269 | -10.0021 | 64.2014 | -59.4315 | 64.3524 | -59.0607 | -59.5413 | -3.3051 | -12.2681 | 64.238 | -59.3445 | 64.4211 | -59.1614 | -59.3719 | -59.2117 | -0.17395 | -0.045776 | 0.10529 | 0.19684 | 55.9525 | -0.28381 | 56.1264 | -0.10986 | -0.086975 | -0.009155 | 0.17395 | 0.09613 | 0.045776 | -0.11444 | 0.13275 | -0.027466 | 0.37079 | 123.7839 | 0.1831 | 123.7656 | 123.6328 | 123.5825 | 123.4589 | 123.4955 | -123.6786 | -123.5916 | 123.6099 | 123.6786 | 49.2554 | 46.9894
342.4844 | 123.7747 | -59.2438 | 64.2334 | 0.1864 | 0.0049915 | 0.05779 | 0.069417 | -0.0036699 | -0.0050442 | -0.00069841 | 0.10011 | -0.0030456 | 0.064617 | 0.055511 | -0.0072232 | 0.0085029 | -0.0070645 | -10.0754 | 64.1876 | -59.4269 | 64.2517 | -59.0652 | -59.5596 | -3.2822 | -12.0575 | 64.2471 | -59.3262 | 64.444 | -59.1156 | -59.3353 | -59.1934 | -0.18311 | -0.045776 | 0.018311 | 0.17853 | 55.9616 | -0.31586 | 56.1447 | -0.13275 | -0.082398 | 0.013733 | 0.21057 | 0.12817 | 0.050354 | -0.091553 | 0.13275 | -0.009155 | 0.36163 | 123.6786 | 0.21057 | 123.7701 | 123.6145 | 123.5733 | 123.4314 | 123.4909 | -123.6603 | -123.5596 | 123.4955 | 123.6877 | 49.1684 | 47.1863
343.4844 | 123.761 | -59.2438 | 64.2838 | 0.12536 | 0.013537 | 0.06313 | 0.071553 | -0.0026019 | 0.013114 | 0.0025066 | 0.22218 | 0.0087034 | 0.071025 | 0.054443 | -0.0072232 | 0.010639 | -0.0038605 | -10.2173 | 64.2197 | -59.4131 | 64.2883 | -59.0103 | -59.5459 | -3.2822 | -12.3138 | 64.2654 | -59.3124 | 64.4577 | -59.079 | -59.3124 | -59.1568 | -0.16937 | -0.064086 | 0.004578 | 0.23346 | 55.9616 | -0.30212 | 56.131 | -0.13275 | -0.068665 | -0.01831 | 0.17395 | 0.1648 | 0.086975 | -0.068665 | 0.15564 | 0 | 0.40283 | 123.7015 | 0.23346 | 123.7701 | 123.6328 | 123.5779 | 123.4634 | 123.5092 | -123.6969 | -123.5962 | 123.5321 | 123.7015 | 49.0265 | 46.9299
344.4844 | 123.7564 | -59.2529 | 64.2975 | 0.0032924 | -0.0035535 | 0.065267 | 0.073689 | 0.019829 | 0.0035008 | -0.010311 | 0.069594 | 0.0033634 | 0.063548 | 0.072601 | -0.016836 | -4.2099e-05 | -0.0027915 | -10.3729 | 64.2563 | -59.3948 | 64.3341 | -58.9783 | -59.4864 | -3.2867 | -12.5473 | 64.27 | -59.3124 | 64.4211 | -59.1293 | -59.3765 | -59.2209 | -0.14191 | -0.041198 | 0.036621 | 0.27466 | 55.9662 | -0.23346 | 56.1081 | -0.091553 | -0.059509 | -0.027465 | 0.1236 | 0.1236 | 0.032044 | -0.1236 | 0.091553 | -0.064087 | 0.41656 | 123.7289 | 0.18311 | 123.7335 | 123.6511 | 123.5825 | 123.5092 | 123.523 | -123.6923 | -123.6099 | 123.587 | 123.674 | 48.88 | 46.7056
345.4844 | 123.6694 | -59.2163 | 64.3982 | 0.23217 | 0.0017875 | 0.05779 | 0.070485 | 0.0070111 | -0.013589 | 0.0067786 | -0.037217 | 0.010839 | 0.06248 | 0.064056 | -0.0072232 | 0.0074349 | -0.00065554 | -10.437 | 64.3387 | -59.404 | 64.4623 | -58.8638 | -59.3719 | -3.0487 | -12.648 | 64.3616 | -59.2987 | 64.4119 | -59.1339 | -59.3903 | -59.2438 | -0.18768 | -0.059509 | 0.064087 | 0.35248 | 56.1676 | -0.15564 | 56.3553 | 0.032044 | -0.082397 | -0.036621 | 0.013733 | 0.082398 | -0.027465 | -0.17395 | 0.054932 | -0.091553 | 0.54016 | 123.8663 | 0.1648 | 123.7106 | 123.7427 | 123.6603 | 123.555 | 123.5779 | -123.8022 | -123.6969 | 123.6786 | 123.6282 | 48.7793 | 46.5683
346.4844 | 123.7976 | -59.2209 | 64.3341 | 0.1101 | 0.0081955 | 0.052449 | 0.063008 | 0.0091481 | 0.0035008 | -0.0017664 | 0.10011 | -0.0019776 | 0.076366 | 0.03949 | -0.0082912 | 0.0031619 | 0.012161 | -10.5469 | 64.2746 | -59.3948 | 64.3204 | -58.9737 | -59.5093 | -3.1723 | -13.2797 | 64.3066 | -59.2667 | 64.4897 | -59.0149 | -59.2758 | -59.1156 | -0.17395 | -0.059509 | -0.013732 | 0.24719 | 56.0486 | -0.28839 | 56.2225 | -0.11444 | -0.045777 | -0.027465 | 0.15564 | 0.20599 | 0.10529 | -0.054932 | 0.15106 | -0.009155 | 0.42114 | 123.7152 | 0.25177 | 123.7564 | 123.6694 | 123.5733 | 123.4955 | 123.5275 | -123.7289 | -123.6008 | 123.5413 | 123.7106 | 48.674 | 45.9412
347.4844 | 123.7793 | -59.1843 | 64.3433 | 0.049069 | 0.0028555 | 0.054585 | 0.082234 | 0.0070111 | -0.021066 | 0.0025066 | 0.14589 | -0.00090962 | 0.068889 | 0.057647 | -0.012563 | 0.0042299 | -0.0017235 | -10.6705 | 64.2929 | -59.3445 | 64.3524 | -58.9325 | -59.491 | -3.1952 | -13.3804 | 64.3021 | -59.2667 | 64.5218 | -59.0286 | -59.2712 | -59.1156 | -0.16022 | -0.050354 | 0.009155 | 0.25177 | 55.9891 | -0.3067 | 56.1493 | -0.14648 | -0.082398 | -0.041199 | 0.17853 | 0.15564 | 0.068664 | -0.086975 | 0.15106 | -0.004577 | 0.41199 | 123.6969 | 0.23804 | 123.7885 | 123.6374 | 123.5687 | 123.4772 | 123.4863 | -123.6877 | -123.6099 | 123.5367 | 123.7061 | 48.5138 | 45.8038
348.4844 | 123.7747 | -59.1614 | 64.3753 | 0.049069 | 0.0092645 | 0.064198 | 0.068349 | 0.017693 | -0.0039762 | -0.0081744 | 0.11537 | 0.0033634 | 0.063548 | 0.085418 | -0.013631 | 0.02132 | -0.010269 | -11.1374 | 64.3112 | -59.3124 | 64.4119 | -58.905 | -59.4452 | -3.2501 | -13.6002 | 64.3524 | -59.2255 | 64.5538 | -58.9737 | -59.23 | -59.0744 | -0.15106 | -0.064087 | 0.036621 | 0.25635 | 55.9113 | -0.28381 | 56.0623 | -0.13275 | -0.064087 | -0.022888 | 0.17853 | 0.18768 | 0.086975 | -0.068665 | 0.15106 | -0.004578 | 0.40741 | 123.7244 | 0.25177 | 123.7793 | 123.6237 | 123.5779 | 123.4726 | 123.5138 | -123.6877 | -123.6008 | 123.5733 | 123.7152 | 48.024 | 45.5612
349.4844 | 123.8159 | -59.1339 | 64.3799 | 0.079586 | 0.0049915 | 0.051381 | 0.077962 | 0.019829 | 0.0099088 | 0.0046426 | 0.084853 | 0.0076354 | 0.060344 | 0.060852 | -0.0082912 | -0.0021781 | 0.00041246 | -11.087 | 64.3021 | -59.2941 | 64.357 | -58.9462 | -59.4772 | -2.6917 | -13.8886 | 64.3478 | -59.2392 | 64.5584 | -58.905 | -59.2209 | -59.0744 | -0.16022 | -0.07782 | -0.022888 | 0.18768 | 56.4423 | -0.34332 | 56.6025 | -0.18311 | -0.10529 | -0.032044 | 0.17853 | 0.22888 | 0.059509 | -0.086975 | 0.16479 | 0.018311 | 0.3479 | 123.6511 | 0.33417 | 123.7976 | 123.5962 | 123.587 | 123.436 | 123.4817 | -123.674 | -123.6191 | 123.4909 | 123.6923 | 48.0469 | 45.2454
350.4844 | 123.7015 | -59.1522 | 64.4302 | 0.15588 | -0.0056895 | 0.058858 | 0.073689 | -0.0058059 | -0.015725 | 0.01212 | 0.13063 | 0.00015838 | 0.068889 | 0.060852 | -0.022176 | 0.0031619 | 0.0014805 | -11.1282 | 64.3845 | -59.3033 | 64.476 | -58.8181 | -59.3491 | -2.4307 | -14.2044 | 64.4394 | -59.1843 | 64.4897 | -59.0195 | -59.2941 | -59.1293 | -0.15106 | -0.045777 | 0.045776 | 0.33417 | 56.7215 | -0.19684 | 56.8726 | -0.045776 | -0.032043 | 0.009155 | 0.059509 | 0.13275 | 0.022889 | -0.14191 | 0.054932 | -0.10986 | 0.48523 | 123.7793 | 0.1648 | 123.674 | 123.6877 | 123.6237 | 123.5367 | 123.5916 | -123.7335 | -123.6145 | 123.6282 | 123.642 | 48.024 | 44.9478
351.4844 | 123.7518 | -59.1431 | 64.4073 | 0.079586 | 0.0060595 | 0.056722 | 0.075825 | 0.0080791 | 0.0024328 | -0.0028344 | 0.16115 | 0.0022944 | 0.073162 | 0.045898 | -0.012563 | 0.0095709 | -0.0027915 | -11.3068 | 64.3387 | -59.2712 | 64.389 | -58.8501 | -59.3765 | -2.33 | -14.5523 | 64.3707 | -59.2163 | 64.5493 | -58.9691 | -59.2209 | -59.0652 | -0.12817 | -0.068665 | -0.018311 | 0.29297 | 56.813 | -0.23346 | 56.9412 | -0.10529 | -0.073243 | -0.036621 | 0.14191 | 0.17395 | 0.077819 | -0.07782 | 0.15106 | -0.004577 | 0.42114 | 123.6603 | 0.24719 | 123.7656 | 123.6099 | 123.587 | 123.4818 | 123.5138 | -123.6786 | -123.6237 | 123.5321 | 123.6923 | 47.8363 | 44.5908
352.4844 | 123.7885 | -59.1156 | 64.4165 | 0.018551 | 0.0017875 | 0.054585 | 0.075825 | -0.0004649 | 0.0013638 | 0.018529 | 0.14589 | -0.0030456 | 0.066753 | 0.038421 | -0.012563 | 0.014911 | -0.017746 | -11.4899 | 64.3707 | -59.2758 | 64.4302 | -58.8364 | -59.404 | -2.2522 | -14.7354 | 64.3799 | -59.166 | 64.5905 | -58.8959 | -59.1751 | -59.0195 | -0.16022 | -0.045776 | 0.013733 | 0.27924 | 56.8634 | -0.28839 | 57.0236 | -0.12817 | -0.050354 | -0.036621 | 0.17395 | 0.21973 | 0.096131 | -0.059509 | 0.14648 | -0.009155 | 0.43945 | 123.7061 | 0.27008 | 123.7564 | 123.6465 | 123.5458 | 123.4863 | 123.4955 | -123.6923 | -123.5825 | 123.5458 | 123.7061 | 47.6257 | 44.3802
353.4844 | 123.7839 | -59.079 | 64.4394 | 0.1101 | -0.0067575 | 0.056722 | 0.077962 | 0.0016711 | 0.0045688 | -0.0081744 | 0.13063 | 0.0076354 | 0.066753 | 0.0042417 | -0.0072232 | 0.012775 | 0.0046845 | -12.1674 | 64.4119 | -59.2346 | 64.4577 | -58.7677 | -59.3765 | -2.3895 | -14.8911 | 64.4211 | -59.1339 | 64.6225 | -58.8638 | -59.1476 | -59.0057 | -0.15564 | -0.027466 | 0.018311 | 0.31128 | 56.6895 | -0.29755 | 56.8451 | -0.14191 | -0.054932 | -0.01831 | 0.18311 | 0.21515 | 0.073242 | -0.068665 | 0.12817 | -0.013733 | 0.46692 | 123.6923 | 0.27008 | 123.7564 | 123.6465 | 123.555 | 123.4909 | 123.5001 | -123.674 | -123.5733 | 123.5367 | 123.7015 | 46.9116 | 44.1879
354.4844 | 123.7564 | -59.0469 | 64.4806 | -0.011967 | 0.0092645 | 0.058858 | 0.077962 | -0.0036699 | -0.0039762 | -0.0081744 | 0.10011 | 0.0054994 | 0.07423 | 0.067261 | -0.0093592 | 0.0010259 | 0.0014805 | -12.4008 | 64.444 | -59.23 | 64.5218 | -58.7265 | -59.3033 | -2.3804 | -15.1199 | 64.4714 | -59.1202 | 64.6408 | -58.8226 | -59.1202 | -58.9645 | -0.18311 | -0.036621 | 0.041199 | 0.32044 | 56.6666 | -0.25635 | 56.8497 | -0.073242 | -0.073242 | -0.009155 | 0.16022 | 0.2243 | 0.082397 | -0.073242 | 0.15564 | 0 | 0.50354 | 123.7518 | 0.29755 | 123.761 | 123.674 | 123.5916 | 123.4909 | 123.5184 | -123.7106 | -123.6008 | 123.5687 | 123.6877 | 46.6461 | 43.927
355.4844 | 123.6603 | -59.0424 | 64.5538 | 0.0032924 | 0.0049915 | 0.062062 | 0.077962 | -0.021828 | -0.011453 | -0.0071064 | -0.11351 | 0.00015838 | 0.068889 | 0.01065 | -0.010427 | 0.0063669 | 0.0025485 | -12.5473 | 64.5264 | -59.198 | 64.6637 | -58.5709 | -59.1797 | -2.124 | -15.4449 | 64.5493 | -59.079 | 64.5721 | -58.8913 | -59.1476 | -59.0424 | -0.15564 | -0.027466 | 0.10986 | 0.4715 | 56.9183 | -0.13733 | 57.074 | 0.018311 | -0.036621 | -0.004578 | 0.018311 | 0.15106 | 0 | -0.10529 | 0.036621 | -0.068665 | 0.62714 | 123.8617 | 0.18768 | 123.6511 | 123.7244 | 123.6282 | 123.5687 | 123.5916 | -123.7518 | -123.6328 | 123.7061 | 123.6145 | 46.4951 | 43.5974
356.4844 | 123.8022 | -58.9737 | 64.5447 | 0.0032924 | 0.0028555 | 0.056722 | 0.072621 | 0.0038071 | -0.0039762 | -0.0039024 | 0.10011 | 0.015112 | 0.07957 | 0.059784 | -0.0147 | 0.011707 | 0.0057535 | -12.7258 | 64.4943 | -59.1568 | 64.5493 | -58.6533 | -59.2804 | -2.1469 | -15.7059 | 64.5264 | -59.0469 | 64.7186 | -58.7402 | -59.024 | -58.8821 | -0.1831 | -0.050354 | 0.004577 | 0.32044 | 56.8268 | -0.3067 | 57.0099 | -0.1236 | -0.073242 | -0.018311 | 0.17395 | 0.23346 | 0.091553 | -0.050354 | 0.1648 | 0.022888 | 0.50354 | 123.7061 | 0.3067 | 123.7656 | 123.6511 | 123.5733 | 123.468 | 123.5001 | -123.7015 | -123.5916 | 123.5229 | 123.6923 | 46.2479 | 43.2678
357.4844 | 123.7381 | -58.9691 | 64.5905 | 0.1101 | 0.0060595 | 0.056722 | 0.080098 | -0.0036699 | -0.011453 | 0.0046426 | 0.054336 | 0.0022944 | 0.075298 | 0.06192 | 0.00025378 | 0.019184 | -0.014542 | -13.028 | 64.5172 | -59.1293 | 64.6088 | -58.5938 | -59.2209 | -2.0645 | -15.9164 | 64.5676 | -59.024 | 64.7141 | -58.7585 | -59.0424 | -58.9188 | -0.16022 | -0.073242 | 0.018311 | 0.37537 | 56.9046 | -0.25177 | 57.0648 | -0.091553 | -0.054932 | -0.022888 | 0.1236 | 0.21057 | 0.050354 | -0.073242 | 0.10529 | -0.01831 | 0.53558 | 123.7381 | 0.2655 | 123.7381 | 123.6465 | 123.5916 | 123.4863 | 123.5367 | -123.7198 | -123.6145 | 123.5779 | 123.6832 | 45.9412 | 43.0527
358.4844 | 123.7015 | -58.9096 | 64.5996 | 0.0032924 | 0.0049915 | 0.052449 | 0.075825 | 0.0027391 | 0.017386 | -0.015651 | 0.14589 | 0.0054994 | 0.064617 | 0.055511 | -0.0147 | 0.013843 | -0.0038605 | -13.2294 | 64.5538 | -59.0744 | 64.6408 | -58.5434 | -59.1751 | -2.0004 | -16.658 | 64.5813 | -58.9874 | 64.7507 | -58.7173 | -58.873 | -58.786 | -0.16479 | -0.045776 | 0.041199 | 0.36621 | 56.9092 | -0.2655 | 57.074 | -0.10071 | -0.07782 | -0.01831 | 0.15106 | 0.19226 | 0.1236 | 0.036621 | 0.20142 | 0.11444 | 0.53101 | 123.7152 | 0.27008 | 123.7381 | 123.6282 | 123.5687 | 123.4634 | 123.4909 | -123.674 | -123.587 | 123.5504 | 123.6603 | 45.6802 | 42.2516
359.4844 | 123.7564 | -58.9142 | 64.6133 | 0.094845 | 0.0071275 | 0.067403 | 0.076894 | 0.014488 | -0.0061122 | -0.0028344 | 0.11537 | 0.0044314 | 0.071025 | 0.052307 | -0.0093592 | 0.010639 | 0.0057535 | -13.4308 | 64.5676 | -59.0607 | 64.6912 | -58.5388 | -59.1797 | -1.9501 | -16.9739 | 64.6225 | -58.9828 | 64.7781 | -58.6807 | -58.992 | -58.8272 | -0.14648 | -0.045776 | 0.07782 | 0.37537 | 56.9641 | -0.2655 | 57.1106 | -0.11902 | -0.068664 | 0.009156 | 0.16479 | 0.23346 | 0.086976 | -0.077819 | 0.15564 | -0.009155 | 0.52185 | 123.7518 | 0.30212 | 123.761 | 123.6282 | 123.6053 | 123.4818 | 123.5367 | -123.674 | -123.5962 | 123.6053 | 123.6923 | 45.4834 | 41.9403
360.4844 | 123.7701 | -58.8272 | 64.6774 | 0.12536 | 0.0028555 | 0.06313 | 0.086507 | -0.015419 | 0.012046 | -0.012447 | 0.17641 | 0.0076354 | 0.055004 | 0.048034 | -0.016836 | 0.011707 | -0.014542 | -13.4399 | 64.6637 | -58.9371 | 64.6317 | -58.5022 | -59.1248 | -2.2797 | -17.0563 | 64.6637 | -58.8821 | 64.8605 | -58.5709 | -58.8913 | -58.7585 | -0.10986 | -0.013733 | -0.045776 | 0.32501 | 56.5475 | -0.29755 | 56.6574 | -0.18768 | -0.054932 | -0.013733 | 0.18311 | 0.25635 | 0.068664 | -0.064087 | 0.1236 | -0.009155 | 0.43488 | 123.5687 | 0.31128 | 123.7427 | 123.6008 | 123.5458 | 123.4909 | 123.4909 | -123.6145 | -123.5596 | 123.4589 | 123.6877 | 45.3873 | 41.7709
361.4844 | 123.7518 | -58.8226 | 64.6866 | 0.064327 | -0.0035535 | 0.062062 | 0.074757 | 0.0048751 | 0.0056368 | -0.0060384 | 0.19167 | -0.0041136 | 0.064617 | 0.058716 | -0.0029502 | 0.014911 | 0.0014805 | -13.8107 | 64.6591 | -58.9966 | 64.7186 | -58.4335 | -59.0973 | -2.3163 | -17.569 | 64.6591 | -58.9188 | 64.8834 | -58.667 | -58.9783 | -58.7677 | -0.17395 | -0.027465 | 0.032044 | 0.3891 | 56.5063 | -0.27466 | 56.6803 | -0.10071 | -0.09613 | -0.027465 | 0.19684 | 0.15564 | 0.054932 | -0.15564 | 0.15106 | -0.059509 | 0.56305 | 123.7152 | 0.25177 | 123.8022 | 123.6557 | 123.5779 | 123.4818 | 123.4818 | -123.6832 | -123.6053 | 123.5413 | 123.7061 | 45.0119 | 41.2537
362.4844 | 123.7701 | -58.7997 | 64.7049 | 0.094845 | -0.0035535 | 0.06313 | 0.072621 | -0.0090099 | -0.00077219 | 0.0025066 | 0.054336 | -0.00090962 | 0.067821 | 0.054443 | -0.015768 | 0.0052979 | 0.0068215 | -14.0945 | 64.6957 | -58.9828 | 64.7369 | -58.4061 | -59.079 | -2.3209 | -17.8619 | 64.7049 | -58.8913 | 64.8605 | -58.5617 | -58.8959 | -58.754 | -0.18311 | -0.009155 | 0.032043 | 0.39368 | 56.4789 | -0.27923 | 56.662 | -0.09613 | -0.091552 | 0 | 0.15564 | 0.23804 | 0.045777 | -0.09613 | 0.13733 | -0.004578 | 0.57678 | 123.7198 | 0.32959 | 123.7518 | 123.6786 | 123.5962 | 123.4955 | 123.5046 | -123.6877 | -123.5962 | 123.5367 | 123.6603 | 44.7052 | 40.9378
363.4844 | 123.761 | -58.7585 | 64.7736 | 0.094845 | -0.00034947 | 0.056722 | 0.077962 | -0.0015339 | -0.0082492 | -0.010311 | 0.084853 | 0.0065674 | 0.06248 | 0.057647 | -0.0072232 | 0.0052979 | -0.00065554 | -14.447 | 64.7461 | -58.9233 | 64.8285 | -58.3328 | -59.0332 | -2.3666 | -18.0267 | 64.7324 | -58.8684 | 64.9063 | -58.4839 | -58.8593 | -58.6807 | -0.1648 | -0.027466 | 0.054931 | 0.42572 | 56.3919 | -0.27466 | 56.5567 | -0.10986 | -0.10986 | -0.041199 | 0.13275 | 0.27466 | 0.07782 | -0.10071 | 0.18768 | 0.009155 | 0.59052 | 123.7518 | 0.38452 | 123.7747 | 123.6694 | 123.6008 | 123.5046 | 123.4909 | -123.6969 | -123.642 | 123.587 | 123.6649 | 44.3115 | 40.7318
364.4844 | 123.7564 | -58.7036 | 64.7964 | 0.018551 | 0.0071275 | 0.058858 | 0.076894 | -0.0004649 | -0.0050442 | 0.0014386 | 0.084853 | 0.0044314 | 0.056072 | 0.056579 | -0.018972 | 0.01598 | 0.0036165 | -14.6896 | 64.7415 | -58.873 | 64.8239 | -58.3054 | -58.9874 | -2.2888 | -18.3929 | 64.7736 | -58.7906 | 64.9612 | -58.4702 | -58.8181 | -58.6533 | -0.16937 | -0.054932 | 0.027466 | 0.39825 | 56.4148 | -0.28381 | 56.5842 | -0.11444 | -0.086975 | -0.022888 | 0.16479 | 0.23346 | 0.050354 | -0.11444 | 0.13733 | -0.027466 | 0.56763 | 123.6969 | 0.32043 | 123.7518 | 123.6145 | 123.5641 | 123.4451 | 123.4772 | -123.6694 | -123.587 | 123.5275 | 123.6649 | 44.014 | 40.3107
365.4844 | 123.7885 | -58.6761 | 64.8605 | 0.20166 | 0.0081955 | 0.060994 | 0.080098 | -0.013283 | -0.0082492 | -0.0017664 | -0.021958 | 0.0012264 | 0.060344 | 0.082214 | -0.0029502 | 0.0095709 | -0.0059965 | -14.7858 | 64.8193 | -58.8089 | 64.8239 | -58.342 | -58.7814 | -2.1469 | -18.7912 | 64.8148 | -58.7265 | 65.0436 | -58.3282 | -58.7219 | -58.5709 | -0.13275 | -0.041199 | -0.036621 | 0.33417 | 56.5292 | -0.10529 | 56.662 | 0.027466 | -0.050354 | -0.045777 | 0.1831 | 0.3479 | 0.10529 | -0.045777 | 0.15564 | 0.004577 | 0.46692 | 123.6328 | 0.39825 | 123.7701 | 123.6282 | 123.5413 | 123.4955 | 123.4909 | -123.6694 | -123.587 | 123.5001 | 123.7198 | 43.8904 | 39.8849
366.4844 | 123.7427 | -58.6075 | 64.9338 | 0.094845 | -0.0024855 | 0.065267 | 0.085438 | -0.0015339 | 0.0035008 | -0.016719 | 0.23744 | 0.0012264 | 0.066753 | 0.069397 | -0.012563 | 0.010639 | 0.012161 | -15.6418 | 64.888 | -58.786 | 64.9658 | -58.1497 | -58.8455 | -2.3666 | -18.9743 | 64.9017 | -58.6761 | 65.0757 | -58.2962 | -58.6624 | -58.5068 | -0.17853 | -0.045777 | 0.032043 | 0.45776 | 56.2408 | -0.23804 | 56.4194 | -0.059509 | -0.068664 | -0.032044 | 0.14191 | 0.31128 | 0.10071 | -0.054932 | 0.16937 | 0.013732 | 0.63629 | 123.7518 | 0.37994 | 123.7518 | 123.674 | 123.5779 | 123.4955 | 123.5092 | -123.7198 | -123.6099 | 123.5733 | 123.6832 | 42.9657 | 39.6332
367.4844 | 123.761 | -58.5892 | 64.9887 | 0.094845 | -0.0024855 | 0.059926 | 0.072621 | -0.016487 | -0.0082492 | 0.0067786 | 0.11537 | 0.0054994 | 0.071025 | 0.068329 | -0.016836 | 0.0052979 | -0.00065554 | -15.8295 | 64.9246 | -58.7082 | 64.9979 | -58.0765 | -58.8089 | -2.3529 | -19.2993 | 64.9841 | -58.6121 | 65.1123 | -58.255 | -58.667 | -58.4793 | -0.11902 | -0.064086 | 0.009156 | 0.5127 | 56.2363 | -0.21973 | 56.3553 | -0.10071 | -0.022889 | -0.004577 | 0.1236 | 0.33417 | 0.10986 | -0.07782 | 0.13275 | -0.054931 | 0.63171 | 123.7061 | 0.35706 | 123.7244 | 123.6328 | 123.5962 | 123.5138 | 123.5733 | -123.6969 | -123.6008 | 123.587 | 123.7015 | 42.7597 | 39.2899
368.4844 | 123.7427 | -58.493 | 65.0528 | 0.03381 | 0.0092645 | 0.050313 | 0.072621 | -0.0026019 | 0.016318 | 0.0025066 | 0.10011 | -0.0051816 | 0.06248 | 0.069397 | -0.0093592 | 0.0095709 | -0.011337 | -16.3559 | 64.9796 | -58.6487 | 65.0574 | -58.0261 | -58.7494 | -2.4078 | -19.6243 | 64.9979 | -58.5846 | 65.1581 | -58.2184 | -58.6075 | -58.4335 | -0.15564 | -0.073242 | 0.004578 | 0.46692 | 56.0852 | -0.25635 | 56.2408 | -0.10071 | -0.091553 | -0.054931 | 0.10529 | 0.27466 | 0.059509 | -0.11444 | 0.15106 | -0.022888 | 0.62256 | 123.7061 | 0.36621 | 123.7427 | 123.6282 | 123.5825 | 123.4726 | 123.4909 | -123.7015 | -123.6374 | 123.5504 | 123.6511 | 42.1371 | 38.8687
369.4844 | 123.761 | -58.4747 | 65.0574 | 0.079586 | 0.0092645 | 0.052449 | 0.071553 | -0.0068739 | -0.0039762 | -0.0092424 | 0.084853 | -0.0019776 | 0.075298 | 0.065124 | -0.0093592 | 0.0052979 | -0.0070645 | -16.7496 | 65.0299 | -58.6487 | 65.0894 | -57.9666 | -58.7173 | -2.3758 | -19.9997 | 65.0345 | -58.548 | 65.1764 | -58.1589 | -58.5571 | -58.4106 | -0.17395 | -0.027466 | 0.032044 | 0.50812 | 56.0989 | -0.24262 | 56.2729 | -0.068664 | -0.073243 | -0.022888 | 0.11902 | 0.31586 | 0.064086 | -0.082398 | 0.13733 | -0.009155 | 0.68207 | 123.7381 | 0.3891 | 123.7244 | 123.6786 | 123.5825 | 123.5046 | 123.5092 | -123.7061 | -123.6053 | 123.5641 | 123.6511 | 41.7252 | 38.475
370.4844 | 123.7656 | -58.4061 | 65.1398 | 0.15588 | 0.015673 | 0.053517 | 0.076894 | -0.014351 | -0.0071802 | -0.024196 | 0.069594 | -0.0062496 | 0.069957 | 0.064056 | -0.0029502 | 0.0095709 | -0.0017235 | -17.0425 | 65.0986 | -58.5342 | 65.1169 | -57.9529 | -58.6899 | -2.4216 | -20.3979 | 65.1077 | -58.461 | 65.2634 | -58.0627 | -58.4747 | -58.3145 | -0.12817 | -0.041199 | -0.022889 | 0.45319 | 55.9845 | -0.28381 | 56.1127 | -0.15564 | -0.054932 | -0.032044 | 0.1236 | 0.34332 | 0.091553 | -0.068664 | 0.14648 | -0.013732 | 0.58136 | 123.6511 | 0.39825 | 123.7244 | 123.6328 | 123.5687 | 123.5046 | 123.5138 | -123.674 | -123.6008 | 123.5229 | 123.6694 | 41.3635 | 38.0081
371.4844 | 123.7427 | -58.342 | 65.1764 | 0.018551 | 0.0092645 | 0.054585 | 0.072621 | -0.022896 | 0.00029581 | 0.013188 | -0.067735 | -0.011591 | 0.061412 | 0.076874 | -0.013631 | 0.0052979 | -0.019882 | -17.3859 | 65.1169 | -58.5388 | 65.1627 | -57.9071 | -58.6395 | -2.3621 | -20.7413 | 65.1443 | -58.4473 | 65.3091 | -58.0307 | -58.461 | -58.2825 | -0.19684 | -0.05951 | -0.013733 | 0.43488 | 55.9799 | -0.29755 | 56.1768 | -0.10071 | -0.10529 | -0.032044 | 0.13275 | 0.31128 | 0.059509 | -0.11902 | 0.16479 | -0.013733 | 0.63171 | 123.7015 | 0.41656 | 123.7564 | 123.6557 | 123.5916 | 123.4589 | 123.4863 | -123.7152 | -123.6237 | 123.5046 | 123.6511 | 40.9561 | 37.6007
372.4844 | 123.7335 | -58.2504 | 65.2542 | -0.011967 | 0.0060595 | 0.065267 | 0.081166 | 0.0027391 | 0.0035008 | -0.0017664 | 0.039077 | -0.00090962 | 0.089183 | 0.074737 | -0.0082912 | 0.01598 | -0.00065554 | -17.6376 | 65.2039 | -58.4106 | 65.2405 | -57.7972 | -58.5526 | -2.3209 | -20.8282 | 65.2039 | -58.3328 | 65.419 | -57.9163 | -58.342 | -58.1635 | -0.16022 | -0.050354 | -0.013732 | 0.45319 | 55.9296 | -0.30212 | 56.0898 | -0.14191 | -0.082398 | -0.050354 | 0.16479 | 0.33417 | 0.086975 | -0.091553 | 0.16937 | -0.009155 | 0.6134 | 123.6511 | 0.41656 | 123.7518 | 123.6145 | 123.5367 | 123.4543 | 123.4543 | -123.6649 | -123.587 | 123.4909 | 123.6694 | 40.6128 | 37.4222
373.4844 | 123.7335 | -58.1772 | 65.3275 | 0.049069 | 0.0017875 | 0.052449 | 0.072621 | 0.0038071 | 0.0024328 | 0.00037059 | 0.069594 | 0.0033634 | 0.06248 | 0.093963 | -0.0093592 | 0.0074349 | -0.013474 | -17.9306 | 65.3046 | -58.3374 | 65.3503 | -57.6508 | -58.4518 | -2.2385 | -21.1578 | 65.3183 | -58.2504 | 65.4785 | -57.8156 | -58.2642 | -58.1085 | -0.16022 | -0.022889 | 0.022888 | 0.52643 | 55.9387 | -0.27466 | 56.0989 | -0.11444 | -0.073242 | -0.009156 | 0.15106 | 0.36163 | 0.068664 | -0.086975 | 0.14191 | -0.013733 | 0.68664 | 123.6877 | 0.43488 | 123.7289 | 123.642 | 123.5687 | 123.4818 | 123.4955 | -123.6649 | -123.5779 | 123.5275 | 123.6557 | 40.2466 | 37.0193
374.4844 | 123.7152 | -58.1451 | 65.3824 | 0.049069 | -0.0046215 | 0.053517 | 0.076894 | 0.0091481 | 0.0035008 | -0.0049704 | -0.0066996 | 0.0076354 | 0.076366 | 0.067261 | -0.012563 | 0.020252 | -0.014542 | -18.2373 | 65.3091 | -58.2916 | 65.4007 | -57.6004 | -58.3878 | -2.1469 | -21.524 | 65.3732 | -58.2184 | 65.5197 | -57.8018 | -58.223 | -58.0444 | -0.14648 | -0.073242 | 0.018311 | 0.54474 | 55.9982 | -0.24261 | 56.1447 | -0.09613 | -0.073242 | -0.009155 | 0.13733 | 0.34332 | 0.10071 | -0.077819 | 0.17395 | -0.004577 | 0.69122 | 123.6923 | 0.41656 | 123.7381 | 123.6008 | 123.5916 | 123.4543 | 123.5184 | -123.674 | -123.6008 | 123.5458 | 123.6649 | 39.9078 | 36.6211
375.4844 | 123.7747 | -58.0582 | 65.4327 | 0.20166 | -0.0014175 | 0.060994 | 0.070485 | 0.015556 | -0.0050442 | 0.0025066 | 0.7715 | 0.0033634 | 0.077434 | 0.057647 | -0.013631 | 0.0085029 | -0.014542 | -18.5028 | 65.4282 | -58.2001 | 65.4099 | -57.5867 | -58.3832 | -2.0279 | -22.3526 | 65.4602 | -58.136 | 65.6296 | -57.7057 | -58.049 | -57.9208 | -0.14191 | -0.004577 | -0.022888 | 0.4715 | 56.0303 | -0.32501 | 56.1722 | -0.18311 | -0.077819 | 0.027466 | 0.19684 | 0.35248 | 0.13733 | 0.009156 | 0.21515 | 0.086975 | 0.6134 | 123.6099 | 0.4303 | 123.7656 | 123.6282 | 123.5962 | 123.4863 | 123.5184 | -123.6328 | -123.5687 | 123.468 | 123.6877 | 39.5554 | 35.7056
376.4844 | 123.8068 | -58.0261 | 65.4785 | 0.079586 | 0.0039235 | 0.062062 | 0.075825 | 0.0059431 | -0.010385 | -0.0028344 | 0.11537 | -0.0030456 | 0.07423 | 0.053375 | -0.013631 | 0.017048 | 0.0046845 | -19.0018 | 65.419 | -58.2367 | 65.5197 | -57.4356 | -58.2916 | -1.973 | -22.728 | 65.4419 | -58.1314 | 65.6158 | -57.6691 | -58.1314 | -58.049 | -0.21057 | -0.05951 | 0.041198 | 0.59051 | 56.0532 | -0.2655 | 56.2637 | -0.054932 | -0.10529 | -0.036621 | 0.13733 | 0.35706 | -0.022888 | -0.10529 | 0.082398 | 0 | 0.80109 | 123.7564 | 0.46234 | 123.7473 | 123.6557 | 123.5733 | 123.4451 | 123.468 | -123.7152 | -123.6099 | 123.5458 | 123.642 | 39.0244 | 35.2982
377.4844 | 123.7152 | -57.9849 | 65.5518 | 0.1101 | 0.0049915 | 0.050313 | 0.080098 | -0.0047379 | 0.0077728 | 0.0046426 | 0.023818 | 0.0012264 | 0.077434 | 0.057647 | -0.010427 | 0.012775 | -0.0038605 | -19.3817 | 65.5106 | -58.1451 | 65.538 | -57.3807 | -58.2275 | -1.9272 | -23.1949 | 65.5197 | -58.0261 | 65.6708 | -57.5729 | -58.0673 | -57.8842 | -0.16022 | -0.041199 | -0.013733 | 0.60425 | 56.0577 | -0.24262 | 56.218 | -0.082397 | -0.041199 | -0.032044 | 0.11902 | 0.41199 | 0.10071 | -0.082398 | 0.14191 | -0.041199 | 0.76447 | 123.6832 | 0.45319 | 123.6969 | 123.6557 | 123.5458 | 123.4955 | 123.5046 | -123.6969 | -123.5779 | 123.5229 | 123.6557 | 38.6032 | 34.79
378.4844 | 123.7518 | -57.8476 | 65.6204 | -0.011967 | 0.0017875 | 0.050313 | 0.077962 | 0.016624 | -0.00077219 | 0.0099836 | -0.021958 | -0.0019776 | 0.071025 | 0.069397 | -0.0082912 | 0.013843 | -0.019882 | -19.6243 | 65.593 | -58.0215 | 65.593 | -57.3303 | -58.1726 | -1.8265 | -23.4192 | 65.6021 | -57.9666 | 65.7944 | -57.4631 | -57.9391 | -57.7789 | -0.17395 | -0.027465 | -0.027465 | 0.51727 | 56.0211 | -0.32501 | 56.1951 | -0.15106 | -0.11902 | -0.01831 | 0.17395 | 0.38452 | 0.068664 | -0.091553 | 0.18768 | 0.027466 | 0.69122 | 123.6145 | 0.50354 | 123.761 | 123.6145 | 123.5687 | 123.4406 | 123.4497 | -123.642 | -123.587 | 123.4406 | 123.642 | 38.2233 | 34.4284
379.4844 | 123.8022 | -57.7606 | 65.7211 | 0.094845 | 0.011401 | 0.054585 | 0.076894 | 0.0038071 | 0.0024328 | 0.0099836 | -0.098252 | 0.0065674 | 0.066753 | 0.034149 | -0.012563 | 0.022388 | -0.018814 | -19.9677 | 65.6342 | -57.9529 | 65.6662 | -57.2388 | -58.0994 | -1.7441 | -23.6618 | 65.6982 | -57.8842 | 65.7394 | -57.193 | -57.6736 | -57.5821 | -0.19226 | -0.086975 | -0.054931 | 0.52185 | 56.0165 | -0.33874 | 56.2088 | -0.14648 | -0.1236 | -0.022888 | 0.018311 | 0.56763 | 0.17853 | 0.086975 | 0.30212 | 0.21057 | 0.71411 | 123.6191 | 0.69122 | 123.6237 | 123.587 | 123.5825 | 123.3948 | 123.4589 | -123.674 | -123.6053 | 123.4268 | 123.5001 | 37.793 | 34.0988
380.4844 | 123.6877 | -57.7332 | 65.8585 | 0.17114 | 0.0081955 | 0.06313 | 0.077962 | -0.0079419 | -0.0061122 | 0.0035746 | -0.021958 | 0.0022944 | 0.071025 | 0.035217 | -0.011495 | 0.0042299 | -0.0081325 | -20.3979 | 65.8447 | -57.8476 | 65.8997 | -56.9641 | -57.843 | -1.5427 | -24.0097 | 65.8401 | -57.7789 | 65.8997 | -57.3029 | -57.8247 | -57.6782 | -0.11444 | -0.013732 | 0.041199 | 0.76904 | 56.1905 | -0.10986 | 56.3049 | 0.004577 | -0.045777 | -0.01831 | 0.041199 | 0.4303 | 0.054931 | -0.091553 | 0.10071 | -0.045776 | 0.88348 | 123.7473 | 0.47608 | 123.6786 | 123.6923 | 123.6191 | 123.5779 | 123.5733 | -123.7061 | -123.6374 | 123.6328 | 123.6328 | 37.3352 | 33.7234
381.4844 | 123.7518 | -57.6279 | 65.9088 | 0.049069 | -0.00034947 | 0.059926 | 0.074757 | -0.013283 | 0.0067048 | -0.0092424 | 0.0085594 | -0.010523 | 0.071025 | 0.018127 | -0.016836 | 0.0085029 | 0.0014805 | -20.8603 | 65.8173 | -57.7744 | 65.9088 | -56.9687 | -57.8659 | -1.6434 | -24.0921 | 65.8859 | -57.692 | 66.0736 | -57.1335 | -57.6691 | -57.5089 | -0.14648 | -0.091552 | 0 | 0.65918 | 55.9845 | -0.23804 | 56.131 | -0.091553 | -0.064087 | -0.022888 | 0.16479 | 0.49438 | 0.11902 | -0.041198 | 0.18311 | 0.022889 | 0.80566 | 123.6832 | 0.55847 | 123.7656 | 123.5916 | 123.5779 | 123.4451 | 123.5138 | -123.6832 | -123.6008 | 123.5367 | 123.7015 | 36.7676 | 33.5358
382.4844 | 123.7656 | -57.518 | 66.0095 | 0.049069 | 0.0081955 | 0.058858 | 0.076894 | -0.0047379 | 0.0099088 | -0.0071064 | 0.054336 | 0.00015838 | 0.069957 | 0.069397 | -0.011495 | 0.014911 | 0.0068215 | -21.3089 | 65.9637 | -57.6553 | 65.9821 | -56.8542 | -57.7881 | -1.5793 | -24.4034 | 66.0049 | -57.5638 | 66.1697 | -57.0282 | -57.5546 | -57.3944 | -0.13733 | -0.045776 | -0.027465 | 0.66376 | 55.9387 | -0.27008 | 56.076 | -0.13275 | -0.045777 | -0.004577 | 0.16022 | 0.48981 | 0.1236 | -0.036621 | 0.16937 | 0.009156 | 0.80109 | 123.6374 | 0.53558 | 123.7335 | 123.6191 | 123.5687 | 123.4818 | 123.5229 | -123.6649 | -123.5733 | 123.5001 | 123.6877 | 36.2091 | 33.1146
383.4844 | 123.7381 | -57.4081 | 66.156 | 0.064327 | 0.00071953 | 0.052449 | 0.070485 | 0.0006031 | -0.0061122 | -0.010311 | 0.023818 | 0.0022944 | 0.059276 | 0.066192 | -0.0093592 | 0.014911 | -0.018814 | -21.7575 | 66.0965 | -57.5455 | 66.1469 | -56.662 | -57.6187 | -1.3779 | -24.7513 | 66.1057 | -57.4631 | 66.2613 | -56.9046 | -57.4539 | -57.2891 | -0.13733 | -0.059509 | -0.009155 | 0.74615 | 56.0303 | -0.21057 | 56.1676 | -0.073242 | -0.054932 | -0.050354 | 0.10529 | 0.50354 | 0.11902 | -0.045776 | 0.17395 | 0.009156 | 0.88348 | 123.6923 | 0.55847 | 123.7244 | 123.642 | 123.5687 | 123.5046 | 123.5138 | -123.7015 | -123.6191 | 123.555 | 123.6694 | 35.6506 | 32.6569
384.4844 | 123.7335 | -57.2983 | 66.2384 | 0.079586 | 0.0049915 | 0.064198 | 0.073689 | 0.0006031 | -0.026407 | 0.0046426 | 0.069594 | -0.0051816 | 0.060344 | 0.050171 | 0.0034578 | 0.018116 | -0.01561 | -22.1558 | 66.1926 | -57.4265 | 66.2476 | -56.5201 | -57.518 | -1.2817 | -24.8108 | 66.2384 | -57.3669 | 66.3391 | -56.7947 | -57.3486 | -57.1701 | -0.12817 | -0.045776 | 0.009156 | 0.7782 | 56.0165 | -0.21973 | 56.1447 | -0.091552 | -0.068664 | 0 | 0.10071 | 0.50354 | 0.12817 | -0.050354 | 0.19684 | 0.01831 | 0.90637 | 123.674 | 0.5722 | 123.7061 | 123.6191 | 123.6053 | 123.4909 | 123.5367 | -123.6649 | -123.6053 | 123.5458 | 123.6374 | 35.1425 | 32.4875
385.4844 | 123.6511 | -57.2159 | 66.3528 | 0.26269 | 0.0028555 | 0.050313 | 0.072621 | -0.0058059 | 0.0077728 | -0.010311 | -0.11351 | 0.01618 | 0.064617 | 0.054443 | -0.013631 | 0.011707 | -0.0038605 | -22.4808 | 66.3712 | -57.3349 | 66.4581 | -56.2637 | -57.3532 | -0.97046 | -25.2457 | 66.3895 | -57.2708 | 66.4124 | -56.6986 | -57.3074 | -57.1243 | -0.11902 | 0.018311 | 0.10529 | 0.95215 | 56.2454 | -0.13733 | 56.3644 | -0.01831 | -0.054932 | 0.036621 | 0.05951 | 0.51727 | 0.091552 | -0.091553 | 0.14648 | -0.036621 | 1.0712 | 123.793 | 0.5722 | 123.6832 | 123.7061 | 123.6603 | 123.587 | 123.6053 | -123.6877 | -123.6237 | 123.674 | 123.6282 | 34.7351 | 31.9702
386.4844 | 123.7976 | -57.0465 | 66.4398 | 0.079586 | 0.0071275 | 0.058858 | 0.086507 | 0.015556 | 0.0013638 | -0.0060384 | 0.0085594 | 0.0033634 | 0.063548 | 0.033081 | -0.011495 | 0.018116 | -0.0070645 | -22.7692 | 66.4124 | -57.1884 | 66.4261 | -56.3416 | -57.3853 | -1.0803 | -25.296 | 66.4261 | -57.1106 | 66.6229 | -56.4743 | -57.0877 | -56.9 | -0.14191 | -0.027465 | -0.013733 | 0.70496 | 55.9662 | -0.33875 | 56.1081 | -0.19684 | -0.064087 | -0.013733 | 0.18311 | 0.57221 | 0.14648 | -0.041199 | 0.21057 | 0.022888 | 0.84686 | 123.6145 | 0.63629 | 123.7335 | 123.6008 | 123.5367 | 123.4589 | 123.4726 | -123.6282 | -123.5504 | 123.4726 | 123.6694 | 34.2773 | 31.7505
387.4844 | 123.7289 | -56.9778 | 66.5085 | 0.12536 | 0.0092645 | 0.066335 | 0.080098 | -0.0015339 | -0.0061122 | -0.0081744 | 0.0085594 | 0.0044314 | 0.077434 | 0.049103 | -0.0050872 | 0.02132 | -0.018814 | -23.3597 | 66.481 | -57.1564 | 66.5039 | -56.1951 | -57.2525 | -1.0483 | -25.6256 | 66.4856 | -57.0694 | 66.6595 | -56.4331 | -57.0328 | -56.8771 | -0.17853 | -0.027466 | -0.004578 | 0.78278 | 55.9296 | -0.27466 | 56.1081 | -0.09613 | -0.091553 | -0.022888 | 0.15106 | 0.54474 | 0.10071 | -0.054932 | 0.19226 | 0.036621 | 0.9613 | 123.6603 | 0.63629 | 123.7289 | 123.6374 | 123.555 | 123.4589 | 123.4634 | -123.6649 | -123.5779 | 123.4818 | 123.6374 | 33.6182 | 31.3522
388.4844 | 123.7289 | -56.8771 | 66.6275 | -0.011967 | 0.00071953 | 0.071675 | 0.072621 | 0.014488 | -0.0039762 | 0.0025066 | 0.10011 | 0.0022944 | 0.069957 | 0.075805 | -0.0072232 | 0.013843 | 0.0089575 | -23.79 | 66.5955 | -57.0557 | 66.6458 | -56.0074 | -57.0969 | -0.86517 | -25.8408 | 66.6046 | -56.9641 | 66.7694 | -56.3095 | -56.9183 | -56.7673 | -0.17853 | -0.032043 | 0.018311 | 0.86975 | 56.012 | -0.21973 | 56.1905 | -0.041199 | -0.086975 | -0.022888 | 0.14191 | 0.56763 | 0.10986 | -0.041199 | 0.19684 | 0.045776 | 1.0483 | 123.7015 | 0.6546 | 123.7335 | 123.6511 | 123.5687 | 123.4726 | 123.4818 | -123.6832 | -123.5916 | 123.5229 | 123.6465 | 33.0872 | 31.0364
389.4844 | 123.7473 | -56.7719 | 66.7694 | 0.094845 | 0.0081955 | 0.055654 | 0.06728 | 0.016624 | -0.014657 | -0.017787 | 0.023818 | 0.0033634 | 0.073162 | 0.041626 | -0.013631 | 0.017048 | 0.0089575 | -24.1608 | 66.7419 | -56.9092 | 66.7236 | -55.925 | -57.0007 | -0.74616 | -25.9186 | 66.7648 | -56.7947 | 66.9067 | -56.1264 | -56.7719 | -56.6162 | -0.13733 | -0.027466 | -0.045776 | 0.84686 | 56.0257 | -0.22888 | 56.163 | -0.091552 | -0.022888 | -0.004577 | 0.13733 | 0.64545 | 0.15564 | 0 | 0.17853 | 0.022888 | 0.98419 | 123.6328 | 0.66833 | 123.7015 | 123.6511 | 123.5596 | 123.5138 | 123.5367 | -123.6786 | -123.5641 | 123.4955 | 123.6786 | 32.6111 | 30.8533
390.4844 | 123.7885 | -56.6162 | 66.8655 | 0.15588 | 0.0071275 | 0.049245 | 0.074757 | 0.0038071 | -0.0050442 | -0.011379 | 0.17641 | 0.0076354 | 0.080638 | 0.038421 | -0.0061552 | 0.010639 | 0.0068215 | -24.4263 | 66.8564 | -56.7856 | 66.8472 | -55.7648 | -56.9 | -0.65918 | -25.9872 | 66.861 | -56.6849 | 67.0853 | -55.9158 | -56.5796 | -56.4468 | -0.16937 | -0.009156 | -0.018311 | 0.85144 | 55.957 | -0.28381 | 56.1264 | -0.11444 | -0.068664 | -0.004578 | 0.21973 | 0.70038 | 0.16937 | 0.036621 | 0.23804 | 0.10528 | 1.0208 | 123.6328 | 0.76904 | 123.7701 | 123.642 | 123.5458 | 123.4726 | 123.4772 | -123.6511 | -123.5504 | 123.4634 | 123.7015 | 32.1899 | 30.629
391.4844 | 123.7564 | -56.5155 | 66.98 | -0.011967 | -0.0046215 | 0.066335 | 0.081166 | 0.0091481 | -0.012521 | -0.0028344 | 0.023818 | -0.0030456 | 0.066753 | 0.055511 | -0.015768 | -0.0011101 | 0.0025485 | -24.8016 | 66.9342 | -56.694 | 67.0212 | -55.5725 | -56.749 | -0.52643 | -26.3763 | 66.9617 | -56.6071 | 67.1265 | -55.8792 | -56.5567 | -56.4148 | -0.17853 | -0.045776 | 0.041199 | 0.94299 | 55.9891 | -0.23346 | 56.1676 | -0.054931 | -0.091553 | -0.01831 | 0.14648 | 0.63629 | 0.10071 | -0.041199 | 0.19226 | 0.050354 | 1.1215 | 123.7152 | 0.72785 | 123.7335 | 123.6282 | 123.5687 | 123.4497 | 123.4772 | -123.674 | -123.587 | 123.5367 | 123.642 | 31.7139 | 30.1392
392.4844 | 123.7564 | -56.4789 | 67.0166 | 0.049069 | 0.0071275 | 0.070607 | 0.075825 | 0.0091481 | -0.0061122 | -0.0081744 | 0.0085594 | -0.0019776 | 0.056072 | 0.053375 | -0.0018822 | 0.013843 | -0.0070645 | -25.2777 | 66.98 | -56.6208 | 67.0074 | -55.5496 | -56.7261 | -0.49439 | -26.4725 | 67.0212 | -56.5475 | 67.2134 | -55.7739 | -56.4743 | -56.3095 | -0.14191 | -0.036622 | -0.009156 | 0.92926 | 55.9845 | -0.24719 | 56.1264 | -0.10528 | -0.068664 | 0.004577 | 0.19684 | 0.70496 | 0.16937 | 0.004578 | 0.23804 | 0.073242 | 1.0712 | 123.6282 | 0.77362 | 123.761 | 123.6008 | 123.5687 | 123.4589 | 123.5001 | -123.6374 | -123.5641 | 123.4863 | 123.6923 | 31.2012 | 30.0064
393.4844 | 123.7381 | -56.3644 | 67.1036 | 0.064327 | 0.010333 | 0.062062 | 0.077962 | 0.0091481 | 0.014182 | -0.0039024 | -0.037217 | -0.011591 | 0.071025 | 0.066192 | -0.010427 | 0.017048 | -0.016678 | -25.6073 | 67.0944 | -56.5247 | 67.131 | -55.4123 | -56.6071 | -0.39368 | -26.6647 | 67.1265 | -56.4468 | 67.3279 | -55.632 | -56.3416 | -56.1813 | -0.16022 | -0.009156 | 0.027465 | 0.95215 | 55.9708 | -0.24262 | 56.131 | -0.082398 | -0.082397 | 0.022888 | 0.2243 | 0.73242 | 0.18311 | 0.022888 | 0.2655 | 0.10529 | 1.1124 | 123.6557 | 0.81482 | 123.7747 | 123.6191 | 123.5733 | 123.4589 | 123.4909 | -123.6282 | -123.5504 | 123.4955 | 123.6923 | 30.7571 | 29.6997
394.4844 | 123.674 | -56.2592 | 67.3233 | 0.12536 | 0.0017875 | 0.056722 | 0.080098 | -0.0026019 | -0.0039762 | 0.0089146 | 0.069594 | 0.0012264 | 0.076366 | 0.077942 | -0.012563 | 0.014911 | 0.015366 | -25.8636 | 67.3279 | -56.3507 | 67.4057 | -55.0461 | -56.2912 | -0.068665 | -26.9073 | 67.3416 | -56.3187 | 67.3782 | -55.5725 | -56.3004 | -56.1264 | -0.091553 | 0.004578 | 0.082398 | 1.2131 | 56.1905 | -0.032044 | 56.282 | 0.059509 | -0.05951 | 0.018311 | 0.054932 | 0.68664 | 0.13275 | -0.041199 | 0.19226 | 0.018311 | 1.3046 | 123.7564 | 0.74616 | 123.6969 | 123.6786 | 123.6603 | 123.587 | 123.6008 | -123.674 | -123.642 | 123.6649 | 123.6374 | 30.3955 | 29.3518
395.4844 | 123.6603 | -56.0394 | 67.5476 | 0.23217 | -0.0024855 | 0.056722 | 0.069417 | 0.0016711 | -0.00077219 | -0.0092424 | 0.14589 | 0.0087034 | 0.076366 | 0.060852 | -0.0050872 | 0.017048 | -0.0027915 | -25.8591 | 67.5156 | -56.1813 | 67.5934 | -54.8309 | -56.1172 | 0.15564 | -26.7197 | 67.5201 | -56.1218 | 67.5797 | -55.3116 | -56.0761 | -55.9433 | -0.14191 | -0.032043 | 0.045777 | 1.2085 | 56.1951 | -0.07782 | 56.337 | 0.064086 | -0.082397 | -0.027465 | 0.032044 | 0.72784 | 0.096131 | -0.036621 | 0.17853 | 0.045776 | 1.3504 | 123.7747 | 0.81024 | 123.7015 | 123.6969 | 123.642 | 123.555 | 123.5596 | -123.7289 | -123.6694 | 123.6328 | 123.6191 | 30.1804 | 29.3198
396.4844 | 123.7335 | -55.9525 | 67.5659 | 0.049069 | 0.0092645 | 0.056722 | 0.070485 | -0.011147 | 0.0013638 | -0.0081744 | 0.054336 | 0.0033634 | 0.060344 | 0.046966 | -0.0040182 | 0.0095709 | -0.00065554 | -26.0788 | 67.5064 | -56.1035 | 67.5522 | -54.8538 | -56.1539 | 0.10529 | -26.8982 | 67.5522 | -56.0303 | 67.7124 | -55.1743 | -55.9433 | -55.7877 | -0.15106 | -0.059509 | -0.013733 | 1.0986 | 56.0577 | -0.20142 | 56.2088 | -0.050354 | -0.077819 | -0.013733 | 0.14648 | 0.7782 | 0.1648 | 0.009156 | 0.24261 | 0.086975 | 1.2497 | 123.6557 | 0.85602 | 123.7427 | 123.6099 | 123.5825 | 123.4589 | 123.5046 | -123.6694 | -123.5962 | 123.5046 | 123.6649 | 29.8737 | 29.0543
397.4844 | 123.7656 | -55.7739 | 67.7856 | -0.011967 | 0.011401 | 0.060994 | 0.074757 | -0.013283 | 0.0067048 | -0.00069841 | 0.14589 | 0.0022944 | 0.066753 | 0.046966 | -0.0072232 | 0.017048 | -0.0070645 | -26.3077 | 67.7216 | -55.9158 | 67.7673 | -54.5837 | -55.9662 | 0.30212 | -26.8753 | 67.7353 | -55.8243 | 67.8864 | -54.9454 | -55.7281 | -55.5862 | -0.14191 | -0.064087 | -0.018311 | 1.1902 | 56.0761 | -0.19226 | 56.218 | -0.050354 | -0.050354 | -0.050354 | 0.10071 | 0.82855 | 0.18768 | 0.045777 | 0.23804 | 0.096131 | 1.3321 | 123.6832 | 0.87891 | 123.7106 | 123.6374 | 123.5596 | 123.4955 | 123.5092 | -123.7015 | -123.6099 | 123.5413 | 123.6603 | 29.4662 | 28.8986
398.4844 | 123.7427 | -55.6137 | 67.9413 | 0.064327 | 0.010333 | 0.05779 | 0.082234 | -0.010078 | -0.0093172 | 0.00037059 | 0.10011 | -0.0083866 | 0.064617 | 0.018127 | -0.0050872 | 0.0031619 | 0.0025485 | -26.3809 | 67.8589 | -55.7877 | 67.9138 | -54.4235 | -55.7922 | 0.42572 | -26.9211 | 67.8955 | -55.687 | 68.0191 | -54.8035 | -55.6137 | -55.4352 | -0.17395 | -0.082397 | -0.027466 | 1.1902 | 56.0394 | -0.17853 | 56.2134 | -0.004577 | -0.073243 | -0.045776 | 0.07782 | 0.81024 | 0.17853 | 0 | 0.25177 | 0.073243 | 1.3641 | 123.7015 | 0.88348 | 123.7061 | 123.6465 | 123.5825 | 123.4726 | 123.5092 | -123.7289 | -123.6282 | 123.5275 | 123.6328 | 29.2328 | 28.6926
399.4844 | 123.6694 | -55.513 | 68.0557 | 0.24743 | 0.0060595 | 0.064198 | 0.072621 | 0.010216 | -0.0029082 | -0.0028344 | 0.054336 | 0.021521 | 0.072093 | 0.075805 | -0.0082912 | 0.013843 | -0.011337 | -26.5732 | 68.0145 | -55.687 | 68.129 | -54.1397 | -55.5862 | 0.59509 | -26.9989 | 68.0878 | -55.6 | 68.1061 | -54.6799 | -55.5222 | -55.3894 | -0.17395 | -0.041199 | 0.073242 | 1.3733 | 56.1081 | -0.073243 | 56.282 | 0.10071 | -0.086976 | 0.032044 | 0.050354 | 0.83313 | 0.1236 | -0.009156 | 0.21057 | 0.07782 | 1.5472 | 123.8159 | 0.9201 | 123.7061 | 123.7015 | 123.6877 | 123.5275 | 123.6008 | -123.7427 | -123.6557 | 123.642 | 123.6191 | 28.9398 | 28.5141
400.4844 | 123.8251 | -55.3574 | 68.1519 | 0.12536 | 0.0017875 | 0.059926 | 0.06194 | 0.014488 | -0.0050442 | -0.0017664 | 0.29848 | -0.0030456 | 0.056072 | 0.073669 | -0.0093592 | 0.013843 | -0.0038605 | -26.6876 | 68.1198 | -55.5313 | 68.1015 | -54.1672 | -55.5954 | 0.60883 | -26.9485 | 68.1107 | -55.4352 | 68.367 | -54.3961 | -55.2521 | -55.1376 | -0.17395 | -0.032043 | -0.050354 | 1.1902 | 55.9662 | -0.23804 | 56.1401 | -0.064087 | -0.07782 | -0.041198 | 0.21515 | 0.9613 | 0.21973 | 0.10529 | 0.29755 | 0.18311 | 1.3641 | 123.6328 | 1.0391 | 123.8022 | 123.6511 | 123.5458 | 123.4772 | 123.468 | -123.6832 | -123.587 | 123.4589 | 123.7244 | 28.6697 | 28.4088
401.4844 | 123.7381 | -55.1697 | 68.335 | 0.018551 | 0.0081955 | 0.052449 | 0.070485 | -0.0015339 | -0.0050442 | -0.011379 | 0.13063 | 0.00015838 | 0.066753 | 0.091827 | -0.013631 | 0.0042299 | -0.0081325 | -26.7609 | 68.2571 | -55.3711 | 68.3441 | -53.8696 | -55.3665 | 0.82398 | -26.9073 | 68.3212 | -55.275 | 68.4631 | -54.2816 | -55.1651 | -54.9866 | -0.20142 | -0.07782 | 0.009155 | 1.3 | 55.9937 | -0.19684 | 56.1951 | 0.004578 | -0.10529 | -0.013733 | 0.12817 | 0.88806 | 0.18311 | 0.004578 | 0.28839 | 0.10986 | 1.5015 | 123.7152 | 0.99335 | 123.7381 | 123.6282 | 123.5962 | 123.4268 | 123.4909 | -123.7061 | -123.6099 | 123.5138 | 123.6328 | 28.4088 | 28.2623
402.4844 | 123.7473 | -55.1102 | 68.4128 | 0.03381 | 0.017809 | 0.05779 | 0.076894 | -0.014351 | -0.0071802 | 0.0035746 | -0.021958 | -0.0019776 | 0.071025 | 0.071533 | -0.018972 | 0.0085029 | -0.0070645 | -26.9028 | 68.3716 | -55.2612 | 68.4174 | -53.7415 | -55.2612 | 0.87891 | -26.9302 | 68.3899 | -55.1743 | 68.5272 | -54.1763 | -55.0598 | -54.9133 | -0.15106 | -0.041199 | 0.004577 | 1.3687 | 55.9891 | -0.15106 | 56.1401 | 0 | -0.064087 | -0.022888 | 0.11444 | 0.93384 | 0.19684 | 0.050354 | 0.26093 | 0.11444 | 1.5198 | 123.6786 | 0.99792 | 123.7015 | 123.6328 | 123.5641 | 123.4818 | 123.5001 | -123.674 | -123.587 | 123.5275 | 123.6374 | 28.2074 | 28.1799
403.4844 | 123.7061 | -54.9637 | 68.573 | 0.14062 | 0.0071275 | 0.062062 | 0.08437 | -0.0015339 | 0.0077728 | 0.0089146 | 0.054336 | -0.0030456 | 0.058208 | 0.092895 | -0.0072232 | 0.010639 | 0.0025485 | -26.9577 | 68.5135 | -55.1285 | 68.5593 | -53.5629 | -55.1193 | 1.062 | -26.5594 | 68.5547 | -55.0552 | 68.7057 | -53.9474 | -54.8813 | -54.7623 | -0.16479 | -0.059509 | -0.013733 | 1.4008 | 56.0257 | -0.15564 | 56.1905 | 0.009155 | -0.091553 | -0.018311 | 0.13275 | 1.0162 | 0.20142 | 0.082397 | 0.29297 | 0.17395 | 1.5656 | 123.6877 | 1.1078 | 123.761 | 123.642 | 123.6099 | 123.4772 | 123.5184 | -123.7015 | -123.6282 | 123.5229 | 123.6694 | 28.006 | 28.4042
404.4844 | 123.6923 | -54.8538 | 68.7057 | 0.094845 | 0.0028555 | 0.064198 | 0.077962 | 0.0091481 | -0.0018402 | 0.0067786 | -0.067735 | 0.0065674 | 0.065685 | 0.0961 | -0.0147 | 0.010639 | -0.0038605 | -27.0401 | 68.7241 | -55.0186 | 68.8156 | -53.2516 | -54.8676 | 1.3733 | -26.6464 | 68.7286 | -54.8859 | 68.7881 | -53.8101 | -54.8172 | -54.6616 | -0.16479 | 0.01831 | 0.10986 | 1.6022 | 56.2271 | -0.013733 | 56.3919 | 0.15106 | -0.032043 | 0.022888 | 0.082397 | 1.0437 | 0.19226 | 0.036621 | 0.2243 | 0.068664 | 1.767 | 123.8342 | 1.0757 | 123.674 | 123.7427 | 123.6145 | 123.5779 | 123.5825 | -123.7244 | -123.5916 | 123.6694 | 123.642 | 27.8137 | 28.2074
405.4844 | 123.7381 | -54.6112 | 68.9346 | 0.1864 | 0.0049915 | 0.065267 | 0.077962 | 0.0027391 | -0.011453 | 0.0035746 | 0.14589 | 0.00015838 | 0.072093 | 0.065124 | -0.0050872 | 0.014911 | -0.00065554 | -26.8387 | 68.8614 | -54.7668 | 68.8843 | -53.1464 | -54.8035 | 1.5747 | -26.2711 | 68.8889 | -54.689 | 69.0537 | -53.4805 | -54.4922 | -54.3823 | -0.15564 | -0.073242 | -0.050354 | 1.4648 | 56.1859 | -0.19226 | 56.3416 | -0.036621 | -0.07782 | -0.045776 | 0.11902 | 1.1307 | 0.22888 | 0.11902 | 0.3067 | 0.19684 | 1.6205 | 123.6511 | 1.2085 | 123.7427 | 123.6282 | 123.5779 | 123.4726 | 123.5001 | -123.7015 | -123.6237 | 123.4955 | 123.6649 | 27.7725 | 28.3401
406.4844 | 123.7518 | -54.4464 | 69.0445 | -0.042484 | 0.016741 | 0.070607 | 0.072621 | -0.0015339 | -0.0082492 | 0.013188 | 0.069594 | -0.00090962 | 0.071025 | 0.055511 | -0.0093592 | 0.0074349 | 0.0078895 | -26.7105 | 68.9987 | -54.6066 | 69.0079 | -52.9449 | -54.6478 | 1.7715 | -26.1658 | 69.0262 | -54.538 | 69.2047 | -53.3249 | -54.3732 | -54.2358 | -0.16022 | -0.045777 | -0.036621 | 1.5015 | 56.218 | -0.20142 | 56.3782 | -0.041199 | -0.091553 | -0.018311 | 0.16022 | 1.1215 | 0.21057 | 0.073242 | 0.30212 | 0.1648 | 1.6617 | 123.6145 | 1.2131 | 123.7427 | 123.6053 | 123.5641 | 123.4451 | 123.4726 | -123.6511 | -123.5825 | 123.4543 | 123.6511 | 27.7359 | 28.2806
407.4844 | 123.7427 | -54.332 | 69.1864 | 0.064327 | 0.011401 | 0.062062 | 0.086507 | 0.0016711 | 0.0013638 | 0.0025066 | 0.13063 | 0.0087034 | 0.080638 | 0.060852 | -0.023245 | 0.012775 | -0.017746 | -26.7609 | 69.1498 | -54.4922 | 69.2001 | -52.6932 | -54.4556 | 1.9821 | -26.1749 | 69.1772 | -54.4144 | 69.3146 | -53.1555 | -54.2358 | -54.1031 | -0.16022 | -0.036621 | 0.013733 | 1.6388 | 56.3141 | -0.1236 | 56.4743 | 0.036621 | -0.082398 | -0.009155 | 0.12817 | 1.1765 | 0.22888 | 0.09613 | 0.31128 | 0.17853 | 1.799 | 123.6923 | 1.2589 | 123.7289 | 123.642 | 123.5916 | 123.4818 | 123.5092 | -123.6786 | -123.6008 | 123.5321 | 123.6465 | 27.5711 | 28.157
408.4844 | 123.7473 | -54.1855 | 69.3375 | 0.049069 | 0.0039235 | 0.053517 | 0.07903 | 0.0006031 | 0.0056368 | 0.0046426 | 0.0085594 | 0.012976 | 0.080638 | 0.077942 | -0.018972 | 0.01598 | -0.00065554 | -26.825 | 69.3054 | -54.3365 | 69.3649 | -52.478 | -54.2816 | 2.0828 | -25.8682 | 69.3146 | -54.2587 | 69.4565 | -52.9404 | -54.071 | -53.9703 | -0.15106 | -0.032043 | 0.027466 | 1.7075 | 56.2683 | -0.09613 | 56.4194 | 0.054932 | -0.073242 | -0.022888 | 0.11902 | 1.2451 | 0.21515 | 0.11444 | 0.28839 | 0.18768 | 1.8585 | 123.7015 | 1.3184 | 123.7152 | 123.642 | 123.5733 | 123.4909 | 123.5001 | -123.674 | -123.5962 | 123.5504 | 123.642 | 27.3605 | 28.3173
409.4844 | 123.6465 | -54.0344 | 69.5572 | 0.23217 | -0.0046215 | 0.058858 | 0.077962 | 0.016624 | -0.00077219 | -0.0071064 | -0.12877 | 0.0076354 | 0.063548 | 0.060852 | -0.0147 | 0.018116 | -0.00065554 | -26.8341 | 69.5206 | -54.1672 | 69.8593 | -52.0523 | -54.1168 | 2.2293 | -25.6302 | 69.5435 | -54.0756 | 69.5892 | -52.7985 | -53.9658 | -53.8376 | -0.13275 | -0.036621 | 0.30212 | 1.9821 | 56.2637 | -0.082397 | 56.3965 | 0.050354 | -0.041199 | -0.013733 | 0.032043 | 1.236 | 0.19684 | 0.068665 | 0.23804 | 0.10986 | 2.1149 | 124.0265 | 1.2772 | 123.6649 | 123.6877 | 123.6191 | 123.555 | 123.5779 | -123.7244 | -123.6328 | 123.8937 | 123.6237 | 27.2003 | 28.4042
410.4844 | 123.8068 | -53.8376 | 69.6808 | 0.03381 | 0.0028555 | 0.053517 | 0.066212 | 0.0006031 | 0.012046 | 0.015324 | 0.26796 | 0.0097714 | 0.078502 | 0.073669 | -0.016836 | 0.018116 | 0.010025 | -26.6785 | 69.6487 | -53.9886 | 69.6625 | -52.0706 | -53.9978 | 2.3849 | -25.2686 | 69.6442 | -53.92 | 69.8502 | -52.4414 | -53.6591 | -53.5629 | -0.15106 | -0.032043 | -0.01831 | 1.767 | 56.2225 | -0.16022 | 56.3736 | -0.009156 | -0.082398 | -0.036621 | 0.16937 | 1.3962 | 0.27466 | 0.17853 | 0.35706 | 0.26093 | 1.918 | 123.6511 | 1.4786 | 123.7701 | 123.6374 | 123.5641 | 123.4863 | 123.4818 | -123.6694 | -123.6008 | 123.5001 | 123.6877 | 27.1591 | 28.569
411.4844 | 123.7335 | -53.7231 | 69.7906 | 0.049069 | 0.0081955 | 0.062062 | 0.075825 | -0.017555 | -0.010385 | -0.020992 | 0.10011 | -0.0041136 | 0.056072 | 0.065124 | -0.0082912 | 0.017048 | -0.0017235 | -26.7654 | 69.7266 | -53.8879 | 69.8044 | -51.8875 | -53.8559 | 2.5406 | -25.145 | 69.7678 | -53.8147 | 69.9097 | -52.3361 | -53.6133 | -53.4851 | -0.16479 | -0.064087 | 0.013733 | 1.8356 | 56.2637 | -0.13275 | 56.4285 | 0.032043 | -0.091552 | -0.022888 | 0.11902 | 1.387 | 0.23804 | 0.10986 | 0.32959 | 0.20142 | 2.0004 | 123.6923 | 1.4786 | 123.7244 | 123.6145 | 123.5825 | 123.4497 | 123.4909 | -123.6786 | -123.6053 | 123.5275 | 123.6328 | 26.9577 | 28.5782
412.4844 | 123.7793 | -53.5767 | 69.9234 | -0.011967 | 0.012469 | 0.05779 | 0.087575 | -0.0026019 | -0.017862 | -0.0092424 | 0.14589 | 0.0076354 | 0.077434 | 0.059784 | -0.013631 | 0.014911 | -0.013474 | -26.6922 | 69.8639 | -53.7415 | 69.873 | -51.7502 | -53.7369 | 2.7237 | -24.939 | 69.8959 | -53.6545 | 70.0745 | -52.0889 | -53.421 | -53.302 | -0.1648 | -0.059509 | -0.050354 | 1.8265 | 56.3004 | -0.16022 | 56.4651 | 0.004578 | -0.07782 | -0.027466 | 0.15106 | 1.4877 | 0.27466 | 0.15564 | 0.35248 | 0.23346 | 1.9913 | 123.6145 | 1.5656 | 123.7289 | 123.6053 | 123.5504 | 123.4406 | 123.4726 | -123.6649 | -123.5779 | 123.4497 | 123.6511 | 26.8845 | 28.6377
413.4844 | 123.7564 | -53.2379 | 70.2576 | 0.12536 | 0.011401 | 0.064198 | 0.07903 | 0.0091481 | -0.010385 | -0.00069841 | 0.054336 | 0.0087034 | 0.071025 | 0.041626 | -0.0072232 | 0.012775 | 0.0046845 | -26.6556 | 70.1797 | -53.4164 | 70.2209 | -51.3199 | -53.3844 | 2.9617 | -25.946 | 70.2484 | -53.3295 | 70.4086 | -51.0269 | -53.1097 | -52.9724 | -0.17853 | -0.077819 | -0.036621 | 1.918 | 56.1996 | -0.14648 | 56.3782 | 0.032044 | -0.091553 | -0.009155 | 0.15106 | 2.211 | 0.2655 | 0.12817 | 0.35706 | 0.21973 | 2.0966 | 123.6374 | 2.3026 | 123.7381 | 123.5962 | 123.5779 | 123.4177 | 123.4863 | -123.674 | -123.587 | 123.4589 | 123.6465 | 26.5823 | 27.2919
414.4844 | 123.7564 | -52.9037 | 70.5917 | 0.1864 | 0.0039235 | 0.062062 | 0.072621 | -0.0079419 | 0.0024328 | -0.015651 | 0.2527 | 0.0097714 | 0.069957 | 0.04483 | -0.015768 | 0.0052979 | -0.0092005 | -26.1887 | 70.546 | -53.0731 | 70.5688 | -50.9262 | -53.0457 | 3.3691 | -25.6027 | 70.5643 | -53.0136 | 70.752 | -50.4135 | -52.6657 | -52.597 | -0.16937 | -0.045777 | -0.022888 | 1.9775 | 56.2729 | -0.14191 | 56.4423 | 0.027466 | -0.10986 | -0.027466 | 0.16022 | 2.4902 | 0.3067 | 0.23804 | 0.41656 | 0.3479 | 2.1469 | 123.642 | 2.6001 | 123.7656 | 123.6191 | 123.5779 | 123.4497 | 123.468 | -123.6649 | -123.6053 | 123.4726 | 123.6557 | 26.7151 | 27.301
415.4844 | 123.7564 | -52.7939 | 70.7565 | 0.1864 | 0.0092645 | 0.054585 | 0.07903 | 0.0048751 | -0.03602 | 0.0046426 | 0.16115 | 0.0033634 | 0.075298 | 0.077942 | -0.013631 | 0.014911 | -0.0070645 | -26.0834 | 70.6696 | -52.9541 | 70.7108 | -50.6973 | -52.8854 | 3.6255 | -25.1678 | 70.7291 | -52.8625 | 70.8664 | -50.2533 | -52.5879 | -52.4734 | -0.16022 | -0.086975 | -0.045777 | 2.0966 | 56.4194 | -0.091553 | 56.5796 | 0.068665 | -0.068665 | -0.027466 | 0.10986 | 2.5406 | 0.32043 | 0.20599 | 0.3891 | 0.27466 | 2.2568 | 123.6649 | 2.6093 | 123.7289 | 123.6237 | 123.5916 | 123.4634 | 123.5229 | -123.7106 | -123.6191 | 123.5046 | 123.6603 | 26.7105 | 27.626
416.4844 | 123.7244 | -52.4918 | 71.0449 | 0.0032924 | 0.010333 | 0.05779 | 0.081166 | 0.0080791 | -0.014657 | -0.0092424 | 0.0085594 | 0.0022944 | 0.065685 | 0.06192 | -0.02004 | 0.018116 | -0.0049285 | -25.7492 | 70.9671 | -52.6566 | 71.0129 | -50.3357 | -52.5833 | 3.8452 | -24.6552 | 71.0175 | -52.5421 | 71.1548 | -49.8459 | -52.2949 | -52.1942 | -0.16479 | -0.07782 | -0.032044 | 2.1561 | 56.337 | -0.091553 | 56.5018 | 0.073242 | -0.050354 | -0.027466 | 0.10986 | 2.6459 | 0.29755 | 0.19684 | 0.3479 | 0.24719 | 2.3209 | 123.6694 | 2.6962 | 123.6969 | 123.6237 | 123.5596 | 123.4589 | 123.5092 | -123.7015 | -123.587 | 123.5046 | 123.6465 | 26.7426 | 27.8366
417.4844 | 123.7244 | -52.4323 | 71.1044 | 0.12536 | 0.00071953 | 0.069539 | 0.081166 | 0.0091481 | 0.0056368 | -0.013515 | 0.20692 | 0.010839 | 0.072093 | 0.092895 | -0.013631 | 0.010639 | 0.026047 | -25.6851 | 71.0861 | -52.5696 | 71.1182 | -50.1343 | -52.4689 | 4.0558 | -24.6323 | 71.077 | -52.4643 | 71.2097 | -49.6628 | -52.2263 | -52.121 | -0.13733 | -0.01831 | 0.013733 | 2.298 | 56.488 | -0.036621 | 56.6254 | 0.10071 | -0.032043 | -0.027466 | 0.10529 | 2.7695 | 0.31128 | 0.20599 | 0.34332 | 0.23804 | 2.4353 | 123.6877 | 2.8015 | 123.674 | 123.6557 | 123.5413 | 123.5184 | 123.5092 | -123.674 | -123.5687 | 123.5504 | 123.642 | 26.7471 | 27.8
418.4844 | 123.7244 | -52.2537 | 71.2509 | 0.049069 | 0.0092645 | 0.04604 | 0.074757 | -0.0004649 | -0.013589 | -0.0017664 | 0.14589 | 0.0097714 | 0.055004 | 0.060852 | -0.0040182 | 0.012775 | 0.00041246 | -25.4425 | 71.2234 | -52.4048 | 71.2921 | -49.8596 | -52.2949 | 4.2297 | -24.3301 | 71.2555 | -52.3407 | 71.3882 | -49.3423 | -52.0432 | -51.9562 | -0.15106 | -0.027466 | 0.041198 | 2.3941 | 56.4835 | -0.041199 | 56.6345 | 0.10986 | -0.086975 | 0.004577 | 0.13733 | 2.9114 | 0.29755 | 0.21057 | 0.38452 | 0.29755 | 2.5452 | 123.6969 | 2.9984 | 123.7289 | 123.6282 | 123.5962 | 123.4772 | 123.5092 | -123.6557 | -123.5916 | 123.5458 | 123.642 | 26.8112 | 27.9236
419.4844 | 123.8205 | -51.9882 | 71.521 | 0.03381 | 0.00071953 | 0.059926 | 0.077962 | 0.0038071 | -0.016794 | 0.0057106 | 0.20692 | -0.0062496 | 0.072093 | 0.042694 | -0.00081422 | 0.019184 | -0.010269 | -25.1038 | 71.5073 | -52.1439 | 71.4661 | -49.6353 | -52.1027 | 4.4495 | -23.9365 | 71.489 | -52.066 | 71.7133 | -49.8093 | -51.6495 | -51.622 | -0.15564 | -0.013733 | -0.054932 | 2.3529 | 56.4377 | -0.11444 | 56.5933 | 0.041199 | -0.07782 | -0.032043 | 0.19226 | 2.179 | 0.36621 | 0.33874 | 0.44403 | 0.41656 | 2.5085 | 123.6099 | 2.2568 | 123.7793 | 123.6511 | 123.555 | 123.4955 | 123.4772 | -123.6649 | -123.587 | 123.4543 | 123.7015 | 26.8845 | 28.0518
420.4844 | 123.7885 | -51.8417 | 71.6858 | 0.12536 | 0.0017875 | 0.041768 | 0.068349 | -0.0058059 | -0.0029082 | -0.0017664 | -0.14403 | 0.0076354 | 0.068889 | 0.062988 | -0.015768 | 0.014911 | -0.029495 | -24.8795 | 71.6583 | -51.9745 | 71.6537 | -49.4751 | -51.86 | 4.8569 | -23.7671 | 71.6492 | -51.9333 | 71.8826 | -49.9146 | -51.503 | -51.4709 | -0.13275 | -0.027466 | -0.032043 | 2.3666 | 56.6986 | -0.01831 | 56.8314 | 0.11444 | -0.091553 | -0.036621 | 0.19684 | 1.9272 | 0.37079 | 0.33874 | 0.46234 | 0.4303 | 2.4994 | 123.6282 | 2.0187 | 123.8159 | 123.6328 | 123.5825 | 123.5001 | 123.4909 | -123.6603 | -123.6191 | 123.4955 | 123.7244 | 26.9623 | 28.0746
421.4844 | 123.7518 | -51.6174 | 71.9193 | 0.094845 | 0.0081955 | 0.060994 | 0.083302 | -0.0015339 | 0.019522 | -0.010311 | 0.11537 | 0.0054994 | 0.064617 | 0.06192 | -0.012563 | 0.022388 | 0.0078895 | -24.678 | 71.8506 | -51.7776 | 71.8689 | -49.0128 | -51.6495 | 4.8614 | -23.4512 | 71.8826 | -51.709 | 72.02 | -49.7177 | -51.3657 | -51.2741 | -0.16022 | -0.068664 | -0.050354 | 2.6047 | 56.4789 | -0.032043 | 56.6391 | 0.12817 | -0.091552 | -0.036621 | 0.10071 | 1.8997 | 0.34332 | 0.25177 | 0.43487 | 0.34332 | 2.7649 | 123.6465 | 1.9913 | 123.7289 | 123.6282 | 123.5916 | 123.468 | 123.5001 | -123.6969 | -123.6282 | 123.4863 | 123.6374 | 26.9394 | 28.1662
422.4844 | 123.7335 | -51.5625 | 71.9559 | 0.20166 | 0.00071953 | 0.058858 | 0.088643 | -0.0004649 | -0.00077219 | 0.01212 | -0.0066996 | 0.0087034 | 0.072093 | 0.073669 | -0.024313 | 0.017048 | 0.00041246 | -24.4812 | 71.8918 | -51.7273 | 71.9284 | -48.88 | -51.6083 | 4.9438 | -23.3688 | 71.9284 | -51.6449 | 72.1069 | -49.5895 | -51.297 | -51.2192 | -0.16479 | -0.064087 | -0.027466 | 2.6825 | 56.5063 | -0.045776 | 56.6711 | 0.11902 | -0.082397 | -0.027466 | 0.15106 | 1.973 | 0.34332 | 0.2655 | 0.42572 | 0.3479 | 2.8473 | 123.6557 | 2.0554 | 123.7518 | 123.6191 | 123.5733 | 123.4543 | 123.4909 | -123.6832 | -123.6008 | 123.4909 | 123.6694 | 27.0813 | 28.1937
423.4844 | 123.7335 | -51.3657 | 72.1298 | 0.018551 | -0.00034947 | 0.048177 | 0.073689 | -0.0036699 | -0.0071802 | -0.010311 | 0.0085594 | 0.0076354 | 0.053935 | 0.083282 | -0.010427 | 0.01598 | -0.00065554 | -24.2065 | 72.0886 | -51.5396 | 72.1298 | -48.5092 | -51.384 | 5.1956 | -23.1995 | 72.1161 | -51.4847 | 72.2717 | -49.3973 | -51.0956 | -51.0269 | -0.17395 | -0.041199 | 0 | 2.8564 | 56.5613 | -0.01831 | 56.7352 | 0.15564 | -0.11902 | -0.013733 | 0.14191 | 1.9684 | 0.33875 | 0.27008 | 0.45776 | 0.3891 | 3.0304 | 123.6694 | 2.0874 | 123.7564 | 123.6282 | 123.6008 | 123.4543 | 123.4818 | -123.6694 | -123.6145 | 123.4955 | 123.6374 | 27.1591 | 28.1662
424.4844 | 123.7381 | -51.2833 | 72.2214 | 0.049069 | 0.0049915 | 0.064198 | 0.088643 | 0.0016711 | -0.015725 | -0.0017664 | 0.11537 | 0.0022944 | 0.077434 | 0.053375 | -0.023245 | 0.02132 | 0.00041246 | -23.8953 | 72.1939 | -51.416 | 72.226 | -48.3307 | -51.265 | 5.3787 | -22.8607 | 72.2534 | -51.329 | 72.3495 | -49.2691 | -50.9674 | -50.9079 | -0.13275 | -0.027466 | 0.004577 | 2.9526 | 56.662 | 0.01831 | 56.7947 | 0.15106 | -0.045777 | 0.032043 | 0.12817 | 2.0142 | 0.37537 | 0.31586 | 0.42114 | 0.36163 | 3.0853 | 123.642 | 2.0599 | 123.6786 | 123.6099 | 123.5825 | 123.4772 | 123.5367 | -123.6374 | -123.5504 | 123.5092 | 123.6328 | 27.388 | 28.4225
425.4844 | 123.793 | -50.9171 | 72.551 | 0.018551 | 0.0081955 | 0.058858 | 0.082234 | 0.0080791 | -0.0029082 | -0.018856 | 0.20692 | 0.0065674 | 0.084911 | 0.057647 | -0.0147 | 0.023456 | -0.027359 | -23.4787 | 72.5235 | -51.0864 | 72.5143 | -47.9599 | -50.9857 | 5.722 | -22.0963 | 72.5327 | -50.9995 | 72.6746 | -48.7427 | -50.6195 | -50.4776 | -0.16937 | -0.027465 | -0.036621 | 2.9572 | 56.6391 | -0.068665 | 56.8085 | 0.10071 | -0.082398 | -0.01831 | 0.1236 | 2.1744 | 0.43945 | 0.29755 | 0.52185 | 0.37994 | 3.1265 | 123.6008 | 2.2568 | 123.674 | 123.6099 | 123.5321 | 123.4406 | 123.4497 | -123.6374 | -123.5504 | 123.4314 | 123.5916 | 27.4384 | 28.8208
426.4844 | 123.7564 | -50.9399 | 72.5601 | 0.049069 | 0.0092645 | 0.069539 | 0.077962 | -0.0079419 | 0.013114 | -0.014583 | -0.14403 | 0.0065674 | 0.063548 | 0.10892 | -0.02004 | 0.020252 | -0.011337 | -23.5062 | 72.496 | -51.1093 | 72.4457 | -48.0469 | -51.0864 | 5.9418 | -22.197 | 72.5464 | -50.9949 | 72.7341 | -48.7427 | -50.5463 | -50.4913 | -0.16937 | -0.064087 | -0.11444 | 2.8931 | 56.8817 | -0.14649 | 57.0511 | 0.022888 | -0.054932 | -0.013733 | 0.17395 | 2.1973 | 0.44861 | 0.39368 | 0.50354 | 0.44861 | 3.0624 | 123.555 | 2.2522 | 123.7289 | 123.6053 | 123.5413 | 123.436 | 123.4863 | -123.6694 | -123.555 | 123.3856 | 123.674 | 27.4338 | 28.743
427.4844 | 123.761 | -50.7523 | 72.7432 | -0.027225 | 0.0081955 | 0.069539 | 0.082234 | 0.0027391 | 0.016318 | -0.0049704 | -0.11351 | -0.0041136 | 0.071025 | 0.077942 | -0.0147 | 0.014911 | 0.0036165 | -23.2269 | 72.7158 | -50.9354 | 72.6791 | -47.5388 | -50.7889 | 6.1798 | -21.8582 | 72.7341 | -50.853 | 73.0545 | -48.468 | -50.2945 | -50.2716 | -0.18311 | -0.027466 | -0.064087 | 3.2135 | 56.9321 | -0.036621 | 57.1152 | 0.14648 | -0.10071 | -0.009155 | 0.31128 | 2.2842 | 0.48065 | 0.45776 | 0.58136 | 0.55847 | 3.3966 | 123.6145 | 2.3849 | 123.9075 | 123.6511 | 123.587 | 123.468 | 123.4863 | -123.6786 | -123.5962 | 123.4314 | 123.8068 | 27.5253 | 28.894
428.4844 | 123.7747 | -50.6149 | 72.876 | 0.03381 | 0.00071953 | 0.058858 | 0.07903 | -0.0026019 | 0.0099088 | -0.0028344 | 0.054336 | 0.0065674 | 0.069957 | 0.040558 | -0.0082912 | 0.02132 | 0.0068215 | -22.9019 | 72.8668 | -50.7523 | 72.8439 | -47.2961 | -50.5875 | 6.3995 | -21.3409 | 72.9126 | -50.6378 | 73.0682 | -48.2483 | -50.1938 | -50.1617 | -0.13733 | -0.009156 | -0.032044 | 3.3188 | 57.0145 | 0.027466 | 57.1518 | 0.16479 | -0.022888 | 0.036621 | 0.19226 | 2.3666 | 0.45319 | 0.42114 | 0.47607 | 0.44403 | 3.4561 | 123.5962 | 2.3895 | 123.7061 | 123.6191 | 123.5504 | 123.4818 | 123.5275 | -123.6282 | -123.5138 | 123.4589 | 123.6832 | 27.713 | 29.274
429.4844 | 123.7427 | -50.473 | 73.0225 | -0.011967 | 0.0071275 | 0.065267 | 0.081166 | -0.013283 | 0.013114 | 0.0078466 | -0.021958 | 0.0033634 | 0.064617 | 0.046966 | -0.018972 | 0.01598 | -0.01561 | -22.6135 | 72.9904 | -50.6424 | 73.0316 | -47.0856 | -50.4456 | 6.6833 | -21.1121 | 73.0087 | -50.5371 | 73.2101 | -48.0331 | -50.029 | -50.0198 | -0.16937 | -0.032044 | 0.009155 | 3.3875 | 57.1564 | 0.027465 | 57.3257 | 0.19684 | -0.064087 | -0.013733 | 0.18768 | 2.4399 | 0.45319 | 0.44403 | 0.51727 | 0.50812 | 3.5568 | 123.674 | 2.504 | 123.7473 | 123.6328 | 123.5458 | 123.4634 | 123.4818 | -123.6649 | -123.5596 | 123.5046 | 123.6832 | 27.8595 | 29.361
430.4844 | 123.7793 | -50.4868 | 73.027 | 0.03381 | 0.00071953 | 0.059926 | 0.075825 | 0.0091481 | 0.022727 | -0.0092424 | 0.10011 | 0.0065674 | 0.072093 | 0.059784 | -0.012563 | 0.012775 | -0.0070645 | -22.316 | 72.9904 | -50.6607 | 73.027 | -46.875 | -50.4227 | 6.9489 | -21.3364 | 72.995 | -50.5508 | 73.2056 | -47.9095 | -49.9878 | -49.9786 | -0.17395 | -0.036622 | 0 | 3.6118 | 57.4356 | 0.064087 | 57.6096 | 0.23804 | -0.064087 | -0.032044 | 0.17853 | 2.5772 | 0.50812 | 0.49896 | 0.5722 | 0.56305 | 3.7857 | 123.6877 | 2.6413 | 123.7564 | 123.6511 | 123.5458 | 123.4772 | 123.4818 | -123.6877 | -123.5779 | 123.5138 | 123.6923 | 28.1708 | 29.1504
431.4844 | 123.7198 | -50.6058 | 72.9126 | 0.1101 | 0.010333 | 0.058858 | 0.086507 | -0.0004649 | -0.012521 | -0.0071064 | 0.069594 | 0.0033634 | 0.063548 | 0.091827 | -0.0061552 | 0.02132 | 0.0057535 | -22.1054 | 72.8577 | -50.7477 | 72.908 | -46.8475 | -50.5096 | 6.9489 | -19.6289 | 72.9218 | -50.6607 | 73.0041 | -47.905 | -50.1297 | -50.1205 | -0.14191 | -0.054932 | -0.004578 | 3.7582 | 57.5546 | 0.09613 | 57.6965 | 0.23804 | -0.054932 | 0.009155 | 0.091552 | 2.7008 | 0.48523 | 0.47607 | 0.54016 | 0.53101 | 3.9001 | 123.6557 | 2.7557 | 123.6649 | 123.6053 | 123.5825 | 123.4634 | 123.5275 | -123.6603 | -123.5733 | 123.5138 | 123.6099 | 28.5004 | 30.9769
432.4844 | 123.7701 | -50.116 | 73.3521 | -0.1493 | 0.0071275 | 0.056722 | 0.08437 | 0.0038071 | -0.014657 | -0.0092424 | -0.037217 | -0.0073186 | 0.053935 | 0.089691 | -0.02004 | 0.02132 | -0.0059965 | -21.254 | 73.3337 | -50.2853 | 73.3612 | -46.312 | -50.1205 | 7.3563 | -21.4325 | 73.3566 | -50.1663 | 73.558 | -47.2961 | -49.5026 | -49.6033 | -0.16937 | -0.018311 | 0.009155 | 3.804 | 57.4722 | -0.004577 | 57.6416 | 0.16479 | -0.050354 | 0.004577 | 0.20599 | 2.8198 | 0.5127 | 0.6134 | 0.56305 | 0.66376 | 3.9734 | 123.6465 | 2.8702 | 123.7244 | 123.6191 | 123.5229 | 123.4497 | 123.4726 | -123.6374 | -123.5184 | 123.4772 | 123.674 | 28.862 | 28.6835
433.4844 | 123.7656 | -49.4751 | 74.0204 | -0.011967 | 0.012469 | 0.06313 | 0.086507 | -0.0090099 | 0.0056368 | 0.0089146 | 0.069594 | -0.00090962 | 0.076366 | 0.077942 | -0.0061552 | 0.014911 | -0.0059965 | -20.3064 | 73.97 | -49.6216 | 73.7778 | -45.6573 | -49.3378 | 8.2123 | -21.9406 | 73.9838 | -49.5667 | 74.1898 | -46.5454 | -48.8388 | -48.9487 | -0.14648 | -0.050354 | -0.24262 | 3.8177 | 57.6874 | 0.13733 | 57.8339 | 0.28381 | -0.091552 | -0.036621 | 0.16937 | 2.9297 | 0.52643 | 0.63629 | 0.61798 | 0.72784 | 3.9642 | 123.3994 | 3.0212 | 123.7564 | 123.5916 | 123.5504 | 123.4451 | 123.4589 | -123.642 | -123.587 | 123.2529 | 123.6649 | 29.1687 | 27.5345
434.4844 | 123.7564 | -49.1638 | 74.3179 | 0.064327 | -0.0014175 | 0.066335 | 0.086507 | -0.0036699 | 0.0024328 | -0.018856 | -0.11351 | 0.011908 | 0.06248 | 0.068329 | -0.0029502 | 0.029865 | 0.0014805 | -19.8807 | 74.3408 | -49.3149 | 74.3729 | -44.9936 | -49.0128 | 8.6975 | -22.5403 | 74.3683 | -49.2233 | 74.5193 | -46.2387 | -48.4955 | -48.5962 | -0.15106 | 0.022888 | 0.054932 | 4.1702 | 57.8613 | 0.15106 | 58.0124 | 0.30212 | -0.05951 | 0.050354 | 0.20142 | 2.9251 | 0.56763 | 0.66833 | 0.62714 | 0.72785 | 4.3213 | 123.6877 | 2.9846 | 123.7427 | 123.6557 | 123.5916 | 123.5046 | 123.5321 | -123.6328 | -123.5413 | 123.5367 | 123.6832 | 29.2831 | 26.6235
435.4844 | 123.7061 | -48.7152 | 74.8032 | 0.018551 | 0.022082 | 0.053517 | 0.082234 | 0.0080791 | -0.028543 | 0.0025066 | 0.14589 | 0.0033634 | 0.072093 | 0.040558 | -0.0093592 | 0.0063669 | 0.013229 | -19.2581 | 74.7803 | -48.8297 | 74.7986 | -44.426 | -48.5458 | 9.0637 | -23.0072 | 74.8032 | -48.7701 | 74.9451 | -45.7031 | -48.0011 | -48.1613 | -0.11444 | -0.022889 | -0.004578 | 4.2892 | 57.7789 | 0.16937 | 57.8934 | 0.28381 | -0.054932 | 0 | 0.14191 | 3.0121 | 0.55389 | 0.71411 | 0.60883 | 0.76904 | 4.4037 | 123.6282 | 3.067 | 123.7152 | 123.6099 | 123.5733 | 123.4955 | 123.5184 | -123.6328 | -123.5733 | 123.5138 | 123.6603 | 29.4571 | 25.708
436.4844 | 123.7656 | -48.3765 | 75.1328 | 0.03381 | 0.0071275 | 0.065267 | 0.088643 | -0.013283 | -0.0082492 | -0.0060384 | -0.021958 | 0.0012264 | 0.072093 | 0.058716 | -0.0050872 | 0.024524 | -0.0059965 | -19.0155 | 75.1099 | -48.4955 | 75.1144 | -43.9682 | -48.2346 | 9.5032 | -23.4192 | 75.1328 | -48.4085 | 75.3113 | -45.3232 | -47.5113 | -47.7859 | -0.11902 | -0.022888 | -0.01831 | 4.4083 | 57.8796 | 0.14191 | 57.9987 | 0.26093 | -0.032043 | 0 | 0.17853 | 3.0533 | 0.59052 | 0.86517 | 0.62256 | 0.89722 | 4.5273 | 123.6099 | 3.0853 | 123.7198 | 123.6053 | 123.5413 | 123.4863 | 123.5092 | -123.6282 | -123.5413 | 123.4909 | 123.6877 | 29.361 | 24.9573
437.4844 | 123.7564 | -47.5388 | 75.9888 | 0.20166 | 0.0092645 | 0.062062 | 0.08437 | -0.0036699 | -0.016794 | 0.0089146 | -0.0066996 | 0.0044314 | 0.069957 | 0.076874 | -0.015768 | 0.030933 | 0.0046845 | -18.0771 | 75.9384 | -47.7081 | 75.9705 | -42.9977 | -47.3694 | 10.5881 | -25.3098 | 75.9705 | -47.6074 | 76.1581 | -44.4809 | -46.5637 | -46.9391 | -0.16937 | -0.050354 | -0.018311 | 4.541 | 58.1268 | 0.16937 | 58.2962 | 0.33874 | -0.068665 | -0.018311 | 0.16937 | 3.0579 | 0.59967 | 0.97504 | 0.66833 | 1.0437 | 4.7104 | 123.6786 | 3.1265 | 123.7656 | 123.6465 | 123.5779 | 123.4772 | 123.5092 | -123.6969 | -123.5962 | 123.5092 | 123.6969 | 29.4617 | 22.229
439.0312 | 123.7061 | -45.7169 | 77.8381 | 0.17114 | 0.0039235 | 0.059926 | 0.086507 | 0.01342 | -0.0029082 | -0.013515 | 0.16115 | 0.014044 | 0.076366 | 0.071533 | -0.011495 | 0.01598 | -0.025223 | -16.1728 | 77.774 | -45.8771 | 77.7512 | -41.0431 | -45.5521 | 12.1765 | -29.5029 | 77.7786 | -45.8084 | 77.9343 | -42.6041 | -44.8013 | -45.1584 | -0.16022 | -0.064087 | -0.086975 | 4.6738 | 57.8934 | 0.1648 | 58.0536 | 0.32501 | -0.091553 | -0.05951 | 0.09613 | 3.1128 | 0.55847 | 0.91553 | 0.65002 | 1.0071 | 4.834 | 123.6282 | 3.2043 | 123.7427 | 123.6511 | 123.587 | 123.4909 | 123.4955 | -123.7152 | -123.6465 | 123.468 | 123.6511 | 29.5441 | 16.214
439.6406 | 123.7289 | -45.3918 | 78.1082 | 0.094845 | 0.0071275 | 0.06313 | 0.07903 | 0.0006031 | 0.0013638 | 0.0046426 | -0.052476 | 0.011908 | 0.069957 | 0.11212 | -0.011495 | 0.033069 | -0.013474 | -15.9164 | 78.1174 | -45.5292 | 78.1723 | -40.5762 | -45.1492 | 12.4146 | -30.7617 | 78.1174 | -45.4468 | 78.241 | -41.7572 | -44.5358 | -44.838 | -0.13733 | 0.009156 | 0.064087 | 4.8157 | 57.8064 | 0.24262 | 57.9437 | 0.37994 | -0.054931 | 0.009156 | 0.13275 | 3.6346 | 0.55389 | 0.85602 | 0.60882 | 0.91095 | 4.953 | 123.7015 | 3.6896 | 123.6877 | 123.6465 | 123.5641 | 123.5092 | 123.5092 | -123.6374 | -123.555 | 123.5641 | 123.6328 | 29.4754 | 14.6301
440.5 | 123.7198 | -44.8929 | 78.653 | 0.21692 | 0.0049915 | 0.05779 | 0.082234 | 0.014488 | 0.0024328 | 0.0099836 | 0.13063 | 0.012976 | 0.080638 | 0.040558 | -0.012563 | 0.010639 | 0.010025 | -15.2435 | 78.6346 | -45.0256 | 78.6118 | -39.9628 | -44.6823 | 12.9044 | -31.041 | 78.6346 | -44.9341 | 78.7766 | -41.6702 | -43.8538 | -44.2978 | -0.13275 | -0.01831 | -0.041199 | 4.9301 | 57.7972 | 0.21057 | 57.93 | 0.34332 | -0.041199 | -0.01831 | 0.1236 | 3.2227 | 0.59509 | 1.0391 | 0.63629 | 1.0803 | 5.0629 | 123.6374 | 3.2639 | 123.7106 | 123.6603 | 123.5687 | 123.5275 | 123.5275 | -123.6786 | -123.587 | 123.5046 | 123.6694 | 29.6494 | 13.8519
441.4844 | 123.7289 | -44.3985 | 79.0787 | 0.12536 | 0.0060595 | 0.069539 | 0.08437 | -0.0058059 | -0.012521 | 0.0025066 | -0.082994 | 0.020452 | 0.07423 | 0.080078 | -0.023245 | 0.027729 | 0.0089575 | -14.7263 | 79.0833 | -44.5862 | 79.129 | -39.3127 | -44.1788 | 13.2294 | -31.5765 | 79.0878 | -44.4809 | 79.2297 | -40.5396 | -43.4052 | -43.7759 | -0.18768 | 0.004578 | 0.050354 | 5.0858 | 57.6279 | 0.21973 | 57.8156 | 0.40741 | -0.082397 | 0.009156 | 0.15106 | 3.8589 | 0.62256 | 0.99335 | 0.70496 | 1.0757 | 5.2734 | 123.7152 | 3.9413 | 123.7106 | 123.6694 | 123.5687 | 123.4818 | 123.4863 | -123.6649 | -123.5596 | 123.5275 | 123.6282 | 29.6722 | 12.822
442.4844 | 123.7473 | -44.3985 | 79.0512 | 0.018551 | 0.0039235 | 0.068471 | 0.083302 | 0.0038071 | -0.0039762 | 0.0089146 | -0.021958 | 0.0022944 | 0.077434 | 0.070465 | -0.02004 | 0.025593 | 0.0025485 | -14.5981 | 79.0649 | -44.5496 | 79.0695 | -39.2395 | -44.2154 | 13.1378 | -31.604 | 79.1061 | -44.4489 | 79.2801 | -39.8071 | -43.2404 | -43.6798 | -0.15106 | 0.013733 | 0.018311 | 5.159 | 57.5363 | 0.18311 | 57.6874 | 0.33417 | -0.050354 | 0.054932 | 0.22888 | 4.5914 | 0.71869 | 1.1581 | 0.76904 | 1.2085 | 5.3101 | 123.6191 | 4.6417 | 123.7289 | 123.6145 | 123.555 | 123.4634 | 123.5046 | -123.6008 | -123.5001 | 123.468 | 123.6786 | 29.8004 | 12.7945
443.4844 | 123.7244 | -44.4992 | 79.0329 | 0.15588 | 0.0092645 | 0.062062 | 0.091847 | -0.0026019 | 0.018454 | 0.011052 | -0.15929 | 0.011908 | 0.067821 | 0.090759 | -0.011495 | 0.027729 | 0.011093 | -14.5935 | 79.0283 | -44.7006 | 79.0878 | -39.0472 | -44.1833 | 12.8632 | -30.9769 | 79.0512 | -44.5816 | 79.1153 | -39.7202 | -43.2907 | -43.84 | -0.20142 | -0.004578 | 0.054932 | 5.452 | 57.3624 | 0.31586 | 57.5638 | 0.51727 | -0.082397 | 0.01831 | 0.082397 | 4.7791 | 0.65918 | 1.2085 | 0.74158 | 1.2909 | 5.6534 | 123.7885 | 4.8614 | 123.6969 | 123.7289 | 123.6328 | 123.5275 | 123.5504 | -123.7335 | -123.6145 | 123.587 | 123.6145 | 29.9057 | 13.5223
444.4844 | 123.7427 | -44.1879 | 79.2847 | 0.049069 | 0.00071953 | 0.055654 | 0.092915 | 0.012352 | 0.0067048 | -0.026332 | 0.069594 | 0.0022944 | 0.088115 | 0.058716 | -0.0050872 | 0.02132 | -0.0049285 | -14.3646 | 79.2664 | -44.3802 | 79.2847 | -38.7131 | -43.959 | 12.8311 | -30.5008 | 79.2755 | -44.3115 | 79.4586 | -39.2258 | -42.8696 | -43.4784 | -0.19226 | -0.018311 | 0 | 5.4749 | 57.019 | 0.22888 | 57.2113 | 0.42114 | -0.1236 | -0.009155 | 0.17395 | 4.9622 | 0.70953 | 1.3184 | 0.83313 | 1.442 | 5.6671 | 123.6649 | 5.0858 | 123.7701 | 123.6465 | 123.587 | 123.4543 | 123.4634 | -123.6649 | -123.5962 | 123.4726 | 123.6465 | 29.8233 | 13.6871
445.4844 | 123.7061 | -44.0735 | 79.4357 | 0.049069 | 0.02315 | 0.059926 | 0.073689 | 0.012352 | 0.012046 | -0.014583 | 0.17641 | 0.0022944 | 0.083843 | 0.077942 | -0.0050872 | 0.030933 | -0.00065554 | -14.1586 | 79.4495 | -44.2108 | 79.4357 | -38.4613 | -43.8629 | 12.9959 | -31.5216 | 79.4174 | -44.1559 | 79.5593 | -39.3173 | -42.2607 | -43.396 | -0.13733 | 0.013733 | 0 | 5.6122 | 57.0694 | 0.21057 | 57.2067 | 0.3479 | -0.082398 | -0.018311 | 0.1236 | 4.7562 | 0.67749 | 1.8127 | 0.75989 | 1.8951 | 5.7495 | 123.6465 | 4.8386 | 123.7152 | 123.6603 | 123.5733 | 123.5229 | 123.4909 | -123.6465 | -123.5916 | 123.5092 | 123.6328 | 29.9149 | 12.5519
446.4844 | 123.7427 | -43.8995 | 79.6051 | 0.0032924 | 0.011401 | 0.059926 | 0.082234 | 0.0091481 | 0.012046 | -0.0049704 | -0.021958 | 0.0033634 | 0.068889 | 0.10037 | -0.012563 | 0.037342 | -0.0070645 | -15.0742 | 79.6143 | -44.0781 | 79.6555 | -37.2757 | -43.5654 | 10.6384 | -31.6956 | 79.628 | -43.9957 | 79.7516 | -39.2349 | -41.8442 | -43.1946 | -0.17853 | 0.009155 | 0.050354 | 6.6238 | 54.538 | 0.33417 | 54.7165 | 0.5127 | -0.096131 | 0.022888 | 0.14648 | 4.6646 | 0.70496 | 2.0554 | 0.80109 | 2.1515 | 6.8024 | 123.7335 | 4.7607 | 123.7473 | 123.6923 | 123.6237 | 123.5138 | 123.5275 | -123.6832 | -123.6008 | 123.555 | 123.6511 | 28.8254 | 12.204
447.4844 | 123.642 | -44.133 | 79.4174 | 0.049069 | 0.0049915 | 0.065267 | 0.085438 | 0.017693 | 0.0056368 | 0.0099836 | -0.037217 | 0.018316 | 0.084911 | 0.10998 | -0.0147 | 0.034138 | 0.011093 | -14.296 | 79.422 | -44.2841 | 79.3945 | -38.3057 | -43.7439 | 13.1058 | -31.5353 | 79.422 | -44.2017 | 79.4678 | -39.2761 | -41.8808 | -43.4509 | -0.15106 | 0.004578 | -0.022888 | 5.8273 | 57.2388 | 0.3891 | 57.3898 | 0.54016 | -0.068664 | 0.004578 | 0.050354 | 4.8569 | 0.68207 | 2.2522 | 0.75073 | 2.3209 | 5.9784 | 123.6786 | 4.9255 | 123.6694 | 123.7061 | 123.6237 | 123.555 | 123.555 | -123.7015 | -123.6191 | 123.5275 | 123.6008 | 29.837 | 12.5977
448.4844 | 123.6877 | -43.7714 | 79.7516 | 0.018551 | 0.0049915 | 0.056722 | 0.087575 | 0.018761 | -0.0071802 | -0.0081744 | -0.12877 | 0.0097714 | 0.07957 | 0.071533 | -0.0147 | 0.039478 | -0.00065554 | -14.2593 | 79.7607 | -43.9682 | 79.8248 | -37.5824 | -43.3411 | 13.3072 | -30.8166 | 79.7882 | -43.8309 | 79.8569 | -39.0976 | -40.6265 | -43.0527 | -0.19684 | 0.009155 | 0.073242 | 6.189 | 57.0786 | 0.4303 | 57.2754 | 0.62714 | -0.05951 | 0.036621 | 0.10529 | 4.6738 | 0.71869 | 3.1448 | 0.7782 | 3.2043 | 6.3858 | 123.793 | 4.7333 | 123.6877 | 123.7289 | 123.6191 | 123.5321 | 123.5596 | -123.7198 | -123.5825 | 123.5962 | 123.6282 | 29.512 | 12.9547
449.4844 | 123.6603 | -44.014 | 79.5181 | 0.079586 | 0.0017875 | 0.068471 | 0.083302 | -0.016487 | -0.0082492 | -0.00069841 | -0.082994 | 0.012976 | 0.07423 | 0.098236 | -0.011495 | 0.037342 | 0.0089575 | -14.7491 | 79.5685 | -44.1605 | 79.5776 | -37.4268 | -43.5196 | 13.2065 | -30.9723 | 79.509 | -44.0964 | 79.5776 | -39.2303 | -40.7089 | -43.2861 | -0.14648 | 0.050354 | 0.05951 | 6.5872 | 57.2205 | 0.49438 | 57.3669 | 0.64087 | -0.082398 | -0.009155 | 0.05951 | 4.7836 | 0.72784 | 3.3051 | 0.81024 | 3.3875 | 6.7337 | 123.7381 | 4.866 | 123.674 | 123.7289 | 123.6053 | 123.5825 | 123.5229 | -123.6786 | -123.6145 | 123.5916 | 123.5916 | 29.2648 | 13.0417
450.4844 | 123.7198 | -44.0323 | 79.4815 | 0.1101 | 0.0092645 | 0.070607 | 0.085438 | 0.015556 | -0.0093172 | 0.00037059 | 0.10011 | 0.010839 | 0.077434 | 0.070465 | -0.0072232 | 0.022388 | -0.02095 | -14.4791 | 79.4632 | -44.1559 | 79.4632 | -36.3464 | -43.6157 | 12.3505 | -30.3909 | 79.4678 | -44.0598 | 79.5776 | -38.8824 | -40.4617 | -43.2037 | -0.1236 | -0.01831 | -0.01831 | 7.6859 | 56.3828 | 0.41656 | 56.5063 | 0.54016 | -0.027465 | -0.013733 | 0.096131 | 5.1498 | 0.82855 | 3.5706 | 0.85602 | 3.598 | 7.8094 | 123.6191 | 5.1773 | 123.6374 | 123.6191 | 123.5275 | 123.4955 | 123.5001 | -123.6374 | -123.5413 | 123.4955 | 123.6099 | 29.5532 | 13.6414
451.4844 | 123.642 | -43.9041 | 79.6875 | 0.049069 | 0.0092645 | 0.071675 | 0.081166 | 0.011284 | 0.017386 | -0.013515 | 0.039077 | 0.0097714 | 0.078502 | 0.070465 | -0.0072232 | 0.048023 | 0.020706 | -15.2298 | 79.6692 | -44.046 | 79.6783 | -35.7559 | -43.19 | 10.9406 | -30.4367 | 79.6921 | -43.9178 | 79.7195 | -39.3768 | -40.2328 | -43.071 | -0.14191 | -0.018311 | -0.009155 | 8.1482 | 54.8447 | 0.71411 | 54.9866 | 0.85602 | -0.013733 | 0.004578 | 0.032043 | 4.5273 | 0.83313 | 3.6713 | 0.84686 | 3.685 | 8.2901 | 123.7244 | 4.541 | 123.6374 | 123.7152 | 123.6099 | 123.5733 | 123.5962 | -123.7335 | -123.6053 | 123.5825 | 123.6237 | 28.6743 | 13.4674
452.4844 | 123.6877 | -43.9407 | 79.5914 | 0.14062 | 0.0028555 | 0.078084 | 0.098256 | 0.0048751 | -0.0093172 | -0.00069841 | -0.0066996 | 0.017248 | 0.080638 | 0.090759 | -0.0082912 | 0.043751 | 0.010025 | -15.1749 | 79.6051 | -44.0964 | 79.6783 | -35.907 | -43.428 | 11.3022 | -30.5054 | 79.5914 | -44.0094 | 79.6783 | -39.1891 | -39.8804 | -43.0206 | -0.15564 | 0.013733 | 0.086975 | 8.0338 | 55.2429 | 0.51269 | 55.3986 | 0.66833 | -0.068664 | 0 | 0.086975 | 4.7516 | 0.9201 | 4.0604 | 0.98877 | 4.129 | 8.1894 | 123.7747 | 4.8203 | 123.6877 | 123.7015 | 123.6008 | 123.5458 | 123.5321 | -123.6877 | -123.6008 | 123.6191 | 123.6191 | 28.7659 | 13.4354
453.4844 | 123.7244 | -43.8766 | 79.7195 | 0.03381 | 0.011401 | 0.067403 | 0.097188 | 0.01342 | 0.0067048 | -0.0071064 | -0.12877 | 0.017248 | 0.084911 | 0.077942 | -0.018972 | 0.044819 | 0.0014805 | -15.7562 | 79.6371 | -44.0735 | 79.7928 | -36.1084 | -43.3182 | 12.0071 | -29.718 | 79.66 | -43.9453 | 79.7241 | -38.9694 | -39.6973 | -43.0023 | -0.19684 | -0.082397 | 0.073243 | 7.7683 | 55.8838 | 0.55847 | 56.0806 | 0.75531 | -0.068664 | -0.059509 | 0.004578 | 4.9072 | 0.87433 | 4.1794 | 0.94299 | 4.248 | 7.9651 | 123.8663 | 4.9759 | 123.6694 | 123.7106 | 123.6053 | 123.5138 | 123.5367 | -123.793 | -123.6649 | 123.6694 | 123.6008 | 28.1204 | 14.1586
454.4844 | 123.6145 | -43.8446 | 79.7104 | 0.03381 | 0.0081955 | 0.06313 | 0.088643 | -0.0004649 | 0.014182 | -0.0039024 | -0.098252 | 0.014044 | 0.084911 | 0.10464 | -0.0050872 | 0.044819 | -0.013474 | -15.5502 | 79.6875 | -44.0048 | 79.7836 | -34.9686 | -43.2587 | 10.8124 | -28.6743 | 79.715 | -43.9041 | 79.7195 | -37.8937 | -39.2944 | -42.8833 | -0.16022 | -0.022888 | 0.073242 | 8.876 | 54.657 | 0.58594 | 54.8172 | 0.74615 | -0.05951 | 0.004578 | 0.009155 | 5.9509 | 0.9613 | 4.5502 | 1.0208 | 4.6097 | 9.0363 | 123.7885 | 6.0104 | 123.6237 | 123.6923 | 123.6191 | 123.5321 | 123.5596 | -123.7152 | -123.6145 | 123.6282 | 123.5641 | 28.2944 | 15.1703
455.4844 | 123.7061 | -43.7851 | 79.7287 | 0.20166 | -0.0024855 | 0.065267 | 0.070485 | -0.0015339 | -0.013589 | -0.0039024 | 0.16115 | 0.0065674 | 0.090251 | 0.10358 | -0.0072232 | 0.044819 | 0.0046845 | -15.6097 | 79.7241 | -43.9178 | 79.7104 | -34.7672 | -43.2907 | 10.5652 | -29.2191 | 79.7012 | -43.8538 | 79.8065 | -37.5549 | -38.5529 | -42.7322 | -0.13275 | -0.004578 | -0.018311 | 9.0179 | 54.3503 | 0.49439 | 54.483 | 0.62714 | -0.068665 | -0.027466 | 0.07782 | 6.2302 | 1.0529 | 5.2322 | 1.1215 | 5.3009 | 9.1507 | 123.6282 | 6.2988 | 123.6603 | 123.642 | 123.555 | 123.5092 | 123.4863 | -123.6465 | -123.5825 | 123.4955 | 123.5916 | 28.1754 | 14.566
456.4844 | 123.6145 | -43.8171 | 79.7379 | -0.042484 | 0.0081955 | 0.069539 | 0.087575 | 0.0080791 | 0.0088408 | 0.013188 | -0.23558 | 0.0087034 | 0.072093 | 0.13882 | -0.02004 | 0.044819 | -0.014542 | -17.189 | 79.715 | -43.9728 | 79.8019 | -34.3735 | -43.1992 | 10.0204 | -25.589 | 79.715 | -43.8858 | 79.8111 | -37.4908 | -37.9257 | -42.7643 | -0.15564 | -0.022888 | 0.064087 | 9.4437 | 53.8376 | 0.61798 | 53.9932 | 0.77362 | -0.068664 | -0.022888 | 0.073242 | 6.3263 | 1.0529 | 5.8914 | 1.1215 | 5.9601 | 9.5993 | 123.7747 | 6.395 | 123.6969 | 123.6877 | 123.6008 | 123.5321 | 123.5321 | -123.7106 | -123.6237 | 123.6191 | 123.6282 | 26.6281 | 18.2281
457.4844 | 123.6511 | -44.0094 | 79.509 | 0.049069 | 0.011401 | 0.069539 | 0.10146 | 0.0006031 | -0.023202 | -0.014583 | -0.17455 | 0.0097714 | 0.072093 | 0.10144 | -0.011495 | 0.059772 | 0.0036165 | -16.9968 | 79.4861 | -44.1971 | 79.6051 | -35.2432 | -43.3456 | 12.1994 | -25.8453 | 79.5181 | -44.0689 | 79.5547 | -37.7609 | -37.6923 | -42.9245 | -0.18768 | -0.022888 | 0.096131 | 8.7662 | 56.2088 | 0.66376 | 56.3965 | 0.85144 | -0.05951 | 0.009155 | 0.045777 | 6.2485 | 1.0849 | 6.3171 | 1.1444 | 6.3766 | 8.9539 | 123.8022 | 6.308 | 123.6237 | 123.6832 | 123.587 | 123.4955 | 123.5275 | -123.7061 | -123.5779 | 123.6145 | 123.5641 | 27.0126 | 18.1641
458.4844 | 123.6511 | -43.895 | 79.6234 | 0.03381 | 0.012469 | 0.055654 | 0.091847 | -0.0058059 | 0.021659 | -0.0049704 | 0.0085594 | 0.0076354 | 0.091319 | 0.12814 | -0.0050872 | 0.056568 | -0.0038605 | -17.6056 | 79.6234 | -44.0872 | 79.6829 | -33.9981 | -43.2037 | 9.4254 | -25.6302 | 79.6326 | -43.9682 | 79.6463 | -37.1841 | -36.9415 | -42.778 | -0.19226 | 0 | 0.059509 | 9.8969 | 53.3203 | 0.69122 | 53.5126 | 0.88348 | -0.073243 | 0.009155 | 0.022888 | 6.7108 | 1.1169 | 6.9534 | 1.1902 | 7.0267 | 10.0891 | 123.7701 | 6.7841 | 123.6145 | 123.7106 | 123.6008 | 123.5184 | 123.5275 | -123.7106 | -123.5916 | 123.5779 | 123.5413 | 26.2894 | 18.2648
459.4844 | 123.6465 | -43.7073 | 79.8203 | 0.049069 | 0.0071275 | 0.058858 | 0.090779 | 0.0038071 | 0.00029581 | -0.0028344 | -0.7849 | 0.00015838 | 0.080638 | 0.10464 | -0.0050872 | 0.075794 | 0.011093 | -16.1133 | 79.8065 | -43.8675 | 79.8981 | -34.8175 | -42.9886 | 12.4237 | -24.9298 | 79.8386 | -43.7668 | 79.8935 | -36.9232 | -36.5158 | -42.4942 | -0.16022 | -0.013732 | 0.07782 | 8.8898 | 56.131 | 0.71869 | 56.2912 | 0.87891 | -0.05951 | 0.018311 | 0.073243 | 6.7841 | 1.2131 | 7.1915 | 1.2726 | 7.251 | 9.05 | 123.7656 | 6.8436 | 123.6603 | 123.674 | 123.6053 | 123.5138 | 123.5458 | -123.6877 | -123.587 | 123.6053 | 123.6008 | 27.594 | 18.7775
460.4844 | 123.7518 | -43.4967 | 79.9942 | -0.011967 | 0.0049915 | 0.077016 | 0.088643 | -0.0058059 | -0.0029082 | 0.0057106 | -0.067735 | 0.015112 | 0.075298 | 0.12067 | -0.022176 | 0.074726 | -0.012405 | -17.7109 | 79.9393 | -43.6707 | 79.9805 | -33.4579 | -42.9016 | 9.4162 | -24.5773 | 79.9576 | -43.5608 | 80.0949 | -36.882 | -35.9253 | -42.1097 | -0.17395 | -0.054932 | -0.013733 | 10.0388 | 52.9129 | 0.59509 | 53.0869 | 0.76904 | -0.064087 | -0.036621 | 0.10071 | 6.6147 | 1.387 | 7.5714 | 1.4511 | 7.6355 | 10.2127 | 123.6511 | 6.6788 | 123.6557 | 123.6099 | 123.5184 | 123.436 | 123.4543 | -123.6649 | -123.555 | 123.4772 | 123.5916 | 25.7858 | 18.9194
461.4844 | 123.642 | -43.3365 | 80.2002 | 0.0032924 | 0.019946 | 0.068471 | 0.082234 | 0.0048751 | 0.00029581 | -0.0092424 | -0.11351 | 0.0097714 | 0.097728 | 0.15378 | -0.0082912 | 0.06084 | 0.0089575 | -19.3359 | 80.2551 | -43.4097 | 80.2826 | -34.1675 | -42.5079 | 11.8744 | -26.1932 | 80.3055 | -43.2999 | 80.2643 | -36.5295 | -35.5774 | -43.2541 | -0.073242 | 0.054932 | 0.082398 | 9.169 | 55.2109 | 0.82855 | 55.2841 | 0.90179 | 0.036621 | 0.10529 | 0.064087 | 6.8069 | 0.082398 | 7.7591 | 0.045777 | 7.7225 | 9.2422 | 123.6923 | 6.7703 | 123.5641 | 123.6649 | 123.6053 | 123.5916 | 123.642 | -123.6099 | -123.5001 | 123.6191 | 123.6008 | 24.0005 | 17.1432
462.4844 | 123.6465 | -43.3777 | 80.1498 | 0.14062 | 0.02315 | 0.066335 | 0.095051 | -0.0090099 | -0.0082492 | -0.0071064 | -0.20506 | 0.014044 | 0.094524 | 0.14737 | -0.0029502 | 0.067249 | 0.012161 | -17.981 | 80.1498 | -43.5425 | 80.1956 | -33.5266 | -42.6315 | 10.2402 | -27.1545 | 80.1453 | -43.4235 | 80.191 | -37.2528 | -35.2615 | -41.6382 | -0.16479 | 0 | 0.045777 | 9.8511 | 53.6179 | 0.74615 | 53.7827 | 0.91095 | -0.045776 | -0.004577 | 0.041199 | 6.1249 | 1.7395 | 8.1161 | 1.7853 | 8.1619 | 10.0159 | 123.7381 | 6.1707 | 123.6145 | 123.6923 | 123.5687 | 123.5275 | 123.5229 | -123.6923 | -123.5733 | 123.5733 | 123.5687 | 25.3967 | 16.2231
463.4844 | 123.6008 | -43.1122 | 80.4245 | 0.064327 | 0.019946 | 0.068471 | 0.086507 | 0.015556 | 0.016318 | -0.0028344 | -0.098252 | 0.025793 | 0.087047 | 0.12494 | 0.00025378 | 0.075794 | -0.013474 | -19.2902 | 80.4062 | -43.277 | 80.4794 | -33.371 | -42.3431 | 10.4965 | -26.5503 | 80.4153 | -43.1763 | 80.4245 | -36.6898 | -34.6161 | -41.4551 | -0.16479 | -0.018311 | 0.054931 | 9.7412 | 53.6087 | 0.76904 | 53.7735 | 0.93384 | -0.064087 | -0.009156 | 0 | 6.4224 | 1.6571 | 8.4961 | 1.7212 | 8.5602 | 9.906 | 123.7564 | 6.4865 | 123.6008 | 123.6832 | 123.5916 | 123.5184 | 123.5275 | -123.7015 | -123.6008 | 123.5916 | 123.5367 | 23.822 | 16.5619
464.4688 | 123.6099 | -42.9886 | 80.5984 | 0.094845 | 0.0028555 | 0.078084 | 0.09612 | 0.016624 | 0.0024328 | -0.0092424 | -0.11351 | 0.019384 | 0.087047 | 0.12921 | -0.010427 | 0.073658 | 0.0036165 | -19.0018 | 80.5573 | -43.1442 | 80.6442 | -32.0114 | -42.1692 | 1.4877 | -27.0859 | 80.5527 | -43.0298 | 80.5573 | -35.8795 | -34.1629 | -41.3132 | -0.15564 | -0.041199 | 0.045776 | 10.9772 | 44.4763 | 0.8194 | 44.632 | 0.97504 | -0.041199 | -0.045777 | -0.041199 | 7.1091 | 1.6754 | 8.8257 | 1.7166 | 8.8669 | 11.1328 | 123.7885 | 7.1503 | 123.587 | 123.7015 | 123.5825 | 123.5458 | 123.5413 | -123.7427 | -123.6282 | 123.6328 | 123.5458 | 23.9868 | 15.9027
465.4844 | 123.7289 | -50.9949 | 72.4319 | 0.12536 | 0.025286 | 0.075948 | 0.086507 | 0.015556 | 0.017386 | -0.0060384 | -0.31187 | 0.0022944 | 0.098796 | 0.52975 | -0.0018822 | 0.4475 | 0.0078895 | -26.5228 | 72.3175 | -51.2375 | 72.345 | -39.8483 | -50.3586 | 0.67291 | 5.2505 | 72.29 | -51.1185 | 72.5281 | -40.0223 | 40.2878 | -48.5687 | -0.24262 | -0.11444 | -0.086975 | 11.1465 | 51.6678 | 0.63629 | 51.9104 | 0.87891 | -0.1236 | -0.14191 | 0.09613 | 10.9726 | 2.4261 | 91.2827 | 2.5497 | 91.4062 | 11.3892 | 123.5825 | 11.0962 | 123.6465 | 123.555 | 123.4085 | 123.3124 | 123.2849 | -123.6694 | -123.5504 | 123.3398 | 123.5229 | 24.472 | 56.2454
466.4844 | 123.6374 | -49.7726 | 73.732 | 0.064327 | 0.0049915 | 0.073811 | 0.093983 | -0.0036699 | 0.0088408 | -0.0028344 | -0.58653 | 0.0044314 | 0.11695 | 0.57461 | -0.0093592 | 0.47313 | 0.010025 | -29.3701 | 73.3063 | -50.3265 | 73.4482 | -39.0015 | -49.4293 | 1.3962 | 3.6896 | 73.3063 | -50.1663 | 73.6084 | -39.3585 | 47.6257 | -46.376 | -0.55389 | -0.42572 | -0.28381 | 10.7712 | 51.1688 | 0.34332 | 51.7227 | 0.89722 | -0.39368 | -0.42572 | -0.1236 | 10.4141 | 3.3966 | 97.3984 | 3.7903 | 97.7921 | 11.3251 | 123.7747 | 10.8078 | 123.7747 | 123.6328 | 123.4726 | 123.0789 | 123.0789 | -124.0585 | -123.8983 | 123.2208 | 123.381 | 20.4025 | 53.4622
467.4844 | 123.7061 | -37.1796 | 86.2839 | 0.17114 | 0.034899 | 0.075948 | 0.086507 | 0.0016711 | -0.010385 | -0.0274 | -0.0066996 | 0.010839 | 0.0048024 | -0.01178 | -0.017904 | 0.022388 | -0.011337 | -18.8736 | 86.2701 | -37.3627 | 86.2701 | -26.0239 | -36.8179 | 10.9039 | -32.9498 | 86.2885 | -37.3032 | -36.6119 | -33.2657 | -36.6989 | -30.6702 | -0.18311 | -0.013733 | -0.013733 | 11.1557 | 48.0835 | 0.36163 | 48.2666 | 0.54474 | -0.1236 | 0.004577 | -122.8958 | 3.9139 | 6.5094 | 0.48065 | 6.633 | 0.60425 | 11.3388 | 123.6328 | 4.0375 | 0.69122 | 123.6328 | 123.5916 | 123.4497 | 123.468 | -123.6465 | -123.587 | 123.4497 | 0.56763 | 18.306 | 4.2297
468.4844 | 123.6786 | -48.3582 | 75.1007 | 0.24743 | 0.016741 | 0.081288 | 0.099324 | -0.0015339 | 0.0056368 | -0.0039024 | -0.54076 | 0.011908 | 0.12336 | 0.66754 | -0.0147 | 0.53081 | 0.02391 | -39.2715 | 75.0687 | -48.5367 | 75.1144 | -38.3514 | -46.9894 | -4.6051 | -0.1236 | 75.0595 | -48.3765 | 75.1602 | -37.3947 | 52.1347 | -44.5953 | -0.17853 | -0.032043 | 0.013733 | 10.0067 | 43.7531 | 1.3687 | 43.9316 | 1.5472 | -0.018311 | -0.041199 | 0.059509 | 10.9634 | 3.7628 | 100.4929 | 3.7811 | 100.5112 | 10.1852 | 123.6511 | 10.9818 | 123.5367 | 123.6053 | 123.436 | 123.4268 | 123.4177 | -123.6374 | -123.4772 | 123.4726 | 123.5184 | 9.0866 | 48.2346
469.4844 | 123.6603 | -37.0468 | 86.5082 | 0.15588 | 0.0060595 | 0.081288 | 0.086507 | -0.0058059 | -0.0061122 | -0.0028344 | 0.054336 | 0.0097714 | 0.027233 | -0.0043033 | -0.010427 | 0.025593 | -0.0059965 | -19.3314 | 86.4624 | -37.1841 | 86.5036 | -26.5686 | -36.0397 | 4.5868 | -32.8262 | 86.5082 | -37.1292 | -36.3144 | -33.1833 | -36.4059 | -30.4138 | -0.13733 | -0.045777 | -0.004578 | 10.4782 | 41.6336 | 1.0071 | 41.7709 | 1.1444 | -0.082397 | 0 | -122.8226 | 3.8635 | 6.633 | 0.64087 | 6.7154 | 0.72327 | 10.6155 | 123.6877 | 3.9459 | 0.81482 | 123.6465 | 123.6374 | 123.5092 | 123.555 | -123.6923 | -123.6374 | 123.5504 | 0.73242 | 17.7155 | 4.2206
470.4844 | 123.8068 | -46.0098 | 77.3483 | 0.018551 | 0.0017875 | 0.083425 | 0.089711 | 0.0070111 | -0.0071802 | -0.010311 | 0.10011 | -0.0030456 | 0.1255 | 0.0042417 | 0.14552 | 0.034138 | 0.0025485 | -27.9419 | 77.7512 | -45.8771 | 77.4582 | -33.2291 | -48.381 | -6.1752 | -32.3044 | 77.4811 | -46.0098 | -31.7871 | 77.5085 | -32.0068 | 55.806 | 0.13275 | 0.40283 | 0.10986 | 12.7808 | 39.8346 | -2.3712 | 39.7018 | -2.504 | 0 | 0.13275 | -109.1354 | 123.5184 | 101.8158 | 14.003 | 101.8158 | 14.003 | 12.648 | 123.3353 | 123.5184 | 14.2227 | 123.6282 | 123.4909 | 123.761 | 123.4909 | -123.2254 | -123.3582 | 123.468 | 14.2227 | 18.0679 | 13.7054
471.4844 | 123.6649 | -37.001 | 86.4853 | 0.0032924 | 0.00071953 | 0.060994 | 0.099324 | 0.01342 | 0.0045688 | 0.0025066 | 0.039077 | 0.018316 | 0.0069384 | 0.0053097 | -0.0147 | 0.028797 | 0.015366 | -19.6884 | 86.499 | -37.0972 | 86.5173 | -23.9319 | -35.9802 | -0.20142 | -32.3456 | 86.5219 | -37.056 | -35.1242 | -33.0734 | -36.4288 | -31.2744 | -0.09613 | 0.013732 | 0.032043 | 13.0692 | 36.7996 | 1.0208 | 36.8958 | 1.1169 | -0.054931 | 0.036621 | -121.6095 | 3.9276 | 5.7266 | 0.57221 | 5.7816 | 0.62714 | 13.1653 | 123.6145 | 3.9825 | 1.9318 | 123.5962 | 123.5779 | 123.5001 | 123.523 | -123.5825 | -123.5413 | 123.5184 | 1.8768 | 17.3126 | 4.6555
472.4844 | 123.6603 | -48.88 | 74.6017 | 0.14062 | 0.0081955 | 0.075948 | 0.093983 | -0.0047379 | -0.019998 | 0.0014386 | -0.63231 | 0.015112 | 0.12123 | 0.62802 | 0.00025378 | 0.46459 | 0.013229 | -32.9956 | 74.8581 | -48.761 | 74.5605 | -36.0764 | -47.8729 | -10.7346 | 1.4603 | 74.3958 | -49.0677 | 74.5834 | -39.5874 | 36.8637 | -44.577 | 0.11902 | 0.25635 | -0.041199 | 12.8036 | 38.1454 | 1.0071 | 38.0264 | 0.88806 | -0.18768 | -0.20599 | -0.018311 | 9.2926 | 4.303 | 85.7437 | 4.4907 | 85.9314 | 12.6846 | 123.3215 | 9.4803 | 123.6511 | 123.6191 | 123.4634 | 123.7381 | 123.2758 | -123.3627 | -123.6694 | 123.4406 | 123.4634 | 15.8844 | 50.3403
473.4844 | 123.642 | -48.999 | 74.4415 | 0.049069 | 0.034899 | 0.083425 | 0.091847 | 0.0016711 | -0.011453 | 0.00037059 | -0.5255 | 0.01618 | 0.10414 | 0.58743 | -0.015768 | 0.46245 | 0.028183 | -32.0618 | 74.4598 | -49.1776 | 74.6704 | -34.4925 | -47.818 | -14.3967 | 1.8402 | 74.4827 | -48.9944 | 74.4598 | -39.7659 | 35.5499 | -44.6045 | -0.17853 | 0.018311 | 0.22888 | 14.5065 | 34.6024 | 1.181 | 34.7809 | 1.3596 | 0.004577 | 0.041199 | 0.018311 | 9.2331 | 4.3945 | 84.5489 | 4.39 | 84.5444 | 14.6851 | 123.848 | 9.2285 | 123.4543 | 123.6374 | 123.4772 | 123.4589 | 123.4818 | -123.6191 | -123.436 | 123.6694 | 123.4589 | 16.9373 | 50.8392
474.4844 | 123.7335 | -47.8683 | 75.5905 | 0.1101 | 0.015673 | 0.070607 | 0.092915 | 0.0048751 | 0.0088408 | -0.010311 | -0.58653 | 0.014044 | 0.102 | 0.33856 | -0.0040182 | 0.19969 | 0.031387 | -33.0185 | 75.6271 | -47.9874 | 75.8286 | -33.728 | -46.5134 | -15.4221 | -1.2085 | 75.7416 | -47.7722 | 75.7782 | -38.8916 | 28.1982 | -43.5242 | -0.11902 | 0.036621 | 0.23804 | 14.1403 | 32.4463 | 1.355 | 32.5653 | 1.474 | 0.09613 | 0.15106 | 0.18768 | 8.9767 | 4.3442 | 76.0666 | 4.248 | 75.9705 | 14.2593 | 123.8159 | 8.8806 | 123.5504 | 123.6145 | 123.5138 | 123.4955 | 123.6099 | -123.5779 | -123.3627 | 123.6969 | 123.6465 | 14.8499 | 46.6599
475.4844 | 123.6877 | -47.4609 | 75.9888 | 0.15588 | 0.030627 | 0.075948 | 0.089711 | 0.0027391 | -0.0018402 | -0.0049704 | -0.23558 | 0.014044 | 0.11161 | 0.51907 | -0.010427 | 0.38341 | 0.026047 | -32.2449 | 75.8743 | -47.7127 | 75.9659 | -33.3984 | -46.312 | -12.41 | -1.8631 | 75.9201 | -47.525 | 76.0025 | -39.006 | 25.6439 | -43.3273 | -0.25177 | -0.11444 | -0.022889 | 14.0625 | 35.051 | 1.149 | 35.3027 | 1.4008 | -0.064087 | -0.068665 | 0.013732 | 8.4549 | 4.1336 | 73.1049 | 4.1977 | 73.1689 | 14.3143 | 123.6786 | 8.519 | 123.5275 | 123.587 | 123.4451 | 123.3353 | 123.381 | -123.7015 | -123.5138 | 123.4268 | 123.4634 | 15.2161 | 45.5978
476.4844 | 123.7015 | -32.5378 | 90.889 | -0.53076 | -0.014234 | 0.067403 | 0.098256 | 0.0006031 | 0.0056368 | -0.013515 | 0.16115 | 0.010839 | -0.0090826 | -3.1262e-05 | -0.022176 | 0.033069 | -0.013474 | -17.7017 | 92.3447 | -31.4026 | 91.658 | -18.5394 | -30.5786 | 0.70496 | -42.3843 | 91.452 | -32.1854 | -41.9724 | -32.254 | -50.5371 | -32.4692 | 1.1353 | 1.4557 | 0.76904 | 13.9984 | 33.2428 | 1.9592 | 32.1075 | 0.82398 | 0.35248 | 0.56305 | -132.8613 | 0.28381 | 0.068665 | -17.9993 | -0.28381 | -18.3517 | 12.8632 | 123.0606 | -0.068664 | -9.787 | 123.7473 | 123.6374 | 124.8825 | 123.9899 | -122.2916 | -123.0743 | 124.1959 | -9.4345 | 14.8361 | -9.8465
477.4844 | 123.674 | -35.5453 | 87.9776 | 0.094845 | 0.031695 | 0.072743 | 0.089711 | 0.0006031 | 0.022727 | 0.0025066 | 0.14589 | 0.017248 | 0.0048024 | -0.010712 | -0.013631 | 0.014911 | -0.016678 | -21.9864 | 87.941 | -35.6827 | 87.9456 | -21.936 | -34.1583 | -1.4374 | -31.6818 | 87.973 | -35.614 | -34.3872 | -31.4987 | -34.758 | -30.4047 | -0.13733 | -0.036621 | -0.032043 | 13.6093 | 34.108 | 1.387 | 34.2453 | 1.5244 | -0.068665 | -0.004578 | -122.3648 | 4.0466 | 5.1407 | 0.78735 | 5.2094 | 0.85602 | 13.7466 | 123.6282 | 4.1153 | 1.2268 | 123.6237 | 123.587 | 123.4863 | 123.5184 | -123.6603 | -123.5916 | 123.4909 | 1.1581 | 13.559 | 3.8635
478.4688 | 123.6694 | -35.3989 | 88.1012 | 0.17114 | 0.0028555 | 0.08022 | 0.097188 | 0.0027391 | 0.0056368 | -0.0071064 | 0.054336 | 0.023657 | 0.0037344 | -0.02887 | -0.010427 | 0.011707 | 0.0068215 | -23.6847 | 88.1607 | -35.495 | 88.1195 | -22.0276 | -33.5815 | -4.1061 | -31.2698 | 88.1149 | -35.4584 | -34.3094 | -31.4987 | -34.4147 | -30.4916 | -0.09613 | 0.05951 | 0.018311 | 13.3713 | 31.2927 | 1.8173 | 31.3889 | 1.9135 | -0.059509 | 0.013733 | -122.4106 | 3.9001 | 4.9072 | 0.98419 | 4.9667 | 1.0437 | 13.4674 | 123.6145 | 3.9597 | 1.149 | 123.6557 | 123.5733 | 123.5596 | 123.5138 | -123.5962 | -123.5596 | 123.5184 | 1.0895 | 11.7142 | 4.129
479.4844 | 123.6877 | -45.1767 | 78.1769 | -2.5754 | -0.00034947 | 0.08022 | 0.092915 | 0.0038071 | 0.25878 | 0.02921 | -0.067735 | 0.012976 | 0.15113 | 0.040558 | 0.19038 | 0.045887 | 0.0089575 | -18.187 | 92.7429 | -29.1641 | 82.7637 | -28.7704 | -41.6611 | -11.7828 | -30.748 | 79.1794 | -44.0964 | -30.8853 | 78.2913 | -31.1371 | 59.9762 | 16.0126 | 14.566 | 4.5868 | 16.4062 | 33.3939 | 3.5156 | 17.3813 | -12.4969 | 1.0803 | 1.0025 | -109.0622 | 123.468 | 105.1529 | 14.0396 | 104.0726 | 12.9593 | 0.39368 | 111.9278 | 122.3877 | 13.2111 | 121.907 | 123.2758 | 137.9196 | 124.3561 | -107.341 | -122.2733 | 127.9404 | 14.2914 | 26.9897 | 14.4287
480.4844 | 123.7427 | -34.9182 | 88.5132 | 0.1101 | -0.0035535 | 0.075948 | 0.095051 | -0.0036699 | 0.0099088 | -0.0092424 | 0.49684 | 0.022589 | -0.0037426 | -0.038483 | -0.0082912 | 0.0095709 | 0.011093 | -22.2427 | 88.559 | -35.0189 | 88.4628 | -20.1279 | -33.9386 | -4.8065 | -31.1737 | 88.4903 | -34.9731 | -33.9294 | -31.0364 | -33.9752 | -30.1804 | -0.10071 | 0.045776 | -0.050354 | 14.7903 | 30.1117 | 0.97961 | 30.2124 | 1.0803 | -0.054932 | -0.022889 | -122.4426 | 3.8818 | 4.7379 | 0.94299 | 4.7928 | 0.99793 | 14.8911 | 123.4818 | 3.9368 | 1.0437 | 123.5779 | 123.4634 | 123.4772 | 123.4085 | -123.5321 | -123.4863 | 123.381 | 0.98877 | 12.6755 | 3.7445
481.4844 | 124.6124 | -42.3981 | 89.0533 | 0.079586 | 0.0049915 | 0.088765 | 0.11214 | 0.017693 | -0.014657 | 0.013188 | -0.2661 | 0.015112 | 0.1255 | 0.26807 | -0.033926 | 0.15056 | 0.020706 | -41.3589 | 70.1523 | -53.3981 | 70.4086 | -37.2162 | -51.384 | -21.9772 | 21.2814 | 70.546 | -52.3773 | 70.6924 | -57.3624 | -137.1826 | -78.4287 | -11.0001 | -18.9011 | -18.6447 | 5.1819 | 20.4208 | -8.9859 | 31.4209 | 2.0142 | -9.9792 | -18.5074 | -18.3609 | -14.9643 | -36.0306 | -94.7845 | -26.0513 | -84.8053 | 16.1819 | 123.8068 | -4.985 | 123.0698 | 123.5504 | 122.9233 | 112.5504 | 112.944 | -142.4515 | -141.4307 | 112.8067 | 113.0905 | 1.0391 | 63.6795
482.4844 | 123.6923 | -49.5026 | 73.938 | 0.14062 | 0.0081955 | 0.069539 | 0.11107 | 0.0048751 | -0.0039762 | 0.0057106 | -0.66283 | 0.012976 | 0.12657 | 0.72629 | -0.031789 | 0.53188 | 0.059158 | -37.4542 | 73.9105 | -49.6719 | 73.9609 | -33.6182 | -47.5479 | -21.1212 | 17.5232 | 73.8373 | -49.5529 | 73.9883 | -38.2324 | 57.1884 | -42.0227 | -0.16937 | -0.027466 | 0.022888 | 15.8844 | 28.3813 | 1.9547 | 28.5507 | 2.124 | -0.050354 | -0.10071 | 0.050354 | 11.2701 | 7.4799 | 106.691 | 7.5302 | 106.7413 | 16.0538 | 123.6328 | 11.3205 | 123.5413 | 123.5825 | 123.3902 | 123.4131 | 123.3398 | -123.6099 | -123.4909 | 123.4634 | 123.4909 | 12.0483 | 67.0258
483.4844 | 123.6786 | -49.1043 | 74.3179 | 0.1101 | 0.02315 | 0.081288 | 0.10573 | 0.0016711 | 0.00029581 | 0.0067786 | -0.43395 | 0.01618 | 0.14152 | 0.59918 | -0.022176 | 0.38448 | 0.036728 | -37.207 | 74.2218 | -49.3057 | 74.5605 | -32.6386 | -46.5225 | -22.4716 | 20.8832 | 74.2218 | -49.1867 | 74.3866 | -37.6648 | 61.2259 | -41.8304 | -0.20142 | -0.09613 | 0.24262 | 16.4658 | 26.6327 | 2.5818 | 26.8341 | 2.7832 | -0.082398 | -0.09613 | 0.068665 | 11.4395 | 7.2739 | 110.3302 | 7.3563 | 110.4126 | 16.6672 | 123.8663 | 11.5219 | 123.5733 | 123.5275 | 123.4085 | 123.3261 | 123.3261 | -123.6237 | -123.5046 | 123.6649 | 123.4909 | 11.8973 | 69.9875
484.4844 | 123.6511 | -48.6053 | 74.7528 | 0.17114 | 0.0039235 | 0.075948 | 0.10253 | 0.0006031 | 0.0077728 | -0.0071064 | -0.55602 | 0.0044314 | 0.12977 | 0.79892 | 0.0045258 | 0.57567 | 0.047409 | -31.7642 | 74.8947 | -48.6237 | 75.2563 | -30.5054 | -48.4634 | -22.9202 | 15.6784 | 74.794 | -48.6008 | 74.9908 | -36.0764 | 57.5912 | -40.8051 | -0.01831 | 0.14191 | 0.50354 | 18.1 | 25.6851 | 0.14191 | 25.7034 | 0.16022 | 0.004578 | 0.041198 | 0.23804 | 12.529 | 7.8003 | 106.1966 | 7.7957 | 106.192 | 18.1183 | 123.88 | 12.5244 | 123.5916 | 123.5184 | 123.3948 | 123.5001 | 123.3994 | -123.3765 | -123.3536 | 123.8617 | 123.5962 | 16.8411 | 64.2838
485.4844 | 123.7015 | -50.7294 | 72.6654 | 0.064327 | 0.0060595 | 0.082356 | 0.10787 | 0.0038071 | 0.0024328 | -0.0081744 | -0.098252 | 0.0054994 | 0.1223 | 0.55432 | -0.00081422 | 0.38127 | 0.042068 | -33.7784 | 72.377 | -51.1322 | 72.377 | -32.5928 | -48.6877 | -25.3189 | 19.7937 | 72.3541 | -50.9491 | 72.6196 | -38.6124 | 60.4385 | -42.9794 | -0.40283 | -0.28839 | -0.28839 | 18.1366 | 25.4105 | 2.0416 | 25.8133 | 2.4445 | -0.21973 | -0.31128 | -0.045776 | 12.117 | 7.7499 | 111.1679 | 7.9697 | 111.3876 | 18.5394 | 123.5092 | 12.3367 | 123.5687 | 123.5092 | 123.3032 | 123.1064 | 123.0835 | -123.7976 | -123.6145 | 123.1064 | 123.349 | 16.951 | 70.5231
486.4844 | 123.6465 | -48.8205 | 74.6201 | 0.1101 | 0.042376 | 0.068471 | 0.11535 | 0.0016711 | 0.0013638 | 0.018529 | -0.64757 | -0.0019776 | 0.15327 | 0.55539 | -0.043539 | 0.36632 | 0.034592 | -32.0663 | 74.3317 | -49.2508 | 74.4049 | -30.0842 | -46.4676 | -26.1887 | 12.5519 | 74.3912 | -49.0585 | 74.7025 | -36.4105 | 62.59 | -40.9012 | -0.4303 | -0.28839 | -0.21515 | 18.7363 | 22.6318 | 2.3529 | 23.0621 | 2.7832 | -0.23804 | -0.22888 | 0.082398 | 12.41 | 7.9193 | 111.4105 | 8.1573 | 111.6486 | 19.1666 | 123.6557 | 12.648 | 123.761 | 123.5825 | 123.4497 | 123.1522 | 123.2117 | -123.8708 | -123.6786 | 123.2254 | 123.523 | 16.7542 | 61.3724
487.4844 | 123.7061 | -46.8384 | 76.5381 | 0.094845 | 0.00071953 | 0.083425 | 0.10573 | -0.0026019 | 0.022727 | -0.0049704 | -0.15929 | 0.012976 | 0.18104 | -0.0085763 | 0.17329 | 0.032001 | 0.0057535 | -29.7409 | 76.6113 | -46.9757 | 76.6113 | -28.1845 | -45.3186 | -24.8749 | -27.8229 | 76.5015 | -46.9574 | -19.7662 | 76.5747 | -20.0958 | 63.1805 | -0.13733 | 0.073242 | 0.073242 | 18.6539 | 21.9635 | 1.5198 | 22.1008 | 1.6571 | -0.11902 | -0.036621 | -96.3043 | 123.4131 | 110.0189 | 26.7426 | 110.1379 | 26.8616 | 18.7912 | 123.587 | 123.5321 | 27.1912 | 123.587 | 123.4589 | 123.4497 | 123.3398 | -123.5138 | -123.4955 | 123.4497 | 27.0721 | 17.0975 | 19.0155
488.4844 | 123.6465 | -46.843 | 76.5747 | 0.20166 | 0.012469 | 0.069539 | 0.10039 | 0.0027391 | -0.010385 | -0.019924 | -0.7086 | 0.015112 | 0.15113 | 0.7391 | -0.0018822 | 0.53081 | 0.045273 | -28.5416 | 76.5839 | -46.9894 | 76.7578 | -27.8458 | -44.1833 | -25.6485 | 6.3721 | 76.3596 | -46.9986 | 76.5472 | -35.6186 | 60.3882 | -36.937 | -0.14648 | 0.009155 | 0.1831 | 18.9972 | 21.1945 | 2.6596 | 21.3409 | 2.8061 | -0.15564 | -0.21515 | -0.027466 | 11.2244 | 9.906 | 107.2311 | 10.0616 | 107.3868 | 19.1437 | 123.7473 | 11.38 | 123.5458 | 123.5733 | 123.3582 | 123.4268 | 123.2025 | -123.5641 | -123.5733 | 123.6008 | 123.3902 | 18.3014 | 53.215
489.4844 | 123.6786 | -33.2062 | 90.2847 | 0.12536 | 0.0017875 | 0.072743 | 0.11428 | 0.015556 | 0.0013638 | -0.011379 | 0.19167 | 0.01618 | -0.01122 | -0.0043033 | -0.011495 | 0.0074349 | -0.0027915 | -14.5798 | 90.2664 | -33.3481 | 90.3259 | -13.6276 | -30.3772 | -11.4075 | -30.8807 | 90.2618 | -33.2703 | -32.7484 | -29.2511 | -32.8537 | -28.7888 | -0.14191 | -0.018311 | 0.041199 | 19.5786 | 21.7987 | 2.829 | 21.9406 | 2.9709 | -0.064087 | -0.022888 | -123.0331 | 3.9551 | 4.4174 | 0.35248 | 4.4815 | 0.41656 | 19.7205 | 123.674 | 4.0192 | 0.52185 | 123.6145 | 123.5321 | 123.4726 | 123.468 | -123.6328 | -123.555 | 123.5321 | 0.45776 | 18.6264 | 2.3254
490.4844 | 123.7473 | -32.8445 | 90.564 | 0.03381 | 0.0081955 | 0.079152 | 0.10146 | 0.0048751 | 0.0077728 | -0.0028344 | 0.20692 | 0.0076354 | 0.0026664 | -0.043823 | 0.0045258 | 0.01598 | -0.00065554 | -14.9734 | 90.5273 | -33.078 | 90.4175 | -14.0167 | -29.9789 | -12.0483 | -30.5054 | 90.477 | -32.991 | -32.1579 | -28.7888 | -32.2403 | -28.3173 | -0.23346 | -0.036621 | -0.14648 | 18.8278 | 20.7962 | 2.8656 | 21.0297 | 3.0991 | -0.14648 | -0.086975 | -122.7219 | 4.0558 | 4.5273 | 0.60425 | 4.6738 | 0.75073 | 19.0613 | 123.4955 | 4.2023 | 0.83313 | 123.6053 | 123.468 | 123.3719 | 123.3215 | -123.642 | -123.555 | 123.262 | 0.68664 | 17.8711 | 2.3392
491.4844 | 123.7198 | -47.3145 | 76.0986 | 0.12536 | 0.0092645 | 0.078084 | 0.12923 | 0.011284 | 0.033408 | -0.010311 | -0.082994 | 0.0054994 | 0.20454 | -0.025666 | 0.20854 | 0.035206 | -0.018814 | -30.5969 | 76.0803 | -47.5113 | 76.1078 | -26.5182 | -44.3161 | -24.7055 | -28.2532 | 76.0254 | -47.4701 | -19.9127 | 76.0895 | -20.6223 | 66.2018 | -0.19684 | -0.018311 | 0.009155 | 20.7962 | 22.6089 | 2.9984 | 22.8058 | 3.1952 | -0.15564 | -0.073242 | -96.0114 | 123.4039 | 113.5162 | 26.6922 | 113.6719 | 26.8478 | 20.993 | 123.6191 | 123.5596 | 27.5574 | 123.5916 | 123.4955 | 123.3948 | 123.3398 | -123.6099 | -123.5687 | 123.4222 | 27.4017 | 16.7175 | 19.0613
492.4688 | 123.7106 | -45.9961 | 77.4307 | 0.17114 | 0.011401 | 0.081288 | 0.11535 | -0.0004649 | 0.01525 | -0.017787 | -0.38817 | 0.0065674 | 0.17356 | 0.45178 | -0.0147 | 0.24456 | 0.028183 | -28.5049 | 77.1881 | -46.4218 | 77.3346 | -25.1999 | -43.2312 | -23.6343 | 8.5007 | 77.3071 | -46.1288 | 77.4948 | -31.0318 | 68.1335 | -31.0684 | -0.42572 | -0.24262 | -0.09613 | 20.7962 | 22.3618 | 2.7649 | 22.7875 | 3.1906 | -0.13275 | -0.1236 | 0.064087 | 14.9643 | 14.9277 | 114.1296 | 15.0604 | 114.2624 | 21.2219 | 123.7564 | 15.097 | 123.6237 | 123.6099 | 123.436 | 123.1842 | 123.3032 | -123.8525 | -123.5596 | 123.3307 | 123.4909 | 17.4912 | 54.4968
493.4844 | 123.6877 | -47.5342 | 75.8881 | 0.03381 | 0.024218 | 0.088765 | 0.099324 | 0.011284 | 0.029135 | 0.0035746 | -0.23558 | 0.0076354 | 0.21095 | 0.41974 | -0.0040182 | 0.20824 | 0.020706 | -27.301 | 75.6912 | -48.2437 | 75.4623 | -24.7742 | -44.7601 | -22.7875 | 7.6035 | 75.5676 | -47.3465 | 75.9201 | -24.1608 | 67.3279 | -21.6202 | -0.70953 | -0.19684 | -0.42572 | 22.76 | 24.7467 | 2.774 | 25.4562 | 3.4836 | 0.18768 | -0.32044 | 0.032043 | 23.3734 | 25.914 | 114.8621 | 25.7263 | 114.6744 | 23.4695 | 123.7061 | 23.1857 | 123.2666 | 123.9349 | 122.9141 | 123.2254 | 123.1018 | -124.1318 | -123.2346 | 122.9965 | 123.4543 | 20.2332 | 55.1376
494.4844 | 123.6694 | -33.7372 | 89.6667 | 0.17114 | 0.012469 | 0.083425 | 0.11535 | 0.0016711 | 0.0045688 | -0.016719 | 0.14589 | 0.0087034 | 0.0069384 | 0.011719 | -0.0093592 | 0.0085029 | 0.0036165 | -13.3896 | 90.3122 | -33.2748 | 90.2893 | -11.5036 | -30.7709 | -9.4711 | -31.3156 | 90.2893 | -33.2474 | -32.9178 | -29.7729 | -33.2382 | -29.3015 | 0.46234 | 0.64545 | 0.62256 | 22.2336 | 24.2661 | 2.9663 | 23.8037 | 2.504 | 0.48981 | 0.62256 | -122.5845 | 3.9642 | 4.4357 | 0.49896 | 3.9459 | 0.009155 | 21.7712 | 123.5641 | 3.4744 | 0.32959 | 123.587 | 123.5367 | 124.0494 | 124.0265 | -122.9416 | -122.9141 | 124.0265 | 0.8194 | 20.3476 | 2.4216
495.4844 | 123.7885 | -33.49 | 89.8499 | 0.094845 | 0.0081955 | 0.075948 | 0.10466 | 0.0027391 | 0.023795 | 0.0014386 | 0.20692 | 0.0097714 | -0.0080146 | -0.0096443 | -0.0061552 | 0.013843 | 0.0036165 | -15.2756 | 89.9139 | -33.6411 | 89.8499 | -11.3113 | -30.0613 | -9.5627 | -32.0847 | 89.8773 | -33.5587 | -33.5678 | -29.3838 | -33.7189 | -29.1275 | -0.15106 | 0.064086 | 0 | 22.1786 | 23.9273 | 3.4286 | 24.0784 | 3.5797 | -0.068665 | 0.027465 | -123.4177 | 4.1061 | 4.3625 | -0.22888 | 4.4312 | -0.16022 | 22.3297 | 123.4909 | 4.1748 | -0.009155 | 123.555 | 123.436 | 123.4039 | 123.3673 | -123.4909 | -123.4085 | 123.3398 | -0.07782 | 18.2144 | 1.4053
496.4844 | 123.6923 | -47.1176 | 76.5518 | 0.14062 | 0.0039235 | 0.075948 | 0.12282 | 0.012352 | 0.014182 | -0.0081744 | -0.23558 | 0.0076354 | 0.23552 | -0.0075083 | 0.25446 | 0.028797 | -0.0049285 | -27.7496 | 76.3321 | -47.2687 | 91.507 | -9.8969 | -39.5691 | -20.8374 | -30.1895 | 77.2614 | -46.1975 | -22.3297 | 76.2909 | -22.7417 | 66.8427 | -0.15106 | -0.21973 | 14.9551 | 37.2208 | 26.2802 | 7.5485 | 26.4313 | 7.6996 | 0.9201 | 0.70953 | -98.8815 | 123.4085 | 113.9603 | 24.3759 | 113.0402 | 23.4558 | 37.3718 | 138.7756 | 122.4884 | 23.8678 | 123.6008 | 123.4589 | 123.4497 | 124.379 | -123.8205 | -122.7493 | 138.6246 | 24.7879 | 19.368 | 16.9281
497.4844 | 123.6511 | -34.9594 | 88.5544 | 0.29321 | 0.010333 | 0.081288 | 0.17196 | -0.0090099 | 0.075064 | -0.0071064 | 0.16115 | 0.010839 | -0.00053758 | -0.013916 | -0.015768 | 0.0020939 | 0.016434 | -8.4915 | 88.9206 | -34.671 | 89.0442 | -9.4849 | -14.1403 | -7.7911 | -33.316 | 88.9618 | -34.6115 | -34.9594 | -31.2149 | -35.17 | -30.6885 | 0.28839 | 0.36621 | 0.48981 | 25.4745 | 27.1683 | 20.8191 | 26.8799 | 20.5307 | 0.3479 | 0.40741 | -123.5138 | 3.7445 | 4.2709 | -0.21057 | 3.923 | -0.55847 | 25.1862 | 123.7152 | 3.3966 | -0.3479 | 123.5916 | 123.5733 | 123.88 | 123.9212 | -123.2254 | -123.1659 | 124.0036 | 0 | 26.4679 | 1.6434
498.4844 | 123.5687 | -49.6765 | 73.7045 | -0.17981 | 0.026354 | 0.089833 | 0.48812 | 0.0080791 | 0.36346 | -0.00069841 | -0.61705 | 0.01618 | 0.18852 | 0.68783 | 0.00025378 | 0.41011 | 0.059158 | -6.2485 | 73.5535 | -49.9512 | 73.4207 | -16.7358 | 15.7288 | -14.6484 | 2.774 | 73.5764 | -49.8138 | 73.3658 | -38.3743 | 60.6308 | -39.1067 | -0.27466 | -0.15106 | -0.28381 | 32.9407 | 35.0281 | 65.4053 | 35.3027 | 65.6799 | -0.13733 | -0.12817 | -0.33874 | 11.3022 | 10.5698 | 110.3073 | 10.7071 | 110.4446 | 33.2153 | 123.3719 | 11.4395 | 123.1796 | 123.5046 | 123.3902 | 123.23 | 123.2529 | -123.6557 | -123.5184 | 123.0972 | 123.0423 | 43.428 | 52.4506
499.4844 | 123.5596 | -37.056 | 86.5311 | -0.16455 | 0.014605 | 0.095174 | 0.47423 | 0.0006031 | 0.33996 | -0.011379 | -0.25084 | 0.019384 | 0.0069384 | 0.40585 | -0.0029502 | 0.39623 | -0.012405 | 6.2942 | 84.3567 | -39.006 | 84.9472 | -6.6101 | 19.9356 | -4.4266 | -38.1546 | 85.0479 | -38.2919 | -39.1342 | -35.5545 | -51.3931 | -35.8337 | -1.9501 | -2.1744 | -1.5839 | 30.4459 | 32.6294 | 56.9916 | 34.5795 | 58.9416 | -1.236 | -1.4832 | -125.6653 | 1.5015 | 1.2222 | -14.3372 | 2.4582 | -13.1012 | 32.3959 | 123.9532 | 2.7374 | -0.84229 | 123.3627 | 123.3398 | 121.4127 | 122.1039 | -125.5371 | -124.823 | 122.0032 | -2.0782 | 43.3502 | -1.0986
500.4844 | 123.6374 | -53.6179 | 69.0674 | -0.51551 | 0.010333 | 0.088765 | 0.57036 | 0.012352 | 0.44677 | 0.0057106 | -0.25084 | 0.012976 | 0.24513 | -0.0043033 | 0.25874 | 0.029865 | 0.00041246 | -4.6417 | 69.0628 | -54.3823 | 69.0537 | -20.2515 | 14.3875 | -18.0084 | -40.3336 | 70.7611 | -51.0956 | -24.4034 | 68.7241 | -24.8749 | 59.8618 | -0.76446 | -0.004578 | -0.013733 | 33.3664 | 35.6094 | 68.0054 | 36.3739 | 68.7698 | 2.5223 | 1.6937 | -93.4708 | 122.3419 | 113.4796 | 28.743 | 110.9573 | 26.2207 | 34.1309 | 123.436 | 119.8196 | 26.6922 | 123.4451 | 121.8567 | 122.6807 | 124.379 | -123.4497 | -120.163 | 122.6715 | 29.2145 | 48.9761 | 13.2843
501.4844 | 123.587 | -39.7751 | 83.5785 | -0.80542 | 0.032763 | 0.096242 | 0.79894 | 0.023033 | 0.55892 | 0.049504 | -0.47972 | 0.020452 | 0.018688 | -0.014984 | -0.0147 | 0.0074349 | -0.00065554 | 39.9216 | 83.5556 | -39.8987 | 83.7112 | -24.7696 | 69.4016 | -31.5674 | -38.118 | 83.5648 | -39.8849 | -39.3723 | -35.5865 | -39.4867 | -35.2707 | -0.1236 | -0.022888 | 0.13275 | 15.0055 | 8.2077 | 109.1766 | 8.3313 | 109.3002 | -0.10986 | -0.013733 | -122.9507 | 4.1885 | 4.5044 | 0.28839 | 4.6143 | 0.39825 | 15.1291 | 123.6099 | 4.2984 | 0.5127 | 123.4543 | 123.4497 | 123.3307 | 123.3398 | -123.4772 | -123.4634 | 123.4863 | 0.40283 | 79.6967 | 1.6571
502.4844 | 122.9599 | -26.532 | 96.3959 | 0.21692 | 0.0049915 | 0.010793 | 0.030965 | 0.01342 | 0.0045688 | -0.014583 | -0.75438 | 0.021521 | 0.01762 | -0.029938 | -0.0018822 | 0.0085029 | 0.013229 | -22.5815 | 97.0642 | -26.5594 | -25.8865 | -21.2631 | -25.9918 | -20.8191 | -26.3626 | 96.5927 | -26.5366 | -28.9444 | -23.4741 | -28.9993 | -23.3643 | -0.027466 | 0.66833 | -122.2824 | 5.2689 | 5.7129 | 0.54016 | 5.7404 | 0.56763 | -0.004578 | 0.19684 | -125.3403 | 3.0579 | 3.1677 | -2.4673 | 3.1723 | -2.4628 | 5.2963 | 0.67291 | 3.0624 | -2.4078 | 123.6237 | 123.1293 | 123.5962 | 123.1247 | -122.9553 | -122.9324 | 0.64545 | -2.4124 | 3.9505 | 0.16937
503.4844 | 123.5825 | -40.7639 | 82.5851 | -0.1493 | -0.0035535 | 0.098378 | 0.61843 | 0.014488 | 0.43181 | 0.055913 | -0.61705 | 0.018316 | 0.031505 | -0.03421 | -0.0093592 | 0.0042299 | 0.0078895 | 47.818 | 82.4661 | -41.0339 | 82.2281 | -25.058 | 72.02 | -31.7368 | -39.0152 | 82.3059 | -40.9149 | -40.4114 | -36.3876 | -40.4297 | -36.1542 | -0.27008 | -0.11902 | -0.35706 | 15.7059 | 9.0271 | 112.7838 | 9.2972 | 113.0539 | -0.15106 | -0.27924 | -122.9965 | 4.3762 | 4.6097 | 0.33417 | 4.7607 | 0.48523 | 15.976 | 123.262 | 4.5273 | 0.50354 | 123.5001 | 123.2208 | 123.23 | 123.0698 | -123.6191 | -123.5001 | 122.9919 | 0.35248 | 88.5818 | 1.7487
504.4844 | 123.587 | -56.749 | 66.5176 | -0.60706 | 0.0081955 | 0.13363 | 0.77544 | 0.0080791 | 0.58669 | 0.026005 | -1.0901 | 0.010839 | 0.21522 | 0.50626 | -0.0050872 | 0.24028 | 0.070908 | 29.0634 | 66.0782 | -57.2845 | 65.7944 | -13.4811 | 53.0777 | -6.926 | -0.28381 | 66.3162 | -57.0236 | 66.243 | -38.2645 | 57.225 | -38.1729 | -0.53558 | -0.43945 | -0.72327 | 43.2678 | 49.823 | 109.8267 | 50.3586 | 110.3622 | -0.27466 | -0.20142 | -0.27466 | 18.4845 | 18.576 | 113.974 | 18.8507 | 114.2487 | 43.8034 | 123.0789 | 18.7592 | 123.2666 | 123.3627 | 123.3398 | 122.8271 | 123.0652 | -123.8022 | -123.5413 | 122.5433 | 122.9919 | 85.8124 | 56.4651
505.4844 | 123.5596 | -39.1617 | 84.1644 | 0.094845 | -0.031324 | -0.01057 | 0.038441 | -0.0004649 | 0.0035008 | -0.00069841 | -1.4868 | 0.011908 | 0.20988 | 0.76153 | -0.016836 | 0.48488 | 0.081589 | -33.2245 | 84.1003 | -39.4272 | -37.8571 | -32.2632 | -37.9669 | -31.723 | 17.6422 | 84.0591 | -39.2532 | 83.8303 | -25.6805 | 70.0745 | -26.4267 | -0.2655 | -0.064087 | -122.0215 | 6.8985 | 7.4387 | 1.1948 | 7.7042 | 1.4603 | -0.091553 | -0.10529 | -0.33417 | 13.4811 | 12.735 | 109.2361 | 12.8265 | 109.3277 | 7.164 | 1.5701 | 13.5727 | 123.0835 | 123.5275 | 123.3124 | 123.262 | 123.2208 | -123.5916 | -123.4177 | 1.3046 | 122.9919 | 5.9372 | 56.8039
506.4844 | 123.5962 | -39.5782 | 83.7662 | 0.30847 | 0.0081955 | -0.0062967 | 0.032033 | 0.012352 | -0.012521 | 0.014256 | -1.4868 | 0.022589 | 0.20134 | 0.57355 | -0.0029502 | 0.30544 | 0.059158 | -33.1879 | 83.432 | -40.1688 | -38.4064 | -32.135 | -38.5345 | -31.6727 | 13.9572 | 83.5968 | -39.8026 | 83.3954 | -24.147 | 73.4116 | -24.9252 | -0.59052 | -0.33417 | -122.1725 | 7.4432 | 7.9056 | 1.0437 | 8.4961 | 1.6342 | -0.2243 | -0.16937 | -0.37079 | 15.4312 | 14.653 | 112.9898 | 14.8773 | 113.2141 | 8.0338 | 1.7624 | 15.6555 | 123.1979 | 123.6008 | 123.3994 | 123.0103 | 123.175 | -123.9349 | -123.5687 | 1.1719 | 122.9736 | 6.3904 | 53.5355
507.4844 | 123.587 | -39.4592 | 83.9584 | 0.29321 | 0.018878 | -0.0052287 | 0.026692 | -0.0090099 | 0.0024328 | 0.0078466 | -1.2121 | 0.012976 | 0.1992 | 0.71881 | -0.0050872 | 0.46779 | 0.078384 | -34.4055 | 83.8715 | -39.7018 | -38.8184 | -33.6731 | -39.9857 | -33.6914 | 17.6559 | 82.8644 | -40.274 | 83.551 | -26.8158 | 70.3125 | -28.157 | -0.24261 | -0.086975 | -122.7768 | 5.7861 | 5.7678 | -0.52643 | 6.0104 | -0.28381 | -0.81482 | -1.0941 | -0.40741 | 12.6434 | 11.3022 | 109.7717 | 12.117 | 110.5865 | 6.0287 | 0.88348 | 13.4583 | 123.8251 | 123.5733 | 123.1384 | 123.3307 | 122.3236 | -123.6603 | -124.2325 | 0.64087 | 123.0103 | 5.0537 | 57.1152
508.4844 | 123.6374 | -39.6286 | 83.6975 | -0.13404 | 0.0092645 | -0.016978 | 0.029896 | 0.0038071 | 0.0045688 | -0.0092424 | -1.0596 | 0.017248 | 0.20881 | 0.80319 | -0.0072232 | 0.50518 | 0.057022 | -34.8907 | 83.7845 | -39.7888 | -38.0997 | -32.1304 | -38.237 | -31.9702 | 16.5298 | 83.6746 | -39.6881 | 83.6929 | -24.9115 | 69.7128 | -25.5753 | -0.16022 | 0.086975 | -121.7972 | 7.4982 | 7.6584 | 1.3916 | 7.8186 | 1.5518 | -0.059509 | -0.022888 | -0.004578 | 14.7171 | 14.0533 | 109.3414 | 14.1129 | 109.4009 | 7.6584 | 1.6891 | 14.7766 | 123.381 | 123.5733 | 123.3627 | 123.4131 | 123.3032 | -123.4863 | -123.3856 | 1.5289 | 123.3215 | 4.7379 | 56.1584
509.4844 | 123.5779 | -27.9785 | 95.4758 | 0.30847 | 0.011401 | -0.020183 | 0.032033 | -0.0090099 | 0.020591 | -0.0039024 | -0.17455 | 0.022589 | 0.01762 | 0.0095817 | -0.013631 | 0.0020939 | 0.011093 | -22.76 | 95.5444 | -28.0701 | -26.5411 | -21.5332 | -26.6602 | -21.3821 | -25.9369 | 95.5078 | -28.0106 | -27.1362 | -23.6389 | -27.2049 | -23.378 | -0.091552 | 0.068665 | -122.0169 | 6.4453 | 6.5964 | 1.3184 | 6.6879 | 1.4099 | -0.032043 | 0.032043 | -122.612 | 4.3396 | 4.6005 | 0.77362 | 4.6326 | 0.80566 | 6.5369 | 1.5289 | 4.3716 | 0.87433 | 123.6145 | 123.5184 | 123.5229 | 123.4863 | -123.5458 | -123.4863 | 1.4374 | 0.84229 | 5.2185 | 2.0416
510.4844 | 123.6557 | -44.6045 | 78.7811 | -0.50025 | -0.0067575 | -0.0062967 | 0.035237 | 0.010216 | 0.0045688 | -0.0028344 | -0.5255 | 0.018316 | 0.25795 | -0.014984 | 0.28437 | 0.034138 | 0.011093 | -40.5258 | 78.685 | -44.8654 | -43.0206 | -36.6898 | -43.1396 | -36.5524 | -19.4046 | 78.7079 | -44.7464 | -8.1802 | 78.7811 | -9.1599 | 72.8073 | -0.26093 | -0.09613 | -121.8018 | 7.9147 | 8.0521 | 1.4648 | 8.313 | 1.7258 | -0.14191 | -0.073242 | -86.9614 | 123.3856 | 117.4118 | 35.4446 | 117.5537 | 35.5865 | 8.1757 | 1.8448 | 123.5275 | 36.5662 | 123.5504 | 123.4543 | 123.2895 | 123.3124 | -123.6465 | -123.5275 | 1.5839 | 36.4243 | 4.0787 | 25.1999
511.4844 | 123.5962 | -42.2882 | 81.1203 | 0.20166 | 0.0081955 | -0.0041607 | 0.026692 | -0.0079419 | -0.0029082 | 0.0014386 | -0.34239 | 0.010839 | 0.24833 | 0.34711 | -0.011495 | 0.11104 | 0.034592 | -38.7955 | 80.4062 | -43.1534 | -40.3931 | -34.671 | -40.5075 | -34.4376 | 20.8466 | 80.7495 | -42.6498 | 80.6625 | -8.8669 | 75.1694 | -8.432 | -0.86517 | -0.71411 | -121.5134 | 7.6172 | 7.8506 | 1.7807 | 8.7158 | 2.6459 | -0.36163 | -0.37079 | -0.45776 | 33.4213 | 33.8562 | 117.4576 | 34.2178 | 117.8192 | 8.4824 | 2.7603 | 33.783 | 123.3124 | 123.5596 | 123.3994 | 122.6944 | 123.0377 | -124.2737 | -123.7701 | 1.8951 | 122.9507 | 3.4927 | 63.1348
512.4844 | 123.6237 | -39.8621 | 83.4778 | 0.079586 | 0.035967 | -0.013774 | 0.037373 | 0.0027391 | 0.0013638 | -0.0049704 | -0.69334 | 0.014044 | 0.20668 | 0.72095 | -0.012563 | 0.43682 | 0.080521 | -34.9365 | 83.4412 | -40.0406 | -38.3972 | -32.254 | -38.4933 | -32.0572 | 18.9926 | 83.3725 | -39.9536 | 83.3725 | -24.4583 | 71.1456 | -25.3418 | -0.17853 | -0.036621 | -121.875 | 7.608 | 7.8049 | 1.3687 | 7.9834 | 1.5472 | -0.091552 | -0.10529 | -0.10529 | 15.4037 | 14.5203 | 111.0077 | 14.6118 | 111.0992 | 7.7866 | 1.6434 | 15.4953 | 123.3261 | 123.4818 | 123.3261 | 123.3032 | 123.2346 | -123.5184 | -123.4314 | 1.4648 | 123.2346 | 4.9255 | 58.8547
513.4844 | 123.5687 | -36.5067 | 86.9431 | 0.079586 | 0.026354 | -0.0030927 | 0.030965 | 0.012352 | 0.012046 | -0.018856 | 0.039077 | 0.011908 | 0.016551 | -0.018189 | -0.017904 | 0.013843 | 0.0089575 | -32.5699 | 86.9339 | -36.6165 | -34.8587 | -29.2099 | -34.9777 | -29.0314 | -3.9139 | -3.6346 | -3.9093 | -3.9139 | -3.8818 | -3.8773 | -3.8544 | -0.10986 | -0.009155 | -121.8018 | 7.2968 | 7.4753 | 1.5289 | 7.5851 | 1.6388 | 32.5974 | -90.5777 | -90.8569 | 32.6248 | 32.6523 | 32.6294 | 0.054932 | 0.032044 | 7.4066 | 1.7578 | 0.027466 | -0.004577 | 123.5504 | 0.27466 | 123.4406 | 32.872 | -123.5596 | -90.8524 | 1.6479 | 32.5928 | 3.9368 | 32.5928
514.4844 | 123.6237 | -36.4105 | 87.0666 | 0.094845 | 0.021014 | 0.00011227 | 0.02776 | 0.010216 | 0.013114 | -0.013515 | 0.17641 | 0.011908 | 0.011211 | 0.0031737 | -0.017904 | 0.0052979 | 0.0025485 | -33.0093 | 87.03 | -36.5295 | -34.7443 | -29.1 | -34.8724 | -28.8986 | -3.9459 | -3.7674 | -3.9963 | -3.9551 | -3.9093 | -3.923 | -3.891 | -0.11902 | -0.036621 | -121.8109 | 7.3105 | 7.5119 | 1.5381 | 7.6309 | 1.6571 | 32.4142 | -90.834 | -91.0217 | 32.5012 | 32.5195 | 32.4875 | 0.10529 | 0.073242 | 7.4295 | 1.7853 | 0.086975 | 0.041199 | 123.5596 | 0.22888 | 123.4406 | 32.6431 | -123.5962 | -91.0629 | 1.6663 | 32.4554 | 3.4012 | 32.4646
515.4844 | 123.4863 | -36.1725 | 87.3138 | 0.32373 | 0.025286 | 0.0033163 | 0.024556 | 0.0070111 | -0.014657 | -0.010311 | 0.0085594 | 0.024725 | 0.014415 | -0.017121 | -0.016836 | 0.012775 | -0.0081325 | -33.2199 | 87.3047 | -36.3373 | -34.433 | -29.0131 | -34.5886 | -28.8116 | -4.2023 | -3.8452 | -4.1565 | -4.1382 | -3.9597 | -3.8498 | -3.9597 | -0.16479 | -0.009156 | -121.7468 | 7.1594 | 7.3608 | 1.5839 | 7.5256 | 1.7487 | 32.016 | -91.1591 | -91.452 | 32.2128 | 32.2128 | 32.3227 | 0.19684 | 0.3067 | 7.3242 | 1.9043 | 0.19684 | 0.01831 | 123.642 | 0.31128 | 123.4772 | 32.3273 | -123.6511 | -91.4703 | 1.7395 | 32.0343 | 2.9526 | 31.9702
516.4844 | 123.674 | -36.0306 | 87.4237 | 0.20166 | 0.011401 | 0.00011227 | 0.029896 | 0.0027391 | -0.011453 | -0.0017664 | -0.22032 | 0.0065674 | 0.0048024 | -0.070526 | -0.015768 | 0.0052979 | -0.00065554 | -32.991 | 87.4329 | -36.1176 | -34.4192 | -29.0039 | -34.6527 | -28.6926 | -3.6896 | -3.6301 | -3.8589 | -3.7354 | -3.6896 | -3.7262 | -3.685 | -0.086975 | 0.009155 | -121.843 | 7.0267 | 7.338 | 1.3779 | 7.4249 | 1.4648 | 32.1716 | -91.0538 | -91.1591 | 32.341 | 32.3456 | 32.3044 | 0.17395 | 0.13275 | 7.1136 | 1.6983 | 0.16937 | 0.1236 | 123.5504 | 0.22888 | 123.4634 | 32.4005 | -123.5413 | -91.2827 | 1.6113 | 32.2952 | 3.0396 | 32.341
517.4844 | 123.642 | -35.9207 | 87.5427 | 0.15588 | 0.024218 | -0.0041607 | 0.033101 | 0.0038071 | 0.0056368 | 0.0057106 | 0.14589 | 0.010839 | 0.016551 | -0.0075083 | -0.010427 | -0.0032471 | -0.0027915 | -32.8857 | 87.5153 | -36.0626 | -34.2316 | -28.8757 | -34.3872 | -28.6514 | -3.8864 | -3.717 | -3.9459 | -3.8773 | -3.8223 | -3.8315 | -3.8177 | -0.14191 | -0.027466 | -121.7743 | 7.045 | 7.2693 | 1.5335 | 7.4112 | 1.6754 | 31.9748 | -91.2598 | -91.42 | 32.0984 | 32.103 | 32.0892 | 0.12817 | 0.11444 | 7.1869 | 1.8311 | 0.1236 | 0.068665 | 123.5779 | 0.22888 | 123.436 | 32.2037 | -123.6053 | -91.4886 | 1.6891 | 32.0435 | 3.035 | 32.0343
518.4844 | 123.6603 | -35.495 | 87.9547 | 0.17114 | 0.019946 | -0.0073647 | 0.020283 | 0.020897 | 0.0013638 | 0.00037059 | 0.35951 | 0.023657 | 0.0090754 | -0.048096 | -0.010427 | 0.010639 | -0.0017235 | -32.8857 | 87.9547 | -35.5911 | -33.7921 | -29.187 | -33.9615 | -28.9307 | -4.0192 | -3.8406 | -4.0924 | -3.9825 | -3.9093 | -3.9368 | -3.9139 | -0.09613 | 0 | -121.7468 | 6.308 | 6.5643 | 1.5335 | 6.6605 | 1.6296 | 31.4026 | -91.7953 | -91.9373 | 31.5857 | 31.5811 | 31.5582 | 0.17853 | 0.15564 | 6.4041 | 1.799 | 0.1831 | 0.10986 | 123.5458 | 0.25177 | 123.4497 | 31.6544 | -123.5458 | -92.0471 | 1.7029 | 31.5125 | 2.6093 | 31.4758
519.4844 | 123.6877 | -35.0418 | 88.4125 | 0.1864 | 0.016741 | -0.0041607 | 0.030965 | -0.011147 | 0.014182 | -0.016719 | 0.19167 | 0.0033634 | 0.0037344 | -0.037415 | -0.02004 | 0.022388 | -0.028427 | -32.5058 | 88.385 | -35.2066 | -33.316 | -28.981 | -33.4763 | -28.6926 | -3.9688 | -3.9917 | -4.216 | -4.1199 | -4.0512 | -4.1016 | -4.0787 | -0.16479 | -0.027466 | -121.7285 | 6.0608 | 6.3492 | 1.5656 | 6.514 | 1.7303 | 30.8258 | -92.4042 | -92.5323 | 30.9906 | 30.9631 | 30.9402 | 0.13733 | 0.11444 | 6.2256 | 1.8906 | 0.16479 | 0.09613 | 123.5916 | 0.2243 | 123.4268 | 31.0501 | -123.6191 | -92.6285 | 1.7258 | 30.9219 | 2.536 | 31.073
520.4844 | 123.5916 | -35.1883 | 88.2889 | 0.23217 | 0.025286 | 0.0043843 | 0.037373 | -0.0015339 | 0.016318 | -0.0049704 | -0.052476 | 0.026861 | 0.016551 | 0.0085137 | -0.0093592 | -0.0085871 | -0.02095 | -32.547 | 88.3163 | -35.3302 | -33.2703 | -29.0222 | -33.4122 | -28.6652 | -4.4174 | -4.1245 | -4.3808 | -4.3854 | -4.3442 | -4.3808 | -4.335 | -0.14191 | 0.027466 | -121.5591 | 6.1661 | 6.5231 | 1.7761 | 6.665 | 1.918 | 30.8075 | -92.4133 | -92.6743 | 30.8441 | 30.8533 | 30.8075 | 0.045776 | 0 | 6.308 | 2.0599 | 0.036621 | -0.004578 | 123.6465 | 0.25635 | 123.5046 | 31.0638 | -123.6191 | -92.6697 | 1.918 | 30.8029 | 2.6413 | 30.7709
521.4844 | 123.6923 | -34.9045 | 88.5452 | 0.1101 | 0.016741 | -0.0041607 | 0.026692 | -0.0079419 | 0.0056368 | 0.0014386 | 0.2527 | 0.022589 | 0.010143 | 0.011719 | -0.012563 | -0.0011101 | -0.0027915 | -32.3456 | 88.5315 | -35.0555 | -33.1192 | -28.9719 | -33.3298 | -28.7476 | -4.1748 | -4.0649 | -4.2801 | -4.1748 | -4.0924 | -4.1153 | -4.1382 | -0.15106 | -0.013733 | -121.6644 | 5.9326 | 6.1569 | 1.5747 | 6.308 | 1.7258 | 30.6244 | -92.6102 | -92.72 | 30.8121 | 30.7663 | 30.7892 | 0.14191 | 0.1648 | 6.0837 | 1.9363 | 0.18768 | 0.10529 | 123.587 | 0.21515 | 123.436 | 30.8395 | -123.6008 | -92.8253 | 1.7853 | 30.7297 | 2.5589 | 30.7297
522.4844 | 123.6877 | -34.9319 | 88.5315 | 0.24743 | 0.024218 | -0.00095673 | 0.033101 | 0.0016711 | 0.0045688 | -0.014583 | 0.34425 | 0.024725 | 0.021892 | -0.016052 | -0.013631 | 0.017048 | 0.0057535 | -32.1991 | 88.504 | -35.0784 | -33.0414 | -28.83 | -33.2657 | -28.7338 | -4.2709 | -4.0833 | -4.3259 | -4.2343 | -4.1473 | -4.1794 | -4.1611 | -0.14648 | -0.027466 | -121.5729 | 6.102 | 6.1981 | 1.6663 | 6.3446 | 1.8127 | 30.6061 | -92.6147 | -92.7658 | 30.7846 | 30.7709 | 30.7526 | 0.16479 | 0.14648 | 6.2485 | 2.037 | 0.17853 | 0.091553 | 123.5825 | 0.24261 | 123.436 | 30.8487 | -123.6099 | -92.8574 | 1.8906 | 30.6976 | 2.7328 | 30.661
523.7656 | 123.6465 | -34.6985 | 88.7787 | 0.12536 | 0.019946 | -0.0095007 | 0.02242 | 0.0048751 | 0.0099088 | -0.017787 | 0.49684 | 0.014044 | 0.01762 | -0.025666 | -0.013631 | 0.0063669 | 0.015366 | -32.1259 | 88.765 | -34.8129 | -32.785 | -28.5324 | -32.9864 | -28.418 | -4.3259 | -4.0329 | -4.2847 | -4.216 | -4.1519 | -4.1611 | -4.1245 | -0.11444 | -0.013733 | -121.5637 | 6.1661 | 6.2805 | 1.712 | 6.395 | 1.8265 | 30.4138 | -92.8116 | -92.9947 | 30.5466 | 30.574 | 30.5374 | 0.16022 | 0.1236 | 6.2805 | 2.0279 | 0.13275 | 0.068665 | 123.5779 | 0.25177 | 123.4634 | 30.6656 | -123.5916 | -93.0634 | 1.9135 | 30.4825 | 2.5726 | 30.3726
524.5156 | 123.6328 | -34.8221 | 88.6871 | 0.094845 | 0.0071275 | -0.011638 | 0.029896 | -0.0090099 | 0.021659 | 0.0089146 | -0.067735 | 0.031134 | 0.025096 | 0.030945 | -0.018972 | 0.014911 | 0.0036165 | -32.1945 | 88.6917 | -34.9823 | -32.7484 | -28.3356 | -32.9773 | -28.2211 | -4.1473 | -3.8589 | -4.1336 | -4.0695 | -4.0375 | -4.0741 | -4.01 | -0.16022 | 0.004577 | -121.4355 | 6.4865 | 6.601 | 1.8448 | 6.7612 | 2.005 | 30.6885 | -92.5461 | -92.7567 | 30.7846 | 30.8121 | 30.748 | 0.1236 | 0.059509 | 6.6467 | 2.2339 | 0.09613 | 0.064087 | 123.674 | 0.27466 | 123.5138 | 30.9631 | -123.6694 | -92.8207 | 2.0737 | 30.7526 | 2.6276 | 30.6747
525.4844 | 123.6237 | -34.6527 | 88.8794 | 0.1864 | 0.018878 | -0.00095673 | 0.033101 | 0.011284 | 0.014182 | -0.016719 | -0.0066996 | 0.030065 | 0.010143 | 0.028808 | -0.021108 | 0.012775 | -0.012405 | -31.9427 | 88.8382 | -34.8083 | -32.4509 | -28.0746 | -32.7347 | -28.0014 | -4.1428 | -3.8635 | -4.1382 | -4.0787 | -4.0192 | -4.0237 | -3.9963 | -0.15564 | -0.041199 | -121.3303 | 6.5781 | 6.6513 | 1.918 | 6.8069 | 2.0737 | 30.5145 | -92.7429 | -92.9581 | 30.6335 | 30.6564 | 30.629 | 0.14191 | 0.11444 | 6.7337 | 2.3575 | 0.11902 | 0.05951 | 123.6465 | 0.27466 | 123.4909 | 30.7892 | -123.6877 | -93.0176 | 2.2018 | 30.574 | 2.71 | 30.5099
526.5156 | 123.7244 | -34.7168 | 88.7283 | 0.20166 | 0.021014 | -0.0020247 | 0.029896 | 0.023033 | 0.0056368 | -0.010311 | 0.29848 | 0.0054994 | -0.00053758 | -0.0096443 | -0.0050872 | 0.027729 | 0.010025 | -32.0435 | 88.7512 | -34.8541 | -32.7072 | -27.9053 | -32.9544 | -27.8183 | -3.8773 | -3.7399 | -3.9642 | -3.8269 | -3.7582 | -3.7903 | -3.7949 | -0.13733 | 0.022888 | -121.4355 | 6.8115 | 6.8985 | 1.7624 | 7.0358 | 1.8997 | 30.7526 | -92.4683 | -92.5552 | 30.9586 | 30.9219 | 30.9265 | 0.16937 | 0.17395 | 6.9489 | 2.1469 | 0.20599 | 0.13733 | 123.6053 | 0.2243 | 123.468 | 30.9769 | -123.5825 | -92.6926 | 2.0096 | 30.8899 | 2.6733 | 30.8395
527.6875 | 123.6374 | -34.6298 | 88.8657 | 0.1864 | 0.027422 | -0.012706 | 0.025624 | 0.036919 | 0.0035008 | -0.0028344 | 0.16115 | 0.022589 | 0.014415 | -0.014984 | -0.0082912 | 0.010639 | -0.018814 | -31.7642 | 88.8611 | -34.758 | -32.4417 | -28.0014 | -32.7118 | -27.9282 | -3.9368 | -3.717 | -3.9459 | -3.8864 | -3.8452 | -3.8406 | -3.8223 | -0.12817 | -0.004578 | -121.3074 | 6.6284 | 6.7017 | 1.918 | 6.8298 | 2.0462 | 30.6839 | -92.5827 | -92.7521 | 30.7846 | 30.8075 | 30.7892 | 0.1236 | 0.10529 | 6.7566 | 2.3163 | 0.10071 | 0.059509 | 123.6191 | 0.22888 | 123.4909 | 30.9128 | -123.6237 | -92.8116 | 2.1881 | 30.7434 | 2.8656 | 30.6931
528.4844 | 123.6053 | -34.4513 | 89.0991 | 0.29321 | 0.016741 | 0.00011227 | 0.037373 | -0.0079419 | 0.0056368 | -0.0060384 | 0.023818 | 0.022589 | 0.0015984 | -0.010712 | -0.016836 | 0.022388 | -0.0081325 | -31.6406 | 89.0671 | -34.6069 | -32.1854 | -28.9078 | -32.579 | -28.7704 | -4.0878 | -3.7262 | -4.0375 | -4.0237 | -3.9505 | -3.978 | -3.9413 | -0.15564 | -0.032043 | -121.2845 | 5.5435 | 5.6808 | 1.8723 | 5.8365 | 2.0279 | 30.4138 | -92.8253 | -93.1229 | 30.5008 | 30.5099 | 30.4733 | 0.096131 | 0.05951 | 5.6992 | 2.4216 | 0.086976 | 0.013733 | 123.674 | 0.31128 | 123.5184 | 30.7251 | -123.7061 | -93.1366 | 2.2659 | 30.4276 | 2.8107 | 30.3635
529.4844 | 123.6649 | -34.9045 | 88.5452 | 0.1101 | 0.012469 | 0.0011803 | 0.032033 | 0.0016711 | 0.0099088 | 0.0089146 | 0.32899 | 0.024725 | 0.0037344 | -0.036347 | -0.0093592 | 0.012775 | -0.0038605 | -31.8787 | 88.559 | -35.0464 | -32.579 | -27.9968 | -32.8308 | -27.9007 | -3.9825 | -3.7628 | -4.0009 | -3.9322 | -3.8773 | -3.8773 | -3.8544 | -0.14191 | 0.013733 | -121.1243 | 6.9077 | 7.0038 | 2.0737 | 7.1457 | 2.2156 | 30.9036 | -92.308 | -92.4774 | 31.0272 | 31.0501 | 31.0272 | 0.14648 | 0.1236 | 7.0496 | 2.4673 | 0.1236 | 0.068664 | 123.6053 | 0.23804 | 123.4634 | 31.1417 | -123.5916 | -92.5461 | 2.3254 | 30.9723 | 3.0258 | 30.9219
530.6875 | 123.7198 | -34.8862 | 88.559 | 0.049069 | 0.021014 | 0.0033163 | 0.029896 | 0.0080791 | -0.010385 | -0.0028344 | 0.084853 | 0.015112 | 0.016551 | -0.0010993 | -0.012563 | 0.025593 | 0.0068215 | -32.1991 | 88.5452 | -35.0784 | -32.6386 | -28.0289 | -32.9269 | -27.9053 | -3.8773 | -3.7582 | -3.9505 | -3.8361 | -3.7949 | -3.8315 | -3.7994 | -0.19226 | -0.013733 | -121.1975 | 6.8573 | 6.9809 | 1.9592 | 7.1732 | 2.1515 | 30.9357 | -92.3172 | -92.395 | 31.0913 | 31.0867 | 31.0547 | 0.15106 | 0.11902 | 7.0496 | 2.4399 | 0.15564 | 0.11444 | 123.6237 | 0.19226 | 123.4314 | 31.1279 | -123.6374 | -92.5095 | 2.2476 | 31.0501 | 2.6871 | 31.0089
531.4844 | 123.5733 | -34.7214 | 88.829 | 0.17114 | 0.017809 | -0.0052287 | 0.030965 | 0.012352 | 0.0056368 | -0.020992 | 0.17641 | 0.021521 | 0.015483 | -0.0085763 | -0.0082912 | 0.011707 | -0.031632 | -31.9977 | 88.8611 | -34.8312 | -32.0938 | -27.507 | -32.4554 | -27.42 | -4.0009 | -3.6758 | -3.9688 | -3.9459 | -3.891 | -3.891 | -3.8727 | -0.10986 | 0.032043 | -120.9229 | 7.2144 | 7.3013 | 2.2659 | 7.4112 | 2.3758 | 30.7526 | -92.5049 | -92.775 | 30.8304 | 30.8487 | 30.8304 | 0.09613 | 0.07782 | 7.3242 | 2.7374 | 0.07782 | 0.022888 | 123.6923 | 0.29297 | 123.5825 | 31.0455 | -123.6603 | -92.7979 | 2.6276 | 30.7755 | 2.7237 | 30.7205
532.4844 | 123.642 | -35.5911 | 87.6892 | 0.15588 | 0.02315 | -0.0062967 | 0.021352 | 0.0048751 | 0.0035008 | -0.010311 | 0.28322 | 0.0044314 | 0.019756 | -0.010712 | -0.016836 | 0.010639 | 0.0089575 | -32.0068 | 88.4399 | -35.1151 | -29.3518 | -24.6323 | -30.0705 | -28.3768 | -3.9139 | -3.5934 | -3.8589 | -3.7216 | -3.6484 | -3.6667 | -3.6072 | 0.47607 | 0.75073 | -117.041 | 10.9589 | 7.2144 | 5.5206 | 6.7383 | 5.0446 | 31.7322 | -91.2827 | -91.4108 | 31.9427 | 31.9839 | 31.9244 | 0.25177 | 0.19226 | 10.4828 | 5.7632 | 0.21057 | 0.13733 | 123.555 | 0.2655 | 124.0311 | 31.9977 | -122.8043 | -91.5482 | 6.2393 | 31.8695 | 3.5843 | 31.6772
533.4844 | 123.7152 | -48.1613 | 75.2426 | 0.064327 | 0.18337 | 0.047109 | 0.032033 | 0.0027391 | 0.12847 | -0.0039024 | 0.22218 | 0.019384 | 0.0069384 | -3.1262e-05 | -0.02004 | 0.012775 | 0.012161 | 62.7502 | 75.2151 | -48.4039 | -29.9423 | -25.7675 | -30.5511 | -25.621 | -1.6983 | -1.5335 | -1.7853 | -1.5976 | -1.5701 | -1.5839 | -1.5656 | -0.24262 | -0.027466 | -105.1849 | 22.3938 | 22.5403 | 17.6102 | 22.7829 | 17.8528 | 46.376 | -76.7761 | -76.8402 | 46.5912 | 46.5958 | 46.5775 | 0.21973 | 0.20142 | 22.6364 | 18.4616 | 0.21515 | 0.18768 | 123.6191 | 0.25177 | 123.3765 | 46.6278 | -123.6465 | -77.0279 | 18.219 | 46.5637 | 110.9116 | 46.463
534.4844 | 123.6877 | -46.2158 | 77.2156 | -0.027225 | 0.15773 | 0.044972 | 0.026692 | 0.028374 | 0.10497 | -0.011379 | 0.26796 | 0.011908 | 0.011211 | -0.022461 | -0.02004 | 0.013843 | 0.015366 | 69.0125 | 77.211 | -46.3623 | -31.1874 | -25.8957 | -31.3339 | -25.6256 | -1.6754 | -1.4969 | -1.7349 | -1.6159 | -1.5701 | -1.5793 | -1.561 | -0.14648 | -0.004577 | -108.403 | 20.3201 | 20.5902 | 14.8819 | 20.7367 | 15.0284 | 44.4809 | -78.7125 | -78.8315 | 44.6457 | 44.6548 | 44.6365 | 0.17395 | 0.15564 | 20.4666 | 15.1749 | 0.16479 | 0.11902 | 123.5733 | 0.23804 | 123.4268 | 44.7189 | -123.5779 | -78.9505 | 15.0284 | 44.5999 | 115.2283 | 44.5404
535.4844 | 123.674 | -45.8633 | 77.6093 | 0.064327 | 0.14491 | 0.04604 | 0.023488 | 0.0059431 | 0.096427 | 0.0057106 | 0.14589 | 0.01618 | 0.0048024 | -0.033142 | -0.022176 | 0.011707 | -0.0081325 | 70.015 | 77.6001 | -45.9915 | -30.6244 | -25.8179 | -30.6061 | -25.5981 | -1.5884 | -1.5289 | -1.7166 | -1.6617 | -1.6663 | -1.4969 | -1.5335 | -0.12817 | -0.009155 | -108.2336 | 20.0455 | 20.2652 | 15.2573 | 20.3934 | 15.3854 | 44.1467 | -79.1382 | -79.2709 | 44.1971 | 44.3298 | 44.3665 | 0.18311 | 0.21973 | 20.1736 | 15.3671 | 0.050354 | 0.054932 | 123.5916 | 0.18768 | 123.4634 | 44.3344 | -123.6008 | -79.3259 | 15.239 | 44.2017 | 115.8783 | 44.2749
536.4844 | 123.674 | -45.7718 | 77.6825 | 0.018551 | 0.15026 | 0.043904 | 0.029896 | 0.019829 | 0.097495 | 0.0025066 | 0.069594 | 0.020452 | 0.0069384 | 0.02774 | -0.015768 | 0.013843 | 0.0036165 | 70.2393 | 77.6367 | -45.9091 | -30.2948 | -25.5432 | -29.9469 | -25.3738 | -1.6754 | -1.6022 | -1.7944 | -1.6846 | -1.6708 | -1.6617 | -1.6617 | -0.13733 | -0.045776 | -107.9773 | 20.2286 | 20.398 | 15.8249 | 20.5353 | 15.9622 | 43.9774 | -79.2847 | -79.3671 | 44.101 | 44.1101 | 44.1101 | 0.13275 | 0.13275 | 20.3659 | 15.6143 | 0.1236 | 0.10986 | 123.5458 | 0.19226 | 123.4085 | 44.1696 | -123.5916 | -79.4769 | 15.477 | 44.0872 | 116.011 | 44.0964
537.4844 | 123.642 | -45.1538 | 78.3646 | -0.027225 | 0.17375 | 0.035359 | 0.034169 | 0.0038071 | 0.1242 | 0.00037059 | 0.13063 | 0.0087034 | 0.0080074 | -0.019257 | -0.015768 | 0.024524 | 0.0014805 | 70.3812 | 78.7537 | -44.8105 | -32.4829 | -25.9552 | -32.2174 | -26.3626 | -1.8036 | -1.7532 | -1.9363 | -1.8356 | -1.7487 | -1.7578 | -1.7303 | 0.34332 | 0.3891 | -110.8475 | 19.1986 | 18.7912 | 12.9364 | 18.4479 | 12.5931 | 43.2175 | -80.1178 | -80.2002 | 43.4052 | 43.4235 | 43.396 | 0.20599 | 0.17853 | 18.8553 | 12.3276 | 0.18768 | 0.10071 | 123.5641 | 0.1831 | 123.9075 | 43.4006 | -123.175 | -80.3009 | 12.6709 | 43.3182 | 115.535 | 43.3502
538.4844 | 123.7518 | -55.1651 | 68.2434 | -0.22559 | 0.45574 | 0.077016 | 0.037373 | -0.0036699 | 0.36346 | -0.0092424 | 0.17641 | 0.0087034 | 0.020824 | 0.013855 | -0.022176 | 0.014911 | -0.0092005 | 61.1114 | 68.0511 | -55.4764 | -0.58136 | -21.0617 | 3.772 | -20.3613 | -1.0345 | -0.89264 | -1.0849 | -1.0025 | -0.98877 | -0.98877 | -1.1353 | -0.31128 | -0.19226 | -68.8248 | 34.1034 | 34.8038 | 58.9371 | 35.1151 | 59.2484 | 54.0802 | -69.136 | -69.2459 | 54.1763 | 54.0298 | 54.1763 | -0.050354 | 0.09613 | 34.4147 | 54.895 | 0.09613 | 0.082398 | 123.5275 | 0.19226 | 123.2162 | 54.2725 | -123.7198 | -69.3283 | 54.5837 | 54.1626 | 116.2766 | 54.1306
539.4844 | 123.7152 | -99.6826 | 23.6298 | -0.68335 | 0.82103 | 0.1379 | 0.051259 | -0.0090099 | 0.6636 | -0.0028344 | 0.13063 | 0.011908 | 0.0058704 | -0.018189 | -0.021108 | 0.013843 | -0.0038605 | 17.1524 | 23.5611 | -99.8932 | -0.13733 | -45.6619 | 5.9235 | -44.8654 | -4.3991 | -4.216 | -4.422 | -4.3533 | -4.335 | -4.3488 | -4.3076 | -0.21057 | -0.068665 | -23.7671 | 54.0207 | 54.8172 | 105.6061 | 55.0278 | 105.8166 | 95.2606 | -27.8458 | -27.9831 | 95.3476 | 95.3751 | 95.3339 | 0.11444 | 0.073242 | 54.2313 | 99.7559 | 0.086975 | 0.068664 | 123.4543 | 0.20599 | 123.2437 | 95.4666 | -123.5229 | -28.0518 | 99.5453 | 95.3293 | 116.835 | 95.2835
540.4844 | 123.7152 | -103.0838 | 20.2698 | -0.68335 | 0.83492 | 0.12935 | 0.059804 | 0.0006031 | 0.68069 | 0.0089146 | -0.41869 | 0.0087034 | -0.017628 | -0.013916 | -0.016836 | 0.012775 | -0.033768 | 14.978 | 20.1645 | -103.2898 | -0.46692 | -48.5367 | 6.308 | -47.6486 | -4.39 | -4.3167 | -4.5502 | -4.4312 | -4.4449 | -4.422 | -4.422 | -0.20599 | -0.10528 | -20.7367 | 54.5471 | 55.4352 | 109.3918 | 55.6412 | 109.5978 | 98.5336 | -24.5865 | -24.7009 | 98.6389 | 98.6618 | 98.6618 | 0.12817 | 0.12817 | 54.7531 | 102.8229 | 0.10529 | 0.11902 | 123.4543 | 0.23346 | 123.2483 | 98.7671 | -123.5596 | -24.8199 | 102.6169 | 98.6526 | 118.0618 | 98.6938
541.4844 | 123.6557 | -104.8737 | 18.5349 | -0.69861 | 0.84133 | 0.14751 | 0.053395 | 0.015556 | 0.68496 | 0.0067786 | 0.084853 | 0.021521 | 0.0026664 | 0.018127 | -0.0147 | 0.014911 | -0.0092005 | 13.7375 | 18.4708 | -104.9698 | -0.3479 | -52.0065 | 6.3309 | -51.004 | -4.8477 | -4.6463 | -4.8706 | -4.7928 | -4.7836 | -4.7928 | -4.7516 | -0.096131 | -0.064087 | -18.8828 | 52.8671 | 53.8696 | 111.2045 | 53.9658 | 111.3007 | 100.0031 | -23.1812 | -23.3276 | 100.09 | 100.1221 | 100.0809 | 0.11902 | 0.077819 | 52.9633 | 104.6219 | 0.086975 | 0.077819 | 123.4406 | 0.2243 | 123.3444 | 100.2274 | -123.5046 | -23.4055 | 104.5258 | 100.0809 | 118.6111 | 100.0259
542.4844 | 123.6328 | -105.9814 | 17.3996 | -0.75965 | 0.86162 | 0.14004 | 0.042714 | 0.012352 | 0.70952 | 0.016392 | 0.054336 | 0.012976 | 0.0069384 | -0.012848 | -0.015768 | 0.0020939 | -0.0017235 | 12.8403 | 17.2668 | -106.1325 | -0.43488 | -53.8376 | 6.1752 | -52.7847 | -5.0171 | -4.7745 | -5.0308 | -5.0262 | -5.0171 | -5.0171 | -4.9759 | -0.15106 | -0.13275 | -17.8345 | 52.1439 | 53.1967 | 112.1567 | 53.3478 | 112.3077 | 100.9506 | -22.1741 | -22.4258 | 100.9644 | 101.0056 | 100.9644 | 0.054932 | 0.013733 | 52.2949 | 105.6976 | 0.013733 | 0.004578 | 123.3994 | 0.25635 | 123.2483 | 101.207 | -123.5321 | -22.4304 | 105.5466 | 100.9552 | 118.8217 | 100.9644
543.4844 | 123.7473 | -106.5399 | 16.8137 | -0.80542 | 0.86589 | 0.13149 | 0.052327 | 0.0070111 | 0.69243 | 0.0067786 | 0.039077 | 0.010839 | 0.0058704 | 0.0031737 | -0.013631 | 0.0052979 | -0.0070645 | 12.2864 | 16.7633 | -106.604 | -1.4832 | -56.5338 | 5.9052 | -55.8655 | -5.1682 | -4.9896 | -5.2094 | -5.127 | -5.3467 | -5.4062 | -5.1773 | -0.064087 | -0.050354 | -18.2968 | 50.0061 | 50.6744 | 112.4451 | 50.7385 | 112.5092 | 101.3306 | -21.8033 | -21.9406 | 101.1932 | 101.3626 | 101.1337 | 0.032044 | -0.19684 | 50.0702 | 105.1209 | -0.13733 | 0.082398 | 123.3673 | 0.21973 | 123.3032 | 101.5503 | -123.4177 | -22.023 | 105.0568 | 101.413 | 118.8263 | 101.3718
544.4844 | 123.587 | -107.1396 | 16.2048 | -1.0343 | 0.86589 | 0.14004 | 0.057667 | 0.01342 | 0.67 | 0.011052 | 0.16115 | 0.014044 | -0.015492 | -0.0064393 | -0.0029502 | 0.0085029 | -0.00065554 | 11.911 | 16.0446 | -107.2723 | -1.5152 | -55.1285 | 5.7999 | -54.3594 | -4.9026 | -4.7516 | -4.9255 | -4.8386 | -4.834 | -4.8477 | -4.8294 | -0.13275 | -0.16022 | -17.72 | 52.0111 | 52.7802 | 112.9395 | 52.9129 | 113.0722 | 102.2141 | -20.9564 | -21.0434 | 102.3056 | 102.3102 | 102.2919 | 0.09613 | 0.07782 | 52.1439 | 105.7571 | 0.091553 | 0.086975 | 123.317 | 0.17395 | 123.1842 | 102.388 | -123.4772 | -21.1304 | 105.6244 | 102.301 | 119.0506 | 102.2369
545.4844 | 123.6511 | -107.428 | 15.9302 | -0.65284 | 0.85628 | 0.1379 | 0.053395 | 0.018761 | 0.68923 | -0.0028344 | 0.19167 | 0.0033634 | 0.014415 | -0.033142 | -0.015768 | 0.0095709 | -0.019882 | 11.5768 | 15.8615 | -107.4738 | -1.6434 | -56.1172 | 5.7175 | -55.4031 | -5.0034 | -4.8614 | -5.1041 | -5.0034 | -4.9393 | -4.9576 | -4.9622 | -0.045776 | -0.068665 | -17.5735 | 51.3107 | 52.0248 | 113.1454 | 52.0706 | 113.1912 | 102.3239 | -20.7916 | -20.9335 | 102.4887 | 102.4658 | 102.4704 | 0.14191 | 0.14648 | 51.3565 | 105.8304 | 0.1648 | 0.10071 | 123.3353 | 0.24262 | 123.2895 | 102.5665 | -123.4039 | -21.0342 | 105.7846 | 102.4246 | 119.0048 | 102.4246
546.4844 | 123.674 | -61.4731 | 61.8301 | 0.079586 | 0.0060595 | 0.0054523 | 0.030965 | 0.01342 | -0.0050442 | -0.0081744 | 0.31374 | 0.010839 | -0.0058786 | -0.032074 | -0.0082912 | 0.019184 | 0.0057535 | 0.10529 | 0.14191 | -0.036621 | -0.068665 | -0.013733 | -0.054932 | 0 | 0.10986 | 0.13275 | -0.036621 | 0.15106 | 0.16022 | 0.13275 | 0.13275 | 61.4365 | -61.6882 | -61.8988 | 61.4594 | 61.4731 | 61.4182 | 0.036621 | -0.018311 | 61.4365 | -61.6974 | -61.6791 | 61.6333 | 61.6058 | 61.6058 | 0.16937 | 0.16937 | 0.022888 | -0.032044 | 0.19684 | 0.18768 | 0.17853 | 0.16937 | 61.615 | 61.6058 | -61.8668 | -61.8668 | 61.4044 | 61.6241 | 61.5784 | 61.5829
547.4844 | 123.6145 | -61.5555 | 61.7569 | 0.049069 | 0.025286 | -0.0020247 | 0.032033 | -0.0015339 | -0.0029082 | -0.013515 | 0.023818 | 0.019384 | -0.0016066 | 0.021332 | -0.013631 | 0.022388 | -0.0027915 | 0.050354 | 0.11902 | -0.059509 | -0.054932 | 0.022888 | -0.036621 | -0.022888 | 0.082397 | 0.13733 | -0.050354 | 0.1236 | 0.07782 | 0.073242 | 0.07782 | 61.496 | -61.6379 | -61.8118 | 61.5784 | 61.5326 | 61.5189 | 0.036621 | 0.022888 | 61.5051 | -61.6196 | -61.6333 | 61.6333 | 61.6333 | 61.6287 | 0.12817 | 0.1236 | 0.082397 | 0.004577 | 0.12817 | 0.17395 | 0.17853 | 0.18768 | 61.6745 | 61.6928 | -61.8164 | -61.8073 | 61.5005 | 61.6791 | 61.6058 | 61.6379
548.4844 | 123.6191 | -61.5555 | 61.7798 | -0.088261 | 0.0081955 | 0.00011227 | 0.026692 | -0.0047379 | -0.0071802 | -0.041286 | 0.069594 | 0.022589 | 0.0090754 | 0.020263 | -0.0093592 | 0.02132 | -0.016678 | 0.054932 | 0.082397 | -0.082397 | -0.054932 | -0.018311 | -0.064087 | -0.032043 | 0.082397 | 0.12817 | -0.050354 | 0.13275 | 0.091553 | 0.073242 | 0.10071 | 61.4731 | -61.6974 | -61.8347 | 61.5372 | 61.5234 | 61.4914 | 0.050354 | 0.01831 | 61.5051 | -61.6516 | -61.647 | 61.647 | 61.6562 | 61.6287 | 0.15106 | 0.1236 | 0.064086 | 0.027465 | 0.14191 | 0.18311 | 0.16479 | 0.17853 | 61.6379 | 61.6837 | -61.8622 | -61.8301 | 61.5005 | 61.6882 | 61.6104 | 61.6379
549.4844 | 123.6328 | -61.5784 | 61.7706 | 0.23217 | 0.00071953 | 0.0011803 | 0.023488 | 0.0006031 | -0.027475 | 0.0014386 | 0.054336 | 0.021521 | 0.013347 | 0.0063777 | -0.0050872 | 0.019184 | -0.014542 | 0 | 0.073242 | -0.10071 | -0.064087 | -0.022888 | -0.059509 | -0.013733 | 0.086975 | 0.11444 | -0.059509 | 0.13275 | 0.10071 | 0.07782 | 0.11444 | 61.4777 | -61.6974 | -61.8347 | 61.5555 | 61.5646 | 61.5189 | 0.086975 | 0.041199 | 61.5189 | -61.6562 | -61.6379 | 61.6791 | 61.6928 | 61.6562 | 0.17395 | 0.13733 | 0.07782 | 0.036621 | 0.16022 | 0.19226 | 0.17395 | 0.17395 | 61.6516 | 61.6928 | -61.8713 | -61.8301 | 61.5143 | 61.7111 | 61.5784 | 61.6653
550.4844 | 123.6603 | -61.5784 | 61.7752 | 0.14062 | 0.011401 | -0.014842 | 0.030965 | 0.0080791 | 0.010977 | 0.0025066 | 0.22218 | 0.022589 | 0.014415 | -0.0096443 | -0.0040182 | 0.010639 | -0.00065554 | 0.009155 | 0.073242 | -0.11902 | -0.041199 | 0.032043 | -0.036621 | -0.009155 | 0.073242 | 0.13733 | -0.059509 | 0.13733 | 0.13733 | 0.13733 | 0.14191 | 61.4594 | -61.702 | -61.8164 | 61.6104 | 61.5692 | 61.5417 | 0.10986 | 0.082398 | 61.5189 | -61.6379 | -61.6379 | 61.7157 | 61.7203 | 61.7157 | 0.20142 | 0.19684 | 0.15106 | 0.07782 | 0.19684 | 0.19684 | 0.19226 | 0.19684 | 61.6516 | 61.7157 | -61.8942 | -61.8347 | 61.5372 | 61.7157 | 61.5875 | 61.6516
551.4844 | 123.7564 | -61.5692 | 61.8347 | 0.094845 | 0.012469 | 0.0011803 | 0.02242 | -0.014351 | 0.00029581 | 0.011052 | 0.13063 | 0.014044 | 0.0069384 | -0.01178 | -0.015768 | 0.014911 | -0.0038605 | 0.045776 | 0.091553 | -0.073242 | -0.091553 | -0.022888 | -0.091553 | -0.036621 | 0.09613 | 0.13275 | -0.036621 | 0.14191 | 0.16022 | 0.041199 | 0.086975 | 61.496 | -61.7432 | -61.9263 | 61.5463 | 61.5326 | 61.4777 | 0.036621 | -0.018311 | 61.5326 | -61.702 | -61.6928 | 61.7294 | 61.6562 | 61.6104 | 0.1236 | 0.07782 | 0.050354 | -0.018311 | 0.19684 | 0.17853 | 0.16479 | 0.16937 | 61.6608 | 61.702 | -61.908 | -61.8713 | 61.4777 | 61.7111 | 61.615 | 61.6653
552.4844 | 123.6603 | -61.6196 | 61.7661 | -0.073002 | 0.013537 | 0.0022483 | 0.029896 | -0.0015339 | -0.0093172 | -0.0060384 | 0.10011 | 0.011908 | 0.011211 | -0.032074 | -0.013631 | 0.01598 | -0.0038605 | 0.041199 | 0.07782 | -0.045776 | -0.10071 | -0.018311 | -0.091553 | -0.21057 | 0.054932 | 0.09613 | -0.09613 | 0.12817 | 0.1236 | 0.10071 | 0.10529 | 61.5738 | -61.6882 | -61.8668 | 61.6013 | 61.409 | 61.528 | -0.1648 | -0.045777 | 61.5234 | -61.6699 | -61.6379 | 61.7432 | 61.7249 | 61.7203 | 0.20142 | 0.19684 | 0.027465 | -0.054932 | 0.21973 | 0.2243 | 0.1236 | 0.19226 | 61.6974 | 61.7157 | -61.8118 | -61.8622 | 61.5189 | 61.7477 | 61.6608 | 61.6745
553.4844 | 123.6557 | -61.615 | 61.7844 | 0.018551 | 0.0092645 | 0.016133 | 0.024556 | 0.0059431 | -0.0018402 | -0.0049704 | 0.084853 | 0.014044 | 0.0037344 | 0.043762 | -0.022176 | 0.025593 | -0.012405 | 0.041199 | 0.073242 | -0.082397 | -0.10071 | -0.032043 | -0.07782 | -0.045776 | -0.1236 | 0.10529 | -0.091553 | 0.12817 | 0.091553 | 0.10529 | 0.11902 | 61.5326 | -61.7111 | -61.8851 | 61.5829 | 61.5692 | 61.5372 | 0.036621 | 0.004577 | 61.5234 | -61.6791 | -61.6562 | 61.7065 | 61.734 | 61.7203 | 0.21057 | 0.19684 | 0.050354 | -0.018311 | 0.18311 | 0.21973 | 0.15564 | 0.19684 | 61.6882 | 61.7203 | -61.8668 | -61.8759 | 61.5143 | 61.7432 | 61.6562 | 61.4914
554.4844 | 123.6557 | -61.6013 | 61.7889 | 0.0032924 | 0.011401 | -0.0052287 | 0.018147 | -0.0015339 | -0.0061122 | -0.0028344 | 0.10011 | 0.0054994 | 0.00053042 | -0.0053713 | -0.015768 | 0.02132 | -0.013474 | 0.036621 | 0.059509 | -0.073242 | -0.068665 | -0.018311 | -0.054932 | -0.022888 | 0.059509 | 0.14648 | -0.054932 | 0.091553 | 0.073242 | 0.07782 | 0.09613 | 61.528 | -61.7294 | -61.8576 | 61.5829 | 61.5784 | 61.5463 | 0.050354 | 0.01831 | 61.5463 | -61.6425 | -61.6974 | 61.6745 | 61.6974 | 61.6791 | 0.15106 | 0.13275 | 0.054931 | 0.004577 | 0.12817 | 0.14649 | 0.13275 | 0.20142 | 61.6608 | 61.7477 | -61.8622 | -61.8439 | 61.5326 | 61.6928 | 61.6379 | 61.6608
555.4844 | 123.642 | -61.5921 | 61.8301 | 0.14062 | 0.00071953 | -0.014842 | 0.02776 | -0.0015339 | -0.0029082 | -0.011379 | 0.22218 | 0.0076354 | -0.0016066 | -0.0053713 | -0.015768 | 0.020252 | -0.0070645 | 0 | 0.09613 | -0.07782 | -0.045776 | 0.027466 | -0.041199 | -0.027466 | 0.018311 | 0.14648 | -0.064087 | 0.10529 | 0.07782 | 0.054932 | 0.091553 | 61.5143 | -61.734 | -61.8759 | 61.6196 | 61.5646 | 61.5509 | 0.050354 | 0.036621 | 61.528 | -61.6837 | -61.7249 | 61.6699 | 61.6837 | 61.647 | 0.15564 | 0.11902 | 0.10529 | 0.032044 | 0.14191 | 0.16937 | 0.17395 | 0.21057 | 61.6882 | 61.7386 | -61.908 | -61.8942 | 61.5463 | 61.6974 | 61.5921 | 61.6104
556.4844 | 123.5825 | -61.647 | 61.8347 | 0.1864 | 0.0017875 | -0.0095007 | 0.028828 | -0.010078 | -0.0093172 | -0.013515 | 0.054336 | 0.019384 | 0.0069384 | 0.0085137 | -0.012563 | 0.023456 | -0.014542 | -0.022888 | 0.11902 | -0.1236 | 0.11902 | 0.26093 | 0.16479 | 0.073242 | -0.10071 | 0.20142 | -0.073242 | 0.013733 | 0.032043 | 0.013733 | 0.050354 | 61.5234 | -61.7157 | -61.7157 | 61.908 | 61.7203 | 61.8118 | 0.19684 | 0.28839 | 61.5738 | -61.6333 | -61.821 | 61.6791 | 61.6974 | 61.6608 | 0.1236 | 0.086975 | 0.38452 | 0.24261 | 0.10529 | 0.086975 | 0.24261 | 0.27466 | 61.7661 | 61.8484 | -61.9583 | -61.908 | 61.7661 | 61.6608 | 61.6241 | 61.5463
557.4844 | 123.6649 | -61.6013 | 61.7752 | 0.018551 | 0.014605 | 0.0011803 | 0.033101 | -0.0079419 | 0.0045688 | -0.014583 | -0.0066996 | 0.019384 | -0.0037426 | -0.0096443 | -0.012563 | 0.010639 | -0.0038605 | 0.054932 | 0.073242 | -0.068665 | -0.10071 | -0.032043 | -0.10071 | -0.050354 | 0.10071 | 0.1236 | -0.050354 | 0.1236 | 0.12817 | 0.086975 | 0.11444 | 61.5326 | -61.702 | -61.8759 | 61.5692 | 61.5509 | 61.5005 | 0.018311 | -0.032043 | 61.5509 | -61.6516 | -61.6516 | 61.7294 | 61.7157 | 61.6882 | 0.16479 | 0.13733 | 0.036622 | -0.032043 | 0.17853 | 0.17395 | 0.14191 | 0.17395 | 61.6745 | 61.7249 | -61.8439 | -61.8256 | 61.5005 | 61.7249 | 61.6562 | 61.702
558.4844 | 123.6649 | -61.6196 | 61.7981 | 0.03381 | 0.012469 | 0.0075883 | 0.032033 | -0.0058059 | -0.0029082 | -0.0081744 | 0.17641 | 0.012976 | -0.0048106 | -0.012848 | -0.015768 | 0.022388 | -0.0327 | 0.032043 | 0.059509 | -0.054932 | -0.17853 | -0.045776 | -0.045776 | -0.086975 | 0.073242 | 0.09613 | -0.073242 | 0.11902 | 0.11902 | 0.086975 | 0.11902 | 61.5646 | -61.7386 | -61.9766 | 61.5738 | 61.5326 | 61.5738 | -0.032043 | 0.009156 | 61.5463 | -61.702 | -61.6791 | 61.7386 | 61.7386 | 61.7065 | 0.19226 | 0.16022 | 0.009156 | -0.1236 | 0.19226 | 0.19226 | 0.11444 | 0.16937 | 61.6791 | 61.7157 | -61.853 | -61.8713 | 61.441 | 61.7386 | 61.6516 | 61.6928
559.4844 | 123.6832 | -61.6333 | 61.8027 | 0.03381 | 0.018878 | -0.0052287 | 0.028828 | 0.0016711 | -0.0071802 | -0.012447 | 0.26796 | 0.0044314 | -0.00053758 | 0.01065 | -0.0072232 | 0.011707 | -0.019882 | 0.036621 | 0.086975 | -0.045776 | -0.10529 | -0.027466 | -0.12817 | -0.19684 | 0.050354 | 0.059509 | -0.082397 | 0.10529 | 0.14191 | 0.10071 | 0.10071 | 61.5875 | -61.7157 | -61.908 | 61.6058 | 61.4365 | 61.5051 | -0.15106 | -0.082398 | 61.5509 | -61.7432 | -61.6974 | 61.7752 | 61.734 | 61.734 | 0.18311 | 0.18311 | 0.01831 | -0.05951 | 0.2243 | 0.18768 | 0.13275 | 0.14191 | 61.7203 | 61.6928 | -61.8484 | -61.8851 | 61.528 | 61.7386 | 61.6699 | 61.6837
560.4844 | 123.6694 | -61.647 | 61.8301 | 0.094845 | 0.011401 | -0.0062967 | 0.020283 | -0.0026019 | -0.0018402 | -0.014583 | 0.20692 | 0.011908 | 0.011211 | -0.0064393 | -0.018972 | 0.017048 | -0.00065554 | -0.009155 | 0.082397 | -0.082397 | -0.041199 | 0.050354 | -0.032043 | -0.009155 | -0.004578 | 0.14648 | -0.068665 | 0.064087 | 0.07782 | 0.082397 | 0.07782 | 61.5646 | -61.7477 | -61.8713 | 61.6974 | 61.6379 | 61.615 | 0.073242 | 0.050354 | 61.5784 | -61.6837 | -61.7661 | 61.7249 | 61.7249 | 61.7294 | 0.14649 | 0.15106 | 0.13275 | 0.041198 | 0.14649 | 0.13275 | 0.16479 | 0.21515 | 61.7294 | 61.7935 | -61.9125 | -61.8988 | 61.6058 | 61.7111 | 61.6379 | 61.6425
561.4844 | 123.5733 | -61.6333 | 61.8805 | 0.094845 | 0.0060595 | -0.014842 | 0.02776 | 0.01342 | 0.0024328 | -0.0017664 | 0.20692 | 0.01618 | -0.00053758 | -0.0010993 | -0.0050872 | 0.01598 | -0.0092005 | -0.004578 | 0.10529 | -0.086975 | 0.009155 | 0.091553 | 0.009155 | 0.041199 | -0.050354 | 0.15564 | -0.073242 | -0.013733 | 0.018311 | 0.022888 | 0.027466 | 61.5463 | -61.7752 | -61.8713 | 61.7249 | 61.6745 | 61.6425 | 0.12817 | 0.09613 | 61.5601 | -61.7249 | -61.8942 | 61.6516 | 61.6608 | 61.6562 | 0.10071 | 0.09613 | 0.17853 | 0.09613 | 0.091553 | 0.059509 | 0.19226 | 0.22888 | 61.7386 | 61.7889 | -61.9675 | -61.9537 | 61.6425 | 61.6196 | 61.6287 | 61.5829
562.4844 | 123.6603 | -61.6241 | 61.8256 | 0.0032924 | 0.0060595 | -0.0030927 | 0.017079 | 0.018761 | 0.014182 | -0.010311 | 0.17641 | 0.015112 | -0.0016066 | -0.0075083 | -0.0072232 | 0.025593 | -0.013474 | 0.036621 | 0.059509 | -0.064087 | -0.064087 | 0.004578 | -0.064087 | -0.041199 | 0.059509 | 0.12817 | -0.054932 | 0.086975 | 0.082397 | 0.07782 | 0.09613 | 61.5601 | -61.7661 | -61.8896 | 61.6287 | 61.5829 | 61.5601 | 0.022888 | 0 | 61.5692 | -61.6974 | -61.7386 | 61.7065 | 61.7203 | 61.702 | 0.15106 | 0.13275 | 0.068665 | 0 | 0.13733 | 0.14191 | 0.1236 | 0.18311 | 61.6837 | 61.7523 | -61.8896 | -61.8805 | 61.5601 | 61.7111 | 61.6608 | 61.6837
563.5 | 123.6877 | -61.6287 | 61.7889 | 0.03381 | 0.016741 | 0.0054523 | 0.023488 | 0.0091481 | -0.012521 | -0.0071064 | 0.023818 | 0.015112 | 0.0058704 | -0.026734 | -0.018972 | 0.019184 | 0.0025485 | 0.041199 | 0.073242 | -0.050354 | -0.09613 | -0.032043 | -0.10071 | -0.059509 | 0.086975 | 0.10986 | -0.073242 | 0.091553 | 0.11902 | 0.082397 | 0.11902 | 61.5784 | -61.7157 | -61.8851 | 61.5967 | 61.5692 | 61.528 | -0.009155 | -0.050354 | 61.5555 | -61.6791 | -61.6974 | 61.7477 | 61.7477 | 61.7111 | 0.19226 | 0.15564 | 0.018311 | -0.045776 | 0.19226 | 0.16479 | 0.1236 | 0.18311 | 61.702 | 61.7386 | -61.8393 | -61.8622 | 61.5326 | 61.7203 | 61.6699 | 61.7157
564.4844 | 123.7198 | -61.6104 | 61.7798 | 0.018551 | 0.022082 | 0.0075883 | 0.020283 | 0.0027391 | -0.017862 | 0.0078466 | 0.069594 | 0.011908 | 0.01762 | -3.1262e-05 | -0.021108 | 0.023456 | -0.0027915 | 0.059509 | 0.073242 | -0.068665 | -0.10529 | -0.018311 | -0.086975 | -0.054932 | 0.082397 | 0.12817 | -0.050354 | 0.10529 | 0.11444 | 0.10986 | 0.1236 | 61.5417 | -61.7065 | -61.8851 | 61.5921 | 61.5555 | 61.5234 | 0.013733 | -0.01831 | 61.5601 | -61.6516 | -61.6745 | 61.7249 | 61.734 | 61.7203 | 0.17395 | 0.16022 | 0.050354 | -0.036621 | 0.16479 | 0.15564 | 0.14191 | 0.17853 | 61.6837 | 61.7386 | -61.8484 | -61.8301 | 61.5051 | 61.7157 | 61.6699 | 61.6928
565.4844 | 123.6649 | -61.6287 | 61.821 | 0.094845 | 0.0071275 | -0.0030927 | 0.023488 | 0.0006031 | -0.021066 | -0.0028344 | 0.17641 | 0.0087034 | 0.010143 | -0.050232 | -0.0093592 | 0.01598 | -0.0092005 | 0.018311 | 0.09613 | -0.050354 | -0.041199 | 0.041199 | -0.054932 | -0.004578 | 0.018311 | 0.1236 | -0.068665 | 0.059509 | 0.068665 | 0.082397 | 0.09613 | 61.5784 | -61.7249 | -61.8622 | 61.6699 | 61.6241 | 61.5738 | 0.045776 | -0.004578 | 61.5601 | -61.6974 | -61.7615 | 61.6974 | 61.7249 | 61.7111 | 0.16479 | 0.15106 | 0.091553 | 0.009155 | 0.13733 | 0.12817 | 0.14648 | 0.19226 | 61.7249 | 61.7523 | -61.8713 | -61.8896 | 61.5875 | 61.6882 | 61.647 | 61.647
566.4844 | 123.7381 | -61.6241 | 61.8439 | 0.064327 | 0.0071275 | -0.01057 | 0.020283 | 0.0091481 | 0.013114 | -0.0017664 | 0.19167 | 0.021521 | 0.010143 | 0.014923 | -0.021108 | 0.0074349 | -0.0081325 | 0.059509 | 0.086975 | -0.041199 | -0.10071 | -0.045776 | -0.11444 | -0.068665 | 0.13733 | 0.13275 | -0.022888 | 0.11902 | 0.16937 | 0.13275 | 0.14191 | 61.5829 | -61.7569 | -61.9446 | 61.5784 | 61.5555 | 61.5097 | -0.027466 | -0.073242 | 61.6013 | -61.7111 | -61.7249 | 61.7935 | 61.7661 | 61.7569 | 0.16479 | 0.15564 | -0.004577 | -0.059509 | 0.19226 | 0.14191 | 0.12817 | 0.15564 | 61.7111 | 61.7569 | -61.8851 | -61.8668 | 61.5234 | 61.7432 | 61.6837 | 61.7615
567.4844 | 123.6877 | -61.6013 | 61.7981 | 0.0032924 | 0.016741 | 0.0043843 | 0.032033 | -0.016487 | 0.0099088 | -0.014583 | -0.067735 | 0.021521 | 0.010143 | -0.0053713 | -0.023245 | 0.013843 | -0.014542 | 0.032043 | 0.073242 | -0.07782 | -0.11444 | -0.022888 | -0.09613 | -0.041199 | 0.086975 | 0.10529 | -0.064087 | 0.068665 | 0.11902 | 0.10986 | 0.086975 | 61.5234 | -61.7249 | -61.9125 | 61.5784 | 61.5601 | 61.5051 | 0.036621 | -0.01831 | 61.5372 | -61.6928 | -61.7294 | 61.7203 | 61.6882 | 61.7111 | 0.15106 | 0.17395 | 0.054932 | -0.036621 | 0.18311 | 0.13275 | 0.15106 | 0.16937 | 61.6745 | 61.7065 | -61.8759 | -61.8622 | 61.4868 | 61.6699 | 61.6333 | 61.6882
568.4844 | 123.6786 | -61.647 | 61.8073 | 0.14062 | 0.012469 | 0.0033163 | 0.021352 | 0.014488 | -0.0050442 | -0.0071064 | 0.14589 | 0.012976 | 0.011211 | -0.027802 | -0.018972 | 0.018116 | -0.010269 | -0.013733 | 0.082397 | -0.059509 | -0.045776 | 0.036621 | -0.050354 | -0.013733 | -0.004578 | 0.14648 | -0.07782 | 0.041199 | 0.073242 | 0.059509 | 0.091553 | 61.5875 | -61.7249 | -61.853 | 61.6837 | 61.6333 | 61.5967 | 0.045776 | 0.009155 | 61.5692 | -61.6608 | -61.7661 | 61.7203 | 61.7386 | 61.7065 | 0.16937 | 0.13733 | 0.09613 | 0.013733 | 0.15106 | 0.11902 | 0.14191 | 0.2243 | 61.7294 | 61.7935 | -61.8668 | -61.8851 | 61.6013 | 61.6882 | 61.6333 | 61.6425
569.4844 | 123.6969 | -61.615 | 61.8073 | 0.0032924 | 0.012469 | -0.016978 | 0.020283 | -0.0090099 | -0.019998 | -0.018856 | -0.098252 | 0.018316 | 0.0026664 | -0.020325 | -0.026449 | 0.012775 | -0.017746 | -0.054932 | 0.059509 | -0.064087 | -0.091553 | -0.027466 | -0.10529 | -0.041199 | 0.068665 | 0.12817 | -0.045776 | 0.091553 | 0.10071 | 0.082397 | 0.10986 | 61.5509 | -61.7477 | -61.8988 | 61.5875 | 61.5738 | 61.5097 | 0.022888 | -0.041199 | 61.5692 | -61.6791 | -61.7157 | 61.7157 | 61.7249 | 61.6974 | 0.15564 | 0.12817 | 0.036621 | -0.027466 | 0.14648 | 0.13733 | 0.1236 | 0.17395 | 61.6745 | 61.7432 | -61.8713 | -61.853 | 61.5234 | 61.7065 | 61.5601 | 61.6837
570.4844 | 123.7015 | -61.615 | 61.8256 | 0.064327 | 0.0092645 | -0.0073647 | 0.019215 | 0.0091481 | -0.014657 | 0.0057106 | 0.14589 | 0.022589 | 0.0080074 | -0.0053713 | -0.0072232 | 0.010639 | -0.014542 | 0.013733 | 0.10071 | -0.082397 | -0.10986 | 0.013733 | -0.050354 | -0.045776 | 0.054932 | 0.10071 | -0.10071 | 0.10529 | 0.13275 | 0.1236 | 0.14191 | 61.5326 | -61.7249 | -61.9354 | 61.6287 | 61.5692 | 61.5646 | 0.036621 | 0.032043 | 61.5143 | -61.7249 | -61.7203 | 61.7477 | 61.7569 | 61.7386 | 0.24262 | 0.2243 | 0.09613 | -0.027466 | 0.23346 | 0.20599 | 0.18311 | 0.20142 | 61.7157 | 61.7157 | -61.908 | -61.9263 | 61.5051 | 61.7203 | 61.6287 | 61.6699
571.4844 | 123.7198 | -61.6287 | 61.8164 | 0.064327 | 0.017809 | -0.0030927 | 0.029896 | -0.010078 | -0.033883 | -0.0071064 | -0.021958 | 0.014044 | -0.00053758 | -3.1262e-05 | -0.016836 | 0.0074349 | -0.017746 | 0.032043 | 0.059509 | -0.082397 | -0.091553 | -0.027466 | -0.086975 | -0.041199 | 0.064087 | 0.11444 | -0.059509 | 0.13275 | 0.11444 | 0.086975 | 0.13275 | 61.5463 | -61.7569 | -61.908 | 61.6013 | 61.5875 | 61.5417 | 0.041198 | -0.004578 | 61.5692 | -61.702 | -61.6837 | 61.7432 | 61.7615 | 61.7157 | 0.19226 | 0.14648 | 0.054931 | -0.009156 | 0.17395 | 0.19226 | 0.14191 | 0.17395 | 61.6882 | 61.7432 | -61.8988 | -61.8759 | 61.5372 | 61.7615 | 61.6608 | 61.6928
572.4844 | 123.7335 | -61.615 | 61.8256 | 0.094845 | 0.013537 | -0.0084327 | 0.02776 | 0.017693 | -0.0082492 | -0.018856 | -0.082994 | 0.0087034 | 0.0080074 | -0.020325 | -0.010427 | 0.020252 | -0.018814 | 0.041199 | 0.07782 | -0.073242 | -0.10529 | -0.018311 | -0.10529 | -0.059509 | 0.082397 | 0.1236 | -0.073242 | 0.11902 | 0.13275 | 0.10071 | 0.12817 | 61.5417 | -61.7477 | -61.9308 | 61.5967 | 61.5555 | 61.5097 | 0.013733 | -0.032044 | 61.5417 | -61.702 | -61.7065 | 61.7477 | 61.7432 | 61.7157 | 0.20142 | 0.17395 | 0.054931 | -0.032044 | 0.20599 | 0.19226 | 0.15106 | 0.19684 | 61.6928 | 61.7386 | -61.8988 | -61.8988 | 61.5097 | 61.734 | 61.6562 | 61.6974
573.4844 | 123.7381 | -61.615 | 61.821 | -0.042484 | 0.010333 | -0.0095007 | 0.035237 | 0.01342 | -0.0061122 | -0.011379 | -0.082994 | 0.014044 | -0.013356 | 0.0053097 | -0.013631 | 0.01598 | -0.0017235 | 0.045776 | 0.073242 | -0.07782 | -0.09613 | -0.009155 | -0.10071 | -0.050354 | 0.07782 | 0.10986 | -0.054932 | 0.11444 | 0.12817 | 0.09613 | 0.1236 | 61.5372 | -61.7477 | -61.9171 | 61.6058 | 61.5646 | 61.5143 | 0.027466 | -0.022888 | 61.5601 | -61.7111 | -61.7065 | 61.7432 | 61.7386 | 61.7111 | 0.17853 | 0.15106 | 0.068665 | -0.01831 | 0.18311 | 0.16937 | 0.15106 | 0.16479 | 61.6882 | 61.7249 | -61.8988 | -61.8759 | 61.5189 | 61.7294 | 61.6608 | 61.6928
574.4844 | 123.7335 | -61.6241 | 61.7981 | 0.094845 | 0.0039235 | -0.01057 | 0.028828 | 0.011284 | -0.015725 | -0.0017664 | -0.067735 | 0.018316 | -0.0026746 | -0.0096443 | -0.023245 | 0.023456 | 0.0025485 | 0.027466 | 0.07782 | -0.09613 | -0.059509 | 0.013733 | -0.10529 | -0.050354 | 0.07782 | 0.10071 | -0.045776 | 0.10529 | 0.11902 | 0.082397 | 0.13275 | 61.528 | -61.7203 | -61.8576 | 61.6379 | 61.5738 | 61.5189 | 0.045776 | -0.009156 | 61.5784 | -61.6974 | -61.6928 | 61.7432 | 61.7569 | 61.7065 | 0.17853 | 0.12817 | 0.10986 | 0.036621 | 0.16479 | 0.15106 | 0.17395 | 0.14648 | 61.702 | 61.7249 | -61.8942 | -61.8439 | 61.5646 | 61.7294 | 61.6516 | 61.702
575.4844 | 123.6649 | -61.6516 | 61.8301 | -0.011967 | 0.0039235 | 0.00011227 | 0.018147 | 0.01342 | -0.034951 | -0.011379 | 0.13063 | 0.018316 | -0.0037426 | -0.0010993 | -0.012563 | 0.020252 | 0.010025 | 0.018311 | 0.082397 | -0.054932 | -0.036621 | 0.036621 | -0.036621 | -0.004578 | 0.009155 | 0.13275 | -0.073242 | 0.050354 | 0.07782 | 0.059509 | 0.086975 | 61.5967 | -61.7477 | -61.8668 | 61.6882 | 61.647 | 61.615 | 0.050354 | 0.018311 | 61.5784 | -61.6974 | -61.7798 | 61.7294 | 61.7386 | 61.7111 | 0.16022 | 0.13275 | 0.091553 | 0.018311 | 0.15106 | 0.1236 | 0.13733 | 0.20599 | 61.734 | 61.7844 | -61.8851 | -61.9034 | 61.615 | 61.702 | 61.6699 | 61.6608
576.4844 | 123.7381 | -61.6058 | 61.8027 | 0.049069 | 0.014605 | -0.0030927 | 0.019215 | 0.0038071 | -0.010385 | -0.032741 | -0.067735 | 0.015112 | -0.0058786 | -0.0021673 | -0.017904 | 0.023456 | -0.018814 | 0.045776 | 0.073242 | -0.091553 | -0.11444 | -0.013733 | -0.09613 | -0.059509 | 0.082397 | 0.11444 | -0.064087 | 0.11902 | 0.13275 | 0.091553 | 0.15106 | 61.5143 | -61.7294 | -61.9171 | 61.5921 | 61.5463 | 61.5097 | 0.032044 | -0.004577 | 61.5417 | -61.6882 | -61.6837 | 61.7386 | 61.7569 | 61.6974 | 0.21515 | 0.15564 | 0.07782 | -0.022888 | 0.19684 | 0.18311 | 0.16479 | 0.17853 | 61.6791 | 61.7203 | -61.8942 | -61.8668 | 61.4914 | 61.7249 | 61.6516 | 61.6882
577.4844 | 123.6603 | -61.6653 | 61.8393 | 0.12536 | 0.0092645 | -0.0095007 | 0.025624 | 0.014488 | 0.00029581 | -0.0092424 | -0.098252 | 0.021521 | 0.0058704 | -0.01178 | -0.017904 | 0.025593 | -0.0027915 | 0.009155 | 0.10529 | -0.09613 | 0.022888 | 0.10986 | 0.009155 | 0.036621 | -0.032043 | 0.14648 | -0.10071 | 0.041199 | 0.032043 | 0.009155 | 0.054932 | 61.5692 | -61.734 | -61.8164 | 61.7752 | 61.702 | 61.6745 | 0.13275 | 0.10528 | 61.5646 | -61.6928 | -61.7981 | 61.6974 | 61.7203 | 61.6745 | 0.15564 | 0.10986 | 0.20599 | 0.11902 | 0.13275 | 0.14191 | 0.20142 | 0.24719 | 61.7706 | 61.8118 | -61.9354 | -61.94 | 61.6882 | 61.7065 | 61.6745 | 61.6333
578.4844 | 123.6374 | -61.6608 | 61.8301 | 0.12536 | 0.0039235 | -0.0030927 | 0.025624 | 0.018761 | -0.016794 | -0.0028344 | 0.10011 | 0.020452 | -0.0080146 | -0.0096443 | -0.0061552 | 0.020252 | -0.010269 | -0.041199 | 0.11444 | -0.1236 | 0.022888 | 0.013733 | 0.050354 | 0.086975 | -0.086975 | 0.16022 | -0.064087 | 0.009155 | 0 | -0.004578 | 0.045776 | 61.5372 | -61.7157 | -61.8073 | 61.6745 | 61.7477 | 61.7111 | 0.21057 | 0.17395 | 61.5967 | -61.6699 | -61.821 | 61.6608 | 61.7065 | 61.6562 | 0.10986 | 0.059509 | 0.13733 | 0.14648 | 0.064087 | 0.073242 | 0.23804 | 0.2243 | 61.7752 | 61.821 | -61.9537 | -61.8942 | 61.6837 | 61.6699 | 61.6196 | 61.5738
579.4844 | 123.7015 | -61.6516 | 61.8439 | 0.018551 | 0.0060595 | -0.0062967 | 0.02242 | -0.0015339 | -0.010385 | -0.013515 | -0.11351 | 0.011908 | -0.00053758 | -0.0064393 | -0.02004 | 0.024524 | -0.0017235 | -0.050354 | 0.10986 | -0.10529 | 0 | 0.07782 | -0.009155 | 0.013733 | -0.018311 | 0.13275 | -0.091553 | 0.059509 | 0.059509 | 0.054932 | 0.086975 | 61.5463 | -61.734 | -61.8439 | 61.7294 | 61.6653 | 61.6425 | 0.11902 | 0.096131 | 61.5601 | -61.7111 | -61.7844 | 61.7111 | 61.7386 | 61.7065 | 0.17853 | 0.14649 | 0.18311 | 0.10529 | 0.15106 | 0.15106 | 0.21515 | 0.2243 | 61.7615 | 61.7844 | -61.9492 | -61.9354 | 61.6516 | 61.7111 | 61.6013 | 61.6333
580.4844 | 123.6877 | -61.6379 | 61.8118 | 0.12536 | 0.0081955 | 0.0022483 | 0.024556 | 0.012352 | -0.013589 | -0.015651 | 0.28322 | 0.021521 | 0.0058704 | -0.0043033 | -0.012563 | 0.0074349 | -0.011337 | -0.018311 | 0.10529 | -0.045776 | -0.041199 | 0.059509 | -0.054932 | -0.009155 | 0 | 0.13275 | -0.064087 | 0.068665 | 0.07782 | 0.068665 | 0.073242 | 61.5921 | -61.7065 | -61.853 | 61.6974 | 61.6287 | 61.5829 | 0.036621 | -0.009156 | 61.5738 | -61.6791 | -61.7432 | 61.7157 | 61.7111 | 61.7065 | 0.13733 | 0.13275 | 0.10528 | 0.004577 | 0.14191 | 0.13275 | 0.15106 | 0.19684 | 61.7432 | 61.7706 | -61.8576 | -61.8759 | 61.5967 | 61.7065 | 61.6196 | 61.6379
581.4844 | 123.642 | -61.6882 | 61.8439 | 0.03381 | 0.013537 | 0.0043843 | 0.041646 | -0.010078 | -0.0061122 | -0.0039024 | 0.19167 | 0.020452 | 0.015483 | -0.016052 | -0.02004 | 0.024524 | 0.015366 | -0.041199 | 0.10529 | -0.11902 | 0.045776 | 0.14191 | 0.1236 | 0.059509 | -0.11902 | 0.16022 | -0.086975 | -0.009155 | -0.013733 | -0.009155 | 0.041199 | 61.5692 | -61.7386 | -61.7981 | 61.8301 | 61.7477 | 61.8118 | 0.17853 | 0.24261 | 61.6013 | -61.6837 | -61.853 | 61.6745 | 61.7294 | 61.6791 | 0.12817 | 0.07782 | 0.26093 | 0.16479 | 0.073242 | 0.07782 | 0.22431 | 0.24719 | 61.7935 | 61.8484 | -61.9629 | -61.9308 | 61.734 | 61.6791 | 61.647 | 61.5692
582.6406 | 123.6832 | -61.647 | 61.8713 | 0.14062 | 0.018878 | -0.0030927 | 0.028828 | 0.0091481 | -0.027475 | -0.011379 | -0.12877 | 0.021521 | 0.015483 | -0.0085763 | -0.0093592 | 0.022388 | -0.0092005 | 0.022888 | 0.11902 | -0.10986 | -0.009155 | 0.073242 | -0.027466 | 0.050354 | 0.013733 | 0.16937 | -0.082397 | 0.11444 | 0.064087 | 0.013733 | 0.07782 | 61.5372 | -61.7523 | -61.8805 | 61.7203 | 61.6974 | 61.6196 | 0.16022 | 0.082397 | 61.5646 | -61.702 | -61.7569 | 61.7111 | 61.7249 | 61.6608 | 0.16022 | 0.09613 | 0.18311 | 0.10071 | 0.14648 | 0.19684 | 0.22888 | 0.25177 | 61.7661 | 61.8164 | -61.9812 | -61.9537 | 61.6379 | 61.7615 | 61.6699 | 61.6608
583.4844 | 123.6465 | -61.6562 | 61.8759 | 0.12536 | 0.02315 | -0.0095007 | 0.026692 | -0.0058059 | 0.00029581 | -0.026332 | 0.16115 | 0.025793 | -0.0069466 | 0.0074457 | -0.0029502 | 0.01598 | -0.01561 | 0.027466 | 0.10071 | -0.064087 | -0.013733 | 0.059509 | -0.032043 | 0.022888 | 0.009155 | 0.16937 | -0.059509 | -0.009155 | 0.07782 | 0.073242 | 0.045776 | 61.5921 | -61.7752 | -61.8896 | 61.7157 | 61.6791 | 61.6241 | 0.086975 | 0.032044 | 61.5967 | -61.7065 | -61.8851 | 61.734 | 61.702 | 61.7294 | 0.10528 | 0.13275 | 0.1236 | 0.050354 | 0.13733 | 0.050354 | 0.1648 | 0.22888 | 61.7569 | 61.8256 | -61.94 | -61.9354 | 61.6425 | 61.647 | 61.6837 | 61.6653
584.4844 | 123.6557 | -61.6791 | 61.8622 | 0.14062 | 0.014605 | 0.00011227 | 0.024556 | 0.0091481 | 0.022727 | -0.014583 | -0.052476 | 0.022589 | -0.00053758 | -0.0032353 | -0.012563 | 0.013843 | -0.02095 | -0.045776 | 0.10986 | -0.09613 | 0.086975 | 0.27008 | 0.027466 | -0.009155 | 0 | 0.17395 | -0.073242 | 0 | 0 | -0.027466 | 0.045776 | 61.5829 | -61.7523 | -61.7752 | 61.9492 | 61.6699 | 61.7065 | 0.086975 | 0.1236 | 61.6058 | -61.6882 | -61.8622 | 61.6791 | 61.7249 | 61.6516 | 0.11902 | 0.045776 | 0.36621 | 0.1831 | 0.073242 | 0.073242 | 0.20599 | 0.24719 | 61.7889 | 61.853 | -61.9583 | -61.9354 | 61.7661 | 61.6791 | 61.6333 | 61.6791
585.4844 | 123.7061 | -61.6379 | 61.853 | 0.079586 | 0.011401 | 0.00011227 | 0.023488 | 0.0006031 | 0.0013638 | 0.00037059 | 0.20692 | 0.024725 | 0.0058704 | -0.024597 | -0.017904 | 0.0095709 | -0.025223 | 0 | 0.086975 | -0.068665 | -0.041199 | 0.064087 | -0.050354 | 0.009155 | -0.004578 | 0.12817 | -0.064087 | 0.054932 | 0.073242 | 0.064087 | 0.082397 | 61.5692 | -61.7661 | -61.8942 | 61.702 | 61.647 | 61.5875 | 0.07782 | 0.018311 | 61.5738 | -61.7249 | -61.7981 | 61.7111 | 61.7203 | 61.702 | 0.14648 | 0.12817 | 0.13275 | 0.027466 | 0.13733 | 0.11902 | 0.15564 | 0.19226 | 61.7249 | 61.7661 | -61.9217 | -61.9171 | 61.5967 | 61.6928 | 61.6379 | 61.6333
586.4844 | 123.642 | -61.6699 | 61.8393 | 0.094845 | 0.011401 | -0.0084327 | 0.020283 | -0.0090099 | -0.017862 | -0.013515 | -0.052476 | 0.019384 | -0.0058786 | -0.033142 | -0.022176 | 0.0085029 | -0.018814 | -0.036621 | 0.11444 | -0.10529 | 0.050354 | 0.14648 | 0.041199 | 0.064087 | -0.091553 | 0.15106 | -0.11444 | -0.013733 | -0.022888 | -0.045776 | 0.022888 | 61.5646 | -61.7249 | -61.7889 | 61.8164 | 61.734 | 61.7111 | 0.16937 | 0.14649 | 61.5555 | -61.6882 | -61.853 | 61.647 | 61.6928 | 61.6241 | 0.13733 | 0.068665 | 0.25177 | 0.15564 | 0.091553 | 0.10071 | 0.21973 | 0.2655 | 61.7844 | 61.821 | -61.9446 | -61.9537 | 61.7203 | 61.6562 | 61.6333 | 61.5784
587.4844 | 123.6099 | -61.6791 | 61.8484 | 0.018551 | 0.022082 | 0.0097253 | 0.032033 | -0.0079419 | -0.0061122 | -0.0017664 | -0.12877 | 0.020452 | -0.0037426 | -0.013916 | -0.011495 | 0.02132 | 0.00041246 | -0.068665 | 0.10529 | -0.12817 | 0.068665 | 0.17395 | 0.045776 | 0.068665 | -0.091553 | 0.15564 | -0.10529 | -0.013733 | -0.018311 | -0.050354 | 0.018311 | 61.5509 | -61.7432 | -61.7798 | 61.853 | 61.7477 | 61.7249 | 0.19684 | 0.17395 | 61.5738 | -61.6928 | -61.8622 | 61.6608 | 61.6974 | 61.6287 | 0.1236 | 0.054932 | 0.30212 | 0.19684 | 0.086975 | 0.091553 | 0.23346 | 0.26093 | 61.7844 | 61.8347 | -61.9766 | -61.9537 | 61.7477 | 61.6653 | 61.6104 | 61.5875
588.4844 | 123.6603 | -61.6791 | 61.8439 | 0.094845 | 0.014605 | -0.013774 | 0.02776 | 0.0048751 | -0.0061122 | -0.0049704 | 0.0085594 | 0.018316 | 0.018688 | -0.0075083 | -0.021108 | 0.017048 | -0.0070645 | -0.036621 | 0.10071 | -0.11902 | 0.050354 | 0.14648 | 0.036621 | 0.073242 | -0.07782 | 0.14191 | -0.11444 | -0.041199 | 0.068665 | -0.018311 | 0.004578 | 61.5601 | -61.7432 | -61.7935 | 61.8256 | 61.7523 | 61.7157 | 0.19226 | 0.15564 | 61.5646 | -61.702 | -61.8851 | 61.7477 | 61.6837 | 61.6608 | 0.11902 | 0.09613 | 0.2655 | 0.16937 | 0.18311 | 0.073242 | 0.21973 | 0.25635 | 61.7798 | 61.821 | -61.9629 | -61.9583 | 61.7294 | 61.6379 | 61.6425 | 61.6013
589.4844 | 123.6511 | -61.6928 | 61.8301 | 0.12536 | 0.0049915 | 0.00011227 | 0.026692 | 0.0070111 | 0.016318 | -0.0092424 | -0.15929 | 0.023657 | -0.00053758 | 0.0021047 | -0.0147 | 0.01598 | -0.014542 | -0.032043 | 0.10529 | -0.11902 | 0.054932 | 0.14191 | 0.050354 | 0.064087 | -0.082397 | 0.14648 | -0.10071 | -0.018311 | -0.022888 | -0.041199 | 0.027466 | 61.5738 | -61.7249 | -61.7752 | 61.8347 | 61.7569 | 61.7432 | 0.18311 | 0.16937 | 61.5921 | -61.6837 | -61.8484 | 61.6699 | 61.7203 | 61.6516 | 0.12817 | 0.059509 | 0.26093 | 0.17395 | 0.07782 | 0.082397 | 0.22431 | 0.24719 | 61.7981 | 61.8393 | -61.9492 | -61.9308 | 61.7477 | 61.6745 | 61.6608 | 61.6104
590.4844 | 123.761 | -61.6516 | 61.7935 | 0.094845 | 0.016741 | 0.0033163 | 0.02776 | 0.010216 | 0.010977 | -0.018856 | 0.16115 | 0.020452 | -0.0069466 | -0.0064393 | -0.022176 | 0.017048 | -0.022018 | 0.041199 | 0.064087 | -0.07782 | -0.10529 | -0.018311 | -0.10986 | -0.045776 | 0.10071 | 0.1236 | -0.064087 | 0.09613 | 0.12817 | 0.10986 | 0.1236 | 61.5738 | -61.7294 | -61.8988 | 61.6333 | 61.6058 | 61.5417 | 0.032044 | -0.032043 | 61.5875 | -61.6699 | -61.6974 | 61.7798 | 61.7752 | 61.7615 | 0.18768 | 0.17395 | 0.059509 | -0.027466 | 0.19226 | 0.16022 | 0.14191 | 0.18768 | 61.7157 | 61.7752 | -61.8713 | -61.8576 | 61.5463 | 61.7477 | 61.6928 | 61.7523
591.4844 | 123.642 | -61.6745 | 61.8896 | 0.12536 | 0.010333 | -0.0020247 | 0.024556 | 0.0038071 | -0.0082492 | -0.013515 | -0.021958 | 0.010839 | 0.00053042 | -0.02887 | -0.0147 | 0.023456 | -0.0027915 | -0.018311 | 0.10986 | -0.073242 | 0.022888 | 0.091553 | 0.004578 | 0.045776 | -0.054932 | 0.15106 | -0.09613 | -0.027466 | -0.004578 | -0.054932 | 0.013733 | 61.6013 | -61.7798 | -61.8668 | 61.7661 | 61.7203 | 61.6791 | 0.11902 | 0.07782 | 61.5784 | -61.7386 | -61.9171 | 61.6699 | 61.6882 | 61.6196 | 0.10986 | 0.041198 | 0.16479 | 0.09613 | 0.091552 | 0.068664 | 0.18311 | 0.24719 | 61.7844 | 61.8256 | -61.9629 | -61.9858 | 61.6974 | 61.647 | 61.6562 | 61.6196
592.4844 | 123.642 | -61.6608 | 61.8759 | 0.17114 | 0.012469 | -0.00095673 | 0.024556 | 0.011284 | -0.0018402 | -0.010311 | -0.021958 | 0.017248 | 0.0037344 | -0.018189 | -0.0029502 | 0.013843 | 0.0057535 | -0.009155 | 0.16022 | -0.036621 | 0.004578 | 0.086975 | -0.018311 | 0.045776 | -0.027466 | 0.15106 | -0.082397 | -0.018311 | 0 | -0.022888 | 0.032043 | 61.6241 | -61.7157 | -61.8713 | 61.7477 | 61.7065 | 61.6425 | 0.082397 | 0.01831 | 61.5784 | -61.7249 | -61.8942 | 61.6608 | 61.6928 | 61.6379 | 0.11444 | 0.059509 | 0.1236 | 0.041199 | 0.082397 | 0.064086 | 0.19684 | 0.23346 | 61.821 | 61.8118 | -61.9125 | -61.9583 | 61.6653 | 61.6425 | 61.6516 | 61.6333
593.4844 | 123.6099 | -61.6974 | 61.8988 | 0.018551 | 0.0081955 | -0.00095673 | 0.019215 | 0.012352 | -0.011453 | -0.0039024 | 0.054336 | 0.021521 | 0.0090754 | -0.032074 | -0.00081422 | 0.025593 | -0.00065554 | -0.027466 | 0.086975 | -0.11444 | 0.027466 | 0.11444 | 0.004578 | 0.054932 | -0.091553 | 0.12817 | -0.12817 | -0.032043 | 0.004578 | -0.068665 | -0.004578 | 61.5829 | -61.8118 | -61.8713 | 61.8118 | 61.7523 | 61.702 | 0.16937 | 0.11902 | 61.5692 | -61.7706 | -61.9308 | 61.702 | 61.6928 | 61.6287 | 0.1236 | 0.059509 | 0.22888 | 0.14191 | 0.13275 | 0.096131 | 0.20142 | 0.25635 | 61.7844 | 61.8256 | -62.0132 | -62.027 | 61.7249 | 61.6653 | 61.6699 | 61.6058
594.4844 | 123.642 | -61.6745 | 61.8668 | 0.14062 | 0.012469 | -0.0041607 | 0.030965 | -0.0026019 | -0.022134 | -0.024196 | 0.0085594 | 0.017248 | -0.0037426 | 0.0042417 | -0.025381 | 0.026661 | 0.013229 | -0.022888 | 0.10071 | -0.1236 | 0.009155 | 0.09613 | -0.004578 | 0.045776 | -0.059509 | 0.13733 | -0.10986 | -0.018311 | -0.013733 | -0.045776 | 0.018311 | 61.5509 | -61.7661 | -61.8576 | 61.7706 | 61.7203 | 61.6699 | 0.16937 | 0.11902 | 61.5646 | -61.7294 | -61.8851 | 61.6608 | 61.6928 | 61.6287 | 0.12817 | 0.064087 | 0.21973 | 0.13275 | 0.09613 | 0.091552 | 0.2243 | 0.24719 | 61.7752 | 61.8118 | -61.9904 | -61.9766 | 61.6837 | 61.6562 | 61.6516 | 61.615
595.4844 | 123.761 | -61.6241 | 61.8347 | 0.03381 | 0.014605 | 0.0075883 | 0.029896 | -0.0036699 | 0.0099088 | 0.0035746 | 0.20692 | 0.025793 | 0.011211 | -0.014984 | -0.017904 | 0.01598 | -0.0017235 | 0.022888 | 0.054932 | -0.064087 | -0.10986 | -0.018311 | -0.086975 | -0.041199 | 0.07782 | 0.10529 | -0.045776 | 0.07782 | 0.11444 | 0.082397 | 0.11902 | 61.5601 | -61.7798 | -61.9446 | 61.6058 | 61.5829 | 61.5372 | 0.022888 | -0.022888 | 61.5784 | -61.7294 | -61.7569 | 61.7386 | 61.7432 | 61.7065 | 0.16479 | 0.12817 | 0.045776 | -0.045776 | 0.16022 | 0.1236 | 0.11902 | 0.15106 | 61.6791 | 61.7294 | -61.8988 | -61.8805 | 61.5143 | 61.702 | 61.647 | 61.702
596.4844 | 123.6191 | -61.6745 | 61.8988 | 0.064327 | 0.019946 | -0.0041607 | 0.029896 | 0.0091481 | -0.0093172 | -0.011379 | -0.082994 | 0.025793 | -0.0016066 | -0.0032353 | -0.016836 | 0.025593 | -0.0027915 | -0.013733 | 0.10986 | -0.10986 | 0.050354 | 0.13275 | 0.032043 | 0.07782 | -0.082397 | 0.15564 | -0.10071 | -0.032043 | -0.041199 | -0.059509 | -0.018311 | 61.5646 | -61.7889 | -61.8484 | 61.8073 | 61.7523 | 61.7065 | 0.18768 | 0.14191 | 61.5738 | -61.7432 | -61.9308 | 61.6333 | 61.6562 | 61.615 | 0.082397 | 0.041199 | 0.24261 | 0.16022 | 0.059509 | 0.068665 | 0.21973 | 0.25635 | 61.7844 | 61.8301 | -62.0087 | -61.9995 | 61.7249 | 61.6425 | 61.6608 | 61.5921
597.4844 | 123.6374 | -61.6928 | 61.8896 | 0.03381 | 0.018878 | 0.0022483 | 0.02776 | -0.0026019 | -0.0039762 | -0.017787 | -0.0066996 | 0.012976 | 0.0090754 | -0.055573 | -0.011495 | 0.024524 | -0.014542 | -0.013733 | 0.086975 | -0.10071 | 0.032043 | 0.11902 | 0.018311 | 0.068665 | -0.041199 | 0.16937 | -0.086975 | -0.009155 | -0.009155 | -0.032043 | 0.018311 | 61.5921 | -61.8027 | -61.8576 | 61.8118 | 61.7615 | 61.7111 | 0.16937 | 0.11902 | 61.6058 | -61.7203 | -61.8988 | 61.6837 | 61.7111 | 61.6608 | 0.10529 | 0.054932 | 0.21973 | 0.13275 | 0.07782 | 0.07782 | 0.18768 | 0.25635 | 61.7798 | 61.8622 | -61.9904 | -61.9766 | 61.7249 | 61.6837 | 61.6791 | 61.6516
598.4844 | 123.6694 | -61.6653 | 61.8805 | 0.079586 | 0.0039235 | -0.0095007 | 0.02242 | 0.0038071 | -0.011453 | -0.010311 | 0.039077 | 0.0054994 | 0.030437 | 0.040558 | -0.024313 | 0.018116 | -0.0070645 | 0.018311 | 0.10529 | -0.082397 | -0.013733 | 0.068665 | -0.013733 | 0.032043 | 0.009155 | 0.16479 | -0.059509 | 0.032043 | 0.064087 | 0.036621 | 0.073242 | 61.5829 | -61.7752 | -61.8942 | 61.734 | 61.6974 | 61.6516 | 0.11444 | 0.068664 | 61.6058 | -61.7157 | -61.8484 | 61.7294 | 61.7386 | 61.702 | 0.13275 | 0.09613 | 0.15106 | 0.068664 | 0.1236 | 0.091552 | 0.18768 | 0.2243 | 61.7706 | 61.8301 | -61.9629 | -61.94 | 61.6516 | 61.6974 | 61.6837 | 61.6745
599.4844 | 123.6969 | -61.6608 | 61.8805 | 0.094845 | 0.010333 | 0.0022483 | 0.030965 | 0.0038071 | -0.021066 | 0.0014386 | 0.069594 | 0.023657 | 0.010143 | -0.010712 | -0.025381 | 0.014911 | 0.0068215 | 0.004578 | 0.086975 | -0.09613 | -0.004578 | 0.064087 | -0.018311 | 0.032043 | 0.022888 | 0.15564 | -0.059509 | 0.041199 | 0.073242 | 0.032043 | 0.073242 | 61.5646 | -61.7935 | -61.8851 | 61.7249 | 61.6928 | 61.6425 | 0.12817 | 0.077819 | 61.6013 | -61.7249 | -61.8393 | 61.734 | 61.734 | 61.6928 | 0.13275 | 0.091552 | 0.16022 | 0.091552 | 0.13275 | 0.10071 | 0.1831 | 0.21515 | 61.7477 | 61.8164 | -61.9766 | -61.94 | 61.6562 | 61.702 | 61.6653 | 61.6837
600.4844 | 123.7564 | -61.6562 | 61.8622 | 0.03381 | 0.014605 | -0.00095673 | 0.017079 | 0.023033 | -0.013589 | -0.011379 | 0.34425 | 0.011908 | 0.014415 | -0.023529 | -0.012563 | 0.020252 | 0.0089575 | 0.027466 | 0.073242 | -0.068665 | -0.10071 | -0.027466 | -0.10529 | -0.036621 | 0.091553 | 0.11902 | -0.045776 | 0.07782 | 0.14191 | 0.1236 | 0.11902 | 61.5875 | -61.7889 | -61.9629 | 61.6287 | 61.6196 | 61.5509 | 0.032044 | -0.036621 | 61.6104 | -61.7432 | -61.7844 | 61.7981 | 61.7752 | 61.7798 | 0.16479 | 0.16937 | 0.041199 | -0.032043 | 0.18768 | 0.1236 | 0.14191 | 0.16479 | 61.7294 | 61.7752 | -61.9308 | -61.908 | 61.5555 | 61.734 | 61.6837 | 61.7477
601.4844 | 123.6786 | -61.6379 | 61.8805 | 0.094845 | 0.0049915 | -0.0052287 | 0.029896 | 0.012352 | 0.0045688 | -0.010311 | 0.023818 | 0.014044 | 0.013347 | -0.01178 | -0.028585 | 0.018116 | 0.0046845 | 0.009155 | 0.10529 | -0.10986 | 0 | 0.054932 | -0.027466 | 0.036621 | 0.013733 | 0.15564 | -0.059509 | 0.027466 | 0.054932 | 0.022888 | 0.064087 | 61.528 | -61.7752 | -61.8805 | 61.6928 | 61.6745 | 61.6104 | 0.14648 | 0.082397 | 61.5784 | -61.7249 | -61.853 | 61.6928 | 61.702 | 61.6608 | 0.1236 | 0.082397 | 0.16479 | 0.10986 | 0.11444 | 0.086975 | 0.21515 | 0.21515 | 61.7432 | 61.7935 | -61.9904 | -61.94 | 61.6379 | 61.6653 | 61.647 | 61.6516
602.4844 | 123.6786 | -61.6699 | 61.8851 | 0.064327 | 0.010333 | -0.0030927 | 0.017079 | -0.0026019 | -0.0039762 | -0.020992 | 0.0085594 | 0.026861 | 0.0048024 | -0.013916 | -0.018972 | 0.02132 | -0.0017235 | -0.004578 | 0.091553 | -0.07782 | 0.009155 | 0.073242 | 0.009155 | 0.064087 | -0.022888 | 0.17395 | -0.07782 | 0.009155 | 0.018311 | -0.009155 | 0.041199 | 61.5921 | -61.7935 | -61.8759 | 61.7432 | 61.734 | 61.6791 | 0.14191 | 0.086975 | 61.5921 | -61.7111 | -61.8759 | 61.6882 | 61.7111 | 61.6608 | 0.11902 | 0.068665 | 0.15106 | 0.086975 | 0.096131 | 0.086975 | 0.16937 | 0.25177 | 61.7615 | 61.8439 | -61.9629 | -61.9629 | 61.6791 | 61.6791 | 61.6653 | 61.647
603.4844 | 123.6557 | -61.6791 | 61.8805 | 0.079586 | 0.013537 | -0.0020247 | 0.028828 | 0.014488 | 0.012046 | -0.017787 | 0.084853 | 0.018316 | 0.014415 | -0.0010993 | -0.0147 | 0.018116 | -0.0092005 | 0 | 0.091553 | -0.091553 | -0.004578 | 0.07782 | 0 | 0.059509 | 0.004578 | 0.15564 | -0.086975 | 0.018311 | 0.027466 | -0.004578 | 0.036621 | 61.5875 | -61.7889 | -61.8851 | 61.7569 | 61.7386 | 61.6791 | 0.15106 | 0.091553 | 61.5921 | -61.7249 | -61.8622 | 61.7065 | 61.7157 | 61.6745 | 0.1236 | 0.082397 | 0.16937 | 0.086975 | 0.11444 | 0.10529 | 0.18311 | 0.24261 | 61.7706 | 61.8347 | -61.972 | -61.9675 | 61.6745 | 61.6974 | 61.6791 | 61.6837
604.4844 | 123.6694 | -61.6699 | 61.8713 | 0.1101 | 0.011401 | 0.0011803 | 0.013875 | 0.0016711 | -0.017862 | -0.00069841 | 0.084853 | 0.031134 | 0.00053042 | -0.04596 | -0.0147 | 0.020252 | -0.01561 | 0.004578 | 0.10071 | -0.10071 | -0.013733 | 0.064087 | -0.009155 | 0.041199 | 0.004578 | 0.15106 | -0.073242 | 0.027466 | 0.050354 | 0.018311 | 0.064087 | 61.5692 | -61.7706 | -61.8851 | 61.734 | 61.7111 | 61.6608 | 0.14191 | 0.091553 | 61.5967 | -61.7203 | -61.8439 | 61.7203 | 61.734 | 61.6882 | 0.13733 | 0.091553 | 0.1648 | 0.086975 | 0.1236 | 0.10071 | 0.20142 | 0.2243 | 61.7706 | 61.821 | -61.972 | -61.9446 | 61.6562 | 61.6974 | 61.6745 | 61.6745
605.4844 | 123.6145 | -61.7111 | 61.8805 | 0.049069 | 0.011401 | -0.0020247 | 0.011738 | 0.017693 | 0.00029581 | 0.0014386 | 0.11537 | 0.0054994 | 0.015483 | -0.0075083 | -0.011495 | 0.018116 | -0.00065554 | -0.032043 | 0.10071 | -0.09613 | 0.068665 | 0.17395 | 0.059509 | 0.091553 | -0.11444 | 0.15564 | -0.09613 | -0.027466 | -0.032043 | -0.050354 | 0.036621 | 61.615 | -61.7798 | -61.8118 | 61.8851 | 61.8027 | 61.7706 | 0.18768 | 0.15564 | 61.615 | -61.7249 | -61.908 | 61.6791 | 61.7477 | 61.6608 | 0.13275 | 0.045776 | 0.27008 | 0.16479 | 0.064087 | 0.068664 | 0.19684 | 0.25177 | 61.8118 | 61.8668 | -61.9766 | -61.9766 | 61.7798 | 61.6837 | 61.6791 | 61.5967
606.4844 | 123.7106 | -61.6608 | 61.8759 | 0.094845 | 0.0028555 | 0.0011803 | 0.020283 | -0.0015339 | 0.0035008 | -0.014583 | 0.13063 | 0.018316 | 0.0090754 | -0.014984 | -0.0082912 | 0.018116 | -0.0081325 | 0.013733 | 0.10071 | -0.10071 | 0 | 0.064087 | -0.027466 | 0.036621 | 0.009155 | 0.15106 | -0.07782 | 0.027466 | 0.068665 | 0.027466 | 0.054932 | 61.5601 | -61.7752 | -61.8759 | 61.7249 | 61.6974 | 61.6333 | 0.13733 | 0.073242 | 61.5829 | -61.7249 | -61.8484 | 61.7294 | 61.7157 | 61.6882 | 0.13275 | 0.10529 | 0.1648 | 0.10071 | 0.14649 | 0.10529 | 0.20142 | 0.22888 | 61.7615 | 61.8118 | -61.9766 | -61.9537 | 61.6608 | 61.6882 | 61.6745 | 61.6699
607.4844 | 123.6832 | -61.6745 | 61.9034 | 0.079586 | 0.0049915 | -0.0052287 | 0.020283 | -0.012215 | -0.011453 | -0.030605 | 0.039077 | 0.021521 | 0.01762 | -0.019257 | -0.018972 | 0.020252 | -0.0017235 | 0.018311 | 0.091553 | -0.10071 | 0 | 0.059509 | -0.013733 | 0.027466 | 0.027466 | 0.14648 | -0.059509 | 0.036621 | 0.059509 | 0.036621 | 0.073242 | 61.5738 | -61.8118 | -61.9034 | 61.734 | 61.702 | 61.6608 | 0.12817 | 0.086975 | 61.615 | -61.7569 | -61.8668 | 61.734 | 61.7477 | 61.7111 | 0.13275 | 0.09613 | 0.16022 | 0.10071 | 0.11902 | 0.09613 | 0.19226 | 0.20599 | 61.7661 | 61.821 | -62.0041 | -61.9629 | 61.6745 | 61.7111 | 61.6928 | 61.702
608.4844 | 123.7152 | -61.6699 | 61.8805 | 0.17114 | 0.022082 | -0.0030927 | 0.028828 | 0.010216 | 0.0024328 | 0.0078466 | 0.16115 | 0.020452 | 0.014415 | -0.042755 | -0.018972 | 0.02132 | -0.0092005 | -0.004578 | 0.10529 | -0.091553 | -0.004578 | 0.059509 | -0.018311 | 0.032043 | 0.018311 | 0.14648 | -0.064087 | 0.027466 | 0.068665 | 0.036621 | 0.073242 | 61.5784 | -61.7752 | -61.8851 | 61.7294 | 61.702 | 61.6516 | 0.1236 | 0.073242 | 61.6058 | -61.734 | -61.853 | 61.7386 | 61.7432 | 61.7065 | 0.13733 | 0.10071 | 0.15106 | 0.086975 | 0.13275 | 0.091553 | 0.19684 | 0.21057 | 61.7752 | 61.8164 | -61.972 | -61.9446 | 61.6653 | 61.6974 | 61.6653 | 61.6882
609.4844 | 123.6877 | -61.6653 | 61.8942 | 0.018551 | 0.021014 | -0.0073647 | 0.026692 | 0.01342 | 0.0056368 | -0.0060384 | 0.10011 | 0.01618 | 0.0026664 | -0.031006 | -0.021108 | 0.029865 | 0.0057535 | 0.009155 | 0.086975 | -0.082397 | 0.013733 | 0.073242 | -0.013733 | 0.032043 | 0.004578 | 0.14648 | -0.082397 | 0.013733 | 0.032043 | 0.004578 | 0.073242 | 61.5829 | -61.8073 | -61.8805 | 61.7386 | 61.6974 | 61.6516 | 0.11444 | 0.068664 | 61.5829 | -61.7477 | -61.8805 | 61.6974 | 61.7386 | 61.6699 | 0.15564 | 0.086975 | 0.15564 | 0.09613 | 0.11444 | 0.09613 | 0.16937 | 0.22888 | 61.7523 | 61.8118 | -61.9766 | -61.9766 | 61.6791 | 61.6791 | 61.6745 | 61.6699
610.4844 | 123.7518 | -61.6516 | 61.8347 | -0.011967 | 0.0049915 | -0.0073647 | 0.02776 | 0.014488 | -0.019998 | 0.0025066 | 0.14589 | 0.03327 | -0.0026746 | 0.012787 | -0.025381 | 0.018116 | -0.013474 | -0.036621 | 0.09613 | -0.11902 | 0 | 0.091553 | -0.004578 | 0.009155 | -0.009155 | 0.1236 | -0.068665 | 0.068665 | 0.07782 | 0.059509 | 0.10529 | 61.5326 | -61.7386 | -61.8347 | 61.7432 | 61.6608 | 61.647 | 0.12817 | 0.11444 | 61.5829 | -61.7111 | -61.7661 | 61.7294 | 61.7569 | 61.7111 | 0.17395 | 0.12817 | 0.21057 | 0.11902 | 0.14649 | 0.13733 | 0.21515 | 0.19226 | 61.7477 | 61.7752 | -61.9537 | -61.9034 | 61.6516 | 61.7203 | 61.615 | 61.6425
611.4844 | 123.6877 | -61.6745 | 61.908 | 0.064327 | 0.0049915 | -0.00095673 | 0.028828 | 0.010216 | -0.011453 | -0.015651 | 0.23744 | 0.012976 | 0.00053042 | -0.050232 | -0.02004 | 0.017048 | -0.0059965 | 0.004578 | 0.10986 | -0.09613 | 0.009155 | 0.091553 | 0 | 0.050354 | -0.013733 | 0.15106 | -0.064087 | 0.032043 | 0.041199 | 0.036621 | 0.073242 | 61.5784 | -61.7981 | -61.8988 | 61.7661 | 61.7249 | 61.6745 | 0.14648 | 0.09613 | 61.6104 | -61.7569 | -61.8759 | 61.7157 | 61.7477 | 61.7111 | 0.13733 | 0.10071 | 0.18768 | 0.10528 | 0.10529 | 0.09613 | 0.20599 | 0.21515 | 61.7844 | 61.8256 | -62.0041 | -61.972 | 61.6837 | 61.7065 | 61.6791 | 61.6608
612.4844 | 123.7106 | -61.6791 | 61.8851 | 0.064327 | 0.013537 | -0.0062967 | 0.016011 | -0.0036699 | -0.0018402 | -0.0049704 | 0.22218 | 0.015112 | 0.013347 | 0.011719 | -0.023245 | 0.013843 | -0.013474 | -0.009155 | 0.091553 | -0.1236 | 0.009155 | 0.10529 | 0.004578 | 0.054932 | -0.018311 | 0.15564 | -0.07782 | 0.013733 | 0.036621 | 0.022888 | 0.045776 | 61.5555 | -61.7935 | -61.8759 | 61.7844 | 61.734 | 61.6837 | 0.17853 | 0.12817 | 61.6013 | -61.7294 | -61.8713 | 61.7157 | 61.7249 | 61.702 | 0.1236 | 0.10071 | 0.22888 | 0.13275 | 0.11444 | 0.091553 | 0.21515 | 0.23346 | 61.7706 | 61.8347 | -62.0087 | -61.9629 | 61.6882 | 61.6928 | 61.6699 | 61.6608
613.4844 | 123.7061 | -61.6837 | 61.8851 | 0.1864 | 0.0028555 | -0.0030927 | 0.02776 | 0.0091481 | -0.0093172 | -0.018856 | 0.039077 | 0.01618 | 0.0090754 | -3.1262e-05 | -0.017904 | 0.014911 | 0.0046845 | 0.022888 | 0.10986 | -0.086975 | 0 | 0.059509 | -0.018311 | 0.041199 | 0.022888 | 0.16479 | -0.082397 | 0.036621 | 0.068665 | 0.059509 | 0.064087 | 61.5967 | -61.7752 | -61.8851 | 61.7432 | 61.7249 | 61.6653 | 0.12817 | 0.068664 | 61.6013 | -61.7203 | -61.8485 | 61.7523 | 61.7477 | 61.7432 | 0.14648 | 0.14191 | 0.14648 | 0.086975 | 0.15106 | 0.11902 | 0.19684 | 0.24719 | 61.7935 | 61.8484 | -61.972 | -61.9675 | 61.6837 | 61.7203 | 61.7065 | 61.7065
614.4844 | 123.7152 | -61.7065 | 61.8942 | 0.049069 | 0.0081955 | -0.0030927 | 0.02242 | -0.0015339 | -0.013589 | -0.011379 | 0.084853 | 0.030065 | -0.0090826 | 0.0053097 | -0.018972 | 0.027729 | -0.0038605 | 0.009155 | 0.09613 | -0.10071 | -0.009155 | 0.068665 | -0.009155 | 0.032043 | 0.027466 | 0.15564 | -0.064087 | 0.032043 | 0.068665 | 0.027466 | 0.082397 | 61.6058 | -61.7981 | -61.9034 | 61.7752 | 61.7386 | 61.6974 | 0.13275 | 0.091553 | 61.6425 | -61.7386 | -61.8622 | 61.7752 | 61.7889 | 61.734 | 0.14648 | 0.091553 | 0.16937 | 0.091553 | 0.13275 | 0.09613 | 0.19684 | 0.21973 | 61.8027 | 61.8622 | -61.9949 | -61.9583 | 61.6974 | 61.7386 | 61.7157 | 61.734
615.4844 | 123.7015 | -61.6882 | 61.8576 | 0.03381 | 0.0060595 | -0.0073647 | 0.021352 | -0.0015339 | -0.011453 | -0.0060384 | 0.17641 | 0.017248 | 0.0058704 | -0.0032353 | -0.011495 | 0.0074349 | 0.0014805 | -0.050354 | 0.10986 | -0.10986 | 0.050354 | 0.12817 | 0.022888 | 0.059509 | -0.086975 | 0.14191 | -0.10529 | -0.032043 | -0.013733 | -0.027466 | 0.041199 | 61.5784 | -61.7477 | -61.8073 | 61.8164 | 61.7477 | 61.7111 | 0.16937 | 0.13275 | 61.5829 | -61.7157 | -61.8896 | 61.6745 | 61.7294 | 61.6608 | 0.14649 | 0.07782 | 0.23804 | 0.16022 | 0.091553 | 0.073243 | 0.21973 | 0.24719 | 61.7981 | 61.8301 | -61.9675 | -61.9629 | 61.7386 | 61.6562 | 61.6379 | 61.6013
616.4844 | 123.7152 | -61.6699 | 61.8988 | 0.20166 | 0.0092645 | 0.00011227 | 0.021352 | 0.0048751 | -0.0061122 | -0.02206 | 0.14589 | 0.019384 | 0.0069384 | 0.0074457 | -0.022176 | 0.019184 | 0.014297 | 0.009155 | 0.091553 | -0.091553 | 0 | 0.068665 | -0.027466 | 0.022888 | 0.013733 | 0.16022 | -0.082397 | 0.036621 | 0.050354 | 0.022888 | 0.064087 | 61.5784 | -61.8073 | -61.8988 | 61.7386 | 61.6928 | 61.6425 | 0.11444 | 0.064087 | 61.5875 | -61.7386 | -61.8622 | 61.7203 | 61.734 | 61.6928 | 0.14648 | 0.10528 | 0.16022 | 0.091553 | 0.13275 | 0.11902 | 0.18311 | 0.24261 | 61.7615 | 61.8301 | -61.9904 | -61.9812 | 61.6699 | 61.7065 | 61.6791 | 61.6837
617.4844 | 123.7061 | -61.6791 | 61.8805 | 0.15588 | 0.0039235 | -0.0041607 | 0.024556 | -0.0058059 | -0.0061122 | 0.0025066 | 0.069594 | 0.020452 | 0.012279 | -0.0053713 | -0.016836 | 0.017048 | 0.0025485 | 0.027466 | 0.091553 | -0.091553 | -0.022888 | 0.059509 | -0.027466 | 0.022888 | 0.013733 | 0.16022 | -0.082397 | 0.022888 | 0.045776 | 0.032043 | 0.07782 | 61.5875 | -61.7889 | -61.9034 | 61.7386 | 61.702 | 61.6516 | 0.11444 | 0.064087 | 61.5967 | -61.7203 | -61.8576 | 61.7249 | 61.7569 | 61.7111 | 0.16022 | 0.11444 | 0.15106 | 0.068665 | 0.12817 | 0.10528 | 0.18311 | 0.24261 | 61.7706 | 61.8393 | -61.972 | -61.9629 | 61.6562 | 61.702 | 61.7065 | 61.6928
618.4844 | 123.7381 | -61.6608 | 61.9034 | 0.018551 | 0.0081955 | -0.0095007 | 0.030965 | -0.0036699 | -0.0018402 | -0.010311 | 0.13063 | 0.017248 | 0.011211 | -0.0085763 | -0.0147 | 0.0095709 | -0.011337 | -0.004578 | 0.10986 | -0.1236 | 0.013733 | 0.10986 | 0.009155 | 0.041199 | -0.004578 | 0.15106 | -0.082397 | 0 | 0.050354 | 0.036621 | 0.086975 | 61.5372 | -61.7935 | -61.8896 | 61.7706 | 61.702 | 61.6699 | 0.16479 | 0.13275 | 61.5784 | -61.7523 | -61.9034 | 61.7111 | 61.7477 | 61.6974 | 0.16937 | 0.11902 | 0.23346 | 0.13733 | 0.13275 | 0.082397 | 0.23346 | 0.23346 | 61.7706 | 61.8118 | -62.027 | -61.9858 | 61.6745 | 61.6608 | 61.6562 | 61.6562
619.4844 | 123.7061 | -61.6928 | 61.8805 | 0.049069 | 0.021014 | 0.0011803 | 0.030965 | 0.0070111 | 0.0099088 | 0.0067786 | 0.20692 | 0.027929 | 0.010143 | -0.0032353 | -0.023245 | 0.012775 | -0.0092005 | -0.013733 | 0.10986 | -0.11444 | 0.022888 | 0.10986 | -0.013733 | 0.059509 | -0.013733 | 0.15106 | -0.07782 | 0.013733 | 0.041199 | 0.013733 | 0.050354 | 61.5784 | -61.7706 | -61.8576 | 61.8027 | 61.7523 | 61.6791 | 0.17395 | 0.10071 | 61.615 | -61.7294 | -61.8668 | 61.734 | 61.7432 | 61.7065 | 0.12817 | 0.091553 | 0.2243 | 0.13733 | 0.11902 | 0.091553 | 0.2243 | 0.22888 | 61.8027 | 61.8439 | -61.9949 | -61.9583 | 61.7157 | 61.7065 | 61.6791 | 61.6791
620.4844 | 123.7106 | -61.6653 | 61.8759 | 0.018551 | 0.0028555 | -0.0041607 | 0.026692 | 0.011284 | -0.0050442 | -0.0092424 | 0.11537 | 0.014044 | 0.0015984 | -0.0010993 | -0.024313 | 0.0074349 | 0.010025 | -0.036621 | 0.10529 | -0.09613 | 0.045776 | 0.12817 | 0.022888 | 0.036621 | -0.050354 | 0.14191 | -0.10071 | -0.009155 | 0.009155 | -0.004578 | 0.041199 | 61.5692 | -61.7706 | -61.8301 | 61.7935 | 61.702 | 61.6882 | 0.13275 | 0.11902 | 61.5646 | -61.734 | -61.8851 | 61.6745 | 61.7065 | 61.6608 | 0.14191 | 0.09613 | 0.2243 | 0.14191 | 0.10986 | 0.091553 | 0.20142 | 0.24262 | 61.7706 | 61.8073 | -61.972 | -61.9766 | 61.7111 | 61.6562 | 61.6287 | 61.615
621.4844 | 123.7106 | -61.6791 | 61.8896 | 0.064327 | 0.012469 | -0.0084327 | 0.021352 | 0.011284 | -0.0061122 | -0.0092424 | 0.13063 | 0.021521 | 0.0026664 | -0.026734 | -0.012563 | 0.01598 | -0.0049285 | 0.018311 | 0.10071 | -0.086975 | -0.018311 | 0.064087 | -0.013733 | 0.041199 | 0.004578 | 0.15106 | -0.07782 | 0.013733 | 0.059509 | 0.032043 | 0.068665 | 61.5921 | -61.7889 | -61.908 | 61.7432 | 61.7203 | 61.6653 | 0.12817 | 0.073242 | 61.6013 | -61.7386 | -61.8759 | 61.7386 | 61.7477 | 61.7111 | 0.14649 | 0.10986 | 0.15106 | 0.068664 | 0.13733 | 0.091553 | 0.18768 | 0.22888 | 61.7798 | 61.8301 | -61.9766 | -61.9675 | 61.6608 | 61.6928 | 61.6974 | 61.6837
622.4844 | 123.7015 | -61.6837 | 61.8668 | 0.12536 | 0.015673 | -0.0062967 | 0.020283 | 0.0006031 | -0.0082492 | -0.0071064 | 0.17641 | 0.022589 | 0.0080074 | -0.052368 | -0.011495 | 0.010639 | 0.0068215 | 0.004578 | 0.10071 | -0.091553 | 0 | 0.07782 | -0.022888 | 0.041199 | 0.022888 | 0.14648 | -0.082397 | 0.018311 | 0.059509 | 0.027466 | 0.068665 | 61.5921 | -61.7661 | -61.8668 | 61.7615 | 61.7249 | 61.6608 | 0.13275 | 0.068665 | 61.6013 | -61.7203 | -61.8484 | 61.7432 | 61.7523 | 61.7111 | 0.15106 | 0.10986 | 0.16937 | 0.091553 | 0.14191 | 0.10071 | 0.19226 | 0.22888 | 61.7844 | 61.8301 | -61.9583 | -61.9492 | 61.6837 | 61.702 | 61.6882 | 61.7065
623.4844 | 123.6969 | -61.6928 | 61.8942 | 0.12536 | 0.015673 | -0.00095673 | 0.026692 | 0.014488 | -0.016794 | -0.0071064 | 0.17641 | 0.025793 | 0.020824 | -0.018189 | -0.012563 | 0.020252 | 0.014297 | 0.013733 | 0.091553 | -0.10986 | 0.013733 | 0.068665 | -0.013733 | 0.045776 | -0.009155 | 0.16479 | -0.064087 | 0.022888 | 0.036621 | 0.013733 | 0.059509 | 61.5829 | -61.8027 | -61.8805 | 61.7615 | 61.7386 | 61.6791 | 0.15564 | 0.09613 | 61.6287 | -61.7294 | -61.8713 | 61.7294 | 61.7523 | 61.7065 | 0.1236 | 0.07782 | 0.17853 | 0.1236 | 0.10071 | 0.086975 | 0.20142 | 0.22888 | 61.7844 | 61.8576 | -62.0041 | -61.9583 | 61.7065 | 61.7157 | 61.7065 | 61.6837
624.4844 | 123.7015 | -61.6928 | 61.8851 | 0.1864 | 0.016741 | 0.0033163 | 0.019215 | 0.010216 | -0.0061122 | -0.0028344 | 0.13063 | 0.012976 | 0.0026664 | -0.0096443 | -0.0093592 | 0.020252 | 0.010025 | 0.018311 | 0.07782 | -0.091553 | -0.022888 | 0.059509 | -0.013733 | 0.027466 | 0.009155 | 0.14191 | -0.082397 | 0.013733 | 0.036621 | 0.013733 | 0.059509 | 61.6013 | -61.8073 | -61.908 | 61.7523 | 61.7203 | 61.6791 | 0.11902 | 0.07782 | 61.6104 | -61.7432 | -61.8713 | 61.7294 | 61.7523 | 61.7065 | 0.14191 | 0.09613 | 0.15106 | 0.068665 | 0.11902 | 0.09613 | 0.16937 | 0.2243 | 61.7706 | 61.8347 | -61.9766 | -61.9675 | 61.6699 | 61.7065 | 61.7111 | 61.702
625.4844 | 123.674 | -61.6745 | 61.8759 | 0.018551 | 0.010333 | -0.0084327 | 0.02242 | -0.0090099 | -0.0050442 | 0.0057106 | 0.14589 | 0.017248 | 0.011211 | -0.01178 | -0.018972 | 0.0095709 | 0.0025485 | -0.050354 | 0.10529 | -0.10071 | 0.054932 | 0.13733 | 0.036621 | 0.068665 | -0.064087 | 0.15564 | -0.091553 | -0.027466 | -0.018311 | -0.041199 | 0.032043 | 61.5738 | -61.7706 | -61.821 | 61.8118 | 61.7432 | 61.7111 | 0.16937 | 0.13733 | 61.5829 | -61.7203 | -61.9034 | 61.6562 | 61.7065 | 61.6333 | 0.1236 | 0.050354 | 0.23804 | 0.15564 | 0.073242 | 0.064087 | 0.20599 | 0.24719 | 61.7798 | 61.8301 | -61.9766 | -61.9675 | 61.7294 | 61.647 | 61.6241 | 61.6104
626.4844 | 123.7244 | -61.6837 | 61.8759 | 0.018551 | 0.015673 | 0.0011803 | 0.017079 | -0.0036699 | -0.0082492 | -0.020992 | 0.26796 | 0.019384 | -0.0016066 | -0.031006 | -0.023245 | 0.024524 | 0.014297 | -0.004578 | 0.10529 | -0.10986 | 0.004578 | 0.09613 | 0 | 0.036621 | -0.009155 | 0.15106 | -0.091553 | 0.018311 | 0.036621 | 0.036621 | 0.068665 | 61.5738 | -61.7706 | -61.8713 | 61.7798 | 61.7203 | 61.6837 | 0.14648 | 0.10986 | 61.5921 | -61.7249 | -61.8576 | 61.7203 | 61.7523 | 61.7203 | 0.16022 | 0.12817 | 0.20599 | 0.11444 | 0.12817 | 0.10986 | 0.21515 | 0.24261 | 61.7889 | 61.8347 | -61.9858 | -61.9675 | 61.6882 | 61.702 | 61.6791 | 61.6745
627.4844 | 123.7198 | -61.6745 | 61.8759 | 0.064327 | 0.016741 | 0.0033163 | 0.02776 | 0.011284 | -0.00077219 | -0.0081744 | 0.11537 | 0.01618 | -0.010151 | -0.0032353 | -0.017904 | 0.011707 | -0.012405 | 0.009155 | 0.10529 | -0.12817 | 0.009155 | 0.073242 | -0.018311 | 0.027466 | 0.022888 | 0.14191 | -0.07782 | 0.022888 | 0.059509 | 0.027466 | 0.068665 | 61.5463 | -61.7706 | -61.8668 | 61.7477 | 61.702 | 61.6562 | 0.15564 | 0.10986 | 61.5967 | -61.734 | -61.853 | 61.734 | 61.7432 | 61.702 | 0.14649 | 0.10529 | 0.20142 | 0.13733 | 0.13733 | 0.10071 | 0.23346 | 0.21973 | 61.7798 | 61.8164 | -62.0041 | -61.9537 | 61.6837 | 61.6974 | 61.6837 | 61.6974
628.4844 | 123.7244 | -61.6608 | 61.8805 | 0.14062 | 0.0071275 | 0.00011227 | 0.02776 | 0.012352 | -0.0018402 | -0.00069841 | 0.10011 | 0.034338 | 0.0015984 | -0.010712 | -0.012563 | 0.018116 | -0.00065554 | 0.009155 | 0.09613 | -0.09613 | -0.013733 | 0.059509 | -0.018311 | 0.027466 | 0.022888 | 0.16022 | -0.09613 | 0.013733 | 0.059509 | 0.032043 | 0.073242 | 61.5646 | -61.7844 | -61.8942 | 61.7203 | 61.6882 | 61.6425 | 0.1236 | 0.077819 | 61.5646 | -61.7203 | -61.8668 | 61.7203 | 61.734 | 61.6928 | 0.16937 | 0.12817 | 0.15564 | 0.082397 | 0.15564 | 0.10986 | 0.19226 | 0.25635 | 61.7569 | 61.821 | -61.9766 | -61.9766 | 61.647 | 61.6745 | 61.6699 | 61.6837
629.4844 | 123.6877 | -61.6837 | 61.8851 | 0.15588 | 0.011401 | -0.0062967 | 0.017079 | -0.0026019 | -0.0071802 | -0.015651 | 0.084853 | 0.022589 | -0.0016066 | -0.027802 | -0.017904 | 0.014911 | -0.0017235 | 0.013733 | 0.10529 | -0.09613 | 0.004578 | 0.073242 | -0.027466 | 0.045776 | 0.013733 | 0.15106 | -0.086975 | 0.036621 | 0.045776 | 0.032043 | 0.073242 | 61.5875 | -61.7798 | -61.8805 | 61.7569 | 61.7294 | 61.6562 | 0.14191 | 0.068664 | 61.5967 | -61.734 | -61.8485 | 61.7294 | 61.7569 | 61.7157 | 0.16022 | 0.11902 | 0.16937 | 0.10071 | 0.13275 | 0.1236 | 0.20142 | 0.23804 | 61.7889 | 61.8347 | -61.9812 | -61.972 | 61.6882 | 61.7203 | 61.6974 | 61.6974
630.4844 | 123.7793 | -61.647 | 61.8301 | 0.049069 | 0.018878 | -0.0073647 | 0.019215 | 0.0048751 | 0.014182 | -0.025264 | 0.26796 | 0.015112 | -0.0026746 | -0.024597 | -0.022176 | 0.025593 | -0.018814 | 0.027466 | 0.068665 | -0.045776 | -0.10529 | -0.027466 | -0.073242 | -0.050354 | 0.07782 | 0.1236 | -0.068665 | 0.082397 | 0.10529 | 0.086975 | 0.10529 | 61.6013 | -61.7615 | -61.9354 | 61.6196 | 61.5967 | 61.5738 | -0.004578 | -0.027466 | 61.5784 | -61.7065 | -61.7477 | 61.7523 | 61.7523 | 61.734 | 0.17395 | 0.15564 | 0.01831 | -0.05951 | 0.17395 | 0.15106 | 0.11444 | 0.19226 | 61.7157 | 61.7706 | -61.8759 | -61.8988 | 61.5417 | 61.7294 | 61.6745 | 61.7249
631.4844 | 123.6969 | -61.6837 | 61.8805 | 0.15588 | 0.024218 | -0.00095673 | 0.02242 | -0.023964 | -0.0018402 | 0.0067786 | 0.11537 | 0.017248 | 0.0048024 | -0.010712 | -0.021108 | 0.030933 | -0.014542 | 0 | 0.091553 | -0.082397 | -0.004578 | 0.064087 | -0.013733 | 0.036621 | 0.013733 | 0.15564 | -0.082397 | 0.013733 | 0.018311 | 0.018311 | 0.050354 | 61.6013 | -61.7889 | -61.8851 | 61.7477 | 61.7203 | 61.6699 | 0.11902 | 0.068664 | 61.6013 | -61.7249 | -61.8668 | 61.702 | 61.734 | 61.702 | 0.13275 | 0.10071 | 0.14648 | 0.077819 | 0.10071 | 0.09613 | 0.17395 | 0.23804 | 61.7752 | 61.8393 | -61.9629 | -61.9629 | 61.6791 | 61.6974 | 61.6837 | 61.6974
632.4844 | 123.7106 | -61.6882 | 61.9171 | 0.15588 | 0.016741 | -0.00095673 | 0.025624 | 0.0048751 | -0.00077219 | -0.0039024 | 0.26796 | 0.021521 | 0.0048024 | -0.043823 | -0.032858 | 0.013843 | -0.01561 | 0.013733 | 0.10071 | -0.11444 | 0.009155 | 0.086975 | -0.013733 | 0.041199 | 0.018311 | 0.16022 | -0.082397 | 0.013733 | 0.045776 | 0.041199 | 0.073242 | 61.5738 | -61.8164 | -61.908 | 61.7752 | 61.7294 | 61.6745 | 0.15564 | 0.10071 | 61.6058 | -61.7569 | -61.9034 | 61.734 | 61.7615 | 61.7294 | 0.15564 | 0.1236 | 0.20142 | 0.1236 | 0.12817 | 0.09613 | 0.21515 | 0.24261 | 61.7889 | 61.8484 | -62.0316 | -61.9995 | 61.6974 | 61.702 | 61.702 | 61.7065
633.4844 | 123.7015 | -61.6699 | 61.8759 | 0.21692 | 0.0081955 | -0.0052287 | 0.024556 | -0.0015339 | -0.021066 | -0.02206 | 0.11537 | 0.017248 | 0.0090754 | -0.0075083 | -0.017904 | 0.011707 | 0.012161 | 0 | 0.091553 | -0.10529 | 0.004578 | 0.09613 | -0.009155 | 0.050354 | -0.004578 | 0.15564 | -0.073242 | 0.013733 | 0.050354 | 0.036621 | 0.073242 | 61.5646 | -61.7844 | -61.8713 | 61.7661 | 61.7203 | 61.6608 | 0.15564 | 0.096131 | 61.5967 | -61.7203 | -61.8622 | 61.7203 | 61.7432 | 61.7065 | 0.14648 | 0.10986 | 0.20142 | 0.10986 | 0.1236 | 0.086975 | 0.19684 | 0.22888 | 61.7615 | 61.8256 | -61.9812 | -61.9492 | 61.6745 | 61.6837 | 61.6699 | 61.6653
634.4844 | 123.7152 | -61.6791 | 61.8622 | 0.17114 | 0.017809 | -0.01057 | 0.028828 | 0.0006031 | -0.0029082 | -0.011379 | 0.11537 | 0.025793 | 0.0026664 | -0.013916 | -0.013631 | 0.022388 | -0.013474 | 0.009155 | 0.10529 | -0.10986 | -0.009155 | 0.054932 | -0.027466 | 0.041199 | 0.027466 | 0.14191 | -0.07782 | 0.018311 | 0.054932 | 0.032043 | 0.054932 | 61.5692 | -61.7569 | -61.8713 | 61.734 | 61.7203 | 61.6516 | 0.15106 | 0.082397 | 61.6013 | -61.7203 | -61.8439 | 61.734 | 61.734 | 61.7111 | 0.13275 | 0.10986 | 0.16479 | 0.10071 | 0.13275 | 0.096131 | 0.21515 | 0.21973 | 61.7844 | 61.821 | -61.972 | -61.94 | 61.6699 | 61.6974 | 61.6882 | 61.7065
635.4844 | 123.7198 | -61.6653 | 61.8713 | 0.03381 | 0.011401 | 0.0054523 | 0.02776 | -0.0047379 | -0.013589 | 0.015324 | 0.054336 | 0.015112 | 0.0048024 | -0.019257 | -0.017904 | 0.014911 | 0.0025485 | -0.036621 | 0.10071 | -0.11444 | 0.045776 | 0.11444 | 0.022888 | 0.064087 | -0.059509 | 0.15106 | -0.082397 | 0.004578 | 0.018311 | -0.004578 | 0.050354 | 61.5509 | -61.7706 | -61.8256 | 61.7798 | 61.7294 | 61.6882 | 0.17853 | 0.13733 | 61.5829 | -61.7203 | -61.8668 | 61.6837 | 61.7157 | 61.6608 | 0.13275 | 0.077819 | 0.22888 | 0.16022 | 0.10071 | 0.086975 | 0.21515 | 0.23346 | 61.7661 | 61.8164 | -61.9858 | -61.9537 | 61.7111 | 61.6699 | 61.6287 | 61.6058
636.4844 | 123.6969 | -61.6699 | 61.8896 | 0.12536 | 0.015673 | -0.0020247 | 0.023488 | -0.0058059 | 0.014182 | -0.015651 | 0.023818 | 0.01618 | -0.00053758 | -0.0021673 | -0.017904 | 0.010639 | -0.0038605 | 0.009155 | 0.09613 | -0.091553 | 0 | 0.073242 | -0.004578 | 0.032043 | -0.009155 | 0.16022 | -0.082397 | 0.013733 | 0.022888 | 0.013733 | 0.041199 | 61.5784 | -61.7935 | -61.8896 | 61.7432 | 61.702 | 61.6653 | 0.1236 | 0.086975 | 61.5875 | -61.7294 | -61.8759 | 61.6928 | 61.7111 | 61.6837 | 0.1236 | 0.09613 | 0.16479 | 0.091553 | 0.10528 | 0.09613 | 0.18768 | 0.24261 | 61.7661 | 61.8301 | -61.9812 | -61.972 | 61.6699 | 61.6837 | 61.6791 | 61.6608
637.4844 | 123.7244 | -61.702 | 61.8759 | 0.15588 | 0.015673 | -0.01057 | 0.011738 | 0.012352 | -0.0029082 | -0.012447 | 0.14589 | 0.022589 | 0.00053042 | -0.017121 | -0.012563 | 0.025593 | -0.014542 | -0.009155 | 0.10529 | -0.10986 | 0 | 0.064087 | -0.018311 | 0.032043 | -0.004578 | 0.12817 | -0.082397 | 0.013733 | 0.045776 | 0.009155 | 0.045776 | 61.5921 | -61.7706 | -61.8759 | 61.7661 | 61.734 | 61.6837 | 0.14191 | 0.091552 | 61.6196 | -61.7477 | -61.8622 | 61.7477 | 61.7477 | 61.7111 | 0.12817 | 0.091552 | 0.17395 | 0.10986 | 0.12817 | 0.09613 | 0.21515 | 0.21057 | 61.8073 | 61.8301 | -61.9858 | -61.9583 | 61.702 | 61.7157 | 61.6928 | 61.6974
638.4844 | 123.7061 | -61.7065 | 61.8851 | 0.12536 | 0.0092645 | -0.0052287 | 0.030965 | 0.0016711 | -0.0029082 | -0.015651 | 0.084853 | 0.0076354 | -0.0016066 | -0.041687 | -0.015768 | 0.01598 | -0.0070645 | 0.004578 | 0.086975 | -0.09613 | 0 | 0.064087 | -0.027466 | 0.032043 | 0.013733 | 0.15106 | -0.07782 | 0.018311 | 0.050354 | 0.009155 | 0.050354 | 61.6104 | -61.7981 | -61.8851 | 61.7706 | 61.7386 | 61.6791 | 0.12817 | 0.068664 | 61.6287 | -61.734 | -61.8668 | 61.7569 | 61.7569 | 61.7157 | 0.12817 | 0.086975 | 0.16022 | 0.09613 | 0.12817 | 0.096131 | 0.1831 | 0.22888 | 61.7935 | 61.8576 | -61.9812 | -61.9629 | 61.7065 | 61.7249 | 61.7111 | 61.7203
639.4844 | 123.7244 | -61.6882 | 61.8851 | 0.14062 | 0.015673 | -0.0030927 | 0.017079 | 0.015556 | -0.017862 | -0.012447 | 0.22218 | 0.021521 | 0.0058704 | -0.0075083 | -0.018972 | 0.018116 | -0.0059965 | -0.013733 | 0.11444 | -0.11902 | -0.004578 | 0.09613 | -0.018311 | 0.036621 | 0 | 0.13733 | -0.068665 | 0.009155 | 0.064087 | 0.027466 | 0.064087 | 61.5692 | -61.7706 | -61.8896 | 61.7844 | 61.7249 | 61.6699 | 0.15564 | 0.10071 | 61.6196 | -61.7477 | -61.8759 | 61.7523 | 61.7523 | 61.7157 | 0.13275 | 0.096131 | 0.21515 | 0.11444 | 0.13275 | 0.07782 | 0.23346 | 0.20599 | 61.8027 | 61.8256 | -62.0041 | -61.9537 | 61.6837 | 61.6974 | 61.6745 | 61.6882
640.4844 | 123.7198 | -61.7157 | 61.8668 | 0.049069 | 0.0049915 | -0.0041607 | 0.026692 | 0.01342 | -0.014657 | -0.0092424 | 0.039077 | 0.024725 | 0.0037344 | -0.010712 | -0.018972 | 0.020252 | 0.0025485 | -0.032043 | 0.10529 | -0.10986 | 0.036621 | 0.11444 | 0.009155 | 0.032043 | -0.059509 | 0.13733 | -0.10071 | -0.004578 | 0.013733 | 0.009155 | 0.054932 | 61.6058 | -61.7615 | -61.8301 | 61.8301 | 61.7477 | 61.7249 | 0.14191 | 0.11902 | 61.615 | -61.7294 | -61.8713 | 61.7294 | 61.7706 | 61.7249 | 0.15564 | 0.10986 | 0.2243 | 0.14648 | 0.11444 | 0.09613 | 0.21515 | 0.23804 | 61.821 | 61.853 | -61.9766 | -61.9675 | 61.7523 | 61.7111 | 61.6837 | 61.6562
641.4844 | 123.7427 | -61.6974 | 61.8851 | 0.12536 | 0.012469 | -0.01057 | 0.020283 | 0.0070111 | -0.010385 | -0.02206 | 0.039077 | 0.012976 | 0.0048024 | -0.013916 | -0.026449 | 0.01598 | -0.016678 | 0.018311 | 0.082397 | -0.086975 | -0.013733 | 0.068665 | -0.013733 | 0.032043 | 0.013733 | 0.14648 | -0.073242 | 0.022888 | 0.054932 | 0.032043 | 0.059509 | 61.6104 | -61.8027 | -61.8988 | 61.7661 | 61.7294 | 61.6837 | 0.11902 | 0.073242 | 61.6241 | -61.7386 | -61.8622 | 61.7523 | 61.7569 | 61.7294 | 0.13275 | 0.10529 | 0.15564 | 0.073242 | 0.12817 | 0.09613 | 0.16937 | 0.21973 | 61.7798 | 61.8439 | -61.972 | -61.9583 | 61.6837 | 61.7203 | 61.7157 | 61.7111
642.4844 | 123.8022 | -61.6699 | 61.8668 | 0.094845 | -0.0067575 | -0.0073647 | 0.025624 | 0.0080791 | -0.00077219 | -0.013515 | 0.20692 | 0.022589 | 0.0048024 | 0.0010367 | -0.018972 | 0.019184 | -0.0017235 | -0.018311 | 0.073242 | -0.091553 | -0.036621 | 0.054932 | -0.041199 | 0.004578 | 0.009155 | 0.11902 | -0.073242 | 0.059509 | 0.082397 | 0.064087 | 0.11444 | 61.5784 | -61.7935 | -61.9034 | 61.7249 | 61.6745 | 61.6287 | 0.096131 | 0.050354 | 61.5967 | -61.7477 | -61.8073 | 61.7523 | 61.7844 | 61.734 | 0.18768 | 0.13733 | 0.14649 | 0.054932 | 0.15564 | 0.13275 | 0.16479 | 0.19226 | 61.7432 | 61.7889 | -61.9583 | -61.94 | 61.6333 | 61.7294 | 61.6516 | 61.6791
643.4844 | 123.7289 | -61.6974 | 61.8851 | 0.14062 | 0.017809 | 0.00011227 | 0.019215 | 0.0027391 | -0.0082492 | -0.0071064 | 0.039077 | 0.012976 | 0.0015984 | -0.017121 | -0.016836 | 0.017048 | 0.0036165 | 0.009155 | 0.10529 | -0.10529 | -0.009155 | 0.054932 | -0.018311 | 0.036621 | 0.013733 | 0.13733 | -0.07782 | -0.004578 | 0.041199 | 0.009155 | 0.064087 | 61.5921 | -61.7798 | -61.8942 | 61.7523 | 61.734 | 61.6791 | 0.14191 | 0.086975 | 61.6196 | -61.7477 | -61.8896 | 61.7386 | 61.7615 | 61.7065 | 0.14191 | 0.086975 | 0.16022 | 0.096131 | 0.11902 | 0.073242 | 0.21057 | 0.21515 | 61.8027 | 61.8347 | -61.9904 | -61.9629 | 61.6882 | 61.6928 | 61.7065 | 61.7111
644.4844 | 123.7198 | -61.6974 | 61.8759 | 0.21692 | 0.0071275 | -0.0020247 | 0.02776 | 0.0059431 | -0.0093172 | -0.013515 | 0.069594 | 0.030065 | 0.0069384 | 0.021332 | -0.015768 | 0.011707 | -0.0059965 | 0.018311 | 0.09613 | -0.086975 | 0 | 0.059509 | -0.027466 | 0.032043 | 0.013733 | 0.16022 | -0.064087 | 0.027466 | 0.045776 | 0.032043 | 0.059509 | 61.6104 | -61.7798 | -61.8759 | 61.7569 | 61.7294 | 61.6699 | 0.11902 | 0.059509 | 61.6333 | -61.7157 | -61.8484 | 61.7432 | 61.7569 | 61.7294 | 0.1236 | 0.09613 | 0.14648 | 0.086975 | 0.10986 | 0.091553 | 0.1831 | 0.2243 | 61.7935 | 61.8576 | -61.9629 | -61.94 | 61.6974 | 61.7249 | 61.7157 | 61.7111
645.4844 | 123.6877 | -61.734 | 61.8988 | 0.0032924 | 0.018878 | -0.0084327 | 0.029896 | 0.026237 | -0.0082492 | -0.024196 | 0.023818 | 0.01618 | -0.0026746 | -0.027802 | -0.010427 | 0.023456 | -0.00065554 | -0.059509 | 0.09613 | -0.11444 | 0.054932 | 0.15564 | 0.032043 | 0.068665 | -0.07782 | 0.13733 | -0.11444 | -0.050354 | -0.036621 | -0.054932 | 0.022888 | 61.6196 | -61.8027 | -61.8439 | 61.8896 | 61.8027 | 61.7661 | 0.18311 | 0.14648 | 61.6196 | -61.7615 | -61.9492 | 61.6974 | 61.7569 | 61.6791 | 0.13733 | 0.059509 | 0.27008 | 0.16937 | 0.07782 | 0.064087 | 0.21057 | 0.25177 | 61.8301 | 61.8713 | -62.0132 | -62.0132 | 61.7889 | 61.6837 | 61.6745 | 61.6562
646.4844 | 123.7061 | -61.7111 | 61.8851 | 0.1864 | 0.0017875 | 0.0022483 | 0.028828 | 0.016624 | -0.015725 | -0.00069841 | 0.23744 | 0.018316 | -0.0026746 | -0.023529 | -0.016836 | 0.023456 | -0.0038605 | -0.032043 | 0.1236 | -0.10986 | 0.045776 | 0.13275 | 0.022888 | 0.068665 | -0.068665 | 0.14648 | -0.10071 | -0.004578 | 0.009155 | 0.009155 | 0.054932 | 61.6013 | -61.7615 | -61.8393 | 61.8439 | 61.7798 | 61.734 | 0.17853 | 0.13275 | 61.6104 | -61.7386 | -61.8896 | 61.7203 | 61.7661 | 61.7203 | 0.15564 | 0.10986 | 0.24261 | 0.15564 | 0.10986 | 0.09613 | 0.23346 | 0.24719 | 61.8347 | 61.8576 | -61.9949 | -61.9858 | 61.7569 | 61.7065 | 61.6791 | 61.6425
647.4844 | 123.8113 | -61.6699 | 61.853 | 0.018551 | 0.019946 | 0.0022483 | 0.013875 | 0.019829 | -0.013589 | -0.0081744 | 0.22218 | 0.0097714 | 0.0048024 | -0.043823 | -0.024313 | 0.013843 | 0.0046845 | 0.036621 | 0.054932 | -0.07782 | -0.091553 | -0.009155 | -0.091553 | -0.045776 | 0.07782 | 0.11444 | -0.054932 | 0.091553 | 0.1236 | 0.086975 | 0.1236 | 61.5921 | -61.7981 | -61.9446 | 61.6608 | 61.6241 | 61.5784 | 0.032044 | -0.013733 | 61.615 | -61.7386 | -61.7615 | 61.7935 | 61.7935 | 61.7569 | 0.17853 | 0.14191 | 0.068665 | -0.013733 | 0.17853 | 0.14649 | 0.13275 | 0.16937 | 61.7249 | 61.7844 | -61.9308 | -61.908 | 61.5784 | 61.7615 | 61.7065 | 61.7477
648.4844 | 123.7198 | -61.702 | 61.8942 | 0.079586 | 0.0071275 | -0.012706 | 0.02242 | 0.018761 | -0.013589 | -0.0049704 | 0.10011 | 0.015112 | 0.0069384 | -3.1262e-05 | -0.012563 | 0.0052979 | -0.0027915 | -0.018311 | 0.10071 | -0.10071 | 0.013733 | 0.10529 | -0.009155 | 0.054932 | -0.009155 | 0.15106 | -0.086975 | 0.004578 | 0.041199 | 0 | 0.018311 | 61.6013 | -61.7935 | -61.8805 | 61.8073 | 61.7569 | 61.6928 | 0.15564 | 0.091553 | 61.615 | -61.7432 | -61.8896 | 61.7432 | 61.7203 | 61.702 | 0.10529 | 0.086975 | 0.20599 | 0.11444 | 0.12817 | 0.091553 | 0.20142 | 0.23804 | 61.8027 | 61.853 | -61.9949 | -61.9812 | 61.7157 | 61.7065 | 61.6837 | 61.6928
649.4844 | 123.7289 | -61.6974 | 61.8942 | 0.049069 | 0.015673 | -0.013774 | 0.032033 | -0.0047379 | 0.0035008 | -0.0081744 | 0.14589 | 0.012976 | 0.015483 | -0.0021673 | -0.018972 | 0.013843 | -0.00065554 | -0.022888 | 0.10986 | -0.11444 | 0.036621 | 0.14191 | 0.018311 | 0.082397 | -0.059509 | 0.16479 | -0.09613 | -0.004578 | 0.022888 | 0.018311 | 0.045776 | 61.5829 | -61.7844 | -61.8576 | 61.8393 | 61.7798 | 61.7157 | 0.19684 | 0.13275 | 61.6013 | -61.7294 | -61.8988 | 61.7203 | 61.7432 | 61.7157 | 0.14191 | 0.11444 | 0.25635 | 0.15106 | 0.11902 | 0.091552 | 0.2243 | 0.26092 | 61.8073 | 61.8622 | -62.0087 | -61.9904 | 61.734 | 61.6928 | 61.6745 | 61.6379
650.4844 | 123.7015 | -61.6837 | 61.9125 | 0.094845 | 0.0028555 | -0.0030927 | 0.02776 | 0.017693 | 0.0045688 | 0.0014386 | -0.021958 | 0.040747 | 0.0037344 | 0.012787 | -0.015768 | 0.020252 | -0.0092005 | -0.050354 | 0.10071 | -0.10986 | 0.050354 | 0.12817 | 0.036621 | 0.068665 | -0.07782 | 0.13275 | -0.091553 | -0.013733 | -0.027466 | -0.022888 | 0.022888 | 61.5738 | -61.8118 | -61.8622 | 61.8118 | 61.7523 | 61.7203 | 0.17853 | 0.14648 | 61.5921 | -61.7798 | -61.9263 | 61.6562 | 61.7065 | 61.6608 | 0.11444 | 0.068665 | 0.23804 | 0.16022 | 0.064087 | 0.07782 | 0.21057 | 0.2243 | 61.7844 | 61.8164 | -62.0224 | -62.0041 | 61.734 | 61.6699 | 61.6333 | 61.6058
651.4844 | 123.7244 | -61.6791 | 61.8896 | 0.21692 | 0.011401 | -0.013774 | 0.021352 | -0.015419 | -0.022134 | 0.014256 | 0.13063 | 0.015112 | 0.0090754 | 0.0074457 | -0.02004 | 0.017048 | -0.013474 | -0.004578 | 0.09613 | -0.10529 | 0.022888 | 0.091553 | -0.027466 | 0.041199 | -0.004578 | 0.16022 | -0.07782 | 0.004578 | 0.064087 | 0.032043 | 0.064087 | 61.5738 | -61.7935 | -61.8668 | 61.7706 | 61.7203 | 61.6516 | 0.14649 | 0.07782 | 61.6013 | -61.7294 | -61.8851 | 61.7432 | 61.7432 | 61.7111 | 0.14191 | 0.10986 | 0.19684 | 0.12817 | 0.14191 | 0.082398 | 0.20142 | 0.23804 | 61.7752 | 61.8393 | -61.9949 | -61.9675 | 61.702 | 61.6837 | 61.6745 | 61.6745
652.4844 | 123.7976 | -61.6653 | 61.8576 | -0.027225 | 0.0092645 | 0.0011803 | 0.018147 | 0.0006031 | -0.013589 | 0.0014386 | 0.2527 | 0.010839 | 0.0090754 | -0.014984 | -0.018972 | 0.01598 | -0.013474 | 0.050354 | 0.064087 | -0.07782 | -0.10071 | -0.032043 | -0.10529 | -0.064087 | 0.086975 | 0.10529 | -0.068665 | 0.09613 | 0.1236 | 0.10071 | 0.12817 | 61.5875 | -61.7935 | -61.9583 | 61.6333 | 61.6013 | 61.5601 | 0.013733 | -0.027466 | 61.5967 | -61.7523 | -61.7615 | 61.7889 | 61.7935 | 61.7661 | 0.19684 | 0.16937 | 0.045777 | -0.022888 | 0.19226 | 0.16479 | 0.14191 | 0.17395 | 61.7294 | 61.7706 | -61.9354 | -61.9263 | 61.5646 | 61.7615 | 61.7157 | 61.7523
653.4844 | 123.6832 | -61.702 | 61.8988 | 0.079586 | 0.012469 | -0.0095007 | 0.018147 | 0.015556 | -0.0082492 | 0.0099836 | 0.23744 | 0.020452 | 0.013347 | -0.0043033 | -0.030721 | 0.019184 | -0.0027915 | -0.050354 | 0.10071 | -0.11444 | 0.041199 | 0.12817 | 0.022888 | 0.086975 | -0.07782 | 0.14191 | -0.09613 | -0.045776 | 0.004578 | -0.013733 | 0.022888 | 61.5875 | -61.7981 | -61.8576 | 61.8301 | 61.7889 | 61.7249 | 0.20142 | 0.13733 | 61.6058 | -61.7569 | -61.9446 | 61.7065 | 61.7249 | 61.6882 | 0.11902 | 0.082397 | 0.24262 | 0.15564 | 0.10071 | 0.050354 | 0.21515 | 0.23804 | 61.8027 | 61.8439 | -62.0132 | -61.9949 | 61.7432 | 61.6562 | 61.6516 | 61.6241
654.4844 | 123.7198 | -61.6837 | 61.9171 | 0.17114 | 0.0071275 | -0.012706 | 0.019215 | 0.0059431 | -0.010385 | -0.0060384 | 0.17641 | 0.015112 | 0.0080074 | -0.026734 | -0.015768 | 0.014911 | -0.012405 | -0.036621 | 0.1236 | -0.10529 | 0.050354 | 0.13733 | 0.018311 | 0.082397 | -0.068665 | 0.16479 | -0.091553 | -0.018311 | 0.013733 | 0 | 0.027466 | 61.5784 | -61.7935 | -61.8668 | 61.821 | 61.7661 | 61.702 | 0.18768 | 0.1236 | 61.5921 | -61.7523 | -61.9354 | 61.6974 | 61.7111 | 61.6837 | 0.11902 | 0.091553 | 0.24262 | 0.15564 | 0.10529 | 0.073242 | 0.22888 | 0.25635 | 61.8073 | 61.8484 | -62.0224 | -62.0087 | 61.734 | 61.6653 | 61.647 | 61.615
655.4844 | 123.7152 | -61.7294 | 61.8622 | 0.1101 | 0.011401 | 0.0033163 | 0.023488 | 0.028374 | -0.00077219 | 0.0014386 | 0.13063 | 0.012976 | -0.010151 | -0.027802 | -0.022176 | 0.0085029 | -0.01561 | -0.036621 | 0.10986 | -0.09613 | 0.018311 | 0.11444 | 0.027466 | 0.045776 | -0.054932 | 0.14191 | -0.091553 | -0.004578 | 0.013733 | -0.018311 | 0.054932 | 61.6333 | -61.7523 | -61.8439 | 61.8439 | 61.7752 | 61.7569 | 0.14191 | 0.1236 | 61.6379 | -61.7203 | -61.8668 | 61.7432 | 61.7844 | 61.7111 | 0.14649 | 0.073242 | 0.21057 | 0.11444 | 0.10529 | 0.086975 | 0.20599 | 0.23346 | 61.8393 | 61.8713 | -61.9583 | -61.9537 | 61.7477 | 61.7249 | 61.6928 | 61.6745
656.4844 | 123.6832 | -61.702 | 61.8988 | 0.24743 | 0.0060595 | -0.018046 | 0.025624 | -0.0047379 | 0.00029581 | -0.012447 | 0.22218 | 0.023657 | 0.0080074 | -0.024597 | -0.0147 | 0.013843 | -0.013474 | -0.050354 | 0.10986 | -0.10529 | 0.036621 | 0.13275 | 0.027466 | 0.07782 | -0.064087 | 0.15106 | -0.09613 | -0.045776 | -0.013733 | -0.022888 | 0.009155 | 61.5967 | -61.7889 | -61.8622 | 61.8347 | 61.7798 | 61.7294 | 0.18311 | 0.13275 | 61.6058 | -61.7477 | -61.9446 | 61.6882 | 61.7111 | 61.6791 | 0.10528 | 0.073242 | 0.23804 | 0.14191 | 0.082397 | 0.050354 | 0.21515 | 0.24719 | 61.8118 | 61.853 | -62.0041 | -61.9949 | 61.7386 | 61.6562 | 61.6516 | 61.6379
657.4844 | 123.6923 | -61.7386 | 61.8988 | 0.0032924 | 0.011401 | -0.0073647 | 0.033101 | 0.0080791 | 0.0035008 | -0.0081744 | -0.082994 | 0.01618 | 0.010143 | -0.020325 | -0.022176 | 0.025593 | 0.0025485 | -0.027466 | 0.09613 | -0.11444 | 0.050354 | 0.13733 | 0.013733 | 0.059509 | -0.086975 | 0.14191 | -0.091553 | -0.036621 | -0.022888 | -0.050354 | 0.013733 | 61.6241 | -61.8027 | -61.8484 | 61.8759 | 61.7981 | 61.7523 | 0.17395 | 0.12817 | 61.647 | -61.7569 | -61.9354 | 61.7157 | 61.7523 | 61.6882 | 0.10529 | 0.041199 | 0.25177 | 0.16479 | 0.068665 | 0.054932 | 0.21057 | 0.23346 | 61.8347 | 61.8805 | -62.0132 | -61.9904 | 61.7889 | 61.702 | 61.7111 | 61.6516
658.4844 | 123.7061 | -61.702 | 61.8988 | 0.12536 | 0.0081955 | -0.012706 | 0.009602 | -0.013283 | -0.016794 | -0.00069841 | 0.22218 | 0.0097714 | 0.015483 | -0.032074 | -0.0093592 | 0.014911 | -0.010269 | -0.041199 | 0.10986 | -0.11444 | 0.059509 | 0.15106 | 0.022888 | 0.082397 | -0.073242 | 0.16937 | -0.086975 | -0.036621 | 0 | -0.022888 | 0.013733 | 61.5875 | -61.7889 | -61.8393 | 61.853 | 61.7844 | 61.7249 | 0.19684 | 0.13733 | 61.615 | -61.7294 | -61.9354 | 61.702 | 61.7157 | 61.6791 | 0.10071 | 0.064087 | 0.2655 | 0.17395 | 0.086975 | 0.050354 | 0.2243 | 0.25635 | 61.8118 | 61.8713 | -62.0132 | -61.9858 | 61.7615 | 61.6653 | 61.6608 | 61.6287
659.4844 | 123.6786 | -61.7157 | 61.9354 | 0.049069 | 0.0071275 | -0.0030927 | 0.018147 | 0.019829 | 0.00029581 | 0.0046426 | 0.13063 | 0.026861 | 0.0048024 | -0.032074 | -0.0082912 | 0.0074349 | -0.0027915 | -0.041199 | 0.10071 | -0.10986 | 0.036621 | 0.1236 | 0.027466 | 0.07782 | -0.082397 | 0.16022 | -0.10529 | -0.032043 | 0.009155 | -0.013733 | 0.022888 | 61.6058 | -61.8347 | -61.8988 | 61.8393 | 61.7935 | 61.7432 | 0.18768 | 0.13733 | 61.6104 | -61.7752 | -61.9675 | 61.7249 | 61.7386 | 61.702 | 0.12817 | 0.091553 | 0.23346 | 0.14648 | 0.11444 | 0.073243 | 0.21057 | 0.2655 | 61.8164 | 61.8759 | -62.0453 | -62.0407 | 61.7523 | 61.6837 | 61.6745 | 61.6333
660.4844 | 123.7381 | -61.6699 | 61.9263 | 0.1101 | 0.018878 | -0.0095007 | 0.025624 | 0.0048751 | 0.0056368 | -0.019924 | -0.0066996 | 0.023657 | 0.0069384 | -0.0043033 | -0.017904 | 0.020252 | -0.0049285 | 0.009155 | 0.09613 | -0.10529 | 0 | 0.064087 | -0.027466 | 0.041199 | 0.004578 | 0.15106 | -0.086975 | 0.027466 | 0.059509 | 0.018311 | 0.064087 | 61.5646 | -61.8301 | -61.9263 | 61.734 | 61.7111 | 61.6425 | 0.14649 | 0.07782 | 61.5829 | -61.7752 | -61.8988 | 61.7294 | 61.734 | 61.6882 | 0.15106 | 0.10529 | 0.16937 | 0.10529 | 0.14648 | 0.11444 | 0.20142 | 0.23804 | 61.7661 | 61.821 | -62.0316 | -62.0132 | 61.6699 | 61.6974 | 61.6791 | 61.6745
661.4844 | 123.6923 | -61.7065 | 61.908 | 0.12536 | 0.011401 | 0.0033163 | 0.017079 | 0.01342 | -0.0050442 | -0.00069841 | 0.19167 | 0.021521 | 0.012279 | -0.026734 | -0.013631 | 0.029865 | 0.0025485 | 0.013733 | 0.09613 | -0.09613 | -0.009155 | 0.091553 | -0.009155 | 0.041199 | -0.027466 | 0.14648 | -0.082397 | -0.032043 | 0.027466 | 0 | 0.009155 | 61.6104 | -61.8118 | -61.9171 | 61.7981 | 61.7477 | 61.6974 | 0.13733 | 0.086975 | 61.6241 | -61.7615 | -61.94 | 61.734 | 61.7157 | 61.7065 | 0.091552 | 0.082397 | 0.18768 | 0.086975 | 0.10986 | 0.050354 | 0.19226 | 0.22888 | 61.8027 | 61.853 | -62.0041 | -61.9904 | 61.6974 | 61.6745 | 61.7203 | 61.6791
662.4844 | 123.7152 | -61.702 | 61.8851 | 0.018551 | 0.016741 | -0.0073647 | 0.012807 | 0.0059431 | -0.0061122 | -0.014583 | 0.10011 | 0.020452 | 0.014415 | 0.0085137 | -0.018972 | 0.019184 | -0.023087 | 0 | 0.086975 | -0.10071 | 0.013733 | 0.082397 | 0.004578 | 0.045776 | -0.004578 | 0.14191 | -0.07782 | -0.004578 | 0.018311 | -0.018311 | 0.032043 | 61.6013 | -61.7981 | -61.8713 | 61.7844 | 61.7477 | 61.7065 | 0.14648 | 0.10529 | 61.6241 | -61.7432 | -61.8896 | 61.7203 | 61.734 | 61.6837 | 0.10986 | 0.059509 | 0.18311 | 0.11444 | 0.096131 | 0.073242 | 0.18768 | 0.21973 | 61.7889 | 61.8439 | -61.9858 | -61.9629 | 61.7157 | 61.6974 | 61.702 | 61.6974
663.4844 | 123.7701 | -61.6745 | 61.8759 | 0.079586 | 0.015673 | -0.01057 | 0.020283 | 0.017693 | 0.0056368 | 0.0025066 | 0.49684 | 0.00015838 | 0.012279 | -0.035279 | -0.021108 | 0.019184 | -0.0059965 | 0.032043 | 0.073242 | -0.073242 | -0.082397 | 0 | -0.07782 | -0.018311 | 0.045776 | 0.15106 | -0.059509 | 0.036621 | 0.09613 | 0.073242 | 0.07782 | 61.6013 | -61.8027 | -61.9583 | 61.6745 | 61.6562 | 61.5967 | 0.054931 | -0.004578 | 61.615 | -61.7249 | -61.8393 | 61.7706 | 61.7523 | 61.7477 | 0.13733 | 0.13275 | 0.073242 | -0.009155 | 0.15564 | 0.09613 | 0.14648 | 0.21057 | 61.7477 | 61.8256 | -61.9492 | -61.9354 | 61.5921 | 61.7111 | 61.7065 | 61.7203
664.4844 | 123.7152 | -61.7203 | 61.9034 | 0.17114 | 0.010333 | -0.0030927 | 0.024556 | -0.0015339 | -0.019998 | 0.0057106 | 0.29848 | 0.020452 | 0.013347 | -0.023529 | -0.026449 | 0.013843 | -0.0038605 | 0.027466 | 0.068665 | -0.10071 | -0.050354 | 0.054932 | -0.041199 | 0.013733 | 0.004578 | 0.14191 | -0.091553 | 0 | 0.027466 | 0.004578 | 0.045776 | 61.6196 | -61.8347 | -61.9537 | 61.7752 | 61.734 | 61.6791 | 0.11444 | 0.059509 | 61.6287 | -61.7615 | -61.9034 | 61.7477 | 61.7661 | 61.7249 | 0.13733 | 0.096131 | 0.15564 | 0.050354 | 0.11902 | 0.091553 | 0.16937 | 0.23346 | 61.7889 | 61.8622 | -62.0041 | -61.9949 | 61.6699 | 61.7203 | 61.7477 | 61.7249
665.4844 | 123.7564 | -61.7249 | 61.9125 | 0.14062 | 0.0092645 | -0.012706 | 0.026692 | 0.0048751 | -0.0071802 | -0.0017664 | 0.069594 | 0.012976 | -0.01122 | 0.015991 | -0.025381 | 0.019184 | -0.019882 | -0.036621 | 0.10071 | -0.11444 | 0.032043 | 0.12817 | 0.018311 | 0.073242 | -0.050354 | 0.15106 | -0.10529 | 0 | 0.054932 | 0 | 0.068665 | 61.6104 | -61.8118 | -61.8805 | 61.853 | 61.7981 | 61.7432 | 0.18768 | 0.13275 | 61.6196 | -61.7615 | -61.9125 | 61.7798 | 61.7935 | 61.7249 | 0.17395 | 0.10529 | 0.24262 | 0.14648 | 0.16022 | 0.10529 | 0.21515 | 0.25635 | 61.8256 | 61.8759 | -62.027 | -62.0178 | 61.7569 | 61.7249 | 61.6882 | 61.6745
666.4844 | 123.8297 | -61.6699 | 61.8988 | 0.12536 | 0.014605 | -0.00095673 | 0.018147 | -0.0015339 | -0.0018402 | -0.0049704 | 0.48158 | 0.018316 | 0.0080074 | -0.0021673 | -0.017904 | 0.0095709 | 0.022842 | 0.045776 | 0.068665 | -0.064087 | -0.13733 | -0.059509 | -0.13275 | -0.059509 | 0.11444 | 0.11902 | -0.064087 | 0.07782 | 0.15106 | 0.13275 | 0.11902 | 61.6058 | -61.8301 | -62.0361 | 61.6104 | 61.6104 | 61.5372 | 0.004578 | -0.068664 | 61.6058 | -61.7798 | -61.821 | 61.821 | 61.7889 | 61.8027 | 0.18311 | 0.19684 | 0.004578 | -0.073242 | 0.21515 | 0.14191 | 0.13275 | 0.18311 | 61.7386 | 61.7889 | -61.9629 | -61.9629 | 61.5326 | 61.7477 | 61.7157 | 61.7844
667.4844 | 123.8434 | -61.6699 | 61.8805 | 0.094845 | 0.019946 | -0.0073647 | 0.02242 | 0.0080791 | 0.00029581 | 0.0025066 | 0.26796 | 0.0054994 | -0.0026746 | -0.018189 | -0.028585 | 0.018116 | 0.0057535 | 0.027466 | 0.064087 | -0.064087 | -0.10986 | -0.041199 | -0.10529 | -0.068665 | 0.09613 | 0.11902 | -0.068665 | 0.091553 | 0.16479 | 0.15564 | 0.12817 | 61.6058 | -61.8164 | -61.9904 | 61.6287 | 61.6013 | 61.5646 | -0.004578 | -0.041199 | 61.6013 | -61.7615 | -61.7889 | 61.8347 | 61.7981 | 61.8256 | 0.19684 | 0.22431 | 0.022888 | -0.045776 | 0.23346 | 0.16022 | 0.12817 | 0.18768 | 61.734 | 61.7889 | -61.9446 | -61.9492 | 61.5601 | 61.7615 | 61.6974 | 61.7661
668.4844 | 123.8342 | -61.6745 | 61.8622 | 0.064327 | 0.0060595 | 0.0043843 | 0.026692 | 0.0027391 | -0.0093172 | -0.011379 | 0.31374 | 0.012976 | 0.0090754 | -0.0064393 | -0.028585 | 0.022388 | -0.018814 | 0.041199 | 0.054932 | -0.064087 | -0.12817 | -0.068665 | -0.12817 | -0.041199 | 0.10986 | 0.10986 | -0.050354 | 0.082397 | 0.15564 | 0.14191 | 0.12817 | 61.6104 | -61.8073 | -61.9904 | 61.6058 | 61.6333 | 61.5463 | 0.022888 | -0.064087 | 61.6241 | -61.7523 | -61.7798 | 61.8301 | 61.8027 | 61.8164 | 0.17853 | 0.19226 | -0.004578 | -0.064087 | 0.20599 | 0.13275 | 0.11902 | 0.16022 | 61.7294 | 61.7844 | -61.9263 | -61.9125 | 61.5463 | 61.7569 | 61.7157 | 61.7844
669.4844 | 123.8663 | -61.6699 | 61.8668 | 0.14062 | 0.012469 | -0.012706 | 0.013875 | 0.015556 | -0.00077219 | -0.016719 | 0.39003 | 0.012976 | 0.00053042 | -0.022461 | -0.025381 | 0.0074349 | 0.0014805 | 0.032043 | 0.07782 | -0.064087 | -0.091553 | -0.041199 | -0.10529 | -0.059509 | 0.11444 | 0.10986 | -0.050354 | 0.10529 | 0.16937 | 0.15564 | 0.13275 | 61.6058 | -61.7889 | -61.9583 | 61.6287 | 61.6104 | 61.5646 | 0.004578 | -0.041199 | 61.6196 | -61.7569 | -61.7615 | 61.8393 | 61.8027 | 61.8256 | 0.18311 | 0.20599 | 0.022888 | -0.027466 | 0.21973 | 0.15564 | 0.14191 | 0.16022 | 61.7477 | 61.7798 | -61.9308 | -61.9171 | 61.5784 | 61.7752 | 61.702 | 61.7844
670.4844 | 123.7015 | -61.7065 | 61.9171 | 0.1101 | 0.0092645 | -0.0095007 | 0.023488 | 0.0070111 | -0.01893 | 0.0025066 | 0.14589 | 0.015112 | 0.0058704 | -0.0053713 | -0.018972 | 0.011707 | 0.0014805 | -0.041199 | 0.09613 | -0.10071 | 0.050354 | 0.13733 | 0.022888 | 0.073242 | -0.068665 | 0.16937 | -0.10529 | -0.032043 | -0.004578 | -0.013733 | 0.013733 | 61.6058 | -61.821 | -61.8668 | 61.8439 | 61.7798 | 61.7294 | 0.17395 | 0.1236 | 61.6013 | -61.7477 | -61.9492 | 61.702 | 61.7203 | 61.6928 | 0.11902 | 0.091553 | 0.23804 | 0.15106 | 0.10071 | 0.073243 | 0.19684 | 0.27466 | 61.8027 | 61.8759 | -62.0178 | -62.0224 | 61.7569 | 61.6745 | 61.6653 | 61.6379
671.4844 | 123.8525 | -61.6882 | 61.8713 | 0.079586 | 0.014605 | -0.01057 | 0.028828 | -0.0090099 | -0.02427 | -0.0081744 | 0.26796 | 0.0076354 | 0.0058704 | -0.024597 | -0.016836 | 0.022388 | 0.0014805 | 0.018311 | 0.07782 | -0.073242 | -0.09613 | -0.041199 | -0.15106 | -0.059509 | 0.14191 | 0.11444 | -0.054932 | 0.10529 | 0.17395 | 0.1236 | 0.11902 | 61.615 | -61.7935 | -61.9675 | 61.647 | 61.6287 | 61.5372 | 0.013733 | -0.07782 | 61.6333 | -61.7569 | -61.7661 | 61.8622 | 61.8073 | 61.8118 | 0.17395 | 0.17853 | 0.032043 | -0.022888 | 0.22888 | 0.16022 | 0.15106 | 0.16937 | 61.7661 | 61.8027 | -61.9446 | -61.9263 | 61.5921 | 61.7935 | 61.7065 | 61.8301
672.4844 | 123.8297 | -61.6653 | 61.8805 | 0.018551 | 0.010333 | -0.00095673 | 0.021352 | -0.0015339 | -0.0029082 | -0.019924 | 0.2527 | 0.021521 | -0.00053758 | -0.0032353 | -0.016836 | 0.0095709 | -0.010269 | 0.022888 | 0.086975 | -0.073242 | -0.086975 | -0.004578 | -0.10986 | -0.045776 | 0.086975 | 0.11902 | -0.073242 | 0.082397 | 0.14648 | 0.12817 | 0.10529 | 61.5921 | -61.7935 | -61.9675 | 61.6608 | 61.6196 | 61.5555 | 0.027466 | -0.036621 | 61.5921 | -61.7615 | -61.7981 | 61.8118 | 61.7706 | 61.7935 | 0.17853 | 0.20142 | 0.068664 | -0.013733 | 0.21973 | 0.15564 | 0.16022 | 0.19226 | 61.7523 | 61.7844 | -61.9537 | -61.9537 | 61.5784 | 61.7477 | 61.6882 | 61.7523
673.4844 | 123.8113 | -61.6653 | 61.8896 | 0.12536 | 0.012469 | -0.0073647 | 0.02776 | 0.024101 | -0.011453 | -0.0017664 | 0.22218 | 0.025793 | 0.0037344 | 0.0085137 | -0.018972 | 0.024524 | -0.0059965 | 0.036621 | 0.064087 | -0.068665 | -0.10529 | -0.018311 | -0.09613 | -0.036621 | 0.09613 | 0.1236 | -0.050354 | 0.086975 | 0.14191 | 0.11902 | 0.10986 | 61.5967 | -61.8256 | -61.9949 | 61.647 | 61.6287 | 61.5692 | 0.032044 | -0.027465 | 61.615 | -61.7661 | -61.8027 | 61.8073 | 61.7752 | 61.7844 | 0.16022 | 0.16937 | 0.050354 | -0.036621 | 0.19226 | 0.13733 | 0.13275 | 0.17395 | 61.7294 | 61.7889 | -61.9583 | -61.94 | 61.5601 | 61.7523 | 61.702 | 61.7615
674.4844 | 123.7839 | -61.6974 | 61.853 | 0.079586 | 0.018878 | 0.0022483 | 0.017079 | 0.0048751 | 0.016318 | -0.018856 | 0.19167 | 0.020452 | -0.0090826 | -0.026734 | -0.016836 | 0.013843 | -0.016678 | -0.018311 | 0.082397 | -0.082397 | -0.045776 | 0.054932 | -0.064087 | -0.004578 | -0.004578 | 0.11902 | -0.07782 | 0.036621 | 0.073242 | 0.054932 | 0.068665 | 61.615 | -61.7706 | -61.8988 | 61.7523 | 61.6928 | 61.6333 | 0.077819 | 0.01831 | 61.6196 | -61.734 | -61.8164 | 61.7706 | 61.7661 | 61.7523 | 0.14649 | 0.13275 | 0.13733 | 0.036621 | 0.15106 | 0.11444 | 0.16479 | 0.19684 | 61.7798 | 61.8164 | -61.9354 | -61.9308 | 61.6516 | 61.734 | 61.6791 | 61.6928
675.4844 | 123.7793 | -61.702 | 61.8759 | 0.064327 | 0.014605 | -0.0073647 | 0.030965 | 0.0006031 | 0.0067048 | -0.026332 | 0.13063 | 0.012976 | -0.01122 | -0.031006 | -0.026449 | 0.0074349 | -0.0038605 | -0.004578 | 0.07782 | -0.086975 | -0.036621 | 0.041199 | -0.041199 | -0.018311 | 0 | 0.10986 | -0.07782 | 0.050354 | 0.082397 | 0.064087 | 0.068665 | 61.615 | -61.7981 | -61.9125 | 61.7432 | 61.6837 | 61.6608 | 0.068664 | 0.045776 | 61.6241 | -61.7661 | -61.8256 | 61.7844 | 61.7706 | 61.7661 | 0.14649 | 0.14191 | 0.12817 | 0.050354 | 0.16022 | 0.12817 | 0.16479 | 0.18768 | 61.7798 | 61.8118 | -61.9629 | -61.9537 | 61.6653 | 61.7523 | 61.6974 | 61.702
676.4844 | 123.8663 | -61.647 | 61.8713 | 0.03381 | 0.019946 | -0.0062967 | 0.028828 | 0.0048751 | -0.015725 | -0.0081744 | 0.20692 | 0.014044 | 0.0048024 | -0.021393 | -0.024313 | 0.01598 | 0.0025485 | 0.032043 | 0.082397 | -0.082397 | -0.11902 | -0.022888 | -0.11444 | -0.064087 | 0.082397 | 0.10986 | -0.045776 | 0.09613 | 0.17853 | 0.14648 | 0.13733 | 61.5646 | -61.7889 | -61.9904 | 61.6241 | 61.5829 | 61.5326 | 0.01831 | -0.032044 | 61.6013 | -61.7615 | -61.7752 | 61.8256 | 61.7844 | 61.7935 | 0.18311 | 0.19226 | 0.059509 | -0.036622 | 0.2243 | 0.14191 | 0.16479 | 0.15564 | 61.7294 | 61.7569 | -61.9537 | -61.9171 | 61.528 | 61.7432 | 61.6791 | 61.7294
677.4844 | 123.7839 | -61.6974 | 61.8576 | 0.0032924 | 0.0092645 | -0.0052287 | 0.014943 | -0.0015339 | -0.0029082 | -0.0049704 | 0.069594 | 0.010839 | 0.0058704 | 0.024536 | -0.0147 | 0.02132 | 0.00041246 | -0.013733 | 0.041199 | -0.068665 | -0.059509 | 0.041199 | -0.059509 | -0.032043 | -0.009155 | 0.11902 | -0.082397 | 0.032043 | 0.059509 | 0.036621 | 0.07782 | 61.6287 | -61.8164 | -61.9171 | 61.7386 | 61.6653 | 61.6379 | 0.036622 | 0.009156 | 61.615 | -61.7386 | -61.8256 | 61.7569 | 61.7752 | 61.734 | 0.16022 | 0.11902 | 0.10986 | 0.009156 | 0.14191 | 0.11444 | 0.10986 | 0.20142 | 61.7386 | 61.8164 | -61.9263 | -61.94 | 61.6379 | 61.7294 | 61.6837 | 61.6882
678.4844 | 123.7885 | -61.7065 | 61.8805 | 0.079586 | 0.012469 | -0.0041607 | 0.024556 | 0.01342 | -0.00077219 | -0.011379 | 0.14589 | 0.020452 | 0.0026664 | 0.014923 | -0.016836 | 0.02132 | -0.0038605 | -0.009155 | 0.064087 | -0.073242 | -0.045776 | 0.050354 | -0.050354 | -0.013733 | -0.009155 | 0.1236 | -0.091553 | 0.045776 | 0.064087 | 0.068665 | 0.073242 | 61.6333 | -61.8164 | -61.9263 | 61.7569 | 61.6928 | 61.6562 | 0.059509 | 0.022888 | 61.615 | -61.7569 | -61.8347 | 61.7706 | 61.7798 | 61.7752 | 0.16479 | 0.16022 | 0.1236 | 0.027466 | 0.15564 | 0.13733 | 0.13733 | 0.21515 | 61.7706 | 61.8301 | -61.9537 | -61.972 | 61.6608 | 61.7523 | 61.6974 | 61.6974
679.4844 | 123.8251 | -61.6791 | 61.8576 | 0.1101 | 0.017809 | -0.0095007 | 0.032033 | 0.011284 | -0.0018402 | -0.0071064 | 0.2527 | 0.014044 | 0.0015984 | -0.035279 | -0.013631 | 0.012775 | -0.012405 | 0.027466 | 0.054932 | -0.07782 | -0.086975 | -0.009155 | -0.091553 | -0.050354 | 0.09613 | 0.11444 | -0.073242 | 0.10529 | 0.1236 | 0.14191 | 0.15564 | 61.6013 | -61.8027 | -61.9446 | 61.6699 | 61.6287 | 61.5875 | 0.027466 | -0.013733 | 61.6058 | -61.7432 | -61.7523 | 61.8027 | 61.8347 | 61.821 | 0.22888 | 0.21515 | 0.068665 | -0.009155 | 0.19684 | 0.17853 | 0.13275 | 0.18768 | 61.734 | 61.7935 | -61.9354 | -61.9308 | 61.5921 | 61.7844 | 61.7065 | 61.7752
680.4844 | 123.7885 | -61.6745 | 61.8439 | 0.0032924 | 0.014605 | 0.00011227 | 0.02242 | -0.012215 | -0.016794 | -0.017787 | 0.16115 | 0.019384 | -0.0058786 | -0.0021673 | -0.022176 | 0.020252 | -0.022018 | 0.027466 | 0.064087 | -0.064087 | -0.10986 | -0.027466 | -0.10529 | -0.032043 | 0.073242 | 0.1236 | -0.045776 | 0.07782 | 0.082397 | 0.082397 | 0.091553 | 61.6104 | -61.7798 | -61.9537 | 61.647 | 61.6425 | 61.5692 | 0.032044 | -0.041199 | 61.6287 | -61.7203 | -61.7661 | 61.7569 | 61.7661 | 61.7569 | 0.13733 | 0.12817 | 0.036621 | -0.045776 | 0.12817 | 0.1236 | 0.12817 | 0.16937 | 61.7386 | 61.7981 | -61.908 | -61.8896 | 61.5646 | 61.7523 | 61.702 | 61.7477
681.4844 | 123.8205 | -61.6791 | 61.8576 | 0.064327 | 0.0071275 | -0.0041607 | 0.018147 | 0.0016711 | 0.0045688 | -0.020992 | 0.084853 | 0.0044314 | -0.010151 | -0.0075083 | -0.023245 | 0.030933 | 0.0025485 | 0.050354 | 0.059509 | -0.064087 | -0.10986 | -0.032043 | -0.10986 | -0.050354 | 0.10071 | 0.10529 | -0.059509 | 0.082397 | 0.10986 | 0.082397 | 0.10986 | 61.615 | -61.7981 | -61.9675 | 61.647 | 61.6287 | 61.5692 | 0.013733 | -0.045776 | 61.6196 | -61.7523 | -61.7752 | 61.7889 | 61.7889 | 61.7615 | 0.16937 | 0.14191 | 0.032044 | -0.045776 | 0.16937 | 0.14191 | 0.1236 | 0.16479 | 61.7386 | 61.7844 | -61.9217 | -61.9171 | 61.5692 | 61.7615 | 61.7294 | 61.7798
682.4844 | 123.8342 | -61.6928 | 61.853 | 0.0032924 | 0.012469 | -0.0062967 | 0.028828 | 0.0059431 | 0.0099088 | -0.0017664 | 0.11537 | 0.021521 | -0.0058786 | -0.025666 | -0.022176 | 0.011707 | 0.0078895 | 0.018311 | 0.068665 | -0.073242 | -0.086975 | 0.004578 | -0.10071 | -0.045776 | 0.064087 | 0.10529 | -0.07782 | 0.091553 | 0.14191 | 0.11444 | 0.1236 | 61.6196 | -61.7844 | -61.94 | 61.6974 | 61.647 | 61.5921 | 0.027466 | -0.027466 | 61.615 | -61.7477 | -61.7615 | 61.8347 | 61.8164 | 61.8073 | 0.20142 | 0.19226 | 0.07782 | -0.013733 | 0.21973 | 0.16937 | 0.14191 | 0.18311 | 61.7615 | 61.7981 | -61.9263 | -61.9308 | 61.6058 | 61.7844 | 61.7111 | 61.7569
683.4844 | 123.7839 | -61.6928 | 61.8393 | 0.03381 | 0.019946 | 0.00011227 | 0.01067 | -0.0079419 | 0.00029581 | -0.0049704 | 0.069594 | 0.014044 | 0.0037344 | 0.0010367 | -0.017904 | 0.019184 | -0.022018 | 0.018311 | 0.050354 | -0.064087 | -0.10071 | -0.009155 | -0.09613 | -0.059509 | 0.073242 | 0.09613 | -0.064087 | 0.09613 | 0.1236 | 0.082397 | 0.10071 | 61.6287 | -61.7889 | -61.94 | 61.6837 | 61.6333 | 61.5967 | 0.004578 | -0.032043 | 61.6287 | -61.7432 | -61.7432 | 61.8164 | 61.7935 | 61.7752 | 0.1648 | 0.14648 | 0.054932 | -0.036621 | 0.18768 | 0.16022 | 0.11444 | 0.16022 | 61.7432 | 61.7889 | -61.9034 | -61.9034 | 61.5921 | 61.7889 | 61.7111 | 61.7661
684.4844 | 123.793 | -61.6882 | 61.8759 | -0.073002 | 0.0092645 | -0.0041607 | 0.02776 | 0.0091481 | -0.00077219 | -0.0071064 | 0.023818 | 0.014044 | -0.010151 | -0.0064393 | -0.016836 | 0.014911 | -0.0070645 | 0.009155 | 0.059509 | -0.068665 | -0.082397 | 0 | -0.073242 | -0.022888 | 0.022888 | 0.10986 | -0.059509 | 0.059509 | 0.082397 | 0.068665 | 0.082397 | 61.6196 | -61.8164 | -61.9583 | 61.6882 | 61.6653 | 61.615 | 0.045777 | -0.004577 | 61.6287 | -61.7661 | -61.8164 | 61.7706 | 61.7706 | 61.7569 | 0.14191 | 0.12817 | 0.068665 | -0.013732 | 0.14191 | 0.11902 | 0.12817 | 0.16937 | 61.7477 | 61.7981 | -61.9446 | -61.9354 | 61.6058 | 61.7477 | 61.6974 | 61.7111
685.4844 | 123.8571 | -61.6928 | 61.8759 | 0.064327 | 0.014605 | -0.0041607 | 0.021352 | -0.013283 | -0.013589 | -0.0049704 | 0.13063 | 0.024725 | -0.0048106 | -0.026734 | -0.017904 | 0.01598 | -0.011337 | 0.027466 | 0.068665 | -0.068665 | -0.082397 | 0.004578 | -0.09613 | -0.036621 | 0.07782 | 0.14191 | -0.064087 | 0.09613 | 0.11902 | 0.11444 | 0.10986 | 61.6241 | -61.8073 | -61.9583 | 61.6974 | 61.6562 | 61.5967 | 0.032044 | -0.027465 | 61.6287 | -61.734 | -61.7798 | 61.8118 | 61.8027 | 61.8073 | 0.17395 | 0.17853 | 0.073243 | -0.013732 | 0.18311 | 0.16022 | 0.13733 | 0.20599 | 61.7615 | 61.8347 | -61.9446 | -61.94 | 61.6104 | 61.7889 | 61.7203 | 61.7706
686.4844 | 123.7976 | -61.6974 | 61.8622 | 0.079586 | 0.016741 | 0.0043843 | 0.021352 | 0.0027391 | -0.0093172 | -0.0028344 | 0.10011 | 0.018316 | 0.0048024 | -0.0096443 | -0.028585 | 0.011707 | -0.00065554 | 0.032043 | 0.059509 | -0.064087 | -0.09613 | -0.013733 | -0.086975 | -0.045776 | 0.07782 | 0.10529 | -0.054932 | 0.09613 | 0.086975 | 0.068665 | 0.10529 | 61.6333 | -61.8027 | -61.9583 | 61.6837 | 61.6516 | 61.6104 | 0.018311 | -0.022888 | 61.6425 | -61.7569 | -61.7661 | 61.7844 | 61.8027 | 61.7661 | 0.16022 | 0.1236 | 0.050354 | -0.032043 | 0.14191 | 0.15106 | 0.1236 | 0.16022 | 61.7569 | 61.8027 | -61.9263 | -61.9171 | 61.6013 | 61.7935 | 61.7294 | 61.7752
687.4844 | 123.8297 | -61.6928 | 61.853 | 0.049069 | 0.024218 | 0.0022483 | 0.034169 | -0.013283 | -0.0039762 | -0.0071064 | -0.067735 | 0.01618 | -0.0026746 | -0.021393 | -0.0147 | 0.023456 | -0.017746 | 0.045776 | 0.064087 | -0.064087 | -0.091553 | -0.018311 | -0.09613 | -0.064087 | 0.064087 | 0.1236 | -0.07782 | 0.11902 | 0.1236 | 0.082397 | 0.11902 | 61.6287 | -61.7889 | -61.9446 | 61.6745 | 61.6287 | 61.5967 | 0 | -0.032043 | 61.615 | -61.7294 | -61.734 | 61.8164 | 61.8118 | 61.7752 | 0.19684 | 0.16022 | 0.045776 | -0.027466 | 0.20142 | 0.19684 | 0.12817 | 0.20142 | 61.7569 | 61.8164 | -61.9171 | -61.9308 | 61.6013 | 61.8118 | 61.7386 | 61.7569
688.4844 | 123.7015 | -61.7294 | 61.8988 | 0.1864 | 0.013537 | -0.0095007 | 0.025624 | -0.010078 | -0.0018402 | 0.0089146 | 0.084853 | 0.020452 | -0.0016066 | 0.0010367 | -0.015768 | 0.01598 | -0.013474 | -0.009155 | 0.086975 | -0.09613 | 0.009155 | 0.086975 | -0.009155 | 0.059509 | -0.064087 | 0.15564 | -0.086975 | -0.027466 | 0.018311 | -0.013733 | 0.009155 | 61.6333 | -61.8118 | -61.8896 | 61.8164 | 61.7889 | 61.7203 | 0.15564 | 0.086975 | 61.6425 | -61.7432 | -61.9263 | 61.7477 | 61.7386 | 61.7157 | 0.09613 | 0.073242 | 0.1831 | 0.10528 | 0.10529 | 0.059509 | 0.1831 | 0.24261 | 61.8164 | 61.8851 | -61.9949 | -61.9858 | 61.7386 | 61.702 | 61.7203 | 61.6653
689.4844 | 123.8297 | -61.6837 | 61.8256 | 0.03381 | 0.019946 | 0.0086563 | 0.030965 | -0.0015339 | -0.013589 | -0.0092424 | -0.067735 | 0.015112 | 0.00053042 | -0.0010993 | -0.018972 | 0.022388 | -0.00065554 | 0.045776 | 0.059509 | -0.064087 | -0.11444 | -0.032043 | -0.10529 | -0.054932 | 0.07782 | 0.091553 | -0.064087 | 0.10071 | 0.11902 | 0.091553 | 0.10986 | 61.6196 | -61.7661 | -61.94 | 61.6516 | 61.6287 | 61.5784 | 0.009155 | -0.041199 | 61.6196 | -61.734 | -61.7249 | 61.8027 | 61.7935 | 61.7752 | 0.17395 | 0.15564 | 0.032044 | -0.050354 | 0.18311 | 0.1648 | 0.1236 | 0.15564 | 61.7432 | 61.7752 | -61.8896 | -61.8896 | 61.5692 | 61.7844 | 61.7294 | 61.7615
690.4844 | 123.8434 | -61.6837 | 61.8301 | 0.079586 | 0.010333 | 0.0011803 | 0.02242 | 0.012352 | -0.0050442 | 0.0046426 | 0.039077 | 0.011908 | 0.0048024 | 0.0031737 | -0.027517 | 0.013843 | 0.0014805 | 0.045776 | 0.050354 | -0.091553 | -0.10986 | -0.013733 | -0.10986 | -0.068665 | 0.082397 | 0.11444 | -0.054932 | 0.11444 | 0.11902 | 0.073242 | 0.11444 | 61.5921 | -61.7798 | -61.94 | 61.6699 | 61.615 | 61.5738 | 0.022888 | -0.01831 | 61.6287 | -61.7157 | -61.7157 | 61.8027 | 61.7981 | 61.7569 | 0.16937 | 0.12817 | 0.07782 | -0.01831 | 0.17395 | 0.16937 | 0.14191 | 0.16937 | 61.734 | 61.7981 | -61.9217 | -61.8851 | 61.5738 | 61.7981 | 61.7294 | 61.7661
691.4844 | 123.7244 | -61.6928 | 61.8942 | 0.03381 | 0.016741 | -0.0073647 | 0.020283 | 0.021965 | 0.0067048 | -0.012447 | 0.14589 | 0.0065674 | 0.0080074 | 0.0010367 | -0.0040182 | 0.0042299 | -0.024155 | 0.041199 | 0.064087 | -0.07782 | -0.064087 | 0.022888 | -0.073242 | 0 | 0.018311 | 0.13275 | -0.082397 | 0.013733 | 0.054932 | 0.045776 | 0.050354 | 61.615 | -61.8301 | -61.9583 | 61.7157 | 61.6928 | 61.6196 | 0.07782 | 0.004578 | 61.6104 | -61.7615 | -61.8805 | 61.7477 | 61.7432 | 61.7386 | 0.13275 | 0.12817 | 0.10071 | 0.013733 | 0.13733 | 0.09613 | 0.14191 | 0.21515 | 61.7569 | 61.8256 | -61.972 | -61.9766 | 61.6287 | 61.7065 | 61.734 | 61.7111
692.4844 | 123.8022 | -61.7111 | 61.8439 | -0.042484 | 0.017809 | -0.0020247 | 0.020283 | -0.0047379 | -0.0018402 | -0.0060384 | 0.069594 | 0.022589 | 0.0058704 | -0.024597 | -0.0147 | 0.01598 | -0.013474 | 0.027466 | 0.064087 | -0.050354 | -0.11444 | -0.032043 | -0.10529 | -0.050354 | 0.086975 | 0.10986 | -0.068665 | 0.09613 | 0.11902 | 0.07782 | 0.10986 | 61.6608 | -61.7798 | -61.9583 | 61.6791 | 61.6608 | 61.6058 | 0 | -0.054932 | 61.6425 | -61.734 | -61.7477 | 61.8301 | 61.821 | 61.7889 | 0.17853 | 0.14649 | 0.018311 | -0.064087 | 0.18768 | 0.16479 | 0.11444 | 0.17853 | 61.7752 | 61.821 | -61.8942 | -61.9125 | 61.5967 | 61.8073 | 61.7386 | 61.7981
693.4844 | 123.8113 | -61.6882 | 61.8668 | -0.10352 | 0.0081955 | -0.0030927 | 0.025624 | 0.0070111 | -0.0093172 | -0.0060384 | 0.069594 | 0.019384 | -0.00053758 | -0.013916 | -0.02004 | 0.013843 | 0.011093 | 0.036621 | 0.036621 | -0.045776 | -0.10986 | -0.036621 | -0.09613 | -0.050354 | 0.068665 | 0.10529 | -0.054932 | 0.10986 | 0.10529 | 0.07782 | 0.09613 | 61.6425 | -61.8301 | -61.9766 | 61.6516 | 61.6379 | 61.5921 | -0.004578 | -0.050354 | 61.6333 | -61.7615 | -61.7569 | 61.7935 | 61.7844 | 61.7661 | 0.15106 | 0.13275 | 0.009155 | -0.064087 | 0.16022 | 0.16479 | 0.082397 | 0.16022 | 61.7249 | 61.7935 | -61.9125 | -61.9217 | 61.5784 | 61.7981 | 61.7249 | 61.7569
694.4844 | 123.7839 | -61.6791 | 61.8759 | 0.049069 | 0.019946 | -0.0052287 | 0.020283 | 0.0070111 | -0.010385 | -0.0039024 | 0.10011 | 0.0044314 | -0.0069466 | -0.018189 | -0.026449 | 0.014911 | -0.0049285 | 0.041199 | 0.050354 | -0.07782 | -0.086975 | -0.022888 | -0.091553 | -0.027466 | 0.064087 | 0.1236 | -0.064087 | 0.045776 | 0.11444 | 0.091553 | 0.086975 | 61.6013 | -61.8256 | -61.9629 | 61.6562 | 61.6516 | 61.5875 | 0.050354 | -0.013733 | 61.615 | -61.7523 | -61.8301 | 61.7935 | 61.7661 | 61.7706 | 0.15106 | 0.15564 | 0.054932 | -0.009155 | 0.17853 | 0.10986 | 0.12817 | 0.18768 | 61.7294 | 61.8027 | -61.9537 | -61.94 | 61.5921 | 61.7249 | 61.7203 | 61.7432
695.4844 | 123.793 | -61.6928 | 61.8393 | -0.011967 | 0.011401 | -0.0041607 | 0.02776 | -0.0015339 | -0.01893 | -0.016719 | -0.067735 | 0.019384 | -0.00053758 | -3.1262e-05 | -0.023245 | 0.020252 | -0.0027915 | 0.027466 | 0.07782 | -0.068665 | -0.07782 | 0.013733 | -0.091553 | -0.036621 | 0.059509 | 0.10529 | -0.064087 | 0.10529 | 0.11444 | 0.086975 | 0.11902 | 61.6241 | -61.7615 | -61.9171 | 61.7065 | 61.6562 | 61.6013 | 0.032044 | -0.022888 | 61.6287 | -61.734 | -61.734 | 61.8073 | 61.8118 | 61.7798 | 0.18311 | 0.15106 | 0.082398 | -0.009155 | 0.17853 | 0.16937 | 0.14649 | 0.16937 | 61.7706 | 61.7981 | -61.908 | -61.9034 | 61.615 | 61.7981 | 61.7203 | 61.7523
696.4844 | 123.8342 | -61.6928 | 61.8393 | 0.064327 | 0.013537 | -0.0062967 | 0.026692 | 0.034782 | -0.012521 | -0.0081744 | 0.023818 | 0.014044 | 0.0015984 | -0.033142 | -0.022176 | 0.020252 | -0.012405 | 0.041199 | 0.036621 | -0.07782 | -0.10071 | -0.018311 | -0.10986 | -0.059509 | 0.064087 | 0.1236 | -0.082397 | 0.10986 | 0.11902 | 0.091553 | 0.1236 | 61.615 | -61.8027 | -61.94 | 61.6745 | 61.6333 | 61.5829 | 0.018311 | -0.032043 | 61.6104 | -61.7157 | -61.7294 | 61.8118 | 61.8164 | 61.7844 | 0.20599 | 0.17395 | 0.059509 | -0.022888 | 0.20142 | 0.19226 | 0.11444 | 0.20599 | 61.7294 | 61.8164 | -61.9171 | -61.9217 | 61.5921 | 61.8027 | 61.734 | 61.7569
697.4844 | 123.8068 | -61.6837 | 61.8851 | 0.14062 | 0.011401 | -0.0030927 | 0.020283 | 0.0027391 | -0.0093172 | -0.015651 | 0.16115 | 0.0097714 | 0.0090754 | -0.02887 | -0.026449 | 0.0095709 | 0.00041246 | 0.027466 | 0.064087 | -0.059509 | -0.12817 | -0.022888 | -0.10986 | -0.045776 | 0.073242 | 0.11444 | -0.068665 | 0.07782 | 0.1236 | 0.10986 | 0.11902 | 61.6241 | -61.821 | -62.0132 | 61.6608 | 61.6379 | 61.5738 | 0.013733 | -0.050354 | 61.615 | -61.7706 | -61.8073 | 61.8073 | 61.8027 | 61.7935 | 0.18768 | 0.17853 | 0.036621 | -0.068665 | 0.19226 | 0.14649 | 0.1236 | 0.18311 | 61.7477 | 61.7981 | -61.9446 | -61.9537 | 61.5555 | 61.7615 | 61.7111 | 61.7569
698.4844 | 123.793 | -61.702 | 61.8347 | 0.018551 | 0.0049915 | -0.0073647 | 0.020283 | -0.010078 | -0.017862 | -0.023128 | 0.10011 | 0.020452 | -0.01122 | 0.0095817 | -0.013631 | 0.01598 | -0.010269 | -0.009155 | 0.064087 | -0.064087 | -0.068665 | 0.032043 | -0.050354 | -0.013733 | 0.036621 | 0.1236 | -0.07782 | 0.045776 | 0.068665 | 0.054932 | 0.068665 | 61.6379 | -61.7706 | -61.9034 | 61.734 | 61.6882 | 61.6516 | 0.050354 | 0.013733 | 61.6241 | -61.7111 | -61.7889 | 61.7706 | 61.7706 | 61.7569 | 0.14649 | 0.13275 | 0.09613 | -0.004578 | 0.14649 | 0.1236 | 0.12817 | 0.20142 | 61.7661 | 61.8256 | -61.8988 | -61.9125 | 61.6333 | 61.7477 | 61.6928 | 61.7386
699.4844 | 123.8113 | -61.6928 | 61.8347 | 0.049069 | 0.011401 | -0.0041607 | 0.025624 | 0.0027391 | 0.0088408 | -0.019924 | 0.023818 | 0.014044 | -0.0026746 | -0.012848 | -0.022176 | 0.024524 | -0.0038605 | 0.022888 | 0.054932 | -0.050354 | -0.10529 | -0.041199 | -0.10071 | -0.050354 | 0.073242 | 0.10529 | -0.054932 | 0.10071 | 0.10529 | 0.082397 | 0.10529 | 61.6425 | -61.7798 | -61.94 | 61.6516 | 61.6425 | 61.5921 | 0 | -0.050354 | 61.6379 | -61.7294 | -61.734 | 61.7981 | 61.7981 | 61.7752 | 0.16022 | 0.13733 | 0.009155 | -0.054932 | 0.16022 | 0.15564 | 0.10529 | 0.16022 | 61.7477 | 61.7981 | -61.8851 | -61.8896 | 61.5875 | 61.7935 | 61.7157 | 61.7661
700.4844 | 123.8434 | -61.702 | 61.8851 | 0.079586 | 0.011401 | -0.0073647 | 0.02776 | -0.012215 | -0.0050442 | -0.013515 | 0.17641 | 0.014044 | 0.0090754 | -0.024597 | -0.018972 | 0.017048 | -0.024155 | 0.032043 | 0.054932 | -0.054932 | -0.11902 | -0.036621 | -0.10986 | -0.027466 | 0.10529 | 0.10529 | -0.064087 | 0.091553 | 0.14648 | 0.13733 | 0.11902 | 61.647 | -61.8301 | -62.0041 | 61.6653 | 61.6745 | 61.5921 | 0.027466 | -0.054931 | 61.6379 | -61.7798 | -61.7935 | 61.8484 | 61.821 | 61.8393 | 0.18311 | 0.20142 | 0.018311 | -0.064087 | 0.21057 | 0.15564 | 0.10986 | 0.16937 | 61.7569 | 61.8073 | -61.94 | -61.9492 | 61.5829 | 61.7935 | 61.734 | 61.8073
701.4844 | 123.8251 | -61.6928 | 61.8439 | 0.094845 | 0.021014 | -0.0073647 | 0.024556 | -0.0015339 | -0.013589 | 0.0067786 | 0.023818 | 0.015112 | 0.0090754 | -0.014984 | -0.018972 | 0.018116 | 0.01857 | 0.018311 | 0.068665 | -0.064087 | -0.10986 | -0.018311 | -0.10071 | -0.054932 | 0.07782 | 0.10986 | -0.064087 | 0.10071 | 0.10986 | 0.086975 | 0.10529 | 61.6287 | -61.7752 | -61.9537 | 61.6745 | 61.6379 | 61.5921 | 0.009155 | -0.036621 | 61.6287 | -61.734 | -61.7432 | 61.8027 | 61.7981 | 61.7798 | 0.16937 | 0.15106 | 0.045776 | -0.045776 | 0.17395 | 0.1648 | 0.13275 | 0.17395 | 61.7615 | 61.8027 | -61.908 | -61.908 | 61.5829 | 61.7935 | 61.7111 | 61.7706
702.4844 | 123.7976 | -61.6837 | 61.853 | -0.011967 | 0.015673 | 0.0022483 | 0.02242 | -0.0036699 | 0.0045688 | 0.0025066 | 0.039077 | 0.01618 | 0.011211 | -0.01178 | -0.02004 | 0.014911 | -0.014542 | 0.022888 | 0.059509 | -0.07782 | -0.07782 | -0.009155 | -0.07782 | -0.032043 | 0.041199 | 0.09613 | -0.073242 | 0.050354 | 0.068665 | 0.059509 | 0.086975 | 61.6058 | -61.7935 | -61.9308 | 61.6745 | 61.6516 | 61.6058 | 0.045777 | 0 | 61.6104 | -61.7569 | -61.8027 | 61.7523 | 61.7706 | 61.7432 | 0.16022 | 0.13275 | 0.068665 | 0 | 0.14191 | 0.1236 | 0.13733 | 0.16937 | 61.7432 | 61.7798 | -61.9308 | -61.9263 | 61.6058 | 61.734 | 61.7065 | 61.7249
703.4844 | 123.6969 | -61.7203 | 61.9217 | 0.15588 | 0.0092645 | -0.011638 | 0.017079 | -0.0026019 | -0.022134 | -0.0049704 | 0.14589 | 0.012976 | 0.012279 | 0.028808 | -0.0093592 | 0.019184 | -0.0027915 | 0.009155 | 0.10071 | -0.07782 | -0.009155 | 0.064087 | -0.013733 | 0.041199 | -0.032043 | 0.15564 | -0.09613 | -0.027466 | 0.013733 | 0.009155 | 0.022888 | 61.6425 | -61.821 | -61.9308 | 61.7844 | 61.7615 | 61.7065 | 0.11902 | 0.064087 | 61.6241 | -61.7661 | -61.9492 | 61.734 | 61.7432 | 61.7294 | 0.11902 | 0.10528 | 0.14191 | 0.068665 | 0.10986 | 0.068664 | 0.17853 | 0.25177 | 61.821 | 61.8759 | -61.9995 | -62.0178 | 61.7111 | 61.6928 | 61.7294 | 61.6882
704.4844 | 123.8342 | -61.6791 | 61.8347 | -0.011967 | 0.013537 | -0.0030927 | 0.029896 | 0.012352 | 0.0056368 | 0.0089146 | -0.067735 | 0.025793 | -0.0026746 | 0.017059 | -0.02004 | 0.025593 | -0.0070645 | 0.041199 | 0.064087 | -0.068665 | -0.10071 | -0.032043 | -0.09613 | -0.059509 | 0.086975 | 0.10986 | -0.073242 | 0.10986 | 0.1236 | 0.091553 | 0.10986 | 61.6104 | -61.7706 | -61.9354 | 61.647 | 61.6196 | 61.5829 | 0.009156 | -0.027465 | 61.6058 | -61.7249 | -61.7249 | 61.8027 | 61.7889 | 61.7706 | 0.18311 | 0.16479 | 0.036622 | -0.032043 | 0.19684 | 0.18311 | 0.13275 | 0.18311 | 61.7432 | 61.7889 | -61.9034 | -61.908 | 61.5784 | 61.7889 | 61.7203 | 61.7661
705.4844 | 123.793 | -61.7065 | 61.8668 | -0.073002 | 0.0071275 | -0.0041607 | 0.030965 | 0.016624 | -0.015725 | -0.00069841 | 0.13063 | 0.010839 | 0.0015984 | -0.037415 | -0.011495 | 0.018116 | -0.0027915 | 0.022888 | 0.073242 | -0.07782 | -0.082397 | -0.022888 | -0.082397 | -0.050354 | 0.059509 | 0.1236 | -0.050354 | 0.064087 | 0.068665 | 0.064087 | 0.07782 | 61.6287 | -61.7935 | -61.9492 | 61.6837 | 61.6562 | 61.6241 | 0.027466 | -0.004577 | 61.6562 | -61.7432 | -61.8027 | 61.7752 | 61.7844 | 61.7706 | 0.12817 | 0.11444 | 0.054932 | -0.004577 | 0.11902 | 0.11444 | 0.15106 | 0.17395 | 61.7798 | 61.8301 | -61.9446 | -61.9171 | 61.6241 | 61.7706 | 61.7294 | 61.7661
706.4844 | 123.7244 | -61.7294 | 61.8759 | 0.1101 | 0.013537 | -0.013774 | 0.026692 | 0.019829 | -0.011453 | -0.010311 | 0.069594 | 0.01618 | 0.012279 | 0.0063777 | -0.017904 | 0.019184 | -0.013474 | -0.041199 | 0.11444 | -0.10986 | 0.041199 | 0.11902 | 0.027466 | 0.082397 | -0.082397 | 0.16479 | -0.10986 | -0.027466 | 0 | -0.018311 | 0.009155 | 61.6196 | -61.7615 | -61.8347 | 61.8484 | 61.8118 | 61.7569 | 0.19226 | 0.13733 | 61.6196 | -61.7111 | -61.9034 | 61.7294 | 61.7386 | 61.7111 | 0.11902 | 0.091552 | 0.22888 | 0.15106 | 0.10986 | 0.082397 | 0.2243 | 0.27466 | 61.8439 | 61.8942 | -61.9858 | -61.9858 | 61.7706 | 61.702 | 61.6882 | 61.647
707.4844 | 123.8068 | -61.7065 | 61.8668 | 0.049069 | 0.0071275 | -0.0030927 | 0.036305 | 0.018761 | 0.0067048 | -0.0039024 | 0.0085594 | 0.015112 | 0.0015984 | -0.0043033 | -0.025381 | 0.017048 | 0.00041246 | 0.027466 | 0.059509 | -0.054932 | -0.11902 | -0.022888 | -0.09613 | -0.041199 | 0.068665 | 0.10071 | -0.059509 | 0.082397 | 0.10071 | 0.082397 | 0.10529 | 61.6516 | -61.8073 | -61.9858 | 61.6837 | 61.6653 | 61.6104 | 0.013733 | -0.041198 | 61.647 | -61.7661 | -61.7844 | 61.8073 | 61.8118 | 61.7889 | 0.16479 | 0.14191 | 0.032044 | -0.064087 | 0.16022 | 0.14191 | 0.11444 | 0.16022 | 61.7661 | 61.8073 | -61.9217 | -61.9263 | 61.5875 | 61.7889 | 61.734 | 61.7752
708.4844 | 123.7839 | -61.702 | 61.8851 | 0.15588 | 0.015673 | -0.0095007 | 0.026692 | 0.010216 | -0.0071802 | 0.0057106 | 0.2527 | 0.011908 | 0.010143 | -0.047028 | -0.015768 | 0.020252 | 0.0057535 | -0.013733 | 0.059509 | -0.073242 | -0.064087 | 0.027466 | -0.059509 | -0.018311 | 0.009155 | 0.10529 | -0.068665 | 0.041199 | 0.064087 | 0.054932 | 0.073242 | 61.6287 | -61.8256 | -61.9492 | 61.7294 | 61.6837 | 61.6425 | 0.054931 | 0.013733 | 61.6333 | -61.7798 | -61.8439 | 61.7661 | 61.7752 | 61.7569 | 0.14191 | 0.1236 | 0.10071 | 0.009155 | 0.13275 | 0.10986 | 0.13275 | 0.17395 | 61.7615 | 61.8073 | -61.9583 | -61.9537 | 61.6379 | 61.7432 | 61.6882 | 61.7111
709.4844 | 123.8297 | -61.6791 | 61.8668 | 0.018551 | 0.0060595 | -0.0052287 | 0.026692 | -0.014351 | 0.0035008 | 0.0046426 | 0.14589 | 0.010839 | 0.00053042 | -0.052368 | -0.023245 | 0.014911 | -0.0081325 | 0.036621 | 0.073242 | -0.07782 | -0.10071 | -0.036621 | -0.10529 | -0.054932 | 0.086975 | 0.11902 | -0.059509 | 0.086975 | 0.14191 | 0.11444 | 0.091553 | 61.6013 | -61.7935 | -61.9675 | 61.6425 | 61.6241 | 61.5738 | 0.022888 | -0.027466 | 61.6196 | -61.7477 | -61.7798 | 61.821 | 61.7706 | 61.7935 | 0.15106 | 0.17395 | 0.041199 | -0.022888 | 0.20142 | 0.14648 | 0.15106 | 0.17853 | 61.7523 | 61.7981 | -61.9446 | -61.9263 | 61.5784 | 61.7661 | 61.7157 | 61.7661
710.4844 | 123.8388 | -61.6745 | 61.8805 | 0.094845 | 0.010333 | 0.0011803 | 0.020283 | 0.0038071 | 0.016318 | -0.0060384 | 0.2527 | 0.023657 | 0.0015984 | -0.0043033 | -0.011495 | 0.023456 | -0.0038605 | -0.004578 | 0.068665 | -0.086975 | -0.068665 | 0.022888 | -0.068665 | -0.022888 | 0.045776 | 0.1236 | -0.086975 | 0.07782 | 0.09613 | 0.091553 | 0.10071 | 61.5875 | -61.8118 | -61.9492 | 61.6974 | 61.6516 | 61.6058 | 0.064087 | 0.01831 | 61.5875 | -61.7569 | -61.8027 | 61.7706 | 61.7752 | 61.7661 | 0.18768 | 0.17853 | 0.10986 | 0.01831 | 0.1831 | 0.16479 | 0.15564 | 0.21057 | 61.7432 | 61.7981 | -61.9675 | -61.9675 | 61.6058 | 61.7523 | 61.6699 | 61.7203
711.4844 | 123.7793 | -61.702 | 61.8759 | 0.1101 | 0.025286 | -0.0052287 | 0.034169 | 0.0091481 | -0.0093172 | -0.0092424 | 0.039077 | 0.017248 | 0.00053042 | -0.013916 | -0.023245 | 0.020252 | -0.022018 | 0.009155 | 0.064087 | -0.059509 | -0.082397 | 0 | -0.068665 | -0.032043 | 0.032043 | 0.10529 | -0.086975 | 0.050354 | 0.086975 | 0.045776 | 0.082397 | 61.6425 | -61.8118 | -61.9583 | 61.702 | 61.6699 | 61.6333 | 0.027466 | -0.009156 | 61.615 | -61.7706 | -61.8256 | 61.7889 | 61.7844 | 61.7477 | 0.16937 | 0.13275 | 0.059509 | -0.022888 | 0.17395 | 0.13733 | 0.1236 | 0.19226 | 61.7661 | 61.8073 | -61.9354 | -61.9629 | 61.6196 | 61.7523 | 61.7111 | 61.734
712.4844 | 123.7152 | -61.734 | 61.9171 | 0.17114 | 0.018878 | 0.0011803 | 0.036305 | -0.0015339 | -0.015725 | 0.00037059 | 0.11537 | 0.025793 | 0.0026664 | 0.012787 | -0.013631 | 0.019184 | -0.0092005 | -0.004578 | 0.086975 | -0.082397 | -0.009155 | 0.091553 | -0.004578 | 0.054932 | -0.054932 | 0.16022 | -0.10529 | -0.041199 | 0.018311 | -0.013733 | 0.004578 | 61.6516 | -61.8301 | -61.9263 | 61.8256 | 61.7889 | 61.7294 | 0.13733 | 0.077819 | 61.6287 | -61.7569 | -61.9583 | 61.7523 | 61.7386 | 61.7203 | 0.10986 | 0.091553 | 0.17395 | 0.073242 | 0.1236 | 0.064087 | 0.16937 | 0.2655 | 61.821 | 61.8942 | -61.9995 | -62.0224 | 61.7249 | 61.6928 | 61.7294 | 61.6791
713.4844 | 123.8525 | -61.6974 | 61.8576 | 0.14062 | 0.0071275 | -0.00095673 | 0.02776 | 0.014488 | -0.0050442 | -0.00069841 | 0.2527 | 0.020452 | -0.0058786 | -0.025666 | -0.018972 | 0.0095709 | 0.0046845 | 0.009155 | 0.082397 | -0.082397 | -0.09613 | 0 | -0.10071 | -0.050354 | 0.064087 | 0.1236 | -0.059509 | 0.086975 | 0.1236 | 0.11444 | 0.13275 | 61.615 | -61.7752 | -61.9537 | 61.6974 | 61.647 | 61.5967 | 0.032043 | -0.018311 | 61.6379 | -61.734 | -61.7706 | 61.821 | 61.8301 | 61.8118 | 0.19226 | 0.17395 | 0.082397 | -0.013733 | 0.1831 | 0.14648 | 0.16479 | 0.1831 | 61.7798 | 61.821 | -61.94 | -61.9171 | 61.6013 | 61.7844 | 61.7065 | 61.7615
714.5 | 123.8388 | -61.6974 | 61.8622 | 0.018551 | 0.011401 | -0.0041607 | 0.025624 | -0.0079419 | -0.016794 | 0.011052 | -0.052476 | 0.012976 | 0.0037344 | -0.0075083 | -0.030721 | 0.019184 | -0.0059965 | 0.041199 | 0.054932 | -0.068665 | -0.09613 | -0.009155 | -0.10071 | -0.064087 | 0.068665 | 0.10986 | -0.073242 | 0.11902 | 0.12817 | 0.086975 | 0.13275 | 61.6287 | -61.8073 | -61.9583 | 61.6882 | 61.6333 | 61.5967 | 0.004578 | -0.032043 | 61.6241 | -61.7523 | -61.7432 | 61.8256 | 61.8301 | 61.7844 | 0.20599 | 0.16022 | 0.05951 | -0.027465 | 0.20142 | 0.19226 | 0.1236 | 0.18311 | 61.7523 | 61.8073 | -61.9308 | -61.9354 | 61.6013 | 61.8164 | 61.7386 | 61.7661
715.4844 | 123.8251 | -61.702 | 61.8622 | 0.018551 | 0.018878 | -0.00095673 | 0.026692 | 0.011284 | -0.00077219 | -0.013515 | -0.021958 | 0.014044 | -0.0037426 | -0.014984 | -0.02004 | 0.017048 | -0.0038605 | 0.041199 | 0.050354 | -0.054932 | -0.09613 | -0.018311 | -0.10529 | -0.068665 | 0.082397 | 0.10986 | -0.059509 | 0.10986 | 0.10529 | 0.086975 | 0.11444 | 61.647 | -61.8118 | -61.9583 | 61.6837 | 61.6333 | 61.5967 | -0.013733 | -0.050354 | 61.6425 | -61.7523 | -61.7523 | 61.8073 | 61.8164 | 61.7889 | 0.17395 | 0.14648 | 0.036621 | -0.041198 | 0.16479 | 0.16937 | 0.10529 | 0.16937 | 61.7523 | 61.8118 | -61.9171 | -61.9217 | 61.6058 | 61.8118 | 61.7432 | 61.7844
716.4844 | 123.8113 | -61.6974 | 61.8622 | 0.03381 | 0.0039235 | -0.0073647 | 0.024556 | 0.016624 | -0.027475 | -0.010311 | 0.11537 | 0.0076354 | -0.0037426 | -0.0043033 | -0.017904 | 0.022388 | -0.0059965 | 0.032043 | 0.041199 | -0.059509 | -0.10529 | -0.027466 | -0.091553 | -0.045776 | 0.073242 | 0.10986 | -0.068665 | 0.086975 | 0.091553 | 0.086975 | 0.10529 | 61.6379 | -61.821 | -61.9675 | 61.6699 | 61.6516 | 61.6058 | 0.013733 | -0.032044 | 61.6287 | -61.7523 | -61.7752 | 61.7889 | 61.8027 | 61.7844 | 0.17395 | 0.15564 | 0.032043 | -0.045777 | 0.16022 | 0.15564 | 0.10071 | 0.17853 | 61.7386 | 61.8073 | -61.9217 | -61.9308 | 61.5921 | 61.7844 | 61.7294 | 61.7706
717.4844 | 123.7106 | -61.7477 | 61.9125 | 0.17114 | 0.0081955 | -0.011638 | 0.02776 | 0.0016711 | -0.011453 | -0.0028344 | 0.14589 | 0.021521 | 0.00053042 | 0.0031737 | -0.011495 | 0.010639 | 0.0014805 | -0.018311 | 0.091553 | -0.10986 | 0.013733 | 0.10529 | -0.004578 | 0.050354 | -0.073242 | 0.15106 | -0.11444 | -0.036621 | 0.009155 | -0.018311 | 0.018311 | 61.6379 | -61.821 | -61.8988 | 61.853 | 61.7981 | 61.7432 | 0.16022 | 0.10529 | 61.6333 | -61.7615 | -61.9492 | 61.7569 | 61.7661 | 61.7294 | 0.13275 | 0.09613 | 0.21515 | 0.1236 | 0.1236 | 0.07782 | 0.20142 | 0.2655 | 61.8393 | 61.8988 | -62.0224 | -62.027 | 61.7615 | 61.7111 | 61.7294 | 61.6745
718.4844 | 123.8113 | -61.6974 | 61.8942 | 0.20166 | 0.010333 | -0.018046 | 0.018147 | 0.0070111 | 0.0077728 | 0.00037059 | 0.26796 | 0.01618 | 0.0069384 | -0.025666 | -0.0147 | 0.028797 | -0.0017235 | -0.004578 | 0.064087 | -0.082397 | -0.059509 | 0.022888 | -0.059509 | -0.027466 | 0.004578 | 0.11902 | -0.07782 | 0.059509 | 0.11444 | 0.073242 | 0.086975 | 61.615 | -61.8301 | -61.9537 | 61.7203 | 61.6699 | 61.6379 | 0.054931 | 0.022888 | 61.6196 | -61.7752 | -61.8347 | 61.8118 | 61.7844 | 61.7706 | 0.16479 | 0.15106 | 0.10528 | 0.022888 | 0.19226 | 0.13733 | 0.14648 | 0.19684 | 61.7615 | 61.8164 | -61.9766 | -61.972 | 61.6379 | 61.7569 | 61.6928 | 61.702
719.4844 | 123.7335 | -61.7294 | 61.9354 | 0.21692 | 0.014605 | -0.0084327 | 0.026692 | -0.013283 | -0.014657 | -0.0060384 | 0.14589 | 0.022589 | 0.01762 | -0.035279 | -0.023245 | 0.028797 | -0.022018 | 0.009155 | 0.068665 | -0.091553 | -0.027466 | 0.064087 | -0.022888 | 0.032043 | -0.050354 | 0.14191 | -0.09613 | -0.013733 | 0.004578 | -0.004578 | 0.009155 | 61.6379 | -61.8668 | -61.9629 | 61.7935 | 61.7615 | 61.7065 | 0.1236 | 0.068665 | 61.6333 | -61.7935 | -61.9492 | 61.734 | 61.7386 | 61.7249 | 0.10528 | 0.091552 | 0.15564 | 0.064087 | 0.10071 | 0.082397 | 0.16022 | 0.23804 | 61.7981 | 61.8713 | -62.027 | -62.0316 | 61.702 | 61.7157 | 61.7386 | 61.6791
720.4844 | 123.8022 | -61.7249 | 61.8988 | 0.03381 | 0.0071275 | -0.0030927 | 0.034169 | 0.0016711 | -0.01893 | 0.0046426 | 0.11537 | 0.018316 | 0.019756 | -0.013916 | -0.013631 | 0.011707 | 0.00041246 | -0.022888 | 0.064087 | -0.086975 | -0.064087 | 0.027466 | -0.059509 | -0.013733 | 0.004578 | 0.09613 | -0.09613 | 0.041199 | 0.054932 | 0.045776 | 0.068665 | 61.6379 | -61.8347 | -61.9629 | 61.7523 | 61.7111 | 61.6653 | 0.073242 | 0.027466 | 61.6287 | -61.8027 | -61.8576 | 61.7798 | 61.7935 | 61.7706 | 0.16479 | 0.14191 | 0.11444 | 0.022888 | 0.15106 | 0.13733 | 0.15106 | 0.19226 | 61.7889 | 61.821 | -61.9858 | -61.9949 | 61.6608 | 61.7661 | 61.702 | 61.7294
721.4844 | 123.8617 | -61.6699 | 61.8347 | -0.011967 | 0.014605 | -0.021251 | 0.034169 | 0.0038071 | -0.0082492 | -0.013515 | -0.021958 | 0.01618 | -0.012288 | -0.022461 | -0.015768 | 0.0052979 | -0.0070645 | 0.045776 | 0.064087 | -0.068665 | -0.10529 | -0.032043 | -0.10986 | -0.054932 | 0.07782 | 0.10529 | -0.073242 | 0.10071 | 0.1236 | 0.086975 | 0.1236 | 61.6013 | -61.7706 | -61.94 | 61.6379 | 61.615 | 61.5601 | 0.013733 | -0.041198 | 61.5967 | -61.7294 | -61.734 | 61.7935 | 61.7935 | 61.7569 | 0.19684 | 0.16022 | 0.036622 | -0.036621 | 0.19684 | 0.17395 | 0.13275 | 0.17853 | 61.734 | 61.7752 | -61.9034 | -61.908 | 61.5646 | 61.7706 | 61.7157 | 61.7477
722.4844 | 123.8342 | -61.6791 | 61.8713 | 0.21692 | 0.0071275 | -0.0052287 | 0.024556 | 0.0080791 | -0.012521 | -0.0017664 | 0.16115 | 0.0087034 | 0.0026664 | -0.024597 | -0.028585 | 0.02132 | -0.0038605 | 0.032043 | 0.086975 | -0.050354 | -0.10529 | -0.027466 | -0.10071 | -0.036621 | 0.07782 | 0.10529 | -0.064087 | 0.091553 | 0.12817 | 0.11902 | 0.11444 | 61.6287 | -61.7844 | -61.9766 | 61.6516 | 61.6425 | 61.5784 | 0.013733 | -0.050354 | 61.615 | -61.7661 | -61.7798 | 61.8073 | 61.7935 | 61.7981 | 0.17853 | 0.18311 | 0.022888 | -0.054932 | 0.19226 | 0.15564 | 0.13733 | 0.16937 | 61.7661 | 61.7844 | -61.9217 | -61.9354 | 61.5738 | 61.7706 | 61.7111 | 61.7569
723.4844 | 123.8388 | -61.702 | 61.8622 | 0.018551 | 0.012469 | -0.0052287 | 0.025624 | -0.0004649 | -0.015725 | -0.013515 | 0.11537 | 0.019384 | -0.0016066 | 0.0010367 | -0.028585 | 0.023456 | 0.011093 | 0.032043 | 0.073242 | -0.054932 | -0.09613 | -0.022888 | -0.11902 | -0.054932 | 0.068665 | 0.11902 | -0.059509 | 0.091553 | 0.10986 | 0.082397 | 0.10529 | 61.647 | -61.7889 | -61.9583 | 61.6791 | 61.647 | 61.5829 | 0 | -0.064087 | 61.6425 | -61.7432 | -61.7706 | 61.8118 | 61.8073 | 61.7844 | 0.16479 | 0.14191 | 0.032044 | -0.041198 | 0.16937 | 0.15106 | 0.12817 | 0.17853 | 61.7752 | 61.821 | -61.9171 | -61.9217 | 61.6058 | 61.7935 | 61.734 | 61.7706
724.4844 | 123.793 | -61.7111 | 61.8713 | -0.011967 | 0.011401 | -0.0084327 | 0.018147 | -0.02076 | -0.019998 | -0.013515 | 0.069594 | 0.021521 | -0.0069466 | -0.022461 | -0.021108 | 0.014911 | -0.0070645 | 0.022888 | 0.050354 | -0.064087 | -0.09613 | -0.036621 | -0.09613 | -0.059509 | 0.064087 | 0.10986 | -0.073242 | 0.082397 | 0.082397 | 0.073242 | 0.07782 | 61.647 | -61.821 | -61.9675 | 61.6745 | 61.6516 | 61.615 | 0.004578 | -0.032043 | 61.6379 | -61.7615 | -61.7889 | 61.7935 | 61.7889 | 61.7844 | 0.15106 | 0.14648 | 0.027466 | -0.032043 | 0.15564 | 0.15564 | 0.11444 | 0.18311 | 61.7615 | 61.821 | -61.9354 | -61.9446 | 61.615 | 61.7935 | 61.734 | 61.7752
725.4844 | 123.8205 | -61.7065 | 61.853 | 0.0032924 | 0.014605 | -0.00095673 | 0.029896 | 0.0006031 | -0.012521 | -0.011379 | 0.069594 | 0.018316 | -0.0026746 | -0.021393 | -0.023245 | 0.01598 | -0.016678 | 0.027466 | 0.064087 | -0.07782 | -0.10986 | -0.036621 | -0.09613 | -0.041199 | 0.073242 | 0.09613 | -0.07782 | 0.086975 | 0.09613 | 0.07782 | 0.09613 | 61.6287 | -61.7889 | -61.9629 | 61.6699 | 61.6653 | 61.6104 | 0.036621 | -0.01831 | 61.6287 | -61.7569 | -61.7661 | 61.8027 | 61.8027 | 61.7844 | 0.17395 | 0.15564 | 0.041199 | -0.032043 | 0.17395 | 0.16479 | 0.14191 | 0.17395 | 61.7706 | 61.8027 | -61.9308 | -61.9308 | 61.5967 | 61.7935 | 61.734 | 61.7798
726.4844 | 123.7976 | -61.734 | 61.8713 | 0.1101 | 0.0039235 | -0.01591 | 0.025624 | 0.012352 | -0.0018402 | -0.0071064 | 0.13063 | 0.017248 | -0.0090826 | -0.024597 | -0.021108 | 0.01598 | 0.017502 | 0.009155 | 0.054932 | -0.07782 | -0.073242 | 0 | -0.073242 | -0.022888 | 0.013733 | 0.10529 | -0.07782 | 0.054932 | 0.068665 | 0.064087 | 0.082397 | 61.6562 | -61.8164 | -61.9446 | 61.734 | 61.7111 | 61.6608 | 0.054932 | 0.004578 | 61.6562 | -61.7661 | -61.8164 | 61.8027 | 61.8164 | 61.7981 | 0.16022 | 0.14191 | 0.07782 | 0.004578 | 0.14649 | 0.13275 | 0.13275 | 0.18311 | 61.7889 | 61.8393 | -61.9492 | -61.9492 | 61.6608 | 61.7889 | 61.7432 | 61.7477
727.4844 | 123.8205 | -61.6974 | 61.8713 | -0.057743 | 0.013537 | -0.01057 | 0.020283 | 0.015556 | 0.0077728 | -0.0081744 | 0.31374 | 0.023657 | 0.0058704 | -0.024597 | -0.026449 | 0.01598 | 0.00041246 | -0.018311 | 0.068665 | -0.073242 | -0.054932 | 0.045776 | -0.068665 | -0.018311 | -0.004578 | 0.1236 | -0.082397 | 0.050354 | 0.07782 | 0.073242 | 0.091553 | 61.6241 | -61.8027 | -61.9263 | 61.7432 | 61.6791 | 61.6287 | 0.054931 | 0.004577 | 61.615 | -61.7477 | -61.821 | 61.7752 | 61.7889 | 61.7706 | 0.17395 | 0.15564 | 0.11902 | 0.01831 | 0.16022 | 0.13275 | 0.14191 | 0.20599 | 61.7661 | 61.821 | -61.9446 | -61.9537 | 61.6425 | 61.7477 | 61.6791 | 61.6928
728.4844 | 123.8113 | -61.7157 | 61.8668 | 0.049069 | 0.02315 | -0.0073647 | 0.014943 | 0.01342 | -0.0039762 | -0.015651 | 0.11537 | 0.021521 | 0.0037344 | 0.014923 | -0.026449 | 0.023456 | 0.015366 | 0.018311 | 0.059509 | -0.059509 | -0.09613 | -0.027466 | -0.10071 | -0.041199 | 0.068665 | 0.10071 | -0.068665 | 0.10071 | 0.091553 | 0.082397 | 0.091553 | 61.6562 | -61.8073 | -61.9629 | 61.6882 | 61.6745 | 61.615 | 0.01831 | -0.041199 | 61.647 | -61.7661 | -61.7661 | 61.8073 | 61.8073 | 61.7981 | 0.16022 | 0.15106 | 0.032043 | -0.036621 | 0.16022 | 0.16937 | 0.11902 | 0.16937 | 61.7752 | 61.8164 | -61.9263 | -61.9354 | 61.6196 | 61.8164 | 61.734 | 61.7844
729.4844 | 123.8617 | -61.6882 | 61.8622 | 0.079586 | 0.016741 | -0.0041607 | 0.026692 | 0.0027391 | -0.00077219 | -0.0017664 | 0.20692 | 0.019384 | -0.0037426 | -0.025666 | -0.017904 | 0.013843 | -0.012405 | 0.018311 | 0.059509 | -0.068665 | -0.11902 | -0.045776 | -0.11444 | -0.059509 | 0.10986 | 0.11902 | -0.059509 | 0.09613 | 0.16022 | 0.14191 | 0.11444 | 61.6196 | -61.8027 | -61.9812 | 61.6425 | 61.6287 | 61.5738 | 0.009156 | -0.045776 | 61.6287 | -61.7432 | -61.7661 | 61.8484 | 61.8027 | 61.8301 | 0.17395 | 0.20142 | 0.022889 | -0.050354 | 0.21973 | 0.15564 | 0.12817 | 0.17853 | 61.7477 | 61.8073 | -61.9308 | -61.9217 | 61.5692 | 61.7844 | 61.7065 | 61.7981
730.4844 | 123.8022 | -61.7203 | 61.8896 | 0.03381 | 0.021014 | -0.014842 | 0.025624 | -0.0068739 | -0.0071802 | -0.018856 | 0.069594 | 0.01618 | -0.0048106 | 0.01065 | -0.018972 | 0.0095709 | 0.00041246 | 0.004578 | 0.064087 | -0.082397 | -0.10071 | -0.022888 | -0.09613 | -0.050354 | 0.054932 | 0.10986 | -0.086975 | 0.054932 | 0.073242 | 0.050354 | 0.073242 | 61.6379 | -61.8256 | -61.9904 | 61.6974 | 61.6699 | 61.6241 | 0.032043 | -0.013733 | 61.6333 | -61.7798 | -61.8347 | 61.7935 | 61.7935 | 61.7706 | 0.16022 | 0.13733 | 0.059509 | -0.018311 | 0.16022 | 0.14191 | 0.14648 | 0.19684 | 61.7844 | 61.8301 | -61.972 | -61.9766 | 61.6196 | 61.7752 | 61.7249 | 61.7752
731.4844 | 123.848 | -61.7065 | 61.8713 | 0.018551 | 0.0092645 | -0.0041607 | 0.028828 | 0.014488 | -0.013589 | -0.0039024 | -0.021958 | 0.011908 | -0.0058786 | -0.0043033 | -0.024313 | 0.02132 | -0.0049285 | -0.013733 | 0.07782 | -0.09613 | -0.041199 | 0.027466 | -0.068665 | -0.027466 | 0.036621 | 0.10986 | -0.082397 | 0.09613 | 0.10986 | 0.07782 | 0.11444 | 61.6104 | -61.7935 | -61.9125 | 61.734 | 61.6791 | 61.6379 | 0.068664 | 0.027465 | 61.6241 | -61.7615 | -61.7752 | 61.8164 | 61.821 | 61.7844 | 0.19684 | 0.16022 | 0.1236 | 0.054931 | 0.19226 | 0.17853 | 0.17395 | 0.19226 | 61.7844 | 61.8164 | -61.9675 | -61.9537 | 61.6653 | 61.8027 | 61.6928 | 61.7432
732.4844 | 123.8022 | -61.7111 | 61.8713 | 0.14062 | 0.012469 | -0.012706 | 0.025624 | 0.018761 | -0.026407 | -0.020992 | 0.16115 | 0.018316 | 0.0015984 | -0.033142 | -0.018972 | 0.01598 | -0.010269 | -0.009155 | 0.073242 | -0.091553 | -0.041199 | 0.041199 | -0.059509 | -0.018311 | -0.013733 | 0.11902 | -0.10071 | 0.036621 | 0.054932 | 0.036621 | 0.073242 | 61.6196 | -61.7981 | -61.9125 | 61.7523 | 61.6928 | 61.6516 | 0.073242 | 0.032044 | 61.6104 | -61.7523 | -61.8347 | 61.7661 | 61.7844 | 61.7477 | 0.17395 | 0.13733 | 0.13275 | 0.050354 | 0.15564 | 0.13733 | 0.16479 | 0.21973 | 61.7844 | 61.8301 | -61.9629 | -61.972 | 61.6699 | 61.7477 | 61.702 | 61.6974
733.4844 | 123.848 | -61.6882 | 61.8896 | 0.0032924 | 0.017809 | -0.01057 | 0.020283 | 0.0006031 | -0.016794 | -0.0071064 | 0.29848 | 0.020452 | -0.0090826 | -0.024597 | -0.028585 | 0.014911 | -0.01561 | 0.032043 | 0.059509 | -0.068665 | -0.1236 | -0.041199 | -0.11902 | -0.050354 | 0.09613 | 0.091553 | -0.082397 | 0.082397 | 0.15564 | 0.11902 | 0.10986 | 61.6196 | -61.8301 | -62.0132 | 61.647 | 61.6379 | 61.5692 | 0.018311 | -0.050354 | 61.6058 | -61.7981 | -61.8073 | 61.8439 | 61.7981 | 61.8073 | 0.19226 | 0.20142 | 0.027466 | -0.054931 | 0.23804 | 0.16479 | 0.12817 | 0.17395 | 61.7477 | 61.7798 | -61.9583 | -61.972 | 61.5646 | 61.7706 | 61.7203 | 61.7844
734.4844 | 123.8709 | -61.6699 | 61.8851 | 0.064327 | 0.0039235 | -0.0062967 | 0.018147 | 0.015556 | -0.0061122 | -0.0060384 | 0.23744 | 0.020452 | 0.010143 | -0.029938 | -0.026449 | 0.011707 | 0.00041246 | 0.041199 | 0.068665 | -0.082397 | -0.14191 | -0.054932 | -0.14191 | -0.068665 | 0.10529 | 0.10071 | -0.073242 | 0.09613 | 0.14648 | 0.13275 | 0.10529 | 61.5875 | -61.8164 | -62.027 | 61.615 | 61.6013 | 61.528 | 0.013732 | -0.05951 | 61.5967 | -61.7844 | -61.7889 | 61.8164 | 61.7752 | 61.8027 | 0.17853 | 0.20599 | 0.027465 | -0.05951 | 0.21973 | 0.16937 | 0.15106 | 0.17395 | 61.7386 | 61.7706 | -61.9675 | -61.9583 | 61.528 | 61.7661 | 61.7111 | 61.7752
735.4844 | 123.848 | -61.702 | 61.8896 | -0.027225 | 0.014605 | -0.0073647 | 0.029896 | -0.012215 | -0.015725 | -0.018856 | -0.098252 | 0.022589 | -0.0058786 | 0.020263 | -0.030721 | 0.012775 | -0.0027915 | 0.022888 | 0.059509 | -0.07782 | -0.091553 | -0.013733 | -0.10071 | -0.050354 | 0.064087 | 0.10529 | -0.068665 | 0.10529 | 0.12817 | 0.086975 | 0.12817 | 61.6241 | -61.8301 | -61.9812 | 61.6882 | 61.6516 | 61.6013 | 0.027466 | -0.022888 | 61.6333 | -61.7844 | -61.7844 | 61.8301 | 61.8301 | 61.7889 | 0.19684 | 0.15564 | 0.064087 | -0.013733 | 0.19684 | 0.17395 | 0.13733 | 0.17395 | 61.7615 | 61.8073 | -61.9675 | -61.9583 | 61.6104 | 61.8073 | 61.7249 | 61.7661
736.4844 | 123.7793 | -61.7157 | 61.8896 | 0.0032924 | 0.013537 | 0.00011227 | 0.028828 | 0.0027391 | -0.017862 | -0.017787 | -0.11351 | 0.012976 | 0.015483 | -0.038483 | -0.023245 | 0.022388 | -0.0049285 | -0.036621 | 0.10986 | -0.09613 | 0.032043 | 0.11444 | 0 | 0.036621 | -0.041199 | 0.14648 | -0.091553 | 0.036621 | 0.032043 | -0.009155 | 0.045776 | 61.6196 | -61.7798 | -61.8576 | 61.8301 | 61.7523 | 61.7157 | 0.13275 | 0.09613 | 61.6241 | -61.7432 | -61.853 | 61.7477 | 61.7615 | 61.7065 | 0.13733 | 0.082398 | 0.21057 | 0.12817 | 0.1236 | 0.12817 | 0.20599 | 0.23804 | 61.8256 | 61.8622 | -61.9858 | -61.9812 | 61.7477 | 61.7523 | 61.6791 | 61.6745
737.4844 | 123.793 | -61.7065 | 61.8622 | 0.03381 | 0.014605 | -0.012706 | 0.021352 | 0.017693 | 0.016318 | -0.010311 | 0.0085594 | 0.0097714 | -0.0037426 | 0.0053097 | -0.017904 | 0.022388 | 0.0036165 | 0.018311 | 0.054932 | -0.054932 | -0.10071 | -0.041199 | -0.10071 | -0.059509 | 0.07782 | 0.11902 | -0.068665 | 0.09613 | 0.09613 | 0.073242 | 0.10071 | 61.6516 | -61.8073 | -61.9629 | 61.6653 | 61.647 | 61.6058 | -0.004577 | -0.045776 | 61.6379 | -61.7432 | -61.7661 | 61.8027 | 61.8073 | 61.7798 | 0.16937 | 0.14191 | 0.013733 | -0.045776 | 0.16479 | 0.16479 | 0.10986 | 0.18768 | 61.7615 | 61.8256 | -61.9171 | -61.9308 | 61.6058 | 61.8027 | 61.7249 | 61.7844
738.4844 | 123.7839 | -61.7065 | 61.8713 | 0.018551 | -0.00034947 | -0.011638 | 0.035237 | 0.0059431 | -0.0039762 | -0.0017664 | -0.082994 | 0.015112 | -0.0037426 | 0.0010367 | -0.025381 | 0.02132 | 0.0025485 | -0.041199 | 0.086975 | -0.12817 | -0.004578 | 0.091553 | 0.004578 | 0.027466 | -0.045776 | 0.14191 | -0.091553 | 0.050354 | 0.059509 | 0.013733 | 0.064087 | 61.5784 | -61.7844 | -61.8759 | 61.7981 | 61.734 | 61.7111 | 0.15564 | 0.13275 | 61.615 | -61.7294 | -61.821 | 61.7661 | 61.7706 | 61.7203 | 0.15564 | 0.10529 | 0.21973 | 0.1236 | 0.15106 | 0.14191 | 0.21515 | 0.23346 | 61.7935 | 61.8485 | -61.9995 | -61.9629 | 61.702 | 61.7569 | 61.6653 | 61.6608
739.4844 | 123.8022 | -61.6928 | 61.8668 | 0.03381 | 0.015673 | -0.01591 | 0.02242 | 0.0080791 | -0.010385 | -0.010311 | 0.11537 | 0.01618 | 0.015483 | -0.014984 | -0.013631 | 0.020252 | 0.0046845 | -0.018311 | 0.064087 | -0.082397 | -0.073242 | 0.027466 | -0.064087 | -0.022888 | -0.022888 | 0.11902 | -0.091553 | 0.032043 | 0.068665 | 0.050354 | 0.064087 | 61.6104 | -61.8027 | -61.94 | 61.7203 | 61.6699 | 61.6287 | 0.059509 | 0.01831 | 61.6013 | -61.7477 | -61.8347 | 61.7615 | 61.7569 | 61.7432 | 0.15564 | 0.14191 | 0.10986 | 0.009155 | 0.16022 | 0.1236 | 0.14648 | 0.21057 | 61.7569 | 61.8118 | -61.9492 | -61.9583 | 61.6196 | 61.7249 | 61.6745 | 61.6699
740.4844 | 123.7518 | -61.7569 | 61.8896 | 0.14062 | 0.0017875 | -0.0084327 | 0.029896 | 0.011284 | -0.034951 | 0.00037059 | -0.22032 | 0.024725 | 0.0058704 | 0.011719 | -0.02004 | 0.026661 | -0.0092005 | -0.041199 | 0.086975 | -0.10529 | 0.036621 | 0.13275 | 0.032043 | 0.059509 | -0.082397 | 0.15564 | -0.10529 | -0.032043 | -0.013733 | -0.041199 | 0.013733 | 61.6516 | -61.8027 | -61.853 | 61.8896 | 61.8164 | 61.7889 | 0.16479 | 0.13733 | 61.6516 | -61.734 | -61.9217 | 61.7432 | 61.7706 | 61.7157 | 0.11902 | 0.064087 | 0.23804 | 0.14191 | 0.091553 | 0.073243 | 0.19226 | 0.26093 | 61.8439 | 61.9125 | -61.9949 | -61.9949 | 61.7935 | 61.7249 | 61.7157 | 61.6745
741.4844 | 123.7289 | -61.7615 | 61.8896 | 0.064327 | 0.0071275 | 0.0011803 | 0.028828 | -0.016487 | -0.0093172 | -0.0017664 | -0.23558 | 0.018316 | 0.0058704 | -0.0032353 | -0.015768 | 0.0085029 | -0.0081325 | -0.073242 | 0.10071 | -0.11444 | 0.050354 | 0.13275 | 0.027466 | 0.068665 | -0.10529 | 0.12817 | -0.11902 | -0.022888 | -0.036621 | -0.059509 | 0.013733 | 61.647 | -61.7889 | -61.8393 | 61.8942 | 61.8301 | 61.7889 | 0.18311 | 0.14191 | 61.6425 | -61.7615 | -61.9125 | 61.7249 | 61.7752 | 61.702 | 0.13275 | 0.05951 | 0.24719 | 0.16479 | 0.082398 | 0.096131 | 0.21515 | 0.24719 | 61.8622 | 61.8896 | -62.0041 | -62.0087 | 61.8118 | 61.7386 | 61.6882 | 61.6562
742.4844 | 123.793 | -61.7294 | 61.8622 | 0.049069 | 0.025286 | -0.0062967 | 0.023488 | 0.020897 | -0.025338 | -0.015651 | 0.16115 | 0.022589 | -0.0048106 | -0.023529 | -0.012563 | 0.018116 | 0.0078895 | -0.009155 | 0.059509 | -0.059509 | -0.068665 | 0.022888 | -0.059509 | -0.022888 | -0.004578 | 0.10071 | -0.068665 | 0.045776 | 0.064087 | 0.054932 | 0.07782 | 61.6699 | -61.8027 | -61.9308 | 61.7523 | 61.7065 | 61.6699 | 0.036621 | 0 | 61.6608 | -61.7615 | -61.8164 | 61.7935 | 61.8073 | 61.7844 | 0.14649 | 0.1236 | 0.082397 | -0.009156 | 0.13275 | 0.11444 | 0.11902 | 0.16937 | 61.7889 | 61.8301 | -61.9217 | -61.9308 | 61.6608 | 61.7752 | 61.7203 | 61.7249
743.4844 | 123.7976 | -61.7249 | 61.8668 | 0.1101 | 0.013537 | -0.0095007 | 0.026692 | -0.0079419 | 0.014182 | -0.010311 | 0.11537 | 0.015112 | 0.0090754 | -0.022461 | -0.011495 | 0.020252 | -0.019882 | 0.018311 | 0.045776 | -0.07782 | -0.091553 | -0.027466 | -0.091553 | -0.054932 | 0.059509 | 0.10986 | -0.073242 | 0.059509 | 0.082397 | 0.059509 | 0.07782 | 61.647 | -61.821 | -61.9583 | 61.6974 | 61.6699 | 61.6333 | 0.022888 | -0.013733 | 61.6516 | -61.7569 | -61.8073 | 61.8073 | 61.8027 | 61.7844 | 0.15106 | 0.13275 | 0.050354 | -0.013733 | 0.15564 | 0.13275 | 0.1236 | 0.18311 | 61.7706 | 61.8347 | -61.9446 | -61.94 | 61.6333 | 61.7844 | 61.7432 | 61.7844
744.4844 | 123.8617 | -61.6928 | 61.8759 | -0.042484 | 0.013537 | -0.0062967 | 0.024556 | -0.0058059 | -0.0050442 | -0.025264 | 0.023818 | 0.022589 | 0.013347 | -0.037415 | -0.023245 | 0.02132 | -0.011337 | 0.045776 | 0.059509 | -0.068665 | -0.11444 | -0.018311 | -0.10986 | -0.064087 | 0.068665 | 0.10071 | -0.059509 | 0.10071 | 0.12817 | 0.091553 | 0.11444 | 61.6241 | -61.8164 | -61.9904 | 61.6745 | 61.6287 | 61.5829 | 0.004578 | -0.041198 | 61.6333 | -61.7752 | -61.7752 | 61.821 | 61.8073 | 61.7844 | 0.17395 | 0.15106 | 0.050354 | -0.045776 | 0.18768 | 0.16022 | 0.12817 | 0.16022 | 61.7523 | 61.7935 | -61.9446 | -61.9354 | 61.5784 | 61.7935 | 61.7386 | 61.7615
745.4844 | 123.7473 | -61.7477 | 61.8942 | 0.064327 | 0.018878 | -0.0030927 | 0.026692 | 0.0091481 | -0.0093172 | 0.0089146 | -0.098252 | 0.024725 | 0.012279 | 0.028808 | -0.025381 | 0.025593 | -0.0070645 | -0.004578 | 0.091553 | -0.10071 | 0 | 0.07782 | 0 | 0.050354 | -0.022888 | 0.14648 | -0.09613 | 0 | 0.009155 | -0.022888 | 0.041199 | 61.647 | -61.8027 | -61.8942 | 61.8256 | 61.7981 | 61.7477 | 0.15106 | 0.10071 | 61.6516 | -61.7477 | -61.8942 | 61.7569 | 61.7889 | 61.7249 | 0.13733 | 0.073242 | 0.17853 | 0.10071 | 0.10528 | 0.09613 | 0.19226 | 0.24261 | 61.8393 | 61.8942 | -61.9949 | -61.9904 | 61.7477 | 61.7477 | 61.7432 | 61.7249
746.4844 | 123.7335 | -61.7432 | 61.908 | -0.011967 | 0.014605 | -0.0052287 | 0.038441 | 0.0080791 | -0.00077219 | 0.0089146 | -0.17455 | 0.024725 | -0.0058786 | 0.0053097 | -0.022176 | 0.027729 | -0.0049285 | -0.027466 | 0.10071 | -0.10071 | 0.018311 | 0.091553 | 0.018311 | 0.068665 | -0.059509 | 0.15106 | -0.091553 | -0.027466 | -0.009155 | -0.050354 | 0.013733 | 61.6425 | -61.8073 | -61.8896 | 61.8347 | 61.8118 | 61.7615 | 0.16937 | 0.11902 | 61.6516 | -61.7569 | -61.9354 | 61.734 | 61.7569 | 61.6928 | 0.10529 | 0.041199 | 0.19226 | 0.11902 | 0.082398 | 0.064087 | 0.20142 | 0.24261 | 61.8439 | 61.8942 | -62.0087 | -61.9995 | 61.7615 | 61.7157 | 61.7157 | 61.6837
747.4844 | 123.7885 | -61.7477 | 61.8896 | 0.094845 | 0.0092645 | 0.00011227 | 0.02242 | -0.0090099 | -0.0050442 | -0.015651 | -0.021958 | 0.025793 | -0.017628 | 0.014923 | -0.015768 | 0.02132 | -0.0038605 | -0.054932 | 0.10986 | -0.10986 | 0.032043 | 0.091553 | -0.009155 | 0.036621 | -0.045776 | 0.15564 | -0.09613 | 0.018311 | 0.036621 | 0.022888 | 0.073242 | 61.6379 | -61.7798 | -61.8576 | 61.8393 | 61.7844 | 61.7386 | 0.14648 | 0.10071 | 61.6516 | -61.734 | -61.8713 | 61.7844 | 61.821 | 61.7706 | 0.16937 | 0.11902 | 0.20142 | 0.14191 | 0.13275 | 0.11444 | 0.21973 | 0.25177 | 61.8576 | 61.9034 | -61.9995 | -61.9858 | 61.7798 | 61.7661 | 61.6928 | 61.702
748.4844 | 123.8525 | -61.6974 | 61.8668 | 0.064327 | 0.016741 | -0.0020247 | 0.018147 | 0.0016711 | 0.00029581 | -0.0039024 | 0.31374 | 0.017248 | 0.00053042 | -0.041687 | -0.022176 | 0.013843 | -0.0070645 | -0.018311 | 0.07782 | -0.09613 | -0.07782 | 0 | -0.073242 | -0.036621 | 0.018311 | 0.10986 | -0.082397 | 0.068665 | 0.11444 | 0.11444 | 0.10986 | 61.6013 | -61.7889 | -61.9446 | 61.6974 | 61.6608 | 61.6241 | 0.059509 | 0.022888 | 61.615 | -61.7569 | -61.7981 | 61.8118 | 61.8073 | 61.8118 | 0.19226 | 0.19684 | 0.09613 | 0.01831 | 0.19684 | 0.15106 | 0.17395 | 0.19226 | 61.7752 | 61.8073 | -61.9629 | -61.9492 | 61.6196 | 61.7661 | 61.6791 | 61.7157
749.4844 | 123.8342 | -61.6745 | 61.8668 | 0.0032924 | 0.013537 | -0.00095673 | 0.02242 | 0.014488 | 0.0056368 | 0.0014386 | 0.10011 | 0.019384 | -0.012288 | -0.022461 | -0.013631 | 0.017048 | 0.0014805 | 0.022888 | 0.054932 | -0.068665 | -0.11444 | -0.027466 | -0.1236 | -0.054932 | 0.091553 | 0.10529 | -0.054932 | 0.091553 | 0.1236 | 0.086975 | 0.10986 | 61.6058 | -61.8118 | -61.9812 | 61.647 | 61.6196 | 61.5509 | 0.013733 | -0.054931 | 61.6196 | -61.7615 | -61.7752 | 61.7981 | 61.7844 | 61.7615 | 0.16479 | 0.14191 | 0.041199 | -0.045776 | 0.17853 | 0.14649 | 0.1236 | 0.16022 | 61.7294 | 61.7798 | -61.9354 | -61.9217 | 61.5601 | 61.7661 | 61.6974 | 61.7661
750.4844 | 123.7885 | -61.734 | 61.8988 | 0.14062 | 0.018878 | -0.0062967 | 0.032033 | -0.0015339 | 0.0056368 | -0.011379 | -0.0066996 | 0.018316 | 0.0090754 | -0.0032353 | -0.027517 | 0.013843 | -0.01561 | -0.013733 | 0.09613 | -0.10529 | 0 | 0.07782 | -0.013733 | 0.036621 | -0.004578 | 0.14648 | -0.082397 | 0.027466 | 0.054932 | 0.022888 | 0.059509 | 61.6287 | -61.8027 | -61.8988 | 61.8118 | 61.7706 | 61.7203 | 0.14191 | 0.091553 | 61.6516 | -61.7523 | -61.8713 | 61.7889 | 61.7935 | 61.7569 | 0.14191 | 0.10528 | 0.18311 | 0.10529 | 0.13733 | 0.10986 | 0.20142 | 0.22888 | 61.8301 | 61.8805 | -62.0041 | -61.9812 | 61.734 | 61.7615 | 61.7203 | 61.7294
751.4844 | 123.7473 | -61.7661 | 61.9125 | 0.079586 | 0.018878 | -0.016978 | 0.038441 | 0.018761 | -0.010385 | -0.00069841 | -0.15929 | 0.026861 | -0.0026746 | -0.023529 | -0.017904 | 0.017048 | -0.014542 | -0.013733 | 0.086975 | -0.10986 | 0 | 0.086975 | -0.009155 | 0.045776 | -0.032043 | 0.15106 | -0.09613 | 0.004578 | 0.009155 | -0.032043 | 0.027466 | 61.6562 | -61.8256 | -61.9125 | 61.853 | 61.8118 | 61.7569 | 0.15564 | 0.10071 | 61.6699 | -61.7615 | -61.908 | 61.7752 | 61.7935 | 61.734 | 0.1236 | 0.064087 | 0.19684 | 0.10986 | 0.10528 | 0.10071 | 0.19684 | 0.24719 | 61.853 | 61.9171 | -62.0224 | -62.0087 | 61.7661 | 61.7706 | 61.7523 | 61.734
752.4844 | 123.8251 | -61.7157 | 61.8805 | 0.018551 | 0.017809 | 0.0033163 | 0.02776 | -0.0036699 | -0.023202 | -0.014583 | 0.17641 | 0.020452 | 0.0069384 | -0.036347 | -0.030721 | 0.014911 | 0.010025 | 0.004578 | 0.050354 | -0.082397 | -0.10529 | -0.027466 | -0.10071 | -0.045776 | 0.064087 | 0.10986 | -0.059509 | 0.064087 | 0.086975 | 0.064087 | 0.09613 | 61.6333 | -61.8301 | -61.9858 | 61.6882 | 61.6699 | 61.615 | 0.036621 | -0.018311 | 61.6562 | -61.7706 | -61.8164 | 61.8027 | 61.8118 | 61.7798 | 0.15564 | 0.1236 | 0.054931 | -0.022889 | 0.14648 | 0.1236 | 0.13275 | 0.16937 | 61.7661 | 61.8256 | -61.9629 | -61.94 | 61.6104 | 61.7798 | 61.7203 | 61.7798
753.4844 | 123.8342 | -61.7249 | 61.8576 | 0.049069 | 0.022082 | -0.0073647 | 0.025624 | 0.0038071 | -0.014657 | -0.0039024 | 0.10011 | 0.0097714 | 0.016551 | -0.0085763 | -0.021108 | 0.0095709 | -0.0081325 | 0.018311 | 0.068665 | -0.054932 | -0.11902 | -0.036621 | -0.11902 | -0.059509 | 0.086975 | 0.11444 | -0.073242 | 0.068665 | 0.10986 | 0.082397 | 0.09613 | 61.6699 | -61.7889 | -61.9766 | 61.6882 | 61.6653 | 61.6058 | -0.004577 | -0.064087 | 61.6516 | -61.7432 | -61.7889 | 61.8347 | 61.821 | 61.8073 | 0.16937 | 0.15564 | 0.018311 | -0.064087 | 0.18311 | 0.14191 | 0.1236 | 0.18768 | 61.7935 | 61.8393 | -61.9125 | -61.9308 | 61.6058 | 61.7935 | 61.7432 | 61.8118
754.4844 | 123.7747 | -61.7203 | 61.9217 | 0.049069 | 0.013537 | -0.0030927 | 0.030965 | 0.010216 | 0.0024328 | 0.0025066 | -0.067735 | 0.01618 | -0.01122 | -0.0043033 | -0.029653 | 0.029865 | -0.017746 | 0 | 0.073242 | -0.10071 | 0.004578 | 0.050354 | -0.022888 | 0.032043 | -0.004578 | 0.12817 | -0.091553 | 0.027466 | 0.059509 | 0.018311 | 0.054932 | 61.6196 | -61.8484 | -61.9171 | 61.7706 | 61.7523 | 61.6974 | 0.13275 | 0.07782 | 61.6287 | -61.7935 | -61.8942 | 61.7798 | 61.7752 | 61.7386 | 0.14649 | 0.10986 | 0.15106 | 0.10529 | 0.15106 | 0.11902 | 0.17395 | 0.21973 | 61.7935 | 61.8484 | -62.0224 | -62.0132 | 61.7249 | 61.7477 | 61.7203 | 61.7157
755.4844 | 123.7656 | -61.7203 | 61.9263 | -0.011967 | 0.012469 | -0.0020247 | 0.026692 | 0.018761 | -0.025338 | -0.0049704 | 0.054336 | 0.024725 | -0.0048106 | -0.029938 | -0.022176 | 0.013843 | -0.00065554 | 0 | 0.10529 | -0.086975 | 0 | 0.068665 | -0.018311 | 0.018311 | -0.004578 | 0.13275 | -0.10529 | 0.022888 | 0.068665 | 0.027466 | 0.059509 | 61.6333 | -61.821 | -61.9263 | 61.7889 | 61.7386 | 61.702 | 0.10529 | 0.068664 | 61.615 | -61.7935 | -61.9034 | 61.7889 | 61.7798 | 61.7477 | 0.16479 | 0.13275 | 0.15564 | 0.086975 | 0.17395 | 0.12817 | 0.19226 | 0.23804 | 61.8256 | 61.853 | -62.0132 | -62.0316 | 61.7203 | 61.7432 | 61.7203 | 61.7157
756.4844 | 123.7473 | -61.7294 | 61.9308 | 0.23217 | 0.010333 | -0.0062967 | 0.026692 | -0.014351 | -0.0071802 | -0.019924 | 0.19167 | 0.019384 | 0.016551 | -0.03421 | 0.00025378 | 0.010639 | 0.0025485 | -0.059509 | 0.086975 | -0.1236 | 0.036621 | 0.13275 | 0.013733 | 0.07782 | -0.086975 | 0.15106 | -0.10986 | -0.050354 | 0 | -0.022888 | 0.013733 | 61.6058 | -61.8439 | -61.8942 | 61.8622 | 61.8073 | 61.7432 | 0.20142 | 0.13733 | 61.6196 | -61.7798 | -61.9812 | 61.7294 | 61.7432 | 61.7065 | 0.1236 | 0.086975 | 0.25635 | 0.16022 | 0.10986 | 0.059509 | 0.21057 | 0.26093 | 61.8164 | 61.8805 | -62.0544 | -62.0407 | 61.7661 | 61.6791 | 61.6699 | 61.6425
757.4844 | 123.7656 | -61.734 | 61.9171 | 0.094845 | 0.018878 | -0.0062967 | 0.029896 | 0.0080791 | -0.017862 | -0.0028344 | -0.14403 | 0.010839 | 0.0015984 | 0.015991 | -0.0147 | 0.014911 | -0.016678 | -0.009155 | 0.086975 | -0.09613 | 0.004578 | 0.082397 | -0.018311 | 0.036621 | -0.018311 | 0.13733 | -0.10071 | -0.009155 | 0.009155 | -0.013733 | 0.022888 | 61.6379 | -61.8301 | -61.9125 | 61.8164 | 61.7706 | 61.7157 | 0.13275 | 0.077819 | 61.6333 | -61.7798 | -61.9263 | 61.7432 | 61.7569 | 61.7203 | 0.1236 | 0.086975 | 0.17853 | 0.10071 | 0.10986 | 0.091553 | 0.1831 | 0.23804 | 61.821 | 61.8713 | -62.0132 | -62.0178 | 61.7386 | 61.7249 | 61.7249 | 61.7157
758.4844 | 123.7747 | -61.7477 | 61.8988 | 0.049069 | 0.016741 | -0.0041607 | 0.025624 | 0.0059431 | -0.019998 | -0.031673 | -0.021958 | 0.014044 | -0.0026746 | -0.031006 | -0.02004 | 0.025593 | -0.0038605 | -0.041199 | 0.09613 | -0.10986 | 0.032043 | 0.13275 | 0.013733 | 0.041199 | -0.064087 | 0.1236 | -0.09613 | 0 | 0.004578 | -0.009155 | 0.041199 | 61.6379 | -61.8027 | -61.8668 | 61.8805 | 61.7889 | 61.7615 | 0.15106 | 0.1236 | 61.6516 | -61.7752 | -61.8988 | 61.7523 | 61.7889 | 61.7386 | 0.13733 | 0.086975 | 0.24261 | 0.14191 | 0.10071 | 0.09613 | 0.20599 | 0.21973 | 61.8439 | 61.8713 | -62.0087 | -61.9949 | 61.7798 | 61.7477 | 61.7065 | 61.6837
759.4844 | 123.7473 | -61.734 | 61.8851 | -0.027225 | 0.011401 | -0.0041607 | 0.04485 | -0.014351 | 0.0035008 | -0.019924 | -0.082994 | 0.023657 | 0.0058704 | -0.041687 | -0.0147 | 0.017048 | 0.0014805 | -0.050354 | 0.11902 | -0.10986 | 0.036621 | 0.13275 | 0.022888 | 0.050354 | -0.07782 | 0.13733 | -0.10986 | -0.018311 | -0.018311 | -0.054932 | 0.013733 | 61.6241 | -61.7661 | -61.8485 | 61.8668 | 61.7844 | 61.7569 | 0.16022 | 0.13275 | 61.6241 | -61.7477 | -61.9034 | 61.7157 | 61.7477 | 61.6791 | 0.1236 | 0.054931 | 0.24261 | 0.14648 | 0.091552 | 0.091552 | 0.22888 | 0.24719 | 61.853 | 61.8713 | -61.9949 | -61.9949 | 61.7706 | 61.7157 | 61.6837 | 61.6562
760.4844 | 123.7473 | -61.702 | 61.8988 | 0.14062 | 0.018878 | 0.0033163 | 0.037373 | 0.014488 | -0.00077219 | -0.0060384 | -0.052476 | 0.018316 | 0.0080074 | -0.027802 | -0.02004 | 0.019184 | -0.0070645 | -0.018311 | 0.09613 | -0.11902 | 0.004578 | 0.07782 | 0.004578 | 0.041199 | -0.036621 | 0.15106 | -0.10071 | -0.022888 | 0 | -0.032043 | 0.032043 | 61.5829 | -61.8027 | -61.8942 | 61.7798 | 61.7432 | 61.7065 | 0.16022 | 0.1236 | 61.6013 | -61.7477 | -61.9217 | 61.702 | 61.734 | 61.6699 | 0.13275 | 0.068665 | 0.19684 | 0.1236 | 0.10071 | 0.07782 | 0.21515 | 0.25177 | 61.7981 | 61.853 | -62.0178 | -61.9995 | 61.7065 | 61.6791 | 61.6837 | 61.6653
761.4844 | 123.7793 | -61.7294 | 61.9034 | 0.15588 | 0.010333 | -0.01057 | 0.028828 | -0.0079419 | -0.0050442 | -0.0049704 | 0.023818 | 0.027929 | 0.012279 | 0.011719 | -0.027517 | 0.019184 | -0.024155 | -0.027466 | 0.11444 | -0.10529 | 0.032043 | 0.11444 | -0.004578 | 0.059509 | -0.050354 | 0.14191 | -0.10986 | -0.004578 | 0.050354 | 0.018311 | 0.045776 | 61.6241 | -61.7889 | -61.8713 | 61.8439 | 61.7889 | 61.7249 | 0.16479 | 0.10071 | 61.6196 | -61.7615 | -61.908 | 61.7798 | 61.7752 | 61.7477 | 0.15564 | 0.12817 | 0.21973 | 0.13733 | 0.16022 | 0.10529 | 0.21973 | 0.25177 | 61.8439 | 61.8713 | -62.0087 | -62.0132 | 61.7615 | 61.7249 | 61.702 | 61.6791
762.4844 | 123.7381 | -61.7432 | 61.9217 | 0.1101 | 0.0039235 | -0.01057 | 0.025624 | 0.0048751 | 0.0045688 | -0.02206 | -0.021958 | 0.017248 | 0.010143 | -0.0085763 | -0.024313 | 0.02132 | -0.0081325 | -0.009155 | 0.086975 | -0.11902 | 0.013733 | 0.10529 | 0.004578 | 0.050354 | -0.045776 | 0.13275 | -0.09613 | -0.032043 | -0.004578 | -0.045776 | 0.013733 | 61.6241 | -61.8347 | -61.908 | 61.8484 | 61.7935 | 61.7477 | 0.16937 | 0.1236 | 61.647 | -61.7889 | -61.9537 | 61.7386 | 61.7569 | 61.6974 | 0.10986 | 0.050354 | 0.22431 | 0.13275 | 0.091552 | 0.064087 | 0.20599 | 0.22888 | 61.8301 | 61.8759 | -62.0407 | -62.0178 | 61.7569 | 61.7111 | 61.734 | 61.6974
763.4844 | 123.848 | -61.7249 | 61.8393 | -0.011967 | 0.0039235 | -0.0030927 | 0.02242 | 0.011284 | 0.0024328 | -0.00069841 | 0.20692 | 0.019384 | 0.00053042 | -0.041687 | -0.02004 | 0.013843 | -0.0070645 | 0.041199 | 0.041199 | -0.064087 | -0.11902 | -0.045776 | -0.10529 | -0.059509 | 0.07782 | 0.091553 | -0.059509 | 0.082397 | 0.10071 | 0.091553 | 0.10529 | 61.6608 | -61.7981 | -61.9583 | 61.6791 | 61.6653 | 61.6196 | 0.004578 | -0.041199 | 61.6653 | -61.7477 | -61.7569 | 61.8256 | 61.8301 | 61.8164 | 0.16479 | 0.15106 | 0.018311 | -0.054932 | 0.16022 | 0.14191 | 0.10529 | 0.15106 | 61.7661 | 61.8164 | -61.9034 | -61.8988 | 61.6058 | 61.8073 | 61.7661 | 61.8027
764.4844 | 123.7793 | -61.7477 | 61.9125 | 0.1101 | 0.018878 | -0.0030927 | 0.034169 | 0.0048751 | 0.014182 | -0.0028344 | 0.11537 | 0.017248 | 0.013347 | -0.01178 | -0.018972 | 0.027729 | 0.014297 | 0 | 0.091553 | -0.09613 | -0.013733 | 0.064087 | -0.036621 | 0.041199 | 0.009155 | 0.13733 | -0.086975 | 0.022888 | 0.050354 | 0.018311 | 0.068665 | 61.6516 | -61.821 | -61.9263 | 61.8118 | 61.7889 | 61.7111 | 0.13733 | 0.059509 | 61.6608 | -61.7752 | -61.8896 | 61.7981 | 61.8164 | 61.7661 | 0.15564 | 0.10529 | 0.16022 | 0.082397 | 0.13733 | 0.10986 | 0.18768 | 0.2243 | 61.8393 | 61.8851 | -62.0087 | -61.9995 | 61.734 | 61.7706 | 61.7477 | 61.7569
765.4844 | 123.7473 | -61.7477 | 61.94 | 0.27795 | 0.010333 | -0.01591 | 0.028828 | 0.012352 | 0.00029581 | -0.015651 | 0.26796 | 0.01618 | 0.0069384 | -0.014984 | -0.024313 | 0.017048 | 0.00041246 | -0.045776 | 0.10071 | -0.13733 | 0.041199 | 0.13275 | 0.032043 | 0.068665 | -0.082397 | 0.14648 | -0.10986 | -0.045776 | 0 | -0.027466 | 0.018311 | 61.6104 | -61.8393 | -61.8988 | 61.8805 | 61.8164 | 61.7798 | 0.20599 | 0.16937 | 61.6379 | -61.7935 | -61.9858 | 61.7477 | 61.7661 | 61.7203 | 0.12817 | 0.082397 | 0.27008 | 0.17853 | 0.10986 | 0.064087 | 0.23804 | 0.25635 | 61.8484 | 61.8942 | -62.0773 | -62.0499 | 61.7889 | 61.702 | 61.702 | 61.6653
766.4844 | 123.7427 | -61.7386 | 61.9675 | 0.20166 | 0.0017875 | -0.01057 | 0.018147 | -0.0036699 | -0.013589 | -0.016719 | 0.084853 | 0.026861 | -0.0016066 | -0.0096443 | -0.017904 | 0.012775 | -0.0070645 | -0.059509 | 0.11444 | -0.11902 | 0.045776 | 0.12817 | 0.013733 | 0.07782 | -0.086975 | 0.14648 | -0.11902 | -0.045776 | -0.004578 | -0.022888 | 0.018311 | 61.6196 | -61.853 | -61.9217 | 61.8668 | 61.8164 | 61.7523 | 0.19684 | 0.13275 | 61.6196 | -61.821 | -62.0132 | 61.734 | 61.7569 | 61.7157 | 0.13733 | 0.096131 | 0.24719 | 0.16479 | 0.11444 | 0.073243 | 0.23346 | 0.2655 | 61.853 | 61.8851 | -62.0865 | -62.0865 | 61.7844 | 61.6928 | 61.6791 | 61.6516
767.4844 | 123.7701 | -61.7569 | 61.9171 | -0.073002 | 0.012469 | -0.0084327 | 0.026692 | -0.0004649 | -0.010385 | -0.030605 | 0.069594 | 0.025793 | 0.0090754 | -0.013916 | -0.022176 | 0.014911 | -0.016678 | -0.041199 | 0.09613 | -0.1236 | 0.045776 | 0.14648 | 0.013733 | 0.07782 | -0.082397 | 0.14191 | -0.11902 | -0.032043 | -0.027466 | -0.032043 | 0.018311 | 61.6333 | -61.821 | -61.8713 | 61.9034 | 61.8347 | 61.7706 | 0.20142 | 0.13733 | 61.6379 | -61.7752 | -61.9492 | 61.7294 | 61.7752 | 61.7249 | 0.13733 | 0.086976 | 0.27008 | 0.16937 | 0.091553 | 0.086976 | 0.21973 | 0.26093 | 61.853 | 61.8988 | -62.0407 | -62.0361 | 61.8027 | 61.7249 | 61.7157 | 61.6745
768.4844 | 123.793 | -61.734 | 61.9308 | 0.094845 | 0.016741 | 0.0033163 | 0.033101 | -0.0036699 | -0.015725 | -0.0071064 | 0.084853 | 0.019384 | 0.0080074 | 0.017059 | -0.031789 | 0.02132 | -0.022018 | 0.004578 | 0.082397 | -0.082397 | -0.004578 | 0.045776 | -0.036621 | 0.032043 | 0.013733 | 0.11902 | -0.11902 | 0.009155 | 0.045776 | 0.009155 | 0.050354 | 61.6516 | -61.8484 | -61.9354 | 61.7798 | 61.7661 | 61.6974 | 0.11444 | 0.045776 | 61.615 | -61.8118 | -61.9217 | 61.7798 | 61.7844 | 61.7432 | 0.16937 | 0.12817 | 0.12817 | 0.077819 | 0.16479 | 0.12817 | 0.16479 | 0.23804 | 61.8164 | 61.853 | -62.0132 | -62.0499 | 61.7294 | 61.7432 | 61.7386 | 61.7477
769.4844 | 123.7335 | -61.7386 | 61.9354 | 0.12536 | 0.014605 | -0.0030927 | 0.009602 | 0.0027391 | -0.00077219 | 0.0014386 | -0.098252 | 0.022589 | 0.0069384 | -0.0043033 | -0.02004 | 0.022388 | -0.010269 | -0.036621 | 0.09613 | -0.10529 | 0.022888 | 0.12817 | 0.022888 | 0.07782 | -0.10986 | 0.16022 | -0.10986 | -0.045776 | -0.054932 | -0.068665 | 0 | 61.6333 | -61.8393 | -61.9125 | 61.8668 | 61.8164 | 61.7615 | 0.18311 | 0.12817 | 61.6287 | -61.7752 | -61.9812 | 61.6837 | 61.7386 | 61.6699 | 0.10986 | 0.041198 | 0.23346 | 0.12817 | 0.054931 | 0.064087 | 0.20142 | 0.27008 | 61.8347 | 61.8988 | -62.0407 | -62.0453 | 61.7615 | 61.6928 | 61.702 | 61.6287
770.4844 | 123.8297 | -61.7157 | 61.908 | 0.064327 | 0.016741 | -0.00095673 | 0.024556 | 0.012352 | 0.0024328 | -0.0028344 | 0.34425 | 0.0097714 | 0.011211 | -0.021393 | -0.011495 | 0.013843 | 0.0078895 | 0.027466 | 0.045776 | -0.07782 | -0.09613 | -0.004578 | -0.082397 | -0.013733 | 0.032043 | 0.11902 | -0.086975 | 0.018311 | 0.068665 | 0.059509 | 0.073242 | 61.6379 | -61.8622 | -62.0041 | 61.7111 | 61.702 | 61.6333 | 0.064087 | -0.004577 | 61.6287 | -61.7889 | -61.8896 | 61.7844 | 61.7889 | 61.7752 | 0.16022 | 0.14648 | 0.073242 | -0.01831 | 0.15564 | 0.10529 | 0.1236 | 0.20599 | 61.7615 | 61.8347 | -61.9858 | -61.9949 | 61.6196 | 61.734 | 61.7432 | 61.7477
771.4844 | 123.761 | -61.7569 | 61.9675 | 0.20166 | 0.0060595 | -0.0041607 | 0.028828 | 0.0027391 | -0.032815 | -0.019924 | 0.2527 | 0.014044 | 0.0037344 | -0.053437 | -0.024313 | 0.0052979 | 0.013229 | -0.041199 | 0.11444 | -0.11444 | 0.050354 | 0.10986 | 0.022888 | 0.091553 | -0.07782 | 0.16022 | -0.10071 | -0.050354 | -0.018311 | -0.022888 | 0.013733 | 61.6425 | -61.853 | -61.9171 | 61.8668 | 61.8484 | 61.7798 | 0.20599 | 0.13733 | 61.6562 | -61.8073 | -62.0178 | 61.7386 | 61.7706 | 61.734 | 0.11444 | 0.07782 | 0.2243 | 0.16479 | 0.082397 | 0.050354 | 0.22888 | 0.26093 | 61.8713 | 61.9171 | -62.0819 | -62.0682 | 61.8073 | 61.7065 | 61.7157 | 61.6791
772.4844 | 123.8113 | -61.7249 | 61.9308 | 0.12536 | 0.012469 | -0.011638 | 0.025624 | -0.0090099 | -0.01893 | -0.0092424 | -0.052476 | 0.023657 | 0.0090754 | -0.022461 | -0.018972 | 0.026661 | -0.017746 | -0.004578 | 0.068665 | -0.10071 | -0.022888 | 0.050354 | -0.027466 | 0.032043 | 0.009155 | 0.13733 | -0.10986 | 0.009155 | 0.022888 | 0.009155 | 0.050354 | 61.6241 | -61.8622 | -61.9537 | 61.7752 | 61.7569 | 61.6974 | 0.13275 | 0.073242 | 61.615 | -61.7935 | -61.9217 | 61.7477 | 61.7752 | 61.734 | 0.16022 | 0.11902 | 0.15106 | 0.07782 | 0.13275 | 0.11902 | 0.16937 | 0.24719 | 61.7935 | 61.8622 | -62.0316 | -62.0407 | 61.702 | 61.734 | 61.7203 | 61.734
773.4844 | 123.7381 | -61.7477 | 61.9354 | 0.1864 | 0.015673 | -0.0095007 | 0.034169 | 0.0091481 | -0.012521 | -0.013515 | 0.14589 | 0.023657 | 0.0080074 | -0.0032353 | -0.0093592 | 0.01598 | -0.00065554 | -0.036621 | 0.09613 | -0.10986 | 0.036621 | 0.11444 | 0.022888 | 0.073242 | -0.064087 | 0.14648 | -0.10529 | -0.054932 | -0.013733 | -0.032043 | 0.004578 | 61.6379 | -61.8393 | -61.8988 | 61.8622 | 61.821 | 61.7706 | 0.18311 | 0.13275 | 61.6425 | -61.7889 | -61.9904 | 61.734 | 61.7523 | 61.7157 | 0.10986 | 0.073243 | 0.2243 | 0.14648 | 0.091553 | 0.050354 | 0.20599 | 0.25177 | 61.8439 | 61.8942 | -62.0453 | -62.0407 | 61.7844 | 61.6928 | 61.7111 | 61.6837
774.4844 | 123.7564 | -61.7386 | 61.9171 | 0.21692 | 0.0081955 | -0.011638 | 0.025624 | 0.0080791 | -0.016794 | -0.014583 | 0.22218 | 0.022589 | 0.0069384 | -0.012848 | -0.017904 | 0.0063669 | -0.0081325 | -0.054932 | 0.10071 | -0.10529 | 0.050354 | 0.12817 | 0.018311 | 0.059509 | -0.082397 | 0.1236 | -0.10986 | -0.059509 | 0 | -0.018311 | 0.018311 | 61.6333 | -61.8164 | -61.8668 | 61.8668 | 61.7981 | 61.7569 | 0.16479 | 0.1236 | 61.6287 | -61.7935 | -61.9766 | 61.7386 | 61.7569 | 61.7203 | 0.12817 | 0.091552 | 0.23346 | 0.15564 | 0.10986 | 0.050354 | 0.20599 | 0.23346 | 61.8393 | 61.8622 | -62.0224 | -62.027 | 61.7889 | 61.6791 | 61.6837 | 61.6562
775.4844 | 123.7427 | -61.734 | 61.9537 | 0.14062 | 0.017809 | -0.019115 | 0.035237 | 0.0027391 | -0.0029082 | 0.0025066 | 0.14589 | 0.011908 | 0.015483 | -0.010712 | -0.023245 | 0.01598 | -0.0038605 | -0.045776 | 0.10529 | -0.11902 | 0.027466 | 0.13733 | 0.009155 | 0.07782 | -0.091553 | 0.13275 | -0.11902 | -0.059509 | -0.004578 | -0.041199 | 0.018311 | 61.615 | -61.8484 | -61.9263 | 61.8713 | 61.8118 | 61.7432 | 0.19684 | 0.12817 | 61.615 | -61.821 | -62.0132 | 61.7294 | 61.7523 | 61.6928 | 0.13733 | 0.07782 | 0.25635 | 0.14649 | 0.11444 | 0.05951 | 0.22431 | 0.25177 | 61.8393 | 61.8668 | -62.0728 | -62.0728 | 61.7615 | 61.6745 | 61.6882 | 61.6425
776.4844 | 123.7885 | -61.7294 | 61.9446 | 0.079586 | 0.013537 | -0.0095007 | 0.030965 | 0.0016711 | -0.013589 | -0.012447 | 0.069594 | 0.01618 | 0.010143 | -0.029938 | -0.026449 | 0.01598 | -0.010269 | -0.032043 | 0.07782 | -0.11902 | 0.041199 | 0.1236 | 0.004578 | 0.054932 | -0.07782 | 0.14648 | -0.09613 | -0.032043 | 0.018311 | 0.004578 | 0.050354 | 61.6104 | -61.8668 | -61.9034 | 61.853 | 61.7844 | 61.734 | 0.17395 | 0.1236 | 61.6333 | -61.7981 | -61.9766 | 61.7477 | 61.7798 | 61.734 | 0.14648 | 0.10071 | 0.24261 | 0.16022 | 0.11444 | 0.064087 | 0.19684 | 0.24261 | 61.8073 | 61.8759 | -62.0636 | -62.0407 | 61.7706 | 61.6974 | 61.6974 | 61.6516
777.4844 | 123.7885 | -61.734 | 61.9308 | 0.079586 | -0.0035535 | -0.0041607 | 0.02242 | 0.023033 | -0.0082492 | -0.013515 | 0.11537 | 0.023657 | 0.010143 | -0.020325 | -0.024313 | 0.019184 | 0.024979 | -0.041199 | 0.09613 | -0.11902 | 0.032043 | 0.13275 | 0.027466 | 0.059509 | -0.082397 | 0.13275 | -0.10986 | -0.045776 | 0.004578 | 0 | 0.018311 | 61.615 | -61.8347 | -61.8988 | 61.8668 | 61.7935 | 61.7615 | 0.17853 | 0.14649 | 61.6241 | -61.7981 | -61.9766 | 61.7386 | 61.7523 | 61.734 | 0.12817 | 0.10986 | 0.25177 | 0.15106 | 0.11444 | 0.064087 | 0.21515 | 0.24261 | 61.8301 | 61.8668 | -62.0499 | -62.0407 | 61.7661 | 61.6882 | 61.6928 | 61.6516
778.4844 | 123.7427 | -61.7432 | 61.9308 | 0.079586 | 0.014605 | -0.0062967 | 0.024556 | 0.0070111 | -0.0029082 | -0.023128 | 0.2527 | 0.0097714 | 0.012279 | -0.052368 | -0.013631 | 0.011707 | 0.00041246 | -0.041199 | 0.11444 | -0.1236 | 0.027466 | 0.13275 | 0.018311 | 0.07782 | -0.07782 | 0.14648 | -0.12817 | -0.059509 | -0.013733 | -0.032043 | 0.004578 | 61.6196 | -61.8164 | -61.9034 | 61.8759 | 61.821 | 61.7615 | 0.20142 | 0.14191 | 61.615 | -61.7844 | -61.9904 | 61.7294 | 61.7477 | 61.7111 | 0.13275 | 0.096131 | 0.25635 | 0.15106 | 0.11444 | 0.068665 | 0.23804 | 0.27466 | 61.8576 | 61.8896 | -62.0544 | -62.059 | 61.7706 | 61.6837 | 61.702 | 61.6653
779.4844 | 123.7564 | -61.7569 | 61.9125 | 0.049069 | 0.018878 | 0.00011227 | 0.032033 | 0.0091481 | -0.0050442 | -0.026332 | -0.098252 | 0.017248 | 0.011211 | 0.013855 | -0.022176 | 0.012775 | -0.023087 | -0.064087 | 0.086975 | -0.10986 | 0.050354 | 0.13733 | 0.009155 | 0.059509 | -0.091553 | 0.13733 | -0.10986 | -0.045776 | -0.050354 | -0.073242 | 0.013733 | 61.647 | -61.8256 | -61.8622 | 61.8942 | 61.8164 | 61.7661 | 0.16937 | 0.11902 | 61.647 | -61.7752 | -61.9583 | 61.7065 | 61.7706 | 61.6837 | 0.1236 | 0.036621 | 0.24719 | 0.16022 | 0.059509 | 0.064087 | 0.19684 | 0.24719 | 61.8439 | 61.8942 | -62.0224 | -62.0224 | 61.8073 | 61.7111 | 61.6928 | 61.6653
780.4844 | 123.7793 | -61.7294 | 61.9171 | 0.1101 | 0.011401 | -0.0052287 | 0.032033 | 0.010216 | -0.029611 | -0.0092424 | 0.23744 | 0.024725 | 0.014415 | 0.0042417 | -0.015768 | 0.011707 | -0.013474 | -0.045776 | 0.10071 | -0.1236 | 0.036621 | 0.12817 | 0.009155 | 0.068665 | -0.068665 | 0.15106 | -0.10529 | -0.013733 | 0.032043 | 0 | 0.059509 | 61.6058 | -61.8164 | -61.8805 | 61.8576 | 61.7981 | 61.7386 | 0.19226 | 0.13275 | 61.6241 | -61.7661 | -61.9308 | 61.7615 | 61.7889 | 61.7294 | 0.16479 | 0.10529 | 0.25177 | 0.16022 | 0.13733 | 0.091553 | 0.2243 | 0.25635 | 61.8301 | 61.8805 | -62.0407 | -62.0224 | 61.7661 | 61.7157 | 61.6837 | 61.6608

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.7302 | 22.491 | 22.2991 | 22.5165
0.2698 | 22.4877 | 22.3173 | 22.519
1.2698 | 22.4879 | 22.3082 | 22.5249
2.2698 | 22.4963 | 22.3074 | 22.5206
3.2698 | 22.491 | 22.3079 | 22.5189
4.2698 | 22.4872 | 22.3016 | 22.5226
5.2698 | 22.4876 | 22.3052 | 22.5165
6.2698 | 22.5528 | 22.2973 | 22.5126
7.2698 | 23.0438 | 22.3086 | 22.526
8.2698 | 24.2608 | 22.3039 | 22.517
9.2698 | 26.1706 | 22.3106 | 22.5162
10.2698 | 28.6933 | 22.3 | 22.5188
11.2698 | 31.7409 | 22.3028 | 22.5238
12.2698 | 35.2016 | 22.3188 | 22.528
13.2698 | 39.011 | 22.3199 | 22.535
14.2698 | 43.1346 | 22.3228 | 22.5378
15.2698 | 47.499 | 22.3308 | 22.5551
16.2698 | 52.0862 | 22.3438 | 22.5657
17.2698 | 56.8219 | 22.3686 | 22.5799
18.2698 | 61.7806 | 22.3888 | 22.6126
19.2698 | 66.8919 | 22.4126 | 22.6447
20.2698 | 72.1381 | 22.4348 | 22.6797
21.2698 | 77.5371 | 22.4744 | 22.7166
22.2698 | 82.9888 | 22.5242 | 22.7627
23.2698 | 88.6078 | 22.5786 | 22.8161
24.2698 | 94.3031 | 22.6238 | 22.8734
25.2698 | 100.0741 | 22.6937 | 22.9296
26.2698 | 105.9765 | 22.7671 | 23.0074
27.2698 | 111.9337 | 22.8467 | 23.0903
28.2698 | 117.9062 | 22.9457 | 23.1813
29.2698 | 123.9432 | 23.0418 | 23.2821
30.2698 | 129.9781 | 23.1474 | 23.3865
31.2698 | 136.0854 | 23.2752 | 23.5018
32.2698 | 142.2027 | 23.4016 | 23.6305
33.2698 | 148.2318 | 23.555 | 23.7713
34.2698 | 154.2144 | 23.7105 | 23.9192
35.2698 | 160.1805 | 23.8805 | 24.0833
36.2698 | 166.1434 | 24.0583 | 24.2593
37.2698 | 172.0702 | 24.2647 | 24.4512
38.2698 | 177.9881 | 24.4835 | 24.6631
39.2698 | 183.9709 | 24.7179 | 24.885
40.2698 | 189.9352 | 24.9515 | 25.1266
41.2698 | 195.9491 | 25.2259 | 25.384
42.2698 | 201.9109 | 25.4913 | 25.6624
43.2698 | 207.7386 | 25.7835 | 25.955
44.2698 | 213.6934 | 26.0973 | 26.2549
45.2698 | 219.8009 | 26.4272 | 26.5764
46.2698 | 225.5575 | 26.7558 | 26.8994
47.2698 | 231.5022 | 27.126 | 27.2566
48.2698 | 237.3828 | 27.4945 | 27.6207
49.2698 | 243.1832 | 27.885 | 28.0019
50.2698 | 249.084 | 28.3112 | 28.3982
51.2698 | 254.9237 | 28.745 | 28.809
52.2698 | 260.7715 | 29.1946 | 29.2463
53.2698 | 266.6107 | 29.6688 | 29.7086
54.2698 | 272.4252 | 30.1518 | 30.1784
55.2698 | 278.2004 | 30.6736 | 30.6683
56.2698 | 283.9615 | 31.2034 | 31.1687
57.2698 | 289.5743 | 31.7573 | 31.6936
58.2698 | 295.1835 | 32.3216 | 32.2229
59.2698 | 300.8653 | 32.8979 | 32.7544
60.2698 | 306.322 | 33.4942 | 33.3108
61.2698 | 311.8257 | 34.1293 | 33.8846
62.2698 | 317.5223 | 34.7819 | 34.4737
63.2698 | 323.0729 | 35.4578 | 35.0872
64.2698 | 328.448 | 36.1545 | 35.7246
65.2698 | 333.7927 | 36.854 | 36.3887
66.2698 | 339.2736 | 37.5829 | 37.0899
67.2698 | 344.6291 | 38.331 | 37.8027
68.2698 | 349.9209 | 39.1154 | 38.542
69.2698 | 355.2079 | 39.9101 | 39.3161
70.2698 | 360.4506 | 40.7247 | 40.1113
71.2698 | 365.7272 | 41.5845 | 40.9343
72.2698 | 370.9468 | 42.4658 | 41.7793
73.2698 | 376.1656 | 43.3494 | 42.6393
74.2698 | 381.3804 | 44.2729 | 43.5154
75.2698 | 386.5086 | 45.2005 | 44.4087
76.2854 | 391.5472 | 46.178 | 45.3464
77.2698 | 396.6491 | 47.1475 | 46.2781
78.2698 | 401.6049 | 48.159 | 47.2465
79.2698 | 406.405 | 49.196 | 48.2471
80.2698 | 411.3314 | 50.2643 | 49.272
81.2698 | 416.1234 | 51.3694 | 50.334
82.2698 | 421.151 | 52.4831 | 51.4217
83.2698 | 426.0034 | 53.6406 | 52.5284
84.2698 | 430.6902 | 54.8332 | 53.6516
85.2698 | 435.0075 | 56.0702 | 54.8015
86.2698 | 438.8887 | 57.3317 | 55.9768
87.2698 | 442.4805 | 58.6423 | 57.1809
88.2698 | 445.8724 | 59.9806 | 58.4009
89.2698 | 448.9641 | 61.3585 | 59.634
90.2698 | 451.8941 | 62.7491 | 60.9002
91.2698 | 454.7123 | 64.142 | 62.1615
92.2698 | 457.5293 | 65.5572 | 63.4375
93.2698 | 460.3226 | 66.9643 | 64.7252
94.2698 | 462.8651 | 68.3922 | 66.0223
95.2698 | 465.196 | 69.8327 | 67.3252
96.2698 | 467.3977 | 71.2662 | 68.6407
97.2698 | 469.3754 | 72.6794 | 69.9802
98.2698 | 471.1095 | 74.1397 | 71.3156
99.2698 | 472.734 | 75.6253 | 72.6569
100.2698 | 473.9853 | 77.1169 | 74.0176
101.2698 | 474.9146 | 78.6089 | 75.3757
102.2698 | 475.4667 | 80.1071 | 76.7434
103.2698 | 476.1443 | 81.618 | 78.1159
104.2698 | 476.6475 | 83.1011 | 79.5004
105.2698 | 477.087 | 84.5986 | 80.8802
106.2698 | 477.1312 | 86.0883 | 82.2548
107.2698 | 477.2628 | 87.5663 | 83.6128
108.2698 | 477.3086 | 89.048 | 84.9813
109.2698 | 477.4311 | 90.5147 | 86.3355
110.2698 | 477.4721 | 91.9791 | 87.6896
111.2698 | 477.3296 | 93.4424 | 89.0547
112.2698 | 477.1346 | 94.8779 | 90.3971
113.2698 | 477.0401 | 96.3135 | 91.7417
114.2698 | 476.9742 | 97.7575 | 93.0663
115.2698 | 476.9953 | 99.1759 | 94.384
116.2698 | 476.9509 | 100.5832 | 95.7002
117.2698 | 476.828 | 101.9921 | 97.0062
118.2698 | 476.7354 | 103.3867 | 98.3119
119.2698 | 476.7146 | 104.7775 | 99.603
120.2698 | 476.6491 | 106.1504 | 100.8808
121.2698 | 476.4142 | 107.5204 | 102.1493
122.2698 | 476.3533 | 108.8646 | 103.4235
123.2698 | 476.2999 | 110.2007 | 104.6803
124.2698 | 476.2063 | 111.531 | 105.9282
125.2698 | 476.3806 | 112.8502 | 107.1909
126.2698 | 476.3505 | 114.1464 | 108.4289
127.2698 | 476.3346 | 115.4582 | 109.6698
128.2698 | 476.4894 | 116.7551 | 110.8936
129.2698 | 476.6733 | 118.0507 | 112.1224
130.2698 | 476.8579 | 119.3289 | 113.3447
131.2698 | 476.9116 | 120.5955 | 114.5614
132.2698 | 477.1252 | 121.861 | 115.7743
133.2698 | 477.2443 | 123.1133 | 117.006
134.2698 | 477.2605 | 124.3659 | 118.2078
135.2698 | 477.3237 | 125.6171 | 119.4104
136.2698 | 477.4589 | 126.8784 | 120.6061
137.2698 | 477.6078 | 128.1174 | 121.7957
138.2698 | 477.6125 | 129.3624 | 122.9767
139.2698 | 477.5703 | 130.6019 | 124.1521
140.2698 | 477.7008 | 131.8337 | 125.3297
141.2698 | 477.813 | 133.0527 | 126.5134
142.2698 | 478.0558 | 134.2767 | 127.6684
143.2698 | 478.1135 | 135.4986 | 128.8215
144.2698 | 478.0896 | 136.7186 | 129.9572
145.2698 | 478.1169 | 137.9331 | 131.092
146.2698 | 477.9815 | 139.1524 | 132.2121
147.2698 | 477.9666 | 140.3588 | 133.3161
148.2698 | 477.9746 | 141.5522 | 134.407
149.2698 | 478.0226 | 142.7456 | 135.4844
150.2698 | 478.152 | 143.9358 | 136.5564
151.2698 | 478.1745 | 145.1177 | 137.5919
152.2698 | 478.1025 | 146.3053 | 138.6258
153.2698 | 478.2379 | 147.4777 | 139.6294
154.2698 | 478.3978 | 148.6392 | 140.6171
155.2698 | 478.4826 | 149.796 | 141.6037
156.2698 | 478.5327 | 150.9477 | 142.5782
157.2698 | 478.5135 | 152.0913 | 143.5322
158.2698 | 478.5995 | 153.2323 | 144.4886
159.2698 | 478.6442 | 154.3641 | 145.4261
160.2698 | 478.6971 | 155.5119 | 146.3574
161.2698 | 478.7341 | 156.6371 | 147.2703
162.2698 | 478.716 | 157.7432 | 148.1813
163.2698 | 478.537 | 158.8694 | 149.0686
164.2698 | 478.4676 | 159.9645 | 149.9601
165.2698 | 478.4968 | 161.0476 | 150.8491
166.2698 | 478.438 | 162.1317 | 151.7363
167.2698 | 478.4055 | 163.2018 | 152.6105
168.2698 | 478.4357 | 164.2627 | 153.5004
169.2698 | 478.4932 | 165.3235 | 154.3818
170.2698 | 478.5863 | 166.3688 | 155.2835
171.2698 | 478.6921 | 167.4017 | 156.1565
172.2698 | 478.7521 | 168.4351 | 157.0352
173.2698 | 478.7674 | 169.4478 | 157.9253
174.2698 | 478.8121 | 170.4629 | 158.8004
175.2698 | 478.7443 | 171.4594 | 159.6739
176.2698 | 478.8012 | 172.4553 | 160.5406
177.2698 | 478.9109 | 173.4405 | 161.4045
178.2698 | 479.0654 | 174.4205 | 162.2694
179.2698 | 479.2192 | 175.3912 | 163.1321
180.2698 | 479.2064 | 176.3501 | 163.9939
181.2698 | 479.1677 | 177.2912 | 164.8641
182.2698 | 479.2042 | 178.2421 | 165.7193
183.2698 | 479.2472 | 179.1651 | 166.5839
184.2698 | 479.2247 | 180.0969 | 167.4535
185.2698 | 479.1213 | 181.0172 | 168.3177
186.2698 | 479.092 | 181.9381 | 169.1977
187.2698 | 479.0596 | 182.8632 | 170.0748
188.2698 | 478.939 | 183.7738 | 170.9664
189.2698 | 478.942 | 184.6965 | 171.8574
190.2698 | 478.9828 | 185.5957 | 172.7565
191.2698 | 478.824 | 186.4875 | 173.6571
192.2698 | 478.7618 | 187.3801 | 174.561
193.2698 | 478.7223 | 188.2629 | 175.4802
194.2698 | 478.6582 | 189.1335 | 176.3914
195.2698 | 478.6655 | 189.9982 | 177.2957
196.2698 | 478.5104 | 190.8667 | 178.2079
197.2698 | 478.4201 | 191.7216 | 179.1091
198.2698 | 478.2126 | 192.5782 | 180.0216
199.2698 | 478.1683 | 193.4412 | 180.9344
200.2698 | 478.2317 | 194.3176 | 181.8453
201.2698 | 478.2117 | 195.1978 | 182.7521
202.2698 | 478.1216 | 196.0617 | 183.6735
203.2698 | 478.1311 | 196.9439 | 184.5933
204.2698 | 478.0368 | 197.8257 | 185.5081
205.2698 | 477.9513 | 198.7058 | 186.4281
206.2698 | 477.9065 | 199.5889 | 187.3406
207.2698 | 477.8291 | 200.4698 | 188.2468
208.2698 | 477.8121 | 201.3702 | 189.1254
209.2698 | 477.8636 | 202.2659 | 190.0104
210.2698 | 477.8223 | 203.1564 | 190.8946
211.2698 | 477.9096 | 204.0737 | 191.7839
212.2698 | 477.7475 | 204.9592 | 192.6752
213.2698 | 477.6775 | 205.8409 | 193.5573
214.2698 | 477.6077 | 206.7302 | 194.4591
215.2698 | 477.6174 | 207.5959 | 195.3457
216.2698 | 477.6773 | 208.4842 | 196.2321
217.2698 | 477.5504 | 209.3444 | 197.1196
218.2698 | 477.4529 | 210.2151 | 198.0081
219.2698 | 477.1897 | 211.0906 | 198.8822
220.2698 | 477.1634 | 211.9512 | 199.7696
221.2698 | 477.069 | 212.8206 | 200.6362
222.2698 | 477.0011 | 213.6953 | 201.5277
223.2698 | 476.8933 | 214.57 | 202.3953
224.2698 | 476.7787 | 215.4353 | 203.2751
225.2698 | 476.6036 | 216.3023 | 204.1672
226.2698 | 476.5649 | 217.1718 | 205.0317
227.2698 | 476.4906 | 218.0476 | 205.8944
228.2698 | 476.3479 | 218.9003 | 206.7604
229.2698 | 476.3169 | 219.7513 | 207.6276
230.2698 | 476.2441 | 220.3319 | 208.4968
231.2698 | 476.1222 | 220.9645 | 209.3731
232.2698 | 475.9744 | 221.7239 | 210.2508
233.2698 | 475.8608 | 222.4821 | 211.1258
234.2698 | 475.7567 | 223.3591 | 212.0137
235.2698 | 475.8275 | 224.2534 | 212.9021
236.2698 | 475.82 | 225.1528 | 213.7939
237.2698 | 475.8584 | 226.0572 | 214.6688
238.2698 | 475.8309 | 226.9037 | 215.5432
239.2698 | 475.8342 | 227.6301 | 216.408
240.2698 | 475.8289 | 228.3838 | 217.2442
241.2698 | 475.925 | 229.1534 | 218.0564
242.2698 | 476.1058 | 229.9303 | 218.8282
243.2698 | 476.1514 | 230.7706 | 219.5088
244.2698 | 476.1765 | 231.6228 | 219.933
245.2698 | 476.3364 | 232.4935 | 220.1857
246.2698 | 476.363 | 233.3504 | 220.1129
247.2698 | 476.4418 | 234.1792 | 220.014
248.2698 | 476.4817 | 235.127 | 220.0137
249.2698 | 476.4603 | 236.0091 | 220.05
250.2698 | 476.4709 | 236.8396 | 220.0776
251.2698 | 476.3767 | 237.6334 | 220.0859
252.2698 | 476.4718 | 238.4019 | 220.0825
253.2698 | 476.4962 | 239.1566 | 220.0854
254.2698 | 476.5027 | 239.8873 | 220.1064
255.2698 | 476.4451 | 240.578 | 220.1474
256.2698 | 476.3562 | 241.2623 | 220.1847
257.2698 | 476.2527 | 241.9037 | 220.2416
258.2698 | 476.1418 | 242.5395 | 220.3172
259.2698 | 476.1404 | 243.127 | 220.378
260.2698 | 475.9672 | 243.6496 | 220.4223
261.2698 | 475.8948 | 244.1172 | 220.4414
262.2698 | 475.8055 | 244.4915 | 220.4473
263.2698 | 475.7669 | 244.8996 | 220.4577
264.2698 | 475.7751 | 245.2007 | 220.4876
265.2698 | 475.7905 | 245.5147 | 220.5372
266.2698 | 475.6736 | 245.8457 | 220.5867
267.2698 | 475.5446 | 246.104 | 220.6542
268.2698 | 475.556 | 246.384 | 220.7514
269.2698 | 475.5498 | 246.6735 | 220.8689
270.2698 | 475.6128 | 246.9646 | 221.0145
271.2698 | 475.5724 | 247.6621 | 221.1744
272.2698 | 475.5689 | 248.0003 | 221.3504
273.2698 | 475.5861 | 248.3376 | 221.5453
274.2698 | 475.4458 | 248.6505 | 221.7543
275.2698 | 475.3302 | 249.0524 | 221.99
276.2698 | 475.3287 | 249.3643 | 222.2168
277.2698 | 475.289 | 249.6122 | 222.4628
278.2698 | 475.2773 | 249.9385 | 222.736
279.2698 | 475.3606 | 250.4763 | 223.0789
280.2698 | 475.4603 | 250.9409 | 223.4295
281.2698 | 475.5053 | 251.4092 | 223.8298
282.2698 | 475.4131 | 251.8465 | 224.2886
283.2698 | 475.3994 | 252.1985 | 224.778
284.2698 | 475.4525 | 252.7553 | 225.3092
285.2698 | 475.4156 | 253.2486 | 225.8822
286.2698 | 475.3655 | 253.6835 | 226.5223
287.2698 | 475.3933 | 254.1143 | 227.2515
288.2698 | 475.29 | 254.5346 | 228.1138
289.2698 | 475.1866 | 255.0142 | 229.0585
290.2698 | 475.2083 | 255.7404 | 230.0804
291.2698 | 475.1281 | 256.1773 | 231.226
292.2698 | 475.0368 | 256.5913 | 232.4231
293.2698 | 474.9668 | 257.0866 | 233.6722
294.2698 | 474.8904 | 257.5565 | 234.9293
295.2698 | 474.8596 | 257.9942 | 236.2004
296.2698 | 474.7848 | 258.4548 | 237.497
297.2698 | 474.7014 | 259.021 | 238.7696
298.2698 | 474.5999 | 259.2769 | 240.1096
299.2698 | 474.6497 | 259.4663 | 241.6021
300.2698 | 474.6284 | 259.5644 | 243.2937
301.2698 | 474.8007 | 259.2211 | 244.9997
302.2698 | 475.0943 | 258.1677 | 246.6539
303.2698 | 475.4969 | 256.7151 | 248.3466
304.2698 | 475.914 | 255.6047 | 250.1801
305.2698 | 476.2513 | 254.8528 | 252.0505
306.2698 | 476.4277 | 254.371 | 254.1389
307.2698 | 476.651 | 254.1036 | 256.5637
308.2698 | 476.7583 | 254.0825 | 259.5641
309.2698 | 476.7391 | 254.2862 | 262.3313
310.2698 | 476.9063 | 254.6854 | 264.6324
311.2698 | 476.9795 | 255.4662 | 266.5533
312.2698 | 476.8735 | 256.4357 | 267.5821
313.2698 | 476.7106 | 257.6064 | 269.0985
314.2698 | 476.6786 | 259.0389 | 270.5407
315.2698 | 476.4547 | 260.2374 | 272.2118
316.2698 | 476.2461 | 261.3839 | 273.9567
317.2698 | 476.0166 | 262.4704 | 275.7545
318.2698 | 475.6566 | 264.4339 | 277.3244
319.2698 | 475.2996 | 266.1161 | 279.0424
320.2698 | 475.0466 | 266.8472 | 281.1309
321.2698 | 474.882 | 268.084 | 283.2945
322.2698 | 474.6005 | 269.8231 | 285.7719
323.2698 | 474.3705 | 270.7527 | 287.8103
324.2698 | 474.041 | 272.079 | 290.03
325.2698 | 473.5721 | 273.2576 | 291.5018
326.2698 | 473.3656 | 274.1821 | 292.3784
327.2698 | 473.0661 | 275.1161 | 293.4143
328.2698 | 472.8279 | 276.1188 | 293.6655
329.2698 | 472.5839 | 276.3745 | 294.7068
330.2698 | 472.3504 | 277.8338 | 295.8899
331.2698 | 472.1636 | 278.73 | 297.1279
332.2698 | 472.0287 | 280.5951 | 298.3169
333.2698 | 471.8271 | 281.5153 | 299.4076
334.2698 | 471.6416 | 283.0342 | 300.554
335.2698 | 471.4908 | 283.085 | 301.3302
336.2698 | 471.1851 | 284.3496 | 302.1228
337.2698 | 470.924 | 285.4782 | 302.9578
338.2698 | 470.7833 | 286.1186 | 303.4034
339.2698 | 470.6203 | 287.5143 | 303.7768
340.2698 | 470.5043 | 287.1892 | 304.2871
341.2698 | 470.3791 | 289.3261 | 305.973
342.2698 | 470.2044 | 290.4663 | 306.7373
343.2698 | 470.0735 | 290.3843 | 307.6664
344.2698 | 469.9536 | 291.4968 | 309.165
345.2698 | 469.8463 | 292.9032 | 310.6267
346.2698 | 469.7556 | 292.974 | 311.4662
347.2698 | 469.6703 | 294.0873 | 312.1662
348.2698 | 469.7296 | 295.0136 | 313.5297
349.2698 | 469.7756 | 296.4702 | 315.0102
350.2698 | 469.7177 | 296.8415 | 315.3719
351.2698 | 469.6392 | 296.8029 | 316.021
352.2698 | 469.667 | 298.3808 | 317.5894
353.2698 | 469.6419 | 298.873 | 318.3209
354.2698 | 469.6223 | 301.4259 | 319.6516
355.2698 | 469.5349 | 301.3694 | 320.1626
356.2698 | 469.5714 | 302.0527 | 321.3025
357.2698 | 469.6244 | 302.8987 | 322.4562
358.2698 | 469.6912 | 303.6029 | 323.4974
359.2698 | 469.7382 | 304.2572 | 324.6395
360.2698 | 469.8415 | 306.1951 | 325.9177
361.2698 | 469.8879 | 305.7059 | 326.6989
362.2698 | 469.9925 | 306.3489 | 328.3163
363.2698 | 470.0563 | 307.8437 | 330.1155
364.2698 | 470.1387 | 308.9737 | 331.6437
365.2698 | 470.1689 | 310.4027 | 332.8943
366.2698 | 470.2324 | 311.0124 | 334.3574
367.2698 | 470.2715 | 312.5428 | 335.9858
368.2698 | 470.4189 | 313.425 | 337.167
369.2698 | 470.4609 | 314.2632 | 338.3982
370.2698 | 470.4509 | 314.5171 | 339.39
371.2698 | 470.5252 | 316.9306 | 340.3926
372.2698 | 470.5966 | 318.3683 | 342.1307
373.2698 | 470.6509 | 319.1176 | 343.2402
374.2698 | 470.7435 | 320.963 | 343.7891
375.2698 | 470.8304 | 322.3041 | 345.1312
376.2698 | 470.8919 | 323.676 | 346.3169
377.2698 | 470.9436 | 325.1223 | 347.0366
378.2698 | 470.9517 | 326.6138 | 348.3762
379.2698 | 470.9639 | 327.7688 | 349.459
380.2698 | 471.0382 | 329.9859 | 350.5253
381.2698 | 471.054 | 330.6348 | 351.4146
382.2698 | 471.016 | 332.4328 | 353.0733
383.2698 | 470.9975 | 333.6521 | 354.5817
384.2698 | 470.9174 | 335.172 | 355.8646
385.2698 | 470.9224 | 336.643 | 357.1666
386.2698 | 470.9539 | 337.7205 | 359.0446
387.2698 | 470.9592 | 338.8089 | 360.9416
388.2698 | 470.8615 | 340.0978 | 362.0829
389.2698 | 470.7871 | 341.429 | 363.5699
390.2698 | 470.6731 | 342.6176 | 364.6769
391.2698 | 470.6364 | 343.9005 | 366.3025
392.2698 | 470.6958 | 345.3633 | 367.259
393.2698 | 470.7309 | 346.2316 | 368.1757
394.2698 | 470.7787 | 347.4129 | 369.4886
395.2698 | 470.7525 | 349.0009 | 370.0589
396.2698 | 470.6966 | 349.4074 | 370.9941
397.2698 | 470.7558 | 350.4568 | 371.9677
398.2698 | 470.8085 | 352.2121 | 373.3748
399.2698 | 470.8207 | 353.6784 | 374.4442
400.2698 | 470.7918 | 354.4543 | 375.7719
401.2698 | 470.8435 | 355.3119 | 376.4276
402.2698 | 470.8703 | 356.4495 | 377.3944
403.2698 | 470.959 | 357.5287 | 378.247
404.2698 | 471.0154 | 358.4921 | 379.1081
405.2698 | 471.1538 | 359.2383 | 379.681
406.2698 | 471.2134 | 360.7361 | 380.4953
407.2698 | 471.2023 | 361.5748 | 380.9612
408.2698 | 471.2846 | 362.332 | 381.7519
409.2698 | 471.3667 | 363.6073 | 381.7572
410.2698 | 471.4138 | 364.3341 | 382.2749
411.2698 | 471.521 | 365.6515 | 382.9215
412.2698 | 471.5914 | 366.6544 | 383.3018
413.2698 | 471.5689 | 367.571 | 383.6802
414.2698 | 471.6697 | 368.5747 | 383.5449
415.2698 | 471.7865 | 369.3929 | 383.5702
416.2698 | 471.8534 | 370.3842 | 384.1558
417.2698 | 471.8605 | 371.2101 | 384.2051
418.2698 | 471.9533 | 372.1453 | 384.194
419.2698 | 472.0005 | 373.0453 | 384.0037
420.2854 | 472.0046 | 373.8357 | 384.2356
421.2698 | 471.9897 | 374.8062 | 384.3004
422.2698 | 471.9255 | 375.6973 | 385.0694
423.2698 | 471.8928 | 376.2894 | 384.606
424.2698 | 471.8488 | 377.3758 | 384.0799
425.2698 | 471.8435 | 378.1897 | 384.5317
426.2698 | 471.8054 | 379.0709 | 385.2631
427.2698 | 471.7144 | 379.7786 | 385.1288
428.2698 | 471.6856 | 380.4265 | 385.1794
429.2698 | 471.7133 | 381.104 | 385.6659
430.2698 | 471.6221 | 381.7976 | 385.9512
431.2698 | 471.6139 | 382.499 | 385.8398
432.2698 | 471.6652 | 383.0352 | 385.8952
433.2698 | 471.6918 | 383.8251 | 386.6271
434.2698 | 471.688 | 384.3559 | 386.3716
435.2698 | 471.6485 | 385.1531 | 386.7729
436.2698 | 471.663 | 385.7316 | 387.1151
437.2698 | 471.584 | 385.9939 | 387.3372
438.2698 | 471.553 | 386.3834 | 387.2564
439.2698 | 471.5455 | 386.8674 | 387.7528
440.2698 | 471.5339 | 387.2245 | 388.0085
441.2698 | 471.4763 | 387.5382 | 388.2444
442.2698 | 471.5275 | 388.0962 | 388.4717
443.2698 | 471.5613 | 388.5479 | 388.7987
444.2698 | 471.5618 | 388.9821 | 389.0348
445.2698 | 471.5975 | 389.4096 | 389.76
446.2698 | 471.6034 | 389.6699 | 389.8535
447.2698 | 471.661 | 390.0883 | 389.4152
448.2698 | 471.6144 | 390.2786 | 389.6458
449.2698 | 471.5147 | 390.6867 | 389.7443
450.2698 | 471.5368 | 390.7822 | 389.7659
451.2698 | 471.6247 | 391.0411 | 390.1212
452.2698 | 471.5296 | 391.3325 | 390.3815
453.2698 | 471.5907 | 391.5297 | 390.7253
454.2698 | 471.5548 | 392.0285 | 391.2048
455.2698 | 471.5962 | 392.2395 | 391.8373
456.2698 | 471.6609 | 392.7899 | 391.7622
457.2698 | 471.6893 | 393.2675 | 392.278
458.2698 | 471.742 | 393.7346 | 393.114
459.2698 | 471.8025 | 394.3692 | 393.8731
460.2698 | 471.6915 | 394.947 | 393.9743
461.2698 | 471.6733 | 395.6757 | 394.1666
462.2698 | 471.7361 | 396.2904 | 394.8923
463.2698 | 471.8903 | 397.0274 | 395.5538
464.2698 | 471.9775 | 397.9595 | 395.8926
465.2698 | 472.0613 | 398.8505 | 396.542
466.2698 | 472.1506 | 399.858 | 397.444
467.2698 | 472.2626 | 400.7849 | 397.8991
468.2698 | 472.3109 | 401.732 | 398.3844
469.2698 | 472.4327 | 402.9278 | 399.3107
470.2698 | 472.5971 | 403.9503 | 400.154
471.2698 | 472.6941 | 404.9878 | 400.7637
472.2698 | 472.7001 | 405.8636 | 401.2495
473.2698 | 472.7113 | 406.8744 | 401.8233
474.2698 | 472.7233 | 407.9813 | 402.6414
475.2698 | 472.6866 | 408.8996 | 403.1316
476.2698 | 472.7924 | 409.9449 | 404.2329
477.2698 | 472.8788 | 410.9874 | 404.5338
478.2698 | 472.929 | 412.018 | 405.0354
479.2698 | 472.8907 | 412.9615 | 405.4967
480.2698 | 472.8399 | 414.1003 | 406.2047
481.2698 | 472.8288 | 415.1597 | 406.7287
482.2698 | 472.805 | 416.4256 | 407.6835
483.2698 | 472.7969 | 417.3443 | 408.3539
484.2698 | 472.7957 | 418.5085 | 408.9718
485.2698 | 472.7207 | 419.8239 | 409.7438
486.2698 | 472.8016 | 421.0018 | 410.3319
487.2698 | 472.8179 | 422.1461 | 410.9519
488.2698 | 472.7886 | 423.4661 | 411.6177
489.2698 | 472.8002 | 424.609 | 411.9351
490.2698 | 472.7466 | 425.8818 | 412.8708
491.2698 | 472.6867 | 427.3844 | 413.5171
492.2698 | 472.7184 | 428.5531 | 414.2655
493.2698 | 472.7105 | 429.8849 | 414.7781
494.2698 | 472.8112 | 431.0623 | 415.4519
495.2698 | 472.9168 | 432.3 | 415.7438
496.2698 | 472.913 | 433.6172 | 416.6407
497.2698 | 472.9494 | 434.7951 | 416.884
498.2698 | 472.9248 | 435.918 | 417.708
499.2698 | 472.8979 | 437.1746 | 418.3327
500.2698 | 472.8525 | 438.5124 | 418.8907
501.2698 | 472.8246 | 439.3952 | 419.2039
502.2698 | 472.8788 | 440.5487 | 419.7796
503.2698 | 472.9027 | 441.6854 | 420.5858
504.2698 | 472.9326 | 442.7949 | 420.7949
505.2698 | 472.9323 | 443.9333 | 421.2987
506.2698 | 472.9376 | 445.1388 | 422.213
507.2698 | 472.8733 | 446.2266 | 422.7015
508.2698 | 472.7598 | 447.3097 | 423.2252
509.2698 | 472.6781 | 448.4646 | 423.5123
510.2698 | 472.6993 | 449.8465 | 424.0584
511.2698 | 472.7053 | 451.0575 | 424.8059
512.2698 | 472.7013 | 451.9142 | 425.3625
513.2698 | 472.728 | 452.7256 | 425.7827
514.2698 | 472.7957 | 453.5487 | 426.5893
515.2698 | 472.8013 | 454.3865 | 427.0967
516.2698 | 472.7357 | 455.4187 | 427.4181
517.2698 | 472.7082 | 456.1601 | 428.0192
518.2698 | 472.6775 | 456.8766 | 428.6101
519.2698 | 472.6697 | 457.8105 | 429.1302
520.2698 | 472.6387 | 458.4725 | 429.6959
521.2698 | 472.6243 | 459.0696 | 430.357
522.2698 | 472.6205 | 459.7353 | 431.0207
523.2698 | 472.6233 | 460.4624 | 431.6594
524.2698 | 472.6035 | 461.0556 | 432.0849
525.2698 | 472.5609 | 461.7119 | 432.7646
526.2698 | 472.4967 | 462.216 | 433.4201
527.2698 | 472.448 | 462.6938 | 434.0697
528.2698 | 472.406 | 463.3033 | 434.7328
529.2698 | 472.4071 | 463.3391 | 435.3919
530.2698 | 472.4541 | 463.8733 | 435.9858
531.2698 | 472.4365 | 464.2787 | 436.773
532.2698 | 472.4296 | 464.2062 | 437.3269
533.2698 | 472.4774 | 464.513 | 438.043
534.2698 | 472.5888 | 464.9156 | 438.6429
535.2698 | 472.6318 | 465.0442 | 439.3739
536.2698 | 472.5458 | 465.2986 | 440.0356
537.2698 | 472.4773 | 465.4686 | 440.5457
538.2698 | 472.4812 | 465.6731 | 441.463
539.2698 | 472.5385 | 465.781 | 442.0946
540.2698 | 472.5618 | 465.4179 | 442.6317
541.2698 | 472.5687 | 465.8526 | 443.4101
542.2698 | 472.5785 | 466.3063 | 444.2572
543.2698 | 472.5821 | 466.2935 | 444.8471
544.2698 | 472.5759 | 466.5488 | 445.3399
545.2698 | 472.4813 | 467.0587 | 446.0465
546.2698 | 472.5066 | 467.0244 | 446.8545
547.2698 | 472.5804 | 467.379 | 447.4529
548.2698 | 472.5824 | 467.3428 | 448.133
549.2698 | 472.6236 | 467.3454 | 449.3304
550.2698 | 472.6843 | 467.5653 | 450.1148
551.2698 | 472.764 | 467.6592 | 450.8544
552.2698 | 472.7277 | 467.5782 | 451.66
553.2698 | 472.7571 | 467.7613 | 452.3453
554.2698 | 472.7724 | 467.6617 | 452.849
555.2698 | 472.8016 | 467.5903 | 453.6637
556.2698 | 472.7686 | 467.3553 | 454.2501
557.2698 | 472.6623 | 467.2808 | 454.7233
558.2698 | 472.7164 | 467.125 | 455.3016
559.2698 | 472.7354 | 467.2944 | 455.7481
560.2698 | 472.8362 | 467.4112 | 456.4808
561.2698 | 472.7712 | 467.2987 | 456.818
562.2698 | 472.8108 | 467.1888 | 457.2705
563.2698 | 472.8721 | 466.8664 | 457.5645
564.2698 | 472.8931 | 466.6215 | 457.8187
565.2698 | 472.8842 | 466.3252 | 458.0832
566.2698 | 472.9593 | 466.3887 | 458.7116
567.2698 | 472.9634 | 465.9874 | 459.1218
568.2698 | 472.8521 | 465.6802 | 459.6065
569.2698 | 472.7434 | 465.5539 | 460.0828
570.2698 | 472.8093 | 464.8821 | 460.3425
571.2698 | 472.8306 | 464.9205 | 460.6057
572.2698 | 472.8463 | 464.4762 | 460.99
573.2698 | 472.7971 | 464.2018 | 461.2675
574.2698 | 472.7927 | 463.8904 | 461.3551
575.2698 | 472.8467 | 463.4674 | 461.7401
576.2698 | 472.7985 | 463.348 | 461.9151
577.2698 | 472.7847 | 463.1436 | 462.2274
578.2698 | 472.7357 | 462.7125 | 462.3565
579.2698 | 472.7539 | 462.7929 | 462.7158
580.2698 | 472.7945 | 462.8013 | 462.9866
581.2698 | 472.807 | 462.568 | 463.3086
582.2698 | 472.804 | 462.9851 | 463.9693
583.2698 | 472.808 | 463.209 | 464.4582
584.2698 | 472.8073 | 463.276 | 464.6561
585.2698 | 472.7344 | 463.4452 | 464.9695
586.2698 | 472.7361 | 464.0206 | 465.4165
587.2698 | 472.6785 | 464.1853 | 465.7772
588.2698 | 472.696 | 464.4348 | 465.6967
589.2698 | 472.6933 | 464.8526 | 466.2769
590.2698 | 472.7392 | 464.7185 | 466.156
591.2698 | 472.751 | 464.9596 | 465.9851
592.2698 | 472.8047 | 465.5866 | 466.6393
593.2698 | 472.7611 | 465.6584 | 466.609
594.2698 | 472.758 | 466.0383 | 466.9501
595.2698 | 472.7538 | 466.2024 | 466.968
596.2698 | 472.7253 | 466.5374 | 467.011
597.2698 | 472.6751 | 466.8329 | 467.1423
598.2698 | 472.6916 | 467.1623 | 467.4302
599.2698 | 472.6359 | 467.6085 | 467.4021
600.2698 | 472.62 | 468.4216 | 467.4007
601.2698 | 472.632 | 468.9916 | 467.6923
602.2698 | 472.6857 | 469.4525 | 468.2134
603.2698 | 472.7222 | 470.1714 | 468.396
604.2698 | 472.7034 | 470.2813 | 468.2066
605.2698 | 472.7128 | 471.2091 | 468.0833
606.2698 | 472.7491 | 470.9278 | 467.9151
607.2698 | 472.7759 | 471.9873 | 468.4563
608.2698 | 472.7429 | 472.6979 | 468.6333
609.2698 | 472.7338 | 473.3515 | 468.8172
610.2698 | 472.7417 | 473.879 | 469.2294
611.2698 | 472.7581 | 475.0777 | 469.3635
612.2698 | 472.7109 | 475.5896 | 469.7186
613.2698 | 472.7822 | 476.0473 | 470.0284
614.2698 | 472.713 | 476.5646 | 469.9229
615.2698 | 472.6742 | 477.627 | 470.2863
616.2698 | 472.6767 | 478.0064 | 470.625
617.2698 | 472.615 | 479.2157 | 470.8182
618.2698 | 472.5203 | 479.8897 | 470.9464
619.2698 | 472.458 | 480.5255 | 470.8158
620.2698 | 472.4464 | 481.7411 | 471.5438
621.2698 | 472.4551 | 481.439 | 471.321
622.2698 | 472.5344 | 482.0124 | 471.5541
623.2698 | 472.5919 | 482.2887 | 471.9996
624.2698 | 472.4834 | 483.0371 | 472.426
625.2698 | 472.4435 | 483.1726 | 472.8599
626.2698 | 472.3675 | 483.7795 | 473.1441
627.2698 | 472.3999 | 484.9012 | 473.2124
628.2698 | 472.3971 | 486.2646 | 474.4192
629.2698 | 472.3811 | 486.6595 | 474.6953
630.2698 | 472.4082 | 487.3938 | 475.2175
631.2698 | 472.4033 | 488.4758 | 475.646
632.2698 | 472.4097 | 489.3213 | 476.0564
633.2698 | 472.5093 | 489.9023 | 476.2209
634.2698 | 472.6333 | 490.4218 | 476.4637
635.2698 | 472.6049 | 490.9376 | 476.667
636.2698 | 472.5788 | 492.3577 | 477.1113
637.2698 | 472.613 | 493.5383 | 477.3596
638.2698 | 472.5713 | 494.2404 | 477.6477
639.2698 | 472.4642 | 495.2808 | 477.9616
640.2698 | 472.4398 | 495.2999 | 478.242
641.2698 | 472.3981 | 497.2329 | 478.5138
642.2698 | 472.4613 | 500.7701 | 478.9733
643.2698 | 472.5285 | 501.3141 | 479.1018
644.2698 | 472.5077 | 503.329 | 479.2965
645.2698 | 472.5032 | 499.0838 | 478.8676
646.2698 | 472.4865 | 500.136 | 479.1794
647.2698 | 472.4896 | 500.3405 | 479.1087
648.2698 | 472.3789 | 498.6382 | 478.6656
649.2698 | 472.3297 | 491.6952 | 477.3738
650.2698 | 472.2618 | 492.8269 | 477.5467
651.2698 | 472.2071 | 492.9303 | 477.6852
652.2698 | 472.2381 | 493.7583 | 477.946
653.2698 | 472.2146 | 494.6226 | 477.8791
654.2698 | 472.1746 | 494.807 | 477.6013
655.2698 | 472.1768 | 495.288 | 477.6605
656.2698 | 472.0901 | 495.7898 | 477.2172
657.2698 | 471.9648 | 496.1613 | 477.5533
658.2698 | 471.9236 | 496.2423 | 477.6146
659.2698 | 471.8694 | 498.0718 | 476.4642
660.2698 | 471.6944 | 499.1513 | 476.5104
661.2698 | 471.5907 | 499.481 | 476.3804
662.2698 | 471.4725 | 499.9731 | 476.8356
663.2698 | 471.3622 | 500.0219 | 476.7818
664.2698 | 471.2306 | 501.4778 | 476.4604
665.2698 | 471.149 | 502.2286 | 476.465
666.2698 | 471.0371 | 502.2643 | 477.5492
667.2698 | 470.9549 | 502.8299 | 477.7178
668.2698 | 470.9015 | 503.5781 | 477.6954
669.2698 | 470.8706 | 503.9507 | 477.6755
670.2698 | 470.8156 | 504.3972 | 477.6368
671.2698 | 470.7515 | 505.3058 | 478.0018
672.2698 | 470.7053 | 505.6364 | 478.2123
673.2698 | 470.6115 | 506.4565 | 478.7368
674.2698 | 470.5259 | 506.4855 | 479.0058
675.2698 | 470.3864 | 507.1068 | 479.412
676.2698 | 470.3429 | 507.3012 | 479.7679
677.2698 | 470.2583 | 515.3117 | 481.9011
678.2698 | 470.1647 | 515.1623 | 482.3271
679.2698 | 470.0955 | 515.5781 | 482.8315
680.2698 | 469.9975 | 515.9275 | 483.1055
681.2698 | 470.0165 | 519.2694 | 484.2796
682.2698 | 469.98 | 515.2413 | 483.7593
683.2698 | 469.9173 | 503.8698 | 482.2827
684.2698 | 469.8729 | 501.1868 | 481.7077
685.2698 | 469.7831 | 498.5814 | 481.5505
686.2698 | 469.7111 | 498.8615 | 481.8158
687.2698 | 469.5899 | 498.49 | 482.1036
688.2698 | 469.5233 | 496.1254 | 481.8844
689.2698 | 469.554 | 497.9956 | 482.5622
690.2698 | 469.5763 | 532.2518 | 489.6543
691.2698 | 469.5368 | 532.4673 | 490.0908
692.2698 | 469.5343 | 532.5591 | 490.4945
693.2698 | 469.5578 | 533.3091 | 490.8361
694.2698 | 469.5114 | 533.2444 | 491.053
695.2698 | 469.5024 | 534.0536 | 491.5768
696.2698 | 469.5814 | 534.1649 | 492.0712
697.2698 | 469.7626 | 534.5574 | 492.4789
698.2698 | 469.7875 | 534.9262 | 492.8286
699.2698 | 469.8145 | 535.0134 | 493.1515
700.2698 | 469.8321 | 535.6354 | 493.5245
701.2698 | 469.8253 | 535.7916 | 493.8532
702.2698 | 469.7685 | 536.2238 | 494.2653
703.2698 | 469.7694 | 536.1559 | 494.7844
704.2698 | 469.7892 | 536.663 | 495.1571
705.2698 | 469.8171 | 537.0467 | 495.5596
706.2698 | 469.8716 | 537.181 | 495.8256
707.2698 | 469.9563 | 537.4352 | 496.2214
708.2698 | 469.8025 | 537.7041 | 496.9448
709.2698 | 469.6263 | 538.0143 | 497.2989
710.2698 | 469.4054 | 538.1667 | 497.7283
711.2698 | 469.2172 | 538.4069 | 498.1123
712.2698 | 469.1887 | 538.3459 | 498.6188
713.2698 | 469.1844 | 538.9741 | 499.068
714.2698 | 469.0766 | 539.2075 | 499.3151
715.2698 | 469.0234 | 539.3492 | 500.0232
716.2698 | 469.0615 | 539.5719 | 500.1989
717.2698 | 469.1077 | 539.704 | 500.6189
718.2698 | 469.1528 | 540.3 | 501.1066
719.2698 | 469.0825 | 540.6174 | 501.4516
720.2698 | 468.9987 | 540.7835 | 502.0726
721.2698 | 468.9165 | 541.1462 | 502.4587
722.2698 | 468.8143 | 541.3369 | 502.8951
723.2698 | 468.7232 | 541.7274 | 503.4469
724.2698 | 468.6622 | 541.7788 | 503.8561
725.2698 | 468.6553 | 541.9539 | 504.3855
726.2698 | 468.7136 | 542.2226 | 504.9351
727.2698 | 468.7253 | 542.518 | 505.3103
728.2698 | 468.6908 | 542.8754 | 506.135
729.2698 | 468.7469 | 543.0706 | 506.7146
730.2698 | 468.7833 | 543.1718 | 507.4081
731.2698 | 468.6903 | 543.856 | 507.6559
732.2698 | 468.6396 | 544.0274 | 508.5922
733.2698 | 468.6044 | 544.4161 | 509.2174
734.2698 | 468.5024 | 544.8565 | 509.7366
735.2698 | 468.4143 | 545.2249 | 510.0763
736.2698 | 468.5143 | 545.5791 | 510.918
737.2698 | 468.5282 | 545.7219 | 511.3407
738.2698 | 468.4048 | 546.1404 | 511.9876
739.2698 | 468.3402 | 546.3778 | 512.6195
740.2698 | 468.3744 | 546.8205 | 513.2133
741.2698 | 468.4756 | 547.0708 | 513.8231
742.2698 | 468.4152 | 547.4671 | 514.3154
743.2698 | 468.3367 | 547.746 | 514.9653
744.2698 | 468.3167 | 548.0198 | 515.3282
745.2698 | 468.1698 | 548.3848 | 516.0692
746.2698 | 467.919 | 548.7076 | 516.5901
747.2698 | 467.6506 | 549.3482 | 516.6166
748.2698 | 467.5157 | 549.7622 | 517.4832
749.2698 | 467.2477 | 549.959 | 518.0046
750.2698 | 467.015 | 550.4682 | 518.6726
751.2698 | 466.6732 | 550.9841 | 519.3479
752.2698 | 466.4236 | 551.7999 | 519.8066
753.2698 | 466.1983 | 552.161 | 520.5273
754.2698 | 466.0836 | 553.0513 | 520.2128
755.2698 | 465.8965 | 553.3175 | 521.1441
756.2698 | 465.4892 | 553.8272 | 521.39
757.2698 | 465.0636 | 554.109 | 522.2991
758.2698 | 464.7166 | 554.6352 | 522.4406
759.2698 | 464.2455 | 555.2352 | 522.8777
760.2698 | 463.8622 | 555.6289 | 523.5225
761.2698 | 463.5652 | 556.0595 | 524.6849
762.2698 | 463.2091 | 556.3997 | 525.1887
763.2698 | 462.8296 | 557.1768 | 525.4207
764.2698 | 462.4506 | 557.6565 | 525.7865
765.2698 | 462.0935 | 558.0623 | 526.0625
766.2698 | 461.7091 | 558.5987 | 526.5557
767.2698 | 461.3089 | 559.2761 | 527.0026
768.2698 | 460.8941 | 559.9089 | 527.6031
769.2698 | 460.424 | 560.0685 | 528.2764
770.2698 | 460.0178 | 560.323 | 529.291
771.2698 | 459.6792 | 561.0094 | 529.3299
772.2698 | 459.3198 | 561.4896 | 529.7949
773.2698 | 458.841 | 561.7804 | 530.0093
774.2698 | 458.3767 | 561.986 | 530.8005
775.2698 | 457.909 | 562.4623 | 531.5016
776.2698 | 457.4339 | 562.6229 | 532.4335
777.2698 | 457.0323 | 563.34 | 532.1341
778.2698 | 456.6486 | 563.5502 | 532.8663
779.2698 | 456.1782 | 564.0499 | 533.8788
780.2698 | 455.7488 | 564.4391 | 534.6791