## Test Conditions
DESIREE-FIRE Test Number 9 - Circuit Simulator Data Only
Test Date: | 2009-07-17
DCSim DAQ Start Time | 12:09
DCSim Time for Synchronization | 12:08
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 12:06
Fire Time | 12:10
Offset | 0:01 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 60 | seconds
Heat Source Offset | 0:04 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 218 | seconds
Heat Source Stop Time | 12:38
Test Duration | 0:28 | hour:minutes:seconds
| 1666 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.71875 | 123.7518 | -67.067 | 56.5109 | 0.047088 | 0.0018858 | 0.0016025 | 0.058801 | -0.00016792 | 0.062215 | 0.080738 | 0.0014873 | -5.2e-05 | 0.06701 | -0.0084002 | 0.067367 | -67.0632 | 0.019721 | -66.9612 | 56.4579 | 56.1929 | 56.2894 | -67.1214 | -67.045 | 0.023253 | -67.1299 | 56.2489 | 56.4541 | 56.3978 | -67.1294 | -0.054451 | -0.053059 | 0.003778 | 0.10577 | 0.16022 | -0.318 | -0.22156 | -0.062394 | -0.26202 | 0.021955 | -0.062916 | -0.000522 | -0.056785 | -0.11311 | 123.5248 | 123.2599 | 123.3563 | 67.0867 | -123.6323 | 123.3159 | 123.5211 | 123.4648 | 67.0902 | -123.6403
0.28125 | 123.7381 | -67.067 | 56.5155 | 0.06235 | -0.00025117 | -0.0016025 | 0.057733 | 0.00090108 | 0.05901 | 0.080738 | 0.00041927 | 0.001016 | 0.064873 | -0.0084002 | 0.067367 | -67.0769 | 0.015142 | -66.9337 | 56.4258 | 56.0281 | 56.2161 | -66.9474 | -67.0267 | 0.009516 | -67.1345 | 56.0978 | 56.4541 | 56.1139 | -67.1294 | 0.11955 | -0.089686 | -0.009957 | 0.13324 | 0.013694 | -0.48742 | -0.29939 | -0.062394 | -0.41769 | 0.04027 | -0.067494 | -0.0051 | -0.061363 | -0.40156 | 123.4928 | 123.095 | 123.2831 | 67.0821 | -123.4629 | 123.1648 | 123.5211 | 123.1809 | 67.0765 | -123.6449
1.2656 | 123.7152 | -67.0624 | 56.5292 | 0.047088 | 0.0018858 | -0.0016025 | 0.058801 | 0.00090108 | 0.055805 | 0.065477 | 0.00041927 | -0.001121 | 0.06701 | -0.0084002 | 0.068435 | -67.0723 | 0.0243 | -66.9246 | 56.4258 | 56.0968 | 56.2482 | -66.9886 | -67.0221 | 0.009516 | -67.1345 | 56.1436 | 56.4633 | 56.1643 | -67.1294 | 0.07376 | -0.10342 | -0.009957 | 0.13782 | 0.06406 | -0.43247 | -0.28107 | -0.066972 | -0.38563 | 0.040271 | -0.072072 | -0.0051 | -0.065939 | -0.36492 | 123.4882 | 123.1591 | 123.3105 | 67.0867 | -123.5179 | 123.206 | 123.5257 | 123.2267 | 67.0719 | -123.6586
2.2812 | 123.7015 | -67.0898 | 56.5384 | 0.031826 | 0.0018858 | -0.0016025 | 0.056664 | 0.00090108 | 0.057942 | 0.065477 | 0.0014873 | 0.001016 | 0.06701 | -0.0094682 | 0.068435 | -67.0632 | 0.015142 | -66.9337 | 56.4304 | 56.1242 | 56.2573 | -66.9886 | -67.0084 | 0.018674 | -67.1345 | 56.139 | 56.4541 | 56.1368 | -67.1294 | 0.10123 | -0.10799 | 0.026666 | 0.15613 | 0.054904 | -0.41415 | -0.28107 | -0.039506 | -0.39937 | 0.081473 | -0.044606 | -0.0051 | -0.084251 | -0.40155 | 123.5202 | 123.2141 | 123.3472 | 67.105 | -123.527 | 123.2289 | 123.544 | 123.2267 | 67.1085 | -123.6677
3.2656 | 123.8022 | -67.0258 | 56.5109 | 0.077612 | 0.0029538 | -0.00053454 | 0.059869 | 0.0019691 | 0.056874 | 0.050216 | 0.00041927 | 0.001016 | 0.06701 | -0.0073322 | 0.067367 | -67.0678 | 0.010564 | -66.9337 | 56.4258 | 56.0876 | 56.2482 | -66.9795 | -67.013 | 0.004938 | -67.139 | 56.1116 | 56.4587 | 56.1414 | -67.1294 | 0.046296 | -0.085108 | -0.041999 | 0.092043 | 0.045747 | -0.42332 | -0.26276 | -0.10359 | -0.39937 | 0.012807 | -0.11327 | -0.009679 | -0.052207 | -0.36951 | 123.4516 | 123.1134 | 123.2739 | 67.0363 | -123.4904 | 123.1373 | 123.4845 | 123.1672 | 67.0307 | -123.6403
4.2656 | 123.8113 | -67.012 | 56.5201 | 0.077612 | 0.0029538 | -0.00053454 | 0.058801 | 0.00090108 | 0.060079 | 0.050216 | 0.0014873 | -5.2e-05 | 0.065941 | -0.0073322 | 0.066298 | -67.0723 | 0.005985 | -66.9383 | 56.4304 | 56.0372 | 56.1978 | -66.9062 | -67.0175 | 0.014095 | -67.1345 | 56.0795 | 56.4633 | 56.146 | -67.1294 | 0.10583 | -0.089685 | -0.060311 | 0.073731 | -0.032095 | -0.48284 | -0.32228 | -0.11733 | -0.44058 | -0.005505 | -0.12243 | -0.0051 | -0.056784 | -0.37409 | 123.4424 | 123.0493 | 123.2098 | 67.018 | -123.4263 | 123.0915 | 123.4753 | 123.158 | 67.0261 | -123.6494
5.2812 | 123.7518 | -67.0395 | 56.4926 | 0.06235 | 0.00081683 | -0.0016025 | 0.057733 | 0.00090108 | 0.057942 | 0.050216 | 0.0014873 | 0.001016 | 0.069146 | -0.0094682 | 0.069503 | -67.0678 | 0.015142 | -66.9383 | 56.4304 | 56.0189 | 56.1932 | -66.9291 | -67.0221 | 0.004938 | -67.139 | 56.1024 | 56.445 | 56.1552 | -67.1385 | 0.1104 | -0.062219 | -0.028266 | 0.1012 | -0.009201 | -0.47369 | -0.2994 | -0.099018 | -0.39022 | 0.017383 | -0.099539 | -0.000521 | -0.047632 | -0.33746 | 123.4699 | 123.0584 | 123.2327 | 67.0546 | -123.4217 | 123.1419 | 123.4845 | 123.1946 | 67.0444 | -123.6311
6.2656 | 123.7381 | -67.0166 | 56.5201 | 0.06235 | 0.0018858 | 0.0026715 | 0.058801 | 0.00090108 | 0.061147 | 0.080738 | 0.00041927 | 0.002084 | 0.068078 | -0.0084002 | 0.069503 | -67.0678 | 0.010564 | -66.9337 | 56.4258 | 56.0372 | 56.2436 | -66.9428 | -67.0221 | 0.009516 | -67.139 | 56.0932 | 56.4496 | 56.1597 | -67.1339 | 0.073773 | -0.094264 | -0.051154 | 0.082888 | 0.009115 | -0.48284 | -0.2765 | -0.11733 | -0.42684 | -0.005505 | -0.12243 | -0.0051 | -0.07052 | -0.36035 | 123.4424 | 123.0538 | 123.2602 | 67.0272 | -123.4629 | 123.1098 | 123.4662 | 123.1763 | 67.0261 | -123.654
7.2656 | 123.7839 | -67.0349 | 56.5247 | 0.031826 | 0.00081683 | -0.0016025 | 0.059869 | 0.00090108 | 0.05901 | 0.080738 | 0.00041927 | -5.2e-05 | 0.068078 | -0.0084002 | 0.068435 | -67.0678 | 0.015142 | -66.9383 | 56.4258 | 56.0418 | 56.2207 | -66.9566 | -67.0267 | 0.014095 | -67.1253 | 56.0658 | 56.4587 | 56.1597 | -67.1294 | 0.078346 | -0.098841 | -0.032844 | 0.096619 | 0.018273 | -0.48284 | -0.30397 | -0.094438 | -0.45889 | 0.008226 | -0.090381 | 0.004057 | -0.06594 | -0.36493 | 123.4607 | 123.0767 | 123.2556 | 67.0501 | -123.4812 | 123.1007 | 123.4936 | 123.1946 | 67.049 | -123.654
8.2656 | 123.7152 | -67.0486 | 56.5384 | 0.06235 | 0.00081683 | 0.00053446 | 0.058801 | -0.00016792 | 0.057942 | 0.065477 | 0.0014873 | 0.002084 | 0.065941 | -0.0073322 | 0.066298 | -67.0678 | 0.015142 | -66.9337 | 56.4212 | 56.0235 | 56.1795 | -66.8879 | -67.0175 | 0.009516 | -67.1299 | 56.0566 | 56.4496 | 56.1552 | -67.1385 | 0.16076 | -0.11715 | -0.019111 | 0.11493 | -0.045832 | -0.51489 | -0.35891 | -0.089863 | -0.48178 | 0.031116 | -0.081227 | 0.008636 | -0.08883 | -0.38324 | 123.4699 | 123.0721 | 123.2281 | 67.0638 | -123.4263 | 123.1053 | 123.4982 | 123.2038 | 67.0582 | -123.6769
9.2656 | 123.7244 | -67.0532 | 56.5384 | 0.06235 | 0.0029538 | 0.00053446 | 0.057733 | 0.00090108 | 0.060079 | 0.050216 | 0.00041927 | 0.001016 | 0.068078 | -0.0094682 | 0.066298 | -67.0723 | 0.010564 | -66.9474 | 56.4167 | 56.0235 | 56.1932 | -66.9428 | -67.0175 | 0.000359 | -67.1299 | 56.0566 | 56.4496 | 56.1597 | -67.1339 | 0.11039 | -0.12173 | -0.019112 | 0.10577 | -0.00462 | -0.51489 | -0.34517 | -0.080706 | -0.48178 | 0.035694 | -0.076649 | 0.004057 | -0.08883 | -0.37866 | 123.4699 | 123.0767 | 123.2464 | 67.0638 | -123.4812 | 123.1098 | 123.5028 | 123.213 | 67.0536 | -123.6723
10.2812 | 123.6923 | -67.0853 | 56.5063 | 0.06235 | 0.0018858 | -0.00053454 | 0.059869 | 0.00090108 | 0.056874 | 0.034955 | 0.0014873 | 0.002084 | 0.06701 | -0.0062632 | 0.068435 | -67.0723 | 0.010564 | -66.9246 | 56.4258 | 56.0464 | 56.1657 | -66.9428 | -67.013 | 0.009516 | -67.1345 | 56.0246 | 56.4496 | 56.1552 | -67.1339 | 0.14244 | -0.080531 | 0.012931 | 0.16071 | 0.018271 | -0.45995 | -0.3406 | -0.048663 | -0.48179 | 0.072316 | -0.049184 | -0.000521 | -0.056787 | -0.3512 | 123.5111 | 123.1317 | 123.251 | 67.0958 | -123.4492 | 123.1098 | 123.5348 | 123.2404 | 67.0948 | -123.6403
11.2656 | 123.8205 | -67.0212 | 56.5247 | 0.06235 | 0.0018858 | 0.00053446 | 0.060938 | -0.00016792 | 0.057942 | 0.080738 | 0.0014873 | 0.002084 | 0.06701 | -0.0073322 | 0.068435 | -67.0632 | 0.015142 | -66.9383 | 56.4167 | 56.0464 | 56.2253 | -66.9337 | -67.0175 | 0.004938 | -67.1207 | 56.0703 | 56.4496 | 56.1597 | -67.1339 | 0.087508 | -0.108 | -0.041999 | 0.082886 | -0.004622 | -0.47826 | -0.29939 | -0.11275 | -0.45431 | 0.00365 | -0.099535 | 0.013215 | -0.075097 | -0.36493 | 123.4378 | 123.0676 | 123.2464 | 67.0363 | -123.4583 | 123.0915 | 123.4707 | 123.1809 | 67.0261 | -123.6586
12.2812 | 123.7793 | -67.0395 | 56.5155 | 0.077612 | 0.00081683 | 0.0026715 | 0.056664 | 0.00090108 | 0.057942 | 0.065477 | 0.00041927 | -0.001121 | 0.065941 | -0.0062632 | 0.068435 | -67.0632 | 0.005985 | -66.9337 | 56.4258 | 56.0556 | 56.1978 | -66.9566 | -67.0267 | 0.014095 | -67.1299 | 56.0795 | 56.4496 | 56.1597 | -67.1339 | 0.082924 | -0.089686 | -0.023688 | 0.10578 | 0.022852 | -0.45995 | -0.31771 | -0.094439 | -0.436 | 0.012804 | -0.090382 | 0.004057 | -0.065942 | -0.35577 | 123.4653 | 123.095 | 123.2373 | 67.0455 | -123.4721 | 123.119 | 123.4891 | 123.1992 | 67.0536 | -123.6494
13.2656 | 123.8205 | -67.0349 | 56.5155 | 0.06235 | 0.0018858 | 0.00053446 | 0.058801 | 0.00090108 | 0.05901 | 0.080738 | 0.0014873 | 0.002084 | 0.068078 | -0.0051952 | 0.067367 | -67.0632 | 0.005985 | -66.9383 | 56.4212 | 56.0281 | 56.1795 | -66.9337 | -67.0175 | 0.009516 | -67.1345 | 56.0612 | 56.4587 | 56.1689 | -67.1339 | 0.10124 | -0.094264 | -0.028266 | 0.096619 | -0.004622 | -0.48742 | -0.33602 | -0.099017 | -0.45431 | 0.017383 | -0.099538 | -0.000521 | -0.056785 | -0.34661 | 123.4562 | 123.063 | 123.2144 | 67.0409 | -123.4492 | 123.0961 | 123.4936 | 123.2038 | 67.0444 | -123.6494
14.2656 | 123.7747 | -67.0212 | 56.5292 | 0.047088 | -0.00025117 | 0.00053446 | 0.056664 | 0.0019691 | 0.05901 | 0.065477 | -0.00064973 | -5.2e-05 | 0.06701 | -0.0084002 | 0.067367 | -67.0678 | 0.010564 | -66.9383 | 56.4258 | 56.0556 | 56.239 | -66.9474 | -67.013 | 0.009516 | -67.1299 | 56.0658 | 56.4541 | 56.1597 | -67.1294 | 0.073771 | -0.10342 | -0.046577 | 0.082886 | 0.009115 | -0.47368 | -0.29023 | -0.10817 | -0.46347 | 0.008229 | -0.10869 | -0.000522 | -0.075096 | -0.3695 | 123.447 | 123.0767 | 123.2602 | 67.0317 | -123.4766 | 123.0869 | 123.4753 | 123.1809 | 67.0307 | -123.6586
15.2812 | 123.7839 | -67.0395 | 56.5155 | 0.047088 | -0.00025117 | 0.00053446 | 0.057733 | 0.0019691 | 0.056874 | 0.065477 | -0.00064973 | -5.2e-05 | 0.065941 | -0.0051952 | 0.067367 | -67.0678 | 0.010564 | -66.9474 | 56.4212 | 56.0464 | 56.2207 | -66.9291 | -67.0175 | 0.004938 | -67.1299 | 56.0978 | 56.4587 | 56.1552 | -67.1339 | 0.1104 | -0.094264 | -0.028266 | 0.092041 | -0.018357 | -0.46911 | -0.29481 | -0.094439 | -0.41769 | 0.021961 | -0.090382 | 0.004057 | -0.056785 | -0.36035 | 123.4607 | 123.0859 | 123.2602 | 67.0501 | -123.4446 | 123.1373 | 123.4982 | 123.1946 | 67.0444 | -123.6494
16.2656 | 123.7061 | -67.0532 | 56.5521 | 0.047088 | 0.0018858 | 0.00053446 | 0.058801 | 0.0019691 | 0.057942 | 0.080738 | -0.00064973 | -5.2e-05 | 0.065941 | -0.0073322 | 0.068435 | -67.0678 | 0.015142 | -66.9383 | 56.4167 | 56.0464 | 56.239 | -66.8925 | -67.0175 | 0.009516 | -67.1345 | 56.0749 | 56.4541 | 56.1552 | -67.1294 | 0.16076 | -0.13546 | -0.014533 | 0.11493 | -0.045832 | -0.50573 | -0.31312 | -0.076127 | -0.4772 | 0.035694 | -0.081227 | -0.0051 | -0.097984 | -0.39697 | 123.4699 | 123.0996 | 123.2922 | 67.0684 | -123.4446 | 123.1281 | 123.5074 | 123.2084 | 67.0627 | -123.6815
17.2656 | 123.7106 | -67.0532 | 56.5475 | 0.077612 | 0.00081683 | -0.00053454 | 0.057733 | -0.0012359 | 0.05901 | 0.065477 | 0.0014873 | 0.001016 | 0.065941 | -0.0051952 | 0.066298 | -67.0632 | 0.005985 | -66.9337 | 56.4167 | 56.0418 | 56.2161 | -66.9428 | -67.013 | 0.004938 | -67.1345 | 56.0749 | 56.4587 | 56.1506 | -67.1385 | 0.11039 | -0.13088 | -0.009955 | 0.11951 | 0.009115 | -0.50573 | -0.33143 | -0.085285 | -0.47262 | 0.040273 | -0.081227 | 0.004058 | -0.088828 | -0.39697 | 123.4699 | 123.095 | 123.2693 | 67.0592 | -123.4904 | 123.1281 | 123.5119 | 123.2038 | 67.0582 | -123.6861
18.2656 | 123.8159 | -67.0303 | 56.5063 | 0.047088 | 0.0018858 | -0.00053454 | 0.057733 | 0.0019691 | 0.055805 | 0.080738 | 0.00041927 | 0.001016 | 0.069146 | -0.0041272 | 0.067367 | -67.0769 | 0.010564 | -66.9383 | 56.4258 | 56.0464 | 56.207 | -66.9428 | -67.013 | 0.009516 | -67.1253 | 56.0658 | 56.4496 | 56.1506 | -67.1431 | 0.087505 | -0.080531 | -0.046579 | 0.092041 | 0.004536 | -0.45995 | -0.29939 | -0.11275 | -0.44058 | 0.017384 | -0.094959 | 0.017794 | -0.056787 | -0.35577 | 123.4562 | 123.0767 | 123.2373 | 67.0409 | -123.4492 | 123.0961 | 123.4799 | 123.1809 | 67.0399 | -123.6494
19.2812 | 123.6969 | -67.1036 | 56.5155 | 0.031826 | 0.00081683 | -0.00053454 | 0.057733 | 0.00090108 | 0.060079 | 0.065477 | -0.00064973 | -5.2e-05 | 0.068078 | -0.0051952 | 0.067367 | -67.0586 | 0.010564 | -66.9291 | 56.4212 | 56.0327 | 56.2344 | -66.952 | -67.0175 | 0.009516 | -67.1345 | 56.107 | 56.4587 | 56.1552 | -67.1385 | 0.15159 | -0.094264 | 0.044978 | 0.17444 | 0.022851 | -0.48284 | -0.28108 | -0.034931 | -0.40853 | 0.086048 | -0.030873 | 0.004058 | -0.056785 | -0.36035 | 123.5248 | 123.1362 | 123.338 | 67.1141 | -123.4675 | 123.2106 | 123.5623 | 123.2587 | 67.1131 | -123.654
20.2812 | 123.8251 | -67.0029 | 56.4926 | 0.077612 | -0.00025117 | -0.00053454 | 0.057733 | 0.0019691 | 0.060079 | 0.065477 | 0.00041927 | 0.001016 | 0.06701 | -0.0073322 | 0.068435 | -67.0723 | 0.010564 | -66.9337 | 56.4212 | 56.0647 | 56.2207 | -66.9016 | -67.0175 | 0.009516 | -67.1299 | 56.0887 | 56.4541 | 56.1506 | -67.1339 | 0.10125 | -0.071376 | -0.069466 | 0.069155 | -0.032095 | -0.4279 | -0.27193 | -0.13106 | -0.40395 | -0.01466 | -0.127 | 0.004057 | -0.038475 | -0.34204 | 123.4241 | 123.0676 | 123.2236 | 67.0134 | -123.3942 | 123.0915 | 123.457 | 123.1534 | 67.0124 | -123.6265
21.2656 | 123.6877 | -67.0532 | 56.5384 | 0.047088 | 0.00081683 | 0.0016025 | 0.058801 | -0.0012359 | 0.057942 | 0.095999 | -0.00064973 | 0.002084 | 0.06701 | -0.0051952 | 0.067367 | -67.0723 | 0.005985 | -66.9337 | 56.4258 | 56.0418 | 56.2024 | -66.9291 | -67.0221 | 0.009516 | -67.1299 | 56.052 | 56.4541 | 56.1597 | -67.1385 | 0.12413 | -0.11257 | -0.019112 | 0.11951 | -0.004622 | -0.49657 | -0.33602 | -0.085285 | -0.48636 | 0.031116 | -0.076649 | 0.008636 | -0.084251 | -0.37866 | 123.479 | 123.095 | 123.2556 | 67.0592 | -123.4675 | 123.1053 | 123.5074 | 123.213 | 67.0627 | -123.6769
22.2812 | 123.8113 | -67.0212 | 56.4789 | 0.06235 | 0.00081683 | -0.0016025 | 0.058801 | 0.00090108 | 0.05901 | 0.050216 | 0.0025553 | 0.001016 | 0.065941 | -0.0051952 | 0.06523 | -67.0678 | 0.005985 | -66.9383 | 56.4167 | 56.051 | 56.239 | -66.9245 | -67.013 | 0.004938 | -67.1299 | 56.1024 | 56.4496 | 56.1643 | -67.1385 | 0.096666 | -0.062221 | -0.046577 | 0.082886 | -0.01378 | -0.42791 | -0.23988 | -0.11733 | -0.37648 | 0.008229 | -0.10869 | 0.008636 | -0.029321 | -0.31457 | 123.4378 | 123.0722 | 123.2602 | 67.0272 | -123.4034 | 123.1236 | 123.4707 | 123.1855 | 67.0261 | -123.6174
23.2656 | 123.7106 | -67.0578 | 56.5521 | 0.077612 | -0.00025117 | -0.0016025 | 0.058801 | 0.00090108 | 0.057942 | 0.065477 | -0.00064973 | -5.2e-05 | 0.065941 | -0.0051952 | 0.067367 | -67.0678 | 0.010564 | -66.9337 | 56.4212 | 56.0784 | 56.2207 | -66.9199 | -67.0175 | 0.004938 | -67.1207 | 56.0749 | 56.4541 | 56.1643 | -67.1385 | 0.13787 | -0.13088 | -0.009956 | 0.12409 | -0.013779 | -0.47368 | -0.33143 | -0.080708 | -0.4772 | 0.040271 | -0.062914 | 0.017794 | -0.097984 | -0.38781 | 123.479 | 123.1362 | 123.2785 | 67.0684 | -123.4721 | 123.1327 | 123.5119 | 123.2221 | 67.0627 | -123.6906
24.2812 | 123.7976 | -67.0303 | 56.4606 | 0.06235 | 0.0018858 | -0.00053454 | 0.055596 | 0.00090108 | 0.056874 | 0.050216 | 0.00041927 | 0.001016 | 0.064873 | -0.0051952 | 0.068435 | -67.0723 | 0.015142 | -66.9383 | 56.4258 | 56.0372 | 56.2482 | -66.9016 | -67.0221 | 0.004938 | -67.1345 | 56.0749 | 56.4587 | 56.1552 | -67.1431 | 0.12871 | -0.034754 | -0.042001 | 0.092041 | -0.036674 | -0.42333 | -0.21241 | -0.11275 | -0.38565 | 0.008227 | -0.10412 | 0.008637 | -0.001853 | -0.30542 | 123.4562 | 123.0676 | 123.2785 | 67.0455 | -123.3622 | 123.1053 | 123.4891 | 123.1855 | 67.0353 | -123.6037
25.2812 | 123.7518 | -67.067 | 56.5247 | 0.047088 | -0.00025117 | 0.00053446 | 0.056664 | -0.00016792 | 0.05901 | 0.050216 | -0.00064973 | 0.001016 | 0.06701 | -0.0041272 | 0.066298 | -67.0632 | 0.010564 | -66.9383 | 56.4258 | 56.0327 | 56.2161 | -66.8513 | -67.0221 | 0.004938 | -67.1207 | 56.0749 | 56.4541 | 56.1506 | -67.1339 | 0.2157 | -0.098841 | 0.003778 | 0.12866 | -0.087042 | -0.492 | -0.30855 | -0.066973 | -0.44973 | 0.044849 | -0.053758 | 0.013215 | -0.070518 | -0.37408 | 123.4928 | 123.0996 | 123.2831 | 67.0775 | -123.3759 | 123.1419 | 123.5211 | 123.2175 | 67.0719 | -123.6586
26.2656 | 123.7015 | -67.0807 | 56.5384 | 0.047088 | -0.0013202 | 0.00053446 | 0.056664 | 0.0019691 | 0.057942 | 0.050216 | -0.00064973 | -5.2e-05 | 0.065941 | -0.0041272 | 0.066298 | -67.0678 | 0.005985 | -66.9383 | 56.4212 | 56.0464 | 56.207 | -66.9428 | -67.0221 | 0.009516 | -67.1253 | 56.0703 | 56.4496 | 56.1597 | -67.1385 | 0.13786 | -0.11715 | 0.012932 | 0.14239 | 0.004536 | -0.492 | -0.33144 | -0.05782 | -0.46804 | 0.058581 | -0.044605 | 0.013215 | -0.08883 | -0.37866 | 123.5019 | 123.1271 | 123.2876 | 67.0867 | -123.4812 | 123.151 | 123.5302 | 123.2404 | 67.0902 | -123.6769
27.2812 | 123.7015 | -67.0715 | 56.5338 | 0.077612 | -0.0013202 | 0.00053446 | 0.056664 | -0.00016792 | 0.057942 | 0.050216 | 0.00041927 | -5.2e-05 | 0.065941 | -0.0051952 | 0.066298 | -67.0632 | 0.010564 | -66.9337 | 56.4258 | 56.0922 | 56.207 | -66.9611 | -67.0175 | 0.014095 | -67.1299 | 56.0887 | 56.4541 | 56.1597 | -67.1385 | 0.11039 | -0.108 | 0.008355 | 0.13782 | 0.027431 | -0.44163 | -0.32686 | -0.066975 | -0.44515 | 0.054004 | -0.058339 | 0.008636 | -0.079673 | -0.37408 | 123.4974 | 123.1637 | 123.2785 | 67.0821 | -123.495 | 123.1602 | 123.5257 | 123.2313 | 67.0856 | -123.6723
28.2656 | 123.7198 | -67.0349 | 56.543 | 0.06235 | 0.00081683 | -0.00053454 | 0.057733 | 0.00090108 | 0.05901 | 0.050216 | 0.00041927 | -0.001121 | 0.06701 | -0.0019902 | 0.067367 | -67.0632 | 0.010564 | -66.9429 | 56.4258 | 56.0693 | 56.2253 | -66.9566 | -67.0175 | 0.014095 | -67.1345 | 56.0887 | 56.4633 | 56.1597 | -67.1385 | 0.078346 | -0.11715 | -0.028266 | 0.092041 | 0.013695 | -0.47368 | -0.3177 | -0.1036 | -0.45431 | 0.017383 | -0.099538 | 0.004058 | -0.079672 | -0.38324 | 123.4607 | 123.1042 | 123.2602 | 67.0455 | -123.4995 | 123.1236 | 123.4982 | 123.1946 | 67.049 | -123.6815
29.2812 | 123.6969 | -67.067 | 56.5201 | 0.06235 | -0.0013202 | 0.00053446 | 0.058801 | 0.00090108 | 0.056874 | 0.034955 | 0.00041927 | -0.001121 | 0.06701 | -0.0030582 | 0.067367 | -67.0678 | 0.005985 | -66.9383 | 56.4212 | 56.083 | 56.2253 | -66.8787 | -67.0175 | 0.014095 | -67.1207 | 56.1024 | 56.4587 | 56.1597 | -67.1385 | 0.18823 | -0.098842 | -0.0008 | 0.12866 | -0.059569 | -0.43705 | -0.29481 | -0.071552 | -0.41768 | 0.049427 | -0.053758 | 0.017794 | -0.061363 | -0.36035 | 123.4882 | 123.15 | 123.2922 | 67.0729 | -123.3988 | 123.1694 | 123.5257 | 123.2267 | 67.0811 | -123.6586
30.2969 | 123.7198 | -67.0624 | 56.5247 | 0.06235 | 0.0018858 | -0.00053454 | 0.056664 | 0.00090108 | 0.061147 | 0.050216 | 0.0014873 | 0.001016 | 0.063805 | -0.0030582 | 0.066298 | -67.0586 | 0.005985 | -66.9429 | 56.4258 | 56.0784 | 56.2298 | -66.9611 | -67.0221 | 0.004938 | -67.1345 | 56.0795 | 56.4633 | 56.1597 | -67.1339 | 0.10123 | -0.098841 | 0.003779 | 0.11951 | 0.018274 | -0.44621 | -0.29481 | -0.071551 | -0.44515 | 0.040271 | -0.072072 | -0.000521 | -0.061361 | -0.36493 | 123.4882 | 123.1408 | 123.2922 | 67.0684 | -123.4858 | 123.1419 | 123.5257 | 123.2221 | 67.0673 | -123.6586
31.2656 | 123.6649 | -67.0349 | 56.543 | 0.06235 | 0.0018858 | -0.00053454 | 0.057733 | 0.00090108 | 0.05901 | 0.050216 | 0.0014873 | 0.001016 | 0.064873 | -0.0019902 | 0.066298 | -67.0678 | 0.015142 | -66.9429 | 56.4121 | 56.0464 | 56.2436 | -66.9291 | -67.013 | 0.009516 | -67.1299 | 56.0887 | 56.4679 | 56.1506 | -67.1339 | 0.10582 | -0.13089 | -0.032844 | 0.092041 | -0.013779 | -0.49657 | -0.29939 | -0.099017 | -0.45431 | 0.021962 | -0.09496 | 0.004057 | -0.075093 | -0.39239 | 123.447 | 123.0813 | 123.2785 | 67.0501 | -123.4721 | 123.1236 | 123.5028 | 123.1855 | 67.0444 | -123.6769
32.2812 | 123.6923 | -67.067 | 56.4972 | 0.047088 | 0.00081683 | -0.00053454 | 0.056664 | 0.0019691 | 0.057942 | 0.080738 | 0.00041927 | -0.001121 | 0.065941 | -0.0041272 | 0.066298 | -67.0723 | 0.015142 | -66.9337 | 56.4121 | 56.051 | 56.2298 | -66.9291 | -67.0175 | 0.004938 | -67.1253 | 56.1024 | 56.4587 | 56.1597 | -67.1385 | 0.13786 | -0.08511 | -0.005379 | 0.13324 | -0.004622 | -0.44622 | -0.26734 | -0.071552 | -0.39479 | 0.049427 | -0.058337 | 0.013215 | -0.038474 | -0.33746 | 123.479 | 123.1179 | 123.2968 | 67.0821 | -123.4263 | 123.1694 | 123.5257 | 123.2267 | 67.0719 | -123.6357
33.2656 | 123.7244 | -67.0303 | 56.5384 | 0.047088 | 0.00081683 | -0.0016025 | 0.055596 | 0.0019691 | 0.056874 | 0.065477 | 0.0014873 | 0.002084 | 0.064873 | -0.0019902 | 0.06523 | -67.0632 | 0.010564 | -66.9429 | 56.4167 | 56.051 | 56.2115 | -66.8879 | -67.0084 | 0.004938 | -67.1253 | 56.0795 | 56.4633 | 56.1506 | -67.1339 | 0.14245 | -0.12173 | -0.032844 | 0.087463 | -0.054989 | -0.48742 | -0.32686 | -0.10359 | -0.45889 | 0.021963 | -0.094959 | 0.008636 | -0.075094 | -0.38782 | 123.447 | 123.0813 | 123.2419 | 67.0409 | -123.4263 | 123.1098 | 123.4936 | 123.1809 | 67.0353 | -123.6723
34.2812 | 123.7747 | -67.067 | 56.4697 | 0.031826 | -0.00025117 | -0.00053454 | 0.057733 | -0.00016792 | 0.055805 | 0.065477 | 0.0014873 | 0.001016 | 0.064873 | -0.0041272 | 0.067367 | -67.0632 | 0.010564 | -66.9337 | 56.4167 | 56.0693 | 56.1978 | -66.9245 | -67.0084 | 0.009516 | -67.1299 | 56.0841 | 56.4633 | 56.1643 | -67.1339 | 0.14244 | -0.053066 | 0.003778 | 0.13324 | -0.009201 | -0.40044 | -0.27193 | -0.066973 | -0.38564 | 0.058585 | -0.062916 | 0.004057 | -0.00643 | -0.30542 | 123.4836 | 123.1362 | 123.2648 | 67.0775 | -123.3942 | 123.151 | 123.5303 | 123.2313 | 67.0765 | -123.6037
35.2812 | 123.7885 | -67.0212 | 56.5247 | 0.092874 | 0.0018858 | -0.0016025 | 0.057733 | 0.00090108 | 0.05901 | 0.095999 | 0.0014873 | -0.001121 | 0.068078 | -0.0019902 | 0.066298 | -67.0632 | 0.005985 | -66.9474 | 56.4212 | 56.0693 | 56.2253 | -66.9566 | -67.013 | 0.004938 | -67.1253 | 56.0887 | 56.4587 | 56.1552 | -67.1339 | 0.064613 | -0.10342 | -0.041999 | 0.07373 | 0.009117 | -0.45537 | -0.29939 | -0.11275 | -0.436 | 0.008229 | -0.10411 | 0.008636 | -0.06594 | -0.36951 | 123.4424 | 123.0905 | 123.2464 | 67.0272 | -123.4812 | 123.1098 | 123.4799 | 123.1763 | 67.0261 | -123.6586
36.2812 | 123.7473 | -67.0441 | 56.543 | 0.06235 | 0.0018858 | 0.00053446 | 0.055596 | 0.00090108 | 0.057942 | 0.065477 | 0.00041927 | -5.2e-05 | 0.064873 | -0.00092216 | 0.067367 | -67.0678 | 0.005985 | -66.9383 | 56.4212 | 56.0418 | 56.2161 | -66.9474 | -67.0175 | 0.009516 | -67.1253 | 56.0932 | 56.4633 | 56.1689 | -67.1385 | 0.096659 | -0.12173 | -0.023689 | 0.10577 | 0.009115 | -0.50115 | -0.32686 | -0.094441 | -0.44973 | 0.026538 | -0.081226 | 0.013215 | -0.079672 | -0.37408 | 123.4653 | 123.0859 | 123.2602 | 67.0501 | -123.4904 | 123.1373 | 123.5074 | 123.213 | 67.0536 | -123.6815
37.2812 | 123.7061 | -67.0807 | 56.5247 | 0.06235 | -0.00025117 | -0.0016025 | 0.057733 | -0.00016792 | 0.057942 | 0.034955 | 0.00041927 | 0.001016 | 0.063805 | -0.0030582 | 0.067367 | -67.0586 | 0.005985 | -66.9429 | 56.4167 | 56.0372 | 56.2253 | -66.9382 | -67.0084 | 0.004938 | -67.1299 | 56.052 | 56.4633 | 56.1597 | -67.1294 | 0.14244 | -0.108 | 0.022089 | 0.13782 | -0.004621 | -0.48742 | -0.29939 | -0.048662 | -0.47263 | 0.072317 | -0.049184 | -0.000522 | -0.061361 | -0.36493 | 123.4973 | 123.1179 | 123.306 | 67.0867 | -123.4629 | 123.1327 | 123.544 | 123.2404 | 67.0856 | -123.654
38.2812 | 123.7244 | -67.0349 | 56.543 | 0.077612 | 0.0018858 | 0.00053446 | 0.055596 | -0.0012359 | 0.057942 | 0.065477 | -0.0027857 | -5.2e-05 | 0.06701 | -0.0019902 | 0.067367 | -67.0678 | 0.010564 | -66.9429 | 56.4258 | 56.0556 | 56.1978 | -66.9474 | -67.0038 | 0.004938 | -67.1345 | 56.0932 | 56.4725 | 56.1597 | -67.1385 | 0.087504 | -0.11715 | -0.032844 | 0.092041 | 0.004537 | -0.48742 | -0.34517 | -0.1036 | -0.44973 | 0.03112 | -0.099538 | 0.004058 | -0.070515 | -0.38324 | 123.4607 | 123.0905 | 123.2327 | 67.0455 | -123.4904 | 123.1282 | 123.5074 | 123.1946 | 67.0399 | -123.6815
39.2656 | 123.7015 | -67.0624 | 56.5201 | 0.06235 | -0.00025117 | -0.00053454 | 0.057733 | 0.00090108 | 0.056874 | 0.050216 | 0.00041927 | -5.2e-05 | 0.06701 | -0.00092216 | 0.067367 | -67.0586 | 0.015142 | -66.9291 | 56.4167 | 56.0281 | 56.2207 | -66.9566 | -67.0175 | 0.004938 | -67.1299 | 56.0795 | 56.4633 | 56.1552 | -67.1339 | 0.10581 | -0.10342 | 0.003779 | 0.13324 | 0.02743 | -0.492 | -0.29939 | -0.071551 | -0.44058 | 0.044849 | -0.067494 | 0.004057 | -0.056784 | -0.36493 | 123.479 | 123.0905 | 123.2831 | 67.0775 | -123.4766 | 123.1419 | 123.5257 | 123.2175 | 67.0673 | -123.654
40.2969 | 123.761 | -67.0624 | 56.543 | 0.06235 | -0.00025117 | -0.0016025 | 0.055596 | -0.00016792 | 0.057942 | 0.065477 | 0.00041927 | -5.2e-05 | 0.064873 | -0.0030582 | 0.06523 | -67.0586 | 0.010564 | -66.9383 | 56.4212 | 56.0693 | 56.2253 | -66.9245 | -67.0221 | 0.004938 | -67.1299 | 56.0795 | 56.4587 | 56.1597 | -67.1385 | 0.13786 | -0.12173 | 0.003779 | 0.12408 | -0.01378 | -0.47368 | -0.3177 | -0.07613 | -0.46346 | 0.040271 | -0.067494 | 0.008636 | -0.084251 | -0.38324 | 123.4836 | 123.1317 | 123.2876 | 67.0729 | -123.4675 | 123.1419 | 123.5211 | 123.2221 | 67.0673 | -123.6815
41.2656 | 123.7518 | -67.0349 | 56.5247 | 0.047088 | -0.00025117 | -0.00053454 | 0.057733 | -0.00016792 | 0.057942 | 0.080738 | 0.0014873 | -5.2e-05 | 0.064873 | -0.0030582 | 0.066298 | -67.0723 | 0.001407 | -66.9383 | 56.4121 | 56.0556 | 56.1932 | -66.9337 | -67.013 | 0.004938 | -67.1253 | 56.0475 | 56.4587 | 56.1643 | -67.1385 | 0.10124 | -0.11258 | -0.037423 | 0.096619 | -0.004622 | -0.4691 | -0.33144 | -0.1036 | -0.4772 | 0.021962 | -0.090381 | 0.013215 | -0.06594 | -0.36035 | 123.447 | 123.0905 | 123.2281 | 67.0363 | -123.4583 | 123.0824 | 123.4936 | 123.1992 | 67.0399 | -123.6632
42.2812 | 123.6786 | -67.1036 | 56.5292 | 0.077612 | 0.00081683 | 0.00053446 | 0.057733 | -0.00016792 | 0.056874 | 0.065477 | 0.0014873 | -5.2e-05 | 0.065941 | -0.0019902 | 0.066298 | -67.0632 | 0.015142 | -66.9337 | 56.4121 | 56.0556 | 56.2253 | -66.9474 | -67.0175 | 0.014095 | -67.1299 | 56.0703 | 56.4587 | 56.1597 | -67.1431 | 0.15617 | -0.11715 | 0.040399 | 0.16986 | 0.013694 | -0.47368 | -0.30397 | -0.03951 | -0.45889 | 0.086048 | -0.026295 | 0.013215 | -0.070518 | -0.3695 | 123.5157 | 123.1591 | 123.3288 | 67.1187 | -123.4766 | 123.1739 | 123.5623 | 123.2633 | 67.1177 | -123.6723
43.2656 | 123.7015 | -67.0624 | 56.5384 | 0.06235 | 0.0018858 | 0.00053446 | 0.057733 | -0.00016792 | 0.056874 | 0.050216 | -0.00064973 | -0.001121 | 0.065941 | -0.00092216 | 0.066298 | -67.0678 | 0.005985 | -66.9383 | 56.4212 | 56.0418 | 56.2115 | -66.9016 | -67.0175 | 0.000359 | -67.1253 | 56.0703 | 56.4587 | 56.1643 | -67.1431 | 0.16076 | -0.11715 | -0.005378 | 0.12408 | -0.036674 | -0.49657 | -0.32686 | -0.080709 | -0.46804 | 0.044849 | -0.062915 | 0.017794 | -0.079673 | -0.37408 | 123.4836 | 123.1042 | 123.2739 | 67.0684 | -123.44 | 123.1327 | 123.5211 | 123.2267 | 67.0627 | -123.6815
44.2812 | 123.761 | -67.0441 | 56.5292 | 0.06235 | 0.00081683 | -0.00053454 | 0.056664 | -0.0012359 | 0.056874 | 0.065477 | -0.00064973 | -0.001121 | 0.064873 | -0.0019902 | 0.066298 | -67.0632 | 0.015142 | -66.9291 | 56.4167 | 56.0601 | 56.2253 | -66.9382 | -67.0084 | 0.009516 | -67.1299 | 56.0703 | 56.4633 | 56.1597 | -67.1385 | 0.10582 | -0.11257 | -0.019111 | 0.11493 | 0.009114 | -0.4691 | -0.30397 | -0.094441 | -0.45889 | 0.035696 | -0.085805 | 0.008636 | -0.065939 | -0.3695 | 123.4607 | 123.1042 | 123.2693 | 67.0592 | -123.4675 | 123.1144 | 123.5074 | 123.2038 | 67.0536 | -123.6677
45.2812 | 123.6969 | -67.067 | 56.5063 | 0.077612 | -0.00025117 | -0.00053454 | 0.055596 | -0.00016792 | 0.055805 | 0.050216 | -0.00064973 | -5.2e-05 | 0.064873 | 0.00014684 | 0.066298 | -67.0678 | 0.015142 | -66.9337 | 56.4212 | 56.0693 | 56.2024 | -66.9291 | -67.0084 | 0.004938 | -67.1253 | 56.0612 | 56.4541 | 56.1552 | -67.1385 | 0.13786 | -0.085109 | -0.0008 | 0.13324 | -0.004622 | -0.43706 | -0.30397 | -0.071552 | -0.44516 | 0.058585 | -0.058337 | 0.013215 | -0.052208 | -0.3512 | 123.4882 | 123.1362 | 123.2693 | 67.0821 | -123.4354 | 123.1281 | 123.5211 | 123.2221 | 67.0719 | -123.6449
46.2656 | 123.6969 | -67.0624 | 56.5384 | 0.077612 | -0.00025117 | 0.00053446 | 0.057733 | -0.0012359 | 0.056874 | 0.065477 | 0.00041927 | -5.2e-05 | 0.065941 | -0.00092216 | 0.064162 | -67.0586 | 0.001407 | -66.9337 | 56.4258 | 56.0189 | 56.2344 | -66.9337 | -67.0221 | 0.014095 | -67.1253 | 56.0795 | 56.4587 | 56.1552 | -67.1385 | 0.12871 | -0.11257 | 0.003779 | 0.12866 | -4.3e-05 | -0.51947 | -0.30397 | -0.07613 | -0.45889 | 0.040271 | -0.062915 | 0.013215 | -0.079673 | -0.38324 | 123.4882 | 123.0813 | 123.2968 | 67.0638 | -123.4721 | 123.1419 | 123.5211 | 123.2175 | 67.0765 | -123.6769
47.2812 | 123.6877 | -67.0715 | 56.5018 | 0.047088 | 0.00081683 | -0.00053454 | 0.055596 | 0.00090108 | 0.056874 | 0.065477 | -0.00064973 | 0.001016 | 0.065941 | -0.00092216 | 0.06523 | -67.0632 | 0.010564 | -66.9383 | 56.4212 | 56.051 | 56.2344 | -66.9611 | -67.0175 | 0.018674 | -67.1299 | 56.0749 | 56.4679 | 56.1552 | -67.1339 | 0.11039 | -0.080531 | 0.008355 | 0.13324 | 0.022852 | -0.4508 | -0.26734 | -0.062396 | -0.42684 | 0.054004 | -0.058339 | 0.004057 | -0.033894 | -0.34662 | 123.4928 | 123.1225 | 123.306 | 67.0821 | -123.4629 | 123.1465 | 123.5394 | 123.2267 | 67.0902 | -123.6357
48.2812 | 123.7289 | -67.0624 | 56.5338 | 0.047088 | -0.00025117 | -0.00053454 | 0.056664 | -0.0012359 | 0.056874 | 0.065477 | 0.00041927 | 0.002084 | 0.063805 | -0.00092216 | 0.064162 | -67.0632 | 0.015142 | -66.9337 | 56.4304 | 56.0601 | 56.1841 | -66.9428 | -67.0175 | 0.014095 | -67.1253 | 56.0749 | 56.4587 | 56.1552 | -67.1431 | 0.11955 | -0.10342 | -0.0008 | 0.12866 | 0.009115 | -0.47368 | -0.34975 | -0.080709 | -0.45889 | 0.044849 | -0.062915 | 0.017794 | -0.075095 | -0.37866 | 123.4928 | 123.1225 | 123.2464 | 67.0775 | -123.4766 | 123.1373 | 123.5211 | 123.2175 | 67.0765 | -123.6769
49.2656 | 123.7198 | -67.0441 | 56.5292 | 0.06235 | -0.00025117 | -0.00053454 | 0.056664 | -0.00016792 | 0.05901 | 0.095999 | 0.00041927 | 0.003152 | 0.064873 | 0.00014684 | 0.066298 | -67.0678 | 0.010564 | -66.9337 | 56.4304 | 56.0647 | 56.2161 | -66.8879 | -67.0175 | 0.004938 | -67.1299 | 56.0383 | 56.4587 | 56.1552 | -67.1431 | 0.15618 | -0.09884 | -0.023689 | 0.11035 | -0.045832 | -0.46452 | -0.31312 | -0.09902 | -0.49094 | 0.026538 | -0.085805 | 0.013215 | -0.070518 | -0.37408 | 123.4745 | 123.1088 | 123.2602 | 67.0546 | -123.4171 | 123.0824 | 123.5028 | 123.1992 | 67.049 | -123.6723
50.2812 | 123.7885 | -67.0258 | 56.4606 | 0.06235 | -0.00025117 | -0.00053454 | 0.055596 | -0.00016792 | 0.057942 | 0.050216 | -0.00064973 | 0.001016 | 0.063805 | 0.0012148 | 0.06523 | -67.0632 | 0.005985 | -66.9291 | 56.4121 | 56.1013 | 56.2161 | -66.9016 | -67.013 | 0.014095 | -67.1253 | 56.0932 | 56.4541 | 56.1414 | -67.1431 | 0.12414 | -0.048489 | -0.037421 | 0.096621 | -0.027517 | -0.35923 | -0.24446 | -0.11733 | -0.36733 | 0.012807 | -0.099536 | 0.017794 | -0.006431 | -0.31915 | 123.4378 | 123.1271 | 123.2419 | 67.0317 | -123.3622 | 123.119 | 123.4799 | 123.1672 | 67.0399 | -123.6037
51.2656 | 123.7381 | -67.0303 | 56.5338 | 0.077612 | -0.0013202 | -0.00053454 | 0.056664 | -0.0012359 | 0.055805 | 0.050216 | -0.00064973 | -5.2e-05 | 0.063805 | 0.00014684 | 0.066298 | -67.0632 | 0.019721 | -66.9566 | 56.4533 | 56.1334 | 56.2848 | -67.0665 | -67.0221 | 0.014095 | -67.1253 | 56.1757 | 56.4679 | 56.2055 | -67.1385 | -0.036126 | -0.080525 | -0.032844 | 0.073728 | 0.10985 | -0.40042 | -0.24902 | -0.10817 | -0.35816 | 0.008227 | -0.094959 | 0.013215 | -0.065937 | -0.3283 | 123.4836 | 123.1637 | 123.3151 | 67.0501 | -123.6003 | 123.206 | 123.4982 | 123.2359 | 67.0444 | -123.6723
52.2812 | 123.7427 | -67.0578 | 56.5063 | 0.047088 | -0.00025117 | -0.00053454 | 0.056664 | -0.00016792 | 0.057942 | 0.095999 | -0.00064973 | -5.2e-05 | 0.064873 | 0.00014684 | 0.06523 | -67.054 | 0.028878 | -66.952 | 56.4487 | 56.1792 | 56.2848 | -67.0848 | -67.0267 | 0.014095 | -67.1299 | 56.1757 | 56.4633 | 56.2147 | -67.1431 | -0.026976 | -0.057639 | 0.003779 | 0.10577 | 0.13275 | -0.32716 | -0.22156 | -0.085287 | -0.3307 | 0.031114 | -0.072072 | 0.013215 | -0.043051 | -0.29167 | 123.5065 | 123.237 | 123.3426 | 67.0867 | -123.5911 | 123.2335 | 123.5211 | 123.2725 | 67.0719 | -123.6494
53.2656 | 123.6786 | -67.067 | 56.5292 | 0.047088 | -0.0013202 | 0.0016025 | 0.056664 | 0.00090108 | 0.056874 | 0.050216 | -0.0017177 | -0.001121 | 0.06701 | 0.00014684 | 0.06523 | -67.0632 | 0.0243 | -66.9566 | 56.4441 | 56.1746 | 56.2848 | -67.0985 | -67.0313 | 0.018674 | -67.1253 | 56.1757 | 56.4679 | 56.2101 | -67.1385 | -0.031557 | -0.085105 | 0.003778 | 0.11035 | 0.14191 | -0.35463 | -0.24445 | -0.071552 | -0.35358 | 0.035691 | -0.058337 | 0.013215 | -0.06136 | -0.31914 | 123.5111 | 123.2416 | 123.3517 | 67.0913 | -123.6277 | 123.2426 | 123.5348 | 123.2771 | 67.0856 | -123.6677
54.2656 | 123.6877 | -67.0395 | 56.5475 | 0.047088 | 0.00081683 | 0.00053446 | 0.056664 | 0.0019691 | 0.056874 | 0.065477 | -0.00064973 | -5.2e-05 | 0.064873 | 0.00014684 | 0.066298 | -67.0586 | 0.015142 | -66.952 | 56.4487 | 56.1609 | 56.2848 | -67.0436 | -67.0221 | 0.014095 | -67.1299 | 56.1757 | 56.4725 | 56.2193 | -67.1385 | -0.004075 | -0.098837 | -0.019109 | 0.087463 | 0.091538 | -0.38668 | -0.26276 | -0.099018 | -0.37189 | 0.017383 | -0.090382 | 0.008636 | -0.075092 | -0.32829 | 123.4882 | 123.2004 | 123.3243 | 67.0546 | -123.5911 | 123.2151 | 123.5119 | 123.2587 | 67.0536 | -123.6861
55.2656 | 123.7106 | -67.0578 | 56.5521 | 0.047088 | -0.0013202 | -0.00053454 | 0.057733 | 0.00090108 | 0.056874 | 0.080738 | -0.0017177 | 0.001016 | 0.064873 | 0.0022838 | 0.064162 | -67.0586 | 0.015142 | -66.9566 | 56.4579 | 56.1746 | 56.2894 | -67.0298 | -67.0358 | 0.018674 | -67.1253 | 56.1711 | 56.4725 | 56.1872 | -67.1431 | 0.027971 | -0.094258 | -0.000799 | 0.10119 | 0.073223 | -0.37752 | -0.26275 | -0.085287 | -0.38105 | 0.021957 | -0.067493 | 0.017794 | -0.07967 | -0.36492 | 123.5157 | 123.2324 | 123.3472 | 67.0729 | -123.582 | 123.2289 | 123.5303 | 123.245 | 67.0765 | -123.6952
56.2812 | 123.8113 | -67.0258 | 56.4606 | 0.047088 | -0.00025117 | -0.0016025 | 0.056664 | 0.00090108 | 0.057942 | 0.050216 | -0.00064973 | 0.001016 | 0.065941 | 0.0022838 | 0.063094 | -67.0586 | 0.019721 | -66.9566 | 56.467 | 56.0968 | 56.2756 | -66.9428 | -67.0313 | 0.023253 | -67.1253 | 56.1757 | 56.4633 | 56.1872 | -67.1385 | 0.082928 | 0.006452 | -0.032842 | 0.069151 | -0.013777 | -0.36381 | -0.18494 | -0.11275 | -0.28492 | -0.005508 | -0.099536 | 0.013215 | 0.002726 | -0.27337 | 123.4928 | 123.1225 | 123.3014 | 67.0455 | -123.4034 | 123.2014 | 123.4891 | 123.213 | 67.049 | -123.5991
57.2656 | 123.7061 | -67.0441 | 56.5475 | 0.06235 | -0.0023882 | 0.00053446 | 0.055596 | -0.00016792 | 0.060079 | 0.080738 | 0.00041927 | -0.001121 | 0.064873 | 0.00014684 | 0.06523 | -67.0586 | 0.0243 | -66.9566 | 56.4579 | 56.1471 | 56.2939 | -67.0344 | -67.0404 | 0.014095 | -67.1253 | 56.1757 | 56.4679 | 56.1918 | -67.1339 | 0.009659 | -0.08968 | -0.014532 | 0.087461 | 0.077802 | -0.40041 | -0.2536 | -0.089862 | -0.37189 | 0.003645 | -0.081226 | 0.008636 | -0.07967 | -0.35576 | 123.5019 | 123.1912 | 123.338 | 67.0684 | -123.582 | 123.2197 | 123.5119 | 123.2358 | 67.0582 | -123.6815
58.2656 | 123.6969 | -67.0761 | 56.5384 | 0.047088 | -0.00025117 | -0.0016025 | 0.057733 | 0.00090108 | 0.055805 | 0.034955 | 0.00041927 | -5.2e-05 | 0.064873 | 0.00014684 | 0.064162 | -67.0586 | 0.015142 | -66.9337 | 56.4304 | 56.2204 | 56.2802 | -67.0985 | -67.0175 | 0.014095 | -67.1299 | 56.2855 | 56.4541 | 56.4757 | -67.1385 | -0.022402 | -0.10799 | 0.017512 | 0.1424 | 0.1648 | -0.318 | -0.25818 | -0.062397 | -0.25285 | 0.058582 | -0.053761 | 0.008636 | -0.084251 | -0.062735 | 123.5065 | 123.2965 | 123.3563 | 67.0913 | -123.6369 | 123.3616 | 123.5303 | 123.5518 | 67.0902 | -123.6769
59.2812 | 123.6557 | -67.0853 | 56.5201 | 0.031826 | 0.00081683 | 0.00053446 | 0.056664 | -0.00016792 | 0.055805 | 0.080738 | 0.00041927 | 0.002084 | 0.063805 | 0.0012148 | 0.063094 | -67.0678 | 0.010564 | -66.9291 | 56.435 | 56.2433 | 56.2665 | -67.0894 | -67.0038 | 0.009516 | -67.1299 | 56.2535 | 56.4633 | 56.3795 | -67.1431 | -0.004089 | -0.085107 | 0.01751 | 0.15613 | 0.16022 | -0.27679 | -0.25361 | -0.057821 | -0.26659 | 0.081474 | -0.044606 | 0.013215 | -0.056784 | -0.14058 | 123.5202 | 123.3286 | 123.3517 | 67.0958 | -123.6094 | 123.3388 | 123.5486 | 123.4648 | 67.0948 | -123.6632
60.2812 | 123.7656 | -67.0486 | 56.5384 | 0.031826 | -0.0013202 | 0.00053446 | 0.056664 | -0.00016792 | 0.056874 | 0.065477 | -0.00064973 | -5.2e-05 | 0.064873 | 0.0012148 | 0.064162 | -67.0586 | 0.005985 | -66.9383 | 56.435 | 56.3257 | 56.2573 | -67.0481 | -67.0175 | 0.009516 | -67.1299 | 56.2489 | 56.4633 | 56.407 | -67.1431 | 0.000501 | -0.10342 | -0.009954 | 0.11035 | 0.10985 | -0.21268 | -0.28107 | -0.094442 | -0.28948 | 0.031116 | -0.081227 | 0.013215 | -0.075094 | -0.13141 | 123.4836 | 123.3744 | 123.306 | 67.0546 | -123.5865 | 123.2976 | 123.5119 | 123.4556 | 67.0582 | -123.6815
61.2656 | 123.6969 | -67.0532 | 56.5338 | 0.06235 | 0.0018858 | 0.00053446 | 0.056664 | -0.0012359 | 0.055805 | 0.080738 | -0.0017177 | -5.2e-05 | 0.064873 | 0.0033518 | 0.064162 | -67.0632 | 0.005985 | -66.9337 | 56.4258 | 56.2067 | 56.2619 | -67.0527 | -67.0175 | 0.004938 | -67.1299 | 56.226 | 56.4679 | 56.2376 | -67.1339 | 0.0005 | -0.108 | -0.009955 | 0.11951 | 0.11901 | -0.32716 | -0.27192 | -0.080706 | -0.3078 | 0.035694 | -0.076649 | 0.004057 | -0.065937 | -0.29624 | 123.479 | 123.2599 | 123.3151 | 67.0592 | -123.5865 | 123.2792 | 123.5211 | 123.2908 | 67.0582 | -123.6677
62.2812 | 123.7564 | -67.0532 | 56.4835 | 0.047088 | -0.0013202 | 0.00053446 | 0.055596 | -0.0023039 | 0.055805 | 0.050216 | 0.00041927 | -0.001121 | 0.065941 | 0.0012148 | 0.064162 | -67.0632 | 0.005985 | -66.9291 | 56.4212 | 56.1929 | 56.2619 | -67.0436 | -67.0175 | 0.009516 | -67.1253 | 56.1985 | 56.4587 | 56.2467 | -67.1431 | 0.009658 | -0.06222 | -0.009955 | 0.12409 | 0.11443 | -0.29054 | -0.22156 | -0.089864 | -0.28491 | 0.035694 | -0.07207 | 0.017794 | -0.024741 | -0.23673 | 123.4745 | 123.2461 | 123.3151 | 67.0592 | -123.527 | 123.2518 | 123.5119 | 123.2999 | 67.0627 | -123.6265
63.2656 | 123.7106 | -67.0807 | 56.5475 | 0.06235 | -0.00025117 | 0.0026715 | 0.058801 | -0.00016792 | 0.055805 | 0.080738 | -0.00064973 | -0.001121 | 0.063805 | 0.0022838 | 0.064162 | -67.0586 | 0.010564 | -66.9246 | 56.4258 | 56.1929 | 56.2711 | -67.0436 | -67.0313 | 0.009516 | -67.1253 | 56.1894 | 56.4587 | 56.2605 | -67.1339 | 0.037123 | -0.12173 | 0.022089 | 0.15613 | 0.11901 | -0.35462 | -0.27649 | -0.053241 | -0.35816 | 0.049423 | -0.044605 | 0.008636 | -0.088828 | -0.28708 | 123.5065 | 123.2736 | 123.3517 | 67.0913 | -123.5911 | 123.2701 | 123.5394 | 123.3411 | 67.0902 | -123.6815
64.2656 | 123.7015 | -67.0578 | 56.5063 | 0.047088 | -0.0013202 | 0.0026715 | 0.056664 | -0.0012359 | 0.054737 | 0.050216 | 0.00041927 | -0.001121 | 0.064873 | 0.0022838 | 0.064162 | -67.054 | 0.010564 | -66.9383 | 56.4258 | 56.1563 | 56.2619 | -67.0344 | -67.0175 | 0.004938 | -67.1253 | 56.1848 | 56.4633 | 56.2513 | -67.1431 | 0.023392 | -0.080531 | 0.003779 | 0.11951 | 0.096115 | -0.35006 | -0.24445 | -0.085287 | -0.32154 | 0.040271 | -0.067493 | 0.017794 | -0.043051 | -0.25504 | 123.4836 | 123.2141 | 123.3197 | 67.0684 | -123.5408 | 123.2426 | 123.5211 | 123.3091 | 67.0627 | -123.6494
65.2812 | 123.7976 | -67.0532 | 56.4835 | 0.047088 | -0.0034562 | 0.0026715 | 0.057733 | -0.0023039 | 0.05901 | 0.095999 | -0.0017177 | -0.001121 | 0.062737 | 0.0012148 | 0.064162 | -67.054 | 0.028878 | -66.9932 | 56.4853 | 56.1426 | 56.2894 | -67.0207 | -67.0587 | 0.014095 | -67.1345 | 56.3222 | 56.4679 | 56.2421 | -67.1385 | 0.032552 | 0.001877 | -0.000798 | 0.059991 | 0.027439 | -0.34091 | -0.19409 | -0.085285 | -0.1613 | -0.005514 | -0.081227 | 0.004058 | -0.015583 | -0.24131 | 123.5386 | 123.1958 | 123.3426 | 67.0821 | -123.5041 | 123.3754 | 123.5211 | 123.2954 | 67.0673 | -123.622
66.2656 | 123.761 | -67.0441 | 56.5842 | 0.06235 | -0.00025117 | 0.00053446 | 0.055596 | -0.00016792 | 0.057942 | 0.065477 | -0.0017177 | -0.002189 | 0.064873 | 0.0044198 | 0.063094 | -67.0586 | 0.015142 | -66.9749 | 56.4762 | 56.1517 | 56.2848 | -67.0161 | -67.045 | 0.009516 | -67.1299 | 56.2947 | 56.4633 | 56.1872 | -67.1568 | 0.027975 | -0.10799 | -0.014532 | 0.069148 | 0.041173 | -0.43246 | -0.29938 | -0.11276 | -0.28947 | -0.000934 | -0.085805 | 0.026951 | -0.12087 | -0.39696 | 123.5202 | 123.1958 | 123.3289 | 67.0592 | -123.6003 | 123.3388 | 123.5074 | 123.2313 | 67.0536 | -123.741
67.2656 | 123.7106 | -67.0624 | 56.5475 | 0.077612 | 0.00081683 | 0.00053446 | 0.054527 | -0.00016792 | 0.055805 | 0.080738 | -0.00064973 | -5.2e-05 | 0.065941 | 0.0033518 | 0.064162 | -67.054 | 0.010564 | -66.9612 | 56.4396 | 56.1426 | 56.2665 | -66.9932 | -67.0404 | 0.009516 | -67.1207 | 56.1436 | 56.4679 | 56.1506 | -67.1431 | 0.069181 | -0.10799 | 0.008357 | 0.10119 | 0.032013 | -0.40499 | -0.28107 | -0.080709 | -0.40394 | 0.021956 | -0.058336 | 0.022373 | -0.07967 | -0.39697 | 123.5019 | 123.2049 | 123.3289 | 67.0729 | -123.5407 | 123.206 | 123.5303 | 123.213 | 67.0719 | -123.6906
68.2812 | 123.7427 | -67.067 | 56.5018 | 0.031826 | -0.0013202 | 0.00053446 | 0.056664 | 0.00090108 | 0.055805 | 0.065477 | 0.00041927 | 0.002084 | 0.063805 | 0.0044198 | 0.06523 | -67.0586 | 0.019721 | -66.9383 | 56.4441 | 56.1288 | 56.2848 | -67.0115 | -67.013 | 0.014095 | -67.1207 | 56.1619 | 56.4587 | 56.1277 | -67.1477 | 0.055443 | -0.057639 | 0.008357 | 0.12866 | 0.07322 | -0.37295 | -0.21698 | -0.08071 | -0.33985 | 0.054006 | -0.053758 | 0.026952 | -0.043052 | -0.37409 | 123.5111 | 123.1958 | 123.3517 | 67.0867 | -123.5133 | 123.2289 | 123.5257 | 123.1946 | 67.0811 | -123.6494
69.2656 | 123.6877 | -67.0486 | 56.5613 | 0.077612 | -0.00025117 | 0.0026715 | 0.056664 | 0.00090108 | 0.055805 | 0.095999 | 0.00041927 | -0.001121 | 0.063805 | 0.0044198 | 0.064162 | -67.0632 | 0.015142 | -66.9291 | 56.4304 | 56.1151 | 56.2665 | -66.9978 | -67.013 | 0.004938 | -67.1161 | 56.2626 | 56.4587 | 56.0956 | -67.1431 | 0.050869 | -0.13088 | -0.014533 | 0.11951 | 0.06864 | -0.4462 | -0.2948 | -0.094442 | -0.29863 | 0.035695 | -0.067491 | 0.026951 | -0.10256 | -0.46565 | 123.479 | 123.1637 | 123.3151 | 67.0638 | -123.5591 | 123.3113 | 123.5074 | 123.1443 | 67.0536 | -123.7044
70.2656 | 123.7289 | -67.0349 | 56.5247 | 0.06235 | -0.00025117 | -0.00053454 | 0.055596 | -0.0012359 | 0.055805 | 0.080738 | -0.00064973 | 0.001016 | 0.063805 | 0.0033518 | 0.064162 | -67.0632 | 0.019721 | -66.92 | 56.4258 | 56.0922 | 56.2482 | -66.9382 | -67.013 | 0.014095 | -67.1161 | 56.0932 | 56.4633 | 55.9766 | -67.1385 | 0.096662 | -0.098841 | -0.028266 | 0.11493 | 0.018271 | -0.43247 | -0.2765 | -0.1036 | -0.43142 | 0.021962 | -0.081224 | 0.022372 | -0.061361 | -0.54807 | 123.4607 | 123.1271 | 123.2831 | 67.0546 | -123.4629 | 123.1282 | 123.4982 | 123.0115 | 67.049 | -123.6632
71.2812 | 123.6603 | -67.0761 | 56.4835 | 0.06235 | -0.00025117 | -0.00053454 | 0.054527 | -0.0012359 | 0.053669 | 0.050216 | 0.00041927 | -5.2e-05 | 0.063805 | 0.0044198 | 0.064162 | -67.0632 | 0.010564 | -66.9246 | 56.4167 | 56.0189 | 56.207 | -66.9245 | -67.013 | 0.014095 | -67.1161 | 56.0841 | 56.4679 | 56.0132 | -67.1477 | 0.1516 | -0.066798 | 0.012933 | 0.15155 | -4.5e-05 | -0.46454 | -0.27651 | -0.071555 | -0.39938 | 0.063161 | -0.040025 | 0.03153 | -0.015583 | -0.47024 | 123.4928 | 123.095 | 123.2831 | 67.0867 | -123.408 | 123.1602 | 123.544 | 123.0893 | 67.0902 | -123.6311
72.2812 | 123.6969 | -67.0898 | 56.5155 | 0.06235 | -0.0013202 | 0.00053446 | 0.055596 | -0.0012359 | 0.056874 | 0.065477 | 0.0014873 | 0.001016 | 0.065941 | 0.0065568 | 0.064162 | -67.054 | 0.010564 | -66.9291 | 56.4258 | 56.0143 | 56.1841 | -66.8467 | -67.0084 | 0.014095 | -67.1299 | 56.107 | 56.4679 | 56.0086 | -67.1431 | 0.24317 | -0.089686 | 0.035823 | 0.16071 | -0.082464 | -0.50116 | -0.33144 | -0.053243 | -0.40853 | 0.081473 | -0.040028 | 0.013215 | -0.047627 | -0.50687 | 123.5157 | 123.1042 | 123.2739 | 67.1004 | -123.3622 | 123.1968 | 123.5577 | 123.0985 | 67.1039 | -123.6586
73.2656 | 123.6877 | -67.0624 | 56.5247 | 0.031826 | -0.0013202 | -0.00053454 | 0.054527 | -0.0012359 | 0.054737 | 0.034955 | 0.0014873 | -0.001121 | 0.063805 | 0.0044198 | 0.06523 | -67.0586 | 0.005985 | -66.9291 | 56.4167 | 55.9731 | 56.2253 | -66.984 | -67.0038 | 0.004938 | -67.1253 | 56.0978 | 56.4587 | 56.0315 | -67.1431 | 0.078339 | -0.108 | 0.003779 | 0.13324 | 0.054903 | -0.55153 | -0.29939 | -0.080709 | -0.42684 | 0.058586 | -0.062915 | 0.017794 | -0.06594 | -0.49313 | 123.479 | 123.0355 | 123.2876 | 67.0684 | -123.5087 | 123.1602 | 123.5211 | 123.0939 | 67.0673 | -123.6677
74.2812 | 123.7106 | -67.0532 | 56.4972 | 0.047088 | -0.0013202 | 0.00053446 | 0.056664 | -0.00016792 | 0.055805 | 0.065477 | -0.00064973 | -5.2e-05 | 0.063805 | 0.0044198 | 0.064162 | -67.054 | 0.001407 | -66.9291 | 56.4121 | 56.0098 | 56.2115 | -66.8879 | -67.0175 | 0.014095 | -67.1253 | 56.0429 | 56.4633 | 55.9857 | -67.1385 | 0.16534 | -0.08511 | -0.000798 | 0.12409 | -0.041254 | -0.48743 | -0.28566 | -0.085285 | -0.45432 | 0.035694 | -0.07207 | 0.013215 | -0.033895 | -0.51145 | 123.4653 | 123.063 | 123.2648 | 67.0546 | -123.3851 | 123.0961 | 123.5165 | 123.039 | 67.0673 | -123.6357
75.2656 | 123.7106 | -67.0486 | 56.5018 | 0.06235 | -0.0013202 | -0.00053454 | 0.055596 | 0.00090108 | 0.055805 | 0.050216 | 0.00041927 | -0.001121 | 0.062737 | 0.0044198 | 0.063094 | -67.0632 | 0.015142 | -66.9291 | 56.4212 | 56.0281 | 56.1932 | -66.9474 | -67.0084 | 0.009516 | -67.1253 | 56.0887 | 56.4633 | 55.972 | -67.1339 | 0.10124 | -0.080531 | -0.014533 | 0.11951 | 0.018272 | -0.47369 | -0.30855 | -0.085284 | -0.41311 | 0.040274 | -0.076648 | 0.008636 | -0.038473 | -0.52976 | 123.4699 | 123.0767 | 123.2419 | 67.0638 | -123.4492 | 123.1373 | 123.5119 | 123.0207 | 67.0582 | -123.6357
76.2656 | 123.6923 | -67.0532 | 56.543 | 0.06235 | -0.0013202 | -0.00053454 | 0.054527 | -0.0012359 | 0.055805 | 0.080738 | 0.00041927 | -0.001121 | 0.063805 | 0.0044198 | 0.063094 | -67.054 | 0.010564 | -66.9383 | 56.4212 | 56.051 | 56.1978 | -66.7963 | -67.013 | 0.009516 | -67.1207 | 56.107 | 56.4541 | 55.9903 | -67.1385 | 0.25692 | -0.12173 | -0.000798 | 0.11493 | -0.14199 | -0.492 | -0.34517 | -0.085285 | -0.43599 | 0.040273 | -0.067491 | 0.017794 | -0.088829 | -0.55264 | 123.4745 | 123.1042 | 123.251 | 67.0638 | -123.3393 | 123.1602 | 123.5074 | 123.0435 | 67.0627 | -123.6815
77.2812 | 123.7656 | -67.0624 | 56.5201 | 0.047088 | 0.00081683 | -0.0016025 | 0.054527 | -0.00016792 | 0.054737 | 0.080738 | -0.00064973 | -5.2e-05 | 0.063805 | 0.0054888 | 0.062025 | -67.054 | 0.010564 | -66.9337 | 56.4121 | 56.0235 | 56.1886 | -66.9154 | -67.0084 | 0.014095 | -67.1161 | 56.0383 | 56.4679 | 55.9949 | -67.1385 | 0.14702 | -0.108 | 0.008357 | 0.12866 | -0.018358 | -0.49658 | -0.33144 | -0.07613 | -0.48178 | 0.054007 | -0.053758 | 0.022372 | -0.052205 | -0.52518 | 123.4745 | 123.0859 | 123.251 | 67.0729 | -123.4354 | 123.1007 | 123.5303 | 123.0573 | 67.0765 | -123.6586
78.2656 | 123.7518 | -67.0624 | 56.543 | 0.077612 | 0.00081683 | 0.00053446 | 0.054527 | -0.0012359 | 0.055805 | 0.065477 | -0.00064973 | -5.2e-05 | 0.063805 | 0.0054888 | 0.063094 | -67.0586 | 0.010564 | -66.9291 | 56.4304 | 55.9869 | 56.2344 | -66.8833 | -67.0175 | 0.004938 | -67.1207 | 56.1299 | 56.4633 | 55.9949 | -67.1385 | 0.17907 | -0.11257 | 0.003779 | 0.13324 | -0.045833 | -0.5561 | -0.30854 | -0.07613 | -0.4131 | 0.044849 | -0.058336 | 0.017794 | -0.079672 | -0.54807 | 123.4928 | 123.0492 | 123.2968 | 67.0729 | -123.4263 | 123.1922 | 123.5257 | 123.0573 | 67.0673 | -123.6815
79.2656 | 123.7289 | -67.0441 | 56.5292 | 0.06235 | -0.0013202 | 0.00053446 | 0.057733 | -0.0012359 | 0.053669 | 0.034955 | 0.00041927 | -0.001121 | 0.063805 | 0.0054888 | 0.06523 | -67.0632 | 0.019721 | -66.9246 | 56.4167 | 56.051 | 56.239 | -66.9291 | -67.0175 | 0.009516 | -67.1253 | 56.1024 | 56.4541 | 55.9857 | -67.1385 | 0.11498 | -0.11257 | -0.019111 | 0.11951 | 0.004534 | -0.47826 | -0.29023 | -0.094441 | -0.42684 | 0.026538 | -0.081226 | 0.013215 | -0.075096 | -0.54349 | 123.4607 | 123.095 | 123.2831 | 67.0638 | -123.4583 | 123.1465 | 123.4982 | 123.0298 | 67.0536 | -123.6677
80.2812 | 123.7701 | -67.0303 | 56.488 | 0.047088 | -0.0013202 | 0.00053446 | 0.056664 | -0.0012359 | 0.053669 | 0.065477 | 0.0014873 | -0.001121 | 0.063805 | 0.0076248 | 0.062025 | -67.0632 | 0.015142 | -66.9246 | 56.4167 | 56.0006 | 56.2024 | -66.9703 | -67.0038 | 0.014095 | -67.1299 | 56.0429 | 56.4633 | 56.0453 | -67.1431 | 0.060031 | -0.071376 | -0.032844 | 0.10578 | 0.045745 | -0.48743 | -0.28566 | -0.11275 | -0.44516 | 0.026542 | -0.099538 | 0.013215 | -0.02474 | -0.44277 | 123.447 | 123.0309 | 123.2327 | 67.0455 | -123.4583 | 123.0732 | 123.4936 | 123.0756 | 67.0444 | -123.6311
81.2656 | 123.6923 | -67.0532 | 56.543 | 0.047088 | -0.0013202 | -0.00053454 | 0.055596 | -0.0023039 | 0.053669 | 0.065477 | -0.00064973 | -0.001121 | 0.062737 | 0.0065568 | 0.063094 | -67.054 | 0.010564 | -66.92 | 56.4258 | 56.0098 | 56.2207 | -66.984 | -67.013 | 0.009516 | -67.1207 | 56.0749 | 56.4633 | 56.0453 | -67.1522 | 0.069184 | -0.11715 | -0.000798 | 0.13324 | 0.06406 | -0.53321 | -0.32228 | -0.099021 | -0.46804 | 0.040273 | -0.067491 | 0.03153 | -0.079672 | -0.4977 | 123.479 | 123.063 | 123.2739 | 67.0638 | -123.527 | 123.1281 | 123.5165 | 123.0985 | 67.0627 | -123.6952
82.2656 | 123.7015 | -67.0578 | 56.5567 | 0.06235 | -0.0013202 | 0.00053446 | 0.055596 | -0.0012359 | 0.055805 | 0.065477 | -0.00064973 | -0.001121 | 0.063805 | 0.0044198 | 0.063094 | -67.054 | 0.010564 | -66.9291 | 56.4212 | 56.0189 | 56.2298 | -66.9291 | -67.0084 | 0.009516 | -67.1207 | 56.1116 | 56.4633 | 56.0224 | -67.1477 | 0.12871 | -0.13546 | 0.003779 | 0.12866 | -4.4e-05 | -0.53778 | -0.32686 | -0.089866 | -0.44515 | 0.049429 | -0.062914 | 0.026952 | -0.093405 | -0.53433 | 123.479 | 123.0767 | 123.2876 | 67.0684 | -123.4858 | 123.1694 | 123.5211 | 123.0802 | 67.0673 | -123.7044
83.2656 | 123.7061 | -67.0898 | 56.5063 | 0.047088 | -0.0013202 | 0.00053446 | 0.056664 | -0.00016792 | 0.054737 | 0.050216 | -0.0017177 | -0.001121 | 0.062737 | 0.0054888 | 0.063094 | -67.054 | 0.015142 | -66.9291 | 56.4167 | 56.0372 | 56.2527 | -66.8925 | -67.0084 | 0.009516 | -67.1299 | 56.107 | 56.4633 | 55.9812 | -67.1431 | 0.19738 | -0.089687 | 0.035823 | 0.16071 | -0.036675 | -0.46911 | -0.25361 | -0.053243 | -0.39937 | 0.081473 | -0.040028 | 0.013215 | -0.043051 | -0.52518 | 123.5065 | 123.1271 | 123.3426 | 67.105 | -123.3988 | 123.1968 | 123.5531 | 123.071 | 67.0994 | -123.6494
84.2812 | 123.6511 | -67.0807 | 56.5063 | 0.031826 | 0.00081683 | 0.00053446 | 0.053459 | -0.00016792 | 0.054737 | 0.065477 | -0.0017177 | -5.2e-05 | 0.065941 | 0.0044198 | 0.063094 | -67.054 | 0.005985 | -66.9291 | 56.4212 | 56.0281 | 56.1932 | -66.8879 | -67.0084 | 0.014095 | -67.1207 | 56.0795 | 56.4633 | 55.9995 | -67.1431 | 0.19281 | -0.085109 | 0.026667 | 0.15155 | -0.041254 | -0.47827 | -0.31313 | -0.062399 | -0.42684 | 0.072317 | -0.040026 | 0.022373 | -0.043051 | -0.50687 | 123.5019 | 123.1088 | 123.2739 | 67.0867 | -123.3942 | 123.1602 | 123.544 | 123.0802 | 67.0948 | -123.6494
85.2656 | 123.7518 | -67.0349 | 56.5018 | 0.031826 | -0.0013202 | -0.00053454 | 0.055596 | -0.0012359 | 0.053669 | 0.065477 | -0.00064973 | -0.002189 | 0.062737 | 0.0065568 | 0.062025 | -67.054 | 0.010564 | -66.9291 | 56.4212 | 56.051 | 56.2115 | -66.9154 | -67.0175 | 0.009516 | -67.1253 | 56.0475 | 56.4633 | 55.9812 | -67.1477 | 0.11956 | -0.080531 | -0.019109 | 0.10578 | -0.01378 | -0.4508 | -0.29024 | -0.11275 | -0.45432 | 0.017383 | -0.090381 | 0.022373 | -0.038473 | -0.5206 | 123.4562 | 123.0859 | 123.2464 | 67.0455 | -123.4171 | 123.0824 | 123.4982 | 123.0161 | 67.0444 | -123.6494
86.2812 | 123.7885 | -67.0349 | 56.5018 | 0.06235 | -0.0013202 | -0.00053454 | 0.057733 | -0.00016792 | 0.054737 | 0.080738 | -0.00064973 | -0.001121 | 0.063805 | 0.0076248 | 0.062025 | -67.0586 | 0.005985 | -66.92 | 56.4212 | 56.0189 | 56.1978 | -66.9474 | -66.9946 | 0.000359 | -67.1207 | 56.0383 | 56.4679 | 56.0361 | -67.1477 | 0.087504 | -0.080531 | -0.023687 | 0.11493 | 0.027429 | -0.48285 | -0.30397 | -0.11275 | -0.46347 | 0.040277 | -0.085802 | 0.026952 | -0.033894 | -0.46566 | 123.4562 | 123.0538 | 123.2327 | 67.0409 | -123.4492 | 123.0732 | 123.5028 | 123.071 | 67.0353 | -123.6494
87.2656 | 123.7015 | -67.0395 | 56.5292 | 0.077612 | -0.0023882 | 0.00053446 | 0.054527 | -0.00016792 | 0.054737 | 0.065477 | -0.00064973 | -0.001121 | 0.064873 | 0.0065568 | 0.062025 | -67.0494 | 0.005985 | -66.9291 | 56.4258 | 55.9777 | 56.2207 | -66.9703 | -67.0084 | 0.014095 | -67.1161 | 56.0703 | 56.4496 | 56.0315 | -67.1431 | 0.069187 | -0.10342 | -0.009953 | 0.11035 | 0.041167 | -0.55152 | -0.30855 | -0.1036 | -0.45889 | 0.031119 | -0.076646 | 0.026951 | -0.079675 | -0.4977 | 123.4653 | 123.0172 | 123.2602 | 67.0455 | -123.4995 | 123.1098 | 123.4891 | 123.071 | 67.0536 | -123.6723
88.2812 | 123.6694 | -67.0761 | 56.5018 | 0.031826 | -0.0013202 | 0.0016025 | 0.055596 | -0.0012359 | 0.054737 | 0.065477 | -0.0017177 | -5.2e-05 | 0.063805 | 0.0065568 | 0.064162 | -67.0494 | 0.010564 | -66.9246 | 56.4167 | 56.0189 | 56.2253 | -66.9474 | -66.9992 | 0.014095 | -67.1253 | 56.052 | 56.4587 | 55.9857 | -67.1477 | 0.1287 | -0.085109 | 0.026668 | 0.15155 | 0.02285 | -0.48285 | -0.2765 | -0.071555 | -0.44974 | 0.076897 | -0.049182 | 0.022373 | -0.043052 | -0.51602 | 123.4928 | 123.095 | 123.3014 | 67.0867 | -123.4492 | 123.1281 | 123.5348 | 123.0619 | 67.0902 | -123.6494
89.2812 | 123.6832 | -67.0761 | 56.5063 | 0.047088 | -0.0013202 | -0.00053454 | 0.055596 | -0.0012359 | 0.054737 | 0.065477 | -0.0027857 | -0.002189 | 0.064873 | 0.0065568 | 0.062025 | -67.0494 | 0.015142 | -66.9246 | 56.4167 | 55.9731 | 56.2024 | -66.8879 | -67.0084 | 0.009516 | -67.1116 | 56.0108 | 56.4633 | 56.0132 | -67.1431 | 0.18823 | -0.089687 | 0.026668 | 0.15155 | -0.036676 | -0.53322 | -0.30397 | -0.066976 | -0.49552 | 0.06774 | -0.035446 | 0.03153 | -0.043051 | -0.49313 | 123.4928 | 123.0492 | 123.2785 | 67.0913 | -123.3942 | 123.0869 | 123.5394 | 123.0893 | 67.0856 | -123.6494
90.2656 | 123.7106 | -67.067 | 56.5155 | 0.06235 | -0.0013202 | 0.0016025 | 0.054527 | -0.0023039 | 0.053669 | 0.050216 | -0.00064973 | -0.001121 | 0.062737 | 0.0065568 | 0.062025 | -67.054 | 0.010564 | -66.9291 | 56.4167 | 56.0556 | 56.2344 | -66.984 | -67.0084 | 0.004938 | -67.1161 | 56.0978 | 56.4541 | 55.9812 | -67.1431 | 0.082917 | -0.098842 | 0.012935 | 0.13782 | 0.054903 | -0.45995 | -0.28108 | -0.076131 | -0.41769 | 0.058585 | -0.04918 | 0.026951 | -0.061363 | -0.53434 | 123.4836 | 123.1225 | 123.3014 | 67.0775 | -123.4995 | 123.1648 | 123.5211 | 123.0481 | 67.0719 | -123.6586
91.2812 | 123.793 | -67.0212 | 56.4514 | 0.047088 | -0.00025117 | -0.0016025 | 0.054527 | -0.00016792 | 0.0526 | 0.065477 | 0.00041927 | -5.2e-05 | 0.063805 | 0.0086938 | 0.062025 | -67.0586 | 0.015142 | -66.92 | 56.4212 | 56.0327 | 56.2161 | -66.9291 | -67.0084 | 0.014095 | -67.1207 | 56.0475 | 56.4541 | 55.9857 | -67.1477 | 0.092087 | -0.030177 | -0.03742 | 0.1012 | 0.009113 | -0.41876 | -0.23531 | -0.12649 | -0.40396 | 0.012808 | -0.099535 | 0.026952 | 0.002724 | -0.46567 | 123.4424 | 123.0538 | 123.2373 | 67.0363 | -123.3805 | 123.0686 | 123.4753 | 123.0069 | 67.0353 | -123.5991
92.2812 | 123.7198 | -67.0624 | 56.5063 | 0.06235 | -0.00025117 | -0.00053454 | 0.054527 | -0.0012359 | 0.0526 | 0.080738 | 0.00041927 | -0.001121 | 0.062737 | 0.0076248 | 0.063094 | -67.054 | 0.015142 | -66.9291 | 56.4212 | 56.0281 | 56.2619 | -66.8604 | -67.0038 | 0.004938 | -67.1161 | 56.1207 | 56.4587 | 55.9949 | -67.1385 | 0.20197 | -0.085109 | 0.008357 | 0.13324 | -0.068728 | -0.47827 | -0.24445 | -0.07613 | -0.38564 | 0.058586 | -0.053758 | 0.022372 | -0.04763 | -0.51145 | 123.4836 | 123.0905 | 123.3243 | 67.0775 | -123.3668 | 123.1831 | 123.5211 | 123.0573 | 67.0673 | -123.6449
93.2656 | 123.7061 | -67.0349 | 56.5109 | 0.047088 | -0.0013202 | -0.00053454 | 0.055596 | -0.00016792 | 0.0526 | 0.065477 | -0.00064973 | -0.001121 | 0.062737 | 0.0076248 | 0.05882 | -67.0494 | 0.010564 | -66.9291 | 56.4258 | 56.0189 | 56.2207 | -66.9428 | -67.0084 | 0.004938 | -67.1161 | 56.0703 | 56.4633 | 55.9812 | -67.1477 | 0.092083 | -0.085108 | -0.014531 | 0.10578 | 0.013693 | -0.492 | -0.29024 | -0.11275 | -0.44058 | 0.026541 | -0.081224 | 0.03153 | -0.047628 | -0.52976 | 123.4607 | 123.0538 | 123.2556 | 67.0455 | -123.4538 | 123.1053 | 123.4982 | 123.0161 | 67.0399 | -123.6586
94.2812 | 123.7976 | -67.0303 | 56.488 | 0.06235 | -0.0023882 | 0.00053446 | 0.053459 | -0.0012359 | 0.0526 | 0.065477 | -0.0017177 | -0.001121 | 0.062737 | 0.0076248 | 0.063094 | -67.054 | 0.010564 | -66.9246 | 56.4212 | 55.9869 | 56.1978 | -66.9566 | -67.013 | 0.004938 | -67.1253 | 56.02 | 56.4633 | 55.972 | -67.1477 | 0.073768 | -0.066798 | -0.023687 | 0.10578 | 0.032008 | -0.50117 | -0.29024 | -0.11733 | -0.46805 | 0.017384 | -0.094959 | 0.022373 | -0.02474 | -0.51603 | 123.4516 | 123.0172 | 123.2281 | 67.0409 | -123.4446 | 123.0503 | 123.4936 | 123.0023 | 67.0353 | -123.6357
95.2656 | 123.7152 | -67.0486 | 56.5109 | 0.06235 | 0.00081683 | 0.00053446 | 0.054527 | -0.00016792 | 0.053669 | 0.065477 | -0.0017177 | -5.2e-05 | 0.063805 | 0.0086938 | 0.062025 | -67.0586 | 0.015142 | -66.9246 | 56.4212 | 56.0281 | 56.239 | -66.8604 | -67.0038 | 0.009516 | -67.1161 | 56.0658 | 56.4541 | 56.0407 | -67.1477 | 0.18824 | -0.089686 | -0.009954 | 0.12409 | -0.06415 | -0.48284 | -0.27192 | -0.099021 | -0.44516 | 0.044853 | -0.067491 | 0.03153 | -0.056785 | -0.47024 | 123.4699 | 123.0767 | 123.2876 | 67.0638 | -123.3713 | 123.1144 | 123.5028 | 123.0893 | 67.0582 | -123.6586
96.2812 | 123.8159 | -66.9891 | 56.488 | 0.06235 | -0.00025117 | -0.00053454 | 0.055596 | -0.0012359 | 0.054737 | 0.080738 | -0.00064973 | -5.2e-05 | 0.062737 | 0.0076248 | 0.060957 | -67.0494 | 0.010564 | -66.9246 | 56.4258 | 56.0098 | 56.2298 | -66.9199 | -67.0038 | 0.009516 | -67.1207 | 56.0749 | 56.4541 | 56.0498 | -67.1385 | 0.069201 | -0.06222 | -0.060307 | 0.064578 | -0.004623 | -0.47827 | -0.25819 | -0.14937 | -0.41311 | -0.014656 | -0.13158 | 0.017794 | -0.033897 | -0.43819 | 123.415 | 122.9989 | 123.219 | 66.9997 | -123.408 | 123.0641 | 123.4433 | 123.039 | 66.9987 | -123.6265
97.2656 | 123.6923 | -67.0624 | 56.5155 | 0.06235 | -0.0013202 | 0.00053446 | 0.052391 | -0.00016792 | 0.053669 | 0.065477 | 0.00041927 | -0.001121 | 0.063805 | 0.0086938 | 0.063094 | -67.054 | 0.010564 | -66.9154 | 56.4258 | 56.0006 | 56.2115 | -66.8925 | -67.0038 | 0.018674 | -67.1207 | 56.0108 | 56.4633 | 55.9812 | -67.1568 | 0.16992 | -0.089686 | 0.008357 | 0.14698 | -0.02294 | -0.5149 | -0.30397 | -0.094445 | -0.50468 | 0.058586 | -0.058336 | 0.036109 | -0.052206 | -0.53434 | 123.4882 | 123.063 | 123.2739 | 67.0729 | -123.408 | 123.0732 | 123.5257 | 123.0435 | 67.0811 | -123.6723
98.2656 | 123.8068 | -67.0395 | 56.4606 | 0.047088 | -0.00025117 | -0.0016025 | 0.053459 | -0.00016792 | 0.050464 | 0.080738 | -0.0017177 | -0.001121 | 0.063805 | 0.0076248 | 0.062025 | -67.054 | 0.015142 | -66.9246 | 56.4121 | 56.0418 | 56.1886 | -66.9108 | -66.9992 | 0.014095 | -67.1253 | 56.0795 | 56.4587 | 56.0727 | -67.1477 | 0.12871 | -0.048489 | -0.014531 | 0.11493 | -0.013781 | -0.41876 | -0.27193 | -0.10818 | -0.38107 | 0.040276 | -0.085803 | 0.022373 | -0.001853 | -0.38783 | 123.4516 | 123.0813 | 123.2281 | 67.0546 | -123.3713 | 123.119 | 123.4982 | 123.1122 | 67.0536 | -123.6082
99.2812 | 123.8068 | -67.0258 | 56.4606 | 0.047088 | -0.0013202 | 0.0016025 | 0.055596 | -0.0012359 | 0.053669 | 0.080738 | 0.00041927 | -0.001121 | 0.063805 | 0.0086938 | 0.059889 | -67.054 | 0.019721 | -66.9246 | 56.4212 | 56.0372 | 56.1978 | -66.8925 | -67.0038 | 0.009516 | -67.1253 | 56.0612 | 56.4633 | 55.9812 | -67.1431 | 0.1333 | -0.039332 | -0.028264 | 0.1012 | -0.032097 | -0.42333 | -0.26277 | -0.11733 | -0.39938 | 0.021965 | -0.099536 | 0.017794 | 0.002726 | -0.4794 | 123.447 | 123.063 | 123.2236 | 67.0455 | -123.353 | 123.0869 | 123.4891 | 123.0069 | 67.0353 | -123.6037
100.2812 | 123.8113 | -67.0166 | 56.4606 | 0.047088 | -0.0034562 | -0.00053454 | 0.053459 | -0.0012359 | 0.0526 | 0.050216 | -0.00064973 | -0.001121 | 0.063805 | 0.010831 | 0.059889 | -67.054 | 0.001407 | -66.9154 | 56.4075 | 56.0327 | 56.2024 | -66.9199 | -67.0038 | 0.004938 | -67.1207 | 56.0291 | 56.4541 | 55.972 | -67.1477 | 0.096667 | -0.053067 | -0.037419 | 0.1012 | 0.004534 | -0.42791 | -0.2582 | -0.13106 | -0.43143 | 0.01281 | -0.10411 | 0.026952 | -0.006431 | -0.48856 | 123.4241 | 123.0493 | 123.219 | 67.018 | -123.3805 | 123.0457 | 123.4707 | 122.9886 | 67.0215 | -123.6082
101.2812 | 123.7839 | -67.0029 | 56.4651 | 0.031826 | 0.00081683 | -0.0016025 | 0.056664 | -0.0012359 | 0.053669 | 0.050216 | -0.00064973 | -0.001121 | 0.062737 | 0.0065568 | 0.062025 | -67.0494 | 0.015142 | -66.9291 | 56.4121 | 55.9823 | 56.2619 | -66.8787 | -67.0038 | 0.018674 | -67.1253 | 56.0795 | 56.4633 | 55.9903 | -67.1431 | 0.12414 | -0.053067 | -0.046574 | 0.073733 | -0.050412 | -0.48286 | -0.20325 | -0.14022 | -0.38564 | -0.000923 | -0.12242 | 0.017794 | -0.001852 | -0.47482 | 123.415 | 122.9852 | 123.2648 | 67.018 | -123.3439 | 123.0824 | 123.4662 | 122.9932 | 67.0215 | -123.6082
102.2656 | 123.6786 | -67.067 | 56.5247 | 0.047088 | -0.0013202 | -0.0016025 | 0.053459 | -0.00016792 | 0.0526 | 0.050216 | 0.0014873 | -0.002189 | 0.063805 | 0.0086938 | 0.062025 | -67.0494 | 0.015142 | -66.9291 | 56.4258 | 56.0327 | 56.239 | -66.9611 | -67.0084 | 0.014095 | -67.1207 | 56.0887 | 56.4633 | 55.9766 | -67.1385 | 0.10581 | -0.098841 | 0.017513 | 0.13782 | 0.032009 | -0.492 | -0.28565 | -0.071552 | -0.436 | 0.058585 | -0.053758 | 0.017794 | -0.061361 | -0.54807 | 123.4928 | 123.0996 | 123.306 | 67.0821 | -123.4858 | 123.1556 | 123.5303 | 123.0435 | 67.0811 | -123.6632
103.2656 | 123.6969 | -67.0853 | 56.5338 | 0.06235 | -0.0023882 | 0.00053446 | 0.055596 | -0.00016792 | 0.055805 | 0.065477 | -0.0017177 | -0.001121 | 0.062737 | 0.0097618 | 0.062025 | -67.0494 | 0.019721 | -66.9383 | 56.4533 | 56.1883 | 56.3031 | -67.1168 | -67.013 | 0.027831 | -67.1207 | 56.1757 | 56.4633 | 56.2788 | -67.1431 | -0.031562 | -0.080525 | 0.035823 | 0.14697 | 0.17853 | -0.34547 | -0.23071 | -0.057821 | -0.35816 | 0.072316 | -0.035448 | 0.022373 | -0.070516 | -0.25504 | 123.5386 | 123.2736 | 123.3884 | 67.105 | -123.6506 | 123.2609 | 123.5486 | 123.364 | 67.1131 | -123.6769
104.2812 | 123.7839 | -67.0074 | 56.4835 | 0.06235 | -0.0013202 | -0.0016025 | 0.055596 | -0.00016792 | 0.054737 | 0.080738 | -0.0017177 | -0.001121 | 0.062737 | 0.0097618 | 0.060957 | -67.0494 | 0.028878 | -66.9612 | 56.467 | 56.2021 | 56.3168 | -67.1306 | -67.0313 | 0.027831 | -67.1161 | 56.2031 | 56.4541 | 56.3612 | -67.1431 | -0.12312 | -0.016436 | -0.041997 | 0.046262 | 0.16938 | -0.28138 | -0.16662 | -0.13564 | -0.28034 | -0.023819 | -0.10869 | 0.026951 | -0.029319 | -0.12227 | 123.4745 | 123.2095 | 123.3243 | 67.0363 | -123.614 | 123.2106 | 123.4616 | 123.3686 | 67.0353 | -123.6265
105.2656 | 123.8113 | -67.0303 | 56.4285 | 0.047088 | -0.0013202 | 0.00053446 | 0.054527 | -0.0012359 | 0.055805 | 0.065477 | -0.0027857 | -0.001121 | 0.063805 | 0.011899 | 0.059889 | -67.0494 | 0.028878 | -66.9703 | 56.4716 | 56.2021 | 56.326 | -67.1351 | -67.0404 | 0.027831 | -67.1207 | 56.3313 | 56.4725 | 56.3978 | -67.1522 | -0.10481 | 0.043073 | -0.019109 | 0.059993 | 0.1648 | -0.22645 | -0.10253 | -0.12191 | -0.097207 | -0.010088 | -0.09038 | 0.03153 | 0.043926 | -0.030709 | 123.5019 | 123.2324 | 123.3563 | 67.0592 | -123.5637 | 123.3617 | 123.5028 | 123.4282 | 67.0582 | -123.5808
106.2812 | 123.793 | -67.0166 | 56.5338 | 0.06235 | -0.0023882 | 0.00053446 | 0.056664 | -0.0012359 | 0.056874 | 0.080738 | -0.0017177 | -0.002189 | 0.062737 | 0.010831 | 0.059889 | -67.054 | 0.0243 | -66.9703 | 56.4945 | 56.2158 | 56.3306 | -67.1489 | -67.0496 | 0.018674 | -67.1161 | 56.3405 | 56.4633 | 56.407 | -67.1477 | -0.13228 | -0.03932 | -0.037419 | 0.046261 | 0.17854 | -0.318 | -0.20324 | -0.13106 | -0.19334 | -0.032977 | -0.099534 | 0.03153 | -0.070516 | -0.12684 | 123.5111 | 123.2324 | 123.3472 | 67.0409 | -123.6827 | 123.3571 | 123.4799 | 123.4236 | 67.0353 | -123.6815
107.2656 | 123.6877 | -67.0303 | 56.5384 | 0.092874 | -0.0055932 | 0.0016025 | 0.055596 | -0.0023039 | 0.056874 | 0.080738 | -0.0017177 | -0.002189 | 0.0606 | 0.0097618 | 0.060957 | -67.0494 | 0.033457 | -66.9841 | 56.4945 | 56.2296 | 56.3397 | -67.1489 | -67.045 | 0.023253 | -67.1207 | 56.3451 | 56.4633 | 56.3978 | -67.1477 | -0.11855 | -0.043898 | -0.019109 | 0.046259 | 0.16481 | -0.30884 | -0.19866 | -0.11733 | -0.19333 | -0.014667 | -0.09038 | 0.026952 | -0.075094 | -0.14057 | 123.5248 | 123.2599 | 123.3701 | 67.0638 | -123.6873 | 123.3754 | 123.4936 | 123.4282 | 67.0536 | -123.6861
108.2812 | 123.8113 | -67.0349 | 56.4697 | 0.047088 | -0.0045252 | 0.00053446 | 0.054527 | -0.0055089 | 0.05901 | 0.11126 | -0.0038537 | -0.003257 | 0.061668 | 0.0097618 | 0.060957 | -67.0449 | 0.0243 | -66.9887 | 56.4945 | 56.1883 | 56.3031 | -67.0665 | -67.0633 | 0.018674 | -67.1161 | 56.3496 | 56.4633 | 56.3108 | -67.1477 | -0.031548 | 0.024766 | -0.009952 | 0.046258 | 0.077806 | -0.28139 | -0.16662 | -0.11275 | -0.12009 | -0.028404 | -0.081224 | 0.03153 | -0.00643 | -0.1589 | 123.5294 | 123.2233 | 123.338 | 67.0592 | -123.5362 | 123.3845 | 123.4982 | 123.3457 | 67.0536 | -123.6174
109.2812 | 123.8251 | -67.0395 | 56.488 | 0.047088 | -0.0023882 | -0.00053454 | 0.055596 | -0.0055089 | 0.055805 | 0.065477 | -0.0017177 | -0.002189 | 0.064873 | 0.010831 | 0.062025 | -67.0494 | 0.005985 | -66.9337 | 56.435 | 56.1975 | 56.2802 | -67.0527 | -67.0221 | 0.014095 | -67.1253 | 56.1802 | 56.4633 | 56.2971 | -67.1477 | -0.013233 | -0.053063 | -0.009953 | 0.10578 | 0.11901 | -0.29054 | -0.20783 | -0.10818 | -0.30781 | 0.017383 | -0.085803 | 0.022373 | -0.02474 | -0.19095 | 123.4745 | 123.237 | 123.3197 | 67.0455 | -123.5408 | 123.2197 | 123.5028 | 123.3366 | 67.0536 | -123.6357
110.2969 | 123.8068 | -67.012 | 56.4835 | 0.031826 | -0.00025117 | 0.00053446 | 0.054527 | -0.0033719 | 0.0526 | 0.065477 | 0.00041927 | -0.001121 | 0.062737 | 0.011899 | 0.060957 | -67.0494 | 0.019721 | -66.9291 | 56.4304 | 56.1883 | 56.2802 | -67.0527 | -67.0084 | 0.009516 | -67.1161 | 56.1757 | 56.4633 | 56.3108 | -67.1568 | -0.040699 | -0.053063 | -0.037419 | 0.082888 | 0.12359 | -0.29512 | -0.20325 | -0.1448 | -0.30781 | 0.003653 | -0.10411 | 0.040687 | -0.020162 | -0.17263 | 123.4424 | 123.2004 | 123.2922 | 67.0317 | -123.5362 | 123.1877 | 123.4753 | 123.3228 | 67.0215 | -123.6403
111.2812 | 123.793 | -67.0532 | 56.4972 | 0.047088 | -0.00025117 | -0.00053454 | 0.053459 | -0.0033719 | 0.051532 | 0.065477 | -0.0017177 | -5.2e-05 | 0.062737 | 0.010831 | 0.059889 | -67.0494 | 0.019721 | -66.92 | 56.4167 | 56.1929 | 56.2756 | -67.0481 | -67.013 | 0.004938 | -67.1207 | 56.194 | 56.4587 | 56.3154 | -67.1477 | 0.005079 | -0.080531 | 0.00378 | 0.13324 | 0.12816 | -0.30427 | -0.22156 | -0.094443 | -0.30322 | 0.040273 | -0.067491 | 0.026952 | -0.038474 | -0.18179 | 123.4699 | 123.2461 | 123.3289 | 67.0729 | -123.5453 | 123.2472 | 123.5119 | 123.3686 | 67.0582 | -123.6449
112.2656 | 123.8022 | -67.0303 | 56.4926 | 0.077612 | -0.0013202 | -0.00053454 | 0.053459 | -0.0012359 | 0.051532 | 0.080738 | -0.00064973 | -5.2e-05 | 0.062737 | 0.011899 | 0.062025 | -67.0494 | 0.010564 | -66.9246 | 56.4212 | 56.1929 | 56.2711 | -67.0527 | -67.0084 | 0.009516 | -67.1161 | 56.1848 | 56.4587 | 56.3108 | -67.1477 | -0.022389 | -0.071376 | -0.019109 | 0.10578 | 0.12816 | -0.29969 | -0.22156 | -0.11733 | -0.30781 | 0.021963 | -0.085802 | 0.03153 | -0.033897 | -0.18179 | 123.4516 | 123.2233 | 123.3014 | 67.0409 | -123.5453 | 123.2151 | 123.4891 | 123.3412 | 67.0399 | -123.6403
113.2656 | 123.7976 | -66.9937 | 56.4926 | 0.047088 | -0.0013202 | -0.00053454 | 0.055596 | -0.0023039 | 0.053669 | 0.080738 | -0.00064973 | -0.002189 | 0.062737 | 0.0097618 | 0.060957 | -67.054 | 0.005985 | -66.9291 | 56.4212 | 56.1929 | 56.2756 | -67.0573 | -67.0038 | 0.014095 | -67.1161 | 56.1894 | 56.4633 | 56.3337 | -67.1522 | -0.063589 | -0.071376 | -0.060308 | 0.064577 | 0.12817 | -0.29969 | -0.21698 | -0.15853 | -0.30323 | -0.010079 | -0.12242 | 0.036108 | -0.029318 | -0.1589 | 123.415 | 123.1866 | 123.2693 | 66.9997 | -123.5499 | 123.1831 | 123.457 | 123.3274 | 67.0078 | -123.6449
114.2812 | 123.7747 | -67.0395 | 56.4743 | 0.047088 | -0.0013202 | 0.00053446 | 0.054527 | -0.0023039 | 0.053669 | 0.065477 | 0.00041927 | -0.002189 | 0.0606 | 0.011899 | 0.059889 | -67.0449 | 0.015142 | -66.9246 | 56.4212 | 56.2021 | 56.2756 | -67.0527 | -67.0084 | 0.004938 | -67.1207 | 56.194 | 56.4633 | 56.2925 | -67.1522 | -0.013233 | -0.053065 | -0.005374 | 0.11493 | 0.12816 | -0.27222 | -0.19867 | -0.11275 | -0.28034 | 0.031119 | -0.081224 | 0.03153 | -0.011007 | -0.18179 | 123.4607 | 123.2416 | 123.3151 | 67.0546 | -123.527 | 123.2335 | 123.5028 | 123.332 | 67.0444 | -123.6265
115.2812 | 123.8159 | -66.9891 | 56.4972 | 0.06235 | -0.00025117 | 0.00053446 | 0.054527 | -0.0012359 | 0.0526 | 0.050216 | 0.0014873 | -0.002189 | 0.062737 | 0.010831 | 0.059889 | -67.0449 | 0.005985 | -66.9337 | 56.4258 | 56.2067 | 56.2802 | -67.0619 | -67.0084 | 0.009516 | -67.1253 | 56.194 | 56.4633 | 56.32 | -67.1431 | -0.072745 | -0.071375 | -0.055728 | 0.055422 | 0.12817 | -0.29053 | -0.21698 | -0.15395 | -0.30322 | -0.019235 | -0.13616 | 0.017794 | -0.033895 | -0.17721 | 123.415 | 123.1958 | 123.2693 | 66.9951 | -123.5591 | 123.1831 | 123.4524 | 123.3091 | 66.9987 | -123.6403
116.2812 | 123.793 | -67.0074 | 56.5247 | 0.06235 | -0.0034562 | 0.0016025 | 0.054527 | -0.0012359 | 0.050464 | 0.065477 | 0.00041927 | -0.001121 | 0.062737 | 0.011899 | 0.059889 | -67.054 | 0.010564 | -66.9291 | 56.4212 | 56.1929 | 56.2802 | -67.0573 | -67.0084 | 0.018674 | -67.1161 | 56.2077 | 56.4633 | 56.2605 | -67.1477 | -0.049856 | -0.10342 | -0.046575 | 0.07831 | 0.12817 | -0.33174 | -0.24445 | -0.14022 | -0.31696 | -0.000925 | -0.10869 | 0.03153 | -0.061361 | -0.2642 | 123.4287 | 123.2004 | 123.2877 | 67.018 | -123.582 | 123.2151 | 123.4707 | 123.2679 | 67.0261 | -123.6723
117.2656 | 123.6694 | -67.0578 | 56.5109 | 0.047088 | -0.0023882 | 0.00053446 | 0.053459 | -0.0033719 | 0.0526 | 0.080738 | -0.0017177 | -0.003257 | 0.061668 | 0.0097618 | 0.060957 | -67.0449 | 0.019721 | -66.9291 | 56.4304 | 56.1975 | 56.2756 | -67.0527 | -67.0038 | 0.009516 | -67.1161 | 56.1894 | 56.4587 | 56.2879 | -67.1431 | 0.005077 | -0.080529 | 0.012936 | 0.12866 | 0.12359 | -0.31343 | -0.23529 | -0.085287 | -0.32154 | 0.054008 | -0.058336 | 0.026951 | -0.052207 | -0.22299 | 123.4882 | 123.2553 | 123.3334 | 67.0775 | -123.5636 | 123.2472 | 123.5165 | 123.3457 | 67.0673 | -123.654
118.2656 | 123.674 | -67.0853 | 56.5109 | 0.077612 | -0.0023882 | -0.0016025 | 0.054527 | -0.0044409 | 0.0526 | 0.080738 | -0.0017177 | -0.002189 | 0.062737 | 0.010831 | 0.060957 | -67.0449 | 0.005985 | -66.9291 | 56.4212 | 56.2067 | 56.2802 | -67.0619 | -67.0084 | 0.018674 | -67.1207 | 56.2123 | 56.4679 | 56.3108 | -67.1431 | 0.023385 | -0.089686 | 0.040402 | 0.15613 | 0.13274 | -0.30427 | -0.23071 | -0.057821 | -0.29864 | 0.076895 | -0.035448 | 0.022373 | -0.043049 | -0.2001 | 123.5065 | 123.2919 | 123.3655 | 67.0913 | -123.5728 | 123.2975 | 123.5531 | 123.3961 | 67.1039 | -123.654
119.2812 | 123.7976 | -67.0395 | 56.456 | 0.047088 | -0.0013202 | -0.00053454 | 0.054527 | -0.00016792 | 0.051532 | 0.065477 | -0.00064973 | -0.002189 | 0.061668 | 0.010831 | 0.059889 | -67.0449 | 0.010564 | -66.92 | 56.4212 | 56.2112 | 56.2756 | -67.0527 | -67.0084 | 0.009516 | -67.1207 | 56.2077 | 56.4633 | 56.2559 | -67.1522 | -0.013233 | -0.034755 | -0.005374 | 0.11951 | 0.13274 | -0.24476 | -0.18036 | -0.11275 | -0.24829 | 0.031119 | -0.081224 | 0.03153 | 0.007303 | -0.20011 | 123.4607 | 123.2507 | 123.3151 | 67.0501 | -123.5087 | 123.2472 | 123.5028 | 123.2954 | 67.049 | -123.6082
120.2812 | 123.7427 | -67.0303 | 56.5109 | 0.06235 | -0.0013202 | 0.00053446 | 0.055596 | -0.0012359 | 0.053669 | 0.065477 | -0.0017177 | -0.002189 | 0.062737 | 0.012967 | 0.05882 | -67.0494 | 0.005985 | -66.9291 | 56.4258 | 56.2204 | 56.2802 | -67.0527 | -67.0038 | 0.014095 | -67.1161 | 56.2123 | 56.4633 | 56.2879 | -67.1522 | -0.022389 | -0.085108 | -0.019109 | 0.1012 | 0.12359 | -0.29053 | -0.23071 | -0.12191 | -0.29864 | 0.026542 | -0.085802 | 0.036108 | -0.047628 | -0.22299 | 123.4562 | 123.2507 | 123.3105 | 67.0363 | -123.5636 | 123.2426 | 123.4936 | 123.3183 | 67.0444 | -123.6632
121.2812 | 123.8205 | -66.9937 | 56.5201 | 0.077612 | -0.0023882 | 0.00053446 | 0.054527 | -0.0012359 | 0.051532 | 0.050216 | -0.0017177 | -0.002189 | 0.061668 | 0.011899 | 0.059889 | -67.054 | 0.005985 | -66.9291 | 56.4212 | 56.2158 | 56.2711 | -67.0619 | -67.0084 | 0.009516 | -67.1207 | 56.2077 | 56.4633 | 56.2696 | -67.1522 | -0.068168 | -0.098842 | -0.060308 | 0.064577 | 0.13274 | -0.30427 | -0.24903 | -0.15853 | -0.31238 | -0.014658 | -0.127 | 0.03153 | -0.056784 | -0.25046 | 123.415 | 123.2095 | 123.2648 | 66.9997 | -123.582 | 123.2014 | 123.457 | 123.2633 | 67.0032 | -123.6723
122.2812 | 123.7473 | -67.0258 | 56.4789 | 0.047088 | -0.0013202 | 0.00053446 | 0.055596 | -0.0023039 | 0.051532 | 0.065477 | -0.00064973 | -5.2e-05 | 0.061668 | 0.012967 | 0.059889 | -67.0494 | 0.010564 | -66.9337 | 56.4167 | 56.2204 | 56.2802 | -67.0619 | -67.0084 | 0.004938 | -67.1253 | 56.1848 | 56.4587 | 56.2238 | -67.1522 | -0.036124 | -0.062221 | -0.023686 | 0.092043 | 0.12817 | -0.25849 | -0.19867 | -0.12649 | -0.29407 | 0.017386 | -0.099536 | 0.026951 | -0.020164 | -0.25505 | 123.4424 | 123.2462 | 123.306 | 67.0363 | -123.5408 | 123.2106 | 123.4845 | 123.2496 | 67.0307 | -123.6311
123.2656 | 123.6877 | -67.067 | 56.5109 | 0.077612 | -0.0023882 | 0.00053446 | 0.054527 | -0.0012359 | 0.053669 | 0.080738 | -0.00064973 | -0.002189 | 0.063805 | 0.011899 | 0.062025 | -67.0449 | 0.015142 | -66.9337 | 56.4304 | 56.2158 | 56.2848 | -67.0527 | -67.0038 | 0.009516 | -67.1161 | 56.2169 | 56.4633 | 56.2376 | -67.1385 | 0.014233 | -0.080529 | 0.022092 | 0.13324 | 0.11901 | -0.29511 | -0.22613 | -0.071552 | -0.29407 | 0.063164 | -0.04918 | 0.022372 | -0.047628 | -0.27336 | 123.4974 | 123.2828 | 123.3517 | 67.0821 | -123.5636 | 123.2838 | 123.5303 | 123.3045 | 67.0765 | -123.6494
124.2812 | 123.7747 | -67.0303 | 56.488 | 0.031826 | -0.00025117 | 0.0016025 | 0.054527 | -0.00016792 | 0.053669 | 0.065477 | -0.00064973 | -0.001121 | 0.061668 | 0.011899 | 0.05882 | -67.054 | 0.005985 | -66.9291 | 56.4212 | 56.2158 | 56.2848 | -67.0573 | -67.0038 | 0.014095 | -67.1161 | 56.2214 | 56.4633 | 56.2559 | -67.1477 | -0.026968 | -0.066798 | -0.023687 | 0.1012 | 0.12817 | -0.27222 | -0.20325 | -0.11733 | -0.2666 | 0.026542 | -0.085802 | 0.03153 | -0.02474 | -0.23215 | 123.4516 | 123.2462 | 123.3151 | 67.0363 | -123.5453 | 123.2518 | 123.4936 | 123.2862 | 67.0444 | -123.6357
125.2812 | 123.8205 | -66.9754 | 56.5063 | 0.047088 | -0.0013202 | -0.0016025 | 0.054527 | -0.0023039 | 0.0526 | 0.065477 | -0.0017177 | -0.001121 | 0.061668 | 0.012967 | 0.060957 | -67.0494 | 0.010564 | -66.9291 | 56.4167 | 56.2158 | 56.2756 | -67.0527 | -67.0084 | 0.004938 | -67.1161 | 56.1894 | 56.4587 | 56.3062 | -67.1477 | -0.07732 | -0.089687 | -0.07404 | 0.046267 | 0.12359 | -0.29053 | -0.23072 | -0.17226 | -0.31696 | -0.032968 | -0.14073 | 0.03153 | -0.04763 | -0.2001 | 123.3921 | 123.1912 | 123.251 | 66.986 | -123.5591 | 123.1648 | 123.4341 | 123.2816 | 66.9803 | -123.654
126.2812 | 123.7427 | -67.0212 | 56.488 | 0.047088 | -0.0013202 | -0.0016025 | 0.055596 | -0.00016792 | 0.0526 | 0.050216 | -0.00064973 | -5.2e-05 | 0.063805 | 0.015104 | 0.060957 | -67.0494 | 0.019721 | -66.9337 | 56.4258 | 56.2204 | 56.2848 | -67.0527 | -67.0038 | 0.014095 | -67.1207 | 56.2214 | 56.4587 | 56.233 | -67.1477 | -0.031544 | -0.06222 | -0.028264 | 0.087465 | 0.11901 | -0.26764 | -0.20325 | -0.12649 | -0.2666 | 0.017387 | -0.099535 | 0.026952 | -0.029319 | -0.25505 | 123.447 | 123.2416 | 123.306 | 67.0409 | -123.5408 | 123.2426 | 123.4799 | 123.2542 | 67.0353 | -123.6357
127.2656 | 123.6877 | -67.0715 | 56.5063 | 0.06235 | 0.0018858 | -0.00053454 | 0.053459 | -0.0023039 | 0.0526 | 0.065477 | -0.00064973 | 0.001016 | 0.061668 | 0.011899 | 0.05882 | -67.054 | 0.015142 | -66.9291 | 56.4304 | 56.2204 | 56.2848 | -67.0527 | -67.0084 | 0.009516 | -67.1161 | 56.226 | 56.4633 | 56.2605 | -67.1522 | 0.01881 | -0.075952 | 0.017512 | 0.1424 | 0.12359 | -0.28595 | -0.22156 | -0.080711 | -0.28033 | 0.063162 | -0.044603 | 0.036108 | -0.043051 | -0.24589 | 123.5019 | 123.2919 | 123.3563 | 67.0867 | -123.5591 | 123.2975 | 123.5348 | 123.332 | 67.081 | -123.6586
128.2656 | 123.6969 | -67.0944 | 56.5018 | 0.047088 | -0.0013202 | 0.00053446 | 0.053459 | -0.0023039 | 0.051532 | 0.065477 | -0.0017177 | -0.001121 | 0.059532 | 0.014036 | 0.05882 | -67.0494 | 0.015142 | -66.9337 | 56.4258 | 56.2204 | 56.2848 | -67.0527 | -67.0038 | 0.014095 | -67.1161 | 56.2306 | 56.4633 | 56.2696 | -67.1477 | 0.041698 | -0.075953 | 0.044978 | 0.16071 | 0.11901 | -0.28137 | -0.21698 | -0.053245 | -0.27117 | 0.090629 | -0.021715 | 0.03153 | -0.038473 | -0.23215 | 123.5202 | 123.3148 | 123.3792 | 67.1096 | -123.5545 | 123.325 | 123.5577 | 123.364 | 67.1085 | -123.6494
129.2812 | 123.7701 | -67.0074 | 56.4743 | 0.047088 | -0.0013202 | -0.0016025 | 0.053459 | -0.0012359 | 0.051532 | 0.050216 | -0.0038537 | -5.2e-05 | 0.061668 | 0.012967 | 0.059889 | -67.0357 | 0.015142 | -66.9337 | 56.4304 | 56.2204 | 56.2756 | -67.0619 | -67.0084 | 0.009516 | -67.1207 | 56.2214 | 56.4679 | 56.2696 | -67.1568 | -0.054435 | -0.043908 | -0.028262 | 0.073732 | 0.12817 | -0.25391 | -0.19867 | -0.14938 | -0.25287 | -0.000925 | -0.11327 | 0.036109 | -0.006428 | -0.20469 | 123.4378 | 123.2278 | 123.2831 | 67.0226 | -123.5362 | 123.2289 | 123.4753 | 123.2771 | 67.017 | -123.6311
130.2656 | 123.8159 | -66.9983 | 56.4926 | 0.06235 | -0.00025117 | -0.00053454 | 0.054527 | -0.0023039 | 0.051532 | 0.065477 | -0.00064973 | -0.002189 | 0.061668 | 0.015104 | 0.059889 | -67.054 | 0.010564 | -66.9291 | 56.4304 | 56.2204 | 56.2848 | -67.0573 | -66.9992 | 0.014095 | -67.1161 | 56.2306 | 56.4633 | 56.2788 | -67.1477 | -0.059011 | -0.062219 | -0.05573 | 0.069155 | 0.12817 | -0.27222 | -0.20782 | -0.14938 | -0.26202 | -0.000923 | -0.11785 | 0.03153 | -0.029318 | -0.21384 | 123.4287 | 123.2187 | 123.2831 | 67.0089 | -123.5499 | 123.2289 | 123.4616 | 123.2771 | 67.0124 | -123.6403
131.2812 | 123.7976 | -67.0212 | 56.4743 | 0.031826 | 0.00081683 | -0.0016025 | 0.054527 | -0.0012359 | 0.0526 | 0.065477 | 0.00041927 | -5.2e-05 | 0.062737 | 0.015104 | 0.059889 | -67.0449 | 0.015142 | -66.9291 | 56.4304 | 56.225 | 56.2848 | -67.0573 | -67.0038 | 0.014095 | -67.1161 | 56.2306 | 56.4725 | 56.2238 | -67.1477 | -0.036123 | -0.043908 | -0.023685 | 0.092043 | 0.12817 | -0.24933 | -0.18951 | -0.12649 | -0.24371 | 0.017387 | -0.094957 | 0.03153 | -0.00185 | -0.25047 | 123.4516 | 123.2462 | 123.306 | 67.0363 | -123.5316 | 123.2518 | 123.4936 | 123.245 | 67.0353 | -123.622
132.2656 | 123.8022 | -67.0074 | 56.4835 | 0.047088 | -0.0013202 | 0.00053446 | 0.052391 | -0.00016792 | 0.0526 | 0.050216 | -0.0017177 | -0.002189 | 0.061668 | 0.015104 | 0.059889 | -67.0449 | 0.010564 | -66.9337 | 56.4258 | 56.2296 | 56.2894 | -67.0481 | -67.0038 | 0.014095 | -67.1161 | 56.226 | 56.4633 | 56.265 | -67.1477 | -0.040698 | -0.057642 | -0.037418 | 0.073732 | 0.11443 | -0.25391 | -0.19409 | -0.14022 | -0.25744 | 0.003654 | -0.10869 | 0.03153 | -0.020162 | -0.21842 | 123.4333 | 123.237 | 123.2968 | 67.018 | -123.5316 | 123.2335 | 123.4707 | 123.2725 | 67.0215 | -123.6311
133.2656 | 123.6786 | -67.0624 | 56.5155 | 0.06235 | -0.0023882 | -0.0016025 | 0.053459 | -0.0023039 | 0.053669 | 0.065477 | -0.00064973 | -0.001121 | 0.061668 | 0.015104 | 0.059889 | -67.0403 | 0.019721 | -66.9291 | 56.4258 | 56.2296 | 56.2848 | -67.0481 | -66.9992 | 0.000359 | -67.1161 | 56.2306 | 56.4587 | 56.2696 | -67.1522 | 0.014234 | -0.089686 | 0.022092 | 0.13324 | 0.11901 | -0.28595 | -0.23071 | -0.089866 | -0.28491 | 0.063164 | -0.053758 | 0.036108 | -0.056785 | -0.24589 | 123.4882 | 123.2919 | 123.3472 | 67.0821 | -123.5636 | 123.293 | 123.5211 | 123.332 | 67.0627 | -123.6677
134.2812 | 123.7793 | -67.0258 | 56.4743 | 0.077612 | -0.0013202 | -0.0016025 | 0.054527 | -0.0012359 | 0.053669 | 0.050216 | -0.0017177 | -0.002189 | 0.062737 | 0.015104 | 0.059889 | -67.0311 | 0.019721 | -66.9291 | 56.4212 | 56.225 | 56.2756 | -67.039 | -67.0038 | 0.009516 | -67.1161 | 56.2214 | 56.4679 | 56.2559 | -67.1522 | -0.01323 | -0.053065 | -0.005372 | 0.096621 | 0.10985 | -0.24933 | -0.19867 | -0.12649 | -0.25287 | 0.021965 | -0.090379 | 0.036108 | -0.006428 | -0.21842 | 123.447 | 123.2507 | 123.3014 | 67.0455 | -123.5133 | 123.2472 | 123.4936 | 123.2816 | 67.0353 | -123.6265
135.2656 | 123.7381 | -67.0349 | 56.4972 | 0.047088 | -0.00025117 | -0.00053454 | 0.053459 | -0.0023039 | 0.0526 | 0.065477 | -0.0017177 | -0.002189 | 0.062737 | 0.015104 | 0.060957 | -67.0449 | 0.015142 | -66.9383 | 56.4258 | 56.2112 | 56.2802 | -67.0619 | -67.0084 | 0.009516 | -67.1116 | 56.2214 | 56.4679 | 56.2879 | -67.1522 | -0.026969 | -0.071375 | -0.009952 | 0.096619 | 0.12359 | -0.28596 | -0.21698 | -0.11733 | -0.27575 | 0.026541 | -0.076645 | 0.040687 | -0.029316 | -0.20926 | 123.4607 | 123.2461 | 123.3151 | 67.0501 | -123.5591 | 123.2563 | 123.5028 | 123.3228 | 67.0444 | -123.6494
136.2812 | 123.793 | -67.0258 | 56.4926 | 0.047088 | -0.0013202 | -0.00053454 | 0.053459 | -0.0023039 | 0.053669 | 0.065477 | -0.00064973 | -0.002189 | 0.0606 | 0.014036 | 0.05882 | -67.054 | 0.010564 | -66.9291 | 56.4258 | 56.2112 | 56.2802 | -67.0527 | -67.0084 | 0.014095 | -67.1116 | 56.2123 | 56.4587 | 56.2376 | -67.1522 | -0.026966 | -0.066798 | -0.028264 | 0.096621 | 0.12359 | -0.28138 | -0.2124 | -0.12649 | -0.28033 | 0.017386 | -0.0858 | 0.040687 | -0.033897 | -0.25505 | 123.4516 | 123.237 | 123.306 | 67.0363 | -123.5453 | 123.238 | 123.4845 | 123.2633 | 67.0399 | -123.6449
137.2656 | 123.6786 | -67.0761 | 56.5155 | 0.047088 | -0.0023882 | 0.0016025 | 0.052391 | -0.0023039 | 0.0526 | 0.050216 | -0.0017177 | -0.002189 | 0.0606 | 0.015104 | 0.060957 | -67.0449 | 0.015142 | -66.9337 | 56.435 | 56.2112 | 56.2802 | -67.0619 | -67.0038 | 0.014095 | -67.1161 | 56.2214 | 56.4587 | 56.2559 | -67.1477 | 0.01423 | -0.080529 | 0.031247 | 0.1424 | 0.12817 | -0.30427 | -0.23529 | -0.071555 | -0.29407 | 0.072319 | -0.040025 | 0.03153 | -0.056785 | -0.25962 | 123.5111 | 123.2873 | 123.3563 | 67.0913 | -123.5774 | 123.2975 | 123.5348 | 123.332 | 67.0902 | -123.6632
138.2656 | 123.6786 | -67.0624 | 56.543 | 0.031826 | -0.0023882 | 0.0016025 | 0.053459 | -0.00016792 | 0.051532 | 0.080738 | -0.0017177 | -0.002189 | 0.058464 | 0.015104 | 0.059889 | -67.0494 | 0.010564 | -66.9246 | 56.4396 | 56.2296 | 56.2848 | -67.0527 | -67.0084 | 0.014095 | -67.1207 | 56.2077 | 56.4633 | 56.2788 | -67.1614 | 0.009655 | -0.10342 | 0.012935 | 0.13782 | 0.12816 | -0.31342 | -0.25818 | -0.099024 | -0.33527 | 0.054007 | -0.058336 | 0.040688 | -0.079672 | -0.26419 | 123.5019 | 123.2919 | 123.3472 | 67.0729 | -123.5957 | 123.2701 | 123.5257 | 123.3412 | 67.0765 | -123.7044
139.2812 | 123.793 | -67.0441 | 56.4651 | 0.06235 | -0.00025117 | -0.00053454 | 0.054527 | -0.0033719 | 0.050464 | 0.080738 | -0.00064973 | -0.001121 | 0.062737 | 0.016172 | 0.059889 | -67.0494 | 0.015142 | -66.9291 | 56.4167 | 56.2158 | 56.2802 | -67.0436 | -67.0084 | 0.009516 | -67.1207 | 56.2169 | 56.4633 | 56.2788 | -67.1477 | 0.000502 | -0.048488 | -0.005376 | 0.11493 | 0.11443 | -0.24933 | -0.18494 | -0.1036 | -0.24829 | 0.035696 | -0.076647 | 0.026952 | -0.001852 | -0.18637 | 123.4607 | 123.2599 | 123.3243 | 67.0592 | -123.5087 | 123.2609 | 123.5074 | 123.3228 | 67.0536 | -123.6128
140.2656 | 123.8068 | -67.0258 | 56.4743 | 0.06235 | -0.0013202 | -0.00053454 | 0.052391 | -0.0023039 | 0.0526 | 0.065477 | -0.00064973 | -0.002189 | 0.061668 | 0.016172 | 0.05882 | -67.0449 | 0.010564 | -66.9337 | 56.4212 | 56.2204 | 56.2756 | -67.0527 | -67.0084 | 0.014095 | -67.1207 | 56.2123 | 56.4633 | 56.32 | -67.1522 | -0.026966 | -0.053065 | -0.019107 | 0.092043 | 0.11901 | -0.25391 | -0.19867 | -0.12649 | -0.26202 | 0.017386 | -0.094957 | 0.03153 | -0.011007 | -0.15432 | 123.447 | 123.2462 | 123.3014 | 67.0363 | -123.527 | 123.238 | 123.4891 | 123.3457 | 67.0399 | -123.6265
141.2812 | 123.6603 | -67.0624 | 56.4926 | 0.047088 | -0.0013202 | -0.00053454 | 0.051322 | -0.0023039 | 0.049395 | 0.080738 | -0.0027857 | -0.002189 | 0.061668 | 0.016172 | 0.057752 | -67.0449 | 0.015142 | -66.9291 | 56.4212 | 56.2204 | 56.2802 | -67.0573 | -67.0038 | 0.004938 | -67.1207 | 56.2214 | 56.4633 | 56.265 | -67.1431 | 0.005076 | -0.071376 | 0.017514 | 0.13324 | 0.12817 | -0.27222 | -0.2124 | -0.080709 | -0.27118 | 0.058586 | -0.058336 | 0.022373 | -0.029318 | -0.22758 | 123.4836 | 123.2828 | 123.3426 | 67.0775 | -123.5499 | 123.2838 | 123.5257 | 123.3274 | 67.0673 | -123.6357
142.2656 | 123.7244 | -67.0395 | 56.5338 | 0.047088 | -0.0034562 | 0.00053446 | 0.052391 | -0.0033719 | 0.053669 | 0.050216 | -0.0017177 | -0.003257 | 0.0606 | 0.016172 | 0.05882 | -67.0449 | 0.019721 | -66.9383 | 56.4258 | 56.2112 | 56.2802 | -67.0665 | -67.0084 | 0.004938 | -67.1207 | 56.226 | 56.4587 | 56.2879 | -67.1477 | -0.02697 | -0.108 | -0.005374 | 0.1012 | 0.12817 | -0.32258 | -0.2536 | -0.10818 | -0.3078 | 0.031119 | -0.081224 | 0.026952 | -0.075095 | -0.24588 | 123.4653 | 123.2507 | 123.3197 | 67.0592 | -123.6003 | 123.2655 | 123.4982 | 123.3274 | 67.0444 | -123.6815
143.2656 | 123.7106 | -67.0532 | 56.5063 | 0.06235 | -0.0023882 | -0.0016025 | 0.052391 | -0.0023039 | 0.051532 | 0.065477 | -0.0017177 | -0.002189 | 0.062737 | 0.014036 | 0.057752 | -67.0494 | 0.015142 | -66.9383 | 56.435 | 56.2204 | 56.2939 | -67.0573 | -67.0084 | 0.014095 | -67.1161 | 56.2123 | 56.4633 | 56.233 | -67.1477 | -0.004079 | -0.071374 | 0.00378 | 0.11493 | 0.11901 | -0.28595 | -0.2124 | -0.094443 | -0.29407 | 0.044852 | -0.062913 | 0.03153 | -0.043051 | -0.27336 | 123.4882 | 123.2736 | 123.3472 | 67.0684 | -123.5637 | 123.2655 | 123.5165 | 123.2862 | 67.0673 | -123.654
144.2812 | 123.7885 | -67.0303 | 56.456 | 0.047088 | -0.0023882 | -0.0016025 | 0.051322 | -0.0044409 | 0.050464 | 0.065477 | -0.0038537 | -0.001121 | 0.061668 | 0.017241 | 0.059889 | -67.0449 | 0.010564 | -66.9337 | 56.4212 | 56.2204 | 56.2848 | -67.039 | -67.0038 | 0.014095 | -67.1161 | 56.2077 | 56.4679 | 56.2467 | -67.1522 | -0.008653 | -0.034755 | -0.01453 | 0.09662 | 0.10527 | -0.2356 | -0.1712 | -0.12191 | -0.24829 | 0.026542 | -0.085802 | 0.036108 | 0.011882 | -0.20927 | 123.4516 | 123.2507 | 123.3151 | 67.0409 | -123.495 | 123.238 | 123.4982 | 123.2771 | 67.0444 | -123.6082
145.2656 | 123.6786 | -67.0532 | 56.5201 | 0.016564 | -0.0023882 | -0.00053454 | 0.053459 | -0.0033719 | 0.0526 | 0.065477 | -0.0027857 | -0.003257 | 0.062737 | 0.017241 | 0.057752 | -67.0403 | 0.015142 | -66.9383 | 56.4212 | 56.2112 | 56.2848 | -67.0573 | -67.0084 | 0.014095 | -67.107 | 56.2123 | 56.4679 | 56.2559 | -67.1477 | -0.004079 | -0.098842 | 0.012937 | 0.11493 | 0.11901 | -0.30884 | -0.23529 | -0.094443 | -0.3078 | 0.044852 | -0.053755 | 0.040688 | -0.052205 | -0.2642 | 123.4745 | 123.2645 | 123.338 | 67.0684 | -123.5774 | 123.2655 | 123.5211 | 123.3091 | 67.0673 | -123.6677
146.2812 | 123.7381 | -67.0029 | 56.5018 | 0.047088 | -0.0034562 | -0.0016025 | 0.052391 | -0.0033719 | 0.0526 | 0.095999 | -0.0017177 | -0.003257 | 0.061668 | 0.016172 | 0.059889 | -67.0449 | 0.019721 | -66.9337 | 56.4212 | 56.2158 | 56.2802 | -67.0527 | -67.0084 | 0.014095 | -67.1116 | 56.2123 | 56.4633 | 56.265 | -67.1614 | -0.049854 | -0.080531 | -0.041995 | 0.069155 | 0.11901 | -0.28595 | -0.22156 | -0.15853 | -0.28949 | -0.005502 | -0.10869 | 0.049845 | -0.038473 | -0.23673 | 123.4241 | 123.2187 | 123.2831 | 67.0226 | -123.5545 | 123.2151 | 123.4662 | 123.2679 | 67.017 | -123.6632
147.2656 | 123.6923 | -67.0303 | 56.5247 | 0.031826 | -0.0034562 | -0.00053454 | 0.051322 | -0.0033719 | 0.051532 | 0.050216 | -0.0027857 | -0.002189 | 0.0606 | 0.016172 | 0.059889 | -67.0403 | 0.019721 | -66.9337 | 56.4304 | 56.2112 | 56.2894 | -67.0619 | -67.0038 | 0.014095 | -67.1116 | 56.2077 | 56.4587 | 56.32 | -67.1568 | -0.031547 | -0.094262 | -0.009952 | 0.09662 | 0.12817 | -0.31342 | -0.23529 | -0.12649 | -0.31696 | 0.026542 | -0.081223 | 0.045266 | -0.06594 | -0.20468 | 123.4607 | 123.2416 | 123.3197 | 67.0501 | -123.5865 | 123.238 | 123.4891 | 123.3503 | 67.0444 | -123.6815
148.2656 | 123.6649 | -67.0532 | 56.5155 | 0.016564 | -0.0034562 | 0.00053446 | 0.053459 | -0.0044409 | 0.0526 | 0.065477 | -0.0027857 | -0.003257 | 0.059532 | 0.016172 | 0.05882 | -67.0449 | 0.015142 | -66.9291 | 56.4258 | 56.2204 | 56.2848 | -67.0527 | -67.0038 | 0.014095 | -67.1116 | 56.2077 | 56.4633 | 56.2421 | -67.1568 | 0.0005 | -0.089686 | 0.008359 | 0.12409 | 0.12359 | -0.29511 | -0.23071 | -0.1036 | -0.3078 | 0.049431 | -0.058334 | 0.045266 | -0.052206 | -0.27336 | 123.479 | 123.2736 | 123.338 | 67.0684 | -123.5682 | 123.2609 | 123.5165 | 123.2954 | 67.0673 | -123.6723
149.2812 | 123.7473 | -67.0303 | 56.4789 | 0.047088 | -0.0045252 | -0.0016025 | 0.052391 | -0.0033719 | 0.051532 | 0.065477 | -0.00064973 | -0.002189 | 0.0606 | 0.017241 | 0.057752 | -67.0449 | 0.019721 | -66.9246 | 56.4258 | 56.2021 | 56.2848 | -67.0481 | -66.9946 | 0.009516 | -67.107 | 56.2031 | 56.4633 | 56.2605 | -67.1522 | -0.01781 | -0.053065 | -0.01453 | 0.10578 | 0.12359 | -0.2768 | -0.19409 | -0.12191 | -0.27576 | 0.035699 | -0.076644 | 0.045266 | -0.015585 | -0.21842 | 123.4562 | 123.2324 | 123.3151 | 67.0501 | -123.527 | 123.2335 | 123.4936 | 123.2908 | 67.0399 | -123.6311
150.2656 | 123.7198 | -67.0395 | 56.5109 | 0.047088 | -0.0034562 | 0.00053446 | 0.053459 | -0.0044409 | 0.051532 | 0.065477 | -0.0017177 | -0.003257 | 0.061668 | 0.019377 | 0.05882 | -67.0403 | 0.010564 | -66.9337 | 56.4212 | 56.2021 | 56.2894 | -67.0527 | -66.9992 | 0.014095 | -67.1116 | 56.2123 | 56.4633 | 56.2513 | -67.1477 | -0.013233 | -0.089686 | -0.000796 | 0.10578 | 0.11901 | -0.30885 | -0.22156 | -0.10818 | -0.29864 | 0.040276 | -0.072067 | 0.036109 | -0.047628 | -0.25962 | 123.4607 | 123.2416 | 123.3289 | 67.0501 | -123.5636 | 123.2518 | 123.5028 | 123.2908 | 67.0536 | -123.6586
151.2656 | 123.6969 | -67.0303 | 56.5109 | 0.047088 | -0.0045252 | 0.00053446 | 0.053459 | -0.0044409 | 0.051532 | 0.080738 | -0.0027857 | -0.003257 | 0.061668 | 0.017241 | 0.057752 | -67.0449 | 0.015142 | -66.9246 | 56.435 | 56.2112 | 56.2939 | -67.071 | -67.0084 | 0.014095 | -67.1116 | 56.2123 | 56.4587 | 56.2925 | -67.1568 | -0.040705 | -0.075951 | -0.01453 | 0.10578 | 0.14648 | -0.29969 | -0.21698 | -0.12649 | -0.29864 | 0.021963 | -0.081223 | 0.045266 | -0.052207 | -0.21841 | 123.4653 | 123.2416 | 123.3243 | 67.0455 | -123.582 | 123.2426 | 123.4891 | 123.3228 | 67.0444 | -123.6677
152.2656 | 123.6694 | -67.067 | 56.5018 | 0.06235 | -0.0023882 | -0.0016025 | 0.053459 | -0.0033719 | 0.051532 | 0.050216 | -0.0017177 | -0.003257 | 0.059532 | 0.018309 | 0.057752 | -67.0449 | 0.015142 | -66.9383 | 56.4258 | 56.2067 | 56.2848 | -67.0527 | -66.9992 | 0.014095 | -67.1116 | 56.2077 | 56.4633 | 56.3017 | -67.1568 | 0.014233 | -0.075953 | 0.022092 | 0.12866 | 0.11443 | -0.29511 | -0.21698 | -0.089867 | -0.29407 | 0.067742 | -0.044601 | 0.045266 | -0.038473 | -0.2001 | 123.4928 | 123.2736 | 123.3517 | 67.0821 | -123.5545 | 123.2747 | 123.5303 | 123.3686 | 67.0811 | -123.6586
153.2656 | 123.6877 | -67.0349 | 56.5201 | 0.077612 | -0.0013202 | -0.00053454 | 0.053459 | -0.0044409 | 0.051532 | 0.065477 | -0.00064973 | -0.003257 | 0.059532 | 0.017241 | 0.05882 | -67.0357 | 0.015142 | -66.9291 | 56.4258 | 56.1975 | 56.2848 | -67.0527 | -67.0084 | 0.014095 | -67.1116 | 56.2123 | 56.4679 | 56.265 | -67.1522 | -0.017811 | -0.094264 | -0.000796 | 0.10578 | 0.12359 | -0.32258 | -0.23529 | -0.11733 | -0.3078 | 0.026541 | -0.076645 | 0.040687 | -0.052205 | -0.25504 | 123.4607 | 123.2324 | 123.3197 | 67.0501 | -123.5728 | 123.2472 | 123.5028 | 123.3 | 67.049 | -123.6723
154.2812 | 123.6511 | -67.0486 | 56.5338 | 0.06235 | -0.0034562 | 0.00053446 | 0.053459 | -0.0033719 | 0.051532 | 0.050216 | -0.00064973 | -0.001121 | 0.0606 | 0.018309 | 0.057752 | -67.0449 | 0.015142 | -66.92 | 56.4258 | 56.2021 | 56.2894 | -67.0573 | -66.9992 | 0.018674 | -67.1116 | 56.1985 | 56.4679 | 56.3062 | -67.1568 | -0.008657 | -0.108 | 0.003781 | 0.12867 | 0.13732 | -0.33173 | -0.24444 | -0.10818 | -0.33527 | 0.049431 | -0.062912 | 0.045266 | -0.065937 | -0.22757 | 123.4745 | 123.2507 | 123.338 | 67.0638 | -123.5911 | 123.2472 | 123.5165 | 123.3549 | 67.0673 | -123.6906
155.2969 | 123.7976 | -67.0212 | 56.456 | 0.047088 | -0.0023882 | -0.00053454 | 0.051322 | -0.0044409 | 0.051532 | 0.080738 | -0.0017177 | -0.004326 | 0.0606 | 0.017241 | 0.057752 | -67.0449 | 0.015142 | -66.9337 | 56.4258 | 56.2021 | 56.2848 | -67.0481 | -66.9992 | 0.023253 | -67.1116 | 56.1985 | 56.4587 | 56.3337 | -67.1568 | -0.026965 | -0.030177 | -0.023685 | 0.087465 | 0.11443 | -0.25391 | -0.1712 | -0.13564 | -0.25745 | 0.021965 | -0.090378 | 0.045266 | 0.002724 | -0.12227 | 123.447 | 123.2233 | 123.306 | 67.0363 | -123.5041 | 123.2197 | 123.4799 | 123.3549 | 67.0444 | -123.6128
156.2812 | 123.7518 | -67.012 | 56.5109 | 0.06235 | -0.0034562 | -0.0026705 | 0.053459 | -0.0012359 | 0.049395 | 0.065477 | -0.0017177 | -0.002189 | 0.0606 | 0.015104 | 0.05882 | -67.0449 | 0.005985 | -66.9337 | 56.4167 | 56.2112 | 56.2848 | -67.0344 | -66.9992 | 0.009516 | -67.1116 | 56.1985 | 56.4679 | 56.3246 | -67.1431 | -0.022384 | -0.094264 | -0.03284 | 0.07831 | 0.10069 | -0.29969 | -0.22613 | -0.13106 | -0.31238 | 0.01281 | -0.099533 | 0.03153 | -0.043049 | -0.18636 | 123.4287 | 123.2233 | 123.2968 | 67.018 | -123.5453 | 123.2106 | 123.4799 | 123.3366 | 67.0215 | -123.654
157.2656 | 123.6969 | -67.0349 | 56.5201 | 0.06235 | -0.0023882 | -0.00053454 | 0.052391 | -0.0023039 | 0.050464 | 0.080738 | -0.0017177 | -0.004326 | 0.059532 | 0.017241 | 0.057752 | -67.0357 | 0.010564 | -66.9337 | 56.435 | 56.2112 | 56.2848 | -67.0619 | -67.0038 | 0.023253 | -67.1116 | 56.2031 | 56.4633 | 56.3246 | -67.1568 | -0.026969 | -0.085107 | -0.000796 | 0.1012 | 0.12817 | -0.30884 | -0.23529 | -0.12191 | -0.31696 | 0.03112 | -0.076645 | 0.045266 | -0.056784 | -0.19552 | 123.4699 | 123.2461 | 123.3197 | 67.0455 | -123.582 | 123.238 | 123.4982 | 123.3595 | 67.0582 | -123.6769
158.2656 | 123.6877 | -67.067 | 56.5018 | 0.077612 | -0.0023882 | 0.00053446 | 0.051322 | -0.0044409 | 0.049395 | 0.065477 | -0.00064973 | -0.003257 | 0.058464 | 0.017241 | 0.05882 | -67.0449 | 0.010564 | -66.9246 | 56.435 | 56.2021 | 56.2985 | -67.0436 | -67.013 | 0.004938 | -67.1161 | 56.2031 | 56.4679 | 56.3108 | -67.1477 | 0.023391 | -0.066796 | 0.022092 | 0.1424 | 0.11901 | -0.29969 | -0.20324 | -0.08071 | -0.29865 | 0.054006 | -0.04918 | 0.03153 | -0.033894 | -0.19094 | 123.5019 | 123.269 | 123.3655 | 67.0775 | -123.5453 | 123.2701 | 123.5348 | 123.3778 | 67.0719 | -123.6494
159.2812 | 123.6923 | -67.0486 | 56.5155 | 0.047088 | -0.0034562 | -0.00053454 | 0.052391 | -0.0044409 | 0.051532 | 0.050216 | -0.0017177 | -0.004326 | 0.058464 | 0.018309 | 0.056684 | -67.0494 | 0.015142 | -66.9291 | 56.4212 | 56.1883 | 56.2939 | -67.0436 | -66.9992 | 0.023253 | -67.1116 | 56.1985 | 56.4679 | 56.3062 | -67.1477 | 0.00508 | -0.094264 | -0.000798 | 0.11951 | 0.11443 | -0.32716 | -0.22156 | -0.099021 | -0.31696 | 0.049431 | -0.062912 | 0.036109 | -0.047627 | -0.20926 | 123.4699 | 123.237 | 123.3426 | 67.0638 | -123.5591 | 123.2472 | 123.5165 | 123.3549 | 67.0719 | -123.6632
160.2656 | 123.7198 | -67.0395 | 56.4835 | 0.06235 | -0.0034562 | -0.00053454 | 0.053459 | -0.0033719 | 0.050464 | 0.050216 | -0.00064973 | -0.004326 | 0.0606 | 0.018309 | 0.057752 | -67.0494 | 0.010564 | -66.9291 | 56.4258 | 56.2021 | 56.2894 | -67.0436 | -66.9992 | 0.004938 | -67.1116 | 56.194 | 56.4679 | 56.2834 | -67.1522 | -0.004075 | -0.057642 | -0.009953 | 0.11035 | 0.11443 | -0.28138 | -0.19409 | -0.11275 | -0.28949 | 0.040276 | -0.072067 | 0.040687 | -0.015583 | -0.20011 | 123.4653 | 123.2416 | 123.3289 | 67.0501 | -123.527 | 123.2335 | 123.5074 | 123.3228 | 67.0444 | -123.6357
161.2812 | 123.7656 | -66.9754 | 56.5201 | 0.06235 | -0.0023882 | 0.00053446 | 0.053459 | -0.0044409 | 0.051532 | 0.080738 | -0.0017177 | -0.005394 | 0.058464 | 0.018309 | 0.056684 | -67.0449 | 0.015142 | -66.9291 | 56.4212 | 56.1975 | 56.2894 | -67.0619 | -67.0038 | 0.009516 | -67.1116 | 56.194 | 56.4679 | 56.2879 | -67.1522 | -0.086478 | -0.098842 | -0.069461 | 0.046267 | 0.13274 | -0.32258 | -0.23071 | -0.17684 | -0.32611 | -0.028389 | -0.13615 | 0.040687 | -0.052205 | -0.23215 | 123.3966 | 123.1729 | 123.2648 | 66.9905 | -123.582 | 123.1694 | 123.4433 | 123.2633 | 66.9849 | -123.6723
162.4062 | 123.7976 | -67.0258 | 56.4926 | 0.047088 | -0.0055932 | 0.0016025 | 0.053459 | -0.0044409 | 0.0526 | 0.050216 | -0.00064973 | -0.003257 | 0.058464 | 0.018309 | 0.057752 | -67.0357 | 0.015142 | -66.9246 | 56.4212 | 56.1975 | 56.2848 | -67.0436 | -67.0038 | 0.009516 | -67.1161 | 56.1894 | 56.4633 | 56.3154 | -67.1614 | -0.017808 | -0.071376 | -0.009951 | 0.1012 | 0.11901 | -0.29512 | -0.20782 | -0.13564 | -0.30323 | 0.021965 | -0.090379 | 0.045266 | -0.029318 | -0.17721 | 123.447 | 123.2233 | 123.3105 | 67.0409 | -123.5362 | 123.2151 | 123.4891 | 123.3412 | 67.0353 | -123.654
163.2812 | 123.674 | -67.0212 | 56.543 | 0.077612 | -0.0045252 | 0.00053446 | 0.051322 | -0.0033719 | 0.051532 | 0.080738 | -0.00064973 | -0.004326 | 0.059532 | 0.019377 | 0.05882 | -67.0449 | 0.015142 | -66.9291 | 56.4167 | 56.2021 | 56.2939 | -67.0481 | -66.9992 | 0.014095 | -67.1116 | 56.1985 | 56.4587 | 56.2925 | -67.1614 | -0.026965 | -0.12631 | -0.023685 | 0.092043 | 0.11901 | -0.34089 | -0.24902 | -0.14022 | -0.34442 | 0.021965 | -0.090378 | 0.049845 | -0.084251 | -0.25046 | 123.4378 | 123.2233 | 123.3151 | 67.0363 | -123.5911 | 123.2197 | 123.4799 | 123.3137 | 67.0353 | -123.7044
164.2812 | 123.7518 | -67.012 | 56.5155 | 0.06235 | -0.0013202 | 0.00053446 | 0.052391 | -0.0033719 | 0.049395 | 0.095999 | -0.0027857 | -0.003257 | 0.0606 | 0.019377 | 0.05882 | -67.0403 | 0.010564 | -66.9291 | 56.4258 | 56.1838 | 56.2848 | -67.0481 | -66.9992 | 0.009516 | -67.107 | 56.194 | 56.4587 | 56.3062 | -67.1614 | -0.03612 | -0.089686 | -0.028262 | 0.082888 | 0.11901 | -0.33174 | -0.23071 | -0.14938 | -0.32154 | 0.01281 | -0.094954 | 0.054424 | -0.056785 | -0.20926 | 123.4378 | 123.1958 | 123.2968 | 67.0226 | -123.5636 | 123.206 | 123.4707 | 123.3183 | 67.0215 | -123.6769
165.3125 | 123.7335 | -67.0074 | 56.543 | 0.031826 | -0.0034562 | -0.00053454 | 0.052391 | -0.0033719 | 0.0526 | 0.034955 | -0.0027857 | -0.002189 | 0.0606 | 0.019377 | 0.055616 | -67.0311 | 0.010564 | -66.9246 | 56.4212 | 56.2067 | 56.2894 | -67.0619 | -66.9946 | 0.009516 | -67.1116 | 56.1985 | 56.4633 | 56.3062 | -67.1522 | -0.054435 | -0.12173 | -0.023683 | 0.082888 | 0.13732 | -0.33631 | -0.2536 | -0.1448 | -0.34442 | 0.012811 | -0.10411 | 0.040687 | -0.079672 | -0.23672 | 123.4287 | 123.2141 | 123.2968 | 67.018 | -123.6048 | 123.206 | 123.4707 | 123.3137 | 67.017 | -123.6952
166.2656 | 123.7061 | -67.0303 | 56.5247 | 0.077612 | -0.0013202 | -0.00053454 | 0.053459 | -0.0033719 | 0.051532 | 0.050216 | -0.0017177 | -0.002189 | 0.059532 | 0.019377 | 0.055616 | -67.0403 | 0.015142 | -66.9246 | 56.4258 | 56.2021 | 56.2848 | -67.0481 | -67.0038 | 0.014095 | -67.1116 | 56.2031 | 56.4633 | 56.3154 | -67.1568 | -0.01781 | -0.098841 | -0.009952 | 0.10578 | 0.12359 | -0.32258 | -0.23987 | -0.12649 | -0.32153 | 0.026542 | -0.081223 | 0.045266 | -0.061361 | -0.20925 | 123.4562 | 123.2324 | 123.3151 | 67.0455 | -123.5728 | 123.2335 | 123.4936 | 123.3457 | 67.0444 | -123.6815
167.2656 | 123.7289 | -67.0349 | 56.5155 | 0.047088 | -0.0034562 | 0.00053446 | 0.052391 | -0.0023039 | 0.051532 | 0.080738 | -0.0038537 | -0.003257 | 0.058464 | 0.019377 | 0.057752 | -67.0403 | 0.010564 | -66.9291 | 56.4212 | 56.2021 | 56.2894 | -67.0481 | -67.013 | 0.014095 | -67.1116 | 56.1985 | 56.4633 | 56.32 | -67.1477 | -0.013232 | -0.094264 | -0.005374 | 0.10578 | 0.11901 | -0.31342 | -0.22613 | -0.11275 | -0.31696 | 0.021962 | -0.076645 | 0.036109 | -0.052206 | -0.19552 | 123.4562 | 123.237 | 123.3243 | 67.0455 | -123.5636 | 123.2335 | 123.4982 | 123.3549 | 67.049 | -123.6632
168.2656 | 123.6465 | -67.0624 | 56.5109 | 0.047088 | -0.0023882 | -0.00053454 | 0.052391 | -0.0012359 | 0.051532 | 0.080738 | -0.0017177 | -0.003257 | 0.0606 | 0.020446 | 0.056684 | -67.0403 | 0.010564 | -66.9291 | 56.4304 | 56.1975 | 56.2802 | -67.0481 | -66.9992 | 0.018674 | -67.107 | 56.194 | 56.4725 | 56.3246 | -67.1568 | 0.014234 | -0.080529 | 0.022092 | 0.13324 | 0.11901 | -0.31343 | -0.23071 | -0.094445 | -0.31696 | 0.063164 | -0.0446 | 0.049845 | -0.038471 | -0.18636 | 123.4928 | 123.2599 | 123.3426 | 67.0729 | -123.5591 | 123.2563 | 123.5348 | 123.3869 | 67.0811 | -123.6677
169.2812 | 123.7106 | -67.099 | 56.5018 | 0.047088 | -0.0023882 | -0.00053454 | 0.050254 | -0.0033719 | 0.0526 | 0.065477 | -0.0027857 | -0.002189 | 0.057395 | 0.020446 | 0.055616 | -67.0403 | 0.010564 | -66.9291 | 56.4258 | 56.2021 | 56.2939 | -67.0527 | -67.0084 | 0.014095 | -67.1116 | 56.2031 | 56.4679 | 56.2879 | -67.1477 | 0.046276 | -0.075953 | 0.058713 | 0.16986 | 0.12359 | -0.29969 | -0.20782 | -0.048667 | -0.29865 | 0.090628 | -0.012558 | 0.036109 | -0.033894 | -0.21384 | 123.5248 | 123.3011 | 123.3929 | 67.1096 | -123.5545 | 123.3021 | 123.5669 | 123.3869 | 67.1131 | -123.6494
170.2656 | 123.7198 | -67.0349 | 56.5292 | 0.06235 | -0.0034562 | 0.00053446 | 0.052391 | -0.0023039 | 0.051532 | 0.065477 | -0.0038537 | -0.002189 | 0.058464 | 0.020446 | 0.055616 | -67.0357 | 0.015142 | -66.9337 | 56.4258 | 56.2021 | 56.2802 | -67.0481 | -67.0084 | 0.018674 | -67.107 | 56.1985 | 56.4633 | 56.3017 | -67.1477 | -0.013232 | -0.10342 | -0.000796 | 0.1012 | 0.11443 | -0.32716 | -0.24902 | -0.11275 | -0.33069 | 0.026541 | -0.072066 | 0.040688 | -0.065939 | -0.22757 | 123.4607 | 123.237 | 123.3151 | 67.0501 | -123.5774 | 123.2335 | 123.4982 | 123.3366 | 67.0536 | -123.6769
171.2812 | 123.674 | -67.0853 | 56.4697 | 0.047088 | -0.0034562 | -0.00053454 | 0.050254 | -0.0044409 | 0.049395 | 0.065477 | -0.0017177 | -0.003257 | 0.058464 | 0.019377 | 0.05882 | -67.0403 | 0.010564 | -66.9291 | 56.4212 | 56.1929 | 56.2848 | -67.0573 | -67.0038 | 0.014095 | -67.1116 | 56.1985 | 56.4725 | 56.3291 | -67.1522 | 0.027964 | -0.048488 | 0.04498 | 0.15613 | 0.12817 | -0.27681 | -0.18494 | -0.066978 | -0.27118 | 0.081474 | -0.026291 | 0.040687 | 0.002727 | -0.14059 | 123.5065 | 123.2782 | 123.3701 | 67.0958 | -123.527 | 123.2838 | 123.5577 | 123.4144 | 67.0994 | -123.622
172.2656 | 123.6786 | -67.0532 | 56.5201 | 0.047088 | -0.0023882 | -0.00053454 | 0.051322 | -0.0044409 | 0.050464 | 0.065477 | -0.0027857 | -0.003257 | 0.058464 | 0.020446 | 0.056684 | -67.0449 | 0.005985 | -66.9337 | 56.4258 | 56.1929 | 56.2939 | -67.0573 | -67.0084 | 0.009516 | -67.107 | 56.1894 | 56.4587 | 56.3108 | -67.1477 | -0.004079 | -0.094264 | 0.008359 | 0.11951 | 0.12359 | -0.32716 | -0.22613 | -0.094443 | -0.33069 | 0.044852 | -0.053755 | 0.040688 | -0.061363 | -0.20925 | 123.479 | 123.2461 | 123.3472 | 67.0592 | -123.5774 | 123.2426 | 123.5119 | 123.364 | 67.0627 | -123.6677
173.2656 | 123.7152 | -67.0258 | 56.5063 | 0.06235 | -0.0045252 | -0.0026705 | 0.051322 | -0.0033719 | 0.050464 | 0.080738 | -0.00064973 | -0.003257 | 0.058464 | 0.020446 | 0.055616 | -67.0494 | 0.015142 | -66.9383 | 56.4304 | 56.2021 | 56.2894 | -67.0665 | -66.9992 | 0.014095 | -67.107 | 56.1985 | 56.4679 | 56.2879 | -67.1568 | -0.040703 | -0.075952 | -0.023686 | 0.087464 | 0.12817 | -0.30427 | -0.21698 | -0.13107 | -0.3078 | 0.026543 | -0.081221 | 0.049845 | -0.038472 | -0.21842 | 123.4562 | 123.2278 | 123.3151 | 67.0409 | -123.5728 | 123.2243 | 123.4936 | 123.3137 | 67.0399 | -123.6632
174.2812 | 123.7473 | -66.9937 | 56.4697 | 0.031826 | -0.0023882 | -0.0016025 | 0.050254 | -0.0044409 | 0.049395 | 0.050216 | -0.0038537 | -0.001121 | 0.058464 | 0.020446 | 0.054547 | -67.0449 | 0.019721 | -66.9291 | 56.4212 | 56.2021 | 56.2939 | -67.0527 | -67.0084 | 0.009516 | -67.1161 | 56.1894 | 56.4679 | 56.3108 | -67.1614 | -0.05901 | -0.048488 | -0.051151 | 0.064577 | 0.12359 | -0.26765 | -0.17578 | -0.16769 | -0.28034 | -0.014658 | -0.12242 | 0.045266 | -0.001851 | -0.1589 | 123.415 | 123.1958 | 123.2877 | 67.0134 | -123.5224 | 123.1831 | 123.4616 | 123.3045 | 67.0032 | -123.6311
175.2656 | 123.6557 | -67.0349 | 56.5521 | 0.077612 | -0.0034562 | -0.0016025 | 0.051322 | -0.0023039 | 0.049395 | 0.065477 | -0.0027857 | -0.001121 | 0.059532 | 0.020446 | 0.056684 | -67.0403 | 0.010564 | -66.9291 | 56.4304 | 56.2021 | 56.2894 | -67.0436 | -67.0038 | 0.014095 | -67.1116 | 56.194 | 56.4725 | 56.32 | -67.1522 | -0.008653 | -0.12173 | -0.005374 | 0.10578 | 0.11443 | -0.35005 | -0.26275 | -0.11733 | -0.35816 | 0.03112 | -0.076645 | 0.040687 | -0.07967 | -0.23214 | 123.4653 | 123.237 | 123.3243 | 67.0455 | -123.5957 | 123.2289 | 123.5074 | 123.3549 | 67.049 | -123.7044
176.2812 | 123.7061 | -67.0303 | 56.5292 | 0.047088 | -0.0013202 | -0.0016025 | 0.051322 | -0.0023039 | 0.051532 | 0.080738 | -0.0027857 | -0.002189 | 0.059532 | 0.021514 | 0.056684 | -67.0311 | 0.015142 | -66.9337 | 56.4258 | 56.1975 | 56.2939 | -67.0527 | -67.0084 | 0.018674 | -67.1161 | 56.1985 | 56.4725 | 56.3017 | -67.1614 | -0.022389 | -0.10342 | -0.000795 | 0.09662 | 0.11901 | -0.33174 | -0.23529 | -0.13107 | -0.33069 | 0.021963 | -0.085802 | 0.045266 | -0.056782 | -0.22757 | 123.4562 | 123.2278 | 123.3243 | 67.0455 | -123.582 | 123.2289 | 123.5028 | 123.332 | 67.049 | -123.6906
177.2656 | 123.7152 | -67.0212 | 56.543 | 0.047088 | -0.0023882 | -0.0026705 | 0.051322 | -0.0023039 | 0.051532 | 0.050216 | -0.00064973 | -0.003257 | 0.059532 | 0.021514 | 0.055616 | -67.0403 | 0.015142 | -66.9246 | 56.4258 | 56.2067 | 56.2939 | -67.0573 | -67.0084 | 0.014095 | -67.1116 | 56.1894 | 56.4725 | 56.2834 | -67.1477 | -0.036123 | -0.11715 | -0.019107 | 0.096621 | 0.13274 | -0.33631 | -0.24902 | -0.12649 | -0.35358 | 0.012808 | -0.090378 | 0.036109 | -0.070515 | -0.25961 | 123.447 | 123.2278 | 123.3151 | 67.0363 | -123.6003 | 123.2106 | 123.4936 | 123.3045 | 67.0353 | -123.6906
178.2656 | 123.6786 | -67.0532 | 56.5384 | 0.047088 | -0.0034562 | -0.00053454 | 0.053459 | -0.0023039 | 0.050464 | 0.065477 | 0.00041927 | -0.004326 | 0.057395 | 0.021514 | 0.055616 | -67.0403 | 0.010564 | -66.9291 | 56.4167 | 56.2067 | 56.2894 | -67.0527 | -66.9992 | 0.014095 | -67.1116 | 56.1985 | 56.4633 | 56.32 | -67.1477 | 0.0005 | -0.12173 | 0.012937 | 0.12409 | 0.12359 | -0.33173 | -0.24902 | -0.094443 | -0.33985 | 0.054009 | -0.058334 | 0.036109 | -0.075094 | -0.21841 | 123.4699 | 123.2599 | 123.3426 | 67.0638 | -123.5911 | 123.2518 | 123.5165 | 123.3732 | 67.0673 | -123.6861
179.2812 | 123.6877 | -67.0441 | 56.5247 | 0.06235 | -0.0034562 | -0.0026705 | 0.052391 | -0.0044409 | 0.050464 | 0.080738 | -0.0027857 | -0.004326 | 0.058464 | 0.021514 | 0.056684 | -67.0311 | 0.010564 | -66.9337 | 56.4258 | 56.2021 | 56.2939 | -67.0573 | -67.0084 | 0.014095 | -67.1024 | 56.194 | 56.4725 | 56.3337 | -67.1568 | -0.013235 | -0.098841 | 0.012938 | 0.11035 | 0.12359 | -0.32258 | -0.23071 | -0.11276 | -0.33069 | 0.035696 | -0.058332 | 0.054424 | -0.052204 | -0.19094 | 123.4699 | 123.2461 | 123.338 | 67.0546 | -123.582 | 123.238 | 123.5165 | 123.3778 | 67.0582 | -123.6815
180.2656 | 123.7106 | -67.0532 | 56.5018 | 0.077612 | -0.0034562 | -0.0026705 | 0.051322 | -0.0023039 | 0.050464 | 0.050216 | -0.0027857 | -0.003257 | 0.059532 | 0.023651 | 0.056684 | -67.0449 | 0.015142 | -66.9246 | 56.4304 | 56.2067 | 56.2985 | -67.0573 | -67.0084 | 0.009516 | -67.1116 | 56.1985 | 56.4725 | 56.3062 | -67.1568 | -0.004079 | -0.071374 | 0.008359 | 0.12866 | 0.13274 | -0.29511 | -0.20324 | -0.1036 | -0.30322 | 0.044852 | -0.058334 | 0.045266 | -0.029316 | -0.19552 | 123.4836 | 123.2599 | 123.3517 | 67.0684 | -123.5591 | 123.2518 | 123.5257 | 123.3595 | 67.0627 | -123.6586
181.2812 | 123.7106 | -67.0349 | 56.5155 | 0.06235 | -0.0045252 | -0.0026705 | 0.051322 | -0.0023039 | 0.050464 | 0.065477 | -0.0017177 | -0.002189 | 0.057395 | 0.023651 | 0.056684 | -67.0357 | 0.015142 | -66.9337 | 56.4258 | 56.2112 | 56.2985 | -67.0481 | -67.0038 | 0.018674 | -67.107 | 56.194 | 56.4633 | 56.2925 | -67.1614 | -0.013232 | -0.089686 | -0.000796 | 0.1012 | 0.11443 | -0.30427 | -0.21698 | -0.12649 | -0.32154 | 0.03112 | -0.072066 | 0.054424 | -0.052206 | -0.22299 | 123.4607 | 123.2461 | 123.3334 | 67.0501 | -123.5636 | 123.2289 | 123.4982 | 123.3274 | 67.0536 | -123.6769
182.2656 | 123.6877 | -67.0258 | 56.5384 | 0.047088 | -0.0034562 | 0.00053446 | 0.050254 | -0.0033719 | 0.049395 | 0.065477 | -0.00064973 | -0.003257 | 0.059532 | 0.021514 | 0.056684 | -67.0357 | 0.005985 | -66.9246 | 56.4258 | 56.2112 | 56.2985 | -67.0436 | -66.9992 | 0.014095 | -67.1024 | 56.194 | 56.4725 | 56.3291 | -67.1568 | -0.017808 | -0.11257 | -0.009951 | 0.1012 | 0.11901 | -0.32715 | -0.23986 | -0.13107 | -0.34442 | 0.026543 | -0.076642 | 0.054424 | -0.065937 | -0.20925 | 123.4516 | 123.237 | 123.3243 | 67.0317 | -123.582 | 123.2197 | 123.4982 | 123.3549 | 67.0399 | -123.6952
183.2656 | 123.8022 | -66.9937 | 56.5155 | 0.06235 | -0.0034562 | -0.0016025 | 0.052391 | -0.0033719 | 0.049395 | 0.065477 | -0.0017177 | -0.002189 | 0.058464 | 0.021514 | 0.055616 | -67.0403 | 0.015142 | -66.9291 | 56.4258 | 56.2021 | 56.2985 | -67.0527 | -66.9946 | 0.018674 | -67.1116 | 56.2031 | 56.4725 | 56.3383 | -67.1568 | -0.05901 | -0.089686 | -0.046573 | 0.064577 | 0.12359 | -0.31342 | -0.21698 | -0.16311 | -0.31238 | -0.000922 | -0.11784 | 0.045266 | -0.043049 | -0.17721 | 123.4195 | 123.1958 | 123.2922 | 67.0089 | -123.5682 | 123.1968 | 123.4662 | 123.332 | 67.0124 | -123.6723
184.2812 | 123.6923 | -67.012 | 56.5292 | 0.077612 | -0.0023882 | -0.00053454 | 0.051322 | -0.0044409 | 0.050464 | 0.065477 | -0.0038537 | -0.006462 | 0.059532 | 0.021514 | 0.056684 | -67.0403 | 0.010564 | -66.9383 | 56.4304 | 56.2112 | 56.2939 | -67.0573 | -66.9992 | 0.023253 | -67.1024 | 56.1985 | 56.477 | 56.32 | -67.1614 | -0.045278 | -0.09884 | -0.028262 | 0.073731 | 0.11901 | -0.318 | -0.23529 | -0.14938 | -0.33069 | 0.01281 | -0.090375 | 0.059003 | -0.052203 | -0.20925 | 123.4424 | 123.2233 | 123.306 | 67.0226 | -123.5865 | 123.2106 | 123.4891 | 123.332 | 67.0353 | -123.6906
185.2656 | 123.7015 | -67.0486 | 56.5384 | 0.031826 | -0.0034562 | 0.00053446 | 0.052391 | -0.0044409 | 0.049395 | 0.065477 | -0.0027857 | -0.003257 | 0.057395 | 0.021514 | 0.054547 | -67.0357 | 0.010564 | -66.9291 | 56.4258 | 56.2067 | 56.2939 | -67.0436 | -66.9946 | 0.014095 | -67.1116 | 56.194 | 56.4633 | 56.3062 | -67.1568 | 0.00508 | -0.11257 | 0.012937 | 0.11951 | 0.11443 | -0.33173 | -0.24444 | -0.10818 | -0.34442 | 0.05401 | -0.062912 | 0.045266 | -0.075094 | -0.23214 | 123.4745 | 123.2553 | 123.3426 | 67.0592 | -123.582 | 123.2426 | 123.5119 | 123.3549 | 67.0627 | -123.6952
186.2812 | 123.7152 | -67.0212 | 56.5018 | 0.06235 | -0.0034562 | -0.0016025 | 0.051322 | -0.0044409 | 0.049395 | 0.034955 | -0.0017177 | -0.003257 | 0.058464 | 0.022583 | 0.055616 | -67.0403 | 0.015142 | -66.9246 | 56.4258 | 56.2067 | 56.2848 | -67.0527 | -67.0038 | 0.014095 | -67.1116 | 56.194 | 56.4725 | 56.3383 | -67.1568 | -0.031544 | -0.075953 | -0.019107 | 0.096621 | 0.12816 | -0.29511 | -0.21698 | -0.13564 | -0.3078 | 0.017387 | -0.090378 | 0.045266 | -0.029316 | -0.16347 | 123.447 | 123.2278 | 123.306 | 67.0363 | -123.5545 | 123.2151 | 123.4936 | 123.3595 | 67.0353 | -123.6586
187.2656 | 123.7244 | -67.0532 | 56.5384 | 0.06235 | -0.0034562 | -0.00053454 | 0.052391 | -0.0044409 | 0.049395 | 0.065477 | -0.00064973 | -0.005394 | 0.057395 | 0.022583 | 0.056684 | -67.0357 | 0.019721 | -66.9291 | 56.4258 | 56.2112 | 56.2939 | -67.0527 | -67.0038 | 0.009516 | -67.1024 | 56.1985 | 56.4725 | 56.32 | -67.1614 | 0.0005 | -0.11257 | 0.017515 | 0.12409 | 0.12359 | -0.32715 | -0.24444 | -0.10818 | -0.33985 | 0.049431 | -0.049176 | 0.059003 | -0.065937 | -0.21841 | 123.479 | 123.2645 | 123.3472 | 67.0729 | -123.5911 | 123.2518 | 123.5257 | 123.3732 | 67.0627 | -123.6998
188.2656 | 123.7106 | -67.0258 | 56.5109 | 0.077612 | -0.0045252 | -0.00053454 | 0.049185 | -0.0033719 | 0.050464 | 0.095999 | -0.0038537 | -0.004326 | 0.056327 | 0.021514 | 0.055616 | -67.0403 | 0.019721 | -66.9337 | 56.4258 | 56.1929 | 56.2894 | -67.071 | -67.0038 | 0.014095 | -67.1116 | 56.1985 | 56.4679 | 56.3337 | -67.1568 | -0.045282 | -0.085108 | -0.014529 | 0.092043 | 0.13733 | -0.318 | -0.22156 | -0.13107 | -0.31238 | 0.021965 | -0.0858 | 0.045266 | -0.043049 | -0.17721 | 123.4516 | 123.2187 | 123.3151 | 67.0455 | -123.582 | 123.2243 | 123.4936 | 123.3595 | 67.0399 | -123.6677
189.2812 | 123.6969 | -67.0441 | 56.5155 | 0.06235 | -0.0045252 | 0.00053446 | 0.052391 | -0.0033719 | 0.049395 | 0.080738 | -0.0027857 | -0.002189 | 0.058464 | 0.022583 | 0.055616 | -67.0357 | 0.010564 | -66.9291 | 56.4258 | 56.2021 | 56.2939 | -67.0573 | -67.0038 | 0.009516 | -67.1116 | 56.1985 | 56.477 | 56.3291 | -67.1522 | -0.013235 | -0.089686 | 0.008359 | 0.11493 | 0.12817 | -0.31342 | -0.22156 | -0.10818 | -0.31696 | 0.040275 | -0.06749 | 0.040687 | -0.03847 | -0.18636 | 123.4699 | 123.2461 | 123.338 | 67.0546 | -123.5728 | 123.2426 | 123.5211 | 123.3732 | 67.0536 | -123.6677
190.2812 | 123.7244 | -67.0166 | 56.575 | 0.077612 | -0.0023882 | 0.00053446 | 0.050254 | -0.0044409 | 0.051532 | 0.065477 | -0.0027857 | -0.002189 | 0.057395 | 0.022583 | 0.056684 | -67.0403 | 0.015142 | -66.9246 | 56.4167 | 56.1929 | 56.3031 | -67.0344 | -67.0038 | 0.018674 | -67.1024 | 56.2031 | 56.4679 | 56.3017 | -67.1522 | -0.017806 | -0.15835 | -0.023684 | 0.092044 | 0.10985 | -0.38209 | -0.27191 | -0.13564 | -0.37189 | 0.01281 | -0.085797 | 0.049845 | -0.10714 | -0.27334 | 123.4333 | 123.2095 | 123.3197 | 67.0317 | -123.6094 | 123.2197 | 123.4845 | 123.3183 | 67.0353 | -123.7273
191.2812 | 123.6603 | -67.0166 | 56.5338 | 0.077612 | -0.0045252 | -0.00053454 | 0.050254 | -0.0033719 | 0.049395 | 0.050216 | -0.0017177 | -0.003257 | 0.059532 | 0.023651 | 0.053479 | -67.0357 | 0.010564 | -66.9291 | 56.4258 | 56.1929 | 56.3031 | -67.0573 | -66.9946 | 0.009516 | -67.1116 | 56.194 | 56.4679 | 56.3154 | -67.166 | -0.0407 | -0.108 | -0.019106 | 0.087466 | 0.12817 | -0.34089 | -0.23071 | -0.14938 | -0.33985 | 0.021967 | -0.094955 | 0.054424 | -0.065937 | -0.21841 | 123.4424 | 123.2095 | 123.3197 | 67.0272 | -123.5911 | 123.2106 | 123.4845 | 123.332 | 67.0261 | -123.6998
192.2656 | 123.7518 | -67.0074 | 56.4972 | 0.047088 | -0.0023882 | -0.00053454 | 0.053459 | -0.0012359 | 0.049395 | 0.065477 | -0.0027857 | -0.005394 | 0.058464 | 0.023651 | 0.055616 | -67.0449 | 0.005985 | -66.9291 | 56.4212 | 56.1929 | 56.2985 | -67.0481 | -66.9946 | 0.009516 | -67.1161 | 56.1985 | 56.4587 | 56.2696 | -67.1706 | -0.040698 | -0.075953 | -0.037418 | 0.07831 | 0.11901 | -0.30427 | -0.19867 | -0.16311 | -0.29865 | 0.012811 | -0.10869 | 0.054424 | -0.038474 | -0.22757 | 123.4287 | 123.2004 | 123.306 | 67.0134 | -123.5453 | 123.206 | 123.4662 | 123.2771 | 67.017 | -123.6678
193.2656 | 123.7976 | -66.9983 | 56.5109 | 0.077612 | -0.0034562 | -0.0026705 | 0.051322 | -0.0044409 | 0.049395 | 0.034955 | -0.0017177 | -0.003257 | 0.059532 | 0.023651 | 0.054547 | -67.0403 | 0.010564 | -66.9337 | 56.4212 | 56.2021 | 56.3031 | -67.0481 | -66.9946 | 0.014095 | -67.107 | 56.194 | 56.4633 | 56.3246 | -67.1614 | -0.049853 | -0.089686 | -0.041995 | 0.064577 | 0.11443 | -0.30885 | -0.20782 | -0.16311 | -0.31696 | 0.003656 | -0.10869 | 0.054424 | -0.047628 | -0.18636 | 123.4195 | 123.2004 | 123.3014 | 67.0089 | -123.5591 | 123.1923 | 123.4616 | 123.3229 | 67.0124 | -123.6723
194.2812 | 123.6511 | -67.0395 | 56.4926 | 0.06235 | -0.0034562 | -0.0016025 | 0.051322 | -0.0033719 | 0.051532 | 0.065477 | -0.0017177 | -0.003257 | 0.058464 | 0.023651 | 0.055616 | -67.0266 | 0.015142 | -66.9291 | 56.4258 | 56.2021 | 56.2985 | -67.0527 | -66.9946 | 0.014095 | -67.107 | 56.1985 | 56.4633 | 56.3246 | -67.1614 | -0.013233 | -0.066798 | 0.012939 | 0.11035 | 0.12359 | -0.29054 | -0.19409 | -0.12191 | -0.29407 | 0.044855 | -0.067488 | 0.054424 | -0.029318 | -0.16805 | 123.4653 | 123.2416 | 123.338 | 67.0546 | -123.5453 | 123.238 | 123.5028 | 123.3641 | 67.0536 | -123.654
195.2812 | 123.674 | -67.0074 | 56.5384 | 0.077612 | -0.0034562 | -0.0016025 | 0.051322 | -0.0023039 | 0.048327 | 0.080738 | -0.0017177 | -0.004326 | 0.059532 | 0.024719 | 0.054547 | -67.0357 | 0.0243 | -66.9291 | 56.4167 | 56.1883 | 56.2985 | -67.0619 | -67.0038 | 0.004938 | -67.1024 | 56.1985 | 56.4725 | 56.2971 | -67.1568 | -0.054435 | -0.12173 | -0.028262 | 0.07831 | 0.13274 | -0.35005 | -0.23986 | -0.14938 | -0.33985 | 0.003654 | -0.094953 | 0.054424 | -0.065937 | -0.2413 | 123.4241 | 123.1958 | 123.306 | 67.0317 | -123.6003 | 123.206 | 123.4799 | 123.3045 | 67.0124 | -123.6952
196.2812 | 123.7381 | -67.0166 | 56.5338 | 0.06235 | -0.0055932 | 0.00053446 | 0.051322 | -0.0033719 | 0.049395 | 0.080738 | -0.0027857 | -0.002189 | 0.058464 | 0.024719 | 0.053479 | -67.0311 | 0.015142 | -66.9429 | 56.4258 | 56.2067 | 56.3031 | -67.0573 | -66.9946 | 0.014095 | -67.1116 | 56.1985 | 56.4679 | 56.3154 | -67.1568 | -0.0407 | -0.108 | -0.014527 | 0.073731 | 0.11443 | -0.32716 | -0.23071 | -0.14022 | -0.33527 | 0.021967 | -0.094955 | 0.045266 | -0.065937 | -0.21841 | 123.4424 | 123.2233 | 123.3197 | 67.0317 | -123.5911 | 123.2151 | 123.4845 | 123.332 | 67.0307 | -123.6906
197.2656 | 123.793 | -67.0212 | 56.4743 | 0.077612 | -0.0023882 | 0.00053446 | 0.051322 | -0.0012359 | 0.049395 | 0.080738 | -0.0027857 | -0.004326 | 0.057395 | 0.024719 | 0.055616 | -67.0357 | 0.010564 | -66.9246 | 56.4167 | 56.2021 | 56.2894 | -67.0436 | -66.9992 | 0.009516 | -67.1116 | 56.1985 | 56.4725 | 56.3246 | -67.1568 | -0.022386 | -0.057643 | -0.014529 | 0.096621 | 0.11901 | -0.27222 | -0.18493 | -0.13564 | -0.27576 | 0.021965 | -0.090378 | 0.045266 | -0.00185 | -0.14974 | 123.4378 | 123.2233 | 123.3105 | 67.0317 | -123.5179 | 123.2197 | 123.4936 | 123.3457 | 67.0307 | -123.6311
198.2812 | 123.6465 | -67.0303 | 56.5567 | 0.092874 | -0.0045252 | -0.00053454 | 0.051322 | -0.0023039 | 0.049395 | 0.065477 | -0.0017177 | -0.003257 | 0.059532 | 0.026856 | 0.054547 | -67.0403 | 0.005985 | -66.92 | 56.4212 | 56.2067 | 56.2894 | -67.0527 | -67.0084 | 0.009516 | -67.0932 | 56.194 | 56.4725 | 56.2925 | -67.1522 | -0.022389 | -0.13546 | -0.009952 | 0.11035 | 0.13274 | -0.35004 | -0.26733 | -0.12191 | -0.36274 | 0.021963 | -0.062908 | 0.059002 | -0.084248 | -0.26419 | 123.4516 | 123.237 | 123.3197 | 67.0363 | -123.6094 | 123.2243 | 123.5028 | 123.3228 | 67.0399 | -123.7089
199.2812 | 123.6649 | -67.0166 | 56.5292 | 0.077612 | -0.0045252 | -0.00053454 | 0.050254 | -0.0044409 | 0.049395 | 0.065477 | -0.00064973 | -0.003257 | 0.057395 | 0.023651 | 0.055616 | -67.0311 | 0.0243 | -66.9291 | 56.4258 | 56.2067 | 56.2939 | -67.0619 | -66.9992 | 0.014095 | -67.1161 | 56.1985 | 56.4679 | 56.3062 | -67.1522 | -0.045279 | -0.10342 | -0.014527 | 0.087466 | 0.13274 | -0.32258 | -0.23529 | -0.13564 | -0.33069 | 0.017388 | -0.099534 | 0.036108 | -0.06136 | -0.22299 | 123.4424 | 123.2233 | 123.3105 | 67.0409 | -123.5911 | 123.2151 | 123.4845 | 123.3228 | 67.0307 | -123.6815
200.2812 | 123.7656 | -66.9846 | 56.5018 | 0.06235 | -0.0034562 | -0.0016025 | 0.051322 | -0.0065769 | 0.049395 | 0.080738 | -0.0017177 | -0.003257 | 0.058464 | 0.023651 | 0.054547 | -67.0357 | 0.010564 | -66.9246 | 56.4212 | 56.1929 | 56.2939 | -67.0573 | -66.9992 | 0.014095 | -67.1116 | 56.1985 | 56.4679 | 56.3429 | -67.1568 | -0.072744 | -0.080531 | -0.05115 | 0.06 | 0.13274 | -0.30885 | -0.20782 | -0.17226 | -0.30322 | -0.014656 | -0.127 | 0.045266 | -0.033894 | -0.15889 | 123.4058 | 123.1775 | 123.2785 | 66.9951 | -123.5591 | 123.1831 | 123.4524 | 123.3274 | 66.9987 | -123.6586
201.2812 | 123.7335 | -67.0303 | 56.4835 | 0.047088 | -0.0034562 | -0.00053454 | 0.051322 | -0.0023039 | 0.048327 | 0.065477 | -0.0017177 | -0.003257 | 0.058464 | 0.025788 | 0.055616 | -67.0357 | 0.019721 | -66.9246 | 56.4258 | 56.2021 | 56.2939 | -67.0481 | -66.9992 | 0.014095 | -67.1024 | 56.2077 | 56.4725 | 56.3246 | -67.1614 | -0.01781 | -0.057642 | -0.005374 | 0.10578 | 0.12359 | -0.28138 | -0.18951 | -0.13107 | -0.27576 | 0.03112 | -0.072065 | 0.059003 | -0.011005 | -0.1589 | 123.4562 | 123.2324 | 123.3243 | 67.0501 | -123.5316 | 123.238 | 123.5028 | 123.3549 | 67.0444 | -123.6449
202.2812 | 123.6832 | -67.0395 | 56.575 | 0.077612 | -0.0034562 | -0.0016025 | 0.051322 | -0.0044409 | 0.050464 | 0.080738 | -0.0017177 | -0.004326 | 0.057395 | 0.024719 | 0.054547 | -67.0311 | 0.019721 | -66.9337 | 56.4212 | 56.1929 | 56.2939 | -67.0436 | -67.0038 | 0.000359 | -67.1024 | 56.1985 | 56.4679 | 56.3337 | -67.1568 | -0.004075 | -0.15377 | 0.008361 | 0.10578 | 0.10985 | -0.38209 | -0.28106 | -0.11733 | -0.37647 | 0.035698 | -0.062909 | 0.054424 | -0.10714 | -0.24129 | 123.4607 | 123.2324 | 123.3334 | 67.0592 | -123.6186 | 123.238 | 123.5074 | 123.3732 | 67.0398 | -123.7318
203.2812 | 123.8113 | -67.0029 | 56.4835 | 0.06235 | -0.0045252 | -0.0016025 | 0.049185 | -0.0055089 | 0.048327 | 0.080738 | -0.0038537 | -0.004326 | 0.056327 | 0.024719 | 0.054547 | -67.0357 | 0.0243 | -66.9246 | 56.4304 | 56.2021 | 56.2939 | -67.0481 | -66.9992 | 0.018674 | -67.1116 | 56.1985 | 56.4633 | 56.3062 | -67.1614 | -0.045275 | -0.053063 | -0.032839 | 0.078311 | 0.12359 | -0.28138 | -0.18951 | -0.15853 | -0.28491 | 0.003655 | -0.10869 | 0.049845 | -0.020162 | -0.17721 | 123.4333 | 123.2049 | 123.2968 | 67.0272 | -123.5316 | 123.2014 | 123.4662 | 123.3091 | 67.0215 | -123.6449
204.2812 | 123.6832 | -67.0303 | 56.5018 | 0.047088 | -0.0045252 | 0.00053446 | 0.051322 | -0.0044409 | 0.050464 | 0.080738 | -0.0027857 | -0.005394 | 0.059532 | 0.024719 | 0.054547 | -67.0311 | 0.019721 | -66.9291 | 56.4258 | 56.2067 | 56.2985 | -67.0619 | -66.9992 | 0.009516 | -67.0978 | 56.2031 | 56.4679 | 56.2925 | -67.1568 | -0.031547 | -0.075953 | -0.000795 | 0.1012 | 0.13274 | -0.29511 | -0.20324 | -0.12649 | -0.29865 | 0.03112 | -0.067487 | 0.059002 | -0.033894 | -0.20926 | 123.4562 | 123.237 | 123.3289 | 67.0501 | -123.5637 | 123.2335 | 123.4982 | 123.3228 | 67.0399 | -123.6586
205.2656 | 123.9075 | -66.9479 | 56.5475 | 0.077612 | -0.0045252 | 0.00053446 | 0.051322 | -0.0033719 | 0.049395 | 0.065477 | -0.0027857 | -0.004326 | 0.059532 | 0.026856 | 0.054547 | -67.0357 | 0.005985 | -66.9246 | 56.4258 | 56.2112 | 56.2985 | -67.0436 | -66.9992 | 0.009516 | -67.1116 | 56.194 | 56.4633 | 56.3062 | -67.166 | -0.095628 | -0.12173 | -0.087771 | 0.023379 | 0.11901 | -0.33631 | -0.24902 | -0.21804 | -0.35358 | -0.051277 | -0.16362 | 0.054424 | -0.084249 | -0.2413 | 123.3738 | 123.1592 | 123.2465 | 66.9539 | -123.5911 | 123.1419 | 123.4112 | 123.2542 | 66.9575 | -123.7135
206.2812 | 123.7381 | -67.0441 | 56.488 | 0.06235 | -0.0023882 | -0.00053454 | 0.048117 | -0.0033719 | 0.049395 | 0.065477 | -0.0049217 | -0.003257 | 0.059532 | 0.025788 | 0.053479 | -67.0357 | 0.019721 | -66.9291 | 56.4258 | 56.2021 | 56.2894 | -67.0481 | -66.9992 | 0.009516 | -67.107 | 56.2031 | 56.4633 | 56.3108 | -67.1614 | -0.004077 | -0.06222 | 0.008359 | 0.11493 | 0.11901 | -0.28596 | -0.19867 | -0.11733 | -0.28491 | 0.044853 | -0.062911 | 0.054424 | -0.02474 | -0.17721 | 123.4699 | 123.2461 | 123.3334 | 67.0638 | -123.5362 | 123.2472 | 123.5074 | 123.3549 | 67.0536 | -123.6494
207.2656 | 123.7793 | -67.0029 | 56.5109 | 0.077612 | -0.0013202 | -0.00053454 | 0.050254 | -0.0055089 | 0.050464 | 0.065477 | -0.0017177 | -0.004326 | 0.058464 | 0.024719 | 0.054547 | -67.0357 | 0.019721 | -66.92 | 56.4167 | 56.2021 | 56.2939 | -67.0436 | -67.0038 | 0.018674 | -67.1116 | 56.1985 | 56.4679 | 56.3017 | -67.1568 | -0.040696 | -0.094264 | -0.032839 | 0.08289 | 0.12359 | -0.30885 | -0.21698 | -0.15395 | -0.31238 | -0.000923 | -0.10869 | 0.045266 | -0.043049 | -0.20926 | 123.4195 | 123.2049 | 123.2968 | 67.0226 | -123.5545 | 123.2014 | 123.4707 | 123.3045 | 67.0215 | -123.6677
208.2656 | 123.8113 | -66.9662 | 56.5063 | 0.06235 | -0.0034562 | -0.00053454 | 0.050254 | -0.0044409 | 0.048327 | 0.080738 | -0.0027857 | -0.005394 | 0.057395 | 0.026856 | 0.053479 | -67.0266 | 0.019721 | -66.9246 | 56.4258 | 56.2067 | 56.2894 | -67.0527 | -66.9946 | 0.014095 | -67.1024 | 56.1985 | 56.4633 | 56.3291 | -67.1614 | -0.086475 | -0.080531 | -0.060303 | 0.04169 | 0.12816 | -0.29969 | -0.21698 | -0.19515 | -0.3078 | -0.028387 | -0.13615 | 0.059003 | -0.043051 | -0.17721 | 123.3921 | 123.1729 | 123.2556 | 66.986 | -123.5591 | 123.1648 | 123.4295 | 123.2954 | 66.9803 | -123.6677
209.2812 | 123.6786 | -67.0395 | 56.543 | 0.077612 | -0.0034562 | -0.00053454 | 0.050254 | -0.0055089 | 0.047259 | 0.080738 | -0.0027857 | -0.004326 | 0.057395 | 0.026856 | 0.054547 | -67.0311 | 0.010564 | -66.9337 | 56.4258 | 56.2112 | 56.2939 | -67.0481 | -66.9901 | 0.018674 | -67.107 | 56.2031 | 56.4679 | 56.3062 | -67.166 | -0.008654 | -0.11715 | 0.008361 | 0.10578 | 0.11443 | -0.33173 | -0.24902 | -0.12649 | -0.33984 | 0.049434 | -0.067488 | 0.059003 | -0.075093 | -0.23672 | 123.4653 | 123.2507 | 123.3334 | 67.0501 | -123.5911 | 123.2426 | 123.5074 | 123.3457 | 67.0582 | -123.709
210.2812 | 123.8022 | -66.9846 | 56.488 | 0.06235 | -0.0034562 | -0.0016025 | 0.051322 | -0.0033719 | 0.049395 | 0.080738 | -0.0027857 | -0.004326 | 0.056327 | 0.025788 | 0.056684 | -67.0357 | 0.019721 | -66.9246 | 56.4304 | 56.2021 | 56.2985 | -67.071 | -66.9992 | 0.014095 | -67.107 | 56.1985 | 56.4725 | 56.2742 | -67.1568 | -0.086481 | -0.057641 | -0.05115 | 0.06 | 0.14648 | -0.28596 | -0.18951 | -0.17226 | -0.28949 | -0.014656 | -0.12242 | 0.049845 | -0.015583 | -0.21384 | 123.415 | 123.1866 | 123.2831 | 67.0043 | -123.5591 | 123.1831 | 123.457 | 123.2588 | 66.9987 | -123.6449
211.2812 | 123.7015 | -67.0258 | 56.5247 | 0.077612 | -0.0034562 | -0.0016025 | 0.050254 | -0.0044409 | 0.049395 | 0.065477 | -0.0017177 | -0.004326 | 0.057395 | 0.025788 | 0.056684 | -67.0311 | 0.019721 | -66.9337 | 56.4304 | 56.2158 | 56.3031 | -67.0619 | -67.0084 | 0.014095 | -67.107 | 56.2031 | 56.4679 | 56.3154 | -67.166 | -0.036124 | -0.094262 | -0.005372 | 0.092043 | 0.12817 | -0.30884 | -0.22155 | -0.14022 | -0.32153 | 0.017386 | -0.081221 | 0.059003 | -0.056782 | -0.20925 | 123.4562 | 123.2416 | 123.3289 | 67.0455 | -123.5865 | 123.2289 | 123.4936 | 123.3412 | 67.0399 | -123.6906
212.2656 | 123.7701 | -66.9983 | 56.488 | 0.06235 | -0.0045252 | 0.00053446 | 0.049185 | -0.0065769 | 0.049395 | 0.080738 | -0.0027857 | -0.004326 | 0.058464 | 0.026856 | 0.053479 | -67.0357 | 0.019721 | -66.92 | 56.4304 | 56.2067 | 56.2985 | -67.0481 | -66.9992 | 0.009516 | -67.1116 | 56.1985 | 56.4633 | 56.2971 | -67.166 | -0.049853 | -0.057641 | -0.037417 | 0.078312 | 0.12816 | -0.28138 | -0.18951 | -0.16769 | -0.28949 | -0.000923 | -0.11327 | 0.054424 | -0.02474 | -0.19095 | 123.4287 | 123.2049 | 123.2968 | 67.018 | -123.5362 | 123.1968 | 123.4616 | 123.2954 | 67.0078 | -123.654
213.2656 | 123.7518 | -67.0074 | 56.4926 | 0.06235 | -0.0034562 | -0.00053454 | 0.051322 | -0.0033719 | 0.048327 | 0.065477 | -0.0027857 | -0.004326 | 0.057395 | 0.025788 | 0.054547 | -67.0311 | 0.010564 | -66.9154 | 56.4258 | 56.2067 | 56.2985 | -67.0298 | -66.9946 | 0.014095 | -67.0978 | 56.194 | 56.4633 | 56.2834 | -67.1614 | -0.022383 | -0.066798 | -0.023683 | 0.092045 | 0.11443 | -0.28596 | -0.19409 | -0.15396 | -0.29865 | 0.012811 | -0.090375 | 0.063581 | -0.029318 | -0.20926 | 123.4333 | 123.2141 | 123.306 | 67.018 | -123.5224 | 123.2014 | 123.4707 | 123.2908 | 67.0215 | -123.654
214.2812 | 123.6786 | -67.0349 | 56.5338 | 0.06235 | -0.0034562 | -0.0016025 | 0.050254 | -0.0033719 | 0.047259 | 0.080738 | -0.0027857 | -0.006462 | 0.058464 | 0.025788 | 0.055616 | -67.0311 | 0.019721 | -66.9246 | 56.4258 | 56.2158 | 56.2985 | -67.0481 | -66.9992 | 0.014095 | -67.1024 | 56.1985 | 56.4633 | 56.3246 | -67.1568 | -0.013232 | -0.108 | 0.003783 | 0.11035 | 0.12359 | -0.318 | -0.23529 | -0.12191 | -0.33527 | 0.035698 | -0.067487 | 0.054424 | -0.070516 | -0.20925 | 123.4607 | 123.2507 | 123.3334 | 67.0546 | -123.582 | 123.2335 | 123.4982 | 123.3595 | 67.049 | -123.6906
215.2656 | 123.7244 | -66.9983 | 56.5063 | 0.092874 | -0.0034562 | 0.00053446 | 0.049185 | -0.0044409 | 0.048327 | 0.065477 | -0.0027857 | -0.003257 | 0.058464 | 0.027924 | 0.053479 | -67.0266 | 0.019721 | -66.9337 | 56.4212 | 56.2021 | 56.3031 | -67.0573 | -66.9946 | 0.014095 | -67.107 | 56.2123 | 56.4679 | 56.2925 | -67.1568 | -0.059011 | -0.085109 | -0.02826 | 0.064577 | 0.12359 | -0.30427 | -0.20324 | -0.15853 | -0.29407 | 0.003656 | -0.10869 | 0.049845 | -0.038472 | -0.21384 | 123.4195 | 123.2004 | 123.3014 | 67.018 | -123.5637 | 123.2106 | 123.4662 | 123.2908 | 67.0124 | -123.6632
216.2812 | 123.6603 | -67.0349 | 56.5384 | 0.06235 | -0.0034562 | -0.00053454 | 0.051322 | -0.0033719 | 0.049395 | 0.080738 | -0.0038537 | -0.004326 | 0.057395 | 0.026856 | 0.053479 | -67.0311 | 0.015142 | -66.9291 | 56.435 | 56.2112 | 56.3077 | -67.0619 | -66.9992 | 0.014095 | -67.1024 | 56.2031 | 56.4725 | 56.2788 | -67.1568 | -0.026969 | -0.10342 | 0.003783 | 0.10578 | 0.13274 | -0.32715 | -0.23071 | -0.12191 | -0.33527 | 0.035698 | -0.067487 | 0.054424 | -0.065937 | -0.25961 | 123.4699 | 123.2461 | 123.3426 | 67.0501 | -123.6003 | 123.238 | 123.5074 | 123.3137 | 67.049 | -123.6952
217.2656 | 123.7427 | -67.0029 | 56.4835 | 0.06235 | -0.0034562 | -0.00053454 | 0.050254 | -0.0044409 | 0.048327 | 0.050216 | -0.0017177 | -0.004326 | 0.057395 | 0.027924 | 0.053479 | -67.0311 | 0.010564 | -66.9337 | 56.4258 | 56.2067 | 56.2985 | -67.0527 | -66.9946 | 0.014095 | -67.107 | 56.1985 | 56.4587 | 56.3017 | -67.1568 | -0.049854 | -0.057642 | -0.02826 | 0.069155 | 0.11901 | -0.2768 | -0.18493 | -0.15395 | -0.28491 | 0.008234 | -0.10411 | 0.049845 | -0.024741 | -0.18179 | 123.4287 | 123.2095 | 123.3014 | 67.0134 | -123.5362 | 123.2014 | 123.4616 | 123.3045 | 67.017 | -123.6403
218.2812 | 123.7793 | -66.9937 | 56.4835 | 0.047088 | -0.0023882 | 0.00053446 | 0.051322 | -0.0033719 | 0.047259 | 0.050216 | -0.0027857 | -0.005394 | 0.058464 | 0.027924 | 0.054547 | -67.0311 | 0.015142 | -66.9246 | 56.4304 | 56.2067 | 56.3031 | -67.039 | -67.0038 | 0.009516 | -67.107 | 56.2031 | 56.4633 | 56.3246 | -67.1706 | -0.045274 | -0.053063 | -0.037416 | 0.069155 | 0.11443 | -0.2768 | -0.18036 | -0.17685 | -0.28034 | -0.010079 | -0.11326 | 0.063582 | -0.020162 | -0.1589 | 123.4241 | 123.2004 | 123.2968 | 67.0089 | -123.5224 | 123.1968 | 123.457 | 123.3183 | 67.0032 | -123.654
219.2812 | 123.8022 | -66.9662 | 56.4743 | 0.06235 | -0.0045252 | 0.0016025 | 0.050254 | -0.0044409 | 0.048327 | 0.065477 | -0.0027857 | -0.005394 | 0.058464 | 0.026856 | 0.053479 | -67.0357 | 0.005985 | -66.9291 | 56.4258 | 56.2021 | 56.3031 | -67.0436 | -66.9992 | 0.014095 | -67.107 | 56.2031 | 56.4725 | 56.3383 | -67.1568 | -0.077317 | -0.048487 | -0.06946 | 0.037112 | 0.11443 | -0.27222 | -0.1712 | -0.19058 | -0.27118 | -0.032966 | -0.14073 | 0.049845 | -0.00185 | -0.13601 | 123.3921 | 123.1683 | 123.2694 | 66.9722 | -123.5179 | 123.1694 | 123.4387 | 123.3045 | 66.9803 | -123.6311
220.2656 | 123.7335 | -66.9891 | 56.4926 | 0.047088 | -0.0023882 | -0.00053454 | 0.050254 | -0.0055089 | 0.049395 | 0.065477 | -0.0027857 | -0.006462 | 0.055259 | 0.028993 | 0.053479 | -67.0266 | 0.010564 | -66.9246 | 56.4304 | 56.2067 | 56.2985 | -67.0527 | -66.9946 | 0.009516 | -67.0978 | 56.1985 | 56.4725 | 56.3246 | -67.1568 | -0.063587 | -0.062219 | -0.037415 | 0.064578 | 0.12816 | -0.28596 | -0.19409 | -0.16769 | -0.29407 | -0.005499 | -0.10868 | 0.059002 | -0.020161 | -0.16805 | 123.4195 | 123.1958 | 123.2877 | 66.9997 | -123.5453 | 123.1877 | 123.4616 | 123.3137 | 66.9987 | -123.6494
221.2812 | 123.7793 | -66.9846 | 56.4926 | 0.06235 | -0.0034562 | 0.00053446 | 0.050254 | -0.0044409 | 0.048327 | 0.065477 | -0.0017177 | -0.004326 | 0.056327 | 0.027924 | 0.054547 | -67.0357 | 0.015142 | -66.9291 | 56.4304 | 56.2067 | 56.2985 | -67.0481 | -66.9946 | 0.004938 | -67.1024 | 56.194 | 56.4633 | 56.3062 | -67.1614 | -0.063586 | -0.062219 | -0.05115 | 0.055422 | 0.11901 | -0.28596 | -0.19409 | -0.17684 | -0.29865 | -0.010077 | -0.11784 | 0.059003 | -0.029318 | -0.18637 | 123.415 | 123.1912 | 123.2831 | 66.9997 | -123.5408 | 123.1785 | 123.4479 | 123.2908 | 66.9895 | -123.654
222.2812 | 123.8068 | -66.9708 | 56.5109 | 0.077612 | -0.0034562 | -0.0016025 | 0.050254 | -0.0055089 | 0.048327 | 0.065477 | -0.0017177 | -0.005394 | 0.056327 | 0.028993 | 0.053479 | -67.0311 | 0.015142 | -66.9246 | 56.4212 | 56.2067 | 56.2985 | -67.0665 | -66.9946 | 0.009516 | -67.1024 | 56.1985 | 56.4679 | 56.2971 | -67.1614 | -0.095635 | -0.089686 | -0.060304 | 0.046267 | 0.1419 | -0.30427 | -0.2124 | -0.19058 | -0.31238 | -0.02381 | -0.13157 | 0.059003 | -0.043049 | -0.21384 | 123.3921 | 123.1775 | 123.2694 | 66.986 | -123.5774 | 123.1694 | 123.4387 | 123.2679 | 66.9803 | -123.6723
223.2656 | 123.7198 | -67.0258 | 56.4789 | 0.047088 | -0.0034562 | -0.00053454 | 0.050254 | -0.0055089 | 0.047259 | 0.050216 | -0.0038537 | -0.005394 | 0.056327 | 0.027924 | 0.054547 | -67.0266 | 0.010564 | -66.9291 | 56.4258 | 56.2112 | 56.3031 | -67.0481 | -66.9946 | 0.004938 | -67.1116 | 56.1894 | 56.4679 | 56.3154 | -67.166 | -0.022387 | -0.053065 | -0.000794 | 0.096621 | 0.11901 | -0.26765 | -0.17578 | -0.14022 | -0.28949 | 0.031122 | -0.0858 | 0.054424 | -0.011006 | -0.16348 | 123.4516 | 123.237 | 123.3289 | 67.0363 | -123.527 | 123.2151 | 123.4936 | 123.3412 | 67.0307 | -123.6449
224.2812 | 123.8159 | -66.9525 | 56.5475 | 0.06235 | -0.0045252 | 0.00053446 | 0.049185 | -0.0044409 | 0.048327 | 0.050216 | -0.0027857 | -0.004326 | 0.058464 | 0.030061 | 0.052411 | -67.0311 | 0.019721 | -66.9291 | 56.4258 | 56.2158 | 56.2985 | -67.0573 | -67.0038 | 0.018674 | -67.107 | 56.194 | 56.4633 | 56.3017 | -67.166 | -0.10479 | -0.12173 | -0.078614 | 0.023379 | 0.12817 | -0.33173 | -0.24902 | -0.21347 | -0.35358 | -0.051277 | -0.15446 | 0.059003 | -0.084249 | -0.24588 | 123.3783 | 123.1683 | 123.251 | 66.9722 | -123.6048 | 123.1465 | 123.4158 | 123.2542 | 66.9712 | -123.7135
225.2656 | 123.7473 | -66.9891 | 56.4697 | 0.06235 | -0.0023882 | -0.0016025 | 0.048117 | -0.0055089 | 0.048327 | 0.080738 | -0.0027857 | -0.005394 | 0.056327 | 0.027924 | 0.052411 | -67.0266 | 0.0243 | -66.9246 | 56.4258 | 56.2067 | 56.2985 | -67.0481 | -66.9992 | 0.009516 | -67.107 | 56.2077 | 56.4725 | 56.265 | -67.1614 | -0.059008 | -0.04391 | -0.037415 | 0.064578 | 0.12359 | -0.26307 | -0.1712 | -0.17227 | -0.26203 | -0.010078 | -0.11784 | 0.054424 | 0.002727 | -0.20469 | 123.415 | 123.1958 | 123.2877 | 67.0134 | -123.5179 | 123.1968 | 123.4616 | 123.2542 | 66.9987 | -123.6311
226.2812 | 123.7701 | -66.9754 | 56.5063 | 0.077612 | -0.0055932 | 0.00053446 | 0.051322 | -0.0055089 | 0.047259 | 0.080738 | -0.0027857 | -0.005394 | 0.056327 | 0.028993 | 0.052411 | -67.0311 | 0.015142 | -66.9337 | 56.4258 | 56.2067 | 56.2939 | -67.0619 | -66.9901 | 0.018674 | -67.1116 | 56.2123 | 56.4679 | 56.2971 | -67.1568 | -0.086478 | -0.080531 | -0.055726 | 0.041689 | 0.12817 | -0.29969 | -0.2124 | -0.18142 | -0.29407 | -0.014653 | -0.13615 | 0.045266 | -0.038472 | -0.20926 | 123.4012 | 123.1821 | 123.2694 | 66.9905 | -123.5682 | 123.1877 | 123.4433 | 123.2725 | 66.9941 | -123.6632
227.2656 | 123.7839 | -67.012 | 56.4926 | 0.047088 | -0.0045252 | -0.00053454 | 0.051322 | -0.0055089 | 0.049395 | 0.065477 | -0.0027857 | -0.005394 | 0.056327 | 0.028993 | 0.053479 | -67.0266 | 0.019721 | -66.9291 | 56.4212 | 56.2158 | 56.2985 | -67.0481 | -66.9946 | 0.014095 | -67.1024 | 56.194 | 56.4633 | 56.2879 | -67.1522 | -0.03612 | -0.071376 | -0.014527 | 0.082888 | 0.11901 | -0.2768 | -0.19409 | -0.14022 | -0.29865 | 0.017389 | -0.090375 | 0.049845 | -0.029318 | -0.20468 | 123.4333 | 123.2278 | 123.3106 | 67.0317 | -123.5408 | 123.206 | 123.4753 | 123.3 | 67.0261 | -123.6449
228.2656 | 123.7244 | -66.9983 | 56.488 | 0.047088 | -0.0034562 | -0.00053454 | 0.049185 | -0.0055089 | 0.048327 | 0.050216 | -0.0027857 | -0.004326 | 0.055259 | 0.027924 | 0.053479 | -67.0311 | 0.010564 | -66.9291 | 56.4258 | 56.2112 | 56.2985 | -67.0436 | -66.9946 | 0.009516 | -67.1024 | 56.1985 | 56.4679 | 56.3108 | -67.166 | -0.045274 | -0.06222 | -0.032838 | 0.069155 | 0.11443 | -0.2768 | -0.18951 | -0.16769 | -0.28949 | 0.003656 | -0.10411 | 0.063582 | -0.020161 | -0.17721 | 123.4241 | 123.2095 | 123.2968 | 67.0089 | -123.5316 | 123.1968 | 123.4662 | 123.3091 | 67.0078 | -123.654
229.2656 | 123.7381 | -67.0166 | 56.4743 | 0.047088 | -0.0055932 | -0.00053454 | 0.049185 | -0.0055089 | 0.047259 | 0.034955 | -0.0027857 | -0.005394 | 0.056327 | 0.027924 | 0.052411 | -67.0266 | 0.005985 | -66.9246 | 56.435 | 56.2112 | 56.3031 | -67.0573 | -67.0038 | 0.009516 | -67.1161 | 56.194 | 56.4633 | 56.2467 | -67.166 | -0.0407 | -0.03933 | -0.009949 | 0.092044 | 0.13274 | -0.26307 | -0.1712 | -0.14938 | -0.28034 | 0.01281 | -0.099534 | 0.049845 | -0.011007 | -0.22758 | 123.4516 | 123.2278 | 123.3197 | 67.0226 | -123.5316 | 123.2106 | 123.4799 | 123.2633 | 67.0261 | -123.6403
230.2812 | 123.7885 | -66.9754 | 56.4926 | 0.06235 | -0.0023882 | -0.0016025 | 0.051322 | -0.0055089 | 0.047259 | 0.050216 | -0.0017177 | -0.005394 | 0.057395 | 0.028993 | 0.052411 | -67.0266 | 0.010564 | -66.9246 | 56.4258 | 56.2158 | 56.2985 | -67.0436 | -66.9992 | 0.018674 | -67.1116 | 56.1985 | 56.4679 | 56.3246 | -67.1614 | -0.068162 | -0.066798 | -0.051148 | 0.050845 | 0.11901 | -0.2768 | -0.19409 | -0.186 | -0.29407 | -0.023811 | -0.13615 | 0.049845 | -0.024739 | -0.16805 | 123.4012 | 123.1912 | 123.2739 | 66.986 | -123.5362 | 123.1739 | 123.4433 | 123.3 | 66.9941 | -123.654
231.2656 | 123.7839 | -66.9846 | 56.5109 | 0.047088 | -0.0045252 | 0.00053446 | 0.050254 | -0.0076459 | 0.049395 | 0.065477 | -0.0038537 | -0.005394 | 0.056327 | 0.027924 | 0.052411 | -67.0311 | 0.015142 | -66.9246 | 56.4304 | 56.2204 | 56.3031 | -67.039 | -66.9946 | 0.014095 | -67.1024 | 56.1985 | 56.4679 | 56.3062 | -67.1568 | -0.054429 | -0.080529 | -0.046571 | 0.06 | 0.11443 | -0.29053 | -0.20782 | -0.17226 | -0.31238 | -0.010077 | -0.11784 | 0.054424 | -0.043049 | -0.20468 | 123.415 | 123.205 | 123.2877 | 66.9997 | -123.5499 | 123.1831 | 123.4524 | 123.2908 | 66.9987 | -123.6677
232.2656 | 123.7793 | -67.0258 | 56.4606 | 0.06235 | -0.0045252 | -0.00053454 | 0.051322 | -0.0033719 | 0.04619 | 0.050216 | -0.0027857 | -0.003257 | 0.056327 | 0.032198 | 0.052411 | -67.0266 | 0.015142 | -66.9154 | 56.4304 | 56.2021 | 56.2985 | -67.0573 | -66.9901 | 0.014095 | -67.107 | 56.1985 | 56.4679 | 56.2925 | -67.166 | -0.031545 | -0.030175 | -0.000794 | 0.11036 | 0.1419 | -0.25849 | -0.16204 | -0.14022 | -0.26203 | 0.035701 | -0.081221 | 0.059003 | 0.007305 | -0.16806 | 123.4562 | 123.2278 | 123.3243 | 67.0409 | -123.5179 | 123.2243 | 123.4936 | 123.3183 | 67.0399 | -123.6266
233.2656 | 123.7885 | -66.9983 | 56.4514 | 0.06235 | -0.0034562 | -0.00053454 | 0.049185 | -0.0033719 | 0.04619 | 0.050216 | -0.0027857 | -0.004326 | 0.056327 | 0.030061 | 0.053479 | -67.0266 | 0.015142 | -66.9291 | 56.4304 | 56.2067 | 56.3031 | -67.0481 | -66.9946 | 0.009516 | -67.1024 | 56.194 | 56.4725 | 56.3154 | -67.1614 | -0.049853 | -0.02102 | -0.02826 | 0.069155 | 0.11901 | -0.24476 | -0.14831 | -0.16311 | -0.25745 | 0.003656 | -0.10411 | 0.059003 | 0.021038 | -0.13601 | 123.4287 | 123.2049 | 123.3014 | 67.0134 | -123.4996 | 123.1923 | 123.4707 | 123.3137 | 67.0078 | -123.6128
234.2812 | 123.7381 | -66.9983 | 56.4926 | 0.047088 | -0.0034562 | 0.00053446 | 0.050254 | -0.0055089 | 0.047259 | 0.080738 | -0.0038537 | -0.006462 | 0.057395 | 0.028993 | 0.052411 | -67.0357 | 0.019721 | -66.92 | 56.4258 | 56.2067 | 56.2939 | -67.0573 | -66.9992 | 0.014095 | -67.107 | 56.194 | 56.4725 | 56.3291 | -67.1614 | -0.059011 | -0.066798 | -0.037417 | 0.078312 | 0.13732 | -0.28596 | -0.19867 | -0.16311 | -0.29865 | -0.000923 | -0.10869 | 0.054424 | -0.020161 | -0.16347 | 123.4241 | 123.2049 | 123.2922 | 67.018 | -123.5499 | 123.1923 | 123.4707 | 123.3274 | 67.0124 | -123.654
235.2656 | 123.7198 | -66.9891 | 56.4697 | 0.077612 | -0.0045252 | -0.0016025 | 0.050254 | -0.0044409 | 0.048327 | 0.050216 | -0.0027857 | -0.006462 | 0.056327 | 0.030061 | 0.052411 | -67.0266 | 0.015142 | -66.92 | 56.4258 | 56.2158 | 56.2985 | -67.0665 | -66.9992 | 0.014095 | -67.1024 | 56.194 | 56.477 | 56.2925 | -67.166 | -0.077324 | -0.04391 | -0.037415 | 0.069157 | 0.14648 | -0.25391 | -0.1712 | -0.17685 | -0.27576 | -0.010078 | -0.11326 | 0.063582 | 0.007306 | -0.17722 | 123.415 | 123.205 | 123.2877 | 67.0043 | -123.5362 | 123.1831 | 123.4662 | 123.2816 | 67.0032 | -123.6357
236.2812 | 123.8068 | -66.9754 | 56.5018 | 0.06235 | -0.0055932 | -0.00053454 | 0.050254 | -0.0023039 | 0.047259 | 0.034955 | -0.0038537 | -0.003257 | 0.057395 | 0.027924 | 0.053479 | -67.0357 | 0.019721 | -66.9246 | 56.4304 | 56.2112 | 56.3031 | -67.039 | -66.9992 | 0.014095 | -67.1116 | 56.194 | 56.4725 | 56.3062 | -67.1522 | -0.063584 | -0.071374 | -0.060305 | 0.050845 | 0.11443 | -0.29053 | -0.19867 | -0.17684 | -0.3078 | -0.023811 | -0.13615 | 0.040687 | -0.029316 | -0.19552 | 123.4058 | 123.1866 | 123.2785 | 66.9951 | -123.5408 | 123.1694 | 123.4479 | 123.2816 | 66.9895 | -123.654
237.2656 | 123.7198 | -67.012 | 56.4697 | 0.047088 | -0.0055932 | -0.0016025 | 0.050254 | -0.0044409 | 0.048327 | 0.065477 | -0.0038537 | -0.004326 | 0.055259 | 0.031129 | 0.053479 | -67.0266 | 0.015142 | -66.9246 | 56.4212 | 56.2067 | 56.3031 | -67.0481 | -66.9901 | 0.004938 | -67.1024 | 56.194 | 56.477 | 56.3154 | -67.1614 | -0.03612 | -0.048488 | -0.014527 | 0.087466 | 0.12359 | -0.26307 | -0.16662 | -0.14938 | -0.27576 | 0.021968 | -0.090375 | 0.059003 | 0.007306 | -0.15432 | 123.4333 | 123.2187 | 123.3151 | 67.0272 | -123.5179 | 123.206 | 123.4891 | 123.3274 | 67.017 | -123.6311
238.2812 | 123.7198 | -67.0029 | 56.4835 | 0.047088 | -0.0045252 | -0.0016025 | 0.049185 | -0.0044409 | 0.047259 | 0.050216 | -0.0038537 | -0.002189 | 0.057395 | 0.028993 | 0.052411 | -67.0266 | 0.015142 | -66.92 | 56.4212 | 56.2067 | 56.3031 | -67.039 | -66.9992 | 0.018674 | -67.107 | 56.194 | 56.4587 | 56.3062 | -67.1614 | -0.036118 | -0.06222 | -0.023682 | 0.08289 | 0.11901 | -0.2768 | -0.18036 | -0.15853 | -0.28949 | 0.003655 | -0.10411 | 0.054424 | -0.024741 | -0.17721 | 123.4241 | 123.2095 | 123.306 | 67.018 | -123.5224 | 123.1968 | 123.4616 | 123.3091 | 67.0215 | -123.6449
239.2812 | 123.7885 | -66.9891 | 56.5018 | 0.047088 | -0.0055932 | -0.0016025 | 0.050254 | -0.0055089 | 0.048327 | 0.050216 | -0.0027857 | -0.004326 | 0.056327 | 0.031129 | 0.052411 | -67.0403 | 0.010564 | -66.9246 | 56.4212 | 56.1975 | 56.3077 | -67.0665 | -66.9855 | 0.009516 | -67.0978 | 56.1985 | 56.4679 | 56.32 | -67.1568 | -0.077324 | -0.080531 | -0.05115 | 0.064578 | 0.1419 | -0.30427 | -0.19409 | -0.16769 | -0.30322 | 0.003658 | -0.10868 | 0.059002 | -0.033894 | -0.18179 | 123.4104 | 123.1866 | 123.2968 | 66.9997 | -123.5682 | 123.1877 | 123.457 | 123.3091 | 66.9987 | -123.6586
240.2656 | 123.7793 | -67.0212 | 56.4743 | 0.047088 | -0.0034562 | -0.0016025 | 0.049185 | -0.0044409 | 0.047259 | 0.065477 | -0.0038537 | -0.006462 | 0.057395 | 0.031129 | 0.053479 | -67.0357 | 0.015142 | -66.9246 | 56.4258 | 56.2112 | 56.3077 | -67.0481 | -66.9946 | 0.018674 | -67.1024 | 56.1848 | 56.4725 | 56.3062 | -67.166 | -0.026965 | -0.048487 | -0.014529 | 0.096621 | 0.12359 | -0.26307 | -0.16662 | -0.1448 | -0.28949 | 0.026544 | -0.08122 | 0.063582 | -0.00185 | -0.16806 | 123.447 | 123.2324 | 123.3289 | 67.0363 | -123.5224 | 123.206 | 123.4936 | 123.3274 | 67.0399 | -123.6403
241.2656 | 123.7473 | -67.012 | 56.5063 | 0.077612 | -0.0034562 | 0.00053446 | 0.050254 | -0.0033719 | 0.047259 | 0.065477 | -0.0027857 | -0.005394 | 0.055259 | 0.031129 | 0.052411 | -67.0266 | 0.010564 | -66.9291 | 56.4121 | 56.2021 | 56.3031 | -67.0573 | -66.9992 | 0.014095 | -67.0978 | 56.1894 | 56.4679 | 56.3291 | -67.1614 | -0.045278 | -0.094266 | -0.014527 | 0.082888 | 0.12817 | -0.30427 | -0.20324 | -0.14938 | -0.31696 | 0.01281 | -0.085797 | 0.063581 | -0.038472 | -0.17721 | 123.4241 | 123.2141 | 123.3151 | 67.0226 | -123.5637 | 123.2014 | 123.4799 | 123.3412 | 67.0261 | -123.6677
242.2656 | 123.7473 | -67.0166 | 56.5018 | 0.047088 | -0.0055932 | -0.0016025 | 0.050254 | -0.0044409 | 0.04619 | 0.11126 | -0.0038537 | -0.004326 | 0.056327 | 0.030061 | 0.053479 | -67.0266 | 0.010564 | -66.92 | 56.4258 | 56.1929 | 56.3031 | -67.0436 | -66.9992 | 0.014095 | -67.107 | 56.1985 | 56.4725 | 56.3062 | -67.166 | -0.026963 | -0.075953 | -0.009949 | 0.096623 | 0.12359 | -0.30885 | -0.19867 | -0.14938 | -0.30322 | 0.017388 | -0.090376 | 0.059003 | -0.029316 | -0.19552 | 123.4424 | 123.2095 | 123.3197 | 67.0272 | -123.5453 | 123.2151 | 123.4891 | 123.3228 | 67.0307 | -123.6678
243.2656 | 123.7885 | -67.0166 | 56.4789 | 0.047088 | -0.0066612 | -0.0016025 | 0.048117 | -0.0055089 | 0.048327 | 0.065477 | -0.0038537 | -0.006462 | 0.054191 | 0.028993 | 0.052411 | -67.0266 | 0.010564 | -66.9246 | 56.4212 | 56.2067 | 56.2985 | -67.0436 | -66.9992 | 0.014095 | -67.107 | 56.1894 | 56.4725 | 56.2971 | -67.1522 | -0.026963 | -0.057643 | -0.009949 | 0.092044 | 0.11901 | -0.27222 | -0.18036 | -0.13564 | -0.28949 | 0.017388 | -0.090376 | 0.045266 | -0.006428 | -0.18179 | 123.4378 | 123.2233 | 123.3151 | 67.0272 | -123.5224 | 123.206 | 123.4891 | 123.3137 | 67.0307 | -123.6311
244.2812 | 123.6557 | -66.9937 | 56.5338 | 0.077612 | -0.0045252 | 0.00053446 | 0.047048 | -0.0087139 | 0.047259 | 0.080738 | -0.0059907 | -0.005394 | 0.057395 | 0.031129 | 0.051343 | -67.0266 | 0.015142 | -66.9246 | 56.4304 | 56.2067 | 56.3077 | -67.0481 | -66.9946 | 0.018674 | -67.1024 | 56.2031 | 56.4725 | 56.2834 | -67.1614 | -0.054431 | -0.10342 | -0.032838 | 0.069155 | 0.12359 | -0.32716 | -0.22613 | -0.16769 | -0.33069 | -0.000922 | -0.10869 | 0.059003 | -0.061359 | -0.25046 | 123.4241 | 123.2004 | 123.3014 | 67.0089 | -123.582 | 123.1968 | 123.4662 | 123.2771 | 67.0124 | -123.6952
245.2656 | 123.7106 | -67.0395 | 56.4743 | 0.031826 | -0.0066612 | -0.0016025 | 0.050254 | -0.0044409 | 0.04619 | 0.080738 | -0.0038537 | -0.005394 | 0.056327 | 0.032198 | 0.052411 | -67.022 | 0.005985 | -66.92 | 56.4212 | 56.2067 | 56.3031 | -67.0481 | -67.0084 | 0.009516 | -67.1024 | 56.1985 | 56.4725 | 56.3246 | -67.1706 | -0.008654 | -0.053065 | 0.017518 | 0.11951 | 0.12816 | -0.26765 | -0.1712 | -0.13107 | -0.27576 | 0.031119 | -0.062909 | 0.068161 | -0.00185 | -0.14974 | 123.4607 | 123.2461 | 123.3426 | 67.0455 | -123.5224 | 123.238 | 123.5119 | 123.3641 | 67.049 | -123.6449
246.2812 | 123.7427 | -67.0212 | 56.488 | 0.047088 | -0.0045252 | -0.00053454 | 0.050254 | -0.0044409 | 0.04619 | 0.080738 | -0.0038537 | -0.003257 | 0.055259 | 0.031129 | 0.053479 | -67.0266 | 0.019721 | -66.92 | 56.435 | 56.2112 | 56.2985 | -67.0481 | -66.9992 | 0.014095 | -67.0978 | 56.194 | 56.4725 | 56.32 | -67.166 | -0.026965 | -0.053063 | -0.005372 | 0.1012 | 0.12816 | -0.2768 | -0.18951 | -0.1448 | -0.29407 | 0.021965 | -0.076642 | 0.06816 | -0.015583 | -0.16805 | 123.4562 | 123.2324 | 123.3197 | 67.0409 | -123.5362 | 123.2151 | 123.4936 | 123.3412 | 67.0353 | -123.654
247.2656 | 123.7747 | -67.0166 | 56.4606 | 0.06235 | -0.0066612 | -0.0037395 | 0.049185 | -0.0044409 | 0.048327 | 0.050216 | -0.0027857 | -0.006462 | 0.055259 | 0.031129 | 0.050274 | -67.022 | 0.010564 | -66.9291 | 56.4304 | 56.2021 | 56.2939 | -67.0527 | -66.9992 | 0.014095 | -67.1024 | 56.194 | 56.4725 | 56.3246 | -67.1568 | -0.036121 | -0.030175 | -0.00537 | 0.087466 | 0.12359 | -0.25849 | -0.16662 | -0.14022 | -0.2666 | 0.017388 | -0.085797 | 0.054424 | 0.011883 | -0.13601 | 123.447 | 123.2187 | 123.3105 | 67.0272 | -123.5133 | 123.2106 | 123.4891 | 123.3412 | 67.0307 | -123.6174
248.2656 | 123.7976 | -67.012 | 56.456 | 0.06235 | -0.0045252 | -0.0016025 | 0.050254 | -0.0044409 | 0.047259 | 0.050216 | -0.0027857 | -0.004326 | 0.057395 | 0.032198 | 0.053479 | -67.022 | 0.015142 | -66.92 | 56.4304 | 56.2067 | 56.3031 | -67.0527 | -66.9992 | 0.009516 | -67.0978 | 56.1985 | 56.4816 | 56.2834 | -67.166 | -0.040699 | -0.025598 | -0.009948 | 0.092045 | 0.13274 | -0.24934 | -0.15289 | -0.15396 | -0.25745 | 0.01281 | -0.085797 | 0.06816 | 0.025617 | -0.17264 | 123.4424 | 123.2187 | 123.3151 | 67.0272 | -123.5087 | 123.2106 | 123.4936 | 123.2954 | 67.0215 | -123.622
249.2812 | 123.7381 | -66.9983 | 56.488 | 0.06235 | -0.0023882 | 0.00053446 | 0.050254 | -0.0055089 | 0.04619 | 0.065477 | -0.0038537 | -0.004326 | 0.054191 | 0.031129 | 0.051343 | -67.0266 | 0.019721 | -66.9291 | 56.4212 | 56.2067 | 56.3031 | -67.0619 | -66.9946 | 0.004938 | -67.1024 | 56.194 | 56.4725 | 56.32 | -67.1614 | -0.06359 | -0.066798 | -0.02826 | 0.069155 | 0.13274 | -0.28138 | -0.18493 | -0.16311 | -0.29407 | 0.003656 | -0.10411 | 0.059003 | -0.015583 | -0.16805 | 123.4195 | 123.2049 | 123.3014 | 67.018 | -123.5499 | 123.1923 | 123.4707 | 123.3183 | 67.0032 | -123.6494
250.2812 | 123.7289 | -67.0166 | 56.4743 | 0.06235 | -0.0055932 | -0.00053454 | 0.047048 | -0.0044409 | 0.045122 | 0.080738 | -0.0038537 | -0.005394 | 0.054191 | 0.031129 | 0.052411 | -67.0266 | 0.015142 | -66.9246 | 56.4212 | 56.2067 | 56.3031 | -67.0527 | -66.9946 | 0.014095 | -67.0978 | 56.1894 | 56.477 | 56.3108 | -67.166 | -0.036121 | -0.053065 | -0.009949 | 0.092044 | 0.12816 | -0.26765 | -0.1712 | -0.14938 | -0.28492 | 0.021967 | -0.081219 | 0.06816 | 0.002729 | -0.16348 | 123.4378 | 123.2233 | 123.3197 | 67.0317 | -123.527 | 123.206 | 123.4936 | 123.3274 | 67.0307 | -123.6403
251.2812 | 123.7381 | -67.0395 | 56.4926 | 0.047088 | -0.0045252 | -0.0016025 | 0.048117 | -0.0055089 | 0.047259 | 0.065477 | -0.0027857 | -0.005394 | 0.054191 | 0.031129 | 0.050274 | -67.0311 | 0.015142 | -66.9154 | 56.4167 | 56.2067 | 56.3031 | -67.0481 | -66.9992 | 0.014095 | -67.1024 | 56.194 | 56.477 | 56.3246 | -67.166 | -0.008654 | -0.075954 | 0.008361 | 0.12409 | 0.13274 | -0.28596 | -0.18951 | -0.12649 | -0.29865 | 0.040276 | -0.062909 | 0.063582 | -0.015582 | -0.16805 | 123.4562 | 123.2461 | 123.3426 | 67.0546 | -123.5408 | 123.2335 | 123.5165 | 123.3641 | 67.0536 | -123.6586
252.2656 | 123.7289 | -67.0074 | 56.488 | 0.06235 | -0.0055932 | -0.00053454 | 0.048117 | -0.0044409 | 0.047259 | 0.065477 | -0.0038537 | -0.004326 | 0.057395 | 0.032198 | 0.051343 | -67.0128 | 0.019721 | -66.92 | 56.4258 | 56.2067 | 56.3031 | -67.0527 | -66.9992 | 0.014095 | -67.1024 | 56.1894 | 56.477 | 56.3062 | -67.166 | -0.045277 | -0.06222 | -0.00537 | 0.087467 | 0.13274 | -0.28138 | -0.18493 | -0.15854 | -0.29865 | 0.008232 | -0.094953 | 0.063582 | -0.011004 | -0.18179 | 123.4333 | 123.2141 | 123.3106 | 67.0272 | -123.5408 | 123.1968 | 123.4845 | 123.3137 | 67.0215 | -123.654
253.2656 | 123.7198 | -67.0395 | 56.5063 | 0.077612 | -0.0045252 | -0.0016025 | 0.048117 | -0.0055089 | 0.048327 | 0.050216 | -0.0038537 | -0.005394 | 0.055259 | 0.034335 | 0.052411 | -67.0266 | 0.015142 | -66.92 | 56.4304 | 56.2067 | 56.3077 | -67.039 | -66.9992 | 0.014095 | -67.1024 | 56.194 | 56.4679 | 56.3017 | -67.166 | 0.000503 | -0.075952 | 0.012939 | 0.11951 | 0.11901 | -0.29969 | -0.19867 | -0.12649 | -0.31238 | 0.040276 | -0.062909 | 0.063582 | -0.038472 | -0.20468 | 123.4699 | 123.2461 | 123.3472 | 67.0546 | -123.5453 | 123.2335 | 123.5074 | 123.3412 | 67.0536 | -123.6723
254.2812 | 123.7793 | -67.0029 | 56.488 | 0.06235 | -0.0045252 | -0.0016025 | 0.047048 | -0.0044409 | 0.047259 | 0.080738 | -0.0038537 | -0.006462 | 0.055259 | 0.032198 | 0.052411 | -67.0266 | 0.015142 | -66.9246 | 56.4258 | 56.2112 | 56.3077 | -67.0527 | -66.9946 | 0.014095 | -67.1024 | 56.194 | 56.4725 | 56.3154 | -67.1706 | -0.049854 | -0.06222 | -0.023682 | 0.078311 | 0.12816 | -0.2768 | -0.18035 | -0.16769 | -0.29407 | 0.008234 | -0.09953 | 0.068161 | -0.015583 | -0.17263 | 123.4287 | 123.2141 | 123.3106 | 67.018 | -123.5408 | 123.1968 | 123.4753 | 123.3183 | 67.017 | -123.6586
255.2656 | 123.7427 | -66.9846 | 56.5109 | 0.06235 | -0.0045252 | -0.0016025 | 0.048117 | -0.0044409 | 0.04619 | 0.080738 | -0.0038537 | -0.004326 | 0.055259 | 0.033266 | 0.052411 | -67.0266 | 0.010564 | -66.9246 | 56.4304 | 56.2112 | 56.3077 | -67.0481 | -66.9992 | 0.014095 | -67.107 | 56.1985 | 56.4725 | 56.3246 | -67.166 | -0.063586 | -0.080529 | -0.041993 | 0.06 | 0.12359 | -0.29969 | -0.20324 | -0.18142 | -0.31238 | -0.014656 | -0.12242 | 0.059003 | -0.038471 | -0.18636 | 123.415 | 123.1958 | 123.2922 | 66.9951 | -123.5591 | 123.1831 | 123.457 | 123.3091 | 66.9987 | -123.6769
256.2656 | 123.6923 | -67.0349 | 56.5338 | 0.077612 | -0.0066612 | 0.00053446 | 0.048117 | -0.0033719 | 0.047259 | 0.080738 | -0.0038537 | -0.005394 | 0.055259 | 0.033266 | 0.051343 | -67.0266 | 0.015142 | -66.9154 | 56.4304 | 56.2112 | 56.3077 | -67.0481 | -66.9992 | 0.009516 | -67.0932 | 56.1985 | 56.4679 | 56.3291 | -67.1614 | -0.013232 | -0.10342 | 0.008361 | 0.11951 | 0.13274 | -0.32258 | -0.22613 | -0.12649 | -0.33527 | 0.035698 | -0.05833 | 0.06816 | -0.065937 | -0.20467 | 123.4653 | 123.2461 | 123.3426 | 67.0501 | -123.582 | 123.2335 | 123.5028 | 123.3641 | 67.0444 | -123.6952
257.2656 | 123.7244 | -67.0395 | 56.4651 | 0.06235 | -0.0055932 | -0.0016025 | 0.049185 | -0.0044409 | 0.047259 | 0.050216 | -0.0038537 | -0.005394 | 0.055259 | 0.034335 | 0.050274 | -67.022 | 0.015142 | -66.92 | 56.4212 | 56.2067 | 56.3077 | -67.0298 | -66.9946 | 0.014095 | -67.0978 | 56.1894 | 56.4679 | 56.2879 | -67.1568 | 0.009661 | -0.04391 | 0.017518 | 0.11951 | 0.10985 | -0.25849 | -0.15747 | -0.11733 | -0.27576 | 0.044855 | -0.058331 | 0.059002 | 0.002727 | -0.17722 | 123.4607 | 123.2461 | 123.3472 | 67.0546 | -123.495 | 123.2289 | 123.5074 | 123.3274 | 67.0536 | -123.622
258.2656 | 123.8068 | -67.012 | 56.4606 | 0.06235 | -0.0034562 | -0.00053454 | 0.049185 | -0.0044409 | 0.047259 | 0.065477 | -0.0049217 | -0.004326 | 0.056327 | 0.034335 | 0.052411 | -67.0266 | 0.015142 | -66.92 | 56.4258 | 56.1975 | 56.3031 | -67.0665 | -66.9901 | 0.009516 | -67.1024 | 56.1894 | 56.4725 | 56.2788 | -67.166 | -0.054436 | -0.034754 | -0.014527 | 0.092045 | 0.14648 | -0.26307 | -0.15747 | -0.15396 | -0.27118 | 0.021968 | -0.090375 | 0.063582 | 0.011883 | -0.1818 | 123.4378 | 123.2095 | 123.3151 | 67.0272 | -123.527 | 123.2014 | 123.4845 | 123.2908 | 67.0215 | -123.6266
259.2656 | 123.7152 | -67.0166 | 56.4972 | 0.016564 | -0.0034562 | -0.0026705 | 0.04598 | -0.0033719 | 0.04619 | 0.065477 | -0.0038537 | -0.003257 | 0.057395 | 0.034335 | 0.051343 | -67.0311 | 0.015142 | -66.92 | 56.4258 | 56.2067 | 56.3168 | -67.0436 | -66.9946 | 0.014095 | -67.1024 | 56.1894 | 56.4679 | 56.2971 | -67.166 | -0.026963 | -0.071375 | -0.014527 | 0.096623 | 0.12359 | -0.29053 | -0.18035 | -0.14938 | -0.3078 | 0.021967 | -0.085797 | 0.063582 | -0.029316 | -0.2001 | 123.4424 | 123.2233 | 123.3334 | 67.0317 | -123.5408 | 123.206 | 123.4845 | 123.3137 | 67.0307 | -123.6632
260.2656 | 123.7289 | -67.0303 | 56.4835 | 0.06235 | -0.0045252 | -0.00053454 | 0.048117 | -0.0044409 | 0.048327 | 0.065477 | -0.0038537 | -0.003257 | 0.056327 | 0.034335 | 0.051343 | -67.0266 | 0.015142 | -66.9291 | 56.4258 | 56.2112 | 56.3168 | -67.0573 | -66.9946 | 0.014095 | -67.107 | 56.1894 | 56.4679 | 56.3108 | -67.1706 | -0.026968 | -0.057642 | 0.003783 | 0.1012 | 0.12817 | -0.27222 | -0.16662 | -0.14023 | -0.29407 | 0.035699 | -0.076644 | 0.063582 | -0.015583 | -0.17263 | 123.4562 | 123.2416 | 123.3472 | 67.0455 | -123.5408 | 123.2197 | 123.4982 | 123.3412 | 67.0444 | -123.654
261.2656 | 123.6969 | -67.0441 | 56.4789 | 0.06235 | -0.0066612 | -0.0026705 | 0.048117 | -0.0044409 | 0.047259 | 0.034955 | -0.0038537 | -0.005394 | 0.058464 | 0.034335 | 0.051343 | -67.0266 | 0.015142 | -66.9246 | 56.4304 | 56.2067 | 56.3123 | -67.0481 | -66.9946 | 0.014095 | -67.0978 | 56.194 | 56.4679 | 56.3062 | -67.1614 | -0.004077 | -0.048486 | 0.017516 | 0.11951 | 0.12359 | -0.27222 | -0.16662 | -0.11733 | -0.28491 | 0.049432 | -0.053754 | 0.063581 | -0.011006 | -0.17263 | 123.4745 | 123.2507 | 123.3563 | 67.0592 | -123.527 | 123.238 | 123.5119 | 123.3503 | 67.0582 | -123.6403
262.2656 | 123.7198 | -66.9983 | 56.4377 | 0.06235 | -0.0045252 | -0.0026705 | 0.047048 | -0.0044409 | 0.047259 | 0.050216 | -0.0027857 | -0.004326 | 0.056327 | 0.036471 | 0.051343 | -67.0311 | 0.015142 | -66.92 | 56.4304 | 56.2021 | 56.3077 | -67.0436 | -66.9901 | 0.009516 | -67.1024 | 56.1848 | 56.4679 | 56.2742 | -67.166 | -0.045274 | -0.007287 | -0.032838 | 0.078312 | 0.12359 | -0.2356 | -0.13 | -0.16769 | -0.25287 | 0.008235 | -0.10411 | 0.063582 | 0.030193 | -0.16349 | 123.4287 | 123.2004 | 123.306 | 67.0134 | -123.4812 | 123.1831 | 123.4662 | 123.2725 | 67.0078 | -123.6037
263.2656 | 123.7793 | -66.9754 | 56.4697 | 0.047088 | -0.0055932 | -0.0026705 | 0.048117 | -0.0044409 | 0.04619 | 0.050216 | -0.0049217 | -0.004326 | 0.056327 | 0.035403 | 0.051343 | -67.0266 | 0.010564 | -66.92 | 56.4258 | 56.2112 | 56.3123 | -67.0436 | -66.9992 | 0.004938 | -67.0978 | 56.194 | 56.4679 | 56.2971 | -67.1706 | -0.068162 | -0.04391 | -0.051148 | 0.055424 | 0.12359 | -0.25849 | -0.15747 | -0.19516 | -0.27576 | -0.023811 | -0.12242 | 0.072739 | -0.001851 | -0.17264 | 123.4012 | 123.1866 | 123.2877 | 66.986 | -123.5133 | 123.1694 | 123.4433 | 123.2725 | 66.9803 | -123.6403
264.2812 | 123.7427 | -66.9983 | 56.5155 | 0.047088 | -0.0023882 | -0.0016025 | 0.048117 | -0.0033719 | 0.047259 | 0.080738 | -0.0038537 | -0.004326 | 0.055259 | 0.033266 | 0.051343 | -67.0266 | 0.015142 | -66.92 | 56.4258 | 56.2067 | 56.3123 | -67.0436 | -66.9901 | 0.009516 | -67.1024 | 56.194 | 56.4725 | 56.2788 | -67.166 | -0.045274 | -0.089686 | -0.02826 | 0.078312 | 0.12359 | -0.30885 | -0.20324 | -0.16769 | -0.32154 | 0.008235 | -0.10411 | 0.063582 | -0.043049 | -0.23673 | 123.4241 | 123.2049 | 123.3106 | 67.0134 | -123.5591 | 123.1923 | 123.4707 | 123.2771 | 67.0078 | -123.6815
265.2656 | 123.7564 | -67.0212 | 56.4743 | 0.031826 | -0.0023882 | -0.0016025 | 0.048117 | -0.0065769 | 0.049395 | 0.050216 | -0.0017177 | -0.004326 | 0.055259 | 0.034335 | 0.051343 | -67.0174 | 0.019721 | -66.9246 | 56.4304 | 56.2067 | 56.3077 | -67.0436 | -66.9901 | 0.009516 | -67.1024 | 56.1802 | 56.4679 | 56.3154 | -67.166 | -0.022386 | -0.043908 | 0.003785 | 0.096621 | 0.11901 | -0.26765 | -0.16662 | -0.1448 | -0.29407 | 0.031123 | -0.08122 | 0.063582 | -0.006428 | -0.1589 | 123.4516 | 123.2278 | 123.3289 | 67.0409 | -123.5179 | 123.2014 | 123.4891 | 123.3366 | 67.0307 | -123.6403
266.2656 | 123.7747 | -66.9891 | 56.4835 | 0.047088 | -0.0055932 | -0.0016025 | 0.048117 | -0.0033719 | 0.04619 | 0.080738 | -0.0027857 | -0.003257 | 0.057395 | 0.033266 | 0.049206 | -67.0266 | 0.005985 | -66.92 | 56.4304 | 56.2067 | 56.3077 | -67.0527 | -66.9946 | 0.018674 | -67.0978 | 56.1985 | 56.4725 | 56.2971 | -67.1706 | -0.063587 | -0.053063 | -0.037415 | 0.069157 | 0.13274 | -0.2768 | -0.17578 | -0.18142 | -0.28491 | -0.005499 | -0.10868 | 0.072739 | -0.011005 | -0.18637 | 123.4195 | 123.1958 | 123.2968 | 66.9951 | -123.5362 | 123.1877 | 123.4616 | 123.2862 | 67.0078 | -123.654
267.2656 | 123.7701 | -66.9983 | 56.4743 | 0.047088 | -0.0034562 | -0.0026705 | 0.047048 | -0.0033719 | 0.04619 | 0.080738 | -0.0038537 | -0.005394 | 0.057395 | 0.035403 | 0.051343 | -67.022 | 0.010564 | -66.9246 | 56.4258 | 56.2112 | 56.3031 | -67.0527 | -66.9946 | 0.014095 | -67.1024 | 56.194 | 56.4725 | 56.3246 | -67.166 | -0.054432 | -0.048487 | -0.023681 | 0.073733 | 0.12816 | -0.26307 | -0.1712 | -0.16769 | -0.28034 | 0.003656 | -0.10411 | 0.063582 | -0.00185 | -0.14974 | 123.4241 | 123.2095 | 123.3014 | 67.0089 | -123.527 | 123.1923 | 123.4707 | 123.3229 | 67.0124 | -123.6403
268.2656 | 123.6877 | -67.0395 | 56.4926 | 0.047088 | -0.0045252 | -0.0016025 | 0.048117 | -0.0044409 | 0.045122 | 0.065477 | -0.0049217 | -0.004326 | 0.055259 | 0.035403 | 0.051343 | -67.022 | 0.015142 | -66.9246 | 56.4258 | 56.2021 | 56.3031 | -67.0527 | -66.9946 | 0.014095 | -67.0978 | 56.1848 | 56.4679 | 56.2971 | -67.1706 | -0.013233 | -0.066798 | 0.017518 | 0.11493 | 0.12816 | -0.29054 | -0.18951 | -0.13107 | -0.30781 | 0.044855 | -0.058331 | 0.072739 | -0.024739 | -0.19553 | 123.4653 | 123.2416 | 123.3426 | 67.0546 | -123.5453 | 123.2243 | 123.5074 | 123.3366 | 67.0536 | -123.6632
269.2812 | 123.7289 | -66.9983 | 56.4926 | 0.047088 | -0.0055932 | -0.0026705 | 0.047048 | -0.0033719 | 0.045122 | 0.065477 | -0.0038537 | -0.004326 | 0.053122 | 0.036471 | 0.050274 | -67.0266 | 0.019721 | -66.92 | 56.4258 | 56.1883 | 56.3077 | -67.0481 | -66.9901 | 0.009516 | -67.0978 | 56.194 | 56.4679 | 56.2925 | -67.166 | -0.049853 | -0.066798 | -0.02826 | 0.078312 | 0.12816 | -0.30427 | -0.18493 | -0.16769 | -0.29865 | 0.008235 | -0.09953 | 0.06816 | -0.024739 | -0.2001 | 123.4241 | 123.1866 | 123.306 | 67.018 | -123.5408 | 123.1923 | 123.4662 | 123.2908 | 67.0078 | -123.6586
270.2656 | 123.7473 | -67.0029 | 56.4789 | 0.047088 | -0.0045252 | -0.0016025 | 0.04598 | -0.0044409 | 0.048327 | 0.050216 | -0.0038537 | -0.004326 | 0.056327 | 0.034335 | 0.049206 | -67.0266 | 0.015142 | -66.92 | 56.4258 | 56.1929 | 56.3031 | -67.039 | -66.9946 | 0.018674 | -67.1024 | 56.2031 | 56.4679 | 56.3062 | -67.1614 | -0.036118 | -0.053065 | -0.023682 | 0.08289 | 0.11901 | -0.28596 | -0.17578 | -0.15853 | -0.27576 | 0.008234 | -0.09953 | 0.059003 | -0.011006 | -0.17263 | 123.4287 | 123.1958 | 123.306 | 67.018 | -123.5179 | 123.206 | 123.4707 | 123.3091 | 67.0215 | -123.6403
271.2656 | 123.7976 | -66.98 | 56.456 | 0.06235 | -0.0045252 | -0.0026705 | 0.04598 | -0.0065769 | 0.045122 | 0.065477 | -0.0038537 | -0.004326 | 0.055259 | 0.034335 | 0.050274 | -67.022 | 0.015142 | -66.92 | 56.4258 | 56.2067 | 56.3077 | -67.0436 | -66.9901 | 0.009516 | -67.0978 | 56.1848 | 56.4633 | 56.2971 | -67.166 | -0.063585 | -0.030177 | -0.041992 | 0.060001 | 0.12359 | -0.24934 | -0.14831 | -0.186 | -0.27118 | -0.010076 | -0.11784 | 0.06816 | 0.007303 | -0.1589 | 123.4058 | 123.1866 | 123.2877 | 66.9951 | -123.4996 | 123.1648 | 123.4433 | 123.2771 | 66.9895 | -123.622
272.2656 | 123.6786 | -67.0258 | 56.5567 | 0.047088 | -0.0055932 | -0.0016025 | 0.047048 | -0.0065769 | 0.047259 | 0.080738 | -0.0038537 | -0.005394 | 0.055259 | 0.035403 | 0.051343 | -67.0266 | 0.010564 | -66.9291 | 56.4304 | 56.2021 | 56.3077 | -67.0527 | -66.9992 | 0.023253 | -67.0978 | 56.1894 | 56.4679 | 56.3017 | -67.1751 | -0.026966 | -0.12631 | -0.000794 | 0.096621 | 0.12359 | -0.35462 | -0.24902 | -0.14938 | -0.36731 | 0.026543 | -0.072064 | 0.077317 | -0.088826 | -0.25503 | 123.4562 | 123.2278 | 123.3334 | 67.0363 | -123.6094 | 123.2151 | 123.4936 | 123.3274 | 67.049 | -123.7318
273.2656 | 123.6465 | -67.0349 | 56.488 | 0.06235 | -0.0055932 | -0.0037395 | 0.048117 | -0.0033719 | 0.04619 | 0.080738 | -0.0038537 | -0.004326 | 0.055259 | 0.035403 | 0.049206 | -67.022 | 0.0243 | -66.92 | 56.4258 | 56.1975 | 56.3123 | -67.0436 | -66.9946 | 0.018674 | -67.1024 | 56.194 | 56.4633 | 56.2696 | -67.1614 | -0.008653 | -0.06222 | 0.01294 | 0.11493 | 0.12359 | -0.29054 | -0.17578 | -0.12649 | -0.29407 | 0.040277 | -0.067487 | 0.059003 | -0.02474 | -0.21842 | 123.4607 | 123.2324 | 123.3472 | 67.0592 | -123.5316 | 123.2289 | 123.4982 | 123.3045 | 67.0536 | -123.6494
274.2812 | 123.7335 | -67.0166 | 56.4743 | 0.06235 | -0.0055932 | -0.00053454 | 0.047048 | -0.0044409 | 0.04619 | 0.065477 | -0.0038537 | -0.006462 | 0.054191 | 0.03754 | 0.051343 | -67.0266 | 0.019721 | -66.9291 | 56.4258 | 56.2112 | 56.3123 | -67.0619 | -66.9946 | 0.014095 | -67.0978 | 56.2031 | 56.4725 | 56.3291 | -67.1614 | -0.045279 | -0.048487 | -0.009949 | 0.087466 | 0.13274 | -0.26307 | -0.16204 | -0.1448 | -0.27118 | 0.021967 | -0.081219 | 0.063581 | -0.00185 | -0.14516 | 123.4424 | 123.2278 | 123.3289 | 67.0363 | -123.5362 | 123.2197 | 123.4891 | 123.3457 | 67.0307 | -123.6357
275.2656 | 123.6603 | -67.0303 | 56.5155 | 0.06235 | -0.0045252 | -0.0016025 | 0.047048 | -0.0033719 | 0.047259 | 0.050216 | -0.0038537 | -0.005394 | 0.056327 | 0.035403 | 0.050274 | -67.0174 | 0.015142 | -66.9154 | 56.4304 | 56.1838 | 56.3123 | -67.039 | -66.9946 | 0.009516 | -67.0978 | 56.1985 | 56.4725 | 56.32 | -67.1614 | -0.008653 | -0.085107 | 0.01294 | 0.11493 | 0.12359 | -0.33174 | -0.20324 | -0.13107 | -0.31696 | 0.035699 | -0.067487 | 0.063581 | -0.043049 | -0.19552 | 123.4607 | 123.2141 | 123.3426 | 67.0455 | -123.5545 | 123.2289 | 123.5028 | 123.3503 | 67.0399 | -123.6769
276.2656 | 123.7793 | -66.9891 | 56.456 | 0.077612 | -0.0055932 | -0.00053454 | 0.04598 | -0.0033719 | 0.045122 | 0.080738 | -0.0038537 | -0.004326 | 0.055259 | 0.03754 | 0.050274 | -67.0311 | 0.015142 | -66.9108 | 56.4258 | 56.2112 | 56.3077 | -67.0665 | -66.9946 | 0.018674 | -67.1024 | 56.1848 | 56.4633 | 56.2925 | -67.1706 | -0.077324 | -0.030177 | -0.041993 | 0.078313 | 0.15564 | -0.24476 | -0.14831 | -0.18142 | -0.27118 | -0.005499 | -0.11326 | 0.068161 | 0.007303 | -0.16348 | 123.415 | 123.2004 | 123.2968 | 67.0043 | -123.5225 | 123.1739 | 123.4524 | 123.2816 | 67.0078 | -123.6266
277.2656 | 123.7747 | -66.9983 | 56.4743 | 0.047088 | -0.0055932 | -0.0037395 | 0.048117 | -0.0065769 | 0.04619 | 0.080738 | -0.0038537 | -0.004326 | 0.055259 | 0.035403 | 0.050274 | -67.0174 | 0.015142 | -66.9291 | 56.4212 | 56.1929 | 56.3077 | -67.0481 | -66.9901 | 0.014095 | -67.107 | 56.194 | 56.477 | 56.3291 | -67.1614 | -0.049853 | -0.053065 | -0.019103 | 0.069155 | 0.11901 | -0.28138 | -0.16662 | -0.16311 | -0.28034 | 0.008235 | -0.10869 | 0.054424 | 0.002729 | -0.14516 | 123.4195 | 123.1912 | 123.306 | 67.0134 | -123.5224 | 123.1923 | 123.4753 | 123.3274 | 67.0124 | -123.6357
278.2656 | 123.7518 | -67.0349 | 56.4697 | 0.047088 | -0.0045252 | -0.0026705 | 0.048117 | -0.0044409 | 0.045122 | 0.065477 | -0.0049217 | -0.005394 | 0.054191 | 0.036471 | 0.051343 | -67.0128 | 0.019721 | -66.92 | 56.4304 | 56.2067 | 56.3168 | -67.0436 | -66.9901 | 0.014095 | -67.0932 | 56.194 | 56.4725 | 56.2971 | -67.1614 | -0.008653 | -0.039331 | 0.022096 | 0.11493 | 0.12359 | -0.26307 | -0.15289 | -0.12649 | -0.27576 | 0.044856 | -0.05833 | 0.06816 | 0.002727 | -0.17264 | 123.4653 | 123.2416 | 123.3518 | 67.0546 | -123.5133 | 123.2289 | 123.5074 | 123.332 | 67.049 | -123.6311
279.2812 | 123.7518 | -67.0258 | 56.4972 | 0.047088 | -0.0066612 | -0.0026705 | 0.047048 | -0.0044409 | 0.044054 | 0.080738 | -0.0027857 | -0.005394 | 0.054191 | 0.036471 | 0.049206 | -67.0174 | 0.015142 | -66.9154 | 56.4258 | 56.2204 | 56.3077 | -67.0481 | -66.9901 | 0.014095 | -67.0978 | 56.1894 | 56.4816 | 56.3017 | -67.1706 | -0.022387 | -0.071375 | 0.008363 | 0.11036 | 0.13274 | -0.2768 | -0.18951 | -0.1448 | -0.3078 | 0.035701 | -0.072064 | 0.072739 | -0.015581 | -0.19552 | 123.4516 | 123.2462 | 123.3334 | 67.0409 | -123.5453 | 123.2151 | 123.5074 | 123.3274 | 67.0399 | -123.6678
280.2656 | 123.7061 | -67.012 | 56.4972 | 0.047088 | -0.0055932 | -0.0026705 | 0.047048 | -0.0055089 | 0.04619 | 0.034955 | -0.0049217 | -0.006462 | 0.055259 | 0.035403 | 0.049206 | -67.0174 | 0.015142 | -66.92 | 56.4258 | 56.2112 | 56.3077 | -67.039 | -66.9901 | 0.014095 | -67.0978 | 56.1985 | 56.4725 | 56.3154 | -67.166 | -0.026963 | -0.071375 | -0.00537 | 0.092045 | 0.11901 | -0.28596 | -0.18951 | -0.15396 | -0.29865 | 0.021968 | -0.085797 | 0.06816 | -0.024738 | -0.18179 | 123.4378 | 123.2233 | 123.3197 | 67.0272 | -123.5362 | 123.2106 | 123.4845 | 123.3274 | 67.0261 | -123.6632
281.2656 | 123.674 | -67.0395 | 56.5155 | 0.06235 | -0.0055932 | -0.00053454 | 0.047048 | -0.0044409 | 0.045122 | 0.080738 | -0.0038537 | -0.006462 | 0.055259 | 0.03754 | 0.048138 | -67.0128 | 0.015142 | -66.9291 | 56.4258 | 56.2112 | 56.3123 | -67.0481 | -66.9901 | 0.018674 | -67.0978 | 56.194 | 56.4725 | 56.2788 | -67.1614 | -0.008654 | -0.089686 | 0.026674 | 0.11035 | 0.11901 | -0.30427 | -0.20324 | -0.12191 | -0.32154 | 0.049434 | -0.058331 | 0.063581 | -0.043049 | -0.23673 | 123.4653 | 123.2507 | 123.3518 | 67.0546 | -123.5636 | 123.2335 | 123.5119 | 123.3183 | 67.0582 | -123.6769
282.2812 | 123.793 | -67.0258 | 56.4468 | 0.06235 | -0.0066612 | -0.0016025 | 0.047048 | -0.0055089 | 0.04619 | 0.050216 | -0.0038537 | -0.005394 | 0.055259 | 0.036471 | 0.051343 | -67.0266 | 0.010564 | -66.9154 | 56.4258 | 56.1929 | 56.3077 | -67.0344 | -66.9946 | 0.009516 | -67.1024 | 56.194 | 56.477 | 56.3108 | -67.166 | -0.008651 | -0.021021 | -0.000794 | 0.11036 | 0.11901 | -0.25392 | -0.13916 | -0.14022 | -0.25287 | 0.031122 | -0.076642 | 0.063582 | 0.030195 | -0.13601 | 123.4516 | 123.2187 | 123.3334 | 67.0363 | -123.4812 | 123.2197 | 123.5028 | 123.3366 | 67.0353 | -123.6128
283.2656 | 123.6877 | -67.0395 | 56.4926 | 0.031826 | -0.0055932 | -0.0016025 | 0.04598 | -0.0076459 | 0.047259 | 0.065477 | -0.0049217 | -0.005394 | 0.054191 | 0.03754 | 0.050274 | -67.0174 | 0.010564 | -66.9154 | 56.4258 | 56.2112 | 56.3077 | -67.0481 | -66.9946 | 0.018674 | -67.0978 | 56.1985 | 56.4816 | 56.3246 | -67.1751 | -0.008654 | -0.066798 | 0.022096 | 0.12409 | 0.13274 | -0.28138 | -0.18493 | -0.13565 | -0.29407 | 0.044855 | -0.058331 | 0.077317 | -0.011004 | -0.16805 | 123.4653 | 123.2507 | 123.3472 | 67.0501 | -123.5408 | 123.238 | 123.5211 | 123.3641 | 67.0582 | -123.6678
284.2812 | 123.7289 | -67.012 | 56.5063 | 0.031826 | -0.0066612 | -0.0016025 | 0.047048 | -0.0055089 | 0.045122 | 0.065477 | -0.0027857 | -0.006462 | 0.054191 | 0.036471 | 0.048138 | -67.0174 | 0.019721 | -66.92 | 56.435 | 56.2112 | 56.3123 | -67.039 | -66.9946 | 0.023253 | -67.0932 | 56.194 | 56.4725 | 56.2971 | -67.1706 | -0.026963 | -0.071374 | -0.00537 | 0.092045 | 0.11901 | -0.29511 | -0.19409 | -0.15854 | -0.31238 | 0.017389 | -0.081218 | 0.077318 | -0.033894 | -0.20926 | 123.447 | 123.2233 | 123.3243 | 67.0317 | -123.5453 | 123.206 | 123.4845 | 123.3091 | 67.0353 | -123.6769
285.2812 | 123.7747 | -67.0074 | 56.4514 | 0.077612 | -0.0055932 | -0.0026705 | 0.044912 | -0.0055089 | 0.04619 | 0.050216 | -0.0038537 | -0.006462 | 0.053122 | 0.03754 | 0.051343 | -67.0174 | 0.019721 | -66.9291 | 56.4304 | 56.2112 | 56.3077 | -67.0527 | -66.9901 | 0.014095 | -67.0932 | 56.1894 | 56.477 | 56.3246 | -67.1706 | -0.045277 | -0.02102 | -0.009948 | 0.07831 | 0.12359 | -0.24018 | -0.14373 | -0.16311 | -0.26203 | 0.01739 | -0.085796 | 0.077318 | 0.025617 | -0.12685 | 123.4378 | 123.2187 | 123.3151 | 67.0272 | -123.5041 | 123.1968 | 123.4845 | 123.332 | 67.0215 | -123.622
286.2656 | 123.674 | -67.0074 | 56.4926 | 0.047088 | -0.0045252 | -0.0016025 | 0.04598 | -0.0065769 | 0.044054 | 0.080738 | -0.0038537 | -0.006462 | 0.054191 | 0.038608 | 0.050274 | -67.022 | 0.010564 | -66.9291 | 56.4304 | 56.2158 | 56.3123 | -67.0619 | -66.9946 | 0.018674 | -67.0887 | 56.1985 | 56.4679 | 56.3108 | -67.1706 | -0.054435 | -0.062219 | -0.014526 | 0.07831 | 0.13274 | -0.2768 | -0.18035 | -0.16311 | -0.29407 | 0.012811 | -0.081217 | 0.081897 | -0.024739 | -0.18179 | 123.4378 | 123.2233 | 123.3197 | 67.018 | -123.5545 | 123.206 | 123.4753 | 123.3183 | 67.0261 | -123.6632
287.2812 | 123.7198 | -67.0029 | 56.5018 | 0.047088 | -0.0045252 | -0.0016025 | 0.047048 | -0.0055089 | 0.045122 | 0.050216 | -0.0038537 | -0.006462 | 0.055259 | 0.038608 | 0.049206 | -67.0128 | 0.019721 | -66.9291 | 56.4258 | 56.2112 | 56.3123 | -67.0436 | -66.9901 | 0.014095 | -67.1024 | 56.194 | 56.4725 | 56.2834 | -67.1706 | -0.040696 | -0.075953 | -0.009947 | 0.073733 | 0.11443 | -0.29053 | -0.18951 | -0.16769 | -0.3078 | 0.012813 | -0.09953 | 0.068161 | -0.029316 | -0.21842 | 123.4287 | 123.2141 | 123.3151 | 67.0226 | -123.5453 | 123.1968 | 123.4753 | 123.2862 | 67.017 | -123.6723
288.2656 | 123.6649 | -67.0303 | 56.5201 | 0.047088 | -0.0045252 | -0.00053454 | 0.044912 | -0.0044409 | 0.04619 | 0.080738 | -0.0038537 | -0.004326 | 0.056327 | 0.036471 | 0.049206 | -67.0128 | 0.019721 | -66.9246 | 56.4304 | 56.2067 | 56.3123 | -67.0527 | -66.9946 | 0.018674 | -67.0887 | 56.2031 | 56.4725 | 56.3154 | -67.1614 | -0.022389 | -0.089685 | 0.017518 | 0.10578 | 0.12816 | -0.31342 | -0.20782 | -0.13107 | -0.31696 | 0.035699 | -0.058329 | 0.072739 | -0.047627 | -0.20468 | 123.4607 | 123.237 | 123.3426 | 67.0501 | -123.5728 | 123.2335 | 123.5028 | 123.3457 | 67.049 | -123.6815
289.2656 | 123.6694 | -67.0486 | 56.5063 | 0.06235 | -0.0077302 | -0.0016025 | 0.04598 | -0.0055089 | 0.04619 | 0.080738 | -0.0038537 | -0.006462 | 0.054191 | 0.038608 | 0.049206 | -67.0174 | 0.015142 | -66.9246 | 56.4304 | 56.2112 | 56.3077 | -67.0481 | -66.9901 | 0.014095 | -67.0932 | 56.1985 | 56.4816 | 56.32 | -67.166 | 0.000501 | -0.075952 | 0.031251 | 0.12409 | 0.12359 | -0.29511 | -0.19867 | -0.11734 | -0.3078 | 0.058589 | -0.044597 | 0.072739 | -0.024737 | -0.18637 | 123.479 | 123.2599 | 123.3563 | 67.0638 | -123.5545 | 123.2472 | 123.5303 | 123.3686 | 67.0627 | -123.6723
290.2656 | 123.7106 | -67.012 | 56.5018 | 0.06235 | -0.0055932 | -0.0016025 | 0.04598 | -0.0055089 | 0.045122 | 0.050216 | -0.0038537 | -0.005394 | 0.054191 | 0.036471 | 0.050274 | -67.0174 | 0.019721 | -66.92 | 56.435 | 56.2021 | 56.3168 | -67.0481 | -66.9946 | 0.014095 | -67.0978 | 56.1985 | 56.477 | 56.32 | -67.166 | -0.03612 | -0.066796 | -0.00537 | 0.092045 | 0.12816 | -0.29969 | -0.18493 | -0.15396 | -0.30322 | 0.017389 | -0.085797 | 0.06816 | -0.024737 | -0.18179 | 123.447 | 123.2141 | 123.3289 | 67.0317 | -123.5499 | 123.2106 | 123.4891 | 123.332 | 67.0261 | -123.6678
291.2656 | 123.642 | -67.0532 | 56.4972 | 0.031826 | -0.0077302 | -0.0026705 | 0.047048 | -0.0044409 | 0.045122 | 0.050216 | -0.0038537 | -0.004326 | 0.052054 | 0.03754 | 0.050274 | -67.022 | 0.019721 | -66.9246 | 56.435 | 56.2158 | 56.3123 | -67.0573 | -66.9901 | 0.018674 | -67.0978 | 56.1985 | 56.477 | 56.3108 | -67.1706 | -0.004079 | -0.062218 | 0.031251 | 0.12866 | 0.13274 | -0.28138 | -0.18493 | -0.11734 | -0.29865 | 0.063167 | -0.044598 | 0.072739 | -0.020159 | -0.18637 | 123.4882 | 123.269 | 123.3655 | 67.0729 | -123.5545 | 123.2518 | 123.5303 | 123.364 | 67.0719 | -123.6678
292.2812 | 123.6511 | -67.0074 | 56.5109 | 0.047088 | -0.0055932 | -0.0026705 | 0.04598 | -0.0065769 | 0.047259 | 0.080738 | -0.0049217 | -0.007531 | 0.053122 | 0.03754 | 0.049206 | -67.0082 | 0.015142 | -66.9246 | 56.4304 | 56.2067 | 56.3123 | -67.0481 | -66.9946 | 0.014095 | -67.0932 | 56.2031 | 56.4816 | 56.265 | -67.1751 | -0.040698 | -0.080529 | -0.000791 | 0.082888 | 0.12359 | -0.30427 | -0.19866 | -0.16769 | -0.3078 | 0.012811 | -0.085796 | 0.081896 | -0.029314 | -0.24589 | 123.4378 | 123.2141 | 123.3197 | 67.0226 | -123.5591 | 123.2106 | 123.4891 | 123.2725 | 67.0215 | -123.6861
293.2656 | 123.6969 | -67.0029 | 56.5109 | 0.031826 | -0.0066612 | -0.0026705 | 0.04598 | -0.0044409 | 0.045122 | 0.065477 | -0.0038537 | -0.006462 | 0.056327 | 0.03754 | 0.051343 | -67.0174 | 0.019721 | -66.9291 | 56.4304 | 56.2158 | 56.3123 | -67.0527 | -66.9901 | 0.014095 | -67.0932 | 56.1894 | 56.477 | 56.3108 | -67.166 | -0.049854 | -0.080529 | -0.014525 | 0.073733 | 0.12359 | -0.29511 | -0.19866 | -0.16311 | -0.32154 | 0.012813 | -0.090373 | 0.072739 | -0.033892 | -0.2001 | 123.4333 | 123.2187 | 123.3151 | 67.0226 | -123.5636 | 123.1923 | 123.4799 | 123.3137 | 67.017 | -123.6769
294.2812 | 123.7656 | -66.9662 | 56.4651 | 0.047088 | -0.0066612 | -0.0026705 | 0.04598 | -0.0055089 | 0.04619 | 0.050216 | -0.0038537 | -0.007531 | 0.054191 | 0.03754 | 0.048138 | -67.022 | 0.0243 | -66.92 | 56.4304 | 56.2112 | 56.3123 | -67.0436 | -66.9992 | 0.014095 | -67.1024 | 56.194 | 56.4816 | 56.2971 | -67.166 | -0.077317 | -0.034753 | -0.055724 | 0.046269 | 0.12359 | -0.25391 | -0.15289 | -0.19973 | -0.27118 | -0.032966 | -0.13615 | 0.063582 | 0.016462 | -0.16806 | 123.3966 | 123.1775 | 123.2785 | 66.9905 | -123.5087 | 123.1602 | 123.4479 | 123.2633 | 66.9803 | -123.6311
295.2656 | 123.6969 | -67.0166 | 56.5109 | 0.092874 | -0.0077302 | -0.0026705 | 0.047048 | -0.0055089 | 0.044054 | 0.080738 | -0.0038537 | -0.004326 | 0.056327 | 0.038608 | 0.049206 | -67.022 | 0.019721 | -66.92 | 56.4304 | 56.2021 | 56.3123 | -67.0481 | -66.9809 | 0.014095 | -67.0887 | 56.1985 | 56.477 | 56.3154 | -67.1614 | -0.031542 | -0.080529 | -0.00537 | 0.096623 | 0.12816 | -0.30885 | -0.19866 | -0.1448 | -0.31238 | 0.035703 | -0.072061 | 0.072739 | -0.033892 | -0.19552 | 123.447 | 123.2187 | 123.3289 | 67.0363 | -123.5591 | 123.2151 | 123.4936 | 123.332 | 67.0307 | -123.6723
296.2656 | 123.7061 | -67.0258 | 56.5201 | 0.077612 | -0.0055932 | -0.00053454 | 0.044912 | -0.0055089 | 0.045122 | 0.065477 | -0.0049217 | -0.005394 | 0.054191 | 0.038608 | 0.051343 | -67.0174 | 0.015142 | -66.9246 | 56.4212 | 56.2067 | 56.3214 | -67.071 | -66.9901 | 0.014095 | -67.0932 | 56.194 | 56.4725 | 56.2879 | -67.1614 | -0.045282 | -0.098842 | 0.008363 | 0.1012 | 0.14648 | -0.31342 | -0.19866 | -0.13564 | -0.32611 | 0.035701 | -0.067485 | 0.06816 | -0.047627 | -0.23215 | 123.447 | 123.2324 | 123.3472 | 67.0409 | -123.5911 | 123.2197 | 123.4982 | 123.3137 | 67.0399 | -123.6815
297.2812 | 123.7015 | -67.012 | 56.4697 | 0.06235 | -0.0066612 | -0.0016025 | 0.048117 | -0.0065769 | 0.044054 | 0.065477 | -0.0038537 | -0.006462 | 0.053122 | 0.038608 | 0.049206 | -67.022 | 0.010564 | -66.9246 | 56.4258 | 56.2112 | 56.3077 | -67.0436 | -66.9946 | 0.009516 | -67.0887 | 56.194 | 56.4725 | 56.32 | -67.166 | -0.031541 | -0.04391 | -0.009948 | 0.087466 | 0.11901 | -0.25849 | -0.16204 | -0.15396 | -0.27576 | 0.017389 | -0.076639 | 0.077318 | 0.002727 | -0.14974 | 123.4378 | 123.2233 | 123.3197 | 67.0226 | -123.5133 | 123.206 | 123.4845 | 123.332 | 67.0215 | -123.6357
298.2656 | 123.674 | -67.0166 | 56.5292 | 0.047088 | -0.0066612 | -0.0037395 | 0.04598 | -0.0076459 | 0.045122 | 0.050216 | -0.0049217 | -0.006462 | 0.052054 | 0.038608 | 0.048138 | -67.0128 | 0.019721 | -66.9246 | 56.4258 | 56.2158 | 56.3168 | -67.0573 | -66.9855 | 0.018674 | -67.0978 | 56.1894 | 56.4725 | 56.3062 | -67.1706 | -0.0407 | -0.10342 | 0.003786 | 0.092044 | 0.13274 | -0.31342 | -0.2124 | -0.15396 | -0.33985 | 0.031124 | -0.081219 | 0.072739 | -0.056782 | -0.22299 | 123.4424 | 123.2324 | 123.3334 | 67.0363 | -123.5865 | 123.206 | 123.4891 | 123.3228 | 67.0353 | -123.6998
299.2656 | 123.7244 | -67.0166 | 56.4697 | 0.047088 | -0.0055932 | -0.0026705 | 0.04598 | -0.0055089 | 0.045122 | 0.065477 | -0.0049217 | -0.006462 | 0.053122 | 0.038608 | 0.050274 | -67.022 | 0.015142 | -66.9246 | 56.4258 | 56.2112 | 56.3123 | -67.0481 | -66.9901 | 0.014095 | -67.0887 | 56.1848 | 56.4725 | 56.3108 | -67.166 | -0.031542 | -0.04391 | -0.00537 | 0.092044 | 0.12359 | -0.25849 | -0.15747 | -0.14938 | -0.28492 | 0.026546 | -0.072061 | 0.077318 | 0.002727 | -0.1589 | 123.4424 | 123.2278 | 123.3289 | 67.0317 | -123.5179 | 123.2014 | 123.4891 | 123.3274 | 67.0307 | -123.6357
300.2656 | 123.6786 | -67.0441 | 56.4926 | 0.06235 | -0.0077302 | -0.0026705 | 0.049185 | -0.0055089 | 0.045122 | 0.050216 | -0.0038537 | -0.005394 | 0.053122 | 0.039676 | 0.049206 | -67.022 | 0.019721 | -66.9246 | 56.4258 | 56.2067 | 56.3168 | -67.0527 | -66.9901 | 0.014095 | -67.1024 | 56.2031 | 56.4679 | 56.3383 | -67.1614 | -0.008656 | -0.066798 | 0.022095 | 0.11951 | 0.12816 | -0.28596 | -0.17578 | -0.11733 | -0.28949 | 0.054011 | -0.058332 | 0.059003 | -0.024739 | -0.15432 | 123.4699 | 123.2507 | 123.3609 | 67.0638 | -123.5453 | 123.2472 | 123.5119 | 123.3824 | 67.0582 | -123.654
301.2656 | 123.7106 | -67.0303 | 56.4926 | 0.06235 | -0.0066612 | -0.0016025 | 0.04598 | -0.0065769 | 0.045122 | 0.065477 | -0.0059907 | -0.006462 | 0.055259 | 0.038608 | 0.048138 | -67.0128 | 0.019721 | -66.9291 | 56.4212 | 56.2158 | 56.3123 | -67.039 | -66.9901 | 0.014095 | -67.0932 | 56.1894 | 56.477 | 56.3062 | -67.166 | -0.008653 | -0.071376 | 0.017518 | 0.1012 | 0.10985 | -0.2768 | -0.18035 | -0.13565 | -0.30323 | 0.040278 | -0.062908 | 0.072739 | -0.015582 | -0.18637 | 123.4516 | 123.2462 | 123.3426 | 67.0501 | -123.5316 | 123.2197 | 123.5074 | 123.3366 | 67.0444 | -123.6586
302.2812 | 123.7701 | -67.012 | 56.4697 | 0.06235 | -0.0055932 | 0.00053446 | 0.047048 | -0.0044409 | 0.047259 | 0.050216 | -0.0059907 | -0.005394 | 0.052054 | 0.038608 | 0.048138 | -67.0174 | 0.015142 | -66.9291 | 56.4304 | 56.2067 | 56.3168 | -67.0481 | -66.9809 | 0.018674 | -67.0932 | 56.194 | 56.4679 | 56.3108 | -67.166 | -0.03612 | -0.039331 | -0.00537 | 0.082888 | 0.11901 | -0.26307 | -0.15289 | -0.15396 | -0.27576 | 0.031125 | -0.081218 | 0.072739 | -0.001851 | -0.1589 | 123.4424 | 123.2187 | 123.3289 | 67.0272 | -123.5179 | 123.206 | 123.4799 | 123.3228 | 67.0307 | -123.6357
303.2656 | 123.6832 | -67.0166 | 56.5338 | 0.047088 | -0.0066612 | -0.00053454 | 0.044912 | -0.0044409 | 0.044054 | 0.065477 | -0.0049217 | -0.007531 | 0.053122 | 0.040745 | 0.048138 | -67.0128 | 0.015142 | -66.92 | 56.435 | 56.2158 | 56.3168 | -67.039 | -66.9946 | 0.023253 | -67.0978 | 56.194 | 56.4725 | 56.32 | -67.166 | -0.022385 | -0.098839 | 0.003786 | 0.096623 | 0.11901 | -0.318 | -0.21697 | -0.14938 | -0.33985 | 0.021967 | -0.081219 | 0.06816 | -0.061359 | -0.21383 | 123.4516 | 123.2324 | 123.3334 | 67.0317 | -123.5728 | 123.2106 | 123.4891 | 123.3366 | 67.0399 | -123.6998
304.2656 | 123.7061 | -67.0441 | 56.4835 | 0.047088 | -0.0055932 | -0.0026705 | 0.044912 | -0.0065769 | 0.044054 | 0.050216 | -0.0049217 | -0.004326 | 0.053122 | 0.038608 | 0.049206 | -67.0174 | 0.019721 | -66.9246 | 56.4304 | 56.1975 | 56.3123 | -67.0527 | -66.9901 | 0.023253 | -67.0978 | 56.1894 | 56.4725 | 56.3062 | -67.1706 | -0.008656 | -0.053063 | 0.026673 | 0.11951 | 0.12816 | -0.28596 | -0.1712 | -0.12649 | -0.29407 | 0.054011 | -0.053754 | 0.072739 | -0.011005 | -0.17721 | 123.4745 | 123.2416 | 123.3563 | 67.0638 | -123.5362 | 123.2335 | 123.5165 | 123.3503 | 67.0673 | -123.654
305.2656 | 123.6923 | -67.0258 | 56.5155 | 0.077612 | -0.0066612 | -0.0026705 | 0.04598 | -0.0055089 | 0.044054 | 0.065477 | -0.0059907 | -0.006462 | 0.053122 | 0.040745 | 0.04707 | -67.0266 | 0.019721 | -66.9246 | 56.4396 | 56.1929 | 56.3168 | -67.0436 | -66.9946 | 0.014095 | -67.1024 | 56.1985 | 56.477 | 56.3154 | -67.1706 | -0.017808 | -0.07595 | -0.000794 | 0.1012 | 0.11901 | -0.32258 | -0.19866 | -0.1448 | -0.31696 | 0.031122 | -0.076642 | 0.068161 | -0.03847 | -0.2001 | 123.4653 | 123.2187 | 123.3426 | 67.0455 | -123.5591 | 123.2243 | 123.5028 | 123.3412 | 67.0399 | -123.6861
306.2656 | 123.7061 | -67.0441 | 56.4835 | 0.06235 | -0.0066612 | -0.0016025 | 0.044912 | -0.0055089 | 0.045122 | 0.050216 | -0.0038537 | -0.006462 | 0.054191 | 0.040745 | 0.048138 | -67.0174 | 0.019721 | -66.92 | 56.4304 | 56.1975 | 56.3214 | -67.0527 | -66.9901 | 0.018674 | -67.0932 | 56.1985 | 56.4725 | 56.3246 | -67.166 | -0.008656 | -0.053063 | 0.026673 | 0.12409 | 0.13274 | -0.28596 | -0.16204 | -0.12191 | -0.28491 | 0.054011 | -0.049175 | 0.072739 | -0.011005 | -0.1589 | 123.4745 | 123.2416 | 123.3655 | 67.0638 | -123.5362 | 123.2426 | 123.5165 | 123.3686 | 67.0627 | -123.6494
307.2656 | 123.7152 | -67.0074 | 56.5201 | 0.047088 | -0.0055932 | -0.0037395 | 0.047048 | -0.0065769 | 0.045122 | 0.050216 | -0.0027857 | -0.004326 | 0.054191 | 0.040745 | 0.049206 | -67.0128 | 0.010564 | -66.9246 | 56.4304 | 56.2112 | 56.3214 | -67.0436 | -66.9946 | 0.014095 | -67.0932 | 56.194 | 56.477 | 56.3062 | -67.1706 | -0.036119 | -0.089685 | -0.00537 | 0.082888 | 0.11901 | -0.30884 | -0.19866 | -0.16311 | -0.32611 | 0.012811 | -0.085796 | 0.077318 | -0.043048 | -0.21383 | 123.4378 | 123.2187 | 123.3289 | 67.018 | -123.5636 | 123.2014 | 123.4845 | 123.3137 | 67.0215 | -123.6906
308.2656 | 123.6923 | -67.0166 | 56.5247 | 0.077612 | -0.0055932 | -0.0016025 | 0.044912 | -0.0044409 | 0.044054 | 0.034955 | -0.0049217 | -0.006462 | 0.052054 | 0.041813 | 0.048138 | -67.022 | 0.010564 | -66.9246 | 56.435 | 56.2158 | 56.3123 | -67.0573 | -66.9992 | 0.018674 | -67.0932 | 56.2031 | 56.4679 | 56.2742 | -67.1706 | -0.0407 | -0.089684 | -0.00537 | 0.092044 | 0.13274 | -0.30884 | -0.2124 | -0.15396 | -0.32153 | 0.017388 | -0.07664 | 0.077318 | -0.056782 | -0.25046 | 123.4516 | 123.2324 | 123.3289 | 67.0272 | -123.582 | 123.2197 | 123.4845 | 123.2908 | 67.0353 | -123.6952
309.2812 | 123.6649 | -67.0349 | 56.5018 | 0.06235 | -0.0055932 | -0.0026705 | 0.04598 | -0.0055089 | 0.042985 | 0.065477 | -0.0049217 | -0.005394 | 0.053122 | 0.039676 | 0.048138 | -67.0128 | 0.015142 | -66.92 | 56.4304 | 56.2067 | 56.3168 | -67.0573 | -66.9855 | 0.014095 | -67.1024 | 56.1985 | 56.477 | 56.2696 | -67.1751 | -0.02239 | -0.071374 | 0.022096 | 0.11493 | 0.13732 | -0.29511 | -0.18493 | -0.14023 | -0.30322 | 0.049434 | -0.067487 | 0.072739 | -0.024737 | -0.23215 | 123.4653 | 123.2416 | 123.3518 | 67.0501 | -123.5591 | 123.2335 | 123.5119 | 123.3045 | 67.049 | -123.6769
310.2656 | 123.6832 | -67.0029 | 56.5109 | 0.06235 | -0.0077302 | -0.0016025 | 0.04598 | -0.0065769 | 0.045122 | 0.095999 | -0.0049217 | -0.006462 | 0.053122 | 0.040745 | 0.049206 | -67.0128 | 0.0243 | -66.9108 | 56.4258 | 56.2112 | 56.3168 | -67.0527 | -66.9901 | 0.018674 | -67.0932 | 56.194 | 56.4679 | 56.3017 | -67.1706 | -0.049854 | -0.085108 | -0.009947 | 0.092046 | 0.1419 | -0.29969 | -0.19409 | -0.16769 | -0.31696 | 0.012813 | -0.090373 | 0.077318 | -0.043049 | -0.20926 | 123.4287 | 123.2141 | 123.3197 | 67.0272 | -123.5636 | 123.1968 | 123.4707 | 123.3045 | 67.0215 | -123.6815
311.2656 | 123.6969 | -67.0258 | 56.4972 | 0.031826 | -0.0077302 | -0.0037395 | 0.043843 | -0.0044409 | 0.045122 | 0.080738 | -0.0049217 | -0.007531 | 0.050986 | 0.041813 | 0.04707 | -67.0174 | 0.015142 | -66.9154 | 56.4304 | 56.2204 | 56.3168 | -67.0481 | -66.9992 | 0.014095 | -67.1024 | 56.1985 | 56.4679 | 56.3154 | -67.166 | -0.022387 | -0.066796 | 0.008363 | 0.11036 | 0.13274 | -0.2768 | -0.18035 | -0.14022 | -0.29865 | 0.026543 | -0.076642 | 0.063582 | -0.029316 | -0.18179 | 123.4562 | 123.2462 | 123.3426 | 67.0409 | -123.5453 | 123.2243 | 123.4936 | 123.3412 | 67.0399 | -123.6632
312.2656 | 123.7061 | -67.0166 | 56.5292 | 0.06235 | -0.0066612 | -0.0026705 | 0.04598 | -0.0065769 | 0.042985 | 0.080738 | -0.0059907 | -0.006462 | 0.053122 | 0.040745 | 0.048138 | -67.0128 | 0.010564 | -66.92 | 56.4304 | 56.2158 | 56.3214 | -67.0481 | -66.9946 | 0.014095 | -67.0932 | 56.2031 | 56.4725 | 56.3017 | -67.166 | -0.031542 | -0.09884 | 0.003786 | 0.096623 | 0.12816 | -0.31342 | -0.20782 | -0.14938 | -0.32611 | 0.021967 | -0.07664 | 0.072739 | -0.056782 | -0.22757 | 123.447 | 123.2324 | 123.338 | 67.0272 | -123.5774 | 123.2197 | 123.4891 | 123.3183 | 67.0307 | -123.6952
313.2656 | 123.6969 | -66.9983 | 56.4835 | 0.077612 | -0.0066612 | -0.00053454 | 0.044912 | -0.0065769 | 0.047259 | 0.065477 | -0.0059907 | -0.007531 | 0.053122 | 0.041813 | 0.04707 | -67.0082 | 0.019721 | -66.9108 | 56.4304 | 56.2112 | 56.3214 | -67.0527 | -66.9901 | 0.014095 | -67.0932 | 56.1985 | 56.477 | 56.3017 | -67.1751 | -0.054432 | -0.053063 | -0.009946 | 0.087468 | 0.1419 | -0.27222 | -0.16204 | -0.17685 | -0.28491 | 0.008235 | -0.094951 | 0.081896 | -0.006426 | -0.18179 | 123.4287 | 123.2095 | 123.3197 | 67.018 | -123.5362 | 123.1968 | 123.4753 | 123.3 | 67.0124 | -123.6586
314.2656 | 123.7015 | -67.0212 | 56.5018 | 0.06235 | -0.0077302 | -0.0026705 | 0.044912 | -0.0055089 | 0.045122 | 0.065477 | -0.0038537 | -0.005394 | 0.053122 | 0.042881 | 0.049206 | -67.0128 | 0.019721 | -66.92 | 56.4212 | 56.2158 | 56.3214 | -67.0481 | -66.9901 | 0.018674 | -67.0932 | 56.194 | 56.477 | 56.3108 | -67.1706 | -0.026965 | -0.080531 | 0.008363 | 0.1012 | 0.12816 | -0.28595 | -0.18035 | -0.14938 | -0.3078 | 0.031123 | -0.072063 | 0.077318 | -0.024737 | -0.19094 | 123.4424 | 123.237 | 123.3426 | 67.0409 | -123.5499 | 123.2151 | 123.4982 | 123.332 | 67.0399 | -123.6723
315.2656 | 123.7061 | -66.9983 | 56.5292 | 0.06235 | -0.0066612 | -0.0037395 | 0.043843 | -0.0055089 | 0.044054 | 0.065477 | -0.0038537 | -0.005394 | 0.053122 | 0.042881 | 0.048138 | -67.0128 | 0.019721 | -66.92 | 56.4304 | 56.2204 | 56.3214 | -67.0481 | -66.9855 | 0.009516 | -67.0978 | 56.2031 | 56.4816 | 56.3337 | -67.1751 | -0.049853 | -0.09884 | -0.014525 | 0.078312 | 0.12816 | -0.30884 | -0.20782 | -0.17685 | -0.32611 | 0.012813 | -0.09953 | 0.077317 | -0.047625 | -0.19552 | 123.4287 | 123.2187 | 123.3197 | 67.018 | -123.5774 | 123.2014 | 123.4799 | 123.332 | 67.0078 | -123.7044
316.2656 | 123.6923 | -67.0258 | 56.5247 | 0.092874 | -0.0066612 | -0.0026705 | 0.044912 | -0.0065769 | 0.045122 | 0.065477 | -0.0049217 | -0.005394 | 0.052054 | 0.041813 | 0.049206 | -67.022 | 0.015142 | -66.9154 | 56.435 | 56.2204 | 56.3214 | -67.0619 | -66.9946 | 0.018674 | -67.0932 | 56.1894 | 56.4725 | 56.3246 | -67.166 | -0.036124 | -0.089684 | 0.003785 | 0.11036 | 0.14648 | -0.30426 | -0.20324 | -0.14022 | -0.33527 | 0.031122 | -0.067485 | 0.072739 | -0.052204 | -0.2001 | 123.4607 | 123.2462 | 123.3472 | 67.0409 | -123.5865 | 123.2151 | 123.4982 | 123.3503 | 67.0444 | -123.6906
317.2656 | 123.6694 | -67.0349 | 56.543 | 0.06235 | -0.0077302 | -0.0016025 | 0.04598 | -0.0044409 | 0.044054 | 0.065477 | -0.0049217 | -0.005394 | 0.054191 | 0.042881 | 0.04707 | -67.0128 | 0.019721 | -66.9154 | 56.4258 | 56.2204 | 56.3077 | -67.0527 | -66.9809 | 0.014095 | -67.0978 | 56.1985 | 56.477 | 56.2925 | -67.1706 | -0.017811 | -0.11715 | 0.022096 | 0.11951 | 0.13732 | -0.32257 | -0.23529 | -0.13565 | -0.34442 | 0.054013 | -0.062909 | 0.072739 | -0.065936 | -0.25046 | 123.4607 | 123.2553 | 123.3426 | 67.0546 | -123.5957 | 123.2335 | 123.5119 | 123.3274 | 67.049 | -123.7135
318.2656 | 123.6923 | -67.0166 | 56.5201 | 0.047088 | -0.0066612 | -0.0048075 | 0.04598 | -0.0055089 | 0.044054 | 0.080738 | -0.0059907 | -0.007531 | 0.052054 | 0.041813 | 0.048138 | -67.0128 | 0.0243 | -66.92 | 56.4258 | 56.2112 | 56.3168 | -67.0481 | -66.9946 | 0.018674 | -67.0887 | 56.2031 | 56.477 | 56.2788 | -67.1706 | -0.031542 | -0.094264 | 0.003786 | 0.096623 | 0.12816 | -0.30884 | -0.20324 | -0.15396 | -0.31696 | 0.021967 | -0.072061 | 0.081897 | -0.043048 | -0.2413 | 123.4424 | 123.2278 | 123.3334 | 67.0409 | -123.5682 | 123.2197 | 123.4936 | 123.2954 | 67.0353 | -123.6906
319.2656 | 123.6099 | -67.0532 | 56.5063 | 0.047088 | -0.0087982 | -0.00053454 | 0.044912 | -0.0065769 | 0.044054 | 0.080738 | -0.0038537 | -0.007531 | 0.053122 | 0.041813 | 0.048138 | -67.0174 | 0.010564 | -66.92 | 56.4258 | 56.2204 | 56.3214 | -67.0481 | -66.9855 | 0.009516 | -67.0841 | 56.194 | 56.4725 | 56.3154 | -67.1706 | 0.005079 | -0.080531 | 0.035829 | 0.13324 | 0.12816 | -0.28595 | -0.18493 | -0.11734 | -0.31238 | 0.067745 | -0.030862 | 0.086475 | -0.033894 | -0.19094 | 123.479 | 123.2736 | 123.3746 | 67.0638 | -123.5545 | 123.2472 | 123.5257 | 123.3686 | 67.0627 | -123.6769
320.2656 | 123.6374 | -67.0029 | 56.5521 | 0.047088 | -0.0066612 | -0.0026705 | 0.04598 | -0.0044409 | 0.045122 | 0.080738 | -0.0049217 | -0.005394 | 0.053122 | 0.042881 | 0.046001 | -67.0174 | 0.010564 | -66.9154 | 56.4212 | 56.2204 | 56.3214 | -67.0436 | -66.9901 | 0.018674 | -67.0932 | 56.2031 | 56.477 | 56.32 | -67.166 | -0.040696 | -0.13088 | -0.014525 | 0.087468 | 0.12816 | -0.33173 | -0.23071 | -0.16311 | -0.349 | 0.012813 | -0.090373 | 0.072739 | -0.075091 | -0.23214 | 123.4241 | 123.2233 | 123.3243 | 67.0134 | -123.5957 | 123.206 | 123.4799 | 123.3229 | 67.0215 | -123.7181
321.2656 | 123.6465 | -67.0212 | 56.5475 | 0.06235 | -0.0098662 | -0.0026705 | 0.043843 | -0.0055089 | 0.044054 | 0.065477 | -0.0049217 | -0.006462 | 0.052054 | 0.041813 | 0.044933 | -67.0174 | 0.019721 | -66.9154 | 56.4396 | 56.2204 | 56.3214 | -67.0573 | -66.9855 | 0.009516 | -67.0887 | 56.2031 | 56.4862 | 56.3337 | -67.1751 | -0.036123 | -0.10799 | 0.003785 | 0.10578 | 0.1419 | -0.32715 | -0.22613 | -0.15396 | -0.34442 | 0.035701 | -0.067484 | 0.086475 | -0.061356 | -0.21383 | 123.4607 | 123.2416 | 123.3426 | 67.0409 | -123.6048 | 123.2243 | 123.5074 | 123.3549 | 67.0307 | -123.7227
322.2656 | 123.642 | -66.9937 | 56.543 | 0.047088 | -0.0077302 | -0.0037395 | 0.042775 | -0.0055089 | 0.044054 | 0.080738 | -0.0059907 | -0.006462 | 0.052054 | 0.042881 | 0.04707 | -67.0174 | 0.019721 | -66.92 | 56.4258 | 56.2112 | 56.3214 | -67.0481 | -66.9855 | 0.018674 | -67.0978 | 56.2031 | 56.477 | 56.3108 | -67.1751 | -0.054431 | -0.11715 | -0.023681 | 0.073734 | 0.12816 | -0.33173 | -0.22155 | -0.18143 | -0.33984 | 0.008235 | -0.10411 | 0.077317 | -0.065936 | -0.23214 | 123.4195 | 123.2049 | 123.3151 | 67.0134 | -123.5911 | 123.1968 | 123.4707 | 123.3045 | 67.0124 | -123.7181
323.2656 | 123.6557 | -67.0258 | 56.5109 | 0.047088 | -0.0077302 | -0.0026705 | 0.041706 | -0.0055089 | 0.045122 | 0.065477 | -0.0059907 | -0.006462 | 0.053122 | 0.04395 | 0.046001 | -67.0128 | 0.005985 | -66.92 | 56.4212 | 56.2204 | 56.3123 | -67.0481 | -66.9855 | 0.018674 | -67.0841 | 56.2031 | 56.477 | 56.3291 | -67.166 | -0.022387 | -0.089686 | 0.012941 | 0.10578 | 0.12816 | -0.29053 | -0.19866 | -0.14022 | -0.3078 | 0.040279 | -0.058328 | 0.081896 | -0.033892 | -0.18178 | 123.447 | 123.2462 | 123.338 | 67.0317 | -123.5591 | 123.2289 | 123.5028 | 123.3549 | 67.0444 | -123.6769
324.2812 | 123.6282 | -67.0532 | 56.5155 | 0.031826 | -0.0077302 | -0.0016025 | 0.043843 | -0.0076459 | 0.044054 | 0.050216 | -0.0059907 | -0.005394 | 0.052054 | 0.04395 | 0.04707 | -67.0174 | 0.019721 | -66.92 | 56.4304 | 56.2112 | 56.3168 | -67.0573 | -66.9809 | 0.018674 | -67.0887 | 56.1985 | 56.4725 | 56.32 | -67.1751 | -0.004079 | -0.085107 | 0.035829 | 0.13324 | 0.13732 | -0.30427 | -0.19866 | -0.12192 | -0.31696 | 0.072324 | -0.03544 | 0.086475 | -0.043049 | -0.19552 | 123.4836 | 123.2645 | 123.3701 | 67.0729 | -123.5728 | 123.2518 | 123.5257 | 123.3732 | 67.0719 | -123.6906
325.2656 | 123.6649 | -67.012 | 56.543 | 0.047088 | -0.0066612 | -0.0016025 | 0.04598 | -0.0033719 | 0.042985 | 0.050216 | -0.0049217 | -0.005394 | 0.053122 | 0.04395 | 0.046001 | -67.022 | 0.010564 | -66.9108 | 56.4258 | 56.2021 | 56.3168 | -67.0481 | -66.9855 | 0.018674 | -67.0932 | 56.2031 | 56.4725 | 56.3154 | -67.166 | -0.03612 | -0.11715 | -0.009948 | 0.1012 | 0.13732 | -0.34089 | -0.22613 | -0.15396 | -0.33984 | 0.026546 | -0.081218 | 0.072739 | -0.070515 | -0.22756 | 123.4378 | 123.2141 | 123.3289 | 67.0226 | -123.5911 | 123.2151 | 123.4845 | 123.3274 | 67.0307 | -123.709
326.2656 | 123.6511 | -66.9983 | 56.5338 | 0.077612 | -0.0087982 | -0.0026705 | 0.044912 | -0.0065769 | 0.044054 | 0.065477 | -0.0070587 | -0.007531 | 0.050986 | 0.041813 | 0.046001 | -67.0128 | 0.010564 | -66.9246 | 56.435 | 56.2158 | 56.3214 | -67.0619 | -66.9855 | 0.009516 | -67.0932 | 56.2031 | 56.4679 | 56.3017 | -67.1751 | -0.06359 | -0.098839 | -0.014525 | 0.073733 | 0.13732 | -0.318 | -0.21239 | -0.17685 | -0.33069 | 0.012813 | -0.094951 | 0.081896 | -0.065937 | -0.23214 | 123.4333 | 123.2141 | 123.3197 | 67.0089 | -123.5957 | 123.2014 | 123.4662 | 123.3 | 67.0078 | -123.709
327.2656 | 123.674 | -66.9754 | 56.5659 | 0.077612 | -0.0066612 | -0.0026705 | 0.044912 | -0.0065769 | 0.044054 | 0.080738 | -0.0038537 | -0.006462 | 0.052054 | 0.045018 | 0.046001 | -67.0128 | 0.019721 | -66.92 | 56.4304 | 56.2112 | 56.3214 | -67.0619 | -66.9855 | 0.018674 | -67.0932 | 56.2031 | 56.4725 | 56.2925 | -67.166 | -0.086478 | -0.13546 | -0.037413 | 0.055424 | 0.1419 | -0.35462 | -0.24444 | -0.19058 | -0.36273 | -0.010075 | -0.11784 | 0.072739 | -0.093403 | -0.27335 | 123.4058 | 123.1866 | 123.2968 | 66.9951 | -123.6277 | 123.1785 | 123.4479 | 123.2679 | 66.9941 | -123.7318
328.2656 | 123.6877 | -67.0029 | 56.5247 | 0.077612 | -0.0077302 | -0.0037395 | 0.044912 | -0.0065769 | 0.044054 | 0.065477 | -0.0038537 | -0.005394 | 0.052054 | 0.042881 | 0.044933 | -67.0128 | 0.019721 | -66.9154 | 56.4304 | 56.2158 | 56.3168 | -67.0619 | -66.9855 | 0.023253 | -67.0932 | 56.2077 | 56.4633 | 56.3291 | -67.1706 | -0.059012 | -0.094262 | -0.009947 | 0.087468 | 0.14648 | -0.30884 | -0.20782 | -0.16769 | -0.31696 | 0.017391 | -0.090373 | 0.077318 | -0.061361 | -0.19552 | 123.4333 | 123.2187 | 123.3197 | 67.0226 | -123.5865 | 123.2106 | 123.4662 | 123.332 | 67.0261 | -123.6952
329.2812 | 123.6969 | -67.0212 | 56.5018 | 0.047088 | -0.0077302 | -0.0016025 | 0.044912 | -0.0076459 | 0.044054 | 0.080738 | -0.0049217 | -0.006462 | 0.053122 | 0.04395 | 0.048138 | -67.0128 | 0.019721 | -66.92 | 56.4258 | 56.225 | 56.3214 | -67.0481 | -66.9901 | 0.014095 | -67.0978 | 56.1985 | 56.477 | 56.3246 | -67.1706 | -0.026965 | -0.075953 | 0.008363 | 0.1012 | 0.12816 | -0.2768 | -0.18035 | -0.14938 | -0.30322 | 0.031123 | -0.076642 | 0.072739 | -0.024737 | -0.17721 | 123.447 | 123.2462 | 123.3426 | 67.0409 | -123.5499 | 123.2197 | 123.4982 | 123.3457 | 67.0353 | -123.6723
330.2656 | 123.6374 | -67.0166 | 56.5338 | 0.047088 | -0.0077302 | -0.0026705 | 0.044912 | -0.0076459 | 0.044054 | 0.095999 | -0.0070587 | -0.006462 | 0.053122 | 0.04395 | 0.04707 | -67.0128 | 0.010564 | -66.92 | 56.4212 | 56.2204 | 56.3214 | -67.0436 | -66.9901 | 0.009516 | -67.0932 | 56.1985 | 56.4862 | 56.3291 | -67.1614 | -0.026963 | -0.11257 | 0.003786 | 0.096623 | 0.12359 | -0.31342 | -0.21239 | -0.1448 | -0.33527 | 0.026546 | -0.07664 | 0.06816 | -0.047623 | -0.20467 | 123.4378 | 123.237 | 123.338 | 67.0272 | -123.5774 | 123.2151 | 123.5028 | 123.3457 | 67.0261 | -123.6952
331.2656 | 123.6053 | -66.9937 | 56.543 | 0.077612 | -0.0077302 | -0.0026705 | 0.043843 | -0.0055089 | 0.042985 | 0.065477 | -0.0049217 | -0.006462 | 0.052054 | 0.042881 | 0.04707 | -67.0128 | 0.010564 | -66.92 | 56.4304 | 56.2204 | 56.326 | -67.0573 | -66.9855 | 0.009516 | -67.0887 | 56.1985 | 56.477 | 56.2742 | -67.1751 | -0.063589 | -0.11257 | -0.019103 | 0.073734 | 0.13732 | -0.32257 | -0.21697 | -0.18143 | -0.34442 | 0.008235 | -0.09495 | 0.086475 | -0.065936 | -0.26877 | 123.4241 | 123.2141 | 123.3197 | 67.0043 | -123.6003 | 123.1923 | 123.4707 | 123.2679 | 67.0032 | -123.7181
332.2656 | 123.642 | -67.0258 | 56.5247 | 0.047088 | -0.0087982 | -0.0026705 | 0.043843 | -0.0055089 | 0.044054 | 0.080738 | -0.0038537 | -0.006462 | 0.052054 | 0.045018 | 0.04707 | -67.0128 | 0.010564 | -66.9246 | 56.4304 | 56.2204 | 56.3168 | -67.0527 | -66.9809 | 0.014095 | -67.0887 | 56.2031 | 56.477 | 56.2971 | -67.166 | -0.026966 | -0.094262 | 0.012941 | 0.1012 | 0.12816 | -0.30426 | -0.20782 | -0.14022 | -0.32153 | 0.044858 | -0.062906 | 0.077318 | -0.047625 | -0.22757 | 123.4562 | 123.2462 | 123.3426 | 67.0363 | -123.5774 | 123.2289 | 123.5028 | 123.3228 | 67.0399 | -123.6906
333.2656 | 123.6465 | -67.0303 | 56.543 | 0.047088 | -0.0066612 | -0.0037395 | 0.044912 | -0.0065769 | 0.045122 | 0.065477 | -0.0038537 | -0.007531 | 0.053122 | 0.042881 | 0.049206 | -67.0082 | 0.010564 | -66.92 | 56.4304 | 56.225 | 56.326 | -67.0436 | -66.9855 | 0.023253 | -67.0932 | 56.194 | 56.4679 | 56.2879 | -67.1797 | -0.013231 | -0.11257 | 0.022097 | 0.11035 | 0.12359 | -0.318 | -0.21697 | -0.14938 | -0.349 | 0.044856 | -0.062908 | 0.086475 | -0.075093 | -0.25504 | 123.4607 | 123.2553 | 123.3563 | 67.0409 | -123.5865 | 123.2243 | 123.4982 | 123.3183 | 67.0536 | -123.7227
334.2656 | 123.6603 | -67.0349 | 56.543 | 0.077612 | -0.0055932 | -0.0026705 | 0.044912 | -0.0076459 | 0.045122 | 0.065477 | -0.0049217 | -0.007531 | 0.050986 | 0.04395 | 0.04707 | -67.0174 | 0.015142 | -66.9154 | 56.435 | 56.2158 | 56.3168 | -67.0527 | -66.9901 | 0.014095 | -67.0932 | 56.2077 | 56.4816 | 56.3291 | -67.1751 | -0.017811 | -0.108 | 0.017518 | 0.11951 | 0.13732 | -0.32715 | -0.22613 | -0.14023 | -0.33527 | 0.044856 | -0.05833 | 0.081896 | -0.061358 | -0.21383 | 123.4699 | 123.2507 | 123.3518 | 67.0501 | -123.5957 | 123.2426 | 123.5165 | 123.3641 | 67.049 | -123.7181
335.2656 | 123.6832 | -66.9983 | 56.5338 | 0.06235 | -0.0077302 | -0.0026705 | 0.047048 | -0.0076459 | 0.047259 | 0.095999 | -0.0059907 | -0.007531 | 0.052054 | 0.045018 | 0.046001 | -67.0082 | 0.010564 | -66.92 | 56.4258 | 56.2204 | 56.3168 | -67.0665 | -66.9809 | 0.018674 | -67.0932 | 56.1985 | 56.4725 | 56.2971 | -67.166 | -0.068169 | -0.108 | -0.009946 | 0.078312 | 0.14648 | -0.31342 | -0.21697 | -0.16769 | -0.33527 | 0.017392 | -0.094951 | 0.072739 | -0.061359 | -0.23672 | 123.4241 | 123.2187 | 123.3151 | 67.0089 | -123.6003 | 123.1968 | 123.4707 | 123.2954 | 67.017 | -123.6998
336.2656 | 123.6969 | -66.9846 | 56.5063 | 0.031826 | -0.0066612 | -0.0026705 | 0.04598 | -0.0055089 | 0.044054 | 0.065477 | -0.0049217 | -0.005394 | 0.052054 | 0.042881 | 0.04707 | -67.0128 | 0.019721 | -66.92 | 56.4304 | 56.2204 | 56.3214 | -67.0527 | -66.9901 | 0.014095 | -67.0932 | 56.1985 | 56.4725 | 56.3062 | -67.166 | -0.068165 | -0.075952 | -0.028258 | 0.064579 | 0.13274 | -0.28595 | -0.18493 | -0.18142 | -0.3078 | -0.005498 | -0.10868 | 0.072739 | -0.033894 | -0.2001 | 123.415 | 123.205 | 123.306 | 67.0043 | -123.5591 | 123.1831 | 123.457 | 123.2908 | 66.9987 | -123.6723
337.2656 | 123.7518 | -66.9846 | 56.5063 | 0.047088 | -0.0087982 | -0.0037395 | 0.044912 | -0.0055089 | 0.044054 | 0.065477 | -0.0049217 | -0.007531 | 0.050986 | 0.045018 | 0.046001 | -67.0174 | 0.015142 | -66.9291 | 56.4304 | 56.2158 | 56.3214 | -67.0436 | -66.9855 | 0.014095 | -67.0887 | 56.2031 | 56.4725 | 56.2971 | -67.1706 | -0.059007 | -0.075952 | -0.032836 | 0.055422 | 0.11443 | -0.29053 | -0.18493 | -0.186 | -0.30322 | -0.00092 | -0.1041 | 0.081897 | -0.033894 | -0.20926 | 123.415 | 123.2004 | 123.306 | 66.9997 | -123.5499 | 123.1877 | 123.457 | 123.2816 | 66.9987 | -123.6769
338.2656 | 123.7747 | -66.9571 | 56.5063 | 0.06235 | -0.0077302 | -0.0016025 | 0.044912 | -0.0044409 | 0.044054 | 0.080738 | -0.0038537 | -0.005394 | 0.052054 | 0.04395 | 0.04707 | -67.0082 | 0.019721 | -66.9154 | 56.4258 | 56.2112 | 56.3214 | -67.039 | -66.9809 | 0.009516 | -67.0932 | 56.1985 | 56.4679 | 56.2742 | -67.1751 | -0.081895 | -0.080531 | -0.051145 | 0.041691 | 0.12359 | -0.29511 | -0.18493 | -0.21805 | -0.3078 | -0.023807 | -0.13615 | 0.081896 | -0.038472 | -0.23215 | 123.3829 | 123.1683 | 123.2785 | 66.9768 | -123.5453 | 123.1556 | 123.425 | 123.2313 | 66.9666 | -123.6815
339.2812 | 123.6969 | -67.0074 | 56.5201 | 0.047088 | -0.0066612 | -0.0037395 | 0.043843 | -0.0055089 | 0.044054 | 0.080738 | -0.0059907 | -0.005394 | 0.053122 | 0.04395 | 0.04707 | -67.0128 | 0.019721 | -66.92 | 56.4304 | 56.2204 | 56.3214 | -67.0527 | -66.9901 | 0.014095 | -67.0795 | 56.2031 | 56.4725 | 56.3154 | -67.166 | -0.045277 | -0.089685 | -0.00537 | 0.087467 | 0.13274 | -0.29969 | -0.19866 | -0.15854 | -0.31696 | 0.01739 | -0.07206 | 0.086475 | -0.047627 | -0.20468 | 123.4378 | 123.2278 | 123.3289 | 67.0272 | -123.5728 | 123.2106 | 123.4799 | 123.3229 | 67.0215 | -123.6861
340.2656 | 123.7244 | -66.9754 | 56.5018 | 0.06235 | -0.0066612 | -0.0026705 | 0.04598 | -0.0055089 | 0.045122 | 0.080738 | -0.0049217 | -0.006462 | 0.053122 | 0.041813 | 0.046001 | -67.0082 | 0.010564 | -66.9291 | 56.435 | 56.2204 | 56.3214 | -67.0527 | -66.9901 | 0.018674 | -67.0887 | 56.2077 | 56.477 | 56.3246 | -67.1751 | -0.07732 | -0.066796 | -0.032834 | 0.046267 | 0.12359 | -0.28137 | -0.18035 | -0.19974 | -0.29407 | -0.014653 | -0.11326 | 0.086475 | -0.024737 | -0.17721 | 123.4104 | 123.1958 | 123.2968 | 66.986 | -123.5545 | 123.1831 | 123.4524 | 123.3 | 66.9941 | -123.6769
341.2656 | 123.7839 | -66.9617 | 56.4972 | 0.047088 | -0.0098662 | -0.0048075 | 0.044912 | -0.0065769 | 0.045122 | 0.080738 | -0.0059907 | -0.005394 | 0.050986 | 0.046087 | 0.04707 | -67.0082 | 0.015142 | -66.9154 | 56.4304 | 56.2158 | 56.3214 | -67.0436 | -66.9809 | 0.014095 | -67.0887 | 56.2031 | 56.4725 | 56.3246 | -67.1797 | -0.081895 | -0.066796 | -0.046567 | 0.046269 | 0.12816 | -0.28138 | -0.17577 | -0.21805 | -0.29407 | -0.019229 | -0.12699 | 0.091054 | -0.024738 | -0.17263 | 123.3921 | 123.1775 | 123.2831 | 66.9768 | -123.5408 | 123.1648 | 123.4341 | 123.2862 | 66.9758 | -123.6769
342.2656 | 123.8205 | -66.9754 | 56.488 | 0.031826 | -0.0077302 | -0.0016025 | 0.043843 | -0.0065769 | 0.044054 | 0.11126 | -0.0038537 | -0.006462 | 0.052054 | 0.046087 | 0.044933 | -67.0037 | 0.010564 | -66.9154 | 56.4258 | 56.2112 | 56.326 | -67.0436 | -66.9855 | 0.018674 | -67.0887 | 56.1985 | 56.4725 | 56.32 | -67.1797 | -0.068162 | -0.06222 | -0.028256 | 0.060002 | 0.12816 | -0.2768 | -0.16204 | -0.20431 | -0.28949 | -0.010075 | -0.11326 | 0.091054 | -0.015583 | -0.16805 | 123.4012 | 123.1866 | 123.3014 | 66.986 | -123.5316 | 123.1739 | 123.4479 | 123.2954 | 66.9941 | -123.6678
343.2656 | 123.7885 | -66.9891 | 56.4972 | 0.047088 | -0.0077302 | -0.0016025 | 0.047048 | -0.0065769 | 0.044054 | 0.065477 | -0.0038537 | -0.008599 | 0.052054 | 0.046087 | 0.041728 | -67.0128 | 0.015142 | -66.9246 | 56.435 | 56.2112 | 56.3214 | -67.0527 | -66.9855 | 0.014095 | -67.0887 | 56.1985 | 56.477 | 56.3108 | -67.1751 | -0.063587 | -0.062218 | -0.02368 | 0.064578 | 0.12816 | -0.28596 | -0.17577 | -0.186 | -0.29865 | 0.003658 | -0.099527 | 0.086475 | -0.020159 | -0.18637 | 123.4241 | 123.2004 | 123.3106 | 67.0043 | -123.5499 | 123.1877 | 123.4662 | 123.3 | 67.0032 | -123.6723
344.2812 | 123.674 | -66.9937 | 56.5155 | 0.092874 | -0.0087982 | -0.0016025 | 0.044912 | -0.0055089 | 0.044054 | 0.065477 | -0.0049217 | -0.006462 | 0.053122 | 0.045018 | 0.044933 | -67.0082 | 0.010564 | -66.92 | 56.4396 | 56.2158 | 56.326 | -67.0527 | -66.9763 | 0.014095 | -67.0978 | 56.2031 | 56.4725 | 56.3246 | -67.1751 | -0.05901 | -0.07595 | -0.014524 | 0.073734 | 0.13274 | -0.29969 | -0.18951 | -0.18143 | -0.31238 | 0.017393 | -0.10411 | 0.077317 | -0.043049 | -0.19094 | 123.4333 | 123.2095 | 123.3197 | 67.0043 | -123.5682 | 123.1968 | 123.4662 | 123.3183 | 67.0078 | -123.6906
345.2656 | 123.7656 | -66.9708 | 56.4972 | 0.06235 | -0.0077302 | -0.0048075 | 0.043843 | -0.0076459 | 0.041917 | 0.065477 | -0.0059907 | -0.006462 | 0.053122 | 0.045018 | 0.046001 | -67.0174 | 0.015142 | -66.9246 | 56.4258 | 56.225 | 56.3214 | -67.039 | -66.9809 | 0.018674 | -67.0841 | 56.194 | 56.477 | 56.3291 | -67.1614 | -0.068162 | -0.071375 | -0.046569 | 0.046267 | 0.11443 | -0.27222 | -0.17577 | -0.19058 | -0.30322 | -0.010074 | -0.11326 | 0.077317 | -0.020159 | -0.16805 | 123.3966 | 123.1958 | 123.2922 | 66.986 | -123.5362 | 123.1648 | 123.4479 | 123.3 | 66.9895 | -123.6586
346.2656 | 123.7564 | -66.9754 | 56.4972 | 0.077612 | -0.0077302 | -0.0058765 | 0.043843 | -0.0055089 | 0.044054 | 0.065477 | -0.0049217 | -0.006462 | 0.048849 | 0.045018 | 0.046001 | -67.0082 | 0.019721 | -66.9154 | 56.4304 | 56.2204 | 56.3123 | -67.0481 | -66.9855 | 0.014095 | -67.0887 | 56.194 | 56.4679 | 56.32 | -67.1751 | -0.072741 | -0.066796 | -0.032834 | 0.060002 | 0.13274 | -0.2768 | -0.18493 | -0.19974 | -0.30322 | -0.010075 | -0.11326 | 0.086475 | -0.029316 | -0.17721 | 123.4058 | 123.1958 | 123.2877 | 66.9951 | -123.5453 | 123.1694 | 123.4433 | 123.2954 | 66.9895 | -123.6723
347.2656 | 123.8297 | -66.9296 | 56.543 | 0.047088 | -0.0077302 | -0.0026705 | 0.043843 | -0.0087139 | 0.042985 | 0.080738 | -0.0049217 | -0.006462 | 0.053122 | 0.046087 | 0.04707 | -67.0128 | 0.015142 | -66.92 | 56.4212 | 56.2112 | 56.3168 | -67.0527 | -66.9855 | 0.014095 | -67.0887 | 56.1985 | 56.4725 | 56.3062 | -67.1751 | -0.1231 | -0.12173 | -0.08319 | 0.009647 | 0.13274 | -0.33173 | -0.22613 | -0.24551 | -0.34442 | -0.055852 | -0.15904 | 0.086475 | -0.070515 | -0.23672 | 123.3509 | 123.1409 | 123.2465 | 66.9448 | -123.5957 | 123.1282 | 123.4021 | 123.2359 | 66.9437 | -123.7181
348.2656 | 123.7701 | -66.9662 | 56.4926 | 0.06235 | -0.0077302 | -0.0037395 | 0.043843 | -0.0055089 | 0.045122 | 0.080738 | -0.0038537 | -0.006462 | 0.049918 | 0.045018 | 0.046001 | -67.0082 | 0.019721 | -66.9154 | 56.4258 | 56.2204 | 56.3123 | -67.0619 | -66.9855 | 0.014095 | -67.0932 | 56.1985 | 56.4816 | 56.3062 | -67.1797 | -0.095633 | -0.066798 | -0.041989 | 0.050847 | 0.14648 | -0.27222 | -0.18035 | -0.21347 | -0.29407 | -0.01923 | -0.12699 | 0.086475 | -0.011004 | -0.18637 | 123.3921 | 123.1866 | 123.2785 | 66.986 | -123.5545 | 123.1648 | 123.4479 | 123.2725 | 66.9803 | -123.6723
349.2812 | 123.6694 | -67.0349 | 56.5384 | 0.06235 | -0.0077302 | -0.0026705 | 0.043843 | -0.0044409 | 0.041917 | 0.080738 | -0.0049217 | -0.006462 | 0.050986 | 0.047155 | 0.044933 | -67.0037 | 0.015142 | -66.9337 | 56.4304 | 56.2204 | 56.3214 | -67.0481 | -66.9901 | 0.009516 | -67.0978 | 56.2031 | 56.477 | 56.3154 | -67.166 | -0.013232 | -0.10799 | 0.031253 | 0.1012 | 0.11443 | -0.318 | -0.21697 | -0.13107 | -0.33527 | 0.044856 | -0.062909 | 0.06816 | -0.061358 | -0.22299 | 123.4653 | 123.2553 | 123.3563 | 67.0501 | -123.5865 | 123.238 | 123.5119 | 123.3503 | 67.0444 | -123.7044
350.2656 | 123.8068 | -66.9754 | 56.4651 | 0.077612 | -0.0077302 | -0.0026705 | 0.043843 | -0.0076459 | 0.042985 | 0.080738 | -0.0049217 | -0.005394 | 0.052054 | 0.045018 | 0.046001 | -67.0082 | 0.015142 | -66.9291 | 56.4258 | 56.225 | 56.326 | -67.0527 | -66.9855 | 0.018674 | -67.0978 | 56.1985 | 56.477 | 56.2925 | -67.166 | -0.07732 | -0.039332 | -0.032834 | 0.046267 | 0.12359 | -0.24018 | -0.13915 | -0.19058 | -0.2666 | -0.010075 | -0.12242 | 0.06816 | 0.011884 | -0.17264 | 123.4012 | 123.2004 | 123.3014 | 66.9905 | -123.5179 | 123.1739 | 123.4524 | 123.2679 | 66.9941 | -123.6311
351.2656 | 123.761 | -66.9754 | 56.488 | 0.077612 | -0.0077302 | -0.0037395 | 0.044912 | -0.0076459 | 0.044054 | 0.065477 | -0.0070587 | -0.006462 | 0.052054 | 0.04395 | 0.046001 | -67.0082 | 0.0243 | -66.92 | 56.4258 | 56.2158 | 56.326 | -67.0436 | -66.9809 | 0.018674 | -67.0887 | 56.2031 | 56.4725 | 56.3017 | -67.166 | -0.068162 | -0.06222 | -0.032834 | 0.055424 | 0.12359 | -0.27222 | -0.16204 | -0.19058 | -0.28491 | -0.005496 | -0.11326 | 0.077318 | -0.015583 | -0.18637 | 123.4012 | 123.1912 | 123.3014 | 66.9997 | -123.5316 | 123.1785 | 123.4479 | 123.2771 | 66.9941 | -123.654
352.2656 | 123.7747 | -66.9525 | 56.5155 | 0.06235 | -0.0087982 | -0.0037395 | 0.043843 | -0.0076459 | 0.042985 | 0.065477 | -0.0038537 | -0.006462 | 0.050986 | 0.046087 | 0.044933 | -67.0037 | 0.005985 | -66.92 | 56.435 | 56.2112 | 56.326 | -67.0619 | -66.9855 | 0.009516 | -67.0887 | 56.1985 | 56.4725 | 56.3291 | -67.1751 | -0.10937 | -0.080529 | -0.051144 | 0.032536 | 0.1419 | -0.30427 | -0.18951 | -0.22262 | -0.31696 | -0.032963 | -0.13615 | 0.086475 | -0.043049 | -0.18636 | 123.3875 | 123.1638 | 123.2785 | 66.9585 | -123.5774 | 123.1511 | 123.425 | 123.2817 | 66.962 | -123.6906
353.2656 | 123.7839 | -66.9662 | 56.4926 | 0.077612 | -0.0066612 | -0.0037395 | 0.044912 | -0.0076459 | 0.044054 | 0.065477 | -0.0049217 | -0.005394 | 0.050986 | 0.048223 | 0.044933 | -67.0128 | 0.010564 | -66.9246 | 56.4212 | 56.2204 | 56.3214 | -67.0481 | -66.9855 | 0.014095 | -67.0887 | 56.2031 | 56.4725 | 56.3108 | -67.1797 | -0.081896 | -0.071376 | -0.046568 | 0.04169 | 0.12359 | -0.27222 | -0.1712 | -0.21347 | -0.28949 | -0.01923 | -0.12242 | 0.091054 | -0.020161 | -0.18179 | 123.3875 | 123.1866 | 123.2877 | 66.9768 | -123.5408 | 123.1694 | 123.4387 | 123.2771 | 66.9803 | -123.6723
354.2656 | 123.6694 | -67.0166 | 56.543 | 0.06235 | -0.0087982 | -0.0037395 | 0.042775 | -0.0065769 | 0.044054 | 0.065477 | -0.0059907 | -0.006462 | 0.050986 | 0.046087 | 0.046001 | -66.9991 | 0.010564 | -66.9246 | 56.4304 | 56.2204 | 56.3214 | -67.0573 | -66.9809 | 0.018674 | -67.0841 | 56.2031 | 56.477 | 56.3337 | -67.1751 | -0.0407 | -0.11257 | 0.017522 | 0.092044 | 0.13274 | -0.32257 | -0.22155 | -0.15854 | -0.33984 | 0.035703 | -0.067483 | 0.091053 | -0.065936 | -0.20925 | 123.447 | 123.237 | 123.338 | 67.0272 | -123.6003 | 123.2197 | 123.4936 | 123.3503 | 67.0353 | -123.7181
355.2656 | 123.7518 | -67.012 | 56.4743 | 0.031826 | -0.0098662 | -0.0037395 | 0.044912 | -0.0065769 | 0.044054 | 0.065477 | -0.0059907 | -0.006462 | 0.049918 | 0.047155 | 0.046001 | -67.0082 | 0.010564 | -66.9154 | 56.4212 | 56.2204 | 56.3214 | -67.0481 | -66.9809 | 0.004938 | -67.0887 | 56.1985 | 56.477 | 56.3154 | -67.1751 | -0.03612 | -0.053065 | 0.003787 | 0.096623 | 0.13274 | -0.25391 | -0.15288 | -0.16311 | -0.27576 | 0.031125 | -0.076639 | 0.086475 | 0.002729 | -0.1589 | 123.4333 | 123.2324 | 123.3334 | 67.0226 | -123.5224 | 123.2106 | 123.4891 | 123.3274 | 67.017 | -123.6494
356.2656 | 123.7427 | -66.98 | 56.4743 | 0.077612 | -0.0077302 | -0.0048075 | 0.044912 | -0.0044409 | 0.044054 | 0.080738 | -0.0059907 | -0.006462 | 0.050986 | 0.047155 | 0.04707 | -67.0037 | 0.015142 | -66.9246 | 56.4258 | 56.2204 | 56.326 | -67.0619 | -66.9763 | 0.014095 | -67.0887 | 56.1985 | 56.4725 | 56.3291 | -67.1751 | -0.081901 | -0.048487 | -0.023679 | 0.055422 | 0.13732 | -0.25391 | -0.14831 | -0.19516 | -0.27576 | 0.00366 | -0.10868 | 0.086475 | -0.00185 | -0.14516 | 123.4058 | 123.2004 | 123.306 | 66.9951 | -123.5362 | 123.1785 | 123.4524 | 123.3091 | 66.9941 | -123.6494
357.2656 | 123.7427 | -66.9846 | 56.4743 | 0.06235 | -0.0077302 | -0.0037395 | 0.043843 | -0.0076459 | 0.040849 | 0.034955 | -0.0049217 | -0.006462 | 0.050986 | 0.046087 | 0.046001 | -67.0128 | 0.010564 | -66.9246 | 56.4258 | 56.2112 | 56.3214 | -67.0436 | -66.9855 | 0.014095 | -67.0887 | 56.1985 | 56.4725 | 56.3337 | -67.1614 | -0.059007 | -0.048487 | -0.028258 | 0.06 | 0.11901 | -0.26307 | -0.15288 | -0.17684 | -0.27576 | -0.00092 | -0.1041 | 0.072739 | -0.00185 | -0.14058 | 123.4104 | 123.1958 | 123.306 | 66.9951 | -123.5179 | 123.1831 | 123.457 | 123.3183 | 66.9987 | -123.6357
358.2656 | 123.7289 | -66.9708 | 56.4835 | 0.06235 | -0.0087982 | -0.0037395 | 0.042775 | -0.0087139 | 0.044054 | 0.050216 | -0.0070587 | -0.006462 | 0.052054 | 0.047155 | 0.044933 | -67.0082 | 0.015142 | -66.92 | 56.4258 | 56.225 | 56.3214 | -67.039 | -66.9809 | 0.014095 | -67.0932 | 56.1985 | 56.4679 | 56.2879 | -67.166 | -0.068162 | -0.057642 | -0.037412 | 0.050846 | 0.11901 | -0.25849 | -0.16204 | -0.19516 | -0.28491 | -0.010074 | -0.12242 | 0.072739 | -0.015583 | -0.19553 | 123.3966 | 123.1958 | 123.2922 | 66.986 | -123.5224 | 123.1694 | 123.4387 | 123.2588 | 66.9849 | -123.6494
359.2656 | 123.7976 | -66.9525 | 56.5018 | 0.06235 | -0.0087982 | -0.0048075 | 0.044912 | -0.0076459 | 0.044054 | 0.065477 | -0.0070587 | -0.006462 | 0.052054 | 0.046087 | 0.044933 | -67.0128 | 0.015142 | -66.9291 | 56.4258 | 56.2204 | 56.3168 | -67.0619 | -66.9763 | 0.018674 | -67.0887 | 56.1985 | 56.477 | 56.3108 | -67.1751 | -0.10937 | -0.075953 | -0.060301 | 0.023379 | 0.13274 | -0.28137 | -0.18493 | -0.22262 | -0.30322 | -0.023805 | -0.13615 | 0.086475 | -0.024737 | -0.19094 | 123.3783 | 123.1729 | 123.2694 | 66.9677 | -123.5637 | 123.1511 | 123.4295 | 123.2633 | 66.9712 | -123.6769
360.2656 | 123.761 | -66.9846 | 56.5018 | 0.077612 | -0.0087982 | -0.0037395 | 0.043843 | -0.0044409 | 0.044054 | 0.050216 | -0.0038537 | -0.007531 | 0.049918 | 0.047155 | 0.044933 | -67.0037 | 0.010564 | -66.92 | 56.435 | 56.2204 | 56.3214 | -67.0436 | -66.9855 | 0.014095 | -67.0978 | 56.2031 | 56.4725 | 56.3383 | -67.1706 | -0.059007 | -0.066796 | -0.019101 | 0.064579 | 0.12359 | -0.28137 | -0.18035 | -0.186 | -0.29865 | -0.00092 | -0.11326 | 0.072739 | -0.029316 | -0.16347 | 123.4195 | 123.205 | 123.306 | 66.9951 | -123.5453 | 123.1877 | 123.457 | 123.3229 | 66.9987 | -123.6723
361.2656 | 123.7473 | -66.9937 | 56.4606 | 0.06235 | -0.0087982 | -0.0016025 | 0.042775 | -0.0065769 | 0.042985 | 0.050216 | -0.0049217 | -0.007531 | 0.050986 | 0.048223 | 0.044933 | -67.0128 | 0.015142 | -66.92 | 56.4212 | 56.225 | 56.326 | -67.0436 | -66.9809 | 0.014095 | -67.0887 | 56.2031 | 56.4725 | 56.32 | -67.1751 | -0.049852 | -0.039332 | -0.019103 | 0.073734 | 0.12359 | -0.2356 | -0.13457 | -0.18143 | -0.25745 | 0.012814 | -0.09495 | 0.086475 | 0.011883 | -0.14059 | 123.415 | 123.2187 | 123.3197 | 67.0089 | -123.5041 | 123.1968 | 123.4662 | 123.3137 | 67.0078 | -123.6357
362.2656 | 123.7106 | -67.0166 | 56.4651 | 0.06235 | -0.0077302 | -0.0048075 | 0.042775 | -0.0076459 | 0.042985 | 0.065477 | -0.0059907 | -0.007531 | 0.053122 | 0.047155 | 0.044933 | -67.0037 | 0.005985 | -66.9291 | 56.4258 | 56.2204 | 56.326 | -67.0573 | -66.9763 | 0.018674 | -67.0887 | 56.1985 | 56.4816 | 56.3246 | -67.1706 | -0.0407 | -0.039332 | 0.012943 | 0.087466 | 0.12817 | -0.24475 | -0.13915 | -0.15396 | -0.2666 | 0.040282 | -0.072061 | 0.081897 | 0.016462 | -0.14059 | 123.4424 | 123.237 | 123.3426 | 67.0226 | -123.5225 | 123.2151 | 123.4982 | 123.3412 | 67.0353 | -123.6357
363.2656 | 123.7335 | -67.0074 | 56.4972 | 0.031826 | -0.0087982 | -0.0026705 | 0.044912 | -0.0076459 | 0.041917 | 0.080738 | -0.0059907 | -0.006462 | 0.050986 | 0.046087 | 0.044933 | -67.0082 | 0.015142 | -66.92 | 56.4304 | 56.2204 | 56.326 | -67.0481 | -66.9809 | 0.018674 | -67.0932 | 56.2031 | 56.4725 | 56.3246 | -67.1706 | -0.040698 | -0.066796 | -0.000791 | 0.087467 | 0.12816 | -0.2768 | -0.17119 | -0.16311 | -0.29407 | 0.026547 | -0.085796 | 0.077318 | -0.024738 | -0.17263 | 123.4378 | 123.2278 | 123.3334 | 67.0226 | -123.5453 | 123.2106 | 123.4799 | 123.332 | 67.0261 | -123.6678
364.2656 | 123.7793 | -66.98 | 56.4926 | 0.077612 | -0.010935 | -0.0037395 | 0.043843 | -0.0097819 | 0.041917 | 0.080738 | -0.0049217 | -0.008599 | 0.050986 | 0.047155 | 0.043865 | -67.0037 | 0.019721 | -66.92 | 56.4212 | 56.2204 | 56.3214 | -67.0527 | -66.9809 | 0.004938 | -67.0932 | 56.1985 | 56.4816 | 56.3337 | -67.1751 | -0.072743 | -0.071376 | -0.023679 | 0.060001 | 0.13274 | -0.27222 | -0.1712 | -0.19516 | -0.29407 | -0.000919 | -0.11326 | 0.081896 | -0.011004 | -0.1589 | 123.4012 | 123.2004 | 123.3014 | 66.9997 | -123.5453 | 123.1785 | 123.4616 | 123.3137 | 66.9849 | -123.6678
365.2656 | 123.7335 | -66.9983 | 56.4835 | 0.047088 | -0.0087982 | -0.0048075 | 0.042775 | -0.0055089 | 0.042985 | 0.080738 | -0.0049217 | -0.007531 | 0.049918 | 0.047155 | 0.046001 | -67.0128 | 0.010564 | -66.92 | 56.4258 | 56.225 | 56.326 | -67.0481 | -66.9809 | 0.018674 | -67.0932 | 56.194 | 56.4816 | 56.3246 | -67.1751 | -0.049853 | -0.057642 | -0.014525 | 0.078312 | 0.12816 | -0.25849 | -0.15746 | -0.17685 | -0.28949 | 0.017392 | -0.094951 | 0.081896 | -0.001848 | -0.1589 | 123.4241 | 123.2233 | 123.3243 | 67.0089 | -123.5316 | 123.1923 | 123.4799 | 123.3229 | 67.017 | -123.6586
366.2656 | 123.7289 | -66.9662 | 56.4926 | 0.06235 | -0.0087982 | -0.0037395 | 0.043843 | -0.0076459 | 0.040849 | 0.080738 | -0.0059907 | -0.007531 | 0.050986 | 0.048223 | 0.043865 | -67.0082 | 0.019721 | -66.9246 | 56.4304 | 56.2204 | 56.3214 | -67.0527 | -66.9901 | 0.014095 | -67.0887 | 56.1985 | 56.477 | 56.3062 | -67.1797 | -0.086475 | -0.062219 | -0.041989 | 0.04169 | 0.12816 | -0.27222 | -0.1712 | -0.21347 | -0.29407 | -0.023808 | -0.12242 | 0.091054 | -0.015582 | -0.18637 | 123.3966 | 123.1866 | 123.2877 | 66.986 | -123.5453 | 123.1648 | 123.4433 | 123.2725 | 66.9803 | -123.6723
367.3281 | 123.6511 | -67.0166 | 56.5247 | 0.06235 | -0.0098662 | -0.0016025 | 0.043843 | -0.0065769 | 0.041917 | 0.065477 | -0.0059907 | -0.007531 | 0.050986 | 0.049292 | 0.044933 | -67.0128 | 0.019721 | -66.9246 | 56.4396 | 56.2296 | 56.3214 | -67.0573 | -66.9855 | 0.023253 | -67.0841 | 56.1985 | 56.4679 | 56.32 | -67.1706 | -0.0407 | -0.085105 | 0.003786 | 0.092044 | 0.13274 | -0.29511 | -0.20324 | -0.15396 | -0.32611 | 0.031124 | -0.067483 | 0.086475 | -0.056782 | -0.20468 | 123.4562 | 123.2462 | 123.338 | 67.0363 | -123.582 | 123.2151 | 123.4845 | 123.3366 | 67.0399 | -123.6952
368.2656 | 123.7564 | -66.9754 | 56.4377 | 0.047088 | -0.0087982 | -0.0026705 | 0.04598 | -0.0076459 | 0.040849 | 0.050216 | -0.0049217 | -0.007531 | 0.050986 | 0.048223 | 0.042797 | -67.0082 | 0.010564 | -66.9154 | 56.4304 | 56.2204 | 56.3306 | -67.0481 | -66.9809 | 0.014095 | -67.0887 | 56.2031 | 56.4725 | 56.3383 | -67.1751 | -0.072741 | -0.007287 | -0.032834 | 0.060002 | 0.13274 | -0.21729 | -0.10711 | -0.19974 | -0.23456 | -0.005496 | -0.11326 | 0.086475 | 0.034771 | -0.099386 | 123.4058 | 123.1958 | 123.306 | 66.986 | -123.4858 | 123.1785 | 123.4479 | 123.3137 | 66.9895 | -123.6128
369.2656 | 123.7427 | -66.9754 | 56.4789 | 0.06235 | -0.0087982 | -0.0037395 | 0.044912 | -0.0076459 | 0.042985 | 0.050216 | -0.0049217 | -0.006462 | 0.050986 | 0.049292 | 0.044933 | -67.0037 | 0.019721 | -66.9246 | 56.4258 | 56.2067 | 56.326 | -67.0436 | -66.9809 | 0.014095 | -67.0932 | 56.194 | 56.4725 | 56.3017 | -67.1751 | -0.068162 | -0.053065 | -0.028256 | 0.050845 | 0.11901 | -0.27222 | -0.15288 | -0.19974 | -0.28491 | -0.005496 | -0.11784 | 0.081896 | -0.006428 | -0.17721 | 123.4012 | 123.1821 | 123.3014 | 66.9951 | -123.5224 | 123.1694 | 123.4479 | 123.2771 | 66.9895 | -123.654
370.2656 | 123.7473 | -67.0029 | 56.4835 | 0.06235 | -0.0087982 | -0.0026705 | 0.043843 | -0.0087139 | 0.042985 | 0.065477 | -0.0059907 | -0.007531 | 0.050986 | 0.049292 | 0.046001 | -67.0082 | 0.019721 | -66.9154 | 56.4212 | 56.2204 | 56.326 | -67.0527 | -66.9809 | 0.014095 | -67.0887 | 56.1985 | 56.477 | 56.2834 | -67.166 | -0.049854 | -0.06222 | -0.005368 | 0.087468 | 0.13732 | -0.26306 | -0.15746 | -0.16311 | -0.28491 | 0.02197 | -0.085794 | 0.077318 | -0.006426 | -0.20011 | 123.4241 | 123.2233 | 123.3289 | 67.0226 | -123.5362 | 123.2014 | 123.4799 | 123.2862 | 67.017 | -123.6494
371.2656 | 123.7564 | -66.9708 | 56.4514 | 0.06235 | -0.0087982 | -0.0026705 | 0.042775 | -0.0076459 | 0.042985 | 0.080738 | -0.0049217 | -0.007531 | 0.052054 | 0.05036 | 0.043865 | -67.0037 | 0.015142 | -66.92 | 56.4258 | 56.2158 | 56.3306 | -67.0527 | -66.9809 | 0.009516 | -67.0932 | 56.2077 | 56.477 | 56.32 | -67.1751 | -0.081898 | -0.025599 | -0.032834 | 0.050846 | 0.13274 | -0.2356 | -0.12084 | -0.20431 | -0.24371 | -0.010074 | -0.12242 | 0.081896 | 0.025617 | -0.13143 | 123.3966 | 123.1866 | 123.3014 | 66.986 | -123.5041 | 123.1785 | 123.4479 | 123.2908 | 66.9803 | -123.6266
372.2656 | 123.7518 | -66.98 | 56.4651 | 0.047088 | -0.010935 | -0.0048075 | 0.043843 | -0.0065769 | 0.041917 | 0.080738 | -0.0049217 | -0.006462 | 0.052054 | 0.05036 | 0.043865 | -67.0037 | 0.015142 | -66.9246 | 56.4304 | 56.2112 | 56.3214 | -67.0481 | -66.9809 | 0.009516 | -67.0978 | 56.194 | 56.4725 | 56.3337 | -67.1889 | -0.068164 | -0.034753 | -0.023679 | 0.055422 | 0.12359 | -0.25391 | -0.14373 | -0.20889 | -0.27118 | -0.000919 | -0.11784 | 0.091054 | 0.007305 | -0.13143 | 123.4104 | 123.1912 | 123.3014 | 66.9951 | -123.5133 | 123.1739 | 123.4524 | 123.3137 | 66.9895 | -123.654
373.2656 | 123.7473 | -67.0258 | 56.488 | 0.06235 | -0.0098662 | -0.0037395 | 0.043843 | -0.0076459 | 0.041917 | 0.065477 | -0.0070587 | -0.007531 | 0.049918 | 0.048223 | 0.042797 | -67.0082 | 0.010564 | -66.9154 | 56.4304 | 56.2112 | 56.326 | -67.0436 | -66.9763 | 0.014095 | -67.0841 | 56.194 | 56.477 | 56.3017 | -67.1797 | -0.017808 | -0.057641 | 0.01752 | 0.11036 | 0.12816 | -0.2768 | -0.16204 | -0.15396 | -0.29407 | 0.049437 | -0.058328 | 0.095632 | -0.011004 | -0.18637 | 123.4562 | 123.237 | 123.3518 | 67.0363 | -123.5316 | 123.2197 | 123.5028 | 123.3274 | 67.0399 | -123.6678
374.2812 | 123.7564 | -66.9571 | 56.4743 | 0.06235 | -0.010935 | -0.0037395 | 0.043843 | -0.0087139 | 0.041917 | 0.065477 | -0.0049217 | -0.007531 | 0.049918 | 0.049292 | 0.044933 | -67.0082 | 0.010564 | -66.9108 | 56.4304 | 56.2204 | 56.326 | -67.0481 | -66.9763 | 0.014095 | -67.0841 | 56.1985 | 56.4725 | 56.3062 | -67.1706 | -0.091052 | -0.043908 | -0.051145 | 0.046269 | 0.13732 | -0.25391 | -0.14831 | -0.21347 | -0.27576 | -0.019228 | -0.12699 | 0.086475 | -0.00185 | -0.16806 | 123.3875 | 123.1775 | 123.2831 | 66.9677 | -123.5224 | 123.1556 | 123.4295 | 123.2633 | 66.9712 | -123.6449
375.2656 | 123.7656 | -66.9983 | 56.4697 | 0.047088 | -0.0098662 | -0.0048075 | 0.041706 | -0.0055089 | 0.042985 | 0.050216 | -0.0049217 | -0.007531 | 0.049918 | 0.049292 | 0.044933 | -67.0037 | 0.015142 | -66.92 | 56.4258 | 56.2112 | 56.3306 | -67.0527 | -66.9763 | 0.014095 | -67.0932 | 56.194 | 56.4725 | 56.3246 | -67.1751 | -0.054432 | -0.04391 | -0.005368 | 0.078312 | 0.13274 | -0.25849 | -0.13915 | -0.17685 | -0.27576 | 0.021971 | -0.094951 | 0.081896 | 0.002727 | -0.14516 | 123.4241 | 123.2095 | 123.3289 | 67.0134 | -123.5224 | 123.1923 | 123.4707 | 123.3229 | 67.0124 | -123.6449
376.2656 | 123.7015 | -66.9891 | 56.4835 | 0.047088 | -0.0098662 | -0.0037395 | 0.044912 | -0.0076459 | 0.041917 | 0.050216 | -0.0070587 | -0.006462 | 0.048849 | 0.048223 | 0.042797 | -67.0037 | 0.015142 | -66.92 | 56.4304 | 56.2158 | 56.326 | -67.0527 | -66.9763 | 0.018674 | -67.0795 | 56.1894 | 56.4725 | 56.3154 | -67.1751 | -0.063587 | -0.053063 | -0.014523 | 0.069157 | 0.13274 | -0.26764 | -0.15746 | -0.186 | -0.29407 | 0.012816 | -0.09037 | 0.095632 | -0.011005 | -0.16806 | 123.4195 | 123.205 | 123.3151 | 67.0043 | -123.5362 | 123.1785 | 123.4616 | 123.3045 | 67.0078 | -123.6586
377.2656 | 123.7656 | -67.0074 | 56.4606 | 0.06235 | -0.0087982 | -0.0048075 | 0.043843 | -0.0055089 | 0.041917 | 0.050216 | -0.0059907 | -0.006462 | 0.048849 | 0.048223 | 0.043865 | -67.0037 | 0.015142 | -66.9291 | 56.4258 | 56.2158 | 56.326 | -67.0481 | -66.9809 | 0.014095 | -67.0795 | 56.1985 | 56.4725 | 56.2925 | -67.1751 | -0.040698 | -0.034754 | 0.003787 | 0.07831 | 0.11901 | -0.24476 | -0.13457 | -0.16769 | -0.26203 | 0.026547 | -0.07206 | 0.095632 | 0.011883 | -0.16806 | 123.4333 | 123.2233 | 123.3334 | 67.0226 | -123.5087 | 123.206 | 123.4799 | 123.3 | 67.0215 | -123.6357
378.2656 | 123.7152 | -67.012 | 56.4651 | 0.031826 | -0.0098662 | -0.0048075 | 0.042775 | -0.0076459 | 0.041917 | 0.050216 | -0.0059907 | -0.006462 | 0.050986 | 0.05036 | 0.043865 | -67.0037 | 0.015142 | -66.9154 | 56.4304 | 56.2158 | 56.3214 | -67.0436 | -66.9809 | 0.014095 | -67.0932 | 56.1894 | 56.4725 | 56.3337 | -67.1751 | -0.031541 | -0.034753 | 0.008365 | 0.096623 | 0.12816 | -0.24933 | -0.14373 | -0.16311 | -0.27576 | 0.031125 | -0.081218 | 0.081896 | 0.007305 | -0.13143 | 123.4424 | 123.2278 | 123.3334 | 67.0272 | -123.5087 | 123.2014 | 123.4845 | 123.3457 | 67.0261 | -123.6403
379.2812 | 123.7152 | -66.9846 | 56.4926 | 0.06235 | -0.010935 | -0.0026705 | 0.043843 | -0.0065769 | 0.041917 | 0.080738 | -0.0059907 | -0.007531 | 0.050986 | 0.05036 | 0.046001 | -67.0037 | 0.010564 | -66.92 | 56.4304 | 56.225 | 56.326 | -67.0481 | -66.9763 | 0.018674 | -67.0932 | 56.194 | 56.4679 | 56.3062 | -67.1751 | -0.063586 | -0.062219 | -0.019101 | 0.064579 | 0.12816 | -0.26764 | -0.16662 | -0.19058 | -0.29865 | 0.008238 | -0.10868 | 0.081896 | -0.024739 | -0.18637 | 123.415 | 123.2095 | 123.3106 | 66.9951 | -123.5408 | 123.1785 | 123.4524 | 123.2908 | 67.0032 | -123.6678
380.2656 | 123.7198 | -66.9937 | 56.4972 | 0.016564 | -0.0098662 | -0.0037395 | 0.043843 | -0.0065769 | 0.042985 | 0.065477 | -0.0059907 | -0.007531 | 0.048849 | 0.051428 | 0.043865 | -67.0128 | 0.019721 | -66.92 | 56.4258 | 56.1975 | 56.326 | -67.0573 | -66.9855 | 0.018674 | -67.0841 | 56.194 | 56.4725 | 56.265 | -67.1706 | -0.063589 | -0.071375 | -0.019103 | 0.073734 | 0.13732 | -0.29969 | -0.17119 | -0.17685 | -0.30322 | 0.008235 | -0.090372 | 0.086475 | -0.024738 | -0.23215 | 123.4195 | 123.1912 | 123.3197 | 67.0134 | -123.5545 | 123.1877 | 123.4662 | 123.2588 | 67.0124 | -123.6678
381.2656 | 123.6786 | -67.0303 | 56.4926 | 0.047088 | -0.010935 | -0.0058765 | 0.042775 | -0.0065769 | 0.041917 | 0.065477 | -0.0070587 | -0.007531 | 0.049918 | 0.05036 | 0.043865 | -67.0082 | 0.015142 | -66.9246 | 56.4258 | 56.2158 | 56.3352 | -67.0527 | -66.9763 | 0.014095 | -67.0887 | 56.1894 | 56.4679 | 56.3246 | -67.1706 | -0.022389 | -0.066798 | 0.022097 | 0.10578 | 0.12816 | -0.2768 | -0.15746 | -0.14023 | -0.30323 | 0.054014 | -0.058329 | 0.081897 | -0.024739 | -0.16805 | 123.4562 | 123.2462 | 123.3655 | 67.0455 | -123.5453 | 123.2197 | 123.4982 | 123.3549 | 67.0444 | -123.6632
382.2656 | 123.6328 | -67.0349 | 56.4972 | 0.047088 | -0.0098662 | -0.0037395 | 0.042775 | -0.0055089 | 0.041917 | 0.050216 | -0.0049217 | -0.007531 | 0.048849 | 0.05036 | 0.043865 | -67.0037 | 0.015142 | -66.9246 | 56.435 | 56.2204 | 56.3306 | -67.0527 | -66.9855 | 0.018674 | -67.0841 | 56.194 | 56.4679 | 56.3108 | -67.1706 | -0.017811 | -0.062218 | 0.031253 | 0.11035 | 0.12816 | -0.2768 | -0.16662 | -0.13565 | -0.30322 | 0.049434 | -0.049173 | 0.086475 | -0.029316 | -0.18637 | 123.4699 | 123.2553 | 123.3655 | 67.0501 | -123.5499 | 123.2289 | 123.5028 | 123.3457 | 67.0536 | -123.6678
383.2812 | 123.7198 | -66.9754 | 56.4743 | 0.06235 | -0.0098662 | -0.0048075 | 0.042775 | -0.0055089 | 0.041917 | 0.065477 | -0.0049217 | -0.005394 | 0.049918 | 0.052497 | 0.042797 | -67.0037 | 0.019721 | -66.9246 | 56.4212 | 56.2204 | 56.3352 | -67.0619 | -66.9855 | 0.018674 | -67.0887 | 56.194 | 56.4725 | 56.3017 | -67.1797 | -0.086478 | -0.053065 | -0.028256 | 0.050845 | 0.13732 | -0.25391 | -0.13915 | -0.20431 | -0.28034 | -0.010075 | -0.11326 | 0.091054 | -0.00185 | -0.17263 | 123.3966 | 123.1958 | 123.3106 | 66.9951 | -123.5362 | 123.1694 | 123.4479 | 123.2771 | 66.9941 | -123.654
384.2812 | 123.7106 | -67.0074 | 56.4423 | 0.047088 | -0.0098662 | -0.0058765 | 0.042775 | -0.0033719 | 0.041917 | 0.065477 | -0.0049217 | -0.007531 | 0.049918 | 0.052497 | 0.042797 | -67.0037 | 0.015142 | -66.92 | 56.4304 | 56.2021 | 56.3306 | -67.0344 | -66.9855 | 0.018674 | -67.0932 | 56.1985 | 56.4816 | 56.2879 | -67.1751 | -0.026962 | -0.011865 | 0.003787 | 0.087467 | 0.11443 | -0.24018 | -0.11169 | -0.16769 | -0.24372 | 0.021968 | -0.085796 | 0.081896 | 0.03935 | -0.15433 | 123.4378 | 123.2095 | 123.338 | 67.0226 | -123.4767 | 123.206 | 123.4891 | 123.2954 | 67.0261 | -123.6174
385.2656 | 123.6008 | -67.0258 | 56.5201 | 0.047088 | -0.0098662 | -0.0048075 | 0.042775 | -0.0065769 | 0.041917 | 0.065477 | -0.0059907 | -0.005394 | 0.050986 | 0.051428 | 0.042797 | -66.9991 | 0.019721 | -66.92 | 56.4304 | 56.2158 | 56.326 | -67.0527 | -66.9809 | 0.009516 | -67.0841 | 56.1985 | 56.4725 | 56.2788 | -67.1751 | -0.026966 | -0.089685 | 0.026677 | 0.10578 | 0.13274 | -0.30427 | -0.19408 | -0.14938 | -0.32154 | 0.044858 | -0.058328 | 0.091053 | -0.047627 | -0.2413 | 123.4562 | 123.2416 | 123.3518 | 67.0455 | -123.5728 | 123.2243 | 123.4982 | 123.3045 | 67.0353 | -123.6952
386.2656 | 123.6282 | -67.0349 | 56.4926 | 0.06235 | -0.0087982 | -0.0058765 | 0.041706 | -0.0065769 | 0.041917 | 0.050216 | -0.0049217 | -0.006462 | 0.047781 | 0.049292 | 0.043865 | -67.0082 | 0.019721 | -66.92 | 56.4304 | 56.2112 | 56.326 | -67.0436 | -66.9809 | 0.014095 | -67.0841 | 56.194 | 56.4679 | 56.2834 | -67.1751 | -0.008653 | -0.062219 | 0.026675 | 0.11493 | 0.12359 | -0.28138 | -0.16662 | -0.14023 | -0.29865 | 0.054013 | -0.049173 | 0.091053 | -0.024739 | -0.20926 | 123.4653 | 123.2461 | 123.3609 | 67.0546 | -123.5362 | 123.2289 | 123.5028 | 123.3183 | 67.049 | -123.6678
387.2656 | 123.6053 | -67.0395 | 56.5063 | 0.047088 | -0.0098662 | -0.0048075 | 0.040638 | -0.0076459 | 0.040849 | 0.050216 | -0.0070587 | -0.007531 | 0.048849 | 0.051428 | 0.043865 | -67.0037 | 0.019721 | -66.9291 | 56.4304 | 56.2158 | 56.326 | -67.0527 | -66.9855 | 0.023253 | -67.0887 | 56.194 | 56.477 | 56.2971 | -67.1797 | -0.013233 | -0.075952 | 0.035831 | 0.11035 | 0.12359 | -0.29053 | -0.18035 | -0.14023 | -0.31238 | 0.054012 | -0.049173 | 0.091054 | -0.029315 | -0.20926 | 123.4699 | 123.2553 | 123.3655 | 67.0592 | -123.5591 | 123.2335 | 123.5165 | 123.3366 | 67.0627 | -123.6861
388.2812 | 123.7335 | -66.9983 | 56.4514 | 0.077612 | -0.0098662 | -0.0058765 | 0.041706 | -0.0065769 | 0.042985 | 0.050216 | -0.0049217 | -0.005394 | 0.049918 | 0.051428 | 0.043865 | -66.9991 | 0.015142 | -66.9246 | 56.4258 | 56.2112 | 56.3306 | -67.0665 | -66.9855 | 0.018674 | -67.0841 | 56.194 | 56.4725 | 56.2788 | -67.1797 | -0.068169 | -0.025599 | -0.000789 | 0.073733 | 0.1419 | -0.24018 | -0.12084 | -0.18143 | -0.25745 | 0.012813 | -0.085794 | 0.095632 | 0.021038 | -0.17264 | 123.4241 | 123.2095 | 123.3289 | 67.0134 | -123.5179 | 123.1923 | 123.4707 | 123.2771 | 67.017 | -123.6311
389.2812 | 123.7335 | -66.9891 | 56.4606 | 0.047088 | -0.010935 | -0.0048075 | 0.042775 | -0.0076459 | 0.041917 | 0.065477 | -0.0070587 | -0.006462 | 0.049918 | 0.053565 | 0.042797 | -67.0082 | 0.010564 | -66.92 | 56.4258 | 56.2158 | 56.326 | -67.0481 | -66.9901 | 0.014095 | -67.0841 | 56.194 | 56.477 | 56.2879 | -67.1751 | -0.059008 | -0.034754 | -0.019101 | 0.069157 | 0.12816 | -0.24476 | -0.13457 | -0.186 | -0.2666 | -0.00092 | -0.094949 | 0.091053 | 0.016462 | -0.17264 | 123.415 | 123.205 | 123.3151 | 66.9997 | -123.5087 | 123.1831 | 123.4662 | 123.2771 | 67.0032 | -123.6357
390.2656 | 123.6694 | -66.9983 | 56.5018 | 0.06235 | -0.0087982 | -0.0048075 | 0.040638 | -0.0076459 | 0.041917 | 0.080738 | -0.0059907 | -0.004326 | 0.047781 | 0.051428 | 0.042797 | -66.9945 | 0.015142 | -66.9154 | 56.4304 | 56.2204 | 56.3352 | -67.0619 | -66.9855 | 0.018674 | -67.0749 | 56.1985 | 56.4725 | 56.3154 | -67.1751 | -0.06359 | -0.071374 | 0.003789 | 0.08289 | 0.14648 | -0.28137 | -0.16662 | -0.17685 | -0.30322 | 0.012813 | -0.076636 | 0.10021 | -0.029316 | -0.18637 | 123.4287 | 123.2187 | 123.3334 | 67.0134 | -123.5637 | 123.1968 | 123.4707 | 123.3137 | 67.017 | -123.6769
391.2656 | 123.642 | -67.0074 | 56.5018 | 0.047088 | -0.010935 | -0.0048075 | 0.042775 | -0.0065769 | 0.042985 | 0.065477 | -0.0038537 | -0.006462 | 0.049918 | 0.051428 | 0.043865 | -67.0082 | 0.019721 | -66.9246 | 56.4304 | 56.2204 | 56.3352 | -67.0436 | -66.9809 | 0.023253 | -67.0887 | 56.194 | 56.4725 | 56.3246 | -67.1751 | -0.036119 | -0.071374 | -0.000791 | 0.082888 | 0.11901 | -0.28137 | -0.16662 | -0.16769 | -0.3078 | 0.026547 | -0.081217 | 0.086475 | -0.029316 | -0.17721 | 123.4378 | 123.2278 | 123.3426 | 67.0272 | -123.5453 | 123.2014 | 123.4799 | 123.332 | 67.0307 | -123.6769
392.2656 | 123.6649 | -67.0074 | 56.4972 | 0.06235 | -0.0087982 | -0.0058765 | 0.041706 | -0.0076459 | 0.039781 | 0.065477 | -0.0059907 | -0.006462 | 0.050986 | 0.049292 | 0.042797 | -67.0037 | 0.0243 | -66.9337 | 56.4258 | 56.2112 | 56.326 | -67.0527 | -66.9855 | 0.018674 | -67.0795 | 56.194 | 56.477 | 56.3062 | -67.166 | -0.045277 | -0.071375 | 0.003787 | 0.073732 | 0.11901 | -0.28596 | -0.17119 | -0.15854 | -0.30322 | 0.021968 | -0.07206 | 0.086475 | -0.020159 | -0.19094 | 123.4333 | 123.2187 | 123.3334 | 67.0317 | -123.5499 | 123.2014 | 123.4845 | 123.3137 | 67.0261 | -123.6632
393.2812 | 123.7473 | -66.9891 | 56.4606 | 0.047088 | -0.010935 | -0.0048075 | 0.041706 | -0.0076459 | 0.042985 | 0.034955 | -0.0049217 | -0.006462 | 0.048849 | 0.05036 | 0.042797 | -66.9991 | 0.015142 | -66.92 | 56.4212 | 56.2112 | 56.326 | -67.0527 | -66.9763 | 0.014095 | -67.0795 | 56.194 | 56.477 | 56.2925 | -67.1706 | -0.063587 | -0.039332 | -0.009944 | 0.069157 | 0.13274 | -0.24933 | -0.13457 | -0.18142 | -0.2666 | 0.012816 | -0.09037 | 0.091054 | 0.016462 | -0.16806 | 123.4104 | 123.2004 | 123.3151 | 67.0043 | -123.5133 | 123.1831 | 123.4662 | 123.2816 | 67.0032 | -123.6311
394.2812 | 123.7656 | -66.9846 | 56.456 | 0.047088 | -0.0087982 | -0.0058765 | 0.042775 | -0.0076459 | 0.044054 | 0.065477 | -0.0038537 | -0.006462 | 0.049918 | 0.052497 | 0.042797 | -67.0037 | 0.015142 | -66.9246 | 56.435 | 56.2204 | 56.3397 | -67.0436 | -66.9901 | 0.014095 | -67.0795 | 56.1894 | 56.477 | 56.32 | -67.1797 | -0.059007 | -0.02102 | -0.019101 | 0.06 | 0.11901 | -0.2356 | -0.11626 | -0.19516 | -0.26661 | -0.005498 | -0.094948 | 0.10021 | 0.021039 | -0.13601 | 123.4195 | 123.205 | 123.3243 | 66.9997 | -123.4996 | 123.1739 | 123.4616 | 123.3045 | 66.9987 | -123.6357
395.2656 | 123.6328 | -67.0212 | 56.5063 | 0.077612 | -0.0098662 | -0.0058765 | 0.041706 | -0.0076459 | 0.040849 | 0.050216 | -0.0049217 | -0.003257 | 0.048849 | 0.053565 | 0.042797 | -67.0037 | 0.019721 | -66.9291 | 56.4396 | 56.2204 | 56.3306 | -67.0527 | -66.9855 | 0.023253 | -67.0841 | 56.194 | 56.4816 | 56.32 | -67.1706 | -0.031544 | -0.066795 | 0.01752 | 0.092043 | 0.12359 | -0.28595 | -0.17577 | -0.14938 | -0.31238 | 0.035701 | -0.062906 | 0.086475 | -0.024737 | -0.18637 | 123.4607 | 123.2416 | 123.3518 | 67.0409 | -123.5591 | 123.2151 | 123.5028 | 123.3412 | 67.0444 | -123.6769
396.2656 | 123.6786 | -67.012 | 56.5201 | 0.06235 | -0.0098662 | -0.0058765 | 0.040638 | -0.0065769 | 0.041917 | 0.080738 | -0.0049217 | -0.006462 | 0.049918 | 0.051428 | 0.043865 | -67.0037 | 0.0243 | -66.9291 | 56.435 | 56.225 | 56.326 | -67.0665 | -66.9855 | 0.018674 | -67.0932 | 56.1985 | 56.4725 | 56.2788 | -67.1797 | -0.054436 | -0.085107 | 0.008365 | 0.082888 | 0.13732 | -0.29511 | -0.19408 | -0.16769 | -0.32154 | 0.026546 | -0.081218 | 0.086475 | -0.047627 | -0.2413 | 123.447 | 123.237 | 123.338 | 67.0363 | -123.5865 | 123.2106 | 123.4845 | 123.2908 | 67.0307 | -123.6998
397.2656 | 123.6969 | -67.012 | 56.5063 | 0.047088 | -0.0098662 | -0.0037395 | 0.041706 | -0.0076459 | 0.039781 | 0.080738 | -0.0070587 | -0.006462 | 0.048849 | 0.051428 | 0.042797 | -66.9945 | 0.019721 | -66.92 | 56.435 | 56.2204 | 56.3352 | -67.0481 | -66.9809 | 0.018674 | -67.0841 | 56.194 | 56.477 | 56.3108 | -67.1797 | -0.03612 | -0.071374 | 0.017522 | 0.092045 | 0.12816 | -0.28595 | -0.17119 | -0.16769 | -0.31238 | 0.031125 | -0.072061 | 0.095632 | -0.029315 | -0.19552 | 123.447 | 123.2324 | 123.3472 | 67.0317 | -123.5545 | 123.206 | 123.4891 | 123.3228 | 67.0307 | -123.6861
398.2812 | 123.761 | -66.9937 | 56.4835 | 0.047088 | -0.0087982 | -0.0048075 | 0.040638 | -0.0076459 | 0.040849 | 0.065477 | -0.0059907 | -0.007531 | 0.048849 | 0.052497 | 0.043865 | -66.9991 | 0.019721 | -66.92 | 56.435 | 56.2021 | 56.326 | -67.0436 | -66.9763 | 0.009516 | -67.0795 | 56.194 | 56.4679 | 56.3017 | -67.1751 | -0.049852 | -0.048485 | -0.005367 | 0.073734 | 0.12359 | -0.28138 | -0.15746 | -0.18143 | -0.28949 | 0.017393 | -0.085793 | 0.095632 | -0.015583 | -0.18179 | 123.4287 | 123.1958 | 123.3197 | 67.0134 | -123.527 | 123.1877 | 123.4616 | 123.2954 | 67.0032 | -123.6586
399.2812 | 123.642 | -67.0349 | 56.4926 | 0.047088 | -0.0066612 | -0.0069445 | 0.041706 | -0.0087139 | 0.040849 | 0.050216 | -0.0059907 | -0.006462 | 0.048849 | 0.052497 | 0.041728 | -67.0082 | 0.010564 | -66.9246 | 56.4258 | 56.2112 | 56.326 | -67.0527 | -66.9855 | 0.018674 | -67.0795 | 56.1894 | 56.4725 | 56.2742 | -67.1751 | -0.017811 | -0.066798 | 0.026675 | 0.11035 | 0.12816 | -0.28138 | -0.16662 | -0.14023 | -0.30323 | 0.049434 | -0.044594 | 0.095632 | -0.020161 | -0.21842 | 123.4607 | 123.2461 | 123.3609 | 67.0455 | -123.5453 | 123.2243 | 123.5074 | 123.3091 | 67.0536 | -123.6678
400.2656 | 123.6603 | -67.0029 | 56.5063 | 0.06235 | -0.0098662 | -0.0048075 | 0.040638 | -0.0055089 | 0.040849 | 0.080738 | -0.0049217 | -0.007531 | 0.047781 | 0.052497 | 0.041728 | -67.0082 | 0.015142 | -66.9246 | 56.4304 | 56.2204 | 56.3352 | -67.0436 | -66.9809 | 0.014095 | -67.0932 | 56.194 | 56.4725 | 56.3154 | -67.1751 | -0.040696 | -0.075952 | -0.005368 | 0.078311 | 0.11901 | -0.28595 | -0.17119 | -0.17227 | -0.31238 | 0.02197 | -0.090373 | 0.081896 | -0.033894 | -0.19094 | 123.4333 | 123.2233 | 123.338 | 67.018 | -123.5499 | 123.1968 | 123.4753 | 123.3183 | 67.017 | -123.6815
401.2656 | 123.6832 | -67.0258 | 56.5018 | 0.047088 | -0.010935 | -0.0048075 | 0.041706 | -0.0076459 | 0.039781 | 0.065477 | -0.0070587 | -0.007531 | 0.048849 | 0.053565 | 0.04066 | -67.0037 | 0.0243 | -66.92 | 56.4304 | 56.2204 | 56.3352 | -67.0436 | -66.9855 | 0.014095 | -67.0841 | 56.194 | 56.4816 | 56.3017 | -67.1797 | -0.017808 | -0.071374 | 0.022098 | 0.10578 | 0.12359 | -0.28137 | -0.16662 | -0.15396 | -0.3078 | 0.040279 | -0.058328 | 0.095632 | -0.020159 | -0.2001 | 123.4562 | 123.2462 | 123.3609 | 67.0501 | -123.5453 | 123.2197 | 123.5074 | 123.3274 | 67.0399 | -123.6815
402.2656 | 123.6694 | -67.0166 | 56.5063 | 0.06235 | -0.0098662 | -0.0058765 | 0.041706 | -0.0076459 | 0.041917 | 0.095999 | -0.0059907 | -0.008599 | 0.048849 | 0.052497 | 0.042797 | -67.0037 | 0.019721 | -66.92 | 56.4258 | 56.225 | 56.3352 | -67.0527 | -66.9809 | 0.018674 | -67.0749 | 56.2031 | 56.4725 | 56.2834 | -67.1751 | -0.036121 | -0.080531 | 0.012943 | 0.096623 | 0.13274 | -0.28138 | -0.17119 | -0.15854 | -0.30322 | 0.035703 | -0.058325 | 0.10021 | -0.033894 | -0.22299 | 123.4424 | 123.2416 | 123.3518 | 67.0363 | -123.5591 | 123.2197 | 123.4891 | 123.3 | 67.0353 | -123.6815
403.2656 | 123.6649 | -67.0029 | 56.5338 | 0.047088 | -0.012003 | -0.0048075 | 0.041706 | -0.0055089 | 0.041917 | 0.065477 | -0.0059907 | -0.008599 | 0.046713 | 0.054633 | 0.042797 | -66.9945 | 0.019721 | -66.9246 | 56.4304 | 56.2204 | 56.3306 | -67.0481 | -66.9809 | 0.014095 | -67.0795 | 56.194 | 56.4725 | 56.2971 | -67.1751 | -0.045275 | -0.10342 | 0.008367 | 0.078311 | 0.12359 | -0.31342 | -0.20324 | -0.17227 | -0.33985 | 0.02197 | -0.076637 | 0.095632 | -0.061359 | -0.23672 | 123.4333 | 123.2233 | 123.3334 | 67.0226 | -123.582 | 123.1968 | 123.4753 | 123.3 | 67.017 | -123.709
404.2812 | 123.7244 | -67.0486 | 56.456 | 0.047088 | -0.0087982 | -0.0037395 | 0.041706 | -0.0087139 | 0.040849 | 0.065477 | -0.0070587 | -0.006462 | 0.048849 | 0.052497 | 0.043865 | -67.0037 | 0.015142 | -66.9246 | 56.4304 | 56.1929 | 56.3306 | -67.0436 | -66.9901 | 0.018674 | -67.0795 | 56.1985 | 56.477 | 56.32 | -67.1797 | 0.00508 | -0.025598 | 0.044986 | 0.12409 | 0.11901 | -0.26307 | -0.12542 | -0.13107 | -0.25745 | 0.058589 | -0.030861 | 0.10021 | 0.021039 | -0.13601 | 123.479 | 123.2416 | 123.3792 | 67.0638 | -123.4996 | 123.2472 | 123.5257 | 123.3686 | 67.0673 | -123.6357
405.2656 | 123.6603 | -66.9937 | 56.5247 | 0.077612 | -0.010935 | -0.0058765 | 0.041706 | -0.0087139 | 0.039781 | 0.095999 | -0.0070587 | -0.006462 | 0.049918 | 0.053565 | 0.043865 | -66.9991 | 0.019721 | -66.9154 | 56.4258 | 56.2158 | 56.3352 | -67.0527 | -66.9809 | 0.023253 | -67.0795 | 56.1985 | 56.4679 | 56.2925 | -67.1751 | -0.05901 | -0.098841 | -0.005367 | 0.078312 | 0.13732 | -0.30884 | -0.1895 | -0.18143 | -0.32611 | 0.012814 | -0.085793 | 0.095632 | -0.056782 | -0.23215 | 123.4195 | 123.2095 | 123.3289 | 67.0134 | -123.5774 | 123.1923 | 123.4616 | 123.2862 | 67.017 | -123.6998
406.2656 | 123.6969 | -66.9983 | 56.543 | 0.06235 | -0.010935 | -0.0048075 | 0.040638 | -0.0076459 | 0.041917 | 0.065477 | -0.0059907 | -0.007531 | 0.049918 | 0.053565 | 0.041728 | -66.9991 | 0.019721 | -66.9154 | 56.4304 | 56.225 | 56.3306 | -67.0573 | -66.9809 | 0.018674 | -67.0795 | 56.2031 | 56.4725 | 56.32 | -67.1751 | -0.059011 | -0.11257 | -0.000789 | 0.08289 | 0.1419 | -0.318 | -0.21239 | -0.17685 | -0.33984 | 0.017392 | -0.081215 | 0.095632 | -0.070515 | -0.22299 | 123.4287 | 123.2233 | 123.3289 | 67.018 | -123.6003 | 123.2014 | 123.4707 | 123.3183 | 67.017 | -123.7181
407.2656 | 123.6832 | -66.9891 | 56.5384 | 0.06235 | -0.012003 | -0.0048075 | 0.040638 | -0.0076459 | 0.040849 | 0.095999 | -0.0059907 | -0.007531 | 0.047781 | 0.055702 | 0.039592 | -66.9991 | 0.019721 | -66.9154 | 56.4304 | 56.2296 | 56.3306 | -67.0527 | -66.9809 | 0.014095 | -67.0703 | 56.194 | 56.477 | 56.3246 | -67.1751 | -0.063587 | -0.10799 | -0.009944 | 0.073735 | 0.13732 | -0.30884 | -0.20781 | -0.186 | -0.34442 | 0.008237 | -0.081213 | 0.10479 | -0.061358 | -0.21383 | 123.4195 | 123.2187 | 123.3197 | 67.0089 | -123.5911 | 123.1831 | 123.4662 | 123.3137 | 67.0032 | -123.7135
408.2656 | 123.6786 | -67.0074 | 56.5247 | 0.077612 | -0.010935 | -0.0037395 | 0.041706 | -0.0076459 | 0.041917 | 0.065477 | -0.0059907 | -0.006462 | 0.048849 | 0.053565 | 0.042797 | -67.0037 | 0.019721 | -66.92 | 56.435 | 56.2112 | 56.3306 | -67.0527 | -66.9809 | 0.018674 | -67.0841 | 56.2031 | 56.477 | 56.3246 | -67.1751 | -0.045277 | -0.089684 | 0.003787 | 0.087467 | 0.13274 | -0.31342 | -0.19408 | -0.16769 | -0.32153 | 0.026547 | -0.076639 | 0.091053 | -0.047625 | -0.2001 | 123.4424 | 123.2187 | 123.338 | 67.0272 | -123.5774 | 123.2106 | 123.4845 | 123.332 | 67.0261 | -123.6998
409.2812 | 123.6603 | -67.0395 | 56.5155 | 0.047088 | -0.010935 | -0.0058765 | 0.042775 | -0.0055089 | 0.039781 | 0.050216 | -0.0070587 | -0.006462 | 0.046713 | 0.054633 | 0.04066 | -66.9991 | 0.010564 | -66.92 | 56.4396 | 56.2204 | 56.3306 | -67.0481 | -66.9763 | 0.014095 | -67.0887 | 56.194 | 56.477 | 56.3291 | -67.1797 | -0.008654 | -0.07595 | 0.04041 | 0.11951 | 0.12816 | -0.29511 | -0.18493 | -0.14023 | -0.32154 | 0.06317 | -0.049173 | 0.091054 | -0.03847 | -0.18636 | 123.479 | 123.2599 | 123.3701 | 67.0501 | -123.5636 | 123.2335 | 123.5165 | 123.3686 | 67.0536 | -123.6952
410.2656 | 123.6511 | -66.9983 | 56.5247 | 0.077612 | -0.012003 | -0.0048075 | 0.040638 | -0.0065769 | 0.040849 | 0.065477 | -0.0070587 | -0.008599 | 0.048849 | 0.054633 | 0.042797 | -67.0037 | 0.015142 | -66.9246 | 56.435 | 56.2296 | 56.3397 | -67.0573 | -66.9946 | 0.009516 | -67.0887 | 56.1894 | 56.4725 | 56.2879 | -67.1797 | -0.059011 | -0.089684 | -0.005368 | 0.073733 | 0.13274 | -0.29511 | -0.18492 | -0.18143 | -0.33527 | 0.003656 | -0.090372 | 0.091054 | -0.052204 | -0.23672 | 123.4333 | 123.2278 | 123.338 | 67.0134 | -123.582 | 123.1877 | 123.4707 | 123.2862 | 67.0078 | -123.7044
411.2656 | 123.6237 | -67.012 | 56.5247 | 0.047088 | -0.012003 | -0.0048075 | 0.040638 | -0.0065769 | 0.038712 | 0.034955 | -0.0070587 | -0.006462 | 0.047781 | 0.053565 | 0.041728 | -66.9991 | 0.019721 | -66.92 | 56.435 | 56.225 | 56.326 | -67.0527 | -66.9855 | 0.014095 | -67.0841 | 56.2077 | 56.4679 | 56.3062 | -67.1751 | -0.040699 | -0.089684 | 0.012944 | 0.092045 | 0.13274 | -0.29969 | -0.19866 | -0.16311 | -0.31696 | 0.026546 | -0.072061 | 0.091053 | -0.056782 | -0.21841 | 123.447 | 123.237 | 123.338 | 67.0317 | -123.5774 | 123.2197 | 123.4799 | 123.3183 | 67.0261 | -123.6998
412.2656 | 123.6282 | -66.9983 | 56.5292 | 0.06235 | -0.012003 | -0.0048075 | 0.041706 | -0.0076459 | 0.040849 | 0.080738 | -0.0059907 | -0.007531 | 0.047781 | 0.054633 | 0.042797 | -67.0037 | 0.019721 | -66.9337 | 56.4304 | 56.2296 | 56.3397 | -67.071 | -66.9855 | 0.014095 | -67.0841 | 56.2031 | 56.4725 | 56.2971 | -67.1751 | -0.072748 | -0.09884 | -0.005368 | 0.064577 | 0.13733 | -0.29968 | -0.1895 | -0.17685 | -0.32611 | 0.012813 | -0.085794 | 0.091053 | -0.056782 | -0.23215 | 123.4287 | 123.2278 | 123.338 | 67.018 | -123.6003 | 123.2014 | 123.4707 | 123.2954 | 67.0124 | -123.7044
413.2656 | 123.5779 | -66.9937 | 56.5659 | 0.047088 | -0.010935 | -0.0048075 | 0.041706 | -0.0087139 | 0.039781 | 0.050216 | -0.0059907 | -0.007531 | 0.048849 | 0.053565 | 0.041728 | -66.9991 | 0.019721 | -66.92 | 56.4304 | 56.2296 | 56.326 | -67.0527 | -66.9763 | 0.018674 | -67.0841 | 56.1985 | 56.4725 | 56.3246 | -67.1843 | -0.05901 | -0.13546 | -0.005367 | 0.073734 | 0.13274 | -0.33631 | -0.23986 | -0.19058 | -0.36731 | 0.017393 | -0.090372 | 0.10021 | -0.093403 | -0.2413 | 123.4241 | 123.2233 | 123.3197 | 67.0134 | -123.6186 | 123.1923 | 123.4662 | 123.3183 | 67.0124 | -123.7502
414.2812 | 123.6603 | -67.0166 | 56.5292 | 0.06235 | -0.012003 | -0.0048075 | 0.03957 | -0.0076459 | 0.040849 | 0.080738 | -0.0070587 | -0.008599 | 0.048849 | 0.053565 | 0.04066 | -67.0082 | 0.015142 | -66.92 | 56.4441 | 56.2204 | 56.3352 | -67.0481 | -66.9717 | 0.018674 | -67.0841 | 56.1985 | 56.4725 | 56.3108 | -67.1751 | -0.031542 | -0.085105 | 0.008365 | 0.096623 | 0.12816 | -0.30884 | -0.19408 | -0.15854 | -0.33069 | 0.044861 | -0.067483 | 0.091053 | -0.056782 | -0.21841 | 123.4607 | 123.237 | 123.3518 | 67.0317 | -123.5774 | 123.2151 | 123.4891 | 123.3274 | 67.0353 | -123.7044
415.2656 | 123.6282 | -66.9891 | 56.543 | 0.06235 | -0.010935 | -0.0026705 | 0.041706 | -0.0076459 | 0.039781 | 0.080738 | -0.0070587 | -0.006462 | 0.047781 | 0.054633 | 0.041728 | -67.0037 | 0.010564 | -66.92 | 56.4304 | 56.2112 | 56.3352 | -67.0527 | -66.9855 | 0.018674 | -67.0749 | 56.2031 | 56.4725 | 56.3246 | -67.1843 | -0.063587 | -0.11257 | -0.014523 | 0.069157 | 0.13274 | -0.33173 | -0.20781 | -0.19516 | -0.33984 | 0.003658 | -0.085791 | 0.10937 | -0.070515 | -0.21841 | 123.4195 | 123.2004 | 123.3243 | 66.9997 | -123.5957 | 123.1923 | 123.4616 | 123.3137 | 67.0078 | -123.7273
416.2656 | 123.6191 | -67.0074 | 56.5247 | 0.06235 | -0.013072 | -0.0048075 | 0.040638 | -0.0076459 | 0.039781 | 0.065477 | -0.0059907 | -0.008599 | 0.047781 | 0.054633 | 0.04066 | -66.9991 | 0.015142 | -66.9291 | 56.4212 | 56.225 | 56.3352 | -67.0573 | -66.9717 | 0.014095 | -67.0841 | 56.1985 | 56.477 | 56.3246 | -67.1843 | -0.049856 | -0.10342 | 0.008366 | 0.07831 | 0.12817 | -0.29969 | -0.1895 | -0.17685 | -0.32611 | 0.035705 | -0.076639 | 0.10021 | -0.047625 | -0.2001 | 123.4287 | 123.2324 | 123.3426 | 67.0226 | -123.582 | 123.206 | 123.4845 | 123.332 | 67.0215 | -123.709
417.2656 | 123.674 | -66.9937 | 56.5338 | 0.077612 | -0.012003 | -0.0037395 | 0.042775 | -0.0076459 | 0.040849 | 0.080738 | -0.0049217 | -0.008599 | 0.048849 | 0.05677 | 0.042797 | -66.9991 | 0.015142 | -66.9246 | 56.435 | 56.225 | 56.3306 | -67.0436 | -66.9809 | 0.014095 | -67.0887 | 56.2031 | 56.4725 | 56.2925 | -67.1751 | -0.049852 | -0.098839 | -0.005367 | 0.069155 | 0.11901 | -0.30884 | -0.20324 | -0.18143 | -0.33069 | 0.012814 | -0.09495 | 0.086475 | -0.061359 | -0.2413 | 123.4287 | 123.2187 | 123.3243 | 67.0089 | -123.5774 | 123.1968 | 123.4662 | 123.2862 | 67.0078 | -123.709
418.2656 | 123.6694 | -67.0074 | 56.5155 | 0.06235 | -0.013072 | -0.0037395 | 0.040638 | -0.0076459 | 0.039781 | 0.050216 | -0.0059907 | -0.006462 | 0.047781 | 0.055702 | 0.041728 | -66.9991 | 0.019721 | -66.92 | 56.4258 | 56.225 | 56.3397 | -67.0481 | -66.9763 | 0.014095 | -67.0795 | 56.2031 | 56.4725 | 56.32 | -67.1797 | -0.040698 | -0.089686 | 0.008366 | 0.087467 | 0.12816 | -0.29053 | -0.17577 | -0.17227 | -0.31238 | 0.031126 | -0.07206 | 0.10021 | -0.043049 | -0.19552 | 123.4333 | 123.2324 | 123.3472 | 67.0272 | -123.5636 | 123.2106 | 123.4799 | 123.3274 | 67.0215 | -123.6952
419.2812 | 123.6465 | -67.0166 | 56.488 | 0.06235 | -0.01414 | -0.0058765 | 0.040638 | -0.0076459 | 0.040849 | 0.095999 | -0.0059907 | -0.007531 | 0.048849 | 0.055702 | 0.042797 | -66.9945 | 0.015142 | -66.9154 | 56.4258 | 56.225 | 56.326 | -67.0436 | -66.9763 | 0.014095 | -67.0841 | 56.2031 | 56.4725 | 56.3017 | -67.1751 | -0.026963 | -0.06222 | 0.0221 | 0.1012 | 0.12816 | -0.26306 | -0.16204 | -0.15854 | -0.28491 | 0.040282 | -0.067483 | 0.091053 | -0.015583 | -0.18637 | 123.4424 | 123.2416 | 123.3426 | 67.0317 | -123.5316 | 123.2197 | 123.4891 | 123.3183 | 67.0307 | -123.6632
420.2656 | 123.642 | -67.0074 | 56.5292 | 0.06235 | -0.010935 | -0.0026705 | 0.040638 | -0.0076459 | 0.041917 | 0.065477 | -0.0070587 | -0.006462 | 0.047781 | 0.05677 | 0.042797 | -67.0037 | 0.010564 | -66.92 | 56.4304 | 56.2296 | 56.3352 | -67.0573 | -66.9809 | 0.014095 | -67.0795 | 56.2031 | 56.477 | 56.3062 | -67.1797 | -0.049856 | -0.09884 | 0.003787 | 0.087467 | 0.13732 | -0.29968 | -0.19408 | -0.17227 | -0.32611 | 0.026547 | -0.07206 | 0.10021 | -0.052203 | -0.22299 | 123.4378 | 123.237 | 123.3426 | 67.018 | -123.5865 | 123.2106 | 123.4845 | 123.3137 | 67.0215 | -123.709
421.2656 | 123.6099 | -66.9937 | 56.5155 | 0.06235 | -0.013072 | -0.0048075 | 0.041706 | -0.0087139 | 0.040849 | 0.065477 | -0.0059907 | -0.007531 | 0.047781 | 0.05677 | 0.041728 | -66.9991 | 0.019721 | -66.9246 | 56.435 | 56.2387 | 56.3397 | -67.0619 | -66.9809 | 0.014095 | -67.0795 | 56.1985 | 56.477 | 56.3062 | -67.1843 | -0.068168 | -0.080529 | -0.005367 | 0.069155 | 0.13732 | -0.27679 | -0.17577 | -0.19058 | -0.31696 | 0.012814 | -0.085793 | 0.10479 | -0.03847 | -0.20926 | 123.4287 | 123.2324 | 123.3334 | 67.0134 | -123.5774 | 123.1923 | 123.4707 | 123.3 | 67.0078 | -123.6998
422.2656 | 123.6694 | -67.0166 | 56.5247 | 0.047088 | -0.012003 | -0.0037395 | 0.040638 | -0.0076459 | 0.039781 | 0.080738 | -0.0070587 | -0.007531 | 0.047781 | 0.055702 | 0.041728 | -67.0082 | 0.010564 | -66.9337 | 56.4304 | 56.2296 | 56.3352 | -67.0665 | -66.9809 | 0.014095 | -67.0749 | 56.2077 | 56.4816 | 56.3291 | -67.1889 | -0.049858 | -0.094262 | 0.008365 | 0.082888 | 0.13275 | -0.29511 | -0.1895 | -0.17227 | -0.31696 | 0.035703 | -0.058325 | 0.11395 | -0.043047 | -0.19552 | 123.447 | 123.2462 | 123.3518 | 67.0272 | -123.5911 | 123.2243 | 123.4982 | 123.3457 | 67.0307 | -123.7135
423.2656 | 123.6557 | -66.9937 | 56.5063 | 0.06235 | -0.010935 | -0.0058765 | 0.040638 | -0.0097819 | 0.040849 | 0.095999 | -0.0049217 | -0.006462 | 0.046713 | 0.054633 | 0.042797 | -66.9991 | 0.015142 | -66.9291 | 56.4258 | 56.2112 | 56.3352 | -67.0527 | -66.9763 | 0.014095 | -67.0841 | 56.2031 | 56.4816 | 56.3703 | -67.1751 | -0.05901 | -0.080531 | -0.005367 | 0.064577 | 0.12359 | -0.29511 | -0.17119 | -0.18143 | -0.30322 | 0.017393 | -0.090372 | 0.091053 | -0.024737 | -0.136 | 123.4195 | 123.2049 | 123.3289 | 67.0089 | -123.5591 | 123.1968 | 123.4753 | 123.3641 | 67.0078 | -123.6815
424.2812 | 123.6374 | -67.0166 | 56.5109 | 0.06235 | -0.013072 | -0.0048075 | 0.041706 | -0.0076459 | 0.039781 | 0.065477 | -0.0070587 | -0.006462 | 0.047781 | 0.055702 | 0.042797 | -66.9945 | 0.015142 | -66.92 | 56.4304 | 56.2112 | 56.3397 | -67.0573 | -66.9717 | 0.018674 | -67.0795 | 56.194 | 56.477 | 56.3291 | -67.1889 | -0.0407 | -0.080529 | 0.0221 | 0.096623 | 0.13732 | -0.29969 | -0.17119 | -0.17227 | -0.31696 | 0.044861 | -0.062904 | 0.10937 | -0.033892 | -0.18178 | 123.447 | 123.2278 | 123.3563 | 67.0317 | -123.5682 | 123.2106 | 123.4936 | 123.3457 | 67.0353 | -123.6998
425.2656 | 123.642 | -66.9846 | 56.5384 | 0.06235 | -0.012003 | -0.0058765 | 0.040638 | -0.0097819 | 0.039781 | 0.080738 | -0.0059907 | -0.006462 | 0.046713 | 0.054633 | 0.041728 | -67.0037 | 0.010564 | -66.92 | 56.4258 | 56.2204 | 56.3306 | -67.0527 | -66.9809 | 0.014095 | -67.0887 | 56.194 | 56.477 | 56.3703 | -67.1797 | -0.068165 | -0.11257 | -0.019101 | 0.064579 | 0.13274 | -0.318 | -0.20781 | -0.19516 | -0.34442 | 0.003659 | -0.1041 | 0.091054 | -0.061358 | -0.16804 | 123.4104 | 123.205 | 123.3151 | 66.9951 | -123.5911 | 123.1785 | 123.4616 | 123.3549 | 66.9987 | -123.7181
426.2656 | 123.6877 | -66.9846 | 56.5155 | 0.06235 | -0.012003 | -0.0048075 | 0.03957 | -0.0076459 | 0.042985 | 0.050216 | -0.0059907 | -0.007531 | 0.046713 | 0.05677 | 0.04066 | -66.9945 | 0.010564 | -66.92 | 56.4258 | 56.2341 | 56.3397 | -67.0665 | -66.9763 | 0.014095 | -67.0841 | 56.2031 | 56.477 | 56.32 | -67.1797 | -0.081902 | -0.089686 | -0.009944 | 0.064579 | 0.14648 | -0.28137 | -0.17577 | -0.19516 | -0.31238 | 0.008238 | -0.099527 | 0.095632 | -0.03847 | -0.19552 | 123.4104 | 123.2187 | 123.3243 | 66.9951 | -123.582 | 123.1877 | 123.4616 | 123.3045 | 66.9987 | -123.6952
427.2656 | 123.7015 | -66.9434 | 56.5018 | 0.06235 | -0.012003 | -0.0058765 | 0.03957 | -0.0076459 | 0.038712 | 0.065477 | -0.0059907 | -0.008599 | 0.048849 | 0.05677 | 0.04066 | -66.9991 | 0.019721 | -66.92 | 56.4304 | 56.2341 | 56.3397 | -67.0436 | -66.9809 | 0.018674 | -67.0795 | 56.2031 | 56.4862 | 56.3246 | -67.1843 | -0.10021 | -0.071374 | -0.055721 | 0.02338 | 0.12359 | -0.26764 | -0.16204 | -0.24094 | -0.29865 | -0.03754 | -0.13615 | 0.10479 | -0.01558 | -0.17721 | 123.3738 | 123.1775 | 123.2831 | 66.9631 | -123.5453 | 123.1465 | 123.4295 | 123.2679 | 66.962 | -123.6861
428.2656 | 123.6649 | -66.9846 | 56.5338 | 0.06235 | -0.015208 | -0.0037395 | 0.041706 | -0.0087139 | 0.040849 | 0.080738 | -0.0070587 | -0.007531 | 0.046713 | 0.055702 | 0.042797 | -66.9991 | 0.019721 | -66.9154 | 56.4258 | 56.225 | 56.3352 | -67.0436 | -66.9763 | 0.018674 | -67.0841 | 56.1985 | 56.477 | 56.32 | -67.1751 | -0.059007 | -0.108 | -0.014522 | 0.069157 | 0.12816 | -0.30884 | -0.19866 | -0.19058 | -0.33527 | 0.008238 | -0.099527 | 0.091053 | -0.05678 | -0.21383 | 123.4104 | 123.2095 | 123.3197 | 67.0043 | -123.5774 | 123.1831 | 123.4616 | 123.3045 | 67.0032 | -123.709
429.2812 | 123.6877 | -67.0029 | 56.5063 | 0.047088 | -0.012003 | -0.0048075 | 0.040638 | -0.0087139 | 0.040849 | 0.080738 | -0.0059907 | -0.007531 | 0.049918 | 0.055702 | 0.039592 | -67.0037 | 0.019721 | -66.9154 | 56.435 | 56.225 | 56.3397 | -67.0573 | -66.9809 | 0.014095 | -67.0841 | 56.1985 | 56.477 | 56.3246 | -67.1797 | -0.054433 | -0.071374 | -0.00079 | 0.087468 | 0.1419 | -0.28138 | -0.16662 | -0.17685 | -0.3078 | 0.02197 | -0.081216 | 0.095632 | -0.029315 | -0.18179 | 123.4378 | 123.2278 | 123.3426 | 67.0226 | -123.5637 | 123.2014 | 123.4799 | 123.3274 | 67.017 | -123.6861
430.2656 | 123.7473 | -66.98 | 56.4926 | 0.047088 | -0.013072 | -0.0037395 | 0.040638 | -0.0076459 | 0.039781 | 0.080738 | -0.0059907 | -0.007531 | 0.046713 | 0.05677 | 0.041728 | -67.0037 | 0.019721 | -66.9246 | 56.4304 | 56.2204 | 56.3352 | -67.0527 | -66.9809 | 0.004938 | -67.0841 | 56.2077 | 56.477 | 56.3566 | -67.1797 | -0.072743 | -0.062219 | -0.023679 | 0.055422 | 0.12816 | -0.27222 | -0.15746 | -0.19974 | -0.28491 | -0.000919 | -0.10411 | 0.095632 | -0.015582 | -0.136 | 123.4104 | 123.2004 | 123.3151 | 66.9997 | -123.5453 | 123.1877 | 123.457 | 123.3366 | 66.9849 | -123.6723
431.2656 | 123.7564 | -66.9479 | 56.488 | 0.06235 | -0.013072 | -0.0058765 | 0.041706 | -0.0097819 | 0.040849 | 0.080738 | -0.0059907 | -0.009667 | 0.046713 | 0.05677 | 0.041728 | -66.9945 | 0.0243 | -66.9154 | 56.4258 | 56.2296 | 56.3443 | -67.0665 | -66.9809 | 0.018674 | -67.0841 | 56.2077 | 56.4862 | 56.3566 | -67.1751 | -0.11852 | -0.06222 | -0.046565 | 0.032536 | 0.15106 | -0.25849 | -0.14372 | -0.2272 | -0.28034 | -0.032962 | -0.13615 | 0.091053 | -0.001847 | -0.13143 | 123.3738 | 123.1775 | 123.2922 | 66.9722 | -123.5545 | 123.1556 | 123.4341 | 123.3045 | 66.9666 | -123.6632
432.2656 | 123.7335 | -66.9617 | 56.5063 | 0.031826 | -0.013072 | -0.0037395 | 0.041706 | -0.0076459 | 0.039781 | 0.050216 | -0.0070587 | -0.009667 | 0.046713 | 0.05677 | 0.038523 | -67.0037 | 0.015142 | -66.92 | 56.4258 | 56.2341 | 56.3397 | -67.0481 | -66.9809 | 0.018674 | -67.0795 | 56.2077 | 56.4816 | 56.3658 | -67.1797 | -0.086474 | -0.080531 | -0.041989 | 0.041691 | 0.12816 | -0.27222 | -0.16662 | -0.21805 | -0.29865 | -0.019229 | -0.11784 | 0.10021 | -0.024737 | -0.14058 | 123.3875 | 123.1958 | 123.3014 | 66.9768 | -123.5545 | 123.1694 | 123.4433 | 123.3274 | 66.9803 | -123.6861
433.2656 | 123.7564 | -66.9754 | 56.456 | 0.092874 | -0.013072 | -0.0026705 | 0.040638 | -0.0087139 | 0.039781 | 0.080738 | -0.0059907 | -0.007531 | 0.047781 | 0.057839 | 0.039592 | -66.9899 | 0.010564 | -66.9154 | 56.4258 | 56.225 | 56.3306 | -67.0619 | -66.9809 | 0.014095 | -67.0841 | 56.1985 | 56.4862 | 56.3566 | -67.1797 | -0.086478 | -0.030177 | -0.014521 | 0.060002 | 0.14648 | -0.23102 | -0.12542 | -0.20431 | -0.25745 | -0.005496 | -0.10868 | 0.095632 | 0.030196 | -0.099382 | 123.4012 | 123.2004 | 123.306 | 66.986 | -123.5179 | 123.1739 | 123.4616 | 123.332 | 66.9895 | -123.6357
434.2812 | 123.6649 | -67.0029 | 56.5063 | 0.077612 | -0.01414 | -0.0048075 | 0.040638 | -0.0076459 | 0.040849 | 0.050216 | -0.0059907 | -0.009667 | 0.047781 | 0.057839 | 0.039592 | -66.9991 | 0.015142 | -66.9154 | 56.4396 | 56.2341 | 56.3397 | -67.0619 | -66.9809 | 0.014095 | -67.0795 | 56.1985 | 56.477 | 56.3429 | -67.1797 | -0.059012 | -0.066795 | 0.003789 | 0.087468 | 0.14648 | -0.27222 | -0.16662 | -0.17685 | -0.3078 | 0.02197 | -0.076637 | 0.10021 | -0.029315 | -0.16347 | 123.4424 | 123.237 | 123.3426 | 67.018 | -123.5682 | 123.2014 | 123.4799 | 123.3457 | 67.017 | -123.6861
435.2656 | 123.6786 | -66.98 | 56.5155 | 0.06235 | -0.012003 | -0.0058765 | 0.041706 | -0.0087139 | 0.037644 | 0.065477 | -0.0049217 | -0.008599 | 0.047781 | 0.058907 | 0.04066 | -67.0037 | 0.015142 | -66.9154 | 56.4258 | 56.225 | 56.3306 | -67.0481 | -66.9763 | 0.014095 | -67.0795 | 56.1985 | 56.4862 | 56.3383 | -67.1843 | -0.068164 | -0.089686 | -0.023679 | 0.064579 | 0.13274 | -0.29053 | -0.18493 | -0.20432 | -0.31696 | 0.00366 | -0.099526 | 0.10479 | -0.029313 | -0.17721 | 123.4058 | 123.205 | 123.3106 | 66.9951 | -123.5636 | 123.1785 | 123.4662 | 123.3183 | 66.9941 | -123.6998
436.2656 | 123.8342 | -66.9479 | 56.5567 | 0.047088 | -0.013072 | -0.0058765 | 0.037433 | -0.0097819 | 0.039781 | 0.065477 | -0.0070587 | -0.007531 | 0.046713 | 0.058907 | 0.039592 | -66.9991 | 0.015142 | -66.9246 | 56.4212 | 56.225 | 56.3397 | -67.0527 | -66.9809 | 0.023253 | -67.0841 | 56.194 | 56.4725 | 56.352 | -67.1843 | -0.10479 | -0.13546 | -0.051143 | 0.023379 | 0.12816 | -0.33173 | -0.21697 | -0.23636 | -0.36274 | -0.032962 | -0.13615 | 0.10021 | -0.084248 | -0.20467 | 123.3692 | 123.1729 | 123.2877 | 66.9631 | -123.6094 | 123.1419 | 123.4204 | 123.3 | 66.9712 | -123.741
437.2656 | 123.7381 | -66.9342 | 56.4835 | 0.077612 | -0.015208 | -0.0058765 | 0.040638 | -0.0076459 | 0.039781 | 0.065477 | -0.0070587 | -0.008599 | 0.046713 | 0.058907 | 0.041728 | -66.9945 | 0.015142 | -66.92 | 56.4212 | 56.2204 | 56.3352 | -67.0481 | -66.9809 | 0.004938 | -67.0887 | 56.1985 | 56.4862 | 56.3703 | -67.1843 | -0.11394 | -0.06222 | -0.060298 | 0.014225 | 0.12816 | -0.26306 | -0.1483 | -0.25009 | -0.28491 | -0.046695 | -0.15446 | 0.095633 | 0.002731 | -0.11311 | 123.3554 | 123.1546 | 123.2694 | 66.9493 | -123.5316 | 123.1327 | 123.4204 | 123.3046 | 66.9391 | -123.6678
438.2656 | 123.7244 | -66.9754 | 56.4926 | 0.06235 | -0.012003 | -0.0026705 | 0.040638 | -0.0087139 | 0.038712 | 0.065477 | -0.0070587 | -0.007531 | 0.047781 | 0.057839 | 0.039592 | -66.9991 | 0.019721 | -66.9108 | 56.4258 | 56.2158 | 56.3352 | -67.0481 | -66.9809 | 0.014095 | -67.0795 | 56.2031 | 56.477 | 56.3612 | -67.1751 | -0.072741 | -0.066798 | -0.023677 | 0.06458 | 0.13732 | -0.2768 | -0.15746 | -0.19974 | -0.28949 | -0.005496 | -0.1041 | 0.095632 | -0.015582 | -0.13143 | 123.4012 | 123.1912 | 123.3106 | 66.9951 | -123.5408 | 123.1785 | 123.4524 | 123.3366 | 66.9895 | -123.6678
439.2812 | 123.7244 | -66.98 | 56.4972 | 0.077612 | -0.013072 | -0.0037395 | 0.03957 | -0.0097819 | 0.040849 | 0.065477 | -0.0081267 | -0.007531 | 0.046713 | 0.057839 | 0.041728 | -66.9945 | 0.0243 | -66.9154 | 56.435 | 56.2341 | 56.3397 | -67.0527 | -66.9763 | 0.023253 | -67.0749 | 56.2031 | 56.477 | 56.3658 | -67.1889 | -0.072743 | -0.062218 | -0.014522 | 0.064579 | 0.13732 | -0.26306 | -0.15746 | -0.20889 | -0.29407 | 0.00366 | -0.094947 | 0.11395 | -0.020159 | -0.13142 | 123.415 | 123.2141 | 123.3197 | 67.0043 | -123.5499 | 123.1831 | 123.457 | 123.3457 | 67.0032 | -123.6861
440.2656 | 123.7518 | -66.9754 | 56.4972 | 0.06235 | -0.013072 | -0.0048075 | 0.03957 | -0.0076459 | 0.039781 | 0.095999 | -0.0059907 | -0.008599 | 0.046713 | 0.059975 | 0.039592 | -66.9945 | 0.015142 | -66.92 | 56.4258 | 56.2341 | 56.3397 | -67.0436 | -66.9809 | 0.009516 | -67.0795 | 56.1985 | 56.4862 | 56.3612 | -67.1843 | -0.068162 | -0.071375 | -0.019099 | 0.055424 | 0.12359 | -0.26306 | -0.15746 | -0.20889 | -0.29865 | -0.005496 | -0.1041 | 0.10479 | -0.011002 | -0.136 | 123.4012 | 123.2095 | 123.3151 | 66.9905 | -123.5408 | 123.1739 | 123.4616 | 123.3366 | 66.9849 | -123.6815
441.2656 | 123.7564 | -66.9571 | 56.5109 | 0.06235 | -0.013072 | -0.0069445 | 0.041706 | -0.0087139 | 0.039781 | 0.065477 | -0.0070587 | -0.007531 | 0.045645 | 0.057839 | 0.04066 | -66.9899 | 0.019721 | -66.92 | 56.4304 | 56.225 | 56.3397 | -67.0481 | -66.9763 | 0.023253 | -67.0795 | 56.1985 | 56.4816 | 56.3703 | -67.1797 | -0.091052 | -0.080529 | -0.032832 | 0.037113 | 0.12816 | -0.28595 | -0.17119 | -0.22262 | -0.31238 | -0.019228 | -0.12241 | 0.10021 | -0.029314 | -0.14058 | 123.3875 | 123.1821 | 123.2968 | 66.9768 | -123.5591 | 123.1556 | 123.4387 | 123.3274 | 66.9803 | -123.6906
442.2656 | 123.7427 | -66.98 | 56.5018 | 0.047088 | -0.013072 | -0.0058765 | 0.040638 | -0.0076459 | 0.038712 | 0.050216 | -0.0070587 | -0.008599 | 0.045645 | 0.057839 | 0.039592 | -66.9945 | 0.019721 | -66.92 | 56.435 | 56.2341 | 56.3397 | -67.0527 | -66.9763 | 0.009516 | -67.0749 | 56.1985 | 56.4725 | 56.3658 | -67.1797 | -0.072743 | -0.066796 | -0.014522 | 0.060001 | 0.13274 | -0.26764 | -0.16204 | -0.19974 | -0.30322 | 0.00366 | -0.094947 | 0.10479 | -0.029316 | -0.136 | 123.415 | 123.2141 | 123.3197 | 66.9997 | -123.5545 | 123.1785 | 123.4524 | 123.3457 | 66.9895 | -123.6815
443.2656 | 123.7244 | -66.9617 | 56.488 | 0.06235 | -0.013072 | -0.0058765 | 0.040638 | -0.0087139 | 0.039781 | 0.080738 | -0.0070587 | -0.007531 | 0.045645 | 0.058907 | 0.04066 | -66.9945 | 0.019721 | -66.9154 | 56.4258 | 56.225 | 56.3352 | -67.0481 | -66.9717 | 0.018674 | -67.0841 | 56.2077 | 56.4816 | 56.3703 | -67.1751 | -0.086474 | -0.06222 | -0.032832 | 0.046269 | 0.13274 | -0.26306 | -0.15288 | -0.21347 | -0.28034 | -0.010071 | -0.12242 | 0.091053 | -0.006426 | -0.11769 | 123.3875 | 123.1866 | 123.2968 | 66.9814 | -123.5362 | 123.1694 | 123.4433 | 123.332 | 66.9803 | -123.6632
444.2656 | 123.6923 | -66.98 | 56.488 | 0.06235 | -0.013072 | -0.0026705 | 0.041706 | -0.0087139 | 0.039781 | 0.065477 | -0.0081267 | -0.009667 | 0.046713 | 0.057839 | 0.039592 | -66.9945 | 0.015142 | -66.9154 | 56.435 | 56.2296 | 56.3397 | -67.0573 | -66.9763 | 0.009516 | -67.0841 | 56.1985 | 56.477 | 56.3612 | -67.1797 | -0.077322 | -0.053063 | -0.014522 | 0.064579 | 0.1419 | -0.25849 | -0.1483 | -0.19974 | -0.28949 | 0.00366 | -0.10411 | 0.095632 | -0.011004 | -0.12685 | 123.415 | 123.2095 | 123.3197 | 66.9951 | -123.5453 | 123.1785 | 123.457 | 123.3412 | 66.9895 | -123.6678
445.2656 | 123.7152 | -66.9662 | 56.4514 | 0.06235 | -0.01414 | -0.0037395 | 0.03957 | -0.0065769 | 0.038712 | 0.080738 | -0.0070587 | -0.008599 | 0.047781 | 0.058907 | 0.04066 | -66.9945 | 0.0243 | -66.9154 | 56.4304 | 56.2296 | 56.3397 | -67.039 | -66.9763 | 0.014095 | -67.0795 | 56.2031 | 56.4816 | 56.352 | -67.1797 | -0.072739 | -0.02102 | -0.028254 | 0.050847 | 0.12359 | -0.22186 | -0.11168 | -0.21347 | -0.24829 | -0.010072 | -0.11326 | 0.10021 | 0.030195 | -0.099383 | 123.3966 | 123.1958 | 123.306 | 66.9905 | -123.4904 | 123.1694 | 123.4479 | 123.3183 | 66.9803 | -123.6311
446.2656 | 123.7198 | -66.9846 | 56.4972 | 0.06235 | -0.01414 | -0.0048075 | 0.03957 | -0.0087139 | 0.039781 | 0.065477 | -0.0059907 | -0.009667 | 0.047781 | 0.059975 | 0.039592 | -66.9991 | 0.015142 | -66.9154 | 56.4304 | 56.2296 | 56.3352 | -67.0436 | -66.9763 | 0.014095 | -67.0841 | 56.2031 | 56.4816 | 56.3612 | -67.1843 | -0.059007 | -0.066796 | -0.014522 | 0.069157 | 0.12816 | -0.26764 | -0.16204 | -0.19974 | -0.29407 | 0.008238 | -0.099527 | 0.10021 | -0.015581 | -0.136 | 123.415 | 123.2141 | 123.3197 | 66.9997 | -123.5408 | 123.1877 | 123.4662 | 123.3457 | 66.9987 | -123.6815
447.2656 | 123.7015 | -66.9937 | 56.4789 | 0.047088 | -0.01414 | -0.0058765 | 0.03957 | -0.0076459 | 0.039781 | 0.080738 | -0.0070587 | -0.009667 | 0.045645 | 0.058907 | 0.04066 | -66.9991 | 0.015142 | -66.9154 | 56.4212 | 56.225 | 56.3443 | -67.039 | -66.9717 | 0.014095 | -67.0795 | 56.1985 | 56.477 | 56.3658 | -67.1797 | -0.045274 | -0.057643 | -0.005367 | 0.078312 | 0.12359 | -0.25391 | -0.13457 | -0.186 | -0.28034 | 0.021972 | -0.085793 | 0.10021 | -0.001849 | -0.11311 | 123.415 | 123.2187 | 123.338 | 67.0089 | -123.5179 | 123.1923 | 123.4707 | 123.3595 | 67.0078 | -123.6586
448.2656 | 123.7518 | -66.9525 | 56.4651 | 0.06235 | -0.013072 | -0.0048075 | 0.038501 | -0.0087139 | 0.038712 | 0.050216 | -0.0070587 | -0.007531 | 0.046713 | 0.057839 | 0.039592 | -66.9945 | 0.015142 | -66.9154 | 56.435 | 56.225 | 56.3397 | -67.0527 | -66.9717 | 0.018674 | -67.0841 | 56.194 | 56.477 | 56.3612 | -67.1843 | -0.10021 | -0.030175 | -0.041987 | 0.037114 | 0.13732 | -0.24018 | -0.12542 | -0.23178 | -0.27118 | -0.019226 | -0.13157 | 0.10021 | 0.011884 | -0.10396 | 123.3875 | 123.1775 | 123.2922 | 66.9677 | -123.5179 | 123.1465 | 123.4295 | 123.3137 | 66.9712 | -123.6494
449.2812 | 123.7015 | -66.9205 | 56.5292 | 0.047088 | -0.015208 | -0.0037395 | 0.040638 | -0.0097819 | 0.038712 | 0.080738 | -0.0070587 | -0.008599 | 0.045645 | 0.058907 | 0.04066 | -66.9991 | 0.005985 | -66.92 | 56.4304 | 56.225 | 56.3489 | -67.0436 | -66.9763 | 0.018674 | -67.0795 | 56.1985 | 56.4816 | 56.3703 | -67.1843 | -0.12309 | -0.09884 | -0.078609 | 0.000492 | 0.12359 | -0.30426 | -0.18035 | -0.26382 | -0.33069 | -0.055849 | -0.15903 | 0.10479 | -0.047625 | -0.15889 | 123.3509 | 123.1454 | 123.2694 | 66.9265 | -123.5728 | 123.119 | 123.4021 | 123.2908 | 66.9391 | -123.7135
450.2656 | 123.7106 | -66.9846 | 56.4743 | 0.047088 | -0.012003 | -0.0048075 | 0.038501 | -0.0097819 | 0.039781 | 0.080738 | -0.0059907 | -0.007531 | 0.046713 | 0.058907 | 0.041728 | -66.9945 | 0.015142 | -66.92 | 56.4258 | 56.2204 | 56.3443 | -67.0436 | -66.9809 | 0.014095 | -67.0887 | 56.2077 | 56.477 | 56.3062 | -67.1889 | -0.059007 | -0.048487 | -0.009944 | 0.064579 | 0.12359 | -0.25391 | -0.12999 | -0.20432 | -0.2666 | 0.003659 | -0.1041 | 0.10021 | 0.002729 | -0.16806 | 123.4104 | 123.205 | 123.3289 | 66.9997 | -123.5179 | 123.1923 | 123.4616 | 123.2908 | 66.9987 | -123.6632
451.2656 | 123.7564 | -66.98 | 56.456 | 0.06235 | -0.01414 | -0.0058765 | 0.03957 | -0.0087139 | 0.039781 | 0.080738 | -0.0070587 | -0.008599 | 0.045645 | 0.057839 | 0.04066 | -67.0037 | 0.015142 | -66.9154 | 56.435 | 56.2204 | 56.3306 | -67.0436 | -66.9763 | 0.014095 | -67.0795 | 56.194 | 56.477 | 56.3246 | -67.1797 | -0.063585 | -0.02102 | -0.023679 | 0.064579 | 0.12816 | -0.2356 | -0.12542 | -0.19974 | -0.26203 | 0.00366 | -0.099526 | 0.10021 | 0.021039 | -0.13143 | 123.415 | 123.2004 | 123.3106 | 66.9951 | -123.4996 | 123.1739 | 123.457 | 123.3045 | 66.9941 | -123.6357
452.2656 | 123.7518 | -66.9708 | 56.4697 | 0.047088 | -0.01414 | -0.0058765 | 0.03957 | -0.0087139 | 0.039781 | 0.065477 | -0.0070587 | -0.007531 | 0.047781 | 0.059975 | 0.04066 | -66.9899 | 0.015142 | -66.92 | 56.435 | 56.2204 | 56.3443 | -67.0527 | -66.9809 | 0.014095 | -67.0841 | 56.2031 | 56.477 | 56.2971 | -67.1797 | -0.081898 | -0.034753 | -0.019099 | 0.050846 | 0.13274 | -0.24933 | -0.12541 | -0.20889 | -0.2666 | -0.010074 | -0.11326 | 0.095632 | 0.007306 | -0.17264 | 123.4058 | 123.1912 | 123.3151 | 66.986 | -123.5224 | 123.1739 | 123.4479 | 123.2679 | 66.9849 | -123.6494
453.2656 | 123.7564 | -66.9754 | 56.4789 | 0.047088 | -0.01414 | -0.0048075 | 0.038501 | -0.0076459 | 0.037644 | 0.050216 | -0.0059907 | -0.007531 | 0.046713 | 0.059975 | 0.039592 | -66.9899 | 0.019721 | -66.9154 | 56.4258 | 56.2204 | 56.3352 | -67.0527 | -66.9763 | 0.018674 | -67.0795 | 56.1985 | 56.4725 | 56.3246 | -67.1751 | -0.07732 | -0.053065 | -0.014521 | 0.060002 | 0.13732 | -0.25849 | -0.14373 | -0.19974 | -0.28034 | -0.000917 | -0.1041 | 0.095632 | -0.006428 | -0.15432 | 123.4012 | 123.1958 | 123.3106 | 66.9951 | -123.5316 | 123.1739 | 123.4479 | 123.3 | 66.9941 | -123.654
454.2812 | 123.7564 | -66.9525 | 56.488 | 0.06235 | -0.01414 | -0.0037395 | 0.038501 | -0.0076459 | 0.039781 | 0.095999 | -0.0081267 | -0.007531 | 0.046713 | 0.059975 | 0.04066 | -66.9945 | 0.010564 | -66.92 | 56.4258 | 56.2341 | 56.3443 | -67.0527 | -66.9717 | 0.018674 | -67.0795 | 56.2031 | 56.477 | 56.32 | -67.1843 | -0.10021 | -0.06222 | -0.041987 | 0.032536 | 0.13274 | -0.25391 | -0.14372 | -0.23178 | -0.28491 | -0.019226 | -0.12699 | 0.10479 | -0.011004 | -0.16805 | 123.3783 | 123.1866 | 123.2968 | 66.9631 | -123.5408 | 123.1556 | 123.4295 | 123.2725 | 66.9712 | -123.6723
455.2656 | 123.7656 | -66.9754 | 56.4743 | 0.047088 | -0.01414 | -0.0058765 | 0.038501 | -0.0087139 | 0.039781 | 0.065477 | -0.0049217 | -0.008599 | 0.046713 | 0.057839 | 0.04066 | -66.9945 | 0.0243 | -66.92 | 56.4258 | 56.2296 | 56.3489 | -67.0481 | -66.9672 | 0.018674 | -67.0795 | 56.1985 | 56.4816 | 56.3154 | -67.1843 | -0.072741 | -0.048487 | -0.019099 | 0.055424 | 0.12816 | -0.24475 | -0.12541 | -0.20889 | -0.27576 | 0.00824 | -0.1041 | 0.10479 | 0.007307 | -0.1589 | 123.4012 | 123.205 | 123.3243 | 66.9997 | -123.5224 | 123.1739 | 123.457 | 123.2908 | 66.9941 | -123.6586
456.2656 | 123.7289 | -66.9754 | 56.4697 | 0.047088 | -0.013072 | -0.0058765 | 0.040638 | -0.0087139 | 0.038712 | 0.080738 | -0.0070587 | -0.008599 | 0.046713 | 0.058907 | 0.039592 | -66.9945 | 0.0243 | -66.92 | 56.435 | 56.2204 | 56.3443 | -67.0481 | -66.9809 | 0.009516 | -67.0795 | 56.1985 | 56.4816 | 56.2925 | -67.1843 | -0.072741 | -0.034753 | -0.019099 | 0.055424 | 0.12816 | -0.24933 | -0.12541 | -0.20889 | -0.27118 | -0.005496 | -0.1041 | 0.10479 | 0.011884 | -0.17722 | 123.4104 | 123.1958 | 123.3197 | 66.9997 | -123.5179 | 123.1739 | 123.457 | 123.2679 | 66.9849 | -123.654
457.2656 | 123.7152 | -66.9891 | 56.4789 | 0.06235 | -0.01414 | -0.0058765 | 0.03957 | -0.0087139 | 0.039781 | 0.050216 | -0.0070587 | -0.006462 | 0.044577 | 0.061044 | 0.041728 | -66.9991 | 0.015142 | -66.9154 | 56.4304 | 56.2204 | 56.3397 | -67.0436 | -66.9717 | 0.018674 | -67.0841 | 56.194 | 56.4816 | 56.3017 | -67.1797 | -0.054429 | -0.048486 | -0.009944 | 0.073735 | 0.12816 | -0.25849 | -0.13915 | -0.19058 | -0.28491 | 0.017395 | -0.094949 | 0.095632 | 0.002729 | -0.17721 | 123.4195 | 123.2095 | 123.3289 | 67.0043 | -123.5224 | 123.1831 | 123.4707 | 123.2908 | 67.0078 | -123.6586
458.2656 | 123.5596 | -67.0807 | 56.4697 | 0.06235 | -0.015208 | -0.0048075 | 0.038501 | -0.0087139 | 0.038712 | 0.050216 | -0.0081267 | -0.008599 | 0.044577 | 0.062112 | 0.038523 | -66.9945 | 0.0243 | -66.92 | 56.4258 | 56.225 | 56.3443 | -67.0436 | -66.9763 | 0.023253 | -67.0795 | 56.2031 | 56.477 | 56.3246 | -67.1797 | 0.037123 | -0.04391 | 0.086186 | 0.16071 | 0.12359 | -0.24475 | -0.12541 | -0.099029 | -0.2666 | 0.10437 | 0.001182 | 0.10021 | 0.007306 | -0.14516 | 123.5065 | 123.3057 | 123.425 | 67.105 | -123.5133 | 123.2838 | 123.5577 | 123.4052 | 67.1039 | -123.6494
459.2812 | 123.7106 | -66.9754 | 56.4789 | 0.077612 | -0.015208 | -0.0069445 | 0.040638 | -0.0087139 | 0.039781 | 0.065477 | -0.0059907 | -0.006462 | 0.045645 | 0.059975 | 0.039592 | -66.9945 | 0.015142 | -66.9154 | 56.4258 | 56.2204 | 56.3397 | -67.0573 | -66.9763 | 0.018674 | -67.0703 | 56.2031 | 56.4725 | 56.3337 | -67.1843 | -0.081899 | -0.053065 | -0.019099 | 0.060002 | 0.1419 | -0.25849 | -0.13915 | -0.20889 | -0.27576 | -0.000917 | -0.094946 | 0.11395 | -0.006428 | -0.14516 | 123.4012 | 123.1958 | 123.3151 | 66.9905 | -123.5362 | 123.1785 | 123.4479 | 123.3091 | 66.9941 | -123.6632
460.2656 | 123.642 | -67.0532 | 56.4972 | 0.047088 | -0.013072 | -0.0058765 | 0.03957 | -0.0087139 | 0.038712 | 0.080738 | -0.0059907 | -0.006462 | 0.046713 | 0.061044 | 0.039592 | -66.9899 | 0.015142 | -66.92 | 56.4304 | 56.2296 | 56.3489 | -67.0527 | -66.9809 | 0.009516 | -67.0749 | 56.194 | 56.4816 | 56.3062 | -67.1843 | 0.0005 | -0.066796 | 0.063299 | 0.13324 | 0.13274 | -0.26764 | -0.1483 | -0.13107 | -0.30322 | 0.072324 | -0.021704 | 0.10937 | -0.015581 | -0.19094 | 123.4836 | 123.2828 | 123.4021 | 67.0684 | -123.5499 | 123.2472 | 123.5348 | 123.3595 | 67.0627 | -123.6815
461.2656 | 123.6237 | -67.0578 | 56.5292 | 0.06235 | -0.013072 | -0.0080125 | 0.038501 | -0.0065769 | 0.039781 | 0.065477 | -0.0059907 | -0.008599 | 0.046713 | 0.061044 | 0.039592 | -66.9899 | 0.019721 | -66.92 | 56.4304 | 56.225 | 56.3397 | -67.0665 | -66.9717 | 0.018674 | -67.0795 | 56.1985 | 56.4725 | 56.2834 | -67.1843 | -0.00866 | -0.09884 | 0.067876 | 0.13782 | 0.14648 | -0.30426 | -0.1895 | -0.1265 | -0.33069 | 0.086059 | -0.021706 | 0.10479 | -0.056782 | -0.24588 | 123.4882 | 123.2828 | 123.3975 | 67.0775 | -123.5957 | 123.2563 | 123.5303 | 123.3412 | 67.0765 | -123.7135
462.2656 | 123.6008 | -67.0349 | 56.5063 | 0.047088 | -0.015208 | -0.0069445 | 0.03957 | -0.0087139 | 0.037644 | 0.065477 | -0.0059907 | -0.007531 | 0.044577 | 0.061044 | 0.039592 | -66.9991 | 0.015142 | -66.9154 | 56.4396 | 56.2296 | 56.3443 | -67.0481 | -66.9809 | 0.018674 | -67.0749 | 56.194 | 56.477 | 56.3108 | -67.1843 | -0.013232 | -0.066795 | 0.035832 | 0.11951 | 0.13274 | -0.2768 | -0.16204 | -0.14938 | -0.31238 | 0.054013 | -0.040015 | 0.10937 | -0.029315 | -0.19552 | 123.4745 | 123.2645 | 123.3792 | 67.0501 | -123.5545 | 123.2289 | 123.5119 | 123.3457 | 67.0536 | -123.6906
463.2656 | 123.6008 | -67.0303 | 56.4926 | 0.06235 | -0.01414 | -0.0080125 | 0.037433 | -0.0097819 | 0.038712 | 0.050216 | -0.0070587 | -0.008599 | 0.044577 | 0.058907 | 0.039592 | -67.0037 | 0.019721 | -66.92 | 56.4304 | 56.2158 | 56.3443 | -67.0436 | -66.9763 | 0.014095 | -67.0795 | 56.194 | 56.4725 | 56.2834 | -67.1843 | -0.013231 | -0.062219 | 0.026675 | 0.11035 | 0.12359 | -0.2768 | -0.1483 | -0.15396 | -0.29865 | 0.054014 | -0.049172 | 0.10479 | -0.020161 | -0.20926 | 123.4607 | 123.2462 | 123.3746 | 67.0501 | -123.5362 | 123.2243 | 123.5028 | 123.3137 | 67.0444 | -123.6769
464.2656 | 123.7198 | -67.0212 | 56.4377 | 0.06235 | -0.013072 | -0.0080125 | 0.03957 | -0.0065769 | 0.037644 | 0.050216 | -0.0070587 | -0.006462 | 0.045645 | 0.061044 | 0.036387 | -66.9899 | 0.015142 | -66.92 | 56.4212 | 56.2158 | 56.3443 | -67.0665 | -66.9763 | 0.004938 | -67.0795 | 56.1894 | 56.477 | 56.3475 | -67.1843 | -0.045281 | -0.016444 | 0.031255 | 0.1012 | 0.14648 | -0.22187 | -0.093371 | -0.16312 | -0.24829 | 0.044859 | -0.058327 | 0.10479 | 0.03935 | -0.090228 | 123.4424 | 123.237 | 123.3655 | 67.0363 | -123.5041 | 123.2106 | 123.4982 | 123.3686 | 67.0261 | -123.622
465.2656 | 123.674 | -66.98 | 56.5201 | 0.06235 | -0.01414 | -0.0069445 | 0.037433 | -0.0097819 | 0.038712 | 0.050216 | -0.0081267 | -0.007531 | 0.046713 | 0.061044 | 0.037455 | -66.9899 | 0.019721 | -66.9154 | 56.435 | 56.225 | 56.3489 | -67.071 | -66.9672 | 0.018674 | -67.0749 | 56.1894 | 56.4862 | 56.3429 | -67.1843 | -0.091059 | -0.085107 | -0.009944 | 0.064579 | 0.15564 | -0.29511 | -0.17119 | -0.20432 | -0.33069 | 0.012817 | -0.094947 | 0.10937 | -0.033891 | -0.17721 | 123.415 | 123.205 | 123.3289 | 66.9997 | -123.5911 | 123.1694 | 123.4662 | 123.3229 | 66.9987 | -123.7044
466.2656 | 123.7152 | -67.0029 | 56.5109 | 0.047088 | -0.01414 | -0.0058765 | 0.037433 | -0.0097819 | 0.037644 | 0.050216 | -0.0059907 | -0.010735 | 0.045645 | 0.059975 | 0.039592 | -66.9945 | 0.0243 | -66.92 | 56.435 | 56.2067 | 56.3397 | -67.071 | -66.9809 | 0.018674 | -67.0703 | 56.1985 | 56.477 | 56.3154 | -67.1797 | -0.06817 | -0.075951 | 0.008367 | 0.08289 | 0.15106 | -0.30427 | -0.17119 | -0.17685 | -0.31238 | 0.02197 | -0.06748 | 0.10937 | -0.033892 | -0.19552 | 123.4378 | 123.2095 | 123.3426 | 67.0272 | -123.582 | 123.2014 | 123.4799 | 123.3183 | 67.0215 | -123.6906
467.2656 | 123.6465 | -67.0029 | 56.4972 | 0.077612 | -0.015208 | -0.0069445 | 0.038501 | -0.0097819 | 0.036576 | 0.050216 | -0.0059907 | -0.007531 | 0.046713 | 0.062112 | 0.039592 | -66.9899 | 0.019721 | -66.9246 | 56.4258 | 56.2296 | 56.3397 | -67.0619 | -66.9763 | 0.018674 | -67.0749 | 56.2031 | 56.4816 | 56.2971 | -67.1843 | -0.059012 | -0.071375 | 0.012945 | 0.078311 | 0.13732 | -0.26764 | -0.15746 | -0.18143 | -0.29407 | 0.026549 | -0.072058 | 0.10937 | -0.015581 | -0.2001 | 123.4287 | 123.2324 | 123.3426 | 67.0226 | -123.5591 | 123.206 | 123.4845 | 123.3 | 67.0215 | -123.6815
468.2656 | 123.6694 | -66.9983 | 56.5155 | 0.06235 | -0.01414 | -0.0058765 | 0.03957 | -0.0097819 | 0.037644 | 0.080738 | -0.0059907 | -0.007531 | 0.045645 | 0.06318 | 0.04066 | -66.9991 | 0.019721 | -66.9246 | 56.4304 | 56.225 | 56.3397 | -67.0481 | -66.9763 | 0.018674 | -67.0795 | 56.194 | 56.4816 | 56.32 | -67.1843 | -0.049853 | -0.085107 | -0.000789 | 0.073733 | 0.12359 | -0.29053 | -0.17577 | -0.18601 | -0.32154 | 0.021971 | -0.081215 | 0.10479 | -0.033892 | -0.19552 | 123.4287 | 123.2233 | 123.338 | 67.018 | -123.5636 | 123.1923 | 123.4799 | 123.3183 | 67.017 | -123.6998
469.2812 | 123.7518 | -66.98 | 56.4377 | 0.047088 | -0.013072 | -0.0058765 | 0.037433 | -0.0097819 | 0.039781 | 0.065477 | -0.0049217 | -0.005394 | 0.046713 | 0.062112 | 0.038523 | -66.9899 | 0.019721 | -66.9246 | 56.4304 | 56.2204 | 56.3443 | -67.0481 | -66.9717 | 0.018674 | -67.0795 | 56.2031 | 56.4816 | 56.3154 | -67.1843 | -0.068164 | -0.007287 | -0.009944 | 0.055422 | 0.12359 | -0.21729 | -0.093371 | -0.20432 | -0.23456 | 0.008239 | -0.099526 | 0.10479 | 0.043928 | -0.12228 | 123.4104 | 123.2004 | 123.3243 | 66.9997 | -123.4858 | 123.1831 | 123.4616 | 123.2954 | 66.9987 | -123.622
470.2656 | 123.6465 | -67.0074 | 56.5247 | 0.047088 | -0.01414 | -0.0058765 | 0.040638 | -0.0097819 | 0.039781 | 0.065477 | -0.0070587 | -0.007531 | 0.046713 | 0.06318 | 0.039592 | -66.9899 | 0.015142 | -66.92 | 56.435 | 56.2296 | 56.3443 | -67.0573 | -66.9809 | 0.014095 | -67.0749 | 56.1985 | 56.4725 | 56.3154 | -67.1751 | -0.049856 | -0.089684 | 0.017522 | 0.087467 | 0.13732 | -0.29511 | -0.18035 | -0.16769 | -0.32611 | 0.026547 | -0.067481 | 0.10021 | -0.052204 | -0.20925 | 123.4424 | 123.237 | 123.3518 | 67.0226 | -123.582 | 123.206 | 123.4799 | 123.3229 | 67.0215 | -123.6998
471.2656 | 123.6786 | -67.0166 | 56.5018 | 0.047088 | -0.016277 | -0.0058765 | 0.038501 | -0.0087139 | 0.039781 | 0.095999 | -0.0070587 | -0.007531 | 0.045645 | 0.059975 | 0.038523 | -66.9945 | 0.0243 | -66.92 | 56.4396 | 56.2296 | 56.3489 | -67.0527 | -66.9763 | 0.018674 | -67.0841 | 56.1985 | 56.4862 | 56.3246 | -67.1843 | -0.036121 | -0.062217 | 0.0221 | 0.096623 | 0.13274 | -0.27222 | -0.15288 | -0.16769 | -0.30322 | 0.040282 | -0.067483 | 0.10021 | -0.01558 | -0.17721 | 123.4562 | 123.2462 | 123.3655 | 67.0409 | -123.5545 | 123.2151 | 123.5028 | 123.3412 | 67.0353 | -123.6861
472.2656 | 123.6832 | -66.9983 | 56.5155 | 0.031826 | -0.01414 | -0.0069445 | 0.037433 | -0.0087139 | 0.037644 | 0.080738 | -0.0059907 | -0.008599 | 0.045645 | 0.062112 | 0.038523 | -66.9853 | 0.010564 | -66.92 | 56.4304 | 56.225 | 56.3535 | -67.0573 | -66.9717 | 0.018674 | -67.0841 | 56.1985 | 56.477 | 56.32 | -67.1889 | -0.059011 | -0.085107 | 0.012946 | 0.078312 | 0.13732 | -0.29053 | -0.16203 | -0.19058 | -0.31696 | 0.02655 | -0.085794 | 0.10479 | -0.03847 | -0.19552 | 123.4287 | 123.2233 | 123.3518 | 67.0089 | -123.5728 | 123.1968 | 123.4753 | 123.3183 | 67.017 | -123.7044
473.2656 | 123.6786 | -66.9891 | 56.5292 | 0.047088 | -0.015208 | -0.0058765 | 0.03957 | -0.0097819 | 0.036576 | 0.065477 | -0.0070587 | -0.007531 | 0.046713 | 0.06318 | 0.039592 | -66.9899 | 0.015142 | -66.92 | 56.4304 | 56.2341 | 56.3443 | -67.0527 | -66.9763 | 0.027831 | -67.0887 | 56.1985 | 56.477 | 56.3062 | -67.1843 | -0.063587 | -0.09884 | -0.000788 | 0.069157 | 0.13274 | -0.2951 | -0.18492 | -0.19516 | -0.33069 | 0.012816 | -0.099527 | 0.095633 | -0.052203 | -0.22299 | 123.4195 | 123.2233 | 123.3334 | 67.0043 | -123.582 | 123.1877 | 123.4662 | 123.2954 | 67.017 | -123.7135
474.2812 | 123.7015 | -66.9754 | 56.4651 | 0.031826 | -0.013072 | -0.0069445 | 0.03957 | -0.0097819 | 0.037644 | 0.050216 | -0.0070587 | -0.008599 | 0.044577 | 0.061044 | 0.038523 | -66.9945 | 0.0243 | -66.92 | 56.4212 | 56.225 | 56.3443 | -67.039 | -66.9763 | 0.014095 | -67.0703 | 56.194 | 56.477 | 56.3017 | -67.1889 | -0.063584 | -0.04391 | -0.019099 | 0.055424 | 0.11901 | -0.24018 | -0.12084 | -0.21347 | -0.27118 | -0.000917 | -0.094946 | 0.11853 | 0.011884 | -0.16348 | 123.3966 | 123.2004 | 123.3197 | 66.9997 | -123.5041 | 123.1694 | 123.4524 | 123.2771 | 66.9895 | -123.654
475.2656 | 123.6832 | -66.9846 | 56.5063 | 0.06235 | -0.015208 | -0.0069445 | 0.038501 | -0.0087139 | 0.038712 | 0.065477 | -0.0081267 | -0.006462 | 0.045645 | 0.064249 | 0.038523 | -66.9945 | 0.0243 | -66.92 | 56.435 | 56.225 | 56.3489 | -67.0573 | -66.9717 | 0.014095 | -67.0703 | 56.2077 | 56.477 | 56.32 | -67.198 | -0.072744 | -0.071374 | -0.009944 | 0.064579 | 0.13732 | -0.28138 | -0.15746 | -0.21347 | -0.29865 | 0.012817 | -0.085791 | 0.12768 | -0.029315 | -0.18637 | 123.4195 | 123.2095 | 123.3334 | 67.0089 | -123.5637 | 123.1923 | 123.4616 | 123.3045 | 66.9987 | -123.7044
476.2656 | 123.7061 | -67.0212 | 56.488 | 0.047088 | -0.015208 | -0.0026705 | 0.038501 | -0.0097819 | 0.038712 | 0.050216 | -0.0059907 | -0.005394 | 0.046713 | 0.064249 | 0.038523 | -66.9899 | 0.015142 | -66.92 | 56.435 | 56.2112 | 56.3489 | -67.0573 | -66.9763 | 0.018674 | -67.0658 | 56.194 | 56.477 | 56.3246 | -67.1751 | -0.036123 | -0.053063 | 0.031255 | 0.1012 | 0.13732 | -0.2768 | -0.13915 | -0.15396 | -0.29407 | 0.044859 | -0.044591 | 0.10937 | -0.011004 | -0.16347 | 123.4562 | 123.2324 | 123.3701 | 67.0363 | -123.5453 | 123.2151 | 123.4982 | 123.3457 | 67.0399 | -123.6632
477.2656 | 123.642 | -67.0166 | 56.5201 | 0.077612 | -0.015208 | -0.0069445 | 0.03957 | -0.0087139 | 0.039781 | 0.050216 | -0.0070587 | -0.008599 | 0.045645 | 0.06318 | 0.039592 | -66.9853 | 0.019721 | -66.92 | 56.4304 | 56.2341 | 56.3443 | -67.0619 | -66.9717 | 0.018674 | -67.0749 | 56.194 | 56.477 | 56.3108 | -67.1889 | -0.045279 | -0.089685 | 0.031257 | 0.096623 | 0.1419 | -0.28595 | -0.17577 | -0.17227 | -0.32611 | 0.044861 | -0.058325 | 0.11395 | -0.043048 | -0.20925 | 123.447 | 123.2507 | 123.3609 | 67.0363 | -123.582 | 123.2106 | 123.4936 | 123.3274 | 67.0353 | -123.709
478.2656 | 123.6694 | -67.012 | 56.488 | 0.077612 | -0.015208 | -0.0069445 | 0.037433 | -0.0087139 | 0.038712 | 0.080738 | -0.0091947 | -0.007531 | 0.045645 | 0.06318 | 0.039592 | -66.9899 | 0.015142 | -66.92 | 56.435 | 56.2341 | 56.3443 | -67.0665 | -66.9763 | 0.018674 | -67.0887 | 56.2031 | 56.4725 | 56.3154 | -67.1797 | -0.054436 | -0.053063 | 0.0221 | 0.092045 | 0.14648 | -0.25391 | -0.14372 | -0.16769 | -0.28491 | 0.035704 | -0.076639 | 0.091054 | -0.015583 | -0.17263 | 123.447 | 123.2462 | 123.3563 | 67.0272 | -123.5545 | 123.2151 | 123.4845 | 123.3274 | 67.0307 | -123.6678
479.2812 | 123.7244 | -66.9754 | 56.488 | 0.077612 | -0.017345 | -0.0069445 | 0.040638 | -0.0097819 | 0.038712 | 0.050216 | -0.0070587 | -0.006462 | 0.044577 | 0.062112 | 0.038523 | -66.9899 | 0.015142 | -66.9246 | 56.4258 | 56.2341 | 56.3535 | -67.0527 | -66.9717 | 0.009516 | -67.0749 | 56.1985 | 56.477 | 56.3154 | -67.1751 | -0.07732 | -0.06222 | -0.014521 | 0.050845 | 0.12816 | -0.25391 | -0.13457 | -0.19974 | -0.28949 | 0.003662 | -0.099524 | 0.10021 | -0.011004 | -0.17263 | 123.4012 | 123.2095 | 123.3289 | 66.9905 | -123.5408 | 123.1739 | 123.4524 | 123.2908 | 66.9849 | -123.6632
480.2656 | 123.6649 | -66.9754 | 56.5247 | 0.06235 | -0.017345 | -0.0069445 | 0.03957 | -0.0087139 | 0.036576 | 0.065477 | -0.0091947 | -0.007531 | 0.044577 | 0.065317 | 0.037455 | -66.9945 | 0.019721 | -66.9154 | 56.4441 | 56.2296 | 56.3535 | -67.0573 | -66.9809 | 0.023253 | -67.0795 | 56.1985 | 56.4862 | 56.32 | -67.1797 | -0.081899 | -0.080527 | -0.019099 | 0.060002 | 0.1419 | -0.29511 | -0.17119 | -0.20431 | -0.32611 | -0.005496 | -0.1041 | 0.10021 | -0.038468 | -0.20468 | 123.4195 | 123.205 | 123.3289 | 66.9951 | -123.582 | 123.1739 | 123.4616 | 123.2954 | 66.9987 | -123.7044
481.2656 | 123.6786 | -66.9662 | 56.5338 | 0.047088 | -0.017345 | -0.0058765 | 0.038501 | -0.0087139 | 0.037644 | 0.050216 | -0.0059907 | -0.008599 | 0.045645 | 0.062112 | 0.037455 | -66.9945 | 0.019721 | -66.92 | 56.4304 | 56.2341 | 56.3489 | -67.0619 | -66.9763 | 0.018674 | -67.0703 | 56.2031 | 56.4816 | 56.3291 | -67.1751 | -0.095633 | -0.10342 | -0.028254 | 0.046269 | 0.1419 | -0.29968 | -0.18492 | -0.20889 | -0.33069 | -0.010072 | -0.1041 | 0.10479 | -0.052202 | -0.20467 | 123.3966 | 123.2004 | 123.3151 | 66.986 | -123.5957 | 123.1694 | 123.4479 | 123.2954 | 66.9849 | -123.709
482.2656 | 123.674 | -66.9983 | 56.5155 | 0.092874 | -0.016277 | -0.0048075 | 0.037433 | -0.0097819 | 0.037644 | 0.050216 | -0.0081267 | -0.006462 | 0.044577 | 0.06318 | 0.039592 | -66.9899 | 0.0243 | -66.92 | 56.435 | 56.2204 | 56.3489 | -67.0573 | -66.9763 | 0.018674 | -67.0749 | 56.2031 | 56.4862 | 56.3291 | -67.1843 | -0.059011 | -0.080529 | 0.008367 | 0.078312 | 0.13732 | -0.29511 | -0.16661 | -0.18601 | -0.31238 | 0.021971 | -0.076636 | 0.10937 | -0.029313 | -0.18636 | 123.4333 | 123.2187 | 123.3472 | 67.0226 | -123.5728 | 123.2014 | 123.4845 | 123.3274 | 67.017 | -123.6998
483.2656 | 123.6832 | -66.9937 | 56.5201 | 0.06235 | -0.017345 | -0.0069445 | 0.036364 | -0.010851 | 0.037644 | 0.065477 | -0.0070587 | -0.008599 | 0.045645 | 0.064249 | 0.039592 | -66.9945 | 0.0243 | -66.9246 | 56.435 | 56.2341 | 56.3443 | -67.0665 | -66.9717 | 0.014095 | -67.0749 | 56.2077 | 56.4816 | 56.3291 | -67.1889 | -0.072747 | -0.085107 | -0.000789 | 0.069155 | 0.1419 | -0.28595 | -0.17577 | -0.19516 | -0.31238 | 0.021972 | -0.081214 | 0.11395 | -0.03847 | -0.19094 | 123.4287 | 123.2278 | 123.338 | 67.018 | -123.5865 | 123.2014 | 123.4753 | 123.3229 | 67.0078 | -123.709
484.2812 | 123.7701 | -66.9571 | 56.488 | 0.06235 | -0.017345 | -0.0058765 | 0.038501 | -0.0087139 | 0.037644 | 0.034955 | -0.0070587 | -0.008599 | 0.044577 | 0.064249 | 0.037455 | -66.9945 | 0.015142 | -66.9154 | 56.435 | 56.2341 | 56.3443 | -67.0619 | -66.9717 | 0.014095 | -67.0658 | 56.2031 | 56.4725 | 56.2971 | -67.1843 | -0.10479 | -0.053063 | -0.03741 | 0.041691 | 0.14648 | -0.25391 | -0.14372 | -0.2272 | -0.28491 | -0.014649 | -0.10868 | 0.11853 | -0.015583 | -0.19095 | 123.3921 | 123.1912 | 123.3014 | 66.9722 | -123.5499 | 123.1602 | 123.4295 | 123.2542 | 66.9712 | -123.6723
485.2656 | 123.6694 | -66.9937 | 56.5155 | 0.06235 | -0.016277 | -0.0069445 | 0.038501 | -0.0097819 | 0.037644 | 0.080738 | -0.0070587 | -0.008599 | 0.04244 | 0.064249 | 0.038523 | -66.9899 | 0.019721 | -66.92 | 56.4304 | 56.2387 | 56.3443 | -67.0527 | -66.9717 | 0.023253 | -67.0795 | 56.2031 | 56.477 | 56.3337 | -67.1889 | -0.05901 | -0.085107 | 0.003789 | 0.073734 | 0.13274 | -0.27679 | -0.17119 | -0.19516 | -0.31238 | 0.021972 | -0.085793 | 0.10937 | -0.03847 | -0.18178 | 123.4241 | 123.2324 | 123.338 | 67.0134 | -123.5682 | 123.1968 | 123.4707 | 123.3274 | 67.017 | -123.7044
486.2656 | 123.6282 | -67.0074 | 56.5155 | 0.077612 | -0.017345 | -0.0058765 | 0.037433 | -0.0097819 | 0.037644 | 0.065477 | -0.0081267 | -0.009667 | 0.046713 | 0.064249 | 0.038523 | -66.9945 | 0.015142 | -66.9108 | 56.4304 | 56.2296 | 56.3489 | -67.0527 | -66.9672 | 0.014095 | -67.0703 | 56.2031 | 56.477 | 56.3703 | -67.1843 | -0.045277 | -0.085107 | 0.012944 | 0.096623 | 0.1419 | -0.28595 | -0.16661 | -0.17685 | -0.31238 | 0.040283 | -0.062903 | 0.11395 | -0.03847 | -0.14516 | 123.4378 | 123.237 | 123.3563 | 67.0226 | -123.5682 | 123.2106 | 123.4845 | 123.3778 | 67.0215 | -123.6998
487.2656 | 123.6237 | -66.9846 | 56.5247 | 0.06235 | -0.015208 | -0.0069445 | 0.037433 | -0.0087139 | 0.037644 | 0.065477 | -0.0070587 | -0.008599 | 0.046713 | 0.064249 | 0.037455 | -66.9945 | 0.019721 | -66.92 | 56.4304 | 56.225 | 56.3443 | -67.0665 | -66.9717 | 0.009516 | -67.0795 | 56.2031 | 56.477 | 56.3658 | -67.1797 | -0.081902 | -0.094262 | -0.009944 | 0.064579 | 0.14648 | -0.29969 | -0.18035 | -0.19516 | -0.32153 | 0.012817 | -0.094948 | 0.10021 | -0.047625 | -0.15889 | 123.415 | 123.2095 | 123.3289 | 67.0043 | -123.5911 | 123.1877 | 123.4616 | 123.3503 | 66.9941 | -123.7044
488.2656 | 123.642 | -67.0029 | 56.4926 | 0.06235 | -0.016277 | -0.0037395 | 0.038501 | -0.010851 | 0.038712 | 0.065477 | -0.0070587 | -0.007531 | 0.045645 | 0.064249 | 0.036387 | -66.9899 | 0.0243 | -66.9154 | 56.4258 | 56.2387 | 56.3535 | -67.0527 | -66.9626 | 0.023253 | -67.0795 | 56.2031 | 56.4816 | 56.3749 | -67.1889 | -0.049854 | -0.066798 | 0.012945 | 0.087468 | 0.13732 | -0.25391 | -0.13915 | -0.18601 | -0.28949 | 0.040285 | -0.076637 | 0.10937 | -0.011004 | -0.11769 | 123.4287 | 123.2416 | 123.3563 | 67.0272 | -123.5453 | 123.206 | 123.4845 | 123.3778 | 67.0261 | -123.6815
489.2812 | 123.6969 | -66.9891 | 56.4743 | 0.06235 | -0.016277 | -0.0058765 | 0.038501 | -0.0076459 | 0.038712 | 0.080738 | -0.0081267 | -0.008599 | 0.045645 | 0.06318 | 0.038523 | -66.9899 | 0.0243 | -66.92 | 56.4258 | 56.2204 | 56.3443 | -67.0573 | -66.9672 | 0.014095 | -67.0749 | 56.194 | 56.477 | 56.352 | -67.1843 | -0.068166 | -0.048487 | -0.000788 | 0.069157 | 0.13732 | -0.25391 | -0.12999 | -0.19516 | -0.28034 | 0.021973 | -0.085791 | 0.10937 | 0.002729 | -0.12227 | 123.415 | 123.2095 | 123.3334 | 67.0134 | -123.5316 | 123.1831 | 123.4662 | 123.3412 | 67.0032 | -123.6586
490.2656 | 123.6557 | -66.9846 | 56.5292 | 0.06235 | -0.017345 | -0.0048075 | 0.038501 | -0.0097819 | 0.036576 | 0.080738 | -0.0091947 | -0.009667 | 0.04244 | 0.065317 | 0.037455 | -66.9853 | 0.015142 | -66.92 | 56.4396 | 56.2341 | 56.3489 | -67.0619 | -66.9763 | 0.018674 | -67.0795 | 56.2123 | 56.4679 | 56.3703 | -67.1797 | -0.077323 | -0.089683 | -0.000787 | 0.064579 | 0.1419 | -0.2951 | -0.18035 | -0.19516 | -0.31696 | 0.008238 | -0.094948 | 0.10021 | -0.06136 | -0.15889 | 123.4241 | 123.2187 | 123.3334 | 66.9997 | -123.5911 | 123.1968 | 123.4524 | 123.3549 | 67.0032 | -123.709
491.2656 | 123.6557 | -66.9754 | 56.5109 | 0.06235 | -0.016277 | -0.0080125 | 0.037433 | -0.0097819 | 0.039781 | 0.080738 | -0.0059907 | -0.008599 | 0.045645 | 0.064249 | 0.038523 | -66.9945 | 0.0243 | -66.9154 | 56.435 | 56.2387 | 56.3535 | -67.0527 | -66.9763 | 0.018674 | -67.0795 | 56.2031 | 56.477 | 56.3703 | -67.1843 | -0.07732 | -0.075951 | -0.019099 | 0.060002 | 0.13732 | -0.27222 | -0.15746 | -0.20889 | -0.3078 | -0.000917 | -0.1041 | 0.10479 | -0.033892 | -0.14058 | 123.4104 | 123.2141 | 123.3289 | 66.9997 | -123.5636 | 123.1785 | 123.4524 | 123.3458 | 66.9941 | -123.6952
492.2656 | 123.6328 | -66.9937 | 56.5292 | 0.06235 | -0.017345 | -0.0058765 | 0.037433 | -0.011919 | 0.038712 | 0.080738 | -0.0091947 | -0.009667 | 0.04244 | 0.065317 | 0.037455 | -66.9899 | 0.015142 | -66.9246 | 56.4304 | 56.2387 | 56.3489 | -67.0573 | -66.9763 | 0.018674 | -67.0749 | 56.1985 | 56.477 | 56.3703 | -67.1751 | -0.063589 | -0.09884 | 0.003789 | 0.069155 | 0.13274 | -0.29053 | -0.18035 | -0.18143 | -0.33069 | 0.017393 | -0.081214 | 0.10021 | -0.052203 | -0.15889 | 123.4241 | 123.2324 | 123.3426 | 67.0089 | -123.5865 | 123.1923 | 123.4707 | 123.3641 | 67.0124 | -123.7044
493.2656 | 123.6191 | -66.9891 | 56.5109 | 0.047088 | -0.016277 | -0.0058765 | 0.036364 | -0.0097819 | 0.036576 | 0.080738 | -0.0070587 | -0.008599 | 0.044577 | 0.065317 | 0.037455 | -66.9899 | 0.019721 | -66.9154 | 56.435 | 56.2341 | 56.3489 | -67.0619 | -66.9717 | 0.027831 | -67.0703 | 56.194 | 56.4679 | 56.3475 | -67.1889 | -0.072745 | -0.075951 | -0.000788 | 0.073735 | 0.14648 | -0.27679 | -0.16204 | -0.19974 | -0.31696 | 0.017395 | -0.081213 | 0.11853 | -0.043049 | -0.16347 | 123.4241 | 123.2233 | 123.338 | 67.0089 | -123.5728 | 123.1831 | 123.457 | 123.3366 | 67.017 | -123.6998
494.2812 | 123.6328 | -67.0166 | 56.4972 | 0.031826 | -0.016277 | -0.0048075 | 0.038501 | -0.0087139 | 0.037644 | 0.080738 | -0.0091947 | -0.008599 | 0.045645 | 0.065317 | 0.037455 | -66.9899 | 0.010564 | -66.9154 | 56.435 | 56.2341 | 56.3443 | -67.0481 | -66.9717 | 0.018674 | -67.0703 | 56.2031 | 56.4725 | 56.3703 | -67.1843 | -0.031542 | -0.062218 | 0.026678 | 0.1012 | 0.13274 | -0.26306 | -0.15288 | -0.16769 | -0.29407 | 0.044861 | -0.053747 | 0.11395 | -0.024738 | -0.12684 | 123.4516 | 123.2507 | 123.3609 | 67.0272 | -123.5453 | 123.2197 | 123.4891 | 123.387 | 67.0353 | -123.6815
495.2656 | 123.6328 | -67.0029 | 56.5247 | 0.06235 | -0.015208 | -0.0058765 | 0.038501 | -0.010851 | 0.039781 | 0.065477 | -0.0070587 | -0.009667 | 0.045645 | 0.068522 | 0.037455 | -66.9899 | 0.019721 | -66.92 | 56.4396 | 56.225 | 56.3443 | -67.0619 | -66.958 | 0.014095 | -67.0795 | 56.1985 | 56.477 | 56.352 | -67.1751 | -0.059012 | -0.085105 | 0.012945 | 0.08289 | 0.1419 | -0.29969 | -0.18035 | -0.17227 | -0.32611 | 0.044864 | -0.076637 | 0.095632 | -0.047625 | -0.17263 | 123.4424 | 123.2278 | 123.3472 | 67.0226 | -123.5865 | 123.2014 | 123.4799 | 123.3549 | 67.017 | -123.6998
496.2656 | 123.6237 | -66.9891 | 56.5201 | 0.092874 | -0.017345 | -0.0058765 | 0.036364 | -0.0097819 | 0.037644 | 0.065477 | -0.0059907 | -0.009667 | 0.045645 | 0.065317 | 0.037455 | -66.9945 | 0.019721 | -66.92 | 56.4304 | 56.2341 | 56.3489 | -67.0481 | -66.9763 | 0.014095 | -67.0749 | 56.2077 | 56.4816 | 56.3429 | -67.1843 | -0.059008 | -0.089685 | -0.005366 | 0.069157 | 0.12816 | -0.28595 | -0.17119 | -0.19516 | -0.31238 | 0.012816 | -0.085791 | 0.10937 | -0.03847 | -0.17721 | 123.4195 | 123.2233 | 123.338 | 67.0089 | -123.5682 | 123.1968 | 123.4707 | 123.332 | 67.0032 | -123.7044
497.2656 | 123.6191 | -67.0212 | 56.5247 | 0.06235 | -0.016277 | -0.0069445 | 0.037433 | -0.0097819 | 0.037644 | 0.065477 | -0.0091947 | -0.008599 | 0.045645 | 0.066386 | 0.038523 | -66.9899 | 0.010564 | -66.9154 | 56.4304 | 56.2341 | 56.3489 | -67.0436 | -66.9763 | 0.018674 | -67.0703 | 56.2031 | 56.4816 | 56.3795 | -67.1889 | -0.022386 | -0.094262 | 0.031255 | 0.10578 | 0.12816 | -0.29053 | -0.17577 | -0.1677 | -0.32153 | 0.044859 | -0.04917 | 0.11853 | -0.043047 | -0.14515 | 123.4516 | 123.2553 | 123.3701 | 67.0317 | -123.5682 | 123.2243 | 123.5028 | 123.4007 | 67.0399 | -123.7135
498.2656 | 123.6282 | -66.9983 | 56.5201 | 0.047088 | -0.018413 | -0.0058765 | 0.036364 | -0.0097819 | 0.035507 | 0.050216 | -0.0081267 | -0.009667 | 0.044577 | 0.064249 | 0.038523 | -66.9945 | 0.005985 | -66.9154 | 56.4258 | 56.2387 | 56.3443 | -67.0527 | -66.9717 | 0.014095 | -67.0749 | 56.2031 | 56.4816 | 56.3658 | -67.1889 | -0.054432 | -0.094264 | 0.003789 | 0.08289 | 0.13732 | -0.28137 | -0.17577 | -0.19058 | -0.31696 | 0.02655 | -0.076636 | 0.11395 | -0.03847 | -0.15431 | 123.4241 | 123.237 | 123.3426 | 67.0043 | -123.5728 | 123.2014 | 123.4799 | 123.3641 | 67.0124 | -123.709
499.2656 | 123.6877 | -66.98 | 56.5338 | 0.06235 | -0.018413 | -0.0069445 | 0.035296 | -0.011919 | 0.037644 | 0.065477 | -0.0091947 | -0.008599 | 0.04244 | 0.065317 | 0.037455 | -66.9991 | 0.019721 | -66.9154 | 56.4304 | 56.2341 | 56.3535 | -67.0527 | -66.9717 | 0.018674 | -67.0749 | 56.2031 | 56.4862 | 56.3612 | -67.1843 | -0.072743 | -0.10342 | -0.0191 | 0.064579 | 0.13732 | -0.29968 | -0.18034 | -0.20432 | -0.33069 | 0.008239 | -0.094947 | 0.10937 | -0.047623 | -0.17262 | 123.4104 | 123.2141 | 123.3334 | 66.9997 | -123.5865 | 123.1831 | 123.4662 | 123.3412 | 66.9987 | -123.7181
500.2656 | 123.7244 | -66.9571 | 56.5109 | 0.06235 | -0.016277 | -0.0058765 | 0.036364 | -0.0076459 | 0.035507 | 0.065477 | -0.0070587 | -0.008599 | 0.044577 | 0.066386 | 0.038523 | -66.9899 | 0.015142 | -66.9154 | 56.435 | 56.2341 | 56.3443 | -67.0527 | -66.9717 | 0.014095 | -67.0658 | 56.2031 | 56.4862 | 56.352 | -67.1843 | -0.095631 | -0.075951 | -0.032832 | 0.041691 | 0.13732 | -0.27679 | -0.16661 | -0.2272 | -0.3078 | -0.014649 | -0.10868 | 0.11853 | -0.024735 | -0.15889 | 123.3921 | 123.1912 | 123.3014 | 66.9722 | -123.5636 | 123.1602 | 123.4433 | 123.3091 | 66.9712 | -123.6952
501.2656 | 123.642 | -66.98 | 56.5384 | 0.047088 | -0.018413 | -0.0069445 | 0.038501 | -0.010851 | 0.037644 | 0.095999 | -0.0070587 | -0.008599 | 0.043508 | 0.068522 | 0.037455 | -66.9945 | 0.015142 | -66.92 | 56.435 | 56.2387 | 56.3489 | -67.0527 | -66.9809 | 0.018674 | -67.0658 | 56.194 | 56.4908 | 56.3703 | -67.1889 | -0.072743 | -0.10342 | -0.014522 | 0.060001 | 0.13274 | -0.29968 | -0.1895 | -0.20889 | -0.34442 | -0.000919 | -0.08579 | 0.1231 | -0.047622 | -0.16804 | 123.415 | 123.2187 | 123.3289 | 66.9951 | -123.5911 | 123.1739 | 123.4707 | 123.3503 | 66.9987 | -123.7273
502.2656 | 123.674 | -66.9708 | 56.5018 | 0.047088 | -0.019482 | -0.0048075 | 0.036364 | -0.0097819 | 0.036576 | 0.080738 | -0.0081267 | -0.007531 | 0.04244 | 0.065317 | 0.037455 | -66.9853 | 0.019721 | -66.92 | 56.4396 | 56.2387 | 56.3489 | -67.0527 | -66.9717 | 0.018674 | -67.0841 | 56.2031 | 56.4862 | 56.3612 | -67.1843 | -0.081898 | -0.062217 | -0.01452 | 0.050846 | 0.13274 | -0.26306 | -0.15288 | -0.21347 | -0.29865 | -0.000916 | -0.11326 | 0.10021 | -0.01558 | -0.14058 | 123.4104 | 123.2095 | 123.3197 | 66.9905 | -123.5545 | 123.1739 | 123.457 | 123.332 | 66.9895 | -123.6861
503.2656 | 123.7061 | -66.9662 | 56.5063 | 0.092874 | -0.017345 | -0.0080125 | 0.037433 | -0.0097819 | 0.037644 | 0.080738 | -0.0081267 | -0.008599 | 0.043508 | 0.065317 | 0.037455 | -66.9899 | 0.0243 | -66.9154 | 56.4304 | 56.2296 | 56.3443 | -67.0527 | -66.9626 | 0.009516 | -67.0703 | 56.2077 | 56.4908 | 56.3703 | -67.1889 | -0.086475 | -0.075952 | -0.023676 | 0.050847 | 0.13732 | -0.2768 | -0.16204 | -0.22263 | -0.29865 | 0.003664 | -0.1041 | 0.11853 | -0.015579 | -0.136 | 123.3966 | 123.1958 | 123.3106 | 66.9905 | -123.5591 | 123.1739 | 123.457 | 123.3366 | 66.9758 | -123.6952
504.2656 | 123.6191 | -67.012 | 56.5475 | 0.047088 | -0.019482 | -0.0058765 | 0.038501 | -0.0097819 | 0.036576 | 0.080738 | -0.0070587 | -0.009667 | 0.043508 | 0.067454 | 0.038523 | -66.9853 | 0.019721 | -66.9291 | 56.4304 | 56.2387 | 56.3443 | -67.0665 | -66.9763 | 0.023253 | -67.0749 | 56.2077 | 56.4862 | 56.3429 | -67.1797 | -0.054436 | -0.11715 | 0.026679 | 0.082888 | 0.13732 | -0.30884 | -0.20323 | -0.16769 | -0.33984 | 0.035704 | -0.062903 | 0.10479 | -0.061356 | -0.20467 | 123.4424 | 123.2507 | 123.3563 | 67.0317 | -123.614 | 123.2197 | 123.4982 | 123.3549 | 67.0353 | -123.7273
505.2656 | 123.6237 | -66.98 | 56.5521 | 0.06235 | -0.017345 | -0.0069445 | 0.037433 | -0.010851 | 0.037644 | 0.034955 | -0.0091947 | -0.008599 | 0.04244 | 0.068522 | 0.036387 | -66.9899 | 0.0243 | -66.9154 | 56.4304 | 56.2296 | 56.3535 | -67.0481 | -66.9717 | 0.018674 | -67.0795 | 56.2077 | 56.4725 | 56.3291 | -67.1797 | -0.068164 | -0.12173 | -0.009944 | 0.064579 | 0.13274 | -0.32257 | -0.19866 | -0.19974 | -0.34442 | 0.008239 | -0.099526 | 0.10021 | -0.07967 | -0.22298 | 123.4104 | 123.2095 | 123.3334 | 67.0043 | -123.6003 | 123.1877 | 123.4524 | 123.3091 | 66.9987 | -123.7318
506.2656 | 123.7747 | -66.9388 | 56.4651 | 0.047088 | -0.017345 | -0.0048075 | 0.036364 | -0.0097819 | 0.037644 | 0.095999 | -0.0091947 | -0.008599 | 0.044577 | 0.066386 | 0.036387 | -66.9853 | 0.0243 | -66.9154 | 56.4304 | 56.2341 | 56.3443 | -67.0619 | -66.9717 | 0.014095 | -67.0795 | 56.2031 | 56.477 | 56.3566 | -67.1889 | -0.1231 | -0.034753 | -0.046563 | 0.023381 | 0.14648 | -0.23102 | -0.12084 | -0.25009 | -0.26202 | -0.032959 | -0.14072 | 0.10937 | 0.011884 | -0.10854 | 123.3692 | 123.1729 | 123.2831 | 66.9631 | -123.527 | 123.1419 | 123.4158 | 123.2954 | 66.9529 | -123.654
507.2656 | 123.7473 | -66.9662 | 56.488 | 0.077612 | -0.017345 | -0.0058765 | 0.035296 | -0.010851 | 0.035507 | 0.095999 | -0.0081267 | -0.010735 | 0.04244 | 0.065317 | 0.036387 | -66.9899 | 0.019721 | -66.9108 | 56.4396 | 56.2296 | 56.3489 | -67.0573 | -66.9672 | 0.014095 | -67.0749 | 56.2031 | 56.4816 | 56.2879 | -67.1889 | -0.091054 | -0.048484 | -0.023676 | 0.055425 | 0.14648 | -0.25849 | -0.13915 | -0.22263 | -0.28491 | -0.000915 | -0.10868 | 0.11395 | -0.006426 | -0.2001 | 123.4058 | 123.1958 | 123.3151 | 66.986 | -123.5453 | 123.1694 | 123.4479 | 123.2542 | 66.9803 | -123.6769
508.2656 | 123.7473 | -66.925 | 56.5063 | 0.077612 | -0.017345 | -0.0058765 | 0.038501 | -0.0097819 | 0.038712 | 0.080738 | -0.0070587 | -0.008599 | 0.044577 | 0.068522 | 0.037455 | -66.9899 | 0.0243 | -66.9246 | 56.4304 | 56.2433 | 56.3535 | -67.0665 | -66.9717 | 0.009516 | -67.0703 | 56.2077 | 56.4862 | 56.3566 | -67.1843 | -0.14141 | -0.075952 | -0.064875 | 0.000491 | 0.1419 | -0.26306 | -0.15288 | -0.25925 | -0.29865 | -0.046692 | -0.1453 | 0.11395 | -0.020158 | -0.14974 | 123.3554 | 123.1683 | 123.2785 | 66.9493 | -123.5728 | 123.1328 | 123.4112 | 123.2817 | 66.9346 | -123.6906
509.2812 | 123.5916 | -66.9846 | 56.5247 | 0.047088 | -0.018413 | -0.0069445 | 0.037433 | -0.010851 | 0.037644 | 0.080738 | -0.0091947 | -0.009667 | 0.04244 | 0.067454 | 0.037455 | -66.9945 | 0.0243 | -66.9108 | 56.435 | 56.2433 | 56.358 | -67.0665 | -66.9717 | 0.018674 | -67.0749 | 56.2077 | 56.4816 | 56.3703 | -67.1843 | -0.081902 | -0.089684 | -0.009944 | 0.073735 | 0.15564 | -0.28137 | -0.16661 | -0.19974 | -0.31696 | 0.012817 | -0.090369 | 0.10937 | -0.043047 | -0.15431 | 123.4195 | 123.2278 | 123.3426 | 67.0089 | -123.5911 | 123.1923 | 123.4662 | 123.3549 | 67.0032 | -123.709
510.2656 | 123.761 | -66.9479 | 56.5018 | 0.047088 | -0.018413 | -0.0058765 | 0.036364 | -0.010851 | 0.035507 | 0.080738 | -0.0070587 | -0.009667 | 0.04244 | 0.068522 | 0.036387 | -66.9853 | 0.015142 | -66.9154 | 56.435 | 56.2296 | 56.3397 | -67.0436 | -66.9717 | 0.018674 | -67.0749 | 56.2031 | 56.477 | 56.3703 | -67.1843 | -0.095628 | -0.066796 | -0.037408 | 0.032536 | 0.12816 | -0.27222 | -0.16204 | -0.23636 | -0.29865 | -0.023804 | -0.12699 | 0.10937 | -0.024737 | -0.13142 | 123.3829 | 123.1775 | 123.2877 | 66.9631 | -123.5453 | 123.1511 | 123.425 | 123.3183 | 66.9666 | -123.6861
511.2656 | 123.7427 | -66.9617 | 56.4743 | 0.06235 | -0.017345 | -0.0058765 | 0.038501 | -0.010851 | 0.037644 | 0.080738 | -0.0081267 | -0.008599 | 0.043508 | 0.068522 | 0.037455 | -66.9899 | 0.0243 | -66.9246 | 56.435 | 56.2341 | 56.3443 | -67.0527 | -66.9717 | 0.023253 | -67.0703 | 56.2031 | 56.477 | 56.3703 | -67.1889 | -0.091053 | -0.03933 | -0.028254 | 0.037112 | 0.12816 | -0.24017 | -0.12999 | -0.2272 | -0.27118 | -0.010071 | -0.10868 | 0.11853 | 0.002729 | -0.10396 | 123.3966 | 123.1958 | 123.306 | 66.986 | -123.527 | 123.1648 | 123.4387 | 123.332 | 66.9849 | -123.6632
512.2656 | 123.7335 | -66.9662 | 56.4697 | 0.077612 | -0.017345 | -0.0080125 | 0.037433 | -0.0087139 | 0.036576 | 0.095999 | -0.0070587 | -0.008599 | 0.044577 | 0.069591 | 0.036387 | -66.9899 | 0.015142 | -66.92 | 56.4396 | 56.2387 | 56.3535 | -67.0527 | -66.9717 | 0.009516 | -67.0749 | 56.2031 | 56.477 | 56.3703 | -67.1843 | -0.086475 | -0.030174 | -0.023676 | 0.046269 | 0.13274 | -0.23102 | -0.11626 | -0.21805 | -0.2666 | -0.005493 | -0.10868 | 0.10937 | 0.007306 | -0.099379 | 123.4058 | 123.205 | 123.3197 | 66.9814 | -123.5224 | 123.1694 | 123.4433 | 123.3366 | 66.9758 | -123.654
513.2656 | 123.761 | -66.9479 | 56.4926 | 0.047088 | -0.018413 | -0.0058765 | 0.037433 | -0.0087139 | 0.037644 | 0.065477 | -0.0081267 | -0.010735 | 0.043508 | 0.068522 | 0.038523 | -66.9899 | 0.015142 | -66.9154 | 56.4396 | 56.2341 | 56.3535 | -67.0619 | -66.9855 | 0.004938 | -67.0703 | 56.1985 | 56.4725 | 56.3703 | -67.1935 | -0.11394 | -0.053062 | -0.041987 | 0.032536 | 0.14648 | -0.25848 | -0.13915 | -0.24552 | -0.29407 | -0.037541 | -0.12241 | 0.12311 | -0.020161 | -0.12227 | 123.3875 | 123.1821 | 123.3014 | 66.9631 | -123.5545 | 123.1465 | 123.4204 | 123.3183 | 66.9529 | -123.6861
514.2812 | 123.6374 | -66.9846 | 56.5475 | 0.077612 | -0.018413 | -0.0058765 | 0.035296 | -0.010851 | 0.036576 | 0.065477 | -0.0081267 | -0.008599 | 0.04244 | 0.066386 | 0.037455 | -66.9853 | 0.015142 | -66.92 | 56.4304 | 56.2296 | 56.3397 | -67.0573 | -66.9672 | 0.014095 | -67.0703 | 56.2031 | 56.4816 | 56.3703 | -67.1843 | -0.072744 | -0.11715 | -0.000787 | 0.064579 | 0.13732 | -0.31799 | -0.20781 | -0.19974 | -0.34442 | 0.017395 | -0.085791 | 0.11395 | -0.065935 | -0.1772 | 123.415 | 123.2141 | 123.3243 | 66.9997 | -123.6048 | 123.1877 | 123.4662 | 123.3549 | 66.9987 | -123.7318
515.2656 | 123.7335 | -66.9434 | 56.4926 | 0.047088 | -0.017345 | -0.0058765 | 0.037433 | -0.0087139 | 0.037644 | 0.080738 | -0.0081267 | -0.007531 | 0.043508 | 0.066386 | 0.036387 | -66.9853 | 0.0243 | -66.92 | 56.435 | 56.2387 | 56.3535 | -67.0619 | -66.9717 | 0.018674 | -67.0703 | 56.2077 | 56.4862 | 56.3566 | -67.1935 | -0.11852 | -0.057641 | -0.041986 | 0.02338 | 0.1419 | -0.25391 | -0.13915 | -0.2501 | -0.28491 | -0.028382 | -0.12699 | 0.12311 | -0.006425 | -0.136 | 123.3783 | 123.1821 | 123.2968 | 66.9677 | -123.5545 | 123.1511 | 123.4295 | 123.3 | 66.962 | -123.6861
516.2656 | 123.7473 | -66.9388 | 56.488 | 0.047088 | -0.018413 | -0.0069445 | 0.036364 | -0.0076459 | 0.037644 | 0.065477 | -0.0070587 | -0.008599 | 0.043508 | 0.068522 | 0.036387 | -66.9899 | 0.015142 | -66.92 | 56.4304 | 56.2341 | 56.358 | -67.0436 | -66.9717 | 0.014095 | -67.0749 | 56.2031 | 56.477 | 56.3475 | -67.1889 | -0.10478 | -0.057641 | -0.051142 | 0.018803 | 0.12359 | -0.25391 | -0.12999 | -0.25009 | -0.28491 | -0.032959 | -0.13614 | 0.11395 | -0.011004 | -0.14058 | 123.3692 | 123.1729 | 123.2968 | 66.9539 | -123.5316 | 123.1419 | 123.4158 | 123.2862 | 66.9529 | -123.6769
517.2656 | 123.7289 | -66.9754 | 56.4835 | 0.06235 | -0.018413 | -0.0058765 | 0.037433 | -0.0097819 | 0.037644 | 0.080738 | -0.0081267 | -0.009667 | 0.043508 | 0.068522 | 0.037455 | -66.9808 | 0.010564 | -66.9108 | 56.4258 | 56.2341 | 56.3489 | -67.0527 | -66.9717 | 0.014095 | -67.0703 | 56.2031 | 56.477 | 56.2925 | -67.1889 | -0.07732 | -0.057642 | -0.005364 | 0.06458 | 0.1419 | -0.24933 | -0.13457 | -0.21347 | -0.28034 | 0.003662 | -0.094946 | 0.11853 | -0.006426 | -0.19095 | 123.4012 | 123.2095 | 123.3243 | 66.986 | -123.5362 | 123.1785 | 123.4524 | 123.2679 | 66.9895 | -123.6723
518.2656 | 123.7518 | -66.9617 | 56.5063 | 0.06235 | -0.018413 | -0.0058765 | 0.035296 | -0.010851 | 0.038712 | 0.080738 | -0.0091947 | -0.008599 | 0.044577 | 0.068522 | 0.037455 | -66.9853 | 0.019721 | -66.9154 | 56.435 | 56.2296 | 56.3489 | -67.0436 | -66.9763 | 0.014095 | -67.0795 | 56.1894 | 56.4816 | 56.3291 | -67.1889 | -0.081895 | -0.071374 | -0.023675 | 0.046269 | 0.12816 | -0.2768 | -0.15746 | -0.2272 | -0.31696 | -0.01465 | -0.11784 | 0.10937 | -0.024737 | -0.17721 | 123.3966 | 123.1912 | 123.3106 | 66.9814 | -123.5499 | 123.1511 | 123.4433 | 123.2908 | 66.9758 | -123.6952
519.2812 | 123.6237 | -66.9754 | 56.5338 | 0.06235 | -0.017345 | -0.0080125 | 0.037433 | -0.010851 | 0.036576 | 0.065477 | -0.0081267 | -0.007531 | 0.044577 | 0.068522 | 0.035319 | -66.9808 | 0.0243 | -66.9154 | 56.4304 | 56.2296 | 56.3535 | -67.0481 | -66.9717 | 0.014095 | -67.0658 | 56.194 | 56.4816 | 56.3246 | -67.1889 | -0.072741 | -0.10342 | -0.005364 | 0.060002 | 0.13274 | -0.30426 | -0.18034 | -0.21347 | -0.33985 | 0.003662 | -0.090367 | 0.1231 | -0.052202 | -0.20925 | 123.4058 | 123.205 | 123.3289 | 66.9997 | -123.582 | 123.1694 | 123.457 | 123.3 | 66.9895 | -123.7227
520.2656 | 123.6832 | -66.9662 | 56.4789 | 0.047088 | -0.019482 | -0.0058765 | 0.037433 | -0.010851 | 0.038712 | 0.065477 | -0.0081267 | -0.008599 | 0.045645 | 0.067454 | 0.037455 | -66.9853 | 0.015142 | -66.9108 | 56.4258 | 56.225 | 56.3489 | -67.0527 | -66.9672 | 0.014095 | -67.0703 | 56.1985 | 56.477 | 56.3154 | -67.1843 | -0.086475 | -0.053065 | -0.019097 | 0.055425 | 0.1419 | -0.25391 | -0.12999 | -0.21805 | -0.28034 | -0.000915 | -0.1041 | 0.11395 | -0.001849 | -0.16348 | 123.3921 | 123.1912 | 123.3151 | 66.9814 | -123.5316 | 123.1648 | 123.4433 | 123.2817 | 66.9803 | -123.6632
521.2656 | 123.7015 | -66.9846 | 56.4697 | 0.047088 | -0.017345 | -0.0080125 | 0.035296 | -0.010851 | 0.035507 | 0.050216 | -0.0091947 | -0.009667 | 0.043508 | 0.066386 | 0.036387 | -66.9899 | 0.019721 | -66.92 | 56.4304 | 56.2341 | 56.3443 | -67.0573 | -66.9717 | 0.018674 | -67.0749 | 56.194 | 56.4816 | 56.2879 | -67.1889 | -0.072744 | -0.039331 | -0.005366 | 0.064579 | 0.13732 | -0.2356 | -0.12541 | -0.20432 | -0.27576 | 0.012817 | -0.090369 | 0.11395 | 0.011884 | -0.18179 | 123.415 | 123.2187 | 123.3289 | 67.0043 | -123.527 | 123.1785 | 123.4662 | 123.2725 | 67.0032 | -123.6586
522.2656 | 123.6511 | -66.9434 | 56.4972 | 0.077612 | -0.016277 | -0.0058765 | 0.035296 | -0.0097819 | 0.037644 | 0.050216 | -0.0081267 | -0.008599 | 0.04244 | 0.069591 | 0.036387 | -66.9853 | 0.019721 | -66.9154 | 56.4304 | 56.2296 | 56.3489 | -67.0527 | -66.9672 | 0.018674 | -67.0795 | 56.1894 | 56.4862 | 56.2971 | -67.1935 | -0.10936 | -0.066796 | -0.041986 | 0.027958 | 0.13732 | -0.26764 | -0.1483 | -0.2501 | -0.3078 | -0.023804 | -0.13615 | 0.11395 | -0.011002 | -0.2001 | 123.3738 | 123.1729 | 123.2922 | 66.9631 | -123.5499 | 123.1327 | 123.4295 | 123.2404 | 66.962 | -123.6906
523.2656 | 123.6969 | -66.98 | 56.5063 | 0.06235 | -0.019482 | -0.0080125 | 0.037433 | -0.0097819 | 0.036576 | 0.050216 | -0.0070587 | -0.009667 | 0.043508 | 0.068522 | 0.035319 | -66.9853 | 0.010564 | -66.9108 | 56.4304 | 56.2341 | 56.3535 | -67.0573 | -66.9717 | 0.023253 | -67.0703 | 56.1985 | 56.4725 | 56.2925 | -67.1889 | -0.077322 | -0.075952 | -0.005365 | 0.069157 | 0.14648 | -0.27222 | -0.15288 | -0.20889 | -0.3078 | 0.008239 | -0.090369 | 0.11853 | -0.033894 | -0.21384 | 123.4104 | 123.2141 | 123.3334 | 66.9905 | -123.5637 | 123.1785 | 123.4524 | 123.2725 | 67.0032 | -123.6952
524.2812 | 123.7656 | -66.9525 | 56.488 | 0.06235 | -0.018413 | -0.0080125 | 0.038501 | -0.0087139 | 0.035507 | 0.065477 | -0.0081267 | -0.007531 | 0.04244 | 0.069591 | 0.035319 | -66.9899 | 0.019721 | -66.92 | 56.4304 | 56.2341 | 56.3489 | -67.0481 | -66.9672 | 0.014095 | -67.0749 | 56.2031 | 56.4816 | 56.32 | -67.1889 | -0.095629 | -0.057641 | -0.037409 | 0.032536 | 0.12816 | -0.25391 | -0.13915 | -0.23636 | -0.28491 | -0.014648 | -0.12241 | 0.11395 | -0.006426 | -0.16805 | 123.3829 | 123.1866 | 123.3014 | 66.9722 | -123.5362 | 123.1556 | 123.4341 | 123.2725 | 66.9666 | -123.6769
525.2656 | 123.7381 | -66.9617 | 56.4972 | 0.06235 | -0.017345 | -0.0080125 | 0.036364 | -0.0087139 | 0.038712 | 0.065477 | -0.0091947 | -0.009667 | 0.043508 | 0.069591 | 0.036387 | -66.9853 | 0.015142 | -66.9108 | 56.435 | 56.2296 | 56.3535 | -67.0344 | -66.9717 | 0.014095 | -67.0749 | 56.1985 | 56.4862 | 56.2971 | -67.1889 | -0.072738 | -0.062218 | -0.023675 | 0.050847 | 0.12359 | -0.26764 | -0.14372 | -0.2272 | -0.29865 | -0.010071 | -0.11326 | 0.11395 | -0.011002 | -0.2001 | 123.3966 | 123.1912 | 123.3151 | 66.9768 | -123.5316 | 123.1602 | 123.4479 | 123.2588 | 66.9758 | -123.6861
526.2656 | 123.6969 | -66.9846 | 56.4697 | 0.06235 | -0.019482 | -0.0080125 | 0.036364 | -0.010851 | 0.036576 | 0.065477 | -0.0070587 | -0.009667 | 0.043508 | 0.067454 | 0.036387 | -66.9808 | 0.019721 | -66.9062 | 56.4258 | 56.2341 | 56.3489 | -67.039 | -66.9763 | 0.018674 | -67.0749 | 56.194 | 56.4816 | 56.3154 | -67.1843 | -0.054429 | -0.04391 | 0.003791 | 0.078313 | 0.13274 | -0.2356 | -0.12084 | -0.19974 | -0.27576 | 0.008238 | -0.090369 | 0.10937 | 0.011884 | -0.15432 | 123.4104 | 123.2187 | 123.3334 | 67.0043 | -123.5087 | 123.1785 | 123.4662 | 123.3 | 67.0032 | -123.654
527.2656 | 123.7061 | -66.9937 | 56.4514 | 0.031826 | -0.018413 | -0.01015 | 0.037433 | -0.0087139 | 0.035507 | 0.034955 | -0.0081267 | -0.009667 | 0.043508 | 0.068522 | 0.036387 | -66.9899 | 0.019721 | -66.9108 | 56.4304 | 56.2296 | 56.3535 | -67.0344 | -66.9717 | 0.018674 | -67.0749 | 56.1985 | 56.4816 | 56.3246 | -67.1797 | -0.040695 | -0.02102 | 0.003789 | 0.08289 | 0.12359 | -0.22186 | -0.097947 | -0.186 | -0.25287 | 0.021972 | -0.081214 | 0.10479 | 0.030195 | -0.12685 | 123.4241 | 123.2233 | 123.3472 | 67.0134 | -123.4858 | 123.1923 | 123.4753 | 123.3183 | 67.0124 | -123.6311
528.2656 | 123.7289 | -66.9617 | 56.456 | 0.06235 | -0.018413 | -0.0080125 | 0.035296 | -0.0097819 | 0.037644 | 0.050216 | -0.0070587 | -0.008599 | 0.04244 | 0.068522 | 0.035319 | -66.9853 | 0.010564 | -66.9154 | 56.4304 | 56.2387 | 56.3535 | -67.0436 | -66.9717 | 0.018674 | -67.0749 | 56.194 | 56.4816 | 56.2971 | -67.1843 | -0.081895 | -0.025598 | -0.023675 | 0.046269 | 0.12816 | -0.21728 | -0.10252 | -0.22263 | -0.26203 | -0.010071 | -0.11326 | 0.10937 | 0.025617 | -0.1589 | 123.3921 | 123.2004 | 123.3151 | 66.9722 | -123.4996 | 123.1556 | 123.4433 | 123.2588 | 66.9803 | -123.6403
529.2812 | 123.761 | -66.9525 | 56.488 | 0.047088 | -0.018413 | -0.0069445 | 0.036364 | -0.010851 | 0.037644 | 0.065477 | -0.0091947 | -0.008599 | 0.04244 | 0.070659 | 0.036387 | -66.9945 | 0.019721 | -66.9108 | 56.435 | 56.225 | 56.358 | -67.0481 | -66.9809 | 0.018674 | -67.0703 | 56.2077 | 56.477 | 56.3062 | -67.1843 | -0.095629 | -0.053063 | -0.041987 | 0.041692 | 0.13732 | -0.26306 | -0.12999 | -0.23178 | -0.28034 | -0.028384 | -0.11783 | 0.11395 | -0.011004 | -0.18179 | 123.3875 | 123.1775 | 123.3106 | 66.9722 | -123.5362 | 123.1602 | 123.4295 | 123.2588 | 66.9712 | -123.6723
530.2656 | 123.7015 | -66.9525 | 56.4514 | 0.047088 | -0.017345 | -0.0080125 | 0.036364 | -0.0087139 | 0.036576 | 0.050216 | -0.0081267 | -0.008599 | 0.043508 | 0.069591 | 0.036387 | -66.9808 | 0.019721 | -66.9154 | 56.4304 | 56.2341 | 56.3626 | -67.039 | -66.9717 | 0.014095 | -67.0658 | 56.194 | 56.4816 | 56.3246 | -67.1843 | -0.086472 | -0.02102 | -0.028252 | 0.037114 | 0.12359 | -0.21729 | -0.08879 | -0.23178 | -0.25745 | -0.019226 | -0.11325 | 0.11853 | 0.030195 | -0.12685 | 123.3829 | 123.1866 | 123.3151 | 66.9722 | -123.4904 | 123.1465 | 123.4341 | 123.2771 | 66.9666 | -123.6357
531.2812 | 123.674 | -66.9754 | 56.4972 | 0.047088 | -0.018413 | -0.0080125 | 0.036364 | -0.0097819 | 0.035507 | 0.080738 | -0.0070587 | -0.006462 | 0.04244 | 0.069591 | 0.036387 | -66.9899 | 0.015142 | -66.9108 | 56.4304 | 56.2341 | 56.3535 | -67.0619 | -66.9717 | 0.018674 | -67.0703 | 56.2031 | 56.4862 | 56.2925 | -67.1889 | -0.086478 | -0.066796 | -0.014521 | 0.06458 | 0.15106 | -0.26306 | -0.14372 | -0.21347 | -0.29407 | 0.003662 | -0.094946 | 0.11853 | -0.011002 | -0.20468 | 123.4058 | 123.2095 | 123.3289 | 66.9905 | -123.5591 | 123.1785 | 123.4616 | 123.2679 | 66.9941 | -123.6861
532.2656 | 123.7015 | -66.9708 | 56.4697 | 0.077612 | -0.018413 | -0.0080125 | 0.036364 | -0.010851 | 0.035507 | 0.065477 | -0.0081267 | -0.007531 | 0.043508 | 0.069591 | 0.03425 | -66.9762 | 0.019721 | -66.9108 | 56.4304 | 56.2296 | 56.358 | -67.0527 | -66.9717 | 0.009516 | -67.0749 | 56.194 | 56.4862 | 56.3291 | -67.1889 | -0.081898 | -0.039331 | -0.005363 | 0.060002 | 0.1419 | -0.24018 | -0.11168 | -0.21805 | -0.27576 | -0.000916 | -0.1041 | 0.11395 | 0.016463 | -0.14059 | 123.4012 | 123.2004 | 123.3289 | 66.9905 | -123.5224 | 123.1648 | 123.457 | 123.3 | 66.9803 | -123.6586
533.2656 | 123.7289 | -66.9617 | 56.4331 | 0.06235 | -0.017345 | -0.0069445 | 0.035296 | -0.0097819 | 0.034439 | 0.065477 | -0.0070587 | -0.008599 | 0.044577 | 0.070659 | 0.036387 | -66.9899 | 0.010564 | -66.9108 | 56.435 | 56.2296 | 56.358 | -67.0481 | -66.9717 | 0.009516 | -67.0749 | 56.1985 | 56.4816 | 56.2925 | -67.1889 | -0.086474 | 0.001869 | -0.028254 | 0.050847 | 0.13732 | -0.20355 | -0.075057 | -0.2272 | -0.23456 | -0.010071 | -0.11326 | 0.11395 | 0.048506 | -0.14059 | 123.3966 | 123.1912 | 123.3197 | 66.9722 | -123.4812 | 123.1602 | 123.4433 | 123.2542 | 66.9712 | -123.622
534.2812 | 123.6832 | -66.9754 | 56.4926 | 0.016564 | -0.018413 | -0.0069445 | 0.034227 | -0.0087139 | 0.037644 | 0.065477 | -0.0070587 | -0.009667 | 0.04244 | 0.070659 | 0.036387 | -66.9808 | 0.010564 | -66.9108 | 56.4396 | 56.2341 | 56.3535 | -67.0573 | -66.9717 | 0.014095 | -67.0703 | 56.1985 | 56.4816 | 56.2788 | -67.1843 | -0.081899 | -0.053062 | -0.005364 | 0.06458 | 0.14648 | -0.25848 | -0.13915 | -0.20889 | -0.29407 | 0.003662 | -0.094946 | 0.11395 | -0.011004 | -0.21384 | 123.415 | 123.2095 | 123.3289 | 66.986 | -123.5499 | 123.1739 | 123.457 | 123.2542 | 66.9895 | -123.6769
535.2656 | 123.7244 | -66.9754 | 56.456 | 0.047088 | -0.018413 | -0.0090815 | 0.036364 | -0.0076459 | 0.034439 | 0.065477 | -0.0081267 | -0.009667 | 0.04244 | 0.068522 | 0.035319 | -66.9853 | 0.0243 | -66.9108 | 56.435 | 56.2341 | 56.3535 | -67.0481 | -66.9717 | 0.014095 | -67.0703 | 56.1985 | 56.4816 | 56.32 | -67.1889 | -0.072741 | -0.02102 | -0.009942 | 0.06458 | 0.13732 | -0.22186 | -0.10252 | -0.21347 | -0.25745 | 0.003662 | -0.094946 | 0.11853 | 0.025617 | -0.13601 | 123.4104 | 123.2095 | 123.3289 | 66.9997 | -123.5041 | 123.1739 | 123.457 | 123.2954 | 66.9895 | -123.6449
536.2656 | 123.7335 | -66.9708 | 56.4697 | 0.031826 | -0.019482 | -0.0080125 | 0.035296 | -0.0097819 | 0.036576 | 0.050216 | -0.0081267 | -0.009667 | 0.041372 | 0.070659 | 0.036387 | -66.9853 | 0.019721 | -66.9108 | 56.4258 | 56.2296 | 56.3489 | -67.0527 | -66.9717 | 0.027831 | -67.0703 | 56.1985 | 56.477 | 56.3246 | -67.1935 | -0.081898 | -0.04391 | -0.01452 | 0.060002 | 0.1419 | -0.24018 | -0.12084 | -0.22263 | -0.27118 | -0.000916 | -0.099524 | 0.12311 | 0.007306 | -0.14516 | 123.3966 | 123.2004 | 123.3197 | 66.9905 | -123.5224 | 123.1694 | 123.4479 | 123.2954 | 66.9987 | -123.6632
537.2656 | 123.7427 | -66.9708 | 56.4651 | 0.047088 | -0.018413 | -0.0090815 | 0.037433 | -0.012987 | 0.036576 | 0.065477 | -0.0081267 | -0.008599 | 0.04244 | 0.070659 | 0.035319 | -66.9899 | 0.0243 | -66.9108 | 56.4258 | 56.2204 | 56.3489 | -67.0527 | -66.9672 | 0.009516 | -67.0703 | 56.1894 | 56.4816 | 56.3017 | -67.1843 | -0.081898 | -0.039332 | -0.019099 | 0.060002 | 0.1419 | -0.24475 | -0.11626 | -0.21347 | -0.27576 | 0.003662 | -0.099524 | 0.11395 | 0.016462 | -0.16348 | 123.3966 | 123.1912 | 123.3197 | 66.9951 | -123.5179 | 123.1602 | 123.4524 | 123.2725 | 66.9803 | -123.6494
538.2656 | 123.7289 | -66.9525 | 56.4743 | 0.047088 | -0.019482 | -0.0080125 | 0.036364 | -0.0087139 | 0.036576 | 0.065477 | -0.0070587 | -0.007531 | 0.043508 | 0.071727 | 0.035319 | -66.9853 | 0.019721 | -66.9108 | 56.4258 | 56.2387 | 56.3489 | -67.0527 | -66.9672 | 0.018674 | -67.0749 | 56.1985 | 56.4816 | 56.3291 | -67.198 | -0.10021 | -0.048487 | -0.03283 | 0.041692 | 0.1419 | -0.23559 | -0.12541 | -0.24552 | -0.27576 | -0.014648 | -0.12241 | 0.12311 | 0.007307 | -0.14516 | 123.3783 | 123.1912 | 123.3014 | 66.9722 | -123.527 | 123.1511 | 123.4341 | 123.2817 | 66.9712 | -123.6723
539.2812 | 123.6877 | -66.9662 | 56.5018 | 0.06235 | -0.02055 | -0.0090815 | 0.036364 | -0.010851 | 0.035507 | 0.050216 | -0.0070587 | -0.007531 | 0.04244 | 0.070659 | 0.03425 | -66.9808 | 0.019721 | -66.9108 | 56.4258 | 56.2204 | 56.3535 | -67.0481 | -66.9717 | 0.009516 | -67.0749 | 56.1985 | 56.4816 | 56.2971 | -67.1889 | -0.081896 | -0.075953 | -0.014519 | 0.055425 | 0.13732 | -0.28137 | -0.1483 | -0.22263 | -0.30322 | -0.005493 | -0.10868 | 0.11395 | -0.020159 | -0.20468 | 123.3921 | 123.1866 | 123.3197 | 66.986 | -123.5499 | 123.1648 | 123.4479 | 123.2633 | 66.9758 | -123.6906
540.2656 | 123.761 | -66.9571 | 56.456 | 0.031826 | -0.019482 | -0.0080125 | 0.035296 | -0.0097819 | 0.036576 | 0.050216 | -0.0091947 | -0.007531 | 0.041372 | 0.068522 | 0.035319 | -66.9899 | 0.015142 | -66.9108 | 56.4304 | 56.2296 | 56.3489 | -67.0481 | -66.9717 | 0.014095 | -67.0658 | 56.1985 | 56.4908 | 56.3017 | -67.1843 | -0.091052 | -0.025598 | -0.032832 | 0.046269 | 0.13732 | -0.22644 | -0.1071 | -0.2272 | -0.25745 | -0.014649 | -0.10868 | 0.11853 | 0.034775 | -0.15433 | 123.3875 | 123.1866 | 123.306 | 66.9722 | -123.5041 | 123.1556 | 123.4479 | 123.2588 | 66.9712 | -123.6403
541.2656 | 123.6832 | -67.0212 | 56.4926 | 0.06235 | -0.019482 | -0.0080125 | 0.035296 | -0.0087139 | 0.035507 | 0.065477 | -0.0070587 | -0.008599 | 0.041372 | 0.070659 | 0.036387 | -66.9808 | 0.0243 | -66.9108 | 56.4304 | 56.225 | 56.358 | -67.0527 | -66.9717 | 0.014095 | -67.0658 | 56.194 | 56.4816 | 56.3154 | -67.1889 | -0.031544 | -0.062219 | 0.040412 | 0.11036 | 0.1419 | -0.26764 | -0.13457 | -0.1677 | -0.29865 | 0.049438 | -0.044591 | 0.1231 | -0.011004 | -0.17721 | 123.4516 | 123.2462 | 123.3792 | 67.0455 | -123.5453 | 123.2151 | 123.5028 | 123.3366 | 67.0353 | -123.6815
542.2656 | 123.7335 | -66.9754 | 56.456 | 0.06235 | -0.017345 | -0.0080125 | 0.035296 | -0.0097819 | 0.035507 | 0.065477 | -0.0081267 | -0.008599 | 0.041372 | 0.070659 | 0.03425 | -66.9853 | 0.019721 | -66.9108 | 56.4258 | 56.2296 | 56.3489 | -67.0481 | -66.9672 | 0.018674 | -67.0703 | 56.194 | 56.4908 | 56.32 | -67.1843 | -0.072741 | -0.030177 | -0.009942 | 0.06458 | 0.13732 | -0.22644 | -0.1071 | -0.20889 | -0.26203 | 0.00824 | -0.094946 | 0.11395 | 0.034775 | -0.13601 | 123.4012 | 123.205 | 123.3243 | 66.9951 | -123.5041 | 123.1694 | 123.4662 | 123.2954 | 66.9941 | -123.6403
543.2656 | 123.7427 | -66.9846 | 56.4926 | 0.047088 | -0.018413 | -0.0080125 | 0.033159 | -0.0097819 | 0.037644 | 0.050216 | -0.0091947 | -0.009667 | 0.041372 | 0.069591 | 0.033182 | -66.9899 | 0.019721 | -66.9154 | 56.435 | 56.2341 | 56.3443 | -67.0436 | -66.9717 | 0.014095 | -67.0658 | 56.194 | 56.4908 | 56.2971 | -67.1889 | -0.059007 | -0.057641 | -0.005366 | 0.069157 | 0.12816 | -0.25848 | -0.1483 | -0.20432 | -0.29865 | 0.012817 | -0.081212 | 0.1231 | -0.001846 | -0.19553 | 123.4195 | 123.2187 | 123.3289 | 67.0043 | -123.5362 | 123.1785 | 123.4753 | 123.2816 | 66.9987 | -123.6815
544.2812 | 123.7244 | -66.98 | 56.488 | 0.06235 | -0.018413 | -0.0069445 | 0.035296 | -0.011919 | 0.035507 | 0.065477 | -0.0091947 | -0.009667 | 0.040304 | 0.071727 | 0.035319 | -66.9899 | 0.015142 | -66.9154 | 56.4304 | 56.225 | 56.3626 | -67.0481 | -66.9717 | 0.018674 | -67.0658 | 56.1985 | 56.4862 | 56.3291 | -67.1843 | -0.068164 | -0.057641 | -0.009944 | 0.064579 | 0.13274 | -0.26306 | -0.12541 | -0.20432 | -0.28949 | 0.008239 | -0.08579 | 0.11853 | -0.001847 | -0.1589 | 123.4104 | 123.205 | 123.3426 | 66.9951 | -123.5362 | 123.1785 | 123.4662 | 123.3091 | 66.9987 | -123.6723
545.2656 | 123.7198 | -66.9891 | 56.4423 | 0.047088 | -0.02055 | -0.0069445 | 0.035296 | -0.0097819 | 0.033371 | 0.050216 | -0.0070587 | -0.009667 | 0.040304 | 0.071727 | 0.035319 | -66.9762 | 0.0243 | -66.9017 | 56.4304 | 56.2387 | 56.358 | -67.0665 | -66.9763 | 0.009516 | -67.0749 | 56.2031 | 56.4862 | 56.3566 | -67.1797 | -0.077324 | -0.011865 | 0.012948 | 0.08747 | 0.16479 | -0.20355 | -0.084213 | -0.19058 | -0.23914 | 0.012816 | -0.085791 | 0.10479 | 0.043929 | -0.085649 | 123.4195 | 123.2278 | 123.3472 | 67.0134 | -123.5087 | 123.1923 | 123.4753 | 123.3457 | 66.9987 | -123.622
546.2656 | 123.7244 | -66.9708 | 56.4697 | 0.06235 | -0.019482 | -0.0080125 | 0.034227 | -0.0097819 | 0.035507 | 0.065477 | -0.0091947 | -0.009667 | 0.041372 | 0.072796 | 0.03425 | -66.9853 | 0.019721 | -66.9108 | 56.435 | 56.2296 | 56.3535 | -67.0436 | -66.9809 | 0.023253 | -67.0749 | 56.2031 | 56.4816 | 56.3612 | -67.1843 | -0.07274 | -0.034753 | -0.01452 | 0.060002 | 0.13274 | -0.24018 | -0.11626 | -0.21347 | -0.2666 | -0.010074 | -0.1041 | 0.10937 | 0.011884 | -0.10854 | 123.4058 | 123.2004 | 123.3243 | 66.9905 | -123.5133 | 123.1739 | 123.4524 | 123.332 | 66.9941 | -123.654
547.2656 | 123.7061 | -66.9662 | 56.4743 | 0.031826 | -0.019482 | -0.0080125 | 0.035296 | -0.0087139 | 0.037644 | 0.065477 | -0.0081267 | -0.009667 | 0.041372 | 0.072796 | 0.03425 | -66.9945 | 0.0243 | -66.9017 | 56.435 | 56.2341 | 56.358 | -67.071 | -66.9809 | 0.018674 | -67.0749 | 56.2031 | 56.4953 | 56.3703 | -67.1843 | -0.10479 | -0.03933 | -0.028254 | 0.064582 | 0.16937 | -0.24017 | -0.11626 | -0.21805 | -0.27118 | -0.014651 | -0.10868 | 0.10937 | 0.021043 | -0.10396 | 123.4012 | 123.2004 | 123.3243 | 66.9905 | -123.5453 | 123.1694 | 123.4616 | 123.3366 | 66.9849 | -123.6586
548.2656 | 123.6145 | -66.9983 | 56.4972 | 0.06235 | -0.019482 | -0.0080125 | 0.035296 | -0.0087139 | 0.034439 | 0.065477 | -0.0081267 | -0.008599 | 0.041372 | 0.072796 | 0.035319 | -66.9853 | 0.0243 | -66.9154 | 56.4304 | 56.2341 | 56.358 | -67.039 | -66.9672 | 0.027831 | -67.0612 | 56.2031 | 56.4862 | 56.3566 | -67.1935 | -0.040696 | -0.066796 | 0.012946 | 0.08289 | 0.12359 | -0.26306 | -0.13914 | -0.19516 | -0.29407 | 0.031128 | -0.0629 | 0.13226 | -0.011002 | -0.14058 | 123.4287 | 123.2324 | 123.3563 | 67.0226 | -123.5362 | 123.2014 | 123.4845 | 123.3549 | 67.0261 | -123.6906
549.2812 | 123.6786 | -66.9754 | 56.4606 | 0.06235 | -0.02055 | -0.0080125 | 0.036364 | -0.010851 | 0.036576 | 0.065477 | -0.0081267 | -0.009667 | 0.041372 | 0.071727 | 0.03425 | -66.9853 | 0.015142 | -66.9062 | 56.4304 | 56.2341 | 56.3535 | -67.0573 | -66.9672 | 0.018674 | -67.0749 | 56.1985 | 56.4816 | 56.3429 | -67.1935 | -0.081899 | -0.030175 | -0.009942 | 0.069158 | 0.15106 | -0.22644 | -0.1071 | -0.21805 | -0.26203 | 0.00824 | -0.099524 | 0.11853 | 0.02104 | -0.1177 | 123.4058 | 123.2095 | 123.3289 | 66.9905 | -123.5179 | 123.1739 | 123.457 | 123.3183 | 66.9941 | -123.654
550.2656 | 123.6649 | -67.012 | 56.488 | 0.047088 | -0.019482 | -0.0069445 | 0.034227 | -0.010851 | 0.036576 | 0.065477 | -0.0081267 | -0.008599 | 0.041372 | 0.072796 | 0.036387 | -66.9853 | 0.019721 | -66.9108 | 56.4304 | 56.2341 | 56.3535 | -67.0481 | -66.9763 | 0.018674 | -67.0749 | 56.194 | 56.4816 | 56.3337 | -67.1889 | -0.03612 | -0.057641 | 0.026679 | 0.1012 | 0.13732 | -0.25391 | -0.13457 | -0.17685 | -0.29407 | 0.035704 | -0.062903 | 0.11395 | -0.006426 | -0.15432 | 123.4424 | 123.2462 | 123.3655 | 67.0317 | -123.5362 | 123.206 | 123.4936 | 123.3457 | 67.0307 | -123.6769
551.2656 | 123.6237 | -67.0074 | 56.5018 | 0.06235 | -0.02055 | -0.0090815 | 0.034227 | -0.010851 | 0.034439 | 0.050216 | -0.0081267 | -0.009667 | 0.04244 | 0.073864 | 0.03425 | -66.9808 | 0.015142 | -66.9062 | 56.435 | 56.2387 | 56.3535 | -67.0527 | -66.9763 | 0.023253 | -67.0703 | 56.1985 | 56.477 | 56.3291 | -67.1843 | -0.045277 | -0.066796 | 0.026679 | 0.1012 | 0.14648 | -0.26306 | -0.1483 | -0.17685 | -0.30322 | 0.031126 | -0.062903 | 0.11395 | -0.024737 | -0.17263 | 123.4424 | 123.2462 | 123.3609 | 67.0226 | -123.5545 | 123.206 | 123.4845 | 123.3366 | 67.0307 | -123.6861
552.2656 | 123.6969 | -66.9983 | 56.4651 | 0.06235 | -0.018413 | -0.0080125 | 0.034227 | -0.0097819 | 0.035507 | 0.065477 | -0.0070587 | -0.008599 | 0.040304 | 0.072796 | 0.03425 | -66.9853 | 0.015142 | -66.92 | 56.4304 | 56.2296 | 56.358 | -67.0481 | -66.9672 | 0.018674 | -67.0658 | 56.1985 | 56.4816 | 56.32 | -67.1843 | -0.049853 | -0.034753 | 0.012946 | 0.078312 | 0.12816 | -0.2356 | -0.1071 | -0.18601 | -0.2666 | 0.031128 | -0.067479 | 0.11853 | 0.016462 | -0.14517 | 123.4287 | 123.2278 | 123.3563 | 67.0134 | -123.5133 | 123.1968 | 123.4799 | 123.3183 | 67.017 | -123.6494
553.2656 | 123.642 | -66.9846 | 56.4972 | 0.047088 | -0.02055 | -0.0069445 | 0.035296 | -0.0097819 | 0.034439 | 0.050216 | -0.0091947 | -0.008599 | 0.041372 | 0.072796 | 0.03425 | -66.9853 | 0.019721 | -66.9108 | 56.4258 | 56.2387 | 56.3535 | -67.039 | -66.9717 | 0.009516 | -67.0658 | 56.1985 | 56.4816 | 56.3246 | -67.1889 | -0.054429 | -0.071375 | -0.000787 | 0.073735 | 0.12816 | -0.25848 | -0.14372 | -0.20432 | -0.29865 | 0.012817 | -0.081212 | 0.1231 | -0.015581 | -0.17263 | 123.4104 | 123.2233 | 123.338 | 67.0043 | -123.5362 | 123.1831 | 123.4662 | 123.3091 | 66.9941 | -123.6861
554.2812 | 123.7061 | -66.9754 | 56.4743 | 0.077612 | -0.019482 | -0.0069445 | 0.035296 | -0.011919 | 0.036576 | 0.065477 | -0.0081267 | -0.009667 | 0.041372 | 0.073864 | 0.033182 | -66.9808 | 0.019721 | -66.9062 | 56.435 | 56.2341 | 56.358 | -67.0436 | -66.9672 | 0.018674 | -67.0703 | 56.1985 | 56.4862 | 56.2925 | -67.1889 | -0.068162 | -0.03933 | -0.005364 | 0.069158 | 0.13732 | -0.24017 | -0.11626 | -0.21347 | -0.27576 | 0.00824 | -0.094946 | 0.11853 | 0.011886 | -0.18179 | 123.4104 | 123.2095 | 123.3335 | 66.9951 | -123.5179 | 123.1739 | 123.4616 | 123.2679 | 66.9941 | -123.6632
555.2656 | 123.6099 | -67.0166 | 56.4835 | 0.047088 | -0.021618 | -0.0080125 | 0.035296 | -0.0087139 | 0.036576 | 0.034955 | -0.0091947 | -0.008599 | 0.041372 | 0.073864 | 0.035319 | -66.9762 | 0.0243 | -66.9062 | 56.4304 | 56.2341 | 56.3626 | -67.0436 | -66.9763 | 0.018674 | -67.0703 | 56.1985 | 56.4862 | 56.3154 | -67.1843 | -0.026963 | -0.053063 | 0.040414 | 0.11036 | 0.13732 | -0.24933 | -0.12083 | -0.16769 | -0.28491 | 0.040282 | -0.053747 | 0.11395 | 0.002731 | -0.16806 | 123.447 | 123.2507 | 123.3792 | 67.0409 | -123.527 | 123.2151 | 123.5028 | 123.332 | 67.0353 | -123.6678
556.2656 | 123.6969 | -66.98 | 56.4651 | 0.031826 | -0.021618 | -0.0090815 | 0.035296 | -0.012987 | 0.036576 | 0.050216 | -0.010263 | -0.009667 | 0.041372 | 0.073864 | 0.03425 | -66.9808 | 0.019721 | -66.9154 | 56.4304 | 56.2387 | 56.3535 | -67.0436 | -66.9763 | 0.018674 | -67.0749 | 56.1985 | 56.4908 | 56.3291 | -67.1843 | -0.063585 | -0.034753 | -0.000787 | 0.064579 | 0.12816 | -0.22644 | -0.11168 | -0.20432 | -0.2666 | 0.00366 | -0.094947 | 0.10937 | 0.02562 | -0.13601 | 123.4104 | 123.2187 | 123.3334 | 66.9997 | -123.5087 | 123.1785 | 123.4707 | 123.3091 | 66.9987 | -123.6494
557.2656 | 123.6237 | -67.0074 | 56.5063 | 0.047088 | -0.02055 | -0.0090815 | 0.034227 | -0.0097819 | 0.033371 | 0.034955 | -0.010263 | -0.008599 | 0.04244 | 0.073864 | 0.03425 | -66.9853 | 0.019721 | -66.92 | 56.4258 | 56.2433 | 56.3535 | -67.0436 | -66.9763 | 0.014095 | -67.0703 | 56.194 | 56.4862 | 56.3658 | -67.1843 | -0.036119 | -0.080531 | 0.022101 | 0.087467 | 0.12359 | -0.26306 | -0.15288 | -0.17685 | -0.31238 | 0.031126 | -0.062903 | 0.11395 | -0.020158 | -0.14058 | 123.4333 | 123.2507 | 123.3609 | 67.0272 | -123.5499 | 123.2014 | 123.4936 | 123.3732 | 67.0215 | -123.6906
558.2656 | 123.6511 | -66.98 | 56.5201 | 0.031826 | -0.022687 | -0.0080125 | 0.033159 | -0.010851 | 0.035507 | 0.095999 | -0.0091947 | -0.009667 | 0.040304 | 0.071727 | 0.03425 | -66.9853 | 0.019721 | -66.9017 | 56.4304 | 56.2433 | 56.3626 | -67.0481 | -66.9672 | 0.018674 | -67.0703 | 56.2031 | 56.4816 | 56.3703 | -67.1889 | -0.068164 | -0.089685 | -0.005365 | 0.078314 | 0.14648 | -0.27679 | -0.15745 | -0.20889 | -0.31696 | 0.012817 | -0.090369 | 0.11853 | -0.03847 | -0.14973 | 123.4104 | 123.2233 | 123.3426 | 66.9997 | -123.5682 | 123.1831 | 123.4616 | 123.3503 | 66.9987 | -123.709
559.2812 | 123.6694 | -66.9617 | 56.4835 | 0.047088 | -0.022687 | -0.0090815 | 0.036364 | -0.010851 | 0.036576 | 0.065477 | -0.0091947 | -0.008599 | 0.04244 | 0.074932 | 0.035319 | -66.9762 | 0.019721 | -66.9108 | 56.4258 | 56.2433 | 56.358 | -67.0436 | -66.9763 | 0.018674 | -67.0749 | 56.2031 | 56.4816 | 56.3749 | -67.198 | -0.081895 | -0.057642 | -0.014518 | 0.050847 | 0.13274 | -0.24017 | -0.12541 | -0.23636 | -0.28034 | -0.01465 | -0.11326 | 0.12311 | -0.001848 | -0.10853 | 123.3875 | 123.205 | 123.3197 | 66.9814 | -123.527 | 123.1648 | 123.4433 | 123.3366 | 66.9803 | -123.6815
560.2656 | 123.6374 | -67.012 | 56.488 | 0.06235 | -0.021618 | -0.0090815 | 0.034227 | -0.011919 | 0.035507 | 0.065477 | -0.010263 | -0.011804 | 0.041372 | 0.073864 | 0.036387 | -66.9853 | 0.019721 | -66.9017 | 56.4304 | 56.2387 | 56.358 | -67.0436 | -66.9672 | 0.023253 | -67.0703 | 56.2031 | 56.4862 | 56.3749 | -67.1843 | -0.031541 | -0.057641 | 0.026679 | 0.11036 | 0.1419 | -0.24933 | -0.12999 | -0.17227 | -0.28491 | 0.044861 | -0.058325 | 0.11395 | -0.001847 | -0.11311 | 123.4424 | 123.2507 | 123.3701 | 67.0317 | -123.5316 | 123.2151 | 123.4982 | 123.3869 | 67.0353 | -123.6723
561.2656 | 123.5596 | -67.0258 | 56.5247 | 0.047088 | -0.022687 | -0.0090815 | 0.035296 | -0.011919 | 0.034439 | 0.080738 | -0.0081267 | -0.011804 | 0.040304 | 0.073864 | 0.03425 | -66.9716 | 0.015142 | -66.9017 | 56.4304 | 56.2387 | 56.3626 | -67.0481 | -66.9672 | 0.014095 | -67.0658 | 56.194 | 56.4816 | 56.3749 | -67.1889 | -0.022387 | -0.094262 | 0.054147 | 0.12409 | 0.14648 | -0.28595 | -0.16203 | -0.16312 | -0.33069 | 0.058594 | -0.040013 | 0.1231 | -0.043047 | -0.14973 | 123.4562 | 123.2645 | 123.3884 | 67.0409 | -123.5728 | 123.2197 | 123.5074 | 123.4007 | 67.0399 | -123.7135
562.2656 | 123.6008 | -67.0212 | 56.4697 | 0.06235 | -0.022687 | -0.0090815 | 0.035296 | -0.011919 | 0.036576 | 0.080738 | -0.010263 | -0.009667 | 0.041372 | 0.072796 | 0.033182 | -66.9853 | 0.028878 | -66.9108 | 56.4304 | 56.2387 | 56.358 | -67.0481 | -66.9717 | 0.023253 | -67.0703 | 56.2031 | 56.4862 | 56.3749 | -67.1889 | -0.026965 | -0.039331 | 0.035834 | 0.11036 | 0.13732 | -0.23102 | -0.11168 | -0.1677 | -0.2666 | 0.049438 | -0.04917 | 0.11853 | 0.016463 | -0.094801 | 123.4516 | 123.2599 | 123.3792 | 67.0501 | -123.5179 | 123.2243 | 123.5074 | 123.3961 | 67.0444 | -123.6586
563.2656 | 123.6053 | -67.0303 | 56.5018 | 0.047088 | -0.022687 | -0.0080125 | 0.033159 | -0.010851 | 0.035507 | 0.065477 | -0.0081267 | -0.010735 | 0.040304 | 0.076001 | 0.03425 | -66.9808 | 0.028878 | -66.9108 | 56.435 | 56.2433 | 56.358 | -67.0436 | -66.9717 | 0.018674 | -67.0658 | 56.2077 | 56.4862 | 56.3703 | -67.1935 | -0.013231 | -0.066796 | 0.049567 | 0.11951 | 0.13274 | -0.25848 | -0.14372 | -0.16312 | -0.29407 | 0.058593 | -0.035436 | 0.12768 | -0.01558 | -0.13142 | 123.4653 | 123.2736 | 123.3884 | 67.0592 | -123.5453 | 123.238 | 123.5165 | 123.4007 | 67.049 | -123.6952
564.2656 | 123.6832 | -67.0029 | 56.4697 | 0.06235 | -0.023755 | -0.0080125 | 0.036364 | -0.011919 | 0.034439 | 0.065477 | -0.010263 | -0.009667 | 0.040304 | 0.073864 | 0.033182 | -66.9899 | 0.015142 | -66.9108 | 56.4396 | 56.2387 | 56.3489 | -67.0527 | -66.9763 | 0.014095 | -67.0749 | 56.1985 | 56.4862 | 56.3795 | -67.1889 | -0.049854 | -0.030174 | 0.012945 | 0.092046 | 0.1419 | -0.23102 | -0.12084 | -0.18601 | -0.27118 | 0.026549 | -0.072058 | 0.11395 | 0.016463 | -0.090222 | 123.4424 | 123.2416 | 123.3518 | 67.018 | -123.5224 | 123.2014 | 123.4891 | 123.3824 | 67.017 | -123.6586
565.2812 | 123.7015 | -66.9662 | 56.4926 | 0.06235 | -0.022687 | -0.0090815 | 0.035296 | -0.010851 | 0.035507 | 0.050216 | -0.0091947 | -0.009667 | 0.041372 | 0.077069 | 0.032114 | -66.9808 | 0.015142 | -66.9154 | 56.4396 | 56.2479 | 56.3535 | -67.0527 | -66.958 | 0.014095 | -67.0703 | 56.2031 | 56.4862 | 56.3703 | -67.1935 | -0.086475 | -0.053062 | -0.014519 | 0.050847 | 0.13732 | -0.24475 | -0.13915 | -0.22721 | -0.28949 | 0.008243 | -0.1041 | 0.12311 | -0.006425 | -0.12227 | 123.4058 | 123.2141 | 123.3197 | 66.9814 | -123.5453 | 123.1694 | 123.4524 | 123.3366 | 66.9803 | -123.6861
566.2656 | 123.6008 | -66.9846 | 56.5247 | 0.047088 | -0.02055 | -0.0090815 | 0.034227 | -0.010851 | 0.034439 | 0.065477 | -0.0081267 | -0.009667 | 0.041372 | 0.074932 | 0.03425 | -66.9808 | 0.0243 | -66.9108 | 56.4304 | 56.2433 | 56.3626 | -67.0573 | -66.9626 | 0.014095 | -67.0612 | 56.2077 | 56.4862 | 56.3703 | -67.1935 | -0.072744 | -0.094262 | 0.003791 | 0.073735 | 0.14648 | -0.28137 | -0.16203 | -0.2089 | -0.31696 | 0.021974 | -0.076633 | 0.13226 | -0.038468 | -0.15431 | 123.415 | 123.2278 | 123.3472 | 67.0089 | -123.582 | 123.1923 | 123.4707 | 123.3549 | 66.9987 | -123.7181
567.2656 | 123.5962 | -66.9983 | 56.5018 | 0.047088 | -0.023755 | -0.0080125 | 0.033159 | -0.011919 | 0.034439 | 0.080738 | -0.010263 | -0.010735 | 0.041372 | 0.074932 | 0.03425 | -66.9808 | 0.028878 | -66.9062 | 56.4396 | 56.2341 | 56.3626 | -67.0573 | -66.9717 | 0.018674 | -67.0703 | 56.2123 | 56.4816 | 56.3703 | -67.1889 | -0.059011 | -0.062217 | 0.017524 | 0.092046 | 0.15106 | -0.26764 | -0.13914 | -0.19058 | -0.28949 | 0.02655 | -0.072058 | 0.11853 | -0.020159 | -0.13142 | 123.4378 | 123.2324 | 123.3609 | 67.0272 | -123.5591 | 123.2106 | 123.4799 | 123.3686 | 67.017 | -123.6906
568.2656 | 123.6328 | -67.0029 | 56.5018 | 0.047088 | -0.021618 | -0.0080125 | 0.033159 | -0.014056 | 0.035507 | 0.050216 | -0.0091947 | -0.010735 | 0.040304 | 0.076001 | 0.033182 | -66.9808 | 0.019721 | -66.9108 | 56.435 | 56.2433 | 56.3672 | -67.0619 | -66.9763 | 0.009516 | -67.0612 | 56.2123 | 56.4816 | 56.3703 | -67.1889 | -0.059012 | -0.066796 | 0.022102 | 0.092046 | 0.15106 | -0.25848 | -0.13457 | -0.18601 | -0.28949 | 0.026549 | -0.058322 | 0.12768 | -0.020159 | -0.13142 | 123.4378 | 123.2462 | 123.3701 | 67.0226 | -123.5637 | 123.2151 | 123.4845 | 123.3732 | 67.0124 | -123.6906
569.2812 | 123.761 | -66.9662 | 56.4606 | 0.06235 | -0.021618 | -0.0080125 | 0.034227 | -0.011919 | 0.034439 | 0.050216 | -0.0091947 | -0.009667 | 0.040304 | 0.076001 | 0.033182 | -66.9853 | 0.0243 | -66.9062 | 56.4304 | 56.2433 | 56.3626 | -67.0527 | -66.9626 | 0.014095 | -67.0658 | 56.1985 | 56.477 | 56.3566 | -67.1889 | -0.086475 | -0.030175 | -0.019097 | 0.060003 | 0.14648 | -0.21728 | -0.097945 | -0.22263 | -0.26203 | 0.003664 | -0.099522 | 0.1231 | 0.016462 | -0.10396 | 123.3966 | 123.2095 | 123.3289 | 66.9905 | -123.5133 | 123.1648 | 123.4433 | 123.3229 | 66.9803 | -123.6494
570.2812 | 123.7564 | -66.98 | 56.4468 | 0.047088 | -0.022687 | -0.01015 | 0.034227 | -0.012987 | 0.034439 | 0.050216 | -0.0091947 | -0.008599 | 0.039235 | 0.078138 | 0.03425 | -66.9808 | 0.015142 | -66.9062 | 56.435 | 56.2387 | 56.358 | -67.071 | -66.9763 | 0.014095 | -67.0703 | 56.2077 | 56.477 | 56.3703 | -67.1889 | -0.091059 | -0.011864 | -0.000787 | 0.073735 | 0.16479 | -0.20813 | -0.08879 | -0.20889 | -0.23914 | 0.00366 | -0.090369 | 0.11853 | 0.030195 | -0.07649 | 123.415 | 123.2187 | 123.338 | 66.9951 | -123.5179 | 123.1877 | 123.457 | 123.3503 | 66.9941 | -123.6357
571.2656 | 123.6603 | -66.98 | 56.4835 | 0.06235 | -0.024824 | -0.0080125 | 0.034227 | -0.011919 | 0.034439 | 0.080738 | -0.0091947 | -0.010735 | 0.041372 | 0.077069 | 0.033182 | -66.9716 | 0.019721 | -66.9108 | 56.435 | 56.2524 | 56.3626 | -67.0527 | -66.9763 | 0.023253 | -67.0658 | 56.2077 | 56.4908 | 56.3795 | -67.1889 | -0.072743 | -0.048485 | 0.00837 | 0.069157 | 0.1419 | -0.23101 | -0.12083 | -0.20889 | -0.27576 | 0.00366 | -0.08579 | 0.1231 | 0.00731 | -0.10395 | 123.415 | 123.2324 | 123.3426 | 66.9997 | -123.5362 | 123.1877 | 123.4707 | 123.3595 | 67.0032 | -123.6723
572.2656 | 123.642 | -67.012 | 56.5018 | 0.06235 | -0.022687 | -0.0080125 | 0.034227 | -0.010851 | 0.034439 | 0.065477 | -0.010263 | -0.009667 | 0.041372 | 0.074932 | 0.033182 | -66.9853 | 0.0243 | -66.9108 | 56.435 | 56.2433 | 56.358 | -67.0527 | -66.9672 | 0.018674 | -67.0703 | 56.2077 | 56.4862 | 56.3749 | -67.1889 | -0.040699 | -0.066796 | 0.026679 | 0.1012 | 0.1419 | -0.25848 | -0.14372 | -0.17685 | -0.29407 | 0.044861 | -0.058325 | 0.11853 | -0.01558 | -0.12684 | 123.447 | 123.2553 | 123.3701 | 67.0363 | -123.5545 | 123.2197 | 123.4982 | 123.3869 | 67.0307 | -123.6906
573.2656 | 123.6465 | -66.9708 | 56.5155 | 0.047088 | -0.022687 | -0.0090815 | 0.033159 | -0.010851 | 0.035507 | 0.050216 | -0.0091947 | -0.009667 | 0.04244 | 0.076001 | 0.032114 | -66.9808 | 0.015142 | -66.9017 | 56.435 | 56.2387 | 56.3626 | -67.071 | -66.9717 | 0.018674 | -67.0703 | 56.2077 | 56.4908 | 56.3795 | -67.1889 | -0.10021 | -0.080529 | -0.009942 | 0.069159 | 0.16937 | -0.27679 | -0.15288 | -0.21805 | -0.3078 | -0.000916 | -0.099524 | 0.11853 | -0.024734 | -0.136 | 123.4058 | 123.2095 | 123.3335 | 66.986 | -123.5865 | 123.1785 | 123.4616 | 123.3503 | 66.9895 | -123.7044
574.2812 | 123.6465 | -67.0212 | 56.5155 | 0.06235 | -0.023755 | -0.0080125 | 0.035296 | -0.011919 | 0.033371 | 0.065477 | -0.0081267 | -0.010735 | 0.04244 | 0.077069 | 0.032114 | -66.967 | 0.0243 | -66.9108 | 56.435 | 56.2433 | 56.358 | -67.0665 | -66.9717 | 0.023253 | -67.0658 | 56.1985 | 56.4908 | 56.3658 | -67.1935 | -0.045281 | -0.080529 | 0.054147 | 0.11036 | 0.15564 | -0.27221 | -0.15746 | -0.17227 | -0.31696 | 0.049438 | -0.044591 | 0.12768 | -0.024734 | -0.14973 | 123.4562 | 123.2645 | 123.3792 | 67.0455 | -123.582 | 123.2197 | 123.5119 | 123.3869 | 67.0444 | -123.709
575.2812 | 123.6877 | -66.9571 | 56.4789 | 0.047088 | -0.023755 | -0.0080125 | 0.034227 | -0.011919 | 0.036576 | 0.050216 | -0.0070587 | -0.008599 | 0.040304 | 0.077069 | 0.032114 | -66.9808 | 0.015142 | -66.9062 | 56.435 | 56.2433 | 56.358 | -67.0573 | -66.9626 | 0.014095 | -67.0612 | 56.1985 | 56.477 | 56.352 | -67.1843 | -0.10021 | -0.043908 | -0.023675 | 0.050847 | 0.15106 | -0.23559 | -0.12083 | -0.2272 | -0.28034 | -0.005492 | -0.1041 | 0.12311 | -0.001849 | -0.12685 | 123.3921 | 123.2004 | 123.3151 | 66.9722 | -123.5362 | 123.1556 | 123.4341 | 123.3091 | 66.9712 | -123.6632
576.2656 | 123.6557 | -66.98 | 56.5247 | 0.06235 | -0.022687 | -0.0090815 | 0.034227 | -0.011919 | 0.036576 | 0.065477 | -0.010263 | -0.010735 | 0.040304 | 0.074932 | 0.033182 | -66.9899 | 0.019721 | -66.9017 | 56.4304 | 56.2433 | 56.3672 | -67.0481 | -66.9672 | 0.014095 | -67.0612 | 56.2077 | 56.4862 | 56.3703 | -67.1889 | -0.068164 | -0.094262 | -0.009944 | 0.078314 | 0.14648 | -0.28137 | -0.15745 | -0.20889 | -0.31696 | 0.012817 | -0.081211 | 0.12768 | -0.038468 | -0.15431 | 123.4104 | 123.2233 | 123.3472 | 66.9997 | -123.5728 | 123.1877 | 123.4662 | 123.3503 | 66.9941 | -123.7135
577.2656 | 123.6374 | -66.9708 | 56.5109 | 0.06235 | -0.022687 | -0.0080125 | 0.033159 | -0.010851 | 0.034439 | 0.065477 | -0.0070587 | -0.008599 | 0.040304 | 0.077069 | 0.032114 | -66.9762 | 0.015142 | -66.9154 | 56.4396 | 56.2341 | 56.3626 | -67.0573 | -66.9626 | 0.009516 | -67.0658 | 56.2031 | 56.4862 | 56.3612 | -67.1889 | -0.086477 | -0.071372 | -0.005363 | 0.055424 | 0.1419 | -0.27679 | -0.1483 | -0.21805 | -0.3078 | 0.008241 | -0.094945 | 0.1231 | -0.024735 | -0.14973 | 123.4104 | 123.205 | 123.3335 | 66.986 | -123.5682 | 123.1739 | 123.457 | 123.332 | 66.9803 | -123.6998
578.2656 | 123.6374 | -66.9983 | 56.5201 | 0.047088 | -0.022687 | -0.01015 | 0.035296 | -0.0097819 | 0.035507 | 0.080738 | -0.0070587 | -0.010735 | 0.039235 | 0.076001 | 0.029977 | -66.9808 | 0.015142 | -66.9062 | 56.435 | 56.2479 | 56.3672 | -67.0436 | -66.9763 | 0.018674 | -67.0658 | 56.2031 | 56.4862 | 56.3658 | -67.1889 | -0.045274 | -0.085107 | 0.017524 | 0.092046 | 0.13732 | -0.27221 | -0.15288 | -0.19058 | -0.31696 | 0.021971 | -0.067479 | 0.1231 | -0.033891 | -0.15431 | 123.4333 | 123.2462 | 123.3655 | 67.0134 | -123.5636 | 123.2014 | 123.4845 | 123.3641 | 67.017 | -123.709
579.2656 | 123.6786 | -66.9708 | 56.4926 | 0.06235 | -0.022687 | -0.0080125 | 0.033159 | -0.012987 | 0.035507 | 0.050216 | -0.010263 | -0.009667 | 0.040304 | 0.077069 | 0.032114 | -66.9808 | 0.010564 | -66.92 | 56.4396 | 56.2524 | 56.358 | -67.0481 | -66.9626 | 0.014095 | -67.0658 | 56.2031 | 56.4862 | 56.3658 | -67.1889 | -0.077319 | -0.053062 | -0.009942 | 0.050846 | 0.12816 | -0.24017 | -0.13457 | -0.21805 | -0.28949 | 0.008241 | -0.094945 | 0.1231 | -0.006425 | -0.12685 | 123.4104 | 123.2233 | 123.3289 | 66.9814 | -123.5408 | 123.1739 | 123.457 | 123.3366 | 66.9849 | -123.6815
580.2812 | 123.674 | -66.98 | 56.456 | 0.047088 | -0.021618 | -0.0090815 | 0.035296 | -0.0097819 | 0.034439 | 0.034955 | -0.0091947 | -0.009667 | 0.039235 | 0.079206 | 0.033182 | -66.9762 | 0.015142 | -66.9062 | 56.435 | 56.2341 | 56.358 | -67.0481 | -66.9672 | 0.018674 | -67.0703 | 56.194 | 56.4908 | 56.3154 | -67.1843 | -0.068164 | -0.02102 | 0.003792 | 0.073735 | 0.1419 | -0.22186 | -0.097946 | -0.20432 | -0.26203 | 0.012817 | -0.090369 | 0.11395 | 0.034775 | -0.14059 | 123.415 | 123.2141 | 123.338 | 66.9951 | -123.5041 | 123.1739 | 123.4707 | 123.2954 | 66.9987 | -123.6403
581.2656 | 123.6237 | -66.9937 | 56.5155 | 0.06235 | -0.021618 | -0.0069445 | 0.036364 | -0.010851 | 0.036576 | 0.050216 | -0.0070587 | -0.009667 | 0.038167 | 0.077069 | 0.033182 | -66.9853 | 0.019721 | -66.9108 | 56.435 | 56.2296 | 56.3626 | -67.0573 | -66.9717 | 0.014095 | -67.0612 | 56.2031 | 56.4862 | 56.3383 | -67.1935 | -0.063589 | -0.080529 | 0.008368 | 0.08289 | 0.14648 | -0.28595 | -0.15288 | -0.19974 | -0.31238 | 0.021972 | -0.067478 | 0.13226 | -0.029313 | -0.17721 | 123.4287 | 123.2233 | 123.3563 | 67.0134 | -123.5728 | 123.1968 | 123.4799 | 123.332 | 67.0078 | -123.709
582.2656 | 123.6465 | -66.9937 | 56.5018 | 0.06235 | -0.021618 | -0.0069445 | 0.033159 | -0.0097819 | 0.034439 | 0.050216 | -0.0070587 | -0.010735 | 0.039235 | 0.077069 | 0.033182 | -66.9762 | 0.010564 | -66.9108 | 56.4396 | 56.2387 | 56.358 | -67.0665 | -66.9626 | 0.009516 | -67.052 | 56.1985 | 56.4816 | 56.3337 | -67.1889 | -0.072747 | -0.062217 | 0.017525 | 0.08289 | 0.15564 | -0.26306 | -0.14372 | -0.19516 | -0.30322 | 0.031129 | -0.058321 | 0.13684 | -0.020159 | -0.16805 | 123.4333 | 123.2324 | 123.3518 | 67.0043 | -123.5682 | 123.1923 | 123.4753 | 123.3274 | 67.0032 | -123.6906
583.2656 | 123.6694 | -66.9662 | 56.5384 | 0.047088 | -0.022687 | -0.01015 | 0.035296 | -0.0097819 | 0.034439 | 0.080738 | -0.0081267 | -0.009667 | 0.041372 | 0.077069 | 0.033182 | -66.9808 | 0.019721 | -66.9062 | 56.4304 | 56.2296 | 56.3672 | -67.0573 | -66.9717 | 0.014095 | -67.0612 | 56.2077 | 56.4953 | 56.3246 | -67.198 | -0.091054 | -0.10799 | -0.014519 | 0.060003 | 0.15106 | -0.30884 | -0.17119 | -0.23179 | -0.33069 | -0.005493 | -0.094943 | 0.13684 | -0.043044 | -0.21383 | 123.3966 | 123.1958 | 123.3335 | 66.986 | -123.5957 | 123.1739 | 123.4616 | 123.2908 | 66.9803 | -123.7364
584.2812 | 123.6832 | -66.98 | 56.488 | 0.06235 | -0.023755 | -0.01015 | 0.034227 | -0.012987 | 0.035507 | 0.080738 | -0.0091947 | -0.008599 | 0.038167 | 0.077069 | 0.031046 | -66.9853 | 0.010564 | -66.9062 | 56.435 | 56.2433 | 56.3626 | -67.0619 | -66.958 | 0.014095 | -67.0566 | 56.2123 | 56.4953 | 56.3154 | -67.1889 | -0.081901 | -0.053063 | -0.005365 | 0.073735 | 0.15564 | -0.24475 | -0.12541 | -0.20889 | -0.27576 | 0.021975 | -0.076632 | 0.13226 | 0.00731 | -0.17263 | 123.415 | 123.2233 | 123.3426 | 66.9905 | -123.5499 | 123.1923 | 123.4753 | 123.2954 | 66.9941 | -123.6769
585.2656 | 123.6511 | -66.9662 | 56.543 | 0.077612 | -0.021618 | -0.0090815 | 0.033159 | -0.010851 | 0.033371 | 0.095999 | -0.0091947 | -0.007531 | 0.041372 | 0.078138 | 0.031046 | -66.9716 | 0.015142 | -66.9062 | 56.4396 | 56.2433 | 56.358 | -67.0527 | -66.9672 | 0.014095 | -67.0612 | 56.2031 | 56.4953 | 56.3658 | -67.1797 | -0.086475 | -0.10342 | -0.005362 | 0.060003 | 0.14648 | -0.29968 | -0.18492 | -0.21347 | -0.33984 | -0.000915 | -0.094943 | 0.11853 | -0.047622 | -0.1772 | 123.4058 | 123.2095 | 123.3243 | 66.9814 | -123.5957 | 123.1694 | 123.4616 | 123.332 | 66.9803 | -123.7227
586.2656 | 123.6191 | -66.9891 | 56.5109 | 0.077612 | -0.022687 | -0.0090815 | 0.033159 | -0.010851 | 0.033371 | 0.050216 | -0.010263 | -0.008599 | 0.041372 | 0.077069 | 0.032114 | -66.9716 | 0.010564 | -66.9017 | 56.435 | 56.2479 | 56.358 | -67.0481 | -66.958 | 0.018674 | -67.0612 | 56.2077 | 56.4862 | 56.3658 | -67.1843 | -0.059008 | -0.075951 | 0.017526 | 0.08747 | 0.14648 | -0.26306 | -0.15288 | -0.19516 | -0.30322 | 0.031131 | -0.072055 | 0.12311 | -0.024735 | -0.14516 | 123.4241 | 123.237 | 123.3472 | 66.9997 | -123.5591 | 123.1968 | 123.4753 | 123.3549 | 67.0078 | -123.6952
587.2656 | 123.6374 | -67.0029 | 56.5384 | 0.047088 | -0.022687 | -0.0090815 | 0.032091 | -0.011919 | 0.034439 | 0.080738 | -0.0091947 | -0.009667 | 0.040304 | 0.078138 | 0.032114 | -66.9762 | 0.010564 | -66.9017 | 56.4396 | 56.2387 | 56.3672 | -67.0527 | -66.9672 | 0.018674 | -67.0703 | 56.2031 | 56.4862 | 56.3475 | -67.1889 | -0.049854 | -0.098838 | 0.026681 | 0.1012 | 0.15106 | -0.29968 | -0.17119 | -0.18601 | -0.33527 | 0.035706 | -0.06748 | 0.11853 | -0.052201 | -0.19094 | 123.4424 | 123.2416 | 123.3701 | 67.0134 | -123.5911 | 123.206 | 123.4891 | 123.3503 | 67.0215 | -123.7273
588.2656 | 123.6832 | -66.9617 | 56.5109 | 0.06235 | -0.023755 | -0.0090815 | 0.033159 | -0.010851 | 0.033371 | 0.065477 | -0.010263 | -0.009667 | 0.040304 | 0.078138 | 0.032114 | -66.9808 | 0.010564 | -66.9062 | 56.4304 | 56.2479 | 56.3626 | -67.0481 | -66.9672 | 0.014095 | -67.0612 | 56.2031 | 56.4816 | 56.3612 | -67.1935 | -0.086474 | -0.080529 | -0.019097 | 0.055425 | 0.1419 | -0.26306 | -0.1483 | -0.23178 | -0.3078 | -0.005493 | -0.099521 | 0.13226 | -0.029314 | -0.14973 | 123.3921 | 123.2095 | 123.3243 | 66.9722 | -123.5591 | 123.1648 | 123.4433 | 123.3229 | 66.9758 | -123.7044
589.2812 | 123.6603 | -66.9937 | 56.5018 | 0.031826 | -0.022687 | -0.0080125 | 0.033159 | -0.012987 | 0.034439 | 0.080738 | -0.0091947 | -0.008599 | 0.040304 | 0.078138 | 0.032114 | -66.9808 | 0.019721 | -66.9154 | 56.4396 | 56.2479 | 56.3672 | -67.0527 | -66.9763 | 0.018674 | -67.052 | 56.2123 | 56.4862 | 56.3703 | -67.1935 | -0.05901 | -0.062217 | 0.012946 | 0.078312 | 0.13732 | -0.2539 | -0.13457 | -0.19974 | -0.28949 | 0.017393 | -0.058321 | 0.14142 | -0.01558 | -0.13142 | 123.4333 | 123.2416 | 123.3609 | 67.0134 | -123.5545 | 123.206 | 123.4799 | 123.3641 | 67.0124 | -123.6952
590.2656 | 123.7381 | -66.9388 | 56.456 | 0.06235 | -0.022687 | -0.01015 | 0.033159 | -0.010851 | 0.035507 | 0.065477 | -0.0081267 | -0.009667 | 0.040304 | 0.079206 | 0.032114 | -66.9808 | 0.010564 | -66.9062 | 56.435 | 56.2387 | 56.3626 | -67.0527 | -66.958 | 0.004938 | -67.0658 | 56.2031 | 56.4862 | 56.3703 | -67.1889 | -0.11394 | -0.02102 | -0.041985 | 0.032537 | 0.14648 | -0.21728 | -0.093368 | -0.25009 | -0.25287 | -0.019223 | -0.12699 | 0.1231 | 0.030196 | -0.085646 | 123.3738 | 123.1775 | 123.3014 | 66.9493 | -123.5087 | 123.1419 | 123.425 | 123.3091 | 66.9437 | -123.6449
591.2812 | 123.6374 | -66.98 | 56.5155 | 0.06235 | -0.023755 | -0.01015 | 0.033159 | -0.012987 | 0.034439 | 0.065477 | -0.0081267 | -0.008599 | 0.039235 | 0.078138 | 0.029977 | -66.9762 | 0.015142 | -66.9108 | 56.4304 | 56.2433 | 56.358 | -67.0436 | -66.9626 | 0.014095 | -67.0612 | 56.1985 | 56.4816 | 56.3612 | -67.1935 | -0.063585 | -0.085107 | 0.003792 | 0.069157 | 0.13274 | -0.27221 | -0.15746 | -0.21347 | -0.31696 | 0.017396 | -0.081211 | 0.13226 | -0.033892 | -0.15431 | 123.4104 | 123.2233 | 123.338 | 66.9951 | -123.5591 | 123.1785 | 123.4616 | 123.3412 | 66.9941 | -123.709
592.2656 | 123.7198 | -66.9479 | 56.4972 | 0.047088 | -0.024824 | -0.0090815 | 0.033159 | -0.010851 | 0.033371 | 0.065477 | -0.0081267 | -0.009667 | 0.040304 | 0.078138 | 0.032114 | -66.9808 | 0.015142 | -66.9108 | 56.435 | 56.2433 | 56.3672 | -67.0573 | -66.9672 | 0.004938 | -67.0658 | 56.2031 | 56.477 | 56.3612 | -67.1889 | -0.10937 | -0.062218 | -0.03283 | 0.037114 | 0.14648 | -0.2539 | -0.12999 | -0.24094 | -0.29407 | -0.019226 | -0.11783 | 0.1231 | -0.020159 | -0.136 | 123.3829 | 123.1912 | 123.3151 | 66.9631 | -123.5545 | 123.1511 | 123.425 | 123.3091 | 66.9529 | -123.6861
593.2656 | 123.6969 | -66.9571 | 56.4926 | 0.06235 | -0.023755 | -0.011218 | 0.031022 | -0.0087139 | 0.035507 | 0.065477 | -0.011332 | -0.007531 | 0.039235 | 0.077069 | 0.031046 | -66.9762 | 0.010564 | -66.9017 | 56.435 | 56.2479 | 56.358 | -67.0619 | -66.958 | 0.009516 | -67.0612 | 56.2077 | 56.4908 | 56.3566 | -67.1889 | -0.10479 | -0.057641 | -0.019096 | 0.055426 | 0.16021 | -0.24475 | -0.13457 | -0.23178 | -0.28491 | -0.000913 | -0.1041 | 0.12768 | -0.001846 | -0.136 | 123.3921 | 123.205 | 123.3151 | 66.9677 | -123.5545 | 123.1648 | 123.4479 | 123.3137 | 66.9666 | -123.6815
594.2656 | 123.6649 | -66.9434 | 56.5247 | 0.077612 | -0.023755 | -0.0090815 | 0.033159 | -0.011919 | 0.034439 | 0.065477 | -0.0091947 | -0.007531 | 0.039235 | 0.078138 | 0.029977 | -66.9762 | 0.015142 | -66.9017 | 56.4396 | 56.2433 | 56.3672 | -67.0481 | -66.958 | 0.014095 | -67.0658 | 56.1985 | 56.4953 | 56.3612 | -67.1889 | -0.10478 | -0.085105 | -0.032829 | 0.041693 | 0.14648 | -0.28137 | -0.15745 | -0.24552 | -0.32611 | -0.014646 | -0.12241 | 0.1231 | -0.029311 | -0.16347 | 123.3829 | 123.1866 | 123.3106 | 66.9585 | -123.5728 | 123.1419 | 123.4387 | 123.3045 | 66.9575 | -123.7135
595.2656 | 123.8709 | -66.9296 | 56.5338 | 0.077612 | -0.023755 | -0.0080125 | 0.033159 | -0.011919 | 0.035507 | 0.080738 | -0.0070587 | -0.010735 | 0.040304 | 0.080274 | 0.029977 | -66.9762 | 0.010564 | -66.9062 | 56.435 | 56.2341 | 56.3672 | -67.039 | -66.9672 | 0.009516 | -67.0658 | 56.2123 | 56.4953 | 56.3337 | -67.1889 | -0.10936 | -0.098839 | -0.046562 | 0.023381 | 0.13274 | -0.29968 | -0.16661 | -0.25925 | -0.32153 | -0.037537 | -0.13614 | 0.1231 | -0.038466 | -0.20009 | 123.3646 | 123.1638 | 123.2968 | 66.9402 | -123.5728 | 123.1419 | 123.425 | 123.2633 | 66.9391 | -123.7227
596.2656 | 123.761 | -66.98 | 56.4926 | 0.06235 | -0.024824 | -0.0090815 | 0.034227 | -0.0097819 | 0.033371 | 0.080738 | -0.010263 | -0.009667 | 0.039235 | 0.080274 | 0.032114 | -66.9808 | 0.015142 | -66.9062 | 56.4396 | 56.2479 | 56.3672 | -67.0436 | -66.9626 | 0.009516 | -67.0658 | 56.1985 | 56.4816 | 56.3566 | -67.1889 | -0.063585 | -0.053062 | -0.000787 | 0.073735 | 0.13732 | -0.24475 | -0.12541 | -0.20889 | -0.29407 | 0.017396 | -0.08579 | 0.1231 | -0.011004 | -0.136 | 123.4195 | 123.2278 | 123.3472 | 66.9951 | -123.5362 | 123.1785 | 123.4616 | 123.3366 | 66.9895 | -123.6815
597.2656 | 123.7106 | -66.9479 | 56.4972 | 0.047088 | -0.024824 | -0.01015 | 0.034227 | -0.010851 | 0.035507 | 0.080738 | -0.0081267 | -0.005394 | 0.039235 | 0.078138 | 0.032114 | -66.9762 | 0.015142 | -66.9108 | 56.4441 | 56.2387 | 56.3626 | -67.0527 | -66.9717 | 0.004938 | -67.052 | 56.1985 | 56.4816 | 56.3429 | -67.1889 | -0.10479 | -0.053061 | -0.028251 | 0.037114 | 0.1419 | -0.25848 | -0.13457 | -0.24094 | -0.29865 | -0.023804 | -0.1041 | 0.13684 | -0.015581 | -0.15432 | 123.3921 | 123.1866 | 123.3106 | 66.9631 | -123.5499 | 123.1465 | 123.4295 | 123.2908 | 66.9529 | -123.6861
598.2656 | 123.7518 | -66.9159 | 56.5155 | 0.047088 | -0.023755 | -0.0090815 | 0.033159 | -0.010851 | 0.034439 | 0.080738 | -0.010263 | -0.007531 | 0.039235 | 0.078138 | 0.031046 | -66.9853 | 0.015142 | -66.9017 | 56.4304 | 56.2433 | 56.3718 | -67.0619 | -66.9626 | 0.014095 | -67.0658 | 56.2031 | 56.4816 | 56.3703 | -67.1843 | -0.14599 | -0.085107 | -0.069451 | 0.014228 | 0.16021 | -0.27221 | -0.14372 | -0.2684 | -0.31238 | -0.04669 | -0.14988 | 0.11853 | -0.033892 | -0.14516 | 123.3463 | 123.1592 | 123.2877 | 66.931 | -123.5774 | 123.119 | 123.3975 | 123.2862 | 66.93 | -123.6998
599.2812 | 123.6099 | -66.98 | 56.5659 | 0.06235 | -0.022687 | -0.01015 | 0.033159 | -0.0097819 | 0.035507 | 0.095999 | -0.0091947 | -0.009667 | 0.039235 | 0.080274 | 0.029977 | -66.9762 | 0.015142 | -66.9108 | 56.4304 | 56.2479 | 56.3718 | -67.0481 | -66.958 | 0.009516 | -67.0612 | 56.2031 | 56.4908 | 56.3749 | -67.1889 | -0.068164 | -0.13546 | 0.003792 | 0.069157 | 0.13732 | -0.31799 | -0.19407 | -0.20889 | -0.36273 | 0.021975 | -0.081211 | 0.12768 | -0.075088 | -0.19093 | 123.4104 | 123.2278 | 123.3518 | 66.9951 | -123.614 | 123.1831 | 123.4707 | 123.3549 | 66.9895 | -123.7547
600.2656 | 123.7427 | -66.9113 | 56.5109 | 0.06235 | -0.023755 | -0.0090815 | 0.033159 | -0.011919 | 0.035507 | 0.050216 | -0.010263 | -0.009667 | 0.038167 | 0.080274 | 0.031046 | -66.9762 | 0.015142 | -66.9108 | 56.435 | 56.2479 | 56.3672 | -67.0481 | -66.9717 | 0.009516 | -67.0658 | 56.2031 | 56.4862 | 56.3154 | -67.1889 | -0.13683 | -0.075951 | -0.064872 | 0.000493 | 0.13732 | -0.26306 | -0.14372 | -0.27756 | -0.3078 | -0.060425 | -0.15445 | 0.1231 | -0.024735 | -0.19552 | 123.3463 | 123.1592 | 123.2785 | 66.9265 | -123.5591 | 123.1144 | 123.3975 | 123.2267 | 66.9208 | -123.6998
601.2656 | 123.7747 | -66.9571 | 56.4972 | 0.047088 | -0.024824 | -0.0090815 | 0.033159 | -0.010851 | 0.034439 | 0.080738 | -0.0091947 | -0.009667 | 0.038167 | 0.080274 | 0.031046 | -66.9762 | 0.010564 | -66.9017 | 56.435 | 56.2433 | 56.3626 | -67.0527 | -66.9717 | 0.004938 | -67.0612 | 56.2031 | 56.4816 | 56.3566 | -67.1935 | -0.095631 | -0.062218 | -0.019096 | 0.055426 | 0.15106 | -0.2539 | -0.13457 | -0.23636 | -0.29407 | -0.014649 | -0.1041 | 0.13226 | -0.015581 | -0.14058 | 123.3921 | 123.2004 | 123.3197 | 66.9677 | -123.5499 | 123.1602 | 123.4387 | 123.3137 | 66.962 | -123.6906
602.2656 | 123.7518 | -66.9296 | 56.4835 | 0.077612 | -0.022687 | -0.01015 | 0.034227 | -0.011919 | 0.033371 | 0.065477 | -0.0081267 | -0.009667 | 0.039235 | 0.081343 | 0.031046 | -66.9716 | 0.010564 | -66.8971 | 56.435 | 56.2433 | 56.3718 | -67.0344 | -66.9672 | 0.000359 | -67.0703 | 56.2077 | 56.4953 | 56.3566 | -67.1935 | -0.10478 | -0.048485 | -0.041984 | 0.032538 | 0.13732 | -0.24017 | -0.11168 | -0.26383 | -0.27576 | -0.037537 | -0.14072 | 0.12311 | 0.011888 | -0.12685 | 123.3646 | 123.1729 | 123.3014 | 66.9402 | -123.5179 | 123.1373 | 123.425 | 123.2862 | 66.93 | -123.6769
603.2656 | 123.7289 | -66.9662 | 56.4835 | 0.047088 | -0.024824 | -0.01015 | 0.032091 | -0.0097819 | 0.034439 | 0.080738 | -0.0081267 | -0.008599 | 0.038167 | 0.080274 | 0.031046 | -66.9808 | 0.005985 | -66.9017 | 56.4396 | 56.2296 | 56.3626 | -67.0436 | -66.958 | 0.004938 | -67.0658 | 56.2031 | 56.4908 | 56.3337 | -67.1935 | -0.077317 | -0.043906 | -0.014519 | 0.064582 | 0.1419 | -0.25391 | -0.12083 | -0.22721 | -0.28034 | 0.008243 | -0.099522 | 0.12768 | 0.00731 | -0.14974 | 123.4058 | 123.1958 | 123.3289 | 66.9722 | -123.527 | 123.1694 | 123.457 | 123.3 | 66.9712 | -123.6769
604.2812 | 123.7244 | -66.9479 | 56.5063 | 0.047088 | -0.023755 | -0.0090815 | 0.035296 | -0.010851 | 0.035507 | 0.080738 | -0.0070587 | -0.009667 | 0.039235 | 0.080274 | 0.029977 | -66.9808 | 0.001407 | -66.9017 | 56.4396 | 56.2433 | 56.3672 | -67.0619 | -66.9672 | 0.004938 | -67.0566 | 56.2031 | 56.4908 | 56.2834 | -67.1935 | -0.11394 | -0.066795 | -0.03283 | 0.046271 | 0.16021 | -0.26306 | -0.13914 | -0.24552 | -0.30322 | -0.019226 | -0.10868 | 0.13684 | -0.015579 | -0.22299 | 123.3875 | 123.1912 | 123.3151 | 66.9493 | -123.5682 | 123.1511 | 123.4387 | 123.2313 | 66.9529 | -123.6998
605.2656 | 123.7427 | -66.9434 | 56.4651 | 0.047088 | -0.022687 | -0.012287 | 0.034227 | -0.011919 | 0.033371 | 0.050216 | -0.0091947 | -0.008599 | 0.039235 | 0.079206 | 0.029977 | -66.9808 | 0.001407 | -66.9017 | 56.4441 | 56.2296 | 56.3626 | -67.0527 | -66.9626 | 0.009516 | -67.0612 | 56.2031 | 56.4953 | 56.3383 | -67.1843 | -0.10936 | -0.021018 | -0.037408 | 0.041693 | 0.15106 | -0.2356 | -0.10252 | -0.24094 | -0.26202 | -0.019225 | -0.11783 | 0.12311 | 0.030198 | -0.12685 | 123.3875 | 123.1729 | 123.306 | 66.9448 | -123.5179 | 123.1465 | 123.4387 | 123.2817 | 66.9529 | -123.6494
606.2656 | 123.7106 | -66.9708 | 56.4972 | 0.06235 | -0.022687 | -0.01015 | 0.034227 | -0.010851 | 0.033371 | 0.065477 | -0.0081267 | -0.009667 | 0.038167 | 0.079206 | 0.029977 | -66.9762 | 0.005985 | -66.9017 | 56.4304 | 56.2433 | 56.3672 | -67.0481 | -66.9626 | 0.009516 | -67.0658 | 56.2031 | 56.4908 | 56.3475 | -67.1935 | -0.077319 | -0.066796 | -0.005363 | 0.069159 | 0.14648 | -0.2539 | -0.12999 | -0.22263 | -0.29407 | 0.008241 | -0.094945 | 0.12768 | -0.006423 | -0.14974 | 123.4012 | 123.2141 | 123.338 | 66.9768 | -123.5453 | 123.1739 | 123.4616 | 123.3183 | 66.9803 | -123.6906
607.2656 | 123.7244 | -66.9525 | 56.4743 | 0.047088 | -0.024824 | -0.011218 | 0.033159 | -0.010851 | 0.034439 | 0.065477 | -0.0091947 | -0.010735 | 0.038167 | 0.081343 | 0.029977 | -66.9853 | 0.005985 | -66.9017 | 56.4304 | 56.2433 | 56.3626 | -67.0344 | -66.9626 | 0.014095 | -67.0612 | 56.2077 | 56.4953 | 56.32 | -67.1843 | -0.081893 | -0.043908 | -0.03283 | 0.050849 | 0.13274 | -0.23101 | -0.11168 | -0.23178 | -0.2666 | -0.010069 | -0.10868 | 0.12311 | 0.021043 | -0.15432 | 123.3829 | 123.1958 | 123.3151 | 66.9585 | -123.5087 | 123.1602 | 123.4479 | 123.2725 | 66.9666 | -123.6586
608.2656 | 123.7335 | -66.9525 | 56.4743 | 0.047088 | -0.024824 | -0.0090815 | 0.033159 | -0.010851 | 0.032302 | 0.095999 | -0.010263 | -0.010735 | 0.037099 | 0.080274 | 0.029977 | -66.9762 | 0.010564 | -66.9062 | 56.4304 | 56.2433 | 56.3672 | -67.0481 | -66.9626 | 0.009516 | -67.0658 | 56.2031 | 56.4953 | 56.3749 | -67.1935 | -0.095629 | -0.043908 | -0.023673 | 0.04627 | 0.1419 | -0.23101 | -0.1071 | -0.24094 | -0.27118 | -0.010069 | -0.11325 | 0.12768 | 0.021043 | -0.099378 | 123.3829 | 123.1958 | 123.3197 | 66.9631 | -123.5224 | 123.1556 | 123.4479 | 123.3274 | 66.962 | -123.6678
609.2812 | 123.6008 | -66.9846 | 56.5384 | 0.047088 | -0.024824 | -0.01015 | 0.032091 | -0.011919 | 0.033371 | 0.065477 | -0.0091947 | -0.010735 | 0.038167 | 0.081343 | 0.031046 | -66.9762 | 0.001407 | -66.9062 | 56.435 | 56.2433 | 56.3672 | -67.0481 | -66.9626 | 0.014095 | -67.0612 | 56.2077 | 56.4816 | 56.3566 | -67.1935 | -0.063586 | -0.10342 | 0.00837 | 0.078313 | 0.1419 | -0.2951 | -0.17119 | -0.2089 | -0.33069 | 0.021974 | -0.076633 | 0.13226 | -0.05678 | -0.18178 | 123.4195 | 123.2278 | 123.3518 | 66.986 | -123.5865 | 123.1923 | 123.4662 | 123.3412 | 66.9987 | -123.7318
610.2656 | 123.6969 | -66.9708 | 56.4697 | 0.06235 | -0.024824 | -0.0090815 | 0.033159 | -0.011919 | 0.035507 | 0.050216 | -0.0091947 | -0.008599 | 0.038167 | 0.080274 | 0.029977 | -66.9808 | 0.001407 | -66.9062 | 56.435 | 56.2433 | 56.358 | -67.0481 | -66.9626 | 0.004938 | -67.0658 | 56.1985 | 56.4908 | 56.3612 | -67.1797 | -0.077319 | -0.034753 | -0.009942 | 0.06458 | 0.1419 | -0.22644 | -0.11168 | -0.20889 | -0.27118 | 0.008241 | -0.094945 | 0.11395 | 0.021042 | -0.10854 | 123.4058 | 123.2141 | 123.3289 | 66.9722 | -123.5179 | 123.1694 | 123.4616 | 123.332 | 66.9758 | -123.6494
611.2656 | 123.6877 | -66.9617 | 56.4972 | 0.077612 | -0.025892 | -0.0090815 | 0.033159 | -0.011919 | 0.032302 | 0.050216 | -0.010263 | -0.008599 | 0.038167 | 0.082411 | 0.029977 | -66.9716 | -0.003172 | -66.9017 | 56.4258 | 56.2433 | 56.3672 | -67.0436 | -66.9626 | 0.004938 | -67.0612 | 56.2031 | 56.4908 | 56.3658 | -67.1889 | -0.081895 | -0.071375 | -0.00994 | 0.060004 | 0.1419 | -0.2539 | -0.12999 | -0.2272 | -0.29407 | -0.000914 | -0.099521 | 0.12768 | -0.006423 | -0.13142 | 123.3875 | 123.205 | 123.3289 | 66.9585 | -123.5408 | 123.1648 | 123.4524 | 123.3274 | 66.9666 | -123.6861
612.2656 | 123.6969 | -66.9754 | 56.4743 | 0.047088 | -0.024824 | -0.0090815 | 0.031022 | -0.011919 | 0.034439 | 0.065477 | -0.0081267 | -0.010735 | 0.037099 | 0.082411 | 0.028909 | -66.9762 | 0.005985 | -66.9108 | 56.4396 | 56.2387 | 56.3626 | -67.039 | -66.9626 | 0.000359 | -67.0703 | 56.1985 | 56.4862 | 56.3703 | -67.1889 | -0.063584 | -0.034751 | -0.000785 | 0.06458 | 0.12816 | -0.23559 | -0.11168 | -0.21347 | -0.27576 | 0.012819 | -0.094946 | 0.11853 | 0.011886 | -0.10396 | 123.415 | 123.2141 | 123.338 | 66.9814 | -123.5133 | 123.1739 | 123.4616 | 123.3458 | 66.9758 | -123.6632
613.2656 | 123.6786 | -66.9479 | 56.5155 | 0.077612 | -0.024824 | -0.0090815 | 0.033159 | -0.010851 | 0.033371 | 0.065477 | -0.010263 | -0.009667 | 0.038167 | 0.082411 | 0.028909 | -66.9716 | -0.003172 | -66.9062 | 56.4396 | 56.2524 | 56.3718 | -67.0481 | -66.9717 | 0.009516 | -67.0703 | 56.2031 | 56.4862 | 56.3749 | -67.1935 | -0.10021 | -0.07595 | -0.023673 | 0.041692 | 0.1419 | -0.26306 | -0.14372 | -0.24552 | -0.31238 | -0.023804 | -0.12241 | 0.12311 | -0.029313 | -0.14058 | 123.3875 | 123.2004 | 123.3197 | 66.9448 | -123.5636 | 123.1511 | 123.4341 | 123.3229 | 66.9575 | -123.709
614.2812 | 123.6969 | -66.9434 | 56.5292 | 0.06235 | -0.025892 | -0.01015 | 0.033159 | -0.0097819 | 0.033371 | 0.080738 | -0.0091947 | -0.009667 | 0.037099 | 0.081343 | 0.029977 | -66.9762 | 0.001407 | -66.9062 | 56.4258 | 56.2524 | 56.3672 | -67.039 | -66.9672 | 0.004938 | -67.0566 | 56.2077 | 56.4862 | 56.3703 | -67.1889 | -0.095628 | -0.10342 | -0.032829 | 0.037114 | 0.13274 | -0.27679 | -0.16203 | -0.24552 | -0.32153 | -0.023804 | -0.11325 | 0.13226 | -0.043046 | -0.15889 | 123.3692 | 123.1958 | 123.3106 | 66.9448 | -123.5682 | 123.1511 | 123.4295 | 123.3137 | 66.9483 | -123.7181
615.2656 | 123.7244 | -66.9662 | 56.4835 | 0.047088 | -0.024824 | -0.01015 | 0.032091 | -0.010851 | 0.034439 | 0.065477 | -0.010263 | -0.010735 | 0.037099 | 0.082411 | 0.029977 | -66.9808 | 0.001407 | -66.8925 | 56.4396 | 56.2479 | 56.3626 | -67.071 | -66.958 | 0.004938 | -67.0612 | 56.1985 | 56.477 | 56.3703 | -67.1889 | -0.10479 | -0.043906 | -0.014519 | 0.073738 | 0.17853 | -0.23559 | -0.12083 | -0.22263 | -0.28491 | 0.008243 | -0.094943 | 0.12768 | -0.006426 | -0.11311 | 123.4058 | 123.2141 | 123.3289 | 66.9677 | -123.5545 | 123.1648 | 123.4433 | 123.3366 | 66.9712 | -123.6723
616.2656 | 123.7198 | -66.9662 | 56.4926 | 0.06235 | -0.025892 | -0.0090815 | 0.033159 | -0.012987 | 0.032302 | 0.065477 | -0.0091947 | -0.009667 | 0.040304 | 0.082411 | 0.028909 | -66.9762 | -0.003172 | -66.9062 | 56.435 | 56.2341 | 56.3718 | -67.039 | -66.9626 | 0.000359 | -67.0612 | 56.2031 | 56.4908 | 56.3658 | -67.2026 | -0.072739 | -0.057641 | -0.00994 | 0.060003 | 0.13274 | -0.25848 | -0.12083 | -0.23636 | -0.28949 | 0.003664 | -0.094943 | 0.14142 | -0.001846 | -0.12685 | 123.4012 | 123.2004 | 123.338 | 66.9631 | -123.5316 | 123.1694 | 123.457 | 123.332 | 66.9666 | -123.6952
617.2656 | 123.6969 | -66.9525 | 56.4697 | 0.031826 | -0.028029 | -0.01015 | 0.032091 | -0.012987 | 0.033371 | 0.080738 | -0.011332 | -0.009667 | 0.038167 | 0.082411 | 0.028909 | -66.9762 | 0.001407 | -66.9017 | 56.435 | 56.2433 | 56.3718 | -67.0436 | -66.9672 | 0.000359 | -67.0612 | 56.2077 | 56.4908 | 56.3841 | -67.1935 | -0.09105 | -0.034753 | -0.023673 | 0.050849 | 0.1419 | -0.22644 | -0.097943 | -0.24094 | -0.26203 | -0.014648 | -0.10868 | 0.13226 | 0.021042 | -0.085644 | 123.3875 | 123.1958 | 123.3243 | 66.9539 | -123.5133 | 123.1602 | 123.4433 | 123.3366 | 66.9529 | -123.6632
618.2656 | 123.6832 | -66.9434 | 56.4789 | 0.06235 | -0.025892 | -0.0090815 | 0.032091 | -0.011919 | 0.033371 | 0.050216 | -0.010263 | -0.011804 | 0.038167 | 0.083479 | 0.029977 | -66.9808 | 0.001407 | -66.9017 | 56.435 | 56.2433 | 56.3672 | -67.0527 | -66.9626 | 0.000359 | -67.0612 | 56.1985 | 56.4862 | 56.3658 | -67.1889 | -0.10936 | -0.043908 | -0.037408 | 0.041693 | 0.15106 | -0.23559 | -0.11168 | -0.24552 | -0.28034 | -0.019225 | -0.11783 | 0.12768 | 0.007308 | -0.11311 | 123.3783 | 123.1866 | 123.3106 | 66.9448 | -123.5316 | 123.1419 | 123.4295 | 123.3091 | 66.9437 | -123.6678
619.2656 | 123.7335 | -66.9388 | 56.5018 | 0.047088 | -0.025892 | -0.0080125 | 0.031022 | -0.010851 | 0.034439 | 0.065477 | -0.010263 | -0.010735 | 0.038167 | 0.082411 | 0.031046 | -66.9808 | -0.012329 | -66.9062 | 56.4304 | 56.2524 | 56.3718 | -67.0481 | -66.9672 | -0.00422 | -67.0658 | 56.2077 | 56.4908 | 56.3658 | -67.1889 | -0.10936 | -0.071374 | -0.041985 | 0.032537 | 0.1419 | -0.24932 | -0.12999 | -0.25009 | -0.29407 | -0.028381 | -0.12699 | 0.1231 | -0.011001 | -0.136 | 123.3692 | 123.1912 | 123.3106 | 66.9265 | -123.5499 | 123.1465 | 123.4296 | 123.3046 | 66.9346 | -123.6906
620.2656 | 123.6374 | -66.9571 | 56.4972 | 0.031826 | -0.02696 | -0.01015 | 0.034227 | -0.010851 | 0.032302 | 0.065477 | -0.010263 | -0.008599 | 0.038167 | 0.083479 | 0.031046 | -66.9716 | -0.012329 | -66.9062 | 56.435 | 56.2433 | 56.3672 | -67.0436 | -66.958 | 0.004938 | -67.0612 | 56.2077 | 56.4953 | 56.3658 | -67.1935 | -0.086473 | -0.062218 | -0.014518 | 0.050847 | 0.13732 | -0.2539 | -0.12999 | -0.23636 | -0.28949 | -0.000913 | -0.1041 | 0.13226 | -0.001845 | -0.13142 | 123.3921 | 123.2004 | 123.3243 | 66.9448 | -123.5408 | 123.1648 | 123.4524 | 123.3229 | 66.962 | -123.6906
621.2656 | 123.6923 | -66.9708 | 56.4789 | 0.06235 | -0.025892 | -0.0090815 | 0.032091 | -0.011919 | 0.033371 | 0.050216 | -0.010263 | -0.009667 | 0.038167 | 0.081343 | 0.029977 | -66.9808 | -0.012329 | -66.9062 | 56.4304 | 56.2433 | 56.3764 | -67.039 | -66.958 | 0.000359 | -67.052 | 56.2077 | 56.4862 | 56.3658 | -67.1935 | -0.068162 | -0.048486 | -0.009942 | 0.06458 | 0.13274 | -0.23559 | -0.10252 | -0.22263 | -0.27118 | 0.01282 | -0.081209 | 0.14142 | 0.007308 | -0.11311 | 123.4012 | 123.2141 | 123.3472 | 66.9585 | -123.5179 | 123.1785 | 123.457 | 123.3366 | 66.9712 | -123.6723
622.2656 | 123.7381 | -66.9754 | 56.4789 | 0.047088 | -0.025892 | -0.011218 | 0.033159 | -0.011919 | 0.032302 | 0.080738 | -0.010263 | -0.010735 | 0.037099 | 0.082411 | 0.032114 | -66.9762 | -0.003172 | -66.9017 | 56.4441 | 56.2479 | 56.3672 | -67.0436 | -66.9672 | 0.000359 | -67.0612 | 56.2077 | 56.4908 | 56.3703 | -67.1889 | -0.068162 | -0.034751 | -0.000785 | 0.073737 | 0.1419 | -0.23101 | -0.11168 | -0.21347 | -0.27118 | 0.00824 | -0.085788 | 0.12768 | 0.011887 | -0.10853 | 123.4195 | 123.2233 | 123.3426 | 66.9722 | -123.5224 | 123.1831 | 123.4662 | 123.3458 | 66.9758 | -123.6678
623.2656 | 123.7061 | -66.9708 | 56.4835 | 0.06235 | -0.02696 | -0.0090815 | 0.031022 | -0.012987 | 0.033371 | 0.065477 | -0.010263 | -0.011804 | 0.038167 | 0.082411 | 0.029977 | -66.9762 | -0.012329 | -66.8971 | 56.4304 | 56.2479 | 56.3672 | -67.039 | -66.9672 | -0.00422 | -67.0566 | 56.2031 | 56.4816 | 56.3703 | -67.1935 | -0.068162 | -0.053063 | -0.005363 | 0.073737 | 0.1419 | -0.23559 | -0.11625 | -0.22263 | -0.28034 | 0.003662 | -0.085787 | 0.13684 | -0.001848 | -0.11311 | 123.4012 | 123.2187 | 123.338 | 66.9585 | -123.5224 | 123.1739 | 123.4524 | 123.3412 | 66.9666 | -123.6769
624.3281 | 123.7198 | -66.9617 | 56.4697 | 0.047088 | -0.028029 | -0.0090815 | 0.031022 | -0.014056 | 0.031234 | 0.080738 | -0.010263 | -0.010735 | 0.040304 | 0.082411 | 0.029977 | -66.9808 | -0.003172 | -66.9062 | 56.4396 | 56.2479 | 56.3764 | -67.039 | -66.9626 | 0.000359 | -67.0658 | 56.2077 | 56.4908 | 56.3703 | -67.198 | -0.077317 | -0.030174 | -0.019097 | 0.055425 | 0.13274 | -0.22186 | -0.093365 | -0.23636 | -0.26203 | -0.000914 | -0.1041 | 0.13226 | 0.021042 | -0.099379 | 123.4012 | 123.2095 | 123.338 | 66.9585 | -123.5087 | 123.1694 | 123.4524 | 123.332 | 66.962 | -123.6678
625.2656 | 123.674 | -66.9525 | 56.4789 | 0.047088 | -0.024824 | -0.01015 | 0.032091 | -0.010851 | 0.032302 | 0.065477 | -0.010263 | -0.010735 | 0.036031 | 0.082411 | 0.031046 | -66.9762 | -0.003172 | -66.9017 | 56.4396 | 56.2387 | 56.3718 | -67.0436 | -66.9626 | -0.00422 | -67.0566 | 56.2031 | 56.4908 | 56.3658 | -67.1843 | -0.09105 | -0.039329 | -0.023673 | 0.050849 | 0.1419 | -0.24017 | -0.1071 | -0.23178 | -0.27576 | -0.010069 | -0.1041 | 0.12768 | 0.011887 | -0.11311 | 123.3921 | 123.1912 | 123.3243 | 66.9493 | -123.5224 | 123.1556 | 123.4433 | 123.3183 | 66.9483 | -123.6632
626.2656 | 123.7015 | -66.9617 | 56.4789 | 0.06235 | -0.023755 | -0.01015 | 0.032091 | -0.0097819 | 0.031234 | 0.050216 | -0.0091947 | -0.010735 | 0.038167 | 0.082411 | 0.029977 | -66.9762 | -0.003172 | -66.9062 | 56.435 | 56.2433 | 56.3718 | -67.0527 | -66.9626 | -0.00422 | -67.0566 | 56.2077 | 56.4862 | 56.3749 | -67.1889 | -0.091053 | -0.043908 | -0.014518 | 0.055425 | 0.14648 | -0.23559 | -0.1071 | -0.2272 | -0.27118 | -0.000914 | -0.094942 | 0.13226 | 0.007308 | -0.10396 | 123.3966 | 123.205 | 123.3335 | 66.9585 | -123.5316 | 123.1694 | 123.4479 | 123.3366 | 66.9574 | -123.6678
627.2656 | 123.6877 | -66.98 | 56.4697 | 0.047088 | -0.02696 | -0.0090815 | 0.031022 | -0.010851 | 0.032302 | 0.080738 | -0.010263 | -0.008599 | 0.037099 | 0.082411 | 0.028909 | -66.9808 | -0.007751 | -66.9062 | 56.435 | 56.2433 | 56.3672 | -67.0481 | -66.9626 | -0.00422 | -67.0612 | 56.2031 | 56.4862 | 56.3612 | -67.1843 | -0.068164 | -0.034753 | -0.000787 | 0.073735 | 0.1419 | -0.22644 | -0.10252 | -0.20432 | -0.2666 | 0.017396 | -0.081211 | 0.12311 | 0.016463 | -0.10854 | 123.415 | 123.2233 | 123.3472 | 66.9722 | -123.5179 | 123.1831 | 123.4662 | 123.3412 | 66.9758 | -123.654
628.2656 | 123.6923 | -66.9434 | 56.456 | 0.047088 | -0.025892 | -0.01015 | 0.029954 | -0.014056 | 0.032302 | 0.050216 | -0.0081267 | -0.009667 | 0.039235 | 0.083479 | 0.028909 | -66.9716 | -0.007751 | -66.9017 | 56.4304 | 56.2341 | 56.3809 | -67.0436 | -66.9626 | -0.00422 | -67.0612 | 56.2123 | 56.4908 | 56.3612 | -67.1889 | -0.10021 | -0.025598 | -0.028251 | 0.041693 | 0.1419 | -0.22186 | -0.075053 | -0.24552 | -0.24371 | -0.019225 | -0.11783 | 0.12768 | 0.034775 | -0.094804 | 123.3738 | 123.1775 | 123.3243 | 66.9356 | -123.4996 | 123.1556 | 123.4341 | 123.3045 | 66.9391 | -123.6449
629.2812 | 123.761 | -66.9067 | 56.488 | 0.047088 | -0.025892 | -0.01015 | 0.031022 | -0.011919 | 0.034439 | 0.095999 | -0.0081267 | -0.009667 | 0.037099 | 0.082411 | 0.029977 | -66.9808 | -0.007751 | -66.9017 | 56.435 | 56.2479 | 56.3764 | -67.039 | -66.9717 | -0.008798 | -67.0612 | 56.2031 | 56.4816 | 56.3703 | -67.1935 | -0.13225 | -0.053063 | -0.074029 | 0.005072 | 0.13732 | -0.24017 | -0.11167 | -0.28672 | -0.28491 | -0.065003 | -0.15445 | 0.13226 | -0.006426 | -0.11769 | 123.3417 | 123.1546 | 123.2831 | 66.899 | -123.527 | 123.1099 | 123.3883 | 123.2771 | 66.8979 | -123.6815
630.2656 | 123.7381 | -66.9388 | 56.4423 | 0.031826 | -0.02696 | -0.01015 | 0.032091 | -0.011919 | 0.033371 | 0.065477 | -0.010263 | -0.010735 | 0.038167 | 0.082411 | 0.028909 | -66.9808 | -0.007751 | -66.9062 | 56.4396 | 56.2524 | 56.3672 | -67.0573 | -66.958 | 0.000359 | -67.0612 | 56.1985 | 56.4862 | 56.3749 | -67.1843 | -0.11852 | -0.002708 | -0.041985 | 0.032537 | 0.15106 | -0.18981 | -0.075056 | -0.24551 | -0.24372 | -0.019223 | -0.12241 | 0.12311 | 0.043929 | -0.067335 | 123.3783 | 123.1912 | 123.306 | 66.931 | -123.4996 | 123.1373 | 123.425 | 123.3137 | 66.9391 | -123.6266
631.2656 | 123.7152 | -66.9662 | 56.456 | 0.06235 | -0.02696 | -0.011218 | 0.033159 | -0.010851 | 0.033371 | 0.065477 | -0.010263 | -0.008599 | 0.038167 | 0.082411 | 0.028909 | -66.9716 | -0.007751 | -66.8925 | 56.4396 | 56.2433 | 56.3718 | -67.039 | -66.9672 | -0.00422 | -67.0566 | 56.2031 | 56.4953 | 56.3703 | -67.198 | -0.072739 | -0.016441 | -0.005362 | 0.073738 | 0.14648 | -0.2127 | -0.08421 | -0.23179 | -0.25287 | -0.000915 | -0.090364 | 0.14142 | 0.039353 | -0.085646 | 123.4058 | 123.2095 | 123.338 | 66.9585 | -123.495 | 123.1694 | 123.4616 | 123.3366 | 66.962 | -123.654
632.2656 | 123.7244 | -66.9662 | 56.4697 | 0.06235 | -0.024824 | -0.011218 | 0.031022 | -0.011919 | 0.031234 | 0.065477 | -0.0091947 | -0.009667 | 0.037099 | 0.084548 | 0.028909 | -66.9808 | -0.003172 | -66.9062 | 56.435 | 56.2387 | 56.3626 | -67.0481 | -66.958 | -0.013377 | -67.0566 | 56.2031 | 56.4908 | 56.3703 | -67.1935 | -0.081896 | -0.034753 | -0.014519 | 0.060003 | 0.1419 | -0.23102 | -0.1071 | -0.22721 | -0.2666 | 0.008243 | -0.090364 | 0.13684 | 0.021042 | -0.099379 | 123.4012 | 123.205 | 123.3289 | 66.9631 | -123.5179 | 123.1694 | 123.457 | 123.3366 | 66.9529 | -123.6632
633.2656 | 123.7106 | -66.9571 | 56.4743 | 0.06235 | -0.02696 | -0.011218 | 0.033159 | -0.011919 | 0.032302 | 0.050216 | -0.0124 | -0.009667 | 0.037099 | 0.085616 | 0.031046 | -66.9808 | -0.012329 | -66.9062 | 56.4396 | 56.2387 | 56.3672 | -67.039 | -66.958 | -0.00422 | -67.0475 | 56.2077 | 56.4908 | 56.3749 | -67.1935 | -0.081895 | -0.034751 | -0.023675 | 0.050847 | 0.13274 | -0.23559 | -0.1071 | -0.23636 | -0.2666 | -0.000913 | -0.090363 | 0.146 | 0.016465 | -0.099378 | 123.3966 | 123.1958 | 123.3243 | 66.9448 | -123.5133 | 123.1648 | 123.4479 | 123.332 | 66.9529 | -123.6678
634.2812 | 123.7244 | -66.9296 | 56.4743 | 0.077612 | -0.024824 | -0.012287 | 0.032091 | -0.011919 | 0.031234 | 0.050216 | -0.011332 | -0.008599 | 0.037099 | 0.084548 | 0.028909 | -66.9762 | -0.016908 | -66.8971 | 56.435 | 56.2524 | 56.3672 | -67.039 | -66.9626 | -0.00422 | -67.0566 | 56.2123 | 56.4862 | 56.3612 | -67.1889 | -0.10936 | -0.03933 | -0.046562 | 0.032538 | 0.1419 | -0.22186 | -0.1071 | -0.25925 | -0.26202 | -0.032958 | -0.12699 | 0.13226 | 0.011886 | -0.11311 | 123.3646 | 123.1821 | 123.2968 | 66.9127 | -123.5133 | 123.1419 | 123.4158 | 123.2908 | 66.9254 | -123.6632
635.2656 | 123.7244 | -66.9708 | 56.4606 | 0.047088 | -0.025892 | -0.01015 | 0.028885 | -0.0097819 | 0.031234 | 0.065477 | -0.011332 | -0.009667 | 0.038167 | 0.084548 | 0.029977 | -66.9762 | -0.007751 | -66.9017 | 56.4396 | 56.2479 | 56.3764 | -67.039 | -66.958 | -0.017956 | -67.052 | 56.2031 | 56.4862 | 56.3749 | -67.1935 | -0.068162 | -0.021018 | -0.005363 | 0.069159 | 0.13732 | -0.2127 | -0.084209 | -0.22263 | -0.25745 | 0.01282 | -0.081209 | 0.14142 | 0.025619 | -0.085645 | 123.4104 | 123.2187 | 123.3472 | 66.9631 | -123.4996 | 123.1739 | 123.457 | 123.3458 | 66.9529 | -123.654
636.2656 | 123.6374 | -66.9937 | 56.4743 | 0.06235 | -0.028029 | -0.011218 | 0.032091 | -0.0097819 | 0.033371 | 0.065477 | -0.011332 | -0.011804 | 0.036031 | 0.083479 | 0.027841 | -66.9716 | -0.021486 | -66.9017 | 56.4441 | 56.2433 | 56.3764 | -67.039 | -66.9626 | -0.008798 | -67.0566 | 56.2031 | 56.4908 | 56.3749 | -67.1935 | -0.045274 | -0.030173 | 0.022103 | 0.092047 | 0.13732 | -0.23101 | -0.097942 | -0.19974 | -0.27118 | 0.031129 | -0.062899 | 0.13684 | 0.016465 | -0.099378 | 123.4378 | 123.237 | 123.3701 | 66.9722 | -123.5133 | 123.1968 | 123.4845 | 123.3686 | 66.9849 | -123.6678
637.3438 | 123.6328 | -66.9617 | 56.5292 | 0.031826 | -0.029097 | -0.01015 | 0.031022 | -0.010851 | 0.031234 | 0.080738 | -0.010263 | -0.009667 | 0.039235 | 0.084548 | 0.028909 | -66.9716 | -0.021486 | -66.9062 | 56.4441 | 56.2524 | 56.3764 | -67.0665 | -66.958 | -0.008798 | -67.0475 | 56.2031 | 56.4862 | 56.3612 | -67.1889 | -0.10479 | -0.085105 | -0.00994 | 0.055425 | 0.16022 | -0.27679 | -0.15287 | -0.2272 | -0.32611 | 0.003665 | -0.085785 | 0.14142 | -0.043046 | -0.16805 | 123.4058 | 123.2141 | 123.338 | 66.9402 | -123.5957 | 123.1648 | 123.4479 | 123.3229 | 66.9529 | -123.7181
638.7188 | 123.6511 | -66.9617 | 56.5338 | 0.06235 | -0.029097 | -0.01015 | 0.029954 | -0.010851 | 0.031234 | 0.080738 | -0.0124 | -0.011804 | 0.037099 | 0.085616 | 0.028909 | -66.9716 | -0.021486 | -66.9017 | 56.435 | 56.2524 | 56.3672 | -67.0527 | -66.9672 | -0.013377 | -67.0612 | 56.2123 | 56.4953 | 56.3703 | -67.198 | -0.091053 | -0.098839 | -0.00994 | 0.060004 | 0.15106 | -0.28137 | -0.16661 | -0.23636 | -0.32153 | -0.005493 | -0.099521 | 0.13684 | -0.038466 | -0.16347 | 123.3966 | 123.2141 | 123.3289 | 66.9402 | -123.5865 | 123.174 | 123.457 | 123.332 | 66.9483 | -123.7318
639.7031 | 123.6694 | -67.0212 | 56.5201 | 0.06235 | -0.028029 | -0.011218 | 0.031022 | -0.012987 | 0.032302 | 0.065477 | -0.010263 | -0.010735 | 0.037099 | 0.084548 | 0.028909 | -66.9716 | -0.021486 | -66.9062 | 56.4396 | 56.2524 | 56.3626 | -67.0527 | -66.9672 | -0.008798 | -67.0566 | 56.2031 | 56.4862 | 56.3703 | -67.1935 | -0.031544 | -0.080528 | 0.049569 | 0.11493 | 0.14648 | -0.26763 | -0.15745 | -0.17227 | -0.31696 | 0.054016 | -0.035433 | 0.13684 | -0.033891 | -0.14973 | 123.4607 | 123.2736 | 123.3838 | 66.9997 | -123.5728 | 123.2243 | 123.5074 | 123.3915 | 67.0124 | -123.7135
640.8906 | 123.6877 | -66.9525 | 56.4743 | 0.06235 | -0.029097 | -0.01015 | 0.031022 | -0.011919 | 0.031234 | 0.065477 | -0.0081267 | -0.009667 | 0.037099 | 0.084548 | 0.029977 | -66.9762 | -0.021486 | -66.8971 | 56.4396 | 56.2479 | 56.3672 | -67.0481 | -66.9672 | -0.008798 | -67.0566 | 56.2077 | 56.4908 | 56.3658 | -67.198 | -0.095629 | -0.034751 | -0.023673 | 0.055427 | 0.15106 | -0.22644 | -0.1071 | -0.24552 | -0.2666 | -0.014648 | -0.1041 | 0.14142 | 0.016465 | -0.10853 | 123.3921 | 123.2004 | 123.3197 | 66.931 | -123.5224 | 123.1602 | 123.4433 | 123.3183 | 66.9437 | -123.6723
642.5781 | 123.6191 | -66.98 | 56.5659 | 0.06235 | -0.028029 | -0.0090815 | 0.031022 | -0.014056 | 0.033371 | 0.065477 | -0.011332 | -0.010735 | 0.038167 | 0.085616 | 0.027841 | -66.9716 | -0.012329 | -66.9017 | 56.435 | 56.2524 | 56.3672 | -67.0481 | -66.9672 | -0.013377 | -67.0612 | 56.2031 | 56.4999 | 56.3658 | -67.1889 | -0.068164 | -0.13088 | 0.00837 | 0.078314 | 0.14648 | -0.31341 | -0.19865 | -0.20889 | -0.36273 | 0.012817 | -0.081211 | 0.12768 | -0.065931 | -0.20009 | 123.415 | 123.2324 | 123.3472 | 66.9677 | -123.614 | 123.1831 | 123.4799 | 123.3457 | 66.9666 | -123.7547
643.7344 | 123.6603 | -66.9434 | 56.5247 | 0.092874 | -0.02696 | -0.01015 | 0.029954 | -0.011919 | 0.032302 | 0.050216 | -0.010263 | -0.010735 | 0.038167 | 0.083479 | 0.029977 | -66.9716 | -0.016908 | -66.9017 | 56.4396 | 56.2479 | 56.3764 | -67.0436 | -66.9626 | -0.013377 | -67.0612 | 56.2077 | 56.4908 | 56.3703 | -67.1889 | -0.10021 | -0.085105 | -0.028251 | 0.041693 | 0.1419 | -0.27679 | -0.1483 | -0.24552 | -0.31696 | -0.019225 | -0.11783 | 0.12768 | -0.033889 | -0.15431 | 123.3829 | 123.1912 | 123.3197 | 66.9265 | -123.5682 | 123.1511 | 123.4341 | 123.3137 | 66.93 | -123.7135
644.4688 | 123.7289 | -66.9479 | 56.4743 | 0.031826 | -0.028029 | -0.011218 | 0.031022 | -0.011919 | 0.030166 | 0.065477 | -0.011332 | -0.007531 | 0.037099 | 0.085616 | 0.029977 | -66.9716 | -0.021486 | -66.9017 | 56.4396 | 56.2433 | 56.3764 | -67.039 | -66.9626 | -0.017956 | -67.0612 | 56.2031 | 56.4908 | 56.3749 | -67.1797 | -0.09105 | -0.034751 | -0.023673 | 0.046271 | 0.13732 | -0.23101 | -0.097942 | -0.23178 | -0.27118 | -0.014647 | -0.11325 | 0.11853 | 0.016465 | -0.099378 | 123.3875 | 123.1912 | 123.3243 | 66.9265 | -123.5133 | 123.1511 | 123.4387 | 123.3229 | 66.93 | -123.654
645.9844 | 123.6282 | -66.98 | 56.5109 | 0.06235 | -0.029097 | -0.0090815 | 0.031022 | -0.011919 | 0.032302 | 0.080738 | -0.011332 | -0.010735 | 0.036031 | 0.085616 | 0.027841 | -66.967 | -0.021486 | -66.9062 | 56.4487 | 56.257 | 56.3764 | -67.0665 | -66.9626 | -0.022535 | -67.0566 | 56.1985 | 56.4862 | 56.3795 | -67.1843 | -0.08648 | -0.062216 | 0.012948 | 0.073735 | 0.16022 | -0.2539 | -0.13456 | -0.20432 | -0.31238 | 0.017396 | -0.076632 | 0.12768 | -0.024735 | -0.13142 | 123.4287 | 123.237 | 123.3563 | 66.9585 | -123.5774 | 123.1785 | 123.4662 | 123.3595 | 66.9574 | -123.6952
649.7656 | 123.5916 | -66.9937 | 56.5475 | 0.06235 | -0.030165 | -0.01015 | 0.029954 | -0.011919 | 0.031234 | 0.065477 | -0.010263 | -0.009667 | 0.036031 | 0.084548 | 0.027841 | -66.9762 | -0.016908 | -66.9017 | 56.4396 | 56.2616 | 56.3672 | -67.0527 | -66.9717 | -0.027113 | -67.0566 | 56.2169 | 56.4953 | 56.3703 | -67.198 | -0.05901 | -0.10799 | 0.017525 | 0.092047 | 0.15106 | -0.28594 | -0.18034 | -0.20432 | -0.33069 | 0.021972 | -0.062899 | 0.14142 | -0.052199 | -0.1772 | 123.4333 | 123.2553 | 123.3609 | 66.9768 | -123.6003 | 123.2106 | 123.4891 | 123.3641 | 66.9666 | -123.7456
650.3125 | 123.7198 | -66.98 | 56.4972 | 0.031826 | -0.030165 | -0.011218 | 0.031022 | -0.011919 | 0.031234 | 0.065477 | -0.0091947 | -0.009667 | 0.036031 | 0.086684 | 0.028909 | -66.9716 | -0.030644 | -66.8971 | 56.435 | 56.2479 | 56.3764 | -67.039 | -66.958 | -0.027113 | -67.0566 | 56.1985 | 56.4953 | 56.3703 | -67.1843 | -0.059007 | -0.062218 | 0.00837 | 0.082892 | 0.1419 | -0.24932 | -0.12083 | -0.20432 | -0.29865 | 0.021975 | -0.076632 | 0.12768 | -0.001845 | -0.12684 | 123.415 | 123.2278 | 123.3563 | 66.9493 | -123.5362 | 123.1785 | 123.4753 | 123.3503 | 66.9529 | -123.6815
651.2656 | 123.6694 | -66.9662 | 56.4926 | 0.06235 | -0.029097 | -0.011218 | 0.031022 | -0.011919 | 0.033371 | 0.050216 | -0.0124 | -0.010735 | 0.038167 | 0.086684 | 0.027841 | -66.9716 | -0.021486 | -66.8971 | 56.435 | 56.2524 | 56.3764 | -67.0481 | -66.9672 | -0.031692 | -67.0566 | 56.2077 | 56.4953 | 56.3795 | -67.1843 | -0.081896 | -0.057641 | -0.005362 | 0.06916 | 0.15106 | -0.24017 | -0.11625 | -0.21805 | -0.28491 | -0.000915 | -0.090364 | 0.12768 | 0.002732 | -0.11311 | 123.4012 | 123.2187 | 123.3426 | 66.9448 | -123.5408 | 123.1739 | 123.4616 | 123.3458 | 66.9346 | -123.6769
652.2812 | 123.7289 | -66.9937 | 56.4651 | 0.06235 | -0.028029 | -0.011218 | 0.031022 | -0.011919 | 0.031234 | 0.050216 | -0.011332 | -0.009667 | 0.037099 | 0.085616 | 0.027841 | -66.9716 | -0.026065 | -66.9017 | 56.435 | 56.2387 | 56.3764 | -67.0344 | -66.9626 | -0.031692 | -67.0566 | 56.2123 | 56.4999 | 56.3703 | -67.1889 | -0.040695 | -0.030175 | 0.022103 | 0.092047 | 0.13274 | -0.22644 | -0.088787 | -0.19516 | -0.25287 | 0.031129 | -0.062899 | 0.13226 | 0.034777 | -0.094801 | 123.4287 | 123.2324 | 123.3701 | 66.9676 | -123.4996 | 123.206 | 123.4936 | 123.3641 | 66.962 | -123.654
653.2656 | 123.6328 | -66.9571 | 56.5201 | 0.047088 | -0.030165 | -0.01015 | 0.029954 | -0.0097819 | 0.032302 | 0.080738 | -0.0091947 | -0.010735 | 0.036031 | 0.085616 | 0.028909 | -66.967 | -0.026065 | -66.9017 | 56.435 | 56.2524 | 56.3718 | -67.039 | -66.9626 | -0.031692 | -67.0566 | 56.2123 | 56.4908 | 56.3795 | -67.1889 | -0.081895 | -0.085107 | -0.00994 | 0.055426 | 0.13732 | -0.26763 | -0.1483 | -0.23178 | -0.3078 | -0.005492 | -0.09952 | 0.13226 | -0.029312 | -0.14058 | 123.3921 | 123.2095 | 123.3289 | 66.931 | -123.5591 | 123.1694 | 123.4479 | 123.3366 | 66.9254 | -123.709
654.2812 | 123.6649 | -66.9754 | 56.488 | 0.06235 | -0.030165 | -0.0090815 | 0.028885 | -0.012987 | 0.031234 | 0.050216 | -0.011332 | -0.009667 | 0.037099 | 0.086684 | 0.027841 | -66.9716 | -0.021486 | -66.8971 | 56.435 | 56.2616 | 56.3809 | -67.0436 | -66.9626 | -0.031692 | -67.0566 | 56.2031 | 56.4908 | 56.3703 | -67.1935 | -0.068162 | -0.053063 | 0.003793 | 0.078315 | 0.14648 | -0.22643 | -0.1071 | -0.21805 | -0.28491 | 0.012819 | -0.081209 | 0.13684 | 0.002732 | -0.11769 | 123.4104 | 123.237 | 123.3563 | 66.9539 | -123.5316 | 123.1785 | 123.4662 | 123.3458 | 66.9437 | -123.6815
655.2656 | 123.6191 | -66.9846 | 56.488 | 0.047088 | -0.031234 | -0.01015 | 0.031022 | -0.010851 | 0.032302 | 0.080738 | -0.011332 | -0.011804 | 0.036031 | 0.087753 | 0.027841 | -66.9716 | -0.026065 | -66.8971 | 56.4441 | 56.2524 | 56.3809 | -67.0436 | -66.958 | -0.036271 | -67.0566 | 56.2169 | 56.4953 | 56.3841 | -67.1889 | -0.059007 | -0.043906 | 0.012948 | 0.08747 | 0.14648 | -0.23559 | -0.1071 | -0.20432 | -0.27118 | 0.026553 | -0.072054 | 0.13226 | 0.00731 | -0.10395 | 123.4287 | 123.237 | 123.3655 | 66.9585 | -123.5316 | 123.2014 | 123.4799 | 123.3686 | 66.9483 | -123.6769
656.2656 | 123.6694 | -66.9617 | 56.4972 | 0.06235 | -0.030165 | -0.0090815 | 0.029954 | -0.011919 | 0.033371 | 0.065477 | -0.0091947 | -0.010735 | 0.037099 | 0.085616 | 0.028909 | -66.9808 | -0.021486 | -66.9017 | 56.4441 | 56.2524 | 56.3764 | -67.0527 | -66.9626 | -0.036271 | -67.0612 | 56.2169 | 56.4908 | 56.3749 | -67.1935 | -0.091053 | -0.053061 | -0.019097 | 0.060004 | 0.15106 | -0.24475 | -0.12083 | -0.23178 | -0.28033 | -0.000914 | -0.099521 | 0.13226 | -0.006423 | -0.12227 | 123.4058 | 123.2141 | 123.338 | 66.9402 | -123.5499 | 123.1785 | 123.4524 | 123.3366 | 66.9254 | -123.6906
657.2812 | 123.6877 | -66.9479 | 56.4514 | 0.06235 | -0.029097 | -0.01015 | 0.032091 | -0.010851 | 0.032302 | 0.065477 | -0.010263 | -0.010735 | 0.034962 | 0.088821 | 0.027841 | -66.9716 | -0.030644 | -66.8925 | 56.4441 | 56.257 | 56.3764 | -67.0344 | -66.958 | -0.040849 | -67.0475 | 56.2077 | 56.4953 | 56.3703 | -67.1843 | -0.086471 | -0.007285 | -0.023673 | 0.055427 | 0.1419 | -0.19439 | -0.075054 | -0.23636 | -0.24371 | -0.010068 | -0.099518 | 0.13684 | 0.043931 | -0.081068 | 123.3921 | 123.205 | 123.3243 | 66.9173 | -123.4858 | 123.1556 | 123.4433 | 123.3183 | 66.9071 | -123.6357
658.2656 | 123.6282 | -66.9754 | 56.5338 | 0.077612 | -0.029097 | -0.01015 | 0.029954 | -0.010851 | 0.031234 | 0.065477 | -0.011332 | -0.011804 | 0.036031 | 0.087753 | 0.025704 | -66.9625 | -0.035222 | -66.8925 | 56.4487 | 56.2479 | 56.3764 | -67.0527 | -66.9626 | -0.040849 | -67.052 | 56.2169 | 56.4908 | 56.3841 | -67.1889 | -0.07732 | -0.085104 | 0.01295 | 0.082893 | 0.16021 | -0.28595 | -0.15745 | -0.21347 | -0.31695 | 0.012819 | -0.076631 | 0.13684 | -0.043044 | -0.14973 | 123.4241 | 123.2233 | 123.3518 | 66.9402 | -123.5865 | 123.1923 | 123.4662 | 123.3595 | 66.9346 | -123.7227
659.2812 | 123.6099 | -66.9983 | 56.488 | 0.047088 | -0.030165 | -0.01015 | 0.029954 | -0.011919 | 0.032302 | 0.050216 | -0.010263 | -0.010735 | 0.037099 | 0.088821 | 0.025704 | -66.967 | -0.044379 | -66.8879 | 56.4533 | 56.2616 | 56.3855 | -67.039 | -66.958 | -0.036271 | -67.0475 | 56.2123 | 56.4953 | 56.3841 | -67.1843 | -0.040696 | -0.034749 | 0.031259 | 0.11036 | 0.15105 | -0.22643 | -0.10252 | -0.18601 | -0.27576 | 0.040286 | -0.049164 | 0.13684 | 0.00731 | -0.10395 | 123.4516 | 123.2599 | 123.3838 | 66.9539 | -123.527 | 123.2106 | 123.4936 | 123.3824 | 66.962 | -123.6723
660.2656 | 123.642 | -66.9708 | 56.5109 | 0.06235 | -0.029097 | -0.011218 | 0.028885 | -0.012987 | 0.031234 | 0.065477 | -0.011332 | -0.011804 | 0.036031 | 0.086684 | 0.027841 | -66.9625 | -0.039801 | -66.9017 | 56.4441 | 56.2616 | 56.3764 | -67.0481 | -66.9488 | -0.054586 | -67.0475 | 56.2123 | 56.4999 | 56.3703 | -67.1843 | -0.077319 | -0.066794 | 0.008372 | 0.069159 | 0.14648 | -0.24932 | -0.13456 | -0.21347 | -0.29864 | 0.021977 | -0.07663 | 0.13684 | -0.010999 | -0.14058 | 123.415 | 123.2324 | 123.3472 | 66.931 | -123.5591 | 123.1831 | 123.4708 | 123.3412 | 66.9162 | -123.6952
661.3281 | 123.7015 | -66.9342 | 56.488 | 0.047088 | -0.029097 | -0.012287 | 0.028885 | -0.011919 | 0.032302 | 0.065477 | -0.0091947 | -0.009667 | 0.037099 | 0.086684 | 0.026773 | -66.967 | -0.039801 | -66.8925 | 56.4487 | 56.257 | 56.3764 | -67.039 | -66.958 | -0.050007 | -67.0566 | 56.2077 | 56.4953 | 56.3795 | -67.1843 | -0.10478 | -0.039328 | -0.032828 | 0.041694 | 0.14648 | -0.23101 | -0.11167 | -0.25009 | -0.28034 | -0.023801 | -0.12241 | 0.12768 | 0.00731 | -0.10853 | 123.3829 | 123.1912 | 123.3106 | 66.8944 | -123.527 | 123.1419 | 123.4296 | 123.3137 | 66.8842 | -123.6723
662.2812 | 123.7061 | -66.9662 | 56.4651 | 0.06235 | -0.029097 | -0.011218 | 0.028885 | -0.012987 | 0.031234 | 0.065477 | -0.0091947 | -0.009667 | 0.032826 | 0.087753 | 0.026773 | -66.9625 | -0.044379 | -66.8879 | 56.4396 | 56.257 | 56.3809 | -67.039 | -66.9534 | -0.045428 | -67.0475 | 56.2123 | 56.4953 | 56.3749 | -67.1843 | -0.072739 | -0.025596 | 0.003795 | 0.078316 | 0.15105 | -0.20812 | -0.084208 | -0.21805 | -0.25287 | 0.012821 | -0.081207 | 0.13684 | 0.030198 | -0.090223 | 123.4058 | 123.2233 | 123.3472 | 66.9219 | -123.5041 | 123.1785 | 123.4616 | 123.3412 | 66.9208 | -123.6494
663.2656 | 123.6374 | -66.9525 | 56.5567 | 0.047088 | -0.029097 | -0.01015 | 0.029954 | -0.012987 | 0.032302 | 0.065477 | -0.011332 | -0.010735 | 0.036031 | 0.088821 | 0.027841 | -66.9533 | -0.035222 | -66.9017 | 56.4487 | 56.2616 | 56.3855 | -67.0298 | -66.958 | -0.054586 | -67.0566 | 56.2169 | 56.5045 | 56.3658 | -67.1935 | -0.077314 | -0.10799 | -0.000782 | 0.050849 | 0.12816 | -0.2951 | -0.17118 | -0.24094 | -0.33984 | -0.00549 | -0.1041 | 0.13684 | -0.052198 | -0.19093 | 123.4012 | 123.2141 | 123.338 | 66.9173 | -123.5865 | 123.1694 | 123.457 | 123.3183 | 66.8979 | -123.7502
664.2812 | 123.6008 | -66.9846 | 56.4972 | 0.031826 | -0.028029 | -0.011218 | 0.028885 | -0.014056 | 0.031234 | 0.065477 | -0.011332 | -0.011804 | 0.034962 | 0.086684 | 0.025704 | -66.9625 | -0.035222 | -66.9017 | 56.4533 | 56.2616 | 56.3809 | -67.039 | -66.9488 | -0.050007 | -67.052 | 56.2169 | 56.4908 | 56.3841 | -67.1889 | -0.054429 | -0.043904 | 0.022105 | 0.082892 | 0.13732 | -0.23559 | -0.11625 | -0.20432 | -0.28033 | 0.03571 | -0.067476 | 0.13684 | -0.006423 | -0.11311 | 123.4378 | 123.2462 | 123.3655 | 66.9493 | -123.5362 | 123.2014 | 123.4753 | 123.3686 | 66.9346 | -123.6861
665.2656 | 123.5825 | -66.9983 | 56.5338 | 0.031826 | -0.030165 | -0.01015 | 0.031022 | -0.011919 | 0.031234 | 0.034955 | -0.011332 | -0.009667 | 0.036031 | 0.086684 | 0.026773 | -66.9579 | -0.044379 | -66.8971 | 56.4441 | 56.2616 | 56.3809 | -67.0481 | -66.9626 | -0.050007 | -67.0475 | 56.2169 | 56.4953 | 56.3795 | -67.1889 | -0.049853 | -0.089682 | 0.040416 | 0.1012 | 0.15106 | -0.27221 | -0.15287 | -0.19058 | -0.31695 | 0.035707 | -0.049164 | 0.14142 | -0.038466 | -0.15431 | 123.4424 | 123.2599 | 123.3792 | 66.9539 | -123.582 | 123.2151 | 123.4936 | 123.3778 | 66.9483 | -123.7227
666.2656 | 123.6282 | -66.9479 | 56.5247 | 0.06235 | -0.029097 | -0.012287 | 0.028885 | -0.010851 | 0.031234 | 0.080738 | -0.011332 | -0.009667 | 0.034962 | 0.086684 | 0.025704 | -66.9625 | -0.044379 | -66.8971 | 56.4487 | 56.2662 | 56.3809 | -67.0481 | -66.9626 | -0.054586 | -67.0566 | 56.2077 | 56.4908 | 56.3749 | -67.1843 | -0.10021 | -0.075949 | -0.014516 | 0.050849 | 0.15106 | -0.25847 | -0.14372 | -0.23636 | -0.31696 | -0.014647 | -0.10868 | 0.12768 | -0.033889 | -0.14973 | 123.3966 | 123.2141 | 123.3289 | 66.9036 | -123.5728 | 123.1556 | 123.4387 | 123.3229 | 66.8934 | -123.709
667.2812 | 123.6008 | -67.0029 | 56.4972 | 0.06235 | -0.029097 | -0.011218 | 0.031022 | -0.014056 | 0.030166 | 0.050216 | -0.010263 | -0.010735 | 0.036031 | 0.087753 | 0.029977 | -66.9625 | -0.044379 | -66.8971 | 56.4533 | 56.2662 | 56.3809 | -67.0344 | -66.9534 | -0.054586 | -67.0429 | 56.2077 | 56.4908 | 56.3703 | -67.1889 | -0.031539 | -0.043904 | 0.040416 | 0.10578 | 0.13732 | -0.23101 | -0.11625 | -0.18601 | -0.28949 | 0.049442 | -0.040007 | 0.146 | -0.006423 | -0.12684 | 123.4562 | 123.2691 | 123.3838 | 66.9585 | -123.5316 | 123.2106 | 123.4936 | 123.3732 | 66.9483 | -123.6861
668.2656 | 123.6145 | -66.9662 | 56.5292 | 0.077612 | -0.028029 | -0.012287 | 0.028885 | -0.012987 | 0.032302 | 0.065477 | -0.011332 | -0.010735 | 0.034962 | 0.087753 | 0.026773 | -66.9625 | -0.044379 | -66.8971 | 56.4441 | 56.257 | 56.3901 | -67.0619 | -66.958 | -0.059164 | -67.0566 | 56.2123 | 56.4999 | 56.3658 | -67.1889 | -0.095633 | -0.085105 | 0.003795 | 0.06916 | 0.16479 | -0.27221 | -0.13914 | -0.22263 | -0.31696 | 0.008243 | -0.090364 | 0.13226 | -0.02931 | -0.16347 | 123.4104 | 123.2233 | 123.3563 | 66.9219 | -123.5911 | 123.1785 | 123.4662 | 123.332 | 66.9071 | -123.7181
669.2812 | 123.6603 | -66.9662 | 56.5155 | 0.06235 | -0.030165 | -0.01015 | 0.029954 | -0.014056 | 0.032302 | 0.095999 | -0.0124 | -0.009667 | 0.036031 | 0.087753 | 0.026773 | -66.9716 | -0.048958 | -66.8971 | 56.4441 | 56.257 | 56.3855 | -67.0436 | -66.9534 | -0.054586 | -67.052 | 56.2031 | 56.4862 | 56.3841 | -67.1843 | -0.077317 | -0.071372 | -0.005362 | 0.06916 | 0.14648 | -0.25848 | -0.12998 | -0.21805 | -0.31238 | 0.012821 | -0.085786 | 0.13226 | -0.029313 | -0.13142 | 123.4104 | 123.2233 | 123.3518 | 66.9173 | -123.5591 | 123.1694 | 123.4524 | 123.3503 | 66.9117 | -123.6998
670.2656 | 123.6008 | -66.9891 | 56.5247 | 0.047088 | -0.031234 | -0.0090815 | 0.028885 | -0.011919 | 0.031234 | 0.065477 | -0.0091947 | -0.010735 | 0.034962 | 0.086684 | 0.026773 | -66.967 | -0.044379 | -66.8925 | 56.4396 | 56.257 | 56.3809 | -67.039 | -66.958 | -0.068322 | -67.0475 | 56.2214 | 56.4908 | 56.3703 | -67.1889 | -0.049851 | -0.085105 | 0.022104 | 0.096626 | 0.14648 | -0.26763 | -0.14372 | -0.19974 | -0.30322 | 0.031131 | -0.058319 | 0.14142 | -0.033889 | -0.15431 | 123.4287 | 123.2462 | 123.3701 | 66.9448 | -123.5636 | 123.2106 | 123.4799 | 123.3595 | 66.9208 | -123.7135
671.2656 | 123.642 | -66.9662 | 56.5475 | 0.092874 | -0.029097 | -0.012287 | 0.028885 | -0.011919 | 0.032302 | 0.080738 | -0.010263 | -0.010735 | 0.037099 | 0.088821 | 0.027841 | -66.967 | -0.053537 | -66.8971 | 56.4441 | 56.2616 | 56.3901 | -67.0481 | -66.958 | -0.068322 | -67.0475 | 56.2077 | 56.4999 | 56.3841 | -67.1843 | -0.081896 | -0.10341 | -0.000784 | 0.06916 | 0.15106 | -0.28594 | -0.15745 | -0.21805 | -0.33984 | 0.008243 | -0.081207 | 0.13684 | -0.04762 | -0.16346 | 123.4104 | 123.2279 | 123.3563 | 66.9127 | -123.5957 | 123.1739 | 123.4662 | 123.3503 | 66.8979 | -123.7318
672.2656 | 123.7106 | -66.9159 | 56.5063 | 0.06235 | -0.030165 | -0.0090815 | 0.028885 | -0.014056 | 0.030166 | 0.080738 | -0.0091947 | -0.011804 | 0.036031 | 0.08989 | 0.026773 | -66.9579 | -0.058115 | -66.8925 | 56.4441 | 56.2616 | 56.3809 | -67.039 | -66.958 | -0.068322 | -67.0475 | 56.2077 | 56.4953 | 56.3795 | -67.1935 | -0.12309 | -0.062217 | -0.041981 | 0.023384 | 0.14648 | -0.24474 | -0.12541 | -0.27756 | -0.29865 | -0.042111 | -0.13156 | 0.146 | -0.011001 | -0.12684 | 123.36 | 123.1775 | 123.2968 | 66.8578 | -123.5453 | 123.1236 | 123.4112 | 123.2954 | 66.8476 | -123.6998
673.2656 | 123.7427 | -66.925 | 56.5704 | 0.06235 | -0.029097 | -0.011218 | 0.029954 | -0.011919 | 0.031234 | 0.095999 | -0.010263 | -0.012872 | 0.036031 | 0.088821 | 0.026773 | -66.9625 | -0.058115 | -66.8971 | 56.4441 | 56.257 | 56.3855 | -67.039 | -66.9488 | -0.0729 | -67.0429 | 56.2123 | 56.4953 | 56.3749 | -67.1843 | -0.11394 | -0.1263 | -0.037404 | 0.027961 | 0.1419 | -0.31341 | -0.18492 | -0.25925 | -0.35815 | -0.023799 | -0.11783 | 0.14142 | -0.075088 | -0.19551 | 123.3692 | 123.1821 | 123.3106 | 66.8669 | -123.6094 | 123.1373 | 123.4204 | 123.3 | 66.8521 | -123.7547
674.2812 | 123.6053 | -66.9754 | 56.5384 | 0.06235 | -0.031234 | -0.012287 | 0.032091 | -0.012987 | 0.031234 | 0.095999 | -0.0091947 | -0.010735 | 0.034962 | 0.088821 | 0.026773 | -66.967 | -0.062694 | -66.8971 | 56.4487 | 56.2662 | 56.3855 | -67.0527 | -66.9534 | -0.077479 | -67.0475 | 56.2169 | 56.4999 | 56.3612 | -67.1935 | -0.07732 | -0.089682 | 0.008371 | 0.078315 | 0.15564 | -0.27221 | -0.15287 | -0.21805 | -0.32153 | 0.021976 | -0.072052 | 0.146 | -0.038465 | -0.1772 | 123.4241 | 123.2416 | 123.3609 | 66.9127 | -123.5911 | 123.1923 | 123.4753 | 123.3366 | 66.8979 | -123.7318
675.2656 | 123.7244 | -66.9434 | 56.488 | 0.047088 | -0.029097 | -0.011218 | 0.031022 | -0.012987 | 0.033371 | 0.065477 | -0.0124 | -0.009667 | 0.033894 | 0.088821 | 0.027841 | -66.9625 | -0.067272 | -66.8925 | 56.4396 | 56.257 | 56.3764 | -67.039 | -66.958 | -0.0729 | -67.0429 | 56.2169 | 56.4953 | 56.3658 | -67.1935 | -0.095628 | -0.048484 | -0.019094 | 0.050849 | 0.14648 | -0.23101 | -0.11167 | -0.2501 | -0.27118 | -0.014646 | -0.099517 | 0.15058 | 0.00731 | -0.12227 | 123.3829 | 123.2004 | 123.3197 | 66.8761 | -123.527 | 123.1602 | 123.4387 | 123.3091 | 66.8705 | -123.6815
676.2656 | 123.6923 | -66.9525 | 56.4972 | 0.047088 | -0.031234 | -0.011218 | 0.031022 | -0.016192 | 0.031234 | 0.080738 | -0.011332 | -0.008599 | 0.034962 | 0.090958 | 0.025704 | -66.9579 | -0.062694 | -66.8971 | 56.4396 | 56.2662 | 56.3855 | -67.0527 | -66.958 | -0.082058 | -67.0475 | 56.2169 | 56.4908 | 56.3932 | -67.1935 | -0.10021 | -0.057639 | -0.00536 | 0.055427 | 0.15564 | -0.23101 | -0.11167 | -0.24094 | -0.28033 | -0.00549 | -0.09494 | 0.146 | -0.006423 | -0.10395 | 123.3921 | 123.2187 | 123.338 | 66.8898 | -123.5499 | 123.1694 | 123.4433 | 123.3458 | 66.8705 | -123.6906
677.2656 | 123.6832 | -66.9342 | 56.5338 | 0.077612 | -0.029097 | -0.011218 | 0.027817 | -0.011919 | 0.031234 | 0.065477 | -0.0091947 | -0.009667 | 0.037099 | 0.08989 | 0.026773 | -66.9579 | -0.067272 | -66.8925 | 56.4441 | 56.2616 | 56.3809 | -67.0344 | -66.9534 | -0.082058 | -67.0429 | 56.2123 | 56.4999 | 56.3887 | -67.1889 | -0.1002 | -0.089682 | -0.023671 | 0.041694 | 0.1419 | -0.27221 | -0.15287 | -0.25467 | -0.32153 | -0.019223 | -0.10867 | 0.146 | -0.033887 | -0.14515 | 123.3783 | 123.1958 | 123.3151 | 66.8669 | -123.5682 | 123.1465 | 123.4341 | 123.3229 | 66.8521 | -123.7227
678.2656 | 123.7015 | -66.925 | 56.4972 | 0.077612 | -0.031234 | -0.012287 | 0.029954 | -0.011919 | 0.030166 | 0.050216 | -0.010263 | -0.009667 | 0.036031 | 0.088821 | 0.025704 | -66.967 | -0.067272 | -66.8879 | 56.4441 | 56.2662 | 56.3809 | -67.0344 | -66.9488 | -0.082058 | -67.0429 | 56.2123 | 56.4999 | 56.3841 | -67.1935 | -0.10936 | -0.053061 | -0.041983 | 0.037117 | 0.14648 | -0.23101 | -0.11625 | -0.26841 | -0.28491 | -0.023799 | -0.11783 | 0.15058 | 0.002734 | -0.11311 | 123.3692 | 123.1912 | 123.306 | 66.8578 | -123.5316 | 123.1373 | 123.425 | 123.3091 | 66.843 | -123.6906
679.2656 | 123.7335 | -66.925 | 56.488 | 0.06235 | -0.029097 | -0.012287 | 0.028885 | -0.012987 | 0.030166 | 0.080738 | -0.0124 | -0.010735 | 0.033894 | 0.08989 | 0.027841 | -66.967 | -0.067272 | -66.8879 | 56.435 | 56.2616 | 56.3855 | -67.039 | -66.9534 | -0.086637 | -67.052 | 56.2077 | 56.4999 | 56.3749 | -67.1843 | -0.11394 | -0.053063 | -0.041983 | 0.037117 | 0.15105 | -0.22643 | -0.10252 | -0.25925 | -0.28034 | -0.028378 | -0.12699 | 0.13226 | 0.011889 | -0.11311 | 123.36 | 123.1867 | 123.3106 | 66.8578 | -123.527 | 123.1328 | 123.425 | 123.3 | 66.8384 | -123.6723
680.2656 | 123.7335 | -66.9342 | 56.5018 | 0.06235 | -0.030165 | -0.011218 | 0.031022 | -0.012987 | 0.030166 | 0.065477 | -0.010263 | -0.011804 | 0.033894 | 0.08989 | 0.026773 | -66.967 | -0.067272 | -66.8971 | 56.4441 | 56.257 | 56.3855 | -67.0344 | -66.9488 | -0.091215 | -67.052 | 56.2214 | 56.5045 | 56.3658 | -67.1935 | -0.1002 | -0.057639 | -0.032828 | 0.037116 | 0.13732 | -0.24474 | -0.11625 | -0.25925 | -0.28033 | -0.014644 | -0.11783 | 0.14142 | 0.002734 | -0.136 | 123.3783 | 123.1912 | 123.3197 | 66.8669 | -123.5362 | 123.1556 | 123.4387 | 123.3 | 66.843 | -123.6952
681.2656 | 123.7701 | -66.9022 | 56.4835 | 0.06235 | -0.030165 | -0.01015 | 0.028885 | -0.011919 | 0.030166 | 0.065477 | -0.010263 | -0.009667 | 0.034962 | 0.090958 | 0.026773 | -66.9579 | -0.071851 | -66.9017 | 56.4396 | 56.257 | 56.3764 | -67.039 | -66.958 | -0.095794 | -67.0475 | 56.2123 | 56.4908 | 56.3795 | -67.1935 | -0.13683 | -0.043906 | -0.055714 | 0.000495 | 0.13732 | -0.22643 | -0.1071 | -0.29129 | -0.27118 | -0.055844 | -0.14529 | 0.146 | 0.00731 | -0.10395 | 123.3417 | 123.1592 | 123.2785 | 66.8303 | -123.5224 | 123.1144 | 123.3929 | 123.2817 | 66.8064 | -123.6769
682.2656 | 123.7564 | -66.9342 | 56.4972 | 0.06235 | -0.032302 | -0.011218 | 0.029954 | -0.014056 | 0.029097 | 0.095999 | -0.013468 | -0.010735 | 0.033894 | 0.090958 | 0.026773 | -66.9625 | -0.067272 | -66.8971 | 56.4396 | 56.2662 | 56.3764 | -67.0344 | -66.9672 | -0.091215 | -67.052 | 56.2123 | 56.4908 | 56.3795 | -67.1935 | -0.1002 | -0.057639 | -0.028249 | 0.037116 | 0.13732 | -0.23101 | -0.12083 | -0.25925 | -0.28491 | -0.032959 | -0.11783 | 0.14142 | -0.006423 | -0.11769 | 123.3738 | 123.2004 | 123.3106 | 66.8669 | -123.5316 | 123.1465 | 123.425 | 123.3137 | 66.843 | -123.6906
683.2656 | 123.7381 | -66.9388 | 56.4835 | 0.092874 | -0.030165 | -0.011218 | 0.028885 | -0.014056 | 0.031234 | 0.080738 | -0.011332 | -0.009667 | 0.034962 | 0.08989 | 0.027841 | -66.9625 | -0.07643 | -66.8971 | 56.435 | 56.2616 | 56.3809 | -67.0527 | -66.9672 | -0.095794 | -67.0475 | 56.2214 | 56.4999 | 56.3841 | -67.1935 | -0.11394 | -0.048485 | -0.023671 | 0.041694 | 0.15564 | -0.22185 | -0.10252 | -0.25467 | -0.26202 | -0.028381 | -0.10867 | 0.146 | 0.016467 | -0.099376 | 123.3738 | 123.2004 | 123.3197 | 66.8624 | -123.5362 | 123.1602 | 123.4387 | 123.3229 | 66.843 | -123.6769
684.2812 | 123.6282 | -66.9617 | 56.4789 | 0.047088 | -0.031234 | -0.011218 | 0.028885 | -0.010851 | 0.030166 | 0.080738 | -0.010263 | -0.009667 | 0.036031 | 0.08989 | 0.025704 | -66.9625 | -0.081008 | -66.8925 | 56.4487 | 56.2616 | 56.3809 | -67.0481 | -66.9488 | -0.10037 | -67.052 | 56.2169 | 56.4953 | 56.3795 | -67.1889 | -0.086474 | -0.030173 | -0.000783 | 0.06916 | 0.15563 | -0.21728 | -0.097941 | -0.2272 | -0.26202 | 0.012822 | -0.090364 | 0.13684 | 0.016465 | -0.099377 | 123.4104 | 123.2233 | 123.3426 | 66.8807 | -123.527 | 123.1785 | 123.457 | 123.3412 | 66.8613 | -123.6678
685.2656 | 123.7518 | -66.925 | 56.4789 | 0.047088 | -0.032302 | -0.011218 | 0.029954 | -0.011919 | 0.028029 | 0.080738 | -0.011332 | -0.011804 | 0.036031 | 0.08989 | 0.025704 | -66.9579 | -0.07643 | -66.8879 | 56.4441 | 56.257 | 56.3901 | -67.039 | -66.9534 | -0.10495 | -67.0475 | 56.2169 | 56.4999 | 56.3795 | -67.1935 | -0.11394 | -0.034751 | -0.032826 | 0.037117 | 0.15105 | -0.22186 | -0.088784 | -0.26841 | -0.26202 | -0.028378 | -0.12241 | 0.146 | 0.021044 | -0.099377 | 123.3692 | 123.1821 | 123.3151 | 66.8486 | -123.5179 | 123.1419 | 123.425 | 123.3046 | 66.8201 | -123.6723
686.2656 | 123.6923 | -66.9434 | 56.4697 | 0.06235 | -0.031234 | -0.01015 | 0.029954 | -0.011919 | 0.029097 | 0.065477 | -0.011332 | -0.009667 | 0.034962 | 0.092026 | 0.025704 | -66.967 | -0.081008 | -66.9017 | 56.4396 | 56.2616 | 56.3809 | -67.0344 | -66.9534 | -0.10953 | -67.0475 | 56.2077 | 56.4908 | 56.3612 | -67.1889 | -0.091049 | -0.030174 | -0.023673 | 0.041693 | 0.13274 | -0.20812 | -0.088786 | -0.24552 | -0.26203 | -0.010068 | -0.1041 | 0.14142 | 0.021042 | -0.10854 | 123.3829 | 123.205 | 123.3243 | 66.8624 | -123.5041 | 123.1511 | 123.4341 | 123.3045 | 66.8338 | -123.6586
687.2656 | 123.6969 | -66.925 | 56.5018 | 0.077612 | -0.031234 | -0.013355 | 0.028885 | -0.012987 | 0.033371 | 0.065477 | -0.010263 | -0.008599 | 0.034962 | 0.092026 | 0.025704 | -66.9625 | -0.090166 | -66.8971 | 56.4441 | 56.257 | 56.3809 | -67.0481 | -66.9443 | -0.10953 | -67.0383 | 56.2169 | 56.4953 | 56.3749 | -67.1843 | -0.12309 | -0.057639 | -0.037404 | 0.027961 | 0.15106 | -0.24474 | -0.12083 | -0.25925 | -0.28491 | -0.01922 | -0.11325 | 0.146 | -0.006423 | -0.12684 | 123.3692 | 123.1821 | 123.306 | 66.8349 | -123.5499 | 123.1419 | 123.4204 | 123.3 | 66.8155 | -123.6861
688.2656 | 123.6832 | -66.925 | 56.4972 | 0.031826 | -0.03337 | -0.01015 | 0.029954 | -0.014056 | 0.030166 | 0.095999 | -0.011332 | -0.012872 | 0.034962 | 0.092026 | 0.026773 | -66.9579 | -0.085587 | -66.8925 | 56.4533 | 56.2662 | 56.3855 | -67.0298 | -66.958 | -0.10953 | -67.0475 | 56.2123 | 56.5091 | 56.3841 | -67.1797 | -0.10478 | -0.043904 | -0.032826 | 0.032539 | 0.13732 | -0.23101 | -0.11167 | -0.25467 | -0.28491 | -0.032956 | -0.12241 | 0.13226 | 0.011891 | -0.11311 | 123.3783 | 123.1912 | 123.3106 | 66.8395 | -123.527 | 123.1373 | 123.4341 | 123.3091 | 66.8155 | -123.6769
689.2812 | 123.642 | -66.9525 | 56.5384 | 0.06235 | -0.031234 | -0.011218 | 0.028885 | -0.012987 | 0.030166 | 0.080738 | -0.0091947 | -0.009667 | 0.033894 | 0.08989 | 0.025704 | -66.9533 | -0.085587 | -66.8879 | 56.4487 | 56.2708 | 56.3901 | -67.0436 | -66.9534 | -0.11869 | -67.0429 | 56.2306 | 56.4999 | 56.3887 | -67.1797 | -0.09105 | -0.089682 | -0.000782 | 0.064583 | 0.15563 | -0.26763 | -0.14829 | -0.2272 | -0.3078 | -0.000912 | -0.090361 | 0.13684 | -0.038465 | -0.14973 | 123.4012 | 123.2233 | 123.3426 | 66.8669 | -123.582 | 123.1831 | 123.4524 | 123.3412 | 66.8338 | -123.7181
690.2656 | 123.674 | -66.9113 | 56.4789 | 0.077612 | -0.031234 | -0.011218 | 0.028885 | -0.011919 | 0.031234 | 0.065477 | -0.0091947 | -0.009667 | 0.034962 | 0.092026 | 0.025704 | -66.9533 | -0.094744 | -66.8788 | 56.4624 | 56.2662 | 56.3947 | -67.0298 | -66.9534 | -0.11869 | -67.0337 | 56.2214 | 56.5091 | 56.3749 | -67.1889 | -0.11851 | -0.016437 | -0.041981 | 0.032541 | 0.15105 | -0.2127 | -0.084205 | -0.27756 | -0.25744 | -0.042111 | -0.1224 | 0.15516 | 0.030201 | -0.10396 | 123.3738 | 123.1775 | 123.306 | 66.8166 | -123.5087 | 123.1328 | 123.4204 | 123.2862 | 66.7926 | -123.6678
691.2656 | 123.7015 | -66.9479 | 56.4972 | 0.047088 | -0.032302 | -0.012287 | 0.028885 | -0.014056 | 0.030166 | 0.050216 | -0.010263 | -0.010735 | 0.033894 | 0.092026 | 0.026773 | -66.9533 | -0.099323 | -66.8834 | 56.4533 | 56.2753 | 56.3901 | -67.0344 | -66.9488 | -0.11869 | -67.0337 | 56.2169 | 56.5045 | 56.3978 | -67.1751 | -0.086471 | -0.043904 | -0.00536 | 0.064584 | 0.15105 | -0.22185 | -0.10709 | -0.2272 | -0.28033 | -0.000911 | -0.085782 | 0.14142 | 0.007312 | -0.099373 | 123.4012 | 123.2233 | 123.338 | 66.8486 | -123.5316 | 123.1648 | 123.4524 | 123.3458 | 66.8293 | -123.6723
692.2656 | 123.6694 | -66.9525 | 56.5155 | 0.06235 | -0.03337 | -0.013355 | 0.026749 | -0.014056 | 0.031234 | 0.080738 | -0.011332 | -0.010735 | 0.034962 | 0.092026 | 0.023568 | -66.9533 | -0.099323 | -66.8788 | 56.4624 | 56.2708 | 56.3901 | -67.0252 | -66.9351 | -0.11869 | -67.0337 | 56.2306 | 56.4953 | 56.4024 | -67.1751 | -0.072735 | -0.053058 | -0.000782 | 0.07374 | 0.14647 | -0.24474 | -0.12541 | -0.22262 | -0.28491 | 0.017403 | -0.081204 | 0.14142 | -0.020156 | -0.11311 | 123.415 | 123.2233 | 123.3426 | 66.8532 | -123.5408 | 123.1831 | 123.4479 | 123.3549 | 66.8338 | -123.6906
693.2656 | 123.7061 | -66.9434 | 56.4789 | 0.047088 | -0.032302 | -0.014424 | 0.029954 | -0.011919 | 0.032302 | 0.095999 | -0.011332 | -0.010735 | 0.034962 | 0.090958 | 0.024636 | -66.9533 | -0.10848 | -66.8788 | 56.4579 | 56.2799 | 56.3901 | -67.0207 | -66.9397 | -0.12784 | -67.0291 | 56.2214 | 56.5091 | 56.3887 | -67.1751 | -0.077312 | -0.021016 | -0.009938 | 0.064584 | 0.1419 | -0.19896 | -0.088784 | -0.23178 | -0.25744 | 0.003669 | -0.085781 | 0.146 | 0.030201 | -0.09022 | 123.4012 | 123.2233 | 123.3335 | 66.8349 | -123.4996 | 123.1648 | 123.4524 | 123.332 | 66.8155 | -123.654
694.2812 | 123.6877 | -66.8976 | 56.5292 | 0.047088 | -0.032302 | -0.012287 | 0.028885 | -0.012987 | 0.032302 | 0.065477 | -0.010263 | -0.010735 | 0.032826 | 0.092026 | 0.023568 | -66.9441 | -0.10848 | -66.8742 | 56.4579 | 56.2753 | 56.3947 | -67.039 | -66.9351 | -0.13242 | -67.0337 | 56.2352 | 56.5091 | 56.4024 | -67.1797 | -0.1414 | -0.07137 | -0.046557 | 0.023386 | 0.16479 | -0.25389 | -0.13456 | -0.28213 | -0.29406 | -0.037529 | -0.13614 | 0.146 | -0.020153 | -0.12684 | 123.3554 | 123.1729 | 123.2923 | 66.7891 | -123.5682 | 123.1328 | 123.4067 | 123.3 | 66.7652 | -123.709
695.2656 | 123.6923 | -66.9205 | 56.4606 | 0.031826 | -0.03337 | -0.012287 | 0.027817 | -0.012987 | 0.029097 | 0.065477 | -0.011332 | -0.012872 | 0.034962 | 0.093095 | 0.026773 | -66.9533 | -0.1039 | -66.8788 | 56.4579 | 56.2891 | 56.3947 | -67.0298 | -66.9397 | -0.13242 | -67.0291 | 56.2306 | 56.5137 | 56.3932 | -67.1751 | -0.10936 | -0.002705 | -0.032826 | 0.041696 | 0.15105 | -0.17149 | -0.065894 | -0.25467 | -0.22998 | -0.019219 | -0.10867 | 0.146 | 0.053091 | -0.06733 | 123.3783 | 123.2095 | 123.3151 | 66.8166 | -123.4904 | 123.1511 | 123.4341 | 123.3137 | 66.788 | -123.6357
696.2656 | 123.7015 | -66.925 | 56.5063 | 0.06235 | -0.03337 | -0.011218 | 0.027817 | -0.012987 | 0.029097 | 0.065477 | -0.011332 | -0.011804 | 0.033894 | 0.090958 | 0.025704 | -66.9487 | -0.10848 | -66.8834 | 56.4487 | 56.2708 | 56.3901 | -67.039 | -66.9397 | -0.137 | -67.0291 | 56.2214 | 56.5091 | 56.3887 | -67.1751 | -0.11394 | -0.057639 | -0.023669 | 0.041696 | 0.15563 | -0.23559 | -0.11625 | -0.25009 | -0.28491 | -0.014641 | -0.10409 | 0.146 | 0.002735 | -0.11769 | 123.3738 | 123.1958 | 123.3151 | 66.8166 | -123.5453 | 123.1465 | 123.4341 | 123.3137 | 66.788 | -123.6815
697.2656 | 123.6877 | -66.9708 | 56.4926 | 0.06235 | -0.03337 | -0.011218 | 0.028885 | -0.015124 | 0.030166 | 0.080738 | -0.010263 | -0.011804 | 0.034962 | 0.092026 | 0.023568 | -66.9533 | -0.11764 | -66.8742 | 56.4579 | 56.2662 | 56.3947 | -67.0298 | -66.9305 | -0.137 | -67.0383 | 56.2306 | 56.4999 | 56.3932 | -67.1706 | -0.059004 | -0.034749 | 0.017528 | 0.096628 | 0.15563 | -0.22643 | -0.097938 | -0.19973 | -0.26202 | 0.040292 | -0.067473 | 0.13226 | 0.007311 | -0.099374 | 123.4287 | 123.237 | 123.3655 | 66.8532 | -123.5224 | 123.2014 | 123.4708 | 123.3641 | 66.8338 | -123.6632
698.2656 | 123.7015 | -66.9479 | 56.4972 | 0.06235 | -0.031234 | -0.01015 | 0.029954 | -0.014056 | 0.029097 | 0.065477 | -0.011332 | -0.011804 | 0.034962 | 0.092026 | 0.025704 | -66.9441 | -0.12222 | -66.8742 | 56.4579 | 56.2662 | 56.3993 | -67.0344 | -66.9443 | -0.14158 | -67.02 | 56.226 | 56.5091 | 56.3887 | -67.1751 | -0.086471 | -0.039326 | 0.003797 | 0.07374 | 0.16021 | -0.23101 | -0.097937 | -0.2272 | -0.27118 | 0.003668 | -0.072046 | 0.15516 | 0.011891 | -0.10853 | 123.4058 | 123.2141 | 123.3472 | 66.8257 | -123.5316 | 123.174 | 123.457 | 123.3366 | 66.8064 | -123.6723
699.2812 | 123.7656 | -66.9159 | 56.5201 | 0.06235 | -0.032302 | -0.012287 | 0.027817 | -0.012987 | 0.029097 | 0.080738 | -0.011332 | -0.010735 | 0.037099 | 0.093095 | 0.023568 | -66.9441 | -0.11306 | -66.8696 | 56.4624 | 56.2845 | 56.3993 | -67.0252 | -66.9397 | -0.15074 | -67.0246 | 56.2352 | 56.5182 | 56.3932 | -67.1751 | -0.10936 | -0.057636 | -0.028246 | 0.046276 | 0.15563 | -0.23558 | -0.12083 | -0.25924 | -0.28491 | -0.023796 | -0.10867 | 0.15058 | -0.001841 | -0.12684 | 123.3783 | 123.2004 | 123.3151 | 66.8028 | -123.5453 | 123.1511 | 123.4341 | 123.3091 | 66.7652 | -123.6952
700.2656 | 123.7198 | -66.9113 | 56.4972 | 0.047088 | -0.032302 | -0.012287 | 0.027817 | -0.011919 | 0.030166 | 0.050216 | -0.011332 | -0.010735 | 0.033894 | 0.094163 | 0.024636 | -66.9487 | -0.12679 | -66.8605 | 56.467 | 56.2799 | 56.4084 | -67.0161 | -66.9214 | -0.15532 | -67.0246 | 56.2352 | 56.5137 | 56.3932 | -67.166 | -0.10478 | -0.030169 | -0.037402 | 0.050854 | 0.15563 | -0.21727 | -0.08878 | -0.25467 | -0.26202 | -0.01006 | -0.11325 | 0.14142 | 0.01647 | -0.10395 | 123.3783 | 123.1912 | 123.3197 | 66.7845 | -123.5133 | 123.1465 | 123.425 | 123.3046 | 66.756 | -123.6632
701.2656 | 123.7106 | -66.9067 | 56.5109 | 0.047088 | -0.032302 | -0.011218 | 0.027817 | -0.011919 | 0.031234 | 0.065477 | -0.011332 | -0.010735 | 0.032826 | 0.093095 | 0.025704 | -66.9304 | -0.12222 | -66.8467 | 56.4808 | 56.2891 | 56.4176 | -67.0161 | -66.9122 | -0.15532 | -67.0154 | 56.2443 | 56.532 | 56.4024 | -67.1568 | -0.10935 | -0.030167 | -0.023667 | 0.060011 | 0.16936 | -0.22185 | -0.093355 | -0.25008 | -0.2666 | -0.00548 | -0.10867 | 0.14142 | 0.021051 | -0.10853 | 123.3875 | 123.1958 | 123.3243 | 66.7845 | -123.527 | 123.1511 | 123.4387 | 123.3091 | 66.7514 | -123.6677
702.2656 | 123.7061 | -66.9205 | 56.5155 | 0.031826 | -0.03337 | -0.013355 | 0.027817 | -0.012987 | 0.030166 | 0.065477 | -0.011332 | -0.010735 | 0.033894 | 0.093095 | 0.024636 | -66.9304 | -0.12679 | -66.8559 | 56.4808 | 56.2937 | 56.4176 | -67.0115 | -66.9305 | -0.1599 | -67.02 | 56.2398 | 56.5228 | 56.4024 | -67.1706 | -0.091042 | -0.034745 | -0.009934 | 0.064587 | 0.15563 | -0.22185 | -0.097933 | -0.25009 | -0.27575 | -0.010062 | -0.099512 | 0.15058 | 0.007316 | -0.11311 | 123.4012 | 123.2141 | 123.338 | 66.7937 | -123.527 | 123.1602 | 123.4433 | 123.3229 | 66.7606 | -123.6861
703.2656 | 123.6877 | -66.925 | 56.5384 | 0.047088 | -0.03337 | -0.012287 | 0.027817 | -0.011919 | 0.029097 | 0.034955 | -0.011332 | -0.009667 | 0.034962 | 0.093095 | 0.024636 | -66.9167 | -0.13137 | -66.8421 | 56.4808 | 56.2845 | 56.4176 | -66.9886 | -66.9214 | -0.1599 | -67.0062 | 56.2581 | 56.532 | 56.4116 | -67.1522 | -0.063569 | -0.057633 | 0.00838 | 0.0829 | 0.14647 | -0.25389 | -0.12082 | -0.22719 | -0.28033 | 0.003673 | -0.081198 | 0.146 | -0.006415 | -0.12684 | 123.4058 | 123.2095 | 123.3426 | 66.7937 | -123.527 | 123.1831 | 123.457 | 123.3366 | 66.7652 | -123.6906
704.2812 | 123.7289 | -66.893 | 56.5521 | 0.047088 | -0.03337 | -0.012287 | 0.028885 | -0.015124 | 0.028029 | 0.080738 | -0.010263 | -0.011804 | 0.033894 | 0.093095 | 0.024636 | -66.9212 | -0.13137 | -66.833 | 56.4853 | 56.3028 | 56.4359 | -67.0024 | -66.9168 | -0.16905 | -67.0062 | 56.2626 | 56.5411 | 56.4207 | -67.1568 | -0.10935 | -0.066788 | -0.028243 | 0.060013 | 0.16936 | -0.24931 | -0.11624 | -0.26382 | -0.28948 | -0.023792 | -0.11324 | 0.15058 | -0.010991 | -0.13141 | 123.3783 | 123.1958 | 123.3289 | 66.7616 | -123.5545 | 123.1556 | 123.4341 | 123.3137 | 66.724 | -123.7089
705.2656 | 123.7198 | -66.8793 | 56.5247 | 0.06235 | -0.03337 | -0.013355 | 0.027817 | -0.012987 | 0.029097 | 0.050216 | -0.011332 | -0.011804 | 0.031758 | 0.094163 | 0.024636 | -66.9121 | -0.13595 | -66.8193 | 56.4945 | 56.3166 | 56.4313 | -66.984 | -66.8939 | -0.17363 | -66.9971 | 56.2672 | 56.5411 | 56.4161 | -67.1431 | -0.10477 | -0.030165 | -0.032819 | 0.060015 | 0.16478 | -0.20811 | -0.093353 | -0.26381 | -0.25744 | -0.014631 | -0.11782 | 0.146 | 0.016475 | -0.10852 | 123.3738 | 123.1958 | 123.3106 | 66.7433 | -123.5087 | 123.1465 | 123.4204 | 123.2954 | 66.7056 | -123.6677
706.2656 | 123.7244 | -66.9205 | 56.456 | 0.031826 | -0.032302 | -0.011218 | 0.028885 | -0.014056 | 0.028029 | 0.065477 | -0.0124 | -0.009667 | 0.032826 | 0.092026 | 0.024636 | -66.9396 | -0.13595 | -66.8559 | 56.4762 | 56.2891 | 56.413 | -67.0207 | -66.926 | -0.17821 | -67.0154 | 56.2352 | 56.5182 | 56.4024 | -67.166 | -0.1002 | 0.020186 | -0.01909 | 0.064587 | 0.16479 | -0.16692 | -0.043003 | -0.24551 | -0.22082 | -0.005483 | -0.094933 | 0.15058 | 0.062246 | -0.053596 | 123.3967 | 123.2095 | 123.3335 | 66.7845 | -123.4767 | 123.1556 | 123.4387 | 123.3229 | 66.7423 | -123.622
707.2656 | 123.6969 | -66.8838 | 56.543 | 0.06235 | -0.03337 | -0.012287 | 0.027817 | -0.015124 | 0.030166 | 0.065477 | -0.010263 | -0.010735 | 0.033894 | 0.094163 | 0.024636 | -66.9167 | -0.14511 | -66.8238 | 56.4853 | 56.2982 | 56.4313 | -66.984 | -66.9076 | -0.16905 | -66.9971 | 56.2581 | 56.5457 | 56.4207 | -67.1477 | -0.10019 | -0.057633 | -0.032819 | 0.060014 | 0.1602 | -0.24473 | -0.11166 | -0.26382 | -0.2849 | -0.023789 | -0.11324 | 0.15058 | 0.002743 | -0.12226 | 123.3692 | 123.1821 | 123.3152 | 66.7387 | -123.527 | 123.1419 | 123.4296 | 123.3046 | 66.7148 | -123.6906
708.2656 | 123.7381 | -66.9342 | 56.4972 | 0.047088 | -0.032302 | -0.012287 | 0.027817 | -0.012987 | 0.030166 | 0.065477 | -0.010263 | -0.010735 | 0.034962 | 0.094163 | 0.025704 | -66.9396 | -0.13595 | -66.8605 | 56.4624 | 56.2891 | 56.4084 | -67.0161 | -66.9214 | -0.18737 | -67.0246 | 56.2443 | 56.5274 | 56.4116 | -67.166 | -0.081888 | -0.034747 | -0.005357 | 0.073742 | 0.15563 | -0.20811 | -0.08878 | -0.23178 | -0.25286 | 0.012828 | -0.090357 | 0.14142 | 0.030205 | -0.085637 | 123.3966 | 123.2233 | 123.3426 | 66.7983 | -123.5133 | 123.1785 | 123.4616 | 123.3458 | 66.7468 | -123.6632
709.2812 | 123.7106 | -66.9159 | 56.5109 | 0.077612 | -0.032302 | -0.011218 | 0.027817 | -0.012987 | 0.029097 | 0.050216 | -0.010263 | -0.011804 | 0.033894 | 0.092026 | 0.022499 | -66.9075 | -0.14969 | -66.8238 | 56.4899 | 56.312 | 56.4359 | -66.9978 | -66.8985 | -0.19653 | -66.9971 | 56.2672 | 56.5457 | 56.4299 | -67.1431 | -0.081882 | -0.02101 | 0.008381 | 0.092058 | 0.17394 | -0.19895 | -0.075041 | -0.22719 | -0.2437 | 0.017412 | -0.081195 | 0.146 | 0.034787 | -0.081056 | 123.4058 | 123.2279 | 123.3518 | 66.7662 | -123.5087 | 123.1831 | 123.4616 | 123.3458 | 66.7194 | -123.654
710.2656 | 123.7106 | -66.9388 | 56.4651 | 0.047088 | -0.032302 | -0.011218 | 0.027817 | -0.012987 | 0.029097 | 0.065477 | -0.010263 | -0.009667 | 0.034962 | 0.093095 | 0.025704 | -66.9167 | -0.14969 | -66.8376 | 56.4945 | 56.2982 | 56.4267 | -67.0024 | -66.9076 | -0.19195 | -67.02 | 56.2489 | 56.5274 | 56.407 | -67.1568 | -0.063573 | 0.029344 | 0.022113 | 0.10121 | 0.16478 | -0.16691 | -0.038422 | -0.21804 | -0.21624 | 0.031143 | -0.081201 | 0.13684 | 0.062248 | -0.058173 | 123.4333 | 123.237 | 123.3655 | 66.7891 | -123.4675 | 123.1877 | 123.4662 | 123.3458 | 66.7468 | -123.622
711.2656 | 123.7473 | -66.893 | 56.5201 | 0.047088 | -0.034439 | -0.014424 | 0.027817 | -0.012987 | 0.028029 | 0.080738 | -0.011332 | -0.009667 | 0.031758 | 0.092026 | 0.024636 | -66.9029 | -0.14969 | -66.8147 | 56.5037 | 56.3166 | 56.4405 | -66.9978 | -66.8939 | -0.19195 | -66.9879 | 56.2626 | 56.5503 | 56.4299 | -67.1339 | -0.10477 | -0.016431 | -0.009929 | 0.078326 | 0.1831 | -0.20353 | -0.079618 | -0.24092 | -0.25744 | -0.000898 | -0.094927 | 0.146 | 0.030209 | -0.090212 | 123.3967 | 123.2096 | 123.3335 | 66.7433 | -123.5179 | 123.1556 | 123.4433 | 123.3229 | 66.7011 | -123.654
712.2656 | 123.6969 | -66.8976 | 56.5063 | 0.047088 | -0.03337 | -0.011218 | 0.027817 | -0.014056 | 0.029097 | 0.065477 | -0.0091947 | -0.010735 | 0.032826 | 0.094163 | 0.023568 | -66.935 | -0.15427 | -66.8421 | 56.4762 | 56.2982 | 56.4221 | -67.0252 | -66.9214 | -0.2011 | -67.0108 | 56.2443 | 56.5274 | 56.4024 | -67.1706 | -0.12767 | -0.030168 | -0.0374 | 0.055434 | 0.1831 | -0.20811 | -0.0842 | -0.27298 | -0.26202 | -0.023793 | -0.11324 | 0.15973 | 0.021049 | -0.10395 | 123.3738 | 123.1958 | 123.3197 | 66.7433 | -123.5316 | 123.1419 | 123.425 | 123.3 | 66.6965 | -123.6769
713.2656 | 123.6603 | -66.9434 | 56.5109 | 0.031826 | -0.03337 | -0.013355 | 0.027817 | -0.014056 | 0.030166 | 0.065477 | -0.0124 | -0.011804 | 0.034962 | 0.094163 | 0.022499 | -66.935 | -0.168 | -66.8513 | 56.4762 | 56.2845 | 56.4084 | -67.0115 | -66.926 | -0.21026 | -67.0154 | 56.2352 | 56.5228 | 56.3841 | -67.1706 | -0.068154 | -0.034745 | 0.008376 | 0.092054 | 0.16021 | -0.22643 | -0.10251 | -0.2272 | -0.27575 | 0.017405 | -0.072045 | 0.15516 | 0.011894 | -0.12684 | 123.4195 | 123.2279 | 123.3518 | 66.7754 | -123.5224 | 123.1785 | 123.4662 | 123.3274 | 66.7331 | -123.6815
714.2812 | 123.6603 | -66.925 | 56.5109 | 0.077612 | -0.03337 | -0.012287 | 0.028885 | -0.012987 | 0.029097 | 0.065477 | -0.0091947 | -0.010735 | 0.031758 | 0.095231 | 0.024636 | -66.9121 | -0.168 | -66.833 | 56.4899 | 56.2982 | 56.4267 | -67.0024 | -66.926 | -0.21026 | -67.0017 | 56.2535 | 56.5366 | 56.4207 | -67.1522 | -0.077306 | -0.02101 | 0.012958 | 0.092057 | 0.16936 | -0.21269 | -0.084198 | -0.22719 | -0.25744 | -0.000905 | -0.076619 | 0.15058 | 0.02563 | -0.090213 | 123.415 | 123.2233 | 123.3518 | 66.757 | -123.5133 | 123.1785 | 123.4616 | 123.3458 | 66.7148 | -123.6632
715.2656 | 123.7244 | -66.925 | 56.5292 | 0.06235 | -0.032302 | -0.012287 | 0.027817 | -0.015124 | 0.030166 | 0.065477 | -0.0124 | -0.008599 | 0.032826 | 0.094163 | 0.023568 | -66.9121 | -0.16342 | -66.8193 | 56.4899 | 56.312 | 56.4313 | -66.9932 | -66.8939 | -0.21484 | -66.9925 | 56.2581 | 56.5457 | 56.4253 | -67.1385 | -0.068148 | -0.039321 | 0.012958 | 0.10579 | 0.17394 | -0.21726 | -0.097931 | -0.21346 | -0.27117 | 0.031146 | -0.067461 | 0.146 | 0.016476 | -0.10394 | 123.415 | 123.237 | 123.3564 | 66.7616 | -123.5224 | 123.1831 | 123.4708 | 123.3503 | 66.7102 | -123.6677
716.2656 | 123.7015 | -66.8427 | 56.5567 | 0.06235 | -0.034439 | -0.013355 | 0.027817 | -0.014056 | 0.029097 | 0.065477 | -0.013468 | -0.011804 | 0.034962 | 0.094163 | 0.024636 | -66.8755 | -0.17716 | -66.7689 | 56.5311 | 56.3486 | 56.4771 | -66.9474 | -66.8664 | -0.21942 | -66.9605 | 56.2947 | 56.5732 | 56.4711 | -67.1156 | -0.10476 | -0.025582 | -0.032813 | 0.073755 | 0.17851 | -0.2081 | -0.079611 | -0.27296 | -0.26201 | -0.02378 | -0.11781 | 0.15515 | 0.016481 | -0.085625 | 123.3738 | 123.1913 | 123.3197 | 66.6655 | -123.5041 | 123.1373 | 123.4158 | 123.3137 | 66.6232 | -123.6723
717.2656 | 123.7244 | -66.9113 | 56.5063 | 0.06235 | -0.034439 | -0.012287 | 0.024612 | -0.014056 | 0.030166 | 0.050216 | -0.011332 | -0.009667 | 0.031758 | 0.0963 | 0.023568 | -66.9029 | -0.17258 | -66.8055 | 56.5037 | 56.312 | 56.4405 | -66.984 | -66.8985 | -0.224 | -66.9788 | 56.2672 | 56.5549 | 56.4299 | -67.1294 | -0.072723 | -0.002698 | 0.008382 | 0.10579 | 0.17852 | -0.19438 | -0.065885 | -0.21803 | -0.23913 | 0.012834 | -0.067458 | 0.15058 | 0.048521 | -0.076479 | 123.415 | 123.2233 | 123.3518 | 66.7387 | -123.4904 | 123.1785 | 123.4662 | 123.3412 | 66.6873 | -123.6357
718.2656 | 123.7152 | -66.861 | 56.5338 | 0.06235 | -0.03337 | -0.013355 | 0.026749 | -0.011919 | 0.029097 | 0.065477 | -0.011332 | -0.012872 | 0.033894 | 0.094163 | 0.024636 | -66.9029 | -0.17716 | -66.8147 | 56.5037 | 56.3028 | 56.4496 | -66.984 | -66.9031 | -0.22858 | -66.9879 | 56.2626 | 56.5457 | 56.4299 | -67.1477 | -0.12308 | -0.030163 | -0.041972 | 0.046283 | 0.16936 | -0.231 | -0.084193 | -0.2867 | -0.27117 | -0.042099 | -0.12697 | 0.15973 | 0.011899 | -0.10394 | 123.3646 | 123.1638 | 123.3106 | 66.6838 | -123.5179 | 123.1236 | 123.4067 | 123.2908 | 66.6324 | -123.6815
719.2812 | 123.7244 | -66.8564 | 56.5704 | 0.047088 | -0.03337 | -0.011218 | 0.028885 | -0.012987 | 0.029097 | 0.065477 | -0.0124 | -0.011804 | 0.032826 | 0.095231 | 0.023568 | -66.8846 | -0.18174 | -66.7826 | 56.5174 | 56.3303 | 56.4542 | -66.9795 | -66.8756 | -0.23773 | -66.9742 | 56.2855 | 56.5686 | 56.4573 | -67.1294 | -0.12308 | -0.05305 | -0.028237 | 0.073753 | 0.19683 | -0.24015 | -0.11624 | -0.27297 | -0.2849 | -0.019205 | -0.11781 | 0.15515 | -0.00183 | -0.11309 | 123.3738 | 123.1867 | 123.3106 | 66.6746 | -123.5499 | 123.1419 | 123.425 | 123.3137 | 66.6187 | -123.6998
720.2656 | 123.6237 | -66.9296 | 56.5659 | 0.047088 | -0.035507 | -0.012287 | 0.027817 | -0.011919 | 0.029097 | 0.050216 | -0.011332 | -0.010735 | 0.032826 | 0.095231 | 0.025704 | -66.9029 | -0.18174 | -66.8101 | 56.4945 | 56.3166 | 56.4496 | -66.9886 | -66.8939 | -0.23773 | -66.9879 | 56.2672 | 56.5594 | 56.4344 | -67.1385 | -0.058992 | -0.071364 | 0.026692 | 0.11952 | 0.17852 | -0.2493 | -0.11624 | -0.20888 | -0.29864 | 0.035723 | -0.058306 | 0.15058 | -0.006409 | -0.13141 | 123.4241 | 123.2462 | 123.3792 | 66.7479 | -123.5545 | 123.1968 | 123.4891 | 123.3641 | 66.6919 | -123.7044
721.2656 | 123.6328 | -66.8884 | 56.575 | 0.031826 | -0.034439 | -0.012287 | 0.024612 | -0.015124 | 0.028029 | 0.050216 | -0.011332 | -0.010735 | 0.033894 | 0.0963 | 0.024636 | -66.8938 | -0.19547 | -66.8009 | 56.5174 | 56.3303 | 56.4542 | -66.9657 | -66.8802 | -0.24231 | -66.9788 | 56.2764 | 56.564 | 56.4528 | -67.1248 | -0.077296 | -0.057627 | -0.005349 | 0.087484 | 0.16478 | -0.24472 | -0.12081 | -0.23634 | -0.29863 | 0.008261 | -0.090346 | 0.146 | -0.010986 | -0.12225 | 123.4058 | 123.2187 | 123.3426 | 66.693 | -123.5407 | 123.1648 | 123.4525 | 123.3412 | 66.6461 | -123.6998
722.2656 | 123.6969 | -66.8884 | 56.543 | 0.06235 | -0.03337 | -0.012287 | 0.02568 | -0.014056 | 0.029097 | 0.050216 | -0.011332 | -0.010735 | 0.032826 | 0.095231 | 0.023568 | -66.8617 | -0.1909 | -66.746 | 56.5494 | 56.3669 | 56.4817 | -66.9428 | -66.8527 | -0.25147 | -66.9376 | 56.3176 | 56.6007 | 56.4757 | -67.0927 | -0.054401 | 0.006465 | 0.026699 | 0.14242 | 0.19682 | -0.17605 | -0.061299 | -0.20429 | -0.22538 | 0.035733 | -0.049138 | 0.15515 | 0.057686 | -0.067313 | 123.4379 | 123.2553 | 123.3701 | 66.6975 | -123.4858 | 123.206 | 123.4891 | 123.3641 | 66.637 | -123.6357
723.2656 | 123.6191 | -66.8884 | 56.5842 | 0.031826 | -0.034439 | -0.012287 | 0.02568 | -0.012987 | 0.029097 | 0.050216 | -0.0124 | -0.008599 | 0.033894 | 0.094163 | 0.025704 | -66.8617 | -0.18632 | -66.7643 | 56.5494 | 56.3578 | 56.4817 | -66.9428 | -66.8573 | -0.25605 | -66.9513 | 56.3084 | 56.5961 | 56.4619 | -67.1019 | -0.054401 | -0.034733 | 0.026699 | 0.12411 | 0.17851 | -0.2264 | -0.1025 | -0.21345 | -0.27574 | 0.031154 | -0.062874 | 0.15058 | 0.011909 | -0.12225 | 123.4379 | 123.2462 | 123.3701 | 66.7021 | -123.527 | 123.1969 | 123.4845 | 123.3503 | 66.6324 | -123.686
724.2812 | 123.6786 | -66.8564 | 56.575 | 0.06235 | -0.03337 | -0.012287 | 0.026749 | -0.014056 | 0.030166 | 0.065477 | -0.010263 | -0.011804 | 0.034962 | 0.0963 | 0.023568 | -66.8617 | -0.20005 | -66.746 | 56.5403 | 56.3623 | 56.4862 | -66.9337 | -66.8573 | -0.26063 | -66.9421 | 56.3084 | 56.5961 | 56.4665 | -67.0973 | -0.077287 | -0.034735 | -0.005345 | 0.11038 | 0.18767 | -0.21267 | -0.088763 | -0.24092 | -0.26658 | -0.00089 | -0.085761 | 0.15515 | 0.021064 | -0.10851 | 123.3967 | 123.2187 | 123.3426 | 66.6563 | -123.5087 | 123.1648 | 123.4525 | 123.3229 | 66.5958 | -123.6723
725.2656 | 123.6557 | -66.8701 | 56.5887 | 0.06235 | -0.035507 | -0.013355 | 0.026749 | -0.014056 | 0.028029 | 0.050216 | -0.0124 | -0.010735 | 0.031758 | 0.095231 | 0.023568 | -66.8526 | -0.20005 | -66.7277 | 56.5494 | 56.3578 | 56.5 | -66.9382 | -66.8435 | -0.26978 | -66.9376 | 56.3176 | 56.5961 | 56.4802 | -67.0927 | -0.068133 | -0.039311 | 0.017545 | 0.14242 | 0.21056 | -0.23098 | -0.088761 | -0.2226 | -0.27116 | 0.026579 | -0.067449 | 0.15515 | 0.007331 | -0.10851 | 123.4196 | 123.2279 | 123.3701 | 66.6701 | -123.527 | 123.1877 | 123.4662 | 123.3504 | 66.6003 | -123.6815
726.2656 | 123.6328 | -66.925 | 56.5521 | 0.047088 | -0.036576 | -0.011218 | 0.026749 | -0.014056 | 0.026961 | 0.050216 | -0.010263 | -0.011804 | 0.032826 | 0.0963 | 0.024636 | -66.8343 | -0.20463 | -66.714 | 56.5632 | 56.3944 | 56.5091 | -66.9108 | -66.8298 | -0.26978 | -66.9193 | 56.3313 | 56.6144 | 56.5031 | -67.079 | 0.014272 | 0.011045 | 0.090791 | 0.21109 | 0.19682 | -0.15773 | -0.042982 | -0.15393 | -0.2208 | 0.095248 | 0.005798 | 0.15973 | 0.062267 | -0.048997 | 123.4882 | 123.3194 | 123.4342 | 66.7204 | -123.4629 | 123.2564 | 123.5394 | 123.4282 | 66.6553 | -123.6311
727.2656 | 123.5962 | -66.8472 | 56.662 | 0.06235 | -0.034439 | -0.013355 | 0.026749 | -0.012987 | 0.029097 | 0.080738 | -0.011332 | -0.009667 | 0.033894 | 0.098436 | 0.025704 | -66.848 | -0.20463 | -66.7231 | 56.554 | 56.3807 | 56.5046 | -66.9337 | -66.8435 | -0.2881 | -66.933 | 56.3267 | 56.6052 | 56.494 | -67.079 | -0.086442 | -0.10798 | -0.000765 | 0.12412 | 0.21056 | -0.28133 | -0.15742 | -0.23175 | -0.33524 | 0.003691 | -0.085758 | 0.146 | -0.056753 | -0.16802 | 123.4012 | 123.2279 | 123.3518 | 66.6426 | -123.5957 | 123.174 | 123.4525 | 123.3412 | 66.5591 | -123.741
728.2656 | 123.555 | -66.8289 | 56.6803 | 0.06235 | -0.035507 | -0.013355 | 0.026749 | -0.014056 | 0.029097 | 0.080738 | -0.0124 | -0.009667 | 0.032826 | 0.094163 | 0.024636 | -66.8205 | -0.21837 | -66.6819 | 56.5861 | 56.399 | 56.5275 | -66.9108 | -66.8161 | -0.27894 | -66.9009 | 56.3496 | 56.6327 | 56.5306 | -67.0607 | -0.081859 | -0.094237 | 0.008395 | 0.14701 | 0.22887 | -0.28133 | -0.15284 | -0.23175 | -0.33066 | 0.012853 | -0.072018 | 0.15973 | -0.047593 | -0.1497 | 123.415 | 123.2279 | 123.3564 | 66.6106 | -123.5911 | 123.1786 | 123.4616 | 123.3595 | 66.55 | -123.741
729.2812 | 123.7198 | -66.8381 | 56.5475 | 0.06235 | -0.036576 | -0.012287 | 0.024612 | -0.015124 | 0.029097 | 0.034955 | -0.0124 | -0.009667 | 0.031758 | 0.098436 | 0.023568 | -66.8572 | -0.21837 | -66.746 | 56.5403 | 56.3486 | 56.4817 | -66.9474 | -66.8527 | -0.2881 | -66.9421 | 56.3038 | 56.6052 | 56.4757 | -67.0973 | -0.10933 | -0.007269 | -0.019076 | 0.092069 | 0.2014 | -0.19894 | -0.065876 | -0.25923 | -0.2437 | -0.014621 | -0.10407 | 0.15515 | 0.057688 | -0.07189 | 123.3784 | 123.1867 | 123.3197 | 66.6197 | -123.495 | 123.1419 | 123.4433 | 123.3137 | 66.55 | -123.6448
730.2656 | 123.6328 | -66.9113 | 56.5704 | 0.047088 | -0.035507 | -0.012287 | 0.02568 | -0.014056 | 0.029097 | 0.065477 | -0.013468 | -0.011804 | 0.032826 | 0.0963 | 0.022499 | -66.8434 | -0.22752 | -66.7277 | 56.5494 | 56.3623 | 56.5 | -66.9337 | -66.839 | -0.30184 | -66.9238 | 56.3176 | 56.6052 | 56.4848 | -67.0836 | -0.022355 | -0.021001 | 0.067901 | 0.18362 | 0.20598 | -0.20809 | -0.070451 | -0.17225 | -0.25285 | 0.072357 | -0.012514 | 0.15973 | 0.034799 | -0.085622 | 123.4607 | 123.2737 | 123.4113 | 66.6838 | -123.5041 | 123.2289 | 123.5165 | 123.3961 | 66.6095 | -123.654
731.2656 | 123.6786 | -66.8701 | 56.543 | 0.047088 | -0.035507 | -0.013355 | 0.026749 | -0.015124 | 0.030166 | 0.050216 | -0.0124 | -0.011804 | 0.031758 | 0.0963 | 0.023568 | -66.8755 | -0.22752 | -66.7552 | 56.5311 | 56.3532 | 56.4771 | -66.9474 | -66.8619 | -0.29726 | -66.9513 | 56.2947 | 56.5869 | 56.4665 | -67.1065 | -0.077291 | -0.011849 | -0.005347 | 0.11496 | 0.19225 | -0.18979 | -0.065878 | -0.23634 | -0.24828 | 0.008265 | -0.081185 | 0.15515 | 0.04395 | -0.076471 | 123.4012 | 123.2233 | 123.3472 | 66.6426 | -123.4904 | 123.1648 | 123.457 | 123.3366 | 66.5729 | -123.6494
732.2656 | 123.6557 | -66.8106 | 56.6528 | 0.047088 | -0.034439 | -0.014424 | 0.02568 | -0.014056 | 0.030166 | 0.050216 | -0.011332 | -0.010735 | 0.032826 | 0.097368 | 0.023568 | -66.8205 | -0.24126 | -66.6865 | 56.5815 | 56.4081 | 56.5229 | -66.9062 | -66.8206 | -0.31557 | -66.8964 | 56.3451 | 56.6373 | 56.5169 | -67.0515 | -0.09559 | -0.071349 | -0.009915 | 0.12412 | 0.21971 | -0.2447 | -0.12995 | -0.2409 | -0.30777 | -0.010036 | -0.08575 | 0.15515 | -0.015548 | -0.13597 | 123.3921 | 123.2187 | 123.3335 | 66.5693 | -123.559 | 123.1557 | 123.4479 | 123.3275 | 66.495 | -123.7043
733.2656 | 123.6282 | -66.8381 | 56.6345 | 0.077612 | -0.036576 | -0.012287 | 0.027817 | -0.010851 | 0.028029 | 0.065477 | -0.0124 | -0.011804 | 0.032826 | 0.098436 | 0.022499 | -66.8297 | -0.24126 | -66.7002 | 56.5769 | 56.399 | 56.5137 | -66.9337 | -66.8298 | -0.32015 | -66.9193 | 56.3359 | 56.6281 | 56.5031 | -67.0652 | -0.095597 | -0.057617 | 0.008394 | 0.13785 | 0.23345 | -0.23555 | -0.1208 | -0.22717 | -0.29862 | 0.008273 | -0.081177 | 0.146 | -0.006394 | -0.13139 | 123.415 | 123.237 | 123.3518 | 66.5968 | -123.5682 | 123.174 | 123.4662 | 123.3412 | 66.5179 | -123.6998
734.2812 | 123.674 | -66.8243 | 56.6071 | 0.047088 | -0.034439 | -0.013355 | 0.026749 | -0.014056 | 0.029097 | 0.034955 | -0.0124 | -0.010735 | 0.032826 | 0.098436 | 0.024636 | -66.8297 | -0.24126 | -66.7048 | 56.5723 | 56.3807 | 56.5137 | -66.9245 | -66.8206 | -0.32931 | -66.9101 | 56.3313 | 56.619 | 56.5031 | -67.0652 | -0.10017 | -0.03473 | -0.005339 | 0.11954 | 0.21971 | -0.2264 | -0.093336 | -0.24091 | -0.27573 | 0.003697 | -0.085753 | 0.15515 | 0.011913 | -0.10393 | 123.3967 | 123.205 | 123.3381 | 66.5831 | -123.5316 | 123.1557 | 123.4433 | 123.3275 | 66.495 | -123.6723
735.2656 | 123.5916 | -66.8015 | 56.6849 | 0.077612 | -0.036576 | -0.012287 | 0.02568 | -0.014056 | 0.029097 | 0.050216 | -0.010263 | -0.009667 | 0.031758 | 0.098436 | 0.023568 | -66.7702 | -0.24584 | -66.6224 | 56.6181 | 56.4356 | 56.5595 | -66.8513 | -66.7703 | -0.32931 | -66.8551 | 56.3863 | 56.6785 | 56.5535 | -67.0057 | -0.049798 | -0.066765 | 0.031292 | 0.17906 | 0.22886 | -0.24927 | -0.12537 | -0.20427 | -0.29861 | 0.031175 | -0.053696 | 0.15057 | -0.006384 | -0.13138 | 123.4196 | 123.2371 | 123.361 | 66.5556 | -123.5361 | 123.1877 | 123.4799 | 123.3549 | 66.4721 | -123.6906
736.2656 | 123.6145 | -66.7923 | 56.6757 | 0.031826 | -0.035507 | -0.013355 | 0.026749 | -0.012987 | 0.028029 | 0.065477 | -0.0124 | -0.010735 | 0.031758 | 0.097368 | 0.022499 | -66.7885 | -0.255 | -66.6453 | 56.609 | 56.4264 | 56.5503 | -66.8925 | -66.7932 | -0.33847 | -66.8735 | 56.3679 | 56.6556 | 56.5443 | -67.0378 | -0.10016 | -0.066767 | 0.003822 | 0.14701 | 0.24718 | -0.24927 | -0.12537 | -0.24548 | -0.30777 | -0.000875 | -0.081167 | 0.16431 | -0.020122 | -0.13139 | 123.4013 | 123.2187 | 123.3426 | 66.5373 | -123.5682 | 123.1602 | 123.4479 | 123.3366 | 66.4538 | -123.7135
737.2656 | 123.6237 | -66.806 | 56.7123 | 0.031826 | -0.036576 | -0.012287 | 0.026749 | -0.014056 | 0.028029 | 0.065477 | -0.013468 | -0.011804 | 0.031758 | 0.097368 | 0.022499 | -66.7839 | -0.26415 | -66.627 | 56.6181 | 56.4356 | 56.5687 | -66.8513 | -66.7749 | -0.3522 | -66.8597 | 56.3817 | 56.6693 | 56.5489 | -67.024 | -0.045221 | -0.094231 | 0.022134 | 0.17906 | 0.22428 | -0.27674 | -0.14368 | -0.21801 | -0.33066 | 0.031173 | -0.053698 | 0.16431 | -0.043007 | -0.16343 | 123.4241 | 123.2416 | 123.3747 | 66.5419 | -123.5636 | 123.1877 | 123.4754 | 123.3549 | 66.4538 | -123.7364
738.2656 | 123.642 | -66.8152 | 56.662 | 0.06235 | -0.035507 | -0.012287 | 0.027817 | -0.016192 | 0.028029 | 0.080738 | -0.010263 | -0.008599 | 0.032826 | 0.097368 | 0.021431 | -66.7747 | -0.26873 | -66.627 | 56.6181 | 56.4402 | 56.5732 | -66.865 | -66.7749 | -0.35678 | -66.8551 | 56.3817 | 56.6739 | 56.5581 | -67.024 | -0.049801 | -0.043877 | 0.040447 | 0.18822 | 0.23802 | -0.2218 | -0.088745 | -0.20885 | -0.2803 | 0.040329 | -0.039963 | 0.16889 | 0.011926 | -0.10392 | 123.4333 | 123.2554 | 123.3884 | 66.5465 | -123.527 | 123.1969 | 123.4891 | 123.3733 | 66.4584 | -123.686
739.2812 | 123.7518 | -66.7603 | 56.662 | 0.047088 | -0.036576 | -0.013355 | 0.02568 | -0.012987 | 0.029097 | 0.065477 | -0.0124 | -0.009667 | 0.030689 | 0.0963 | 0.023568 | -66.7793 | -0.27789 | -66.6361 | 56.6227 | 56.4493 | 56.5732 | -66.865 | -66.7749 | -0.36594 | -66.8414 | 56.3863 | 56.6876 | 56.5489 | -67.0103 | -0.10473 | -0.039299 | -0.019064 | 0.12413 | 0.22886 | -0.21265 | -0.088745 | -0.25005 | -0.27572 | -0.014603 | -0.081159 | 0.16889 | 0.025661 | -0.11307 | 123.3829 | 123.2096 | 123.3335 | 66.4824 | -123.527 | 123.1465 | 123.4479 | 123.3092 | 66.3943 | -123.6723
740.2656 | 123.6008 | -66.7557 | 56.7032 | 0.031826 | -0.037644 | -0.013355 | 0.02568 | -0.014056 | 0.026961 | 0.065477 | -0.011332 | -0.010735 | 0.031758 | 0.097368 | 0.021431 | -66.7473 | -0.28704 | -66.5903 | 56.6547 | 56.4722 | 56.6007 | -66.8329 | -66.7474 | -0.36594 | -66.8185 | 56.4137 | 56.7105 | 56.5718 | -66.9874 | -0.077259 | -0.048449 | 0.008407 | 0.16533 | 0.24259 | -0.23095 | -0.10247 | -0.23173 | -0.28945 | 0.008291 | -0.062843 | 0.16889 | 0.007355 | -0.13138 | 123.4104 | 123.2279 | 123.3564 | 66.4686 | -123.5361 | 123.1694 | 123.4662 | 123.3275 | 66.3897 | -123.6906
741.2656 | 123.5825 | -66.7831 | 56.7307 | 0.047088 | -0.036576 | -0.015492 | 0.02568 | -0.012987 | 0.029097 | 0.050216 | -0.010263 | -0.010735 | 0.031758 | 0.0963 | 0.022499 | -66.7335 | -0.29162 | -66.5629 | 56.6776 | 56.4768 | 56.619 | -66.81 | -66.7291 | -0.37052 | -66.8002 | 56.4366 | 56.7243 | 56.6084 | -66.9737 | -0.026898 | -0.053023 | 0.049608 | 0.22027 | 0.24717 | -0.25384 | -0.11162 | -0.19053 | -0.29402 | 0.054072 | -0.017063 | 0.17346 | -0.006375 | -0.12222 | 123.4608 | 123.26 | 123.4022 | 66.4915 | -123.5407 | 123.2198 | 123.5074 | 123.3916 | 66.4126 | -123.7043
742.2656 | 123.5825 | -66.8106 | 56.7078 | 0.047088 | -0.036576 | -0.013355 | 0.026749 | -0.014056 | 0.029097 | 0.065477 | -0.011332 | -0.010735 | 0.030689 | 0.097368 | 0.022499 | -66.7747 | -0.30536 | -66.6178 | 56.6318 | 56.4539 | 56.587 | -66.8467 | -66.7703 | -0.38883 | -66.8368 | 56.4 | 56.6876 | 56.5764 | -67.0103 | -0.036064 | -0.075919 | 0.035869 | 0.1928 | 0.22886 | -0.25384 | -0.12079 | -0.19969 | -0.30776 | 0.04033 | -0.026226 | 0.17347 | -0.020116 | -0.13138 | 123.4425 | 123.2645 | 123.3976 | 66.5052 | -123.5544 | 123.2106 | 123.4983 | 123.387 | 66.4218 | -123.7181
743.2656 | 123.6008 | -66.774 | 56.7352 | 0.047088 | -0.035507 | -0.014424 | 0.026749 | -0.015124 | 0.028029 | 0.080738 | -0.013468 | -0.011804 | 0.032826 | 0.0963 | 0.022499 | -66.761 | -0.30994 | -66.5995 | 56.641 | 56.4677 | 56.5916 | -66.8467 | -66.7565 | -0.38425 | -66.8185 | 56.4137 | 56.6968 | 56.5718 | -67.0011 | -0.072685 | -0.094227 | 0.012983 | 0.17449 | 0.24717 | -0.26757 | -0.14367 | -0.22716 | -0.32149 | 0.017445 | -0.044532 | 0.18262 | -0.038423 | -0.16342 | 123.415 | 123.2416 | 123.3655 | 66.464 | -123.5819 | 123.1877 | 123.4708 | 123.3458 | 66.3897 | -123.7364
744.2812 | 123.7152 | -66.7648 | 56.6345 | 0.047088 | -0.035507 | -0.013355 | 0.027817 | -0.014056 | 0.028029 | 0.050216 | -0.010263 | -0.011804 | 0.031758 | 0.098436 | 0.022499 | -66.7747 | -0.31452 | -66.6087 | 56.6135 | 56.4448 | 56.5732 | -66.8741 | -66.7749 | -0.39341 | -66.8414 | 56.3954 | 56.6922 | 56.5535 | -67.0149 | -0.10931 | -0.02099 | -0.009907 | 0.15618 | 0.26549 | -0.18976 | -0.061279 | -0.25005 | -0.2391 | -0.010025 | -0.076581 | 0.17347 | 0.057706 | -0.081029 | 123.3784 | 123.2096 | 123.3381 | 66.4503 | -123.5087 | 123.1603 | 123.4571 | 123.3183 | 66.3714 | -123.6494
745.2656 | 123.5916 | -66.9662 | 56.5475 | 0.031826 | -0.036576 | -0.014424 | 0.02568 | -0.015124 | 0.029097 | 0.065477 | -0.013468 | -0.009667 | 0.030689 | 0.098436 | 0.021431 | -66.9716 | -0.32367 | -66.7643 | 56.4441 | 56.2479 | 56.3764 | -67.0481 | -66.9626 | -0.39799 | -67.0291 | 56.1985 | 56.4862 | 56.3703 | -67.2072 | -0.081896 | -0.10341 | -0.005362 | 0.20193 | 0.28383 | -0.29968 | -0.17118 | -0.24094 | -0.349 | 0.003664 | -0.062892 | 0.17805 | -0.061356 | -0.1772 | 123.4104 | 123.2141 | 123.3426 | 66.6426 | -123.5957 | 123.1648 | 123.4524 | 123.3366 | 66.5683 | -123.7547
746.2656 | 123.5596 | -67.099 | 56.4102 | 0.047088 | -0.036576 | -0.013355 | 0.02568 | -0.014056 | 0.028029 | 0.050216 | -0.011332 | -0.011804 | 0.031758 | 0.097368 | 0.023568 | -67.0815 | -0.33283 | -66.9062 | 56.3159 | 56.138 | 56.2665 | -67.1764 | -67.0816 | -0.41173 | -67.1528 | 56.0795 | 56.3671 | 56.2559 | -67.3308 | -0.077355 | -0.094281 | 0.017508 | 0.19275 | 0.27011 | -0.27224 | -0.14374 | -0.23182 | -0.33071 | 0.017369 | -0.053766 | 0.17805 | -0.043071 | -0.15433 | 123.4149 | 123.237 | 123.3655 | 66.7662 | -123.5866 | 123.1785 | 123.4661 | 123.3549 | 66.6873 | -123.741
747.2656 | 123.5733 | -67.4194 | 56.1035 | 0.047088 | -0.036576 | -0.013355 | 0.027817 | -0.016192 | 0.029097 | 0.050216 | -0.0124 | -0.011804 | 0.031758 | 0.098436 | 0.022499 | -67.3425 | -0.34657 | -67.1672 | 56.0595 | 55.877 | 56.0101 | -67.4465 | -67.3426 | -0.42546 | -67.4092 | 55.8185 | 56.1107 | 55.9812 | -67.5918 | -0.027077 | -0.04397 | 0.076974 | 0.25223 | 0.2793 | -0.22654 | -0.093442 | -0.17238 | -0.28499 | 0.076817 | 0.010261 | 0.18264 | 0.007229 | -0.12235 | 123.479 | 123.2964 | 123.4295 | 67.0729 | -123.55 | 123.238 | 123.5302 | 123.4006 | 66.994 | -123.6953
748.2812 | 123.674 | -67.3965 | 56.0257 | 0.077612 | -0.036576 | -0.013355 | 0.02568 | -0.012987 | 0.028029 | 0.065477 | -0.0124 | -0.011804 | 0.032826 | 0.098436 | 0.022499 | -67.4066 | -0.35115 | -67.2359 | 55.9954 | 55.8083 | 55.9414 | -67.4923 | -67.3976 | -0.42546 | -67.4733 | 55.759 | 56.0558 | 55.9354 | -67.6513 | -0.095755 | -0.030247 | -0.010012 | 0.16066 | 0.25642 | -0.21741 | -0.084301 | -0.25479 | -0.26669 | -0.001016 | -0.07673 | 0.17806 | 0.030105 | -0.090316 | 123.392 | 123.2048 | 123.3379 | 67.0454 | -123.518 | 123.1556 | 123.4523 | 123.3319 | 66.9711 | -123.677
749.2812 | 123.6282 | -67.4057 | 56.0806 | 0.031826 | -0.037644 | -0.013355 | 0.027817 | -0.012987 | 0.029097 | 0.065477 | -0.011332 | -0.011804 | 0.031758 | 0.098436 | 0.022499 | -67.4157 | -0.35572 | -67.2038 | 55.9863 | 55.7991 | 55.9277 | -67.506 | -67.4113 | -0.43004 | -67.4824 | 55.7453 | 56.0375 | 55.9171 | -67.6605 | -0.10034 | -0.094335 | -0.010013 | 0.20187 | 0.3022 | -0.28149 | -0.15297 | -0.25479 | -0.33535 | -0.005597 | -0.076731 | 0.17806 | -0.04314 | -0.16356 | 123.392 | 123.2048 | 123.3334 | 67.05 | -123.5867 | 123.151 | 123.4432 | 123.3228 | 66.9757 | -123.7411
750.2656 | 123.6053 | -67.7078 | 55.7648 | 0.06235 | -0.037644 | -0.012287 | 0.027817 | -0.014056 | 0.026961 | 0.080738 | -0.013468 | -0.011804 | 0.029621 | 0.10057 | 0.023568 | -67.4569 | -0.35115 | -67.2313 | 55.9451 | 55.7579 | 55.891 | -67.5656 | -67.4571 | -0.44836 | -67.5053 | 55.7041 | 56.0009 | 55.8804 | -67.7063 | 0.14226 | 0.18032 | 0.25091 | 0.47652 | 0.33426 | -0.006848 | 0.12626 | 0.001544 | -0.060703 | 0.25074 | 0.2025 | 0.20096 | 0.23609 | 0.11567 | 123.6529 | 123.4657 | 123.5989 | 67.3567 | -123.3303 | 123.4119 | 123.7087 | 123.5883 | 67.2595 | -123.4711
751.2656 | 123.6374 | -67.6666 | 55.7922 | 0.06235 | -0.036576 | -0.015492 | 0.02568 | -0.012987 | 0.028029 | 0.065477 | -0.013468 | -0.010735 | 0.031758 | 0.099505 | 0.022499 | -67.6309 | -0.36946 | -67.3915 | 55.7803 | 55.5885 | 55.7262 | -67.7167 | -67.6082 | -0.45293 | -67.661 | 55.5438 | 55.836 | 55.7156 | -67.862 | -0.050041 | -0.011971 | 0.035728 | 0.27508 | 0.32512 | -0.20373 | -0.066035 | -0.19534 | -0.24842 | 0.058444 | 0.005624 | 0.20096 | 0.043792 | -0.076629 | 123.4469 | 123.2551 | 123.3928 | 67.2972 | -123.5089 | 123.2104 | 123.5027 | 123.3822 | 67.2137 | -123.6542
752.2656 | 123.6099 | -68.0786 | 55.4123 | 0.06235 | -0.037644 | -0.014424 | 0.02568 | -0.012987 | 0.028029 | 0.065477 | -0.011332 | -0.011804 | 0.031758 | 0.10057 | 0.021431 | -67.9422 | -0.37862 | -67.7486 | 55.4506 | 55.2817 | 55.4011 | -68.0372 | -67.947 | -0.47125 | -67.9861 | 55.2233 | 55.5155 | 55.3905 | -68.1916 | 0.041421 | 0.038329 | 0.13639 | 0.32997 | 0.28854 | -0.13058 | -0.011172 | -0.11302 | -0.18897 | 0.13161 | 0.092523 | 0.20555 | 0.10323 | -0.021765 | 123.5292 | 123.3603 | 123.4797 | 67.7 | -123.4495 | 123.3019 | 123.5941 | 123.4691 | 67.6074 | -123.6039
753.2812 | 123.7015 | -68.4586 | 54.9774 | 0.047088 | -0.036576 | -0.014424 | 0.026749 | -0.014056 | 0.026961 | 0.095999 | -0.011332 | -0.011804 | 0.031758 | 0.098436 | 0.022499 | -68.3314 | -0.39235 | -68.1241 | 55.0615 | 54.8833 | 55.0165 | -68.4356 | -68.327 | -0.47125 | -68.3799 | 54.8296 | 55.1218 | 54.9876 | -68.59 | 0.022998 | 0.084041 | 0.12717 | 0.33449 | 0.31149 | -0.094068 | 0.0391 | -0.13144 | -0.14784 | 0.13152 | 0.078697 | 0.21013 | 0.14435 | 0.010193 | 123.52 | 123.3419 | 123.4751 | 68.0662 | -123.413 | 123.2881 | 123.5803 | 123.4462 | 67.9873 | -123.5674
754.2812 | 123.6969 | -68.4311 | 54.9866 | 0.031826 | -0.037644 | -0.012287 | 0.026749 | -0.014056 | 0.028029 | 0.080738 | -0.010263 | -0.010735 | 0.029621 | 0.099505 | 0.022499 | -68.4916 | -0.39693 | -68.298 | 54.8921 | 54.7048 | 54.8517 | -68.5867 | -68.4873 | -0.48041 | -68.5355 | 54.6647 | 54.9478 | 54.8365 | -68.7503 | -0.15557 | -0.094515 | -0.060544 | 0.13305 | 0.28862 | -0.2818 | -0.13489 | -0.31916 | -0.32182 | -0.056203 | -0.10444 | 0.21472 | -0.038792 | -0.15006 | 123.3231 | 123.1359 | 123.2828 | 68.0342 | -123.5732 | 123.0958 | 123.3789 | 123.2676 | 67.9507 | -123.7368
755.2656 | 123.6374 | -68.3304 | 55.1285 | 0.047088 | -0.038712 | -0.014424 | 0.022475 | -0.014056 | 0.029097 | 0.080738 | -0.011332 | -0.011804 | 0.029621 | 0.098436 | 0.021431 | -68.3543 | -0.39693 | -68.1561 | 55.0431 | 54.8559 | 54.9845 | -68.4493 | -68.3499 | -0.49414 | -68.389 | 54.8113 | 55.0943 | 54.983 | -68.5946 | -0.11891 | -0.085335 | -0.0239 | 0.17427 | 0.29318 | -0.2726 | -0.14401 | -0.26419 | -0.31722 | -0.01955 | -0.058634 | 0.20556 | -0.034184 | -0.14545 | 123.3735 | 123.1863 | 123.3149 | 67.9335 | -123.5778 | 123.1416 | 123.4247 | 123.3134 | 67.8362 | -123.7231
756.2656 | 123.6328 | -69.0491 | 54.4189 | 0.047088 | -0.037644 | -0.014424 | 0.026749 | -0.016192 | 0.026961 | 0.065477 | -0.0124 | -0.012872 | 0.030689 | 0.10057 | 0.022499 | -69.1509 | -0.40609 | -68.9527 | 54.2419 | 54.0591 | 54.1924 | -69.2598 | -69.1512 | -0.49872 | -69.204 | 54.0054 | 54.2885 | 54.1818 | -69.405 | -0.21069 | -0.17702 | -0.10185 | 0.096336 | 0.30703 | -0.3598 | -0.22658 | -0.35595 | -0.4135 | -0.10214 | -0.15496 | 0.201 | -0.13048 | -0.23717 | 123.291 | 123.1082 | 123.2414 | 68.643 | -123.6787 | 123.0545 | 123.3375 | 123.2308 | 68.5504 | -123.824
757.2656 | 123.6374 | -69.9326 | 53.5309 | 0.077612 | -0.037644 | -0.011218 | 0.024612 | -0.014056 | 0.025892 | 0.065477 | -0.011332 | -0.010735 | 0.031758 | 0.10057 | 0.022499 | -69.6179 | -0.4244 | -69.406 | 53.7704 | 53.5921 | 53.7208 | -69.7268 | -69.632 | -0.51704 | -69.6756 | 53.5247 | 53.8214 | 53.6964 | -69.8904 | 0.20574 | 0.23947 | 0.31464 | 0.52657 | 0.32083 | 0.061208 | 0.18989 | 0.042179 | -0.00618 | 0.30058 | 0.25692 | 0.21474 | 0.29056 | 0.16556 | 123.7029 | 123.5246 | 123.6533 | 69.5082 | -123.2577 | 123.4573 | 123.754 | 123.629 | 69.4155 | -123.4213
758.2812 | 123.6969 | -91.951 | 31.4209 | 0.031826 | -0.037644 | -0.013355 | 0.032091 | -0.015124 | 0.026961 | 0.065477 | -0.010263 | -0.010735 | 0.031758 | 0.10057 | 0.022499 | -91.1775 | -0.65333 | -90.9651 | 32.0001 | 31.8285 | 32.0182 | -91.5408 | -91.2755 | -0.80092 | -91.2963 | 31.7769 | 32.0639 | 31.8886 | -91.6077 | 0.41018 | 0.57922 | 0.77344 | 0.98588 | 0.5757 | 0.40756 | 0.5973 | 0.34328 | 0.35595 | 0.67546 | 0.65469 | 0.31141 | 0.64303 | 0.46766 | 123.9511 | 123.7795 | 123.9692 | 91.2977 | -122.9617 | 123.7278 | 124.0149 | 123.8395 | 91.1501 | -123.0286
759.2812 | 123.5962 | -84.05 | 39.4547 | 0.047088 | -0.038712 | -0.01656 | 0.031022 | -0.014056 | 0.026961 | 0.080738 | -0.013468 | -0.011804 | 0.030689 | 0.10057 | 0.023568 | -94.3137 | -0.66249 | -94.1653 | 28.8639 | 28.7377 | 28.891 | -94.6682 | -94.3616 | -0.80549 | -94.3824 | 28.6909 | 28.9734 | 28.8301 | -94.7396 | -10.6182 | -10.5907 | -10.2638 | -10.1153 | 0.50289 | -10.717 | -10.5636 | -10.6896 | -10.7637 | -10.3116 | -10.3324 | 0.35726 | -10.4813 | -10.6246 | 112.9139 | 112.7877 | 112.941 | 83.3875 | -134.1229 | 112.7409 | 113.0234 | 112.88 | 83.2445 | -134.1943
760.2656 | 123.6557 | -99.7971 | 23.6847 | 0.047088 | -0.037644 | -0.014424 | 0.035296 | -0.015124 | 0.028029 | 0.065477 | -0.0124 | -0.010735 | 0.029621 | 0.10057 | 0.022499 | -99.5468 | -0.80901 | -99.4349 | 23.672 | 23.4857 | 23.6531 | -100.0347 | -99.6317 | -0.96575 | -99.6387 | 23.5539 | 23.6897 | 23.5189 | -100.0419 | -0.23766 | -0.012661 | 0.25022 | 0.36213 | 0.59979 | -0.19903 | -0.031602 | -0.24483 | -0.13082 | 0.16538 | 0.15835 | 0.40318 | 0.004968 | -0.16582 | 123.4691 | 123.2827 | 123.4501 | 98.9881 | -123.7194 | 123.3509 | 123.4867 | 123.3159 | 98.8313 | -123.7266
761.2656 | 123.6282 | -102.3697 | 21.1487 | 0.06235 | -0.038712 | -0.014424 | 0.033159 | -0.014056 | 0.029097 | 0.065477 | -0.011332 | -0.011804 | 0.032826 | 0.099505 | 0.021431 | -101.804 | -0.84106 | -101.6646 | 21.3508 | 21.3702 | 21.4874 | -102.2921 | -101.889 | -1.0115 | -101.8914 | 21.3379 | 21.4324 | 21.2799 | -102.3038 | 0.077563 | 0.20211 | 0.56571 | 0.70514 | 0.62758 | 0.22152 | 0.33873 | 0.065866 | 0.1892 | 0.48071 | 0.47825 | 0.41239 | 0.28373 | 0.13126 | 123.7205 | 123.7399 | 123.8571 | 101.5286 | -123.4408 | 123.7076 | 123.8021 | 123.6496 | 101.3582 | -123.4525
762.2656 | 123.5733 | -103.4821 | 20.05 | 0.06235 | -0.037644 | -0.013355 | 0.034227 | -0.012987 | 0.026961 | 0.065477 | -0.010263 | -0.010735 | 0.031758 | 0.10057 | 0.022499 | -103.2187 | -0.85021 | -103.1113 | 19.9223 | 19.9507 | 20.0635 | -103.6063 | -103.3084 | -0.96117 | -103.2925 | 19.9185 | 20.013 | 20.0666 | -103.737 | -0.12422 | -0.12772 | 0.26335 | 0.37077 | 0.49499 | -0.099316 | 0.013417 | -0.25494 | -0.1315 | 0.17367 | 0.18953 | 0.44447 | -0.037007 | 0.016559 | 123.4044 | 123.4328 | 123.5455 | 102.6318 | -123.6563 | 123.4006 | 123.4951 | 123.5487 | 102.5209 | -123.787
763.2812 | 123.5825 | -104.4479 | 19.0796 | 0.047088 | -0.039781 | -0.014424 | 0.034227 | -0.014056 | 0.026961 | 0.050216 | -0.011332 | -0.009667 | 0.030689 | 0.10057 | 0.021431 | -104.258 | -0.86395 | -104.1506 | 18.883 | 18.893 | 19.0287 | -104.6411 | -104.334 | -0.97033 | -104.3319 | 18.8747 | 18.9829 | 18.8212 | -104.7764 | -0.19318 | -0.19655 | 0.18994 | 0.29738 | 0.49056 | -0.18659 | -0.050889 | -0.32845 | -0.20494 | 0.11392 | 0.11605 | 0.4445 | -0.096733 | -0.25836 | 123.331 | 123.3409 | 123.4766 | 103.584 | -123.7207 | 123.3226 | 123.4308 | 123.2692 | 103.4776 | -123.856
764.2812 | 123.5504 | -104.068 | 19.4687 | 0.047088 | -0.040849 | -0.014424 | 0.034227 | -0.016192 | 0.029097 | 0.050216 | -0.013468 | -0.011804 | 0.030689 | 0.10164 | 0.021431 | -103.8139 | -0.79527 | -103.7065 | 19.3317 | 19.2089 | 19.4591 | -104.197 | -103.8945 | -0.97033 | -103.8511 | 19.3233 | 19.4178 | 19.2654 | -104.3368 | -0.12897 | -0.13697 | 0.2541 | 0.36153 | 0.4905 | -0.25974 | -0.009599 | -0.26883 | -0.14534 | 0.17354 | 0.21687 | 0.48569 | -0.050865 | -0.20334 | 123.3997 | 123.2769 | 123.5271 | 103.2727 | -123.6656 | 123.3913 | 123.4858 | 123.3333 | 103.0977 | -123.8055
765.2656 | 123.6191 | -104.1412 | 19.4366 | 0.077612 | -0.038712 | -0.013355 | 0.033159 | -0.014056 | 0.026961 | 0.065477 | -0.013468 | -0.011804 | 0.030689 | 0.10057 | 0.020363 | -103.8322 | -0.80443 | -103.7156 | 19.3042 | 19.3372 | 19.3538 | -104.3389 | -103.9128 | -0.97033 | -103.9152 | 19.2959 | 19.3949 | 19.4485 | -104.3551 | -0.19767 | -0.1324 | 0.30902 | 0.42561 | 0.62329 | -0.099489 | -0.082864 | -0.2139 | -0.14077 | 0.22846 | 0.22601 | 0.43991 | -0.041715 | 0.011851 | 123.4455 | 123.4784 | 123.495 | 103.3368 | -123.7756 | 123.4371 | 123.5362 | 123.5897 | 103.1709 | -123.7918
766.2656 | 123.6099 | -103.9032 | 19.6426 | 0.047088 | -0.039781 | -0.013355 | 0.033159 | -0.014056 | 0.026961 | 0.080738 | -0.014536 | -0.010735 | 0.029621 | 0.10164 | 0.021431 | -103.585 | -0.79985 | -103.4318 | 19.5652 | 19.4379 | 19.6102 | -103.9726 | -103.6655 | -0.98864 | -103.6359 | 19.5614 | 19.6559 | 19.5172 | -104.0987 | -0.069394 | -0.077422 | 0.31822 | 0.47143 | 0.54083 | -0.20474 | -0.032455 | -0.19552 | -0.081212 | 0.23768 | 0.26727 | 0.46279 | 0.013272 | -0.12546 | 123.4684 | 123.3411 | 123.5134 | 103.1033 | -123.6152 | 123.4646 | 123.5591 | 123.4204 | 102.9146 | -123.7414
767.2656 | 123.5962 | -95.4163 | 28.0243 | 0.047088 | -0.039781 | -0.014424 | 0.031022 | -0.012987 | 0.028029 | 0.065477 | -0.014536 | -0.012872 | 0.029621 | 0.10164 | 0.021431 | -86.709 | -0.71286 | -86.3868 | 36.7113 | 36.4028 | 36.7662 | -86.9207 | -86.912 | -0.8696 | -86.8641 | 36.3187 | 36.6746 | 36.4031 | -87.1159 | 8.4956 | 8.687 | 8.7072 | 9.0294 | 0.53385 | 8.3785 | 8.7419 | 8.3004 | 8.2944 | 8.5042 | 8.5521 | 0.25178 | 8.6503 | 8.3788 | 132.1275 | 131.8191 | 132.1825 | 94.7034 | -114.945 | 131.735 | 132.0908 | 131.8193 | 94.5467 | -115.1402
768.2656 | 123.6099 | -103.9398 | 19.5786 | 0.047088 | -0.038712 | -0.013355 | 0.034227 | -0.014056 | 0.026961 | 0.050216 | -0.0124 | -0.011804 | 0.030689 | 0.10057 | 0.022499 | -103.7132 | -0.80901 | -103.5188 | 19.4279 | 19.2959 | 19.4774 | -104.2107 | -103.7937 | -1.007 | -103.787 | 19.2547 | 19.5231 | 19.3707 | -104.2361 | -0.27088 | -0.15069 | 0.22665 | 0.42106 | 0.69194 | -0.2826 | -0.10115 | -0.29627 | -0.32388 | 0.14609 | 0.1528 | 0.44906 | -0.05542 | -0.20789 | 123.3677 | 123.2358 | 123.4172 | 103.1308 | -123.7892 | 123.1945 | 123.463 | 123.3105 | 102.9329 | -123.8146
769.2812 | 123.6465 | -103.5507 | 19.9722 | 0.031826 | -0.039781 | -0.014424 | 0.033159 | -0.014056 | 0.026961 | 0.065477 | -0.015604 | -0.009667 | 0.030689 | 0.10164 | 0.022499 | -103.2828 | -0.80443 | -103.0701 | 19.8582 | 19.7309 | 19.8941 | -103.6841 | -103.3816 | -1.0024 | -103.3566 | 19.6713 | 19.9444 | 19.7782 | -103.8148 | -0.1334 | -0.11399 | 0.26792 | 0.48064 | 0.61404 | -0.24128 | -0.078172 | -0.26411 | -0.30092 | 0.16908 | 0.1941 | 0.45821 | -0.027866 | -0.19407 | 123.409 | 123.2817 | 123.4448 | 102.7463 | -123.6563 | 123.222 | 123.4951 | 123.3289 | 102.5483 | -123.7871
770.2656 | 123.5733 | -103.1296 | 20.3842 | 0.06235 | -0.038712 | -0.014424 | 0.034227 | -0.014056 | 0.028029 | 0.095999 | -0.013468 | -0.011804 | 0.030689 | 0.10164 | 0.020363 | -103.0173 | -0.80901 | -102.7908 | 20.1329 | 19.9874 | 20.1688 | -103.3956 | -103.1023 | -1.0161 | -103.0773 | 19.946 | 20.2145 | 20.0666 | -103.5401 | -0.26607 | -0.25128 | 0.11232 | 0.33877 | 0.60484 | -0.39685 | -0.21544 | -0.41053 | -0.4382 | 0.027237 | 0.052255 | 0.46278 | -0.16972 | -0.31761 | 123.2625 | 123.1169 | 123.2984 | 102.3206 | -123.7799 | 123.0756 | 123.3441 | 123.1962 | 102.1135 | -123.9243
771.2656 | 123.5916 | -103.0426 | 20.4803 | 0.06235 | -0.039781 | -0.013355 | 0.035296 | -0.014056 | 0.025892 | 0.050216 | -0.015604 | -0.011804 | 0.030689 | 0.10378 | 0.020363 | -102.7838 | -0.81816 | -102.539 | 20.3573 | 20.23 | 20.4023 | -103.1667 | -102.8642 | -1.0115 | -102.8621 | 20.1749 | 20.4572 | 20.2681 | -103.2974 | -0.1241 | -0.12307 | 0.25884 | 0.5036 | 0.6277 | -0.2503 | -0.078065 | -0.25482 | -0.3054 | 0.17835 | 0.18048 | 0.4353 | -0.02318 | -0.21228 | 123.3999 | 123.2727 | 123.4449 | 102.2244 | -123.647 | 123.2175 | 123.4998 | 123.3107 | 102.0311 | -123.7778
772.3125 | 123.587 | -103.3813 | 20.1508 | 0.047088 | -0.039781 | -0.013355 | 0.034227 | -0.016192 | 0.028029 | 0.065477 | -0.0124 | -0.009667 | 0.029621 | 0.10271 | 0.021431 | -102.6556 | -0.81359 | -102.42 | 20.4809 | 20.3399 | 20.5213 | -103.0431 | -102.7406 | -1.0207 | -102.711 | 20.2986 | 20.5762 | 20.41 | -103.1692 | 0.33828 | 0.33014 | 0.72578 | 0.96138 | 0.6231 | 0.18919 | 0.37057 | 0.21213 | 0.14781 | 0.64073 | 0.67032 | 0.45819 | 0.42545 | 0.25925 | 123.8622 | 123.7213 | 123.9027 | 102.5678 | -123.1938 | 123.6799 | 123.9576 | 123.7914 | 102.3607 | -123.32
773.2656 | 123.6008 | -104.0817 | 19.4641 | 0.031826 | -0.039781 | -0.012287 | 0.034227 | -0.014056 | 0.028029 | 0.080738 | -0.013468 | -0.010735 | 0.030689 | 0.10271 | 0.021431 | -103.7727 | -0.82732 | -103.5096 | 19.3775 | 19.2547 | 19.4133 | -104.1603 | -103.8624 | -1.0527 | -103.8191 | 19.1906 | 19.4636 | 19.3157 | -104.2956 | -0.078602 | -0.086608 | 0.30903 | 0.57213 | 0.65073 | -0.20937 | -0.050807 | -0.21388 | -0.27354 | 0.21932 | 0.26265 | 0.47653 | -0.000501 | -0.14839 | 123.4592 | 123.3365 | 123.495 | 103.2544 | -123.6244 | 123.2723 | 123.5453 | 123.3974 | 103.029 | -123.7597
774.7969 | 123.6603 | -103.2761 | 20.2057 | 0.047088 | -0.038712 | -0.013355 | 0.033159 | -0.014056 | 0.028029 | 0.050216 | -0.013468 | -0.011804 | 0.029621 | 0.10271 | 0.021431 | -103.3927 | -0.82732 | -103.1159 | 19.7346 | 19.6165 | 19.7796 | -103.7894 | -103.4732 | -1.0482 | -103.4482 | 19.566 | 19.8253 | 19.6912 | -103.9247 | -0.51337 | -0.47107 | -0.11662 | 0.1602 | 0.67357 | -0.58922 | -0.4261 | -0.64866 | -0.63968 | -0.19715 | -0.17214 | 0.47653 | -0.38037 | -0.51452 | 123.0107 | 122.8925 | 123.0557 | 102.4487 | -123.9951 | 122.8421 | 123.1014 | 122.9672 | 102.2279 | -124.1304
775.3594 | 123.5733 | -103.3356 | 20.2148 | 0.047088 | -0.039781 | -0.014424 | 0.034227 | -0.015124 | 0.028029 | 0.065477 | -0.0124 | -0.010735 | 0.030689 | 0.10378 | 0.021431 | -103.118 | -0.83648 | -102.8183 | 20.0185 | 19.8958 | 20.0589 | -103.5055 | -103.2077 | -1.0573 | -103.1689 | 19.8453 | 20.1092 | 19.9613 | -103.6546 | -0.16997 | -0.19637 | 0.21759 | 0.51729 | 0.68727 | -0.31906 | -0.15596 | -0.319 | -0.36955 | 0.12792 | 0.16667 | 0.48568 | -0.10565 | -0.25354 | 123.354 | 123.2314 | 123.3945 | 102.4991 | -123.7204 | 123.1809 | 123.4448 | 123.2969 | 102.2782 | -123.8694
776.2656 | 123.7015 | -103.1342 | 20.3568 | 0.047088 | -0.040849 | -0.014424 | 0.035296 | -0.015124 | 0.026961 | 0.080738 | -0.013468 | -0.010735 | 0.028553 | 0.10164 | 0.021431 | -102.8387 | -0.8319 | -102.5482 | 20.2978 | 20.1797 | 20.3473 | -103.2262 | -102.9283 | -1.0665 | -102.8896 | 20.1063 | 20.3885 | 20.2498 | -103.3615 | -0.092072 | -0.058991 | 0.29545 | 0.586 | 0.67807 | -0.17707 | -0.009411 | -0.22738 | -0.25048 | 0.20581 | 0.24456 | 0.47194 | 0.031738 | -0.107 | 123.4319 | 123.3138 | 123.4815 | 102.3023 | -123.583 | 123.2404 | 123.5226 | 123.3839 | 102.0677 | -123.7183
777.2656 | 123.5779 | -102.8 | 20.6955 | 0.077612 | -0.040849 | -0.014424 | 0.033159 | -0.014056 | 0.028029 | 0.065477 | -0.011332 | -0.010735 | 0.030689 | 0.10271 | 0.022499 | -102.5777 | -0.84564 | -102.246 | 20.5679 | 20.4407 | 20.6083 | -102.9652 | -102.6674 | -1.0756 | -102.6103 | 20.381 | 20.6495 | 20.4924 | -103.1051 | -0.16524 | -0.12761 | 0.22226 | 0.554 | 0.71924 | -0.25482 | -0.087177 | -0.30513 | -0.31452 | 0.13263 | 0.18969 | 0.49482 | -0.046028 | -0.20308 | 123.3679 | 123.2407 | 123.4083 | 101.9544 | -123.6607 | 123.181 | 123.4495 | 123.2924 | 101.7244 | -123.8006
778.2656 | 123.6328 | -101.9531 | 21.524 | 0.077612 | -0.040849 | -0.013355 | 0.034227 | -0.014056 | 0.028029 | 0.080738 | -0.014536 | -0.010735 | 0.029621 | 0.10378 | 0.021431 | -102.6006 | -0.84106 | -102.2094 | 20.5404 | 20.4178 | 20.5763 | -102.9698 | -102.6765 | -1.0756 | -102.6332 | 20.3581 | 20.6357 | 20.497 | -103.1143 | -1.0167 | -0.98363 | -0.6475 | -0.25624 | 0.76044 | -1.1063 | -0.94778 | -1.1612 | -1.166 | -0.7234 | -0.68006 | 0.48109 | -0.88832 | -1.0271 | 122.4935 | 122.3709 | 122.5294 | 101.1121 | -124.4939 | 122.3112 | 122.5889 | 122.4501 | 100.8775 | -124.6383
779.2969 | 123.6008 | -103.2394 | 20.2972 | 0.06235 | -0.038712 | -0.012287 | 0.032091 | -0.014056 | 0.028029 | 0.065477 | -0.011332 | -0.009667 | 0.030689 | 0.10378 | 0.019295 | -102.6006 | -0.85937 | -102.2643 | 20.5541 | 20.4269 | 20.5992 | -102.9698 | -102.6811 | -1.0848 | -102.6378 | 20.3672 | 20.6403 | 20.4878 | -103.1143 | 0.26963 | 0.25691 | 0.63882 | 0.97514 | 0.7055 | 0.1297 | 0.30192 | 0.12517 | 0.070001 | 0.55834 | 0.60167 | 0.47651 | 0.34307 | 0.1906 | 123.7936 | 123.6664 | 123.8386 | 102.3801 | -123.267 | 123.6067 | 123.8798 | 123.7273 | 102.1546 | -123.4115
780.2656 | 123.587 | -102.5665 | 20.961 | 0.077612 | -0.040849 | -0.013355 | 0.033159 | -0.012987 | 0.026961 | 0.080738 | -0.0124 | -0.011804 | 0.029621 | 0.10164 | 0.021431 | -102.5732 | -0.86395 | -102.3147 | 20.5725 | 20.4498 | 20.6129 | -102.9561 | -102.6536 | -1.0985 | -102.624 | 20.3856 | 20.6678 | 20.5245 | -103.0914 | -0.38954 | -0.38854 | -0.006626 | 0.25186 | 0.6414 | -0.51116 | -0.3481 | -0.52485 | -0.57544 | -0.087099 | -0.057503 | 0.46735 | -0.29322 | -0.43653 | 123.139 | 123.0164 | 123.1794 | 101.7026 | -123.9171 | 122.9521 | 123.2343 | 123.091 | 101.468 | -124.0524
781.2656 | 123.6374 | -102.6215 | 20.9015 | 0.077612 | -0.040849 | -0.013355 | 0.033159 | -0.014056 | 0.025892 | 0.095999 | -0.0124 | -0.010735 | 0.030689 | 0.10164 | 0.021431 | -102.3809 | -0.87769 | -102.1041 | 20.7648 | 20.6376 | 20.8144 | -102.7638 | -102.4613 | -1.1077 | -102.4271 | 20.5824 | 20.8509 | 20.7122 | -102.9036 | -0.1423 | -0.13674 | 0.2406 | 0.51739 | 0.65969 | -0.26392 | -0.087133 | -0.28219 | -0.31906 | 0.16014 | 0.19431 | 0.4765 | -0.050562 | -0.1893 | 123.3862 | 123.259 | 123.4358 | 101.7438 | -123.6652 | 123.2039 | 123.4724 | 123.3337 | 101.5138 | -123.8051
782.2656 | 123.7015 | -103.0838 | 20.3659 | 0.06235 | -0.040849 | -0.015492 | 0.033159 | -0.014056 | 0.028029 | 0.065477 | -0.0124 | -0.011804 | 0.030689 | 0.10164 | 0.019295 | -102.6739 | -0.88684 | -102.3971 | 20.4763 | 20.3537 | 20.5122 | -103.0522 | -102.7635 | -1.126 | -102.7248 | 20.2894 | 20.5533 | 20.4192 | -103.1967 | 0.031573 | 0.11041 | 0.40992 | 0.68673 | 0.65515 | -0.012227 | 0.14626 | -0.11289 | -0.076499 | 0.32028 | 0.35904 | 0.47193 | 0.18741 | 0.053255 | 123.5601 | 123.4375 | 123.596 | 102.197 | -123.4181 | 123.3732 | 123.6371 | 123.503 | 101.9578 | -123.5626
783.2656 | 123.7289 | -79.8798 | 43.634 | 0.077612 | -0.039781 | -0.013355 | 0.027817 | -0.011919 | 0.028029 | 0.080738 | -0.0124 | -0.010735 | 0.029621 | 0.10378 | 0.019295 | -82.6617 | -0.59839 | -82.5273 | 40.4701 | 40.4506 | 40.4062 | -82.937 | -82.6355 | -0.77802 | -82.5922 | 40.3936 | 40.6076 | 40.6154 | -83.0499 | -3.0573 | -3.1639 | -2.782 | -2.6476 | 0.40967 | -3.1835 | -3.2278 | -3.1701 | -3.2405 | -2.7557 | -2.7124 | 0.45772 | -3.0264 | -3.0187 | 120.3499 | 120.3303 | 120.286 | 79.2814 | -126.571 | 120.2733 | 120.4874 | 120.4951 | 79.1017 | -126.6839
784.2812 | 123.5413 | -68.4998 | 55.0369 | 0.06235 | -0.041917 | -0.012287 | 0.026749 | -0.015124 | 0.028029 | 0.065477 | -0.0124 | -0.011804 | 0.031758 | 0.10485 | 0.020363 | -78.9395 | -0.46103 | -79.1074 | 43.9589 | 44.2007 | 43.8264 | -79.3334 | -78.7665 | -0.64524 | -78.7186 | 44.1434 | 44.2384 | 44.4751 | -79.3182 | -10.8336 | -11.0781 | -10.4398 | -10.6076 | 0.22604 | -10.8362 | -11.2105 | -10.8184 | -10.8936 | -10.2667 | -10.2188 | 0.59958 | -10.7985 | -10.5618 | 112.4586 | 112.7005 | 112.3262 | 68.0387 | -134.3703 | 112.6431 | 112.7382 | 112.9749 | 67.8545 | -134.3551
785.2812 | 123.7244 | -68.7881 | 54.6249 | 0.047088 | -0.039781 | -0.014424 | 0.02568 | -0.012987 | 0.028029 | 0.080738 | -0.011332 | -0.012872 | 0.029621 | 0.10271 | 0.021431 | -68.8533 | -0.49766 | -68.5911 | 54.5166 | 54.3385 | 54.4671 | -68.9805 | -68.9314 | -0.6544 | -68.8469 | 54.2893 | 54.5769 | 54.4519 | -69.1349 | -0.1923 | -0.10831 | -0.06518 | 0.19709 | 0.3894 | -0.28648 | -0.15785 | -0.34673 | -0.33563 | -0.14328 | -0.058741 | 0.28798 | -0.048026 | -0.17303 | 123.3048 | 123.1266 | 123.2552 | 68.2905 | -123.6054 | 123.0775 | 123.3651 | 123.2401 | 68.1337 | -123.7598
786.2656 | 123.6237 | -102.7542 | 20.6818 | 0.06235 | -0.041917 | -0.014424 | 0.034227 | -0.014056 | 0.025892 | 0.065477 | -0.013468 | -0.010735 | 0.028553 | 0.10271 | 0.020363 | -102.4175 | -0.93263 | -102.2872 | 20.8197 | 20.7566 | 20.8601 | -102.9194 | -102.5117 | -1.1901 | -102.4546 | 20.7061 | 20.8097 | 20.8587 | -102.9494 | -0.16523 | 0.13793 | 0.33672 | 0.46701 | 0.63224 | 0.074861 | 0.17838 | -0.19523 | 0.024287 | 0.24252 | 0.29959 | 0.49482 | 0.12796 | 0.17694 | 123.5739 | 123.5108 | 123.6144 | 101.8216 | -123.6012 | 123.4603 | 123.5639 | 123.6129 | 101.5641 | -123.6312
787.3281 | 123.6374 | -69.1956 | 54.2908 | 0.031826 | -0.040849 | -0.014424 | 0.024612 | -0.015124 | 0.025892 | 0.034955 | -0.0124 | -0.010735 | 0.030689 | 0.10485 | 0.019295 | -69.2288 | -0.52055 | -68.9939 | 54.1458 | 53.9767 | 54.1008 | -69.3605 | -69.3023 | -0.68187 | -69.2178 | 53.9139 | 54.2106 | 54.0673 | -69.5012 | -0.16494 | -0.14499 | -0.033198 | 0.20162 | 0.36656 | -0.31405 | -0.18997 | -0.30562 | -0.37689 | -0.10675 | -0.022206 | 0.28341 | -0.080146 | -0.22346 | 123.3413 | 123.1723 | 123.2964 | 68.675 | -123.6513 | 123.1094 | 123.4062 | 123.2629 | 68.5137 | -123.7919
788.3125 | 123.6786 | -69.8502 | 53.5538 | 0.031826 | -0.040849 | -0.01656 | 0.022475 | -0.012987 | 0.025892 | 0.050216 | -0.0124 | -0.010735 | 0.029621 | 0.10271 | 0.021431 | -69.9796 | -0.53429 | -69.7036 | 53.3766 | 53.2029 | 53.3453 | -70.1023 | -69.9891 | -0.7185 | -69.9733 | 53.1447 | 53.4414 | 53.2752 | -70.2613 | -0.25213 | -0.17716 | -0.12945 | 0.14659 | 0.39871 | -0.35089 | -0.20845 | -0.4111 | -0.40908 | -0.13895 | -0.12309 | 0.28801 | -0.11235 | -0.27856 | 123.2268 | 123.053 | 123.1955 | 69.3159 | -123.6561 | 122.9948 | 123.2916 | 123.1254 | 69.1317 | -123.815
789.2812 | 123.674 | -71.4569 | 51.9516 | 0.031826 | -0.042986 | -0.015492 | 0.024612 | -0.015124 | 0.023756 | 0.050216 | -0.011332 | -0.010735 | 0.029621 | 0.10378 | 0.020363 | -71.1425 | -0.56634 | -70.8436 | 52.2183 | 52.0444 | 52.1732 | -71.2653 | -71.1475 | -0.75055 | -71.1317 | 51.9818 | 52.2739 | 52.1489 | -71.4334 | 0.19158 | 0.26668 | 0.31439 | 0.61334 | 0.42177 | 0.092816 | 0.22161 | 0.023471 | 0.030152 | 0.30938 | 0.32524 | 0.30177 | 0.32228 | 0.19728 | 123.6752 | 123.5013 | 123.6301 | 70.8906 | -123.2169 | 123.4387 | 123.7308 | 123.6058 | 70.7064 | -123.385
790.2812 | 123.5962 | -71.8552 | 51.6357 | 0.06235 | -0.040849 | -0.01656 | 0.024612 | -0.012987 | 0.026961 | 0.080738 | -0.011332 | -0.010735 | 0.028553 | 0.10485 | 0.019295 | -71.6919 | -0.5755 | -71.3792 | 51.6597 | 51.4949 | 51.6192 | -71.8423 | -71.7015 | -0.77344 | -71.672 | 51.4415 | 51.7244 | 51.5903 | -71.9783 | 0.012886 | 0.023974 | 0.16324 | 0.47594 | 0.46305 | -0.1408 | -0.016548 | -0.12315 | -0.19425 | 0.15362 | 0.18321 | 0.30637 | 0.088701 | -0.045455 | 123.5149 | 123.3501 | 123.4744 | 71.2797 | -123.478 | 123.2967 | 123.5796 | 123.4455 | 71.0817 | -123.6141
791.2656 | 123.7244 | -71.9101 | 51.4893 | 0.06235 | -0.040849 | -0.015492 | 0.026749 | -0.014056 | 0.025892 | 0.065477 | -0.011332 | -0.011804 | 0.027485 | 0.10378 | 0.020363 | -72.136 | -0.60297 | -71.8004 | 51.1973 | 51.0371 | 51.1568 | -72.2864 | -72.1503 | -0.80092 | -72.1298 | 50.9791 | 51.2666 | 51.1416 | -72.4499 | -0.37634 | -0.29196 | -0.22594 | 0.10967 | 0.48601 | -0.45221 | -0.3325 | -0.53984 | -0.5102 | -0.24017 | -0.21973 | 0.32011 | -0.22268 | -0.34767 | 123.1074 | 122.9471 | 123.0668 | 71.3071 | -123.7757 | 122.8892 | 123.1767 | 123.0517 | 71.1092 | -123.9392
792.3281 | 123.7335 | -72.7249 | 50.6699 | 0.047088 | -0.040849 | -0.015492 | 0.02568 | -0.015124 | 0.026961 | 0.065477 | -0.011332 | -0.011804 | 0.029621 | 0.10378 | 0.019295 | -72.69 | -0.61213 | -72.3452 | 50.6525 | 50.4784 | 50.6165 | -72.8359 | -72.6951 | -0.82381 | -72.6793 | 50.4205 | 50.7172 | 50.5738 | -72.9994 | -0.11099 | -0.017391 | 0.034898 | 0.37967 | 0.49066 | -0.19144 | -0.053381 | -0.27448 | -0.24938 | 0.029786 | 0.045647 | 0.32013 | 0.04729 | -0.096024 | 123.3774 | 123.2033 | 123.3414 | 72.1128 | -123.5058 | 123.1454 | 123.4421 | 123.2988 | 71.9011 | -123.6693
793.2656 | 123.7152 | -102.42 | 20.9976 | 0.077612 | -0.040849 | -0.015492 | 0.033159 | -0.015124 | 0.024824 | 0.065477 | -0.0124 | -0.010735 | 0.028553 | 0.10591 | 0.020363 | -102.1107 | -1.0242 | -101.7699 | 21.1448 | 21.068 | 21.1852 | -102.6035 | -102.1958 | -1.3412 | -102.1295 | 21.022 | 21.1302 | 21.1746 | -102.6289 | -0.18345 | 0.14714 | 0.30931 | 0.65019 | 0.83364 | 0.070371 | 0.1876 | -0.20888 | 0.024347 | 0.22429 | 0.29051 | 0.49939 | 0.1326 | 0.17701 | 123.5648 | 123.488 | 123.6053 | 101.3958 | -123.6011 | 123.442 | 123.5503 | 123.5947 | 101.0788 | -123.6265
794.2656 | 123.6237 | -103.1158 | 20.3751 | 0.077612 | -0.041917 | -0.015492 | 0.034227 | -0.012987 | 0.025892 | 0.080738 | -0.0124 | -0.009667 | 0.029621 | 0.10485 | 0.019295 | -102.7151 | -1.0334 | -102.3376 | 20.4305 | 20.4498 | 20.5671 | -103.2125 | -102.8093 | -1.3458 | -102.7385 | 20.413 | 20.5167 | 20.5657 | -103.2425 | -0.096645 | 0.055471 | 0.40076 | 0.77829 | 0.87493 | 0.074775 | 0.19205 | -0.12664 | 0.037966 | 0.30654 | 0.37735 | 0.50398 | 0.14163 | 0.19062 | 123.5464 | 123.5657 | 123.683 | 102.0825 | -123.5876 | 123.5289 | 123.6325 | 123.6815 | 101.7701 | -123.6175
795.2656 | 123.7061 | -103.4088 | 20.0409 | 0.06235 | -0.041917 | -0.015492 | 0.033159 | -0.014056 | 0.026961 | 0.050216 | -0.011332 | -0.009667 | 0.028553 | 0.10591 | 0.020363 | -103.0722 | -1.0425 | -102.8549 | 20.0734 | 19.937 | 20.2008 | -103.5788 | -103.171 | -1.3549 | -103.0911 | 20.0559 | 20.1596 | 20.2131 | -103.6042 | -0.16999 | 0.032524 | 0.33661 | 0.55391 | 0.7239 | -0.1039 | 0.15993 | -0.1954 | 0.01501 | 0.23779 | 0.31775 | 0.51315 | 0.11866 | 0.17223 | 123.4822 | 123.3458 | 123.6096 | 102.3663 | -123.6197 | 123.4647 | 123.5684 | 123.6219 | 102.0539 | -123.6451
796.2656 | 123.7198 | -102.8549 | 20.5765 | 0.06235 | -0.038712 | -0.015492 | 0.032091 | -0.014056 | 0.025892 | 0.065477 | -0.013468 | -0.011804 | 0.028553 | 0.10591 | 0.021431 | -102.8204 | -1.0334 | -102.4383 | 20.3207 | 20.1797 | 20.4481 | -103.1988 | -102.9009 | -1.3549 | -102.8484 | 20.3077 | 20.416 | 20.2223 | -103.3524 | -0.34383 | -0.25583 | 0.034532 | 0.41664 | 0.76047 | -0.3968 | -0.12841 | -0.49745 | -0.26876 | -0.045959 | 0.006532 | 0.50399 | -0.16052 | -0.3542 | 123.1756 | 123.0346 | 123.303 | 101.8216 | -123.7752 | 123.1626 | 123.2709 | 123.0772 | 101.5 | -123.9288
797.2656 | 123.7015 | -87.4786 | 35.9619 | 0.047088 | -0.041917 | -0.015492 | 0.027817 | -0.016192 | 0.025892 | 0.080738 | -0.013468 | -0.010735 | 0.028553 | 0.10698 | 0.021431 | -85.2302 | -0.90058 | -84.9172 | 38.1901 | 38.01 | 38.213 | -85.5607 | -85.3324 | -1.1718 | -85.2936 | 37.9853 | 38.1352 | 38.1017 | -85.6324 | 1.9179 | 2.2282 | 2.2484 | 2.5614 | 0.64354 | 2.0481 | 2.2511 | 1.8463 | 2.0234 | 2.1463 | 2.185 | 0.33874 | 2.1732 | 2.1398 | 125.6687 | 125.4887 | 125.6917 | 86.5781 | -121.5226 | 125.4639 | 125.6138 | 125.5804 | 86.3068 | -121.5943
798.2656 | 123.7015 | -103.3401 | 20.0775 | 0.06235 | -0.039781 | -0.01656 | 0.032091 | -0.012987 | 0.025892 | 0.065477 | -0.014536 | -0.009667 | 0.028553 | 0.10591 | 0.019295 | -103.0447 | -1.0608 | -102.832 | 20.197 | 20.1247 | 20.2329 | -103.5513 | -103.1252 | -1.3961 | -103.0819 | 20.088 | 20.187 | 20.236 | -103.5722 | -0.21118 | 0.11952 | 0.29542 | 0.50814 | 0.71932 | 0.047217 | 0.15536 | -0.23201 | 0.010439 | 0.21491 | 0.25825 | 0.49025 | 0.10951 | 0.1585 | 123.5372 | 123.4649 | 123.573 | 102.2793 | -123.6288 | 123.4281 | 123.5272 | 123.5762 | 101.944 | -123.6497
799.2812 | 123.5962 | -103.006 | 20.5124 | 0.06235 | -0.041917 | -0.015492 | 0.029954 | -0.012987 | 0.029097 | 0.050216 | -0.011332 | -0.010735 | 0.028553 | 0.10591 | 0.020363 | -102.5457 | -1.0608 | -102.278 | 20.5816 | 20.6147 | 20.7228 | -103.0568 | -102.6399 | -1.4007 | -102.5691 | 20.5779 | 20.6815 | 20.7305 | -103.0776 | -0.050826 | 0.069229 | 0.4603 | 0.72794 | 0.77877 | 0.10229 | 0.21039 | -0.071663 | 0.065462 | 0.36609 | 0.4369 | 0.50856 | 0.16913 | 0.21812 | 123.5876 | 123.6207 | 123.7288 | 101.9452 | -123.5692 | 123.5838 | 123.6875 | 123.7365 | 101.6053 | -123.59
800.2656 | 123.6969 | -103.688 | 19.7937 | 0.06235 | -0.040849 | -0.017629 | 0.031022 | -0.015124 | 0.025892 | 0.080738 | -0.013468 | -0.011804 | 0.028553 | 0.10805 | 0.021431 | -103.4156 | -1.0791 | -103.1067 | 19.73 | 19.5982 | 19.8574 | -103.8032 | -103.5007 | -1.419 | -103.4207 | 19.7079 | 19.8162 | 19.6225 | -103.9522 | -0.11512 | -0.063662 | 0.27247 | 0.58134 | 0.69646 | -0.19554 | 0.063727 | -0.26415 | -0.085763 | 0.18736 | 0.26732 | 0.53147 | 0.022461 | -0.17122 | 123.4181 | 123.2862 | 123.5455 | 102.6089 | -123.5969 | 123.396 | 123.5042 | 123.3105 | 102.269 | -123.7459
801.2656 | 123.7198 | -104.1504 | 19.2993 | 0.047088 | -0.041917 | -0.01656 | 0.033159 | -0.014056 | 0.025892 | 0.065477 | -0.011332 | -0.009667 | 0.028553 | 0.10698 | 0.021431 | -103.8505 | -1.0929 | -103.331 | 19.2859 | 19.1586 | 19.4225 | -104.2473 | -103.9357 | -1.4465 | -103.8603 | 19.273 | 19.3858 | 19.2058 | -104.3826 | -0.096936 | -0.013381 | 0.29987 | 0.81935 | 0.91628 | -0.14074 | 0.12314 | -0.23222 | -0.026335 | 0.21473 | 0.29011 | 0.52232 | 0.086458 | -0.093485 | 123.4363 | 123.309 | 123.5729 | 103.0575 | -123.5466 | 123.4234 | 123.5362 | 123.3562 | 102.7039 | -123.6819
802.2656 | 123.7198 | -103.9948 | 19.4366 | 0.06235 | -0.041917 | -0.01656 | 0.033159 | -0.011919 | 0.026961 | 0.080738 | -0.013468 | -0.009667 | 0.028553 | 0.10485 | 0.021431 | -103.7315 | -1.0975 | -103.2166 | 19.3958 | 19.2593 | 19.5278 | -104.1329 | -103.8258 | -1.4602 | -103.7412 | 19.3829 | 19.4865 | 19.2699 | -104.2773 | -0.1381 | -0.04083 | 0.26326 | 0.77816 | 0.91627 | -0.17733 | 0.091123 | -0.28254 | -0.053781 | 0.16897 | 0.25351 | 0.53606 | 0.049857 | -0.16671 | 123.3906 | 123.2541 | 123.5225 | 102.8973 | -123.5695 | 123.3776 | 123.4813 | 123.2647 | 102.5345 | -123.7139
803.2656 | 123.7289 | -104.2236 | 19.2673 | 0.06235 | -0.041917 | -0.015492 | 0.033159 | -0.012987 | 0.025892 | 0.050216 | -0.0124 | -0.009667 | 0.027485 | 0.10485 | 0.019295 | -103.9741 | -1.1066 | -103.4501 | 19.1577 | 19.0212 | 19.2943 | -104.371 | -104.0684 | -1.4786 | -103.9793 | 19.1539 | 19.2484 | 19.0456 | -104.52 | -0.14732 | -0.10953 | 0.24949 | 0.77355 | 0.92088 | -0.24606 | 0.026987 | -0.29634 | -0.11333 | 0.15518 | 0.2443 | 0.54064 | -0.018857 | -0.22169 | 123.3814 | 123.2448 | 123.5179 | 103.117 | -123.6382 | 123.3776 | 123.472 | 123.2692 | 102.7451 | -123.7872
804.2812 | 123.6053 | -104.4754 | 19.0384 | 0.06235 | -0.042986 | -0.014424 | 0.032091 | -0.014056 | 0.025892 | 0.065477 | -0.013468 | -0.011804 | 0.029621 | 0.10698 | 0.020363 | -104.1069 | -1.1158 | -103.5416 | 19.0158 | 18.9067 | 19.1523 | -104.5221 | -104.1967 | -1.5015 | -104.1075 | 19.012 | 19.1019 | 18.9677 | -104.6482 | -0.04666 | -0.022581 | 0.36849 | 0.93376 | 0.98042 | -0.13165 | 0.11393 | -0.17278 | -0.026384 | 0.27875 | 0.36787 | 0.54064 | 0.063509 | -0.070647 | 123.4912 | 123.3821 | 123.6277 | 103.3596 | -123.5605 | 123.4874 | 123.5773 | 123.4431 | 102.9739 | -123.6866
805.2656 | 123.6328 | -104.1595 | 19.2856 | 0.06235 | -0.041917 | -0.01656 | 0.033159 | -0.014056 | 0.025892 | 0.065477 | -0.011332 | -0.010735 | 0.028553 | 0.10698 | 0.020363 | -104.1252 | -1.1158 | -103.4547 | 19.0067 | 18.8838 | 19.1432 | -104.5129 | -104.2058 | -1.5106 | -104.1167 | 19.0074 | 19.0973 | 18.922 | -104.6619 | -0.35336 | -0.27893 | 0.034318 | 0.70489 | 1.0582 | -0.40174 | -0.14242 | -0.50237 | -0.27815 | -0.046264 | 0.042856 | 0.54522 | -0.18826 | -0.36362 | 123.1662 | 123.0434 | 123.3027 | 103.0438 | -123.7985 | 123.167 | 123.2569 | 123.0815 | 102.6489 | -123.9475
806.2656 | 123.7289 | -104.1733 | 19.281 | 0.06235 | -0.045122 | -0.015492 | 0.033159 | -0.014056 | 0.025892 | 0.065477 | -0.0124 | -0.011804 | 0.027485 | 0.10805 | 0.020363 | -103.7361 | -1.1249 | -102.9877 | 19.3958 | 19.2639 | 19.427 | -104.142 | -103.8304 | -1.5335 | -103.7229 | 19.3829 | 19.4819 | 19.334 | -104.2819 | 0.031267 | 0.11481 | 0.43721 | 1.1856 | 1.1543 | -0.017111 | 0.14603 | -0.10859 | 0.10186 | 0.34292 | 0.45036 | 0.55895 | 0.20092 | 0.053026 | 123.5691 | 123.4372 | 123.6003 | 103.0483 | -123.423 | 123.5561 | 123.6552 | 123.5073 | 102.6398 | -123.5629
807.2656 | 123.6969 | -104.0176 | 19.4138 | 0.092874 | -0.044054 | -0.014424 | 0.032091 | -0.014056 | 0.024824 | 0.095999 | -0.014536 | -0.008599 | 0.029621 | 0.10378 | 0.020363 | -103.8963 | -1.1341 | -103.1159 | 19.2402 | 19.1082 | 19.2897 | -104.2931 | -103.9769 | -1.5472 | -103.8603 | 19.2318 | 19.3308 | 19.1784 | -104.433 | -0.27548 | -0.17361 | 0.12133 | 0.90177 | 1.1773 | -0.30555 | -0.12408 | -0.41533 | -0.18198 | 0.040765 | 0.15736 | 0.57269 | -0.082926 | -0.2354 | 123.2578 | 123.1258 | 123.3073 | 102.8836 | -123.7069 | 123.2494 | 123.3485 | 123.196 | 102.4704 | -123.8467
808.2656 | 123.7061 | -104.4159 | 19.0155 | 0.06235 | -0.044054 | -0.01656 | 0.031022 | -0.012987 | 0.026961 | 0.080738 | -0.014536 | -0.012872 | 0.027485 | 0.10591 | 0.019295 | -104.1527 | -1.1432 | -103.1525 | 18.9746 | 18.8518 | 19.0287 | -104.5495 | -104.2379 | -1.5839 | -104.1167 | 18.9616 | 19.0607 | 18.922 | -104.694 | -0.13364 | -0.040898 | 0.2632 | 1.2634 | 1.397 | -0.16371 | 0.013198 | -0.27807 | -0.053859 | 0.17803 | 0.2992 | 0.57728 | 0.04519 | -0.093545 | 123.3905 | 123.2677 | 123.4446 | 103.2726 | -123.565 | 123.3775 | 123.4766 | 123.3379 | 102.832 | -123.7095
809.2812 | 123.6969 | -104.2465 | 19.1757 | 0.047088 | -0.044054 | -0.017629 | 0.033159 | -0.014056 | 0.024824 | 0.050216 | -0.0124 | -0.011804 | 0.028553 | 0.10698 | 0.020363 | -104.1206 | -1.1524 | -102.8045 | 19.0112 | 18.8838 | 19.0562 | -104.5129 | -104.2104 | -1.5976 | -104.0846 | 19.0028 | 19.1065 | 18.922 | -104.6619 | -0.26638 | -0.16449 | 0.12587 | 1.442 | 1.7084 | -0.29188 | -0.11955 | -0.41539 | -0.17287 | 0.036132 | 0.16188 | 0.57728 | -0.069241 | -0.25376 | 123.2578 | 123.1304 | 123.3027 | 103.0941 | -123.6886 | 123.2494 | 123.353 | 123.1685 | 102.6489 | -123.8376
810.2656 | 123.7198 | -104.4571 | 18.9789 | 0.06235 | -0.042986 | -0.014424 | 0.033159 | -0.012987 | 0.026961 | 0.065477 | -0.013468 | -0.011804 | 0.027485 | 0.10698 | 0.019295 | -104.2168 | -1.1661 | -103.1616 | 18.9105 | 18.7694 | 18.9554 | -104.6182 | -104.3111 | -1.6297 | -104.1808 | 18.9021 | 18.9966 | 18.8395 | -104.7672 | -0.16113 | -0.068375 | 0.2403 | 1.2954 | 1.4566 | -0.20951 | -0.023438 | -0.31014 | -0.076759 | 0.14597 | 0.2763 | 0.58644 | 0.017711 | -0.13934 | 123.3676 | 123.2265 | 123.4125 | 103.291 | -123.5971 | 123.3592 | 123.4537 | 123.2966 | 102.8274 | -123.7461
811.2656 | 123.7335 | -104.2831 | 19.1437 | 0.077612 | -0.045122 | -0.014424 | 0.034227 | -0.011919 | 0.025892 | 0.065477 | -0.013468 | -0.011804 | 0.027485 | 0.10805 | 0.019295 | -104.1023 | -1.1661 | -102.7038 | 19.0204 | 18.8884 | 19.0653 | -104.5083 | -104.2012 | -1.6388 | -104.0572 | 19.0166 | 19.1065 | 18.9403 | -104.6482 | -0.22518 | -0.12329 | 0.18081 | 1.5793 | 1.8045 | -0.25525 | -0.078347 | -0.36504 | -0.12709 | 0.081911 | 0.22597 | 0.59101 | -0.037198 | -0.20341 | 123.3035 | 123.1716 | 123.3485 | 103.117 | -123.652 | 123.2997 | 123.3896 | 123.2234 | 102.6443 | -123.7919
812.2656 | 123.7198 | -104.3243 | 19.1071 | 0.047088 | -0.042986 | -0.015492 | 0.034227 | -0.014056 | 0.024824 | 0.080738 | -0.013468 | -0.010735 | 0.027485 | 0.10698 | 0.020363 | -104.0886 | -1.1707 | -102.4886 | 19.0295 | 18.9022 | 19.0745 | -104.4992 | -104.1875 | -1.6617 | -104.0434 | 19.0212 | 19.1248 | 18.9815 | -104.6436 | -0.17483 | -0.077511 | 0.23574 | 1.8357 | 2.0105 | -0.2049 | -0.032569 | -0.31926 | -0.085892 | 0.13685 | 0.28091 | 0.60017 | 0.017737 | -0.12558 | 123.3539 | 123.2265 | 123.3988 | 103.1536 | -123.6062 | 123.3455 | 123.4491 | 123.3058 | 102.6626 | -123.7507
813.2656 | 123.7244 | -103.7521 | 19.6838 | 0.077612 | -0.044054 | -0.015492 | 0.033159 | -0.014056 | 0.026961 | 0.050216 | -0.0124 | -0.010735 | 0.028553 | 0.10805 | 0.019295 | -103.791 | -1.1753 | -102.4703 | 19.3455 | 19.2135 | 19.3904 | -104.1832 | -103.867 | -1.6846 | -103.7321 | 19.3371 | 19.4361 | 19.2928 | -104.3231 | -0.43109 | -0.33838 | -0.038869 | 1.2818 | 1.7129 | -0.47031 | -0.29343 | -0.57095 | -0.34676 | -0.11485 | 0.020058 | 0.591 | -0.2477 | -0.39101 | 123.0976 | 122.9657 | 123.1425 | 102.5768 | -123.8671 | 123.0892 | 123.1883 | 123.045 | 102.0675 | -124.0069
814.2812 | 123.5641 | -103.6514 | 19.8486 | 0.031826 | -0.045122 | -0.01656 | 0.034227 | -0.014056 | 0.023756 | 0.065477 | -0.0124 | -0.011804 | 0.027485 | 0.10912 | 0.017158 | -102.9165 | -1.1707 | -100.9549 | 20.2153 | 20.0835 | 20.2558 | -103.3178 | -103.0153 | -1.6983 | -102.8621 | 20.1978 | 20.3015 | 20.149 | -103.4577 | 0.33362 | 0.36671 | 0.73489 | 2.6965 | 2.3629 | 0.23489 | 0.40713 | 0.19374 | 0.3492 | 0.63608 | 0.7893 | 0.59556 | 0.45286 | 0.30039 | 123.8668 | 123.7349 | 123.9072 | 102.4807 | -123.1664 | 123.8493 | 123.9529 | 123.8005 | 101.9531 | -123.3063
815.2656 | 123.7061 | -103.7979 | 19.6381 | 0.047088 | -0.041917 | -0.015492 | 0.032091 | -0.014056 | 0.023756 | 0.050216 | -0.014536 | -0.011804 | 0.027485 | 0.10698 | 0.018226 | -103.3103 | -1.1707 | -101.3258 | 19.8216 | 19.6852 | 19.862 | -103.7116 | -103.3954 | -1.7304 | -103.2742 | 19.8087 | 19.9169 | 19.7598 | -103.856 | 0.08632 | 0.18354 | 0.48764 | 2.4722 | 2.3858 | 0.047094 | 0.22394 | -0.05813 | 0.1706 | 0.40254 | 0.52371 | 0.58184 | 0.27883 | 0.12178 | 123.6195 | 123.4831 | 123.6599 | 102.6272 | -123.3497 | 123.6066 | 123.7148 | 123.5578 | 102.0675 | -123.4941
816.2656 | 123.6877 | -104.1 | 19.3588 | 0.06235 | -0.045122 | -0.013355 | 0.035296 | -0.011919 | 0.025892 | 0.050216 | -0.0124 | -0.010735 | 0.027485 | 0.10591 | 0.018226 | -103.6399 | -1.189 | -100.8221 | 19.4782 | 19.3738 | 19.5323 | -104.0275 | -103.725 | -1.7579 | -103.5856 | 19.4836 | 19.5827 | 19.4348 | -104.1857 | 0.072498 | 0.1194 | 0.46012 | 3.2779 | 3.2054 | 0.014963 | 0.17352 | -0.085681 | 0.12477 | 0.37499 | 0.51448 | 0.60016 | 0.22383 | 0.075935 | 123.5783 | 123.4738 | 123.6324 | 102.911 | -123.3864 | 123.5836 | 123.6827 | 123.5348 | 102.3422 | -123.5445
817.2656 | 123.6511 | -103.9856 | 19.4824 | 0.077612 | -0.044054 | -0.01656 | 0.035296 | -0.012987 | 0.025892 | 0.095999 | -0.013468 | -0.009667 | 0.028553 | 0.10805 | 0.019295 | -103.6399 | -1.1982 | -101.074 | 19.4782 | 19.3646 | 19.5278 | -104.0321 | -103.7205 | -1.7853 | -103.5718 | 19.4836 | 19.5827 | 19.4485 | -104.1811 | -0.046522 | -0.004195 | 0.34568 | 2.9116 | 2.9582 | -0.11779 | 0.045347 | -0.19554 | 0.00117 | 0.26513 | 0.41377 | 0.60932 | 0.10023 | -0.033925 | 123.4638 | 123.3502 | 123.5134 | 102.7874 | -123.5145 | 123.4692 | 123.5683 | 123.4341 | 102.2003 | -123.6636
818.2656 | 123.6786 | -103.949 | 19.4778 | 0.077612 | -0.045122 | -0.01656 | 0.034227 | -0.014056 | 0.024824 | 0.050216 | -0.0124 | -0.010735 | 0.026416 | 0.10698 | 0.018226 | -103.6079 | -1.2073 | -101.0785 | 19.5149 | 19.3738 | 19.569 | -104.0046 | -103.7022 | -1.8082 | -103.5398 | 19.5065 | 19.6055 | 19.4668 | -104.1537 | -0.055669 | 0.03701 | 0.3411 | 2.8704 | 2.9261 | -0.10406 | 0.091132 | -0.20469 | 0.028641 | 0.24682 | 0.4092 | 0.61389 | 0.1277 | -0.011033 | 123.4638 | 123.3228 | 123.518 | 102.7416 | -123.4825 | 123.4555 | 123.5545 | 123.4158 | 102.1407 | -123.6315
819.2812 | 123.6282 | -103.9032 | 19.6198 | 0.047088 | -0.044054 | -0.01656 | 0.032091 | -0.014056 | 0.025892 | 0.080738 | -0.0124 | -0.011804 | 0.028553 | 0.10805 | 0.019295 | -103.8139 | -1.2302 | -101.2433 | 19.3134 | 19.1723 | 19.3584 | -104.2199 | -103.9128 | -1.8449 | -103.7412 | 19.3005 | 19.3995 | 19.2425 | -104.3643 | -0.31666 | -0.30635 | 0.089301 | 2.6598 | 2.9765 | -0.44744 | -0.26139 | -0.46109 | -0.3193 | -0.009575 | 0.16196 | 0.62306 | -0.22024 | -0.37729 | 123.2166 | 123.0755 | 123.2616 | 102.673 | -123.8396 | 123.2037 | 123.3027 | 123.1457 | 102.0583 | -123.984
820.2656 | 123.7015 | -104.1458 | 19.3222 | 0.06235 | -0.045122 | -0.015492 | 0.033159 | -0.010851 | 0.023756 | 0.080738 | -0.014536 | -0.009667 | 0.028553 | 0.10805 | 0.019295 | -103.9604 | -1.2348 | -101.1014 | 19.1623 | 19.0349 | 19.2073 | -104.3526 | -104.0456 | -1.8632 | -103.8923 | 19.1585 | 19.2622 | 19.1051 | -104.5108 | -0.20683 | -0.15989 | 0.18541 | 3.0444 | 3.2512 | -0.28726 | -0.11494 | -0.365 | -0.16369 | 0.10026 | 0.25348 | 0.61848 | -0.060054 | -0.2171 | 123.3081 | 123.1808 | 123.3531 | 102.911 | -123.6748 | 123.3043 | 123.408 | 123.2509 | 102.2826 | -123.833
821.2656 | 123.6603 | -103.6743 | 19.7891 | 0.06235 | -0.044054 | -0.01656 | 0.034227 | -0.012987 | 0.025892 | 0.080738 | -0.0124 | -0.011804 | 0.028553 | 0.10698 | 0.018226 | -103.6628 | -1.2302 | -100.6024 | 19.4599 | 19.3463 | 19.5049 | -104.0687 | -103.7479 | -1.8769 | -103.5993 | 19.4515 | 19.5598 | 19.4164 | -104.2132 | -0.39443 | -0.32921 | 0.011506 | 3.0719 | 3.4664 | -0.44281 | -0.28425 | -0.53887 | -0.33758 | -0.073623 | 0.07502 | 0.61389 | -0.22936 | -0.37268 | 123.1342 | 123.0206 | 123.1792 | 102.4441 | -123.8579 | 123.1259 | 123.2341 | 123.0908 | 101.7974 | -124.0023
822.2656 | 123.6649 | -103.8208 | 19.6198 | 0.077612 | -0.045122 | -0.01656 | 0.034227 | -0.012987 | 0.026961 | 0.095999 | -0.014536 | -0.011804 | 0.029621 | 0.10805 | 0.018226 | -103.7269 | -1.2486 | -100.4193 | 19.405 | 19.2822 | 19.4499 | -104.1237 | -103.812 | -1.9135 | -103.6542 | 19.3966 | 19.4957 | 19.3478 | -104.2681 | -0.30289 | -0.21478 | 0.093893 | 3.4015 | 3.7044 | -0.33754 | -0.16982 | -0.44734 | -0.22315 | 0.00876 | 0.16656 | 0.6139 | -0.12409 | -0.27198 | 123.2258 | 123.103 | 123.2707 | 102.5722 | -123.7434 | 123.2174 | 123.3165 | 123.1686 | 101.9073 | -123.8879
823.2656 | 123.6603 | -105.1712 | 18.2968 | 0.047088 | -0.044054 | -0.01656 | 0.035296 | -0.010851 | 0.028029 | 0.080738 | -0.0124 | -0.011804 | 0.027485 | 0.10805 | 0.019295 | -104.7204 | -1.2623 | -100.6161 | 18.3931 | 18.2611 | 18.4381 | -105.1356 | -104.8148 | -1.9685 | -104.6616 | 18.3848 | 18.4975 | 18.313 | -105.2755 | 0.035565 | 0.096335 | 0.45079 | 4.5551 | 4.5195 | -0.035704 | 0.14125 | -0.10427 | 0.087939 | 0.35643 | 0.50965 | 0.61392 | 0.20071 | 0.01619 | 123.5644 | 123.4323 | 123.6093 | 103.9089 | -123.4325 | 123.556 | 123.6687 | 123.4842 | 103.2027 | -123.5723
824.2812 | 123.6237 | -105.748 | 17.7246 | 0.06235 | -0.045122 | -0.014424 | 0.034227 | -0.010851 | 0.023756 | 0.050216 | -0.0124 | -0.012872 | 0.023212 | 0.10805 | 0.01609 | -105.3889 | -1.2989 | -101.0144 | 17.7293 | 17.5972 | 17.7742 | -105.7996 | -105.4924 | -2.0921 | -105.3072 | 17.7209 | 17.8245 | 17.672 | -105.944 | -0.051597 | 0.004674 | 0.35912 | 4.7336 | 4.7851 | -0.12744 | 0.049555 | -0.196 | -0.003738 | 0.25556 | 0.44083 | 0.63683 | 0.099861 | -0.05261 | 123.4773 | 123.3452 | 123.5221 | 104.4491 | -123.5242 | 123.4689 | 123.5725 | 123.42 | 103.6559 | -123.6686
825.2656 | 123.6786 | -105.5237 | 17.9443 | 0.06235 | -0.044054 | -0.015492 | 0.035296 | -0.011919 | 0.023756 | 0.080738 | -0.014536 | -0.010735 | 0.020007 | 0.10912 | 0.018226 | -105.2698 | -1.2943 | -100.3552 | 17.8437 | 17.7208 | 17.8978 | -105.6851 | -105.3596 | -2.1196 | -105.1881 | 17.8445 | 17.9435 | 17.7819 | -105.8341 | -0.16143 | -0.10059 | 0.25386 | 5.1685 | 5.3299 | -0.22354 | -0.046549 | -0.31041 | -0.099845 | 0.16404 | 0.33557 | 0.64598 | -0.000822 | -0.16245 | 123.3674 | 123.2445 | 123.4215 | 104.2293 | -123.6294 | 123.3682 | 123.4672 | 123.3056 | 103.4041 | -123.7784
826.2656 | 123.6649 | -105.8075 | 17.6605 | 0.047088 | -0.046191 | -0.01656 | 0.035296 | -0.010851 | 0.026961 | 0.050216 | -0.014536 | -0.012872 | 0.018939 | 0.10805 | 0.019295 | -105.572 | -1.3081 | -100.433 | 17.5461 | 17.4186 | 17.591 | -105.9782 | -105.6664 | -2.1471 | -105.4766 | 17.5423 | 17.6459 | 17.4934 | -106.1363 | -0.17067 | -0.11437 | 0.2355 | 5.3745 | 5.5452 | -0.24193 | -0.069502 | -0.3288 | -0.11821 | 0.14108 | 0.33093 | 0.65973 | -0.014617 | -0.16709 | 123.3536 | 123.2261 | 123.3985 | 104.4994 | -123.6387 | 123.3498 | 123.4534 | 123.3009 | 103.6604 | -123.7968
827.2656 | 123.6694 | -105.8487 | 17.601 | 0.031826 | -0.047259 | -0.015492 | 0.035296 | -0.010851 | 0.026961 | 0.034955 | -0.0124 | -0.011804 | 0.11081 | 0.20314 | 0.019295 | -105.3614 | -1.3081 | -99.9797 | 17.7568 | 17.6246 | 17.8062 | -105.7675 | -105.4375 | -0.51704 | 16.6056 | 17.7346 | 17.8474 | 17.6857 | -105.9119 | 0.081164 | 0.15574 | 0.4873 | 5.869 | 5.7878 | 0.023627 | 0.2052 | -0.063238 | 0.13359 | 0.41121 | 122.4543 | 122.5175 | 0.24635 | 0.084722 | 123.6054 | 123.4733 | 123.6549 | 104.5406 | -123.3685 | 123.5833 | 123.6961 | 123.5344 | 105.3317 | -123.5129
828.2656 | 123.6511 | -106.1691 | 17.2943 | 0.06235 | -0.045122 | -0.01656 | 0.034227 | -0.010851 | 0.024824 | 0.050216 | -0.013468 | -0.012872 | 0.10974 | 0.20207 | 0.017158 | -105.8833 | -1.3355 | -100.3414 | 17.2302 | 17.1072 | 17.2751 | -106.2895 | -105.9595 | -0.53535 | 17.3061 | 17.1989 | 17.3208 | 17.1592 | -106.4339 | -0.1204 | -0.064073 | 0.2858 | 5.8277 | 5.9481 | -0.18709 | -0.019215 | -0.26479 | -0.095389 | 0.20967 | 123.4752 | 123.74 | 0.026512 | -0.13512 | 123.3994 | 123.2763 | 123.4442 | 104.8336 | -123.5838 | 123.3681 | 123.49 | 123.3283 | 105.6338 | -123.7282
829.2812 | 123.587 | -106.2332 | 17.2256 | 0.077612 | -0.044054 | -0.01656 | 0.033159 | -0.011919 | 0.025892 | 0.034955 | -0.013468 | -0.011804 | 0.11188 | 0.20207 | 0.019295 | -105.9657 | -1.3447 | -100.1034 | 17.1295 | 17.0111 | 17.1835 | -106.3994 | -106.0648 | -0.45751 | 17.2191 | 17.1119 | 17.2155 | 17.063 | -106.5301 | -0.16621 | -0.096133 | 0.26748 | 6.1299 | 6.2961 | -0.21458 | -0.042122 | -0.29686 | -0.11371 | 0.16845 | 123.4523 | 123.7492 | -0.010131 | -0.1626 | 123.3627 | 123.2443 | 123.4167 | 104.8885 | -123.6251 | 123.3451 | 123.4487 | 123.2963 | 105.7757 | -123.7557
830.2656 | 123.7427 | -106.4621 | 16.9601 | 0.047088 | -0.045122 | -0.01656 | 0.038501 | -0.010851 | 0.023756 | 0.065477 | -0.0124 | -0.012872 | 0.11188 | 0.2042 | 0.019295 | -106.0939 | -1.363 | -99.3891 | 17.0059 | 16.8691 | 17.0553 | -106.5139 | -106.1747 | -0.47125 | 17.1047 | 16.9883 | 17.0873 | 16.9348 | -106.6583 | -0.051798 | 0.045754 | 0.36816 | 7.073 | 7.1248 | -0.091027 | 0.09518 | -0.19618 | 0.028168 | 0.28744 | 123.5667 | 123.7629 | 0.12717 | -0.0253 | 123.468 | 123.3312 | 123.5174 | 105.0991 | -123.474 | 123.4504 | 123.5494 | 123.3969 | 105.9908 | -123.6184
831.2656 | 123.6969 | -106.897 | 16.5161 | 0.047088 | -0.045122 | -0.015492 | 0.037433 | -0.010851 | 0.024824 | 0.050216 | -0.011332 | -0.010735 | 0.10974 | 0.20207 | 0.020363 | -106.6388 | -1.418 | -100.1812 | 16.4611 | 16.3471 | 16.5105 | -107.0588 | -106.7195 | -0.49872 | 16.5598 | 16.4435 | 16.547 | 16.39 | -107.1986 | -0.16181 | -0.055043 | 0.25821 | 6.7158 | 6.8776 | -0.16899 | -0.005643 | -0.30161 | -0.072642 | 0.17745 | 123.4568 | 123.7584 | 0.030927 | -0.12612 | 123.358 | 123.2441 | 123.4074 | 105.479 | -123.5749 | 123.3404 | 123.444 | 123.287 | 106.3983 | -123.7147
832.2656 | 123.6786 | -107.0206 | 16.4383 | 0.06235 | -0.045122 | -0.01656 | 0.038501 | -0.011919 | 0.025892 | 0.050216 | -0.0124 | -0.011804 | 0.10974 | 0.20207 | 0.017158 | -106.7074 | -1.4317 | -99.8973 | 16.3741 | 16.251 | 16.4326 | -107.1321 | -106.7974 | -0.49872 | 16.4911 | 16.3702 | 16.4646 | 16.3213 | -107.2627 | -0.11148 | -0.064213 | 0.31313 | 7.1232 | 7.2347 | -0.18733 | -0.005659 | -0.24211 | -0.068078 | 0.22321 | 123.5117 | 123.7538 | 0.026332 | -0.11698 | 123.3946 | 123.2715 | 123.4532 | 105.5889 | -123.5703 | 123.3908 | 123.4852 | 123.3419 | 106.5218 | -123.701
833.2656 | 123.6877 | -107.3502 | 16.0812 | 0.06235 | -0.045122 | -0.015492 | 0.036364 | -0.010851 | 0.023756 | 0.080738 | -0.014536 | -0.011804 | 0.11188 | 0.20207 | 0.017158 | -107.1012 | -1.4637 | -100.3872 | 15.9849 | 15.8618 | 16.0435 | -107.5258 | -107.182 | -0.52619 | 16.079 | 15.9719 | 16.08 | 15.9184 | -107.6748 | -0.17568 | -0.096321 | 0.24898 | 6.9629 | 7.1386 | -0.21948 | -0.037785 | -0.32462 | -0.10935 | 0.16819 | 123.4292 | 123.7538 | -0.001215 | -0.16284 | 123.3351 | 123.2119 | 123.3936 | 105.8864 | -123.6071 | 123.322 | 123.4302 | 123.2686 | 106.824 | -123.756
834.2812 | 123.6786 | -107.2723 | 16.1499 | 0.06235 | -0.045122 | -0.015492 | 0.037433 | -0.0087139 | 0.023756 | 0.065477 | -0.013468 | -0.012872 | 0.11081 | 0.20314 | 0.018226 | -106.9776 | -1.4637 | -99.2838 | 16.1131 | 15.9854 | 16.1625 | -107.4114 | -107.0583 | -0.53535 | 16.2164 | 16.0955 | 16.1945 | 16.042 | -107.5466 | -0.13903 | -0.03679 | 0.29478 | 7.9885 | 8.1275 | -0.16452 | 0.012594 | -0.27423 | -0.054396 | 0.21399 | 123.4887 | 123.763 | 0.044586 | -0.10788 | 123.3855 | 123.2577 | 123.4348 | 105.8086 | -123.5613 | 123.3678 | 123.4668 | 123.3144 | 106.737 | -123.6965
835.2656 | 123.7427 | -106.7413 | 16.6672 | 0.031826 | -0.045122 | -0.01656 | 0.036364 | -0.0087139 | 0.025892 | 0.065477 | -0.0124 | -0.010735 | 0.11081 | 0.20314 | 0.018226 | -106.4785 | -1.4637 | -99.2426 | 16.6076 | 16.4753 | 16.6616 | -106.9077 | -106.5593 | -0.52619 | 16.7155 | 16.5991 | 16.6981 | 16.5319 | -107.0383 | -0.16635 | -0.059597 | 0.26281 | 7.4987 | 7.665 | -0.19185 | -0.005611 | -0.29699 | -0.068035 | 0.18207 | 123.4568 | 123.7538 | 0.030959 | -0.13525 | 123.3489 | 123.2167 | 123.4029 | 105.2776 | -123.5749 | 123.3405 | 123.4395 | 123.2733 | 106.2151 | -123.7055
836.2656 | 123.6786 | -106.6406 | 16.777 | 0.06235 | -0.045122 | -0.015492 | 0.038501 | -0.0097819 | 0.025892 | 0.065477 | -0.013468 | -0.011804 | 0.10974 | 0.20207 | 0.01609 | -106.4282 | -1.4592 | -98.0981 | 16.6671 | 16.5349 | 16.7165 | -106.8482 | -106.5135 | -0.52619 | 16.7658 | 16.6495 | 16.7485 | 16.5823 | -106.9971 | -0.20753 | -0.10994 | 0.21247 | 8.5426 | 8.7501 | -0.24218 | -0.060532 | -0.35649 | -0.12753 | 0.12714 | 123.4065 | 123.7629 | -0.02854 | -0.19475 | 123.3077 | 123.1755 | 123.3571 | 105.1815 | -123.6252 | 123.2901 | 123.3891 | 123.2229 | 106.1144 | -123.7742
837.2656 | 123.6237 | -107.7805 | 15.6464 | 0.047088 | -0.046191 | -0.01656 | 0.037433 | -0.0097819 | 0.026961 | 0.065477 | -0.011332 | -0.011804 | 0.10974 | 0.2042 | 0.019295 | -107.5087 | -1.4866 | -98.6291 | 15.5729 | 15.4542 | 15.6314 | -107.9379 | -107.5941 | -0.57656 | 15.6715 | 15.5552 | 15.6588 | 15.5155 | -108.0823 | -0.15748 | -0.073499 | 0.2718 | 9.1513 | 9.3088 | -0.19213 | -0.014984 | -0.30183 | -0.091119 | 0.1864 | 123.452 | 123.7538 | 0.012429 | -0.13088 | 123.3533 | 123.2347 | 123.4118 | 106.2938 | -123.5843 | 123.3357 | 123.4392 | 123.2959 | 107.2039 | -123.7287
838.2656 | 123.5779 | -108.1558 | 15.3442 | 0.047088 | -0.045122 | -0.01656 | 0.038501 | -0.0087139 | 0.024824 | 0.080738 | -0.013468 | -0.010735 | 0.10867 | 0.2042 | 0.018226 | -107.8246 | -1.5095 | -99.6501 | 15.257 | 15.1383 | 15.3109 | -108.2447 | -107.9008 | -0.59945 | 15.3556 | 15.2485 | 15.3429 | 15.1904 | -108.3845 | -0.088905 | -0.087284 | 0.33126 | 8.5057 | 8.5946 | -0.20595 | -0.033362 | -0.22867 | -0.095754 | 0.25499 | 123.5114 | 123.7401 | -0.00137 | -0.15384 | 123.4128 | 123.2941 | 123.4667 | 106.6463 | -123.589 | 123.4043 | 123.4987 | 123.3462 | 107.5564 | -123.7287
839.2812 | 123.6145 | -107.3181 | 16.1041 | 0.047088 | -0.047259 | -0.01656 | 0.037433 | -0.0097819 | 0.025892 | 0.019694 | -0.0124 | -0.011804 | 0.10974 | 0.20207 | 0.018226 | -107.1012 | -1.5095 | -98.7024 | 15.9712 | 15.848 | 16.0297 | -107.5258 | -107.1865 | -0.56282 | 16.079 | 15.9627 | 16.0709 | 15.9184 | -107.6748 | -0.20772 | -0.13294 | 0.21694 | 8.6157 | 8.8234 | -0.25611 | -0.074409 | -0.35666 | -0.1414 | 0.13157 | 123.3971 | 123.7538 | -0.03326 | -0.18573 | 123.2893 | 123.1661 | 123.3478 | 105.8086 | -123.63 | 123.2808 | 123.389 | 123.2365 | 106.7553 | -123.7789
840.2656 | 123.5962 | -108.1604 | 15.303 | 0.031826 | -0.048328 | -0.01656 | 0.037433 | -0.0097819 | 0.024824 | 0.050216 | -0.011332 | -0.012872 | 0.10974 | 0.20314 | 0.017158 | -107.7055 | -1.5278 | -98.4094 | 15.3806 | 15.2573 | 15.4345 | -108.1211 | -107.7955 | -0.61319 | 15.4746 | 15.3492 | 15.4619 | 15.3049 | -108.2838 | 0.039302 | 0.07753 | 0.45487 | 9.751 | 9.7117 | -0.045704 | 0.13146 | -0.12336 | 0.046171 | 0.36488 | 123.635 | 123.7584 | 0.15887 | 0.001822 | 123.541 | 123.4177 | 123.5949 | 106.6326 | -123.4241 | 123.5096 | 123.6223 | 123.4653 | 107.5472 | -123.5868
841.2656 | 123.6832 | -107.6111 | 15.8112 | 0.047088 | -0.044054 | -0.015492 | 0.03957 | -0.0076459 | 0.026961 | 0.050216 | -0.0124 | -0.011804 | 0.10974 | 0.20207 | 0.018226 | -107.3805 | -1.537 | -98.3957 | 15.7011 | 15.5733 | 15.7596 | -107.8052 | -107.4613 | -0.59945 | 15.8089 | 15.6972 | 15.787 | 15.6254 | -107.9495 | -0.19407 | -0.1101 | 0.23062 | 9.2154 | 9.4095 | -0.23788 | -0.051578 | -0.33842 | -0.11398 | 0.14981 | 123.42 | 123.7584 | -0.024165 | -0.18579 | 123.3121 | 123.1844 | 123.3707 | 106.0741 | -123.6163 | 123.3083 | 123.3981 | 123.2364 | 107.0116 | -123.7607
842.2656 | 123.6649 | -108.6731 | 14.7354 | 0.06235 | -0.046191 | -0.017629 | 0.038501 | -0.0097819 | 0.023756 | 0.034955 | -0.0124 | -0.01394 | 0.10867 | 0.2042 | 0.018226 | -108.3877 | -1.5645 | -99.641 | 14.6847 | 14.5568 | 14.7431 | -108.8308 | -108.4823 | -0.64066 | 14.7787 | 14.6716 | 14.7705 | 14.6089 | -108.966 | -0.15774 | -0.050758 | 0.28539 | 9.0321 | 9.1899 | -0.17865 | 0.007716 | -0.29291 | -0.063819 | 0.19077 | 123.4518 | 123.7447 | 0.035129 | -0.1265 | 123.3578 | 123.2299 | 123.4162 | 107.1086 | -123.5662 | 123.3447 | 123.4436 | 123.282 | 108.0324 | -123.7014
843.2656 | 123.6511 | -108.7418 | 14.6942 | 0.077612 | -0.048328 | -0.015492 | 0.036364 | -0.010851 | 0.024824 | 0.065477 | -0.013468 | -0.012872 | 0.10974 | 0.2042 | 0.017158 | -108.4747 | -1.5919 | -100.0301 | 14.5931 | 14.4743 | 14.6607 | -108.9224 | -108.5693 | -0.64982 | 14.6871 | 14.5846 | 14.679 | 14.5128 | -109.053 | -0.18065 | -0.10113 | 0.26706 | 8.7117 | 8.8923 | -0.21988 | -0.033499 | -0.31124 | -0.10961 | 0.17244 | 123.4289 | 123.7401 | -0.015244 | -0.18145 | 123.3348 | 123.2161 | 123.4025 | 107.1498 | -123.6166 | 123.3264 | 123.4207 | 123.2545 | 108.0919 | -123.7472
844.2812 | 123.6465 | -107.9361 | 15.4999 | 0.047088 | -0.046191 | -0.01656 | 0.038501 | -0.0087139 | 0.024824 | 0.080738 | -0.0124 | -0.012872 | 0.10974 | 0.2042 | 0.018226 | -107.6964 | -1.5736 | -98.913 | 15.3714 | 15.2528 | 15.4253 | -108.1348 | -107.7772 | -0.60861 | 15.4746 | 15.3629 | 15.4619 | 15.3003 | -108.27 | -0.19874 | -0.12847 | 0.23973 | 9.0231 | 9.2218 | -0.24712 | -0.074537 | -0.33393 | -0.13693 | 0.15889 | 123.4107 | 123.7447 | -0.037967 | -0.1996 | 123.3075 | 123.1889 | 123.3614 | 106.3625 | -123.6347 | 123.299 | 123.398 | 123.2364 | 107.3275 | -123.7699
845.2656 | 123.5779 | -108.9935 | 14.4882 | 0.031826 | -0.047259 | -0.017629 | 0.038501 | -0.0097819 | 0.024824 | 0.065477 | -0.0124 | -0.012872 | 0.10867 | 0.2042 | 0.017158 | -108.7174 | -1.6194 | -99.9614 | 14.3504 | 14.2225 | 14.4089 | -109.1559 | -108.8074 | -0.64524 | 14.4398 | 14.3328 | 14.4363 | 14.2701 | -109.3094 | -0.1624 | -0.13779 | 0.27618 | 9.0321 | 9.1945 | -0.26572 | -0.079329 | -0.31588 | -0.15544 | 0.18612 | 123.4334 | 123.7493 | -0.051916 | -0.21812 | 123.344 | 123.216 | 123.4024 | 107.3741 | -123.6442 | 123.3263 | 123.4298 | 123.2636 | 108.3483 | -123.7976
846.2656 | 123.6145 | -109.1629 | 14.3051 | 0.047088 | -0.047259 | -0.01656 | 0.038501 | -0.0076459 | 0.026961 | 0.050216 | -0.015604 | -0.011804 | 0.1076 | 0.20314 | 0.017158 | -108.7631 | -1.6286 | -99.2655 | 14.2955 | 14.1813 | 14.3677 | -109.2063 | -108.8486 | -0.6544 | 14.3986 | 14.3007 | 14.3951 | 14.2335 | -109.3323 | -0.0434 | -0.009623 | 0.39977 | 9.8974 | 9.9408 | -0.12383 | 0.062569 | -0.1694 | -0.004379 | 0.31428 | 123.5615 | 123.7309 | 0.089982 | -0.071646 | 123.4584 | 123.3442 | 123.5306 | 107.5343 | -123.5114 | 123.4636 | 123.558 | 123.3964 | 108.5085 | -123.6374
847.2656 | 123.5962 | -108.8699 | 14.6118 | 0.031826 | -0.047259 | -0.01656 | 0.036364 | -0.0097819 | 0.022687 | 0.050216 | -0.011332 | -0.01394 | 0.10867 | 0.20207 | 0.018226 | -108.6258 | -1.6377 | -99.8332 | 14.4374 | 14.3187 | 14.4959 | -109.0689 | -108.7067 | -0.64982 | 14.5314 | 14.4244 | 14.5325 | 14.3754 | -109.2087 | -0.199 | -0.17439 | 0.24415 | 9.0367 | 9.2357 | -0.29316 | -0.11593 | -0.33875 | -0.18746 | 0.16325 | 123.4014 | 123.7401 | -0.079361 | -0.23641 | 123.3074 | 123.1886 | 123.3658 | 107.2322 | -123.6808 | 123.2943 | 123.4024 | 123.2453 | 108.2201 | -123.8205
848.2656 | 123.6694 | -109.2041 | 14.209 | 0.047088 | -0.046191 | -0.01656 | 0.037433 | -0.0065769 | 0.022687 | 0.050216 | -0.0124 | -0.011804 | 0.10867 | 0.20314 | 0.017158 | -108.8547 | -1.6469 | -99.3571 | 14.2039 | 14.0806 | 14.267 | -109.2979 | -108.9494 | -0.66813 | 14.2933 | 14.1909 | 14.2944 | 14.1282 | -109.4468 | -0.093779 | -0.005059 | 0.3494 | 9.847 | 9.9408 | -0.12843 | 0.057971 | -0.24268 | -0.018132 | 0.25475 | 123.4974 | 123.7401 | 0.085384 | -0.080823 | 123.408 | 123.2847 | 123.4711 | 107.5572 | -123.5069 | 123.395 | 123.4985 | 123.3323 | 108.536 | -123.6558
849.2812 | 123.6145 | -108.8928 | 14.5432 | 0.047088 | -0.048328 | -0.015492 | 0.037433 | -0.0087139 | 0.025892 | 0.080738 | -0.0124 | -0.010735 | 0.10867 | 0.2042 | 0.017158 | -108.6304 | -1.656 | -98.9771 | 14.4237 | 14.3049 | 14.4913 | -109.0689 | -108.725 | -0.65897 | 14.5177 | 14.4198 | 14.5233 | 14.3571 | -109.2178 | -0.17611 | -0.11946 | 0.26246 | 9.9157 | 10.0918 | -0.23823 | -0.051846 | -0.32502 | -0.12338 | 0.16782 | 123.4105 | 123.7355 | -0.019854 | -0.18606 | 123.3165 | 123.1977 | 123.3841 | 107.2368 | -123.6121 | 123.3126 | 123.4161 | 123.2499 | 108.2338 | -123.761
850.2656 | 123.6008 | -108.9935 | 14.4424 | 0.031826 | -0.048328 | -0.015492 | 0.037433 | -0.0076459 | 0.024824 | 0.080738 | -0.011332 | -0.01394 | 0.11081 | 0.20527 | 0.01609 | -108.9005 | -1.6744 | -98.5101 | 14.1627 | 14.0348 | 14.2212 | -109.3482 | -108.9997 | -0.69103 | 14.2475 | 14.1451 | 14.2532 | 14.0824 | -109.488 | -0.35472 | -0.27973 | 0.093044 | 10.4834 | 10.8381 | -0.40768 | -0.22128 | -0.49446 | -0.29738 | -0.006189 | 123.2411 | 123.7355 | -0.18928 | -0.36007 | 123.1562 | 123.0283 | 123.2147 | 107.3192 | -123.7907 | 123.1386 | 123.2467 | 123.0759 | 108.3025 | -123.9304
851.2656 | 123.5596 | -109.9045 | 13.5956 | 0.047088 | -0.047259 | -0.01656 | 0.038501 | -0.0097819 | 0.024824 | 0.080738 | -0.011332 | -0.010735 | 0.10867 | 0.20314 | 0.017158 | -109.3858 | -1.7018 | -98.8764 | 13.6774 | 13.5494 | 13.7313 | -109.8336 | -109.4759 | -0.72766 | 13.6798 | 13.6597 | 13.7541 | 13.5925 | -109.9825 | 0.070865 | 0.081829 | 0.51869 | 11.0281 | 10.9572 | -0.046184 | 0.13568 | -0.07802 | 0.064165 | 0.42858 | 123.5843 | 123.6623 | 0.15851 | -0.003117 | 123.5819 | 123.4539 | 123.6357 | 108.2026 | -123.4292 | 123.5642 | 123.6586 | 123.4969 | 109.1768 | -123.5781
852.2656 | 123.5138 | -110.3531 | 13.1836 | 0.077612 | -0.048328 | -0.01656 | 0.038501 | -0.0076459 | 0.024824 | 0.065477 | -0.0124 | -0.012872 | 0.10867 | 0.2042 | 0.017158 | -109.8803 | -1.711 | -99.673 | 13.1829 | 13.0503 | 13.2322 | -110.3373 | -109.9796 | -0.75513 | 13.1761 | 13.1653 | 13.2596 | 13.1071 | -110.4724 | 0.015791 | -0.00065 | 0.47283 | 10.6801 | 10.6643 | -0.1333 | 0.048597 | -0.11935 | -0.018325 | 0.37353 | 123.5292 | 123.6486 | 0.07601 | -0.076462 | 123.536 | 123.4034 | 123.5853 | 108.6421 | -123.5209 | 123.5184 | 123.6127 | 123.4602 | 109.598 | -123.656
853.2656 | 123.6603 | -109.5062 | 13.9938 | 0.047088 | -0.048328 | -0.017629 | 0.03957 | -0.0087139 | 0.023756 | 0.080738 | -0.0124 | -0.011804 | 0.10974 | 0.2042 | 0.01609 | -109.395 | -1.7156 | -98.3957 | 13.6591 | 13.5402 | 13.7129 | -109.8565 | -109.4942 | -0.74597 | 13.7301 | 13.6506 | 13.7587 | 13.5558 | -109.9871 | -0.35028 | -0.33474 | 0.11127 | 11.1106 | 11.4609 | -0.4536 | -0.28089 | -0.48085 | -0.34325 | 0.012006 | 123.2364 | 123.7172 | -0.23516 | -0.438 | 123.1653 | 123.0465 | 123.2192 | 107.7907 | -123.8503 | 123.1568 | 123.2649 | 123.0621 | 108.7603 | -123.9809
854.2812 | 123.6969 | -110.408 | 12.9776 | 0.047088 | -0.047259 | -0.015492 | 0.038501 | -0.0076459 | 0.023756 | 0.065477 | -0.0124 | -0.010735 | 0.10653 | 0.20207 | 0.017158 | -110.0817 | -1.7293 | -98.7757 | 12.9678 | 12.8305 | 13.0307 | -110.5433 | -110.1856 | -0.7826 | 13.0021 | 12.9501 | 13.0673 | 12.8919 | -110.6831 | -0.13533 | -0.00984 | 0.32631 | 11.6324 | 11.7677 | -0.14709 | 0.053132 | -0.27504 | -0.02752 | 0.22241 | 123.4101 | 123.6852 | 0.089702 | -0.085662 | 123.3758 | 123.2385 | 123.4388 | 108.6787 | -123.5209 | 123.3581 | 123.4753 | 123.3 | 109.6254 | -123.6607
855.2656 | 123.5504 | -110.7742 | 12.7121 | 0.031826 | -0.049396 | -0.015492 | 0.038501 | -0.0065769 | 0.023756 | 0.034955 | -0.011332 | -0.010735 | 0.10653 | 0.2042 | 0.019295 | -110.4297 | -1.743 | -98.3865 | 12.629 | 12.4962 | 12.6873 | -110.8913 | -110.529 | -0.83297 | 12.6541 | 12.6113 | 12.7148 | 12.5531 | -111.0265 | -0.11712 | -0.083138 | 0.34456 | 12.3877 | 12.5048 | -0.21585 | -0.02476 | -0.25224 | -0.10083 | 0.24522 | 123.4284 | 123.6806 | 0.002653 | -0.15897 | 123.4032 | 123.2705 | 123.4616 | 109.0312 | -123.6034 | 123.3855 | 123.489 | 123.3274 | 109.9413 | -123.7386
856.2656 | 123.587 | -110.9528 | 12.5656 | 0.047088 | -0.050464 | -0.014424 | 0.038501 | -0.0065769 | 0.025892 | 0.065477 | -0.014536 | -0.012872 | 0.1076 | 0.20314 | 0.018226 | -110.5945 | -1.7705 | -99.4212 | 12.4596 | 12.3406 | 12.5271 | -111.0608 | -110.6847 | -0.84212 | 12.4527 | 12.4602 | 12.5499 | 12.3883 | -111.1913 | -0.10801 | -0.10605 | 0.35827 | 11.5316 | 11.6396 | -0.22505 | -0.038527 | -0.23855 | -0.10543 | 0.26807 | 123.4054 | 123.644 | -0.015693 | -0.17732 | 123.4123 | 123.2933 | 123.4798 | 109.1822 | -123.6264 | 123.4129 | 123.5027 | 123.3411 | 110.1106 | -123.7569
857.2656 | 123.5458 | -110.8154 | 12.6846 | 0.031826 | -0.048328 | -0.01656 | 0.03957 | -0.0076459 | 0.024824 | 0.065477 | -0.013468 | -0.012872 | 0.10867 | 0.20527 | 0.017158 | -110.4846 | -1.7751 | -99.1328 | 12.5694 | 12.4413 | 12.6324 | -110.9417 | -110.5748 | -0.8467 | 12.5946 | 12.5563 | 12.6644 | 12.4982 | -111.0814 | -0.12628 | -0.11519 | 0.33082 | 11.6827 | 11.809 | -0.24333 | -0.052237 | -0.26599 | -0.1283 | 0.24064 | 123.4101 | 123.676 | -0.020246 | -0.18645 | 123.3849 | 123.2567 | 123.4478 | 109.0403 | -123.6263 | 123.3718 | 123.4798 | 123.3136 | 109.9687 | -123.766
858.2656 | 123.5779 | -111.0397 | 12.442 | 0.06235 | -0.046191 | -0.017629 | 0.040638 | -0.0065769 | 0.023756 | 0.080738 | -0.0124 | -0.011804 | 0.1076 | 0.20314 | 0.018226 | -110.6632 | -1.7797 | -98.3132 | 12.3817 | 12.2536 | 12.4584 | -111.1569 | -110.7534 | -0.94285 | 12.3748 | 12.3823 | 12.4812 | 12.3059 | -111.2508 | -0.11719 | -0.060291 | 0.37657 | 12.7265 | 12.8437 | -0.18846 | 0.01639 | -0.2111 | -0.059671 | 0.28637 | 123.4146 | 123.6257 | 0.039224 | -0.13614 | 123.4215 | 123.2933 | 123.4981 | 109.2601 | -123.5989 | 123.4221 | 123.521 | 123.3456 | 110.0969 | -123.6928
859.2812 | 123.5916 | -111.1221 | 12.323 | 0.047088 | -0.049396 | -0.015492 | 0.040638 | -0.0065769 | 0.023756 | 0.050216 | -0.0124 | -0.010735 | 0.10653 | 0.2042 | 0.017158 | -110.773 | -1.7888 | -98.2125 | 12.2718 | 12.1391 | 12.3394 | -111.2439 | -110.8724 | -0.99322 | 12.2787 | 12.2633 | 12.3668 | 12.1548 | -111.3836 | -0.12179 | -0.051153 | 0.34908 | 12.9096 | 13.0314 | -0.18391 | 0.016365 | -0.26149 | -0.059693 | 0.24972 | 123.4008 | 123.6623 | 0.043778 | -0.16822 | 123.394 | 123.2612 | 123.4615 | 109.3333 | -123.5669 | 123.3854 | 123.4889 | 123.2769 | 110.1289 | -123.7066
860.2656 | 123.5596 | -110.5179 | 12.9547 | 0.031826 | -0.049396 | -0.017629 | 0.040638 | -0.0055089 | 0.024824 | 0.050216 | -0.011332 | -0.010735 | 0.10867 | 0.2042 | 0.018226 | -110.1138 | -1.7842 | -96.1157 | 12.9403 | 12.8122 | 12.9941 | -110.5662 | -110.2085 | -0.87418 | 12.9701 | 12.9272 | 13.0353 | 12.8507 | -110.7105 | -0.04836 | -0.014422 | 0.40412 | 14.4022 | 14.4506 | -0.14252 | 0.039391 | -0.19265 | -0.027525 | 0.30938 | 123.488 | 123.6806 | 0.08054 | -0.10398 | 123.4582 | 123.3301 | 123.512 | 108.7336 | -123.521 | 123.4451 | 123.5531 | 123.3686 | 109.6437 | -123.6652
861.2656 | 123.5184 | -110.7376 | 12.7533 | 0.047088 | -0.048328 | -0.01656 | 0.040638 | -0.0055089 | 0.024824 | 0.034955 | -0.011332 | -0.010735 | 0.1076 | 0.20527 | 0.017158 | -110.1321 | -1.7888 | -96.2713 | 12.9174 | 12.7893 | 12.9758 | -110.5937 | -110.2314 | -0.89707 | 12.9701 | 12.9043 | 13.0124 | 12.8278 | -110.7334 | 0.14389 | 0.1641 | 0.60554 | 14.4663 | 14.3224 | 0.035999 | 0.22249 | 0.004184 | 0.151 | 0.50622 | 123.7077 | 123.7035 | 0.25906 | 0.074542 | 123.655 | 123.5269 | 123.7134 | 108.9488 | -123.347 | 123.6419 | 123.75 | 123.5654 | 109.8405 | -123.4867
862.2656 | 123.5458 | -111.2228 | 12.3047 | 0.06235 | -0.048328 | -0.015492 | 0.040638 | -0.0033719 | 0.023756 | 0.050216 | -0.014536 | -0.012872 | 0.10547 | 0.2042 | 0.01609 | -110.828 | -1.8117 | -96.1843 | 12.2077 | 12.0841 | 12.2753 | -111.308 | -110.9365 | -1.2954 | 12.2466 | 12.2038 | 12.3027 | 12.1227 | -111.4431 | -0.08519 | -0.09694 | 0.39485 | 15.0385 | 15.1237 | -0.22055 | -0.029424 | -0.2203 | -0.1009 | 0.28633 | 123.4695 | 123.6898 | -0.002011 | -0.18195 | 123.4306 | 123.307 | 123.4981 | 109.4111 | -123.6127 | 123.4266 | 123.5255 | 123.3456 | 109.9274 | -123.7478
863.2656 | 123.5916 | -111.5387 | 11.9476 | 0.06235 | -0.049396 | -0.017629 | 0.042775 | -0.0023039 | 0.025892 | 0.065477 | -0.022013 | -0.012872 | 0.013598 | 0.11019 | 0.01609 | -110.5762 | -1.8575 | -94.9024 | 12.4733 | 12.3589 | 12.5408 | -110.8181 | -110.6938 | -9.1983 | -109.6111 | 12.4693 | 12.5545 | 12.37 | -111.0494 | 0.72061 | 0.52566 | 0.96252 | 16.6363 | 15.9157 | 0.41124 | 0.59319 | 0.48933 | 0.52171 | 0.84485 | 1.9276 | 1.4382 | 0.60687 | 0.42234 | 124.012 | 123.8976 | 124.0795 | 109.6812 | -122.7657 | 124.008 | 124.0932 | 123.9087 | 102.3404 | -122.997
864.2812 | 123.6694 | -114.212 | 9.1141 | 0.031826 | -0.049396 | -0.020834 | 0.099401 | 0.061795 | 0.024824 | 0.080738 | -0.018809 | -0.012872 | 0.011461 | 0.11339 | 0.01609 | -113.5063 | -0.98299 | -9.0505 | 9.6347 | 9.5383 | 9.7204 | -114.06 | -113.6608 | -9.7294 | -113.2558 | 9.5116 | 9.6425 | 9.6274 | -114.0943 | 0.15207 | 0.52062 | 0.70569 | 105.1615 | 105.0095 | 0.42418 | 0.60633 | 0.11776 | 0.39756 | 0.55119 | 0.95624 | 0.83848 | 0.52843 | 0.51332 | 123.8467 | 123.7503 | 123.9324 | 113.229 | -123.174 | 123.7237 | 123.8545 | 123.8394 | 104.4826 | -123.2084
865.2656 | 123.5779 | -114.8621 | 8.6746 | 0.031826 | -0.050464 | -0.019766 | 0.10047 | 0.062863 | 0.024824 | 0.080738 | -0.016673 | -0.015009 | 0.0093254 | 0.11232 | 0.01609 | -114.477 | -0.98757 | -9.783 | 8.6366 | 8.5813 | 8.6994 | -115.0719 | -114.6086 | -9.5646 | -114.2585 | 8.5501 | 8.6535 | 8.6888 | -115.1291 | -0.20984 | -0.038017 | 0.3851 | 105.079 | 105.2889 | -0.093358 | 0.024752 | -0.26703 | -0.12448 | 0.25342 | 0.60353 | 0.87056 | -0.021093 | 0.014159 | 123.4987 | 123.4433 | 123.5614 | 113.8745 | -123.7465 | 123.4122 | 123.5156 | 123.5508 | 105.2975 | -123.8037
866.2656 | 123.587 | -116.478 | 7.0358 | 0.031826 | -0.048328 | -0.019766 | 0.10047 | 0.062863 | 0.023756 | 0.080738 | -0.017741 | -0.012872 | 0.010393 | 0.11446 | 0.017158 | -115.9833 | -1.015 | -9.925 | 7.112 | 7.0565 | 7.1839 | -116.6104 | -116.1288 | -9.5554 | -115.8336 | 7.0164 | 7.1334 | 7.1641 | -116.6676 | -0.13246 | 0.076174 | 0.49471 | 106.553 | 106.6855 | 0.020654 | 0.14803 | -0.18961 | -0.019478 | 0.3492 | 0.64436 | 0.83397 | 0.097605 | 0.12828 | 123.59 | 123.5344 | 123.6618 | 115.4629 | -123.6463 | 123.4943 | 123.6114 | 123.6421 | 106.9226 | -123.7034
867.2656 | 123.5779 | -116.954 | 6.5643 | 0.047088 | -0.052601 | -0.021902 | 0.10261 | 0.062863 | 0.024824 | 0.065477 | -0.017741 | -0.012872 | 0.0093254 | 0.11446 | 0.015022 | -116.5647 | -1.0288 | -9.6503 | 6.526 | 6.475 | 6.607 | -117.1919 | -116.7103 | -9.5783 | -116.3831 | 6.444 | 6.5474 | 6.5872 | -117.2491 | -0.23791 | -0.038363 | 0.38933 | 107.3038 | 107.5417 | -0.089373 | 0.042622 | -0.29504 | -0.12029 | 0.24377 | 0.57099 | 0.86603 | -0.016959 | 0.022871 | 123.48 | 123.429 | 123.561 | 115.9253 | -123.7563 | 123.3981 | 123.5014 | 123.5412 | 107.3757 | -123.8134
868.2656 | 123.317 | -117.1646 | 6.3492 | 0.047088 | -0.049396 | -0.017629 | 0.10368 | 0.065 | 0.026961 | 0.050216 | -0.017741 | -0.012872 | 0.0082564 | 0.11553 | 0.01609 | -116.7662 | -1.0379 | -9.6503 | 6.2467 | 6.2781 | 6.4055 | -117.3934 | -116.9026 | -9.5371 | -116.612 | 6.2517 | 6.3505 | 6.3949 | -117.4368 | -0.22881 | -0.1025 | 0.39846 | 107.5143 | 107.7432 | -0.071117 | 0.056312 | -0.2722 | -0.097441 | 0.26204 | 0.55262 | 0.82483 | 0.00131 | 0.045719 | 123.4113 | 123.4427 | 123.5701 | 116.1267 | -123.7426 | 123.4164 | 123.5151 | 123.5595 | 107.6275 | -123.786
869.2812 | 123.6145 | -117.2241 | 6.2942 | 0.077612 | -0.048328 | -0.019766 | 0.10154 | 0.067136 | 0.024824 | 0.050216 | -0.018809 | -0.01394 | 0.0093254 | 0.11446 | 0.015022 | -116.8119 | -1.0608 | -10.1081 | 6.1872 | 6.2369 | 6.3551 | -117.4438 | -116.9484 | -9.4364 | -116.6852 | 6.1968 | 6.3047 | 6.34 | -117.4872 | -0.21967 | -0.10708 | 0.41218 | 107.116 | 107.3357 | -0.057396 | 0.06088 | -0.26306 | -0.097451 | 0.27576 | 0.53887 | 0.80193 | 0.010456 | 0.045708 | 123.4113 | 123.461 | 123.5793 | 116.1633 | -123.738 | 123.4209 | 123.5288 | 123.5641 | 107.7878 | -123.7814
870.2656 | 123.2986 | -117.5262 | 6.015 | 0.031826 | -0.050464 | -0.020834 | 0.10047 | 0.065 | 0.022687 | 0.065477 | -0.018809 | -0.012872 | 0.0093254 | 0.11446 | 0.015022 | -117.0638 | -1.0746 | -10.3095 | 5.9399 | 5.9759 | 6.1079 | -117.7002 | -117.2048 | -9.5142 | -116.9188 | 5.945 | 6.0483 | 6.079 | -117.7482 | -0.17396 | -0.075081 | 0.46249 | 107.2167 | 107.3907 | -0.039159 | 0.09287 | -0.22193 | -0.070033 | 0.32148 | 0.60748 | 0.82941 | 0.03329 | 0.063963 | 123.4662 | 123.5021 | 123.6341 | 116.4517 | -123.7152 | 123.4712 | 123.5746 | 123.6052 | 108.012 | -123.7632
871.2656 | 123.2986 | -117.6361 | 5.8914 | 0.047088 | -0.050464 | -0.020834 | 0.10154 | 0.065 | 0.022687 | 0.065477 | -0.018809 | -0.012872 | 0.010393 | 0.1166 | 0.015022 | -117.2057 | -1.0929 | -10.4652 | 5.798 | 5.8385 | 5.9614 | -117.7368 | -117.3467 | -9.6012 | -117.0836 | 5.8076 | 5.9064 | 5.9462 | -117.8901 | -0.10073 | -0.093414 | 0.43043 | 107.1709 | 107.2716 | -0.05293 | 0.069952 | -0.25401 | -0.083791 | 0.2894 | 0.55251 | 0.80652 | 0.01495 | 0.05478 | 123.4341 | 123.4746 | 123.5975 | 116.5432 | -123.6283 | 123.4437 | 123.5425 | 123.5823 | 108.0349 | -123.7815
872.2656 | 123.4177 | -117.8604 | 5.6625 | 0.047088 | -0.051533 | -0.020834 | 0.10154 | 0.063931 | 0.022687 | 0.050216 | -0.016673 | -0.01394 | 0.0093254 | 0.11339 | 0.015022 | -117.4209 | -1.102 | -10.3004 | 5.5782 | 5.6233 | 5.7416 | -117.9383 | -117.5573 | -9.7248 | -117.3171 | 5.597 | 5.7003 | 5.731 | -118.1053 | -0.077899 | -0.084295 | 0.43955 | 107.56 | 107.6379 | -0.039259 | 0.07906 | -0.24491 | -0.065521 | 0.30308 | 0.5433 | 0.78821 | 0.037794 | 0.068467 | 123.4387 | 123.4837 | 123.602 | 116.7584 | -123.6008 | 123.4574 | 123.5607 | 123.5914 | 108.1356 | -123.7679
873.2656 | 123.3719 | -117.5858 | 5.9097 | 0.06235 | -0.052601 | -0.021902 | 0.10261 | 0.066068 | 0.022687 | 0.065477 | -0.017741 | -0.01394 | 0.010393 | 0.11446 | 0.015022 | -117.2194 | -1.1204 | -10.4606 | 5.7705 | 5.6462 | 5.9431 | -117.7597 | -117.365 | -9.766 | -117.1111 | 5.7847 | 5.8926 | 5.9279 | -117.913 | -0.17398 | -0.13919 | 0.36634 | 107.1251 | 107.2991 | -0.26356 | 0.033326 | -0.32726 | -0.12499 | 0.22073 | 0.47468 | 0.80194 | -0.017097 | 0.018155 | 123.3563 | 123.2319 | 123.5288 | 116.4654 | -123.6695 | 123.3705 | 123.4784 | 123.5136 | 107.8197 | -123.8227
874.2812 | 123.642 | -117.6361 | 5.8273 | 0.047088 | -0.050464 | -0.020834 | 0.10047 | 0.063931 | 0.023756 | 0.050216 | -0.015604 | -0.015009 | 0.010393 | 0.11767 | 0.015022 | -117.2652 | -1.1387 | -10.6026 | 5.7202 | 5.6095 | 5.8927 | -117.7964 | -117.4154 | -9.9583 | -117.1752 | 5.7344 | 5.8377 | 5.8684 | -117.9634 | -0.16026 | -0.10716 | 0.37091 | 107.0336 | 107.1938 | -0.21779 | 0.065359 | -0.32727 | -0.092961 | 0.22072 | 0.46094 | 0.78821 | 0.010357 | 0.04103 | 123.3563 | 123.2456 | 123.5288 | 116.4974 | -123.6237 | 123.3705 | 123.4738 | 123.5045 | 107.6778 | -123.7907
875.2656 | 123.5367 | -117.7048 | 5.8411 | 0.031826 | -0.051533 | -0.020834 | 0.099401 | 0.062863 | 0.023756 | 0.080738 | -0.017741 | -0.01394 | 0.0093254 | 0.11446 | 0.015022 | -117.2606 | -1.1524 | -10.7262 | 5.7293 | 5.6095 | 5.8973 | -117.8009 | -117.3971 | -10.0957 | -117.1477 | 5.7435 | 5.8514 | 5.8867 | -117.9496 | -0.096171 | -0.11174 | 0.44415 | 106.9786 | 107.0748 | -0.23152 | 0.056205 | -0.24487 | -0.097536 | 0.3077 | 0.55707 | 0.80194 | 0.010361 | 0.045612 | 123.4341 | 123.3143 | 123.602 | 116.5524 | -123.642 | 123.4483 | 123.5562 | 123.5914 | 107.6091 | -123.7907
876.2656 | 123.5458 | -117.6361 | 5.9097 | 0.077612 | -0.051533 | -0.019766 | 0.099401 | 0.062863 | 0.023756 | 0.050216 | -0.018809 | -0.012872 | 0.010393 | 0.11553 | 0.015022 | -117.1782 | -1.1707 | -10.8315 | 5.8209 | 5.7057 | 5.9888 | -117.6956 | -117.3101 | -10.2422 | -117.0744 | 5.8351 | 5.9293 | 5.9691 | -117.8581 | -0.059521 | -0.088833 | 0.4579 | 106.8046 | 106.8642 | -0.20403 | 0.079112 | -0.22196 | -0.074631 | 0.32603 | 0.56167 | 0.78363 | 0.019532 | 0.059362 | 123.457 | 123.3418 | 123.6249 | 116.4654 | -123.6054 | 123.4712 | 123.5654 | 123.6052 | 107.3939 | -123.7678
877.2656 | 123.555 | -118.1351 | 5.3696 | 0.06235 | -0.052601 | -0.021902 | 0.10154 | 0.065 | 0.023756 | 0.050216 | -0.020945 | -0.015009 | 0.0093254 | 0.1166 | 0.013953 | -117.6727 | -1.2028 | -10.8223 | 5.331 | 5.2158 | 5.5081 | -118.1993 | -117.7954 | -10.5169 | -117.5415 | 5.336 | 5.4485 | 5.2594 | -118.3572 | -0.064239 | -0.038559 | 0.46239 | 107.3128 | 107.377 | -0.15381 | 0.13852 | -0.22209 | -0.033526 | 0.33965 | 0.5936 | 0.81569 | 0.07894 | -0.11016 | 123.4661 | 123.3508 | 123.6432 | 116.9323 | -123.5689 | 123.4711 | 123.5836 | 123.3945 | 107.6181 | -123.7267
878.2656 | 123.5596 | -118.2129 | 5.3055 | 0.06235 | -0.051533 | -0.021902 | 0.10047 | 0.065 | 0.023756 | 0.080738 | -0.017741 | -0.01394 | 0.0082564 | 0.1166 | 0.01609 | -117.7734 | -1.2302 | -11.065 | 5.2211 | 5.1104 | 5.3982 | -118.3046 | -117.9099 | -10.7596 | -117.6834 | 5.2307 | 5.334 | 5.1266 | -118.467 | -0.091735 | -0.084353 | 0.43949 | 107.1479 | 107.2397 | -0.19504 | 0.092721 | -0.25416 | -0.074744 | 0.303 | 0.52948 | 0.78364 | 0.028562 | -0.17885 | 123.434 | 123.3233 | 123.6111 | 116.9827 | -123.6101 | 123.4436 | 123.5469 | 123.3395 | 107.4533 | -123.7725
879.2969 | 123.5413 | -118.2541 | 5.2689 | 0.06235 | -0.051533 | -0.019766 | 0.10047 | 0.065 | 0.023756 | 0.065477 | -0.017741 | -0.01394 | 0.0093254 | 0.11553 | 0.013953 | -117.7826 | -1.2486 | -11.1199 | 5.2028 | 5.0784 | 5.3753 | -118.3229 | -117.9282 | -11.016 | -117.7017 | 5.2124 | 5.3203 | 5.1037 | -118.4899 | -0.068852 | -0.066046 | 0.47153 | 107.1342 | 107.203 | -0.19047 | 0.10645 | -0.23585 | -0.056437 | 0.32589 | 0.55237 | 0.78822 | 0.051447 | -0.16512 | 123.4569 | 123.3325 | 123.6294 | 117.0055 | -123.5918 | 123.4665 | 123.5744 | 123.3578 | 107.2381 | -123.7588
880.2656 | 123.5321 | -118.0939 | 5.4474 | 0.06235 | -0.052601 | -0.019766 | 0.099401 | 0.062863 | 0.022687 | 0.065477 | -0.017741 | -0.01394 | 0.0082564 | 0.1166 | 0.013953 | -117.7047 | -1.276 | -11.5869 | 5.2852 | 5.17 | 5.4531 | -118.2451 | -117.8412 | -11.2037 | -117.5873 | 5.2903 | 5.3936 | 5.1953 | -118.4029 | -0.15123 | -0.16216 | 0.38915 | 106.507 | 106.6582 | -0.27742 | 0.005757 | -0.30907 | -0.15713 | 0.25266 | 0.50662 | 0.81569 | -0.053824 | -0.25208 | 123.3791 | 123.2638 | 123.547 | 116.8178 | -123.6925 | 123.3841 | 123.4874 | 123.2892 | 106.8901 | -123.8503
881.2656 | 123.5504 | -117.9153 | 5.5893 | 0.047088 | -0.053669 | -0.020834 | 0.10047 | 0.063931 | 0.023756 | 0.065477 | -0.017741 | -0.012872 | 0.0093254 | 0.11553 | 0.013953 | -117.4804 | -1.3035 | -11.7929 | 5.5004 | 5.3852 | 5.6729 | -118.0299 | -117.6214 | -11.3503 | -117.3675 | 5.5054 | 5.6179 | 5.3556 | -118.1969 | -0.11455 | -0.088885 | 0.43496 | 106.1224 | 106.237 | -0.20412 | 0.083624 | -0.28155 | -0.083848 | 0.29391 | 0.54787 | 0.82942 | 0.028622 | -0.23374 | 123.4158 | 123.3005 | 123.5883 | 116.6118 | -123.6192 | 123.4208 | 123.5333 | 123.2709 | 106.5651 | -123.7862
882.2656 | 123.5413 | -118.1854 | 5.3513 | 0.031826 | -0.052601 | -0.019766 | 0.099401 | 0.063931 | 0.024824 | 0.050216 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.01609 | -117.7093 | -1.3035 | -10.6117 | 5.2806 | 5.1654 | 5.4531 | -118.2543 | -117.8458 | -11.6341 | -117.6101 | 5.2857 | 5.3981 | 5.122 | -118.4121 | -0.068833 | -0.07061 | 0.47612 | 107.5737 | 107.6426 | -0.18587 | 0.10189 | -0.22668 | -0.065578 | 0.33964 | 0.57528 | 0.80196 | 0.046886 | -0.22921 | 123.4661 | 123.3508 | 123.6386 | 116.8819 | -123.6055 | 123.4711 | 123.5836 | 123.3075 | 106.5513 | -123.7634
883.2656 | 123.5275 | -118.2999 | 5.246 | 0.047088 | -0.051533 | -0.020834 | 0.099401 | 0.067136 | 0.023756 | 0.050216 | -0.017741 | -0.012872 | 0.0082564 | 0.11767 | 0.013953 | -117.8604 | -1.3172 | -10.0989 | 5.1204 | 5.0051 | 5.3021 | -118.4099 | -118.0015 | -11.8768 | -117.7612 | 5.13 | 5.2379 | 4.9893 | -118.5678 | -0.11008 | -0.12557 | 0.43947 | 108.2009 | 108.311 | -0.24085 | 0.056079 | -0.26792 | -0.11596 | 0.2984 | 0.53862 | 0.80654 | -0.00808 | -0.2567 | 123.4203 | 123.305 | 123.6019 | 116.9826 | -123.6559 | 123.4299 | 123.5378 | 123.2891 | 106.4231 | -123.8138
884.2812 | 123.6191 | -118.2587 | 5.2322 | 0.031826 | -0.052601 | -0.020834 | 0.10154 | 0.066068 | 0.023756 | 0.080738 | -0.017741 | -0.01394 | 0.0093254 | 0.11446 | 0.013953 | -117.8604 | -1.3447 | -10.2317 | 5.1204 | 5.0097 | 5.2883 | -118.4054 | -117.9877 | -11.8173 | -117.7475 | 5.1346 | 5.2333 | 4.9801 | -118.5632 | -0.14669 | -0.11184 | 0.39828 | 108.027 | 108.1737 | -0.22254 | 0.056076 | -0.30454 | -0.097651 | 0.27094 | 0.51116 | 0.8157 | 0.001074 | -0.25213 | 123.3791 | 123.2684 | 123.547 | 116.914 | -123.6376 | 123.3933 | 123.492 | 123.2388 | 106.4414 | -123.7954
885.2656 | 123.5641 | -118.4052 | 5.0903 | 0.047088 | -0.053669 | -0.020834 | 0.10154 | 0.063931 | 0.021619 | 0.065477 | -0.019877 | -0.01394 | 0.0093254 | 0.1166 | 0.013953 | -117.9382 | -1.3768 | -9.9753 | 5.0471 | 4.9319 | 5.2151 | -118.4832 | -118.0701 | -12.5133 | -117.7979 | 5.0613 | 5.1601 | 4.9069 | -118.6365 | -0.078053 | -0.043183 | 0.46693 | 108.4298 | 108.5079 | -0.15847 | 0.12473 | -0.23131 | -0.029 | 0.33501 | 0.60728 | 0.83859 | 0.069724 | -0.18348 | 123.4523 | 123.337 | 123.6202 | 117.0284 | -123.5735 | 123.4665 | 123.5652 | 123.312 | 105.8919 | -123.7268
886.2656 | 123.5275 | -118.3182 | 5.2094 | 0.047088 | -0.051533 | -0.020834 | 0.10047 | 0.066068 | 0.022687 | 0.080738 | -0.016673 | -0.01394 | 0.0082564 | 0.1166 | 0.013953 | -117.9062 | -1.3996 | -9.3802 | 5.07 | 4.9593 | 5.2425 | -118.4557 | -118.0335 | -12.7605 | -117.7796 | 5.0888 | 5.1875 | 4.9297 | -118.6136 | -0.13755 | -0.13931 | 0.412 | 108.938 | 109.0756 | -0.25002 | 0.033178 | -0.29539 | -0.12055 | 0.28466 | 0.53862 | 0.83401 | -0.021824 | -0.2796 | 123.3882 | 123.2775 | 123.5607 | 116.9185 | -123.6651 | 123.407 | 123.5057 | 123.2479 | 105.5577 | -123.8229
887.2656 | 123.5367 | -65.7761 | 57.6096 | 0.047088 | -0.0045252 | -0.017629 | -0.043767 | -0.03649 | -0.03607 | 0.034955 | -0.017741 | -0.011804 | 0.0082564 | 0.11873 | 0.015022 | -0.099677 | 0.05635 | -0.026723 | 0.070441 | -0.04543 | 0.20607 | -0.26453 | -65.795 | -5.9108 | -65.6006 | 57.54 | 57.6446 | 57.5287 | -66.035 | 65.5115 | -57.5391 | 65.6764 | 65.7493 | 0.23781 | -57.655 | -57.4035 | -0.25895 | -0.069514 | -0.018951 | 0.17548 | 0.43443 | 0.035018 | -0.080824 | 65.8465 | 65.7306 | 65.9821 | 65.8324 | -57.8741 | 123.3161 | 123.4206 | 123.3048 | 59.8653 | -123.6446
888.2656 | 123.5458 | -66.1194 | 57.3349 | 0.047088 | -0.0034562 | -0.01656 | -0.042698 | -0.03649 | -0.035002 | 0.050216 | -0.016673 | -0.01394 | 0.0082564 | 0.1166 | 0.012885 | -0.040158 | 0.051771 | -0.022144 | 0.056706 | -0.054588 | 0.19691 | -0.053899 | -66.0789 | -6.2862 | -65.8661 | 57.247 | 57.3561 | 57.2494 | -66.3235 | 66.0655 | -57.2782 | 66.0792 | 66.0972 | 0.031755 | -57.3895 | -57.138 | -0.20409 | -0.08788 | 0.040492 | 0.25324 | 0.45733 | 0.021224 | -0.085461 | 66.1761 | 66.0648 | 66.3163 | 66.1712 | -57.3888 | 123.3664 | 123.4755 | 123.3688 | 59.8332 | -123.6584
889.2812 | 123.6832 | -66.2384 | 57.1198 | 0.06235 | -0.0034562 | -0.017629 | -0.04163 | -0.03649 | -0.035002 | 0.050216 | -0.016673 | -0.011804 | 0.012529 | 0.1166 | 0.015022 | -0.03558 | 0.060928 | -0.017566 | 0.038393 | -0.059167 | 0.20607 | -0.040163 | -66.3948 | -6.6388 | -66.1592 | 56.9357 | 57.0448 | 56.9244 | -66.6486 | 66.1982 | -57.0814 | 66.2028 | 66.2208 | 0.022597 | -57.1789 | -56.9137 | -0.41017 | -0.18407 | -0.15642 | 0.079218 | 0.48939 | -0.074972 | -0.19539 | 66.2768 | 66.1792 | 66.4445 | 66.2993 | -57.1599 | 123.1741 | 123.2832 | 123.1628 | 59.5996 | -123.7683
890.2656 | 123.555 | -66.6687 | 56.7947 | 0.047088 | -0.0055932 | -0.018697 | -0.04163 | -0.03649 | -0.033933 | 0.034955 | -0.016673 | -0.012872 | 0.0093254 | 0.11767 | 0.013953 | -0.031001 | 0.047193 | -0.012988 | 0.052128 | -0.054588 | 0.20149 | -0.040163 | -66.61 | -6.8631 | -66.3835 | 56.7159 | 56.8204 | 56.7092 | -66.8684 | 66.6285 | -56.7426 | 66.6377 | 66.6557 | 0.027175 | -56.8493 | -56.5933 | -0.19966 | -0.078824 | 0.058678 | 0.28516 | 0.48482 | 0.025689 | -0.085575 | 66.7208 | 66.6141 | 66.8702 | 66.7159 | -56.8349 | 123.3846 | 123.4891 | 123.3779 | 59.8056 | -123.6631
891.2656 | 123.4818 | -66.7374 | 56.7169 | 0.047088 | -0.0023882 | -0.018697 | -0.042698 | -0.035422 | -0.035002 | 0.050216 | -0.016673 | -0.012872 | 0.010393 | 0.11767 | 0.015022 | -0.031001 | 0.051771 | -0.012988 | 0.052128 | -0.040851 | 0.19691 | -0.035584 | -66.6467 | -7.06 | -66.4889 | 56.6106 | 56.7289 | 56.5901 | -66.9691 | 66.7018 | -56.6648 | 66.7064 | 66.7244 | 0.022596 | -56.7578 | -56.52 | -0.23173 | -0.10631 | 0.090713 | 0.24851 | 0.48024 | 0.011937 | -0.1268 | 66.7895 | 66.6965 | 66.9343 | 66.7891 | -56.7525 | 123.348 | 123.4662 | 123.3275 | 59.6774 | -123.686
892.2656 | 123.5596 | -67.0486 | 56.4056 | 0.047088 | -0.0055932 | -0.018697 | -0.043767 | -0.035422 | -0.035002 | 0.065477 | -0.017741 | -0.008599 | 0.0093254 | 0.11767 | 0.012885 | -0.017266 | 0.0243 | -0.008409 | 0.047549 | -0.04543 | 0.20607 | -0.040163 | -66.9534 | -7.2798 | -66.7773 | 56.313 | 56.4221 | 56.2879 | -67.2759 | 67.0085 | -56.3581 | 67.0314 | 67.0402 | 0.031754 | -56.4511 | -56.1996 | -0.22723 | -0.092633 | 0.095218 | 0.27133 | 0.49856 | 0.01645 | -0.11771 | 67.0962 | 67.0032 | 67.2547 | 67.0729 | -56.4458 | 123.3617 | 123.4707 | 123.3366 | 59.7689 | -123.6815
893.2656 | 123.5458 | -67.305 | 56.1493 | 0.077612 | -0.00025117 | -0.01656 | -0.042698 | -0.037559 | -0.030728 | 0.065477 | -0.016673 | -0.011804 | 0.0093254 | 0.11767 | 0.012885 | -0.026423 | 0.019721 | -0.008409 | 0.061284 | -0.050009 | 0.20149 | -0.031005 | -67.2419 | -7.4996 | -67.0658 | 56.0108 | 56.1107 | 56.0086 | -67.5827 | 67.274 | -56.088 | 67.2786 | 67.2966 | 0.022596 | -56.1993 | -55.9478 | -0.27766 | -0.13847 | 0.063108 | 0.23922 | 0.51688 | -0.038547 | -0.14065 | 67.3663 | 67.255 | 67.5065 | 67.3247 | -56.1803 | 123.3158 | 123.4157 | 123.3136 | 59.8054 | -123.7319
894.2812 | 123.6786 | -67.3233 | 56.0303 | 0.047088 | 0.0018858 | -0.017629 | -0.042698 | -0.035422 | -0.02966 | 0.034955 | -0.017741 | -0.011804 | 0.0093254 | 0.1166 | 0.013953 | -0.021844 | 0.019721 | -0.012988 | 0.065863 | -0.054588 | 0.20149 | -0.031005 | -67.251 | -7.6965 | -67.0612 | 56.0017 | 56.1107 | 55.9903 | -67.5781 | 67.2923 | -55.9644 | 67.3015 | 67.3103 | 0.018017 | -56.0849 | -55.8288 | -0.25477 | -0.028603 | 0.07226 | 0.26211 | 0.51688 | 0.080472 | -0.039949 | 67.3892 | 67.2687 | 67.5248 | 67.343 | -56.0613 | 123.325 | 123.434 | 123.3136 | 59.6269 | -123.6083
895.2656 | 123.5687 | -67.6849 | 55.806 | 0.016564 | -0.00025117 | -0.018697 | -0.04163 | -0.03649 | -0.028592 | 0.065477 | -0.018809 | -0.01394 | 0.0093254 | 0.1166 | 0.01609 | -0.021844 | 0.010564 | -0.003831 | 0.056706 | -0.054588 | 0.19691 | -0.040163 | -67.5807 | -8.0353 | -67.4 | 55.6766 | 55.7948 | 55.6607 | -67.9123 | 67.6448 | -55.7493 | 67.6631 | 67.6811 | 0.036332 | -55.8606 | -55.6091 | -0.22739 | -0.12937 | 0.10423 | 0.28492 | 0.51231 | -0.011148 | -0.14531 | 67.7416 | 67.6303 | 67.8818 | 67.6955 | -55.8461 | 123.3615 | 123.4798 | 123.3456 | 59.6497 | -123.7183
896.2656 | 123.5504 | -67.8772 | 55.6 | 0.092874 | -0.00025117 | -0.018697 | -0.040562 | -0.037559 | -0.030728 | 0.050216 | -0.017741 | -0.011804 | 0.0082564 | 0.1166 | 0.013953 | -0.021844 | 0.028878 | -0.017566 | 0.047549 | -0.050009 | 0.13739 | -0.040163 | -67.7318 | -8.6534 | -67.5191 | 55.5347 | 55.6437 | 55.5279 | -68.0589 | 67.837 | -55.5524 | 67.8554 | 67.8596 | 0.022597 | -55.65 | -55.4626 | -0.18165 | -0.065313 | 0.14539 | 0.35813 | 0.53979 | 0.043751 | -0.072091 | 67.9247 | 67.8272 | 68.0146 | 67.9061 | -55.6401 | 123.4119 | 123.5209 | 123.4051 | 59.2238 | -123.6588
897.2656 | 123.5641 | -67.6987 | 55.7739 | 0.047088 | -0.00025117 | -0.017629 | -0.042698 | -0.03649 | -0.030728 | 0.065477 | -0.016673 | -0.012872 | 0.010393 | 0.11767 | 0.015022 | -0.021844 | 0.015142 | -0.008409 | 0.056706 | -0.059167 | 0.12823 | -0.035584 | -67.6952 | -9.0426 | -67.4962 | 55.5621 | 55.6804 | 55.5508 | -68.0314 | 67.6631 | -55.7172 | 67.6768 | 67.6903 | 0.027175 | -55.8331 | -55.6457 | -0.33271 | -0.21179 | 0.003491 | 0.2025 | 0.53521 | -0.09357 | -0.22315 | 67.7554 | 67.6395 | 67.8269 | 67.7138 | -55.8095 | 123.2608 | 123.379 | 123.2494 | 58.6561 | -123.8053
898.2656 | 123.5687 | -68.0237 | 55.4214 | 0.031826 | -0.0013202 | -0.019766 | -0.042698 | -0.035422 | -0.02966 | 0.065477 | -0.017741 | -0.01394 | 0.010393 | 0.11873 | 0.013953 | -0.017266 | 0.010564 | -0.003831 | 0.061284 | -0.054588 | 0.12365 | -0.031005 | -67.9745 | -9.2395 | -67.7663 | 55.2828 | 55.4011 | 55.2715 | -68.3107 | 67.9927 | -55.3602 | 68.0064 | 68.0199 | 0.027174 | -55.476 | -55.2978 | -0.287 | -0.1386 | 0.049203 | 0.25737 | 0.54437 | -0.020387 | -0.14996 | 68.085 | 67.9691 | 68.1473 | 68.0342 | -55.4525 | 123.3065 | 123.4247 | 123.2952 | 58.7842 | -123.7321
899.2812 | 123.6969 | -67.9733 | 55.4169 | 0.06235 | -0.0013202 | -0.017629 | -0.042698 | -0.035422 | -0.030728 | 0.034955 | -0.017741 | -0.012872 | 0.0093254 | 0.11873 | 0.012885 | -0.012688 | 0.010564 | -0.017566 | 0.052128 | -0.050009 | 0.13281 | -0.026426 | -67.9058 | -5.7688 | -67.6976 | 55.3653 | 55.4789 | 55.3539 | -68.2328 | 67.9469 | -55.3647 | 67.9606 | 67.9558 | 0.00886 | -55.4669 | -55.2841 | -0.25952 | -0.051611 | 0.06753 | 0.2757 | 0.53521 | 0.062027 | -0.062972 | 68.0255 | 67.9233 | 68.1061 | 67.9839 | -55.4433 | 123.3386 | 123.4522 | 123.3272 | 62.2045 | -123.6497
900.2656 | 123.6237 | -68.3029 | 55.1605 | 0.06235 | -0.00025117 | -0.017629 | -0.04163 | -0.037559 | -0.031797 | 0.034955 | -0.017741 | -0.012872 | 0.0093254 | 0.11873 | 0.013953 | -0.012688 | 0.010564 | -0.017566 | 0.052128 | -0.054588 | 0.13281 | -0.031005 | -68.1988 | -5.6543 | -68.009 | 55.0722 | 55.1767 | 55.0471 | -68.5305 | 68.2719 | -55.1084 | 68.2902 | 68.2854 | 0.013439 | -55.2151 | -55.0277 | -0.22755 | -0.088287 | 0.10408 | 0.29393 | 0.52148 | 0.016188 | -0.11339 | 68.355 | 68.2483 | 68.4357 | 68.3135 | -55.1915 | 123.3752 | 123.4796 | 123.35 | 62.6486 | -123.691
901.2656 | 123.5916 | -68.5501 | 54.9133 | 0.06235 | 0.00081683 | -0.018697 | -0.043767 | -0.03649 | -0.02966 | 0.080738 | -0.017741 | -0.012872 | 0.0093254 | 0.11873 | 0.017158 | -0.017266 | 0.005985 | -0.003831 | 0.042971 | -0.050009 | 0.14197 | -0.026426 | -68.4323 | -5.4895 | -68.215 | 54.8296 | 54.9432 | 54.8045 | -68.7686 | 68.5237 | -54.8704 | 68.5328 | 68.5463 | 0.022595 | -54.9633 | -54.7714 | -0.21846 | -0.083755 | 0.11776 | 0.33508 | 0.55354 | 0.029871 | -0.10886 | 68.5931 | 68.5001 | 68.6921 | 68.5561 | -54.9398 | 123.3797 | 123.4933 | 123.3546 | 63.0606 | -123.6819
902.2656 | 123.6053 | -68.7012 | 54.7577 | 0.06235 | 0.00081683 | -0.018697 | -0.043767 | -0.03649 | -0.02966 | 0.050216 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.011817 | -0.021844 | 0.015142 | -0.008409 | 0.056706 | -0.054588 | 0.13739 | -0.035584 | -68.6109 | -5.2423 | -68.3982 | 54.6647 | 54.7738 | 54.6351 | -68.9471 | 68.6656 | -54.701 | 68.6793 | 68.6928 | 0.027175 | -54.8123 | -54.6203 | -0.24597 | -0.092941 | 0.090252 | 0.303 | 0.54897 | 0.016103 | -0.12263 | 68.7579 | 68.6466 | 68.8386 | 68.7163 | -54.7933 | 123.3659 | 123.475 | 123.3362 | 63.4589 | -123.7048
903.2656 | 123.5825 | -68.7927 | 54.6753 | 0.047088 | -0.00025117 | -0.019766 | -0.042698 | -0.037559 | -0.02966 | 0.080738 | -0.016673 | -0.011804 | 0.0082564 | 0.1198 | 0.015022 | -0.021844 | 0.010564 | -0.003831 | 0.061284 | -0.050009 | 0.11449 | -0.026426 | -68.7803 | -5.1736 | -68.5676 | 54.4862 | 54.5998 | 54.4702 | -69.1211 | 68.7663 | -54.614 | 68.7709 | 68.7889 | 0.022595 | -54.7253 | -54.5608 | -0.32841 | -0.18911 | 0.012393 | 0.22514 | 0.55355 | -0.075487 | -0.20507 | 68.854 | 68.7427 | 68.9072 | 68.8033 | -54.7017 | 123.2789 | 123.3925 | 123.263 | 63.6191 | -123.7964
904.2812 | 123.6008 | -68.7881 | 54.6799 | 0.06235 | -0.0013202 | -0.018697 | -0.042698 | -0.035422 | -0.02966 | 0.065477 | -0.015604 | -0.010735 | 0.010393 | 0.11873 | 0.013953 | -0.017266 | -0.003172 | -0.008409 | 0.042971 | -0.04543 | 0.12823 | -0.026426 | -68.8078 | -5.6223 | -68.5813 | 54.4496 | 54.5678 | 54.4382 | -69.1532 | 68.7617 | -54.6369 | 68.7709 | 68.7797 | 0.018017 | -54.7253 | -54.5516 | -0.36504 | -0.23031 | -0.019657 | 0.20682 | 0.57186 | -0.11211 | -0.24169 | 68.8311 | 68.7427 | 68.9164 | 68.785 | -54.7063 | 123.2377 | 123.3559 | 123.2263 | 63.1658 | -123.8331
905.2812 | 123.6969 | -68.9301 | 54.5013 | 0.047088 | -0.0013202 | -0.019766 | -0.042698 | -0.03649 | -0.030728 | 0.065477 | -0.017741 | -0.012872 | 0.010393 | 0.11873 | 0.012885 | -0.012688 | 0.001407 | -0.012988 | 0.038393 | -0.050009 | 0.13739 | -0.026426 | -69.2016 | -5.5994 | -68.9659 | 54.0512 | 54.1557 | 54.0398 | -69.547 | 68.9036 | -54.4629 | 68.9174 | 68.9171 | 0.013438 | -54.5514 | -54.364 | -0.61691 | -0.45011 | -0.27152 | -0.03588 | 0.58103 | -0.34566 | -0.4615 | 68.9684 | 68.88 | 69.0674 | 68.9315 | -54.5278 | 122.9813 | 123.0857 | 122.9699 | 63.3307 | -124.0483
906.2656 | 123.6465 | -69.1772 | 54.2999 | 0.06235 | -0.00025117 | -0.019766 | -0.043767 | -0.03649 | -0.02966 | 0.050216 | -0.017741 | -0.010735 | 0.010393 | 0.1198 | 0.013953 | -0.017266 | 0.001407 | -0.012988 | 0.052128 | -0.04543 | 0.13281 | -0.035584 | -69.0734 | -5.4941 | -68.8698 | 54.184 | 54.2839 | 54.1818 | -69.4233 | 69.1417 | -54.2478 | 69.16 | 69.1643 | 0.022596 | -54.3454 | -54.1671 | -0.24609 | -0.11592 | 0.10388 | 0.30746 | 0.55356 | -0.016045 | -0.11815 | 69.2294 | 69.1318 | 69.3101 | 69.1787 | -54.3355 | 123.3613 | 123.4611 | 123.359 | 63.6832 | -123.7233
907.2656 | 123.5962 | -69.0628 | 54.4235 | 0.06235 | -0.00025117 | -0.019766 | -0.042698 | -0.03649 | -0.02966 | 0.065477 | -0.017741 | -0.011804 | 0.010393 | 0.1198 | 0.012885 | -0.017266 | -0.003172 | -0.003831 | 0.033814 | -0.050009 | 0.14655 | -0.026426 | -68.9177 | -5.5582 | -68.6912 | 54.358 | 54.4624 | 54.3329 | -69.2585 | 69.0364 | -54.3897 | 69.0455 | 69.059 | 0.022595 | -54.4735 | -54.277 | -0.1957 | -0.065533 | 0.14511 | 0.37159 | 0.56729 | 0.038925 | -0.090653 | 69.0966 | 69.0128 | 69.2094 | 69.0596 | -54.4499 | 123.4208 | 123.5253 | 123.3957 | 63.5046 | -123.682
908.2656 | 123.642 | -69.4885 | 53.9749 | 0.06235 | -0.0013202 | -0.018697 | -0.042698 | -0.035422 | -0.030728 | 0.050216 | -0.017741 | -0.011804 | 0.0093254 | 0.11767 | 0.012885 | -0.012688 | -0.003172 | -0.008409 | 0.061284 | -0.04543 | 0.13281 | -0.026426 | -69.2977 | -7.0646 | -69.0529 | 53.978 | 54.0778 | 53.9574 | -69.634 | 69.4621 | -53.9136 | 69.4758 | 69.4801 | 0.018017 | -54.0203 | -53.8421 | -0.14544 | 0.00306 | 0.1908 | 0.43559 | 0.58103 | 0.10293 | -0.017491 | 69.5498 | 69.4431 | 69.6213 | 69.4854 | -54.0013 | 123.4665 | 123.5664 | 123.4459 | 62.4239 | -123.6089
909.2812 | 123.5733 | -69.8776 | 53.595 | 0.047088 | -0.0013202 | -0.018697 | -0.042698 | -0.035422 | -0.02966 | 0.065477 | -0.015604 | -0.011804 | 0.0082564 | 0.11873 | 0.013953 | -0.008109 | -0.003172 | -0.003831 | 0.056706 | -0.054588 | 0.13739 | -0.026426 | -69.7098 | -8.4016 | -69.465 | 53.5568 | 53.6658 | 53.5453 | -70.0552 | 69.8512 | -53.5383 | 69.8695 | 69.8738 | 0.022595 | -53.6496 | -53.4576 | -0.17759 | -0.038218 | 0.16781 | 0.41261 | 0.5902 | 0.0708 | -0.049621 | 69.9343 | 69.823 | 70.015 | 69.8745 | -53.6214 | 123.4344 | 123.5434 | 123.423 | 61.4761 | -123.6502
910.2812 | 123.6191 | -69.7815 | 53.6591 | 0.047088 | -0.0013202 | -0.019766 | -0.044835 | -0.03649 | -0.02966 | 0.080738 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.013953 | -0.017266 | -0.012329 | -0.008409 | 0.056706 | -0.059167 | 0.14197 | -0.031005 | -69.7876 | -7.3439 | -69.5566 | 53.4743 | 53.5834 | 53.4721 | -70.1331 | 69.7505 | -53.6024 | 69.7642 | 69.7731 | 0.022596 | -53.7182 | -53.5171 | -0.35156 | -0.18472 | -0.006154 | 0.22491 | 0.57647 | -0.075702 | -0.18697 | 69.8382 | 69.7223 | 69.9235 | 69.7692 | -53.6901 | 123.2558 | 123.3648 | 123.2536 | 62.4376 | -123.7921
911.2656 | 123.5916 | -70.079 | 53.4073 | 0.047088 | -0.0013202 | -0.019766 | -0.042698 | -0.037559 | -0.030728 | 0.050216 | -0.016673 | -0.011804 | 0.011461 | 0.11873 | 0.012885 | -0.017266 | 0.001407 | -0.003831 | 0.042971 | -0.054588 | 0.12365 | -0.026426 | -70.0898 | -5.7368 | -69.8771 | 53.1722 | 53.2766 | 53.1653 | -70.4444 | 70.0526 | -53.3643 | 70.0618 | 70.0752 | 0.022595 | -53.4619 | -53.2836 | -0.36537 | -0.23513 | -0.010802 | 0.20194 | 0.56732 | -0.1307 | -0.24196 | 70.122 | 70.0245 | 70.2027 | 70.0804 | -53.4337 | 123.2512 | 123.3556 | 123.2444 | 64.3423 | -123.8517
912.2656 | 123.6099 | -70.4819 | 53.0273 | 0.06235 | -0.0023882 | -0.019766 | -0.042698 | -0.03649 | -0.032865 | 0.080738 | -0.017741 | -0.012872 | 0.010393 | 0.1198 | 0.013953 | -0.026423 | -0.007751 | 0.000747 | 0.047549 | -0.04543 | 0.13739 | -0.021847 | -70.3371 | -6.4648 | -70.1152 | 52.9341 | 53.0385 | 52.9318 | -70.6825 | 70.46 | -52.9798 | 70.4554 | 70.4826 | 0.022594 | -53.0728 | -52.89 | -0.20064 | -0.093266 | 0.14478 | 0.36668 | 0.56732 | 0.011158 | -0.095527 | 70.5294 | 70.4364 | 70.6193 | 70.4741 | -53.0492 | 123.416 | 123.5204 | 123.4137 | 64.0171 | -123.7099
913.2656 | 123.5687 | -70.2209 | 53.2928 | 0.047088 | -0.0023882 | -0.019766 | -0.042698 | -0.03649 | -0.030728 | 0.065477 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.012885 | -0.017266 | -0.007751 | -0.003831 | 0.047549 | -0.054588 | 0.13739 | -0.026426 | -70.1997 | -6.1397 | -69.9778 | 53.0577 | 53.1621 | 53.0509 | -70.5543 | 70.1945 | -53.2453 | 70.2037 | 70.2171 | 0.022595 | -53.3474 | -53.1555 | -0.33336 | -0.23515 | 0.021215 | 0.24312 | 0.57648 | -0.13072 | -0.24199 | 70.2685 | 70.1664 | 70.3583 | 70.2132 | -53.3193 | 123.2786 | 123.3831 | 123.2718 | 64.0813 | -123.8472
914.2812 | 123.6053 | -70.2301 | 53.2562 | 0.031826 | -0.0013202 | -0.017629 | -0.043767 | -0.035422 | -0.030728 | 0.050216 | -0.017741 | -0.012872 | 0.010393 | 0.1198 | 0.015022 | -0.008109 | -0.012329 | -0.003831 | 0.065863 | -0.050009 | 0.12365 | -0.021847 | -70.1677 | -7.4996 | -69.9366 | 53.0897 | 53.1988 | 53.0738 | -70.5177 | 70.2083 | -53.1904 | 70.222 | 70.2263 | 0.018016 | -53.3062 | -53.1326 | -0.28757 | -0.16648 | 0.062422 | 0.29348 | 0.58105 | -0.057473 | -0.18247 | 70.296 | 70.1801 | 70.3538 | 70.2178 | -53.2781 | 123.3199 | 123.4289 | 123.3039 | 62.7305 | -123.7739
915.2812 | 123.5916 | -69.9097 | 53.5538 | 0.047088 | -0.0034562 | -0.020834 | -0.042698 | -0.037559 | -0.028592 | 0.065477 | -0.017741 | -0.011804 | 0.0093254 | 0.12087 | 0.015022 | -0.017266 | -0.003172 | -0.012988 | 0.047549 | -0.054588 | 0.10534 | -0.021847 | -69.6594 | -7.7468 | -69.4192 | 53.6071 | 53.7253 | 53.5911 | -70.0048 | 69.8878 | -53.5062 | 69.8924 | 69.8967 | 0.008859 | -53.6084 | -53.4484 | -0.095179 | 0.053345 | 0.25022 | 0.49044 | 0.58562 | 0.17152 | 0.037364 | 69.9572 | 69.8551 | 70.015 | 69.9065 | -53.5756 | 123.5168 | 123.635 | 123.5008 | 62.1628 | -123.5586
916.2656 | 123.5779 | -70.5505 | 52.9678 | 0.047088 | -0.0045252 | -0.019766 | -0.043767 | -0.03649 | -0.02966 | 0.080738 | -0.017741 | -0.011804 | 0.011461 | 0.12087 | 0.012885 | -0.017266 | -0.003172 | -0.008409 | 0.052128 | -0.04543 | 0.12365 | -0.026426 | -70.3188 | -6.4419 | -70.0969 | 52.9387 | 53.0431 | 52.9364 | -70.6825 | 70.5241 | -52.9157 | 70.5333 | 70.5421 | 0.018017 | -53.0133 | -52.8442 | -0.13197 | -0.029178 | 0.23176 | 0.45366 | 0.58564 | 0.075247 | -0.031438 | 70.6027 | 70.5051 | 70.6742 | 70.5474 | -52.9943 | 123.4892 | 123.5936 | 123.4869 | 64.1087 | -123.6503
917.2656 | 123.6053 | -71.0953 | 52.4139 | 0.06235 | -0.0013202 | -0.017629 | -0.043767 | -0.03649 | -0.02966 | 0.065477 | -0.017741 | -0.012872 | 0.011461 | 0.12087 | 0.012885 | -0.017266 | -0.026065 | -0.017566 | 0.042971 | -0.050009 | 0.12823 | -0.021847 | -70.9552 | -6.4831 | -70.7242 | 52.3022 | 52.4067 | 52.2862 | -71.3144 | 71.0734 | -52.371 | 71.078 | 71.0777 | 0.004281 | -52.4639 | -52.2857 | -0.21911 | -0.11169 | 0.14006 | 0.37112 | 0.59023 | -0.007285 | -0.12771 | 71.1382 | 71.0453 | 71.2235 | 71.0692 | -52.4358 | 123.3975 | 123.5019 | 123.3815 | 64.6122 | -123.7283
918.2656 | 123.587 | -70.9167 | 52.5375 | 0.06235 | -0.0034562 | -0.019766 | -0.042698 | -0.03649 | -0.031797 | 0.065477 | -0.015604 | -0.012872 | 0.010393 | 0.12087 | 0.013953 | -0.012688 | -0.021486 | -0.008409 | 0.056706 | -0.050009 | 0.12823 | -0.021847 | -70.7446 | -11.7257 | -70.5135 | 52.5037 | 52.6081 | 52.4923 | -71.1175 | 70.8949 | -52.4808 | 70.9041 | 70.9083 | 0.013438 | -52.5875 | -52.4093 | -0.20075 | -0.033838 | 0.17215 | 0.40321 | 0.60396 | 0.070577 | -0.045266 | 70.9735 | 70.8667 | 71.045 | 70.8953 | -52.5594 | 123.4204 | 123.5249 | 123.409 | 59.191 | -123.655
919.2812 | 123.6237 | -70.8527 | 52.6245 | 0.06235 | -0.0023882 | -0.019766 | -0.043767 | -0.03649 | -0.02966 | 0.065477 | -0.017741 | -0.010735 | 0.010393 | 0.12194 | 0.013953 | -0.008109 | -0.021486 | -0.003831 | 0.07502 | -0.050009 | 0.11907 | -0.021847 | -70.6759 | -12.2202 | -70.4357 | 52.5815 | 52.6814 | 52.5747 | -71.0488 | 70.8308 | -52.5495 | 70.8446 | 70.8488 | 0.018016 | -52.6745 | -52.5054 | -0.19616 | -0.042978 | 0.17674 | 0.41696 | 0.61312 | 0.056859 | -0.049826 | 70.9277 | 70.8027 | 70.9717 | 70.8312 | -52.6464 | 123.4342 | 123.534 | 123.4273 | 58.6324 | -123.6733
920.2812 | 123.6328 | -70.4178 | 53.0457 | 0.06235 | -0.0045252 | -0.020834 | -0.042698 | -0.037559 | -0.032865 | 0.050216 | -0.016673 | -0.011804 | 0.0071884 | 0.12087 | 0.013953 | -0.021844 | -0.021486 | -0.008409 | 0.056706 | -0.040851 | 0.12823 | -0.026426 | -70.5935 | -8.4245 | -70.3579 | 52.6456 | 52.7501 | 52.6434 | -70.9664 | 70.3914 | -52.9889 | 70.3959 | 70.4094 | 0.018017 | -53.0865 | -52.9174 | -0.54861 | -0.40002 | -0.17571 | 0.059924 | 0.60854 | -0.2956 | -0.40229 | 70.4745 | 70.3769 | 70.546 | 70.3963 | -53.0721 | 123.0634 | 123.1678 | 123.0612 | 61.9933 | -124.0121
921.2656 | 123.6191 | -71.0037 | 52.4918 | 0.06235 | -0.0034562 | -0.019766 | -0.044835 | -0.03649 | -0.02966 | 0.065477 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.011817 | -0.017266 | -0.021486 | -0.008409 | 0.047549 | -0.054588 | 0.13281 | -0.017268 | -70.653 | -9.3494 | -70.422 | 52.5815 | 52.6951 | 52.5701 | -71.0351 | 70.9865 | -52.4442 | 70.9865 | 70.9953 | 0.008859 | -52.5463 | -52.359 | -0.031358 | 0.089774 | 0.3507 | 0.58176 | 0.61312 | 0.20335 | 0.078348 | 71.0513 | 70.9491 | 71.1365 | 70.9822 | -52.509 | 123.5853 | 123.6988 | 123.5738 | 61.6544 | -123.5268
922.2656 | 123.6465 | -70.491 | 52.9678 | 0.06235 | -0.0034562 | -0.017629 | -0.043767 | -0.035422 | -0.030728 | 0.080738 | -0.017741 | -0.015009 | 0.0093254 | 0.12194 | 0.011817 | -0.012688 | -0.030644 | -0.012988 | 0.056706 | -0.054588 | 0.12365 | -0.026426 | -70.3005 | -10.0041 | -70.074 | 52.9432 | 53.0477 | 52.9318 | -70.6734 | 70.4646 | -52.9111 | 70.4783 | 70.478 | 0.013438 | -53.0224 | -52.8442 | -0.18233 | -0.024599 | 0.19057 | 0.41705 | 0.59937 | 0.079825 | -0.036017 | 70.5477 | 70.4364 | 70.6147 | 70.4604 | -52.9943 | 123.4343 | 123.5387 | 123.4228 | 60.4869 | -123.6412
923.2656 | 123.5825 | -70.0104 | 53.4988 | 0.047088 | -0.0055932 | -0.018697 | -0.043767 | -0.037559 | -0.030728 | 0.065477 | -0.020945 | -0.011804 | 0.0082564 | 0.12301 | 0.012885 | -0.012688 | -0.026065 | -0.008409 | 0.042971 | -0.050009 | 0.12365 | -0.031005 | -69.8014 | -12.234 | -69.5383 | 53.456 | 53.5696 | 53.4538 | -70.1559 | 69.9794 | -53.4559 | 69.9977 | 70.002 | 0.022596 | -53.5488 | -53.3752 | -0.14557 | -0.042814 | 0.20899 | 0.4721 | 0.61767 | 0.07078 | -0.045062 | 70.0533 | 69.9604 | 70.134 | 69.9843 | -53.5298 | 123.4664 | 123.58 | 123.4642 | 57.7764 | -123.6548
924.2812 | 123.5962 | -70.5643 | 52.9266 | 0.06235 | -0.0045252 | -0.018697 | -0.043767 | -0.037559 | -0.030728 | 0.050216 | -0.017741 | -0.012872 | 0.0082564 | 0.12194 | 0.011817 | -0.017266 | -0.016908 | -0.012988 | 0.056706 | -0.054588 | 0.11449 | -0.021847 | -70.3783 | -11.7074 | -70.1152 | 52.8654 | 52.9744 | 52.854 | -70.7604 | 70.5424 | -52.8699 | 70.547 | 70.5513 | 0.008859 | -52.9812 | -52.8121 | -0.19608 | -0.061235 | 0.18597 | 0.44908 | 0.64516 | 0.047766 | -0.072655 | 70.621 | 70.5097 | 70.6788 | 70.5474 | -52.9485 | 123.4297 | 123.5387 | 123.4183 | 58.8569 | -123.687
925.2656 | 123.7106 | -70.546 | 52.858 | 0.047088 | -0.0045252 | -0.018697 | -0.044835 | -0.03649 | -0.030728 | 0.080738 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.013953 | -0.017266 | -0.026065 | -0.003831 | 0.042971 | -0.050009 | 0.11907 | -0.021847 | -70.3737 | -13.3512 | -70.1335 | 52.8471 | 52.9607 | 52.8448 | -70.7741 | 70.5241 | -52.815 | 70.5287 | 70.5421 | 0.018016 | -52.908 | -52.7389 | -0.22813 | -0.010884 | 0.17224 | 0.41245 | 0.64058 | 0.1027 | -0.013147 | 70.5889 | 70.4959 | 70.665 | 70.5199 | -52.8798 | 123.393 | 123.5066 | 123.3908 | 57.1948 | -123.6321
926.2656 | 123.6511 | -70.7932 | 52.6611 | 0.077612 | -0.0055932 | -0.020834 | -0.043767 | -0.03649 | -0.030728 | 0.065477 | -0.017741 | -0.01394 | 0.0093254 | 0.1198 | 0.011817 | -0.026423 | -0.030644 | -0.008409 | 0.056706 | -0.050009 | 0.12823 | -0.026426 | -70.708 | -14.885 | -70.4723 | 52.5083 | 52.6127 | 52.5014 | -71.1175 | 70.7667 | -52.6044 | 70.7667 | 70.7847 | 0.018017 | -52.7111 | -52.5329 | -0.32435 | -0.15286 | 0.085183 | 0.32082 | 0.64517 | -0.048441 | -0.1597 | 70.8499 | 70.7431 | 70.9214 | 70.7625 | -52.6876 | 123.3014 | 123.4058 | 123.2946 | 55.9081 | -123.7786
927.2656 | 123.7152 | -70.4544 | 52.9312 | 0.06235 | -0.0045252 | -0.018697 | -0.044835 | -0.037559 | -0.031797 | 0.080738 | -0.018809 | -0.012872 | 0.0082564 | 0.12194 | 0.012885 | -0.017266 | -0.030644 | -0.008409 | 0.033814 | -0.054588 | 0.13281 | -0.026426 | -70.4653 | -12.7513 | -70.2022 | 52.7464 | 52.8554 | 52.7304 | -70.8702 | 70.428 | -52.8974 | 70.4371 | 70.446 | 0.018017 | -52.9858 | -52.7984 | -0.41584 | -0.18485 | -0.01089 | 0.25222 | 0.66806 | -0.075855 | -0.20085 | 70.4882 | 70.3998 | 70.5872 | 70.4238 | -52.9576 | 123.2008 | 123.3098 | 123.1848 | 57.7031 | -123.8015
928.2656 | 123.6877 | -71.3837 | 52.034 | 0.06235 | -0.0055932 | -0.018697 | -0.043767 | -0.03649 | -0.031797 | 0.095999 | -0.017741 | -0.012872 | 0.0093254 | 0.1198 | 0.012885 | -0.012688 | -0.030644 | -0.008409 | 0.038393 | -0.04543 | 0.11449 | -0.026426 | -71.1842 | -11.0572 | -70.9394 | 52.0413 | 52.1503 | 52.0344 | -71.5845 | 71.3572 | -51.9956 | 71.371 | 71.3753 | 0.018017 | -52.0794 | -51.9195 | -0.20087 | 0.007274 | 0.19951 | 0.44431 | 0.64518 | 0.11626 | 0.000414 | 71.4221 | 71.3382 | 71.4982 | 71.353 | -52.0604 | 123.4249 | 123.5339 | 123.4181 | 60.3264 | -123.6185
929.2812 | 123.6191 | -70.9213 | 52.5375 | 0.06235 | -0.0055932 | -0.018697 | -0.044835 | -0.037559 | -0.030728 | 0.080738 | -0.018809 | -0.01394 | 0.0093254 | 0.12194 | 0.011817 | -0.021844 | -0.026065 | -0.008409 | 0.038393 | -0.050009 | 0.12365 | -0.026426 | -70.7354 | -12.9253 | -70.4769 | 52.49 | 52.5944 | 52.4648 | -71.145 | 70.8949 | -52.4991 | 70.8995 | 70.9129 | 0.018017 | -52.5875 | -52.4139 | -0.22365 | -0.047573 | 0.18588 | 0.44442 | 0.66806 | 0.056841 | -0.072737 | 70.9597 | 70.8713 | 71.045 | 70.8953 | -52.564 | 123.4113 | 123.5157 | 123.3861 | 57.996 | -123.6825
930.2656 | 123.6649 | -70.8755 | 52.5879 | 0.06235 | -0.0045252 | -0.019766 | -0.043767 | -0.038627 | -0.033933 | 0.065477 | -0.018809 | -0.01394 | 0.010393 | 0.12301 | 0.013953 | -0.012688 | -0.035222 | -0.012988 | 0.047549 | -0.04543 | 0.11449 | -0.026426 | -70.6484 | -12.7468 | -70.4082 | 52.5632 | 52.6722 | 52.5564 | -71.0671 | 70.8491 | -52.5403 | 70.8629 | 70.8626 | 0.013438 | -52.6333 | -52.4734 | -0.19158 | -0.024671 | 0.2271 | 0.46732 | 0.65891 | 0.084323 | -0.031519 | 70.9231 | 70.8301 | 70.99 | 70.8403 | -52.6143 | 123.4388 | 123.5478 | 123.4319 | 58.1288 | -123.655
931.2656 | 123.7289 | -71.0037 | 52.4185 | 0.047088 | -0.0045252 | -0.018697 | -0.045904 | -0.038627 | -0.031797 | 0.095999 | -0.017741 | -0.012872 | 0.011461 | 0.12194 | 0.011817 | -0.017266 | -0.039801 | -0.012988 | 0.038393 | -0.04543 | 0.12823 | -0.026426 | -70.7766 | -11.9043 | -70.5685 | 52.3892 | 52.5028 | 52.3686 | -71.2457 | 70.9773 | -52.3801 | 70.9865 | 70.9907 | 0.013438 | -52.4639 | -52.2903 | -0.24198 | -0.029281 | 0.22707 | 0.43524 | 0.67722 | 0.084288 | -0.049869 | 71.0421 | 70.9583 | 71.132 | 70.9639 | -52.4449 | 123.393 | 123.5065 | 123.3724 | 59.0994 | -123.6642
932.2656 | 123.6969 | -70.6558 | 52.7939 | 0.047088 | -0.0055932 | -0.017629 | -0.043767 | -0.03649 | -0.030728 | 0.080738 | -0.017741 | -0.012872 | 0.0093254 | 0.12087 | 0.011817 | -0.017266 | -0.030644 | -0.012988 | 0.056706 | -0.050009 | 0.12365 | -0.026426 | -70.4287 | -12.4949 | -70.161 | 52.8013 | 52.9149 | 52.7761 | -70.829 | 70.6294 | -52.7372 | 70.6386 | 70.6428 | 0.013438 | -52.8439 | -52.6702 | -0.17321 | 0.007418 | 0.22716 | 0.49484 | 0.66806 | 0.121 | -0.017739 | 70.7125 | 70.6058 | 70.7795 | 70.6252 | -52.8203 | 123.4571 | 123.5707 | 123.432 | 58.1609 | -123.6229
933.2656 | 123.6923 | -70.99 | 52.4185 | 0.06235 | -0.0055932 | -0.019766 | -0.043767 | -0.038627 | -0.02966 | 0.065477 | -0.018809 | -0.012872 | 0.0093254 | 0.12301 | 0.011817 | -0.012688 | -0.035222 | -0.003831 | 0.052128 | -0.04543 | 0.13281 | -0.031005 | -70.7995 | -12.8521 | -70.5273 | 52.4167 | 52.5303 | 52.3915 | -71.2137 | 70.959 | -52.3664 | 70.9773 | 70.9862 | 0.027174 | -52.4639 | -52.2857 | -0.22366 | -0.00181 | 0.19045 | 0.46272 | 0.68638 | 0.11176 | -0.026976 | 71.0421 | 70.9446 | 71.1228 | 70.9548 | -52.4495 | 123.4067 | 123.5203 | 123.3815 | 58.1379 | -123.6322
934.2656 | 123.7473 | -70.1248 | 53.2745 | 0.047088 | -0.0066612 | -0.021902 | -0.045904 | -0.037559 | -0.031797 | 0.080738 | -0.017741 | -0.012872 | 0.010393 | 0.12301 | 0.010749 | -0.017266 | -0.035222 | -0.008409 | 0.047549 | -0.054588 | 0.12365 | -0.026426 | -70.1677 | -13.2092 | -69.9137 | 53.0348 | 53.1438 | 53.0188 | -70.6001 | 70.0984 | -53.227 | 70.1076 | 70.1164 | 0.018017 | -53.3291 | -53.1509 | -0.47528 | -0.23973 | -0.042864 | 0.21109 | 0.68637 | -0.13073 | -0.25572 | 70.1724 | 70.0702 | 70.2485 | 70.0896 | -53.301 | 123.1596 | 123.2686 | 123.1436 | 56.9156 | -123.8746
935.2656 | 123.7106 | -70.1523 | 53.2562 | 0.06235 | -0.0077302 | -0.019766 | -0.044835 | -0.03649 | -0.031797 | 0.080738 | -0.016673 | -0.012872 | 0.0082564 | 0.12301 | 0.011817 | -0.012688 | -0.035222 | -0.012988 | 0.042971 | -0.050009 | 0.11449 | -0.017268 | -69.8426 | -16.4418 | -69.5795 | 53.3553 | 53.4643 | 53.3439 | -70.2796 | 70.135 | -53.2133 | 70.1396 | 70.1393 | 0.00428 | -53.3062 | -53.1417 | -0.12729 | 0.099074 | 0.30969 | 0.5728 | 0.70009 | 0.20809 | 0.087665 | 70.1953 | 70.1023 | 70.2668 | 70.1171 | -53.2735 | 123.5076 | 123.6166 | 123.4962 | 53.7105 | -123.5358
936.2656 | 123.7335 | -70.0607 | 53.3707 | 0.047088 | -0.0034562 | -0.018697 | -0.045904 | -0.039695 | -0.030728 | 0.065477 | -0.017741 | -0.011804 | 0.0082564 | 0.12301 | 0.012885 | -0.012688 | -0.044379 | -0.012988 | 0.038393 | -0.050009 | 0.12823 | -0.017268 | -69.8014 | -14.4821 | -69.5978 | 53.2912 | 53.4048 | 53.2935 | -70.3299 | 70.0435 | -53.3323 | 70.048 | 70.0477 | 0.00428 | -53.4207 | -53.2424 | -0.26921 | -0.079466 | 0.25935 | 0.46293 | 0.73215 | 0.034123 | -0.07714 | 70.0991 | 70.0107 | 70.189 | 70.0164 | -53.3879 | 123.3519 | 123.4655 | 123.3543 | 55.5786 | -123.7006
937.2656 | 123.7061 | -70.3171 | 53.1143 | 0.031826 | -0.0066612 | -0.019766 | -0.043767 | -0.037559 | -0.030728 | 0.065477 | -0.017741 | -0.011804 | 0.010393 | 0.12301 | 0.011817 | -0.003531 | -0.039801 | -0.012988 | 0.056706 | -0.050009 | 0.14197 | -0.021847 | -69.8609 | -13.5938 | -69.7626 | 53.1355 | 53.2537 | 53.1241 | -70.4948 | 70.2952 | -53.0576 | 70.3135 | 70.3041 | 0.008859 | -53.1643 | -52.9724 | -0.1777 | 0.021213 | 0.45617 | 0.55445 | 0.73215 | 0.13938 | 0.009799 | 70.3738 | 70.2671 | 70.459 | 70.2773 | -53.1362 | 123.4526 | 123.5708 | 123.4412 | 56.7232 | -123.6091
938.2656 | 123.7106 | -69.8593 | 53.5629 | 0.077612 | -0.0055932 | -0.020834 | -0.042698 | -0.038627 | -0.031797 | 0.050216 | -0.017741 | -0.012872 | 0.0082564 | 0.12301 | 0.011817 | -0.012688 | -0.030644 | -0.008409 | 0.052128 | -0.050009 | 0.11449 | -0.017268 | -69.838 | -10.9519 | -69.6894 | 53.2363 | 53.3453 | 53.2248 | -70.3986 | 69.842 | -53.5108 | 69.8466 | 69.8509 | 0.008859 | -53.6129 | -53.4484 | -0.53931 | -0.32667 | 0.0213 | 0.16994 | 0.70925 | -0.21766 | -0.33808 | 69.9114 | 69.8093 | 69.9738 | 69.8287 | -53.5802 | 123.0956 | 123.2046 | 123.0842 | 58.9074 | -123.9616
939.2656 | 123.5641 | -70.134 | 53.4027 | 0.031826 | -0.0055932 | -0.019766 | -0.045904 | -0.035422 | -0.031797 | 0.095999 | -0.018809 | -0.012872 | 0.0093254 | 0.12301 | 0.010749 | -0.008109 | -0.035222 | -0.008409 | 0.038393 | -0.054588 | 0.11907 | -0.026426 | -69.9342 | -11.3686 | -69.8267 | 53.0943 | 53.2079 | 53.0921 | -70.5406 | 70.1075 | -53.3643 | 70.1259 | 70.1256 | 0.018017 | -53.4573 | -53.2836 | -0.4066 | -0.30839 | 0.1998 | 0.30724 | 0.71384 | -0.1948 | -0.31064 | 70.1724 | 70.0794 | 70.253 | 70.0987 | -53.4291 | 123.2283 | 123.3419 | 123.226 | 58.7654 | -123.9433
940.2656 | 123.7381 | -71.4935 | 51.9058 | 0.047088 | -0.0055932 | -0.019766 | -0.048041 | -0.037559 | -0.031797 | 0.080738 | -0.017741 | -0.012872 | 0.010393 | 0.12301 | 0.010749 | -0.012688 | -0.030644 | -0.012988 | 0.052128 | -0.050009 | 0.13281 | -0.021847 | -70.6027 | -12.2568 | -70.5181 | 52.403 | 52.5211 | 52.387 | -71.2365 | 71.4717 | -51.8537 | 71.4808 | 71.4805 | 0.008859 | -51.9558 | -51.773 | 0.25698 | 0.49715 | 0.89087 | 0.97541 | 0.71843 | 0.6153 | 0.48114 | 71.5457 | 71.4435 | 71.6263 | 71.4629 | -51.9277 | 123.8965 | 124.0147 | 123.8805 | 59.2367 | -123.1424
941.2656 | 123.7198 | -70.6604 | 52.7481 | 0.06235 | -0.0055932 | -0.019766 | -0.044835 | -0.037559 | -0.032865 | 0.080738 | -0.017741 | -0.01394 | 0.0082564 | 0.12301 | 0.010749 | -0.008109 | -0.035222 | -0.017566 | 0.056706 | -0.054588 | 0.12365 | -0.021847 | -70.4149 | -12.4354 | -70.367 | 52.5403 | 52.6402 | 52.5289 | -71.0992 | 70.6386 | -52.6914 | 70.6523 | 70.6428 | 0.004281 | -52.8027 | -52.6245 | -0.43879 | -0.20778 | 0.24547 | 0.29338 | 0.73217 | -0.10794 | -0.21921 | 70.7171 | 70.6058 | 70.7841 | 70.6252 | -52.77 | 123.2007 | 123.3006 | 123.1893 | 58.225 | -123.8473
942.2656 | 123.7518 | -70.9579 | 52.4689 | 0.06235 | -0.0055932 | -0.021902 | -0.043767 | -0.039695 | -0.031797 | 0.065477 | -0.018809 | -0.012872 | 0.0082564 | 0.12408 | 0.011817 | -0.012688 | -0.035222 | -0.008409 | 0.042971 | -0.054588 | 0.13281 | -0.012689 | -70.5294 | -12.4949 | -70.5135 | 52.4167 | 52.5349 | 52.4099 | -71.2228 | 70.9453 | -52.4259 | 70.9453 | 70.9495 | 0.00428 | -52.5235 | -52.3361 | -0.26487 | -0.052164 | 0.42855 | 0.44441 | 0.70928 | 0.065984 | -0.059016 | 71.0009 | 70.9034 | 71.0908 | 70.9227 | -52.4816 | 123.3747 | 123.4928 | 123.3678 | 58.463 | -123.6917
943.2656 | 123.7289 | -71.5439 | 51.8738 | 0.047088 | -0.0055932 | -0.020834 | -0.043767 | -0.03649 | -0.030728 | 0.065477 | -0.019877 | -0.011804 | 0.0093254 | 0.12301 | 0.011817 | -0.017266 | -0.044379 | -0.003831 | 0.029236 | -0.050009 | 0.11907 | -0.017268 | -70.8408 | -12.8155 | -70.8753 | 52.0733 | 52.1869 | 52.0665 | -71.5616 | 71.5266 | -51.8445 | 71.5266 | 71.5401 | 0.013437 | -51.9238 | -51.7547 | -0.017761 | 0.19954 | 0.70313 | 0.66863 | 0.68639 | 0.3131 | 0.19268 | 71.5731 | 71.4939 | 71.663 | 71.4995 | -51.891 | 123.6172 | 123.7308 | 123.6103 | 58.7284 | -123.4354
944.2812 | 123.642 | -71.3882 | 52.1484 | 0.047088 | -0.0066612 | -0.020834 | -0.043767 | -0.03649 | -0.031797 | 0.065477 | -0.018809 | -0.01394 | 0.0093254 | 0.12515 | 0.012885 | -0.012688 | -0.035222 | -0.003831 | 0.061284 | -0.050009 | 0.11907 | -0.031005 | -71.1017 | -13.2367 | -71.1729 | 51.8169 | 51.9213 | 51.8101 | -71.8181 | 71.3572 | -52.0872 | 71.3756 | 71.3844 | 0.027174 | -52.1984 | -52.0294 | -0.42981 | -0.33151 | 0.28651 | 0.21537 | 0.64519 | -0.22711 | -0.33838 | 71.4495 | 71.3382 | 71.5073 | 71.353 | -52.1794 | 123.2052 | 123.3096 | 123.1983 | 58.1516 | -123.9665
945.2656 | 123.7656 | -71.4706 | 51.9562 | 0.06235 | -0.0055932 | -0.020834 | -0.044835 | -0.037559 | -0.031797 | 0.080738 | -0.017741 | -0.011804 | 0.010393 | 0.12301 | 0.010749 | -0.012688 | -0.044379 | -0.008409 | 0.052128 | -0.054588 | 0.12823 | -0.017268 | -71.3169 | -13.255 | -71.2919 | 51.6979 | 51.8206 | 51.691 | -71.928 | 71.4534 | -51.904 | 71.458 | 71.4622 | 0.008859 | -52.0108 | -51.8279 | -0.45731 | -0.25829 | 0.15371 | 0.17872 | 0.63603 | -0.13558 | -0.26516 | 71.5228 | 71.4161 | 71.5989 | 71.4263 | -51.9734 | 123.1685 | 123.2912 | 123.1617 | 58.2156 | -123.8841
946.2656 | 123.7289 | -71.4752 | 51.9791 | 0.06235 | -0.0077302 | -0.019766 | -0.044835 | -0.037559 | -0.02966 | 0.050216 | -0.018809 | -0.011804 | 0.0093254 | 0.12408 | 0.011817 | -0.021844 | -0.044379 | -0.012988 | 0.047549 | -0.050009 | 0.13281 | -0.012689 | -71.0697 | -13.1176 | -71.1042 | 51.8856 | 51.9992 | 51.8696 | -71.754 | 71.4625 | -51.9315 | 71.4534 | 71.4622 | -0.000299 | -52.0291 | -51.8463 | -0.27874 | -0.093462 | 0.40553 | 0.37103 | 0.64976 | 0.020094 | -0.10948 | 71.5228 | 71.4252 | 71.608 | 71.4308 | -51.9918 | 123.3608 | 123.4744 | 123.3448 | 58.3576 | -123.733
947.2656 | 123.7106 | -72.1664 | 51.2329 | 0.031826 | -0.0045252 | -0.020834 | -0.045904 | -0.038627 | -0.02966 | 0.095999 | -0.018809 | -0.01394 | 0.0093254 | 0.12408 | 0.010749 | -0.008109 | -0.044379 | -0.003831 | 0.042971 | -0.050009 | 0.14197 | -0.012689 | -71.5779 | -12.7697 | -71.6536 | 51.3224 | 51.436 | 51.3064 | -72.3126 | 72.1538 | -51.1899 | 72.1583 | 72.1626 | 0.008858 | -51.2829 | -51.0909 | -0.14613 | 0.089538 | 0.58852 | 0.51281 | 0.65893 | 0.20308 | 0.073503 | 72.2094 | 72.1164 | 72.3084 | 72.1221 | -51.2456 | 123.4889 | 123.6024 | 123.4729 | 59.3968 | -123.5455
948.2656 | 123.7106 | -71.6858 | 51.7319 | 0.077612 | -0.0066612 | -0.019766 | -0.044835 | -0.037559 | -0.02966 | 0.050216 | -0.017741 | -0.012872 | 0.0071884 | 0.12515 | 0.010749 | -0.017266 | -0.044379 | -0.008409 | 0.047549 | -0.054588 | 0.12365 | -0.017268 | -71.5779 | -12.8155 | -71.6491 | 51.3453 | 51.4589 | 51.3201 | -72.2897 | 71.6685 | -51.6843 | 71.6685 | 71.6774 | 0.008859 | -51.7865 | -51.6082 | -0.60389 | -0.38653 | 0.10787 | 0.036733 | 0.64062 | -0.27299 | -0.41172 | 71.7333 | 71.6312 | 71.8094 | 71.6414 | -51.7491 | 123.0311 | 123.1447 | 123.0059 | 58.8703 | -124.0215
949.2812 | 123.6465 | -71.9101 | 51.5717 | 0.092874 | -0.0066612 | -0.020834 | -0.045904 | -0.037559 | -0.028592 | 0.080738 | -0.015604 | -0.01394 | 0.0082564 | 0.12408 | 0.010749 | -0.021844 | -0.044379 | -0.008409 | 0.061284 | -0.050009 | 0.14197 | -0.021847 | -71.6558 | -13.2046 | -71.6124 | 51.3957 | 51.4955 | 51.3843 | -72.253 | 71.8882 | -51.5104 | 71.8883 | 71.9017 | 0.013438 | -51.6217 | -51.4297 | -0.34295 | -0.17595 | 0.25433 | 0.29767 | 0.64062 | -0.076142 | -0.1874 | 71.9714 | 71.8601 | 72.0521 | 71.8657 | -51.5935 | 123.3058 | 123.4056 | 123.2943 | 58.7055 | -123.8247
950.2656 | 123.7564 | -71.8231 | 51.6083 | 0.047088 | -0.0077302 | -0.021902 | -0.044835 | -0.03649 | -0.030728 | 0.050216 | -0.017741 | -0.011804 | 0.0071884 | 0.12621 | 0.011817 | -0.012688 | -0.044379 | -0.008409 | 0.052128 | -0.050009 | 0.13739 | -0.012689 | -71.4406 | -12.5819 | -71.3972 | 51.6063 | 51.7107 | 51.5903 | -72.0378 | 71.8104 | -51.5561 | 71.8104 | 71.8147 | 0.00428 | -51.6583 | -51.4709 | -0.21472 | -0.001962 | 0.38256 | 0.42589 | 0.64061 | 0.10243 | -0.017989 | 71.8752 | 71.7731 | 71.9605 | 71.7787 | -51.621 | 123.4294 | 123.5338 | 123.4134 | 59.2412 | -123.6461
951.2656 | 123.7381 | -71.3379 | 52.0889 | 0.047088 | -0.0066612 | -0.021902 | -0.044835 | -0.035422 | -0.030728 | 0.065477 | -0.016673 | -0.011804 | 0.0082564 | 0.12621 | 0.011817 | -0.008109 | -0.044379 | -0.008409 | 0.061284 | -0.050009 | 0.11907 | -0.017268 | -71.1155 | -16.2495 | -71.1271 | 51.8215 | 51.9305 | 51.8055 | -71.8181 | 71.3206 | -52.0276 | 71.3298 | 71.3295 | 0.008859 | -52.1389 | -51.9699 | -0.48017 | -0.26742 | 0.22242 | 0.21081 | 0.69097 | -0.15845 | -0.28345 | 71.3992 | 71.2879 | 71.457 | 71.2935 | -52.1062 | 123.1594 | 123.2684 | 123.1434 | 55.0884 | -123.907
952.2656 | 123.7198 | -71.6446 | 51.7776 | 0.047088 | -0.0066612 | -0.018697 | -0.045904 | -0.037559 | -0.031797 | 0.050216 | -0.016673 | -0.012872 | 0.0093254 | 0.12408 | 0.0096795 | -0.017266 | -0.044379 | -0.008409 | 0.047549 | -0.054588 | 0.13739 | -0.021847 | -71.2803 | -13.6762 | -71.1958 | 51.7711 | 51.8801 | 51.7597 | -71.8776 | 71.6227 | -51.7301 | 71.6273 | 71.6362 | 0.013438 | -51.8322 | -51.6403 | -0.23299 | -0.006509 | 0.36429 | 0.44883 | 0.68182 | 0.10247 | -0.017954 | 71.6921 | 71.59 | 71.782 | 71.6002 | -51.7995 | 123.4157 | 123.5247 | 123.4043 | 57.9683 | -123.6552
953.2656 | 123.7473 | -71.8643 | 51.5625 | 0.047088 | -0.0087982 | -0.020834 | -0.045904 | -0.03649 | -0.030728 | 0.065477 | -0.018809 | -0.010735 | 0.0082564 | 0.12408 | 0.0096795 | -0.017266 | -0.044379 | -0.003831 | 0.047549 | -0.054588 | 0.12365 | -0.00811 | -71.4818 | -17.8429 | -71.4247 | 51.5651 | 51.6649 | 51.5445 | -72.0882 | 71.8562 | -51.515 | 71.8471 | 71.8605 | 0.004279 | -51.6171 | -51.4388 | -0.22389 | 0.002608 | 0.38255 | 0.43962 | 0.66351 | 0.10242 | -0.017999 | 71.9119 | 71.8097 | 71.988 | 71.8199 | -51.5706 | 123.4294 | 123.5292 | 123.4088 | 54.0214 | -123.6507
954.2812 | 123.7152 | -72.5784 | 50.8484 | 0.092874 | -0.0055932 | -0.020834 | -0.046972 | -0.03649 | -0.02966 | 0.065477 | -0.019877 | -0.010735 | 0.0093254 | 0.12515 | 0.011817 | -0.017266 | -0.044379 | -0.003831 | 0.038393 | -0.054588 | 0.12823 | -0.017268 | -72.1777 | -19.4088 | -72.1115 | 50.8463 | 50.9736 | 50.8257 | -72.7979 | 72.5612 | -50.81 | 72.5612 | 72.5746 | 0.013437 | -50.903 | -50.7202 | -0.2195 | -0.002105 | 0.40069 | 0.46692 | 0.68642 | 0.12516 | -0.022729 | 72.6168 | 72.5238 | 72.7067 | 72.5341 | -50.8657 | 123.4247 | 123.552 | 123.4041 | 53.1696 | -123.6463
955.2656 | 123.6969 | -71.7224 | 51.7593 | 0.031826 | -0.0055932 | -0.021902 | -0.045904 | -0.037559 | -0.031797 | 0.080738 | -0.017741 | -0.011804 | 0.0082564 | 0.12621 | 0.0096795 | -0.012688 | -0.039801 | -0.012988 | 0.042971 | -0.050009 | 0.12823 | -0.00811 | -71.4818 | -19.2348 | -71.3972 | 51.5331 | 51.6512 | 51.5262 | -72.1065 | 71.7143 | -51.7164 | 71.7097 | 71.7094 | -0.004878 | -51.8093 | -51.6311 | -0.38411 | -0.22628 | 0.24064 | 0.32518 | 0.7093 | -0.10815 | -0.23315 | 71.7654 | 71.6724 | 71.8506 | 71.6826 | -51.7674 | 123.2555 | 123.3736 | 123.2486 | 52.4876 | -123.8659
956.2656 | 123.6969 | -71.6446 | 51.8234 | 0.06235 | -0.0034562 | -0.021902 | -0.046972 | -0.034354 | -0.02966 | 0.080738 | -0.017741 | -0.009667 | 0.0082564 | 0.12408 | 0.011817 | -0.017266 | -0.048958 | -0.012988 | 0.056706 | -0.054588 | 0.11449 | -0.021847 | -71.5092 | -18.8136 | -71.4155 | 51.4919 | 51.5962 | 51.4712 | -72.1569 | 71.6227 | -51.7667 | 71.6273 | 71.6316 | 0.008859 | -51.878 | -51.7089 | -0.5123 | -0.33157 | 0.13535 | 0.22905 | 0.74135 | -0.22718 | -0.35218 | 71.7013 | 71.59 | 71.7591 | 71.5956 | -51.8453 | 123.1364 | 123.2408 | 123.1158 | 52.831 | -123.9803
957.2656 | 123.6969 | -71.6675 | 51.7914 | 0.077612 | -0.0066612 | -0.020834 | -0.046972 | -0.037559 | -0.031797 | 0.065477 | -0.017741 | -0.011804 | 0.0093254 | 0.12515 | 0.011817 | -0.017266 | -0.048958 | 0.000747 | 0.056706 | -0.050009 | 0.10992 | -0.021847 | -71.5413 | -19.4866 | -71.4613 | 51.4323 | 51.5413 | 51.4117 | -72.2118 | 71.6456 | -51.7347 | 71.6502 | 71.6682 | 0.022594 | -51.8414 | -51.6815 | -0.54436 | -0.35905 | 0.12619 | 0.20615 | 0.75051 | -0.25008 | -0.37966 | 71.7242 | 71.6175 | 71.7774 | 71.6185 | -51.8132 | 123.0998 | 123.2088 | 123.0792 | 52.1808 | -124.0032
958.2656 | 123.7106 | -71.5805 | 51.9058 | 0.06235 | -0.0066612 | -0.020834 | -0.046972 | -0.035422 | -0.02966 | 0.065477 | -0.016673 | -0.010735 | 0.0071884 | 0.12515 | 0.0096795 | -0.021844 | -0.048958 | -0.008409 | 0.052128 | -0.040851 | 0.12365 | -0.017268 | -71.0285 | -19.2852 | -70.8798 | 51.9863 | 52.0953 | 51.9657 | -71.6624 | 71.5632 | -51.8537 | 71.5587 | 71.5721 | 0.008859 | -51.9467 | -51.7822 | -0.081874 | 0.080506 | 0.55203 | 0.70067 | 0.78254 | 0.18949 | 0.059909 | 71.6326 | 71.5397 | 71.7042 | 71.5315 | -51.9231 | 123.5668 | 123.6758 | 123.5462 | 52.2953 | -123.5682
959.2812 | 123.7244 | -71.521 | 51.8875 | 0.047088 | -0.0077302 | -0.021902 | -0.045904 | -0.037559 | -0.02966 | 0.065477 | -0.017741 | -0.011804 | 0.0071884 | 0.12728 | 0.0096795 | -0.012688 | -0.053537 | -0.003831 | 0.042971 | -0.050009 | 0.13739 | -0.021847 | -71.1429 | -19.2485 | -71.0126 | 51.849 | 51.958 | 51.8192 | -71.7952 | 71.4991 | -51.8445 | 71.5083 | 71.5172 | 0.018016 | -51.9375 | -51.7501 | -0.27417 | -0.038537 | 0.37805 | 0.50838 | 0.78255 | 0.07044 | -0.068295 | 71.564 | 71.471 | 71.6584 | 71.4675 | -51.9094 | 123.37 | 123.4789 | 123.3402 | 52.2725 | -123.6827
960.2656 | 123.6923 | -71.6171 | 51.8097 | 0.031826 | -0.0066612 | -0.022971 | -0.045904 | -0.038627 | -0.031797 | 0.080738 | -0.017741 | -0.010735 | 0.0082564 | 0.12515 | 0.0086115 | -0.017266 | -0.044379 | 0.000747 | 0.047549 | -0.054588 | 0.14197 | -0.012689 | -71.0331 | -19.7385 | -70.8753 | 51.9726 | 52.0816 | 51.9474 | -71.6807 | 71.6044 | -51.7621 | 71.5999 | 71.6179 | 0.013436 | -51.8643 | -51.6677 | -0.063569 | 0.1629 | 0.58407 | 0.74187 | 0.80544 | 0.27188 | 0.13773 | 71.6647 | 71.5625 | 71.7591 | 71.5727 | -51.8224 | 123.5897 | 123.6987 | 123.5645 | 51.8787 | -123.4904
961.2656 | 123.6786 | -71.434 | 52.0294 | 0.077612 | -0.0087982 | -0.022971 | -0.048041 | -0.03649 | -0.02966 | 0.080738 | -0.017741 | -0.011804 | 0.0082564 | 0.12728 | 0.012885 | -0.008109 | -0.044379 | 0.000747 | 0.047549 | -0.054588 | 0.12365 | -0.00811 | -70.8453 | -14.7935 | -70.6967 | 52.1328 | 52.251 | 52.1122 | -71.5113 | 71.4259 | -51.9819 | 71.4259 | 71.4348 | 0.008857 | -52.084 | -51.9058 | -0.077257 | 0.10342 | 0.58869 | 0.73733 | 0.81459 | 0.22156 | 0.082828 | 71.4816 | 71.3794 | 71.5577 | 71.3896 | -52.0375 | 123.5669 | 123.685 | 123.5463 | 56.6406 | -123.5407
962.2656 | 123.6786 | -71.0541 | 52.4094 | 0.047088 | -0.0077302 | -0.019766 | -0.045904 | -0.038627 | -0.02966 | 0.034955 | -0.016673 | -0.012872 | 0.0061204 | 0.12621 | 0.0096795 | -0.012688 | -0.048958 | -0.008409 | 0.047549 | -0.054588 | 0.12365 | -0.012689 | -70.5752 | -14.0517 | -70.4449 | 52.3938 | 52.5074 | 52.3778 | -71.2503 | 71.0414 | -52.3618 | 71.0414 | 71.0457 | 0.00428 | -52.464 | -52.2857 | -0.19621 | -0.015547 | 0.47889 | 0.60922 | 0.80543 | 0.098021 | -0.031557 | 71.1016 | 70.9995 | 71.1777 | 71.0051 | -52.4221 | 123.4479 | 123.5615 | 123.4319 | 57.0024 | -123.6596
963.2656 | 123.6877 | -71.1594 | 52.3132 | 0.06235 | -0.0066612 | -0.020834 | -0.043767 | -0.035422 | -0.02966 | 0.050216 | -0.017741 | -0.011804 | 0.0071884 | 0.12515 | 0.0096795 | -0.008109 | -0.048958 | -0.003831 | 0.056706 | -0.054588 | 0.12365 | -0.021847 | -70.708 | -16.396 | -70.5547 | 52.2565 | 52.3838 | 52.2404 | -71.3831 | 71.1375 | -52.2565 | 71.1513 | 71.1555 | 0.018016 | -52.3678 | -52.1896 | -0.22371 | -0.056771 | 0.45139 | 0.60462 | 0.82832 | 0.07053 | -0.072784 | 71.2161 | 71.1048 | 71.283 | 71.1104 | -52.3351 | 123.4158 | 123.5431 | 123.3998 | 54.7634 | -123.6963
964.2812 | 123.7289 | -70.5688 | 52.8809 | 0.06235 | -0.0066612 | -0.022971 | -0.046972 | -0.03649 | -0.030728 | 0.065477 | -0.017741 | -0.012872 | 0.0093254 | 0.12621 | 0.010749 | -0.012688 | -0.053537 | -0.003831 | 0.052128 | -0.054588 | 0.13281 | -0.012689 | -70.2043 | -12.6872 | -70.0877 | 52.7738 | 52.8966 | 52.7578 | -70.8748 | 70.5562 | -52.8287 | 70.5562 | 70.565 | 0.008858 | -52.9354 | -52.748 | -0.30598 | -0.10703 | 0.36454 | 0.48113 | 0.78711 | 0.015707 | -0.12303 | 70.621 | 70.5143 | 70.7017 | 70.5153 | -52.8935 | 123.3427 | 123.4654 | 123.3267 | 57.8816 | -123.7557
965.2656 | 123.7381 | -70.8572 | 52.6154 | 0.06235 | -0.0077302 | -0.021902 | -0.044835 | -0.035422 | -0.030728 | 0.034955 | -0.016673 | -0.009667 | 0.0071884 | 0.12728 | 0.011817 | -0.012688 | -0.058115 | -0.008409 | 0.056706 | -0.050009 | 0.12365 | -0.012689 | -70.5111 | -13.2001 | -70.3762 | 52.4716 | 52.5898 | 52.4419 | -71.1816 | 70.8446 | -52.5587 | 70.8446 | 70.8488 | 0.00428 | -52.6654 | -52.4917 | -0.32436 | -0.14371 | 0.34616 | 0.48106 | 0.80543 | -0.025557 | -0.17345 | 70.9139 | 70.8072 | 70.9809 | 70.7991 | -52.628 | 123.3289 | 123.447 | 123.2991 | 57.6572 | -123.797
966.2656 | 123.6923 | -70.6604 | 52.8168 | 0.06235 | -0.0087982 | -0.021902 | -0.044835 | -0.034354 | -0.030728 | 0.050216 | -0.018809 | -0.011804 | 0.0071884 | 0.12515 | 0.010749 | -0.017266 | -0.058115 | -0.017566 | 0.033814 | -0.050009 | 0.12823 | -0.021847 | -70.0257 | -13.6534 | -69.8725 | 52.957 | 53.066 | 52.941 | -70.6917 | 70.6386 | -52.783 | 70.6431 | 70.6428 | 0.004281 | -52.8668 | -52.6885 | -0.03127 | 0.1402 | 0.63466 | 0.78788 | 0.81915 | 0.2492 | 0.1242 | 70.6942 | 70.6104 | 70.7886 | 70.6023 | -52.8386 | 123.6174 | 123.7264 | 123.6014 | 57.007 | -123.5084
967.2656 | 123.6877 | -70.0241 | 53.4027 | 0.047088 | -0.0077302 | -0.022971 | -0.046972 | -0.03649 | -0.031797 | 0.065477 | -0.017741 | -0.012872 | 0.0071884 | 0.12515 | 0.010749 | -0.017266 | -0.058115 | -0.008409 | 0.061284 | -0.054588 | 0.11907 | -0.021847 | -69.8563 | -13.6121 | -69.6573 | 53.1905 | 53.2995 | 53.1836 | -70.4582 | 70.0023 | -53.3414 | 70.0068 | 70.0157 | 0.013438 | -53.4573 | -53.2836 | -0.43404 | -0.21224 | 0.16778 | 0.36679 | 0.80083 | -0.10323 | -0.21907 | 70.0854 | 69.9695 | 70.1432 | 69.966 | -53.4246 | 123.2146 | 123.3236 | 123.2077 | 56.412 | -123.8609
968.2656 | 123.6969 | -70.166 | 53.302 | 0.047088 | -0.0087982 | -0.022971 | -0.044835 | -0.03649 | -0.031797 | 0.080738 | -0.018809 | -0.011804 | 0.0071884 | 0.12621 | 0.0096795 | -0.021844 | -0.044379 | -0.012988 | 0.042971 | -0.050009 | 0.13739 | -0.021847 | -69.7556 | -13.9143 | -69.5841 | 53.2775 | 53.3911 | 53.2477 | -70.3712 | 70.1442 | -53.259 | 70.1442 | 70.153 | 0.008859 | -53.352 | -53.1646 | -0.20514 | -0.024537 | 0.41042 | 0.58196 | 0.78709 | 0.089053 | -0.054261 | 70.209 | 70.116 | 70.3034 | 70.1216 | -53.3238 | 123.4435 | 123.5571 | 123.4138 | 56.2517 | -123.6732
969.2812 | 123.761 | -70.5231 | 52.8992 | 0.06235 | -0.0066612 | -0.021902 | -0.045904 | -0.03649 | -0.031797 | 0.065477 | -0.018809 | -0.010735 | 0.0061204 | 0.12728 | 0.0096795 | -0.012688 | -0.058115 | -0.008409 | 0.033814 | -0.059167 | 0.10992 | -0.017268 | -70.3829 | -13.603 | -70.2617 | 52.6044 | 52.7134 | 52.5884 | -71.058 | 70.5058 | -52.8654 | 70.5104 | 70.5147 | 0.008859 | -52.9583 | -52.7893 | -0.5349 | -0.29474 | 0.14019 | 0.26136 | 0.79627 | -0.18575 | -0.31075 | 70.5569 | 70.4639 | 70.633 | 70.465 | -52.9164 | 123.1275 | 123.2365 | 123.1115 | 56.9201 | -123.9571
970.2656 | 123.6969 | -70.2209 | 53.2242 | 0.06235 | -0.0087982 | -0.020834 | -0.045904 | -0.03649 | -0.030728 | 0.050216 | -0.018809 | -0.010735 | 0.0082564 | 0.12835 | 0.0096795 | -0.017266 | -0.058115 | -0.012988 | 0.047549 | -0.050009 | 0.12823 | -0.026426 | -70.0349 | -13.4931 | -69.8542 | 52.9661 | 53.0797 | 52.9501 | -70.6779 | 70.1945 | -53.1766 | 70.2037 | 70.208 | 0.013438 | -53.2742 | -53.096 | -0.45699 | -0.25805 | 0.18605 | 0.36674 | 0.82373 | -0.14447 | -0.27405 | 70.2685 | 70.1709 | 70.3492 | 70.1628 | -53.2506 | 123.1871 | 123.3007 | 123.1711 | 56.7278 | -123.9021
971.2656 | 123.674 | -70.4727 | 52.9861 | 0.077612 | -0.0098662 | -0.021902 | -0.046972 | -0.037559 | -0.030728 | 0.065477 | -0.017741 | -0.01394 | 0.0082564 | 0.12835 | 0.0086115 | -0.017266 | -0.053537 | -0.008409 | 0.038393 | -0.054588 | 0.12365 | -0.012689 | -70.0807 | -13.8869 | -69.8176 | 52.9524 | 53.0614 | 52.9227 | -70.6871 | 70.46 | -52.9478 | 70.4555 | 70.4643 | 0.00428 | -53.0407 | -52.8625 | -0.21437 | -0.033753 | 0.39203 | 0.65514 | 0.86952 | 0.07525 | -0.063485 | 70.5111 | 70.4181 | 70.5964 | 70.4192 | -52.9988 | 123.4251 | 123.5341 | 123.3954 | 56.5858 | -123.6732
972.2656 | 123.6923 | -69.9829 | 53.508 | 0.031826 | -0.0098662 | -0.020834 | -0.046972 | -0.035422 | -0.030728 | 0.065477 | -0.018809 | -0.010735 | 0.0082564 | 0.12728 | 0.0086115 | -0.017266 | -0.048958 | 0.000747 | 0.038393 | -0.054588 | 0.11449 | -0.021847 | -69.8243 | -13.4977 | -69.465 | 53.2729 | 53.3773 | 53.2523 | -70.3712 | 69.9611 | -53.4696 | 69.9656 | 69.9837 | 0.022594 | -53.5626 | -53.3935 | -0.38824 | -0.23511 | 0.15863 | 0.5179 | 0.90614 | -0.13068 | -0.25568 | 70.0213 | 69.9283 | 70.0974 | 69.934 | -53.5298 | 123.2558 | 123.3602 | 123.2352 | 56.4852 | -123.8791
973.2656 | 123.674 | -69.5801 | 53.8788 | 0.016564 | -0.0077302 | -0.021902 | -0.045904 | -0.035422 | -0.02966 | 0.065477 | -0.018809 | -0.009667 | 0.0071884 | 0.12728 | 0.010749 | -0.017266 | -0.058115 | -0.012988 | 0.056706 | -0.054588 | 0.13281 | -0.012689 | -69.4168 | -12.3622 | -69.0575 | 53.6758 | 53.7894 | 53.6552 | -69.982 | 69.5674 | -53.8221 | 69.5628 | 69.5671 | -0.000299 | -53.9334 | -53.746 | -0.40188 | -0.20299 | 0.16331 | 0.52257 | 0.92444 | -0.089391 | -0.22355 | 69.6368 | 69.5255 | 69.7129 | 69.522 | -53.8915 | 123.2559 | 123.3695 | 123.2353 | 57.2179 | -123.8607
974.2812 | 123.7335 | -69.5343 | 53.9154 | 0.047088 | -0.0087982 | -0.022971 | -0.046972 | -0.035422 | -0.030728 | 0.050216 | -0.017741 | -0.011804 | 0.0071884 | 0.12835 | 0.0086115 | -0.012688 | -0.053537 | -0.008409 | 0.052128 | -0.054588 | 0.14197 | -0.012689 | -69.4305 | -13.342 | -69.0896 | 53.6621 | 53.7711 | 53.6507 | -69.9911 | 69.5216 | -53.8633 | 69.5216 | 69.5259 | 0.00428 | -53.97 | -53.7734 | -0.45681 | -0.25335 | 0.10379 | 0.44474 | 0.90155 | -0.14433 | -0.26475 | 69.5864 | 69.4797 | 69.6763 | 69.4808 | -53.9281 | 123.1964 | 123.3054 | 123.185 | 56.1923 | -123.9065
975.2656 | 123.7015 | -69.4016 | 54.0115 | 0.031826 | -0.0077302 | -0.022971 | -0.048041 | -0.037559 | -0.027523 | 0.065477 | -0.017741 | -0.010735 | 0.0061204 | 0.12835 | 0.0096795 | -0.008109 | -0.053537 | -0.012988 | 0.042971 | -0.054588 | 0.12365 | -0.017268 | -69.3389 | -14.8438 | -69.0117 | 53.7216 | 53.8352 | 53.7148 | -69.9362 | 69.3843 | -53.9686 | 69.3934 | 69.3886 | 0.00428 | -54.0661 | -53.8879 | -0.53462 | -0.28996 | 0.062616 | 0.38983 | 0.92444 | -0.17636 | -0.29678 | 69.4445 | 69.347 | 69.5252 | 69.348 | -54.0288 | 123.1231 | 123.2367 | 123.1163 | 54.5577 | -123.9477
976.2656 | 123.7106 | -69.4885 | 53.9291 | 0.031826 | -0.0077302 | -0.020834 | -0.046972 | -0.03649 | -0.031797 | 0.050216 | -0.018809 | -0.012872 | 0.0093254 | 0.12835 | 0.0086115 | -0.012688 | -0.058115 | -0.008409 | 0.061284 | -0.059167 | 0.12823 | -0.021847 | -69.1695 | -12.7513 | -68.737 | 53.9139 | 54.0366 | 53.8887 | -69.7301 | 69.4667 | -53.8679 | 69.4758 | 69.4801 | 0.013438 | -53.9883 | -53.8009 | -0.24159 | -0.015262 | 0.319 | 0.75153 | 0.99312 | 0.1075 | -0.040393 | 69.5498 | 69.4294 | 69.6168 | 69.4304 | -53.951 | 123.4024 | 123.5252 | 123.3773 | 56.7372 | -123.6593
977.2656 | 123.6923 | -69.1727 | 54.2953 | 0.06235 | -0.0087982 | -0.021902 | -0.046972 | -0.03649 | -0.031797 | 0.050216 | -0.017741 | -0.012872 | 0.0071884 | 0.12942 | 0.010749 | -0.017266 | -0.058115 | -0.008409 | 0.033814 | -0.059167 | 0.13739 | -0.012689 | -68.7986 | -11.2816 | -68.4623 | 54.2161 | 54.3342 | 54.1909 | -69.4371 | 69.16 | -54.2615 | 69.1554 | 69.1643 | 0.00428 | -54.3545 | -54.158 | -0.26441 | -0.079292 | 0.37402 | 0.71039 | 0.9748 | 0.038898 | -0.10442 | 69.2065 | 69.1135 | 69.3101 | 69.1146 | -54.308 | 123.3887 | 123.5069 | 123.3636 | 57.8911 | -123.7324
978.2656 | 123.6969 | -69.017 | 54.4373 | 0.047088 | -0.0098662 | -0.021902 | -0.046972 | -0.037559 | -0.031797 | 0.065477 | -0.016673 | -0.012872 | 0.0082564 | 0.12728 | 0.0096795 | -0.021844 | -0.053537 | 0.000747 | 0.056706 | -0.054588 | 0.11449 | -0.012689 | -68.4186 | -12.5957 | -68.1463 | 54.4587 | 54.5723 | 54.4428 | -69.1944 | 69.0043 | -54.3805 | 68.9952 | 69.0178 | 0.013436 | -54.4918 | -54.3228 | -0.17737 | 0.021461 | 0.59841 | 0.87068 | 1.0481 | 0.13508 | 0.0055 | 69.0737 | 68.9624 | 69.1315 | 68.9635 | -54.4499 | 123.4757 | 123.5894 | 123.4598 | 56.4214 | -123.6317
979.2812 | 123.6923 | -69.2368 | 54.2221 | 0.047088 | -0.0098662 | -0.021902 | -0.045904 | -0.037559 | -0.030728 | 0.050216 | -0.018809 | -0.01394 | 0.0061204 | 0.12728 | 0.0086115 | -0.008109 | -0.053537 | -0.003831 | 0.056706 | -0.054588 | 0.12823 | -0.021847 | -68.6063 | -12.8612 | -68.3799 | 54.2802 | 54.3892 | 54.2733 | -69.3684 | 69.2149 | -54.1654 | 69.2286 | 69.2329 | 0.018016 | -54.2767 | -54.0939 | -0.13164 | 0.058049 | 0.63041 | 0.8569 | 0.98853 | 0.16708 | 0.051241 | 69.2935 | 69.1822 | 69.365 | 69.1832 | -54.244 | 123.5169 | 123.6259 | 123.5101 | 56.3755 | -123.5905
980.2656 | 123.6969 | -68.8522 | 54.6112 | 0.047088 | -0.0098662 | -0.022971 | -0.046972 | -0.037559 | -0.030728 | 0.050216 | -0.018809 | -0.012872 | 0.0061204 | 0.12942 | 0.0086115 | -0.017266 | -0.044379 | 0.005325 | 0.056706 | -0.050009 | 0.13281 | -0.026426 | -68.3682 | -12.4858 | -68.1555 | 54.4725 | 54.5861 | 54.4656 | -69.1807 | 68.8258 | -54.5545 | 68.835 | 68.8576 | 0.031751 | -54.6612 | -54.4784 | -0.32843 | -0.13875 | 0.48399 | 0.69673 | 1.0252 | -0.025136 | -0.14556 | 68.9089 | 68.8022 | 68.985 | 68.8079 | -54.6376 | 123.3247 | 123.4383 | 123.3179 | 56.3665 | -123.7919
981.2656 | 123.6786 | -68.7698 | 54.6661 | 0.06235 | -0.0098662 | -0.019766 | -0.048041 | -0.035422 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0061204 | 0.12728 | 0.0086115 | -0.017266 | -0.039801 | -0.008409 | 0.042971 | -0.054588 | 0.12823 | -0.021847 | -68.3454 | -15.6909 | -68.1692 | 54.5045 | 54.6181 | 54.4977 | -69.1532 | 68.748 | -54.6232 | 68.7526 | 68.7614 | 0.013438 | -54.7207 | -54.5379 | -0.38335 | -0.16164 | 0.42448 | 0.6006 | 0.98395 | -0.048018 | -0.16844 | 68.8128 | 68.7152 | 68.8981 | 68.73 | -54.688 | 123.2743 | 123.388 | 123.2675 | 53.079 | -123.8193
982.2656 | 123.7015 | -69.0582 | 54.4052 | 0.047088 | -0.010935 | -0.024039 | -0.046972 | -0.037559 | -0.031797 | 0.065477 | -0.018809 | -0.01394 | 0.0071884 | 0.12942 | 0.0075435 | -0.017266 | -0.048958 | -0.017566 | 0.056706 | -0.04543 | 0.11449 | -0.017268 | -68.5789 | -15.3566 | -68.5722 | 54.2206 | 54.3342 | 54.2092 | -69.4279 | 69.041 | -54.3485 | 69.041 | 69.0407 | -0.000298 | -54.4506 | -54.2907 | -0.36969 | -0.18458 | 0.47936 | 0.48606 | 0.85575 | -0.070965 | -0.19597 | 69.1149 | 69.0128 | 69.1727 | 69.0093 | -54.4225 | 123.2789 | 123.3925 | 123.2675 | 53.7016 | -123.8331
983.2656 | 123.7152 | -68.9438 | 54.4876 | 0.047088 | -0.010935 | -0.020834 | -0.045904 | -0.037559 | -0.030728 | 0.050216 | -0.018809 | -0.011804 | 0.0071884 | 0.13049 | 0.0086115 | -0.017266 | -0.048958 | -0.003831 | 0.056706 | -0.054588 | 0.11449 | -0.017268 | -68.4644 | -15.1048 | -68.3982 | 54.3443 | 54.4624 | 54.3329 | -69.3089 | 68.9265 | -54.4309 | 68.9265 | 68.94 | 0.013437 | -54.5422 | -54.3731 | -0.36508 | -0.14336 | 0.47939 | 0.54561 | 0.91069 | -0.025162 | -0.15474 | 69.0005 | 68.8892 | 69.0583 | 68.8948 | -54.5049 | 123.288 | 123.4062 | 123.2767 | 53.839 | -123.7965
984.2969 | 123.7244 | -68.8934 | 54.5654 | 0.06235 | -0.0098662 | -0.022971 | -0.043767 | -0.038627 | -0.031797 | 0.080738 | -0.017741 | -0.010735 | 0.0071884 | 0.12835 | 0.0086115 | -0.017266 | -0.053537 | -0.012988 | 0.052128 | -0.054588 | 0.11449 | -0.012689 | -68.4369 | -15.4574 | -68.4165 | 54.358 | 54.4624 | 54.3466 | -69.2997 | 68.8807 | -54.5133 | 68.8762 | 68.8804 | -0.000299 | -54.62 | -54.4509 | -0.40628 | -0.20744 | 0.4565 | 0.47694 | 0.88322 | -0.10298 | -0.21883 | 68.9456 | 68.8388 | 69.0079 | 68.8399 | -54.5781 | 123.2514 | 123.3559 | 123.24 | 53.4361 | -123.8651
985.2656 | 123.6969 | -68.985 | 54.4922 | 0.06235 | -0.010935 | -0.021902 | -0.046972 | -0.03649 | -0.031797 | 0.050216 | -0.017741 | -0.011804 | 0.0082564 | 0.12835 | 0.0086115 | -0.017266 | -0.048958 | -0.008409 | 0.047549 | -0.059167 | 0.12365 | -0.021847 | -68.4232 | -15.32 | -68.3799 | 54.3534 | 54.4716 | 54.3374 | -69.3043 | 68.9631 | -54.4446 | 68.9677 | 68.9766 | 0.013438 | -54.5514 | -54.3685 | -0.3193 | -0.13878 | 0.56179 | 0.60513 | 0.92443 | -0.020582 | -0.15474 | 69.0325 | 68.9258 | 69.1086 | 68.936 | -54.514 | 123.3384 | 123.4566 | 123.3224 | 53.665 | -123.7965
986.2656 | 123.674 | -68.9621 | 54.4785 | 0.06235 | -0.012003 | -0.020834 | -0.045904 | -0.03649 | -0.032865 | 0.065477 | -0.018809 | -0.012872 | 0.0071884 | 0.12942 | 0.0086115 | -0.026423 | -0.053537 | -0.008409 | 0.047549 | -0.054588 | 0.12823 | -0.017268 | -68.295 | -17.1606 | -68.2059 | 54.4953 | 54.6135 | 54.4702 | -69.1623 | 68.9448 | -54.4309 | 68.9357 | 68.9537 | 0.008859 | -54.533 | -54.3502 | -0.20025 | 0.01689 | 0.66711 | 0.75623 | 0.95648 | 0.13509 | -0.008227 | 69.0096 | 68.9075 | 69.0903 | 68.9086 | -54.4957 | 123.4574 | 123.5756 | 123.4323 | 51.8015 | -123.6408
987.2812 | 123.7244 | -68.6966 | 54.744 | 0.047088 | -0.010935 | -0.024039 | -0.045904 | -0.037559 | -0.032865 | 0.080738 | -0.019877 | -0.010735 | 0.0082564 | 0.12942 | 0.0096795 | -0.021844 | -0.044379 | -0.003831 | 0.042971 | -0.054588 | 0.11907 | -0.017268 | -68.1668 | -16.7898 | -68.0593 | 54.6327 | 54.7463 | 54.6259 | -69.025 | 68.6793 | -54.701 | 68.6748 | 68.6928 | 0.013437 | -54.7985 | -54.6249 | -0.32839 | -0.11126 | 0.52981 | 0.63724 | 0.96563 | 0.002363 | -0.11806 | 68.7396 | 68.642 | 68.8157 | 68.6522 | -54.7612 | 123.3293 | 123.4429 | 123.3225 | 51.9068 | -123.7689
988.2656 | 123.7061 | -68.7195 | 54.7211 | 0.031826 | -0.012003 | -0.021902 | -0.045904 | -0.035422 | -0.032865 | 0.065477 | -0.016673 | -0.011804 | 0.0061204 | 0.12942 | 0.0064745 | -0.021844 | -0.048958 | -0.008409 | 0.033814 | -0.054588 | 0.12823 | -0.017268 | -68.1988 | -14.5004 | -68.0639 | 54.6098 | 54.7188 | 54.5939 | -69.0387 | 68.7022 | -54.6873 | 68.6976 | 68.7111 | 0.008859 | -54.7757 | -54.5928 | -0.31924 | -0.11126 | 0.52065 | 0.65555 | 0.97479 | -0.00222 | -0.12722 | 68.7533 | 68.6649 | 68.8477 | 68.6705 | -54.7383 | 123.3293 | 123.4383 | 123.3133 | 54.2191 | -123.7598
989.2656 | 123.7244 | -68.5822 | 54.8492 | 0.047088 | -0.010935 | -0.022971 | -0.045904 | -0.037559 | -0.031797 | 0.065477 | -0.017741 | -0.012872 | 0.0061204 | 0.12942 | 0.0075435 | -0.012688 | -0.048958 | -0.008409 | 0.052128 | -0.050009 | 0.12365 | -0.017268 | -68.1118 | -14.07 | -67.9495 | 54.7105 | 54.8242 | 54.6946 | -68.9426 | 68.5649 | -54.7971 | 68.5695 | 68.5737 | 0.008859 | -54.8993 | -54.7256 | -0.36041 | -0.13871 | 0.47031 | 0.63269 | 0.9931 | -0.025086 | -0.15466 | 68.6343 | 68.5321 | 68.7058 | 68.5332 | -54.8665 | 123.2927 | 123.4063 | 123.2767 | 54.5121 | -123.7918
990.2656 | 123.7015 | -68.3807 | 55.0919 | 0.047088 | -0.012003 | -0.022971 | -0.046972 | -0.038627 | -0.032865 | 0.065477 | -0.017741 | -0.012872 | 0.0050524 | 0.13049 | 0.0064745 | -0.021844 | -0.053537 | -0.017566 | 0.047549 | -0.059167 | 0.12365 | -0.012689 | -67.9699 | -13.5343 | -67.7388 | 54.9486 | 55.0485 | 54.9327 | -68.7136 | 68.368 | -55.0443 | 68.3589 | 68.3632 | -0.004877 | -55.151 | -54.9682 | -0.33288 | -0.14324 | 0.41084 | 0.6419 | 0.97478 | -0.043349 | -0.15919 | 68.4283 | 68.3216 | 68.5044 | 68.3272 | -55.1045 | 123.3294 | 123.4292 | 123.3134 | 54.8464 | -123.8055
991.2656 | 123.7198 | -68.3166 | 55.1468 | 0.047088 | -0.012003 | -0.020834 | -0.046972 | -0.035422 | -0.031797 | 0.065477 | -0.020945 | -0.012872 | 0.0071884 | 0.12835 | 0.0086115 | -0.017266 | -0.048958 | -0.003831 | 0.038393 | -0.054588 | 0.11449 | -0.017268 | -68.0294 | -10.1873 | -67.7526 | 54.9761 | 55.076 | 54.951 | -68.6861 | 68.2994 | -55.1084 | 68.2994 | 68.3128 | 0.013437 | -55.2014 | -55.0323 | -0.3695 | -0.1707 | 0.28723 | 0.56407 | 0.93357 | -0.07081 | -0.19581 | 68.355 | 68.2621 | 68.4311 | 68.2677 | -55.1641 | 123.2927 | 123.3926 | 123.2676 | 58.1294 | -123.8329
992.2812 | 123.7289 | -68.4952 | 54.9774 | 0.06235 | -0.0098662 | -0.022971 | -0.048041 | -0.035422 | -0.032865 | 0.065477 | -0.019877 | -0.011804 | 0.0071884 | 0.12942 | 0.0075435 | -0.012688 | -0.044379 | -0.017566 | 0.052128 | -0.054588 | 0.11449 | -0.021847 | -68.0294 | -10.3338 | -67.8075 | 54.9624 | 55.0668 | 54.9647 | -68.6907 | 68.4733 | -54.9253 | 68.4825 | 68.4776 | 0.004281 | -55.032 | -54.8629 | -0.19555 | -0.015066 | 0.46576 | 0.68766 | 0.88321 | 0.089406 | -0.0127 | 68.5473 | 68.4406 | 68.6097 | 68.4508 | -54.9993 | 123.4575 | 123.562 | 123.4599 | 58.1614 | -123.6681
993.2656 | 123.6786 | -67.9413 | 55.5588 | 0.047088 | -0.012003 | -0.021902 | -0.046972 | -0.038627 | -0.031797 | 0.065477 | -0.019877 | -0.011804 | 0.0071884 | 0.12835 | 0.0075435 | -0.026423 | -0.048958 | -0.012988 | 0.042971 | -0.059167 | 0.12365 | -0.021847 | -67.6357 | -12.7788 | -67.3405 | 55.3698 | 55.4881 | 55.3676 | -68.2786 | 67.9194 | -55.5158 | 67.9149 | 67.9283 | 0.008859 | -55.6179 | -55.4351 | -0.33735 | -0.18894 | 0.30563 | 0.60079 | 0.93814 | -0.070722 | -0.19114 | 67.9843 | 67.8821 | 68.0649 | 67.8923 | -55.5806 | 123.3111 | 123.4293 | 123.3089 | 55.1625 | -123.8374
994.2812 | 123.7106 | -68.1015 | 55.3802 | 0.077612 | -0.013072 | -0.022971 | -0.046972 | -0.03649 | -0.031797 | 0.050216 | -0.018809 | -0.01394 | 0.0061204 | 0.13049 | 0.010749 | -0.017266 | -0.048958 | -0.003831 | 0.052128 | -0.054588 | 0.12365 | -0.026426 | -67.599 | -18.3877 | -67.2031 | 55.3973 | 55.5064 | 55.3905 | -68.2512 | 68.0751 | -55.3281 | 68.0842 | 68.0977 | 0.022595 | -55.4348 | -55.2566 | -0.14966 | 0.017059 | 0.50248 | 0.89837 | 1.048 | 0.12612 | 0.010278 | 68.1536 | 68.0469 | 68.2252 | 68.0525 | -55.4067 | 123.4988 | 123.6079 | 123.492 | 49.7138 | -123.6314
995.2656 | 123.7106 | -67.9962 | 55.4626 | 0.06235 | -0.010935 | -0.021902 | -0.046972 | -0.037559 | -0.031797 | 0.065477 | -0.018809 | -0.010735 | 0.0071884 | 0.12942 | 0.0075435 | -0.021844 | -0.058115 | -0.012988 | 0.047549 | -0.054588 | 0.13281 | -0.017268 | -67.5944 | -19.8071 | -67.1894 | 55.3607 | 55.4743 | 55.3356 | -68.3015 | 67.9789 | -55.4151 | 67.9744 | 67.9832 | 0.00428 | -55.5172 | -55.3298 | -0.30531 | -0.10197 | 0.40177 | 0.80682 | 1.1121 | 0.011673 | -0.12706 | 68.0438 | 67.9416 | 68.129 | 67.9381 | -55.4799 | 123.3569 | 123.4705 | 123.3318 | 48.1891 | -123.7642
996.2656 | 123.7656 | -68.0695 | 55.394 | 0.047088 | -0.012003 | -0.022971 | -0.045904 | -0.03649 | -0.031797 | 0.065477 | -0.019877 | -0.01394 | 0.0082564 | 0.12835 | 0.0086115 | -0.021844 | -0.053537 | -0.003831 | 0.047549 | -0.050009 | 0.10992 | -0.017268 | -67.6311 | -19.3264 | -67.2214 | 55.3103 | 55.424 | 55.3035 | -68.3473 | 68.0522 | -55.3464 | 68.0476 | 68.0656 | 0.013437 | -55.444 | -55.2841 | -0.27786 | -0.083665 | 0.43838 | 0.84801 | 1.1259 | 0.029972 | -0.090449 | 68.117 | 68.0194 | 68.1794 | 68.0159 | -55.4113 | 123.3798 | 123.4934 | 123.373 | 48.7431 | -123.7413
997.2812 | 123.7839 | -68.0969 | 55.3436 | 0.077612 | -0.013072 | -0.022971 | -0.048041 | -0.038627 | -0.030728 | 0.050216 | -0.018809 | -0.01394 | 0.0082564 | 0.12942 | 0.0096795 | -0.012688 | -0.048958 | -0.003831 | 0.052128 | -0.050009 | 0.12365 | -0.021847 | -67.6952 | -18.2687 | -67.3268 | 55.26 | 55.3644 | 55.244 | -68.4023 | 68.0751 | -55.2915 | 68.0842 | 68.0931 | 0.018016 | -55.3936 | -55.22 | -0.30534 | -0.083674 | 0.40175 | 0.77017 | 1.0755 | 0.020804 | -0.099617 | 68.1491 | 68.0469 | 68.2206 | 68.048 | -55.3655 | 123.3569 | 123.4614 | 123.3409 | 49.8282 | -123.7459
998.2656 | 123.7427 | -68.1015 | 55.3574 | 0.047088 | -0.0098662 | -0.020834 | -0.046972 | -0.037559 | -0.031797 | 0.080738 | -0.019877 | -0.012872 | 0.0071884 | 0.13049 | 0.0096795 | -0.017266 | -0.048958 | -0.012988 | 0.056706 | -0.050009 | 0.11907 | -0.017268 | -67.7181 | -17.1011 | -67.3451 | 55.2325 | 55.3415 | 55.212 | -68.4297 | 68.0842 | -55.3007 | 68.0842 | 68.0885 | 0.00428 | -55.4074 | -55.2383 | -0.32823 | -0.12488 | 0.38343 | 0.75643 | 1.0847 | -0.015822 | -0.1454 | 68.1582 | 68.0515 | 68.2206 | 68.0525 | -55.3746 | 123.334 | 123.443 | 123.3135 | 51.0004 | -123.7871
999.2812 | 123.6191 | -68.074 | 55.4626 | 0.047088 | -0.01414 | -0.021902 | -0.046972 | -0.037559 | -0.032865 | 0.080738 | -0.019877 | -0.01394 | 0.0071884 | 0.13049 | 0.0086115 | -0.021844 | -0.048958 | -0.003831 | 0.052128 | -0.050009 | 0.13739 | -0.035584 | -67.5761 | -20.2055 | -67.1802 | 55.3698 | 55.4835 | 55.3676 | -68.2878 | 68.0385 | -55.4105 | 68.0522 | 68.0702 | 0.031753 | -55.5127 | -55.3253 | -0.21375 | -0.092809 | 0.49791 | 0.8938 | 1.1076 | 0.02083 | -0.095012 | 68.1262 | 68.024 | 68.2114 | 68.0251 | -55.4982 | 123.4439 | 123.5575 | 123.4417 | 47.8685 | -123.7504
1000.2656 | 123.7244 | -67.8726 | 55.5542 | 0.077612 | -0.013072 | -0.024039 | -0.048041 | -0.037559 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0082564 | 0.13049 | 0.0096795 | -0.017266 | -0.044379 | -0.008409 | 0.056706 | -0.040851 | 0.11907 | -0.017268 | -67.6585 | -20.906 | -67.3313 | 55.3149 | 55.4331 | 55.2898 | -68.3473 | 67.8554 | -55.4975 | 67.8554 | 67.8642 | 0.008859 | -55.5951 | -55.4351 | -0.4747 | -0.2393 | 0.21407 | 0.54129 | 1.016 | -0.12109 | -0.2644 | 67.9293 | 67.8318 | 67.9917 | 67.8282 | -55.5715 | 123.1875 | 123.3057 | 123.1624 | 46.9666 | -123.9015
1001.2812 | 123.7473 | -67.9733 | 55.4901 | 0.047088 | -0.0098662 | -0.022971 | -0.049109 | -0.038627 | -0.030728 | 0.080738 | -0.019877 | -0.012872 | 0.0061204 | 0.13049 | 0.0064745 | -0.008109 | -0.048958 | -0.003831 | 0.056706 | -0.04543 | 0.12365 | -0.026426 | -67.48 | -22.2842 | -67.1207 | 55.5072 | 55.6208 | 55.4958 | -68.155 | 67.9469 | -55.4334 | 67.9652 | 67.9695 | 0.022595 | -55.5355 | -55.3665 | -0.18168 | 0.01708 | 0.49335 | 0.85261 | 1.0343 | 0.13072 | 0.005723 | 68.03 | 67.9279 | 68.097 | 67.9244 | -55.5165 | 123.4805 | 123.5942 | 123.4692 | 45.6891 | -123.6451
1002.2812 | 123.642 | -67.662 | 55.8517 | 0.06235 | -0.013072 | -0.021902 | -0.049109 | -0.03649 | -0.032865 | 0.065477 | -0.017741 | -0.011804 | 0.0071884 | 0.13262 | 0.0064745 | -0.017266 | -0.048958 | -0.003831 | 0.052128 | -0.050009 | 0.12365 | -0.021847 | -67.4113 | -22.9023 | -67.0383 | 55.585 | 55.6941 | 55.5828 | -68.068 | 67.6402 | -55.7996 | 67.6448 | 67.6582 | 0.018016 | -55.9018 | -55.7281 | -0.40596 | -0.26672 | 0.25075 | 0.62375 | 1.0297 | -0.15765 | -0.26892 | 67.7142 | 67.612 | 67.7857 | 67.6131 | -55.8736 | 123.2471 | 123.3561 | 123.2449 | 44.7597 | -123.9198
1003.2656 | 123.7427 | -67.7994 | 55.6274 | 0.06235 | -0.013072 | -0.022971 | -0.048041 | -0.039695 | -0.030728 | 0.050216 | -0.018809 | -0.012872 | 0.0061204 | 0.12942 | 0.0075435 | -0.012688 | -0.048958 | -0.008409 | 0.047549 | -0.059167 | 0.12823 | -0.017268 | -67.3701 | -22.3346 | -67.0291 | 55.6079 | 55.7307 | 55.6057 | -68.0405 | 67.7821 | -55.5799 | 67.7867 | 67.791 | 0.008859 | -55.6866 | -55.4992 | -0.24116 | -0.019522 | 0.42929 | 0.77024 | 1.0114 | 0.10328 | -0.02172 | 67.8469 | 67.7402 | 67.9276 | 67.7504 | -55.6447 | 123.4073 | 123.5301 | 123.4051 | 45.4648 | -123.668
1004.2812 | 123.7564 | -67.5476 | 55.9021 | 0.06235 | -0.015208 | -0.021902 | -0.046972 | -0.03649 | -0.030728 | 0.065477 | -0.017741 | -0.015009 | 0.0071884 | 0.13049 | 0.0086115 | -0.017266 | -0.053537 | -0.003831 | 0.047549 | -0.054588 | 0.11907 | -0.021847 | -67.2053 | -22.623 | -66.7865 | 55.7819 | 55.8864 | 55.7706 | -67.8803 | 67.5258 | -55.8546 | 67.5303 | 67.5438 | 0.018016 | -55.9567 | -55.783 | -0.33267 | -0.1202 | 0.34235 | 0.76114 | 1.0938 | -0.015707 | -0.13155 | 67.5952 | 67.493 | 67.6667 | 67.4941 | -55.9239 | 123.3295 | 123.434 | 123.3182 | 44.9246 | -123.7824
1005.2656 | 123.7198 | -67.6117 | 55.8426 | 0.047088 | -0.01414 | -0.022971 | -0.048041 | -0.03649 | -0.031797 | 0.050216 | -0.019877 | -0.012872 | 0.0071884 | 0.13049 | 0.0064745 | -0.012688 | -0.058115 | -0.003831 | 0.056706 | -0.054588 | 0.12365 | -0.021847 | -67.2098 | -21.8035 | -66.8139 | 55.7773 | 55.8864 | 55.766 | -67.8803 | 67.5898 | -55.7859 | 67.599 | 67.6079 | 0.018016 | -55.8972 | -55.7189 | -0.26858 | -0.065267 | 0.40186 | 0.79775 | 1.0663 | 0.043803 | -0.076618 | 67.6684 | 67.5571 | 67.7353 | 67.5536 | -55.8644 | 123.389 | 123.4981 | 123.3777 | 45.8082 | -123.7229
1006.2812 | 123.7061 | -67.5705 | 55.957 | 0.092874 | -0.013072 | -0.021902 | -0.048041 | -0.038627 | -0.031797 | 0.080738 | -0.018809 | -0.01394 | 0.0071884 | 0.13156 | 0.0075435 | -0.012688 | -0.053537 | -0.008409 | 0.056706 | -0.04543 | 0.12823 | -0.017268 | -67.306 | -22.6047 | -66.965 | 55.672 | 55.7857 | 55.6652 | -67.9856 | 67.5532 | -55.9003 | 67.5578 | 67.5621 | 0.008859 | -56.0025 | -55.8288 | -0.41509 | -0.28501 | 0.26451 | 0.60546 | 1.0206 | -0.17137 | -0.29179 | 67.6272 | 67.5251 | 67.6987 | 67.517 | -55.9743 | 123.2425 | 123.3562 | 123.2357 | 44.9658 | -123.9426
1007.2812 | 123.7198 | -67.5476 | 55.9158 | 0.047088 | -0.013072 | -0.024039 | -0.046972 | -0.03649 | -0.02966 | 0.080738 | -0.019877 | -0.012872 | 0.0050524 | 0.13156 | 0.0054065 | -0.017266 | -0.053537 | -0.008409 | 0.047549 | -0.050009 | 0.13281 | -0.012689 | -67.2877 | -22.2201 | -66.9284 | 55.6903 | 55.8086 | 55.6881 | -67.981 | 67.5349 | -55.8683 | 67.5303 | 67.5392 | 0.00428 | -55.9658 | -55.783 | -0.4334 | -0.2255 | 0.25993 | 0.6192 | 1.0526 | -0.10728 | -0.2277 | 67.5952 | 67.4976 | 67.6804 | 67.4941 | -55.9285 | 123.2379 | 123.3562 | 123.2357 | 45.3275 | -123.8968
1008.2656 | 123.6969 | -67.5156 | 55.9296 | 0.047088 | -0.01414 | -0.022971 | -0.049109 | -0.03649 | -0.031797 | 0.080738 | -0.019877 | -0.012872 | 0.0061204 | 0.12942 | 0.0054065 | -0.017266 | -0.058115 | -0.003831 | 0.052128 | -0.059167 | 0.11907 | -0.017268 | -67.1183 | -22.0095 | -66.7086 | 55.8689 | 55.9871 | 55.8759 | -67.7933 | 67.4983 | -55.8774 | 67.4983 | 67.5117 | 0.013437 | -55.9887 | -55.8105 | -0.27772 | -0.060672 | 0.3973 | 0.80693 | 1.0846 | 0.057557 | -0.053706 | 67.5677 | 67.4564 | 67.6346 | 67.4574 | -55.9468 | 123.3845 | 123.5027 | 123.3914 | 45.5061 | -123.7228
1009.2812 | 123.6145 | -67.5247 | 56.0028 | 0.06235 | -0.01414 | -0.021902 | -0.046972 | -0.037559 | -0.032865 | 0.065477 | -0.018809 | -0.01394 | 0.0061204 | 0.13262 | 0.0064745 | -0.021844 | -0.048958 | -0.012988 | 0.052128 | -0.054588 | 0.13739 | -0.026426 | -67.045 | -21.7119 | -66.5713 | 55.9513 | 56.065 | 55.9491 | -67.7109 | 67.4983 | -55.9507 | 67.5029 | 67.5117 | 0.013438 | -56.0574 | -55.8654 | -0.18614 | -0.051502 | 0.47972 | 0.95345 | 1.1396 | 0.062151 | -0.053692 | 67.5768 | 67.4701 | 67.6621 | 67.4758 | -56.0292 | 123.476 | 123.5897 | 123.4738 | 45.8128 | -123.7137
1010.2656 | 123.7518 | -67.3004 | 56.1539 | 0.031826 | -0.013072 | -0.021902 | -0.046972 | -0.037559 | -0.030728 | 0.065477 | -0.018809 | -0.01394 | 0.0061204 | 0.13049 | 0.0064745 | -0.021844 | -0.039801 | -0.008409 | 0.056706 | -0.050009 | 0.11449 | -0.017268 | -66.9488 | -21.634 | -66.5713 | 56.0291 | 56.1565 | 56.0132 | -67.6376 | 67.2831 | -56.0972 | 67.2786 | 67.292 | 0.008859 | -56.2039 | -56.0394 | -0.33718 | -0.12473 | 0.35157 | 0.72915 | 1.0663 | 0.002661 | -0.14065 | 67.3571 | 67.2504 | 67.4149 | 67.2606 | -56.1711 | 123.3296 | 123.4569 | 123.3136 | 45.6664 | -123.7915
1011.2812 | 123.6053 | -66.9525 | 56.5796 | 0.047088 | -0.01414 | -0.024039 | -0.048041 | -0.037559 | -0.032865 | 0.080738 | -0.018809 | -0.01394 | 0.0082564 | 0.13156 | 0.0064745 | -0.017266 | -0.048958 | -0.008409 | 0.038393 | -0.059167 | 0.13739 | -0.017268 | -66.5551 | -19.3996 | -66.1317 | 56.4183 | 56.532 | 56.4161 | -67.2392 | 66.9352 | -56.5412 | 66.9352 | 66.9441 | 0.008859 | -56.6388 | -56.4422 | -0.28673 | -0.16128 | 0.39744 | 0.8208 | 1.1075 | -0.047614 | -0.16346 | 66.9909 | 66.8933 | 67.0899 | 66.9036 | -56.5969 | 123.3708 | 123.4845 | 123.3686 | 47.5529 | -123.8188
1012.2812 | 123.6099 | -67.1036 | 56.4423 | 0.031826 | -0.015208 | -0.024039 | -0.050177 | -0.03649 | -0.031797 | 0.050216 | -0.019877 | -0.012872 | 0.0061204 | 0.13369 | 0.0086115 | -0.017266 | -0.048958 | -0.008409 | 0.047549 | -0.050009 | 0.13281 | -0.021847 | -66.6375 | -18.8868 | -66.2508 | 56.3267 | 56.4358 | 56.3154 | -67.3354 | 67.0817 | -56.3947 | 67.0863 | 67.0952 | 0.013438 | -56.4923 | -56.3095 | -0.23182 | -0.11552 | 0.46608 | 0.85282 | 1.0846 | -0.006436 | -0.12686 | 67.1511 | 67.0536 | 67.2364 | 67.0546 | -56.4641 | 123.4303 | 123.5394 | 123.419 | 48.2168 | -123.7777
1013.2812 | 123.7381 | -67.186 | 56.2866 | 0.06235 | -0.015208 | -0.022971 | -0.048041 | -0.037559 | -0.031797 | 0.034955 | -0.017741 | -0.012872 | 0.0061204 | 0.13262 | 0.0075435 | -0.017266 | -0.048958 | -0.003831 | 0.042971 | -0.050009 | 0.12823 | -0.00811 | -66.7382 | -19.6057 | -66.3698 | 56.194 | 56.3214 | 56.1826 | -67.4636 | 67.1779 | -56.2436 | 67.1687 | 67.1821 | 0.004279 | -56.3366 | -56.1584 | -0.27763 | -0.092654 | 0.44775 | 0.81617 | 1.0938 | 0.034739 | -0.104 | 67.2289 | 67.136 | 67.3142 | 67.137 | -56.2947 | 123.3799 | 123.5073 | 123.3686 | 47.5803 | -123.7502
1014.2812 | 123.7106 | -66.9937 | 56.4743 | 0.047088 | -0.01414 | -0.022971 | -0.046972 | -0.038627 | -0.030728 | 0.065477 | -0.018809 | -0.012872 | 0.0061204 | 0.13262 | 0.0075435 | -0.021844 | -0.053537 | 0.000747 | 0.042971 | -0.050009 | 0.10992 | -0.017268 | -66.5917 | -22.5818 | -66.2324 | 56.3725 | 56.4908 | 56.3703 | -67.2896 | 66.9764 | -56.4313 | 66.9719 | 66.9945 | 0.018015 | -56.5243 | -56.3644 | -0.2959 | -0.10178 | 0.402 | 0.76127 | 1.0572 | 0.016465 | -0.10396 | 67.0367 | 66.9437 | 67.1036 | 66.9402 | -56.4916 | 123.3662 | 123.4845 | 123.3641 | 44.4119 | -123.7639
1015.2812 | 123.7106 | -66.7648 | 56.6849 | 0.031826 | -0.015208 | -0.022971 | -0.046972 | -0.037559 | -0.033933 | 0.11126 | -0.017741 | -0.011804 | 0.0061204 | 0.13156 | 0.0064745 | -0.017266 | -0.053537 | 0.000747 | 0.042971 | -0.050009 | 0.11907 | -0.012689 | -66.3719 | -22.069 | -66.063 | 56.5374 | 56.651 | 56.5214 | -67.1248 | 66.7521 | -56.6419 | 66.7476 | 66.7656 | 0.013436 | -56.7349 | -56.5658 | -0.35994 | -0.14752 | 0.3929 | 0.7018 | 1.0617 | -0.033855 | -0.16343 | 66.8078 | 66.7148 | 66.8839 | 66.7113 | -56.6976 | 123.3022 | 123.4159 | 123.2863 | 44.6958 | -123.8096
1016.2812 | 123.6053 | -67.1585 | 56.4102 | 0.047088 | -0.015208 | -0.020834 | -0.046972 | -0.038627 | -0.031797 | 0.065477 | -0.019877 | -0.01394 | 0.0061204 | 0.13369 | 0.0064745 | -0.017266 | -0.053537 | -0.012988 | 0.056706 | -0.04543 | 0.12365 | -0.021847 | -66.6009 | -22.6093 | -66.2737 | 56.2993 | 56.4084 | 56.2925 | -67.3629 | 67.1367 | -56.3535 | 67.1412 | 67.1455 | 0.008859 | -56.4556 | -56.2866 | -0.20436 | -0.11095 | 0.55764 | 0.88486 | 1.0892 | -0.001863 | -0.11771 | 67.2152 | 67.1131 | 67.2822 | 67.105 | -56.4321 | 123.4578 | 123.5669 | 123.451 | 44.5492 | -123.7731
1017.2969 | 123.7152 | -67.1722 | 56.2683 | 0.06235 | -0.013072 | -0.024039 | -0.046972 | -0.037559 | -0.032865 | 0.065477 | -0.018809 | -0.011804 | 0.0071884 | 0.13156 | 0.0064745 | -0.026423 | -0.048958 | -0.008409 | 0.052128 | -0.050009 | 0.13739 | -0.021847 | -66.436 | -18.6121 | -66.3286 | 56.2764 | 56.39 | 56.2605 | -67.3949 | 67.1504 | -56.2162 | 67.1458 | 67.1638 | 0.013438 | -56.3183 | -56.1309 | -0.22268 | 0.008068 | 0.73621 | 0.84364 | 1.0663 | 0.12173 | -0.00785 | 67.2244 | 67.1222 | 67.3096 | 67.1233 | -56.2902 | 123.4486 | 123.5623 | 123.4327 | 48.5601 | -123.6632
1018.2656 | 123.7518 | -67.0303 | 56.4056 | 0.031826 | -0.01414 | -0.024039 | -0.046972 | -0.038627 | -0.032865 | 0.050216 | -0.019877 | -0.01394 | 0.0061204 | 0.13156 | 0.0064745 | -0.017266 | -0.058115 | -0.008409 | 0.042971 | -0.054588 | 0.12823 | -0.026426 | -66.5459 | -20.4619 | -66.3469 | 56.2443 | 56.3626 | 56.2284 | -67.4224 | 67.0039 | -56.3627 | 67.0131 | 67.0219 | 0.018017 | -56.4602 | -56.2774 | -0.39206 | -0.16131 | 0.48441 | 0.68342 | 1.0755 | -0.043072 | -0.17723 | 67.0733 | 66.9757 | 67.1586 | 66.9722 | -56.4321 | 123.2747 | 123.3929 | 123.2587 | 46.5684 | -123.828
1019.2812 | 123.7289 | -66.8381 | 56.662 | 0.06235 | -0.01414 | -0.021902 | -0.051246 | -0.03649 | -0.032865 | 0.065477 | -0.019877 | -0.011804 | 0.0061204 | 0.13262 | 0.0054065 | -0.012688 | -0.062694 | -0.012988 | 0.042971 | -0.059167 | 0.13281 | -0.026426 | -66.317 | -21.4372 | -66.1683 | 56.4 | 56.5137 | 56.3932 | -67.253 | 66.8116 | -56.619 | 66.8254 | 66.8251 | 0.013438 | -56.7212 | -56.5292 | -0.4149 | -0.26199 | 0.52109 | 0.66973 | 1.0846 | -0.14833 | -0.26875 | 66.881 | 66.7789 | 66.9709 | 66.7754 | -56.6884 | 123.2381 | 123.3517 | 123.2313 | 45.4009 | -123.915
1020.2656 | 123.7518 | -67.099 | 56.3461 | 0.047088 | -0.015208 | -0.022971 | -0.048041 | -0.037559 | -0.030728 | 0.050216 | -0.019877 | -0.012872 | 0.0071884 | 0.13369 | 0.0064745 | -0.017266 | -0.058115 | -0.003831 | 0.042971 | -0.054588 | 0.12365 | -0.017268 | -66.4818 | -17.8566 | -66.3286 | 56.2581 | 56.3763 | 56.2559 | -67.4087 | 67.0817 | -56.3032 | 67.0817 | 67.0952 | 0.013437 | -56.4007 | -56.2225 | -0.30966 | -0.088065 | 0.61718 | 0.7704 | 1.0801 | 0.030173 | -0.090247 | 67.142 | 67.0444 | 67.2227 | 67.0409 | -56.3634 | 123.3571 | 123.4753 | 123.3549 | 49.2424 | -123.7548
1021.2656 | 123.7244 | -66.6687 | 56.8451 | 0.047088 | -0.01414 | -0.025108 | -0.046972 | -0.035422 | -0.02966 | 0.065477 | -0.017741 | -0.012872 | 0.0071884 | 0.13262 | 0.0054065 | -0.012688 | -0.058115 | -0.008409 | 0.052128 | -0.054588 | 0.11449 | -0.017268 | -65.9873 | -16.8859 | -65.7288 | 56.8029 | 56.9257 | 56.7824 | -66.8592 | 66.6514 | -56.793 | 66.656 | 66.6603 | 0.008859 | -56.8997 | -56.7306 | -0.1905 | -0.042187 | 0.68138 | 0.93991 | 1.1304 | 0.080643 | -0.062671 | 66.7208 | 66.6141 | 66.7832 | 66.6106 | -56.8624 | 123.4716 | 123.5944 | 123.4511 | 49.7828 | -123.7043
1022.2812 | 123.6328 | -66.5497 | 56.9687 | 0.047088 | -0.015208 | -0.024039 | -0.050177 | -0.038627 | -0.030728 | 0.050216 | -0.018809 | -0.012872 | 0.0039834 | 0.13369 | 0.0064745 | -0.017266 | -0.053537 | -0.008409 | 0.052128 | -0.054588 | 0.12365 | -0.026426 | -65.9782 | -17.9024 | -65.6876 | 56.835 | 56.9578 | 56.8328 | -66.8271 | 66.5233 | -56.9166 | 66.5324 | 66.5413 | 0.018017 | -57.0233 | -56.845 | -0.27746 | -0.13373 | 0.57152 | 0.8621 | 1.1396 | -0.010903 | -0.1359 | 66.6018 | 66.4951 | 66.6733 | 66.4961 | -56.9951 | 123.3846 | 123.5075 | 123.3825 | 48.6473 | -123.7958
1023.2812 | 123.7244 | -66.7236 | 56.7535 | 0.06235 | -0.016277 | -0.022971 | -0.048041 | -0.03649 | -0.030728 | 0.065477 | -0.017741 | -0.012872 | 0.0050524 | 0.13262 | 0.0064745 | -0.017266 | -0.053537 | -0.003831 | 0.052128 | -0.050009 | 0.14197 | -0.017268 | -66.0789 | -18.287 | -65.7929 | 56.7525 | 56.8754 | 56.7458 | -66.9096 | 66.7064 | -56.7014 | 66.7064 | 66.7198 | 0.013437 | -56.8035 | -56.6116 | -0.18593 | -0.000997 | 0.64474 | 0.93075 | 1.1167 | 0.12183 | -0.007747 | 66.7758 | 66.6736 | 66.8656 | 66.6701 | -56.7708 | 123.4762 | 123.599 | 123.4694 | 48.4366 | -123.6631
1024.2812 | 123.7106 | -66.5543 | 56.9046 | 0.077612 | -0.015208 | -0.024039 | -0.048041 | -0.037559 | -0.031797 | 0.050216 | -0.018809 | -0.011804 | 0.0061204 | 0.13369 | 0.0064745 | -0.021844 | -0.048958 | -0.008409 | 0.047549 | -0.054588 | 0.12823 | -0.012689 | -66.0377 | -17.8337 | -65.7517 | 56.78 | 56.8983 | 56.7687 | -66.8913 | 66.5416 | -56.8571 | 66.5324 | 66.5459 | 0.00428 | -56.9592 | -56.7764 | -0.33699 | -0.12459 | 0.51658 | 0.80258 | 1.1396 | -0.006338 | -0.13592 | 66.6018 | 66.4997 | 66.6825 | 66.5053 | -56.9173 | 123.3343 | 123.4525 | 123.3229 | 48.7205 | -123.7959
1025.2812 | 123.7061 | -66.2888 | 57.2113 | 0.031826 | -0.013072 | -0.022971 | -0.049109 | -0.037559 | -0.031797 | 0.050216 | -0.019877 | -0.011804 | 0.0050524 | 0.13262 | 0.0064745 | -0.021844 | -0.058115 | -0.008409 | 0.061284 | -0.054588 | 0.13281 | -0.021847 | -65.7263 | -17.3667 | -65.4449 | 57.0547 | 57.173 | 57.0571 | -66.6119 | 66.2669 | -57.15 | 66.2669 | 66.2803 | 0.013438 | -57.2659 | -57.0785 | -0.32319 | -0.15658 | 0.56243 | 0.84385 | 1.167 | -0.038324 | -0.15417 | 66.35 | 66.2342 | 66.4216 | 66.2306 | -57.2332 | 123.3435 | 123.4617 | 123.3459 | 48.9221 | -123.8232
1026.2812 | 123.7427 | -66.1469 | 57.3166 | 0.047088 | -0.016277 | -0.022971 | -0.050177 | -0.037559 | -0.033933 | 0.080738 | -0.018809 | -0.012872 | 0.0050524 | 0.13476 | 0.0075435 | -0.017266 | -0.044379 | -0.008409 | 0.056706 | -0.054588 | 0.13281 | -0.021847 | -65.6531 | -17.4079 | -65.3213 | 57.1555 | 57.26 | 57.1396 | -66.5158 | 66.125 | -57.2599 | 66.1296 | 66.1384 | 0.013438 | -57.3712 | -57.1838 | -0.36894 | -0.16114 | 0.49378 | 0.82557 | 1.1945 | -0.056615 | -0.17704 | 66.2036 | 66.0923 | 66.2797 | 66.1025 | -57.3384 | 123.3023 | 123.4068 | 123.2864 | 48.739 | -123.8324
1027.2969 | 123.7564 | -65.9912 | 57.4356 | 0.047088 | -0.01414 | -0.021902 | -0.046972 | -0.03649 | -0.031797 | 0.034955 | -0.019877 | -0.012872 | 0.0061204 | 0.13369 | 0.0064745 | -0.012688 | -0.053537 | -0.008409 | 0.056706 | -0.063746 | 0.12823 | -0.017268 | -65.5844 | -16.0205 | -65.1244 | 57.2791 | 57.3836 | 57.2449 | -66.3967 | 65.9739 | -57.3789 | 65.9785 | 65.9828 | 0.008859 | -57.4994 | -57.3074 | -0.40553 | -0.15654 | 0.40682 | 0.86681 | 1.2723 | -0.052012 | -0.19075 | 66.0479 | 65.9275 | 66.1194 | 65.9377 | -57.4529 | 123.2703 | 123.3748 | 123.2361 | 49.9707 | -123.8323
1028.2812 | 123.7061 | -66.1148 | 57.3578 | 0.047088 | -0.015208 | -0.021902 | -0.049109 | -0.037559 | -0.031797 | 0.065477 | -0.019877 | -0.012872 | 0.0050524 | 0.13369 | 0.0054065 | -0.017266 | -0.058115 | -0.008409 | 0.042971 | -0.050009 | 0.12823 | -0.021847 | -65.5615 | -16.1625 | -65.161 | 57.247 | 57.3607 | 57.2357 | -66.4242 | 66.093 | -57.3148 | 66.0975 | 66.1064 | 0.013438 | -57.4078 | -57.2296 | -0.3094 | -0.11077 | 0.55331 | 0.95378 | 1.2632 | 0.002915 | -0.12208 | 66.1578 | 66.0648 | 66.243 | 66.0567 | -57.3796 | 123.3618 | 123.4755 | 123.3505 | 49.9523 | -123.782
1029.2812 | 123.7381 | -65.831 | 57.637 | 0.06235 | -0.015208 | -0.024039 | -0.050177 | -0.038627 | -0.02966 | 0.065477 | -0.020945 | -0.012872 | 0.0050524 | 0.13476 | 0.0064745 | -0.012688 | -0.058115 | -0.012988 | 0.061284 | -0.050009 | 0.13281 | -0.021847 | -65.4241 | -15.5352 | -64.9916 | 57.4027 | 57.5072 | 57.396 | -66.2777 | 65.8091 | -57.5757 | 65.8183 | 65.818 | 0.008859 | -57.687 | -57.5042 | -0.4467 | -0.23433 | 0.40686 | 0.83938 | 1.2861 | -0.12981 | -0.24107 | 65.8923 | 65.781 | 65.9638 | 65.7729 | -57.6589 | 123.2337 | 123.3382 | 123.2269 | 50.2958 | -123.9147
1030.2656 | 123.674 | -66.1514 | 57.3303 | 0.047088 | -0.017345 | -0.024039 | -0.049109 | -0.037559 | -0.033933 | 0.050216 | -0.019877 | -0.012872 | 0.0061204 | 0.13369 | 0.0064745 | -0.021844 | -0.058115 | -0.008409 | 0.052128 | -0.050009 | 0.11449 | -0.026426 | -65.4882 | -15.3658 | -65.0969 | 57.302 | 57.4248 | 57.2998 | -66.3601 | 66.125 | -57.2782 | 66.1296 | 66.143 | 0.018017 | -57.3803 | -57.2158 | -0.20868 | -0.02836 | 0.66319 | 1.0545 | 1.2632 | 0.094481 | -0.030518 | 66.2036 | 66.1014 | 66.2659 | 66.0933 | -57.3567 | 123.4534 | 123.5762 | 123.4512 | 50.7856 | -123.6904
1031.2812 | 123.7061 | -66.1423 | 57.3212 | 0.031826 | -0.016277 | -0.022971 | -0.050177 | -0.037559 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0071884 | 0.1369 | 0.0043385 | -0.017266 | -0.058115 | -0.008409 | 0.065863 | -0.059167 | 0.12365 | -0.017268 | -65.5752 | -15.4482 | -65.1473 | 57.2516 | 57.3653 | 57.2494 | -66.4196 | 66.125 | -57.2553 | 66.125 | 66.1339 | 0.008859 | -57.3803 | -57.1975 | -0.27736 | -0.069568 | 0.56704 | 0.99498 | 1.2723 | 0.044115 | -0.071728 | 66.2081 | 66.0831 | 66.2659 | 66.0842 | -57.3384 | 123.3939 | 123.5076 | 123.3917 | 50.6941 | -123.7408
1032.2812 | 123.7061 | -66.1148 | 57.3578 | 0.06235 | -0.016277 | -0.025108 | -0.049109 | -0.038627 | -0.032865 | 0.034955 | -0.019877 | -0.011804 | 0.0071884 | 0.13583 | 0.0075435 | -0.017266 | -0.048958 | -0.008409 | 0.038393 | -0.059167 | 0.14197 | -0.017268 | -65.7309 | -13.5572 | -65.216 | 57.1921 | 57.292 | 57.167 | -66.4883 | 66.0975 | -57.3194 | 66.0975 | 66.1064 | 0.008859 | -57.417 | -57.2158 | -0.37351 | -0.16571 | 0.3839 | 0.89884 | 1.2723 | -0.065764 | -0.19076 | 66.1532 | 66.0556 | 66.2568 | 66.0658 | -57.3751 | 123.3069 | 123.4068 | 123.2818 | 52.5576 | -123.8461
1033.2812 | 123.7335 | -65.8905 | 57.5317 | 0.047088 | -0.015208 | -0.022971 | -0.049109 | -0.03649 | -0.031797 | 0.065477 | -0.018809 | -0.011804 | 0.0050524 | 0.13476 | 0.0064745 | -0.021844 | -0.053537 | -0.008409 | 0.061284 | -0.054588 | 0.12823 | -0.012689 | -65.4241 | -13.5618 | -64.8726 | 57.4897 | 57.6034 | 57.4829 | -66.177 | 65.8778 | -57.4705 | 65.8687 | 65.8821 | 0.00428 | -57.5863 | -57.4035 | -0.28645 | -0.042057 | 0.46637 | 1.0179 | 1.3044 | 0.071631 | -0.04879 | 65.9518 | 65.8359 | 66.0187 | 65.837 | -57.5444 | 123.3802 | 123.4939 | 123.3735 | 52.3287 | -123.7087
1034.2812 | 123.6923 | -65.7349 | 57.7515 | 0.06235 | -0.017345 | -0.022971 | -0.050177 | -0.03649 | -0.032865 | 0.065477 | -0.019877 | -0.011804 | 0.0050524 | 0.13476 | 0.0043385 | -0.017266 | -0.062694 | -0.003831 | 0.061284 | -0.054588 | 0.14197 | -0.012689 | -65.328 | -13.0398 | -64.7444 | 57.6041 | 57.7133 | 57.5883 | -66.0716 | 65.7222 | -57.6902 | 65.7176 | 65.731 | 0.008858 | -57.8061 | -57.6095 | -0.33678 | -0.14732 | 0.40688 | 0.9905 | 1.3273 | -0.03821 | -0.16321 | 65.7961 | 65.6803 | 65.8768 | 65.6722 | -57.7642 | 123.339 | 123.4481 | 123.3231 | 52.6951 | -123.8231
1035.2812 | 123.7061 | -65.6525 | 57.8156 | 0.092874 | -0.015208 | -0.025108 | -0.049109 | -0.037559 | -0.032865 | 0.080738 | -0.018809 | -0.012872 | 0.0061204 | 0.13583 | 0.0043385 | -0.012688 | -0.053537 | -0.008409 | 0.047549 | -0.054588 | 0.11907 | -0.00811 | -65.1677 | -12.6369 | -64.575 | 57.7735 | 57.8827 | 57.7577 | -65.9022 | 65.6444 | -57.768 | 65.6398 | 65.6441 | -0.000299 | -57.8701 | -57.6965 | -0.24976 | -0.042005 | 0.48474 | 1.0775 | 1.3273 | 0.067112 | -0.057888 | 65.7 | 65.5979 | 65.7715 | 65.5989 | -57.8237 | 123.426 | 123.5351 | 123.4101 | 53.0156 | -123.7178
1036.2656 | 123.7701 | -65.8768 | 57.5729 | 0.06235 | -0.016277 | -0.026176 | -0.049109 | -0.037559 | -0.031797 | 0.065477 | -0.017741 | -0.012872 | 0.0050524 | 0.1369 | 0.0064745 | -0.012688 | -0.053537 | -0.003831 | 0.056706 | -0.059167 | 0.12823 | -0.017268 | -65.4287 | -13.2871 | -64.8955 | 57.5126 | 57.6263 | 57.4967 | -66.1586 | 65.8595 | -57.5162 | 65.8641 | 65.8729 | 0.013437 | -57.6321 | -57.4447 | -0.28187 | -0.060364 | 0.44805 | 0.98131 | 1.2632 | 0.053325 | -0.076253 | 65.9335 | 65.8176 | 66.005 | 65.8232 | -57.5902 | 123.3893 | 123.503 | 123.3735 | 52.5897 | -123.7316
1037.2812 | 123.7473 | -65.8401 | 57.637 | 0.031826 | -0.016277 | -0.021902 | -0.050177 | -0.038627 | -0.031797 | 0.065477 | -0.017741 | -0.012872 | 0.0061204 | 0.13476 | 0.0064745 | -0.076785 | -0.026065 | -0.063349 | 0.001765 | -0.059167 | 0.073287 | -0.053899 | -65.4012 | -15.494 | -64.8451 | 57.5263 | 57.6492 | 57.5196 | -66.1403 | 65.7862 | -57.6353 | 65.7634 | 65.7768 | -0.00945 | -57.6962 | -57.5637 | -0.30018 | -0.11071 | 0.4389 | 0.99505 | 1.2952 | 0.012131 | -0.11745 | 65.8419 | 65.781 | 65.9134 | 65.8141 | -57.6909 | 123.3665 | 123.4893 | 123.3597 | 50.3462 | -123.7773
1038.2656 | 123.6511 | -65.7028 | 57.7927 | 0.047088 | -0.018413 | -0.025108 | -0.050177 | -0.037559 | -0.030728 | 0.080738 | -0.019877 | -0.012872 | 0.0050524 | 0.13476 | 0.0054065 | -0.067628 | -0.016908 | -0.049614 | 0.010922 | -0.059167 | 0.077866 | -0.063057 | -65.1586 | -13.0123 | -64.5566 | 57.7598 | 57.8827 | 57.7668 | -65.8976 | 65.6398 | -57.7817 | 65.6352 | 65.6532 | 0.013443 | -57.8518 | -57.7148 | -0.19483 | -0.032852 | 0.54425 | 1.1462 | 1.341 | 0.09 | -0.025843 | 65.7137 | 65.6437 | 65.7807 | 65.6859 | -57.8557 | 123.4626 | 123.5855 | 123.4696 | 52.6905 | -123.6903
1039.2812 | 123.6832 | -65.6891 | 57.7835 | 0.047088 | -0.018413 | -0.024039 | -0.049109 | -0.037559 | -0.031797 | 0.065477 | -0.020945 | -0.011804 | 0.0050524 | 0.13369 | 0.0054065 | -0.081363 | -0.021486 | -0.05877 | 0.006344 | -0.059167 | 0.068708 | -0.049321 | -65.154 | -14.2623 | -64.5704 | 57.7873 | 57.901 | 57.7897 | -65.8839 | 65.6398 | -57.7772 | 65.6077 | 65.6303 | -0.009449 | -57.8427 | -57.7148 | -0.19482 | 0.003775 | 0.53509 | 1.1187 | 1.3135 | 0.11747 | 0.006206 | 65.6954 | 65.6299 | 65.7578 | 65.6676 | -57.8328 | 123.4764 | 123.5901 | 123.4788 | 51.4268 | -123.6674
1040.2812 | 123.7381 | -65.7028 | 57.7606 | 0.06235 | -0.017345 | -0.025108 | -0.048041 | -0.037559 | -0.031797 | 0.065477 | -0.019877 | -0.010735 | 0.0061204 | 0.1369 | 0.0064745 | -0.081363 | -0.030644 | -0.045036 | 0.010922 | -0.059167 | 0.068708 | -0.053899 | -65.2181 | -12.3026 | -64.6619 | 57.7049 | 57.8231 | 57.689 | -65.9618 | 65.6489 | -57.7497 | 65.6215 | 65.6578 | 0.008863 | -57.8198 | -57.6919 | -0.25893 | -0.05575 | 0.48472 | 1.0409 | 1.2998 | 0.062522 | -0.071635 | 65.7137 | 65.6437 | 65.7715 | 65.6722 | -57.8145 | 123.4077 | 123.526 | 123.3918 | 53.4002 | -123.7224
1041.2656 | 123.7015 | -65.831 | 57.6782 | 0.047088 | -0.017345 | -0.022971 | -0.049109 | -0.035422 | -0.031797 | 0.050216 | -0.018809 | -0.012872 | 0.0061204 | 0.13476 | 0.0054065 | -0.017266 | 0.019721 | -0.008409 | 0.052128 | -0.054588 | 0.11907 | -0.021847 | -65.2547 | -12.4217 | -64.6986 | 57.682 | 57.8048 | 57.6707 | -65.9801 | 65.8091 | -57.6261 | 65.8137 | 65.8226 | 0.013438 | -57.7328 | -57.5592 | -0.14907 | 0.003754 | 0.57627 | 1.1324 | 1.2815 | 0.1266 | -0.007552 | 65.8831 | 65.7764 | 65.9501 | 65.8507 | -57.7001 | 123.513 | 123.6358 | 123.5017 | 53.4093 | -123.6583
1042.2656 | 123.761 | -65.7349 | 57.7148 | 0.031826 | -0.018413 | -0.025108 | -0.048041 | -0.037559 | -0.031797 | 0.065477 | -0.018809 | -0.011804 | 0.0050524 | 0.13583 | 0.0054065 | -0.017266 | 0.0243 | -0.012988 | 0.033814 | -0.059167 | 0.13739 | -0.026426 | -65.3142 | -12.0325 | -64.7718 | 57.6179 | 57.7316 | 57.6066 | -66.0625 | 65.7084 | -57.681 | 65.7176 | 65.7219 | 0.013438 | -57.774 | -57.5775 | -0.32762 | -0.096965 | 0.42061 | 0.96303 | 1.2907 | 0.016726 | -0.10827 | 65.7687 | 65.6757 | 65.8723 | 65.7592 | -57.7413 | 123.3527 | 123.4664 | 123.3414 | 53.7024 | -123.7773
1043.2812 | 123.6511 | -65.9225 | 57.637 | 0.077612 | -0.018413 | -0.024039 | -0.049109 | -0.03649 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0050524 | 0.13583 | 0.0064745 | -0.017266 | 0.028878 | -0.003831 | 0.038393 | -0.059167 | 0.11907 | -0.031005 | -65.5661 | -11.5517 | -64.9916 | 57.3935 | 57.5118 | 57.3914 | -66.2823 | 65.8915 | -57.5986 | 65.9053 | 65.9187 | 0.027174 | -57.6962 | -57.518 | -0.35972 | -0.24349 | 0.35647 | 0.93093 | 1.2907 | -0.12523 | -0.24565 | 65.9609 | 65.8634 | 66.0416 | 65.9514 | -57.668 | 123.3161 | 123.4343 | 123.3139 | 54.3708 | -123.9193
1044.2656 | 123.6511 | -65.8539 | 57.6599 | 0.047088 | -0.018413 | -0.024039 | -0.049109 | -0.037559 | -0.032865 | 0.050216 | -0.020945 | -0.012872 | 0.0039834 | 0.13476 | 0.0064745 | -0.03558 | 0.010564 | -0.022144 | 0.033814 | -0.054588 | 0.11449 | -0.035584 | -65.3188 | -12.0233 | -64.8634 | 57.5629 | 57.672 | 57.5562 | -66.1037 | 65.8183 | -57.6261 | 65.8183 | 65.8317 | 0.01344 | -57.7145 | -57.5454 | -0.24981 | -0.096975 | 0.53505 | 0.99047 | 1.2403 | 0.012136 | -0.10371 | 65.8877 | 65.7993 | 65.9684 | 65.8644 | -57.6955 | 123.4168 | 123.5259 | 123.4101 | 53.8305 | -123.7636
1045.2656 | 123.6786 | -65.8813 | 57.6096 | 0.077612 | -0.018413 | -0.025108 | -0.049109 | -0.03649 | -0.032865 | 0.050216 | -0.019877 | -0.012872 | 0.0029154 | 0.13583 | 0.0054065 | -0.031001 | 0.010564 | -0.022144 | 0.029236 | -0.054588 | 0.11907 | -0.031005 | -65.3783 | -12.0462 | -64.9504 | 57.4805 | 57.5988 | 57.4738 | -66.1907 | 65.8503 | -57.5803 | 65.8503 | 65.8592 | 0.008861 | -57.6641 | -57.4905 | -0.30934 | -0.12903 | 0.503 | 0.93094 | 1.2403 | -0.010768 | -0.13577 | 65.9106 | 65.8268 | 66.0004 | 65.8919 | -57.6406 | 123.3619 | 123.4801 | 123.3551 | 53.8351 | -123.8003
1046.2812 | 123.7106 | -66.0141 | 57.4951 | 0.077612 | -0.017345 | -0.025108 | -0.051246 | -0.037559 | -0.032865 | 0.065477 | -0.020945 | -0.01394 | 0.0050524 | 0.1369 | 0.0054065 | -0.017266 | 0.0243 | -0.008409 | 0.052128 | -0.050009 | 0.12823 | -0.021847 | -65.3738 | -12.3805 | -64.9779 | 57.4714 | 57.5851 | 57.4555 | -66.209 | 65.9923 | -57.443 | 65.9968 | 66.0057 | 0.013438 | -57.5451 | -57.3669 | -0.19491 | -0.02375 | 0.64033 | 1.0362 | 1.2311 | 0.089938 | -0.039641 | 66.0662 | 65.9641 | 66.1423 | 66.0384 | -57.517 | 123.4855 | 123.5992 | 123.4696 | 53.6336 | -123.7041
1047.2812 | 123.7244 | -65.8722 | 57.605 | 0.06235 | -0.018413 | -0.022971 | -0.051246 | -0.037559 | -0.032865 | 0.065477 | -0.019877 | -0.01394 | 0.0050524 | 0.13583 | 0.0054065 | -0.017266 | 0.028878 | -0.008409 | 0.047549 | -0.054588 | 0.13739 | -0.026426 | -65.3142 | -13.5847 | -64.8955 | 57.5309 | 57.64 | 57.515 | -66.1541 | 65.8458 | -57.5574 | 65.8549 | 65.8638 | 0.018017 | -57.6596 | -57.4676 | -0.28187 | -0.074093 | 0.55794 | 0.97673 | 1.2586 | 0.035018 | -0.089982 | 65.9197 | 65.8176 | 66.0096 | 65.9011 | -57.6314 | 123.4031 | 123.5122 | 123.3872 | 52.2875 | -123.759
1048.2812 | 123.7381 | -65.9409 | 57.5134 | 0.047088 | -0.018413 | -0.022971 | -0.050177 | -0.038627 | -0.032865 | 0.065477 | -0.018809 | -0.011804 | 0.0061204 | 0.1369 | 0.0064745 | -0.017266 | 0.028878 | 0.000747 | 0.056706 | -0.054588 | 0.13739 | -0.012689 | -65.3188 | -11.9272 | -64.9596 | 57.4668 | 57.5805 | 57.4601 | -66.2136 | 65.9282 | -57.4567 | 65.9236 | 65.9416 | 0.013436 | -57.568 | -57.376 | -0.27273 | -0.04664 | 0.62203 | 0.98129 | 1.254 | 0.067048 | -0.053373 | 65.9976 | 65.8863 | 66.0782 | 65.9697 | -57.5261 | 123.4076 | 123.5213 | 123.4009 | 54.0137 | -123.727
1049.2812 | 123.7381 | -65.9409 | 57.55 | 0.047088 | -0.018413 | -0.024039 | -0.048041 | -0.038627 | -0.033933 | 0.065477 | -0.019877 | -0.012872 | 0.0050524 | 0.1369 | 0.0054065 | -0.017266 | 0.0243 | -0.012988 | 0.038393 | -0.04543 | 0.12823 | -0.031005 | -65.273 | -15.4116 | -64.9733 | 57.4622 | 57.5759 | 57.4509 | -66.2182 | 65.9099 | -57.5117 | 65.9236 | 65.9279 | 0.018017 | -57.5955 | -57.4218 | -0.27731 | -0.087839 | 0.66782 | 0.96756 | 1.2449 | 0.025848 | -0.099151 | 65.9792 | 65.8954 | 66.0691 | 65.9652 | -57.5811 | 123.4031 | 123.5168 | 123.3918 | 50.5293 | -123.7682
1050.2656 | 123.6603 | -65.8676 | 57.6462 | 0.047088 | -0.018413 | -0.024039 | -0.046972 | -0.037559 | -0.030728 | 0.065477 | -0.019877 | -0.01394 | 0.0039834 | 0.1369 | 0.0043385 | -0.012688 | 0.0243 | -0.003831 | 0.056706 | -0.050009 | 0.11907 | -0.012689 | -65.1677 | -15.7962 | -64.8817 | 57.5629 | 57.6812 | 57.5562 | -66.122 | 65.8549 | -57.5895 | 65.8549 | 65.8638 | 0.008858 | -57.6962 | -57.5271 | -0.2544 | -0.083242 | 0.69988 | 0.98589 | 1.2403 | 0.035026 | -0.089973 | 65.9243 | 65.8176 | 65.9867 | 65.8919 | -57.6589 | 123.4306 | 123.5488 | 123.4238 | 50.0714 | -123.7682
1051.2812 | 123.7564 | -65.918 | 57.5134 | 0.047088 | -0.019482 | -0.026176 | -0.050177 | -0.037559 | -0.032865 | 0.050216 | -0.019877 | -0.011804 | 0.0039834 | 0.13583 | 0.0054065 | -0.021844 | 0.0243 | -0.008409 | 0.052128 | -0.04543 | 0.13281 | -0.017268 | -65.2639 | -16.2907 | -65.0008 | 57.4439 | 57.5576 | 57.4234 | -66.2273 | 65.9007 | -57.4613 | 65.8961 | 65.9096 | 0.008859 | -57.5589 | -57.3806 | -0.30935 | -0.069532 | 0.65409 | 0.9172 | 1.2266 | 0.044155 | -0.090002 | 65.9701 | 65.8725 | 66.0508 | 65.9423 | -57.5307 | 123.3619 | 123.4756 | 123.3414 | 49.6273 | -123.7408
1052.2812 | 123.6969 | -65.8081 | 57.6736 | 0.06235 | -0.021618 | -0.022971 | -0.049109 | -0.034354 | -0.031797 | 0.065477 | -0.019877 | -0.012872 | 0.0039834 | 0.1369 | 0.0054065 | -0.017266 | 0.0243 | -0.003831 | 0.042971 | -0.050009 | 0.13281 | -0.012689 | -65.4196 | -12.4034 | -64.9916 | 57.4759 | 57.5988 | 57.4646 | -66.2044 | 65.7954 | -57.6307 | 65.7908 | 65.8043 | 0.008858 | -57.7237 | -57.5408 | -0.39632 | -0.1977 | 0.38855 | 0.81649 | 1.2128 | -0.074855 | -0.20901 | 65.8511 | 65.7581 | 65.9409 | 65.8324 | -57.6863 | 123.2841 | 123.4069 | 123.2727 | 53.4047 | -123.8781
1053.2656 | 123.642 | -65.8951 | 57.637 | 0.047088 | -0.021618 | -0.026176 | -0.051246 | -0.037559 | -0.033933 | 0.050216 | -0.019877 | -0.012872 | 0.0050524 | 0.13797 | 0.0043385 | -0.017266 | 0.033457 | -0.008409 | 0.052128 | -0.059167 | 0.12365 | -0.026426 | -65.328 | -14.5645 | -64.8771 | 57.5629 | 57.6766 | 57.5608 | -66.1083 | 65.8687 | -57.5849 | 65.8778 | 65.8867 | 0.018017 | -57.6962 | -57.5134 | -0.21319 | -0.074087 | 0.5671 | 1.0179 | 1.2311 | 0.039603 | -0.07624 | 65.9472 | 65.8359 | 66.0187 | 65.9285 | -57.6634 | 123.458 | 123.5717 | 123.4559 | 51.3306 | -123.7453
1054.2656 | 123.6328 | -65.918 | 57.6599 | 0.031826 | -0.021618 | -0.024039 | -0.048041 | -0.038627 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0039834 | 0.13583 | 0.0043385 | -0.017266 | 0.028878 | -0.003831 | 0.042971 | -0.063746 | 0.13739 | -0.021847 | -65.328 | -11.7028 | -64.9184 | 57.5675 | 57.6904 | 57.5654 | -66.1083 | 65.8961 | -57.6169 | 65.9007 | 65.9141 | 0.018016 | -57.7237 | -57.5225 | -0.1903 | -0.092397 | 0.58998 | 0.99961 | 1.1899 | 0.03045 | -0.094549 | 65.9609 | 65.8542 | 66.0554 | 65.9468 | -57.6818 | 123.4855 | 123.6083 | 123.4833 | 54.2151 | -123.7682
1055.2812 | 123.7198 | -65.6891 | 57.7927 | 0.047088 | -0.019482 | -0.025108 | -0.048041 | -0.038627 | -0.033933 | 0.080738 | -0.019877 | -0.012872 | 0.0039834 | 0.13797 | 0.0043385 | -0.012688 | 0.033457 | -0.012988 | 0.056706 | -0.050009 | 0.13739 | -0.012689 | -65.1815 | -11.5884 | -64.7764 | 57.6728 | 57.7957 | 57.6615 | -66.003 | 65.6764 | -57.736 | 65.6764 | 65.6761 | -0.000299 | -57.8427 | -57.6553 | -0.31387 | -0.11984 | 0.50762 | 0.91267 | 1.2265 | 0.003006 | -0.13115 | 65.7458 | 65.6391 | 65.8265 | 65.7225 | -57.8054 | 123.3619 | 123.4848 | 123.3506 | 54.1007 | -123.7956
1056.2656 | 123.642 | -65.7761 | 57.7469 | 0.047088 | -0.021618 | -0.022971 | -0.049109 | -0.037559 | -0.033933 | 0.065477 | -0.019877 | -0.01394 | 0.0039834 | 0.13797 | 0.0054065 | -0.017266 | 0.033457 | -0.003831 | 0.052128 | -0.04543 | 0.12823 | -0.021847 | -65.2456 | -12.2477 | -64.7764 | 57.6545 | 57.7819 | 57.6661 | -66.0259 | 65.7542 | -57.6948 | 65.7588 | 65.7722 | 0.018016 | -57.7923 | -57.6187 | -0.24979 | -0.09238 | 0.53049 | 0.99965 | 1.2494 | 0.035047 | -0.080795 | 65.8282 | 65.7306 | 65.9043 | 65.8095 | -57.7687 | 123.4306 | 123.558 | 123.4422 | 53.5284 | -123.7727
1057.2812 | 123.6832 | -65.8493 | 57.637 | 0.06235 | -0.02055 | -0.024039 | -0.050177 | -0.037559 | -0.032865 | 0.065477 | -0.020945 | -0.012872 | 0.0050524 | 0.13797 | 0.0054065 | -0.017266 | 0.028878 | -0.012988 | 0.052128 | -0.054588 | 0.13739 | -0.021847 | -65.2227 | -11.7166 | -64.8909 | 57.5721 | 57.6858 | 57.5699 | -66.1037 | 65.8275 | -57.5849 | 65.832 | 65.8363 | 0.008859 | -57.6916 | -57.4996 | -0.25439 | -0.06493 | 0.62663 | 0.95842 | 1.2128 | 0.04876 | -0.067082 | 65.9014 | 65.7947 | 65.9867 | 65.8782 | -57.6589 | 123.4214 | 123.5351 | 123.4192 | 54.1327 | -123.7407
1058.2812 | 123.8068 | -66.0324 | 57.4356 | 0.047088 | -0.02055 | -0.026176 | -0.049109 | -0.037559 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0039834 | 0.13797 | 0.0054065 | -0.017266 | 0.0243 | -0.003831 | 0.052128 | -0.054588 | 0.13281 | -0.021847 | -65.502 | -12.5224 | -65.1336 | 57.3661 | 57.4889 | 57.3639 | -66.3052 | 66.0106 | -57.3835 | 66.0151 | 66.0286 | 0.018016 | -57.4902 | -57.3028 | -0.27275 | -0.069547 | 0.53043 | 0.89886 | 1.1716 | 0.053296 | -0.071704 | 66.0845 | 65.9778 | 66.1652 | 66.0567 | -57.4575 | 123.3985 | 123.5213 | 123.3963 | 53.51 | -123.7408
1059.2812 | 123.6374 | -66.1331 | 57.4036 | 0.047088 | -0.018413 | -0.025108 | -0.050177 | -0.037559 | -0.032865 | 0.080738 | -0.018809 | -0.01394 | 0.0029154 | 0.13903 | 0.0054065 | -0.072207 | -0.016908 | -0.054192 | 0.020079 | -0.063746 | 0.082444 | -0.053899 | -65.5844 | -12.6186 | -65.2618 | 57.2836 | 57.4065 | 57.2815 | -66.3876 | 66.0792 | -57.3835 | 66.0609 | 66.0789 | -0.000293 | -57.4673 | -57.3211 | -0.25446 | -0.11992 | 0.54873 | 0.87136 | 1.1258 | 0.002925 | -0.12207 | 66.1532 | 66.0694 | 66.2156 | 66.1162 | -57.4575 | 123.4168 | 123.5396 | 123.4146 | 53.5146 | -123.7911
1060.2656 | 123.6511 | -65.9317 | 57.5958 | 0.047088 | -0.021618 | -0.024039 | -0.046972 | -0.039695 | -0.032865 | 0.095999 | -0.019877 | -0.01394 | 0.0029154 | 0.13797 | 0.0043385 | -0.076785 | -0.016908 | -0.049614 | 0.010922 | -0.063746 | 0.073287 | -0.058478 | -65.4974 | -14.4226 | -65.161 | 57.4027 | 57.5164 | 57.3914 | -66.264 | 65.8732 | -57.5849 | 65.8549 | 65.8821 | 0.008864 | -57.6596 | -57.5225 | -0.33225 | -0.19314 | 0.4343 | 0.77067 | 1.1029 | -0.079449 | -0.20445 | 65.9426 | 65.868 | 66.005 | 65.9148 | -57.6543 | 123.3344 | 123.4481 | 123.3231 | 51.5091 | -123.8598
1061.2812 | 123.7427 | -65.7806 | 57.692 | 0.06235 | -0.02055 | -0.021902 | -0.049109 | -0.037559 | -0.033933 | 0.034955 | -0.018809 | -0.015009 | 0.0039834 | 0.13797 | 0.0032705 | -0.076785 | -0.016908 | -0.054192 | 0.006344 | -0.063746 | 0.073287 | -0.049321 | -65.273 | -13.049 | -65.0511 | 57.5996 | 57.7133 | 57.5883 | -66.0808 | 65.7313 | -57.6856 | 65.7039 | 65.7264 | -0.004871 | -57.7557 | -57.6187 | -0.30016 | -0.092391 | 0.5076 | 0.7295 | 1.0297 | 0.021299 | -0.1037 | 65.787 | 65.7169 | 65.8539 | 65.7637 | -57.7413 | 123.3802 | 123.4939 | 123.3689 | 52.7317 | -123.7728
1062.2656 | 123.6603 | -65.8356 | 57.7194 | 0.047088 | -0.02055 | -0.024039 | -0.050177 | -0.03649 | -0.030728 | 0.050216 | -0.017741 | -0.01394 | 0.0050524 | 0.13903 | 0.0032705 | -0.072207 | -0.016908 | -0.054192 | 0.006344 | -0.063746 | 0.073287 | -0.067636 | -65.2639 | -13.0123 | -65.0054 | 57.6362 | 57.7499 | 57.6249 | -66.0396 | 65.7679 | -57.7131 | 65.7634 | 65.7814 | 0.013444 | -57.7832 | -57.6461 | -0.20402 | -0.083228 | 0.57169 | 0.83022 | 1.0342 | 0.030463 | -0.094536 | 65.8419 | 65.7718 | 65.9089 | 65.8187 | -57.7871 | 123.4718 | 123.5855 | 123.4605 | 52.8232 | -123.759
1063.2812 | 123.6969 | -65.5106 | 57.9712 | 0.047088 | -0.02055 | -0.024039 | -0.050177 | -0.03649 | -0.033933 | 0.065477 | -0.023082 | -0.012872 | 0.0039834 | 0.1401 | 0.0043385 | -0.072207 | -0.016908 | -0.049614 | 0.010922 | -0.054588 | 0.073287 | -0.058478 | -65.0533 | -13.1955 | -64.7535 | 57.856 | 57.9651 | 57.8492 | -65.8244 | 65.4521 | -57.9603 | 65.4384 | 65.4609 | 0.008864 | -58.0258 | -57.8979 | -0.31383 | -0.11523 | 0.4573 | 0.75704 | 1.0709 | -0.006112 | -0.12195 | 65.5215 | 65.456 | 65.5838 | 65.4937 | -58.0297 | 123.3665 | 123.4756 | 123.3598 | 52.3151 | -123.7956
1064.2812 | 123.7656 | -65.6479 | 57.7881 | 0.047088 | -0.02055 | -0.024039 | -0.049109 | -0.038627 | -0.032865 | 0.080738 | -0.019877 | -0.01394 | 0.0039834 | 0.1369 | 0.0054065 | -0.081363 | -0.016908 | -0.054192 | -0.002813 | -0.054588 | 0.073287 | -0.049321 | -65.0487 | -13.2458 | -64.7673 | 57.8331 | 57.9513 | 57.8218 | -65.8381 | 65.5986 | -57.7909 | 65.5665 | 65.5937 | -0.004871 | -57.8427 | -57.7148 | -0.19024 | 0.044982 | 0.5992 | 0.88063 | 1.0709 | 0.16326 | 0.033679 | 65.6451 | 65.5933 | 65.7212 | 65.631 | -57.8374 | 123.481 | 123.5992 | 123.4697 | 52.402 | -123.6262
1065.2656 | 123.6694 | -65.5289 | 57.9758 | 0.047088 | -0.02055 | -0.026176 | -0.050177 | -0.03649 | -0.032865 | 0.050216 | -0.019877 | -0.01394 | 0.0018474 | 0.1401 | 0.0043385 | -0.072207 | -0.021486 | -0.063349 | 0.010922 | -0.068325 | 0.073287 | -0.053899 | -65.0075 | -12.6323 | -64.7535 | 57.8422 | 57.9605 | 57.8401 | -65.8381 | 65.475 | -57.9648 | 65.4567 | 65.4655 | -0.00945 | -58.0441 | -57.9025 | -0.30925 | -0.13354 | 0.52139 | 0.77535 | 1.0846 | -0.015269 | -0.13569 | 65.5398 | 65.4605 | 65.6022 | 65.5074 | -58.0297 | 123.3711 | 123.4894 | 123.3689 | 52.8966 | -123.8139
1066.2656 | 123.6694 | -65.5975 | 57.9391 | 0.06235 | -0.022687 | -0.025108 | -0.050177 | -0.037559 | -0.032865 | 0.050216 | -0.020945 | -0.012872 | 0.0039834 | 0.1401 | 0.0054065 | -0.076785 | -0.016908 | -0.054192 | 0.015501 | -0.063746 | 0.068708 | -0.053899 | -65.0624 | -11.0755 | -64.7764 | 57.8193 | 57.933 | 57.8034 | -65.8656 | 65.5436 | -57.9236 | 65.5207 | 65.5433 | -0.000293 | -58.0029 | -57.8704 | -0.26806 | -0.11982 | 0.53511 | 0.82112 | 1.0892 | -0.00612 | -0.1357 | 65.613 | 65.5338 | 65.6662 | 65.5806 | -57.993 | 123.4169 | 123.5306 | 123.401 | 54.522 | -123.8047
1067.2812 | 123.7564 | -65.5792 | 57.9025 | 0.06235 | -0.02055 | -0.024039 | -0.051246 | -0.037559 | -0.033933 | 0.065477 | -0.018809 | -0.01394 | 0.0050524 | 0.1401 | 0.0043385 | -0.072207 | -0.026065 | -0.05877 | 0.010922 | -0.054588 | 0.073287 | -0.053899 | -65.1357 | -10.7413 | -64.8268 | 57.7827 | 57.8964 | 57.776 | -65.8976 | 65.5253 | -57.8916 | 65.507 | 65.5205 | -0.004871 | -57.9571 | -57.8292 | -0.31842 | -0.11982 | 0.44355 | 0.75244 | 1.0709 | -0.006127 | -0.12655 | 65.5901 | 65.5246 | 65.6525 | 65.5532 | -57.9564 | 123.3619 | 123.4756 | 123.3552 | 54.8379 | -123.8002
1068.2812 | 123.6008 | -65.7532 | 57.7881 | 0.06235 | -0.021618 | -0.025108 | -0.050177 | -0.03649 | -0.031797 | 0.065477 | -0.020945 | -0.012872 | 0.0039834 | 0.13797 | 0.0043385 | -0.072207 | -0.016908 | -0.054192 | 0.001765 | -0.059167 | 0.06413 | -0.049321 | -65.3188 | -9.5691 | -65.0328 | 57.6682 | 57.7957 | 57.6661 | -66.003 | 65.7039 | -57.7863 | 65.681 | 65.699 | -0.004871 | -57.8473 | -57.724 | -0.24979 | -0.11984 | 0.43435 | 0.72035 | 0.97014 | 0.007584 | -0.12199 | 65.7549 | 65.694 | 65.8173 | 65.7363 | -57.8374 | 123.4214 | 123.5488 | 123.4193 | 56.184 | -123.791
1069.2656 | 123.6145 | -65.7211 | 57.8247 | 0.047088 | -0.022687 | -0.024039 | -0.050177 | -0.038627 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0039834 | 0.1401 | 0.0043385 | -0.076785 | -0.021486 | -0.049614 | 0.015501 | -0.063746 | 0.082444 | -0.053899 | -65.2318 | -9.7889 | -64.9504 | 57.7278 | 57.8552 | 57.7256 | -65.948 | 65.6672 | -57.8092 | 65.6443 | 65.6715 | 0.004285 | -57.8885 | -57.7423 | -0.22688 | -0.096945 | 0.4893 | 0.77072 | 0.99761 | 0.030485 | -0.099093 | 65.7366 | 65.6574 | 65.8036 | 65.6996 | -57.8786 | 123.4489 | 123.5763 | 123.4467 | 55.9322 | -123.7727
1070.2812 | 123.6008 | -65.506 | 58.049 | 0.047088 | -0.021618 | -0.025108 | -0.052314 | -0.038627 | -0.032865 | 0.034955 | -0.020945 | -0.012872 | 0.0039834 | 0.1401 | 0.0054065 | -0.072207 | -0.016908 | -0.054192 | 0.010922 | -0.054588 | 0.073287 | -0.053899 | -65.0121 | -9.3036 | -64.7535 | 57.9384 | 58.0567 | 57.9317 | -65.7465 | 65.4521 | -58.0381 | 65.4338 | 65.4518 | -0.000293 | -58.1036 | -57.9757 | -0.24057 | -0.11064 | 0.49393 | 0.75246 | 0.99303 | 0.00764 | -0.11736 | 65.5169 | 65.4514 | 65.5793 | 65.4891 | -58.1029 | 123.4444 | 123.5626 | 123.4376 | 56.2024 | -123.7956
1071.2812 | 123.6191 | -65.5472 | 58.0307 | 0.06235 | -0.021618 | -0.025108 | -0.052314 | -0.038627 | -0.032865 | 0.050216 | -0.019877 | -0.012872 | 0.0039834 | 0.13903 | 0.0032705 | -0.072207 | -0.016908 | -0.054192 | 0.001765 | -0.063746 | 0.073287 | -0.053899 | -65.0945 | -8.777 | -64.8222 | 57.8789 | 57.9971 | 57.863 | -65.8107 | 65.4933 | -58.0289 | 65.475 | 65.493 | -0.000293 | -58.0944 | -57.9574 | -0.26347 | -0.15185 | 0.45271 | 0.72498 | 0.98845 | -0.033572 | -0.16773 | 65.5489 | 65.4834 | 65.6205 | 65.5303 | -58.0846 | 123.426 | 123.5443 | 123.4102 | 56.7702 | -123.8414
1072.2812 | 123.6557 | -65.3229 | 58.168 | 0.016564 | -0.022687 | -0.026176 | -0.049109 | -0.038627 | -0.031797 | 0.065477 | -0.018809 | -0.011804 | 0.0029154 | 0.1401 | 0.0032705 | -0.081363 | -0.012329 | -0.054192 | 0.010922 | -0.068325 | 0.077866 | -0.049321 | -64.9067 | -8.6763 | -64.6482 | 58.0483 | 58.1711 | 58.0324 | -65.6412 | 65.2736 | -58.1571 | 65.2415 | 65.2687 | -0.004871 | -58.2364 | -58.0902 | -0.31836 | -0.11977 | 0.41613 | 0.67466 | 0.99302 | 0.003086 | -0.13565 | 65.3338 | 65.2546 | 65.4007 | 65.3105 | -58.2174 | 123.3711 | 123.494 | 123.3553 | 56.6466 | -123.8093
1073.2812 | 123.674 | -65.4465 | 58.0811 | 0.06235 | -0.021618 | -0.025108 | -0.050177 | -0.03649 | -0.030728 | 0.034955 | -0.018809 | -0.01394 | 0.0039834 | 0.14117 | 0.0054065 | -0.072207 | -0.016908 | -0.049614 | 0.020079 | -0.063746 | 0.077866 | -0.053899 | -64.98 | -8.5527 | -64.7673 | 57.9704 | 58.0887 | 57.9637 | -65.7099 | 65.3926 | -58.061 | 65.3743 | 65.3969 | 0.004285 | -58.1448 | -58.0032 | -0.26345 | -0.11063 | 0.46647 | 0.67921 | 0.94266 | 0.007646 | -0.11735 | 65.4666 | 65.3827 | 65.5243 | 65.4296 | -58.135 | 123.4169 | 123.5352 | 123.4102 | 56.8938 | -123.791
1074.2656 | 123.6832 | -65.7761 | 57.7469 | 0.047088 | -0.02055 | -0.026176 | -0.049109 | -0.038627 | -0.032865 | 0.050216 | -0.018809 | -0.010735 | 0.0039834 | 0.14117 | 0.0043385 | -0.076785 | -0.026065 | -0.054192 | 0.006344 | -0.059167 | 0.073287 | -0.058478 | -65.2501 | -8.864 | -65.1244 | 57.6728 | 57.7957 | 57.6661 | -66.0121 | 65.7176 | -57.7405 | 65.6993 | 65.7219 | 0.004286 | -57.8061 | -57.6736 | -0.23606 | -0.074067 | 0.52591 | 0.65166 | 0.88772 | 0.048783 | -0.080795 | 65.7824 | 65.7169 | 65.8493 | 65.75 | -57.8054 | 123.4489 | 123.5717 | 123.4422 | 56.912 | -123.759
1075.2812 | 123.6145 | -65.5975 | 57.9575 | 0.047088 | -0.021618 | -0.025108 | -0.049109 | -0.03649 | -0.032865 | 0.050216 | -0.019877 | -0.012872 | 0.0039834 | 0.14117 | 0.0054065 | -0.081363 | -0.012329 | -0.049614 | 0.015501 | -0.059167 | 0.068708 | -0.053899 | -65.099 | -8.9419 | -64.8451 | 57.856 | 57.9788 | 57.8447 | -65.829 | 65.5436 | -57.942 | 65.5162 | 65.5479 | 0.004285 | -58.0166 | -57.8888 | -0.23143 | -0.1015 | 0.49849 | 0.75244 | 0.98387 | 0.021356 | -0.1128 | 65.613 | 65.5384 | 65.6662 | 65.5852 | -58.0114 | 123.4535 | 123.5763 | 123.4422 | 56.6557 | -123.7864
1076.2812 | 123.6603 | -65.4236 | 58.0902 | 0.06235 | -0.021618 | -0.026176 | -0.051246 | -0.037559 | -0.031797 | 0.065477 | -0.019877 | -0.01394 | 0.0018474 | 0.13903 | 0.0032705 | -0.072207 | -0.021486 | -0.049614 | 0.015501 | -0.059167 | 0.077866 | -0.049321 | -64.9937 | -9.0975 | -64.7123 | 57.9704 | 58.0887 | 57.9683 | -65.7099 | 65.3743 | -58.0747 | 65.3514 | 65.374 | -0.000293 | -58.1494 | -58.0123 | -0.28633 | -0.11979 | 0.42985 | 0.71127 | 0.9976 | -0.001509 | -0.12193 | 65.4391 | 65.3644 | 65.5015 | 65.4021 | -58.1395 | 123.394 | 123.5123 | 123.3919 | 56.326 | -123.8001
1077.2656 | 123.6465 | -65.4144 | 58.1268 | 0.031826 | -0.023755 | -0.026176 | -0.051246 | -0.038627 | -0.033933 | 0.050216 | -0.018809 | -0.01394 | 0.0018474 | 0.14117 | 0.0043385 | -0.076785 | -0.021486 | -0.054192 | 0.010922 | -0.059167 | 0.077866 | -0.058478 | -64.9754 | -9.0151 | -64.6894 | 57.9887 | 58.107 | 57.982 | -65.7008 | 65.356 | -58.1159 | 65.3376 | 65.3602 | 0.004286 | -58.186 | -58.049 | -0.28633 | -0.13809 | 0.439 | 0.72501 | 1.0113 | -0.019816 | -0.14482 | 65.4254 | 65.3553 | 65.4923 | 65.3929 | -58.1853 | 123.4032 | 123.5214 | 123.3964 | 56.3993 | -123.8276
1078.2812 | 123.6511 | -65.3137 | 58.2184 | 0.047088 | -0.022687 | -0.026176 | -0.051246 | -0.038627 | -0.032865 | 0.065477 | -0.018809 | -0.015009 | 0.0029154 | 0.14117 | 0.0022015 | -0.076785 | -0.021486 | -0.05877 | 0.015501 | -0.054588 | 0.077866 | -0.058478 | -64.8976 | -9.212 | -64.5154 | 58.0895 | 58.2032 | 58.0827 | -65.5909 | 65.2552 | -58.2029 | 65.2369 | 65.255 | -0.000292 | -58.273 | -58.1405 | -0.27715 | -0.12892 | 0.41613 | 0.79829 | 1.0754 | -0.015218 | -0.13564 | 65.3292 | 65.2591 | 65.3916 | 65.2922 | -58.2769 | 123.4032 | 123.5169 | 123.3965 | 56.1017 | -123.8093
1079.2812 | 123.6328 | -65.1443 | 58.374 | 0.047088 | -0.021618 | -0.026176 | -0.050177 | -0.038627 | -0.032865 | 0.050216 | -0.020945 | -0.012872 | 0.0029154 | 0.14331 | 0.0032705 | -0.072207 | -0.021486 | -0.054192 | 0.010922 | -0.059167 | 0.077866 | -0.058478 | -64.7511 | -9.3539 | -64.3643 | 58.2314 | 58.3543 | 58.2247 | -65.4443 | 65.0859 | -58.3631 | 65.0721 | 65.0902 | 0.004286 | -58.4332 | -58.2962 | -0.3 | -0.14263 | 0.39328 | 0.78002 | 1.08 | -0.019763 | -0.14934 | 65.1553 | 65.0852 | 65.2222 | 65.1229 | -58.4325 | 123.3757 | 123.4986 | 123.369 | 55.7904 | -123.8184
1080.2812 | 123.6282 | -65.2084 | 58.3603 | 0.031826 | -0.02055 | -0.025108 | -0.050177 | -0.03649 | -0.030728 | 0.050216 | -0.019877 | -0.01394 | 0.0039834 | 0.1401 | 0.0032705 | -0.076785 | -0.016908 | -0.054192 | 0.001765 | -0.059167 | 0.077866 | -0.053899 | -64.7236 | -9.8439 | -64.346 | 58.2543 | 58.3726 | 58.243 | -65.426 | 65.1545 | -58.3585 | 65.1316 | 65.1542 | -0.000293 | -58.4195 | -58.2824 | -0.2176 | -0.106 | 0.48484 | 0.86242 | 1.08 | 0.012283 | -0.11729 | 65.2102 | 65.1493 | 65.2863 | 65.1915 | -58.4142 | 123.4627 | 123.581 | 123.4514 | 55.3646 | -123.7863
1081.2812 | 123.6877 | -65.0436 | 58.4793 | 0.047088 | -0.021618 | -0.026176 | -0.050177 | -0.03649 | -0.032865 | 0.065477 | -0.019877 | -0.01394 | 0.0039834 | 0.13903 | 0.0022015 | -0.081363 | -0.016908 | -0.05877 | 0.015501 | -0.054588 | 0.087023 | -0.053899 | -64.6274 | -9.5188 | -64.2544 | 58.355 | 58.4733 | 58.3575 | -65.3207 | 64.9897 | -58.4638 | 64.9623 | 64.9849 | -0.004871 | -58.5339 | -58.3923 | -0.27708 | -0.12429 | 0.4162 | 0.7892 | 1.0663 | -0.006006 | -0.12185 | 65.0591 | 64.9891 | 65.1307 | 65.0267 | -58.5332 | 123.3987 | 123.5169 | 123.4011 | 55.5249 | -123.8
1082.2656 | 123.6786 | -65.1901 | 58.3145 | 0.047088 | -0.022687 | -0.027244 | -0.053383 | -0.038627 | -0.032865 | 0.065477 | -0.022013 | -0.015009 | 0.0029154 | 0.1401 | 0.0022015 | -0.012688 | 0.019721 | 0.000747 | 0.056706 | -0.059167 | 0.13281 | -0.021847 | -64.7785 | -9.9858 | -64.4101 | 58.2085 | 58.3268 | 58.2018 | -65.481 | 65.1683 | -58.2578 | 65.1774 | 65.1909 | 0.022594 | -58.3737 | -58.1817 | -0.29085 | -0.10601 | 0.41159 | 0.78001 | 1.0709 | 0.012274 | -0.11273 | 65.2468 | 65.131 | 65.3229 | 65.2098 | -58.3364 | 123.3986 | 123.5169 | 123.3919 | 55.2043 | -123.7955
1083.2812 | 123.7656 | -65.1901 | 58.2825 | 0.047088 | -0.022687 | -0.027244 | -0.051246 | -0.037559 | -0.031797 | 0.050216 | -0.019877 | -0.015009 | 0.0018474 | 0.14117 | 0.0032705 | -0.012688 | 0.0243 | 0.000747 | 0.052128 | -0.054588 | 0.14197 | -0.012689 | -64.7602 | -9.8668 | -64.4147 | 58.236 | 58.3405 | 58.2201 | -65.4581 | 65.1774 | -58.2303 | 65.1774 | 65.1909 | 0.013436 | -58.3371 | -58.1405 | -0.26796 | -0.046496 | 0.4299 | 0.77543 | 1.0434 | 0.058053 | -0.062368 | 65.2423 | 65.1355 | 65.3321 | 65.2144 | -58.2952 | 123.4261 | 123.5306 | 123.4102 | 55.3234 | -123.7406
1084.2656 | 123.6832 | -65.1581 | 58.3694 | 0.092874 | -0.021618 | -0.026176 | -0.050177 | -0.037559 | -0.031797 | 0.050216 | -0.018809 | -0.01394 | 0.0029154 | 0.14117 | 0.0032705 | -0.021844 | 0.028878 | -0.003831 | 0.056706 | -0.050009 | 0.14197 | -0.021847 | -64.774 | -10.3338 | -64.4239 | 58.2222 | 58.3405 | 58.2201 | -65.4581 | 65.1362 | -58.3127 | 65.1362 | 65.1542 | 0.018016 | -58.4195 | -58.2275 | -0.3 | -0.14721 | 0.38412 | 0.73423 | 1.0342 | -0.028922 | -0.14934 | 65.2148 | 65.1081 | 65.3 | 65.187 | -58.3913 | 123.3803 | 123.4986 | 123.3782 | 54.8243 | -123.8275
1085.2812 | 123.7701 | -65.0711 | 58.3786 | 0.047088 | -0.023755 | -0.025108 | -0.051246 | -0.037559 | -0.030728 | 0.080738 | -0.018809 | -0.01394 | 0.0029154 | 0.14224 | 0.0032705 | -0.076785 | -0.012329 | -0.049614 | 0.015501 | -0.063746 | 0.077866 | -0.049321 | -64.7144 | -10.4849 | -64.3323 | 58.3047 | 58.4138 | 58.2888 | -65.3848 | 65.0218 | -58.3631 | 64.9943 | 65.0215 | -0.000293 | -58.4423 | -58.3007 | -0.31372 | -0.073948 | 0.35667 | 0.73883 | 1.0525 | 0.035181 | -0.089819 | 65.0866 | 65.0074 | 65.149 | 65.0588 | -58.4279 | 123.3758 | 123.4849 | 123.3599 | 54.5862 | -123.7634
1086.2656 | 123.6374 | -65.3687 | 58.1909 | 0.06235 | -0.024824 | -0.026176 | -0.051246 | -0.038627 | -0.031797 | 0.080738 | -0.018809 | -0.015009 | 0.0039834 | 0.14117 | 0.0032705 | -0.072207 | -0.012329 | -0.049614 | 0.010922 | -0.054588 | 0.087023 | -0.058478 | -64.9892 | -9.212 | -64.694 | 58.0483 | 58.1528 | 58.0415 | -65.6367 | 65.3102 | -58.18 | 65.2964 | 65.319 | 0.008864 | -58.2455 | -58.1039 | -0.268 | -0.14266 | 0.37949 | 0.67465 | 0.94266 | -0.038117 | -0.14938 | 65.3796 | 65.3141 | 65.4557 | 65.3563 | -58.2494 | 123.4169 | 123.5215 | 123.4102 | 56.1566 | -123.8276
1087.2812 | 123.6786 | -65.1215 | 58.4061 | 0.06235 | -0.022687 | -0.026176 | -0.051246 | -0.037559 | -0.033933 | 0.065477 | -0.018809 | -0.012872 | 0.0029154 | 0.14117 | 0.0022015 | -0.076785 | -0.012329 | -0.054192 | 0.015501 | -0.054588 | 0.073287 | -0.049321 | -64.7831 | -9.4547 | -64.401 | 58.2497 | 58.3634 | 58.243 | -65.4352 | 65.0721 | -58.3906 | 65.0447 | 65.0673 | -0.004871 | -58.4607 | -58.3328 | -0.31373 | -0.15636 | 0.33834 | 0.7205 | 1.0342 | -0.04265 | -0.16307 | 65.137 | 65.0669 | 65.1947 | 65.1091 | -58.4554 | 123.3712 | 123.4849 | 123.3645 | 55.6668 | -123.8413
1088.2812 | 123.6511 | -65.1901 | 58.3099 | 0.047088 | -0.023755 | -0.026176 | -0.051246 | -0.037559 | -0.032865 | 0.065477 | -0.020945 | -0.012872 | 0.0018474 | 0.14224 | 0.0022015 | -0.067628 | -0.016908 | -0.054192 | 0.015501 | -0.063746 | 0.077866 | -0.053899 | -64.8381 | -9.3082 | -64.4605 | 58.1993 | 58.3131 | 58.1972 | -65.4856 | 65.1362 | -58.2944 | 65.1225 | 65.1359 | -0.000293 | -58.3737 | -58.2321 | -0.29543 | -0.11059 | 0.35206 | 0.72964 | 1.0251 | 0.003115 | -0.11273 | 65.2056 | 65.1264 | 65.268 | 65.1732 | -58.3638 | 123.3895 | 123.5032 | 123.3873 | 55.882 | -123.7955
1089.2656 | 123.6374 | -65.0711 | 58.4839 | 0.06235 | -0.024824 | -0.026176 | -0.051246 | -0.038627 | -0.035002 | 0.050216 | -0.020945 | -0.015009 | 0.0039834 | 0.14224 | 0.0022015 | -0.076785 | -0.016908 | -0.05877 | 0.020079 | -0.059167 | 0.073287 | -0.058478 | -64.7144 | -9.3448 | -64.3185 | 58.3275 | 58.4367 | 58.3163 | -65.3665 | 65.0126 | -58.4638 | 64.9943 | 65.0123 | -0.000292 | -58.5431 | -58.4106 | -0.2954 | -0.15634 | 0.35667 | 0.75256 | 1.048 | -0.047212 | -0.16763 | 65.0912 | 65.0119 | 65.1444 | 65.0542 | -58.5424 | 123.3987 | 123.5078 | 123.3874 | 55.7263 | -123.8504
1090.2812 | 123.6694 | -65.1031 | 58.429 | 0.047088 | -0.025892 | -0.026176 | -0.051246 | -0.039695 | -0.035002 | 0.065477 | -0.019877 | -0.01394 | 0.0018474 | 0.14224 | 0.0022015 | -0.076785 | -0.016908 | -0.049614 | 0.015501 | -0.054588 | 0.091601 | -0.053899 | -64.6961 | -9.1021 | -64.3002 | 58.355 | 58.4641 | 58.3437 | -65.339 | 65.0493 | -58.4135 | 65.0264 | 65.0535 | 0.004285 | -58.4835 | -58.3374 | -0.23588 | -0.073939 | 0.40703 | 0.80292 | 1.0388 | 0.035191 | -0.08523 | 65.1187 | 65.0486 | 65.1947 | 65.0862 | -58.4829 | 123.4582 | 123.5673 | 123.4469 | 56.001 | -123.768
1091.2812 | 123.6465 | -65.0711 | 58.5159 | 0.06235 | -0.024824 | -0.025108 | -0.050177 | -0.037559 | -0.035002 | 0.050216 | -0.018809 | -0.015009 | 0.0029154 | 0.14224 | 0.0022015 | -0.072207 | -0.021486 | -0.049614 | 0.015501 | -0.054588 | 0.082444 | -0.049321 | -64.6229 | -12.0004 | -64.1812 | 58.442 | 58.5649 | 58.4399 | -65.2383 | 65.0218 | -58.5004 | 64.9989 | 65.0215 | -0.000293 | -58.5705 | -58.4335 | -0.16719 | -0.073922 | 0.44824 | 0.88992 | 1.0571 | 0.048946 | -0.076054 | 65.0866 | 65.0165 | 65.1535 | 65.0496 | -58.5653 | 123.5131 | 123.636 | 123.511 | 53.0707 | -123.7542
1092.2812 | 123.7198 | -64.9704 | 58.5434 | 0.06235 | -0.024824 | -0.026176 | -0.051246 | -0.038627 | -0.035002 | 0.050216 | -0.022013 | -0.015009 | 0.0018474 | 0.14331 | 0.0043385 | -0.076785 | -0.021486 | -0.054192 | 0.015501 | -0.059167 | 0.077866 | -0.053899 | -64.6137 | -12.1103 | -64.172 | 58.4466 | 58.574 | 58.4445 | -65.2383 | 64.9165 | -58.5279 | 64.8936 | 64.9162 | -0.000293 | -58.6026 | -58.4655 | -0.2679 | -0.09681 | 0.35669 | 0.79837 | 1.0663 | 0.030637 | -0.098941 | 64.9859 | 64.9112 | 65.0483 | 64.9489 | -58.5973 | 123.417 | 123.5444 | 123.4149 | 52.8601 | -123.7817
1093.2812 | 123.6099 | -65.1077 | 58.4427 | 0.047088 | -0.023755 | -0.024039 | -0.053383 | -0.038627 | -0.033933 | 0.050216 | -0.022013 | -0.015009 | 0.0039834 | 0.14224 | 0.0011335 | -0.072207 | -0.016908 | -0.049614 | 0.010922 | -0.059167 | 0.087023 | -0.058478 | -64.7144 | -11.6937 | -64.3231 | 58.3459 | 58.4596 | 58.3391 | -65.3482 | 65.0492 | -58.4318 | 65.0355 | 65.0581 | 0.008864 | -58.5019 | -58.3557 | -0.24046 | -0.096829 | 0.39329 | 0.7846 | 1.0251 | 0.01688 | -0.10354 | 65.1186 | 65.0486 | 65.1947 | 65.0908 | -58.5012 | 123.4536 | 123.5673 | 123.4469 | 53.4141 | -123.7909
1094.2656 | 123.6374 | -65.1627 | 58.4198 | 0.077612 | -0.023755 | -0.026176 | -0.051246 | -0.037559 | -0.033933 | 0.080738 | -0.022013 | -0.011804 | 0.0039834 | 0.14224 | 0.0022015 | -0.067628 | -0.012329 | -0.05877 | 0.015501 | -0.063746 | 0.091601 | -0.053899 | -64.7877 | -12.6689 | -64.4147 | 58.2909 | 58.4046 | 58.2888 | -65.3986 | 65.1088 | -58.4043 | 65.095 | 65.1039 | -0.004871 | -58.4835 | -58.3282 | -0.2359 | -0.12888 | 0.37496 | 0.74796 | 0.98386 | -0.015176 | -0.13102 | 65.1782 | 65.0989 | 65.2543 | 65.1503 | -58.4737 | 123.4536 | 123.5673 | 123.4514 | 52.4937 | -123.8184
1095.2812 | 123.7793 | -65.1535 | 58.2916 | 0.077612 | -0.023755 | -0.026176 | -0.052314 | -0.03649 | -0.035002 | 0.050216 | -0.019877 | -0.015009 | 0.0029154 | 0.14224 | 0.0022015 | -0.076785 | -0.016908 | -0.054192 | 0.015501 | -0.059167 | 0.073287 | -0.049321 | -64.8335 | -12.3164 | -64.4742 | 58.2314 | 58.3497 | 58.2201 | -65.4581 | 65.1042 | -58.2761 | 65.0767 | 65.0993 | -0.004871 | -58.3508 | -58.2183 | -0.30458 | -0.060229 | 0.32002 | 0.67928 | 0.98386 | 0.058055 | -0.071523 | 65.169 | 65.0943 | 65.2268 | 65.1366 | -58.3409 | 123.3849 | 123.5032 | 123.3736 | 52.8371 | -123.7497
1096.2656 | 123.6465 | -65.2451 | 58.2916 | 0.031826 | -0.025892 | -0.024039 | -0.049109 | -0.039695 | -0.032865 | 0.065477 | -0.019877 | -0.01394 | 0.0050524 | 0.14331 | 0.0043385 | -0.076785 | -0.007751 | -0.054192 | 0.010922 | -0.059167 | 0.073287 | -0.053899 | -64.9571 | -12.3438 | -64.6482 | 58.1124 | 58.2306 | 58.0919 | -65.5909 | 65.1912 | -58.2807 | 65.1683 | 65.1909 | -0.000293 | -58.3508 | -58.2183 | -0.34581 | -0.17927 | 0.28795 | 0.59685 | 0.94266 | -0.060988 | -0.19972 | 65.256 | 65.1859 | 65.3183 | 65.2373 | -58.3455 | 123.3574 | 123.4757 | 123.337 | 52.9012 | -123.8825
1097.2812 | 123.7747 | -65.2908 | 58.1589 | 0.031826 | -0.024824 | -0.027244 | -0.050177 | -0.037559 | -0.033933 | 0.065477 | -0.018809 | -0.015009 | 0.0029154 | 0.14224 | 0.0032705 | -0.076785 | -0.021486 | -0.049614 | 0.024657 | -0.068325 | 0.077866 | -0.053899 | -64.9342 | -12.3484 | -64.6162 | 58.1261 | 58.2444 | 58.1194 | -65.5588 | 65.2369 | -58.1342 | 65.214 | 65.2412 | 0.004285 | -58.2272 | -58.081 | -0.26798 | -0.032783 | 0.35662 | 0.67467 | 0.94266 | 0.085498 | -0.039501 | 65.3155 | 65.2225 | 65.3687 | 65.2693 | -58.2128 | 123.4169 | 123.5352 | 123.4102 | 52.9424 | -123.7177
1098.2812 | 123.6465 | -65.1627 | 58.4198 | 0.047088 | -0.02696 | -0.027244 | -0.051246 | -0.039695 | -0.033933 | 0.095999 | -0.020945 | -0.015009 | 0.0029154 | 0.14117 | 0.0032705 | -0.067628 | -0.007751 | -0.054192 | 0.010922 | -0.059167 | 0.091601 | -0.049321 | -64.7877 | -12.2889 | -64.4239 | 58.268 | 58.3909 | 58.2705 | -65.4123 | 65.1133 | -58.4089 | 65.095 | 65.1085 | -0.004871 | -58.479 | -58.3282 | -0.24963 | -0.15178 | 0.37496 | 0.7388 | 0.98844 | -0.028911 | -0.14933 | 65.1736 | 65.1035 | 65.2543 | 65.1549 | -58.4691 | 123.4307 | 123.5535 | 123.4331 | 52.8738 | -123.8321
1099.2812 | 123.6786 | -65.1993 | 58.3649 | 0.047088 | -0.02696 | -0.026176 | -0.052314 | -0.037559 | -0.033933 | 0.050216 | -0.020945 | -0.017145 | 0.0029154 | 0.14331 | 0.0032705 | -0.076785 | -0.012329 | -0.040457 | 0.010922 | -0.059167 | 0.082444 | -0.058478 | -64.8106 | -12.7468 | -64.4376 | 58.2451 | 58.368 | 58.2476 | -65.4443 | 65.1408 | -58.3539 | 65.1225 | 65.1588 | 0.018021 | -58.424 | -58.2824 | -0.24507 | -0.11974 | 0.38869 | 0.76169 | 1.0068 | 0.003128 | -0.11729 | 65.2102 | 65.1401 | 65.2817 | 65.187 | -58.4233 | 123.4444 | 123.5673 | 123.4469 | 52.4525 | -123.8092
1100.2812 | 123.7427 | -65.0574 | 58.3878 | 0.06235 | -0.025892 | -0.025108 | -0.052314 | -0.037559 | -0.032865 | 0.065477 | -0.019877 | -0.015009 | 0.0039834 | 0.14224 | 0.0032705 | -0.072207 | -0.012329 | -0.054192 | 0.006344 | -0.050009 | 0.073287 | -0.058478 | -64.7419 | -13.2596 | -64.3964 | 58.3001 | 58.4184 | 58.2979 | -65.3848 | 64.9989 | -58.3814 | 64.9852 | 65.0032 | 0.004286 | -58.4378 | -58.3145 | -0.32745 | -0.087682 | 0.31546 | 0.66099 | 0.98844 | 0.030604 | -0.089817 | 65.0637 | 65.0074 | 65.1307 | 65.045 | -58.4462 | 123.3574 | 123.4757 | 123.3553 | 51.7978 | -123.7726
1101.2812 | 123.6969 | -65.1123 | 58.3786 | 0.047088 | -0.025892 | -0.025108 | -0.052314 | -0.038627 | -0.035002 | 0.050216 | -0.018809 | -0.012872 | 0.0039834 | 0.14331 | 0.0032705 | -0.072207 | -0.016908 | -0.054192 | 0.015501 | -0.054588 | 0.087023 | -0.049321 | -64.7877 | -12.994 | -64.433 | 58.268 | 58.3817 | 58.2613 | -65.426 | 65.063 | -58.3631 | 65.0401 | 65.0581 | -0.004871 | -58.4332 | -58.2916 | -0.31372 | -0.11058 | 0.32461 | 0.67929 | 0.99302 | 0.00313 | -0.11729 | 65.1278 | 65.0577 | 65.1993 | 65.0954 | -58.4279 | 123.3803 | 123.494 | 123.3736 | 52.1183 | -123.8046
1102.2812 | 123.6649 | -65.332 | 58.2092 | 0.047088 | -0.024824 | -0.026176 | -0.053383 | -0.038627 | -0.033933 | 0.050216 | -0.019877 | -0.015009 | 0.0018474 | 0.14331 | 0.0032705 | -0.076785 | -0.012329 | -0.054192 | 0.015501 | -0.059167 | 0.09618 | -0.049321 | -64.8655 | -12.4812 | -64.5612 | 58.1856 | 58.2993 | 58.1697 | -65.5039 | 65.2827 | -58.1937 | 65.2552 | 65.2778 | -0.004871 | -58.2684 | -58.113 | -0.17184 | -0.023617 | 0.4665 | 0.77081 | 0.94265 | 0.090088 | -0.039491 | 65.3475 | 65.2729 | 65.4282 | 65.3197 | -58.2585 | 123.5176 | 123.6313 | 123.5018 | 52.8508 | -123.7131
1103.2812 | 123.6099 | -64.9887 | 58.5571 | 0.047088 | -0.025892 | -0.026176 | -0.051246 | -0.038627 | -0.033933 | 0.065477 | -0.019877 | -0.012872 | 0.0018474 | 0.14331 | 0.0022015 | -0.076785 | -0.007751 | -0.049614 | 0.024657 | -0.059167 | 0.091601 | -0.049321 | -64.7099 | -12.6644 | -64.3323 | 58.3275 | 58.4504 | 58.3254 | -65.3573 | 64.9394 | -58.5325 | 64.9119 | 64.9391 | -0.000293 | -58.6163 | -58.4655 | -0.36864 | -0.22958 | 0.27885 | 0.65643 | 1.0251 | -0.10672 | -0.23172 | 65.0134 | 64.9295 | 65.0803 | 64.981 | -58.6065 | 123.3163 | 123.4391 | 123.3141 | 52.3244 | -123.9145
1104.2812 | 123.6923 | -64.9933 | 58.5342 | 0.047088 | -0.025892 | -0.025108 | -0.052314 | -0.039695 | -0.032865 | 0.065477 | -0.019877 | -0.015009 | 0.0029154 | 0.14331 | 0.0022015 | -0.072207 | -0.021486 | -0.045036 | 0.024657 | -0.063746 | 0.073287 | -0.058478 | -64.6412 | -12.2202 | -64.2911 | 58.41 | 58.5237 | 58.4078 | -65.2795 | 64.9348 | -58.5096 | 64.9211 | 64.9483 | 0.013442 | -58.598 | -58.461 | -0.28622 | -0.12428 | 0.35211 | 0.70221 | 0.98844 | -0.010573 | -0.12642 | 65.0179 | 64.9295 | 65.0666 | 64.9718 | -58.5927 | 123.4032 | 123.517 | 123.4011 | 52.7731 | -123.8137
1105.2812 | 123.7335 | -65.1077 | 58.3694 | 0.031826 | -0.024824 | -0.029381 | -0.051246 | -0.038627 | -0.033933 | 0.065477 | -0.018809 | -0.015009 | 0.0018474 | 0.14224 | 0.0032705 | -0.067628 | -0.026065 | -0.049614 | 0.015501 | -0.068325 | 0.082444 | -0.049321 | -64.7144 | -12.0142 | -64.346 | 58.3275 | 58.4413 | 58.3071 | -65.3665 | 65.0584 | -58.3539 | 65.0401 | 65.0581 | -0.000293 | -58.4378 | -58.287 | -0.25878 | -0.041901 | 0.39329 | 0.76171 | 1.0205 | 0.071807 | -0.062349 | 65.1232 | 65.0394 | 65.1902 | 65.0817 | -58.4188 | 123.4353 | 123.549 | 123.4148 | 53.0936 | -123.736
1106.2656 | 123.7656 | -65.1031 | 58.3923 | 0.06235 | -0.025892 | -0.028313 | -0.051246 | -0.038627 | -0.032865 | 0.065477 | -0.018809 | -0.015009 | 0.0029154 | 0.14331 | 0.0022015 | -0.067628 | -0.016908 | -0.054192 | 0.020079 | -0.059167 | 0.087023 | -0.053899 | -64.7328 | -12.5682 | -64.3735 | 58.3184 | 58.4367 | 58.3208 | -65.3665 | 65.0493 | -58.3723 | 65.0355 | 65.049 | -0.000293 | -58.4515 | -58.3053 | -0.26336 | -0.073946 | 0.3704 | 0.72966 | 0.99302 | 0.044341 | -0.071502 | 65.1232 | 65.044 | 65.1902 | 65.0862 | -58.4462 | 123.4215 | 123.5398 | 123.424 | 52.5349 | -123.7588
1107.2812 | 123.6649 | -64.9246 | 58.6121 | 0.047088 | -0.024824 | -0.028313 | -0.050177 | -0.037559 | -0.033933 | 0.050216 | -0.019877 | -0.012872 | 0.0029154 | 0.14224 | 0.0022015 | -0.067628 | -0.012329 | -0.049614 | 0.020079 | -0.063746 | 0.091601 | -0.044742 | -64.6045 | -12.1836 | -64.2178 | 58.4466 | 58.5649 | 58.449 | -65.2383 | 64.8799 | -58.592 | 64.857 | 64.875 | -0.004872 | -58.6758 | -58.5205 | -0.31368 | -0.16547 | 0.32007 | 0.70681 | 1.0205 | -0.047185 | -0.16303 | 64.9447 | 64.8609 | 65.0162 | 64.9123 | -58.6568 | 123.3712 | 123.4895 | 123.3737 | 52.741 | -123.8504
1108.2812 | 123.6465 | -65.007 | 58.5114 | 0.047088 | -0.028029 | -0.027244 | -0.054451 | -0.037559 | -0.032865 | 0.065477 | -0.020945 | -0.01394 | 0.0018474 | 0.14224 | 0.0022015 | -0.067628 | -0.012329 | -0.045036 | 0.020079 | -0.054588 | 0.082444 | -0.053899 | -64.6412 | -12.6048 | -64.2911 | 58.4054 | 58.5191 | 58.3895 | -65.2932 | 64.9531 | -58.4913 | 64.9394 | 64.962 | 0.008863 | -58.5659 | -58.4289 | -0.28623 | -0.10597 | 0.36584 | 0.71595 | 1.0022 | 0.007736 | -0.12184 | 65.0271 | 64.9524 | 65.0895 | 64.9947 | -58.5653 | 123.4124 | 123.5261 | 123.3965 | 52.4022 | -123.8046
1109.2812 | 123.6832 | -65.213 | 58.2916 | 0.047088 | -0.024824 | -0.025108 | -0.052314 | -0.037559 | -0.035002 | 0.065477 | -0.022013 | -0.015009 | 0.0039834 | 0.14331 | 0.0011335 | -0.067628 | -0.012329 | -0.045036 | 0.015501 | -0.059167 | 0.082444 | -0.058478 | -64.7328 | -13.516 | -64.3826 | 58.323 | 58.4458 | 58.3208 | -65.3711 | 65.1545 | -58.2761 | 65.1454 | 65.168 | 0.013442 | -58.3508 | -58.2092 | -0.15807 | 0.031341 | 0.48026 | 0.83037 | 0.98844 | 0.15421 | 0.029206 | 65.2285 | 65.1538 | 65.2955 | 65.2007 | -58.3501 | 123.536 | 123.6588 | 123.5338 | 51.697 | -123.6627
1110.2812 | 123.6877 | -65.0848 | 58.4198 | 0.06235 | -0.02696 | -0.025108 | -0.051246 | -0.03649 | -0.032865 | 0.050216 | -0.020945 | -0.012872 | 0.0029154 | 0.14224 | 0.0022015 | -0.072207 | -0.012329 | -0.045036 | 0.029236 | -0.054588 | 0.077866 | -0.053899 | -64.7602 | -13.5847 | -64.3872 | 58.3001 | 58.4138 | 58.2934 | -65.4031 | 65.0309 | -58.3906 | 65.0126 | 65.0398 | 0.008863 | -58.4744 | -58.3419 | -0.3183 | -0.11973 | 0.32461 | 0.69761 | 1.0159 | -0.006018 | -0.12644 | 65.1141 | 65.0303 | 65.1627 | 65.0725 | -58.4737 | 123.3849 | 123.4986 | 123.3782 | 51.5002 | -123.8229
1111.2812 | 123.642 | -64.975 | 58.5297 | 0.077612 | -0.02696 | -0.026176 | -0.053383 | -0.037559 | -0.033933 | 0.050216 | -0.020945 | -0.01394 | 0.0018474 | 0.14331 | 0.0022015 | -0.072207 | -0.021486 | -0.040457 | 0.024657 | -0.063746 | 0.091601 | -0.053899 | -64.7465 | -13.2504 | -64.3826 | 58.3275 | 58.4367 | 58.3208 | -65.3802 | 64.9211 | -58.505 | 64.9028 | 64.9345 | 0.013442 | -58.5934 | -58.4381 | -0.40527 | -0.20212 | 0.22849 | 0.59233 | 0.9976 | -0.092988 | -0.20883 | 64.9996 | 64.9112 | 65.0666 | 64.9535 | -58.5836 | 123.3025 | 123.4117 | 123.2958 | 51.7245 | -123.9099
1112.2812 | 123.6374 | -65.062 | 58.4793 | 0.077612 | -0.025892 | -0.025108 | -0.053383 | -0.038627 | -0.032865 | 0.080738 | -0.019877 | -0.015009 | 0.0018474 | 0.14331 | 0.0022015 | -0.067628 | -0.012329 | -0.045036 | 0.010922 | -0.059167 | 0.077866 | -0.049321 | -64.7373 | -13.7999 | -64.3964 | 58.3184 | 58.4321 | 58.3071 | -65.3757 | 65.0126 | -58.4684 | 64.9943 | 65.0169 | 0.004285 | -58.5385 | -58.4014 | -0.31371 | -0.16092 | 0.32462 | 0.66557 | 0.97928 | -0.047213 | -0.17221 | 65.0729 | 65.0028 | 65.1398 | 65.0496 | -58.5286 | 123.3803 | 123.494 | 123.369 | 51.2621 | -123.855
1113.2812 | 123.6877 | -65.126 | 58.374 | 0.047088 | -0.025892 | -0.027244 | -0.051246 | -0.037559 | -0.033933 | 0.050216 | -0.018809 | -0.015009 | 0.0029154 | 0.14331 | 0.0022015 | -0.067628 | -0.007751 | -0.045036 | 0.020079 | -0.059167 | 0.082444 | -0.049321 | -64.7511 | -13.7037 | -64.4559 | 58.2863 | 58.3909 | 58.2705 | -65.4169 | 65.0767 | -58.3539 | 65.0584 | 65.081 | 0.004285 | -58.4332 | -58.2916 | -0.29084 | -0.087684 | 0.37497 | 0.67013 | 0.96097 | 0.016866 | -0.10356 | 65.1461 | 65.0669 | 65.2085 | 65.1183 | -58.4233 | 123.4124 | 123.5169 | 123.3965 | 51.4223 | -123.7909
1114.2656 | 123.7793 | -65.0253 | 58.4335 | 0.047088 | -0.025892 | -0.027244 | -0.052314 | -0.037559 | -0.032865 | 0.050216 | -0.019877 | -0.01394 | 0.0029154 | 0.14438 | 0.0022015 | -0.076785 | -0.012329 | -0.040457 | 0.020079 | -0.059167 | 0.068708 | -0.063057 | -64.6686 | -13.6305 | -64.3369 | 58.3733 | 58.4962 | 58.3575 | -65.3161 | 64.9623 | -58.4135 | 64.9485 | 64.9849 | 0.0226 | -58.4927 | -58.3648 | -0.29081 | -0.060203 | 0.35668 | 0.68847 | 0.97928 | 0.062663 | -0.076072 | 65.0454 | 64.9662 | 65.094 | 65.013 | -58.4966 | 123.3987 | 123.5215 | 123.3828 | 51.3949 | -123.7497
1115.2812 | 123.6832 | -65.0208 | 58.5159 | 0.06235 | -0.02696 | -0.028313 | -0.051246 | -0.038627 | -0.035002 | 0.080738 | -0.018809 | -0.012872 | 0.0018474 | 0.14438 | 0.0032705 | -0.06305 | -0.007751 | -0.045036 | 0.010922 | -0.063746 | 0.082444 | -0.049321 | -64.7236 | -13.5984 | -64.401 | 58.323 | 58.4275 | 58.3117 | -65.3894 | 64.9714 | -58.505 | 64.9577 | 64.9757 | 0.004285 | -58.5797 | -58.4335 | -0.36865 | -0.19296 | 0.29716 | 0.61979 | 0.98844 | -0.088413 | -0.20425 | 65.0317 | 64.957 | 65.1032 | 65.013 | -58.5653 | 123.3437 | 123.4483 | 123.3324 | 51.4223 | -123.9053
1116.2812 | 123.7747 | -65.3183 | 58.1314 | 0.06235 | -0.028029 | -0.028313 | -0.052314 | -0.037559 | -0.032865 | 0.080738 | -0.019877 | -0.015009 | 0.0018474 | 0.14438 | 0.0022015 | -0.06305 | -0.007751 | -0.049614 | 0.020079 | -0.054588 | 0.082444 | -0.049321 | -64.9892 | -12.7971 | -64.7627 | 58.0803 | 58.1986 | 58.069 | -65.6229 | 65.269 | -58.1113 | 65.2552 | 65.2687 | -0.000293 | -58.186 | -58.049 | -0.30462 | -0.051102 | 0.32914 | 0.55562 | 0.86024 | 0.067178 | -0.0624 | 65.3384 | 65.2637 | 65.4007 | 65.3105 | -58.1807 | 123.3986 | 123.5169 | 123.3873 | 52.5212 | -123.7543
1117.2812 | 123.6374 | -65.3091 | 58.2413 | 0.06235 | -0.02696 | -0.026176 | -0.052314 | -0.03649 | -0.033933 | 0.065477 | -0.020945 | -0.015009 | 0.0029154 | 0.14544 | 0.0032705 | -0.06305 | -0.007751 | -0.040457 | 0.015501 | -0.063746 | 0.077866 | -0.049321 | -64.9388 | -13.5389 | -64.694 | 58.094 | 58.2077 | 58.0965 | -65.6 | 65.2598 | -58.2258 | 65.2461 | 65.2687 | 0.008864 | -58.305 | -58.1634 | -0.29088 | -0.14723 | 0.37035 | 0.61515 | 0.90603 | -0.033527 | -0.14479 | 65.3246 | 65.2454 | 65.387 | 65.3014 | -58.2906 | 123.4032 | 123.5169 | 123.4056 | 51.7703 | -123.8413
1118.2812 | 123.6374 | -65.3 | 58.2596 | 0.06235 | -0.028029 | -0.026176 | -0.053383 | -0.037559 | -0.033933 | 0.065477 | -0.018809 | -0.012872 | 0.0018474 | 0.14544 | 0.0022015 | -0.06305 | -0.016908 | -0.045036 | 0.020079 | -0.059167 | 0.082444 | -0.049321 | -64.9251 | -13.6808 | -64.6024 | 58.1352 | 58.2444 | 58.1331 | -65.5634 | 65.2507 | -58.2395 | 65.2369 | 65.255 | 0.004285 | -58.3188 | -58.1771 | -0.26341 | -0.12433 | 0.37493 | 0.69756 | 0.96097 | -0.01521 | -0.12647 | 65.3201 | 65.2408 | 65.3824 | 65.2831 | -58.3089 | 123.4352 | 123.5444 | 123.4331 | 51.6192 | -123.823
1119.2812 | 123.7747 | -65.2817 | 58.1955 | 0.06235 | -0.02696 | -0.026176 | -0.052314 | -0.03649 | -0.032865 | 0.065477 | -0.022013 | -0.011804 | 0.0018474 | 0.14438 | 0.0022015 | -0.072207 | -0.016908 | -0.040457 | 0.029236 | -0.059167 | 0.091601 | -0.053899 | -64.9434 | -13.5526 | -64.5978 | 58.1124 | 58.2352 | 58.1011 | -65.5954 | 65.2278 | -58.1663 | 65.2095 | 65.2412 | 0.013442 | -58.2547 | -58.1039 | -0.31377 | -0.08314 | 0.3383 | 0.68383 | 0.9976 | 0.03972 | -0.094437 | 65.3109 | 65.2225 | 65.3733 | 65.2648 | -58.2494 | 123.394 | 123.5169 | 123.3827 | 51.7291 | -123.7909
1120.2812 | 123.6649 | -65.2817 | 58.2504 | 0.047088 | -0.028029 | -0.027244 | -0.052314 | -0.037559 | -0.032865 | 0.080738 | -0.020945 | -0.01394 | 0.0039834 | 0.14438 | 0.0022015 | -0.072207 | -0.007751 | -0.035879 | 0.024657 | -0.059167 | 0.091601 | -0.049321 | -64.9296 | -12.2385 | -64.6665 | 58.1352 | 58.2444 | 58.1285 | -65.5771 | 65.2324 | -58.2258 | 65.2095 | 65.2458 | 0.013442 | -58.3096 | -58.1588 | -0.29545 | -0.11518 | 0.35204 | 0.61515 | 0.9106 | -0.006054 | -0.1219 | 65.3063 | 65.2225 | 65.3733 | 65.2739 | -58.2997 | 123.4169 | 123.526 | 123.4102 | 53.0431 | -123.8276
1121.2656 | 123.7427 | -65.451 | 58.0536 | 0.06235 | -0.024824 | -0.027244 | -0.053383 | -0.038627 | -0.031797 | 0.050216 | -0.019877 | -0.012872 | 0.0029154 | 0.14544 | 0.0022015 | -0.06305 | -0.016908 | -0.045036 | 0.024657 | -0.059167 | 0.077866 | -0.044742 | -65.0762 | -12.1332 | -64.8451 | 57.9842 | 58.1024 | 57.9729 | -65.7145 | 65.4063 | -58.0289 | 65.388 | 65.406 | -0.000294 | -58.1128 | -57.9757 | -0.26345 | -0.069431 | 0.37489 | 0.60595 | 0.8694 | 0.048848 | -0.08073 | 65.4757 | 65.3919 | 65.5289 | 65.4341 | -58.0983 | 123.4352 | 123.5535 | 123.4239 | 53.3178 | -123.7681
1122.2656 | 123.7198 | -65.3503 | 58.1543 | 0.06235 | -0.028029 | -0.028313 | -0.053383 | -0.038627 | -0.032865 | 0.034955 | -0.022013 | -0.012872 | 0.0029154 | 0.14544 | 0.0011335 | -0.06305 | -0.016908 | -0.040457 | 0.020079 | -0.054588 | 0.082444 | -0.040163 | -65.0349 | -11.7349 | -64.8588 | 58.0299 | 58.1482 | 58.0186 | -65.6779 | 65.3102 | -58.1342 | 65.2873 | 65.3099 | -0.000294 | -58.2089 | -58.0719 | -0.32752 | -0.12435 | 0.31539 | 0.49151 | 0.81903 | -0.006074 | -0.13565 | 65.3704 | 65.2958 | 65.4328 | 65.3334 | -58.1945 | 123.3803 | 123.4986 | 123.369 | 53.6155 | -123.8322
1123.2812 | 123.642 | -65.2176 | 58.3145 | 0.077612 | -0.02696 | -0.028313 | -0.052314 | -0.038627 | -0.032865 | 0.065477 | -0.019877 | -0.012872 | 0.0029154 | 0.14758 | 0.0011335 | -0.06305 | -0.007751 | -0.049614 | 0.010922 | -0.059167 | 0.091601 | -0.053899 | -64.8655 | -11.6799 | -64.6803 | 58.1948 | 58.3085 | 58.1789 | -65.4993 | 65.1637 | -58.3036 | 65.1545 | 65.168 | 0.004285 | -58.3737 | -58.2229 | -0.2817 | -0.11975 | 0.35206 | 0.53733 | 0.81903 | -0.00604 | -0.13562 | 65.2285 | 65.1584 | 65.3092 | 65.2098 | -58.3684 | 123.4124 | 123.5261 | 123.3965 | 53.5377 | -123.8138
1124.2656 | 123.7701 | -65.1306 | 58.3374 | 0.06235 | -0.02696 | -0.027244 | -0.052314 | -0.037559 | -0.033933 | 0.050216 | -0.019877 | -0.01394 | 0.0018474 | 0.14544 | 0.0032705 | -0.06305 | -0.012329 | -0.049614 | 0.020079 | -0.063746 | 0.082444 | -0.049321 | -64.7877 | -12.3896 | -64.607 | 58.268 | 58.3772 | 58.2522 | -65.4398 | 65.0813 | -58.3173 | 65.0676 | 65.081 | -0.000293 | -58.4011 | -58.255 | -0.30915 | -0.069377 | 0.34292 | 0.52361 | 0.83276 | 0.039751 | -0.085249 | 65.1507 | 65.0669 | 65.2131 | 65.1183 | -58.3867 | 123.3986 | 123.5078 | 123.3828 | 52.741 | -123.7772
1125.2812 | 123.6465 | -65.0986 | 58.4381 | 0.06235 | -0.025892 | -0.028313 | -0.053383 | -0.037559 | -0.033933 | 0.065477 | -0.019877 | -0.016077 | 0.0029154 | 0.14331 | 0.0011335 | -0.067628 | -0.007751 | -0.049614 | 0.020079 | -0.063746 | 0.082444 | -0.040163 | -64.7648 | -12.6689 | -64.5658 | 58.2955 | 58.4184 | 58.2888 | -65.4031 | 65.0584 | -58.418 | 65.0309 | 65.049 | -0.009451 | -58.5019 | -58.3557 | -0.30456 | -0.14261 | 0.33377 | 0.53278 | 0.83734 | -0.01975 | -0.14933 | 65.1187 | 65.0348 | 65.181 | 65.0908 | -58.4783 | 123.3941 | 123.5169 | 123.3874 | 52.4296 | -123.8412
1126.2656 | 123.7885 | -65.0436 | 58.3969 | 0.031826 | -0.02696 | -0.027244 | -0.051246 | -0.037559 | -0.035002 | 0.050216 | -0.020945 | -0.01394 | 0.00077942 | 0.14651 | 0.0022015 | -0.06305 | -0.012329 | -0.040457 | 0.020079 | -0.068325 | 0.082444 | -0.040163 | -64.7236 | -12.7513 | -64.5063 | 58.3413 | 58.4596 | 58.33 | -65.3528 | 65.0035 | -58.3768 | 64.9806 | 65.0032 | -0.000294 | -58.4652 | -58.3145 | -0.30913 | -0.055631 | 0.32004 | 0.53737 | 0.8465 | 0.062656 | -0.066922 | 65.0637 | 64.9753 | 65.1261 | 65.0313 | -58.4371 | 123.3849 | 123.5032 | 123.3736 | 52.2923 | -123.7497
1127.2656 | 123.761 | -65.0894 | 58.3694 | 0.047088 | -0.02696 | -0.028313 | -0.054451 | -0.039695 | -0.033933 | 0.050216 | -0.020945 | -0.012872 | 0.0029154 | 0.14651 | 0.0011335 | -0.058472 | -0.007751 | -0.049614 | 0.015501 | -0.059167 | 0.09618 | -0.044742 | -64.7602 | -13.5435 | -64.488 | 58.3321 | 58.4458 | 58.3025 | -65.3711 | 65.0447 | -58.3539 | 65.0309 | 65.0398 | -0.004872 | -58.4286 | -58.2733 | -0.28167 | -0.037322 | 0.32919 | 0.60146 | 0.88313 | 0.076386 | -0.066928 | 65.1049 | 65.0302 | 65.1856 | 65.0817 | -58.4142 | 123.4215 | 123.5352 | 123.3919 | 51.546 | -123.7405
1128.2812 | 123.7198 | -65.0711 | 58.3786 | 0.031826 | -0.024824 | -0.028313 | -0.054451 | -0.037559 | -0.033933 | 0.065477 | -0.020945 | -0.01394 | 0.00077942 | 0.14758 | 0.0022015 | -0.072207 | -0.016908 | -0.045036 | 0.010922 | -0.063746 | 0.09618 | -0.035584 | -64.8152 | -13.081 | -64.5612 | 58.2772 | 58.4 | 58.2659 | -65.426 | 65.0355 | -58.3677 | 64.9989 | 65.0261 | -0.009452 | -58.4423 | -58.2824 | -0.35492 | -0.10142 | 0.25594 | 0.50989 | 0.86481 | 0.021445 | -0.11271 | 65.082 | 65.0074 | 65.1673 | 65.0542 | -58.4142 | 123.3483 | 123.4712 | 123.337 | 51.9901 | -123.8046
1129.2656 | 123.7656 | -65.0299 | 58.4198 | 0.031826 | -0.02696 | -0.028313 | -0.051246 | -0.037559 | -0.03607 | 0.050216 | -0.020945 | -0.011804 | 0.0018474 | 0.14651 | 0.0022015 | -0.067628 | -0.016908 | -0.049614 | 0.029236 | -0.054588 | 0.091601 | -0.044742 | -64.7236 | -12.7697 | -64.488 | 58.355 | 58.4687 | 58.3437 | -65.3528 | 64.9852 | -58.3906 | 64.9623 | 64.9803 | -0.004872 | -58.4744 | -58.3282 | -0.32286 | -0.064784 | 0.30631 | 0.54195 | 0.86481 | 0.048925 | -0.076075 | 65.0591 | 64.9753 | 65.1215 | 65.013 | -58.4645 | 123.3849 | 123.4986 | 123.3736 | 52.2602 | -123.7726
1130.2812 | 123.7152 | -65.1398 | 58.3786 | 0.047088 | -0.02696 | -0.028313 | -0.054451 | -0.03649 | -0.032865 | 0.065477 | -0.020945 | -0.011804 | 0.0029154 | 0.14651 | 6.5515e-05 | -0.06305 | -0.012329 | -0.040457 | 0.020079 | -0.054588 | 0.087023 | -0.035584 | -64.806 | -12.0645 | -64.6207 | 58.2634 | 58.3909 | 58.243 | -65.4352 | 65.1042 | -58.3585 | 65.0767 | 65.0993 | -0.004873 | -58.4332 | -58.2916 | -0.29542 | -0.11516 | 0.33376 | 0.51903 | 0.81445 | 0.012288 | -0.13561 | 65.1598 | 65.0852 | 65.2268 | 65.1274 | -58.4142 | 123.4032 | 123.5307 | 123.3828 | 53.0752 | -123.8138
1131.2812 | 123.7289 | -65.1672 | 58.287 | 0.047088 | -0.02696 | -0.028313 | -0.053383 | -0.03649 | -0.033933 | 0.065477 | -0.017741 | -0.012872 | 0.0029154 | 0.14544 | 0.0011335 | -0.058472 | -0.007751 | -0.049614 | 0.020079 | -0.059167 | 0.10076 | -0.053899 | -64.8426 | -12.9574 | -64.6482 | 58.2268 | 58.3497 | 58.2201 | -65.4718 | 65.1133 | -58.267 | 65.1088 | 65.1176 | 0.004285 | -58.3462 | -58.1863 | -0.30458 | -0.06023 | 0.3246 | 0.51902 | 0.82361 | 0.062633 | -0.066945 | 65.1873 | 65.1081 | 65.268 | 65.1595 | -58.3409 | 123.3941 | 123.5169 | 123.3873 | 52.2098 | -123.7589
1132.2656 | 123.7198 | -65.1031 | 58.3969 | 0.047088 | -0.02696 | -0.03045 | -0.054451 | -0.038627 | -0.032865 | 0.050216 | -0.020945 | -0.01394 | 0.0029154 | 0.14651 | 0.0011335 | -0.058472 | -0.012329 | -0.045036 | 0.015501 | -0.059167 | 0.082444 | -0.049321 | -64.7282 | -13.1589 | -64.4925 | 58.3459 | 58.4596 | 58.33 | -65.3665 | 65.0538 | -58.3814 | 65.0447 | 65.0581 | 0.004285 | -58.4561 | -58.3145 | -0.26336 | -0.051053 | 0.37498 | 0.61061 | 0.87397 | 0.062656 | -0.066922 | 65.1187 | 65.044 | 65.1856 | 65.0908 | -58.4462 | 123.449 | 123.5627 | 123.4331 | 51.9443 | -123.7634
1133.2812 | 123.7427 | -65.1718 | 58.3008 | 0.047088 | -0.02696 | -0.028313 | -0.053383 | -0.037559 | -0.033933 | 0.065477 | -0.019877 | -0.012872 | 0.00077942 | 0.14544 | -0.0010025 | -0.067628 | -0.016908 | -0.045036 | 0.024657 | -0.059167 | 0.091601 | -0.044742 | -64.8152 | -12.9437 | -64.5933 | 58.2497 | 58.3772 | 58.2476 | -65.4443 | 65.1271 | -58.2761 | 65.1042 | 65.1268 | -0.000294 | -58.3599 | -58.2092 | -0.27253 | -0.05107 | 0.35665 | 0.57855 | 0.85108 | 0.076372 | -0.053206 | 65.1965 | 65.1126 | 65.2634 | 65.1549 | -58.3455 | 123.4215 | 123.549 | 123.4194 | 52.2282 | -123.7451
1134.2656 | 123.6603 | -65.2084 | 58.3328 | 0.06235 | -0.02696 | -0.027244 | -0.052314 | -0.037559 | -0.035002 | 0.050216 | -0.019877 | -0.016077 | 0.00077942 | 0.14651 | 0.0011335 | -0.06305 | -0.012329 | -0.045036 | 0.020079 | -0.054588 | 0.087023 | -0.040163 | -64.8335 | -12.9482 | -64.607 | 58.236 | 58.3588 | 58.2109 | -65.4627 | 65.1683 | -58.3127 | 65.1454 | 65.1634 | -0.004873 | -58.3874 | -58.2458 | -0.25423 | -0.09685 | 0.37495 | 0.60143 | 0.85566 | 0.026013 | -0.12188 | 65.2285 | 65.1538 | 65.2955 | 65.1961 | -58.373 | 123.4444 | 123.5673 | 123.4194 | 52.2602 | -123.7955
1135.2969 | 123.7061 | -65.2176 | 58.287 | 0.047088 | -0.029097 | -0.028313 | -0.054451 | -0.037559 | -0.035002 | 0.065477 | -0.020945 | -0.011804 | 0.0029154 | 0.14758 | 0.0011335 | -0.067628 | -0.012329 | -0.045036 | 0.024657 | -0.068325 | 0.087023 | -0.044742 | -64.8701 | -12.962 | -64.6436 | 58.1948 | 58.3176 | 58.1835 | -65.5084 | 65.1728 | -58.2624 | 65.15 | 65.1726 | -0.000294 | -58.3554 | -58.2 | -0.29086 | -0.092279 | 0.34748 | 0.57396 | 0.86482 | 0.030583 | -0.10357 | 65.2422 | 65.1493 | 65.3046 | 65.2053 | -58.3318 | 123.4124 | 123.5352 | 123.4011 | 52.2556 | -123.7955
1136.2656 | 123.674 | -65.2405 | 58.2687 | 0.047088 | -0.02696 | -0.028313 | -0.053383 | -0.039695 | -0.033933 | 0.065477 | -0.020945 | -0.011804 | 0.0018474 | 0.14651 | 0.0011335 | -0.06305 | -0.003172 | -0.049614 | 0.015501 | -0.063746 | 0.10076 | -0.040163 | -64.8884 | -12.9665 | -64.6253 | 58.181 | 58.3131 | 58.1789 | -65.5176 | 65.2003 | -58.2532 | 65.1774 | 65.1909 | -0.009451 | -58.3325 | -58.168 | -0.27713 | -0.087705 | 0.35205 | 0.61516 | 0.89229 | 0.044314 | -0.089842 | 65.256 | 65.1767 | 65.3412 | 65.2373 | -58.3089 | 123.4215 | 123.5535 | 123.4194 | 52.2739 | -123.7863
1137.2812 | 123.7473 | -65.2084 | 58.2733 | 0.047088 | -0.029097 | -0.029381 | -0.053383 | -0.03649 | -0.032865 | 0.034955 | -0.019877 | -0.01394 | 0.0018474 | 0.14651 | 0.0011335 | -0.067628 | -0.007751 | -0.040457 | 0.006344 | -0.063746 | 0.09618 | -0.053899 | -64.8793 | -12.3072 | -64.6345 | 58.1948 | 58.3176 | 58.1697 | -65.5084 | 65.1545 | -58.267 | 65.1408 | 65.168 | 0.013442 | -58.3371 | -58.1771 | -0.30001 | -0.078546 | 0.32916 | 0.57396 | 0.87397 | 0.044316 | -0.10358 | 65.2148 | 65.1447 | 65.3046 | 65.2007 | -58.3272 | 123.4032 | 123.5261 | 123.3782 | 52.9012 | -123.7818
1138.2812 | 123.7701 | -65.2359 | 58.2092 | 0.047088 | -0.030165 | -0.028313 | -0.054451 | -0.037559 | -0.035002 | 0.050216 | -0.020945 | -0.012872 | 0.0018474 | 0.14651 | 6.5515e-05 | -0.067628 | -0.012329 | -0.045036 | 0.033814 | -0.036272 | 0.11449 | -0.12716 | -64.9022 | -11.6662 | -64.6482 | 58.1719 | 58.2947 | 58.2705 | -65.5268 | 65.1087 | -58.1754 | 65.1683 | 65.1909 | 0.082126 | -58.2455 | -58.0947 | -0.29086 | -0.037353 | 0.33374 | 0.58769 | 0.87855 | 0.085509 | 0.061239 | 65.2697 | 65.1996 | 65.3504 | 65.2236 | -58.3364 | 123.4078 | 123.5306 | 123.5064 | 53.5697 | -123.736
1139.2812 | 123.793 | -65.2679 | 58.2138 | 0.06235 | -0.02696 | -0.029381 | -0.054451 | -0.03649 | -0.033933 | 0.050216 | -0.019877 | -0.012872 | 0.0039834 | 0.14651 | 6.5515e-05 | -0.067628 | -0.007751 | -0.045036 | 0.024657 | -0.063746 | 2.9e-05 | 0.07431 | -64.948 | -10.9565 | -64.694 | 58.1169 | 58.2444 | 57.8676 | -65.5817 | 65.3423 | -58.1891 | 65.2003 | 65.2229 | -0.11935 | -58.2776 | -58.2138 | -0.31377 | -0.096871 | 0.31999 | 0.57395 | 0.88771 | 0.030567 | -0.34625 | 65.2926 | 65.2042 | 65.268 | 65.2602 | -58.1395 | 123.3849 | 123.5123 | 123.1355 | 54.3115 | -123.7955
1140.2812 | 123.7518 | -65.2863 | 58.1863 | 0.047088 | -0.029097 | -0.029381 | -0.054451 | -0.035422 | -0.031797 | 0.050216 | -0.019877 | -0.012872 | 0.0018474 | 0.14651 | -0.0010025 | -0.067628 | -0.007751 | -0.045036 | -0.01197 | -0.072904 | 0.077866 | 0.055995 | -64.98 | -9.7157 | -64.7032 | 58.0803 | 58.2032 | 57.8721 | -65.6138 | 65.3422 | -58.1983 | 65.2186 | 65.2412 | -0.10103 | -58.2592 | -58.1085 | -0.32751 | -0.10603 | 0.30625 | 0.5831 | 0.91061 | 0.016826 | -0.31421 | 65.2743 | 65.2134 | 65.3641 | 65.2785 | -58.1303 | 123.3666 | 123.4894 | 123.1584 | 55.5706 | -123.8001
1141.2812 | 123.7793 | -65.2817 | 58.2001 | 0.047088 | -0.030165 | -0.029381 | -0.055519 | -0.037559 | -0.032865 | 0.050216 | -0.019877 | -0.012872 | 0.0029154 | 0.14758 | 0.0011335 | -0.067628 | -0.012329 | -0.05877 | 0.020079 | -0.054588 | 0.018344 | 0.065153 | -64.9525 | -11.1808 | -64.6757 | 58.1124 | 58.2352 | 57.8721 | -65.5909 | 65.3468 | -58.18 | 65.214 | 65.2229 | -0.12392 | -58.2547 | -58.1817 | -0.30919 | -0.087717 | 0.32915 | 0.60599 | 0.91518 | 0.035143 | -0.32794 | 65.3018 | 65.2271 | 65.3 | 65.2693 | -58.1349 | 123.394 | 123.5169 | 123.1538 | 54.1008 | -123.7909
1142.2656 | 123.6465 | -65.3412 | 58.2504 | 0.047088 | -0.030165 | -0.028313 | -0.054451 | -0.03649 | -0.032865 | 0.065477 | -0.020945 | -0.015009 | 0.0018474 | 0.14758 | 0.0011335 | -0.06305 | -0.007751 | -0.040457 | 0.024657 | -0.063746 | 0.004608 | 0.055995 | -64.9617 | -11.7395 | -64.6711 | 58.1078 | 58.2306 | 57.863 | -65.6 | 65.3972 | -58.2258 | 65.2781 | 65.3007 | -0.096452 | -58.3142 | -58.2458 | -0.25884 | -0.14265 | 0.3795 | 0.67008 | 0.92892 | -0.019789 | -0.38746 | 65.3658 | 65.2774 | 65.3458 | 65.3334 | -58.1944 | 123.449 | 123.5718 | 123.2042 | 53.6017 | -123.8505
1143.2812 | 123.7289 | -65.1993 | 58.2779 | 0.06235 | -0.029097 | -0.03045 | -0.054451 | -0.037559 | -0.033933 | 0.065477 | -0.019877 | -0.012872 | 0.00077942 | 0.14651 | 0.0022015 | -0.072207 | -0.016908 | -0.035879 | 0.020079 | -0.072904 | 2.9e-05 | 0.055995 | -64.893 | -11.6341 | -64.575 | 58.181 | 58.2947 | 57.95 | -65.5359 | 65.2553 | -58.2578 | 65.1271 | 65.1634 | -0.091874 | -58.3508 | -58.2779 | -0.33664 | -0.09686 | 0.30627 | 0.62433 | 0.96097 | 0.016845 | -0.32793 | 65.2194 | 65.1264 | 65.1993 | 65.1824 | -58.2219 | 123.3803 | 123.494 | 123.1492 | 53.5651 | -123.8138
1144.2812 | 123.642 | -65.2634 | 58.2916 | 0.047088 | -0.028029 | -0.028313 | -0.054451 | -0.038627 | -0.032865 | 0.065477 | -0.019877 | -0.015009 | 0.0018474 | 0.14758 | -0.0020715 | -0.06305 | -0.012329 | -0.040457 | 0.006344 | -0.059167 | 0.11449 | 0.060574 | -64.893 | -11.2816 | -64.6299 | 58.1673 | 58.281 | 57.9454 | -65.5451 | 65.3239 | -58.2853 | 65.2003 | 65.2229 | -0.10103 | -58.3508 | -58.1771 | -0.28171 | -0.12433 | 0.37036 | 0.63347 | 0.91518 | -0.010624 | -0.34624 | 65.2697 | 65.2042 | 65.3779 | 65.251 | -58.2311 | 123.4307 | 123.5444 | 123.2088 | 53.9818 | -123.8367
1145.2812 | 123.7335 | -65.2634 | 58.2092 | 0.06235 | -0.031234 | -0.029381 | -0.055519 | -0.038627 | -0.032865 | 0.095999 | -0.019877 | -0.01394 | 0.00077942 | 0.14651 | 0.0011335 | -0.06305 | -0.012329 | -0.045036 | 0.020079 | -0.063746 | 0.004608 | 0.078889 | -64.9296 | -11.5838 | -64.6391 | 58.1261 | 58.2535 | 57.8492 | -65.5726 | 65.3423 | -58.1891 | 65.2003 | 65.2183 | -0.12393 | -58.273 | -58.2046 | -0.30918 | -0.083137 | 0.33373 | 0.62431 | 0.9335 | 0.044302 | -0.35999 | 65.2834 | 65.1996 | 65.268 | 65.251 | -58.1303 | 123.3895 | 123.5169 | 123.1126 | 53.6796 | -123.7818
1146.2656 | 123.7061 | -65.2496 | 58.2642 | 0.06235 | -0.032302 | -0.028313 | -0.054451 | -0.039695 | -0.03607 | 0.065477 | -0.022013 | -0.015009 | -0.0013576 | 0.14972 | -0.0010025 | -0.058472 | -0.012329 | -0.049614 | 0.024657 | -0.068325 | 0.036658 | -0.031005 | -64.9525 | -11.6937 | -64.6345 | 58.1444 | 58.2718 | 57.8401 | -65.5497 | 65.2186 | -58.2395 | 65.1912 | 65.2 | -0.018609 | -58.3325 | -58.2275 | -0.30002 | -0.11975 | 0.2971 | 0.61516 | 0.91518 | 0.007685 | -0.42408 | 65.2743 | 65.1813 | 65.2863 | 65.2373 | -58.2952 | 123.394 | 123.5215 | 123.0897 | 53.556 | -123.8138
1147.2812 | 123.642 | -65.3183 | 58.2367 | 0.047088 | -0.029097 | -0.029381 | -0.056588 | -0.038627 | -0.035002 | 0.050216 | -0.020945 | -0.01394 | 0.0029154 | 0.14758 | 6.5515e-05 | -0.06305 | -0.003172 | -0.045036 | 0.024657 | -0.059167 | 0.018344 | -0.012689 | -64.9571 | -11.5792 | -64.6253 | 58.1261 | 58.2398 | 57.9958 | -65.5726 | 65.3056 | -58.212 | 65.2552 | 65.2733 | -0.032347 | -58.2959 | -58.2184 | -0.25425 | -0.1106 | 0.36119 | 0.69298 | 0.94724 | 0.003101 | -0.24094 | 65.343 | 65.2591 | 65.3366 | 65.3151 | -58.2494 | 123.4444 | 123.5581 | 123.3141 | 53.7391 | -123.8092
1148.2812 | 123.7244 | -65.2725 | 58.2001 | 0.047088 | -0.030165 | -0.03045 | -0.055519 | -0.038627 | -0.03607 | 0.065477 | -0.019877 | -0.012872 | 0.0029154 | 0.14758 | 6.5515e-05 | -0.06305 | -0.003172 | -0.045036 | 0.033814 | -0.04543 | 0.11907 | -0.15006 | -64.9388 | -14.0242 | -64.6207 | 58.1398 | 58.2535 | 58.2476 | -65.5634 | 65.1225 | -58.1663 | 65.2095 | 65.2275 | 0.10502 | -58.2455 | -58.081 | -0.29087 | -0.060246 | 0.33373 | 0.65178 | 0.94266 | 0.053458 | 0.047502 | 65.3063 | 65.2271 | 65.3916 | 65.2693 | -58.3501 | 123.4123 | 123.5261 | 123.5201 | 51.2483 | -123.7635
1149.2812 | 123.6969 | -65.3778 | 58.1497 | 0.047088 | -0.030165 | -0.031518 | -0.054451 | -0.037559 | -0.032865 | 0.050216 | -0.020945 | -0.015009 | 0.0018474 | 0.14972 | 6.5515e-05 | -0.072207 | -0.003172 | -0.045036 | -0.025705 | -0.036272 | 0.11907 | -0.049321 | -65.0075 | -14.4775 | -64.7352 | 58.0666 | 58.1803 | 58.1331 | -65.6412 | 65.3285 | -58.1754 | 65.3056 | 65.3328 | 0.004285 | -58.186 | -58.0306 | -0.26343 | -0.083148 | 0.37033 | 0.6426 | 0.90603 | 0.030554 | -0.016609 | 65.3521 | 65.3415 | 65.4969 | 65.3746 | -58.199 | 123.4444 | 123.5581 | 123.5109 | 50.9003 | -123.791
1150.2812 | 123.6557 | -65.3549 | 58.1909 | 0.047088 | -0.031234 | -0.028313 | -0.056588 | -0.037559 | -0.032865 | 0.034955 | -0.019877 | -0.01394 | 0.00077942 | 0.14758 | -0.0010025 | -0.06305 | -0.016908 | -0.045036 | 0.015501 | -0.059167 | 0.09618 | -0.085952 | -64.9892 | -14.5874 | -64.6848 | 58.094 | 58.2077 | 58.1468 | -65.6138 | 65.269 | -58.1754 | 65.2919 | 65.3099 | 0.040916 | -58.2501 | -58.0947 | -0.25884 | -0.096876 | 0.36576 | 0.67008 | 0.92892 | 0.016827 | -0.044073 | 65.3704 | 65.2958 | 65.4511 | 65.338 | -58.2769 | 123.449 | 123.5627 | 123.5018 | 50.7675 | -123.8047
1151.2656 | 123.6603 | -65.3549 | 58.2001 | 0.06235 | -0.030165 | -0.03045 | -0.054451 | -0.037559 | -0.033933 | 0.065477 | -0.019877 | -0.015009 | 0.0018474 | 0.14865 | 0.0011335 | -0.072207 | -0.016908 | -0.049614 | 0.024657 | -0.040851 | 0.10534 | -0.076794 | -64.98 | -14.3173 | -64.6665 | 58.1124 | 58.2261 | 58.0873 | -65.6046 | 65.2781 | -58.1754 | 65.2827 | 65.3053 | 0.02718 | -58.2409 | -58.0947 | -0.24968 | -0.087717 | 0.37492 | 0.68839 | 0.93808 | 0.025986 | -0.11275 | 65.3796 | 65.3141 | 65.4603 | 65.338 | -58.2769 | 123.4673 | 123.581 | 123.4422 | 51.0377 | -123.8047
1152.2656 | 123.7061 | -65.3366 | 58.2092 | 0.047088 | -0.031234 | -0.028313 | -0.053383 | -0.039695 | -0.033933 | 0.050216 | -0.022013 | -0.01394 | 0.00077942 | 0.14865 | 0.0011335 | -0.067628 | -0.007751 | -0.049614 | 0.020079 | -0.040851 | 0.091601 | -0.063057 | -64.9754 | -14.0929 | -64.6619 | 58.094 | 58.2123 | 58.1011 | -65.6092 | 65.2736 | -58.1891 | 65.269 | 65.287 | 0.013443 | -58.2501 | -58.1176 | -0.27257 | -0.11519 | 0.36118 | 0.67466 | 0.94724 | 0.003094 | -0.10817 | 65.3567 | 65.2958 | 65.4282 | 65.3289 | -58.2723 | 123.4307 | 123.5489 | 123.4377 | 51.2437 | -123.8184
1153.2812 | 123.6328 | -65.3778 | 58.168 | 0.031826 | -0.031234 | -0.027244 | -0.054451 | -0.038627 | -0.035002 | 0.065477 | -0.019877 | -0.012872 | 0.0018474 | 0.14865 | 6.5515e-05 | -0.067628 | -0.012329 | -0.045036 | 0.020079 | -0.059167 | 0.09618 | -0.044742 | -65.0166 | -14.1387 | -64.7306 | 58.0437 | 58.162 | 58.037 | -65.6641 | 65.3331 | -58.148 | 65.3102 | 65.3328 | -0.000294 | -58.2272 | -58.0719 | -0.28632 | -0.12435 | 0.36118 | 0.64718 | 0.9335 | -0.006072 | -0.13107 | 65.3979 | 65.3186 | 65.474 | 65.3655 | -58.2128 | 123.4215 | 123.5398 | 123.4148 | 51.2391 | -123.8322
1154.2656 | 123.674 | -65.332 | 58.2321 | 0.06235 | -0.030165 | -0.029381 | -0.054451 | -0.039695 | -0.032865 | 0.080738 | -0.020945 | -0.012872 | 0.00077942 | 0.15185 | 0.0011335 | -0.06305 | -0.007751 | -0.040457 | 0.024657 | -0.059167 | 0.077866 | -0.040163 | -64.9663 | -13.9235 | -64.6757 | 58.0986 | 58.2215 | 58.037 | -65.6046 | 65.2919 | -58.2075 | 65.269 | 65.2916 | -0.000294 | -58.2913 | -58.1543 | -0.27257 | -0.1335 | 0.36576 | 0.65635 | 0.92892 | -0.010637 | -0.19516 | 65.3567 | 65.2729 | 65.4099 | 65.3243 | -58.2723 | 123.4307 | 123.5535 | 123.369 | 51.4085 | -123.8367
1155.2812 | 123.6557 | -65.3824 | 58.1772 | 0.047088 | -0.034439 | -0.027244 | -0.055519 | -0.039695 | -0.037138 | 0.095999 | -0.023082 | -0.01394 | 0.00077942 | 0.14972 | 6.5515e-05 | -0.06305 | -0.007751 | -0.049614 | 0.020079 | -0.063746 | 0.091601 | -0.031005 | -65.0578 | -12.527 | -64.7398 | 58.0483 | 58.1711 | 57.9179 | -65.655 | 65.3514 | -58.1571 | 65.3193 | 65.3328 | -0.018609 | -58.2409 | -58.0856 | -0.27259 | -0.12893 | 0.32454 | 0.6426 | 0.91519 | -0.006069 | -0.25927 | 65.4025 | 65.3186 | 65.474 | 65.3746 | -58.2082 | 123.4306 | 123.5535 | 123.3003 | 52.8554 | -123.8322
1156.2656 | 123.7015 | -65.3183 | 58.1863 | 0.06235 | -0.032302 | -0.029381 | -0.056588 | -0.039695 | -0.03607 | 0.065477 | -0.020945 | -0.01394 | 0.00077942 | 0.14972 | 0.0011335 | -0.072207 | -0.012329 | -0.045036 | 0.010922 | -0.063746 | 0.11449 | 0.069732 | -65.0075 | -13.4336 | -64.6757 | 58.094 | 58.2169 | 57.9042 | -65.6092 | 65.388 | -58.1754 | 65.2461 | 65.2733 | -0.11477 | -58.2501 | -58.0718 | -0.29089 | -0.092298 | 0.31082 | 0.64261 | 0.9335 | 0.030562 | -0.28216 | 65.3292 | 65.2546 | 65.4328 | 65.306 | -58.1166 | 123.4123 | 123.5352 | 123.2225 | 51.8847 | -123.7955
1157.2812 | 123.6282 | -65.3275 | 58.2367 | 0.06235 | -0.032302 | -0.03045 | -0.054451 | -0.038627 | -0.03607 | 0.034955 | -0.020945 | -0.012872 | 0.0018474 | 0.14865 | 0.0011335 | -0.06305 | -0.003172 | -0.045036 | -0.002813 | -0.072904 | 0.068708 | 0.14757 | -64.9525 | -14.5233 | -64.6162 | 58.1261 | 58.2398 | 57.8676 | -65.5817 | 65.475 | -58.2395 | 65.2644 | 65.2824 | -0.19261 | -58.3096 | -58.168 | -0.25426 | -0.1106 | 0.37492 | 0.71129 | 0.96555 | 0.003101 | -0.36914 | 65.3246 | 65.2546 | 65.3962 | 65.3243 | -58.0891 | 123.4535 | 123.5672 | 123.195 | 50.8041 | -123.8184
1158.2812 | 123.6511 | -65.387 | 58.1635 | 0.047088 | -0.032302 | -0.027244 | -0.054451 | -0.038627 | -0.03607 | 0.050216 | -0.020945 | -0.011804 | 0.00077942 | 0.14972 | 6.5515e-05 | -0.06305 | -0.003172 | -0.045036 | 0.020079 | -0.086641 | 0.036658 | 0.11094 | -64.9983 | -14.1158 | -64.7215 | 58.0574 | 58.1803 | 57.8996 | -65.655 | 65.4979 | -58.1434 | 65.3239 | 65.3419 | -0.15598 | -58.2501 | -58.1268 | -0.26801 | -0.10604 | 0.38865 | 0.66549 | 0.9335 | 0.016821 | -0.26385 | 65.407 | 65.3003 | 65.4236 | 65.3838 | -58.0525 | 123.4444 | 123.5672 | 123.2866 | 51.2712 | -123.8184
1159.2656 | 123.674 | -65.4282 | 58.1177 | 0.016564 | -0.032302 | -0.03045 | -0.056588 | -0.038627 | -0.03607 | 0.050216 | -0.022013 | -0.012872 | 0.00077942 | 0.14972 | 6.5515e-05 | -0.067628 | -0.012329 | -0.045036 | 0.020079 | -0.082062 | 0.041237 | 0.14757 | -64.9983 | -11.7257 | -64.726 | 58.0391 | 58.1574 | 57.7851 | -65.6733 | 65.5757 | -58.0976 | 65.3605 | 65.3831 | -0.19261 | -58.1997 | -58.0764 | -0.24512 | -0.078576 | 0.42985 | 0.70211 | 0.94724 | 0.039704 | -0.33254 | 65.4482 | 65.3461 | 65.4694 | 65.4158 | -57.9701 | 123.4673 | 123.5855 | 123.2133 | 53.7024 | -123.791
1160.2812 | 123.6969 | -65.4282 | 58.1131 | 0.06235 | -0.031234 | -0.03045 | -0.056588 | -0.03649 | -0.035002 | 0.065477 | -0.018809 | -0.012872 | -0.00028958 | 0.14972 | 6.5515e-05 | -0.067628 | -0.012329 | -0.045036 | 0.029236 | -0.077483 | 0.009187 | 0.15673 | -65.0258 | -11.4281 | -64.7535 | 58.0025 | 58.1116 | 57.6798 | -65.7053 | 65.5849 | -58.0839 | 65.3605 | 65.3831 | -0.20177 | -58.1906 | -58.1039 | -0.27718 | -0.11063 | 0.40237 | 0.67464 | 0.95182 | -0.001504 | -0.43327 | 65.4574 | 65.3507 | 65.4373 | 65.4158 | -57.9564 | 123.4306 | 123.5398 | 123.108 | 54.0001 | -123.8184
1161.2812 | 123.6877 | -65.4648 | 58.1085 | 0.047088 | -0.031234 | -0.031518 | -0.056588 | -0.037559 | -0.032865 | 0.050216 | -0.020945 | -0.012872 | 0.0018474 | 0.15079 | -0.0010025 | -0.06305 | -0.007751 | -0.045036 | 0.033814 | -0.086641 | -0.013707 | 0.15673 | -65.0716 | -11.5243 | -64.7673 | 57.9704 | 58.0795 | 57.5745 | -65.742 | 65.6215 | -58.0747 | 65.4017 | 65.4197 | -0.20177 | -58.1952 | -58.1222 | -0.27719 | -0.1381 | 0.39321 | 0.69753 | 0.97471 | -0.028977 | -0.534 | 65.4986 | 65.3781 | 65.4511 | 65.457 | -57.9518 | 123.4352 | 123.5443 | 123.0393 | 53.9405 | -123.8505
1162.2656 | 123.674 | -65.419 | 58.1177 | 0.06235 | -0.03337 | -0.028313 | -0.055519 | -0.038627 | -0.033933 | 0.065477 | -0.020945 | -0.012872 | 0.00077942 | 0.14865 | -0.0020715 | -0.067628 | -0.007751 | -0.045036 | 0.020079 | -0.082062 | 0.018344 | 0.15673 | -65.0533 | -10.2514 | -64.7673 | 57.9842 | 58.0887 | 57.602 | -65.7282 | 65.5757 | -58.0976 | 65.3514 | 65.374 | -0.20177 | -58.1997 | -58.0993 | -0.30923 | -0.13352 | 0.36574 | 0.65175 | 0.96098 | -0.028975 | -0.51568 | 65.4391 | 65.3369 | 65.4373 | 65.4113 | -57.9609 | 123.4032 | 123.5077 | 123.021 | 55.1676 | -123.8459
1163.2812 | 123.6282 | -65.419 | 58.1177 | 0.06235 | -0.034439 | -0.029381 | -0.054451 | -0.039695 | -0.035002 | 0.065477 | -0.018809 | -0.01394 | -0.00028958 | 0.14972 | -0.0010025 | -0.06305 | -0.012329 | -0.040457 | 0.024657 | -0.086641 | -0.009128 | 0.15215 | -65.0166 | -11.0572 | -64.7169 | 58.0116 | 58.1345 | 57.6249 | -65.6916 | 65.5712 | -58.093 | 65.356 | 65.3785 | -0.19261 | -58.2043 | -58.1268 | -0.2726 | -0.10605 | 0.40237 | 0.70211 | 0.97471 | 0.016811 | -0.49279 | 65.4437 | 65.3324 | 65.4099 | 65.4067 | -57.9655 | 123.4306 | 123.5535 | 123.0439 | 54.3618 | -123.8093
1164.2656 | 123.6557 | -65.4327 | 58.1451 | 0.077612 | -0.031234 | -0.03045 | -0.053383 | -0.037559 | -0.031797 | 0.065477 | -0.020945 | -0.011804 | 0.0018474 | 0.14972 | 0.0011335 | -0.058472 | -0.012329 | -0.040457 | 0.024657 | -0.082062 | -0.018285 | 0.16589 | -65.0121 | -10.4162 | -64.7123 | 58.0025 | 58.1208 | 57.6203 | -65.7099 | 65.5986 | -58.1205 | 65.3743 | 65.3923 | -0.20635 | -58.2272 | -58.1634 | -0.27718 | -0.14267 | 0.42068 | 0.72043 | 0.9976 | -0.024391 | -0.52484 | 65.4574 | 65.3507 | 65.4145 | 65.4204 | -57.9793 | 123.4352 | 123.5535 | 123.053 | 55.0165 | -123.8551
1165.2812 | 123.6465 | -65.4236 | 58.0994 | 0.047088 | -0.031234 | -0.03045 | -0.055519 | -0.037559 | -0.035002 | 0.050216 | -0.022013 | -0.012872 | 0.0018474 | 0.14972 | 0.0011335 | -0.06305 | -0.007751 | -0.040457 | -0.002813 | -0.072904 | 0.013765 | 0.16131 | -64.9892 | -10.375 | -64.6711 | 58.0162 | 58.1345 | 57.7119 | -65.6962 | 65.5849 | -58.1022 | 65.3605 | 65.3831 | -0.20177 | -58.1723 | -58.0856 | -0.2726 | -0.083157 | 0.43442 | 0.75248 | 1.0251 | 0.035122 | -0.38749 | 65.4208 | 65.3507 | 65.4373 | 65.4158 | -57.9381 | 123.4398 | 123.5581 | 123.1355 | 55.0486 | -123.7955
1166.2812 | 123.7015 | -65.4144 | 58.0948 | 0.047088 | -0.031234 | -0.032586 | -0.054451 | -0.038627 | -0.035002 | 0.065477 | -0.020945 | -0.01394 | 0.00077942 | 0.14865 | 6.5515e-05 | -0.058472 | -0.007751 | -0.049614 | 0.024657 | -0.082062 | -0.013707 | 0.16131 | -65.0075 | -10.7825 | -64.6894 | 57.9933 | 58.1208 | 57.6066 | -65.7099 | 65.5757 | -58.0701 | 65.356 | 65.3648 | -0.21092 | -58.1769 | -58.1085 | -0.29549 | -0.10147 | 0.40695 | 0.72501 | 1.0205 | 0.025963 | -0.48822 | 65.4391 | 65.3324 | 65.4007 | 65.4067 | -57.9335 | 123.4077 | 123.5352 | 123.021 | 54.6319 | -123.8047
1167.2656 | 123.7061 | -65.3824 | 58.1451 | 0.047088 | -0.03337 | -0.029381 | -0.056588 | -0.037559 | -0.035002 | 0.050216 | -0.020945 | -0.01394 | 0.00077942 | 0.14972 | -0.0010025 | -0.06305 | -0.007751 | -0.040457 | 0.033814 | -0.082062 | -0.004549 | 0.16589 | -64.9846 | -10.6451 | -64.6528 | 58.0254 | 58.1436 | 57.6569 | -65.6824 | 65.5483 | -58.1113 | 65.3193 | 65.3419 | -0.20635 | -58.2272 | -58.1497 | -0.30006 | -0.11978 | 0.3978 | 0.7296 | 1.0297 | -0.001498 | -0.48821 | 65.4162 | 65.3003 | 65.3778 | 65.3746 | -57.9793 | 123.4077 | 123.526 | 123.0393 | 54.7372 | -123.8276
1168.2812 | 123.6877 | -65.3824 | 58.1543 | 0.06235 | -0.032302 | -0.03045 | -0.055519 | -0.039695 | -0.033933 | 0.050216 | -0.020945 | -0.01394 | 0.00077942 | 0.15079 | 6.5515e-05 | -0.06305 | -0.007751 | -0.040457 | 0.024657 | -0.077483 | 0.022922 | 0.15673 | -64.948 | -10.5444 | -64.6391 | 58.0483 | 58.1711 | 57.6981 | -65.6504 | 65.5391 | -58.1296 | 65.3193 | 65.3419 | -0.19719 | -58.2318 | -58.1314 | -0.26801 | -0.10604 | 0.43443 | 0.74333 | 1.0113 | 0.016819 | -0.45616 | 65.407 | 65.3049 | 65.4053 | 65.3746 | -57.9976 | 123.4306 | 123.5535 | 123.0805 | 54.838 | -123.8047
1169.2812 | 123.6603 | -65.4099 | 58.1451 | 0.047088 | -0.03337 | -0.03045 | -0.055519 | -0.037559 | -0.035002 | 0.065477 | -0.022013 | -0.01394 | 0.00077942 | 0.15185 | -0.0010025 | -0.053893 | -0.007751 | -0.040457 | 0.029236 | -0.082062 | 0.041237 | 0.14757 | -64.9892 | -10.6131 | -64.6665 | 58.0254 | 58.1345 | 57.6981 | -65.687 | 65.5574 | -58.1159 | 65.356 | 65.3694 | -0.18803 | -58.2272 | -58.1039 | -0.27717 | -0.11978 | 0.42069 | 0.74332 | 1.0205 | -0.010655 | -0.447 | 65.4391 | 65.3278 | 65.4511 | 65.4021 | -57.9976 | 123.4352 | 123.5443 | 123.108 | 54.7968 | -123.8322
1170.2812 | 123.6374 | -65.4694 | 58.0811 | 0.031826 | -0.03337 | -0.03045 | -0.055519 | -0.037559 | -0.033933 | 0.080738 | -0.018809 | -0.01394 | 0.0018474 | 0.15185 | 6.5515e-05 | -0.067628 | -0.003172 | -0.040457 | 0.029236 | -0.082062 | 0.03208 | 0.15673 | -65.0716 | -9.0884 | -64.7489 | 57.9475 | 58.0658 | 57.5791 | -65.7694 | 65.6261 | -58.0518 | 65.4017 | 65.4289 | -0.19719 | -58.1631 | -58.049 | -0.30008 | -0.13352 | 0.39778 | 0.72042 | 1.0205 | -0.015247 | -0.50196 | 65.4986 | 65.3873 | 65.5014 | 65.4662 | -57.9243 | 123.4169 | 123.5352 | 123.0485 | 56.381 | -123.8505
1171.2812 | 123.6603 | -65.4739 | 58.0719 | 0.077612 | -0.03337 | -0.027244 | -0.054451 | -0.037559 | -0.035002 | 0.050216 | -0.019877 | -0.012872 | 0.00077942 | 0.15185 | -0.0010025 | -0.058472 | -0.007751 | -0.045036 | 0.033814 | -0.082062 | -0.018285 | 0.16131 | -65.0762 | -10.0774 | -64.7673 | 57.9384 | 58.0475 | 57.5516 | -65.7832 | 65.6352 | -58.0381 | 65.4155 | 65.4289 | -0.20635 | -58.154 | -58.0902 | -0.30924 | -0.13353 | 0.39778 | 0.70668 | 1.0159 | -0.024406 | -0.52027 | 65.5078 | 65.3919 | 65.4557 | 65.4662 | -57.9106 | 123.4123 | 123.5214 | 123.0256 | 55.3966 | -123.8551
1172.2656 | 123.7747 | -65.4007 | 58.0673 | 0.031826 | -0.03337 | -0.03045 | -0.055519 | -0.037559 | -0.03607 | 0.065477 | -0.020945 | -0.012872 | 0.0029154 | 0.14972 | 6.5515e-05 | -0.06305 | -0.003172 | -0.040457 | 0.024657 | -0.082062 | 0.050394 | 0.15215 | -65.0212 | -9.592 | -64.6436 | 57.9842 | 58.107 | 57.6386 | -65.7191 | 65.5528 | -58.0427 | 65.3376 | 65.3602 | -0.19261 | -58.1494 | -58.0169 | -0.31838 | -0.083164 | 0.37949 | 0.75706 | 1.0754 | 0.039693 | -0.4287 | 65.4254 | 65.3186 | 65.4511 | 65.3975 | -57.9152 | 123.3849 | 123.5077 | 123.0393 | 55.8087 | -123.7864
1173.2812 | 123.7839 | -65.451 | 57.9941 | 0.077612 | -0.032302 | -0.031518 | -0.056588 | -0.038627 | -0.032865 | 0.050216 | -0.020945 | -0.012872 | 0.0018474 | 0.15079 | -0.0020715 | -0.06305 | -0.007751 | -0.040457 | 0.015501 | -0.082062 | 2.9e-05 | 0.16589 | -65.0624 | -9.4272 | -64.7581 | 57.9521 | 58.0704 | 57.6615 | -65.7649 | 65.6169 | -57.9786 | 65.388 | 65.4106 | -0.20635 | -58.0761 | -57.9941 | -0.31381 | -0.041971 | 0.38863 | 0.69295 | 1.0068 | 0.076306 | -0.33257 | 65.4666 | 65.369 | 65.4511 | 65.4433 | -57.8282 | 123.4032 | 123.5214 | 123.1126 | 56.0238 | -123.7589
1174.2812 | 123.6694 | -65.4144 | 58.1314 | 0.06235 | -0.032302 | -0.03045 | -0.055519 | -0.037559 | -0.033933 | 0.080738 | -0.020945 | -0.016077 | -0.00028958 | 0.15185 | 6.5515e-05 | -0.058472 | -0.012329 | -0.045036 | 0.024657 | -0.082062 | 0.018344 | 0.16589 | -65.0258 | -9.3768 | -64.7306 | 57.9842 | 58.0979 | 57.5974 | -65.7328 | 65.5803 | -58.1068 | 65.356 | 65.3694 | -0.21093 | -58.2135 | -58.1131 | -0.31838 | -0.14725 | 0.38864 | 0.6838 | 1.0022 | -0.033551 | -0.534 | 65.4391 | 65.3324 | 65.4328 | 65.4021 | -57.9655 | 123.3986 | 123.5123 | 123.0118 | 56.0376 | -123.8642
1175.2812 | 123.7564 | -65.419 | 58.0353 | 0.047088 | -0.034439 | -0.03045 | -0.055519 | -0.038627 | -0.035002 | 0.080738 | -0.022013 | -0.012872 | 0.0029154 | 0.15079 | -0.0010025 | -0.067628 | -0.007751 | -0.045036 | 0.024657 | -0.082062 | 0.009187 | 0.16131 | -65.0304 | -9.0151 | -64.7581 | 57.9567 | 58.0841 | 57.6569 | -65.7557 | 65.5803 | -58.0106 | 65.3514 | 65.374 | -0.20635 | -58.1173 | -58.0261 | -0.3367 | -0.078591 | 0.38864 | 0.66091 | 0.99761 | 0.048844 | -0.37834 | 65.4437 | 65.3369 | 65.4282 | 65.4113 | -57.874 | 123.3757 | 123.5031 | 123.0759 | 56.4039 | -123.791
1176.2656 | 123.7885 | -65.4373 | 58.017 | 0.047088 | -0.035507 | -0.029381 | -0.055519 | -0.037559 | -0.033933 | 0.065477 | -0.019877 | -0.015009 | 0.0018474 | 0.15185 | -0.0020715 | -0.06305 | -0.003172 | -0.040457 | 0.015501 | -0.077483 | -0.032021 | 0.17047 | -65.0533 | -8.4657 | -64.7856 | 57.9384 | 58.0658 | 57.5791 | -65.7694 | 65.6078 | -58.0015 | 65.3743 | 65.3969 | -0.21093 | -58.0945 | -58.049 | -0.33213 | -0.078595 | 0.38405 | 0.65174 | 0.98387 | 0.04884 | -0.43787 | 65.4528 | 65.3598 | 65.4053 | 65.4341 | -57.8465 | 123.3757 | 123.5031 | 123.0164 | 56.9716 | -123.7864
1177.2812 | 123.7015 | -65.4099 | 58.1223 | 0.092874 | -0.035507 | -0.032586 | -0.055519 | -0.038627 | -0.035002 | 0.050216 | -0.019877 | -0.012872 | 0.00077942 | 0.15185 | 6.5515e-05 | -0.067628 | -0.003172 | -0.045036 | 0.029236 | -0.082062 | -0.022864 | 0.16131 | -65.0166 | -8.7496 | -64.7398 | 57.9704 | 58.0933 | 57.5928 | -65.742 | 65.5712 | -58.093 | 65.3422 | 65.3648 | -0.20635 | -58.2043 | -58.1451 | -0.33212 | -0.15183 | 0.39322 | 0.67007 | 1.0022 | -0.028974 | -0.52942 | 65.4391 | 65.3278 | 65.387 | 65.4067 | -57.9609 | 123.3803 | 123.5031 | 123.0027 | 56.6603 | -123.8642
1178.2812 | 123.6877 | -65.4694 | 58.0536 | 0.06235 | -0.036576 | -0.031518 | -0.056588 | -0.037559 | -0.033933 | 0.080738 | -0.019877 | -0.01394 | 0.0018474 | 0.15185 | 6.5515e-05 | -0.06305 | -0.012329 | -0.040457 | 0.006344 | -0.077483 | 0.022922 | 0.16131 | -65.0029 | -9.3265 | -64.694 | 57.9979 | 58.1208 | 57.7073 | -65.7191 | 65.6307 | -58.0472 | 65.4063 | 65.4289 | -0.20177 | -58.1311 | -58.0307 | -0.24972 | -0.055695 | 0.46646 | 0.77536 | 1.0251 | 0.067162 | -0.34629 | 65.4757 | 65.3919 | 65.4923 | 65.457 | -57.8923 | 123.4673 | 123.5901 | 123.1767 | 56.1429 | -123.7727
1179.2656 | 123.7198 | -65.4602 | 58.0811 | 0.077612 | -0.037644 | -0.028313 | -0.054451 | -0.03649 | -0.033933 | 0.065477 | -0.019877 | -0.01394 | -0.00028958 | 0.15079 | -0.0010025 | -0.06305 | -0.007751 | -0.040457 | 0.015501 | -0.086641 | 0.036658 | 0.15215 | -65.0212 | -9.9034 | -64.7398 | 57.9613 | 58.0795 | 57.5974 | -65.7465 | 65.6124 | -58.0656 | 65.3972 | 65.4197 | -0.19261 | -58.1677 | -58.0444 | -0.28634 | -0.11979 | 0.43899 | 0.72042 | 1.0068 | -0.001511 | -0.48364 | 65.4757 | 65.3736 | 65.4969 | 65.4525 | -57.9289 | 123.4215 | 123.5397 | 123.0576 | 55.5568 | -123.8276
1180.2812 | 123.6969 | -65.4236 | 58.0765 | 0.077612 | -0.036576 | -0.03045 | -0.054451 | -0.037559 | -0.033933 | 0.050216 | -0.019877 | -0.01394 | -0.00028958 | 0.15079 | -0.0010025 | -0.067628 | -0.016908 | -0.040457 | 0.029236 | -0.082062 | 0.009187 | 0.16131 | -65.0258 | -10.4254 | -64.7306 | 57.9658 | 58.075 | 57.5745 | -65.7465 | 65.5849 | -58.0472 | 65.356 | 65.3831 | -0.20177 | -58.1585 | -58.0673 | -0.32296 | -0.11063 | 0.39779 | 0.69296 | 1.0159 | -0.001512 | -0.50196 | 65.4528 | 65.3415 | 65.4328 | 65.4067 | -57.9152 | 123.3894 | 123.4985 | 122.9981 | 54.9982 | -123.823
1181.2812 | 123.7381 | -65.451 | 58.0627 | 0.047088 | -0.034439 | -0.031518 | -0.055519 | -0.03649 | -0.035002 | 0.065477 | -0.023082 | -0.01394 | -0.00028958 | 0.15079 | 0.0011335 | -0.06305 | -0.007751 | -0.045036 | -0.002813 | -0.082062 | 0.013765 | 0.16131 | -65.0166 | -11.4006 | -64.7535 | 57.9796 | 58.0933 | 57.6981 | -65.7465 | 65.6124 | -58.0656 | 65.388 | 65.406 | -0.20635 | -58.1448 | -58.049 | -0.2955 | -0.083164 | 0.43442 | 0.69753 | 0.99303 | 0.030535 | -0.3646 | 65.4482 | 65.369 | 65.4648 | 65.4433 | -57.9014 | 123.4306 | 123.5443 | 123.1492 | 54.0504 | -123.8093
1182.2812 | 123.7839 | -65.4556 | 58.0536 | 0.077612 | -0.035507 | -0.03045 | -0.057656 | -0.037559 | -0.03607 | 0.050216 | -0.018809 | -0.012872 | 0.0018474 | 0.15185 | 6.5515e-05 | -0.06305 | -0.012329 | -0.035879 | 0.006344 | -0.082062 | 0.018344 | 0.15673 | -65.0441 | -11.1076 | -64.7764 | 57.9475 | 58.0704 | 57.6249 | -65.7694 | 65.6124 | -58.0472 | 65.3926 | 65.4197 | -0.19261 | -58.1357 | -58.0352 | -0.31381 | -0.10606 | 0.41152 | 0.67921 | 0.99303 | 0.016797 | -0.4287 | 65.462 | 65.3736 | 65.474 | 65.4433 | -57.8969 | 123.4032 | 123.526 | 123.0805 | 54.348 | -123.823
1183.2812 | 123.6969 | -65.4877 | 58.049 | 0.031826 | -0.034439 | -0.03045 | -0.055519 | -0.039695 | -0.035002 | 0.034955 | -0.022013 | -0.012872 | 0.00077942 | 0.15079 | -0.0020715 | -0.067628 | -0.003172 | -0.040457 | 0.024657 | -0.086641 | 0.022922 | 0.16131 | -65.0258 | -11.4006 | -64.7489 | 57.975 | 58.0933 | 57.6752 | -65.742 | 65.649 | -58.0244 | 65.42 | 65.4472 | -0.20177 | -58.1357 | -58.0261 | -0.2543 | -0.07401 | 0.46188 | 0.73873 | 0.99303 | 0.044268 | -0.37376 | 65.5123 | 65.401 | 65.5106 | 65.4845 | -57.8877 | 123.4627 | 123.581 | 123.1629 | 54.087 | -123.791
1184.2656 | 123.7335 | -65.4465 | 58.0353 | 0.047088 | -0.035507 | -0.03045 | -0.055519 | -0.038627 | -0.033933 | 0.095999 | -0.020945 | -0.01394 | 0.0018474 | 0.15185 | 0.0011335 | -0.067628 | -0.012329 | -0.040457 | 0.024657 | -0.09122 | 0.018344 | 0.15215 | -65.0441 | -12.2019 | -64.7856 | 57.9567 | 58.0795 | 57.5654 | -65.7649 | 65.5986 | -58.0106 | 65.3788 | 65.406 | -0.19261 | -58.1265 | -58.0169 | -0.31839 | -0.078591 | 0.40237 | 0.6609 | 0.97929 | 0.044266 | -0.46992 | 65.4711 | 65.3553 | 65.4648 | 65.4341 | -57.8831 | 123.4032 | 123.526 | 123.0118 | 53.2446 | -123.8001
1185.2812 | 123.6465 | -65.3778 | 58.1818 | 0.077612 | -0.035507 | -0.029381 | -0.056588 | -0.03649 | -0.035002 | 0.065477 | -0.022013 | -0.01394 | 0.00077942 | 0.15292 | -0.0010025 | -0.06305 | 0.001407 | -0.035879 | 0.020079 | -0.086641 | 0.022922 | 0.16131 | -64.9754 | -11.9547 | -64.7169 | 58.0254 | 58.1436 | 57.6295 | -65.6962 | 65.5391 | -58.1617 | 65.3148 | 65.3419 | -0.19719 | -58.2684 | -58.1588 | -0.31837 | -0.1564 | 0.40238 | 0.66092 | 0.97929 | -0.038119 | -0.5523 | 65.3979 | 65.2912 | 65.4007 | 65.3792 | -58.0205 | 123.4032 | 123.5215 | 123.0073 | 53.4232 | -123.8779
1186.2656 | 123.7564 | -65.387 | 58.0856 | 0.077612 | -0.035507 | -0.031518 | -0.056588 | -0.035422 | -0.032865 | 0.080738 | -0.020945 | -0.012872 | 0.00077942 | 0.15292 | -0.0010025 | -0.067628 | -0.007751 | -0.035879 | 0.020079 | -0.086641 | 0.018344 | 0.14757 | -64.9892 | -11.744 | -64.7444 | 57.9979 | 58.1162 | 57.634 | -65.7191 | 65.5345 | -58.0656 | 65.3193 | 65.3511 | -0.18345 | -58.1723 | -58.0673 | -0.33211 | -0.087738 | 0.3978 | 0.6426 | 0.97471 | 0.03054 | -0.45159 | 65.407 | 65.3003 | 65.4053 | 65.3792 | -57.9381 | 123.3849 | 123.5031 | 123.021 | 53.6429 | -123.8047
1187.2656 | 123.8159 | -65.3412 | 58.1406 | 0.06235 | -0.034439 | -0.028313 | -0.057656 | -0.038627 | -0.033933 | 0.050216 | -0.020945 | -0.01394 | 0.0018474 | 0.15079 | 6.5515e-05 | -0.06305 | -0.003172 | -0.040457 | 0.015501 | -0.086641 | -0.009128 | 0.15673 | -64.9296 | -12.1561 | -64.726 | 58.0345 | 58.1528 | 57.6661 | -65.687 | 65.4979 | -58.1251 | 65.2781 | 65.3007 | -0.19719 | -58.2272 | -58.1497 | -0.34584 | -0.10604 | 0.41155 | 0.61514 | 0.96097 | 0.012237 | -0.47447 | 65.3567 | 65.2545 | 65.3321 | 65.338 | -57.9838 | 123.3757 | 123.494 | 123.0073 | 53.1851 | -123.8276
1188.2812 | 123.674 | -65.4236 | 58.0765 | 0.031826 | -0.035507 | -0.031518 | -0.055519 | -0.037559 | -0.035002 | 0.019694 | -0.022013 | -0.01394 | 0.00077942 | 0.15399 | 6.5515e-05 | -0.058472 | 0.001407 | -0.035879 | 0.020079 | -0.086641 | 0.03208 | 0.15673 | -64.9663 | -12.4537 | -64.6986 | 57.9842 | 58.1116 | 57.6981 | -65.7282 | 65.5803 | -58.0564 | 65.3651 | 65.3877 | -0.19261 | -58.1631 | -58.0444 | -0.30465 | -0.092319 | 0.45732 | 0.72501 | 1.0297 | 0.035117 | -0.37833 | 65.4437 | 65.3369 | 65.4557 | 65.425 | -57.9197 | 123.4077 | 123.5352 | 123.1217 | 52.9699 | -123.8047
1189.2812 | 123.8022 | -65.4236 | 58.0582 | 0.06235 | -0.036576 | -0.031518 | -0.057656 | -0.038627 | -0.03607 | 0.050216 | -0.022013 | -0.01394 | -0.0013576 | 0.15399 | -0.0020715 | -0.058472 | -0.007751 | -0.035879 | 0.033814 | -0.082062 | 0.036658 | 0.15673 | -64.9892 | -12.0462 | -64.7169 | 57.9704 | 58.0979 | 57.5883 | -65.742 | 65.5803 | -58.0244 | 65.3651 | 65.3877 | -0.19261 | -58.1402 | -58.0215 | -0.31838 | -0.087744 | 0.43442 | 0.70669 | 1.0251 | 0.039691 | -0.46991 | 65.4574 | 65.3415 | 65.4602 | 65.4158 | -57.9014 | 123.394 | 123.5214 | 123.0118 | 53.3774 | -123.8001
1190.2812 | 123.7473 | -65.4556 | 58.0307 | 0.06235 | -0.035507 | -0.029381 | -0.057656 | -0.038627 | -0.03607 | 0.050216 | -0.020945 | -0.012872 | -0.00028958 | 0.15292 | 6.5515e-05 | -0.058472 | -0.012329 | -0.035879 | 0.033814 | -0.09122 | 0.009187 | 0.15673 | -65.0121 | -12.8155 | -64.6482 | 57.9567 | 58.075 | 57.5699 | -65.7603 | 65.6124 | -57.9969 | 65.3972 | 65.4197 | -0.19261 | -58.1219 | -58.0215 | -0.30466 | -0.074014 | 0.44357 | 0.80742 | 1.1121 | 0.044264 | -0.46076 | 65.4894 | 65.3644 | 65.4648 | 65.4433 | -57.874 | 123.4123 | 123.5306 | 123.0256 | 52.6402 | -123.791
1191.2812 | 123.793 | -65.3961 | 58.0536 | 0.06235 | -0.036576 | -0.031518 | -0.056588 | -0.037559 | -0.035002 | 0.065477 | -0.019877 | -0.015009 | -0.00028958 | 0.15185 | -0.0010025 | -0.06305 | -0.007751 | -0.045036 | 0.029236 | -0.086641 | 0.050394 | 0.16131 | -64.9937 | -13.0764 | -64.607 | 57.9613 | 58.0887 | 57.6066 | -65.7557 | 65.5574 | -58.0244 | 65.3331 | 65.3511 | -0.20635 | -58.1402 | -58.0032 | -0.35959 | -0.092323 | 0.40238 | 0.78911 | 1.1487 | 0.035112 | -0.44702 | 65.4254 | 65.3095 | 65.4465 | 65.3884 | -57.8923 | 123.3574 | 123.4848 | 123.0027 | 52.3197 | -123.8093
1192.2656 | 123.7289 | -65.4327 | 58.0627 | 0.031826 | -0.035507 | -0.029381 | -0.057656 | -0.038627 | -0.032865 | 0.065477 | -0.019877 | -0.01394 | 0.00077942 | 0.15292 | -0.0010025 | -0.058472 | -0.007751 | -0.045036 | 0.024657 | -0.086641 | 0.022922 | 0.15215 | -64.9846 | -11.7349 | -64.5704 | 57.975 | 58.1116 | 57.6707 | -65.7328 | 65.5849 | -58.0381 | 65.3743 | 65.3877 | -0.19719 | -58.1494 | -58.0398 | -0.30007 | -0.087743 | 0.44816 | 0.86237 | 1.1624 | 0.04885 | -0.39207 | 65.4574 | 65.3461 | 65.4557 | 65.425 | -57.9106 | 123.4077 | 123.5443 | 123.1034 | 53.6979 | -123.7956
1193.2812 | 123.6969 | -65.5609 | 58.0261 | 0.047088 | -0.035507 | -0.032586 | -0.058725 | -0.037559 | -0.033933 | 0.034955 | -0.020945 | -0.015009 | -0.00028958 | 0.15506 | 6.5515e-05 | -0.072207 | 0.001407 | -0.031301 | 0.029236 | -0.086641 | 0.022922 | 0.15673 | -65.0487 | -11.4739 | -64.6391 | 57.9201 | 58.0383 | 57.5379 | -65.7923 | 65.7176 | -57.9969 | 65.4887 | 65.5296 | -0.18803 | -58.1128 | -58.0032 | -0.23142 | -0.10606 | 0.51223 | 0.92186 | 1.1533 | 0.012213 | -0.48823 | 65.5901 | 65.4743 | 65.5838 | 65.5623 | -57.8694 | 123.481 | 123.5992 | 123.0988 | 54.087 | -123.8185
1194.2656 | 123.7427 | -65.3503 | 58.1406 | 0.047088 | -0.035507 | -0.031518 | -0.057656 | -0.03649 | -0.03607 | 0.034955 | -0.019877 | -0.012872 | -0.00028958 | 0.15506 | -0.0020715 | -0.06305 | -0.003172 | -0.045036 | 0.024657 | -0.086641 | 0.054973 | 0.15673 | -64.9388 | -12.8567 | -64.5246 | 58.0437 | 58.1528 | 57.6936 | -65.6824 | 65.5071 | -58.1159 | 65.2873 | 65.3053 | -0.20177 | -58.2272 | -58.0856 | -0.3321 | -0.096885 | 0.41155 | 0.82576 | 1.1579 | 0.012237 | -0.447 | 65.375 | 65.2637 | 65.4053 | 65.3472 | -57.9838 | 123.394 | 123.5031 | 123.0439 | 52.4937 | -123.823
1195.2656 | 123.7976 | -65.3046 | 58.1451 | 0.06235 | -0.035507 | -0.031518 | -0.056588 | -0.038627 | -0.033933 | 0.065477 | -0.019877 | -0.01394 | 0.0018474 | 0.15185 | -0.0020715 | -0.058472 | -0.003172 | -0.040457 | 0.020079 | -0.086641 | 0.004608 | 0.15215 | -64.9113 | -12.8383 | -64.5063 | 58.0528 | 58.1711 | 57.689 | -65.6733 | 65.4567 | -58.1251 | 65.2461 | 65.2641 | -0.19261 | -58.2318 | -58.1405 | -0.36872 | -0.092306 | 0.39324 | 0.79829 | 1.167 | 0.025974 | -0.45616 | 65.3246 | 65.2179 | 65.3092 | 65.3014 | -57.993 | 123.3574 | 123.4757 | 122.9935 | 52.4662 | -123.8184
1196.2656 | 123.7152 | -65.3 | 58.2092 | 0.031826 | -0.037644 | -0.031518 | -0.057656 | -0.037559 | -0.037138 | 0.050216 | -0.020945 | -0.01394 | -0.00028958 | 0.15292 | -0.0010025 | -0.06305 | -0.003172 | -0.040457 | 0.006344 | -0.09122 | 0.009187 | 0.16131 | -64.8289 | -12.8292 | -64.3872 | 58.1581 | 58.281 | 57.8859 | -65.5634 | 65.4613 | -58.2029 | 65.2369 | 65.2595 | -0.20177 | -58.3004 | -58.2 | -0.26341 | -0.051088 | 0.47108 | 0.91276 | 1.1762 | 0.071773 | -0.32336 | 65.3063 | 65.2088 | 65.3092 | 65.2968 | -58.0479 | 123.4581 | 123.581 | 123.1859 | 52.4708 | -123.7726
1197.2656 | 123.7793 | -65.2313 | 58.2642 | 0.047088 | -0.036576 | -0.029381 | -0.057656 | -0.03649 | -0.03607 | 0.065477 | -0.020945 | -0.012872 | 0.00077942 | 0.15506 | -0.0010025 | -0.058472 | 0.001407 | -0.040457 | 0.020079 | -0.082062 | 0.050394 | 0.16131 | -64.7877 | -12.5499 | -64.3598 | 58.1856 | 58.2947 | 57.8172 | -65.5405 | 65.3926 | -58.2441 | 65.1729 | 65.1909 | -0.20177 | -58.3462 | -58.2138 | -0.30918 | -0.078548 | 0.44363 | 0.87157 | 1.1807 | 0.030578 | -0.44697 | 65.2514 | 65.1493 | 65.2817 | 65.2327 | -58.1028 | 123.4169 | 123.5261 | 123.0485 | 52.6814 | -123.8047
1198.2812 | 123.6923 | -65.2679 | 58.2733 | 0.077612 | -0.036576 | -0.03045 | -0.057656 | -0.037559 | -0.035002 | 0.050216 | -0.019877 | -0.015009 | 0.0018474 | 0.15506 | -0.0020715 | -0.053893 | -0.007751 | -0.031301 | 0.015501 | -0.086641 | 0.009187 | 0.16589 | -64.8243 | -8.745 | -64.4147 | 58.1536 | 58.281 | 57.7943 | -65.568 | 65.4338 | -58.2578 | 65.2141 | 65.2366 | -0.19719 | -58.36 | -58.2641 | -0.30003 | -0.11975 | 0.44362 | 0.85325 | 1.1533 | 0.007687 | -0.47902 | 65.2834 | 65.1813 | 65.2771 | 65.2602 | -58.1074 | 123.4215 | 123.5489 | 123.0622 | 56.523 | -123.8413
1199.2812 | 123.7793 | -65.1535 | 58.2916 | 0.06235 | -0.037644 | -0.031518 | -0.057656 | -0.037559 | -0.035002 | 0.050216 | -0.019877 | -0.01394 | 0.00077942 | 0.15506 | -0.0020715 | -0.06305 | -0.012329 | -0.035879 | 0.029236 | -0.086641 | 0.027501 | 0.14299 | -64.7694 | -9.7019 | -64.3781 | 58.2085 | 58.3222 | 57.8538 | -65.5176 | 65.2965 | -58.2624 | 65.0905 | 65.1176 | -0.17887 | -58.3783 | -58.2641 | -0.3641 | -0.083122 | 0.38412 | 0.77544 | 1.1395 | 0.030584 | -0.43781 | 65.1827 | 65.0669 | 65.181 | 65.1412 | -58.1486 | 123.362 | 123.4757 | 123.0073 | 55.4516 | -123.8092
1200.2812 | 123.7564 | -65.1581 | 58.3511 | 0.06235 | -0.035507 | -0.031518 | -0.056588 | -0.038627 | -0.035002 | 0.050216 | -0.020945 | -0.01394 | 0.00077942 | 0.15399 | -0.0031395 | -0.053893 | -0.012329 | -0.035879 | 0.033814 | -0.086641 | -0.009128 | 0.15215 | -64.7053 | -10.4986 | -64.2682 | 58.2589 | 58.3772 | 57.8676 | -65.4672 | 65.3102 | -58.3173 | 65.1042 | 65.1222 | -0.18803 | -58.4378 | -58.3603 | -0.30916 | -0.092267 | 0.4528 | 0.8899 | 1.1991 | 0.026018 | -0.48358 | 65.1919 | 65.0714 | 65.149 | 65.1458 | -58.199 | 123.4169 | 123.5352 | 123.0256 | 54.6595 | -123.8184
1201.2656 | 123.7289 | -65.1215 | 58.342 | 0.047088 | -0.035507 | -0.03045 | -0.056588 | -0.037559 | -0.033933 | 0.050216 | -0.019877 | -0.01394 | -0.0013576 | 0.15399 | -0.0010025 | -0.058472 | 0.001407 | -0.040457 | 0.006344 | -0.082062 | 0.045815 | 0.15215 | -64.6915 | -9.5188 | -64.2682 | 58.2772 | 58.3955 | 57.9637 | -65.4398 | 65.2736 | -58.3356 | 65.063 | 65.081 | -0.19261 | -58.424 | -58.2962 | -0.31831 | -0.064798 | 0.42992 | 0.85328 | 1.1716 | 0.053487 | -0.37828 | 65.1278 | 65.0394 | 65.1673 | 65.1229 | -58.1898 | 123.3986 | 123.5169 | 123.0852 | 55.6027 | -123.7817
1202.2656 | 123.7198 | -65.1901 | 58.3008 | 0.031826 | -0.035507 | -0.031518 | -0.056588 | -0.038627 | -0.035002 | 0.050216 | -0.019877 | -0.01394 | -0.00028958 | 0.15399 | -0.0020715 | -0.058472 | -0.003172 | -0.040457 | 0.029236 | -0.082062 | 0.018344 | 0.16131 | -64.7282 | -8.4016 | -64.3369 | 58.2268 | 58.3405 | 57.9042 | -65.4993 | 65.3514 | -58.2715 | 65.1317 | 65.1497 | -0.20177 | -58.3828 | -58.2824 | -0.30917 | -0.073963 | 0.46195 | 0.85327 | 1.1624 | 0.039743 | -0.3966 | 65.2194 | 65.1081 | 65.2085 | 65.187 | -58.1395 | 123.4169 | 123.5306 | 123.0943 | 56.7886 | -123.8001
1203.2812 | 123.7335 | -65.1901 | 58.3054 | 0.06235 | -0.037644 | -0.031518 | -0.057656 | -0.03649 | -0.035002 | 0.050216 | -0.020945 | -0.01394 | -0.00028958 | 0.15506 | -0.0020715 | -0.053893 | -0.003172 | -0.031301 | 0.029236 | -0.086641 | 0.018344 | 0.15673 | -64.719 | -8.0856 | -64.3231 | 58.2177 | 58.3314 | 57.8355 | -65.5084 | 65.3469 | -58.2761 | 65.1362 | 65.1588 | -0.18803 | -58.392 | -58.287 | -0.31832 | -0.087698 | 0.47111 | 0.867 | 1.1853 | 0.026008 | -0.46986 | 65.2194 | 65.1035 | 65.2085 | 65.187 | -58.1486 | 123.4078 | 123.5215 | 123.0256 | 57.1045 | -123.8138
1204.2656 | 123.674 | -65.2679 | 58.2825 | 0.047088 | -0.038712 | -0.03045 | -0.057656 | -0.037559 | -0.035002 | 0.050216 | -0.019877 | -0.015009 | -0.00028958 | 0.15399 | -0.0031395 | -0.058472 | -0.007751 | -0.040457 | 0.015501 | -0.086641 | 0.009187 | 0.16131 | -64.7556 | -7.8521 | -64.3506 | 58.1948 | 58.3039 | 57.8218 | -65.5313 | 65.4293 | -58.267 | 65.2095 | 65.2275 | -0.20177 | -58.3691 | -58.2733 | -0.2634 | -0.087702 | 0.5123 | 0.91735 | 1.1807 | 0.021424 | -0.46071 | 65.2834 | 65.1813 | 65.2771 | 65.2602 | -58.1212 | 123.4627 | 123.5718 | 123.0897 | 57.4158 | -123.8138
1205.2812 | 123.7839 | -65.2039 | 58.2275 | 0.047088 | -0.037644 | -0.031518 | -0.059793 | -0.037559 | -0.037138 | 0.050216 | -0.018809 | -0.01394 | -0.00028958 | 0.15506 | -0.0020715 | -0.053893 | 0.001407 | -0.040457 | 0.010922 | -0.086641 | 0.050394 | 0.16131 | -64.7556 | -7.527 | -64.5017 | 58.1902 | 58.3039 | 57.863 | -65.5451 | 65.3652 | -58.2166 | 65.15 | 65.1634 | -0.20177 | -58.3142 | -58.1771 | -0.34122 | -0.037349 | 0.44821 | 0.70216 | 1.0434 | 0.076356 | -0.36457 | 65.2148 | 65.1172 | 65.2543 | 65.2053 | -58.0662 | 123.394 | 123.5078 | 123.0668 | 57.6768 | -123.7726
1206.2812 | 123.793 | -65.2405 | 58.2321 | 0.047088 | -0.038712 | -0.029381 | -0.057656 | -0.03649 | -0.033933 | 0.065477 | -0.020945 | -0.012872 | 0.00077942 | 0.15613 | -0.0010025 | -0.053893 | -0.003172 | -0.040457 | 0.020079 | -0.086641 | 0.027501 | 0.16131 | -64.7877 | -7.701 | -64.5292 | 58.1673 | 58.2856 | 57.7943 | -65.5634 | 65.4018 | -58.212 | 65.1866 | 65.2 | -0.20177 | -58.3188 | -58.2046 | -0.32292 | -0.064819 | 0.45278 | 0.71131 | 1.0342 | 0.053464 | -0.43782 | 65.2606 | 65.1538 | 65.268 | 65.2373 | -58.0708 | 123.4078 | 123.5261 | 123.0348 | 57.5394 | -123.7955
1207.2812 | 123.7289 | -65.2679 | 58.2184 | 0.047088 | -0.037644 | -0.03045 | -0.057656 | -0.039695 | -0.035002 | 0.065477 | -0.020945 | -0.01394 | -0.00028958 | 0.15506 | -0.0020715 | -0.058472 | -0.003172 | -0.040457 | 0.001765 | -0.09122 | 0.009187 | 0.16131 | -64.7969 | -7.7606 | -64.3598 | 58.1581 | 58.2718 | 57.8447 | -65.568 | 65.4293 | -58.2166 | 65.2095 | 65.2275 | -0.20177 | -58.3096 | -58.2092 | -0.30003 | -0.060243 | 0.47109 | 0.90819 | 1.2082 | 0.053461 | -0.37373 | 65.2697 | 65.1767 | 65.2771 | 65.2648 | -58.0571 | 123.4261 | 123.5398 | 123.1126 | 57.5074 | -123.7864
1208.2656 | 123.7839 | -65.2496 | 58.2367 | 0.047088 | -0.036576 | -0.03045 | -0.056588 | -0.039695 | -0.035002 | 0.065477 | -0.020945 | -0.015009 | -0.00028958 | 0.15506 | -0.0031395 | -0.053893 | -0.012329 | -0.035879 | 0.029236 | -0.086641 | 0.022922 | 0.14757 | -64.8014 | -8.7908 | -64.346 | 58.1627 | 58.2947 | 57.7897 | -65.5542 | 65.3972 | -58.2075 | 65.1957 | 65.2138 | -0.18345 | -58.3233 | -58.2138 | -0.3046 | -0.073975 | 0.4482 | 0.90362 | 1.2082 | 0.058044 | -0.44698 | 65.2789 | 65.163 | 65.2726 | 65.2373 | -58.0891 | 123.4124 | 123.5444 | 123.0393 | 56.4589 | -123.7909
1209.2812 | 123.7061 | -65.2954 | 58.2458 | 0.047088 | -0.038712 | -0.03045 | -0.056588 | -0.038627 | -0.037138 | 0.034955 | -0.020945 | -0.012872 | -0.00028958 | 0.15613 | -0.0020715 | -0.053893 | 0.001407 | -0.031301 | 0.029236 | -0.086641 | 0.027501 | 0.15673 | -64.8289 | -8.4153 | -64.3918 | 58.1398 | 58.249 | 57.7439 | -65.5817 | 65.4521 | -58.2166 | 65.2415 | 65.2641 | -0.18803 | -58.3325 | -58.2183 | -0.2863 | -0.10602 | 0.4665 | 0.90361 | 1.1899 | 0.003102 | -0.50192 | 65.3246 | 65.2088 | 65.3229 | 65.2968 | -58.0891 | 123.4352 | 123.5444 | 123.0393 | 56.8801 | -123.8276
1210.2812 | 123.7244 | -65.2222 | 58.2779 | 0.031826 | -0.037644 | -0.031518 | -0.057656 | -0.037559 | -0.035002 | 0.050216 | -0.022013 | -0.01394 | -0.00028958 | 0.15506 | -0.0020715 | -0.053893 | 0.001407 | -0.031301 | 0.006344 | -0.086641 | 0.12365 | 0.092626 | -64.774 | -8.1452 | -64.3277 | 58.1993 | 58.3359 | 58.156 | -65.5222 | 65.3148 | -58.2715 | 65.1683 | 65.1909 | -0.12393 | -58.3645 | -58.1542 | -0.30002 | -0.078546 | 0.44821 | 0.89447 | 1.1945 | 0.058052 | -0.12189 | 65.2285 | 65.1355 | 65.3458 | 65.2236 | -58.1853 | 123.4215 | 123.5581 | 123.3782 | 57.077 | -123.8001
1211.2656 | 123.6328 | -65.2725 | 58.2733 | 0.031826 | -0.039781 | -0.031518 | -0.057656 | -0.037559 | -0.03607 | 0.050216 | -0.019877 | -0.015009 | -0.0013576 | 0.15399 | -0.0010025 | -0.058472 | 0.005985 | -0.026723 | 0.042971 | -0.077483 | 0.12823 | 0.07431 | -64.8289 | -7.5957 | -64.3643 | 58.1856 | 58.2993 | 58.1652 | -65.5451 | 65.3468 | -58.2303 | 65.2141 | 65.2458 | -0.10103 | -58.3508 | -58.1451 | -0.27256 | -0.087703 | 0.44362 | 0.90819 | 1.1807 | 0.026002 | -0.10815 | 65.3155 | 65.195 | 65.4008 | 65.2785 | -58.199 | 123.4581 | 123.5718 | 123.4377 | 57.6768 | -123.8184
1212.2656 | 123.642 | -65.2634 | 58.2825 | 0.047088 | -0.038712 | -0.03045 | -0.057656 | -0.038627 | -0.039275 | 0.050216 | -0.022013 | -0.01394 | -0.00028958 | 0.15613 | -0.0020715 | -0.053893 | 0.001407 | -0.031301 | 0.038393 | -0.068325 | 0.13281 | 0.010206 | -64.8381 | -7.9117 | -64.3689 | 58.1765 | 58.2993 | 58.156 | -65.5588 | 65.2736 | -58.2441 | 65.2095 | 65.2321 | -0.041507 | -58.3508 | -58.1497 | -0.29545 | -0.10602 | 0.4253 | 0.89446 | 1.1899 | 0.016846 | -0.12647 | 65.3018 | 65.195 | 65.3962 | 65.2648 | -58.2723 | 123.4398 | 123.5627 | 123.4194 | 57.3517 | -123.8413
1213.2812 | 123.7427 | -65.2084 | 58.2642 | 0.047088 | -0.039781 | -0.03045 | -0.056588 | -0.037559 | -0.040343 | 0.065477 | -0.020945 | -0.015009 | 0.00077942 | 0.15613 | -0.0031395 | -0.06305 | 0.005985 | -0.031301 | 0.029236 | -0.063746 | 0.12823 | 0.023942 | -64.8243 | -8.5572 | -64.3598 | 58.1765 | 58.3039 | 58.2201 | -65.5542 | 65.2324 | -58.2349 | 65.1454 | 65.1771 | -0.055243 | -58.3279 | -58.1359 | -0.3458 | -0.087705 | 0.38411 | 0.84868 | 1.1945 | 0.039735 | -0.044057 | 65.2377 | 65.1447 | 65.3367 | 65.2144 | -58.2402 | 123.3849 | 123.5123 | 123.4285 | 56.6512 | -123.8184
1214.2656 | 123.7885 | -65.2908 | 58.1909 | 0.06235 | -0.042986 | -0.03045 | -0.058725 | -0.039695 | -0.039275 | 0.065477 | -0.020945 | -0.016077 | 0.00077942 | 0.15613 | -0.0042075 | -0.053893 | 0.005985 | -0.031301 | 0.029236 | -0.063746 | 0.13739 | -0.031005 | -64.8381 | -7.7834 | -64.3781 | 58.1627 | 58.2856 | 58.2247 | -65.5726 | 65.2598 | -58.1617 | 65.2369 | 65.2595 | -0.000296 | -58.2547 | -58.0535 | -0.28172 | -0.028199 | 0.45277 | 0.91277 | 1.1945 | 0.094663 | 0.033764 | 65.3201 | 65.2271 | 65.4282 | 65.2968 | -58.2219 | 123.4536 | 123.5764 | 123.5155 | 57.5074 | -123.7635
1215.2812 | 123.7381 | -65.2679 | 58.2184 | 0.047088 | -0.044054 | -0.029381 | -0.056588 | -0.040764 | -0.040343 | 0.065477 | -0.023082 | -0.017145 | -0.0024256 | 0.1572 | -0.0031395 | -0.058472 | 0.005985 | -0.035879 | 0.010922 | -0.054588 | 0.12823 | -0.035584 | -64.8472 | -7.8063 | -64.3781 | 58.1581 | 58.2718 | 58.1377 | -65.568 | 65.2324 | -58.2075 | 65.2095 | 65.2321 | -0.000295 | -58.273 | -58.0902 | -0.30003 | -0.060243 | 0.42072 | 0.88988 | 1.1899 | 0.053461 | -0.080696 | 65.2789 | 65.2134 | 65.3962 | 65.2739 | -58.254 | 123.4261 | 123.5398 | 123.4056 | 57.4616 | -123.7864
1216.2656 | 123.7061 | -65.3183 | 58.2321 | 0.06235 | -0.042986 | -0.028313 | -0.057656 | -0.041832 | -0.040343 | 0.065477 | -0.023082 | -0.016077 | -0.0024256 | 0.15826 | -0.0031395 | -0.049315 | 0.010564 | -0.031301 | 0.006344 | -0.059167 | 0.13281 | -0.035584 | -64.8838 | -5.0225 | -64.4467 | 58.1124 | 58.2306 | 58.0599 | -65.6092 | 65.2827 | -58.2258 | 65.269 | 65.287 | 0.004283 | -58.2913 | -58.0993 | -0.29089 | -0.11976 | 0.43445 | 0.87155 | 1.1624 | -0.001479 | -0.17227 | 65.3246 | 65.2591 | 65.4511 | 65.3289 | -58.2677 | 123.4307 | 123.5489 | 123.3782 | 60.2958 | -123.8413
1217.2812 | 123.6557 | -65.3137 | 58.2413 | 0.031826 | -0.041917 | -0.032586 | -0.058725 | -0.040764 | -0.038207 | 0.095999 | -0.020945 | -0.01394 | -0.00028958 | 0.1572 | -0.0020715 | -0.053893 | -0.003172 | -0.035879 | 0.015501 | -0.054588 | 0.13281 | -0.040163 | -64.8518 | -7.9941 | -64.4422 | 58.149 | 58.2673 | 58.0553 | -65.5817 | 65.2736 | -58.2258 | 65.2598 | 65.2778 | 0.004284 | -58.2959 | -58.1085 | -0.26799 | -0.092288 | 0.46192 | 0.87155 | 1.1395 | 0.025994 | -0.186 | 65.3292 | 65.2591 | 65.4465 | 65.3105 | -58.2814 | 123.4627 | 123.581 | 123.369 | 57.3197 | -123.823
1218.2812 | 123.7015 | -65.332 | 58.223 | 0.016564 | -0.040849 | -0.031518 | -0.056588 | -0.039695 | -0.037138 | 0.080738 | -0.019877 | -0.015009 | -0.0024256 | 0.15826 | -0.0020715 | -0.053893 | -0.021486 | -0.026723 | 0.006344 | -0.04543 | 0.13281 | -0.040163 | -64.8197 | -7.7331 | -64.4925 | 58.1215 | 58.249 | 58.0827 | -65.5909 | 65.2919 | -58.2166 | 65.2781 | 65.3053 | 0.01344 | -58.2684 | -58.0902 | -0.25884 | -0.10145 | 0.51228 | 0.8395 | 1.0983 | 0.025991 | -0.14022 | 65.3384 | 65.2866 | 65.4648 | 65.3105 | -58.2631 | 123.4535 | 123.581 | 123.4148 | 57.5989 | -123.8138
1219.2812 | 123.7701 | -65.3183 | 58.1863 | 0.031826 | -0.038712 | -0.031518 | -0.058725 | -0.038627 | -0.035002 | 0.050216 | -0.019877 | -0.01394 | -0.0013576 | 0.15506 | -0.0020715 | -0.053893 | -0.012329 | -0.026723 | 0.001765 | -0.04543 | 0.11449 | -0.035584 | -64.8014 | -8.2917 | -64.4925 | 58.1261 | 58.2444 | 58.1102 | -65.6138 | 65.2827 | -58.1846 | 65.2644 | 65.2916 | 0.008861 | -58.2318 | -58.0718 | -0.29546 | -0.060248 | 0.51686 | 0.82576 | 1.1212 | 0.058033 | -0.076123 | 65.3201 | 65.2729 | 65.4328 | 65.306 | -58.2219 | 123.4444 | 123.5627 | 123.4285 | 57.0266 | -123.8001
1220.2812 | 123.7335 | -65.3 | 58.2001 | 0.06235 | -0.040849 | -0.03045 | -0.057656 | -0.038627 | -0.038207 | 0.065477 | -0.022013 | -0.01394 | -0.00028958 | 0.1572 | -0.0020715 | -0.053893 | -0.007751 | -0.035879 | 0.001765 | -0.04543 | 0.12823 | -0.044742 | -64.806 | -8.5572 | -64.5063 | 58.1169 | 58.2306 | 58.1011 | -65.6092 | 65.2552 | -58.1983 | 65.2461 | 65.2641 | 0.008863 | -58.2455 | -58.0718 | -0.3092 | -0.083138 | 0.49398 | 0.79372 | 1.1029 | 0.030565 | -0.099014 | 65.3018 | 65.2546 | 65.4282 | 65.2922 | -58.2448 | 123.4169 | 123.5306 | 123.401 | 56.7427 | -123.8093
1221.2656 | 123.6786 | -65.3366 | 58.2184 | 0.031826 | -0.042986 | -0.031518 | -0.057656 | -0.037559 | -0.038207 | 0.080738 | -0.022013 | -0.016077 | -0.0024256 | 0.1572 | -0.0020715 | -0.049315 | -0.003172 | -0.031301 | 0.020079 | -0.036272 | 0.13281 | -0.049321 | -64.8106 | -8.3878 | -64.5063 | 58.1078 | 58.2215 | 58.1011 | -65.6183 | 65.2873 | -58.1983 | 65.2873 | 65.3053 | 0.01802 | -58.2547 | -58.0856 | -0.28173 | -0.11061 | 0.52602 | 0.83034 | 1.1121 | 0.003096 | -0.11733 | 65.3567 | 65.3003 | 65.4694 | 65.3334 | -58.2677 | 123.4444 | 123.5581 | 123.4377 | 56.9488 | -123.8367
1222.2656 | 123.6649 | -65.3503 | 58.2504 | 0.047088 | -0.040849 | -0.031518 | -0.057656 | -0.039695 | -0.037138 | 0.065477 | -0.020945 | -0.015009 | -0.0024256 | 0.15826 | -0.0020715 | -0.049315 | -0.003172 | -0.040457 | 0.010922 | -0.036272 | 0.12365 | -0.049321 | -64.8152 | -8.1864 | -64.488 | 58.1261 | 58.2398 | 58.1194 | -65.6046 | 65.301 | -58.2395 | 65.301 | 65.3099 | 0.008864 | -58.2867 | -58.1268 | -0.25426 | -0.12434 | 0.53517 | 0.86239 | 1.1166 | -0.010632 | -0.13105 | 65.3613 | 65.3141 | 65.474 | 65.3472 | -58.2997 | 123.4764 | 123.5901 | 123.4697 | 57.164 | -123.855
1223.2812 | 123.6603 | -65.3366 | 58.1772 | 0.047088 | -0.039781 | -0.029381 | -0.058725 | -0.039695 | -0.03607 | 0.065477 | -0.019877 | -0.01394 | -0.0013576 | 0.15613 | -0.0042075 | -0.044736 | -0.035222 | -0.022144 | 0.010922 | -0.031693 | 0.12365 | -0.049321 | -64.8335 | -7.2477 | -64.5704 | 58.0986 | 58.2261 | 58.1148 | -65.6275 | 65.2873 | -58.1663 | 65.2919 | 65.3145 | 0.027177 | -58.2089 | -58.0535 | -0.29089 | -0.078564 | 0.50312 | 0.76624 | 1.0571 | 0.048874 | -0.06239 | 65.3475 | 65.3049 | 65.4603 | 65.3014 | -58.2265 | 123.4352 | 123.5627 | 123.4514 | 58.0889 | -123.8047
1224.2656 | 123.7106 | -65.3091 | 58.2596 | 0.06235 | -0.040849 | -0.032586 | -0.058725 | -0.039695 | -0.037138 | 0.065477 | -0.020945 | -0.016077 | -0.0024256 | 0.1572 | -0.0042075 | -0.044736 | -0.035222 | -0.031301 | 0.015501 | -0.063746 | 0.11449 | -0.053899 | -64.8014 | -7.0554 | -64.5109 | 58.1307 | 58.2535 | 58.0782 | -65.5954 | 65.2552 | -58.2441 | 65.2644 | 65.2778 | 0.022598 | -58.3233 | -58.1451 | -0.2863 | -0.12891 | 0.50771 | 0.79829 | 1.0846 | -0.006052 | -0.18142 | 65.3246 | 65.2454 | 65.4236 | 65.2739 | -58.3135 | 123.4398 | 123.5627 | 123.3873 | 58.2537 | -123.855
1225.2812 | 123.7885 | -65.3412 | 58.136 | 0.047088 | -0.039781 | -0.031518 | -0.058725 | -0.038627 | -0.03607 | 0.050216 | -0.020945 | -0.012872 | -0.00028958 | 0.15826 | -0.0031395 | -0.049315 | -0.030644 | -0.026723 | 0.033814 | -0.068325 | 0.10534 | -0.053899 | -64.8381 | -5.8924 | -64.5521 | 58.0986 | 58.2169 | 57.9545 | -65.6367 | 65.2873 | -58.1022 | 65.2919 | 65.3145 | 0.027176 | -58.2043 | -58.0306 | -0.29547 | -0.037365 | 0.50312 | 0.78913 | 1.0846 | 0.080916 | -0.18144 | 65.375 | 65.2729 | 65.4465 | 65.3105 | -58.1899 | 123.4398 | 123.5581 | 123.2957 | 59.4487 | -123.7726
1226.2656 | 123.7061 | -65.3366 | 58.2184 | 0.06235 | -0.040849 | -0.033655 | -0.058725 | -0.039695 | -0.037138 | 0.034955 | -0.020945 | -0.01394 | -0.0034936 | 0.15826 | -0.0020715 | -0.053893 | -0.021486 | -0.035879 | 0.006344 | -0.059167 | 0.12823 | -0.058478 | -64.8197 | -6.0985 | -64.5337 | 58.1169 | 58.2352 | 58.0232 | -65.6229 | 65.2781 | -58.212 | 65.2827 | 65.3007 | 0.022599 | -58.2776 | -58.0902 | -0.28631 | -0.10145 | 0.51686 | 0.80287 | 1.0892 | 0.016832 | -0.19516 | 65.343 | 65.2774 | 65.4648 | 65.3151 | -58.2769 | 123.4535 | 123.5718 | 123.3598 | 59.2381 | -123.8413
1227.2812 | 123.6282 | -65.3732 | 58.1772 | 0.047088 | -0.040849 | -0.032586 | -0.059793 | -0.037559 | -0.038207 | 0.050216 | -0.022013 | -0.015009 | -0.0034936 | 0.1572 | -0.0031395 | -0.044736 | -0.007751 | -0.035879 | 0.001765 | -0.063746 | 0.11907 | -0.053899 | -64.8381 | -7.2248 | -64.5246 | 58.0757 | 58.2032 | 58.0003 | -65.6504 | 65.3193 | -58.1754 | 65.3285 | 65.3374 | 0.01802 | -58.2409 | -58.0581 | -0.27716 | -0.10146 | 0.53517 | 0.84864 | 1.1258 | 0.025981 | -0.17686 | 65.375 | 65.3095 | 65.4923 | 65.3655 | -58.2311 | 123.449 | 123.5764 | 123.3736 | 58.1484 | -123.8276
1228.2812 | 123.6557 | -65.3732 | 58.1818 | 0.06235 | -0.040849 | -0.032586 | -0.058725 | -0.039695 | -0.039275 | 0.065477 | -0.020945 | -0.012872 | -0.0034936 | 0.15826 | -0.0031395 | -0.044736 | -0.026065 | -0.031301 | 0.020079 | -0.063746 | 0.11449 | -0.058478 | -64.8152 | -7.4034 | -64.52 | 58.0895 | 58.2169 | 58.0049 | -65.6321 | 65.3148 | -58.1617 | 65.3285 | 65.3419 | 0.027177 | -58.2455 | -58.0673 | -0.25885 | -0.092299 | 0.55806 | 0.85322 | 1.1121 | 0.035139 | -0.17685 | 65.3933 | 65.3095 | 65.4877 | 65.3472 | -58.2402 | 123.4627 | 123.5901 | 123.3781 | 57.9698 | -123.8138
1229.2812 | 123.6969 | -65.3137 | 58.2367 | 0.06235 | -0.038712 | -0.033655 | -0.058725 | -0.037559 | -0.03607 | 0.065477 | -0.019877 | -0.015009 | -0.0024256 | 0.1604 | -0.0020715 | -0.049315 | -0.030644 | -0.035879 | 0.042971 | -0.063746 | 0.11907 | -0.058478 | -64.8014 | -7.7056 | -64.5063 | 58.1169 | 58.2398 | 58.0141 | -65.6229 | 65.2552 | -58.1937 | 65.2644 | 65.2778 | 0.022599 | -58.3004 | -58.1176 | -0.3092 | -0.11976 | 0.51229 | 0.80745 | 1.1166 | 0.003101 | -0.22263 | 65.3567 | 65.25 | 65.4328 | 65.2831 | -58.2952 | 123.4307 | 123.5535 | 123.3278 | 57.6081 | -123.8596
1230.2656 | 123.6557 | -65.3641 | 58.2184 | 0.06235 | -0.040849 | -0.033655 | -0.059793 | -0.038627 | -0.033933 | 0.050216 | -0.019877 | -0.01394 | -0.0034936 | 0.15826 | -0.0031395 | -0.053893 | -0.003172 | -0.026723 | 0.015501 | -0.063746 | 0.12823 | -0.058478 | -64.806 | -7.4675 | -64.5475 | 58.1032 | 58.2306 | 58.0049 | -65.6229 | 65.3056 | -58.2029 | 65.3102 | 65.3374 | 0.031755 | -58.2821 | -58.0902 | -0.25884 | -0.11519 | 0.55806 | 0.8166 | 1.0754 | 0.012254 | -0.21348 | 65.3796 | 65.3003 | 65.4923 | 65.3609 | -58.2769 | 123.4673 | 123.5947 | 123.369 | 57.8966 | -123.8413
1231.2812 | 123.7152 | -65.3275 | 58.2001 | 0.06235 | -0.040849 | -0.031518 | -0.057656 | -0.039695 | -0.037138 | 0.065477 | -0.022013 | -0.011804 | -0.0013576 | 0.15933 | -0.0042075 | -0.049315 | 0.001407 | -0.035879 | 0.024657 | -0.068325 | 0.11449 | -0.067636 | -64.8014 | -7.4538 | -64.6436 | 58.094 | 58.2123 | 57.9912 | -65.6321 | 65.2598 | -58.1754 | 65.2781 | 65.2916 | 0.031757 | -58.2684 | -58.0856 | -0.30462 | -0.10603 | 0.52602 | 0.68382 | 0.98844 | 0.01225 | -0.2089 | 65.3521 | 65.2591 | 65.4419 | 65.3289 | -58.2677 | 123.4215 | 123.5398 | 123.3186 | 57.8737 | -123.8321
1232.2656 | 123.6511 | -65.3412 | 58.2275 | 0.047088 | -0.039781 | -0.031518 | -0.058725 | -0.03649 | -0.03607 | 0.080738 | -0.020945 | -0.012872 | -0.0013576 | 0.1572 | -0.0052755 | -0.058472 | -0.030644 | -0.026723 | 0.029236 | -0.068325 | 0.12823 | -0.040163 | -64.8014 | -7.1379 | -64.5292 | 58.1032 | 58.2215 | 58.0095 | -65.6275 | 65.301 | -58.1983 | 65.2827 | 65.3145 | 0.01344 | -58.2959 | -58.0993 | -0.28631 | -0.12434 | 0.53975 | 0.81202 | 1.0983 | -0.006059 | -0.21805 | 65.3704 | 65.2729 | 65.4694 | 65.3105 | -58.2677 | 123.4444 | 123.5627 | 123.3507 | 58.2033 | -123.855
1233.2812 | 123.7061 | -65.3595 | 58.1955 | 0.047088 | -0.040849 | -0.032586 | -0.058725 | -0.039695 | -0.03607 | 0.050216 | -0.020945 | -0.012872 | -0.0024256 | 0.1572 | -0.0042075 | -0.044736 | -0.039801 | -0.035879 | 0.033814 | -0.068325 | 0.12823 | -0.053899 | -64.8152 | -6.6617 | -64.575 | 58.0895 | 58.2123 | 57.9912 | -65.6367 | 65.3056 | -58.1617 | 65.3148 | 65.3236 | 0.01802 | -58.2638 | -58.0673 | -0.27716 | -0.10603 | 0.54433 | 0.78455 | 1.0617 | 0.016827 | -0.20432 | 65.3933 | 65.2912 | 65.4877 | 65.3197 | -58.2494 | 123.449 | 123.5718 | 123.3507 | 58.6978 | -123.8322
1234.2656 | 123.6694 | -65.3595 | 58.1818 | 0.077612 | -0.040849 | -0.031518 | -0.059793 | -0.037559 | -0.035002 | 0.080738 | -0.020945 | -0.012872 | -0.0013576 | 0.1572 | -0.0042075 | -0.044736 | 0.001407 | -0.031301 | 0.029236 | -0.063746 | 0.12365 | -0.072215 | -64.8243 | -5.9565 | -64.6803 | 58.0757 | 58.1986 | 57.9912 | -65.6641 | 65.2873 | -58.1525 | 65.3148 | 65.3282 | 0.040914 | -58.2455 | -58.0581 | -0.30463 | -0.10603 | 0.53517 | 0.67924 | 0.98387 | 0.016824 | -0.19059 | 65.3887 | 65.2958 | 65.4831 | 65.3609 | -58.254 | 123.4352 | 123.5581 | 123.3507 | 59.403 | -123.8459
1235.2812 | 123.674 | -65.3824 | 58.1543 | 0.047088 | -0.040849 | -0.031518 | -0.058725 | -0.039695 | -0.03607 | 0.065477 | -0.019877 | -0.012872 | -0.0013576 | 0.1572 | -0.0042075 | -0.049315 | -0.003172 | -0.026723 | 0.020079 | -0.059167 | 0.12365 | -0.067636 | -64.8426 | -6.593 | -64.7169 | 58.0757 | 58.194 | 57.9958 | -65.655 | 65.3147 | -58.1342 | 65.3331 | 65.3557 | 0.040913 | -58.2135 | -58.0306 | -0.27259 | -0.078569 | 0.53974 | 0.66549 | 0.93808 | 0.039712 | -0.15854 | 65.4025 | 65.3232 | 65.506 | 65.3792 | -58.2219 | 123.4581 | 123.5764 | 123.3781 | 58.7894 | -123.8093
1236.2656 | 123.674 | -65.3732 | 58.1543 | 0.077612 | -0.041917 | -0.032586 | -0.056588 | -0.038627 | -0.03607 | 0.034955 | -0.020945 | -0.011804 | -0.0024256 | 0.15826 | -0.0031395 | -0.049315 | 0.001407 | -0.022144 | 0.024657 | -0.063746 | 0.11907 | -0.058478 | -64.8564 | -6.2404 | -64.7444 | 58.0574 | 58.1894 | 57.9866 | -65.6733 | 65.3148 | -58.1296 | 65.3239 | 65.3511 | 0.036334 | -58.218 | -58.0352 | -0.30006 | -0.096883 | 0.51685 | 0.62887 | 0.92892 | 0.035133 | -0.1677 | 65.3979 | 65.3095 | 65.4923 | 65.3746 | -58.2128 | 123.4306 | 123.5627 | 123.3598 | 59.1328 | -123.8276
1237.2812 | 123.6603 | -65.3458 | 58.2047 | 0.047088 | -0.039781 | -0.034723 | -0.057656 | -0.039695 | -0.037138 | 0.080738 | -0.020945 | -0.012872 | -0.0034936 | 0.15613 | -0.0042075 | -0.053893 | 0.001407 | -0.035879 | 0.029236 | -0.059167 | 0.11449 | -0.063057 | -64.8335 | -7.0234 | -64.6619 | 58.0895 | 58.2215 | 58.0507 | -65.6412 | 65.2827 | -58.1754 | 65.2919 | 65.3099 | 0.027178 | -58.2638 | -58.0902 | -0.29547 | -0.11519 | 0.51228 | 0.68382 | 0.97929 | 0.016829 | -0.15396 | 65.375 | 65.2866 | 65.4603 | 65.3472 | -58.2677 | 123.4352 | 123.5672 | 123.3965 | 58.3224 | -123.8459
1238.2812 | 123.7152 | -65.332 | 58.2138 | 0.06235 | -0.040849 | -0.032586 | -0.059793 | -0.037559 | -0.037138 | 0.065477 | -0.020945 | -0.015009 | -0.0024256 | 0.15933 | -0.0031395 | -0.053893 | 0.005985 | -0.031301 | 0.029236 | -0.068325 | 0.11449 | -0.063057 | -64.8106 | -7.5499 | -64.6665 | 58.1032 | 58.2261 | 57.9958 | -65.6229 | 65.269 | -58.1846 | 65.2781 | 65.3007 | 0.031756 | -58.2821 | -58.0993 | -0.29089 | -0.11061 | 0.52144 | 0.6655 | 0.95639 | 0.012253 | -0.21805 | 65.3613 | 65.2637 | 65.4465 | 65.338 | -58.2769 | 123.4352 | 123.5581 | 123.3278 | 57.7821 | -123.8367
1239.2812 | 123.7015 | -65.3412 | 58.168 | 0.047088 | -0.040849 | -0.032586 | -0.058725 | -0.038627 | -0.03607 | 0.065477 | -0.020945 | -0.011804 | -0.0034936 | 0.15826 | -0.0020715 | -0.053893 | 0.001407 | -0.031301 | 0.020079 | -0.063746 | 0.13281 | -0.063057 | -64.8472 | -7.6873 | -64.694 | 58.0757 | 58.2032 | 57.9866 | -65.6504 | 65.2781 | -58.148 | 65.2873 | 65.3099 | 0.031756 | -58.2318 | -58.0352 | -0.3092 | -0.092302 | 0.49397 | 0.64719 | 0.95639 | 0.035136 | -0.18144 | 65.3613 | 65.2774 | 65.474 | 65.3426 | -58.2311 | 123.4169 | 123.5444 | 123.3278 | 57.6539 | -123.8184
1240.2812 | 123.6557 | -65.3641 | 58.1543 | 0.06235 | -0.040849 | -0.032586 | -0.057656 | -0.038627 | -0.03607 | 0.050216 | -0.019877 | -0.012872 | -0.0013576 | 0.15826 | -0.0020715 | -0.058472 | -0.003172 | -0.031301 | 0.029236 | -0.063746 | 0.12365 | -0.058478 | -64.8747 | -7.2844 | -64.7032 | 58.062 | 58.1803 | 57.982 | -65.6779 | 65.3056 | -58.1251 | 65.3056 | 65.3328 | 0.027177 | -58.218 | -58.0306 | -0.31379 | -0.092304 | 0.48938 | 0.66092 | 0.97471 | 0.025976 | -0.17228 | 65.3933 | 65.3003 | 65.4877 | 65.3609 | -58.2128 | 123.4261 | 123.5443 | 123.3461 | 58.0797 | -123.8322
1241.2656 | 123.674 | -65.3412 | 58.223 | 0.06235 | -0.042986 | -0.032586 | -0.058725 | -0.039695 | -0.037138 | 0.080738 | -0.020945 | -0.012872 | -0.0013576 | 0.15933 | -0.0031395 | -0.053893 | -0.003172 | -0.031301 | 0.020079 | -0.063746 | 0.12365 | -0.049321 | -64.8197 | -7.1012 | -64.6619 | 58.0895 | 58.2169 | 58.0095 | -65.6367 | 65.2919 | -58.2029 | 65.2873 | 65.3099 | 0.01802 | -58.2867 | -58.0993 | -0.29547 | -0.1335 | 0.52144 | 0.67924 | 0.97471 | -0.006059 | -0.21347 | 65.3613 | 65.2774 | 65.4648 | 65.338 | -58.2723 | 123.4307 | 123.5581 | 123.3507 | 58.24 | -123.8596
1242.2656 | 123.7793 | -65.3046 | 58.1863 | 0.06235 | -0.040849 | -0.033655 | -0.059793 | -0.037559 | -0.03607 | 0.080738 | -0.020945 | -0.012872 | -0.0013576 | 0.1604 | -0.0042075 | -0.053893 | -0.007751 | -0.026723 | 0.029236 | -0.063746 | 0.11907 | -0.044742 | -64.8106 | -7.4904 | -64.6207 | 58.0849 | 58.2032 | 58.0049 | -65.6458 | 65.2598 | -58.1571 | 65.2507 | 65.2778 | 0.018019 | -58.2501 | -58.0673 | -0.34125 | -0.10146 | 0.49397 | 0.68383 | 1.0251 | 0.016826 | -0.18143 | 65.3338 | 65.2408 | 65.4236 | 65.2968 | -58.2311 | 123.3894 | 123.5077 | 123.3095 | 57.8142 | -123.8322
1243.2812 | 123.6923 | -65.3824 | 58.1772 | 0.077612 | -0.041917 | -0.033655 | -0.058725 | -0.039695 | -0.03607 | 0.065477 | -0.022013 | -0.012872 | -0.0024256 | 0.15933 | -0.0052755 | -0.053893 | 0.005985 | -0.026723 | 0.024657 | -0.063746 | 0.12365 | -0.063057 | -64.806 | -8.3833 | -64.6436 | 58.0803 | 58.2032 | 58.0003 | -65.6504 | 65.3193 | -58.1525 | 65.3285 | 65.3557 | 0.036334 | -58.2409 | -58.0535 | -0.26801 | -0.096878 | 0.57637 | 0.73875 | 1.0068 | 0.025981 | -0.17686 | 65.407 | 65.3186 | 65.506 | 65.3884 | -58.2402 | 123.4627 | 123.5856 | 123.3827 | 56.9991 | -123.8276
1244.2656 | 123.7381 | -65.3503 | 58.1543 | 0.06235 | -0.041917 | -0.031518 | -0.058725 | -0.037559 | -0.038207 | 0.065477 | -0.019877 | -0.01394 | -0.0034936 | 0.15933 | -0.0052755 | -0.053893 | -0.007751 | -0.031301 | 0.033814 | -0.068325 | 0.12823 | -0.049321 | -64.8106 | -8.3787 | -64.6665 | 58.0712 | 58.1849 | 57.9179 | -65.6687 | 65.301 | -58.1205 | 65.2964 | 65.319 | 0.01802 | -58.2226 | -58.0261 | -0.31837 | -0.083147 | 0.53975 | 0.68382 | 1.0022 | 0.030554 | -0.23638 | 65.3842 | 65.282 | 65.4786 | 65.3426 | -58.2036 | 123.4215 | 123.5352 | 123.2683 | 56.9717 | -123.823
1245.2656 | 123.7335 | -65.3549 | 58.2413 | 0.06235 | -0.044054 | -0.033655 | -0.058725 | -0.038627 | -0.03607 | 0.080738 | -0.022013 | -0.01394 | -0.0013576 | 0.15933 | -0.0063445 | -0.049315 | 0.001407 | -0.031301 | 0.029236 | -0.059167 | 0.12823 | -0.058478 | -64.8243 | -7.6003 | -64.6848 | 58.0666 | 58.1849 | 57.9317 | -65.6687 | 65.2964 | -58.212 | 65.3056 | 65.3236 | 0.027177 | -58.3004 | -58.113 | -0.31379 | -0.1747 | 0.53059 | 0.67008 | 0.98387 | -0.056421 | -0.30962 | 65.3842 | 65.2958 | 65.4831 | 65.3563 | -58.2998 | 123.4215 | 123.5398 | 123.2866 | 57.7546 | -123.91
1246.2656 | 123.7793 | -65.3824 | 58.0994 | 0.06235 | -0.041917 | -0.034723 | -0.058725 | -0.038627 | -0.03607 | 0.050216 | -0.019877 | -0.01394 | -0.0013576 | 0.1604 | -0.0042075 | -0.053893 | -0.003172 | -0.040457 | 0.024657 | -0.059167 | 0.11449 | -0.058478 | -64.8747 | -5.3247 | -64.7444 | 58.0162 | 58.1436 | 57.8904 | -65.7237 | 65.3239 | -58.0747 | 65.3285 | 65.3419 | 0.018021 | -58.1585 | -57.9849 | -0.34127 | -0.083157 | 0.50769 | 0.63802 | 0.97929 | 0.044279 | -0.20892 | 65.407 | 65.3232 | 65.4969 | 65.3792 | -58.1578 | 123.3986 | 123.526 | 123.2728 | 60.0577 | -123.823
1247.2656 | 123.6649 | -65.3549 | 58.2047 | 0.047088 | -0.042986 | -0.033655 | -0.058725 | -0.038627 | -0.038207 | 0.065477 | -0.020945 | -0.015009 | -0.0024256 | 0.16147 | -0.0042075 | -0.058472 | 0.001407 | -0.026723 | 0.024657 | -0.068325 | 0.12365 | -0.063057 | -64.8289 | -7.2569 | -64.6803 | 58.0574 | 58.1803 | 58.0049 | -65.6733 | 65.2919 | -58.18 | 65.2964 | 65.3282 | 0.036334 | -58.273 | -58.081 | -0.31837 | -0.14724 | 0.52601 | 0.67466 | 0.99302 | -0.024378 | -0.19974 | 65.3796 | 65.2866 | 65.4786 | 65.3563 | -58.2677 | 123.4123 | 123.5352 | 123.3598 | 58.098 | -123.8779
1248.2812 | 123.6969 | -65.3778 | 58.1726 | 0.047088 | -0.044054 | -0.035791 | -0.059793 | -0.039695 | -0.037138 | 0.065477 | -0.020945 | -0.01394 | -0.0013576 | 0.1604 | -0.0031395 | -0.049315 | -0.003172 | -0.031301 | 0.006344 | -0.068325 | 0.12823 | -0.063057 | -64.8289 | -7.4996 | -64.7032 | 58.062 | 58.1803 | 57.9912 | -65.6824 | 65.3148 | -58.1663 | 65.3285 | 65.3465 | 0.031756 | -58.2409 | -58.0444 | -0.30464 | -0.11061 | 0.5489 | 0.67465 | 0.97929 | 0.007666 | -0.18143 | 65.3842 | 65.3095 | 65.506 | 65.3746 | -58.2357 | 123.4398 | 123.5581 | 123.369 | 57.8782 | -123.8551
1249.2656 | 123.7839 | -65.3275 | 58.1589 | 0.047088 | -0.042986 | -0.032586 | -0.059793 | -0.039695 | -0.03607 | 0.050216 | -0.020945 | -0.01394 | -0.0024256 | 0.15933 | -0.0031395 | -0.049315 | 0.001407 | -0.035879 | 0.024657 | -0.068325 | 0.11907 | -0.063057 | -64.8152 | -8.1955 | -64.6299 | 58.0849 | 58.2077 | 57.8813 | -65.6595 | 65.2644 | -58.1342 | 65.2781 | 65.2916 | 0.027178 | -58.2272 | -58.0398 | -0.3321 | -0.07399 | 0.51229 | 0.69756 | 1.0297 | 0.04887 | -0.27759 | 65.3521 | 65.2591 | 65.4465 | 65.3289 | -58.2219 | 123.4123 | 123.5352 | 123.2087 | 57.1319 | -123.8184
1250.2656 | 123.8388 | -65.3137 | 58.1085 | 0.047088 | -0.042986 | -0.032586 | -0.060862 | -0.038627 | -0.038207 | 0.065477 | -0.020945 | -0.015009 | -0.0024256 | 0.15933 | -0.0031395 | -0.049315 | 0.001407 | -0.026723 | 0.010922 | -0.063746 | 0.13281 | -0.053899 | -64.8197 | -8.6488 | -64.6207 | 58.0757 | 58.1894 | 58.0003 | -65.6641 | 65.2598 | -58.0976 | 65.2644 | 65.287 | 0.027176 | -58.1723 | -57.9757 | -0.35041 | -0.032793 | 0.49397 | 0.69298 | 1.0434 | 0.080909 | -0.10819 | 65.3246 | 65.25 | 65.4465 | 65.3151 | -58.1624 | 123.3894 | 123.5032 | 123.3141 | 56.6649 | -123.7726
1251.2656 | 123.7152 | -65.3503 | 58.1955 | 0.077612 | -0.044054 | -0.033655 | -0.058725 | -0.037559 | -0.03607 | 0.065477 | -0.020945 | -0.015009 | -0.0024256 | 0.15933 | -0.0042075 | -0.049315 | 0.001407 | -0.026723 | 0.010922 | -0.072904 | 0.12823 | -0.053899 | -64.8289 | -8.1269 | -64.6619 | 58.0483 | 58.1665 | 57.9591 | -65.6916 | 65.2964 | -58.1846 | 65.301 | 65.3236 | 0.027176 | -58.2684 | -58.0673 | -0.34126 | -0.14724 | 0.52144 | 0.68839 | 1.0297 | -0.028959 | -0.23637 | 65.3613 | 65.2774 | 65.4786 | 65.3517 | -58.2494 | 123.3986 | 123.5169 | 123.3095 | 57.2235 | -123.8871
1252.2656 | 123.7289 | -65.3915 | 58.1039 | 0.047088 | -0.044054 | -0.034723 | -0.059793 | -0.03649 | -0.037138 | 0.080738 | -0.020945 | -0.01394 | -0.0013576 | 0.1604 | -0.0042075 | -0.049315 | -0.007751 | -0.031301 | 0.024657 | -0.063746 | 0.12823 | -0.058478 | -64.806 | -6.8906 | -64.7306 | 58.0574 | 58.1803 | 57.9545 | -65.6824 | 65.3331 | -58.0793 | 65.3422 | 65.3602 | 0.027177 | -58.1677 | -57.9757 | -0.2909 | -0.046529 | 0.58553 | 0.66091 | 0.95182 | 0.07633 | -0.1494 | 65.4162 | 65.3278 | 65.5198 | 65.3838 | -58.1624 | 123.449 | 123.5718 | 123.3461 | 58.5009 | -123.7864
1253.2812 | 123.7564 | -65.3366 | 58.1177 | 0.047088 | -0.044054 | -0.034723 | -0.060862 | -0.038627 | -0.037138 | 0.080738 | -0.019877 | -0.015009 | -0.0024256 | 0.16147 | -0.0042075 | -0.049315 | -0.003172 | -0.040457 | 0.010922 | -0.072904 | 0.12823 | -0.058478 | -64.8335 | -6.8128 | -64.7444 | 58.0254 | 58.162 | 57.9179 | -65.7008 | 65.2781 | -58.1068 | 65.2873 | 65.2962 | 0.018021 | -58.1906 | -57.9894 | -0.36415 | -0.092311 | 0.50312 | 0.59224 | 0.9564 | 0.044282 | -0.19976 | 65.3475 | 65.2637 | 65.4648 | 65.3334 | -58.1762 | 123.362 | 123.4986 | 123.2545 | 58.5238 | -123.8184
1254.2656 | 123.7381 | -65.3778 | 58.1085 | 0.06235 | -0.045122 | -0.033655 | -0.058725 | -0.038627 | -0.037138 | 0.065477 | -0.020945 | -0.01394 | -0.0013576 | 0.1604 | -0.0042075 | -0.049315 | 0.005985 | -0.035879 | 0.001765 | -0.068325 | 0.11907 | -0.049321 | -64.8335 | -7.2157 | -64.7032 | 58.0483 | 58.1803 | 57.9683 | -65.6916 | 65.3285 | -58.1068 | 65.3285 | 65.3419 | 0.013442 | -58.1768 | -57.9894 | -0.31379 | -0.060264 | 0.54432 | 0.67465 | 0.98845 | 0.071752 | -0.14024 | 65.3796 | 65.3095 | 65.4969 | 65.3838 | -58.1578 | 123.4261 | 123.5581 | 123.3461 | 58.1621 | -123.8001
1255.2656 | 123.7198 | -65.3687 | 58.1818 | 0.06235 | -0.046191 | -0.033655 | -0.057656 | -0.039695 | -0.038207 | 0.080738 | -0.020945 | -0.016077 | -0.0024256 | 0.16147 | -0.0042075 | -0.049315 | 0.001407 | -0.026723 | 0.015501 | -0.068325 | 0.11907 | -0.063057 | -64.8243 | -7.2294 | -64.6665 | 58.0528 | 58.1803 | 58.0095 | -65.6962 | 65.3056 | -58.1663 | 65.3193 | 65.3419 | 0.036334 | -58.2501 | -58.0627 | -0.32753 | -0.12893 | 0.54433 | 0.70213 | 1.0297 | -0.00149 | -0.17228 | 65.3842 | 65.3003 | 65.4877 | 65.3701 | -58.2448 | 123.4215 | 123.5489 | 123.3781 | 58.1392 | -123.8779
1256.2656 | 123.7747 | -65.3687 | 58.1314 | 0.031826 | -0.046191 | -0.031518 | -0.059793 | -0.039695 | -0.039275 | 0.050216 | -0.022013 | -0.015009 | -0.0024256 | 0.16147 | -0.0063445 | -0.044736 | -0.003172 | -0.026723 | 0.006344 | -0.072904 | 0.12823 | -0.044742 | -64.8106 | -6.7395 | -64.6711 | 58.0391 | 58.1665 | 57.9225 | -65.7053 | 65.3239 | -58.1251 | 65.3239 | 65.3419 | 0.018019 | -58.2043 | -58.0032 | -0.33669 | -0.092309 | 0.55806 | 0.69755 | 1.0342 | 0.035128 | -0.20891 | 65.375 | 65.2957 | 65.4969 | 65.3655 | -58.1762 | 123.4078 | 123.5352 | 123.2911 | 58.6291 | -123.8367
1257.2656 | 123.7656 | -65.3275 | 58.168 | 0.047088 | -0.045122 | -0.032586 | -0.059793 | -0.040764 | -0.037138 | 0.019694 | -0.019877 | -0.015009 | -0.0034936 | 0.16254 | -0.0052755 | -0.049315 | 0.005985 | -0.035879 | 0.024657 | -0.068325 | 0.10992 | -0.044742 | -64.7923 | -7.1882 | -64.6528 | 58.0712 | 58.1849 | 57.9774 | -65.6641 | 65.2827 | -58.1434 | 65.2781 | 65.2916 | 0.008863 | -58.2364 | -58.0581 | -0.33667 | -0.09688 | 0.53518 | 0.67466 | 1.0113 | 0.016821 | -0.19059 | 65.3521 | 65.2591 | 65.4374 | 65.3334 | -58.2128 | 123.3986 | 123.5123 | 123.3049 | 58.1392 | -123.8322
1258.2812 | 123.8022 | -65.3275 | 58.168 | 0.047088 | -0.044054 | -0.033655 | -0.059793 | -0.039695 | -0.035002 | 0.080738 | -0.020945 | -0.015009 | -0.0034936 | 0.16147 | -0.0052755 | -0.049315 | -0.026065 | -0.031301 | 0.006344 | -0.036272 | 0.12365 | -0.044742 | -64.7923 | -7.1745 | -64.6162 | 58.0757 | 58.1986 | 58.069 | -65.6641 | 65.2827 | -58.1617 | 65.2781 | 65.2962 | 0.013441 | -58.2043 | -58.0444 | -0.33667 | -0.092302 | 0.53518 | 0.71129 | 1.048 | 0.030557 | -0.099021 | 65.3338 | 65.2912 | 65.4511 | 65.3014 | -58.2128 | 123.4032 | 123.526 | 123.3965 | 58.153 | -123.8322
1259.2656 | 123.6832 | -65.3915 | 58.1406 | 0.031826 | -0.045122 | -0.032586 | -0.057656 | -0.038627 | -0.039275 | 0.050216 | -0.022013 | -0.016077 | -0.0024256 | 0.16147 | -0.0042075 | -0.049315 | 0.001407 | -0.035879 | 0.015501 | -0.04543 | 0.11907 | -0.049321 | -64.7877 | -7.5041 | -64.6528 | 58.0666 | 58.1894 | 58.0599 | -65.6641 | 65.3422 | -58.1251 | 65.3422 | 65.3557 | 0.013442 | -58.186 | -58.0215 | -0.27259 | -0.073993 | 0.60384 | 0.73875 | 1.0113 | 0.048866 | -0.080712 | 65.407 | 65.3461 | 65.5106 | 65.3929 | -58.1899 | 123.4581 | 123.581 | 123.4514 | 57.8874 | -123.8047
1260.2656 | 123.7701 | -65.3503 | 58.1543 | 0.031826 | -0.045122 | -0.033655 | -0.059793 | -0.039695 | -0.038207 | 0.065477 | -0.022013 | -0.016077 | -0.0034936 | 0.16147 | -0.0063445 | -0.044736 | -0.003172 | -0.026723 | 0.006344 | -0.040851 | 0.11449 | -0.035584 | -64.774 | -7.7468 | -64.5978 | 58.0803 | 58.2123 | 58.069 | -65.6504 | 65.3148 | -58.148 | 65.3056 | 65.3236 | 0.008861 | -58.1951 | -58.0398 | -0.30005 | -0.07399 | 0.57638 | 0.7525 | 1.0525 | 0.058026 | -0.085288 | 65.3567 | 65.3095 | 65.4648 | 65.3472 | -58.1899 | 123.4306 | 123.5627 | 123.4194 | 57.6035 | -123.8047
1261.2656 | 123.7427 | -65.3687 | 58.1406 | 0.047088 | -0.046191 | -0.031518 | -0.060862 | -0.039695 | -0.038207 | 0.095999 | -0.019877 | -0.015009 | -0.0034936 | 0.16254 | -0.0063445 | -0.049315 | 0.001407 | -0.026723 | 0.006344 | -0.031693 | 0.13281 | -0.049321 | -64.7602 | -7.7102 | -64.6391 | 58.0895 | 58.2077 | 58.0827 | -65.655 | 65.3193 | -58.1342 | 65.3193 | 65.3419 | 0.022598 | -58.1723 | -58.0078 | -0.28632 | -0.0511 | 0.60843 | 0.7296 | 1.0159 | 0.067181 | -0.057819 | 65.375 | 65.337 | 65.5015 | 65.3701 | -58.1899 | 123.4581 | 123.5764 | 123.4514 | 57.6585 | -123.7955
1262.2656 | 123.7106 | -65.3732 | 58.1268 | 0.047088 | -0.047259 | -0.031518 | -0.060862 | -0.039695 | -0.039275 | 0.065477 | -0.022013 | -0.015009 | -0.0056306 | 0.16254 | -0.0042075 | -0.044736 | -0.016908 | -0.031301 | 0.029236 | -0.036272 | 0.13281 | -0.044742 | -64.7785 | -6.8402 | -64.6391 | 58.0712 | 58.1849 | 58.0507 | -65.6824 | 65.3285 | -58.0976 | 65.3285 | 65.3419 | 0.013441 | -58.1631 | -57.994 | -0.30921 | -0.055681 | 0.59469 | 0.73418 | 1.0434 | 0.05802 | -0.076136 | 65.4025 | 65.337 | 65.506 | 65.3563 | -58.1716 | 123.4444 | 123.5581 | 123.4239 | 58.533 | -123.8093
1263.2812 | 123.7793 | -65.3503 | 58.1085 | 0.092874 | -0.048328 | -0.03045 | -0.059793 | -0.040764 | -0.040343 | 0.034955 | -0.023082 | -0.015009 | -0.0024256 | 0.1604 | -0.0042075 | -0.044736 | -0.007751 | -0.026723 | 0.015501 | -0.040851 | 0.12823 | -0.035584 | -64.7694 | -6.8311 | -64.6207 | 58.0666 | 58.1894 | 58.0599 | -65.6687 | 65.3148 | -58.093 | 65.3056 | 65.3236 | 0.008861 | -58.1494 | -57.9803 | -0.31837 | -0.04195 | 0.58096 | 0.7296 | 1.048 | 0.080909 | -0.048669 | 65.3658 | 65.3095 | 65.4786 | 65.3426 | -58.1441 | 123.4169 | 123.5398 | 123.4102 | 58.5193 | -123.7772
1264.2656 | 123.6649 | -65.3687 | 58.2275 | 0.047088 | -0.046191 | -0.034723 | -0.059793 | -0.039695 | -0.038207 | 0.050216 | -0.023082 | -0.01394 | -0.0034936 | 0.16254 | -0.0063445 | -0.044736 | -0.026065 | -0.022144 | 0.010922 | -0.031693 | 0.13739 | -0.049321 | -64.774 | -6.5838 | -64.6345 | 58.0666 | 58.1986 | 58.0736 | -65.6733 | 65.3193 | -58.2166 | 65.3239 | 65.3465 | 0.027177 | -58.2592 | -58.0902 | -0.30463 | -0.16097 | 0.59469 | 0.73418 | 1.0388 | -0.028952 | -0.15395 | 65.3796 | 65.337 | 65.506 | 65.3426 | -58.2769 | 123.4352 | 123.5672 | 123.4422 | 58.7848 | -123.9008
1265.2656 | 123.674 | -65.3732 | 58.168 | 0.047088 | -0.047259 | -0.033655 | -0.058725 | -0.039695 | -0.038207 | 0.050216 | -0.022013 | -0.01394 | -0.0034936 | 0.16147 | -0.0052755 | -0.049315 | -0.026065 | -0.031301 | 0.024657 | -0.031693 | 0.11449 | -0.040163 | -64.7236 | -7.0234 | -64.6207 | 58.1078 | 58.2306 | 58.1056 | -65.6458 | 65.3331 | -58.1434 | 65.3239 | 65.3419 | 0.008862 | -58.1997 | -58.0535 | -0.27258 | -0.060252 | 0.64964 | 0.75249 | 1.0251 | 0.062608 | -0.062392 | 65.3979 | 65.3415 | 65.4877 | 65.3472 | -58.2082 | 123.481 | 123.6039 | 123.4789 | 58.3498 | -123.8138
1266.2656 | 123.6649 | -65.387 | 58.168 | 0.06235 | -0.047259 | -0.034723 | -0.059793 | -0.039695 | -0.038207 | 0.034955 | -0.022013 | -0.016077 | -0.0034936 | 0.16254 | -0.0052755 | -0.040158 | -0.021486 | -0.031301 | 0.024657 | -0.031693 | 0.13739 | -0.049321 | -64.7511 | -6.4053 | -64.6482 | 58.0849 | 58.2032 | 58.0873 | -65.6595 | 65.3376 | -58.1434 | 65.3468 | 65.3557 | 0.01802 | -58.1997 | -58.0306 | -0.27259 | -0.083145 | 0.6359 | 0.73875 | 1.0113 | 0.035136 | -0.080706 | 65.4116 | 65.3553 | 65.5243 | 65.3655 | -58.2174 | 123.4718 | 123.5901 | 123.4743 | 58.9817 | -123.8276
1267.2656 | 123.6374 | -65.4007 | 58.1543 | 0.077612 | -0.048328 | -0.033655 | -0.058725 | -0.038627 | -0.038207 | 0.050216 | -0.023082 | -0.016077 | -0.0056306 | 0.16147 | -0.0042075 | -0.040158 | -0.021486 | -0.031301 | 0.020079 | -0.031693 | 0.13739 | -0.049321 | -64.7511 | -6.4007 | -64.7123 | 58.0712 | 58.194 | 58.0644 | -65.6687 | 65.3514 | -58.1342 | 65.3605 | 65.3694 | 0.01802 | -58.186 | -58.0169 | -0.26801 | -0.083147 | 0.64963 | 0.68838 | 0.9564 | 0.039712 | -0.089866 | 65.4208 | 65.369 | 65.5381 | 65.3792 | -58.2036 | 123.4718 | 123.5947 | 123.4651 | 59 | -123.823
1268.2812 | 123.7839 | -65.3503 | 58.1039 | 0.06235 | -0.047259 | -0.033655 | -0.058725 | -0.038627 | -0.037138 | 0.065477 | -0.02415 | -0.016077 | -0.0024256 | 0.1604 | -0.0074125 | -0.044736 | -0.030644 | -0.022144 | 0.015501 | -0.031693 | 0.12823 | -0.044742 | -64.7556 | -6.0115 | -64.6894 | 58.062 | 58.1894 | 58.0644 | -65.6824 | 65.3056 | -58.0884 | 65.3056 | 65.3282 | 0.022598 | -58.1356 | -57.9757 | -0.3321 | -0.04195 | 0.5947 | 0.66092 | 0.99303 | 0.085487 | -0.039512 | 65.3658 | 65.3186 | 65.4786 | 65.3197 | -58.1487 | 123.4123 | 123.5398 | 123.4148 | 59.3389 | -123.7864
1269.2812 | 123.7793 | -65.3366 | 58.1085 | 0.047088 | -0.048328 | -0.032586 | -0.06193 | -0.037559 | -0.038207 | 0.034955 | -0.02415 | -0.016077 | -0.0034936 | 0.1604 | -0.0063445 | -0.044736 | -0.012329 | -0.022144 | 0.006344 | -0.036272 | 0.13281 | -0.044742 | -64.7556 | -6.3915 | -64.6894 | 58.0712 | 58.1986 | 58.069 | -65.6687 | 65.2919 | -58.1022 | 65.2919 | 65.3145 | 0.022598 | -58.1448 | -57.9757 | -0.3321 | -0.037371 | 0.58096 | 0.64719 | 0.97929 | 0.090066 | -0.039512 | 65.343 | 65.3003 | 65.4694 | 65.3243 | -58.1533 | 123.4078 | 123.5352 | 123.4056 | 58.9451 | -123.7772
1270.2656 | 123.6511 | -65.3824 | 58.1863 | 0.031826 | -0.048328 | -0.032586 | -0.06193 | -0.039695 | -0.041411 | 0.050216 | -0.022013 | -0.016077 | -0.0045626 | 0.16467 | -0.0042075 | -0.040158 | -0.016908 | -0.031301 | 0.020079 | -0.040851 | 0.13281 | -0.044742 | -64.7373 | -6.245 | -64.6803 | 58.0666 | 58.1894 | 58.0507 | -65.6733 | 65.3376 | -58.1663 | 65.3422 | 65.3511 | 0.013441 | -58.2272 | -58.0535 | -0.2909 | -0.11977 | 0.64505 | 0.70212 | 0.99302 | 0.00309 | -0.13565 | 65.4025 | 65.3415 | 65.5152 | 65.3655 | -58.2311 | 123.449 | 123.5718 | 123.4331 | 59.1374 | -123.8596
1271.2812 | 123.7198 | -66.6733 | 56.8909 | 0.06235 | -0.047259 | -0.033655 | -0.058725 | -0.038627 | -0.040343 | 0.050216 | 0.022851 | 0.009562 | -0.0034936 | 0.16361 | 0.066298 | -0.044736 | -0.026065 | -0.026723 | 0.010922 | -0.059167 | 0.12365 | -0.035584 | 56.745 | -0.10953 | -65.7975 | 56.7892 | 56.9028 | 56.7733 | -66.937 | 66.6377 | -56.8799 | 66.6285 | 66.6466 | 0.008861 | -56.95 | -56.7672 | -0.26376 | -0.1017 | 123.4183 | 0.87581 | 1.1396 | 0.011974 | -0.1176 | 66.6842 | 66.6141 | 66.7969 | 66.6472 | -56.9265 | 123.4624 | 123.5761 | 123.4465 | 66.5637 | -123.8279
1272.2656 | 123.7152 | -66.6229 | 56.9366 | 0.06235 | -0.049396 | -0.032586 | -0.060862 | -0.037559 | -0.037138 | 0.065477 | 0.018578 | 0.01063 | -0.0024256 | 0.16254 | 0.066298 | -0.044736 | -0.026065 | -0.031301 | 0.024657 | -0.054588 | 0.13739 | -0.040163 | 56.8274 | -0.095794 | -65.7563 | 56.7983 | 56.9349 | 56.7962 | -66.9096 | 66.5828 | -56.912 | 66.5782 | 66.5916 | 0.008862 | -56.9912 | -56.7993 | -0.28664 | -0.13832 | 123.4503 | 0.86667 | 1.1533 | -0.001753 | -0.14049 | 66.6476 | 66.5683 | 66.7603 | 66.5969 | -56.9768 | 123.4213 | 123.5578 | 123.4191 | 66.5271 | -123.8462
1273.2812 | 123.7564 | -66.6275 | 56.8085 | 0.06235 | -0.048328 | -0.032586 | -0.059793 | -0.039695 | -0.039275 | 0.065477 | 0.019646 | 0.009562 | -0.0034936 | 0.16254 | 0.067367 | -0.049315 | -0.021486 | -0.026723 | 0.006344 | -0.04543 | 0.13281 | -0.031005 | 56.8503 | 0.52233 | -65.8066 | 56.8029 | 56.9212 | 56.7824 | -66.9279 | 66.5965 | -56.8021 | 66.5782 | 66.6008 | 0.004282 | -56.8539 | -56.6757 | -0.30038 | -0.005566 | 123.4778 | 0.82088 | 1.1213 | 0.11268 | -0.02605 | 66.6338 | 66.5821 | 66.7603 | 66.606 | -56.8395 | 123.4304 | 123.5487 | 123.4099 | 67.1498 | -123.7364
1274.2812 | 123.7518 | -66.6504 | 56.8451 | 0.06235 | -0.047259 | -0.032586 | -0.060862 | -0.039695 | -0.038207 | 0.065477 | 0.019646 | 0.009562 | -0.0024256 | 0.16361 | 0.067367 | -0.044736 | -0.021486 | -0.026723 | 0.020079 | -0.054588 | 0.11907 | -0.040163 | 56.8412 | 1.3144 | -65.8295 | 56.7754 | 56.9028 | 56.7733 | -66.9325 | 66.6102 | -56.825 | 66.6057 | 66.6237 | 0.01344 | -56.8997 | -56.726 | -0.28207 | -0.069658 | 123.4915 | 0.82087 | 1.1029 | 0.05775 | -0.071828 | 66.6705 | 66.5958 | 66.7695 | 66.6289 | -56.8853 | 123.4258 | 123.5532 | 123.4237 | 67.9648 | -123.7776
1275.2656 | 123.7015 | -66.6183 | 56.9138 | 0.077612 | -0.047259 | -0.033655 | -0.059793 | -0.039695 | -0.038207 | 0.080738 | 0.021782 | 0.009562 | -0.0034936 | 0.16254 | 0.066298 | -0.03558 | -0.021486 | -0.026723 | 0.024657 | -0.04543 | 0.13281 | -0.040163 | 56.8778 | 0.3346 | -65.7654 | 56.8121 | 56.9349 | 56.8053 | -66.905 | 66.5782 | -56.8891 | 66.5828 | 66.5916 | 0.01344 | -56.9592 | -56.7809 | -0.28664 | -0.10169 | 123.4961 | 0.85293 | 1.1396 | 0.021136 | -0.10844 | 66.643 | 66.5729 | 66.7512 | 66.5969 | -56.9539 | 123.4304 | 123.5532 | 123.4237 | 66.953 | -123.8187
1276.2656 | 123.6603 | -66.6412 | 56.9183 | 0.047088 | -0.048328 | -0.031518 | -0.06193 | -0.038627 | -0.039275 | 0.065477 | 0.022851 | 0.007426 | -0.0024256 | 0.16467 | 0.066298 | -0.044736 | -0.012329 | -0.031301 | 0.010922 | -0.04543 | 0.12823 | -0.040163 | 56.864 | 0.078197 | -65.7975 | 56.7983 | 56.9212 | 56.787 | -66.9141 | 66.6011 | -56.9074 | 66.5965 | 66.6099 | 0.008862 | -56.9638 | -56.7901 | -0.27291 | -0.12001 | 123.5053 | 0.84377 | 1.1167 | 0.002822 | -0.13133 | 66.6522 | 66.5958 | 66.7695 | 66.6289 | -56.9585 | 123.4396 | 123.5624 | 123.4282 | 66.7194 | -123.8325
1277.2656 | 123.7106 | -66.6092 | 56.9183 | 0.06235 | -0.048328 | -0.032586 | -0.059793 | -0.039695 | -0.039275 | 0.080738 | 0.035669 | -0.005394 | -0.0034936 | 0.16361 | 0.066298 | -0.049315 | -0.016908 | -0.017566 | 0.024657 | -0.050009 | 0.14197 | -0.040163 | 56.8686 | 0.49944 | -65.8249 | 56.7983 | 56.9257 | 56.787 | -66.9187 | 66.569 | -56.8937 | 66.5599 | 66.5916 | 0.022597 | -56.9683 | -56.7764 | -0.30953 | -0.12001 | 123.4778 | 0.78425 | 1.0938 | 0.007401 | -0.13133 | 66.6338 | 66.5592 | 66.7512 | 66.5923 | -56.9585 | 123.4075 | 123.5349 | 123.3962 | 67.1086 | -123.8371
1278.2812 | 123.7473 | -66.6229 | 56.8359 | 0.047088 | -0.048328 | -0.033655 | -0.060862 | -0.039695 | -0.041411 | 0.034955 | 0.026055 | 0.002084 | -0.0034936 | 0.16254 | 0.067367 | -0.040158 | -0.016908 | -0.022144 | 0.015501 | -0.050009 | 0.12823 | -0.035584 | 56.8503 | 1.2961 | -65.8433 | 56.7892 | 56.912 | 56.787 | -66.9279 | 66.5873 | -56.8204 | 66.5828 | 66.6008 | 0.01344 | -56.8859 | -56.7077 | -0.30496 | -0.046766 | 123.4732 | 0.77967 | 1.0846 | 0.076063 | -0.048937 | 66.6384 | 66.5729 | 66.7512 | 66.606 | -56.8715 | 123.4121 | 123.5349 | 123.4099 | 67.9191 | -123.7638
1279.2812 | 123.7701 | -66.6138 | 56.8405 | 0.047088 | -0.049396 | -0.032586 | -0.06193 | -0.037559 | -0.038207 | 0.050216 | 0.032464 | -0.003257 | -0.0024256 | 0.16361 | 0.066298 | -0.044736 | -0.021486 | -0.026723 | 0.010922 | -0.04543 | 0.11449 | -0.035584 | 56.8686 | 0.36666 | -65.8158 | 56.7892 | 56.912 | 56.787 | -66.9325 | 66.5782 | -56.8296 | 66.569 | 66.587 | 0.008861 | -56.8859 | -56.726 | -0.31869 | -0.051344 | 123.4824 | 0.79799 | 1.1167 | 0.071485 | -0.053515 | 66.6247 | 66.5683 | 66.7283 | 66.5923 | -56.8761 | 123.4029 | 123.5258 | 123.4008 | 66.9804 | -123.773
1280.2656 | 123.6923 | -66.5955 | 56.9229 | 0.06235 | -0.049396 | -0.033655 | -0.060862 | -0.038627 | -0.039275 | 0.050216 | 0.031396 | -0.003257 | -0.0034936 | 0.16361 | 0.066298 | -0.049315 | -0.021486 | -0.017566 | 0.015501 | -0.04543 | 0.12823 | -0.044742 | 56.8778 | -0.7826 | -65.7883 | 56.7983 | 56.9303 | 56.8145 | -66.9141 | 66.5507 | -56.9074 | 66.5461 | 66.5779 | 0.027176 | -56.9683 | -56.7947 | -0.31869 | -0.12459 | 123.4732 | 0.80715 | 1.1258 | 0.007401 | -0.10844 | 66.611 | 66.55 | 66.7237 | 66.574 | -56.9677 | 123.3938 | 123.5258 | 123.4099 | 65.8129 | -123.8371
1281.2656 | 123.7015 | -66.6 | 56.9183 | 0.031826 | -0.049396 | -0.032586 | -0.06193 | -0.040764 | -0.039275 | 0.034955 | 0.030328 | -0.001121 | -0.0034936 | 0.16254 | 0.06523 | -0.040158 | -0.016908 | -0.017566 | 0.010922 | -0.040851 | 0.14197 | -0.040163 | 56.8961 | -1.593 | -65.7654 | 56.8166 | 56.944 | 56.8145 | -66.8958 | 66.5599 | -56.9074 | 66.5599 | 66.5825 | 0.022597 | -56.9592 | -56.7764 | -0.29579 | -0.10169 | 123.4961 | 0.83462 | 1.1304 | 0.025715 | -0.10386 | 66.611 | 66.5592 | 66.742 | 66.5831 | -56.9585 | 123.4167 | 123.5441 | 123.4145 | 65.007 | -123.8142
1282.2656 | 123.6877 | -66.6138 | 56.9275 | 0.077612 | -0.050464 | -0.032586 | -0.060862 | -0.038627 | -0.038207 | 0.065477 | 0.028191 | -0.001121 | -0.0045626 | 0.16361 | 0.064162 | -0.040158 | -0.021486 | -0.022144 | 0.006344 | -0.040851 | 0.13739 | -0.040163 | 56.9053 | -1.7487 | -65.7608 | 56.8304 | 56.9532 | 56.8282 | -66.8867 | 66.5736 | -56.9211 | 66.5736 | 66.5916 | 0.018019 | -56.9683 | -56.7901 | -0.2729 | -0.097113 | 123.519 | 0.85293 | 1.1258 | 0.025717 | -0.099282 | 66.6201 | 66.5729 | 66.7512 | 66.5923 | -56.9677 | 123.4441 | 123.567 | 123.442 | 64.8651 | -123.8142
1283.2812 | 123.6145 | -66.6504 | 56.9229 | 0.077612 | -0.050464 | -0.032586 | -0.062998 | -0.039695 | -0.040343 | 0.065477 | 0.030328 | -0.002189 | -0.0045626 | 0.16361 | 0.06523 | -0.040158 | -0.021486 | -0.026723 | 0.020079 | -0.036272 | 0.14655 | -0.040163 | 56.8961 | -0.91996 | -65.77 | 56.8075 | 56.9395 | 56.8053 | -66.8958 | 66.6102 | -56.9028 | 66.6102 | 66.6237 | 0.01344 | -56.9592 | -56.7764 | -0.24544 | -0.11543 | 123.5465 | 0.8804 | 1.1258 | 0.016559 | -0.1176 | 66.6705 | 66.6141 | 66.7969 | 66.6289 | -56.9631 | 123.4579 | 123.5899 | 123.4557 | 65.7304 | -123.8187
1284.2812 | 123.7839 | -66.5863 | 56.8954 | 0.077612 | -0.049396 | -0.033655 | -0.060862 | -0.039695 | -0.039275 | 0.080738 | 0.02926 | 0.001016 | -0.0024256 | 0.16467 | 0.066298 | -0.044736 | -0.026065 | -0.022144 | 0.020079 | -0.036272 | 0.13281 | -0.044742 | 56.8961 | 0.2934 | -65.802 | 56.8166 | 56.9395 | 56.8191 | -66.8958 | 66.5416 | -56.8754 | 66.5416 | 66.5642 | 0.022598 | -56.9317 | -56.7626 | -0.30953 | -0.078805 | 123.4824 | 0.78426 | 1.0938 | 0.044025 | -0.076396 | 66.6064 | 66.55 | 66.7191 | 66.5602 | -56.9402 | 123.4029 | 123.5258 | 123.4054 | 66.8797 | -123.7913
1285.2656 | 123.6557 | -66.6 | 56.9504 | 0.077612 | -0.050464 | -0.034723 | -0.059793 | -0.039695 | -0.040343 | 0.065477 | 0.02926 | 0.001016 | -0.0045626 | 0.16467 | 0.06523 | -0.040158 | -0.021486 | -0.017566 | 0.024657 | -0.027115 | 0.12823 | -0.044742 | 56.8961 | -0.031692 | -65.802 | 56.8075 | 56.9349 | 56.8007 | -66.9004 | 66.5553 | -56.9257 | 66.5599 | 66.5825 | 0.027176 | -56.9775 | -56.8221 | -0.30037 | -0.14289 | 123.4961 | 0.79799 | 1.0984 | -0.015485 | -0.14964 | 66.6247 | 66.5729 | 66.7283 | 66.5786 | -56.9951 | 123.4075 | 123.5349 | 123.4008 | 66.5683 | -123.8508
1286.2656 | 123.6557 | -66.6367 | 56.8954 | 0.047088 | -0.049396 | -0.033655 | -0.06193 | -0.040764 | -0.040343 | 0.080738 | 0.031396 | -0.002189 | -0.0045626 | 0.16361 | 0.06523 | -0.044736 | -0.030644 | -0.022144 | 0.015501 | -0.027115 | 0.11907 | -0.040163 | 56.8824 | -0.43004 | -65.7975 | 56.7937 | 56.9257 | 56.8007 | -66.9141 | 66.5965 | -56.8799 | 66.5919 | 66.6145 | 0.018019 | -56.9226 | -56.7764 | -0.27749 | -0.1017 | 123.519 | 0.83919 | 1.1167 | 0.030289 | -0.094711 | 66.6522 | 66.6095 | 66.7557 | 66.606 | -56.9356 | 123.4304 | 123.5624 | 123.4374 | 66.2066 | -123.8096
1287.2656 | 123.6786 | -66.6367 | 56.9321 | 0.047088 | -0.051533 | -0.031518 | -0.059793 | -0.039695 | -0.041411 | 0.050216 | 0.02926 | -5.2e-05 | -0.0045626 | 0.16361 | 0.066298 | -0.044736 | -0.026065 | -0.026723 | 0.001765 | -0.031693 | 0.12365 | -0.049321 | 56.8824 | -0.46667 | -65.8066 | 56.7937 | 56.9257 | 56.8053 | -66.905 | 66.5873 | -56.9303 | 66.5919 | 66.6099 | 0.022598 | -56.9638 | -56.8084 | -0.26833 | -0.13832 | 123.519 | 0.83003 | 1.0984 | -0.006332 | -0.12675 | 66.6384 | 66.605 | 66.7603 | 66.6106 | -56.9814 | 123.4304 | 123.5624 | 123.442 | 66.17 | -123.8371
1288.2812 | 123.6923 | -66.5634 | 56.9641 | 0.031826 | -0.050464 | -0.034723 | -0.060862 | -0.040764 | -0.040343 | 0.065477 | 0.02926 | -5.2e-05 | -0.0066986 | 0.16467 | 0.06523 | -0.044736 | -0.016908 | -0.022144 | 0.015501 | -0.031693 | 0.14197 | -0.049321 | 56.9327 | -0.38883 | -65.7929 | 56.8441 | 56.9761 | 56.8419 | -66.8592 | 66.5141 | -56.9486 | 66.5187 | 66.5413 | 0.027177 | -56.9958 | -56.8221 | -0.29578 | -0.12 | 123.4961 | 0.77053 | 1.0663 | 0.011989 | -0.12217 | 66.5789 | 66.5317 | 66.7054 | 66.5465 | -57.0134 | 123.4075 | 123.5395 | 123.4054 | 66.1746 | -123.8233
1289.2656 | 123.7015 | -66.5863 | 56.8863 | 0.047088 | -0.050464 | -0.034723 | -0.060862 | -0.040764 | -0.039275 | 0.065477 | 0.033532 | -0.006462 | -0.0045626 | 0.16467 | 0.06523 | -0.044736 | -0.021486 | -0.026723 | 0.020079 | -0.040851 | 0.13281 | -0.044742 | 56.8869 | 0.22929 | -65.8387 | 56.8075 | 56.9349 | 56.8099 | -66.905 | 66.5416 | -56.8662 | 66.5416 | 66.5596 | 0.018019 | -56.9271 | -56.7535 | -0.31868 | -0.078807 | 123.4732 | 0.74763 | 1.0663 | 0.048601 | -0.076399 | 66.6064 | 66.5455 | 66.7191 | 66.5648 | -56.931 | 123.3938 | 123.5212 | 123.3962 | 66.8156 | -123.7913
1290.2656 | 123.6511 | -66.5955 | 56.9504 | 0.077612 | -0.050464 | -0.032586 | -0.060862 | -0.039695 | -0.040343 | 0.050216 | 0.021782 | 0.004221 | -0.0034936 | 0.16467 | 0.06523 | -0.03558 | -0.021486 | -0.017566 | 0.006344 | -0.022536 | 0.13281 | -0.049321 | 56.9053 | -0.054586 | -65.8066 | 56.8075 | 56.9395 | 56.8145 | -66.905 | 66.5461 | -56.944 | 66.5599 | 66.5779 | 0.031755 | -56.9729 | -56.8176 | -0.30953 | -0.14289 | 123.5007 | 0.78883 | 1.0984 | -0.010906 | -0.13591 | 66.6018 | 66.5729 | 66.7283 | 66.574 | -56.9997 | 123.4029 | 123.5349 | 123.4099 | 66.5409 | -123.8554
1291.2656 | 123.6694 | -66.6092 | 56.955 | 0.047088 | -0.049396 | -0.032586 | -0.06193 | -0.039695 | -0.039275 | 0.080738 | 0.018578 | 0.01063 | -0.0056306 | 0.16681 | 0.067367 | -0.040158 | -0.016908 | -0.022144 | 0.020079 | -0.027115 | 0.13739 | -0.063057 | 56.9098 | -0.15532 | -65.7929 | 56.8258 | 56.944 | 56.8282 | -66.8867 | 66.5461 | -56.9349 | 66.569 | 66.587 | 0.040913 | -56.9821 | -56.8176 | -0.27748 | -0.12916 | 123.519 | 0.8163 | 1.0938 | -0.010906 | -0.12675 | 66.6293 | 66.5821 | 66.7466 | 66.5923 | -57.018 | 123.435 | 123.5532 | 123.4374 | 66.4539 | -123.8416
1292.2656 | 123.6557 | -66.6092 | 56.955 | 0.06235 | -0.052601 | -0.034723 | -0.060862 | -0.039695 | -0.041411 | 0.065477 | 0.016441 | 0.01063 | -0.0024256 | 0.16254 | 0.06523 | -0.040158 | -0.021486 | -0.022144 | 0.015501 | -0.036272 | 0.14197 | -0.044742 | 56.8915 | -0.12327 | -65.8249 | 56.8075 | 56.9349 | 56.8007 | -66.9004 | 66.5644 | -56.9395 | 66.569 | 66.587 | 0.022598 | -56.9912 | -56.813 | -0.29122 | -0.14747 | 123.5007 | 0.78425 | 1.0755 | -0.020063 | -0.15422 | 66.6247 | 66.5729 | 66.7512 | 66.5877 | -56.9997 | 123.4167 | 123.5441 | 123.4099 | 66.4859 | -123.8554
1293.2812 | 123.7015 | -66.5955 | 56.9138 | 0.06235 | -0.051533 | -0.035791 | -0.06193 | -0.039695 | -0.040343 | 0.065477 | 0.016441 | 0.013835 | -0.0045626 | 0.16681 | 0.066298 | -0.044736 | -0.016908 | -0.026723 | 0.020079 | -0.027115 | 0.13281 | -0.040163 | 56.9098 | -0.72766 | -65.7975 | 56.8258 | 56.944 | 56.8191 | -66.8867 | 66.5553 | -56.8937 | 66.5507 | 66.5687 | 0.01344 | -56.9409 | -56.7809 | -0.29121 | -0.087958 | 123.5053 | 0.79799 | 1.0892 | 0.030293 | -0.094706 | 66.6155 | 66.5683 | 66.7283 | 66.5786 | -56.9539 | 123.4213 | 123.5395 | 123.4145 | 65.8678 | -123.8004
1294.2656 | 123.6694 | -66.5909 | 56.9412 | 0.077612 | -0.050464 | -0.031518 | -0.062998 | -0.039695 | -0.041411 | 0.080738 | 0.016441 | 0.013835 | -0.0045626 | 0.16895 | 0.06523 | -0.040158 | -0.016908 | -0.022144 | 0.015501 | -0.027115 | 0.12823 | -0.044742 | 56.9098 | -0.32473 | -65.7883 | 56.8258 | 56.944 | 56.8282 | -66.8775 | 66.5461 | -56.9257 | 66.5507 | 66.5687 | 0.022598 | -56.9683 | -56.813 | -0.28663 | -0.11542 | 123.5007 | 0.80257 | 1.0892 | 0.002827 | -0.11302 | 66.6064 | 66.5638 | 66.7191 | 66.574 | -56.986 | 123.4167 | 123.5349 | 123.4191 | 66.2662 | -123.8187
1295.2656 | 123.6694 | -66.6229 | 56.9229 | 0.06235 | -0.050464 | -0.033655 | -0.06193 | -0.040764 | -0.039275 | 0.080738 | 0.013237 | 0.015972 | -0.0034936 | 0.16574 | 0.066298 | -0.03558 | -0.021486 | -0.026723 | 0.010922 | -0.031693 | 0.13281 | -0.044742 | 56.8915 | -0.5674 | -65.8295 | 56.7983 | 56.9212 | 56.7962 | -66.905 | 66.5782 | -56.912 | 66.5873 | 66.5962 | 0.018019 | -56.9546 | -56.7901 | -0.28206 | -0.12459 | 123.5144 | 0.79341 | 1.0755 | -0.001756 | -0.12676 | 66.6338 | 66.5912 | 66.7557 | 66.6014 | -56.9677 | 123.4213 | 123.5441 | 123.4191 | 66.0555 | -123.8279
1296.2656 | 123.642 | -66.6 | 56.9366 | 0.047088 | -0.050464 | -0.032586 | -0.060862 | -0.038627 | -0.041411 | 0.095999 | 0.012169 | 0.015972 | -0.0034936 | 0.16574 | 0.06523 | -0.044736 | -0.021486 | -0.026723 | 0.020079 | -0.031693 | 0.14197 | -0.040163 | 56.8961 | -0.48956 | -65.8066 | 56.8029 | 56.9303 | 56.8099 | -66.8958 | 66.5599 | -56.9166 | 66.5553 | 66.5733 | 0.01344 | -56.9683 | -56.7947 | -0.29579 | -0.13374 | 123.4961 | 0.79341 | 1.0892 | -0.006332 | -0.12675 | 66.6201 | 66.5683 | 66.742 | 66.5786 | -56.9768 | 123.4029 | 123.5304 | 123.4099 | 66.1105 | -123.8325
1297.2656 | 123.6557 | -66.6229 | 56.9412 | 0.077612 | -0.051533 | -0.033655 | -0.06193 | -0.038627 | -0.040343 | 0.080738 | 0.010032 | 0.015972 | -0.0066986 | 0.16681 | 0.06523 | -0.03558 | -0.016908 | -0.022144 | 0.015501 | -0.027115 | 0.12365 | -0.049321 | 56.8961 | -0.43462 | -65.8112 | 56.8075 | 56.9303 | 56.8053 | -66.8913 | 66.5736 | -56.9257 | 66.5873 | 66.6008 | 0.027177 | -56.9683 | -56.8176 | -0.26833 | -0.13374 | 123.519 | 0.81172 | 1.08 | -0.010909 | -0.13591 | 66.6384 | 66.5958 | 66.7466 | 66.606 | -56.9905 | 123.4304 | 123.5532 | 123.4282 | 66.1883 | -123.8325
1298.2812 | 123.6786 | -66.5909 | 56.9092 | 0.06235 | -0.051533 | -0.032586 | -0.064067 | -0.037559 | -0.041411 | 0.080738 | 0.013237 | 0.01704 | -0.0045626 | 0.16574 | 0.06523 | -0.040158 | -0.016908 | -0.017566 | 0.024657 | -0.031693 | 0.13281 | -0.049321 | 56.8869 | -0.50788 | -65.8112 | 56.7892 | 56.9166 | 56.7916 | -66.905 | 66.5416 | -56.8845 | 66.5507 | 66.5733 | 0.031755 | -56.9409 | -56.7764 | -0.31411 | -0.12001 | 123.4778 | 0.77968 | 1.0938 | 0.007399 | -0.1176 | 66.6155 | 66.5592 | 66.7237 | 66.574 | -56.9585 | 123.3801 | 123.5075 | 123.3825 | 66.083 | -123.8142
1299.2656 | 123.6374 | -66.5771 | 56.9641 | 0.092874 | -0.050464 | -0.033655 | -0.059793 | -0.038627 | -0.039275 | 0.095999 | 0.016441 | 0.014904 | -0.0056306 | 0.16681 | 0.064162 | -0.040158 | -0.016908 | -0.026723 | 0.010922 | -0.022536 | 0.14655 | -0.044742 | 56.9007 | -0.38883 | -65.7792 | 56.8258 | 56.9395 | 56.8236 | -66.8867 | 66.5324 | -56.9532 | 66.537 | 66.5504 | 0.018019 | -56.9866 | -56.8176 | -0.30953 | -0.13831 | 123.4778 | 0.798 | 1.1075 | -0.024639 | -0.14048 | 66.5881 | 66.5546 | 66.7237 | 66.5602 | -57.0089 | 123.4029 | 123.5166 | 123.4008 | 66.1883 | -123.8508
1300.2656 | 123.6191 | -66.5955 | 56.9412 | 0.077612 | -0.051533 | -0.034723 | -0.062998 | -0.040764 | -0.039275 | 0.080738 | 0.014305 | 0.014904 | -0.0066986 | 0.16574 | 0.06523 | -0.040158 | -0.012329 | -0.022144 | 0.015501 | -0.022536 | 0.14655 | -0.044742 | 56.9053 | 0.47197 | -65.7883 | 56.8121 | 56.9303 | 56.8191 | -66.8913 | 66.5507 | -56.9257 | 66.5553 | 66.5733 | 0.022598 | -56.9638 | -56.7947 | -0.29579 | -0.12916 | 123.5007 | 0.80715 | 1.1029 | -0.010909 | -0.12217 | 66.611 | 66.5729 | 66.742 | 66.5831 | -56.986 | 123.4075 | 123.5258 | 123.4145 | 67.0674 | -123.8325
1301.2656 | 123.6511 | -66.6092 | 56.9412 | 0.06235 | -0.052601 | -0.032586 | -0.06193 | -0.040764 | -0.041411 | 0.050216 | 0.014305 | 0.01704 | -0.0045626 | 0.16681 | 0.064162 | -0.03558 | -0.007751 | -0.026723 | 0.024657 | -0.027115 | 0.13281 | -0.044742 | 56.9053 | -0.52619 | -65.7425 | 56.8121 | 56.9257 | 56.8145 | -66.8958 | 66.5644 | -56.9166 | 66.5736 | 66.5825 | 0.018019 | -56.9683 | -56.8084 | -0.28664 | -0.12916 | 123.5144 | 0.86667 | 1.1533 | -0.015487 | -0.12675 | 66.6338 | 66.5821 | 66.742 | 66.6014 | -56.986 | 123.4213 | 123.5349 | 123.4237 | 66.083 | -123.8371
1302.2656 | 123.587 | -66.6641 | 56.8726 | 0.06235 | -0.052601 | -0.035791 | -0.060862 | -0.039695 | -0.039275 | 0.065477 | 0.013237 | 0.018108 | -0.0045626 | 0.16681 | 0.064162 | -0.040158 | -0.016908 | -0.022144 | 0.010922 | -0.027115 | 0.13739 | -0.044742 | 56.8503 | -0.73681 | -65.8112 | 56.7525 | 56.8891 | 56.7687 | -66.937 | 66.6194 | -56.8616 | 66.624 | 66.642 | 0.022598 | -56.8997 | -56.7352 | -0.27292 | -0.12002 | 123.5144 | 0.85292 | 1.1258 | 0.016548 | -0.10387 | 66.675 | 66.637 | 66.8015 | 66.6472 | -56.9173 | 123.4167 | 123.5532 | 123.4328 | 65.9273 | -123.8096
1303.2812 | 123.7106 | -66.6458 | 56.8909 | 0.06235 | -0.050464 | -0.033655 | -0.06193 | -0.039695 | -0.040343 | 0.080738 | 0.013237 | 0.01704 | -0.0034936 | 0.16681 | 0.063094 | -0.040158 | -0.012329 | -0.017566 | 0.024657 | -0.036272 | 0.13281 | -0.044742 | 56.8595 | -0.72766 | -65.7837 | 56.7754 | 56.8983 | 56.7824 | -66.9279 | 66.6011 | -56.8662 | 66.6057 | 66.6282 | 0.027176 | -56.9271 | -56.7581 | -0.28207 | -0.11543 | 123.5053 | 0.86208 | 1.1442 | 0.007395 | -0.10845 | 66.6705 | 66.6095 | 66.7786 | 66.6335 | -56.9356 | 123.4212 | 123.5441 | 123.4282 | 65.9182 | -123.8188
1304.2656 | 123.6328 | -66.6367 | 56.8954 | 0.06235 | -0.052601 | -0.03686 | -0.060862 | -0.040764 | -0.039275 | 0.095999 | 0.012169 | 0.019177 | -0.0056306 | 0.16681 | 0.066298 | -0.03558 | -0.012329 | -0.012988 | 0.024657 | -0.022536 | 0.14197 | -0.044742 | 56.8595 | -0.5903 | -65.8204 | 56.78 | 56.9028 | 56.787 | -66.9187 | 66.5919 | -56.8708 | 66.6011 | 66.6237 | 0.031754 | -56.918 | -56.7535 | -0.28207 | -0.11543 | 123.4961 | 0.8163 | 1.0984 | 0.007396 | -0.10845 | 66.6613 | 66.6141 | 66.7786 | 66.6243 | -56.9402 | 123.4167 | 123.5395 | 123.4237 | 66.0464 | -123.8142
1305.2656 | 123.7152 | -66.6 | 56.9092 | 0.077612 | -0.053669 | -0.035791 | -0.06193 | -0.038627 | -0.040343 | 0.065477 | 0.0111 | 0.018108 | -0.0034936 | 0.16681 | 0.066298 | -0.040158 | -0.016908 | -0.022144 | 0.010922 | -0.027115 | 0.14655 | -0.053899 | 56.8824 | 0.000359 | -65.8112 | 56.7983 | 56.912 | 56.8007 | -66.9141 | 66.5461 | -56.8983 | 66.5599 | 66.5779 | 0.031755 | -56.9363 | -56.7626 | -0.31411 | -0.11085 | 123.4824 | 0.78883 | 1.1029 | 0.00282 | -0.10844 | 66.611 | 66.5729 | 66.7466 | 66.5831 | -56.9631 | 123.3984 | 123.512 | 123.4008 | 66.6004 | -123.8233
1306.2656 | 123.7518 | -66.5955 | 56.8817 | 0.047088 | -0.052601 | -0.035791 | -0.062998 | -0.039695 | -0.041411 | 0.065477 | 0.0111 | 0.018108 | -0.0056306 | 0.16788 | 0.064162 | -0.049315 | -0.012329 | -0.022144 | 0.024657 | -0.027115 | 0.14197 | -0.044742 | 56.8778 | -0.39341 | -65.8295 | 56.7846 | 56.912 | 56.7824 | -66.9141 | 66.5507 | -56.8571 | 66.5461 | 66.5733 | 0.022598 | -56.9088 | -56.7397 | -0.31869 | -0.097122 | 123.4732 | 0.76594 | 1.0846 | 0.030286 | -0.099292 | 66.6201 | 66.5683 | 66.7374 | 66.5831 | -56.9265 | 123.3801 | 123.5075 | 123.3779 | 66.202 | -123.7959
1307.2656 | 123.7106 | -66.6458 | 56.8542 | 0.06235 | -0.053669 | -0.034723 | -0.062998 | -0.039695 | -0.040343 | 0.065477 | 0.012169 | 0.01704 | -0.0056306 | 0.16467 | 0.06523 | -0.03558 | -0.016908 | -0.017566 | 0.006344 | -0.036272 | 0.14655 | -0.044742 | 56.8412 | 0.35292 | -65.8433 | 56.7525 | 56.8845 | 56.7641 | -66.9416 | 66.6011 | -56.8479 | 66.6102 | 66.6282 | 0.027176 | -56.8905 | -56.7077 | -0.29581 | -0.1017 | 123.487 | 0.80256 | 1.0984 | 0.03028 | -0.090141 | 66.6522 | 66.6095 | 66.7924 | 66.6289 | -56.899 | 123.3984 | 123.5303 | 123.4099 | 66.9987 | -123.7959
1308.2812 | 123.6694 | -66.6687 | 56.8771 | 0.06235 | -0.053669 | -0.033655 | -0.06193 | -0.040764 | -0.04248 | 0.065477 | 0.0111 | 0.019177 | -0.0034936 | 0.16788 | 0.063094 | -0.03558 | -0.007751 | -0.026723 | 0.015501 | -0.027115 | 0.13739 | -0.040163 | 56.8503 | 0.10109 | -65.8249 | 56.7663 | 56.8937 | 56.7641 | -66.9416 | 66.6285 | -56.8616 | 66.6331 | 66.642 | 0.01344 | -56.9043 | -56.7397 | -0.27292 | -0.11086 | 123.519 | 0.84376 | 1.1167 | 0.01655 | -0.11303 | 66.6842 | 66.6416 | 66.8061 | 66.6609 | -56.9173 | 123.435 | 123.5624 | 123.4328 | 66.7698 | -123.8188
1309.2656 | 123.674 | -66.6 | 56.8954 | 0.077612 | -0.053669 | -0.032586 | -0.06193 | -0.038627 | -0.040343 | 0.080738 | 0.012169 | 0.01704 | -0.0066986 | 0.16681 | 0.064162 | -0.049315 | -0.016908 | -0.026723 | 0.029236 | -0.022536 | 0.14655 | -0.044742 | 56.864 | 0.27508 | -65.8341 | 56.7617 | 56.8937 | 56.7733 | -66.9325 | 66.5553 | -56.8662 | 66.5507 | 66.5733 | 0.018019 | -56.918 | -56.7489 | -0.33242 | -0.13375 | 123.4641 | 0.76594 | 1.0984 | -0.001761 | -0.12218 | 66.6293 | 66.5775 | 66.7466 | 66.5831 | -56.9402 | 123.3617 | 123.4937 | 123.3733 | 66.8751 | -123.8279
1310.2656 | 123.7198 | -66.6412 | 56.8405 | 0.077612 | -0.053669 | -0.034723 | -0.064067 | -0.040764 | -0.041411 | 0.065477 | 0.012169 | 0.018108 | -0.0045626 | 0.16681 | 0.063094 | -0.044736 | -0.007751 | -0.026723 | 0.024657 | -0.022536 | 0.12365 | -0.044742 | 56.8366 | 0.52691 | -65.8661 | 56.7525 | 56.88 | 56.7504 | -66.9462 | 66.5965 | -56.8159 | 66.5965 | 66.6145 | 0.018019 | -56.8631 | -56.7169 | -0.30496 | -0.087972 | 123.4778 | 0.77509 | 1.08 | 0.039435 | -0.090143 | 66.6659 | 66.6187 | 66.7649 | 66.6335 | -56.8853 | 123.3938 | 123.5212 | 123.3916 | 67.1681 | -123.7867
1311.2656 | 123.7518 | -66.6458 | 56.8451 | 0.047088 | -0.054738 | -0.034723 | -0.06193 | -0.039695 | -0.041411 | 0.050216 | 0.014305 | 0.018108 | -0.0045626 | 0.16574 | 0.06523 | -0.040158 | -0.016908 | -0.017566 | 0.020079 | -0.022536 | 0.13281 | -0.040163 | 56.8366 | -0.16905 | -65.8616 | 56.7525 | 56.8754 | 56.755 | -66.9508 | 66.6056 | -56.825 | 66.6057 | 66.6282 | 0.022597 | -56.8676 | -56.7123 | -0.30496 | -0.09255 | 123.4824 | 0.78424 | 1.0892 | 0.030278 | -0.090143 | 66.6659 | 66.6233 | 66.7786 | 66.6289 | -56.8853 | 123.3984 | 123.5212 | 123.4008 | 66.4768 | -123.7959
1312.2656 | 123.7747 | -66.5588 | 56.8863 | 0.06235 | -0.052601 | -0.035791 | -0.06193 | -0.039695 | -0.041411 | 0.080738 | 0.0111 | 0.020245 | -0.0045626 | 0.16788 | 0.063094 | -0.040158 | -0.012329 | -0.017566 | 0.029236 | -0.031693 | 0.14197 | -0.044742 | 56.8869 | 0.087354 | -65.8295 | 56.7983 | 56.9349 | 56.8053 | -66.9004 | 66.5141 | -56.8571 | 66.5187 | 66.5413 | 0.027176 | -56.918 | -56.7443 | -0.34157 | -0.087964 | 123.4458 | 0.72932 | 1.0709 | 0.048601 | -0.080977 | 66.5881 | 66.5271 | 66.7008 | 66.5465 | -56.931 | 123.3572 | 123.4937 | 123.3642 | 66.6462 | -123.7867
1313.2812 | 123.6282 | -66.6458 | 56.9229 | 0.06235 | -0.054738 | -0.033655 | -0.06193 | -0.040764 | -0.040343 | 0.065477 | 0.0111 | 0.01704 | -0.0045626 | 0.16788 | 0.064162 | -0.040158 | -0.012329 | -0.017566 | 0.010922 | -0.027115 | 0.14655 | -0.049321 | 56.864 | 0.000359 | -65.8524 | 56.7663 | 56.8891 | 56.7824 | -66.9325 | 66.5965 | -56.912 | 66.6057 | 66.6282 | 0.031755 | -56.95 | -56.7764 | -0.28665 | -0.15664 | 123.5099 | 0.7934 | 1.08 | -0.033806 | -0.14049 | 66.6567 | 66.6187 | 66.7924 | 66.6335 | -56.9722 | 123.4121 | 123.5349 | 123.4282 | 66.6462 | -123.8554
1314.2656 | 123.7518 | -66.6183 | 56.8085 | 0.031826 | -0.054738 | -0.035791 | -0.06193 | -0.039695 | -0.039275 | 0.065477 | 0.013237 | 0.019177 | -0.0045626 | 0.16788 | 0.063094 | -0.040158 | -0.016908 | -0.026723 | 0.010922 | -0.027115 | 0.13739 | -0.049321 | 56.832 | 0.43992 | -65.8799 | 56.7525 | 56.8708 | 56.7412 | -66.9462 | 66.569 | -56.7976 | 66.5782 | 66.5916 | 0.022598 | -56.8356 | -56.6711 | -0.32785 | -0.055929 | 123.4503 | 0.73846 | 1.0663 | 0.062321 | -0.067258 | 66.6293 | 66.5912 | 66.7557 | 66.6014 | -56.8578 | 123.3709 | 123.4891 | 123.3596 | 67.0583 | -123.7547
1315.2656 | 123.7656 | -66.6 | 56.8451 | 0.077612 | -0.052601 | -0.034723 | -0.062998 | -0.040764 | -0.039275 | 0.065477 | 0.012169 | 0.018108 | -0.0045626 | 0.16574 | 0.063094 | -0.03558 | -0.012329 | -0.022144 | 0.015501 | -0.022536 | 0.13281 | -0.040163 | 56.8503 | 0.73295 | -65.9028 | 56.7617 | 56.8845 | 56.7687 | -66.9325 | 66.5599 | -56.8296 | 66.5645 | 66.5779 | 0.018019 | -56.8676 | -56.7123 | -0.33242 | -0.083393 | 123.4503 | 0.69726 | 1.0297 | 0.039435 | -0.076407 | 66.6155 | 66.5775 | 66.7328 | 66.5877 | -56.8853 | 123.3617 | 123.4846 | 123.3687 | 67.333 | -123.7776
1316.2656 | 123.7473 | -66.5726 | 56.8542 | 0.077612 | -0.053669 | -0.032586 | -0.06193 | -0.040764 | -0.040343 | 0.080738 | 0.010032 | 0.01704 | -0.0066986 | 0.16895 | 0.064162 | -0.031001 | -0.012329 | -0.017566 | 0.020079 | -0.031693 | 0.15112 | -0.040163 | 56.8824 | 0.84742 | -65.8524 | 56.7983 | 56.9212 | 56.7916 | -66.9004 | 66.5324 | -56.8342 | 66.5416 | 66.555 | 0.022597 | -56.8859 | -56.7031 | -0.32784 | -0.05592 | 123.4549 | 0.72016 | 1.048 | 0.066909 | -0.062669 | 66.5926 | 66.5409 | 66.7237 | 66.5602 | -56.8944 | 123.3709 | 123.4937 | 123.3641 | 67.42 | -123.7547
1317.2656 | 123.7427 | -66.5955 | 56.8222 | 0.06235 | -0.055806 | -0.033655 | -0.062998 | -0.040764 | -0.040343 | 0.065477 | 0.0111 | 0.01704 | -0.0045626 | 0.16788 | 0.064162 | -0.040158 | -0.012329 | -0.022144 | 0.038393 | -0.031693 | 0.13739 | -0.044742 | 56.8503 | 1.1359 | -65.8982 | 56.7571 | 56.8891 | 56.7641 | -66.9325 | 66.5507 | -56.7838 | 66.5553 | 66.5733 | 0.022598 | -56.8539 | -56.6848 | -0.337 | -0.065084 | 123.4458 | 0.69726 | 1.0343 | 0.066902 | -0.058098 | 66.6339 | 66.5638 | 66.7328 | 66.5831 | -56.8669 | 123.3526 | 123.4846 | 123.3596 | 67.7313 | -123.7547
1318.2812 | 123.6603 | -66.5955 | 56.9138 | 0.077612 | -0.056875 | -0.035791 | -0.062998 | -0.040764 | -0.040343 | 0.065477 | 0.012169 | 0.01704 | -0.0066986 | 0.16788 | 0.063094 | -0.03558 | -0.016908 | -0.022144 | 0.024657 | -0.031693 | 0.14197 | -0.044742 | 56.8366 | 1.548 | -65.8753 | 56.7525 | 56.8754 | 56.755 | -66.9462 | 66.5507 | -56.8891 | 66.5599 | 66.5733 | 0.022598 | -56.9454 | -56.7718 | -0.35074 | -0.16121 | 123.432 | 0.72015 | 1.0709 | -0.038386 | -0.15881 | 66.6201 | 66.5638 | 66.7374 | 66.5786 | -56.9585 | 123.348 | 123.4708 | 123.3504 | 68.1434 | -123.86
1319.2656 | 123.7473 | -66.6641 | 56.7993 | 0.047088 | -0.054738 | -0.03686 | -0.060862 | -0.040764 | -0.039275 | 0.065477 | 0.012169 | 0.015972 | -0.0056306 | 0.16574 | 0.064162 | -0.040158 | -0.016908 | -0.017566 | 0.015501 | -0.022536 | 0.13739 | -0.044742 | 56.7999 | 1.7357 | -65.9257 | 56.7068 | 56.8342 | 56.7046 | -66.9828 | 66.6194 | -56.7838 | 66.624 | 66.6466 | 0.027176 | -56.8219 | -56.6619 | -0.3187 | -0.092558 | 123.4641 | 0.73845 | 1.0572 | 0.034848 | -0.09473 | 66.6796 | 66.6416 | 66.8015 | 66.6472 | -56.8441 | 123.3709 | 123.4983 | 123.3687 | 68.3998 | -123.7821
1320.2656 | 123.7335 | -66.6733 | 56.7764 | 0.077612 | -0.055806 | -0.034723 | -0.062998 | -0.039695 | -0.040343 | 0.050216 | 0.014305 | 0.015972 | -0.0045626 | 0.16788 | 0.06523 | -0.040158 | -0.003172 | -0.017566 | 0.024657 | -0.036272 | 0.15112 | -0.035584 | 56.7999 | 1.4381 | -65.9074 | 56.7251 | 56.8433 | 56.7183 | -66.9782 | 66.6377 | -56.7518 | 66.6331 | 66.6557 | 0.018018 | -56.8127 | -56.6253 | -0.30497 | -0.051356 | 123.4732 | 0.76592 | 1.0709 | 0.066893 | -0.058107 | 66.6979 | 66.637 | 66.8244 | 66.6701 | -56.812 | 123.3984 | 123.5166 | 123.3916 | 68.1114 | -123.7547
1321.2656 | 123.7015 | -66.6367 | 56.8222 | 0.047088 | -0.054738 | -0.03686 | -0.06193 | -0.038627 | -0.040343 | 0.065477 | 0.013237 | 0.01704 | -0.0066986 | 0.16788 | 0.064162 | -0.031001 | -0.003172 | -0.022144 | 0.015501 | -0.031693 | 0.15112 | -0.044742 | 56.8274 | 1.3511 | -65.889 | 56.7342 | 56.8708 | 56.7412 | -66.9508 | 66.5919 | -56.8067 | 66.6057 | 66.6145 | 0.022598 | -56.8539 | -56.6711 | -0.31412 | -0.087976 | 123.4641 | 0.74762 | 1.0617 | 0.048588 | -0.080991 | 66.6522 | 66.605 | 66.7878 | 66.6335 | -56.8669 | 123.3709 | 123.5075 | 123.3779 | 67.9877 | -123.773
1322.2656 | 123.7106 | -66.6229 | 56.8497 | 0.06235 | -0.053669 | -0.035791 | -0.06193 | -0.040764 | -0.041411 | 0.050216 | 0.012169 | 0.01704 | -0.0045626 | 0.17002 | 0.060957 | -0.03558 | -0.012329 | -0.017566 | 0.024657 | -0.027115 | 0.13739 | -0.040163 | 56.8549 | 0.93899 | -65.8845 | 56.7754 | 56.8937 | 56.7641 | -66.9187 | 66.5828 | -56.825 | 66.5873 | 66.6054 | 0.022597 | -56.8768 | -56.7123 | -0.2958 | -0.074235 | 123.4778 | 0.73846 | 1.0343 | 0.044016 | -0.085563 | 66.6476 | 66.5958 | 66.7603 | 66.6106 | -56.8898 | 123.3984 | 123.5166 | 123.387 | 67.5619 | -123.7684
1323.2812 | 123.7244 | -66.5268 | 56.8954 | 0.06235 | -0.054738 | -0.033655 | -0.060862 | -0.039695 | -0.039275 | 0.050216 | 0.013237 | 0.015972 | -0.0056306 | 0.16895 | 0.063094 | -0.044736 | -0.012329 | -0.017566 | 0.020079 | -0.017957 | 0.12823 | -0.035584 | 56.8778 | 0.56812 | -65.8524 | 56.7892 | 56.9166 | 56.7916 | -66.905 | 66.4912 | -56.8754 | 66.4821 | 66.5092 | 0.018018 | -56.9134 | -56.7672 | -0.37819 | -0.10628 | 123.4046 | 0.67438 | 1.0526 | 0.021132 | -0.10387 | 66.5469 | 66.5088 | 66.655 | 66.5145 | -56.931 | 123.316 | 123.4434 | 123.3184 | 67.0949 | -123.8004
1324.2656 | 123.7289 | -66.5451 | 56.8817 | 0.047088 | -0.054738 | -0.03686 | -0.062998 | -0.039695 | -0.040343 | 0.050216 | 0.013237 | 0.018108 | -0.0056306 | 0.17002 | 0.064162 | -0.03558 | 0.005985 | -0.022144 | 0.020079 | -0.031693 | 0.14655 | -0.044742 | 56.8961 | 0.75585 | -65.8295 | 56.8166 | 56.9532 | 56.8191 | -66.8775 | 66.5004 | -56.8616 | 66.5095 | 66.523 | 0.022598 | -56.9134 | -56.7352 | -0.33241 | -0.065072 | 123.4412 | 0.71559 | 1.048 | 0.071493 | -0.062663 | 66.5652 | 66.5134 | 66.6917 | 66.5511 | -56.9265 | 123.3617 | 123.4983 | 123.3642 | 67.301 | -123.7592
1325.2656 | 123.7473 | -66.5543 | 56.9138 | 0.06235 | -0.054738 | -0.035791 | -0.064067 | -0.039695 | -0.039275 | 0.050216 | 0.015373 | 0.01704 | -0.0066986 | 0.16788 | 0.063094 | -0.03558 | -0.003172 | -0.017566 | 0.033814 | -0.022536 | 0.14655 | -0.044742 | 56.8915 | 0.77416 | -65.8478 | 56.8166 | 56.9395 | 56.8191 | -66.8821 | 66.5095 | -56.8799 | 66.5187 | 66.5367 | 0.027176 | -56.9363 | -56.7672 | -0.32783 | -0.097115 | 123.4458 | 0.70643 | 1.0343 | 0.025715 | -0.094706 | 66.5881 | 66.5317 | 66.7008 | 66.5511 | -56.9585 | 123.3709 | 123.4937 | 123.3733 | 67.3284 | -123.7959
1326.2656 | 123.7473 | -66.5497 | 56.9092 | 0.06235 | -0.055806 | -0.034723 | -0.064067 | -0.038627 | -0.038207 | 0.050216 | 0.012169 | 0.01704 | -0.0056306 | 0.17002 | 0.064162 | -0.040158 | 0.010564 | -0.017566 | 0.024657 | -0.031693 | 0.14197 | -0.049321 | 56.9053 | 0.45823 | -65.8341 | 56.835 | 56.9532 | 56.8419 | -66.8684 | 66.5004 | -56.8845 | 66.5095 | 66.5321 | 0.031755 | -56.9409 | -56.7672 | -0.31867 | -0.074224 | 123.4549 | 0.71559 | 1.0343 | 0.044027 | -0.067236 | 66.5743 | 66.518 | 66.6916 | 66.5602 | -56.9585 | 123.3846 | 123.5029 | 123.3916 | 67.0079 | -123.7775
1327.2656 | 123.7381 | -66.5543 | 56.9046 | 0.06235 | -0.055806 | -0.034723 | -0.062998 | -0.039695 | -0.041411 | 0.080738 | 0.010032 | 0.018108 | -0.0045626 | 0.16895 | 0.063094 | -0.040158 | 0.001407 | -0.017566 | 0.015501 | -0.022536 | 0.14655 | -0.035584 | 56.9144 | 0.66885 | -65.8524 | 56.835 | 56.9669 | 56.8282 | -66.8638 | 66.5187 | -56.8891 | 66.5141 | 66.5367 | 0.018018 | -56.9271 | -56.7581 | -0.30952 | -0.069646 | 123.4687 | 0.70185 | 1.0114 | 0.062341 | -0.076394 | 66.5698 | 66.5317 | 66.7008 | 66.5557 | -56.9402 | 123.3892 | 123.5212 | 123.3825 | 67.2231 | -123.7684
1328.2812 | 123.6969 | -66.5863 | 56.8771 | 0.047088 | -0.056875 | -0.035791 | -0.065135 | -0.040764 | -0.04248 | 0.065477 | 0.012169 | 0.01704 | -0.0077666 | 0.17002 | 0.062025 | -0.03558 | 0.015142 | -0.026723 | 0.033814 | -0.017957 | 0.11907 | -0.040163 | 56.8915 | 0.36666 | -65.8982 | 56.7983 | 56.912 | 56.7824 | -66.905 | 66.5461 | -56.8433 | 66.5507 | 66.5596 | 0.01344 | -56.8951 | -56.7581 | -0.31868 | -0.078808 | 123.4778 | 0.6881 | 1.0068 | 0.034864 | -0.094714 | 66.6201 | 66.5683 | 66.7054 | 66.6014 | -56.9173 | 123.3846 | 123.4983 | 123.3687 | 66.953 | -123.7821
1329.2656 | 123.7335 | -66.5405 | 56.9 | 0.047088 | -0.055806 | -0.034723 | -0.064067 | -0.039695 | -0.04248 | 0.034955 | 0.013237 | 0.01704 | -0.0066986 | 0.17002 | 0.063094 | -0.031001 | 0.015142 | -0.017566 | 0.029236 | -0.027115 | 0.10992 | -0.035584 | 56.9144 | 0.67801 | -65.8661 | 56.8166 | 56.9349 | 56.787 | -66.8821 | 66.5049 | -56.8708 | 66.5095 | 66.523 | 0.018018 | -56.9271 | -56.7901 | -0.34157 | -0.083382 | 123.4549 | 0.67438 | 1.0159 | 0.034869 | -0.11302 | 66.5698 | 66.5134 | 66.6504 | 66.5557 | -56.9356 | 123.3572 | 123.4754 | 123.3275 | 67.2185 | -123.7821
1330.2656 | 123.7518 | -66.6138 | 56.8359 | 0.047088 | -0.057943 | -0.034723 | -0.064067 | -0.040764 | -0.04248 | 0.095999 | 0.013237 | 0.018108 | -0.0088356 | 0.17002 | 0.062025 | -0.03558 | 0.015142 | -0.017566 | 0.042971 | -0.022536 | 0.12823 | -0.035584 | 56.8824 | 0.96189 | -65.9211 | 56.7983 | 56.9166 | 56.7687 | -66.905 | 66.5782 | -56.793 | 66.5782 | 66.5962 | 0.018018 | -56.8585 | -56.7077 | -0.29122 | -0.037609 | 123.4961 | 0.69268 | 0.9839 | 0.080642 | -0.067251 | 66.6567 | 66.5912 | 66.742 | 66.6289 | -56.8715 | 123.4121 | 123.5303 | 123.3825 | 67.5757 | -123.7409
1331.2656 | 123.6557 | -66.6367 | 56.8451 | 0.047088 | -0.056875 | -0.034723 | -0.064067 | -0.041832 | -0.04248 | 0.050216 | 0.012169 | 0.01704 | -0.0077666 | 0.17002 | 0.062025 | -0.03558 | 0.005985 | -0.017566 | 0.033814 | -0.031693 | 0.12823 | -0.044742 | 56.8595 | 1.1176 | -65.9348 | 56.7663 | 56.8891 | 56.7641 | -66.9325 | 66.5919 | -56.8113 | 66.6011 | 66.6191 | 0.027176 | -56.8768 | -56.7169 | -0.2958 | -0.078815 | 123.4961 | 0.70183 | 0.99763 | 0.044014 | -0.080986 | 66.6705 | 66.605 | 66.7649 | 66.6426 | -56.8898 | 123.4029 | 123.5258 | 123.4008 | 67.7542 | -123.7776
1332.2656 | 123.6557 | -66.6367 | 56.8726 | 0.047088 | -0.056875 | -0.035791 | -0.064067 | -0.041832 | -0.041411 | 0.065477 | 0.013237 | 0.01704 | -0.0066986 | 0.17002 | 0.064162 | -0.044736 | 0.010564 | -0.022144 | 0.047549 | -0.022536 | 0.13739 | -0.040163 | 56.8595 | 0.67801 | -65.944 | 56.7709 | 56.8891 | 56.7595 | -66.937 | 66.5965 | -56.825 | 66.5919 | 66.6145 | 0.018019 | -56.8951 | -56.7352 | -0.30038 | -0.1017 | 123.4961 | 0.69267 | 0.99305 | 0.016548 | -0.11303 | 66.6842 | 66.6141 | 66.774 | 66.6472 | -56.9127 | 123.4075 | 123.5258 | 123.3962 | 67.3147 | -123.8096
1333.2812 | 123.7198 | -66.6092 | 56.8726 | 0.031826 | -0.057943 | -0.035791 | -0.062998 | -0.039695 | -0.04248 | 0.050216 | 0.0111 | 0.01704 | -0.0056306 | 0.17108 | 0.064162 | -0.03558 | 0.005985 | -0.022144 | 0.052128 | -0.022536 | 0.11907 | -0.040163 | 56.864 | 0.64596 | -65.9394 | 56.7617 | 56.8937 | 56.7412 | -66.9325 | 66.569 | -56.8204 | 66.5736 | 66.587 | 0.018019 | -56.8951 | -56.7535 | -0.32327 | -0.11086 | 123.4732 | 0.66978 | 0.99305 | 0.021127 | -0.13135 | 66.6613 | 66.5867 | 66.7283 | 66.6152 | -56.9127 | 123.3709 | 123.5029 | 123.3504 | 67.2551 | -123.805
1334.2656 | 123.6191 | -66.6733 | 56.8771 | 0.077612 | -0.057943 | -0.035791 | -0.062998 | -0.041832 | -0.041411 | 0.080738 | 0.010032 | 0.01704 | -0.0066986 | 0.17108 | 0.062025 | -0.040158 | 0.010564 | -0.012988 | 0.047549 | -0.022536 | 0.13281 | -0.040163 | 56.8503 | 0.59101 | -65.9623 | 56.7525 | 56.8845 | 56.7412 | -66.9462 | 66.6331 | -56.8296 | 66.6331 | 66.6603 | 0.027175 | -56.8997 | -56.7443 | -0.27292 | -0.12459 | 123.5236 | 0.71098 | 0.9839 | 0.007392 | -0.13592 | 66.7208 | 66.6507 | 66.8061 | 66.6838 | -56.9173 | 123.4258 | 123.5578 | 123.4145 | 67.2643 | -123.8233
1335.2656 | 123.587 | -66.687 | 56.8588 | 0.06235 | -0.056875 | -0.033655 | -0.062998 | -0.041832 | -0.045685 | 0.080738 | 0.012169 | 0.01704 | -0.0066986 | 0.17215 | 0.063094 | -0.03558 | 0.015142 | -0.026723 | 0.042971 | -0.027115 | 0.13281 | -0.040163 | 56.8412 | 0.055303 | -65.9715 | 56.7525 | 56.8662 | 56.7137 | -66.9599 | 66.6468 | -56.8159 | 66.6514 | 66.6603 | 0.01344 | -56.8859 | -56.726 | -0.27292 | -0.10628 | 123.5282 | 0.71555 | 0.98848 | 0.007388 | -0.14508 | 66.73 | 66.6599 | 66.8198 | 66.7022 | -56.899 | 123.4396 | 123.5532 | 123.4008 | 66.7423 | -123.8188
1336.2656 | 123.6237 | -66.6641 | 56.8726 | 0.031826 | -0.056875 | -0.033655 | -0.065135 | -0.040764 | -0.04248 | 0.050216 | 0.0089643 | 0.01704 | -0.0077666 | 0.17215 | 0.064162 | -0.03558 | 0.015142 | -0.008409 | 0.029236 | -0.027115 | 0.13281 | -0.040163 | 56.8686 | 0.45823 | -65.9577 | 56.7709 | 56.8891 | 56.7641 | -66.9279 | 66.624 | -56.8433 | 66.6285 | 66.6557 | 0.031754 | -56.8997 | -56.7398 | -0.26376 | -0.1017 | 123.5327 | 0.7064 | 0.97016 | 0.016548 | -0.10845 | 66.6934 | 66.637 | 66.7969 | 66.6793 | -56.9127 | 123.435 | 123.5532 | 123.4282 | 67.1224 | -123.8004
1337.2656 | 123.587 | -66.6458 | 56.8954 | 0.06235 | -0.057943 | -0.034723 | -0.06193 | -0.040764 | -0.043548 | 0.050216 | 0.010032 | 0.01704 | -0.0066986 | 0.17108 | 0.063094 | -0.040158 | 0.015142 | -0.012988 | 0.042971 | -0.027115 | 0.13739 | -0.035584 | 56.8824 | 0.29797 | -65.9257 | 56.7846 | 56.9074 | 56.7733 | -66.9141 | 66.6102 | -56.8525 | 66.6057 | 66.6328 | 0.022596 | -56.9226 | -56.7581 | -0.26833 | -0.11085 | 123.5282 | 0.72014 | 0.98848 | 0.011974 | -0.12218 | 66.6888 | 66.6187 | 66.7832 | 66.661 | -56.931 | 123.4304 | 123.5532 | 123.4191 | 66.9438 | -123.8096
1338.2812 | 123.8022 | -66.6367 | 56.8314 | 0.047088 | -0.059011 | -0.035791 | -0.064067 | -0.039695 | -0.04248 | 0.050216 | 0.0111 | 0.01704 | -0.0056306 | 0.17108 | 0.062025 | -0.03558 | 0.015142 | -0.012988 | 0.033814 | -0.031693 | 0.12823 | -0.035584 | 56.8824 | 0.15604 | -65.8982 | 56.7937 | 56.9074 | 56.7595 | -66.9096 | 66.6011 | -56.7975 | 66.6011 | 66.6237 | 0.022596 | -56.8631 | -56.7031 | -0.27291 | -0.037611 | 123.519 | 0.73846 | 1.0114 | 0.076061 | -0.071831 | 66.6705 | 66.605 | 66.7649 | 66.6518 | -56.8669 | 123.4304 | 123.5441 | 123.3962 | 66.7927 | -123.7409
1339.2656 | 123.6053 | -66.5909 | 56.9229 | 0.031826 | -0.056875 | -0.034723 | -0.064067 | -0.040764 | -0.043548 | 0.050216 | 0.010032 | 0.01704 | -0.0066986 | 0.17215 | 0.063094 | -0.026423 | -0.003172 | -0.022144 | 0.033814 | -0.022536 | 0.12823 | -0.044742 | 56.9053 | 0.21556 | -65.8661 | 56.8075 | 56.9349 | 56.7962 | -66.8821 | 66.5461 | -56.8891 | 66.5645 | 66.5687 | 0.022598 | -56.9454 | -56.7947 | -0.29121 | -0.11543 | 123.4961 | 0.72473 | 1.0159 | 0.01198 | -0.12676 | 66.6247 | 66.5683 | 66.7191 | 66.5877 | -56.9677 | 123.3984 | 123.5258 | 123.387 | 66.8064 | -123.805
1340.2656 | 123.6877 | -66.6138 | 56.9 | 0.06235 | -0.059011 | -0.034723 | -0.064067 | -0.041832 | -0.043548 | 0.080738 | 0.010032 | 0.015972 | -0.0066986 | 0.17429 | 0.062025 | -0.031001 | -0.003172 | -0.022144 | 0.052128 | -0.022536 | 0.12365 | -0.035584 | 56.8869 | 0.06904 | -65.9119 | 56.78 | 56.9028 | 56.755 | -66.9141 | 66.5782 | -56.8479 | 66.5828 | 66.5916 | 0.01344 | -56.9226 | -56.7764 | -0.30038 | -0.12001 | 123.5007 | 0.70184 | 1.0022 | 0.002819 | -0.14507 | 66.6659 | 66.5912 | 66.7374 | 66.6106 | -56.9356 | 123.3938 | 123.5166 | 123.3687 | 66.6828 | -123.8142
1341.2656 | 123.6649 | -66.5817 | 56.9229 | 0.06235 | -0.057943 | -0.034723 | -0.06193 | -0.040764 | -0.04248 | 0.080738 | 0.0111 | 0.015972 | -0.0088356 | 0.17108 | 0.062025 | -0.03558 | -0.003172 | -0.012988 | 0.038393 | -0.027115 | 0.13281 | -0.040163 | 56.919 | -2.5179 | -65.8478 | 56.8258 | 56.9486 | 56.8007 | -66.8729 | 66.5416 | -56.8845 | 66.5461 | 66.5687 | 0.027175 | -56.95 | -56.7901 | -0.29121 | -0.097114 | 123.5007 | 0.73389 | 1.0251 | 0.025716 | -0.12218 | 66.6201 | 66.5546 | 66.7145 | 66.5786 | -56.9631 | 123.4075 | 123.5304 | 123.3825 | 64.0638 | -123.7958
1342.2656 | 123.6603 | -66.5726 | 56.9366 | 0.016564 | -0.061148 | -0.034723 | -0.064067 | -0.040764 | -0.043548 | 0.080738 | 0.0111 | 0.01704 | -0.0066986 | 0.17108 | 0.059889 | -0.03558 | 0.001407 | -0.012988 | 0.033814 | -0.022536 | 0.13281 | -0.031005 | 56.9327 | -3.7588 | -65.8112 | 56.835 | 56.9578 | 56.8191 | -66.8592 | 66.5416 | -56.9028 | 66.537 | 66.5596 | 0.018017 | -56.9592 | -56.8038 | -0.28663 | -0.10169 | 123.5053 | 0.76137 | 1.048 | 0.02114 | -0.1176 | 66.6064 | 66.55 | 66.7054 | 66.574 | -56.9677 | 123.4075 | 123.5304 | 123.3916 | 62.8138 | -123.7958
1343.2812 | 123.6191 | -66.5726 | 56.9275 | 0.047088 | -0.057943 | -0.033655 | -0.064067 | -0.040764 | -0.043548 | 0.065477 | 0.0111 | 0.019177 | -0.0077666 | 0.17215 | 0.063094 | -0.031001 | -0.007751 | -0.003831 | 0.038393 | -0.027115 | 0.14655 | -0.044742 | 56.919 | -3.104 | -65.8341 | 56.8212 | 56.9486 | 56.8053 | -66.8729 | 66.5278 | -56.8891 | 66.5416 | 66.5687 | 0.040911 | -56.9546 | -56.7809 | -0.30036 | -0.10627 | 123.4916 | 0.73847 | 1.0388 | 0.021139 | -0.12217 | 66.611 | 66.5455 | 66.7191 | 66.5648 | -56.9722 | 123.3938 | 123.5212 | 123.3779 | 63.4686 | -123.8004
1344.2656 | 123.6099 | -66.6138 | 56.8771 | 0.06235 | -0.059011 | -0.034723 | -0.065135 | -0.038627 | -0.044616 | 0.095999 | 0.0111 | 0.018108 | -0.0077666 | 0.17215 | 0.063094 | -0.031001 | 0.001407 | -0.017566 | 0.033814 | -0.017957 | 0.12823 | -0.040163 | 56.8549 | 0.018674 | -65.9074 | 56.7571 | 56.88 | 56.7412 | -66.9325 | 66.5736 | -56.8433 | 66.5828 | 66.5962 | 0.022597 | -56.8951 | -56.7489 | -0.31869 | -0.12002 | 123.4687 | 0.70641 | 1.0251 | 0.002814 | -0.13592 | 66.6476 | 66.5958 | 66.742 | 66.6152 | -56.9173 | 123.3709 | 123.4937 | 123.355 | 66.6324 | -123.8096
1345.2656 | 123.6374 | -66.6458 | 56.8588 | 0.047088 | -0.06008 | -0.035791 | -0.062998 | -0.0429 | -0.043548 | 0.050216 | 0.012169 | 0.019177 | -0.0066986 | 0.17322 | 0.062025 | -0.03558 | 0.019721 | -0.017566 | 0.052128 | -0.022536 | 0.13281 | -0.035584 | 56.864 | 0.59559 | -65.8982 | 56.7617 | 56.8937 | 56.7504 | -66.9279 | 66.6102 | -56.8067 | 66.6102 | 66.6282 | 0.018018 | -56.8814 | -56.726 | -0.28207 | -0.097126 | 123.5099 | 0.74761 | 1.0297 | 0.03486 | -0.10845 | 66.6979 | 66.6233 | 66.7786 | 66.6655 | -56.8944 | 123.4075 | 123.5395 | 123.3962 | 67.2414 | -123.7867
1346.2656 | 123.6649 | -66.6504 | 56.8817 | 0.077612 | -0.06008 | -0.035791 | -0.065135 | -0.040764 | -0.041411 | 0.080738 | 0.0111 | 0.019177 | -0.0056306 | 0.17322 | 0.062025 | -0.031001 | 0.015142 | -0.012988 | 0.042971 | -0.027115 | 0.12365 | -0.040163 | 56.8686 | 0.6368 | -65.9257 | 56.7754 | 56.8983 | 56.7458 | -66.9279 | 66.6102 | -56.8387 | 66.6194 | 66.6374 | 0.027175 | -56.9088 | -56.7581 | -0.27749 | -0.10628 | 123.519 | 0.72472 | 1.0022 | 0.01655 | -0.13592 | 66.6934 | 66.6233 | 66.774 | 66.6655 | -56.9219 | 123.4258 | 123.5487 | 123.3962 | 67.2872 | -123.8096
1347.2656 | 123.642 | -66.6504 | 56.8634 | 0.047088 | -0.057943 | -0.034723 | -0.062998 | -0.039695 | -0.043548 | 0.065477 | 0.0089643 | 0.015972 | -0.0088356 | 0.17322 | 0.060957 | -0.03558 | -0.003172 | -0.017566 | 0.042971 | -0.022536 | 0.12823 | -0.049321 | 56.864 | 0.88863 | -65.9486 | 56.7709 | 56.8937 | 56.7595 | -66.9187 | 66.6011 | -56.8204 | 66.6148 | 66.6328 | 0.031755 | -56.8859 | -56.7352 | -0.26833 | -0.092546 | 123.5144 | 0.70183 | 0.97016 | 0.030283 | -0.10387 | 66.6934 | 66.6279 | 66.7786 | 66.6472 | -56.9127 | 123.4212 | 123.5441 | 123.4099 | 67.539 | -123.7821
1348.2812 | 123.6282 | -66.5909 | 56.8954 | 0.047088 | -0.059011 | -0.035791 | -0.065135 | -0.040764 | -0.043548 | 0.065477 | 0.010032 | 0.01704 | -0.0077666 | 0.17322 | 0.063094 | -0.026423 | -0.003172 | -0.012988 | 0.047549 | -0.022536 | 0.13281 | -0.035584 | 56.919 | 0.77416 | -65.8707 | 56.8258 | 56.9486 | 56.8191 | -66.8684 | 66.5553 | -56.8479 | 66.5645 | 66.5779 | 0.022596 | -56.918 | -56.7626 | -0.27748 | -0.069648 | 123.5099 | 0.72015 | 0.99763 | 0.053182 | -0.076396 | 66.6384 | 66.5683 | 66.7237 | 66.5877 | -56.931 | 123.4167 | 123.5395 | 123.4099 | 67.365 | -123.7638
1349.2656 | 123.6649 | -66.6092 | 56.9183 | 0.06235 | -0.057943 | -0.034723 | -0.065135 | -0.0429 | -0.041411 | 0.065477 | 0.010032 | 0.015972 | -0.0077666 | 0.17215 | 0.060957 | -0.031001 | 0.001407 | -0.008409 | 0.042971 | -0.022536 | 0.12365 | -0.040163 | 56.8915 | 1.5663 | -65.9394 | 56.7983 | 56.9212 | 56.787 | -66.8958 | 66.569 | -56.8754 | 66.5782 | 66.6008 | 0.031754 | -56.9409 | -56.7947 | -0.28664 | -0.12001 | 123.5007 | 0.66978 | 0.95642 | 0.002822 | -0.13133 | 66.6522 | 66.5867 | 66.7328 | 66.6106 | -56.9585 | 123.4075 | 123.5303 | 123.3962 | 68.1755 | -123.8142
1350.2656 | 123.6649 | -66.6092 | 56.8817 | 0.06235 | -0.061148 | -0.035791 | -0.064067 | -0.040764 | -0.043548 | 0.065477 | 0.012169 | 0.01704 | -0.0056306 | 0.17322 | 0.063094 | -0.031001 | 0.005985 | -0.008409 | 0.056706 | -0.017957 | 0.13281 | -0.044742 | 56.8915 | 1.1359 | -65.9394 | 56.8029 | 56.9257 | 56.7824 | -66.8913 | 66.5644 | -56.825 | 66.5782 | 66.6008 | 0.036333 | -56.8997 | -56.7489 | -0.28206 | -0.078808 | 123.5007 | 0.66978 | 0.95184 | 0.044022 | -0.099292 | 66.6659 | 66.5912 | 66.742 | 66.6152 | -56.9265 | 123.4121 | 123.5349 | 123.3916 | 67.7451 | -123.773
1351.2656 | 123.6465 | -66.5817 | 56.9412 | 0.047088 | -0.06008 | -0.035791 | -0.065135 | -0.041832 | -0.043548 | 0.080738 | 0.0111 | 0.018108 | -0.0088356 | 0.17322 | 0.060957 | -0.03558 | 0.015142 | -0.012988 | 0.042971 | -0.031693 | 0.12365 | -0.040163 | 56.8961 | 0.79705 | -65.9028 | 56.8075 | 56.9257 | 56.7916 | -66.8821 | 66.5416 | -56.8983 | 66.5461 | 66.5687 | 0.027175 | -56.9729 | -56.8176 | -0.30037 | -0.13374 | 123.4778 | 0.67895 | 0.97932 | -0.015487 | -0.14964 | 66.6247 | 66.55 | 66.7054 | 66.5969 | -56.9814 | 123.3892 | 123.5075 | 123.3733 | 67.3788 | -123.8233
1352.2656 | 123.6328 | -66.5405 | 56.9321 | 0.06235 | -0.061148 | -0.034723 | -0.065135 | -0.0429 | -0.043548 | 0.065477 | 0.012169 | 0.01704 | -0.0066986 | 0.17215 | 0.062025 | -0.031001 | 0.005985 | -0.017566 | 0.038393 | -0.017957 | 0.13281 | -0.035584 | 56.919 | 1.2183 | -65.8845 | 56.8258 | 56.944 | 56.8145 | -66.8638 | 66.5049 | -56.8937 | 66.5095 | 66.523 | 0.018018 | -56.95 | -56.7993 | -0.32325 | -0.10627 | 123.4595 | 0.65606 | 0.97932 | 0.011982 | -0.1176 | 66.5789 | 66.5226 | 66.6733 | 66.5465 | -56.9677 | 123.3663 | 123.4846 | 123.355 | 67.7588 | -123.7958
1353.2812 | 123.6145 | -66.6046 | 56.9275 | 0.047088 | -0.061148 | -0.034723 | -0.064067 | -0.040764 | -0.043548 | 0.034955 | 0.012169 | 0.014904 | -0.0066986 | 0.17322 | 0.060957 | -0.03558 | 0.019721 | -0.017566 | 0.033814 | -0.027115 | 0.12365 | -0.040163 | 56.9281 | 0.91152 | -65.857 | 56.835 | 56.9532 | 56.8282 | -66.8546 | 66.5645 | -56.8937 | 66.569 | 66.587 | 0.022597 | -56.9546 | -56.8038 | -0.25001 | -0.092534 | 123.5328 | 0.74762 | 0.99763 | 0.025717 | -0.099282 | 66.6384 | 66.5775 | 66.7283 | 66.6243 | -56.9677 | 123.4396 | 123.5578 | 123.4328 | 67.5161 | -123.7821
1354.2656 | 123.6099 | -66.5726 | 56.9412 | 0.047088 | -0.06008 | -0.035791 | -0.067272 | -0.0429 | -0.043548 | 0.065477 | 0.010032 | 0.015972 | -0.0056306 | 0.17215 | 0.060957 | -0.03558 | 0.015142 | -0.022144 | 0.038393 | -0.022536 | 0.15112 | -0.031005 | 56.9098 | 1.4701 | -65.9074 | 56.8166 | 56.9395 | 56.8099 | -66.8729 | 66.5416 | -56.9028 | 66.537 | 66.5504 | 0.008861 | -56.9638 | -56.7901 | -0.30036 | -0.12458 | 123.4824 | 0.66522 | 0.96558 | -0.001751 | -0.13133 | 66.611 | 66.55 | 66.7237 | 66.5877 | -56.9722 | 123.3892 | 123.512 | 123.3825 | 68.0427 | -123.8142
1355.2656 | 123.555 | -66.5405 | 56.9504 | 0.077612 | -0.062216 | -0.034723 | -0.065135 | -0.041832 | -0.044616 | 0.065477 | 0.0111 | 0.018108 | -0.0066986 | 0.17322 | 0.062025 | -0.03558 | 0.001407 | -0.012988 | 0.056706 | -0.022536 | 0.13739 | -0.040163 | 56.9236 | 1.232 | -65.8845 | 56.835 | 56.9578 | 56.8099 | -66.8684 | 66.5004 | -56.8937 | 66.5049 | 66.5275 | 0.027175 | -56.9729 | -56.813 | -0.32783 | -0.11542 | 123.4641 | 0.65606 | 0.9839 | 0.007408 | -0.14048 | 66.5972 | 66.518 | 66.6779 | 66.5419 | -56.9905 | 123.3755 | 123.4983 | 123.3504 | 67.7726 | -123.8187
1356.2656 | 123.6328 | -66.5359 | 56.9824 | 0.06235 | -0.061148 | -0.033655 | -0.065135 | -0.041832 | -0.043548 | 0.080738 | 0.012169 | 0.018108 | -0.0088356 | 0.17322 | 0.060957 | -0.03558 | -0.003172 | -0.012988 | 0.020079 | -0.036272 | 0.13739 | -0.040163 | 56.951 | 0.10109 | -65.8341 | 56.8578 | 56.9807 | 56.8557 | -66.8317 | 66.4958 | -56.9623 | 66.5004 | 66.523 | 0.027175 | -57.0187 | -56.845 | -0.29578 | -0.12457 | 123.487 | 0.70185 | 0.99763 | -0.001743 | -0.12674 | 66.556 | 66.4997 | 66.6733 | 66.5328 | -57.0226 | 123.3938 | 123.5166 | 123.3916 | 66.637 | -123.8141
1357.2656 | 123.6191 | -66.4902 | 57.019 | 0.047088 | -0.063285 | -0.034723 | -0.064067 | -0.041832 | -0.044616 | 0.080738 | 0.0111 | 0.018108 | -0.0077666 | 0.17429 | 0.060957 | -0.021844 | -0.003172 | -0.017566 | 0.024657 | -0.017957 | 0.12823 | -0.040163 | 56.9877 | -0.086637 | -65.7929 | 56.8853 | 57.0082 | 56.8877 | -66.8088 | 66.45 | -56.9944 | 66.4683 | 66.4726 | 0.022597 | -57.037 | -56.8908 | -0.31866 | -0.13372 | 123.4778 | 0.69728 | 1.0159 | -0.010892 | -0.13131 | 66.5148 | 66.4722 | 66.6184 | 66.487 | -57.0592 | 123.3755 | 123.4983 | 123.3779 | 66.4035 | -123.8279
1358.2656 | 123.6237 | -66.5359 | 56.987 | 0.092874 | -0.06008 | -0.035791 | -0.065135 | -0.0429 | -0.043548 | 0.080738 | 0.010032 | 0.01704 | -0.0066986 | 0.17536 | 0.059889 | -0.03558 | -0.003172 | -0.012988 | 0.042971 | -0.017957 | 0.13739 | -0.044742 | 56.9556 | 1.58 | -65.8524 | 56.8533 | 56.9853 | 56.8465 | -66.8363 | 66.4912 | -56.944 | 66.5004 | 66.523 | 0.031754 | -57.005 | -56.8496 | -0.30036 | -0.13373 | 123.4916 | 0.68354 | 0.98389 | -0.001742 | -0.14048 | 66.5789 | 66.518 | 66.6733 | 66.5328 | -57.0317 | 123.3892 | 123.5212 | 123.3825 | 68.116 | -123.8233
1359.2656 | 123.6237 | -66.481 | 57.0328 | 0.06235 | -0.061148 | -0.03686 | -0.067272 | -0.040764 | -0.043548 | 0.065477 | 0.0111 | 0.01704 | -0.0077666 | 0.17429 | 0.063094 | -0.031001 | 0.005985 | -0.012988 | 0.056706 | -0.027115 | 0.13281 | -0.040163 | 56.9648 | -0.017956 | -65.8066 | 56.8716 | 56.999 | 56.8465 | -66.8134 | 66.4409 | -56.9761 | 66.45 | 66.468 | 0.027175 | -57.0599 | -56.9 | -0.33239 | -0.16119 | 123.4458 | 0.67439 | 1.0068 | -0.033783 | -0.18625 | 66.5377 | 66.4539 | 66.6138 | 66.487 | -57.0729 | 123.3526 | 123.48 | 123.3275 | 66.4631 | -123.8462
1360.2812 | 123.6832 | -66.5085 | 56.9504 | 0.031826 | -0.06008 | -0.035791 | -0.065135 | -0.041832 | -0.043548 | 0.065477 | 0.010032 | 0.019177 | -0.0077666 | 0.17429 | 0.059889 | -0.031001 | 0.001407 | -0.012988 | 0.047549 | -0.027115 | 0.16486 | -0.026426 | 56.951 | 0.36666 | -65.8112 | 56.8578 | 56.9853 | 56.8374 | -66.8317 | 66.4821 | -56.9028 | 66.4775 | 66.4955 | 0.013438 | -56.9775 | -56.7855 | -0.32324 | -0.09253 | 123.4595 | 0.69728 | 1.0205 | 0.03488 | -0.11301 | 66.556 | 66.4814 | 66.6733 | 66.5099 | -56.9768 | 123.3663 | 123.4937 | 123.3458 | 66.8751 | -123.7821
1361.2656 | 123.6969 | -66.5222 | 56.9687 | 0.077612 | -0.06008 | -0.035791 | -0.066204 | -0.041832 | -0.04248 | 0.080738 | 0.010032 | 0.019177 | -0.0066986 | 0.17322 | 0.060957 | -0.031001 | -0.003172 | -0.012988 | 0.042971 | -0.017957 | 0.13281 | -0.040163 | 56.9419 | 1.1359 | -65.8387 | 56.8441 | 56.9853 | 56.8374 | -66.8455 | 66.4821 | -56.9257 | 66.4912 | 66.5092 | 0.027175 | -56.9866 | -56.8359 | -0.32325 | -0.12458 | 123.4641 | 0.68354 | 1.0068 | 0.016569 | -0.13132 | 66.5652 | 66.5043 | 66.655 | 66.519 | -57.0089 | 123.3663 | 123.5075 | 123.3596 | 67.6581 | -123.8142
1362.2656 | 123.6328 | -66.5131 | 57.0007 | 0.06235 | -0.061148 | -0.035791 | -0.065135 | -0.040764 | -0.045685 | 0.050216 | 0.0078963 | 0.018108 | -0.0088356 | 0.17429 | 0.062025 | -0.031001 | 0.005985 | -0.008409 | 0.029236 | -0.027115 | 0.14655 | -0.044742 | 56.9602 | 0.90236 | -65.7975 | 56.867 | 57.0036 | 56.8694 | -66.8317 | 66.4683 | -56.9715 | 66.4821 | 66.5047 | 0.036333 | -57.0278 | -56.8542 | -0.31866 | -0.13373 | 123.4733 | 0.7156 | 1.0343 | 0.00284 | -0.13132 | 66.5423 | 66.4859 | 66.6596 | 66.519 | -57.0455 | 123.3801 | 123.5166 | 123.3825 | 67.4154 | -123.8325
1363.2812 | 123.642 | -66.5314 | 56.9504 | 0.06235 | -0.062216 | -0.03686 | -0.065135 | -0.0429 | -0.044616 | 0.080738 | 0.0089643 | 0.01704 | -0.0066986 | 0.17322 | 0.060957 | -0.03558 | 0.005985 | -0.012988 | 0.042971 | -0.022536 | 0.13739 | -0.035584 | 56.9373 | 1.9646 | -65.8204 | 56.835 | 56.9624 | 56.8145 | -66.8546 | 66.4958 | -56.9074 | 66.4958 | 66.5184 | 0.022596 | -56.9729 | -56.813 | -0.32325 | -0.11542 | 123.4687 | 0.71101 | 1.0343 | 0.011987 | -0.13591 | 66.5743 | 66.5088 | 66.6688 | 66.5374 | -56.986 | 123.3663 | 123.4937 | 123.3458 | 68.496 | -123.805
1364.2656 | 123.6557 | -66.4948 | 57.0007 | 0.047088 | -0.059011 | -0.035791 | -0.066204 | -0.0429 | -0.043548 | 0.080738 | 0.0111 | 0.018108 | -0.0066986 | 0.17429 | 0.063094 | -0.03558 | 0.001407 | -0.008409 | 0.033814 | -0.017957 | 0.12823 | -0.044742 | 56.951 | 2.537 | -65.8295 | 56.8578 | 56.9898 | 56.8557 | -66.8271 | 66.45 | -56.9669 | 66.4592 | 66.4863 | 0.036333 | -57.0187 | -56.8725 | -0.3324 | -0.14288 | 123.4458 | 0.66523 | 0.99763 | -0.010896 | -0.14505 | 66.5286 | 66.4768 | 66.623 | 66.4962 | -57.0455 | 123.3526 | 123.4846 | 123.3504 | 69.0317 | -123.8279
1365.2812 | 123.6557 | -66.5314 | 56.9733 | 0.06235 | -0.061148 | -0.03686 | -0.065135 | -0.041832 | -0.04248 | 0.065477 | 0.012169 | 0.01704 | -0.0066986 | 0.17322 | 0.063094 | -0.03558 | 0.001407 | -0.017566 | 0.052128 | -0.027115 | 0.14655 | -0.044742 | 56.951 | 2.569 | -65.8066 | 56.8624 | 56.9898 | 56.8374 | -66.8363 | 66.4866 | -56.9211 | 66.4958 | 66.5138 | 0.027176 | -57.0004 | -56.8267 | -0.30493 | -0.11084 | 123.4824 | 0.72475 | 1.0297 | 0.016569 | -0.1359 | 66.5835 | 66.5043 | 66.6779 | 66.5328 | -57.018 | 123.3938 | 123.5212 | 123.3687 | 69.1004 | -123.8096
1366.2656 | 123.7244 | -66.4902 | 56.9321 | 0.06235 | -0.06008 | -0.035791 | -0.064067 | -0.0429 | -0.04248 | 0.080738 | 0.010032 | 0.018108 | -0.0088356 | 0.17536 | 0.063094 | -0.03558 | -0.007751 | -0.022144 | 0.042971 | -0.027115 | 0.13739 | -0.044742 | 56.9648 | 1.9829 | -65.7929 | 56.8762 | 57.0036 | 56.8603 | -66.8226 | 66.4454 | -56.8891 | 66.4546 | 66.468 | 0.022598 | -56.9592 | -56.7947 | -0.3324 | -0.055906 | 123.4549 | 0.69728 | 1.0297 | 0.071504 | -0.07181 | 66.5331 | 66.4631 | 66.6276 | 66.4824 | -56.9768 | 123.3663 | 123.4937 | 123.3504 | 68.4731 | -123.7546
1367.2656 | 123.7381 | -66.4673 | 56.9733 | 0.077612 | -0.061148 | -0.034723 | -0.066204 | -0.0429 | -0.041411 | 0.050216 | 0.0111 | 0.019177 | -0.0088356 | 0.17643 | 0.060957 | -0.031001 | -0.003172 | -0.017566 | 0.038393 | -0.022536 | 0.14197 | -0.035584 | 56.9694 | 0.050725 | -65.7929 | 56.8762 | 57.0127 | 56.8648 | -66.8226 | 66.4317 | -56.9349 | 66.4363 | 66.4497 | 0.018018 | -56.9958 | -56.8313 | -0.35528 | -0.097105 | 123.4366 | 0.6744 | 1.0297 | 0.039462 | -0.10843 | 66.5057 | 66.4447 | 66.6093 | 66.4641 | -57.0089 | 123.3434 | 123.48 | 123.3321 | 66.518 | -123.7958
1368.2812 | 123.6511 | -66.5085 | 57.0053 | 0.031826 | -0.061148 | -0.03686 | -0.065135 | -0.0429 | -0.043548 | 0.065477 | 0.010032 | 0.015972 | -0.0066986 | 0.17429 | 0.060957 | -0.026423 | 0.005985 | -0.008409 | 0.052128 | -0.022536 | 0.12823 | -0.040163 | 56.9877 | 0.43076 | -65.7837 | 56.8991 | 57.0265 | 56.8786 | -66.7951 | 66.4683 | -56.9532 | 66.4821 | 66.5001 | 0.031754 | -57.0278 | -56.8771 | -0.28661 | -0.10626 | 123.4962 | 0.72475 | 1.0114 | 0.021155 | -0.12674 | 66.5606 | 66.4859 | 66.6367 | 66.5145 | -57.0455 | 123.4075 | 123.5349 | 123.3871 | 66.9392 | -123.8004
1369.2656 | 123.7244 | -66.4536 | 56.9916 | 0.047088 | -0.062216 | -0.035791 | -0.066204 | -0.041832 | -0.04248 | 0.065477 | 0.010032 | 0.015972 | -0.0077666 | 0.17429 | 0.062025 | -0.031001 | 0.001407 | -0.008409 | 0.042971 | -0.027115 | 0.14655 | -0.035584 | 56.9739 | 2.1157 | -65.8295 | 56.8807 | 57.0082 | 56.8648 | -66.8088 | 66.418 | -56.9486 | 66.4226 | 66.4451 | 0.027175 | -57.0187 | -56.845 | -0.35528 | -0.11084 | 123.4275 | 0.62403 | 0.97932 | 0.016574 | -0.12674 | 66.4965 | 66.4264 | 66.6001 | 66.455 | -57.0272 | 123.3343 | 123.4617 | 123.3184 | 68.5693 | -123.8004
1370.2812 | 123.6649 | -66.5176 | 56.987 | 0.047088 | -0.063285 | -0.03686 | -0.066204 | -0.041832 | -0.044616 | 0.050216 | 0.0111 | 0.018108 | -0.0088356 | 0.17429 | 0.062025 | -0.031001 | 0.005985 | -0.012988 | 0.038393 | -0.022536 | 0.14655 | -0.035584 | 56.9785 | 2.4591 | -65.8158 | 56.8945 | 57.0173 | 56.874 | -66.8043 | 66.4821 | -56.9486 | 66.4866 | 66.5047 | 0.022596 | -57.0095 | -56.8405 | -0.28661 | -0.092524 | 123.4962 | 0.70186 | 0.98847 | 0.030308 | -0.11301 | 66.556 | 66.4951 | 66.6642 | 66.5236 | -57.0226 | 123.4121 | 123.5349 | 123.3916 | 68.9768 | -123.7913
1371.2656 | 123.7198 | -66.5085 | 56.9824 | 0.077612 | -0.062216 | -0.035791 | -0.064067 | -0.039695 | -0.043548 | 0.065477 | 0.013237 | 0.01704 | -0.0099036 | 0.17643 | 0.060957 | -0.021844 | 0.001407 | -0.012988 | 0.047549 | -0.022536 | 0.15112 | -0.031005 | 56.9877 | 2.1111 | -65.8158 | 56.8945 | 57.0219 | 56.874 | -66.7997 | 66.4775 | -56.9349 | 66.4866 | 66.4955 | 0.018017 | -57.005 | -56.8313 | -0.29119 | -0.087946 | 123.4962 | 0.6927 | 0.98389 | 0.039464 | -0.10843 | 66.556 | 66.4859 | 66.6596 | 66.5099 | -57.0134 | 123.403 | 123.5304 | 123.3825 | 68.6196 | -123.7821
1372.2656 | 123.7289 | -66.4581 | 56.9595 | 0.047088 | -0.061148 | -0.035791 | -0.066204 | -0.041832 | -0.043548 | 0.065477 | 0.012169 | 0.018108 | -0.0077666 | 0.17643 | 0.060957 | -0.031001 | 0.001407 | -0.003831 | 0.029236 | -0.022536 | 0.12823 | -0.035584 | 56.9694 | 2.5095 | -65.8295 | 56.8716 | 57.0082 | 56.8648 | -66.818 | 66.4225 | -56.9303 | 66.4271 | 66.4543 | 0.031753 | -56.9821 | -56.8313 | -0.35986 | -0.08795 | 123.4275 | 0.62861 | 0.98847 | 0.048617 | -0.094697 | 66.4874 | 66.4356 | 66.5864 | 66.4595 | -56.9951 | 123.3297 | 123.4663 | 123.323 | 68.9676 | -123.7775
1373.2812 | 123.6694 | -66.4902 | 57.0236 | 0.06235 | -0.062216 | -0.03686 | -0.064067 | -0.041832 | -0.044616 | 0.080738 | 0.0078963 | 0.015972 | -0.0077666 | 0.17536 | 0.059889 | -0.026423 | 0.001407 | -0.008409 | 0.052128 | -0.022536 | 0.13739 | -0.044742 | 56.9831 | 2.537 | -65.8158 | 56.8945 | 57.0219 | 56.874 | -66.8043 | 66.4454 | -56.9715 | 66.4638 | 66.4818 | 0.036333 | -57.0462 | -56.8862 | -0.31408 | -0.12915 | 123.4733 | 0.67439 | 0.98847 | -0.001735 | -0.14963 | 66.5423 | 66.4676 | 66.6276 | 66.4916 | -57.0684 | 123.3846 | 123.5121 | 123.3642 | 69.0271 | -123.8279
1374.2656 | 123.761 | -66.4581 | 57.0099 | 0.06235 | -0.062216 | -0.03686 | -0.067272 | -0.040764 | -0.044616 | 0.065477 | 0.0089643 | 0.018108 | -0.0088356 | 0.17536 | 0.059889 | -0.031001 | 0.001407 | -0.003831 | 0.047549 | -0.027115 | 0.14197 | -0.031005 | 57.0106 | 1.8089 | -65.7792 | 56.9082 | 57.0402 | 56.8969 | -66.7814 | 66.4271 | -56.9623 | 66.4271 | 66.4543 | 0.027174 | -57.037 | -56.8679 | -0.32323 | -0.10168 | 123.4687 | 0.67898 | 1.0022 | 0.030313 | -0.113 | 66.5057 | 66.431 | 66.6001 | 66.4595 | -57.0409 | 123.3663 | 123.4983 | 123.355 | 68.2671 | -123.7912
1375.2812 | 123.6145 | -66.4764 | 57.0282 | 0.047088 | -0.062216 | -0.03686 | -0.066204 | -0.041832 | -0.043548 | 0.095999 | 0.010032 | 0.01704 | -0.0077666 | 0.17643 | 0.05882 | -0.03558 | 0.010564 | -0.012988 | 0.042971 | -0.017957 | 0.13739 | -0.044742 | 56.9968 | 1.9784 | -65.7929 | 56.9036 | 57.0402 | 56.8969 | -66.7905 | 66.4317 | -56.9852 | 66.4409 | 66.4635 | 0.031754 | -57.0462 | -56.8908 | -0.31408 | -0.12457 | 123.4733 | 0.68355 | 0.99763 | 0.012003 | -0.13131 | 66.5194 | 66.4585 | 66.6138 | 66.487 | -57.0729 | 123.3801 | 123.5166 | 123.3733 | 68.4548 | -123.8187
1376.2656 | 123.7518 | -66.4352 | 56.9824 | 0.047088 | -0.062216 | -0.035791 | -0.066204 | -0.040764 | -0.040343 | 0.065477 | 0.010032 | 0.01704 | -0.0088356 | 0.17429 | 0.059889 | -0.03558 | 0.001407 | -0.003831 | 0.042971 | -0.017957 | 0.13281 | -0.031005 | 57.0151 | 2.1844 | -65.77 | 56.9128 | 57.0539 | 56.9015 | -66.7768 | 66.4042 | -56.9395 | 66.3997 | 66.4314 | 0.027174 | -57.0004 | -56.8496 | -0.34154 | -0.069632 | 123.4504 | 0.66525 | 1.0068 | 0.071515 | -0.080956 | 66.4782 | 66.4173 | 66.5681 | 66.4366 | -57.0134 | 123.348 | 123.4892 | 123.3367 | 68.6196 | -123.7592
1377.2656 | 123.7839 | -66.4856 | 56.9687 | 0.06235 | -0.062216 | -0.03686 | -0.066204 | -0.039695 | -0.044616 | 0.050216 | 0.0111 | 0.01704 | -0.0088356 | 0.17429 | 0.05882 | -0.03558 | 0.005985 | -0.012988 | 0.033814 | -0.027115 | 0.13281 | -0.035584 | 56.9922 | 2.3035 | -65.8249 | 56.8991 | 57.0265 | 56.8832 | -66.8088 | 66.45 | -56.9349 | 66.45 | 66.4726 | 0.022596 | -56.9958 | -56.8359 | -0.32324 | -0.069634 | 123.4778 | 0.66066 | 0.98389 | 0.057776 | -0.085538 | 66.5194 | 66.4585 | 66.6184 | 66.4916 | -57.0043 | 123.3847 | 123.5121 | 123.3687 | 68.789 | -123.7775
1378.2812 | 123.6282 | -66.481 | 57.019 | 0.06235 | -0.063285 | -0.035791 | -0.065135 | -0.0429 | -0.044616 | 0.065477 | 0.0111 | 0.018108 | -0.0088356 | 0.17643 | 0.059889 | -0.026423 | 0.001407 | -0.012988 | 0.042971 | -0.022536 | 0.13281 | -0.040163 | 56.9922 | 2.1844 | -65.802 | 56.8991 | 57.0265 | 56.8832 | -66.7997 | 66.4409 | -56.9761 | 66.4546 | 66.468 | 0.027175 | -57.0416 | -56.8862 | -0.31866 | -0.11999 | 123.4733 | 0.67897 | 0.99763 | 0.007422 | -0.13589 | 66.524 | 66.4585 | 66.6138 | 66.4824 | -57.0592 | 123.3801 | 123.5075 | 123.3642 | 68.6654 | -123.8187
1379.2656 | 123.7473 | -66.4536 | 56.9733 | 0.077612 | -0.063285 | -0.03686 | -0.067272 | -0.039695 | -0.045685 | 0.065477 | 0.0089643 | 0.018108 | -0.0088356 | 0.17536 | 0.060957 | -0.026423 | 0.010564 | -0.022144 | 0.015501 | -0.017957 | 0.14655 | -0.031005 | 56.9877 | 2.102 | -65.8799 | 56.8945 | 57.031 | 56.8923 | -66.8088 | 66.4225 | -56.9578 | 66.4271 | 66.4314 | 0.008861 | -56.9912 | -56.8267 | -0.35528 | -0.078791 | 123.4412 | 0.57367 | 0.92895 | 0.057777 | -0.080959 | 66.4691 | 66.4356 | 66.6001 | 66.4641 | -57.0043 | 123.348 | 123.4846 | 123.3459 | 68.5555 | -123.7821
1380.2656 | 123.6511 | -66.4948 | 57.0099 | 0.06235 | -0.062216 | -0.035791 | -0.065135 | -0.041832 | -0.044616 | 0.050216 | 0.0111 | 0.018108 | -0.0066986 | 0.1775 | 0.060957 | -0.031001 | 0.015142 | -0.003831 | 0.033814 | -0.017957 | 0.14197 | -0.035584 | 56.9831 | 2.0333 | -65.8753 | 56.8899 | 57.0219 | 56.8877 | -66.7997 | 66.4592 | -56.9761 | 66.4637 | 66.4909 | 0.031753 | -57.0278 | -56.8679 | -0.30492 | -0.11999 | 123.4778 | 0.61945 | 0.92437 | 0.011998 | -0.12216 | 66.5286 | 66.4768 | 66.6367 | 66.5099 | -57.0455 | 123.3846 | 123.5166 | 123.3825 | 68.5281 | -123.8096
1381.2656 | 123.6969 | -66.481 | 56.9733 | 0.047088 | -0.064353 | -0.035791 | -0.066204 | -0.041832 | -0.044616 | 0.065477 | 0.010032 | 0.018108 | -0.0066986 | 0.17643 | 0.059889 | -0.031001 | 0.019721 | -0.008409 | 0.033814 | -0.022536 | 0.15112 | -0.040163 | 56.9785 | 1.6395 | -65.8661 | 56.8899 | 57.0173 | 56.8786 | -66.7997 | 66.4409 | -56.9395 | 66.45 | 66.4726 | 0.031754 | -56.9958 | -56.8221 | -0.31866 | -0.083369 | 123.4595 | 0.61487 | 0.93353 | 0.044041 | -0.094694 | 66.5148 | 66.4585 | 66.6321 | 66.5007 | -57.0134 | 123.3709 | 123.4983 | 123.3596 | 68.1206 | -123.7729
1382.2656 | 123.7015 | -66.4719 | 56.9824 | 0.06235 | -0.063285 | -0.035791 | -0.065135 | -0.041832 | -0.044616 | 0.034955 | 0.010032 | 0.019177 | -0.0099036 | 0.1775 | 0.059889 | -0.044736 | 0.019721 | -0.012988 | 0.038393 | -0.013378 | 0.12823 | -0.031005 | 56.9968 | 1.3373 | -65.8707 | 56.8899 | 57.0356 | 56.8786 | -66.7951 | 66.4409 | -56.944 | 66.4271 | 66.4589 | 0.018017 | -56.9958 | -56.8542 | -0.32323 | -0.092524 | 123.4687 | 0.60114 | 0.92437 | 0.0532 | -0.10385 | 66.5103 | 66.4585 | 66.6001 | 66.4916 | -57.0134 | 123.3618 | 123.5075 | 123.3504 | 67.8092 | -123.7775
1383.2812 | 123.7381 | -66.4581 | 56.9824 | 0.077612 | -0.063285 | -0.035791 | -0.066204 | -0.0429 | -0.043548 | 0.065477 | 0.010032 | 0.018108 | -0.0088356 | 0.17856 | 0.05882 | -0.031001 | 0.019721 | -0.012988 | 0.042971 | -0.027115 | 0.13739 | -0.044742 | 56.9831 | 1.6212 | -65.8707 | 56.8899 | 57.0173 | 56.8832 | -66.8043 | 66.4134 | -56.9395 | 66.4271 | 66.4451 | 0.031754 | -57.0095 | -56.845 | -0.34612 | -0.092524 | 123.4412 | 0.5874 | 0.93353 | 0.034886 | -0.099271 | 66.5011 | 66.431 | 66.5955 | 66.4779 | -57.0272 | 123.348 | 123.4754 | 123.3413 | 68.0794 | -123.7867
1384.2656 | 123.674 | -66.4719 | 56.987 | 0.06235 | -0.063285 | -0.037928 | -0.065135 | -0.041832 | -0.043548 | 0.050216 | 0.010032 | 0.018108 | -0.0088356 | 0.17643 | 0.059889 | -0.031001 | 0.019721 | -0.008409 | 0.038393 | -0.017957 | 0.14197 | -0.040163 | 56.9831 | 1.1359 | -65.8524 | 56.8899 | 57.0127 | 56.874 | -66.8043 | 66.4317 | -56.9486 | 66.4409 | 66.4635 | 0.031754 | -57.005 | -56.845 | -0.33239 | -0.097102 | 123.455 | 0.61945 | 0.95184 | 0.025729 | -0.11301 | 66.5103 | 66.4539 | 66.6138 | 66.4916 | -57.0272 | 123.3618 | 123.4846 | 123.3459 | 67.6077 | -123.7913
1385.2656 | 123.7061 | -66.4627 | 56.9778 | 0.06235 | -0.065421 | -0.035791 | -0.067272 | -0.040764 | -0.04248 | 0.050216 | 0.0089643 | 0.018108 | -0.0099036 | 0.17643 | 0.059889 | -0.021844 | 0.015142 | -0.008409 | 0.033814 | -0.022536 | 0.15112 | -0.035584 | 56.9922 | 1.232 | -65.8204 | 56.8991 | 57.0356 | 56.8877 | -66.7951 | 66.4271 | -56.944 | 66.4409 | 66.4543 | 0.027175 | -57.0004 | -56.8267 | -0.33239 | -0.078789 | 123.455 | 0.64235 | 0.97474 | 0.057778 | -0.090114 | 66.4965 | 66.4402 | 66.6138 | 66.4779 | -57.0134 | 123.3618 | 123.4983 | 123.3504 | 67.6947 | -123.7729
1386.2656 | 123.7106 | -66.4902 | 56.9595 | 0.031826 | -0.063285 | -0.03686 | -0.067272 | -0.040764 | -0.044616 | 0.080738 | 0.0111 | 0.019177 | -0.0088356 | 0.17643 | 0.059889 | -0.031001 | 0.0243 | -0.008409 | 0.042971 | -0.013378 | 0.13739 | -0.035584 | 56.9877 | 1.5709 | -65.8524 | 56.8899 | 57.0173 | 56.874 | -66.7997 | 66.4546 | -56.9166 | 66.4592 | 66.4818 | 0.027175 | -56.9729 | -56.8221 | -0.3095 | -0.069636 | 123.4778 | 0.63776 | 0.94726 | 0.057774 | -0.08554 | 66.5331 | 66.4768 | 66.6276 | 66.5145 | -56.9951 | 123.3801 | 123.5075 | 123.3642 | 68.061 | -123.7592
1387.2656 | 123.6969 | -66.481 | 56.9595 | 0.047088 | -0.063285 | -0.037928 | -0.065135 | -0.041832 | -0.043548 | 0.050216 | 0.010032 | 0.019177 | -0.0077666 | 0.1775 | 0.05882 | -0.03558 | 0.0243 | -0.012988 | 0.029236 | -0.022536 | 0.13739 | -0.040163 | 56.9831 | 0.82453 | -65.8936 | 56.8945 | 57.0219 | 56.8694 | -66.8088 | 66.4409 | -56.9303 | 66.4454 | 66.468 | 0.027175 | -56.9821 | -56.8221 | -0.32782 | -0.065058 | 123.4641 | 0.5874 | 0.91521 | 0.062352 | -0.090119 | 66.5103 | 66.4585 | 66.6184 | 66.5053 | -56.9997 | 123.3755 | 123.5029 | 123.3504 | 67.3055 | -123.7684
1388.2656 | 123.8159 | -66.4581 | 56.9458 | 0.06235 | -0.064353 | -0.03686 | -0.065135 | -0.040764 | -0.043548 | 0.065477 | 0.0089643 | 0.018108 | -0.0099036 | 0.17643 | 0.059889 | -0.031001 | 0.0243 | -0.022144 | 0.038393 | -0.027115 | 0.13739 | -0.026426 | 56.9968 | 1.58 | -65.8524 | 56.8991 | 57.0356 | 56.8923 | -66.7905 | 66.4317 | -56.9074 | 66.4271 | 66.436 | 0.004282 | -56.9729 | -56.8084 | -0.33239 | -0.046746 | 123.455 | 0.60572 | 0.93811 | 0.089821 | -0.053493 | 66.4965 | 66.431 | 66.5955 | 66.4824 | -56.9722 | 123.3572 | 123.4938 | 123.3504 | 68.0381 | -123.7363
1389.2656 | 123.7335 | -66.4581 | 56.9687 | 0.06235 | -0.064353 | -0.037928 | -0.065135 | -0.040764 | -0.044616 | 0.050216 | 0.0089643 | 0.019177 | -0.0077666 | 0.17963 | 0.060957 | -0.031001 | 0.015142 | -0.017566 | 0.033814 | -0.013378 | 0.13739 | -0.031005 | 57.006 | 1.319 | -65.8158 | 56.9036 | 57.0402 | 56.8832 | -66.7859 | 66.4271 | -56.9349 | 66.4271 | 66.4406 | 0.013439 | -56.9821 | -56.8313 | -0.32781 | -0.065056 | 123.4641 | 0.64235 | 0.97016 | 0.071512 | -0.085538 | 66.4919 | 66.4448 | 66.5955 | 66.4733 | -56.9997 | 123.3618 | 123.4983 | 123.3413 | 67.7772 | -123.7546
1390.2656 | 123.8297 | -66.4261 | 57.0328 | 0.031826 | -0.064353 | -0.035791 | -0.066204 | -0.0429 | -0.043548 | 0.065477 | 0.012169 | 0.015972 | -0.0088356 | 0.17856 | 0.057752 | -0.017266 | 0.015142 | -0.012988 | 0.033814 | -0.027115 | 0.14197 | -0.031005 | 57.0518 | 0.72837 | -65.7746 | 56.954 | 57.0951 | 56.9381 | -66.7402 | 66.3951 | -56.999 | 66.4088 | 66.4131 | 0.018017 | -57.0599 | -56.8908 | -0.31406 | -0.078779 | 123.4779 | 0.65151 | 0.96558 | 0.062368 | -0.094682 | 66.4599 | 66.399 | 66.5681 | 66.4412 | -57.0638 | 123.3801 | 123.5212 | 123.3642 | 67.1545 | -123.7729
1391.2656 | 123.7244 | -66.3803 | 57.074 | 0.047088 | -0.064353 | -0.03686 | -0.066204 | -0.041832 | -0.043548 | 0.050216 | 0.010032 | 0.018108 | -0.0088356 | 0.1775 | 0.059889 | -0.031001 | 0.019721 | -0.008409 | 0.029236 | -0.017957 | 0.14197 | -0.031005 | 57.0518 | 0.71464 | -65.7746 | 56.9632 | 57.1043 | 56.9518 | -66.7218 | 66.3493 | -57.0447 | 66.3493 | 66.3719 | 0.022596 | -57.0919 | -56.932 | -0.34153 | -0.11082 | 123.4321 | 0.60574 | 0.94726 | 0.030326 | -0.12214 | 66.4095 | 66.3624 | 66.5223 | 66.4 | -57.105 | 123.3435 | 123.4846 | 123.3321 | 67.0949 | -123.7958
1392.2656 | 123.7335 | -66.4261 | 57.0236 | 0.06235 | -0.06649 | -0.037928 | -0.067272 | -0.041832 | -0.045685 | 0.065477 | 0.0089643 | 0.01704 | -0.0088356 | 0.1775 | 0.059889 | -0.03558 | 0.0243 | -0.008409 | 0.056706 | -0.017957 | 0.16028 | -0.040163 | 57.038 | 1.9051 | -65.7975 | 56.9403 | 57.0768 | 56.9244 | -66.7447 | 66.3859 | -56.9669 | 66.3905 | 66.4177 | 0.031754 | -57.0416 | -56.8633 | -0.31864 | -0.08336 | 123.4641 | 0.62862 | 0.94726 | 0.053209 | -0.099262 | 66.4828 | 66.4081 | 66.5864 | 66.4504 | -57.0638 | 123.3663 | 123.5029 | 123.3504 | 68.3312 | -123.7684
1393.2812 | 123.6969 | -66.4078 | 57.0328 | 0.077612 | -0.065421 | -0.037928 | -0.065135 | -0.043968 | -0.044616 | 0.065477 | 0.0089643 | 0.019177 | -0.0088356 | 0.1775 | 0.060957 | -0.026423 | 0.019721 | -0.008409 | 0.065863 | -0.022536 | 0.14655 | -0.031005 | 57.0472 | 1.9509 | -65.7792 | 56.9632 | 57.0906 | 56.9427 | -66.7264 | 66.3768 | -56.9669 | 66.3814 | 66.3994 | 0.022596 | -57.0553 | -56.8862 | -0.31864 | -0.069622 | 123.455 | 0.62862 | 0.94726 | 0.057789 | -0.090103 | 66.4736 | 66.3852 | 66.5543 | 66.4275 | -57.0638 | 123.3709 | 123.4983 | 123.3504 | 68.3587 | -123.7592
1394.2656 | 123.7381 | -66.3345 | 57.0877 | 0.047088 | -0.064353 | -0.035791 | -0.06834 | -0.040764 | -0.043548 | 0.065477 | 0.0089643 | 0.018108 | -0.0088356 | 0.17856 | 0.05882 | -0.031001 | 0.0243 | -0.012988 | 0.038393 | -0.017957 | 0.13281 | -0.031005 | 57.093 | 1.9372 | -65.7334 | 57.0089 | 57.1409 | 56.9885 | -66.6852 | 66.3035 | -57.0493 | 66.3035 | 66.3215 | 0.018017 | -57.1057 | -56.9549 | -0.35067 | -0.078769 | 123.4275 | 0.60117 | 0.95184 | 0.053222 | -0.099249 | 66.3729 | 66.3166 | 66.4673 | 66.3588 | -57.1187 | 123.3435 | 123.4755 | 123.323 | 68.2717 | -123.7729
1395.2656 | 123.6328 | -66.3712 | 57.1335 | 0.06235 | -0.064353 | -0.03686 | -0.067272 | -0.041832 | -0.044616 | 0.065477 | 0.010032 | 0.01704 | -0.0099036 | 0.1775 | 0.059889 | -0.03558 | 0.0243 | -0.008409 | 0.042971 | -0.022536 | 0.13281 | -0.040163 | 57.1113 | 2.5324 | -65.7379 | 57.0227 | 57.1455 | 57.0068 | -66.676 | 66.331 | -57.0905 | 66.3356 | 66.3627 | 0.031754 | -57.156 | -57.0007 | -0.30489 | -0.11081 | 123.4825 | 0.63321 | 0.9381 | 0.012025 | -0.12671 | 66.4141 | 66.3486 | 66.504 | 66.3955 | -57.1736 | 123.3938 | 123.5167 | 123.3779 | 68.9035 | -123.8095
1396.2656 | 123.6786 | -66.3803 | 57.1335 | 0.047088 | -0.064353 | -0.03686 | -0.066204 | -0.039695 | -0.043548 | 0.050216 | 0.0111 | 0.015972 | -0.0099036 | 0.1775 | 0.057752 | -0.021844 | 0.0243 | -0.008409 | 0.029236 | -0.013378 | 0.14655 | -0.035584 | 57.1296 | 2.743 | -65.7196 | 57.0318 | 57.1684 | 57.0159 | -66.6623 | 66.3447 | -57.1042 | 66.3585 | 66.3719 | 0.027175 | -57.1469 | -56.9869 | -0.282 | -0.10165 | 123.5099 | 0.66068 | 0.94268 | 0.034918 | -0.11755 | 66.4095 | 66.3669 | 66.5269 | 66.4046 | -57.1691 | 123.4121 | 123.5487 | 123.3962 | 69.1233 | -123.7958
1397.2656 | 123.6145 | -66.3528 | 57.1701 | 0.047088 | -0.065421 | -0.040065 | -0.065135 | -0.041832 | -0.045685 | 0.034955 | 0.012169 | 0.014904 | -0.0077666 | 0.17963 | 0.057752 | -0.026423 | 0.019721 | -0.003831 | 0.042971 | -0.027115 | 0.16028 | -0.035584 | 57.1479 | 2.537 | -65.683 | 57.0593 | 57.1867 | 57.0434 | -66.6348 | 66.3173 | -57.1271 | 66.3264 | 66.349 | 0.031753 | -57.1972 | -57.0098 | -0.28199 | -0.1108 | 123.5008 | 0.66985 | 0.95184 | 0.016611 | -0.1267 | 66.3958 | 66.3257 | 66.5131 | 66.3726 | -57.2057 | 123.4121 | 123.5396 | 123.3962 | 68.8898 | -123.8049
1398.2812 | 123.6786 | -66.3208 | 57.1152 | 0.031826 | -0.06649 | -0.035791 | -0.066204 | -0.040764 | -0.045685 | 0.050216 | 0.010032 | 0.015972 | -0.0088356 | 0.17856 | 0.057752 | -0.031001 | 0.015142 | -0.012988 | 0.047549 | -0.022536 | 0.16944 | -0.031005 | 57.1617 | 3.0452 | -65.6784 | 57.0685 | 57.205 | 57.0526 | -66.6257 | 66.2898 | -57.0676 | 66.2898 | 66.3078 | 0.018017 | -57.1377 | -56.9457 | -0.30488 | -0.046714 | 123.4825 | 0.64238 | 0.94726 | 0.089858 | -0.062614 | 66.3684 | 66.2983 | 66.4902 | 66.3359 | -57.1462 | 123.3893 | 123.5258 | 123.3734 | 69.366 | -123.7409
1399.2656 | 123.5916 | -66.3803 | 57.1243 | 0.047088 | -0.06649 | -0.038997 | -0.066204 | -0.0429 | -0.046753 | 0.050216 | 0.010032 | 0.018108 | -0.010972 | 0.17856 | 0.05882 | -0.026423 | 0.019721 | -0.008409 | 0.056706 | -0.022536 | 0.16486 | -0.040163 | 57.1021 | 3.265 | -65.7471 | 57.0181 | 57.1501 | 56.993 | -66.6715 | 66.3401 | -57.0676 | 66.3539 | 66.3719 | 0.031754 | -57.1469 | -56.9595 | -0.29116 | -0.10623 | 123.4824 | 0.63321 | 0.92437 | 0.025758 | -0.13129 | 66.437 | 66.3578 | 66.5452 | 66.4 | -57.1645 | 123.3984 | 123.5304 | 123.3733 | 69.6453 | -123.7958
1400.2656 | 123.6282 | -66.4215 | 57.0648 | 0.047088 | -0.065421 | -0.038997 | -0.067272 | -0.043968 | -0.044616 | 0.065477 | 0.0089643 | 0.01704 | -0.0088356 | 0.1775 | 0.059889 | -0.021844 | 0.015142 | -0.008409 | 0.047549 | -0.017957 | 0.15112 | -0.035584 | 57.0701 | 3.265 | -65.7975 | 56.9769 | 57.1089 | 56.9518 | -66.7035 | 66.3859 | -57.0173 | 66.3997 | 66.4131 | 0.027175 | -57.0828 | -56.9137 | -0.28201 | -0.08793 | 123.4916 | 0.62404 | 0.90605 | 0.044061 | -0.11299 | 66.4691 | 66.4036 | 66.5726 | 66.4367 | -57.1004 | 123.3984 | 123.5304 | 123.3733 | 69.6865 | -123.7683
1401.3125 | 123.5825 | -66.4124 | 57.0969 | 0.047088 | -0.064353 | -0.03686 | -0.066204 | -0.0429 | -0.044616 | 0.065477 | 0.0089643 | 0.01704 | -0.0099036 | 0.17856 | 0.059889 | -0.03558 | 0.019721 | -0.008409 | 0.061284 | -0.027115 | 0.13281 | -0.040163 | 57.0884 | 0.17435 | -65.8112 | 56.9952 | 57.1318 | 56.9701 | -66.6989 | 66.3722 | -57.0356 | 66.3768 | 66.4039 | 0.031754 | -57.124 | -56.9641 | -0.28659 | -0.10166 | 123.5008 | 0.60115 | 0.88774 | 0.03491 | -0.12672 | 66.4736 | 66.3852 | 66.5452 | 66.4321 | -57.137 | 123.4076 | 123.5441 | 123.3825 | 66.5867 | -123.7958
1402.2656 | 123.6191 | -66.3803 | 57.1472 | 0.06235 | -0.06649 | -0.038997 | -0.067272 | -0.041832 | -0.045685 | 0.050216 | 0.0111 | 0.01704 | -0.0088356 | 0.1775 | 0.057752 | -0.031001 | 0.015142 | -0.012988 | 0.038393 | -0.013378 | 0.14197 | -0.040163 | 57.1388 | 0.12856 | -65.7608 | 57.0364 | 57.173 | 57.0297 | -66.6532 | 66.3401 | -57.1088 | 66.3493 | 66.3673 | 0.027175 | -57.1606 | -57.0053 | -0.27284 | -0.11081 | 123.5191 | 0.61947 | 0.89231 | 0.025763 | -0.11755 | 66.4187 | 66.3669 | 66.5223 | 66.3955 | -57.1874 | 123.4167 | 123.5533 | 123.41 | 66.5089 | -123.8004
1403.7344 | 123.7564 | -66.3528 | 57.1243 | 0.06235 | -0.065421 | -0.03686 | -0.066204 | -0.040764 | -0.043548 | 0.095999 | 0.010032 | 0.018108 | -0.0099036 | 0.17856 | 0.05882 | -0.026423 | 0.005985 | -0.017566 | 0.038393 | -0.017957 | 0.1557 | -0.040163 | 57.0792 | 1.2595 | -65.8158 | 56.9952 | 57.1272 | 56.9701 | -66.6989 | 66.3127 | -57.0859 | 66.3264 | 66.3353 | 0.022597 | -57.1423 | -56.9686 | -0.3461 | -0.12913 | 123.4321 | 0.53706 | 0.88316 | 0.002865 | -0.15418 | 66.3912 | 66.3349 | 66.5085 | 66.3588 | -57.1645 | 123.348 | 123.48 | 123.323 | 67.6123 | -123.8233
1404.2812 | 123.7244 | -66.3528 | 57.0694 | 0.06235 | -0.06649 | -0.037928 | -0.065135 | -0.041832 | -0.045685 | 0.080738 | 0.010032 | 0.018108 | -0.010972 | 0.17856 | 0.056684 | -0.026423 | 0.005985 | -0.003831 | 0.042971 | -0.017957 | 0.13281 | -0.035584 | 57.0701 | 2.7247 | -65.8158 | 56.9815 | 57.1135 | 56.961 | -66.6989 | 66.3173 | -57.0264 | 66.3264 | 66.349 | 0.031753 | -57.0874 | -56.9366 | -0.3461 | -0.087929 | 123.4229 | 0.53706 | 0.88316 | 0.044062 | -0.10841 | 66.3958 | 66.3349 | 66.4857 | 66.3588 | -57.105 | 123.3343 | 123.4663 | 123.3138 | 69.0775 | -123.7683
1405.2656 | 123.587 | -66.4169 | 57.0648 | 0.047088 | -0.065421 | -0.037928 | -0.067272 | -0.041832 | -0.046753 | 0.080738 | 0.0111 | 0.015972 | -0.0099036 | 0.17963 | 0.05882 | -0.026423 | 0.019721 | 0.000747 | 0.047549 | -0.022536 | 0.15112 | -0.040163 | 57.0472 | 3.2055 | -65.8341 | 56.9769 | 57.0906 | 56.9427 | -66.7356 | 66.3768 | -57.0173 | 66.3905 | 66.4177 | 0.04091 | -57.0874 | -56.9137 | -0.31864 | -0.08793 | 123.4641 | 0.58283 | 0.90148 | 0.025746 | -0.12215 | 66.4645 | 66.3944 | 66.5681 | 66.4367 | -57.105 | 123.3938 | 123.5075 | 123.3596 | 69.6224 | -123.8004
1406.2656 | 123.6053 | -66.4124 | 57.0831 | 0.06235 | -0.06649 | -0.037928 | -0.067272 | -0.0429 | -0.043548 | 0.050216 | 0.0068283 | 0.01704 | -0.0099036 | 0.17856 | 0.057752 | -0.031001 | 0.015142 | -0.008409 | 0.042971 | -0.013378 | 0.15112 | -0.035584 | 57.0472 | 3.8602 | -65.8478 | 56.9677 | 57.0906 | 56.9335 | -66.7402 | 66.3768 | -57.0402 | 66.3814 | 66.4039 | 0.027175 | -57.0965 | -56.932 | -0.3278 | -0.1154 | 123.4595 | 0.56452 | 0.89232 | 0.007435 | -0.14961 | 66.4553 | 66.399 | 66.5635 | 66.4275 | -57.1187 | 123.3801 | 123.5029 | 123.3459 | 70.2726 | -123.8233
1407.2656 | 123.6191 | -66.4627 | 57.0328 | 0.06235 | -0.065421 | -0.037928 | -0.066204 | -0.0429 | -0.044616 | 0.065477 | 0.0078963 | 0.015972 | -0.0099036 | 0.17856 | 0.05882 | -0.026423 | 0.019721 | -0.003831 | 0.052128 | -0.017957 | 0.1557 | -0.035584 | 57.0518 | 4.0983 | -65.8753 | 56.9586 | 57.086 | 56.9381 | -66.731 | 66.4271 | -56.9806 | 66.4363 | 66.4589 | 0.031753 | -57.0507 | -56.8771 | -0.26828 | -0.074201 | 123.5145 | 0.5874 | 0.85569 | 0.053211 | -0.094682 | 66.5148 | 66.4448 | 66.6184 | 66.4824 | -57.0684 | 123.4213 | 123.5487 | 123.4008 | 70.561 | -123.7638
1408.2969 | 123.587 | -66.5085 | 57.0282 | 0.047088 | -0.06649 | -0.035791 | -0.067272 | -0.0429 | -0.045685 | 0.065477 | 0.0089643 | 0.01704 | -0.0099036 | 0.1807 | 0.057752 | -0.026423 | 0.015142 | -0.003831 | 0.042971 | -0.022536 | 0.1557 | -0.031005 | 57.0151 | 4.3456 | -65.9028 | 56.9357 | 57.0585 | 56.9106 | -66.7676 | 66.4775 | -56.9852 | 66.4821 | 66.5047 | 0.027174 | -57.0507 | -56.8725 | -0.25914 | -0.092515 | 123.5236 | 0.60571 | 0.86485 | 0.030317 | -0.11758 | 66.5515 | 66.4859 | 66.6642 | 66.5236 | -57.0592 | 123.4442 | 123.567 | 123.4191 | 70.854 | -123.7958
1409.2656 | 123.642 | -66.4215 | 57.1014 | 0.031826 | -0.06649 | -0.035791 | -0.067272 | -0.0429 | -0.044616 | 0.050216 | 0.010032 | 0.015972 | -0.010972 | 0.17856 | 0.057752 | -0.021844 | 0.010564 | -0.008409 | 0.047549 | -0.017957 | 0.13739 | -0.031005 | 57.038 | 4.8629 | -65.8616 | 56.9494 | 57.0768 | 56.9473 | -66.7447 | 66.3905 | -57.0539 | 66.3997 | 66.4131 | 0.022596 | -57.1194 | -56.9641 | -0.32322 | -0.15202 | 123.4595 | 0.55994 | 0.88316 | -0.02461 | -0.15419 | 66.4691 | 66.4036 | 66.5589 | 66.4321 | -57.1324 | 123.3709 | 123.4983 | 123.3688 | 71.2845 | -123.8462
1410.2656 | 123.674 | -66.4948 | 57.0145 | 0.06235 | -0.067558 | -0.03686 | -0.067272 | -0.040764 | -0.044616 | 0.050216 | 0.0089643 | 0.01704 | -0.010972 | 0.17963 | 0.05882 | -0.031001 | 0.015142 | -0.012988 | 0.038393 | -0.017957 | 0.14197 | -0.035584 | 57.0197 | 4.8355 | -65.8845 | 56.9448 | 57.0631 | 56.9289 | -66.763 | 66.4592 | -56.9761 | 66.4637 | 66.4818 | 0.022596 | -57.0324 | -56.8725 | -0.26829 | -0.069625 | 123.5145 | 0.61029 | 0.87858 | 0.048629 | -0.085528 | 66.5331 | 66.4768 | 66.6367 | 66.5099 | -57.05 | 123.4396 | 123.5578 | 123.4237 | 71.3302 | -123.7775
1411.2656 | 123.6694 | -66.481 | 57.019 | 0.092874 | -0.067558 | -0.03686 | -0.067272 | -0.0429 | -0.046753 | 0.080738 | 0.0111 | 0.01704 | -0.0088356 | 0.1807 | 0.05882 | -0.026423 | 0.010564 | -0.008409 | 0.052128 | -0.017957 | 0.1557 | -0.035584 | 57.0197 | 5.4811 | -65.9028 | 56.9357 | 57.0539 | 56.9106 | -66.7722 | 66.4454 | -56.9669 | 66.4546 | 66.4726 | 0.027175 | -57.037 | -56.8633 | -0.29118 | -0.08336 | 123.5007 | 0.57824 | 0.86943 | 0.034894 | -0.10842 | 66.5331 | 66.4631 | 66.6367 | 66.4916 | -57.0546 | 123.4167 | 123.535 | 123.3916 | 71.9621 | -123.7912
1412.2656 | 123.6557 | -66.4398 | 57.0419 | 0.06235 | -0.067558 | -0.037928 | -0.065135 | -0.0429 | -0.046753 | 0.065477 | 0.0089643 | 0.015972 | -0.0099036 | 0.18177 | 0.05882 | -0.026423 | 0.015142 | -0.008409 | 0.033814 | -0.013378 | 0.1557 | -0.040163 | 57.0335 | 5.5452 | -65.8936 | 56.9494 | 57.0631 | 56.9198 | -66.763 | 66.3997 | -57.0081 | 66.4134 | 66.4314 | 0.031754 | -57.0553 | -56.8862 | -0.32323 | -0.092513 | 123.4733 | 0.5462 | 0.86943 | 0.021163 | -0.12215 | 66.4736 | 66.4264 | 66.5955 | 66.455 | -57.0821 | 123.3892 | 123.5029 | 123.3596 | 71.985 | -123.805
1413.2812 | 123.6237 | -66.4719 | 57.0145 | 0.047088 | -0.065421 | -0.035791 | -0.066204 | -0.0429 | -0.045685 | 0.050216 | 0.0089643 | 0.018108 | -0.0088356 | 0.18177 | 0.05882 | -0.026423 | 0.010564 | -0.003831 | 0.047549 | -0.017957 | 0.14197 | -0.031005 | 57.0472 | 5.0095 | -65.857 | 56.9632 | 57.086 | 56.9473 | -66.7447 | 66.4409 | -56.9669 | 66.4454 | 66.468 | 0.027174 | -57.0324 | -56.8725 | -0.27287 | -0.051311 | 123.5191 | 0.61487 | 0.88774 | 0.071522 | -0.067213 | 66.5194 | 66.4539 | 66.6138 | 66.4824 | -57.0455 | 123.435 | 123.5579 | 123.4191 | 71.4813 | -123.7592
1414.2656 | 123.6328 | -66.4581 | 57.0602 | 0.047088 | -0.067558 | -0.037928 | -0.066204 | -0.0429 | -0.044616 | 0.065477 | 0.010032 | 0.019177 | -0.0088356 | 0.1807 | 0.057752 | -0.026423 | 0.019721 | 0.000747 | 0.024657 | -0.008799 | 0.14655 | -0.031005 | 57.0289 | 5.3208 | -65.889 | 56.9494 | 57.0723 | 56.9244 | -66.7585 | 66.4271 | -57.0356 | 66.4317 | 66.4589 | 0.031752 | -57.069 | -56.9137 | -0.30034 | -0.11082 | 123.487 | 0.56909 | 0.86942 | 0.012009 | -0.13588 | 66.4828 | 66.4493 | 66.6047 | 66.4779 | -57.0912 | 123.4075 | 123.5304 | 123.3825 | 71.7789 | -123.8187
1415.2656 | 123.5916 | -66.4352 | 57.0786 | 0.077612 | -0.068627 | -0.037928 | -0.067272 | -0.0429 | -0.044616 | 0.080738 | 0.010032 | 0.015972 | -0.010972 | 0.17963 | 0.05882 | -0.026423 | 0.010564 | -0.008409 | 0.052128 | -0.017957 | 0.16486 | -0.031005 | 57.0426 | 4.7805 | -65.8524 | 56.9632 | 57.0906 | 56.9381 | -66.7447 | 66.4042 | -57.0264 | 66.4088 | 66.4268 | 0.022596 | -57.0965 | -56.9137 | -0.30949 | -0.1154 | 123.4779 | 0.58283 | 0.89232 | 0.012013 | -0.14046 | 66.4874 | 66.4173 | 66.6001 | 66.4458 | -57.1096 | 123.3984 | 123.5258 | 123.3733 | 71.2158 | -123.8233
1416.2656 | 123.6511 | -66.4215 | 57.0694 | 0.06235 | -0.06649 | -0.037928 | -0.066204 | -0.040764 | -0.044616 | 0.065477 | 0.0089643 | 0.018108 | -0.010972 | 0.1807 | 0.05882 | -0.031001 | 0.010564 | -0.012988 | 0.042971 | -0.022536 | 0.15112 | -0.035584 | 57.0426 | 5.1468 | -65.8707 | 56.9586 | 57.0768 | 56.9335 | -66.7493 | 66.3859 | -57.0264 | 66.3905 | 66.4085 | 0.022596 | -57.0919 | -56.9183 | -0.3278 | -0.11082 | 123.4641 | 0.55078 | 0.87858 | 0.007433 | -0.13588 | 66.4645 | 66.399 | 66.5726 | 66.4321 | -57.105 | 123.3801 | 123.4983 | 123.355 | 71.5683 | -123.8187
1417.2656 | 123.6191 | -66.4261 | 57.074 | 0.077612 | -0.067558 | -0.037928 | -0.067272 | -0.041832 | -0.045685 | 0.065477 | 0.010032 | 0.018108 | -0.0099036 | 0.18177 | 0.057752 | -0.026423 | 0.015142 | -0.012988 | 0.047549 | -0.022536 | 0.1557 | -0.040163 | 57.0335 | 4.8813 | -65.8799 | 56.9494 | 57.0723 | 56.9244 | -66.7539 | 66.3859 | -57.0264 | 66.3997 | 66.4131 | 0.027175 | -57.0965 | -56.9183 | -0.3278 | -0.12456 | 123.4595 | 0.5462 | 0.874 | -0.001724 | -0.14962 | 66.4736 | 66.4035 | 66.5818 | 66.4412 | -57.1141 | 123.3755 | 123.4983 | 123.3504 | 71.3073 | -123.8279
1418.2812 | 123.587 | -66.481 | 57.0145 | 0.047088 | -0.067558 | -0.037928 | -0.070477 | -0.0429 | -0.046753 | 0.065477 | 0.0078963 | 0.018108 | -0.010972 | 0.1807 | 0.05882 | -0.026423 | 0.015142 | -0.008409 | 0.042971 | -0.013378 | 0.14197 | -0.031005 | 57.0335 | 5.4078 | -65.8845 | 56.9494 | 57.0723 | 56.9106 | -66.7539 | 66.45 | -56.9715 | 66.4546 | 66.4726 | 0.022596 | -57.0278 | -56.8725 | -0.27287 | -0.065047 | 123.5145 | 0.59656 | 0.86942 | 0.057786 | -0.10384 | 66.524 | 66.4676 | 66.623 | 66.4962 | -57.0455 | 123.4304 | 123.5533 | 123.3916 | 71.8888 | -123.7684
1419.2656 | 123.6237 | -66.4856 | 57.0374 | 0.06235 | -0.069695 | -0.03686 | -0.067272 | -0.041832 | -0.044616 | 0.095999 | 0.0089643 | 0.01704 | -0.0088356 | 0.17856 | 0.057752 | -0.026423 | 0.010564 | -0.008409 | 0.038393 | -0.017957 | 0.16028 | -0.040163 | 57.006 | 5.5818 | -65.9028 | 56.9265 | 57.0585 | 56.9015 | -66.763 | 66.4454 | -56.999 | 66.4592 | 66.4772 | 0.031754 | -57.0553 | -56.8771 | -0.27745 | -0.11083 | 123.4916 | 0.58282 | 0.86027 | 0.021161 | -0.13589 | 66.524 | 66.4676 | 66.6459 | 66.4962 | -57.0775 | 123.4121 | 123.5441 | 123.3871 | 72.0674 | -123.8004
1420.2656 | 123.6603 | -66.4444 | 57.0374 | 0.06235 | -0.067558 | -0.03686 | -0.067272 | -0.041832 | -0.044616 | 0.065477 | 0.010032 | 0.015972 | -0.0088356 | 0.18177 | 0.057752 | -0.03558 | 0.015142 | -0.003831 | 0.029236 | -0.022536 | 0.14655 | -0.031005 | 57.0106 | 5.2613 | -65.8936 | 56.9265 | 57.0539 | 56.9015 | -66.7768 | 66.4134 | -57.0081 | 66.4088 | 66.4406 | 0.027174 | -57.0599 | -56.8908 | -0.33238 | -0.11083 | 123.455 | 0.55078 | 0.88316 | 0.016583 | -0.13589 | 66.4736 | 66.4219 | 66.5909 | 66.4595 | -57.0684 | 123.3709 | 123.4983 | 123.3459 | 71.7057 | -123.8141
1421.2656 | 123.6282 | -66.449 | 57.0648 | 0.06235 | -0.068627 | -0.038997 | -0.067272 | -0.041832 | -0.045685 | 0.034955 | 0.0089643 | 0.014904 | -0.019518 | 0.18284 | 0.057752 | -0.03558 | 0.015142 | -0.008409 | 0.042971 | -0.017957 | 0.15112 | -0.031005 | 57.0197 | 5.275 | -65.8753 | 56.9403 | 57.0677 | 56.9244 | -66.763 | 66.418 | -57.0218 | 66.4134 | 66.4406 | 0.022596 | -57.0828 | -56.9137 | -0.31407 | -0.12456 | 123.4687 | 0.57367 | 0.88774 | 0.002853 | -0.14046 | 66.4919 | 66.431 | 66.6001 | 66.4641 | -57.0958 | 123.3892 | 123.5166 | 123.3733 | 71.724 | -123.8279
1422.2656 | 123.7701 | -66.4398 | 56.9733 | 0.06235 | -0.067558 | -0.03686 | -0.06834 | -0.040764 | -0.044616 | 0.050216 | 0.0078963 | 0.014904 | -0.022723 | 0.17963 | 0.057752 | -0.021844 | 0.010564 | -0.008409 | 0.038393 | -0.017957 | 0.14655 | -0.026426 | 57.0014 | 5.5864 | -65.9257 | 56.9219 | 57.0448 | 56.8969 | -66.7859 | 66.4134 | -56.9349 | 66.418 | 66.4314 | 0.018017 | -56.9912 | -56.8267 | -0.34612 | -0.05132 | 123.4412 | 0.51415 | 0.86027 | 0.071512 | -0.07638 | 66.4782 | 66.4219 | 66.5864 | 66.4504 | -56.9997 | 123.3618 | 123.4846 | 123.3367 | 72.0262 | -123.7592
1423.2812 | 123.6328 | -66.4719 | 57.019 | 0.047088 | -0.067558 | -0.037928 | -0.067272 | -0.041832 | -0.045685 | 0.050216 | 0.0089643 | 0.015972 | -0.020586 | 0.18284 | 0.057752 | -0.026423 | 0.005985 | -0.008409 | 0.029236 | -0.017957 | 0.14655 | -0.035584 | 57.0014 | 5.6322 | -65.9303 | 56.9174 | 57.0402 | 56.8969 | -66.7814 | 66.4363 | -56.9898 | 66.4454 | 66.4635 | 0.027175 | -57.037 | -56.8725 | -0.3095 | -0.10167 | 123.4733 | 0.54161 | 0.85111 | 0.021158 | -0.12216 | 66.5011 | 66.4539 | 66.6184 | 66.4778 | -57.0546 | 123.3892 | 123.5121 | 123.3688 | 72.104 | -123.8004
1424.2656 | 123.7335 | -66.4352 | 57.0007 | 0.077612 | -0.069695 | -0.038997 | -0.06834 | -0.0429 | -0.045685 | 0.080738 | 0.0078963 | 0.015972 | -0.021654 | 0.18177 | 0.056684 | -0.031001 | 0.010564 | -0.003831 | 0.061284 | -0.017957 | 0.14655 | -0.040163 | 57.006 | 5.8245 | -65.9257 | 56.9357 | 57.0585 | 56.9015 | -66.7676 | 66.3951 | -56.9394 | 66.4042 | 66.4314 | 0.036332 | -57.0187 | -56.8542 | -0.33238 | -0.065049 | 123.4412 | 0.50957 | 0.84195 | 0.057783 | -0.099266 | 66.4965 | 66.4173 | 66.5818 | 66.4458 | -57.0409 | 123.3709 | 123.4938 | 123.3367 | 72.2597 | -123.7684
1425.2656 | 123.7244 | -66.4307 | 57.0328 | 0.06235 | -0.068627 | -0.037928 | -0.06834 | -0.043968 | -0.044616 | 0.080738 | 0.0078963 | 0.015972 | -0.021654 | 0.1807 | 0.056684 | -0.031001 | 0.005985 | -0.017566 | 0.052128 | -0.022536 | 0.16028 | -0.031005 | 57.0151 | 5.7695 | -65.9211 | 56.9357 | 57.0631 | 56.9106 | -66.7676 | 66.3997 | -56.9806 | 66.3997 | 66.4131 | 0.013439 | -57.0553 | -56.8725 | -0.33696 | -0.097093 | 123.4458 | 0.50957 | 0.84653 | 0.030318 | -0.12215 | 66.4828 | 66.4081 | 66.5909 | 66.4366 | -57.0638 | 123.3663 | 123.4938 | 123.3413 | 72.2002 | -123.8004
1426.2656 | 123.7427 | -66.3986 | 57.0145 | 0.06235 | -0.068627 | -0.038997 | -0.06834 | -0.041832 | -0.044616 | 0.080738 | 0.0089643 | 0.014904 | -0.021654 | 0.18177 | 0.055616 | -0.03558 | 0.010564 | -0.008409 | 0.029236 | -0.008799 | 0.15112 | -0.040163 | 57.0243 | 6.3602 | -65.9257 | 56.9403 | 57.0631 | 56.9198 | -66.7676 | 66.3585 | -56.9852 | 66.363 | 66.3902 | 0.031754 | -57.0233 | -56.8633 | -0.369 | -0.074204 | 123.4229 | 0.47295 | 0.84195 | 0.048629 | -0.094685 | 66.4279 | 66.3898 | 66.5497 | 66.4092 | -57.0546 | 123.3389 | 123.4617 | 123.3184 | 72.7588 | -123.7821
1427.2656 | 123.6282 | -66.4032 | 57.0648 | 0.06235 | -0.069695 | -0.040065 | -0.069409 | -0.0429 | -0.044616 | 0.065477 | 0.0078963 | 0.013835 | -0.021654 | 0.1807 | 0.056684 | -0.031001 | 0.015142 | -0.012988 | 0.029236 | -0.017957 | 0.16944 | -0.049321 | 57.038 | 6.0076 | -65.9119 | 56.9632 | 57.0906 | 56.9381 | -66.7356 | 66.3539 | -57.0356 | 66.3722 | 66.3902 | 0.036333 | -57.0828 | -56.8954 | -0.33237 | -0.10166 | 123.4412 | 0.49126 | 0.82364 | 0.025746 | -0.12673 | 66.4324 | 66.3852 | 66.5726 | 66.4183 | -57.1141 | 123.3664 | 123.4938 | 123.3413 | 72.4108 | -123.8004
1428.2812 | 123.642 | -66.4398 | 57.0786 | 0.047088 | -0.069695 | -0.037928 | -0.06834 | -0.041832 | -0.044616 | 0.080738 | 0.0078963 | 0.013835 | -0.020586 | 0.18177 | 0.056684 | -0.026423 | 0.010564 | -0.008409 | 0.024657 | -0.022536 | 0.14655 | -0.035584 | 57.0472 | 6.0259 | -65.8936 | 56.9632 | 57.0906 | 56.9427 | -66.7356 | 66.4042 | -57.0539 | 66.4134 | 66.4314 | 0.027175 | -57.1011 | -56.932 | -0.29575 | -0.1154 | 123.487 | 0.5462 | 0.84195 | 0.012013 | -0.13588 | 66.4645 | 66.4173 | 66.5864 | 66.4504 | -57.1141 | 123.403 | 123.5304 | 123.3825 | 72.4658 | -123.8141
1429.2656 | 123.7061 | -66.4124 | 57.0419 | 0.047088 | -0.067558 | -0.03686 | -0.06834 | -0.041832 | -0.045685 | 0.065477 | 0.0078963 | 0.014904 | -0.020586 | 0.18177 | 0.057752 | -0.031001 | 0.015142 | -0.012988 | 0.042971 | -0.022536 | 0.16028 | -0.040163 | 57.0243 | 6.5525 | -65.9394 | 56.954 | 57.0723 | 56.9289 | -66.7539 | 66.3722 | -56.999 | 66.3814 | 66.3994 | 0.027175 | -57.0645 | -56.8817 | -0.34153 | -0.087934 | 123.4367 | 0.47295 | 0.81448 | 0.03032 | -0.11299 | 66.4553 | 66.3898 | 66.5726 | 66.4275 | -57.0821 | 123.3664 | 123.4846 | 123.3413 | 72.9648 | -123.7958
1430.2656 | 123.7701 | -66.394 | 57.0374 | 0.077612 | -0.068627 | -0.037928 | -0.066204 | -0.040764 | -0.045685 | 0.050216 | 0.0089643 | 0.014904 | -0.022723 | 0.18284 | 0.055616 | -0.026423 | 0.005985 | -0.012988 | 0.029236 | -0.017957 | 0.13739 | -0.026426 | 57.0472 | 5.884 | -65.9028 | 56.9723 | 57.0997 | 56.9656 | -66.7264 | 66.3676 | -57.0081 | 66.3676 | 66.3811 | 0.013438 | -57.0553 | -56.9 | -0.33237 | -0.065043 | 123.4412 | 0.49126 | 0.82364 | 0.062369 | -0.071788 | 66.4233 | 66.3761 | 66.5314 | 66.4 | -57.0638 | 123.3664 | 123.4938 | 123.3596 | 72.278 | -123.7638
1431.2656 | 123.7244 | -66.3528 | 57.0602 | 0.06235 | -0.069695 | -0.038997 | -0.06834 | -0.043968 | -0.046753 | 0.050216 | 0.010032 | 0.014904 | -0.021654 | 0.18284 | 0.055616 | -0.03558 | 0.015142 | -0.008409 | 0.033814 | -0.017957 | 0.13739 | -0.035584 | 57.0472 | 5.6871 | -65.9028 | 56.9769 | 57.0997 | 56.9564 | -66.7356 | 66.3173 | -57.0264 | 66.3173 | 66.3444 | 0.027175 | -57.0782 | -56.9229 | -0.38273 | -0.083353 | 123.4 | 0.45007 | 0.83279 | 0.039481 | -0.10383 | 66.3867 | 66.3349 | 66.4902 | 66.368 | -57.0958 | 123.3297 | 123.4526 | 123.3093 | 72.04 | -123.7958
1432.2812 | 123.7244 | -66.3666 | 57.0694 | 0.06235 | -0.069695 | -0.038997 | -0.06834 | -0.0429 | -0.045685 | 0.080738 | 0.0089643 | 0.015972 | -0.022723 | 0.18284 | 0.056684 | -0.031001 | 0.010564 | -0.017566 | 0.047549 | -0.013378 | 0.15112 | -0.026426 | 57.0335 | 5.4902 | -65.9165 | 56.9723 | 57.0951 | 56.9518 | -66.731 | 66.3402 | -57.0218 | 66.3356 | 66.349 | 0.00886 | -57.0828 | -56.9183 | -0.36442 | -0.097086 | 123.4 | 0.45006 | 0.81448 | 0.025747 | -0.11757 | 66.4141 | 66.3532 | 66.5177 | 66.3771 | -57.0958 | 123.3389 | 123.4617 | 123.3184 | 71.8568 | -123.8004
1433.2812 | 123.6328 | -66.3895 | 57.1014 | 0.06235 | -0.069695 | -0.038997 | -0.067272 | -0.041832 | -0.045685 | 0.080738 | 0.0078963 | 0.014904 | -0.022723 | 0.18177 | 0.055616 | -0.026423 | 0.010564 | 0.000747 | 0.052128 | -0.013378 | 0.14655 | -0.044742 | 57.0426 | 5.8657 | -65.9257 | 56.9677 | 57.0906 | 56.9518 | -66.7264 | 66.3447 | -57.0493 | 66.363 | 66.3902 | 0.045489 | -57.1148 | -56.9549 | -0.33695 | -0.13371 | 123.4321 | 0.46379 | 0.80074 | -0.010875 | -0.14961 | 66.4416 | 66.3761 | 66.536 | 66.4 | -57.1462 | 123.3572 | 123.48 | 123.3413 | 72.2552 | -123.8279
1434.2656 | 123.7198 | -66.3895 | 57.0328 | 0.06235 | -0.069695 | -0.03686 | -0.06834 | -0.0429 | -0.045685 | 0.065477 | 0.0068283 | 0.013835 | -0.020586 | 0.18284 | 0.056684 | -0.03558 | 0.010564 | -0.012988 | 0.038393 | -0.00422 | 0.15112 | -0.031005 | 57.038 | 5.8886 | -65.9257 | 56.9586 | 57.0814 | 56.9381 | -66.7447 | 66.3585 | -56.9944 | 66.3539 | 66.3765 | 0.018017 | -57.037 | -56.8817 | -0.35527 | -0.074201 | 123.4275 | 0.46379 | 0.81906 | 0.048632 | -0.094682 | 66.4279 | 66.3852 | 66.5406 | 66.4 | -57.0638 | 123.348 | 123.4709 | 123.3276 | 72.278 | -123.7775
1435.2656 | 123.7015 | -66.394 | 57.0282 | 0.047088 | -0.068627 | -0.040065 | -0.070477 | -0.0429 | -0.047821 | 0.080738 | 0.0089643 | 0.015972 | -0.021654 | 0.18177 | 0.056684 | -0.026423 | 0.015142 | -0.012988 | 0.052128 | -0.022536 | 0.15112 | -0.035584 | 57.006 | 5.797 | -65.9486 | 56.9403 | 57.0585 | 56.9015 | -66.7676 | 66.3585 | -56.9761 | 66.3676 | 66.3811 | 0.022596 | -57.0507 | -56.8771 | -0.37358 | -0.087937 | 123.4 | 0.44548 | 0.81906 | 0.030317 | -0.12673 | 66.4462 | 66.3715 | 66.5452 | 66.4092 | -57.0638 | 123.3343 | 123.4526 | 123.2955 | 72.191 | -123.7958
1436.2656 | 123.6786 | -66.4124 | 57.0282 | 0.06235 | -0.069695 | -0.041133 | -0.06834 | -0.0429 | -0.045685 | 0.050216 | 0.0078963 | 0.014904 | -0.021654 | 0.18284 | 0.054547 | -0.026423 | 0.010564 | -0.003831 | 0.029236 | -0.017957 | 0.14197 | -0.035584 | 57.0014 | 5.7787 | -65.9531 | 56.9357 | 57.0585 | 56.9244 | -66.7722 | 66.3768 | -56.999 | 66.3859 | 66.4085 | 0.031753 | -57.0462 | -56.8862 | -0.35985 | -0.092515 | 123.4138 | 0.45921 | 0.81906 | 0.030317 | -0.10384 | 66.4416 | 66.3944 | 66.5543 | 66.4229 | -57.0638 | 123.348 | 123.4709 | 123.3367 | 72.191 | -123.8004
1437.2656 | 123.6969 | -66.4444 | 56.9962 | 0.06235 | -0.068627 | -0.038997 | -0.069409 | -0.0429 | -0.046753 | 0.065477 | 0.010032 | 0.014904 | -0.022723 | 0.18177 | 0.055616 | -0.021844 | 0.015142 | -0.008409 | 0.047549 | -0.017957 | 0.12823 | -0.031005 | 56.9877 | 5.6459 | -65.9577 | 56.9357 | 57.0539 | 56.906 | -66.7722 | 66.4134 | -56.9486 | 66.4226 | 66.436 | 0.022596 | -57.0141 | -56.8679 | -0.32781 | -0.060472 | 123.4321 | 0.48667 | 0.81448 | 0.057782 | -0.090111 | 66.4919 | 66.4264 | 66.5726 | 66.4595 | -57.0272 | 123.3801 | 123.4983 | 123.3504 | 72.0903 | -123.7684
1438.2812 | 123.7381 | -66.4032 | 57.0145 | 0.06235 | -0.069695 | -0.038997 | -0.069409 | -0.043968 | -0.046753 | 0.065477 | 0.0068283 | 0.01704 | -0.022723 | 0.18391 | 0.056684 | -0.026423 | 0.005985 | -0.012988 | 0.029236 | -0.013378 | 0.13739 | -0.040163 | 57.006 | 5.1102 | -65.9486 | 56.9357 | 57.0631 | 56.9289 | -66.7585 | 66.363 | -56.9852 | 66.3768 | 66.3902 | 0.027175 | -57.0278 | -56.8771 | -0.35527 | -0.078782 | 123.4092 | 0.45463 | 0.8099 | 0.048629 | -0.085528 | 66.4324 | 66.3898 | 66.5406 | 66.4092 | -57.0546 | 123.3389 | 123.4663 | 123.3321 | 71.5134 | -123.7729
1439.2656 | 123.6832 | -66.4124 | 57.0282 | 0.047088 | -0.070763 | -0.03686 | -0.067272 | -0.043968 | -0.043548 | 0.065477 | 0.0078963 | 0.015972 | -0.022723 | 0.18284 | 0.055616 | -0.031001 | 0.010564 | -0.008409 | 0.029236 | -0.013378 | 0.16028 | -0.031005 | 57.0106 | 5.4261 | -65.9303 | 56.9494 | 57.0631 | 56.9244 | -66.7539 | 66.3813 | -56.999 | 66.3814 | 66.4039 | 0.022596 | -57.0416 | -56.8679 | -0.34153 | -0.07878 | 123.4229 | 0.4821 | 0.82364 | 0.034896 | -0.10384 | 66.4416 | 66.399 | 66.5726 | 66.4229 | -57.0592 | 123.3618 | 123.4754 | 123.3367 | 71.8385 | -123.7821
1440.2656 | 123.6877 | -66.4398 | 57.0282 | 0.031826 | -0.069695 | -0.037928 | -0.06834 | -0.041832 | -0.044616 | 0.065477 | 0.0089643 | 0.014904 | -0.021654 | 0.18284 | 0.057752 | -0.031001 | 0.010564 | -0.012988 | 0.038393 | -0.013378 | 0.1557 | -0.035584 | 57.006 | 6.0397 | -65.9303 | 56.9494 | 57.0723 | 56.9289 | -66.7585 | 66.4042 | -56.9898 | 66.4088 | 66.4268 | 0.022596 | -57.0416 | -56.8725 | -0.31865 | -0.07878 | 123.4458 | 0.50957 | 0.82822 | 0.044053 | -0.099261 | 66.4782 | 66.4264 | 66.5955 | 66.4504 | -57.0638 | 123.3892 | 123.5121 | 123.3688 | 72.4795 | -123.7867
1441.2812 | 123.6923 | -66.4124 | 57.0602 | 0.077612 | -0.069695 | -0.037928 | -0.06834 | -0.041832 | -0.046753 | 0.050216 | 0.0089643 | 0.014904 | -0.022723 | 0.18391 | 0.055616 | -0.031001 | 0.015142 | -0.012988 | 0.033814 | -0.017957 | 0.16028 | -0.040163 | 57.0197 | 5.6871 | -65.9303 | 56.954 | 57.0723 | 56.9244 | -66.7493 | 66.3722 | -57.0264 | 66.3814 | 66.3994 | 0.027175 | -57.0782 | -56.9 | -0.33695 | -0.10625 | 123.4321 | 0.4821 | 0.81906 | 0.012009 | -0.13588 | 66.4462 | 66.3944 | 66.5726 | 66.4275 | -57.1004 | 123.3664 | 123.4846 | 123.3367 | 72.0995 | -123.8096
1442.2656 | 123.7015 | -66.4124 | 57.0099 | 0.06235 | -0.069695 | -0.040065 | -0.069409 | -0.0429 | -0.045685 | 0.034955 | 0.0089643 | 0.015972 | -0.021654 | 0.18391 | 0.056684 | -0.03558 | 0.010564 | -0.008409 | 0.033814 | -0.013378 | 0.16486 | -0.040163 | 57.0151 | 5.4399 | -65.9303 | 56.9311 | 57.0585 | 56.906 | -66.763 | 66.3722 | -56.9761 | 66.3768 | 66.4039 | 0.031754 | -57.0233 | -56.845 | -0.35069 | -0.078784 | 123.4275 | 0.4821 | 0.8328 | 0.048627 | -0.10384 | 66.4462 | 66.399 | 66.5772 | 66.4229 | -57.0501 | 123.3435 | 123.4709 | 123.3184 | 71.8522 | -123.7729
1443.2812 | 123.7427 | -66.4124 | 57.0099 | 0.06235 | -0.070763 | -0.03686 | -0.06834 | -0.041832 | -0.046753 | 0.050216 | 0.0068283 | 0.014904 | -0.022723 | 0.18284 | 0.056684 | -0.031001 | 0.015142 | 0.000747 | 0.047549 | -0.017957 | 0.16944 | -0.035584 | 57.006 | 5.5131 | -65.944 | 56.9357 | 57.0539 | 56.9152 | -66.763 | 66.3768 | -56.9623 | 66.3814 | 66.4131 | 0.036331 | -57.0278 | -56.8404 | -0.35069 | -0.074205 | 123.4183 | 0.46837 | 0.81906 | 0.044049 | -0.094687 | 66.4599 | 66.3944 | 66.5818 | 66.4275 | -57.0455 | 123.348 | 123.4663 | 123.3276 | 71.9255 | -123.7729
1444.2656 | 123.6969 | -66.4352 | 56.9962 | 0.031826 | -0.071832 | -0.037928 | -0.070477 | -0.0429 | -0.046753 | 0.034955 | 0.010032 | 0.015972 | -0.023791 | 0.18284 | 0.056684 | -0.031001 | 0.010564 | -0.008409 | 0.042971 | -0.008799 | 0.14655 | -0.035584 | 56.9968 | 5.6139 | -65.9669 | 56.9265 | 57.0494 | 56.8923 | -66.7814 | 66.3997 | -56.9532 | 66.4042 | 66.4268 | 0.027175 | -57.005 | -56.8496 | -0.34612 | -0.069629 | 123.4321 | 0.46836 | 0.81448 | 0.053203 | -0.10385 | 66.4782 | 66.4264 | 66.5818 | 66.4458 | -57.0317 | 123.3618 | 123.4846 | 123.3276 | 72.0491 | -123.7775
1445.2656 | 123.7015 | -66.3895 | 57.0099 | 0.047088 | -0.071832 | -0.038997 | -0.06834 | -0.0429 | -0.045685 | 0.065477 | 0.0089643 | 0.015972 | -0.022723 | 0.18391 | 0.057752 | -0.031001 | 0.015142 | -0.012988 | 0.029236 | -0.008799 | 0.16028 | -0.031005 | 57.0197 | 5.5085 | -65.9486 | 56.9403 | 57.0631 | 56.9244 | -66.7539 | 66.3585 | -56.9807 | 66.3585 | 66.3765 | 0.018017 | -57.0187 | -56.8496 | -0.36442 | -0.069627 | 123.4092 | 0.4409 | 0.80532 | 0.053206 | -0.085529 | 66.4187 | 66.3807 | 66.5497 | 66.4046 | -57.0409 | 123.3297 | 123.4526 | 123.3138 | 71.898 | -123.7638
1446.2812 | 123.7015 | -66.3528 | 57.0923 | 0.077612 | -0.070763 | -0.03686 | -0.067272 | -0.043968 | -0.044616 | 0.095999 | 0.0057593 | 0.014904 | -0.021654 | 0.18497 | 0.057752 | -0.031001 | 0.015142 | -0.012988 | 0.061284 | -0.017957 | 0.17402 | -0.040163 | 57.0564 | 5.2155 | -65.9074 | 56.9815 | 57.0951 | 56.9473 | -66.7264 | 66.3127 | -57.031 | 66.3218 | 66.3399 | 0.027175 | -57.1102 | -56.9183 | -0.37357 | -0.11082 | 123.4092 | 0.44549 | 0.81906 | 0.002859 | -0.14503 | 66.4141 | 66.3349 | 66.5269 | 66.368 | -57.1324 | 123.3343 | 123.448 | 123.3001 | 71.5684 | -123.8187
1447.2656 | 123.761 | -66.4124 | 57.0145 | 0.047088 | -0.071832 | -0.038997 | -0.06834 | -0.0429 | -0.044616 | 0.065477 | 0.0078963 | 0.015972 | -0.023791 | 0.18391 | 0.055616 | -0.026423 | 0.005985 | -0.003831 | 0.056706 | -0.017957 | 0.16486 | -0.040163 | 57.0426 | 5.7375 | -65.9119 | 56.9677 | 57.0951 | 56.9335 | -66.731 | 66.3722 | -56.9578 | 66.3859 | 66.4085 | 0.036332 | -57.0324 | -56.8496 | -0.31864 | -0.046733 | 123.455 | 0.50042 | 0.81906 | 0.080679 | -0.080949 | 66.4691 | 66.3944 | 66.5772 | 66.4183 | -57.0546 | 123.3801 | 123.5075 | 123.3459 | 72.1498 | -123.7455
1448.2656 | 123.7335 | -66.4032 | 57.0099 | 0.047088 | -0.073968 | -0.037928 | -0.06834 | -0.041832 | -0.046753 | 0.080738 | 0.0057593 | 0.013835 | -0.023791 | 0.18284 | 0.054547 | -0.031001 | 0.005985 | -0.003831 | 0.020079 | -0.013378 | 0.1557 | -0.040163 | 57.038 | 6.1908 | -65.9211 | 56.9677 | 57.0951 | 56.9473 | -66.7356 | 66.363 | -56.9898 | 66.3722 | 66.3994 | 0.036332 | -57.0233 | -56.8542 | -0.33237 | -0.042156 | 123.4412 | 0.48211 | 0.81448 | 0.085256 | -0.062636 | 66.4233 | 66.3898 | 66.5589 | 66.4092 | -57.0501 | 123.3709 | 123.4983 | 123.3504 | 72.594 | -123.7455
1449.2656 | 123.7518 | -66.4352 | 56.9962 | 0.047088 | -0.071832 | -0.040065 | -0.06834 | -0.041832 | -0.046753 | 0.065477 | 0.0089643 | 0.015972 | -0.022723 | 0.18497 | 0.054547 | -0.031001 | 0.005985 | -0.008409 | 0.047549 | -0.013378 | 0.14655 | -0.040163 | 57.0426 | 6.3281 | -65.9303 | 56.9586 | 57.086 | 56.9244 | -66.7447 | 66.3951 | -56.9486 | 66.4042 | 66.4268 | 0.031754 | -57.0095 | -56.8496 | -0.30949 | -0.03758 | 123.4779 | 0.50499 | 0.81448 | 0.089832 | -0.071796 | 66.4828 | 66.4219 | 66.5818 | 66.4412 | -57.0363 | 123.3938 | 123.5212 | 123.3596 | 72.7634 | -123.7409
1450.2656 | 123.642 | -66.4627 | 56.987 | 0.031826 | -0.073968 | -0.040065 | -0.069409 | -0.0429 | -0.044616 | 0.080738 | 0.0089643 | 0.013835 | -0.023791 | 0.18391 | 0.055616 | -0.026423 | 0.010564 | -0.003831 | 0.047549 | -0.013378 | 0.16944 | -0.040163 | 57.0106 | 6.6349 | -65.9577 | 56.9357 | 57.0585 | 56.9106 | -66.7768 | 66.4225 | -56.9395 | 66.4363 | 66.4589 | 0.036332 | -57.0004 | -56.8176 | -0.31407 | -0.051317 | 123.4733 | 0.50499 | 0.81906 | 0.071515 | -0.076377 | 66.5103 | 66.4493 | 66.6321 | 66.4733 | -57.0272 | 123.3984 | 123.5212 | 123.3733 | 73.0976 | -123.7638
1451.2812 | 123.674 | -66.4307 | 57.0374 | 0.06235 | -0.0729 | -0.040065 | -0.069409 | -0.041832 | -0.045685 | 0.065477 | 0.0089643 | 0.015972 | -0.023791 | 0.18497 | 0.056684 | -0.017266 | 0.005985 | -0.012988 | 0.061284 | -0.013378 | 0.16486 | -0.040163 | 57.0151 | 6.1999 | -65.9486 | 56.9494 | 57.0631 | 56.9198 | -66.7585 | 66.3905 | -56.9761 | 66.4134 | 66.4177 | 0.027175 | -57.0507 | -56.8725 | -0.3278 | -0.087936 | 123.4458 | 0.4821 | 0.8099 | 0.02574 | -0.11757 | 66.4919 | 66.4173 | 66.5955 | 66.4366 | -57.0775 | 123.3801 | 123.4938 | 123.3504 | 72.6306 | -123.7958
1452.2656 | 123.7061 | -66.4352 | 56.9778 | 0.031826 | -0.0729 | -0.040065 | -0.06834 | -0.043968 | -0.046753 | 0.065477 | 0.0078963 | 0.014904 | -0.022723 | 0.18391 | 0.055616 | -0.026423 | 0.010564 | 0.000747 | 0.052128 | -0.017957 | 0.15112 | -0.031005 | 57.0151 | 6.2961 | -65.9577 | 56.9403 | 57.0677 | 56.906 | -66.7768 | 66.4042 | -56.9257 | 66.4088 | 66.436 | 0.031752 | -56.9958 | -56.8267 | -0.34154 | -0.037583 | 123.4504 | 0.47752 | 0.81906 | 0.089828 | -0.0718 | 66.4874 | 66.4173 | 66.5864 | 66.4458 | -57.0088 | 123.3755 | 123.5029 | 123.3413 | 72.7313 | -123.7546
1453.2812 | 123.6969 | -66.4124 | 57.0053 | 0.047088 | -0.0729 | -0.038997 | -0.06834 | -0.0429 | -0.044616 | 0.080738 | 0.0068283 | 0.014904 | -0.024859 | 0.18391 | 0.056684 | -0.017266 | 0.015142 | -0.008409 | 0.029236 | -0.008799 | 0.16944 | -0.031005 | 57.0243 | 6.0855 | -65.9303 | 56.954 | 57.0723 | 56.9152 | -66.7539 | 66.3813 | -56.9761 | 66.3951 | 66.4039 | 0.022596 | -57.0141 | -56.8359 | -0.34153 | -0.051313 | 123.4367 | 0.4821 | 0.82364 | 0.066941 | -0.090109 | 66.4416 | 66.4036 | 66.5818 | 66.4275 | -57.0363 | 123.3664 | 123.4846 | 123.3276 | 72.4978 | -123.7592
1454.2656 | 123.6465 | -66.4627 | 56.9824 | 0.016564 | -0.071832 | -0.037928 | -0.067272 | -0.041832 | -0.046753 | 0.050216 | 0.0068283 | 0.015972 | -0.022723 | 0.18711 | 0.055616 | -0.031001 | 0.015142 | -0.008409 | 0.052128 | -0.017957 | 0.1557 | -0.031005 | 57.0014 | 6.264 | -65.9486 | 56.9357 | 57.0585 | 56.8969 | -66.7768 | 66.4317 | -56.9303 | 66.4317 | 66.4543 | 0.022596 | -57.0004 | -56.8267 | -0.31407 | -0.046739 | 123.4641 | 0.51414 | 0.82822 | 0.076093 | -0.085535 | 66.5148 | 66.4448 | 66.6184 | 66.4779 | -57.0134 | 123.3984 | 123.5212 | 123.3596 | 72.7267 | -123.7592
1455.2656 | 123.6237 | -66.4444 | 57.0786 | 0.047088 | -0.0729 | -0.040065 | -0.067272 | -0.041832 | -0.046753 | 0.034955 | 0.0089643 | 0.015972 | -0.021654 | 0.18604 | 0.056684 | -0.021844 | 0.015142 | -0.008409 | 0.061284 | -0.013378 | 0.18317 | -0.035584 | 57.0289 | 5.8977 | -65.8616 | 56.9586 | 57.0814 | 56.9381 | -66.7493 | 66.4088 | -57.0173 | 66.4226 | 66.436 | 0.027175 | -57.0919 | -56.8954 | -0.30491 | -0.11998 | 123.4733 | 0.58283 | 0.88774 | 0.002856 | -0.14046 | 66.5057 | 66.431 | 66.6276 | 66.4595 | -57.1141 | 123.403 | 123.5258 | 123.3825 | 72.3421 | -123.8279
1456.2812 | 123.6969 | -66.4169 | 57.0328 | 0.047088 | -0.0729 | -0.038997 | -0.069409 | -0.041832 | -0.046753 | 0.080738 | 0.0078963 | 0.015972 | -0.022723 | 0.18391 | 0.056684 | -0.021844 | 0.015142 | -0.008409 | 0.047549 | -0.008799 | 0.15112 | -0.035584 | 57.0335 | 5.7421 | -65.8661 | 56.9586 | 57.0768 | 56.9244 | -66.7539 | 66.3813 | -56.9852 | 66.3951 | 66.4085 | 0.027175 | -57.0416 | -56.8817 | -0.33696 | -0.074201 | 123.4504 | 0.55078 | 0.88774 | 0.044054 | -0.10842 | 66.4645 | 66.4081 | 66.5681 | 66.4321 | -57.0684 | 123.3755 | 123.4938 | 123.3413 | 72.159 | -123.7867
1457.2656 | 123.6511 | -66.4352 | 57.0877 | 0.06235 | -0.071832 | -0.038997 | -0.06834 | -0.0429 | -0.046753 | 0.065477 | 0.0089643 | 0.015972 | -0.023791 | 0.18497 | 0.055616 | -0.031001 | 0.015142 | -0.008409 | 0.029236 | -0.022536 | 0.17402 | -0.035584 | 57.0426 | 6.1862 | -65.8707 | 56.9586 | 57.0906 | 56.961 | -66.7539 | 66.3997 | -57.0585 | 66.4042 | 66.4268 | 0.027175 | -57.1102 | -56.9137 | -0.31865 | -0.12913 | 123.4779 | 0.56452 | 0.88316 | 0.002857 | -0.12672 | 66.4645 | 66.4127 | 66.6093 | 66.4504 | -57.1233 | 123.3938 | 123.5258 | 123.3962 | 72.6214 | -123.8416
1458.2812 | 123.6923 | -66.4078 | 57.0282 | 0.047088 | -0.0729 | -0.040065 | -0.06834 | -0.041832 | -0.046753 | 0.065477 | 0.0078963 | 0.01704 | -0.023791 | 0.18604 | 0.054547 | -0.021844 | 0.010564 | -0.003831 | 0.056706 | -0.013378 | 0.13739 | -0.026426 | 57.0518 | 5.797 | -65.857 | 56.9769 | 57.0951 | 56.9427 | -66.7218 | 66.3813 | -56.9715 | 66.3859 | 66.4039 | 0.022595 | -57.0416 | -56.8908 | -0.31406 | -0.051309 | 123.4595 | 0.55079 | 0.86485 | 0.066946 | -0.085525 | 66.4645 | 66.3944 | 66.5452 | 66.4183 | -57.0546 | 123.3847 | 123.5029 | 123.3504 | 72.2048 | -123.75
1459.2656 | 123.6008 | -66.4352 | 57.0831 | 0.06235 | -0.075037 | -0.040065 | -0.069409 | -0.0429 | -0.045685 | 0.080738 | 0.0078963 | 0.014904 | -0.023791 | 0.18497 | 0.055616 | -0.021844 | 0.019721 | -0.003831 | 0.042971 | -0.013378 | 0.1786 | -0.035584 | 57.038 | 5.4719 | -65.8524 | 56.9906 | 57.1135 | 56.961 | -66.7173 | 66.3997 | -57.0402 | 66.4134 | 66.4314 | 0.031753 | -57.0965 | -56.9045 | -0.28202 | -0.092505 | 123.4733 | 0.58283 | 0.86485 | 0.030329 | -0.12214 | 66.4782 | 66.4219 | 66.6138 | 66.455 | -57.1187 | 123.4259 | 123.5487 | 123.3962 | 71.9072 | -123.8004
1460.2656 | 123.5825 | -66.4307 | 57.0602 | 0.077612 | -0.0729 | -0.040065 | -0.06834 | -0.0429 | -0.046753 | 0.050216 | 0.0078963 | 0.015972 | -0.022723 | 0.18497 | 0.056684 | -0.017266 | 0.010564 | 0.000747 | 0.033814 | -0.013378 | 0.17402 | -0.040163 | 57.0426 | 5.4536 | -65.8661 | 56.9632 | 57.086 | 56.9335 | -66.7402 | 66.3905 | -57.0264 | 66.4134 | 66.4314 | 0.04091 | -57.0736 | -56.8862 | -0.30949 | -0.097088 | 123.4733 | 0.56452 | 0.874 | 0.025745 | -0.12673 | 66.4645 | 66.4173 | 66.6047 | 66.4412 | -57.1004 | 123.3938 | 123.5167 | 123.3642 | 71.8843 | -123.8004
1461.2656 | 123.7289 | -66.3895 | 57.0511 | 0.06235 | -0.073968 | -0.038997 | -0.067272 | -0.041832 | -0.046753 | 0.080738 | 0.0078963 | 0.015972 | -0.021654 | 0.18497 | 0.056684 | -0.026423 | 0.019721 | -0.008409 | 0.020079 | -0.017957 | 0.16486 | -0.035584 | 57.0335 | 5.3803 | -65.8295 | 56.9723 | 57.0951 | 56.961 | -66.7264 | 66.3539 | -57.031 | 66.363 | 66.3811 | 0.027175 | -57.069 | -56.8862 | -0.33695 | -0.078775 | 123.4229 | 0.55995 | 0.8969 | 0.044058 | -0.090099 | 66.4095 | 66.3715 | 66.5543 | 66.4092 | -57.0867 | 123.3618 | 123.4846 | 123.3505 | 71.7698 | -123.7775
1462.2656 | 123.6328 | -66.4352 | 57.074 | 0.031826 | -0.075037 | -0.042202 | -0.069409 | -0.0429 | -0.045685 | 0.034955 | 0.0078963 | 0.013835 | -0.023791 | 0.18604 | 0.054547 | -0.026423 | 0.010564 | -0.008409 | 0.029236 | -0.022536 | 0.16486 | -0.035584 | 57.0426 | 5.8657 | -65.8249 | 56.9723 | 57.0951 | 56.9564 | -66.731 | 66.3997 | -57.0447 | 66.4088 | 66.4268 | 0.027175 | -57.0965 | -56.9091 | -0.29575 | -0.10166 | 123.4779 | 0.6103 | 0.90605 | 0.021169 | -0.11757 | 66.4645 | 66.4127 | 66.6001 | 66.4458 | -57.1096 | 123.4076 | 123.5304 | 123.3917 | 72.3009 | -123.805
1463.2812 | 123.7381 | -66.4032 | 57.0145 | 0.077612 | -0.075037 | -0.038997 | -0.067272 | -0.041832 | -0.047821 | 0.050216 | 0.0078963 | 0.014904 | -0.023791 | 0.18604 | 0.055616 | -0.031001 | 0.010564 | 0.000747 | 0.038393 | -0.017957 | 0.14655 | -0.031005 | 57.0564 | 5.9023 | -65.8158 | 56.986 | 57.1089 | 56.961 | -66.7173 | 66.3722 | -56.9761 | 66.3722 | 66.4039 | 0.031752 | -57.0324 | -56.8679 | -0.31406 | -0.028419 | 123.4595 | 0.58742 | 0.90148 | 0.094415 | -0.053478 | 66.4416 | 66.3852 | 66.5497 | 66.4138 | -57.0455 | 123.3892 | 123.5121 | 123.3642 | 72.3055 | -123.7317
1464.2656 | 123.6465 | -66.4215 | 57.1014 | 0.047088 | -0.073968 | -0.037928 | -0.069409 | -0.0429 | -0.046753 | 0.050216 | 0.0089643 | 0.014904 | -0.022723 | 0.18818 | 0.055616 | -0.026423 | 0.019721 | -0.003831 | 0.052128 | -0.013378 | 0.16028 | -0.040163 | 57.0472 | 6.0168 | -65.8433 | 56.9815 | 57.0997 | 56.9564 | -66.7218 | 66.3813 | -57.0493 | 66.3951 | 66.4177 | 0.036332 | -57.1148 | -56.9412 | -0.30033 | -0.11997 | 123.4687 | 0.57825 | 0.87858 | -0.001717 | -0.14503 | 66.4736 | 66.4081 | 66.5818 | 66.4412 | -57.1416 | 123.403 | 123.5212 | 123.3779 | 72.4383 | -123.8233
1465.2656 | 123.6328 | -66.4078 | 57.1106 | 0.047088 | -0.076105 | -0.038997 | -0.070477 | -0.043968 | -0.045685 | 0.080738 | 0.0068283 | 0.013835 | -0.021654 | 0.18497 | 0.054547 | -0.021844 | 0.015142 | -0.008409 | 0.047549 | -0.013378 | 0.15112 | -0.035584 | 57.0701 | 5.7192 | -65.8249 | 56.9906 | 57.1226 | 56.9656 | -66.7035 | 66.3722 | -57.063 | 66.3859 | 66.3994 | 0.027175 | -57.124 | -56.9595 | -0.29574 | -0.11997 | 123.4779 | 0.58284 | 0.87858 | 0.01202 | -0.14503 | 66.4553 | 66.3944 | 66.5589 | 66.4229 | -57.1462 | 123.3984 | 123.5304 | 123.3733 | 72.1269 | -123.8141
1466.2656 | 123.6374 | -66.3895 | 57.0877 | 0.047088 | -0.073968 | -0.037928 | -0.072614 | -0.041832 | -0.047821 | 0.065477 | 0.0057593 | 0.014904 | -0.023791 | 0.18711 | 0.056684 | -0.026423 | 0.015142 | -0.008409 | 0.033814 | -0.022536 | 0.1557 | -0.035584 | 57.0655 | 5.5498 | -65.8112 | 56.986 | 57.118 | 56.9885 | -66.7035 | 66.3539 | -57.0539 | 66.363 | 66.3811 | 0.027175 | -57.1102 | -56.932 | -0.31405 | -0.10166 | 123.455 | 0.57826 | 0.89232 | 0.030329 | -0.099249 | 66.4233 | 66.3669 | 66.5452 | 66.4046 | -57.1233 | 123.3755 | 123.5075 | 123.3779 | 71.9392 | -123.7912
1467.2656 | 123.6053 | -66.4169 | 57.1106 | 0.077612 | -0.076105 | -0.038997 | -0.069409 | -0.043968 | -0.046753 | 0.065477 | 0.0068283 | 0.01704 | -0.023791 | 0.18818 | 0.053479 | -0.017266 | 0.015142 | -0.003831 | 0.052128 | -0.017957 | 0.16944 | -0.035584 | 57.0655 | 6.003 | -65.8295 | 56.9952 | 57.1089 | 56.9564 | -66.7173 | 66.3813 | -57.0585 | 66.3997 | 66.4131 | 0.031753 | -57.1286 | -56.9412 | -0.30033 | -0.11539 | 123.4824 | 0.58741 | 0.88774 | -0.001716 | -0.15419 | 66.4691 | 66.399 | 66.5864 | 66.4321 | -57.1462 | 123.4121 | 123.5258 | 123.3733 | 72.42 | -123.8279
1468.2812 | 123.5962 | -66.4261 | 57.0831 | 0.047088 | -0.075037 | -0.038997 | -0.070477 | -0.0429 | -0.046753 | 0.080738 | 0.0068283 | 0.015972 | -0.022723 | 0.18711 | 0.054547 | -0.021844 | 0.019721 | -0.012988 | 0.052128 | -0.017957 | 0.16486 | -0.031005 | 57.0701 | 6.3556 | -65.8158 | 56.9952 | 57.118 | 56.9701 | -66.7081 | 66.3951 | -57.031 | 66.4042 | 66.4131 | 0.018017 | -57.1011 | -56.9183 | -0.28201 | -0.087927 | 123.4962 | 0.6103 | 0.89232 | 0.034907 | -0.11298 | 66.4782 | 66.4081 | 66.5909 | 66.4458 | -57.1141 | 123.4213 | 123.5441 | 123.3962 | 72.7817 | -123.7912
1469.2656 | 123.5962 | -66.394 | 57.1106 | 0.06235 | -0.073968 | -0.040065 | -0.06834 | -0.0429 | -0.046753 | 0.050216 | 0.0078963 | 0.013835 | -0.021654 | 0.18711 | 0.055616 | -0.026423 | 0.015142 | -0.022144 | 0.042971 | -0.027115 | 0.1786 | -0.031005 | 57.0747 | 6.1862 | -65.8295 | 56.9906 | 57.118 | 56.9701 | -66.7127 | 66.363 | -57.0676 | 66.3676 | 66.3719 | 0.008861 | -57.1377 | -56.932 | -0.31864 | -0.11997 | 123.4687 | 0.56453 | 0.88316 | 0.007441 | -0.14045 | 66.437 | 66.3669 | 66.5726 | 66.4092 | -57.1416 | 123.3847 | 123.5121 | 123.3642 | 72.5802 | -123.8233
1470.2656 | 123.6099 | -66.4169 | 57.0923 | 0.047088 | -0.076105 | -0.040065 | -0.06834 | -0.0429 | -0.04889 | 0.019694 | 0.0068283 | 0.015972 | -0.022723 | 0.18818 | 0.054547 | -0.021844 | 0.019721 | 0.000747 | 0.061284 | -0.013378 | 0.1557 | -0.040163 | 57.0609 | 6.0259 | -65.8204 | 56.9815 | 57.1135 | 56.9656 | -66.7173 | 66.3768 | -57.031 | 66.3951 | 66.4177 | 0.04091 | -57.1057 | -56.9366 | -0.30033 | -0.11082 | 123.4779 | 0.59657 | 0.8969 | 0.021174 | -0.12672 | 66.4782 | 66.4036 | 66.5726 | 66.4367 | -57.1324 | 123.3984 | 123.5304 | 123.3825 | 72.4429 | -123.8095
1471.2656 | 123.5962 | -66.3895 | 57.1472 | 0.047088 | -0.077173 | -0.038997 | -0.06834 | -0.041832 | -0.046753 | 0.050216 | 0.0089643 | 0.015972 | -0.022723 | 0.18925 | 0.053479 | -0.026423 | 0.015142 | -0.008409 | 0.052128 | -0.008799 | 0.16486 | -0.040163 | 57.0609 | 5.8611 | -65.8204 | 56.9952 | 57.1089 | 56.961 | -66.7173 | 66.3493 | -57.0951 | 66.363 | 66.3811 | 0.031754 | -57.156 | -56.9824 | -0.32779 | -0.15201 | 123.4504 | 0.5691 | 0.8969 | -0.038337 | -0.18623 | 66.4416 | 66.3807 | 66.5543 | 66.4046 | -57.1874 | 123.3847 | 123.4983 | 123.3505 | 72.2506 | -123.8645
1472.2656 | 123.6694 | -66.3712 | 57.0648 | 0.077612 | -0.075037 | -0.037928 | -0.070477 | -0.0429 | -0.047821 | 0.050216 | 0.0089643 | 0.015972 | -0.024859 | 0.18711 | 0.053479 | -0.026423 | 0.010564 | -0.003831 | 0.042971 | -0.013378 | 0.1786 | -0.040163 | 57.0655 | 6.3144 | -65.8204 | 56.9998 | 57.1226 | 56.9793 | -66.7081 | 66.331 | -57.0218 | 66.3447 | 66.3673 | 0.036332 | -57.0782 | -56.8862 | -0.33694 | -0.065037 | 123.4367 | 0.55079 | 0.88774 | 0.057797 | -0.085517 | 66.4141 | 66.3578 | 66.5498 | 66.3817 | -57.105 | 123.3709 | 123.4938 | 123.3505 | 72.6856 | -123.7729
1473.2812 | 123.6465 | -66.394 | 57.0969 | 0.06235 | -0.075037 | -0.041133 | -0.069409 | -0.040764 | -0.046753 | 0.095999 | 0.0078963 | 0.015972 | -0.024859 | 0.18818 | 0.053479 | -0.031001 | 0.010564 | -0.008409 | 0.047549 | -0.017957 | 0.16944 | -0.031005 | 57.0701 | 6.1084 | -65.8158 | 56.9906 | 57.1226 | 56.9839 | -66.7127 | 66.363 | -57.0493 | 66.363 | 66.3856 | 0.022596 | -57.1148 | -56.9274 | -0.31864 | -0.10624 | 123.4641 | 0.57826 | 0.8969 | 0.025753 | -0.11298 | 66.4416 | 66.3761 | 66.5635 | 66.4046 | -57.1279 | 123.3847 | 123.5167 | 123.3779 | 72.5024 | -123.8095
1474.2656 | 123.6282 | -66.4124 | 57.0923 | 0.047088 | -0.076105 | -0.041133 | -0.069409 | -0.041832 | -0.045685 | 0.080738 | 0.0068283 | 0.014904 | -0.022723 | 0.18604 | 0.055616 | -0.031001 | 0.015142 | -0.012988 | 0.061284 | -0.013378 | 0.13739 | -0.040163 | 57.0609 | 6.09 | -65.8249 | 56.9906 | 57.118 | 56.9701 | -66.7127 | 66.3722 | -57.031 | 66.3814 | 66.3994 | 0.027175 | -57.1057 | -56.9549 | -0.30032 | -0.10166 | 123.4733 | 0.58741 | 0.88774 | 0.025752 | -0.12214 | 66.4736 | 66.399 | 66.5497 | 66.4275 | -57.1324 | 123.403 | 123.5304 | 123.3825 | 72.5024 | -123.805
1475.2656 | 123.6145 | -66.4307 | 57.0877 | 0.047088 | -0.076105 | -0.041133 | -0.06834 | -0.0429 | -0.04889 | 0.080738 | 0.0057593 | 0.015972 | -0.021654 | 0.18604 | 0.055616 | -0.021844 | 0.0243 | -0.003831 | 0.056706 | -0.017957 | 0.13739 | -0.035584 | 57.0426 | 5.9435 | -65.8341 | 56.9677 | 57.0997 | 56.9473 | -66.7402 | 66.3951 | -57.031 | 66.4088 | 66.4268 | 0.031753 | -57.1057 | -56.9503 | -0.30949 | -0.11998 | 123.4733 | 0.59657 | 0.90605 | 0.012015 | -0.14046 | 66.4874 | 66.4127 | 66.5681 | 66.455 | -57.1233 | 123.3984 | 123.5304 | 123.3779 | 72.3742 | -123.8279
1476.2656 | 123.6465 | -66.4078 | 57.0694 | 0.077612 | -0.075037 | -0.040065 | -0.069409 | -0.043968 | -0.045685 | 0.080738 | 0.0057593 | 0.013835 | -0.023791 | 0.18818 | 0.054547 | -0.031001 | 0.019721 | -0.008409 | 0.042971 | -0.013378 | 0.16486 | -0.031005 | 57.0426 | 6.09 | -65.8295 | 56.9677 | 57.1043 | 56.9473 | -66.731 | 66.3768 | -57.0264 | 66.3768 | 66.3994 | 0.022596 | -57.0828 | -56.9045 | -0.32322 | -0.10167 | 123.4504 | 0.57826 | 0.90148 | 0.034904 | -0.12215 | 66.4507 | 66.3944 | 66.5726 | 66.4275 | -57.1004 | 123.3755 | 123.5121 | 123.355 | 72.4978 | -123.8004
1477.2656 | 123.6923 | -66.362 | 57.074 | 0.06235 | -0.076105 | -0.040065 | -0.069409 | -0.041832 | -0.047821 | 0.080738 | 0.0078963 | 0.015972 | -0.022723 | 0.18711 | 0.053479 | -0.026423 | 0.015142 | -0.003831 | 0.052128 | -0.008799 | 0.1557 | -0.040163 | 57.0747 | 6.0763 | -65.7929 | 57.0044 | 57.1409 | 56.9885 | -66.6989 | 66.3218 | -57.0218 | 66.3356 | 66.3582 | 0.036332 | -57.0828 | -56.9183 | -0.33694 | -0.069615 | 123.4367 | 0.56911 | 0.90605 | 0.066955 | -0.085516 | 66.4141 | 66.3532 | 66.5177 | 66.3771 | -57.1141 | 123.3664 | 123.5029 | 123.3505 | 72.4383 | -123.7729
1478.2812 | 123.6328 | -66.362 | 57.1564 | 0.06235 | -0.076105 | -0.040065 | -0.06834 | -0.0429 | -0.047821 | 0.095999 | 0.0078963 | 0.015972 | -0.023791 | 0.18711 | 0.054547 | -0.017266 | 0.0243 | -0.008409 | 0.038393 | -0.013378 | 0.16486 | -0.035584 | 57.1113 | 5.8336 | -65.7746 | 57.0273 | 57.1592 | 57.0205 | -66.6669 | 66.3264 | -57.118 | 66.3447 | 66.3536 | 0.027175 | -57.1698 | -56.9915 | -0.30489 | -0.12912 | 123.4733 | 0.58743 | 0.89232 | 0.002873 | -0.13586 | 66.4004 | 66.3486 | 66.5269 | 66.3863 | -57.192 | 123.3893 | 123.5212 | 123.3825 | 72.1956 | -123.8233
1479.2656 | 123.6374 | -66.3483 | 57.1426 | 0.06235 | -0.076105 | -0.040065 | -0.069409 | -0.043968 | -0.047821 | 0.050216 | 0.0068283 | 0.014904 | -0.023791 | 0.18818 | 0.053479 | -0.021844 | 0.015142 | -0.008409 | 0.038393 | -0.013378 | 0.17402 | -0.044742 | 57.1205 | 5.852 | -65.7746 | 57.0456 | 57.1776 | 57.0342 | -66.6623 | 66.3035 | -57.1042 | 66.3264 | 66.3399 | 0.036333 | -57.156 | -56.9686 | -0.31404 | -0.097072 | 123.4687 | 0.57369 | 0.88774 | 0.03492 | -0.10839 | 66.3867 | 66.3349 | 66.5223 | 66.3634 | -57.1874 | 123.3938 | 123.5258 | 123.3825 | 72.2002 | -123.805
1480.2656 | 123.6877 | -66.3528 | 57.1106 | 0.077612 | -0.077173 | -0.040065 | -0.070477 | -0.0429 | -0.046753 | 0.080738 | 0.0089643 | 0.014904 | -0.023791 | 0.18818 | 0.054547 | -0.021844 | 0.015142 | -0.003831 | 0.061284 | -0.013378 | 0.1557 | -0.031005 | 57.0976 | 5.9069 | -65.7929 | 57.0181 | 57.1592 | 56.9885 | -66.6852 | 66.3218 | -57.0493 | 66.331 | 66.349 | 0.027174 | -57.124 | -56.9549 | -0.33236 | -0.0925 | 123.4504 | 0.55996 | 0.89232 | 0.048649 | -0.12214 | 66.4141 | 66.3395 | 66.5085 | 66.368 | -57.1416 | 123.3709 | 123.5121 | 123.3413 | 72.2597 | -123.7958
1481.2656 | 123.7061 | -66.3483 | 57.1106 | 0.031826 | -0.075037 | -0.042202 | -0.069409 | -0.041832 | -0.045685 | 0.080738 | 0.0078963 | 0.015972 | -0.023791 | 0.18925 | 0.053479 | -0.031001 | 0.019721 | -0.003831 | 0.061284 | -0.013378 | 0.14655 | -0.040163 | 57.1021 | 5.8748 | -65.7746 | 57.0318 | 57.1547 | 57.0114 | -66.6715 | 66.3081 | -57.0493 | 66.3173 | 66.3444 | 0.036332 | -57.124 | -56.9641 | -0.3232 | -0.078765 | 123.4504 | 0.57369 | 0.8969 | 0.04407 | -0.099244 | 66.4096 | 66.3349 | 66.4948 | 66.368 | -57.1508 | 123.3801 | 123.5029 | 123.3596 | 72.2231 | -123.7821
1482.2656 | 123.6969 | -66.2842 | 57.1243 | 0.077612 | -0.078242 | -0.040065 | -0.071546 | -0.0429 | -0.045685 | 0.065477 | 0.0078963 | 0.014904 | -0.025927 | 0.18818 | 0.056684 | -0.017266 | 0.0243 | 0.000747 | 0.061284 | -0.013378 | 0.16486 | -0.026426 | 57.125 | 5.9527 | -65.7654 | 57.0593 | 57.1776 | 57.0342 | -66.6532 | 66.2578 | -57.063 | 66.2669 | 66.2849 | 0.027173 | -57.1377 | -56.9595 | -0.36897 | -0.065027 | 123.4092 | 0.51876 | 0.88774 | 0.05323 | -0.090084 | 66.3455 | 66.2708 | 66.449 | 66.3085 | -57.1508 | 123.3435 | 123.4617 | 123.3184 | 72.2369 | -123.7775
1483.2656 | 123.6099 | -66.3025 | 57.1609 | 0.047088 | -0.076105 | -0.041133 | -0.069409 | -0.043968 | -0.046753 | 0.065477 | 0.0078963 | 0.015972 | -0.023791 | 0.18818 | 0.054547 | -0.031001 | 0.019721 | -0.008409 | 0.056706 | -0.013378 | 0.1786 | -0.035584 | 57.1205 | 6.2961 | -65.7654 | 57.0456 | 57.1776 | 57.0251 | -66.6532 | 66.2669 | -57.1042 | 66.2715 | 66.2941 | 0.027175 | -57.1743 | -56.9824 | -0.35066 | -0.11538 | 123.4229 | 0.53707 | 0.88774 | 0.016609 | -0.13586 | 66.3592 | 66.2891 | 66.4811 | 66.3222 | -57.1965 | 123.3481 | 123.48 | 123.3276 | 72.5986 | -123.8141
1484.2656 | 123.7198 | -66.2979 | 57.1289 | 0.047088 | -0.076105 | -0.040065 | -0.069409 | -0.043968 | -0.046753 | 0.11126 | 0.010032 | 0.014904 | -0.023791 | 0.18711 | 0.054547 | -0.026423 | 0.028878 | -0.012988 | 0.033814 | -0.013378 | 0.17402 | -0.031005 | 57.1205 | 6.1816 | -65.7471 | 57.0593 | 57.1821 | 57.0297 | -66.6486 | 66.2669 | -57.0951 | 66.2715 | 66.2849 | 0.018017 | -57.1423 | -56.9549 | -0.35066 | -0.069604 | 123.4184 | 0.55081 | 0.90147 | 0.053232 | -0.09924 | 66.3317 | 66.2845 | 66.4719 | 66.3268 | -57.1599 | 123.3572 | 123.4801 | 123.3276 | 72.4795 | -123.7775
1485.2656 | 123.7335 | -66.2933 | 57.0969 | 0.047088 | -0.077173 | -0.040065 | -0.070477 | -0.041832 | -0.047821 | 0.080738 | 0.0078963 | 0.014904 | -0.023791 | 0.18925 | 0.053479 | -0.021844 | 0.015142 | -0.003831 | 0.029236 | -0.017957 | 0.1786 | -0.035584 | 57.1205 | 6.3007 | -65.683 | 57.0456 | 57.1776 | 57.0251 | -66.6532 | 66.2578 | -57.0676 | 66.2715 | 66.2895 | 0.031753 | -57.1148 | -56.9183 | -0.35982 | -0.051296 | 123.4138 | 0.61034 | 0.97015 | 0.080696 | -0.071775 | 66.3226 | 66.2754 | 66.4719 | 66.3085 | -57.1324 | 123.3389 | 123.4709 | 123.3184 | 72.594 | -123.75
1486.2656 | 123.7427 | -66.2842 | 57.1335 | 0.092874 | -0.076105 | -0.041133 | -0.069409 | -0.0429 | -0.04889 | 0.080738 | 0.0078963 | 0.013835 | -0.024859 | 0.18925 | 0.056684 | -0.03558 | 0.0243 | -0.012988 | 0.056706 | -0.013378 | 0.15112 | -0.031005 | 57.1342 | 6.5983 | -65.7379 | 57.0639 | 57.1821 | 57.0388 | -66.6348 | 66.2532 | -57.0768 | 66.2486 | 66.2712 | 0.018017 | -57.1469 | -56.9824 | -0.35066 | -0.069603 | 123.4184 | 0.54624 | 0.89689 | 0.048654 | -0.09466 | 66.3409 | 66.2708 | 66.4353 | 66.3085 | -57.1645 | 123.3481 | 123.4663 | 123.323 | 72.8825 | -123.7683
1487.2656 | 123.7427 | -66.2704 | 57.1838 | 0.077612 | -0.076105 | -0.042202 | -0.069409 | -0.043968 | -0.047821 | 0.095999 | 0.0078963 | 0.014904 | -0.024859 | 0.18925 | 0.053479 | -0.021844 | 0.019721 | -0.003831 | 0.038393 | -0.013378 | 0.1557 | -0.035584 | 57.1342 | 6.3785 | -65.7379 | 57.073 | 57.1913 | 57.0526 | -66.644 | 66.2349 | -57.1454 | 66.2486 | 66.2666 | 0.031753 | -57.1972 | -57.0281 | -0.37355 | -0.1108 | 123.4046 | 0.5325 | 0.90605 | 0.007457 | -0.13128 | 66.3088 | 66.2571 | 66.4261 | 66.2902 | -57.2194 | 123.3435 | 123.4617 | 123.323 | 72.6489 | -123.8278
1488.2812 | 123.6237 | -66.2888 | 57.2159 | 0.077612 | -0.077173 | -0.040065 | -0.070477 | -0.0429 | -0.047821 | 0.050216 | 0.0046913 | 0.014904 | -0.022723 | 0.19032 | 0.055616 | -0.026423 | 0.019721 | -0.008409 | 0.065863 | -0.013378 | 0.16028 | -0.021847 | 57.1708 | 6.5388 | -64.3323 | 57.0914 | 57.2188 | 57.0663 | -66.4608 | 66.2669 | -57.15 | 66.2623 | 66.2803 | 0.013438 | -57.2293 | -57.0556 | -0.17209 | -0.12453 | 123.4596 | 1.9565 | 2.1286 | 0.002885 | -0.14959 | 66.3546 | 66.2754 | 66.449 | 66.3085 | -57.2377 | 123.3801 | 123.5075 | 123.3551 | 72.8275 | -123.6767
1489.2656 | 123.7198 | -66.2247 | 57.1793 | 0.077612 | -0.078242 | -0.041133 | -0.069409 | -0.043968 | -0.047821 | 0.080738 | 0.0057593 | 0.015972 | -0.023791 | 0.18818 | 0.054547 | -0.031001 | 0.019721 | -0.008409 | 0.052128 | -0.017957 | 0.16944 | -0.031005 | 57.1617 | 6.6624 | -65.6967 | 57.0868 | 57.2233 | 57.0571 | -66.6074 | 66.1937 | -57.1271 | 66.1937 | 66.2163 | 0.022596 | -57.1972 | -57.0098 | -0.38269 | -0.092487 | 123.3863 | 0.52793 | 0.91063 | 0.044085 | -0.12212 | 66.2768 | 66.2067 | 66.3941 | 66.2444 | -57.2103 | 123.3114 | 123.448 | 123.2818 | 72.8871 | -123.7866
1490.2656 | 123.7381 | -66.2155 | 57.1655 | 0.047088 | -0.078242 | -0.040065 | -0.070477 | -0.043968 | -0.04889 | 0.080738 | 0.0068283 | 0.014904 | -0.022723 | 0.18925 | 0.054547 | -0.021844 | 0.010564 | -0.003831 | 0.047549 | -0.008799 | 0.1557 | -0.035584 | 57.1571 | 6.3465 | -65.7151 | 57.0914 | 57.2233 | 57.0709 | -66.6074 | 66.1799 | -57.118 | 66.1937 | 66.2117 | 0.031753 | -57.1743 | -57.0098 | -0.39185 | -0.074175 | 123.3726 | 0.50046 | 0.89231 | 0.057818 | -0.094653 | 66.2631 | 66.2067 | 66.3712 | 66.2261 | -57.2011 | 123.3069 | 123.4389 | 123.2864 | 72.562 | -123.7729
1491.2656 | 123.7106 | -66.2796 | 57.1472 | 0.047088 | -0.077173 | -0.042202 | -0.070477 | -0.041832 | -0.047821 | 0.050216 | 0.0078963 | 0.014904 | -0.024859 | 0.18925 | 0.053479 | -0.026423 | 0.015142 | -0.003831 | 0.033814 | -0.017957 | 0.16486 | -0.026426 | 57.1388 | 6.5296 | -65.7379 | 57.0639 | 57.2005 | 57.0388 | -66.6394 | 66.2532 | -57.1134 | 66.2532 | 66.2758 | 0.022595 | -57.1652 | -56.9824 | -0.35981 | -0.083336 | 123.4184 | 0.54166 | 0.90147 | 0.053235 | -0.10839 | 66.3134 | 66.2616 | 66.4445 | 66.2947 | -57.1736 | 123.3435 | 123.4801 | 123.3184 | 72.8092 | -123.7866
1492.2812 | 123.6191 | -66.33 | 57.1793 | 0.06235 | -0.077173 | -0.040065 | -0.070477 | -0.0429 | -0.046753 | 0.050216 | 0.0046913 | 0.015972 | -0.023791 | 0.18818 | 0.055616 | -0.026423 | 0.019721 | -0.003831 | 0.038393 | -0.013378 | 0.17402 | -0.035584 | 57.1159 | 6.4197 | -65.7563 | 57.041 | 57.1684 | 57.0297 | -66.6623 | 66.2944 | -57.1409 | 66.3035 | 66.3261 | 0.031753 | -57.1926 | -57.0052 | -0.33236 | -0.13827 | 123.4458 | 0.5737 | 0.90605 | -0.010858 | -0.14959 | 66.3683 | 66.3166 | 66.504 | 66.3497 | -57.2148 | 123.3709 | 123.4984 | 123.3596 | 72.7497 | -123.8416
1493.2812 | 123.7152 | -66.2979 | 57.1198 | 0.077612 | -0.078242 | -0.041133 | -0.06834 | -0.043968 | -0.046753 | 0.034955 | 0.0068283 | 0.015972 | -0.024859 | 0.18925 | 0.054547 | -0.017266 | 0.015142 | 0.000747 | 0.065863 | -0.008799 | 0.1786 | -0.031005 | 57.125 | 6.6074 | -65.7563 | 57.0456 | 57.1776 | 57.0205 | -66.6532 | 66.2669 | -57.0539 | 66.2806 | 66.2987 | 0.031752 | -57.1286 | -56.9412 | -0.35524 | -0.074184 | 123.4229 | 0.54165 | 0.89689 | 0.057808 | -0.099242 | 66.3638 | 66.2891 | 66.4765 | 66.3131 | -57.1508 | 123.3435 | 123.4755 | 123.3184 | 72.9053 | -123.7729
1494.2656 | 123.7518 | -66.2704 | 57.1747 | 0.047088 | -0.078242 | -0.041133 | -0.071546 | -0.041832 | -0.046753 | 0.065477 | 0.0078963 | 0.014904 | -0.023791 | 0.18925 | 0.053479 | -0.021844 | 0.019721 | 0.000747 | 0.052128 | -0.013378 | 0.16028 | -0.026426 | 57.1708 | 6.5159 | -65.7059 | 57.0868 | 57.2233 | 57.0755 | -66.6028 | 66.244 | -57.1226 | 66.2486 | 66.2712 | 0.027173 | -57.1881 | -57.0144 | -0.33234 | -0.08791 | 123.4413 | 0.56455 | 0.89689 | 0.048662 | -0.099231 | 66.3226 | 66.2571 | 66.4307 | 66.2902 | -57.2011 | 123.3572 | 123.4938 | 123.3459 | 72.7863 | -123.7775
1495.2656 | 123.7381 | -66.2796 | 57.1426 | 0.077612 | -0.080379 | -0.040065 | -0.071546 | -0.041832 | -0.04889 | 0.050216 | 0.0078963 | 0.015972 | -0.023791 | 0.19032 | 0.055616 | -0.026423 | 0.019721 | -0.003831 | 0.065863 | -0.013378 | 0.16486 | -0.026426 | 57.1571 | 6.3007 | -65.7288 | 57.0776 | 57.205 | 57.0342 | -66.6165 | 66.2532 | -57.0768 | 66.2532 | 66.2758 | 0.022595 | -57.156 | -56.9778 | -0.33692 | -0.065023 | 123.4367 | 0.55082 | 0.88774 | 0.062392 | -0.10839 | 66.3455 | 66.2662 | 66.4445 | 66.2993 | -57.1691 | 123.3572 | 123.4846 | 123.3138 | 72.5803 | -123.7592
1496.2656 | 123.7473 | -66.2247 | 57.1701 | 0.047088 | -0.078242 | -0.041133 | -0.072614 | -0.041832 | -0.047821 | 0.065477 | 0.0078963 | 0.015972 | -0.022723 | 0.18925 | 0.053479 | -0.026423 | 0.019721 | 0.000747 | 0.061284 | -0.013378 | 0.16486 | -0.021847 | 57.1754 | 6.264 | -65.6967 | 57.1097 | 57.2371 | 57.08 | -66.5982 | 66.2028 | -57.1088 | 66.1982 | 66.2254 | 0.022594 | -57.1835 | -57.0052 | -0.37354 | -0.060439 | 123.4001 | 0.52793 | 0.90147 | 0.066976 | -0.090074 | 66.286 | 66.2113 | 66.3895 | 66.2444 | -57.192 | 123.3343 | 123.4618 | 123.3047 | 72.4887 | -123.7683
1497.2656 | 123.7289 | -66.2842 | 57.1609 | 0.06235 | -0.07931 | -0.040065 | -0.070477 | -0.0429 | -0.04889 | 0.050216 | 0.0078963 | 0.015972 | -0.024859 | 0.19138 | 0.054547 | -0.017266 | 0.015142 | 0.000747 | 0.052128 | -0.013378 | 0.16944 | -0.026426 | 57.1754 | 6.6761 | -65.7196 | 57.1005 | 57.2279 | 57.08 | -66.6119 | 66.2578 | -57.1088 | 66.2669 | 66.2849 | 0.027173 | -57.1743 | -56.9915 | -0.32776 | -0.060441 | 123.4596 | 0.56455 | 0.89231 | 0.066974 | -0.080919 | 66.3363 | 66.2708 | 66.4536 | 66.2993 | -57.1874 | 123.3847 | 123.5121 | 123.3642 | 72.9603 | -123.7729
1498.2812 | 123.642 | -66.3116 | 57.2067 | 0.06235 | -0.07931 | -0.038997 | -0.071546 | -0.0429 | -0.049958 | 0.080738 | 0.0078963 | 0.014904 | -0.024859 | 0.19138 | 0.052411 | -0.026423 | 0.0243 | -0.003831 | 0.038393 | -0.013378 | 0.16028 | -0.035584 | 57.1388 | 6.7402 | -65.7334 | 57.0685 | 57.1959 | 57.0526 | -66.6348 | 66.2761 | -57.1683 | 66.2852 | 66.3078 | 0.031753 | -57.2201 | -57.0464 | -0.32319 | -0.13827 | 123.4504 | 0.57828 | 0.90147 | -0.010853 | -0.15417 | 66.35 | 66.2983 | 66.4719 | 66.3359 | -57.2423 | 123.3801 | 123.5075 | 123.3642 | 73.0519 | -123.8416
1499.2656 | 123.6832 | -66.2888 | 57.1564 | 0.031826 | -0.078242 | -0.040065 | -0.071546 | -0.043968 | -0.046753 | 0.080738 | 0.0078963 | 0.014904 | -0.024859 | 0.19032 | 0.053479 | -0.021844 | 0.019721 | -0.003831 | 0.047549 | -0.00422 | 0.16486 | -0.031005 | 57.1525 | 6.9783 | -65.7379 | 57.0776 | 57.1913 | 57.0434 | -66.6211 | 66.2578 | -57.1088 | 66.2669 | 66.2849 | 0.027174 | -57.1606 | -56.9915 | -0.33234 | -0.078756 | 123.4413 | 0.55081 | 0.88316 | 0.034923 | -0.11297 | 66.3363 | 66.2845 | 66.4536 | 66.3085 | -57.1874 | 123.3664 | 123.4801 | 123.3322 | 73.2671 | -123.7775
1500.2656 | 123.7106 | -66.2979 | 57.1472 | 0.06235 | -0.078242 | -0.040065 | -0.070477 | -0.043968 | -0.046753 | 0.080738 | 0.0089643 | 0.014904 | -0.024859 | 0.19138 | 0.054547 | -0.017266 | 0.0243 | -0.003831 | 0.042971 | -0.008799 | 0.17402 | -0.017268 | 57.1433 | 6.9096 | -65.7242 | 57.0685 | 57.2005 | 57.0526 | -66.644 | 66.2806 | -57.1042 | 66.2806 | 66.2941 | 0.013437 | -57.156 | -56.9732 | -0.34608 | -0.078758 | 123.4413 | 0.5737 | 0.91979 | 0.053235 | -0.094658 | 66.3409 | 66.2891 | 66.4719 | 66.3222 | -57.1645 | 123.3664 | 123.4984 | 123.3505 | 73.2075 | -123.7912
1501.2656 | 123.7061 | -66.2704 | 57.2342 | 0.047088 | -0.07931 | -0.037928 | -0.071546 | -0.0429 | -0.045685 | 0.050216 | 0.0057593 | 0.014904 | -0.022723 | 0.19138 | 0.055616 | -0.012688 | 0.015142 | 0.000747 | 0.042971 | -0.017957 | 0.16028 | -0.031005 | 57.1342 | 7.1477 | -65.6922 | 57.0685 | 57.2005 | 57.048 | -66.6303 | 66.2394 | -57.1912 | 66.2578 | 66.2712 | 0.031752 | -57.2521 | -57.0739 | -0.35981 | -0.16573 | 123.4046 | 0.57829 | 0.9381 | -0.03374 | -0.18621 | 66.3134 | 66.2525 | 66.4307 | 66.2856 | -57.2652 | 123.3389 | 123.4709 | 123.3184 | 73.4182 | -123.8645
1502.2656 | 123.7518 | -66.3208 | 57.106 | 0.077612 | -0.07931 | -0.041133 | -0.070477 | -0.0429 | -0.047821 | 0.080738 | 0.0068283 | 0.014904 | -0.023791 | 0.19138 | 0.054547 | -0.026423 | 0.019721 | -0.008409 | 0.061284 | -0.008799 | 0.16944 | -0.031005 | 57.125 | 7.2759 | -65.7563 | 57.0501 | 57.173 | 57.0297 | -66.6577 | 66.2898 | -57.0447 | 66.2944 | 66.3124 | 0.022596 | -57.1148 | -56.9366 | -0.33693 | -0.055873 | 123.4458 | 0.56454 | 0.90147 | 0.066962 | -0.076352 | 66.3821 | 66.312 | 66.4902 | 66.3405 | -57.137 | 123.3709 | 123.4938 | 123.3505 | 73.5967 | -123.7637
1503.2656 | 123.7198 | -66.3208 | 57.1198 | 0.077612 | -0.080379 | -0.038997 | -0.071546 | -0.041832 | -0.047821 | 0.065477 | 0.0078963 | 0.014904 | -0.023791 | 0.19138 | 0.053479 | -0.026423 | 0.0243 | -0.003831 | 0.038393 | -0.00422 | 0.1557 | -0.026426 | 57.1205 | 7.0195 | -65.7517 | 57.0456 | 57.1684 | 57.0388 | -66.6577 | 66.2944 | -57.0814 | 66.2944 | 66.317 | 0.022595 | -57.124 | -56.964 | -0.33693 | -0.074184 | 123.4413 | 0.56912 | 0.90605 | 0.048651 | -0.080927 | 66.3592 | 66.3166 | 66.4765 | 66.3451 | -57.1462 | 123.3664 | 123.4892 | 123.3596 | 73.3403 | -123.7775
1504.2656 | 123.7106 | -66.2933 | 57.1243 | 0.06235 | -0.078242 | -0.041133 | -0.070477 | -0.0429 | -0.046753 | 0.050216 | 0.0078963 | 0.015972 | -0.025927 | 0.19138 | 0.053479 | -0.021844 | 0.0243 | -0.003831 | 0.065863 | -0.013378 | 0.1786 | -0.026426 | 57.1159 | 6.7906 | -65.7563 | 57.0547 | 57.173 | 57.0251 | -66.6532 | 66.2669 | -57.0585 | 66.2715 | 66.2895 | 0.022595 | -57.1377 | -56.9457 | -0.35982 | -0.069605 | 123.4092 | 0.53708 | 0.89689 | 0.048651 | -0.099241 | 66.3592 | 66.28 | 66.4719 | 66.3176 | -57.1508 | 123.3481 | 123.4663 | 123.3184 | 73.0839 | -123.7775
1505.2656 | 123.6832 | -66.33 | 57.1518 | 0.06235 | -0.078242 | -0.041133 | -0.073683 | -0.041832 | -0.046753 | 0.050216 | 0.0068283 | 0.013835 | -0.024859 | 0.19032 | 0.052411 | -0.021844 | 0.0243 | 0.000747 | 0.038393 | -0.013378 | 0.17402 | -0.035584 | 57.1113 | 6.8684 | -65.7334 | 57.0364 | 57.1776 | 57.0159 | -66.6715 | 66.2944 | -57.1134 | 66.3081 | 66.3307 | 0.036331 | -57.1652 | -56.9778 | -0.34151 | -0.11538 | 123.4413 | 0.59659 | 0.9381 | 0.025765 | -0.13586 | 66.3683 | 66.3166 | 66.504 | 66.3543 | -57.1874 | 123.3664 | 123.5075 | 123.3459 | 73.1984 | -123.8233
1506.2656 | 123.6694 | -66.3345 | 57.1335 | 0.047088 | -0.078242 | -0.040065 | -0.071546 | -0.043968 | -0.04889 | 0.065477 | 0.0078963 | 0.015972 | -0.024859 | 0.19138 | 0.053479 | -0.017266 | 0.019721 | -0.012988 | 0.024657 | -0.017957 | 0.16944 | -0.035584 | 57.1342 | 6.4518 | -65.7288 | 57.0547 | 57.1867 | 57.0251 | -66.6532 | 66.299 | -57.1088 | 66.3173 | 66.3215 | 0.022596 | -57.1514 | -56.964 | -0.31862 | -0.07876 | 123.4687 | 0.60575 | 0.92437 | 0.053232 | -0.1084 | 66.3592 | 66.3166 | 66.504 | 66.3543 | -57.1691 | 123.3893 | 123.5213 | 123.3596 | 72.7863 | -123.7866
1507.2656 | 123.7518 | -66.2888 | 57.1198 | 0.06235 | -0.07931 | -0.040065 | -0.072614 | -0.041832 | -0.047821 | 0.095999 | 0.0089643 | 0.015972 | -0.025927 | 0.19245 | 0.053479 | -0.026423 | 0.019721 | -0.008409 | 0.033814 | -0.017957 | 0.18317 | -0.031005 | 57.125 | 6.5296 | -65.7334 | 57.0547 | 57.1821 | 57.0388 | -66.644 | 66.2578 | -57.0859 | 66.2623 | 66.2803 | 0.022596 | -57.1377 | -56.9366 | -0.35524 | -0.065027 | 123.4138 | 0.55539 | 0.91063 | 0.062387 | -0.080927 | 66.3226 | 66.2708 | 66.4719 | 66.3085 | -57.1508 | 123.3435 | 123.4709 | 123.3276 | 72.8184 | -123.7637
1508.2812 | 123.7564 | -66.2888 | 57.1243 | 0.047088 | -0.080379 | -0.042202 | -0.070477 | -0.0429 | -0.04889 | 0.050216 | 0.0068283 | 0.013835 | -0.023791 | 0.19245 | 0.052411 | -0.017266 | 0.019721 | 0.000747 | 0.056706 | -0.013378 | 0.15112 | -0.031005 | 57.1067 | 6.9692 | -65.7517 | 57.0364 | 57.1638 | 57.0205 | -66.6623 | 66.2578 | -57.0676 | 66.2715 | 66.2895 | 0.031752 | -57.1377 | -56.9732 | -0.37355 | -0.087919 | 123.3955 | 0.53708 | 0.91063 | 0.039494 | -0.10382 | 66.3455 | 66.2754 | 66.4399 | 66.3085 | -57.1553 | 123.3252 | 123.4526 | 123.3093 | 73.2579 | -123.7866
1509.2656 | 123.7015 | -66.362 | 57.106 | 0.06235 | -0.080379 | -0.041133 | -0.069409 | -0.045037 | -0.047821 | 0.050216 | 0.0057593 | 0.013835 | -0.023791 | 0.19138 | 0.050274 | -0.017266 | 0.015142 | -0.003831 | 0.042971 | -0.017957 | 0.1557 | -0.031005 | 57.1021 | 7.0607 | -65.7654 | 57.0181 | 57.1501 | 57.0068 | -66.676 | 66.331 | -57.063 | 66.3447 | 66.3582 | 0.027174 | -57.124 | -56.9503 | -0.31405 | -0.087922 | 123.4641 | 0.59658 | 0.91063 | 0.044069 | -0.099245 | 66.405 | 66.344 | 66.5177 | 66.3771 | -57.137 | 123.3801 | 123.5121 | 123.3688 | 73.4227 | -123.7821
1510.2656 | 123.7473 | -66.3254 | 57.1335 | 0.06235 | -0.080379 | -0.041133 | -0.071546 | -0.0429 | -0.047821 | 0.080738 | 0.0078963 | 0.014904 | -0.024859 | 0.19245 | 0.052411 | -0.021844 | 0.010564 | -0.008409 | 0.029236 | -0.017957 | 0.16486 | -0.026426 | 57.1296 | 7.2393 | -65.7471 | 57.0593 | 57.1821 | 57.0526 | -66.6532 | 66.299 | -57.1042 | 66.3035 | 66.317 | 0.018017 | -57.1514 | -56.9686 | -0.32778 | -0.074182 | 123.455 | 0.57828 | 0.90605 | 0.048654 | -0.080925 | 66.3546 | 66.3074 | 66.4902 | 66.3359 | -57.1599 | 123.3847 | 123.5075 | 123.3779 | 73.5647 | -123.7866
1511.2656 | 123.6969 | -66.3025 | 57.1335 | 0.06235 | -0.07931 | -0.042202 | -0.069409 | -0.045037 | -0.049958 | 0.080738 | 0.0068283 | 0.014904 | -0.023791 | 0.19245 | 0.053479 | -0.021844 | 0.019721 | -0.008409 | 0.052128 | -0.013378 | 0.16028 | -0.031005 | 57.1113 | 7.0974 | -65.7746 | 57.041 | 57.173 | 57.0205 | -66.6669 | 66.2715 | -57.0814 | 66.2806 | 66.2941 | 0.022596 | -57.1469 | -56.9732 | -0.3644 | -0.092496 | 123.4138 | 0.52792 | 0.89232 | 0.039496 | -0.11298 | 66.3546 | 66.2891 | 66.4628 | 66.3222 | -57.1645 | 123.3435 | 123.4755 | 123.323 | 73.3998 | -123.8004
1512.2656 | 123.7244 | -66.3254 | 57.1381 | 0.06235 | -0.081447 | -0.040065 | -0.071546 | -0.041832 | -0.047821 | 0.065477 | 0.0057593 | 0.01704 | -0.024859 | 0.19245 | 0.053479 | -0.021844 | 0.015142 | -0.008409 | 0.024657 | -0.017957 | 0.16486 | -0.031005 | 57.1205 | 7.0058 | -65.7654 | 57.0456 | 57.1776 | 57.0251 | -66.6577 | 66.2944 | -57.1134 | 66.3035 | 66.317 | 0.022596 | -57.156 | -56.9732 | -0.33235 | -0.092495 | 123.4458 | 0.55996 | 0.89232 | 0.039497 | -0.11297 | 66.35 | 66.3074 | 66.4902 | 66.3405 | -57.1691 | 123.3709 | 123.5029 | 123.3505 | 73.3312 | -123.7958
1513.2812 | 123.7335 | -66.2567 | 57.1426 | 0.047088 | -0.081447 | -0.042202 | -0.072614 | -0.0429 | -0.046753 | 0.050216 | 0.0068283 | 0.014904 | -0.025927 | 0.19245 | 0.052411 | -0.026423 | 0.0243 | -0.008409 | 0.024657 | -0.013378 | 0.18317 | -0.035584 | 57.1479 | 6.9966 | -65.7334 | 57.0776 | 57.205 | 57.0663 | -66.6211 | 66.2211 | -57.118 | 66.2303 | 66.2483 | 0.027175 | -57.156 | -56.9595 | -0.36439 | -0.065023 | 123.4046 | 0.52335 | 0.88774 | 0.062392 | -0.076344 | 66.2814 | 66.2433 | 66.4399 | 66.281 | -57.1782 | 123.3343 | 123.4617 | 123.323 | 73.2533 | -123.7637
1514.2656 | 123.6923 | -66.3071 | 57.106 | 0.06235 | -0.080379 | -0.042202 | -0.071546 | -0.0429 | -0.04889 | 0.080738 | 0.0057593 | 0.015972 | -0.023791 | 0.19138 | 0.051343 | -0.021844 | 0.015142 | -0.008409 | 0.038393 | -0.017957 | 0.16028 | -0.035584 | 57.1388 | 6.5754 | -65.7379 | 57.0547 | 57.1867 | 57.0342 | -66.644 | 66.2715 | -57.0676 | 66.2852 | 66.2987 | 0.027175 | -57.124 | -56.9457 | -0.33693 | -0.051294 | 123.4458 | 0.56912 | 0.90605 | 0.080698 | -0.071773 | 66.3455 | 66.2891 | 66.4673 | 66.3222 | -57.1416 | 123.3618 | 123.4938 | 123.3413 | 72.8825 | -123.75
1515.2656 | 123.6694 | -66.3254 | 57.1655 | 0.047088 | -0.081447 | -0.041133 | -0.072614 | -0.043968 | -0.04889 | 0.065477 | 0.0068283 | 0.015972 | -0.023791 | 0.19352 | 0.053479 | -0.026423 | 0.019721 | -0.012988 | 0.042971 | -0.008799 | 0.16944 | -0.035584 | 57.1388 | 6.9371 | -65.7563 | 57.073 | 57.2005 | 57.0526 | -66.6303 | 66.2898 | -57.1226 | 66.299 | 66.3124 | 0.022596 | -57.1743 | -56.9961 | -0.30488 | -0.092489 | 123.4641 | 0.56912 | 0.874 | 0.034925 | -0.11297 | 66.3683 | 66.3166 | 66.4948 | 66.3451 | -57.2011 | 123.3984 | 123.5258 | 123.3779 | 73.2625 | -123.7958
1516.2656 | 123.6786 | -66.2842 | 57.1335 | 0.047088 | -0.082515 | -0.042202 | -0.071546 | -0.045037 | -0.04889 | 0.050216 | 0.0057593 | 0.013835 | -0.023791 | 0.19245 | 0.052411 | -0.026423 | 0.015142 | 0.000747 | 0.033814 | -0.013378 | 0.16486 | -0.040163 | 57.1525 | 7.3583 | -65.7334 | 57.0822 | 57.205 | 57.0526 | -66.6303 | 66.244 | -57.0997 | 66.2578 | 66.2849 | 0.04091 | -57.1469 | -56.9686 | -0.34608 | -0.051289 | 123.4367 | 0.55082 | 0.89689 | 0.071547 | -0.080925 | 66.318 | 66.2708 | 66.449 | 66.2993 | -57.1736 | 123.3664 | 123.4892 | 123.3367 | 73.6425 | -123.7637
1517.2656 | 123.674 | -66.275 | 57.1838 | 0.047088 | -0.083584 | -0.041133 | -0.072614 | -0.0429 | -0.046753 | 0.080738 | 0.0057593 | 0.013835 | -0.025927 | 0.19352 | 0.052411 | -0.021844 | 0.019721 | 0.000747 | 0.038393 | -0.013378 | 0.1557 | -0.040163 | 57.1479 | 7.0699 | -65.7379 | 57.0868 | 57.2096 | 57.0755 | -66.6165 | 66.2349 | -57.1454 | 66.2532 | 66.2758 | 0.04091 | -57.1972 | -57.0281 | -0.3415 | -0.097065 | 123.4229 | 0.53708 | 0.87858 | 0.025771 | -0.10839 | 66.3134 | 66.2616 | 66.4307 | 66.2947 | -57.224 | 123.3618 | 123.4846 | 123.3505 | 73.3449 | -123.8004
1518.2812 | 123.7061 | -66.2521 | 57.2067 | 0.06235 | -0.081447 | -0.041133 | -0.070477 | -0.0429 | -0.04889 | 0.080738 | 0.0078963 | 0.015972 | -0.025927 | 0.19352 | 0.054547 | -0.026423 | 0.015142 | 0.000747 | 0.042971 | -0.017957 | 0.16944 | -0.040163 | 57.1708 | 6.9188 | -65.7151 | 57.1005 | 57.2233 | 57.0755 | -66.6074 | 66.212 | -57.1638 | 66.2257 | 66.2529 | 0.04091 | -57.2247 | -57.0373 | -0.35523 | -0.10622 | 123.423 | 0.53709 | 0.89231 | 0.016619 | -0.13127 | 66.2951 | 66.2342 | 66.4216 | 66.2673 | -57.2469 | 123.3526 | 123.4755 | 123.3276 | 73.1709 | -123.8141
1519.2656 | 123.7061 | -66.2796 | 57.1243 | 0.06235 | -0.080379 | -0.041133 | -0.069409 | -0.043968 | -0.046753 | 0.034955 | 0.0078963 | 0.014904 | -0.025927 | 0.19245 | 0.052411 | -0.021844 | 0.028878 | -0.003831 | 0.033814 | -0.017957 | 0.17402 | -0.040163 | 57.1388 | 7.1386 | -65.7517 | 57.0639 | 57.1913 | 57.0526 | -66.6394 | 66.2394 | -57.0905 | 66.2578 | 66.2758 | 0.036332 | -57.1423 | -56.9503 | -0.35981 | -0.060448 | 123.4184 | 0.52792 | 0.88774 | 0.066966 | -0.07177 | 66.3134 | 66.2616 | 66.4536 | 66.3085 | -57.1645 | 123.3435 | 123.4709 | 123.3322 | 73.4182 | -123.7637
1520.2656 | 123.7106 | -66.2384 | 57.1518 | 0.047088 | -0.080379 | -0.042202 | -0.072614 | -0.0429 | -0.047821 | 0.065477 | 0.0068283 | 0.015972 | -0.025927 | 0.19245 | 0.053479 | -0.017266 | 0.019721 | -0.008409 | 0.033814 | -0.013378 | 0.1557 | -0.035584 | 57.1571 | 6.9188 | -65.7196 | 57.0914 | 57.2233 | 57.08 | -66.6119 | 66.2028 | -57.118 | 66.2211 | 66.23 | 0.027175 | -57.1652 | -56.9961 | -0.37354 | -0.060442 | 123.3955 | 0.51877 | 0.89231 | 0.071551 | -0.071763 | 66.2722 | 66.225 | 66.3941 | 66.2581 | -57.1874 | 123.3298 | 123.4617 | 123.3184 | 73.1572 | -123.7637
1521.2656 | 123.6511 | -66.2979 | 57.1747 | 0.06235 | -0.081447 | -0.042202 | -0.071546 | -0.0429 | -0.047821 | 0.080738 | 0.0068283 | 0.014904 | -0.025927 | 0.19459 | 0.054547 | -0.021844 | 0.0243 | -0.003831 | 0.024657 | -0.013378 | 0.16944 | -0.031005 | 57.1617 | 6.9325 | -65.7288 | 57.0868 | 57.2142 | 57.0846 | -66.6211 | 66.2669 | -57.15 | 66.2761 | 66.2941 | 0.027174 | -57.1881 | -57.0052 | -0.32319 | -0.08791 | 123.4596 | 0.56913 | 0.89231 | 0.039505 | -0.090073 | 66.3226 | 66.2845 | 66.4674 | 66.3222 | -57.2057 | 123.3847 | 123.5121 | 123.3825 | 73.2304 | -123.7958
1522.2656 | 123.6832 | -66.2933 | 57.1655 | 0.06235 | -0.080379 | -0.04327 | -0.071546 | -0.0429 | -0.047821 | 0.080738 | 0.0068283 | 0.014904 | -0.025927 | 0.19245 | 0.051343 | -0.017266 | 0.015142 | -0.003831 | 0.038393 | -0.017957 | 0.17402 | -0.035584 | 57.1754 | 7.1889 | -65.7151 | 57.1005 | 57.2325 | 57.0709 | -66.6074 | 66.2578 | -57.1271 | 66.2761 | 66.2895 | 0.031753 | -57.1835 | -56.9915 | -0.31403 | -0.065018 | 123.4687 | 0.57828 | 0.89231 | 0.066975 | -0.094653 | 66.3317 | 66.2754 | 66.4674 | 66.3085 | -57.2011 | 123.3938 | 123.5258 | 123.3642 | 73.4823 | -123.7729
1523.2812 | 123.7061 | -66.2888 | 57.1609 | 0.06235 | -0.081447 | -0.042202 | -0.072614 | -0.043968 | -0.04889 | 0.065477 | 0.0068283 | 0.013835 | -0.025927 | 0.19245 | 0.051343 | -0.021844 | 0.019721 | -0.008409 | 0.061284 | -0.013378 | 0.18317 | -0.040163 | 57.1662 | 7.6834 | -65.7288 | 57.0959 | 57.2233 | 57.0663 | -66.6119 | 66.2486 | -57.0997 | 66.2669 | 66.2803 | 0.031754 | -57.1743 | -56.9778 | -0.32319 | -0.06502 | 123.455 | 0.55997 | 0.88316 | 0.062395 | -0.094655 | 66.35 | 66.2754 | 66.4719 | 66.3085 | -57.2011 | 123.3847 | 123.5121 | 123.3551 | 73.9722 | -123.7729
1524.2656 | 123.6923 | -66.3025 | 57.1564 | 0.047088 | -0.080379 | -0.041133 | -0.070477 | -0.043968 | -0.047821 | 0.050216 | 0.0068283 | 0.014904 | -0.026996 | 0.19352 | 0.053479 | -0.021844 | 0.0243 | -0.008409 | 0.042971 | -0.017957 | 0.1786 | -0.035584 | 57.1846 | 7.9994 | -65.7013 | 57.1051 | 57.2371 | 57.0892 | -66.5936 | 66.2669 | -57.1134 | 66.2806 | 66.2941 | 0.027175 | -57.1743 | -56.9778 | -0.29114 | -0.051285 | 123.487 | 0.60118 | 0.89232 | 0.080709 | -0.067184 | 66.3455 | 66.2845 | 66.4811 | 66.3268 | -57.192 | 123.4076 | 123.5396 | 123.3917 | 74.3019 | -123.75
1525.2656 | 123.6877 | -66.2888 | 57.1335 | 0.047088 | -0.082515 | -0.041133 | -0.071546 | -0.0429 | -0.04889 | 0.080738 | 0.0078963 | 0.014904 | -0.023791 | 0.19352 | 0.052411 | -0.031001 | 0.015142 | -0.003831 | 0.056706 | -0.013378 | 0.1786 | -0.031005 | 57.1662 | 7.6651 | -65.7242 | 57.0914 | 57.2233 | 57.08 | -66.6074 | 66.2578 | -57.0768 | 66.2578 | 66.2849 | 0.027174 | -57.1469 | -56.9549 | -0.31861 | -0.042132 | 123.455 | 0.56455 | 0.88316 | 0.089861 | -0.053453 | 66.3455 | 66.2754 | 66.4674 | 66.3039 | -57.1645 | 123.3801 | 123.5121 | 123.3688 | 73.9539 | -123.7408
1526.2656 | 123.7518 | -66.2567 | 57.1793 | 0.047088 | -0.083584 | -0.04327 | -0.072614 | -0.0429 | -0.047821 | 0.065477 | 0.0057593 | 0.014904 | -0.026996 | 0.19459 | 0.054547 | -0.026423 | 0.019721 | -0.008409 | 0.042971 | -0.00422 | 0.16944 | -0.031005 | 57.1754 | 7.3767 | -65.6876 | 57.1051 | 57.2325 | 57.0892 | -66.5936 | 66.2257 | -57.1363 | 66.2303 | 66.2483 | 0.022596 | -57.1835 | -57.0098 | -0.33692 | -0.074173 | 123.4321 | 0.56914 | 0.90605 | 0.053242 | -0.090072 | 66.2997 | 66.2525 | 66.4262 | 66.2764 | -57.2103 | 123.3618 | 123.4892 | 123.3459 | 73.6334 | -123.7729
1527.2656 | 123.7106 | -66.2338 | 57.1838 | 0.031826 | -0.083584 | -0.042202 | -0.071546 | -0.043968 | -0.047821 | 0.050216 | 0.0057593 | 0.013835 | -0.028064 | 0.19459 | 0.053479 | -0.017266 | 0.019721 | -0.012988 | 0.047549 | -0.013378 | 0.17402 | -0.040163 | 57.1891 | 7.5369 | -65.7105 | 57.1234 | 57.2554 | 57.1029 | -66.5799 | 66.1937 | -57.1363 | 66.2166 | 66.2208 | 0.027175 | -57.1972 | -57.0098 | -0.34607 | -0.060437 | 123.423 | 0.52335 | 0.86942 | 0.071557 | -0.080914 | 66.2814 | 66.2204 | 66.4078 | 66.2535 | -57.224 | 123.3572 | 123.4892 | 123.3367 | 73.7707 | -123.7637
1528.2812 | 123.7427 | -66.2521 | 57.1701 | 0.06235 | -0.082515 | -0.041133 | -0.070477 | -0.043968 | -0.047821 | 0.065477 | 0.0068283 | 0.014904 | -0.024859 | 0.19459 | 0.053479 | -0.026423 | 0.0243 | -0.003831 | 0.033814 | -0.008799 | 0.16944 | -0.040163 | 57.18 | 7.9169 | -65.7242 | 57.1097 | 57.2417 | 57.0938 | -66.6028 | 66.212 | -57.1363 | 66.2257 | 66.2483 | 0.036332 | -57.1789 | -57.0007 | -0.35065 | -0.060439 | 123.4321 | 0.52793 | 0.87858 | 0.071554 | -0.076338 | 66.2859 | 66.2433 | 66.4216 | 66.2764 | -57.2103 | 123.3618 | 123.4938 | 123.3459 | 74.1691 | -123.7729
1529.2656 | 123.674 | -66.2292 | 57.1976 | 0.031826 | -0.081447 | -0.042202 | -0.071546 | -0.043968 | -0.04889 | 0.080738 | 0.0057593 | 0.014904 | -0.025927 | 0.19566 | 0.051343 | -0.031001 | 0.015142 | 0.000747 | 0.038393 | -0.008799 | 0.18317 | -0.035584 | 57.1937 | 7.6789 | -65.7059 | 57.1326 | 57.2554 | 57.1075 | -66.5799 | 66.1937 | -57.1592 | 66.1982 | 66.23 | 0.036331 | -57.2064 | -57.0144 | -0.35064 | -0.065013 | 123.423 | 0.52335 | 0.874 | 0.057824 | -0.090068 | 66.2676 | 66.2204 | 66.4124 | 66.2444 | -57.2332 | 123.3618 | 123.4846 | 123.3368 | 73.9081 | -123.7775
1530.2656 | 123.6923 | -66.2521 | 57.1609 | 0.047088 | -0.082515 | -0.042202 | -0.071546 | -0.0429 | -0.04889 | 0.065477 | 0.0068283 | 0.014904 | -0.025927 | 0.19352 | 0.052411 | -0.026423 | 0.0243 | -0.008409 | 0.029236 | -0.017957 | 0.18317 | -0.031005 | 57.2029 | 7.3446 | -65.6601 | 57.1326 | 57.2691 | 57.1167 | -66.5662 | 66.2211 | -57.1317 | 66.2257 | 66.2437 | 0.022596 | -57.1789 | -56.9778 | -0.31402 | -0.028392 | 123.455 | 0.59203 | 0.90605 | 0.10818 | -0.04429 | 66.2814 | 66.2342 | 66.4353 | 66.2764 | -57.192 | 123.3847 | 123.5213 | 123.3688 | 73.5967 | -123.7271
1531.2656 | 123.7198 | -66.2292 | 57.1884 | 0.031826 | -0.082515 | -0.042202 | -0.074751 | -0.0429 | -0.046753 | 0.050216 | 0.0068283 | 0.013835 | -0.024859 | 0.19459 | 0.052411 | -0.017266 | 0.019721 | -0.003831 | 0.042971 | -0.017957 | 0.16944 | -0.035584 | 57.1937 | 7.743 | -65.6738 | 57.128 | 57.2691 | 57.1075 | -66.5753 | 66.1937 | -57.1454 | 66.212 | 66.2254 | 0.031753 | -57.2064 | -57.019 | -0.34606 | -0.060436 | 123.423 | 0.55541 | 0.90147 | 0.080715 | -0.080913 | 66.2722 | 66.2113 | 66.3987 | 66.249 | -57.224 | 123.3572 | 123.4984 | 123.3368 | 73.9722 | -123.7637
1532.2812 | 123.6969 | -66.2201 | 57.2342 | 0.077612 | -0.084652 | -0.042202 | -0.072614 | -0.043968 | -0.047821 | 0.080738 | 0.0057593 | 0.015972 | -0.024859 | 0.19459 | 0.053479 | -0.026423 | 0.015142 | -0.003831 | 0.047549 | -0.008799 | 0.16944 | -0.035584 | 57.1937 | 7.7567 | -65.683 | 57.1142 | 57.2462 | 57.0938 | -66.5891 | 66.1845 | -57.1866 | 66.1937 | 66.2163 | 0.031753 | -57.243 | -57.0648 | -0.36896 | -0.11995 | 123.4138 | 0.53709 | 0.90605 | 0.012046 | -0.14043 | 66.2676 | 66.2113 | 66.3895 | 66.2352 | -57.2698 | 123.3343 | 123.4663 | 123.3139 | 73.9768 | -123.8232
1533.2812 | 123.7198 | -66.2018 | 57.1976 | 0.047088 | -0.082515 | -0.04327 | -0.071546 | -0.040764 | -0.04889 | 0.065477 | 0.0057593 | 0.014904 | -0.024859 | 0.19459 | 0.052411 | -0.017266 | 0.015142 | -0.003831 | 0.033814 | -0.008799 | 0.16028 | -0.035584 | 57.212 | 7.4545 | -65.6693 | 57.1509 | 57.2783 | 57.1304 | -66.557 | 66.1662 | -57.1638 | 66.1845 | 66.198 | 0.031753 | -57.2064 | -57.0373 | -0.35522 | -0.046699 | 123.4138 | 0.53252 | 0.88773 | 0.080717 | -0.067175 | 66.2356 | 66.193 | 66.3621 | 66.2169 | -57.2332 | 123.3527 | 123.4801 | 123.3322 | 73.6563 | -123.7546
1534.2656 | 123.7289 | -66.2338 | 57.1564 | 0.047088 | -0.08572 | -0.041133 | -0.072614 | -0.043968 | -0.04889 | 0.065477 | 0.0057593 | 0.014904 | -0.024859 | 0.19459 | 0.053479 | -0.026423 | 0.015142 | -0.008409 | 0.052128 | -0.008799 | 0.16486 | -0.035584 | 57.2029 | 7.4408 | -65.7013 | 57.1326 | 57.2508 | 57.1075 | -66.5891 | 66.1982 | -57.1042 | 66.2074 | 66.2254 | 0.027175 | -57.1652 | -56.9915 | -0.35522 | -0.023814 | 123.4367 | 0.53251 | 0.88774 | 0.094445 | -0.048869 | 66.286 | 66.225 | 66.3987 | 66.249 | -57.192 | 123.3664 | 123.4846 | 123.3413 | 73.6746 | -123.7454
1535.2656 | 123.7061 | -66.2155 | 57.1976 | 0.031826 | -0.083584 | -0.042202 | -0.072614 | -0.043968 | -0.047821 | 0.050216 | 0.0068283 | 0.015972 | -0.025927 | 0.19459 | 0.052411 | -0.026423 | 0.015142 | -0.003831 | 0.033814 | -0.008799 | 0.16028 | -0.040163 | 57.1937 | 7.8437 | -65.6967 | 57.1326 | 57.26 | 57.1029 | -66.5845 | 66.1754 | -57.1638 | 66.1891 | 66.2117 | 0.036332 | -57.2064 | -57.0373 | -0.36896 | -0.065013 | 123.4092 | 0.51878 | 0.88773 | 0.062403 | -0.094647 | 66.2493 | 66.2067 | 66.3758 | 66.2307 | -57.2377 | 123.3481 | 123.4755 | 123.3184 | 74.0592 | -123.782
1536.2656 | 123.7381 | -66.2201 | 57.1976 | 0.077612 | -0.084652 | -0.040065 | -0.073683 | -0.043968 | -0.04889 | 0.050216 | 0.0057593 | 0.014904 | -0.024859 | 0.19459 | 0.051343 | -0.021844 | 0.019721 | -0.003831 | 0.029236 | -0.013378 | 0.17402 | -0.031005 | 57.212 | 7.8391 | -65.683 | 57.1371 | 57.2646 | 57.1075 | -66.5616 | 66.1891 | -57.1683 | 66.1982 | 66.2163 | 0.027174 | -57.2109 | -57.0236 | -0.34148 | -0.060434 | 123.4321 | 0.53709 | 0.87858 | 0.066981 | -0.090068 | 66.2493 | 66.2067 | 66.3941 | 66.2398 | -57.2286 | 123.3572 | 123.4846 | 123.3276 | 74.0592 | -123.7591
1537.2812 | 123.7335 | -66.2064 | 57.1655 | 0.06235 | -0.082515 | -0.042202 | -0.071546 | -0.045037 | -0.049958 | 0.065477 | 0.0068283 | 0.013835 | -0.025927 | 0.19459 | 0.052411 | -0.021844 | 0.019721 | 0.000747 | 0.065863 | -0.00422 | 0.17402 | -0.031005 | 57.1891 | 7.8116 | -65.7059 | 57.1142 | 57.2417 | 57.0846 | -66.5891 | 66.1754 | -57.0997 | 66.1845 | 66.2071 | 0.031752 | -57.1697 | -56.9915 | -0.38269 | -0.051283 | 123.3955 | 0.50047 | 0.88316 | 0.076132 | -0.080917 | 66.2722 | 66.2021 | 66.3804 | 66.2261 | -57.1965 | 123.3206 | 123.448 | 123.291 | 74.018 | -123.7546
1538.2812 | 123.6694 | -66.2064 | 57.1884 | 0.031826 | -0.08572 | -0.04327 | -0.073683 | -0.0429 | -0.04889 | 0.050216 | 0.0057593 | 0.014904 | -0.024859 | 0.19566 | 0.051343 | -0.026423 | 0.019721 | 0.000747 | 0.038393 | -0.013378 | 0.15112 | -0.031005 | 57.1937 | 7.4316 | -65.6876 | 57.1188 | 57.2646 | 57.1121 | -66.5799 | 66.1754 | -57.15 | 66.1799 | 66.2071 | 0.031752 | -57.2018 | -57.0373 | -0.37353 | -0.069593 | 123.4001 | 0.51878 | 0.89231 | 0.076136 | -0.076335 | 66.2448 | 66.193 | 66.3575 | 66.2261 | -57.2194 | 123.3252 | 123.4709 | 123.3184 | 73.638 | -123.7683
1539.2656 | 123.5962 | -66.275 | 57.2113 | 0.06235 | -0.083584 | -0.04327 | -0.071546 | -0.0429 | -0.046753 | 0.050216 | 0.0068283 | 0.014904 | -0.026996 | 0.19673 | 0.051343 | -0.017266 | 0.015142 | 0.005325 | 0.038393 | -0.013378 | 0.16944 | -0.035584 | 57.212 | 7.4179 | -65.6784 | 57.1417 | 57.2737 | 57.1212 | -66.5662 | 66.2394 | -57.1729 | 66.2578 | 66.2803 | 0.040909 | -57.2247 | -57.0419 | -0.29113 | -0.069589 | 123.4871 | 0.5966 | 0.88774 | 0.062406 | -0.090066 | 66.3134 | 66.2616 | 66.4445 | 66.2902 | -57.2469 | 123.4167 | 123.5487 | 123.3963 | 73.6929 | -123.7775
1540.2656 | 123.6191 | -66.2933 | 57.2205 | 0.047088 | -0.084652 | -0.042202 | -0.072614 | -0.043968 | -0.04889 | 0.095999 | 0.0078963 | 0.015972 | -0.025927 | 0.19566 | 0.051343 | -0.021844 | 0.0243 | -0.003831 | 0.047549 | -0.008799 | 0.1786 | -0.031005 | 57.2029 | 7.5232 | -65.6876 | 57.1371 | 57.2646 | 57.1167 | -66.5753 | 66.2623 | -57.1729 | 66.2715 | 66.2895 | 0.027174 | -57.2293 | -57.0419 | -0.28198 | -0.083322 | 123.4962 | 0.60576 | 0.88773 | 0.044093 | -0.1038 | 66.3409 | 66.2845 | 66.4719 | 66.3176 | -57.2515 | 123.4305 | 123.5579 | 123.41 | 73.8165 | -123.7958
1541.2656 | 123.6145 | -66.2521 | 57.193 | 0.031826 | -0.08572 | -0.04327 | -0.072614 | -0.045037 | -0.047821 | 0.095999 | 0.0068283 | 0.014904 | -0.025927 | 0.19566 | 0.050274 | -0.017266 | 0.028878 | 0.000747 | 0.033814 | -0.008799 | 0.16028 | -0.035584 | 57.212 | 7.0928 | -65.6601 | 57.1463 | 57.2783 | 57.1304 | -66.5478 | 66.2166 | -57.1592 | 66.2349 | 66.2529 | 0.036331 | -57.2018 | -57.0327 | -0.2957 | -0.046699 | 123.4642 | 0.59203 | 0.88773 | 0.085295 | -0.062597 | 66.2859 | 66.2433 | 66.4124 | 66.281 | -57.2286 | 123.3984 | 123.5304 | 123.3825 | 73.3449 | -123.7408
1542.2812 | 123.7335 | -66.2201 | 57.2205 | 0.047088 | -0.084652 | -0.04327 | -0.072614 | -0.043968 | -0.04889 | 0.065477 | 0.0078963 | 0.014904 | -0.026996 | 0.19673 | 0.052411 | -0.017266 | 0.015142 | -0.008409 | 0.042971 | -0.008799 | 0.15112 | -0.031005 | 57.2029 | 6.9692 | -65.6372 | 57.1371 | 57.2737 | 57.1167 | -66.5616 | 66.1891 | -57.1775 | 66.2028 | 66.2117 | 0.022596 | -57.2293 | -57.0693 | -0.34148 | -0.083322 | 123.423 | 0.58288 | 0.92436 | 0.053251 | -0.1038 | 66.2631 | 66.2113 | 66.3712 | 66.2352 | -57.2515 | 123.3572 | 123.4938 | 123.3368 | 73.1892 | -123.782
1543.2812 | 123.6649 | -66.2338 | 57.1976 | 0.06235 | -0.08572 | -0.042202 | -0.072614 | -0.0429 | -0.047821 | 0.050216 | 0.0078963 | 0.013835 | -0.025927 | 0.19566 | 0.052411 | -0.017266 | 0.019721 | -0.003831 | 0.033814 | -0.013378 | 0.18775 | -0.031005 | 57.1983 | 7.2439 | -65.6647 | 57.128 | 57.2646 | 57.1212 | -66.5799 | 66.2028 | -57.1638 | 66.2166 | 66.23 | 0.027174 | -57.2109 | -57.0098 | -0.34607 | -0.069591 | 123.4321 | 0.56914 | 0.91521 | 0.066981 | -0.076333 | 66.2676 | 66.2204 | 66.4216 | 66.2535 | -57.2286 | 123.3618 | 123.4984 | 123.3551 | 73.4777 | -123.7775
1544.2656 | 123.6191 | -66.3071 | 57.1884 | 0.047088 | -0.08572 | -0.04327 | -0.071546 | -0.0429 | -0.04889 | 0.050216 | 0.0078963 | 0.011699 | -0.028064 | 0.19566 | 0.050274 | -0.012688 | 0.015142 | -0.003831 | 0.029236 | -0.008799 | 0.16944 | -0.035584 | 57.1846 | 7.0241 | -65.6922 | 57.1188 | 57.2508 | 57.1029 | -66.5891 | 66.2715 | -57.1592 | 66.2944 | 66.3032 | 0.031753 | -57.1972 | -57.019 | -0.28198 | -0.069593 | 123.4916 | 0.61491 | 0.89689 | 0.062401 | -0.085492 | 66.3363 | 66.2983 | 66.4765 | 66.3222 | -57.224 | 123.4259 | 123.5579 | 123.41 | 73.3312 | -123.7775
1545.2656 | 123.5962 | -66.2979 | 57.2205 | 0.047088 | -0.08572 | -0.04327 | -0.073683 | -0.043968 | -0.051026 | 0.065477 | 0.0078963 | 0.011699 | -0.024859 | 0.19673 | 0.050274 | -0.026423 | 0.019721 | 0.000747 | 0.047549 | -0.013378 | 0.16944 | -0.040163 | 57.1937 | 6.58 | -65.6876 | 57.1188 | 57.26 | 57.1075 | -66.5707 | 66.2577 | -57.1729 | 66.2715 | 66.2987 | 0.04091 | -57.2338 | -57.051 | -0.27282 | -0.10164 | 123.4916 | 0.61033 | 0.88316 | 0.039515 | -0.11296 | 66.3455 | 66.2845 | 66.4674 | 66.3176 | -57.2606 | 123.4167 | 123.5579 | 123.4054 | 72.8779 | -123.7912
1546.2656 | 123.5687 | -66.2476 | 57.2525 | 0.047088 | -0.084652 | -0.04327 | -0.071546 | -0.043968 | -0.049958 | 0.065477 | 0.0089643 | 0.013835 | -0.025927 | 0.19673 | 0.051343 | -0.026423 | 0.0243 | -0.008409 | 0.056706 | -0.008799 | 0.18317 | -0.040163 | 57.2029 | 6.5388 | -65.6464 | 57.1371 | 57.2737 | 57.1212 | -66.5707 | 66.2074 | -57.1958 | 66.2211 | 66.2391 | 0.031754 | -57.2613 | -57.0693 | -0.32318 | -0.11536 | 123.4504 | 0.60119 | 0.92436 | 0.021208 | -0.13126 | 66.3043 | 66.2388 | 66.4307 | 66.2719 | -57.2927 | 123.3847 | 123.5213 | 123.3688 | 72.7863 | -123.8232
1547.2812 | 123.6832 | -66.2384 | 57.1838 | 0.047088 | -0.084652 | -0.04327 | -0.073683 | -0.0429 | -0.047821 | 0.065477 | 0.010032 | 0.01063 | -0.024859 | 0.19673 | 0.051343 | -0.026423 | 0.010564 | -0.003831 | 0.052128 | -0.008799 | 0.16944 | -0.040163 | 57.1983 | 6.9142 | -65.6509 | 57.128 | 57.2691 | 57.1167 | -66.5662 | 66.1982 | -57.1317 | 66.212 | 66.2346 | 0.036332 | -57.1926 | -57.0144 | -0.32775 | -0.055858 | 123.4367 | 0.58746 | 0.91521 | 0.085293 | -0.067178 | 66.2905 | 66.2296 | 66.4078 | 66.249 | -57.224 | 123.3664 | 123.5075 | 123.3551 | 73.1526 | -123.75
1548.2812 | 123.6694 | -66.2796 | 57.2021 | 0.031826 | -0.08572 | -0.044339 | -0.072614 | -0.041832 | -0.051026 | 0.050216 | 0.0111 | 0.01063 | -0.024859 | 0.19566 | 0.051343 | -0.021844 | 0.019721 | 0.000747 | 0.047549 | -0.008799 | 0.16944 | -0.035584 | 57.18 | 7.2027 | -65.6784 | 57.1142 | 57.2554 | 57.1121 | -66.5845 | 66.244 | -57.1546 | 66.2578 | 66.2803 | 0.036331 | -57.2109 | -57.0327 | -0.30487 | -0.087904 | 123.4596 | 0.60118 | 0.90605 | 0.053247 | -0.090067 | 66.3272 | 66.2708 | 66.449 | 66.2993 | -57.2377 | 123.3938 | 123.535 | 123.3917 | 73.4823 | -123.7866
1549.2656 | 123.5825 | -66.2476 | 57.2571 | 0.047088 | -0.08572 | -0.042202 | -0.073683 | -0.0429 | -0.049958 | 0.034955 | 0.0089643 | 0.011699 | -0.025927 | 0.19566 | 0.052411 | -0.021844 | 0.015142 | -0.003831 | 0.042971 | -0.013378 | 0.1786 | -0.040163 | 57.2212 | 6.7082 | -65.6555 | 57.1509 | 57.2829 | 57.1396 | -66.5433 | 66.2074 | -57.2141 | 66.2257 | 66.2437 | 0.036332 | -57.2705 | -57.0785 | -0.2957 | -0.10621 | 123.4687 | 0.59203 | 0.88773 | 0.025787 | -0.11753 | 66.2905 | 66.2342 | 66.4262 | 66.2627 | -57.2972 | 123.3984 | 123.5304 | 123.3871 | 72.9557 | -123.8003
1550.2656 | 123.5779 | -66.2567 | 57.2342 | 0.047088 | -0.087857 | -0.044339 | -0.072614 | -0.043968 | -0.051026 | 0.065477 | 0.0068283 | 0.013835 | -0.025927 | 0.19673 | 0.051343 | -0.021844 | 0.028878 | -0.003831 | 0.061284 | -0.013378 | 0.16944 | -0.031005 | 57.2212 | 6.8089 | -65.6647 | 57.1463 | 57.2829 | 57.1167 | -66.5524 | 66.2257 | -57.1729 | 66.2349 | 66.2529 | 0.027174 | -57.2476 | -57.0648 | -0.2957 | -0.087898 | 123.4779 | 0.59203 | 0.88773 | 0.048675 | -0.11753 | 66.318 | 66.2433 | 66.4262 | 66.2856 | -57.2652 | 123.403 | 123.5396 | 123.3734 | 73.0656 | -123.7866
1551.2656 | 123.5825 | -66.243 | 57.2525 | 0.047088 | -0.08572 | -0.042202 | -0.072614 | -0.0429 | -0.051026 | 0.065477 | 0.0068283 | 0.014904 | -0.026996 | 0.19566 | 0.050274 | -0.031001 | 0.0243 | 0.000747 | 0.047549 | -0.013378 | 0.18317 | -0.031005 | 57.2212 | 6.4975 | -65.6647 | 57.1509 | 57.2783 | 57.1212 | -66.5524 | 66.212 | -57.205 | 66.212 | 66.2437 | 0.031752 | -57.2659 | -57.0693 | -0.30944 | -0.10163 | 123.4642 | 0.5783 | 0.88773 | 0.025786 | -0.13126 | 66.2905 | 66.2296 | 66.4262 | 66.2673 | -57.2835 | 123.3939 | 123.5213 | 123.3642 | 72.7405 | -123.8049
1552.2812 | 123.674 | -66.1926 | 57.2113 | 0.047088 | -0.08572 | -0.042202 | -0.073683 | -0.045037 | -0.04889 | 0.065477 | 0.0068283 | 0.013835 | -0.025927 | 0.19673 | 0.051343 | -0.021844 | 0.028878 | 0.000747 | 0.047549 | -0.008799 | 0.18317 | -0.035584 | 57.2349 | 6.5296 | -65.6464 | 57.16 | 57.2966 | 57.1304 | -66.5433 | 66.157 | -57.1638 | 66.1708 | 66.1934 | 0.036331 | -57.2201 | -57.0281 | -0.35063 | -0.051275 | 123.4275 | 0.54626 | 0.89689 | 0.085299 | -0.080908 | 66.2402 | 66.1838 | 66.3758 | 66.2215 | -57.2469 | 123.3527 | 123.4892 | 123.323 | 72.7222 | -123.7546
1553.2812 | 123.7198 | -66.2018 | 57.2113 | 0.047088 | -0.086789 | -0.04327 | -0.071546 | -0.043968 | -0.049958 | 0.065477 | 0.0057593 | 0.01704 | -0.024859 | 0.19886 | 0.051343 | -0.021844 | 0.015142 | -0.003831 | 0.033814 | -0.00422 | 0.17402 | -0.031005 | 57.2166 | 6.3236 | -65.6372 | 57.16 | 57.292 | 57.1533 | -66.5524 | 66.1708 | -57.1775 | 66.1799 | 66.198 | 0.027174 | -57.2155 | -57.0373 | -0.35064 | -0.051275 | 123.4184 | 0.56457 | 0.91521 | 0.08072 | -0.058015 | 66.2356 | 66.1976 | 66.3758 | 66.2169 | -57.2423 | 123.3618 | 123.4938 | 123.3551 | 72.5253 | -123.7637
1554.2656 | 123.6328 | -66.2064 | 57.2754 | 0.031826 | -0.087857 | -0.042202 | -0.072614 | -0.043968 | -0.051026 | 0.050216 | 0.0068283 | 0.014904 | -0.024859 | 0.19779 | 0.050274 | -0.021844 | 0.015142 | -0.003831 | 0.061284 | -0.013378 | 0.18317 | -0.040163 | 57.2349 | 6.7173 | -65.6647 | 57.16 | 57.292 | 57.1441 | -66.5341 | 66.1662 | -57.2141 | 66.1845 | 66.2025 | 0.036332 | -57.2888 | -57.0922 | -0.32774 | -0.11536 | 123.4413 | 0.54167 | 0.86942 | 0.016633 | -0.13126 | 66.2676 | 66.193 | 66.3895 | 66.2215 | -57.3156 | 123.3664 | 123.4984 | 123.3505 | 72.9237 | -123.8095
1555.2656 | 123.5962 | -66.2476 | 57.2571 | 0.06235 | -0.086789 | -0.04327 | -0.073683 | -0.043968 | -0.051026 | 0.065477 | 0.0078963 | 0.013835 | -0.025927 | 0.19673 | 0.048138 | -0.026423 | 0.015142 | 0.000747 | 0.047549 | -0.00422 | 0.15112 | -0.040163 | 57.2395 | 7.0974 | -65.6464 | 57.1646 | 57.3149 | 57.1579 | -66.5341 | 66.2074 | -57.2095 | 66.2211 | 66.2483 | 0.04091 | -57.2613 | -57.106 | -0.28655 | -0.092472 | 123.4871 | 0.60119 | 0.88773 | 0.057837 | -0.099213 | 66.2951 | 66.2433 | 66.3987 | 66.2627 | -57.2972 | 123.4122 | 123.5625 | 123.4054 | 73.3449 | -123.7912
1556.2656 | 123.6099 | -66.2338 | 57.2342 | 0.047088 | -0.086789 | -0.042202 | -0.073683 | -0.043968 | -0.04889 | 0.065477 | 0.0046913 | 0.012767 | -0.024859 | 0.19779 | 0.049206 | -0.017266 | 0.019721 | 0.005325 | 0.052128 | -0.008799 | 0.1557 | -0.035584 | 57.2303 | 7.166 | -65.6647 | 57.16 | 57.2966 | 57.1579 | -66.5341 | 66.1982 | -57.1821 | 66.2166 | 66.2392 | 0.040909 | -57.243 | -57.0785 | -0.30028 | -0.074163 | 123.4642 | 0.56914 | 0.86942 | 0.062411 | -0.076325 | 66.286 | 66.225 | 66.3895 | 66.2535 | -57.2698 | 123.3939 | 123.5304 | 123.3917 | 73.3999 | -123.7683
1557.2656 | 123.6328 | -66.243 | 57.2433 | 0.06235 | -0.086789 | -0.04327 | -0.072614 | -0.0429 | -0.049958 | 0.050216 | 0.0057593 | 0.014904 | -0.025927 | 0.19673 | 0.049206 | -0.017266 | 0.0243 | 0.000747 | 0.038393 | -0.00422 | 0.1786 | -0.031005 | 57.2349 | 7.3355 | -65.6784 | 57.16 | 57.292 | 57.1441 | -66.5433 | 66.212 | -57.205 | 66.2257 | 66.2437 | 0.031752 | -57.2476 | -57.0648 | -0.30028 | -0.083318 | 123.4779 | 0.56456 | 0.86484 | 0.048677 | -0.099216 | 66.2814 | 66.2388 | 66.4216 | 66.2673 | -57.2744 | 123.403 | 123.535 | 123.3871 | 73.5784 | -123.7866
1558.2656 | 123.6237 | -66.2659 | 57.2433 | 0.047088 | -0.086789 | -0.04327 | -0.073683 | -0.041832 | -0.04889 | 0.065477 | 0.0068283 | 0.015972 | -0.025927 | 0.19886 | 0.050274 | -0.017266 | 0.015142 | 0.000747 | 0.042971 | -0.013378 | 0.17402 | -0.031005 | 57.2349 | 7.4591 | -65.6693 | 57.1646 | 57.3012 | 57.1441 | -66.5341 | 66.2349 | -57.2004 | 66.2486 | 66.2666 | 0.031752 | -57.2567 | -57.0693 | -0.26824 | -0.078739 | 123.5008 | 0.59661 | 0.86484 | 0.057834 | -0.099216 | 66.3088 | 66.2525 | 66.4399 | 66.281 | -57.2744 | 123.4305 | 123.567 | 123.41 | 73.7249 | -123.7775
1559.2656 | 123.5779 | -66.2292 | 57.2571 | 0.047088 | -0.088925 | -0.044339 | -0.073683 | -0.041832 | -0.049958 | 0.050216 | 0.0057593 | 0.014904 | -0.026996 | 0.19886 | 0.050274 | -0.021844 | 0.0243 | 0.000747 | 0.042971 | -0.013378 | 0.16486 | -0.040163 | 57.2258 | 7.4637 | -65.6738 | 57.16 | 57.2829 | 57.1396 | -66.5478 | 66.1891 | -57.2141 | 66.2074 | 66.23 | 0.04091 | -57.2705 | -57.0922 | -0.31859 | -0.097051 | 123.455 | 0.55541 | 0.874 | 0.025787 | -0.11753 | 66.2722 | 66.2159 | 66.3941 | 66.2535 | -57.2972 | 123.3893 | 123.5121 | 123.3688 | 73.6929 | -123.8049
1560.2656 | 123.6328 | -66.2109 | 57.2754 | 0.047088 | -0.087857 | -0.04327 | -0.073683 | -0.0429 | -0.049958 | 0.080738 | 0.0068283 | 0.013835 | -0.026996 | 0.19779 | 0.049206 | -0.021844 | 0.0243 | 0.000747 | 0.033814 | -0.00422 | 0.17402 | -0.049321 | 57.2441 | 7.3904 | -65.683 | 57.1692 | 57.3012 | 57.1533 | -66.5295 | 66.1616 | -57.2416 | 66.1891 | 66.2117 | 0.050068 | -57.2796 | -57.1014 | -0.31859 | -0.1062 | 123.455 | 0.52794 | 0.84653 | 0.02579 | -0.1221 | 66.2448 | 66.2067 | 66.385 | 66.2352 | -57.3247 | 123.3801 | 123.5121 | 123.3642 | 73.6013 | -123.8049
1561.2656 | 123.642 | -66.1972 | 57.2983 | 0.047088 | -0.088925 | -0.04327 | -0.073683 | -0.043968 | -0.051026 | 0.080738 | 0.0057593 | 0.015972 | -0.025927 | 0.19779 | 0.049206 | -0.017266 | 0.019721 | -0.003831 | 0.047549 | 0.000359 | 0.18775 | -0.035584 | 57.2441 | 7.4591 | -65.6693 | 57.1738 | 57.2966 | 57.1579 | -66.5249 | 66.1616 | -57.2507 | 66.1799 | 66.1934 | 0.031753 | -57.2979 | -57.1105 | -0.32774 | -0.12451 | 123.4413 | 0.52794 | 0.85568 | -0.001676 | -0.14041 | 66.2448 | 66.1976 | 66.385 | 66.2169 | -57.3339 | 123.371 | 123.4938 | 123.3551 | 73.6563 | -123.8232
1562.2656 | 123.6237 | -66.2521 | 57.2479 | 0.077612 | -0.091062 | -0.04327 | -0.072614 | -0.041832 | -0.049958 | 0.065477 | 0.0078963 | 0.013835 | -0.025927 | 0.19779 | 0.051343 | -0.026423 | 0.0243 | 0.000747 | 0.029236 | -0.013378 | 0.1786 | -0.035584 | 57.2349 | 7.3492 | -65.683 | 57.16 | 57.2783 | 57.1396 | -66.5433 | 66.2166 | -57.2187 | 66.2257 | 66.2529 | 0.036331 | -57.2613 | -57.0693 | -0.29113 | -0.087896 | 123.4871 | 0.56914 | 0.86026 | 0.030363 | -0.10837 | 66.2814 | 66.2388 | 66.4307 | 66.2764 | -57.2835 | 123.4122 | 123.5304 | 123.3917 | 73.6013 | -123.7912
1563.2812 | 123.5275 | -66.2659 | 57.1793 | 0.06235 | -0.088925 | -0.04327 | -0.072614 | -0.0429 | -0.04889 | 0.034955 | 0.0078963 | 0.013835 | -0.028064 | 0.19886 | 0.050274 | -0.031001 | 0.0243 | 0.000747 | 0.042971 | -0.00422 | 0.16486 | -0.031005 | 57.2212 | 7.8162 | -65.6922 | 57.16 | 57.2829 | 57.1441 | -66.5387 | 66.2349 | -57.1363 | 66.2349 | 66.2666 | 0.031752 | -57.1835 | -57.0144 | -0.27281 | -0.019231 | 123.4871 | 0.57371 | 0.84653 | 0.10361 | -0.035129 | 66.3088 | 66.2616 | 66.4307 | 66.2902 | -57.2103 | 123.4259 | 123.5487 | 123.41 | 74.0821 | -123.7179
1564.2656 | 123.6237 | -66.2201 | 57.2571 | 0.031826 | -0.086789 | -0.044339 | -0.072614 | -0.045037 | -0.051026 | 0.080738 | 0.0057593 | 0.01704 | -0.026996 | 0.19886 | 0.049206 | -0.026423 | 0.019721 | -0.003831 | 0.042971 | -0.00422 | 0.16486 | -0.040163 | 57.2487 | 7.5049 | -65.6738 | 57.1738 | 57.3012 | 57.1579 | -66.5295 | 66.1799 | -57.2141 | 66.1937 | 66.2163 | 0.036332 | -57.2613 | -57.0922 | -0.30943 | -0.083315 | 123.4688 | 0.54625 | 0.85568 | 0.044101 | -0.099213 | 66.2631 | 66.2159 | 66.385 | 66.2398 | -57.2972 | 123.3939 | 123.5213 | 123.378 | 73.725 | -123.7866
1565.2656 | 123.6511 | -66.2384 | 57.2525 | 0.047088 | -0.087857 | -0.042202 | -0.073683 | -0.043968 | -0.052095 | 0.050216 | 0.0068283 | 0.014904 | -0.025927 | 0.19886 | 0.049206 | -0.021844 | 0.0243 | -0.003831 | 0.056706 | -0.00422 | 0.18317 | -0.031005 | 57.2532 | 7.427 | -65.6738 | 57.1738 | 57.3103 | 57.1533 | -66.5249 | 66.2074 | -57.1958 | 66.2166 | 66.2346 | 0.027174 | -57.2567 | -57.0693 | -0.28654 | -0.078737 | 123.4916 | 0.56456 | 0.8511 | 0.057836 | -0.099213 | 66.2951 | 66.2342 | 66.4216 | 66.2627 | -57.2835 | 123.4122 | 123.5487 | 123.3917 | 73.6654 | -123.7774
1566.2656 | 123.6282 | -66.2064 | 57.2571 | 0.047088 | -0.088925 | -0.04327 | -0.073683 | -0.0429 | -0.051026 | 0.080738 | 0.0068283 | 0.012767 | -0.025927 | 0.19993 | 0.049206 | -0.021844 | 0.015142 | 0.005325 | 0.038393 | -0.013378 | 0.1786 | -0.035584 | 57.2303 | 7.2897 | -65.683 | 57.1646 | 57.292 | 57.1396 | -66.5433 | 66.1708 | -57.2187 | 66.1845 | 66.2117 | 0.040909 | -57.2705 | -57.0785 | -0.3369 | -0.092472 | 123.4367 | 0.52336 | 0.86026 | 0.034944 | -0.11753 | 66.2448 | 66.193 | 66.385 | 66.2215 | -57.2927 | 123.371 | 123.4984 | 123.3459 | 73.496 | -123.8003
1567.2656 | 123.587 | -66.2338 | 57.2617 | 0.031826 | -0.088925 | -0.04327 | -0.073683 | -0.045037 | -0.04889 | 0.065477 | 0.010032 | 0.014904 | -0.025927 | 0.19886 | 0.049206 | -0.026423 | 0.028878 | -0.003831 | 0.052128 | -0.013378 | 0.16944 | -0.040163 | 57.2303 | 7.2576 | -65.6967 | 57.1646 | 57.3012 | 57.1396 | -66.5341 | 66.1937 | -57.2095 | 66.2074 | 66.23 | 0.036332 | -57.275 | -57.0922 | -0.30028 | -0.09705 | 123.4642 | 0.53709 | 0.83737 | 0.039523 | -0.1221 | 66.286 | 66.2204 | 66.4033 | 66.2627 | -57.3018 | 123.3984 | 123.535 | 123.3734 | 73.4914 | -123.7958
1568.2812 | 123.5825 | -66.2384 | 57.2571 | 0.031826 | -0.089994 | -0.04327 | -0.073683 | -0.0429 | -0.051026 | 0.095999 | 0.0078963 | 0.015972 | -0.025927 | 0.19993 | 0.049206 | -0.021844 | 0.0243 | 0.000747 | 0.033814 | -0.00422 | 0.17402 | -0.058478 | 57.2349 | 7.1523 | -65.6189 | 57.16 | 57.292 | 57.135 | -66.5341 | 66.1799 | -57.2233 | 66.2166 | 66.2392 | 0.059225 | -57.2613 | -57.0831 | -0.2957 | -0.097051 | 123.4733 | 0.61951 | 0.91521 | 0.034944 | -0.12211 | 66.2722 | 66.2342 | 66.4124 | 66.2627 | -57.3156 | 123.3984 | 123.5304 | 123.3734 | 73.3907 | -123.7912
1569.2656 | 123.587 | -66.2338 | 57.2708 | 0.06235 | -0.087857 | -0.044339 | -0.074751 | -0.043968 | -0.051026 | 0.065477 | 0.0057593 | 0.012767 | -0.025927 | 0.19993 | 0.050274 | -0.026423 | 0.019721 | -0.003831 | 0.047549 | -0.00422 | 0.18775 | -0.044742 | 57.2487 | 7.3904 | -65.6097 | 57.1783 | 57.3012 | 57.1624 | -66.5249 | 66.1891 | -57.2233 | 66.2074 | 66.23 | 0.040911 | -57.275 | -57.0831 | -0.29112 | -0.09247 | 123.4825 | 0.62409 | 0.91521 | 0.030368 | -0.10837 | 66.2814 | 66.2296 | 66.4216 | 66.2535 | -57.3156 | 123.4122 | 123.535 | 123.3963 | 73.6242 | -123.7958
1570.2656 | 123.6145 | -66.2384 | 57.2617 | 0.06235 | -0.086789 | -0.044339 | -0.073683 | -0.043968 | -0.049958 | 0.065477 | 0.0057593 | 0.013835 | -0.025927 | 0.19993 | 0.048138 | -0.031001 | 0.028878 | -0.003831 | 0.052128 | 0.000359 | 0.17402 | -0.044742 | 57.2303 | 7.5278 | -65.6555 | 57.1646 | 57.2966 | 57.1579 | -66.5387 | 66.1937 | -57.2095 | 66.2074 | 66.2346 | 0.040911 | -57.2613 | -57.0876 | -0.30028 | -0.09705 | 123.4687 | 0.58288 | 0.88316 | 0.034945 | -0.10379 | 66.2905 | 66.2388 | 66.4124 | 66.2673 | -57.3064 | 123.403 | 123.535 | 123.3963 | 73.7662 | -123.8003
1571.2656 | 123.6053 | -66.188 | 57.2708 | 0.047088 | -0.089994 | -0.04327 | -0.072614 | -0.043968 | -0.049958 | 0.065477 | 0.0057593 | 0.014904 | -0.026996 | 0.201 | 0.051343 | -0.021844 | 0.028878 | 0.000747 | 0.042971 | -0.00422 | 0.18317 | -0.044742 | 57.2532 | 7.3217 | -65.6418 | 57.1829 | 57.3103 | 57.1716 | -66.5204 | 66.1433 | -57.2278 | 66.1662 | 66.1888 | 0.045489 | -57.275 | -57.0876 | -0.33232 | -0.087891 | 123.4413 | 0.54626 | 0.87858 | 0.039525 | -0.09921 | 66.231 | 66.1838 | 66.3712 | 66.2169 | -57.3156 | 123.371 | 123.4984 | 123.3597 | 73.5098 | -123.7912
1572.2656 | 123.5962 | -66.2109 | 57.3074 | 0.092874 | -0.088925 | -0.045407 | -0.073683 | -0.041832 | -0.052095 | 0.065477 | 0.0057593 | 0.014904 | -0.026996 | 0.19993 | 0.050274 | -0.017266 | 0.019721 | 0.000747 | 0.047549 | -0.008799 | 0.17402 | -0.040163 | 57.2532 | 7.6697 | -65.6281 | 57.1967 | 57.3195 | 57.1808 | -66.5112 | 66.1708 | -57.2599 | 66.1937 | 66.2117 | 0.04091 | -57.3162 | -57.1334 | -0.30027 | -0.11078 | 123.4642 | 0.58288 | 0.88316 | 0.012062 | -0.12667 | 66.2585 | 66.2021 | 66.385 | 66.2307 | -57.3476 | 123.4076 | 123.5304 | 123.3917 | 73.8806 | -123.8186
1573.2812 | 123.6145 | -66.1835 | 57.2983 | 0.047088 | -0.091062 | -0.04327 | -0.074751 | -0.0429 | -0.049958 | 0.050216 | 0.0068283 | 0.013835 | -0.025927 | 0.19886 | 0.050274 | -0.021844 | 0.028878 | -0.008409 | 0.052128 | -0.008799 | 0.1786 | -0.040163 | 57.2578 | 7.6285 | -65.6143 | 57.1921 | 57.3195 | 57.1762 | -66.5158 | 66.1433 | -57.2462 | 66.1616 | 66.1751 | 0.031754 | -57.3071 | -57.1197 | -0.33232 | -0.1062 | 123.4413 | 0.56915 | 0.90147 | 0.021217 | -0.1221 | 66.2356 | 66.1747 | 66.3621 | 66.2124 | -57.3384 | 123.3756 | 123.503 | 123.3597 | 73.812 | -123.8141
1574.2656 | 123.6649 | -66.1652 | 57.2845 | 0.077612 | -0.088925 | -0.046475 | -0.074751 | -0.043968 | -0.049958 | 0.065477 | 0.0068283 | 0.014904 | -0.026996 | 0.201 | 0.048138 | -0.017266 | 0.019721 | -0.008409 | 0.056706 | -0.00422 | 0.16944 | -0.040163 | 57.2532 | 7.5049 | -65.6052 | 57.1875 | 57.3195 | 57.1762 | -66.5112 | 66.125 | -57.2278 | 66.1479 | 66.1568 | 0.031754 | -57.2888 | -57.1151 | -0.34605 | -0.097046 | 123.4184 | 0.56 | 0.90605 | 0.03495 | -0.10836 | 66.2219 | 66.1609 | 66.3346 | 66.1849 | -57.3247 | 123.3527 | 123.4847 | 123.3413 | 73.67 | -123.7958
1575.2656 | 123.6786 | -66.1285 | 57.2662 | 0.06235 | -0.088925 | -0.045407 | -0.074751 | -0.0429 | -0.04889 | 0.065477 | 0.0068283 | 0.013835 | -0.025927 | 0.19886 | 0.048138 | -0.03558 | 0.019721 | 0.000747 | 0.047549 | -0.008799 | 0.1557 | -0.040163 | 57.267 | 7.2713 | -65.6097 | 57.2012 | 57.3378 | 57.167 | -66.5066 | 66.0884 | -57.2187 | 66.093 | 66.1293 | 0.04091 | -57.275 | -57.1105 | -0.37809 | -0.065 | 123.3955 | 0.5188 | 0.89689 | 0.071575 | -0.099211 | 66.1761 | 66.1197 | 66.2842 | 66.1483 | -57.3064 | 123.3298 | 123.4664 | 123.2956 | 73.3999 | -123.7729
1576.2656 | 123.5779 | -66.188 | 57.3212 | 0.047088 | -0.089994 | -0.044339 | -0.072614 | -0.043968 | -0.049958 | 0.050216 | 0.0068283 | 0.013835 | -0.026996 | 0.19993 | 0.049206 | -0.021844 | 0.0243 | -0.008409 | 0.052128 | -0.008799 | 0.16486 | -0.035584 | 57.2715 | 6.7036 | -65.6097 | 57.2012 | 57.3241 | 57.1808 | -66.5021 | 66.1525 | -57.269 | 66.1662 | 66.1796 | 0.027175 | -57.33 | -57.1563 | -0.314 | -0.11993 | 123.4596 | 0.57831 | 0.89231 | 0.002907 | -0.14041 | 66.2402 | 66.1793 | 66.3529 | 66.2123 | -57.3568 | 123.3893 | 123.5121 | 123.3688 | 72.8916 | -123.8232
1577.2656 | 123.6099 | -66.1652 | 57.312 | 0.077612 | -0.088925 | -0.045407 | -0.072614 | -0.043968 | -0.051026 | 0.065477 | 0.0078963 | 0.015972 | -0.025927 | 0.19993 | 0.049206 | -0.026423 | 0.0243 | -0.003831 | 0.038393 | -0.00422 | 0.17402 | -0.040163 | 57.2761 | 6.873 | -65.596 | 57.2058 | 57.3332 | 57.1899 | -66.5066 | 66.125 | -57.2736 | 66.1387 | 66.1613 | 0.036332 | -57.3162 | -57.138 | -0.34147 | -0.1062 | 123.4413 | 0.56916 | 0.91063 | 0.021219 | -0.12209 | 66.2036 | 66.1609 | 66.3392 | 66.1895 | -57.3522 | 123.371 | 123.4984 | 123.3551 | 73.0382 | -123.8186
1578.2656 | 123.6328 | -66.1789 | 57.3029 | 0.06235 | -0.089994 | -0.045407 | -0.072614 | -0.045037 | -0.051026 | 0.065477 | 0.0057593 | 0.013835 | -0.025927 | 0.19993 | 0.049206 | -0.017266 | 0.0243 | -0.003831 | 0.033814 | -0.008799 | 0.1786 | -0.049321 | 57.267 | 7.4637 | -65.4541 | 57.1967 | 57.3332 | 57.1762 | -66.5021 | 66.1296 | -57.269 | 66.1616 | 66.1751 | 0.04549 | -57.3117 | -57.1243 | -0.32316 | -0.1062 | 123.4459 | 0.72483 | 1.048 | 0.030375 | -0.12667 | 66.2127 | 66.1701 | 66.3575 | 66.2032 | -57.3522 | 123.3756 | 123.5121 | 123.3551 | 73.6425 | -123.8049
1579.2656 | 123.6832 | -66.1789 | 57.2708 | 0.092874 | -0.088925 | -0.045407 | -0.074751 | -0.045037 | -0.047821 | 0.065477 | 0.0057593 | 0.013835 | -0.026996 | 0.19993 | 0.048138 | -0.026423 | 0.019721 | -0.003831 | 0.024657 | -0.008799 | 0.18775 | -0.035584 | 57.267 | 7.308 | -65.6372 | 57.2104 | 57.3378 | 57.1853 | -66.4975 | 66.1433 | -57.2462 | 66.1525 | 66.1751 | 0.031753 | -57.2796 | -57.0831 | -0.31858 | -0.060421 | 123.4459 | 0.54168 | 0.86026 | 0.066997 | -0.085474 | 66.2036 | 66.1701 | 66.3666 | 66.1986 | -57.3064 | 123.3893 | 123.5167 | 123.3642 | 73.4869 | -123.7683
1580.2656 | 123.6923 | -66.1789 | 57.2479 | 0.077612 | -0.089994 | -0.045407 | -0.074751 | -0.0429 | -0.051026 | 0.065477 | 0.0057593 | 0.014904 | -0.025927 | 0.19993 | 0.049206 | -0.017266 | 0.033457 | 0.000747 | 0.047549 | -0.008799 | 0.16944 | -0.035584 | 57.2532 | 7.1294 | -65.6281 | 57.1829 | 57.3149 | 57.167 | -66.5249 | 66.1433 | -57.2004 | 66.1616 | 66.1796 | 0.036331 | -57.2567 | -57.0785 | -0.34605 | -0.065003 | 123.4321 | 0.55084 | 0.89689 | 0.066992 | -0.080901 | 66.2264 | 66.1701 | 66.3483 | 66.2124 | -57.2835 | 123.3618 | 123.4938 | 123.3459 | 73.3083 | -123.7729
1581.2656 | 123.7152 | -66.124 | 57.2708 | 0.047088 | -0.089994 | -0.045407 | -0.073683 | -0.0429 | -0.049958 | 0.065477 | 0.0057593 | 0.014904 | -0.026996 | 0.20207 | 0.049206 | -0.017266 | 0.015142 | 0.000747 | 0.047549 | -0.00422 | 0.18317 | -0.035584 | 57.2532 | 7.1203 | -65.6418 | 57.1921 | 57.3149 | 57.1167 | -66.5158 | 66.0884 | -57.2233 | 66.1067 | 66.1247 | 0.036331 | -57.275 | -57.0876 | -0.39183 | -0.078735 | 123.3772 | 0.48217 | 0.874 | 0.044104 | -0.15415 | 66.1715 | 66.1197 | 66.3071 | 66.1391 | -57.3064 | 123.316 | 123.4389 | 123.2406 | 73.2442 | -123.7866
1582.2812 | 123.6923 | -66.1514 | 57.2983 | 0.06235 | -0.092131 | -0.044339 | -0.072614 | -0.0429 | -0.049958 | 0.050216 | 0.0068283 | 0.013835 | -0.026996 | 0.201 | 0.048138 | -0.017266 | 0.019721 | -0.008409 | 0.065863 | -0.017957 | 0.16028 | -0.040163 | 57.2807 | 6.9966 | -65.6189 | 57.2058 | 57.3378 | 57.1853 | -66.4975 | 66.1113 | -57.2324 | 66.1342 | 66.143 | 0.031754 | -57.3162 | -57.138 | -0.34605 | -0.092465 | 123.4321 | 0.53253 | 0.87858 | 0.039531 | -0.11294 | 66.2173 | 66.1335 | 66.3117 | 66.1711 | -57.3384 | 123.3572 | 123.4892 | 123.3368 | 73.1481 | -123.7958
1583.2812 | 123.6191 | -66.1835 | 57.2983 | 0.06235 | -0.088925 | -0.045407 | -0.072614 | -0.0429 | -0.051026 | 0.065477 | 0.0057593 | 0.014904 | -0.028064 | 0.20207 | 0.049206 | -0.021844 | 0.0243 | -0.003831 | 0.052128 | -0.008799 | 0.18775 | -0.035584 | 57.2807 | 6.7356 | -65.6464 | 57.2104 | 57.347 | 57.1762 | -66.4929 | 66.1479 | -57.2462 | 66.1616 | 66.1796 | 0.031753 | -57.3071 | -57.1105 | -0.30942 | -0.087887 | 123.4642 | 0.5371 | 0.84652 | 0.048688 | -0.1221 | 66.2356 | 66.1747 | 66.3712 | 66.2078 | -57.3339 | 123.3939 | 123.5304 | 123.3597 | 72.9191 | -123.7912
1584.2656 | 123.7381 | -66.0736 | 57.3074 | 0.077612 | -0.089994 | -0.045407 | -0.072614 | -0.043968 | -0.051026 | 0.095999 | 0.0068283 | 0.014904 | -0.026996 | 0.20207 | 0.049206 | -0.026423 | 0.015142 | -0.003831 | 0.047549 | -0.00422 | 0.1786 | -0.035584 | 57.2899 | 6.9463 | -65.5777 | 57.2241 | 57.347 | 57.2037 | -66.4883 | 66.038 | -57.2599 | 66.0472 | 66.0698 | 0.031753 | -57.3117 | -57.1288 | -0.41471 | -0.083306 | 123.3635 | 0.49592 | 0.91063 | 0.039533 | -0.10378 | 66.1212 | 66.0694 | 66.2522 | 66.0887 | -57.343 | 123.2977 | 123.4206 | 123.2773 | 73.0199 | -123.7957
1585.2656 | 123.7289 | -66.1285 | 57.3074 | 0.06235 | -0.089994 | -0.044339 | -0.074751 | -0.0429 | -0.049958 | 0.065477 | 0.0046913 | 0.015972 | -0.028064 | 0.19886 | 0.049206 | -0.026423 | 0.0243 | 0.000747 | 0.024657 | -0.008799 | 0.1786 | -0.031005 | 57.299 | 7.2713 | -65.6509 | 57.2241 | 57.3607 | 57.222 | -66.4746 | 66.0975 | -57.2828 | 66.1021 | 66.1293 | 0.031752 | -57.3162 | -57.1288 | -0.34604 | -0.083306 | 123.4276 | 0.47759 | 0.82363 | 0.053269 | -0.085466 | 66.1532 | 66.1197 | 66.3071 | 66.1528 | -57.3384 | 123.3527 | 123.4892 | 123.3505 | 73.3999 | -123.782
1586.2656 | 123.7473 | -66.0919 | 57.2891 | 0.047088 | -0.091062 | -0.044339 | -0.072614 | -0.045037 | -0.051026 | 0.065477 | 0.0068283 | 0.014904 | -0.026996 | 0.201 | 0.04707 | -0.026423 | 0.0243 | -0.003831 | 0.038393 | -0.008799 | 0.16486 | -0.035584 | 57.3082 | 7.5552 | -65.6372 | 57.2379 | 57.3699 | 57.222 | -66.47 | 66.0563 | -57.2507 | 66.0655 | 66.0881 | 0.031753 | -57.2979 | -57.1243 | -0.37808 | -0.051261 | 123.4001 | 0.45471 | 0.83279 | 0.080736 | -0.067156 | 66.1303 | 66.0831 | 66.2568 | 66.1162 | -57.3247 | 123.3298 | 123.4618 | 123.3139 | 73.6471 | -123.7591
1587.2656 | 123.7289 | -66.124 | 57.2983 | 0.06235 | -0.091062 | -0.045407 | -0.073683 | -0.043968 | -0.051026 | 0.065477 | 0.0057593 | 0.014904 | -0.025927 | 0.20207 | 0.049206 | -0.026423 | 0.0243 | 0.000747 | 0.042971 | -0.008799 | 0.17402 | -0.044742 | 57.2899 | 7.6148 | -65.6738 | 57.2241 | 57.3515 | 57.2037 | -66.4792 | 66.0792 | -57.2553 | 66.0975 | 66.1247 | 0.045489 | -57.3071 | -57.1243 | -0.3552 | -0.074151 | 123.4138 | 0.45012 | 0.80532 | 0.053267 | -0.094626 | 66.1669 | 66.1152 | 66.298 | 66.1483 | -57.343 | 123.3481 | 123.4755 | 123.3276 | 73.7387 | -123.7774
1588.2812 | 123.7427 | -66.124 | 57.2983 | 0.047088 | -0.091062 | -0.044339 | -0.073683 | -0.043968 | -0.051026 | 0.080738 | 0.0057593 | 0.013835 | -0.028064 | 0.20207 | 0.050274 | -0.021844 | 0.015142 | 0.000747 | 0.042971 | -0.013378 | 0.18317 | -0.040163 | 57.299 | 7.0836 | -65.6372 | 57.2379 | 57.3607 | 57.2174 | -66.4746 | 66.0838 | -57.2553 | 66.1021 | 66.1247 | 0.04091 | -57.3117 | -57.1151 | -0.35062 | -0.060416 | 123.423 | 0.48675 | 0.83737 | 0.062424 | -0.08089 | 66.1669 | 66.1106 | 66.3071 | 66.1391 | -57.3384 | 123.3618 | 123.4847 | 123.3414 | 73.2076 | -123.7729
1589.2656 | 123.6832 | -66.1194 | 57.3029 | 0.06235 | -0.092131 | -0.045407 | -0.074751 | -0.043968 | -0.04889 | 0.080738 | 0.0068283 | 0.013835 | -0.026996 | 0.20207 | 0.048138 | -0.021844 | 0.015142 | -0.008409 | 0.056706 | -0.008799 | 0.1786 | -0.035584 | 57.3082 | 7.2439 | -65.6372 | 57.2379 | 57.3744 | 57.2265 | -66.4654 | 66.0838 | -57.2462 | 66.0975 | 66.111 | 0.027175 | -57.3117 | -57.1243 | -0.34604 | -0.064993 | 123.4276 | 0.48217 | 0.82821 | 0.071583 | -0.07631 | 66.1761 | 66.1106 | 66.298 | 66.1345 | -57.3384 | 123.3572 | 123.4938 | 123.3459 | 73.3633 | -123.7683
1590.2656 | 123.7289 | -66.1148 | 57.3303 | 0.06235 | -0.092131 | -0.045407 | -0.073683 | -0.041832 | -0.052095 | 0.080738 | 0.0057593 | 0.014904 | -0.026996 | 0.20207 | 0.048138 | -0.021844 | 0.019721 | -0.003831 | 0.042971 | -0.013378 | 0.18317 | -0.040163 | 57.3082 | 6.6578 | -65.6372 | 57.2516 | 57.3699 | 57.2403 | -66.4608 | 66.0746 | -57.2874 | 66.093 | 66.111 | 0.036332 | -57.3437 | -57.1471 | -0.34604 | -0.078723 | 123.423 | 0.47759 | 0.82363 | 0.039538 | -0.09004 | 66.1578 | 66.1014 | 66.298 | 66.1345 | -57.3705 | 123.3664 | 123.4847 | 123.3551 | 72.7726 | -123.7912
1591.2656 | 123.6832 | -66.1011 | 57.3257 | 0.047088 | -0.092131 | -0.047544 | -0.074751 | -0.0429 | -0.049958 | 0.065477 | 0.0068283 | 0.014904 | -0.026996 | 0.20207 | 0.048138 | -0.021844 | 0.019721 | -0.003831 | 0.056706 | -0.00422 | 0.17402 | -0.031005 | 57.3036 | 6.96 | -65.3167 | 57.2424 | 57.3561 | 57.2311 | -66.47 | 66.0701 | -57.269 | 66.0792 | 66.0972 | 0.027174 | -57.33 | -57.1517 | -0.36893 | -0.083303 | 123.4047 | 0.78437 | 1.1533 | 0.030379 | -0.09462 | 66.1578 | 66.0969 | 66.2751 | 66.1208 | -57.3567 | 123.3435 | 123.4572 | 123.3322 | 73.0611 | -123.7957
1592.2656 | 123.6786 | -66.1285 | 57.2983 | 0.047088 | -0.093199 | -0.044339 | -0.075819 | -0.043968 | -0.052095 | 0.080738 | 0.0057593 | 0.014904 | -0.026996 | 0.201 | 0.048138 | -0.021844 | 0.019721 | -0.003831 | 0.052128 | -0.008799 | 0.1786 | -0.035584 | 57.3036 | 7.2164 | -65.6509 | 57.247 | 57.3699 | 57.1991 | -66.4746 | 66.093 | -57.2462 | 66.1067 | 66.1247 | 0.031753 | -57.3071 | -57.1197 | -0.34604 | -0.051259 | 123.4321 | 0.47759 | 0.82363 | 0.071581 | -0.099204 | 66.1807 | 66.1197 | 66.3071 | 66.1483 | -57.3339 | 123.3756 | 123.4984 | 123.3276 | 73.3449 | -123.7729
1593.2812 | 123.7473 | -66.1011 | 57.312 | 0.047088 | -0.092131 | -0.044339 | -0.074751 | -0.043968 | -0.051026 | 0.065477 | 0.0057593 | 0.014904 | -0.028064 | 0.201 | 0.049206 | -0.021844 | 0.019721 | 0.000747 | 0.042971 | -0.00422 | 0.18317 | -0.031005 | 57.2944 | 7.1569 | -65.6922 | 57.2379 | 57.3744 | 57.222 | -66.47 | 66.0701 | -57.269 | 66.0792 | 66.1018 | 0.031752 | -57.3162 | -57.1288 | -0.36893 | -0.074149 | 123.3955 | 0.40892 | 0.77784 | 0.062427 | -0.090044 | 66.144 | 66.0969 | 66.2842 | 66.1208 | -57.343 | 123.3389 | 123.4755 | 123.323 | 73.258 | -123.782
1594.2656 | 123.6694 | -66.1423 | 57.2845 | 0.06235 | -0.093199 | -0.044339 | -0.074751 | -0.043968 | -0.051026 | 0.050216 | 0.0068283 | 0.014904 | -0.026996 | 0.20314 | 0.049206 | -0.017266 | 0.0243 | -0.003831 | 0.056706 | -0.008799 | 0.1786 | -0.031005 | 57.2853 | 6.7585 | -65.6876 | 57.2241 | 57.3515 | 57.1991 | -66.4837 | 66.1113 | -57.2278 | 66.125 | 66.1384 | 0.027174 | -57.2933 | -57.106 | -0.34146 | -0.060418 | 123.4276 | 0.4547 | 0.79616 | 0.067 | -0.085471 | 66.199 | 66.1335 | 66.3209 | 66.1666 | -57.3156 | 123.3664 | 123.4938 | 123.3413 | 72.9008 | -123.7683
1595.2656 | 123.674 | -66.1331 | 57.2983 | 0.077612 | -0.092131 | -0.044339 | -0.073683 | -0.045037 | -0.049958 | 0.080738 | 0.0068283 | 0.012767 | -0.025927 | 0.20207 | 0.049206 | -0.021844 | 0.0243 | -0.003831 | 0.065863 | -0.013378 | 0.18317 | -0.035584 | 57.3036 | 6.8135 | -65.6693 | 57.2424 | 57.3699 | 57.2128 | -66.4654 | 66.0975 | -57.2324 | 66.1113 | 66.1293 | 0.031753 | -57.3117 | -57.1151 | -0.3323 | -0.055837 | 123.4367 | 0.46385 | 0.79616 | 0.071581 | -0.085468 | 66.199 | 66.1197 | 66.3163 | 66.1574 | -57.3339 | 123.3756 | 123.503 | 123.3459 | 72.9466 | -123.7637
1596.2656 | 123.6832 | -66.1194 | 57.2983 | 0.047088 | -0.092131 | -0.044339 | -0.074751 | -0.0429 | -0.04889 | 0.050216 | 0.0068283 | 0.014904 | -0.026996 | 0.201 | 0.048138 | -0.021844 | 0.019721 | -0.008409 | 0.033814 | -0.00422 | 0.18775 | -0.031005 | 57.3036 | 7.0424 | -65.6738 | 57.2379 | 57.3699 | 57.2128 | -66.47 | 66.0884 | -57.2645 | 66.0975 | 66.111 | 0.022596 | -57.3025 | -57.1105 | -0.35062 | -0.060416 | 123.423 | 0.44554 | 0.79616 | 0.071581 | -0.085468 | 66.1532 | 66.1152 | 66.3071 | 66.1391 | -57.3293 | 123.3572 | 123.4892 | 123.3322 | 73.1618 | -123.7683
1597.2656 | 123.6557 | -66.0919 | 57.3578 | 0.077612 | -0.094267 | -0.045407 | -0.074751 | -0.043968 | -0.051026 | 0.065477 | 0.0068283 | 0.014904 | -0.028064 | 0.19993 | 0.048138 | -0.021844 | 0.019721 | 0.000747 | 0.038393 | -0.008799 | 0.16944 | -0.035584 | 57.3219 | 6.8455 | -65.6326 | 57.2653 | 57.3973 | 57.2586 | -66.4425 | 66.0563 | -57.3194 | 66.0701 | 66.0927 | 0.036331 | -57.3666 | -57.1883 | -0.35061 | -0.092454 | 123.4138 | 0.45929 | 0.80989 | 0.039544 | -0.099191 | 66.1303 | 66.0831 | 66.2614 | 66.1116 | -57.3934 | 123.3573 | 123.4893 | 123.3505 | 72.9374 | -123.8003
1598.2812 | 123.6649 | -66.0965 | 57.3624 | 0.047088 | -0.093199 | -0.045407 | -0.072614 | -0.043968 | -0.052095 | 0.065477 | 0.0046913 | 0.014904 | -0.026996 | 0.20207 | 0.049206 | -0.026423 | 0.0243 | 0.000747 | 0.042971 | -0.008799 | 0.16944 | -0.040163 | 57.3357 | 6.667 | -65.5731 | 57.2699 | 57.4019 | 57.2678 | -66.4288 | 66.0563 | -57.3194 | 66.0701 | 66.0972 | 0.04091 | -57.3712 | -57.1929 | -0.33229 | -0.092453 | 123.4321 | 0.52339 | 0.85568 | 0.039544 | -0.094612 | 66.1395 | 66.0877 | 66.2659 | 66.1208 | -57.4025 | 123.3664 | 123.4984 | 123.3643 | 72.7635 | -123.7912
1599.2656 | 123.6511 | -66.0828 | 57.3441 | 0.031826 | -0.094267 | -0.045407 | -0.074751 | -0.0429 | -0.051026 | 0.050216 | 0.016441 | 0.002084 | -0.026996 | 0.20207 | 0.048138 | -0.021844 | 0.0243 | -0.003831 | 0.061284 | -0.017957 | 0.18317 | -0.031005 | 57.3311 | 6.6303 | -65.5777 | 57.2745 | 57.4111 | 57.2586 | -66.4242 | 66.0518 | -57.2828 | 66.0609 | 66.0789 | 0.027174 | -57.362 | -57.1609 | -0.34145 | -0.069564 | 123.4138 | 0.50507 | 0.84652 | 0.067013 | -0.085458 | 66.144 | 66.0648 | 66.2659 | 66.1071 | -57.3751 | 123.3573 | 123.4938 | 123.3414 | 72.7131 | -123.7683
1600.2656 | 123.6603 | -66.1148 | 57.2891 | 0.031826 | -0.093199 | -0.044339 | -0.074751 | -0.041832 | -0.049958 | 0.050216 | 0.013237 | 0.008494 | -0.028064 | 0.2042 | 0.048138 | -0.008109 | 0.019721 | -0.008409 | 0.056706 | -0.008799 | 0.16944 | -0.040163 | 57.3357 | 6.7127 | -65.5868 | 57.2653 | 57.4019 | 57.2403 | -66.4334 | 66.0746 | -57.2324 | 66.1067 | 66.1064 | 0.031754 | -57.2979 | -57.1197 | -0.31856 | -0.02379 | 123.4505 | 0.52796 | 0.84652 | 0.11279 | -0.048842 | 66.1715 | 66.106 | 66.2842 | 66.1345 | -57.3293 | 123.3801 | 123.5167 | 123.3551 | 72.8276 | -123.7225
1601.2656 | 123.7015 | -66.1102 | 57.2983 | 0.031826 | -0.093199 | -0.044339 | -0.073683 | -0.0429 | -0.052095 | 0.080738 | 0.019646 | 0.002084 | -0.025927 | 0.20314 | 0.048138 | -0.021844 | 0.0243 | 0.000747 | 0.042971 | -0.008799 | 0.1786 | -0.031005 | 57.3036 | 6.6212 | -65.6555 | 57.2424 | 57.3836 | 57.2082 | -66.4608 | 66.0792 | -57.2553 | 66.0884 | 66.111 | 0.031752 | -57.3071 | -57.1197 | -0.35061 | -0.055837 | 123.4138 | 0.4547 | 0.80532 | 0.085317 | -0.090047 | 66.1532 | 66.1014 | 66.2888 | 66.1345 | -57.3293 | 123.3527 | 123.4938 | 123.3185 | 72.7314 | -123.7591
1602.2656 | 123.6969 | -67.3416 | 56.0349 | 0.047088 | -0.093199 | -0.045407 | -0.072614 | -0.043968 | -0.052095 | 0.034955 | 0.016441 | 0.003152 | 0.062737 | 0.29181 | 0.048138 | -0.012688 | 0.0243 | 0.000747 | 0.029236 | -0.00422 | 0.19233 | -0.031005 | 56.049 | 21.3097 | 51.7701 | 55.9925 | 56.1199 | 55.9812 | -67.688 | 67.3106 | -56.0056 | 67.3289 | 67.3424 | 0.031752 | -56.0391 | -55.8425 | -0.34635 | -0.042338 | 123.3906 | 119.1117 | 119.458 | 0.085051 | -0.053685 | 67.3709 | 67.3374 | 67.5339 | 67.3659 | -56.0659 | 123.3341 | 123.4615 | 123.3228 | 88.6513 | -123.7228
1603.2812 | 123.7198 | -67.3233 | 56.0761 | 0.06235 | -0.095336 | -0.044339 | -0.075819 | -0.043968 | -0.051026 | 0.080738 | 0.018578 | 0.004221 | 0.064873 | 0.29288 | 0.050274 | -0.021844 | 0.015142 | -0.008409 | 0.052128 | -0.008799 | 0.18775 | -0.040163 | 56.0445 | 21.6851 | 52.2646 | 55.9788 | 56.1153 | 55.9491 | -67.6971 | 67.2831 | -56.0239 | 67.3015 | 67.3149 | 0.031754 | -56.0848 | -55.8883 | -0.37382 | -0.097273 | 123.3678 | 119.5879 | 119.9617 | 0.039273 | -0.12693 | 67.3754 | 67.3145 | 67.5111 | 67.3384 | -56.1162 | 123.3021 | 123.4386 | 123.2724 | 89.0084 | -123.7732
1604.2656 | 123.7015 | -67.3553 | 56.0257 | 0.047088 | -0.093199 | -0.045407 | -0.075819 | -0.046105 | -0.052095 | 0.050216 | 0.013237 | 0.007426 | 0.063805 | 0.29395 | 0.048138 | -0.021844 | 0.0243 | 0.000747 | 0.033814 | -0.00422 | 0.1786 | -0.031005 | 56.0445 | 21.882 | 52.7316 | 55.9696 | 56.1062 | 55.9537 | -67.7017 | 67.3243 | -55.9919 | 67.3335 | 67.3561 | 0.031752 | -56.0299 | -55.8471 | -0.34636 | -0.056076 | 123.3998 | 120.0869 | 120.4333 | 0.08047 | -0.072001 | 67.3892 | 67.3511 | 67.5339 | 67.3796 | -56.0567 | 123.325 | 123.4615 | 123.309 | 89.2374 | -123.7274
1605.2656 | 123.7427 | -67.3691 | 56.044 | 0.06235 | -0.093199 | -0.047544 | -0.074751 | -0.0429 | -0.051026 | 0.065477 | 0.037805 | -0.019282 | 0.064873 | 0.29395 | 0.04707 | -0.021844 | 0.015142 | -0.008409 | 0.042971 | 0.004938 | 0.1786 | -0.031005 | 56.0445 | 21.8408 | 52.8827 | 55.9879 | 56.1153 | 55.94 | -67.6971 | 67.3381 | -56.001 | 67.3472 | 67.3607 | 0.022596 | -56.0391 | -55.8654 | -0.32804 | -0.056072 | 123.4135 | 120.2518 | 120.5798 | 0.071317 | -0.10405 | 67.4121 | 67.374 | 67.5477 | 67.3842 | -56.075 | 123.357 | 123.4844 | 123.309 | 89.2099 | -123.7411
1606.2656 | 123.7015 | -67.3599 | 56.0257 | 0.047088 | -0.092131 | -0.04327 | -0.074751 | -0.041832 | -0.052095 | 0.065477 | 0.039942 | -0.017145 | 0.062737 | 0.29395 | 0.048138 | -0.026423 | 0.015142 | -0.003831 | 0.033814 | -0.00422 | 0.16944 | -0.040163 | 56.0353 | 22.2804 | 52.9193 | 55.965 | 56.097 | 55.9445 | -67.7063 | 67.3198 | -55.9919 | 67.3335 | 67.3561 | 0.036332 | -56.0299 | -55.8563 | -0.34636 | -0.060654 | 123.3952 | 120.2792 | 120.6256 | 0.071313 | -0.081158 | 67.3937 | 67.3557 | 67.5294 | 67.3751 | -56.0659 | 123.325 | 123.4569 | 123.3045 | 89.6403 | -123.732
1607.2656 | 123.6923 | -67.3645 | 56.0577 | 0.077612 | -0.094267 | -0.044339 | -0.075819 | -0.041832 | -0.052095 | 0.034955 | 0.038873 | -0.019282 | 0.065941 | 0.29608 | 0.04707 | -0.026423 | 0.0243 | -0.003831 | 0.052128 | -0.008799 | 0.1786 | -0.026426 | 56.0399 | 22.4223 | 53.0567 | 55.9696 | 56.097 | 55.9537 | -67.7017 | 67.3381 | -56.0056 | 67.3381 | 67.3607 | 0.022595 | -56.0665 | -55.8791 | -0.3372 | -0.088119 | 123.4044 | 120.4212 | 120.7584 | 0.03927 | -0.10404 | 67.4166 | 67.3557 | 67.5431 | 67.3888 | -56.0842 | 123.3341 | 123.4615 | 123.3182 | 89.7868 | -123.7594
1608.2812 | 123.6511 | -67.3279 | 56.0577 | 0.047088 | -0.093199 | -0.045407 | -0.075819 | -0.045037 | -0.051026 | 0.065477 | 0.038873 | -0.02035 | 0.063805 | 0.29395 | 0.049206 | -0.017266 | 0.019721 | 0.000747 | 0.038393 | -0.008799 | 0.19691 | -0.035584 | 56.0445 | 22.2758 | 52.9422 | 55.9834 | 56.1107 | 55.9537 | -67.6971 | 67.2923 | -56.0193 | 67.3106 | 67.3286 | 0.036331 | -56.0665 | -55.8608 | -0.36924 | -0.074383 | 123.3723 | 120.2701 | 120.6393 | 0.053006 | -0.10404 | 67.3663 | 67.3191 | 67.5248 | 67.3476 | -56.0933 | 123.3112 | 123.4386 | 123.2816 | 89.6037 | -123.7549
1609.2656 | 123.555 | -67.4149 | 56.0532 | 0.06235 | -0.094267 | -0.044339 | -0.072614 | -0.043968 | -0.051026 | 0.065477 | 0.038873 | -0.021418 | 0.063805 | 0.29288 | 0.049206 | -0.017266 | 0.0243 | -0.003831 | 0.056706 | -0.008799 | 0.18317 | -0.040163 | 56.0353 | 22.2895 | 52.7774 | 55.965 | 56.097 | 55.9491 | -67.7063 | 67.3747 | -55.9965 | 67.3976 | 67.411 | 0.036332 | -56.062 | -55.87 | -0.29143 | -0.08812 | 123.4502 | 120.1922 | 120.4837 | 0.043847 | -0.10405 | 67.4716 | 67.4061 | 67.598 | 67.4392 | -56.0933 | 123.3799 | 123.5119 | 123.364 | 89.7044 | -123.7594
1610.2656 | 123.6832 | -67.3645 | 56.0211 | 0.06235 | -0.095336 | -0.044339 | -0.074751 | -0.045037 | -0.052095 | 0.050216 | 0.037805 | -0.017145 | 0.065941 | 0.29395 | 0.048138 | -0.017266 | 0.028878 | 0.000747 | 0.052128 | 0.000359 | 0.17402 | -0.040163 | 56.0216 | 21.795 | 52.9056 | 55.9696 | 56.097 | 55.9491 | -67.6971 | 67.3243 | -55.969 | 67.3472 | 67.3652 | 0.04091 | -56.0208 | -55.8471 | -0.33262 | -0.051498 | 123.3861 | 120.2701 | 120.6027 | 0.075891 | -0.072002 | 67.4166 | 67.3649 | 67.5385 | 67.3934 | -56.0613 | 123.3341 | 123.4615 | 123.3136 | 89.1595 | -123.7182
1611.2656 | 123.6649 | -67.3691 | 56.0486 | 0.06235 | -0.094267 | -0.046475 | -0.074751 | -0.045037 | -0.049958 | 0.065477 | 0.039942 | -0.019282 | 0.064873 | 0.29395 | 0.048138 | -0.021844 | 0.015142 | -0.003831 | 0.061284 | -0.008799 | 0.16028 | -0.035584 | 56.0445 | 22.0285 | 52.9926 | 55.9788 | 56.0924 | 55.9491 | -67.6971 | 67.3335 | -55.9873 | 67.3472 | 67.3652 | 0.031753 | -56.0574 | -55.8883 | -0.32804 | -0.069807 | 123.4135 | 120.3617 | 120.6897 | 0.043846 | -0.099468 | 67.4304 | 67.3603 | 67.5294 | 67.3842 | -56.0842 | 123.3479 | 123.4615 | 123.3182 | 89.3976 | -123.7457
1612.2812 | 123.6923 | -67.3553 | 56.0486 | 0.031826 | -0.094267 | -0.045407 | -0.075819 | -0.043968 | -0.051026 | 0.050216 | 0.039942 | -0.018213 | 0.062737 | 0.29395 | 0.048138 | -0.021844 | 0.0243 | 0.000747 | 0.024657 | -0.008799 | 0.18775 | -0.035584 | 56.0353 | 21.8774 | 52.9605 | 55.9696 | 56.097 | 55.9354 | -67.7017 | 67.3198 | -56.0239 | 67.3335 | 67.3561 | 0.036331 | -56.0574 | -55.8608 | -0.34636 | -0.078964 | 123.3906 | 120.3159 | 120.6622 | 0.048425 | -0.1132 | 67.38 | 67.3465 | 67.5431 | 67.3796 | -56.0842 | 123.325 | 123.4524 | 123.2907 | 89.2328 | -123.7503
1613.2812 | 123.6786 | -67.3645 | 56.0486 | 0.047088 | -0.095336 | -0.045407 | -0.072614 | -0.0429 | -0.052095 | 0.095999 | 0.039942 | -0.019282 | 0.062737 | 0.29502 | 0.04707 | -0.017266 | 0.019721 | -0.003831 | 0.038393 | -0.00422 | 0.18775 | -0.026426 | 56.0261 | 21.8957 | 52.9285 | 55.965 | 56.097 | 55.9537 | -67.7063 | 67.3381 | -56.0102 | 67.3472 | 67.3607 | 0.022595 | -56.0528 | -55.8608 | -0.34178 | -0.083542 | 123.3906 | 120.293 | 120.6348 | 0.048425 | -0.094889 | 67.4029 | 67.3603 | 67.5523 | 67.3842 | -56.075 | 123.3295 | 123.4615 | 123.3182 | 89.2603 | -123.7549
1614.2656 | 123.5596 | -67.4103 | 56.0715 | 0.031826 | -0.094267 | -0.044339 | -0.074751 | -0.043968 | -0.052095 | 0.065477 | 0.039942 | -0.019282 | 0.065941 | 0.29502 | 0.04707 | -0.012688 | 0.019721 | 0.005325 | 0.038393 | -0.008799 | 0.18317 | -0.031005 | 56.0307 | 21.7721 | 52.8827 | 55.965 | 56.0924 | 55.9445 | -67.6971 | 67.3793 | -56.0331 | 67.3976 | 67.4156 | 0.03633 | -56.0803 | -55.8883 | -0.28685 | -0.10643 | 123.441 | 120.293 | 120.5798 | 0.020958 | -0.12693 | 67.4487 | 67.4015 | 67.5935 | 67.43 | -56.1025 | 123.3753 | 123.5027 | 123.3548 | 89.1824 | -123.7686
1615.2656 | 123.5687 | -67.424 | 56.044 | 0.047088 | -0.094267 | -0.044339 | -0.073683 | -0.043968 | -0.052095 | 0.080738 | 0.038873 | -0.018213 | 0.063805 | 0.29502 | 0.049206 | -0.021844 | 0.0243 | 0.000747 | 0.033814 | -0.013378 | 0.18775 | -0.035584 | 56.017 | 21.6119 | 52.8735 | 55.9467 | 56.0695 | 55.9216 | -67.72 | 67.3884 | -56.0102 | 67.4022 | 67.4248 | 0.036331 | -56.0574 | -55.8563 | -0.29601 | -0.097278 | 123.441 | 120.2975 | 120.5936 | 0.025531 | -0.12236 | 67.4578 | 67.4106 | 67.6118 | 67.4483 | -56.0796 | 123.3707 | 123.4935 | 123.3457 | 89.0359 | -123.764
1616.2656 | 123.5779 | -67.424 | 56.0349 | 0.077612 | -0.094267 | -0.044339 | -0.076888 | -0.0429 | -0.052095 | 0.065477 | 0.038873 | -0.019282 | 0.063805 | 0.29502 | 0.048138 | -0.021844 | 0.019721 | 0.000747 | 0.038393 | -0.00422 | 0.19691 | -0.040163 | 56.0124 | 21.6851 | 52.8369 | 55.9513 | 56.0787 | 55.9354 | -67.7154 | 67.3838 | -55.9965 | 67.4022 | 67.4248 | 0.04091 | -56.0391 | -55.8379 | -0.29143 | -0.083545 | 123.4364 | 120.2609 | 120.5523 | 0.043843 | -0.099471 | 67.4624 | 67.4198 | 67.6209 | 67.4437 | -56.075 | 123.3753 | 123.5027 | 123.3594 | 89.1091 | -123.7503
1617.2656 | 123.6191 | -67.4332 | 56.0532 | 0.031826 | -0.095336 | -0.04327 | -0.075819 | -0.045037 | -0.052095 | 0.034955 | 0.038873 | -0.018213 | 0.062737 | 0.29502 | 0.04707 | -0.026423 | 0.019721 | 0.000747 | 0.047549 | -0.00422 | 0.17402 | -0.031005 | 55.9895 | 21.6348 | 52.9376 | 55.933 | 56.0695 | 55.8942 | -67.7338 | 67.4022 | -56.0056 | 67.4067 | 67.4339 | 0.031752 | -56.0574 | -55.8791 | -0.30059 | -0.12017 | 123.4227 | 120.3708 | 120.6714 | 0.016375 | -0.15899 | 67.4807 | 67.4289 | 67.6072 | 67.4529 | -56.0842 | 123.3662 | 123.5027 | 123.3273 | 89.0679 | -123.7869
1618.2812 | 123.6649 | -67.424 | 56.0074 | 0.031826 | -0.094267 | -0.044339 | -0.074751 | -0.043968 | -0.049958 | 0.065477 | 0.038873 | -0.02035 | 0.062737 | 0.29502 | 0.049206 | -0.026423 | 0.015142 | 0.000747 | 0.070441 | -0.00422 | 0.17402 | -0.031005 | 56.0124 | 21.6485 | 52.9514 | 55.9559 | 56.0787 | 55.9216 | -67.7109 | 67.393 | -55.9369 | 67.3976 | 67.4248 | 0.031752 | -56.0116 | -55.8334 | -0.28685 | -0.0515 | 123.4364 | 120.3754 | 120.6622 | 0.071309 | -0.08574 | 67.4945 | 67.4198 | 67.598 | 67.4392 | -56.0384 | 123.3799 | 123.5027 | 123.3457 | 89.0725 | -123.7182
1619.2656 | 123.5687 | -67.4103 | 56.0669 | 0.047088 | -0.096404 | -0.046475 | -0.075819 | -0.0429 | -0.052095 | 0.065477 | 0.038873 | -0.019282 | 0.062737 | 0.29395 | 0.048138 | -0.017266 | 0.0243 | 0.005325 | 0.033814 | 0.000359 | 0.19691 | -0.035584 | 56.0261 | 21.3555 | 52.9331 | 55.965 | 56.0924 | 55.9491 | -67.6971 | 67.3747 | -56.0331 | 67.393 | 67.4156 | 0.040909 | -56.0665 | -55.87 | -0.28685 | -0.10185 | 123.4364 | 120.3433 | 120.6302 | 0.025535 | -0.11778 | 67.4441 | 67.4106 | 67.6072 | 67.4346 | -56.1025 | 123.3753 | 123.5027 | 123.3594 | 88.7657 | -123.764
1620.2656 | 123.5321 | -67.4103 | 56.0532 | 0.06235 | -0.095336 | -0.044339 | -0.073683 | -0.045037 | -0.053163 | 0.065477 | 0.04101 | -0.018213 | 0.062737 | 0.29502 | 0.048138 | -0.031001 | 0.028878 | 0.005325 | 0.061284 | -0.00422 | 0.18317 | -0.040163 | 56.0445 | 21.5111 | 53.1666 | 55.9788 | 56.1107 | 55.94 | -67.6788 | 67.3701 | -55.9919 | 67.3793 | 67.4156 | 0.045488 | -56.0574 | -55.87 | -0.26853 | -0.074385 | 123.4547 | 120.5769 | 120.8454 | 0.057583 | -0.1132 | 67.4716 | 67.4061 | 67.5935 | 67.4392 | -56.0933 | 123.3891 | 123.521 | 123.3502 | 88.9214 | -123.732
1621.2656 | 123.5458 | -67.4057 | 56.0577 | 0.031826 | -0.096404 | -0.045407 | -0.075819 | -0.045037 | -0.052095 | 0.050216 | 0.038873 | -0.02035 | 0.062737 | 0.29608 | 0.048138 | -0.012688 | 0.0243 | 0.000747 | 0.047549 | -0.00422 | 0.1786 | -0.035584 | 56.0353 | 21.7355 | 53.1116 | 55.9788 | 56.1062 | 55.9354 | -67.6834 | 67.3701 | -56.0102 | 67.393 | 67.4064 | 0.036331 | -56.062 | -55.8791 | -0.27769 | -0.078962 | 123.441 | 120.5173 | 120.795 | 0.048427 | -0.12236 | 67.4532 | 67.4015 | 67.5843 | 67.43 | -56.0933 | 123.3845 | 123.5119 | 123.3411 | 89.1412 | -123.7411
1622.2656 | 123.5916 | -67.3828 | 56.0715 | 0.047088 | -0.096404 | -0.045407 | -0.075819 | -0.043968 | -0.053163 | 0.050216 | 0.04101 | -0.019282 | 0.062737 | 0.29502 | 0.048138 | -0.021844 | 0.0243 | 0.005325 | 0.029236 | -0.008799 | 0.18775 | -0.040163 | 56.0399 | 21.6485 | 53.1849 | 55.9742 | 56.1062 | 55.9537 | -67.6834 | 67.3426 | -56.0422 | 67.361 | 67.3881 | 0.045488 | -56.0803 | -55.8837 | -0.30057 | -0.097273 | 123.4227 | 120.5677 | 120.8683 | 0.034694 | -0.11778 | 67.412 | 67.374 | 67.5706 | 67.4071 | -56.1116 | 123.357 | 123.489 | 123.3365 | 89.0313 | -123.7549
1623.2812 | 123.5641 | -67.3874 | 56.0669 | 0.047088 | -0.097472 | -0.04327 | -0.076888 | -0.045037 | -0.051026 | 0.065477 | 0.038873 | -0.02035 | 0.061668 | 0.29502 | 0.04707 | -0.021844 | 0.0243 | -0.003831 | 0.047549 | -0.008799 | 0.18317 | -0.031005 | 56.0399 | 21.4928 | 53.1025 | 55.9834 | 56.1062 | 55.9629 | -67.6788 | 67.3564 | -56.0193 | 67.3655 | 67.3836 | 0.027174 | -56.0757 | -55.8837 | -0.29142 | -0.083539 | 123.4273 | 120.4899 | 120.7813 | 0.039271 | -0.10404 | 67.4349 | 67.3786 | 67.5706 | 67.4117 | -56.0979 | 123.3707 | 123.4936 | 123.3502 | 88.8802 | -123.7457
1624.2656 | 123.5413 | -67.3874 | 56.0669 | 0.031826 | -0.096404 | -0.044339 | -0.073683 | -0.043968 | -0.052095 | 0.065477 | 0.038873 | -0.018213 | 0.063805 | 0.29608 | 0.048138 | -0.026423 | 0.0243 | 0.000747 | 0.056706 | -0.008799 | 0.19691 | -0.040163 | 56.0307 | 21.4516 | 53.4184 | 55.9742 | 56.1016 | 55.9583 | -67.688 | 67.3472 | -56.0102 | 67.361 | 67.3881 | 0.04091 | -56.0757 | -55.87 | -0.30058 | -0.092696 | 123.4181 | 120.8058 | 121.1064 | 0.034692 | -0.10862 | 67.4441 | 67.3786 | 67.5843 | 67.4117 | -56.1071 | 123.3616 | 123.489 | 123.3457 | 88.839 | -123.7549
1625.2656 | 123.5367 | -67.4011 | 56.0669 | 0.047088 | -0.095336 | -0.04327 | -0.074751 | -0.045037 | -0.052095 | 0.034955 | 0.04101 | -0.017145 | 0.062737 | 0.29502 | 0.048138 | -0.026423 | 0.015142 | -0.003831 | 0.056706 | -0.00422 | 0.1786 | -0.035584 | 56.0445 | 21.9782 | 53.4321 | 55.9788 | 56.1062 | 55.972 | -67.6834 | 67.3655 | -56.0102 | 67.3747 | 67.3973 | 0.031753 | -56.0711 | -55.8883 | -0.28226 | -0.088118 | 123.4456 | 120.8333 | 121.1155 | 0.039271 | -0.094886 | 67.4578 | 67.3969 | 67.5797 | 67.4163 | -56.1025 | 123.3799 | 123.5073 | 123.3731 | 89.3793 | -123.7503
1626.2656 | 123.555 | -67.3874 | 56.0898 | 0.06235 | -0.096404 | -0.044339 | -0.074751 | -0.045037 | -0.052095 | 0.050216 | 0.037805 | -0.019282 | 0.0606 | 0.29502 | 0.048138 | -0.008109 | 0.033457 | -0.008409 | 0.024657 | -0.00422 | 0.18775 | -0.040163 | 56.0536 | 22.2025 | 53.3406 | 55.9879 | 56.1153 | 55.9583 | -67.6742 | 67.3472 | -56.0651 | 67.3793 | 67.379 | 0.031754 | -56.094 | -55.902 | -0.28684 | -0.10185 | 123.441 | 120.728 | 121.0148 | 0.02554 | -0.13151 | 67.412 | 67.3832 | 67.5751 | 67.4208 | -56.1299 | 123.3753 | 123.5027 | 123.3457 | 89.5899 | -123.764
1627.2656 | 123.5413 | -67.424 | 56.0715 | 0.06235 | -0.097472 | -0.046475 | -0.074751 | -0.041832 | -0.052095 | 0.065477 | 0.038873 | -0.019282 | 0.062737 | 0.29608 | 0.048138 | -0.021844 | 0.028878 | 0.000747 | 0.056706 | -0.00422 | 0.18317 | -0.031005 | 56.0124 | 21.9324 | 53.2215 | 55.9513 | 56.0833 | 55.9354 | -67.7017 | 67.393 | -56.0148 | 67.4022 | 67.4248 | 0.031752 | -56.0757 | -55.8883 | -0.27769 | -0.12017 | 123.4364 | 120.6455 | 120.9232 | 0.011801 | -0.13609 | 67.4807 | 67.4198 | 67.6072 | 67.4529 | -56.1025 | 123.3753 | 123.5073 | 123.3594 | 89.3564 | -123.7732
1628.2812 | 123.6465 | -67.3828 | 56.0303 | 0.06235 | -0.096404 | -0.044339 | -0.075819 | -0.045037 | -0.054231 | 0.095999 | 0.038873 | -0.019282 | 0.061668 | 0.29608 | 0.04707 | -0.026423 | 0.0243 | -0.003831 | 0.038393 | 0.000359 | 0.18775 | -0.035584 | 56.0261 | 22.1201 | 53.281 | 55.9513 | 56.0879 | 55.9262 | -67.7109 | 67.3472 | -55.9919 | 67.3564 | 67.379 | 0.031753 | -56.0299 | -55.8425 | -0.32805 | -0.078967 | 123.409 | 120.6639 | 120.9919 | 0.057579 | -0.10405 | 67.4212 | 67.3832 | 67.5706 | 67.4071 | -56.0659 | 123.3341 | 123.4707 | 123.309 | 89.5029 | -123.7411
1629.2656 | 123.5962 | -67.4194 | 56.0303 | 0.047088 | -0.095336 | -0.045407 | -0.075819 | -0.043968 | -0.052095 | 0.080738 | 0.037805 | -0.02035 | 0.062737 | 0.29608 | 0.046001 | -0.012688 | 0.019721 | -0.003831 | 0.033814 | -0.00422 | 0.20607 | -0.040163 | 56.0124 | 22.0514 | 53.3635 | 55.9376 | 56.0695 | 55.9262 | -67.7063 | 67.3793 | -55.9965 | 67.4067 | 67.4156 | 0.036332 | -56.0345 | -55.8242 | -0.28685 | -0.092702 | 123.4318 | 120.7829 | 121.0697 | 0.039264 | -0.10405 | 67.4532 | 67.4152 | 67.6255 | 67.4392 | -56.0704 | 123.357 | 123.489 | 123.3457 | 89.4709 | -123.7366
1630.2656 | 123.6191 | -61.6608 | 61.8164 | 0.047088 | -0.096404 | -0.047544 | -0.074751 | -0.045037 | -0.053163 | 0.065477 | 0.027123 | -0.042784 | -0.10498 | 0.21596 | -0.042665 | -0.017266 | 0.015142 | 0.000747 | 0.056706 | -0.00422 | 0.19691 | -0.040163 | 2.6384 | 0.83826 | 2.4207 | 2.6805 | 2.9257 | 2.6908 | -3.4701 | 61.6206 | -61.7597 | 61.6435 | 61.6615 | 0.04091 | -61.8206 | -61.6195 | 58.1907 | -59.1359 | 64.2992 | 64.0815 | 5.8908 | -58.8907 | -59.1256 | 61.7175 | 61.6565 | 61.8577 | 61.6759 | -61.8566 | 64.3413 | 64.5865 | 64.3516 | 62.499 | -65.2865
1631.2656 | 123.5596 | -61.6791 | 61.7889 | 0.047088 | -0.099609 | -0.046475 | -0.075819 | -0.0429 | -0.052095 | 0.050216 | -0.0059907 | -0.043852 | -0.11352 | 0.21275 | -0.077917 | -0.021844 | 0.019721 | 0.000747 | 0.061284 | 0.004938 | 0.18775 | -0.040163 | 0.051413 | 0.023253 | 0.007751 | 0.16234 | 0.27926 | 0.28704 | -0.27862 | 61.6389 | -61.7277 | 61.6572 | 61.6798 | 0.04091 | -61.784 | -61.6012 | 61.4005 | -61.6266 | 61.7305 | 61.6868 | 0.28637 | -61.5097 | -61.5019 | 61.7404 | 61.684 | 61.8668 | 61.6988 | -61.8291 | 61.8414 | 61.9583 | 61.9661 | 61.7023 | -62.0676
1632.2656 | 123.5916 | -61.6791 | 61.821 | 0.031826 | -0.099609 | -0.047544 | -0.074751 | -0.0429 | -0.052095 | 0.050216 | -0.0070587 | -0.044921 | -0.11245 | 0.21275 | -0.080054 | -0.012688 | 0.0243 | 0.000747 | 0.047549 | -0.008799 | 0.18775 | -0.035584 | 0.037677 | 0.018674 | -0.015143 | 0.13487 | 0.25637 | 0.26415 | -0.2603 | 61.6435 | -61.7734 | 61.6664 | 61.6798 | 0.036331 | -61.8298 | -61.6332 | 61.4188 | -61.6861 | 61.7168 | 61.6639 | 0.24516 | -61.5646 | -61.5568 | 61.7266 | 61.6703 | 61.8668 | 61.7034 | -61.8566 | 61.8139 | 61.9354 | 61.9432 | 61.6978 | -62.0813
1633.2812 | 123.674 | -61.615 | 61.7798 | 0.047088 | -0.098541 | -0.045407 | -0.077956 | -0.041832 | -0.052095 | 0.095999 | -0.0059907 | -0.043852 | -0.11245 | 0.21382 | -0.077917 | -0.017266 | 0.019721 | -0.003831 | 0.065863 | 0.000359 | 0.19233 | -0.040163 | 0.02852 | 0.027831 | -0.019721 | 0.13029 | 0.24264 | 0.25957 | -0.26488 | 61.5748 | -61.7139 | 61.5977 | 61.6112 | 0.036332 | -61.7794 | -61.5875 | 61.3501 | -61.6495 | 61.6435 | 61.5953 | 0.24516 | -61.5371 | -61.5202 | 61.6809 | 61.6153 | 61.8073 | 61.6347 | -61.8199 | 61.7453 | 61.8576 | 61.8746 | 61.6428 | -62.0447
1634.2656 | 123.6191 | -61.6653 | 61.8256 | 0.047088 | -0.098541 | -0.045407 | -0.074751 | -0.043968 | -0.051026 | 0.034955 | -0.0070587 | -0.043852 | -0.11139 | 0.21275 | -0.078986 | -0.021844 | 0.0243 | -0.003831 | 0.042971 | -0.00422 | 0.19691 | -0.035584 | 0.02852 | 0.004938 | -0.019721 | 0.12114 | 0.24721 | 0.26415 | -0.2603 | 61.6298 | -61.7826 | 61.6435 | 61.6615 | 0.031753 | -61.8298 | -61.6287 | 61.405 | -61.7044 | 61.6939 | 61.6456 | 0.24058 | -61.5783 | -61.5614 | 61.7083 | 61.6611 | 61.8623 | 61.6896 | -61.8611 | 61.7865 | 61.9126 | 61.9295 | 61.6703 | -62.0859
1635.2656 | 123.6145 | -61.647 | 61.8118 | 0.047088 | -0.099609 | -0.044339 | -0.077956 | -0.043968 | -0.052095 | 0.080738 | -0.0059907 | -0.042784 | -0.11139 | 0.21382 | -0.076849 | -0.026423 | 0.0243 | -0.008409 | 0.047549 | -0.00422 | 0.18775 | -0.040163 | 0.019362 | 0.004938 | -0.019721 | 0.12571 | 0.24721 | 0.25957 | -0.2603 | 61.6069 | -61.7643 | 61.6206 | 61.6386 | 0.031754 | -61.816 | -61.6241 | 61.3867 | -61.6861 | 61.6664 | 61.6273 | 0.24058 | -61.5646 | -61.5523 | 61.6946 | 61.6428 | 61.8348 | 61.6713 | -61.852 | 61.7727 | 61.8942 | 61.9066 | 61.652 | -62.0721
1636.2656 | 123.6557 | -61.6516 | 61.821 | 0.06235 | -0.098541 | -0.045407 | -0.075819 | -0.043968 | -0.052095 | 0.080738 | -0.0081267 | -0.043852 | -0.11139 | 0.21275 | -0.077917 | -0.017266 | 0.019721 | 0.000747 | 0.052128 | -0.008799 | 0.1786 | -0.044742 | 0.019362 | 0.009516 | -0.019721 | 0.12114 | 0.23806 | 0.25042 | -0.2603 | 61.6069 | -61.7689 | 61.6343 | 61.6524 | 0.045489 | -61.8298 | -61.6424 | 61.3913 | -61.6998 | 61.671 | 61.6319 | 0.24058 | -61.5829 | -61.5706 | 61.7037 | 61.6428 | 61.8302 | 61.6713 | -61.8657 | 61.7727 | 61.8897 | 61.902 | 61.6611 | -62.0813
1637.2656 | 123.6511 | -61.647 | 61.8164 | 0.047088 | -0.10068 | -0.046475 | -0.076888 | -0.043968 | -0.052095 | 0.080738 | -0.0070587 | -0.043852 | -0.11245 | 0.21275 | -0.077917 | -0.017266 | 0.0243 | -0.008409 | 0.047549 | -0.008799 | 0.1786 | -0.031005 | 0.014784 | 0.009516 | -0.028879 | 0.11656 | 0.23348 | -0.11587 | -0.26946 | 61.616 | -61.7689 | 61.6298 | 61.6386 | 0.022596 | -61.8252 | -61.6378 | 61.3776 | -61.6998 | 61.6618 | 61.6182 | 0.24058 | -61.5829 | -61.9323 | 61.6946 | 61.6382 | 61.8256 | 61.6713 | -61.8474 | 61.7636 | 61.8805 | 61.5312 | 61.6565 | -62.0859
1638.2812 | 123.6649 | -61.6287 | 61.7844 | 0.06235 | -0.097472 | -0.047544 | -0.075819 | -0.046105 | -0.052095 | 0.050216 | -0.0049217 | -0.044921 | -0.11245 | 0.21168 | -0.076849 | -0.021844 | 0.0243 | 0.005325 | 0.047549 | -0.00422 | 0.19691 | -0.035584 | 0.019362 | 0.004938 | -0.028879 | 0.12114 | 0.23806 | -0.12045 | -0.26488 | 61.5931 | -61.7368 | 61.6069 | 61.634 | 0.040909 | -61.7886 | -61.5875 | 61.3638 | -61.6632 | 61.6481 | 61.5998 | 0.236 | -61.5463 | -61.9048 | 61.6763 | 61.6245 | 61.8256 | 61.653 | -61.8199 | 61.7499 | 61.8668 | 61.5083 | 61.6337 | -62.0492
1639.2656 | 123.642 | -61.6608 | 61.8256 | 0.06235 | -0.10068 | -0.046475 | -0.075819 | -0.045037 | -0.053163 | 0.065477 | -0.0049217 | -0.043852 | -0.11139 | 0.21275 | -0.080054 | -0.021844 | 0.028878 | -0.003831 | 0.033814 | 0.000359 | 0.19233 | -0.040163 | 0.014784 | 0.014095 | -0.0243 | 0.11198 | 0.23348 | -0.11587 | -0.2603 | 61.6206 | -61.7917 | 61.6389 | 61.6569 | 0.036332 | -61.8252 | -61.6332 | 61.4005 | -61.7136 | 61.6756 | 61.6365 | 0.236 | -61.5921 | -61.9414 | 61.6946 | 61.6611 | 61.8531 | 61.6896 | -61.8657 | 61.7727 | 61.8942 | 61.5449 | 61.6749 | -62.0859
1640.2656 | 123.6465 | -61.6379 | 61.8393 | 0.06235 | -0.098541 | -0.046475 | -0.074751 | -0.0429 | -0.053163 | 0.065477 | -0.0038537 | -0.042784 | -0.11352 | 0.21382 | -0.078986 | -0.017266 | 0.028878 | -0.008409 | 0.052128 | -0.008799 | 0.18317 | -0.040163 | 0.019362 | 0.009516 | -0.028879 | 0.11656 | 0.23348 | -0.12045 | -0.2603 | 61.5977 | -61.7872 | 61.6206 | 61.6295 | 0.031754 | -61.8481 | -61.6561 | 61.3776 | -61.7227 | 61.6572 | 61.609 | 0.23142 | -61.6058 | -61.9597 | 61.69 | 61.6291 | 61.8211 | 61.6668 | -61.8795 | 61.7544 | 61.8714 | 61.5174 | 61.6474 | -62.0996
1641.2656 | 123.642 | -61.6608 | 61.7889 | 0.031826 | -0.099609 | -0.046475 | -0.074751 | -0.043968 | -0.051026 | 0.065477 | -0.0049217 | -0.042784 | -0.11245 | 0.21275 | -0.077917 | -0.026423 | 0.0243 | -0.003831 | 0.052128 | -0.00422 | 0.17402 | -0.040163 | 0.019362 | 0.014095 | -0.028879 | 0.11198 | 0.23806 | -0.11587 | -0.2603 | 61.6206 | -61.7368 | 61.6343 | 61.6569 | 0.036332 | -61.7932 | -61.6149 | 61.4005 | -61.677 | 61.6801 | 61.6319 | 0.23142 | -61.5509 | -61.9048 | 61.7129 | 61.6565 | 61.8348 | 61.6851 | -61.8291 | 61.7727 | 61.8988 | 61.5449 | 61.6749 | -62.0492
1642.2656 | 123.6465 | -61.6699 | 61.8393 | 0.047088 | -0.10068 | -0.047544 | -0.076888 | -0.046105 | -0.052095 | 0.065477 | -0.0049217 | -0.043852 | -0.11352 | 0.21275 | -0.076849 | -0.021844 | 0.015142 | -0.008409 | 0.038393 | 0.000359 | 0.18317 | -0.044742 | 0.010205 | 0.014095 | -0.033458 | 0.10282 | 0.2289 | -0.11587 | -0.26946 | 61.6252 | -61.8009 | 61.6481 | 61.6615 | 0.036333 | -61.8389 | -61.6561 | 61.4005 | -61.7365 | 61.6801 | 61.6365 | 0.236 | -61.6104 | -61.9552 | 61.7083 | 61.6703 | 61.8531 | 61.6851 | -61.884 | 61.7727 | 61.8988 | 61.554 | 61.684 | -62.1088
1643.2812 | 123.6832 | -61.6699 | 61.7844 | 0.047088 | -0.10068 | -0.046475 | -0.077956 | -0.043968 | -0.052095 | 0.065477 | -0.0038537 | -0.043852 | -0.11245 | 0.21382 | -0.077917 | -0.021844 | 0.015142 | 0.000747 | 0.042971 | -0.00422 | 0.19691 | -0.035584 | 0.014784 | 0.009516 | -0.028879 | 0.1074 | 0.23348 | -0.12045 | -0.26488 | 61.6343 | -61.7414 | 61.6481 | 61.6707 | 0.036331 | -61.7886 | -61.5875 | 61.405 | -61.677 | 61.6847 | 61.641 | 0.236 | -61.5509 | -61.9048 | 61.7129 | 61.6657 | 61.8668 | 61.6851 | -61.8199 | 61.7773 | 61.9034 | 61.5495 | 61.6794 | -62.0492
1644.2656 | 123.6282 | -61.6562 | 61.8439 | 0.06235 | -0.10068 | -0.047544 | -0.075819 | -0.045037 | -0.052095 | 0.065477 | -0.0070587 | -0.043852 | -0.11245 | 0.21382 | -0.078986 | -0.021844 | 0.019721 | -0.008409 | 0.070441 | -0.00422 | 0.19691 | -0.040163 | 0.005626 | 0.014095 | -0.033458 | 0.11198 | 0.23348 | -0.12045 | -0.2603 | 61.616 | -61.7734 | 61.6343 | 61.6478 | 0.031754 | -61.8481 | -61.647 | 61.3959 | -61.7319 | 61.6618 | 61.6227 | 0.22685 | -61.6104 | -61.9643 | 61.7266 | 61.652 | 61.8531 | 61.6759 | -61.884 | 61.7682 | 61.8897 | 61.5357 | 61.6703 | -62.1042
1645.2656 | 123.6511 | -61.6425 | 61.8164 | 0.06235 | -0.099609 | -0.046475 | -0.076888 | -0.045037 | -0.052095 | 0.095999 | -0.0038537 | -0.042784 | -0.11352 | 0.21275 | -0.077917 | -0.017266 | 0.019721 | 0.000747 | 0.052128 | -0.00422 | 0.18775 | -0.044742 | 0.005626 | 0.018674 | -0.038036 | 0.11198 | 0.23348 | -0.11587 | -0.25115 | 61.5977 | -61.7643 | 61.6252 | 61.6432 | 0.045489 | -61.8206 | -61.6287 | 61.3913 | -61.7044 | 61.6481 | 61.6044 | 0.21311 | -61.5829 | -61.9323 | 61.6946 | 61.6382 | 61.8302 | 61.6622 | -61.8611 | 61.7544 | 61.8759 | 61.5266 | 61.6611 | -62.0676
1646.2656 | 123.6649 | -61.6562 | 61.8301 | 0.031826 | -0.10068 | -0.047544 | -0.075819 | -0.045037 | -0.052095 | 0.080738 | -0.0038537 | -0.042784 | -0.11245 | 0.21596 | -0.076849 | -0.021844 | 0.015142 | -0.003831 | 0.056706 | -0.008799 | 0.20607 | -0.040163 | 0.010205 | 0.009516 | -0.033458 | 0.1074 | 0.23348 | -0.12045 | -0.25572 | 61.616 | -61.7734 | 61.6343 | 61.6524 | 0.036332 | -61.8389 | -61.6241 | 61.4005 | -61.7227 | 61.6664 | 61.6227 | 0.22227 | -61.5967 | -61.9506 | 61.7129 | 61.6474 | 61.8623 | 61.6713 | -61.8703 | 61.7636 | 61.8897 | 61.5357 | 61.6657 | -62.0859
1647.2656 | 123.642 | -61.647 | 61.853 | 0.031826 | -0.10068 | -0.047544 | -0.075819 | -0.0429 | -0.051026 | 0.080738 | -0.0049217 | -0.044921 | -0.11245 | 0.21382 | -0.076849 | -0.021844 | 0.0243 | 0.000747 | 0.042971 | -0.008799 | 0.18775 | -0.031005 | 0.010205 | 0.018674 | -0.028879 | 0.098244 | 0.2289 | -0.12503 | -0.25572 | 61.616 | -61.8101 | 61.6252 | 61.6478 | 0.031752 | -61.8618 | -61.6653 | 61.3913 | -61.7548 | 61.6572 | 61.6182 | 0.22685 | -61.6241 | -61.9781 | 61.69 | 61.6382 | 61.8348 | 61.6713 | -61.884 | 61.7453 | 61.8759 | 61.522 | 61.6657 | -62.1088
1648.2812 | 123.5962 | -61.6699 | 61.8393 | 0.031826 | -0.10068 | -0.046475 | -0.076888 | -0.043968 | -0.053163 | 0.034955 | -0.0049217 | -0.041716 | -0.11245 | 0.21489 | -0.077917 | -0.008109 | 0.0243 | 0.005325 | 0.024657 | 0.000359 | 0.19691 | -0.040163 | 0.014784 | 0.004938 | -0.038036 | 0.10282 | 0.2289 | -0.12045 | -0.25115 | 61.6298 | -61.8146 | 61.6618 | 61.6752 | 0.045488 | -61.8389 | -61.6424 | 61.4188 | -61.7365 | 61.6847 | 61.6319 | 0.21311 | -61.6104 | -61.9597 | 61.6946 | 61.6703 | 61.8668 | 61.6942 | -61.8795 | 61.7727 | 61.8988 | 61.5495 | 61.6749 | -62.0904
1649.2656 | 123.6282 | -61.647 | 61.8484 | 0.047088 | -0.099609 | -0.046475 | -0.075819 | -0.043968 | -0.052095 | 0.065477 | -0.0059907 | -0.042784 | -0.11245 | 0.21489 | -0.076849 | -0.031001 | 0.019721 | -0.003831 | 0.042971 | 0.000359 | 0.19691 | -0.040163 | 0.010205 | 0.009516 | -0.033458 | 0.098244 | 0.23348 | -0.11587 | -0.26488 | 61.6069 | -61.8055 | 61.616 | 61.6432 | 0.036332 | -61.8481 | -61.6515 | 61.3822 | -61.7502 | 61.6572 | 61.6136 | 0.23142 | -61.615 | -61.9643 | 61.69 | 61.6474 | 61.8439 | 61.6668 | -61.8886 | 61.7453 | 61.8805 | 61.5312 | 61.6565 | -62.1133
1650.3281 | 123.6832 | -61.6562 | 61.7798 | 0.031826 | -0.10175 | -0.045407 | -0.076888 | -0.043968 | -0.052095 | 0.050216 | -0.0059907 | -0.043852 | -0.11245 | 0.21489 | -0.078986 | -0.021844 | 0.0243 | -0.012988 | 0.070441 | -0.008799 | 0.18775 | -0.035584 | 0.010205 | 0.004938 | -0.038036 | 0.098244 | 0.22432 | -0.11587 | -0.25115 | 61.6206 | -61.7093 | 61.6343 | 61.6432 | 0.022596 | -61.7886 | -61.592 | 61.405 | -61.6815 | 61.6664 | 61.6182 | 0.21311 | -61.5555 | -61.8957 | 61.7266 | 61.6474 | 61.8439 | 61.6805 | -61.8154 | 61.7544 | 61.8805 | 61.5403 | 61.6611 | -62.0309
1651.2656 | 123.6145 | -61.6791 | 61.853 | 0.06235 | -0.10175 | -0.046475 | -0.076888 | -0.041832 | -0.052095 | 0.095999 | -0.0038537 | -0.042784 | -0.11245 | 0.21382 | -0.077917 | -0.026423 | 0.019721 | -0.003831 | 0.047549 | -0.00422 | 0.18317 | -0.040163 | 0.010205 | 0.004938 | -0.033458 | 0.10282 | 0.22432 | -0.11587 | -0.25572 | 61.6389 | -61.8055 | 61.6527 | 61.6752 | 0.036332 | -61.8572 | -61.6699 | 61.4234 | -61.7502 | 61.6893 | 61.6456 | 0.22227 | -61.6287 | -61.9689 | 61.7266 | 61.6749 | 61.8622 | 61.6988 | -61.8932 | 61.7819 | 61.9034 | 61.5632 | 61.684 | -62.1088
1652.2656 | 123.642 | -61.6882 | 61.821 | 0.06235 | -0.10175 | -0.046475 | -0.077956 | -0.043968 | -0.053163 | 0.080738 | -0.0059907 | -0.042784 | -0.11139 | 0.21382 | -0.078986 | -0.017266 | 0.015142 | -0.008409 | 0.052128 | 0.000359 | 0.1786 | -0.040163 | 0.010205 | 0.004938 | -0.033458 | 0.098244 | 0.21516 | -0.12045 | -0.2603 | 61.6481 | -61.7689 | 61.671 | 61.6798 | 0.031754 | -61.8206 | -61.6424 | 61.4279 | -61.7227 | 61.6984 | 61.6548 | 0.22685 | -61.6058 | -61.9414 | 61.7404 | 61.6886 | 61.8668 | 61.7034 | -61.8611 | 61.7865 | 61.9034 | 61.5678 | 61.6932 | -62.0813
1653.2812 | 123.6145 | -61.6837 | 61.8301 | 0.06235 | -0.10175 | -0.047544 | -0.077956 | -0.043968 | -0.053163 | 0.034955 | -0.0049217 | -0.044921 | -0.11459 | 0.21702 | -0.077917 | -0.021844 | 0.0243 | -0.003831 | 0.052128 | 0.000359 | 0.20607 | -0.031005 | 0.014784 | 0.014095 | -0.028879 | 0.098244 | 0.22432 | -0.12503 | -0.25572 | 61.6527 | -61.778 | 61.6618 | 61.6798 | 0.027174 | -61.8298 | -61.6241 | 61.4279 | -61.7319 | 61.6984 | 61.6548 | 0.22685 | -61.6058 | -61.9552 | 61.7358 | 61.684 | 61.8897 | 61.708 | -61.8611 | 61.7819 | 61.908 | 61.5586 | 61.6977 | -62.0859
1654.2656 | 123.6374 | -61.6745 | 61.8576 | 0.077612 | -0.10068 | -0.046475 | -0.076888 | -0.043968 | -0.053163 | 0.065477 | -0.0038537 | -0.044921 | -0.11139 | 0.21275 | -0.077917 | -0.017266 | 0.028878 | 0.000747 | 0.061284 | 0.000359 | 0.19233 | -0.035584 | 0.005626 | 0.014095 | -0.042615 | 0.10282 | 0.21974 | -0.11587 | -0.2603 | 61.6389 | -61.7963 | 61.6572 | 61.6752 | 0.036331 | -61.8572 | -61.6653 | 61.4142 | -61.7548 | 61.6801 | 61.6319 | 0.21769 | -61.6379 | -61.9735 | 61.7358 | 61.6749 | 61.8668 | 61.7034 | -61.8932 | 61.7773 | 61.8942 | 61.5586 | 61.6886 | -62.1179
1655.2656 | 123.6603 | -61.6653 | 61.8576 | 0.047088 | -0.099609 | -0.047544 | -0.076888 | -0.0429 | -0.053163 | 0.065477 | -0.0038537 | -0.042784 | -0.11459 | 0.21702 | -0.077917 | -0.021844 | 0.0243 | -0.003831 | 0.052128 | -0.00422 | 0.1786 | -0.040163 | 0.005626 | 0.014095 | -0.028879 | 0.098244 | 0.2289 | -0.12503 | -0.2603 | 61.6252 | -61.8055 | 61.6435 | 61.6615 | 0.036332 | -61.8618 | -61.679 | 61.405 | -61.7594 | 61.671 | 61.6365 | 0.23142 | -61.6287 | -61.9826 | 61.7175 | 61.6611 | 61.8439 | 61.6896 | -61.8978 | 61.7636 | 61.8942 | 61.5403 | 61.6794 | -62.1179
1656.2656 | 123.7381 | -61.6287 | 61.8118 | 0.047088 | -0.10175 | -0.047544 | -0.075819 | -0.045037 | -0.052095 | 0.050216 | -0.0038537 | -0.043852 | -0.11245 | 0.21275 | -0.076849 | -0.012688 | 0.019721 | -0.008409 | 0.047549 | -0.013378 | 0.20607 | -0.035584 | 0.005626 | 0.009516 | -0.028879 | 0.10282 | 0.21516 | -0.12045 | -0.26488 | 61.5931 | -61.7643 | 61.616 | 61.6203 | 0.027175 | -61.8252 | -61.6058 | 61.3638 | -61.709 | 61.6343 | 61.5998 | 0.236 | -61.5967 | -61.9323 | 61.6763 | 61.6153 | 61.8348 | 61.6484 | -61.8474 | 61.7315 | 61.8439 | 61.5083 | 61.6382 | -62.0767
1657.2656 | 123.7564 | -61.6333 | 61.821 | 0.016564 | -0.10068 | -0.048612 | -0.077956 | -0.045037 | -0.051026 | 0.065477 | -0.0038537 | -0.041716 | -0.11139 | 0.21275 | -0.080054 | -0.021844 | 0.028878 | 0.000747 | 0.024657 | -0.095798 | 0.16944 | 0.11552 | 0.010205 | 0.004938 | -0.038036 | 0.093665 | 0.21516 | -0.1525 | -0.2603 | 61.7488 | -61.7963 | 61.6115 | 61.634 | -0.11477 | -61.9168 | -61.6515 | 61.373 | -61.7273 | 61.6435 | 61.5953 | 0.22227 | -61.6058 | -61.9735 | 61.658 | 61.5375 | 61.8027 | 61.6622 | -61.7055 | 61.727 | 61.8485 | 61.4808 | 61.6382 | -62.0813
1658.2656 | 123.642 | -61.6425 | 61.853 | 0.047088 | -0.099609 | -0.049681 | -0.076888 | -0.0429 | -0.052095 | 0.050216 | -0.0038537 | -0.041716 | -0.11245 | 0.21382 | -0.076849 | -0.017266 | 0.019721 | -0.003831 | 0.006344 | -0.11411 | 0.12823 | 0.15673 | 0.010205 | 0.009516 | -0.038036 | 0.093665 | 0.21516 | -0.16624 | -0.2603 | 61.7992 | -61.8467 | 61.6252 | 61.6386 | -0.16056 | -61.9671 | -61.7248 | 61.3822 | -61.7594 | 61.6527 | 61.6044 | 0.22227 | -61.6379 | -62.0193 | 61.6488 | 61.5283 | 61.7707 | 61.6622 | -61.6963 | 61.7361 | 61.8576 | 61.4762 | 61.652 | -62.1133
1659.2656 | 123.6694 | -61.6333 | 61.8576 | 0.06235 | -0.10068 | -0.047544 | -0.075819 | -0.043968 | -0.051026 | 0.065477 | -0.0049217 | -0.042784 | -0.11032 | 0.21596 | -0.077917 | -0.021844 | 0.019721 | 0.005325 | 0.084176 | -0.11411 | 0.12365 | 0.16131 | 0.005626 | 0.014095 | -0.042615 | 0.10282 | 0.21974 | -0.17539 | -0.2603 | 61.7946 | -61.7734 | 61.6115 | 61.6386 | -0.15599 | -61.9717 | -61.734 | 61.373 | -61.7548 | 61.6389 | 61.5907 | 0.21769 | -61.6379 | -62.033 | 61.7175 | 61.5192 | 61.757 | 61.653 | -61.6963 | 61.7361 | 61.853 | 61.4579 | 61.6474 | -62.1179
1660.2656 | 123.7015 | -61.6562 | 61.8439 | 0.031826 | -0.10068 | -0.048612 | -0.076888 | -0.043968 | -0.051026 | 0.050216 | -0.0049217 | -0.042784 | -0.11139 | 0.21382 | -0.077917 | -0.031001 | 0.019721 | -0.003831 | 0.088755 | -0.10496 | 0.10076 | 0.15673 | 0.001048 | 0.009516 | -0.033458 | 0.093665 | 0.22432 | -0.17081 | -0.25572 | 61.8129 | -61.7551 | 61.6252 | 61.6524 | -0.16056 | -61.9488 | -61.7431 | 61.4005 | -61.7502 | 61.6572 | 61.6227 | 0.22227 | -61.6195 | -62.0147 | 61.7449 | 61.5512 | 61.7569 | 61.6759 | -61.6871 | 61.7499 | 61.8805 | 61.4854 | 61.6657 | -62.0996
1661.2656 | 123.7335 | -61.6287 | 61.8118 | 0.06235 | -0.10175 | -0.048612 | -0.076888 | -0.0429 | -0.051026 | 0.065477 | -0.0049217 | -0.042784 | -0.11352 | 0.21489 | -0.078986 | -0.017266 | 0.0243 | -0.003831 | 0.084176 | -0.10953 | 0.087023 | 0.16589 | 0.005626 | 0.018674 | -0.042615 | 0.098244 | 0.21516 | -0.16624 | -0.25572 | 61.7946 | -61.7277 | 61.6115 | 61.6249 | -0.16972 | -61.9214 | -61.7248 | 61.373 | -61.7136 | 61.6343 | 61.5861 | 0.21311 | -61.5967 | -61.9781 | 61.7129 | 61.5192 | 61.7157 | 61.653 | -61.6459 | 61.727 | 61.8439 | 61.4625 | 61.6474 | -62.0676
1662.2656 | 123.7518 | -61.615 | 61.8347 | 0.047088 | -0.10068 | -0.048612 | -0.074751 | -0.045037 | -0.049958 | 0.065477 | -0.0049217 | -0.042784 | -0.11245 | 0.21382 | -0.076849 | -0.021844 | 0.0243 | -0.003831 | 0.084176 | -0.11411 | 0.12365 | 0.15215 | 0.005626 | 0.004938 | -0.047194 | 0.093665 | 0.22432 | -0.17081 | -0.25572 | 61.7671 | -61.7505 | 61.5931 | 61.6112 | -0.15598 | -61.9488 | -61.7111 | 61.3593 | -61.7411 | 61.6206 | 61.5678 | 0.20853 | -61.6104 | -62.0055 | 61.6992 | 61.5009 | 61.7386 | 61.6393 | -61.6826 | 61.7087 | 61.8393 | 61.4442 | 61.6199 | -62.0904
1663.2812 | 123.6694 | -61.6882 | 61.8484 | 0.077612 | -0.10068 | -0.047544 | -0.076888 | -0.045037 | -0.051026 | 0.050216 | -0.0049217 | -0.042784 | -0.11245 | 0.21489 | -0.077917 | -0.021844 | 0.019721 | -0.003831 | 0.088755 | -0.10953 | 0.09618 | 0.16131 | 0.005626 | 0.014095 | -0.033458 | 0.089087 | 0.22432 | -0.16624 | -0.25115 | 61.8495 | -61.7597 | 61.6664 | 61.6844 | -0.16514 | -61.958 | -61.7523 | 61.4371 | -61.7594 | 61.6939 | 61.6548 | 0.21769 | -61.6241 | -62.0147 | 61.777 | 61.5787 | 61.7844 | 61.708 | -61.6871 | 61.7773 | 61.9126 | 61.522 | 61.7023 | -62.0996
1664.2656 | 123.7564 | -61.6241 | 61.8347 | 0.047088 | -0.10068 | -0.050749 | -0.077956 | -0.043968 | -0.052095 | 0.065477 | -0.0017177 | -0.042784 | -0.11139 | 0.21596 | -0.077917 | -0.031001 | 0.015142 | -0.008409 | 0.088755 | -0.11869 | 0.10076 | 0.15673 | 0.010205 | 0.009516 | -0.033458 | 0.098244 | 0.21974 | -0.17081 | -0.2603 | 61.7809 | -61.746 | 61.5931 | 61.6157 | -0.16514 | -61.9534 | -61.734 | 61.3638 | -61.7365 | 61.6344 | 61.5907 | 0.22685 | -61.615 | -62.0055 | 61.7129 | 61.5055 | 61.7249 | 61.6393 | -61.678 | 61.7224 | 61.8439 | 61.4533 | 61.6337 | -62.095
1665.2656 | 123.7518 | -61.6333 | 61.853 | 0.047088 | -0.099609 | -0.046475 | -0.076888 | -0.043968 | -0.051026 | 0.065477 | -0.0038537 | -0.041716 | -0.11139 | 0.21596 | -0.078986 | -0.021844 | 0.010564 | 0.000747 | 0.07502 | -0.11411 | 0.11907 | 0.15673 | -0.00811 | 0.009516 | -0.038036 | 0.098244 | 0.21974 | -0.17081 | -0.26488 | 61.79 | -61.778 | 61.6115 | 61.634 | -0.15598 | -61.9671 | -61.734 | 61.3684 | -61.7548 | 61.6252 | 61.5953 | 0.22685 | -61.6333 | -62.0238 | 61.7083 | 61.5192 | 61.7524 | 61.6439 | -61.6963 | 61.7315 | 61.853 | 61.4625 | 61.6428 | -62.1179
1666.2656 | 123.7518 | -61.6287 | 61.8301 | 0.06235 | -0.10068 | -0.047544 | -0.077956 | -0.043968 | -0.051026 | 0.080738 | -0.0059907 | -0.041716 | -0.11352 | 0.21489 | -0.077917 | -0.017266 | 0.019721 | -0.008409 | 0.079598 | -0.11869 | 0.087023 | 0.15673 | -0.012689 | 0.009516 | -0.042615 | 0.093665 | 0.21974 | -0.17997 | -0.25115 | 61.7855 | -61.7505 | 61.6115 | 61.6203 | -0.16514 | -61.9488 | -61.7431 | 61.3776 | -61.7365 | 61.616 | 61.5861 | 0.20853 | -61.6104 | -62.0101 | 61.7083 | 61.51 | 61.7157 | 61.6484 | -61.6734 | 61.7224 | 61.8485 | 61.4488 | 61.6382 | -62.0813

## Thermal Data
Fire Time | South 11 C | Cable 1 | Cable 2
-0.9646 | 22.8582 | 21.5611 | 21.7449
0.0354 | 22.8493 | 21.56 | 21.7422
1.0354 | 22.8553 | 21.5613 | 21.7399
2.0354 | 22.8652 | 21.5625 | 21.7399
3.0354 | 23.0214 | 21.5646 | 21.7373
4.0354 | 23.6815 | 21.5585 | 21.743
5.0354 | 24.9172 | 21.5566 | 21.7412
6.0354 | 26.7465 | 21.5551 | 21.7435
7.0354 | 29.092 | 21.5626 | 21.7415
8.0354 | 31.8433 | 21.5622 | 21.7477
9.0354 | 34.9603 | 21.5687 | 21.7514
10.0354 | 38.3917 | 21.556 | 21.7604
11.0354 | 42.1084 | 21.5718 | 21.7709
12.0354 | 46.0523 | 21.591 | 21.7803
13.0354 | 50.2331 | 21.6094 | 21.7987
14.0354 | 54.6115 | 21.6192 | 21.8144
15.0354 | 59.1707 | 21.6415 | 21.8517
16.0354 | 63.8705 | 21.6694 | 21.8817
17.0354 | 68.6972 | 21.702 | 21.914
18.0354 | 73.6728 | 21.7267 | 21.9463
19.0354 | 78.8012 | 21.7691 | 21.9977
20.0354 | 83.9997 | 21.8062 | 22.0502
21.0354 | 89.2642 | 21.8593 | 22.1087
22.0354 | 94.5829 | 21.9139 | 22.1724
23.0354 | 100.0336 | 21.9879 | 22.2452
24.0354 | 105.6059 | 22.0584 | 22.3225
25.0354 | 111.2673 | 22.1413 | 22.4064
26.0354 | 117.0172 | 22.2256 | 22.4967
27.0354 | 122.8175 | 22.3354 | 22.5983
28.0354 | 128.6947 | 22.4343 | 22.7076
29.0354 | 134.5634 | 22.5507 | 22.8313
30.0354 | 140.4399 | 22.6827 | 22.9538
31.0354 | 146.3427 | 22.8253 | 23.0922
32.0354 | 152.278 | 22.9841 | 23.2389
33.0354 | 158.2379 | 23.1422 | 23.4043
34.0354 | 164.1667 | 23.3125 | 23.5719
35.0354 | 170.0552 | 23.5041 | 23.7448
36.0354 | 175.997 | 23.6944 | 23.9342
37.0354 | 181.9126 | 23.9106 | 24.1404
38.0354 | 187.8469 | 24.1368 | 24.3562
39.0354 | 193.7561 | 24.3729 | 24.5792
40.0354 | 199.6882 | 24.6265 | 24.817
41.0354 | 205.5758 | 24.8873 | 25.0724
42.0354 | 211.4042 | 25.1798 | 25.3308
43.0354 | 217.2215 | 25.4782 | 25.6129
44.0354 | 223.1933 | 25.7915 | 25.8969
45.0354 | 229.0199 | 26.1336 | 26.1978
46.0354 | 234.8475 | 26.4694 | 26.5052
47.0354 | 240.709 | 26.8183 | 26.8365
48.0354 | 246.5186 | 27.1996 | 27.1786
49.0354 | 252.2835 | 27.6119 | 27.5557
50.0354 | 257.9794 | 28.0244 | 27.9338
51.0354 | 263.7009 | 28.4545 | 28.3343
52.0354 | 269.5592 | 28.8999 | 28.7527
53.0354 | 275.2596 | 29.3737 | 29.1892
54.0354 | 280.9196 | 29.853 | 29.6463
55.0354 | 286.3808 | 30.3563 | 30.1173
56.0354 | 291.3266 | 30.8873 | 30.5899
57.0354 | 295.9121 | 31.4349 | 31.0938
58.0354 | 300.1698 | 31.9992 | 31.6166
59.0354 | 304.1358 | 32.5679 | 32.1503
60.0354 | 307.9755 | 33.1604 | 32.6812
61.0354 | 311.6537 | 33.7643 | 33.2275
62.0354 | 315.0917 | 34.3854 | 33.7861
63.0354 | 318.423 | 35.0098 | 34.3632
64.0354 | 321.4958 | 35.6399 | 34.9455
65.0354 | 324.2587 | 36.2873 | 35.5347
66.0354 | 326.6613 | 36.9385 | 36.1333
67.0354 | 328.6352 | 37.5968 | 36.7412
68.0354 | 330.3156 | 38.2858 | 37.3564
69.0354 | 331.8282 | 38.9581 | 37.9737
70.0354 | 333.1693 | 39.6418 | 38.5862
71.0354 | 334.2384 | 40.3426 | 39.208
72.0354 | 335.1265 | 41.0516 | 39.825
73.0354 | 335.9452 | 41.7452 | 40.4381
74.0354 | 336.6556 | 42.4328 | 41.0726
75.0354 | 337.1301 | 43.1341 | 41.6854
76.0354 | 337.491 | 43.838 | 42.3026
77.0354 | 337.7047 | 44.5291 | 42.9167
78.0354 | 337.9224 | 45.219 | 43.527
79.0354 | 338.0434 | 45.9138 | 44.1492
80.0354 | 338.0332 | 46.5964 | 44.7506
81.0354 | 337.997 | 47.2941 | 45.3665
82.0354 | 337.9377 | 47.9716 | 45.9704
83.0354 | 337.7704 | 48.6748 | 46.5771
84.0354 | 337.5967 | 49.3402 | 47.1737
85.0354 | 337.3461 | 50.0245 | 47.7778
86.0354 | 337.0431 | 50.712 | 48.3774
87.0354 | 336.8028 | 51.3998 | 48.974
88.0354 | 336.6147 | 52.0706 | 49.5775
89.0354 | 336.3129 | 52.7385 | 50.1837
90.0354 | 335.9985 | 53.4159 | 50.7892
91.0354 | 335.6376 | 54.0836 | 51.3789
92.0354 | 335.2715 | 54.7379 | 51.9745
93.0354 | 334.8568 | 55.3986 | 52.5754
94.0354 | 334.3301 | 56.0554 | 53.1632
95.0354 | 333.8771 | 56.7096 | 53.753
96.0354 | 333.4114 | 57.3607 | 54.3438
97.0354 | 332.986 | 58.0114 | 54.9394
98.0354 | 332.5573 | 58.6405 | 55.5131
99.0354 | 332.0723 | 59.2807 | 56.0966
100.0354 | 331.5892 | 59.931 | 56.6762
101.0354 | 331.0408 | 60.5579 | 57.2602
102.0354 | 330.4968 | 61.1785 | 57.8391
103.0354 | 329.9556 | 61.7979 | 58.4068
104.0354 | 329.3725 | 62.4135 | 58.9727
105.0354 | 328.8279 | 63.0167 | 59.5439
106.0354 | 328.2982 | 63.6148 | 60.1148
107.0354 | 327.7699 | 64.2086 | 60.674
108.0354 | 327.2348 | 64.8031 | 61.2284
109.0354 | 326.7279 | 65.3775 | 61.7719
110.0354 | 326.2237 | 65.9625 | 62.3143
111.0354 | 325.7677 | 66.5389 | 62.8631
112.0354 | 325.2772 | 67.1115 | 63.4079
113.0354 | 324.748 | 67.6599 | 63.9311
114.0354 | 324.1718 | 68.2157 | 64.4682
115.0354 | 323.7019 | 68.7738 | 64.9814
116.0354 | 323.3104 | 69.3299 | 65.5073
117.0354 | 322.9662 | 69.8692 | 66.0235
118.0354 | 322.6919 | 70.4156 | 66.544
119.0354 | 322.4958 | 70.9578 | 67.0528
120.0354 | 322.23 | 71.4829 | 67.5597
121.0354 | 321.9727 | 72.0104 | 68.0627
122.0354 | 321.8809 | 72.5329 | 68.5638
123.0354 | 321.7699 | 73.0502 | 69.0621
124.0354 | 321.7209 | 73.5663 | 69.5677
125.0354 | 321.7022 | 74.0826 | 70.064
126.0354 | 321.7158 | 74.5892 | 70.5514
127.0354 | 321.7142 | 75.0908 | 71.0367
128.0354 | 321.7757 | 75.6041 | 71.5171
129.0354 | 321.9177 | 76.1076 | 72.0001
130.0354 | 322.133 | 76.6095 | 72.4826
131.0354 | 322.2705 | 77.1104 | 72.9689
132.0354 | 322.4838 | 77.6029 | 73.4535
133.0354 | 322.776 | 78.0918 | 73.929
134.0354 | 323.0762 | 78.5881 | 74.4072
135.0354 | 323.4727 | 79.0853 | 74.8857
136.0354 | 323.8022 | 79.5631 | 75.3614
137.0354 | 324.115 | 80.0484 | 75.8374
138.0354 | 324.3803 | 80.5418 | 76.3137
139.0354 | 324.6978 | 81.0209 | 76.795
140.0354 | 325.0644 | 81.5057 | 77.2601
141.0354 | 325.44 | 81.9915 | 77.7306
142.0354 | 325.8074 | 82.4658 | 78.2029
143.0354 | 326.1509 | 82.9393 | 78.6776
144.0354 | 326.5544 | 83.4204 | 79.1617
145.0354 | 326.8111 | 83.8893 | 79.6264
146.0354 | 327.1121 | 84.3696 | 80.094
147.0354 | 327.4178 | 84.8442 | 80.5645
148.0354 | 327.7602 | 85.322 | 81.0355
149.0354 | 328.039 | 85.7939 | 81.5066
150.0354 | 328.2962 | 86.2807 | 81.977
151.0354 | 328.6186 | 86.7472 | 82.4422
152.0354 | 328.8826 | 87.2251 | 82.9125
153.0354 | 329.0601 | 87.7006 | 83.3779
154.0354 | 329.2688 | 88.1893 | 83.852
155.0354 | 329.3811 | 88.6585 | 84.315
156.0354 | 329.5339 | 89.1272 | 84.7855
157.0354 | 329.6974 | 89.5908 | 85.2426
158.0354 | 329.7951 | 90.0577 | 85.7159
159.0354 | 329.9202 | 90.5375 | 86.1797
160.0354 | 330.0997 | 90.9946 | 86.6457
161.0354 | 330.2342 | 91.475 | 87.0952
162.0354 | 330.373 | 91.9313 | 87.5546
163.0354 | 330.4734 | 92.397 | 88.0211
164.0354 | 330.5559 | 92.8565 | 88.4816
165.0354 | 330.6752 | 93.3207 | 88.942
166.0354 | 330.6749 | 93.7787 | 89.3933
167.0354 | 330.7114 | 94.2416 | 89.8436
168.0354 | 330.7634 | 94.6873 | 90.2952
169.0354 | 330.7854 | 95.1576 | 90.7527
170.0354 | 330.8454 | 95.6071 | 91.1976
171.0354 | 330.9279 | 96.067 | 91.636
172.0354 | 330.8964 | 96.5091 | 92.0813
173.0354 | 330.878 | 96.9601 | 92.5304
174.0354 | 330.8549 | 97.418 | 92.9678
175.0354 | 330.8834 | 97.8737 | 93.4121
176.0354 | 330.9138 | 98.3218 | 93.8477
177.0354 | 330.8921 | 98.7627 | 94.2887
178.0354 | 330.9376 | 99.2008 | 94.7262
179.0354 | 330.8922 | 99.6397 | 95.1576
180.0354 | 330.7639 | 100.0891 | 95.594
181.0354 | 330.6974 | 100.5289 | 96.0311
182.0354 | 330.6729 | 100.9619 | 96.46
183.0354 | 330.6555 | 101.3885 | 96.8929
184.0354 | 330.5955 | 101.8276 | 97.3157
185.0354 | 330.4995 | 102.2731 | 97.7606
186.0354 | 330.4619 | 102.6991 | 98.1859
187.0354 | 330.3564 | 103.1313 | 98.6154
188.0354 | 330.2443 | 103.5637 | 99.0315
189.0354 | 330.1632 | 103.9882 | 99.4534
190.0354 | 330.1723 | 104.4055 | 99.8835
191.0354 | 330.143 | 104.8273 | 100.3075
192.0354 | 330.1006 | 105.2434 | 100.7156
193.0354 | 330.069 | 105.6683 | 101.1343
194.0354 | 330.0571 | 106.0827 | 101.5469
195.0354 | 330.0125 | 106.4958 | 101.9648
196.0354 | 330.0068 | 106.904 | 102.379
197.0354 | 329.9865 | 107.3275 | 102.7943
198.0354 | 329.8886 | 107.7405 | 103.1977
199.0354 | 329.8274 | 108.1426 | 103.6035
200.0354 | 329.7857 | 108.5481 | 104.0073
201.0354 | 329.7803 | 108.9562 | 104.4084
202.0354 | 329.7417 | 109.3565 | 104.8171
203.0354 | 329.7173 | 109.7497 | 105.2084
204.0354 | 329.6632 | 110.1594 | 105.6118
205.0354 | 329.6583 | 110.5477 | 106.0124
206.0354 | 329.6295 | 110.9289 | 106.4003
207.0354 | 329.5891 | 111.3269 | 106.8011
208.0354 | 329.5503 | 111.7162 | 107.1992
209.0354 | 329.5621 | 112.1047 | 107.5942
210.0354 | 329.5534 | 112.4888 | 107.9852
211.0354 | 329.5255 | 112.8647 | 108.3713
212.0354 | 329.5692 | 113.2479 | 108.7538
213.0354 | 329.6011 | 113.6309 | 109.1396
214.0354 | 329.6739 | 114.003 | 109.5145
215.0354 | 329.7326 | 114.3858 | 109.9005
216.0354 | 329.799 | 114.7589 | 110.2897
217.0354 | 329.8716 | 115.1363 | 110.6597
218.0354 | 329.9066 | 115.5144 | 111.0333
219.0354 | 329.9212 | 115.8854 | 111.4141
220.0354 | 329.9524 | 116.2496 | 111.7976
221.0354 | 329.9657 | 116.6297 | 112.1605
222.0354 | 329.9899 | 117.0008 | 112.5297
223.0354 | 330.0296 | 117.3578 | 112.9024
224.0354 | 330.0454 | 117.7134 | 113.2738
225.0354 | 330.0098 | 118.0879 | 113.6469
226.0354 | 329.9921 | 118.446 | 114.0113
227.0354 | 330.0048 | 118.8103 | 114.371
228.0354 | 330.076 | 119.1627 | 114.739
229.0354 | 330.1686 | 119.5174 | 115.1031
230.0354 | 330.2228 | 119.8743 | 115.4624
231.0354 | 330.2839 | 120.2206 | 115.8223
232.0354 | 330.3069 | 120.5677 | 116.1703
233.0354 | 330.293 | 120.9258 | 116.5399
234.0354 | 330.3068 | 121.2725 | 116.8939
235.0354 | 330.2672 | 121.6254 | 117.2583
236.0354 | 330.2938 | 121.9593 | 117.61
237.0354 | 330.2869 | 122.2993 | 117.9598
238.0354 | 330.3592 | 122.6436 | 118.3201
239.0354 | 330.3811 | 122.984 | 118.6688
240.0354 | 330.3861 | 123.3205 | 119.0189
241.0354 | 330.3887 | 123.6496 | 119.356
242.0354 | 330.4458 | 123.9902 | 119.7014
243.0354 | 330.5063 | 124.3147 | 120.0517
244.0354 | 330.4649 | 124.6424 | 120.3868
245.0354 | 330.4708 | 124.9696 | 120.7202
246.0354 | 330.4895 | 125.2931 | 121.0616
247.0354 | 330.5193 | 125.6124 | 121.3879
248.0354 | 330.5506 | 125.9451 | 121.7203
249.0354 | 330.5989 | 126.2693 | 122.0574
250.0354 | 330.6265 | 126.5835 | 122.391
251.0354 | 330.6113 | 126.8988 | 122.7149
252.0354 | 330.5928 | 127.1991 | 123.0416
253.0354 | 330.5896 | 127.4976 | 123.3752
254.0354 | 330.519 | 127.8155 | 123.7061
255.0354 | 330.5482 | 128.1192 | 124.0286
256.0354 | 330.5936 | 128.4213 | 124.3548
257.0354 | 330.5969 | 128.7077 | 124.6737
258.0354 | 330.5945 | 129.0139 | 125.0036
259.0354 | 330.5743 | 129.3088 | 125.3204
260.0354 | 330.5364 | 129.5966 | 125.644
261.0354 | 330.5311 | 129.8765 | 125.9626
262.0354 | 330.5257 | 130.1675 | 126.2858
263.0354 | 330.482 | 130.4604 | 126.5989
264.0354 | 330.5007 | 130.7469 | 126.9124
265.0354 | 330.529 | 131.0156 | 127.2241
266.0354 | 330.5079 | 131.3021 | 127.5253
267.0354 | 330.4794 | 131.5859 | 127.8298
268.0354 | 330.4425 | 131.8598 | 128.1118
269.0354 | 330.4251 | 132.1528 | 128.4106
270.0354 | 330.3544 | 132.4378 | 128.6953
271.0354 | 330.3085 | 132.7217 | 128.9842
272.0354 | 330.3076 | 133.012 | 129.2596
273.0354 | 330.2372 | 133.2993 | 129.526
274.0354 | 330.2097 | 133.5893 | 129.7998
275.0354 | 330.2746 | 133.8802 | 130.0651
276.0354 | 330.3 | 134.1715 | 130.3246
277.0354 | 330.2356 | 134.4744 | 130.5826
278.0354 | 330.1948 | 134.746 | 130.8383
279.0354 | 330.1966 | 135.0606 | 131.0875
280.0354 | 330.1375 | 135.3716 | 131.3439
281.0354 | 330.0763 | 135.687 | 131.6004
282.0354 | 330.0301 | 135.9955 | 131.8437
283.0354 | 329.9706 | 136.31 | 132.1057
284.0354 | 329.9721 | 136.6115 | 132.3503
285.0354 | 329.9635 | 136.9169 | 132.6066
286.0354 | 329.9418 | 137.2406 | 132.8511
287.0354 | 329.9772 | 137.5378 | 133.1072
288.0354 | 329.9684 | 137.8614 | 133.3549
289.0354 | 329.9374 | 138.1668 | 133.6112
290.0354 | 329.8959 | 138.4771 | 133.8707
291.0354 | 329.8402 | 138.7878 | 134.1228
292.0354 | 329.793 | 139.1117 | 134.3841
293.0354 | 329.7927 | 139.418 | 134.6614
294.0354 | 329.8103 | 139.7229 | 134.931
295.0354 | 329.8139 | 140.0465 | 135.2191
296.0354 | 329.8374 | 140.3601 | 135.4975
297.0354 | 329.8624 | 140.6718 | 135.8
298.0354 | 329.8689 | 140.991 | 136.097
299.0354 | 329.8888 | 141.2945 | 136.3897
300.0354 | 329.8399 | 141.622 | 136.6898
301.0354 | 329.8601 | 141.9298 | 136.9879
302.0354 | 329.8728 | 142.2602 | 137.293
303.0354 | 329.8534 | 142.568 | 137.6074
304.0354 | 329.8698 | 142.8928 | 137.9175
305.0354 | 329.8888 | 143.2119 | 138.2393
306.0354 | 329.8639 | 143.539 | 138.5504
307.0354 | 329.8393 | 143.8672 | 138.8682
308.0354 | 329.8238 | 144.1821 | 139.1974
309.0354 | 329.8123 | 144.5061 | 139.5131
310.0354 | 329.8014 | 144.8323 | 139.8379
311.0354 | 329.7692 | 145.1567 | 140.1641
312.0354 | 329.727 | 145.4903 | 140.4957
313.0354 | 329.7412 | 145.8127 | 140.8077
314.0354 | 329.7297 | 146.1303 | 141.1383
315.0354 | 329.7268 | 146.466 | 141.4775
316.0354 | 329.7595 | 146.7991 | 141.8153
317.0354 | 329.7304 | 147.1115 | 142.1497
318.0354 | 329.677 | 147.4339 | 142.4744
319.0354 | 329.6702 | 147.763 | 142.8089
320.0354 | 329.6509 | 148.0931 | 143.1383
321.0354 | 329.6558 | 148.4054 | 143.4665
322.0354 | 329.6637 | 148.7314 | 143.7922
323.0354 | 329.6608 | 149.0371 | 144.116
324.0354 | 329.6084 | 149.3767 | 144.4378
325.0354 | 329.6091 | 149.6981 | 144.7659
326.0354 | 329.6145 | 150.0176 | 145.0931
327.0354 | 329.611 | 150.3307 | 145.4171
328.0354 | 329.6368 | 150.6564 | 145.7497
329.0354 | 329.6857 | 150.9717 | 146.0733
330.0354 | 329.6941 | 151.2896 | 146.3918
331.0354 | 329.6854 | 151.6067 | 146.7076
332.0354 | 329.7269 | 151.9146 | 147.026
333.0354 | 329.7833 | 152.2424 | 147.3401
334.0354 | 329.84 | 152.5515 | 147.6668
335.0354 | 329.8214 | 152.8663 | 147.9855
336.0354 | 329.8384 | 153.1845 | 148.3019
337.0354 | 329.8511 | 153.4919 | 148.6197
338.0354 | 329.8724 | 153.8057 | 148.9287
339.0354 | 329.8543 | 154.1195 | 149.2473
340.0354 | 329.8258 | 154.4192 | 149.5638
341.0354 | 329.8288 | 154.7471 | 149.8712
342.0354 | 329.8513 | 155.0675 | 150.1887
343.0354 | 329.8749 | 155.3866 | 150.5034
344.0354 | 329.8677 | 155.6897 | 150.8276
345.0354 | 329.8147 | 156.0123 | 151.1346
346.0354 | 329.8357 | 156.3204 | 151.4529
347.0354 | 329.8545 | 156.6315 | 151.7639
348.0354 | 329.8426 | 156.9345 | 152.0756
349.0354 | 329.8399 | 157.2455 | 152.38
350.0354 | 329.7905 | 157.5554 | 152.7023
351.0354 | 329.7757 | 157.8809 | 153.015
352.0354 | 329.8033 | 158.1859 | 153.3235
353.0354 | 329.8803 | 158.5036 | 153.6348
354.0354 | 329.9303 | 158.8136 | 153.949
355.0354 | 329.9182 | 159.1285 | 154.2627
356.0354 | 329.9449 | 159.4399 | 154.5746
357.0354 | 329.9328 | 159.7393 | 154.8854
358.0354 | 329.9552 | 160.0485 | 155.2077
359.0354 | 329.9666 | 160.3519 | 155.5168
360.0354 | 329.9988 | 160.6724 | 155.8237
361.0354 | 330.0584 | 160.9807 | 156.1351
362.0354 | 330.0657 | 161.2918 | 156.4423
363.0354 | 330.1104 | 161.5983 | 156.7419
364.0354 | 330.0622 | 161.8981 | 157.0534
365.0354 | 330.0338 | 162.211 | 157.3608
366.0354 | 330.0603 | 162.5138 | 157.6699
367.0354 | 330.0263 | 162.8291 | 157.9728
368.0354 | 330.0477 | 163.1301 | 158.2772
369.0354 | 330.0705 | 163.444 | 158.5822
370.0354 | 330.1276 | 163.7462 | 158.8843
371.0354 | 330.1061 | 164.0465 | 159.1932
372.0354 | 330.1202 | 164.3524 | 159.488
373.0354 | 330.1321 | 164.6522 | 159.7903
374.0354 | 330.1868 | 164.9748 | 160.0996
375.0354 | 330.2629 | 165.2775 | 160.3945
376.0354 | 330.2982 | 165.5751 | 160.6925
377.0354 | 330.3044 | 165.8868 | 160.9995
378.0354 | 330.3399 | 166.1886 | 161.3031
379.0354 | 330.3769 | 166.4811 | 161.5972
380.0354 | 330.3983 | 166.7835 | 161.8945
381.0354 | 330.4149 | 167.0773 | 162.1889
382.0354 | 330.484 | 167.3872 | 162.4906
383.0354 | 330.531 | 167.6799 | 162.7837
384.0354 | 330.5392 | 167.9829 | 163.0847
385.0354 | 330.5269 | 168.2784 | 163.3749
386.0354 | 330.5175 | 168.5748 | 163.6702
387.0354 | 330.5497 | 168.8617 | 163.962
388.0354 | 330.5678 | 169.1605 | 164.2589
389.0354 | 330.5248 | 169.4566 | 164.5495
390.0354 | 330.4771 | 169.737 | 164.8506
391.0354 | 330.416 | 170.0281 | 165.1528
392.0354 | 330.392 | 170.3256 | 165.445
393.0354 | 330.4051 | 170.6092 | 165.7345
394.0354 | 330.3994 | 170.9118 | 166.0288
395.0354 | 330.368 | 171.1838 | 166.3077
396.0354 | 330.345 | 171.4842 | 166.5999
397.0354 | 330.2663 | 171.7746 | 166.8839
398.0354 | 330.2273 | 172.0454 | 167.1742
399.0354 | 330.2211 | 172.3337 | 167.4618
400.0354 | 330.1985 | 172.6149 | 167.7406
401.0354 | 330.1434 | 172.9062 | 168.0301
402.0354 | 330.0707 | 173.1773 | 168.3136
403.0354 | 330.0114 | 173.4644 | 168.5959
404.0354 | 329.9371 | 173.7473 | 168.8767
405.0354 | 329.9098 | 174.0233 | 169.1565
406.0354 | 329.9 | 174.2992 | 169.4296
407.0354 | 329.8862 | 174.5898 | 169.7138
408.0354 | 329.8316 | 174.8656 | 169.9844
409.0354 | 329.8328 | 175.1512 | 170.2593
410.0354 | 329.8144 | 175.4206 | 170.5376
411.0354 | 329.7326 | 175.6899 | 170.8067
412.0354 | 329.6799 | 175.963 | 171.0808
413.0354 | 329.6419 | 176.2336 | 171.3438
414.0354 | 329.5907 | 176.5069 | 171.6108
415.0354 | 329.5686 | 176.7745 | 171.8864
416.0354 | 329.5451 | 177.0507 | 172.1602
417.0354 | 329.5018 | 177.3096 | 172.4226
418.0354 | 329.5159 | 177.5813 | 172.6882
419.0354 | 329.5527 | 177.8471 | 172.9625
420.0354 | 329.576 | 178.1118 | 173.2294
421.0354 | 329.5375 | 178.3754 | 173.495
422.0354 | 329.5734 | 178.6423 | 173.7692
423.0354 | 329.5988 | 178.909 | 174.0298
424.0354 | 329.5942 | 179.1645 | 174.294
425.0354 | 329.6266 | 179.4383 | 174.5522
426.0354 | 329.6298 | 179.6859 | 174.8343
427.0354 | 329.6625 | 179.9428 | 175.093
428.0354 | 329.6915 | 180.21 | 175.3585
429.0354 | 329.7171 | 180.4777 | 175.6136
430.0354 | 329.6986 | 180.7295 | 175.8734
431.0354 | 329.6668 | 180.9944 | 176.1344
432.0354 | 329.6476 | 181.2497 | 176.3932
433.0354 | 329.6216 | 181.5013 | 176.6521
434.0354 | 329.6526 | 181.7645 | 176.9071
435.0354 | 329.6493 | 182.0133 | 177.1671
436.0354 | 329.7065 | 182.2822 | 177.4302
437.0354 | 329.7313 | 182.5219 | 177.6878
438.0354 | 329.7824 | 182.7818 | 177.9421
439.0354 | 329.8402 | 183.028 | 178.2111
440.0354 | 329.8874 | 183.2828 | 178.464
441.0354 | 329.9401 | 183.5361 | 178.7144
442.0354 | 329.9395 | 183.7862 | 178.9778
443.0354 | 329.9364 | 184.0405 | 179.2331
444.0354 | 329.8934 | 184.2803 | 179.4887
445.0354 | 329.8862 | 184.5373 | 179.735
446.0354 | 329.8812 | 184.7924 | 179.9891
447.0354 | 329.9283 | 185.0328 | 180.251
448.0354 | 329.9352 | 185.2772 | 180.4987
449.0354 | 329.916 | 185.533 | 180.7507
450.0354 | 329.9596 | 185.7777 | 181.0116
451.0354 | 330.0364 | 186.0319 | 181.2555
452.0354 | 330.0928 | 186.2763 | 181.5238
453.0354 | 330.1484 | 186.5371 | 181.7697
454.0354 | 330.131 | 186.785 | 182.0122
455.0354 | 330.1518 | 187.0323 | 182.2702
456.0354 | 330.1651 | 187.2833 | 182.5203
457.0354 | 330.172 | 187.5316 | 182.7696
458.0354 | 330.211 | 187.7754 | 183.0217
459.0354 | 330.2348 | 188.0242 | 183.2603
460.0354 | 330.2761 | 188.2635 | 183.5182
461.0354 | 330.2849 | 188.5111 | 183.7629
462.0354 | 330.2805 | 188.7566 | 184.0054
463.0354 | 330.2927 | 189.0111 | 184.2468
464.0354 | 330.2913 | 189.2446 | 184.5068
465.0354 | 330.2703 | 189.4873 | 184.76
466.0354 | 330.2888 | 189.729 | 184.996
467.0354 | 330.3037 | 189.9845 | 185.2463
468.0354 | 330.2627 | 190.2203 | 185.4886
469.0354 | 330.2155 | 190.4642 | 185.7298
470.0354 | 330.1984 | 190.714 | 185.967
471.0354 | 330.1847 | 190.9622 | 186.2159
472.0354 | 330.152 | 191.1906 | 186.4562
473.0354 | 330.0904 | 191.4394 | 186.6961
474.0354 | 330.0796 | 191.6804 | 186.9402
475.0354 | 330.0363 | 191.9257 | 187.1887
476.0354 | 329.9617 | 192.1765 | 187.4255
477.0354 | 329.9092 | 192.4201 | 187.6745
478.0354 | 329.8618 | 192.6627 | 187.904
479.0354 | 329.8117 | 192.8918 | 188.1503
480.0354 | 329.8099 | 193.1381 | 188.3938
481.0354 | 329.8281 | 193.3896 | 188.6366
482.0354 | 329.8229 | 193.6172 | 188.8727
483.0354 | 329.7944 | 193.8746 | 189.1151
484.0354 | 329.7666 | 194.1097 | 189.3567
485.0354 | 329.7256 | 194.3607 | 189.5856
486.0354 | 329.6951 | 194.6027 | 189.8223
487.0354 | 329.6657 | 194.837 | 190.0557
488.0354 | 329.6142 | 195.0885 | 190.2945
489.0354 | 329.6062 | 195.3134 | 190.5297
490.0354 | 329.6117 | 195.5599 | 190.7727
491.0354 | 329.6689 | 195.8006 | 191.0047
492.0354 | 329.7025 | 196.0401 | 191.245
493.0354 | 329.7309 | 196.2716 | 191.4769
494.0354 | 329.7729 | 196.5249 | 191.7065
495.0354 | 329.8158 | 196.754 | 191.9483
496.0354 | 329.7883 | 196.9879 | 192.1788
497.0354 | 329.7852 | 197.2106 | 192.4059
498.0354 | 329.768 | 197.4576 | 192.6489
499.0354 | 329.7828 | 197.6947 | 192.8852
500.0354 | 329.8175 | 197.9245 | 193.1171
501.0354 | 329.8936 | 198.1604 | 193.3589
502.0354 | 329.8704 | 198.3934 | 193.594
503.0354 | 329.8389 | 198.6234 | 193.826
504.0354 | 329.8211 | 198.8578 | 194.0641
505.0354 | 329.8329 | 199.0913 | 194.3114
506.0354 | 329.8198 | 199.3221 | 194.5545
507.0354 | 329.8359 | 199.5477 | 194.7804
508.0354 | 329.834 | 199.7851 | 195.0373
509.0354 | 329.7967 | 200.0229 | 195.2711
510.0354 | 329.7955 | 200.2489 | 195.5108
511.0354 | 329.8102 | 200.4833 | 195.7423
512.0354 | 329.7717 | 200.7251 | 195.9819
513.0354 | 329.7341 | 200.9528 | 196.2286
514.0354 | 329.7582 | 201.182 | 196.4646
515.0354 | 329.777 | 201.4188 | 196.7078
516.0354 | 329.8273 | 201.6498 | 196.948
517.0354 | 329.8289 | 201.8845 | 197.1841
518.0354 | 329.8727 | 202.1156 | 197.4302
519.0354 | 329.9034 | 202.3448 | 197.6722
520.0354 | 329.972 | 202.5836 | 197.9109
521.0354 | 329.9882 | 202.8064 | 198.1549
522.0354 | 330.0204 | 203.042 | 198.3948
523.0354 | 330.0527 | 203.2749 | 198.6388
524.0354 | 330.0631 | 203.4994 | 198.88
525.0354 | 330.015 | 203.7286 | 199.1198
526.0354 | 330.0002 | 203.963 | 199.3562
527.0354 | 330.0211 | 204.2001 | 199.5942
528.0354 | 330.0265 | 204.427 | 199.8351
529.0354 | 330.0237 | 204.6522 | 200.0715
530.0354 | 330.0083 | 204.8696 | 200.3105
531.0354 | 329.9514 | 205.1034 | 200.5517
532.0354 | 329.8582 | 205.3344 | 200.7778
533.0354 | 329.8057 | 205.5585 | 201.0053
534.0354 | 329.8033 | 205.779 | 201.2443
535.0354 | 329.7962 | 205.9952 | 201.4736
536.0354 | 329.7722 | 206.2151 | 201.693
537.0354 | 329.7655 | 206.4356 | 201.9192
538.0354 | 329.74 | 206.6628 | 202.1404
539.0354 | 329.7053 | 206.8647 | 202.3666
540.0354 | 329.6468 | 207.0966 | 202.5871
541.0354 | 329.5667 | 207.3043 | 202.8116
542.0354 | 329.4847 | 207.5254 | 203.0313
543.0354 | 329.4337 | 207.7547 | 203.2527
544.0354 | 329.3808 | 207.9577 | 203.4652
545.0354 | 329.3114 | 208.1777 | 203.6895
546.0354 | 329.2112 | 208.3888 | 203.9056
547.0354 | 329.1669 | 208.6033 | 204.129
548.0354 | 329.1388 | 208.8149 | 204.3457
549.0354 | 329.1452 | 209.0101 | 204.5559
550.0354 | 329.1298 | 209.2206 | 204.7749
551.0354 | 329.1242 | 209.4438 | 204.9812
552.0354 | 329.1094 | 209.6554 | 205.1943
553.0354 | 329.0944 | 209.8616 | 205.4028
554.0354 | 329.1082 | 210.0679 | 205.6112
555.0354 | 329.1305 | 210.2735 | 205.8232
556.0354 | 329.1305 | 210.4777 | 206.0241
557.0354 | 329.1017 | 210.6856 | 206.2267
558.0354 | 329.0865 | 210.8856 | 206.4252
559.0354 | 329.0772 | 211.0947 | 206.6382
560.0354 | 329.0864 | 211.2953 | 206.8438
561.0354 | 329.1172 | 211.5058 | 207.0414
562.0354 | 329.1446 | 211.7083 | 207.247
563.0354 | 329.1255 | 211.9191 | 207.4448
564.0354 | 329.1512 | 212.1177 | 207.6497
565.0354 | 329.1981 | 212.3249 | 207.8406
566.0354 | 329.248 | 212.5313 | 208.0303
567.0354 | 329.2795 | 212.7338 | 208.2261
568.0354 | 329.3177 | 212.9333 | 208.4268
569.0354 | 329.3054 | 213.1289 | 208.6146
570.0354 | 329.2773 | 213.3365 | 208.8078
571.0354 | 329.2845 | 213.5462 | 208.9971
572.0354 | 329.3432 | 213.7541 | 209.186
573.0354 | 329.3949 | 213.9697 | 209.3793
574.0354 | 329.4541 | 214.1771 | 209.5734
575.0354 | 329.5196 | 214.3738 | 209.7593
576.0354 | 329.5451 | 214.5817 | 209.9637
577.0354 | 329.5685 | 214.7863 | 210.1491
578.0354 | 329.6 | 214.9984 | 210.3438
579.0354 | 329.6367 | 215.1978 | 210.5392
580.0354 | 329.6805 | 215.3877 | 210.7284
581.0354 | 329.722 | 215.6072 | 210.9234
582.0354 | 329.7637 | 215.8128 | 211.1186
583.0354 | 329.8384 | 216.0126 | 211.3106
584.0354 | 329.8367 | 216.2213 | 211.4982
585.0354 | 329.8319 | 216.4256 | 211.6983
586.0354 | 329.8591 | 216.6286 | 211.8887
587.0354 | 329.9063 | 216.8404 | 212.082
588.0354 | 329.9173 | 217.0487 | 212.2834
589.0354 | 329.893 | 217.2397 | 212.4748
590.0354 | 329.891 | 217.4452 | 212.6732
591.0354 | 329.8889 | 217.6499 | 212.8596
592.0354 | 329.8357 | 217.8637 | 213.0632
593.0354 | 329.8259 | 218.0611 | 213.2579
594.0354 | 329.8632 | 218.2617 | 213.4504
595.0354 | 329.8512 | 218.4642 | 213.6477
596.0354 | 329.8199 | 218.6705 | 213.8527
597.0354 | 329.8258 | 218.8568 | 214.0493
598.0354 | 329.816 | 219.0685 | 214.2503
599.0354 | 329.779 | 219.2684 | 214.4441
600.0354 | 329.7408 | 219.4709 | 214.6305
601.0354 | 329.7318 | 219.665 | 214.8271
602.0354 | 329.7574 | 219.875 | 215.025
603.0354 | 329.708 | 220.0687 | 215.2126
604.0354 | 329.675 | 220.2717 | 215.404
605.0354 | 329.6617 | 220.4673 | 215.602
606.0354 | 329.6195 | 220.6638 | 215.7942
607.0354 | 329.5927 | 220.8698 | 215.9831
608.0354 | 329.5671 | 221.0562 | 216.1701
609.0354 | 329.5352 | 221.2543 | 216.3613
610.0354 | 329.5228 | 221.4517 | 216.5486
611.0354 | 329.4693 | 221.6559 | 216.7439
612.0354 | 329.4779 | 221.8454 | 216.933
613.0354 | 329.4898 | 222.0337 | 217.1187
614.0354 | 329.499 | 222.2411 | 217.3077
615.0354 | 329.4869 | 222.4308 | 217.4949
616.0354 | 329.4596 | 222.618 | 217.6797
617.0354 | 329.3959 | 222.8111 | 217.8697
618.0354 | 329.3544 | 223.01 | 218.0561
619.0354 | 329.3295 | 223.2002 | 218.243
620.0354 | 329.3678 | 223.3936 | 218.4339
621.0354 | 329.3655 | 223.5937 | 218.6201
622.0354 | 329.3662 | 223.7804 | 218.7898
623.0354 | 329.3766 | 223.9763 | 218.9715
624.0354 | 329.3746 | 224.1651 | 219.158
625.0354 | 329.3547 | 224.3457 | 219.3327
626.0354 | 329.3865 | 224.551 | 219.518
627.0354 | 329.4063 | 224.7202 | 219.6972
628.0354 | 329.415 | 224.9123 | 219.8781
629.0354 | 329.4073 | 225.1002 | 220.0616
630.0354 | 329.4296 | 225.2729 | 220.2343
631.0354 | 329.4607 | 225.4638 | 220.4227
632.0354 | 329.4735 | 225.6481 | 220.6
633.0354 | 329.511 | 225.8193 | 220.7807
634.0354 | 329.5074 | 226.0116 | 220.9646
635.0354 | 329.5 | 226.1996 | 221.1425
636.0354 | 329.5037 | 226.3814 | 221.3245
637.0354 | 329.5199 | 226.5681 | 221.4967
638.0354 | 329.5356 | 226.739 | 221.681
639.0354 | 329.5105 | 226.9195 | 221.8502
640.0354 | 329.4958 | 227.1064 | 222.0294
641.0354 | 329.4575 | 227.2846 | 222.2057
642.0354 | 329.4705 | 227.4679 | 222.3842
643.0354 | 329.4929 | 227.6508 | 222.5634
644.0354 | 329.4251 | 227.823 | 222.7433
645.0354 | 329.4 | 228.0062 | 222.9116
646.0354 | 329.4374 | 228.175 | 223.0886
647.0354 | 329.4844 | 228.3505 | 223.2673
648.0354 | 329.5032 | 228.537 | 223.4421
649.0354 | 329.5115 | 228.7022 | 223.6201
650.0354 | 329.5387 | 228.8752 | 223.7965
651.0354 | 329.5314 | 229.0583 | 223.9727
652.0354 | 329.5644 | 229.2325 | 224.1453
653.0354 | 329.5378 | 229.3981 | 224.3086
654.0354 | 329.496 | 229.574 | 224.4884
655.0354 | 329.4871 | 229.7394 | 224.6616
656.0354 | 329.4863 | 229.91 | 224.8253
657.0354 | 329.489 | 230.0867 | 224.9968
658.0354 | 329.5025 | 230.2484 | 225.1671
659.0354 | 329.4889 | 230.3983 | 225.3313
660.0354 | 329.4845 | 230.563 | 225.4895
661.0354 | 329.4513 | 230.733 | 225.6543
662.0354 | 329.4759 | 230.8888 | 225.836
663.0354 | 329.5243 | 231.0588 | 225.994
664.0354 | 329.5348 | 231.2168 | 226.1568
665.0354 | 329.5438 | 231.3777 | 226.3183
666.0354 | 329.5497 | 231.5301 | 226.4847
667.0354 | 329.5513 | 231.6947 | 226.6535
668.0354 | 329.5685 | 231.8507 | 226.8178
669.0354 | 329.617 | 232.0028 | 226.9752
670.0354 | 329.6614 | 232.1618 | 227.1402
671.0354 | 329.695 | 232.3268 | 227.2972
672.0354 | 329.7179 | 232.4935 | 227.4599
673.0354 | 329.7479 | 232.6524 | 227.6183
674.0354 | 329.7671 | 232.8052 | 227.7775
675.0354 | 329.7453 | 232.9596 | 227.9351
676.0354 | 329.6939 | 233.1176 | 228.0984
677.0354 | 329.638 | 233.2933 | 228.2547
678.0354 | 329.6178 | 233.4352 | 228.4156
679.0354 | 329.5967 | 233.5881 | 228.5705
680.0354 | 329.5845 | 233.7536 | 228.7209
681.0354 | 329.6061 | 233.906 | 228.8715
682.0354 | 329.5757 | 234.0531 | 229.0269
683.0354 | 329.554 | 234.1963 | 229.1839
684.0354 | 329.5312 | 234.3569 | 229.3332
685.0354 | 329.5618 | 234.4917 | 229.4955
686.0354 | 329.5749 | 234.6374 | 229.6412
687.0354 | 329.5557 | 234.7889 | 229.7859
688.0354 | 329.5222 | 234.9305 | 229.9323
689.0354 | 329.5128 | 235.0765 | 230.0806
690.0354 | 329.5016 | 235.2077 | 230.2347
691.0354 | 329.4969 | 235.3488 | 230.3804
692.0354 | 329.5005 | 235.4908 | 230.5272
693.0354 | 329.5166 | 235.6381 | 230.6688
694.0354 | 329.4918 | 235.7788 | 230.8197
695.0354 | 329.4827 | 235.9192 | 230.9651
696.0354 | 329.4534 | 236.0664 | 231.0985
697.0354 | 329.4568 | 236.1904 | 231.2444
698.0354 | 329.47 | 236.3086 | 231.3828
699.0354 | 329.4705 | 236.429 | 231.5256
700.0354 | 329.4888 | 236.5483 | 231.6546
701.0354 | 329.5033 | 236.6755 | 231.7953
702.0354 | 329.5166 | 236.7998 | 231.9302
703.0354 | 329.5528 | 236.9261 | 232.0672
704.0354 | 329.5949 | 237.0422 | 232.2041
705.0354 | 329.6079 | 237.1854 | 232.34
706.0354 | 329.6027 | 237.3202 | 232.4662
707.0354 | 329.6004 | 237.4514 | 232.5915
708.0354 | 329.6262 | 237.5801 | 232.7161
709.0354 | 329.6586 | 237.721 | 232.8401
710.0354 | 329.6971 | 237.8554 | 232.958
711.0354 | 329.7373 | 237.98 | 233.0918
712.0354 | 329.7691 | 238.1129 | 233.2098
713.0354 | 329.8159 | 238.247 | 233.3629
714.0354 | 329.8334 | 238.3945 | 233.4818
715.0354 | 329.8027 | 238.5254 | 233.6317
716.0354 | 329.8391 | 238.6498 | 233.7713
717.0354 | 329.8778 | 238.7981 | 233.8998
718.0354 | 329.9448 | 238.9337 | 234.0248
719.0354 | 329.975 | 239.0651 | 234.1463
720.0354 | 329.9757 | 239.1941 | 234.2787
721.0354 | 329.9347 | 239.3309 | 234.4098
722.0354 | 329.9311 | 239.4482 | 234.5432
723.0354 | 329.8947 | 239.5828 | 234.6684
724.0354 | 329.9129 | 239.7074 | 234.8036
725.0354 | 329.9085 | 239.8341 | 234.9542
726.0354 | 329.8936 | 239.952 | 235.1149
727.0354 | 329.9056 | 240.0746 | 235.2554
728.0354 | 329.91 | 240.1964 | 235.4022
729.0354 | 329.8695 | 240.3143 | 235.5416
730.0354 | 329.8715 | 240.43 | 235.6802
731.0354 | 329.8793 | 240.5607 | 235.823
732.0354 | 329.8822 | 240.6703 | 235.9571
733.0354 | 329.8818 | 240.7934 | 236.0946
734.0354 | 329.8763 | 240.914 | 236.2305
735.0354 | 329.8614 | 241.0328 | 236.3666
736.0354 | 329.8067 | 241.156 | 236.4888
737.0354 | 329.8185 | 241.2773 | 236.6233
738.0354 | 329.862 | 241.4033 | 236.7444
739.0354 | 329.8773 | 241.5212 | 236.8656
740.0354 | 329.8991 | 241.6367 | 236.9915
741.0354 | 329.886 | 241.7608 | 237.109
742.0354 | 329.8801 | 241.8814 | 237.2324
743.0354 | 329.8657 | 241.9879 | 237.3443
744.0354 | 329.8259 | 242.0974 | 237.4564
745.0354 | 329.8336 | 242.2128 | 237.5739
746.0354 | 329.7978 | 242.3365 | 237.6882
747.0354 | 329.7703 | 242.4568 | 237.7986
748.0354 | 329.7646 | 242.5786 | 237.9093
749.0354 | 329.7766 | 242.6919 | 238.0014
750.0354 | 329.7821 | 242.8034 | 238.1035
751.0354 | 329.7712 | 242.9068 | 238.2002
752.0354 | 329.7669 | 243.0363 | 238.33
753.0354 | 329.7199 | 243.1309 | 238.5154
754.0354 | 329.7471 | 243.2419 | 238.688
755.0354 | 329.7894 | 243.3348 | 238.837
756.0354 | 329.8019 | 243.4336 | 238.9544
757.0354 | 329.7868 | 243.5383 | 239.0979
758.0354 | 329.7807 | 243.6361 | 239.2404
759.0354 | 329.7927 | 243.7263 | 239.3605
760.0354 | 329.7997 | 243.7998 | 239.4815
761.0354 | 329.8146 | 243.935 | 239.5998
762.0354 | 329.8519 | 244.0315 | 239.7151
763.0354 | 329.8446 | 244.159 | 239.8346
764.0354 | 329.8361 | 244.2668 | 239.9503
765.0354 | 329.842 | 244.3561 | 240.0558
766.0354 | 329.8793 | 244.4607 | 240.174
767.0354 | 329.8948 | 244.5704 | 240.2741
768.0354 | 329.9497 | 244.6708 | 240.377
769.0354 | 329.9715 | 244.7621 | 240.4864
770.0354 | 329.9979 | 244.8778 | 240.5931
771.0354 | 330.0044 | 244.9805 | 240.6936
772.0354 | 330.0276 | 245.0989 | 240.8089
773.0354 | 330.0293 | 245.2014 | 240.9498
774.0354 | 329.9891 | 245.3028 | 241.0677
775.0354 | 329.9985 | 245.4103 | 241.1699
776.0354 | 329.9973 | 245.511 | 241.2824
777.0354 | 329.9894 | 245.6123 | 241.3855
778.0354 | 330.0087 | 245.7041 | 241.4972
779.0354 | 330.039 | 245.8075 | 241.6079
780.0354 | 330.0745 | 245.9007 | 241.7116
781.0354 | 330.0781 | 245.993 | 241.8222
782.0354 | 330.0444 | 246.0897 | 241.93
783.0354 | 330.0464 | 246.1818 | 242.0371
784.0354 | 330.0469 | 246.2639 | 242.1397
785.0354 | 330.0489 | 246.3538 | 242.2385
786.0354 | 330.0178 | 246.46 | 242.3407
787.0354 | 330.0125 | 246.5617 | 242.4494
788.0354 | 330.0157 | 246.6569 | 242.5577
789.0354 | 330.0143 | 246.7428 | 242.6581
790.0354 | 330.0315 | 246.8598 | 242.7645
791.0354 | 330.0417 | 246.9689 | 242.8701
792.0354 | 330.0447 | 247.0646 | 242.9674
793.0354 | 330.0631 | 247.1745 | 243.0723
794.0354 | 330.0639 | 247.2812 | 243.1674
795.0354 | 330.0746 | 247.379 | 243.2586
796.0354 | 330.0899 | 247.4834 | 243.3528
797.0354 | 330.0639 | 247.5816 | 243.4451
798.0354 | 330.0471 | 247.673 | 243.5425
799.0354 | 330.0194 | 247.7783 | 243.6509
800.0354 | 329.9902 | 247.8601 | 243.753
801.0354 | 329.9661 | 247.9398 | 243.8582
802.0354 | 329.9181 | 248.0329 | 243.9482
803.0354 | 329.8938 | 248.1328 | 244.0443
804.0354 | 329.8897 | 248.2253 | 244.1323
805.0354 | 329.8555 | 248.322 | 244.2322
806.0354 | 329.7972 | 248.4112 | 244.3286
807.0354 | 329.7436 | 248.5101 | 244.411
808.0354 | 329.6631 | 248.6061 | 244.5067
809.0354 | 329.6108 | 248.6941 | 244.5931
810.0354 | 329.5862 | 248.8005 | 244.6754
811.0354 | 329.6076 | 248.8953 | 244.7718
812.0354 | 329.6087 | 248.9889 | 244.8515
813.0354 | 329.6003 | 249.0788 | 244.937
814.0354 | 329.574 | 249.177 | 245.0204
815.0354 | 329.5799 | 249.2667 | 245.0987
816.0354 | 329.5754 | 249.3516 | 245.1802
817.0354 | 329.575 | 249.4232 | 245.2656
818.0354 | 329.5674 | 249.4916 | 245.3517
819.0354 | 329.5679 | 249.5984 | 245.4336
820.0354 | 329.5533 | 249.6898 | 245.5222
821.0354 | 329.5252 | 249.801 | 245.616
822.0354 | 329.4624 | 249.9043 | 245.7063
823.0354 | 329.4341 | 250.0099 | 245.7956
824.0354 | 329.3923 | 250.1108 | 245.8807
825.0354 | 329.3933 | 250.2235 | 245.9668
826.0354 | 329.3592 | 250.3283 | 246.0644
827.0354 | 329.3372 | 250.4351 | 246.1514
828.0354 | 329.2669 | 250.5472 | 246.2432
829.0354 | 329.2445 | 250.6489 | 246.3315
830.0354 | 329.2443 | 250.7686 | 246.4181
831.0354 | 329.2457 | 250.8701 | 246.5126
832.0354 | 329.2776 | 250.9939 | 246.603
833.0354 | 329.3601 | 251.1078 | 246.6896
834.0354 | 329.3458 | 251.2386 | 246.7737
835.0354 | 329.3294 | 251.3749 | 246.8652
836.0354 | 329.3191 | 251.5257 | 246.9627
837.0354 | 329.2831 | 251.6897 | 247.0544
838.0354 | 329.3249 | 251.8789 | 247.1478
839.0354 | 329.335 | 252.0881 | 247.2411
840.0354 | 329.3701 | 252.3174 | 247.3345
841.0354 | 329.3839 | 252.5567 | 247.4269
842.0354 | 329.3955 | 252.8125 | 247.5236
843.0354 | 329.4027 | 253.0778 | 247.6174
844.0354 | 329.4631 | 253.3347 | 247.7094
845.0354 | 329.4855 | 253.594 | 247.8062
846.0354 | 329.5012 | 253.8643 | 247.8943
847.0354 | 329.5409 | 254.1237 | 247.9832
848.0354 | 329.5808 | 254.3902 | 248.0805
849.0354 | 329.5789 | 254.6432 | 248.1698
850.0354 | 329.5834 | 254.9095 | 248.2587
851.0354 | 329.632 | 255.1417 | 248.3583
852.0354 | 329.6756 | 255.3979 | 248.4437
853.0354 | 329.7307 | 255.6369 | 248.5261
854.0354 | 329.7749 | 255.8863 | 248.6155
855.0354 | 329.8129 | 256.134 | 248.7057
856.0354 | 329.8434 | 256.3753 | 248.7914
857.0354 | 329.8456 | 256.6053 | 248.8744
858.0354 | 329.8512 | 256.831 | 248.9534
859.0354 | 329.8397 | 257.0581 | 249.0436
860.0354 | 329.8476 | 257.3027 | 249.1267
861.0354 | 329.8124 | 257.5514 | 249.2144
862.0354 | 329.8209 | 257.8006 | 249.3031
863.0354 | 329.8475 | 258.0416 | 249.3912
864.0354 | 329.8677 | 258.2896 | 249.4677
865.0354 | 329.8721 | 258.529 | 249.5568
866.0354 | 329.8528 | 258.7848 | 249.6311
867.0354 | 329.8177 | 259.0252 | 249.722
868.0354 | 329.8166 | 259.2697 | 249.7912
869.0354 | 329.8255 | 259.5009 | 249.8729
870.0354 | 329.8266 | 259.7396 | 249.9677
871.0354 | 329.7992 | 259.971 | 250.0511
872.0354 | 329.7969 | 260.1792 | 250.1343
873.0354 | 329.7833 | 260.3925 | 250.2064
874.0354 | 329.8043 | 260.5935 | 250.2922
875.0354 | 329.7589 | 260.7974 | 250.3774
876.0354 | 329.7039 | 260.9983 | 250.4505
877.0354 | 329.701 | 261.1956 | 250.5303
878.0354 | 329.7248 | 261.3931 | 250.6152
879.0354 | 329.7073 | 261.5905 | 250.6956
880.0354 | 329.702 | 261.7975 | 250.7728
881.0354 | 329.6709 | 261.9889 | 250.8544
882.0354 | 329.6721 | 262.1832 | 250.9387
883.0354 | 329.6692 | 262.3765 | 251.0176
884.0354 | 329.6465 | 262.5492 | 251.103
885.0354 | 329.6451 | 262.7247 | 251.1908
886.0354 | 329.671 | 262.9059 | 251.2864
887.0354 | 329.7209 | 263.0807 | 251.3685
888.0354 | 329.7095 | 263.2619 | 251.4635
889.0354 | 329.6729 | 263.4515 | 251.5533
890.0354 | 329.6247 | 263.6306 | 251.64
891.0354 | 329.599 | 263.8114 | 251.7268
892.0354 | 329.586 | 263.9944 | 251.8187
893.0354 | 329.5526 | 264.1716 | 251.9065
894.0354 | 329.5275 | 264.3312 | 251.9796
895.0354 | 329.4946 | 264.5103 | 252.0676
896.0354 | 329.4559 | 264.6739 | 252.1564
897.0354 | 329.4128 | 264.8456 | 252.231
898.0354 | 329.4157 | 265.0006 | 252.3217
899.0354 | 329.4211 | 265.1581 | 252.4091
900.0354 | 329.3384 | 265.3165 | 252.4904
901.0354 | 329.2768 | 265.4494 | 252.5685
902.0354 | 329.2154 | 265.5981 | 252.6672
903.0354 | 329.1669 | 265.7369 | 252.7409
904.0354 | 329.1312 | 265.8672 | 252.8284
905.0354 | 329.1337 | 266.0341 | 252.9059
906.0354 | 329.1033 | 266.1699 | 252.9808
907.0354 | 329.055 | 266.2924 | 253.0539
908.0354 | 328.9943 | 266.4264 | 253.1219
909.0354 | 328.9495 | 266.5586 | 253.2073
910.0354 | 328.8952 | 266.6857 | 253.2872
911.0354 | 328.8612 | 266.8019 | 253.3541
912.0354 | 328.7934 | 266.9089 | 253.4295
913.0354 | 328.7638 | 267.018 | 253.5101
914.0354 | 328.7555 | 267.1257 | 253.5866
915.0354 | 328.7589 | 267.2257 | 253.6694
916.0354 | 328.7592 | 267.3272 | 253.7373
917.0354 | 328.7134 | 267.4431 | 253.8188
918.0354 | 328.6654 | 267.5536 | 253.8982
919.0354 | 328.6403 | 267.6613 | 253.9748
920.0354 | 328.6111 | 267.7699 | 254.0466
921.0354 | 328.6171 | 267.8797 | 254.1266
922.0354 | 328.5691 | 267.9966 | 254.1954
923.0354 | 328.5513 | 268.1061 | 254.2785
924.0354 | 328.5941 | 268.2261 | 254.3564
925.0354 | 328.6452 | 268.3385 | 254.4364
926.0354 | 328.6729 | 268.4449 | 254.506
927.0354 | 328.6966 | 268.5447 | 254.5832
928.0354 | 328.7466 | 268.6271 | 254.6628
929.0354 | 328.767 | 268.7336 | 254.729
930.0354 | 328.8076 | 268.8231 | 254.8045
931.0354 | 328.8886 | 268.909 | 254.8774
932.0354 | 328.9495 | 269.0085 | 254.9503
933.0354 | 329.0058 | 269.0938 | 255.025
934.0354 | 329.0741 | 269.1804 | 255.0915
935.0354 | 329.1191 | 269.2697 | 255.1595
936.0354 | 329.1398 | 269.3665 | 255.2373
937.0354 | 329.1842 | 269.4647 | 255.3127
938.0354 | 329.2359 | 269.5448 | 255.376
939.0354 | 329.3419 | 269.6281 | 255.4508
940.0354 | 329.4203 | 269.7142 | 255.5254
941.0354 | 329.483 | 269.7985 | 255.5985
942.0354 | 329.5341 | 269.878 | 255.6757
943.0354 | 329.5687 | 269.9626 | 255.7446
944.0354 | 329.5936 | 270.0247 | 255.8207
945.0354 | 329.6277 | 270.1083 | 255.8968
946.0354 | 329.6874 | 270.1845 | 255.9658
947.0354 | 329.741 | 270.2816 | 256.0392
948.0354 | 329.77 | 270.3594 | 256.1119
949.0354 | 329.7973 | 270.4323 | 256.1807
950.0354 | 329.7988 | 270.525 | 256.2515
951.0354 | 329.8392 | 270.612 | 256.3278
952.0354 | 329.8509 | 270.7026 | 256.4008
953.0354 | 329.8781 | 270.7857 | 256.4708
954.0354 | 329.9071 | 270.8735 | 256.5316
955.0354 | 329.902 | 270.9718 | 256.6064
956.0354 | 329.8944 | 271.0616 | 256.6733
957.0354 | 329.8679 | 271.1347 | 256.7424
958.0354 | 329.8709 | 271.219 | 256.813
959.0354 | 329.8461 | 271.3021 | 256.8716
960.0354 | 329.8253 | 271.3853 | 256.9382
961.0354 | 329.8277 | 271.4599 | 257.0126
962.0354 | 329.8096 | 271.5532 | 257.0838
963.0354 | 329.7871 | 271.6189 | 257.1436
964.0354 | 329.7781 | 271.6982 | 257.2155
965.0354 | 329.7507 | 271.7671 | 257.2847
966.0354 | 329.7402 | 271.8363 | 257.3584
967.0354 | 329.7 | 271.9142 | 257.4213
968.0354 | 329.6392 | 271.9717 | 257.4911
969.0354 | 329.582 | 272.0331 | 257.5566
970.0354 | 329.5533 | 272.083 | 257.6274
971.0354 | 329.5576 | 272.1261 | 257.6895
972.0354 | 329.5366 | 272.1904 | 257.7504
973.0354 | 329.5038 | 272.2594 | 257.8194
974.0354 | 329.4768 | 272.3171 | 257.8779
975.0354 | 329.4359 | 272.3767 | 257.9456
976.0354 | 329.4214 | 272.4348 | 258.0214
977.0354 | 329.3886 | 272.4948 | 258.0796
978.0354 | 329.3648 | 272.5522 | 258.1447
979.0354 | 329.3367 | 272.6053 | 258.2093
980.0354 | 329.3114 | 272.6512 | 258.2667
981.0354 | 329.2505 | 272.7179 | 258.3371
982.0354 | 329.2002 | 272.775 | 258.3997
983.0354 | 329.1572 | 272.8262 | 258.4638
984.0354 | 329.1033 | 272.8779 | 258.528
985.0354 | 329.1065 | 272.9325 | 258.6016
986.0354 | 329.0906 | 272.9794 | 258.6647
987.0354 | 329.0759 | 273.0253 | 258.731
988.0354 | 329.057 | 273.0673 | 258.7917
989.0354 | 329.0439 | 273.1089 | 258.8523
990.0354 | 329.0425 | 273.1705 | 258.928
991.0354 | 328.9988 | 273.2122 | 258.9742
992.0354 | 328.9926 | 273.2593 | 259.0403
993.0354 | 328.9744 | 273.3138 | 259.0979
994.0354 | 328.969 | 273.3903 | 259.165
995.0354 | 328.9515 | 273.4491 | 259.2336
996.0354 | 328.9047 | 273.4956 | 259.2979
997.0354 | 328.8913 | 273.5716 | 259.364
998.0354 | 328.8891 | 273.6181 | 259.4302
999.0354 | 328.9444 | 273.6621 | 259.4985
1000.0354 | 328.9564 | 273.7227 | 259.5567
1001.0354 | 328.9066 | 273.7654 | 259.6237
1002.0354 | 328.8799 | 273.826 | 259.687
1003.0354 | 328.8292 | 273.8755 | 259.7506
1004.0354 | 328.8145 | 273.9303 | 259.8058
1005.0354 | 328.7993 | 273.9839 | 259.872
1006.0354 | 328.8285 | 274.038 | 259.9386
1007.0354 | 328.8388 | 274.0866 | 259.9994
1008.0354 | 328.8849 | 274.1466 | 260.0616
1009.0354 | 328.9313 | 274.2013 | 260.1284
1010.0354 | 328.9584 | 274.2628 | 260.191
1011.0354 | 328.9754 | 274.3191 | 260.2497
1012.0354 | 328.981 | 274.3765 | 260.3139
1013.0354 | 328.9903 | 274.4388 | 260.3799
1014.0354 | 329.0342 | 274.4945 | 260.446
1015.0354 | 329.0673 | 274.5533 | 260.503
1016.0354 | 329.0778 | 274.6186 | 260.5659
1017.0354 | 329.0729 | 274.6713 | 260.6262
1018.0354 | 329.1052 | 274.7383 | 260.694
1019.0354 | 329.1096 | 274.8042 | 260.7619
1020.0354 | 329.1154 | 274.8574 | 260.8243
1021.0354 | 329.1057 | 274.9283 | 260.8898
1022.0354 | 329.1276 | 274.9899 | 260.9487
1023.0354 | 329.1242 | 275.0545 | 261.0154
1024.0354 | 329.0974 | 275.1042 | 261.0785
1025.0354 | 329.0951 | 275.162 | 261.1369
1026.0354 | 329.1222 | 275.2123 | 261.2007
1027.0354 | 329.0983 | 275.2617 | 261.2596
1028.0354 | 329.0616 | 275.3164 | 261.3178
1029.0354 | 329.0435 | 275.3716 | 261.3867
1030.0354 | 329.056 | 275.4185 | 261.4446
1031.0354 | 329.0304 | 275.4722 | 261.5035
1032.0354 | 329.0077 | 275.5153 | 261.5583
1033.0354 | 328.992 | 275.5675 | 261.6155
1034.0354 | 329.0011 | 275.6168 | 261.6854
1035.0354 | 329.006 | 275.6615 | 261.7378
1036.0354 | 329.0013 | 275.7137 | 261.8018
1037.0354 | 329.006 | 275.7685 | 261.8652
1038.0354 | 328.9829 | 275.8027 | 261.9298
1039.0354 | 328.9615 | 275.8425 | 261.9946
1040.0354 | 328.9871 | 275.8865 | 262.0507
1041.0354 | 328.985 | 275.9256 | 262.1066
1042.0354 | 328.962 | 275.9792 | 262.1741
1043.0354 | 328.9392 | 276.0084 | 262.2396
1044.0354 | 328.9175 | 276.0471 | 262.3024
1045.0354 | 328.883 | 276.0885 | 262.3591
1046.0354 | 328.8633 | 276.1159 | 262.4247
1047.0354 | 328.8452 | 276.1542 | 262.4805
1048.0354 | 328.8334 | 276.1845 | 262.5427
1049.0354 | 328.8534 | 276.2152 | 262.607
1050.0354 | 328.8529 | 276.2591 | 262.663
1051.0354 | 328.8432 | 276.3008 | 262.7171
1052.0354 | 328.8436 | 276.3371 | 262.7881
1053.0354 | 328.8383 | 276.3692 | 262.8384
1054.0354 | 328.8367 | 276.4034 | 262.8985
1055.0354 | 328.8137 | 276.4422 | 262.9592
1056.0354 | 328.7943 | 276.4833 | 263.011
1057.0354 | 328.7856 | 276.4939 | 263.0676
1058.0354 | 328.8001 | 276.5244 | 263.1292
1059.0354 | 328.8085 | 276.5435 | 263.1891
1060.0354 | 328.8101 | 276.5659 | 263.2427
1061.0354 | 328.8138 | 276.6102 | 263.2888
1062.0354 | 328.8268 | 276.6221 | 263.3467
1063.0354 | 328.8426 | 276.6559 | 263.4068
1064.0354 | 328.8784 | 276.6862 | 263.4547
1065.0354 | 328.9044 | 276.7143 | 263.5119
1066.0354 | 328.945 | 276.7435 | 263.5581
1067.0354 | 328.941 | 276.78 | 263.6118
1068.0354 | 328.9283 | 276.8184 | 263.6658
1069.0354 | 328.9711 | 276.8634 | 263.7148
1070.0354 | 328.9414 | 276.8529 | 263.7679
1071.0354 | 328.9474 | 276.923 | 263.8223
1072.0354 | 328.9851 | 276.9766 | 263.8681
1073.0354 | 329.0376 | 277.0152 | 263.9216
1074.0354 | 329.0856 | 277.0738 | 263.9658
1075.0354 | 329.0889 | 277.0886 | 264.0224
1076.0354 | 329.114 | 277.1192 | 264.0678
1077.0354 | 329.0943 | 277.1711 | 264.1209
1078.0354 | 329.1041 | 277.2256 | 264.1706
1079.0354 | 329.1376 | 277.1952 | 264.2157
1080.0354 | 329.1655 | 277.2141 | 264.2649
1081.0354 | 329.1822 | 277.2547 | 264.3112
1082.0354 | 329.2006 | 277.2622 | 264.3684
1083.0354 | 329.2353 | 277.3089 | 264.4127
1084.0354 | 329.2813 | 277.3328 | 264.4617
1085.0354 | 329.2894 | 277.3701 | 264.5027
1086.0354 | 329.3018 | 277.404 | 264.5517
1087.0354 | 329.3 | 277.4507 | 264.5986
1088.0354 | 329.2992 | 277.5083 | 264.6425
1089.0354 | 329.2817 | 277.5666 | 264.6921
1090.0354 | 329.2704 | 277.6228 | 264.7425
1091.0354 | 329.2681 | 277.6363 | 264.7862
1092.0354 | 329.3069 | 277.6723 | 264.8291
1093.0354 | 329.32 | 277.6592 | 264.8779
1094.0354 | 329.3215 | 277.7034 | 264.9142
1095.0354 | 329.3338 | 277.7455 | 264.9596
1096.0354 | 329.37 | 277.7699 | 265.0081
1097.0354 | 329.3583 | 277.812 | 265.0486
1098.0354 | 329.3751 | 277.8416 | 265.0974
1099.0354 | 329.391 | 277.87 | 265.147
1100.0354 | 329.4282 | 277.8764 | 265.1926
1101.0354 | 329.4587 | 277.8997 | 265.2333
1102.0354 | 329.4911 | 277.9068 | 265.2712
1103.0354 | 329.5111 | 277.9005 | 265.3138
1104.0354 | 329.5414 | 277.9094 | 265.356
1105.0354 | 329.5927 | 277.924 | 265.4022
1106.0354 | 329.6122 | 277.9571 | 265.4394
1107.0354 | 329.5788 | 277.9679 | 265.4801
1108.0354 | 329.585 | 277.9882 | 265.5205
1109.0354 | 329.576 | 278.0039 | 265.5715
1110.0354 | 329.5917 | 278.0245 | 265.619
1111.0354 | 329.6279 | 278.0526 | 265.6596
1112.0354 | 329.6685 | 278.088 | 265.7049
1113.0354 | 329.7117 | 278.1011 | 265.7552
1114.0354 | 329.7346 | 278.1188 | 265.7913
1115.0354 | 329.7599 | 278.1652 | 265.8455
1116.0354 | 329.8145 | 278.2061 | 265.8882
1117.0354 | 329.8496 | 278.2127 | 265.9372
1118.0354 | 329.8519 | 278.256 | 265.9758
1119.0354 | 329.8535 | 278.3045 | 266.0186
1120.0354 | 329.8559 | 278.331 | 266.0694
1121.0354 | 329.8814 | 278.3523 | 266.1115
1122.051 | 329.8497 | 278.3781 | 266.1571
1123.0354 | 329.8093 | 278.3963 | 266.1986
1124.0354 | 329.831 | 278.4397 | 266.2418
1125.0354 | 329.843 | 278.4577 | 266.2858
1126.0354 | 329.8667 | 278.4713 | 266.3339
1127.0354 | 329.8444 | 278.4949 | 266.3851
1128.0354 | 329.8198 | 278.5224 | 266.4247
1129.0354 | 329.8269 | 278.554 | 266.4682
1130.0354 | 329.8453 | 278.5816 | 266.5168
1131.0354 | 329.8204 | 278.6022 | 266.5623
1132.0354 | 329.7905 | 278.6362 | 266.6075
1133.0354 | 329.7743 | 278.6525 | 266.6452
1134.0354 | 329.7293 | 278.6827 | 266.6908
1135.0354 | 329.7542 | 278.7035 | 266.731
1136.0354 | 329.7372 | 278.7296 | 266.7784
1137.0354 | 329.7156 | 278.7501 | 266.8223
1138.0354 | 329.6538 | 278.784 | 266.8664
1139.0354 | 329.5711 | 278.8036 | 266.9101
1140.0354 | 329.542 | 278.828 | 266.9577
1141.0354 | 329.5241 | 278.8619 | 267.012
1142.0354 | 329.6275 | 278.8789 | 267.0489
1143.0354 | 330.34 | 278.9171 | 267.1091
1144.0354 | 331.6442 | 278.9398 | 267.1571
1145.0354 | 333.5415 | 278.9708 | 267.1957
1146.0354 | 335.8224 | 279.0189 | 267.2319
1147.0354 | 338.5851 | 279.0534 | 267.2836
1148.0354 | 341.6342 | 279.1143 | 267.3264
1149.0354 | 344.7582 | 279.1815 | 267.3795
1150.0354 | 347.9957 | 279.2556 | 267.4246
1151.0354 | 351.139 | 279.3485 | 267.4724
1152.0354 | 354.0699 | 279.4438 | 267.5236
1153.0354 | 356.7762 | 279.541 | 267.5822
1154.0354 | 359.2173 | 279.6734 | 267.634
1155.0354 | 361.3922 | 279.8008 | 267.6831
1156.0354 | 363.2978 | 279.9446 | 267.7487
1157.0354 | 364.9591 | 280.1244 | 267.8068
1158.0354 | 366.2777 | 280.3177 | 267.8597
1159.0354 | 367.4338 | 280.5051 | 267.9142
1160.0354 | 368.3694 | 280.7093 | 267.9912
1161.0354 | 369.1102 | 280.9291 | 268.0646
1162.0354 | 369.6569 | 281.232 | 268.1419
1163.0354 | 370.0686 | 281.4584 | 268.2076
1164.0354 | 370.403 | 281.6668 | 268.2886
1165.0354 | 370.6742 | 281.8897 | 268.3719
1166.0354 | 370.8005 | 282.1065 | 268.4558
1167.0354 | 370.796 | 282.3427 | 268.5379
1168.0354 | 370.8292 | 282.5908 | 268.6318
1169.0354 | 370.8078 | 282.8198 | 268.7238
1170.0354 | 370.7496 | 283.0503 | 268.8078
1171.0354 | 370.6108 | 283.2802 | 268.8971
1172.0354 | 370.4552 | 283.5372 | 268.9816
1173.0354 | 370.2219 | 283.7822 | 269.0766
1174.0354 | 369.9635 | 284.0411 | 269.1791
1175.0354 | 369.673 | 284.3074 | 269.2817
1176.0354 | 369.3622 | 284.5626 | 269.3752
1177.0354 | 368.998 | 284.8124 | 269.4699
1178.0354 | 368.6095 | 285.0488 | 269.5768
1179.0354 | 368.2363 | 285.2893 | 269.6883
1180.0354 | 367.7995 | 285.5074 | 269.7998
1181.0354 | 367.4006 | 285.7631 | 269.9043
1182.0354 | 367.0302 | 285.998 | 270.0074
1183.0354 | 366.6389 | 286.2218 | 270.1124
1184.0354 | 366.2371 | 286.4393 | 270.2182
1185.0354 | 365.8512 | 286.6506 | 270.3203
1186.0354 | 365.4074 | 286.8625 | 270.4353
1187.0354 | 364.8959 | 287.0502 | 270.5457
1188.0354 | 364.415 | 287.2006 | 270.6506
1189.0354 | 363.9044 | 287.4017 | 270.7642
1190.0354 | 363.406 | 287.5777 | 270.8804
1191.0354 | 362.8985 | 287.7729 | 270.9911
1192.0354 | 362.4175 | 287.9523 | 271.0959
1193.0354 | 361.9597 | 288.1397 | 271.2066
1194.0354 | 361.4528 | 288.3425 | 271.3123
1195.0354 | 360.9626 | 288.5264 | 271.4337
1196.0354 | 360.4799 | 288.6668 | 271.5464
1197.0354 | 359.9774 | 288.8479 | 271.6581
1198.0354 | 359.5074 | 288.9864 | 271.7755
1199.0354 | 359.0283 | 289.1307 | 271.89
1200.0354 | 358.511 | 289.2963 | 272.0172
1201.0354 | 357.998 | 289.4419 | 272.1257
1202.0354 | 357.4935 | 289.6122 | 272.2351
1203.0354 | 356.9696 | 289.7601 | 272.3508
1204.0354 | 356.4113 | 289.9021 | 272.4725
1205.0354 | 355.864 | 290.0331 | 272.5835
1206.0354 | 355.3178 | 290.1533 | 272.6999
1207.0354 | 354.8074 | 290.2707 | 272.812
1208.0354 | 354.2701 | 290.3802 | 272.9125
1209.0354 | 353.7187 | 290.4876 | 273.0232
1210.0354 | 353.223 | 290.5949 | 273.1294
1211.0354 | 352.7189 | 290.6902 | 273.2383
1212.0354 | 352.1765 | 290.7752 | 273.3541
1213.0354 | 351.6982 | 290.8646 | 273.4543
1214.0354 | 351.1912 | 290.9711 | 273.5616
1215.0354 | 350.666 | 291.0454 | 273.6691
1216.0354 | 350.1321 | 291.1586 | 273.7753
1217.0354 | 349.6546 | 291.2505 | 273.8746
1218.0354 | 349.1893 | 291.3578 | 273.9771
1219.0354 | 348.7076 | 291.4253 | 274.0709
1220.0354 | 348.2121 | 291.4927 | 274.1708
1221.0354 | 347.7314 | 291.5678 | 274.2659
1222.0354 | 347.2322 | 291.6574 | 274.3722
1223.0354 | 346.8084 | 291.7436 | 274.4668
1224.0354 | 346.4175 | 291.837 | 274.5734
1225.0354 | 346.0523 | 291.9316 | 274.6753
1226.0354 | 345.7099 | 292.04 | 274.7706
1227.0354 | 345.3762 | 292.1426 | 274.8566
1228.0354 | 345.1416 | 292.2357 | 274.9587
1229.0354 | 344.9242 | 292.316 | 275.0653
1230.0354 | 344.7717 | 292.3977 | 275.1647
1231.0354 | 344.682 | 292.445 | 275.2608
1232.0354 | 344.6953 | 292.4902 | 275.3509
1233.0354 | 344.7238 | 292.5356 | 275.4365
1234.0354 | 344.8031 | 292.5833 | 275.535
1235.0354 | 344.9363 | 292.6093 | 275.6241
1236.0354 | 345.0643 | 292.6383 | 275.7134
1237.0354 | 345.2568 | 292.6687 | 275.8039
1238.0354 | 345.526 | 292.7161 | 275.8924
1239.0354 | 345.7915 | 292.757 | 275.9801
1240.0354 | 346.0664 | 292.808 | 276.0684
1241.0354 | 346.3502 | 292.8543 | 276.1524
1242.0354 | 346.6723 | 292.9043 | 276.2349
1243.0354 | 347.0796 | 292.9423 | 276.3211
1244.0354 | 347.4985 | 292.977 | 276.4029
1245.0354 | 347.9319 | 293.0277 | 276.498
1246.0354 | 348.3641 | 293.0808 | 276.5849
1247.0354 | 348.7336 | 293.1227 | 276.6632
1248.0354 | 349.1461 | 293.1763 | 276.7459
1249.0354 | 349.5835 | 293.2109 | 276.832
1250.0354 | 349.9809 | 293.2476 | 276.9144
1251.0354 | 350.4029 | 293.286 | 276.9994
1252.0354 | 350.7611 | 293.3193 | 277.0765
1253.0354 | 351.1087 | 293.381 | 277.1599
1254.0354 | 351.4251 | 293.4047 | 277.2438
1255.0354 | 351.7267 | 293.4555 | 277.332
1256.0354 | 352.0415 | 293.5216 | 277.4075
1257.0354 | 352.3499 | 293.5849 | 277.4967
1258.0354 | 352.6769 | 293.6322 | 277.5809
1259.0354 | 352.9883 | 293.6857 | 277.6608
1260.0354 | 353.2128 | 293.7444 | 277.7467
1261.0354 | 353.4251 | 293.8235 | 277.8318
1262.0354 | 353.5921 | 293.9121 | 277.9152
1263.0354 | 353.7986 | 293.9938 | 277.9969
1264.0354 | 353.991 | 294.0758 | 278.0861
1265.0354 | 354.1379 | 294.1742 | 278.1739
1266.0354 | 354.263 | 294.2704 | 278.2646
1267.0354 | 354.3876 | 294.3576 | 278.3461
1268.0354 | 354.541 | 294.4353 | 278.4333
1269.0354 | 354.6389 | 294.5172 | 278.5199
1270.0354 | 354.7043 | 294.5923 | 278.6104
1271.0354 | 354.7635 | 294.6779 | 278.694
1272.0354 | 354.8158 | 294.7764 | 278.7876
1273.0354 | 354.8409 | 294.8601 | 278.8726
1274.0354 | 354.8523 | 294.9671 | 278.9615
1275.0354 | 354.8581 | 295.0569 | 279.0493
1276.0354 | 354.8976 | 295.1549 | 279.1411
1277.0354 | 354.9352 | 295.2625 | 279.2238
1278.0354 | 354.9853 | 295.3575 | 279.3097
1279.0354 | 354.9633 | 295.4637 | 279.4026
1280.0354 | 354.8972 | 295.5488 | 279.5001
1281.0354 | 354.8318 | 295.6285 | 279.5887
1282.0354 | 354.7599 | 295.7017 | 279.6789
1283.0354 | 354.7072 | 295.7761 | 279.7671
1284.0354 | 354.6965 | 295.8387 | 279.8498
1285.0354 | 354.6327 | 295.9075 | 279.9452
1286.0354 | 354.6042 | 295.968 | 280.038
1287.0354 | 354.5679 | 296.039 | 280.1339
1288.0354 | 354.5743 | 296.1018 | 280.2272
1289.0354 | 354.5533 | 296.1767 | 280.3241
1290.0354 | 354.52 | 296.2566 | 280.4142
1291.0354 | 354.4743 | 296.3386 | 280.4971
1292.0354 | 354.4214 | 296.4281 | 280.5869
1293.0354 | 354.3824 | 296.5004 | 280.6778
1294.0354 | 354.3632 | 296.5704 | 280.7703
1295.0354 | 354.3295 | 296.6265 | 280.8549
1296.0354 | 354.2898 | 296.6875 | 280.9492
1297.0354 | 354.2284 | 296.7557 | 281.0356
1298.0354 | 354.1679 | 296.8151 | 281.1183
1299.0354 | 354.0892 | 296.8661 | 281.2188
1300.0354 | 354.0745 | 296.9232 | 281.2994
1301.0354 | 354.0504 | 296.9689 | 281.3905
1302.0354 | 353.997 | 297.0008 | 281.4763
1303.0354 | 353.9497 | 297.0319 | 281.558
1304.0354 | 353.9195 | 297.0809 | 281.6465
1305.0354 | 353.9784 | 297.1364 | 281.7397
1306.0354 | 354.0383 | 297.2118 | 281.8207
1307.0354 | 354.0537 | 297.2725 | 281.9132
1308.0354 | 354.0597 | 297.3533 | 281.9965
1309.0354 | 354.0865 | 297.4094 | 282.0768
1310.0354 | 354.1329 | 297.456 | 282.1636
1311.0354 | 354.137 | 297.4855 | 282.2528
1312.0354 | 354.1363 | 297.5652 | 282.3415
1313.0354 | 354.1177 | 297.6356 | 282.4315
1314.0354 | 354.1306 | 297.7049 | 282.5282
1315.0354 | 354.1332 | 297.7608 | 282.6095
1316.0354 | 354.1225 | 297.8336 | 282.6978
1317.0354 | 354.1102 | 297.8837 | 282.7862
1318.0354 | 354.1181 | 297.9484 | 282.8795
1319.0354 | 354.1516 | 298.008 | 282.9753
1320.0354 | 354.1758 | 298.0547 | 283.0652
1321.0354 | 354.179 | 298.1018 | 283.1586
1322.0354 | 354.1185 | 298.1392 | 283.2495
1323.0354 | 354.1293 | 298.16 | 283.3379
1324.0354 | 354.1194 | 298.2038 | 283.4252
1325.0354 | 354.1168 | 298.2215 | 283.5186
1326.0354 | 354.1303 | 298.2825 | 283.61
1327.0354 | 354.1102 | 298.3214 | 283.703
1328.0354 | 354.1026 | 298.389 | 283.7975
1329.0354 | 354.1038 | 298.4553 | 283.8864
1330.0354 | 354.1078 | 298.5126 | 283.968
1331.0354 | 354.1113 | 298.5639 | 284.0485
1332.0354 | 354.1741 | 298.6151 | 284.1264
1333.0354 | 354.2246 | 298.6546 | 284.2199
1334.0354 | 354.2387 | 298.713 | 284.305
1335.0354 | 354.2727 | 298.7736 | 284.3974
1336.0354 | 354.2399 | 298.8373 | 284.4785
1337.0354 | 354.2481 | 298.8774 | 284.5687
1338.0354 | 354.2934 | 298.9009 | 284.6544
1339.0354 | 354.2955 | 298.9446 | 284.7445
1340.0354 | 354.2852 | 298.9899 | 284.8317
1341.0354 | 354.306 | 299.0338 | 284.9201
1342.0354 | 354.3391 | 299.0847 | 285.0035
1343.0354 | 354.349 | 299.1252 | 285.0853
1344.0354 | 354.3449 | 299.1871 | 285.1783
1345.0354 | 354.3262 | 299.2721 | 285.2635
1346.0354 | 354.2982 | 299.3407 | 285.355
1347.0354 | 354.3183 | 299.414 | 285.4423
1348.0354 | 354.3088 | 299.4712 | 285.5354
1349.0354 | 354.3673 | 299.5519 | 285.6221
1350.0354 | 354.4174 | 299.635 | 285.7168
1351.0354 | 354.4325 | 299.6992 | 285.8176
1352.0354 | 354.4317 | 299.7611 | 285.9149
1353.0354 | 354.4221 | 299.7909 | 286.005
1354.0354 | 354.4342 | 299.8539 | 286.0865
1355.0354 | 354.4862 | 299.9041 | 286.178
1356.0354 | 354.5233 | 299.9635 | 286.2676
1357.0354 | 354.4926 | 300.0026 | 286.3523
1358.0354 | 354.471 | 300.0376 | 286.4334
1359.0354 | 354.4553 | 300.086 | 286.5081
1360.0354 | 354.4676 | 300.1393 | 286.5933
1361.0354 | 354.5211 | 300.1855 | 286.6806
1362.0354 | 354.5467 | 300.2218 | 286.759
1363.0354 | 354.5813 | 300.249 | 286.8417
1364.0354 | 354.553 | 300.323 | 286.9163
1365.0354 | 354.5422 | 300.374 | 286.9966
1366.0354 | 354.5896 | 300.4497 | 287.0838
1367.0354 | 354.6084 | 300.515 | 287.1597
1368.0354 | 354.6164 | 300.5728 | 287.246
1369.0354 | 354.5844 | 300.6266 | 287.3301
1370.0354 | 354.6126 | 300.7013 | 287.4254
1371.0354 | 354.6183 | 300.7682 | 287.5115
1372.0354 | 354.6177 | 300.8271 | 287.6019
1373.0354 | 354.6465 | 300.8872 | 287.6901
1374.0354 | 354.6935 | 300.9332 | 287.7769
1375.0354 | 354.714 | 300.9901 | 287.8569
1376.0354 | 354.7348 | 301.0308 | 287.9419
1377.0354 | 354.7398 | 301.0945 | 288.0287
1378.0354 | 354.7409 | 301.1406 | 288.1094
1379.0354 | 354.7201 | 301.1781 | 288.1974
1380.0354 | 354.7076 | 301.2382 | 288.2816
1381.0354 | 354.7018 | 301.2889 | 288.3625
1382.0354 | 354.7202 | 301.3156 | 288.4461
1383.0354 | 354.7096 | 301.3669 | 288.5318
1384.0354 | 354.6652 | 301.4269 | 288.6041
1385.0354 | 354.6584 | 301.5108 | 288.6958
1386.0354 | 354.6767 | 301.5688 | 288.7769
1387.0354 | 354.6586 | 301.6359 | 288.8681
1388.0354 | 354.6948 | 301.7015 | 288.9559
1389.0354 | 354.6821 | 301.7857 | 289.036
1390.0354 | 354.6433 | 301.8646 | 289.1278
1391.0354 | 354.5789 | 301.9396 | 289.2141
1392.0354 | 354.5113 | 302.0071 | 289.2921
1393.0354 | 354.4913 | 302.0711 | 289.3626
1394.0354 | 354.4698 | 302.1235 | 289.4503
1395.0354 | 354.4668 | 302.1642 | 289.5431
1396.0354 | 354.4771 | 302.2148 | 289.6373
1397.0354 | 354.4859 | 302.2562 | 289.7211
1398.0354 | 354.5154 | 302.3028 | 289.7977
1399.0354 | 354.4993 | 302.3367 | 289.8832
1400.0354 | 354.4689 | 302.4004 | 289.9695
1401.0354 | 354.4217 | 302.4573 | 290.0638
1402.0354 | 354.4895 | 302.4897 | 290.1423
1403.0354 | 354.4903 | 302.5263 | 290.2211
1404.0354 | 354.5082 | 302.5617 | 290.3099
1405.0354 | 354.5068 | 302.5924 | 290.4036
1406.0354 | 354.4877 | 302.601 | 290.4825
1407.0354 | 354.4946 | 302.64 | 290.5704
1408.0354 | 354.4655 | 302.681 | 290.6655
1409.0354 | 354.4915 | 302.722 | 290.7559
1410.0354 | 354.465 | 302.7736 | 290.8399
1411.0354 | 354.4568 | 302.8343 | 290.9217
1412.0354 | 354.4786 | 302.8998 | 291.0114
1413.0354 | 354.5111 | 302.9611 | 291.0889
1414.0354 | 354.5021 | 303.0118 | 291.1769
1415.0354 | 354.4875 | 303.0687 | 291.2684
1416.0354 | 354.4896 | 303.1052 | 291.357
1417.0354 | 354.5069 | 303.1622 | 291.4349
1418.0354 | 354.5023 | 303.2073 | 291.5178
1419.0354 | 354.5108 | 303.2565 | 291.5983
1420.0354 | 354.4983 | 303.3153 | 291.6791
1421.0354 | 354.4343 | 303.367 | 291.7727
1422.0354 | 354.4245 | 303.4278 | 291.8662
1423.0354 | 354.4044 | 303.4649 | 291.9528
1424.0354 | 354.373 | 303.5254 | 292.0405
1425.0354 | 354.2895 | 303.5816 | 292.1265
1426.0354 | 354.2076 | 303.6319 | 292.2157
1427.0354 | 354.1747 | 303.6978 | 292.3043
1428.0354 | 354.1717 | 303.7407 | 292.3948
1429.0354 | 354.1105 | 303.7934 | 292.4802
1430.0354 | 354.0604 | 303.8351 | 292.5674
1431.0354 | 354.0212 | 303.881 | 292.6594
1432.0354 | 354.0311 | 303.9371 | 292.7404
1433.0354 | 354.0003 | 303.9779 | 292.8422
1434.0354 | 353.9593 | 304.0341 | 292.9295
1435.0354 | 353.9461 | 304.1034 | 293.0076
1436.0354 | 353.9451 | 304.1829 | 293.0975
1437.0354 | 353.9101 | 304.241 | 293.1881
1438.0354 | 353.8743 | 304.3131 | 293.274
1439.0354 | 353.8586 | 304.3757 | 293.3549
1440.0354 | 353.9185 | 304.4444 | 293.437
1441.0354 | 353.8847 | 304.5195 | 293.5146
1442.0354 | 353.8879 | 304.5821 | 293.5961
1443.0354 | 353.8789 | 304.6419 | 293.6842
1444.0354 | 353.9122 | 304.715 | 293.7668
1445.0354 | 353.9507 | 304.7635 | 293.8496
1446.0354 | 353.9793 | 304.8302 | 293.9341
1447.0354 | 353.9984 | 304.8772 | 294.0227
1448.0354 | 354.0377 | 304.9308 | 294.1029
1449.0354 | 354.0507 | 304.9751 | 294.1946
1450.0354 | 354.0533 | 305.037 | 294.2717
1451.0354 | 354.0752 | 305.091 | 294.3527
1452.0354 | 354.1025 | 305.1451 | 294.4406
1453.0354 | 354.1358 | 305.1978 | 294.5301
1454.0354 | 354.2095 | 305.2291 | 294.6199
1455.0354 | 354.2929 | 305.2922 | 294.697
1456.0354 | 354.2554 | 305.3442 | 294.777
1457.0354 | 354.2671 | 305.4056 | 294.8596
1458.0354 | 354.3165 | 305.4604 | 294.9443
1459.0354 | 354.3095 | 305.5286 | 295.0268
1460.0354 | 354.3177 | 305.5851 | 295.1063
1461.0354 | 354.3796 | 305.6543 | 295.1897
1462.0354 | 354.4553 | 305.7212 | 295.2778
1463.0354 | 354.4938 | 305.7904 | 295.3608
1464.0354 | 354.5286 | 305.8399 | 295.4454
1465.0354 | 354.5444 | 305.889 | 295.5289
1466.0354 | 354.5099 | 305.9311 | 295.6015
1467.0354 | 354.5052 | 305.9704 | 295.6855
1468.0354 | 354.5145 | 306.0102 | 295.7742
1469.0354 | 354.485 | 306.0587 | 295.8512
1470.0354 | 354.473 | 306.105 | 295.9262
1471.0354 | 354.4744 | 306.1501 | 296.0074
1472.0354 | 354.475 | 306.1987 | 296.0928
1473.0354 | 354.5091 | 306.2542 | 296.1715
1474.0354 | 354.5282 | 306.3033 | 296.2543
1475.0354 | 354.53 | 306.3704 | 296.3421
1476.0354 | 354.5 | 306.4205 | 296.4316
1477.0354 | 354.5069 | 306.4777 | 296.501
1478.0354 | 354.5111 | 306.5496 | 296.5799
1479.0354 | 354.5238 | 306.6108 | 296.6593
1480.0354 | 354.4922 | 306.6726 | 296.7337
1481.0354 | 354.445 | 306.7268 | 296.8079
1482.0354 | 354.4516 | 306.7815 | 296.8887
1483.0354 | 354.479 | 306.8366 | 296.9601
1484.0354 | 354.4874 | 306.9012 | 297.0367
1485.0354 | 354.4931 | 306.9822 | 297.1315
1486.0354 | 354.5324 | 307.0472 | 297.2077
1487.0354 | 354.582 | 307.1069 | 297.2877
1488.0354 | 354.5692 | 307.166 | 297.3622
1489.0354 | 354.6091 | 307.2316 | 297.4309
1490.0354 | 354.6062 | 307.2962 | 297.5103
1491.0354 | 354.6015 | 307.3567 | 297.5875
1492.0354 | 354.5991 | 307.4221 | 297.6609
1493.0354 | 354.5866 | 307.4889 | 297.7482
1494.0354 | 354.5521 | 307.5479 | 297.8285
1495.0354 | 354.5506 | 307.6053 | 297.9075
1496.0354 | 354.5749 | 307.6415 | 297.9844
1497.0354 | 354.5971 | 307.7052 | 298.0558
1498.0354 | 354.5928 | 307.7583 | 298.138
1499.0354 | 354.5637 | 307.7981 | 298.2199
1500.0354 | 354.517 | 307.8536 | 298.2997
1501.0354 | 354.4888 | 307.8999 | 298.3751
1502.0354 | 354.471 | 307.9363 | 298.4473
1503.0354 | 354.4432 | 307.9815 | 298.5297
1504.0354 | 354.4078 | 308.0177 | 298.6109
1505.0354 | 354.3777 | 308.0727 | 298.6867
1506.0354 | 354.4347 | 308.1168 | 298.7606
1507.0354 | 354.4478 | 308.1576 | 298.8341
1508.0354 | 354.4163 | 308.2068 | 298.9135
1509.0354 | 354.3753 | 308.2649 | 298.9771
1510.0354 | 354.3714 | 308.331 | 299.0436
1511.0354 | 354.3443 | 308.3751 | 299.1239
1512.0354 | 354.302 | 308.4257 | 299.194
1513.0354 | 354.3084 | 308.4605 | 299.2645
1514.0354 | 354.317 | 308.4868 | 299.3341
1515.0354 | 354.2746 | 308.5257 | 299.4054
1516.0354 | 354.2324 | 308.5631 | 299.4749
1517.0354 | 354.2211 | 308.6173 | 299.5451
1518.0354 | 354.2179 | 308.6576 | 299.6138
1519.0354 | 354.1539 | 308.7144 | 299.6858
1520.0354 | 354.1457 | 308.7428 | 299.7618
1521.0354 | 354.1694 | 308.7903 | 299.8251
1522.0354 | 354.242 | 308.8295 | 299.8945
1523.0354 | 354.3621 | 308.8624 | 299.9643
1524.0354 | 354.3858 | 308.8974 | 300.0337
1525.0354 | 354.4301 | 308.9477 | 300.0997
1526.0354 | 354.4878 | 308.9913 | 300.1808
1527.0354 | 354.5517 | 309.0453 | 300.2526
1528.0354 | 354.581 | 309.112 | 300.3206
1529.0354 | 354.6124 | 309.1624 | 300.4006
1530.0354 | 354.6065 | 309.2172 | 300.4723
1531.0354 | 354.5969 | 309.2773 | 300.5503
1532.0354 | 354.6086 | 309.3359 | 300.621
1533.0354 | 354.6305 | 309.4035 | 300.6924
1534.0354 | 354.6161 | 309.4537 | 300.7557
1535.0354 | 354.5636 | 309.5143 | 300.8397
1536.0354 | 354.5135 | 309.5703 | 300.9149
1537.0354 | 354.524 | 309.6216 | 300.9815
1538.0354 | 354.4986 | 309.6701 | 301.0589
1539.0354 | 354.5418 | 309.7261 | 301.1336
1540.0354 | 354.5468 | 309.7749 | 301.2097
1541.0354 | 354.5294 | 309.8211 | 301.2786
1542.0354 | 354.5278 | 309.8801 | 301.3407
1543.0354 | 354.4672 | 309.9205 | 301.4136
1544.0354 | 354.4732 | 309.9776 | 301.4856
1545.0354 | 354.5251 | 310.0179 | 301.5598
1546.0354 | 354.5064 | 310.0719 | 301.6229
1547.0354 | 354.4225 | 310.1163 | 301.6906
1548.0354 | 354.4308 | 310.1708 | 301.7719
1549.0354 | 354.4319 | 310.2274 | 301.8487
1550.0354 | 354.4586 | 310.2753 | 301.9171
1551.0354 | 354.4476 | 310.3231 | 301.9901
1552.0354 | 354.4177 | 310.3859 | 302.0621
1553.0354 | 354.3906 | 310.437 | 302.1323
1554.0354 | 354.3808 | 310.4946 | 302.1977
1555.0354 | 354.3787 | 310.5463 | 302.2639
1556.0354 | 354.3777 | 310.5826 | 302.3249
1557.0354 | 354.3599 | 310.6336 | 302.3922
1558.0354 | 354.3476 | 310.6716 | 302.4496
1559.0354 | 354.3051 | 310.7272 | 302.5179
1560.0354 | 354.3217 | 310.7831 | 302.5775
1561.0354 | 354.3496 | 310.8285 | 302.6491
1562.0354 | 354.3403 | 310.8883 | 302.7167
1563.0354 | 354.3383 | 310.9387 | 302.7805
1564.0354 | 354.3333 | 310.9793 | 302.8465
1565.0354 | 354.3463 | 311.0297 | 302.9126
1566.0354 | 354.3783 | 311.0885 | 302.9842
1567.0354 | 354.3274 | 311.1466 | 303.0466
1568.0354 | 354.279 | 311.2107 | 303.1095
1569.0354 | 354.3007 | 311.2708 | 303.1746
1570.0354 | 354.3418 | 311.3301 | 303.2385
1571.0354 | 354.357 | 311.3997 | 303.3097
1572.0354 | 354.3459 | 311.4603 | 303.3714
1573.0354 | 354.3539 | 311.5277 | 303.4334
1574.0354 | 354.4334 | 311.5743 | 303.508
1575.0354 | 354.4916 | 311.6371 | 303.5729
1576.0354 | 354.5332 | 311.6787 | 303.6314
1577.0354 | 354.5633 | 311.721 | 303.6912
1578.0354 | 354.6025 | 311.7688 | 303.7534
1579.0354 | 354.5754 | 311.8174 | 303.8152
1580.0354 | 354.5761 | 311.8573 | 303.88
1581.0354 | 354.5777 | 311.9078 | 303.9396
1582.0354 | 354.5909 | 311.9332 | 304.0043
1583.0354 | 354.6039 | 311.998 | 304.0511
1584.0354 | 354.6203 | 312.0409 | 304.1077
1585.0354 | 354.6725 | 312.0677 | 304.163
1586.0354 | 354.6734 | 312.107 | 304.2321
1587.0354 | 354.6378 | 312.1432 | 304.2915
1588.0354 | 354.6335 | 312.1824 | 304.3541
1589.0354 | 354.6473 | 312.2182 | 304.4023
1590.0354 | 354.6193 | 312.2751 | 304.4651
1591.0354 | 354.5836 | 312.3125 | 304.5249
1592.0354 | 354.5558 | 312.3559 | 304.5875
1593.0354 | 354.5896 | 312.4067 | 304.656
1594.0354 | 354.6172 | 312.4445 | 304.7192
1595.0354 | 354.6508 | 312.4823 | 304.7773
1596.0354 | 354.6735 | 312.5146 | 304.8357
1597.0354 | 354.6997 | 312.5683 | 304.9039
1598.0354 | 354.6744 | 312.6231 | 304.9793
1599.0354 | 354.661 | 312.6653 | 305.0376
1600.0354 | 354.6149 | 312.7269 | 305.0948
1601.0354 | 354.6036 | 312.7648 | 305.1607
1602.0354 | 354.6016 | 312.7988 | 305.2153
1603.0354 | 354.5994 | 312.8357 | 305.278
1604.0354 | 354.5801 | 312.8591 | 305.3348
1605.0354 | 354.5653 | 312.8888 | 305.3996
1606.0354 | 354.5844 | 312.9209 | 305.4564
1607.0354 | 354.6095 | 312.9468 | 305.5102
1608.0354 | 354.5933 | 312.9654 | 305.5759
1609.0354 | 354.5898 | 313.0098 | 305.6347
1610.0354 | 354.6237 | 313.0355 | 305.7063
1611.0354 | 354.632 | 313.0851 | 305.7714
1612.0354 | 354.6486 | 313.1136 | 305.8365
1613.0354 | 354.669 | 313.1618 | 305.9015
1614.0354 | 354.6485 | 313.2095 | 305.9621
1615.0354 | 354.6389 | 313.2669 | 306.0213
1616.0354 | 354.6006 | 313.3108 | 306.0782
1617.0354 | 354.5529 | 313.3554 | 306.1318
1618.0354 | 354.5065 | 313.3963 | 306.1792
1619.0354 | 354.501 | 313.4378 | 306.2389
1620.0354 | 354.4916 | 313.473 | 306.2914
1621.0354 | 354.4705 | 313.5076 | 306.353
1622.0354 | 354.4172 | 313.5456 | 306.4156
1623.0354 | 354.3668 | 313.5877 | 306.4677
1624.0354 | 354.3509 | 313.6321 | 306.5216
1625.0354 | 354.3503 | 313.6742 | 306.5741
1626.0354 | 354.2444 | 313.7256 | 306.6261
1627.0354 | 354.1639 | 313.7772 | 306.6903
1628.0354 | 354.1564 | 313.8184 | 306.7447
1629.0354 | 354.1281 | 313.8683 | 306.8046
1630.0354 | 354.1144 | 313.937 | 306.8837
1631.0354 | 354.0319 | 313.9999 | 306.9396
1632.0354 | 354.0419 | 314.0693 | 306.9676
1633.0354 | 354.0837 | 314.133 | 307.0836
1634.0354 | 354.0647 | 314.1802 | 307.1478
1635.0354 | 353.9724 | 314.242 | 307.2118
1636.0354 | 353.8682 | 314.2959 | 307.2631
1637.0354 | 353.7923 | 314.3395 | 307.3373
1638.0354 | 353.7951 | 314.393 | 307.4001
1639.0354 | 353.834 | 314.4381 | 307.4591
1640.0354 | 353.8489 | 314.4819 | 307.5186
1641.0354 | 353.8529 | 314.5283 | 307.5841
1642.0354 | 353.9117 | 314.5683 | 307.6434
1643.0354 | 353.9648 | 314.6094 | 307.7154
1644.0354 | 353.989 | 314.6546 | 307.7677
1645.0354 | 354.001 | 314.6908 | 307.8376
1646.0354 | 354.0267 | 314.7161 | 307.9012
1647.0354 | 354.1052 | 314.7398 | 307.9543
1648.0354 | 354.1383 | 314.7864 | 308.0192
1649.0354 | 354.1633 | 314.819 | 308.0945
1650.0354 | 354.1509 | 314.8395 | 308.1727
1651.0354 | 354.1354 | 314.8765 | 308.255
1652.0354 | 354.1272 | 314.928 | 308.3212
1653.0354 | 354.1081 | 314.9505 | 308.3858
1654.0354 | 354.0719 | 314.9991 | 308.4564
1655.0354 | 354.0898 | 315.0433 | 308.5192
1656.0354 | 354.0836 | 315.0867 | 308.5844
1657.0354 | 354.0984 | 315.1216 | 308.656
1658.0354 | 354.1133 | 315.173 | 308.7215
1659.0354 | 354.1103 | 315.2203 | 308.7836
1660.0354 | 354.156 | 315.2724 | 308.8434
1661.0354 | 354.1419 | 315.3094 | 308.9025
1662.0354 | 354.0596 | 315.3555 | 308.9567
1663.0354 | 353.9008 | 315.3997 | 309.0148
1664.0354 | 353.7684 | 315.4584 | 309.0763
1665.0354 | 353.6264 | 315.5069 | 309.1272
1666.0354 | 353.4811 | 315.5422 | 309.1774