## Test Conditions
DESIREE-FIRE Test Number 11 - Circuit Data Data Only
Test Date: | 2009-07-22
DCSim DAQ Start Time | 12:22
DCSim Time for Synchronization | 12:29
Heat Source Synchronization | 8:33 | hours:minutes:seconds
Heat Source DAQ Start Time | 12:21
Fire Time | 12:33
Offset | 0:12 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 715 | seconds
Heat Source Offset | 0:12 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 750 | seconds
Heat Source Stop Time | 13:20
Test Duration | 0:47 | hours:minutes:seconds
| 2795 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC25 in the Temperature Data File
Large Coil | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC25 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.35938 | 123.2574 | -58.2275 | 64.7552 | 0.61387 | 0.022053 | 0.054947 | -0.0024082 | 0.068351 | 0.011163 | 0.0067127 | 0.46419 | 0.014451 | 0.066941 | 0.069098 | -0.0050469 | 0.00096301 | 64.8376 | -58.2367 | -0.09613 | -58.461 | 64.7964 | -58.2504 | -58.3191 | -58.1406 | -0.032043 | -58.4976 | 64.8056 | 64.7552 | -58.2733 | -58.3466 | -0.022888 | -0.091553 | 0.041199 | -0.009155 | -0.23346 | -0.14191 | 0.082397 | -0.045776 | -0.11902 | 0.050354 | 0.086975 | -0.27008 | -0.15106 | 0 | 123.024 | 123.0652 | 58.1314 | -123.0743 | 123.0331 | 122.9828 | 58.1955 | -123.1018
0.64062 | 123.2758 | -58.2321 | 64.7278 | 0.61387 | 0.00069119 | 0.065628 | -0.0077492 | 0.08544 | 0.0058221 | 0.0024397 | 0.54048 | -0.0058434 | 0.069078 | 0.06269 | 0.0013611 | 0.006304 | 64.8926 | -58.1268 | -0.013733 | -58.4061 | 64.7369 | -58.2687 | -58.2504 | -58.1131 | 0.068665 | -58.4427 | 64.7781 | 64.7049 | -58.2458 | -58.342 | -0.036621 | -0.01831 | 0.009155 | 0.10529 | -0.17395 | -0.15564 | 0.16479 | -0.013733 | -0.10986 | 0.050354 | 0.11902 | -0.21057 | -0.10071 | -0.022888 | 122.9691 | 123.1247 | 58.2184 | -122.9782 | 123.0103 | 122.937 | 58.3008 | -123.0698
1.7031 | 123.2346 | -58.2138 | 64.8148 | -0.17959 | 0.01244 | 0.067764 | 0.0018638 | 0.079032 | 0.011163 | 0.0045757 | -0.26824 | 0.011247 | 0.063737 | 0.065894 | 0.01311 | 0.00096301 | 64.888 | -58.1772 | -0.018311 | -58.4106 | 64.8285 | -58.2458 | -58.2916 | -58.1451 | 0.082397 | -58.493 | 64.8514 | 64.769 | -58.2321 | -58.3374 | -0.032044 | -0.07782 | 0.013733 | 0.036621 | -0.19684 | -0.11902 | 0.073242 | -0.018311 | -0.1236 | 0.036621 | 0.068664 | -0.27924 | -0.15564 | -0.045776 | 123.0423 | 123.1018 | 58.1955 | -123.1064 | 123.0652 | 122.9828 | 58.2962 | -123.1522
2.6406 | 123.1613 | -58.2275 | 64.8102 | 0.2324 | 0.018849 | 0.075241 | -0.0024082 | 0.072623 | 0.016503 | -0.00076433 | 0.44893 | -0.0015704 | 0.075486 | 0.064826 | 0.01311 | 0.009508 | 64.7919 | -58.2642 | -0.13733 | -58.4793 | 64.7964 | -58.2733 | -58.3328 | -58.2413 | -0.068665 | -58.5754 | 64.8285 | 64.7552 | -58.287 | -58.3694 | -0.045776 | -0.10529 | -0.013733 | -0.036621 | -0.25177 | -0.14648 | -0.018311 | -0.059509 | -0.14191 | 0.01831 | -0.013733 | -0.3479 | -0.20599 | -0.054932 | 123.024 | 123.0194 | 58.0902 | -123.143 | 123.056 | 122.9828 | 58.1589 | -123.1796
3.7031 | 123.2117 | -58.223 | 64.8056 | -0.13381 | 0.0038952 | 0.056015 | -0.0088172 | 0.069419 | 0.010095 | 0.010985 | -0.06987 | 0.0091106 | 0.080827 | 0.072303 | -0.00077485 | -0.00010499 | 64.8605 | -58.1635 | 0.009155 | -58.4015 | 64.8102 | -58.2321 | -58.287 | -58.168 | 0.091553 | -58.4839 | 64.8468 | 64.769 | -58.2413 | -58.3374 | -0.009156 | -0.064087 | 0.004578 | 0.059509 | -0.17853 | -0.11444 | 0.054932 | -0.018311 | -0.11444 | 0.041199 | 0.054931 | -0.26093 | -0.14649 | -0.036621 | 123.0331 | 123.0835 | 58.2321 | -123.0927 | 123.0698 | 122.9919 | 58.3145 | -123.143
4.6406 | 123.1384 | -58.2504 | 64.7919 | 0.53758 | 0.011372 | 0.063492 | -0.0024082 | 0.079032 | 0.0079581 | 0.0045757 | 0.38789 | 0.010179 | 0.063737 | 0.065894 | -0.0082519 | 0.007372 | 64.7644 | -58.2962 | -0.12817 | -58.4976 | 64.8056 | -58.2825 | -58.3054 | -58.2367 | -0.073242 | -58.5709 | 64.8285 | 64.7552 | -58.2962 | -58.3786 | -0.032044 | -0.054932 | 0.013733 | -0.045777 | -0.24719 | -0.19226 | -0.027466 | -0.045777 | -0.12817 | 0.036621 | 0.013733 | -0.32043 | -0.19226 | -0.036621 | 123.056 | 123.0148 | 58.1223 | -123.0972 | 123.0789 | 123.0057 | 58.1772 | -123.1705
5.7031 | 123.1934 | -58.2092 | 64.8285 | -0.33217 | -0.0099898 | 0.067764 | 0.0029318 | 0.084372 | -0.0069949 | -0.0018323 | -0.2072 | 0.0069746 | 0.059465 | 0.052009 | -0.0050469 | 0.009508 | 64.8102 | -58.1863 | -0.027466 | -58.4381 | 64.8331 | -58.2504 | -58.2962 | -58.1909 | 0.064087 | -58.5205 | 64.8926 | 64.8056 | -58.2321 | -58.3374 | -0.041198 | -0.086975 | 0.004578 | 0.022889 | -0.22888 | -0.14191 | -0.01831 | -0.022888 | -0.12817 | 0.064087 | 0.018311 | -0.31128 | -0.18311 | -0.022888 | 123.0423 | 123.0194 | 58.1818 | -123.1247 | 123.1018 | 123.0148 | 58.2733 | -123.1659
6.6406 | 123.2117 | -58.2596 | 64.7781 | 0.4918 | 0.016713 | 0.061355 | 0.0093408 | 0.069419 | 0.0079581 | -0.010377 | 0.35738 | 0.013383 | 0.065873 | 0.057349 | -0.00077485 | 0.009508 | 64.7644 | -58.2687 | -0.15106 | -58.4885 | 64.7919 | -58.2825 | -58.3099 | -58.2367 | -0.073242 | -58.5617 | 64.8605 | 64.7461 | -58.2916 | -58.3603 | -0.022888 | -0.050354 | 0.013733 | -0.009155 | -0.22888 | -0.17853 | -0.013733 | -0.032043 | -0.10071 | 0.082398 | 0.022889 | -0.30212 | -0.20142 | -0.032043 | 123.0515 | 123.024 | 58.1085 | -123.0881 | 123.1201 | 123.0057 | 58.1863 | -123.1384
7.6406 | 123.1476 | -58.2458 | 64.7919 | 0.47654 | 0.0049632 | 0.061355 | 0.0061368 | 0.053397 | 0.0058221 | 0.0077807 | 0.41841 | 0.0080426 | 0.06801 | 0.066962 | -0.0050469 | 0.006304 | 64.7369 | -58.2733 | -0.14648 | -58.5251 | 64.8056 | -58.2596 | -58.3099 | -58.2413 | -0.059509 | -58.5617 | 64.8376 | 64.7827 | -58.2779 | -58.3878 | -0.013733 | -0.064087 | 0.013733 | -0.027465 | -0.27923 | -0.21515 | -0.054932 | -0.032043 | -0.14191 | 0.045776 | 0.004578 | -0.31586 | -0.17395 | -0.009155 | 123.0515 | 122.9828 | 58.0994 | -123.1018 | 123.0835 | 123.0286 | 58.1863 | -123.1796
8.6406 | 123.2025 | -58.2596 | 64.7873 | 0.4918 | 0.0049632 | 0.056015 | -0.0013402 | 0.083304 | 0.017572 | 0.0035077 | 0.52522 | 0.0091106 | 0.062669 | 0.078712 | 0.0024291 | 0.010577 | 64.7919 | -58.2733 | -0.14191 | -58.4747 | 64.7827 | -58.2504 | -58.3191 | -58.2184 | -0.064087 | -58.5617 | 64.8468 | 64.7736 | -58.2687 | -58.374 | 0.009156 | -0.059509 | -0.004577 | -0.013732 | -0.21515 | -0.15564 | 0.004578 | -0.009155 | -0.11444 | 0.05951 | 0.041199 | -0.30212 | -0.18768 | -0.013732 | 123.0423 | 123.0515 | 58.1177 | -123.1064 | 123.1064 | 123.0331 | 58.1955 | -123.1613
9.6406 | 123.23 | -58.2321 | 64.7919 | 0.14085 | 0.014576 | 0.066696 | -0.010953 | 0.069419 | 0.0090271 | 0.012053 | 0.15901 | -0.0015704 | 0.069078 | 0.063758 | 0.0034971 | 0.005236 | 64.8514 | -58.1955 | -0.041199 | -58.4335 | 64.8056 | -58.255 | -58.2962 | -58.1909 | 0 | -58.548 | 64.8605 | 64.7736 | -58.2825 | -58.3374 | -0.022888 | -0.064087 | 0.013733 | 0.036621 | -0.20142 | -0.13733 | 0.059509 | -0.050354 | -0.10528 | 0.068665 | 0.041199 | -0.31586 | -0.21057 | -0.01831 | 123.0377 | 123.0835 | 58.1909 | -123.0881 | 123.0927 | 123.0057 | 58.2321 | -123.1293
10.6406 | 123.175 | -58.2458 | 64.8102 | 0.40025 | -0.00037681 | 0.061355 | 0.0018638 | 0.065146 | 0.011163 | 0.0024397 | 0.2353 | 0.0027016 | 0.063737 | 0.059485 | 0.0024291 | 0.009508 | 64.8056 | -58.2321 | -0.082397 | -58.4473 | 64.8102 | -58.2413 | -58.3054 | -58.2321 | -0.045776 | -58.5388 | 64.856 | 64.7873 | -58.2779 | -58.3557 | 0.004578 | -0.059509 | 0 | 0.013733 | -0.20142 | -0.14191 | -0.004578 | -0.032043 | -0.10986 | 0.045776 | 0.013733 | -0.29297 | -0.1831 | -0.022889 | 123.056 | 123.0515 | 58.1635 | -123.1155 | 123.1018 | 123.0331 | 58.2001 | -123.1659
11.6406 | 123.1705 | -58.2413 | 64.8193 | 0.17137 | 0.017781 | 0.062424 | 0.00079576 | 0.061942 | 0.0068901 | 0.0045757 | 0.28108 | 0.02086 | 0.074418 | 0.058417 | 0.0056341 | 0.004168 | 64.8193 | -58.2138 | -0.054932 | -58.4473 | 64.7873 | -58.2504 | -58.2733 | -58.2092 | 0.009155 | -58.5342 | 64.8468 | 64.7873 | -58.2596 | -58.3603 | -0.009155 | -0.032043 | -0.032044 | 0.027466 | -0.20599 | -0.17395 | 0 | -0.018311 | -0.11902 | 0.027466 | 0.032043 | -0.29297 | -0.17395 | -0.032044 | 123.0286 | 123.0606 | 58.1863 | -123.0927 | 123.0881 | 123.0286 | 58.2504 | -123.1796
12.7031 | 123.175 | -58.2367 | 64.8285 | -0.2864 | 0.0017592 | 0.078445 | -0.0013402 | 0.077964 | -0.016608 | -0.0029003 | -0.16142 | 0.0048376 | 0.06801 | 0.077643 | -0.012524 | 0.005236 | 64.8331 | -58.136 | 0.050354 | -58.3923 | 64.7964 | -58.2321 | -58.2504 | -58.1909 | 0.064087 | -58.4839 | 64.8605 | 64.7873 | -58.2642 | -58.3237 | 0.004577 | -0.013733 | -0.032043 | 0.10071 | -0.15564 | -0.14191 | 0.004578 | -0.027466 | -0.086975 | 0.032044 | 0.045776 | -0.24719 | -0.16022 | -0.041199 | 123.0331 | 123.0698 | 58.287 | -123.0789 | 123.0972 | 123.024 | 58.3008 | -123.1522
13.6406 | 123.1796 | -58.2413 | 64.7964 | 0.38499 | 0.047688 | 0.053879 | 0.00079576 | 0.075827 | 0.011163 | 0.0077807 | 0.097976 | 0.0059056 | 0.065873 | 0.073371 | 0.0013611 | -0.004377 | 64.8102 | -58.2184 | -0.073242 | -58.4564 | 64.801 | -58.2458 | -58.3054 | -58.223 | -0.018311 | -58.548 | 64.8651 | 64.769 | -58.2916 | -58.3694 | -0.004578 | -0.064087 | 0.004577 | 0.022888 | -0.21515 | -0.15106 | 0.013733 | -0.050354 | -0.12817 | 0.068664 | 0.018311 | -0.3067 | -0.17853 | -0.027466 | 123.0423 | 123.0515 | 58.168 | -123.1018 | 123.1064 | 123.0103 | 58.223 | -123.1659
14.6406 | 123.1338 | -58.2733 | 64.7827 | 0.3087 | 0.0038952 | 0.058151 | 0.0018638 | 0.072623 | 0.0068901 | 0.0013717 | 0.18953 | 0.0059056 | 0.078691 | 0.073371 | 0.0013611 | -0.00010499 | 64.8285 | -58.2047 | -0.059509 | -58.4656 | 64.801 | -58.287 | -58.3008 | -58.2184 | 0.004578 | -58.5388 | 64.8422 | 64.7736 | -58.2825 | -58.3923 | -0.013733 | -0.027466 | 0.01831 | 0.068664 | -0.19226 | -0.16479 | 0.045776 | -0.009156 | -0.11902 | 0.059509 | 0.054931 | -0.2655 | -0.14648 | -0.009155 | 123.0743 | 123.1018 | 58.2138 | -123.0835 | 123.1155 | 123.0469 | 58.2779 | -123.175
15.7031 | 123.317 | -58.2047 | 64.7919 | 0.15611 | -0.028148 | 0.096603 | -0.016294 | 0.0801 | -0.030494 | -0.0082413 | 0.26582 | -0.0015704 | 0.053056 | 0.066962 | -0.0039789 | 0.0031 | 64.8514 | -58.0948 | 0.050354 | -58.3832 | 64.7736 | -58.2047 | -58.255 | -58.0948 | 0.13733 | -58.3832 | 64.801 | 64.7507 | -58.2413 | -58.3237 | 0 | -0.050354 | -0.01831 | 0.10986 | -0.17853 | -0.12817 | 0.059509 | -0.036621 | -0.11902 | 0.009155 | 0.10986 | -0.17853 | -0.05951 | -0.041199 | 122.9782 | 123.056 | 58.255 | -123.0469 | 123.0057 | 122.9553 | 58.342 | -123.1155
16.6406 | 123.2025 | -58.2184 | 64.801 | 0.00352 | 0.013508 | 0.06456 | 0.017886 | 0.076896 | 0.015435 | 0.0013717 | -0.06987 | 0.012315 | 0.075486 | 0.061622 | 0.010974 | -0.00865 | 64.8605 | -58.1635 | -0.009155 | -58.4244 | 64.8102 | -58.2504 | -58.2962 | -58.168 | 0.073242 | -58.4885 | 64.8514 | 64.7644 | -58.2458 | -58.3511 | -0.032043 | -0.07782 | 0.009156 | 0.054932 | -0.20599 | -0.12817 | 0.05951 | -0.027466 | -0.13275 | 0.050354 | 0.050354 | -0.27008 | -0.13733 | -0.036621 | 123.0286 | 123.0789 | 58.2092 | -123.0972 | 123.0698 | 122.9828 | 58.2916 | -123.1522
17.7031 | 123.3261 | -58.1772 | 64.7827 | 0.064555 | -0.029216 | 0.074173 | -0.0088172 | 0.079032 | -0.028357 | -0.0029003 | 0.11323 | -0.015456 | 0.053056 | 0.059485 | -0.0039789 | 0.011645 | 64.92 | -58.0353 | 0.068665 | -58.3649 | 64.7781 | -58.223 | -58.2413 | -58.0765 | 0.17853 | -58.3466 | 64.8148 | 64.7415 | -58.2092 | -58.3099 | -0.045776 | -0.064087 | -0.004578 | 0.14191 | -0.18768 | -0.1236 | 0.13733 | -0.032044 | -0.13275 | 0.032043 | 0.10071 | -0.16937 | -0.036621 | -0.041199 | 122.9553 | 123.0972 | 58.2459 | -123.024 | 122.9919 | 122.9187 | 58.3557 | -123.0927
18.6406 | 123.1384 | -58.2184 | 64.8056 | 0.20188 | 0.019917 | 0.075241 | -0.0024082 | 0.070487 | 0.017572 | 0.0056447 | 0.067459 | 0.0091106 | 0.072282 | 0.065894 | 0.0067021 | -0.006513 | 64.8331 | -58.2047 | -0.054932 | -58.4473 | 64.8102 | -58.2458 | -58.2962 | -58.1955 | -0.013733 | -58.5434 | 64.8743 | 64.7552 | -58.2733 | -58.374 | -0.027466 | -0.07782 | 0.004578 | 0.013733 | -0.22888 | -0.15106 | 0.027466 | -0.054931 | -0.15564 | 0.068665 | 0.022888 | -0.32501 | -0.16937 | -0.050354 | 123.0286 | 123.0515 | 58.1635 | -123.1018 | 123.0927 | 122.9736 | 58.2047 | -123.1796
19.7031 | 123.3078 | -58.1818 | 64.7873 | -0.22536 | -0.015331 | 0.075241 | -0.0098852 | 0.074759 | -0.020881 | -0.0050373 | 0.036941 | -0.0079794 | 0.059465 | 0.060554 | -0.0082519 | 0.00844 | 64.8972 | -58.0261 | 0.091553 | -58.3603 | 64.7507 | -58.2001 | -58.2367 | -58.1039 | 0.18768 | -58.3878 | 64.8102 | 64.7415 | -58.2367 | -58.3237 | -0.01831 | -0.054931 | -0.036621 | 0.15564 | -0.17853 | -0.1236 | 0.10986 | -0.054931 | -0.14191 | 0.022889 | 0.07782 | -0.20599 | -0.064087 | -0.045776 | 122.9324 | 123.0789 | 58.2733 | -123.024 | 122.9919 | 122.9233 | 58.3694 | -123.111
20.6406 | 123.2117 | -58.2138 | 64.7827 | 0.12559 | 0.022053 | 0.063492 | -0.014158 | 0.060874 | 0.022912 | 0.0056447 | 0.036941 | -0.0026384 | 0.077623 | 0.057349 | 0.0024291 | -0.009718 | 64.8468 | -58.1863 | -0.036621 | -58.4381 | 64.7781 | -58.2184 | -58.2825 | -58.1955 | -0.004578 | -58.548 | 64.8468 | 64.769 | -58.2687 | -58.342 | -0.004578 | -0.068665 | -0.004578 | 0.027466 | -0.2243 | -0.15564 | 0.064087 | -0.054932 | -0.12817 | 0.064087 | 0.01831 | -0.33417 | -0.20599 | -0.013733 | 122.9919 | 123.0606 | 58.1772 | -123.0652 | 123.0606 | 122.9828 | 58.2092 | -123.1247
21.7031 | 123.2895 | -58.1589 | 64.7873 | -0.37795 | -0.034557 | 0.070968 | -0.022702 | 0.066214 | -0.016608 | 0.0013717 | -0.085129 | -0.0015704 | 0.061601 | 0.057349 | -0.013592 | -0.001173 | 64.9109 | -58.017 | 0.10986 | -58.3511 | 64.7644 | -58.223 | -58.2458 | -58.0856 | 0.17853 | -58.3832 | 64.8056 | 64.7186 | -58.2275 | -58.2962 | -0.064086 | -0.086975 | -0.022888 | 0.14191 | -0.19226 | -0.10529 | 0.1236 | -0.068664 | -0.13733 | 0.018311 | 0.073243 | -0.2243 | -0.086975 | -0.068664 | 122.9233 | 123.0698 | 58.2687 | -123.0331 | 122.9645 | 122.8775 | 58.3374 | -123.0835
22.6406 | 123.1888 | -58.2367 | 64.7964 | 0.20188 | 0.0060322 | 0.061355 | 0.0072048 | 0.065146 | 0.014367 | -0.0018323 | -0.024094 | 0.00056556 | 0.071214 | 0.060554 | 0.00029315 | 0.0031 | 64.8834 | -58.1772 | -0.027466 | -58.4198 | 64.801 | -58.2413 | -58.2779 | -58.1772 | 0.018311 | -58.5114 | 64.8468 | 64.7278 | -58.2687 | -58.3786 | -0.004578 | -0.041199 | 0.004577 | 0.059509 | -0.18311 | -0.14191 | 0.086975 | -0.032044 | -0.14191 | 0.050354 | 0.059509 | -0.27466 | -0.13275 | -0.068665 | 123.0377 | 123.1201 | 58.2092 | -123.0743 | 123.0835 | 122.9645 | 58.255 | -123.175
23.7031 | 123.262 | -58.1726 | 64.7964 | -0.16433 | -0.019603 | 0.085922 | -0.0077492 | 0.067282 | -0.01554 | 0.00030367 | 0.021682 | -0.016524 | 0.060533 | 0.058417 | -0.0029109 | 0.005236 | 64.9063 | -58.0673 | 0.09613 | -58.3603 | 64.7736 | -58.1955 | -58.2504 | -58.1039 | 0.18768 | -58.3969 | 64.8239 | 64.7552 | -58.2184 | -58.3282 | -0.022889 | -0.07782 | -0.022888 | 0.10529 | -0.18768 | -0.10986 | 0.10986 | -0.045777 | -0.15564 | 0.027466 | 0.068664 | -0.22431 | -0.068665 | -0.041199 | 122.9462 | 123.0789 | 58.2687 | -123.0469 | 122.9965 | 122.9279 | 58.3603 | -123.1247
24.6406 | 123.2117 | -58.223 | 64.7873 | 0.15611 | 0.014576 | 0.06456 | -0.0045452 | 0.071555 | 0.029321 | 0.0056447 | 0.11323 | 0.0048376 | 0.05626 | 0.055213 | 0.0024291 | -0.006513 | 64.8743 | -58.1497 | -0.004578 | -58.4244 | 64.801 | -58.2367 | -58.2779 | -58.168 | 0.036621 | -58.5114 | 64.856 | 64.7415 | -58.2779 | -58.3878 | -0.013733 | -0.054932 | 0.013733 | 0.073242 | -0.20142 | -0.14648 | 0.086976 | -0.054932 | -0.1648 | 0.068665 | 0.054931 | -0.28839 | -0.1236 | -0.045776 | 123.024 | 123.0972 | 58.2184 | -123.0652 | 123.0789 | 122.9645 | 58.2596 | -123.175
25.7031 | 123.2758 | -58.2047 | 64.8102 | -0.17959 | -0.0099898 | 0.082718 | -0.021634 | 0.072623 | -0.010199 | -0.0061053 | -0.10039 | -0.0090474 | 0.062669 | 0.066962 | 0.0034971 | 0.00096301 | 64.8834 | -58.0811 | 0.07782 | -58.374 | 64.7827 | -58.2184 | -58.2458 | -58.1314 | 0.15564 | -58.4518 | 64.8331 | 64.7781 | -58.2367 | -58.3328 | -0.013733 | -0.041199 | -0.027466 | 0.1236 | -0.16937 | -0.12817 | 0.073242 | -0.032043 | -0.12817 | 0.022888 | 0.073242 | -0.24719 | -0.11902 | -0.032044 | 122.9874 | 123.0881 | 58.2825 | -123.056 | 123.0377 | 122.9828 | 58.3603 | -123.143
26.6406 | 123.2025 | -58.2596 | 64.7644 | 0.50706 | 0.023121 | 0.063492 | -0.0013402 | 0.071555 | 0.011163 | -0.00076433 | 0.32686 | 0.0037696 | 0.084031 | 0.060554 | 0.012042 | 0.00844 | 64.7827 | -58.2504 | -0.14191 | -58.461 | 64.8148 | -58.2642 | -58.3054 | -58.223 | -0.10071 | -58.5526 | 64.8285 | 64.7644 | -58.2733 | -58.3786 | -0.004577 | -0.045776 | 0.050354 | 0.009156 | -0.20142 | -0.15564 | 0.018311 | -0.013732 | -0.11902 | 0.064087 | 0.036622 | -0.29297 | -0.17395 | 0 | 123.0743 | 123.0423 | 58.1177 | -123.0698 | 123.0881 | 123.024 | 58.1589 | -123.143
27.7031 | 123.3124 | -58.2092 | 64.7873 | 0.20188 | 0.0017592 | 0.068832 | -0.014158 | 0.071555 | -0.03263 | -0.00076433 | 0.25056 | 0.0037696 | 0.044511 | 0.049872 | -0.010388 | 0.0031 | 64.8972 | -58.0856 | 0.045776 | -58.4015 | 64.7919 | -58.2458 | -58.2596 | -58.0994 | 0.13733 | -58.3832 | 64.7919 | 64.7415 | -58.2001 | -58.3511 | -0.036621 | -0.050354 | 0.004578 | 0.1236 | -0.19226 | -0.14191 | 0.10986 | 0.009156 | -0.14191 | 0.004578 | 0.10986 | -0.17395 | -0.032044 | -0.045776 | 123.0011 | 123.1064 | 58.255 | -123.0469 | 123.0011 | 122.9507 | 58.3466 | -123.1384
28.6406 | 123.1888 | -58.223 | 64.7736 | 0.15611 | 0.015645 | 0.065628 | 0.011477 | 0.069419 | 0.021844 | -0.0018323 | -0.0088351 | -0.0015704 | 0.071214 | 0.050941 | -0.0018429 | -0.004377 | 64.856 | -58.168 | -0.032043 | -58.4335 | 64.8056 | -58.2779 | -58.2733 | -58.1955 | 0 | -58.548 | 64.8285 | 64.7324 | -58.2687 | -58.3649 | -0.054932 | -0.050354 | 0.032043 | 0.054931 | -0.21057 | -0.16022 | 0.082397 | -0.045777 | -0.14191 | 0.054931 | 0.027465 | -0.32501 | -0.18311 | -0.041199 | 123.0286 | 123.0789 | 58.1909 | -123.0469 | 123.0515 | 122.9553 | 58.223 | -123.1384
29.7031 | 123.3032 | -58.2001 | 64.7827 | 0.095073 | -0.018535 | 0.0699 | -0.0056132 | 0.073691 | -0.024085 | -0.0071733 | -0.0088351 | -0.0058434 | 0.054124 | 0.071235 | -0.00077485 | 0.00844 | 64.9429 | -58.0353 | 0.10529 | -58.3374 | 64.769 | -58.2184 | -58.2367 | -58.0856 | 0.17853 | -58.374 | 64.7873 | 64.7415 | -58.2184 | -58.3054 | -0.018311 | -0.036621 | -0.013733 | 0.1648 | -0.13733 | -0.10071 | 0.16022 | -0.018311 | -0.10529 | 0.004577 | 0.11444 | -0.17395 | -0.068664 | -0.041199 | 122.9691 | 123.143 | 58.3054 | -123.0194 | 122.9874 | 122.9416 | 58.3786 | -123.0881
30.6406 | 123.1934 | -58.2413 | 64.7873 | 0.095073 | 0.0060322 | 0.074173 | 0.0039998 | 0.06301 | 0.025048 | 0.0077807 | 0.021682 | 0.0016336 | 0.051988 | 0.054145 | 0.0034971 | -0.006513 | 64.8697 | -58.1726 | -0.032043 | -58.429 | 64.7964 | -58.2321 | -58.287 | -58.1772 | 0.027466 | -58.5205 | 64.8468 | 64.7461 | -58.2642 | -58.3282 | 0.009155 | -0.045776 | 0.009156 | 0.068665 | -0.18768 | -0.14191 | 0.082398 | -0.022888 | -0.086975 | 0.05951 | 0.064087 | -0.27924 | -0.19226 | -0.041198 | 123.0377 | 123.111 | 58.2092 | -123.0743 | 123.0881 | 122.9874 | 58.2687 | -123.1155
31.7031 | 123.2208 | -58.2047 | 64.8285 | -0.2101 | -0.019603 | 0.077377 | -0.0013402 | 0.065146 | -0.021949 | 0.00030367 | 1.8833 | -0.0037074 | 0.040239 | 0.076575 | -0.0082519 | -0.00865 | 64.8788 | -58.1131 | 0.064087 | -58.3878 | 64.7964 | -58.2047 | -58.2596 | -58.1589 | 0.19684 | -58.4885 | 64.8422 | 64.7873 | -58.2596 | -58.3054 | 0 | -0.054932 | -0.032043 | 0.091553 | -0.18311 | -0.12817 | 0.050354 | -0.054932 | -0.10071 | 0.013733 | 0.045776 | -0.28381 | -0.1831 | -0.041199 | 123.0011 | 123.0835 | 58.2687 | -123.0881 | 123.0469 | 122.9919 | 58.4015 | -123.1338
32.6406 | 123.1888 | -58.2184 | 64.7964 | 0.079814 | 0.015645 | 0.0699 | 0.012545 | 0.064078 | 0.029321 | -0.0071733 | 0.0064239 | 0.011247 | 0.059465 | 0.053077 | 0.0056341 | -0.009718 | 64.856 | -58.1497 | -0.004578 | -58.4335 | 64.8239 | -58.2642 | -58.2916 | -58.1589 | 0.045776 | -58.4976 | 64.8468 | 64.7461 | -58.2504 | -58.3603 | -0.045776 | -0.073242 | 0.027466 | 0.068665 | -0.21515 | -0.14191 | 0.059509 | -0.032043 | -0.14191 | 0.050354 | 0.059509 | -0.27924 | -0.13733 | -0.050354 | 123.0423 | 123.0743 | 58.2138 | -123.0881 | 123.0652 | 122.9645 | 58.2642 | -123.1567
33.7031 | 123.1705 | -58.2367 | 64.8239 | -0.30166 | -0.0035808 | 0.067764 | 0.011477 | 0.068351 | -0.0091309 | 0.0024397 | -0.2072 | -0.010115 | 0.085099 | 0.048804 | -0.011456 | -0.00010499 | 64.7964 | -58.0994 | 0.045776 | -58.4335 | 64.8193 | -58.2596 | -58.2916 | -58.1863 | 0.073242 | -58.5114 | 64.8697 | 64.7873 | -58.2687 | -58.3466 | -0.022889 | -0.054932 | -0.004578 | 0.13733 | -0.19684 | -0.14191 | -0.027466 | -0.032044 | -0.10986 | 0.045776 | 0.050354 | -0.27466 | -0.16479 | -0.036622 | 123.056 | 123.0331 | 58.2825 | -123.1155 | 123.1064 | 123.024 | 58.3099 | -123.1705
34.6406 | 123.1796 | -58.2413 | 64.7827 | 0.21714 | 0.0060322 | 0.063492 | 0.0050688 | 0.068351 | 0.020776 | -0.0029003 | -0.0088351 | -0.0058434 | 0.062669 | 0.060554 | 0.0077701 | -0.001173 | 64.8239 | -58.1909 | -0.050354 | -58.4518 | 64.8239 | -58.255 | -58.2916 | -58.2001 | 0.036621 | -58.5617 | 64.8697 | 64.7552 | -58.2687 | -58.3832 | -0.013733 | -0.050354 | 0.041199 | 0.050354 | -0.21057 | -0.16022 | 0.041199 | -0.027466 | -0.14191 | 0.086975 | 0.041199 | -0.32043 | -0.17853 | -0.027466 | 123.0652 | 123.0652 | 58.1909 | -123.0743 | 123.111 | 122.9965 | 58.2779 | -123.1659
35.7031 | 123.2849 | -58.1863 | 64.7873 | -0.088033 | -0.024944 | 0.073105 | -0.019498 | 0.068351 | -0.029426 | 0.0056447 | 0.0522 | 0.0059056 | 0.058397 | 0.057349 | -0.00077485 | 0.0031 | 64.8972 | -58.0536 | 0.10986 | -58.3511 | 64.7919 | -58.2413 | -58.2321 | -58.0902 | 0.17853 | -58.3694 | 64.8239 | 64.7507 | -58.2184 | -58.3054 | -0.054932 | -0.045777 | 0.004578 | 0.13275 | -0.16479 | -0.11902 | 0.10986 | -0.032044 | -0.11902 | 0.036622 | 0.09613 | -0.18311 | -0.064087 | -0.036621 | 122.9782 | 123.0835 | 58.2962 | -123.0194 | 123.0103 | 122.937 | 58.3649 | -123.0927
36.6406 | 123.2025 | -58.2275 | 64.8056 | 0.018779 | 0.011372 | 0.074173 | 0.014682 | 0.066214 | 0.020776 | 0.0067127 | 0.0064239 | 0.00056556 | 0.065873 | 0.058417 | 0.00029315 | -0.011854 | 64.8788 | -58.1451 | 0 | -58.4015 | 64.801 | -58.2413 | -58.287 | -58.1635 | 0.059509 | -58.4885 | 64.8468 | 64.769 | -58.2596 | -58.3649 | -0.013733 | -0.059509 | -0.004578 | 0.082397 | -0.17395 | -0.11444 | 0.073242 | -0.032044 | -0.13733 | 0.041199 | 0.064087 | -0.26093 | -0.1236 | -0.036621 | 123.0286 | 123.1064 | 58.2275 | -123.0927 | 123.0743 | 122.9965 | 58.287 | -123.1705
37.7031 | 123.2529 | -58.1818 | 64.7827 | -0.14907 | -0.0089218 | 0.077377 | -0.0013402 | 0.067282 | -0.021949 | -0.0050373 | -0.10039 | -0.0090474 | 0.048783 | 0.056281 | 0.0024291 | 0.00844 | 64.8834 | -58.0582 | 0.091553 | -58.374 | 64.7873 | -58.2367 | -58.2596 | -58.1039 | 0.16479 | -58.4061 | 64.8148 | 64.7324 | -58.2367 | -58.3374 | -0.054931 | -0.07782 | 0.004577 | 0.1236 | -0.19226 | -0.11444 | 0.10071 | -0.054931 | -0.15564 | 0.032043 | 0.07782 | -0.2243 | -0.068665 | -0.050354 | 122.9691 | 123.0652 | 58.2733 | -123.0423 | 122.9965 | 122.9141 | 58.3466 | -123.1201
38.6406 | 123.2666 | -58.223 | 64.7461 | 0.46128 | -0.0046498 | 0.076309 | -0.0013402 | 0.064078 | -0.012336 | -0.0018323 | 0.571 | -0.0058434 | 0.051988 | 0.048804 | -0.0093199 | 0.00844 | 64.8422 | -58.1177 | -0.004578 | -58.4106 | 64.7461 | -58.2504 | -58.2733 | -58.1497 | -0.059509 | -58.4518 | 64.7919 | 64.7049 | -58.2458 | -58.3557 | -0.027466 | -0.050354 | 0 | 0.10528 | -0.18768 | -0.13733 | 0.09613 | -0.022889 | -0.13275 | 0.045776 | 0.073242 | -0.22888 | -0.09613 | -0.041199 | 122.9691 | 123.0652 | 58.2184 | -123.0194 | 123.0148 | 122.9279 | 58.1635 | -123.1018
39.7031 | 123.1842 | -58.2275 | 64.8239 | -0.27114 | -0.011058 | 0.078445 | 0.010409 | 0.070487 | 0.0026181 | -0.00076433 | -0.23772 | 0.010179 | 0.058397 | 0.053077 | -0.00077485 | -0.019331 | 64.8239 | -58.1909 | -0.013733 | -58.4381 | 64.8422 | -58.2367 | -58.2779 | -58.1818 | 0.050354 | -58.5022 | 64.9017 | 64.8239 | -58.2458 | -58.3282 | -0.009155 | -0.050354 | 0.01831 | 0.036621 | -0.21057 | -0.16022 | 0 | -0.018311 | -0.10071 | 0.077819 | 0.045776 | -0.27466 | -0.17395 | 0 | 123.0698 | 123.0515 | 58.2138 | -123.1018 | 123.1293 | 123.0515 | 58.2779 | -123.1522
40.6406 | 123.1201 | -58.2596 | 64.8148 | 0.15611 | 0.016713 | 0.049606 | 0.014682 | 0.067282 | 0.013299 | 0.0024397 | 0.18953 | -0.00050244 | 0.078691 | 0.064826 | 0.0045661 | -0.001173 | 64.8422 | -58.2275 | -0.09613 | -58.4656 | 64.8285 | -58.2504 | -58.2916 | -58.2184 | -0.068665 | -58.5709 | 64.8788 | 64.7552 | -58.2825 | -58.3786 | 0.009156 | -0.032043 | 0.013733 | 0.032044 | -0.20599 | -0.17395 | 0.027466 | -0.022888 | -0.11902 | 0.064087 | 0.041199 | -0.31128 | -0.19226 | -0.059509 | 123.0881 | 123.1018 | 58.1635 | -123.1064 | 123.1384 | 123.0148 | 58.1909 | -123.1934
41.7031 | 123.3307 | -58.1909 | 64.7781 | 0.11033 | -0.016399 | 0.073105 | -0.00027224 | 0.051261 | -0.024085 | 0.00030367 | 0.021682 | 0.0037696 | 0.046647 | 0.056281 | -0.0071839 | 0.005236 | 64.9063 | -58.0307 | 0.09613 | -58.3511 | 64.7919 | -58.1818 | -58.2413 | -58.0948 | 0.19684 | -58.3832 | 64.8239 | 64.7186 | -58.2138 | -58.3145 | 0.009155 | -0.050354 | 0.013733 | 0.16022 | -0.16022 | -0.10986 | 0.12817 | -0.022888 | -0.1236 | 0.045777 | 0.09613 | -0.19226 | -0.068665 | -0.059509 | 122.9828 | 123.0972 | 58.287 | -123.0194 | 123.0148 | 122.9095 | 58.3878 | -123.0927
42.6406 | 123.1613 | -58.2642 | 64.7644 | 0.33921 | 0.020985 | 0.053879 | 0.0050688 | 0.068351 | 0.0079581 | 0.0067127 | 0.2353 | 0.0091106 | 0.070146 | 0.052009 | 0.0088381 | -0.002241 | 64.8148 | -58.2275 | -0.054932 | -58.4381 | 64.8102 | -58.2504 | -58.2962 | -58.2321 | -0.009155 | -58.5709 | 64.8468 | 64.7415 | -58.2733 | -58.374 | 0.013733 | -0.032044 | 0.045777 | 0.036621 | -0.17395 | -0.14191 | 0.050354 | -0.009155 | -0.10986 | 0.082398 | 0.032043 | -0.3067 | -0.19684 | -0.022888 | 123.0743 | 123.0789 | 58.2092 | -123.0606 | 123.111 | 123.0057 | 58.255 | -123.1384
43.7031 | 123.1934 | -58.2321 | 64.7919 | -0.11855 | 0.00069119 | 0.060287 | -0.012021 | 0.067282 | -0.0016549 | -0.00076433 | -0.23772 | -0.00050244 | 0.060533 | 0.073371 | 0.0045661 | -0.004377 | 64.856 | -58.1451 | 0.013733 | -58.3923 | 64.8331 | -58.2367 | -58.2733 | -58.1497 | 0.09613 | -58.4747 | 64.8468 | 64.7827 | -58.2596 | -58.3466 | -0.004577 | -0.041198 | 0.041199 | 0.086975 | -0.16022 | -0.11902 | 0.064087 | -0.027466 | -0.11444 | 0.054932 | 0.082398 | -0.24261 | -0.12817 | -0.009155 | 123.0652 | 123.0881 | 58.2459 | -123.0652 | 123.0789 | 123.0148 | 58.3282 | -123.1384
44.6406 | 123.175 | -58.2458 | 64.801 | 0.17137 | 0.025258 | 0.0699 | 0.0039998 | 0.06301 | 0.019708 | 0.012053 | -0.0088351 | -0.0047754 | 0.066941 | 0.064826 | 0.0034971 | -0.004377 | 64.856 | -58.1543 | -0.018311 | -58.4244 | 64.8148 | -58.2413 | -58.2916 | -58.168 | 0.004578 | -58.5114 | 64.8285 | 64.7644 | -58.2733 | -58.3694 | 0.004578 | -0.045776 | 0.013733 | 0.091553 | -0.17853 | -0.13275 | 0.054932 | -0.027465 | -0.1236 | 0.027466 | 0.07782 | -0.2655 | -0.14191 | -0.036621 | 123.0606 | 123.1018 | 58.2275 | -123.0927 | 123.0743 | 123.0103 | 58.2504 | -123.1705
45.7031 | 123.1476 | -58.1909 | 64.8468 | -0.83571 | -0.0057178 | 0.0699 | 0.0082728 | 0.073691 | -0.0059269 | -0.0029003 | -0.14616 | -0.0069114 | 0.055192 | 0.065894 | -0.0082519 | -0.00010499 | 64.8056 | -58.1726 | -0.013733 | -58.4518 | 64.8514 | -58.2458 | -58.3008 | -58.2001 | 0.068665 | -58.5068 | 64.8743 | 64.7827 | -58.2596 | -58.3237 | -0.054932 | -0.10986 | 0.004577 | 0.018311 | -0.26092 | -0.15106 | -0.041199 | -0.068665 | -0.13275 | 0.027466 | -0.009155 | -0.31586 | -0.18311 | -0.064087 | 123.0423 | 122.9965 | 58.1772 | -123.1476 | 123.0652 | 122.9736 | 58.2596 | -123.1705
46.6406 | 123.1613 | -58.2458 | 64.7873 | 0.47654 | -0.00037681 | 0.073105 | -0.0098852 | 0.058738 | 0.0079581 | 0.0056447 | 0.43367 | 0.010179 | 0.071214 | 0.06803 | -0.010388 | -0.00010499 | 64.7507 | -58.2779 | -0.15106 | -58.4747 | 64.7964 | -58.2962 | -58.3008 | -58.2321 | -0.068665 | -58.5526 | 64.8514 | 64.7369 | -58.2825 | -58.3923 | -0.050354 | -0.054931 | 0.009156 | -0.032043 | -0.22888 | -0.17395 | -0.036621 | -0.036621 | -0.14648 | 0.064087 | 0.013733 | -0.3067 | -0.16022 | -0.050354 | 123.0423 | 122.9965 | 58.0948 | -123.0881 | 123.0972 | 122.9828 | 58.1772 | -123.1796
47.7031 | 123.1842 | -58.2275 | 64.8285 | -0.24062 | -0.0014448 | 0.083786 | 0.011477 | 0.059806 | -0.0059269 | -0.0039683 | -0.29875 | -0.0037074 | 0.060533 | 0.071235 | -0.0082519 | 0.002032 | 64.8056 | -58.1863 | -0.027466 | -58.4381 | 64.8193 | -58.2458 | -58.2825 | -58.2047 | 0.073242 | -58.5068 | 64.8651 | 64.7919 | -58.2596 | -58.3511 | -0.018311 | -0.054932 | -0.009155 | 0.041199 | -0.21057 | -0.15564 | -0.022888 | -0.032044 | -0.1236 | 0.036621 | 0.022888 | -0.27924 | -0.15564 | -0.036621 | 123.0469 | 123.0331 | 58.2001 | -123.111 | 123.0927 | 123.0194 | 58.3008 | -123.1796
48.6406 | 123.317 | -58.2001 | 64.769 | 0.12559 | -0.023876 | -0.22597 | -0.010953 | 0.074759 | -0.036902 | -0.0018323 | 0.20479 | -0.00050244 | 0.054124 | 0.074439 | -0.015729 | 0.012713 | 64.8239 | -58.1039 | 0.013733 | -58.4061 | 64.7827 | -58.2367 | -58.2596 | -58.1131 | 0.09613 | -58.3969 | 64.8102 | 64.7095 | -58.2458 | -58.3328 | -0.036621 | -0.05951 | 0.013733 | 0.09613 | -0.20599 | -0.14648 | 0.054932 | -0.045777 | -0.13275 | 0.041199 | 0.086975 | -0.19684 | -0.064087 | -0.059509 | 122.9828 | 123.024 | 58.2138 | -123.0286 | 123.0103 | 122.9095 | 58.2962 | -123.1018
49.7031 | 123.1659 | -58.2138 | 64.8239 | 0.064555 | -0.017467 | 0.065628 | -0.0013402 | 0.059806 | -0.011268 | -0.012513 | -0.23772 | 0.00056556 | 0.069078 | 0.059485 | 0.0034971 | -0.003309 | 64.8743 | -58.1635 | -0.009155 | -58.4244 | 64.8376 | -58.2367 | -58.2687 | -58.2047 | 0.059509 | -58.4976 | 64.9017 | 64.7736 | -58.2642 | -58.3328 | -0.022888 | -0.054932 | 0.013732 | 0.050354 | -0.21057 | -0.15564 | 0.050354 | -0.050354 | -0.11902 | 0.077819 | 0.009155 | -0.28381 | -0.16479 | -0.050354 | 123.0515 | 123.0881 | 58.2047 | -123.0927 | 123.1155 | 122.9874 | 58.2733 | -123.1567
50.6406 | 123.1796 | -58.2596 | 64.7781 | 0.27818 | 0.013508 | 0.059219 | 0.014682 | 0.066214 | 0.019708 | -0.0029003 | 0.35738 | 0.0037696 | 0.053056 | 0.073371 | 0.014179 | -0.004377 | 64.7644 | -58.2642 | -0.11902 | -58.4839 | 64.8148 | -58.2642 | -58.2825 | -58.2321 | -0.07782 | -58.5526 | 64.8331 | 64.7141 | -58.2916 | -58.4198 | -0.004577 | -0.022888 | 0.036621 | -0.004577 | -0.2243 | -0.20142 | -0.013733 | -0.032043 | -0.16022 | 0.054932 | 0.027466 | -0.29297 | -0.13275 | -0.064087 | 123.0743 | 123.024 | 58.1406 | -123.0606 | 123.0927 | 122.9736 | 58.1818 | -123.1979
51.7031 | 123.2162 | -58.1955 | 64.8148 | -0.14907 | -0.016399 | 0.076309 | 0.00079576 | 0.061942 | -0.023017 | -0.0050373 | -0.11565 | -0.0090474 | 0.054124 | 0.063758 | 0.0013611 | 0.0031 | 64.8834 | -58.0902 | 0.091553 | -58.3786 | 64.7919 | -58.1955 | -58.2504 | -58.1406 | 0.16022 | -58.4152 | 64.8285 | 64.7461 | -58.2184 | -58.3374 | 0 | -0.054931 | -0.022888 | 0.10529 | -0.18311 | -0.12817 | 0.068665 | -0.022888 | -0.14191 | 0.013733 | 0.054932 | -0.21973 | -0.07782 | -0.068664 | 122.9874 | 123.0789 | 58.287 | -123.0652 | 123.024 | 122.9416 | 58.3557 | -123.1522
52.6406 | 123.1934 | -58.2642 | 64.7873 | 0.53758 | 0.023121 | 0.068832 | 0.0061368 | 0.074759 | 0.017572 | 0.0056447 | 0.41841 | 0.0091106 | 0.069078 | 0.055213 | 0.0034971 | -0.005445 | 64.7736 | -58.2504 | -0.14648 | -58.4656 | 64.7919 | -58.2642 | -58.3099 | -58.223 | -0.09613 | -58.548 | 64.8285 | 64.7324 | -58.2916 | -58.3694 | 0 | -0.045777 | 0.004578 | 0.013733 | -0.20142 | -0.15564 | -0.013732 | -0.027466 | -0.10529 | 0.041199 | 0.041199 | -0.28381 | -0.17853 | -0.054931 | 123.056 | 123.0377 | 58.1177 | -123.0972 | 123.0927 | 122.9965 | 58.168 | -123.1567
53.7031 | 123.2941 | -58.2275 | 64.7415 | 0.46128 | -0.0078538 | 0.076309 | -0.0013402 | 0.066214 | -0.0059269 | -0.0029003 | 0.66255 | -0.0090474 | 0.075486 | 0.066962 | 0.0013611 | 0.013781 | 64.8605 | -58.1223 | -0.004578 | -58.4244 | 64.7369 | -58.2458 | -58.2687 | -58.1177 | 0.041199 | -58.4381 | 64.7736 | 64.7095 | -58.2642 | -58.342 | -0.018311 | -0.041199 | -0.004578 | 0.10529 | -0.19684 | -0.15564 | 0.11902 | -0.036621 | -0.11444 | 0.032044 | 0.10986 | -0.21057 | -0.09613 | -0.032043 | 122.9645 | 123.0881 | 58.223 | -123.0103 | 123.0011 | 122.937 | 58.2687 | -123.0835
54.6406 | 123.1293 | -58.2458 | 64.8056 | 0.47654 | 0.014576 | 0.067764 | 0.012545 | 0.06301 | 0.019708 | 0.0088487 | 0.44893 | -0.0047754 | 0.069078 | 0.074439 | -0.0050469 | -0.001173 | 64.8056 | -58.2779 | -0.12817 | -58.4702 | 64.8148 | -58.2779 | -58.3054 | -58.2413 | -0.09613 | -58.5663 | 64.8193 | 64.7736 | -58.2596 | -58.374 | -0.032043 | -0.059509 | 0.009155 | -0.032043 | -0.2243 | -0.16479 | 0 | -0.013733 | -0.12817 | 0.013733 | 0.004578 | -0.32043 | -0.19226 | -0.032043 | 123.0606 | 123.0515 | 58.1177 | -123.111 | 123.0652 | 123.0194 | 58.1497 | -123.1796
55.7031 | 123.2666 | -58.1863 | 64.7827 | -0.14907 | -0.037761 | 0.070968 | -0.0024082 | 0.073691 | -0.014472 | -0.00076433 | -0.14616 | 0.0016336 | 0.053056 | 0.066962 | -0.0039789 | 0.00096301 | 64.8972 | -58.0444 | 0.091553 | -58.3603 | 64.801 | -58.2138 | -58.2642 | -58.1131 | 0.16937 | -58.3878 | 64.8148 | 64.7644 | -58.223 | -58.3145 | -0.027466 | -0.07782 | 0.01831 | 0.14191 | -0.17395 | -0.096131 | 0.11444 | -0.036621 | -0.12817 | 0.032043 | 0.073242 | -0.20142 | -0.073242 | -0.018311 | 122.9874 | 123.0835 | 58.2779 | -123.0469 | 123.0011 | 122.9507 | 58.3557 | -123.0972
56.6406 | 123.1613 | -58.2504 | 64.7781 | 0.41551 | 0.02419 | 0.078445 | 0.0082728 | 0.064078 | 0.019708 | 0.00030367 | 0.38789 | 0.0059056 | 0.065873 | 0.077643 | 0.0056341 | -0.00865 | 64.7644 | -58.287 | -0.12817 | -58.493 | 64.7873 | -58.255 | -58.3191 | -58.223 | -0.073242 | -58.5709 | 64.856 | 64.7598 | -58.3054 | -58.374 | -0.004578 | -0.068665 | 0.009155 | -0.036621 | -0.24262 | -0.17395 | -0.013733 | -0.054932 | -0.1236 | 0.07782 | 0.027466 | -0.32043 | -0.19684 | -0.01831 | 123.0377 | 123.0148 | 58.1223 | -123.0972 | 123.1064 | 123.0103 | 58.1772 | -123.1522
57.7031 | 123.3032 | -58.1955 | 64.7781 | -0.14907 | -0.017467 | 0.075241 | -0.0045452 | 0.069419 | -0.023017 | -0.0029003 | -0.054612 | -0.0079794 | 0.047715 | 0.069098 | -0.010388 | 0.002032 | 64.8972 | -58.0536 | 0.10529 | -58.3511 | 64.7873 | -58.223 | -58.2458 | -58.1039 | 0.21515 | -58.3969 | 64.8239 | 64.7644 | -58.2321 | -58.3191 | -0.027465 | -0.050354 | 0.009155 | 0.14191 | -0.15564 | -0.10529 | 0.11902 | -0.036621 | -0.1236 | 0.045777 | 0.091553 | -0.20142 | -0.07782 | -0.013733 | 122.9828 | 123.0927 | 58.3008 | -123.024 | 123.0194 | 122.9599 | 58.4106 | -123.0972
58.6406 | 123.2117 | -58.2138 | 64.7964 | -0.22536 | -0.0067858 | 0.0699 | 0.0039998 | 0.075827 | -0.0059269 | -0.0061053 | -0.16142 | -0.012251 | 0.07335 | 0.065894 | 0.01311 | -0.002241 | 64.8834 | -58.0902 | 0.059509 | -58.3694 | 64.8102 | -58.223 | -58.255 | -58.0444 | 0.13275 | -58.4381 | 64.8193 | 64.7644 | -58.255 | -58.3145 | -0.009155 | -0.041199 | 0.013733 | 0.1236 | -0.15564 | -0.11444 | 0.086975 | -0.041199 | -0.10071 | 0.022888 | 0.16937 | -0.2243 | -0.1236 | -0.032044 | 123.024 | 123.0972 | 58.2733 | -123.0515 | 123.0331 | 122.9782 | 58.3466 | -123.111
59.7031 | 123.23 | -58.1818 | 64.8102 | -0.25588 | -0.031352 | 0.08165 | -0.0088172 | 0.056601 | -0.0091309 | 0.0035077 | -0.17668 | -0.0015704 | 0.053056 | 0.047736 | 0.0088381 | -0.003309 | 64.8972 | -58.0719 | 0.07782 | -58.3786 | 64.801 | -58.2001 | -58.255 | -58.1223 | 0.13733 | -58.5068 | 64.8422 | 64.7232 | -58.2642 | -58.342 | -0.01831 | -0.073242 | -0.009156 | 0.10986 | -0.19684 | -0.1236 | 0.086975 | -0.082397 | -0.16022 | 0.032043 | 0.05951 | -0.32501 | -0.16479 | -0.086975 | 122.9828 | 123.0789 | 58.2596 | -123.0652 | 123.024 | 122.905 | 58.3191 | -123.1522
60.6406 | 123.2437 | -58.2092 | 64.7552 | 0.59861 | 0.017781 | 0.072037 | 0.012545 | 0.060874 | 0.021844 | 0.0045757 | 0.43367 | -0.012251 | 0.081895 | 0.059485 | 0.0013611 | -0.001173 | 64.8148 | -58.2184 | -0.10071 | -58.4518 | 64.8193 | -58.2596 | -58.2733 | -58.1131 | -0.11902 | -58.5022 | 64.7827 | 64.7324 | -58.2642 | -58.3878 | -0.050354 | -0.064086 | 0.064087 | -0.009155 | -0.24261 | -0.17853 | 0.059509 | -0.054931 | -0.17853 | 0.027466 | 0.096131 | -0.29297 | -0.11444 | -0.022888 | 123.0286 | 123.024 | 58.1085 | -123.0286 | 122.9919 | 122.9416 | 58.0902 | -123.143
61.7031 | 123.1522 | -58.2092 | 64.8376 | -0.22536 | 0.0049632 | 0.070968 | 0.010409 | 0.070487 | -0.00058594 | -0.013582 | -0.22246 | 0.0016336 | 0.07335 | 0.073371 | -0.0029109 | 0.00096301 | 64.8148 | -58.1909 | -0.009155 | -58.4335 | 64.8468 | -58.2367 | -58.255 | -58.1909 | 0.064087 | -58.5068 | 64.8697 | 64.769 | -58.2321 | -58.3511 | -0.027465 | -0.045776 | 0.009156 | 0.018311 | -0.2243 | -0.17853 | -0.022888 | -0.022888 | -0.14191 | 0.032044 | 0.018311 | -0.29755 | -0.15564 | -0.068664 | 123.056 | 123.024 | 58.2001 | -123.0927 | 123.0789 | 122.9782 | 58.2733 | -123.1888
62.6406 | 123.175 | -58.2275 | 64.7827 | 0.47654 | 0.01244 | 0.067764 | 0.0018638 | 0.075827 | 0.0079581 | 0.0013717 | 0.47945 | -0.00050244 | 0.064805 | 0.06269 | 0.010974 | 0.002032 | 64.7919 | -58.2413 | -0.13275 | -58.4656 | 64.7873 | -58.2642 | -58.3191 | -58.1589 | -0.054932 | -58.5205 | 64.8148 | 64.7278 | -58.287 | -58.3786 | -0.036621 | -0.091553 | 0.004577 | -0.013733 | -0.23804 | -0.14648 | 0.009155 | -0.059509 | -0.15106 | 0.032043 | 0.068664 | -0.29297 | -0.14191 | -0.054932 | 123.0148 | 123.0194 | 58.0948 | -123.1018 | 123.0423 | 122.9553 | 58.1726 | -123.1613
63.7031 | 123.2574 | -58.1726 | 64.7827 | -0.13381 | -0.035625 | 0.074173 | -0.010953 | 0.070487 | -0.023017 | 0.0013717 | 0.0064239 | -0.0090474 | 0.048783 | 0.061622 | 0.0013611 | 0.006304 | 64.8834 | -58.0536 | 0.091553 | -58.342 | 64.7873 | -58.1955 | -58.2413 | -58.1039 | 0.20142 | -58.3832 | 64.8468 | 64.7415 | -58.223 | -58.3099 | -0.022889 | -0.068665 | 0.004577 | 0.11902 | -0.16937 | -0.10071 | 0.10071 | -0.050354 | -0.13733 | 0.064087 | 0.068664 | -0.21057 | -0.073242 | -0.041199 | 122.9599 | 123.056 | 58.2642 | -123.024 | 123.0194 | 122.9141 | 58.374 | -123.0927
64.6406 | 123.1522 | -58.223 | 64.8193 | 0.26292 | 0.01244 | 0.067764 | -0.0013402 | 0.054465 | 0.01864 | 0.0067127 | 0.067459 | 0.0080426 | 0.070146 | 0.066962 | 0.0088381 | -0.003309 | 64.8331 | -58.1955 | -0.068665 | -58.4518 | 64.801 | -58.2367 | -58.3054 | -58.1909 | 0 | -58.5388 | 64.8605 | 64.7049 | -58.2687 | -58.3649 | -0.013733 | -0.082398 | -0.018311 | 0.027465 | -0.22888 | -0.14648 | 0.013733 | -0.045777 | -0.14191 | 0.041199 | 0.032043 | -0.31586 | -0.17395 | -0.11444 | 123.024 | 123.056 | 58.1543 | -123.1247 | 123.0835 | 122.9279 | 58.223 | -123.1842
65.7031 | 123.2162 | -58.1863 | 64.7781 | -0.24062 | -0.016399 | 0.08165 | -0.0056132 | 0.066214 | -0.021949 | -0.0018323 | -0.16142 | -0.0047754 | 0.043443 | 0.053077 | -0.0061159 | -0.001173 | 64.8788 | -58.0627 | 0.10071 | -58.3694 | 64.7919 | -58.2321 | -58.2321 | -58.1131 | 0.15564 | -58.4152 | 64.8148 | 64.7461 | -58.2413 | -58.3374 | -0.045777 | -0.045777 | 0.013733 | 0.1236 | -0.18311 | -0.13733 | 0.10071 | -0.054932 | -0.15106 | 0.036621 | 0.073242 | -0.22888 | -0.07782 | -0.032043 | 122.9782 | 123.0652 | 58.287 | -123.0103 | 123.0011 | 122.9324 | 58.342 | -123.1155
66.6406 | 123.1384 | -58.255 | 64.7781 | 0.87327 | 0.027394 | 0.072037 | 0.013613 | 0.058738 | 0.010095 | 0.0067127 | 0.12849 | 0.00056556 | 0.05626 | 0.056281 | 0.0067021 | -0.001173 | 64.8239 | -58.2321 | -0.10529 | -58.4427 | 64.8285 | -58.2504 | -58.2962 | -58.2184 | -0.045776 | -58.5617 | 64.8331 | 64.7507 | -58.2962 | -58.3694 | 0.004578 | -0.041199 | 0.050354 | 0.022888 | -0.18768 | -0.14648 | 0.045777 | -0.041199 | -0.11444 | 0.054932 | 0.036621 | -0.3067 | -0.19226 | -0.027466 | 123.0835 | 123.0789 | 58.1497 | -123.0743 | 123.0881 | 123.0057 | 58.2092 | -123.1476
67.7031 | 123.2025 | -58.2047 | 64.8193 | -0.27114 | -0.0035808 | 0.072037 | -0.0088172 | 0.073691 | -0.0048589 | 0.0024397 | -1.9009 | 0.010179 | 0.071214 | 0.063758 | -0.010388 | 0.007372 | 64.8697 | -58.1131 | 0.064087 | -58.3694 | 64.7873 | -58.2275 | -58.2687 | -58.1314 | 0.10529 | -58.4427 | 64.856 | 64.7644 | -58.2367 | -58.3282 | -0.022888 | -0.064087 | -0.032044 | 0.091553 | -0.1648 | -0.10071 | 0.050354 | -0.032043 | -0.1236 | 0.036621 | 0.073242 | -0.23804 | -0.11444 | -0.054932 | 122.9919 | 123.0743 | 58.2687 | -123.0881 | 123.0606 | 122.9691 | 58.3099 | -123.1476
68.6406 | 123.1476 | -58.2504 | 64.7827 | 0.26292 | 0.0071002 | 0.070968 | 0.0050688 | 0.06301 | 0.015435 | 0.0024397 | 0.29634 | 0.0059056 | 0.077623 | 0.064826 | -0.0039789 | 0.00096301 | 64.7827 | -58.2687 | -0.13733 | -58.4747 | 64.8193 | -58.2458 | -58.3054 | -58.2275 | -0.068665 | -58.5617 | 64.8422 | 64.7552 | -58.287 | -58.3694 | 0.004577 | -0.054932 | 0.036621 | -0.018311 | -0.2243 | -0.16937 | 0 | -0.036621 | -0.11902 | 0.059509 | 0.022888 | -0.31128 | -0.19226 | -0.027466 | 123.0698 | 123.0331 | 58.1131 | -123.0881 | 123.0927 | 123.0057 | 58.1818 | -123.1522
69.7031 | 123.1613 | -58.2138 | 64.8102 | -0.2864 | -0.0089218 | 0.065628 | -0.0098852 | 0.071555 | -0.0016549 | -0.0061053 | -0.2072 | -0.00050244 | 0.062669 | 0.061622 | -0.0082519 | -0.001173 | 64.7873 | -58.1772 | -0.027466 | -58.429 | 64.8514 | -58.2184 | -58.2916 | -58.1955 | 0.054932 | -58.4885 | 64.8834 | 64.7919 | -58.2687 | -58.342 | -0.004578 | -0.07782 | 0.041198 | 0.036621 | -0.21515 | -0.13733 | -0.022889 | -0.054932 | -0.12817 | 0.073242 | 0.01831 | -0.27466 | -0.14648 | -0.018311 | 123.0652 | 123.0011 | 58.1863 | -123.1018 | 123.0972 | 123.0057 | 58.2687 | -123.1522
70.6406 | 123.1384 | -58.2687 | 64.7781 | -1.2019 | 0.0060322 | 0.075241 | 0.0082728 | 0.064078 | 0.015435 | 0.0013717 | 0.12849 | -0.0058434 | 0.059465 | 0.066962 | -0.0029109 | -0.006513 | 64.7827 | -58.2001 | -0.07782 | -58.4427 | 64.8239 | -58.2687 | -58.3008 | -58.223 | -0.041199 | -58.5526 | 64.8285 | 64.7461 | -58.255 | -58.3603 | 0 | -0.032043 | 0.045777 | 0.068665 | -0.17395 | -0.14191 | 0.004578 | 0.013733 | -0.091553 | 0.050354 | 0.045777 | -0.28381 | -0.19226 | -0.032043 | 123.0927 | 123.0515 | 58.1909 | -123.0789 | 123.0972 | 123.0148 | 58.2275 | -123.1384
71.7031 | 123.2803 | -58.1635 | 64.7644 | -0.14907 | -0.026012 | 0.076309 | -0.016294 | 0.059806 | -0.029426 | -0.0029003 | 0.067459 | -0.012251 | 0.046647 | 0.0456 | 0.0024291 | 0.006304 | 64.8788 | -58.0582 | 0.082397 | -58.3603 | 64.7964 | -58.2184 | -58.2642 | -58.1085 | 0.20599 | -58.3923 | 64.8239 | 64.7232 | -58.223 | -58.3237 | -0.054932 | -0.10071 | 0.032044 | 0.10529 | -0.19684 | -0.096131 | 0.11444 | -0.059509 | -0.16022 | 0.05951 | 0.054931 | -0.22888 | -0.068665 | -0.041198 | 122.9599 | 123.0423 | 58.2458 | -123.0286 | 122.9874 | 122.8867 | 58.3694 | -123.0881
72.6406 | 123.1888 | -58.2367 | 64.801 | 0.26292 | 0.013508 | 0.072037 | 0.0029318 | 0.066214 | 0.030389 | 0.012053 | 0.14375 | -0.0047754 | 0.059465 | 0.10541 | 0.0056341 | -0.016126 | 64.8422 | -58.1955 | -0.064087 | -58.429 | 64.8148 | -58.2504 | -58.2962 | -58.0811 | 0.13733 | -58.5617 | 64.8468 | 64.7461 | -58.2458 | -58.374 | -0.013733 | -0.05951 | 0.013733 | 0.041198 | -0.19226 | -0.13275 | 0.041199 | -0.009156 | -0.13733 | 0.045777 | 0.15564 | -0.32501 | -0.18768 | -0.054931 | 123.0515 | 123.0789 | 58.1726 | -123.0972 | 123.0835 | 122.9828 | 58.374 | -123.175
73.7031 | 123.1842 | -58.1955 | 64.8376 | -0.40847 | -0.032421 | 0.076309 | -0.012021 | 0.069419 | -0.025153 | -0.0050373 | -0.11565 | 0.0069746 | 0.044511 | 0.057349 | -0.013592 | 0.002032 | 64.8102 | -58.1268 | 0.022888 | -58.3786 | 64.8239 | -58.2001 | -58.2825 | -58.1818 | 0.10529 | -58.4152 | 64.856 | 64.7873 | -58.2367 | -58.3145 | -0.004577 | -0.086975 | -0.013732 | 0.068665 | -0.18311 | -0.09613 | -0.027465 | -0.041198 | -0.11902 | 0.018311 | 0.013733 | -0.21973 | -0.10071 | -0.050354 | 123.0194 | 123.0057 | 58.2184 | -123.1201 | 123.0515 | 122.9828 | 58.3008 | -123.1522
74.6406 | 123.1338 | -58.255 | 64.7919 | 0.18663 | 0.057301 | 0.063492 | 0.033908 | 0.061942 | 0.01864 | -0.010377 | 0.20479 | 0.0091106 | 0.058397 | 0.066962 | -0.0050469 | -0.010786 | 64.7919 | -58.1955 | -0.064087 | -58.4473 | 64.8285 | -58.2733 | -58.287 | -58.2138 | -0.036621 | -58.5663 | 64.856 | 64.7461 | -58.2733 | -58.3878 | -0.01831 | -0.032043 | 0.036621 | 0.059509 | -0.19226 | -0.16022 | 0 | -0.01831 | -0.13275 | 0.064087 | 0.041199 | -0.31128 | -0.17853 | -0.045776 | 123.0835 | 123.0469 | 58.1909 | -123.0789 | 123.111 | 123.0011 | 58.2184 | -123.1796
75.7031 | 123.3261 | -58.1772 | 64.7644 | 0.20188 | -0.017467 | 0.078445 | -0.00027224 | 0.066214 | -0.024085 | -0.01999 | 0.15901 | -0.0090474 | 0.049852 | 0.044532 | -0.0093199 | -0.001173 | 64.8651 | -58.0536 | 0.059509 | -58.3649 | 64.7781 | -58.2184 | -58.2458 | -58.0627 | 0.16937 | -58.3466 | 64.8102 | 64.7461 | -58.1909 | -58.3282 | -0.041199 | -0.068665 | 0.013733 | 0.1236 | -0.18768 | -0.11902 | 0.10071 | -0.013733 | -0.15106 | 0.045777 | 0.11444 | -0.16937 | -0.018311 | -0.01831 | 122.9553 | 123.0423 | 58.2367 | -123.0103 | 122.9874 | 122.9233 | 58.3466 | -123.0927
76.6406 | 123.1201 | -58.2184 | 64.8102 | 0.12559 | 0.015645 | 0.072037 | 0.0061368 | 0.077964 | 0.022912 | 0.0045757 | 0.082718 | 0.01552 | 0.086168 | 0.065894 | -0.0018429 | 0.0031 | 64.856 | -58.1818 | -0.027466 | -58.4335 | 64.801 | -58.2504 | -58.287 | -58.2047 | -0.004578 | -58.7494 | 64.7781 | 64.6774 | -58.3008 | -58.3557 | -0.032043 | -0.068664 | -0.009156 | 0.036621 | -0.21515 | -0.14648 | 0.045776 | -0.082397 | -0.13733 | -0.032044 | 0.013733 | -0.53101 | -0.39368 | -0.13275 | 123.0194 | 123.0743 | 58.1909 | -123.0972 | 122.9965 | 122.8958 | 58.2138 | -123.1659
77.7031 | 123.2986 | -58.1818 | 64.7827 | 0.00352 | -0.019603 | 0.082718 | -0.0066812 | 0.06301 | -0.020881 | -0.0029003 | 0.036941 | 0.00056556 | 0.054124 | 0.066962 | 0.0024291 | 0.00096301 | 64.8972 | -58.0353 | 0.082397 | -58.3694 | 64.7736 | -58.2047 | -58.255 | -58.0811 | 0.18768 | -58.3649 | 64.7964 | 64.7552 | -58.2184 | -58.3054 | -0.022888 | -0.073242 | -0.009155 | 0.14648 | -0.18768 | -0.11444 | 0.11444 | -0.036621 | -0.1236 | 0.013733 | 0.10071 | -0.18311 | -0.059509 | -0.027466 | 122.9553 | 123.0789 | 58.2642 | -123.0377 | 122.9782 | 122.937 | 58.3694 | -123.0881
78.6406 | 123.2071 | -58.1818 | 64.8102 | -0.088033 | 0.023121 | 0.080581 | -0.013089 | 0.060874 | 0.025048 | -0.0018323 | -0.14616 | -0.00050244 | 0.074418 | 0.055213 | 0.0088381 | -0.006513 | 64.856 | -58.1314 | 0.050354 | -58.3694 | 64.8376 | -58.2504 | -58.3099 | -58.1451 | 0.064087 | -58.4885 | 64.8514 | 64.769 | -58.2596 | -58.3511 | -0.068664 | -0.12817 | 0.027465 | 0.050354 | -0.18768 | -0.059509 | 0.045776 | -0.07782 | -0.16937 | 0.041198 | 0.036621 | -0.3067 | -0.13733 | -0.041199 | 123.0194 | 123.0377 | 58.2321 | -123.1201 | 123.0331 | 122.9507 | 58.2458 | -123.1613
79.7031 | 123.3032 | -58.1635 | 64.7781 | -0.011739 | -0.031352 | 0.070968 | -0.010953 | 0.068351 | -0.019813 | 0.00030367 | 0.17427 | 0.00056556 | 0.035966 | 0.054145 | -0.0071839 | 0.015917 | 64.8697 | -58.0765 | 0.050354 | -58.3786 | 64.769 | -58.2092 | -58.2504 | -58.0811 | 0.1831 | -58.3603 | 64.8056 | 64.7461 | -58.223 | -58.3145 | -0.045777 | -0.086975 | -0.009155 | 0.086975 | -0.21515 | -0.12817 | 0.091553 | -0.059509 | -0.15106 | 0.027466 | 0.082397 | -0.19684 | -0.045777 | -0.032043 | 122.9324 | 123.0331 | 58.2138 | -123.0286 | 122.9691 | 122.9095 | 58.3466 | -123.0927
80.6406 | 123.2162 | -58.223 | 64.801 | 0.11033 | 0.0038952 | 0.06456 | 0.01575 | 0.068351 | 0.015435 | 0.0056447 | -1.2753 | 0.0091106 | 0.065873 | 0.0456 | 0.0067021 | -0.019331 | 64.8834 | -58.1635 | -0.032043 | -58.5663 | 64.7827 | -58.2687 | -58.3099 | -58.1406 | 0.07782 | -58.4747 | 64.8422 | 64.7736 | -58.2733 | -58.342 | -0.045777 | -0.086976 | -0.01831 | 0.059509 | -0.34332 | -0.25635 | 0.082398 | -0.050354 | -0.11902 | 0.041199 | 0.082397 | -0.25177 | -0.13275 | -0.027465 | 123.0057 | 123.1064 | 58.1909 | -123.111 | 123.0652 | 122.9965 | 58.3008 | -123.143
81.7031 | 123.2941 | -58.1635 | 64.7781 | -0.34743 | -0.022808 | 0.083786 | -0.010953 | 0.059806 | -0.033698 | 0.0013717 | 0.067459 | -0.0090474 | 0.049852 | 0.057349 | -0.014661 | 0.005236 | 64.8788 | -58.0124 | 0.11444 | -58.3557 | 64.7781 | -58.1863 | -58.2596 | -58.0856 | 0.17853 | -58.3603 | 64.8056 | 64.7278 | -58.2413 | -58.3466 | -0.022888 | -0.096131 | 0 | 0.15106 | -0.19226 | -0.09613 | 0.10071 | -0.07782 | -0.18311 | 0.027466 | 0.07782 | -0.19684 | -0.013733 | -0.050354 | 122.9416 | 123.0423 | 58.2779 | -123.0377 | 122.9691 | 122.8912 | 58.342 | -123.1247
82.6406 | 123.2117 | -58.2367 | 64.769 | 0.095073 | 0.013508 | 0.067764 | 0.0061368 | 0.065146 | 0.028253 | 0.0035077 | -0.66496 | 0.0080426 | 0.075486 | 0.053077 | 0.012042 | -0.009718 | 64.8697 | -58.1406 | 0.045776 | -58.5617 | 64.7964 | -58.2596 | -58.2962 | -58.1543 | 0.050354 | -58.4839 | 64.8651 | 64.7369 | -58.2642 | -58.3603 | -0.022889 | -0.05951 | 0.027466 | 0.09613 | -0.32501 | -0.2655 | 0.10071 | -0.027466 | -0.1236 | 0.09613 | 0.082397 | -0.24719 | -0.1236 | -0.032044 | 123.0331 | 123.1064 | 58.2825 | -123.0652 | 123.1018 | 122.9736 | 58.287 | -123.1293
83.7031 | 123.3215 | -58.1589 | 64.7827 | 0.079814 | -0.018535 | 0.072037 | -0.019498 | 0.072623 | -0.020881 | -0.013582 | 0.28108 | -0.0058434 | 0.061601 | 0.060554 | -0.0061159 | -0.00010499 | 64.8651 | -58.0582 | 0.059509 | -58.374 | 64.7736 | -58.2184 | -58.2458 | -58.0261 | 0.17853 | -58.3694 | 64.7919 | 64.7324 | -58.2321 | -58.3008 | -0.059509 | -0.086975 | -0.009155 | 0.10071 | -0.21515 | -0.12817 | 0.082397 | -0.073242 | -0.14191 | 0.009155 | 0.13275 | -0.21057 | -0.068665 | -0.050354 | 122.9324 | 123.024 | 58.2184 | -123.0286 | 122.9507 | 122.8912 | 58.3374 | -123.0835
84.6406 | 123.2071 | -58.2001 | 64.8102 | 0.079814 | 0.011372 | 0.061355 | 0.022158 | 0.060874 | 0.016503 | -0.0029003 | -0.06987 | -0.010115 | 0.069078 | 0.06803 | 0.0088381 | -0.006513 | 64.8834 | -58.168 | -0.009155 | -58.3923 | 64.8102 | -58.2596 | -58.2779 | -58.1451 | 0.059509 | -58.4793 | 64.8376 | 64.7507 | -58.2642 | -58.3649 | -0.05951 | -0.07782 | 0 | 0.032043 | -0.19226 | -0.11444 | 0.073242 | -0.064087 | -0.16479 | 0.027465 | 0.054931 | -0.27924 | -0.11444 | -0.05951 | 123.0103 | 123.0835 | 58.1909 | -123.0881 | 123.0377 | 122.9507 | 58.2596 | -123.175
85.7031 | 123.2986 | -58.1818 | 64.7919 | 0.049296 | -0.017467 | 0.08165 | -0.010953 | 0.061942 | -0.01554 | -0.0061053 | 0.021682 | -0.0090474 | 0.049852 | 0.057349 | -0.0082519 | 0.00844 | 64.9017 | -58.0124 | 0.09613 | -58.3374 | 64.7964 | -58.2275 | -58.2642 | -58.0856 | 0.18768 | -58.3649 | 64.801 | 64.7324 | -58.2275 | -58.3054 | -0.045776 | -0.082397 | 0.004578 | 0.16937 | -0.15564 | -0.073242 | 0.10986 | -0.045776 | -0.1236 | 0.009155 | 0.096131 | -0.18311 | -0.059509 | -0.059509 | 122.9782 | 123.0835 | 58.2779 | -123.056 | 122.9828 | 122.9141 | 58.3694 | -123.0972
86.6406 | 123.2117 | -58.2001 | 64.801 | 0.00352 | 0.0092362 | 0.063492 | 0.0093408 | 0.082236 | 0.026116 | 0.0088487 | -0.22246 | -0.0037074 | 0.06801 | 0.061622 | -0.0039789 | -0.009718 | 64.8651 | -58.1406 | -0.004578 | -58.4106 | 64.8239 | -58.255 | -58.2779 | -58.1451 | 0.068665 | -58.4702 | 64.8651 | 64.7552 | -58.2687 | -58.3557 | -0.054932 | -0.07782 | 0.022889 | 0.059509 | -0.21057 | -0.13275 | 0.064087 | -0.068665 | -0.15564 | 0.064087 | 0.054931 | -0.27008 | -0.11444 | -0.045776 | 123.024 | 123.0652 | 58.1955 | -123.0789 | 123.0652 | 122.9553 | 58.2687 | -123.1567
87.7031 | 123.2712 | -58.1818 | 64.7781 | 0.33921 | -0.034557 | 0.085922 | -0.00027224 | 0.050193 | -0.027289 | -0.0050373 | 0.35738 | -0.0079794 | 0.065873 | 0.061622 | -0.0082519 | 0.013781 | 64.8056 | -58.1451 | -0.027466 | -58.4061 | 64.7598 | -58.2321 | -58.2962 | -58.1497 | 0.041199 | -58.4381 | 64.8148 | 64.7278 | -58.2367 | -58.3282 | -0.050354 | -0.11444 | -0.01831 | 0.036621 | -0.2243 | -0.10986 | 0.027466 | -0.054931 | -0.14648 | 0.036621 | 0.032044 | -0.25635 | -0.10986 | -0.050354 | 122.9416 | 122.9874 | 58.1543 | -123.0743 | 122.9965 | 122.9095 | 58.223 | -123.1064
88.6406 | 123.1659 | -58.2184 | 64.7781 | 0.095073 | 0.028462 | 0.067764 | 0.010409 | 0.065146 | 0.030389 | -0.0018323 | 0.0064239 | 0.0037696 | 0.076554 | 0.077643 | 0.012042 | -0.018263 | 64.8743 | -58.1497 | -0.022888 | -58.4198 | 64.8239 | -58.2413 | -58.2779 | -58.1406 | 0.041199 | -58.4976 | 64.8422 | 64.7644 | -58.2825 | -58.3557 | -0.022888 | -0.059509 | 0.045777 | 0.068665 | -0.20142 | -0.14191 | 0.096131 | -0.064087 | -0.13733 | 0.064087 | 0.07782 | -0.27924 | -0.14191 | -0.013733 | 123.0423 | 123.0927 | 58.1955 | -123.056 | 123.0606 | 122.9828 | 58.2596 | -123.1338
89.7031 | 123.2895 | -58.1772 | 64.769 | 0.15611 | -0.011058 | 0.075241 | 0.0018638 | 0.055533 | -0.01554 | -0.0018323 | 0.26582 | 0.0016336 | 0.041307 | 0.055213 | -0.011456 | 0.009508 | 64.801 | -58.1223 | 0.004578 | -58.3969 | 64.7827 | -58.2458 | -58.3008 | -58.1085 | 0.10071 | -58.4198 | 64.8193 | 64.7415 | -58.2275 | -58.3328 | -0.068665 | -0.1236 | 0.013733 | 0.054932 | -0.21973 | -0.096131 | 0.032043 | -0.050354 | -0.15564 | 0.050354 | 0.068664 | -0.24262 | -0.086975 | -0.027466 | 122.9599 | 122.9782 | 58.1818 | -123.0698 | 122.9965 | 122.9187 | 58.2779 | -123.1018
90.6406 | 123.2254 | -58.2321 | 64.7781 | 0.064555 | 0.015645 | 0.070968 | 0.010409 | 0.065146 | 0.016503 | 0.0056447 | -0.06987 | 0.0016336 | 0.069078 | 0.053077 | 0.0067021 | -0.002241 | 64.8834 | -58.1543 | 0.004578 | -58.3923 | 64.7964 | -58.2367 | -58.2779 | -58.1543 | 0.068665 | -58.4976 | 64.8468 | 64.7598 | -58.2596 | -58.3603 | -0.004577 | -0.045776 | 0.018311 | 0.07782 | -0.16022 | -0.11444 | 0.10529 | -0.027466 | -0.12817 | 0.068665 | 0.07782 | -0.2655 | -0.13733 | -0.01831 | 123.0286 | 123.1155 | 58.2367 | -123.056 | 123.0789 | 122.9919 | 58.3008 | -123.1384
91.7031 | 123.2803 | -58.168 | 64.7827 | 0.034038 | -0.023876 | 0.074173 | 0.0039998 | 0.067282 | -0.026221 | -0.0093093 | 0.20479 | -0.0069114 | 0.044511 | 0.070167 | 0.0013611 | 0.002032 | 64.8376 | -58.0627 | 0.041199 | -58.374 | 64.7919 | -58.223 | -58.2413 | -58.0856 | 0.13733 | -58.3832 | 64.801 | 64.7369 | -58.2367 | -58.3145 | -0.054931 | -0.073242 | 0.009155 | 0.10529 | -0.20599 | -0.13275 | 0.054931 | -0.068664 | -0.14648 | 0.01831 | 0.082398 | -0.21515 | -0.068665 | -0.045777 | 122.9599 | 123.0057 | 58.2092 | -123.024 | 122.9691 | 122.905 | 58.3054 | -123.0972
92.6406 | 123.1934 | -58.2092 | 64.7781 | -0.25588 | 0.01244 | 0.073105 | 0.00079576 | 0.066214 | 0.016503 | 0.0035077 | -0.28349 | 0.0027016 | 0.053056 | 0.061622 | 0.0034971 | -0.009718 | 64.8468 | -58.1589 | -0.018311 | -58.4015 | 64.8605 | -58.2504 | -58.2779 | -58.1497 | 0.086975 | -58.4839 | 64.8605 | 64.7552 | -58.255 | -58.3603 | -0.041198 | -0.068664 | 0.082398 | 0.050354 | -0.19226 | -0.1236 | 0.068665 | -0.045776 | -0.15106 | 0.082398 | 0.05951 | -0.27466 | -0.1236 | -0.022888 | 123.0698 | 123.056 | 58.1909 | -123.056 | 123.0698 | 122.9645 | 58.2962 | -123.1384
93.6406 | 123.1979 | -58.2275 | 64.7964 | 0.15611 | 0.014576 | 0.070968 | -0.0034762 | 0.056601 | 0.012231 | -0.0039683 | 0.0064239 | 0.0016336 | 0.071214 | 0.066962 | 0.0077701 | -0.007581 | 64.856 | -58.1451 | -0.032043 | -58.4244 | 64.8102 | -58.255 | -58.2733 | -58.1589 | 0.027466 | -58.5068 | 64.8193 | 64.7552 | -58.2504 | -58.3694 | -0.027466 | -0.045776 | 0.013733 | 0.082397 | -0.19684 | -0.15106 | 0.059509 | -0.022888 | -0.14191 | 0.022888 | 0.068664 | -0.27924 | -0.13733 | -0.041199 | 123.0377 | 123.0835 | 58.1955 | -123.0698 | 123.0469 | 122.9828 | 58.255 | -123.1659
94.7031 | 123.2712 | -58.1635 | 64.7736 | -0.088033 | -0.032421 | 0.066696 | -0.0098852 | 0.061942 | -0.020881 | -0.012513 | 0.036941 | -0.0058434 | 0.05092 | 0.059485 | 0.0045661 | -0.00010499 | 64.8743 | -58.0353 | 0.09613 | -58.342 | 64.801 | -58.2092 | -58.2413 | -58.0902 | 0.20142 | -58.3832 | 64.8376 | 64.7324 | -58.2321 | -58.3008 | -0.045777 | -0.07782 | 0.027465 | 0.12817 | -0.17853 | -0.10071 | 0.10071 | -0.068665 | -0.13733 | 0.064086 | 0.073242 | -0.21973 | -0.082398 | -0.041199 | 122.9645 | 123.0377 | 58.2596 | -123.0148 | 123.0011 | 122.8958 | 58.3649 | -123.0743
95.6406 | 123.1979 | -58.2047 | 64.7873 | 0.079814 | 0.014576 | 0.060287 | 0.011477 | 0.06301 | 0.017572 | -0.0039683 | 0.036941 | -0.00050244 | 0.070146 | 0.0456 | 0.012042 | -0.012922 | 64.8605 | -58.1314 | -0.018311 | -58.4015 | 64.8056 | -58.2413 | -58.2779 | -58.1497 | 0.045776 | -58.493 | 64.8605 | 64.7278 | -58.2825 | -58.3466 | -0.036621 | -0.073242 | 0.018311 | 0.073242 | -0.19684 | -0.1236 | 0.073243 | -0.07782 | -0.14191 | 0.073243 | 0.054932 | -0.28839 | -0.14648 | -0.059509 | 123.0103 | 123.0652 | 58.1863 | -123.0652 | 123.0652 | 122.9324 | 58.2504 | -123.1338
96.7031 | 123.2895 | -58.1863 | 64.7873 | -0.17959 | -0.0046498 | 0.068832 | -0.0098852 | 0.061942 | -0.03263 | -0.0082413 | -0.11565 | -0.0047754 | 0.041307 | 0.058417 | -0.0071839 | 0.007372 | 64.8743 | -58.0215 | 0.09613 | -58.3466 | 64.7781 | -58.223 | -58.2596 | -58.0811 | 0.19226 | -58.3557 | 64.8102 | 64.7278 | -58.2092 | -58.287 | -0.036621 | -0.073243 | -0.009155 | 0.16479 | -0.16022 | -0.086975 | 0.086976 | -0.022889 | -0.10071 | 0.022889 | 0.10529 | -0.16937 | -0.068665 | -0.059509 | 122.9645 | 123.0606 | 58.2825 | -123.0469 | 122.9965 | 122.9141 | 58.3786 | -123.0743
97.6406 | 123.2071 | -58.2275 | 64.7873 | 0.12559 | 0.017781 | 0.072037 | 0.0093408 | 0.065146 | 0.014367 | 0.014189 | 0.15901 | -0.0026384 | 0.081895 | 0.053077 | 0.0088381 | -0.002241 | 64.8285 | -58.1589 | -0.045776 | -58.4106 | 64.8148 | -58.2413 | -58.3054 | -58.1863 | 0.004578 | -58.5297 | 64.856 | 64.7324 | -58.2779 | -58.3694 | -0.013733 | -0.07782 | 0.027466 | 0.068664 | -0.18311 | -0.10529 | 0.041199 | -0.050354 | -0.14191 | 0.068665 | 0.041199 | -0.30212 | -0.16022 | -0.054931 | 123.0423 | 123.056 | 58.1818 | -123.0927 | 123.0835 | 122.9599 | 58.2321 | -123.1567
98.7031 | 123.2391 | -58.1955 | 64.7919 | -0.14907 | -0.016399 | 0.082718 | -0.0066812 | 0.066214 | -0.016608 | 0.0045757 | -0.024094 | -0.015456 | 0.046647 | 0.080848 | -0.00077485 | -0.001173 | 64.8743 | -58.0582 | 0.10071 | -58.3603 | 64.769 | -58.2321 | -58.2413 | -58.0948 | 0.1831 | -58.3923 | 64.8193 | 64.7461 | -58.2001 | -58.3237 | -0.036621 | -0.045776 | -0.022888 | 0.13733 | -0.16479 | -0.11902 | 0.082398 | -0.004577 | -0.12817 | 0.027466 | 0.10071 | -0.19684 | -0.068665 | -0.045776 | 122.9645 | 123.0698 | 58.2962 | -123.0331 | 123.0148 | 122.9416 | 58.3786 | -123.1155
99.6406 | 123.2117 | -58.2504 | 64.7964 | 0.00352 | 0.026326 | 0.056015 | 0.0072048 | 0.064078 | 0.0058221 | 0.0035077 | -0.14616 | 0.0016336 | 0.077623 | 0.058417 | 0.0088381 | -0.00865 | 64.8422 | -58.1268 | 0.004578 | -58.3969 | 64.8285 | -58.2504 | -58.287 | -58.1497 | 0.064087 | -58.4747 | 64.8468 | 64.7552 | -58.2825 | -58.3511 | 0 | -0.036621 | 0.032043 | 0.1236 | -0.14648 | -0.10986 | 0.045776 | -0.032044 | -0.10071 | 0.050354 | 0.10071 | -0.2243 | -0.1236 | -0.041199 | 123.0789 | 123.0927 | 58.255 | -123.0835 | 123.0972 | 123.0057 | 58.3145 | -123.1476
100.7031 | 123.3444 | -58.1589 | 64.769 | -0.011739 | -0.047374 | 0.068832 | -0.0045452 | 0.052329 | -0.036902 | -0.0071733 | 0.0522 | -0.011183 | 0.045579 | 0.075507 | -0.0018429 | 0.007372 | 64.8514 | -58.0307 | 0.07782 | -58.3649 | 64.7873 | -58.2458 | -58.2504 | -58.0536 | 0.19226 | -58.3511 | 64.8148 | 64.7232 | -58.2275 | -58.3145 | -0.086975 | -0.091552 | 0.01831 | 0.12817 | -0.20599 | -0.11444 | 0.082397 | -0.068664 | -0.15564 | 0.045776 | 0.10529 | -0.19226 | -0.036621 | -0.045776 | 122.9462 | 123.0103 | 58.2367 | -123.0194 | 122.9736 | 122.8821 | 58.3511 | -123.0835
101.6406 | 123.2117 | -58.2321 | 64.8102 | 0.064555 | 0.0038952 | 0.08165 | 0.013613 | 0.064078 | 0.026116 | 0.00030367 | 0.036941 | 0.0037696 | 0.076554 | 0.075507 | 0.0067021 | -0.004377 | 64.8743 | -58.1268 | 0.004578 | -58.4061 | 64.8193 | -58.2687 | -58.287 | -58.1451 | 0.041199 | -58.5022 | 64.856 | 64.7507 | -58.2733 | -58.3557 | -0.036621 | -0.054931 | 0.009155 | 0.10529 | -0.17395 | -0.11902 | 0.064087 | -0.041198 | -0.1236 | 0.045776 | 0.086975 | -0.27008 | -0.14648 | -0.05951 | 123.0515 | 123.1064 | 58.2367 | -123.0972 | 123.0881 | 122.9828 | 58.2733 | -123.1659
102.7031 | 123.262 | -58.1635 | 64.7507 | -0.011739 | -0.020671 | 0.082718 | -0.0045452 | 0.052329 | -0.021949 | -0.0018323 | 0.22005 | -0.012251 | 0.045579 | 0.042396 | -0.0050469 | 0.006304 | 64.8651 | -58.0719 | 0.050354 | -58.3694 | 64.7919 | -58.2138 | -58.2687 | -58.0902 | 0.15106 | -58.3603 | 64.8148 | 64.6912 | -58.2275 | -58.3145 | -0.050354 | -0.10529 | 0.041199 | 0.091553 | -0.20599 | -0.10071 | 0.11444 | -0.064087 | -0.15106 | 0.064087 | 0.073242 | -0.19684 | -0.045777 | -0.059509 | 122.9553 | 123.0286 | 58.2138 | -123.0194 | 122.9782 | 122.8546 | 58.3145 | -123.0652
103.6406 | 123.1522 | -58.2687 | 64.801 | 0.27818 | 0.017781 | 0.061355 | 0.012545 | 0.073691 | 0.015435 | -0.0018323 | 0.3116 | -0.00050244 | 0.07335 | 0.055213 | 0.0013611 | -0.01399 | 64.7964 | -58.2092 | -0.10071 | -58.4427 | 64.8285 | -58.2733 | -58.3054 | -58.2367 | -0.064087 | -58.5846 | 64.8514 | 64.7415 | -58.3054 | -58.3832 | -0.004577 | -0.036621 | 0.027466 | 0.059509 | -0.17395 | -0.13733 | -0.004577 | -0.036621 | -0.11444 | 0.050354 | 0.032044 | -0.31586 | -0.20142 | -0.059509 | 123.0972 | 123.0652 | 58.168 | -123.1064 | 123.1201 | 123.0103 | 58.2047 | -123.1842
104.7031 | 123.2666 | -58.1955 | 64.7781 | 0.2324 | -0.014263 | 0.077377 | -0.0098852 | 0.053397 | -0.024085 | -0.0082413 | 0.35738 | -0.0037074 | 0.054124 | 0.059485 | -0.010388 | 0.005236 | 64.7919 | -58.1451 | -0.032043 | -58.4106 | 64.7781 | -58.223 | -58.2687 | -58.1543 | 0.07782 | -58.4335 | 64.7919 | 64.7369 | -58.2184 | -58.3282 | -0.027465 | -0.073242 | 0 | 0.050354 | -0.21515 | -0.14191 | 0.013733 | -0.022888 | -0.13275 | 0.013733 | 0.041199 | -0.23804 | -0.10529 | -0.041199 | 122.9736 | 122.9874 | 58.1635 | -123.0469 | 122.9874 | 122.9324 | 58.2733 | -123.1064
105.6406 | 123.1934 | -58.223 | 64.801 | -0.14907 | 0.010304 | 0.065628 | 0.022158 | 0.077964 | 0.013299 | -0.0093093 | -0.25298 | -0.0037074 | 0.06801 | 0.065894 | -0.0029109 | -0.005445 | 64.8376 | -58.1726 | -0.027466 | -58.3923 | 64.8376 | -58.2458 | -58.2916 | -58.168 | 0.086975 | -58.493 | 64.8697 | 64.7644 | -58.2642 | -58.3374 | -0.022889 | -0.068665 | 0.036621 | 0.050354 | -0.16937 | -0.10071 | 0.036621 | -0.041199 | -0.11444 | 0.068665 | 0.054931 | -0.27008 | -0.15564 | -0.036621 | 123.0606 | 123.0606 | 58.1955 | -123.0927 | 123.0927 | 122.9874 | 58.3099 | -123.1384
106.7031 | 123.3032 | -58.1818 | 64.7873 | -0.10329 | -0.035625 | 0.079513 | -0.0013402 | 0.06301 | -0.020881 | -0.00076433 | -0.10039 | -0.010115 | 0.061601 | 0.048804 | -0.016797 | -0.002241 | 64.8972 | -58.049 | 0.09613 | -58.342 | 64.7827 | -58.2047 | -58.2458 | -58.0765 | 0.1831 | -58.3923 | 64.8239 | 64.7232 | -58.2275 | -58.3054 | -0.022888 | -0.064087 | -0.004577 | 0.13275 | -0.16022 | -0.09613 | 0.10986 | -0.045776 | -0.1236 | 0.036622 | 0.10529 | -0.21057 | -0.086975 | -0.064086 | 122.9645 | 123.0789 | 58.2779 | -123.0331 | 123.0057 | 122.905 | 58.3649 | -123.0927
107.6406 | 123.1888 | -58.2275 | 64.7781 | -0.072774 | 0.02419 | 0.077377 | 0.016818 | 0.070487 | 0.0058221 | 0.0024397 | -0.11565 | -0.0037074 | 0.05626 | 0.060554 | 0.01311 | -0.009718 | 64.8514 | -58.1406 | 0 | -58.3923 | 64.8239 | -58.2413 | -58.2825 | -58.1543 | 0.059509 | -58.4839 | 64.8514 | 64.769 | -58.2596 | -58.3466 | -0.013733 | -0.054932 | 0.045777 | 0.086975 | -0.16479 | -0.10986 | 0.073242 | -0.032044 | -0.11902 | 0.073242 | 0.073242 | -0.25635 | -0.13733 | -0.009155 | 123.0515 | 123.0789 | 58.2275 | -123.0606 | 123.0789 | 122.9965 | 58.287 | -123.1247
108.7031 | 123.2712 | -58.168 | 64.7736 | -0.16433 | -0.036693 | 0.0699 | -0.0098852 | 0.050193 | -0.016608 | -0.0050373 | 0.0064239 | -0.01332 | 0.074418 | 0.057349 | -0.00077485 | -0.001173 | 64.888 | -58.0353 | 0.086975 | -58.3466 | 64.7919 | -58.2047 | -58.2733 | -58.0811 | 0.19226 | -58.3557 | 64.801 | 64.7507 | -58.2413 | -58.3282 | -0.036621 | -0.10528 | 0.01831 | 0.13275 | -0.17853 | -0.073243 | 0.11444 | -0.073242 | -0.16022 | 0.027465 | 0.086975 | -0.18768 | -0.027466 | -0.022889 | 122.9599 | 123.056 | 58.255 | -123.0469 | 122.9691 | 122.9187 | 58.3603 | -123.1018
109.6406 | 123.2346 | -58.2092 | 64.769 | 0.064555 | 0.027394 | 0.063492 | 0.0039998 | 0.064078 | 0.029321 | -0.0039683 | -0.085129 | 0.011247 | 0.076554 | 0.065894 | 0.0067021 | -0.016126 | 64.8468 | -58.136 | 0 | -58.4061 | 64.8148 | -58.2275 | -58.3237 | -58.1497 | 0.073242 | -58.4793 | 64.8239 | 64.7324 | -58.255 | -58.3786 | -0.01831 | -0.11444 | 0.045776 | 0.073243 | -0.19684 | -0.082398 | 0.07782 | -0.045776 | -0.16937 | 0.054932 | 0.05951 | -0.27008 | -0.10071 | -0.036621 | 123.024 | 123.056 | 58.2092 | -123.0927 | 123.0331 | 122.9416 | 58.2825 | -123.1476
110.6406 | 123.1842 | -58.223 | 64.8056 | -0.042256 | 0.016713 | 0.06456 | 0.0082728 | 0.070487 | 0.014367 | 0.0099167 | -0.10039 | 0.0069746 | 0.046647 | 0.050941 | 0.0045661 | -0.00010499 | 64.8468 | -58.1406 | 0.004578 | -58.4152 | 64.8285 | -58.2184 | -58.3008 | -58.1223 | 0.068665 | -58.4702 | 64.8331 | 64.7415 | -58.255 | -58.3603 | 0.004577 | -0.07782 | 0.022888 | 0.082397 | -0.19226 | -0.11444 | 0.041199 | -0.032044 | -0.13733 | 0.027466 | 0.10071 | -0.24719 | -0.10986 | -0.064087 | 123.0515 | 123.0698 | 58.2275 | -123.1064 | 123.056 | 122.9645 | 58.2916 | -123.1659
111.6406 | 123.2025 | -58.2275 | 64.8056 | -0.072774 | 0.020985 | 0.070968 | 0.0082728 | 0.067282 | 0.011163 | 0.0024397 | -0.054612 | 0.0080426 | 0.07335 | 0.056281 | -0.0018429 | -0.009718 | 64.8605 | -58.1406 | 0.004578 | -58.4061 | 64.8239 | -58.2458 | -58.2779 | -58.1543 | 0.086975 | -58.4656 | 64.856 | 64.7552 | -58.2687 | -58.3603 | -0.018311 | -0.050354 | 0.018311 | 0.086975 | -0.17853 | -0.12817 | 0.054932 | -0.041199 | -0.13275 | 0.050354 | 0.073242 | -0.23804 | -0.10529 | -0.050354 | 123.0515 | 123.0881 | 58.2321 | -123.0835 | 123.0835 | 122.9828 | 58.3145 | -123.1659
112.6406 | 123.2162 | -58.2092 | 64.801 | -0.16433 | 0.026326 | 0.06456 | 0.0072048 | 0.061942 | 0.0026181 | -0.0071733 | -0.25298 | -0.0015704 | 0.069078 | 0.053077 | -0.0050469 | -0.005445 | 64.7964 | -58.168 | -0.004578 | -58.4152 | 64.8239 | -58.2367 | -58.2962 | -58.1863 | 0.068665 | -58.4702 | 64.888 | 64.7736 | -58.2458 | -58.3511 | -0.027465 | -0.086975 | 0.022889 | 0.041199 | -0.20599 | -0.11902 | -0.004577 | -0.036621 | -0.14191 | 0.086975 | 0.022889 | -0.26093 | -0.11902 | -0.027465 | 123.0331 | 123.0057 | 58.2047 | -123.0972 | 123.0972 | 122.9828 | 58.2779 | -123.1522
113.7031 | 123.2986 | -58.1589 | 64.7644 | -0.011739 | -0.014263 | 0.085922 | -0.016294 | 0.058738 | -0.023017 | -0.00076433 | 0.38789 | -0.010115 | 0.041307 | 0.066962 | -0.014661 | 0.006304 | 64.856 | -58.0582 | 0.059509 | -58.3694 | 64.7644 | -58.1909 | -58.2413 | -58.0673 | 0.16022 | -58.3511 | 64.7964 | 64.7415 | -58.2367 | -58.3282 | -0.032043 | -0.082397 | 0 | 0.10071 | -0.21057 | -0.12817 | 0.091553 | -0.077819 | -0.16937 | 0.032044 | 0.091553 | -0.19226 | -0.022888 | -0.022888 | 122.9233 | 123.0148 | 58.2184 | -123.0057 | 122.9553 | 122.9004 | 58.3191 | -123.0927
114.6406 | 123.1613 | -58.2138 | 64.7964 | -0.11855 | 0.013508 | 0.075241 | 0.017886 | 0.068351 | 0.0026181 | 0.0035077 | -0.17668 | -0.0026384 | 0.078691 | 0.052009 | 0.0024291 | -0.007581 | 64.8376 | -58.136 | -0.009155 | -58.3878 | 64.8422 | -58.255 | -58.2687 | -58.1589 | 0.10071 | -58.4747 | 64.8468 | 64.7736 | -58.2596 | -58.3328 | -0.041199 | -0.054932 | 0.045776 | 0.07782 | -0.17395 | -0.11902 | 0.041198 | -0.045777 | -0.11902 | 0.050354 | 0.054931 | -0.26093 | -0.14191 | -0.022888 | 123.056 | 123.0515 | 58.2047 | -123.0652 | 123.0606 | 122.9874 | 58.3145 | -123.1293
115.7031 | 123.2986 | -58.1635 | 64.7964 | -0.042256 | -0.029216 | 0.076309 | -0.0077492 | 0.060874 | -0.030494 | -0.0018323 | 0.021682 | -0.015456 | 0.042375 | 0.053077 | -0.0082519 | 0.0031 | 64.8743 | -58.0032 | 0.10529 | -58.342 | 64.7873 | -58.2138 | -58.2596 | -58.0811 | 0.20142 | -58.3694 | 64.7964 | 64.7141 | -58.2321 | -58.2962 | -0.050354 | -0.096131 | -0.009156 | 0.16022 | -0.17853 | -0.082397 | 0.07782 | -0.068665 | -0.13275 | 0 | 0.082397 | -0.20599 | -0.073242 | -0.082398 | 122.9507 | 123.0377 | 58.2687 | -123.056 | 122.9599 | 122.8775 | 58.3649 | -123.0927
116.6406 | 123.1613 | -58.2504 | 64.7873 | 0.21714 | 0.032734 | 0.060287 | 0.018954 | 0.065146 | 0.016503 | -0.00076433 | 0.097976 | -0.0037074 | 0.064805 | 0.053077 | -0.0039789 | -0.007581 | 64.801 | -58.2047 | -0.09613 | -58.4518 | 64.8056 | -58.2642 | -58.2962 | -58.2321 | -0.041199 | -58.5388 | 64.8468 | 64.7507 | -58.2825 | -58.3557 | -0.013733 | -0.045777 | 0.018311 | 0.045776 | -0.20142 | -0.15564 | 0.013733 | -0.032044 | -0.10529 | 0.05951 | 0.01831 | -0.28839 | -0.1831 | -0.036621 | 123.056 | 123.0515 | 58.1543 | -123.0835 | 123.0972 | 123.0011 | 58.2092 | -123.143
117.7031 | 123.2208 | -58.1818 | 64.7644 | 0.26292 | -0.032421 | 0.083786 | -0.0024082 | 0.044852 | -0.023017 | 0.0024397 | 0.40315 | -0.0058434 | 0.049852 | 0.053077 | -0.011456 | 0.013781 | 64.7736 | -58.1497 | -0.036621 | -58.4152 | 64.769 | -58.255 | -58.2962 | -58.1543 | 0.059509 | -58.4427 | 64.8193 | 64.7141 | -58.2642 | -58.3374 | -0.073242 | -0.11444 | 0.004578 | 0.032044 | -0.23346 | -0.11902 | 0.009156 | -0.082397 | -0.15564 | 0.054932 | 0.027466 | -0.26093 | -0.10529 | -0.050354 | 122.9507 | 122.9553 | 58.1451 | -123.0606 | 123.0011 | 122.8958 | 58.2413 | -123.1018
118.6406 | 123.2071 | -58.2092 | 64.8148 | -0.13381 | 0.018849 | 0.063492 | 0.00079576 | 0.073691 | 0.012231 | 0.0045757 | -0.11565 | 0.00056556 | 0.05092 | 0.060554 | 0.0099061 | -0.015058 | 64.8697 | -58.1543 | -0.004578 | -58.4015 | 64.8148 | -58.255 | -58.287 | -58.1406 | 0.07782 | -58.4747 | 64.856 | 64.769 | -58.255 | -58.3466 | -0.045776 | -0.077819 | 0 | 0.054932 | -0.19226 | -0.11444 | 0.054932 | -0.045776 | -0.13733 | 0.041199 | 0.068665 | -0.2655 | -0.12817 | -0.045776 | 123.024 | 123.0789 | 58.2047 | -123.1018 | 123.0652 | 122.9782 | 58.287 | -123.1613
119.7031 | 123.2483 | -58.2001 | 64.7736 | 0.29344 | -0.020671 | 0.077377 | 0.0072048 | 0.060874 | -0.019813 | -0.00076433 | 0.58626 | -0.00050244 | 0.05092 | 0.053077 | -0.0029109 | -0.001173 | 64.7919 | -58.1406 | -0.032043 | -58.4061 | 64.7964 | -58.223 | -58.2825 | -58.1451 | 0.041199 | -58.4564 | 64.7781 | 64.7141 | -58.2596 | -58.3511 | -0.022888 | -0.082398 | 0.022888 | 0.059509 | -0.20599 | -0.1236 | 0.01831 | -0.05951 | -0.15106 | 0.004577 | 0.054931 | -0.25635 | -0.10529 | -0.05951 | 122.9965 | 122.9919 | 58.168 | -123.056 | 122.9782 | 122.9141 | 58.2413 | -123.1247
120.6406 | 123.2071 | -58.2138 | 64.7781 | -0.14907 | 0.019917 | 0.065628 | 0.01575 | 0.066214 | 0.017572 | -0.0018323 | -0.23772 | 0.00056556 | 0.066941 | 0.06269 | -0.00077485 | -0.017194 | 64.8422 | -58.1635 | 0 | -58.3969 | 64.8193 | -58.2504 | -58.2779 | -58.1451 | 0.10529 | -58.4793 | 64.8788 | 64.7507 | -58.2458 | -58.3466 | -0.036621 | -0.064087 | 0.041199 | 0.050354 | -0.18311 | -0.11902 | 0.064087 | -0.032044 | -0.13275 | 0.10071 | 0.068664 | -0.2655 | -0.13275 | -0.027466 | 123.0331 | 123.056 | 58.2138 | -123.056 | 123.0927 | 122.9645 | 58.3191 | -123.1247
121.7031 | 123.2574 | -58.2001 | 64.7736 | -0.25588 | -0.02708 | 0.079513 | -0.0098852 | 0.066214 | -0.01554 | -0.010377 | -0.11565 | -0.01332 | 0.053056 | 0.061622 | -0.0082519 | -0.004377 | 64.8651 | -58.0353 | 0.086975 | -58.3603 | 64.7598 | -58.2092 | -58.2504 | -58.0948 | 0.17853 | -58.3878 | 64.8285 | 64.7232 | -58.2458 | -58.342 | -0.009156 | -0.050354 | -0.013733 | 0.1648 | -0.16022 | -0.10986 | 0.091552 | -0.045777 | -0.14191 | 0.054931 | 0.10529 | -0.18768 | -0.045776 | -0.050354 | 122.9599 | 123.0652 | 58.287 | -123.024 | 123.0286 | 122.9233 | 58.3786 | -123.1155
122.6406 | 123.175 | -58.1955 | 64.7964 | 0.11033 | 0.017781 | 0.070968 | 0.012545 | 0.069419 | 0.010095 | -0.0039683 | -0.11565 | -0.0047754 | 0.054124 | 0.060554 | 0.0067021 | -0.010786 | 64.8697 | -58.1406 | 0 | -58.4061 | 64.8376 | -58.2458 | -58.2825 | -58.1451 | 0.064087 | -58.4656 | 64.856 | 64.7415 | -58.255 | -58.3466 | -0.050354 | -0.086975 | 0.041198 | 0.054932 | -0.21057 | -0.1236 | 0.073242 | -0.059509 | -0.15106 | 0.059509 | 0.050354 | -0.27008 | -0.11902 | -0.054932 | 123.0331 | 123.0652 | 58.1955 | -123.0789 | 123.0515 | 122.937 | 58.2596 | -123.143
123.7031 | 123.23 | -58.1955 | 64.7644 | 0.36973 | -0.020671 | 0.08699 | -0.0077492 | 0.071555 | -0.020881 | -0.0039683 | 0.35738 | -0.01332 | 0.053056 | 0.063758 | -0.00077485 | 0.009508 | 64.7919 | -58.136 | -0.027466 | -58.429 | 64.7736 | -58.2504 | -58.2596 | -58.1406 | 0.041199 | -58.4518 | 64.8148 | 64.7507 | -58.2642 | -58.3603 | -0.054931 | -0.064087 | 0.009156 | 0.05951 | -0.23346 | -0.16937 | 0.027466 | -0.068664 | -0.16479 | 0.050354 | 0.054932 | -0.25635 | -0.091552 | -0.013733 | 122.9691 | 122.9874 | 58.168 | -123.024 | 123.0103 | 122.9462 | 58.2367 | -123.1247
124.6406 | 123.2483 | -58.2047 | 64.8056 | -0.026997 | 0.015645 | 0.070968 | 0.02109 | 0.067282 | 0.019708 | 0.0035077 | -0.23772 | -0.0015704 | 0.09044 | 0.056281 | 0.0056341 | -0.010786 | 64.8514 | -58.1543 | 0.009155 | -58.3923 | 64.8422 | -58.2367 | -58.2916 | -58.1497 | 0.10986 | -58.4518 | 64.8651 | 64.7827 | -58.2321 | -58.3603 | -0.032043 | -0.086975 | 0.036621 | 0.050354 | -0.18768 | -0.10071 | 0.045776 | -0.027466 | -0.15564 | 0.059509 | 0.054932 | -0.24719 | -0.091552 | -0.022888 | 123.0469 | 123.056 | 58.2138 | -123.0972 | 123.0698 | 122.9874 | 58.3145 | -123.1659
125.7031 | 123.2391 | -58.223 | 64.769 | 0.44602 | -0.023876 | 0.083786 | -0.0034762 | 0.058738 | -0.023017 | -0.0029003 | 0.43367 | -0.0069114 | 0.05092 | 0.06269 | -0.015729 | 0.00844 | 64.801 | -58.1406 | -0.068665 | -58.4152 | 64.7598 | -58.2367 | -58.2642 | -58.1543 | 0.041199 | -58.4473 | 64.801 | 64.7186 | -58.2596 | -58.3603 | -0.013733 | -0.041199 | -0.009155 | 0.082397 | -0.19226 | -0.15106 | 0.032043 | -0.036622 | -0.13733 | 0.032043 | 0.068664 | -0.22431 | -0.086975 | -0.050354 | 122.9828 | 123.024 | 58.1543 | -123.0331 | 123.024 | 122.9416 | 58.2642 | -123.1293
126.6406 | 123.1567 | -58.2001 | 64.8193 | -0.25588 | 0.0017592 | 0.068832 | 0.018954 | 0.064078 | 0.0079581 | 0.0035077 | -0.26824 | 0.0027016 | 0.055192 | 0.050941 | -0.0029109 | -0.009718 | 64.8193 | -58.1772 | -0.032043 | -58.4244 | 64.8514 | -58.2275 | -58.2779 | -58.1726 | 0.059509 | -58.4976 | 64.8651 | 64.7827 | -58.2733 | -58.3282 | -0.027466 | -0.07782 | 0.032043 | 0.022888 | -0.2243 | -0.14648 | 0 | -0.073242 | -0.12817 | 0.045776 | 0.027466 | -0.29755 | -0.16937 | -0.036621 | 123.0515 | 123.0194 | 58.168 | -123.0972 | 123.0652 | 122.9828 | 58.2596 | -123.1476
127.7188 | 123.2986 | -58.2321 | 64.7278 | 0.47654 | 0.0060322 | 0.060287 | 0.0039998 | 0.067282 | 0.0047541 | -0.0061053 | 0.60152 | -0.0047754 | 0.05626 | 0.072303 | 0.0067021 | 0.004168 | 64.8468 | -58.1039 | -0.004578 | -58.3969 | 64.7507 | -58.2367 | -58.2825 | -58.0948 | 0.050354 | -58.4335 | 64.769 | 64.6774 | -58.2504 | -58.3374 | -0.004577 | -0.050354 | 0.022888 | 0.12817 | -0.16479 | -0.11444 | 0.11902 | -0.01831 | -0.10528 | 0.041199 | 0.13733 | -0.20142 | -0.096131 | -0.050354 | 122.9828 | 123.0789 | 58.2275 | -123.0103 | 123.0011 | 122.9095 | 58.2825 | -123.0652
128.6406 | 123.1888 | -58.2047 | 64.7781 | -0.16433 | -0.00037681 | 0.0699 | 0.011477 | 0.084372 | 0.01864 | 0.0077807 | -0.16142 | 0.0037696 | 0.053056 | 0.064826 | 0.0013611 | -0.009718 | 64.856 | -58.1543 | -0.004578 | -58.3832 | 64.8285 | -58.2275 | -58.2779 | -58.1451 | 0.10071 | -58.4747 | 64.8468 | 64.769 | -58.2642 | -58.3374 | -0.022888 | -0.073242 | 0.050354 | 0.050354 | -0.17853 | -0.10529 | 0.07782 | -0.059509 | -0.13275 | 0.068665 | 0.059509 | -0.27008 | -0.13733 | -0.009155 | 123.0331 | 123.0606 | 58.2001 | -123.056 | 123.0515 | 122.9736 | 58.3054 | -123.1155
129.6406 | 123.1934 | -58.2001 | 64.8102 | -0.026997 | -0.0025128 | 0.066696 | 0.0061368 | 0.072623 | 0.021844 | -0.0061053 | -0.28349 | -0.00050244 | 0.058397 | 0.064826 | -0.00077485 | -0.004377 | 64.8193 | -58.1543 | -0.022888 | -58.4152 | 64.8697 | -58.2504 | -58.2779 | -58.1589 | 0.086975 | -58.4656 | 64.8605 | 64.7781 | -58.255 | -58.3603 | -0.050354 | -0.07782 | 0.059509 | 0.045776 | -0.21515 | -0.13733 | 0.009155 | -0.054932 | -0.16022 | 0.050354 | 0.041198 | -0.2655 | -0.10529 | -0.032044 | 123.0698 | 123.0194 | 58.1772 | -123.0881 | 123.0606 | 122.9782 | 58.287 | -123.1705
130.6406 | 123.1934 | -58.2184 | 64.8239 | 0.17137 | 0.0092362 | 0.076309 | 0.010409 | 0.069419 | -0.0016549 | -0.0029003 | -0.16142 | 0.0027016 | 0.061601 | 0.073371 | -0.0071839 | -0.01399 | 64.8056 | -58.1772 | -0.027466 | -58.4244 | 64.8376 | -58.2413 | -58.287 | -58.1726 | 0.086975 | -58.5068 | 64.8651 | 64.7827 | -58.255 | -58.3603 | -0.022888 | -0.068664 | 0.013732 | 0.041199 | -0.20599 | -0.13733 | -0.018311 | -0.036621 | -0.14191 | 0.041198 | 0.045777 | -0.28839 | -0.14648 | -0.041199 | 123.056 | 123.024 | 58.1909 | -123.111 | 123.0835 | 123.0011 | 58.3054 | -123.1842
131.6406 | 123.1338 | -58.2275 | 64.8148 | 3.1926 | 0.016713 | 0.068832 | 0.013613 | 0.065146 | 0.0058221 | -0.00076433 | -0.039353 | 0.0037696 | 0.063737 | 0.066962 | -0.0050469 | -0.00010499 | 64.8193 | -58.2367 | -0.054932 | -58.4152 | 64.8376 | -58.2642 | -58.3099 | -58.1863 | 0.068665 | -58.4885 | 64.8972 | 64.7919 | -58.2825 | -58.3328 | -0.036621 | -0.082398 | 0.022888 | -0.009155 | -0.18768 | -0.10529 | 0.004578 | -0.054932 | -0.10529 | 0.082398 | 0.041199 | -0.26093 | -0.15564 | -0.022888 | 123.0652 | 123.0469 | 58.1726 | -123.1247 | 123.1247 | 123.0194 | 58.2962 | -123.1476
132.7031 | 123.3078 | -58.1406 | 64.7552 | 0.079814 | -0.038829 | 0.082718 | 0.0018638 | 0.060874 | -0.033698 | -0.010377 | 0.29634 | -0.0079794 | 0.045579 | 0.060554 | -0.0071839 | 0.007372 | 64.7964 | -58.0811 | 0.027466 | -58.3923 | 64.769 | -58.2092 | -58.2642 | -58.0948 | 0.12817 | -58.3923 | 64.801 | 64.7186 | -58.255 | -58.3557 | -0.068665 | -0.1236 | 0.013733 | 0.059509 | -0.25177 | -0.12817 | 0.041199 | -0.11444 | -0.21515 | 0.045776 | 0.045776 | -0.25177 | -0.036621 | -0.036621 | 122.9095 | 122.937 | 58.168 | -123.0194 | 122.9416 | 122.8592 | 58.2687 | -123.111
133.6406 | 123.1659 | -58.223 | 64.8376 | -0.24062 | 0.011372 | 0.063492 | 0.016818 | 0.066214 | 0.0036861 | -0.011445 | -1.4584 | 0.0037696 | 0.074418 | 0.052009 | -0.0039789 | -0.005445 | 64.7827 | -58.1863 | -0.018311 | -58.429 | 64.8605 | -58.2367 | -58.2779 | -58.2458 | 0.073242 | -58.5159 | 64.856 | 64.7736 | -58.2733 | -58.3603 | -0.013733 | -0.054932 | 0.022889 | 0.036621 | -0.20599 | -0.15106 | -0.054931 | -0.050354 | -0.13733 | 0.018311 | -0.022889 | -0.29297 | -0.15564 | -0.064086 | 123.0835 | 123.0057 | 58.2047 | -123.1155 | 123.0789 | 122.9965 | 58.2962 | -123.1979
134.7031 | 123.2712 | -58.1726 | 64.7873 | -0.011739 | -0.014263 | 0.073105 | 0.010409 | 0.070487 | -0.0080629 | -0.00076433 | -0.11565 | -0.014388 | 0.057328 | 0.059485 | -0.0082519 | 0.002032 | 64.8605 | -58.0536 | 0.07782 | -58.3466 | 64.801 | -58.2367 | -58.2184 | -58.1131 | 0.15564 | -58.3969 | 64.8193 | 64.7461 | -58.2138 | -58.3237 | -0.064087 | -0.045777 | 0.013733 | 0.11902 | -0.17395 | -0.12817 | 0.073243 | -0.041199 | -0.15106 | 0.032044 | 0.059509 | -0.22431 | -0.073243 | -0.041198 | 122.9736 | 123.0331 | 58.2504 | -123.0057 | 122.9919 | 122.9187 | 58.3282 | -123.111
135.6406 | 123.1796 | -58.2001 | 64.8148 | -0.13381 | 0.010304 | 0.073105 | 0.0029318 | 0.070487 | 0.017572 | 0.0056447 | -0.28349 | 0.0016336 | 0.069078 | 0.06269 | 0.0077701 | -0.00010499 | 64.8285 | -58.1543 | -0.013733 | -58.3878 | 64.8422 | -58.2321 | -58.2825 | -58.1589 | 0.082397 | -58.461 | 64.8697 | 64.7507 | -58.2367 | -58.3511 | -0.032044 | -0.082398 | 0.027466 | 0.045776 | -0.18768 | -0.10529 | 0.013733 | -0.036621 | -0.15106 | 0.054932 | 0.041198 | -0.26093 | -0.10986 | -0.064087 | 123.0423 | 123.0286 | 58.1863 | -123.0972 | 123.0698 | 122.9507 | 58.2825 | -123.1659
136.7031 | 123.2529 | -58.2138 | 64.7736 | 0.27818 | -0.017467 | 0.076309 | -0.013089 | 0.073691 | -0.017676 | -0.011445 | -0.054612 | 0.00056556 | 0.049852 | 0.071235 | 0.0077701 | 0.006304 | 64.7552 | -57.9391 | 0.1236 | -58.4335 | 64.8148 | -58.2138 | -58.2504 | -58.1451 | 0.041199 | -58.4335 | 64.7873 | 64.7232 | -58.2596 | -58.3374 | 0 | -0.036621 | 0.041198 | 0.27466 | -0.21973 | -0.18311 | -0.018311 | -0.045777 | -0.1236 | 0.013732 | 0.068664 | -0.21973 | -0.096131 | -0.050354 | 123.0286 | 122.9691 | 58.3374 | -123.024 | 123.0011 | 122.937 | 58.255 | -123.111
137.6406 | 123.1522 | -58.2184 | 64.8102 | -0.16433 | -0.0035808 | 0.066696 | -0.00027224 | 0.061942 | 0.0015501 | -0.0039683 | -3.6557 | -0.0037074 | 0.07335 | 0.06269 | -0.010388 | -0.003309 | 64.7873 | -58.168 | -0.018311 | -58.429 | 64.8468 | -58.2367 | -58.287 | -58.168 | -0.036621 | -58.4793 | 64.8834 | 64.769 | -58.255 | -58.3603 | -0.01831 | -0.068664 | 0.036621 | 0.050354 | -0.21057 | -0.14191 | -0.022889 | -0.036621 | -0.14191 | 0.073242 | 0.050354 | -0.26093 | -0.11902 | -0.041199 | 123.0652 | 123.0057 | 58.2001 | -123.0972 | 123.1018 | 122.9874 | 58.1818 | -123.1705
138.7031 | 123.1979 | -58.1909 | 64.8239 | 0.36973 | -0.014263 | 0.079513 | 0.0039998 | 0.072623 | -0.028357 | -0.01999 | 0.4947 | -0.017592 | 0.048783 | 0.059485 | -0.0039789 | 0.004168 | 64.7964 | -58.1314 | -0.041199 | -58.4244 | 64.7644 | -58.2413 | -58.2642 | -58.1543 | 0.013733 | -58.4564 | 64.8285 | 64.7003 | -58.2687 | -58.342 | -0.050354 | -0.073242 | -0.05951 | 0.059509 | -0.23346 | -0.16022 | -0.027466 | -0.07782 | -0.15106 | 0.004577 | 0.036621 | -0.2655 | -0.11444 | -0.1236 | 122.9553 | 122.9874 | 58.1497 | -123.0881 | 123.0194 | 122.8912 | 58.2047 | -123.1659
139.6406 | 123.2391 | -58.2092 | 64.7278 | 0.58335 | 0.0017592 | 0.075241 | 0.014682 | 0.075827 | 0.0036861 | -0.0061053 | 0.92195 | -0.01332 | 0.046647 | 0.063758 | -0.0039789 | -0.009718 | 64.8697 | -58.1085 | 0.054932 | -58.5068 | 64.7095 | -58.2779 | -58.3145 | -58.0673 | 0.045776 | -58.4244 | 64.7736 | 64.7049 | -58.2367 | -58.3511 | -0.068664 | -0.10529 | -0.01831 | 0.10071 | -0.29755 | -0.19226 | 0.14191 | -0.027465 | -0.14191 | 0.045777 | 0.14191 | -0.21515 | -0.073242 | -0.022888 | 122.9187 | 123.0789 | 58.2642 | -123.0423 | 122.9828 | 122.9141 | 58.255 | -123.0789
140.7031 | 123.2941 | -58.1818 | 64.7141 | 0.35447 | 0.0028272 | 0.066696 | 0.0029318 | 0.060874 | 0.0058221 | 0.0013717 | 0.47945 | -0.0015704 | 0.072282 | 0.071235 | 0.0077701 | -0.009718 | 64.8743 | -58.1039 | -0.013733 | -58.4061 | 64.7415 | -58.2367 | -58.2825 | -58.0948 | 0.050354 | -58.4335 | 64.8193 | 64.7232 | -58.255 | -58.3328 | -0.054931 | -0.10071 | 0.027466 | 0.07782 | -0.2243 | -0.1236 | 0.16022 | -0.073242 | -0.15106 | 0.10529 | 0.086975 | -0.25177 | -0.10071 | 0.009156 | 122.9233 | 123.056 | 58.168 | -122.9965 | 123.0011 | 122.905 | 58.2321 | -123.0469
141.6406 | 123.2208 | -58.2092 | 64.8102 | -0.30166 | -0.0025128 | 0.060287 | 0.017886 | 0.061942 | -0.0016549 | 0.00030367 | -0.17668 | 0.0048376 | 0.058397 | 0.052009 | 0.0013611 | -0.007581 | 64.8834 | -58.0765 | 0.073242 | -58.3649 | 64.7873 | -58.2184 | -58.2367 | -58.1314 | 0.13275 | -58.4381 | 64.8514 | 64.7827 | -58.2413 | -58.342 | -0.009155 | -0.027465 | -0.022889 | 0.13275 | -0.15564 | -0.12817 | 0.073242 | -0.032043 | -0.13275 | 0.041198 | 0.07782 | -0.22888 | -0.09613 | -0.027466 | 122.9965 | 123.0927 | 58.2825 | -123.0469 | 123.0606 | 122.9919 | 58.342 | -123.1522
142.7031 | 123.2346 | -58.1955 | 64.7141 | 0.53758 | -0.015331 | 0.070968 | -0.0098852 | 0.060874 | -0.0037909 | -0.0061053 | 0.571 | -0.0079794 | 0.065873 | 0.06269 | 0.0045661 | -0.007581 | 64.856 | -58.0856 | -0.018311 | -58.3969 | 64.7827 | -58.255 | -58.287 | -58.0994 | 0.027466 | -58.4335 | 64.7827 | 64.7003 | -58.2687 | -58.3694 | -0.059509 | -0.091552 | 0.068665 | 0.10986 | -0.20142 | -0.10986 | 0.14191 | -0.073242 | -0.17395 | 0.068665 | 0.096131 | -0.23804 | -0.064087 | -0.013733 | 122.9782 | 123.0515 | 58.1772 | -123.0011 | 122.9782 | 122.8958 | 58.223 | -123.0835
143.6406 | 123.1705 | -58.2138 | 64.8285 | -0.25588 | -0.0035808 | 0.067764 | 0.0072048 | 0.072623 | -0.0016549 | -0.018922 | 0.18953 | 0.00056556 | 0.086168 | 0.073371 | -0.0029109 | -0.012922 | 64.9887 | -58.461 | -0.12817 | -58.4061 | 64.8468 | -58.2596 | -58.2733 | -58.1863 | 0.059509 | -58.4839 | 64.8834 | 64.7644 | -58.2642 | -58.3237 | -0.045777 | -0.059509 | 0.018311 | -0.24719 | -0.19226 | -0.13275 | 0.16022 | -0.050354 | -0.10986 | 0.054932 | 0.027466 | -0.27008 | -0.16022 | -0.064087 | 123.0606 | 123.2025 | 58.0856 | -123.1018 | 123.0972 | 122.9782 | 58.2733 | -123.1522
144.6406 | 123.2483 | -58.2275 | 64.7598 | 0.61387 | 0.016713 | 0.067764 | 0.0061368 | 0.070487 | 0.013299 | -0.0029003 | 0.46419 | -0.0047754 | 0.05626 | 0.06269 | 0.0056341 | -0.007581 | 64.7919 | -58.2275 | -0.13275 | -58.4518 | 64.7919 | -58.2733 | -58.3054 | -58.1589 | -0.045776 | -58.5114 | 64.8422 | 64.7232 | -58.2779 | -58.374 | -0.045776 | -0.07782 | 0.032043 | 0 | -0.2243 | -0.14648 | 0.032043 | -0.050354 | -0.14648 | 0.082397 | 0.068664 | -0.28381 | -0.13733 | -0.036621 | 123.0194 | 123.0194 | 58.0948 | -123.0652 | 123.0698 | 122.9507 | 58.1818 | -123.1338
145.6406 | 123.2346 | -58.1543 | 64.7919 | -0.22536 | -0.030284 | 0.068832 | 0.0082728 | 0.052329 | -0.0059269 | -0.012513 | -0.16142 | -0.012251 | 0.063737 | 0.059485 | 0.0024291 | -0.004377 | 64.8651 | -58.0353 | 0.086975 | -58.3557 | 64.7919 | -58.2184 | -58.255 | -58.1039 | 0.16479 | -58.4198 | 64.856 | 64.7598 | -58.2413 | -58.3191 | -0.064087 | -0.10071 | 0 | 0.11902 | -0.20142 | -0.10071 | 0.073242 | -0.086975 | -0.16479 | 0.064087 | 0.050354 | -0.2655 | -0.10071 | -0.032043 | 122.9462 | 123.0194 | 58.2413 | -123.0469 | 123.0103 | 122.9141 | 58.3191 | -123.111
146.6406 | 123.2574 | -58.1726 | 64.7781 | -0.2101 | -0.0099898 | 0.091263 | 0.0029318 | 0.059806 | -0.014472 | -0.0050373 | -2.4655 | -0.011183 | 0.062669 | 0.052009 | -0.0093199 | -0.01399 | 64.888 | -58.0032 | 0.10986 | -58.2047 | 64.8331 | -58.1909 | -58.2047 | -58.0994 | 0.20599 | -58.3694 | 64.8239 | 64.7186 | -58.2504 | -58.3328 | -0.018311 | -0.032044 | 0.054932 | 0.16937 | -0.032044 | 0 | 0.10986 | -0.07782 | -0.16022 | 0.045777 | 0.073242 | -0.19684 | -0.036621 | -0.059509 | 123.0057 | 123.0606 | 58.2825 | -122.9828 | 122.9965 | 122.8912 | 58.3786 | -123.111
147.6406 | 123.2986 | -58.1863 | 64.7324 | 0.14085 | -0.015331 | 0.065628 | -0.0077492 | 0.068351 | -0.012336 | -0.021058 | 0.082718 | -0.01866 | 0.057328 | 0.053077 | -0.00077485 | -0.021467 | 64.9246 | -58.0078 | 0.07782 | -58.3191 | 64.8102 | -58.1955 | -58.2458 | -57.8613 | -0.041199 | -58.5434 | 64.8148 | 64.7141 | -58.2458 | -58.3328 | -0.009156 | -0.05951 | 0.07782 | 0.17853 | -0.13275 | -0.073242 | 0.19226 | -0.05951 | -0.14648 | 0.082397 | 0.32501 | -0.35706 | -0.21057 | -0.018311 | 122.9965 | 123.111 | 58.2642 | -122.9782 | 123.0011 | 122.9004 | 58.1451 | -123.0652
148.6406 | 123.2803 | -58.1909 | 64.7827 | -0.92727 | -0.024944 | 0.073105 | -0.0045452 | 0.061942 | -0.0091309 | 0.0045757 | -0.085129 | -0.0058434 | 0.05626 | 0.058417 | 0.0045661 | -0.005445 | 64.8651 | -58.0124 | 0.09613 | -58.3603 | 64.801 | -58.2184 | -58.2367 | -58.0856 | 0.19226 | -58.374 | 64.8148 | 64.7278 | -58.2413 | -58.3237 | -0.027466 | -0.045776 | 0.01831 | 0.17853 | -0.16937 | -0.1236 | 0.082397 | -0.050354 | -0.13275 | 0.032043 | 0.10529 | -0.1831 | -0.050354 | -0.054932 | 122.9919 | 123.056 | 58.287 | -123.0194 | 123.0057 | 122.9187 | 58.3832 | -123.1064
149.6406 | 123.1338 | -58.255 | 64.7781 | 0.67491 | 0.042347 | 0.054947 | 0.012545 | 0.064078 | 0.029321 | 0.0013717 | -6.5396 | -0.0037074 | 0.062669 | 0.060554 | 0.0024291 | -0.006513 | 64.7461 | -58.2504 | -0.14648 | -58.4793 | 64.8148 | -58.2779 | -58.3191 | -58.2001 | -0.073242 | -58.5388 | 64.8605 | 64.7278 | -58.287 | -58.3923 | -0.022888 | -0.064087 | 0.036621 | 0.004578 | -0.2243 | -0.16022 | -0.032043 | -0.032043 | -0.13733 | 0.082398 | 0.054932 | -0.28381 | -0.14648 | -0.050354 | 123.0698 | 123.0011 | 58.1085 | -123.0972 | 123.1155 | 122.9828 | 58.1818 | -123.1705
150.7031 | 123.2483 | -58.2184 | 64.7369 | 0.65965 | 0.0049632 | 0.060287 | 0.00079576 | 0.065146 | 0.010095 | -0.0061053 | 0.46419 | -0.0047754 | 0.053056 | 0.069098 | -0.00077485 | 0.002032 | 64.7873 | -58.1772 | -0.10071 | -58.4473 | 64.7964 | -58.2779 | -58.2916 | -58.1268 | -0.004578 | -58.4747 | 64.8331 | 64.7049 | -58.2504 | -58.3694 | -0.059509 | -0.073242 | 0.05951 | 0.041199 | -0.22888 | -0.15564 | 0.050354 | -0.032043 | -0.15106 | 0.096131 | 0.091553 | -0.25635 | -0.10528 | -0.032043 | 123.0148 | 123.0057 | 58.1177 | -123.0286 | 123.0515 | 122.9233 | 58.2138 | -123.1064
151.6406 | 123.1842 | -58.2138 | 64.8102 | -0.22536 | -0.0025128 | 0.070968 | 0.010409 | 0.081168 | -0.00058594 | -0.0050373 | 0.52522 | -0.0047754 | 0.057328 | 0.060554 | 0.00029315 | -0.006513 | 64.7964 | -58.168 | -0.009155 | -58.429 | 64.8239 | -58.2413 | -58.2504 | -58.1589 | 0.032043 | -58.5114 | 64.8788 | 64.7781 | -58.2733 | -58.342 | -0.027466 | -0.036621 | 0.013733 | 0.045776 | -0.21515 | -0.17853 | -0.013733 | -0.059509 | -0.12817 | 0.068664 | 0.054931 | -0.29755 | -0.16937 | -0.032044 | 123.0377 | 123.0103 | 58.2047 | -123.0606 | 123.0927 | 122.9919 | 58.2458 | -123.1522
152.7031 | 123.2941 | -58.223 | 64.7461 | 0.58335 | 0.014576 | 0.068832 | 0.017886 | 0.068351 | 0.0047541 | 0.0024397 | 0.60152 | -0.0037074 | 0.053056 | 0.056281 | 0.0056341 | -0.001173 | 64.8193 | -58.1589 | -0.073242 | -58.4015 | 64.7552 | -58.2413 | -58.2962 | -58.1314 | 0.013733 | -58.4518 | 64.7873 | 64.6774 | -58.287 | -58.3603 | -0.018311 | -0.073243 | 0.009155 | 0.064086 | -0.17853 | -0.10528 | 0.073242 | -0.064087 | -0.13733 | 0.041198 | 0.091552 | -0.22888 | -0.091552 | -0.068665 | 122.9782 | 123.0423 | 58.1497 | -123.0423 | 123.0103 | 122.9004 | 58.2367 | -123.1064
153.6406 | 123.3307 | -58.168 | 64.7644 | 0.11033 | -0.019603 | 0.0699 | -0.0024082 | 0.054465 | -0.023017 | -0.012513 | 0.14375 | 0.0027016 | 0.058397 | 0.043464 | -0.013592 | 0.004168 | 64.8514 | -58.0673 | 0.032043 | -58.374 | 64.7873 | -58.2001 | -58.2596 | -58.0536 | 0.13733 | -58.3511 | 64.8193 | 64.7095 | -58.2275 | -58.3191 | -0.032043 | -0.091553 | 0.022888 | 0.10071 | -0.20599 | -0.11444 | 0.086975 | -0.059509 | -0.15106 | 0.054932 | 0.11444 | -0.1831 | -0.032043 | -0.054931 | 122.9553 | 123.0194 | 58.2001 | -123.024 | 122.9874 | 122.8775 | 58.3054 | -123.0835
154.7031 | 123.2071 | -58.1772 | 64.8331 | -0.27114 | -0.00037681 | 0.067764 | 0.0072048 | 0.06301 | -0.00058594 | -0.0082413 | -0.32927 | -0.00050244 | 0.042375 | 0.063758 | 0.0024291 | -0.010786 | 64.8056 | -58.1177 | 0.004578 | -58.4015 | 64.8376 | -58.2321 | -58.2825 | -58.1543 | 0.086975 | -58.4793 | 64.8651 | 64.7781 | -58.255 | -58.3328 | -0.054932 | -0.10529 | 0.004577 | 0.059509 | -0.2243 | -0.11902 | -0.027466 | -0.07782 | -0.15564 | 0.032043 | 0.022888 | -0.30212 | -0.14648 | -0.054932 | 123.0148 | 122.9828 | 58.1818 | -123.1155 | 123.0423 | 122.9553 | 58.2642 | -123.1659
155.6406 | 123.2483 | -58.1863 | 64.769 | 0.18663 | -0.026012 | 0.08165 | -0.0024082 | 0.070487 | -0.011268 | -0.01999 | 0.0522 | -0.017592 | 0.048783 | 0.06269 | -0.018933 | -0.002241 | 64.9063 | -58.0078 | 0.07782 | -58.3466 | 64.7873 | -58.1863 | -58.2596 | -58.1223 | -0.091553 | -58.3099 | 64.8331 | 64.7186 | -58.2367 | -58.3191 | 0 | -0.073243 | 0.01831 | 0.17853 | -0.16022 | -0.086975 | 0.13733 | -0.050354 | -0.13275 | 0.064087 | 0.064087 | -0.1236 | 0.009155 | -0.050354 | 122.9736 | 123.0927 | 58.2642 | -123.0286 | 123.0194 | 122.905 | 58.0948 | -123.0881
156.6406 | 123.262 | -58.168 | 64.7827 | 0.3087 | -0.018535 | 0.083786 | 0.00079576 | 0.069419 | 0.0015501 | -0.013582 | -0.039353 | -0.010115 | 0.043443 | 0.02851 | 0.0024291 | -0.00865 | 64.8788 | -58.0353 | 0.082397 | -58.3557 | 64.7827 | -58.223 | -58.2596 | -58.0811 | 0.17395 | -58.3786 | 64.8331 | 64.7049 | -58.255 | -58.3099 | -0.054931 | -0.091553 | 0 | 0.13275 | -0.18768 | -0.09613 | 0.09613 | -0.086975 | -0.14191 | 0.050354 | 0.086975 | -0.21057 | -0.068664 | -0.07782 | 122.9507 | 123.0469 | 58.2504 | -123.0423 | 123.0011 | 122.8729 | 58.342 | -123.0927
157.7031 | 123.1522 | -58.2458 | 64.7781 | 0.41551 | 0.022053 | 0.070968 | 0.017886 | 0.066214 | 0.016503 | -0.013582 | 0.32686 | 0.0048376 | 0.054124 | 0.074439 | 0.010974 | -0.003309 | 64.7598 | -58.2047 | -0.13275 | -58.4702 | 64.8148 | -58.2733 | -58.3008 | -58.1863 | -0.073242 | -58.5205 | 64.8376 | 64.7003 | -58.2779 | -58.3878 | -0.027465 | -0.054931 | 0.036621 | 0.041199 | -0.2243 | -0.16937 | -0.01831 | -0.032043 | -0.14191 | 0.059509 | 0.05951 | -0.27466 | -0.13275 | -0.07782 | 123.0606 | 123.0057 | 58.1131 | -123.0789 | 123.0835 | 122.9462 | 58.1726 | -123.1659
158.6406 | 123.2574 | -58.168 | 64.7736 | -0.072774 | -0.019603 | 0.061355 | 0.0082728 | 0.068351 | -0.016608 | -0.031739 | 0.26582 | -0.0090474 | 0.041307 | 0.076575 | -0.0050469 | -0.001173 | 65.2176 | -58.2779 | -0.15106 | -58.3923 | 64.769 | -58.2413 | -58.255 | -58.0811 | 0.19684 | -58.3694 | 64.8056 | 64.7186 | -58.2184 | -58.3145 | -0.073242 | -0.086975 | -0.004578 | -0.10986 | -0.2243 | -0.13733 | 0.44403 | -0.050354 | -0.14648 | 0.032043 | 0.086975 | -0.20142 | -0.054932 | -0.054932 | 122.937 | 123.3856 | 58.017 | -123.0286 | 122.9736 | 122.8867 | 58.3649 | -123.0881
159.7031 | 123.1705 | -58.2413 | 64.7873 | -0.5458 | 0.040211 | 0.060287 | 0.018954 | 0.069419 | 0.014367 | -0.0071733 | 0.29634 | -0.00050244 | 0.060533 | 0.064826 | 0.0077701 | -0.003309 | 64.7827 | -58.2275 | -0.14191 | -58.4747 | 64.8331 | -58.287 | -58.3008 | -58.1909 | -0.068665 | -58.5388 | 64.8376 | 64.7232 | -58.2779 | -58.3557 | -0.045776 | -0.059509 | 0.045777 | 0.013733 | -0.23346 | -0.17395 | -0.004577 | -0.036621 | -0.11444 | 0.050354 | 0.050354 | -0.29755 | -0.1831 | -0.064086 | 123.0743 | 123.024 | 58.0994 | -123.0881 | 123.0789 | 122.9645 | 58.1726 | -123.143
160.6406 | 123.2941 | -58.1818 | 64.7507 | 0.079814 | -0.02708 | 0.079513 | -0.0034762 | 0.061942 | -0.027289 | -0.0071733 | 0.26582 | -0.0079794 | 0.05626 | 0.056281 | -0.0018429 | -0.003309 | 64.8239 | -58.0811 | 0.027466 | -58.3878 | 64.7827 | -58.223 | -58.2596 | -58.0948 | 0.14191 | -58.3878 | 64.8239 | 64.7186 | -58.2642 | -58.3328 | -0.041198 | -0.07782 | 0.032044 | 0.10071 | -0.20599 | -0.12817 | 0.073243 | -0.082397 | -0.15106 | 0.073243 | 0.086975 | -0.20599 | -0.054931 | -0.032043 | 122.9645 | 123.0057 | 58.2092 | -123.0103 | 123.0057 | 122.9004 | 58.3237 | -123.0835
161.7031 | 123.2895 | -58.2001 | 64.7278 | 0.58335 | 0.019917 | 0.060287 | 0.0072048 | 0.076896 | 0.012231 | 0.0024397 | 0.64729 | -0.0047754 | 0.059465 | 0.052009 | 0.0024291 | -0.004377 | 64.8422 | -58.0948 | -0.036621 | -58.3786 | 64.7507 | -58.2733 | -58.2642 | -58.0948 | 0.050354 | -58.4335 | 64.7461 | 64.6591 | -58.2642 | -58.3557 | -0.073242 | -0.064087 | 0.022888 | 0.10529 | -0.17853 | -0.11444 | 0.11444 | -0.064087 | -0.15564 | 0.018311 | 0.10529 | -0.23346 | -0.07782 | -0.068664 | 122.9507 | 123.0423 | 58.1635 | -122.9919 | 122.9462 | 122.8592 | 58.2504 | -123.0835
162.6406 | 123.2529 | -58.168 | 64.7964 | -1.8733 | -0.018535 | 0.067764 | 0.0061368 | 0.061942 | -0.0059269 | -0.0039683 | -0.22246 | -0.0037074 | 0.05092 | 0.061622 | -0.0029109 | 0.00096301 | 64.8102 | -58.017 | 0.091553 | -58.3557 | 64.7781 | -58.223 | -58.2596 | -58.0811 | 0.19684 | -58.374 | 64.7964 | 64.7369 | -58.2047 | -58.3328 | -0.054931 | -0.091553 | -0.018311 | 0.15106 | -0.18768 | -0.09613 | 0.013733 | -0.036621 | -0.16479 | 0 | 0.086975 | -0.20599 | -0.041198 | -0.05951 | 122.9462 | 122.9782 | 58.2596 | -123.056 | 122.9645 | 122.905 | 58.3649 | -123.1293
163.7031 | 123.175 | -58.223 | 64.7598 | 0.55284 | 0.035939 | 0.066696 | -0.0088172 | 0.065146 | 0.013299 | -0.0061053 | 0.47945 | 0.0059056 | 0.060533 | 0.065894 | 0.019519 | -0.009718 | 64.7781 | -58.2092 | -0.11902 | -58.4656 | 64.8148 | -58.2779 | -58.3008 | -58.1543 | -0.041199 | -58.5114 | 64.8102 | 64.7095 | -58.2779 | -58.342 | -0.054932 | -0.07782 | 0.054931 | 0.013732 | -0.24262 | -0.16479 | 0.01831 | -0.054932 | -0.11902 | 0.050354 | 0.068664 | -0.28839 | -0.16937 | -0.050354 | 123.0377 | 123.0011 | 58.1039 | -123.0606 | 123.0331 | 122.9324 | 58.1818 | -123.1018
164.6406 | 123.2803 | -58.1635 | 64.7827 | -0.19484 | -0.022808 | 0.067764 | -0.00027224 | 0.071555 | -0.0037909 | -0.0071733 | -0.66496 | -0.0047754 | 0.061601 | 0.060554 | 0.00029315 | 0.00096301 | 65.1672 | -58.0215 | -0.036621 | -58.4702 | 64.7964 | -58.1955 | -58.2413 | -58.0994 | 0.20142 | -58.374 | 64.8193 | 64.7415 | -58.223 | -58.3191 | -0.032044 | -0.07782 | 0.013733 | 0.14191 | -0.3067 | -0.22888 | 0.38452 | -0.059509 | -0.15564 | 0.036621 | 0.064087 | -0.21057 | -0.054931 | -0.041199 | 122.9599 | 123.3307 | 58.1268 | -123.024 | 122.9828 | 122.905 | 58.3649 | -123.1018
165.7031 | 123.2666 | -58.1863 | 64.7552 | 0.55284 | 0.00069119 | 0.054947 | -0.0045452 | 0.065146 | -0.0091309 | -0.0050373 | 0.571 | -0.0058434 | 0.054124 | 0.059485 | 0.0013611 | -0.002241 | 64.8468 | -58.0948 | -0.027466 | -58.4015 | 64.7552 | -58.2413 | -58.2687 | -58.0994 | 0.036621 | -58.4427 | 64.7964 | 64.6866 | -58.2687 | -58.3603 | -0.054932 | -0.082398 | 0 | 0.091552 | -0.21515 | -0.13275 | 0.091553 | -0.082398 | -0.17395 | 0.041199 | 0.086975 | -0.25635 | -0.082397 | -0.068665 | 122.9416 | 123.0331 | 58.1589 | -123.024 | 122.9828 | 122.8729 | 58.223 | -123.1155
166.6406 | 123.2574 | -58.1726 | 64.769 | -0.17959 | -0.023876 | 0.073105 | 0.0082728 | 0.066214 | -0.0091309 | -0.012513 | -3.4878 | 0.0048376 | 0.060533 | 0.06803 | -0.018933 | -0.00865 | 64.8972 | -58.0215 | 0.091553 | -58.3557 | 64.7873 | -58.2047 | -58.2642 | -58.1085 | 0.11902 | -58.3557 | 64.8148 | 64.7278 | -58.255 | -58.3328 | -0.032044 | -0.091553 | 0.01831 | 0.15106 | -0.18311 | -0.091553 | 0.12817 | -0.082398 | -0.16022 | 0.045776 | 0.064086 | -0.18311 | -0.022888 | -0.041199 | 122.9599 | 123.0698 | 58.2642 | -123.0331 | 122.9874 | 122.9004 | 58.2916 | -123.1018
167.7031 | 123.23 | -58.1863 | 64.7141 | 0.3087 | 0.037007 | 0.083786 | -0.0045452 | 0.054465 | 0.0026181 | -0.0082413 | 0.55574 | -0.011183 | 0.071214 | 0.059485 | 0.010974 | 0.00844 | 64.8514 | -58.0765 | -0.027466 | -58.4152 | 64.7461 | -58.2092 | -58.2779 | -58.1131 | 0.045776 | -58.429 | 64.8056 | 64.6957 | -58.2504 | -58.3557 | -0.022889 | -0.091553 | 0.032044 | 0.10986 | -0.22888 | -0.13733 | 0.13733 | -0.064087 | -0.16937 | 0.091553 | 0.073242 | -0.24262 | -0.073242 | -0.01831 | 122.9324 | 123.0377 | 58.1589 | -122.9919 | 122.9919 | 122.8821 | 58.2321 | -123.0698
168.6406 | 123.3215 | -58.1726 | 64.7644 | 0.11033 | -0.019603 | 0.078445 | 0.0039998 | 0.074759 | -0.018744 | 0.0013717 | 0.17427 | -0.010115 | 0.057328 | 0.071235 | 0.0056341 | 0.002032 | 64.8788 | -58.0627 | 0.045776 | -58.3786 | 64.7873 | -58.2184 | -58.2458 | -58.0719 | 0.14648 | -58.3786 | 64.8148 | 64.7278 | -58.2184 | -58.3237 | -0.045777 | -0.073243 | 0.022888 | 0.10986 | -0.20599 | -0.13275 | 0.11444 | -0.045777 | -0.15106 | 0.050354 | 0.10071 | -0.20599 | -0.054932 | -0.036621 | 122.9599 | 123.0515 | 58.2184 | -123.0103 | 122.9874 | 122.9004 | 58.3191 | -123.0881
169.7031 | 123.2712 | -58.2092 | 64.7507 | 0.61387 | 0.013508 | 0.074173 | 0.024295 | 0.071555 | 0.021844 | -0.0029003 | 0.44893 | -0.0037074 | 0.066941 | 0.06803 | 0.0067021 | -0.017194 | 64.8102 | -58.1589 | -0.086975 | -58.429 | 64.7919 | -58.2642 | -58.3191 | -58.0994 | 0.018311 | -58.4564 | 64.801 | 64.6912 | -58.2779 | -58.3557 | -0.054931 | -0.10986 | 0.041199 | 0.050354 | -0.21973 | -0.10986 | 0.05951 | -0.068664 | -0.14648 | 0.050354 | 0.10986 | -0.24719 | -0.10071 | -0.059509 | 123.0011 | 123.0194 | 58.1223 | -123.0698 | 123.0103 | 122.9004 | 58.2275 | -123.1064
170.6406 | 123.2574 | -58.1909 | 64.7964 | -0.40847 | -0.018535 | 0.077377 | -0.0045452 | 0.074759 | -0.0091309 | -0.011445 | -0.25298 | -0.010115 | 0.041307 | 0.056281 | -0.0039789 | -0.001173 | 64.8514 | -58.0353 | 0.082397 | -58.3511 | 64.7964 | -58.2092 | -58.2779 | -58.1131 | 0.17395 | -58.4106 | 64.8468 | 64.7369 | -58.2642 | -58.3282 | -0.018311 | -0.086975 | 0 | 0.15564 | -0.16022 | -0.073242 | 0.054931 | -0.073242 | -0.13733 | 0.050354 | 0.07782 | -0.21973 | -0.082398 | -0.05951 | 122.9874 | 123.0423 | 58.2733 | -123.0743 | 123.0377 | 122.9279 | 58.3649 | -123.1247
171.7031 | 123.2346 | -58.1955 | 64.7415 | 0.76646 | -0.014263 | 0.077377 | -0.00027224 | 0.069419 | 0.0026181 | -0.013582 | 0.50996 | -0.016524 | 0.058397 | 0.048804 | 0.0056341 | 0.007372 | 64.8376 | -58.0902 | 0 | -58.4061 | 64.7781 | -58.2275 | -58.287 | -58.0994 | 0.050354 | -58.4244 | 64.7964 | 64.6683 | -58.2413 | -58.374 | -0.032043 | -0.091552 | 0.036621 | 0.10529 | -0.21057 | -0.11902 | 0.09613 | -0.045776 | -0.17853 | 0.054932 | 0.096131 | -0.22888 | -0.050354 | -0.073242 | 122.9736 | 123.0331 | 58.1955 | -123.0286 | 122.9919 | 122.8638 | 58.2458 | -123.1155
172.6406 | 123.23 | -58.168 | 64.8193 | -0.24062 | -0.0089218 | 0.073105 | 0.0029318 | 0.074759 | -0.0091309 | 0.0024397 | -0.16142 | -0.019728 | 0.043443 | 0.060554 | -0.0029109 | -0.00865 | 64.8651 | -58.0307 | 0.082397 | -58.3649 | 64.7827 | -58.2275 | -58.255 | -58.0948 | 0.17395 | -58.3969 | 64.8468 | 64.7415 | -58.2504 | -58.3282 | -0.059509 | -0.086975 | -0.036621 | 0.13733 | -0.19684 | -0.10986 | 0.045776 | -0.082397 | -0.16022 | 0.027466 | 0.073242 | -0.22888 | -0.068665 | -0.07782 | 122.9507 | 123.0331 | 58.2504 | -123.0743 | 123.0148 | 122.9095 | 58.342 | -123.1476
173.7031 | 123.2941 | -58.1863 | 64.7278 | 0.56809 | 0.020985 | 0.059219 | 0.026431 | 0.069419 | 0.013299 | 0.00030367 | 0.40315 | -0.0015704 | 0.072282 | 0.058417 | -0.0061159 | -0.002241 | 64.8056 | -58.1635 | -0.091553 | -58.429 | 64.7964 | -58.2962 | -58.3054 | -58.1268 | 0 | -58.4702 | 64.7964 | 64.6774 | -58.2825 | -58.3282 | -0.10986 | -0.11902 | 0.068665 | 0.022888 | -0.24262 | -0.1236 | 0.07782 | -0.096131 | -0.14191 | 0.068665 | 0.059509 | -0.28381 | -0.14191 | -0.050354 | 122.9828 | 122.9919 | 58.0948 | -123.0331 | 122.9828 | 122.8638 | 58.1863 | -123.056
174.6406 | 123.317 | -58.168 | 64.769 | 0.24766 | -0.015331 | 0.068832 | 0.0072048 | 0.060874 | -0.014472 | -0.0039683 | -0.14616 | -0.0090474 | 0.045579 | 0.06269 | -0.012524 | -0.005445 | 64.9155 | -58.0032 | 0.082397 | -58.3374 | 64.7964 | -58.2001 | -58.2504 | -58.0673 | 0.18768 | -58.3786 | 64.8193 | 64.7461 | -58.2275 | -58.3099 | -0.032043 | -0.082397 | 0.027466 | 0.1648 | -0.16937 | -0.086975 | 0.14648 | -0.059509 | -0.14191 | 0.050354 | 0.10071 | -0.21057 | -0.068664 | -0.022888 | 122.9645 | 123.0835 | 58.2504 | -123.0194 | 122.9874 | 122.9141 | 58.3557 | -123.0789
175.6406 | 123.3124 | -58.136 | 64.8331 | -0.13381 | -0.018535 | 0.080581 | -0.00027224 | 0.068351 | -0.0059269 | -0.0082413 | -0.10039 | -0.0058434 | 0.060533 | 0.056281 | -0.0029109 | -0.003309 | 64.9155 | -57.9895 | 0.11444 | -58.3282 | 64.8102 | -58.1955 | -58.2687 | -58.0673 | 0.1831 | -58.3511 | 64.8331 | 64.7141 | -58.2321 | -58.2962 | -0.05951 | -0.13275 | -0.022888 | 0.14648 | -0.19226 | -0.059509 | 0.082397 | -0.096131 | -0.16022 | 0 | 0.068664 | -0.21515 | -0.054931 | -0.11902 | 122.9462 | 123.0515 | 58.2504 | -123.1018 | 122.9691 | 122.85 | 58.3191 | -123.1293
176.7031 | 123.2758 | -58.1863 | 64.7324 | 0.58335 | -0.0035808 | 0.073105 | 0.027499 | 0.073691 | 0.0090271 | -0.0029003 | 0.35738 | -0.0058434 | 0.046647 | 0.069098 | 0.0067021 | -0.010786 | 64.8239 | -58.0582 | 0 | -58.4106 | 64.7369 | -58.2458 | -58.2687 | -58.0902 | 0.045776 | -58.4335 | 64.8056 | 64.682 | -58.2779 | -58.3511 | -0.05951 | -0.082398 | 0.004577 | 0.12817 | -0.22431 | -0.14191 | 0.091553 | -0.091553 | -0.16479 | 0.073242 | 0.09613 | -0.24719 | -0.082398 | -0.050354 | 122.9233 | 123.0103 | 58.1863 | -123.0011 | 122.9919 | 122.8683 | 58.2321 | -123.0835
177.6406 | 123.1796 | -58.2047 | 64.7781 | -0.19484 | 0.0071002 | 0.06456 | 0.0039998 | 0.064078 | 0.020776 | 0.0013717 | -0.10039 | 0.0027016 | 0.060533 | 0.069098 | 0.0034971 | -0.010786 | 64.856 | -58.1268 | -0.004578 | -58.3923 | 64.8514 | -58.2642 | -58.2916 | -58.1314 | 0.10529 | -58.4656 | 64.8331 | 64.7415 | -58.223 | -58.3374 | -0.059509 | -0.086975 | 0.073242 | 0.07782 | -0.18768 | -0.10071 | 0.07782 | -0.01831 | -0.13275 | 0.054932 | 0.073242 | -0.26093 | -0.12817 | -0.036621 | 123.056 | 123.0606 | 58.2001 | -123.0698 | 123.0377 | 122.9462 | 58.3099 | -123.1155
178.7031 | 123.2529 | -58.2001 | 64.7324 | 0.55284 | -0.013195 | 0.0699 | -0.016294 | 0.066214 | -0.012336 | 0.00030367 | 0.64729 | -0.0047754 | 0.05626 | 0.064826 | -0.0071839 | -0.003309 | 64.8239 | -58.0902 | -0.022888 | -58.3878 | 64.7369 | -58.2504 | -58.2962 | -58.1131 | 0.027466 | -58.4564 | 64.7781 | 64.7095 | -58.255 | -58.3603 | -0.050354 | -0.096131 | 0.004577 | 0.10986 | -0.18768 | -0.091552 | 0.091553 | -0.054932 | -0.16022 | 0.045776 | 0.086975 | -0.25635 | -0.09613 | -0.022888 | 122.937 | 123.024 | 58.1772 | -123.0286 | 122.9782 | 122.9095 | 58.2275 | -123.0927
179.6406 | 123.175 | -58.2138 | 64.8056 | -0.057515 | 0.0081682 | 0.080581 | 0.0029318 | 0.054465 | -0.0069949 | -0.010377 | -0.35979 | -0.00050244 | 0.05626 | 0.069098 | -0.0093199 | -0.00865 | 64.7781 | -58.1223 | -0.009155 | -58.429 | 64.8376 | -58.223 | -58.2779 | -58.1589 | 0.068665 | -58.4747 | 64.8743 | 64.769 | -58.2596 | -58.3328 | -0.009155 | -0.064087 | 0.032043 | 0.091553 | -0.21515 | -0.15106 | -0.027466 | -0.045777 | -0.11902 | 0.068665 | 0.054931 | -0.26093 | -0.14191 | -0.036621 | 123.0515 | 122.9919 | 58.2047 | -123.0835 | 123.0881 | 122.9828 | 58.2825 | -123.1384
180.7031 | 123.3124 | -58.2092 | 64.7095 | 0.56809 | 0.011372 | 0.066696 | 0.017886 | 0.064078 | 0.00048206 | -0.0050373 | 0.55574 | -0.0058434 | 0.053056 | 0.057349 | 0.0013611 | -0.005445 | 64.8651 | -58.1085 | -0.018311 | -58.3832 | 64.7461 | -58.2275 | -58.2687 | -58.0627 | -0.21973 | -58.4381 | 64.7507 | 64.6912 | -58.2504 | -58.3557 | -0.01831 | -0.059509 | 0.036621 | 0.10071 | -0.17395 | -0.11444 | 0.15564 | -0.041198 | -0.14648 | 0.041198 | 0.14648 | -0.22888 | -0.082397 | -0.018311 | 122.9553 | 123.0743 | 58.1909 | -122.9782 | 122.9599 | 122.9004 | 57.9895 | -123.0652
181.6406 | 123.317 | -58.1635 | 64.7507 | -0.13381 | -0.023876 | 0.067764 | 0.012545 | 0.060874 | -0.024085 | -0.0061053 | -0.085129 | -0.010115 | 0.048783 | 0.06269 | -0.0029109 | -0.006513 | 64.888 | -58.0215 | 0.10529 | -58.3511 | 64.7964 | -58.2138 | -58.2458 | -58.0673 | 0.18768 | -58.1314 | 64.8651 | 64.801 | -58.2138 | -58.3145 | -0.050354 | -0.082398 | 0.045777 | 0.14191 | -0.18768 | -0.10529 | 0.13733 | -0.050354 | -0.15106 | 0.11444 | 0.09613 | 0.032043 | 0.18311 | 0.050354 | 122.9599 | 123.0515 | 58.2687 | -122.9965 | 123.0286 | 122.9645 | 58.3511 | -123.0652
182.7031 | 123.2712 | -58.1955 | 64.7278 | -3.3534 | -0.0067858 | 0.073105 | -0.0013402 | 0.074759 | 0.013299 | -0.0039683 | 0.32686 | 0.0048376 | 0.060533 | 0.053077 | 0.0013611 | -0.002241 | 64.8239 | -58.049 | 0.009155 | -58.3923 | 64.7736 | -58.223 | -58.2687 | -58.1131 | 0.041199 | -58.4152 | 64.7873 | 64.7003 | -58.287 | -58.3466 | -0.027465 | -0.073242 | 0.045777 | 0.14648 | -0.19684 | -0.1236 | 0.096131 | -0.091552 | -0.15106 | 0.059509 | 0.082398 | -0.21973 | -0.068664 | -0.027466 | 122.9691 | 123.0194 | 58.2047 | -122.9965 | 122.9828 | 122.8958 | 58.2367 | -123.0743
183.6406 | 123.2346 | -58.1909 | 64.7736 | -5.4439 | -0.026012 | 0.061355 | 0.0039998 | 0.070487 | -0.0080629 | -0.0018323 | -0.39031 | -0.010115 | 0.046647 | 0.064826 | 0.00029315 | -0.015058 | 64.7644 | -57.9895 | 0.11444 | -58.3878 | 64.7964 | -58.2321 | -58.2596 | -58.0811 | 0.17395 | -58.3832 | 64.8376 | 64.7415 | -58.255 | -58.3237 | -0.041199 | -0.068665 | 0.022888 | 0.20142 | -0.19684 | -0.12817 | -0.009156 | -0.064087 | -0.13275 | 0.064086 | 0.10986 | -0.19226 | -0.05951 | -0.032044 | 122.9874 | 122.9553 | 58.3054 | -123.0331 | 123.0286 | 122.9324 | 58.3649 | -123.0972
184.7031 | 123.1979 | -58.2047 | 64.7461 | 0.44602 | -0.0078538 | 0.057083 | -0.0013402 | 0.055533 | -0.010199 | -0.013582 | 0.26582 | -0.0079794 | 0.049852 | 0.050941 | -0.0018429 | 0.006304 | 64.8056 | -58.1268 | -0.045776 | -58.4198 | 64.7919 | -58.2275 | -58.2596 | -58.1406 | 0.022888 | -58.4427 | 64.8102 | 64.7095 | -58.2916 | -58.3557 | -0.022888 | -0.054932 | 0.045776 | 0.07782 | -0.21515 | -0.16022 | 0.059509 | -0.086975 | -0.15106 | 0.064087 | 0.064087 | -0.23804 | -0.086975 | -0.036621 | 122.9965 | 123.0103 | 58.1589 | -123.0057 | 123.0148 | 122.9141 | 58.2275 | -123.1018
185.6406 | 123.2025 | -58.1955 | 64.8376 | -0.25588 | -0.0078538 | 0.066696 | 0.0061368 | 0.065146 | 0.0015501 | -0.00076433 | -0.23772 | -0.0079794 | 0.03917 | 0.055213 | -0.0050469 | -0.005445 | 64.856 | -58.0582 | 0.059509 | -58.3603 | 64.8148 | -58.2321 | -58.2596 | -58.1314 | 0.13733 | -58.4381 | 64.8285 | 64.7644 | -58.2825 | -58.3511 | -0.036621 | -0.064087 | -0.022888 | 0.13733 | -0.16479 | -0.10071 | 0.018311 | -0.086975 | -0.15564 | -0.009155 | 0.064087 | -0.24261 | -0.086975 | -0.073242 | 123.0103 | 123.0515 | 58.255 | -123.0972 | 123.024 | 122.9599 | 58.3328 | -123.1888
186.7031 | 123.2529 | -58.2092 | 64.769 | 0.43077 | 0.015645 | 0.079513 | 0.010409 | 0.061942 | -0.011268 | 0.00030367 | 0.26582 | -0.016524 | 0.047715 | 0.050941 | 0.0024291 | -0.004377 | 64.8056 | -58.1314 | -0.045776 | -58.4335 | 64.7781 | -58.2458 | -58.2916 | -58.1314 | 0.032043 | -58.4518 | 64.801 | 64.7003 | -58.2504 | -58.3466 | -0.036621 | -0.082397 | 0.009155 | 0.07782 | -0.2243 | -0.14191 | 0.036621 | -0.041198 | -0.13733 | 0.032043 | 0.07782 | -0.24261 | -0.10528 | -0.068665 | 122.9874 | 123.0148 | 58.1635 | -123.0606 | 123.0103 | 122.9095 | 58.2413 | -123.1155
187.6406 | 123.1796 | -58.1909 | 64.7873 | 0.049296 | 0.043416 | 0.074173 | 0.020022 | 0.072623 | 0.026116 | -0.0093093 | 0.95247 | 0.0037696 | 0.05626 | 0.054145 | 0.018451 | -0.016126 | 64.8651 | -58.1131 | -0.004578 | -58.4015 | 64.8422 | -58.2367 | -58.3054 | -58.1497 | 0.064087 | -58.4793 | 64.8331 | 64.7415 | -58.2825 | -58.342 | -0.045776 | -0.11444 | 0.054932 | 0.07782 | -0.21057 | -0.09613 | 0.07782 | -0.091553 | -0.15106 | 0.045777 | 0.041199 | -0.28839 | -0.13733 | -0.045776 | 123.0331 | 123.056 | 58.1863 | -123.0927 | 123.024 | 122.9324 | 58.255 | -123.1293
188.7031 | 123.2529 | -58.2001 | 64.7507 | 0.62913 | -0.0035808 | 0.06456 | 0.022158 | 0.058738 | 0.014367 | -0.00076433 | 0.41841 | -0.0090474 | 0.064805 | 0.06803 | 0.0034971 | -0.002241 | 64.7873 | -58.1863 | -0.091553 | -58.4518 | 64.7781 | -58.2687 | -58.2962 | -58.1406 | -0.013733 | -58.4747 | 64.8193 | 64.7003 | -58.2825 | -58.3557 | -0.068665 | -0.096131 | 0.027466 | 0.013733 | -0.25177 | -0.15564 | 0.036621 | -0.082398 | -0.15564 | 0.068665 | 0.059509 | -0.27466 | -0.11902 | -0.050354 | 122.9782 | 122.9874 | 58.1085 | -123.0469 | 123.0194 | 122.9004 | 58.1863 | -123.1064
189.6406 | 123.2391 | -58.1726 | 64.7873 | -0.17959 | -0.020671 | 0.078445 | -0.0077492 | 0.06301 | -0.023017 | -0.011445 | 0.097976 | -0.010115 | 0.049852 | 0.066962 | -0.00077485 | -0.006513 | 64.8605 | -58.0902 | 0.10986 | -58.3466 | 64.7873 | -58.2047 | -58.2642 | -58.0856 | 0.16937 | -58.3878 | 64.8148 | 64.7736 | -58.2092 | -58.3282 | -0.032044 | -0.091553 | 0 | 0.082397 | -0.17395 | -0.082398 | 0.073243 | -0.036622 | -0.15564 | 0.027466 | 0.086975 | -0.21515 | -0.059509 | -0.013732 | 122.9599 | 123.0331 | 58.2825 | -123.0515 | 122.9874 | 122.9462 | 58.342 | -123.1155
190.7031 | 123.2162 | -58.2001 | 64.7415 | 0.41551 | -0.0099898 | 0.065628 | -0.0098852 | 0.069419 | -0.019813 | -0.0029003 | 0.67781 | -0.011183 | 0.051988 | 0.06269 | 0.0056341 | 0.002032 | 64.8331 | -58.0856 | -0.013733 | -58.4061 | 64.7552 | -58.2413 | -58.2733 | -58.1131 | 0.036621 | -58.4518 | 64.7919 | 64.7003 | -58.2733 | -58.3466 | -0.041199 | -0.073242 | 0.013733 | 0.11444 | -0.20599 | -0.13275 | 0.091553 | -0.073242 | -0.14648 | 0.050354 | 0.086975 | -0.25177 | -0.10528 | -0.041199 | 122.9553 | 123.0331 | 58.1863 | -123.0148 | 122.9919 | 122.9004 | 58.2367 | -123.0881
191.6406 | 123.2254 | -58.1863 | 64.8148 | -0.2101 | 0.010304 | 0.063492 | 0.010409 | 0.06301 | -0.0048589 | -0.0071733 | -0.23772 | -0.010115 | 0.061601 | 0.06269 | 0.0024291 | -0.003309 | 64.8514 | -58.0582 | 0.068665 | -58.3511 | 64.8331 | -58.223 | -58.2504 | -58.1177 | 0.14648 | -58.4152 | 64.8651 | 64.7552 | -58.2504 | -58.3374 | -0.036621 | -0.064087 | 0.018311 | 0.12817 | -0.16479 | -0.10071 | 0.036621 | -0.064087 | -0.15106 | 0.050354 | 0.068664 | -0.22888 | -0.07782 | -0.059509 | 123.0194 | 123.0377 | 58.255 | -123.0652 | 123.0515 | 122.9416 | 58.3328 | -123.1522
192.7031 | 123.2529 | -58.2001 | 64.7598 | 0.33921 | -0.028148 | 0.080581 | 0.00079576 | 0.061942 | -0.013404 | -0.00076433 | 0.67781 | -0.0026384 | 0.044511 | 0.056281 | 0.00029315 | 0.006304 | 64.801 | -58.1177 | -0.027466 | -58.4106 | 64.7873 | -58.2275 | -58.255 | -58.1406 | 0.054932 | -58.429 | 64.7964 | 64.7049 | -58.2596 | -58.3374 | -0.027466 | -0.054932 | 0.027465 | 0.082397 | -0.21057 | -0.15564 | 0.041198 | -0.05951 | -0.13733 | 0.036621 | 0.059509 | -0.22888 | -0.091553 | -0.054932 | 122.9874 | 123.0011 | 58.1726 | -123.0148 | 122.9965 | 122.905 | 58.255 | -123.0972
193.6406 | 123.1384 | -58.2001 | 64.8285 | -0.24062 | -0.011058 | 0.065628 | 0.0082728 | 0.065146 | 0.0026181 | -0.011445 | -0.14616 | -0.010115 | 0.055192 | 0.06269 | 0.0045661 | -0.007581 | 64.8376 | -58.0948 | 0.032043 | -58.3786 | 64.8285 | -58.2184 | -58.287 | -58.1314 | 0.11902 | -58.4839 | 64.8834 | 64.7781 | -58.2458 | -58.3466 | -0.018311 | -0.086975 | 0 | 0.10529 | -0.17853 | -0.091553 | 0.009155 | -0.045777 | -0.14648 | 0.054932 | 0.068664 | -0.28381 | -0.13733 | -0.050354 | 123.0286 | 123.0377 | 58.2321 | -123.1155 | 123.0835 | 122.9782 | 58.3191 | -123.175
194.7031 | 123.2208 | -58.2138 | 64.7644 | 0.55284 | 0.016713 | 0.068832 | 0.01575 | 0.068351 | 0.014367 | -0.0029003 | 0.47945 | -0.0069114 | 0.066941 | 0.064826 | -0.0018429 | -0.009718 | 64.7827 | -58.1909 | -0.10071 | -58.4518 | 64.8056 | -58.2504 | -58.3099 | -58.1589 | -0.036621 | -58.5022 | 64.8376 | 64.7141 | -58.2916 | -58.3649 | -0.036621 | -0.096131 | 0.041199 | 0.022888 | -0.23804 | -0.14191 | 0.018311 | -0.07782 | -0.15106 | 0.073242 | 0.054931 | -0.28839 | -0.13733 | -0.050354 | 123.0194 | 122.9965 | 58.1131 | -123.0743 | 123.0515 | 122.9279 | 58.1772 | -123.1293
195.6406 | 123.2758 | -58.1772 | 64.7919 | -0.16433 | -0.024944 | 0.080581 | 0.0093408 | 0.069419 | -0.018744 | -0.016786 | -0.66496 | -0.0069114 | 0.058397 | 0.057349 | -0.0018429 | -0.009718 | 65.1215 | -57.9895 | -0.018311 | -58.4702 | 64.7919 | -58.2321 | -58.2458 | -58.0994 | 0.21057 | -58.374 | 64.8102 | 64.7415 | -58.2092 | -58.3282 | -0.054932 | -0.068665 | 0 | 0.18768 | -0.29297 | -0.2243 | 0.32959 | -0.032044 | -0.15106 | 0.018311 | 0.07782 | -0.19684 | -0.045776 | -0.050354 | 122.9691 | 123.2986 | 58.1589 | -123.0377 | 122.9874 | 122.9187 | 58.3878 | -123.1201
196.7031 | 123.1796 | -58.2367 | 64.7644 | 1.4684 | 0.010304 | 0.077377 | 0.011477 | 0.067282 | 0.016503 | 0.0056447 | 0.34212 | 0.0091106 | 0.074418 | 0.064826 | 0.0013611 | -0.023603 | 64.7827 | -58.2092 | -0.12817 | -58.4564 | 64.8102 | -58.2733 | -58.2962 | -58.1726 | -0.054932 | -58.5068 | 64.8468 | 64.7141 | -58.3054 | -58.3878 | -0.036621 | -0.05951 | 0.045777 | 0.027465 | -0.21973 | -0.16022 | 0.018311 | -0.068665 | -0.15106 | 0.082398 | 0.064087 | -0.27008 | -0.11902 | -0.050354 | 123.0469 | 123.0194 | 58.1085 | -123.0606 | 123.0835 | 122.9507 | 58.1818 | -123.1522
197.6562 | 123.23 | -58.2138 | 64.7278 | 0.58335 | -0.00037681 | 0.06456 | -0.0066812 | 0.066214 | 0.0090271 | -0.0029003 | 0.44893 | 0.0027016 | 0.060533 | 0.06803 | 0.0045661 | -0.005445 | 64.8056 | -58.1726 | -0.091553 | -58.4381 | 64.7827 | -58.2321 | -58.2825 | -58.1223 | 0.013733 | -58.4656 | 64.7827 | 64.7141 | -58.2733 | -58.342 | -0.018311 | -0.068665 | 0.054932 | 0.041199 | -0.2243 | -0.15564 | 0.07782 | -0.059509 | -0.12817 | 0.054932 | 0.091553 | -0.25177 | -0.1236 | -0.013733 | 122.9965 | 123.0194 | 58.1223 | -123.0103 | 122.9965 | 122.9279 | 58.2275 | -123.0698
198.7031 | 123.2803 | -58.2001 | 64.7095 | 0.27818 | 0.011372 | 0.065628 | 0.00079576 | 0.053397 | 0.0047541 | -0.0018323 | 0.60152 | -0.0037074 | 0.055192 | 0.052009 | 0.0024291 | 0.002032 | 64.8376 | -58.1177 | -0.032043 | -58.3878 | 64.7461 | -58.2367 | -58.2825 | -58.0948 | 0.036621 | -58.4198 | 64.7781 | 64.6912 | -58.255 | -58.3466 | -0.036621 | -0.082398 | 0.036621 | 0.082397 | -0.18768 | -0.10529 | 0.12817 | -0.054932 | -0.14648 | 0.068664 | 0.10529 | -0.21973 | -0.073242 | -0.018311 | 122.9462 | 123.0377 | 58.168 | -122.9919 | 122.9782 | 122.8912 | 58.2367 | -123.056
199.6406 | 123.2437 | -58.1589 | 64.7415 | -0.24062 | -0.0035808 | 0.079513 | 0.0018638 | 0.065146 | -0.010199 | -0.0071733 | -0.92436 | 0.00056556 | 0.043443 | 0.056281 | -0.0029109 | -0.003309 | 64.7552 | -57.724 | 0.27008 | -58.5388 | 64.7964 | -58.1955 | -58.2458 | -58.0673 | 0.16022 | -58.3511 | 64.7827 | 64.7598 | -58.2001 | -58.2916 | -0.036621 | -0.086975 | 0.054932 | 0.43488 | -0.37994 | -0.29297 | 0.013733 | -0.041198 | -0.13275 | 0.041199 | 0.091553 | -0.19226 | -0.059509 | 0.018311 | 122.9553 | 122.9141 | 58.429 | -122.9874 | 122.9416 | 122.9187 | 58.3191 | -123.0331
200.7031 | 123.2574 | -58.2047 | 64.7507 | 0.65965 | -0.015331 | 0.074173 | -0.0066812 | 0.066214 | 0.0047541 | -0.012513 | 0.50996 | -0.0058434 | 0.060533 | 0.06269 | -0.00077485 | -0.001173 | 64.856 | -58.0902 | -0.032043 | -58.4015 | 64.7736 | -58.223 | -58.2779 | -58.1039 | 0.050354 | -58.429 | 64.7781 | 64.6774 | -58.255 | -58.3649 | -0.01831 | -0.073242 | 0.022889 | 0.11444 | -0.19684 | -0.1236 | 0.10529 | -0.050354 | -0.16022 | 0.027466 | 0.10071 | -0.2243 | -0.064087 | -0.073242 | 122.9782 | 123.0606 | 58.1726 | -123.0286 | 122.9828 | 122.8821 | 58.255 | -123.1155
201.6406 | 123.1522 | -58.1543 | 64.7736 | 0.049296 | 0.0071002 | 0.067764 | 0.012545 | 0.054465 | -0.010199 | -0.0039683 | -0.11565 | -0.0069114 | 0.05626 | 0.059485 | -0.011456 | -0.011854 | 64.9155 | -57.9987 | 0.07782 | -58.3466 | 64.8102 | -58.2092 | -58.255 | -58.0627 | 0.18768 | -58.3511 | 64.801 | 64.7369 | -58.2367 | -58.3099 | -0.054932 | -0.10071 | 0.036621 | 0.15564 | -0.19226 | -0.091553 | 0.14191 | -0.082397 | -0.15564 | 0.027465 | 0.091553 | -0.19684 | -0.041198 | -0.036622 | 122.9645 | 123.0698 | 58.2321 | -123.0286 | 122.9553 | 122.8912 | 58.342 | -123.0835
202.7188 | 123.1934 | -58.2047 | 64.7964 | 0.095073 | 0.018849 | 0.070968 | 0.011477 | 0.064078 | 0.020776 | -0.0061053 | 0.14375 | -0.0058434 | 0.075486 | 0.054145 | 0.0077701 | -0.019331 | 64.9612 | -58.429 | -0.13733 | -58.3832 | 64.801 | -58.2596 | -58.3008 | -58.1406 | 0.045776 | -58.4656 | 64.8331 | 64.7461 | -58.2733 | -58.3694 | -0.054932 | -0.09613 | 0.004577 | -0.2243 | -0.17853 | -0.082398 | 0.16479 | -0.068664 | -0.1648 | 0.036621 | 0.064087 | -0.26093 | -0.09613 | -0.050354 | 123.0057 | 123.1659 | 58.0673 | -123.0972 | 123.0377 | 122.9507 | 58.2504 | -123.1659
203.6406 | 123.2025 | -58.1635 | 64.801 | -0.33217 | -0.015331 | 0.083786 | -0.012021 | 0.075827 | -0.0048589 | 0.00030367 | -0.2072 | -0.015456 | 0.055192 | 0.053077 | -0.0039789 | -0.007581 | 64.8422 | -58.0811 | 0.068665 | -58.342 | 64.8239 | -58.1955 | -58.2413 | -58.1406 | 0.13275 | -58.4198 | 64.8422 | 64.7552 | -58.2642 | -58.3237 | -0.032044 | -0.07782 | 0.022889 | 0.082397 | -0.17853 | -0.10071 | 0.041199 | -0.10071 | -0.16022 | 0.041199 | 0.022888 | -0.25635 | -0.096131 | -0.045776 | 122.9874 | 123.0057 | 58.2321 | -123.0423 | 123.0057 | 122.9187 | 58.2962 | -123.1247
204.7031 | 123.2437 | -58.1772 | 64.7324 | 0.40025 | -0.011058 | 0.072037 | -0.0034762 | 0.060874 | -0.011268 | -0.0050373 | 0.571 | -0.0090474 | 0.066941 | 0.055213 | -0.0050469 | -0.003309 | 64.8193 | -58.0902 | -0.013733 | -58.4015 | 64.7186 | -58.2642 | -58.2687 | -58.0948 | 0.036621 | -58.4152 | 64.7873 | 64.682 | -58.2779 | -58.342 | -0.086975 | -0.091553 | -0.013733 | 0.086975 | -0.2243 | -0.13275 | 0.086975 | -0.10071 | -0.16479 | 0.054931 | 0.082397 | -0.23804 | -0.073242 | -0.050354 | 122.8958 | 122.9965 | 58.1635 | -123.0011 | 122.9645 | 122.8592 | 58.2138 | -123.0743
205.6406 | 123.1659 | -58.2047 | 64.8102 | -0.27114 | 0.022053 | 0.073105 | 0.023226 | 0.071555 | -0.0069949 | -0.0071733 | -0.17668 | -0.0047754 | 0.060533 | 0.069098 | 0.0024291 | -0.010786 | 64.8239 | -58.0948 | 0.036621 | -58.3786 | 64.8422 | -58.2413 | -58.2779 | -58.1772 | 0.073242 | -58.4473 | 64.8788 | 64.7781 | -58.2367 | -58.3466 | -0.036621 | -0.073242 | 0.032043 | 0.10986 | -0.17395 | -0.10071 | 0.013733 | -0.032043 | -0.14191 | 0.068664 | 0.027466 | -0.24262 | -0.10071 | -0.032044 | 123.0469 | 123.0286 | 58.2413 | -123.0881 | 123.0835 | 122.9828 | 58.2779 | -123.1567
206.7031 | 123.1247 | -58.2504 | 64.801 | -0.34743 | 0.0017592 | 0.063492 | 0.013613 | 0.06301 | -0.0069949 | 0.0013717 | -0.29875 | -0.0026384 | 0.060533 | 0.082984 | 0.0056341 | 0.00844 | 64.7873 | -58.1772 | -0.009155 | -58.4198 | 64.8468 | -58.2367 | -58.3099 | -58.1589 | 0.022888 | -58.5251 | 64.888 | 64.7644 | -58.2916 | -58.3557 | 0.013733 | -0.05951 | 0.045777 | 0.073242 | -0.16937 | -0.10986 | -0.013733 | -0.041199 | -0.10529 | 0.086975 | 0.091552 | -0.27466 | -0.16937 | -0.036621 | 123.0972 | 123.0377 | 58.2413 | -123.111 | 123.1384 | 123.0148 | 58.2733 | -123.1567
207.6562 | 123.2117 | -58.168 | 64.801 | -1.1104 | -0.024944 | 0.070968 | -0.017362 | 0.060874 | -0.014472 | -0.012513 | -0.17668 | -0.01332 | 0.038102 | 0.054145 | -0.0061159 | -0.00865 | 64.801 | -58.0078 | 0.10071 | -58.342 | 64.7781 | -58.2047 | -58.2413 | -58.1039 | 0.17395 | -58.3878 | 64.8193 | 64.7415 | -58.2458 | -58.3328 | -0.036621 | -0.073242 | -0.022888 | 0.16022 | -0.17395 | -0.10071 | 0 | -0.07782 | -0.16479 | 0.018311 | 0.064087 | -0.21973 | -0.054931 | -0.059509 | 122.9462 | 122.9691 | 58.2687 | -123.0423 | 122.9874 | 122.9095 | 58.342 | -123.1338
208.7031 | 123.1293 | -58.2367 | 64.7186 | 0.98008 | 0.02953 | 0.068832 | 0.020022 | 0.067282 | 0.028253 | 0.0035077 | 0.32686 | 0.0048376 | 0.072282 | 0.050941 | 0.0099061 | -0.006513 | 64.7324 | -58.2504 | -0.14648 | -58.461 | 64.8102 | -58.2642 | -58.3099 | -58.2047 | -0.059509 | -58.5388 | 64.8331 | 64.7186 | -58.2916 | -58.3878 | -0.027466 | -0.073243 | 0.091553 | -0.013733 | -0.22431 | -0.15106 | 0.013733 | -0.054932 | -0.15106 | 0.11444 | 0.032043 | -0.30212 | -0.15106 | 0 | 123.0469 | 122.9691 | 58.0902 | -123.0286 | 123.0698 | 122.9553 | 58.1772 | -123.1064
209.6406 | 123.2483 | -58.1772 | 64.8102 | -0.22536 | 0.00069119 | 0.070968 | 0.00079576 | 0.053397 | -0.0091309 | -0.010377 | -0.19194 | -0.016524 | 0.057328 | 0.047736 | 0.0013611 | -0.00865 | 64.8422 | -58.0399 | 0.07782 | -58.3557 | 64.7919 | -58.2413 | -58.2321 | -58.0902 | 0.1831 | -58.3923 | 64.8514 | 64.7736 | -58.2367 | -58.3466 | -0.064087 | -0.054932 | -0.018311 | 0.13733 | -0.17853 | -0.1236 | 0.032043 | -0.059509 | -0.16937 | 0.041198 | 0.086975 | -0.21515 | -0.045776 | -0.036621 | 122.9691 | 123.0194 | 58.255 | -123.0423 | 123.0286 | 122.9507 | 58.3603 | -123.1567
210.7031 | 123.2071 | -58.2367 | 64.769 | 0.47654 | 0.01244 | 0.073105 | 0.025363 | 0.073691 | 0.011163 | -0.0029003 | 0.4947 | -0.011183 | 0.058397 | 0.065894 | 0.01311 | -0.00865 | 64.7873 | -58.1726 | -0.10529 | -58.4473 | 64.7964 | -58.2413 | -58.3282 | -58.168 | -0.022888 | -58.4793 | 64.8376 | 64.682 | -58.2825 | -58.3649 | -0.004578 | -0.091553 | 0.027466 | 0.064087 | -0.21057 | -0.11902 | 0.01831 | -0.045777 | -0.12817 | 0.068664 | 0.068664 | -0.24262 | -0.11444 | -0.086975 | 123.0331 | 123.024 | 58.1314 | -123.0972 | 123.0743 | 122.9187 | 58.2138 | -123.1338
211.6406 | 123.1659 | -58.2001 | 64.8056 | -0.95778 | -0.0046498 | 0.06456 | 0.016818 | 0.064078 | 0.0068901 | -0.0018323 | -0.23772 | -0.0058434 | 0.065873 | 0.061622 | 0.0056341 | -0.017194 | 64.7461 | -58.168 | 0 | -58.4152 | 64.8331 | -58.2367 | -58.3145 | -58.1909 | 0.059509 | -58.4793 | 64.8788 | 64.7964 | -58.2733 | -58.3466 | -0.036621 | -0.11444 | 0.027466 | 0.032043 | -0.21515 | -0.10071 | -0.059509 | -0.073242 | -0.14648 | 0.073242 | 0.009155 | -0.27924 | -0.13275 | -0.009155 | 123.0331 | 122.9462 | 58.2001 | -123.1201 | 123.0789 | 122.9965 | 58.2596 | -123.1522
212.7188 | 123.2208 | -58.2184 | 64.7644 | 0.55284 | 0.014576 | 0.061355 | 0.0039998 | 0.070487 | 0.017572 | 0.0013717 | 0.46419 | -0.0058434 | 0.05626 | 0.063758 | -0.0029109 | 0.004168 | 64.7736 | -58.1818 | -0.1236 | -58.4473 | 64.801 | -58.2596 | -58.3191 | -58.1543 | -0.036621 | -58.4747 | 64.801 | 64.7278 | -58.2962 | -58.3694 | -0.041199 | -0.10071 | 0.036621 | 0.036621 | -0.22888 | -0.12817 | 0.009156 | -0.07782 | -0.15106 | 0.036621 | 0.064087 | -0.25635 | -0.10528 | -0.036621 | 123.0194 | 122.9919 | 58.0948 | -123.0835 | 123.0194 | 122.9462 | 58.1818 | -123.1338
213.6406 | 123.1934 | -58.168 | 64.801 | -0.042256 | -0.0025128 | 0.05281 | 0.020022 | 0.066214 | -0.023017 | -0.0093093 | -0.16142 | -0.0058434 | 0.054124 | 0.056281 | -0.0018429 | -0.00010499 | 64.8468 | -58.0444 | 0.068665 | -58.342 | 64.8056 | -58.1955 | -58.2321 | -58.1131 | 0.17853 | -58.4015 | 64.8331 | 64.7415 | -58.255 | -58.3191 | -0.027466 | -0.064087 | 0.004578 | 0.1236 | -0.17395 | -0.10986 | 0.045777 | -0.086975 | -0.15106 | 0.032044 | 0.054932 | -0.23346 | -0.082397 | -0.059509 | 122.9736 | 123.0148 | 58.2367 | -123.0331 | 123.0011 | 122.9095 | 58.3466 | -123.1201
214.7031 | 123.262 | -58.2001 | 64.7232 | 2.2771 | 0.017781 | 0.068832 | 0.0029318 | 0.064078 | -0.010199 | -0.01465 | 0.60152 | -0.012251 | 0.065873 | 0.046668 | 0.0013611 | -0.00865 | 64.8605 | -58.0948 | -0.018311 | -58.3786 | 64.7736 | -58.2367 | -58.2642 | -58.1039 | 0.059509 | -58.4106 | 64.7781 | 64.682 | -58.2687 | -58.342 | -0.036621 | -0.064087 | 0.050354 | 0.10529 | -0.17853 | -0.11444 | 0.13733 | -0.068665 | -0.14191 | 0.054931 | 0.09613 | -0.21057 | -0.068665 | -0.041199 | 122.9736 | 123.0606 | 58.1818 | -122.9874 | 122.9782 | 122.8821 | 58.2596 | -123.0652
215.6406 | 123.1705 | -58.2092 | 64.8148 | -0.89675 | 0.0028272 | 0.061355 | 0.0093408 | 0.06301 | 0.0058221 | 0.00030367 | -0.35979 | -0.0026384 | 0.063737 | 0.063758 | 0.0034971 | -0.007581 | 64.7873 | -58.1497 | -0.041199 | -58.4244 | 64.8376 | -58.2687 | -58.2916 | -58.1772 | 0.064087 | -58.4793 | 64.8788 | 64.7873 | -58.255 | -58.3603 | -0.059509 | -0.082397 | 0.022888 | 0.05951 | -0.21515 | -0.13275 | -0.027466 | -0.045776 | -0.15106 | 0.064087 | 0.032044 | -0.27008 | -0.11902 | -0.027466 | 123.0469 | 122.9965 | 58.168 | -123.1064 | 123.0881 | 122.9965 | 58.2733 | -123.175
216.7031 | 123.2483 | -58.2138 | 64.7964 | 0.35447 | 0.015645 | 0.056015 | 0.025363 | 0.069419 | 0.019708 | -0.010377 | 0.2353 | -0.0037074 | 0.046647 | 0.06269 | 0.0013611 | -0.017194 | 64.7324 | -58.2367 | -0.13733 | -58.4518 | 64.8285 | -58.2733 | -58.3328 | -58.1589 | -0.46234 | -58.6533 | 64.801 | 64.7141 | -58.3008 | -58.3466 | -0.059509 | -0.11902 | 0.032043 | -0.022888 | -0.23804 | -0.11902 | -0.064087 | -0.086975 | -0.13275 | 0.004577 | 0.054931 | -0.43945 | -0.3067 | -0.082398 | 123.0423 | 122.9462 | 58.0765 | -123.1293 | 123.0148 | 122.9279 | 57.7515 | -123.143
217.6562 | 123.2437 | -58.1635 | 64.7461 | 0.2324 | -0.014263 | 0.076309 | 0.010409 | 0.065146 | -0.016608 | -0.013582 | 0.26582 | -0.016524 | 0.057328 | 0.0456 | -0.013592 | 0.006304 | 64.7964 | -58.0902 | 0.013733 | -58.3878 | 64.7873 | -58.2184 | -58.287 | -58.0994 | 0.10986 | -58.4061 | 64.8239 | 64.7278 | -58.2275 | -58.3145 | -0.054932 | -0.1236 | 0.041198 | 0.073242 | -0.2243 | -0.10071 | 0.050354 | -0.064087 | -0.15106 | 0.07782 | 0.064087 | -0.24262 | -0.091553 | -0.018311 | 122.9507 | 122.9599 | 58.1772 | -123.0331 | 122.9874 | 122.8912 | 58.2733 | -123.0606
218.7031 | 123.262 | -58.2001 | 64.7598 | 1.5294 | 0.011372 | 0.074173 | 0.0082728 | 0.066214 | -0.0091309 | -0.0039683 | 0.54048 | -0.015456 | 0.053056 | 0.065894 | 0.0013611 | -0.009718 | 64.8651 | -58.1085 | -0.022888 | -58.3878 | 64.7507 | -58.2367 | -58.2733 | -58.1039 | 0.054932 | -58.4244 | 64.769 | 64.7003 | -58.2504 | -58.3466 | -0.036621 | -0.073242 | -0.009156 | 0.091552 | -0.18768 | -0.11444 | 0.10528 | -0.050354 | -0.14648 | 0.009155 | 0.09613 | -0.2243 | -0.077819 | -0.05951 | 122.9507 | 123.0652 | 58.1772 | -123.0331 | 122.9691 | 122.9004 | 58.255 | -123.1064
219.6406 | 123.1842 | -58.1863 | 64.7964 | -0.27114 | 0.018849 | 0.061355 | 0.026431 | 0.058738 | 0.011163 | 0.00030367 | -0.25298 | -0.0047754 | 0.058397 | 0.064826 | 0.0099061 | -0.007581 | 64.8102 | -58.1863 | -0.036621 | -58.4244 | 64.856 | -58.2504 | -58.287 | -58.168 | 0.064087 | -58.4885 | 64.8605 | 64.7873 | -58.2413 | -58.3237 | -0.064087 | -0.10071 | 0.059509 | 0 | -0.23804 | -0.13733 | 0.013733 | -0.054932 | -0.13733 | 0.064087 | 0.01831 | -0.30212 | -0.16479 | -0.009156 | 123.0423 | 122.9965 | 58.1497 | -123.0835 | 123.0469 | 122.9736 | 58.2504 | -123.1201
220.7031 | 123.2574 | -58.2047 | 64.7186 | 0.67491 | 0.0092362 | 0.067764 | 0.01575 | 0.056601 | 0.0090271 | -0.00076433 | 0.47945 | -0.0079794 | 0.071214 | 0.052009 | -0.0029109 | -0.004377 | 64.8331 | -58.1314 | -0.050354 | -58.4015 | 64.7827 | -58.2504 | -58.287 | -58.1223 | 0.027466 | -58.4473 | 64.7827 | 64.6729 | -58.2779 | -58.3374 | -0.045776 | -0.082397 | 0.064087 | 0.073242 | -0.19684 | -0.11444 | 0.11444 | -0.073242 | -0.13275 | 0.064087 | 0.082398 | -0.24262 | -0.10986 | -0.045776 | 122.9874 | 123.0377 | 58.1543 | -123.0057 | 122.9874 | 122.8775 | 58.2321 | -123.056
221.6406 | 123.2025 | -58.1818 | 64.7827 | -0.13381 | -0.011058 | 0.067764 | 0.0072048 | 0.060874 | -0.0091309 | -0.0050373 | -0.024094 | -0.010115 | 0.064805 | 0.06269 | -0.011456 | -0.00010499 | 64.8697 | -58.0444 | 0.064087 | -58.342 | 64.801 | -58.1909 | -58.2642 | -58.1039 | 0.15106 | -58.4152 | 64.8056 | 64.7827 | -58.2275 | -58.3191 | -0.009155 | -0.082397 | 0.01831 | 0.13733 | -0.16022 | -0.07782 | 0.086975 | -0.045776 | -0.13733 | 0.022888 | 0.07782 | -0.23346 | -0.09613 | 0 | 122.9828 | 123.0515 | 58.2458 | -123.0469 | 122.9874 | 122.9645 | 58.3328 | -123.1018
222.7188 | 123.175 | -58.2275 | 64.7324 | 1.0106 | 0.032734 | 0.060287 | 0.013613 | 0.055533 | 0.013299 | 0.0056447 | 0.46419 | -0.0079794 | 0.062669 | 0.070167 | 0.0024291 | -0.005445 | 64.769 | -58.2001 | -0.11902 | -58.4564 | 64.8102 | -58.2504 | -58.3099 | -58.1635 | -0.050354 | -58.5251 | 64.8331 | 64.7186 | -58.3054 | -58.374 | -0.022888 | -0.082398 | 0.07782 | 0.027466 | -0.22888 | -0.14648 | 0.036621 | -0.07782 | -0.14648 | 0.10071 | 0.064087 | -0.29755 | -0.15106 | -0.013733 | 123.0377 | 122.9965 | 58.1085 | -123.0423 | 123.0606 | 122.9462 | 58.1772 | -123.1064
223.6406 | 123.1842 | -58.2001 | 64.8239 | -0.25588 | -0.013195 | 0.057083 | 0.02109 | 0.069419 | -0.0048589 | 0.00030367 | -0.17668 | -0.0058434 | 0.057328 | 0.059485 | 0.0013611 | -0.009718 | 64.8102 | -58.0719 | 0.041199 | -58.3786 | 64.8102 | -58.2047 | -58.255 | -58.1635 | 0.11902 | -58.4518 | 64.8697 | 64.8056 | -58.2733 | -58.3328 | -0.004578 | -0.054932 | -0.013733 | 0.12817 | -0.17853 | -0.1236 | -0.013733 | -0.073242 | -0.13275 | 0.045776 | 0.036621 | -0.25177 | -0.11902 | -0.018311 | 123.0103 | 123.0103 | 58.2413 | -123.0789 | 123.0698 | 123.0057 | 58.3191 | -123.1567
224.7031 | 123.1018 | -58.2275 | 64.7919 | 0.11033 | 0.0081682 | 0.053879 | 0.014682 | 0.054465 | 0.020776 | -0.0039683 | 0.11323 | 0.00056556 | 0.065873 | 0.056281 | 0.01311 | -0.016126 | 64.7598 | -58.1955 | -0.09613 | -58.4656 | 64.8193 | -58.255 | -58.3008 | -58.2504 | -0.059509 | -58.5709 | 64.8422 | 64.7415 | -58.287 | -58.3969 | -0.027466 | -0.073242 | 0.027466 | 0.032043 | -0.23804 | -0.16479 | -0.032043 | -0.059509 | -0.16937 | 0.050354 | -0.022888 | -0.34332 | -0.17395 | -0.050354 | 123.0469 | 122.9874 | 58.1314 | -123.0927 | 123.0698 | 122.9691 | 58.168 | -123.1888
225.6406 | 123.1979 | -58.2138 | 64.8056 | 0.018779 | 0.010304 | 0.058151 | 0.02109 | 0.068351 | 0.011163 | 0.00030367 | 0.021682 | -0.0047754 | 0.064805 | 0.053077 | 0.0067021 | -0.011854 | 64.8193 | -58.1085 | -0.004578 | -58.3878 | 64.8193 | -58.2733 | -58.2916 | -58.1223 | 0.073242 | -58.461 | 64.8376 | 64.7507 | -58.287 | -58.3832 | -0.059509 | -0.07782 | 0.013733 | 0.10528 | -0.17395 | -0.09613 | 0.013733 | -0.073242 | -0.16937 | 0.032043 | 0.091553 | -0.24719 | -0.07782 | -0.054932 | 123.0331 | 123.0331 | 58.2092 | -123.0972 | 123.0515 | 122.9645 | 58.287 | -123.1888
226.7031 | 123.1842 | -58.2504 | 64.7919 | 0.21714 | 0.015645 | 0.054947 | 0.0072048 | 0.065146 | 0.0026181 | -0.0039683 | 0.14375 | -0.00050244 | 0.085099 | 0.063758 | 0.0077701 | -0.009718 | 64.7598 | -58.1818 | -0.07782 | -58.4335 | 64.8239 | -58.2367 | -58.2962 | -58.2047 | -0.027466 | -58.5251 | 64.8239 | 64.769 | -58.2825 | -58.3694 | 0.013733 | -0.045777 | 0.032044 | 0.068664 | -0.18311 | -0.13733 | -0.032043 | -0.032044 | -0.11902 | 0.032044 | 0.045776 | -0.27466 | -0.15564 | -0.022888 | 123.0743 | 123.0103 | 58.1726 | -123.0881 | 123.0743 | 123.0194 | 58.223 | -123.1613
227.6406 | 123.143 | -58.223 | 64.8056 | 0.27818 | 0.023121 | 0.067764 | 0.029635 | 0.069419 | 0.016503 | 0.0035077 | 0.14375 | -0.0037074 | 0.063737 | 0.059485 | 0.0045661 | -0.006513 | 64.7736 | -58.168 | -0.068665 | -58.429 | 64.801 | -58.2504 | -58.3008 | -58.2001 | -0.009155 | -58.5114 | 64.8376 | 64.7507 | -58.287 | -58.3878 | -0.027466 | -0.07782 | -0.004578 | 0.054931 | -0.20599 | -0.12817 | -0.032043 | -0.064087 | -0.1648 | 0.032043 | 0.022888 | -0.28839 | -0.1236 | -0.054932 | 123.024 | 122.9965 | 58.1543 | -123.1064 | 123.0606 | 122.9736 | 58.2138 | -123.1934
228.7031 | 123.1293 | -58.2504 | 64.769 | 0.47654 | 0.034871 | 0.053879 | 0.050997 | 0.066214 | 0.0090271 | 0.0088487 | 0.32686 | 0.0016336 | 0.087236 | 0.072303 | 0.0088381 | 0.0031 | 64.7369 | -58.1635 | -0.12817 | -58.4747 | 64.8148 | -58.255 | -58.3054 | -58.2001 | -0.064087 | -58.5159 | 64.8468 | 64.769 | -58.3054 | -58.3923 | -0.004578 | -0.054932 | 0.045776 | 0.086975 | -0.2243 | -0.16937 | -0.032044 | -0.054932 | -0.14191 | 0.07782 | 0.050354 | -0.2655 | -0.1236 | 0 | 123.0652 | 122.9874 | 58.1223 | -123.0743 | 123.0972 | 123.0194 | 58.1863 | -123.1613
229.6406 | 123.2483 | -58.1589 | 64.7827 | -0.45424 | -0.018535 | 0.066696 | -0.0034762 | 0.067282 | -0.035834 | -0.010377 | -0.054612 | -0.015456 | 0.043443 | 0.057349 | -0.0082519 | 0.00844 | 64.8468 | -57.9849 | 0.09613 | -58.3282 | 64.7919 | -58.1909 | -58.2825 | -58.0811 | 0.19226 | -58.342 | 64.801 | 64.7598 | -58.2138 | -58.3008 | -0.032043 | -0.1236 | 0.009155 | 0.17395 | -0.16937 | -0.045776 | 0.064087 | -0.054931 | -0.14191 | 0.01831 | 0.07782 | -0.1831 | -0.041199 | -0.022888 | 122.9507 | 123.0057 | 58.255 | -123.0652 | 122.9599 | 122.9187 | 58.3511 | -123.0835
230.7031 | 123.262 | -58.1955 | 64.7644 | -0.39321 | -0.012126 | 0.068832 | 0.0093408 | 0.053397 | -0.026221 | -0.015718 | 0.47945 | -0.014388 | 0.046647 | 0.055213 | -0.011456 | -0.00010499 | 64.7507 | -58.1314 | -0.032043 | -58.4198 | 64.7919 | -58.2596 | -58.2825 | -58.1406 | 0.082397 | -58.4152 | 64.8056 | 64.7232 | -58.2825 | -58.3557 | -0.064087 | -0.086975 | 0.027466 | 0.064087 | -0.2243 | -0.13733 | -0.013733 | -0.086975 | -0.16022 | 0.041199 | 0.054932 | -0.21973 | -0.059509 | -0.041198 | 122.9874 | 122.9462 | 58.1635 | -123.0469 | 123.0011 | 122.9187 | 58.2779 | -123.1201
231.6406 | 123.1613 | -58.1909 | 64.7964 | -0.19484 | 0.0092362 | 0.073105 | 0.011477 | 0.060874 | -0.0048589 | -0.01999 | -0.14616 | -0.0069114 | 0.053056 | 0.055213 | 0.0024291 | -0.006513 | 64.8148 | -58.0582 | 0.064087 | -58.3649 | 64.8056 | -58.2001 | -58.2596 | -58.1314 | 0.12817 | -58.4244 | 64.8651 | 64.7644 | -58.2458 | -58.3282 | -0.009155 | -0.068665 | 0.009155 | 0.13275 | -0.17395 | -0.10529 | 0.01831 | -0.054932 | -0.13733 | 0.068664 | 0.059509 | -0.23346 | -0.09613 | -0.032044 | 122.9965 | 123.0057 | 58.255 | -123.056 | 123.056 | 122.9553 | 58.3191 | -123.1247
232.7031 | 123.262 | -58.1909 | 64.7781 | 0.049296 | -0.020671 | 0.080581 | 0.00079576 | 0.068351 | -0.012336 | -0.0050373 | 0.036941 | -0.011183 | 0.063737 | 0.044532 | -0.0018429 | 0.006304 | 64.8834 | -57.9803 | 0.082397 | -58.3374 | 64.8102 | -58.2001 | -58.2687 | -58.0719 | 0.1831 | -58.3557 | 64.8148 | 64.7278 | -58.255 | -58.342 | -0.009155 | -0.07782 | 0.032044 | 0.21057 | -0.14648 | -0.068664 | 0.10529 | -0.064087 | -0.15106 | 0.036621 | 0.11902 | -0.16479 | -0.013733 | -0.050354 | 123.0011 | 123.0743 | 58.2733 | -123.0469 | 123.0057 | 122.9187 | 58.374 | -123.1201
233.6406 | 123.2483 | -58.1863 | 64.769 | -0.2101 | -0.021739 | 0.070968 | 0.0050688 | 0.058738 | -0.0080629 | -0.017854 | -0.10039 | -0.01332 | 0.042375 | 0.066962 | 0.017383 | -0.005445 | 64.8605 | -58.017 | 0.091553 | -58.3603 | 64.7873 | -58.1955 | -58.2458 | -58.1406 | 0.27008 | -58.4518 | 64.801 | 64.7232 | -58.2413 | -58.3282 | -0.009156 | -0.05951 | 0.01831 | 0.16937 | -0.17395 | -0.11444 | 0.091553 | -0.054932 | -0.14191 | 0.032043 | 0.045776 | -0.2655 | -0.1236 | -0.045776 | 122.9736 | 123.0469 | 58.2779 | -123.0148 | 122.9874 | 122.9095 | 58.4564 | -123.0972
234.7031 | 123.1567 | -58.2367 | 64.7644 | -0.91201 | 0.0049632 | 0.060287 | 0.020022 | 0.060874 | 0.015435 | -0.0050373 | 0.2353 | -0.010115 | 0.080827 | 0.06269 | 0.010974 | -0.015058 | 64.7095 | -58.1497 | -0.09613 | -58.461 | 64.8193 | -58.2504 | -58.3008 | -58.1909 | -0.068665 | -58.5342 | 64.8514 | 64.7278 | -58.3237 | -58.3969 | -0.013733 | -0.064087 | 0.054932 | 0.086975 | -0.22431 | -0.16022 | -0.054931 | -0.086975 | -0.16022 | 0.086975 | 0.045776 | -0.29755 | -0.13733 | -0.036621 | 123.056 | 122.9462 | 58.1406 | -123.0652 | 123.0881 | 122.9645 | 58.168 | -123.1613
235.6406 | 123.2025 | -58.2092 | 64.7781 | 0.034038 | 0.027394 | 0.056015 | 0.020022 | 0.052329 | 0.016503 | 0.0056447 | -0.39031 | 0.0048376 | 0.063737 | 0.061622 | 0.0067021 | -0.015058 | 64.8514 | -58.1223 | -0.004578 | -58.3969 | 64.8193 | -58.2458 | -58.2916 | -58.1451 | 0.068665 | -58.4747 | 64.8605 | 64.7827 | -58.255 | -58.3786 | -0.036621 | -0.082397 | 0.041199 | 0.086976 | -0.18768 | -0.10529 | 0.073242 | -0.045776 | -0.16937 | 0.082398 | 0.064087 | -0.2655 | -0.09613 | 0.004578 | 123.0286 | 123.0606 | 58.2047 | -123.0698 | 123.0698 | 122.9919 | 58.2779 | -123.1567
236.7031 | 123.2208 | -58.2184 | 64.7415 | 0.53758 | 0.022053 | 0.063492 | 0.0039998 | 0.054465 | 0.0036861 | -0.0018323 | 0.46419 | -0.00050244 | 0.07335 | 0.069098 | 0.012042 | 0.00844 | 64.769 | -58.1863 | -0.10529 | -58.4381 | 64.8056 | -58.2504 | -58.2916 | -58.1543 | -0.018311 | -58.4885 | 64.8148 | 64.7141 | -58.2733 | -58.3603 | -0.032043 | -0.073242 | 0.064087 | 0.032044 | -0.21973 | -0.14648 | 0.027466 | -0.054931 | -0.14191 | 0.073242 | 0.064087 | -0.27008 | -0.12817 | -0.027466 | 123.024 | 122.9874 | 58.1131 | -123.0331 | 123.0331 | 122.9324 | 58.2001 | -123.1018
237.6406 | 123.1796 | -58.223 | 64.7827 | -0.16433 | 0.027394 | 0.059219 | 0.01575 | 0.056601 | 0.0068901 | -0.0018323 | -0.2072 | 0.00056556 | 0.063737 | 0.060554 | -0.0039789 | -0.004377 | 64.8148 | -58.1268 | 0.009155 | -58.3878 | 64.8468 | -58.2275 | -58.2596 | -58.1497 | 0.07782 | -58.4518 | 64.8788 | 64.7873 | -58.2596 | -58.3649 | -0.004578 | -0.036622 | 0.064087 | 0.09613 | -0.1648 | -0.12817 | 0.032043 | -0.036622 | -0.14191 | 0.09613 | 0.073242 | -0.22888 | -0.086975 | 0.004577 | 123.0698 | 123.0377 | 58.2321 | -123.0423 | 123.1018 | 123.0103 | 58.3008 | -123.1476
238.7031 | 123.2437 | -58.1955 | 64.7598 | 0.53758 | 0.017781 | 0.054947 | 0.0039998 | 0.076896 | -0.00058594 | 0.0056447 | 0.47945 | 0.0016336 | 0.062669 | 0.057349 | -0.0061159 | -0.005445 | 64.7919 | -58.1131 | -0.064087 | -58.4061 | 64.769 | -58.255 | -58.3099 | -58.0948 | 0.036621 | -58.4473 | 64.769 | 64.6866 | -58.2779 | -58.342 | -0.059509 | -0.11444 | 0.009155 | 0.082398 | -0.21057 | -0.09613 | 0.032043 | -0.082397 | -0.14648 | 0.009155 | 0.10071 | -0.25177 | -0.10529 | -0.073243 | 122.9645 | 122.9874 | 58.1314 | -123.0698 | 122.9645 | 122.8821 | 58.2321 | -123.1018
239.6406 | 123.1979 | -58.1818 | 64.7964 | -0.19484 | 0.0060322 | 0.078445 | 0.0039998 | 0.061942 | -0.021949 | 0.00030367 | -0.06987 | 0.0027016 | 0.05626 | 0.065894 | -0.00077485 | 0.002032 | 64.8422 | -58.0444 | 0.068665 | -58.3466 | 64.7781 | -58.1955 | -58.255 | -58.1268 | 0.15564 | -58.4106 | 64.8514 | 64.801 | -58.2275 | -58.3191 | -0.013733 | -0.073242 | -0.018311 | 0.13733 | -0.1648 | -0.091553 | 0.045776 | -0.045776 | -0.13733 | 0.054931 | 0.054932 | -0.22888 | -0.091553 | 0.004577 | 122.9599 | 123.024 | 58.2504 | -123.0515 | 123.0331 | 122.9828 | 58.3374 | -123.1155
240.7031 | 123.2391 | -58.1772 | 64.8056 | -0.16433 | -0.0025128 | 0.076309 | -0.0013402 | 0.058738 | -0.018744 | -0.013582 | -0.19194 | -0.015456 | 0.048783 | 0.055213 | -0.0018429 | 0.00096301 | 64.8376 | -58.0399 | 0.059509 | -58.3557 | 64.8056 | -58.1955 | -58.2504 | -58.1314 | 0.13733 | -58.4061 | 64.8605 | 64.7736 | -58.2825 | -58.3511 | -0.018311 | -0.073242 | 0 | 0.13733 | -0.17853 | -0.10529 | 0.032043 | -0.10529 | -0.17395 | 0.054932 | 0.045776 | -0.22888 | -0.054932 | -0.032043 | 122.9828 | 123.0148 | 58.2367 | -123.056 | 123.0377 | 122.9507 | 58.3145 | -123.1567
241.6406 | 123.2803 | -58.1314 | 64.7736 | -0.59157 | -0.020671 | 0.076309 | -0.0088172 | 0.065146 | -0.011268 | -0.012513 | -0.039353 | -0.015456 | 0.061601 | 0.048804 | -0.0061159 | 0.006304 | 64.8422 | -57.9758 | 0.10986 | -58.3328 | 64.7964 | -58.1863 | -58.2458 | -58.0902 | 0.1831 | -58.3511 | 64.8285 | 64.7186 | -58.2642 | -58.3374 | -0.054931 | -0.11444 | 0.022888 | 0.15564 | -0.20142 | -0.086975 | 0.068664 | -0.13275 | -0.20599 | 0.054931 | 0.041199 | -0.21973 | -0.013733 | -0.054932 | 122.9279 | 122.9736 | 58.2413 | -123.0194 | 122.9599 | 122.85 | 58.3145 | -123.111
242.7031 | 123.2483 | -58.1955 | 64.7598 | 0.4918 | -0.024944 | 0.070968 | 0.013613 | 0.056601 | -0.014472 | -0.0071733 | 0.34212 | -0.0090474 | 0.062669 | 0.054145 | -0.0050469 | -0.005445 | 64.7552 | -58.1085 | -0.036621 | -58.4106 | 64.7507 | -58.2321 | -58.2733 | -58.1268 | 0.022888 | -58.4473 | 64.7919 | 64.7232 | -58.2642 | -58.3511 | -0.036621 | -0.077819 | -0.009156 | 0.086975 | -0.21515 | -0.13733 | -0.004578 | -0.068664 | -0.15564 | 0.032043 | 0.068665 | -0.25177 | -0.096131 | -0.036621 | 122.9462 | 122.9507 | 58.1589 | -123.0331 | 122.9874 | 122.9187 | 58.2184 | -123.111
243.6406 | 123.2803 | -58.1497 | 64.7507 | 0.049296 | -0.022808 | 0.0699 | 0.0072048 | 0.068351 | -0.011268 | -0.010377 | 0.11323 | -0.011183 | 0.058397 | 0.048804 | -0.0039789 | -0.002241 | 64.8376 | -58.0399 | 0.036621 | -58.3557 | 64.8056 | -58.2275 | -58.2687 | -58.0582 | 0.19684 | -58.3649 | 64.8285 | 64.7232 | -58.2275 | -58.3099 | -0.07782 | -0.11902 | 0.054932 | 0.10986 | -0.20599 | -0.086975 | 0.086975 | -0.07782 | -0.16022 | 0.07782 | 0.091552 | -0.21515 | -0.054931 | -0.027465 | 122.9553 | 122.9874 | 58.1863 | -123.0194 | 122.9782 | 122.8729 | 58.3466 | -123.0606
244.7031 | 123.1796 | -58.2458 | 64.7919 | 0.29344 | 0.019917 | 0.066696 | 0.02109 | 0.065146 | 0.021844 | -0.0029003 | 0.20479 | -0.0026384 | 0.077623 | 0.057349 | 0.015247 | -0.009718 | 64.7964 | -58.2275 | -0.15106 | -58.4839 | 64.8056 | -58.2733 | -58.3099 | -58.2504 | -0.10071 | -58.6029 | 64.856 | 64.7552 | -58.3008 | -58.374 | -0.027465 | -0.064087 | 0.013733 | 0.018311 | -0.23804 | -0.17395 | 0.004578 | -0.054931 | -0.12817 | 0.064087 | -0.004577 | -0.35706 | -0.22888 | -0.036621 | 123.0515 | 123.0423 | 58.0948 | -123.1018 | 123.1018 | 123.0011 | 58.1451 | -123.1659
245.6406 | 123.1384 | -58.1955 | 64.769 | 0.00352 | 0.019917 | 0.058151 | 0.0082728 | 0.064078 | 0.013299 | 0.0013717 | -0.13091 | -0.011183 | 0.044511 | 0.048804 | 0.017383 | -0.004377 | 64.8422 | -58.1131 | -0.018311 | -58.3969 | 64.8148 | -58.255 | -58.3099 | -58.1177 | 0.068665 | -58.4656 | 64.8468 | 64.769 | -58.2733 | -58.3694 | -0.059509 | -0.11444 | 0.045776 | 0.082398 | -0.20142 | -0.086975 | 0.073242 | -0.077819 | -0.17395 | 0.07782 | 0.07782 | -0.27008 | -0.09613 | 0 | 123.0103 | 123.0377 | 58.1772 | -123.0789 | 123.0423 | 122.9645 | 58.2642 | -123.1384
246.7031 | 123.1293 | -58.2184 | 64.7827 | 0.12559 | 0.025258 | 0.063492 | 0.018954 | 0.064078 | 0.020776 | -0.0061053 | -0.085129 | 0.00056556 | 0.060533 | 0.049872 | 0.0099061 | -0.010786 | 64.6957 | -58.0536 | -0.009155 | -58.4106 | 64.8285 | -58.2458 | -58.2825 | -58.136 | 0.041199 | -58.4839 | 64.8422 | 64.7507 | -58.2779 | -58.342 | -0.027466 | -0.064087 | 0.045776 | 0.16479 | -0.19226 | -0.12817 | -0.086975 | -0.059509 | -0.1236 | 0.059509 | 0.082398 | -0.2655 | -0.14191 | -0.032044 | 123.0469 | 122.9141 | 58.2092 | -123.0652 | 123.0606 | 122.9691 | 58.2596 | -123.1247
247.6562 | 123.1247 | -58.223 | 64.801 | 0.12559 | 0.014576 | 0.051742 | 0.023226 | 0.057669 | 0.016503 | -0.0018323 | 0.12849 | -0.0015704 | 0.059465 | 0.063758 | 0.0056341 | -0.011854 | 64.7873 | -58.1543 | -0.059509 | -58.4198 | 64.8148 | -58.2596 | -58.3008 | -58.168 | -0.004578 | -58.5068 | 64.8468 | 64.7736 | -58.2825 | -58.3649 | -0.036622 | -0.07782 | 0.013733 | 0.068664 | -0.19684 | -0.11902 | -0.013733 | -0.05951 | -0.14191 | 0.045777 | 0.054931 | -0.28381 | -0.14191 | -0.027465 | 123.0377 | 123.0103 | 58.1635 | -123.1018 | 123.0698 | 122.9965 | 58.2184 | -123.1659
248.7031 | 123.175 | -58.2184 | 64.7964 | 0.46128 | 0.020985 | 0.066696 | 0.020022 | 0.061942 | -0.00058594 | 0.0077807 | 0.38789 | -0.0026384 | 0.063737 | 0.052009 | -0.0050469 | -0.00010499 | 64.7278 | -58.2047 | -0.13275 | -58.461 | 64.7964 | -58.2504 | -58.3374 | -58.1863 | -0.48981 | -58.4839 | 64.8056 | 64.7781 | -58.3145 | -58.3923 | -0.032043 | -0.11902 | 0 | 0.013733 | -0.24262 | -0.1236 | -0.068665 | -0.09613 | -0.17395 | 0.009155 | 0.032044 | -0.2655 | -0.091553 | -0.018311 | 123.0148 | 122.9462 | 58.0856 | -123.1338 | 123.024 | 122.9965 | 57.7286 | -123.1888
249.6406 | 123.3353 | -58.1955 | 64.7781 | 0.21714 | -0.0057178 | 0.066696 | -0.0045452 | 0.053397 | -0.033698 | 0.0077807 | 0.50996 | -0.0090474 | 0.05626 | 0.058417 | -0.010388 | -0.004377 | 64.7552 | -58.1223 | -0.054932 | -58.4198 | 64.7552 | -58.2504 | -58.287 | -58.1451 | 0.050354 | -58.4381 | 64.7964 | 64.7461 | -58.2825 | -58.3466 | -0.054931 | -0.091552 | -0.022888 | 0.073243 | -0.2243 | -0.13275 | -0.022888 | -0.086975 | -0.15106 | 0.018311 | 0.050354 | -0.24261 | -0.091552 | -0.032043 | 122.9507 | 122.9507 | 58.1406 | -123.0652 | 122.9919 | 122.9416 | 58.2458 | -123.1247
250.7031 | 123.2437 | -58.1909 | 64.7324 | 0.58335 | 0.011372 | 0.050674 | 0.016818 | 0.057669 | -0.0080629 | -0.0061053 | 0.47945 | -0.014388 | 0.066941 | 0.059485 | -0.00077485 | -0.005445 | 64.7919 | -58.0353 | 0.004578 | -58.3969 | 64.7507 | -58.2321 | -58.2825 | -58.1039 | 0.059509 | -58.4061 | 64.7827 | 64.6957 | -58.2779 | -58.3603 | -0.041199 | -0.091553 | 0.01831 | 0.15564 | -0.20599 | -0.11444 | 0.059509 | -0.086975 | -0.16937 | 0.050354 | 0.086975 | -0.21515 | -0.045776 | -0.036621 | 122.9416 | 122.9828 | 58.1955 | -123.0148 | 122.9736 | 122.8867 | 58.2504 | -123.0927
251.6406 | 123.262 | -58.1772 | 64.7598 | 0.095073 | -0.020671 | 0.08165 | 0.0029318 | 0.068351 | -0.024085 | -0.01465 | 0.2353 | -0.021865 | 0.061601 | 0.058417 | -0.0093199 | -0.004377 | 64.8102 | -58.0948 | 0.004578 | -58.3694 | 64.8148 | -58.2367 | -58.255 | -58.0948 | 0.11444 | -58.3786 | 64.7873 | 64.7598 | -58.2733 | -58.3374 | -0.059509 | -0.07782 | 0.054931 | 0.082397 | -0.19226 | -0.11444 | 0.050354 | -0.09613 | -0.16022 | 0.027465 | 0.082397 | -0.20142 | -0.041199 | 0 | 122.9919 | 122.9874 | 58.1818 | -123.0148 | 122.9645 | 122.937 | 58.2916 | -123.0972
252.7031 | 123.2712 | -58.1863 | 64.7461 | 0.3087 | -0.020671 | 0.058151 | 0.0029318 | 0.06301 | -0.014472 | -0.016786 | 0.0064239 | -0.019728 | 0.05092 | 0.052009 | -0.0018429 | 0.0031 | 64.7781 | -58.136 | -0.027466 | -58.3969 | 64.7736 | -58.2138 | -58.2779 | -58.1406 | 0.054932 | -58.4381 | 64.8422 | 64.7415 | -58.255 | -58.3786 | -0.027466 | -0.091553 | 0.027466 | 0.050354 | -0.21057 | -0.11902 | 0.032043 | -0.068665 | -0.19226 | 0.09613 | 0.045776 | -0.25177 | -0.059509 | -0.004578 | 122.9599 | 122.9645 | 58.1589 | -123.024 | 123.0286 | 122.9279 | 58.2413 | -123.1247
253.6406 | 123.2254 | -58.2047 | 64.7507 | 0.36973 | -0.0089218 | 0.077377 | -0.0077492 | 0.060874 | -0.0059269 | -0.013582 | 0.37263 | -0.017592 | 0.047715 | 0.058417 | 0.0034971 | -0.006513 | 64.7873 | -58.1268 | -0.050354 | -58.4106 | 64.7919 | -58.2413 | -58.2779 | -58.1497 | 0.041199 | -58.4473 | 64.8056 | 64.7186 | -58.2733 | -58.3466 | -0.036621 | -0.073242 | 0.041199 | 0.07782 | -0.20599 | -0.13275 | 0.036621 | -0.068664 | -0.14191 | 0.054932 | 0.054932 | -0.24262 | -0.10071 | -0.032043 | 122.9965 | 122.9919 | 58.1543 | -123.0286 | 123.0103 | 122.9233 | 58.2458 | -123.0972
254.7031 | 123.1934 | -58.1909 | 64.7736 | 0.034038 | 0.022053 | 0.056015 | 0.02109 | 0.059806 | 0.026116 | 0.00030367 | -0.054612 | -0.0037074 | 0.061601 | 0.058417 | 0.0067021 | -0.020399 | 64.8743 | -58.1223 | -0.004578 | -58.3923 | 64.8056 | -58.2642 | -58.2733 | -58.1268 | 0 | -58.5663 | 64.8193 | 64.7278 | -58.2596 | -58.3694 | -0.073242 | -0.082397 | 0.032043 | 0.068665 | -0.20142 | -0.11902 | 0.10071 | -0.068665 | -0.17853 | 0.045776 | 0.064087 | -0.37537 | -0.19684 | -0.045777 | 122.9965 | 123.0652 | 58.1863 | -123.0469 | 123.0103 | 122.9187 | 58.1909 | -123.143
255.6406 | 123.262 | -58.1497 | 64.7598 | 0.2324 | -0.018535 | 0.078445 | 0.00079576 | 0.06301 | -0.019813 | -0.012513 | 0.2353 | -0.011183 | 0.03917 | 0.069098 | -0.0018429 | -0.006513 | 64.8056 | -58.0902 | -0.018311 | -58.3832 | 64.7964 | -58.2275 | -58.2962 | -58.0994 | 0.10986 | -58.3969 | 64.8056 | 64.7415 | -58.255 | -58.3191 | -0.07782 | -0.14649 | 0.036621 | 0.059509 | -0.23346 | -0.086975 | 0.045776 | -0.10529 | -0.16937 | 0.045776 | 0.050354 | -0.24719 | -0.07782 | -0.018311 | 122.9462 | 122.9553 | 58.1314 | -123.056 | 122.9553 | 122.8912 | 58.2596 | -123.0789
256.7031 | 123.1293 | -58.2184 | 64.769 | 0.26292 | 0.018849 | 0.070968 | 0.022158 | 0.061942 | 0.027185 | 0.00030367 | 0.2353 | 0.0037696 | 0.074418 | 0.063758 | 0.017383 | -0.010786 | 64.7644 | -58.2367 | -0.14191 | -58.4702 | 64.8239 | -58.2733 | -58.3008 | -58.2138 | -0.07782 | -58.5663 | 64.8331 | 64.7415 | -58.2962 | -58.3694 | -0.054931 | -0.082397 | 0.054932 | -0.01831 | -0.25177 | -0.16937 | -0.004578 | -0.07782 | -0.15106 | 0.064087 | 0.004578 | -0.3479 | -0.19684 | -0.027466 | 123.0423 | 122.9828 | 58.0765 | -123.0698 | 123.0515 | 122.9599 | 58.1406 | -123.1384
257.6406 | 123.23 | -58.1543 | 64.7919 | -0.14907 | -0.012126 | 0.08165 | 0.0039998 | 0.064078 | -0.014472 | 0.0099167 | -0.22246 | -0.011183 | 0.040239 | 0.055213 | -0.0050469 | -0.005445 | 64.5538 | -57.9712 | 0.13275 | -58.4015 | 64.7919 | -58.2001 | -58.255 | -58.1039 | 0.15564 | -58.3786 | 64.8285 | 64.7552 | -58.2275 | -58.3099 | -0.045776 | -0.10071 | 0 | 0.18311 | -0.24719 | -0.14648 | -0.23804 | -0.073242 | -0.15564 | 0.036621 | 0.050354 | -0.2243 | -0.068664 | -0.036621 | 122.9462 | 122.7081 | 58.287 | -123.0469 | 122.9828 | 122.9095 | 58.3099 | -123.1018
258.7031 | 123.175 | -58.1772 | 64.8102 | -0.17959 | 0.014576 | 0.067764 | 0.0072048 | 0.068351 | 0.010095 | -0.0082413 | -0.22246 | -0.012251 | 0.057328 | 0.06269 | 0.014179 | -0.019331 | 64.8102 | -58.1223 | -0.004578 | -58.4015 | 64.8514 | -58.2367 | -58.2962 | -58.1451 | 0.09613 | -58.4702 | 64.8514 | 64.7552 | -58.2733 | -58.374 | -0.059509 | -0.11902 | 0.041198 | 0.054932 | -0.2243 | -0.10528 | 0 | -0.09613 | -0.19684 | 0.041198 | 0.032043 | -0.29297 | -0.096131 | -0.054932 | 123.0286 | 122.9874 | 58.1726 | -123.1064 | 123.0286 | 122.9324 | 58.2733 | -123.1842
259.6406 | 123.2346 | -58.1726 | 64.7644 | 0.20188 | -0.013195 | 0.083786 | -0.0088172 | 0.061942 | -0.031562 | -0.012513 | 0.34212 | -0.025069 | 0.042375 | 0.057349 | -0.0050469 | 0.006304 | 64.7369 | -58.1039 | -0.013733 | -58.3832 | 64.7781 | -58.223 | -58.2596 | -58.1177 | 0.082397 | -58.4198 | 64.7964 | 64.7324 | -58.2779 | -58.342 | -0.050354 | -0.086976 | 0.013733 | 0.068664 | -0.21057 | -0.1236 | -0.027466 | -0.10529 | -0.16937 | 0.032044 | 0.054931 | -0.24719 | -0.07782 | -0.032043 | 122.9507 | 122.9095 | 58.1589 | -123.024 | 122.9691 | 122.905 | 58.255 | -123.1064
260.7031 | 123.143 | -58.1909 | 64.7781 | 0.049296 | 0.023121 | 0.065628 | 0.011477 | 0.061942 | 0.02398 | 0.0056447 | -0.054612 | -0.0079794 | 0.070146 | 0.049872 | 0.010974 | -0.016126 | 64.8331 | -58.1268 | 0.004578 | -58.3923 | 64.8193 | -58.2458 | -58.2916 | -58.1177 | 0.059509 | -58.4702 | 64.856 | 64.7461 | -58.2779 | -58.3649 | -0.054932 | -0.10071 | 0.041199 | 0.064087 | -0.20142 | -0.10071 | 0.054932 | -0.086975 | -0.17395 | 0.07782 | 0.073242 | -0.27924 | -0.10529 | -0.032043 | 123.0103 | 123.024 | 58.1955 | -123.0698 | 123.0469 | 122.937 | 58.2504 | -123.143
261.6406 | 123.2391 | -58.1818 | 64.7232 | 1.8956 | 0.014576 | 0.063492 | 0.0018638 | 0.072623 | -0.019813 | 0.012053 | 0.67781 | -0.01866 | 0.057328 | 0.053077 | -0.0082519 | 0.004168 | 64.8605 | -58.0856 | -0.027466 | -58.3832 | 64.7552 | -58.2367 | -58.2687 | -58.0994 | 0.054932 | -58.4198 | 64.7873 | 64.7095 | -58.2642 | -58.342 | -0.054931 | -0.086975 | 0.032043 | 0.096131 | -0.20142 | -0.11444 | 0.13733 | -0.082397 | -0.16022 | 0.064086 | 0.082398 | -0.23804 | -0.07782 | -0.013733 | 122.937 | 123.0423 | 58.1543 | -122.9919 | 122.9691 | 122.8912 | 58.2367 | -123.0652
262.7031 | 123.2529 | -58.1772 | 64.7324 | 0.4918 | 0.020985 | 0.072037 | 0.00079576 | 0.056601 | -0.0027229 | -0.015718 | 0.58626 | -0.010115 | 0.062669 | 0.052009 | 0.0024291 | -0.006513 | 64.8422 | -58.0902 | -0.022888 | -58.3694 | 64.7369 | -58.2413 | -58.2825 | -58.0811 | 0.059509 | -58.4106 | 64.7781 | 64.6957 | -58.2687 | -58.3603 | -0.064087 | -0.10529 | 0.004577 | 0.086975 | -0.19226 | -0.086975 | 0.10986 | -0.091553 | -0.18311 | 0.045776 | 0.09613 | -0.23346 | -0.050354 | -0.036621 | 122.9141 | 123.0194 | 58.1543 | -123.0148 | 122.9553 | 122.8729 | 58.2367 | -123.0927
263.6406 | 123.2346 | -58.1818 | 64.7644 | 0.20188 | -0.022808 | 0.085922 | -0.0088172 | 0.04592 | -0.024085 | -0.017854 | 0.22005 | -0.017592 | 0.053056 | 0.048804 | -0.0093199 | -0.003309 | 64.7964 | -58.0811 | 0.086975 | -58.3649 | 64.7873 | -58.2184 | -58.255 | -58.1223 | 0.064087 | -58.4473 | 64.8422 | 64.7369 | -58.2596 | -58.3511 | -0.036621 | -0.073242 | 0.022888 | 0.10071 | -0.18311 | -0.10986 | 0.032044 | -0.07782 | -0.16937 | 0.07782 | 0.05951 | -0.2655 | -0.096131 | -0.027466 | 122.9691 | 122.9782 | 58.2687 | -123.0194 | 123.024 | 122.9187 | 58.2458 | -123.1155
264.7031 | 123.1522 | -58.2047 | 64.769 | -0.2864 | 0.027394 | 0.066696 | 0.012545 | 0.056601 | 0.020776 | -0.0061053 | -0.054612 | -0.0037074 | 0.07335 | 0.052009 | 0.014179 | -0.019331 | 64.8468 | -58.1314 | -0.013733 | -58.4152 | 64.8193 | -58.2367 | -58.2916 | -58.1543 | 0.045776 | -58.5114 | 64.8514 | 64.769 | -58.2687 | -58.3603 | -0.032043 | -0.086975 | 0.050354 | 0.073242 | -0.21057 | -0.1236 | 0.07782 | -0.064087 | -0.15564 | 0.082397 | 0.050354 | -0.3067 | -0.15106 | 0 | 123.024 | 123.0515 | 58.1909 | -123.0606 | 123.056 | 122.9736 | 58.2504 | -123.1293
265.6406 | 123.2346 | -58.2001 | 64.7461 | 0.96482 | -0.0035808 | 0.066696 | -0.010953 | 0.061942 | -0.0080629 | -0.0018323 | 0.61677 | -0.017592 | 0.054124 | 0.053077 | -0.00077485 | 0.005236 | 64.8193 | -58.0627 | 0.018311 | -58.3786 | 64.7552 | -58.2092 | -58.255 | -58.0902 | 0.032043 | -58.429 | 64.7736 | 64.7141 | -58.255 | -58.342 | -0.009156 | -0.054932 | 0.009155 | 0.13733 | -0.17853 | -0.1236 | 0.073242 | -0.054932 | -0.14191 | 0.027466 | 0.10986 | -0.22888 | -0.086975 | -0.032044 | 122.9553 | 123.0194 | 58.2184 | -123.0011 | 122.9736 | 122.9141 | 58.2321 | -123.0881
266.7031 | 123.23 | -58.1635 | 64.7552 | 0.3087 | -0.024944 | 0.077377 | 0.0082728 | 0.064078 | -0.021949 | -0.012513 | 0.3116 | -0.015456 | 0.047715 | 0.057349 | -0.0039789 | 0.002032 | 64.7873 | -58.1131 | -0.050354 | -58.4015 | 64.7873 | -58.2275 | -58.2779 | -58.1451 | 0.17853 | -58.3603 | 64.8468 | 64.7278 | -58.2687 | -58.3328 | -0.064087 | -0.11444 | 0.032043 | 0.050354 | -0.23804 | -0.1236 | 0.032043 | -0.10529 | -0.16937 | 0.091553 | 0.01831 | -0.19684 | -0.027466 | -0.027466 | 122.9507 | 122.9507 | 58.1131 | -123.0331 | 123.0103 | 122.8912 | 58.342 | -123.0881
267.6406 | 123.23 | -58.1406 | 64.7964 | 5.0847 | -0.014263 | 0.084854 | -0.0056132 | 0.066214 | -0.011268 | -0.013582 | 0.036941 | -0.024001 | 0.047715 | 0.039191 | 0.0088381 | -0.01399 | 64.888 | -58.0765 | 0.082397 | -58.3374 | 64.7919 | -58.223 | -58.2733 | -58.0994 | 0.1831 | -58.3969 | 64.8605 | 64.7644 | -58.2367 | -58.3099 | -0.082397 | -0.13275 | -0.004578 | 0.064087 | -0.19684 | -0.064087 | 0.091552 | -0.09613 | -0.16937 | 0.064087 | 0.041199 | -0.25635 | -0.086975 | -0.032044 | 122.9324 | 123.0286 | 58.223 | -123.0698 | 123.0011 | 122.905 | 58.3237 | -123.1064
268.7031 | 123.1705 | -58.2092 | 64.769 | 0.079814 | 0.02419 | 0.062424 | 0.024295 | 0.056601 | 0.017572 | 0.0035077 | 0.0064239 | -0.0047754 | 0.070146 | 0.059485 | 0.010974 | -0.022535 | 64.8422 | -58.1406 | -0.032043 | -58.4106 | 64.8148 | -58.2138 | -58.2825 | -58.1497 | -0.022888 | -58.5159 | 64.8376 | 64.7461 | -58.3054 | -58.3694 | -0.004577 | -0.073242 | 0.045776 | 0.068665 | -0.20142 | -0.12817 | 0.073242 | -0.09613 | -0.16022 | 0.068664 | 0.05951 | -0.3067 | -0.14648 | -0.022888 | 123.024 | 123.0515 | 58.1772 | -123.0515 | 123.0469 | 122.9553 | 58.1863 | -123.1384
269.6406 | 123.2803 | -58.2047 | 64.6957 | 0.55284 | -0.00037681 | 0.068832 | 0.014682 | 0.066214 | -0.0016549 | 0.0024397 | 0.58626 | -0.017592 | 0.057328 | 0.058417 | 0.0056341 | -0.001173 | 64.8331 | -58.0811 | -0.032043 | -58.3786 | 64.7507 | -58.2504 | -58.287 | -58.0948 | 0.054932 | -58.4244 | 64.7781 | 64.7003 | -58.2642 | -58.3511 | -0.045776 | -0.082397 | 0.054931 | 0.1236 | -0.17395 | -0.091553 | 0.13733 | -0.059509 | -0.14648 | 0.082397 | 0.10986 | -0.21973 | -0.073242 | 0.004577 | 122.9553 | 123.0377 | 58.1726 | -122.9828 | 122.9828 | 122.905 | 58.2596 | -123.0469
270.7031 | 123.1201 | -58.1863 | 64.7873 | -0.27114 | 0.0071002 | 0.082718 | -0.00027224 | 0.054465 | -0.010199 | -0.00076433 | 0.097976 | -0.0058434 | 0.058397 | 0.059485 | -0.0050469 | -0.009718 | 64.7919 | -58.1406 | -0.013733 | -58.4152 | 64.8376 | -58.2321 | -58.2779 | -58.1726 | 0.073242 | -58.493 | 64.8743 | 64.8285 | -58.255 | -58.3145 | -0.045777 | -0.091553 | 0.050354 | 0.045776 | -0.22888 | -0.13733 | 0.004578 | -0.068665 | -0.12817 | 0.086976 | 0.013733 | -0.3067 | -0.17853 | 0.041199 | 123.024 | 122.9782 | 58.1726 | -123.0652 | 123.0606 | 123.0148 | 58.2596 | -123.1018
271.6406 | 123.2574 | -58.1772 | 64.7141 | 0.53758 | 0.0049632 | 0.076309 | 0.011477 | 0.068351 | 0.0036861 | -0.0093093 | 0.4947 | -0.0079794 | 0.047715 | 0.059485 | 0.0013611 | 0.005236 | 64.8605 | -58.1818 | -0.09613 | -58.3786 | 64.769 | -58.255 | -58.2779 | -58.1085 | 0.041199 | -58.4244 | 64.7919 | 64.7095 | -58.255 | -58.342 | -0.07782 | -0.10071 | 0.054932 | -0.004578 | -0.20142 | -0.10071 | 0.14648 | -0.07782 | -0.16479 | 0.07782 | 0.068664 | -0.24719 | -0.082397 | -0.004577 | 122.9462 | 123.0377 | 58.0811 | -122.9919 | 122.9691 | 122.8867 | 58.2184 | -123.056
272.7031 | 123.2483 | -58.1909 | 64.7552 | 0.33921 | 0.010304 | 0.073105 | 0.018954 | 0.058738 | 0.00048206 | -0.0039683 | 0.55574 | -0.0058434 | 0.05626 | 0.071235 | -0.0050469 | -0.011854 | 64.8605 | -58.1039 | -0.064087 | -58.3923 | 64.7369 | -58.2504 | -58.255 | -58.1039 | 0.036621 | -58.4381 | 64.769 | 64.7095 | -58.2687 | -58.3557 | -0.059509 | -0.064087 | -0.018311 | 0.086975 | -0.20142 | -0.13733 | 0.10529 | -0.07782 | -0.16479 | 0.013733 | 0.086975 | -0.24719 | -0.082397 | -0.045776 | 122.9279 | 123.0515 | 58.1268 | -123.0103 | 122.9599 | 122.9004 | 58.2275 | -123.111
273.6406 | 123.2071 | -58.1726 | 64.7461 | 0.26292 | -0.016399 | 0.0699 | 0.0050688 | 0.049125 | -0.019813 | -0.0082413 | 2.4478 | -0.015456 | 0.043443 | 0.060554 | -0.0071839 | 0.009508 | 64.801 | -58.1131 | -0.032043 | -58.4061 | 64.7781 | -58.2092 | -58.2642 | -58.1268 | 0.050354 | -58.4427 | 64.8056 | 64.7461 | -58.255 | -58.3603 | -0.036622 | -0.091553 | 0.032043 | 0.059509 | -0.23346 | -0.14191 | 0.054931 | -0.082398 | -0.18768 | 0.059509 | 0.045776 | -0.27008 | -0.082397 | 0 | 122.9507 | 122.9736 | 58.1406 | -123.0103 | 122.9782 | 122.9187 | 58.223 | -123.1064
274.7031 | 123.2162 | -58.2001 | 64.7827 | -0.11855 | 0.026326 | 0.065628 | 0.028567 | 0.071555 | 0.017572 | -0.00076433 | -0.26824 | 0.0059056 | 0.072282 | 0.048804 | -0.00077485 | -0.012922 | 64.8376 | -58.1497 | -0.009155 | -58.3832 | 64.8239 | -58.2367 | -58.2733 | -58.1451 | 0.086975 | -58.461 | 64.8697 | 64.7552 | -58.2504 | -58.3603 | -0.036621 | -0.073242 | 0.041199 | 0.050354 | -0.18311 | -0.10986 | 0.054931 | -0.050354 | -0.16022 | 0.086975 | 0.054931 | -0.26093 | -0.10071 | -0.027466 | 123.024 | 123.0377 | 58.1909 | -123.056 | 123.0698 | 122.9553 | 58.287 | -123.143
275.6406 | 123.2437 | -58.1818 | 64.7369 | 0.4918 | 0.0092362 | 0.057083 | -0.0077492 | 0.073691 | -0.01554 | -0.018922 | 0.76936 | -0.010115 | 0.055192 | 0.048804 | 0.0034971 | -0.003309 | 64.856 | -58.049 | 0.022888 | -58.3557 | 64.7598 | -58.223 | -58.2733 | -58.0902 | 0.068665 | -58.4244 | 64.7736 | 64.7232 | -58.3008 | -58.3511 | -0.041198 | -0.091552 | 0.022889 | 0.13275 | -0.17395 | -0.082398 | 0.11902 | -0.11902 | -0.16937 | 0.036622 | 0.091553 | -0.24261 | -0.073242 | -0.013732 | 122.9416 | 123.0377 | 58.2047 | -123.0103 | 122.9553 | 122.905 | 58.2504 | -123.0881
276.7031 | 123.1018 | -58.2138 | 64.8193 | -0.11855 | 0.0071002 | 0.056015 | 0.0050688 | 0.061942 | -0.0027229 | -0.0018323 | -0.26824 | -0.0015704 | 0.059465 | 0.056281 | -0.0018429 | -0.00865 | 64.7873 | -58.1497 | -0.018311 | -58.4152 | 64.8651 | -58.2138 | -58.287 | -58.1772 | 0.054932 | -58.493 | 64.8972 | 64.8102 | -58.2596 | -58.287 | 0 | -0.073242 | 0.045776 | 0.064087 | -0.20142 | -0.12817 | -0.032044 | -0.045777 | -0.073242 | 0.07782 | 0.036621 | -0.27924 | -0.20599 | -0.009155 | 123.0789 | 123.0011 | 58.1955 | -123.1064 | 123.111 | 123.024 | 58.2687 | -123.1064
277.6406 | 123.262 | -58.136 | 64.7781 | -0.11855 | -0.018535 | 0.084854 | 0.0018638 | 0.066214 | -0.013404 | -0.010377 | 0.036941 | -0.011183 | 0.042375 | 0.0456 | -0.0050469 | -0.006513 | 64.856 | -58.0032 | 0.10071 | -58.342 | 64.7736 | -58.2092 | -58.2413 | -58.0673 | 0.18768 | -58.342 | 64.801 | 64.7095 | -58.2504 | -58.3191 | -0.073243 | -0.10529 | -0.004577 | 0.13275 | -0.20599 | -0.10071 | 0.07782 | -0.11444 | -0.18311 | 0.022888 | 0.068664 | -0.20599 | -0.022888 | -0.068664 | 122.9095 | 122.9919 | 58.2367 | -123.0194 | 122.937 | 122.8455 | 58.3237 | -123.0972
278.7031 | 123.1476 | -58.2001 | 64.8102 | -0.2101 | -0.018535 | 0.08165 | 0.0018638 | 0.064078 | -0.0059269 | -0.01465 | -0.11565 | -0.01332 | 0.048783 | 0.052009 | 0.010974 | -0.007581 | 64.7964 | -58.0948 | 0.027466 | -58.3466 | 64.8422 | -58.2184 | -58.2779 | -58.1818 | 0.07782 | -58.4747 | 64.8697 | 64.7919 | -58.2733 | -58.3374 | -0.018311 | -0.07782 | 0.032043 | 0.10529 | -0.14648 | -0.068665 | -0.013733 | -0.073242 | -0.13733 | 0.059509 | 0.01831 | -0.27466 | -0.13733 | -0.018311 | 123.0423 | 122.9965 | 58.2275 | -123.0881 | 123.0698 | 122.9919 | 58.2779 | -123.1476
279.6406 | 123.23 | -58.1909 | 64.7552 | 0.29344 | -0.020671 | 0.075241 | -0.0024082 | 0.050193 | -0.017676 | -0.013582 | 0.35738 | -0.010115 | 0.040239 | 0.047736 | 0.0013611 | -0.001173 | 64.7873 | -58.1039 | -0.041199 | -58.4198 | 64.7873 | -58.2184 | -58.287 | -58.1406 | 0.018311 | -58.4381 | 64.8102 | 64.7186 | -58.2779 | -58.3557 | -0.027466 | -0.09613 | 0.032043 | 0.086975 | -0.22888 | -0.13275 | 0.032043 | -0.086975 | -0.16479 | 0.054932 | 0.050354 | -0.24719 | -0.082397 | -0.036621 | 122.9782 | 122.9782 | 58.1497 | -123.0423 | 123.0011 | 122.9095 | 58.2092 | -123.111
280.7031 | 123.1796 | -58.1818 | 64.7964 | -0.14907 | 0.023121 | 0.070968 | 0.036044 | 0.059806 | 0.014367 | 0.0067127 | -0.19194 | -0.0079794 | 0.065873 | 0.065894 | 0.0067021 | -0.015058 | 64.856 | -58.1131 | 0.009155 | -58.3878 | 64.8331 | -58.2413 | -58.2779 | -58.1314 | 0.10529 | -58.4564 | 64.8697 | 64.7461 | -58.2504 | -58.3694 | -0.059509 | -0.09613 | 0.036621 | 0.068665 | -0.20599 | -0.10986 | 0.059509 | -0.068664 | -0.18768 | 0.073242 | 0.050354 | -0.27466 | -0.086975 | -0.050354 | 123.0148 | 123.0377 | 58.1909 | -123.0743 | 123.0515 | 122.9279 | 58.287 | -123.1659
281.6406 | 123.2254 | -58.1863 | 64.7461 | 0.46128 | -0.0099898 | 0.068832 | 0.0039998 | 0.069419 | -0.012336 | -0.016786 | 0.41841 | -0.020796 | 0.055192 | 0.052009 | -0.0050469 | 0.006304 | 64.7873 | -58.1039 | -0.036621 | -58.429 | 64.7827 | -58.2458 | -58.2779 | -58.1268 | 0.036621 | -58.429 | 64.8056 | 64.7186 | -58.2458 | -58.3466 | -0.05951 | -0.091553 | 0.036621 | 0.082397 | -0.24262 | -0.15106 | 0.041198 | -0.05951 | -0.16022 | 0.059509 | 0.059509 | -0.24262 | -0.082397 | -0.027466 | 122.9691 | 122.9736 | 58.1497 | -123.024 | 122.9919 | 122.905 | 58.223 | -123.0927
282.7031 | 123.1476 | -58.1863 | 64.7873 | 0.11033 | 0.038075 | 0.073105 | 0.02109 | 0.061942 | 0.01864 | -0.0039683 | -0.57341 | -0.011183 | 0.06801 | 0.047736 | 0.0013611 | -0.022535 | 64.856 | -58.1223 | -0.036621 | -58.4747 | 64.801 | -58.2825 | -58.2825 | -58.1268 | 0.041199 | -58.4702 | 64.8331 | 64.769 | -58.2916 | -58.3466 | -0.096131 | -0.096131 | 0.013733 | 0.064087 | -0.28839 | -0.19226 | 0.068665 | -0.10529 | -0.16022 | 0.045777 | 0.059509 | -0.28381 | -0.1236 | -0.01831 | 122.9874 | 123.0423 | 58.1497 | -123.0698 | 123.0194 | 122.9553 | 58.2275 | -123.1338
283.6406 | 123.2529 | -58.1955 | 64.7186 | 0.56809 | 0.0028272 | 0.051742 | 0.010409 | 0.064078 | 0.0079581 | -0.010377 | 1.5018 | -0.0079794 | 0.059465 | 0.0456 | 0.0013611 | 0.004168 | 64.8193 | -58.1039 | -0.036621 | -58.3649 | 64.7598 | -58.2321 | -58.287 | -58.1223 | 0.032043 | -58.4198 | 64.7919 | 64.6912 | -58.2779 | -58.342 | -0.036621 | -0.091552 | 0.041199 | 0.091553 | -0.16937 | -0.07782 | 0.10071 | -0.082397 | -0.14648 | 0.073242 | 0.073243 | -0.2243 | -0.07782 | -0.027466 | 122.9553 | 123.0148 | 58.1589 | -123.0057 | 122.9874 | 122.8867 | 58.2275 | -123.0606
284.7031 | 123.143 | -58.1863 | 64.8102 | -0.011739 | -0.016399 | 0.084854 | 0.0029318 | 0.055533 | -0.0016549 | 0.0067127 | -0.31401 | -0.012251 | 0.048783 | 0.043464 | -0.0018429 | -0.006513 | 64.7552 | -58.1131 | 0.004578 | -58.4198 | 64.8422 | -58.2367 | -58.2687 | -58.1818 | 0.073242 | -58.4747 | 64.8743 | 64.7873 | -58.2825 | -58.3328 | -0.050354 | -0.082398 | 0.032043 | 0.073242 | -0.23346 | -0.15106 | -0.054932 | -0.096131 | -0.14648 | 0.064087 | 0.004577 | -0.28839 | -0.14191 | -0.022889 | 123.0286 | 122.9416 | 58.1909 | -123.0789 | 123.0606 | 122.9736 | 58.2596 | -123.143
285.6406 | 123.0881 | -58.2275 | 64.7827 | 0.26292 | 0.016713 | 0.073105 | 0.022158 | 0.076896 | 0.013299 | 0.00030367 | 0.20479 | -0.0015704 | 0.064805 | 0.064826 | 0.01311 | -0.010786 | 64.7507 | -58.223 | -0.10529 | -58.4564 | 64.8148 | -58.2596 | -58.3099 | -58.2321 | -0.091553 | -58.5754 | 64.8422 | 64.7415 | -58.2962 | -58.3923 | -0.032044 | -0.082398 | 0.032043 | 0.004578 | -0.22888 | -0.14648 | -0.032044 | -0.068665 | -0.16479 | 0.059509 | -0.004578 | -0.3479 | -0.18311 | -0.041199 | 123.0423 | 122.9782 | 58.1223 | -123.0927 | 123.0698 | 122.9691 | 58.136 | -123.175
286.7031 | 123.1384 | -58.1635 | 64.8331 | -0.2864 | -0.013195 | 0.070968 | -0.0077492 | 0.051261 | -0.023017 | -0.012513 | -0.14616 | -0.016524 | 0.040239 | 0.0456 | -0.0039789 | -0.007581 | 64.8239 | -58.0902 | 0.041199 | -58.3511 | 64.7964 | -58.2047 | -58.2642 | -58.1635 | 0.064087 | -58.4518 | 64.8605 | 64.7736 | -58.287 | -58.3237 | -0.041199 | -0.10071 | -0.036621 | 0.073242 | -0.18768 | -0.086975 | -0.009155 | -0.1236 | -0.16022 | 0.027466 | 0 | -0.28839 | -0.12817 | -0.059509 | 122.9599 | 122.9874 | 58.2047 | -123.0972 | 123.024 | 122.937 | 58.2275 | -123.1567
287.6406 | 123.2803 | -58.1451 | 64.7827 | 0.00352 | -0.015331 | 0.08699 | -0.0077492 | 0.060874 | -0.025153 | -0.018922 | 0.036941 | -0.015456 | 0.047715 | 0.043464 | -0.0061159 | 0.00844 | 64.8834 | -58.0078 | 0.07782 | -58.3374 | 64.8148 | -58.2047 | -58.2321 | -58.0444 | 0.18768 | -58.3237 | 64.8193 | 64.7186 | -58.2367 | -58.3145 | -0.059509 | -0.086975 | 0.032043 | 0.13733 | -0.19226 | -0.10528 | 0.10071 | -0.091552 | -0.16937 | 0.036621 | 0.10071 | -0.17853 | -0.009155 | -0.064087 | 122.9599 | 123.0286 | 58.223 | -123.0148 | 122.9645 | 122.8638 | 58.3328 | -123.0972
288.7031 | 123.1934 | -58.1863 | 64.801 | -0.16433 | -0.016399 | 0.0699 | 0.023226 | 0.053397 | -0.0037909 | -0.01465 | -0.13091 | -0.011183 | 0.042375 | 0.050941 | -0.0029109 | -0.019331 | 64.8468 | -58.0399 | 0.07782 | -58.3466 | 64.7827 | -58.2138 | -58.2504 | -58.1131 | 0.14648 | -58.4015 | 64.8468 | 64.7552 | -58.2687 | -58.3145 | -0.027466 | -0.064087 | -0.01831 | 0.14648 | -0.16022 | -0.096131 | 0.045777 | -0.082398 | -0.12817 | 0.045777 | 0.073242 | -0.21515 | -0.086975 | -0.045776 | 122.9691 | 123.0331 | 58.2642 | -123.0515 | 123.0331 | 122.9416 | 58.3328 | -123.1155
289.6406 | 123.2254 | -58.1726 | 64.7736 | 0.56809 | 0.018849 | 0.063492 | 0.0039998 | 0.065146 | -0.0048589 | -0.015718 | 0.571 | -0.0090474 | 0.054124 | 0.057349 | 0.0056341 | -0.00010499 | 64.8148 | -58.0856 | -0.018311 | -58.4061 | 64.7781 | -58.2458 | -58.3054 | -58.1314 | 0.022888 | -58.4427 | 64.7919 | 64.682 | -58.2596 | -58.3786 | -0.073243 | -0.13275 | 0.004577 | 0.086975 | -0.23346 | -0.10071 | 0.041198 | -0.086976 | -0.20599 | 0.01831 | 0.041198 | -0.27008 | -0.064087 | -0.091553 | 122.9507 | 122.9874 | 58.1543 | -123.0789 | 122.9645 | 122.8546 | 58.1955 | -123.1522
290.7031 | 123.1155 | -58.2047 | 64.8239 | 0.29344 | -0.0099898 | 0.072037 | 0.00079576 | 0.065146 | 0.0058221 | -0.017854 | -0.23772 | -0.00050244 | 0.047715 | 0.053077 | -0.0093199 | -0.012922 | 64.7964 | -58.1451 | -0.027466 | -58.4198 | 64.8514 | -58.2184 | -58.2916 | -58.1772 | 0.059509 | -58.5022 | 64.8834 | 64.7919 | -58.2825 | -58.3374 | -0.013733 | -0.086975 | 0.027465 | 0.059509 | -0.21515 | -0.12817 | -0.027466 | -0.07782 | -0.13275 | 0.059509 | 0.027466 | -0.29755 | -0.1648 | -0.032044 | 123.056 | 123.0011 | 58.1772 | -123.1155 | 123.0881 | 122.9965 | 58.2642 | -123.1613
291.6406 | 123.2346 | -58.1909 | 64.7644 | 0.58335 | 0.016713 | 0.068832 | 0.010409 | 0.055533 | 0.015435 | -0.0061053 | 0.46419 | -0.0079794 | 0.065873 | 0.054145 | 0.015247 | -0.009718 | 64.7919 | -58.1635 | -0.086975 | -58.4244 | 64.801 | -58.2642 | -58.3008 | -58.1223 | 0 | -58.461 | 64.7964 | 64.7095 | -58.2825 | -58.3557 | -0.073242 | -0.10986 | 0.036621 | 0.027466 | -0.23346 | -0.1236 | 0.027466 | -0.091553 | -0.16479 | 0.032044 | 0.068665 | -0.27008 | -0.10529 | -0.054931 | 122.9919 | 122.9828 | 58.1039 | -123.0652 | 122.9874 | 122.9004 | 58.1909 | -123.1201
292.7031 | 123.1338 | -58.2413 | 64.7736 | 0.26292 | 0.020985 | 0.063492 | 0.024295 | 0.066214 | 0.017572 | -0.00076433 | 0.37263 | -0.0090474 | 0.076554 | 0.059485 | -0.0018429 | -0.015058 | 64.7507 | -58.2458 | -0.15106 | -58.4702 | 64.8193 | -58.2733 | -58.3282 | -58.223 | -0.073242 | -58.5526 | 64.8468 | 64.7415 | -58.287 | -58.3878 | -0.032043 | -0.086975 | 0.045776 | -0.004578 | -0.22888 | -0.14191 | -0.022889 | -0.045776 | -0.14648 | 0.073242 | 0.018311 | -0.31128 | -0.16479 | -0.032044 | 123.0606 | 122.9919 | 58.0902 | -123.1018 | 123.0881 | 122.9828 | 58.168 | -123.1613
293.6406 | 123.2025 | -58.1863 | 64.7507 | 0.50706 | -0.013195 | 0.079513 | 0.0039998 | 0.060874 | -0.014472 | -0.0093093 | 0.64729 | -0.01866 | 0.047715 | 0.056281 | 0.0013611 | -0.001173 | 64.8239 | -58.0994 | -0.032043 | -58.3923 | 64.7507 | -58.223 | -58.2779 | -58.1406 | 0.036621 | -58.4335 | 64.7919 | 64.7049 | -58.2642 | -58.3603 | -0.036621 | -0.091553 | 0 | 0.086975 | -0.20599 | -0.11444 | 0.073243 | -0.07782 | -0.17395 | 0.041199 | 0.045776 | -0.24719 | -0.073242 | -0.045776 | 122.937 | 123.0103 | 58.1543 | -123.0286 | 122.9782 | 122.8912 | 58.223 | -123.111
294.7031 | 123.2529 | -58.1406 | 64.7644 | -0.10329 | -0.018535 | 0.08165 | 0.00079576 | 0.052329 | -0.020881 | -0.018922 | 0.0522 | -0.016524 | 0.048783 | 0.052009 | -0.0050469 | -0.004377 | 64.8972 | -58.0032 | 0.068665 | -58.342 | 64.7781 | -58.2092 | -58.2367 | -58.0399 | 0.18768 | -58.342 | 64.8331 | 64.7324 | -58.2413 | -58.2962 | -0.068665 | -0.09613 | 0.013733 | 0.13733 | -0.20142 | -0.10529 | 0.13275 | -0.10071 | -0.15564 | 0.068665 | 0.10071 | -0.20142 | -0.045776 | -0.032043 | 122.9187 | 123.0377 | 58.2092 | -123.0011 | 122.9736 | 122.8729 | 58.3282 | -123.0606
295.6406 | 123.2162 | -58.1955 | 64.7461 | 0.58335 | 0.02953 | 0.067764 | 0.0093408 | 0.065146 | 0.014367 | -0.011445 | 0.4947 | -0.0047754 | 0.05092 | 0.074439 | 0.0077701 | -0.012922 | 64.801 | -58.168 | -0.10986 | -58.4518 | 64.7781 | -58.2367 | -58.3008 | -58.1314 | -0.027466 | -58.461 | 64.8285 | 64.7049 | -58.2825 | -58.342 | -0.041198 | -0.10529 | 0.032043 | 0.027466 | -0.25635 | -0.15106 | 0.054931 | -0.086975 | -0.14648 | 0.082397 | 0.064087 | -0.2655 | -0.11902 | -0.041199 | 122.9736 | 122.9965 | 58.0856 | -123.0469 | 123.024 | 122.9004 | 58.168 | -123.0881
296.6406 | 123.1293 | -58.2184 | 64.7781 | 0.50706 | 0.017781 | 0.062424 | 0.03284 | 0.056601 | 0.014367 | -0.0018323 | 1.4713 | -0.0069114 | 0.061601 | 0.047736 | 0.0077701 | -0.00865 | 64.7827 | -58.223 | -0.13733 | -58.4427 | 64.8376 | -58.2733 | -58.3191 | -58.1909 | -0.027466 | -58.5434 | 64.8376 | 64.7507 | -58.2825 | -58.3694 | -0.054931 | -0.10071 | 0.059509 | -0.004577 | -0.2243 | -0.1236 | 0.004578 | -0.064087 | -0.15106 | 0.059509 | 0.027466 | -0.32501 | -0.17395 | -0.027466 | 123.056 | 123.0011 | 58.0811 | -123.0972 | 123.056 | 122.9691 | 58.1909 | -123.1476
297.7031 | 123.2483 | -58.2367 | 64.7461 | 0.55284 | 0.023121 | 0.070968 | 0.017886 | 0.058738 | 0.0026181 | 0.00030367 | 0.571 | 0.0027016 | 0.061601 | 0.059485 | 0.0067021 | -0.009718 | 64.7827 | -58.2001 | -0.11444 | -58.4335 | 64.801 | -58.2596 | -58.3008 | -58.1635 | -0.013733 | -58.4839 | 64.8285 | 64.7552 | -58.287 | -58.3832 | -0.022889 | -0.064087 | 0.054931 | 0.036621 | -0.19684 | -0.13275 | 0.036621 | -0.050354 | -0.14648 | 0.082397 | 0.073242 | -0.24719 | -0.10071 | 0.009155 | 123.0377 | 123.0194 | 58.1223 | -123.0469 | 123.0652 | 122.9919 | 58.223 | -123.1293
298.6406 | 123.1979 | -58.2047 | 64.7644 | 0.11033 | 0.026326 | 0.060287 | 0.0050688 | 0.060874 | -0.0016549 | 0.0013717 | 0.082718 | 0.0027016 | 0.091508 | 0.055213 | 0.0056341 | -0.011854 | 64.8056 | -58.0811 | 0.009155 | -58.3969 | 64.8376 | -58.223 | -58.3008 | -58.1451 | 0.059509 | -58.4793 | 64.8331 | 64.7781 | -58.255 | -58.3649 | -0.01831 | -0.09613 | 0.073242 | 0.1236 | -0.19226 | -0.096131 | 0.041199 | -0.050354 | -0.16022 | 0.068665 | 0.059509 | -0.27466 | -0.11444 | 0.013733 | 123.0423 | 123.0103 | 58.2138 | -123.0652 | 123.0377 | 122.9828 | 58.2642 | -123.1293
299.7031 | 123.2025 | -58.1909 | 64.7873 | -0.24062 | 0.02419 | 0.074173 | 0.01575 | 0.083304 | -0.00058594 | 0.00030367 | -0.25298 | -0.012251 | 0.064805 | 0.054145 | 0.00029315 | -0.002241 | 64.7964 | -58.1589 | -0.027466 | -58.4061 | 64.8514 | -58.2184 | -58.2779 | -58.1726 | 0.07782 | -58.4656 | 64.8697 | 64.7873 | -58.255 | -58.3328 | -0.027466 | -0.086975 | 0.064087 | 0.032043 | -0.21515 | -0.12817 | 0.009156 | -0.064087 | -0.14191 | 0.082398 | 0.018311 | -0.27466 | -0.13275 | 0 | 123.0423 | 122.9874 | 58.1635 | -123.0652 | 123.0606 | 122.9782 | 58.2687 | -123.1201
300.6406 | 123.1384 | -58.1955 | 64.801 | 0.095073 | 0.028462 | 0.062424 | 0.013613 | 0.070487 | 0.011163 | -0.00076433 | 0.11323 | -0.0047754 | 0.076554 | 0.058417 | 0.015247 | -0.011854 | 64.8148 | -58.1543 | -0.027466 | -58.4152 | 64.8331 | -58.2458 | -58.287 | -58.1818 | 0.009155 | -58.5068 | 64.8193 | 64.7507 | -58.2916 | -58.3786 | -0.050354 | -0.091552 | 0.032044 | 0.041199 | -0.21973 | -0.12817 | 0.013733 | -0.09613 | -0.18311 | 0.018311 | 0.013733 | -0.31128 | -0.12817 | -0.050354 | 123.0286 | 123.0103 | 58.168 | -123.0881 | 123.0148 | 122.9462 | 58.2047 | -123.1796
301.7031 | 123.1247 | -58.2092 | 64.8605 | -0.60683 | 0.0092362 | 0.078445 | 0.013613 | 0.065146 | -0.011268 | -0.0018323 | -0.25298 | -0.01332 | 0.072282 | 0.052009 | -0.0082519 | -0.00865 | 64.7507 | -58.1451 | -0.013733 | -58.4106 | 64.8651 | -58.223 | -58.2916 | -58.168 | 0.059509 | -58.4747 | 64.888 | 64.7964 | -58.287 | -58.3328 | -0.013732 | -0.082397 | 0.004577 | 0.064087 | -0.20142 | -0.11902 | -0.10986 | -0.077819 | -0.1236 | 0.027465 | 0.041199 | -0.2655 | -0.14191 | -0.064087 | 123.0743 | 122.9599 | 58.1955 | -123.1522 | 123.0972 | 123.0057 | 58.2687 | -123.1934
302.6406 | 123.2437 | -58.1726 | 64.7369 | -0.14907 | 0.0017592 | 0.08165 | -0.0066812 | 0.061942 | -0.013404 | -0.0029003 | 0.58626 | -0.011183 | 0.049852 | 0.059485 | 0.0034971 | 0.002032 | 64.8148 | -58.0627 | -0.018311 | -58.3878 | 64.7552 | -58.2092 | -58.2596 | -58.1131 | 0.032043 | -58.4061 | 64.7781 | 64.6957 | -58.2962 | -58.3603 | -0.036622 | -0.086976 | 0.018311 | 0.10986 | -0.21515 | -0.12817 | 0.07782 | -0.1236 | -0.18768 | 0.041199 | 0.059509 | -0.23346 | -0.045776 | -0.041198 | 122.9279 | 122.9874 | 58.1543 | -122.9965 | 122.9507 | 122.8683 | 58.2047 | -123.0972
303.7031 | 123.2803 | -58.1589 | 64.7369 | -0.19484 | -0.020671 | 0.075241 | 0.0029318 | 0.054465 | -0.023017 | -0.0082413 | 0.021682 | -0.016524 | 0.042375 | 0.069098 | -0.0082519 | -0.020399 | 64.8605 | -58.0078 | 0.10529 | -58.342 | 64.8148 | -58.1909 | -58.2504 | -57.9346 | -0.009155 | -58.4885 | 64.8422 | 64.7415 | -58.2321 | -58.3511 | -0.032043 | -0.091552 | 0.07782 | 0.15106 | -0.1831 | -0.091553 | 0.1236 | -0.073242 | -0.19226 | 0.10529 | 0.22431 | -0.32959 | -0.13733 | 0.004578 | 122.9736 | 123.0194 | 58.2642 | -122.9874 | 123.0011 | 122.9004 | 58.1497 | -123.0881
304.6406 | 123.1247 | -58.2367 | 64.769 | 0.32395 | 0.02419 | 0.060287 | 0.02109 | 0.071555 | 0.014367 | 0.00030367 | 0.15901 | -0.0037074 | 0.060533 | 0.060554 | 0.00029315 | -0.015058 | 64.7781 | -58.2138 | -0.10529 | -58.429 | 64.8422 | -58.2825 | -58.2779 | -58.2275 | -0.082397 | -58.5754 | 64.8285 | 64.7186 | -58.3008 | -58.3878 | -0.045777 | -0.041199 | 0.073242 | 0.022888 | -0.19226 | -0.15106 | 0.009155 | -0.064087 | -0.15106 | 0.059509 | 0.009155 | -0.33875 | -0.18768 | -0.050354 | 123.0789 | 123.0148 | 58.1314 | -123.0469 | 123.0652 | 122.9553 | 58.1543 | -123.1567
305.7031 | 123.1705 | -58.1955 | 64.8056 | 0.76646 | -0.00037681 | 0.075241 | 0.01575 | 0.067282 | -0.0027229 | 0.0045757 | -0.23772 | -0.014388 | 0.064805 | 0.063758 | 0.0045661 | -0.017194 | 64.7873 | -58.1589 | -0.027466 | -58.4061 | 64.8514 | -58.2458 | -58.3008 | -58.1772 | 0.068665 | -58.5068 | 64.8788 | 64.8102 | -58.2779 | -58.3557 | -0.050354 | -0.10529 | 0.045776 | 0.036621 | -0.21057 | -0.10529 | -0.018311 | -0.082397 | -0.16022 | 0.073242 | 0.018311 | -0.31128 | -0.15106 | 0.004578 | 123.0469 | 122.9828 | 58.168 | -123.1064 | 123.0743 | 123.0057 | 58.2642 | -123.1613
306.6406 | 123.1659 | -58.2001 | 64.7919 | 0.079814 | 0.017781 | 0.067764 | 0.012545 | 0.059806 | 0.017572 | -0.00076433 | 0.0064239 | 0.00056556 | 0.059465 | 0.065894 | 0.0024291 | -0.012922 | 64.8376 | -58.1223 | -0.045776 | -58.3786 | 64.8376 | -58.2413 | -58.3008 | -58.1406 | 0.068665 | -58.4885 | 64.8468 | 64.7644 | -58.2642 | -58.374 | -0.041199 | -0.10071 | 0.045776 | 0.07782 | -0.17853 | -0.07782 | 0.045776 | -0.064087 | -0.17395 | 0.054932 | 0.059509 | -0.28839 | -0.11444 | -0.027466 | 123.0377 | 123.0377 | 58.1543 | -123.0927 | 123.0469 | 122.9645 | 58.2687 | -123.1659
307.7031 | 123.1659 | -58.1909 | 64.7827 | -0.072774 | 0.030598 | 0.061355 | 0.00079576 | 0.055533 | 0.015435 | -0.00076433 | -0.0088351 | -0.0015704 | 0.085099 | 0.055213 | -0.0018429 | -0.00865 | 64.8148 | -58.1314 | -0.009155 | -58.374 | 64.8468 | -58.2321 | -58.3054 | -58.1497 | 0.091553 | -58.461 | 64.8468 | 64.7598 | -58.2779 | -58.3603 | -0.041199 | -0.11444 | 0.064087 | 0.059509 | -0.1831 | -0.068664 | 0.032043 | -0.086975 | -0.16937 | 0.064087 | 0.041199 | -0.27008 | -0.10071 | -0.022888 | 123.0377 | 123.0057 | 58.1818 | -123.0881 | 123.0377 | 122.9507 | 58.2825 | -123.143
308.6406 | 123.1842 | -58.2001 | 64.7919 | 0.079814 | 0.022053 | 0.06456 | 0.011477 | 0.070487 | 0.0079581 | -0.0018323 | 0.021682 | -0.0090474 | 0.060533 | 0.066962 | 0.0099061 | -0.012922 | 64.8102 | -58.1177 | -0.004578 | -58.3878 | 64.8376 | -58.255 | -58.2779 | -58.2367 | 0.17853 | -58.493 | 64.8605 | 64.7598 | -58.2687 | -58.374 | -0.054932 | -0.07782 | 0.045776 | 0.082397 | -0.18768 | -0.10986 | 0.018311 | -0.068665 | -0.17395 | 0.068665 | -0.036621 | -0.29297 | -0.11902 | -0.032043 | 123.0377 | 123.0103 | 58.1955 | -123.0698 | 123.0606 | 122.9599 | 58.3786 | -123.1659
309.7031 | 123.1613 | -58.2138 | 64.8102 | -0.24062 | 0.0071002 | 0.079513 | 0.0093408 | 0.058738 | -0.0091309 | -0.0071733 | -0.16142 | -0.015456 | 0.063737 | 0.054145 | -0.0018429 | -0.007581 | 64.7552 | -58.1451 | -0.018311 | -58.4198 | 64.8514 | -58.223 | -58.2916 | -58.1772 | 0.07782 | -58.4061 | 64.8972 | 64.8102 | -58.2596 | -58.3282 | -0.009155 | -0.07782 | 0.041198 | 0.068664 | -0.20599 | -0.12817 | -0.054932 | -0.045777 | -0.11444 | 0.086975 | 0.036621 | -0.19226 | -0.07782 | 0 | 123.0652 | 122.9691 | 58.1955 | -123.1018 | 123.111 | 123.024 | 58.2916 | -123.1384
310.6406 | 123.1613 | -58.1909 | 64.7827 | 0.079814 | 0.023121 | 0.076309 | 0.014682 | 0.055533 | 0.0026181 | -0.01465 | -0.085129 | -0.0079794 | 0.069078 | 0.043464 | 0.0013611 | -0.023603 | 64.8056 | -58.1085 | 0 | -58.3878 | 64.8239 | -58.2413 | -58.2962 | -58.1451 | 0.07782 | -58.461 | 64.856 | 64.7552 | -58.2733 | -58.3786 | -0.050354 | -0.10529 | 0.041199 | 0.082397 | -0.19684 | -0.091552 | 0.022888 | -0.082397 | -0.18768 | 0.073242 | 0.045776 | -0.27008 | -0.082398 | -0.027466 | 123.0148 | 122.9965 | 58.1909 | -123.0789 | 123.0469 | 122.9462 | 58.2687 | -123.1613
311.7031 | 123.2895 | -58.1772 | 64.7919 | 0.064555 | 0.0092362 | 0.097671 | 0.0082728 | 0.054465 | -0.033698 | -0.0029003 | -0.11565 | -0.019728 | 0.048783 | 0.053077 | -0.0093199 | -0.003309 | 64.8056 | -58.0307 | 0.054932 | -58.3511 | 64.769 | -58.2001 | -58.255 | -58.0582 | 0.20599 | -58.3237 | 64.8148 | 64.7369 | -58.2275 | -58.3328 | -0.022888 | -0.07782 | -0.022888 | 0.14648 | -0.17395 | -0.09613 | 0.013733 | -0.050354 | -0.15564 | 0.022888 | 0.11902 | -0.14648 | 0.009156 | -0.054932 | 122.9462 | 122.9828 | 58.2321 | -123.0469 | 122.9919 | 122.9141 | 58.3832 | -123.1247
312.6406 | 123.2117 | -58.2047 | 64.7369 | -0.14907 | -0.011058 | 0.066696 | -0.0013402 | 0.055533 | -0.012336 | -0.013582 | 0.66255 | -0.020796 | 0.048783 | 0.054145 | -0.00077485 | 0.00844 | 64.801 | -58.0673 | -0.027466 | -58.3878 | 64.7461 | -58.2321 | -58.2642 | -58.1223 | 0.041199 | -58.4061 | 64.7598 | 64.7095 | -58.2779 | -58.3649 | -0.027466 | -0.059509 | 0.009156 | 0.13733 | -0.18311 | -0.1236 | 0.064087 | -0.073242 | -0.16022 | 0.022889 | 0.082398 | -0.20142 | -0.041199 | -0.027465 | 122.9507 | 123.0057 | 58.1772 | -123.0011 | 122.9645 | 122.9141 | 58.2458 | -123.1018
313.7031 | 123.1064 | -58.2092 | 64.8285 | -0.25588 | -0.0067858 | 0.084854 | 0.014682 | 0.066214 | -0.0027229 | -0.016786 | 0.0064239 | -0.011183 | 0.061601 | 0.061622 | -0.0071839 | -0.01399 | 64.7873 | -58.1314 | 0 | -58.4152 | 64.8331 | -58.2184 | -58.2733 | -58.1772 | 0.068665 | -58.4747 | 64.8743 | 64.7919 | -58.2779 | -58.3374 | -0.009155 | -0.064086 | 0.004578 | 0.07782 | -0.20599 | -0.14191 | -0.041199 | -0.068664 | -0.12817 | 0.045777 | 0.032044 | -0.2655 | -0.13733 | -0.036621 | 123.0423 | 122.9965 | 58.2092 | -123.1018 | 123.0835 | 123.0011 | 58.2779 | -123.1659
314.6406 | 123.1018 | -58.2458 | 64.7736 | 0.18663 | 0.014576 | 0.070968 | 0.018954 | 0.071555 | 0.017572 | -0.0050373 | 0.86092 | -0.00050244 | 0.070146 | 0.056281 | -0.00077485 | -0.007581 | 64.7461 | -58.2092 | -0.086975 | -58.4381 | 64.8422 | -58.2642 | -58.3099 | -58.255 | -0.064087 | -58.5892 | 64.8514 | 64.769 | -58.3099 | -58.4061 | -0.01831 | -0.064087 | 0.068664 | 0.036621 | -0.19226 | -0.12817 | -0.027466 | -0.064087 | -0.16022 | 0.077819 | -0.009155 | -0.34332 | -0.1831 | -0.004578 | 123.0881 | 122.9919 | 58.1589 | -123.0835 | 123.0972 | 123.0148 | 58.1818 | -123.1796
315.7031 | 123.2254 | -58.1543 | 64.7736 | -1.0188 | -0.013195 | 0.066696 | 0.0072048 | 0.051261 | -0.013404 | -0.012513 | -0.06987 | -0.019728 | 0.03917 | 0.061622 | -0.0050469 | -0.004377 | 64.8376 | -58.0353 | 0.064087 | -58.3466 | 64.7964 | -58.2275 | -58.2596 | -58.0994 | 0.17853 | -58.3786 | 64.856 | 64.7598 | -58.2275 | -58.3008 | -0.073242 | -0.10529 | 0.022888 | 0.11902 | -0.19226 | -0.086975 | 0.064086 | -0.073242 | -0.14648 | 0.082397 | 0.054932 | -0.2243 | -0.07782 | -0.013733 | 122.9507 | 122.9919 | 58.2184 | -123.0331 | 123.0103 | 122.9141 | 58.3328 | -123.0743
316.6406 | 123.1476 | -58.223 | 64.7736 | 0.36973 | 0.017781 | 0.070968 | 0.022158 | 0.060874 | 0.017572 | -0.0093093 | 0.26582 | -0.0069114 | 0.074418 | 0.052009 | 0.01311 | -0.006513 | 64.7736 | -58.1863 | -0.07782 | -58.4061 | 64.8376 | -58.2642 | -58.3008 | -58.2047 | -0.013733 | -58.5205 | 64.8834 | 64.7461 | -58.2962 | -58.3832 | -0.041199 | -0.07782 | 0.064086 | 0.036621 | -0.18311 | -0.10529 | 0 | -0.073243 | -0.16022 | 0.10986 | 0.01831 | -0.29755 | -0.13733 | -0.027466 | 123.0606 | 122.9965 | 58.1451 | -123.0743 | 123.1064 | 122.9691 | 58.2092 | -123.1567
317.7031 | 123.1064 | -58.2413 | 64.7873 | 0.2324 | 0.031666 | 0.0699 | 0.022158 | 0.066214 | 0.011163 | -0.0029003 | -0.024094 | -0.01332 | 0.058397 | 0.046668 | 0.0045661 | -0.00865 | 64.7598 | -58.2047 | -0.091553 | -58.4244 | 64.8239 | -58.2504 | -58.2779 | -58.2458 | -0.064087 | -58.5709 | 64.8376 | 64.7736 | -58.3099 | -58.3786 | -0.009155 | -0.036621 | 0.036622 | 0.036621 | -0.1831 | -0.14648 | -0.027465 | -0.068665 | -0.13733 | 0.050354 | -0.004578 | -0.32959 | -0.19226 | -0.013732 | 123.0652 | 123.0011 | 58.1497 | -123.0652 | 123.0789 | 123.0148 | 58.1772 | -123.1659
318.6406 | 123.1796 | -58.2138 | 64.8193 | -0.22536 | 0.018849 | 0.063492 | 0.011477 | 0.061942 | -0.0027229 | -0.0018323 | -0.17668 | -0.00050244 | 0.047715 | 0.041327 | 0.00029315 | -0.010786 | 64.769 | -58.1451 | -0.013733 | -58.4015 | 64.856 | -58.2138 | -58.2733 | -58.168 | 0.082397 | -58.4564 | 64.8605 | 64.7827 | -58.2779 | -58.3511 | 0 | -0.059509 | 0.036621 | 0.068664 | -0.18768 | -0.12817 | -0.050354 | -0.064087 | -0.13733 | 0.041199 | 0.045776 | -0.24262 | -0.10529 | -0.036621 | 123.0698 | 122.9828 | 58.2001 | -123.0927 | 123.0743 | 122.9965 | 58.2962 | -123.1705
319.7031 | 123.1888 | -58.1818 | 64.7919 | -0.14907 | -0.011058 | 0.079513 | -0.0045452 | 0.059806 | -0.018744 | -0.0071733 | -0.06987 | -0.01866 | 0.054124 | 0.041327 | -0.0029109 | -0.015058 | 64.8331 | -58.049 | 0.054932 | -58.3511 | 64.8102 | -58.2138 | -58.2596 | -58.1314 | 0.12817 | -58.3923 | 64.8468 | 64.7736 | -58.2642 | -58.3328 | -0.032043 | -0.07782 | 0.018311 | 0.13275 | -0.16937 | -0.091552 | 0.041199 | -0.082397 | -0.15106 | 0.054932 | 0.050354 | -0.21057 | -0.059509 | -0.01831 | 122.9919 | 123.0148 | 58.2367 | -123.0515 | 123.0286 | 122.9553 | 58.3099 | -123.1247
320.6406 | 123.175 | -58.2092 | 64.7964 | 0.095073 | 0.022053 | 0.068832 | 0.016818 | 0.067282 | 0.0068901 | -0.021058 | -1.3516 | 0.0016336 | 0.080827 | 0.054145 | 0.015247 | -0.012922 | 64.8239 | -58.1085 | -0.013733 | -58.4015 | 64.8422 | -58.2458 | -58.3099 | -58.1589 | 0.064087 | -58.4747 | 64.8422 | 64.7369 | -58.2962 | -58.3832 | -0.036621 | -0.10071 | 0.045776 | 0.10071 | -0.19226 | -0.091552 | 0.027466 | -0.086975 | -0.17395 | 0.045776 | 0.050354 | -0.2655 | -0.091552 | -0.05951 | 123.0515 | 123.0331 | 58.1955 | -123.1064 | 123.0515 | 122.9462 | 58.2733 | -123.1796
321.7031 | 123.1567 | -58.2275 | 64.769 | 1.3921 | 0.022053 | 0.072037 | 0.026431 | 0.051261 | 0.00048206 | -0.0029003 | 0.60152 | -0.016524 | 0.065873 | 0.06803 | 0.0013611 | -0.004377 | 64.7873 | -58.2367 | -0.13733 | -58.4427 | 64.8148 | -58.255 | -58.3191 | -58.2001 | -0.068665 | -58.5159 | 64.8193 | 64.7507 | -58.3008 | -58.3878 | -0.027466 | -0.091553 | 0.045776 | -0.009155 | -0.21515 | -0.1236 | 0.01831 | -0.073242 | -0.16022 | 0.050354 | 0.027466 | -0.28839 | -0.12817 | -0.018311 | 123.0423 | 123.0148 | 58.0902 | -123.0881 | 123.0469 | 122.9782 | 58.1589 | -123.1567
322.6406 | 123.2529 | -58.1818 | 64.7461 | 0.52232 | 0.0092362 | 0.065628 | -0.034452 | 0.050193 | -0.029426 | -0.0082413 | 0.84566 | -0.015456 | 0.041307 | 0.058417 | -0.0018429 | -0.009718 | 64.8788 | -58.0765 | 0.009155 | -58.3328 | 64.7415 | -58.223 | -58.2642 | -58.1039 | 0.054932 | -58.4244 | 64.7873 | 64.7095 | -58.2687 | -58.3466 | -0.041198 | -0.082397 | -0.004578 | 0.10529 | -0.15106 | -0.068665 | 0.13275 | -0.086975 | -0.1648 | 0.041198 | 0.07782 | -0.24261 | -0.077819 | -0.036621 | 122.9233 | 123.0606 | 58.1909 | -123.0103 | 122.9691 | 122.8912 | 58.2367 | -123.0927
323.7031 | 123.1613 | -58.1955 | 64.8056 | -0.2101 | 0.00069119 | 0.080581 | 0.017886 | 0.067282 | -0.014472 | -0.0061053 | 0.082718 | -0.0079794 | 0.054124 | 0.050941 | 0.00029315 | -0.00865 | 64.801 | -58.1268 | 0.004578 | -58.3786 | 64.8331 | -58.223 | -58.2642 | -58.1589 | 0.091553 | -58.4839 | 64.9017 | 64.801 | -58.2642 | -58.3054 | -0.027465 | -0.068664 | 0.027466 | 0.068665 | -0.18311 | -0.11444 | -0.004578 | -0.068664 | -0.10986 | 0.09613 | 0.036621 | -0.28839 | -0.17853 | -0.004578 | 123.0286 | 122.9965 | 58.2001 | -123.0698 | 123.0972 | 122.9965 | 58.287 | -123.111
324.6406 | 123.1659 | -58.2001 | 64.8056 | -0.042256 | 0.035939 | 0.062424 | 0.023226 | 0.065146 | 0.011163 | 0.0045757 | -0.024094 | 0.0091106 | 0.072282 | 0.063758 | 0.0099061 | -0.018263 | 64.8193 | -58.1268 | -0.004578 | -58.3832 | 64.8468 | -58.2321 | -58.287 | -58.1406 | 0.045776 | -58.461 | 64.856 | 64.7324 | -58.3054 | -58.3786 | -0.032044 | -0.086975 | 0.041199 | 0.073242 | -0.18311 | -0.096131 | 0.013733 | -0.10529 | -0.17853 | 0.050354 | 0.059509 | -0.26093 | -0.082398 | -0.073242 | 123.0469 | 123.0194 | 58.1955 | -123.0927 | 123.056 | 122.9324 | 58.2458 | -123.1842
325.7031 | 123.1201 | -58.1772 | 64.8102 | -0.25588 | 0.0017592 | 0.08165 | 0.0082728 | 0.057669 | -0.017676 | -0.017854 | -0.13091 | -0.017592 | 0.054124 | 0.057349 | -0.0050469 | -0.009718 | 64.8102 | -58.0948 | 0.036621 | -58.3694 | 64.8102 | -58.1955 | -58.2458 | -58.1772 | 0.050354 | -58.4244 | 64.8468 | 64.8056 | -58.2367 | -58.3237 | -0.018311 | -0.068665 | 0 | 0.082397 | -0.19226 | -0.1236 | 0 | -0.059509 | -0.14648 | 0.036621 | 0 | -0.24719 | -0.10071 | -0.004578 | 122.9874 | 122.9874 | 58.2138 | -123.056 | 123.024 | 122.9828 | 58.2275 | -123.1338
326.7344 | 123.2162 | -58.1818 | 64.769 | 0.11033 | 0.0038952 | 0.084854 | 0.00079576 | 0.053397 | -0.029426 | -0.016786 | 0.25056 | -0.01332 | 0.057328 | 0.043464 | -0.0061159 | 0.004168 | 64.7827 | -58.0902 | 0.013733 | -58.3786 | 64.801 | -58.2092 | -58.2733 | -58.0902 | 0.09613 | -58.3786 | 64.8148 | 64.7324 | -58.2779 | -58.3282 | -0.027466 | -0.091552 | 0.032043 | 0.091553 | -0.19684 | -0.10529 | 0.013733 | -0.09613 | -0.14648 | 0.045776 | 0.091553 | -0.19684 | -0.050354 | -0.036621 | 122.9828 | 122.9645 | 58.1955 | -123.0423 | 122.9965 | 122.9141 | 58.2779 | -123.0972
327.6875 | 123.2025 | -58.1497 | 64.8102 | -0.27114 | -0.0089218 | 0.073105 | 0.00079576 | 0.060874 | -0.0091309 | -0.015718 | -0.19194 | -0.011183 | 0.058397 | 0.057349 | 0.0024291 | -0.012922 | 64.8376 | -58.0536 | 0.068665 | -58.3649 | 64.8193 | -58.223 | -58.2733 | -58.1223 | 0.14648 | -58.4015 | 64.8514 | 64.7461 | -58.2413 | -58.3374 | -0.073242 | -0.1236 | 0.009155 | 0.09613 | -0.21515 | -0.091553 | 0.027465 | -0.091553 | -0.18768 | 0.041198 | 0.027466 | -0.25177 | -0.064087 | -0.064087 | 122.9691 | 122.9874 | 58.2184 | -123.0835 | 123.0011 | 122.8958 | 58.2962 | -123.1476
328.6406 | 123.1384 | -58.2001 | 64.8056 | 0.15611 | 0.017781 | 0.056015 | 0.02109 | 0.053397 | 0.012231 | -0.0071733 | 0.067459 | -0.015456 | 0.072282 | 0.074439 | 0.0088381 | -0.01399 | 64.8056 | -58.0994 | 0 | -58.3878 | 64.8376 | -58.2413 | -58.2916 | -58.1451 | 0.036621 | -58.4839 | 64.856 | 64.7324 | -58.287 | -58.3694 | -0.041199 | -0.091553 | 0.032043 | 0.10071 | -0.18768 | -0.09613 | 0 | -0.086975 | -0.16937 | 0.050354 | 0.054931 | -0.28381 | -0.11444 | -0.073242 | 123.0377 | 123.0057 | 58.2001 | -123.0972 | 123.056 | 122.9324 | 58.2367 | -123.175
329.6406 | 123.1567 | -58.1909 | 64.7644 | -2.0564 | 0.0038952 | 0.0699 | 0.011477 | 0.057669 | 0.0058221 | -0.010377 | 0.32686 | -0.0047754 | 0.043443 | 0.069098 | 0.0067021 | -0.00865 | 64.7003 | -58.1497 | -0.10529 | -58.4518 | 64.8285 | -58.2825 | -58.2962 | -58.1772 | -0.073242 | -58.5022 | 64.8331 | 64.7278 | -58.2962 | -58.3923 | -0.091553 | -0.10529 | 0.064087 | 0.041199 | -0.26092 | -0.15564 | -0.064087 | -0.10529 | -0.20142 | 0.068665 | 0.013733 | -0.31128 | -0.10986 | -0.036621 | 123.0194 | 122.8912 | 58.0856 | -123.0606 | 123.024 | 122.9187 | 58.1177 | -123.1567
330.6406 | 123.2025 | -58.2092 | 64.8102 | -0.042256 | 0.022053 | 0.065628 | 0.02109 | 0.06301 | 0.0068901 | 0.00030367 | -0.10039 | -0.011183 | 0.053056 | 0.060554 | -0.0039789 | -0.010786 | 64.801 | -58.1039 | -0.009155 | -58.3786 | 64.8285 | -58.2413 | -58.2916 | -58.1497 | 0.07782 | -58.4839 | 64.8468 | 64.7736 | -58.2596 | -58.3878 | -0.032043 | -0.082397 | 0.01831 | 0.10529 | -0.16937 | -0.086975 | -0.009156 | -0.050354 | -0.17853 | 0.036621 | 0.05951 | -0.27466 | -0.096131 | -0.036621 | 123.0377 | 123.0103 | 58.2001 | -123.1018 | 123.056 | 122.9828 | 58.287 | -123.1979
331.6406 | 123.1247 | -58.2184 | 64.7873 | 0.26292 | 0.033803 | 0.08699 | 0.010409 | 0.072623 | 0.0068901 | -0.0018323 | 0.25056 | -0.0090474 | 0.063737 | 0.054145 | 0.0034971 | -0.011854 | 64.7644 | -58.168 | -0.064087 | -58.4198 | 64.8285 | -58.2504 | -58.3008 | -58.2092 | 0.009155 | -58.5297 | 64.856 | 64.7598 | -58.287 | -58.3511 | -0.032043 | -0.082397 | 0.041199 | 0.050354 | -0.20142 | -0.11902 | -0.022888 | -0.068664 | -0.13275 | 0.068665 | 0.009155 | -0.31128 | -0.17853 | -0.027465 | 123.0469 | 122.9828 | 58.1543 | -123.0881 | 123.0743 | 122.9782 | 58.2275 | -123.1384
332.6406 | 123.1659 | -58.2184 | 64.7598 | 0.50706 | 0.0060322 | 0.068832 | -0.034452 | 0.065146 | -0.012336 | -0.0071733 | 0.87617 | -0.0026384 | 0.058397 | 0.060554 | -0.0050469 | -0.004377 | 64.9109 | -58.2596 | -0.14191 | -58.3649 | 64.8376 | -58.255 | -58.3099 | -58.1955 | -0.054932 | -58.5159 | 64.8148 | 64.7461 | -58.2962 | -58.3694 | -0.036621 | -0.091553 | 0.077819 | -0.041199 | -0.14648 | -0.054931 | 0.15106 | -0.07782 | -0.15106 | 0.054931 | 0.022888 | -0.29755 | -0.14648 | -0.013733 | 123.056 | 123.1293 | 58.0765 | -123.0698 | 123.0331 | 122.9645 | 58.1635 | -123.1293
333.6406 | 123.1522 | -58.2047 | 64.7736 | 0.4918 | 0.022053 | 0.062424 | 0.020022 | 0.072623 | -0.0027229 | 0.0024397 | 0.4947 | -0.0026384 | 0.061601 | 0.059485 | -0.0018429 | -0.004377 | 64.444 | -58.0673 | 0.045776 | -58.3923 | 64.7919 | -58.2458 | -58.3282 | -58.1772 | -0.073242 | -58.5434 | 64.8285 | 64.7736 | -58.2779 | -58.3511 | -0.041199 | -0.1236 | 0.01831 | 0.13733 | -0.18768 | -0.064087 | -0.32959 | -0.073242 | -0.14648 | 0.054931 | 0.027466 | -0.33875 | -0.19226 | 0 | 122.9965 | 122.6486 | 58.2504 | -123.1018 | 123.0331 | 122.9782 | 58.1314 | -123.1247
334.6406 | 123.1384 | -58.223 | 64.7507 | 0.55284 | 0.032734 | 0.056015 | 0.026431 | 0.072623 | 0.013299 | 0.00030367 | -1.5805 | -0.00050244 | 0.075486 | 0.056281 | -0.00077485 | -0.005445 | 64.7415 | -58.1085 | -0.28381 | -58.6349 | 64.7461 | -58.3054 | -58.3191 | -58.2047 | -0.07782 | -58.5251 | 64.8422 | 64.7598 | -58.3145 | -58.374 | -0.082398 | -0.096131 | -0.004577 | 0.11444 | -0.41199 | -0.31586 | -0.009155 | -0.091553 | -0.15106 | 0.091553 | 0.01831 | -0.30212 | -0.15106 | 0.009156 | 122.9691 | 122.9645 | 57.9391 | -123.0698 | 123.0652 | 122.9828 | 58.1451 | -123.1247
335.6406 | 123.1338 | -58.1955 | 64.769 | 0.15611 | 0.043416 | 0.066696 | 0.016818 | 0.059806 | 0.016503 | -0.015718 | 0.17427 | -0.0015704 | 0.062669 | 0.070167 | -0.0029109 | -0.007581 | 64.7964 | -58.1589 | -0.050354 | -58.4152 | 64.7964 | -58.255 | -58.2825 | -58.1955 | 0.004578 | -58.5114 | 64.8331 | 64.7873 | -58.2642 | -58.3878 | -0.059509 | -0.086975 | 0.027466 | 0.036621 | -0.21973 | -0.13275 | 0.027466 | -0.068664 | -0.19226 | 0.064087 | 0 | -0.31586 | -0.1236 | 0.01831 | 122.9919 | 122.9919 | 58.1451 | -123.0515 | 123.0286 | 122.9828 | 58.2001 | -123.1567
336.6406 | 123.1705 | -58.223 | 64.7964 | 0.12559 | 0.022053 | 0.063492 | 0.010409 | 0.06301 | 0.011163 | 0.0077807 | 0.20479 | 0.0037696 | 0.055192 | 0.057349 | 0.0056341 | -0.009718 | 64.801 | -58.1543 | -0.045776 | -58.4106 | 64.8285 | -58.2596 | -58.2916 | -58.1863 | -0.004578 | -58.5159 | 64.8468 | 64.7827 | -58.3145 | -58.3923 | -0.036622 | -0.068665 | 0.032043 | 0.068664 | -0.18768 | -0.11902 | 0.004577 | -0.091553 | -0.16937 | 0.050354 | 0.036621 | -0.29297 | -0.1236 | -0.013733 | 123.0515 | 123.024 | 58.1772 | -123.0881 | 123.0698 | 123.0057 | 58.2184 | -123.1888
337.6406 | 123.1705 | -58.2138 | 64.7598 | 0.38499 | 0.01244 | 0.063492 | 0.016818 | 0.060874 | 0.0058221 | -0.0071733 | 0.55574 | -0.0079794 | 0.057328 | 0.064826 | -0.0018429 | -0.005445 | 64.7507 | -58.2092 | -0.10986 | -58.4427 | 64.8239 | -58.255 | -58.3054 | -58.1726 | -0.045776 | -58.4839 | 64.8193 | 64.769 | -58.2733 | -58.3557 | -0.041199 | -0.091553 | 0.064087 | 0.004577 | -0.22888 | -0.13733 | -0.009156 | -0.059509 | -0.14191 | 0.059509 | 0.041199 | -0.27008 | -0.12817 | 0.009155 | 123.0377 | 122.9645 | 58.1039 | -123.0652 | 123.0331 | 122.9828 | 58.168 | -123.1155
338.6406 | 123.0698 | -58.1955 | 64.7873 | 0.52232 | 0.018849 | 0.058151 | 0.013613 | 0.059806 | 0.0015501 | -0.00076433 | 0.44893 | -0.0037074 | 0.070146 | 0.055213 | -0.0018429 | -0.001173 | 64.7324 | -58.223 | -0.12817 | -58.4518 | 64.8148 | -58.2596 | -58.3145 | -58.2047 | -0.10071 | -58.7082 | 64.8193 | 64.7324 | -58.3282 | -58.3969 | -0.064087 | -0.11902 | 0.027466 | -0.027465 | -0.25635 | -0.13733 | -0.054931 | -0.13275 | -0.20142 | 0.032044 | -0.009155 | -0.5127 | -0.31128 | -0.054931 | 123.0103 | 122.9279 | 58.0673 | -123.1018 | 123.0148 | 122.9279 | 58.0948 | -123.1842
339.6406 | 123.1522 | -58.2138 | 64.7781 | 1.3158 | 0.022053 | 0.061355 | 0.027499 | 0.064078 | 0.0058221 | 0.017394 | 0.12849 | 0.0069746 | 0.060533 | 0.041327 | 0.0067021 | -0.00865 | 64.8376 | -58.136 | -0.041199 | -58.4106 | 64.8193 | -58.2275 | -58.2687 | -58.1451 | 0.045776 | -58.4976 | 64.8285 | 64.7644 | -58.2733 | -58.3694 | -0.013733 | -0.054932 | 0.041199 | 0.07782 | -0.19684 | -0.14191 | 0.059509 | -0.059509 | -0.15564 | 0.050354 | 0.068664 | -0.28381 | -0.12817 | -0.013733 | 123.0331 | 123.0515 | 58.1726 | -123.0469 | 123.0423 | 122.9782 | 58.2596 | -123.1476
340.6406 | 123.1659 | -58.2092 | 64.7873 | 0.095073 | 0.032734 | 0.060287 | 0.0082728 | 0.067282 | 0.017572 | -0.011445 | 0.0522 | -0.0058434 | 0.07335 | 0.06803 | -0.0071839 | -0.004377 | 64.65 | -58.0673 | 0 | -58.4152 | 64.8102 | -58.255 | -58.2962 | -58.1589 | 0.054932 | -58.4747 | 64.8468 | 64.7827 | -58.287 | -58.3649 | -0.045776 | -0.086975 | 0.022889 | 0.14191 | -0.20599 | -0.11902 | -0.13733 | -0.077819 | -0.15564 | 0.05951 | 0.050354 | -0.2655 | -0.10986 | -0.004577 | 123.0194 | 122.8592 | 58.2092 | -123.0835 | 123.056 | 122.9919 | 58.2642 | -123.1522
341.6406 | 123.1247 | -58.2367 | 64.7781 | 0.50706 | 0.035939 | 0.045334 | 0.0072048 | 0.050193 | -0.0059269 | -0.0061053 | 0.87617 | -0.0058434 | 0.058397 | 0.053077 | 0.0013611 | -0.005445 | 64.9521 | -58.3099 | -0.15564 | -58.3649 | 64.8148 | -58.2458 | -58.2916 | -58.2047 | -0.068665 | -58.5159 | 64.8514 | 64.7552 | -58.3008 | -58.4015 | -0.009156 | -0.054932 | 0.036621 | -0.073243 | -0.12817 | -0.073242 | 0.17395 | -0.064087 | -0.16479 | 0.073242 | 0.032043 | -0.27924 | -0.11444 | -0.022888 | 123.0515 | 123.1888 | 58.0811 | -123.0698 | 123.0881 | 122.9919 | 58.168 | -123.1796
342.6406 | 123.1659 | -58.2092 | 64.7369 | 0.53758 | 0.023121 | 0.066696 | 0.0093408 | 0.069419 | 0.00048206 | -0.012513 | -1.611 | -0.0090474 | 0.066941 | 0.054145 | -0.0018429 | 0.002032 | 64.7369 | -58.2138 | -0.19226 | -58.6578 | 64.7598 | -58.2916 | -58.3191 | -58.1863 | -0.091553 | -58.5159 | 64.8285 | 64.7736 | -58.3237 | -58.374 | -0.082397 | -0.10986 | 0.022889 | -0.004577 | -0.44861 | -0.33875 | 0 | -0.11444 | -0.16479 | 0.091553 | 0.022889 | -0.3067 | -0.14191 | 0.036622 | 122.9691 | 122.9462 | 58.017 | -123.056 | 123.0377 | 122.9828 | 58.1177 | -123.111
343.6406 | 123.1247 | -58.2184 | 64.7781 | 0.29344 | 0.048756 | 0.066696 | 0.011477 | 0.065146 | 0.013299 | -0.0071733 | 0.41841 | 0.00056556 | 0.062669 | 0.065894 | 0.0077701 | -0.006513 | 64.7415 | -58.223 | -0.10071 | -58.4381 | 64.7964 | -58.2687 | -58.3099 | -58.2413 | -0.086975 | -58.5571 | 64.8651 | 64.7919 | -58.3282 | -58.3786 | -0.050354 | -0.091553 | 0.018311 | -0.004577 | -0.21973 | -0.12817 | -0.036621 | -0.10986 | -0.16022 | 0.086975 | -0.022888 | -0.33875 | -0.17853 | 0.013733 | 123.0148 | 122.9599 | 58.1177 | -123.0881 | 123.0835 | 123.0103 | 58.1314 | -123.1567
344.6406 | 123.1201 | -58.2092 | 64.8102 | 0.52232 | 0.042347 | 0.057083 | 0.0082728 | 0.055533 | -0.0027229 | 0.0024397 | 0.54048 | 0.0016336 | 0.063737 | 0.061622 | 0.0045661 | -0.01399 | 64.7324 | -58.2321 | -0.13275 | -58.461 | 64.8331 | -58.2733 | -58.3054 | -58.223 | -0.073242 | -58.7631 | 64.8102 | 64.7278 | -58.3282 | -58.3878 | -0.064086 | -0.09613 | 0.022888 | -0.022888 | -0.25177 | -0.15564 | -0.07782 | -0.11902 | -0.17853 | 0 | -0.013732 | -0.55389 | -0.37537 | -0.082398 | 123.0423 | 122.9416 | 58.0765 | -123.1155 | 123.0194 | 122.937 | 58.136 | -123.1979
345.7031 | 123.1796 | -58.1497 | 64.7919 | -0.14907 | 0.018849 | 0.065628 | 0.014682 | 0.06301 | -0.00058594 | -0.01999 | -0.085129 | 0.0027016 | 0.046647 | 0.052009 | -0.0061159 | -0.004377 | 64.801 | -58.1177 | -0.009155 | -58.3878 | 64.8239 | -58.2367 | -58.3008 | -58.1589 | 0.091553 | -58.4473 | 64.8514 | 64.8056 | -58.2962 | -58.3832 | -0.086975 | -0.15106 | 0.032044 | 0.032043 | -0.23804 | -0.086975 | 0.009155 | -0.14649 | -0.23346 | 0.059509 | -0.009156 | -0.29755 | -0.064087 | 0.013733 | 122.9736 | 122.9507 | 58.1406 | -123.0927 | 123.0011 | 122.9553 | 58.2413 | -123.175
346.6406 | 123.111 | -58.2413 | 64.7873 | 0.24766 | 0.032734 | 0.060287 | -0.00027224 | 0.073691 | 0.0047541 | -0.0093093 | 0.17427 | -0.0079794 | 0.066941 | 0.059485 | 0.0034971 | 0.007372 | 64.7598 | -58.1818 | -0.064087 | -58.4152 | 64.8331 | -58.2413 | -58.3145 | -58.2184 | -0.027466 | -58.5342 | 64.8376 | 64.7873 | -58.3099 | -58.3832 | 0 | -0.073242 | 0.045777 | 0.059509 | -0.17395 | -0.10071 | -0.027465 | -0.068665 | -0.14191 | 0.050354 | 0.022888 | -0.29297 | -0.15106 | 0 | 123.0743 | 123.0011 | 58.1772 | -123.1018 | 123.0789 | 123.0286 | 58.2138 | -123.1705
347.6406 | 123.1567 | -58.2138 | 64.801 | 0.33921 | 0.030598 | 0.06456 | 0.034976 | 0.065146 | 0.0047541 | 0.0024397 | 0.22005 | -0.0090474 | 0.080827 | 0.056281 | 0.0013611 | -0.004377 | 64.7598 | -58.1772 | -0.073242 | -58.4244 | 64.8056 | -58.2413 | -58.3099 | -58.2047 | -0.004578 | -58.5205 | 64.8422 | 64.7781 | -58.3054 | -58.3786 | -0.027466 | -0.096131 | 0.004578 | 0.036621 | -0.21057 | -0.11444 | -0.041198 | -0.091553 | -0.1648 | 0.041199 | 0.009155 | -0.3067 | -0.14191 | -0.022888 | 123.0194 | 122.9736 | 58.1406 | -123.111 | 123.056 | 122.9919 | 58.2092 | -123.1796
348.6406 | 123.1613 | -58.1955 | 64.7873 | 0.27818 | 0.026326 | 0.078445 | 0.012545 | 0.053397 | 0.0026181 | -0.0029003 | 0.32686 | -0.0069114 | 0.063737 | 0.041327 | 0.0077701 | -0.00865 | 64.7736 | -58.1497 | -0.054932 | -58.4106 | 64.8193 | -58.2596 | -58.2916 | -58.2138 | -0.004578 | -58.5068 | 64.8697 | 64.7873 | -58.2962 | -58.374 | -0.064087 | -0.09613 | 0.032044 | 0.045777 | -0.21515 | -0.11902 | -0.013732 | -0.10071 | -0.17853 | 0.082398 | -0.01831 | -0.31128 | -0.13275 | 0 | 123.0148 | 122.9691 | 58.1406 | -123.0789 | 123.0652 | 122.9828 | 58.1909 | -123.1613
349.6406 | 123.1384 | -58.2138 | 64.7964 | 0.55284 | 0.02419 | 0.075241 | 0.022158 | 0.051261 | 0.00048206 | 0.0067127 | 0.54048 | -0.0047754 | 0.064805 | 0.044532 | 0.0077701 | -0.001173 | 64.7141 | -58.2321 | -0.13275 | -58.4518 | 64.7964 | -58.2596 | -58.3099 | -58.3878 | 0.32044 | -58.4976 | 64.8239 | 64.7736 | -58.3145 | -58.374 | -0.045777 | -0.096131 | 0 | -0.018311 | -0.23804 | -0.14191 | -0.082398 | -0.10071 | -0.16022 | 0.027466 | -0.17395 | -0.28381 | -0.1236 | -0.022888 | 123.0103 | 122.9279 | 58.0811 | -123.1064 | 123.0377 | 122.9874 | 58.5342 | -123.1705
350.6406 | 123.111 | -58.2413 | 64.7781 | 0.18663 | 0.026326 | 0.0699 | 0.0061368 | 0.059806 | 0.010095 | -0.017854 | 0.26582 | -0.012251 | 0.06801 | 0.052009 | -0.00077485 | -0.004377 | 64.7461 | -58.1909 | -0.082397 | -58.4198 | 64.8239 | -58.2504 | -58.3191 | -58.2413 | -0.045776 | -58.548 | 64.8331 | 64.7781 | -58.3008 | -58.3878 | -0.009155 | -0.07782 | 0.045777 | 0.050354 | -0.17853 | -0.10071 | -0.032043 | -0.059509 | -0.14648 | 0.054932 | 0 | -0.3067 | -0.16022 | 0 | 123.0652 | 122.9874 | 58.1589 | -123.0972 | 123.0743 | 123.0194 | 58.1955 | -123.1659
351.6406 | 123.175 | -58.1909 | 64.7736 | 0.17137 | 0.023121 | 0.066696 | 0.0029318 | 0.056601 | 0.0047541 | -0.0029003 | 0.067459 | -0.0079794 | 0.057328 | 0.053077 | 0.00029315 | -0.017194 | 64.9017 | -58.1543 | -0.032043 | -58.3923 | 64.7873 | -58.2184 | -58.287 | -58.168 | 0.045776 | -58.4656 | 64.8605 | 64.7781 | -58.2779 | -58.3649 | -0.027466 | -0.09613 | 0.013732 | 0.036621 | -0.20142 | -0.10529 | 0.12817 | -0.086975 | -0.17395 | 0.086975 | 0.022888 | -0.27466 | -0.10071 | 0.004577 | 122.9782 | 123.0927 | 58.1589 | -123.0606 | 123.0515 | 122.9691 | 58.2367 | -123.1384
352.6406 | 123.175 | -58.168 | 64.7827 | -0.088033 | 0.048756 | 0.068832 | 0.0061368 | 0.065146 | 0.0026181 | -0.012513 | 0.15901 | 0.0016336 | 0.06801 | 0.044532 | -0.0082519 | -0.004377 | 64.801 | -58.136 | -0.009155 | -58.3832 | 64.8148 | -58.2413 | -58.2687 | -58.1314 | 0.086975 | -58.4473 | 64.856 | 64.8148 | -58.2779 | -58.3466 | -0.073242 | -0.10071 | 0.032043 | 0.032044 | -0.21515 | -0.11444 | 0.01831 | -0.10986 | -0.17853 | 0.073242 | 0.036621 | -0.27924 | -0.10071 | 0.032043 | 122.9828 | 122.9691 | 58.1589 | -123.0515 | 123.024 | 122.9828 | 58.255 | -123.1293
353.6406 | 123.1613 | -58.2001 | 64.7964 | 0.095073 | 0.026326 | 0.056015 | 0.025363 | 0.061942 | 0.0026181 | 0.0024397 | 2.6309 | 0.0048376 | 0.058397 | 0.058417 | 0.0077701 | -0.009718 | 64.801 | -58.1268 | -0.004578 | -58.3969 | 64.8239 | -58.2184 | -58.2916 | -58.1406 | 0.059509 | -58.461 | 64.8422 | 64.7964 | -58.3054 | -58.3649 | -0.018311 | -0.091553 | 0.027466 | 0.073242 | -0.19684 | -0.10529 | 0.004577 | -0.10529 | -0.16479 | 0.045776 | 0.059509 | -0.26093 | -0.096131 | 0 | 123.024 | 123.0011 | 58.1955 | -123.0881 | 123.0423 | 122.9965 | 58.2596 | -123.1613
354.6406 | 123.1201 | -58.2047 | 64.7781 | 0.095073 | 0.045552 | 0.068832 | 0.0039998 | 0.061942 | 0.0047541 | -0.0071733 | 0.20479 | -0.014388 | 0.065873 | 0.058417 | 0.0067021 | -0.006513 | 64.7736 | -58.1497 | -0.032043 | -58.4152 | 64.8285 | -58.2458 | -58.287 | -58.1955 | 0.009155 | -58.5205 | 64.8468 | 64.7827 | -58.3008 | -58.3649 | -0.041199 | -0.082397 | 0.050354 | 0.054932 | -0.21057 | -0.12817 | -0.004577 | -0.09613 | -0.16022 | 0.068665 | 0.009155 | -0.31586 | -0.15564 | 0.004578 | 123.0331 | 122.9782 | 58.1726 | -123.0652 | 123.0515 | 122.9874 | 58.2138 | -123.143
355.6406 | 123.23 | -58.1909 | 64.7278 | 0.59861 | 0.014576 | 0.073105 | 0.010409 | 0.065146 | -0.010199 | -0.018922 | 0.571 | -0.016524 | 0.057328 | 0.030646 | 0.0013611 | -0.009718 | 64.8148 | -58.1039 | -0.032043 | -58.3649 | 64.7736 | -58.2458 | -58.3008 | -58.1268 | 0.036621 | -58.3969 | 64.769 | 64.7232 | -58.287 | -58.3603 | -0.054932 | -0.10986 | 0.045777 | 0.086975 | -0.17395 | -0.064087 | 0.086975 | -0.09613 | -0.16937 | 0.041199 | 0.064087 | -0.20599 | -0.036621 | -0.004577 | 122.9645 | 123.0057 | 58.1589 | -123.0286 | 122.9599 | 122.9141 | 58.2275 | -123.0881
356.6406 | 123.1613 | -58.2092 | 64.7827 | 0.73594 | 0.02953 | 0.067764 | 0.02109 | 0.057669 | 0.010095 | -0.0093093 | 0.082718 | -0.0037074 | 0.074418 | 0.053077 | 0.0045661 | -0.007581 | 64.8148 | -58.1497 | -0.027466 | -58.3923 | 64.8285 | -58.2275 | -58.2916 | -58.1772 | 0.027466 | -58.4793 | 64.8376 | 64.7827 | -58.287 | -58.374 | -0.01831 | -0.082397 | 0.045776 | 0.05951 | -0.1831 | -0.10071 | 0.032043 | -0.077819 | -0.16479 | 0.054931 | 0.032044 | -0.27008 | -0.10529 | 0 | 123.0377 | 123.024 | 58.1818 | -123.0743 | 123.0469 | 122.9919 | 58.2367 | -123.1567
357.6406 | 123.111 | -58.223 | 64.7736 | 0.24766 | 0.033803 | 0.065628 | 0.023226 | 0.066214 | 0.0058221 | 0.0045757 | 0.22005 | -0.0069114 | 0.065873 | 0.055213 | 0.0034971 | -0.007581 | 64.7644 | -58.1955 | -0.064087 | -58.429 | 64.8193 | -58.2596 | -58.2825 | -58.2092 | -0.022888 | -58.5342 | 64.8605 | 64.801 | -58.2916 | -58.3694 | -0.036622 | -0.05951 | 0.045776 | 0.027465 | -0.20599 | -0.14648 | -0.009156 | -0.068665 | -0.14649 | 0.086975 | 0.013732 | -0.31128 | -0.16479 | 0.027465 | 123.0423 | 122.9874 | 58.1589 | -123.056 | 123.0835 | 123.024 | 58.2001 | -123.143
358.6406 | 123.1247 | -58.2458 | 64.769 | 0.46128 | 0.033803 | 0.063492 | 0.028567 | 0.056601 | 0.0047541 | 0.00030367 | 0.32686 | -0.011183 | 0.071214 | 0.041327 | 0.0099061 | -0.004377 | 64.7324 | -58.255 | -0.14191 | -58.4473 | 64.8331 | -58.2733 | -58.3099 | -58.223 | -0.09613 | -58.5526 | 64.8285 | 64.801 | -58.3282 | -58.374 | -0.027465 | -0.064087 | 0.064087 | -0.009155 | -0.20142 | -0.13733 | -0.036621 | -0.082397 | -0.12817 | 0.059509 | 0.022889 | -0.3067 | -0.17853 | 0.032043 | 123.0789 | 122.9782 | 58.1039 | -123.0789 | 123.0743 | 123.0469 | 58.1497 | -123.143
359.6406 | 123.1705 | -58.1863 | 64.8148 | 0.049296 | 0.0038952 | 0.0699 | 0.020022 | 0.061942 | -0.00058594 | -0.0050373 | 0.036941 | 0.0016336 | 0.078691 | 0.054145 | 0.0024291 | -0.007581 | 64.8148 | -58.1268 | -0.009155 | -58.3923 | 64.8148 | -58.223 | -58.287 | -58.1863 | 0.07782 | -58.4518 | 64.8102 | 64.7964 | -58.2596 | -58.3603 | -0.036621 | -0.10071 | 0 | 0.059509 | -0.20599 | -0.10529 | 0 | -0.073243 | -0.17395 | -0.004577 | 0 | -0.2655 | -0.091552 | -0.01831 | 123.0011 | 123.0011 | 58.1772 | -123.1018 | 122.9965 | 122.9828 | 58.2642 | -123.175
360.6406 | 123.1659 | -58.2001 | 64.8148 | 0.034038 | 0.023121 | 0.061355 | 0.01575 | 0.057669 | 0.017572 | -0.0093093 | 0.036941 | -0.010115 | 0.055192 | 0.049872 | 0.01311 | -0.003309 | 64.801 | -58.1268 | -0.027466 | -58.3786 | 64.8102 | -58.255 | -58.3054 | -58.1497 | 0.07782 | -58.4518 | 64.856 | 64.7736 | -58.287 | -58.3649 | -0.054932 | -0.10529 | -0.004577 | 0.073242 | -0.17853 | -0.073242 | -0.013733 | -0.086975 | -0.16479 | 0.041199 | 0.050354 | -0.25177 | -0.086975 | -0.041198 | 123.0103 | 123.0011 | 58.1726 | -123.1201 | 123.056 | 122.9736 | 58.2779 | -123.1796
361.6406 | 123.1842 | -58.2092 | 64.7736 | 0.55284 | 0.030598 | 0.060287 | 0.011477 | 0.067282 | 0.017572 | -0.0029003 | 0.44893 | -0.0037074 | 0.06801 | 0.06269 | 0.0013611 | -0.007581 | 64.6774 | -58.2413 | -0.13733 | -58.4656 | 64.8148 | -58.2504 | -58.3099 | -58.2413 | -0.082397 | -58.5388 | 64.8743 | 64.769 | -58.3374 | -58.4381 | -0.041198 | -0.10071 | 0.041198 | -0.032043 | -0.25635 | -0.15564 | -0.096131 | -0.12817 | -0.22888 | 0.10071 | -0.032043 | -0.32959 | -0.10071 | -0.004578 | 123.024 | 122.8867 | 58.0719 | -123.0835 | 123.0835 | 122.9782 | 58.1268 | -123.2117
362.6406 | 123.2117 | -58.2138 | 64.7324 | 0.58335 | 0.026326 | 0.054947 | 0.0050688 | 0.066214 | -0.011268 | -0.0061053 | 0.63203 | -0.012251 | 0.057328 | 0.06269 | 0.0045661 | -0.004377 | 64.7552 | -58.1451 | -0.09613 | -58.4244 | 64.7781 | -58.2321 | -58.3008 | -58.1314 | 0.050354 | -58.4244 | 64.8056 | 64.7552 | -58.2779 | -58.3466 | -0.018311 | -0.086975 | 0.045776 | 0.068664 | -0.21057 | -0.1236 | 0.022888 | -0.064087 | -0.13275 | 0.073242 | 0.082397 | -0.21057 | -0.077819 | 0.022888 | 122.9919 | 122.9691 | 58.1177 | -123.0331 | 123.0194 | 122.9691 | 58.2642 | -123.0789
363.6406 | 123.1338 | -58.2367 | 64.7919 | 0.24766 | 0.038075 | 0.060287 | 0.018954 | 0.051261 | 0.016503 | -0.012513 | 0.18953 | -0.00050244 | 0.055192 | 0.055213 | 0.0045661 | -0.010786 | 64.7827 | -58.1863 | -0.086975 | -58.429 | 64.801 | -58.2367 | -58.2916 | -58.2138 | -0.013733 | -58.5114 | 64.8376 | 64.801 | -58.2733 | -58.3832 | 0 | -0.054932 | 0.009155 | 0.050354 | -0.19226 | -0.13733 | -0.009155 | -0.036621 | -0.14648 | 0.045776 | 0.022888 | -0.27466 | -0.12817 | 0.009155 | 123.0377 | 123.0194 | 58.1497 | -123.0835 | 123.0743 | 123.0377 | 58.223 | -123.175
364.6406 | 123.1293 | -58.2001 | 64.7461 | 0.15611 | 0.035939 | 0.0699 | 0.025363 | 0.057669 | 0.0079581 | -0.0071733 | 0.17427 | -0.0058434 | 0.06801 | 0.034919 | 0.0056341 | -0.01399 | 64.7873 | -58.1451 | -0.050354 | -58.4335 | 64.8148 | -58.2413 | -58.287 | -58.2001 | 0.004578 | -58.5068 | 64.8605 | 64.7827 | -58.3099 | -58.374 | -0.041199 | -0.086975 | 0.068664 | 0.054931 | -0.23346 | -0.14648 | 0.041198 | -0.10986 | -0.17395 | 0.11444 | 0 | -0.3067 | -0.13275 | 0.036621 | 123.0148 | 122.9874 | 58.1497 | -123.0331 | 123.0606 | 122.9828 | 58.2047 | -123.1201
365.6406 | 123.175 | -58.2138 | 64.801 | -0.011739 | 0.035939 | 0.066696 | 0.016818 | 0.051261 | -0.0059269 | -0.0071733 | 0.0064239 | -0.012251 | 0.065873 | 0.055213 | 0.0056341 | -0.01399 | 64.8193 | -58.1268 | -0.013733 | -58.3923 | 64.7964 | -58.2458 | -58.2733 | -58.1497 | 0.068665 | -58.4564 | 64.8651 | 64.769 | -58.3054 | -58.374 | -0.032044 | -0.059509 | -0.004577 | 0.086975 | -0.17853 | -0.11902 | 0.018311 | -0.091553 | -0.16022 | 0.064087 | 0.064087 | -0.24262 | -0.082398 | -0.032043 | 123.0103 | 123.0331 | 58.2001 | -123.0743 | 123.0789 | 122.9828 | 58.2825 | -123.175
366.6406 | 123.1934 | -58.1909 | 64.801 | -0.088033 | -0.0046498 | 0.079513 | 0.013613 | 0.056601 | -0.010199 | -0.013582 | -0.085129 | -0.0058434 | 0.071214 | 0.053077 | -0.00077485 | -0.006513 | 64.769 | -58.1406 | -0.009155 | -58.3786 | 64.8331 | -58.2275 | -58.2779 | -58.1726 | 0.086975 | -58.461 | 64.8697 | 64.8056 | -58.255 | -58.3694 | -0.036621 | -0.086975 | 0.032044 | 0.050354 | -0.18768 | -0.10071 | -0.032043 | -0.064087 | -0.17853 | 0.068665 | 0.018311 | -0.27008 | -0.091553 | 0.004578 | 123.024 | 122.9599 | 58.1818 | -123.0789 | 123.0606 | 122.9965 | 58.2779 | -123.1705
367.6406 | 123.1476 | -58.2367 | 64.7644 | 1.8498 | 0.017781 | 0.083786 | 0.013613 | 0.051261 | -0.010199 | -0.00076433 | 0.55574 | -0.0069114 | 0.049852 | 0.057349 | 0.0088381 | -0.003309 | 64.7736 | -58.2321 | -0.15106 | -58.4564 | 64.8193 | -58.2687 | -58.3145 | -58.2047 | -0.064087 | -58.5297 | 64.8285 | 64.7369 | -58.3099 | -58.3969 | -0.032044 | -0.07782 | 0.054932 | 0.004577 | -0.21973 | -0.14191 | 0.009156 | -0.073243 | -0.16022 | 0.064087 | 0.032043 | -0.29297 | -0.13275 | -0.027466 | 123.056 | 123.0103 | 58.0856 | -123.0789 | 123.0652 | 122.9736 | 58.1726 | -123.1613
368.6406 | 123.1705 | -58.2001 | 64.7644 | 0.018779 | 0.028462 | 0.063492 | 0.0082728 | 0.051261 | 0.011163 | -0.0018323 | 1.1203 | -0.010115 | 0.053056 | 0.058417 | 0.00029315 | -0.018263 | 64.801 | -58.1268 | -0.013733 | -58.4061 | 64.8056 | -58.2458 | -58.3054 | -58.1451 | 0.073242 | -58.4518 | 64.8651 | 64.8148 | -58.2596 | -58.374 | -0.045777 | -0.10529 | 0.041199 | 0.073242 | -0.20599 | -0.10071 | 0.036621 | -0.05951 | -0.17395 | 0.10071 | 0.054931 | -0.25177 | -0.07782 | 0.050354 | 123.0057 | 123.0011 | 58.1863 | -123.0698 | 123.0652 | 123.0148 | 58.2733 | -123.1384
369.6406 | 123.1522 | -58.2275 | 64.7461 | 0.50706 | 0.017781 | 0.075241 | 0.024295 | 0.056601 | 0.0047541 | -0.010377 | -0.40556 | -0.0069114 | 0.085099 | 0.060554 | 0.00029315 | -0.009718 | 64.7186 | -58.223 | -0.091553 | -58.6578 | 64.7644 | -58.2962 | -58.3374 | -58.1909 | -0.10071 | -58.5205 | 64.8422 | 64.7873 | -58.287 | -58.3832 | -0.068665 | -0.10986 | 0.01831 | 0.004578 | -0.4303 | -0.32044 | -0.027466 | -0.059509 | -0.15564 | 0.09613 | 0.036621 | -0.29297 | -0.13733 | 0.041198 | 122.9919 | 122.9462 | 58.136 | -123.0835 | 123.0698 | 123.0148 | 58.1268 | -123.1293
370.6406 | 123.1659 | -58.2001 | 64.801 | 0.064555 | 0.02419 | 0.056015 | 0.024295 | 0.058738 | -0.0027229 | 0.0024397 | -0.054612 | -0.0047754 | 0.066941 | 0.047736 | 0.0013611 | -0.011854 | 64.8102 | -58.1268 | -0.009155 | -58.3969 | 64.8285 | -58.2321 | -58.2733 | -58.1451 | 0.068665 | -58.4976 | 64.8605 | 64.7736 | -58.3237 | -58.3557 | -0.032044 | -0.073242 | 0.027466 | 0.073242 | -0.19684 | -0.1236 | 0.009156 | -0.1236 | -0.15564 | 0.05951 | 0.054931 | -0.29755 | -0.14191 | -0.027465 | 123.0286 | 123.0103 | 58.1909 | -123.0743 | 123.0606 | 122.9736 | 58.2687 | -123.1567
371.6406 | 123.1201 | -58.2275 | 64.7873 | 0.29344 | 0.026326 | 0.062424 | 0.011477 | 0.051261 | 0.0090271 | -0.0071733 | 0.32686 | -0.012251 | 0.061601 | 0.059485 | 0.0077701 | -0.012922 | 64.7369 | -58.2001 | -0.091553 | -58.429 | 64.8285 | -58.2596 | -58.2962 | -58.2275 | -0.041199 | -58.5251 | 64.8285 | 64.7827 | -58.287 | -58.3694 | -0.032044 | -0.068665 | 0.041199 | 0.027466 | -0.20142 | -0.13275 | -0.050354 | -0.059509 | -0.14191 | 0.041199 | 0 | -0.29755 | -0.15564 | -0.004577 | 123.056 | 122.9645 | 58.136 | -123.0835 | 123.056 | 123.0103 | 58.1863 | -123.1567
372.6406 | 123.0972 | -58.255 | 64.7141 | 0.73594 | 0.032734 | 0.063492 | 0.022158 | 0.056601 | 0.0036861 | 0.0024397 | 0.54048 | 0.0048376 | 0.07335 | 0.053077 | 0.0045661 | -0.003309 | 64.7049 | -58.2413 | -0.16022 | -58.461 | 64.8239 | -58.2733 | -58.3099 | -58.2321 | -0.073242 | -58.5526 | 64.8468 | 64.7873 | -58.3282 | -58.3923 | -0.01831 | -0.054932 | 0.10986 | 0.013733 | -0.20599 | -0.15106 | -0.009155 | -0.073242 | -0.13733 | 0.13275 | 0.022888 | -0.29755 | -0.16022 | 0.073242 | 123.0789 | 122.9599 | 58.0948 | -123.024 | 123.1018 | 123.0423 | 58.1818 | -123.1064
373.6406 | 123.1384 | -58.2138 | 64.7598 | 0.33921 | -0.00037681 | 0.06456 | 0.0050688 | 0.061942 | -0.0037909 | -0.0039683 | 0.43367 | -0.00050244 | 0.062669 | 0.052009 | -0.0050469 | 0.002032 | 64.7003 | -58.2001 | -0.10529 | -58.4427 | 64.8193 | -58.255 | -58.3099 | -58.2001 | -0.068665 | -58.5159 | 64.8285 | 64.7827 | -58.3054 | -58.3649 | -0.041199 | -0.096131 | 0.059509 | 0.013733 | -0.22888 | -0.13275 | -0.05951 | -0.091553 | -0.15106 | 0.068664 | 0.013733 | -0.30212 | -0.15106 | 0.022888 | 123.0331 | 122.9141 | 58.1085 | -123.0698 | 123.0423 | 122.9965 | 58.1451 | -123.1247
374.6406 | 123.1384 | -58.1818 | 64.7964 | -0.33217 | 0.023121 | 0.067764 | 0.024295 | 0.060874 | -0.0080629 | -0.022126 | -0.085129 | 0.00056556 | 0.063737 | 0.047736 | 0.0056341 | -0.007581 | 64.7507 | -58.1635 | -0.027466 | -58.4015 | 64.856 | -58.223 | -58.287 | -58.1863 | 0.068665 | -58.4839 | 64.8743 | 64.8285 | -58.2825 | -58.3511 | -0.041198 | -0.10529 | 0.059509 | 0.018311 | -0.21973 | -0.11444 | -0.045777 | -0.10071 | -0.16937 | 0.07782 | -0.004577 | -0.30212 | -0.13275 | 0.032043 | 123.0377 | 122.9324 | 58.1543 | -123.0835 | 123.056 | 123.0103 | 58.2504 | -123.1476
375.6406 | 123.143 | -58.2001 | 64.7736 | 0.17137 | 0.028462 | 0.059219 | 0.017886 | 0.055533 | -0.00058594 | 0.0013717 | 0.2353 | -0.0090474 | 0.071214 | 0.057349 | 0.0067021 | -0.015058 | 64.7736 | -58.136 | -0.036621 | -58.4015 | 64.8239 | -58.2184 | -58.3054 | -58.1955 | 0.004578 | -58.5114 | 64.8376 | 64.8193 | -58.3282 | -58.3694 | -0.018311 | -0.10529 | 0.050354 | 0.064087 | -0.20142 | -0.09613 | 0 | -0.12817 | -0.16937 | 0.064086 | 0.004577 | -0.31128 | -0.14191 | 0.045776 | 123.024 | 122.9736 | 58.1635 | -123.0789 | 123.0377 | 123.0194 | 58.2047 | -123.143
376.6406 | 123.1064 | -58.2047 | 64.801 | 0.12559 | 0.02419 | 0.073105 | 0.020022 | 0.058738 | 0.013299 | -0.0061053 | 0.15901 | -0.0058434 | 0.051988 | 0.063758 | 0.012042 | -0.016126 | 64.7827 | -58.1314 | -0.022888 | -58.4061 | 64.8285 | -58.2413 | -58.2825 | -58.1772 | 0 | -58.4976 | 64.8148 | 64.7919 | -58.2916 | -58.4015 | -0.036621 | -0.07782 | 0.027466 | 0.073242 | -0.20142 | -0.1236 | -0.01831 | -0.086975 | -0.19684 | 0.013733 | 0.027466 | -0.29297 | -0.096131 | -0.009155 | 123.0331 | 122.9874 | 58.1818 | -123.0835 | 123.0194 | 122.9965 | 58.2047 | -123.2025
377.6406 | 123.1155 | -58.2275 | 64.7781 | 0.26292 | 0.042347 | 0.058151 | 0.030703 | 0.064078 | 0.0026181 | 0.0013717 | 0.3116 | -0.010115 | 0.065873 | 0.069098 | 0.0056341 | -0.00865 | 64.7369 | -58.1955 | -0.091553 | -58.4335 | 64.8331 | -58.2413 | -58.3237 | -58.223 | -0.073242 | -58.5388 | 64.8422 | 64.8056 | -58.3099 | -58.3969 | -0.013733 | -0.09613 | 0.054932 | 0.032043 | -0.20599 | -0.10986 | -0.041199 | -0.082398 | -0.16937 | 0.064087 | 0.004578 | -0.31128 | -0.14191 | 0.027466 | 123.0606 | 122.9645 | 58.136 | -123.1018 | 123.0698 | 123.0331 | 58.1543 | -123.175
378.6406 | 123.175 | -58.1955 | 64.7964 | 0.034038 | 0.041279 | 0.067764 | 0.018954 | 0.060874 | -0.0048589 | -0.018922 | 0.0064239 | -0.010115 | 0.063737 | 0.055213 | 0.0034971 | -0.005445 | 64.7964 | -58.1177 | -0.022888 | -58.374 | 64.8331 | -58.2321 | -58.287 | -58.1543 | 0.059509 | -58.4473 | 64.8605 | 64.7873 | -58.287 | -58.3649 | -0.036621 | -0.091552 | 0.036621 | 0.07782 | -0.17853 | -0.086975 | 0 | -0.091552 | -0.16937 | 0.064087 | 0.041199 | -0.25177 | -0.082398 | -0.009156 | 123.0286 | 122.9919 | 58.1726 | -123.0835 | 123.056 | 122.9828 | 58.255 | -123.1613
379.6406 | 123.1018 | -58.2275 | 64.7873 | 0.32395 | 0.041279 | 0.059219 | 0.014682 | 0.058738 | -0.0016549 | -0.010377 | 0.26582 | -0.012251 | 0.069078 | 0.057349 | 0.012042 | -0.001173 | 64.7552 | -58.1772 | -0.073242 | -58.4244 | 64.8239 | -58.2367 | -58.3145 | -58.2321 | -0.045776 | -58.5251 | 64.8468 | 64.8148 | -58.3008 | -58.3832 | -0.009155 | -0.086975 | 0.036622 | 0.050354 | -0.19684 | -0.10986 | -0.032043 | -0.073242 | -0.15564 | 0.05951 | -0.004578 | -0.29755 | -0.14191 | 0.027466 | 123.0515 | 122.9828 | 58.1543 | -123.1018 | 123.0743 | 123.0423 | 58.1818 | -123.1705
380.6406 | 123.1613 | -58.2138 | 64.7919 | -0.16433 | 0.034871 | 0.058151 | 0.017886 | 0.066214 | 0.0047541 | -0.012513 | 0.036941 | -0.01332 | 0.062669 | 0.052009 | 0.0056341 | -0.021467 | 64.8148 | -58.1314 | -0.013733 | -58.3878 | 64.8285 | -58.2321 | -58.2687 | -58.1543 | 0.064087 | -58.4564 | 64.8422 | 64.8056 | -58.2825 | -58.3511 | -0.018311 | -0.054932 | 0.036621 | 0.082397 | -0.17395 | -0.11902 | 0.022888 | -0.068665 | -0.13733 | 0.050354 | 0.059509 | -0.24262 | -0.10529 | 0.013733 | 123.0423 | 123.0286 | 58.2001 | -123.0606 | 123.056 | 123.0194 | 58.2779 | -123.143
381.6406 | 123.1659 | -58.223 | 64.7781 | -0.78994 | -0.0067858 | 0.0699 | 0.0093408 | 0.071555 | -0.0016549 | -0.010377 | 0.47945 | -0.0090474 | 0.065873 | 0.056281 | -0.0039789 | -0.004377 | 64.7049 | -58.1955 | -0.12817 | -58.4335 | 64.8102 | -58.2596 | -58.3191 | -58.2092 | -0.064087 | -58.5114 | 64.8239 | 64.769 | -58.3237 | -58.3878 | -0.036622 | -0.096131 | 0.032044 | 0.027465 | -0.21057 | -0.11444 | -0.073242 | -0.10071 | -0.1648 | 0.045777 | 0.013732 | -0.28839 | -0.1236 | -0.009155 | 123.0331 | 122.9279 | 58.0948 | -123.0972 | 123.0469 | 122.9919 | 58.1589 | -123.1659
382.6406 | 123.1476 | -58.1863 | 64.7873 | 0.26292 | 0.027394 | 0.066696 | 0.017886 | 0.046988 | 0.012231 | -0.0018323 | 0.17427 | -0.0058434 | 0.064805 | 0.052009 | 0.0045661 | -0.005445 | 64.7507 | -58.1863 | -0.086975 | -58.4152 | 64.8102 | -58.255 | -58.3145 | -58.2047 | -0.027466 | -58.5251 | 64.8422 | 64.8193 | -58.2642 | -58.3832 | -0.068665 | -0.12817 | 0.022889 | 0 | -0.22888 | -0.10071 | -0.036621 | -0.07782 | -0.19684 | 0.054932 | -0.018311 | -0.33874 | -0.14191 | 0.032044 | 122.9965 | 122.937 | 58.0994 | -123.1018 | 123.0286 | 123.0057 | 58.1589 | -123.1705
383.6406 | 123.1155 | -58.2413 | 64.7827 | 0.27818 | 0.02953 | 0.056015 | 0.01575 | 0.074759 | -0.0016549 | -0.0082413 | 0.25056 | -0.0037074 | 0.070146 | 0.06803 | 0.0034971 | -0.010786 | 64.7598 | -58.1772 | -0.086975 | -58.429 | 64.8331 | -58.2504 | -58.3145 | -58.2092 | -0.032043 | -58.5251 | 64.8376 | 64.7873 | -58.2779 | -58.3649 | -0.009155 | -0.073242 | 0.050354 | 0.064087 | -0.18768 | -0.11444 | -0.022888 | -0.036621 | -0.1236 | 0.054931 | 0.032043 | -0.28381 | -0.16022 | 0.004577 | 123.0743 | 123.0011 | 58.1543 | -123.0972 | 123.0789 | 123.0286 | 58.2092 | -123.1476
384.6406 | 123.1201 | -58.2184 | 64.7873 | 0.27818 | 0.016713 | 0.072037 | 0.012545 | 0.06301 | -0.0016549 | -0.0093093 | 0.22005 | -0.0037074 | 0.065873 | 0.065894 | 0.0024291 | -0.00865 | 64.7324 | -58.1635 | -0.082397 | -58.4381 | 64.7964 | -58.2321 | -58.3099 | -58.2138 | -0.032043 | -58.5022 | 64.8331 | 64.7873 | -58.3145 | -58.3923 | -0.013733 | -0.091553 | 0.009156 | 0.054932 | -0.21973 | -0.12817 | -0.054931 | -0.09613 | -0.17395 | 0.045777 | 0.004578 | -0.28381 | -0.10986 | 0 | 123.0148 | 122.9507 | 58.136 | -123.0972 | 123.0515 | 123.0057 | 58.1863 | -123.1796
385.6875 | 123.1842 | -58.2001 | 64.8193 | -0.13381 | -0.0014448 | 0.067764 | 0.0050688 | 0.061942 | -0.0048589 | -0.0093093 | -0.14616 | -0.0090474 | 0.060533 | 0.058417 | -0.013592 | -0.019331 | 64.7827 | -58.1589 | -0.022888 | -58.3832 | 64.856 | -58.2184 | -58.2825 | -58.168 | 0.073242 | -58.4656 | 64.8468 | 64.8102 | -58.2779 | -58.3466 | -0.018311 | -0.082398 | 0.036621 | 0.041198 | -0.18311 | -0.10071 | -0.036621 | -0.07782 | -0.14648 | 0.027466 | 0.032043 | -0.2655 | -0.11902 | -0.009155 | 123.056 | 122.9828 | 58.1772 | -123.1018 | 123.0469 | 123.0103 | 58.2733 | -123.1659
386.6406 | 123.1842 | -58.1818 | 64.7964 | 0.21714 | 0.022053 | 0.045334 | 0.014682 | 0.058738 | 0.0090271 | -0.011445 | 0.082718 | -0.0047754 | 0.054124 | 0.046668 | 0.012042 | -0.012922 | 64.7369 | -58.0765 | -0.018311 | -58.3969 | 64.8239 | -58.2504 | -58.287 | -58.1726 | 0.041199 | -58.4839 | 64.8468 | 64.7827 | -58.287 | -58.3649 | -0.068664 | -0.10529 | 0.027466 | 0.10529 | -0.21515 | -0.10986 | -0.05951 | -0.10529 | -0.18311 | 0.050354 | 0.009156 | -0.30212 | -0.11902 | -0.013733 | 123.0057 | 122.9187 | 58.1635 | -123.0835 | 123.0286 | 122.9645 | 58.223 | -123.1613
387.6406 | 123.143 | -58.2458 | 64.7873 | 0.21714 | 0.025258 | 0.062424 | 0.012545 | 0.065146 | -0.0037909 | -0.017854 | 0.32686 | -0.010115 | 0.075486 | 0.063758 | 0.0099061 | 0.002032 | 64.7461 | -58.1863 | -0.086975 | -58.4198 | 64.8193 | -58.2184 | -58.3054 | -58.2367 | -0.059509 | -58.5388 | 64.8331 | 64.7919 | -58.287 | -58.374 | 0.027466 | -0.059509 | 0.032044 | 0.05951 | -0.17395 | -0.11444 | -0.041198 | -0.041198 | -0.12817 | 0.045777 | 0.009156 | -0.29297 | -0.16479 | 0.004578 | 123.0652 | 122.9919 | 58.1589 | -123.0927 | 123.0789 | 123.0377 | 58.1863 | -123.1613
388.6406 | 123.1293 | -58.1955 | 64.7781 | 2.155 | 0.027394 | 0.082718 | 0.014682 | 0.061942 | 0.00048206 | -0.013582 | 0.082718 | -0.011183 | 0.080827 | 0.052009 | -0.0039789 | -0.012922 | 64.7873 | -58.1223 | -0.022888 | -58.3832 | 64.8148 | -58.223 | -58.3145 | -58.1772 | 0.022888 | -58.4656 | 64.8285 | 64.8148 | -58.2733 | -58.3649 | -0.027465 | -0.11902 | 0.036621 | 0.073243 | -0.18768 | -0.068665 | 0.009155 | -0.077819 | -0.16937 | 0.050354 | 0.018311 | -0.27008 | -0.10071 | 0.036621 | 123.0103 | 122.9828 | 58.1726 | -123.0927 | 123.024 | 123.0103 | 58.2184 | -123.143
389.6406 | 123.2483 | -58.1863 | 64.7415 | 0.59861 | 0.015645 | 0.078445 | 0.01575 | 0.059806 | -0.010199 | -0.011445 | 0.41841 | -0.011183 | 0.054124 | 0.053077 | -0.0050469 | -0.004377 | 64.7644 | -58.1223 | -0.064087 | -58.4061 | 64.7736 | -58.2504 | -58.2962 | -58.0948 | 0 | -58.4244 | 64.7781 | 64.7369 | -58.3054 | -58.3649 | -0.064087 | -0.10986 | 0.032044 | 0.064087 | -0.21973 | -0.10986 | 0.022888 | -0.11902 | -0.17853 | 0.036621 | 0.091552 | -0.23804 | -0.059509 | -0.004578 | 122.9599 | 122.9507 | 58.1223 | -123.0377 | 122.9645 | 122.9233 | 58.1863 | -123.1064
390.6406 | 123.1384 | -58.2275 | 64.7919 | 0.29344 | 0.025258 | 0.0699 | 0.02109 | 0.064078 | 0.0068901 | -0.00076433 | 0.2353 | 0.00056556 | 0.064805 | 0.053077 | 0.0013611 | -0.010786 | 64.7644 | -58.1863 | -0.091553 | -58.4244 | 64.8422 | -58.2413 | -58.3145 | -58.2504 | -0.054932 | -58.5388 | 64.856 | 64.7964 | -58.3328 | -58.3832 | -0.013733 | -0.086975 | 0.050354 | 0.041199 | -0.19684 | -0.10986 | -0.027466 | -0.10529 | -0.15564 | 0.064087 | -0.022888 | -0.31128 | -0.15564 | 0.004578 | 123.0698 | 122.9919 | 58.136 | -123.1064 | 123.0835 | 123.024 | 58.1726 | -123.175
391.6406 | 123.0423 | -58.2321 | 64.7873 | 0.47654 | 0.025258 | 0.0699 | 0.0072048 | 0.054465 | 0.0058221 | -0.010377 | 0.58626 | -0.010115 | 0.072282 | 0.072303 | 0.0056341 | -0.009718 | 64.7186 | -58.2184 | -0.15106 | -58.4518 | 64.8239 | -58.2367 | -58.3328 | -58.2138 | -0.091553 | -58.548 | 64.8239 | 64.7415 | -58.3282 | -58.4061 | -0.004577 | -0.10071 | 0.036622 | 0.013733 | -0.21973 | -0.11902 | -0.068664 | -0.09613 | -0.17395 | 0.036622 | 0.018311 | -0.31586 | -0.14191 | -0.045776 | 123.056 | 122.9507 | 58.0811 | -123.1201 | 123.056 | 122.9736 | 58.1406 | -123.1934
392.6406 | 123.0743 | -58.2367 | 64.7644 | 0.44602 | 0.028462 | 0.0699 | 0.018954 | 0.064078 | -0.0027229 | -0.0061053 | 0.52522 | -0.014388 | 0.066941 | 0.06269 | 0.0013611 | -0.012922 | 64.7369 | -58.2367 | -0.15564 | -58.4473 | 64.8056 | -58.2779 | -58.3054 | -58.223 | -0.050354 | -58.7311 | 64.7873 | 64.7278 | -58.342 | -58.3923 | -0.041199 | -0.068665 | 0.041199 | 0 | -0.21057 | -0.14191 | -0.027466 | -0.10529 | -0.15564 | 0.022888 | 0.013733 | -0.49439 | -0.33875 | -0.036621 | 123.0423 | 122.9736 | 58.0811 | -123.0698 | 123.024 | 122.9645 | 58.1863 | -123.1567
393.6406 | 123.2346 | -58.1909 | 64.7278 | 0.55284 | 0.023121 | 0.063492 | 0.0093408 | 0.055533 | 0.0047541 | -0.0082413 | 0.25056 | -0.014388 | 0.059465 | 0.042396 | 0.0088381 | -0.002241 | 64.7964 | -58.1268 | -0.050354 | -58.374 | 64.7964 | -58.2321 | -58.3008 | -58.1451 | 0.004578 | -58.4198 | 64.7827 | 64.7507 | -58.2916 | -58.3557 | -0.041199 | -0.10986 | 0.068665 | 0.064087 | -0.1831 | -0.073242 | 0.068665 | -0.10071 | -0.16479 | 0.054932 | 0.045776 | -0.22888 | -0.064087 | 0.022888 | 122.9874 | 122.9874 | 58.1406 | -123.0286 | 122.9736 | 122.9416 | 58.1955 | -123.0835
394.6406 | 123.1796 | -58.1955 | 64.7415 | 0.33921 | 0.032734 | 0.06456 | 0.025363 | 0.057669 | 0.011163 | -0.0050373 | 0.18953 | 0.0027016 | 0.059465 | 0.061622 | 0.0077701 | -0.018263 | 64.8285 | -58.136 | -0.036621 | -58.3969 | 64.8331 | -58.2458 | -58.2779 | -58.1543 | 0.032043 | -58.493 | 64.8376 | 64.8148 | -58.2825 | -58.4015 | -0.050354 | -0.082397 | 0.091553 | 0.05951 | -0.20142 | -0.11902 | 0.086975 | -0.086975 | -0.20599 | 0.09613 | 0.041199 | -0.29755 | -0.091553 | 0.073242 | 123.0286 | 123.024 | 58.1589 | -123.0194 | 123.0331 | 123.0103 | 58.2275 | -123.143
395.6406 | 123.0789 | -58.2092 | 64.7507 | 0.44602 | 0.019917 | 0.074173 | 0.025363 | 0.06301 | 0.013299 | -0.0082413 | 0.46419 | -0.0058434 | 0.055192 | 0.055213 | -0.0018429 | -0.016126 | 64.7186 | -58.2184 | -0.14648 | -58.4381 | 64.801 | -58.2596 | -58.3054 | -58.2321 | -0.073242 | -58.5388 | 64.8193 | 64.7552 | -58.3328 | -58.4198 | -0.050354 | -0.09613 | 0.050354 | -0.009155 | -0.22888 | -0.13275 | -0.032043 | -0.1236 | -0.21057 | 0.068665 | -0.022888 | -0.32959 | -0.11902 | 0.004578 | 123.0103 | 122.9279 | 58.0627 | -123.056 | 123.0286 | 122.9645 | 58.136 | -123.1705
396.6406 | 123.2071 | -58.2321 | 64.7644 | 0.40025 | 0.038075 | 0.0699 | 0.028567 | 0.065146 | -0.00058594 | -0.0093093 | 0.55574 | -0.012251 | 0.084031 | 0.061622 | -0.0082519 | -0.00865 | 64.6957 | -58.2275 | -0.13275 | -58.4564 | 64.8148 | -58.2504 | -58.3008 | -58.2092 | -0.07782 | -58.5342 | 64.8331 | 64.7736 | -58.3054 | -58.3832 | -0.01831 | -0.068664 | 0.050354 | 0.004578 | -0.2243 | -0.15564 | -0.068664 | -0.073242 | -0.15106 | 0.068665 | 0.022888 | -0.30212 | -0.15106 | 0.009156 | 123.0469 | 122.9279 | 58.0994 | -123.0652 | 123.0652 | 123.0057 | 58.1543 | -123.1476
397.6406 | 123.2071 | -58.1955 | 64.7232 | 0.59861 | -0.0057178 | 0.077377 | 0.0093408 | 0.054465 | -0.019813 | -0.01999 | 0.67781 | -0.0026384 | 0.053056 | 0.056281 | -0.010388 | -0.003309 | 64.7827 | -58.1039 | -0.032043 | -58.3969 | 64.7598 | -58.2092 | -58.2733 | -58.1314 | 0.027466 | -58.4152 | 64.7552 | 64.7598 | -58.2596 | -58.374 | -0.013733 | -0.077819 | 0.036621 | 0.091553 | -0.20142 | -0.1236 | 0.059509 | -0.064087 | -0.17853 | 0.032043 | 0.064087 | -0.21973 | -0.041199 | 0.036621 | 122.9553 | 122.9782 | 58.1635 | -122.9965 | 122.9507 | 122.9553 | 58.223 | -123.0972
398.7031 | 123.1018 | -58.2092 | 64.7919 | -0.24062 | 0.017781 | 0.085922 | 0.016818 | 0.057669 | -0.0037909 | -0.017854 | -0.17668 | -0.022933 | 0.054124 | 0.049872 | -0.0071839 | -0.015058 | 64.7736 | -58.1451 | -0.018311 | -58.4061 | 64.8514 | -58.2321 | -58.2825 | -58.1818 | 0.054932 | -58.4839 | 64.9017 | 64.8239 | -58.287 | -58.342 | -0.022888 | -0.073242 | 0.059509 | 0.064087 | -0.19684 | -0.1236 | -0.01831 | -0.077819 | -0.13275 | 0.10986 | 0.027466 | -0.27466 | -0.14191 | 0.032044 | 123.0606 | 122.9828 | 58.1909 | -123.0743 | 123.111 | 123.0331 | 58.2642 | -123.1338
399.6406 | 123.1293 | -58.2092 | 64.7461 | 1.7278 | 0.034871 | 0.063492 | 0.026431 | 0.048056 | 0.011163 | -0.013582 | 0.571 | -0.015456 | 0.069078 | 0.050941 | 0.0067021 | -0.006513 | 64.7736 | -58.2321 | -0.15106 | -58.4381 | 64.8148 | -58.2504 | -58.3099 | -58.1726 | -0.07782 | -58.5068 | 64.8239 | 64.7461 | -58.3099 | -58.3694 | -0.041198 | -0.10071 | 0.068664 | -0.022888 | -0.22888 | -0.12817 | 0.027466 | -0.10071 | -0.16022 | 0.07782 | 0.036622 | -0.29755 | -0.13733 | 0 | 123.024 | 122.9828 | 58.0582 | -123.056 | 123.0331 | 122.9553 | 58.1314 | -123.1155
400.6406 | 123.1201 | -58.2367 | 64.7873 | 0.079814 | 0.039143 | 0.059219 | 0.020022 | 0.051261 | 0.016503 | -0.0029003 | 0.082718 | -0.0015704 | 0.074418 | 0.072303 | 0.0077701 | -0.016126 | 64.7827 | -58.1635 | -0.09613 | -58.429 | 64.8193 | -58.2504 | -58.3008 | -58.2001 | -0.032043 | -58.5251 | 64.8422 | 64.801 | -58.2962 | -58.4061 | -0.013733 | -0.064087 | 0.032044 | 0.073242 | -0.19226 | -0.12817 | -0.004577 | -0.05951 | -0.16937 | 0.054932 | 0.036621 | -0.28839 | -0.11902 | 0.013733 | 123.056 | 123.0194 | 58.1406 | -123.0881 | 123.0789 | 123.0377 | 58.2047 | -123.1934
401.6406 | 123.1567 | -58.2138 | 64.7873 | 0.52232 | 0.00069119 | 0.060287 | -0.0034762 | 0.056601 | -0.020881 | -0.0018323 | 0.3116 | -0.0015704 | 0.078691 | 0.06269 | -0.010388 | -0.002241 | 64.7232 | -58.1955 | -0.09613 | -58.4335 | 64.8148 | -58.2504 | -58.3145 | -58.1955 | -0.068665 | -58.5251 | 64.8102 | 64.7827 | -58.3054 | -58.3832 | -0.036621 | -0.10071 | 0.027466 | 0.01831 | -0.21973 | -0.11902 | -0.064086 | -0.091553 | -0.16937 | 0.022889 | 0.01831 | -0.31128 | -0.14191 | -0.004577 | 123.0286 | 122.937 | 58.1177 | -123.1018 | 123.024 | 122.9965 | 58.1451 | -123.1705
402.6406 | 123.143 | -58.1955 | 64.7644 | 6.8395 | 0.044484 | 0.067764 | 0.043521 | 0.060874 | 0.0026181 | -0.0082413 | 0.55574 | 0.00056556 | 0.062669 | 0.065894 | 0.0034971 | -0.022535 | 64.8422 | -58.2413 | -0.15106 | -58.4244 | 64.8834 | -58.2367 | -58.2962 | -58.1909 | -0.068665 | -58.5068 | 64.8331 | 64.7919 | -58.3054 | -58.3511 | -0.041198 | -0.10071 | 0.11902 | -0.045776 | -0.22888 | -0.12817 | 0.07782 | -0.10986 | -0.15564 | 0.068665 | 0.004578 | -0.31128 | -0.15564 | 0.027466 | 123.0789 | 123.0377 | 58.0444 | -123.0606 | 123.0286 | 122.9874 | 58.1268 | -123.1155
403.6406 | 123.2162 | -58.2275 | 64.7461 | 0.58335 | 0.015645 | 0.066696 | 0.017886 | 0.055533 | 0.011163 | -0.0029003 | 0.63203 | -0.014388 | 0.061601 | 0.055213 | 0.0013611 | 0.00096301 | 64.7827 | -58.168 | -0.09613 | -58.4244 | 64.801 | -58.2367 | -58.2916 | -58.1406 | 0.009155 | -58.4518 | 64.7781 | 64.7598 | -58.3008 | -58.3511 | -0.009155 | -0.064087 | 0.054931 | 0.059509 | -0.19684 | -0.13275 | 0.036621 | -0.073242 | -0.1236 | 0.032043 | 0.086975 | -0.2243 | -0.10071 | 0.013733 | 123.0286 | 123.0103 | 58.1314 | -123.0377 | 123.0057 | 122.9874 | 58.2367 | -123.0972
404.6406 | 123.1338 | -58.2092 | 64.7598 | 0.44602 | 0.030598 | 0.060287 | -0.010953 | 0.064078 | 0.0026181 | -0.023195 | 0.76936 | -0.0069114 | 0.076554 | 0.06269 | 0.0013611 | -0.011854 | 65.0208 | -58.3054 | -0.19684 | -58.3786 | 64.8239 | -58.2504 | -58.3054 | -58.2092 | -0.050354 | -58.5159 | 64.8331 | 64.769 | -58.3099 | -58.3878 | -0.041198 | -0.09613 | 0.064087 | -0.09613 | -0.16937 | -0.073242 | 0.26093 | -0.10071 | -0.17853 | 0.073242 | 0 | -0.3067 | -0.12817 | 0.009155 | 123.0331 | 123.23 | 58.0124 | -123.0652 | 123.0423 | 122.9782 | 58.1589 | -123.1476
405.6406 | 123.1934 | -58.1955 | 64.7186 | 0.33921 | 0.0038952 | 0.061355 | 0.0082728 | 0.056601 | -0.014472 | -0.021058 | 0.67781 | -0.0058434 | 0.05092 | 0.053077 | -0.0039789 | -0.005445 | 64.8514 | -58.0811 | -0.018311 | -58.3878 | 64.7369 | -58.2138 | -58.2596 | -58.0948 | 0.045776 | -58.4106 | 64.769 | 64.7232 | -58.2687 | -58.3649 | -0.01831 | -0.064087 | 0.01831 | 0.11444 | -0.19226 | -0.12817 | 0.13275 | -0.073242 | -0.16937 | 0.050354 | 0.10071 | -0.21515 | -0.045777 | 0.004578 | 122.9324 | 123.0469 | 58.1772 | -122.9782 | 122.9645 | 122.9187 | 58.2413 | -123.0835
406.6406 | 123.143 | -58.2367 | 64.7552 | 0.52232 | 0.020985 | 0.075241 | 0.010409 | 0.043784 | 0.022912 | -0.016786 | 0.38789 | -0.0058434 | 0.063737 | 0.066962 | 0.0099061 | -0.005445 | 64.975 | -58.223 | -0.16937 | -58.4152 | 64.7919 | -58.2458 | -58.2962 | -58.2184 | -0.054932 | -58.5251 | 64.8651 | 64.7598 | -58.3008 | -58.3511 | -0.009156 | -0.05951 | 0.036621 | 0.013733 | -0.17853 | -0.11902 | 0.21973 | -0.064087 | -0.11444 | 0.10986 | 0.01831 | -0.28839 | -0.17395 | 0.004578 | 123.0286 | 123.2117 | 58.0673 | -123.0515 | 123.1018 | 122.9965 | 58.1818 | -123.1064
407.6406 | 123.2529 | -58.2092 | 64.7415 | -3.094 | 0.0017592 | 0.066696 | 0.011477 | 0.073691 | -0.011268 | -0.025331 | 0.54048 | -0.021865 | 0.05092 | 0.054145 | -0.012524 | -0.009718 | 64.7873 | -58.0582 | 0 | -58.3786 | 64.769 | -58.2184 | -58.2687 | -58.1131 | 0.027466 | -58.4106 | 64.7919 | 64.7324 | -58.2687 | -58.3603 | -0.009155 | -0.059509 | 0.027466 | 0.15106 | -0.16937 | -0.10986 | 0.045776 | -0.059509 | -0.15106 | 0.050354 | 0.096131 | -0.20142 | -0.050354 | -0.009155 | 122.9782 | 122.9965 | 58.2092 | -123.0103 | 123.0011 | 122.9416 | 58.2367 | -123.1018
408.6406 | 123.111 | -58.2458 | 64.7781 | 0.21714 | 0.020985 | 0.065628 | 0.023226 | 0.067282 | 0.014367 | -0.011445 | 0.34212 | -0.011183 | 0.075486 | 0.066962 | 0.01311 | -0.012922 | 64.7324 | -58.2321 | -0.16479 | -58.461 | 64.7919 | -58.2504 | -58.3328 | -58.2413 | -0.086975 | -58.5342 | 64.8376 | 64.7598 | -58.2962 | -58.4015 | -0.004577 | -0.086975 | 0.013733 | 0.013733 | -0.21515 | -0.12817 | -0.045776 | -0.050354 | -0.15564 | 0.059509 | 0.004578 | -0.28839 | -0.13275 | -0.01831 | 123.0377 | 122.9782 | 58.0811 | -123.111 | 123.0835 | 123.0057 | 58.1589 | -123.1796
409.6406 | 123.2391 | -58.1863 | 64.7278 | 0.59861 | 0.026326 | 0.083786 | 0.014682 | 0.069419 | -0.012336 | -0.0093093 | 0.67781 | -0.0090474 | 0.058397 | 0.058417 | 0.0067021 | -0.00865 | 64.8148 | -58.0948 | -0.036621 | -58.3649 | 64.7827 | -58.223 | -58.2916 | -58.1039 | 0.041199 | -58.4106 | 64.7964 | 64.7369 | -58.3054 | -58.342 | -0.036621 | -0.10529 | 0.054932 | 0.091552 | -0.17853 | -0.073242 | 0.086975 | -0.11902 | -0.15564 | 0.068665 | 0.082397 | -0.22431 | -0.068665 | 0.009155 | 122.9691 | 123.0011 | 58.1497 | -123.0194 | 122.9828 | 122.9233 | 58.2275 | -123.0698
410.6406 | 123.2162 | -58.1909 | 64.7278 | 0.55284 | 0.017781 | 0.0699 | 0.0082728 | 0.049125 | -0.013404 | -0.0061053 | 0.52522 | -0.01332 | 0.045579 | 0.047736 | 0.00029315 | -0.00865 | 64.7827 | -58.0261 | 0 | -58.3969 | 64.7507 | -58.2458 | -58.2596 | -58.1085 | 0.041199 | -58.4244 | 64.7736 | 64.7415 | -58.2642 | -58.342 | -0.054932 | -0.068665 | 0.022888 | 0.1648 | -0.20599 | -0.13733 | 0.054932 | -0.073242 | -0.15106 | 0.045777 | 0.082397 | -0.23346 | -0.082397 | 0.013733 | 122.9416 | 122.9736 | 58.1909 | -122.9874 | 122.9645 | 122.9324 | 58.2321 | -123.0698
411.6406 | 123.2666 | -58.1863 | 64.6957 | 0.65965 | 0.014576 | 0.06456 | 0.01575 | 0.058738 | 0.011163 | -0.0082413 | 0.64729 | -0.021865 | 0.05626 | 0.054145 | 0.00029315 | -0.007581 | 64.8285 | -58.0994 | -0.027466 | -58.3694 | 64.7598 | -58.2138 | -58.3054 | -58.0994 | 0.045776 | -58.4106 | 64.7873 | 64.7095 | -58.2733 | -58.3466 | -0.027466 | -0.11902 | 0.064087 | 0.086975 | -0.18311 | -0.064087 | 0.13275 | -0.086975 | -0.16022 | 0.091552 | 0.086975 | -0.22431 | -0.064087 | 0.013733 | 122.9462 | 123.0148 | 58.1589 | -123.0011 | 122.9736 | 122.8958 | 58.2321 | -123.0423
412.6406 | 123.2208 | -58.1772 | 64.7324 | 0.50706 | 0.0060322 | 0.085922 | 0.024295 | 0.057669 | -0.025153 | -0.016786 | 0.54048 | -0.029341 | 0.061601 | 0.058417 | 0.0034971 | -0.011854 | 64.801 | -58.1131 | -0.045776 | -58.4061 | 64.7781 | -58.2275 | -58.2687 | -58.136 | 0.032043 | -58.4564 | 64.7827 | 64.7461 | -58.2825 | -58.3511 | -0.050354 | -0.091553 | 0.045776 | 0.064087 | -0.22888 | -0.13733 | 0.068664 | -0.10529 | -0.17395 | 0.050354 | 0.041199 | -0.27924 | -0.10529 | 0.013733 | 122.9553 | 122.9782 | 58.1314 | -123.0011 | 122.9599 | 122.9233 | 58.2092 | -123.0835
413.6406 | 123.2071 | -58.1909 | 64.7415 | 0.55284 | -0.016399 | 0.08165 | 0.0082728 | 0.058738 | -0.0080629 | -0.015718 | 0.50996 | -0.01332 | 0.053056 | 0.0456 | 0.0013611 | -0.00010499 | 64.8239 | -58.1223 | -0.032043 | -58.4106 | 64.7873 | -58.2504 | -58.287 | -58.1314 | 0.009155 | -58.4427 | 64.7919 | 64.7141 | -58.2596 | -58.3511 | -0.059509 | -0.09613 | 0.045776 | 0.068665 | -0.21973 | -0.1236 | 0.082398 | -0.068665 | -0.16022 | 0.050354 | 0.059509 | -0.25177 | -0.091553 | -0.027466 | 122.9782 | 123.0148 | 58.1589 | -123.0286 | 122.9828 | 122.905 | 58.2001 | -123.0927
414.6406 | 123.2208 | -58.1726 | 64.7278 | -2.7431 | -0.011058 | 0.067764 | 0.0072048 | 0.058738 | -0.0016549 | -0.0061053 | 0.40315 | -0.025069 | 0.061601 | 0.06803 | 0.010974 | -0.016126 | 64.7964 | -58.0536 | 0.004578 | -58.4015 | 64.769 | -58.2092 | -58.2733 | -58.0948 | 0.041199 | -58.4152 | 64.7873 | 64.7324 | -58.2825 | -58.3694 | -0.036622 | -0.10071 | 0.041199 | 0.11902 | -0.22888 | -0.12817 | 0.068665 | -0.10986 | -0.19684 | 0.059509 | 0.077819 | -0.24262 | -0.045776 | 0.004578 | 122.9416 | 122.9691 | 58.1772 | -123.0011 | 122.9599 | 122.905 | 58.2138 | -123.0972
415.6406 | 123.2208 | -58.1955 | 64.7324 | 0.64439 | 0.014576 | 0.062424 | 0.01575 | 0.057669 | 0.012231 | -0.017854 | 0.44893 | -0.014388 | 0.064805 | 0.052009 | 0.016315 | -0.012922 | 64.7781 | -58.1497 | -0.082397 | -58.4198 | 64.7919 | -58.2779 | -58.3054 | -58.1223 | -0.009155 | -58.4427 | 64.7964 | 64.7232 | -58.2779 | -58.3557 | -0.082397 | -0.10986 | 0.059509 | 0.045777 | -0.2243 | -0.11444 | 0.045776 | -0.082397 | -0.16022 | 0.064087 | 0.073243 | -0.24719 | -0.086975 | -0.009155 | 122.9874 | 122.9736 | 58.1131 | -123.0377 | 122.9919 | 122.9187 | 58.1863 | -123.0881
416.6406 | 123.1888 | -58.2184 | 64.7049 | 0.59861 | 0.042347 | 0.067764 | 0.020022 | 0.069419 | 0.011163 | -0.0082413 | 0.46419 | -0.017592 | 0.055192 | 0.044532 | 0.0045661 | -0.00865 | 64.7873 | -58.1497 | -0.086975 | -58.4152 | 64.7919 | -58.2733 | -58.2779 | -58.1268 | -0.004578 | -58.4518 | 64.8056 | 64.7232 | -58.2962 | -58.3603 | -0.054931 | -0.059509 | 0.086975 | 0.068665 | -0.19684 | -0.13733 | 0.082397 | -0.07782 | -0.14191 | 0.10071 | 0.091553 | -0.23346 | -0.091552 | 0.018311 | 123.0103 | 123.0057 | 58.1314 | -122.9828 | 123.024 | 122.9416 | 58.2138 | -123.0652
417.6406 | 123.1155 | -58.1955 | 64.8056 | -1.0188 | 0.01244 | 0.073105 | 0.012545 | 0.06301 | -0.0037909 | -0.023195 | -0.23772 | -0.017592 | 0.042375 | 0.059485 | -0.0029109 | -0.009718 | 64.7964 | -58.1451 | -0.018311 | -58.3969 | 64.8331 | -58.2275 | -58.2916 | -58.1635 | 0.068665 | -58.4793 | 64.8788 | 64.8331 | -58.2825 | -58.3557 | -0.032043 | -0.09613 | 0.027466 | 0.050354 | -0.20142 | -0.10529 | -0.009155 | -0.086975 | -0.16022 | 0.073242 | 0.032044 | -0.28381 | -0.1236 | 0.027466 | 123.0286 | 122.9919 | 58.1772 | -123.0972 | 123.0743 | 123.0286 | 58.2642 | -123.1613
418.6406 | 123.1888 | -58.1818 | 64.7736 | 0.4918 | -0.0014448 | 0.072037 | 0.012545 | 0.056601 | -0.014472 | 0.00030367 | 0.37263 | -0.01866 | 0.05092 | 0.056281 | -0.0093199 | -0.010786 | 64.769 | -58.0902 | -0.032043 | -58.4106 | 64.7827 | -58.2458 | -58.255 | -58.1406 | 0.027466 | -58.4335 | 64.7919 | 64.7415 | -58.2825 | -58.3832 | -0.064087 | -0.073242 | 0.009155 | 0.091553 | -0.22888 | -0.15564 | -0.004578 | -0.10071 | -0.20142 | 0.01831 | 0.041199 | -0.25177 | -0.050354 | -0.032044 | 122.9645 | 122.9507 | 58.1497 | -123.0286 | 122.9736 | 122.9233 | 58.2092 | -123.1567
419.6406 | 123.2208 | -58.1863 | 64.7415 | 0.38499 | -0.011058 | 0.066696 | 0.011477 | 0.048056 | -0.0091309 | -0.0061053 | 0.52522 | -0.011183 | 0.059465 | 0.050941 | -0.0039789 | -0.01399 | 64.8102 | -58.0627 | -0.009155 | -58.4015 | 64.7507 | -58.2458 | -58.2642 | -58.0948 | 0.013733 | -58.4244 | 64.7736 | 64.7232 | -58.2962 | -58.3649 | -0.05951 | -0.07782 | 0.009155 | 0.1236 | -0.21515 | -0.13733 | 0.068665 | -0.10986 | -0.17853 | 0.032044 | 0.091552 | -0.23804 | -0.059509 | -0.01831 | 122.937 | 122.9965 | 58.1772 | -123.0057 | 122.9599 | 122.9095 | 58.2001 | -123.1064
420.6406 | 123.2025 | -58.1909 | 64.7141 | 0.64439 | 0.00069119 | 0.06456 | 0.0093408 | 0.060874 | 0.0026181 | -0.0061053 | -2.4808 | -0.016524 | 0.072282 | 0.049872 | 0.0067021 | -0.017194 | 64.8331 | -58.0673 | -0.013733 | -58.3832 | 64.769 | -58.2321 | -58.3008 | -58.0948 | 0.064087 | -58.3923 | 64.8148 | 64.7278 | -58.2733 | -58.3374 | -0.041199 | -0.10986 | 0.054932 | 0.1236 | -0.19226 | -0.082398 | 0.11902 | -0.082397 | -0.14648 | 0.10071 | 0.09613 | -0.20142 | -0.054932 | 0.013733 | 122.9599 | 123.024 | 58.1772 | -123.0148 | 123.0057 | 122.9187 | 58.255 | -123.0515
421.6406 | 123.1384 | -58.1131 | 64.7552 | -0.17959 | -0.014263 | 0.072037 | -0.0045452 | 0.058738 | -0.011268 | -0.022126 | -0.11565 | -0.019728 | 0.047715 | 0.037055 | -0.0061159 | -0.009718 | 64.9063 | -57.9849 | 0.091553 | -58.3191 | 64.7827 | -58.2092 | -58.2504 | -58.0673 | 0.20142 | -58.3557 | 64.8056 | 64.7507 | -58.2275 | -58.3008 | -0.096131 | -0.13733 | 0.027466 | 0.12817 | -0.20599 | -0.068665 | 0.15106 | -0.11444 | -0.18768 | 0.050354 | 0.045776 | -0.24262 | -0.054932 | -0.004578 | 122.8958 | 123.0194 | 58.2047 | -123.0057 | 122.9187 | 122.8638 | 58.3145 | -123.056
422.6406 | 123.1338 | -58.1863 | 64.7873 | -0.24062 | -0.0025128 | 0.068832 | 0.011477 | 0.059806 | -0.0037909 | -0.015718 | -0.19194 | -0.01332 | 0.055192 | 0.047736 | 0.0024291 | -0.022535 | 64.8056 | -58.1039 | 0 | -58.4015 | 64.856 | -58.2092 | -58.287 | -58.1406 | 0.09613 | -58.4702 | 64.8972 | 64.7919 | -58.3008 | -58.3328 | -0.022889 | -0.10071 | 0.068665 | 0.082397 | -0.21515 | -0.11444 | 0.018311 | -0.11444 | -0.14648 | 0.10986 | 0.045776 | -0.28381 | -0.13733 | 0.004578 | 123.0423 | 122.9919 | 58.1863 | -123.0743 | 123.0835 | 122.9782 | 58.2825 | -123.1201
423.6875 | 123.1338 | -58.2321 | 64.7736 | 0.44602 | 0.0081682 | 0.044266 | 0.0072048 | 0.066214 | 0.0036861 | -0.0082413 | 0.20479 | -0.01332 | 0.053056 | 0.064826 | 0.0034971 | -0.009718 | 64.6545 | -58.0582 | -0.045776 | -58.4335 | 64.8468 | -58.2825 | -58.3191 | -58.1863 | -0.068665 | -58.5022 | 64.8285 | 64.7049 | -58.3191 | -58.3832 | -0.050354 | -0.086975 | 0.073242 | 0.17395 | -0.20142 | -0.11444 | -0.11902 | -0.086975 | -0.15106 | 0.054931 | 0.045777 | -0.27008 | -0.11902 | -0.068665 | 123.0789 | 122.8867 | 58.1863 | -123.0927 | 123.0606 | 122.937 | 58.1635 | -123.1567
424.6406 | 123.2025 | -58.1772 | 64.7598 | 0.46128 | -0.0014448 | 0.075241 | 0.010409 | 0.050193 | -0.020881 | -0.013582 | 0.41841 | -0.012251 | 0.057328 | 0.055213 | -0.012524 | -0.016126 | 64.7964 | -58.1039 | -0.036621 | -58.4061 | 64.7736 | -58.2138 | -58.2916 | -58.1268 | 0.027466 | -58.4335 | 64.7873 | 64.7461 | -58.2779 | -58.342 | -0.036621 | -0.11444 | 0.013733 | 0.073242 | -0.22888 | -0.11444 | 0.036621 | -0.10071 | -0.16479 | 0.027465 | 0.050354 | -0.25635 | -0.091553 | -0.013733 | 122.9507 | 122.9736 | 58.1406 | -123.0515 | 122.9645 | 122.9233 | 58.2047 | -123.1018
425.6406 | 123.2254 | -58.1863 | 64.7598 | 0.43077 | -0.016399 | 0.072037 | 0.02109 | 0.050193 | -0.016608 | -0.015718 | 0.28108 | -0.014388 | 0.049852 | 0.054145 | -0.0061159 | -0.001173 | 64.7827 | -58.0902 | -0.041199 | -58.3786 | 64.7964 | -58.223 | -58.2733 | -58.1177 | 0.022888 | -58.4152 | 64.769 | 64.7232 | -58.255 | -58.3282 | -0.036621 | -0.086975 | 0.036621 | 0.09613 | -0.19226 | -0.10529 | 0.022888 | -0.068665 | -0.14191 | 0.009155 | 0.068664 | -0.22888 | -0.086975 | -0.036621 | 122.9828 | 122.9691 | 58.1451 | -123.0331 | 122.9553 | 122.9095 | 58.2092 | -123.0881
426.6406 | 123.2391 | -58.1543 | 64.7598 | 0.064555 | -0.0035808 | 0.070968 | -0.0034762 | 0.052329 | -0.023017 | -0.0093093 | 0.082718 | -0.0079794 | 0.029557 | 0.039191 | -0.0071839 | -0.016126 | 64.8193 | -58.0536 | 0.009155 | -58.3466 | 64.7873 | -58.2184 | -58.2733 | -58.0673 | 0.13733 | -58.3603 | 64.8193 | 64.7232 | -58.255 | -58.3466 | -0.064087 | -0.11902 | 0.027465 | 0.10071 | -0.19226 | -0.073243 | 0.059509 | -0.10071 | -0.19226 | 0.059509 | 0.086975 | -0.20599 | -0.013733 | -0.036621 | 122.9416 | 122.9736 | 58.1635 | -123.0331 | 122.9736 | 122.8775 | 58.2916 | -123.1064
427.6406 | 123.2025 | -58.2184 | 64.7461 | 0.58335 | 0.023121 | 0.061355 | 0.03284 | 0.061942 | 0.021844 | -0.012513 | 0.41841 | -0.0026384 | 0.064805 | 0.048804 | -0.00077485 | -0.022535 | 64.7964 | -58.1863 | -0.10529 | -58.4381 | 64.8239 | -58.2642 | -58.3282 | -58.1406 | -0.059509 | -58.461 | 64.8239 | 64.7232 | -58.3054 | -58.3694 | -0.045776 | -0.10986 | 0.07782 | 0.032044 | -0.21973 | -0.10986 | 0.050354 | -0.086975 | -0.15106 | 0.07782 | 0.07782 | -0.24262 | -0.091553 | -0.022888 | 123.0423 | 123.0148 | 58.1131 | -123.0743 | 123.0423 | 122.9416 | 58.1589 | -123.1155
428.6406 | 123.2162 | -58.1772 | 64.7644 | 0.47654 | -0.0025128 | 0.068832 | 0.0029318 | 0.061942 | -0.012336 | -0.012513 | 0.571 | -0.012251 | 0.066941 | 0.075507 | -0.00077485 | -0.01399 | 64.8056 | -58.0765 | -0.013733 | -58.4015 | 64.769 | -58.2504 | -58.287 | -58.1039 | 0.022888 | -58.4152 | 64.7919 | 64.7232 | -58.2596 | -58.3511 | -0.073242 | -0.10986 | 0.004578 | 0.10071 | -0.2243 | -0.11444 | 0.041199 | -0.082398 | -0.17395 | 0.027466 | 0.073242 | -0.23804 | -0.064087 | -0.041198 | 122.9462 | 122.9828 | 58.1635 | -123.0515 | 122.9691 | 122.9004 | 58.2001 | -123.1155
429.6406 | 123.262 | -58.1497 | 64.7552 | 0.049296 | -0.019603 | 0.0699 | 0.013613 | 0.054465 | -0.018744 | -0.012513 | -0.14616 | -0.01866 | 0.054124 | 0.059485 | -0.00077485 | -0.010786 | 64.8376 | -58.0261 | 0.050354 | -58.3603 | 64.7964 | -58.1909 | -58.2596 | -58.0261 | 0.16479 | -58.3328 | 64.7964 | 64.7415 | -58.2275 | -58.3145 | -0.041199 | -0.10986 | 0.041199 | 0.1236 | -0.21057 | -0.10071 | 0.082397 | -0.07782 | -0.1648 | 0.041199 | 0.1236 | -0.18311 | -0.018311 | -0.013733 | 122.9462 | 122.9874 | 58.2001 | -123.0148 | 122.9462 | 122.8912 | 58.3145 | -123.0698
430.6406 | 123.2574 | -58.1268 | 64.7598 | 0.11033 | -0.024944 | 0.078445 | 0.00079576 | 0.054465 | -0.014472 | -0.016786 | -0.0088351 | -0.019728 | 0.040239 | 0.046668 | 0.00029315 | -0.002241 | 64.8468 | -58.0032 | 0.050354 | -58.3511 | 64.8056 | -58.2138 | -58.2825 | -58.0215 | 0.20142 | -58.342 | 64.8193 | 64.7003 | -58.2413 | -58.342 | -0.086975 | -0.15564 | 0.045776 | 0.1236 | -0.2243 | -0.068664 | 0.086975 | -0.11444 | -0.21515 | 0.059509 | 0.10529 | -0.21515 | 0 | -0.05951 | 122.9324 | 122.9736 | 58.1772 | -123.0423 | 122.9462 | 122.8271 | 58.3282 | -123.1018
431.6406 | 123.2803 | -58.1406 | 64.7598 | -0.10329 | -0.021739 | 0.073105 | 0.0018638 | 0.055533 | -0.00058594 | -0.016786 | -0.0088351 | -0.029341 | 0.049852 | 0.047736 | -0.0029109 | -0.016126 | 64.8514 | -57.9803 | 0.073242 | -58.3511 | 64.8148 | -58.2001 | -58.2642 | -58.0215 | 0.19684 | -58.3191 | 64.7964 | 64.7003 | -58.2367 | -58.3237 | -0.059509 | -0.1236 | 0.054931 | 0.16022 | -0.21057 | -0.086975 | 0.091552 | -0.09613 | -0.18311 | 0.036621 | 0.11902 | -0.17853 | 0.004577 | -0.05951 | 122.9553 | 122.9919 | 58.2138 | -123.024 | 122.937 | 122.8409 | 58.3374 | -123.0835
432.6406 | 123.2437 | -58.1955 | 64.7415 | 0.56809 | 0.028462 | 0.067764 | 0.01575 | 0.066214 | 0.012231 | -0.010377 | 0.54048 | -0.011183 | 0.061601 | 0.06269 | 0.016315 | -0.024671 | 64.8102 | -58.049 | -0.004578 | -58.374 | 64.7781 | -58.223 | -58.2687 | -58.0673 | 0.045776 | -58.58 | 64.7552 | 64.6271 | -58.3191 | -58.3649 | -0.027465 | -0.073242 | 0.036621 | 0.14648 | -0.17853 | -0.10529 | 0.068665 | -0.1236 | -0.16937 | 0.013733 | 0.12817 | -0.38452 | -0.21515 | -0.11444 | 122.9736 | 123.0057 | 58.1909 | -123.0103 | 122.9507 | 122.8226 | 58.2413 | -123.1064
433.6406 | 123.2254 | -58.2001 | 64.7644 | 0.15611 | 0.010304 | 0.072037 | 0.0029318 | 0.056601 | -0.013404 | -0.016786 | 0.26582 | -0.019728 | 0.053056 | 0.056281 | -0.0071839 | -0.005445 | 64.8193 | -58.049 | 0.009155 | -58.3649 | 64.8102 | -58.223 | -58.2825 | -58.0719 | 0.13275 | -58.3786 | 64.8102 | 64.7369 | -58.2596 | -58.3237 | -0.022888 | -0.082398 | 0.045777 | 0.15106 | -0.16479 | -0.082397 | 0.054932 | -0.05951 | -0.1236 | 0.045777 | 0.12817 | -0.17853 | -0.054932 | -0.027466 | 123.0103 | 123.0194 | 58.2092 | -123.0469 | 123.0103 | 122.937 | 58.3328 | -123.0881
434.6406 | 123.23 | -58.1451 | 64.7461 | 0.12559 | -0.023876 | 0.072037 | 0.013613 | 0.051261 | -0.0080629 | -0.01465 | 0.25056 | -0.025069 | 0.057328 | 0.060554 | 0.0034971 | -0.011854 | 64.8285 | -58.049 | 0.022888 | -58.3694 | 64.7964 | -58.2047 | -58.255 | -58.0536 | 0.091553 | -58.374 | 64.8331 | 64.7095 | -58.255 | -58.3466 | -0.059509 | -0.10986 | 0.050354 | 0.096131 | -0.2243 | -0.11444 | 0.082397 | -0.10986 | -0.20142 | 0.086975 | 0.091553 | -0.22888 | -0.027465 | -0.036621 | 122.9416 | 122.9736 | 58.168 | -123.0011 | 122.9782 | 122.8546 | 58.2367 | -123.0927
435.6406 | 123.2574 | -58.1543 | 64.7552 | 0.12559 | -0.017467 | 0.075241 | 0.0093408 | 0.06301 | -0.0059269 | -0.0071733 | -0.17668 | -0.011183 | 0.046647 | 0.058417 | 0.00029315 | -0.019331 | 64.8834 | -57.962 | 0.10529 | -58.3099 | 64.7827 | -58.2001 | -58.2596 | -58.049 | 0.18768 | -58.3466 | 64.8285 | 64.7049 | -58.2413 | -58.342 | -0.045776 | -0.10529 | 0.027466 | 0.19226 | -0.15564 | -0.050354 | 0.12817 | -0.086975 | -0.18768 | 0.073242 | 0.10529 | -0.19226 | -0.004578 | -0.050354 | 122.937 | 123.0377 | 58.2596 | -123.0148 | 122.9828 | 122.8592 | 58.342 | -123.0972
436.6406 | 123.1247 | -58.2047 | 64.8102 | -0.27114 | -0.0089218 | 0.066696 | 0.025363 | 0.061942 | 0.0047541 | -0.012513 | -0.26824 | -0.01866 | 0.048783 | 0.071235 | 0.012042 | -0.018263 | 64.8331 | -58.0399 | 0.041199 | -58.3694 | 64.8514 | -58.2184 | -58.2825 | -58.1268 | 0.10529 | -58.4198 | 64.8651 | 64.7552 | -58.2962 | -58.3282 | -0.013733 | -0.07782 | 0.041198 | 0.16479 | -0.1648 | -0.086975 | 0.022888 | -0.091553 | -0.1236 | 0.054931 | 0.07782 | -0.21515 | -0.091553 | -0.054932 | 123.056 | 123.0377 | 58.2458 | -123.0927 | 123.0698 | 122.9599 | 58.3099 | -123.1384
437.6562 | 123.23 | -58.1772 | 64.7186 | 0.43077 | 0.035939 | 0.060287 | 0.033908 | 0.061942 | 0.026116 | -0.00076433 | 0.47945 | -0.012251 | 0.065873 | 0.037055 | 0.0056341 | -0.018263 | 64.8285 | -58.0627 | -0.027466 | -58.3786 | 64.7736 | -58.2367 | -58.2962 | -58.0856 | 0.041199 | -58.4106 | 64.7736 | 64.6637 | -58.287 | -58.3557 | -0.059509 | -0.11902 | 0.054932 | 0.11444 | -0.20142 | -0.082397 | 0.10986 | -0.10986 | -0.17853 | 0.054932 | 0.091553 | -0.23346 | -0.054932 | -0.054932 | 122.9507 | 123.0057 | 58.1497 | -123.0148 | 122.9507 | 122.8409 | 58.2184 | -123.0743
438.6406 | 123.23 | -58.1268 | 64.7781 | -0.5458 | -0.028148 | 0.070968 | 0.018954 | 0.061942 | -0.010199 | -0.0061053 | -0.17668 | -0.015456 | 0.046647 | 0.054145 | -0.0018429 | -0.012922 | 64.8834 | -57.9529 | 0.10986 | -58.3282 | 64.8102 | -58.2001 | -58.255 | -58.0627 | 0.20599 | -58.3374 | 64.8102 | 64.7186 | -58.2367 | -58.3054 | -0.073242 | -0.12817 | 0.032044 | 0.17395 | -0.20142 | -0.073242 | 0.10529 | -0.10986 | -0.17853 | 0.032044 | 0.064087 | -0.21057 | -0.032043 | -0.059509 | 122.937 | 123.0103 | 58.2367 | -123.0331 | 122.937 | 122.8455 | 58.3328 | -123.0835
439.6406 | 123.143 | -58.1772 | 64.8102 | -0.43899 | 0.02419 | 0.077377 | 0.023226 | 0.061942 | 0.019708 | -0.01999 | -0.28349 | -0.011183 | 0.045579 | 0.059485 | 0.0088381 | -0.018263 | 64.7827 | -58.1085 | -0.036621 | -58.3969 | 64.8697 | -58.2367 | -58.287 | -58.1451 | 0.07782 | -58.4747 | 64.8926 | 64.7644 | -58.2733 | -58.3557 | -0.059509 | -0.10986 | 0.059509 | 0.068664 | -0.21973 | -0.10986 | -0.027466 | -0.09613 | -0.17853 | 0.082397 | 0.032043 | -0.29755 | -0.11902 | -0.045777 | 123.0469 | 122.9599 | 58.1406 | -123.0972 | 123.0698 | 122.9416 | 58.255 | -123.1659
440.6406 | 123.111 | -58.1955 | 64.8422 | -0.30166 | 0.0017592 | 0.0699 | 0.017886 | 0.058738 | -0.0027229 | -0.011445 | -0.25298 | -0.01332 | 0.049852 | 0.052009 | 0.0013611 | 0.00096301 | 64.7919 | -58.0353 | 0.041199 | -58.3649 | 64.8514 | -58.2092 | -58.2733 | -58.1177 | 0.13733 | -58.4335 | 64.8605 | 64.7598 | -58.2733 | -58.3649 | -0.013733 | -0.077819 | 0.009155 | 0.16022 | -0.16937 | -0.091553 | -0.050354 | -0.077819 | -0.16937 | 0.018311 | 0.07782 | -0.23804 | -0.068665 | -0.082397 | 123.0469 | 122.9874 | 58.2367 | -123.1155 | 123.056 | 122.9553 | 58.3328 | -123.2071
441.6406 | 123.2162 | -58.1863 | 64.7736 | -4.6352 | -0.020671 | 0.057083 | 0.0050688 | 0.048056 | -0.011268 | -0.018922 | -0.37505 | -0.015456 | 0.043443 | 0.06269 | 0.0045661 | -0.003309 | 64.7003 | -57.9437 | 0.10529 | -58.3603 | 64.801 | -58.2047 | -58.2687 | -58.0811 | 0.1831 | -58.3649 | 64.8056 | 64.7232 | -58.2779 | -58.342 | -0.018311 | -0.082398 | 0.027465 | 0.24261 | -0.17395 | -0.091553 | -0.073243 | -0.091553 | -0.15564 | 0.032043 | 0.10529 | -0.17853 | -0.022888 | -0.050354 | 122.9874 | 122.8867 | 58.2916 | -123.0423 | 122.9919 | 122.9095 | 58.3694 | -123.1155
442.6406 | 123.1247 | -58.2047 | 64.7598 | 0.46128 | 0.011372 | 0.065628 | 0.024295 | 0.050193 | 0.014367 | -0.0039683 | -0.74126 | -0.014388 | 0.057328 | 0.052009 | 0.0045661 | -0.015058 | 64.7278 | -58.1772 | -0.15564 | -58.4381 | 64.8285 | -58.2779 | -58.3145 | -58.1085 | -0.11444 | -58.493 | 64.8697 | 64.7232 | -58.3145 | -58.3878 | -0.073242 | -0.10986 | 0.068664 | 0.027466 | -0.23346 | -0.1236 | -0.032044 | -0.10986 | -0.18311 | 0.10986 | 0.09613 | -0.28839 | -0.10529 | -0.036621 | 123.0331 | 122.9324 | 58.049 | -123.0743 | 123.0743 | 122.9279 | 58.0902 | -123.1476
443.6406 | 123.1155 | -58.1772 | 64.801 | -0.2101 | -0.0078538 | 0.061355 | 0.014682 | 0.059806 | -0.0091309 | -0.0050373 | -0.22246 | -0.0090474 | 0.051988 | 0.046668 | -0.0061159 | -0.00865 | 64.801 | -58.0399 | 0.045776 | -58.3694 | 64.8239 | -58.2138 | -58.287 | -58.1589 | 0.10986 | -58.4198 | 64.8697 | 64.7736 | -58.2687 | -58.3878 | -0.036621 | -0.10986 | 0.022889 | 0.13733 | -0.19226 | -0.082398 | 0 | -0.091553 | -0.21057 | 0.068665 | 0.01831 | -0.24262 | -0.032044 | -0.027465 | 123.0011 | 122.9782 | 58.223 | -123.0881 | 123.0469 | 122.9507 | 58.287 | -123.1888
444.6406 | 123.1247 | -58.2001 | 64.7964 | -0.2864 | 0.00069119 | 0.068832 | 0.020022 | 0.06301 | -0.00058594 | -0.0082413 | -0.31401 | -0.0037074 | 0.059465 | 0.047736 | 0.0034971 | -0.012922 | 64.7507 | -58.1268 | -0.022888 | -58.4152 | 64.8605 | -58.2458 | -58.2916 | -58.1818 | 0.082397 | -58.4564 | 64.8972 | 64.7827 | -58.287 | -58.3603 | -0.045777 | -0.091553 | 0.064087 | 0.073242 | -0.21515 | -0.1236 | -0.045777 | -0.086975 | -0.16022 | 0.10071 | 0.01831 | -0.25635 | -0.09613 | -0.013733 | 123.0606 | 122.9507 | 58.1772 | -123.0881 | 123.0972 | 122.9828 | 58.2825 | -123.1567
445.6406 | 123.1659 | -58.1909 | 64.8056 | -0.24062 | 0.0028272 | 0.070968 | 0.010409 | 0.057669 | -0.0069949 | -0.015718 | -0.2072 | -0.011183 | 0.049852 | 0.039191 | 0.0056341 | -0.010786 | 64.8102 | -58.0399 | 0.041199 | -58.3511 | 64.7964 | -58.223 | -58.2642 | -58.136 | 0.13733 | -58.429 | 64.8651 | 64.7644 | -58.2458 | -58.3466 | -0.032043 | -0.073242 | -0.009155 | 0.15106 | -0.16022 | -0.086975 | 0.004578 | -0.054932 | -0.15564 | 0.059509 | 0.054932 | -0.23804 | -0.082397 | -0.041199 | 122.9874 | 123.0011 | 58.2321 | -123.0698 | 123.056 | 122.9553 | 58.3282 | -123.1522
446.7031 | 123.143 | -58.2047 | 64.7964 | 0.46128 | 0.019917 | 0.067764 | 0.01575 | 0.06301 | 0.029321 | -0.0061053 | 0.34212 | -0.0015704 | 0.046647 | 0.056281 | 0.00029315 | -0.021467 | 64.7186 | -58.1818 | -0.1236 | -58.4381 | 64.8376 | -58.255 | -58.3328 | -58.2047 | -0.44403 | -58.3786 | 64.8148 | 64.7232 | -58.3099 | -58.3832 | -0.050354 | -0.12817 | 0.041198 | 0.022888 | -0.23346 | -0.10529 | -0.07782 | -0.10529 | -0.17853 | 0.01831 | 0 | -0.17395 | 0.004578 | -0.073242 | 123.0423 | 122.9233 | 58.0811 | -123.1293 | 123.0194 | 122.9279 | 57.7606 | -123.1796
447.6406 | 123.1659 | -58.1772 | 64.7827 | -0.11855 | -0.00037681 | 0.066696 | 0.028567 | 0.067282 | 0.0058221 | -0.011445 | -0.25298 | -0.0047754 | 0.047715 | 0.040259 | 0.0077701 | -0.012922 | 64.7919 | -58.1039 | -0.022888 | -58.3603 | 64.888 | -58.2367 | -58.2825 | -58.1314 | 0.10071 | -58.4473 | 64.8514 | 64.7873 | -58.2642 | -58.3603 | -0.059509 | -0.10529 | 0.10529 | 0.073242 | -0.18311 | -0.07782 | 0.009155 | -0.086975 | -0.18311 | 0.068664 | 0.045776 | -0.27008 | -0.086975 | 0.004577 | 123.0652 | 122.9691 | 58.1543 | -123.0652 | 123.0286 | 122.9645 | 58.2779 | -123.143
448.6406 | 123.2346 | -58.1451 | 64.7644 | -0.2101 | -0.0067858 | 0.076309 | 0.02109 | 0.049125 | -0.024085 | -0.018922 | 5.3165 | -0.01866 | 0.045579 | 0.057349 | 0.0013611 | -0.005445 | 64.8376 | -57.9987 | 0.10071 | -58.3328 | 64.7873 | -58.2047 | -58.2321 | -58.0902 | 0.21057 | -58.3878 | 64.8239 | 64.7186 | -58.2596 | -58.3145 | -0.059509 | -0.086975 | 0.022888 | 0.14648 | -0.18768 | -0.10071 | 0.073242 | -0.11444 | -0.16937 | 0.05951 | 0.054932 | -0.24261 | -0.073242 | -0.045776 | 122.9324 | 122.9828 | 58.2458 | -122.9965 | 122.9691 | 122.8638 | 58.3557 | -123.0789
449.6406 | 123.175 | -58.1543 | 64.7919 | -0.011739 | -0.0014448 | 0.075241 | 0.010409 | 0.053397 | -0.012336 | -0.016786 | -0.17668 | -0.011183 | 0.060533 | 0.046668 | -0.0018429 | -0.020399 | 64.7964 | -58.0261 | 0.059509 | -58.342 | 64.8239 | -58.2092 | -58.2458 | -58.1406 | 0.14191 | -58.4061 | 64.8514 | 64.7415 | -58.2687 | -58.3557 | -0.054932 | -0.091553 | 0.032044 | 0.12817 | -0.18768 | -0.09613 | 0.004578 | -0.11444 | -0.20142 | 0.059509 | 0.013733 | -0.25177 | -0.050354 | -0.050354 | 122.9782 | 122.9507 | 58.2138 | -123.0377 | 123.0057 | 122.8958 | 58.2962 | -123.1476
450.6406 | 123.2025 | -58.1543 | 64.7827 | -0.30166 | -0.0025128 | 0.0699 | 0.012545 | 0.056601 | -0.0048589 | -0.011445 | -0.17668 | -0.032546 | 0.053056 | 0.056281 | -0.0029109 | -0.005445 | 64.801 | -58.0078 | 0.068665 | -58.3466 | 64.8376 | -58.1955 | -58.2504 | -58.136 | 0.16022 | -58.3969 | 64.8743 | 64.7232 | -58.2733 | -58.3328 | -0.041199 | -0.09613 | 0.054931 | 0.14648 | -0.19226 | -0.096131 | 0.01831 | -0.11902 | -0.17853 | 0.091553 | 0.018311 | -0.24262 | -0.064087 | -0.059509 | 122.9919 | 122.9553 | 58.223 | -123.0331 | 123.0286 | 122.8775 | 58.3145 | -123.1155
451.6875 | 123.1293 | -58.1818 | 64.8193 | -0.22536 | 0.010304 | 0.072037 | 0.011477 | 0.048056 | -0.013404 | -0.018922 | -0.26824 | -0.01332 | 0.069078 | 0.049872 | 0.00029315 | -0.016126 | 64.8193 | -58.1314 | -0.027466 | -58.3878 | 64.8651 | -58.2184 | -58.2779 | -58.1726 | 0.086975 | -58.4702 | 64.888 | 64.7781 | -58.287 | -58.3466 | -0.036621 | -0.09613 | 0.045776 | 0.050354 | -0.20599 | -0.10986 | 0 | -0.10529 | -0.1648 | 0.068664 | 0.009156 | -0.28839 | -0.1236 | -0.041199 | 123.0469 | 123.0011 | 58.1543 | -123.0972 | 123.0698 | 122.9599 | 58.2687 | -123.1659
452.6406 | 123.1018 | -58.1726 | 64.8239 | -0.27114 | 0.010304 | 0.088058 | 0.033908 | 0.044852 | -0.0080629 | -0.0082413 | -0.39031 | -0.011183 | 0.058397 | 0.052009 | 0.0034971 | -0.004377 | 64.7278 | -58.0215 | 0.032043 | -58.4015 | 64.8834 | -58.2184 | -58.2733 | -58.168 | 0.068665 | -58.4702 | 64.888 | 64.7552 | -58.2825 | -58.3603 | -0.045777 | -0.10071 | 0.059509 | 0.15106 | -0.22888 | -0.12817 | -0.096131 | -0.10986 | -0.18768 | 0.064086 | 0.004577 | -0.29755 | -0.10986 | -0.068665 | 123.056 | 122.9004 | 58.2047 | -123.0972 | 123.0606 | 122.9279 | 58.2413 | -123.1842
453.6406 | 123.1888 | -58.1589 | 64.8148 | 0.049296 | -0.0014448 | 0.070968 | 0.0072048 | 0.060874 | -0.013404 | -0.016786 | -0.19194 | -0.014388 | 0.064805 | 0.057349 | -0.0093199 | -0.004377 | 64.8285 | -58.0261 | 0.07782 | -58.3282 | 64.8148 | -58.2001 | -58.2733 | -58.1131 | 0.16022 | -58.3786 | 64.8514 | 64.7552 | -58.255 | -58.3511 | -0.041198 | -0.11444 | 0 | 0.13275 | -0.16937 | -0.054932 | 0.013733 | -0.09613 | -0.19226 | 0.036621 | 0.045777 | -0.21973 | -0.027466 | -0.059509 | 122.9736 | 122.9874 | 58.2367 | -123.0881 | 123.0103 | 122.9141 | 58.3191 | -123.1659
454.6406 | 123.2025 | -58.1589 | 64.7919 | -0.22536 | -0.0089218 | 0.0699 | 0.013613 | 0.064078 | -0.011268 | -0.010377 | -0.22246 | -0.021865 | 0.059465 | 0.041327 | -0.0039789 | -0.012922 | 64.8239 | -58.0078 | 0.073242 | -58.342 | 64.8193 | -58.2047 | -58.2642 | -58.1177 | 0.15106 | -58.3969 | 64.8514 | 64.7324 | -58.2596 | -58.3054 | -0.045776 | -0.10528 | 0.027466 | 0.15106 | -0.1831 | -0.07782 | 0.032044 | -0.10071 | -0.14648 | 0.059509 | 0.041199 | -0.23804 | -0.091553 | -0.059509 | 122.9782 | 122.9828 | 58.2321 | -123.056 | 123.0103 | 122.8912 | 58.3099 | -123.0972
455.6406 | 123.2208 | -58.168 | 64.7552 | -0.13381 | -0.0035808 | 0.089126 | 0.0093408 | 0.056601 | -0.016608 | -0.011445 | -0.13091 | -0.010115 | 0.051988 | 0.050941 | -0.0039789 | -0.016126 | 64.8285 | -57.9758 | 0.09613 | -58.3328 | 64.8148 | -58.1909 | -58.255 | -58.0856 | 0.18768 | -58.136 | 64.8697 | 64.7827 | -58.2458 | -58.3191 | -0.022888 | -0.086975 | 0.059509 | 0.19226 | -0.16479 | -0.07782 | 0.073242 | -0.07782 | -0.15106 | 0.11444 | 0.082398 | 0.032044 | 0.18311 | 0.027466 | 122.9828 | 122.9965 | 58.2642 | -123.0103 | 123.0377 | 122.9507 | 58.3557 | -123.0743
456.6406 | 123.2208 | -58.168 | 64.7644 | -0.16433 | 0.00069119 | 0.080581 | 0.023226 | 0.050193 | -0.011268 | -0.013582 | -0.19194 | -0.022933 | 0.042375 | 0.047736 | 0.00029315 | -0.026808 | 64.856 | -57.9712 | 0.091553 | -58.3466 | 64.8056 | -58.2047 | -58.255 | -58.0811 | 0.60425 | -58.3969 | 64.8651 | 64.7049 | -58.2504 | -58.3511 | -0.036621 | -0.086975 | 0.041199 | 0.19684 | -0.17853 | -0.091553 | 0.091553 | -0.082397 | -0.1831 | 0.10071 | 0.086975 | -0.22888 | -0.045777 | -0.059509 | 122.9736 | 123.024 | 58.2596 | -123.0194 | 123.0331 | 122.8729 | 58.7723 | -123.1155
457.6406 | 123.1338 | -58.1863 | 64.8239 | -0.24062 | -0.0089218 | 0.068832 | 0.01575 | 0.053397 | 0.012231 | -0.011445 | -0.60393 | -0.020796 | 0.05626 | 0.065894 | 0.0088381 | -0.012922 | 64.7552 | -58.1039 | -0.045776 | -58.3557 | 64.8468 | -58.2184 | -58.2779 | -58.168 | 0.068665 | -58.4473 | 64.92 | 64.7873 | -58.3008 | -58.342 | -0.032044 | -0.091553 | 0.022888 | 0.082397 | -0.16937 | -0.07782 | -0.068665 | -0.11444 | -0.15564 | 0.09613 | 0.01831 | -0.26093 | -0.10529 | -0.036622 | 123.0331 | 122.9416 | 58.1406 | -123.1018 | 123.1064 | 122.9736 | 58.255 | -123.1659
458.6406 | 123.1293 | -58.2047 | 64.8376 | -0.2101 | 0.0081682 | 0.078445 | 0.016818 | 0.06301 | 0.0079581 | -0.015718 | -0.83281 | -0.01332 | 0.045579 | 0.06269 | -0.0093199 | -0.024671 | 64.769 | -58.136 | -0.032043 | -58.4564 | 64.8697 | -58.2413 | -58.255 | -58.168 | 0.004578 | -58.4793 | 64.9109 | 64.7736 | -58.2779 | -58.3466 | -0.036621 | -0.050354 | 0.032044 | 0.068665 | -0.25177 | -0.20142 | -0.068664 | -0.073242 | -0.14191 | 0.073243 | 0.036621 | -0.27466 | -0.13275 | -0.064086 | 123.0743 | 122.9736 | 58.1726 | -123.0927 | 123.1155 | 122.9782 | 58.2092 | -123.1842
459.6406 | 123.1247 | -58.2001 | 64.8148 | -0.14907 | 0.015645 | 0.075241 | 0.022158 | 0.065146 | -0.0037909 | -0.0029003 | -0.28349 | -0.010115 | 0.057328 | 0.056281 | 0.0034971 | -0.009718 | 64.769 | -58.1085 | 0 | -58.4244 | 64.8376 | -58.255 | -58.2687 | -58.1589 | 0.082397 | -58.4518 | 64.9017 | 64.7644 | -58.287 | -58.342 | -0.054932 | -0.068665 | 0.022888 | 0.091552 | -0.2243 | -0.15564 | -0.045776 | -0.086975 | -0.14191 | 0.086975 | 0.041198 | -0.25177 | -0.10986 | -0.050354 | 123.0377 | 122.9691 | 58.2001 | -123.0835 | 123.1018 | 122.9645 | 58.2825 | -123.1567
460.6406 | 123.1155 | -58.1863 | 64.8376 | -0.22536 | -0.0014448 | 0.066696 | 0.016818 | 0.046988 | 0.00048206 | -0.01465 | 0.35738 | -0.016524 | 0.065873 | 0.042396 | 0.0024291 | -0.00865 | 64.7736 | -58.1085 | -0.009155 | -58.4015 | 64.8422 | -58.2321 | -58.2642 | -58.1635 | 0.07782 | -58.4702 | 64.8926 | 64.801 | -58.2962 | -58.3786 | -0.045777 | -0.07782 | 0.004578 | 0.077819 | -0.21515 | -0.13733 | -0.064086 | -0.10986 | -0.19226 | 0.054932 | 0.022888 | -0.28381 | -0.091553 | -0.036621 | 123.0286 | 122.9599 | 58.1772 | -123.1018 | 123.0789 | 122.9874 | 58.2642 | -123.2162
461.7031 | 123.1155 | -58.1909 | 64.801 | -0.042256 | 0.0017592 | 0.074173 | 0.01575 | 0.051261 | 0.00048206 | -0.0039683 | -0.32927 | -0.0069114 | 0.051988 | 0.033851 | -0.0071839 | -0.006513 | 64.7644 | -58.1268 | -0.027466 | -58.4015 | 64.8697 | -58.2138 | -58.2733 | -58.1635 | 0.073242 | -58.4656 | 64.9063 | 64.7552 | -58.2916 | -58.3649 | -0.022888 | -0.082397 | 0.068665 | 0.064087 | -0.21057 | -0.12817 | -0.036621 | -0.10071 | -0.17395 | 0.10529 | 0.027466 | -0.27466 | -0.10071 | -0.045776 | 123.0606 | 122.9553 | 58.1635 | -123.0743 | 123.0972 | 122.9462 | 58.2642 | -123.1659
462.6406 | 123.1064 | -58.1863 | 64.8056 | -0.25588 | 0.0028272 | 0.070968 | 0.011477 | 0.054465 | -0.014472 | -0.012513 | -1.2753 | -0.017592 | 0.051988 | 0.0456 | 0.0067021 | -0.00865 | 64.769 | -58.0811 | 0.004578 | -58.3878 | 64.8514 | -58.2184 | -58.2687 | -58.1543 | 0.086975 | -58.4473 | 64.888 | 64.7781 | -58.2825 | -58.342 | -0.032044 | -0.082398 | 0.045776 | 0.10529 | -0.20142 | -0.11902 | -0.036621 | -0.096131 | -0.15564 | 0.082397 | 0.032043 | -0.26093 | -0.10529 | -0.027466 | 123.0377 | 122.9553 | 58.1909 | -123.0743 | 123.0743 | 122.9645 | 58.2733 | -123.1476
463.6406 | 123.1201 | -58.1589 | 64.8331 | -0.27114 | 0.01244 | 0.060287 | 0.023226 | 0.059806 | -0.010199 | -0.010377 | -0.039353 | -0.015456 | 0.047715 | 0.047736 | -0.0018429 | -0.011854 | 64.7827 | -58.0811 | 0.018311 | -58.3878 | 64.8514 | -58.2321 | -58.2733 | -58.1955 | 0.10071 | -58.4244 | 64.8788 | 64.7873 | -58.2596 | -58.342 | -0.073242 | -0.11444 | 0.01831 | 0.07782 | -0.22888 | -0.11444 | -0.050354 | -0.10071 | -0.1831 | 0.045776 | -0.036621 | -0.2655 | -0.082397 | -0.045777 | 123.0103 | 122.9416 | 58.1772 | -123.1064 | 123.0377 | 122.9462 | 58.2596 | -123.175
464.6406 | 123.1247 | -58.1772 | 64.8376 | -0.25588 | 0.0060322 | 0.063492 | 0.01575 | 0.068351 | 0.0036861 | -0.0029003 | 0.0522 | -0.0079794 | 0.058397 | 0.061622 | 0.0024291 | -0.017194 | 64.7873 | -58.0673 | 0.013733 | -58.374 | 64.8285 | -58.2275 | -58.2779 | -58.1223 | 0.041199 | -58.4473 | 64.8926 | 64.769 | -58.2687 | -58.3466 | -0.050354 | -0.10071 | -0.009155 | 0.10986 | -0.19684 | -0.09613 | -0.050354 | -0.091553 | -0.16937 | 0.054932 | 0.054932 | -0.27008 | -0.10071 | -0.068664 | 123.0057 | 122.9645 | 58.1909 | -123.1155 | 123.0698 | 122.9462 | 58.2184 | -123.1842
465.6406 | 123.1201 | -58.2184 | 64.8148 | -0.30166 | 0.013508 | 0.066696 | 0.030703 | 0.059806 | 0.0026181 | -0.010377 | -0.28349 | 0.00056556 | 0.051988 | 0.059485 | 0.0099061 | -0.015058 | 64.7461 | -58.1131 | -0.027466 | -58.4106 | 64.8972 | -58.2275 | -58.3054 | -58.2687 | 0.07782 | -58.4793 | 64.9017 | 64.7827 | -58.2733 | -58.3832 | -0.009155 | -0.086975 | 0.082398 | 0.10529 | -0.19226 | -0.10529 | -0.068664 | -0.054931 | -0.16479 | 0.086975 | -0.050354 | -0.26093 | -0.09613 | -0.032043 | 123.1155 | 122.9645 | 58.1909 | -123.1201 | 123.1201 | 123.0011 | 58.2962 | -123.1979
466.6406 | 123.175 | -58.2001 | 64.8239 | -0.10329 | 0.018849 | 0.08165 | 0.0082728 | 0.054465 | 0.010095 | -0.01465 | -0.32927 | -0.0090474 | 0.059465 | 0.058417 | 0.0034971 | -0.022535 | 64.7552 | -58.1085 | -0.027466 | -58.3786 | 64.8605 | -58.255 | -58.2687 | -58.1543 | 0.07782 | -58.4702 | 64.856 | 64.7781 | -58.255 | -58.3511 | -0.054932 | -0.068665 | 0.036621 | 0.091552 | -0.17853 | -0.10986 | -0.068665 | -0.054932 | -0.15106 | 0.032043 | 0.045776 | -0.27008 | -0.11902 | -0.045777 | 123.0606 | 122.9553 | 58.1726 | -123.0927 | 123.056 | 122.9782 | 58.2779 | -123.175
467.6406 | 123.1613 | -58.1955 | 64.7644 | 0.018779 | 0.017781 | 0.068832 | 0.017886 | 0.056601 | 0.014367 | -0.0039683 | -0.31401 | -0.0079794 | 0.05092 | 0.040259 | 0.0034971 | -0.019331 | 64.7873 | -58.0948 | -0.032043 | -58.3786 | 64.8148 | -58.2458 | -58.3099 | -58.1497 | 0.07782 | -58.4473 | 64.8468 | 64.7415 | -58.287 | -58.3649 | -0.050354 | -0.11444 | 0.050354 | 0.10071 | -0.18311 | -0.068664 | 0.022888 | -0.091552 | -0.16937 | 0.082398 | 0.045777 | -0.25177 | -0.082398 | -0.022888 | 123.0103 | 122.9828 | 58.1635 | -123.0743 | 123.0423 | 122.937 | 58.2733 | -123.1293
468.6406 | 123.0972 | -58.1772 | 64.7873 | -0.2101 | 0.011372 | 0.075241 | 0.031771 | 0.057669 | 0.0036861 | -0.016786 | -0.2072 | -0.021865 | 0.054124 | 0.044532 | 0.01311 | -0.005445 | 64.7324 | -58.1177 | -0.036621 | -58.3878 | 64.8651 | -58.2596 | -58.2916 | -58.2779 | 0.15564 | -58.4976 | 64.8743 | 64.7781 | -58.3008 | -58.3557 | -0.082398 | -0.11444 | 0.07782 | 0.059509 | -0.21057 | -0.09613 | -0.054931 | -0.1236 | -0.17853 | 0.086976 | -0.10071 | -0.32043 | -0.14191 | -0.009155 | 123.0423 | 122.9095 | 58.1406 | -123.0789 | 123.0515 | 122.9553 | 58.3328 | -123.143
469.6406 | 123.1064 | -58.1726 | 64.8239 | -0.25588 | -0.013195 | 0.070968 | 0.027499 | 0.044852 | -0.016608 | -0.016786 | 0.0522 | -0.014388 | 0.05626 | 0.056281 | -0.00077485 | -0.009718 | 64.7736 | -58.0673 | 0.018311 | -58.3694 | 64.8422 | -58.2184 | -58.255 | -58.136 | 0.20142 | -58.4518 | 64.8926 | 64.8056 | -58.2596 | -58.3282 | -0.045777 | -0.082398 | 0.01831 | 0.10529 | -0.19684 | -0.11444 | -0.050354 | -0.086976 | -0.15564 | 0.068664 | 0.036621 | -0.27924 | -0.1236 | -0.018311 | 123.0148 | 122.9462 | 58.1909 | -123.0789 | 123.0652 | 122.9782 | 58.374 | -123.1522
470.6406 | 123.1293 | -58.1955 | 64.8193 | -0.27114 | 0.030598 | 0.08699 | 0.03284 | 0.051261 | -0.0069949 | -0.025331 | 0.11323 | -0.012251 | 0.057328 | 0.060554 | -0.010388 | -0.018263 | 64.7552 | -58.0811 | 0.022888 | -58.3786 | 64.8468 | -58.2367 | -58.255 | -58.1497 | 0.20142 | -58.461 | 64.8605 | 64.7919 | -58.287 | -58.3328 | -0.041198 | -0.059509 | 0.027466 | 0.11444 | -0.18311 | -0.1236 | -0.064087 | -0.091552 | -0.13733 | 0.041199 | 0.045777 | -0.2655 | -0.12817 | -0.027466 | 123.0423 | 122.9507 | 58.2184 | -123.0743 | 123.056 | 122.9874 | 58.3969 | -123.1522
471.6406 | 123.1659 | -58.1909 | 64.8102 | -0.25588 | 0.023121 | 0.075241 | 0.01575 | 0.067282 | 0.0026181 | -0.018922 | -0.25298 | -0.017592 | 0.065873 | 0.042396 | 0.012042 | -0.023603 | 64.7369 | -58.1085 | -0.036621 | -58.3786 | 64.8788 | -58.2138 | -58.3054 | -58.168 | 0.068665 | -58.461 | 64.856 | 64.7781 | -58.2779 | -58.3511 | -0.022888 | -0.11444 | 0.068664 | 0.082397 | -0.18768 | -0.073242 | -0.073243 | -0.086975 | -0.16022 | 0.045776 | 0.022888 | -0.27008 | -0.10986 | -0.032044 | 123.0698 | 122.9279 | 58.1543 | -123.1155 | 123.0469 | 122.9691 | 58.2596 | -123.1613
472.6406 | 123.1247 | -58.1863 | 64.7964 | -0.17959 | 0.019917 | 0.0699 | 0.027499 | 0.058738 | 0.012231 | -0.0029003 | -0.25298 | -0.0079794 | 0.059465 | 0.052009 | 0.0034971 | -0.019331 | 64.7461 | -58.1177 | -0.027466 | -58.3969 | 64.8605 | -58.2321 | -58.2916 | -58.1589 | 0.073242 | -58.429 | 64.8972 | 64.7736 | -58.2596 | -58.3603 | -0.045777 | -0.10529 | 0.064087 | 0.068664 | -0.21057 | -0.10529 | -0.050354 | -0.073243 | -0.17395 | 0.10071 | 0.027465 | -0.24262 | -0.068664 | -0.022888 | 123.0469 | 122.9324 | 58.1589 | -123.0881 | 123.0835 | 122.9599 | 58.2596 | -123.1567
473.6406 | 123.1522 | -58.1955 | 64.7827 | -0.22536 | 0.020985 | 0.066696 | 0.01575 | 0.064078 | 0.010095 | -0.013582 | -0.22246 | -0.0058434 | 0.057328 | 0.056281 | 0.0045661 | -0.018263 | 64.7644 | -58.1223 | -0.022888 | -58.3878 | 64.856 | -58.2321 | -58.3008 | -58.168 | 0.082397 | -58.461 | 64.8697 | 64.7964 | -58.3099 | -58.342 | -0.036621 | -0.10529 | 0.073242 | 0.073243 | -0.19226 | -0.086975 | -0.018311 | -0.11444 | -0.14648 | 0.086975 | 0.027466 | -0.2655 | -0.11902 | 0.013733 | 123.0515 | 122.9599 | 58.1726 | -123.0835 | 123.0652 | 122.9919 | 58.2779 | -123.1247
474.6406 | 123.2071 | -58.1635 | 64.801 | -0.19484 | 0.013508 | 0.074173 | 0.037112 | 0.071555 | 0.011163 | -0.0071733 | -0.23772 | -0.012251 | 0.070146 | 0.050941 | -0.00077485 | -0.015058 | 64.7598 | -58.1177 | -0.022888 | -58.3786 | 64.856 | -58.2138 | -58.287 | -58.1589 | 0.086975 | -58.4381 | 64.8605 | 64.7736 | -58.287 | -58.3557 | -0.050354 | -0.1236 | 0.054932 | 0.045776 | -0.21515 | -0.091553 | -0.041198 | -0.1236 | -0.19226 | 0.05951 | 0.004577 | -0.27466 | -0.082397 | -0.027465 | 123.0194 | 122.9233 | 58.1406 | -123.0881 | 123.024 | 122.937 | 58.2504 | -123.1567
475.6406 | 123.1522 | -58.2047 | 64.7919 | -0.13381 | 0.031666 | 0.075241 | 0.02109 | 0.065146 | 0.0026181 | -0.0061053 | -0.23772 | -0.0069114 | 0.065873 | 0.055213 | 0.00029315 | -0.024671 | 64.7644 | -58.1131 | -0.022888 | -58.3786 | 64.8514 | -58.2275 | -58.3008 | -58.1543 | 0.10529 | -58.4335 | 64.8788 | 64.7415 | -58.2779 | -58.3649 | -0.022888 | -0.09613 | 0.059509 | 0.091553 | -0.17395 | -0.07782 | -0.027466 | -0.073242 | -0.16022 | 0.086975 | 0.050354 | -0.22888 | -0.068665 | -0.050354 | 123.056 | 122.9691 | 58.1818 | -123.0927 | 123.0835 | 122.9462 | 58.3099 | -123.1567
476.6406 | 123.0881 | -58.1863 | 64.801 | -0.22536 | 0.017781 | 0.0699 | 0.018954 | 0.061942 | 0.011163 | -0.011445 | -0.49712 | -0.0079794 | 0.062669 | 0.052009 | 0.0045661 | -0.006513 | 64.5767 | -58.0994 | -0.009155 | -58.4564 | 64.8422 | -58.255 | -58.2962 | -58.2092 | 0.064087 | -58.4702 | 64.8834 | 64.801 | -58.2916 | -58.374 | -0.068665 | -0.10986 | 0.041199 | 0.086975 | -0.27008 | -0.16022 | -0.2243 | -0.10529 | -0.18768 | 0.082398 | -0.022889 | -0.28381 | -0.096131 | 0 | 123.0286 | 122.7631 | 58.1772 | -123.0972 | 123.0698 | 122.9874 | 58.2504 | -123.175
477.6406 | 123.1613 | -58.2001 | 64.7919 | -0.10329 | 0.013508 | 0.072037 | 0.022158 | 0.070487 | 0.0036861 | -0.0039683 | -0.16142 | -0.01866 | 0.070146 | 0.055213 | -0.0029109 | -0.019331 | 64.7644 | -58.0948 | -0.013733 | -58.3832 | 64.8376 | -58.2184 | -58.2825 | -58.1726 | 0.086975 | -58.4518 | 64.8514 | 64.7507 | -58.2962 | -58.3603 | -0.018311 | -0.082398 | 0.045776 | 0.10529 | -0.18311 | -0.10071 | -0.027466 | -0.096131 | -0.16022 | 0.059509 | 0.027466 | -0.25177 | -0.091552 | -0.041199 | 123.0377 | 122.9645 | 58.1863 | -123.0743 | 123.0515 | 122.9507 | 58.287 | -123.1522
478.6406 | 123.1659 | -58.2001 | 64.7827 | -0.11855 | 0.022053 | 0.0699 | 0.023226 | 0.058738 | 0.0036861 | -0.0082413 | -0.10039 | -0.0058434 | 0.061601 | 0.049872 | 0.0056341 | -0.012922 | 64.769 | -58.1039 | -0.022888 | -58.3694 | 64.856 | -58.2413 | -58.2687 | -58.1451 | 0.064087 | -58.4564 | 64.8468 | 64.7781 | -58.3008 | -58.3603 | -0.041199 | -0.068665 | 0.073242 | 0.09613 | -0.16937 | -0.10071 | -0.013733 | -0.10071 | -0.16022 | 0.064087 | 0.054931 | -0.25635 | -0.09613 | -0.004578 | 123.056 | 122.9691 | 58.1772 | -123.0515 | 123.0469 | 122.9782 | 58.2642 | -123.143
479.6406 | 123.1567 | -58.1863 | 64.7873 | 0.079814 | 0.025258 | 0.075241 | 0.023226 | 0.059806 | 0.011163 | -0.015718 | 0.0522 | -0.0058434 | 0.062669 | 0.070167 | 0.016315 | -0.01399 | 64.7873 | -58.0856 | -0.022888 | -58.3694 | 64.8285 | -58.2275 | -58.3008 | -58.2184 | 0.16937 | -58.4793 | 64.8148 | 64.7781 | -58.3008 | -58.3649 | -0.041199 | -0.11444 | 0.041199 | 0.10071 | -0.18311 | -0.068665 | 0 | -0.11444 | -0.17853 | 0.027466 | -0.032044 | -0.29297 | -0.11444 | -0.009155 | 123.0148 | 122.9736 | 58.1635 | -123.0881 | 123.0011 | 122.9645 | 58.3557 | -123.1522
480.6406 | 123.1201 | -58.2047 | 64.7781 | 0.034038 | 0.028462 | 0.068832 | 0.01575 | 0.065146 | 0.0047541 | -0.012513 | 0.021682 | -0.0058434 | 0.051988 | 0.059485 | 0.0013611 | -0.002241 | 64.7873 | -58.0994 | -0.013733 | -58.3832 | 64.8331 | -58.2275 | -58.2962 | -58.1863 | 0.10986 | -58.429 | 64.8514 | 64.769 | -58.2962 | -58.374 | -0.022888 | -0.091553 | 0.054932 | 0.10529 | -0.17853 | -0.086975 | 0.009155 | -0.091553 | -0.16937 | 0.073242 | 0.018311 | -0.2243 | -0.054932 | -0.009155 | 123.0377 | 122.9919 | 58.1909 | -123.0743 | 123.056 | 122.9736 | 58.3145 | -123.1522
481.6406 | 123.175 | -58.2047 | 64.7873 | 0.00352 | 0.038075 | 0.073105 | 0.016818 | 0.073691 | 0.013299 | -0.00076433 | 2.5546 | -0.0058434 | 0.065873 | 0.047736 | 0.010974 | -0.006513 | 64.7964 | -58.0902 | -0.036621 | -58.3878 | 64.8285 | -58.2413 | -58.3054 | -58.136 | 0.059509 | -58.4427 | 64.8376 | 64.7827 | -58.2825 | -58.342 | -0.036621 | -0.10071 | 0.041199 | 0.11444 | -0.18311 | -0.082397 | 0.009156 | -0.07782 | -0.13733 | 0.050354 | 0.068665 | -0.23804 | -0.10071 | -0.004577 | 123.0331 | 123.0011 | 58.168 | -123.0927 | 123.0423 | 122.9874 | 58.2642 | -123.1293
482.6406 | 123.1934 | -58.1955 | 64.801 | 0.018779 | 0.026326 | 0.0699 | 0.022158 | 0.054465 | -0.010199 | -0.0093093 | -0.48186 | -0.01332 | 0.063737 | 0.046668 | 0.0013611 | -0.011854 | 64.801 | -58.1039 | -0.013733 | -58.3832 | 64.8376 | -58.2138 | -58.287 | -58.136 | 0.050354 | -58.4564 | 64.856 | 64.7873 | -58.2916 | -58.3511 | -0.01831 | -0.091552 | 0.036621 | 0.091553 | -0.18768 | -0.096131 | 0 | -0.09613 | -0.15564 | 0.054932 | 0.05951 | -0.26093 | -0.10529 | -0.013733 | 123.0331 | 122.9965 | 58.1818 | -123.0881 | 123.0515 | 122.9828 | 58.2458 | -123.1522
483.6406 | 123.1476 | -58.1772 | 64.7873 | -0.13381 | 0.033803 | 0.068832 | 0.023226 | 0.06301 | 0.0026181 | -0.01999 | 0.11323 | -0.011183 | 0.078691 | 0.048804 | 0.0034971 | -0.007581 | 64.7781 | -58.1177 | -0.018311 | -58.3878 | 64.8514 | -58.2413 | -58.2779 | -58.1451 | 0.073242 | -58.4381 | 64.856 | 64.769 | -58.2825 | -58.3511 | -0.064087 | -0.10071 | 0.064087 | 0.059509 | -0.21057 | -0.10986 | -0.009155 | -0.10529 | -0.17395 | 0.068665 | 0.032043 | -0.26093 | -0.086975 | -0.01831 | 123.0286 | 122.9553 | 58.1589 | -123.0652 | 123.0331 | 122.9462 | 58.2504 | -123.1384
484.6406 | 123.1338 | -58.2092 | 64.7827 | -0.16433 | 0.028462 | 0.059219 | 0.022158 | 0.058738 | -0.010199 | -0.010377 | -0.25298 | -0.0047754 | 0.078691 | 0.064826 | 0.0077701 | -0.009718 | 64.7873 | -58.0902 | -0.004578 | -58.3786 | 64.8193 | -58.2458 | -58.2596 | -58.1406 | 0.068665 | -58.4518 | 64.8651 | 64.801 | -58.3008 | -58.3649 | -0.036621 | -0.050354 | 0.036621 | 0.11902 | -0.16937 | -0.11902 | 0.004577 | -0.091552 | -0.15564 | 0.082397 | 0.068665 | -0.24261 | -0.086975 | 0.01831 | 123.0286 | 122.9965 | 58.2047 | -123.0423 | 123.0743 | 123.0103 | 58.2779 | -123.1476
485.6406 | 123.1567 | -58.2001 | 64.7964 | 0.18663 | 0.032734 | 0.075241 | 0.017886 | 0.059806 | 0.0026181 | -0.010377 | 0.22005 | -0.0069114 | 0.054124 | 0.046668 | -0.0029109 | -0.018263 | 64.7552 | -58.1497 | -0.054932 | -58.4061 | 64.7919 | -58.255 | -58.2962 | -58.2001 | -0.004578 | -58.461 | 64.8285 | 64.7781 | -58.3054 | -58.374 | -0.054932 | -0.096131 | -0.004578 | 0.050354 | -0.20599 | -0.10986 | -0.041199 | -0.10529 | -0.17395 | 0.032043 | 0 | -0.26093 | -0.086976 | -0.018311 | 122.9919 | 122.9553 | 58.1451 | -123.0927 | 123.0286 | 122.9782 | 58.1955 | -123.1705
486.6406 | 123.1613 | -58.2138 | 64.7964 | 0.14085 | 0.016713 | 0.067764 | 0.026431 | 0.061942 | 0.012231 | -0.0071733 | 0.2353 | -0.0079794 | 0.076554 | 0.060554 | 0.0088381 | -0.011854 | 64.769 | -58.1314 | -0.064087 | -58.4015 | 64.8148 | -58.2413 | -58.3054 | -58.1909 | -0.004578 | -58.4793 | 64.8376 | 64.7919 | -58.2962 | -58.3832 | -0.027466 | -0.091553 | 0.01831 | 0.082397 | -0.18768 | -0.09613 | -0.027466 | -0.082398 | -0.16937 | 0.041198 | 0.022888 | -0.2655 | -0.09613 | -0.004578 | 123.0286 | 122.9828 | 58.1497 | -123.1018 | 123.0515 | 123.0057 | 58.2092 | -123.1796
487.6406 | 123.0972 | -58.2092 | 64.7598 | 0.064555 | 0.034871 | 0.067764 | 0.037112 | 0.053397 | 0.011163 | -0.01465 | 0.2353 | -0.0015704 | 0.066941 | 0.058417 | 0.0045661 | -0.012922 | 64.7781 | -58.1451 | -0.036621 | -58.4061 | 64.8193 | -58.223 | -58.2916 | -58.1909 | 0.009155 | -58.4885 | 64.8285 | 64.7781 | -58.2825 | -58.3649 | -0.013732 | -0.082397 | 0.059509 | 0.064087 | -0.19684 | -0.11444 | 0.01831 | -0.073242 | -0.15564 | 0.068664 | 0.018311 | -0.27923 | -0.1236 | 0.01831 | 123.0286 | 122.9874 | 58.1726 | -123.0515 | 123.0377 | 122.9874 | 58.2184 | -123.1247
488.6406 | 123.1247 | -58.1818 | 64.7873 | 0.21714 | 0.034871 | 0.059219 | 0.028567 | 0.044852 | 0.010095 | -0.0029003 | 0.18953 | -0.012251 | 0.060533 | 0.053077 | 0.00029315 | -0.010786 | 64.7827 | -58.1406 | -0.045776 | -58.3923 | 64.8056 | -58.2367 | -58.3008 | -58.1863 | 0.009155 | -58.4976 | 64.8422 | 64.7919 | -58.2825 | -58.3649 | -0.054931 | -0.11902 | 0.018311 | 0.041199 | -0.21057 | -0.091553 | -0.004577 | -0.10071 | -0.18311 | 0.054932 | -0.004577 | -0.31586 | -0.13275 | 0.004578 | 122.9874 | 122.9645 | 58.136 | -123.0881 | 123.024 | 122.9736 | 58.1909 | -123.1522
489.6406 | 123.1659 | -58.223 | 64.7736 | 0.049296 | 0.041279 | 0.065628 | 0.027499 | 0.049125 | 0.0079581 | -0.013582 | 0.26582 | -0.011183 | 0.070146 | 0.066962 | 0.015247 | -0.018263 | 64.7736 | -58.1406 | -0.032043 | -58.3923 | 64.8376 | -58.2321 | -58.3054 | -58.1863 | 0.013733 | -58.4702 | 64.856 | 64.8056 | -58.3054 | -58.3832 | -0.009156 | -0.082398 | 0.064086 | 0.082397 | -0.16937 | -0.086975 | 0 | -0.082398 | -0.16022 | 0.082397 | 0.036621 | -0.24719 | -0.086975 | 0.032043 | 123.0606 | 122.9965 | 58.1909 | -123.0789 | 123.0789 | 123.0286 | 58.2367 | -123.1567
490.6406 | 123.1796 | -58.1772 | 64.7964 | -0.026997 | 0.02953 | 0.072037 | 0.027499 | 0.065146 | -0.00058594 | -0.016786 | 0.021682 | -0.01332 | 0.07335 | 0.0456 | 0.0013611 | -0.005445 | 64.7827 | -58.1131 | -0.009155 | -58.3923 | 64.8468 | -58.2321 | -58.2916 | -58.1589 | 0.064087 | -58.4427 | 64.8468 | 64.769 | -58.2916 | -58.342 | -0.054932 | -0.11444 | 0.050354 | 0.064087 | -0.21515 | -0.10071 | -0.013733 | -0.11444 | -0.16479 | 0.050354 | 0.01831 | -0.2655 | -0.10071 | -0.027466 | 123.024 | 122.9599 | 58.168 | -123.0881 | 123.024 | 122.9462 | 58.2413 | -123.1384
491.7031 | 123.1842 | -58.2138 | 64.7598 | 0.59861 | 0.013508 | 0.062424 | 0.02109 | 0.06301 | -0.0016549 | -0.015718 | 0.63203 | -0.0069114 | 0.046647 | 0.048804 | 0.0067021 | -0.001173 | 64.7095 | -58.1909 | -0.12817 | -58.4335 | 64.8148 | -58.2642 | -58.3099 | -58.1818 | -0.045776 | -58.4702 | 64.8193 | 64.7781 | -58.3145 | -58.3878 | -0.050354 | -0.096131 | 0.054931 | 0.022888 | -0.21973 | -0.1236 | -0.050354 | -0.10071 | -0.17395 | 0.059509 | 0.032043 | -0.25635 | -0.082398 | 0.01831 | 123.0286 | 122.9233 | 58.0856 | -123.0698 | 123.0331 | 122.9919 | 58.168 | -123.1476
492.6406 | 123.1293 | -58.2047 | 64.7781 | 0.2324 | 0.045552 | 0.070968 | 0.018954 | 0.055533 | 0.0079581 | -0.0029003 | 0.26582 | -0.012251 | 0.063737 | 0.063758 | 0.0088381 | -0.020399 | 64.7552 | -58.168 | -0.082397 | -58.4106 | 64.7919 | -58.255 | -58.3282 | -58.223 | -0.032043 | -58.5205 | 64.856 | 64.8056 | -58.3191 | -58.3878 | -0.050354 | -0.1236 | 0.013733 | 0.036621 | -0.20599 | -0.082398 | -0.022888 | -0.11444 | -0.18311 | 0.07782 | -0.01831 | -0.31586 | -0.13275 | 0.027466 | 122.9965 | 122.9599 | 58.1223 | -123.1064 | 123.0606 | 123.0103 | 58.1726 | -123.1659
493.6406 | 123.1476 | -58.1955 | 64.7873 | 0.24766 | 0.040211 | 0.060287 | 0.0061368 | 0.058738 | 0.0079581 | -0.010377 | 0.26582 | -0.0090474 | 0.058397 | 0.060554 | 0.01311 | -0.006513 | 64.7507 | -58.1589 | -0.082397 | -58.3969 | 64.8468 | -58.2458 | -58.2916 | -58.2138 | -0.013733 | -58.493 | 64.8468 | 64.7964 | -58.3054 | -58.3694 | -0.050354 | -0.09613 | 0.05951 | 0.036621 | -0.20142 | -0.10529 | -0.036621 | -0.10986 | -0.17395 | 0.05951 | -0.01831 | -0.29755 | -0.1236 | 0.009156 | 123.0423 | 122.9462 | 58.1131 | -123.0789 | 123.0423 | 122.9919 | 58.1818 | -123.1567
494.6406 | 123.143 | -58.2047 | 64.7781 | 0.21714 | 0.037007 | 0.073105 | 0.020022 | 0.069419 | 0.0026181 | -0.013582 | 0.22005 | -0.0079794 | 0.076554 | 0.055213 | 0.0013611 | -0.007581 | 64.769 | -58.1772 | -0.086975 | -58.4198 | 64.8239 | -58.2504 | -58.2916 | -58.1909 | -0.004578 | -58.5068 | 64.8468 | 64.7964 | -58.3054 | -58.3466 | -0.045776 | -0.086975 | 0.045777 | 0.027466 | -0.21515 | -0.12817 | -0.009155 | -0.10071 | -0.14191 | 0.068665 | 0.013733 | -0.30212 | -0.16022 | 0.018311 | 123.0286 | 122.9736 | 58.1177 | -123.0698 | 123.0515 | 123.0011 | 58.2001 | -123.1247
495.6406 | 123.1384 | -58.1955 | 64.7827 | 0.2324 | 0.051961 | 0.062424 | 0.030703 | 0.053397 | 0.010095 | -0.00076433 | 0.20479 | -0.0058434 | 0.066941 | 0.056281 | 0.0077701 | -0.021467 | 64.769 | -58.1635 | -0.082397 | -58.429 | 64.8102 | -58.2367 | -58.3237 | -58.2001 | -0.027466 | -58.4976 | 64.8468 | 64.8285 | -58.2779 | -58.3786 | -0.041198 | -0.12817 | 0.027466 | 0.032044 | -0.23346 | -0.10529 | -0.013733 | -0.082397 | -0.18311 | 0.064087 | -0.004577 | -0.30212 | -0.11902 | 0.045776 | 123.0057 | 122.9645 | 58.1131 | -123.1064 | 123.0423 | 123.024 | 58.168 | -123.1613
496.6406 | 123.1293 | -58.223 | 64.7919 | 0.3087 | 0.04662 | 0.074173 | 0.020022 | 0.046988 | 0.0047541 | -0.011445 | 0.2353 | -0.012251 | 0.054124 | 0.059485 | -0.0018429 | -0.022535 | 64.7873 | -58.1543 | -0.054932 | -58.4152 | 64.8239 | -58.2458 | -58.3008 | -58.1955 | -0.004578 | -58.5022 | 64.8422 | 64.7781 | -58.3145 | -58.3832 | -0.022889 | -0.07782 | 0.032044 | 0.068664 | -0.19226 | -0.11444 | -0.004578 | -0.091553 | -0.16022 | 0.050354 | 0.027465 | -0.27924 | -0.11902 | -0.013733 | 123.0469 | 123.0103 | 58.168 | -123.0927 | 123.0652 | 123.0011 | 58.2184 | -123.175
497.6406 | 123.1659 | -58.1818 | 64.801 | 0.049296 | 0.018849 | 0.066696 | 0.037112 | 0.070487 | 0.013299 | -0.012513 | 0.097976 | -0.019728 | 0.065873 | 0.058417 | 0.018451 | -0.009718 | 64.8056 | -58.1268 | -0.022888 | -58.3786 | 64.8285 | -58.2458 | -58.287 | -58.2687 | 0.19226 | -58.4839 | 64.8285 | 64.801 | -58.287 | -58.3603 | -0.064087 | -0.10529 | 0.027466 | 0.054932 | -0.19684 | -0.091553 | 0.004578 | -0.10529 | -0.17853 | 0.027466 | -0.086975 | -0.30212 | -0.1236 | 0 | 123.0103 | 122.9874 | 58.1589 | -123.0881 | 123.0103 | 122.9828 | 58.374 | -123.1613
498.6406 | 123.143 | -58.2275 | 64.7964 | 0.095073 | 0.041279 | 0.060287 | 0.024295 | 0.055533 | -0.0016549 | -0.0071733 | 0.29634 | -0.0047754 | 0.06801 | 0.074439 | 0.0013611 | -0.01399 | 64.769 | -58.136 | -0.045776 | -58.4152 | 64.8285 | -58.2413 | -58.3099 | -58.1955 | 0.004578 | -58.4976 | 64.8285 | 64.8102 | -58.2916 | -58.3923 | -0.013733 | -0.082398 | 0.032043 | 0.091553 | -0.18768 | -0.10529 | -0.027466 | -0.064087 | -0.16479 | 0.032043 | 0.032043 | -0.27008 | -0.10529 | 0.013733 | 123.056 | 122.9965 | 58.1818 | -123.1064 | 123.056 | 123.0377 | 58.2321 | -123.1888
499.6406 | 123.0927 | -58.2458 | 64.7781 | 0.26292 | 0.034871 | 0.058151 | 0.018954 | 0.055533 | 0.0047541 | -0.013582 | 0.12849 | -0.0047754 | 0.074418 | 0.046668 | 0.0045661 | -0.005445 | 64.7232 | -58.1955 | -0.10529 | -58.4152 | 64.8285 | -58.2504 | -58.287 | -58.2413 | -0.12817 | -58.5434 | 64.8514 | 64.7964 | -58.3191 | -58.3969 | -0.004577 | -0.041198 | 0.050354 | 0.050354 | -0.16937 | -0.12817 | -0.054931 | -0.073242 | -0.15106 | 0.073242 | 0.004578 | -0.29755 | -0.14648 | 0.018311 | 123.0743 | 122.9691 | 58.1406 | -123.0652 | 123.0972 | 123.0423 | 58.1177 | -123.175
500.6406 | 123.0743 | -58.2275 | 64.7873 | 0.29344 | 0.030598 | 0.063492 | 0.024295 | 0.061942 | 0.0058221 | -0.0029003 | 0.14375 | -0.0015704 | 0.066941 | 0.044532 | 0.0077701 | -0.009718 | 64.7369 | -58.1909 | -0.10071 | -58.429 | 64.8376 | -58.255 | -58.3282 | -58.2321 | -0.10529 | -58.5297 | 64.8422 | 64.8056 | -58.3145 | -58.4061 | -0.027466 | -0.10071 | 0.050354 | 0.036621 | -0.20142 | -0.10071 | -0.050354 | -0.086975 | -0.17853 | 0.054932 | -0.004578 | -0.30212 | -0.1236 | 0.018311 | 123.0652 | 122.9645 | 58.1268 | -123.1155 | 123.0698 | 123.0331 | 58.1223 | -123.1934
501.6406 | 123.0743 | -58.2092 | 64.7781 | 0.18663 | 0.023121 | 0.073105 | 0.024295 | 0.050193 | 0.012231 | -0.010377 | 0.2353 | -0.0069114 | 0.062669 | 0.037055 | 0.0024291 | -0.009718 | 64.7278 | -58.1909 | -0.09613 | -58.4244 | 64.8239 | -58.2458 | -58.2779 | -58.2458 | -0.022888 | -58.5251 | 64.8376 | 64.8102 | -58.3145 | -58.3969 | -0.036621 | -0.068664 | 0.045777 | 0.018311 | -0.21515 | -0.14648 | -0.050354 | -0.10529 | -0.18768 | 0.059509 | -0.036621 | -0.31586 | -0.12817 | 0.032044 | 123.0331 | 122.937 | 58.1131 | -123.056 | 123.0469 | 123.0194 | 58.1863 | -123.175
502.6406 | 123.1293 | -58.2184 | 64.7873 | 0.2324 | 0.051961 | 0.068832 | 0.013613 | 0.064078 | 0.0015501 | -0.016786 | 0.26582 | -0.014388 | 0.072282 | 0.06803 | -0.0018429 | -0.015058 | 64.7552 | -58.1909 | -0.082397 | -58.4198 | 64.8331 | -58.2504 | -58.2962 | -58.223 | -0.045776 | -58.5114 | 64.8376 | 64.8193 | -58.3191 | -58.3969 | -0.032043 | -0.07782 | 0.045777 | 0.027466 | -0.20142 | -0.1236 | -0.032043 | -0.10071 | -0.17853 | 0.050354 | -0.004577 | -0.29297 | -0.11444 | 0.032044 | 123.0515 | 122.9736 | 58.136 | -123.0835 | 123.056 | 123.0377 | 58.1726 | -123.1842
503.6406 | 123.1338 | -58.1772 | 64.7598 | -0.057515 | 0.032734 | 0.061355 | 0.0039998 | 0.053397 | 0.0036861 | -0.0071733 | 0.44893 | -0.0026384 | 0.071214 | 0.066962 | -0.0029109 | -0.002241 | 64.7964 | -58.3466 | -0.1831 | -58.3878 | 64.7964 | -58.255 | -58.3099 | -58.1589 | 0.050354 | -58.4381 | 64.8514 | 64.8102 | -58.287 | -58.3466 | -0.07782 | -0.13275 | 0.036621 | -0.16937 | -0.21057 | -0.077819 | 0.036621 | -0.10986 | -0.16937 | 0.091552 | 0.01831 | -0.26093 | -0.091552 | 0.050354 | 122.9736 | 122.9736 | 57.9941 | -123.0698 | 123.0286 | 122.9874 | 58.2275 | -123.1064
504.6406 | 123.1522 | -58.1909 | 64.7873 | 0.064555 | 0.027394 | 0.060287 | 0.020022 | 0.060874 | 0.00048206 | -0.011445 | -0.49712 | -0.011183 | 0.063737 | 0.059485 | -0.0039789 | -0.022535 | 64.7873 | -58.1085 | -0.013733 | -58.3923 | 64.8376 | -58.2413 | -58.287 | -58.1497 | 0.041199 | -58.4747 | 64.8331 | 64.7873 | -58.2779 | -58.3603 | -0.050354 | -0.09613 | 0.050354 | 0.082397 | -0.20142 | -0.10529 | 0 | -0.086975 | -0.16937 | 0.045777 | 0.041199 | -0.28381 | -0.11444 | 0 | 123.0286 | 122.9782 | 58.1772 | -123.0743 | 123.024 | 122.9782 | 58.2321 | -123.1476
505.6406 | 123.1384 | -58.2138 | 64.7736 | 0.12559 | 0.023121 | 0.062424 | 0.02109 | 0.049125 | 0.014367 | 0.0035077 | 0.26582 | -0.01332 | 0.042375 | 0.059485 | 0.0034971 | -0.00865 | 64.7644 | -58.136 | -0.064087 | -58.4061 | 64.8239 | -58.2458 | -58.2962 | -58.1909 | 0 | -58.4839 | 64.856 | 64.8056 | -58.3237 | -58.3649 | -0.032044 | -0.082398 | 0.050354 | 0.07782 | -0.19226 | -0.10986 | -0.009156 | -0.10986 | -0.15106 | 0.082397 | 0.022888 | -0.27008 | -0.11902 | 0.032043 | 123.0377 | 122.9782 | 58.1497 | -123.0698 | 123.0698 | 123.0194 | 58.2138 | -123.1384
506.6406 | 123.0927 | -58.2367 | 64.7598 | 0.24766 | 0.030598 | 0.079513 | 0.010409 | 0.066214 | 0.0015501 | -0.012513 | 0.2353 | -0.0058434 | 0.060533 | 0.056281 | 0.0034971 | -0.015058 | 64.7095 | -58.1909 | -0.10071 | -58.4244 | 64.8102 | -58.2275 | -58.3145 | -58.2504 | -0.10986 | -58.5434 | 64.8651 | 64.7919 | -58.3511 | -58.4015 | 0.009155 | -0.07782 | 0.050354 | 0.045776 | -0.18768 | -0.10986 | -0.050354 | -0.11444 | -0.16479 | 0.10528 | -0.013733 | -0.3067 | -0.14191 | 0.032043 | 123.0469 | 122.9462 | 58.136 | -123.0743 | 123.1018 | 123.0286 | 58.1268 | -123.1613
507.6875 | 123.0835 | -58.2092 | 64.7873 | 0.40025 | 0.034871 | 0.058151 | 0.023226 | 0.050193 | 0.016503 | -0.0018323 | 0.41841 | -0.00050244 | 0.063737 | 0.074439 | 0.0034971 | -0.001173 | 64.7049 | -58.2092 | -0.14191 | -58.4518 | 64.7919 | -58.2687 | -58.3054 | -58.2092 | -0.09613 | -58.7173 | 64.8148 | 64.7324 | -58.3237 | -58.4015 | -0.059509 | -0.09613 | 0.004578 | 0 | -0.24261 | -0.14648 | -0.082397 | -0.11444 | -0.19226 | 0.027466 | 0 | -0.50812 | -0.31586 | -0.054931 | 123.0011 | 122.9141 | 58.0673 | -123.0927 | 123.024 | 122.9416 | 58.1131 | -123.1888
508.6406 | 123.1522 | -58.2138 | 64.7781 | 0.3087 | 0.040211 | 0.072037 | 0.018954 | 0.050193 | 0.0058221 | -0.0050373 | 0.26582 | -0.0079794 | 0.066941 | 0.057349 | 0.0056341 | -0.010786 | 64.7415 | -58.1589 | -0.07782 | -58.4198 | 64.8468 | -58.2504 | -58.3237 | -58.2275 | -0.027466 | -58.5114 | 64.8193 | 64.8102 | -58.3008 | -58.3557 | -0.036621 | -0.10986 | 0.068665 | 0.054931 | -0.20599 | -0.096131 | -0.036621 | -0.086975 | -0.14191 | 0.041199 | -0.013733 | -0.29755 | -0.15564 | 0.032044 | 123.0606 | 122.9553 | 58.136 | -123.1018 | 123.0331 | 123.024 | 58.1863 | -123.1338
509.6406 | 123.1247 | -58.2092 | 64.7873 | 0.27818 | 0.034871 | 0.06456 | 0.033908 | 0.065146 | 0.0047541 | -0.0093093 | 0.26582 | -0.0026384 | 0.063737 | 0.070167 | 0.016315 | -0.007581 | 64.7324 | -58.168 | -0.07782 | -58.4198 | 64.8285 | -58.2367 | -58.3191 | -58.2184 | -0.022888 | -58.5068 | 64.8422 | 64.801 | -58.3191 | -58.3786 | -0.027465 | -0.10986 | 0.041199 | 0.041199 | -0.21057 | -0.10071 | -0.054931 | -0.10986 | -0.16937 | 0.054932 | -0.009155 | -0.29755 | -0.12817 | 0.013733 | 123.0377 | 122.9416 | 58.1314 | -123.1064 | 123.0515 | 123.0103 | 58.1863 | -123.1659
510.6406 | 123.1934 | -58.1863 | 64.769 | 0.049296 | 0.016713 | 0.072037 | 0.018954 | 0.057669 | 0.0036861 | -0.0039683 | -0.71074 | -0.0079794 | 0.066941 | 0.053077 | 0.0024291 | -0.009718 | 64.7919 | -58.1268 | 0.036621 | -58.5251 | 64.801 | -58.2596 | -58.287 | -58.1772 | 0.064087 | -58.461 | 64.856 | 64.7964 | -58.2962 | -58.3649 | -0.073243 | -0.10071 | 0.032043 | 0.059509 | -0.33874 | -0.23804 | 0.022888 | -0.10986 | -0.17853 | 0.086975 | 0.009155 | -0.27466 | -0.096131 | 0.027466 | 122.9874 | 122.9782 | 58.223 | -123.056 | 123.0423 | 122.9828 | 58.2504 | -123.1338
511.6406 | 123.1522 | -58.1726 | 64.7781 | 0.034038 | 0.035939 | 0.06456 | 0.017886 | 0.064078 | -0.00058594 | -0.012513 | 2.7072 | -0.011183 | 0.070146 | 0.059485 | 0.00029315 | -0.011854 | 64.7873 | -58.0902 | -0.009155 | -58.3923 | 64.8331 | -58.2275 | -58.3054 | -58.1223 | 0.036621 | -58.4564 | 64.8376 | 64.801 | -58.2779 | -58.3878 | -0.054932 | -0.13275 | 0.054932 | 0.082397 | -0.21973 | -0.086975 | 0.009155 | -0.10529 | -0.21515 | 0.059509 | 0.050354 | -0.28381 | -0.068665 | 0.022888 | 123.0057 | 122.9599 | 58.1635 | -123.0835 | 123.0103 | 122.9736 | 58.2092 | -123.1659
512.6406 | 123.1155 | -58.2138 | 64.7598 | 0.11033 | 0.028462 | 0.079513 | 0.025363 | 0.059806 | 0.0058221 | -0.0071733 | 0.28108 | -0.01866 | 0.064805 | 0.049872 | -0.0029109 | -0.009718 | 64.7736 | -58.136 | -0.059509 | -58.4106 | 64.8285 | -58.2321 | -58.2962 | -58.1863 | -0.004578 | -58.5022 | 64.8422 | 64.8102 | -58.3099 | -58.3832 | -0.018311 | -0.082398 | 0.068664 | 0.07782 | -0.19684 | -0.11444 | 0.013733 | -0.096131 | -0.16937 | 0.082397 | 0.027466 | -0.28839 | -0.11902 | 0.050354 | 123.0423 | 122.9874 | 58.1543 | -123.056 | 123.056 | 123.024 | 58.2092 | -123.143
513.6406 | 123.0972 | -58.2367 | 64.7781 | 0.24766 | 0.02419 | 0.06456 | 0.014682 | 0.055533 | 0.0068901 | -0.018922 | 0.082718 | -0.010115 | 0.066941 | 0.059485 | -0.0029109 | -0.007581 | 64.7369 | -58.2001 | -0.09613 | -58.4244 | 64.8239 | -58.2458 | -58.2962 | -58.2642 | -0.10071 | -58.5571 | 64.8468 | 64.7827 | -58.3237 | -58.4015 | -0.009156 | -0.05951 | 0.045777 | 0.036621 | -0.18768 | -0.12817 | -0.041199 | -0.086975 | -0.16479 | 0.068665 | -0.027466 | -0.32044 | -0.15564 | 0.004578 | 123.0606 | 122.9736 | 58.1406 | -123.0743 | 123.0835 | 123.0194 | 58.136 | -123.1796
514.6406 | 123.1155 | -58.223 | 64.7827 | 0.29344 | 0.038075 | 0.062424 | 0.034976 | 0.064078 | -0.00058594 | -0.011445 | 0.11323 | -0.0069114 | 0.088304 | 0.053077 | 0.0056341 | -0.015058 | 64.7232 | -58.1909 | -0.09613 | -58.429 | 64.8376 | -58.2321 | -58.3099 | -58.2367 | -0.11902 | -58.5434 | 64.8605 | 64.8056 | -58.3237 | -58.4061 | -0.009156 | -0.086976 | 0.054931 | 0.032043 | -0.20599 | -0.11902 | -0.059509 | -0.10071 | -0.18311 | 0.07782 | -0.013733 | -0.32044 | -0.13733 | 0.022888 | 123.0606 | 122.9462 | 58.1268 | -123.0927 | 123.0835 | 123.0286 | 58.1039 | -123.1888
515.6406 | 123.0927 | -58.2367 | 64.7781 | 0.20188 | 0.025258 | 0.065628 | 0.018954 | 0.064078 | -0.0037909 | -0.011445 | 0.26582 | -0.012251 | 0.061601 | 0.057349 | 0.014179 | -0.019331 | 64.7461 | -58.1818 | -0.10529 | -58.4198 | 64.8331 | -58.255 | -58.3237 | -58.2047 | -0.036621 | -58.5251 | 64.856 | 64.7964 | -58.3099 | -58.3694 | -0.018311 | -0.086975 | 0.054932 | 0.054931 | -0.18311 | -0.096131 | -0.032043 | -0.073243 | -0.13275 | 0.07782 | 0.032043 | -0.28839 | -0.15564 | 0.018311 | 123.0698 | 122.9828 | 58.1314 | -123.1018 | 123.0927 | 123.0331 | 58.2001 | -123.1476
516.6406 | 123.1018 | -58.2092 | 64.7781 | 0.20188 | 0.047688 | 0.074173 | 0.039248 | 0.058738 | 0.010095 | -0.0061053 | 0.28108 | -0.0026384 | 0.071214 | 0.056281 | -0.0029109 | -0.011854 | 64.7507 | -58.1772 | -0.07782 | -58.4152 | 64.8285 | -58.2413 | -58.3099 | -58.2321 | -0.032043 | -58.5205 | 64.8514 | 64.8331 | -58.3191 | -58.3878 | -0.032043 | -0.10071 | 0.050354 | 0.032044 | -0.20599 | -0.10529 | -0.027466 | -0.10986 | -0.17853 | 0.073242 | -0.022888 | -0.31128 | -0.13275 | 0.054932 | 123.0377 | 122.9599 | 58.1314 | -123.0881 | 123.0606 | 123.0423 | 58.1772 | -123.1659
517.6406 | 123.1201 | -58.2001 | 64.7598 | 0.20188 | 0.035939 | 0.070968 | 0.017886 | 0.056601 | 0.0068901 | -0.021058 | -0.085129 | -0.01332 | 0.065873 | 0.060554 | 0.0088381 | -0.01399 | 64.888 | -58.1497 | -0.050354 | -58.3786 | 64.8193 | -58.2321 | -58.3099 | -58.1543 | 0.036621 | -58.461 | 64.8468 | 64.7964 | -58.2962 | -58.3557 | -0.032044 | -0.10986 | 0.059509 | 0.050354 | -0.17853 | -0.068664 | 0.12817 | -0.096131 | -0.15564 | 0.086975 | 0.045776 | -0.26093 | -0.10529 | 0.036621 | 123.0194 | 123.0881 | 58.1497 | -123.0698 | 123.0469 | 122.9965 | 58.2367 | -123.1155
518.6406 | 123.1934 | -58.1772 | 64.8102 | 0.095073 | 0.035939 | 0.067764 | 0.022158 | 0.065146 | 0.0090271 | -0.011445 | 0.41841 | -0.0047754 | 0.070146 | 0.046668 | 0.0056341 | -0.01399 | 64.7964 | -58.1131 | -0.16022 | -58.4061 | 64.8102 | -58.2321 | -58.2733 | -58.1589 | 0.045776 | -58.4564 | 64.8376 | 64.801 | -58.2825 | -58.3649 | -0.054932 | -0.09613 | 0 | 0.064087 | -0.22888 | -0.13275 | -0.013733 | -0.10529 | -0.18768 | 0.027465 | 0.01831 | -0.27924 | -0.091553 | -0.009156 | 122.9874 | 122.9736 | 58.017 | -123.0835 | 123.0148 | 122.9782 | 58.223 | -123.175
519.6406 | 123.1155 | -58.2138 | 64.7644 | 0.18663 | 0.025258 | 0.062424 | 0.027499 | 0.051261 | 0.0058221 | 0.00030367 | 0.28108 | -0.010115 | 0.060533 | 0.047736 | 0.00029315 | -0.020399 | 64.7415 | -58.1406 | -0.073242 | -58.3969 | 64.8148 | -58.2413 | -58.3145 | -58.1955 | -0.018311 | -58.493 | 64.856 | 64.7781 | -58.3145 | -58.3878 | -0.027466 | -0.10071 | 0.050354 | 0.073242 | -0.18311 | -0.082398 | -0.022888 | -0.10071 | -0.17395 | 0.091553 | 0.01831 | -0.27924 | -0.10529 | 0.013733 | 123.0286 | 122.9553 | 58.1406 | -123.0789 | 123.0698 | 122.9919 | 58.1955 | -123.1522
520.6406 | 123.0515 | -58.2275 | 64.7964 | 0.38499 | 0.035939 | 0.05281 | 0.024295 | 0.046988 | 0.0079581 | -0.012513 | 0.37263 | -0.01332 | 0.066941 | 0.042396 | 0.0088381 | -0.016126 | 64.7141 | -58.2458 | -0.13275 | -58.4702 | 64.8193 | -58.2596 | -58.3191 | -58.2504 | -0.091553 | -58.5617 | 64.8148 | 64.7919 | -58.3054 | -58.3969 | -0.032044 | -0.091553 | 0.022888 | -0.018311 | -0.24262 | -0.15106 | -0.082398 | -0.07782 | -0.16937 | 0.01831 | -0.022888 | -0.33417 | -0.16479 | -0.004578 | 123.0469 | 122.9416 | 58.0948 | -123.1155 | 123.0423 | 123.0194 | 58.136 | -123.1934
521.6406 | 123.1064 | -58.2321 | 64.7827 | 0.26292 | 0.045552 | 0.063492 | 0.030703 | 0.052329 | 0.016503 | -0.010377 | 0.17427 | -0.010115 | 0.066941 | 0.050941 | 0.0077701 | -0.015058 | 64.7278 | -58.2092 | -0.10071 | -58.461 | 64.8285 | -58.2733 | -58.3145 | -58.2504 | -0.10529 | -58.5526 | 64.8331 | 64.801 | -58.342 | -58.3923 | -0.041198 | -0.082397 | 0.045776 | 0.022888 | -0.22888 | -0.14648 | -0.054932 | -0.10986 | -0.16022 | 0.050354 | -0.01831 | -0.32043 | -0.16022 | 0.01831 | 123.0606 | 122.9599 | 58.1314 | -123.0972 | 123.0652 | 123.0331 | 58.1268 | -123.175
522.6406 | 123.1155 | -58.2321 | 64.7507 | 0.24766 | 0.041279 | 0.062424 | 0.018954 | 0.055533 | 0.0090271 | -0.011445 | 0.60152 | -0.012251 | 0.059465 | 0.056281 | 0.0077701 | -0.016126 | 64.7095 | -58.1909 | -0.10071 | -58.4244 | 64.8193 | -58.2687 | -58.3191 | -58.2733 | -0.073242 | -58.5434 | 64.8285 | 64.8056 | -58.3191 | -58.3969 | -0.036621 | -0.086975 | 0.068665 | 0.041199 | -0.19226 | -0.10529 | -0.041198 | -0.086975 | -0.16479 | 0.07782 | -0.041198 | -0.31128 | -0.14648 | 0.054932 | 123.0515 | 122.9416 | 58.1314 | -123.0698 | 123.0606 | 123.0377 | 58.1589 | -123.1476
523.6406 | 123.0927 | -58.223 | 64.769 | 0.2324 | 0.023121 | 0.073105 | 0.029635 | 0.051261 | 0.0047541 | -0.013582 | 0.22005 | -0.0079794 | 0.065873 | 0.061622 | -0.0050469 | -0.010786 | 64.7278 | -58.2092 | -0.10071 | -58.429 | 64.8285 | -58.2504 | -58.3008 | -58.2504 | -0.086975 | -58.548 | 64.8651 | 64.801 | -58.3282 | -58.3923 | -0.027466 | -0.07782 | 0.059509 | 0.013732 | -0.20599 | -0.12817 | -0.041199 | -0.10529 | -0.16937 | 0.09613 | -0.027466 | -0.32501 | -0.15564 | 0.032043 | 123.0515 | 122.9507 | 58.1223 | -123.0698 | 123.0881 | 123.024 | 58.136 | -123.1613
524.6406 | 123.1293 | -58.2047 | 64.7873 | 0.11033 | 0.039143 | 0.078445 | 0.023226 | 0.052329 | 0.0068901 | -0.013582 | 0.32686 | -0.0090474 | 0.065873 | 0.056281 | 0.0056341 | -0.00865 | 64.769 | -58.1223 | -0.059509 | -58.4061 | 64.8331 | -58.2504 | -58.287 | -58.2001 | -0.018311 | -58.493 | 64.8697 | 64.8239 | -58.3008 | -58.3557 | -0.045776 | -0.082397 | 0.045777 | 0.082398 | -0.20142 | -0.11902 | -0.01831 | -0.09613 | -0.15106 | 0.082398 | 0.004578 | -0.28839 | -0.13733 | 0.036622 | 123.0377 | 122.9736 | 58.1451 | -123.0743 | 123.0743 | 123.0286 | 58.1863 | -123.143
525.6406 | 123.1201 | -58.1909 | 64.7827 | 0.15611 | 0.031666 | 0.066696 | 0.014682 | 0.060874 | 0.010095 | -0.012513 | 0.22005 | -0.010115 | 0.072282 | 0.052009 | -0.00077485 | -0.027876 | 64.7598 | -58.1451 | -0.050354 | -58.4015 | 64.8056 | -58.2458 | -58.3054 | -58.1863 | -0.004578 | -58.4793 | 64.8651 | 64.8102 | -58.3237 | -58.3557 | -0.054932 | -0.11444 | 0.022888 | 0.045776 | -0.21057 | -0.09613 | -0.022888 | -0.13275 | -0.16479 | 0.082397 | 0.004578 | -0.28839 | -0.1236 | 0.027466 | 122.9965 | 122.9507 | 58.1406 | -123.0881 | 123.056 | 123.0011 | 58.1863 | -123.1384
526.6406 | 123.1201 | -58.2321 | 64.7873 | 0.33921 | 0.027394 | 0.065628 | 0.023226 | 0.057669 | 0.0015501 | -0.013582 | 0.097976 | -0.0079794 | 0.074418 | 0.0456 | 0.0034971 | -0.006513 | 64.7324 | -58.2092 | -0.11444 | -58.4381 | 64.8285 | -58.2504 | -58.3099 | -58.2321 | -0.09613 | -58.5342 | 64.8697 | 64.8102 | -58.3191 | -58.3878 | -0.01831 | -0.07782 | 0.041199 | 0.022888 | -0.20599 | -0.12817 | -0.054931 | -0.086975 | -0.15564 | 0.082398 | 0 | -0.30212 | -0.14648 | 0.022889 | 123.0606 | 122.9645 | 58.1177 | -123.0972 | 123.1018 | 123.0423 | 58.136 | -123.175
527.6406 | 123.1064 | -58.2092 | 64.7873 | 0.4918 | 0.030598 | 0.048538 | 0.023226 | 0.049125 | 0.0036861 | -0.015718 | 0.44893 | -0.0037074 | 0.065873 | 0.060554 | 0.0088381 | 0.015917 | 64.7278 | -58.2138 | -0.15564 | -58.4427 | 64.8331 | -58.2413 | -58.3328 | -58.3557 | -0.11444 | -58.3191 | 64.8468 | 64.7964 | -58.3237 | -58.3878 | -0.032043 | -0.1236 | 0.045777 | -0.004577 | -0.23346 | -0.10986 | -0.059509 | -0.11444 | -0.17853 | 0.05951 | -0.14648 | -0.10986 | 0.068664 | 0.009156 | 123.0423 | 122.937 | 58.0536 | -123.1201 | 123.056 | 123.0057 | 58.0948 | -123.175
528.6406 | 123.1659 | -58.2001 | 64.7873 | 0.44602 | 0.047688 | 0.0699 | 0.042453 | 0.051261 | 0.0068901 | -0.018922 | 0.4947 | -0.01866 | 0.063737 | 0.059485 | -0.0029109 | -0.009718 | 64.7141 | -58.2138 | -0.13275 | -58.4564 | 64.8102 | -58.2642 | -58.3145 | -58.1772 | -0.47607 | -58.6395 | 64.7781 | 64.7781 | -58.3282 | -58.3694 | -0.064087 | -0.11444 | 0.022889 | -0.013733 | -0.25635 | -0.14191 | -0.073242 | -0.12817 | -0.16937 | -0.009155 | 0.022888 | -0.43945 | -0.27008 | -0.009155 | 123.0103 | 122.9141 | 58.0673 | -123.1018 | 122.9782 | 122.9782 | 57.724 | -123.1567
529.6406 | 123.1705 | -58.2184 | 64.769 | 0.4918 | 0.032734 | 0.062424 | 0.02109 | 0.046988 | 0.0068901 | -0.0082413 | 0.46419 | -0.017592 | 0.066941 | 0.047736 | -0.0050469 | -0.011854 | 64.7049 | -58.2092 | -0.15106 | -58.4473 | 64.8239 | -58.2825 | -58.342 | -58.2275 | -0.073242 | -58.5297 | 64.856 | 64.7827 | -58.3328 | -58.4198 | -0.064087 | -0.1236 | 0.054932 | 0.009155 | -0.22888 | -0.10529 | -0.064087 | -0.11444 | -0.20142 | 0.086975 | -0.009155 | -0.31128 | -0.10986 | 0.013733 | 123.0423 | 122.9233 | 58.0673 | -123.111 | 123.0743 | 123.0011 | 58.1451 | -123.1888
530.6406 | 123.111 | -58.2275 | 64.6957 | 0.38499 | 0.035939 | 0.073105 | 0.020022 | 0.067282 | 0.0036861 | -0.01465 | 0.52522 | -0.0079794 | 0.081895 | 0.043464 | 0.00029315 | -0.011854 | 64.6683 | -58.255 | -0.14191 | -58.4564 | 64.8239 | -58.2504 | -58.3145 | -58.2184 | -0.086975 | -58.5251 | 64.8376 | 64.7964 | -58.3237 | -58.3969 | -0.022888 | -0.086975 | 0.12817 | -0.027466 | -0.22888 | -0.14191 | -0.027466 | -0.09613 | -0.16937 | 0.14191 | 0.009155 | -0.29755 | -0.12817 | 0.10071 | 123.0515 | 122.8958 | 58.0856 | -123.0103 | 123.0652 | 123.024 | 58.1406 | -123.0927
531.6406 | 123.111 | -58.2092 | 64.7781 | 0.46128 | 0.039143 | 0.078445 | 0.024295 | 0.052329 | 0.0068901 | -0.015718 | 0.47945 | -0.010115 | 0.07335 | 0.056281 | 0.0034971 | -0.019331 | 64.6912 | -58.2642 | -0.14648 | -58.4335 | 64.8148 | -58.2458 | -58.3099 | -58.2184 | -0.09613 | -58.5159 | 64.8285 | 64.7964 | -58.3237 | -58.3878 | -0.036621 | -0.10071 | 0.036621 | -0.054931 | -0.2243 | -0.1236 | -0.086975 | -0.11444 | -0.17853 | 0.050354 | -0.009155 | -0.3067 | -0.12817 | 0.018311 | 123.024 | 122.9004 | 58.0627 | -123.0881 | 123.0377 | 123.0057 | 58.1131 | -123.1659
532.6406 | 123.111 | -58.1955 | 64.7873 | 0.3087 | 0.048756 | 0.059219 | 0.018954 | 0.052329 | -0.0059269 | -0.018922 | 0.2353 | -0.0026384 | 0.07335 | 0.060554 | 0.0067021 | -0.018263 | 64.7369 | -58.1726 | -0.086975 | -58.4061 | 64.8331 | -58.2458 | -58.2962 | -58.2001 | -0.036621 | -58.5022 | 64.8651 | 64.8102 | -58.3054 | -58.374 | -0.050354 | -0.10071 | 0.045777 | 0.022889 | -0.21057 | -0.10986 | -0.050354 | -0.10986 | -0.17853 | 0.07782 | -0.004577 | -0.3067 | -0.12817 | 0.022889 | 123.0286 | 122.9324 | 58.1085 | -123.0835 | 123.0606 | 123.0057 | 58.1589 | -123.1613
533.6406 | 123.1842 | -58.1726 | 64.7598 | 0.21714 | -0.013195 | 0.074173 | 0.0018638 | 0.053397 | -0.034766 | -0.023195 | 0.40315 | -0.026137 | 0.03917 | 0.044532 | 0.0013611 | -0.00865 | 64.7278 | -58.1177 | -0.054932 | -58.3832 | 64.8056 | -58.2092 | -58.2779 | -58.1635 | -0.013733 | -58.2504 | 64.8422 | 64.8102 | -58.2779 | -58.3466 | -0.036622 | -0.10529 | 0.045776 | 0.054931 | -0.21057 | -0.10529 | -0.032044 | -0.10529 | -0.17395 | 0.082397 | 0.009155 | -0.07782 | 0.096131 | 0.050354 | 122.9782 | 122.9004 | 58.1177 | -123.0377 | 123.0148 | 122.9828 | 58.1589 | -123.1064
534.6406 | 123.1293 | -58.2047 | 64.7507 | 0.46128 | 0.035939 | 0.0699 | 0.033908 | 0.057669 | 0.0015501 | -0.016786 | 1.4102 | -0.014388 | 0.058397 | 0.069098 | 0.022724 | -0.010786 | 64.7049 | -58.4381 | -0.27466 | -58.2596 | 64.8239 | -58.2596 | -58.3237 | -58.2001 | -0.059509 | -58.5159 | 64.8605 | 64.7919 | -58.3191 | -58.3878 | -0.054932 | -0.11902 | 0.073243 | -0.23346 | -0.054932 | 0.064086 | -0.045776 | -0.11444 | -0.18311 | 0.10986 | 0.004578 | -0.31128 | -0.12817 | 0.041199 | 123.0286 | 122.9095 | 57.93 | -123.0743 | 123.0652 | 122.9965 | 58.1451 | -123.1384
535.6406 | 123.1338 | -58.2413 | 64.7644 | 0.52232 | 0.038075 | 0.063492 | 0.028567 | 0.061942 | 0.0026181 | -0.013582 | 1.2729 | 0.0027016 | 0.06801 | 0.040259 | -0.0039789 | -0.018263 | 64.7278 | -58.2184 | -0.14191 | -58.4335 | 64.8102 | -58.2321 | -58.3374 | -58.2321 | -0.022888 | -58.5297 | 64.8697 | 64.8102 | -58.3191 | -58.3786 | 0.009155 | -0.09613 | 0.045777 | 0.022888 | -0.19226 | -0.096131 | -0.036621 | -0.07782 | -0.13733 | 0.10529 | 0.009155 | -0.28839 | -0.15106 | 0.045777 | 123.0515 | 122.9691 | 58.0994 | -123.1018 | 123.111 | 123.0515 | 58.2184 | -123.143
536.6406 | 123.111 | -58.2184 | 64.7644 | 0.44602 | 0.018849 | 0.072037 | 0.025363 | 0.057669 | -0.0037909 | -0.00076433 | 0.44893 | 0.0080426 | 0.065873 | 0.054145 | -0.0093199 | -0.007581 | 64.7278 | -58.2138 | -0.15564 | -58.4473 | 64.8148 | -58.2596 | -58.3145 | -58.1635 | -0.11902 | -58.4335 | 64.8697 | 64.8102 | -58.3099 | -58.3969 | -0.041199 | -0.09613 | 0.050354 | 0.004578 | -0.22888 | -0.13275 | -0.036621 | -0.091553 | -0.17853 | 0.10529 | 0.054932 | -0.21515 | -0.036621 | 0.045777 | 123.0331 | 122.9462 | 58.0627 | -123.0789 | 123.0881 | 123.0286 | 58.0994 | -123.1613
537.6406 | 123.1659 | -58.2321 | 64.7598 | 0.43077 | 0.026326 | 0.066696 | 0.025363 | 0.049125 | 0.0036861 | -0.0071733 | 0.52522 | -0.0058434 | 0.054124 | 0.049872 | 0.0034971 | 0.005236 | 64.7095 | -58.2184 | -0.13733 | -58.4427 | 64.8056 | -58.2321 | -58.3328 | -58.2733 | -0.41657 | -58.3237 | 64.8102 | 64.7964 | -58.3191 | -58.374 | 0 | -0.10071 | 0.045776 | 0.013733 | -0.21057 | -0.10986 | -0.050354 | -0.086975 | -0.14191 | 0.050354 | -0.041198 | -0.091552 | 0.050354 | 0.036621 | 123.0377 | 122.9416 | 58.0948 | -123.0927 | 123.0423 | 123.0286 | 57.8156 | -123.1338
538.6406 | 123.1476 | -58.1726 | 64.7552 | 0.32395 | 0.0028272 | 0.0699 | 0.018954 | 0.046988 | -0.039039 | -0.013582 | 0.41841 | -0.021865 | 0.048783 | 0.043464 | -0.0093199 | -0.00865 | 64.7324 | -58.1131 | -0.045776 | -58.4106 | 64.7598 | -58.2321 | -58.287 | -58.1589 | 0.013733 | -58.4244 | 64.7964 | 64.7781 | -58.2733 | -58.3694 | -0.05951 | -0.11444 | 0.004578 | 0.059509 | -0.23804 | -0.1236 | -0.022888 | -0.10071 | -0.19684 | 0.041199 | 0.013732 | -0.25177 | -0.054931 | 0.022888 | 122.9324 | 122.905 | 58.1268 | -123.0423 | 122.9691 | 122.9507 | 58.1863 | -123.1247
539.6406 | 123.1247 | -58.1955 | 64.7919 | 0.32395 | 0.026326 | 0.083786 | 0.027499 | 0.061942 | 0.028253 | -0.013582 | 0.15901 | -0.011183 | 0.077623 | 0.064826 | 0.0067021 | -0.016126 | 64.7507 | -58.1635 | -0.07782 | -58.4061 | 64.8514 | -58.255 | -58.3145 | -58.2047 | -0.032043 | -58.5297 | 64.8468 | 64.7827 | -58.3374 | -58.374 | -0.059509 | -0.11902 | 0.059509 | 0.032044 | -0.21057 | -0.091553 | -0.041199 | -0.14191 | -0.17853 | 0.054932 | -0.009155 | -0.33417 | -0.15564 | -0.009155 | 123.0469 | 122.9462 | 58.1177 | -123.1064 | 123.0423 | 122.9782 | 58.1635 | -123.1659
540.6406 | 123.1247 | -58.2047 | 64.7552 | -0.65261 | 0.014576 | 0.063492 | 0.02109 | 0.058738 | -0.0016549 | -0.022126 | 0.44893 | -0.011183 | 0.069078 | 0.053077 | -0.00077485 | -0.009718 | 64.6957 | -58.1497 | -0.10071 | -58.4518 | 64.8193 | -58.2458 | -58.3145 | -58.1955 | -0.073242 | -58.5068 | 64.8239 | 64.7964 | -58.3145 | -58.3694 | -0.041199 | -0.10986 | 0.064087 | 0.054932 | -0.24719 | -0.13733 | -0.059509 | -0.10986 | -0.1648 | 0.068665 | 0.009155 | -0.30212 | -0.13733 | 0.041199 | 123.024 | 122.9004 | 58.1039 | -123.0698 | 123.0286 | 123.0011 | 58.1314 | -123.1247
541.6406 | 123.1476 | -58.1818 | 64.7644 | 0.46128 | 0.030598 | 0.062424 | -0.01843 | 0.043784 | 0.0036861 | -0.022126 | 0.89143 | -0.010115 | 0.059465 | 0.0456 | 0.0067021 | -0.003309 | 64.9796 | -58.2687 | -0.16937 | -58.3511 | 64.8331 | -58.255 | -58.3054 | -58.1909 | -0.07782 | -58.5068 | 64.8285 | 64.801 | -58.3191 | -58.3694 | -0.073242 | -0.1236 | 0.068665 | -0.086975 | -0.16937 | -0.045776 | 0.21515 | -0.13733 | -0.18768 | 0.064087 | -0.009155 | -0.32501 | -0.13733 | 0.036621 | 123.0148 | 123.1613 | 58.0124 | -123.0698 | 123.0103 | 122.9828 | 58.1039 | -123.1338
542.6406 | 123.1567 | -58.2001 | 64.7461 | 0.47654 | 0.033803 | 0.057083 | 0.033908 | 0.054465 | 0.0015501 | -0.013582 | -1.1838 | -0.0058434 | 0.053056 | 0.059485 | 0.0024291 | -0.022535 | 64.7278 | -58.2779 | -0.35706 | -58.5709 | 64.7598 | -58.3008 | -58.3054 | -58.2047 | -0.07782 | -58.5022 | 64.8376 | 64.8102 | -58.2962 | -58.3603 | -0.10071 | -0.10529 | 0.013733 | -0.07782 | -0.37079 | -0.2655 | -0.018311 | -0.096131 | -0.16022 | 0.091552 | -0.004578 | -0.30212 | -0.14191 | 0.064087 | 122.9599 | 122.9279 | 57.843 | -123.0515 | 123.0377 | 123.0103 | 58.1223 | -123.1064
543.6406 | 123.23 | -58.1406 | 64.769 | 1.4836 | -0.00037681 | 0.08165 | -0.0045452 | 0.06301 | -0.033698 | -0.025331 | 0.34212 | -0.027205 | 0.028489 | 0.06269 | -0.0029109 | -0.002241 | 64.7369 | -58.0994 | -0.013733 | -58.3832 | 64.7919 | -58.2138 | -58.287 | -58.1223 | 0.086975 | -58.3786 | 64.8148 | 64.7827 | -58.2642 | -58.3282 | -0.073242 | -0.14648 | 0.022888 | 0.041199 | -0.24262 | -0.096131 | -0.032044 | -0.1236 | -0.18768 | 0.045776 | 0.018311 | -0.23804 | -0.050354 | 0.013733 | 122.9324 | 122.8775 | 58.1268 | -123.056 | 122.9553 | 122.9233 | 58.2275 | -123.0972
544.6406 | 123.111 | -58.2092 | 64.7598 | 0.43077 | 0.02953 | 0.08165 | 0.011477 | 0.054465 | 0.016503 | -0.0093093 | 0.43367 | -0.010115 | 0.065873 | 0.084052 | 0.014179 | -0.020399 | 64.7232 | -58.2138 | -0.16479 | -58.4335 | 64.8193 | -58.2642 | -58.3145 | -58.2687 | 0.27924 | -58.5434 | 64.8376 | 64.7781 | -58.3145 | -58.3923 | -0.054931 | -0.10529 | 0.059509 | -0.004577 | -0.2243 | -0.11902 | -0.036621 | -0.10529 | -0.1831 | 0.077819 | -0.059509 | -0.33417 | -0.15106 | 0.01831 | 123.0286 | 122.9324 | 58.0444 | -123.0743 | 123.0469 | 122.9874 | 58.4885 | -123.1522
545.6406 | 123.0652 | -58.2047 | 64.7781 | 0.38499 | 0.033803 | 0.070968 | 0.026431 | 0.055533 | 0.01864 | -0.0050373 | 0.15901 | -0.016524 | 0.061601 | 0.058417 | -0.0039789 | -0.016126 | 64.7415 | -58.1863 | -0.10071 | -58.4106 | 64.8376 | -58.2367 | -58.3054 | -58.2092 | -0.07782 | -58.5526 | 64.8697 | 64.7919 | -58.3282 | -58.3923 | -0.032043 | -0.10071 | 0.059509 | 0.018311 | -0.20599 | -0.10529 | -0.036621 | -0.1236 | -0.18768 | 0.091553 | -0.004578 | -0.3479 | -0.16022 | 0.013733 | 123.0423 | 122.9462 | 58.1039 | -123.0835 | 123.0743 | 122.9965 | 58.1268 | -123.1705
546.6406 | 123.0835 | -58.2321 | 64.7644 | 0.47654 | 0.030598 | 0.074173 | 0.022158 | 0.055533 | 0.0079581 | 0.0024397 | 0.46419 | -0.012251 | 0.05092 | 0.055213 | 0.0013611 | -0.011854 | 64.7186 | -58.2092 | -0.14191 | -58.4473 | 64.8285 | -58.2642 | -58.3374 | -58.2092 | -0.09613 | -58.5159 | 64.8514 | 64.7919 | -58.3328 | -58.3923 | -0.032043 | -0.10528 | 0.064087 | 0.022888 | -0.21515 | -0.10986 | -0.045776 | -0.10071 | -0.16022 | 0.086975 | 0.022888 | -0.28381 | -0.1236 | 0.027466 | 123.0606 | 122.9507 | 58.0902 | -123.1018 | 123.0835 | 123.024 | 58.136 | -123.1567
547.6875 | 123.1064 | -58.1955 | 64.7736 | -0.11855 | 0.027394 | 0.072037 | 0.030703 | 0.053397 | 0.0047541 | -0.017854 | -0.19194 | -0.01332 | 0.065873 | 0.054145 | 0.0045661 | -0.010786 | 64.7873 | -58.1177 | -0.022888 | -58.3466 | 64.8605 | -58.223 | -58.2962 | -58.1406 | 0.07782 | -58.4381 | 64.8605 | 64.8193 | -58.287 | -58.3557 | -0.027465 | -0.10071 | 0.086975 | 0.07782 | -0.15106 | -0.050354 | 0.013732 | -0.091552 | -0.16022 | 0.086975 | 0.054932 | -0.24261 | -0.082397 | 0.045776 | 123.056 | 122.9828 | 58.1726 | -123.0698 | 123.056 | 123.0148 | 58.2733 | -123.1293
548.6406 | 123.1842 | -58.1726 | 64.7644 | 0.26292 | -0.0089218 | 0.077377 | 0.023226 | 0.04058 | -0.043311 | -0.022126 | -2.5723 | -0.017592 | 0.044511 | 0.060554 | -0.011456 | -0.00010499 | 64.7232 | -58.1085 | -0.027466 | -58.3832 | 64.801 | -58.2138 | -58.2825 | -58.1635 | 0.082397 | -58.4061 | 64.8056 | 64.7827 | -58.2779 | -58.3603 | -0.041199 | -0.10986 | 0.036621 | 0.064086 | -0.21057 | -0.10071 | -0.041198 | -0.10529 | -0.18768 | 0.041199 | 0.009155 | -0.23346 | -0.045776 | 0.018311 | 122.9736 | 122.8958 | 58.1451 | -123.0469 | 122.9782 | 122.9553 | 58.255 | -123.1247
549.6406 | 123.1476 | -58.2001 | 64.7369 | 1.8651 | 0.035939 | 0.076309 | 0.029635 | 0.051261 | 0.0079581 | -0.016786 | 0.4947 | -0.01332 | 0.060533 | 0.039191 | 0.01311 | -0.00865 | 64.7873 | -58.2001 | -0.14648 | -58.4106 | 64.8285 | -58.2458 | -58.3328 | -58.1818 | -0.045776 | -58.4976 | 64.8285 | 64.7598 | -58.3282 | -58.3786 | -0.045777 | -0.13275 | 0.091553 | 0 | -0.21057 | -0.07782 | 0.050354 | -0.12817 | -0.17853 | 0.091553 | 0.01831 | -0.29755 | -0.11902 | 0.022889 | 123.0286 | 122.9874 | 58.0536 | -123.0698 | 123.0286 | 122.9599 | 58.1543 | -123.1155
550.6406 | 123.1384 | -58.2001 | 64.7461 | -1.1104 | 0.039143 | 0.085922 | 0.041384 | 0.039511 | 0.011163 | -0.013582 | 0.571 | -0.01332 | 0.069078 | 0.046668 | 0.0045661 | -0.021467 | 64.7644 | -58.1772 | -0.14191 | -58.4427 | 64.8148 | -58.2458 | -58.3328 | -58.1726 | -0.073242 | -58.493 | 64.8376 | 64.7598 | -58.3237 | -58.374 | -0.045777 | -0.13275 | 0.068664 | 0.022888 | -0.24261 | -0.10986 | 0.01831 | -0.1236 | -0.17395 | 0.091552 | 0.027466 | -0.29297 | -0.11902 | 0.013733 | 123.0148 | 122.9645 | 58.0582 | -123.0789 | 123.0377 | 122.9599 | 58.1268 | -123.1201
551.6406 | 123.143 | -58.2092 | 64.7461 | -4.0248 | 0.0028272 | 0.058151 | 0.044589 | 0.057669 | 0.0058221 | -0.021058 | 0.32686 | -0.0090474 | 0.06801 | 0.0456 | 0.0099061 | -0.022535 | 64.7232 | -58.168 | -0.13275 | -58.4335 | 64.8376 | -58.2642 | -58.3008 | -58.1863 | -0.073242 | -58.4793 | 64.8376 | 64.7644 | -58.3008 | -58.3969 | -0.054931 | -0.091552 | 0.091552 | 0.041199 | -0.2243 | -0.13275 | -0.022888 | -0.091552 | -0.18768 | 0.091552 | 0.022889 | -0.27008 | -0.082397 | 0.01831 | 123.0469 | 122.9324 | 58.0765 | -123.0469 | 123.0469 | 122.9736 | 58.136 | -123.143
552.6406 | 123.1567 | -58.223 | 64.769 | 4.2149 | 0.014576 | 0.065628 | 0.023226 | 0.059806 | 0.0068901 | -0.012513 | 0.66255 | -0.01866 | 0.05626 | 0.052009 | 0.010974 | -0.00865 | 64.7781 | -58.2138 | -0.11902 | -58.4152 | 64.8468 | -58.2321 | -58.3099 | -58.1863 | -0.064087 | -58.493 | 64.8148 | 64.7781 | -58.3145 | -58.4015 | -0.009156 | -0.086976 | 0.07782 | 0.009155 | -0.19226 | -0.10529 | 0.009155 | -0.091553 | -0.17853 | 0.045776 | 0.036621 | -0.27008 | -0.091553 | 0.009155 | 123.0698 | 123.0011 | 58.1039 | -123.0789 | 123.0377 | 123.0011 | 58.1589 | -123.1705
553.6406 | 123.262 | -58.1635 | 64.7552 | 0.034038 | -0.019603 | 0.078445 | 0.0082728 | 0.038443 | -0.034766 | -0.013582 | -0.0088351 | -0.019728 | 0.05626 | 0.038123 | -0.0039789 | 0.002032 | 64.8285 | -57.9895 | 0.068665 | -58.3374 | 64.8285 | -58.1955 | -58.2687 | -58.049 | 0.20142 | -58.3145 | 64.7919 | 64.769 | -58.2321 | -58.342 | -0.032044 | -0.10529 | 0.073242 | 0.17395 | -0.17395 | -0.068664 | 0.073242 | -0.068665 | -0.17853 | 0.036621 | 0.11444 | -0.15106 | 0.027466 | 0.013733 | 122.9919 | 122.9919 | 58.2321 | -123.024 | 122.9553 | 122.9324 | 58.3649 | -123.0972
554.6406 | 123.1888 | -58.1635 | 64.7461 | 0.61387 | 0.032734 | 0.065628 | 0.023226 | 0.057669 | 0.0047541 | -0.018922 | 0.55574 | -0.010115 | 0.063737 | 0.053077 | -0.0029109 | -0.015058 | 64.7507 | -58.1589 | -0.09613 | -58.4061 | 64.7964 | -58.2321 | -58.3328 | -58.1497 | 0 | -58.4427 | 64.7873 | 64.7049 | -58.2962 | -58.3466 | -0.068665 | -0.16937 | 0.050354 | 0.004577 | -0.24262 | -0.073242 | 0.004577 | -0.13275 | -0.18311 | 0.041198 | 0.013733 | -0.27924 | -0.09613 | -0.041199 | 122.9599 | 122.9141 | 58.0673 | -123.0789 | 122.9507 | 122.8683 | 58.1635 | -123.0927
555.6406 | 123.2025 | -58.1818 | 64.7552 | 0.53758 | 0.0060322 | 0.068832 | 0.026431 | 0.046988 | 0.0026181 | -0.0050373 | 0.52522 | -0.021865 | 0.057328 | 0.061622 | 0.012042 | -0.019331 | 64.7644 | -58.1589 | -0.10986 | -58.4244 | 64.7964 | -58.2458 | -58.2733 | -58.1314 | -0.027466 | -58.4427 | 64.7964 | 64.7507 | -58.2962 | -58.3649 | -0.064087 | -0.091552 | 0.041199 | 0.022888 | -0.24261 | -0.15106 | 0.009155 | -0.11444 | -0.18311 | 0.041199 | 0.050354 | -0.26093 | -0.07782 | -0.004578 | 122.9782 | 122.9462 | 58.0719 | -123.0286 | 122.9782 | 122.9324 | 58.1543 | -123.1201
556.6406 | 123.2025 | -58.2047 | 64.7141 | 0.50706 | 0.018849 | 0.063492 | 0.022158 | 0.053397 | 0.0047541 | -0.01465 | 0.55574 | -0.027205 | 0.062669 | 0.046668 | 0.0013611 | -0.017194 | 64.7507 | -58.1772 | -0.10986 | -58.4335 | 64.8193 | -58.2596 | -58.3054 | -58.1451 | -0.027466 | -58.4518 | 64.8331 | 64.7461 | -58.2916 | -58.3694 | -0.054932 | -0.10071 | 0.10529 | 0.027466 | -0.22888 | -0.12817 | 0.036621 | -0.086975 | -0.1648 | 0.11902 | 0.059509 | -0.24719 | -0.082397 | 0.032044 | 123.024 | 122.9553 | 58.0948 | -123.0194 | 123.0377 | 122.9507 | 58.1772 | -123.0835
557.6406 | 123.1613 | -58.1909 | 64.7461 | 0.52232 | 0.02953 | 0.062424 | 0.020022 | 0.055533 | 0.0090271 | -0.0061053 | 0.571 | -0.017592 | 0.058397 | 0.070167 | 0.0013611 | -0.010786 | 64.7552 | -58.168 | -0.11444 | -58.429 | 64.8056 | -58.2458 | -58.2962 | -58.1497 | -0.032043 | -58.4793 | 64.7827 | 64.7644 | -58.3008 | -58.3694 | -0.054932 | -0.10529 | 0.059509 | 0.022888 | -0.23804 | -0.13275 | 0.009155 | -0.10986 | -0.17853 | 0.036621 | 0.041199 | -0.28839 | -0.10986 | 0.01831 | 122.9965 | 122.9462 | 58.0765 | -123.0423 | 122.9736 | 122.9553 | 58.1589 | -123.1155
558.6406 | 123.1888 | -58.1635 | 64.7461 | 0.24766 | -0.016399 | 0.080581 | 0.017886 | 0.051261 | -0.033698 | -0.016786 | 0.35738 | -0.030409 | 0.042375 | 0.0456 | 0.0024291 | -0.005445 | 64.7141 | -57.9575 | 0.045776 | -58.4198 | 64.8148 | -58.2092 | -58.2733 | -58.1406 | 0.054932 | -58.4061 | 64.8148 | 64.7827 | -58.2642 | -58.3466 | -0.045777 | -0.10986 | 0.068664 | 0.20599 | -0.25635 | -0.14649 | -0.032044 | -0.10071 | -0.18311 | 0.068664 | 0.022888 | -0.24262 | -0.059509 | 0.036621 | 122.9782 | 122.8775 | 58.2092 | -123.0194 | 122.9782 | 122.9462 | 58.2184 | -123.0927
559.6406 | 123.1567 | -58.2047 | 64.7369 | -0.4695 | 0.017781 | 0.063492 | 0.017886 | 0.058738 | 0.0068901 | -0.013582 | 0.43367 | -0.021865 | 0.057328 | 0.052009 | 0.0013611 | -0.015058 | 64.7186 | -58.1818 | -0.12817 | -58.4381 | 64.8331 | -58.2596 | -58.3282 | -58.1772 | -0.064087 | -58.493 | 64.856 | 64.7507 | -58.3237 | -58.3969 | -0.054932 | -0.1236 | 0.096131 | 0.022888 | -0.23346 | -0.10986 | -0.01831 | -0.11902 | -0.19226 | 0.11902 | 0.027466 | -0.28839 | -0.09613 | 0.013733 | 123.0377 | 122.9233 | 58.0765 | -123.0652 | 123.0606 | 122.9553 | 58.1406 | -123.1338
560.6406 | 123.1934 | -58.1863 | 64.7232 | 0.62913 | 0.02419 | 0.072037 | 0.022158 | 0.050193 | 0.010095 | -0.013582 | 0.52522 | -0.022933 | 0.055192 | 0.042396 | 0.0013611 | -0.021467 | 64.7644 | -58.1268 | -0.09613 | -58.4061 | 64.8193 | -58.2596 | -58.2779 | -58.1177 | 0.018311 | -58.4015 | 64.8056 | 64.7507 | -58.2825 | -58.3328 | -0.073243 | -0.091553 | 0.09613 | 0.059509 | -0.21973 | -0.12817 | 0.041198 | -0.096131 | -0.14648 | 0.082397 | 0.068664 | -0.21515 | -0.068664 | 0.027465 | 123.0057 | 122.9507 | 58.0902 | -123.0011 | 122.9919 | 122.937 | 58.2047 | -123.056
561.6406 | 123.1888 | -58.1955 | 64.7369 | 0.56809 | 0.02419 | 0.078445 | 0.014682 | 0.041648 | 0.015435 | -0.010377 | 0.55574 | -0.016524 | 0.071214 | 0.054145 | 0.015247 | -0.022535 | 64.7461 | -58.168 | -0.10071 | -58.4244 | 64.8056 | -58.2458 | -58.3237 | -58.1223 | -0.018311 | -58.4518 | 64.7919 | 64.7507 | -58.2916 | -58.3649 | -0.050354 | -0.12817 | 0.068665 | 0.027466 | -0.22888 | -0.10071 | 0.009156 | -0.09613 | -0.16937 | 0.054932 | 0.073243 | -0.25635 | -0.086975 | 0.013733 | 123.0011 | 122.9416 | 58.0948 | -123.0606 | 122.9874 | 122.9462 | 58.1772 | -123.1018
562.6406 | 123.1659 | -58.1955 | 64.7232 | 0.61387 | 0.018849 | 0.078445 | 0.022158 | 0.049125 | 0.0047541 | -0.0061053 | 0.54048 | -0.0026384 | 0.063737 | 0.050941 | 0.0024291 | -0.011854 | 64.7415 | -58.1635 | -0.1236 | -58.4335 | 64.8193 | -58.2413 | -58.3008 | -58.1451 | -0.027466 | -58.4793 | 64.8285 | 64.7415 | -58.3099 | -58.374 | -0.045776 | -0.10529 | 0.09613 | 0.032044 | -0.23804 | -0.13275 | 0.01831 | -0.11444 | -0.17853 | 0.10528 | 0.050354 | -0.28381 | -0.10529 | 0.01831 | 123.0148 | 122.937 | 58.0719 | -123.024 | 123.024 | 122.937 | 58.168 | -123.0972
563.6406 | 123.175 | -58.2047 | 64.7324 | -0.10329 | 0.030598 | 0.049606 | 0.03284 | 0.048056 | -0.0059269 | -0.015718 | 0.41841 | -0.0090474 | 0.070146 | 0.063758 | 0.0013611 | -0.017194 | 64.7461 | -58.1863 | -0.14648 | -58.4381 | 64.8376 | -58.2733 | -58.3237 | -58.1635 | -0.068665 | -58.4793 | 64.8285 | 64.7736 | -58.3282 | -58.3832 | -0.068664 | -0.11902 | 0.10529 | 0.018311 | -0.23346 | -0.11444 | 0.013733 | -0.1236 | -0.17853 | 0.09613 | 0.041199 | -0.27466 | -0.09613 | 0.041199 | 123.0423 | 122.9507 | 58.0582 | -123.056 | 123.0331 | 122.9782 | 58.136 | -123.1155
564.6406 | 123.1155 | -58.223 | 64.7278 | 0.36973 | 0.010304 | 0.079513 | 0.023226 | 0.046988 | -0.0037909 | -0.010377 | 0.46419 | -0.0026384 | 0.059465 | 0.053077 | 0.01311 | -0.016126 | 64.7049 | -58.1589 | -0.11902 | -58.4198 | 64.8468 | -58.2687 | -58.3191 | -58.1818 | -0.068665 | -58.5068 | 64.8331 | 64.7552 | -58.3008 | -58.3832 | -0.045777 | -0.096131 | 0.11902 | 0.064086 | -0.19684 | -0.10071 | -0.022888 | -0.07782 | -0.16022 | 0.10529 | 0.041198 | -0.28381 | -0.1236 | 0.027466 | 123.0698 | 122.9279 | 58.1039 | -123.0469 | 123.056 | 122.9782 | 58.1543 | -123.111
565.6406 | 123.0698 | -58.2001 | 64.7552 | 0.36973 | 0.032734 | 0.068832 | 0.026431 | 0.053397 | 0.0026181 | -0.011445 | 0.40315 | -0.021865 | 0.054124 | 0.056281 | 0.012042 | -0.016126 | 64.7095 | -58.2092 | -0.1236 | -58.4518 | 64.8102 | -58.2458 | -58.3328 | -58.2458 | -0.068665 | -58.5526 | 64.8468 | 64.7827 | -58.3099 | -58.4061 | -0.045777 | -0.13275 | 0.054932 | -0.009156 | -0.25177 | -0.11902 | -0.045776 | -0.10986 | -0.20599 | 0.091553 | -0.045777 | -0.35248 | -0.14648 | 0.027466 | 123.0103 | 122.9095 | 58.0765 | -123.0881 | 123.0469 | 122.9828 | 58.1314 | -123.1613
566.6406 | 123.1247 | -58.1818 | 64.769 | 0.50706 | 0.038075 | 0.073105 | 0.026431 | 0.060874 | 0.010095 | -0.012513 | -3.5947 | -0.01332 | 0.069078 | 0.048804 | -0.0039789 | -0.01399 | 64.7095 | -58.1955 | -0.14191 | -58.4473 | 64.8148 | -58.2596 | -58.3099 | -58.1497 | -0.11444 | -58.4656 | 64.856 | 64.7781 | -58.3008 | -58.3511 | -0.07782 | -0.12817 | 0.045776 | -0.013733 | -0.2655 | -0.13733 | -0.059509 | -0.11902 | -0.16937 | 0.086975 | 0.032044 | -0.28381 | -0.11444 | 0.009155 | 122.9965 | 122.8912 | 58.0399 | -123.0789 | 123.0377 | 122.9599 | 58.0673 | -123.1201
567.6406 | 123.1338 | -58.2047 | 64.7781 | 0.46128 | 0.039143 | 0.078445 | 0.028567 | 0.058738 | 0.0036861 | -0.0082413 | 0.41841 | -0.015456 | 0.07335 | 0.041327 | 0.018451 | -0.00865 | 64.6957 | -58.2047 | -0.14191 | -58.4564 | 64.8285 | -58.2458 | -58.3099 | -58.3969 | 0.35248 | -58.4885 | 64.8285 | 64.7644 | -58.3099 | -58.3969 | -0.041199 | -0.10529 | 0.050354 | 0 | -0.25177 | -0.14648 | -0.082397 | -0.10529 | -0.19226 | 0.050354 | -0.19226 | -0.28381 | -0.091552 | -0.013733 | 123.0331 | 122.9004 | 58.0627 | -123.0881 | 123.0331 | 122.9691 | 58.5571 | -123.175
568.6406 | 123.1338 | -58.2001 | 64.7552 | 0.12559 | 0.031666 | 0.066696 | 0.026431 | 0.051261 | 0.0047541 | -0.0082413 | 0.52522 | -0.012251 | 0.069078 | 0.047736 | 0.0099061 | -0.00865 | 64.7324 | -58.1726 | -0.13275 | -58.4244 | 64.8148 | -58.255 | -58.3054 | -58.1726 | -0.059509 | -58.4885 | 64.8331 | 64.769 | -58.3099 | -58.3969 | -0.054932 | -0.10529 | 0.059509 | 0.027466 | -0.2243 | -0.11902 | -0.022888 | -0.10986 | -0.19684 | 0.07782 | 0.027466 | -0.28839 | -0.091552 | 0.013733 | 123.0148 | 122.9324 | 58.0673 | -123.0606 | 123.0331 | 122.9691 | 58.1406 | -123.1522
569.6406 | 123.1476 | -58.2321 | 64.7552 | 2.0482 | 0.027394 | 0.068832 | 0.039248 | 0.055533 | -0.00058594 | -0.023195 | 0.52522 | -0.0090474 | 0.074418 | 0.047736 | 0.0077701 | -0.017194 | 64.7278 | -58.2001 | -0.13733 | -58.4244 | 64.8239 | -58.2596 | -58.3099 | -58.1772 | -0.068665 | -58.4747 | 64.8193 | 64.7644 | -58.3237 | -58.374 | -0.027466 | -0.07782 | 0.068665 | 0.032044 | -0.19226 | -0.11444 | -0.027466 | -0.091552 | -0.14191 | 0.064087 | 0.054932 | -0.24261 | -0.10071 | 0.009155 | 123.056 | 122.9599 | 58.0948 | -123.0652 | 123.0515 | 122.9965 | 58.1635 | -123.1293
570.6875 | 123.1384 | -58.1818 | 64.769 | -0.072774 | 0.032734 | 0.072037 | 0.017886 | 0.054465 | -0.0016549 | -0.010377 | -0.054612 | -0.0079794 | 0.055192 | 0.052009 | 0.012042 | -0.025739 | 64.7827 | -58.1039 | -0.013733 | -58.3878 | 64.8376 | -58.2184 | -58.2962 | -58.1314 | 0.07782 | -58.4244 | 64.8514 | 64.7964 | -58.287 | -58.3511 | -0.036621 | -0.11444 | 0.068664 | 0.07782 | -0.20599 | -0.091552 | 0.013733 | -0.10529 | -0.16937 | 0.082397 | 0.050354 | -0.24261 | -0.073242 | 0.027466 | 123.0194 | 122.9645 | 58.168 | -123.0652 | 123.0331 | 122.9782 | 58.2596 | -123.1201
571.6406 | 123.1659 | -58.223 | 64.7781 | 0.53758 | 0.032734 | 0.063492 | 0.013613 | 0.054465 | 0.00048206 | -0.0029003 | 0.54048 | -0.01332 | 0.071214 | 0.049872 | 0.0024291 | -0.002241 | 64.4028 | -58.0215 | 0.059509 | -58.3649 | 64.8285 | -58.2504 | -58.3054 | -58.1818 | -0.07782 | -58.4976 | 64.8376 | 64.7598 | -58.3054 | -58.3878 | -0.027466 | -0.082398 | 0.050354 | 0.20142 | -0.14191 | -0.059509 | -0.37537 | -0.082398 | -0.1648 | 0.059509 | 0.041198 | -0.27466 | -0.10986 | -0.01831 | 123.0515 | 122.6257 | 58.2825 | -123.0835 | 123.0606 | 122.9828 | 58.1451 | -123.1659
572.6406 | 123.0881 | -58.2184 | 64.7644 | 0.24766 | 0.059437 | 0.070968 | 0.022158 | 0.061942 | 0.0058221 | -0.0018323 | 0.15901 | -0.012251 | 0.071214 | 0.055213 | 0.0088381 | -0.019331 | 64.7095 | -58.1772 | -0.11444 | -58.4335 | 64.8193 | -58.2642 | -58.3145 | -58.2413 | -0.082397 | -58.5434 | 64.8422 | 64.7781 | -58.3099 | -58.3878 | -0.045776 | -0.09613 | 0.054932 | 0.041199 | -0.21515 | -0.11902 | -0.054931 | -0.091553 | -0.16937 | 0.07782 | -0.022888 | -0.32501 | -0.15564 | 0.013733 | 123.0377 | 122.9279 | 58.1039 | -123.0789 | 123.0606 | 122.9965 | 58.136 | -123.1522
573.6406 | 123.0698 | -58.223 | 64.7781 | 0.52232 | 0.020985 | 0.061355 | 0.027499 | 0.061942 | 0.0068901 | -0.0061053 | 0.41841 | 0.0059056 | 0.072282 | 0.046668 | -0.020001 | -0.006513 | 64.7095 | -58.2001 | -0.15564 | -58.429 | 64.8331 | -58.2687 | -58.3145 | -58.1726 | -0.10071 | -58.4198 | 64.8376 | 64.8056 | -58.3099 | -58.3694 | -0.045777 | -0.091553 | 0.054932 | 0.022888 | -0.20599 | -0.11444 | -0.068664 | -0.086976 | -0.14649 | 0.059509 | 0.050354 | -0.19684 | -0.050354 | 0.027466 | 123.056 | 122.9324 | 58.0673 | -123.0927 | 123.0606 | 123.0286 | 58.1223 | -123.1476
574.6406 | 123.143 | -58.2092 | 64.7736 | 0.46128 | 0.02419 | 0.06456 | 0.025363 | 0.049125 | 0.0015501 | -0.0082413 | 0.43367 | -0.014388 | 0.05626 | 0.044532 | 0.0099061 | 0.002032 | 64.6866 | -58.2047 | -0.13733 | -58.4335 | 64.8331 | -58.2504 | -58.3237 | -58.2275 | -0.50354 | -58.3878 | 64.8056 | 64.7598 | -58.3282 | -58.3878 | -0.041198 | -0.11444 | 0.059509 | 0.004578 | -0.2243 | -0.10986 | -0.086976 | -0.11902 | -0.17853 | 0.032043 | -0.01831 | -0.17853 | 0 | -0.013733 | 123.0423 | 122.8958 | 58.0719 | -123.0972 | 123.0148 | 122.9691 | 57.7057 | -123.1613
575.6406 | 123.1842 | -58.1909 | 64.7644 | 0.20188 | 0.035939 | 0.059219 | 0.018954 | 0.064078 | 0.0015501 | -0.01465 | 0.4947 | -0.010115 | 0.079759 | 0.055213 | 0.0077701 | -0.002241 | 64.7232 | -58.1818 | -0.1236 | -58.4335 | 64.856 | -58.2596 | -58.3008 | -58.1772 | -0.064087 | -58.4839 | 64.8376 | 64.7598 | -58.3282 | -58.3969 | -0.068665 | -0.10986 | 0.091553 | 0.009155 | -0.24261 | -0.13275 | -0.041198 | -0.13733 | -0.20599 | 0.073242 | 0.013733 | -0.29297 | -0.086975 | -0.004577 | 123.0469 | 122.9141 | 58.0673 | -123.0652 | 123.0286 | 122.9507 | 58.1268 | -123.1613
576.6406 | 123.1522 | -58.2001 | 64.7461 | -1.2019 | 0.013508 | 0.070968 | 0.036044 | 0.035239 | 0.00048206 | 0.00030367 | 0.41841 | -0.0079794 | 0.055192 | 0.050941 | 0.012042 | -0.010786 | 64.7049 | -58.1818 | -0.14648 | -58.4244 | 64.8376 | -58.2367 | -58.3237 | -58.2092 | -0.059509 | -58.5068 | 64.8514 | 64.7827 | -58.3237 | -58.3694 | -0.036621 | -0.1236 | 0.091552 | 0.01831 | -0.2243 | -0.10071 | -0.041199 | -0.1236 | -0.16937 | 0.10528 | -0.009156 | -0.3067 | -0.13733 | 0.036621 | 123.0377 | 122.905 | 58.0536 | -123.0698 | 123.0515 | 122.9828 | 58.1406 | -123.1155
577.6406 | 123.0835 | -58.2138 | 64.7461 | -3.0177 | 0.015645 | 0.073105 | 0.010409 | 0.059806 | 0.0015501 | -0.0039683 | 0.41841 | -0.021865 | 0.062669 | 0.054145 | 0.0024291 | -0.018263 | 64.6637 | -58.1314 | -0.10529 | -58.4427 | 64.8468 | -58.2321 | -58.3054 | -58.2047 | -0.073242 | -58.493 | 64.8514 | 64.769 | -58.3099 | -58.3786 | -0.018311 | -0.091553 | 0.10071 | 0.082397 | -0.22888 | -0.13733 | -0.082398 | -0.096131 | -0.1648 | 0.10528 | 0.009155 | -0.27924 | -0.11444 | 0.022888 | 123.0606 | 122.8775 | 58.1085 | -123.0515 | 123.0652 | 122.9828 | 58.1406 | -123.1247
578.6406 | 123.1155 | -58.223 | 64.769 | 0.4918 | 0.020985 | 0.074173 | 0.0050688 | 0.057669 | 0.0047541 | -0.029603 | 0.89143 | -0.010115 | 0.057328 | 0.06803 | 0.0056341 | -0.018263 | 65.0345 | -58.287 | -0.20142 | -58.3557 | 64.8468 | -58.2504 | -58.2916 | -58.1955 | -0.054932 | -58.493 | 64.8285 | 64.7873 | -58.3237 | -58.3923 | -0.027466 | -0.068665 | 0.07782 | -0.064087 | -0.13275 | -0.064087 | 0.2655 | -0.10071 | -0.16937 | 0.059509 | 0.027465 | -0.27008 | -0.10071 | 0.01831 | 123.0698 | 123.2574 | 58.0215 | -123.0606 | 123.0515 | 123.0103 | 58.168 | -123.1613
579.6406 | 123.0881 | -58.2367 | 64.7827 | 0.15611 | 0.034871 | 0.062424 | 0.025363 | 0.041648 | 0.020776 | -0.0061053 | 0.40315 | -0.020796 | 0.062669 | 0.043464 | 0.0045661 | -0.019331 | 64.6957 | -58.1955 | -0.12817 | -58.4473 | 64.8514 | -58.2413 | -58.3008 | -58.2504 | -0.10071 | -58.5434 | 64.8743 | 64.7964 | -58.3374 | -58.374 | -0.004578 | -0.064087 | 0.068664 | 0.041198 | -0.21057 | -0.14648 | -0.086975 | -0.10071 | -0.13733 | 0.091553 | -0.013733 | -0.3067 | -0.16937 | 0.013733 | 123.0881 | 122.9324 | 58.1085 | -123.0835 | 123.111 | 123.0331 | 58.136 | -123.1567
580.6406 | 123.1201 | -58.2047 | 64.769 | 0.4918 | 0.034871 | 0.073105 | 0.016818 | 0.055533 | 0.0090271 | -0.010377 | -3.1979 | -0.0069114 | 0.076554 | 0.061622 | -0.0029109 | -0.015058 | 64.7049 | -58.2001 | -0.16022 | -58.4473 | 64.8193 | -58.2779 | -58.342 | -58.2184 | -0.036621 | -58.493 | 64.8468 | 64.8056 | -58.3008 | -58.3832 | -0.073242 | -0.13733 | 0.050354 | 0.004578 | -0.24262 | -0.10529 | -0.064087 | -0.09613 | -0.17853 | 0.07782 | -0.013733 | -0.28839 | -0.10986 | 0.036621 | 123.024 | 122.9095 | 58.0444 | -123.111 | 123.0515 | 123.0103 | 58.168 | -123.1522
581.6406 | 123.1338 | -58.1955 | 64.7141 | 0.59861 | 0.028462 | 0.072037 | 0.025363 | 0.052329 | -0.0016549 | -0.012513 | 0.4947 | -0.01332 | 0.06801 | 0.050941 | 0.0013611 | -0.007581 | 64.7232 | -58.1772 | -0.14191 | -58.4335 | 64.8148 | -58.255 | -58.3099 | -58.1772 | -0.032043 | -58.461 | 64.7964 | 64.769 | -58.3466 | -58.3603 | -0.059509 | -0.11444 | 0.10071 | 0.018311 | -0.23804 | -0.1236 | 0.009156 | -0.15106 | -0.16479 | 0.082398 | 0.018311 | -0.2655 | -0.10071 | 0.054932 | 123.0103 | 122.9187 | 58.0536 | -123.024 | 122.9919 | 122.9645 | 58.1635 | -123.0743
582.6406 | 123.1659 | -58.2184 | 64.7598 | 0.36973 | 0.02953 | 0.06456 | 0.018954 | 0.055533 | 0.0015501 | -0.0029003 | 0.571 | -0.012251 | 0.062669 | 0.056281 | -0.00077485 | -0.019331 | 64.7232 | -58.1772 | -0.12817 | -58.4335 | 64.8376 | -58.2596 | -58.3099 | -58.1726 | -0.050354 | -58.461 | 64.8331 | 64.7964 | -58.3008 | -58.3694 | -0.041199 | -0.091553 | 0.077819 | 0.041199 | -0.21515 | -0.1236 | -0.036621 | -0.082397 | -0.15106 | 0.073242 | 0.045777 | -0.24262 | -0.091553 | 0.036621 | 123.056 | 122.9416 | 58.0902 | -123.0698 | 123.0515 | 123.0148 | 58.168 | -123.1293
583.6406 | 123.1659 | -58.2092 | 64.7461 | 0.20188 | 0.018849 | 0.072037 | 0.014682 | 0.048056 | 0.010095 | -0.017854 | 0.44893 | -0.011183 | 0.079759 | 0.066962 | 0.0024291 | -0.010786 | 64.7095 | -58.1772 | -0.14191 | -58.4244 | 64.8285 | -58.2504 | -58.3282 | -58.1772 | -0.068665 | -58.4885 | 64.8285 | 64.769 | -58.3237 | -58.374 | -0.041198 | -0.11902 | 0.082397 | 0.032044 | -0.21515 | -0.09613 | -0.036621 | -0.11444 | -0.16479 | 0.082397 | 0.032044 | -0.27923 | -0.11444 | 0.022888 | 123.0377 | 122.9187 | 58.0673 | -123.0743 | 123.0377 | 122.9782 | 58.1406 | -123.1201
584.6406 | 123.1201 | -58.2001 | 64.7827 | 2.094 | 0.034871 | 0.079513 | 0.017886 | 0.061942 | -0.0016549 | -0.01465 | 0.54048 | -0.016524 | 0.058397 | 0.056281 | 0.0067021 | -0.010786 | 64.7461 | -58.1772 | -0.15106 | -58.4061 | 64.8148 | -58.2642 | -58.3237 | -58.1909 | -0.073242 | -58.4976 | 64.8376 | 64.7552 | -58.342 | -58.3923 | -0.064087 | -0.1236 | 0.032043 | 0.022888 | -0.20599 | -0.082398 | -0.036621 | -0.14191 | -0.19226 | 0.054931 | 0.009155 | -0.29755 | -0.10529 | -0.027466 | 123.0148 | 122.9462 | 58.049 | -123.1064 | 123.0377 | 122.9553 | 58.1268 | -123.175
585.6406 | 123.1247 | -58.2047 | 64.7552 | 0.46128 | 0.050892 | 0.057083 | 0.047793 | 0.049125 | 0.0047541 | -0.0071733 | 0.34212 | -0.021865 | 0.06801 | 0.056281 | 0.0013611 | -0.01399 | 64.7369 | -58.1451 | -0.15106 | -58.4335 | 64.8331 | -58.2275 | -58.3008 | -58.1955 | -0.054932 | -58.4793 | 64.8331 | 64.7736 | -58.2962 | -58.4106 | -0.022888 | -0.09613 | 0.07782 | 0.059509 | -0.22888 | -0.13275 | -0.018311 | -0.091553 | -0.20599 | 0.07782 | 0.009155 | -0.27466 | -0.068664 | 0.018311 | 123.0377 | 122.9416 | 58.0536 | -123.056 | 123.0377 | 122.9782 | 58.1497 | -123.1659
586.6406 | 123.1018 | -58.2138 | 64.7736 | 0.35447 | 0.027394 | 0.06456 | 0.031771 | 0.054465 | 0.0068901 | -0.0093093 | 0.38789 | -0.011183 | 0.07335 | 0.0456 | 0.0088381 | -0.011854 | 64.7141 | -58.2184 | -0.16479 | -58.4427 | 64.8468 | -58.2504 | -58.3099 | -58.223 | -0.082397 | -58.5068 | 64.856 | 64.7827 | -58.2962 | -58.3786 | -0.036621 | -0.096131 | 0.073242 | -0.004578 | -0.22888 | -0.13275 | -0.05951 | -0.082398 | -0.1648 | 0.082397 | -0.009155 | -0.29297 | -0.12817 | 0.009155 | 123.0606 | 122.9279 | 58.049 | -123.0835 | 123.0698 | 122.9965 | 58.1314 | -123.1522
587.6406 | 123.1338 | -58.2047 | 64.7552 | 0.4918 | 0.043416 | 0.073105 | 0.027499 | 0.054465 | 0.0090271 | -0.0061053 | -0.32927 | -0.0047754 | 0.054124 | 0.043464 | -0.00077485 | -0.011854 | 64.8285 | -58.6761 | -0.40741 | -58.3878 | 64.801 | -58.2733 | -58.3374 | -58.223 | -0.068665 | -58.5114 | 64.8514 | 64.801 | -58.3191 | -58.3603 | -0.068664 | -0.13275 | 0.045776 | -0.4715 | -0.18311 | -0.050354 | 0.073242 | -0.11444 | -0.15564 | 0.09613 | -0.01831 | -0.3067 | -0.15106 | 0.045776 | 123.0057 | 123.0331 | 57.7972 | -123.0927 | 123.056 | 123.0057 | 58.136 | -123.1155
588.6406 | 123.1659 | -58.2001 | 64.7278 | 0.56809 | 0.027394 | 0.065628 | 0.016818 | 0.044852 | 0.00048206 | -0.0093093 | 0.54048 | -0.0026384 | 0.069078 | 0.054145 | 0.015247 | -0.016126 | 64.7278 | -58.1406 | -0.12817 | -58.429 | 64.8285 | -58.2458 | -58.3191 | -58.168 | -0.022888 | -58.4518 | 64.8285 | 64.7598 | -58.2916 | -58.374 | -0.045777 | -0.11902 | 0.10071 | 0.059509 | -0.22888 | -0.10986 | 0 | -0.091553 | -0.17395 | 0.10071 | 0.032043 | -0.25177 | -0.07782 | 0.032044 | 123.0286 | 122.9279 | 58.0719 | -123.0469 | 123.0286 | 122.9599 | 58.1772 | -123.1018
589.6406 | 123.1659 | -58.2047 | 64.7232 | 0.46128 | 0.020985 | 0.05281 | 0.022158 | 0.056601 | -0.00058594 | -0.0050373 | 0.55574 | -0.017592 | 0.070146 | 0.059485 | 0.00029315 | -0.009718 | 64.7095 | -58.1589 | -0.13275 | -58.4152 | 64.8331 | -58.2413 | -58.3282 | -58.1589 | -0.045776 | -58.4747 | 64.8056 | 64.7415 | -58.3099 | -58.3786 | -0.036621 | -0.1236 | 0.10986 | 0.045776 | -0.21057 | -0.086975 | -0.013733 | -0.10529 | -0.17395 | 0.082397 | 0.045776 | -0.27008 | -0.09613 | 0.01831 | 123.0377 | 122.9141 | 58.0719 | -123.0515 | 123.0103 | 122.9462 | 58.1589 | -123.1018
590.6406 | 123.1659 | -58.2001 | 64.7461 | 0.58335 | 0.037007 | 0.0699 | 0.030703 | 0.043784 | -0.0069949 | -0.013582 | 0.63203 | -0.020796 | 0.072282 | 0.061622 | 0.0034971 | -0.021467 | 64.7141 | -58.1772 | -0.13275 | -58.4244 | 64.8193 | -58.2642 | -58.3008 | -58.1635 | -0.054932 | -58.4656 | 64.801 | 64.7644 | -58.3191 | -58.374 | -0.064087 | -0.10071 | 0.073242 | 0.022888 | -0.2243 | -0.1236 | -0.032044 | -0.11902 | -0.17395 | 0.054931 | 0.036621 | -0.2655 | -0.091553 | 0.01831 | 123.0194 | 122.9141 | 58.0673 | -123.0469 | 123.0011 | 122.9645 | 58.1451 | -123.1201
591.6406 | 123.1705 | -58.1726 | 64.7461 | 0.44602 | 0.018849 | 0.066696 | 0.016818 | 0.06301 | 0.0090271 | -0.01999 | 0.55574 | -0.016524 | 0.051988 | 0.063758 | 0.015247 | -0.010786 | 64.7278 | -58.1863 | -0.14191 | -58.429 | 64.8331 | -58.2413 | -58.3145 | -58.1635 | -0.054932 | -58.4747 | 64.8331 | 64.7781 | -58.3191 | -58.3603 | -0.068665 | -0.14191 | 0.086975 | -0.013733 | -0.25635 | -0.11444 | -0.018311 | -0.14648 | -0.18768 | 0.086975 | 0.009155 | -0.30212 | -0.11444 | 0.032043 | 123.0057 | 122.9004 | 58.0307 | -123.0606 | 123.0057 | 122.9507 | 58.1177 | -123.1064
592.6406 | 123.175 | -58.1955 | 64.7507 | 0.44602 | 0.018849 | 0.063492 | 0.013613 | 0.057669 | 0.0068901 | -0.011445 | 0.52522 | -0.01332 | 0.063737 | 0.049872 | 0.01311 | -0.018263 | 64.7232 | -58.1818 | -0.14191 | -58.4381 | 64.801 | -58.2687 | -58.3191 | -58.1543 | -0.050354 | -58.4702 | 64.8422 | 64.769 | -58.3145 | -58.3694 | -0.073242 | -0.1236 | 0.050354 | 0.013733 | -0.24261 | -0.11902 | -0.027465 | -0.11902 | -0.17395 | 0.091553 | 0.041199 | -0.27466 | -0.10071 | 0.018311 | 122.9965 | 122.9187 | 58.0536 | -123.0698 | 123.0377 | 122.9645 | 58.1451 | -123.1201
593.6406 | 123.0881 | -58.1955 | 64.769 | 0.46128 | 0.034871 | 0.073105 | 0.028567 | 0.057669 | 0.011163 | -0.012513 | 0.46419 | -0.015456 | 0.061601 | 0.053077 | 0.0099061 | -0.016126 | 64.7232 | -58.2138 | -0.14191 | -58.4427 | 64.8285 | -58.2367 | -58.3511 | -58.2962 | -0.36621 | -58.287 | 64.7964 | 64.7964 | -58.3054 | -58.3923 | -0.041198 | -0.15564 | 0.059509 | -0.01831 | -0.24719 | -0.091553 | -0.045776 | -0.10986 | -0.19684 | 0.027466 | -0.10071 | -0.091552 | 0.10529 | 0.027466 | 123.024 | 122.9187 | 58.0536 | -123.1201 | 122.9919 | 122.9919 | 57.8293 | -123.1613
594.6406 | 123.1567 | -58.1863 | 64.7461 | 0.55284 | 0.026326 | 0.066696 | 0.016818 | 0.055533 | 0.0058221 | -0.015718 | 0.52522 | -0.024001 | 0.066941 | 0.046668 | 0.0034971 | -0.01399 | 64.7186 | -58.1818 | -0.12817 | -58.4244 | 64.8148 | -58.255 | -58.3145 | -58.1726 | -0.054932 | -58.4976 | 64.8285 | 64.7461 | -58.3282 | -58.3878 | -0.068665 | -0.12817 | 0.068664 | 0.004577 | -0.23804 | -0.10986 | -0.027466 | -0.14191 | -0.20142 | 0.082397 | 0.013733 | -0.31128 | -0.10986 | 0 | 123.0011 | 122.905 | 58.0582 | -123.0606 | 123.0148 | 122.9324 | 58.1314 | -123.1338
595.6406 | 123.2437 | -58.2001 | 64.7278 | 0.62913 | 0.028462 | 0.070968 | 0.020022 | 0.050193 | -0.011268 | -0.017854 | 0.99824 | -0.014388 | 0.055192 | 0.041327 | 0.0056341 | -0.00865 | 64.7598 | -58.1223 | -0.07782 | -58.3786 | 64.7644 | -58.255 | -58.3191 | -58.1131 | 0.018311 | -58.4198 | 64.801 | 64.7552 | -58.2962 | -58.3603 | -0.054932 | -0.11902 | 0.036621 | 0.07782 | -0.17853 | -0.059509 | 0.032044 | -0.096131 | -0.16022 | 0.073242 | 0.086975 | -0.21973 | -0.059509 | 0.027466 | 122.9645 | 122.9599 | 58.1223 | -123.0469 | 123.0011 | 122.9553 | 58.2184 | -123.0881
596.6406 | 123.2391 | -58.1451 | 64.7141 | 0.59861 | 0.025258 | 0.0699 | 0.025363 | 0.067282 | 0.00048206 | -0.016786 | 0.37263 | -0.01866 | 0.061601 | 0.044532 | 0.0056341 | -0.009718 | 64.7644 | -58.1268 | -0.082397 | -58.3878 | 64.801 | -58.2504 | -58.2916 | -58.1131 | 0.018311 | -58.4061 | 64.7964 | 64.7461 | -58.2962 | -58.3603 | -0.10529 | -0.14648 | 0.086975 | 0.018311 | -0.24261 | -0.09613 | 0.050354 | -0.15106 | -0.21515 | 0.082398 | 0.032044 | -0.26093 | -0.045776 | 0.032044 | 122.9462 | 122.9095 | 58.0627 | -123.0057 | 122.9416 | 122.8912 | 58.1635 | -123.0743
597.6406 | 123.23 | -58.1909 | 64.7278 | 0.58335 | 0.022053 | 0.067764 | 0.027499 | 0.057669 | 0.0026181 | -0.028535 | 0.54048 | -0.01866 | 0.045579 | 0.047736 | 0.0024291 | -0.007581 | 64.769 | -58.1223 | -0.091553 | -58.3969 | 64.7919 | -58.2275 | -58.2825 | -58.1085 | 0.022888 | -58.4061 | 64.7827 | 64.769 | -58.2916 | -58.342 | -0.036621 | -0.091553 | 0.064087 | 0.068665 | -0.20599 | -0.11444 | 0.041199 | -0.10071 | -0.15106 | 0.054932 | 0.082397 | -0.21515 | -0.064087 | 0.041199 | 122.9828 | 122.9599 | 58.0994 | -123.0103 | 122.9736 | 122.9599 | 58.2138 | -123.0698
598.6406 | 123.2025 | -58.168 | 64.7186 | 0.61387 | 0.026326 | 0.068832 | 0.012545 | 0.053397 | 0.0015501 | -0.023195 | 0.50996 | -0.020796 | 0.061601 | 0.053077 | -0.00077485 | -0.015058 | 64.7598 | -58.1131 | -0.091553 | -58.3878 | 64.801 | -58.2138 | -58.3008 | -58.1177 | 0.032043 | -58.4244 | 64.8102 | 64.7552 | -58.2962 | -58.3694 | -0.045776 | -0.13275 | 0.082397 | 0.054932 | -0.21973 | -0.086975 | 0.041199 | -0.12817 | -0.20142 | 0.091553 | 0.050354 | -0.25635 | -0.054931 | 0.036621 | 122.9691 | 122.9279 | 58.0765 | -123.0194 | 122.9782 | 122.9233 | 58.2001 | -123.0881
599.6406 | 123.2346 | -58.1543 | 64.7232 | 0.69017 | 0.027394 | 0.066696 | 0.011477 | 0.053397 | 0.0036861 | -0.015718 | 0.58626 | -0.032546 | 0.060533 | 0.058417 | 0.0013611 | -0.010786 | 64.7369 | -58.1223 | -0.082397 | -58.4152 | 64.8148 | -58.2458 | -58.2779 | -58.1314 | 0.027466 | -58.3969 | 64.7873 | 64.7232 | -58.3099 | -58.3694 | -0.091553 | -0.1236 | 0.091552 | 0.032044 | -0.26093 | -0.13733 | 0.013732 | -0.15564 | -0.21515 | 0.064086 | 0.022888 | -0.24262 | -0.027466 | 0 | 122.9691 | 122.8912 | 58.0719 | -123.0011 | 122.9416 | 122.8775 | 58.1818 | -123.0927
600.6406 | 123.1567 | -58.1909 | 64.7415 | -1.736 | 0.025258 | 0.078445 | 0.016818 | 0.067282 | 0.0090271 | -0.018922 | 0.38789 | -0.012251 | 0.062669 | 0.056281 | -0.00077485 | -0.012922 | 64.7095 | -58.1863 | -0.14191 | -58.429 | 64.8468 | -58.255 | -58.2962 | -58.1772 | -0.064087 | -58.4839 | 64.8422 | 64.7781 | -58.2916 | -58.4015 | -0.064087 | -0.10529 | 0.10529 | 0.004578 | -0.23804 | -0.13275 | -0.032043 | -0.10071 | -0.21057 | 0.10071 | 0.013733 | -0.29297 | -0.082398 | 0.036621 | 123.0377 | 122.9004 | 58.049 | -123.0377 | 123.0331 | 122.9691 | 58.1268 | -123.143
601.6406 | 123.2162 | -58.1772 | 64.7278 | 0.65965 | 0.032734 | 0.072037 | 0.03284 | 0.054465 | 0.0036861 | -0.0039683 | 0.571 | -0.015456 | 0.055192 | 0.037055 | 0.0088381 | -0.00865 | 64.7644 | -58.1406 | -0.086975 | -58.4015 | 64.801 | -58.2275 | -58.2962 | -58.1177 | 0.013733 | -58.4106 | 64.7873 | 64.7369 | -58.3099 | -58.3466 | -0.050354 | -0.11902 | 0.073242 | 0.036621 | -0.2243 | -0.10528 | 0.036621 | -0.13275 | -0.16937 | 0.059509 | 0.059509 | -0.23346 | -0.064087 | 0.009155 | 122.9782 | 122.9416 | 58.0902 | -123.024 | 122.9645 | 122.9141 | 58.1909 | -123.0743
602.6406 | 123.2574 | -58.1543 | 64.7186 | 0.58335 | 0.017781 | 0.0699 | 0.02109 | 0.069419 | -0.019813 | -0.012513 | 0.63203 | -0.020796 | 0.063737 | 0.056281 | 0.0067021 | -0.010786 | 64.7827 | -58.0673 | -0.032043 | -58.3511 | 64.7827 | -58.2367 | -58.2779 | -58.049 | -0.21973 | -58.461 | 64.7369 | 64.7324 | -58.3054 | -58.3557 | -0.082397 | -0.1236 | 0.064087 | 0.086975 | -0.19684 | -0.073242 | 0.064087 | -0.15106 | -0.20142 | 0.01831 | 0.10529 | -0.3067 | -0.10529 | 0.013733 | 122.937 | 122.937 | 58.1223 | -122.9965 | 122.8912 | 122.8867 | 57.9346 | -123.0743
603.6406 | 123.2666 | -58.1589 | 64.7369 | 0.52232 | 0.02953 | 0.067764 | 0.018954 | 0.056601 | -0.0048589 | -0.018922 | 0.58626 | -0.022933 | 0.054124 | 0.053077 | 0.0024291 | -0.020399 | 64.7919 | -58.0765 | -0.027466 | -58.3694 | 64.7598 | -58.2321 | -58.2733 | -58.0811 | -0.10986 | -58.5617 | 64.7644 | 64.6912 | -58.3099 | -58.3511 | -0.073242 | -0.11444 | 0.022889 | 0.082398 | -0.21057 | -0.096131 | 0.054932 | -0.15106 | -0.19226 | 0.027466 | 0.07782 | -0.40283 | -0.21057 | -0.045776 | 122.9187 | 122.9507 | 58.1314 | -123.0103 | 122.9233 | 122.85 | 58.049 | -123.0881
604.6406 | 123.2071 | -58.1589 | 64.7095 | 0.58335 | 0.01244 | 0.066696 | 0.033908 | 0.071555 | -0.0037909 | -0.017854 | 0.63203 | -0.020796 | 0.065873 | 0.040259 | 0.0024291 | -0.018263 | 64.8056 | -58.0719 | -0.045776 | -58.3557 | 64.7552 | -58.2184 | -58.3008 | -58.0902 | 0.036621 | -58.4793 | 64.769 | 64.682 | -58.3282 | -58.3786 | -0.059509 | -0.14191 | 0.045776 | 0.086976 | -0.19684 | -0.054932 | 0.09613 | -0.16937 | -0.21973 | 0.059509 | 0.068665 | -0.32043 | -0.10071 | -0.027466 | 122.9141 | 122.9645 | 58.1131 | -123.0103 | 122.9279 | 122.8409 | 58.1955 | -123.0881
605.6406 | 123.3124 | -58.1909 | 64.7095 | 0.61387 | 0.018849 | 0.060287 | 0.012545 | 0.054465 | 0.0036861 | -0.017854 | 0.58626 | -0.025069 | 0.053056 | 0.038123 | 0.0077701 | -0.017194 | 64.8148 | -58.0673 | -0.032043 | -58.3603 | 64.7736 | -58.2275 | -58.287 | -58.1039 | 0.045776 | -58.3969 | 64.7919 | 64.7278 | -58.3099 | -58.4015 | -0.036621 | -0.09613 | 0.064087 | 0.1236 | -0.16937 | -0.073243 | 0.10528 | -0.11902 | -0.21057 | 0.082397 | 0.086975 | -0.20599 | 0.004577 | 0.01831 | 122.9645 | 123.0057 | 58.1589 | -122.9965 | 122.9828 | 122.9187 | 58.2367 | -123.111
606.6406 | 123.2391 | -58.1818 | 64.7049 | 0.65965 | 0.027394 | 0.066696 | 0.013613 | 0.069419 | 0.0015501 | -0.0093093 | 0.54048 | -0.0090474 | 0.058397 | 0.049872 | 0.017383 | -0.023603 | 64.7781 | -58.1451 | -0.10986 | -58.4015 | 64.8239 | -58.2367 | -58.3145 | -58.0994 | 0 | -58.429 | 64.7964 | 64.7141 | -58.3099 | -58.3557 | -0.054931 | -0.13275 | 0.11902 | 0.036621 | -0.21973 | -0.086975 | 0.073242 | -0.12817 | -0.17395 | 0.091553 | 0.082398 | -0.24719 | -0.073242 | 0.009155 | 123.0057 | 122.9599 | 58.0719 | -123.0194 | 122.9782 | 122.8958 | 58.1818 | -123.0606
607.6406 | 123.2025 | -58.1909 | 64.7095 | 0.55284 | 0.014576 | 0.067764 | 0.014682 | 0.052329 | 0.010095 | -0.025331 | 0.571 | -0.011183 | 0.05092 | 0.043464 | 0.01311 | -0.017194 | 64.7552 | -58.136 | -0.11444 | -58.4106 | 64.8056 | -58.2321 | -58.287 | -58.1177 | 0.009155 | -58.4335 | 64.8193 | 64.7415 | -58.3008 | -58.3603 | -0.041199 | -0.09613 | 0.09613 | 0.054932 | -0.21973 | -0.1236 | 0.045776 | -0.10986 | -0.16937 | 0.10986 | 0.073242 | -0.24261 | -0.073242 | 0.032043 | 122.9965 | 122.9462 | 58.0765 | -122.9965 | 123.0103 | 122.9324 | 58.2001 | -123.0698
608.6406 | 123.2437 | -58.1818 | 64.7278 | 0.72068 | 0.023121 | 0.062424 | 0.020022 | 0.064078 | -0.0059269 | -0.013582 | 0.571 | -0.030409 | 0.054124 | 0.061622 | -0.00077485 | -0.016126 | 64.7964 | -58.0444 | -0.045776 | -58.3466 | 64.7873 | -58.2275 | -58.3099 | -58.1039 | 0.027466 | -58.3878 | 64.8102 | 64.7186 | -58.3008 | -58.3694 | -0.045776 | -0.12817 | 0.059509 | 0.13733 | -0.1648 | -0.036621 | 0.068665 | -0.11902 | -0.18768 | 0.082398 | 0.07782 | -0.20599 | -0.01831 | -0.009155 | 122.9691 | 122.9782 | 58.136 | -123.0377 | 122.9919 | 122.9004 | 58.2092 | -123.0972
609.6406 | 123.2208 | -58.168 | 64.7186 | -2.4684 | 0.013508 | 0.063492 | 0.022158 | 0.057669 | -0.0069949 | -0.015718 | 0.38789 | -0.016524 | 0.049852 | 0.052009 | 0.0067021 | -0.006513 | 64.7827 | -58.0215 | -0.027466 | -58.374 | 64.7736 | -58.1955 | -58.2916 | -58.0902 | 0.041199 | -58.3786 | 64.7827 | 64.7278 | -58.2916 | -58.374 | -0.027466 | -0.1236 | 0.054932 | 0.14648 | -0.20599 | -0.082397 | 0.064087 | -0.1236 | -0.20599 | 0.064087 | 0.07782 | -0.21057 | -0.004578 | 0.009155 | 122.9416 | 122.9507 | 58.1406 | -123.0103 | 122.9507 | 122.8958 | 58.2092 | -123.0927
610.6406 | 123.1934 | -58.1635 | 64.7232 | 2.9027 | 0.013508 | 0.067764 | 0.027499 | 0.054465 | -0.0069949 | -0.027467 | 0.52522 | -0.019728 | 0.05626 | 0.050941 | 0.0077701 | -0.023603 | 64.8514 | -58.0582 | -0.022888 | -58.3466 | 64.7827 | -58.2275 | -58.2596 | -58.0994 | 0.045776 | -58.3878 | 64.7964 | 64.7415 | -58.3054 | -58.3374 | -0.064087 | -0.096131 | 0.059509 | 0.10529 | -0.18311 | -0.086975 | 0.12817 | -0.14191 | -0.17395 | 0.073242 | 0.064087 | -0.2243 | -0.050354 | 0.01831 | 122.9462 | 123.0148 | 58.1406 | -122.9828 | 122.9599 | 122.905 | 58.2092 | -123.0606
611.6406 | 123.2162 | -58.1635 | 64.7186 | 0.50706 | 0.0049632 | 0.074173 | 0.00079576 | 0.056601 | -0.016608 | -0.024263 | 0.90669 | -0.016524 | 0.042375 | 0.0456 | 0.00029315 | -0.009718 | 64.9704 | -58.1223 | -0.041199 | -58.3099 | 64.7919 | -58.2001 | -58.2687 | -58.0948 | 0.041199 | -58.3923 | 64.7781 | 64.7278 | -58.3099 | -58.342 | -0.036621 | -0.10529 | 0.073242 | 0.041199 | -0.14648 | -0.041199 | 0.25177 | -0.14648 | -0.17853 | 0.059509 | 0.068664 | -0.22888 | -0.050354 | 0.009155 | 122.9553 | 123.1338 | 58.1223 | -122.9874 | 122.9416 | 122.8912 | 58.2047 | -123.0606
612.6406 | 123.262 | -58.1497 | 64.7278 | 0.58335 | -0.0035808 | 0.077377 | 0.025363 | 0.050193 | 0.0015501 | -0.01999 | 0.78462 | -0.019728 | 0.062669 | 0.038123 | 0.0099061 | -0.026808 | 64.6271 | -58.0124 | 0.059509 | -58.3145 | 64.7781 | -58.2413 | -58.2687 | -58.0856 | 0.036621 | -58.3832 | 64.7873 | 64.6912 | -58.3145 | -58.3603 | -0.091553 | -0.11902 | 0.050354 | 0.13733 | -0.1648 | -0.045776 | -0.10071 | -0.1648 | -0.21057 | 0.059509 | 0.064087 | -0.23346 | -0.022888 | -0.036621 | 122.9279 | 122.7768 | 58.2092 | -122.9965 | 122.937 | 122.8409 | 58.1863 | -123.0881
613.6406 | 123.262 | -58.1635 | 64.7049 | 0.47654 | 0.020985 | 0.082718 | 0.022158 | 0.061942 | 0.012231 | -0.0093093 | 0.50996 | -0.014388 | 0.054124 | 0.041327 | 0.014179 | -0.020399 | 64.8422 | -58.0582 | -0.064087 | -58.3557 | 64.7873 | -58.2321 | -58.2962 | -58.0673 | 0.027466 | -58.4106 | 64.7827 | 64.6866 | -58.2825 | -58.3649 | -0.068665 | -0.13275 | 0.082397 | 0.10529 | -0.19226 | -0.059509 | 0.13733 | -0.11902 | -0.20142 | 0.07782 | 0.09613 | -0.24719 | -0.045777 | -0.018311 | 122.9507 | 123.0057 | 58.0994 | -123.0011 | 122.9462 | 122.85 | 58.1909 | -123.0698
614.6406 | 123.2162 | -58.168 | 64.7141 | 0.56809 | 0.020985 | 0.072037 | 0.026431 | 0.06301 | -0.0037909 | -0.013582 | 0.63203 | -0.015456 | 0.061601 | 0.049872 | 0.0067021 | -0.012922 | 64.7736 | -58.0765 | -0.045776 | -58.3511 | 64.8102 | -58.2367 | -58.2825 | -58.0856 | 0.032043 | -58.3969 | 64.8056 | 64.7095 | -58.2962 | -58.3649 | -0.068664 | -0.11444 | 0.096131 | 0.091553 | -0.1831 | -0.068664 | 0.05951 | -0.12817 | -0.19684 | 0.091553 | 0.082398 | -0.22888 | -0.032044 | -0.004577 | 122.9782 | 122.9416 | 58.1223 | -122.9965 | 122.9736 | 122.8775 | 58.2001 | -123.0789
615.6406 | 123.2208 | -58.1726 | 64.7049 | 0.55284 | 0.037007 | 0.062424 | 0.017886 | 0.064078 | -0.0037909 | -0.011445 | 3.1345 | -0.0090474 | 0.060533 | 0.052009 | 0.0056341 | -0.019331 | 64.8102 | -58.0399 | -0.032043 | -58.374 | 64.7827 | -58.2275 | -58.2779 | -58.0994 | 0.13275 | -58.3969 | 64.769 | 64.7415 | -58.2596 | -58.342 | -0.054932 | -0.10529 | 0.07782 | 0.13275 | -0.20142 | -0.09613 | 0.10529 | -0.086976 | -0.16937 | 0.064087 | 0.073242 | -0.22431 | -0.054932 | 0.036621 | 122.9553 | 122.9828 | 58.1406 | -122.9828 | 122.9416 | 122.9141 | 58.3054 | -123.0469
616.6406 | 123.2071 | -58.1543 | 64.7461 | 0.50706 | 0.016713 | 0.066696 | 0.011477 | 0.056601 | -0.0091309 | -0.012513 | 0.571 | -0.017592 | 0.05092 | 0.043464 | 0.0013611 | -0.016126 | 64.7873 | -58.0536 | -0.027466 | -58.3832 | 64.7781 | -58.2184 | -58.2779 | -58.1131 | 0.022888 | -58.4152 | 64.8056 | 64.7232 | -58.287 | -58.3786 | -0.064087 | -0.1236 | 0.032043 | 0.10071 | -0.22888 | -0.10529 | 0.041198 | -0.13275 | -0.2243 | 0.059509 | 0.041199 | -0.26093 | -0.036621 | -0.022888 | 122.9324 | 122.9416 | 58.1268 | -123.024 | 122.9599 | 122.8775 | 58.1772 | -123.1247
617.6406 | 123.1567 | -58.1863 | 64.7415 | 0.32395 | 0.014576 | 0.06456 | 0.031771 | 0.056601 | -0.0059269 | -0.021058 | 0.4947 | -0.027205 | 0.05626 | 0.040259 | -0.0029109 | -0.020399 | 64.7919 | -58.0582 | -0.041199 | -58.374 | 64.7781 | -58.223 | -58.287 | -58.0948 | 0.032043 | -58.4106 | 64.8102 | 64.7232 | -58.2733 | -58.3603 | -0.036621 | -0.10071 | 0.036621 | 0.12817 | -0.18768 | -0.086975 | 0.050354 | -0.086975 | -0.17395 | 0.068665 | 0.091552 | -0.22431 | -0.050354 | -0.01831 | 122.9645 | 122.9782 | 58.1451 | -123.0286 | 122.9965 | 122.9095 | 58.2184 | -123.1018
618.6406 | 123.1705 | -58.1497 | 64.7369 | 0.50706 | 0.033803 | 0.0699 | 0.02109 | 0.048056 | 0.00048206 | -0.010377 | 0.52522 | -0.01866 | 0.05626 | 0.056281 | 0.0034971 | -0.020399 | 64.7873 | -58.0399 | -0.018311 | -58.3694 | 64.7827 | -58.2367 | -58.287 | -58.0856 | 0.032043 | -58.4106 | 64.8148 | 64.7095 | -58.3008 | -58.3466 | -0.086975 | -0.13733 | 0.045777 | 0.10986 | -0.21973 | -0.082398 | 0.050354 | -0.15106 | -0.19684 | 0.07782 | 0.064087 | -0.26093 | -0.064087 | -0.027465 | 122.9324 | 122.937 | 58.1314 | -123.024 | 122.9645 | 122.8592 | 58.1818 | -123.0835
619.6406 | 123.2346 | -58.1635 | 64.7324 | 0.36973 | 0.014576 | 0.0699 | 0.020022 | 0.046988 | 0.0026181 | -0.021058 | 0.47945 | -0.011183 | 0.055192 | 0.056281 | 0.0034971 | -0.021467 | 64.801 | -58.049 | -0.032043 | -58.3878 | 64.7873 | -58.1909 | -58.2779 | -58.0856 | 0.036621 | -58.4152 | 64.7873 | 64.7049 | -58.3099 | -58.3557 | -0.027466 | -0.11444 | 0.054931 | 0.11444 | -0.2243 | -0.10986 | 0.068664 | -0.14648 | -0.19226 | 0.054931 | 0.07782 | -0.25177 | -0.059509 | -0.027466 | 122.9507 | 122.9645 | 58.1314 | -123.0103 | 122.9507 | 122.8683 | 58.2001 | -123.0881
620.6406 | 123.2025 | -58.1589 | 64.7369 | 0.53758 | 0.02419 | 0.078445 | 0.020022 | 0.057669 | 0.0058221 | -0.011445 | 0.50996 | -0.024001 | 0.057328 | 0.047736 | 0.010974 | -0.020399 | 64.801 | -58.0444 | -0.041199 | -58.3557 | 64.7736 | -58.2275 | -58.2916 | -58.0948 | 0.054932 | -58.4747 | 64.7964 | 64.6637 | -58.3328 | -58.3878 | -0.068664 | -0.13275 | 0.036622 | 0.11444 | -0.19684 | -0.064087 | 0.064087 | -0.17395 | -0.22888 | 0.05951 | 0.064087 | -0.31586 | -0.086975 | -0.073242 | 122.9324 | 122.9599 | 58.1177 | -123.0286 | 122.9553 | 122.8226 | 58.2138 | -123.1247
621.6406 | 123.3261 | -58.1818 | 64.7324 | 0.59861 | 0.0038952 | 0.068832 | 0.016818 | 0.055533 | 0.017572 | -0.010377 | 0.50996 | -0.022933 | 0.038102 | 0.043464 | 0.0077701 | -0.009718 | 64.8193 | -58.0399 | -0.036621 | -58.3649 | 64.7827 | -58.2413 | -58.287 | -58.0765 | 0.045776 | -58.3923 | 64.8102 | 64.7049 | -58.3008 | -58.4152 | -0.059509 | -0.10529 | 0.050354 | 0.14191 | -0.18311 | -0.07782 | 0.086975 | -0.11902 | -0.23346 | 0.07782 | 0.10529 | -0.21057 | 0.022888 | -0.027466 | 122.9645 | 123.0011 | 58.1451 | -123.0194 | 122.9919 | 122.8867 | 58.2275 | -123.1476
622.6406 | 123.175 | -58.1726 | 64.7369 | 1.0259 | 0.010304 | 0.0699 | 0.014682 | 0.049125 | -0.0048589 | -0.010377 | 0.60152 | -0.027205 | 0.042375 | 0.049872 | 0.0056341 | -0.017194 | 64.7964 | -58.0307 | -0.027466 | -58.374 | 64.7736 | -58.2367 | -58.287 | -58.0856 | 0.041199 | -58.3923 | 64.7781 | 64.7003 | -58.2916 | -58.374 | -0.064087 | -0.11444 | 0.036622 | 0.14191 | -0.20142 | -0.086975 | 0.05951 | -0.11902 | -0.20142 | 0.041199 | 0.086975 | -0.21973 | -0.018311 | -0.036621 | 122.9462 | 122.9691 | 58.1451 | -123.024 | 122.9507 | 122.8729 | 58.2138 | -123.111
623.6406 | 123.2071 | -58.1818 | 64.7415 | 0.50706 | 0.013508 | 0.079513 | 0.017886 | 0.061942 | -0.01554 | -0.013582 | 0.46419 | -0.015456 | 0.055192 | 0.053077 | 0.0034971 | -0.005445 | 64.7598 | -58.0765 | -0.059509 | -58.3969 | 64.8148 | -58.2092 | -58.2825 | -58.1314 | 0.018311 | -58.3969 | 64.8376 | 64.7278 | -58.2687 | -58.3511 | -0.027466 | -0.10071 | 0.073242 | 0.10529 | -0.21515 | -0.11444 | 0.018311 | -0.086975 | -0.16937 | 0.09613 | 0.050354 | -0.21515 | -0.045777 | -0.013733 | 122.9965 | 122.9416 | 58.1223 | -123.024 | 123.0194 | 122.9095 | 58.2001 | -123.0927
624.6875 | 123.0972 | -58.2092 | 64.7781 | 1.0564 | 0.031666 | 0.070968 | 0.014682 | 0.056601 | 0.01864 | 0.00030367 | 0.29634 | -0.0079794 | 0.062669 | 0.058417 | 0.016315 | -0.022535 | 64.7369 | -58.2047 | -0.17395 | -58.4473 | 64.8514 | -58.287 | -58.3282 | -58.1863 | -0.086975 | -58.5114 | 64.8651 | 64.7232 | -58.3328 | -58.3878 | -0.077819 | -0.11902 | 0.073242 | 0.004578 | -0.23804 | -0.11902 | -0.041199 | -0.1236 | -0.17853 | 0.086975 | 0.022889 | -0.30212 | -0.1236 | -0.054931 | 123.0606 | 122.9462 | 58.0353 | -123.1064 | 123.0743 | 122.9324 | 58.1223 | -123.1659
625.6406 | 123.1842 | -58.1589 | 64.7278 | 0.50706 | -0.022808 | 0.074173 | 0.01575 | 0.046988 | -0.0069949 | -0.0082413 | 0.50996 | -0.025069 | 0.042375 | 0.053077 | -0.0082519 | -0.006513 | 64.7507 | -58.0765 | -0.050354 | -58.4015 | 64.7919 | -58.2138 | -58.2779 | -58.1268 | 0.018311 | -58.4198 | 64.7873 | 64.7324 | -58.2687 | -58.3603 | -0.054931 | -0.11902 | 0.064087 | 0.082398 | -0.24261 | -0.1236 | 0.022888 | -0.10986 | -0.20142 | 0.059509 | 0.032044 | -0.26093 | -0.059509 | 0.004578 | 122.9507 | 122.9095 | 58.1085 | -123.0057 | 122.9462 | 122.8912 | 58.1772 | -123.0881
626.6406 | 123.1888 | -58.1909 | 64.7507 | 0.43077 | 0.02419 | 0.078445 | 0.020022 | 0.046988 | -0.0080629 | -0.023195 | 0.4947 | -0.022933 | 0.058397 | 0.047736 | -0.0029109 | -0.012922 | 64.7644 | -58.0765 | -0.059509 | -58.4015 | 64.8102 | -58.2184 | -58.2779 | -58.136 | 0.013733 | -58.4198 | 64.8102 | 64.7232 | -58.3054 | -58.3511 | -0.027466 | -0.086975 | 0.05951 | 0.11444 | -0.21057 | -0.1236 | 0.013733 | -0.11444 | -0.16022 | 0.05951 | 0.054932 | -0.22888 | -0.068665 | -0.027465 | 123.0011 | 122.9553 | 58.1314 | -123.0286 | 123.0011 | 122.9141 | 58.2047 | -123.1018
627.6406 | 123.1888 | -58.1589 | 64.7507 | 0.24766 | -0.0025128 | 0.072037 | 0.018954 | 0.046988 | -0.01554 | -0.025331 | 0.32686 | -0.024001 | 0.051988 | 0.050941 | 0.00029315 | -0.012922 | 64.7598 | -58.0765 | -0.059509 | -58.3786 | 64.7964 | -58.2092 | -58.2367 | -58.1314 | 0.032043 | -58.4061 | 64.8422 | 64.7003 | -58.2825 | -58.3374 | -0.050354 | -0.077819 | 0.045777 | 0.082398 | -0.21973 | -0.14191 | 0.009156 | -0.1236 | -0.17853 | 0.091553 | 0.027466 | -0.24719 | -0.068665 | -0.050354 | 122.9553 | 122.9187 | 58.0994 | -122.9874 | 123.0011 | 122.8592 | 58.1909 | -123.0881
628.6406 | 123.2391 | -58.168 | 64.7324 | 0.52232 | 0.031666 | 0.058151 | -0.0066812 | 0.056601 | -0.0080629 | -0.013582 | 0.4947 | -0.021865 | 0.046647 | 0.047736 | 0.0045661 | -0.012922 | 64.7461 | -57.9529 | 0.018311 | -58.3511 | 64.7827 | -58.223 | -58.2779 | -58.0719 | 0.045776 | -58.374 | 64.801 | 64.7003 | -58.2962 | -58.3603 | -0.054931 | -0.10986 | 0.050354 | 0.21515 | -0.1831 | -0.073242 | 0.013733 | -0.12817 | -0.19226 | 0.068664 | 0.096131 | -0.20599 | -0.013732 | -0.032044 | 122.9507 | 122.9141 | 58.1863 | -123.0103 | 122.9691 | 122.8683 | 58.2138 | -123.0927
629.6406 | 123.2025 | -58.1818 | 64.7552 | 0.29344 | -0.00037681 | 0.074173 | 0.01575 | 0.054465 | -0.0048589 | -0.01465 | 0.37263 | -0.022933 | 0.045579 | 0.055213 | 0.00029315 | -0.012922 | 64.7552 | -58.0765 | -0.068665 | -58.374 | 64.8148 | -58.2184 | -58.2825 | -58.1223 | 0.045776 | -58.4198 | 64.8193 | 64.7141 | -58.2962 | -58.3466 | -0.036621 | -0.10071 | 0.059509 | 0.10529 | -0.19226 | -0.091552 | 0 | -0.11444 | -0.1648 | 0.064087 | 0.05951 | -0.23804 | -0.073242 | -0.041199 | 122.9965 | 122.937 | 58.1131 | -123.0377 | 123.0011 | 122.8958 | 58.2275 | -123.1018
630.6406 | 123.1979 | -58.1589 | 64.7461 | 0.35447 | 0.0071002 | 0.077377 | 0.02109 | 0.052329 | 0.0015501 | -0.016786 | 0.20479 | -0.01332 | 0.049852 | 0.053077 | -0.00077485 | -0.017194 | 64.7736 | -58.0811 | -0.068665 | -58.3694 | 64.8056 | -58.2138 | -58.2916 | -58.1131 | 0.022888 | -58.4198 | 64.8285 | 64.7186 | -58.2779 | -58.3374 | -0.054931 | -0.13275 | 0.059509 | 0.07782 | -0.21057 | -0.07782 | 0.027466 | -0.11902 | -0.17853 | 0.082397 | 0.045777 | -0.26093 | -0.082398 | -0.027466 | 122.9645 | 122.9324 | 58.0902 | -123.0377 | 122.9874 | 122.8775 | 58.1818 | -123.0835
631.6406 | 123.2162 | -58.1818 | 64.7461 | 0.46128 | 0.0071002 | 0.068832 | 0.020022 | 0.046988 | -0.014472 | -0.0093093 | 0.35738 | -0.012251 | 0.040239 | 0.048804 | 0.0077701 | -0.016126 | 64.7644 | -58.0719 | -0.059509 | -58.3878 | 64.7964 | -58.2184 | -58.3099 | -58.1177 | 0.032043 | -58.4152 | 64.8285 | 64.7003 | -58.2825 | -58.3374 | -0.036621 | -0.12817 | 0.050354 | 0.10986 | -0.20599 | -0.077819 | 0.01831 | -0.10071 | -0.15564 | 0.082397 | 0.064087 | -0.23346 | -0.07782 | -0.045777 | 122.9782 | 122.9462 | 58.1223 | -123.056 | 123.0103 | 122.8821 | 58.2138 | -123.0835
632.6406 | 123.1888 | -58.1589 | 64.7507 | 0.43077 | 0.0028272 | 0.076309 | 0.014682 | 0.050193 | -0.013404 | -0.012513 | 0.34212 | -0.020796 | 0.046647 | 0.047736 | -0.0029109 | -0.020399 | 64.7461 | -58.0673 | -0.068665 | -58.3969 | 64.801 | -58.2458 | -58.2825 | -58.1131 | 0.022888 | -58.429 | 64.8331 | 64.7141 | -58.2779 | -58.3282 | -0.086975 | -0.1236 | 0.050354 | 0.091553 | -0.23804 | -0.11444 | -0.004577 | -0.11902 | -0.16937 | 0.082398 | 0.045777 | -0.27008 | -0.10071 | -0.036621 | 122.9599 | 122.905 | 58.0902 | -123.0331 | 122.9919 | 122.8729 | 58.1818 | -123.0789
633.6406 | 123.1522 | -58.1406 | 64.7461 | 0.38499 | 0.0092362 | 0.083786 | 0.02109 | 0.050193 | -0.0037909 | -0.027467 | 0.37263 | -0.019728 | 0.031694 | 0.0456 | 0.0067021 | -0.010786 | 64.7644 | -58.0627 | -0.054932 | -58.3923 | 64.8056 | -58.2275 | -58.3054 | -58.1085 | 0.032043 | -58.4106 | 64.8331 | 64.7095 | -58.287 | -58.3603 | -0.086975 | -0.1648 | 0.059509 | 0.07782 | -0.25177 | -0.086975 | 0.01831 | -0.14648 | -0.21973 | 0.086975 | 0.032043 | -0.27008 | -0.050354 | -0.036621 | 122.9462 | 122.905 | 58.0856 | -123.0515 | 122.9736 | 122.85 | 58.1726 | -123.1064
634.6406 | 123.1888 | -58.1818 | 64.7141 | 0.47654 | 0.0038952 | 0.067764 | 0.010409 | 0.046988 | 0.0079581 | -0.016786 | 0.46419 | -0.017592 | 0.05092 | 0.037055 | 0.0034971 | -0.016126 | 64.7827 | -58.0307 | -0.045776 | -58.3786 | 64.7919 | -58.223 | -58.2916 | -58.0673 | 0.036621 | -58.4106 | 64.7919 | 64.6774 | -58.3054 | -58.3603 | -0.041198 | -0.10986 | 0.07782 | 0.15106 | -0.19684 | -0.086975 | 0.068665 | -0.1236 | -0.17853 | 0.07782 | 0.11444 | -0.22888 | -0.050354 | -0.036621 | 122.9736 | 122.9645 | 58.136 | -123.0057 | 122.9736 | 122.8592 | 58.2184 | -123.0743
635.6406 | 123.1979 | -58.1635 | 64.7415 | 0.47654 | 0.013508 | 0.074173 | 0.013613 | 0.055533 | 0.0015501 | -0.023195 | 0.4947 | -0.024001 | 0.062669 | 0.0456 | 0.014179 | -0.012922 | 64.8193 | -58.049 | -0.027466 | -58.3694 | 64.7827 | -58.223 | -58.2687 | -58.0719 | 0.036621 | -58.3969 | 64.8148 | 64.6912 | -58.2916 | -58.3557 | -0.059509 | -0.10529 | 0.041199 | 0.11444 | -0.20599 | -0.10071 | 0.07782 | -0.12817 | -0.19226 | 0.073242 | 0.091553 | -0.23346 | -0.041199 | -0.050354 | 122.9462 | 122.9828 | 58.136 | -123.0103 | 122.9782 | 122.8546 | 58.2001 | -123.0972
636.6406 | 123.1476 | -58.168 | 64.7598 | 0.27818 | -0.0014448 | 0.083786 | 0.016818 | 0.037375 | -0.0016549 | -0.023195 | 0.28108 | -0.026137 | 0.047715 | 0.041327 | 0.010974 | -0.021467 | 64.7644 | -58.0765 | -0.068665 | -58.3878 | 64.8285 | -58.2275 | -58.2733 | -58.1131 | 0.036621 | -58.4061 | 64.8376 | 64.7324 | -58.287 | -58.3374 | -0.059509 | -0.10528 | 0.068664 | 0.091553 | -0.21973 | -0.11444 | 0.004577 | -0.11902 | -0.16937 | 0.077819 | 0.054932 | -0.23804 | -0.068665 | -0.027466 | 122.9965 | 122.9324 | 58.0994 | -123.0331 | 123.0057 | 122.9004 | 58.2047 | -123.0972
637.6406 | 123.1659 | -58.1726 | 64.7461 | 0.21714 | 0.011372 | 0.0699 | 0.0072048 | 0.059806 | 0.0015501 | -0.016786 | 0.20479 | -0.024001 | 0.044511 | 0.038123 | 0.00029315 | -0.020399 | 64.7736 | -58.0765 | -0.059509 | -58.3832 | 64.8193 | -58.2184 | -58.287 | -58.1131 | 0.036621 | -58.4152 | 64.8285 | 64.7232 | -58.2687 | -58.3557 | -0.045777 | -0.11444 | 0.073242 | 0.09613 | -0.21057 | -0.096131 | 0.027466 | -0.096131 | -0.18311 | 0.082397 | 0.059509 | -0.24262 | -0.059509 | -0.022888 | 122.9919 | 122.9462 | 58.1131 | -123.0331 | 123.0011 | 122.8958 | 58.2092 | -123.1018
638.6406 | 123.2208 | -58.1726 | 64.7507 | 0.43077 | -0.0078538 | 0.077377 | 0.02109 | 0.032035 | -0.0037909 | -0.01465 | 0.35738 | -0.027205 | 0.05092 | 0.069098 | 0.0045661 | -0.027876 | 64.7644 | -58.0627 | -0.07782 | -58.3832 | 64.7964 | -58.2092 | -58.2687 | -58.1085 | 0.041199 | -58.429 | 64.8376 | 64.7049 | -58.2642 | -58.3511 | -0.036622 | -0.096131 | 0.045777 | 0.10986 | -0.21057 | -0.11444 | 0.013733 | -0.091553 | -0.17853 | 0.086975 | 0.064086 | -0.25635 | -0.07782 | -0.045776 | 122.9691 | 122.937 | 58.0948 | -123.0194 | 123.0103 | 122.8775 | 58.2138 | -123.1018
639.6406 | 123.2346 | -58.1772 | 64.7461 | 0.47654 | 0.0071002 | 0.075241 | 0.018954 | 0.04592 | 0.0015501 | -0.026399 | 0.34212 | -0.01866 | 0.05092 | 0.047736 | -0.0050469 | -0.011854 | 64.7507 | -58.0856 | -0.086975 | -58.3832 | 64.7964 | -58.2275 | -58.2916 | -58.1177 | 0.013733 | -58.4106 | 64.8239 | 64.6912 | -58.3008 | -58.342 | -0.050354 | -0.11444 | 0.050354 | 0.091553 | -0.20599 | -0.091553 | 0.004577 | -0.1236 | -0.16479 | 0.07782 | 0.059509 | -0.23346 | -0.068665 | -0.054932 | 122.9736 | 122.9279 | 58.0902 | -123.0377 | 123.0011 | 122.8683 | 58.1909 | -123.0881
640.6406 | 123.1659 | -58.168 | 64.7461 | 0.46128 | -0.0057178 | 0.078445 | 0.03284 | 0.059806 | -0.00058594 | -0.0061053 | 0.3116 | -0.015456 | 0.071214 | 0.050941 | -0.0029109 | -0.024671 | 64.7827 | -58.0948 | -0.068665 | -58.4015 | 64.8102 | -58.223 | -58.2825 | -58.1039 | 0.032043 | -58.4152 | 64.8331 | 64.7186 | -58.2779 | -58.3694 | -0.054931 | -0.11444 | 0.064087 | 0.073242 | -0.23346 | -0.11902 | 0.036621 | -0.10986 | -0.20142 | 0.086975 | 0.064087 | -0.24719 | -0.045776 | -0.027466 | 122.9782 | 122.9507 | 58.0994 | -123.0286 | 123.0011 | 122.8867 | 58.2001 | -123.1155
641.6406 | 123.1979 | -58.1818 | 64.7278 | 0.96482 | -0.0046498 | 0.078445 | 0.025363 | 0.054465 | -0.0059269 | -0.017854 | 0.37263 | -0.017592 | 0.059465 | 0.052009 | 0.010974 | -0.024671 | 64.7919 | -57.9895 | -0.009155 | -58.3649 | 64.8056 | -58.2321 | -58.287 | -58.0719 | 0.032043 | -58.3832 | 64.7919 | 64.6912 | -58.2916 | -58.3557 | -0.050354 | -0.10529 | 0.07782 | 0.19226 | -0.18311 | -0.07782 | 0.064087 | -0.10986 | -0.17395 | 0.064087 | 0.10986 | -0.20142 | -0.027466 | -0.036621 | 122.9874 | 122.9736 | 58.1726 | -123.0148 | 122.9736 | 122.8729 | 58.2138 | -123.0835
642.6406 | 123.2208 | -58.1589 | 64.7461 | 0.53758 | 0.010304 | 0.068832 | 0.023226 | 0.039511 | 0.010095 | 0.0045757 | 1.1508 | -0.021865 | 0.049852 | 0.057349 | 0.0077701 | -0.024671 | 64.7873 | -58.2321 | -0.059509 | -58.255 | 64.7736 | -58.2321 | -58.287 | -58.0856 | 0.064087 | -58.3923 | 64.7827 | 64.7003 | -58.2962 | -58.3557 | -0.073242 | -0.12817 | 0.027466 | -0.073242 | -0.09613 | 0.032043 | 0.041198 | -0.13733 | -0.19684 | 0.036621 | 0.073243 | -0.23346 | -0.036621 | -0.045777 | 122.9324 | 122.9462 | 58.0994 | -123.0331 | 122.9416 | 122.8592 | 58.223 | -123.1018
643.6406 | 123.1979 | -58.168 | 64.7369 | 0.47654 | -0.0014448 | 0.067764 | 0.013613 | 0.043784 | -0.0048589 | -0.022126 | 0.22005 | -0.028273 | 0.046647 | 0.059485 | 0.0077701 | -0.017194 | 64.7507 | -58.0673 | -0.073242 | -58.3786 | 64.8239 | -58.223 | -58.2596 | -58.1223 | 0.036621 | -58.4106 | 64.8239 | 64.7049 | -58.3054 | -58.3466 | -0.054931 | -0.091553 | 0.086976 | 0.10071 | -0.21057 | -0.11902 | 0.013733 | -0.13733 | -0.17853 | 0.086976 | 0.045777 | -0.24262 | -0.064087 | -0.032043 | 122.9919 | 122.9187 | 58.0948 | -122.9965 | 122.9919 | 122.8729 | 58.2047 | -123.0835
644.6406 | 123.1842 | -58.1909 | 64.7552 | 0.47654 | 0.022053 | 0.078445 | 0.013613 | 0.054465 | -0.0027229 | -0.0039683 | 0.32686 | -0.026137 | 0.054124 | 0.064826 | 0.0034971 | -0.016126 | 64.7552 | -58.0765 | -0.064087 | -58.3969 | 64.8331 | -58.2138 | -58.3008 | -58.0948 | 0.027466 | -58.4061 | 64.8376 | 64.6866 | -58.2916 | -58.374 | -0.022888 | -0.10986 | 0.07782 | 0.11444 | -0.20599 | -0.096131 | 0 | -0.10071 | -0.1831 | 0.082397 | 0.09613 | -0.21515 | -0.032044 | -0.068665 | 123.024 | 122.9462 | 58.1268 | -123.056 | 123.0286 | 122.8775 | 58.2184 | -123.1293
645.6406 | 123.1842 | -58.168 | 64.7736 | 0.40025 | 0.0028272 | 0.076309 | 0.02109 | 0.039511 | -0.0037909 | -0.011445 | 0.40315 | -0.020796 | 0.046647 | 0.049872 | 0.0024291 | -0.023603 | 64.7781 | -58.0673 | -0.082397 | -58.3969 | 64.8148 | -58.2321 | -58.2916 | -58.1131 | 0.018311 | -58.4198 | 64.8285 | 64.7095 | -58.2779 | -58.3511 | -0.064087 | -0.1236 | 0.041198 | 0.10071 | -0.22888 | -0.10529 | 0.004577 | -0.10986 | -0.1831 | 0.054931 | 0.054932 | -0.25177 | -0.068665 | -0.064087 | 122.9828 | 122.9462 | 58.0856 | -123.0652 | 122.9965 | 122.8775 | 58.1863 | -123.1247
646.6406 | 123.1796 | -58.1497 | 64.7324 | 0.50706 | -0.0035808 | 0.075241 | 0.016818 | 0.06301 | -0.00058594 | -0.013582 | 0.40315 | -0.014388 | 0.062669 | 0.054145 | 0.0024291 | -0.019331 | 64.7827 | -58.0627 | -0.064087 | -58.3878 | 64.7919 | -58.2413 | -58.287 | -58.0948 | 0.022888 | -58.429 | 64.8193 | 64.7095 | -58.3008 | -58.342 | -0.091553 | -0.13733 | 0.059509 | 0.086975 | -0.23804 | -0.10071 | 0.050354 | -0.15106 | -0.19226 | 0.086975 | 0.054931 | -0.27924 | -0.086975 | -0.022888 | 122.9416 | 122.9324 | 58.0856 | -123.0194 | 122.9691 | 122.8592 | 58.1726 | -123.0743
647.6406 | 123.1979 | -58.1772 | 64.769 | 0.44602 | 0.0049632 | 0.08165 | 0.016818 | 0.058738 | 0.0058221 | -0.013582 | 0.44893 | -0.016524 | 0.034898 | 0.048804 | 0.0024291 | -0.018263 | 64.801 | -58.0536 | -0.059509 | -58.3969 | 64.8056 | -58.2138 | -58.2733 | -58.0811 | 0.022888 | -58.4106 | 64.8331 | 64.7003 | -58.3145 | -58.342 | -0.036621 | -0.09613 | 0.036621 | 0.1236 | -0.21973 | -0.1236 | 0.032043 | -0.13733 | -0.16479 | 0.064087 | 0.09613 | -0.23346 | -0.068665 | -0.068665 | 122.9828 | 122.9782 | 58.1177 | -123.0423 | 123.0103 | 122.8775 | 58.2001 | -123.111
648.6406 | 123.2254 | -58.1635 | 64.7507 | 0.59861 | 0.0060322 | 0.076309 | 0.014682 | 0.052329 | 0.011163 | -0.016786 | 0.067459 | -0.024001 | 0.054124 | 0.047736 | 0.010974 | -0.017194 | 64.8102 | -58.017 | -0.009155 | -58.5114 | 64.7461 | -58.287 | -58.3099 | -58.049 | 0.032043 | -58.3878 | 64.8056 | 64.6957 | -58.2733 | -58.3466 | -0.1236 | -0.14648 | -0.004577 | 0.14648 | -0.3479 | -0.20142 | 0.05951 | -0.10986 | -0.18311 | 0.054932 | 0.11444 | -0.2243 | -0.041198 | -0.054931 | 122.9095 | 122.9736 | 58.1543 | -123.0606 | 122.9691 | 122.8592 | 58.1955 | -123.0972
649.6406 | 123.1796 | -58.168 | 64.7232 | 0.40025 | 0.014576 | 0.056015 | 0.024295 | 0.052329 | 0.0068901 | -0.0039683 | 0.37263 | -0.015456 | 0.05626 | 0.048804 | 0.0099061 | -0.017194 | 64.8056 | -58.017 | -0.050354 | -58.3832 | 64.7873 | -58.223 | -58.2642 | -58.0856 | 0.036621 | -58.4061 | 64.7964 | 64.6729 | -58.2962 | -58.374 | -0.054931 | -0.09613 | 0.064086 | 0.15106 | -0.21515 | -0.11902 | 0.082397 | -0.12817 | -0.20599 | 0.073242 | 0.082398 | -0.23804 | -0.032044 | -0.050354 | 122.9553 | 122.9736 | 58.1177 | -122.9874 | 122.9645 | 122.8409 | 58.2047 | -123.0972
650.6406 | 123.2162 | -58.1818 | 64.7461 | 0.50706 | 0.0049632 | 0.076309 | 0.027499 | 0.041648 | -0.0091309 | -0.011445 | 0.46419 | -0.032546 | 0.053056 | 0.056281 | 0.0034971 | -0.012922 | 64.7644 | -58.0673 | -0.068665 | -58.3923 | 64.7919 | -58.2047 | -58.2779 | -58.1039 | 0.027466 | -58.3969 | 64.8193 | 64.6957 | -58.2642 | -58.3557 | -0.022888 | -0.09613 | 0.045776 | 0.11444 | -0.21057 | -0.11444 | 0.01831 | -0.082397 | -0.17395 | 0.073242 | 0.07782 | -0.21515 | -0.041199 | -0.050354 | 122.9736 | 122.9462 | 58.1131 | -123.024 | 123.0011 | 122.8775 | 58.2092 | -123.1018
651.6406 | 123.2208 | -58.1635 | 64.7415 | 0.44602 | 0.01244 | 0.066696 | 0.010409 | 0.060874 | 0.0036861 | -0.018922 | 0.47945 | -0.017592 | 0.038102 | 0.0456 | 0.0056341 | -0.015058 | 64.7873 | -58.0627 | -0.073242 | -58.3969 | 64.8148 | -58.2413 | -58.2825 | -58.0994 | 0.027466 | -58.4152 | 64.8056 | 64.7095 | -58.3237 | -58.3832 | -0.07782 | -0.11902 | 0.073242 | 0.10071 | -0.23346 | -0.11444 | 0.045776 | -0.16022 | -0.21973 | 0.064087 | 0.064087 | -0.25177 | -0.032043 | -0.032043 | 122.9782 | 122.9507 | 58.0902 | -123.024 | 122.9691 | 122.8729 | 58.1909 | -123.1247
652.6406 | 123.175 | -58.1543 | 64.7278 | 0.47654 | 0.011372 | 0.079513 | 0.024295 | 0.069419 | -0.0069949 | -0.01465 | 0.44893 | -0.01866 | 0.051988 | 0.0456 | 0.019519 | -0.020399 | 64.8056 | -58.049 | -0.064087 | -58.3832 | 64.7552 | -58.223 | -58.2642 | -58.0902 | 0.018311 | -58.4061 | 64.801 | 64.7049 | -58.3054 | -58.3649 | -0.068664 | -0.10986 | 0.027466 | 0.10529 | -0.22888 | -0.11902 | 0.07782 | -0.15106 | -0.21057 | 0.073242 | 0.064087 | -0.25177 | -0.041199 | -0.022888 | 122.9095 | 122.9599 | 58.0902 | -122.9919 | 122.9553 | 122.8592 | 58.1726 | -123.0927
653.6406 | 123.175 | -58.1451 | 64.7232 | 0.36973 | 0.025258 | 0.06456 | 0.017886 | 0.049125 | -0.0037909 | -0.018922 | 0.4947 | -0.019728 | 0.057328 | 0.0456 | 0.0088381 | -0.015058 | 64.7873 | -58.017 | -0.050354 | -58.374 | 64.7736 | -58.2413 | -58.2825 | -58.0902 | 0.036621 | -58.3878 | 64.7964 | 64.6683 | -58.2779 | -58.3603 | -0.09613 | -0.13733 | 0.050354 | 0.12817 | -0.22888 | -0.091552 | 0.064086 | -0.13275 | -0.21515 | 0.073242 | 0.054932 | -0.24261 | -0.027465 | -0.054932 | 122.9187 | 122.9324 | 58.0948 | -123.0057 | 122.9416 | 122.8134 | 58.1818 | -123.0835
654.6406 | 123.2162 | -58.1772 | 64.7552 | 0.44602 | 0.011372 | 0.077377 | 0.026431 | 0.051261 | -0.0048589 | -0.01465 | 0.40315 | -0.028273 | 0.053056 | 0.042396 | 0.0024291 | -0.021467 | 64.7644 | -58.0765 | -0.068665 | -58.374 | 64.8102 | -58.2321 | -58.2916 | -58.1223 | 0.009155 | -58.4152 | 64.8148 | 64.7003 | -58.2733 | -58.3282 | -0.054932 | -0.11444 | 0.054932 | 0.10071 | -0.19684 | -0.082397 | 0.009155 | -0.09613 | -0.15106 | 0.059509 | 0.054932 | -0.23804 | -0.086975 | -0.054932 | 122.9874 | 122.9416 | 58.1085 | -123.0469 | 122.9919 | 122.8775 | 58.1863 | -123.0835
655.6406 | 123.2574 | -58.1726 | 64.7324 | 0.33921 | 0.028462 | 0.06456 | 0.030703 | 0.04592 | 0.030389 | -0.018922 | 0.4947 | -0.012251 | 0.045579 | 0.056281 | 0.018451 | -0.015058 | 64.801 | -58.017 | -0.068665 | -58.3649 | 64.7919 | -58.2367 | -58.3054 | -58.0719 | 0.032043 | -58.3832 | 64.7827 | 64.6774 | -58.3054 | -58.3649 | -0.064087 | -0.13275 | 0.059509 | 0.15564 | -0.19226 | -0.059509 | 0.068664 | -0.13275 | -0.19226 | 0.050354 | 0.10071 | -0.21057 | -0.018311 | -0.054932 | 122.9645 | 122.9736 | 58.1039 | -123.0377 | 122.9553 | 122.85 | 58.2047 | -123.0972
656.6406 | 123.23 | -58.1726 | 64.7186 | 0.56809 | 0.011372 | 0.067764 | 0.025363 | 0.055533 | 0.0026181 | -0.01465 | -0.039353 | -0.0090474 | 0.05626 | 0.052009 | 0.0013611 | -0.015058 | 64.8056 | -58.0124 | 0.013733 | -58.5205 | 64.7552 | -58.2596 | -58.3191 | -58.0261 | 0.036621 | -58.3786 | 64.801 | 64.6912 | -58.2596 | -58.3466 | -0.086976 | -0.14648 | 0.036621 | 0.16022 | -0.3479 | -0.20142 | 0.086975 | -0.086976 | -0.17395 | 0.082397 | 0.14648 | -0.20599 | -0.032043 | -0.027466 | 122.9279 | 122.9782 | 58.1863 | -123.0377 | 122.9736 | 122.8638 | 58.2092 | -123.0652
657.6406 | 123.2071 | -58.168 | 64.7141 | 0.50706 | 0.016713 | 0.058151 | 0.030703 | 0.050193 | -0.0048589 | -0.0061053 | 0.43367 | -0.020796 | 0.041307 | 0.052009 | 0.0034971 | -0.017194 | 64.7964 | -58.0307 | -0.064087 | -58.3832 | 64.7827 | -58.2321 | -58.2596 | -58.1085 | 0.032043 | -58.4015 | 64.7964 | 64.7141 | -58.2916 | -58.3694 | -0.064087 | -0.091553 | 0.068665 | 0.13733 | -0.21515 | -0.1236 | 0.082398 | -0.1236 | -0.20142 | 0.082398 | 0.059509 | -0.23346 | -0.032043 | 0 | 122.9507 | 122.9645 | 58.1039 | -122.9736 | 122.9645 | 122.8821 | 58.2001 | -123.0835
658.6406 | 123.1888 | -58.1772 | 64.7461 | 0.69017 | 0.02419 | 0.067764 | 0.0093408 | 0.058738 | -0.0069949 | -0.018922 | 0.58626 | -0.020796 | 0.044511 | 0.044532 | 0.0088381 | -0.010786 | 64.8239 | -58.0215 | -0.050354 | -58.3832 | 64.7919 | -58.2184 | -58.2779 | -58.0673 | 0.059509 | -58.3969 | 64.8056 | 64.7278 | -58.2916 | -58.374 | -0.041199 | -0.10071 | 0.045776 | 0.15564 | -0.20599 | -0.10529 | 0.07782 | -0.11444 | -0.19684 | 0.059509 | 0.10986 | -0.21973 | -0.022889 | -0.018311 | 122.9691 | 123.0011 | 58.1268 | -123.024 | 122.9828 | 122.905 | 58.2367 | -123.1201
659.6406 | 123.1201 | -58.1726 | 64.8193 | -0.13381 | 0.0049632 | 0.083786 | 0.02109 | 0.061942 | -0.0048589 | -0.012513 | -0.42082 | -0.01866 | 0.053056 | 0.044532 | 0.0056341 | -0.027876 | 64.8285 | -58.0582 | -0.054932 | -58.3878 | 64.8926 | -58.2458 | -58.2825 | -58.1451 | 0.082397 | -58.4518 | 64.92 | 64.7964 | -58.3054 | -58.3603 | -0.073243 | -0.10986 | 0.073242 | 0.11444 | -0.21515 | -0.10529 | 0.009155 | -0.13275 | -0.18768 | 0.10071 | 0.027465 | -0.27924 | -0.091552 | -0.022888 | 123.0652 | 123.0011 | 58.1177 | -123.1018 | 123.0927 | 122.9691 | 58.255 | -123.1796
660.6406 | 123.2346 | -58.1635 | 64.7186 | 0.81224 | 0.013508 | 0.085922 | 0.016818 | 0.057669 | 0.0036861 | -0.010377 | 0.44893 | -0.01866 | 0.046647 | 0.047736 | 0.0045661 | -0.021467 | 64.7873 | -57.9803 | -0.032043 | -58.3557 | 64.7919 | -58.2321 | -58.2596 | -58.0627 | 0.036621 | -58.3786 | 64.8239 | 64.6912 | -58.3099 | -58.3511 | -0.068665 | -0.096131 | 0.073242 | 0.1831 | -0.19226 | -0.09613 | 0.068664 | -0.14648 | -0.18768 | 0.10529 | 0.10071 | -0.21515 | -0.027466 | -0.027466 | 122.9553 | 122.9507 | 58.1314 | -122.9782 | 122.9874 | 122.8546 | 58.2001 | -123.0698
661.6406 | 123.2346 | -58.1635 | 64.7278 | 0.26292 | 0.0017592 | 0.074173 | 0.025363 | 0.042716 | 0.013299 | -0.01999 | 0.571 | -0.015456 | 0.049852 | 0.052009 | 0.0034971 | -0.022535 | 64.8468 | -58.0673 | -0.091553 | -58.3511 | 64.7781 | -58.223 | -58.2687 | -58.0673 | 0.027466 | -58.3832 | 64.7873 | 64.682 | -58.3054 | -58.3694 | -0.059509 | -0.10529 | 0.050354 | 0.09613 | -0.18768 | -0.082397 | 0.11902 | -0.14191 | -0.20599 | 0.059509 | 0.09613 | -0.21973 | -0.013733 | -0.045776 | 122.9416 | 123.0103 | 58.0719 | -122.9965 | 122.9507 | 122.8455 | 58.1909 | -123.0972
662.6406 | 123.2391 | -58.1635 | 64.7324 | 0.50706 | 0.022053 | 0.075241 | 0.01575 | 0.066214 | 0.0068901 | 0.0077807 | 0.52522 | -0.017592 | 0.051988 | 0.059485 | 0.019519 | -0.016126 | 64.7507 | -58.0582 | -0.07782 | -58.3511 | 64.7919 | -58.2092 | -58.3191 | -58.0856 | 0.036621 | -58.3832 | 64.769 | 64.7003 | -58.3099 | -58.3694 | -0.045777 | -0.15564 | 0.059509 | 0.10529 | -0.18768 | -0.032043 | 0.01831 | -0.14648 | -0.20599 | 0.036621 | 0.07782 | -0.21973 | -0.013733 | -0.032044 | 122.9553 | 122.9141 | 58.0856 | -123.0515 | 122.9324 | 122.8638 | 58.2001 | -123.1018
663.6406 | 123.2346 | -58.1772 | 64.7278 | 0.4918 | 0.016713 | 0.0699 | 0.022158 | 0.053397 | 0.0068901 | 0.0045757 | 0.64729 | -0.01332 | 0.064805 | 0.050941 | 0.0067021 | -0.018263 | 64.6133 | -57.9575 | 0.073242 | -58.3191 | 64.7781 | -58.2184 | -58.287 | -58.0811 | 0.041199 | -58.3649 | 64.7964 | 64.7141 | -58.2687 | -58.3557 | -0.041199 | -0.10986 | 0.050354 | 0.21973 | -0.14191 | -0.032044 | -0.11444 | -0.091553 | -0.17853 | 0.068665 | 0.09613 | -0.18768 | -0.009155 | -0.013733 | 122.9553 | 122.7905 | 58.2504 | -123.0148 | 122.9736 | 122.8912 | 58.2184 | -123.0835
664.6406 | 123.111 | -58.1955 | 64.8056 | -0.2101 | 0.017781 | 0.0699 | 0.027499 | 0.049125 | 0.0015501 | -0.0039683 | -0.34453 | -0.015456 | 0.06801 | 0.046668 | -0.0029109 | -0.039625 | 64.769 | -58.0994 | -0.064087 | -58.3832 | 64.8743 | -58.2367 | -58.2733 | -58.0399 | 0.13275 | -58.6121 | 64.9063 | 64.7919 | -58.3145 | -58.3649 | -0.041198 | -0.077819 | 0.068665 | 0.096131 | -0.18768 | -0.10986 | -0.036621 | -0.11902 | -0.16937 | 0.10071 | 0.15564 | -0.41656 | -0.24719 | -0.013733 | 123.0698 | 122.9645 | 58.1314 | -123.0789 | 123.1018 | 122.9874 | 58.3282 | -123.1705
665.6406 | 123.175 | -58.168 | 64.7278 | 0.41551 | 0.016713 | 0.075241 | 0.0061368 | 0.059806 | -0.01554 | -0.0093093 | 0.44893 | -0.025069 | 0.05092 | 0.056281 | 0.0045661 | -0.012922 | 64.7781 | -58.0261 | -0.064087 | -58.3786 | 64.8056 | -58.223 | -58.2825 | -58.1177 | 0.022888 | -58.3878 | 64.8102 | 64.7003 | -58.2962 | -58.3694 | -0.054931 | -0.11444 | 0.07782 | 0.14191 | -0.21057 | -0.09613 | 0.050354 | -0.12817 | -0.20142 | 0.082398 | 0.050354 | -0.21973 | -0.01831 | -0.027466 | 122.9736 | 122.9462 | 58.1039 | -123.0103 | 122.9782 | 122.8683 | 58.1909 | -123.0972
666.6406 | 123.1842 | -58.1635 | 64.7415 | 0.53758 | 0.0017592 | 0.066696 | 0.029635 | 0.055533 | -0.0016549 | -0.011445 | 0.44893 | -0.01866 | 0.062669 | 0.054145 | 0.0024291 | -0.026808 | 64.801 | -58.0627 | -0.086975 | -58.3649 | 64.7919 | -58.2138 | -58.2916 | -58.1039 | 0.018311 | -58.4015 | 64.8102 | 64.7003 | -58.3008 | -58.3557 | -0.050354 | -0.12817 | 0.050354 | 0.10071 | -0.20142 | -0.073242 | 0.059509 | -0.13733 | -0.19226 | 0.068665 | 0.059509 | -0.23804 | -0.045776 | -0.041199 | 122.9553 | 122.9645 | 58.0765 | -123.0331 | 122.9736 | 122.8638 | 58.1818 | -123.0972
667.6406 | 123.2025 | -58.1635 | 64.7369 | 0.52232 | 0.0081682 | 0.065628 | 0.014682 | 0.051261 | -0.00058594 | -0.023195 | 0.55574 | -0.021865 | 0.053056 | 0.058417 | 0.0034971 | -0.012922 | 64.7919 | -58.049 | -0.059509 | -58.3694 | 64.769 | -58.2321 | -58.2779 | -58.1085 | 0.013733 | -58.3969 | 64.8148 | 64.7186 | -58.2733 | -58.3374 | -0.068665 | -0.11444 | 0.032044 | 0.11444 | -0.20599 | -0.091553 | 0.054932 | -0.10986 | -0.17395 | 0.07782 | 0.054931 | -0.23346 | -0.05951 | -0.01831 | 122.9324 | 122.9553 | 58.1039 | -123.0148 | 122.9782 | 122.8821 | 58.1772 | -123.0743
668.6406 | 123.2574 | -58.1314 | 64.7186 | 0.55284 | 0.022053 | 0.075241 | 0.012545 | 0.038443 | -0.0080629 | -0.01999 | 2.9209 | -0.017592 | 0.05092 | 0.044532 | 0.019519 | -0.01399 | 64.8056 | -58.017 | -0.064087 | -58.3511 | 64.7964 | -58.2367 | -58.3008 | -58.0856 | 0.1236 | -58.3878 | 64.7919 | 64.7003 | -58.2916 | -58.3511 | -0.10529 | -0.16937 | 0.07782 | 0.11444 | -0.21973 | -0.050354 | 0.086975 | -0.16022 | -0.21973 | 0.073242 | 0.045777 | -0.25635 | -0.036621 | -0.018311 | 122.9279 | 122.937 | 58.0673 | -123.0194 | 122.9233 | 122.8317 | 58.255 | -123.0698
669.6406 | 123.23 | -58.1451 | 64.7827 | -0.86623 | 0.010304 | 0.063492 | 0.027499 | 0.041648 | 0.00048206 | -0.011445 | -0.26824 | -0.029341 | 0.062669 | 0.053077 | 0.015247 | -0.021467 | 64.8056 | -57.9758 | 0.027466 | -58.342 | 64.8102 | -58.1818 | -58.2733 | -58.0765 | 0.17395 | -58.3466 | 64.8376 | 64.7644 | -58.2733 | -58.3282 | -0.036621 | -0.12817 | 0.027466 | 0.16937 | -0.19684 | -0.068665 | 0.022888 | -0.12817 | -0.1831 | 0.054931 | 0.068665 | -0.20142 | -0.018311 | -0.018311 | 122.9553 | 122.9507 | 58.1726 | -123.056 | 122.9828 | 122.9095 | 58.3191 | -123.111
670.6406 | 123.2162 | -58.168 | 64.7736 | 0.47654 | -0.0046498 | 0.092331 | 0.0018638 | 0.043784 | -0.011268 | -0.013582 | 0.28108 | -0.024001 | 0.054124 | 0.043464 | 0.00029315 | -0.019331 | 64.7461 | -58.0811 | -0.086975 | -58.3832 | 64.8239 | -58.2321 | -58.2779 | -58.136 | 0.027466 | -58.4015 | 64.8148 | 64.7415 | -58.2962 | -58.3466 | -0.064087 | -0.10986 | 0.050354 | 0.086975 | -0.21515 | -0.10529 | -0.027466 | -0.12817 | -0.17853 | 0.041198 | 0.032044 | -0.23346 | -0.054931 | -0.032044 | 122.9919 | 122.9141 | 58.0811 | -123.0515 | 122.9828 | 122.9095 | 58.1955 | -123.1201
671.6406 | 123.1934 | -58.1726 | 64.7415 | 0.46128 | 0.0017592 | 0.084854 | 0.022158 | 0.042716 | -0.0016549 | -0.029603 | 0.29634 | -0.028273 | 0.032762 | 0.049872 | 0.0056341 | -0.00865 | 64.7598 | -58.0948 | -0.10071 | -58.3786 | 64.7964 | -58.1909 | -58.2962 | -58.1223 | 0.013733 | -58.3878 | 64.8514 | 64.7324 | -58.2962 | -58.3511 | -0.018311 | -0.1236 | 0.054932 | 0.077819 | -0.20599 | -0.082397 | 0.018311 | -0.1236 | -0.17853 | 0.10986 | 0.050354 | -0.21515 | -0.036621 | -0.009155 | 122.9691 | 122.9324 | 58.0719 | -123.0377 | 123.024 | 122.905 | 58.1863 | -123.0927
672.6406 | 123.175 | -58.1543 | 64.7324 | 0.43077 | -0.012126 | 0.079513 | 0.020022 | 0.046988 | -0.013404 | -0.022126 | 0.34212 | -0.022933 | 0.06801 | 0.047736 | -0.0061159 | -0.024671 | 64.7598 | -58.0856 | -0.10986 | -58.4152 | 64.801 | -58.2184 | -58.287 | -58.1131 | 0.027466 | -58.4061 | 64.8331 | 64.7278 | -58.2962 | -58.3603 | -0.064087 | -0.13275 | 0.068664 | 0.068665 | -0.26093 | -0.12817 | 0.027466 | -0.14191 | -0.20599 | 0.10071 | 0.041199 | -0.25177 | -0.045776 | -0.004578 | 122.9553 | 122.9141 | 58.0444 | -123.0194 | 122.9874 | 122.8821 | 58.1818 | -123.0927
673.6406 | 123.143 | -58.1955 | 64.7552 | 0.47654 | 0.013508 | 0.080581 | 0.02109 | 0.035239 | -0.010199 | -0.011445 | 0.25056 | -0.028273 | 0.045579 | 0.050941 | 0.0024291 | -0.006513 | 64.7598 | -58.0856 | -0.086975 | -58.4244 | 64.7964 | -58.2367 | -58.2825 | -58.1177 | 0.018311 | -58.4061 | 64.8285 | 64.7003 | -58.287 | -58.374 | -0.041198 | -0.086975 | 0.041199 | 0.10986 | -0.22888 | -0.14191 | 0.004578 | -0.091552 | -0.17853 | 0.073242 | 0.07782 | -0.21057 | -0.032044 | -0.054932 | 122.9919 | 122.9553 | 58.1085 | -123.0377 | 123.024 | 122.8958 | 58.2138 | -123.1293
674.6406 | 123.1293 | -58.2001 | 64.7964 | -0.19484 | 0.032734 | 0.078445 | 0.030703 | 0.053397 | 0.022912 | -0.015718 | -0.26824 | -0.012251 | 0.051988 | 0.048804 | 0.0099061 | -0.030012 | 64.8148 | -58.0536 | -0.059509 | -58.3282 | 64.8743 | -58.2458 | -58.3054 | -58.1268 | 0.10071 | -58.4152 | 64.8788 | 64.7598 | -58.3008 | -58.3557 | -0.045777 | -0.10529 | 0.07782 | 0.14648 | -0.12817 | -0.022888 | 0.01831 | -0.10071 | -0.15564 | 0.082397 | 0.073242 | -0.21515 | -0.059509 | -0.036621 | 123.0743 | 123.0148 | 58.1406 | -123.1018 | 123.0789 | 122.9599 | 58.3008 | -123.1522
675.6875 | 123.1293 | -58.1818 | 64.7461 | 1.4073 | 0.030598 | 0.067764 | 0.031771 | 0.043784 | 0.015435 | -0.00076433 | 0.37263 | -0.010115 | 0.062669 | 0.063758 | 0.010974 | -0.018263 | 64.7507 | -58.1543 | -0.17853 | -58.4152 | 64.8331 | -58.2504 | -58.3145 | -58.1543 | -0.091553 | -58.4793 | 64.856 | 64.7278 | -58.3282 | -58.3786 | -0.068664 | -0.13275 | 0.086975 | 0.027466 | -0.23346 | -0.10071 | 0.004577 | -0.14648 | -0.19684 | 0.10986 | 0.027466 | -0.29755 | -0.10071 | -0.018311 | 123.0148 | 122.9324 | 58.0032 | -123.0606 | 123.0377 | 122.9095 | 58.0902 | -123.1247
676.6406 | 123.1934 | -58.1726 | 64.7324 | 0.65965 | -0.00037681 | 0.053879 | 0.017886 | 0.037375 | 0.0015501 | -0.015718 | 0.46419 | -0.010115 | 0.040239 | 0.057349 | 0.0024291 | -0.015058 | 64.7919 | -58.0536 | -0.07782 | -58.3832 | 64.7736 | -58.2275 | -58.2916 | -58.0765 | 0.027466 | -58.3832 | 64.7873 | 64.7186 | -58.2825 | -58.3511 | -0.054932 | -0.11902 | 0.041199 | 0.11902 | -0.21057 | -0.091553 | 0.059509 | -0.10986 | -0.17853 | 0.054931 | 0.09613 | -0.21057 | -0.032044 | -0.013733 | 122.9462 | 122.9645 | 58.0948 | -123.024 | 122.9599 | 122.8912 | 58.2001 | -123.0835
677.6406 | 123.175 | -58.1497 | 64.769 | 0.26292 | -0.0035808 | 0.074173 | 0.018954 | 0.053397 | -0.01554 | -0.029603 | 2.0969 | -0.019728 | 0.046647 | 0.053077 | -0.0050469 | -0.007581 | 64.7415 | -58.0673 | -0.068665 | -58.3786 | 64.8056 | -58.2138 | -58.2825 | -58.1268 | 0.054932 | -58.3786 | 64.8376 | 64.7369 | -58.2779 | -58.3282 | -0.064087 | -0.13275 | 0.036621 | 0.082397 | -0.22888 | -0.09613 | -0.027466 | -0.12817 | -0.17853 | 0.068664 | 0.022888 | -0.22888 | -0.050354 | -0.032044 | 122.9553 | 122.8912 | 58.0811 | -123.0515 | 122.9874 | 122.8867 | 58.2047 | -123.0972
678.6406 | 123.2117 | -58.1589 | 64.7461 | 0.24766 | -0.017467 | 0.068832 | 0.016818 | 0.048056 | -0.014472 | -0.016786 | 1.5628 | -0.029341 | 0.044511 | 0.047736 | -0.0039789 | -0.017194 | 64.7324 | -58.0673 | -0.086975 | -58.3786 | 64.8148 | -58.2367 | -58.2779 | -58.1085 | 0.050354 | -58.3969 | 64.8239 | 64.7461 | -58.3008 | -58.342 | -0.077819 | -0.11902 | 0.068664 | 0.091553 | -0.21973 | -0.10071 | -0.013733 | -0.14191 | -0.1831 | 0.07782 | 0.050354 | -0.23804 | -0.054932 | 0 | 122.9736 | 122.8912 | 58.0719 | -123.024 | 122.9828 | 122.905 | 58.2092 | -123.0881
679.6406 | 123.1613 | -58.1772 | 64.7964 | 0.00352 | 0.055165 | 0.062424 | 0.042453 | 0.059806 | 0.021844 | -0.0039683 | -0.13091 | -0.019728 | 0.076554 | 0.054145 | 0.0099061 | -0.037489 | 64.8331 | -58.0627 | -0.068665 | -58.374 | 64.8788 | -58.2184 | -58.2962 | -58.0902 | 0.054932 | -58.4335 | 64.9017 | 64.7278 | -58.3054 | -58.4152 | -0.041199 | -0.11902 | 0.082397 | 0.11444 | -0.19684 | -0.077819 | 0.036621 | -0.12817 | -0.23804 | 0.10528 | 0.086975 | -0.25635 | -0.018311 | -0.068665 | 123.056 | 123.0103 | 58.1085 | -123.0927 | 123.0789 | 122.905 | 58.2321 | -123.2117
680.6875 | 123.2208 | -58.1635 | 64.7186 | 0.56809 | 0.034871 | 0.059219 | 0.024295 | 0.044852 | 0.012231 | 0.00030367 | 0.46419 | -0.014388 | 0.051988 | 0.059485 | 0.012042 | -0.022535 | 64.7598 | -58.1039 | -0.13733 | -58.3923 | 64.8285 | -58.255 | -58.3054 | -58.0673 | 0.013733 | -58.4198 | 64.8148 | 64.7232 | -58.2962 | -58.3832 | -0.091553 | -0.14191 | 0.10986 | 0.059509 | -0.22888 | -0.086975 | 0.041199 | -0.13275 | -0.21973 | 0.09613 | 0.09613 | -0.25635 | -0.036621 | 0.004578 | 122.9919 | 122.9233 | 58.0261 | -123.024 | 122.9782 | 122.8867 | 58.1772 | -123.1018
681.6406 | 123.1796 | -58.1818 | 64.7461 | 0.17137 | -0.017467 | 0.074173 | 0.023226 | 0.041648 | -0.024085 | -0.017854 | 0.3116 | -0.038954 | 0.049852 | 0.058417 | -0.0029109 | -0.016126 | 64.7369 | -58.0673 | -0.091553 | -58.374 | 64.8239 | -58.2138 | -58.2779 | -58.1039 | 0.009155 | -58.3969 | 64.8376 | 64.7461 | -58.287 | -58.3557 | -0.032043 | -0.09613 | 0.07782 | 0.11444 | -0.19226 | -0.09613 | -0.009156 | -0.10529 | -0.17395 | 0.091552 | 0.07782 | -0.21515 | -0.041199 | 0 | 123.0057 | 122.9187 | 58.0902 | -123.024 | 123.0194 | 122.9279 | 58.1909 | -123.1018
682.6406 | 123.2208 | -58.1772 | 64.7644 | 0.47654 | 0.010304 | 0.077377 | 0.03284 | 0.04592 | -0.016608 | -0.023195 | 0.32686 | -0.028273 | 0.051988 | 0.057349 | 0.0099061 | -0.00865 | 64.7598 | -58.0673 | -0.10986 | -58.3832 | 64.7919 | -58.223 | -58.287 | -58.1314 | 0.013733 | -58.4106 | 64.8193 | 64.7232 | -58.3099 | -58.3603 | -0.045776 | -0.10986 | 0.027466 | 0.10986 | -0.20599 | -0.096131 | -0.004577 | -0.13275 | -0.18311 | 0.054932 | 0.045776 | -0.23346 | -0.050354 | -0.041198 | 122.9691 | 122.937 | 58.0673 | -123.0515 | 122.9965 | 122.9004 | 58.1909 | -123.1247
683.6406 | 123.2071 | -58.168 | 64.7781 | 0.41551 | -0.0057178 | 0.066696 | 0.02109 | 0.054465 | -0.00058594 | -0.023195 | 0.38789 | -0.0090474 | 0.048783 | 0.044532 | 0.0067021 | -0.019331 | 64.7552 | -58.0673 | -0.10071 | -58.3878 | 64.8102 | -58.2275 | -58.2916 | -58.1268 | -0.018311 | -58.3878 | 64.8193 | 64.7049 | -58.2962 | -58.4015 | -0.059509 | -0.1236 | 0.032044 | 0.10071 | -0.21973 | -0.09613 | -0.022888 | -0.12817 | -0.23346 | 0.041199 | 0.041199 | -0.21973 | 0.013733 | -0.073242 | 122.9782 | 122.9233 | 58.0673 | -123.0698 | 122.9874 | 122.8729 | 58.1497 | -123.1796
684.6406 | 123.1384 | -58.1635 | 64.7598 | -0.33217 | 0.022053 | 0.068832 | 0.017886 | 0.059806 | 0.022912 | -0.013582 | -0.13091 | -0.026137 | 0.049852 | 0.043464 | 0.018451 | -0.025739 | 64.8193 | -58.0536 | -0.059509 | -58.3603 | 64.8468 | -58.2367 | -58.2916 | -58.1039 | 0.054932 | -58.429 | 64.8788 | 64.7598 | -58.3145 | -58.3511 | -0.073242 | -0.12817 | 0.086975 | 0.10986 | -0.19684 | -0.068665 | 0.059509 | -0.15106 | -0.18768 | 0.11902 | 0.059509 | -0.2655 | -0.07782 | 0 | 123.0103 | 122.9828 | 58.1039 | -123.0515 | 123.0423 | 122.9233 | 58.2184 | -123.111
685.6406 | 123.2208 | -58.1406 | 64.7644 | 0.36973 | -0.00037681 | 0.082718 | 0.026431 | 0.053397 | -0.01554 | -0.0093093 | 0.22005 | -0.021865 | 0.041307 | 0.055213 | -0.0039789 | -0.002241 | 64.7507 | -58.0444 | -0.059509 | -58.3603 | 64.8148 | -58.2138 | -58.2779 | -58.0902 | 0.086975 | -58.3603 | 64.8331 | 64.7415 | -58.2642 | -58.3282 | -0.073242 | -0.13733 | 0.050354 | 0.09613 | -0.21973 | -0.082398 | -0.013733 | -0.1236 | -0.18768 | 0.068665 | 0.050354 | -0.21973 | -0.032044 | -0.022888 | 122.9553 | 122.8912 | 58.0811 | -123.0423 | 122.9736 | 122.8821 | 58.2275 | -123.0927
686.6406 | 123.2254 | -58.1406 | 64.7507 | -0.026997 | -0.0089218 | 0.079513 | 0.012545 | 0.052329 | -0.017676 | -0.028535 | 0.18953 | -0.034682 | 0.049852 | 0.052009 | -0.0050469 | -0.022535 | 64.7507 | -58.0536 | -0.07782 | -58.3786 | 64.8193 | -58.2184 | -58.2825 | -58.0994 | 0.068665 | -58.3511 | 64.856 | 64.7369 | -58.2687 | -58.3557 | -0.07782 | -0.14191 | 0.068665 | 0.086975 | -0.23804 | -0.09613 | 0 | -0.12817 | -0.21515 | 0.10529 | 0.041199 | -0.21057 | 0.004578 | -0.013733 | 122.9599 | 122.8912 | 58.0627 | -123.0331 | 122.9965 | 122.8775 | 58.2092 | -123.1064
687.6406 | 123.2071 | -58.1589 | 64.7415 | 1.7735 | -0.014263 | 0.08165 | 0.016818 | 0.052329 | -0.014472 | -0.013582 | 0.22005 | -0.033614 | 0.047715 | 0.033851 | -0.0050469 | -0.021467 | 64.7644 | -58.0582 | -0.09613 | -58.3694 | 64.8239 | -58.223 | -58.2458 | -58.0948 | 0.045776 | -58.3786 | 64.8239 | 64.7232 | -58.2733 | -58.3466 | -0.064086 | -0.086975 | 0.082398 | 0.10071 | -0.21057 | -0.1236 | 0.022888 | -0.11444 | -0.18768 | 0.082398 | 0.064087 | -0.21973 | -0.032043 | -0.01831 | 122.9828 | 122.9233 | 58.0627 | -122.9874 | 122.9828 | 122.8821 | 58.2047 | -123.0881
688.6406 | 123.1659 | -58.1497 | 64.769 | 0.21714 | -0.012126 | 0.085922 | 0.020022 | 0.053397 | -0.01554 | -0.010377 | 0.38789 | -0.034682 | 0.047715 | 0.053077 | -0.00077485 | -0.01399 | 64.7232 | -58.0399 | -0.064087 | -58.3878 | 64.8331 | -58.2047 | -58.2642 | -58.0948 | 0.041199 | -58.3694 | 64.8193 | 64.7232 | -58.2916 | -58.3191 | -0.054932 | -0.11444 | 0.064087 | 0.10986 | -0.23804 | -0.1236 | -0.045776 | -0.14191 | -0.16937 | 0.050354 | 0.054931 | -0.21973 | -0.050354 | -0.045776 | 122.9828 | 122.8729 | 58.0856 | -123.0331 | 122.9691 | 122.8729 | 58.1909 | -123.0881
689.6406 | 123.143 | -58.1451 | 64.7598 | 0.44602 | -0.0025128 | 0.075241 | 0.017886 | 0.041648 | -0.0027229 | -0.030671 | 0.3116 | -0.017592 | 0.057328 | 0.037055 | -0.00077485 | -0.019331 | 64.7644 | -58.0536 | -0.086975 | -58.3969 | 64.8148 | -58.2321 | -58.2779 | -58.0994 | -0.009155 | -58.4106 | 64.8331 | 64.7141 | -58.2962 | -58.3603 | -0.086975 | -0.13275 | 0.054931 | 0.091553 | -0.25177 | -0.11902 | 0.004577 | -0.15106 | -0.21515 | 0.073242 | 0.045777 | -0.2655 | -0.050354 | -0.045777 | 122.9599 | 122.9095 | 58.0582 | -123.0377 | 122.9782 | 122.8592 | 58.136 | -123.1201
690.6406 | 123.23 | -58.1497 | 64.769 | 0.12559 | -0.0035808 | 0.08165 | 0.030703 | 0.041648 | -0.020881 | -0.024263 | 0.12849 | -0.024001 | 0.05626 | 0.048804 | -0.0071839 | -0.022535 | 64.801 | -58.0261 | -0.041199 | -58.3511 | 64.8285 | -58.2138 | -58.2642 | -58.0627 | 0.10071 | -58.342 | 64.8468 | 64.7141 | -58.2916 | -58.3145 | -0.064087 | -0.11444 | 0.059509 | 0.1236 | -0.20142 | -0.086975 | 0.032043 | -0.14191 | -0.1648 | 0.07782 | 0.086975 | -0.19226 | -0.027466 | -0.054932 | 122.9782 | 122.9507 | 58.1085 | -123.0331 | 122.9965 | 122.8638 | 58.2504 | -123.0835
691.6406 | 123.2025 | -58.1589 | 64.7552 | 0.15611 | -0.0035808 | 0.075241 | 0.0061368 | 0.044852 | -0.010199 | -0.029603 | 0.021682 | -0.027205 | 0.042375 | 0.057349 | 0.0013611 | -0.015058 | 64.7736 | -58.0399 | -0.064087 | -58.3603 | 64.8102 | -58.2184 | -58.2825 | -58.0765 | 0.091553 | -58.3603 | 64.8605 | 64.7186 | -58.287 | -58.3374 | -0.059509 | -0.1236 | 0.054932 | 0.11902 | -0.20142 | -0.07782 | 0.018311 | -0.12817 | -0.17853 | 0.10529 | 0.082398 | -0.20142 | -0.022889 | -0.036621 | 122.9691 | 122.9324 | 58.0948 | -123.0377 | 123.0194 | 122.8775 | 58.2504 | -123.0927
692.6406 | 123.175 | -58.1543 | 64.769 | 0.88853 | -0.0057178 | 0.076309 | 0.013613 | 0.044852 | -0.011268 | -0.018922 | 0.14375 | -0.027205 | 0.05092 | 0.044532 | -0.0018429 | -0.023603 | 64.7736 | -58.0353 | -0.07782 | -58.3694 | 64.8285 | -58.2047 | -58.2825 | -58.0948 | 0.059509 | -58.3557 | 64.8331 | 64.7278 | -58.287 | -58.3282 | -0.050354 | -0.12817 | 0.059509 | 0.11902 | -0.21515 | -0.086975 | 0.004578 | -0.13275 | -0.17395 | 0.064087 | 0.059509 | -0.20142 | -0.027466 | -0.041199 | 122.9828 | 122.9279 | 58.0765 | -123.0515 | 122.9874 | 122.8821 | 58.2138 | -123.0972
693.6406 | 123.2208 | -58.1589 | 64.7736 | 0.21714 | -0.0025128 | 0.083786 | 0.025363 | 0.048056 | 0.0036861 | -0.025331 | 0.26582 | -0.034682 | 0.055192 | 0.037055 | 0.0056341 | -0.01399 | 64.8148 | -58.0902 | -0.10071 | -58.3694 | 64.8193 | -58.223 | -58.2642 | -58.1039 | 0.054932 | -58.374 | 64.856 | 64.7324 | -58.2687 | -58.3374 | -0.064086 | -0.10528 | 0.045776 | 0.068665 | -0.21057 | -0.10529 | 0.041198 | -0.10986 | -0.17853 | 0.082397 | 0.054932 | -0.21515 | -0.036621 | -0.041199 | 122.9782 | 122.9736 | 58.0582 | -123.0377 | 123.0148 | 122.8912 | 58.2138 | -123.111
694.6406 | 123.2162 | -58.1451 | 64.7507 | 0.2324 | 0.019917 | 0.063492 | 0.0082728 | 0.046988 | 0.0079581 | -0.018922 | 0.067459 | -0.020796 | 0.041307 | 0.057349 | -0.0018429 | -0.024671 | 64.7552 | -58.0536 | -0.11444 | -58.3145 | 64.8422 | -58.1863 | -58.287 | -58.1177 | 0.009155 | -58.3923 | 64.8102 | 64.7186 | -58.2962 | -58.3511 | -0.041198 | -0.14191 | 0.091553 | 0.091553 | -0.16937 | -0.027466 | 0.004578 | -0.15106 | -0.20599 | 0.05951 | 0.027466 | -0.24719 | -0.041199 | -0.032043 | 122.9874 | 122.9004 | 58.0307 | -123.0377 | 122.9553 | 122.8638 | 58.1543 | -123.1018
695.6406 | 123.175 | -58.1314 | 64.769 | 0.3087 | -0.012126 | 0.06456 | 0.018954 | 0.061942 | -0.0059269 | -0.0061053 | 0.2353 | -0.038954 | 0.043443 | 0.049872 | -0.0071839 | -0.040693 | 64.7736 | -58.0627 | -0.10071 | -58.374 | 64.8422 | -58.2092 | -58.2733 | -58.0307 | 0.050354 | -58.4564 | 64.8376 | 64.7369 | -58.2458 | -58.3511 | -0.07782 | -0.14191 | 0.073242 | 0.068665 | -0.24261 | -0.10071 | 0.004578 | -0.11444 | -0.21973 | 0.068664 | 0.10071 | -0.32501 | -0.10529 | -0.032044 | 122.9736 | 122.905 | 58.0307 | -123.0423 | 122.9691 | 122.8683 | 58.1818 | -123.1201
696.6406 | 123.1796 | -58.1497 | 64.7552 | 0.52232 | -0.0046498 | 0.079513 | 0.027499 | 0.046988 | 0.010095 | -0.016786 | 0.47945 | -0.021865 | 0.05626 | 0.053077 | 0.0034971 | -0.021467 | 64.8102 | -58.049 | -0.11444 | -58.3786 | 64.7919 | -58.2092 | -58.2733 | -58.1085 | 0 | -58.4198 | 64.8102 | 64.7232 | -58.2962 | -58.3511 | -0.05951 | -0.1236 | 0.036621 | 0.10071 | -0.22888 | -0.10529 | 0.054932 | -0.14649 | -0.20142 | 0.054932 | 0.041198 | -0.27008 | -0.068665 | -0.032043 | 122.9416 | 122.9599 | 58.0353 | -123.0286 | 122.9599 | 122.8729 | 58.1497 | -123.1064
697.6406 | 123.1659 | -58.1497 | 64.769 | 0.21714 | 0.00069119 | 0.073105 | 0.020022 | 0.042716 | 0.0036861 | -0.023195 | 0.29634 | -0.022933 | 0.054124 | 0.050941 | 0.0024291 | -0.03108 | 64.7736 | -58.049 | -0.12817 | -58.3694 | 64.8331 | -58.2321 | -58.2733 | -58.1131 | 0.018311 | -58.4106 | 64.8239 | 64.6957 | -58.2825 | -58.3466 | -0.082398 | -0.1236 | 0.064087 | 0.10071 | -0.21973 | -0.096131 | 0.004578 | -0.13275 | -0.19684 | 0.054932 | 0.036621 | -0.26093 | -0.064087 | -0.073242 | 122.9828 | 122.9233 | 58.0215 | -123.0423 | 122.9736 | 122.8455 | 58.168 | -123.1155
698.6406 | 123.1796 | -58.1589 | 64.769 | 0.32395 | -0.0046498 | 0.089126 | 0.024295 | 0.067282 | -0.0091309 | -0.011445 | 1.9595 | -0.026137 | 0.05092 | 0.035987 | 0.0013611 | -0.023603 | 64.7781 | -58.0536 | -0.11902 | -58.3649 | 64.8285 | -58.2092 | -58.3054 | -58.1131 | 0.027466 | -58.3969 | 64.8468 | 64.7095 | -58.3145 | -58.3694 | -0.050354 | -0.14648 | 0.059509 | 0.10529 | -0.20599 | -0.059509 | 0.009155 | -0.15564 | -0.21057 | 0.07782 | 0.045777 | -0.23804 | -0.027466 | -0.059509 | 122.9874 | 122.937 | 58.0399 | -123.0743 | 123.0057 | 122.8683 | 58.1863 | -123.1384
699.6406 | 123.2117 | -58.1314 | 64.7461 | 0.27818 | -0.0046498 | 0.084854 | 0.012545 | 0.049125 | -0.0059269 | -0.021058 | 0.28108 | -0.022933 | 0.035966 | 0.0456 | 0.00029315 | -0.025739 | 64.7644 | -58.0582 | -0.11902 | -58.3878 | 64.8193 | -58.2047 | -58.3008 | -58.0994 | 0.018311 | -58.3923 | 64.8376 | 64.7369 | -58.2825 | -58.342 | -0.073242 | -0.16937 | 0.073242 | 0.073242 | -0.25635 | -0.086975 | 0.01831 | -0.15106 | -0.21057 | 0.091552 | 0.032044 | -0.26093 | -0.050354 | -0.009156 | 122.9507 | 122.8958 | 58.0124 | -123.0469 | 122.9691 | 122.8683 | 58.1497 | -123.0881
700.6406 | 123.1888 | -58.1909 | 64.7644 | 0.58335 | -0.012126 | 0.075241 | 0.016818 | 0.048056 | 0.0015501 | -0.01999 | 0.22005 | -0.03575 | 0.043443 | 0.0456 | 0.0024291 | -0.022535 | 64.7781 | -58.049 | -0.11902 | -58.3694 | 64.8376 | -58.2413 | -58.287 | -58.1039 | -0.004578 | -58.3923 | 64.8376 | 64.7049 | -58.2733 | -58.3511 | -0.050354 | -0.09613 | 0.073242 | 0.14191 | -0.17853 | -0.082398 | 0.013733 | -0.082397 | -0.16022 | 0.073242 | 0.086975 | -0.20142 | -0.041199 | -0.059509 | 123.0286 | 122.9691 | 58.0719 | -123.0515 | 123.0286 | 122.8958 | 58.1863 | -123.1155
701.6406 | 123.1796 | -58.1635 | 64.7507 | 0.38499 | 0.0060322 | 0.088058 | 0.022158 | 0.04592 | -0.0080629 | -0.0082413 | 0.3116 | -0.026137 | 0.043443 | 0.044532 | 0.010974 | -0.017194 | 64.7736 | -58.049 | -0.11444 | -58.3786 | 64.8056 | -58.2321 | -58.2779 | -58.0948 | 0.004578 | -58.4198 | 64.8285 | 64.7324 | -58.255 | -58.3328 | -0.068665 | -0.11444 | 0.054932 | 0.11444 | -0.21515 | -0.10071 | 0.022889 | -0.091553 | -0.16937 | 0.07782 | 0.068664 | -0.25635 | -0.086975 | -0.01831 | 122.9691 | 122.937 | 58.049 | -123.0286 | 122.9919 | 122.8958 | 58.168 | -123.0835
702.6406 | 123.1796 | -58.1406 | 64.7644 | 0.4918 | 0.0049632 | 0.082718 | 0.024295 | 0.039511 | 0.0058221 | -0.01465 | 0.3116 | -0.01866 | 0.051988 | 0.053077 | 0.0034971 | -0.01399 | 64.769 | -58.0536 | -0.11444 | -58.3923 | 64.8056 | -58.223 | -58.2687 | -58.1039 | -0.041199 | -58.429 | 64.8239 | 64.6866 | -58.2962 | -58.342 | -0.082397 | -0.12817 | 0.041199 | 0.086975 | -0.25177 | -0.1236 | 0.004578 | -0.15564 | -0.20142 | 0.05951 | 0.036621 | -0.28839 | -0.086975 | -0.07782 | 122.9462 | 122.9095 | 58.0261 | -123.0331 | 122.9645 | 122.8271 | 58.0994 | -123.1064
703.6406 | 123.23 | -58.1772 | 64.7278 | 0.47654 | 0.018849 | 0.073105 | 0.0082728 | 0.048056 | 0.0036861 | -0.00076433 | 0.95247 | -0.030409 | 0.041307 | 0.06269 | 0.01311 | -0.018263 | 64.7095 | -58.1543 | -0.054932 | -58.2413 | 64.7873 | -58.223 | -58.2733 | -58.0444 | 0.018311 | -58.3694 | 64.8285 | 64.6729 | -58.3099 | -58.3328 | -0.045776 | -0.09613 | 0.059509 | 0.022888 | -0.064087 | 0.032043 | -0.01831 | -0.13275 | -0.15564 | 0.10071 | 0.13275 | -0.19226 | -0.036621 | -0.054931 | 122.9645 | 122.8867 | 58.1223 | -123.0011 | 123.0057 | 122.85 | 58.1955 | -123.0606
704.6406 | 123.1842 | -58.168 | 64.7369 | 0.32395 | 0.018849 | 0.083786 | 0.024295 | 0.041648 | 0.0036861 | -0.0071733 | 0.50996 | -0.01866 | 0.041307 | 0.053077 | -0.0018429 | -0.023603 | 64.8102 | -58.0353 | -0.09613 | -58.3832 | 64.7827 | -58.2275 | -58.2916 | -58.0856 | 0.004578 | -58.3969 | 64.8148 | 64.7049 | -58.2779 | -58.3466 | -0.059509 | -0.1236 | 0.045777 | 0.13275 | -0.21515 | -0.091553 | 0.073243 | -0.10986 | -0.17853 | 0.07782 | 0.082398 | -0.22888 | -0.050354 | -0.032043 | 122.9507 | 122.9782 | 58.0719 | -123.0286 | 122.9828 | 122.8729 | 58.1726 | -123.0835
705.6406 | 123.175 | -58.1635 | 64.7552 | 0.47654 | 0.0049632 | 0.075241 | 0.017886 | 0.051261 | -0.0037909 | -0.012513 | 0.2353 | -0.016524 | 0.03917 | 0.043464 | 0.0067021 | -0.015058 | 64.7552 | -58.0582 | -0.14191 | -58.3878 | 64.7873 | -58.223 | -58.2687 | -58.0994 | 0 | -58.4152 | 64.8285 | 64.7186 | -58.2825 | -58.3511 | -0.059509 | -0.10529 | 0.032043 | 0.10529 | -0.2243 | -0.11902 | 0 | -0.11902 | -0.18768 | 0.073242 | 0.064087 | -0.25177 | -0.064087 | -0.036621 | 122.9507 | 122.9187 | 58.0215 | -123.024 | 122.9919 | 122.8821 | 58.1635 | -123.1064
706.6406 | 123.1659 | -58.1726 | 64.7644 | 0.40025 | 0.00069119 | 0.077377 | 0.016818 | 0.04058 | 0.0090271 | -0.016786 | 0.44893 | -0.020796 | 0.05092 | 0.041327 | 0.012042 | -0.019331 | 64.7781 | -58.0399 | -0.10986 | -58.3832 | 64.7964 | -58.223 | -58.287 | -58.1085 | -0.018311 | -58.4061 | 64.8056 | 64.7186 | -58.287 | -58.3374 | -0.050354 | -0.11444 | 0.032044 | 0.13275 | -0.21057 | -0.096131 | 0.013733 | -0.11444 | -0.16479 | 0.041199 | 0.064086 | -0.23346 | -0.068665 | -0.045776 | 122.9691 | 122.9507 | 58.0627 | -123.0515 | 122.9782 | 122.8912 | 58.1543 | -123.1018
707.6406 | 123.1613 | -58.1451 | 64.7415 | 0.58335 | 0.0038952 | 0.077377 | 0.030703 | 0.051261 | -0.0027229 | -0.016786 | 0.38789 | -0.019728 | 0.05092 | 0.058417 | 0.0077701 | -0.023603 | 64.801 | -58.0261 | -0.10986 | -58.374 | 64.8102 | -58.2321 | -58.2642 | -58.0994 | -0.022888 | -58.4015 | 64.8056 | 64.6866 | -58.2916 | -58.3603 | -0.086975 | -0.11902 | 0.068665 | 0.11902 | -0.22888 | -0.10986 | 0.059509 | -0.14648 | -0.21515 | 0.064087 | 0.045777 | -0.25635 | -0.041198 | -0.054932 | 122.9553 | 122.9462 | 58.0353 | -123.0057 | 122.9507 | 122.8317 | 58.1223 | -123.1018
708.6406 | 123.175 | -58.1726 | 64.7324 | 0.52232 | 0.0071002 | 0.076309 | 0.029635 | 0.057669 | 0.016503 | -0.018922 | 0.28108 | -0.019728 | 0.040239 | 0.042396 | 0.012042 | -0.022535 | 64.7964 | -58.0032 | -0.10986 | -58.3694 | 64.7919 | -58.2184 | -58.2733 | -58.0536 | 0.004578 | -58.3878 | 64.8148 | 64.6774 | -58.2962 | -58.3466 | -0.045777 | -0.10071 | 0.059509 | 0.16937 | -0.19684 | -0.096131 | 0.064087 | -0.1236 | -0.17395 | 0.082397 | 0.11902 | -0.21515 | -0.041198 | -0.054932 | 122.9645 | 122.9691 | 58.0627 | -123.0057 | 122.9874 | 122.85 | 58.1772 | -123.0789
709.6406 | 123.2208 | -58.1543 | 64.7186 | 1.0259 | 0.031666 | 0.061355 | 0.020022 | 0.057669 | 0.0068901 | -0.01465 | 0.60152 | -0.025069 | 0.059465 | 0.033851 | 0.026996 | -0.021467 | 64.8376 | -58.0261 | -0.12817 | -58.3466 | 64.7827 | -58.2413 | -58.2962 | -58.0673 | 0.004578 | -58.3832 | 64.7964 | 64.6683 | -58.3008 | -58.3557 | -0.086975 | -0.14191 | 0.064087 | 0.12817 | -0.19226 | -0.050354 | 0.11902 | -0.14648 | -0.20142 | 0.07782 | 0.086975 | -0.22888 | -0.027466 | -0.050354 | 122.937 | 122.9919 | 58.0261 | -123.0148 | 122.9507 | 122.8226 | 58.1589 | -123.0743
710.6406 | 123.2254 | -58.1451 | 64.7461 | 0.56809 | 0.026326 | 0.0699 | 0.022158 | 0.051261 | 0.0068901 | -0.01999 | 0.54048 | -0.03575 | 0.046647 | 0.043464 | 0.010974 | -0.022535 | 64.9887 | -58.0765 | -0.15106 | -58.3191 | 64.8056 | -58.2092 | -58.2825 | -58.0582 | 0.022888 | -58.3694 | 64.7873 | 64.6774 | -58.2733 | -58.3603 | -0.064087 | -0.13733 | 0.059509 | 0.068665 | -0.17395 | -0.036621 | 0.24261 | -0.12817 | -0.21515 | 0.041198 | 0.086975 | -0.2243 | -0.009155 | -0.068665 | 122.9507 | 123.1338 | 57.9941 | -123.0286 | 122.9324 | 122.8226 | 58.168 | -123.1064
711.6406 | 123.2162 | -58.1451 | 64.7324 | 0.61387 | 0.016713 | 0.059219 | 0.016818 | 0.053397 | 0.00048206 | -0.024263 | 0.28108 | -0.014388 | 0.05092 | 0.046668 | 0.010974 | -0.016126 | 64.8148 | -58.0215 | -0.09613 | -58.3511 | 64.7964 | -58.223 | -58.3008 | -58.0673 | 0.045776 | -58.3649 | 64.8422 | 64.7141 | -58.287 | -58.342 | -0.077819 | -0.15564 | 0.064087 | 0.1236 | -0.20599 | -0.050354 | 0.082397 | -0.14191 | -0.19684 | 0.10986 | 0.07782 | -0.21973 | -0.022888 | -0.018311 | 122.9416 | 122.9599 | 58.049 | -123.0331 | 122.9874 | 122.8592 | 58.1909 | -123.0743
712.6406 | 123.1796 | -58.1772 | 64.7278 | 0.64439 | 0.0092362 | 0.070968 | 0.0018638 | 0.043784 | -0.0037909 | -0.015718 | 0.571 | -0.01866 | 0.046647 | 0.041327 | -0.00077485 | -0.019331 | 64.7964 | -58.0307 | -0.11444 | -58.3649 | 64.7919 | -58.2321 | -58.2916 | -58.0994 | -0.013733 | -58.3878 | 64.7873 | 64.682 | -58.3008 | -58.3603 | -0.054932 | -0.11444 | 0.064087 | 0.14648 | -0.18768 | -0.073242 | 0.068665 | -0.1236 | -0.18311 | 0.059509 | 0.07782 | -0.21057 | -0.027465 | -0.045776 | 122.9691 | 122.9736 | 58.0627 | -123.0194 | 122.9645 | 122.8592 | 58.1635 | -123.0881
713.6406 | 123.1934 | -58.1589 | 64.7186 | -0.2101 | 0.015645 | 0.077377 | 0.033908 | 0.057669 | -0.00058594 | -0.01465 | 0.44893 | -0.020796 | 0.066941 | 0.0456 | 0.0024291 | -0.019331 | 64.8193 | -58.0078 | -0.10071 | -58.3649 | 64.8102 | -58.223 | -58.2916 | -58.0582 | -0.009155 | -58.3786 | 64.8239 | 64.6957 | -58.287 | -58.3557 | -0.064086 | -0.13275 | 0.091553 | 0.15106 | -0.20599 | -0.073242 | 0.10071 | -0.12817 | -0.19684 | 0.10529 | 0.10071 | -0.21973 | -0.022888 | -0.022888 | 122.9691 | 122.9782 | 58.0582 | -123.0103 | 122.9828 | 122.8546 | 58.1497 | -123.0743
714.6406 | 123.2162 | -58.1635 | 64.7095 | 0.55284 | 0.028462 | 0.06456 | 0.043521 | 0.054465 | 0.0079581 | -0.0082413 | 0.28108 | -0.0037074 | 0.062669 | 0.052009 | 0.0045661 | -0.019331 | 64.7507 | -57.9483 | -0.086975 | -58.374 | 64.7736 | -58.2275 | -58.2733 | -58.0582 | -0.009155 | -58.374 | 64.8285 | 64.7141 | -58.3054 | -58.3694 | -0.064087 | -0.10986 | 0.064087 | 0.21515 | -0.21057 | -0.10071 | 0.041198 | -0.14191 | -0.20599 | 0.11902 | 0.10529 | -0.21057 | -0.004577 | 0.004577 | 122.937 | 122.9141 | 58.0765 | -122.9828 | 122.9919 | 122.8775 | 58.1543 | -123.0789
715.6406 | 123.2391 | -58.1497 | 64.7141 | 0.62913 | 0.037007 | 0.074173 | 0.011477 | 0.053397 | 0.013299 | -0.021058 | -0.10039 | -0.025069 | 0.05092 | 0.049872 | -0.00077485 | -0.020399 | 64.801 | -58.017 | -0.041199 | -58.5297 | 64.7644 | -58.2413 | -58.3008 | -58.049 | -0.018311 | -58.3603 | 64.8148 | 64.6912 | -58.287 | -58.3374 | -0.091553 | -0.15106 | 0.050354 | 0.13275 | -0.37994 | -0.22888 | 0.086975 | -0.13733 | -0.18768 | 0.10071 | 0.10071 | -0.21057 | -0.022889 | -0.022888 | 122.9141 | 122.9507 | 58.1085 | -123.0148 | 122.9645 | 122.8409 | 58.1314 | -123.0515
716.6406 | 123.2208 | -58.1451 | 64.7369 | 0.62913 | 0.015645 | 0.067764 | 0.025363 | 0.057669 | 0.013299 | -0.0050373 | 0.26582 | -0.022933 | 0.045579 | 0.057349 | 0.0099061 | -0.00865 | 64.7736 | -58.0582 | -0.16022 | -58.3694 | 64.8422 | -58.2275 | -58.287 | -58.0582 | -0.045776 | -58.4106 | 64.7873 | 64.6408 | -58.3237 | -58.3603 | -0.082397 | -0.14191 | 0.10529 | 0.086975 | -0.2243 | -0.082398 | 0.036622 | -0.17853 | -0.21515 | 0.050354 | 0.086975 | -0.2655 | -0.050354 | -0.09613 | 122.9874 | 122.9187 | 57.9849 | -123.024 | 122.9324 | 122.786 | 58.0994 | -123.0972
717.6875 | 123.0835 | -58.1772 | 64.7827 | 0.3087 | 0.038075 | 0.060287 | 0.029635 | 0.048056 | 0.027185 | -0.0050373 | 0.021682 | -0.012251 | 0.061601 | 0.056281 | 0.016315 | -0.030012 | 64.7598 | -58.1085 | -0.17853 | -58.4061 | 64.8697 | -58.2413 | -58.3008 | -58.1589 | -0.082397 | -58.4885 | 64.8834 | 64.7507 | -58.287 | -58.3923 | -0.064087 | -0.1236 | 0.086975 | 0.068664 | -0.22888 | -0.10529 | -0.022888 | -0.10986 | -0.21515 | 0.10071 | 0.01831 | -0.31128 | -0.09613 | -0.032044 | 123.0469 | 122.937 | 57.9987 | -123.0835 | 123.0606 | 122.9279 | 58.0948 | -123.175
718.6406 | 123.1934 | -58.1635 | 64.7369 | 1.1784 | 0.023121 | 0.084854 | 0.022158 | 0.046988 | -0.0080629 | -0.00076433 | 0.63203 | -0.021865 | 0.045579 | 0.049872 | -0.0039789 | -0.020399 | 64.7781 | -58.017 | -0.11902 | -58.3557 | 64.801 | -58.2184 | -58.2779 | -58.0765 | -0.013733 | -58.374 | 64.7964 | 64.7003 | -58.3008 | -58.3603 | -0.054932 | -0.11444 | 0.064087 | 0.14648 | -0.19226 | -0.07782 | 0.041199 | -0.13733 | -0.19684 | 0.05951 | 0.086975 | -0.21057 | -0.013732 | -0.036621 | 122.9645 | 122.9416 | 58.0444 | -123.0148 | 122.9599 | 122.8638 | 58.1497 | -123.0972
719.6406 | 123.23 | -58.168 | 64.7369 | -3.3382 | 0.022053 | 0.061355 | 0.026431 | 0.046988 | -0.0059269 | -0.016786 | 0.40315 | -0.015456 | 0.03917 | 0.056281 | 0.0013611 | -0.011854 | 64.7827 | -57.9849 | -0.10071 | -58.3557 | 64.7919 | -58.2184 | -58.2642 | -58.0856 | -0.027466 | -58.3649 | 64.8148 | 64.7049 | -58.2825 | -58.3603 | -0.050354 | -0.09613 | 0.054932 | 0.18311 | -0.18768 | -0.091553 | 0.045777 | -0.11444 | -0.19226 | 0.07782 | 0.082398 | -0.19684 | -0.004577 | -0.032043 | 122.9599 | 122.9507 | 58.0673 | -123.0011 | 122.9828 | 122.8729 | 58.1406 | -123.0972
720.6406 | 123.1934 | -58.1497 | 64.7461 | 0.56809 | 0.035939 | 0.072037 | 0.014682 | 0.051261 | 0.0015501 | -0.017854 | 0.66255 | -0.027205 | 0.043443 | 0.054145 | 0.0013611 | -0.007581 | 64.9933 | -58.1039 | -0.15106 | -58.3374 | 64.7598 | -58.2047 | -58.255 | -58.0856 | 0.004578 | -58.3649 | 64.8285 | 64.7186 | -58.2779 | -58.3511 | -0.054932 | -0.10529 | 0.013733 | 0.045776 | -0.18768 | -0.082397 | 0.24719 | -0.12817 | -0.20142 | 0.082397 | 0.064087 | -0.21515 | -0.013733 | -0.027466 | 122.9095 | 123.143 | 57.9987 | -123.0011 | 122.9782 | 122.8683 | 58.1543 | -123.0972
721.6406 | 123.2254 | -58.1497 | 64.7369 | 0.62913 | 0.025258 | 0.062424 | 0.014682 | 0.051261 | -0.0037909 | -0.01999 | 0.55574 | -0.031478 | 0.046647 | 0.058417 | 0.0088381 | -0.028944 | 64.8193 | -58.0444 | -0.064087 | -58.4656 | 64.769 | -58.2458 | -58.3466 | -58.0399 | -0.032043 | -58.3786 | 64.8056 | 64.7278 | -58.3054 | -58.3237 | -0.096131 | -0.19684 | 0.032044 | 0.10528 | -0.31586 | -0.11902 | 0.082398 | -0.15564 | -0.17395 | 0.068665 | 0.10986 | -0.22888 | -0.054932 | -0.009155 | 122.9187 | 122.9691 | 58.0856 | -123.0835 | 122.9553 | 122.8775 | 58.1177 | -123.0606
722.6406 | 123.2208 | -58.1726 | 64.7369 | 0.59861 | 0.031666 | 0.072037 | 0.02109 | 0.049125 | 0.0047541 | -0.021058 | 2.5852 | -0.019728 | 0.038102 | 0.0456 | 0.0088381 | -0.018263 | 64.7964 | -58.0399 | -0.14648 | -58.3466 | 64.7919 | -58.255 | -58.287 | -58.0673 | 0.091553 | -58.3878 | 64.8468 | 64.682 | -58.2916 | -58.3237 | -0.082398 | -0.11444 | 0.054932 | 0.13275 | -0.17395 | -0.05951 | 0.05951 | -0.11902 | -0.15106 | 0.10986 | 0.10529 | -0.21515 | -0.064087 | -0.054931 | 122.9645 | 122.9691 | 58.0261 | -123.024 | 123.0194 | 122.8546 | 58.2642 | -123.0606
723.6406 | 123.2391 | -58.168 | 64.7232 | 0.59861 | 0.026326 | 0.066696 | 0.029635 | 0.049125 | 0.013299 | -0.0071733 | 0.29634 | -0.019728 | 0.044511 | 0.048804 | 0.0045661 | -0.016126 | 64.7781 | -58.0902 | -0.17853 | -58.3832 | 64.8376 | -58.2413 | -58.3054 | -58.0765 | -0.17395 | -58.4198 | 64.8193 | 64.6957 | -58.3054 | -58.3786 | -0.073242 | -0.13733 | 0.11444 | 0.07782 | -0.21515 | -0.07782 | 0.054931 | -0.13733 | -0.21057 | 0.09613 | 0.091553 | -0.25177 | -0.041199 | -0.027466 | 123.0057 | 122.9462 | 57.9895 | -123.0286 | 122.9874 | 122.8638 | 57.9941 | -123.1018
724.6406 | 123.2117 | -58.1772 | 64.7507 | 0.58335 | 0.037007 | 0.068832 | 0.014682 | 0.056601 | 0.0068901 | -0.0061053 | 0.47945 | -0.014388 | 0.06801 | 0.0456 | 0.0077701 | -0.026808 | 64.7827 | -58.0994 | -0.19684 | -58.3649 | 64.8285 | -58.255 | -58.2916 | -58.0811 | -0.013733 | -58.374 | 64.856 | 64.7552 | -58.2825 | -58.3557 | -0.07782 | -0.11444 | 0.07782 | 0.07782 | -0.18768 | -0.073242 | 0.032044 | -0.10529 | -0.17853 | 0.10529 | 0.09613 | -0.19684 | -0.01831 | 0.004578 | 123.0057 | 122.9599 | 57.9803 | -123.0423 | 123.0331 | 122.9324 | 58.1635 | -123.1064
725.6406 | 123.1934 | -58.1406 | 64.7232 | 0.7512 | 0.030598 | 0.066696 | 0.010409 | 0.048056 | 0.0047541 | -0.016786 | 0.66255 | -0.026137 | 0.054124 | 0.055213 | -0.0039789 | -0.01399 | 64.801 | -58.0307 | -0.13275 | -58.3694 | 64.7919 | -58.2275 | -58.287 | -58.0856 | -0.018311 | -58.3832 | 64.7919 | 64.7507 | -58.2916 | -58.3786 | -0.086975 | -0.14648 | 0.068664 | 0.10986 | -0.22888 | -0.082398 | 0.077819 | -0.15106 | -0.23804 | 0.068664 | 0.054932 | -0.24262 | -0.004578 | 0.027465 | 122.9324 | 122.9416 | 58.0078 | -123.0103 | 122.9324 | 122.8912 | 58.1223 | -123.1018
726.6406 | 123.2162 | -58.1406 | 64.7324 | -0.011739 | 0.015645 | 0.0699 | 0.01575 | 0.056601 | -0.0080629 | -0.012513 | 0.52522 | -0.01332 | 0.05092 | 0.046668 | 0.01311 | -0.026808 | 64.801 | -58.0124 | -0.13275 | -58.3557 | 64.801 | -58.2092 | -58.2733 | -58.0719 | -0.032043 | -58.3786 | 64.8102 | 64.7232 | -58.3008 | -58.3832 | -0.068665 | -0.13275 | 0.068664 | 0.12817 | -0.21515 | -0.082398 | 0.068664 | -0.16022 | -0.24262 | 0.07782 | 0.068665 | -0.23804 | 0.004578 | -0.009155 | 122.9416 | 122.9416 | 58.0078 | -123.0057 | 122.9507 | 122.8638 | 58.1085 | -123.1155
727.6406 | 123.1705 | -58.1726 | 64.7278 | -2.5294 | 0.011372 | 0.066696 | 0.031771 | 0.044852 | 0.00048206 | -0.01999 | 0.43367 | -0.025069 | 0.048783 | 0.058417 | 0.0045661 | -0.021467 | 64.7964 | -57.9987 | -0.13733 | -58.3557 | 64.801 | -58.2184 | -58.2825 | -58.0856 | -0.032043 | -58.3694 | 64.8056 | 64.6912 | -58.3145 | -58.3786 | -0.045777 | -0.10986 | 0.073242 | 0.17395 | -0.18311 | -0.073242 | 0.068665 | -0.14191 | -0.20599 | 0.07782 | 0.086975 | -0.19684 | 0.009155 | -0.036621 | 122.9736 | 122.9691 | 58.0353 | -123.0103 | 122.9782 | 122.8638 | 58.1406 | -123.1064
728.6406 | 123.1888 | -58.1635 | 64.7278 | 3.2842 | 0.041279 | 0.089126 | 0.049929 | 0.04592 | 0.0036861 | -0.024263 | 0.61677 | -0.027205 | 0.043443 | 0.048804 | 0.0067021 | -0.019331 | 64.8788 | -58.0444 | -0.15564 | -58.3374 | 64.7873 | -58.1955 | -58.2596 | -58.0765 | -0.018311 | -58.3694 | 64.8148 | 64.6957 | -58.2733 | -58.3603 | -0.032044 | -0.096131 | 0.059509 | 0.11902 | -0.17395 | -0.077819 | 0.15106 | -0.10986 | -0.19684 | 0.086975 | 0.086975 | -0.20599 | -0.009155 | -0.032043 | 122.9507 | 123.0423 | 58.0078 | -122.9874 | 122.9782 | 122.8592 | 58.1451 | -123.0881
729.6406 | 123.1979 | -58.1497 | 64.7049 | 0.53758 | 0.0060322 | 0.0699 | 0.010409 | 0.049125 | 0.0015501 | -0.029603 | 0.84566 | -0.029341 | 0.034898 | 0.052009 | 0.01311 | -0.018263 | 65.0024 | -58.1177 | -0.16937 | -58.3145 | 64.7873 | -58.2047 | -58.2779 | -58.0582 | -0.027466 | -58.3786 | 64.8239 | 64.7232 | -58.3054 | -58.3649 | -0.054932 | -0.12817 | 0.082397 | 0.032043 | -0.1648 | -0.036621 | 0.29755 | -0.15564 | -0.21515 | 0.11902 | 0.091552 | -0.22888 | -0.013733 | 0.018311 | 122.937 | 123.1522 | 57.9803 | -122.9828 | 122.9736 | 122.8729 | 58.1223 | -123.0698
730.6406 | 123.2666 | -58.168 | 64.7186 | 0.32395 | 0.026326 | 0.070968 | 0.025363 | 0.058738 | 0.015435 | -0.0082413 | 0.40315 | -0.027205 | 0.05092 | 0.052009 | 0.012042 | -0.01399 | 64.7324 | -58.0124 | -0.16022 | -58.3557 | 64.7964 | -58.2275 | -58.2825 | -58.0765 | -0.045776 | -58.3649 | 64.7964 | 64.7095 | -58.2916 | -58.3694 | -0.059509 | -0.11444 | 0.07782 | 0.15564 | -0.18768 | -0.073242 | 0.013733 | -0.1236 | -0.20142 | 0.07782 | 0.091553 | -0.19684 | 0.004578 | -0.009155 | 122.9645 | 122.9004 | 58.0078 | -123.0011 | 122.9645 | 122.8775 | 58.1223 | -123.0881
731.6406 | 123.23 | -58.1589 | 64.7232 | 0.55284 | 0.011372 | 0.06456 | 0.025363 | 0.057669 | -0.0048589 | -0.016786 | 0.63203 | -0.025069 | 0.044511 | 0.044532 | 0.012042 | -0.011854 | 64.8376 | -58.1406 | -0.2243 | -58.342 | 64.801 | -58.2275 | -58.2916 | -58.0948 | -0.050354 | -58.374 | 64.8193 | 64.7232 | -58.2962 | -58.3603 | -0.068664 | -0.13275 | 0.077819 | 0.018311 | -0.1831 | -0.050354 | 0.11444 | -0.13733 | -0.20142 | 0.09613 | 0.064087 | -0.21515 | -0.013732 | 0 | 122.9599 | 122.9965 | 57.9346 | -123.0148 | 122.9782 | 122.8821 | 58.1085 | -123.0835
732.6406 | 123.2071 | -58.1451 | 64.7461 | 0.56809 | 0.019917 | 0.059219 | 0.013613 | 0.057669 | -0.0027229 | -0.0050373 | -0.78703 | -0.030409 | 0.061601 | 0.050941 | 0.0067021 | -0.018263 | 64.7919 | -58.0399 | -0.27466 | -58.4793 | 64.7461 | -58.2733 | -58.3008 | -58.0856 | -0.036621 | -58.3557 | 64.8331 | 64.7186 | -58.2779 | -58.3603 | -0.12817 | -0.15564 | 0 | 0.10529 | -0.33417 | -0.17853 | 0.045776 | -0.13275 | -0.21515 | 0.086975 | 0.05951 | -0.21057 | 0.004578 | -0.027466 | 122.8912 | 122.937 | 57.8705 | -123.0469 | 122.9782 | 122.8638 | 58.1085 | -123.1064
733.6406 | 123.2071 | -58.1589 | 64.7461 | 0.44602 | 0.0049632 | 0.076309 | 0.026431 | 0.04592 | -0.0027229 | -0.011445 | 0.54048 | -0.026137 | 0.054124 | 0.061622 | 0.01311 | -0.015058 | 64.7919 | -58.0215 | -0.15564 | -58.374 | 64.7964 | -58.223 | -58.2779 | -58.0811 | -0.068665 | -58.3969 | 64.8514 | 64.7461 | -58.2687 | -58.3694 | -0.064086 | -0.11902 | 0.050354 | 0.13733 | -0.21515 | -0.09613 | 0.045776 | -0.10986 | -0.21057 | 0.10528 | 0.07782 | -0.23804 | -0.027466 | 0 | 122.9553 | 122.9507 | 58.0032 | -123.024 | 123.0103 | 122.905 | 58.0902 | -123.1155
734.6406 | 123.2025 | -58.1955 | 64.7461 | 0.53758 | 0.019917 | 0.073105 | 0.025363 | 0.043784 | 0.0015501 | -0.028535 | 0.4947 | -0.022933 | 0.061601 | 0.044532 | -0.00077485 | -0.022535 | 64.7964 | -58.049 | -0.16479 | -58.3786 | 64.8102 | -58.2184 | -58.2916 | -58.0856 | -0.059509 | -58.3878 | 64.8285 | 64.7461 | -58.2962 | -58.3466 | -0.022888 | -0.09613 | 0.064087 | 0.14648 | -0.18311 | -0.086975 | 0.050354 | -0.10071 | -0.15106 | 0.082397 | 0.10986 | -0.19226 | -0.041198 | 0 | 123.0057 | 122.9919 | 58.0307 | -123.0377 | 123.024 | 122.9416 | 58.136 | -123.0927
735.6406 | 123.1934 | -58.168 | 64.7461 | 0.4918 | 0.013508 | 0.067764 | 0.026431 | 0.048056 | -0.017676 | -0.023195 | 0.55574 | -0.016524 | 0.061601 | 0.058417 | -0.0018429 | -0.015058 | 64.8056 | -58.0307 | -0.16937 | -58.374 | 64.8193 | -58.2138 | -58.2825 | -58.1039 | -0.064087 | -58.3878 | 64.8148 | 64.7324 | -58.3008 | -58.3466 | -0.045776 | -0.11444 | 0.073242 | 0.13733 | -0.20599 | -0.091552 | 0.059509 | -0.13275 | -0.17853 | 0.068664 | 0.064087 | -0.21973 | -0.041198 | -0.013733 | 122.9874 | 122.9736 | 57.9987 | -123.0286 | 122.9828 | 122.9004 | 58.1039 | -123.0927
736.6406 | 123.1842 | -58.1726 | 64.7278 | 0.43077 | 0.022053 | 0.072037 | 0.0093408 | 0.050193 | 0.0026181 | -0.015718 | 0.4947 | -0.01866 | 0.053056 | 0.048804 | 0.014179 | -0.024671 | 64.8056 | -58.0124 | -0.16479 | -58.3603 | 64.7873 | -58.2275 | -58.2825 | -58.0811 | -0.068665 | -58.3923 | 64.8148 | 64.7186 | -58.2962 | -58.374 | -0.054932 | -0.10986 | 0.059509 | 0.16022 | -0.18768 | -0.07782 | 0.07782 | -0.1236 | -0.20142 | 0.086975 | 0.091552 | -0.21973 | -0.018311 | -0.009155 | 122.9599 | 122.9782 | 58.0078 | -123.0103 | 122.9874 | 122.8912 | 58.1039 | -123.1018
737.6406 | 123.2071 | -58.1497 | 64.7232 | 0.61387 | 0.0081682 | 0.072037 | 0.023226 | 0.048056 | -0.0016549 | -0.010377 | 0.4947 | -0.028273 | 0.05626 | 0.050941 | 0.0099061 | -0.01399 | 64.8193 | -58.017 | -0.16937 | -58.342 | 64.7919 | -58.2367 | -58.2962 | -58.1818 | -0.11902 | -58.2413 | 64.7964 | 64.7186 | -58.2962 | -58.3466 | -0.086975 | -0.14649 | 0.068664 | 0.13275 | -0.19226 | -0.045776 | 0.09613 | -0.14649 | -0.19684 | 0.073242 | -0.032044 | -0.091553 | 0.10529 | -0.004578 | 122.9416 | 122.9691 | 57.9803 | -123.0194 | 122.9462 | 122.8683 | 58.0307 | -123.0698
738.6406 | 123.2346 | -58.1726 | 64.7278 | 0.43077 | 0.020985 | 0.072037 | 0.036044 | 0.057669 | -0.0059269 | -0.01465 | 0.571 | -0.03575 | 0.060533 | 0.052009 | 0.0034971 | -0.017194 | 64.801 | -58.0261 | -0.1831 | -58.3603 | 64.7964 | -58.2275 | -58.2916 | -58.0765 | -0.068665 | -58.3969 | 64.8056 | 64.7507 | -58.2825 | -58.3374 | -0.054932 | -0.11902 | 0.068665 | 0.14648 | -0.18768 | -0.068665 | 0.073242 | -0.10986 | -0.16479 | 0.07782 | 0.09613 | -0.22431 | -0.05951 | 0.022888 | 122.9691 | 122.9736 | 57.9895 | -123.0194 | 122.9782 | 122.9233 | 58.1039 | -123.0652
739.6406 | 123.1567 | -58.1543 | 64.7507 | 0.52232 | 0.00069119 | 0.074173 | 0.024295 | 0.036307 | -0.0048589 | -0.0093093 | 0.32686 | -0.014388 | 0.048783 | 0.056281 | -0.00077485 | -0.028944 | 64.7598 | -58.0673 | -0.18768 | -58.3649 | 64.8056 | -58.2092 | -58.2733 | -58.1085 | -0.07782 | -58.3786 | 64.8239 | 64.7552 | -58.2733 | -58.342 | -0.054932 | -0.11902 | 0.054932 | 0.086975 | -0.21057 | -0.091553 | 0.009156 | -0.11902 | -0.18768 | 0.073243 | 0.045776 | -0.2243 | -0.036621 | 0.004578 | 122.9599 | 122.9141 | 57.9666 | -123.024 | 122.9782 | 122.9095 | 58.0765 | -123.0927
740.6406 | 123.2025 | -58.1635 | 64.7644 | 0.2324 | -0.0099898 | 0.073105 | 0.010409 | 0.051261 | -0.0080629 | -0.028535 | 0.22005 | -0.026137 | 0.032762 | 0.043464 | 0.0034971 | -0.017194 | 64.7552 | -58.0627 | -0.1831 | -58.3694 | 64.8468 | -58.2275 | -58.2642 | -58.1497 | -0.009155 | -58.3786 | 64.8834 | 64.7095 | -58.2687 | -58.3374 | -0.064087 | -0.10071 | 0.082398 | 0.10071 | -0.20599 | -0.10529 | -0.009155 | -0.10529 | -0.17395 | 0.11902 | 0.013733 | -0.21515 | -0.041199 | -0.054931 | 123.0103 | 122.9187 | 57.9803 | -123.0286 | 123.0469 | 122.8729 | 58.1543 | -123.1018
741.6406 | 123.2162 | -58.1589 | 64.7781 | 0.53758 | -0.0025128 | 0.076309 | 0.023226 | 0.042716 | -0.0027229 | -0.023195 | 0.20479 | -0.031478 | 0.045579 | 0.056281 | 0.0034971 | -0.019331 | 64.7736 | -58.0399 | -0.21057 | -58.3832 | 64.8193 | -58.2184 | -58.2962 | -58.0902 | -0.064087 | -58.4061 | 64.8376 | 64.7232 | -58.3191 | -58.3328 | -0.059509 | -0.13733 | 0.041199 | 0.11902 | -0.2243 | -0.086975 | -0.004577 | -0.16022 | -0.17395 | 0.059509 | 0.068665 | -0.24719 | -0.073242 | -0.054931 | 122.9782 | 122.9324 | 57.9483 | -123.0743 | 122.9965 | 122.8821 | 58.0948 | -123.111
742.6406 | 123.2025 | -58.1589 | 64.7415 | -0.57631 | -0.0014448 | 0.063492 | 0.016818 | 0.051261 | 0.0079581 | -0.016786 | 0.50996 | -0.026137 | 0.051988 | 0.061622 | 0.0077701 | -0.018263 | 64.8148 | -58.0124 | -0.17853 | -58.3466 | 64.8056 | -58.223 | -58.2642 | -58.0627 | -0.068665 | -58.3786 | 64.8148 | 64.7232 | -58.2962 | -58.3557 | -0.064086 | -0.10528 | 0.064087 | 0.14648 | -0.18768 | -0.082398 | 0.073242 | -0.13733 | -0.19684 | 0.073242 | 0.096131 | -0.21973 | -0.022888 | -0.01831 | 122.9645 | 122.9736 | 57.9803 | -123.0057 | 122.9736 | 122.8821 | 58.0902 | -123.0972
743.6406 | 123.175 | -58.1543 | 64.769 | 0.47654 | 0.0092362 | 0.074173 | 0.02109 | 0.057669 | -0.010199 | -0.0071733 | 0.40315 | -0.025069 | 0.054124 | 0.052009 | -0.00077485 | -0.021467 | 64.7827 | -58.0399 | -0.22888 | -58.3786 | 64.801 | -58.2047 | -58.2825 | -58.0765 | -0.11902 | -58.4106 | 64.8239 | 64.7278 | -58.2825 | -58.3511 | -0.050354 | -0.12817 | 0.032043 | 0.11444 | -0.2243 | -0.09613 | 0.013733 | -0.12817 | -0.19684 | 0.054932 | 0.07782 | -0.25635 | -0.05951 | -0.041199 | 122.9553 | 122.937 | 57.9254 | -123.0515 | 122.9782 | 122.8821 | 58.0353 | -123.1201
744.6406 | 123.1888 | -58.1406 | 64.7324 | -1.9038 | 0.028462 | 0.070968 | 0.024295 | 0.048056 | 0.013299 | -0.017854 | 0.29634 | -0.030409 | 0.047715 | 0.054145 | 0.010974 | -0.005445 | 64.8331 | -57.9941 | -0.1831 | -58.3603 | 64.801 | -58.1863 | -58.2733 | -58.0536 | -0.073242 | -58.374 | 64.8148 | 64.7324 | -58.2733 | -58.3511 | -0.045776 | -0.13275 | 0.068664 | 0.14648 | -0.21973 | -0.086976 | 0.10071 | -0.13275 | -0.21057 | 0.082397 | 0.086975 | -0.23346 | -0.022888 | 0 | 122.9416 | 122.9736 | 57.9575 | -123.0057 | 122.9553 | 122.8729 | 58.0673 | -123.0835
745.6406 | 123.1888 | -58.1863 | 64.7598 | -2.3006 | 0.013508 | 0.0699 | 0.013613 | 0.060874 | 0.00048206 | -0.0039683 | 0.25056 | -0.01332 | 0.045579 | 0.066962 | 0.0077701 | -0.017194 | 64.7919 | -57.9575 | -0.16937 | -58.3603 | 64.8239 | -58.2092 | -58.255 | -58.0536 | -0.082397 | -58.3694 | 64.8422 | 64.7324 | -58.2779 | -58.3145 | -0.022889 | -0.068665 | 0.064087 | 0.22888 | -0.17395 | -0.10529 | 0.032043 | -0.091553 | -0.12817 | 0.082397 | 0.13275 | -0.18311 | -0.054932 | -0.027466 | 123.0103 | 122.9782 | 58.017 | -123.0148 | 123.0286 | 122.9187 | 58.1039 | -123.0743
746.6406 | 123.1796 | -58.1131 | 64.7736 | 0.26292 | 0.02419 | 0.082718 | 0.010409 | 0.042716 | -0.021949 | -0.0093093 | 0.18953 | -0.019728 | 0.051988 | 0.044532 | -0.0061159 | -0.011854 | 64.7873 | -58.0307 | -0.21057 | -58.3466 | 64.8651 | -58.1909 | -58.2642 | -58.0856 | -0.07782 | -58.3694 | 64.888 | 64.7736 | -58.2825 | -58.3054 | -0.07782 | -0.15106 | 0.091552 | 0.082397 | -0.23346 | -0.082398 | 0.013732 | -0.16937 | -0.19226 | 0.11444 | 0.027466 | -0.25635 | -0.064087 | 0 | 122.9782 | 122.9004 | 57.9025 | -123.0377 | 123.0011 | 122.8867 | 58.0353 | -123.0789
747.6406 | 123.1934 | -58.1223 | 64.7507 | 0.33921 | 0.0092362 | 0.067764 | 0.020022 | 0.061942 | -0.0027229 | -0.025331 | 0.29634 | -0.037886 | 0.051988 | 0.041327 | 0.0077701 | -0.011854 | 64.7781 | -58.0582 | -0.2243 | -58.3603 | 64.8514 | -58.2275 | -58.2825 | -58.0765 | -0.07782 | -58.3786 | 64.8605 | 64.801 | -58.255 | -58.3008 | -0.10529 | -0.16022 | 0.10071 | 0.064086 | -0.23804 | -0.07782 | 0.027466 | -0.13275 | -0.17853 | 0.10986 | 0.045776 | -0.25635 | -0.07782 | 0.050354 | 122.9736 | 122.9004 | 57.8979 | -123.0331 | 122.9828 | 122.9233 | 58.0444 | -123.0515
748.6406 | 123.1842 | -58.1497 | 64.7369 | 0.18663 | -0.0025128 | 0.077377 | 0.020022 | 0.035239 | -0.010199 | -0.017854 | 0.29634 | -0.036818 | 0.051988 | 0.041327 | -0.0018429 | -0.019331 | 64.7781 | -58.0444 | -0.21973 | -58.3694 | 64.8468 | -58.168 | -58.255 | -58.1039 | -0.032043 | -58.2825 | 64.8697 | 64.7919 | -58.2733 | -58.3145 | -0.018311 | -0.10529 | 0.10986 | 0.10528 | -0.21973 | -0.11444 | 0.041199 | -0.1236 | -0.1648 | 0.13275 | 0.045776 | -0.13275 | 0.032043 | 0.054932 | 122.9965 | 122.9279 | 57.93 | -122.9919 | 123.0194 | 122.9416 | 58.1177 | -123.0515
749.6406 | 123.2025 | -58.1543 | 64.7461 | 0.36973 | -0.011058 | 0.072037 | 0.01575 | 0.046988 | -0.0048589 | -0.025331 | 0.18953 | -0.037886 | 0.042375 | 0.0456 | 0.0045661 | -0.022535 | 64.7644 | -58.0444 | -0.21515 | -58.3557 | 64.8285 | -58.2047 | -58.2779 | -58.0307 | 0.086975 | -58.3923 | 64.8605 | 64.7598 | -58.2733 | -58.3466 | -0.050354 | -0.1236 | 0.082397 | 0.10986 | -0.20142 | -0.07782 | 0.01831 | -0.11902 | -0.19226 | 0.11444 | 0.1236 | -0.23804 | -0.045776 | 0.013733 | 122.9828 | 122.9187 | 57.9391 | -123.024 | 123.0148 | 122.9141 | 58.2413 | -123.0927
750.6406 | 123.2025 | -58.1406 | 64.7781 | 0.26292 | -0.013195 | 0.08699 | 0.013613 | 0.041648 | 0.0026181 | -0.022126 | 0.2353 | -0.010115 | 0.042375 | 0.053077 | -0.0061159 | -0.019331 | 64.7781 | -58.0399 | -0.21973 | -58.3374 | 64.8468 | -58.1955 | -58.2916 | -58.1177 | -0.07782 | -58.3649 | 64.8605 | 64.7461 | -58.287 | -58.3282 | -0.054932 | -0.15106 | 0.068665 | 0.10071 | -0.19684 | -0.045776 | 0 | -0.14648 | -0.18768 | 0.082398 | 0.022888 | -0.2243 | -0.036621 | -0.032043 | 122.9874 | 122.9187 | 57.9208 | -123.0698 | 123.0011 | 122.8867 | 58.0627 | -123.1064
751.6406 | 123.1842 | -58.1543 | 64.7827 | 0.50706 | -0.0014448 | 0.077377 | 0.01575 | 0.048056 | 0.0015501 | -0.023195 | 0.35738 | -0.027205 | 0.062669 | 0.052009 | -0.012524 | -0.017194 | 64.7919 | -58.0261 | -0.24719 | -58.3649 | 64.8422 | -58.1818 | -58.2733 | -58.1039 | -0.10986 | -58.3878 | 64.8697 | 64.7552 | -58.2916 | -58.3466 | -0.027466 | -0.11902 | 0.059509 | 0.12817 | -0.21057 | -0.091553 | 0.009155 | -0.13733 | -0.19226 | 0.086975 | 0.050354 | -0.23346 | -0.041198 | -0.027466 | 122.9965 | 122.9462 | 57.9071 | -123.056 | 123.024 | 122.9095 | 58.0444 | -123.1293
752.6406 | 123.1934 | -58.1543 | 64.7736 | 0.27818 | -0.00037681 | 0.0699 | 0.03818 | 0.051261 | -0.0027229 | -0.021058 | -0.37505 | -0.022933 | 0.028489 | 0.050941 | -0.0039789 | -0.023603 | 64.7873 | -58.0307 | -0.23804 | -58.3557 | 64.8422 | -58.2047 | -58.2596 | -58.0765 | -0.091553 | -58.3694 | 64.8468 | 64.7415 | -58.2642 | -58.3191 | -0.050354 | -0.10529 | 0.068664 | 0.1236 | -0.20142 | -0.09613 | 0.013732 | -0.10986 | -0.16479 | 0.073242 | 0.07782 | -0.21515 | -0.050354 | -0.032044 | 122.9965 | 122.9416 | 57.9163 | -123.0331 | 123.0011 | 122.8958 | 58.0627 | -123.0927
753.6406 | 123.2346 | -58.1131 | 64.7644 | 0.018779 | 0.0060322 | 0.074173 | 0.023226 | 0.056601 | -0.012336 | -0.036012 | 0.067459 | -0.029341 | 0.040239 | 0.047736 | -0.0029109 | -0.019331 | 64.8331 | -57.962 | -0.18768 | -58.3191 | 64.8651 | -58.1863 | -58.2504 | -58.0032 | 0 | -58.3145 | 64.8605 | 64.7324 | -58.2687 | -58.3237 | -0.073242 | -0.13733 | 0.10071 | 0.15106 | -0.20599 | -0.068665 | 0.068665 | -0.15564 | -0.21057 | 0.096131 | 0.10986 | -0.20142 | 0.009155 | -0.032043 | 122.9782 | 122.9462 | 57.9254 | -123.0148 | 122.9736 | 122.8455 | 58.1131 | -123.0881
754.6406 | 123.2254 | -58.1223 | 64.7781 | 0.14085 | -0.0014448 | 0.070968 | 0.011477 | 0.052329 | 0.00048206 | -0.022126 | 0.067459 | -0.026137 | 0.048783 | 0.037055 | 0.0045661 | -0.021467 | 64.8239 | -57.9666 | -0.17395 | -58.3191 | 64.8926 | -58.1772 | -58.2001 | -58.0032 | 0.009155 | -58.3054 | 64.8697 | 64.7415 | -58.2458 | -58.3099 | -0.054932 | -0.07782 | 0.11444 | 0.15564 | -0.19684 | -0.11902 | 0.045777 | -0.1236 | -0.18768 | 0.091553 | 0.11902 | -0.18311 | 0.004578 | -0.036621 | 123.0148 | 122.9462 | 57.9483 | -122.9782 | 122.9919 | 122.8638 | 58.1314 | -123.0881
755.6406 | 123.2437 | -58.1085 | 64.7781 | 0.17137 | -0.014263 | 0.089126 | 0.027499 | 0.055533 | -0.0027229 | -0.026399 | 0.021682 | -0.026137 | 0.047715 | 0.037055 | 0.0067021 | -0.019331 | 64.8605 | -57.9391 | -0.17853 | -58.3054 | 64.8605 | -58.1818 | -58.2413 | -57.9987 | 0.004578 | -58.3145 | 64.8468 | 64.7507 | -58.2504 | -58.287 | -0.073242 | -0.13275 | 0.082398 | 0.16937 | -0.19684 | -0.064087 | 0.082398 | -0.14191 | -0.17853 | 0.068665 | 0.10986 | -0.20599 | -0.027466 | -0.027466 | 122.9691 | 122.9691 | 57.93 | -123.0194 | 122.9553 | 122.8592 | 58.1131 | -123.0652
756.6406 | 123.2574 | -58.1085 | 64.8102 | 0.064555 | -0.0078538 | 0.082718 | 0.026431 | 0.064078 | -0.0016549 | -0.024263 | 0.0522 | -0.040022 | 0.042375 | 0.0456 | 0.0034971 | -0.024671 | 64.8376 | -57.9391 | -0.18768 | -58.2779 | 64.8697 | -58.1451 | -58.2001 | -57.9941 | -0.013733 | -58.287 | 64.8926 | 64.7415 | -58.2367 | -58.2779 | -0.036621 | -0.091552 | 0.059509 | 0.16937 | -0.16937 | -0.07782 | 0.027465 | -0.12817 | -0.16937 | 0.082397 | 0.11444 | -0.17853 | -0.009155 | -0.068665 | 122.9782 | 122.9462 | 57.9208 | -123.0103 | 123.0011 | 122.85 | 58.0948 | -123.0881
757.6406 | 123.23 | -58.0719 | 64.8239 | 0.079814 | 0.0071002 | 0.078445 | 0.027499 | 0.050193 | 0.0015501 | -0.024263 | 0.11323 | -0.03575 | 0.042375 | 0.034919 | -0.0018429 | -0.016126 | 64.8651 | -57.9163 | -0.18768 | -58.2779 | 64.8788 | -58.168 | -58.223 | -58.0032 | -0.018311 | -58.287 | 64.8788 | 64.7415 | -58.2184 | -58.2825 | -0.096131 | -0.15106 | 0.054931 | 0.15564 | -0.20599 | -0.054932 | 0.041198 | -0.14648 | -0.21057 | 0.054931 | 0.068664 | -0.21515 | -0.004577 | -0.082398 | 122.9507 | 122.937 | 57.8842 | -123.0469 | 122.9507 | 122.8134 | 58.0536 | -123.1064
758.6406 | 123.2208 | -58.0902 | 64.8331 | -0.13381 | -0.0035808 | 0.079513 | 0.016818 | 0.049125 | -0.0059269 | -0.022126 | 0.082718 | -0.026137 | 0.054124 | 0.053077 | 0.0077701 | -0.020399 | 64.7964 | -57.9666 | -0.22888 | -58.3237 | 64.9155 | -58.1772 | -58.223 | -58.0399 | -0.059509 | -58.3145 | 64.8926 | 64.7369 | -58.2458 | -58.2916 | -0.086975 | -0.13275 | 0.082397 | 0.1236 | -0.23346 | -0.10071 | -0.036621 | -0.15564 | -0.20142 | 0.059509 | 0.050354 | -0.2243 | -0.022888 | -0.096131 | 123.0057 | 122.8867 | 57.8613 | -123.056 | 122.9828 | 122.8271 | 58.0307 | -123.1247
759.6406 | 123.2254 | -58.049 | 64.8422 | -0.011739 | -0.011058 | 0.070968 | 0.0061368 | 0.053397 | -0.0080629 | -0.011445 | 0.18953 | -0.031478 | 0.045579 | 0.039191 | 0.00029315 | -0.023603 | 64.9017 | -57.8567 | -0.17395 | -58.255 | 64.888 | -58.1635 | -58.2001 | -57.9025 | 0.036621 | -58.2367 | 64.9292 | 64.7873 | -58.1955 | -58.2458 | -0.11444 | -0.15106 | 0.045776 | 0.19226 | -0.20599 | -0.054932 | 0.059509 | -0.14648 | -0.19684 | 0.086975 | 0.14648 | -0.18768 | 0.009156 | -0.054932 | 122.937 | 122.9507 | 57.8751 | -123.0423 | 122.9782 | 122.8363 | 58.0856 | -123.0881
760.6406 | 123.2346 | -58.0307 | 64.8788 | -0.11855 | 0.019917 | 0.090195 | 0.02109 | 0.04592 | -0.0069949 | -0.01465 | -1.1685 | -0.027205 | 0.049852 | 0.024238 | 0.0056341 | -0.036421 | 64.9704 | -57.7835 | -0.27466 | -58.0307 | 65.0024 | -58.0536 | -58.1451 | -57.962 | 0.032043 | -58.2047 | 64.9658 | 64.8285 | -58.1543 | -58.2001 | -0.022888 | -0.11444 | 0.1236 | 0.24719 | 0 | 0.11444 | 0.091553 | -0.1236 | -0.16937 | 0.086975 | 0.068665 | -0.17395 | -0.004578 | -0.050354 | 123.0331 | 123.0011 | 57.756 | -123.024 | 122.9965 | 122.8592 | 58.0627 | -123.0789
761.6406 | 123.2208 | -58.0078 | 64.8834 | -0.17959 | -0.0025128 | 0.0699 | 0.050997 | 0.04058 | 0.013299 | 0.0035077 | -0.68022 | -0.029341 | 0.045579 | 0.046668 | 0.017383 | -0.016126 | 64.7232 | -57.692 | -0.13275 | -58.2825 | 64.9429 | -58.0627 | -58.1635 | -57.9437 | 0.027466 | -58.2321 | 64.9841 | 64.8422 | -58.1543 | -58.2092 | -0.054932 | -0.15564 | 0.059509 | 0.31586 | -0.27466 | -0.11902 | -0.16022 | -0.14648 | -0.20142 | 0.10071 | 0.064086 | -0.22431 | -0.022888 | -0.041199 | 122.9507 | 122.731 | 57.8751 | -123.0469 | 122.9919 | 122.85 | 58.0353 | -123.0927
762.6406 | 123.1934 | -57.8934 | 65.0436 | -1.7207 | 0.0081682 | 0.072037 | 0.031771 | 0.04592 | 0.0026181 | -0.021058 | -0.26824 | -0.021865 | 0.05626 | 0.048804 | 0.0056341 | -0.026808 | 64.9979 | -57.6691 | -0.16022 | -58.1085 | 65.0574 | -58.017 | -58.0811 | -57.8613 | 0.018311 | -58.1314 | 65.0757 | 64.9384 | -58.0582 | -58.1406 | -0.1236 | -0.18768 | 0.013733 | 0.22431 | -0.21515 | -0.027466 | -0.045776 | -0.16479 | -0.24719 | 0.032044 | 0.032044 | -0.23804 | 0.009155 | -0.10529 | 122.9507 | 122.8912 | 57.7332 | -123.1247 | 122.9691 | 122.8317 | 57.9117 | -123.1842
763.6406 | 123.2025 | -33.8013 | 89.2548 | -0.39321 | -0.0014448 | 0.077377 | 0.024295 | 0.064078 | 0.00048206 | -0.015718 | -0.13091 | -0.033614 | 0.043443 | 0.042396 | 0.0077701 | -0.024671 | 89.1357 | -21.373 | -0.009155 | -34.0164 | 89.2776 | -33.8058 | -33.8837 | -33.847 | 0.1236 | -34.053 | 89.296 | 89.1541 | -33.8791 | -33.9432 | -0.004577 | -0.082397 | 0.022888 | 12.4283 | -0.21515 | -0.13275 | -0.11902 | -0.077819 | -0.14191 | 0.041198 | -0.045776 | -0.25177 | -0.10986 | -0.10071 | 123.0789 | 122.937 | 33.7921 | -123.1384 | 123.0972 | 122.9553 | 33.9249 | -123.1979
764.6406 | 123.2117 | -57.9437 | 64.92 | -0.13381 | -0.00037681 | 0.076309 | 0.028567 | 0.053397 | -0.0080629 | -0.01465 | -0.4666 | -0.040022 | 0.063737 | 0.063758 | 0.010974 | -0.027876 | 64.975 | -57.7148 | -0.15106 | -58.1589 | 65.0024 | -58.0536 | -58.0994 | -57.811 | -0.10529 | -58.1955 | 64.9933 | 64.8468 | -58.136 | -58.1863 | -0.10986 | -0.15564 | 0.082397 | 0.22888 | -0.21515 | -0.05951 | 0.054932 | -0.19226 | -0.24261 | 0.073242 | 0.13275 | -0.25177 | -0.009156 | -0.073242 | 122.9462 | 122.9187 | 57.7927 | -123.0194 | 122.937 | 122.7905 | 57.8384 | -123.1064
765.6406 | 123.2071 | -57.9529 | 64.9475 | -0.30166 | -0.0057178 | 0.080581 | 0.026431 | 0.039511 | 0.0036861 | -0.0039683 | -0.97014 | -0.024001 | 0.041307 | 0.047736 | -0.0018429 | -0.027876 | 64.8834 | -57.3257 | 0.045776 | -58.3237 | 65.0574 | -58.0078 | -58.0994 | -57.8705 | 0 | -58.1406 | 65.0253 | 64.8926 | -58.1085 | -58.1589 | -0.054931 | -0.14648 | 0.10986 | 0.62714 | -0.37079 | -0.2243 | -0.064087 | -0.15564 | -0.20599 | 0.07782 | 0.082398 | -0.18768 | 0.018311 | -0.054932 | 123.0103 | 122.8363 | 57.9987 | -123.0469 | 122.9782 | 122.8455 | 57.9529 | -123.1064
766.6875 | 123.2437 | -57.9712 | 64.9567 | -3.3382 | 0.011372 | 0.067764 | 0.030703 | 0.044852 | 0.0090271 | -0.010377 | -0.37505 | -0.026137 | 0.049852 | 0.038123 | -0.0018429 | -0.021467 | 64.8743 | -57.7286 | -0.1831 | -58.1863 | 64.9796 | -58.0673 | -58.1039 | -57.9163 | 0.018311 | -58.1863 | 65.0162 | 64.8834 | -58.1223 | -58.1726 | -0.096131 | -0.13275 | 0.022888 | 0.24261 | -0.21515 | -0.082397 | -0.082397 | -0.15106 | -0.20142 | 0.059509 | 0.054931 | -0.21515 | -0.013733 | -0.073242 | 122.9507 | 122.8455 | 57.7881 | -123.0606 | 122.9874 | 122.8546 | 57.9895 | -123.1293
767.6406 | 123.111 | -58.049 | 64.9384 | -0.31691 | 0.020985 | 0.079513 | 0.037112 | 0.046988 | 0.012231 | -0.0082413 | -0.35979 | -0.027205 | 0.048783 | 0.054145 | -0.0071839 | -0.027876 | 64.9109 | -57.8705 | -0.28381 | -58.2596 | 65.0253 | -58.0765 | -58.1406 | -58.0032 | 0.19684 | -58.4335 | 65.0848 | 64.92 | -58.1497 | -58.2275 | -0.027466 | -0.091553 | 0.086976 | 0.17853 | -0.21057 | -0.11902 | -0.027465 | -0.10071 | -0.17853 | 0.14648 | 0.045776 | -0.38452 | -0.20599 | -0.01831 | 123.0743 | 122.9599 | 57.7652 | -123.0789 | 123.1338 | 122.9691 | 58.2458 | -123.1659
768.6406 | 123.1155 | -58.0124 | 64.975 | -0.19484 | 0.015645 | 0.058151 | 0.033908 | 0.055533 | 0.013299 | 0.0013717 | -0.84807 | -0.011183 | 0.058397 | 0.043464 | 0.012042 | -0.017194 | 64.9017 | -57.8339 | -0.3479 | -58.2321 | 65.0757 | -58.0444 | -58.1131 | -58.0399 | -0.10071 | -58.2733 | 65.0894 | 64.9429 | -58.1497 | -58.2092 | -0.032044 | -0.10071 | 0.10071 | 0.17853 | -0.21973 | -0.11902 | -0.073243 | -0.13733 | -0.19684 | 0.11444 | -0.027466 | -0.26092 | -0.064086 | -0.032044 | 123.0881 | 122.9141 | 57.6645 | -123.0881 | 123.1018 | 122.9553 | 57.9117 | -123.1842
769.6406 | 123.1018 | -58.0078 | 64.9933 | -0.24062 | 0.025258 | 0.079513 | 0.010409 | 0.042716 | 0.00048206 | -0.021058 | -0.9091 | -0.015456 | 0.037034 | 0.044532 | 0.0056341 | -0.021467 | 64.9612 | -57.5775 | -0.27466 | -58.3054 | 65.0848 | -58.0536 | -58.1131 | -57.962 | -0.10071 | -58.2458 | 65.1031 | 64.9796 | -58.0994 | -58.1635 | -0.045777 | -0.10529 | 0.091553 | 0.4303 | -0.29755 | -0.19226 | -0.032043 | -0.091553 | -0.15564 | 0.10986 | 0.045776 | -0.23804 | -0.082398 | -0.013733 | 123.0927 | 122.9691 | 57.7332 | -123.1064 | 123.111 | 122.9874 | 57.9071 | -123.1567
770.6406 | 123.1247 | -57.9346 | 65.0482 | -0.22536 | 0.02419 | 0.085922 | 0.058474 | 0.046988 | 0.014367 | -0.01999 | -0.22246 | -0.016524 | 0.048783 | 0.041327 | 0.0013611 | -0.017194 | 65.0024 | -57.7698 | -0.33875 | -58.1451 | 65.1215 | -57.9758 | -58.0673 | -57.9163 | -0.11902 | -58.1863 | 65.1443 | 65.0299 | -58.049 | -58.1223 | -0.041199 | -0.13275 | 0.073242 | 0.16479 | -0.21057 | -0.07782 | -0.045777 | -0.11444 | -0.18768 | 0.09613 | 0.01831 | -0.25177 | -0.064087 | -0.018311 | 123.056 | 122.937 | 57.5958 | -123.1155 | 123.0789 | 122.9645 | 57.8156 | -123.1705
771.6406 | 123.0927 | -57.9666 | 65.0528 | 0.20188 | 0.0081682 | 0.073105 | 0.03818 | 0.058738 | -0.0069949 | -0.022126 | -0.28349 | -0.0079794 | 0.045579 | 0.048804 | -0.0029109 | -0.027876 | 64.9475 | -57.756 | -0.29297 | -58.1589 | 65.0986 | -57.9941 | -58.0902 | -57.9391 | -0.09613 | -58.2047 | 65.1352 | 64.9887 | -58.0811 | -58.0994 | -0.027466 | -0.1236 | 0.045777 | 0.21057 | -0.19226 | -0.068665 | -0.10529 | -0.11444 | -0.13275 | 0.082398 | 0.027466 | -0.23804 | -0.10529 | -0.064087 | 123.0652 | 122.9141 | 57.6736 | -123.143 | 123.1018 | 122.9553 | 57.8705 | -123.1522
772.6406 | 123.1567 | -57.8751 | 65.1581 | -0.33217 | 0.017781 | 0.068832 | 0.033908 | 0.046988 | -0.0048589 | -0.0093093 | -0.28349 | -0.016524 | 0.049852 | 0.035987 | 0.00029315 | -0.022535 | 65.0208 | -57.637 | -0.31128 | -58.0948 | 65.1947 | -57.9208 | -57.9987 | -57.8796 | -0.11444 | -58.1406 | 65.2039 | 65.0574 | -58.017 | -58.0948 | -0.045776 | -0.1236 | 0.036621 | 0.23804 | -0.21973 | -0.096131 | -0.13733 | -0.14191 | -0.21973 | 0.045776 | -0.004578 | -0.2655 | -0.045776 | -0.10071 | 123.0698 | 122.8958 | 57.5638 | -123.1567 | 123.0789 | 122.9324 | 57.7606 | -123.2529
773.6406 | 123.1705 | -57.8934 | 65.0848 | -0.10329 | 0.040211 | 0.082718 | 0.022158 | 0.048056 | 0.014367 | -0.023195 | -0.085129 | -0.01332 | 0.048783 | 0.034919 | 0.0088381 | -0.023603 | 65.0711 | -57.605 | -0.28381 | -58.0399 | 65.1993 | -57.8979 | -57.9941 | -57.8201 | -0.10529 | -58.1085 | 65.1627 | 65.0345 | -58.0078 | -58.0673 | -0.004577 | -0.10071 | 0.11444 | 0.28839 | -0.14648 | -0.045776 | -0.013733 | -0.11444 | -0.17395 | 0.07782 | 0.073243 | -0.21515 | -0.041199 | -0.050354 | 123.0927 | 122.9645 | 57.6096 | -123.0789 | 123.056 | 122.9279 | 57.7881 | -123.1522
774.6406 | 123.1476 | -57.8705 | 65.0711 | -0.16433 | 0.037007 | 0.072037 | 0.03818 | 0.039511 | 0.013299 | -0.012513 | -0.14616 | -0.024001 | 0.058397 | 0.0456 | 0.0067021 | -0.027876 | 65.0986 | -57.5958 | -0.28381 | -58.0627 | 65.1901 | -57.9254 | -58.0032 | -57.811 | -0.09613 | -58.1223 | 65.1855 | 65.0711 | -57.9529 | -58.0536 | -0.054932 | -0.13275 | 0.11902 | 0.27466 | -0.19226 | -0.059509 | 0.027466 | -0.082398 | -0.18311 | 0.11444 | 0.059509 | -0.25177 | -0.068664 | 0 | 123.0606 | 122.9691 | 57.5867 | -123.0743 | 123.056 | 122.9416 | 57.7744 | -123.1247
775.6406 | 123.1338 | -57.9163 | 65.0299 | -0.072774 | 0.02953 | 0.076309 | 0.031771 | 0.051261 | 0.0047541 | 0.0035077 | -0.06987 | -0.012251 | 0.058397 | 0.041327 | 0.0099061 | -0.019331 | 65.0208 | -57.7011 | -0.30212 | -58.1131 | 65.126 | -57.9758 | -58.049 | -57.8796 | -0.10071 | -58.1772 | 65.126 | 65.0162 | -58.0582 | -58.1131 | -0.059509 | -0.13275 | 0.096131 | 0.21515 | -0.19684 | -0.064087 | -0.009155 | -0.14191 | -0.19684 | 0.096131 | 0.036621 | -0.26093 | -0.064087 | -0.013733 | 123.0423 | 122.937 | 57.6141 | -123.0789 | 123.0423 | 122.9324 | 57.8156 | -123.143
776.6406 | 123.1659 | -57.8613 | 65.094 | -0.14907 | 0.027394 | 0.070968 | 0.028567 | 0.052329 | 0.010095 | -0.00076433 | 0.0522 | -0.01866 | 0.055192 | 0.044532 | 0.0056341 | -0.027876 | 65.062 | -57.605 | -0.27466 | -58.0582 | 65.1581 | -57.9254 | -57.9941 | -57.8339 | -0.10529 | -58.0948 | 65.1672 | 65.0574 | -58.0032 | -58.0673 | -0.064087 | -0.13275 | 0.064087 | 0.25635 | -0.19684 | -0.064087 | -0.032043 | -0.14191 | -0.20599 | 0.073242 | 0.027466 | -0.23346 | -0.027466 | -0.036621 | 123.0194 | 122.9233 | 57.5867 | -123.0881 | 123.0286 | 122.9187 | 57.756 | -123.1613
777.6406 | 123.1796 | -57.8888 | 65.0894 | 0.064555 | 0.025258 | 0.067764 | 0.029635 | 0.056601 | 0.019708 | -0.01465 | 0.0064239 | -0.017592 | 0.05626 | 0.058417 | -0.00077485 | -0.019331 | 65.0757 | -57.6416 | -0.29297 | -58.0582 | 65.1398 | -57.9391 | -58.0078 | -57.843 | -0.086975 | -58.1085 | 65.1535 | 65.0711 | -57.9987 | -58.0811 | -0.050354 | -0.11902 | 0.050354 | 0.24719 | -0.16937 | -0.050355 | -0.013733 | -0.10986 | -0.19226 | 0.064086 | 0.045776 | -0.21973 | -0.027466 | -0.018311 | 123.0286 | 122.9645 | 57.5958 | -123.0972 | 123.0423 | 122.9599 | 57.8018 | -123.1705
778.6406 | 123.1201 | -57.7332 | 65.2222 | 0.064555 | 0.041279 | 0.074173 | 0.011477 | 0.054465 | 0.010095 | -0.0071733 | 0.036941 | -0.0069114 | 0.048783 | 0.055213 | 0.0077701 | -0.03108 | 65.1398 | -57.5409 | -0.31128 | -58.017 | 65.2176 | -57.8613 | -57.9483 | -57.7377 | -0.059509 | -58.0032 | 65.2634 | 65.1489 | -57.8934 | -57.9391 | -0.12817 | -0.21515 | -0.004578 | 0.19226 | -0.28381 | -0.068665 | -0.082397 | -0.16022 | -0.20599 | 0.041199 | -0.004578 | -0.27008 | -0.064087 | -0.073242 | 122.9507 | 122.8729 | 57.4219 | -123.1705 | 122.9965 | 122.8821 | 57.6736 | -123.1613
779.6406 | 123.1201 | -58.017 | 64.9521 | -0.16433 | 0.051961 | 0.067764 | 0.033908 | 0.065146 | 0.0047541 | -0.0093093 | -0.17668 | -0.01332 | 0.061601 | 0.0456 | 0.0045661 | -0.021467 | 64.888 | -57.8522 | -0.32044 | -58.1955 | 65.0345 | -58.0719 | -58.1589 | -57.9849 | -0.10071 | -58.2687 | 65.0299 | 64.9384 | -58.1451 | -58.2184 | -0.054931 | -0.14191 | 0.082398 | 0.16479 | -0.17853 | -0.036621 | -0.064087 | -0.12817 | -0.20142 | 0.07782 | 0.032044 | -0.25177 | -0.050354 | -0.013733 | 123.0515 | 122.905 | 57.6965 | -123.111 | 123.0469 | 122.9553 | 57.9163 | -123.1705
780.6406 | 123.1796 | -58.0627 | 64.8514 | 0.53758 | 0.00069119 | 0.073105 | 0.027499 | 0.046988 | -0.016608 | -0.023195 | 0.73885 | -0.026137 | 0.055192 | 0.056281 | -0.013592 | -0.01399 | 64.8376 | -57.8979 | -0.32959 | -58.2642 | 64.8972 | -58.1314 | -58.1909 | -58.0261 | -0.14648 | -58.2779 | 64.9017 | 64.8193 | -58.2184 | -58.255 | -0.068665 | -0.12817 | 0.045777 | 0.1648 | -0.20142 | -0.073242 | -0.013733 | -0.15564 | -0.19226 | 0.050354 | 0.036621 | -0.21515 | -0.022888 | -0.032043 | 122.9599 | 122.9004 | 57.7332 | -123.0423 | 122.9645 | 122.8821 | 57.9163 | -123.1064
781.6406 | 123.1155 | -57.9437 | 65.0116 | -0.59157 | 0.059437 | 0.072037 | 0.046725 | 0.061942 | 0.0036861 | -0.016786 | 0.036941 | -0.01332 | 0.045579 | 0.057349 | 0.0099061 | -0.036421 | 65.062 | -57.7011 | -0.33875 | -58.1314 | 65.1398 | -57.962 | -58.0444 | -57.8842 | -0.15564 | -58.1863 | 65.1489 | 65.0711 | -58.049 | -58.1177 | -0.01831 | -0.10071 | 0.12817 | 0.24262 | -0.18768 | -0.086975 | 0.050354 | -0.10529 | -0.17395 | 0.13733 | 0.05951 | -0.24261 | -0.068664 | 0.059509 | 123.0835 | 123.0057 | 57.605 | -123.056 | 123.0927 | 123.0148 | 57.7881 | -123.1293
782.6406 | 123.1155 | -58.1039 | 64.9017 | 0.47654 | 0.039143 | 0.077377 | 0.022158 | 0.034171 | 0.014367 | -0.00076433 | 0.021682 | -0.016524 | 0.059465 | 0.047736 | 0.0067021 | -0.023603 | 64.8743 | -57.9391 | -0.33875 | -58.287 | 64.9704 | -58.1451 | -58.2138 | -58.0536 | -0.16479 | -58.3511 | 64.9658 | 64.8972 | -58.2184 | -58.2779 | -0.041199 | -0.10986 | 0.068665 | 0.16479 | -0.1831 | -0.073242 | -0.027465 | -0.11444 | -0.17395 | 0.064087 | 0.050354 | -0.24719 | -0.073242 | -0.004577 | 123.0743 | 122.9782 | 57.7652 | -123.1155 | 123.0698 | 123.0011 | 57.9391 | -123.1796
783.6406 | 123.1201 | -58.0948 | 64.8788 | 0.38499 | 0.02953 | 0.072037 | 0.030703 | 0.056601 | 0.010095 | -0.0050373 | 0.0522 | -0.017592 | 0.061601 | 0.052009 | 0.014179 | -0.017194 | 64.8605 | -57.9666 | -0.34332 | -58.2825 | 64.9292 | -58.136 | -58.2047 | -58.0582 | -0.17853 | -58.3649 | 64.975 | 64.8972 | -58.2092 | -58.2687 | -0.041198 | -0.10986 | 0.050354 | 0.12817 | -0.18768 | -0.07782 | -0.01831 | -0.11444 | -0.17395 | 0.096131 | 0.036621 | -0.27008 | -0.09613 | 0.018311 | 123.024 | 122.9553 | 57.7515 | -123.0835 | 123.0698 | 122.9919 | 57.9163 | -123.1476
784.6406 | 123.1247 | -58.0856 | 64.888 | 0.26292 | 0.070118 | 0.073105 | 0.03818 | 0.050193 | 0.013299 | -0.011445 | 0.11323 | -0.01866 | 0.064805 | 0.057349 | 0.0056341 | -0.016126 | 64.8834 | -57.9391 | -0.3479 | -58.2687 | 64.9567 | -58.1314 | -58.1818 | -58.0536 | -0.15564 | -58.3603 | 64.9933 | 64.9109 | -58.2138 | -58.2825 | -0.045777 | -0.096131 | 0.068665 | 0.14648 | -0.18311 | -0.086975 | -0.004577 | -0.12817 | -0.19684 | 0.10529 | 0.032043 | -0.27466 | -0.07782 | 0.022889 | 123.0423 | 122.9691 | 57.7377 | -123.0698 | 123.0789 | 122.9965 | 57.93 | -123.1705
785.6406 | 123.2071 | -58.0811 | 64.8285 | 0.55284 | 0.017781 | 0.068832 | 0.0050688 | 0.048056 | -0.019813 | -0.021058 | 3.8364 | -0.01866 | 0.040239 | 0.041327 | -0.00077485 | -0.017194 | 64.8422 | -57.9208 | -0.33875 | -58.2687 | 64.8788 | -58.1497 | -58.2092 | -58.0856 | -0.050354 | -58.2733 | 64.9338 | 64.8148 | -58.1955 | -58.2504 | -0.068664 | -0.12817 | 0.050354 | 0.16022 | -0.18768 | -0.059509 | 0.013733 | -0.11444 | -0.16937 | 0.10529 | -0.004577 | -0.19226 | -0.022888 | -0.013733 | 122.9599 | 122.9233 | 57.7423 | -123.0377 | 123.0148 | 122.8958 | 58.0307 | -123.0789
786.6406 | 123.1201 | -58.0765 | 64.8788 | -0.057515 | 0.061574 | 0.050674 | 0.031771 | 0.051261 | 0.011163 | -0.028535 | 0.021682 | -0.017592 | 0.057328 | 0.056281 | 0.014179 | -0.022535 | 64.8743 | -57.9575 | -0.32501 | -58.2687 | 64.9521 | -58.1451 | -58.1772 | -58.0353 | -0.16022 | -58.3054 | 64.9612 | 64.8697 | -58.1863 | -58.2458 | -0.068665 | -0.10071 | 0.073242 | 0.11902 | -0.19226 | -0.091553 | -0.004577 | -0.10986 | -0.16937 | 0.082398 | 0.041199 | -0.22888 | -0.059509 | -0.009155 | 123.0286 | 122.9507 | 57.7515 | -123.056 | 123.0377 | 122.9462 | 57.9163 | -123.1247
787.6406 | 123.1338 | -58.0856 | 64.8834 | 0.26292 | 0.038075 | 0.06456 | 0.02109 | 0.049125 | 0.012231 | -0.015718 | 0.29634 | -0.022933 | 0.059465 | 0.053077 | 0.010974 | -0.021467 | 64.8422 | -58.0032 | -0.39368 | -58.2962 | 64.9384 | -58.1268 | -58.2138 | -58.1039 | -0.24261 | -58.3923 | 64.9704 | 64.9109 | -58.223 | -58.2779 | -0.041199 | -0.12817 | 0.054931 | 0.082397 | -0.21057 | -0.082398 | -0.041199 | -0.13733 | -0.19226 | 0.086975 | -0.018311 | -0.3067 | -0.11444 | 0.027466 | 123.024 | 122.9279 | 57.692 | -123.0972 | 123.056 | 122.9965 | 57.843 | -123.1613
788.6406 | 123.1064 | -58.1085 | 64.9063 | 0.24766 | 0.04662 | 0.062424 | 0.031771 | 0.049125 | 0.0047541 | -0.017854 | 0.17427 | -0.012251 | 0.05626 | 0.043464 | 0.0034971 | -0.017194 | 64.8331 | -57.9987 | -0.39368 | -58.3054 | 64.9429 | -58.1406 | -58.223 | -58.0994 | -0.23804 | -58.3878 | 64.9658 | 64.9338 | -58.223 | -58.3008 | -0.032043 | -0.11444 | 0.036621 | 0.10986 | -0.19684 | -0.082398 | -0.073242 | -0.11444 | -0.19226 | 0.059509 | 0.009156 | -0.27923 | -0.086975 | 0.027466 | 123.0515 | 122.9416 | 57.7148 | -123.1293 | 123.0743 | 123.0423 | 57.8705 | -123.2071
789.6406 | 123.0927 | -58.1131 | 64.8834 | 0.18663 | 0.044484 | 0.077377 | 0.037112 | 0.041648 | 0.013299 | -0.01999 | 0.25056 | -0.01866 | 0.074418 | 0.061622 | 0.0099061 | -0.019331 | 64.8331 | -58.017 | -0.38452 | -58.3099 | 64.9338 | -58.1497 | -58.2138 | -58.1268 | -0.2243 | -58.3969 | 64.9429 | 64.92 | -58.2092 | -58.3054 | -0.036621 | -0.10071 | 0.050354 | 0.09613 | -0.19684 | -0.096131 | -0.050354 | -0.096131 | -0.19226 | 0.059509 | -0.013733 | -0.28381 | -0.091553 | 0.036621 | 123.0469 | 122.9462 | 57.7286 | -123.0972 | 123.056 | 123.0331 | 57.8888 | -123.1888
790.6406 | 123.2254 | -58.0582 | 64.8605 | 0.034038 | 0.0071002 | -0.22063 | 0.014682 | 0.036307 | -0.044379 | -0.031739 | 0.32686 | -0.033614 | 0.038102 | 0.052009 | -0.011456 | -0.00865 | 64.8239 | -57.9208 | -0.33417 | -58.2367 | 64.9292 | -58.1085 | -58.1909 | -58.0032 | -0.11444 | -58.2458 | 64.9292 | 64.8926 | -58.1726 | -58.2367 | -0.050354 | -0.13275 | 0.068664 | 0.13733 | -0.17853 | -0.045776 | -0.036621 | -0.11444 | -0.17853 | 0.068664 | 0.054932 | -0.18768 | -0.009156 | 0.032043 | 122.9874 | 122.8821 | 57.724 | -123.0515 | 122.9874 | 122.9507 | 57.9437 | -123.0972
791.6406 | 123.0972 | -58.0765 | 64.8834 | 0.20188 | 0.044484 | 0.067764 | 0.048861 | 0.052329 | 0.017572 | -0.022126 | 0.11323 | -0.026137 | 0.061601 | 0.040259 | 0.010974 | -0.023603 | 64.8651 | -57.9758 | -0.40741 | -58.2962 | 64.9704 | -58.1406 | -58.1909 | -58.0673 | -0.23346 | -58.3603 | 64.9658 | 64.9109 | -58.2458 | -58.255 | -0.064087 | -0.11444 | 0.086975 | 0.10071 | -0.21973 | -0.10529 | -0.018311 | -0.16937 | -0.17853 | 0.082397 | 0.009155 | -0.28381 | -0.10529 | 0.027466 | 123.0469 | 122.9416 | 57.6691 | -123.0743 | 123.0423 | 122.9874 | 57.843 | -123.1384
792.6406 | 123.1476 | -58.0536 | 64.9109 | 0.064555 | 0.042347 | 0.078445 | 0.040316 | 0.050193 | 0.011163 | -0.0061053 | -0.0088351 | -0.025069 | 0.075486 | 0.054145 | 0.01311 | -0.026808 | 64.9155 | -57.9208 | -0.33417 | -58.2596 | 64.9704 | -58.1223 | -58.1909 | -58.0627 | -0.37994 | -58.3054 | 64.9567 | 64.888 | -58.2001 | -58.2504 | -0.068664 | -0.13733 | 0.059509 | 0.13275 | -0.20599 | -0.068665 | 0.004577 | -0.14648 | -0.19684 | 0.045776 | -0.009155 | -0.25177 | -0.054932 | -0.022889 | 123.024 | 122.9691 | 57.7194 | -123.1018 | 123.0103 | 122.9416 | 57.6736 | -123.1613
793.6406 | 123.1338 | -58.0719 | 64.8926 | 0.049296 | 0.054097 | 0.061355 | 0.027499 | 0.050193 | 0.010095 | -0.0071733 | 0.0522 | -0.0079794 | 0.063737 | 0.058417 | 0.0077701 | -0.024671 | 64.8926 | -57.9117 | -0.34332 | -58.2458 | 64.9887 | -58.1131 | -58.1726 | -58.0261 | -0.15564 | -58.3145 | 64.975 | 64.9155 | -58.2001 | -58.2504 | -0.041199 | -0.10071 | 0.09613 | 0.16022 | -0.17395 | -0.073243 | 0 | -0.12817 | -0.17853 | 0.082398 | 0.045776 | -0.24262 | -0.064087 | 0.022888 | 123.0606 | 122.9645 | 57.7286 | -123.0652 | 123.0469 | 122.9874 | 57.9163 | -123.143
794.6406 | 123.0789 | -58.0994 | 64.9063 | 0.53758 | 0.04662 | 0.057083 | 0.025363 | 0.057669 | -0.0016549 | -0.015718 | 0.40315 | -0.016524 | 0.051988 | 0.048804 | 0.0024291 | -0.016126 | 64.7964 | -58.0215 | -0.47607 | -58.3054 | 64.9841 | -58.1314 | -58.2047 | -58.0811 | -0.31128 | -58.4564 | 64.9429 | 64.8651 | -58.2413 | -58.3145 | -0.032044 | -0.10529 | 0.07782 | 0.07782 | -0.20599 | -0.10071 | -0.10986 | -0.14191 | -0.21515 | 0.036621 | 0.01831 | -0.35706 | -0.14191 | -0.041199 | 123.0835 | 122.8958 | 57.6233 | -123.111 | 123.0423 | 122.9645 | 57.7881 | -123.2208
795.6406 | 123.1796 | -58.049 | 64.8834 | 0.41551 | 0.0028272 | 0.084854 | 0.024295 | 0.037375 | -0.03797 | -0.03708 | 0.52522 | -0.031478 | 0.048783 | 0.037055 | 0.00029315 | -0.015058 | 64.8376 | -57.9254 | -0.39825 | -58.2687 | 64.9246 | -58.0994 | -58.1543 | -58.0261 | -0.21973 | -58.287 | 64.9246 | 64.8972 | -58.1772 | -58.2367 | -0.050354 | -0.10529 | 0.041199 | 0.1236 | -0.21973 | -0.11444 | -0.045777 | -0.12817 | -0.18768 | 0.041199 | 0.022888 | -0.23804 | -0.050354 | 0.013733 | 122.9736 | 122.8867 | 57.6508 | -123.0377 | 122.9736 | 122.9462 | 57.8293 | -123.1201
796.6406 | 123.0835 | -58.0765 | 64.888 | 0.15611 | 0.027394 | 0.065628 | 0.039248 | 0.037375 | 0.013299 | -0.016786 | 0.17427 | -0.011183 | 0.048783 | 0.052009 | 0.014179 | -0.028944 | 64.8743 | -57.9803 | -0.41657 | -58.2687 | 64.9658 | -58.1177 | -58.1543 | -58.0673 | -0.2655 | -58.3557 | 65.0024 | 64.9063 | -58.2001 | -58.2504 | -0.041199 | -0.07782 | 0.07782 | 0.09613 | -0.19226 | -0.11444 | -0.013732 | -0.1236 | -0.17395 | 0.11444 | 0.009155 | -0.27924 | -0.10529 | 0.018311 | 123.0423 | 122.9507 | 57.6599 | -123.0423 | 123.0789 | 122.9828 | 57.811 | -123.1384
797.6406 | 123.1155 | -58.0811 | 64.9063 | 0.26292 | 0.040211 | 0.079513 | 0.014682 | 0.04592 | 0.0068901 | -0.015718 | 0.28108 | -0.022933 | 0.064805 | 0.049872 | 0.0045661 | -0.024671 | 64.8834 | -57.9575 | -0.40741 | -58.2733 | 64.9887 | -58.1085 | -58.1726 | -58.0582 | -0.27008 | -58.374 | 64.9933 | 64.9155 | -58.2047 | -58.2596 | -0.027466 | -0.091552 | 0.082397 | 0.1236 | -0.19226 | -0.10071 | -0.022888 | -0.1236 | -0.17853 | 0.086975 | 0.022888 | -0.29297 | -0.11444 | 0.009155 | 123.0698 | 122.9645 | 57.6736 | -123.0789 | 123.0743 | 122.9965 | 57.811 | -123.1659
798.6406 | 123.1338 | -58.0536 | 64.9155 | 0.18663 | 0.053029 | 0.068832 | 0.027499 | 0.04592 | 0.0090271 | -0.010377 | 0.20479 | -0.021865 | 0.053056 | 0.047736 | 0.010974 | -0.025739 | 64.8926 | -57.9346 | -0.39368 | -58.2733 | 64.9979 | -58.1085 | -58.1726 | -58.0536 | -0.25177 | -58.3328 | 65.0024 | 64.92 | -58.2001 | -58.2458 | -0.054932 | -0.11902 | 0.082398 | 0.11902 | -0.21973 | -0.10071 | -0.022888 | -0.14648 | -0.19226 | 0.086975 | 0 | -0.27924 | -0.086975 | 0.004578 | 123.0515 | 122.9462 | 57.6599 | -123.0881 | 123.056 | 122.9736 | 57.8018 | -123.1613
799.6406 | 123.1613 | -58.0215 | 64.9704 | 0.049296 | 0.050892 | 0.065628 | 0.026431 | 0.060874 | -0.0059269 | -0.016786 | 0.17427 | -0.010115 | 0.078691 | 0.044532 | 0.0099061 | -0.033216 | 64.9338 | -57.8934 | -0.35248 | -58.2367 | 65.0253 | -58.049 | -58.1406 | -58.0673 | -0.1236 | -58.2504 | 65.007 | 64.9612 | -58.1635 | -58.2184 | -0.027466 | -0.11902 | 0.054932 | 0.12817 | -0.21515 | -0.09613 | -0.036621 | -0.14191 | -0.19684 | 0.036621 | -0.045777 | -0.22888 | -0.032043 | -0.009155 | 123.0469 | 122.9553 | 57.6691 | -123.111 | 123.0286 | 122.9828 | 57.8979 | -123.1888
800.6406 | 123.1888 | -58.017 | 64.9063 | 0.3087 | -0.00037681 | 0.074173 | 0.022158 | 0.048056 | -0.040107 | -0.024263 | 0.47945 | -0.032546 | 0.035966 | 0.0456 | -0.010388 | -0.011854 | 64.856 | -57.9025 | -0.39368 | -58.2275 | 64.9704 | -58.0811 | -58.1177 | -58.0124 | -0.21973 | -58.2596 | 64.9704 | 64.9246 | -58.1497 | -58.2047 | -0.064087 | -0.10071 | 0.064087 | 0.11444 | -0.21057 | -0.10986 | -0.050354 | -0.13275 | -0.18768 | 0.064087 | 0.004578 | -0.24262 | -0.054932 | 0.018311 | 122.9874 | 122.8729 | 57.6233 | -123.024 | 122.9874 | 122.9416 | 57.7972 | -123.111
801.6406 | 123.1064 | -58.0765 | 64.9292 | 0.27818 | 0.043416 | 0.065628 | 0.029635 | 0.057669 | 0.011163 | -0.012513 | 0.20479 | -0.014388 | 0.063737 | 0.032783 | 0.012042 | -0.025739 | 64.8651 | -57.9575 | -0.44861 | -58.2687 | 65.007 | -58.0994 | -58.168 | -58.049 | -0.37079 | -58.3969 | 65.0024 | 64.9521 | -58.1726 | -58.2504 | -0.022888 | -0.091553 | 0.07782 | 0.11902 | -0.19226 | -0.10071 | -0.064087 | -0.09613 | -0.17395 | 0.073242 | 0.027466 | -0.32044 | -0.14648 | 0.022888 | 123.0835 | 122.9416 | 57.6279 | -123.0972 | 123.0789 | 123.0286 | 57.7057 | -123.1796
802.6406 | 123.111 | -58.0582 | 64.9475 | 0.3087 | 0.057301 | 0.06456 | 0.03284 | 0.057669 | 0.0058221 | -0.018922 | 0.17427 | -0.014388 | 0.064805 | 0.047736 | 0.0045661 | -0.015058 | 64.8834 | -57.9529 | -0.45319 | -58.2504 | 65.0116 | -58.0994 | -58.1726 | -58.0627 | -0.2655 | -58.3511 | 65.0208 | 64.9658 | -58.168 | -58.2184 | -0.041198 | -0.11444 | 0.064087 | 0.10529 | -0.19226 | -0.07782 | -0.064087 | -0.10986 | -0.16022 | 0.073242 | -0.004577 | -0.29297 | -0.13275 | 0.01831 | 123.0698 | 122.9416 | 57.605 | -123.1201 | 123.0789 | 123.024 | 57.7927 | -123.1659
803.6406 | 123.0927 | -58.0536 | 64.9521 | 0.44602 | 0.026326 | 0.065628 | 0.025363 | 0.050193 | 0.0047541 | -0.010377 | 0.46419 | -0.016524 | 0.06801 | 0.044532 | 0.0034971 | -0.022535 | 64.8422 | -58.0032 | -0.49439 | -58.2962 | 65.0116 | -58.0856 | -58.1909 | -58.0444 | -0.3479 | -58.3511 | 65.0299 | 64.9521 | -58.1909 | -58.2275 | -0.032043 | -0.13733 | 0.05951 | 0.050354 | -0.24262 | -0.10529 | -0.10986 | -0.13733 | -0.17395 | 0.07782 | 0.009155 | -0.29755 | -0.1236 | 0 | 123.0652 | 122.8958 | 57.5592 | -123.143 | 123.0835 | 123.0057 | 57.7057 | -123.1796
804.6875 | 123.1247 | -58.0215 | 64.9933 | -0.27114 | 0.02419 | 0.074173 | 0.036044 | 0.046988 | -0.017676 | -0.0082413 | -0.2072 | -0.017592 | 0.061601 | 0.044532 | -0.0029109 | -0.028944 | 64.9017 | -57.8751 | -0.38452 | -58.2092 | 65.062 | -58.0399 | -58.1268 | -57.9575 | -0.27924 | -58.3008 | 65.0803 | 65.0253 | -58.136 | -58.1635 | -0.018311 | -0.10529 | 0.068665 | 0.14648 | -0.18768 | -0.082398 | -0.091553 | -0.11444 | -0.14191 | 0.086975 | 0.064087 | -0.27924 | -0.13733 | 0.032044 | 123.0835 | 122.9233 | 57.637 | -123.1201 | 123.1018 | 123.0469 | 57.7423 | -123.1567
805.6562 | 123.1384 | -58.0032 | 64.9612 | -0.22536 | 0.0060322 | 0.08165 | 0.024295 | 0.052329 | -0.016608 | -0.017854 | -0.06987 | -0.021865 | 0.049852 | 0.035987 | 0.0045661 | -0.021467 | 64.9292 | -57.7927 | -0.32044 | -58.1543 | 64.9979 | -58.0444 | -58.0902 | -57.9529 | -0.12817 | -58.2138 | 65.0253 | 64.9796 | -58.136 | -58.1772 | -0.041199 | -0.086975 | 0.036621 | 0.21057 | -0.15106 | -0.064087 | -0.032044 | -0.13275 | -0.17395 | 0.064087 | 0.050354 | -0.21057 | -0.036621 | 0.01831 | 123.0011 | 122.9324 | 57.6828 | -123.0515 | 123.0286 | 122.9828 | 57.8751 | -123.1384
806.6406 | 123.1476 | -58.0078 | 64.9612 | 0.00352 | 0.051961 | 0.077377 | 0.031771 | 0.049125 | 0.012231 | -0.0061053 | 3.0277 | -0.01866 | 0.064805 | 0.035987 | 0.01311 | -0.024671 | 64.9704 | -57.8293 | -0.37079 | -58.2138 | 65.0391 | -58.0673 | -58.1131 | -57.9529 | -0.21515 | -58.2779 | 65.0574 | 64.9612 | -58.168 | -58.2321 | -0.05951 | -0.10529 | 0.077819 | 0.17853 | -0.20599 | -0.10071 | 0.009155 | -0.16022 | -0.22431 | 0.09613 | 0.054931 | -0.27008 | -0.045776 | 0 | 123.0469 | 122.9782 | 57.637 | -123.0743 | 123.0652 | 122.9691 | 57.7927 | -123.1934
807.6406 | 123.1201 | -58.0215 | 64.9704 | 0.15611 | 0.050892 | 0.075241 | 0.026431 | 0.046988 | 0.014367 | -0.01465 | 0.25056 | -0.017592 | 0.05626 | 0.052009 | 0.015247 | -0.023603 | 64.9429 | -57.8842 | -0.44861 | -58.2047 | 65.0391 | -58.0261 | -58.1268 | -58.0215 | -0.28381 | -58.2962 | 65.0253 | 64.9612 | -58.1451 | -58.223 | -0.004578 | -0.10529 | 0.068664 | 0.13733 | -0.18311 | -0.07782 | -0.027466 | -0.1236 | -0.20142 | 0.054932 | 0 | -0.27466 | -0.073243 | -0.009155 | 123.0606 | 122.9645 | 57.5729 | -123.0972 | 123.0469 | 122.9828 | 57.7377 | -123.1934
808.6406 | 123.0743 | -58.0215 | 64.9612 | 0.35447 | 0.040211 | 0.067764 | 0.033908 | 0.042716 | 0.012231 | -0.013582 | 0.37263 | -0.015456 | 0.058397 | 0.054145 | 0.0077701 | -0.024671 | 64.888 | -57.9163 | -0.52185 | -58.2275 | 65.062 | -58.0399 | -58.1314 | -58.0215 | -0.34332 | -58.3282 | 65.0528 | 65.0116 | -58.1543 | -58.1863 | -0.018311 | -0.10986 | 0.10071 | 0.10529 | -0.20599 | -0.09613 | -0.073243 | -0.13275 | -0.16479 | 0.091552 | 0 | -0.3067 | -0.14191 | 0.050354 | 123.0835 | 122.9095 | 57.4997 | -123.0927 | 123.0743 | 123.0331 | 57.6782 | -123.1476
809.6406 | 123.143 | -58.0124 | 64.975 | 0.20188 | 0.035939 | 0.063492 | 0.029635 | 0.051261 | 0.0058221 | -0.016786 | 0.35738 | -0.019728 | 0.069078 | 0.046668 | 0.0077701 | -0.017194 | 64.9063 | -57.9483 | -0.49439 | -58.2596 | 65.0528 | -58.0582 | -58.1451 | -58.0399 | -0.3479 | -58.3282 | 65.062 | 64.9933 | -58.1406 | -58.1909 | -0.045777 | -0.13275 | 0.077819 | 0.064087 | -0.24719 | -0.11444 | -0.068665 | -0.12817 | -0.17853 | 0.086975 | -0.027466 | -0.31586 | -0.13733 | 0.01831 | 123.0652 | 122.9187 | 57.518 | -123.1201 | 123.0743 | 123.0057 | 57.6645 | -123.1659
810.6406 | 123.2025 | -57.9437 | 64.9796 | 0.44602 | 0.027394 | 0.076309 | 0.031771 | 0.046988 | -0.03263 | -0.025331 | 0.63203 | -0.027205 | 0.061601 | 0.039191 | -0.013592 | -0.005445 | 64.9338 | -57.7744 | -0.40741 | -58.168 | 65.0208 | -57.9941 | -58.0399 | -57.9254 | -0.25177 | -58.1909 | 65.0208 | 65.0024 | -58.0719 | -58.1451 | -0.050354 | -0.09613 | 0.041199 | 0.16937 | -0.2243 | -0.12817 | -0.045776 | -0.12817 | -0.20142 | 0.041199 | 0.018311 | -0.24719 | -0.045776 | 0.022888 | 122.9645 | 122.8775 | 57.5363 | -123.0194 | 122.9645 | 122.9462 | 57.692 | -123.1247
811.6406 | 123.0881 | -58.0032 | 64.9841 | 0.26292 | 0.053029 | 0.074173 | 0.029635 | 0.046988 | 0.015435 | -0.016786 | 0.35738 | -0.016524 | 0.060533 | 0.047736 | 0.0088381 | -0.030012 | 64.888 | -57.9117 | -0.52643 | -58.2321 | 65.0574 | -58.0627 | -58.1223 | -57.9712 | -0.37994 | -58.3099 | 65.0574 | 65.0162 | -58.1085 | -58.168 | -0.059509 | -0.11902 | 0.073242 | 0.091553 | -0.22888 | -0.10986 | -0.096131 | -0.10529 | -0.1648 | 0.073242 | 0.032044 | -0.3067 | -0.14191 | 0.032043 | 123.0606 | 122.8912 | 57.4768 | -123.1064 | 123.0606 | 123.0194 | 57.6233 | -123.1522
812.6406 | 123.1064 | -57.9712 | 65.0116 | 0.26292 | 0.053029 | 0.072037 | 0.034976 | 0.043784 | 0.013299 | -0.0093093 | 0.18953 | -0.020796 | 0.060533 | 0.041327 | 0.0034971 | -0.038557 | 64.9658 | -57.8247 | -0.44861 | -58.1863 | 65.0345 | -58.0399 | -58.0902 | -57.9529 | -0.31586 | -58.2687 | 65.0986 | 65.0482 | -58.1085 | -58.1497 | -0.068665 | -0.11902 | 0.022888 | 0.14648 | -0.21515 | -0.09613 | -0.045777 | -0.13733 | -0.17853 | 0.086975 | 0.01831 | -0.29755 | -0.11902 | 0.036621 | 123.0057 | 122.937 | 57.5226 | -123.1018 | 123.0698 | 123.0194 | 57.6553 | -123.1613
813.6406 | 123.1293 | -57.962 | 64.9887 | 0.32395 | 0.043416 | 0.079513 | 0.029635 | 0.056601 | 0.0047541 | -0.010377 | 0.067459 | -0.012251 | 0.070146 | 0.057349 | 0.0056341 | -0.021467 | 64.9704 | -57.8201 | -0.45776 | -58.1818 | 65.0757 | -58.017 | -58.0673 | -57.9483 | -0.31586 | -58.2504 | 65.1031 | 65.0436 | -58.1085 | -58.1543 | -0.054932 | -0.10529 | 0.086976 | 0.14191 | -0.21973 | -0.11444 | -0.01831 | -0.14649 | -0.19226 | 0.11444 | 0.013733 | -0.28839 | -0.09613 | 0.054932 | 123.0377 | 122.9324 | 57.5043 | -123.056 | 123.0652 | 123.0057 | 57.6462 | -123.143
814.6406 | 123.111 | -57.9758 | 64.9933 | 0.4918 | 0.027394 | 0.0699 | 0.026431 | 0.039511 | 0.0058221 | -0.01999 | -0.23772 | -0.021865 | 0.058397 | 0.057349 | 0.0067021 | -0.017194 | 64.8285 | -57.6828 | -0.4715 | -58.2275 | 65.0894 | -58.0353 | -58.0948 | -57.9666 | -0.36163 | -58.2504 | 65.0848 | 65.007 | -58.1039 | -58.1955 | -0.059509 | -0.11902 | 0.096131 | 0.29297 | -0.25177 | -0.13275 | -0.16479 | -0.12817 | -0.21973 | 0.091553 | 0.009155 | -0.27466 | -0.054931 | 0.013733 | 123.0652 | 122.8043 | 57.5043 | -123.0881 | 123.0606 | 122.9828 | 57.6141 | -123.1888
815.6406 | 123.1064 | -57.962 | 65.0208 | 0.47654 | 0.026326 | 0.06456 | 0.036044 | 0.04058 | 0.0090271 | -0.032808 | 0.28108 | -0.014388 | 0.05626 | 0.055213 | -0.0039789 | -0.026808 | 65.1352 | -57.8201 | -0.55389 | -58.1497 | 65.0986 | -58.0032 | -58.0948 | -57.9483 | -0.35248 | -58.2504 | 65.1169 | 65.0345 | -58.0856 | -58.136 | -0.041199 | -0.13275 | 0.07782 | 0.14191 | -0.18768 | -0.054931 | 0.11444 | -0.1236 | -0.17395 | 0.09613 | 0.013733 | -0.28839 | -0.11444 | 0.013733 | 123.0606 | 123.0972 | 57.4081 | -123.1155 | 123.0789 | 122.9965 | 57.6096 | -123.1567
816.6406 | 123.1338 | -57.9575 | 65.0208 | 0.46128 | 0.033803 | 0.065628 | 0.012545 | 0.039511 | 0.0047541 | -0.034944 | 0.76936 | -0.016524 | 0.075486 | 0.054145 | 0.0045661 | -0.011854 | 65.2084 | -57.9117 | -0.59967 | -58.1131 | 65.1169 | -57.9712 | -58.0536 | -57.93 | -0.34332 | -58.2367 | 65.1031 | 65.0345 | -58.0902 | -58.1314 | -0.013733 | -0.096131 | 0.09613 | 0.045776 | -0.15564 | -0.059509 | 0.18768 | -0.13275 | -0.17395 | 0.082397 | 0.027465 | -0.27924 | -0.10529 | 0.013733 | 123.0743 | 123.1659 | 57.3578 | -123.0743 | 123.0606 | 122.9919 | 57.6141 | -123.1522
817.6406 | 123.1155 | -57.9437 | 64.9796 | 0.50706 | 0.034871 | 0.075241 | 0.0072048 | 0.060874 | -0.020881 | -0.023195 | 0.4947 | -0.015456 | 0.072282 | 0.046668 | 0.0088381 | -0.012922 | 64.8834 | -57.7652 | -0.44861 | -58.1635 | 65.0894 | -57.9941 | -58.0673 | -57.9346 | -0.39368 | -58.2321 | 65.0986 | 65.0436 | -58.0994 | -58.1543 | -0.050354 | -0.1236 | 0.10986 | 0.17853 | -0.21973 | -0.09613 | -0.09613 | -0.15564 | -0.21057 | 0.11902 | 0.009156 | -0.28839 | -0.07782 | 0.064087 | 123.0331 | 122.8271 | 57.4951 | -123.0469 | 123.0423 | 122.9874 | 57.55 | -123.1338
818.6406 | 123.1201 | -57.9666 | 64.9841 | 0.50706 | 0.048756 | 0.062424 | 0.040316 | 0.054465 | 0.013299 | -0.018922 | 0.28108 | -0.015456 | 0.060533 | 0.056281 | -0.0039789 | -0.010786 | 64.8697 | -57.7972 | -0.50812 | -58.2275 | 65.0848 | -58.017 | -58.0948 | -57.962 | -0.37537 | -58.255 | 65.0757 | 65.0162 | -58.1131 | -58.1589 | -0.050354 | -0.12817 | 0.10071 | 0.16937 | -0.26093 | -0.13275 | -0.11444 | -0.14648 | -0.19226 | 0.091553 | 0.004578 | -0.28839 | -0.09613 | 0.032043 | 123.0515 | 122.8363 | 57.4585 | -123.0789 | 123.0423 | 122.9828 | 57.5912 | -123.143
819.6406 | 123.0927 | -57.9758 | 65.0024 | 0.38499 | 0.039143 | 0.068832 | 0.03284 | 0.053397 | 0.00048206 | -0.01465 | 0.47945 | -0.016524 | 0.060533 | 0.053077 | 0.0099061 | -0.021467 | 64.9246 | -57.8979 | -0.55389 | -58.2047 | 65.0894 | -58.0124 | -58.0856 | -57.9575 | -0.37994 | -58.2413 | 65.0986 | 65.0345 | -58.0856 | -58.1726 | -0.036621 | -0.10986 | 0.086976 | 0.07782 | -0.22888 | -0.11902 | -0.077819 | -0.10986 | -0.19684 | 0.096131 | 0.018311 | -0.2655 | -0.068665 | 0.032044 | 123.0652 | 122.9004 | 57.4219 | -123.0881 | 123.0743 | 123.0103 | 57.5958 | -123.175
820.6406 | 123.1155 | -57.9666 | 65.0024 | 0.47654 | 0.034871 | 0.062424 | 0.027499 | 0.037375 | 0.0058221 | -0.015718 | 0.44893 | -0.014388 | 0.041307 | 0.055213 | -0.0018429 | -0.020399 | 64.92 | -57.8796 | -0.55847 | -58.2092 | 65.0803 | -58.0078 | -58.0811 | -57.962 | -0.40283 | -58.2504 | 65.1031 | 65.0528 | -58.0856 | -58.1726 | -0.041198 | -0.11444 | 0.07782 | 0.086975 | -0.24262 | -0.12817 | -0.082397 | -0.11902 | -0.20599 | 0.10071 | 0.004578 | -0.28381 | -0.07782 | 0.050354 | 123.0469 | 122.8867 | 57.4081 | -123.0835 | 123.0698 | 123.0194 | 57.5638 | -123.175
821.6406 | 123.2941 | -57.9666 | 64.9521 | 0.69017 | 0.027394 | 0.073105 | 0.025363 | 0.051261 | -0.014472 | -0.010377 | 0.63203 | -0.027205 | 0.053056 | 0.031714 | -0.0050469 | -0.019331 | 64.9887 | -57.7515 | -0.45319 | -58.136 | 64.9979 | -57.9895 | -58.0536 | -57.8567 | -0.27466 | -58.1497 | 65.0208 | 64.9612 | -58.0856 | -58.1543 | -0.022888 | -0.086975 | 0.045777 | 0.21515 | -0.16937 | -0.082397 | 0.036621 | -0.11902 | -0.18768 | 0.068665 | 0.10986 | -0.1831 | 0.004578 | 0.009156 | 122.9645 | 122.9553 | 57.5134 | -123.0057 | 122.9874 | 122.9279 | 57.692 | -123.1064
822.6406 | 123.1888 | -57.9163 | 64.9612 | 0.61387 | 0.028462 | 0.075241 | 0.040316 | 0.042716 | 0.0068901 | -0.01999 | 0.55574 | -0.020796 | 0.057328 | 0.052009 | 0.0013611 | -0.018263 | 64.9933 | -57.7835 | -0.49439 | -58.1497 | 65.0528 | -57.9758 | -58.0582 | -57.8613 | -0.32501 | -58.1772 | 65.062 | 64.9979 | -58.0811 | -58.1223 | -0.059509 | -0.14191 | 0.091552 | 0.13275 | -0.23346 | -0.091552 | 0.032043 | -0.16479 | -0.20599 | 0.10071 | 0.054932 | -0.26093 | -0.054932 | 0.036621 | 122.9691 | 122.9095 | 57.4219 | -123.0194 | 122.9782 | 122.9141 | 57.5912 | -123.0835
823.6406 | 123.2162 | -57.9208 | 65.0024 | 0.61387 | 0.027394 | 0.063492 | 0.027499 | 0.04592 | 0.00048206 | -0.012513 | 0.58626 | -0.017592 | 0.058397 | 0.054145 | 0.0077701 | -0.018263 | 65.0116 | -57.7698 | -0.48981 | -58.1406 | 65.0757 | -57.962 | -58.0078 | -57.8201 | -0.37079 | -58.1818 | 65.0803 | 65.0299 | -58.0307 | -58.0811 | -0.041199 | -0.086975 | 0.073243 | 0.15106 | -0.21973 | -0.13275 | 0.009156 | -0.10986 | -0.16022 | 0.07782 | 0.10071 | -0.26093 | -0.10071 | 0.027466 | 122.9965 | 122.9324 | 57.431 | -123.0103 | 123.0011 | 122.9507 | 57.55 | -123.0835
824.6406 | 123.2391 | -57.8934 | 64.9796 | 0.59861 | 0.0092362 | 0.057083 | 0.026431 | 0.057669 | 0.00048206 | -0.01465 | 0.571 | -0.014388 | 0.059465 | 0.039191 | 0.012042 | -0.026808 | 65.007 | -57.7789 | -0.52643 | -58.1131 | 65.1031 | -57.9758 | -58.0399 | -57.843 | -0.31586 | -58.1863 | 65.0894 | 65.0208 | -58.049 | -58.1085 | -0.082397 | -0.14648 | 0.1236 | 0.11444 | -0.21973 | -0.073242 | 0.027466 | -0.15564 | -0.21515 | 0.10986 | 0.050354 | -0.29297 | -0.077819 | 0.041199 | 122.9965 | 122.9004 | 57.3669 | -123.0194 | 122.9828 | 122.9141 | 57.5775 | -123.0881
825.6406 | 123.2071 | -57.8751 | 65.007 | 0.55284 | 0.035939 | 0.066696 | 0.042453 | 0.046988 | 0.0090271 | -0.024263 | 0.52522 | -0.021865 | 0.057328 | 0.050941 | 0.012042 | -0.024671 | 65.0391 | -57.724 | -0.52185 | -58.0948 | 65.126 | -57.9254 | -57.9895 | -57.8018 | -0.3067 | -58.1223 | 65.1123 | 65.0528 | -57.9895 | -58.0856 | -0.050354 | -0.11444 | 0.11902 | 0.15106 | -0.21973 | -0.10529 | 0.032043 | -0.11444 | -0.21057 | 0.10529 | 0.073242 | -0.24719 | -0.036621 | 0.045776 | 123.0011 | 122.9141 | 57.3532 | -122.9965 | 122.9874 | 122.9279 | 57.5684 | -123.0927
826.6406 | 123.1201 | -57.9117 | 65.0391 | 1.4684 | 0.031666 | 0.076309 | 0.020022 | 0.039511 | -0.0059269 | -0.018922 | 0.46419 | -0.01332 | 0.063737 | 0.055213 | 0.0077701 | -0.024671 | 65.0208 | -57.756 | -0.52643 | -58.1268 | 65.1672 | -57.9575 | -57.9987 | -57.8751 | -0.41199 | -58.1772 | 65.1398 | 65.0848 | -58.0215 | -58.0948 | -0.045776 | -0.086975 | 0.12817 | 0.15564 | -0.21515 | -0.12817 | -0.01831 | -0.10986 | -0.18311 | 0.10071 | 0.036621 | -0.2655 | -0.082397 | 0.045777 | 123.0789 | 122.9324 | 57.3853 | -123.0377 | 123.0515 | 122.9965 | 57.4997 | -123.1338
827.6406 | 123.2071 | -57.8705 | 65.0162 | 0.56809 | 0.032734 | 0.061355 | 0.026431 | 0.058738 | -0.014472 | -0.0071733 | 0.4947 | -0.01332 | 0.05626 | 0.046668 | 0.00029315 | -0.016126 | 65.0528 | -57.7103 | -0.51727 | -58.0856 | 65.1306 | -57.9163 | -57.9895 | -57.7789 | -0.3479 | -58.1314 | 65.1077 | 65.062 | -57.9758 | -58.0627 | -0.045777 | -0.11902 | 0.11444 | 0.16022 | -0.21515 | -0.09613 | 0.036621 | -0.10529 | -0.19226 | 0.091553 | 0.091552 | -0.26093 | -0.068665 | 0.045777 | 123.0011 | 122.9233 | 57.3532 | -123.0057 | 122.9782 | 122.9324 | 57.5226 | -123.0789
828.6406 | 123.1842 | -57.8522 | 65.0391 | 0.59861 | 0.033803 | 0.062424 | 0.013613 | 0.04058 | -0.00058594 | -0.017854 | 0.571 | -0.020796 | 0.043443 | 0.053077 | 0.01311 | -0.017194 | 65.1169 | -57.6187 | -0.47607 | -58.017 | 65.126 | -57.8796 | -57.9391 | -57.7377 | -0.3067 | -58.0307 | 65.126 | 65.1123 | -57.9666 | -58.0215 | -0.027466 | -0.086975 | 0.086976 | 0.23346 | -0.16479 | -0.07782 | 0.07782 | -0.11444 | -0.16937 | 0.086976 | 0.11444 | -0.17853 | -0.009156 | 0.073243 | 122.9782 | 122.9691 | 57.3761 | -122.9782 | 122.9782 | 122.9645 | 57.5455 | -123.0606
829.6875 | 123.0972 | -57.9254 | 65.0299 | 0.12559 | 0.043416 | 0.068832 | 0.022158 | 0.043784 | 0.0036861 | -0.0071733 | -0.024094 | -0.016524 | 0.058397 | 0.048804 | 0.01311 | -0.033216 | 65.094 | -57.9483 | -0.53558 | -58.0902 | 65.0894 | -57.9803 | -58.0536 | -57.9071 | -0.32044 | -58.1955 | 65.1215 | 65.0711 | -58.0627 | -58.1223 | -0.054932 | -0.12817 | 0.05951 | -0.022888 | -0.16479 | -0.036621 | 0.064087 | -0.13733 | -0.19684 | 0.091553 | 0.018311 | -0.27008 | -0.073243 | 0.041199 | 123.0148 | 123.0194 | 57.3898 | -123.0835 | 123.0469 | 122.9965 | 57.605 | -123.1522
830.6406 | 123.2071 | -57.9025 | 64.9429 | 0.61387 | 0.018849 | 0.068832 | 0.025363 | 0.035239 | -0.020881 | -0.016786 | 0.63203 | -0.025069 | 0.051988 | 0.046668 | 0.017383 | -0.026808 | 65.0345 | -57.724 | -0.46692 | -58.0948 | 65.0482 | -57.9437 | -58.0215 | -57.8384 | -0.32501 | -58.1039 | 65.0711 | 64.9887 | -58.0353 | -58.0856 | -0.041199 | -0.11902 | 0.10529 | 0.17853 | -0.19226 | -0.073243 | 0.091553 | -0.13275 | -0.1831 | 0.12817 | 0.064087 | -0.20142 | -0.018311 | 0.045776 | 122.9507 | 122.937 | 57.4356 | -122.9645 | 122.9736 | 122.8912 | 57.5775 | -123.0286
831.6406 | 123.2758 | -57.9071 | 64.9246 | 0.59861 | 0.026326 | 0.067764 | 0.020022 | 0.072623 | -0.0016549 | -0.023195 | 0.571 | -0.029341 | 0.053056 | 0.032783 | 0.0056341 | -0.025739 | 65.0162 | -57.7469 | -0.48065 | -58.0994 | 65.0345 | -57.9895 | -58.0399 | -57.8522 | -0.33417 | -58.1451 | 65.0391 | 64.9521 | -58.0856 | -58.1223 | -0.082398 | -0.13275 | 0.10986 | 0.16022 | -0.19226 | -0.059509 | 0.091552 | -0.17853 | -0.21515 | 0.11444 | 0.054931 | -0.23804 | -0.022889 | 0.027465 | 122.9416 | 122.9233 | 57.4265 | -122.9645 | 122.9462 | 122.8592 | 57.5729 | -123.0469
832.6406 | 123.2529 | -57.9346 | 64.9475 | 0.61387 | 0.01244 | 0.079513 | 0.031771 | 0.055533 | -0.017676 | -0.0093093 | 0.58626 | -0.029341 | 0.061601 | 0.049872 | 0.0067021 | -0.021467 | 65.0345 | -57.7377 | -0.48065 | -58.1177 | 65.0482 | -57.9849 | -58.0536 | -57.8522 | -0.33875 | -58.136 | 65.0436 | 64.9841 | -58.0536 | -58.1406 | -0.050354 | -0.11902 | 0.10071 | 0.19684 | -0.18311 | -0.064087 | 0.086975 | -0.11902 | -0.20599 | 0.09613 | 0.082397 | -0.20142 | 0.004578 | 0.036621 | 122.9828 | 122.9691 | 57.4539 | -123.0011 | 122.9782 | 122.9187 | 57.5958 | -123.0881
833.6406 | 123.2254 | -57.8522 | 65.062 | 0.62913 | 0.049824 | 0.063492 | 0.031771 | 0.055533 | 0.0068901 | -0.013582 | 0.4947 | -0.01866 | 0.05626 | 0.058417 | 0.018451 | -0.023603 | 65.0894 | -57.724 | -0.54474 | -58.049 | 65.181 | -57.8751 | -57.9712 | -57.7744 | -0.3891 | -58.0582 | 65.1398 | 65.0986 | -57.9803 | -58.0261 | -0.022888 | -0.11902 | 0.11902 | 0.12817 | -0.19684 | -0.07782 | 0.027466 | -0.12817 | -0.17395 | 0.07782 | 0.07782 | -0.20599 | -0.032044 | 0.036621 | 123.0331 | 122.9416 | 57.3074 | -123.0331 | 122.9919 | 122.9507 | 57.4631 | -123.0881
834.6406 | 123.1934 | -57.7103 | 65.2222 | 0.56809 | 0.02953 | 0.060287 | 0.034976 | 0.038443 | 0.0026181 | -0.012513 | 0.64729 | -0.022933 | 0.062669 | 0.038123 | 0.0088381 | -0.017194 | 65.1764 | -57.6416 | -0.58136 | -57.9391 | 65.2954 | -57.7972 | -57.843 | -57.6324 | -0.3891 | -57.9391 | 65.2863 | 65.2405 | -57.8247 | -57.8888 | -0.086975 | -0.13275 | 0.073242 | 0.068664 | -0.22888 | -0.09613 | -0.045776 | -0.11444 | -0.17853 | 0.064087 | 0.07782 | -0.22888 | -0.050354 | 0.018311 | 123.0057 | 122.8867 | 57.1289 | -123.0652 | 122.9965 | 122.9507 | 57.3212 | -123.111
835.6406 | 123.1979 | -57.7606 | 65.1443 | 0.46128 | 0.011372 | 0.074173 | 0.012545 | 0.050193 | -0.030494 | -0.024263 | 0.571 | -0.027205 | 0.05092 | 0.053077 | -0.0018429 | -0.019331 | 65.1627 | -57.6141 | -0.51727 | -57.9666 | 65.2313 | -57.7881 | -57.8705 | -57.7148 | -0.39825 | -58.0353 | 65.2267 | 65.1489 | -57.93 | -57.962 | -0.027466 | -0.10986 | 0.086975 | 0.14648 | -0.20599 | -0.096131 | 0.018311 | -0.16937 | -0.20142 | 0.082398 | 0.045776 | -0.27466 | -0.073242 | 0.004578 | 122.9919 | 122.9233 | 57.2433 | -123.0148 | 122.9874 | 122.9095 | 57.3624 | -123.1064
836.6406 | 123.1979 | -57.55 | 65.3778 | 2.1398 | 0.01244 | 0.063492 | 0.016818 | 0.042716 | -0.011268 | -0.022126 | 0.61677 | -0.026137 | 0.045579 | 0.044532 | 0.0034971 | -0.010786 | 65.4373 | -57.3853 | -0.48523 | -57.7423 | 65.4099 | -57.5729 | -57.6553 | -57.4585 | -0.34332 | -57.7423 | 65.4236 | 65.3687 | -57.6782 | -57.7469 | -0.022888 | -0.10529 | 0.032043 | 0.16479 | -0.19226 | -0.086976 | 0.059509 | -0.12817 | -0.19684 | 0.045776 | 0.091553 | -0.19226 | 0.004577 | -0.009156 | 122.9599 | 122.9874 | 57.0648 | -123.0331 | 122.9736 | 122.9187 | 57.2067 | -123.1247
837.6406 | 123.1842 | -57.4493 | 65.4419 | -2.0717 | 0.039143 | 0.06456 | 0.031771 | 0.061942 | -0.00058594 | -0.022126 | 0.41841 | -0.024001 | 0.059465 | 0.038123 | 0.017383 | -0.022535 | 65.4831 | -57.2617 | -0.47607 | -57.6508 | 65.5014 | -57.4997 | -57.5638 | -57.3624 | -0.32501 | -57.6645 | 65.5243 | 65.451 | -57.5912 | -57.6599 | -0.050354 | -0.11444 | 0.059509 | 0.18768 | -0.20142 | -0.086975 | 0.041198 | -0.14191 | -0.21057 | 0.082397 | 0.086975 | -0.21515 | -0.004578 | 0.009155 | 122.9507 | 122.9324 | 56.9733 | -123.0057 | 122.9736 | 122.9004 | 57.1243 | -123.1018
838.6406 | 123.1888 | -57.3853 | 65.4922 | 0.94956 | 0.0049632 | 0.080581 | 0.022158 | 0.055533 | -0.013404 | -0.015718 | 0.47945 | -0.028273 | 0.060533 | 0.057349 | 0.010974 | -0.030012 | 65.5518 | -57.1976 | -0.48981 | -57.6141 | 65.5472 | -57.4631 | -57.4997 | -57.3303 | -0.3891 | -57.6141 | 65.5701 | 65.506 | -57.5409 | -57.6187 | -0.07782 | -0.11444 | 0.054931 | 0.18768 | -0.22888 | -0.11444 | 0.059509 | -0.15564 | -0.23346 | 0.077819 | 0.054932 | -0.22888 | 0.004577 | 0.013732 | 122.9324 | 122.937 | 56.8954 | -122.9919 | 122.9553 | 122.8912 | 56.9962 | -123.111
839.6406 | 123.2117 | -57.2388 | 65.6708 | 3.1926 | 0.020985 | 0.0699 | 0.023226 | 0.053397 | -0.0048589 | -0.017854 | 0.61677 | -0.020796 | 0.057328 | 0.047736 | -0.0093199 | -0.021467 | 65.7852 | -57.0786 | -0.49896 | -57.4173 | 65.7623 | -57.2983 | -57.3669 | -57.1518 | -0.37079 | -57.4539 | 65.7349 | 65.6891 | -57.3853 | -57.4356 | -0.059509 | -0.12817 | 0.091553 | 0.16022 | -0.17853 | -0.050354 | 0.11444 | -0.14648 | -0.19684 | 0.064087 | 0.086976 | -0.21515 | -0.01831 | 0.018311 | 123.0011 | 123.024 | 56.7398 | -123.0377 | 122.9736 | 122.9279 | 56.868 | -123.1064
840.6406 | 123.2162 | -57.193 | 65.712 | 0.56809 | 0.026326 | 0.070968 | 0.028567 | 0.044852 | 0.016503 | -0.018922 | 0.52522 | -0.012251 | 0.065873 | 0.044532 | 0.0024291 | -0.023603 | 65.8173 | -57.0053 | -0.50812 | -57.3669 | 65.7852 | -57.2159 | -57.3029 | -57.0877 | -0.37994 | -57.3898 | 65.7898 | 65.7211 | -57.3212 | -57.3853 | -0.022888 | -0.10986 | 0.073242 | 0.18768 | -0.17395 | -0.064087 | 0.10529 | -0.12817 | -0.19226 | 0.07782 | 0.10529 | -0.19684 | -0.004578 | 0.009155 | 122.9782 | 123.0103 | 56.6849 | -123.0148 | 122.9828 | 122.9141 | 56.813 | -123.0972
841.6406 | 123.1613 | -56.8771 | 66.0278 | 0.43077 | 0.0092362 | 0.065628 | 0.022158 | 0.044852 | -0.014472 | -0.027467 | 0.47945 | -0.037886 | 0.038102 | 0.056281 | 0.0045661 | -0.022535 | 66.0278 | -56.7261 | -0.53558 | -57.106 | 66.0736 | -56.9458 | -56.9824 | -56.8314 | -0.41199 | -57.1106 | 66.1011 | 66.0416 | -57.0328 | -57.074 | -0.068665 | -0.10529 | 0.045776 | 0.15106 | -0.22888 | -0.1236 | 0 | -0.15564 | -0.19684 | 0.073242 | 0.045776 | -0.23346 | -0.036621 | 0.013733 | 122.9507 | 122.905 | 56.3416 | -123.0103 | 122.9782 | 122.9187 | 56.4651 | -123.1018
842.6406 | 123.1613 | -56.4651 | 66.4169 | 0.52232 | 0.016713 | 0.08165 | 0.031771 | 0.053397 | -0.0048589 | -0.025331 | 0.54048 | -0.030409 | 0.054124 | 0.047736 | 0.0056341 | -0.025739 | 66.4398 | -56.3324 | -0.49896 | -56.694 | 66.4856 | -56.5384 | -56.5887 | -56.456 | -0.40741 | -56.749 | 66.4764 | 66.3803 | -56.6483 | -56.694 | -0.073242 | -0.1236 | 0.068665 | 0.13275 | -0.22888 | -0.10529 | 0.022888 | -0.18311 | -0.22888 | 0.059509 | 0.009155 | -0.28381 | -0.054931 | -0.036621 | 122.9507 | 122.905 | 55.9662 | -123.0057 | 122.9416 | 122.8455 | 56.0577 | -123.111
843.6406 | 123.1979 | -56.0623 | 66.8335 | 0.17137 | 0.0017592 | 0.076309 | 0.027499 | 0.037375 | -0.012336 | -0.033876 | 0.26582 | -0.031478 | 0.063737 | 0.043464 | 0.0024291 | -0.023603 | 66.8015 | -55.9708 | -0.5722 | -56.3232 | 66.8838 | -56.1722 | -56.2363 | -56.044 | -0.37079 | -56.2958 | 66.9067 | 66.8289 | -56.2134 | -56.3095 | -0.10986 | -0.17395 | 0.050354 | 0.091553 | -0.26093 | -0.086975 | -0.032043 | -0.15106 | -0.24719 | 0.073242 | 0.018311 | -0.23346 | 0.013733 | -0.004578 | 122.9462 | 122.8638 | 55.4901 | -123.0698 | 122.9691 | 122.8912 | 55.6915 | -123.143
844.6406 | 123.175 | -55.5496 | 67.3691 | 0.35447 | 0.011372 | 0.096603 | 0.011477 | 0.048056 | -0.0016549 | -0.029603 | 0.4947 | -0.028273 | 0.054124 | 0.057349 | 0.0056341 | -0.017194 | 67.4561 | -55.3436 | -0.52643 | -55.7098 | 67.4927 | -55.5634 | -55.5954 | -55.4443 | -0.44403 | -55.806 | 67.4561 | 67.337 | -55.6778 | -55.7236 | -0.013732 | -0.045776 | 0.1236 | 0.20599 | -0.16022 | -0.11444 | 0.086975 | -0.12817 | -0.17395 | 0.086975 | 0.10529 | -0.25635 | -0.082397 | -0.032044 | 123.0423 | 123.0057 | 55.0232 | -122.9645 | 123.0057 | 122.8867 | 55.1056 | -123.0927
845.6406 | 123.1888 | -56.0806 | 66.8518 | 0.33921 | -0.0078538 | 0.066696 | 0.01575 | 0.056601 | -0.0091309 | -0.013582 | 0.28108 | -0.032546 | 0.045579 | 0.034919 | 0.00029315 | -0.023603 | 66.8747 | -55.9113 | -0.5722 | -56.2866 | 66.9342 | -56.1264 | -56.1722 | -56.0257 | -0.42114 | -56.2775 | 66.9342 | 66.861 | -56.2042 | -56.2546 | -0.045777 | -0.091553 | 0.082397 | 0.16937 | -0.20599 | -0.11444 | 0.022888 | -0.1236 | -0.17395 | 0.082397 | 0.054931 | -0.19684 | -0.022888 | 0.009155 | 123.0148 | 122.9553 | 55.5084 | -123.024 | 123.0148 | 122.9416 | 55.6595 | -123.1064
846.6406 | 123.1796 | -55.8655 | 67.0166 | 0.35447 | 0.0038952 | 0.073105 | 0.036044 | 0.039511 | -0.0027229 | -0.01999 | 0.43367 | -0.032546 | 0.03917 | 0.053077 | 0.018451 | -0.022535 | 67.0807 | -55.6686 | -0.55389 | -56.0898 | 67.0853 | -55.9479 | -56.0211 | -55.7831 | -0.3891 | -56.0761 | 67.1036 | 67.0212 | -56.0211 | -56.0715 | -0.082397 | -0.15564 | 0.068664 | 0.19684 | -0.2243 | -0.068665 | 0.064086 | -0.15564 | -0.20599 | 0.086975 | 0.082398 | -0.21057 | -0.004578 | 0.004577 | 122.9507 | 122.9462 | 55.3116 | -123.0377 | 122.9691 | 122.8867 | 55.4764 | -123.0881
847.6406 | 123.1522 | -56.0623 | 66.7969 | 0.59861 | 0.025258 | 0.067764 | 0.027499 | 0.046988 | 0.015435 | 0.0013717 | 0.47945 | -0.019728 | 0.053056 | 0.052009 | 0.0088381 | -0.021467 | 66.925 | -55.8517 | -0.58136 | -56.2729 | 66.8976 | -56.1493 | -56.2042 | -55.9799 | -0.40741 | -56.2775 | 66.9113 | 66.8015 | -56.25 | -56.2958 | -0.086975 | -0.14191 | 0.10071 | 0.21057 | -0.21057 | -0.068664 | 0.12817 | -0.18768 | -0.23346 | 0.11444 | 0.082398 | -0.21515 | 0.01831 | 0.004578 | 122.9599 | 122.9874 | 55.481 | -123.0011 | 122.9736 | 122.8638 | 55.6549 | -123.0927
848.6406 | 123.2162 | -55.8609 | 67.0349 | 1.2395 | 0.018849 | 0.06456 | 0.022158 | 0.039511 | 0.0079581 | -0.023195 | 0.66255 | -0.033614 | 0.055192 | 0.043464 | 0.0088381 | -0.026808 | 67.1265 | -55.6503 | -0.56305 | -56.0486 | 67.1082 | -55.9067 | -55.9937 | -55.8014 | -0.41657 | -56.0898 | 67.1082 | 67.0166 | -56.012 | -56.0623 | -0.045776 | -0.13275 | 0.073242 | 0.21057 | -0.18768 | -0.054932 | 0.091553 | -0.15106 | -0.20142 | 0.073242 | 0.059509 | -0.22888 | -0.027466 | -0.01831 | 122.9691 | 122.9874 | 55.2979 | -123.0286 | 122.9691 | 122.8775 | 55.4443 | -123.0972
849.6406 | 123.175 | -55.5405 | 67.3828 | 0.46128 | 0.019917 | 0.073105 | 0.026431 | 0.057669 | -0.0080629 | -0.012513 | 0.43367 | -0.029341 | 0.049852 | 0.050941 | 0.0077701 | -0.018263 | 67.6392 | -55.1605 | -0.55847 | -55.5222 | 67.6758 | -55.3665 | -55.4443 | -55.4672 | -0.59052 | -55.8151 | 67.4698 | 67.4149 | -55.6412 | -55.7144 | 0.17395 | 0.09613 | 0.29297 | 0.37994 | 0.01831 | -0.07782 | 0.25635 | -0.10071 | -0.17395 | 0.086976 | 0.073242 | -0.27466 | -0.10071 | 0.032044 | 123.2162 | 123.1796 | 54.982 | -122.8271 | 123.0103 | 122.9553 | 54.95 | -123.0972
850.6406 | 123.1705 | -54.9179 | 67.9871 | 0.53758 | 0.010304 | 0.074173 | 0.027499 | 0.049125 | -0.0016549 | -0.022126 | 0.46419 | -0.027205 | 0.049852 | 0.042396 | 0.0013611 | -0.022535 | 68.042 | -54.7531 | -0.60883 | -55.1239 | 68.0832 | -54.9362 | -55.0278 | -54.8813 | -0.45319 | -55.1743 | 68.0511 | 67.9871 | -55.0461 | -55.1285 | -0.01831 | -0.10986 | 0.09613 | 0.16479 | -0.20599 | -0.09613 | 0.054931 | -0.12817 | -0.21057 | 0.064086 | 0.036621 | -0.25635 | -0.045776 | 0 | 123.0011 | 122.9599 | 54.3091 | -123.0148 | 122.9691 | 122.905 | 54.4647 | -123.1155
851.6406 | 123.2025 | -54.6158 | 68.3395 | 0.2324 | 0.0081682 | 0.075241 | 0.018954 | 0.049125 | -0.0059269 | -0.01465 | 0.3116 | -0.032546 | 0.041307 | 0.044532 | -0.0029109 | -0.017194 | 68.2983 | -54.5013 | -0.6134 | -54.8447 | 68.3899 | -54.6844 | -54.7256 | -54.6158 | -0.42572 | -54.8584 | 68.3807 | 68.2709 | -54.7852 | -54.8218 | -0.068664 | -0.10986 | 0.050354 | 0.11444 | -0.22888 | -0.11902 | -0.041199 | -0.16937 | -0.20599 | 0.041198 | 0 | -0.24261 | -0.036621 | -0.068665 | 123.0057 | 122.9141 | 54.0024 | -123.0652 | 122.9965 | 122.8867 | 54.1901 | -123.1613
852.6406 | 123.1705 | -30.6747 | 92.2852 | 0.40025 | 0.011372 | 0.068832 | 0.0029318 | 0.044852 | -0.00058594 | -0.023195 | 0.60152 | -0.026137 | 0.048783 | 0.0456 | 0.0067021 | -0.027876 | 92.1982 | -30.7434 | -0.23346 | -31.0043 | 92.308 | -30.7205 | -30.8304 | -30.78 | -0.036621 | -30.7114 | 92.3538 | 92.2531 | -30.8029 | -30.8716 | -0.045776 | -0.15564 | 0.022888 | -0.068664 | -0.32959 | -0.17395 | -0.086975 | -0.12817 | -0.19684 | 0.068665 | -0.10528 | -0.036621 | 0.16022 | -0.032043 | 122.9828 | 122.8729 | 30.4413 | -123.1155 | 123.0286 | 122.9279 | 30.6381 | -123.1567
853.6406 | 123.2117 | -55.3711 | 67.3599 | 0.3087 | 0.0071002 | 0.073105 | 0.023226 | 0.042716 | -0.017676 | -0.016786 | 0.3116 | -0.026137 | 0.059465 | 0.044532 | 0.0077701 | -0.019331 | 67.0624 | -55.6137 | -0.28381 | -55.2429 | 67.6025 | -55.0369 | -54.8172 | -55.2841 | -0.52643 | -55.4718 | 67.7811 | 67.6483 | -55.3711 | -55.4169 | 0.33417 | 0.55389 | 0.24261 | -0.24261 | 0.12817 | -0.42572 | -0.29755 | 0 | -0.045776 | 0.42114 | 0.086975 | -0.10071 | -0.054932 | 0.28839 | 122.9736 | 122.4335 | 55.0873 | -122.1771 | 123.1522 | 123.0194 | 54.8447 | -122.7768
854.6406 | 123.2162 | -26.2527 | 96.7117 | 0.59861 | 0.010304 | 0.063492 | 0.027499 | 0.043784 | 0.0090271 | -0.015718 | 2.5852 | -0.029341 | 0.048783 | 0.042396 | 0.021655 | -0.03108 | 96.7072 | -26.2939 | -0.1831 | -26.5137 | 96.7621 | -26.2939 | -26.3901 | -26.2985 | 0.004578 | -26.2299 | 96.7941 | 96.6934 | -26.3855 | -26.4084 | -0.041198 | -0.13733 | 0.050354 | -0.041198 | -0.26093 | -0.1236 | -0.004578 | -0.13275 | -0.15564 | 0.082397 | -0.045776 | 0.022889 | 0.17853 | -0.018311 | 123.0148 | 122.9599 | 26.0696 | -123.1018 | 123.0469 | 122.9462 | 26.2573 | -123.1201
855.6406 | 123.1979 | -24.8657 | 98.0621 | 0.44602 | 0.011372 | 0.078445 | 0.037112 | 0.049125 | 0.0068901 | -0.025331 | 0.58626 | -0.01866 | 0.035966 | 0.034919 | 0.02486 | -0.026808 | 98.0209 | -24.9527 | -0.17853 | -25.1724 | 98.1171 | -24.9481 | -25.0168 | -24.971 | 0.009155 | -24.852 | 98.1674 | 98.0804 | -25.0031 | -25.058 | -0.082397 | -0.15106 | 0.054931 | -0.086975 | -0.3067 | -0.15564 | -0.041199 | -0.13733 | -0.19226 | 0.10528 | -0.10529 | 0.013733 | 0.20599 | 0.01831 | 122.9828 | 122.8867 | 24.6872 | -123.0789 | 123.0331 | 122.9462 | 24.8749 | -123.1201
856.6406 | 123.2071 | -24.4537 | 98.5153 | 0.36973 | 0.0017592 | 0.073105 | 0.022158 | 0.037375 | -0.0080629 | -0.022126 | 0.3116 | -0.026137 | 0.043443 | 0.061622 | 0.01311 | -0.021467 | 98.41 | -24.559 | -0.2243 | -24.7513 | 98.6115 | -24.527 | -24.5956 | -24.5544 | 0.004578 | -24.44 | 98.6023 | 98.5199 | -24.5773 | -24.6094 | -0.073243 | -0.14191 | 0.09613 | -0.10529 | -0.29755 | -0.15564 | -0.10529 | -0.1236 | -0.15564 | 0.086975 | -0.10071 | 0.013733 | 0.16937 | 0.004577 | 123.0652 | 122.8638 | 24.2294 | -123.111 | 123.056 | 122.9736 | 24.4583 | -123.1247
857.6875 | 123.2254 | -24.0784 | 98.9639 | 0.33921 | 0.047688 | 0.061355 | 0.023226 | 0.033103 | 0.02398 | -0.0050373 | 0.0522 | -0.014388 | 0.055192 | 0.049872 | 0.034473 | -0.035352 | 98.8037 | -24.2249 | -0.30212 | -24.3576 | 99.0784 | -24.1241 | -24.1837 | -24.2157 | -0.09613 | -24.1241 | 99.0692 | 98.9502 | -24.1745 | -24.2386 | -0.045777 | -0.10529 | 0.11444 | -0.14649 | -0.27924 | -0.17395 | -0.16022 | -0.096131 | -0.16022 | 0.10529 | -0.13733 | -0.045777 | 0.11444 | -0.013733 | 123.1567 | 122.8821 | 23.7762 | -123.1476 | 123.1476 | 123.0286 | 23.9822 | -123.2025
858.6406 | 123.1888 | -23.7305 | 99.2523 | 0.36973 | 0.0081682 | 0.065628 | 0.031771 | 0.042716 | -0.017676 | -0.011445 | 0.35738 | -0.027205 | 0.037034 | 0.044532 | 0.015247 | -0.00865 | 99.1608 | -23.8037 | -0.21515 | -23.9731 | 99.3668 | -23.7442 | -23.8037 | -23.8266 | 0 | -23.6938 | 99.3484 | 99.2706 | -23.8449 | -23.8632 | -0.013733 | -0.073242 | 0.11444 | -0.073242 | -0.24261 | -0.16937 | -0.091552 | -0.11444 | -0.13275 | 0.096131 | -0.09613 | 0.036621 | 0.16937 | 0.018311 | 123.0972 | 122.8912 | 23.5153 | -123.056 | 123.0789 | 123.0011 | 23.7305 | -123.1155
859.6406 | 123.1796 | -23.5519 | 99.4217 | 0.43077 | 0.0060322 | 0.068832 | 0.028567 | 0.04592 | -0.0091309 | -0.021058 | 0.20479 | -0.024001 | 0.048783 | 0.046668 | 0.012042 | -0.019331 | 99.3439 | -23.6206 | -0.20142 | -23.8037 | 99.5499 | -23.5794 | -23.6572 | -23.6664 | -0.013733 | -23.5199 | 99.5316 | 99.4034 | -23.6481 | -23.7305 | -0.027466 | -0.10529 | 0.12817 | -0.068664 | -0.25177 | -0.14648 | -0.07782 | -0.09613 | -0.17853 | 0.10986 | -0.11444 | 0.032044 | 0.21057 | -0.018311 | 123.1018 | 122.8958 | 23.3505 | -123.0789 | 123.0835 | 122.9553 | 23.5382 | -123.1522
860.6406 | 123.2071 | -23.2956 | 99.6552 | 0.43077 | 0.0092362 | 0.062424 | 0.026431 | 0.043784 | -0.01554 | -0.01999 | 0.40315 | -0.025069 | 0.051988 | 0.039191 | 0.01311 | -0.012922 | 99.6231 | -23.3231 | -0.20142 | -23.5428 | 99.7559 | -23.3597 | -23.4283 | -23.3826 | 0.027466 | -23.2407 | 99.7513 | 99.6368 | -23.4192 | -23.4604 | -0.064087 | -0.13275 | 0.10071 | -0.027466 | -0.24719 | -0.11444 | -0.032043 | -0.1236 | -0.16479 | 0.096131 | -0.086975 | 0.054931 | 0.21973 | -0.01831 | 123.0515 | 122.9187 | 23.0942 | -123.0835 | 123.0469 | 122.9324 | 23.3231 | -123.1155
861.6406 | 123.2025 | -22.9614 | 100.0076 | 0.33921 | 0.0028272 | 0.068832 | 0.0082728 | 0.052329 | -0.0048589 | -0.01999 | 0.29634 | -0.030409 | 0.047715 | 0.039191 | 0.022724 | -0.033216 | 99.939 | -22.998 | -0.1831 | -23.204 | 100.0854 | -23.0164 | -23.0713 | -23.0347 | 0.018311 | -22.8973 | 100.1129 | 99.9756 | -23.1033 | -23.1171 | -0.054931 | -0.10986 | 0.07782 | -0.036621 | -0.24262 | -0.13275 | -0.068664 | -0.14191 | -0.15564 | 0.10529 | -0.073242 | 0.064087 | 0.21973 | -0.032043 | 123.0469 | 122.9004 | 22.7783 | -123.0789 | 123.0743 | 122.937 | 22.9797 | -123.1247
862.6406 | 123.1659 | -22.6547 | 100.3006 | 0.46128 | 0.0038952 | 0.0699 | 0.034976 | 0.036307 | -0.0016549 | -0.029603 | 0.29634 | -0.032546 | 0.054124 | 0.052009 | 0.0067021 | -0.020399 | 100.2594 | -22.7142 | -0.25635 | -22.9065 | 100.4334 | -22.6868 | -22.7783 | -22.7554 | -0.018311 | -22.6181 | 100.4517 | 100.3189 | -22.7692 | -22.8104 | -0.032044 | -0.1236 | 0.13275 | -0.059509 | -0.25177 | -0.12817 | -0.041199 | -0.11444 | -0.15564 | 0.15106 | -0.10071 | 0.036621 | 0.19226 | 0.018311 | 123.0881 | 122.9141 | 22.3984 | -123.0789 | 123.1064 | 122.9736 | 22.6364 | -123.111
863.6406 | 123.2437 | -22.5769 | 100.3693 | 0.21714 | -0.0035808 | 0.079513 | 0.01575 | 0.044852 | -0.0059269 | -0.030671 | -0.024094 | -0.030409 | 0.057328 | 0.041327 | 0.0056341 | -0.023603 | 100.3189 | -22.6364 | -0.15106 | -22.8012 | 100.5112 | -22.6135 | -22.7188 | -22.641 | 0.10071 | -22.4579 | 100.5386 | 100.3876 | -22.6822 | -22.7325 | -0.036621 | -0.14191 | 0.14191 | -0.05951 | -0.2243 | -0.082397 | -0.050354 | -0.10529 | -0.15564 | 0.16937 | -0.064087 | 0.11902 | 0.27466 | 0.01831 | 123.0881 | 122.8958 | 22.4258 | -123.0881 | 123.1155 | 122.9645 | 22.6776 | -123.1018
864.6406 | 123.1934 | -22.1695 | 100.8133 | 0.2324 | -0.0057178 | 0.079513 | 0.025363 | 0.035239 | -0.0069949 | -0.024263 | 0.14375 | -0.046431 | 0.053056 | 0.050941 | 0.0077701 | -0.027876 | 100.6897 | -22.261 | -0.21057 | -22.4121 | 100.8957 | -22.2382 | -22.3068 | -22.2427 | 0.018311 | -22.0963 | 100.914 | 100.7904 | -22.2977 | -22.3251 | -0.068664 | -0.13733 | 0.082398 | -0.091552 | -0.24261 | -0.10529 | -0.1236 | -0.12817 | -0.15564 | 0.10071 | -0.073242 | 0.073243 | 0.22888 | -0.022888 | 123.0652 | 122.8592 | 21.9589 | -123.1201 | 123.0835 | 122.9599 | 22.1878 | -123.1384
865.6406 | 123.1842 | -22.0642 | 100.8911 | 0.21714 | 0.0049632 | 0.08165 | 0.026431 | 0.059806 | -0.0069949 | -0.025331 | -0.054612 | -0.032546 | 0.042375 | 0.052009 | 0.021655 | -0.006513 | 100.7996 | -22.1329 | -0.17395 | -22.3114 | 100.9872 | -22.1283 | -22.2107 | -22.142 | 0.10071 | -21.9864 | 101.0147 | 100.882 | -22.2015 | -22.2336 | -0.064087 | -0.14648 | 0.096131 | -0.068665 | -0.24719 | -0.10071 | -0.091552 | -0.13733 | -0.16937 | 0.1236 | -0.07782 | 0.07782 | 0.24719 | -0.009155 | 123.0515 | 122.8638 | 21.8903 | -123.1018 | 123.0789 | 122.9462 | 22.1649 | -123.1247
866.6406 | 123.1567 | -22.0459 | 100.914 | 0.35447 | -0.0035808 | 0.074173 | 0.040316 | 0.054465 | -0.0080629 | -0.030671 | -3.7167 | -0.015456 | 0.055192 | 0.047736 | 0.015247 | -0.023603 | 100.8453 | -22.1054 | -0.20599 | -22.2885 | 101.0422 | -22.1054 | -22.1878 | -22.1603 | 0.059509 | -21.9864 | 101.0788 | 100.9232 | -22.1649 | -22.2061 | -0.05951 | -0.14191 | 0.12817 | -0.05951 | -0.24261 | -0.10071 | -0.068664 | -0.11902 | -0.16022 | 0.16479 | -0.11444 | 0.059509 | 0.21973 | 0.009156 | 123.0881 | 122.8912 | 21.8399 | -123.1018 | 123.1247 | 122.9691 | 22.1054 | -123.1201
867.6406 | 123.1842 | -21.7529 | 101.2207 | 0.44602 | 0.013508 | 0.067764 | 0.023226 | 0.046988 | -0.0069949 | -0.022126 | 0.32686 | -0.029341 | 0.046647 | 0.057349 | 0.0067021 | -0.021467 | 101.1246 | -21.785 | -0.21973 | -21.9818 | 101.3351 | -21.7529 | -21.904 | -21.8399 | 0.004578 | -21.6751 | 101.3443 | 101.2299 | -21.8445 | -21.9131 | 0 | -0.15106 | 0.11444 | -0.032043 | -0.22888 | -0.07782 | -0.09613 | -0.091552 | -0.16022 | 0.1236 | -0.086975 | 0.07782 | 0.23804 | 0.009155 | 123.0881 | 122.8775 | 21.5332 | -123.1247 | 123.0972 | 122.9828 | 21.7575 | -123.1338
868.6406 | 123.1888 | -21.6019 | 101.3718 | 0.44602 | 0.0081682 | 0.062424 | 0.02109 | 0.042716 | -0.0059269 | -0.024263 | 0.3116 | -0.021865 | 0.043443 | 0.047736 | 0.0099061 | -0.020399 | 101.3031 | -21.666 | -0.23346 | -21.8719 | 101.4679 | -21.6614 | -21.7346 | -21.698 | 0.018311 | -21.5378 | 101.5228 | 101.3443 | -21.6934 | -21.7667 | -0.059509 | -0.13275 | 0.096131 | -0.064087 | -0.27008 | -0.13733 | -0.068664 | -0.091552 | -0.1648 | 0.15106 | -0.09613 | 0.064087 | 0.22888 | -0.027466 | 123.0698 | 122.905 | 21.3684 | -123.1064 | 123.1247 | 122.9462 | 21.6202 | -123.1384
869.6406 | 123.2437 | -21.785 | 101.1703 | 0.079814 | -0.0025128 | 0.077377 | 0.017886 | 0.04058 | 0.0015501 | -0.012513 | -0.11565 | -0.030409 | 0.029557 | 0.043464 | 0.0088381 | -0.034284 | 101.1749 | -21.7621 | -0.11444 | -21.9772 | 101.2665 | -21.8353 | -21.9223 | -21.8262 | 0.18768 | -21.6385 | 101.3123 | 101.1566 | -21.8994 | -21.936 | -0.050354 | -0.13733 | 0.09613 | 0.022888 | -0.19226 | -0.054932 | 0.004578 | -0.11444 | -0.15106 | 0.14191 | -0.041199 | 0.14648 | 0.29755 | -0.013733 | 123.0515 | 122.9599 | 21.6705 | -123.0927 | 123.0972 | 122.9416 | 21.9727 | -123.1064
870.6406 | 123.2666 | -21.1304 | 101.857 | 0.11033 | 0.0049632 | 0.08165 | 0.011477 | 0.046988 | -0.013404 | -0.032808 | -0.16142 | -0.038954 | 0.047715 | 0.033851 | 0.01311 | -0.021467 | 101.738 | -21.1716 | 0.022888 | -21.3821 | 101.8433 | -21.2585 | -21.3089 | -21.1761 | 0.29755 | -20.874 | 101.9348 | 101.8021 | -21.2585 | -21.2952 | -0.12817 | -0.17853 | -0.013733 | -0.041199 | -0.25177 | -0.073242 | -0.11902 | -0.12817 | -0.16479 | 0.077819 | -0.045776 | 0.25635 | 0.42114 | -0.054932 | 122.9736 | 122.8683 | 21.1533 | -123.1659 | 123.0652 | 122.9324 | 21.4279 | -123.1522
871.6406 | 123.2437 | -20.7596 | 102.2461 | 0.17137 | 0.0017592 | 0.083786 | 0.022158 | 0.030967 | -0.0037909 | -0.0093093 | -0.054612 | -0.031478 | 0.042375 | 0.046668 | 0.023792 | -0.024671 | 102.1408 | -20.7596 | -0.16937 | -20.961 | 102.3331 | -20.7642 | -20.8786 | -20.8054 | 0.11444 | -20.6177 | 102.3651 | 102.2278 | -20.8511 | -20.9198 | -0.004577 | -0.11902 | 0.086975 | 0 | -0.20142 | -0.082398 | -0.10529 | -0.091552 | -0.16022 | 0.11902 | -0.045776 | 0.14191 | 0.30212 | -0.018311 | 123.0927 | 122.9004 | 20.5902 | -123.1247 | 123.1247 | 122.9874 | 20.874 | -123.1659
872.6406 | 123.23 | -21.199 | 101.77 | 0.27818 | 0.02419 | 0.089126 | 0.03284 | 0.042716 | -0.0037909 | -0.016786 | -0.0088351 | -0.032546 | 0.047715 | 0.0456 | 0.01311 | -0.033216 | 101.683 | -21.2311 | -0.16479 | -21.4371 | 101.8616 | -21.2585 | -21.3318 | -21.2677 | 0.11444 | -21.0846 | 101.8982 | 101.7517 | -21.3226 | -21.3638 | -0.059509 | -0.13275 | 0.091552 | -0.032043 | -0.23804 | -0.10529 | -0.086976 | -0.1236 | -0.1648 | 0.12817 | -0.068664 | 0.11444 | 0.27924 | -0.018311 | 123.0606 | 122.8821 | 21.0342 | -123.1018 | 123.0972 | 122.9507 | 21.3135 | -123.1339
873.6406 | 123.2208 | -21.405 | 101.5549 | 0.064555 | -0.012126 | 0.072037 | 0.025363 | 0.042716 | -0.01554 | -0.026399 | -0.19194 | -0.029341 | 0.041307 | 0.043464 | 0.023792 | -0.019331 | 101.4542 | -21.4554 | -0.16479 | -21.6522 | 101.6327 | -21.492 | -21.5744 | -21.4828 | 0.12817 | -21.2494 | 101.6876 | 101.5503 | -21.492 | -21.5561 | -0.086975 | -0.16937 | 0.077819 | -0.050354 | -0.24719 | -0.07782 | -0.10071 | -0.086975 | -0.15106 | 0.13275 | -0.07782 | 0.15564 | 0.3067 | -0.004578 | 123.0377 | 122.8592 | 21.2402 | -123.1293 | 123.0927 | 122.9553 | 21.5332 | -123.111
874.6406 | 123.2117 | -21.1716 | 101.7929 | 0.14085 | -0.0046498 | 0.077377 | 0.02109 | 0.043784 | -0.0027229 | -0.021058 | 0.082718 | -0.032546 | 0.03383 | 0.049872 | 0.012042 | -0.025739 | 101.7197 | -21.1761 | -0.18768 | -21.3959 | 101.9394 | -21.2219 | -21.2952 | -21.2311 | 0.091553 | -21.0342 | 101.944 | 101.7838 | -21.2677 | -21.3226 | -0.050354 | -0.1236 | 0.14648 | -0.004577 | -0.2243 | -0.10071 | -0.073242 | -0.09613 | -0.15106 | 0.15106 | -0.059509 | 0.13733 | 0.28839 | -0.009156 | 123.111 | 122.8912 | 20.9839 | -123.0881 | 123.1155 | 122.9553 | 21.2631 | -123.1155
875.6406 | 123.2117 | -21.2082 | 101.7654 | 0.24766 | 0.013508 | 0.08699 | 0.025363 | 0.033103 | -0.010199 | -0.022126 | 1.1508 | -0.017592 | 0.025285 | 0.039191 | 0.018451 | -0.023603 | 101.6464 | -21.2723 | -0.21515 | -21.492 | 101.825 | -21.2906 | -21.3776 | -21.3135 | 0.073242 | -21.1212 | 101.889 | 101.7197 | -21.3409 | -21.3867 | -0.082397 | -0.16937 | 0.059509 | -0.064087 | -0.28381 | -0.11444 | -0.11902 | -0.13275 | -0.17853 | 0.1236 | -0.10529 | 0.086975 | 0.2655 | -0.045776 | 123.0331 | 122.8546 | 20.993 | -123.143 | 123.0972 | 122.9279 | 21.2814 | -123.1522
876.6406 | 123.23 | -20.9152 | 102.0309 | -0.072774 | 0.0017592 | 0.083786 | 0.044589 | 0.038443 | -0.017676 | -0.025331 | -0.19194 | -0.028273 | 0.048783 | 0.040259 | 0.0077701 | -0.025739 | 101.9806 | -20.8878 | -0.1236 | -21.1487 | 102.1133 | -21.0114 | -21.0938 | -20.9976 | 0.15564 | -20.8145 | 102.1454 | 101.9852 | -21.0663 | -21.08 | -0.096131 | -0.17853 | 0.082397 | 0.027466 | -0.23346 | -0.054932 | -0.050354 | -0.15106 | -0.1648 | 0.11444 | -0.082398 | 0.10071 | 0.2655 | -0.045777 | 123.0286 | 122.8958 | 20.7916 | -123.1247 | 123.0606 | 122.9004 | 21.0709 | -123.111
877.6406 | 123.2391 | -20.6635 | 102.2736 | -0.10329 | 0.018849 | 0.08165 | 0.027499 | 0.039511 | -0.00058594 | -0.027467 | -0.19194 | -0.029341 | 0.054124 | 0.044532 | 0.012042 | -0.033216 | 102.2186 | -20.6497 | -0.13733 | -20.8969 | 102.356 | -20.7504 | -20.842 | -20.7275 | 0.20142 | -20.5444 | 102.4063 | 102.2415 | -20.8054 | -20.8374 | -0.086975 | -0.17853 | 0.082397 | 0.013733 | -0.23346 | -0.054932 | -0.054932 | -0.14191 | -0.17395 | 0.13275 | -0.064087 | 0.11902 | 0.29297 | -0.032044 | 123.0194 | 122.8821 | 20.5261 | -123.1155 | 123.0698 | 122.905 | 20.8649 | -123.111
878.6406 | 123.2208 | -20.3934 | 102.5436 | 0.034038 | 0.00069119 | 0.079513 | 0.031771 | 0.036307 | -0.0091309 | -0.033876 | -0.17668 | -0.033614 | 0.041307 | 0.030646 | 0.0067021 | -0.03108 | 102.5391 | -20.3568 | -0.09613 | -20.5948 | 102.681 | -20.4483 | -20.5307 | -20.4529 | 0.19226 | -20.2515 | 102.6993 | 102.5391 | -20.5124 | -20.5765 | -0.054931 | -0.13733 | 0.13733 | 0.036622 | -0.20142 | -0.064087 | -0.004578 | -0.11902 | -0.18311 | 0.15564 | -0.059509 | 0.14191 | 0.32501 | -0.004578 | 123.0743 | 122.9324 | 20.2972 | -123.0743 | 123.0927 | 122.9324 | 20.5856 | -123.1201
879.6406 | 123.2529 | -20.2332 | 102.7405 | -0.13381 | 0.0028272 | 0.073105 | 0.02109 | 0.050193 | -0.0048589 | -0.022126 | -0.16142 | -0.027205 | 0.035966 | 0.041327 | 0.010974 | -0.030012 | 102.7313 | -20.1508 | -0.10529 | -20.3751 | 102.8687 | -20.2377 | -20.3247 | -20.256 | 0.17395 | -20.0592 | 102.8915 | 102.7267 | -20.3064 | -20.3613 | -0.004578 | -0.091553 | 0.12817 | 0.082397 | -0.14191 | -0.050354 | -0.009156 | -0.073242 | -0.12817 | 0.15106 | -0.022888 | 0.17395 | 0.30212 | -0.013733 | 123.1018 | 122.9645 | 20.1279 | -123.0652 | 123.1247 | 122.9599 | 20.4071 | -123.1018
880.6406 | 123.2391 | -20.1462 | 102.8229 | -0.011739 | -0.0025128 | 0.082718 | 0.026431 | 0.04592 | -0.0091309 | -0.01465 | -0.19194 | -0.024001 | 0.051988 | 0.043464 | 0.01311 | -0.032148 | 102.7496 | -20.105 | -0.1236 | -20.3659 | 102.9282 | -20.2194 | -20.311 | -20.2057 | 0.16937 | -20.0272 | 102.9099 | 102.7634 | -20.2835 | -20.3247 | -0.073242 | -0.1648 | 0.10529 | 0.041199 | -0.21973 | -0.054932 | -0.073242 | -0.13733 | -0.17853 | 0.086975 | -0.059509 | 0.11902 | 0.29755 | -0.059509 | 123.0743 | 122.8958 | 20.0226 | -123.1338 | 123.056 | 122.9095 | 20.3156 | -123.1476
881.6406 | 123.2254 | -20.1645 | 102.7771 | 0.018779 | -0.013195 | 0.072037 | 0.020022 | 0.043784 | 0.0015501 | -0.026399 | -0.2072 | -0.01866 | 0.032762 | 0.048804 | 0.016315 | -0.022535 | 102.7771 | -20.0958 | -0.09613 | -20.3293 | 102.9236 | -20.2103 | -20.2744 | -20.2103 | 0.19684 | -20.0226 | 102.9282 | 102.7771 | -20.2744 | -20.3247 | -0.045776 | -0.10986 | 0.14648 | 0.068665 | -0.16479 | -0.054932 | 0 | -0.10986 | -0.16022 | 0.15106 | -0.045776 | 0.14191 | 0.30212 | 0 | 123.0881 | 122.9416 | 20.0684 | -123.0515 | 123.0927 | 122.9416 | 20.3613 | -123.1018
882.6406 | 123.2162 | -20.2377 | 102.7496 | 0.049296 | -0.0025128 | 0.090195 | 0.031771 | 0.048056 | -0.00058594 | -0.017854 | 0.12849 | -0.024001 | 0.040239 | 0.050941 | 0.0067021 | -0.015058 | 102.6627 | -20.2148 | -0.17853 | -20.4437 | 102.8458 | -20.2744 | -20.3705 | -20.2972 | 0.12817 | -20.0912 | 102.8549 | 102.713 | -20.3247 | -20.4025 | -0.036621 | -0.13275 | 0.09613 | 0.022888 | -0.20599 | -0.073243 | -0.086975 | -0.086975 | -0.16479 | 0.10528 | -0.059509 | 0.14648 | 0.31128 | -0.036621 | 123.0835 | 122.9004 | 20.0592 | -123.1201 | 123.0927 | 122.9507 | 20.3659 | -123.1522
883.6406 | 123.2437 | -20.1965 | 102.7863 | -0.89675 | -0.00037681 | 0.078445 | 0.0093408 | 0.048056 | -0.0059269 | -0.01999 | -0.32927 | -0.037886 | 0.045579 | 0.055213 | 0.016315 | -0.032148 | 102.6535 | -20.1462 | -0.1236 | -20.4117 | 102.8778 | -20.2927 | -20.343 | -20.2744 | 0.16022 | -20.0958 | 102.8961 | 102.7542 | -20.2972 | -20.3705 | -0.096131 | -0.14649 | 0.091553 | 0.050354 | -0.21515 | -0.068664 | -0.13275 | -0.10071 | -0.17395 | 0.10986 | -0.07782 | 0.10071 | 0.27466 | -0.032044 | 123.0743 | 122.85 | 20.0729 | -123.1293 | 123.0927 | 122.9507 | 20.3567 | -123.1567
884.6406 | 123.1888 | -20.1782 | 102.7954 | 4.9626 | 0.017781 | 0.092331 | 0.029635 | 0.039511 | -0.0059269 | -0.031739 | -0.17668 | -0.026137 | 0.032762 | 0.044532 | 0.023792 | -0.030012 | 102.7176 | -20.2011 | -0.16937 | -20.4163 | 102.8778 | -20.2515 | -20.3247 | -20.2377 | 0.17853 | -20.05 | 102.951 | 102.7954 | -20.2789 | -20.3476 | -0.073242 | -0.14648 | 0.082398 | -0.022888 | -0.23804 | -0.091553 | -0.07782 | -0.10071 | -0.16937 | 0.15564 | -0.059509 | 0.12817 | 0.29755 | 0 | 123.056 | 122.8958 | 20.0088 | -123.1201 | 123.1293 | 122.9736 | 20.3568 | -123.143
885.6406 | 123.1705 | -19.8898 | 103.0609 | 4.1692 | 0.0081682 | 0.084854 | 0.011477 | 0.048056 | -0.01554 | -0.017854 | -0.19194 | -0.021865 | 0.053056 | 0.047736 | 0.017383 | -0.032148 | 102.9785 | -19.9036 | -0.13275 | -20.1096 | 103.1799 | -19.9722 | -20.0546 | -19.986 | 0.17853 | -19.7937 | 103.1891 | 103.0334 | -20.0363 | -20.0821 | -0.082397 | -0.16479 | 0.11902 | -0.013732 | -0.21973 | -0.054932 | -0.082397 | -0.14648 | -0.19226 | 0.12817 | -0.09613 | 0.096131 | 0.28839 | -0.027466 | 123.0698 | 122.8683 | 19.7571 | -123.1155 | 123.0789 | 122.9233 | 20.0684 | -123.143
886.6406 | 123.2117 | -20.0775 | 102.9007 | -1.0646 | -0.0078538 | 0.078445 | 0.028567 | 0.042716 | -0.0037909 | -0.022126 | -0.34453 | -0.025069 | 0.05092 | 0.043464 | 0.020587 | -0.028944 | 102.7725 | -20.0088 | -0.13733 | -20.2744 | 103.0014 | -20.1279 | -20.2148 | -20.1599 | 0.17395 | -19.9539 | 103.038 | 102.8778 | -20.2057 | -20.2332 | -0.050354 | -0.13733 | 0.10071 | 0.068665 | -0.19684 | -0.059509 | -0.12817 | -0.12817 | -0.15564 | 0.13733 | -0.082397 | 0.1236 | 0.27924 | -0.022888 | 123.0789 | 122.85 | 19.9402 | -123.1155 | 123.1155 | 122.9553 | 20.2515 | -123.1338
887.6406 | 123.2117 | -19.6335 | 103.3859 | 0.7512 | 0.010304 | 0.079513 | 0.024295 | 0.051261 | -0.0080629 | -0.01465 | -0.23772 | -0.024001 | 0.032762 | 0.017829 | 0.012042 | -0.022535 | 103.2806 | -19.6014 | -0.14191 | -19.8395 | 103.4637 | -19.6838 | -19.7937 | -19.7296 | 0.17395 | -19.5145 | 103.4821 | 103.2852 | -19.7479 | -19.8029 | -0.050354 | -0.16022 | 0.07782 | 0.032044 | -0.20599 | -0.045777 | -0.10528 | -0.11444 | -0.16937 | 0.096131 | -0.09613 | 0.11902 | 0.28839 | -0.10071 | 123.0972 | 122.9141 | 19.4916 | -123.1796 | 123.1155 | 122.9187 | 19.8074 | -123.1888
888.6406 | 123.2162 | -19.5053 | 103.4683 | -0.10329 | 0.0017592 | 0.072037 | 0.023226 | 0.052329 | -0.00058594 | -0.024263 | -0.2072 | -0.028273 | 0.049852 | 0.039191 | 0.0077701 | -0.030012 | 103.3722 | -19.4687 | -0.10986 | -19.7342 | 103.537 | -19.6106 | -19.6747 | -19.6014 | 0.21515 | -19.3863 | 103.5599 | 103.4042 | -19.6655 | -19.6747 | -0.10529 | -0.16937 | 0.068664 | 0.036621 | -0.22888 | -0.059509 | -0.096131 | -0.16022 | -0.16937 | 0.091552 | -0.09613 | 0.11902 | 0.28839 | -0.064087 | 123.0423 | 122.8775 | 19.3954 | -123.143 | 123.0652 | 122.9095 | 19.7205 | -123.143
889.6406 | 123.3582 | -19.2261 | 103.7521 | 0.018779 | 0.00069119 | 0.083786 | 0.029635 | 0.044852 | -0.0069949 | -0.022126 | -0.23772 | -0.03575 | 0.057328 | 0.032783 | 0.018451 | -0.023603 | 103.6789 | -19.1757 | -0.11902 | -19.4138 | 103.8254 | -19.2947 | -19.3817 | -19.2764 | 0.23804 | -19.0521 | 103.8849 | 103.6926 | -19.3314 | -19.3954 | -0.068665 | -0.15564 | 0.073242 | 0.050354 | -0.18768 | -0.032043 | -0.073242 | -0.10529 | -0.16937 | 0.13275 | -0.050354 | 0.17395 | 0.34332 | -0.059509 | 123.0515 | 122.905 | 19.1071 | -123.1338 | 123.111 | 122.9187 | 19.4641 | -123.1476
890.6406 | 123.1247 | -19.2673 | 103.775 | -0.2864 | 0.017781 | 0.078445 | 0.023226 | 0.054465 | 0.0068901 | -0.011445 | -0.22246 | -0.029341 | 0.030626 | 0.024238 | 0.016315 | -0.027876 | 103.5965 | -19.281 | -0.20142 | -19.4824 | 103.8666 | -19.3176 | -19.4138 | -19.4046 | 0.09613 | -19.2123 | 103.8986 | 103.7292 | -19.4138 | -19.4229 | -0.050354 | -0.14648 | 0.091553 | -0.013733 | -0.21515 | -0.068665 | -0.17853 | -0.14648 | -0.15564 | 0.1236 | -0.13733 | 0.054932 | 0.21057 | -0.045776 | 123.1339 | 122.8638 | 19.0659 | -123.1888 | 123.1659 | 122.9965 | 19.3634 | -123.1979
891.6406 | 123.1338 | -17.894 | 105.162 | -0.19484 | 0.00069119 | 0.073105 | 0.027499 | 0.053397 | 0.0058221 | -0.022126 | -0.37505 | -0.021865 | 0.046647 | 0.0456 | 0.026996 | -0.021467 | 105.0064 | -17.8574 | -0.21973 | -18.0725 | 105.2902 | -17.9077 | -17.9718 | -17.9855 | 0.12817 | -17.807 | 105.3131 | 105.162 | -17.9855 | -18.045 | -0.013733 | -0.07782 | 0.12817 | 0.036621 | -0.17853 | -0.10071 | -0.15564 | -0.091553 | -0.15106 | 0.15106 | -0.091553 | 0.086975 | 0.23804 | 0 | 123.1842 | 122.9004 | 17.6743 | -123.1338 | 123.2071 | 123.056 | 18.0222 | -123.2071
892.6406 | 123.0972 | -17.5781 | 105.4642 | -0.25588 | 0.0092362 | 0.076309 | 0.026431 | 0.050193 | 0.0079581 | -0.022126 | -0.34453 | -0.014388 | 0.027421 | 0.039191 | 0.020587 | -0.027876 | 105.3268 | -17.5461 | -0.15564 | -17.7383 | 105.5969 | -17.601 | -17.6651 | -17.6834 | 0.13733 | -17.4545 | 105.6015 | 105.4321 | -17.6697 | -17.72 | -0.022888 | -0.086975 | 0.13275 | 0.032043 | -0.16022 | -0.073242 | -0.13733 | -0.091553 | -0.14191 | 0.13733 | -0.10529 | 0.1236 | 0.2655 | -0.032043 | 123.175 | 122.905 | 17.4225 | -123.1293 | 123.1796 | 123.0103 | 17.7155 | -123.1842
893.6406 | 123.0698 | -17.8665 | 105.2216 | -0.30166 | 0.031666 | 0.072037 | 0.029635 | 0.048056 | -0.0037909 | -0.028535 | -0.32927 | -0.021865 | 0.058397 | 0.041327 | 0.010974 | -0.030012 | 105.0201 | -17.8528 | -0.16937 | -18.0313 | 105.3131 | -17.9031 | -17.9764 | -17.9764 | 0.14191 | -17.7383 | 105.336 | 105.1804 | -17.9489 | -17.9993 | -0.036621 | -0.10986 | 0.091552 | 0.013733 | -0.16479 | -0.054932 | -0.20142 | -0.082398 | -0.13275 | 0.11444 | -0.10986 | 0.12817 | 0.26093 | -0.041199 | 123.1796 | 122.8867 | 17.6971 | -123.1979 | 123.2025 | 123.0469 | 18.0084 | -123.2208
894.6406 | 123.1064 | -17.3218 | 105.7205 | -0.27114 | 0.022053 | 0.070968 | 0.024295 | 0.050193 | 0.00048206 | -0.011445 | -0.34453 | -0.015456 | 0.05092 | 0.02851 | 0.012042 | -0.024671 | 105.5237 | -17.3492 | -0.16937 | -17.5186 | 105.78 | -17.3904 | -17.4866 | -17.4316 | 0.17395 | -17.1661 | 105.867 | 105.6839 | -17.4316 | -17.4774 | -0.068665 | -0.16479 | 0.059509 | -0.027466 | -0.19684 | -0.032044 | -0.19684 | -0.10986 | -0.15564 | 0.14648 | -0.10986 | 0.15564 | 0.31128 | -0.036621 | 123.1018 | 122.8455 | 17.1524 | -123.2071 | 123.1888 | 123.0057 | 17.4957 | -123.1979
895.6406 | 123.1155 | -17.5186 | 105.5145 | -0.22536 | 0.015645 | 0.075241 | 0.027499 | 0.049125 | -0.0059269 | -0.010377 | -0.35979 | -0.038954 | 0.042375 | 0.030646 | 0.0034971 | -0.026808 | 105.2811 | -17.5873 | -0.24261 | -17.8024 | 105.5557 | -17.6331 | -17.7155 | -17.6651 | 0.17395 | -17.3813 | 105.6473 | 105.5008 | -17.6514 | -17.6697 | -0.11444 | -0.19684 | 0.041199 | -0.068664 | -0.28381 | -0.086975 | -0.23346 | -0.13275 | -0.15106 | 0.13275 | -0.14648 | 0.13733 | 0.28839 | -0.013733 | 123.0743 | 122.7997 | 17.276 | -123.23 | 123.1659 | 123.0194 | 17.6926 | -123.1842
896.6406 | 123.1064 | -17.3172 | 105.7205 | -0.22536 | 0.018849 | 0.08165 | 0.028567 | 0.069419 | 0.0015501 | -0.01465 | -0.35979 | -0.021865 | 0.055192 | 0.040259 | 0.016315 | -0.028944 | 105.5237 | -17.3218 | -0.19226 | -17.5369 | 105.8212 | -17.3859 | -17.4728 | -17.4271 | 0.19684 | -17.1707 | 105.867 | 105.7114 | -17.4225 | -17.4774 | -0.068664 | -0.15564 | 0.10071 | -0.004577 | -0.21973 | -0.064087 | -0.19684 | -0.10529 | -0.16022 | 0.14648 | -0.10986 | 0.14648 | 0.3067 | -0.009155 | 123.1384 | 122.8409 | 17.1249 | -123.1934 | 123.1842 | 123.0286 | 17.514 | -123.1979
897.6875 | 123.2071 | -17.1661 | 105.8533 | 0.21714 | 0.027394 | 0.083786 | 0.01575 | 0.044852 | -0.013404 | -0.023195 | 0.43367 | -0.021865 | 0.055192 | 0.052009 | 0.0088381 | -0.028944 | 105.6152 | -17.1066 | -0.16937 | -17.3538 | 105.954 | -17.1936 | -17.2897 | -17.2119 | 0.17395 | -16.9647 | 105.9723 | 105.8258 | -17.2394 | -17.2714 | -0.027466 | -0.1236 | 0.10071 | 0.05951 | -0.18768 | -0.064087 | -0.23804 | -0.073242 | -0.10528 | 0.11902 | -0.045776 | 0.20142 | 0.3067 | -0.027465 | 123.1201 | 122.7814 | 16.9968 | -123.143 | 123.1384 | 122.9919 | 17.3401 | -123.1247
898.6406 | 123.0835 | -18.9651 | 104.0955 | -0.22536 | 0.018849 | 0.070968 | 0.045657 | 0.060874 | 0.0090271 | -0.01465 | -0.43608 | -0.026137 | 0.042375 | 0.043464 | 0.014179 | -0.038557 | 103.7842 | -19.1116 | -0.3067 | -19.2764 | 104.1092 | -19.1025 | -19.1849 | -19.1071 | 0.13733 | -18.9148 | 104.2053 | 104.068 | -19.0842 | -19.0933 | -0.13733 | -0.21973 | 0.013733 | -0.14648 | -0.31128 | -0.091553 | -0.31128 | -0.11902 | -0.12817 | 0.10986 | -0.14191 | 0.050354 | 0.17853 | -0.027466 | 123.0743 | 122.7493 | 18.6584 | -123.2803 | 123.1705 | 123.0331 | 19.1025 | -123.1888
899.6406 | 123.1659 | -18.5028 | 104.5578 | -0.22536 | 0.01244 | 0.075241 | 0.029635 | 0.042716 | 0.013299 | -0.01465 | -0.37505 | -0.019728 | 0.049852 | 0.047736 | 0.0099061 | -0.032148 | 104.3793 | -18.5211 | -0.25177 | -18.6951 | 104.6997 | -18.5028 | -18.5852 | -18.6539 | 0.082397 | -18.3701 | 104.7043 | 104.5715 | -18.576 | -18.6081 | 0 | -0.082397 | 0.14191 | -0.01831 | -0.19226 | -0.10986 | -0.17853 | -0.073242 | -0.10528 | 0.14648 | -0.15106 | 0.13275 | 0.23804 | 0.013733 | 123.2025 | 122.8821 | 18.251 | -123.143 | 123.2071 | 123.0743 | 18.5852 | -123.1659
900.6406 | 123.0789 | -18.4891 | 104.5624 | -0.27114 | 0.011372 | 0.084854 | 0.01575 | 0.058738 | 0.0068901 | -0.028535 | -0.42082 | -0.01866 | 0.053056 | 0.040259 | 0.0067021 | -0.032148 | 104.2877 | -18.5898 | -0.25177 | -18.7683 | 104.6127 | -18.6127 | -18.6859 | -18.6493 | 0.27924 | -18.1915 | 104.7409 | 104.5898 | -18.5852 | -18.6264 | -0.1236 | -0.19684 | 0.050354 | -0.10071 | -0.27924 | -0.082398 | -0.27466 | -0.09613 | -0.13733 | 0.17853 | -0.16022 | 0.29755 | 0.43488 | 0.027466 | 123.1018 | 122.7768 | 18.2373 | -123.2483 | 123.23 | 123.0789 | 18.7683 | -123.1888
901.6406 | 123.056 | -17.9672 | 105.1163 | -0.25588 | -0.00037681 | 0.074173 | 0.028567 | 0.044852 | -0.0048589 | -0.022126 | -0.37505 | -0.024001 | 0.051988 | 0.034919 | 0.016315 | -0.025739 | 104.8599 | -18.0038 | -0.27008 | -18.1824 | 105.2124 | -18.013 | -18.1046 | -18.0817 | 0.45319 | -17.8665 | 105.2719 | 105.098 | -18.013 | -18.0908 | -0.045776 | -0.13733 | 0.09613 | -0.036621 | -0.21515 | -0.07782 | -0.25635 | -0.045776 | -0.1236 | 0.15564 | -0.11444 | 0.10071 | 0.2243 | -0.018311 | 123.1796 | 122.8271 | 17.6971 | -123.2208 | 123.2391 | 123.0652 | 18.4204 | -123.2071
902.6406 | 123.1201 | -18.631 | 104.4067 | -0.25588 | 0.015645 | 0.065628 | 0.030703 | 0.046988 | -0.0069949 | -0.01999 | -0.11565 | -0.026137 | 0.043443 | 0.046668 | 0.016315 | -0.022535 | 104.2419 | -18.5944 | -0.24261 | -18.8141 | 104.5303 | -18.6447 | -18.7225 | -18.7637 | 0.16479 | -18.5165 | 104.5853 | 104.4434 | -18.6951 | -18.7775 | -0.013733 | -0.091553 | 0.1236 | 0.036621 | -0.18311 | -0.091553 | -0.16479 | -0.064087 | -0.14649 | 0.17853 | -0.13275 | 0.11444 | 0.26093 | 0.036621 | 123.1613 | 122.8729 | 18.3884 | -123.1293 | 123.2162 | 123.0743 | 18.7958 | -123.1842
903.6406 | 123.1338 | -19.2307 | 103.8254 | -0.39321 | 0.020985 | 0.079513 | 0.02109 | 0.052329 | 0.0015501 | -0.021058 | -0.32927 | -0.024001 | 0.06801 | 0.037055 | -0.0061159 | -0.018263 | 103.5828 | -19.313 | -0.31586 | -19.4687 | 103.9078 | -19.2947 | -19.3726 | -19.249 | -0.15564 | -19.194 | 103.9856 | 103.7933 | -19.3451 | -19.4 | -0.064087 | -0.14191 | 0.082398 | -0.082397 | -0.23804 | -0.09613 | -0.24261 | -0.11444 | -0.16937 | 0.16022 | -0.01831 | 0.036621 | 0.20599 | -0.032043 | 123.1384 | 122.8134 | 18.9148 | -123.1979 | 123.2162 | 123.024 | 19.075 | -123.2254
904.6406 | 123.111 | -18.8324 | 104.2145 | -0.19484 | 0.032734 | 0.08699 | 0.02109 | 0.049125 | 0.012231 | -0.01465 | -0.35979 | -0.019728 | 0.048783 | 0.040259 | 0.018451 | -0.025739 | 103.9856 | -18.9285 | -0.35248 | -19.0979 | 104.2969 | -18.9056 | -18.9972 | -18.9285 | 0.16022 | -18.718 | 104.3701 | 104.2236 | -18.9194 | -18.9651 | -0.073243 | -0.16479 | 0.082397 | -0.096131 | -0.2655 | -0.10071 | -0.22888 | -0.086976 | -0.13275 | 0.15564 | -0.096131 | 0.11444 | 0.24719 | 0.009155 | 123.1293 | 122.818 | 18.4799 | -123.2117 | 123.2025 | 123.056 | 18.9926 | -123.1796
905.6406 | 123.1384 | -18.7363 | 104.3198 | -0.17959 | 0.032734 | 0.06456 | 0.03284 | 0.054465 | 0.0058221 | -0.0082413 | -0.32927 | -0.015456 | 0.064805 | 0.063758 | 0.021655 | -0.027876 | 104.1595 | -18.7546 | -0.31586 | -18.9148 | 104.4571 | -18.7592 | -18.8507 | -18.8507 | 0.14191 | -18.6447 | 104.4342 | 104.3106 | -18.8507 | -18.8919 | -0.022888 | -0.11444 | 0.13733 | -0.018311 | -0.17853 | -0.064087 | -0.16022 | -0.11444 | -0.15564 | 0.11444 | -0.11444 | 0.091553 | 0.24719 | -0.009155 | 123.1934 | 122.8958 | 18.4204 | -123.1705 | 123.1705 | 123.0469 | 18.8782 | -123.2117
906.6406 | 123.2025 | -18.8782 | 104.1229 | 0.46128 | 0.0038952 | 0.083786 | 0.020022 | 0.036307 | -0.018744 | -0.025331 | 0.35738 | -0.031478 | 0.041307 | 0.046668 | 0.014179 | -0.017194 | 104.0176 | -18.8507 | -0.3479 | -19.043 | 104.3015 | -18.837 | -18.9285 | -18.9697 | 0.032043 | -18.7729 | 104.2328 | 104.1321 | -18.9835 | -19.0338 | 0.041199 | -0.050354 | 0.17853 | 0.027466 | -0.16479 | -0.11444 | -0.10529 | -0.10528 | -0.15564 | 0.10986 | -0.091553 | 0.10529 | 0.26093 | 0.009155 | 123.1796 | 122.8958 | 18.5303 | -123.0515 | 123.111 | 123.0103 | 18.9102 | -123.1567
907.6406 | 123.1155 | -19.1483 | 103.8483 | -0.16433 | 0.034871 | 0.0699 | 0.040316 | 0.058738 | 0.017572 | -0.012513 | -0.23772 | -0.011183 | 0.051988 | 0.039191 | 0.022724 | -0.03108 | 103.656 | -19.2947 | -0.3067 | -19.3817 | 103.9627 | -19.2352 | -19.313 | -19.2856 | 0.16479 | -19.0384 | 103.9948 | 103.8757 | -19.249 | -19.313 | -0.086975 | -0.16479 | 0.11444 | -0.14648 | -0.23346 | -0.068665 | -0.19226 | -0.10071 | -0.16479 | 0.14648 | -0.13733 | 0.10986 | 0.27466 | 0.027465 | 123.111 | 122.8043 | 18.8416 | -123.1613 | 123.143 | 123.024 | 19.313 | -123.1613
908.6406 | 123.1293 | -19.0567 | 103.9856 | -0.16433 | 0.041279 | 0.066696 | 0.02109 | 0.042716 | 0.01864 | -0.012513 | -0.13091 | -0.026137 | 0.054124 | 0.046668 | 0.017383 | -0.028944 | 103.8986 | -19.0338 | -0.27008 | -19.1757 | 104.1458 | -19.0475 | -19.1254 | -19.1391 | 0.10071 | -18.9697 | 104.1321 | 103.9856 | -19.1574 | -19.2123 | 0.009156 | -0.068664 | 0.16022 | 0.022889 | -0.11902 | -0.050354 | -0.086975 | -0.10071 | -0.15564 | 0.14648 | -0.082397 | 0.086975 | 0.24261 | 0 | 123.2025 | 122.9553 | 18.7866 | -123.111 | 123.1888 | 123.0423 | 19.1574 | -123.1979
909.6406 | 123.1567 | -18.9697 | 104.0771 | -0.13381 | 0.057301 | 0.0699 | 0.036044 | 0.052329 | 0.012231 | -0.0093093 | -0.11565 | -0.020796 | 0.048783 | 0.035987 | 0.021655 | -0.023603 | 103.8803 | -19.0521 | -0.33417 | -19.2078 | 104.155 | -19.043 | -19.1483 | -19.0796 | 0.16479 | -18.8507 | 104.1962 | 104.0726 | -19.0887 | -19.1254 | -0.073242 | -0.17853 | 0.07782 | -0.082397 | -0.23804 | -0.05951 | -0.19684 | -0.11902 | -0.15564 | 0.11902 | -0.10986 | 0.11902 | 0.27466 | -0.004577 | 123.1247 | 122.85 | 18.6356 | -123.2254 | 123.1659 | 123.0423 | 19.1345 | -123.2025
910.6406 | 123.1613 | -19.4595 | 103.5828 | -0.10329 | 0.039143 | 0.070968 | 0.036044 | 0.048056 | 0.014367 | -0.011445 | -0.25298 | -0.022933 | 0.072282 | 0.037055 | 0.010974 | -0.024671 | 103.4454 | -19.5282 | -0.43488 | -19.7296 | 103.6697 | -19.5419 | -19.6152 | -19.5007 | 0.14648 | -19.3314 | 103.7567 | 103.6102 | -19.5374 | -19.5923 | -0.082397 | -0.15564 | 0.086975 | -0.068664 | -0.27008 | -0.11444 | -0.13733 | -0.07782 | -0.13275 | 0.17395 | -0.041198 | 0.12817 | 0.26093 | 0.027465 | 123.1293 | 122.905 | 19.0247 | -123.1979 | 123.2162 | 123.0698 | 19.606 | -123.175
911.6406 | 123.2437 | -19.1895 | 103.7796 | 0.52232 | 0.026326 | 0.068832 | 0.031771 | 0.04058 | -0.0027229 | -0.012513 | 0.2353 | -0.020796 | 0.05092 | 0.0456 | 0.029132 | -0.016126 | 103.6652 | -19.2444 | -0.37994 | -19.4138 | 103.8849 | -19.2352 | -19.3359 | -19.3268 | 0.11902 | -19.0384 | 103.8895 | 103.8071 | -19.3085 | -19.3359 | -0.045776 | -0.14648 | 0.10529 | -0.054932 | -0.2243 | -0.07782 | -0.11444 | -0.11902 | -0.14648 | 0.10986 | -0.13733 | 0.15106 | 0.29755 | 0.027466 | 123.0743 | 122.8546 | 18.8095 | -123.1155 | 123.0789 | 122.9965 | 19.3085 | -123.1155
912.6406 | 123.1018 | -19.3863 | 103.6194 | 0.079814 | 0.035939 | 0.060287 | 0.034976 | 0.04058 | 0.0058221 | -0.017854 | 0.097976 | -0.011183 | 0.060533 | 0.037055 | 0.019519 | -0.026808 | 103.5553 | -19.4046 | -0.35706 | -19.5786 | 103.7933 | -19.3954 | -19.4916 | -19.5374 | 0.018311 | -19.3314 | 103.775 | 103.6743 | -19.4962 | -19.5419 | -0.009155 | -0.10528 | 0.17395 | -0.01831 | -0.19226 | -0.086975 | -0.064087 | -0.10986 | -0.15564 | 0.15564 | -0.15106 | 0.054932 | 0.21057 | 0.054931 | 123.1796 | 122.9416 | 19.0292 | -123.111 | 123.1613 | 123.0606 | 19.4046 | -123.1613
913.6406 | 123.1064 | -19.0109 | 103.981 | 0.26292 | 0.047688 | 0.077377 | 0.036044 | 0.036307 | 0.010095 | -0.015718 | 0.15901 | -0.0079794 | 0.061601 | 0.046668 | 0.025928 | -0.017194 | 103.8574 | -19.0887 | -0.40283 | -19.2581 | 104.1138 | -19.0704 | -19.1483 | -19.1437 | 0.091553 | -18.9148 | 104.1733 | 104.0955 | -19.1116 | -19.1483 | -0.05951 | -0.13733 | 0.13275 | -0.07782 | -0.24719 | -0.10986 | -0.1236 | -0.10071 | -0.13733 | 0.19226 | -0.13275 | 0.09613 | 0.23346 | 0.11444 | 123.1247 | 122.8683 | 18.6081 | -123.1293 | 123.1842 | 123.1064 | 19.1025 | -123.1293
914.6406 | 123.0881 | -18.9468 | 104.0863 | 0.3087 | 0.04662 | 0.070968 | 0.028567 | 0.043784 | 0.0068901 | -0.018922 | 0.082718 | -0.010115 | 0.051988 | 0.046668 | 0.021655 | -0.018263 | 103.8803 | -19.0384 | -0.37994 | -19.1849 | 104.1687 | -19.0018 | -19.1162 | -19.1757 | 0.022888 | -18.9285 | 104.1824 | 104.0955 | -19.1116 | -19.1116 | -0.054932 | -0.16937 | 0.082397 | -0.091553 | -0.23804 | -0.068664 | -0.20599 | -0.1648 | -0.1648 | 0.09613 | -0.22888 | 0.01831 | 0.18311 | 0.009155 | 123.1155 | 122.8271 | 18.5669 | -123.2025 | 123.1293 | 123.0423 | 18.9697 | -123.1979
915.6406 | 123.1293 | -19.194 | 103.8162 | 0.3087 | 0.049824 | 0.058151 | 0.03818 | 0.057669 | 0.010095 | -0.0082413 | -0.024094 | -0.01866 | 0.046647 | 0.043464 | 0.023792 | -0.019331 | 103.6789 | -19.2398 | -0.41199 | -19.4595 | 103.8757 | -19.3039 | -19.3405 | -19.2764 | 0.10529 | -19.0979 | 103.9948 | 103.9169 | -19.2673 | -19.3405 | -0.10986 | -0.14648 | 0.059509 | -0.045776 | -0.2655 | -0.11902 | -0.13733 | -0.073242 | -0.14648 | 0.17853 | -0.082397 | 0.096131 | 0.24262 | 0.10071 | 123.0698 | 122.8729 | 18.782 | -123.1567 | 123.1888 | 123.111 | 19.2993 | -123.1567
916.6406 | 123.2208 | -19.1299 | 103.8254 | -0.011739 | 0.0060322 | -0.22063 | 0.018954 | 0.037375 | -0.041175 | -0.039216 | 0.25056 | -0.028273 | 0.037034 | 0.038123 | 0.0045661 | -0.006513 | 103.7064 | -19.1391 | -0.29755 | -19.3726 | 103.9124 | -19.1986 | -19.2856 | -19.194 | 0.23346 | -18.9514 | 103.9581 | 103.8712 | -19.2398 | -19.2764 | -0.068664 | -0.15564 | 0.086976 | -0.009155 | -0.24262 | -0.086976 | -0.11902 | -0.10986 | -0.14648 | 0.13275 | -0.064087 | 0.17853 | 0.32501 | 0.045777 | 123.0423 | 122.8363 | 18.8324 | -123.111 | 123.0881 | 123.0011 | 19.3634 | -123.1018
917.6406 | 123.1247 | -18.663 | 104.361 | 0.55284 | 0.062642 | 0.059219 | 0.043521 | 0.060874 | 0.015435 | -0.016786 | 0.17427 | -0.010115 | 0.051988 | 0.038123 | 0.022724 | -0.027876 | 104.1092 | -18.663 | -0.41199 | -18.956 | 104.4846 | -18.7134 | -18.8141 | -18.8004 | -0.009155 | -18.6264 | 104.48 | 104.3793 | -18.782 | -18.8004 | -0.050354 | -0.15106 | 0.1236 | 0 | -0.29297 | -0.14191 | -0.25177 | -0.11902 | -0.13733 | 0.11902 | -0.13733 | 0.036621 | 0.17395 | 0.01831 | 123.1476 | 122.7722 | 18.251 | -123.175 | 123.143 | 123.0423 | 18.6539 | -123.1613
918.6406 | 123.1476 | -18.782 | 104.2236 | 0.58335 | 0.037007 | 0.075241 | 0.042453 | 0.034171 | 0.0036861 | -0.022126 | 0.41841 | -0.01332 | 0.042375 | 0.041327 | 0.0077701 | -0.018263 | 104.0268 | -18.837 | -0.45776 | -19.0567 | 104.3152 | -18.8461 | -18.924 | -18.9285 | 0.018311 | -18.718 | 104.3701 | 104.2877 | -18.8965 | -18.9056 | -0.064087 | -0.14191 | 0.091553 | -0.054932 | -0.27466 | -0.13275 | -0.19684 | -0.11444 | -0.1236 | 0.14648 | -0.14648 | 0.064086 | 0.18768 | 0.064087 | 123.0972 | 122.8088 | 18.3243 | -123.1476 | 123.1522 | 123.0698 | 18.8004 | -123.1293
919.6406 | 123.1384 | -18.6905 | 104.306 | 0.44602 | 0.040211 | 0.078445 | 0.039248 | 0.044852 | 0.010095 | -0.029603 | 0.43367 | -0.0058434 | 0.041307 | 0.054145 | 0.017383 | -0.012922 | 104.1367 | -18.7363 | -0.4303 | -18.9789 | 104.4159 | -18.7637 | -18.8461 | -18.782 | 0.045776 | -18.6081 | 104.4525 | 104.3655 | -18.7958 | -18.837 | -0.073242 | -0.15564 | 0.10986 | -0.045776 | -0.28839 | -0.13275 | -0.16937 | -0.10528 | -0.14648 | 0.14648 | -0.091552 | 0.082398 | 0.22888 | 0.05951 | 123.1064 | 122.8271 | 18.2602 | -123.1522 | 123.143 | 123.056 | 18.7363 | -123.143
920.6406 | 123.1659 | -18.8187 | 104.1641 | 0.47654 | 0.033803 | 0.063492 | 0.03818 | 0.059806 | 0.0058221 | -0.017854 | 0.47945 | -0.0037074 | 0.037034 | 0.050941 | 0.016315 | -0.034284 | 104.0131 | -18.8507 | -0.41657 | -19.0659 | 104.2877 | -18.8736 | -18.9606 | -18.9148 | 0.059509 | -18.6676 | 104.3198 | 104.2557 | -18.9102 | -18.9651 | -0.054931 | -0.14191 | 0.1236 | -0.032043 | -0.24719 | -0.10529 | -0.15106 | -0.091552 | -0.14648 | 0.15564 | -0.09613 | 0.15106 | 0.29755 | 0.091552 | 123.1064 | 122.8317 | 18.4021 | -123.1247 | 123.1384 | 123.0743 | 18.8782 | -123.1293
921.6406 | 123.1567 | -18.8004 | 104.1962 | 0.3087 | 0.015645 | 0.082718 | 0.01575 | 0.041648 | -0.024085 | -0.01999 | 0.38789 | -0.0058434 | 0.013536 | 0.032783 | 0.010974 | -0.028944 | 104.0955 | -18.7408 | -0.33875 | -18.9606 | 104.3335 | -18.782 | -18.869 | -18.8828 | -0.013733 | -18.663 | 104.3015 | 104.2419 | -18.9011 | -18.9468 | 0.018311 | -0.068665 | 0.13733 | 0.059509 | -0.16022 | -0.091552 | -0.10071 | -0.10071 | -0.14648 | 0.10529 | -0.082397 | 0.13733 | 0.28381 | 0.045776 | 123.1338 | 122.8958 | 18.4616 | -123.0652 | 123.1018 | 123.0423 | 18.7866 | -123.143
922.6406 | 123.2162 | -18.6081 | 104.3427 | 0.56809 | 0.04662 | 0.077377 | 0.026431 | 0.057669 | 0.0015501 | -0.023195 | 0.35738 | -0.0026384 | 0.021012 | 0.037055 | 0.031268 | -0.019331 | 104.2877 | -18.631 | -0.37079 | -18.837 | 104.4846 | -18.6447 | -18.7363 | -18.6951 | 0.10986 | -18.4891 | 104.4891 | 104.4022 | -18.7454 | -18.7637 | -0.036621 | -0.12817 | 0.14191 | -0.022888 | -0.22888 | -0.10071 | -0.054931 | -0.13733 | -0.15564 | 0.14648 | -0.086975 | 0.11902 | 0.27466 | 0.05951 | 123.0927 | 122.8958 | 18.2373 | -123.0789 | 123.0972 | 123.0103 | 18.718 | -123.1064
923.6406 | 123.2025 | -18.0679 | 104.8828 | 0.61387 | 0.031666 | 0.070968 | 0.039248 | 0.036307 | 0.00048206 | -0.024263 | 0.66255 | 0.0048376 | 0.030626 | 0.044532 | 0.016315 | -0.021467 | 104.805 | -18.0908 | -0.31586 | -18.2968 | 104.9973 | -18.1458 | -18.2236 | -18.1229 | 0.1831 | -17.8986 | 105.0385 | 104.9744 | -18.1686 | -18.2098 | -0.07782 | -0.15564 | 0.11444 | -0.022888 | -0.22888 | -0.073242 | -0.077819 | -0.10071 | -0.14191 | 0.15564 | -0.054932 | 0.16937 | 0.31128 | 0.091553 | 123.0652 | 122.8729 | 17.7521 | -123.1064 | 123.1064 | 123.0423 | 18.251 | -123.0927
924.6406 | 123.2162 | -18.6172 | 104.3518 | 0.55284 | 0.02953 | 0.083786 | 0.030703 | 0.055533 | -0.0027229 | -0.038148 | 0.60152 | 0.0080426 | 0.024217 | 0.0456 | 0.020587 | -0.021467 | 104.425 | -18.6996 | -0.33875 | -18.837 | 104.3976 | -18.6996 | -18.7729 | -18.6676 | 0.21057 | -18.4753 | 104.4846 | 104.4113 | -18.7363 | -18.7729 | -0.082397 | -0.15564 | 0.045776 | -0.082397 | -0.21973 | -0.064087 | 0.073242 | -0.11902 | -0.15564 | 0.13275 | -0.050354 | 0.14191 | 0.29755 | 0.059509 | 123.0148 | 123.0423 | 18.2785 | -123.1247 | 123.1018 | 123.0286 | 18.8278 | -123.1247
925.6406 | 123.1796 | -18.3609 | 104.6082 | 2.4907 | 0.0081682 | 0.090195 | 0.020022 | 0.044852 | -0.0016549 | -0.030671 | 0.55574 | -0.00050244 | 0.018876 | 0.044532 | 0.0099061 | -0.020399 | 104.5441 | -18.3655 | -0.3067 | -18.5623 | 104.686 | -18.4204 | -18.4891 | -18.4067 | 0.19226 | -18.1961 | 104.7318 | 104.6402 | -18.4891 | -18.5165 | -0.059509 | -0.12817 | 0.07782 | -0.004578 | -0.20142 | -0.073242 | -0.064087 | -0.12817 | -0.15564 | 0.1236 | -0.045776 | 0.16479 | 0.32043 | 0.032044 | 123.0469 | 122.905 | 18.0542 | -123.0972 | 123.0927 | 123.0011 | 18.5532 | -123.1247
926.6406 | 123.175 | -18.4158 | 104.6036 | -0.14907 | 0.033803 | 0.062424 | 0.040316 | 0.052329 | 0.01864 | -0.018922 | -0.31401 | -0.0015704 | 0.024217 | 0.040259 | 0.022724 | -0.035352 | 104.512 | -18.4341 | -0.33875 | -18.5852 | 104.7775 | -18.4616 | -18.5349 | -18.4982 | 0.25177 | -18.2968 | 104.7729 | 104.6768 | -18.5028 | -18.5349 | -0.045776 | -0.11902 | 0.17395 | -0.01831 | -0.16937 | -0.050354 | -0.091553 | -0.086975 | -0.11902 | 0.16937 | -0.082397 | 0.11902 | 0.23804 | 0.073242 | 123.1934 | 122.9279 | 18.0771 | -123.1384 | 123.1888 | 123.0927 | 18.6676 | -123.1384
927.6406 | 123.1842 | -18.2922 | 104.718 | 0.59861 | 0.023121 | 0.070968 | 0.01575 | 0.036307 | -0.016608 | -0.018922 | 0.55574 | -0.011183 | 0.030626 | 0.048804 | 0.0088381 | -0.020399 | 104.5074 | -18.306 | -0.28381 | -18.5349 | 104.6997 | -18.3792 | -18.4982 | -18.3838 | 0.2655 | -18.132 | 104.7775 | 104.686 | -18.4204 | -18.4616 | -0.086975 | -0.20599 | -0.018311 | -0.013733 | -0.24262 | -0.036621 | -0.21057 | -0.12817 | -0.16937 | 0.059509 | -0.091553 | 0.16022 | 0.32959 | -0.032044 | 122.9919 | 122.7997 | 18.0084 | -123.2162 | 123.0698 | 122.9782 | 18.5577 | -123.1796
928.6406 | 123.175 | -18.219 | 104.7684 | 0.43077 | 0.010304 | 0.088058 | 0.024295 | 0.052329 | -0.012336 | -0.021058 | 0.46419 | 0.0027016 | 0.015672 | 0.047736 | 0.0077701 | -0.017194 | 104.6494 | -18.2007 | -0.33417 | -18.4387 | 104.8462 | -18.2602 | -18.3426 | -18.2968 | 0.2243 | -18.0725 | 104.8828 | 104.8187 | -18.3197 | -18.3517 | -0.041199 | -0.1236 | 0.077819 | 0.01831 | -0.21973 | -0.096131 | -0.11902 | -0.10071 | -0.13275 | 0.11444 | -0.07782 | 0.14648 | 0.27924 | 0.050354 | 123.0652 | 122.8683 | 17.8848 | -123.111 | 123.1018 | 123.0377 | 18.4433 | -123.1201
930.1562 | 123.1155 | -18.2739 | 104.7729 | -2.0869 | 0.0060322 | 0.067764 | 0.031771 | 0.044852 | 0.0026181 | -0.021058 | -0.4666 | -0.00050244 | 0.015672 | 0.037055 | 0.020587 | -0.035352 | 104.5715 | -18.3151 | -0.37537 | -18.5349 | 104.8737 | -18.3609 | -18.4479 | -18.4158 | 0.29755 | -18.1961 | 104.9194 | 104.8096 | -18.3884 | -18.4341 | -0.086975 | -0.17395 | 0.10071 | -0.041199 | -0.26093 | -0.086975 | -0.20142 | -0.11444 | -0.16022 | 0.14648 | -0.14191 | 0.07782 | 0.23804 | 0.036621 | 123.1476 | 122.8455 | 17.8986 | -123.2208 | 123.1934 | 123.0835 | 18.5715 | -123.2071
930.75 | 123.1522 | -18.2098 | 104.805 | -0.2101 | 0.00069119 | 0.074173 | 0.02109 | 0.04592 | -0.011268 | -0.01999 | -0.32927 | 0.0091106 | 0.022081 | 0.034919 | 0.012042 | -0.022535 | 104.6951 | -18.1641 | -0.28839 | -18.3884 | 104.924 | -18.2419 | -18.3243 | -18.2968 | 0.3479 | -18.1137 | 104.9286 | 104.8553 | -18.3151 | -18.3746 | -0.032043 | -0.11444 | 0.11902 | 0.045777 | -0.17853 | -0.064087 | -0.10986 | -0.10529 | -0.1648 | 0.1236 | -0.086975 | 0.096131 | 0.26093 | 0.050354 | 123.1338 | 122.905 | 17.9214 | -123.1293 | 123.1384 | 123.0652 | 18.5577 | -123.1796
931.6406 | 123.1842 | -18.219 | 104.7226 | 0.3087 | -0.0099898 | 0.073105 | 0.024295 | 0.037375 | -0.018744 | -0.032808 | 0.43367 | 0.00056556 | 0.017808 | 0.049872 | 0.0099061 | -0.022535 | 104.5532 | -18.2922 | -0.31128 | -18.5165 | 104.8553 | -18.3563 | -18.4387 | -18.2419 | 0.39368 | -18.0222 | 104.9423 | 104.8462 | -18.2739 | -18.338 | -0.13733 | -0.21973 | 0.13275 | -0.073242 | -0.29755 | -0.07782 | -0.16937 | -0.054932 | -0.11902 | 0.21973 | -0.022888 | 0.19684 | 0.31586 | 0.1236 | 123.0743 | 122.7722 | 17.9077 | -123.1613 | 123.1613 | 123.0652 | 18.6127 | -123.0606
932.6406 | 123.1979 | -18.6722 | 104.3335 | 0.20188 | -0.0046498 | 0.089126 | 0.030703 | 0.043784 | -0.0080629 | -0.017854 | 0.12849 | 0.0016336 | 0.031694 | 0.044532 | 0.012042 | -0.022535 | 104.187 | -18.7225 | -0.37537 | -18.8965 | 104.3884 | -18.7454 | -18.8461 | -18.782 | 0.29755 | -18.5349 | 104.4296 | 104.3381 | -18.7866 | -18.837 | -0.073242 | -0.17395 | 0.054932 | -0.050354 | -0.2243 | -0.050354 | -0.14648 | -0.11444 | -0.16479 | 0.09613 | -0.10986 | 0.13733 | 0.30212 | 0.004578 | 123.0606 | 122.8592 | 18.2968 | -123.1796 | 123.1018 | 123.0103 | 18.9697 | -123.1705
933.6406 | 123.2254 | -18.4113 | 104.5624 | 0.87327 | -0.0046498 | 0.08699 | 0.027499 | 0.043784 | -0.0037909 | -0.021058 | -0.0088351 | 0.0027016 | -0.0046224 | 0.044532 | 0.021655 | -0.03108 | 104.4296 | -18.425 | -0.3479 | -18.6493 | 104.6631 | -18.4708 | -18.5486 | -18.4708 | 0.3479 | -18.251 | 104.6951 | 104.567 | -18.5028 | -18.5577 | -0.059509 | -0.13733 | 0.10071 | -0.013733 | -0.23804 | -0.10071 | -0.13275 | -0.091553 | -0.14648 | 0.13275 | -0.059509 | 0.16022 | 0.3067 | 0.004578 | 123.0743 | 122.8409 | 18.0634 | -123.111 | 123.1064 | 122.9782 | 18.7592 | -123.1201
934.6406 | 123.2254 | -18.3426 | 104.6402 | 0.15611 | 0.022053 | 0.075241 | 0.036044 | 0.050193 | -0.0069949 | -0.028535 | -0.024094 | -0.0037074 | 0.011399 | 0.056281 | 0.0099061 | -0.026808 | 104.5807 | -18.2785 | -0.35248 | -18.5532 | 104.7546 | -18.3655 | -18.4433 | -18.3609 | 0.38452 | -18.132 | 104.7913 | 104.6631 | -18.4525 | -18.5028 | -0.022889 | -0.10071 | 0.11444 | 0.064087 | -0.21057 | -0.10986 | -0.05951 | -0.10986 | -0.16022 | 0.15106 | -0.018311 | 0.21057 | 0.37079 | 0.022888 | 123.0972 | 122.9233 | 17.9901 | -123.0835 | 123.1338 | 123.0057 | 18.7271 | -123.143
935.6406 | 123.2254 | -18.1046 | 104.8737 | 0.12559 | 0.013508 | 0.080581 | 0.02109 | 0.046988 | -0.0091309 | -0.017854 | -0.10039 | -0.0037074 | 0.0049906 | 0.054145 | 0.015247 | -0.023603 | 104.8187 | -18.0405 | -0.20142 | -18.2785 | 104.9973 | -18.1366 | -18.2236 | -18.1046 | 0.49896 | -17.9489 | 105.0247 | 104.8874 | -18.2007 | -18.2465 | -0.032044 | -0.11902 | 0.1236 | 0.064087 | -0.17395 | -0.054931 | -0.054931 | -0.096131 | -0.14191 | 0.15106 | 0 | 0.15564 | 0.29755 | 0.013733 | 123.1018 | 122.9233 | 17.9031 | -123.0972 | 123.1293 | 122.9919 | 18.6035 | -123.1201
936.6406 | 123.1979 | -17.9123 | 105.0247 | 0.24766 | -0.0057178 | 0.076309 | 0.01575 | 0.041648 | -0.010199 | -0.036012 | 0.12849 | 0.0016336 | 0.013536 | 0.044532 | 0.015247 | -0.033216 | 104.8965 | -18.1046 | -0.37537 | -18.1686 | 105.0934 | -18.0176 | -18.1183 | -18.0267 | 0.39368 | -17.7887 | 105.1758 | 105.0568 | -18.0679 | -18.0908 | -0.10529 | -0.20599 | 0.068665 | -0.19226 | -0.25635 | -0.050354 | -0.12817 | -0.15564 | -0.17853 | 0.15106 | -0.11444 | 0.1236 | 0.30212 | 0.032044 | 123.0057 | 122.8088 | 17.5369 | -123.143 | 123.0881 | 122.9691 | 18.306 | -123.1155
937.6406 | 123.2391 | -18.0634 | 104.8965 | -0.011739 | 0.0049632 | 0.079513 | 0.020022 | 0.035239 | -0.012336 | -0.026399 | -0.054612 | 0.00056556 | 0.015672 | 0.029578 | 0.0088381 | -0.026808 | 104.6768 | -18.1183 | -0.2655 | -18.3655 | 104.9194 | -18.2327 | -18.3334 | -18.1046 | 0.50812 | -17.9031 | 105.0156 | 104.9057 | -18.2007 | -18.2465 | -0.16937 | -0.27008 | 0.022889 | -0.054932 | -0.30213 | -0.032044 | -0.21973 | -0.13733 | -0.18311 | 0.11902 | -0.041199 | 0.16022 | 0.34332 | 0.009156 | 122.9828 | 122.7402 | 17.7979 | -123.23 | 123.0789 | 122.9691 | 18.5715 | -123.143
938.6406 | 123.2025 | -17.8024 | 105.1666 | -0.10329 | 0.0081682 | 0.0699 | 0.025363 | 0.048056 | -0.0027229 | -0.015718 | -0.26824 | -0.00050244 | 0.0060586 | 0.039191 | 0.025928 | -0.033216 | 105.1575 | -17.6788 | -0.15564 | -17.9535 | 105.3406 | -17.8299 | -17.9123 | -17.9352 | 0.65002 | -17.6743 | 105.3177 | 105.1758 | -17.9123 | -17.9626 | -0.027466 | -0.10986 | 0.17395 | 0.1236 | -0.15106 | -0.041199 | -0.009155 | -0.10986 | -0.16022 | 0.15106 | -0.13275 | 0.12817 | 0.28839 | 0.009155 | 123.143 | 122.9599 | 17.6468 | -123.0789 | 123.1201 | 122.9782 | 18.4525 | -123.1293
939.6406 | 123.1979 | -17.9214 | 105.0568 | -0.13381 | -0.0035808 | 0.077377 | 0.031771 | 0.053397 | -0.00058594 | -0.027467 | 1.6391 | -0.0037074 | 0.022081 | 0.033851 | 0.016315 | -0.033216 | 105.011 | -17.5781 | -0.15564 | -18.0176 | 105.2078 | -17.9581 | -18.0359 | -17.9443 | 0.50354 | -17.807 | 105.1987 | 105.043 | -17.9993 | -18.0588 | -0.036621 | -0.11444 | 0.15106 | 0.34332 | -0.09613 | 0.018311 | -0.045777 | -0.07782 | -0.13733 | 0.14191 | -0.022888 | 0.11444 | 0.25177 | -0.013733 | 123.1293 | 122.9324 | 17.7658 | -123.0927 | 123.1201 | 122.9645 | 18.425 | -123.1155
940.6406 | 123.2117 | -17.6376 | 105.3589 | -0.17959 | -0.015331 | 0.083786 | -0.0077492 | 0.041648 | -0.0069949 | -0.016786 | -0.17668 | 0.0037696 | 0.00071764 | 0.056281 | 0.010974 | -0.027876 | 105.217 | -17.5415 | -0.2655 | -17.7933 | 105.4413 | -17.6971 | -17.7658 | -17.6331 | 0.54016 | -17.4866 | 105.5054 | 105.3452 | -17.7292 | -17.7933 | -0.05951 | -0.12817 | 0.082397 | 0.09613 | -0.15564 | -0.027466 | -0.14191 | -0.091553 | -0.15564 | 0.14648 | 0.004577 | 0.15106 | 0.3067 | -0.013733 | 123.0789 | 122.8546 | 17.3721 | -123.1247 | 123.143 | 122.9828 | 18.1778 | -123.1522
941.6406 | 123.1934 | -17.5095 | 105.5008 | 0.064555 | 0.01244 | 0.078445 | 0.020022 | 0.036307 | 0.0047541 | -0.026399 | -0.29875 | 0.00056556 | 0.0092626 | 0.034919 | 0.0088381 | -0.03108 | 105.3864 | -17.3676 | -0.29755 | -17.6743 | 105.5923 | -17.5461 | -17.6422 | -17.5644 | 0.53101 | -17.3721 | 105.629 | 105.4596 | -17.6147 | -17.6788 | -0.036622 | -0.13275 | 0.091553 | 0.14191 | -0.16479 | -0.032043 | -0.11444 | -0.10529 | -0.16937 | 0.12817 | -0.054932 | 0.13733 | 0.3067 | -0.041198 | 123.1018 | 122.8958 | 17.2119 | -123.143 | 123.1384 | 122.9691 | 18.0405 | -123.1796
942.6406 | 123.1796 | -17.1387 | 105.867 | -0.31691 | -0.0035808 | 0.082718 | 0.014682 | 0.034171 | -0.00058594 | -0.013582 | -0.37505 | 0.0091106 | 0.017808 | 0.050941 | 0.0077701 | -0.030012 | 105.8029 | -16.9098 | -0.31586 | -17.2989 | 105.9906 | -17.1753 | -17.2531 | -17.2028 | 0.59509 | -16.9693 | 105.9952 | 105.8853 | -17.2577 | -17.2852 | -0.036621 | -0.11444 | 0.1236 | 0.22888 | -0.16022 | -0.045776 | -0.064087 | -0.11902 | -0.14648 | 0.12817 | -0.064087 | 0.16937 | 0.31586 | 0.018311 | 123.1293 | 122.9416 | 16.8228 | -123.1201 | 123.1338 | 123.024 | 17.7338 | -123.1522
943.6406 | 123.1522 | -17.0288 | 106.0638 | -0.19484 | 0.011372 | 0.08165 | 0.022158 | 0.04592 | -0.0037909 | -0.023195 | -0.39031 | -0.0015704 | 0.015672 | 0.041327 | 0.019519 | -0.028944 | 105.8624 | -16.8823 | -0.29755 | -17.2211 | 106.1005 | -17.0975 | -17.1524 | -17.0883 | 0.58136 | -16.8732 | 106.1371 | 106.0135 | -17.1432 | -17.1661 | -0.068664 | -0.1236 | 0.036621 | 0.14648 | -0.19226 | -0.068664 | -0.20142 | -0.11444 | -0.13733 | 0.073242 | -0.059509 | 0.15564 | 0.29297 | -0.050354 | 123.1293 | 122.8912 | 16.7313 | -123.2162 | 123.1659 | 123.0423 | 17.6102 | -123.23
944.6406 | 123.111 | -16.832 | 106.1966 | -0.22536 | 0.016713 | 0.08165 | 0.022158 | 0.050193 | -0.0016549 | -0.018922 | -0.40556 | -0.0015704 | 0.043443 | 0.041327 | 0.017383 | -0.038557 | 106.0226 | -16.6443 | -0.46692 | -17.0288 | 106.2973 | -16.9006 | -16.9739 | -16.9235 | 0.54474 | -16.7496 | 106.3431 | 106.1966 | -16.951 | -16.9876 | -0.068665 | -0.14191 | 0.10071 | 0.18768 | -0.19684 | -0.054932 | -0.17395 | -0.11902 | -0.15564 | 0.14648 | -0.091553 | 0.082397 | 0.23804 | 0 | 123.1293 | 122.8546 | 16.3651 | -123.1705 | 123.175 | 123.0286 | 17.3767 | -123.1842
945.6406 | 123.0835 | -16.1179 | 106.9702 | -0.2101 | 0.025258 | 0.076309 | 0.027499 | 0.044852 | 0.015435 | -0.021058 | -0.51238 | -0.0015704 | 0.03917 | 0.055213 | 0.016315 | -0.032148 | 106.8832 | -15.8936 | -0.48981 | -16.2323 | 107.1854 | -16.0812 | -16.1362 | -16.1545 | 0.85602 | -16.0309 | 107.1716 | 106.9794 | -16.1911 | -16.2415 | 0.036621 | -0.01831 | 0.21515 | 0.2243 | -0.11444 | -0.096131 | -0.086975 | -0.073242 | -0.1236 | 0.20142 | -0.036621 | 0.086975 | 0.21057 | 0.009155 | 123.3032 | 123.0011 | 15.6281 | -123.1064 | 123.2895 | 123.0972 | 16.9739 | -123.2117
946.6406 | 123.1064 | -16.452 | 106.5994 | -0.16433 | 0.026326 | 0.079513 | 0.031771 | 0.049125 | 0.0068901 | -0.023195 | 2.0969 | 0.0027016 | 0.018876 | 0.041327 | 0.015247 | -0.021467 | 106.4209 | -16.2735 | -0.5127 | -16.5802 | 106.8054 | -16.4474 | -16.5253 | -16.5024 | 0.4715 | -16.3834 | 106.7596 | 106.5857 | -16.5573 | -16.6168 | 0.004577 | -0.073243 | 0.20599 | 0.17853 | -0.12817 | -0.054931 | -0.17853 | -0.10529 | -0.1648 | 0.16022 | -0.050354 | 0.068664 | 0.23346 | -0.013733 | 123.2574 | 122.8729 | 15.9393 | -123.1247 | 123.2117 | 123.0377 | 16.9235 | -123.2162
947.6406 | 123.0881 | -16.626 | 106.4209 | -0.19484 | 0.041279 | 0.077377 | 0.027499 | 0.058738 | 0.00048206 | -0.010377 | -0.2072 | -0.020796 | 0.05626 | 0.048804 | 0.014179 | -0.025739 | 106.1783 | -16.3696 | -0.4715 | -16.8182 | 106.572 | -16.626 | -16.713 | -16.713 | 0.49896 | -16.4978 | 106.5857 | 106.4392 | -16.7221 | -16.7953 | 0 | -0.086975 | 0.15106 | 0.25635 | -0.19226 | -0.10528 | -0.24261 | -0.09613 | -0.16937 | 0.1648 | -0.086975 | 0.12817 | 0.29755 | 0.018311 | 123.1979 | 122.8043 | 16.1545 | -123.1338 | 123.2117 | 123.0652 | 17.1249 | -123.2162
948.6406 | 123.175 | -16.8045 | 106.2332 | -0.14907 | 0.027394 | 0.073105 | 0.028567 | 0.053397 | 0.0058221 | -0.0039683 | -0.34453 | 0.0027016 | 0.023149 | 0.06269 | 0.019519 | -0.038557 | 106.1188 | -16.5756 | -0.48065 | -16.9556 | 106.4072 | -16.7953 | -16.9098 | -16.8549 | 0.52643 | -16.6763 | 106.4072 | 106.2424 | -16.9098 | -16.9418 | 0.009155 | -0.10529 | 0.17395 | 0.22888 | -0.15106 | -0.045776 | -0.11444 | -0.10529 | -0.13733 | 0.17395 | -0.050354 | 0.12817 | 0.2655 | 0.009156 | 123.2117 | 122.9233 | 16.3239 | -123.143 | 123.2117 | 123.0469 | 17.3309 | -123.175
949.6406 | 123.1476 | -16.333 | 106.7276 | -0.22536 | 0.048756 | 0.067764 | 0.018954 | 0.039511 | -0.0048589 | -0.016786 | -0.31401 | 0.01552 | 0.028489 | 0.027442 | 0.014179 | -0.033216 | 106.5948 | -15.3992 | -0.44403 | -16.42 | 106.929 | -16.2827 | -16.3651 | -16.3651 | 0.54016 | -16.1636 | 106.9244 | 106.7871 | -16.3971 | -16.4612 | 0.050354 | -0.032043 | 0.20142 | 0.93384 | -0.086975 | -0.054932 | -0.13275 | -0.064087 | -0.12817 | 0.19684 | -0.032043 | 0.16937 | 0.29755 | 0.059509 | 123.262 | 122.9279 | 15.889 | -123.0927 | 123.2574 | 123.1201 | 16.8732 | -123.1888
950.6406 | 123.143 | -16.1957 | 106.8832 | -0.072774 | 0.027394 | 0.08165 | 0.03284 | 0.049125 | 0.0036861 | -0.0061053 | -0.35979 | 0.011247 | 0.035966 | 0.057349 | 0.012042 | -0.023603 | 106.6589 | -14.7629 | -0.43945 | -16.3742 | 106.9565 | -16.2506 | -16.3101 | -16.2643 | 0.71869 | -16.0812 | 106.9839 | 106.897 | -16.2964 | -16.3513 | -0.054931 | -0.11444 | 0.073242 | 1.4328 | -0.17853 | -0.064087 | -0.2243 | -0.10071 | -0.15564 | 0.10071 | -0.068664 | 0.11444 | 0.27008 | 0.013733 | 123.1522 | 122.8546 | 15.7562 | -123.1934 | 123.1796 | 123.0927 | 16.9144 | -123.2346
951.6406 | 123.0972 | -15.8203 | 107.2495 | 0.018779 | 0.047688 | 0.074173 | 0.039248 | 0.050193 | 0.0058221 | -0.013582 | 0.067459 | 0.013383 | 0.025285 | 0.042396 | 0.015247 | -0.024671 | 106.9839 | -14.1632 | -0.43945 | -16.0538 | 107.2769 | -15.8936 | -16.0126 | -15.8752 | 0.70953 | -15.7425 | 107.3456 | 107.222 | -15.976 | -15.9943 | -0.073243 | -0.19226 | 0.027466 | 1.6571 | -0.23346 | -0.041199 | -0.2655 | -0.15564 | -0.17395 | 0.09613 | -0.054932 | 0.077819 | 0.25177 | -0.027466 | 123.0972 | 122.8043 | 15.3809 | -123.262 | 123.1659 | 123.0423 | 16.5298 | -123.2437
952.6406 | 123.1476 | -16.5024 | 106.5079 | 0.018779 | 0.034871 | 0.072037 | 0.034976 | 0.033103 | 0.012231 | -0.0061053 | 0.11323 | 0.011247 | 0.024217 | 0.042396 | 0.022724 | -0.027876 | 106.2836 | -16.3284 | -0.43945 | -16.745 | 106.5811 | -16.6214 | -16.7038 | -16.4841 | 0.64087 | -16.3513 | 106.6772 | 106.5674 | -16.6122 | -16.6443 | -0.11902 | -0.20142 | 0.073242 | 0.17395 | -0.24262 | -0.041199 | -0.22431 | -0.10986 | -0.14191 | 0.16937 | 0.01831 | 0.15106 | 0.29297 | 0.059509 | 123.0835 | 122.7859 | 16.0629 | -123.2117 | 123.1796 | 123.0698 | 17.1432 | -123.1522
953.6406 | 123.056 | -16.2277 | 106.8375 | 0.2324 | 0.070118 | 0.077377 | 0.018954 | 0.042716 | 0.0079581 | -0.012513 | 0.17427 | 0.013383 | 0.041307 | 0.0456 | 0.020587 | -0.025739 | 106.6132 | -15.9943 | -0.51727 | -16.4246 | 106.9473 | -16.2872 | -16.3925 | -16.2827 | 0.66834 | -16.1133 | 106.9702 | 106.8649 | -16.3239 | -16.3513 | -0.059509 | -0.1648 | 0.10986 | 0.23346 | -0.19684 | -0.032044 | -0.2243 | -0.096131 | -0.1236 | 0.13275 | -0.054932 | 0.11444 | 0.23804 | 0.027466 | 123.175 | 122.8409 | 15.7104 | -123.23 | 123.1979 | 123.0927 | 16.8961 | -123.1888
954.6406 | 122.9874 | -16.2643 | 106.81 | 0.47654 | 0.043416 | 0.066696 | 0.034976 | 0.042716 | 0.00048206 | -0.016786 | 0.37263 | -0.0069114 | 0.063737 | 0.0456 | 0.022724 | -0.019331 | 106.572 | -16.0355 | -0.54016 | -16.452 | 106.929 | -16.3055 | -16.3742 | -16.3422 | 0.59967 | -16.1224 | 106.9519 | 106.8466 | -16.3513 | -16.3879 | -0.041199 | -0.10986 | 0.11902 | 0.22888 | -0.18768 | -0.077819 | -0.23804 | -0.086975 | -0.1236 | 0.14191 | -0.07782 | 0.14191 | 0.2655 | 0.036621 | 123.1934 | 122.8363 | 15.7242 | -123.1842 | 123.2162 | 123.111 | 16.864 | -123.1979
955.6406 | 123.0972 | -16.1316 | 106.9427 | 0.11033 | 0.059437 | 0.06456 | 0.033908 | 0.053397 | -0.0016549 | -0.01465 | 0.067459 | -0.022933 | 0.065873 | 0.049872 | 0.0302 | -0.027876 | 106.7642 | -15.9943 | -0.46692 | -16.301 | 107.0343 | -16.1499 | -16.2369 | -16.2003 | 0.6958 | -15.9485 | 107.0343 | 106.9656 | -16.2323 | -16.2872 | -0.01831 | -0.10528 | 0.091553 | 0.13733 | -0.16937 | -0.064087 | -0.17853 | -0.10071 | -0.15564 | 0.091553 | -0.068664 | 0.18311 | 0.33874 | 0.022888 | 123.1659 | 122.8958 | 15.6647 | -123.1796 | 123.1659 | 123.0972 | 16.8274 | -123.23
956.6406 | 123.111 | -16.04 | 107.0389 | 0.17137 | 0.048756 | 0.0699 | 0.029635 | 0.043784 | 0.0079581 | -0.01999 | -0.024094 | -0.016524 | 0.058397 | 0.052009 | 0.021655 | -0.03108 | 106.9061 | -15.9393 | -0.48523 | -16.1591 | 107.1716 | -16.0126 | -16.095 | -16.0767 | 0.62714 | -15.7928 | 107.1808 | 107.103 | -16.1041 | -16.1682 | 0.027466 | -0.054932 | 0.13275 | 0.10071 | -0.11902 | -0.064087 | -0.13275 | -0.064087 | -0.12817 | 0.14191 | -0.036621 | 0.24719 | 0.37537 | 0.064087 | 123.2117 | 122.9462 | 15.5548 | -123.1338 | 123.2208 | 123.143 | 16.6672 | -123.2071
957.6406 | 123.143 | -15.5685 | 107.46 | 0.20188 | 0.045552 | 0.065628 | 0.012545 | 0.052329 | 0.012231 | -0.023195 | 0.11323 | -0.029341 | 0.066941 | 0.046668 | 0.015247 | -0.024671 | 107.2998 | -15.2115 | -0.40741 | -15.7333 | 107.6157 | -15.6006 | -15.7059 | -15.6097 | 0.74616 | -15.4083 | 107.6431 | 107.5516 | -15.6509 | -15.7013 | -0.032044 | -0.13733 | 0.15564 | 0.35706 | -0.16479 | -0.027465 | -0.16022 | -0.082398 | -0.13275 | 0.18311 | -0.041199 | 0.16022 | 0.29297 | 0.091553 | 123.1842 | 122.8683 | 15.1611 | -123.1659 | 123.2117 | 123.1201 | 16.3147 | -123.1613
958.6406 | 123.0743 | -16.2369 | 106.8329 | 0.24766 | 0.050892 | 0.074173 | 0.024295 | 0.04058 | 0.00048206 | -0.01999 | 0.15901 | -0.022933 | 0.055192 | 0.0456 | 0.016315 | -0.015058 | 106.5491 | -16.0309 | -0.51727 | -16.4841 | 106.8878 | -16.3284 | -16.4337 | -16.3467 | 0.66834 | -16.127 | 106.9656 | 106.8741 | -16.3376 | -16.3696 | -0.091553 | -0.19684 | 0.054931 | 0.20599 | -0.24719 | -0.050354 | -0.28381 | -0.10071 | -0.13275 | 0.13275 | -0.10986 | 0.10986 | 0.24262 | 0.041198 | 123.1247 | 122.7859 | 15.7196 | -123.2666 | 123.2025 | 123.111 | 16.9052 | -123.2025
959.6875 | 123.1567 | -15.9805 | 106.9839 | 0.53758 | 0.031666 | 0.083786 | 0.029635 | 0.032035 | -0.025153 | -0.030671 | 0.571 | -0.024001 | 0.055192 | 0.030646 | -0.00077485 | -0.00865 | 106.8695 | -15.6235 | -0.42572 | -16.1362 | 107.1533 | -15.9805 | -16.0629 | -15.976 | 0.72784 | -15.7379 | 107.2083 | 107.1579 | -16.04 | -16.1041 | 0 | -0.082397 | 0.16937 | 0.35706 | -0.15564 | -0.073242 | -0.11444 | -0.059509 | -0.1236 | 0.2243 | 0.004578 | 0.24262 | 0.36621 | 0.17395 | 123.1338 | 122.85 | 15.5548 | -123.0469 | 123.1888 | 123.1384 | 16.7084 | -123.0881
960.6406 | 123.1293 | -16.333 | 106.691 | -2.8651 | 0.037007 | 0.072037 | 0.039248 | 0.039511 | 0.015435 | -0.018922 | 0.28108 | -0.016524 | 0.062669 | 0.049872 | 0.017383 | -0.028944 | 106.5582 | -16.1224 | -0.54932 | -16.4932 | 106.897 | -16.3467 | -16.4291 | -16.4246 | 0.64545 | -16.3376 | 106.8146 | 106.6956 | -16.4841 | -16.5161 | -0.013733 | -0.09613 | 0.20599 | 0.21057 | -0.16022 | -0.064087 | -0.13275 | -0.15106 | -0.18311 | 0.1236 | -0.091553 | -0.004577 | 0.17853 | 0.004578 | 123.23 | 122.8912 | 15.7837 | -123.1201 | 123.1476 | 123.0286 | 16.9785 | -123.2071
961.6406 | 123.1338 | -16.0309 | 106.9794 | 0.65965 | 0.055165 | 0.066696 | 0.033908 | 0.039511 | 0.010095 | -0.01999 | 0.47945 | -0.029341 | 0.062669 | 0.039191 | 0.022724 | -0.011854 | 106.7963 | -15.9348 | -0.55847 | -16.2689 | 107.0938 | -16.0995 | -16.1865 | -16.095 | 0.65918 | -15.8936 | 107.1167 | 107.048 | -16.1499 | -16.1728 | -0.068664 | -0.15564 | 0.11444 | 0.096131 | -0.23804 | -0.082398 | -0.1831 | -0.11902 | -0.14191 | 0.13733 | -0.064087 | 0.13733 | 0.27924 | 0.068665 | 123.1247 | 122.8271 | 15.4724 | -123.1659 | 123.1476 | 123.0789 | 16.6901 | -123.1522
962.6406 | 123.2162 | -16.3376 | 106.6315 | 0.3087 | 0.050892 | 0.073105 | 0.016818 | 0.038443 | -0.0037909 | -0.027467 | 0.46419 | -0.031478 | 0.06801 | 0.040259 | 0.012042 | -0.032148 | 106.5582 | -15.9348 | -0.4303 | -16.4978 | 106.7459 | -16.3651 | -16.4612 | -16.3559 | 0.737 | -16.1407 | 106.7596 | 106.7001 | -16.452 | -16.4658 | -0.027466 | -0.1236 | 0.11444 | 0.40283 | -0.16022 | -0.036621 | -0.073242 | -0.11444 | -0.12817 | 0.12817 | -0.018311 | 0.19684 | 0.32501 | 0.068664 | 123.0835 | 122.8958 | 15.9073 | -123.0927 | 123.0972 | 123.0377 | 17.0746 | -123.0972
963.6406 | 123.1476 | -16.3696 | 106.6589 | 0.85801 | 0.049824 | 0.074173 | 0.044589 | 0.034171 | 0.017572 | -0.028535 | 0.35738 | -0.015456 | 0.05626 | 0.046668 | 0.023792 | -0.017194 | 106.5582 | -16.008 | -0.5722 | -16.5756 | 106.8237 | -16.3971 | -16.4795 | -16.4474 | 0.65002 | -16.3193 | 106.8329 | 106.7368 | -16.4749 | -16.5298 | -0.027466 | -0.10986 | 0.16479 | 0.36163 | -0.20599 | -0.096131 | -0.10071 | -0.10529 | -0.16022 | 0.17395 | -0.07782 | 0.050354 | 0.21057 | 0.077819 | 123.1934 | 122.9279 | 15.7974 | -123.1384 | 123.2025 | 123.1064 | 17.0197 | -123.1888
964.6406 | 123.2346 | -16.5939 | 106.3614 | 0.64439 | 0.035939 | 0.068832 | 0.036044 | 0.044852 | 0.0068901 | -0.012513 | 1.044 | -0.026137 | 0.053056 | 0.048804 | 0.026996 | -0.033216 | 106.2515 | -16.3467 | -0.47607 | -16.8228 | 106.4758 | -16.6855 | -16.7633 | -16.6397 | 0.83313 | -16.4612 | 106.5033 | 106.4255 | -16.713 | -16.7725 | -0.091553 | -0.16937 | 0.11444 | 0.24719 | -0.22888 | -0.059509 | -0.10986 | -0.11902 | -0.17853 | 0.14191 | -0.045776 | 0.13275 | 0.31128 | 0.064087 | 123.0698 | 122.8455 | 16.1179 | -123.1247 | 123.0972 | 123.0194 | 17.4271 | -123.1338
965.6406 | 123.1796 | -16.5344 | 106.4163 | -0.11855 | -0.0099898 | 0.066696 | 0.01575 | 0.041648 | -0.017676 | -0.013582 | 0.44893 | -0.03575 | 0.049852 | 0.056281 | 0.0056341 | -0.01399 | 106.279 | -16.0126 | -0.41657 | -16.7725 | 106.4987 | -16.6122 | -16.6901 | -16.5665 | 1.0391 | -16.3239 | 106.5674 | 106.4896 | -16.6626 | -16.6992 | -0.07782 | -0.15564 | 0.082397 | 0.52185 | -0.23804 | -0.082398 | -0.13733 | -0.12817 | -0.16479 | 0.15106 | -0.032043 | 0.21057 | 0.37537 | 0.073242 | 123.0331 | 122.8134 | 16.1179 | -123.1064 | 123.1018 | 123.024 | 17.5735 | -123.1155
966.6406 | 123.1934 | -16.3788 | 106.5994 | 0.4918 | 0.0081682 | 0.082718 | 0.036044 | 0.029898 | -0.016608 | -0.021058 | 0.571 | -0.031478 | 0.051988 | 0.044532 | 0.0013611 | -0.030012 | 106.4529 | -15.9302 | -0.46692 | -16.6306 | 106.7139 | -16.4337 | -16.539 | -16.3925 | 1.0666 | -16.3971 | 106.7184 | 106.6406 | -16.5298 | -16.5665 | -0.054932 | -0.16022 | 0.11444 | 0.44861 | -0.25177 | -0.091553 | -0.14648 | -0.15106 | -0.18768 | 0.11902 | -0.013733 | -0.018311 | 0.16937 | 0.041199 | 123.0927 | 122.8317 | 15.9119 | -123.1384 | 123.0972 | 123.0194 | 17.4454 | -123.1659
967.6406 | 123.2025 | -16.6443 | 106.3477 | 0.43077 | 0.0071002 | 0.079513 | 0.018954 | 0.043784 | -0.011268 | -0.031739 | 0.50996 | -0.020796 | 0.063737 | 0.060554 | 0.016315 | -0.026808 | 106.1783 | -16.246 | -0.42572 | -16.9373 | 106.366 | -16.7679 | -16.8182 | -16.6946 | 1.0208 | -16.4932 | 106.4896 | 106.4072 | -16.745 | -16.7953 | -0.1236 | -0.17395 | 0.018311 | 0.39825 | -0.29297 | -0.11902 | -0.16937 | -0.10071 | -0.15106 | 0.14191 | -0.050354 | 0.15106 | 0.30212 | 0.05951 | 123.0103 | 122.8226 | 16.2186 | -123.1659 | 123.1338 | 123.0515 | 17.6651 | -123.143
968.6406 | 123.1796 | -16.7496 | 106.2149 | 0.58335 | 0.032734 | 0.077377 | 0.028567 | 0.042716 | -0.019813 | -0.031739 | 0.37263 | -0.027205 | 0.046647 | 0.0456 | 0.0099061 | -0.027876 | 106.1691 | -16.301 | -0.42572 | -16.9464 | 106.3797 | -16.777 | -16.8549 | -16.7862 | 1.0803 | -16.6077 | 106.4072 | 106.3248 | -16.8274 | -16.8823 | -0.027466 | -0.10528 | 0.16479 | 0.44861 | -0.19684 | -0.091553 | -0.045777 | -0.07782 | -0.13275 | 0.19226 | -0.036621 | 0.14191 | 0.27466 | 0.10986 | 123.1293 | 122.9187 | 16.3239 | -123.0698 | 123.1567 | 123.0743 | 17.8299 | -123.0972
969.6406 | 123.1567 | -16.3284 | 106.6818 | 0.40025 | 0.0071002 | 0.075241 | 0.016818 | 0.043784 | -0.012336 | -0.028535 | 0.28108 | -0.027205 | 0.044511 | 0.053077 | 0.018451 | -0.028944 | 106.5445 | -15.8478 | -0.36163 | -16.5161 | 106.8054 | -16.3513 | -16.4383 | -16.3467 | 1.1902 | -16.2003 | 106.842 | 106.7459 | -16.42 | -16.4612 | -0.022888 | -0.10986 | 0.1236 | 0.48065 | -0.18768 | -0.07782 | -0.13733 | -0.091553 | -0.13275 | 0.16022 | -0.018311 | 0.12817 | 0.26093 | 0.064087 | 123.1338 | 122.8729 | 15.9668 | -123.1201 | 123.1705 | 123.0743 | 17.5186 | -123.143
970.6406 | 123.1705 | -16.0858 | 106.9107 | 0.46128 | 0.014576 | 0.078445 | 0.012545 | 0.033103 | -0.00058594 | -0.017854 | 0.41841 | -0.033614 | 0.045579 | 0.031714 | 0.022724 | -0.027876 | 106.778 | -15.6235 | -0.27466 | -16.2781 | 106.9885 | -16.1362 | -16.2415 | -16.1362 | 1.2772 | -15.9439 | 107.0343 | 106.929 | -16.2231 | -16.2369 | -0.050354 | -0.15564 | 0.077819 | 0.46234 | -0.19226 | -0.036621 | -0.13275 | -0.13733 | -0.15106 | 0.1236 | -0.050354 | 0.14191 | 0.29297 | 0.01831 | 123.0743 | 122.8638 | 15.8112 | -123.1522 | 123.1201 | 123.0148 | 17.363 | -123.1476
971.6406 | 123.2117 | -16.1224 | 106.8558 | 0.4918 | 0.018849 | 0.075241 | 0.024295 | 0.052329 | -0.010199 | -0.023195 | 0.61677 | -0.029341 | 0.045579 | 0.041327 | 0.015247 | -0.021467 | 106.7276 | -15.683 | -0.32044 | -16.3467 | 106.9839 | -16.1682 | -16.2781 | -16.1819 | 1.3733 | -15.9851 | 106.9885 | 106.8878 | -16.2689 | -16.2689 | -0.045776 | -0.15564 | 0.12817 | 0.43945 | -0.2243 | -0.068665 | -0.12817 | -0.14648 | -0.14648 | 0.13275 | -0.059509 | 0.13733 | 0.28381 | 0.032043 | 123.1064 | 122.85 | 15.802 | -123.1338 | 123.111 | 123.0103 | 17.4957 | -123.1247
972.6406 | 123.2025 | -16.1682 | 106.81 | -0.11855 | 0.01244 | 0.080581 | 0.018954 | 0.039511 | -0.0080629 | -0.025331 | -0.25298 | -0.036818 | 0.03383 | 0.049872 | 0.0099061 | -0.022535 | 106.8008 | -15.6143 | -0.23346 | -16.2781 | 106.9748 | -16.1774 | -16.2689 | -16.1224 | 1.5793 | -15.9439 | 106.9702 | 106.8787 | -16.246 | -16.301 | -0.009155 | -0.10071 | 0.16479 | 0.55389 | -0.10986 | -0.009155 | -0.009156 | -0.07782 | -0.13275 | 0.16022 | 0.045776 | 0.2243 | 0.35706 | 0.068664 | 123.143 | 122.9691 | 15.9348 | -123.0789 | 123.1384 | 123.0469 | 17.7475 | -123.111
973.6406 | 123.2391 | -16.5939 | 106.3797 | -0.11855 | 0.010304 | 0.066696 | 0.027499 | 0.041648 | -0.010199 | -0.029603 | 0.15901 | -0.045363 | 0.044511 | 0.034919 | 0.0088381 | -0.032148 | 106.279 | -16.2827 | -0.2655 | -16.8228 | 106.485 | -16.6992 | -16.7908 | -16.571 | 1.5244 | -16.3101 | 106.5216 | 106.3751 | -16.6946 | -16.7725 | -0.10529 | -0.19684 | 0.10528 | 0.31128 | -0.22888 | -0.032044 | -0.10071 | -0.10071 | -0.17853 | 0.14191 | 0.022888 | 0.28381 | 0.46234 | -0.004578 | 123.0789 | 122.8729 | 16.3284 | -123.1705 | 123.1155 | 122.9691 | 18.1183 | -123.1522
974.6406 | 123.1934 | -16.6809 | 106.3248 | -0.24062 | -0.00037681 | 0.085922 | 0.054202 | 0.044852 | -0.0059269 | -0.012513 | -0.6497 | -0.031478 | 0.043443 | 0.0456 | 0.022724 | -0.025739 | 105.9448 | -16.2964 | -0.14648 | -16.8915 | 106.3934 | -16.745 | -16.8228 | -16.6855 | 1.5289 | -16.507 | 106.4301 | 106.3156 | -16.7862 | -16.8137 | -0.064087 | -0.14191 | 0.068665 | 0.38452 | -0.21057 | -0.068664 | -0.37994 | -0.10529 | -0.13275 | 0.10529 | -0.004578 | 0.17395 | 0.3067 | -0.009155 | 123.0743 | 122.6257 | 16.5344 | -123.1476 | 123.111 | 122.9965 | 18.2098 | -123.1384
975.6406 | 123.2346 | -16.7404 | 106.2424 | -0.026997 | -0.012126 | 0.073105 | 0.027499 | 0.050193 | -0.0037909 | -0.025331 | -0.35979 | -0.022933 | 0.047715 | 0.042396 | 0.0099061 | -0.03108 | 106.1874 | -16.4291 | -0.21515 | -16.9144 | 106.3614 | -16.7725 | -16.8777 | -16.7221 | 1.6525 | -16.5665 | 106.3751 | 106.2332 | -16.832 | -16.8915 | -0.032044 | -0.13733 | 0.11902 | 0.31128 | -0.17395 | -0.036621 | -0.054932 | -0.091553 | -0.15106 | 0.13275 | 0.01831 | 0.17395 | 0.32501 | -0.009156 | 123.1018 | 122.9279 | 16.5253 | -123.1201 | 123.1155 | 122.9736 | 18.3929 | -123.1339
976.6406 | 123.2208 | -16.301 | 106.6544 | -0.17959 | 0.00069119 | 0.076309 | 0.033908 | 0.036307 | -0.0091309 | -0.025331 | 3.165 | -0.028273 | 0.045579 | 0.047736 | 0.017383 | -0.025739 | 106.6452 | -15.8707 | -0.19684 | -16.4337 | 106.842 | -16.3101 | -16.4291 | -16.2964 | 2.0416 | -16.1316 | 106.842 | 106.6818 | -16.4154 | -16.4566 | -0.009156 | -0.12817 | 0.18768 | 0.4303 | -0.13275 | -0.004578 | -0.009155 | -0.11444 | -0.15564 | 0.18768 | 0.004577 | 0.16937 | 0.32501 | 0.027466 | 123.143 | 122.9462 | 16.1041 | -123.0835 | 123.143 | 122.9828 | 18.3426 | -123.111
977.6406 | 123.2025 | -16.3055 | 106.6635 | 0.18663 | -0.0046498 | 0.072037 | 0.02109 | 0.038443 | -0.023017 | -0.029603 | -0.28349 | -0.028273 | 0.045579 | 0.032783 | 0.014179 | -0.024671 | 106.5445 | -15.9851 | -0.16937 | -16.4886 | 106.7551 | -16.3925 | -16.4429 | -16.2735 | 3.4058 | -16.0904 | 106.8192 | 106.6818 | -16.4154 | -16.4383 | -0.086975 | -0.13733 | 0.091553 | 0.32043 | -0.18311 | -0.045776 | -0.11902 | -0.10986 | -0.13275 | 0.15564 | 0.032043 | 0.21515 | 0.3479 | 0.018311 | 123.0606 | 122.85 | 16.1362 | -123.1064 | 123.1247 | 122.9874 | 19.7113 | -123.1018
978.6406 | 123.1796 | -16.8228 | 106.1691 | -0.30166 | 0.02419 | 0.091263 | 0.034976 | 0.036307 | 0.0026181 | -0.015718 | -0.35979 | -0.033614 | 0.051988 | 0.037055 | 0.010974 | -0.028944 | 106.0638 | -16.4886 | -0.21515 | -17.0242 | 106.2515 | -16.8869 | -16.9785 | -16.8594 | 3.4378 | -16.6992 | 106.2744 | 106.1325 | -16.9876 | -17.0151 | -0.064087 | -0.15564 | 0.082398 | 0.33417 | -0.20142 | -0.045776 | -0.10528 | -0.1648 | -0.19226 | 0.10529 | -0.036621 | 0.1236 | 0.31586 | -0.036621 | 123.0743 | 122.8867 | 16.6077 | -123.1476 | 123.0972 | 122.9553 | 20.2606 | -123.1842
979.6406 | 123.0972 | -16.1087 | 106.9611 | -0.2864 | 0.0071002 | 0.082718 | 0.018954 | 0.038443 | -0.00058594 | -0.016786 | -0.4666 | -0.020796 | 0.030626 | 0.041327 | 0.019519 | -0.030012 | 106.6818 | -15.6097 | -0.21973 | -16.3605 | 107.0297 | -16.2003 | -16.2918 | -16.1041 | 3.2547 | -15.9714 | 107.1121 | 106.9382 | -16.2231 | -16.2598 | -0.091552 | -0.18311 | 0.068664 | 0.49896 | -0.25177 | -0.068665 | -0.27924 | -0.11444 | -0.15106 | 0.15106 | 0.004578 | 0.13733 | 0.28839 | -0.022889 | 123.1384 | 122.7905 | 15.889 | -123.2529 | 123.2208 | 123.0469 | 19.3634 | -123.2208
980.6406 | 123.0835 | -16.5573 | 106.4896 | -0.97304 | 0.014576 | 0.076309 | 0.031771 | 0.051261 | 0.017572 | -0.021058 | -0.43608 | -0.024001 | 0.047715 | 0.040259 | 0.023792 | -0.032148 | 106.2561 | -16.0172 | -0.3479 | -16.7816 | 106.6269 | -16.626 | -16.6992 | -16.5573 | 2.8519 | -16.4749 | 106.6406 | 106.4987 | -16.7038 | -16.7267 | -0.068665 | -0.14191 | 0.13733 | 0.54016 | -0.2243 | -0.082397 | -0.23346 | -0.14648 | -0.16937 | 0.15106 | 0 | 0.082397 | 0.25177 | 0.009155 | 123.1842 | 122.8134 | 16.2094 | -123.1888 | 123.1979 | 123.056 | 19.4092 | -123.2162
981.6406 | 123.1522 | -16.6992 | 106.4117 | -0.37795 | 0.011372 | 0.070968 | 0.020022 | 0.041648 | 0.0036861 | -0.018922 | -0.42082 | -0.025069 | 0.059465 | 0.034919 | 0.010974 | -0.034284 | 106.0867 | -16.2827 | -0.35706 | -16.951 | 106.4667 | -16.7679 | -16.8686 | -16.7358 | 2.8198 | -16.5939 | 106.4758 | 106.3431 | -16.8411 | -16.8823 | -0.068664 | -0.16937 | 0.054932 | 0.41656 | -0.25177 | -0.082398 | -0.32501 | -0.14191 | -0.18311 | 0.064087 | -0.036621 | 0.10529 | 0.28839 | -0.068664 | 123.1659 | 122.7859 | 16.3422 | -123.2803 | 123.175 | 123.0423 | 19.519 | -123.2941
982.6406 | 123.0652 | -16.6901 | 106.3614 | -0.22536 | 0.027394 | 0.075241 | 0.023226 | 0.044852 | -0.011268 | -0.023195 | -0.37505 | -0.019728 | 0.062669 | 0.042396 | 0.014179 | -0.028944 | 106.1829 | -16.2231 | -0.35706 | -16.8732 | 106.5262 | -16.6992 | -16.8045 | -16.6763 | 3.3051 | -16.3651 | 106.6177 | 106.4301 | -16.745 | -16.7999 | -0.009156 | -0.11444 | 0.16479 | 0.46692 | -0.18311 | -0.068665 | -0.17853 | -0.054932 | -0.10986 | 0.25635 | 0.013732 | 0.32501 | 0.43488 | 0.068665 | 123.2162 | 122.8729 | 16.333 | -123.1659 | 123.3078 | 123.1201 | 19.9951 | -123.1613
983.6406 | 123.0743 | -16.5344 | 106.5216 | -0.2864 | 0.02419 | 0.066696 | 0.031771 | 0.055533 | -0.00058594 | -0.017854 | -0.35979 | -0.022933 | 0.051988 | 0.043464 | 0.023792 | -0.019331 | 106.2561 | -16.1224 | -0.39368 | -16.8228 | 106.5994 | -16.6534 | -16.7267 | -16.5894 | 3.3875 | -16.3879 | 106.6818 | 106.5491 | -16.626 | -16.6855 | -0.11902 | -0.19226 | 0.07782 | 0.41199 | -0.28839 | -0.09613 | -0.2655 | -0.091553 | -0.15106 | 0.16022 | -0.054931 | 0.14649 | 0.29755 | 0.027466 | 123.1338 | 122.7905 | 16.1407 | -123.2483 | 123.2162 | 123.0835 | 19.9219 | -123.2071
984.6406 | 123.0881 | -16.5298 | 106.5262 | -0.31691 | 0.019917 | 0.090195 | 0.040316 | 0.042716 | -0.014472 | -0.025331 | 0.25056 | -0.028273 | 0.045579 | 0.040259 | 0.016315 | -0.028944 | 106.3431 | -15.9897 | -0.28839 | -16.6763 | 106.6681 | -16.5298 | -16.6122 | -16.4749 | 3.7537 | -16.3559 | 106.7368 | 106.572 | -16.6122 | -16.6718 | 0 | -0.082398 | 0.14191 | 0.54016 | -0.14649 | -0.064087 | -0.1831 | -0.082398 | -0.14191 | 0.21057 | 0.054931 | 0.17395 | 0.31586 | 0.045776 | 123.1979 | 122.8729 | 16.2415 | -123.1384 | 123.2666 | 123.1018 | 20.2835 | -123.1979
985.6406 | 123.1567 | -16.2048 | 106.842 | 0.21714 | 0.045552 | 0.070968 | 0.046725 | 0.044852 | 0.025048 | -0.023195 | -0.2072 | -0.019728 | 0.063737 | 0.050941 | 0.021655 | -0.034284 | 106.6544 | -15.7562 | -0.29297 | -16.4108 | 106.9656 | -16.2918 | -16.3696 | -16.1362 | 3.8589 | -16.095 | 106.9611 | 106.8329 | -16.333 | -16.3696 | -0.086975 | -0.16479 | 0.1236 | 0.44861 | -0.20599 | -0.041199 | -0.18768 | -0.12817 | -0.16479 | 0.11902 | 0.068665 | 0.10986 | 0.27466 | -0.009155 | 123.1705 | 122.8592 | 15.9119 | -123.2117 | 123.1659 | 123.0377 | 20.0638 | -123.2117
986.6406 | 123.1659 | -16.3651 | 106.6818 | -0.14907 | 0.037007 | 0.062424 | 0.031771 | 0.046988 | 0.012231 | -0.018922 | -0.40556 | -0.027205 | 0.043443 | 0.044532 | 0.020587 | -0.022535 | 106.5765 | -15.5731 | -0.25177 | -16.4566 | 106.9107 | -16.3376 | -16.42 | -16.2598 | 4.3442 | -16.1728 | 106.9061 | 106.7139 | -16.4154 | -16.4795 | 0.027466 | -0.054932 | 0.22888 | 0.79193 | -0.091553 | -0.036621 | -0.10529 | -0.050354 | -0.11444 | 0.2243 | 0.10529 | 0.19226 | 0.3067 | 0.032043 | 123.2758 | 122.9416 | 16.1133 | -123.1018 | 123.2712 | 123.0789 | 20.7092 | -123.1613
987.6406 | 123.1522 | -16.4062 | 106.6177 | 0.72068 | 0.02419 | 0.0699 | 0.041384 | 0.046988 | 0.0047541 | -0.021058 | 0.41841 | -0.012251 | 0.05626 | 0.053077 | 0.01311 | -0.022535 | 106.4438 | -15.7333 | -0.30212 | -16.6031 | 106.7596 | -16.4566 | -16.5253 | -16.3193 | 4.1245 | -16.246 | 106.7825 | 106.636 | -16.4886 | -16.5207 | -0.050354 | -0.11902 | 0.14191 | 0.67291 | -0.19684 | -0.077819 | -0.17395 | -0.082397 | -0.11444 | 0.16479 | 0.086975 | 0.16022 | 0.27466 | 0.01831 | 123.1659 | 122.85 | 16.1041 | -123.143 | 123.1888 | 123.0423 | 20.5307 | -123.1384
988.6406 | 123.1201 | -16.3239 | 106.6956 | -0.17959 | 0.025258 | 0.084854 | 0.018954 | 0.036307 | 0.0058221 | -0.01465 | -0.06987 | -0.019728 | 0.063737 | 0.043464 | 0.019519 | -0.034284 | 106.5262 | -15.6555 | -0.18768 | -16.5344 | 106.8008 | -16.42 | -16.4795 | -16.2598 | 3.978 | -16.1682 | 106.8878 | 106.7505 | -16.4246 | -16.4658 | -0.09613 | -0.15564 | 0.10529 | 0.66833 | -0.21057 | -0.054932 | -0.16937 | -0.10071 | -0.14191 | 0.19226 | 0.064087 | 0.15564 | 0.29755 | 0.054931 | 123.1247 | 122.85 | 16.1362 | -123.175 | 123.2117 | 123.0743 | 20.3018 | -123.1613
989.6406 | 123.1293 | -16.2827 | 106.7413 | -0.057515 | 0.032734 | 0.058151 | 0.03284 | 0.043784 | 0.014367 | -0.0029003 | 0.036941 | -0.016524 | 0.053056 | 0.037055 | 0.023792 | -0.028944 | 106.6452 | -15.4358 | -0.16479 | -16.4154 | 106.9244 | -16.2964 | -16.3651 | -16.1865 | 3.4103 | -16.1224 | 106.9107 | 106.8146 | -16.3742 | -16.42 | -0.013733 | -0.082397 | 0.1831 | 0.84686 | -0.13275 | -0.050354 | -0.09613 | -0.091553 | -0.13733 | 0.16937 | 0.096131 | 0.16022 | 0.29755 | 0.073242 | 123.2071 | 122.9279 | 16.1179 | -123.1064 | 123.1934 | 123.0972 | 19.693 | -123.1613
990.6406 | 123.1659 | -15.8066 | 107.2357 | 0.12559 | 0.039143 | 0.054947 | 0.044589 | 0.051261 | 0.0079581 | -0.015718 | -0.14616 | -0.026137 | 0.041307 | 0.044532 | 0.017383 | -0.022535 | 107.0847 | -14.978 | -0.15564 | -15.9943 | 107.3868 | -15.8386 | -15.9439 | -15.7333 | 3.8681 | -15.6921 | 107.3456 | 107.2678 | -15.9164 | -15.9668 | -0.032043 | -0.13733 | 0.15106 | 0.82855 | -0.18768 | -0.050354 | -0.15106 | -0.10986 | -0.16022 | 0.10986 | 0.073243 | 0.11444 | 0.27466 | 0.032043 | 123.1934 | 122.8912 | 15.6509 | -123.1796 | 123.1522 | 123.0743 | 19.6747 | -123.2025
991.6406 | 123.143 | -16.2827 | 106.7642 | -0.14907 | 0.038075 | 0.082718 | 0.028567 | 0.049125 | -0.0037909 | -0.01999 | -0.32927 | -0.021865 | 0.049852 | 0.049872 | 0.016315 | -0.032148 | 106.6727 | -15.6876 | -0.14191 | -16.3925 | 106.9794 | -16.2506 | -16.3559 | -16.1774 | 3.6713 | -16.2369 | 106.929 | 106.8146 | -16.3834 | -16.4291 | 0.032044 | -0.073242 | 0.21515 | 0.59509 | -0.10986 | -0.036621 | -0.091553 | -0.10071 | -0.14648 | 0.16479 | 0.10529 | 0.045777 | 0.19226 | 0.050354 | 123.262 | 122.9553 | 16.1407 | -123.1201 | 123.2117 | 123.0972 | 19.9539 | -123.1934
992.6406 | 123.2254 | -15.8386 | 107.1167 | 0.46128 | 0.035939 | 0.074173 | 0.029635 | 0.035239 | -0.0048589 | -0.018922 | 0.60152 | -0.025069 | 0.049852 | 0.044532 | 0.012042 | -0.01399 | 106.9702 | -15.2344 | 0.009155 | -16.0629 | 107.2083 | -15.9439 | -16.0217 | -15.7516 | 3.923 | -15.6464 | 107.2449 | 107.1487 | -15.9668 | -15.9897 | -0.10529 | -0.18311 | 0.091553 | 0.60425 | -0.2243 | -0.041198 | -0.14648 | -0.12817 | -0.15106 | 0.12817 | 0.086975 | 0.19226 | 0.34332 | 0.032044 | 123.0469 | 122.8088 | 15.8478 | -123.1384 | 123.0835 | 122.9874 | 19.7617 | -123.1064
993.6406 | 123.0972 | -15.9988 | 107.0755 | 0.2324 | 0.053029 | 0.074173 | 0.033908 | 0.055533 | 0.010095 | -0.022126 | 0.082718 | -0.010115 | 0.070146 | 0.044532 | 0.025928 | -0.032148 | 106.9244 | -15.1199 | -0.064087 | -16.1545 | 107.1808 | -16.0217 | -16.127 | -15.9851 | 4.2984 | -15.8798 | 107.2586 | 107.1442 | -16.0721 | -16.127 | -0.022889 | -0.12817 | 0.10529 | 0.87891 | -0.15564 | -0.027466 | -0.15106 | -0.073243 | -0.12817 | 0.18311 | 0.013733 | 0.11902 | 0.24719 | 0.068665 | 123.1796 | 122.9233 | 15.9348 | -123.2025 | 123.2574 | 123.143 | 20.2972 | -123.2025
994.6406 | 123.0789 | -15.7059 | 107.3456 | 0.29344 | 0.043416 | 0.070968 | 0.045657 | 0.050193 | 0.0047541 | -0.016786 | 0.0522 | -0.012251 | 0.064805 | 0.047736 | 0.020587 | -0.036421 | 107.1442 | -14.9551 | 0.027466 | -15.8798 | 107.4875 | -15.7196 | -15.8295 | -15.7745 | 4.5639 | -15.6464 | 107.4738 | 107.3822 | -15.8478 | -15.8798 | -0.013732 | -0.1236 | 0.14191 | 0.75073 | -0.17395 | -0.050354 | -0.20142 | -0.14191 | -0.17395 | 0.12817 | -0.068664 | 0.05951 | 0.23346 | 0.036621 | 123.1934 | 122.85 | 15.7333 | -123.175 | 123.1796 | 123.0881 | 20.2698 | -123.2254
995.6406 | 123.0698 | -16.0538 | 107.0114 | 0.12559 | 0.056233 | 0.073105 | 0.034976 | 0.049125 | 0.017572 | -0.01465 | 0.34212 | -0.017592 | 0.063737 | 0.054145 | 0.017383 | -0.028944 | 106.7139 | -15.3168 | 0.004578 | -16.3193 | 107.0984 | -16.1362 | -16.2277 | -16.0629 | 5.1407 | -15.921 | 107.135 | 107.0709 | -16.1545 | -16.1728 | -0.082397 | -0.17395 | 0.086975 | 0.737 | -0.2655 | -0.091553 | -0.29755 | -0.10071 | -0.11902 | 0.1236 | -0.009155 | 0.13275 | 0.25177 | 0.059509 | 123.1522 | 122.7676 | 16.0583 | -123.2391 | 123.1888 | 123.1247 | 21.1945 | -123.1842
996.6406 | 123.111 | -15.3717 | 107.6614 | 0.41551 | 0.042347 | 0.075241 | 0.028567 | 0.041648 | 0.0090271 | -0.010377 | 0.40315 | -0.016524 | 0.041307 | 0.050941 | 0.012042 | -0.021467 | 107.4234 | -14.4974 | 0.027466 | -15.6097 | 107.7805 | -15.4633 | -15.5548 | -15.3992 | 4.4907 | -15.3351 | 107.8079 | 107.7209 | -15.4953 | -15.5411 | -0.091553 | -0.18311 | 0.11902 | 0.87433 | -0.23804 | -0.054931 | -0.23804 | -0.1236 | -0.16937 | 0.14648 | -0.027466 | 0.036621 | 0.20599 | 0.059509 | 123.1522 | 122.7951 | 15.3992 | -123.2162 | 123.1796 | 123.0927 | 19.8624 | -123.2025
997.6406 | 123.1842 | -16.0721 | 106.9107 | 0.29344 | 0.011372 | -0.22276 | 0.034976 | 0.052329 | -0.036902 | -0.036012 | 0.37263 | -0.041091 | 0.048783 | 0.038123 | 0.0045661 | -0.006513 | 106.81 | -14.1174 | 0.16022 | -16.1957 | 107.0801 | -16.0309 | -16.1591 | -16.0446 | 4.1794 | -15.8981 | 107.0343 | 106.9702 | -16.1957 | -16.2094 | 0.041199 | -0.086975 | 0.16937 | 1.9547 | -0.1236 | -0.036621 | -0.10071 | -0.1236 | -0.13733 | 0.1236 | 0.027466 | 0.17395 | 0.31128 | 0.059509 | 123.1522 | 122.8821 | 16.2323 | -123.0698 | 123.1064 | 123.0423 | 20.2515 | -123.1201
998.6406 | 123.1293 | -16.2689 | 106.7596 | 0.41551 | 0.032734 | 0.06456 | 0.036044 | 0.032035 | 0.0036861 | -0.03708 | 0.32686 | -0.020796 | 0.053056 | 0.034919 | 0.029132 | -0.027876 | 106.6086 | -15.2481 | 0.073242 | -16.4612 | 106.9153 | -16.2872 | -16.3788 | -16.2415 | 4.8706 | -16.301 | 106.8924 | 106.8604 | -16.3834 | -16.4108 | -0.01831 | -0.10986 | 0.15564 | 1.0208 | -0.19226 | -0.082398 | -0.15106 | -0.11444 | -0.14191 | 0.13275 | 0.027466 | -0.032043 | 0.10986 | 0.10071 | 123.1842 | 122.8775 | 16.3422 | -123.1384 | 123.1613 | 123.1293 | 21.1395 | -123.1705
999.6406 | 123.2208 | -17.157 | 105.8121 | 0.58335 | 0.026326 | 0.072037 | 0.034976 | 0.049125 | -0.0037909 | -0.023195 | 0.50996 | -0.025069 | 0.070146 | 0.057349 | 0.015247 | -0.016126 | 105.6702 | -16.3559 | 0.21057 | -17.3996 | 105.9448 | -17.2256 | -17.3264 | -17.0929 | 5.2414 | -17.0837 | 105.9723 | 105.867 | -17.2897 | -17.3309 | -0.068665 | -0.16937 | 0.13275 | 0.80109 | -0.24262 | -0.073242 | -0.14191 | -0.13275 | -0.17395 | 0.16022 | 0.064086 | 0.073242 | 0.24719 | 0.054931 | 123.1018 | 122.8271 | 17.3676 | -123.1384 | 123.1293 | 123.024 | 22.3984 | -123.143
1000.6406 | 123.2162 | -16.4886 | 106.4758 | 0.59861 | 0.035939 | 0.075241 | 0.03284 | 0.04592 | -0.012336 | -0.023195 | 0.41841 | -0.034682 | 0.055192 | 0.048804 | 0.0067021 | -0.01399 | 106.485 | -15.6692 | 0.07782 | -16.6214 | 106.5582 | -16.5756 | -16.6626 | -16.4246 | 5.1178 | -16.3696 | 106.5903 | 106.5216 | -16.5985 | -16.658 | -0.086976 | -0.17395 | 0.082398 | 0.8194 | -0.13275 | 0.041199 | 0.009155 | -0.10986 | -0.16937 | 0.11444 | 0.064086 | 0.11902 | 0.28839 | 0.045776 | 123.0469 | 122.9736 | 16.5665 | -123.1384 | 123.0789 | 123.0103 | 21.6064 | -123.1338
1001.6406 | 123.1934 | -16.214 | 106.7642 | 0.40025 | 0.022053 | 0.080581 | 0.028567 | 0.058738 | -0.0027229 | -0.025331 | 0.4947 | -0.036818 | 0.043443 | 0.049872 | 0.0034971 | -0.023603 | 106.7505 | -15.271 | 0.33875 | -16.3193 | 106.9519 | -16.2003 | -16.2643 | -16.0034 | 6.1707 | -16.0767 | 106.9382 | 106.8466 | -16.2827 | -16.3605 | 0.013733 | -0.050354 | 0.18768 | 0.94299 | -0.10529 | -0.054932 | -0.013733 | -0.068665 | -0.14648 | 0.17395 | 0.21057 | 0.13733 | 0.28381 | 0.082398 | 123.1659 | 122.9645 | 16.5527 | -123.0286 | 123.1522 | 123.0606 | 22.3846 | -123.1247
1002.6406 | 123.1338 | -16.2781 | 106.7688 | -0.2864 | 0.022053 | 0.073105 | 0.031771 | 0.050193 | -0.013404 | -0.031739 | -0.2072 | -0.032546 | 0.048783 | 0.033851 | 0.0067021 | -0.026808 | 106.6452 | -15.0421 | 0.41657 | -16.4062 | 106.8649 | -16.2918 | -16.3834 | -16.0492 | 6.6925 | -16.0812 | 106.9244 | 106.842 | -16.3651 | -16.3879 | -0.013733 | -0.10529 | 0.09613 | 1.236 | -0.12817 | -0.022888 | -0.1236 | -0.086975 | -0.10986 | 0.15564 | 0.22888 | 0.19684 | 0.3067 | 0.073242 | 123.143 | 122.9233 | 16.6946 | -123.1522 | 123.2025 | 123.1201 | 22.9706 | -123.1567
1003.6406 | 123.1888 | -16.7404 | 106.2561 | 0.3087 | 0.0017592 | 0.067764 | 0.024295 | 0.041648 | -0.018744 | -0.033876 | 0.28108 | -0.030409 | 0.040239 | 0.0456 | -0.00077485 | -0.021467 | 105.8762 | -16.0767 | 0.31586 | -17.1204 | 106.2241 | -16.9464 | -17.0059 | -16.5894 | 6.5277 | -16.6031 | 106.3477 | 106.2515 | -16.8823 | -16.9189 | -0.20599 | -0.2655 | -0.032044 | 0.66376 | -0.37994 | -0.11444 | -0.37994 | -0.14191 | -0.17853 | 0.091552 | 0.15106 | 0.13733 | 0.31586 | -0.004578 | 122.9645 | 122.6166 | 17.0563 | -123.262 | 123.0881 | 122.9919 | 23.2681 | -123.175
1004.6406 | 123.175 | -16.5207 | 106.4941 | 0.32395 | 0.0081682 | 0.075241 | 0.017886 | 0.04058 | -0.025153 | -0.034944 | 0.2353 | -0.026137 | 0.049852 | 0.038123 | 0.016315 | -0.018263 | 106.3202 | -15.5869 | 0.42572 | -16.7267 | 106.6315 | -16.5619 | -16.6489 | -16.3605 | 6.1111 | -16.4062 | 106.5948 | 106.4987 | -16.6626 | -16.6718 | -0.041199 | -0.12817 | 0.13733 | 0.93384 | -0.20599 | -0.07782 | -0.17395 | -0.14191 | -0.15106 | 0.10071 | 0.16022 | 0.11444 | 0.2655 | 0.004577 | 123.1522 | 122.8409 | 16.9464 | -123.143 | 123.1155 | 123.0194 | 22.6318 | -123.1659
1005.6406 | 123.1705 | -16.6168 | 106.3614 | 0.11033 | 0.0071002 | 0.070968 | 0.036044 | 0.043784 | -0.0069949 | -0.033876 | 0.3116 | -0.026137 | 0.051988 | 0.042396 | 0.0056341 | -0.021467 | 106.1829 | -15.8569 | 0.49439 | -16.864 | 106.4896 | -16.6718 | -16.777 | -16.5024 | 6.958 | -16.507 | 106.4987 | 106.3843 | -16.7633 | -16.777 | -0.054932 | -0.16022 | 0.12817 | 0.75989 | -0.24719 | -0.086975 | -0.17853 | -0.14648 | -0.16022 | 0.13733 | 0.11444 | 0.10986 | 0.27008 | 0.022888 | 123.1064 | 122.7997 | 17.1112 | -123.1384 | 123.1155 | 123.0011 | 23.5748 | -123.1384
1006.6406 | 123.1979 | -16.4978 | 106.4804 | 0.095073 | -0.014263 | 0.082718 | 0.013613 | 0.035239 | -0.0080629 | -0.036012 | 0.067459 | -0.031478 | 0.05092 | 0.0456 | 0.01311 | -0.027876 | 106.4209 | -15.8798 | 0.56305 | -16.5985 | 106.6681 | -16.5024 | -16.5894 | -16.2643 | 7.0679 | -16.2689 | 106.6772 | 106.5674 | -16.5848 | -16.6397 | -0.004577 | -0.091552 | 0.18768 | 0.61798 | -0.10071 | -0.009156 | -0.05951 | -0.086975 | -0.14191 | 0.19684 | 0.23346 | 0.22888 | 0.37079 | 0.086975 | 123.1659 | 122.9187 | 17.0609 | -123.0698 | 123.175 | 123.0652 | 23.5657 | -123.1201
1007.6406 | 123.0698 | -16.0355 | 106.9931 | 0.4918 | 0.034871 | 0.066696 | 0.046725 | 0.053397 | 0.026116 | -0.025331 | 0.26582 | -0.014388 | 0.066941 | 0.048804 | 0.018451 | -0.032148 | 106.8054 | -15.3305 | 0.44861 | -16.2827 | 107.1396 | -16.0675 | -16.1636 | -15.8936 | 6.9305 | -15.9851 | 107.1442 | 107.0389 | -16.1682 | -16.1911 | -0.032044 | -0.12817 | 0.14648 | 0.70496 | -0.24719 | -0.11902 | -0.18768 | -0.13275 | -0.15564 | 0.15106 | 0.14191 | 0.050354 | 0.20599 | 0.045776 | 123.175 | 122.8409 | 16.4841 | -123.1567 | 123.1796 | 123.0743 | 22.966 | -123.1842
1008.6406 | 123.1705 | -15.8707 | 107.1213 | -1.3087 | 0.017781 | 0.074173 | 0.039248 | 0.034171 | -0.0037909 | -0.029603 | -0.28349 | -0.037886 | 0.053056 | 0.055213 | 0.0077701 | -0.028944 | 106.9794 | -15.2161 | 0.62714 | -16.0446 | 107.2083 | -15.9302 | -16.0126 | -15.6326 | 6.752 | -15.6418 | 107.2769 | 107.1945 | -15.9805 | -16.0309 | -0.059509 | -0.14191 | 0.086975 | 0.6546 | -0.17395 | -0.032044 | -0.14191 | -0.10986 | -0.16022 | 0.15564 | 0.23804 | 0.22888 | 0.3891 | 0.073242 | 123.0789 | 122.85 | 16.4978 | -123.1339 | 123.1476 | 123.0652 | 22.6227 | -123.1522
1009.6875 | 123.0515 | -15.358 | 107.7347 | 0.17137 | 0.049824 | 0.074173 | 0.024295 | 0.052329 | 0.026116 | -0.0071733 | 0.0064239 | -0.033614 | 0.049852 | 0.052009 | 0.018451 | -0.043897 | 107.5562 | -14.7034 | 0.81024 | -15.4907 | 107.8903 | -15.3397 | -15.4587 | -15.2023 | 9.3063 | -15.3305 | 107.8171 | 107.7301 | -15.4907 | -15.5365 | 0.01831 | -0.10071 | 0.15564 | 0.6546 | -0.13275 | -0.032044 | -0.17853 | -0.13275 | -0.17853 | 0.082398 | 0.15564 | 0.027466 | 0.20599 | -0.004577 | 123.2483 | 122.9141 | 16.1682 | -123.1934 | 123.175 | 123.0881 | 24.6643 | -123.2712
1010.6406 | 123.143 | -15.7791 | 107.3593 | -0.27114 | 0.0060322 | 0.076309 | 0.017886 | 0.043784 | -0.0091309 | -0.029603 | -0.29875 | -0.029341 | 0.060533 | 0.047736 | 0.0056341 | -0.03108 | 107.0068 | -15.0192 | 0.90637 | -15.9988 | 107.3135 | -15.8936 | -15.9897 | -15.6555 | 8.9813 | -15.8066 | 107.3502 | 107.2632 | -15.9256 | -15.9576 | -0.11444 | -0.21057 | -0.045776 | 0.75989 | -0.21973 | -0.009155 | -0.35248 | -0.14648 | -0.17853 | -0.009155 | 0.1236 | -0.027466 | 0.15106 | -0.09613 | 123.0927 | 122.786 | 16.6855 | -123.349 | 123.1293 | 123.0423 | 24.7604 | -123.317
1011.6406 | 123.0927 | -16.2735 | 106.7963 | -0.22536 | 0.011372 | 0.082718 | 0.039248 | 0.050193 | -0.0016549 | -0.016786 | -0.92436 | -0.03575 | 0.063737 | 0.048804 | 0.014179 | -0.030012 | 106.4941 | -15.8478 | 0.84686 | -16.5207 | 106.8558 | -16.3834 | -16.4474 | -16.1133 | 12.0483 | -16.1774 | 106.929 | 106.81 | -16.4062 | -16.4474 | -0.10986 | -0.17395 | 0.059509 | 0.42572 | -0.24719 | -0.073242 | -0.30212 | -0.13275 | -0.17395 | 0.13275 | 0.16022 | 0.096131 | 0.27008 | 0.013733 | 123.1293 | 122.7676 | 17.1204 | -123.2437 | 123.2025 | 123.0835 | 28.3218 | -123.2437
1012.6406 | 123.143 | -16.4246 | 106.6315 | -0.43899 | 0.020985 | 0.068832 | 0.034976 | 0.043784 | -0.0037909 | -0.024263 | -0.4666 | -0.022933 | 0.042375 | 0.039191 | 0.0099061 | -0.020399 | 106.398 | -15.9393 | 0.80566 | -16.6214 | 106.7734 | -16.4658 | -16.5756 | -16.2598 | 12.6114 | -16.2598 | 106.8008 | 106.7093 | -16.5253 | -16.5527 | -0.041198 | -0.15106 | 0.14191 | 0.48523 | -0.19684 | -0.045776 | -0.23346 | -0.10071 | -0.12817 | 0.16937 | 0.1648 | 0.1648 | 0.29297 | 0.07782 | 123.1979 | 122.8226 | 17.2302 | -123.2071 | 123.2254 | 123.1339 | 29.0359 | -123.1842
1013.6406 | 123.143 | -16.3925 | 106.6727 | -0.25588 | 0.040211 | 0.068832 | 0.031771 | 0.044852 | -0.0016549 | -0.022126 | 0.20479 | -0.027205 | 0.049852 | 0.040259 | 0.017383 | -0.030012 | 106.4484 | -15.6509 | 1.1032 | -16.571 | 106.8649 | -16.3467 | -16.4749 | -16.1819 | 13.2706 | -16.2827 | 106.8146 | 106.7368 | -16.4658 | -16.5161 | 0.045776 | -0.082398 | 0.19226 | 0.74158 | -0.17853 | -0.09613 | -0.2243 | -0.073242 | -0.1236 | 0.14191 | 0.21057 | 0.10986 | 0.23346 | 0.064087 | 123.2574 | 122.8409 | 17.4957 | -123.1476 | 123.2071 | 123.1293 | 29.6631 | -123.1888
1014.6406 | 123.0469 | -16.2918 | 106.7734 | 0.35447 | 0.042347 | 0.067764 | 0.033908 | 0.037375 | 0.021844 | -0.015718 | 0.067459 | -0.017592 | 0.053056 | 0.035987 | 0.022724 | -0.023603 | 106.5903 | -15.6326 | 0.8194 | -16.4429 | 106.9519 | -16.2872 | -16.3742 | -16.1362 | 11.7325 | -16.2186 | 106.9107 | 106.8192 | -16.3925 | -16.4246 | 0.004578 | -0.082398 | 0.17853 | 0.65918 | -0.15106 | -0.068664 | -0.1831 | -0.10071 | -0.13275 | 0.13733 | 0.15564 | 0.073242 | 0.20599 | 0.045777 | 123.2437 | 122.8821 | 17.1112 | -123.1476 | 123.2025 | 123.111 | 28.0243 | -123.1979
1015.6406 | 123.1201 | -16.4795 | 106.5445 | 0.018779 | 0.037007 | 0.0699 | 0.033908 | 0.061942 | 0.014367 | -0.015718 | -0.14616 | -0.026137 | 0.060533 | 0.0456 | 0.020587 | -0.030012 | 106.4209 | -15.9897 | 0.90637 | -16.6855 | 106.6864 | -16.5298 | -16.6306 | -16.2186 | 12.8815 | -16.2643 | 106.7093 | 106.6269 | -16.5527 | -16.6077 | -0.050354 | -0.15106 | 0.14191 | 0.48981 | -0.20599 | -0.054932 | -0.1236 | -0.073242 | -0.12817 | 0.16479 | 0.26093 | 0.21515 | 0.34332 | 0.082397 | 123.1659 | 122.9004 | 17.3859 | -123.175 | 123.1888 | 123.1064 | 29.361 | -123.1522
1016.6406 | 123.1522 | -16.6397 | 106.4026 | -0.011739 | 0.04662 | 0.066696 | 0.037112 | 0.057669 | 0.0036861 | -0.010377 | -0.10039 | -0.027205 | 0.054124 | 0.049872 | 0.025928 | -0.021467 | 106.2515 | -15.0604 | 1.1444 | -16.7953 | 106.5582 | -16.6901 | -16.7633 | -16.3559 | 10.8215 | -16.4474 | 106.5674 | 106.5125 | -16.6946 | -16.7267 | -0.050354 | -0.1236 | 0.15564 | 1.5793 | -0.15564 | -0.032043 | -0.15106 | -0.054932 | -0.086976 | 0.1648 | 0.28381 | 0.19226 | 0.27924 | 0.10986 | 123.1979 | 122.8912 | 17.7841 | -123.1659 | 123.2071 | 123.1522 | 27.4612 | -123.1293
1017.6406 | 123.1247 | -16.1865 | 106.8054 | 0.14085 | 0.043416 | 0.070968 | 0.039248 | 0.044852 | 0.0079581 | 0.015258 | -0.0088351 | -0.019728 | 0.066941 | 0.047736 | 0.020587 | -0.028944 | 106.8649 | -13.7833 | 0.90179 | -16.2048 | 107.1716 | -16.0675 | -16.1453 | -15.9668 | 11.1649 | -16.0858 | 107.0389 | 106.9565 | -16.2552 | -16.3239 | 0.11902 | 0.041198 | 0.36621 | 2.4033 | -0.018311 | -0.059509 | 0.059509 | -0.068665 | -0.13733 | 0.23346 | 0.21973 | 0.10071 | 0.23804 | 0.15106 | 123.3582 | 123.0515 | 17.0883 | -122.9507 | 123.2254 | 123.143 | 27.3514 | -123.1293
1018.6406 | 123.1659 | -15.6326 | 107.3868 | -0.11855 | 0.033803 | 0.061355 | 0.036044 | 0.043784 | 0.0068901 | -0.021058 | -0.2072 | -0.015456 | 0.06801 | 0.0456 | 0.012042 | -0.024671 | 107.0938 | -12.9181 | 0.72784 | -15.9348 | 107.3914 | -15.8249 | -15.9073 | -15.4449 | 17.2256 | -15.5228 | 107.5012 | 107.4051 | -15.7516 | -15.77 | -0.19226 | -0.27466 | 0.004577 | 2.7145 | -0.30212 | -0.027465 | -0.29297 | -0.11902 | -0.13733 | 0.11444 | 0.18768 | 0.10986 | 0.24719 | 0.01831 | 123.024 | 122.7264 | 16.3605 | -123.2941 | 123.1338 | 123.0377 | 32.8583 | -123.1567
1019.6406 | 123.1018 | -15.3351 | 107.7164 | 0.24766 | 0.053029 | 0.074173 | 0.037112 | 0.048056 | 0.0036861 | -0.0082413 | 0.036941 | -0.010115 | 0.059465 | 0.049872 | 0.02486 | -0.023603 | 107.4921 | -12.5107 | 0.75531 | -15.5045 | 107.8445 | -15.3854 | -15.4633 | -15.1062 | 13.2248 | -15.2527 | 107.8766 | 107.7759 | -15.4541 | -15.5045 | -0.050354 | -0.12817 | 0.12817 | 2.8244 | -0.16937 | -0.041199 | -0.22431 | -0.11902 | -0.16937 | 0.16022 | 0.22888 | 0.082397 | 0.25177 | 0.059509 | 123.1796 | 122.8271 | 16.0904 | -123.1796 | 123.2117 | 123.111 | 28.5599 | -123.2208
1020.6406 | 123.0789 | -15.8707 | 107.1671 | 0.46128 | 0.035939 | 0.068832 | 0.034976 | 0.052329 | 0.0026181 | -0.011445 | 0.3116 | 0.0059056 | 0.047715 | 0.041327 | -0.0039789 | -0.021467 | 106.9702 | -12.9044 | 0.91553 | -16.008 | 107.3456 | -15.8798 | -15.9622 | -15.6601 | 12.6984 | -15.7791 | 107.341 | 107.2266 | -15.9851 | -16.0263 | -0.009155 | -0.091552 | 0.17853 | 2.9663 | -0.13733 | -0.045777 | -0.19684 | -0.11444 | -0.15564 | 0.17395 | 0.21057 | 0.091553 | 0.24719 | 0.059509 | 123.2162 | 122.8409 | 16.7862 | -123.1293 | 123.2117 | 123.0972 | 28.569 | -123.1934
1021.6406 | 123.1064 | -15.4633 | 107.547 | -4.5436 | 0.027394 | 0.050674 | 0.037112 | 0.027762 | 0.0036861 | -0.029603 | 0.43367 | -0.027205 | 0.054124 | 0.047736 | 0.018451 | -0.026808 | 107.4188 | -12.4512 | 0.86517 | -15.6326 | 107.7621 | -15.4678 | -15.5502 | -15.2939 | 12.7258 | -15.39 | 107.7621 | 107.6752 | -15.5869 | -15.5914 | -0.004577 | -0.086975 | 0.21515 | 3.0121 | -0.16937 | -0.082397 | -0.12817 | -0.1236 | -0.12817 | 0.21515 | 0.16937 | 0.073242 | 0.20142 | 0.12817 | 123.2254 | 122.8821 | 16.3284 | -123.0972 | 123.2254 | 123.1384 | 28.1891 | -123.1384
1022.6406 | 123.1613 | -15.7562 | 107.2586 | 0.40025 | 0.038075 | 0.06456 | 0.027499 | 0.049125 | -0.0069949 | -0.021058 | 0.50996 | -0.017592 | 0.064805 | 0.054145 | 0.0045661 | -0.028944 | 107.1442 | -12.6343 | 0.65002 | -15.9073 | 107.4738 | -15.7379 | -15.8478 | -15.4633 | 12.6114 | -15.683 | 107.4142 | 107.3502 | -15.8478 | -15.8844 | 0.018311 | -0.091552 | 0.21515 | 3.1219 | -0.15106 | -0.05951 | -0.11444 | -0.091552 | -0.12817 | 0.15564 | 0.29297 | 0.073243 | 0.20142 | 0.091553 | 123.23 | 122.9004 | 16.4062 | -123.1064 | 123.1705 | 123.1064 | 28.3676 | -123.143
1023.6406 | 123.1979 | -15.5182 | 107.4417 | 0.59861 | 0.045552 | 0.060287 | 0.03284 | 0.046988 | 0.0036861 | -0.011445 | 0.4947 | -0.025069 | 0.06801 | 0.02851 | 0.015247 | -0.022535 | 107.2723 | -12.5061 | 0.86517 | -15.7516 | 107.5607 | -15.6006 | -15.7059 | -15.239 | 12.6617 | -15.3671 | 107.6157 | 107.515 | -15.6189 | -15.683 | -0.082398 | -0.18768 | 0.11902 | 3.0121 | -0.23346 | -0.045776 | -0.16937 | -0.10071 | -0.16479 | 0.17395 | 0.27923 | 0.15106 | 0.31586 | 0.073243 | 123.0789 | 122.7905 | 16.3834 | -123.1476 | 123.1338 | 123.0331 | 28.1799 | -123.1247
1024.6406 | 123.2254 | -15.477 | 107.4738 | 0.3087 | 0.025258 | 0.072037 | 0.036044 | 0.038443 | -0.0037909 | -0.0082413 | 0.66255 | -0.019728 | 0.05092 | 0.030646 | 0.010974 | -0.01399 | 107.3364 | -12.3825 | 1.5701 | -15.6372 | 107.6294 | -15.5273 | -15.6189 | -15.1794 | 18.869 | -15.358 | 107.6111 | 107.5607 | -15.6097 | -15.6601 | -0.050354 | -0.14191 | 0.15564 | 3.0945 | -0.16022 | -0.018311 | -0.13733 | -0.13275 | -0.1831 | 0.13733 | 0.29755 | 0.11902 | 0.30212 | 0.086975 | 123.1064 | 122.8134 | 17.0471 | -123.0927 | 123.0881 | 123.0377 | 34.346 | -123.1338
1025.6406 | 123.2208 | -15.1062 | 107.8262 | 0.61387 | 0.040211 | 0.080581 | 0.033908 | 0.048056 | -0.0048589 | -0.026399 | 0.34212 | -0.022933 | 0.066941 | 0.027442 | 0.019519 | -0.026808 | 107.6706 | -12.2772 | 1.3916 | -15.3305 | 107.9681 | -15.2115 | -15.3168 | -14.7675 | 14.6255 | -14.8727 | 108.0048 | 107.959 | -15.2298 | -15.271 | -0.10529 | -0.21057 | 0.14191 | 2.829 | -0.2243 | -0.013733 | -0.15564 | -0.1236 | -0.16479 | 0.17853 | 0.33875 | 0.23346 | 0.39825 | 0.13275 | 123.0743 | 122.7768 | 16.4978 | -123.143 | 123.111 | 123.0652 | 29.7317 | -123.0972
1026.6406 | 123.175 | -16.6168 | 106.366 | 0.4918 | 0.02953 | 0.083786 | 0.026431 | 0.051261 | -0.023017 | -0.028535 | 0.61677 | -0.031478 | 0.046647 | 0.042396 | -0.0029109 | -0.016126 | 106.192 | -13.1561 | 1.3046 | -16.832 | 106.4758 | -16.6901 | -16.7679 | -16.3055 | 15.5273 | -16.4749 | 106.517 | 106.4575 | -16.7221 | -16.7404 | -0.073242 | -0.15106 | 0.10986 | 3.4607 | -0.21515 | -0.064087 | -0.17395 | -0.10529 | -0.1236 | 0.15106 | 0.31128 | 0.14191 | 0.2655 | 0.091553 | 123.0927 | 122.8088 | 17.9214 | -123.1338 | 123.1338 | 123.0743 | 32.1442 | -123.1064
1027.6406 | 123.143 | -16.7908 | 106.1874 | 0.4918 | 0.011372 | 0.079513 | 0.03284 | 0.04058 | -0.018744 | -0.026399 | 0.22005 | -0.027205 | 0.053056 | 0.048804 | 0.0034971 | -0.030012 | 106.0135 | -13.1058 | 0.62256 | -17.0242 | 106.3019 | -16.8411 | -16.9327 | -16.4658 | 18.0496 | -16.7267 | 106.3614 | 106.2744 | -16.8869 | -16.9464 | -0.050354 | -0.14191 | 0.11444 | 3.685 | -0.23346 | -0.091553 | -0.17395 | -0.096131 | -0.15564 | 0.17395 | 0.32501 | 0.064086 | 0.21973 | 0.086975 | 123.0927 | 122.8043 | 17.4133 | -123.1201 | 123.1522 | 123.0652 | 34.8404 | -123.1338
1028.6406 | 123.1888 | -16.5756 | 106.4117 | 0.29344 | 0.0071002 | 0.0699 | 0.037112 | 0.038443 | -0.01554 | -0.033876 | 0.35738 | -0.033614 | 0.045579 | 0.041327 | 0.00029315 | -0.018263 | 106.1646 | -13.0417 | 1.2863 | -16.8365 | 106.4758 | -16.6901 | -16.7908 | -16.301 | 18.7042 | -16.5161 | 106.5262 | 106.4484 | -16.713 | -16.7496 | -0.11444 | -0.21515 | 0.064087 | 3.5339 | -0.26093 | -0.045777 | -0.24719 | -0.13733 | -0.17395 | 0.11444 | 0.27466 | 0.05951 | 0.23346 | 0.036621 | 123.0515 | 122.7402 | 17.8619 | -123.2025 | 123.1018 | 123.024 | 35.2798 | -123.1613
1029.6406 | 123.1888 | -17.2348 | 105.78 | 0.24766 | 0.00069119 | 0.080581 | 0.033908 | 0.02883 | -0.011268 | -0.03708 | -0.10039 | -0.025069 | 0.049852 | 0.053077 | 0.01311 | -0.023603 | 105.5649 | -13.4903 | 1.3916 | -17.4637 | 105.867 | -17.308 | -17.3904 | -16.9785 | 18.544 | -17.1936 | 105.8624 | 105.7892 | -17.3584 | -17.3904 | -0.073242 | -0.15564 | 0.086975 | 3.7445 | -0.22888 | -0.073242 | -0.21515 | -0.1236 | -0.15564 | 0.082398 | 0.25635 | 0.041198 | 0.19684 | 0.009156 | 123.1018 | 122.7997 | 18.6264 | -123.1705 | 123.0972 | 123.024 | 35.7788 | -123.1705
1030.6406 | 123.2483 | -16.0492 | 106.9611 | 0.095073 | 0.0017592 | 0.080581 | 0.03284 | 0.026694 | -0.023017 | -0.03708 | 0.067459 | -0.034682 | 0.054124 | 0.0456 | 0.0099061 | -0.041761 | 106.929 | -12.6251 | 1.4465 | -16.1819 | 107.1259 | -16.0263 | -16.1545 | -15.8478 | 19.0842 | -15.9164 | 107.0663 | 106.9656 | -16.1682 | -16.1865 | 0.022888 | -0.10529 | 0.16479 | 3.4241 | -0.13275 | -0.027466 | -0.032044 | -0.11902 | -0.13733 | 0.10528 | 0.20142 | 0.13275 | 0.27008 | 0.004577 | 123.175 | 122.9782 | 17.4957 | -123.1155 | 123.1155 | 123.0148 | 35.1334 | -123.1476
1031.6875 | 123.0972 | -16.301 | 106.778 | -0.31691 | 0.0071002 | 0.0699 | 0.033908 | 0.049125 | 0.0090271 | -0.027467 | -0.4666 | -0.025069 | 0.066941 | 0.047736 | 0.025928 | -0.027876 | 106.5353 | -12.767 | 1.4786 | -16.4749 | 106.9153 | -16.3376 | -16.42 | -16.1682 | 18.4067 | -16.3193 | 106.9382 | 106.8192 | -16.3925 | -16.452 | -0.036621 | -0.11902 | 0.13733 | 3.5339 | -0.17395 | -0.054932 | -0.24262 | -0.091553 | -0.15106 | 0.16022 | 0.13275 | -0.018311 | 0.13275 | 0.041199 | 123.2162 | 122.8363 | 17.7795 | -123.1979 | 123.2391 | 123.1201 | 34.7076 | -123.23
1032.6406 | 123.1934 | -16.4795 | 106.4987 | 0.72068 | -0.0014448 | 0.080581 | 0.029635 | 0.044852 | -0.018744 | -0.023195 | 0.067459 | -0.033614 | 0.037034 | 0.046668 | 0.0056341 | -0.019331 | 106.2927 | -12.9913 | 1.2863 | -16.7404 | 106.5948 | -16.5985 | -16.6809 | -16.3422 | 21.0571 | -16.3605 | 106.6269 | 106.5125 | -16.6214 | -16.6534 | -0.11902 | -0.20142 | 0.096131 | 3.4882 | -0.26093 | -0.059509 | -0.20599 | -0.14191 | -0.17395 | 0.12817 | 0.13733 | 0.11902 | 0.29297 | 0.013733 | 123.0743 | 122.7722 | 17.7658 | -123.1796 | 123.1064 | 122.9919 | 37.5366 | -123.1522
1033.6406 | 123.2391 | -16.1682 | 106.8008 | 0.21714 | -0.0025128 | 0.075241 | 0.033908 | 0.059806 | -0.023017 | -0.025331 | -0.14616 | -0.029341 | 0.03383 | 0.043464 | 0.012042 | -0.03108 | 106.7139 | -12.5427 | 1.4328 | -16.3467 | 106.9199 | -16.2415 | -16.3101 | -15.9531 | 19.0796 | -15.9805 | 106.9473 | 106.8329 | -16.2781 | -16.3055 | -0.073242 | -0.14191 | 0.11902 | 3.6255 | -0.17853 | -0.036621 | -0.086975 | -0.10986 | -0.13733 | 0.14648 | 0.21515 | 0.18768 | 0.32501 | 0.032044 | 123.0881 | 122.8821 | 17.601 | -123.111 | 123.1155 | 123.0011 | 35.2478 | -123.1064
1034.6406 | 123.1705 | -17.7383 | 105.249 | 0.73594 | 0.019917 | 0.079513 | 0.025363 | 0.057669 | -0.0059269 | -0.029603 | -0.31401 | -0.032546 | 0.057328 | 0.043464 | 0.018451 | -0.034284 | 105.0476 | -16.6946 | 1.7441 | -17.9626 | 105.3314 | -17.8436 | -17.9306 | -17.2897 | 19.6243 | -17.6102 | 105.6152 | 105.423 | -17.6971 | -17.8116 | -0.10529 | -0.19226 | 0.082398 | 1.0437 | -0.2243 | -0.032043 | -0.20142 | 0.041198 | -0.073242 | 0.36621 | 0.44861 | 0.12817 | 0.20142 | 0.17395 | 123.0698 | 122.7859 | 19.4824 | -123.1796 | 123.3536 | 123.1613 | 37.3627 | -123.0606
1035.6406 | 123.1384 | -17.5735 | 105.4962 | -0.30166 | 0.0071002 | 0.085922 | 0.03818 | 0.032035 | 0.0068901 | -0.030671 | -0.40556 | -0.033614 | 0.044511 | 0.041327 | 0.023792 | -0.037489 | 105.336 | -16.0812 | 1.6937 | -17.688 | 105.6152 | -17.569 | -17.6651 | -17.4271 | 19.2444 | -17.4683 | 105.6198 | 105.4871 | -17.6788 | -17.7338 | 0.004577 | -0.091553 | 0.11902 | 1.4923 | -0.11444 | -0.022888 | -0.16022 | -0.10529 | -0.16022 | 0.1236 | 0.14648 | 0.10529 | 0.2655 | -0.009155 | 123.1888 | 122.9095 | 19.2673 | -123.1613 | 123.1934 | 123.0606 | 36.8179 | -123.23
1036.6406 | 123.1155 | -16.6992 | 106.3797 | -0.25588 | 0.019917 | 0.078445 | 0.033908 | 0.039511 | -0.0080629 | -0.025331 | -0.039353 | -0.028273 | 0.05626 | 0.050941 | 0.017383 | -0.040693 | 106.2241 | -13.0692 | 1.6388 | -16.8411 | 106.5033 | -16.6901 | -16.8091 | -16.5253 | 23.3826 | -16.5894 | 106.5491 | 106.4117 | -16.7816 | -16.8274 | 0.009156 | -0.10986 | 0.1236 | 3.6301 | -0.14191 | -0.032043 | -0.15564 | -0.082397 | -0.12817 | 0.16937 | 0.17395 | 0.10986 | 0.23804 | 0.032043 | 123.2025 | 122.9233 | 18.338 | -123.1888 | 123.2483 | 123.111 | 40.0818 | -123.2071
1037.6406 | 123.1064 | -16.0904 | 107.016 | 0.018779 | 0.041279 | 0.089126 | 0.036044 | 0.051261 | 0.00048206 | -0.028535 | -0.37505 | -0.026137 | 0.046647 | 0.033851 | 0.016315 | -0.030012 | 106.6681 | -12.7396 | 1.5747 | -16.3193 | 107.0755 | -16.1545 | -16.2781 | -15.8661 | 23.8541 | -16.0492 | 107.1625 | 107.0114 | -16.2003 | -16.2186 | -0.064087 | -0.18768 | 0.059509 | 3.3508 | -0.22888 | -0.041199 | -0.3479 | -0.10986 | -0.12817 | 0.14648 | 0.2243 | 0.041199 | 0.16937 | -0.004577 | 123.1659 | 122.7585 | 17.6651 | -123.2941 | 123.2529 | 123.1018 | 39.9445 | -123.2346
1038.6406 | 123.1659 | -16.1636 | 106.9153 | -0.31691 | 0.0049632 | 0.068832 | 0.03284 | 0.04592 | -0.0016549 | -0.010377 | -0.39031 | -0.015456 | 0.040239 | 0.034919 | 0.021655 | -0.018263 | 106.6177 | -12.7808 | 1.6205 | -16.3788 | 107.0206 | -16.2598 | -16.3467 | -16.0126 | 23.2773 | -16.1774 | 107.0389 | 106.8695 | -16.3055 | -16.3513 | -0.096131 | -0.18311 | 0.10529 | 3.3829 | -0.21515 | -0.032043 | -0.29755 | -0.14191 | -0.18768 | 0.1236 | 0.15106 | -0.013733 | 0.17395 | -0.045776 | 123.1842 | 122.7814 | 17.7841 | -123.262 | 123.2025 | 123.0331 | 39.4409 | -123.2666
1039.7031 | 123.1064 | -16.5482 | 106.5353 | 0.064555 | 0.049824 | 0.080581 | 0.045657 | 0.056601 | 0.021844 | -0.01465 | -0.25298 | -0.0090474 | 0.047715 | 0.048804 | 0.0302 | -0.027876 | 106.2744 | -13.1561 | 1.7441 | -16.777 | 106.5445 | -16.6809 | -16.777 | -16.4383 | 23.0942 | -16.5436 | 106.5811 | 106.4621 | -16.713 | -16.7541 | -0.13275 | -0.22888 | 0.009156 | 3.392 | -0.22888 | 0 | -0.26093 | -0.1648 | -0.20599 | 0.045777 | 0.10986 | 0.004578 | 0.21057 | -0.073242 | 123.0927 | 122.8226 | 18.2922 | -123.3124 | 123.1293 | 123.0103 | 39.6423 | -123.2895
1040.6406 | 123.0972 | -17.5278 | 105.5328 | -1.9343 | 0.038075 | 0.0699 | 0.03818 | 0.046988 | 0.0079581 | -0.018922 | -0.34453 | -0.021865 | 0.051988 | 0.032783 | 0.018451 | -0.028944 | 105.3085 | -13.9069 | 1.5884 | -17.6697 | 105.7068 | -17.5598 | -17.6559 | -17.3996 | 22.6868 | -17.363 | 105.7251 | 105.6107 | -17.5781 | -17.6285 | -0.032043 | -0.12817 | 0.17395 | 3.6209 | -0.14191 | -0.013733 | -0.2243 | -0.050354 | -0.10071 | 0.19226 | 0.12817 | 0.1648 | 0.2655 | 0.07782 | 123.2346 | 122.8363 | 19.1162 | -123.1888 | 123.2529 | 123.1384 | 40.2145 | -123.1613
1041.6406 | 123.1155 | -17.7567 | 105.2444 | 0.079814 | 0.054097 | 0.075241 | 0.036044 | 0.042716 | 0.01864 | -0.011445 | 0.097976 | -0.015456 | 0.047715 | 0.055213 | 0.025928 | -0.035352 | 105.2078 | -13.8382 | 1.7761 | -17.8574 | 105.4688 | -17.7383 | -17.8253 | -17.4912 | 22.4579 | -17.7246 | 105.4413 | 105.3177 | -17.8436 | -17.9077 | 0.018311 | -0.068664 | 0.2243 | 3.9185 | -0.10071 | -0.032044 | -0.036621 | -0.086975 | -0.15106 | 0.19684 | 0.2655 | 0.032044 | 0.18311 | 0.073242 | 123.2254 | 122.9645 | 19.5328 | -123.0698 | 123.1979 | 123.0743 | 40.2145 | -123.1522
1042.6406 | 123.0881 | -17.0883 | 106.0089 | 0.018779 | 0.037007 | 0.067764 | 0.029635 | 0.039511 | 0.013299 | -0.012513 | -0.0088351 | -0.024001 | 0.060533 | 0.037055 | 0.022724 | -0.03108 | 105.78 | -13.3072 | 1.8082 | -17.2714 | 106.0822 | -17.1387 | -17.2073 | -16.951 | 20.1691 | -17.0792 | 106.0638 | 105.9723 | -17.2211 | -17.2623 | -0.050354 | -0.11902 | 0.073242 | 3.7811 | -0.1831 | -0.064087 | -0.22888 | -0.13275 | -0.17395 | 0.054932 | 0.13733 | 0.009155 | 0.1831 | -0.036621 | 123.1705 | 122.8683 | 18.8965 | -123.2162 | 123.1522 | 123.0606 | 37.2574 | -123.2712
1043.6875 | 123.1934 | -17.0425 | 105.954 | 0.59861 | 0.042347 | 0.059219 | 0.030703 | 0.044852 | -0.010199 | -0.025331 | 0.47945 | -0.019728 | 0.054124 | 0.042396 | 0.0099061 | -0.020399 | 105.8304 | -13.1653 | 1.6617 | -17.189 | 106.0638 | -17.0746 | -17.1432 | -16.8549 | 19.5099 | -16.8732 | 106.0959 | 105.9631 | -17.1341 | -17.1799 | -0.032043 | -0.10071 | 0.10986 | 3.8773 | -0.14648 | -0.045776 | -0.1236 | -0.091552 | -0.13733 | 0.14191 | 0.18768 | 0.16937 | 0.3067 | 0.009156 | 123.1064 | 122.8729 | 18.7042 | -123.0972 | 123.1384 | 123.0057 | 36.5524 | -123.1338
1044.6406 | 123.1338 | -16.5939 | 106.4667 | 0.98008 | 0.066914 | 0.074173 | 0.041384 | 0.046988 | 0.012231 | -0.028535 | 0.0064239 | -0.021865 | 0.062669 | 0.048804 | 0.016315 | -0.030012 | 106.3156 | -12.8815 | 1.6388 | -16.777 | 106.5857 | -16.626 | -16.7267 | -16.2918 | 19.6472 | -16.5848 | 106.604 | 106.517 | -16.6901 | -16.7221 | -0.032044 | -0.13275 | 0.11902 | 3.7125 | -0.18311 | -0.050354 | -0.15106 | -0.09613 | -0.12817 | 0.13733 | 0.30212 | 0.009155 | 0.13733 | 0.050354 | 123.1796 | 122.9095 | 18.2327 | -123.1934 | 123.1979 | 123.111 | 36.2412 | -123.1888
1045.6406 | 123.0927 | -15.2618 | 107.7621 | 0.2324 | 0.043416 | 0.072037 | 0.043521 | 0.042716 | 0.011163 | -0.01465 | 0.15901 | -0.019728 | 0.075486 | 0.0456 | 0.016315 | -0.037489 | 107.4875 | -15.0238 | 1.6846 | -15.5228 | 107.8262 | -15.4083 | -15.5136 | -15.0833 | 20.5444 | -14.9963 | 107.9681 | 107.8537 | -15.3717 | -15.3809 | -0.14648 | -0.25177 | 0.064087 | 0.23804 | -0.26093 | -0.009155 | -0.27466 | -0.10986 | -0.11902 | 0.20599 | 0.17853 | 0.2655 | 0.38452 | 0.091553 | 123.0881 | 122.7493 | 16.9464 | -123.2758 | 123.23 | 123.1155 | 35.8063 | -123.143
1046.6406 | 123.0743 | -18.3563 | 104.7134 | 0.18663 | 0.079732 | 0.051742 | 0.052066 | 0.039511 | 0.0047541 | -0.012513 | 0.036941 | -0.011183 | 0.058397 | 0.0456 | 0.018451 | -0.021467 | 104.5303 | -17.8253 | 1.3458 | -18.5532 | 104.8691 | -18.3609 | -18.4662 | -18.1503 | 18.2968 | -18.3014 | 104.8325 | 104.7455 | -18.4616 | -18.4845 | -0.004578 | -0.10986 | 0.15564 | 0.53101 | -0.19684 | -0.086975 | -0.18311 | -0.10529 | -0.12817 | 0.11902 | 0.20599 | 0.054931 | 0.18311 | 0.032043 | 123.2254 | 122.8867 | 19.7021 | -123.1796 | 123.1888 | 123.1018 | 36.6531 | -123.1979
1047.6406 | 123.056 | -18.2556 | 104.805 | 0.24766 | 0.055165 | 0.063492 | 0.030703 | 0.037375 | 0.0079581 | -0.016786 | 0.34212 | -0.015456 | 0.043443 | 0.044532 | 0.02486 | -0.019331 | 104.5258 | -17.9672 | 1.3138 | -18.5349 | 104.892 | -18.3334 | -18.425 | -18.0679 | 17.9398 | -18.2007 | 104.9606 | 104.8691 | -18.3472 | -18.3838 | -0.07782 | -0.16937 | 0.086975 | 0.28839 | -0.27924 | -0.10986 | -0.27924 | -0.091553 | -0.12817 | 0.15564 | 0.18768 | 0.054931 | 0.18311 | 0.064087 | 123.1476 | 122.7814 | 19.5694 | -123.23 | 123.2162 | 123.1247 | 36.1954 | -123.1888
1048.6406 | 123.1384 | -18.5989 | 104.4479 | -0.4695 | 0.017781 | 0.075241 | 0.033908 | 0.049125 | -0.0059269 | -0.023195 | 0.35738 | -0.022933 | 0.058397 | 0.049872 | 0.0099061 | -0.011854 | 104.2053 | -18.1641 | 0.70038 | -18.8324 | 104.5807 | -18.6401 | -18.7225 | -18.4479 | 17.9855 | -18.5394 | 104.5578 | 104.5074 | -18.7042 | -18.7454 | -0.041199 | -0.1236 | 0.13275 | 0.43488 | -0.23346 | -0.10986 | -0.24262 | -0.10529 | -0.14648 | 0.10986 | 0.15106 | 0.059509 | 0.20599 | 0.059509 | 123.1796 | 122.8043 | 19.2993 | -123.1705 | 123.1567 | 123.1064 | 36.5845 | -123.1934
1049.6406 | 123.143 | -18.9148 | 104.0955 | 0.44602 | 0.039143 | 0.065628 | 0.033908 | 0.037375 | -0.0048589 | -0.028535 | 0.46419 | -0.030409 | 0.062669 | 0.050941 | 0.012042 | -0.020399 | 103.9581 | -18.6493 | 0.68207 | -19.1254 | 104.2603 | -18.924 | -19.0247 | -18.7454 | 18.0222 | -18.7637 | 104.2786 | 104.1733 | -19.0201 | -19.0704 | -0.009155 | -0.10986 | 0.16479 | 0.2655 | -0.21057 | -0.10071 | -0.13733 | -0.10529 | -0.15564 | 0.1831 | 0.16937 | 0.15106 | 0.3067 | 0.07782 | 123.175 | 122.8729 | 19.5969 | -123.1201 | 123.1934 | 123.0881 | 36.937 | -123.1659
1050.6406 | 123.175 | -18.3517 | 104.6173 | 0.55284 | 0.033803 | 0.067764 | 0.030703 | 0.039511 | -0.0048589 | -0.026399 | 0.54048 | -0.020796 | 0.058397 | 0.0456 | 0.010974 | -0.020399 | 104.4983 | -18.0496 | 0.86517 | -18.5852 | 104.7684 | -18.4113 | -18.4891 | -17.981 | 17.7063 | -18.2648 | 104.7958 | 104.6951 | -18.4616 | -18.5074 | -0.059509 | -0.13733 | 0.15106 | 0.30212 | -0.23346 | -0.09613 | -0.11902 | -0.10986 | -0.15564 | 0.17853 | 0.37079 | 0.086975 | 0.24261 | 0.077819 | 123.1201 | 122.85 | 19.2169 | -123.1064 | 123.1476 | 123.0469 | 36.058 | -123.1247
1051.6406 | 123.2117 | -18.8416 | 104.0771 | 0.36973 | 0.050892 | 0.0699 | 0.040316 | 0.053397 | -0.0027229 | -0.01999 | 0.43367 | -0.026137 | 0.077623 | 0.041327 | 0.021655 | -0.025739 | 103.9032 | -18.5577 | 0.88348 | -19.0613 | 104.187 | -18.924 | -19.0109 | -18.5211 | 17.5232 | -18.6859 | 104.2694 | 104.2053 | -18.956 | -19.0063 | -0.082397 | -0.16937 | 0.10986 | 0.28381 | -0.21973 | -0.050354 | -0.17395 | -0.11444 | -0.16479 | 0.19226 | 0.32043 | 0.15564 | 0.32043 | 0.12817 | 123.0286 | 122.7448 | 19.725 | -123.0881 | 123.111 | 123.0469 | 36.3647 | -123.0835
1052.6406 | 123.1476 | -19.0704 | 103.862 | 0.56809 | 0.030598 | 0.070968 | 0.037112 | 0.049125 | -0.0080629 | -0.030671 | 0.61677 | -0.03575 | 0.049852 | 0.053077 | 0.019519 | -0.032148 | 103.8757 | -18.6035 | 1.1261 | -19.1986 | 104.068 | -19.0704 | -19.1071 | -18.7225 | 17.0471 | -18.8644 | 104.0543 | 103.9948 | -19.1528 | -19.1895 | 0 | -0.036621 | 0.20599 | 0.46692 | -0.12817 | -0.091552 | 0.013732 | -0.082397 | -0.11902 | 0.19226 | 0.3479 | 0.20599 | 0.32501 | 0.13275 | 123.1384 | 122.9462 | 20.1965 | -122.9691 | 123.1247 | 123.0652 | 36.1176 | -123.0515
1053.6406 | 123.2254 | -19.9585 | 102.9922 | 0.32395 | 0.018849 | 0.062424 | 0.025363 | 0.04592 | 0.0026181 | -0.021058 | 0.63203 | -0.020796 | 0.071214 | 0.049872 | 0.020587 | -0.034284 | 102.9556 | -19.5145 | 1.0117 | -20.1279 | 103.1708 | -19.9585 | -20.0546 | -19.6747 | 13.9069 | -19.8395 | 103.1616 | 103.0563 | -20.0821 | -20.1279 | 0 | -0.09613 | 0.17853 | 0.44403 | -0.16937 | -0.073243 | -0.036622 | -0.1236 | -0.16937 | 0.16937 | 0.28381 | 0.11902 | 0.28839 | 0.064086 | 123.1293 | 122.9141 | 20.9702 | -123.0469 | 123.1201 | 123.0148 | 33.8654 | -123.1201
1054.6406 | 123.1705 | -19.9493 | 103.0243 | 0.21714 | 0.014576 | 0.060287 | 0.034976 | 0.038443 | -0.0080629 | -0.03708 | 0.63203 | -0.045363 | 0.055192 | 0.056281 | 0.016315 | -0.022535 | 102.9327 | -19.5877 | 1.0208 | -20.1828 | 103.125 | -19.9677 | -20.0729 | -19.5923 | 13.9435 | -19.8486 | 103.1387 | 103.1067 | -20.05 | -20.0638 | -0.01831 | -0.1236 | 0.10071 | 0.36163 | -0.23346 | -0.10986 | -0.091553 | -0.10071 | -0.11444 | 0.11444 | 0.35706 | 0.10071 | 0.21515 | 0.082397 | 123.0743 | 122.8821 | 20.9702 | -123.0972 | 123.0881 | 123.056 | 33.8928 | -123.0881
1055.6406 | 123.1934 | -19.6884 | 103.3127 | 0.32395 | -0.0046498 | 0.068832 | 0.040316 | 0.039511 | -0.020881 | -0.03708 | 0.3116 | -0.029341 | 0.058397 | 0.042396 | -0.010388 | -0.020399 | 103.0838 | -19.3359 | 1.0208 | -19.9539 | 103.3905 | -19.7525 | -19.8578 | -19.3634 | 12.2635 | -19.6243 | 103.3768 | 103.3127 | -19.8395 | -19.8807 | -0.064086 | -0.16937 | 0.07782 | 0.35248 | -0.2655 | -0.09613 | -0.22888 | -0.15106 | -0.19226 | 0.064087 | 0.32501 | 0.064087 | 0.25635 | 0 | 123.0789 | 122.7722 | 20.7092 | -123.1705 | 123.0652 | 123.0011 | 31.9519 | -123.1934
1056.6406 | 123.2025 | -20.224 | 102.7588 | 0.29344 | 0.01244 | 0.067764 | 0.020022 | 0.042716 | -0.023017 | -0.039216 | 0.25056 | -0.043227 | 0.043443 | 0.046668 | 0.0045661 | -0.032148 | 102.626 | -19.7754 | 1.4832 | -20.43 | 102.9007 | -20.2469 | -20.3293 | -19.7891 | 11.7416 | -20.1141 | 102.919 | 102.8229 | -20.343 | -20.3705 | -0.022888 | -0.10529 | 0.14191 | 0.44861 | -0.20599 | -0.10071 | -0.13275 | -0.11902 | -0.14648 | 0.16022 | 0.43487 | 0.10986 | 0.25635 | 0.064087 | 123.1247 | 122.85 | 21.7072 | -123.0881 | 123.143 | 123.0469 | 31.9656 | -123.1293
1057.6406 | 123.1934 | -20.224 | 102.7496 | 0.91905 | 0.0028272 | 0.0699 | 0.023226 | 0.04058 | -0.027289 | -0.033876 | 0.11323 | -0.030409 | 0.054124 | 0.02851 | 0.014179 | -0.019331 | 102.6581 | -19.8303 | 1.4877 | -20.4529 | 102.9099 | -20.2423 | -20.311 | -19.7479 | 11.2289 | -20.1187 | 102.919 | 102.8275 | -20.3064 | -20.3659 | -0.018311 | -0.086975 | 0.16022 | 0.39368 | -0.22888 | -0.14191 | -0.091553 | -0.082397 | -0.14191 | 0.16937 | 0.47607 | 0.10529 | 0.24719 | 0.07782 | 123.1338 | 122.8821 | 21.7117 | -123.0606 | 123.143 | 123.0515 | 31.4529 | -123.1155
1058.6406 | 123.2071 | -18.7225 | 104.2511 | 0.12559 | 0.0049632 | 0.08699 | 0.028567 | 0.049125 | -0.018744 | -0.036012 | -0.06987 | -0.036818 | 0.047715 | 0.042396 | 0.01311 | -0.027876 | 104.0726 | -16.0767 | 1.9226 | -18.9972 | 104.3198 | -18.8324 | -18.9423 | -18.3289 | 12.2589 | -18.6447 | 104.361 | 104.2419 | -18.8919 | -18.9285 | -0.10986 | -0.21973 | 0.068664 | 2.6459 | -0.27466 | -0.054931 | -0.17853 | -0.16937 | -0.20599 | 0.10986 | 0.39368 | 0.07782 | 0.28381 | -0.009156 | 123.0423 | 122.7951 | 20.6451 | -123.1934 | 123.0835 | 122.9645 | 30.9814 | -123.1796
1059.6406 | 123.2437 | -17.8986 | 105.0385 | 0.064555 | -0.0014448 | 0.083786 | 0.028567 | 0.048056 | -0.016608 | -0.038148 | 0.067459 | -0.025069 | 0.044511 | 0.047736 | 0.016315 | -0.027876 | 105.0064 | -14.6484 | 1.6708 | -18.0267 | 105.249 | -17.926 | -17.9855 | -17.4271 | 12.3184 | -17.6834 | 105.217 | 105.13 | -18.0222 | -18.0542 | -0.027465 | -0.086975 | 0.21057 | 3.2501 | -0.12817 | -0.041198 | -0.032043 | -0.1236 | -0.15564 | 0.17853 | 0.4715 | 0.21515 | 0.37079 | 0.091553 | 123.1476 | 122.905 | 19.5694 | -123.024 | 123.1155 | 123.0286 | 30.217 | -123.0927
1060.6406 | 123.2254 | -18.0313 | 104.9606 | 0.15611 | -0.012126 | 0.077377 | 0.024295 | 0.02883 | -0.0059269 | -0.031739 | -0.039353 | -0.042159 | 0.045579 | 0.048804 | 0.022724 | -0.034284 | 104.7821 | -14.4516 | 1.8402 | -18.2785 | 105.0247 | -18.1229 | -18.2053 | -17.5003 | 11.6409 | -17.9077 | 105.0797 | 104.9698 | -18.1366 | -18.1824 | -0.091553 | -0.17395 | 0.064087 | 3.5797 | -0.24719 | -0.073242 | -0.17853 | -0.10529 | -0.15106 | 0.11902 | 0.53101 | 0.1236 | 0.27466 | 0.009156 | 123.056 | 122.8134 | 19.8715 | -123.1659 | 123.111 | 123.0011 | 29.6722 | -123.143
1061.6406 | 123.1659 | -17.7292 | 105.2765 | -0.057515 | 0.0071002 | 0.077377 | 0.037112 | 0.044852 | 0.0015501 | -0.026399 | -0.31401 | -0.025069 | 0.043443 | 0.032783 | 0.010974 | -0.041761 | 105.2216 | -13.9893 | 2.1469 | -17.8024 | 105.4779 | -17.6971 | -17.7795 | -17.2256 | 11.8744 | -17.6559 | 105.4184 | 105.2856 | -17.8528 | -17.8986 | 0.032043 | -0.050354 | 0.20142 | 3.7399 | -0.073242 | -0.022888 | -0.054931 | -0.1236 | -0.16937 | 0.14191 | 0.50354 | 0.073242 | 0.24262 | 0.009156 | 123.2071 | 122.9507 | 19.8761 | -123.056 | 123.1476 | 123.0148 | 29.6036 | -123.175
1062.6406 | 123.1384 | -18.7042 | 104.306 | -0.19484 | -0.0057178 | 0.090195 | 0.040316 | 0.041648 | -0.0091309 | -0.027467 | -0.40556 | -0.022933 | 0.05092 | 0.052009 | 0.012042 | -0.03108 | 104.1275 | -14.8773 | 1.7853 | -18.924 | 104.393 | -18.8004 | -18.8919 | -18.1549 | 11.5311 | -18.6127 | 104.512 | 104.3701 | -18.7958 | -18.8507 | -0.09613 | -0.18768 | 0.086975 | 3.8269 | -0.21973 | -0.032043 | -0.17853 | -0.091552 | -0.14648 | 0.20599 | 0.54932 | 0.091553 | 0.23804 | 0.064087 | 123.0972 | 122.8317 | 20.4895 | -123.1979 | 123.2162 | 123.0743 | 30.2353 | -123.1567
1063.6406 | 123.1293 | -18.0313 | 105.043 | -0.24062 | 0.020985 | 0.077377 | 0.046725 | 0.049125 | 0.0058221 | -0.027467 | 0.22005 | -0.032546 | 0.064805 | 0.042396 | 0.012042 | -0.028944 | 104.7684 | -13.9938 | 2.2659 | -18.2648 | 105.1209 | -18.1046 | -18.2007 | -17.5323 | 12.1033 | -17.9718 | 105.1666 | 105.0751 | -18.1549 | -18.1595 | -0.073242 | -0.16937 | 0.07782 | 4.0375 | -0.23346 | -0.064087 | -0.27466 | -0.1236 | -0.12817 | 0.1236 | 0.49896 | 0.059509 | 0.18768 | 0.032043 | 123.1522 | 122.7997 | 20.2972 | -123.2437 | 123.1979 | 123.1064 | 30.1346 | -123.2025
1064.6406 | 123.111 | -18.0817 | 105.0247 | -0.25588 | 0.017781 | 0.077377 | 0.044589 | 0.044852 | 0.0015501 | -0.023195 | -0.37505 | -0.031478 | 0.064805 | 0.039191 | 0.012042 | -0.030012 | 104.7409 | -14.003 | 2.1469 | -18.306 | 105.1025 | -18.1137 | -18.2007 | -17.5781 | 11.8973 | -18.0496 | 105.1437 | 104.9973 | -18.2007 | -18.2327 | -0.032043 | -0.11902 | 0.07782 | 4.0787 | -0.2243 | -0.10529 | -0.28381 | -0.11902 | -0.15106 | 0.11902 | 0.50354 | 0.032043 | 0.18311 | -0.027466 | 123.1842 | 122.8226 | 20.2286 | -123.2254 | 123.2254 | 123.0789 | 29.9789 | -123.2574
1065.6406 | 123.0972 | -18.8599 | 104.187 | -0.24062 | 0.020985 | 0.075241 | 0.03818 | 0.043784 | 0.0047541 | -0.012513 | -2.2519 | -0.025069 | 0.057328 | 0.042396 | 0.016315 | -0.025739 | 103.9536 | -14.7583 | 2.2202 | -19.0796 | 104.3518 | -18.8965 | -18.9468 | -18.338 | 12.0255 | -18.869 | 104.3472 | 104.2099 | -18.9835 | -19.0063 | -0.036621 | -0.086975 | 0.16479 | 4.1016 | -0.21973 | -0.13275 | -0.23346 | -0.1236 | -0.14648 | 0.16022 | 0.52185 | -0.009156 | 0.13733 | 0.022888 | 123.2117 | 122.8134 | 21.08 | -123.1338 | 123.2071 | 123.0698 | 30.8853 | -123.1934
1066.6406 | 123.1522 | -19.0109 | 104.0588 | -0.25588 | 0.011372 | 0.080581 | 0.049929 | 0.060874 | -0.0059269 | -0.024263 | -0.35979 | -0.015456 | 0.05092 | 0.043464 | 0.0067021 | -0.038557 | 103.7521 | -14.5432 | 2.1286 | -19.3039 | 104.0955 | -19.1345 | -19.2169 | -18.5257 | 11.2381 | -19.075 | 104.1641 | 104.0222 | -19.1483 | -19.1849 | -0.1236 | -0.20599 | 0.036621 | 4.4678 | -0.29297 | -0.086975 | -0.3067 | -0.13733 | -0.17395 | 0.10529 | 0.48523 | -0.064087 | 0.10986 | -0.036621 | 123.1064 | 122.7631 | 21.1395 | -123.2758 | 123.175 | 123.0331 | 30.249 | -123.2437
1067.6406 | 123.1155 | -19.0933 | 103.9673 | -0.27114 | 0.02953 | 0.083786 | 0.025363 | 0.044852 | -0.0016549 | -0.012513 | 0.98299 | -0.015456 | 0.053056 | 0.044532 | 0.018451 | -0.027876 | 103.624 | -14.621 | 2.1423 | -19.4275 | 103.9856 | -19.2444 | -19.3588 | -18.5806 | 12.3367 | -18.9926 | 104.0771 | 103.9581 | -19.2078 | -19.2535 | -0.15106 | -0.2655 | 0.018311 | 4.4724 | -0.33417 | -0.068664 | -0.34332 | -0.11444 | -0.16022 | 0.10986 | 0.5127 | 0.10071 | 0.26093 | -0.009155 | 123.0789 | 122.7173 | 21.2357 | -123.3261 | 123.1705 | 123.0515 | 31.4301 | -123.2208
1068.6406 | 123.1018 | -19.4046 | 103.6011 | 0.079814 | 0.04662 | 0.058151 | 0.044589 | 0.048056 | 0.019708 | -0.013582 | -0.17668 | -0.022933 | 0.048783 | 0.049872 | 0.022724 | -0.042829 | 103.4775 | -14.6942 | 1.9455 | -19.6289 | 103.7201 | -19.4458 | -19.5557 | -18.7592 | 11.4304 | -19.368 | 103.7796 | 103.6606 | -19.487 | -19.5419 | -0.041199 | -0.15106 | 0.11902 | 4.7104 | -0.2243 | -0.073242 | -0.1236 | -0.082398 | -0.13733 | 0.17853 | 0.64545 | 0.036621 | 0.17395 | 0.059509 | 123.1247 | 122.8821 | 21.3501 | -123.1567 | 123.1842 | 123.0652 | 30.835 | -123.143
1069.6406 | 123.1155 | -19.3817 | 103.6606 | 3.925 | 0.041279 | 0.073105 | 0.031771 | 0.041648 | 0.011163 | -0.012513 | -0.10039 | -0.017592 | 0.061601 | 0.030646 | 0.015247 | -0.03108 | 103.4775 | -14.7583 | 2.1515 | -19.5831 | 103.7933 | -19.4046 | -19.5053 | -18.8324 | 11.7233 | -19.3954 | 103.7796 | 103.656 | -19.5007 | -19.5419 | -0.022888 | -0.1236 | 0.13275 | 4.6234 | -0.20142 | -0.07782 | -0.1831 | -0.11902 | -0.16022 | 0.11902 | 0.54932 | -0.013733 | 0.14648 | -0.004577 | 123.175 | 122.8592 | 21.5332 | -123.1659 | 123.1613 | 123.0377 | 31.105 | -123.2025
1070.6406 | 123.0972 | -19.0613 | 103.949 | 0.095073 | 0.04662 | 0.074173 | 0.039248 | 0.046988 | 0.0090271 | -0.012513 | 0.14375 | -0.017592 | 0.057328 | 0.047736 | 0.015247 | -0.032148 | 103.8071 | -14.2136 | 2.1606 | -19.2719 | 104.0909 | -19.0933 | -19.194 | -18.5394 | 11.1923 | -19.0842 | 104.1046 | 104.0131 | -19.1895 | -19.2215 | -0.032044 | -0.13275 | 0.14191 | 4.8477 | -0.21057 | -0.07782 | -0.14191 | -0.12817 | -0.16022 | 0.15564 | 0.52185 | -0.022888 | 0.13733 | 0.064087 | 123.1522 | 122.8683 | 21.2219 | -123.143 | 123.1659 | 123.0743 | 30.2536 | -123.1705
1071.6406 | 123.0652 | -19.5511 | 103.5187 | 0.26292 | 0.048756 | 0.074173 | 0.048861 | 0.044852 | 0.012231 | -0.013582 | 0.25056 | -0.010115 | 0.064805 | 0.039191 | 0.014179 | -0.033216 | 103.2761 | -14.4058 | 1.5289 | -19.7845 | 103.624 | -19.606 | -19.7113 | -18.9972 | 10.7071 | -19.5648 | 103.656 | 103.5507 | -19.6518 | -19.693 | -0.054932 | -0.16022 | 0.10529 | 5.1453 | -0.23346 | -0.073242 | -0.24262 | -0.10071 | -0.14191 | 0.13733 | 0.55389 | -0.013733 | 0.12817 | 0.032043 | 123.175 | 122.8271 | 21.08 | -123.23 | 123.2071 | 123.1018 | 30.2582 | -123.2117
1072.6406 | 123.0743 | -19.3863 | 103.6789 | 0.3087 | 0.040211 | 0.072037 | 0.050997 | 0.049125 | 0.013299 | -0.0071733 | 0.38789 | -0.019728 | 0.05626 | 0.055213 | 0.020587 | -0.025739 | 103.4729 | -14.5615 | 2.0004 | -19.5786 | 103.8391 | -19.3863 | -19.4641 | -18.8919 | 11.3571 | -19.4229 | 103.7933 | 103.7201 | -19.5053 | -19.5053 | 0 | -0.077819 | 0.16022 | 4.8248 | -0.19226 | -0.11444 | -0.20599 | -0.11902 | -0.11902 | 0.11444 | 0.49439 | -0.036621 | 0.082397 | 0.041199 | 123.2254 | 122.8592 | 21.3867 | -123.143 | 123.1796 | 123.1064 | 30.7434 | -123.1842
1073.6406 | 123.0927 | -19.162 | 103.894 | 0.17137 | 0.04662 | 0.070968 | 0.034976 | 0.053397 | 0.0058221 | -0.01465 | 0.082718 | -0.0047754 | 0.057328 | 0.052009 | 0.016315 | -0.020399 | 103.6011 | -14.5248 | 1.8127 | -19.4321 | 103.9627 | -19.2627 | -19.3588 | -18.6172 | 12.1582 | -19.1162 | 104.0359 | 103.9581 | -19.2856 | -19.3314 | -0.10071 | -0.19684 | 0.068665 | 4.6371 | -0.27008 | -0.073242 | -0.29297 | -0.1236 | -0.16937 | 0.14191 | 0.54474 | 0.045776 | 0.21515 | 0.064087 | 123.1247 | 122.7631 | 20.9747 | -123.2529 | 123.1979 | 123.1201 | 31.3202 | -123.2254
1074.6406 | 123.1934 | -19.075 | 103.9169 | 0.58335 | 0.041279 | 0.077377 | 0.039248 | 0.04592 | -0.0048589 | -0.027467 | 0.52522 | -0.029341 | 0.054124 | 0.052009 | 0.0088381 | -0.022535 | 103.6697 | -14.5065 | 2.0462 | -19.368 | 103.9993 | -19.1711 | -19.2719 | -18.5074 | 12.1902 | -19.0659 | 104.0222 | 103.9398 | -19.2215 | -19.2673 | -0.096131 | -0.19684 | 0.082398 | 4.5685 | -0.29297 | -0.09613 | -0.24719 | -0.14648 | -0.19226 | 0.10529 | 0.56763 | 0.009155 | 0.20142 | 0.022888 | 123.0743 | 122.7448 | 21.1212 | -123.1888 | 123.0972 | 123.0148 | 31.2653 | -123.1842
1075.6406 | 123.1979 | -19.2169 | 103.7476 | 0.59861 | 0.047688 | 0.066696 | 0.040316 | 0.036307 | 0.0015501 | -0.022126 | 0.66255 | -0.033614 | 0.053056 | 0.030646 | -0.00077485 | -0.025739 | 103.624 | -14.3097 | 3.4058 | -19.4138 | 103.8757 | -19.2764 | -19.3588 | -18.576 | 12.4008 | -19.0842 | 103.8849 | 103.8208 | -19.3359 | -19.3588 | -0.059509 | -0.14191 | 0.12817 | 4.9072 | -0.19684 | -0.054931 | -0.1236 | -0.11902 | -0.14191 | 0.13733 | 0.64087 | 0.13275 | 0.27466 | 0.073242 | 123.0927 | 122.8409 | 22.6227 | -123.1064 | 123.1018 | 123.0377 | 31.6177 | -123.1064
1076.6406 | 123.1842 | -19.1116 | 103.8849 | 0.53758 | 0.0092362 | 0.078445 | 0.041384 | 0.038443 | -0.021949 | -0.029603 | 0.44893 | -0.031478 | 0.053056 | 0.050941 | -0.0050469 | -0.021467 | 103.7567 | -14.1495 | 3.5202 | -19.3268 | 104.0359 | -19.1025 | -19.2444 | -18.576 | 11.8881 | -19.1345 | 104.0131 | 103.949 | -19.2307 | -19.2764 | 0.009155 | -0.13275 | 0.15106 | 4.9622 | -0.21515 | -0.082397 | -0.12817 | -0.11902 | -0.16479 | 0.12817 | 0.53558 | -0.022888 | 0.14191 | 0.064087 | 123.1476 | 122.8683 | 22.6318 | -123.1293 | 123.1247 | 123.0606 | 30.9998 | -123.1613
1077.6406 | 123.1979 | -19.2169 | 103.7201 | 0.69017 | 0.02419 | 0.070968 | 0.02109 | 0.033103 | -0.0091309 | -0.03708 | 0.54048 | -0.020796 | 0.051988 | 0.046668 | 0.0056341 | -0.032148 | 103.7384 | -14.2776 | 2.2842 | -19.4412 | 103.775 | -19.3405 | -19.3954 | -18.6447 | 12.2314 | -19.1574 | 103.8986 | 103.8254 | -19.3359 | -19.3588 | -0.1236 | -0.17853 | 0.054931 | 4.9393 | -0.2243 | -0.045776 | 0.01831 | -0.11902 | -0.14191 | 0.17853 | 0.57221 | 0.059509 | 0.20142 | 0.10528 | 122.9919 | 122.9553 | 21.5012 | -123.1155 | 123.1155 | 123.0423 | 31.4484 | -123.0789
1078.6406 | 123.1247 | -19.0796 | 103.9398 | -0.24062 | 0.011372 | 0.075241 | 0.030703 | 0.042716 | -0.0069949 | -0.03708 | -0.34453 | -0.026137 | 0.053056 | 0.043464 | -0.0018429 | -0.026808 | 103.7292 | -14.0259 | 2.5497 | -19.3405 | 103.9993 | -19.1666 | -19.2581 | -18.4753 | 11.6821 | -19.0155 | 104.0955 | 104.0222 | -19.1986 | -19.2398 | -0.086975 | -0.17853 | 0.05951 | 5.0537 | -0.26093 | -0.082397 | -0.21057 | -0.11902 | -0.16022 | 0.15564 | 0.60425 | 0.064087 | 0.2243 | 0.082398 | 123.0789 | 122.8088 | 21.6293 | -123.1979 | 123.175 | 123.1018 | 30.7617 | -123.1796
1079.6406 | 123.1705 | -20.2332 | 102.7176 | 0.4918 | 0.014576 | 0.080581 | 0.042453 | 0.051261 | -0.016608 | -0.01999 | 0.52522 | -0.042159 | 0.043443 | 0.042396 | 0.0088381 | -0.025739 | 102.6031 | -14.9689 | 3.4607 | -20.4758 | 102.8275 | -20.2881 | -20.3705 | -19.5648 | 12.2864 | -20.1324 | 102.9099 | 102.8229 | -20.3384 | -20.3705 | -0.054932 | -0.13733 | 0.10986 | 5.2643 | -0.24262 | -0.10529 | -0.11444 | -0.10529 | -0.13733 | 0.19226 | 0.66833 | 0.10071 | 0.23804 | 0.10529 | 123.0606 | 122.8363 | 23.6938 | -123.0881 | 123.143 | 123.056 | 32.5195 | -123.0881
1080.6406 | 123.1705 | -19.9036 | 103.0609 | 0.40025 | 0.01244 | 0.080581 | 0.026431 | 0.041648 | -0.012336 | -0.031739 | 0.54048 | -0.034682 | 0.047715 | 0.041327 | 0.023792 | -0.03108 | 102.9327 | -14.6805 | 3.4927 | -20.1553 | 103.1662 | -19.9768 | -20.0546 | -19.2123 | 12.4329 | -19.7983 | 103.2074 | 103.1113 | -20.0272 | -20.0546 | -0.073243 | -0.15106 | 0.10529 | 5.2231 | -0.25177 | -0.10071 | -0.12817 | -0.1236 | -0.15106 | 0.14648 | 0.69122 | 0.10528 | 0.25635 | 0.050354 | 123.0698 | 122.8363 | 23.3963 | -123.1155 | 123.111 | 123.0148 | 32.3364 | -123.1155
1081.6406 | 123.143 | -19.6564 | 103.3218 | 0.29344 | 0.0017592 | 0.0699 | 0.026431 | 0.026694 | -0.014472 | -0.032808 | 0.20479 | -0.030409 | 0.051988 | 0.042396 | 0.016315 | -0.023603 | 103.1387 | -14.5523 | 2.3621 | -19.8898 | 103.4134 | -19.7388 | -19.8166 | -19.0247 | 11.9934 | -19.5831 | 103.4546 | 103.3676 | -19.7662 | -19.8303 | -0.082398 | -0.16022 | 0.091553 | 5.1041 | -0.23346 | -0.073243 | -0.1831 | -0.10986 | -0.17395 | 0.13275 | 0.63171 | 0.073242 | 0.24719 | 0.045777 | 123.0698 | 122.7951 | 22.0184 | -123.1384 | 123.111 | 123.024 | 31.6498 | -123.1522
1082.6406 | 123.23 | -19.7525 | 103.2303 | 0.17137 | 0.015645 | 0.074173 | 0.027499 | 0.037375 | -0.0091309 | -0.029603 | 0.0522 | -0.046431 | 0.041307 | 0.0456 | 0.010974 | -0.024671 | 103.1067 | -14.534 | 2.3849 | -19.9356 | 103.3813 | -19.7891 | -19.899 | -19.0933 | 11.9751 | -19.725 | 103.3447 | 103.2761 | -19.8807 | -19.9081 | -0.036622 | -0.14649 | 0.15106 | 5.2185 | -0.18311 | -0.036621 | -0.1236 | -0.12817 | -0.15564 | 0.11444 | 0.65918 | 0.027465 | 0.18311 | 0.045776 | 123.1338 | 122.8592 | 22.1375 | -123.1293 | 123.0972 | 123.0286 | 31.7276 | -123.1384
1083.6406 | 123.143 | -19.7708 | 103.2578 | -0.16433 | 0.041279 | 0.072037 | 0.056338 | 0.049125 | 0.027185 | -0.016786 | -0.34453 | -0.019728 | 0.07335 | 0.041327 | 0.020587 | -0.046034 | 103.1433 | -14.8682 | 2.3758 | -19.9814 | 103.4042 | -19.8441 | -19.9127 | -19.0201 | 10.3821 | -19.8074 | 103.3951 | 103.2852 | -19.9173 | -19.9493 | -0.073242 | -0.14191 | 0.14648 | 4.9026 | -0.21057 | -0.068664 | -0.11444 | -0.14648 | -0.17853 | 0.13733 | 0.75073 | -0.036621 | 0.14191 | 0.027466 | 123.175 | 122.9141 | 22.1466 | -123.1705 | 123.1659 | 123.056 | 30.1529 | -123.2071
1084.6406 | 123.2483 | -20.2652 | 102.6855 | 0.034038 | 0.0049632 | 0.08165 | 0.023226 | 0.043784 | -0.020881 | -0.031739 | 0.22005 | -0.042159 | 0.031694 | 0.046668 | 0.0099061 | -0.023603 | 102.5436 | -14.9963 | 2.7191 | -20.5124 | 102.7908 | -20.3705 | -20.4712 | -19.574 | 10.9726 | -20.1553 | 102.7954 | 102.6901 | -20.3888 | -20.4437 | -0.10528 | -0.20599 | 0.10529 | 5.2689 | -0.24719 | -0.041199 | -0.14191 | -0.1236 | -0.17853 | 0.10986 | 0.69122 | 0.10986 | 0.28839 | 0.004578 | 123.056 | 122.8088 | 22.9843 | -123.1567 | 123.0606 | 122.9553 | 31.2378 | -123.1293
1085.7031 | 123.0743 | -19.9539 | 103.0838 | -0.24062 | 0.0060322 | 0.088058 | 0.027499 | 0.049125 | -0.00058594 | -0.028535 | -0.06987 | -0.032546 | 0.053056 | 0.031714 | 0.021655 | -0.030012 | 102.8778 | -14.9139 | 2.5909 | -20.1599 | 103.2303 | -19.9722 | -20.1004 | -19.3405 | 11.6364 | -19.9814 | 103.2394 | 103.125 | -20.0684 | -20.1096 | -0.018311 | -0.14648 | 0.14649 | 5.04 | -0.20599 | -0.059509 | -0.20599 | -0.11444 | -0.15564 | 0.15564 | 0.6134 | -0.027466 | 0.12817 | 0.041199 | 123.1842 | 122.8317 | 22.5449 | -123.1842 | 123.1934 | 123.0789 | 31.5903 | -123.1934
1086.6406 | 123.2346 | -19.9356 | 103.0655 | -0.13381 | 0.0049632 | 0.080581 | 0.036044 | 0.041648 | -0.0080629 | -0.027467 | -0.22246 | -0.024001 | 0.043443 | 0.054145 | 0.010974 | -0.037489 | 102.9556 | -14.7537 | 2.3895 | -20.1004 | 103.1891 | -19.9448 | -20.0455 | -19.3863 | 12.6434 | -20.0867 | 103.1662 | 103.0518 | -20.0729 | -20.0958 | -0.009155 | -0.10986 | 0.1236 | 5.1819 | -0.1648 | -0.054932 | -0.10986 | -0.13733 | -0.16022 | 0.10071 | 0.54932 | -0.15106 | 0.009155 | -0.013733 | 123.1247 | 122.8912 | 22.3251 | -123.111 | 123.1018 | 122.9874 | 32.579 | -123.1613
1087.6406 | 123.2071 | -22.3938 | 100.5569 | -0.14907 | 0.0038952 | 0.077377 | 0.025363 | 0.043784 | -0.014472 | -0.032808 | -0.14616 | -0.032546 | 0.03917 | 0.043464 | 0.01311 | -0.03108 | 100.4654 | -21.4783 | 2.2751 | -22.5952 | 100.7217 | -22.467 | -22.5266 | -21.785 | 11.2793 | -22.2885 | 100.6851 | 100.5432 | -22.5266 | -22.5677 | -0.073242 | -0.13275 | 0.16479 | 0.91553 | -0.20142 | -0.068665 | -0.091553 | -0.13275 | -0.17395 | 0.12817 | 0.60883 | 0.10529 | 0.27924 | -0.013733 | 123.1155 | 122.8592 | 24.6689 | -123.0835 | 123.0789 | 122.937 | 33.6731 | -123.1247
1088.6406 | 122.9874 | -103.8986 | 18.9835 | 0.27818 | 0.049824 | 2.3802 | 0.057406 | 0.10253 | 0.030389 | -0.012513 | 0.021682 | -0.021865 | 0.055192 | 0.0456 | 2.2594 | -0.041761 | 18.2007 | -9.6725 | -5.0171 | -104.187 | 18.7271 | -104.2053 | -104.2191 | -102.887 | -14.241 | -18.869 | 19.0109 | 18.9148 | -104.0085 | -104.0039 | -0.3067 | -0.32043 | -0.25635 | 94.2261 | -0.28839 | 0.032043 | -0.78278 | -0.10986 | -0.10528 | 0.027466 | 1.0117 | 85.0296 | 85.1349 | -0.068664 | 122.6257 | 122.0993 | 98.8815 | -123.2025 | 122.9095 | 122.8134 | 89.6576 | -122.9874
1089.6406 | 122.8958 | -104.2191 | 18.5944 | -0.14907 | 0.013508 | 3.0072 | 0.029635 | 0.093985 | -0.0016549 | -0.018922 | -0.43608 | -0.029341 | 0.065873 | 0.041327 | 2.8554 | -0.028944 | 17.8711 | -8.519 | -5.3238 | -104.2007 | 18.4753 | -104.2465 | -104.3015 | -102.919 | -13.4766 | -0.53558 | 18.6539 | 18.5669 | -104.2191 | -104.2419 | -0.027466 | -0.082398 | -0.11902 | 95.7001 | 0.01831 | 0.10071 | -0.72327 | 0 | -0.022888 | 0.05951 | 1.3 | 103.6835 | 103.7064 | -0.027465 | 122.6944 | 122.0901 | 98.8953 | -122.8958 | 122.8729 | 122.7859 | 90.7425 | -122.8363
1090.6406 | 122.7997 | -101.6373 | 21.1395 | -0.22536 | 0.015645 | 2.957 | 0.037112 | 0.082236 | -0.0048589 | -0.018922 | -0.42082 | -0.025069 | 0.057328 | 0.0456 | 2.8116 | -0.03108 | 20.4208 | -8.3588 | -5.2826 | -101.8707 | 20.8511 | -101.8753 | -101.9531 | -100.2319 | -12.4374 | -0.5127 | 21.2814 | 21.199 | -101.5228 | -101.5823 | -0.23804 | -0.31586 | -0.28839 | 93.2785 | -0.23346 | 0.082397 | -0.71869 | 0.11444 | 0.054932 | 0.14191 | 1.4053 | 101.1246 | 101.0696 | 0.05951 | 122.4884 | 122.0581 | 96.3547 | -123.0927 | 122.9187 | 122.8363 | 89.1998 | -122.7219
1091.6406 | 122.905 | -87.1536 | 35.4767 | -0.27114 | 0.022053 | 2.7124 | 0.025363 | 0.084372 | 0.0079581 | -0.018922 | -0.25298 | -0.014388 | 0.059465 | 0.043464 | 2.5755 | -0.020399 | 34.8312 | -7.1548 | -4.248 | -86.4944 | 35.5911 | -86.7508 | -86.8835 | -86.6592 | -9.5444 | -0.43488 | 35.3119 | 35.2112 | -87.0712 | -86.8286 | 0.40283 | 0.27008 | 0.11444 | 79.9988 | 0.65918 | 0.3891 | -0.64545 | 0.082397 | 0.32501 | -0.1648 | 0.49438 | 86.7188 | 86.3937 | -0.2655 | 122.7448 | 121.9849 | 82.9056 | -122.3602 | 122.4655 | 122.3648 | 77.6093 | -122.3053
1092.6406 | 122.7951 | -117.3157 | 5.3879 | -0.25588 | 0.051961 | 3.4206 | 0.03284 | 0.10253 | -0.0016549 | -0.018922 | -0.32927 | -0.016524 | 0.058397 | 0.038123 | 3.2548 | -0.027876 | 4.3579 | -7.5394 | -7.5668 | -117.3523 | 5.1498 | -117.4255 | -117.4942 | -115.8829 | -19.0063 | -0.52185 | 5.452 | 5.3558 | -117.2562 | -117.2928 | -0.10986 | -0.17853 | -0.23804 | 109.7763 | -0.036621 | 0.14191 | -1.03 | 0.059509 | 0.022888 | 0.064087 | 1.4328 | 116.7938 | 116.7709 | -0.032043 | 122.4655 | 121.6736 | 109.7488 | -122.8821 | 122.7676 | 122.6715 | 98.3093 | -122.6807
1093.6406 | 122.6761 | -117.7094 | 4.9805 | 0.79698 | 0.041279 | 3.4387 | 0.037112 | 0.095053 | 0.014367 | -0.024263 | 0.37263 | -0.014388 | 0.066941 | 0.040259 | 3.2741 | -0.017194 | 3.8773 | -7.045 | -7.901 | -117.7826 | 4.7333 | -117.746 | -117.8558 | -116.2125 | -18.4799 | -0.53101 | 5.0171 | 4.9484 | -117.6132 | -117.6407 | -0.036621 | -0.14648 | -0.24719 | 110.6644 | -0.073242 | 0.073242 | -1.1032 | 0.096131 | 0.068665 | 0.036621 | 1.4969 | 117.1783 | 117.1097 | -0.032044 | 122.4426 | 121.5866 | 109.8084 | -122.8363 | 122.7264 | 122.6578 | 99.2294 | -122.6212
1094.6406 | 122.6852 | -118.0527 | 4.6326 | 0.90379 | 0.041279 | 3.4526 | 0.042453 | 0.088645 | -0.0016549 | -0.015718 | -0.039353 | -0.014388 | 0.041307 | 0.049872 | 3.2719 | -0.023603 | 3.5843 | -7.0724 | -8.1299 | -118.0618 | 4.4083 | -118.0664 | -118.1671 | -116.5192 | -18.6493 | -0.56305 | 4.6875 | 4.628 | -117.9382 | -117.9657 | -0.013733 | -0.11444 | -0.2243 | 110.9802 | -0.009156 | 0.10528 | -1.0483 | 0.11444 | 0.086975 | 0.054932 | 1.5335 | 117.4896 | 117.4026 | -0.004577 | 122.4609 | 121.637 | 109.9228 | -122.7997 | 122.7402 | 122.6807 | 99.4034 | -122.5983
1095.6406 | 122.7219 | -118.2083 | 4.4083 | -0.042256 | 0.039143 | 3.4505 | 0.033908 | 0.11001 | 0.015435 | -0.011445 | 0.036941 | -0.015456 | 0.063737 | 0.037055 | 3.2794 | -0.034284 | 3.4012 | -6.9351 | -8.194 | -118.2175 | 4.1794 | -118.2587 | -118.3411 | -116.5741 | -17.8711 | -0.52185 | 4.454 | 4.4128 | -118.0939 | -118.1534 | -0.050354 | -0.13275 | -0.22888 | 111.2732 | -0.009155 | 0.1236 | -1.0071 | 0.11444 | 0.054932 | 0.045777 | 1.6342 | 117.6865 | 117.6315 | 0.004578 | 122.3877 | 121.6095 | 110.0143 | -122.7493 | 122.6624 | 122.6212 | 100.3372 | -122.5616
1096.6406 | 122.6349 | -118.3594 | 4.2618 | 0.17137 | 0.065846 | 3.4451 | 0.037112 | 0.10039 | 0.011163 | -0.0061053 | 0.34212 | -0.010115 | 0.071214 | 0.044532 | 3.2912 | -0.019331 | 3.186 | -6.7245 | -8.1528 | -118.3823 | 4.0054 | -118.3823 | -118.4875 | -116.748 | -17.7567 | -0.53558 | 4.3167 | 4.2618 | -118.2632 | -118.2816 | -0.022888 | -0.12817 | -0.25635 | 111.6348 | -0.022888 | 0.10529 | -1.0757 | 0.09613 | 0.07782 | 0.054931 | 1.6113 | 117.8238 | 117.746 | 0 | 122.3648 | 121.5454 | 110.2066 | -122.7493 | 122.6761 | 122.6212 | 100.6027 | -122.5433
1097.6406 | 122.5937 | -118.4555 | 4.1245 | 0.2324 | 0.056233 | 3.4569 | 0.042453 | 0.1068 | 0.016503 | -0.018922 | 0.44893 | -0.020796 | 0.05626 | 0.043464 | 3.2986 | -0.019331 | 3.067 | -6.5414 | -7.8094 | -118.4921 | 3.8818 | -118.4967 | -118.5837 | -116.8808 | -18.1915 | -0.55389 | 4.1977 | 4.1061 | -118.3548 | -118.3868 | -0.041199 | -0.12817 | -0.24261 | 111.9141 | -0.036621 | 0.091553 | -1.0574 | 0.10071 | 0.068664 | 0.073242 | 1.5747 | 117.9016 | 117.8329 | -0.018311 | 122.3373 | 121.5225 | 110.6461 | -122.7081 | 122.6532 | 122.5616 | 100.264 | -122.5113
1098.6406 | 122.5891 | -118.5471 | 4.0421 | 0.26292 | 0.037007 | 3.4537 | 0.036044 | 0.10253 | 0.010095 | -0.016786 | 0.67781 | -0.016524 | 0.047715 | 0.052009 | 3.3018 | -0.022535 | 2.9572 | -6.6467 | -6.3812 | -118.6066 | 3.7491 | -118.5883 | -118.6752 | -117.215 | -17.2989 | -0.55389 | 4.0695 | 4.0146 | -118.4601 | -118.483 | -0.041199 | -0.12817 | -0.29297 | 111.9003 | -0.059509 | 0.068665 | -1.0849 | 0.086975 | 0.064087 | 0.027466 | 1.3321 | 117.9932 | 117.9291 | -0.027466 | 122.2961 | 121.5042 | 112.1658 | -122.7173 | 122.6166 | 122.5616 | 101.2482 | -122.525
1099.6406 | 122.5937 | -118.634 | 3.9688 | 0.46128 | 0.051961 | 3.443 | 0.039248 | 0.10146 | 0.013299 | -0.011445 | 0.66255 | -0.022933 | 0.058397 | 0.049872 | 3.305 | -0.020399 | 2.861 | -6.7657 | -6.2942 | -118.6844 | 3.717 | -118.6386 | -118.7302 | -117.1921 | -17.1799 | -0.53558 | 4.0237 | 3.9322 | -118.5104 | -118.5562 | -0.004578 | -0.096131 | -0.25177 | 111.8683 | -0.050354 | 0.045777 | -1.1078 | 0.1236 | 0.07782 | 0.054932 | 1.442 | 118.0984 | 118.0206 | -0.036621 | 122.3511 | 121.4951 | 112.3398 | -122.699 | 122.6578 | 122.5662 | 101.4542 | -122.525
1100.6406 | 122.5845 | -118.602 | 3.9505 | 0.47654 | 0.047688 | 3.4526 | 0.026431 | 0.10253 | 0.0015501 | -0.012513 | 0.67781 | -0.029341 | 0.060533 | 0.0456 | 3.2591 | -0.024671 | 2.8519 | -6.7612 | -6.4545 | -118.6478 | 3.7354 | -118.6249 | -118.6935 | -117.1555 | -18.3426 | -0.46692 | 4.0558 | 3.9642 | -118.4647 | -118.5333 | -0.022888 | -0.091552 | -0.21515 | 111.8408 | -0.045776 | 0.045776 | -1.0986 | 0.13733 | 0.068665 | 0.10529 | 1.4465 | 118.1351 | 118.0664 | 0.013733 | 122.3373 | 121.4539 | 112.1475 | -122.644 | 122.6578 | 122.5662 | 100.2594 | -122.4838
1101.6406 | 122.5479 | -118.6157 | 3.9276 | 0.33921 | 0.040211 | 3.4516 | 0.046725 | 0.091849 | 0.014367 | -0.021058 | 0.64729 | -0.019728 | 0.062669 | 0.053077 | 3.2869 | -0.023603 | 2.7695 | -6.8665 | -6.2485 | -118.689 | 3.6667 | -118.6569 | -118.7347 | -117.1417 | -19.1116 | -0.54474 | 3.9551 | 3.9139 | -118.5104 | -118.5608 | -0.041198 | -0.11902 | -0.26092 | 111.7493 | -0.073242 | 0.045776 | -1.1581 | 0.10529 | 0.054932 | 0.027466 | 1.474 | 118.071 | 118.0161 | -0.013733 | 122.2824 | 121.3852 | 112.3672 | -122.6624 | 122.5708 | 122.5296 | 99.5041 | -122.4884
1102.6406 | 122.5937 | -118.6798 | 3.7857 | 0.4918 | 0.026326 | 3.459 | 0.039248 | 0.10787 | 0.0026181 | -0.030671 | 0.81514 | -0.026137 | 0.066941 | 0.055213 | 3.2901 | -0.022535 | 2.7557 | -7.8827 | -5.9097 | -118.7622 | 3.5706 | -118.6935 | -118.7805 | -117.2699 | -19.4366 | -0.48065 | 3.8498 | 3.8223 | -118.5791 | -118.5883 | -0.013732 | -0.10071 | -0.21515 | 110.7971 | -0.082397 | 0.018311 | -1.03 | 0.10071 | 0.091553 | 0.064086 | 1.4099 | 118.1992 | 118.1076 | 0.036621 | 122.2504 | 121.4355 | 112.7701 | -122.5662 | 122.5296 | 122.5021 | 99.2432 | -122.374
1103.6406 | 122.6669 | -118.7256 | 3.7125 | 0.56809 | 0.02419 | 3.4441 | 0.018954 | 0.12069 | -0.00058594 | -0.022126 | 0.99824 | -0.030409 | 0.05626 | 0.050941 | 3.2858 | -0.033216 | 2.8152 | -5.8044 | -5.5298 | -118.6844 | 3.5019 | -118.7027 | -118.7622 | -117.2379 | -18.631 | -0.40741 | 3.8132 | 3.7674 | -118.602 | -118.6523 | 0.022888 | -0.036621 | -0.21057 | 112.9211 | 0.041199 | 0.07782 | -0.89722 | 0.1236 | 0.073242 | 0.10071 | 1.4877 | 118.3182 | 118.2449 | 0.054932 | 122.2275 | 121.5408 | 113.1958 | -122.4747 | 122.5388 | 122.493 | 100.0946 | -122.3648
1104.6406 | 122.6486 | -118.6569 | 3.7537 | 0.52232 | 0.028462 | 3.4067 | 0.024295 | 0.041648 | 0.0058221 | -0.029603 | 2.814 | -0.027205 | 0.053056 | 0.038123 | 3.2826 | -0.021467 | 2.8152 | -116.4825 | -7.1732 | -116.597 | 3.4973 | -118.7851 | -118.8675 | -117.0135 | -19.5419 | -0.40741 | 3.772 | 3.6987 | -118.5928 | -118.6386 | -0.12817 | -0.21057 | -0.25635 | 2.1744 | 2.0599 | 2.2705 | -0.93841 | 0.064087 | 0.01831 | 0.018311 | 1.6434 | 118.2495 | 118.2312 | -0.054932 | 122.1542 | 121.4722 | 111.4838 | -122.6212 | 122.4289 | 122.3557 | 99.115 | -122.3923
1105.6406 | 122.612 | -118.721 | 3.7262 | 0.47654 | 0.0092362 | 3.3768 | 0.037112 | 0.04058 | -0.020881 | -0.024263 | 0.95247 | -0.033614 | 0.045579 | 0.043464 | 3.289 | -0.019331 | 2.7466 | -116.1118 | -7.4524 | -118.6844 | 3.4836 | -118.7393 | -118.8171 | -117.0914 | -19.7983 | -0.46692 | 3.7537 | 3.7216 | -118.6111 | -118.634 | -0.018311 | -0.096131 | -0.24261 | 2.6093 | 0.036621 | 0.13275 | -0.97961 | 0.10986 | 0.086975 | 0.027466 | 1.6296 | 118.2541 | 118.1671 | -0.004577 | 122.2046 | 121.4676 | 111.2686 | -122.5433 | 122.4747 | 122.4426 | 98.9227 | -122.3602
1106.6406 | 122.5845 | -118.6981 | 3.6987 | 0.41551 | 0.016713 | 3.3885 | 0.040316 | 0.033103 | -0.020881 | -0.032808 | 0.81514 | -0.028273 | 0.053056 | 0.038123 | 3.288 | -0.016126 | 2.7649 | -116.0614 | -7.2556 | -118.8263 | 3.4653 | -118.7119 | -118.8217 | -117.1005 | -19.8578 | -0.42114 | 3.772 | 3.6942 | -118.6066 | -118.6111 | -0.013733 | -0.1236 | -0.23346 | 2.6367 | -0.12817 | -0.004578 | -0.93384 | 0.091553 | 0.086975 | 0.073243 | 1.5976 | 118.277 | 118.19 | -0.004577 | 122.1634 | 121.463 | 111.4426 | -122.5204 | 122.4701 | 122.3923 | 98.8403 | -122.3099
1107.6406 | 122.6944 | -97.7463 | 24.6048 | 0.47654 | 0.0092362 | 3.2839 | 0.036044 | 0.065146 | 0.26324 | -0.018922 | 0.72359 | -0.028273 | 0.051988 | 0.037055 | 2.866 | -0.021467 | 2.5909 | -37.0193 | -5.0354 | -37.4496 | 24.559 | -98.2681 | -98.465 | -96.405 | -13.0051 | -0.35248 | 24.7192 | 24.9252 | -97.3709 | -97.7234 | -0.52185 | -0.71869 | -0.045776 | 60.7269 | 60.2966 | 61.0153 | -22.0139 | 0.37537 | 0.022888 | 0.11444 | 1.3412 | 97.3938 | 97.3709 | 0.32043 | 122.3053 | 100.3372 | 92.7109 | -123.0698 | 122.4655 | 122.6715 | 84.7412 | -122.3282
1108.6406 | 122.5067 | -97.1191 | 25.1129 | 0.58335 | 0.017781 | 0.0090179 | 3.6142 | 0.093985 | 0.73855 | -0.028535 | 0.87617 | -0.029341 | 0.047715 | 0.038123 | 2.6984 | -0.032148 | 0.004578 | 24.5178 | -3.1769 | 24.1196 | 24.9481 | -97.0963 | -97.1832 | -95.9244 | -14.7446 | -0.32959 | 25.2457 | 25.1724 | -97.0459 | -97.1603 | 0.022889 | -0.064087 | -0.1648 | 121.637 | 121.2387 | 121.3028 | -25.1083 | 0.073243 | -0.041198 | 0.13275 | 1.1948 | 96.7896 | 96.8307 | 0.059509 | 122.0673 | 97.1237 | 93.9423 | -122.2961 | 122.3648 | 122.2916 | 82.3746 | -122.2733
1109.6406 | 122.5891 | -118.8446 | 3.4882 | 0.3087 | 0.0081682 | 3.1856 | 0.028567 | 0.10467 | -0.021949 | -0.023195 | 0.34212 | -0.038954 | 0.047715 | 0.047736 | 3.0156 | -0.021467 | 2.7328 | -2.1606 | -5.7175 | -119.0689 | 3.3554 | -118.8538 | -118.9407 | -117.2012 | -20.2057 | -0.39368 | 3.5797 | 3.5339 | -118.8354 | -118.8492 | -0.009156 | -0.096131 | -0.13275 | 116.684 | -0.22431 | -0.12817 | -0.75531 | 0.009155 | -0.004578 | 0.091553 | 1.6434 | 118.4509 | 118.4555 | 0.045777 | 122.2 | 121.5775 | 113.1271 | -122.4289 | 122.4243 | 122.3785 | 98.6389 | -122.3373
1110.6406 | 122.5891 | -118.5745 | 3.7582 | -0.10329 | 0.0038952 | 3.4569 | 0.03284 | 0.10253 | -0.014472 | -0.03708 | -0.024094 | -0.043227 | 0.057328 | 0.049872 | 3.2912 | -0.027876 | 2.9114 | -1.2543 | -5.6808 | -118.6615 | 3.5019 | -118.6432 | -118.7302 | -116.9495 | -20.4391 | -0.35706 | 3.8132 | 3.7399 | -118.5196 | -118.5471 | -0.068664 | -0.15564 | -0.25635 | 117.3203 | -0.086975 | 0.068665 | -0.84686 | 0.054932 | 0.027466 | 0.054931 | 1.6251 | 118.2175 | 118.19 | -0.018311 | 122.0764 | 121.4859 | 112.8937 | -122.4884 | 122.3877 | 122.3145 | 98.1354 | -122.3053
1111.6406 | 122.5525 | -118.6935 | 3.6072 | 0.079814 | 0.025258 | 3.4708 | 0.040316 | 0.10146 | -0.01554 | -0.033876 | 0.0522 | -0.044295 | 0.041307 | 0.039191 | 3.2858 | -0.028944 | 2.7191 | -1.149 | -5.7632 | -118.6707 | 3.3875 | -118.7622 | -118.8446 | -117.0593 | -110.6049 | -0.36163 | 3.6758 | 3.6163 | -118.6386 | -118.6707 | -0.068665 | -0.15106 | -0.21973 | 117.5446 | 0.022888 | 0.17395 | -0.88806 | 0.054931 | 0.022888 | 0.068664 | 1.6342 | 118.3319 | 118.309 | 0.009155 | 122.081 | 121.4127 | 112.9303 | -122.4518 | 122.3694 | 122.3099 | 8.0887 | -122.2778
1112.6406 | 122.5479 | -118.6661 | 3.6484 | -0.14907 | 0.0060322 | 3.4601 | 0.031771 | 0.10467 | -0.010199 | -0.030671 | -0.0088351 | -0.033614 | 0.03917 | 0.040259 | 3.2858 | -0.030012 | 2.7374 | -1.2451 | -5.7449 | -118.6935 | 3.3875 | -118.7256 | -118.8171 | -117.0456 | -111.2045 | -0.37079 | 3.6758 | 3.6118 | -118.5928 | -118.6432 | -0.059509 | -0.15106 | -0.26092 | 117.421 | -0.027465 | 0.1236 | -0.91095 | 0.073243 | 0.022889 | 0.027466 | 1.6205 | 118.2953 | 118.2724 | -0.036621 | 122.0535 | 121.4035 | 112.9211 | -122.4655 | 122.3419 | 122.2778 | 7.4615 | -122.2916
1113.6406 | 122.5204 | -118.7805 | 3.5614 | -0.13381 | -0.0035808 | 3.4708 | 0.044589 | 0.096122 | -0.010199 | -0.029603 | -1.6568 | -0.029341 | 0.057328 | 0.039191 | 3.2794 | -0.022535 | 2.6321 | -1.2589 | -6.7017 | -118.7897 | 3.3096 | -118.7988 | -118.8904 | -117.2653 | -111.0352 | -0.38452 | 3.5889 | 3.5156 | -118.6844 | -118.6981 | -0.01831 | -0.10986 | -0.25177 | 117.5217 | -0.009155 | 0.10071 | -0.92926 | 0.096131 | 0.082398 | 0.027466 | 1.5152 | 118.396 | 118.3136 | -0.045776 | 122.0901 | 121.4127 | 112.0789 | -122.4518 | 122.3694 | 122.2961 | 7.7454 | -122.2595
1114.6406 | 122.4792 | -118.7622 | 3.5522 | -1.8733 | 0.018849 | 3.4441 | 0.03818 | 0.1036 | 0.0015501 | -0.01999 | -0.17668 | -0.025069 | 0.054124 | 0.042396 | 3.288 | -0.03108 | 2.6184 | -1.387 | -5.2963 | -118.8171 | 3.2867 | -118.8034 | -118.9041 | -117.0685 | -112.0056 | -0.45319 | 3.5934 | 3.5294 | -118.6615 | -118.7164 | -0.041199 | -0.14191 | -0.2655 | 117.3752 | -0.054932 | 0.086975 | -0.93384 | 0.10071 | 0.045776 | 0.041199 | 1.6937 | 118.309 | 118.2632 | -0.022888 | 122.049 | 121.3806 | 113.4659 | -122.4564 | 122.3557 | 122.2916 | 6.7566 | -122.2687
1115.6406 | 122.4335 | -118.602 | 3.7628 | -0.27114 | 0.0017592 | 3.4718 | 0.036044 | 0.10787 | 0.0026181 | -0.021058 | -0.11565 | -0.038954 | 0.045579 | 0.038123 | 3.288 | -0.017194 | 2.774 | -1.4328 | -5.1727 | -118.84 | 3.479 | -118.6111 | -118.6935 | -117.0547 | -21.7072 | -0.47607 | 3.804 | 3.7445 | -118.5287 | -118.4921 | -0.009155 | -0.091552 | -0.28381 | 117.1692 | -0.23804 | -0.14649 | -0.98877 | 0.073242 | 0.10986 | 0.041199 | 1.5472 | 118.1259 | 118.0161 | -0.01831 | 122.081 | 121.376 | 113.4293 | -122.4564 | 122.406 | 122.3465 | 96.8948 | -122.2549
1116.6406 | 122.4426 | -118.5928 | 3.804 | -0.31691 | 0.016713 | 3.4612 | 0.037112 | 0.1068 | 0.0015501 | -0.027467 | -0.29875 | -0.019728 | 0.051988 | 0.034919 | 3.2944 | -0.03108 | 2.7054 | -1.5564 | -5.191 | -118.6752 | 3.5156 | -118.6432 | -118.7164 | -117.0868 | -110.9024 | -0.28381 | 3.8269 | 3.7674 | -118.4463 | -118.4555 | -0.050354 | -0.1236 | -0.28839 | 117.0364 | -0.082398 | 0.041199 | -1.0986 | 0.14648 | 0.13733 | 0.022888 | 1.506 | 118.309 | 118.1717 | -0.036621 | 122.1085 | 121.2982 | 113.4018 | -122.5204 | 122.4197 | 122.3602 | 7.6904 | -122.2595
1117.6406 | 122.3694 | -118.6615 | 3.6896 | -0.27114 | 0.031666 | 3.4558 | 0.044589 | 0.099326 | 0.0090271 | -0.021058 | -0.35979 | -0.019728 | 0.044511 | 0.050941 | 3.2944 | -0.033216 | 2.916 | -1.5564 | -5.452 | -118.808 | 3.5248 | -118.6478 | -118.7119 | -117.1005 | -22.8973 | -0.50354 | 3.772 | 3.685 | -118.5745 | -118.5471 | 0.013733 | -0.050354 | -0.1648 | 117.1051 | -0.14648 | -0.09613 | -0.77362 | 0.086975 | 0.11444 | 0.082398 | 1.561 | 118.158 | 118.0435 | -0.004577 | 122.1863 | 121.5775 | 113.2095 | -122.4014 | 122.4335 | 122.3465 | 95.7642 | -122.2366
1118.6406 | 122.3923 | -118.8034 | 3.4927 | -0.43899 | 0.023121 | 3.4612 | 0.039248 | 0.11001 | 0.010095 | -0.017854 | -0.2072 | -0.024001 | 0.051988 | 0.040259 | 3.2954 | -0.037489 | 2.4902 | -1.5839 | -6.4362 | -118.7897 | 3.273 | -118.8583 | -118.9316 | -117.2653 | -23.0713 | -0.49896 | 3.5477 | 3.4927 | -118.7073 | -118.7347 | -0.054931 | -0.12817 | -0.21973 | 117.2195 | 0.013733 | 0.14191 | -1.0025 | 0.096131 | 0.068665 | 0.054931 | 1.5381 | 118.3044 | 118.2358 | 0 | 122.0764 | 121.2936 | 112.3672 | -122.4243 | 122.3511 | 122.2961 | 95.7321 | -122.2275
1119.6406 | 122.3877 | -118.7347 | 3.5522 | -0.13381 | 0.027394 | 3.4505 | 0.050997 | 0.1068 | 0.020776 | -0.022126 | -0.11565 | -0.032546 | 0.043443 | 0.043464 | 3.2944 | -0.030012 | 2.5497 | -1.4191 | -6.3309 | -118.7668 | 3.3234 | -118.7851 | -118.8995 | -117.1783 | -21.9086 | -0.48065 | 3.6026 | 3.5248 | -118.6615 | -118.6615 | -0.050354 | -0.16479 | -0.22888 | 117.3157 | -0.032044 | 0.13275 | -1.0025 | 0.073242 | 0.073242 | 0.050354 | 1.5564 | 118.2541 | 118.1808 | -0.027466 | 122.0581 | 121.2845 | 112.4039 | -122.4518 | 122.3373 | 122.2595 | 96.8262 | -122.2137
1120.6406 | 122.3831 | -118.7302 | 3.5431 | -0.072774 | 0.035939 | 3.4473 | 0.048861 | 0.10787 | 0.0068901 | -0.023195 | 0.0522 | -0.012251 | 0.032762 | 0.042396 | 3.289 | -0.028944 | 2.5589 | -1.2863 | -6.015 | -121.2753 | 3.3051 | -118.7714 | -118.8492 | -116.9678 | -20.5627 | -0.4715 | 3.5797 | 3.5202 | -118.6386 | -118.6295 | -0.041198 | -0.11902 | -0.23804 | 117.4438 | -2.5452 | -2.4261 | -0.98419 | 0.091553 | 0.10071 | 0.036621 | 1.7624 | 118.2587 | 118.158 | -0.022888 | 122.0352 | 121.2891 | 112.7151 | -122.3923 | 122.3099 | 122.2504 | 98.1674 | -122.1725
1121.6406 | 122.4472 | -106.9977 | 3.4241 | -0.59157 | 0.015645 | 3.4505 | 0.027499 | 0.087577 | 0.04107 | -0.011445 | 0.067459 | -0.033614 | 0.041307 | 0.0456 | 3.2944 | -0.030012 | 2.005 | -1.7624 | -6.1386 | -127.1896 | 3.1448 | -88.0829 | -77.298 | -117.215 | -21.0526 | -0.54474 | 3.4241 | 3.3463 | -81.9992 | -72.8897 | 18.9148 | 29.6997 | -0.27924 | 105.2353 | -20.192 | -49.8917 | -1.4191 | 24.9985 | 34.108 | 0 | -10.2173 | 106.4529 | 72.345 | -0.07782 | 110.1425 | 109.0027 | 100.8591 | -80.722 | 110.4218 | 110.3439 | 85.9451 | -76.3138
1122.6406 | 122.406 | -110.1471 | 3.5843 | 0.018779 | 0.056233 | 3.4462 | 0.036044 | 0.095053 | 0.027185 | -0.0039683 | -1.3821 | -0.022933 | 0.055192 | 0.0456 | 3.2901 | -0.032148 | 2.2934 | -1.6113 | -6.1615 | -148.8007 | 3.2547 | -99.1333 | -91.8869 | -117.0822 | -21.46 | -0.47607 | 3.6484 | 3.5797 | -97.5357 | -88.9389 | 11.0138 | 18.2602 | -0.32959 | 108.5358 | -38.6536 | -56.9138 | -1.2909 | 12.6114 | 21.2082 | 0.064086 | -6.9351 | 109.671 | 88.4628 | -0.004578 | 113.4018 | 112.4405 | 103.9856 | -95.4712 | 113.7955 | 113.7268 | 88.6871 | -92.5232
1123.6406 | 122.2824 | -118.7668 | 3.5065 | 0.41551 | 0.050892 | 3.4473 | 0.039248 | 0.10146 | 0.010095 | -0.028535 | 0.3116 | -0.01866 | 0.051988 | 0.052009 | 3.2986 | -0.036421 | 2.4536 | -1.2863 | -5.8823 | -118.8034 | 3.2639 | -118.7714 | -118.8675 | -117.1967 | -20.8466 | -0.53558 | 3.5568 | 3.5019 | -118.6798 | -118.689 | -0.004577 | -0.10071 | -0.24262 | 117.4805 | -0.036621 | 0.064087 | -1.0529 | 0.086975 | 0.07782 | 0.050354 | 1.5701 | 118.2312 | 118.1534 | -0.004578 | 122.0306 | 121.2204 | 112.8845 | -122.374 | 122.3236 | 122.2687 | 97.9202 | -122.1954
1124.7031 | 122.4243 | -118.0115 | 4.1519 | 0.58335 | 0.032734 | 3.4409 | 0.026431 | 0.099326 | -0.010199 | -0.024263 | 0.87617 | -0.034682 | 0.049852 | 0.022101 | 3.2677 | -0.010786 | 3.2776 | -1.149 | -5.3925 | -118.0527 | 3.9597 | -118.0023 | -118.0344 | -116.4276 | -20.2789 | -0.28839 | 4.2297 | 4.1473 | -117.9108 | -117.9016 | 0.009156 | -0.022888 | -0.19226 | 116.8625 | -0.041198 | -0.01831 | -0.87433 | 0.10071 | 0.10986 | 0.077819 | 1.5839 | 117.7231 | 117.6132 | -0.004578 | 121.9711 | 121.2891 | 112.619 | -122.1863 | 122.2412 | 122.1588 | 97.7325 | -122.0535
1125.6406 | 122.2458 | -118.808 | 3.4332 | 0.50706 | 0.039143 | 3.458 | 0.036044 | 0.10146 | 0.015435 | -0.022126 | 0.55574 | -0.024001 | 0.055192 | 0.052009 | 3.2847 | -0.028944 | 2.3849 | -1.4557 | -5.8365 | -118.9087 | 3.1952 | -118.8446 | -118.9453 | -117.2928 | -21.1166 | -0.52643 | 3.4836 | 3.4149 | -118.7027 | -118.721 | -0.036621 | -0.13733 | -0.23804 | 117.3523 | -0.10071 | 0.036621 | -1.0483 | 0.10528 | 0.086975 | 0.050354 | 1.5152 | 118.2816 | 118.1946 | -0.018311 | 122.0032 | 121.1929 | 112.9715 | -122.3785 | 122.2916 | 122.2229 | 97.6913 | -122.1542
1126.6406 | 122.2595 | -118.7164 | 3.4973 | 0.56809 | 0.048756 | 3.4526 | 0.048861 | 0.11428 | 0.02398 | -0.010377 | 0.2353 | -0.022933 | 0.061601 | 0.040259 | 3.2869 | -0.025739 | 2.3346 | -1.1261 | -5.6259 | -118.4372 | 3.3096 | -118.7439 | -118.8126 | -117.1005 | -21.4096 | -0.49896 | 3.5797 | 3.4973 | -118.6066 | -118.6386 | -0.027465 | -0.09613 | -0.18768 | 117.5903 | 0.27924 | 0.37537 | -1.1627 | 0.10986 | 0.07782 | 0.082398 | 1.6159 | 118.2175 | 118.1396 | 0 | 122.0261 | 121.051 | 113.0905 | -122.3099 | 122.2961 | 122.2137 | 97.3068 | -122.1359
1127.6406 | 122.3007 | -118.4784 | 3.7079 | 0.62913 | 0.058369 | 3.4505 | 0.03818 | 0.11535 | 0.013299 | -0.033876 | 0.72359 | -0.027205 | 0.054124 | 0.061622 | 3.2783 | -0.028944 | 2.7237 | -1.442 | -5.6396 | -118.4784 | 3.4836 | -118.5013 | -118.6111 | -116.8442 | -21.3776 | -0.45319 | 3.7857 | 3.7125 | -118.4006 | -118.3731 | -0.022888 | -0.13275 | -0.2243 | 117.0364 | 0 | 0.13275 | -0.98419 | 0.07782 | 0.10529 | 0.07782 | 1.6342 | 118.0252 | 117.9199 | 0.004577 | 121.962 | 121.2021 | 112.8387 | -122.319 | 122.2641 | 122.1909 | 97.1008 | -122.081
1128.6406 | 30.011 | -118.7302 | 3.4195 | 0.40025 | 0.0038952 | 3.5306 | -0.061155 | 0.13885 | 0.066705 | -0.030671 | 1.5323 | -0.019728 | 0.069078 | 0.0456 | 3.2783 | -0.010786 | 1.9226 | -2.0462 | -5.3513 | -118.8858 | 3.1815 | -94.8212 | -87.6114 | -117.1509 | -21.3226 | -0.47607 | 3.4744 | 3.4149 | -106.6406 | -107.254 | 23.909 | 31.1188 | -0.23804 | 116.684 | -0.15564 | -31.2744 | -1.4969 | 12.0895 | 11.4761 | 0.054931 | 1.5793 | 118.2541 | 106.778 | -0.004578 | 121.9116 | 120.6528 | 113.3789 | -91.0309 | 122.2046 | 122.1451 | 97.4075 | -110.6735
1129.6406 | 115.4251 | -97.3801 | 24.527 | 0.61387 | 0.017781 | 0.0068819 | 3.6484 | 0.091849 | 0.74069 | -0.011445 | 0.22005 | -0.01866 | 0.05626 | 0.043464 | 2.7411 | -0.024671 | -0.064087 | 22.9431 | -3.4927 | 21.7209 | 23.4558 | -98.0759 | -97.9614 | -96.0388 | -18.3975 | -0.28381 | 24.6277 | 24.6323 | -97.3251 | -97.3572 | -0.6958 | -0.58136 | -1.0712 | 120.3232 | 119.101 | 119.6823 | -24.5911 | 0.054932 | 0.022888 | 0.10071 | 1.3412 | 97.0963 | 97.0734 | 0.10528 | 120.8359 | 97.316 | 93.8873 | -122.4884 | 122.0078 | 122.0123 | 78.9825 | -121.8842
1130.6406 | 122.2733 | -117.0593 | 5.0217 | 3.4367 | 0.038075 | 0.0047449 | 4.2006 | 0.098258 | 0.73 | -0.022126 | 0.44893 | -0.028273 | 0.041307 | 0.042396 | 3.2281 | -0.026808 | -0.13275 | 4.0192 | -4.8935 | 2.8656 | 4.7058 | -117.1005 | -117.1417 | -115.4205 | -25.3967 | -0.35248 | 5.04 | 4.9942 | -116.9769 | -116.9952 | -0.041199 | -0.082398 | -0.31586 | 121.0785 | 119.9249 | 120.0073 | -5.1544 | 0.082397 | 0.064087 | 0.018311 | 1.6388 | 116.7068 | 116.6428 | -0.027465 | 121.7651 | 116.9266 | 112.1658 | -122.1634 | 122.0993 | 122.0535 | 91.6626 | -122.0169
1131.6406 | 122.2595 | -117.4576 | 4.6326 | 0.38499 | 0.017781 | 0.01329 | 4.2017 | 0.11428 | 0.74175 | -0.027467 | 0.69307 | -0.030409 | 0.049852 | 0.048804 | 3.2463 | -0.019331 | -0.068665 | 3.6621 | -5.0903 | 2.8244 | 4.3213 | -117.4667 | -117.4988 | -115.6998 | -24.9298 | -0.37537 | 4.6692 | 4.628 | -117.3477 | -117.3798 | -0.009155 | -0.041198 | -0.31128 | 121.1197 | 120.282 | 120.3232 | -4.7012 | 0.10986 | 0.07782 | 0.036621 | 1.7578 | 117.0822 | 117.0044 | -0.004577 | 121.7789 | 117.3889 | 112.3672 | -122.1313 | 122.1268 | 122.0856 | 92.5278 | -122.0123
1132.7031 | 122.3007 | -117.7048 | 4.3488 | 0.079814 | -0.0035808 | 0.00047294 | 4.1953 | 0.092917 | 0.71398 | -0.026399 | 0.22005 | -0.024001 | 0.059465 | 0.041327 | 3.2452 | -0.026808 | -0.12817 | 3.3508 | -5.072 | 2.4261 | 4.0787 | -117.7002 | -117.7917 | -116.0568 | -25.0992 | -0.34332 | 4.3854 | 4.335 | -117.6132 | -117.627 | 0.004578 | -0.086975 | -0.27008 | 121.0556 | 120.1309 | 120.2179 | -4.4769 | 0.091553 | 0.07782 | 0.036621 | 1.6479 | 117.3615 | 117.2836 | -0.013733 | 121.7834 | 117.5766 | 112.6328 | -122.1405 | 122.0901 | 122.0398 | 92.6056 | -121.9757
1133.6406 | 122.2046 | -117.8238 | 4.2252 | 0.43077 | 0.026326 | 0.0047449 | 4.2038 | 0.095053 | 0.72787 | -0.029603 | 0.61677 | -0.034682 | 0.044511 | 0.041327 | 3.2559 | -0.022535 | -0.30212 | 3.1586 | -5.0903 | 2.1652 | 3.9459 | -117.7963 | -117.9108 | -116.0522 | -25.5478 | -0.39825 | 4.2618 | 4.1931 | -117.778 | -117.7734 | 0.027466 | -0.086975 | -0.27924 | 120.9824 | 119.989 | 120.076 | -4.5273 | 0.045777 | 0.050355 | 0.036621 | 1.7715 | 117.4255 | 117.3752 | -0.032044 | 121.7697 | 117.5217 | 112.7335 | -122.1359 | 122.0856 | 122.0169 | 92.276 | -121.9986
1134.6406 | 122.2412 | -117.9703 | 4.0878 | 0.00352 | 0.014576 | 0.0015409 | 4.206 | 0.091849 | 0.73962 | -0.030671 | 0.44893 | -0.038954 | 0.03917 | 0.049872 | 3.2559 | -0.030012 | -0.61798 | 3.0167 | -5.0674 | 2.1011 | 3.7994 | -117.9199 | -118.0069 | -116.153 | -24.9023 | -0.37537 | 4.1107 | 4.0787 | -117.8787 | -117.8925 | 0.050354 | -0.036621 | -0.28839 | 120.9869 | 120.0714 | 120.108 | -4.7058 | 0.091553 | 0.07782 | 0.022888 | 1.8173 | 117.5949 | 117.5171 | -0.009156 | 121.7697 | 117.3523 | 112.9028 | -122.0947 | 122.081 | 122.049 | 93.0679 | -121.9803
1135.6406 | 122.2137 | -117.9932 | 4.0787 | 0.46128 | -0.011058 | 0.015426 | 4.2006 | 0.081168 | 0.72253 | -0.029603 | 0.58626 | -0.046431 | 0.055192 | 0.044532 | 3.2527 | -0.025739 | -0.59967 | 2.9388 | -5.191 | 1.9867 | 3.7582 | -117.9565 | -118.0298 | -116.1942 | -25.0992 | -0.42114 | 4.0787 | 4.0421 | -117.897 | -117.9382 | 0.036621 | -0.036621 | -0.32043 | 120.932 | 119.9799 | 120.0165 | -4.6783 | 0.09613 | 0.054932 | 0 | 1.799 | 117.572 | 117.5171 | -0.036621 | 121.7514 | 117.3935 | 112.8021 | -122.1085 | 122.0718 | 122.0352 | 92.894 | -122.0169
1136.6406 | 122.1634 | -118.0389 | 3.978 | 0.7512 | -0.0046498 | 0.0090179 | 4.207 | 0.10467 | 0.73641 | -0.033876 | 0.35738 | -0.034682 | 0.037034 | 0.040259 | 3.2527 | -0.020399 | -0.83771 | 2.8381 | -5.3192 | 1.9318 | 3.6575 | -118.0389 | -118.1351 | -116.1484 | -25.5478 | -0.37994 | 4.0146 | 3.9459 | -117.9703 | -118.0115 | 0 | -0.096131 | -0.32043 | 120.8771 | 119.9707 | 120.0668 | -4.8157 | 0.068664 | 0.027465 | 0.036621 | 1.8906 | 117.659 | 117.6315 | -0.032043 | 121.6965 | 117.2012 | 112.7197 | -122.113 | 122.0535 | 121.9849 | 92.4911 | -121.9894
1137.6406 | 122.2229 | -118.0756 | 3.9047 | 0.079814 | -0.0014448 | 0.01329 | 4.2028 | 0.10146 | 0.73535 | -0.034944 | 0.11323 | -0.038954 | 0.054124 | 0.043464 | 3.2623 | -0.027876 | -1.6251 | 2.8793 | -5.1315 | 1.9821 | 3.6301 | -118.0481 | -118.1488 | -116.1346 | -26.0971 | -0.3479 | 3.9413 | 3.8773 | -117.984 | -118.0435 | 0.027466 | -0.073242 | -0.27466 | 120.9549 | 120.0577 | 120.1309 | -5.5298 | 0.091553 | 0.032044 | 0.036621 | 1.9409 | 117.7277 | 117.6956 | -0.027466 | 121.7056 | 116.4505 | 112.944 | -122.0535 | 122.0169 | 121.9528 | 91.9785 | -121.9482
1138.6406 | 122.1909 | -118.0801 | 3.9001 | 0.81224 | 0.010304 | 0.014358 | 4.191 | 0.099326 | 0.73535 | -0.024263 | 0.021682 | -0.03575 | 0.053056 | 0.030646 | 3.2666 | -0.034284 | -1.8311 | 2.8336 | -5.1132 | 1.9135 | 3.6163 | -118.0664 | -118.1305 | -116.2308 | -26.3397 | -0.40283 | 3.923 | 3.8681 | -118.0206 | -118.0573 | 0.013733 | -0.050354 | -0.28381 | 120.9137 | 119.9936 | 120.0439 | -5.7312 | 0.059509 | 0.022888 | 0.022889 | 1.8494 | 117.6773 | 117.6544 | -0.032043 | 121.6965 | 116.2491 | 112.9669 | -122.0306 | 122.0032 | 121.9482 | 91.7404 | -121.9574
1139.6406 | 122.1817 | -118.0756 | 3.891 | -0.22536 | 0.0049632 | 0.012222 | 4.1996 | 0.089713 | 0.74709 | -0.036012 | 1.7459 | -0.037886 | 0.032762 | 0.046668 | 3.2666 | -0.040693 | -1.4465 | 2.8564 | -5.1956 | 2.0416 | 3.6301 | -118.071 | -118.1168 | -116.2445 | -26.152 | -0.38452 | 3.9459 | 3.8727 | -117.9932 | -117.9932 | 0.004578 | -0.041198 | -0.26093 | 120.932 | 120.1172 | 120.1584 | -5.3375 | 0.082398 | 0.082398 | 0.054932 | 1.8311 | 117.691 | 117.6086 | -0.01831 | 121.7056 | 116.629 | 112.8799 | -122.0078 | 122.0215 | 121.9482 | 91.9235 | -121.8842
1140.6406 | 122.0581 | -118.1259 | 3.9093 | -0.27114 | -0.014263 | 0.017563 | 4.207 | 0.086509 | 0.74603 | -0.018922 | -0.10039 | -0.031478 | 0.054124 | 0.048804 | 3.258 | -0.030012 | -2.6962 | 2.774 | -4.9255 | 1.8036 | 3.6255 | -118.0481 | -118.1625 | -116.5604 | -109.4879 | -0.48065 | 3.9413 | 3.8864 | -118.0435 | -118.071 | 0.07782 | -0.036621 | -0.28381 | 120.9 | 119.9295 | 119.9661 | -6.6055 | 0.082398 | 0.054932 | 0.032043 | 1.5656 | 117.6453 | 117.5903 | -0.022888 | 121.7514 | 115.4297 | 113.2004 | -122.0718 | 122.0673 | 122.0123 | 8.638 | -121.9803
1141.6406 | 122.2275 | -0.47607 | 121.6461 | -0.24062 | 0.0049632 | 0.016495 | 0.35861 | -0.038461 | -0.011268 | -0.026399 | -0.45134 | -0.03575 | 0.051988 | 0.043464 | 0.020587 | 0.073595 | 0.045776 | 0.14191 | -0.58594 | 0.054932 | 0.21973 | -0.5127 | -0.63171 | 0.29297 | 6.7154 | 0.022888 | 121.8384 | 121.7239 | -0.61798 | -0.62256 | -0.036621 | -0.15564 | -121.4264 | 0.61798 | 0.53101 | 0.68665 | -121.6003 | -0.14191 | -0.14648 | 0.19226 | 0.76904 | 0.49896 | 0.64545 | 0.07782 | 0.6958 | 0.52185 | -0.10986 | -122.2778 | 122.3145 | 122.2 | 7.1915 | -122.2687
1142.6406 | 122.3465 | -0.48523 | 121.7239 | -0.11855 | 0.0028272 | 0.049606 | 0.35968 | -0.051278 | -0.0037909 | -0.032808 | 0.12849 | -0.028273 | 0.043443 | 0.037055 | 0.022724 | 0.078936 | 0.17395 | 0.032043 | -0.52643 | 0.086975 | 0.19684 | -0.49439 | -0.66376 | 0.41657 | 7.4936 | 0.045776 | 121.8933 | 121.7789 | -0.60883 | -0.62714 | -0.009156 | -0.17853 | -121.5271 | 0.51727 | 0.5722 | 0.75073 | -121.55 | -0.1236 | -0.14191 | 0.16937 | 0.90179 | 0.53101 | 0.67291 | 0.054932 | 0.68207 | 0.65918 | -0.041199 | -122.3877 | 122.3785 | 122.2641 | 7.9788 | -122.3511
1143.6406 | 122.3007 | -0.52643 | 121.8201 | -0.30166 | 0.015645 | 0.00047294 | 0.36716 | -0.029916 | -0.010199 | -0.029603 | -0.28349 | -0.028273 | 0.055192 | 0.030646 | 0.021655 | 0.084276 | -0.027466 | 0.064087 | -0.50354 | -0.009155 | 0.24261 | -0.54474 | -0.67291 | 0.47607 | 9.1003 | -0.041199 | 121.994 | 121.8475 | -0.62714 | -0.66376 | -0.018311 | -0.14648 | -121.5775 | 0.59052 | 0.51727 | 0.66376 | -121.8475 | -0.10071 | -0.13733 | 0.17395 | 1.0025 | 0.48523 | 0.62256 | 0.027466 | 0.76904 | 0.49896 | 0.022888 | -122.493 | 122.5204 | 122.374 | 9.6268 | -122.4838
1144.6406 | 122.0444 | -0.52643 | 121.8384 | -2.27 | 0.039143 | 0.0036769 | 0.38532 | -0.019235 | 0.017572 | -0.021058 | -0.39031 | -0.032546 | 0.066941 | 0.043464 | 0.02486 | 0.056505 | -0.054932 | 0.036621 | -0.50354 | 0.009155 | 0.27008 | -0.5127 | -0.64545 | 0.51727 | 5.8273 | -0.059509 | 122.0123 | 121.8658 | -0.63171 | -0.64087 | 0.013733 | -0.11902 | -121.5683 | 0.56305 | 0.53558 | 0.6546 | -121.8933 | -0.10529 | -0.11444 | 0.17395 | 1.0437 | 0.46692 | 0.58136 | 0.027466 | 0.79651 | 0.4715 | 0.022888 | -122.4838 | 122.5388 | 122.3923 | 6.3538 | -122.4792
1145.6406 | 121.9528 | -0.52643 | 121.8475 | -0.22536 | 0.038075 | 0.016495 | 0.37891 | -0.040597 | 0.0047541 | -0.016786 | -0.29875 | -0.029341 | 0.047715 | 0.032783 | 0.025928 | 0.072527 | -0.022888 | 0.009155 | -0.50354 | 0 | 0.23804 | -0.54016 | -0.68207 | 0.46692 | 7.8003 | -0.059509 | 122.049 | 121.9254 | -0.64087 | -0.6546 | -0.013733 | -0.15564 | -121.6095 | 0.53558 | 0.52643 | 0.68207 | -121.8704 | -0.11444 | -0.12817 | 0.20142 | 0.99335 | 0.46692 | 0.59509 | 0.07782 | 0.76446 | 0.50354 | 0.022888 | -122.5296 | 122.5754 | 122.4518 | 8.3267 | -122.5021
1146.6406 | 121.8292 | -0.51727 | 121.8887 | -0.072774 | 0.033803 | 0.0036769 | 0.38532 | -0.032052 | -0.0059269 | -0.0093093 | -0.31401 | -0.026137 | 0.059465 | 0.041327 | 0.02486 | 0.073595 | -0.022888 | 0.018311 | -0.48065 | 0.018311 | 0.23804 | -0.52643 | -0.6958 | 0.25635 | 4.1107 | -0.032043 | 122.0398 | 121.9025 | -0.63171 | -0.64545 | -0.009155 | -0.17853 | -121.6507 | 0.53558 | 0.53558 | 0.71411 | -121.9116 | -0.11444 | -0.12817 | 0.15106 | 0.77362 | 0.48523 | 0.6134 | 0.013733 | 0.75531 | 0.49438 | 0.036621 | -122.5845 | 122.5571 | 122.4197 | 4.628 | -122.5342
1147.6406 | 121.907 | -0.52185 | 121.907 | -0.13381 | 0.026326 | 0.0068819 | 0.37143 | -0.026712 | 0.00048206 | -0.0082413 | -0.23772 | -0.026137 | 0.047715 | 0.047736 | 0.0045661 | 0.077868 | 0.004578 | 0.050354 | -0.45319 | 0.013733 | 0.23346 | -0.54474 | -0.67291 | 0.30212 | 3.3142 | -0.022888 | 122.0306 | 121.9254 | -0.6134 | -0.61798 | -0.022888 | -0.15106 | -121.6736 | 0.5722 | 0.53558 | 0.68665 | -121.9025 | -0.091552 | -0.09613 | 0.1236 | 0.82397 | 0.49896 | 0.59509 | 0.018311 | 0.75531 | 0.52643 | 0.068665 | -122.58 | 122.5525 | 122.4472 | 3.8361 | -122.525
1148.6406 | 121.9208 | -0.51727 | 121.9208 | 2.4144 | 0.057301 | 0.0090179 | 0.39066 | -0.034188 | 0.0047541 | -0.01465 | 0.0522 | -0.022933 | 0.055192 | 0.043464 | 0.031268 | 0.078936 | 0.045776 | 0.07782 | -0.41199 | 0.036621 | 0.28839 | -0.48065 | -0.6134 | 0.21057 | 4.2297 | -0.059509 | 122.0627 | 121.9437 | -0.60425 | -0.64087 | 0.036621 | -0.09613 | -121.6324 | 0.59509 | 0.55389 | 0.65002 | -121.875 | -0.086975 | -0.1236 | 0.14191 | 0.72784 | 0.45776 | 0.58136 | 0.022889 | 0.80566 | 0.56305 | 0.10529 | -122.5342 | 122.58 | 122.4609 | 4.747 | -122.5616
1149.6406 | 122.1863 | -0.52643 | 121.9162 | -0.13381 | 0.040211 | 0.0047449 | 0.38639 | -0.024575 | -0.010199 | -0.023195 | -0.23772 | -0.027205 | 0.072282 | 0.043464 | 0.0302 | 0.075732 | -0.013733 | 0.018311 | -0.42572 | 0.022888 | 0.23346 | -0.54016 | -0.67749 | 0.20599 | 5.2002 | -0.022888 | 122.0718 | 121.9574 | -0.63171 | -0.63171 | -0.013733 | -0.15106 | -121.6827 | 0.54474 | 0.54932 | 0.70038 | -121.9299 | -0.10529 | -0.10529 | 0.15564 | 0.73242 | 0.50354 | 0.60883 | 0.041198 | 0.75989 | 0.5127 | 0.10071 | -122.5937 | 122.5983 | 122.4838 | 5.7266 | -122.5479
1150.6406 | 122.2229 | -0.50354 | 121.8979 | 0.095073 | 0.015645 | 0.0047449 | 0.37891 | -0.028848 | 0.00048206 | 0.0088487 | -0.10039 | -0.026137 | 0.063737 | 0.039191 | 0.026996 | 0.073595 | 0.068665 | 0.17395 | -0.36621 | 0.009155 | 0.28839 | -0.46692 | -0.59967 | 0.27008 | 5.1132 | -0.041199 | 122.081 | 121.9803 | -0.59052 | -0.64087 | 0.036621 | -0.09613 | -121.6095 | 0.67749 | 0.5127 | 0.60883 | -121.8292 | -0.086975 | -0.13733 | 0.18311 | 0.77362 | 0.46234 | 0.59967 | 0.082398 | 0.79193 | 0.5722 | 0.13733 | -122.4976 | 122.5845 | 122.4838 | 5.6168 | -122.5388
1151.6406 | 122.3877 | -0.5127 | 121.9574 | 0.32395 | 0.038075 | 0.00047294 | 0.36289 | -0.024575 | 0.0036861 | -0.026399 | 0.26582 | -0.028273 | 0.049852 | 0.042396 | 0.02486 | 0.0768 | -0.054932 | -0.027466 | -0.45776 | -0.018311 | 0.2243 | -0.52185 | -0.67291 | 0.18768 | 5.571 | -0.10071 | 122.1085 | 122.0032 | -0.64545 | -0.63629 | -0.009156 | -0.16022 | -121.7331 | 0.48523 | 0.49438 | 0.6546 | -122.0123 | -0.13275 | -0.1236 | 0.15106 | 0.70038 | 0.41199 | 0.53558 | 0.045777 | 0.737 | 0.45776 | 0.054931 | -122.6303 | 122.6212 | 122.5159 | 6.0837 | -122.5937
1152.6406 | 122.4609 | -0.52643 | 121.9345 | 0.47654 | 0.073323 | 0.0068819 | 0.39707 | -0.034188 | -0.0048589 | -0.0093093 | 0.17427 | -0.020796 | 0.05092 | 0.0456 | 0.016315 | 0.089617 | -0.11902 | 0.045776 | -0.41657 | -0.027466 | 0.25177 | -0.51727 | -0.6546 | 0.32959 | 4.5044 | -0.059509 | 122.113 | 122.0215 | -0.61798 | -0.63171 | 0.009155 | -0.12817 | -121.6827 | 0.5722 | 0.49896 | 0.62714 | -122.0535 | -0.091553 | -0.10529 | 0.17853 | 0.85602 | 0.46692 | 0.5722 | 0.086975 | 0.7782 | 0.40741 | 0.10986 | -122.5891 | 122.6395 | 122.5479 | 5.0308 | -122.5662
1153.6406 | 122.4152 | -0.48523 | 121.9345 | 0.46128 | 0.035939 | -0.0059361 | 0.3992 | -0.028848 | -0.0069949 | -0.01465 | 0.34212 | -0.01866 | 0.049852 | 0.029578 | 0.017383 | 0.096026 | -0.050354 | -0.045776 | -0.45776 | -0.018311 | 0.25635 | -0.52643 | -0.65002 | 0.12817 | 5.896 | 0.004578 | 122.168 | 122.049 | -0.60883 | -0.61798 | -0.041199 | -0.1648 | -121.6782 | 0.43945 | 0.46692 | 0.63171 | -121.9849 | -0.1236 | -0.13275 | 0.23346 | 0.6134 | 0.48981 | 0.62256 | 0.11444 | 0.74158 | 0.43488 | 0.027465 | -122.5845 | 122.6532 | 122.5342 | 6.3812 | -122.5525
1154.6406 | 122.5021 | -0.50354 | 121.9254 | 0.52232 | 0.030598 | 0.0015409 | 0.38425 | -0.034188 | -0.013404 | -0.027467 | 0.44893 | -0.026137 | 0.035966 | 0.043464 | 0.022724 | 0.081072 | -0.013733 | 0.013733 | -0.39825 | 0.004578 | 0.21973 | -0.5127 | -0.6546 | 0.46234 | 6.5735 | 0.013733 | 122.0993 | 122.0398 | -0.59967 | -0.62256 | -0.009155 | -0.15106 | -121.7056 | 0.51727 | 0.50812 | 0.65918 | -121.9391 | -0.09613 | -0.11902 | 0.17395 | 0.96588 | 0.51727 | 0.63629 | 0.11444 | 0.72327 | 0.48981 | 0.10529 | -122.58 | 122.6028 | 122.5433 | 7.077 | -122.5479
1155.6406 | 122.4609 | -0.50812 | 121.9254 | 0.46128 | 0.028462 | 0.015426 | 0.39066 | -0.022439 | -0.0069949 | -0.045625 | 0.47945 | -0.029341 | 0.063737 | 0.046668 | 0.026996 | 0.084276 | -0.027466 | -0.041199 | -0.41199 | -0.004578 | 0.21973 | -0.52185 | -0.6546 | 0.71869 | 5.2689 | -0.041199 | 122.113 | 122.0215 | -0.60425 | -0.62714 | -0.013733 | -0.14648 | -121.7056 | 0.46692 | 0.50354 | 0.65002 | -121.9528 | -0.09613 | -0.11902 | 0.18768 | 1.2268 | 0.46692 | 0.58594 | 0.09613 | 0.72784 | 0.48065 | 0.096131 | -122.58 | 122.6212 | 122.5296 | 5.777 | -122.5525
1156.6406 | 122.5159 | -0.48981 | 121.9254 | 0.59861 | 0.041279 | 0.00047294 | 0.3757 | -0.019235 | -0.010199 | -0.027467 | 0.4947 | -0.032546 | 0.057328 | 0.033851 | 0.022724 | 0.078936 | 0.004578 | -0.009155 | -0.38452 | 0.009155 | 0.23346 | -0.52185 | -0.6546 | 0.24261 | 4.4266 | 0.009155 | 122.1085 | 122.0306 | -0.59967 | -0.6134 | -0.032044 | -0.1648 | -121.6919 | 0.48065 | 0.49896 | 0.66376 | -121.9208 | -0.10986 | -0.1236 | 0.1831 | 0.73242 | 0.49896 | 0.62256 | 0.10529 | 0.72327 | 0.49439 | 0.10529 | -122.58 | 122.5983 | 122.5204 | 4.9164 | -122.5388
1157.6406 | 122.5616 | -0.46692 | 121.9208 | 0.62913 | 0.010304 | -0.00059506 | 0.37891 | -0.036325 | -0.018744 | -0.024263 | 0.571 | -0.044295 | 0.051988 | 0.038123 | 0.022724 | 0.088549 | 0.082397 | 0.064087 | -0.32501 | 0.073242 | 0.20599 | -0.49896 | -0.64545 | 0.40283 | 4.5685 | 0.059509 | 122.1313 | 122.0215 | -0.58136 | -0.58136 | -0.032043 | -0.17853 | -121.7148 | 0.53101 | 0.54016 | 0.71869 | -121.8384 | -0.11444 | -0.11444 | 0.21057 | 0.86975 | 0.52643 | 0.64087 | 0.10071 | 0.67291 | 0.54932 | 0.14191 | -122.5662 | 122.5983 | 122.4884 | 5.0354 | -122.5021
1158.6406 | 122.5021 | -0.46692 | 121.9437 | -0.11855 | 0.020985 | 0.0047449 | 0.36289 | -0.029916 | -0.017676 | -0.030671 | 0.47945 | -0.026137 | 0.062669 | 0.032783 | 0.021655 | 0.0768 | 0.041199 | 0.10529 | -0.28381 | 0.064087 | 0.18768 | -0.48065 | -0.61798 | 0.41199 | 2.2064 | 0.054932 | 122.1222 | 122.0627 | -0.56305 | -0.58136 | -0.013733 | -0.15106 | -121.756 | 0.5722 | 0.53101 | 0.68207 | -121.9025 | -0.09613 | -0.11444 | 0.17853 | 0.87891 | 0.52185 | 0.63629 | 0.11902 | 0.6546 | 0.50812 | 0.18311 | -122.5616 | 122.5891 | 122.5296 | 2.6733 | -122.525
1159.6406 | 122.4976 | -0.4715 | 121.9437 | 0.47654 | 0.018849 | 0.0026089 | 0.36823 | -0.024575 | -0.027289 | -0.025331 | 0.4947 | -0.046431 | 0.060533 | 0.041327 | 0.0099061 | 0.088549 | 0.064087 | 0.082397 | -0.29755 | 0.045776 | 0.21515 | -0.48981 | -0.59967 | 0.45776 | 0.76904 | 0.041199 | 122.1405 | 122.0764 | -0.58136 | -0.58594 | -0.01831 | -0.12817 | -121.7285 | 0.55389 | 0.51727 | 0.64545 | -121.8796 | -0.10986 | -0.11444 | 0.19684 | 0.92926 | 0.5127 | 0.62714 | 0.13275 | 0.68665 | 0.53558 | 0.17395 | -122.5433 | 122.612 | 122.5479 | 1.2405 | -122.5296
1160.6406 | 122.5525 | -0.48065 | 121.9391 | 0.46128 | -0.0025128 | 0.014358 | 0.37143 | -0.042733 | -0.020881 | -0.038148 | 0.25056 | -0.051772 | 0.06801 | 0.055213 | 0.025928 | 0.088549 | 0.004578 | 0.059509 | -0.32501 | 0.032043 | 0.2243 | -0.48065 | -0.63171 | 0.41199 | 1.7899 | 0.009155 | 122.1176 | 122.0398 | -0.59509 | -0.59509 | 0 | -0.15106 | -121.7148 | 0.54016 | 0.5127 | 0.66376 | -121.9345 | -0.11444 | -0.11444 | 0.17853 | 0.89264 | 0.48981 | 0.60425 | 0.10071 | 0.70496 | 0.48523 | 0.15564 | -122.5708 | 122.5983 | 122.5204 | 2.2705 | -122.5342
1161.6406 | 122.5479 | -0.53101 | 121.9162 | 0.32395 | -0.012126 | -0.00059506 | 0.37464 | -0.049142 | -0.028357 | -0.03708 | 0.11323 | -0.036818 | 0.038102 | 0.02851 | 0.017383 | 0.086413 | 0 | 0.045776 | -0.32044 | 0.041199 | 0.21515 | -0.48523 | -0.62714 | 0.40283 | 1.0666 | 0.009155 | 122.1268 | 122.0169 | -0.6134 | -0.64087 | 0.045777 | -0.09613 | -121.7011 | 0.57678 | 0.5722 | 0.66834 | -121.9162 | -0.082397 | -0.10986 | 0.21057 | 0.93384 | 0.54016 | 0.65002 | 0.10071 | 0.74616 | 0.53101 | 0.21057 | -122.5433 | 122.6578 | 122.5479 | 1.5976 | -122.5571
1162.6406 | 122.5616 | -0.48523 | 121.9574 | -0.19484 | -0.0057178 | 0.011154 | 0.37998 | -0.013894 | -0.029426 | -0.027467 | -0.28349 | -0.045363 | 0.03383 | 0.02851 | 0.0067021 | 0.077868 | 0.07782 | 0.13275 | -0.25177 | 0.073242 | 0.21515 | -0.48523 | -0.63629 | 0.45319 | 0.66834 | 0.068665 | 122.1268 | 122.0535 | -0.60425 | -0.59967 | 0 | -0.15106 | -121.7422 | 0.61798 | 0.55847 | 0.70953 | -121.8796 | -0.11902 | -0.11444 | 0.16937 | 0.93841 | 0.55389 | 0.66834 | 0.096131 | 0.70038 | 0.56305 | 0.23346 | -122.5937 | 122.612 | 122.5388 | 1.1536 | -122.5571
1163.6406 | 122.5662 | -0.46234 | 121.9849 | 0.12559 | 0.0049632 | 0.0015409 | 0.3757 | -0.03312 | -0.029426 | -0.049897 | -0.17668 | -0.041091 | 0.044511 | 0.034919 | 0.019519 | 0.087481 | 0.054932 | 0.10986 | -0.27924 | 0.059509 | 0.21973 | -0.48981 | -0.62714 | 0.48065 | 0.76904 | 0.054932 | 122.1451 | 122.0398 | -0.58594 | -0.60425 | -0.027466 | -0.1648 | -121.7651 | 0.5722 | 0.52185 | 0.68665 | -121.9299 | -0.1236 | -0.14191 | 0.16022 | 0.94299 | 0.51727 | 0.65918 | 0.054932 | 0.68207 | 0.51727 | 0.18311 | -122.612 | 122.6074 | 122.5021 | 1.2314 | -122.5891
1164.6406 | 122.5479 | -0.49439 | 121.9482 | -0.042256 | -0.0067858 | 0.017563 | 0.37891 | -0.038461 | -0.0059269 | -0.038148 | -0.40556 | -0.033614 | 0.037034 | 0.039191 | 0.025928 | 0.070391 | 0.054932 | 0.11902 | -0.25177 | 0.073242 | 0.21057 | -0.5127 | -0.6546 | 0.42114 | 1.0345 | 0 | 122.1588 | 122.049 | -0.59509 | -0.60883 | -0.01831 | -0.16022 | -121.7377 | 0.6134 | 0.56763 | 0.72784 | -121.8933 | -0.10071 | -0.11444 | 0.21057 | 0.91553 | 0.49439 | 0.60883 | 0.10071 | 0.70496 | 0.54932 | 0.24262 | -122.6028 | 122.6532 | 122.5433 | 1.5289 | -122.5571
1165.6406 | 122.6028 | -0.48065 | 121.9757 | -6.9392 | 0.0049632 | 0.0079499 | 0.36289 | -0.024575 | -0.020881 | -0.026399 | -0.48186 | -0.037886 | 0.041307 | 0.033851 | 0.020587 | 0.073595 | -0.027466 | 0.19226 | -0.2243 | 0.050354 | 0.20599 | -0.5127 | -0.63629 | 0.41657 | 1.3504 | 0.022888 | 122.1634 | 122.0398 | -0.57678 | -0.60425 | -0.032043 | -0.15564 | -121.7697 | 0.67291 | 0.53101 | 0.68665 | -122.0032 | -0.09613 | -0.1236 | 0.18768 | 0.89722 | 0.50354 | 0.62714 | 0.064087 | 0.68665 | 0.45319 | 0.25635 | -122.612 | 122.644 | 122.5204 | 1.8311 | -122.58
1166.6406 | 122.4976 | -0.48065 | 122.0261 | -0.25588 | 0.0060322 | 0.0036769 | 0.37143 | -0.03312 | -0.0037909 | -0.027467 | -0.42082 | -0.038954 | 0.048783 | 0.038123 | 0.021655 | 0.072527 | 0.041199 | 0.11902 | -0.27008 | 0.045776 | 0.21973 | -0.49896 | -0.63171 | 0.4303 | 1.1307 | -0.004578 | 122.1817 | 122.0764 | -0.58136 | -0.60883 | -0.01831 | -0.15106 | -121.8063 | 0.59967 | 0.52643 | 0.67749 | -121.9849 | -0.10071 | -0.12817 | 0.15564 | 0.91095 | 0.47607 | 0.60425 | 0.050354 | 0.70038 | 0.52185 | 0.21057 | -122.6578 | 122.6624 | 122.5571 | 1.6113 | -122.6349
1167.6406 | 122.4701 | -0.54016 | 122.0306 | -0.30166 | 0.0060322 | 0.0026089 | 0.37784 | -0.020303 | -0.0059269 | -0.027467 | -0.48186 | -0.03575 | 0.049852 | 0.058417 | 0.016315 | 0.0768 | 0.009155 | 0.073242 | -0.32959 | 0.004578 | 0.2243 | -0.49896 | -0.65002 | 0.40283 | 0.59052 | -0.050354 | 122.2092 | 122.0673 | -0.60883 | -0.63629 | 0.041199 | -0.10986 | -121.8063 | 0.6134 | 0.54474 | 0.6546 | -122.0215 | -0.068665 | -0.096131 | 0.17853 | 0.94299 | 0.48981 | 0.58594 | 0.036621 | 0.76446 | 0.54932 | 0.21057 | -122.6807 | 122.7493 | 122.6074 | 1.1307 | -122.6669
1168.6406 | 122.4609 | -0.52643 | 122.0352 | -0.2864 | 0.017781 | 0.011154 | 0.3757 | -0.016031 | -0.0027229 | -0.034944 | -0.49712 | -0.030409 | 0.051988 | 0.02851 | 0.026996 | 0.072527 | -0.041199 | 0.009155 | -0.36163 | -0.013733 | 0.25177 | -0.52643 | -0.67291 | 0.40741 | -0.027466 | -0.082397 | 122.1954 | 122.0718 | -0.6134 | -0.64545 | 0 | -0.14648 | -121.7834 | 0.53558 | 0.5127 | 0.65918 | -122.0764 | -0.086975 | -0.11902 | 0.16022 | 0.93384 | 0.44403 | 0.56305 | 0.036621 | 0.7782 | 0.48523 | 0.1648 | -122.7081 | 122.7219 | 122.5983 | 0.49896 | -122.6807
1169.6406 | 122.5891 | -0.48523 | 121.9849 | 0.55284 | 0.050892 | 0.0090179 | 0.3757 | -0.032052 | 0.0015501 | -0.015718 | 0.29634 | -0.028273 | 0.051988 | 0.032783 | 0.026996 | 0.0768 | 0.032043 | 0.064087 | -0.3067 | 0.041199 | 0.21973 | -0.49439 | -0.65918 | 0.56763 | -0.009155 | 0.054932 | 122.1497 | 122.0444 | -0.58136 | -0.60883 | -0.009156 | -0.17395 | -121.7651 | 0.54932 | 0.52643 | 0.70038 | -121.9528 | -0.096131 | -0.1236 | 0.16479 | 1.0529 | 0.54016 | 0.66376 | 0.05951 | 0.70496 | 0.51727 | 0.17853 | -122.644 | 122.6349 | 122.5296 | 0.47607 | -122.5937
1170.6406 | 122.5342 | -0.53101 | 122.0261 | 0.32395 | 0.053029 | 0.0047449 | 0.39279 | -0.03312 | 0.00048206 | -0.021058 | -0.37505 | -0.030409 | 0.063737 | 0.047736 | 0.022724 | 0.067187 | 0.004578 | 0.009155 | -0.36163 | 0.009155 | 0.24719 | -0.53101 | -0.67749 | 0.46692 | -0.022888 | -0.07782 | 122.2137 | 122.113 | -0.6134 | -0.65002 | 0 | -0.14648 | -121.7789 | 0.54016 | 0.54016 | 0.68665 | -122.0215 | -0.082397 | -0.11902 | 0.18768 | 0.99792 | 0.45319 | 0.5722 | 0.086975 | 0.7782 | 0.53558 | 0.16937 | -122.7036 | 122.7448 | 122.644 | 0.50812 | -122.6761
1171.6406 | 122.5296 | -0.48523 | 122.0398 | -0.042256 | 0.050892 | 0.0015409 | 0.37998 | -0.036325 | 0.0036861 | -0.01999 | -0.16142 | -0.020796 | 0.055192 | 0.042396 | 0.032337 | 0.066119 | 0.036621 | 0.07782 | -0.31586 | 0.027466 | 0.21057 | -0.52185 | -0.65002 | 0.51727 | -0.10529 | -0.027466 | 122.2183 | 122.1085 | -0.6134 | -0.61798 | -0.036622 | -0.1648 | -121.8292 | 0.56305 | 0.5127 | 0.67749 | -122.0032 | -0.12817 | -0.13275 | 0.17853 | 1.0025 | 0.45776 | 0.59052 | 0.068664 | 0.6958 | 0.52185 | 0.16937 | -122.6898 | 122.7036 | 122.5937 | 0.37994 | -122.6578
1172.6406 | 122.5113 | -0.49439 | 122.0673 | 0.12559 | 0.035939 | -0.0048681 | 0.39173 | -0.030984 | 0.0090271 | -0.015718 | -0.51238 | -0.01866 | 0.065873 | 0.038123 | 0.025928 | 0.077868 | 0.027466 | 0.064087 | -0.32044 | 0.2655 | 0.25177 | -0.47607 | -0.60883 | 0.47607 | -0.054932 | -0.032043 | 122.2229 | 122.113 | -0.58594 | -0.63171 | 0.018311 | -0.11444 | -121.8155 | 0.55847 | 0.75989 | 0.87433 | -122.0398 | -0.091552 | -0.13733 | 0.15564 | 0.97046 | 0.46234 | 0.59967 | 0.045776 | 0.74616 | 0.52185 | 0.17395 | -122.6761 | 122.7173 | 122.6074 | 0.43945 | -122.699
1173.6406 | 122.5204 | -0.51727 | 122.0215 | 0.00352 | 0.053029 | 0.0079499 | 0.38104 | -0.02778 | -0.0069949 | -0.0039683 | 0.021682 | -0.01866 | 0.055192 | 0.043464 | 0.02486 | 0.074663 | 0.004578 | 0.027466 | -0.32959 | 0.004578 | 0.21057 | -0.53558 | -0.66376 | 0.46234 | -0.032043 | -0.073242 | 122.2 | 122.0993 | -0.61798 | -0.62714 | -0.01831 | -0.14648 | -121.8109 | 0.54474 | 0.52185 | 0.66834 | -122.0169 | -0.10071 | -0.10986 | 0.17853 | 0.97961 | 0.44403 | 0.55389 | 0.07782 | 0.72784 | 0.52185 | 0.18768 | -122.6852 | 122.7173 | 122.6166 | 0.48523 | -122.6486
1174.6406 | 122.6212 | -0.49896 | 122.0123 | 0.55284 | 0.025258 | 0.015426 | 0.37036 | -0.02778 | -0.025153 | -0.026399 | 0.54048 | -0.031478 | 0.044511 | 0.034919 | 0.02486 | 0.083208 | 0.059509 | 0.11902 | -0.25177 | 0.082397 | 0.21057 | -0.48065 | -0.61798 | 0.59509 | -0.15564 | -0.082397 | 122.1222 | 122.0215 | -0.6134 | -0.62256 | 0.01831 | -0.11902 | -121.8018 | 0.61798 | 0.58136 | 0.70038 | -121.9528 | -0.11444 | -0.1236 | 0.10986 | 1.0941 | 0.41657 | 0.54016 | 0.009155 | 0.70953 | 0.55847 | 0.24719 | -122.6303 | 122.6212 | 122.5204 | 0.34332 | -122.6349
1175.6406 | 122.5113 | -0.50354 | 122.0352 | 0.52232 | 0.045552 | 0.0015409 | 0.3757 | -0.030984 | -0.0037909 | -0.027467 | 1.2882 | -0.027205 | 0.057328 | 0.048804 | 0.023792 | 0.075732 | 0.12817 | -0.09613 | -0.39368 | 0.11444 | 0.2655 | -0.50354 | -0.64087 | 0.60883 | 0.20599 | -0.064087 | 122.2549 | 122.1313 | -0.60425 | -0.61798 | 0 | -0.13733 | -121.7697 | 0.40741 | 0.61798 | 0.75531 | -121.907 | -0.10071 | -0.11444 | 0.21973 | 1.1124 | 0.43945 | 0.55389 | 0.096131 | 0.76904 | 0.63171 | 0.10986 | -122.6761 | 122.7585 | 122.6349 | 0.70953 | -122.6532
1176.6406 | 122.493 | -0.52185 | 122.0444 | 0.26292 | 0.041279 | -0.0027321 | 0.37464 | -0.028848 | 0.011163 | -0.016786 | 0.58626 | -0.014388 | 0.066941 | 0.049872 | 0.025928 | 0.078936 | -0.018311 | -0.045776 | -0.3891 | -0.013733 | 0.2243 | -0.53558 | -0.6546 | 0.48065 | 1.03 | -0.10529 | 122.2229 | 122.1451 | -0.62256 | -0.62714 | -0.013732 | -0.13275 | -121.8201 | 0.47607 | 0.50812 | 0.64087 | -122.0627 | -0.10071 | -0.10529 | 0.17853 | 1.0025 | 0.41656 | 0.52185 | 0.10071 | 0.74615 | 0.50354 | 0.13275 | -122.699 | 122.7448 | 122.6669 | 1.5518 | -122.6715
1177.6406 | 122.5662 | -0.50812 | 122.0398 | -3.5976 | 0.027394 | 0.0047449 | 0.38104 | -0.040597 | -0.0037909 | -0.029603 | 0.2353 | -0.020796 | 0.05092 | 0.034919 | 0.026996 | 0.088549 | -0.045776 | -0.032043 | -0.37537 | -0.032043 | 0.24719 | -0.52185 | -0.66376 | 0.37537 | 0.31128 | -0.054932 | 122.2549 | 122.1497 | -0.60425 | -0.6134 | -0.013733 | -0.15564 | -121.7926 | 0.47607 | 0.47607 | 0.63171 | -122.0856 | -0.09613 | -0.10529 | 0.21515 | 0.88348 | 0.45319 | 0.55847 | 0.10986 | 0.75531 | 0.46234 | 0.13275 | -122.7036 | 122.7631 | 122.6578 | 0.8194 | -122.6532
1178.6406 | 122.6486 | -0.45776 | 122.0123 | 0.65965 | 0.037007 | 0.0058129 | 0.37998 | -0.025644 | -0.012336 | -0.032808 | 0.58626 | -0.033614 | 0.057328 | 0.055213 | 0.017383 | 0.089617 | 0.064087 | 0.10071 | -0.25177 | 0.07782 | 0.19226 | -0.4715 | -0.61798 | 0.56305 | 1.3321 | 0.064087 | 122.2 | 122.1085 | -0.58594 | -0.56305 | -0.013733 | -0.16022 | -121.8201 | 0.55847 | 0.53558 | 0.6958 | -121.9482 | -0.12817 | -0.10529 | 0.18768 | 1.0208 | 0.52185 | 0.62714 | 0.09613 | 0.65002 | 0.52185 | 0.20599 | -122.6303 | 122.6578 | 122.5662 | 1.7899 | -122.5754
1179.6406 | 122.5571 | -0.50812 | 122.0856 | -0.25588 | 0.0081682 | -0.0016631 | 0.38211 | -0.014962 | -0.025153 | -0.028535 | -0.23772 | -0.034682 | 0.059465 | 0.042396 | 0.010974 | 0.080004 | 0.022888 | 0.054932 | -0.28381 | 0.050354 | 0.2243 | -0.50812 | -0.65002 | 0.4715 | 0.72327 | -0.013733 | 122.2641 | 122.1771 | -0.58594 | -0.61798 | 0 | -0.14191 | -121.8613 | 0.56305 | 0.55847 | 0.70038 | -122.0627 | -0.077819 | -0.10986 | 0.17853 | 0.97961 | 0.49438 | 0.60425 | 0.091553 | 0.73242 | 0.53101 | 0.2243 | -122.7356 | 122.7722 | 122.6852 | 1.2314 | -122.7036
1180.6406 | 122.6257 | -0.46692 | 122.0398 | -0.94253 | 0.017781 | 0.014358 | 0.37677 | -0.011758 | -0.028357 | -0.032808 | 0.52522 | -0.034682 | 0.051988 | 0.026374 | 0.028064 | 0.078936 | 0.027466 | 0.11444 | -0.23346 | 0.064087 | 0.19226 | -0.49896 | -0.62256 | 0.54474 | 0.57678 | 0.054932 | 122.2229 | 122.1085 | -0.58136 | -0.58594 | -0.032043 | -0.15564 | -121.8475 | 0.58136 | 0.53101 | 0.68665 | -122.0123 | -0.11444 | -0.11902 | 0.1831 | 1.0117 | 0.52185 | 0.64087 | 0.068664 | 0.65918 | 0.49438 | 0.23346 | -122.6624 | 122.6898 | 122.5754 | 1.0437 | -122.6257
1181.6406 | 122.6257 | -0.4715 | 122.0444 | 0.46128 | 0.00069119 | 0.0026089 | 0.37784 | -0.032052 | -0.024085 | -0.034944 | 0.46419 | -0.040022 | 0.046647 | 0.040259 | 0.0088381 | 0.077868 | 0.045776 | 0.10071 | -0.24261 | 0.050354 | 0.20599 | -0.47607 | -0.62256 | 0.88348 | 0.36621 | 0.045776 | 122.2321 | 122.1313 | -0.55389 | -0.56305 | -0.004577 | -0.15106 | -121.8384 | 0.5722 | 0.52185 | 0.67291 | -121.9986 | -0.082397 | -0.091552 | 0.18768 | 1.355 | 0.51727 | 0.60883 | 0.086975 | 0.67749 | 0.51727 | 0.22888 | -122.6669 | 122.7036 | 122.6028 | 0.83771 | -122.6074
1182.6406 | 122.6349 | -0.45776 | 122.0718 | 0.15611 | 0.011372 | 0.016495 | 0.38318 | -0.037393 | -0.036902 | -0.036012 | -0.039353 | -0.047499 | 0.044511 | 0.035987 | 0.021655 | 0.072527 | 0.050354 | 0.10529 | -0.21973 | 0.068665 | 0.22888 | -0.48065 | -0.59967 | 0.60425 | 0.40741 | 0.086975 | 122.2412 | 122.1451 | -0.56305 | -0.58136 | -0.022888 | -0.14191 | -121.843 | 0.56305 | 0.52643 | 0.66834 | -122.0215 | -0.10529 | -0.1236 | 0.16937 | 1.062 | 0.54474 | 0.66834 | 0.073243 | 0.68665 | 0.50812 | 0.23804 | -122.6715 | 122.699 | 122.6028 | 0.86517 | -122.6532
1183.6406 | 122.5937 | -0.46692 | 122.0673 | 0.52232 | 0.030598 | 0.0036769 | 0.37677 | -0.035257 | -0.017676 | -0.03708 | 0.43367 | -0.024001 | 0.042375 | 0.050941 | 0.016315 | 0.084276 | 0.064087 | 0.091553 | -0.24719 | 0.045776 | 0.21973 | -0.4715 | -0.6134 | 0.62256 | 0.9201 | 0.013733 | 122.2458 | 122.113 | -0.56763 | -0.59509 | -0.004578 | -0.14648 | -121.8475 | 0.55847 | 0.5127 | 0.65918 | -122.0032 | -0.10071 | -0.12817 | 0.17853 | 1.0895 | 0.48065 | 0.60883 | 0.045776 | 0.68665 | 0.53101 | 0.21973 | -122.6807 | 122.7127 | 122.58 | 1.387 | -122.6624
1184.6406 | 122.5525 | -0.52643 | 122.1085 | -0.24062 | 0.018849 | 0.0068819 | 0.396 | -0.032052 | -0.0048589 | -0.029603 | -0.51238 | -0.020796 | 0.046647 | 0.048804 | 0.017383 | 0.067187 | 0 | -0.009155 | -0.34332 | -0.018311 | 0.25177 | -0.5127 | -0.66376 | 0.48065 | 1.3 | -0.068665 | 122.2961 | 122.1634 | -0.60883 | -0.62714 | 0.013733 | -0.13733 | -121.8567 | 0.51727 | 0.50812 | 0.64545 | -122.1085 | -0.082398 | -0.10071 | 0.18768 | 1.0071 | 0.45776 | 0.55847 | 0.054932 | 0.7782 | 0.52643 | 0.18311 | -122.7722 | 122.8226 | 122.6898 | 1.8265 | -122.7356
1185.6406 | 122.7173 | -0.46234 | 122.0718 | 0.20188 | -0.0014448 | 0.0015409 | 0.36823 | -0.02778 | -0.026221 | -0.030671 | 0.11323 | -0.020796 | 0.038102 | 0.025306 | 0.0099061 | 0.0768 | 0.064087 | 0.14648 | -0.21057 | 0.07782 | 0.22888 | -0.45319 | -0.60425 | 0.58136 | 2.211 | 0.10071 | 122.2321 | 122.1313 | -0.55847 | -0.58594 | 0.009155 | -0.14191 | -121.843 | 0.60882 | 0.54016 | 0.68207 | -122.0078 | -0.096131 | -0.1236 | 0.16022 | 1.0437 | 0.56305 | 0.68665 | 0.05951 | 0.69122 | 0.52643 | 0.25177 | -122.6761 | 122.6944 | 122.5937 | 2.6733 | -122.6578
1186.6406 | 122.6715 | -0.46234 | 122.0627 | 0.00352 | 0.0017592 | 0.0036769 | 0.37036 | -0.02778 | -0.024085 | -0.032808 | -0.22246 | -0.040022 | 0.043443 | 0.039191 | 0.020587 | 0.081072 | 0.091553 | 0.17395 | -0.17853 | 0.082397 | 0.19684 | -0.48065 | -0.6134 | 0.5722 | 1.5976 | 0.07782 | 122.2137 | 122.1268 | -0.5722 | -0.58136 | -0.018311 | -0.15106 | -121.8658 | 0.63629 | 0.54474 | 0.6958 | -121.9711 | -0.10986 | -0.11902 | 0.15106 | 1.0345 | 0.54016 | 0.65918 | 0.064087 | 0.65918 | 0.55389 | 0.28381 | -122.6761 | 122.6761 | 122.5891 | 2.0599 | -122.644
1187.6406 | 122.5616 | -0.52643 | 122.1039 | -0.14907 | 0.0017592 | 0.0026089 | 0.38639 | -0.041665 | -0.0037909 | -0.027467 | -0.43608 | -0.027205 | 0.053056 | 0.048804 | 0.029132 | 0.071459 | -0.022888 | 0.032043 | -0.31586 | -0.013733 | 0.23346 | -0.51727 | -0.67749 | 0.48065 | 3.7308 | -0.064087 | 122.3053 | 122.1542 | -0.63171 | -0.62714 | 0.009155 | -0.15106 | -121.8704 | 0.55847 | 0.5127 | 0.66376 | -122.1268 | -0.10529 | -0.10071 | 0.20142 | 1.0071 | 0.46234 | 0.56305 | 0.050354 | 0.75989 | 0.50354 | 0.21057 | -122.7814 | 122.8317 | 122.6807 | 4.2572 | -122.731
1188.6406 | 122.6715 | -0.45776 | 122.0947 | -5.8406 | -0.00037681 | -0.0091401 | 0.36395 | -0.038461 | -0.025153 | -0.021058 | -0.35979 | -0.042159 | 0.037034 | 0.046668 | 0.019519 | 0.070391 | -0.027466 | 0.18768 | -0.18768 | 0.064087 | 0.19226 | -0.49896 | -0.63629 | 0.5127 | 8.6929 | 0.059509 | 122.2549 | 122.1268 | -0.58136 | -0.59967 | -0.041198 | -0.17853 | -121.9025 | 0.64545 | 0.52185 | 0.70038 | -122.1222 | -0.1236 | -0.14191 | 0.16022 | 0.97046 | 0.51727 | 0.65918 | 0.032043 | 0.65002 | 0.4303 | 0.27008 | -122.731 | 122.7127 | 122.5845 | 9.1507 | -122.6944
1189.6406 | 122.6807 | -0.46692 | 122.0673 | 0.59861 | 0.026326 | 0.018631 | 0.38318 | -0.041665 | 0.0015501 | -0.024263 | 0.44893 | -0.028273 | 0.063737 | 0.039191 | 0.0302 | 0.071459 | 0.041199 | 0.073242 | -0.25635 | 0.050354 | 0.20599 | -0.49439 | -0.64545 | 0.60425 | 10.6567 | 0.036621 | 122.2458 | 122.1039 | -0.5722 | -0.58594 | -0.027466 | -0.17853 | -121.8613 | 0.54016 | 0.51727 | 0.6958 | -122.0261 | -0.10529 | -0.11902 | 0.17853 | 1.0712 | 0.50354 | 0.62256 | 0.036621 | 0.67291 | 0.50812 | 0.21057 | -122.7127 | 122.7127 | 122.5708 | 11.1237 | -122.6532
1190.6406 | 122.58 | -0.49896 | 122.1268 | -0.2101 | 0.013508 | 0.017563 | 0.36182 | -0.030984 | -0.021949 | -0.031739 | -0.37505 | -0.033614 | 0.060533 | 0.052009 | 0.012042 | 0.073595 | 0.032043 | 0.07782 | -0.2655 | 0.050354 | 0.2243 | -0.51727 | -0.64087 | 0.44861 | 4.9484 | -0.045776 | 122.2916 | 122.1725 | -0.59967 | -0.6134 | -0.018311 | -0.14191 | -121.9025 | 0.57678 | 0.54932 | 0.69122 | -122.0947 | -0.10071 | -0.11444 | 0.1648 | 0.94757 | 0.45319 | 0.56763 | 0.045776 | 0.72327 | 0.53101 | 0.23346 | -122.7676 | 122.7905 | 122.6715 | 5.4474 | -122.7402
1191.6406 | 122.6212 | -0.53558 | 122.0947 | -0.17959 | 0.013508 | 0.015426 | 0.38639 | -0.035257 | 0.0058221 | -0.030671 | -0.48186 | -0.027205 | 0.040239 | 0.027442 | 0.032337 | 0.057574 | -0.027466 | 0.013733 | -0.32044 | 0.004578 | 0.23804 | -0.52643 | -0.65002 | 0.32501 | 6.9672 | -0.045776 | 122.2778 | 122.1588 | -0.6134 | -0.62256 | 0.009155 | -0.11444 | -121.8567 | 0.54932 | 0.54016 | 0.6546 | -122.1222 | -0.07782 | -0.086976 | 0.1831 | 0.86059 | 0.48981 | 0.57678 | 0.064086 | 0.77362 | 0.50812 | 0.21515 | -122.7448 | 122.8134 | 122.6944 | 7.5027 | -122.7173
1192.6406 | 122.5571 | -0.51727 | 122.0993 | 0.17137 | 0.067982 | 0.00047294 | 0.38211 | -0.025644 | 0.019708 | -0.018922 | -0.024094 | -0.016524 | 0.059465 | 0.035987 | 0.033405 | 0.072527 | 0.013733 | 0.018311 | -0.32959 | -0.009155 | 0.20599 | -0.54474 | -0.65918 | 0.27466 | -0.36163 | -0.09613 | 122.2824 | 122.1634 | -0.60425 | -0.63171 | -0.027466 | -0.14191 | -121.8933 | 0.53558 | 0.50812 | 0.65002 | -122.0856 | -0.086975 | -0.11444 | 0.18311 | 0.79193 | 0.42114 | 0.53558 | 0.064087 | 0.72327 | 0.53101 | 0.18768 | -122.7585 | 122.7997 | 122.6807 | 0.15564 | -122.731
1193.6406 | 122.6212 | -0.50812 | 122.1222 | -0.17959 | 0.032734 | 0.0026089 | 0.3693 | -0.021371 | 0.0026181 | -0.024263 | -0.37505 | -0.025069 | 0.06801 | 0.041327 | 0.015247 | 0.075732 | -0.032043 | 0.004578 | -0.31586 | 0 | 0.2243 | -0.52185 | -0.67291 | 0.67291 | 7.1732 | -0.041199 | 122.3053 | 122.1634 | -0.61798 | -0.63171 | -0.013733 | -0.1648 | -121.8979 | 0.5127 | 0.50812 | 0.67291 | -122.1542 | -0.10986 | -0.1236 | 0.18311 | 1.181 | 0.46692 | 0.59052 | 0.041199 | 0.73242 | 0.47607 | 0.19226 | -122.7951 | 122.8134 | 122.6715 | 7.6813 | -122.7539
1194.7031 | 122.7036 | -0.4715 | 122.0993 | -0.011739 | 0.02953 | 0.015426 | 0.37357 | -0.04487 | -0.035834 | -0.027467 | 0.11323 | -0.038954 | 0.054124 | 0.043464 | 0.017383 | 0.085345 | -0.032043 | 0.082397 | -0.23804 | 0.036621 | 0.20142 | -0.48981 | -0.64545 | 0.52643 | 5.3833 | 0.054932 | 122.2733 | 122.1725 | -0.56763 | -0.58136 | -0.01831 | -0.17395 | -121.8979 | 0.55389 | 0.50812 | 0.68207 | -122.1313 | -0.09613 | -0.10986 | 0.17395 | 0.99792 | 0.52643 | 0.63629 | 0.073242 | 0.67291 | 0.43945 | 0.23346 | -122.7448 | 122.7448 | 122.644 | 5.8548 | -122.6807
1195.6406 | 122.612 | -0.5127 | 122.1176 | 0.079814 | 0.033803 | 0.0058129 | 0.38639 | -0.036325 | 0.0079581 | -0.018922 | -0.31401 | -0.029341 | 0.065873 | 0.041327 | 0.031268 | 0.062914 | 0.041199 | 0.041199 | -0.29755 | 0.032043 | 0.22888 | -0.52643 | -0.65918 | 0.39825 | 2.0782 | -0.027466 | 122.2961 | 122.1771 | -0.59509 | -0.60883 | -0.013733 | -0.14648 | -121.8887 | 0.55389 | 0.54474 | 0.69122 | -122.0764 | -0.082398 | -0.096131 | 0.17853 | 0.91095 | 0.48523 | 0.58136 | 0.059509 | 0.74158 | 0.55389 | 0.21515 | -122.7768 | 122.8088 | 122.6898 | 2.5909 | -122.7264
1196.6406 | 122.644 | -0.43945 | 122.168 | 0.079814 | 0.051961 | 0.0047449 | 0.3757 | -0.025644 | -0.00058594 | -0.028535 | -0.10039 | -0.030409 | 0.046647 | 0.0456 | 0.0302 | 0.071459 | 0.032043 | 0.054932 | -0.28839 | 0.022888 | 0.24719 | -0.49896 | -0.66834 | 0.58136 | 1.5747 | 0.013733 | 122.406 | 122.2321 | -0.54016 | -0.55847 | -0.059509 | -0.22888 | -121.9208 | 0.49438 | 0.46234 | 0.69122 | -122.1359 | -0.10071 | -0.11902 | 0.23804 | 1.0208 | 0.45319 | 0.5722 | 0.064087 | 0.68664 | 0.4715 | 0.15106 | -122.8363 | 122.8455 | 122.6715 | 2.0142 | -122.7264
1197.6406 | 122.6395 | -0.46692 | 122.1085 | 0.40025 | 0.0081682 | 0.0015409 | 0.36395 | -0.032052 | -0.027289 | -0.026399 | 0.43367 | -0.027205 | 0.047715 | 0.035987 | 0.0067021 | 0.09389 | 0.036621 | 0.11902 | -0.21515 | 0.054932 | 0.18768 | -0.46234 | -0.6134 | 0.46234 | 6.0471 | 0.054932 | 122.2733 | 122.1725 | -0.56305 | -0.59052 | 0.004578 | -0.14648 | -121.9208 | 0.58594 | 0.52185 | 0.66834 | -122.0718 | -0.09613 | -0.1236 | 0.16479 | 0.92926 | 0.52185 | 0.64545 | 0.064087 | 0.6546 | 0.50354 | 0.25177 | -122.7219 | 122.7402 | 122.6395 | 6.514 | -122.699
1198.6406 | 122.5845 | -0.50812 | 122.1085 | 0.2324 | 0.037007 | -0.0091401 | 0.38211 | -0.037393 | 0.013299 | -0.024263 | -0.024094 | -0.017592 | 0.076554 | 0.029578 | 0.043018 | 0.072527 | 0.022888 | 0.009155 | -0.32501 | 0.013733 | 0.22888 | -0.52185 | -0.65918 | 0.34332 | 5.2872 | -0.086975 | 122.3282 | 122.2137 | -0.60883 | -0.61798 | -0.013733 | -0.15106 | -121.8796 | 0.51727 | 0.52185 | 0.67291 | -122.0856 | -0.10071 | -0.10986 | 0.21973 | 0.85144 | 0.42114 | 0.53101 | 0.10529 | 0.737 | 0.53101 | 0.18311 | -122.7676 | 122.8363 | 122.7219 | 5.7953 | -122.7264
1199.6406 | 122.6074 | -0.51727 | 122.1359 | 0.17137 | 0.048756 | -0.013413 | 0.38852 | -0.029916 | 0.0026181 | -0.01465 | 0.25056 | -0.028273 | 0.061601 | 0.055213 | 0.023792 | 0.081072 | -0.036621 | -0.068665 | -0.38452 | -0.027466 | 0.23346 | -0.49896 | -0.66376 | 0.35706 | 7.663 | -0.091553 | 122.3236 | 122.2275 | -0.59967 | -0.63171 | 0.018311 | -0.14648 | -121.9025 | 0.44861 | 0.48981 | 0.63629 | -122.1725 | -0.082397 | -0.11444 | 0.18768 | 0.87433 | 0.42572 | 0.54016 | 0.091553 | 0.75073 | 0.48065 | 0.13275 | -122.7997 | 122.8409 | 122.7448 | 8.1802 | -122.7676
1200.6406 | 122.6212 | -0.5127 | 122.1313 | 0.58335 | 0.038075 | 0.011154 | 0.37784 | -0.034188 | -0.0048589 | -0.026399 | 5.0876 | -0.015456 | 0.061601 | 0.018897 | 0.026996 | 0.084276 | -0.045776 | -0.027466 | -0.3479 | -0.004578 | 0.23346 | -0.51727 | -0.67749 | 0.25177 | 4.3396 | -0.082397 | 122.3236 | 122.2 | -0.60425 | -0.60883 | -0.004578 | -0.1648 | -121.8979 | 0.48523 | 0.50812 | 0.67291 | -122.1771 | -0.091553 | -0.096131 | 0.19226 | 0.76446 | 0.4303 | 0.52643 | 0.068664 | 0.74615 | 0.46692 | 0.1648 | -122.8088 | 122.8363 | 122.7127 | 4.8523 | -122.7402
1201.6406 | 122.5983 | -0.52185 | 122.1222 | -0.89675 | 0.013508 | -0.0027321 | 0.37036 | -0.028848 | -0.0091309 | -0.030671 | 0.32686 | -0.031478 | 0.057328 | 0.038123 | 0.016315 | 0.083208 | -0.054932 | 0.013733 | -0.31586 | -0.018311 | 0.25635 | -0.52185 | -0.6546 | 0.3067 | 5.6122 | -0.059509 | 122.3099 | 122.2321 | -0.59509 | -0.60883 | 0 | -0.13275 | -121.8658 | 0.53558 | 0.50354 | 0.63629 | -122.1771 | -0.073242 | -0.086975 | 0.18768 | 0.82855 | 0.46234 | 0.54932 | 0.10986 | 0.7782 | 0.46692 | 0.20599 | -122.7768 | 122.8317 | 122.7539 | 6.134 | -122.731
1202.6562 | 122.6303 | -0.54932 | 122.0947 | -0.17959 | 0.050892 | -0.0016631 | 0.39386 | -0.037393 | -0.01554 | -0.016786 | -0.28349 | -0.01332 | 0.069078 | 0.032783 | 0.018451 | 0.074663 | -0.009155 | -0.018311 | -0.32044 | 0 | 0.25177 | -0.54016 | -0.70496 | 0.21057 | 5.9052 | -0.09613 | 122.2961 | 122.1954 | -0.66376 | -0.6546 | 0.009155 | -0.15564 | -121.843 | 0.53101 | 0.54932 | 0.70496 | -122.1039 | -0.11444 | -0.10529 | 0.20142 | 0.75989 | 0.45319 | 0.55847 | 0.10071 | 0.80109 | 0.54016 | 0.22888 | -122.7997 | 122.8455 | 122.7448 | 6.4545 | -122.7493
1203.6406 | 122.6715 | -0.48981 | 122.1085 | 0.59861 | 0.034871 | 0.0079499 | 0.38745 | -0.034188 | -0.01554 | -0.017854 | 0.46419 | -0.028273 | 0.05626 | 0.041327 | 0.021655 | 0.089617 | 0 | 0.027466 | -0.29297 | 0.009155 | 0.20599 | -0.50812 | -0.63629 | 0.32959 | 6.4133 | 0.004578 | 122.3053 | 122.2092 | -0.59052 | -0.60883 | -0.018311 | -0.14648 | -121.9025 | 0.51727 | 0.49896 | 0.64545 | -122.1085 | -0.10071 | -0.11902 | 0.19684 | 0.8194 | 0.49439 | 0.6134 | 0.10071 | 0.6958 | 0.48981 | 0.19684 | -122.7448 | 122.7951 | 122.699 | 6.9031 | -122.7173
1204.6406 | 122.7493 | -0.47607 | 122.1359 | 0.50706 | 0.040211 | 0.0068819 | 0.36609 | -0.035257 | -0.0069949 | -0.01999 | 0.41841 | -0.026137 | 0.069078 | 0.038123 | 0.02486 | 0.078936 | 0.041199 | 0.082397 | -0.25177 | 0.068665 | 0.19684 | -0.48981 | -0.63629 | 0.3067 | 6.8848 | 0.059509 | 122.2824 | 122.1909 | -0.5722 | -0.59509 | -0.013733 | -0.16022 | -121.9391 | 0.55847 | 0.54474 | 0.70496 | -122.0947 | -0.096131 | -0.11902 | 0.14648 | 0.78278 | 0.53558 | 0.6546 | 0.054932 | 0.67291 | 0.51727 | 0.2243 | -122.7722 | 122.7585 | 122.6669 | 7.3608 | -122.731
1205.6406 | 122.7402 | -0.45776 | 122.1176 | 1.0564 | 0.027394 | 0.0015409 | 0.37143 | -0.034188 | -0.01554 | -0.024263 | 0.55574 | -0.03575 | 0.060533 | 0.048804 | 0.025928 | 0.087481 | 0.054932 | 0.11902 | -0.21515 | 0.073242 | 0.20142 | -0.4715 | -0.60883 | 0.31586 | 6.8665 | 0.059509 | 122.2824 | 122.1771 | -0.56763 | -0.59052 | -0.013733 | -0.15106 | -121.9162 | 0.57678 | 0.53101 | 0.68207 | -122.0627 | -0.10986 | -0.13275 | 0.16479 | 0.77362 | 0.51727 | 0.65002 | 0.059509 | 0.65918 | 0.5127 | 0.24261 | -122.7264 | 122.7402 | 122.6349 | 7.3242 | -122.7081
1206.6406 | 122.7356 | -0.46692 | 122.1405 | 0.018779 | 0.017781 | -0.0027321 | 0.38318 | -0.047006 | -0.042243 | -0.041353 | 0.14375 | -0.033614 | 0.049852 | 0.043464 | 0.014179 | 0.088549 | 0.059509 | 0.09613 | -0.21515 | 0.068665 | 0.21515 | -0.46692 | -0.62256 | 0.36163 | 6.0654 | 0.10529 | 122.2916 | 122.2275 | -0.54932 | -0.58136 | 0 | -0.15564 | -121.9254 | 0.56305 | 0.53558 | 0.69122 | -122.081 | -0.082397 | -0.11444 | 0.15106 | 0.82855 | 0.5722 | 0.68665 | 0.086975 | 0.68207 | 0.52643 | 0.25177 | -122.7631 | 122.7585 | 122.6944 | 6.5323 | -122.7219
1207.6562 | 122.6395 | -0.52185 | 122.113 | 1.331 | 0.045552 | 0.016495 | 0.36823 | -0.04487 | 0.0015501 | -0.022126 | 0.43367 | -0.028273 | 0.062669 | 0.040259 | 0.026996 | 0.0768 | 0.009155 | -0.022888 | -0.33417 | -0.009155 | 0.23804 | -0.53101 | -0.66834 | 0.50812 | 5.5939 | -0.041199 | 122.3282 | 122.2321 | -0.61798 | -0.60425 | -0.009155 | -0.14648 | -121.875 | 0.49896 | 0.5127 | 0.65918 | -122.1039 | -0.09613 | -0.082397 | 0.21515 | 1.03 | 0.48065 | 0.56305 | 0.11902 | 0.75989 | 0.53101 | 0.18768 | -122.7814 | 122.85 | 122.7539 | 6.1157 | -122.7173
1208.6406 | 122.7493 | -0.46692 | 122.1313 | 0.079814 | 0.022053 | 0.0079499 | 0.37464 | -0.039529 | -0.035834 | -0.029603 | 0.036941 | -0.037886 | 0.041307 | 0.059485 | 0.0045661 | 0.074663 | 0.054932 | 0.10986 | -0.19684 | 0.045776 | 0.2243 | -0.46692 | -0.60883 | 0.48065 | 6.3263 | 0.082397 | 122.3145 | 122.2412 | -0.56305 | -0.58136 | 0 | -0.14191 | -121.907 | 0.57678 | 0.5127 | 0.6546 | -122.0764 | -0.09613 | -0.11444 | 0.1831 | 0.94757 | 0.54932 | 0.66376 | 0.10986 | 0.69122 | 0.52185 | 0.27008 | -122.7402 | 122.7814 | 122.7081 | 6.7932 | -122.7127
1209.6406 | 122.7127 | -0.46692 | 122.1359 | 0.12559 | 0.0060322 | -0.0016631 | 0.37357 | -0.043802 | -0.023017 | -0.034944 | 0.082718 | -0.041091 | 0.034898 | 0.042396 | 0.012042 | 0.083208 | 0.027466 | 0.086975 | -0.2243 | 0.054932 | 0.23346 | -0.48523 | -0.63171 | 0.56305 | 3.0212 | 0.054932 | 122.319 | 122.2275 | -0.56305 | -0.58136 | -0.01831 | -0.1648 | -121.9025 | 0.55389 | 0.52185 | 0.68665 | -122.1085 | -0.09613 | -0.11444 | 0.18311 | 1.03 | 0.52185 | 0.63629 | 0.091553 | 0.70038 | 0.49438 | 0.24261 | -122.7676 | 122.7859 | 122.6944 | 3.4882 | -122.7173
1210.6406 | 122.6349 | -0.4715 | 122.2046 | -0.30166 | 0.034871 | 0.016495 | 0.36716 | -0.041665 | 0.0079581 | -0.033876 | -0.35979 | -0.030409 | 0.054124 | 0.038123 | 0.0088381 | 0.074663 | -0.009155 | -0.009155 | -0.32959 | 0 | 0.23346 | -0.52643 | -0.65918 | 0.46692 | 1.2268 | -0.004578 | 122.406 | 122.2641 | -0.57678 | -0.56305 | -0.054931 | -0.18768 | -121.9711 | 0.46234 | 0.4715 | 0.65918 | -122.2137 | -0.10529 | -0.091552 | 0.20142 | 0.93842 | 0.46692 | 0.55847 | 0.059509 | 0.70496 | 0.46234 | 0.14191 | -122.8638 | 122.8775 | 122.7356 | 1.6983 | -122.7676
1211.6406 | 122.7264 | -0.49439 | 122.168 | -0.13381 | -0.0035808 | 0.0068819 | 0.37464 | -0.03312 | -0.017676 | -0.036012 | 0.66255 | -0.038954 | 0.047715 | 0.040259 | 0.029132 | 0.070391 | 0.004578 | 0.37537 | -0.082397 | -0.004578 | 0.19684 | -0.52185 | -0.66376 | 0.41657 | 1.268 | 0.036621 | 122.2916 | 122.1771 | -0.58594 | -0.59967 | -0.027466 | -0.16937 | -121.9711 | 0.86975 | 0.48981 | 0.65918 | -122.1634 | -0.091552 | -0.10529 | 0.1236 | 0.91095 | 0.53101 | 0.63629 | 0.009155 | 0.69122 | 0.49896 | 0.41199 | -122.8317 | 122.7859 | 122.6715 | 1.7624 | -122.7676
1212.6562 | 122.6257 | -0.62714 | 122.0764 | -0.31691 | 0.022053 | 0.020767 | 0.35648 | -0.024575 | -0.0091309 | -0.036012 | -0.39031 | -0.031478 | 0.053056 | 0.032783 | 0.018451 | 0.070391 | -0.027466 | 0.018311 | -0.3067 | -0.009155 | 0.23804 | -0.62256 | -0.75073 | 0.11902 | 1.6891 | -0.1831 | 122.2504 | 122.1405 | -0.70953 | -0.71411 | 0.004577 | -0.1236 | -121.8384 | 0.64545 | 0.61798 | 0.74158 | -122.1039 | -0.082398 | -0.086975 | 0.17395 | 0.74616 | 0.44403 | 0.53101 | 0.064087 | 0.86517 | 0.59967 | 0.32043 | -122.8271 | 122.8775 | 122.7676 | 2.3163 | -122.7905
1213.6406 | 122.7676 | -0.51727 | 122.1222 | -0.16433 | -0.0025128 | 0.010086 | 0.35861 | -0.024575 | -0.05506 | -0.057374 | 0.61677 | -0.048567 | 0.027421 | 0.044532 | 0.025928 | 0.078936 | 0.22888 | -0.13733 | -0.27924 | 0.11902 | 0.1831 | -0.54474 | -0.6958 | 0.25635 | 3.2318 | 0 | 122.3053 | 122.1634 | -0.58594 | -0.62256 | -0.027466 | -0.17853 | -121.9391 | 0.37994 | 0.63629 | 0.81482 | -121.8933 | -0.068664 | -0.10529 | 0.18311 | 0.77362 | 0.51727 | 0.62256 | 0.041199 | 0.70038 | 0.74616 | 0.23804 | -122.818 | 122.8226 | 122.6807 | 3.7491 | -122.7448
1214.6406 | 122.6578 | -0.68665 | 122.0215 | -0.2101 | 0.031666 | 0.0047449 | 0.39066 | -0.039529 | 0.00048206 | -0.023195 | -0.40556 | -0.034682 | 0.054124 | 0.02851 | 0.025928 | 0.06505 | -0.013733 | 0.009155 | -0.32501 | 0 | 0.22888 | -0.67749 | -0.8194 | 0.064087 | 2.2751 | -0.25635 | 122.1954 | 122.0718 | -0.77362 | -0.78278 | 0.009156 | -0.13275 | -121.7926 | 0.6958 | 0.68665 | 0.8194 | -122.0352 | -0.086975 | -0.09613 | 0.17395 | 0.75073 | 0.4303 | 0.52643 | 0.050354 | 0.91553 | 0.67291 | 0.36163 | -122.8409 | 122.8821 | 122.7585 | 2.9617 | -122.8043
1215.6406 | 122.6257 | -0.53101 | 122.1497 | -0.25588 | 0.015645 | 0.016495 | 0.35968 | -0.048074 | -0.017676 | -0.042421 | -0.32927 | -0.036818 | 0.064805 | 0.02851 | 0.017383 | 0.081072 | 0.032043 | 0.09613 | -0.21973 | 0.068665 | 0.21515 | -0.53101 | -0.66376 | 0.19684 | 3.1998 | -0.032043 | 122.3373 | 122.2092 | -0.6134 | -0.61798 | 0 | -0.13275 | -121.9345 | 0.62714 | 0.59967 | 0.73242 | -122.1176 | -0.082397 | -0.086975 | 0.18768 | 0.72784 | 0.49896 | 0.58594 | 0.059509 | 0.74616 | 0.56305 | 0.31128 | -122.8134 | 122.8683 | 122.7402 | 3.7308 | -122.7676
1216.6406 | 122.699 | -0.49896 | 122.1451 | -0.13381 | 0.030598 | -0.011276 | 0.39173 | -0.013894 | 0.0068901 | -0.017854 | -0.25298 | -0.025069 | 0.053056 | 0.032783 | 0.029132 | 0.074663 | 0.041199 | 0.059509 | -0.27008 | 0.036621 | 0.2243 | -0.52643 | -0.67291 | 0.23346 | 1.1948 | -0.045776 | 122.3328 | 122.2183 | -0.60883 | -0.63629 | -0.027466 | -0.17395 | -121.9208 | 0.55847 | 0.53558 | 0.70953 | -122.1039 | -0.10986 | -0.13733 | 0.18768 | 0.73242 | 0.45319 | 0.59052 | 0.073242 | 0.72327 | 0.54016 | 0.22888 | -122.818 | 122.8317 | 122.7173 | 1.6937 | -122.7814
1217.6562 | 122.6852 | -0.67749 | 122.0215 | 0.27818 | 0.028462 | 0.0047449 | 0.37464 | -0.029916 | -0.0048589 | -0.031739 | -0.35979 | -0.032546 | 0.044511 | 0.043464 | 0.023792 | 0.074663 | -0.027466 | 0.018311 | -0.31586 | 0 | 0.25177 | -0.68207 | -0.83771 | 0.041199 | 1.7853 | -0.26093 | 122.2321 | 122.113 | -0.75531 | -0.79193 | -0.004578 | -0.16022 | -121.7697 | 0.6958 | 0.67749 | 0.83771 | -122.049 | -0.07782 | -0.11444 | 0.21057 | 0.71869 | 0.41657 | 0.53101 | 0.091553 | 0.92926 | 0.65002 | 0.36163 | -122.8592 | 122.9095 | 122.7905 | 2.4628 | -122.8134
1218.6406 | 122.6166 | -0.68207 | 122.0261 | 0.21714 | 0.044484 | -0.0059361 | 0.37036 | -0.02778 | 0.013299 | -0.022126 | 0.021682 | -0.029341 | 0.062669 | 0.037055 | 0.032337 | 0.070391 | -0.013733 | 0.018311 | -0.32501 | -0.009155 | 0.21057 | -0.67291 | -0.82855 | 0.054932 | 1.8311 | -0.27924 | 122.2 | 122.0581 | -0.79193 | -0.78735 | 0.009155 | -0.14648 | -121.8155 | 0.70038 | 0.67291 | 0.8194 | -122.0398 | -0.10986 | -0.10529 | 0.17395 | 0.737 | 0.40283 | 0.50812 | 0.032043 | 0.89264 | 0.66834 | 0.35706 | -122.8546 | 122.8821 | 122.7402 | 2.5131 | -122.8134
1219.6406 | 122.6532 | -0.66834 | 122.0444 | 0.47654 | 0.044484 | 0.026108 | 0.38852 | -0.034188 | 0.0047541 | -0.022126 | 0.3116 | -0.024001 | 0.060533 | 0.038123 | 0.029132 | 0.08214 | -0.027466 | -0.032043 | -0.35706 | -0.018311 | 0.23346 | -0.65918 | -0.81482 | 0.064087 | 1.3962 | -0.28839 | 122.2092 | 122.1222 | -0.74616 | -0.76446 | 0.009155 | -0.14648 | -121.8109 | 0.63629 | 0.65002 | 0.79651 | -122.0718 | -0.07782 | -0.09613 | 0.16479 | 0.73242 | 0.37994 | 0.47607 | 0.077819 | 0.90179 | 0.64087 | 0.31128 | -122.8592 | 122.8775 | 122.7905 | 2.0645 | -122.8088
1220.6406 | 122.644 | -0.68665 | 122.0306 | 0.35447 | 0.038075 | 0.0015409 | 0.39279 | -0.030984 | -0.00058594 | -0.017854 | 0.20479 | -0.024001 | 0.071214 | 0.053077 | 0.025928 | 0.081072 | -0.041199 | -0.050354 | -0.37079 | -0.022888 | 0.21515 | -0.6958 | -0.82855 | 0.050354 | 0.91553 | -0.29755 | 122.2137 | 122.1268 | -0.78278 | -0.78278 | -0.009155 | -0.14191 | -121.8155 | 0.63629 | 0.66376 | 0.80566 | -122.0718 | -0.09613 | -0.09613 | 0.1831 | 0.737 | 0.3891 | 0.48523 | 0.09613 | 0.9018 | 0.64545 | 0.31586 | -122.8592 | 122.9004 | 122.8134 | 1.6022 | -122.8134
1221.6406 | 122.6898 | -0.6958 | 122.0215 | -0.011739 | 0.02953 | 0.0058129 | 0.36609 | -0.023507 | -0.0048589 | -0.0071733 | -0.14616 | -0.025069 | 0.058397 | 0.044532 | 0.019519 | 0.077868 | 0.032043 | 0.036621 | -0.28839 | 0.013733 | 0.2243 | -0.66376 | -0.83771 | 0.09613 | 1.4923 | -0.24261 | 122.1954 | 122.1268 | -0.75989 | -0.7782 | 0.032044 | -0.14191 | -121.7972 | 0.73242 | 0.70953 | 0.85144 | -121.9894 | -0.064087 | -0.082397 | 0.17395 | 0.79193 | 0.45319 | 0.53558 | 0.10529 | 0.9201 | 0.72784 | 0.40741 | -122.8592 | 122.8912 | 122.8226 | 2.1881 | -122.7997
1222.6562 | 122.6944 | -0.66376 | 122.0032 | 0.20188 | 0.035939 | 0.0047449 | 0.37143 | -0.039529 | 0.015435 | -0.038148 | -0.17668 | -0.021865 | 0.05626 | 0.039191 | 0.018451 | 0.075732 | 0.10986 | 0 | -0.31128 | 0.045776 | 0.27466 | -0.59509 | -0.74616 | 0.10071 | 0.036621 | -0.26093 | 122.2046 | 122.1222 | -0.74616 | -0.75531 | 0.068664 | -0.082398 | -121.7285 | 0.66376 | 0.70953 | 0.79193 | -121.8933 | -0.082398 | -0.091553 | 0.20142 | 0.76447 | 0.40283 | 0.49439 | 0.11902 | 0.93841 | 0.77362 | 0.35248 | -122.7493 | 122.8683 | 122.7859 | 0.70038 | -122.7585
1223.6406 | 122.6532 | -0.69122 | 122.0215 | -1.1104 | 0.066914 | -0.0080721 | 0.3725 | -0.03312 | 0.0026181 | -0.028535 | 0.036941 | -0.017592 | 0.066941 | 0.035987 | 0.021655 | 0.075732 | 0.045776 | 0.036621 | -0.28381 | -0.059509 | 0.26093 | -0.65918 | -0.81482 | 0.073242 | 13.353 | -0.28381 | 122.168 | 122.081 | -0.79651 | -0.80109 | 0.032043 | -0.1236 | -121.7606 | 0.72784 | 0.63171 | 0.75531 | -121.9757 | -0.10529 | -0.10986 | 0.14648 | 0.76447 | 0.40741 | 0.51727 | 0.05951 | 0.95215 | 0.737 | 0.40741 | -122.8363 | 122.8592 | 122.7722 | 14.0442 | -122.8226
1224.6406 | 122.7631 | -0.67291 | 121.9666 | 0.59861 | 0.031666 | 0.0058129 | 0.38425 | -0.048074 | -0.0059269 | -0.028535 | 0.44893 | -0.03575 | 0.05092 | 0.039191 | 0.016315 | 0.08214 | -0.009155 | -0.009155 | -0.30212 | -0.013733 | 0.21057 | -0.68665 | -0.81482 | 0.15106 | 14.9323 | -0.21515 | 122.1863 | 122.1039 | -0.74616 | -0.76446 | -0.013733 | -0.14191 | -121.756 | 0.66376 | 0.65918 | 0.80109 | -121.9757 | -0.073242 | -0.091552 | 0.21973 | 0.82398 | 0.45776 | 0.54932 | 0.13733 | 0.88348 | 0.66376 | 0.37079 | -122.7814 | 122.8592 | 122.7768 | 15.6052 | -122.731
1225.6406 | 122.6944 | -0.66834 | 121.9757 | -0.14907 | 0.048756 | 0.0079499 | 0.37784 | -0.035257 | -0.0048589 | -0.030671 | 0.47945 | -0.022933 | 0.049852 | 0.038123 | 0.015247 | 0.089617 | 0 | -0.036621 | -0.34332 | -0.036621 | 0.22888 | -0.6958 | -0.80566 | 0.1236 | 13.4125 | -0.23346 | 122.2092 | 122.1222 | -0.75989 | -0.78278 | -0.027466 | -0.13733 | -121.7468 | 0.63171 | 0.63171 | 0.76904 | -121.9757 | -0.091553 | -0.11444 | 0.23346 | 0.79193 | 0.43488 | 0.54932 | 0.14648 | 0.89722 | 0.66834 | 0.32501 | -122.7814 | 122.8775 | 122.7905 | 14.0808 | -122.7585
1226.6406 | 122.731 | -0.59509 | 122.0627 | 0.53758 | 0.014576 | 0.012222 | 0.36289 | -0.038461 | -0.034766 | -0.027467 | 0.54048 | -0.030409 | 0.053056 | 0.024238 | 0.0099061 | 0.089617 | 0.032043 | 0.054932 | -0.24261 | -0.004578 | 0.20142 | -0.5722 | -0.73242 | 0.29297 | 14.3967 | -0.11902 | 122.2321 | 122.1817 | -0.70038 | -0.70496 | 0.022888 | -0.13733 | -121.8613 | 0.65002 | 0.59052 | 0.72784 | -122.0306 | -0.10528 | -0.10986 | 0.16937 | 0.88806 | 0.47607 | 0.58594 | 0.11902 | 0.79651 | 0.62714 | 0.35248 | -122.7951 | 122.8271 | 122.7768 | 14.9918 | -122.7676
1227.6562 | 122.7585 | -0.50812 | 122.113 | 0.034038 | 0.019917 | 0.014358 | 0.36609 | -0.054483 | -0.03797 | -0.033876 | 0.25056 | -0.034682 | 0.035966 | 0.032783 | 0.015247 | 0.08214 | 0.022888 | 0.054932 | -0.21973 | 0.041199 | 0.20599 | -0.55389 | -0.67749 | 0.31586 | 14.4928 | 0.009155 | 122.3236 | 122.2504 | -0.62256 | -0.63629 | -0.045776 | -0.16937 | -121.907 | 0.56305 | 0.54932 | 0.71869 | -122.0901 | -0.11444 | -0.12817 | 0.21057 | 0.82397 | 0.51727 | 0.64545 | 0.13733 | 0.71411 | 0.53101 | 0.28839 | -122.7905 | 122.8317 | 122.7585 | 15.0009 | -122.7493
1228.6406 | 122.5983 | -0.53101 | 122.0032 | 0.53758 | 0.053029 | 0.0026089 | 0.36716 | -0.021371 | -0.0069949 | -0.030671 | 0.50996 | -0.040022 | 0.074418 | 0.032783 | 0.020587 | 0.068255 | 0.10071 | 0.082397 | -0.21973 | 0.036621 | 0.20599 | -0.54474 | -0.6958 | 0.32959 | 14.2456 | -0.013733 | 122.2641 | 122.1817 | -0.62256 | -0.65002 | -0.013733 | -0.1648 | -121.7972 | 0.6134 | 0.56763 | 0.73242 | -121.9025 | -0.091553 | -0.11902 | 0.26093 | 0.8606 | 0.51727 | 0.63629 | 0.17853 | 0.737 | 0.63171 | 0.31128 | -122.699 | 122.7951 | 122.7127 | 14.7766 | -122.6532
1229.6406 | 122.7539 | -0.54474 | 122.0993 | 0.53758 | 0.035939 | 0.0068819 | 0.37464 | -0.030984 | -0.0037909 | -0.023195 | -0.31401 | -0.029341 | 0.054124 | 0.052009 | 0.020587 | 0.066119 | 0.086975 | 0.10529 | -0.27466 | -0.21973 | 0.17395 | -0.54474 | -0.70038 | 0.3067 | 13.5269 | -0.009155 | 122.287 | 122.2 | -0.63629 | -0.65002 | 0 | -0.15564 | -121.9254 | 0.65002 | 0.32501 | 0.48065 | -122.0123 | -0.091553 | -0.10529 | 0.18768 | 0.85144 | 0.53558 | 0.64087 | 0.10071 | 0.71869 | 0.63171 | 0.27008 | -122.7997 | 122.8317 | 122.7448 | 14.0717 | -122.7493
1230.6406 | 122.7402 | -0.55389 | 122.1313 | 0.32395 | -0.0035808 | 0.01329 | 0.3725 | -0.029916 | -0.027289 | -0.043489 | 0.2353 | -0.041091 | 0.047715 | 0.042396 | 0.01311 | 0.078936 | 0.004578 | 0.054932 | -0.23804 | 0.022888 | 0.20599 | -0.54016 | -0.67291 | 0.24261 | 13.4491 | -0.041199 | 122.319 | 122.2183 | -0.64545 | -0.6546 | 0.013733 | -0.11902 | -121.9254 | 0.60883 | 0.57678 | 0.6958 | -122.1268 | -0.091553 | -0.10071 | 0.18768 | 0.79651 | 0.5127 | 0.6134 | 0.086975 | 0.75989 | 0.55847 | 0.31586 | -122.8043 | 122.8729 | 122.7722 | 14.003 | -122.7859
1231.6406 | 122.8043 | -0.48981 | 122.1268 | 0.43077 | 0.025258 | -0.0048681 | 0.35648 | -0.026712 | 0.0068901 | -0.018922 | 0.55574 | -0.038954 | 0.049852 | 0.032783 | 0.022724 | 0.063982 | 0.10986 | 0.086975 | -0.20142 | 0.073242 | 0.18768 | -0.52185 | -0.65918 | 0.3479 | 13.4583 | -0.013733 | 122.2961 | 122.1909 | -0.6134 | -0.61798 | -0.032044 | -0.16937 | -121.9391 | 0.57678 | 0.56305 | 0.73242 | -122.0169 | -0.1236 | -0.12817 | 0.16937 | 0.83771 | 0.47607 | 0.60425 | 0.064087 | 0.67749 | 0.59967 | 0.28839 | -122.7859 | 122.7859 | 122.6807 | 13.9481 | -122.7448
1232.6406 | 122.6715 | -0.53558 | 122.168 | -0.27114 | 0.030598 | 0.0079499 | 0.38318 | -0.030984 | -0.013404 | -0.018922 | -0.35979 | -0.042159 | 0.058397 | 0.039191 | 0.01311 | 0.073595 | 0.050354 | 0.064087 | -0.2243 | 0.041199 | 0.21973 | -0.52643 | -0.67291 | 0.27008 | 13.7558 | -0.091553 | 122.3557 | 122.2687 | -0.64087 | -0.63171 | 0.009155 | -0.13733 | -121.9482 | 0.59967 | 0.57678 | 0.71411 | -122.1176 | -0.10529 | -0.096131 | 0.18768 | 0.80566 | 0.44403 | 0.54016 | 0.10071 | 0.75531 | 0.58594 | 0.31128 | -122.8409 | 122.8912 | 122.8043 | 14.2914 | -122.7997
1233.6406 | 122.7448 | -0.55847 | 122.113 | 0.3087 | 0.01244 | 0.0058129 | 0.37784 | -0.021371 | -0.019813 | -0.044557 | 0.22005 | -0.043227 | 0.057328 | 0.043464 | 0.0067021 | 0.081072 | 0.013733 | 0.068665 | -0.25177 | 0.018311 | 0.21515 | -0.52185 | -0.65918 | 0.28381 | 13.7512 | -0.2243 | 122.2687 | 122.1222 | -0.66376 | -0.66834 | 0.036621 | -0.10071 | -121.8979 | 0.62714 | 0.57678 | 0.67749 | -122.0993 | -0.10529 | -0.10986 | 0.15564 | 0.84228 | 0.33417 | 0.44403 | 0.009155 | 0.77362 | 0.5722 | 0.3067 | -122.7722 | 122.8271 | 122.6807 | 14.3097 | -122.7814
1234.6406 | 122.7493 | -0.50812 | 122.1542 | 1.9261 | 0.010304 | 0.01329 | 0.3757 | -0.029916 | -0.014472 | -0.028535 | -0.2072 | -0.03575 | 0.057328 | 0.047736 | 0.020587 | 0.066119 | 0.082397 | 0.11902 | -0.18768 | 0.07782 | 0.20142 | -0.5127 | -0.6546 | 0.30212 | 14.2364 | -0.004578 | 122.3465 | 122.2137 | -0.58594 | -0.62714 | -0.004577 | -0.14648 | -121.9528 | 0.62714 | 0.58594 | 0.73242 | -122.0718 | -0.077819 | -0.11902 | 0.19226 | 0.81024 | 0.50354 | 0.62256 | 0.059509 | 0.70953 | 0.59051 | 0.32043 | -122.8088 | 122.8546 | 122.7219 | 14.7446 | -122.7814
1235.6406 | 122.7814 | -0.53101 | 122.1634 | -0.13381 | 0.023121 | 0.0090179 | 0.35648 | -0.034188 | -0.018744 | -0.03708 | -0.054612 | -0.049636 | 0.041307 | 0.041327 | 0.016315 | 0.072527 | -0.054932 | 0.34332 | -0.10071 | -0.032043 | 0.19684 | -0.54016 | -0.67749 | 0.32959 | 13.7924 | 0.009155 | 122.3465 | 122.2229 | -0.62256 | -0.63171 | -0.009155 | -0.14648 | -121.9666 | 0.87433 | 0.49896 | 0.64545 | -122.2183 | -0.091553 | -0.10071 | 0.18311 | 0.8606 | 0.54016 | 0.64087 | 0.059509 | 0.72784 | 0.47607 | 0.4303 | -122.8409 | 122.8775 | 122.7539 | 14.3234 | -122.7951
1236.6406 | 122.8088 | -0.63171 | 122.0398 | 0.064555 | 0.0071002 | 0.012222 | 0.38639 | -0.037393 | -0.017676 | -0.036012 | -0.0088351 | -0.046431 | 0.043443 | 0.0456 | 0.0077701 | 0.078936 | 0.054932 | 0.13733 | -0.18768 | 0.082397 | 0.23346 | -0.59967 | -0.7782 | 0.22888 | 12.2131 | -0.11444 | 122.2321 | 122.0718 | -0.70496 | -0.74616 | 0.032044 | -0.14648 | -121.8063 | 0.76904 | 0.71411 | 0.86059 | -121.9849 | -0.073242 | -0.11444 | 0.19226 | 0.8606 | 0.51727 | 0.63171 | 0.032043 | 0.86517 | 0.68665 | 0.44403 | -122.818 | 122.8638 | 122.7036 | 12.8448 | -122.7859
1237.6406 | 122.6944 | -0.66376 | 122.0581 | -0.13381 | 0.030598 | -0.0027321 | 0.38425 | -0.019235 | 0.016503 | -0.017854 | -0.32927 | -0.024001 | 0.06801 | 0.041327 | 0.020587 | 0.061846 | 0.027466 | 0.041199 | -0.28381 | 0.027466 | 0.20599 | -0.67291 | -0.82855 | 0.091553 | 12.8174 | -0.25177 | 122.2641 | 122.1085 | -0.76446 | -0.76904 | -0.009156 | -0.16479 | -121.8521 | 0.70496 | 0.69122 | 0.85602 | -122.0306 | -0.10071 | -0.10529 | 0.20599 | 0.75531 | 0.41199 | 0.51727 | 0.050354 | 0.86975 | 0.69122 | 0.37994 | -122.8867 | 122.9279 | 122.7722 | 13.4811 | -122.8271
1238.6406 | 122.7264 | -0.65002 | 122.0718 | -0.14907 | 0.019917 | 0.010086 | 0.35755 | -0.040597 | -0.021949 | -0.032808 | -0.32927 | -0.022933 | 0.043443 | 0.039191 | 0.016315 | 0.068255 | 0.050354 | 0.1236 | -0.21515 | 0.064087 | 0.21057 | -0.64087 | -0.79193 | 0.086975 | 13.1241 | -0.18768 | 122.2504 | 122.1222 | -0.737 | -0.75531 | 0.009155 | -0.14191 | -121.8613 | 0.77362 | 0.71411 | 0.85602 | -122.0215 | -0.086976 | -0.10529 | 0.17853 | 0.737 | 0.46234 | 0.56763 | 0.050354 | 0.86059 | 0.70038 | 0.43488 | -122.8638 | 122.9004 | 122.7722 | 13.7741 | -122.8271
1239.6406 | 122.6669 | -0.64545 | 122.081 | -0.33217 | 0.028462 | 0.019699 | 0.37464 | -0.048074 | -0.0037909 | -0.023195 | -0.43608 | -0.027205 | 0.061601 | 0.034919 | 0.020587 | 0.063982 | -0.032043 | 0 | -0.3067 | -0.045776 | 0.2243 | -0.68665 | -0.83771 | 0.16479 | 13.1744 | -0.37079 | 122.3145 | 122.1634 | -0.72327 | -0.73242 | -0.041199 | -0.19226 | -121.8567 | 0.64545 | 0.59967 | 0.79193 | -122.113 | -0.07782 | -0.086975 | 0.23346 | 0.81024 | 0.27466 | 0.36163 | 0.082397 | 0.86975 | 0.6134 | 0.33875 | -122.9187 | 122.9599 | 122.8088 | 13.8199 | -122.8134
1240.6406 | 122.699 | -0.66834 | 122.0627 | 3.4978 | 0.031666 | 0.012222 | 0.36609 | -0.028848 | -0.00058594 | -0.026399 | -0.23772 | -0.022933 | 0.038102 | 0.042396 | 0.028064 | 0.060778 | 0.018311 | -0.004578 | -0.32501 | 0.009155 | 0.27466 | -0.66376 | -0.80566 | 0.054932 | 13.0829 | -0.27008 | 122.2641 | 122.1497 | -0.75989 | -0.78735 | 0.004578 | -0.13733 | -121.788 | 0.66376 | 0.67749 | 0.81482 | -122.0444 | -0.091553 | -0.11902 | 0.20142 | 0.72327 | 0.39825 | 0.51727 | 0.086975 | 0.94299 | 0.68665 | 0.34332 | -122.8683 | 122.9324 | 122.818 | 13.7512 | -122.85
1241.6406 | 122.7402 | -0.66376 | 122.081 | 0.00352 | 0.042347 | 0.0015409 | 0.37784 | -0.024575 | 0.014367 | -0.010377 | -0.45134 | -0.021865 | 0.062669 | 0.038123 | 0.0302 | 0.069323 | 0.036621 | 0.064087 | -0.27924 | 0.041199 | 0.23804 | -0.65918 | -0.81024 | 0.11444 | 12.9364 | -0.23804 | 122.2687 | 122.1268 | -0.75531 | -0.77362 | 0.004577 | -0.14648 | -121.843 | 0.72784 | 0.70496 | 0.85144 | -122.0444 | -0.091553 | -0.10986 | 0.18768 | 0.7782 | 0.42572 | 0.53558 | 0.045776 | 0.90179 | 0.70038 | 0.38452 | -122.8912 | 122.9324 | 122.7905 | 13.6002 | -122.8546
1242.6406 | 122.7997 | -0.53558 | 122.1313 | 1.5447 | 0.033803 | 0.010086 | 0.36502 | -0.034188 | -0.01554 | -0.026399 | 0.4947 | -0.024001 | 0.046647 | 0.035987 | 0.022724 | 0.085345 | 0.068665 | 0.11902 | -0.19684 | 0.086975 | 0.18768 | -0.54474 | -0.68207 | 0.21973 | 13.5269 | -0.027466 | 122.3328 | 122.1954 | -0.63171 | -0.64545 | -0.009156 | -0.14648 | -121.9437 | 0.6546 | 0.62256 | 0.76904 | -122.0627 | -0.096131 | -0.10986 | 0.20142 | 0.75531 | 0.50812 | 0.61798 | 0.064087 | 0.72327 | 0.60425 | 0.33875 | -122.8134 | 122.8683 | 122.731 | 14.0625 | -122.7768
1243.6406 | 122.7173 | -0.67749 | 122.0673 | 0.3087 | 0.062642 | 0.020767 | 0.38104 | -0.047006 | 0.0026181 | -0.026399 | -0.06987 | -0.016524 | 0.05626 | 0.040259 | 0.029132 | 0.072527 | 0.032043 | 0.027466 | -0.30212 | 0.009155 | 0.23804 | -0.66376 | -0.79651 | 0.027466 | 13.6963 | -0.25177 | 122.2412 | 122.1634 | -0.76904 | -0.7782 | 0.013733 | -0.11902 | -121.8292 | 0.70496 | 0.68665 | 0.80566 | -122.0352 | -0.091553 | -0.10071 | 0.17395 | 0.70496 | 0.42572 | 0.52643 | 0.09613 | 0.91553 | 0.70953 | 0.37537 | -122.8638 | 122.9187 | 122.8409 | 14.3738 | -122.8455
1244.6406 | 122.731 | -0.66834 | 122.0718 | 0.11033 | 0.04662 | -0.0038001 | 0.37464 | -0.020303 | 0.0036861 | -0.028535 | -0.039353 | -0.01866 | 0.058397 | 0.052009 | 0.021655 | 0.075732 | 0.23804 | 0.25177 | -0.23346 | 0.022888 | 0.27924 | -0.6134 | -0.74158 | 0.050354 | 13.8153 | -0.24719 | 122.2504 | 122.1817 | -0.74616 | -0.7782 | 0.054932 | -0.073242 | -121.7926 | 0.9201 | 0.69122 | 0.76447 | -121.8338 | -0.07782 | -0.10986 | 0.17853 | 0.71869 | 0.42114 | 0.53101 | 0.10986 | 0.94757 | 0.90637 | 0.43488 | -122.8134 | 122.9187 | 122.85 | 14.4836 | -122.85
1245.6406 | 122.7539 | -0.66834 | 122.0444 | -0.16433 | 0.049824 | -0.00059506 | 0.37784 | -0.030984 | 0.00048206 | -0.025331 | -0.17668 | -0.031478 | 0.05092 | 0.038123 | 0.021655 | 0.078936 | -0.009155 | 0.022888 | -0.28839 | -0.086975 | 0.21515 | -0.69122 | -0.82855 | 0.050354 | 13.9938 | -0.2243 | 122.2733 | 122.1542 | -0.79651 | -0.79193 | -0.022888 | -0.16022 | -121.8292 | 0.69122 | 0.58136 | 0.74158 | -122.0535 | -0.12817 | -0.1236 | 0.22888 | 0.71869 | 0.44403 | 0.56763 | 0.10986 | 0.88348 | 0.65918 | 0.37994 | -122.8729 | 122.9416 | 122.8226 | 14.6622 | -122.8363
1246.6406 | 122.7402 | -0.57678 | 122.1817 | -1.7055 | 0.037007 | 0.0090179 | 0.38532 | -0.029916 | -0.019813 | -0.022126 | 0.38789 | -0.019728 | 0.05626 | 0.034919 | 0.022724 | 0.081072 | -0.041199 | -0.022888 | -0.3067 | -0.073242 | 0.22888 | -0.57678 | -0.71869 | 0.18768 | 13.5956 | -0.10071 | 122.3694 | 122.2504 | -0.67291 | -0.66834 | 0 | -0.14191 | -121.9528 | 0.55389 | 0.50354 | 0.64545 | -122.2229 | -0.096131 | -0.091553 | 0.18768 | 0.76446 | 0.47607 | 0.56763 | 0.068664 | 0.80566 | 0.53558 | 0.27008 | -122.9004 | 122.9462 | 122.8271 | 14.1724 | -122.85
1247.6406 | 122.7951 | -0.50354 | 122.1542 | 0.56809 | -0.0025128 | -0.00059506 | 0.36823 | -0.032052 | -0.036902 | -0.034944 | 0.43367 | -0.03575 | 0.055192 | 0.040259 | 0.010974 | 0.086413 | -0.027466 | 0.16022 | -0.1831 | -0.082397 | 0.14648 | -0.54932 | -0.70496 | 0.28381 | 13.4766 | 0.045776 | 122.3511 | 122.2733 | -0.61798 | -0.62714 | -0.045776 | -0.20142 | -122.0078 | 0.66376 | 0.42114 | 0.62256 | -122.1817 | -0.11444 | -0.1236 | 0.19684 | 0.78735 | 0.54932 | 0.67291 | 0.11902 | 0.65002 | 0.47607 | 0.32044 | -122.8592 | 122.8546 | 122.7768 | 13.9801 | -122.7814
1248.6406 | 122.8226 | -0.53101 | 122.1313 | 0.58335 | 0.035939 | 0.0036769 | 0.37891 | -0.03312 | -0.0091309 | -0.016786 | 0.37263 | -0.029341 | 0.047715 | 0.040259 | 0.02486 | 0.072527 | 0.059509 | 0.073242 | -0.24261 | -0.26093 | 0.20142 | -0.55389 | -0.68665 | 0.29297 | 13.3667 | 0.032043 | 122.319 | 122.2366 | -0.61798 | -0.64087 | -0.022888 | -0.15564 | -121.9299 | 0.60425 | 0.27008 | 0.42572 | -122.0718 | -0.086975 | -0.10986 | 0.18768 | 0.82397 | 0.56305 | 0.67291 | 0.10528 | 0.73242 | 0.59052 | 0.28839 | -122.818 | 122.85 | 122.7676 | 13.8977 | -122.7722
1249.6406 | 122.7356 | -0.6134 | 122.1497 | 0.50706 | 0.050892 | 0.00047294 | 0.38959 | -0.04487 | -0.00058594 | -0.047761 | 0.58626 | -0.025069 | 0.058397 | 0.046668 | 0.025928 | 0.0768 | 0.23804 | -0.13733 | -0.40283 | -0.46692 | 0.26093 | -0.5722 | -0.72784 | 0.16022 | 12.9501 | -0.07782 | 122.3557 | 122.2504 | -0.68665 | -0.71411 | 0.041198 | -0.11444 | -121.8887 | 0.47607 | 0.14648 | 0.26093 | -121.9116 | -0.073243 | -0.10071 | 0.20599 | 0.77362 | 0.53558 | 0.63629 | 0.10071 | 0.87433 | 0.85144 | 0.21057 | -122.8775 | 122.9691 | 122.8638 | 13.5635 | -122.8638
1250.6406 | 122.8226 | -0.54932 | 122.1222 | 0.049296 | -0.0057178 | -0.0048681 | 0.37677 | -0.035257 | -0.03797 | -0.024263 | -0.0088351 | -0.033614 | 0.041307 | 0.035987 | 0.0088381 | 0.080004 | 0.082397 | 0.16022 | -0.1831 | -0.37079 | 0.19684 | -0.56763 | -0.6958 | 0.19226 | 13.2156 | 0.082397 | 122.3236 | 122.2549 | -0.65918 | -0.65918 | -0.018311 | -0.14648 | -121.9254 | 0.70953 | 0.17853 | 0.32501 | -122.0398 | -0.10986 | -0.10986 | 0.20142 | 0.74158 | 0.63171 | 0.74158 | 0.13275 | 0.74615 | 0.63171 | 0.36621 | -122.818 | 122.8729 | 122.8043 | 13.765 | -122.7814
1251.6406 | 122.7997 | -0.56763 | 122.1268 | 0.44602 | 0.016713 | 0.0047449 | 0.35541 | -0.045938 | -0.021949 | -0.030671 | 0.54048 | -0.031478 | 0.048783 | 0.027442 | 0.025928 | 0.078936 | 0.064087 | 0.10071 | -0.19684 | -0.42572 | 0.19226 | -0.55389 | -0.70496 | 0.21515 | 13.4399 | 0.050354 | 122.319 | 122.2366 | -0.65002 | -0.66834 | 0.013733 | -0.13733 | -121.9345 | 0.66834 | 0.14191 | 0.27924 | -122.0627 | -0.082397 | -0.10071 | 0.19226 | 0.78278 | 0.61798 | 0.71869 | 0.10986 | 0.75989 | 0.63171 | 0.37079 | -122.8317 | 122.8867 | 122.8043 | 14.0076 | -122.7951
1252.6562 | 122.7173 | -0.62256 | 122.1313 | 0.32395 | 0.041279 | -0.0048681 | 0.38639 | -0.02778 | 0.0079581 | -0.021058 | 0.28108 | -0.030409 | 0.064805 | 0.044532 | 0.033405 | 0.063982 | -0.018311 | -0.054932 | -0.3479 | -0.54474 | 0.22888 | -0.61798 | -0.74158 | 0.09613 | 14.0396 | -0.10529 | 122.3877 | 122.2458 | -0.70496 | -0.6958 | 0.004578 | -0.11902 | -121.9025 | 0.56763 | 0.07782 | 0.19684 | -122.1497 | -0.082397 | -0.073242 | 0.25635 | 0.71869 | 0.51727 | 0.59052 | 0.11444 | 0.85144 | 0.60425 | 0.27466 | -122.8729 | 123.0103 | 122.8683 | 14.6622 | -122.8271
1253.6875 | 122.8455 | -0.57678 | 122.113 | -0.11855 | 0.0092362 | 0.00047294 | 0.36502 | -0.026712 | -0.050788 | -0.033876 | 0.32686 | -0.042159 | 0.034898 | 0.022101 | 0.016315 | 0.083208 | 0.21973 | -0.20599 | -0.32501 | -0.48065 | 0.18768 | -0.58594 | -0.75073 | 0.1831 | 14.3051 | 0.041199 | 122.3145 | 122.2321 | -0.68207 | -0.69122 | -0.009155 | -0.17395 | -121.9254 | 0.37079 | 0.09613 | 0.27008 | -121.8933 | -0.10529 | -0.11444 | 0.20142 | 0.75989 | 0.61798 | 0.73242 | 0.11902 | 0.76446 | 0.79651 | 0.25177 | -122.8638 | 122.8912 | 122.8088 | 14.8819 | -122.8043
1254.6406 | 122.85 | -0.63171 | 122.0352 | 0.079814 | 0.0049632 | 0.025039 | 0.37464 | -0.028848 | -0.045447 | -0.039216 | -0.024094 | -0.048567 | 0.034898 | 0.039191 | 0.021655 | 0.083208 | 0.059509 | 0.12817 | -0.20142 | -0.50354 | 0.22888 | -0.63629 | -0.7782 | 0.15106 | 15.3168 | 0.013733 | 122.2549 | 122.1222 | -0.72784 | -0.74158 | -0.004578 | -0.14648 | -121.8063 | 0.75989 | 0.12817 | 0.27466 | -121.9757 | -0.09613 | -0.10986 | 0.21973 | 0.78278 | 0.64545 | 0.75531 | 0.086975 | 0.8606 | 0.69122 | 0.4303 | -122.8134 | 122.8867 | 122.7539 | 15.9485 | -122.7768
1255.6406 | 122.7631 | -0.79651 | 121.9391 | -0.36269 | 0.02953 | -0.0080721 | 0.37891 | -0.041665 | -0.0027229 | -0.034944 | -0.40556 | -0.021865 | 0.071214 | 0.039191 | 0.026996 | 0.05971 | -0.022888 | 0.018311 | -0.34332 | -0.60883 | 0.25177 | -0.79651 | -0.95215 | -0.09613 | 13.8977 | -0.31128 | 122.1817 | 122.049 | -0.90179 | -0.92468 | 0 | -0.15564 | -121.6873 | 0.81482 | 0.18768 | 0.34332 | -121.962 | -0.10528 | -0.12817 | 0.24262 | 0.70038 | 0.48523 | 0.6134 | 0.10986 | 1.0483 | 0.77362 | 0.45319 | -122.8912 | 122.9782 | 122.8455 | 14.6942 | -122.8638
1256.6406 | 122.8271 | -0.75073 | 121.9528 | -0.11855 | -0.00037681 | 0.0079499 | 0.3757 | -0.036325 | -0.027289 | -0.046693 | 0.14375 | -0.038954 | 0.042375 | 0.046668 | -0.00077485 | 0.0768 | 0.013733 | 0.09613 | -0.25635 | -0.62256 | 0.20142 | -0.76446 | -0.93384 | -0.004578 | 13.9023 | -0.17395 | 122.1268 | 122.0169 | -0.85144 | -0.87891 | -0.013733 | -0.18311 | -121.7514 | 0.84686 | 0.12817 | 0.31128 | -121.9391 | -0.10071 | -0.12817 | 0.17395 | 0.74615 | 0.57678 | 0.70496 | 0.064087 | 0.95215 | 0.76446 | 0.49438 | -122.8867 | 122.8775 | 122.7676 | 14.653 | -122.8317
1257.6406 | 122.8546 | -0.76446 | 121.9666 | 0.14085 | -0.0014448 | 0.0090179 | 0.36823 | -0.039529 | -0.019813 | -0.030671 | -0.06987 | -0.041091 | 0.047715 | 0.030646 | 0.018451 | 0.075732 | 0.045776 | 0.11902 | -0.21973 | -0.62714 | 0.22888 | -0.75531 | -0.89722 | 0.018311 | 14.74 | -0.1236 | 122.1542 | 122.0352 | -0.8606 | -0.86975 | 0.009155 | -0.13275 | -121.7377 | 0.88348 | 0.13733 | 0.27008 | -121.9208 | -0.096131 | -0.10529 | 0.18768 | 0.78278 | 0.64087 | 0.74616 | 0.068664 | 0.99335 | 0.81024 | 0.54474 | -122.8638 | 122.9187 | 122.7997 | 15.5045 | -122.8363
1258.6406 | 122.8409 | -0.64087 | 122.0398 | -0.16433 | 0.0071002 | 0.015426 | 0.36609 | -0.034188 | -0.012336 | -0.034944 | -0.22246 | -0.044295 | 0.049852 | 0.06269 | 0.029132 | 0.052233 | 0.068665 | 0.14191 | -0.19226 | -0.49896 | 0.21057 | -0.63171 | -0.78278 | 0.16937 | 13.8062 | -0.073242 | 122.2275 | 122.1451 | -0.74158 | -0.77362 | 0.009155 | -0.14191 | -121.8292 | 0.78278 | 0.14191 | 0.28381 | -121.9711 | -0.10071 | -0.13275 | 0.18768 | 0.81024 | 0.56763 | 0.70038 | 0.10529 | 0.85144 | 0.70953 | 0.44861 | -122.8226 | 122.8683 | 122.7859 | 14.447 | -122.8134
1259.6406 | 122.8271 | -0.5722 | 122.1542 | -0.59157 | 0.0081682 | 0.0068819 | 0.36075 | -0.036325 | -0.033698 | -0.048829 | -0.23772 | -0.048567 | 0.05092 | 0.037055 | 0.017383 | 0.084276 | 0.086975 | 0.1831 | -0.16022 | -0.46692 | 0.19684 | -0.58594 | -0.71869 | 0.20142 | 13.8977 | 0.073242 | 122.2916 | 122.1954 | -0.66376 | -0.68665 | -0.013732 | -0.14648 | -121.9574 | 0.75531 | 0.10529 | 0.25177 | -122.0673 | -0.091552 | -0.11444 | 0.13733 | 0.77362 | 0.64545 | 0.75989 | 0.041199 | 0.76904 | 0.65918 | 0.41199 | -122.8729 | 122.8638 | 122.7676 | 14.4699 | -122.8409
1260.6562 | 122.8271 | -0.57678 | 122.1588 | 0.55284 | 0.041279 | 0.012222 | 0.36609 | -0.024575 | 0.010095 | -0.030671 | 0.29634 | -0.037886 | 0.047715 | 0.053077 | 0.025928 | 0.072527 | 0.054932 | 0.054932 | -0.2655 | -0.50354 | 0.20142 | -0.57678 | -0.74158 | 0.19226 | 13.7466 | 0.013733 | 122.3145 | 122.1954 | -0.6546 | -0.69122 | 0 | -0.1648 | -121.9574 | 0.63171 | 0.073242 | 0.23804 | -122.1039 | -0.07782 | -0.11444 | 0.15564 | 0.76904 | 0.59052 | 0.70496 | 0.036622 | 0.7782 | 0.63171 | 0.31128 | -122.9004 | 122.8912 | 122.7722 | 14.3234 | -122.85
1261.6406 | 122.8546 | -0.57678 | 122.168 | -6.2526 | 0.0028272 | -0.012345 | 0.35327 | -0.017099 | -0.016608 | -0.023195 | -0.45134 | -0.034682 | 0.049852 | 0.031714 | 0.016315 | 0.080004 | -0.027466 | 0.17853 | -0.17853 | -0.47607 | 0.19226 | -0.58594 | -0.737 | 0.17395 | 13.6047 | 0.036621 | 122.3511 | 122.2183 | -0.68665 | -0.69122 | -0.009155 | -0.16022 | -121.9757 | 0.75531 | 0.10071 | 0.26093 | -122.1954 | -0.10986 | -0.11444 | 0.1831 | 0.75073 | 0.6134 | 0.72784 | 0.050354 | 0.76904 | 0.54932 | 0.39825 | -122.905 | 122.9279 | 122.7951 | 14.1815 | -122.8592
1262.6562 | 122.8363 | -0.59509 | 122.1405 | 0.64439 | 0.023121 | 0.0058129 | 0.37891 | -0.037393 | -0.0059269 | -0.026399 | 0.38789 | -0.027205 | 0.065873 | 0.024238 | 0.037677 | 0.072527 | 0.086975 | 0.10529 | -0.20599 | -0.46692 | 0.20142 | -0.56305 | -0.72327 | 0.07782 | 13.7329 | 0.050354 | 122.2687 | 122.1588 | -0.71411 | -0.73242 | 0.032044 | -0.12817 | -121.9391 | 0.70038 | 0.12817 | 0.25635 | -122.0535 | -0.11902 | -0.13733 | 0.12817 | 0.67291 | 0.64545 | 0.78278 | 0.01831 | 0.79651 | 0.68207 | 0.3891 | -122.8638 | 122.8638 | 122.7539 | 14.328 | -122.8729
1263.6406 | 122.7585 | -0.62714 | 122.168 | -0.39321 | 0.041279 | 0.0047449 | 0.396 | -0.038461 | 0.0058221 | -0.027467 | -0.4666 | -0.021865 | 0.062669 | 0.041327 | 0.028064 | 0.069323 | 0.013733 | 0 | -0.31128 | -0.53558 | 0.2243 | -0.59967 | -0.7782 | 0.091553 | 13.7466 | -0.07782 | 122.374 | 122.2687 | -0.70953 | -0.73242 | 0.027466 | -0.15106 | -121.9437 | 0.62714 | 0.091553 | 0.24261 | -122.1542 | -0.082398 | -0.10529 | 0.20599 | 0.71869 | 0.54932 | 0.6546 | 0.10071 | 0.85144 | 0.64087 | 0.31586 | -122.9462 | 123.0011 | 122.8958 | 14.3738 | -122.9004
1264.6406 | 122.7768 | -0.60425 | 122.1771 | -0.16433 | 0.050892 | 0.014358 | 0.37784 | -0.030984 | -0.0016549 | -0.023195 | -0.42082 | -0.024001 | 0.05626 | 0.039191 | 0.026996 | 0.063982 | 0.004578 | 0.032043 | -0.28381 | -0.5127 | 0.2243 | -0.61798 | -0.76446 | 0.13275 | 14.1632 | -0.045776 | 122.3694 | 122.2412 | -0.71411 | -0.71869 | -0.013733 | -0.16022 | -121.9528 | 0.63629 | 0.091553 | 0.25177 | -122.1725 | -0.10986 | -0.11444 | 0.19226 | 0.737 | 0.55847 | 0.67291 | 0.064087 | 0.82855 | 0.60883 | 0.32044 | -122.9416 | 122.9736 | 122.8455 | 14.7675 | -122.8958
1265.6406 | 122.7997 | -0.55389 | 122.2 | 0.50706 | 0.031666 | -0.011276 | 0.36823 | -0.03312 | -0.0037909 | -0.027467 | 0.35738 | -0.020796 | 0.064805 | 0.039191 | 0.0302 | 0.0768 | 0 | 0.050354 | -0.28381 | -0.28839 | 0.21515 | -0.54932 | -0.6958 | 0.22888 | 14.3509 | 0.018311 | 122.3648 | 122.2595 | -0.63171 | -0.63629 | 0.004578 | -0.14191 | -121.9849 | 0.60425 | 0.2655 | 0.40741 | -122.2 | -0.07782 | -0.082398 | 0.16479 | 0.78278 | 0.5722 | 0.6546 | 0.059509 | 0.76904 | 0.55389 | 0.27008 | -122.8958 | 122.9187 | 122.8134 | 14.9048 | -122.8363
1266.6406 | 122.7081 | -0.59509 | 122.2 | 0.14085 | 0.035939 | -0.0038001 | 0.37784 | -0.03312 | 0.0058221 | -0.023195 | -0.054612 | -0.021865 | 0.055192 | 0.037055 | 0.022724 | 0.083208 | 0.032043 | 0.045776 | -0.28381 | -0.41657 | 0.21515 | -0.60425 | -0.72327 | 0.1236 | 14.6713 | -0.07782 | 122.374 | 122.3053 | -0.68207 | -0.70496 | -0.009155 | -0.12817 | -121.9849 | 0.64087 | 0.17853 | 0.3067 | -122.168 | -0.086975 | -0.10986 | 0.17395 | 0.71869 | 0.51727 | 0.62714 | 0.10529 | 0.81024 | 0.62714 | 0.31128 | -122.9233 | 122.9691 | 122.9004 | 15.2664 | -122.905
1267.6406 | 122.7081 | -0.56305 | 122.2504 | 0.4918 | 0.032734 | 0.021835 | 0.3725 | -0.032052 | 0.0026181 | -0.023195 | 0.25056 | -0.026137 | 0.069078 | 0.053077 | 0.023792 | 0.072527 | -0.050354 | -0.064087 | -0.35248 | -0.21515 | 0.2243 | -0.54016 | -0.67749 | 0.13733 | 14.8911 | -0.07782 | 122.4472 | 122.3648 | -0.66376 | -0.65918 | 0.022888 | -0.11444 | -122.0261 | 0.49896 | 0.3479 | 0.46234 | -122.3007 | -0.10071 | -0.096131 | 0.19684 | 0.70038 | 0.48523 | 0.58136 | 0.11444 | 0.78735 | 0.5127 | 0.21057 | -122.9279 | 123.0103 | 122.9279 | 15.4541 | -122.9095
1268.6406 | 122.7997 | -0.52643 | 122.2412 | 0.52232 | 0.040211 | -0.0048681 | 0.38104 | -0.03312 | -0.0069949 | -0.015718 | 0.37263 | -0.026137 | 0.05092 | 0.048804 | 0.023792 | 0.0768 | -0.004578 | 0.004578 | -0.30212 | -0.13275 | 0.21057 | -0.51727 | -0.67749 | 0.21057 | 14.6713 | -0.009155 | 122.4152 | 122.3419 | -0.6134 | -0.63629 | 0.009155 | -0.15106 | -122.0306 | 0.53101 | 0.39368 | 0.54474 | -122.2458 | -0.086975 | -0.10986 | 0.17395 | 0.737 | 0.51727 | 0.62714 | 0.10071 | 0.737 | 0.52185 | 0.2243 | -122.9187 | 122.9416 | 122.8683 | 15.1978 | -122.8775
1269.6406 | 122.7493 | -0.57678 | 122.2229 | 0.26292 | 0.030598 | -0.0048681 | 0.39173 | -0.038461 | 0.0036861 | -0.029603 | 0.082718 | -0.025069 | 0.049852 | 0.0456 | 0.025928 | 0.06505 | -0.009155 | -0.041199 | -0.31586 | -0.28839 | 0.20599 | -0.5722 | -0.70953 | 0.09613 | 14.6118 | -0.10986 | 122.4197 | 122.3236 | -0.66834 | -0.67749 | 0.004577 | -0.13275 | -122.0169 | 0.53558 | 0.28839 | 0.42114 | -122.2321 | -0.091553 | -0.10071 | 0.19684 | 0.67291 | 0.46692 | 0.56763 | 0.10071 | 0.78278 | 0.56763 | 0.26093 | -122.9324 | 122.9965 | 122.9004 | 15.1886 | -122.9004
1270.6406 | 122.9095 | -0.54016 | 122.2046 | 0.049296 | 0.0060322 | 0.04747 | 0.36502 | -0.034188 | -0.056128 | -0.025331 | 0.2353 | -0.038954 | 0.051988 | 0.037055 | 0.0067021 | 0.09389 | 0.054932 | 0.1236 | -0.17853 | -0.35706 | 0.19684 | -0.53101 | -0.68207 | 0.21057 | 14.7125 | 0.1236 | 122.3557 | 122.2733 | -0.60883 | -0.6546 | 0.009155 | -0.14191 | -122.0078 | 0.66376 | 0.18311 | 0.32501 | -122.1497 | -0.068665 | -0.11444 | 0.15106 | 0.75073 | 0.66376 | 0.7782 | 0.068664 | 0.737 | 0.59509 | 0.36163 | -122.8867 | 122.8958 | 122.8134 | 15.2527 | -122.8592
1271.6406 | 122.8088 | -0.59052 | 122.2229 | 0.4918 | 0.047688 | -0.0016631 | 0.38318 | -0.021371 | 0.0047541 | -0.018922 | 0.28108 | -0.021865 | 0.061601 | 0.048804 | 0.029132 | 0.069323 | -0.013733 | -0.036621 | -0.33875 | -0.45319 | 0.23804 | -0.59967 | -0.74158 | 0.091553 | 14.4287 | -0.091553 | 122.4014 | 122.2916 | -0.6958 | -0.68207 | -0.009155 | -0.15106 | -121.9849 | 0.55389 | 0.13733 | 0.28839 | -122.2366 | -0.10529 | -0.091553 | 0.17853 | 0.68207 | 0.49896 | 0.59052 | 0.068665 | 0.82855 | 0.57678 | 0.25177 | -122.9645 | 122.9919 | 122.8821 | 15.0192 | -122.905
1272.6406 | 122.8271 | -0.62714 | 122.1451 | 0.2324 | -0.0067858 | 0.011154 | 0.36823 | -0.051278 | -0.040107 | -0.036012 | 0.2353 | -0.034682 | 0.038102 | 0.02317 | 0.022724 | 0.088549 | -0.018311 | 0.045776 | -0.25635 | -0.48523 | 0.21057 | -0.58594 | -0.72327 | 0.10986 | 14.566 | -0.11902 | 122.3236 | 122.168 | -0.70038 | -0.71869 | 0.041199 | -0.096131 | -121.9345 | 0.67291 | 0.14191 | 0.23804 | -122.1634 | -0.073242 | -0.091553 | 0.17853 | 0.737 | 0.50812 | 0.59967 | 0.022888 | 0.83771 | 0.60883 | 0.37079 | -122.8683 | 122.9507 | 122.7951 | 15.1932 | -122.8638
1273.6406 | 122.7585 | -0.60425 | 122.1634 | 0.50706 | 0.042347 | 0.0079499 | 0.38639 | -0.023507 | -0.0037909 | -0.027467 | 0.25056 | -0.024001 | 0.071214 | 0.02851 | 0.018451 | 0.068255 | 0.013733 | -0.059509 | -0.35248 | -0.53558 | 0.2243 | -0.60425 | -0.76446 | 0.16937 | 13.8474 | -0.045776 | 122.406 | 122.2916 | -0.70496 | -0.71869 | 0 | -0.16022 | -121.9391 | 0.54474 | 0.068665 | 0.22888 | -122.1497 | -0.10071 | -0.11444 | 0.24262 | 0.77362 | 0.55847 | 0.67291 | 0.12817 | 0.82855 | 0.61798 | 0.25177 | -122.9279 | 123.0103 | 122.8958 | 14.4516 | -122.8821
1274.6406 | 122.8043 | -0.83771 | 121.8979 | 0.58335 | 0.02419 | 0.0036769 | 0.36609 | -0.035257 | -0.016608 | -0.030671 | 0.54048 | -0.034682 | 0.051988 | 0.040259 | 0.020587 | 0.077868 | 0.086975 | 0.09613 | -0.23804 | -0.69122 | 0.19684 | -0.80109 | -0.93842 | -0.036621 | 14.0442 | -0.43945 | 122.0673 | 121.9757 | -0.93842 | -0.95673 | 0.036622 | -0.10071 | -121.701 | 0.93384 | 0.14648 | 0.24719 | -121.8109 | -0.10071 | -0.11902 | 0.16937 | 0.80109 | 0.39826 | 0.51727 | 0.07782 | 1.0345 | 0.92468 | 0.59967 | -122.8363 | 122.905 | 122.8134 | 14.8819 | -122.8546
1275.6406 | 122.8134 | -0.65002 | 122.0764 | 3.452 | 0.033803 | 0.0068819 | 0.39707 | -0.037393 | -0.025153 | -0.03708 | 0.4947 | -0.030409 | 0.069078 | 0.037055 | 0.019519 | 0.073595 | 0.10071 | 0.073242 | -0.23804 | -0.5722 | 0.16022 | -0.68207 | -0.83313 | 0.086975 | 13.8657 | -0.059509 | 122.2595 | 122.1634 | -0.76446 | -0.75989 | -0.032044 | -0.18311 | -121.9162 | 0.72327 | 0.077819 | 0.26093 | -121.9757 | -0.11444 | -0.10986 | 0.18311 | 0.737 | 0.59052 | 0.70038 | 0.086975 | 0.81024 | 0.75073 | 0.41199 | -122.9095 | 122.9095 | 122.8134 | 14.5157 | -122.8363
1276.6406 | 122.9233 | -0.75989 | 121.9757 | 0.00352 | 0.018849 | 0.029312 | 0.36609 | -0.038461 | -0.03797 | -0.048829 | 0.12849 | -0.038954 | 0.046647 | 0.040259 | 0.025928 | 0.075732 | 0.064087 | 0.10986 | -0.20599 | -0.6546 | 0.21515 | -0.76446 | -0.91553 | 0 | 13.8611 | -0.13275 | 122.1634 | 122.049 | -0.85144 | -0.86517 | -0.004577 | -0.15564 | -121.7606 | 0.86975 | 0.10529 | 0.26092 | -121.9116 | -0.091552 | -0.10528 | 0.18768 | 0.75989 | 0.62714 | 0.73242 | 0.073242 | 0.97504 | 0.82398 | 0.55389 | -122.8912 | 122.9233 | 122.8088 | 14.621 | -122.8409
1277.6406 | 122.8683 | -0.6546 | 122.1268 | -0.19484 | 0.00069119 | 0.012222 | 0.36289 | -0.045938 | -0.034766 | -0.046693 | 0.082718 | -0.042159 | 0.037034 | 0.041327 | 0.029132 | 0.08214 | 0.07782 | 0.13733 | -0.33417 | -0.44861 | 0.19684 | -0.66376 | -0.78278 | 0.086975 | 13.8931 | -0.032043 | 122.319 | 122.1863 | -0.73242 | -0.75073 | -0.009155 | -0.12817 | -121.9299 | 0.79193 | 0.20599 | 0.33417 | -122.0489 | -0.07782 | -0.09613 | 0.19226 | 0.74158 | 0.62256 | 0.71869 | 0.059509 | 0.85144 | 0.73242 | 0.32044 | -122.9095 | 122.9736 | 122.8409 | 14.5477 | -122.8775
1278.6406 | 122.8409 | -0.63171 | 122.1039 | 0.69017 | -0.0078538 | 0.011154 | 0.37784 | -0.039529 | -0.025153 | -0.044557 | 0.15901 | -0.045363 | 0.05092 | 0.02851 | 0.019519 | 0.08214 | 0.022888 | 0.086975 | -0.22888 | -0.54932 | 0.19684 | -0.65002 | -0.80109 | 0.10071 | 13.9343 | -0.032043 | 122.3007 | 122.2092 | -0.72784 | -0.75989 | -0.01831 | -0.16937 | -121.907 | 0.71869 | 0.082398 | 0.25177 | -122.081 | -0.09613 | -0.12817 | 0.19684 | 0.73242 | 0.59967 | 0.72784 | 0.10528 | 0.82855 | 0.6546 | 0.40283 | -122.905 | 122.9324 | 122.8409 | 14.566 | -122.8638
1279.6406 | 122.8363 | -0.62714 | 122.0993 | 0.034038 | -0.0099898 | 0.014358 | 0.36289 | -0.043802 | -0.020881 | -0.040284 | 0.082718 | -0.029341 | 0.061601 | 0.057349 | 0.0099061 | 0.074663 | 0.064087 | 0.1236 | -0.18768 | -0.10986 | 0.21973 | -0.62714 | -0.76446 | 0.13733 | 14.0259 | -0.073242 | 122.3099 | 122.2092 | -0.71869 | -0.737 | 0 | -0.13733 | -121.8796 | 0.75073 | 0.51727 | 0.6546 | -122.0352 | -0.091553 | -0.10986 | 0.21057 | 0.76447 | 0.55389 | 0.66376 | 0.10986 | 0.84686 | 0.69122 | 0.43945 | -122.8638 | 122.937 | 122.8363 | 14.653 | -122.8363
1280.6406 | 122.8317 | -0.65002 | 122.1405 | -0.2864 | 0.0038952 | 0.018631 | 0.36716 | -0.029916 | -0.014472 | -0.027467 | -0.26824 | -0.036818 | 0.03917 | 0.041327 | 0.023792 | 0.061846 | 0.059509 | 0.10529 | -0.21973 | -0.050354 | 0.2243 | -0.65918 | -0.81024 | 0.068665 | 14.2868 | -0.19226 | 122.3282 | 122.2092 | -0.73242 | -0.77362 | -0.009156 | -0.16022 | -121.9162 | 0.75531 | 0.59967 | 0.75989 | -122.081 | -0.082398 | -0.1236 | 0.18768 | 0.71869 | 0.45776 | 0.58136 | 0.068664 | 0.87433 | 0.70953 | 0.4303 | -122.9507 | 122.9782 | 122.8592 | 14.9368 | -122.9141
1281.6406 | 122.7768 | -0.68665 | 122.0993 | -0.088033 | -0.0046498 | 0.0015409 | 0.37891 | -0.03312 | -0.013404 | -0.039216 | -0.28349 | -0.042159 | 0.043443 | 0.030646 | 0.020587 | 0.071459 | 0.082397 | 0.15106 | -0.17395 | -0.091553 | 0.19684 | -0.66376 | -0.81024 | 0.09613 | 14.9094 | -0.1236 | 122.2733 | 122.1771 | -0.77362 | -0.79193 | 0.022889 | -0.1236 | -121.9025 | 0.83771 | 0.59509 | 0.71869 | -122.0169 | -0.086975 | -0.10529 | 0.17395 | 0.78278 | 0.56305 | 0.66834 | 0.07782 | 0.88348 | 0.76904 | 0.5127 | -122.9095 | 122.9599 | 122.8638 | 15.596 | -122.8912
1282.6406 | 122.7814 | -0.68665 | 122.0718 | 0.034038 | 0.022053 | -0.0016631 | 0.38745 | -0.036325 | 0.017572 | -0.024263 | -0.29875 | -0.026137 | 0.061601 | 0.037055 | 0.022724 | 0.046892 | 0.073242 | 0.059509 | -0.27924 | -0.61798 | 0.22888 | -0.76446 | -0.89722 | 0.19226 | 14.4516 | -0.14191 | 122.3373 | 122.1817 | -0.79651 | -0.81482 | -0.077819 | -0.21057 | -121.843 | 0.74616 | 0.068665 | 0.27924 | -121.9986 | -0.10986 | -0.12817 | 0.2655 | 0.87891 | 0.54474 | 0.67291 | 0.10986 | 0.91553 | 0.75989 | 0.40741 | -122.9691 | 123.024 | 122.8683 | 15.1382 | -122.8867
1283.6406 | 122.7905 | -0.58136 | 122.2458 | -0.22536 | -0.0099898 | -0.00059506 | 0.37357 | -0.041665 | -0.016608 | -0.023195 | -0.31401 | -0.037886 | 0.061601 | 0.047736 | 0.017383 | 0.066119 | 0.027466 | 0.1236 | -0.1831 | -0.036621 | 0.19684 | -0.54932 | -0.67749 | 0.13275 | 14.6118 | -0.050354 | 122.4335 | 122.3099 | -0.64087 | -0.66834 | 0.032044 | -0.09613 | -122.049 | 0.70496 | 0.54474 | 0.64087 | -122.2183 | -0.059509 | -0.086975 | 0.18768 | 0.71411 | 0.53101 | 0.61798 | 0.064086 | 0.7782 | 0.60883 | 0.39826 | -122.9233 | 123.0148 | 122.8912 | 15.1932 | -122.9141
1284.6406 | 105.4871 | 0.022888 | 122.1451 | -0.10329 | 0.042347 | 0.012222 | 0.38532 | -0.042733 | 0.011163 | -0.021058 | -0.23772 | -0.022933 | 0.076554 | 0.038123 | 0.025928 | 0.056505 | 0.036621 | 0.064087 | -0.25635 | -0.082397 | 0.2243 | -0.66376 | -0.82398 | 0.054932 | 14.0945 | -0.2243 | 122.3236 | 122.2092 | -0.75073 | -0.7782 | -0.68665 | -0.84686 | -121.9208 | 0.041199 | -0.10528 | 0.74158 | -122.1085 | -0.77362 | -0.80109 | 0.17853 | 0.032044 | -0.24719 | 0.55389 | 0.064086 | 0.20142 | 0.013733 | -0.27924 | -122.9691 | 122.3007 | 122.1863 | 14.0717 | -122.9233
1285.6406 | 122.9416 | -0.54474 | 105.6793 | -0.22536 | 0.025258 | 0.0079499 | 0.36823 | -0.025644 | -0.026221 | -0.029603 | -0.085129 | -0.037886 | 0.043443 | 0.034919 | 0.025928 | 0.070391 | 0.018311 | 0.10529 | -0.22888 | -0.31128 | 0.21515 | -0.69122 | -0.85144 | -0.022888 | 14.1541 | -0.2243 | 122.2778 | 122.1863 | -0.81482 | -0.82398 | -0.14648 | -0.3067 | -105.4642 | 0.65002 | 0.23346 | 0.54016 | -105.661 | -0.27008 | -0.27924 | 16.5985 | 0.52185 | 0.32043 | 0.59967 | 16.507 | 0.75989 | 0.56305 | 0.31586 | -106.5308 | 122.8226 | 122.731 | 14.6988 | -106.5033
1286.6406 | 93.9331 | 0.091553 | 92.6605 | 0.049296 | 0.055165 | -0.00059506 | 0.3725 | -0.038461 | 0.0047541 | -0.024263 | -0.11565 | -0.030409 | 0.045579 | 0.029578 | 0.021655 | 0.060778 | 0.050354 | 0.050354 | -0.25635 | -0.1831 | 0.23346 | -0.68665 | -0.83771 | 0.036621 | 14.1907 | -0.2243 | 122.3236 | 122.2183 | -0.78735 | -0.80109 | -0.7782 | -0.92926 | -92.4271 | -0.041199 | -0.27466 | 0.6546 | -92.6102 | -0.87891 | -0.89264 | 29.6631 | -0.054932 | -0.31586 | 0.57678 | 29.5578 | 0.14191 | -0.041199 | -0.3479 | -93.4982 | 122.2321 | 122.1268 | 14.0991 | -93.4616
1287.6562 | 122.2458 | -0.79193 | 122.0261 | 0.049296 | 0.00069119 | 0.027176 | 0.36502 | -0.037393 | -0.050788 | -0.040284 | 0.12849 | -0.045363 | 0.026353 | 0.039191 | 0.018451 | 0.077868 | 0.054932 | 0.15106 | -0.18768 | -0.65002 | 0.21057 | -0.78278 | -0.92468 | -0.036621 | 14.0076 | -0.15564 | 122.1771 | 122.049 | -0.88806 | -0.91553 | 0.009155 | -0.13275 | -121.8155 | 0.94299 | 0.14191 | 0.27466 | -121.9711 | -0.096131 | -0.1236 | 0.15106 | 0.75531 | 0.63629 | 0.75989 | 0.022888 | 1.0025 | 0.84686 | 0.60425 | -122.9507 | 122.9691 | 122.8409 | 14.7995 | -122.9416
1288.7031 | 122.3785 | -0.77362 | 121.5317 | 0.52232 | 0.031666 | 0.0058129 | 0.3757 | -0.054483 | -0.030494 | -0.027467 | 0.44893 | -0.033614 | 0.047715 | 0.035987 | 0.01311 | 0.08214 | 0.054932 | 0.13275 | -0.23346 | -0.70038 | 0.19226 | -0.7782 | -0.89722 | -0.054932 | 13.6047 | -0.18768 | 122.2 | 122.0901 | -0.85602 | -0.88348 | -0.004577 | -0.1236 | -121.3394 | 0.90637 | 0.073243 | 0.19684 | -121.4767 | -0.082397 | -0.10986 | 0.66833 | 0.71869 | 0.58594 | 0.6958 | 0.55847 | 0.96588 | 0.82855 | 0.54016 | -122.4289 | 122.9736 | 122.8638 | 14.3784 | -122.4152
1289.6406 | 104.2236 | -0.90179 | 93.2968 | 0.079814 | 0.045552 | 0.014358 | 0.38532 | -0.037393 | 0.0058221 | -0.026399 | -0.34453 | -0.024001 | 0.051988 | 0.042396 | 0.037677 | 0.061846 | 0.082397 | 0.050354 | -0.28839 | -0.64545 | 0.23346 | -0.73242 | -0.87891 | -0.041199 | 13.298 | -0.1831 | 122.2549 | 122.1359 | -0.83771 | -0.85602 | 0.16937 | 0.022888 | -93.0634 | 0.95215 | 0.25635 | 0.23346 | -93.2144 | 0.064086 | 0.045776 | 28.9581 | 0.86059 | 0.71869 | 0.67291 | 28.8391 | 1.1353 | 0.98419 | 0.6134 | -94.1757 | 123.1567 | 123.0377 | 14.1998 | -94.1528
1290.6406 | 121.3577 | -0.87433 | 122.0535 | 0.47654 | 0.059437 | 0.014358 | 0.37143 | -0.028848 | 0.0047541 | -0.023195 | -3.5184 | -0.022933 | 0.049852 | 0.033851 | 0.031268 | 0.074663 | 0.004578 | -0.027466 | -0.3479 | -0.68665 | 0.23346 | -0.72784 | -0.88348 | -0.091553 | 13.623 | -0.20142 | 122.2778 | 122.1588 | -0.82855 | -0.85144 | 0.14648 | -0.009155 | -121.8201 | 0.84686 | 0.18768 | 0.19684 | -122.049 | 0.045777 | 0.022889 | 0.2243 | 0.78278 | 0.67291 | 0.65002 | 0.10528 | 1.1078 | 0.87891 | 0.52643 | -122.937 | 123.1522 | 123.0331 | 14.4974 | -122.905
1291.6406 | 109.9915 | -0.94299 | 100.9232 | 0.24766 | 0.044484 | 0.0036769 | 0.37677 | -0.032052 | 0.0047541 | -0.021058 | 0.021682 | -0.025069 | 0.055192 | 0.047736 | 0.034473 | 0.070391 | -0.032043 | -0.027466 | -0.3479 | -0.68207 | 0.22888 | -0.75073 | -0.88348 | -0.10529 | 13.298 | -0.23804 | 122.3007 | 122.1725 | -0.84228 | -0.84228 | 0.19226 | 0.059509 | -100.6943 | 0.91553 | 0.26092 | 0.20142 | -100.9552 | 0.10071 | 0.10071 | 21.3776 | 0.83771 | 0.70496 | 0.60425 | 21.2494 | 1.1719 | 0.91095 | 0.59509 | -101.8066 | 123.2437 | 123.1155 | 14.241 | -101.7654
1292.6406 | 122.2641 | -0.70038 | 121.344 | 0.034038 | 0.0060322 | 0.029312 | 0.37357 | -0.02778 | -0.044379 | -0.033876 | -0.29875 | -0.036818 | 0.038102 | 0.025306 | 0.018451 | 0.084276 | 0.045776 | 0.16937 | -0.18768 | -0.60425 | 0.21057 | -0.6958 | -0.83771 | 0.018311 | 13.472 | -0.032043 | 122.2366 | 122.1497 | -0.78278 | -0.80109 | 0.004577 | -0.13733 | -121.1334 | 0.86975 | 0.09613 | 0.23346 | -121.2982 | -0.082398 | -0.10071 | 0.89264 | 0.71869 | 0.66833 | 0.76904 | 0.80566 | 0.91095 | 0.74615 | 0.51269 | -122.1817 | 122.937 | 122.85 | 14.1724 | -122.1451
1293.6406 | 105.4688 | -0.99792 | 93.457 | 0.2324 | 0.042347 | 0.0036769 | 0.38959 | -0.034188 | 0.0047541 | -0.031739 | -0.024094 | -0.025069 | 0.058397 | 0.042396 | 0.029132 | 0.060778 | 0.013733 | 0.022888 | -0.3067 | -0.68207 | 0.20599 | -0.77362 | -0.92926 | -0.10529 | 13.028 | -0.23346 | 122.2641 | 122.1359 | -0.85602 | -0.87891 | 0.2243 | 0.068665 | -93.251 | 1.0208 | 0.31586 | 0.24719 | -93.4433 | 0.14191 | 0.11902 | 28.8071 | 0.89264 | 0.76447 | 0.64545 | 28.6789 | 1.2039 | 1.0117 | 0.69122 | -94.3863 | 123.262 | 123.1338 | 14.0259 | -94.3359
1294.6406 | 122.8226 | -0.53558 | 121.431 | 0.78172 | 0.041279 | 0.0079499 | 0.38745 | -0.054483 | 0.0015501 | -0.029603 | 0.3116 | -0.033614 | 0.043443 | 0.043464 | 0.0302 | 0.075732 | 0.013733 | -0.050354 | -0.35248 | -0.69122 | 0.23346 | -0.72784 | -0.87433 | -0.073242 | 13.2248 | -0.19684 | 122.3007 | 122.1634 | -0.82855 | -0.84686 | -0.19226 | -0.33875 | -121.1975 | 0.48523 | -0.15564 | 0.18311 | -121.4172 | -0.29297 | -0.31128 | 0.86975 | 0.46234 | 0.33875 | 0.65003 | 0.73242 | 0.76904 | 0.54932 | 0.18311 | -122.3053 | 122.8363 | 122.699 | 13.7604 | -122.2778
1295.6406 | 122.2916 | -0.52643 | 118.6478 | 0.61387 | 0.028462 | -0.0048681 | 0.38104 | -0.032052 | -0.0069949 | -0.026399 | 0.35738 | -0.027205 | 0.053056 | 0.041327 | 0.022724 | 0.078936 | -0.004578 | 0.004578 | -0.31586 | -0.67749 | 0.22888 | -0.74616 | -0.88348 | -0.027466 | 13.7009 | -0.16479 | 122.2961 | 122.1771 | -0.82398 | -0.83313 | -0.21973 | -0.35706 | -118.4189 | 0.53101 | -0.15106 | 0.20599 | -118.6523 | -0.29755 | -0.3067 | 3.6484 | 0.49896 | 0.36163 | 0.66834 | 3.5294 | 0.75531 | 0.52185 | 0.21057 | -119.5312 | 122.8226 | 122.7036 | 14.2273 | -119.4809
1296.6406 | 122.4655 | -0.84228 | 121.2296 | 0.29344 | -0.0046498 | 0.0058129 | 0.35648 | -0.043802 | -0.041175 | -0.036012 | 0.90669 | -0.032546 | 0.048783 | 0.024238 | 0.012042 | 0.086413 | 0 | 0.045776 | -0.26093 | -0.74158 | 0.19226 | -0.82398 | -0.97961 | -0.16022 | 13.9435 | -0.24261 | 122.1222 | 122.0581 | -0.93384 | -0.9613 | 0.01831 | -0.13733 | -121.0373 | 0.88806 | 0.10071 | 0.23804 | -121.2296 | -0.091553 | -0.11902 | 0.89264 | 0.68207 | 0.59967 | 0.71869 | 0.82855 | 1.0345 | 0.84228 | 0.58136 | -122.2092 | 122.9645 | 122.9004 | 14.7858 | -122.1909
1297.6406 | 122.4747 | -0.72784 | 121.3898 | 0.29344 | -0.014263 | 0.018631 | 0.36182 | -0.037393 | -0.036902 | -0.045625 | 0.35738 | -0.041091 | 0.042375 | 0.035987 | 0.015247 | 0.074663 | 0.009155 | 0.07782 | -0.25177 | -0.64545 | 0.21057 | -0.72327 | -0.8606 | -0.059509 | 13.8886 | -0.1236 | 122.2687 | 122.1817 | -0.81024 | -0.83313 | 0.004577 | -0.13275 | -121.1792 | 0.80566 | 0.082397 | 0.21515 | -121.3806 | -0.082398 | -0.10529 | 0.87891 | 0.66834 | 0.60425 | 0.70953 | 0.79193 | 0.93841 | 0.737 | 0.47607 | -122.2504 | 122.9965 | 122.9095 | 14.6164 | -122.2229
1298.6406 | 122.4701 | -0.71869 | 121.2845 | 0.4918 | 0.013508 | 0.011154 | 0.3693 | -0.039529 | -0.033698 | -0.041353 | 0.28108 | -0.044295 | 0.044511 | 0.025306 | 0.020587 | 0.073595 | 0.032043 | 0.064087 | -0.24261 | -0.63629 | 0.20599 | -0.70953 | -0.83771 | -0.027466 | 13.916 | -0.11902 | 122.2733 | 122.1725 | -0.81482 | -0.8194 | 0.009155 | -0.11902 | -121.0785 | 0.78278 | 0.082397 | 0.20142 | -121.2524 | -0.09613 | -0.10071 | 0.98877 | 0.69122 | 0.59967 | 0.70038 | 0.88806 | 0.92468 | 0.75073 | 0.47607 | -122.1222 | 122.9919 | 122.8912 | 14.6347 | -122.1039
1299.6406 | 122.5021 | -0.6958 | 121.3943 | 0.55284 | 0.0081682 | 0.010086 | 0.3757 | -0.030984 | -0.024085 | -0.040284 | 0.26582 | -0.031478 | 0.03917 | 0.030646 | 0.019519 | 0.081072 | 0.059509 | 0.082397 | -0.2243 | -0.61798 | 0.20142 | -0.6958 | -0.84228 | 0.004578 | 14.0991 | -0.13275 | 122.2824 | 122.1497 | -0.80109 | -0.83313 | 0 | -0.14648 | -121.1929 | 0.7782 | 0.07782 | 0.2243 | -121.3348 | -0.10528 | -0.13733 | 0.88806 | 0.70038 | 0.56305 | 0.70038 | 0.75531 | 0.89722 | 0.75531 | 0.4715 | -122.2366 | 122.9782 | 122.8455 | 14.7949 | -122.2275
1300.6406 | 122.4747 | -0.68665 | 121.4951 | 0.18663 | -0.011058 | 0.017563 | 0.36716 | -0.037393 | -0.023017 | -0.050966 | -0.0088351 | -0.033614 | 0.040239 | 0.044532 | 0.016315 | 0.086413 | 0.068665 | 0.1236 | -0.20599 | -0.60883 | 0.2243 | -0.70953 | -0.82398 | 0.018311 | 13.8748 | -0.045776 | 122.2549 | 122.1634 | -0.78735 | -0.79193 | -0.022888 | -0.13733 | -121.2708 | 0.81024 | 0.07782 | 0.21515 | -121.4264 | -0.10071 | -0.10529 | 0.75989 | 0.70496 | 0.64087 | 0.74616 | 0.66833 | 0.91095 | 0.75531 | 0.48065 | -122.319 | 122.9416 | 122.85 | 14.5615 | -122.287
1301.6406 | 122.5433 | -0.6958 | 121.2936 | 0.32395 | 0.0028272 | 0.016495 | 0.37036 | -0.036325 | -0.019813 | -0.029603 | 0.036941 | -0.042159 | 0.054124 | 0.030646 | 0.016315 | 0.088549 | 0.041199 | 0.09613 | -0.23346 | -0.60425 | 0.20599 | -0.71411 | -0.85144 | -0.022888 | 14.1541 | -0.09613 | 122.2916 | 122.1817 | -0.79193 | -0.79651 | -0.01831 | -0.15564 | -121.0876 | 0.79193 | 0.091553 | 0.24719 | -121.2524 | -0.09613 | -0.10071 | 0.99793 | 0.67291 | 0.59967 | 0.70038 | 0.88806 | 0.9018 | 0.737 | 0.46234 | -122.1451 | 122.9874 | 122.8775 | 14.8499 | -122.0901
1302.6406 | 119.6777 | -0.9201 | 107.0023 | -0.51528 | 0.027394 | -0.0048681 | 0.38959 | -0.038461 | 0.0036861 | -0.031739 | -0.42082 | -0.037886 | 0.060533 | 0.033851 | 0.021655 | 0.061846 | 0.032043 | -0.009155 | -0.3067 | -0.70038 | 0.24261 | -0.77362 | -0.91095 | -0.14191 | 14.0076 | -0.26093 | 122.2916 | 122.1405 | -0.86517 | -0.87433 | 0.14648 | 0.009155 | -106.7596 | 0.91095 | 0.21973 | 0.21057 | -106.9702 | 0.054932 | 0.045776 | 15.2893 | 0.7782 | 0.65918 | 0.6134 | 15.1382 | 1.1627 | 0.95215 | 0.6134 | -107.9132 | 123.2117 | 123.0606 | 14.9277 | -107.8766
1303.6406 | 122.6852 | -0.78735 | 121.8887 | 0.24766 | -0.0014448 | 0.022903 | 0.38318 | -0.039529 | -0.034766 | -0.027467 | 0.0522 | -0.040022 | 0.037034 | 0.035987 | 0.0099061 | 0.084276 | 0.004578 | 0.086975 | -0.23346 | -0.70953 | 0.2243 | -0.80109 | -0.9613 | -0.14648 | 14.2181 | -0.19684 | 122.1542 | 122.0673 | -0.89722 | -0.91095 | -0.013732 | -0.17395 | -121.6644 | 0.87433 | 0.07782 | 0.25177 | -121.8842 | -0.10986 | -0.1236 | 0.2655 | 0.64087 | 0.59052 | 0.71411 | 0.17853 | 1.0117 | 0.79193 | 0.5539 | -122.85 | 122.9416 | 122.8546 | 15.0055 | -122.7997
1304.6406 | 122.2733 | -0.84686 | 121.3989 | -0.2101 | 0.0028272 | 0.015426 | 0.37677 | -0.032052 | -0.012336 | -0.033876 | -0.40556 | -0.036818 | 0.046647 | 0.031714 | 0.026996 | 0.068255 | 0.032043 | 0.073242 | -0.25177 | -0.72327 | 0.21057 | -0.84686 | -0.97046 | -0.18768 | 13.6826 | -0.28381 | 122.2092 | 122.0627 | -0.93842 | -0.95215 | 0 | -0.1236 | -121.1884 | 0.92011 | 0.1236 | 0.24719 | -121.3669 | -0.091553 | -0.10528 | 0.81024 | 0.65918 | 0.56305 | 0.66834 | 0.66376 | 1.0574 | 0.87891 | 0.59509 | -122.3694 | 123.056 | 122.9095 | 14.5294 | -122.3511
1305.6406 | 122.7356 | -0.79193 | 121.8887 | 0.11033 | -0.0057178 | 0.021835 | 0.3757 | -0.028848 | -0.023017 | -0.032808 | -0.16142 | -0.040022 | 0.053056 | 0.033851 | 0.021655 | 0.078936 | 0.086975 | 0.17395 | -0.20599 | -0.68665 | 0.21057 | -0.78735 | -0.89722 | -0.068665 | 13.678 | -0.15106 | 122.168 | 122.0581 | -0.8606 | -0.91553 | 0.004577 | -0.10529 | -121.6782 | 0.96588 | 0.10529 | 0.21057 | -121.8018 | -0.068665 | -0.1236 | 0.27924 | 0.72327 | 0.64087 | 0.76446 | 0.16937 | 1.0025 | 0.87891 | 0.58594 | -122.7859 | 122.9599 | 122.85 | 14.4699 | -122.8043
1306.6406 | 122.3831 | -0.74616 | 121.3486 | -0.25588 | 0.020985 | 0.014358 | 0.37464 | -0.041665 | -0.012336 | -0.031739 | -0.29875 | -0.036818 | 0.047715 | 0.039191 | 0.0302 | 0.070391 | 0.022888 | 0.073242 | -0.24261 | -0.65002 | 0.21973 | -0.74616 | -0.89264 | -0.10986 | 13.4766 | -0.18768 | 122.2916 | 122.1771 | -0.85602 | -0.85602 | 0 | -0.14648 | -121.1288 | 0.8194 | 0.096131 | 0.24261 | -121.3257 | -0.10986 | -0.10986 | 0.94299 | 0.63629 | 0.55847 | 0.66833 | 0.82855 | 0.96588 | 0.76904 | 0.50354 | -122.2412 | 123.0377 | 122.9233 | 14.2227 | -122.2046
1307.6406 | 122.5296 | -0.71869 | 121.701 | -0.24062 | 0.038075 | 0.010086 | 0.37677 | -0.032052 | -0.025153 | -0.034944 | -0.40556 | -0.03575 | 0.051988 | 0.040259 | 0.016315 | 0.067187 | 0.045776 | 0.13275 | -0.22888 | -0.61798 | 0.21515 | -0.70953 | -0.86517 | -0.041199 | 13.8199 | -0.15106 | 122.3419 | 122.1725 | -0.81482 | -0.83771 | 0.009155 | -0.14648 | -121.4859 | 0.85144 | 0.10071 | 0.24719 | -121.6553 | -0.09613 | -0.11902 | 0.64087 | 0.67749 | 0.56763 | 0.68665 | 0.4715 | 0.93384 | 0.76447 | 0.48981 | -122.5662 | 123.0606 | 122.8912 | 14.5386 | -122.5388
1308.6406 | 117.6178 | -0.74616 | 121.669 | 0.12559 | 0.049824 | -0.0059361 | 0.38959 | -0.029916 | 0.011163 | -0.010377 | -1.8857 | -0.012251 | 0.054124 | 0.034919 | 0.031268 | 0.057574 | 0.059509 | 0.07782 | -0.27008 | -0.63171 | 0.22888 | -0.737 | -0.89722 | -0.041199 | 13.7878 | -0.16937 | 122.3328 | 122.1909 | -0.79651 | -0.81024 | 0.009155 | -0.15106 | -121.4401 | 0.82398 | 0.11444 | 0.2655 | -121.6095 | -0.050354 | -0.064087 | 0.66376 | 0.70496 | 0.57678 | 0.64087 | 0.52185 | 0.97504 | 0.80566 | 0.47607 | -122.5662 | 123.0789 | 122.937 | 14.534 | -122.4792
1309.6406 | 122.0764 | -0.74616 | 121.9162 | -0.13381 | 0.032734 | 0.0026089 | 0.37677 | -0.030984 | 0.0058221 | -0.010377 | -0.43608 | -0.027205 | 0.054124 | 0.044532 | 0.029132 | 0.056505 | 0 | 0.041199 | -0.28839 | -0.64545 | 0.23346 | -0.73242 | -0.89264 | -0.082397 | 13.5681 | -0.17853 | 122.319 | 122.1863 | -0.83313 | -0.85602 | 0.013733 | -0.14648 | -121.6827 | 0.78735 | 0.10071 | 0.24719 | -121.9162 | -0.086975 | -0.10986 | 0.40283 | 0.66376 | 0.56763 | 0.67749 | 0.27008 | 0.97961 | 0.74616 | 0.45776 | -122.8088 | 123.0652 | 122.9324 | 14.3143 | -122.7722
1310.6406 | 122.0078 | -0.75531 | 122.0993 | -0.11855 | 0.056233 | 0.00047294 | 0.37998 | -0.03312 | -0.014472 | -0.017854 | -0.37505 | -0.028273 | 0.058397 | 0.038123 | 0.035541 | 0.072527 | -0.027466 | 0 | -0.3067 | -0.65002 | 0.2243 | -0.74616 | -0.89264 | -0.10529 | 13.3026 | -0.19684 | 122.3236 | 122.2 | -0.84228 | -0.84228 | 0.009155 | -0.13733 | -121.875 | 0.75531 | 0.10529 | 0.24261 | -122.1268 | -0.086975 | -0.086975 | 0.2243 | 0.65002 | 0.55847 | 0.64545 | 0.10071 | 0.97961 | 0.72784 | 0.44861 | -122.9919 | 123.0789 | 122.9553 | 14.0579 | -122.9416
1311.6406 | 122.2137 | -0.76446 | 122.1222 | 3.2689 | 0.041279 | 0.019699 | 0.37464 | -0.039529 | -0.0069949 | -0.031739 | -0.25298 | -0.031478 | 0.047715 | 0.030646 | 0.032337 | 0.081072 | 0.004578 | 0.004578 | -0.31128 | -0.67291 | 0.25635 | -0.73242 | -0.89722 | -0.16479 | 13.3987 | -0.23346 | 122.3053 | 122.2046 | -0.85144 | -0.87433 | 0.032043 | -0.13275 | -121.8658 | 0.76904 | 0.091552 | 0.2243 | -122.1176 | -0.086975 | -0.10986 | 0.18311 | 0.59967 | 0.53101 | 0.64087 | 0.082398 | 1.0208 | 0.76904 | 0.45319 | -123.0194 | 123.0698 | 122.9691 | 14.1632 | -122.9965
1312.6406 | 122.4106 | -0.737 | 122.1222 | -4.4673 | 0.030598 | 0.0047449 | 0.38745 | -0.029916 | -0.01554 | -0.030671 | 0.20479 | -0.025069 | 0.061601 | 0.040259 | 0.025928 | 0.0768 | -0.064087 | 0.018311 | -0.33417 | -0.69122 | 0.25177 | -0.74616 | -0.87433 | -0.086975 | 13.504 | -0.18768 | 122.319 | 122.2 | -0.82855 | -0.84686 | -0.009155 | -0.13733 | -121.8704 | 0.75531 | 0.045777 | 0.18311 | -122.1863 | -0.091552 | -0.10986 | 0.19684 | 0.65002 | 0.54932 | 0.65918 | 0.07782 | 0.98877 | 0.67291 | 0.40283 | -122.9965 | 123.056 | 122.937 | 14.241 | -122.9691
1313.6406 | 121.9437 | -0.73242 | 121.994 | -0.13381 | 0.04662 | 0.0079499 | 0.37891 | -0.034188 | -0.00058594 | -0.016786 | -0.26824 | -0.024001 | 0.060533 | 0.034919 | 0.029132 | 0.072527 | 0.009155 | 0.027466 | -0.29755 | -0.63629 | 0.23346 | -0.73242 | -0.88806 | -0.082397 | 14.0762 | -0.14191 | 122.3282 | 122.2046 | -0.81482 | -0.83771 | 0 | -0.15564 | -121.7606 | 0.75989 | 0.09613 | 0.25177 | -121.9849 | -0.082397 | -0.10529 | 0.33417 | 0.65003 | 0.59052 | 0.6958 | 0.21057 | 0.96588 | 0.74158 | 0.43488 | -122.8821 | 123.0606 | 122.937 | 14.8087 | -122.8317
1314.6406 | 122.1176 | -0.71869 | 122.1313 | 0.14085 | 0.055165 | -0.013413 | 0.37891 | -0.028848 | -0.0027229 | -0.0093093 | -0.10039 | -0.027205 | 0.054124 | 0.049872 | 0.034473 | 0.080004 | 0.013733 | 0.082397 | -0.2655 | -0.58136 | 0.28839 | -0.68665 | -0.82855 | -0.068665 | 13.9252 | -0.19226 | 122.3099 | 122.2366 | -0.82855 | -0.84228 | 0.032043 | -0.10986 | -121.843 | 0.80109 | 0.13733 | 0.24719 | -122.1176 | -0.10986 | -0.1236 | 0.17853 | 0.65002 | 0.52643 | 0.65002 | 0.10528 | 1.0071 | 0.73242 | 0.45319 | -122.9599 | 123.0286 | 122.9553 | 14.6439 | -122.9736
1315.6406 | 122.0627 | -0.70038 | 122.1359 | 0.00352 | 0.047688 | -0.0070041 | 0.38104 | -0.040597 | -0.010199 | -0.01465 | -0.10039 | -0.032546 | 0.060533 | 0.039191 | 0.053699 | 0.075732 | 0.022888 | 0.036621 | -0.27008 | -0.61798 | 0.21057 | -0.737 | -0.89264 | -0.022888 | 14.3738 | -0.18768 | 122.3648 | 122.2733 | -0.75531 | -0.78735 | -0.036622 | -0.19226 | -121.9254 | 0.737 | 0.082397 | 0.27466 | -122.113 | -0.054932 | -0.086976 | 0.22888 | 0.67749 | 0.51269 | 0.59967 | 0.13733 | 0.91095 | 0.72327 | 0.4303 | -123.0286 | 123.0652 | 122.9736 | 15.0742 | -122.9233
1316.6406 | 122.8958 | -0.68665 | 122.0947 | 0.58335 | 0.025258 | 0.00047294 | 0.36502 | -0.03312 | -0.014472 | -0.028535 | 0.3116 | -0.026137 | 0.053056 | 0.026374 | 0.032337 | 0.086413 | 0.004578 | 0.041199 | -0.27008 | -0.62256 | 0.21973 | -0.70496 | -0.8606 | 0.004578 | 14.0259 | -0.091553 | 122.2824 | 122.1954 | -0.7782 | -0.81024 | -0.01831 | -0.17395 | -121.875 | 0.72784 | 0.064087 | 0.23804 | -122.0901 | -0.091552 | -0.1236 | 0.18768 | 0.69122 | 0.59509 | 0.71869 | 0.10071 | 0.90637 | 0.69122 | 0.41656 | -122.9553 | 122.9691 | 122.8821 | 14.7125 | -122.905
1317.6406 | 122.9187 | -0.69122 | 122.1176 | 0.18663 | 0.017781 | -0.21956 | 0.37143 | -0.049142 | -0.04972 | -0.042421 | 0.29634 | -0.040022 | 0.046647 | 0.039191 | 0.0088381 | 0.081072 | -0.009155 | 0.059509 | -0.22888 | -0.6134 | 0.20142 | -0.6958 | -0.85144 | -0.022888 | 13.5315 | -0.064087 | 122.3236 | 122.2321 | -0.76904 | -0.76904 | -0.004578 | -0.16022 | -121.9162 | 0.75073 | 0.07782 | 0.23804 | -122.1268 | -0.07782 | -0.07782 | 0.20599 | 0.66834 | 0.62714 | 0.70496 | 0.11444 | 0.89264 | 0.68207 | 0.46234 | -122.9691 | 123.0148 | 122.9233 | 14.2227 | -122.8867
1318.6406 | 122.6395 | -0.72784 | 121.7606 | 0.61387 | 0.040211 | 0.0047449 | 0.37357 | -0.028848 | -0.0037909 | -0.032808 | 0.14375 | -0.031478 | 0.045579 | 0.037055 | 0.035541 | 0.073595 | 0.050354 | 0.041199 | -0.27466 | -0.64545 | 0.20142 | -0.73242 | -0.90637 | -0.059509 | 13.9984 | -0.12817 | 122.2549 | 122.1542 | -0.8194 | -0.8606 | -0.004578 | -0.17853 | -121.5591 | 0.76904 | 0.082397 | 0.26092 | -121.7102 | -0.091553 | -0.13275 | 0.49438 | 0.66834 | 0.59967 | 0.73242 | 0.39368 | 0.92926 | 0.7782 | 0.45319 | -122.6669 | 122.9828 | 122.8821 | 14.7263 | -122.6212
1319.6406 | 122.1542 | -0.85144 | 121.6278 | 0.50706 | 0.043416 | 0.0058129 | 0.38852 | -0.023507 | 0.0047541 | -0.027467 | -0.31401 | -0.028273 | 0.071214 | 0.029578 | 0.0302 | 0.075732 | 0.17395 | -0.31586 | -0.46234 | -0.6958 | 0.23346 | -0.81024 | -0.95673 | -0.18768 | 13.8565 | -0.32044 | 122.2183 | 122.1588 | -0.92468 | -0.93842 | 0.041198 | -0.10529 | -121.3943 | 0.53558 | 0.15564 | 0.26092 | -121.4539 | -0.073243 | -0.086976 | 0.59051 | 0.66376 | 0.531 | 0.61798 | 0.531 | 1.0849 | 1.0254 | 0.3891 | -122.5845 | 123.0698 | 123.0103 | 14.7079 | -122.5662
1320.6406 | 122.8775 | -0.8194 | 121.962 | 0.40025 | -0.00037681 | 0.015426 | 0.35968 | -0.038461 | -0.03797 | -0.022126 | 0.3116 | -0.037886 | 0.042375 | 0.037055 | 0.017383 | 0.077868 | 0 | 0.041199 | -0.27466 | -0.75989 | 0.18768 | -0.81482 | -0.9613 | -0.14191 | 13.7009 | -0.23804 | 122.1863 | 122.0993 | -0.90179 | -0.92468 | 0.004578 | -0.14191 | -121.7743 | 0.8606 | 0.059509 | 0.20142 | -121.962 | -0.082397 | -0.10529 | 0.2243 | 0.67749 | 0.58136 | 0.68665 | 0.13733 | 1.0071 | 0.8194 | 0.54474 | -122.9233 | 123.0057 | 122.9187 | 14.5203 | -122.8867
1321.6406 | 122.7676 | -0.82398 | 121.4722 | 0.12559 | 0.02419 | -0.00059506 | 0.37036 | -0.032052 | 0.00048206 | -0.033876 | 0.38789 | -0.038954 | 0.053056 | 0.030646 | 0.021655 | 0.078936 | 0.09613 | 0.09613 | -0.25635 | -0.71411 | 0.17853 | -0.84228 | -0.9613 | -0.10986 | 13.8611 | -0.24719 | 122.1725 | 122.0627 | -0.94299 | -0.94299 | -0.01831 | -0.13733 | -121.2936 | 0.9201 | 0.10986 | 0.24719 | -121.376 | -0.11902 | -0.11902 | 0.70038 | 0.71411 | 0.57678 | 0.6958 | 0.59052 | 1.0025 | 0.9201 | 0.56763 | -122.4335 | 122.9965 | 122.8867 | 14.6851 | -122.4152
1322.6406 | 122.6944 | -0.81482 | 121.6461 | 0.079814 | -0.0089218 | 0.0090179 | 0.3693 | -0.042733 | -0.031562 | -0.030671 | 0.12849 | -0.041091 | 0.059465 | 0.031714 | 0.015247 | 0.068255 | 0.068665 | 0.10986 | -0.22888 | -0.74616 | 0.21057 | -0.8194 | -0.97046 | -0.091553 | 14.035 | -0.18768 | 122.1588 | 122.0993 | -0.93842 | -0.92926 | -0.004578 | -0.15564 | -121.4355 | 0.92468 | 0.068664 | 0.2243 | -121.5775 | -0.1236 | -0.11444 | 0.51269 | 0.72327 | 0.62714 | 0.74158 | 0.45319 | 1.0254 | 0.88348 | 0.58594 | -122.6166 | 122.9736 | 122.9141 | 14.8499 | -122.5754
1323.6406 | 122.9324 | -0.84228 | 121.4813 | -0.86623 | 0.01244 | 0.0079499 | 0.3725 | -0.03312 | -0.0027229 | -0.036012 | 0.34212 | -0.042159 | 0.059465 | 0.050941 | 0.020587 | 0.083208 | 0.064087 | 0.10071 | -0.23346 | -0.79651 | 0.18768 | -0.8606 | -1.0071 | -0.1236 | 13.6505 | -0.28381 | 122.1451 | 122.049 | -0.97046 | -0.97046 | -0.018311 | -0.1648 | -121.2936 | 0.94299 | 0.045776 | 0.21057 | -121.4172 | -0.12817 | -0.12817 | 0.66376 | 0.71869 | 0.55847 | 0.68665 | 0.56763 | 1.03 | 0.90637 | 0.60883 | -122.4884 | 122.9874 | 122.8912 | 14.4928 | -122.4518
1324.6406 | 122.9507 | -0.8606 | 121.5317 | -0.011739 | -0.0099898 | 0.014358 | 0.37998 | -0.03312 | -0.023017 | -0.050966 | 0.0522 | -0.027205 | 0.040239 | 0.018897 | 0.015247 | 0.073595 | 0.073242 | 0.11444 | -0.23346 | -0.75989 | 0.21515 | -0.84686 | -0.99792 | -0.091553 | 13.8062 | -0.21973 | 122.1497 | 122.0673 | -0.94299 | -0.94757 | 0.013733 | -0.13733 | -121.3165 | 0.97504 | 0.10071 | 0.23804 | -121.4584 | -0.082397 | -0.086975 | 0.61798 | 0.76904 | 0.64087 | 0.72784 | 0.53558 | 1.0757 | 0.93384 | 0.62714 | -122.5296 | 123.0103 | 122.9279 | 14.6667 | -122.4792
1325.6406 | 122.9279 | -0.84686 | 121.7422 | 0.21714 | -0.0046498 | 0.022903 | 0.3725 | -0.036325 | -0.03263 | -0.040284 | -0.024094 | -0.042159 | 0.031694 | 0.035987 | 0.020587 | 0.072527 | 0.050354 | 0.09613 | -0.24261 | -0.75531 | 0.22888 | -0.85602 | -0.98877 | -0.10529 | 13.7604 | -0.24261 | 122.168 | 122.0535 | -0.94299 | -0.9613 | -0.009155 | -0.14191 | -121.5134 | 0.94299 | 0.091553 | 0.23346 | -121.6919 | -0.09613 | -0.11444 | 0.42572 | 0.74158 | 0.60425 | 0.71869 | 0.31128 | 1.0757 | 0.89722 | 0.60425 | -122.731 | 123.0148 | 122.9004 | 14.6072 | -122.7036
1326.6406 | 122.9782 | -0.82398 | 121.6049 | 0.079814 | 0.0038952 | 0.0036769 | 0.36716 | -0.04487 | -0.025153 | -0.043489 | 0.021682 | -0.042159 | 0.043443 | 0.032783 | 0.022724 | 0.070391 | 0.07782 | 0.1236 | -0.21057 | -0.72327 | 0.20599 | -0.81482 | -0.97504 | -0.050354 | 13.8977 | -0.21057 | 122.1771 | 122.0764 | -0.91095 | -0.92926 | 0.009156 | -0.15106 | -121.3989 | 0.94757 | 0.10071 | 0.25177 | -121.5271 | -0.086975 | -0.10528 | 0.57221 | 0.77362 | 0.6134 | 0.71869 | 0.4715 | 1.03 | 0.9018 | 0.6134 | -122.58 | 123.0011 | 122.9004 | 14.7217 | -122.5342
1327.6406 | 122.9233 | -0.8606 | 121.7834 | 0.32395 | 0.0071002 | 0.021835 | 0.36182 | -0.03312 | -0.021949 | -0.033876 | 0.082718 | -0.040022 | 0.03917 | 0.043464 | 0.020587 | 0.073595 | 0.027466 | 0.07782 | -0.27008 | -0.74616 | 0.21057 | -0.8194 | -0.96588 | -0.15106 | 13.8153 | -0.26093 | 122.1634 | 122.0627 | -0.97504 | -0.96588 | 0.041199 | -0.10528 | -121.5729 | 0.93842 | 0.11444 | 0.21973 | -121.756 | -0.11444 | -0.10528 | 0.37994 | 0.70953 | 0.59967 | 0.70496 | 0.27924 | 1.0712 | 0.88806 | 0.59052 | -122.7493 | 123.024 | 122.9233 | 14.6759 | -122.7493
1328.6406 | 122.7814 | -0.82398 | 121.5729 | -0.2101 | 0.0028272 | 0.0079499 | 0.39386 | -0.029916 | -0.019813 | -0.038148 | -0.25298 | -0.030409 | 0.05092 | 0.037055 | 0.021655 | 0.071459 | 0.09613 | 0.15106 | -0.19226 | -0.68207 | 0.19226 | -0.81024 | -0.94757 | -0.032043 | 13.7329 | -0.20142 | 122.1909 | 122.0718 | -0.90179 | -0.92926 | 0.013733 | -0.1236 | -121.3806 | 0.97504 | 0.14191 | 0.2655 | -121.4767 | -0.077819 | -0.10528 | 0.61798 | 0.79193 | 0.62256 | 0.72784 | 0.49896 | 1.0162 | 0.9201 | 0.63171 | -122.5204 | 123.0148 | 122.8958 | 14.5569 | -122.5021
1329.6406 | 122.9187 | -0.78735 | 121.7834 | -0.16433 | 0.016713 | 0.015426 | 0.37143 | -0.035257 | -0.019813 | -0.022126 | 0.11323 | -0.037886 | 0.042375 | 0.032783 | 0.021655 | 0.072527 | 0.032043 | 0.13275 | -0.17853 | -0.65918 | 0.18768 | -0.80566 | -0.95215 | -0.027466 | 13.6368 | -0.18768 | 122.2458 | 122.1176 | -0.86517 | -0.90637 | -0.01831 | -0.16479 | -121.5958 | 0.9201 | 0.12817 | 0.29297 | -121.7514 | -0.077819 | -0.11902 | 0.46234 | 0.75989 | 0.59967 | 0.71869 | 0.33417 | 0.97504 | 0.8194 | 0.60883 | -122.7356 | 123.0331 | 122.905 | 14.4241 | -122.6898
1330.6406 | 122.8958 | -0.81024 | 122.0764 | -0.042256 | 0.022053 | 0.018631 | 0.37036 | -0.034188 | -0.016608 | -0.027467 | -0.37505 | -0.040022 | 0.057328 | 0.026374 | 0.028064 | 0.066119 | 0.059509 | 0.12817 | -0.20599 | -0.67749 | 0.2243 | -0.78735 | -0.94299 | -0.050354 | 13.4216 | -0.2243 | 122.2549 | 122.1313 | -0.89722 | -0.90179 | 0.022888 | -0.13275 | -121.8521 | 0.93842 | 0.13275 | 0.2655 | -122.0169 | -0.086975 | -0.091552 | 0.17853 | 0.75989 | 0.58594 | 0.67749 | 0.054932 | 1.0345 | 0.86975 | 0.60425 | -123.0194 | 123.0652 | 122.9416 | 14.2319 | -122.9782
1331.6406 | 122.9279 | -0.7782 | 122.081 | 4.7643 | 0.026326 | 0.026108 | 0.37036 | -0.023507 | -0.0080629 | -0.029603 | -0.14616 | -0.032546 | 0.042375 | 0.046668 | 0.023792 | 0.070391 | 0.10071 | 0.11902 | -0.21973 | -0.63171 | 0.18768 | -0.79193 | -0.93384 | -0.036621 | 13.06 | -0.1831 | 122.2595 | 122.1085 | -0.8606 | -0.86975 | -0.013733 | -0.15564 | -121.8933 | 0.89722 | 0.14648 | 0.30212 | -121.9803 | -0.082398 | -0.091553 | 0.17853 | 0.74158 | 0.59509 | 0.68665 | 0.027465 | 0.96588 | 0.87891 | 0.55847 | -123.0148 | 123.0377 | 122.8867 | 13.8382 | -122.9507
1332.6406 | 122.287 | -0.80109 | 121.8338 | -0.17959 | 0.039143 | 0.00047294 | 0.38425 | -0.025644 | 0.011163 | -0.018922 | -0.51238 | -0.022933 | 0.058397 | 0.022101 | 0.031268 | 0.06505 | -0.009155 | 0.027466 | -0.31586 | -0.72327 | 0.23346 | -0.81482 | -0.94757 | -0.073242 | 13.1882 | -0.24719 | 122.3007 | 122.1451 | -0.89264 | -0.90179 | -0.013733 | -0.14649 | -121.6003 | 0.82855 | 0.077819 | 0.2243 | -121.843 | -0.091553 | -0.10071 | 0.46692 | 0.72784 | 0.55389 | 0.6546 | 0.31128 | 1.0345 | 0.79193 | 0.48523 | -122.7814 | 123.1018 | 122.9462 | 13.9893 | -122.7356
1333.6406 | 122.5708 | -0.81024 | 122.081 | -0.042256 | 0.027394 | 0.0047449 | 0.38104 | -0.026712 | 0.0015501 | -0.022126 | -0.43608 | -0.028273 | 0.053056 | 0.030646 | 0.02486 | 0.06505 | -0.018311 | 0.018311 | -0.3067 | -0.71869 | 0.22888 | -0.82855 | -0.95673 | -0.11444 | 13.4995 | -0.27008 | 122.319 | 122.1497 | -0.90179 | -0.90179 | -0.01831 | -0.14648 | -121.8521 | 0.82855 | 0.091553 | 0.23804 | -122.0993 | -0.091552 | -0.091552 | 0.23804 | 0.6958 | 0.54016 | 0.63171 | 0.068664 | 1.0391 | 0.79193 | 0.50354 | -123.0377 | 123.1293 | 122.9599 | 14.3097 | -122.9828
1334.6406 | 122.3602 | -0.85144 | 122.0764 | 0.35447 | 0.047688 | 0.0058129 | 0.3725 | -0.045938 | 0.017572 | -0.021058 | -0.054612 | -0.020796 | 0.070146 | 0.033851 | 0.029132 | 0.072527 | -0.022888 | -0.013733 | -0.36621 | -0.77362 | 0.21515 | -0.84686 | -0.97961 | -0.14191 | 13.7421 | -0.33875 | 122.2595 | 122.1497 | -0.92468 | -0.95673 | 0.004577 | -0.12817 | -121.8613 | 0.83771 | 0.077819 | 0.20599 | -122.0993 | -0.073243 | -0.10529 | 0.18311 | 0.70953 | 0.51269 | 0.61798 | 0.073242 | 1.0666 | 0.82855 | 0.48523 | -123.056 | 123.111 | 123.0011 | 14.5935 | -123.0331
1335.6406 | 122.8363 | -0.84228 | 122.0261 | -0.2101 | 0.030598 | 0.0090179 | 0.37891 | -0.029916 | -0.023017 | -0.027467 | -0.42082 | -0.030409 | 0.043443 | 0.034919 | 0.040881 | 0.077868 | -0.032043 | 0.013733 | -0.33875 | -0.83313 | 0.2243 | -0.86975 | -1.0345 | -0.26093 | 13.9618 | -0.37994 | 122.2321 | 122.1313 | -0.94299 | -0.9613 | -0.027466 | -0.19226 | -121.8018 | 0.85602 | 0.009155 | 0.20142 | -122.0581 | -0.10071 | -0.11902 | 0.20599 | 0.58136 | 0.46234 | 0.58136 | 0.10529 | 1.0666 | 0.81024 | 0.50354 | -123.0606 | 123.0743 | 122.9736 | 14.8041 | -122.9874
1336.6562 | 122.9416 | -0.84686 | 121.994 | 0.064555 | -0.00037681 | -0.025162 | 0.36075 | -0.039529 | -0.03797 | -0.030671 | 0.18953 | -0.036818 | 0.043443 | 0.039191 | 0.014179 | 0.092821 | -0.050354 | 0.068665 | -0.27924 | -0.78735 | 0.17853 | -0.89722 | -1.0117 | -0.15106 | 13.9343 | -0.24261 | 122.1909 | 122.0764 | -0.94757 | -0.95673 | -0.050354 | -0.16479 | -121.8155 | 0.91553 | 0.059509 | 0.2243 | -122.0444 | -0.10071 | -0.10986 | 0.19684 | 0.6958 | 0.60425 | 0.71411 | 0.082397 | 1.0254 | 0.79651 | 0.56763 | -123.0057 | 123.0377 | 122.9233 | 14.7812 | -122.9507
1337.6406 | 122.9691 | -0.80109 | 122.0123 | 0.50706 | 0.035939 | 0.01329 | 0.37036 | -0.029916 | -0.018744 | -0.028535 | 0.35738 | -0.028273 | 0.055192 | 0.037055 | 0.033405 | 0.074663 | 0.027466 | 0.073242 | -0.30212 | -0.75989 | 0.19684 | -0.84228 | -1.0025 | -0.064087 | 13.3759 | -0.2243 | 122.2046 | 122.081 | -0.91095 | -0.93384 | -0.041199 | -0.20142 | -121.8155 | 0.87433 | 0.041198 | 0.24261 | -121.9849 | -0.10986 | -0.13275 | 0.19226 | 0.737 | 0.57678 | 0.70953 | 0.068665 | 0.99792 | 0.82855 | 0.49896 | -123.0148 | 123.0057 | 122.8821 | 14.1769 | -122.9462
1338.6406 | 122.4472 | -0.88348 | 121.7422 | 0.18663 | 0.057301 | 0.010086 | 0.37677 | -0.02778 | 0.013299 | -0.01465 | 0.0522 | -0.024001 | 0.055192 | 0.025306 | 0.029132 | 0.060778 | 0.013733 | 0.013733 | -0.34332 | -0.79651 | 0.21973 | -0.88348 | -1.0071 | -0.19226 | 13.1699 | -0.35706 | 122.2046 | 122.1176 | -0.96588 | -0.97961 | 0 | -0.1236 | -121.5225 | 0.89722 | 0.086975 | 0.21057 | -121.7285 | -0.082397 | -0.09613 | 0.46234 | 0.69122 | 0.52643 | 0.62256 | 0.37537 | 1.1032 | 0.89722 | 0.54016 | -122.7493 | 123.0881 | 123.0011 | 14.0533 | -122.7219
1339.6406 | 122.5937 | -0.8606 | 122.0215 | -0.011739 | 0.037007 | -0.0016631 | 0.38211 | -0.035257 | 0.0079581 | -0.027467 | 0.021682 | -0.031478 | 0.051988 | 0.047736 | 0.032337 | 0.077868 | 0.059509 | 0.036621 | -0.31586 | -0.7782 | 0.25635 | -0.84228 | -0.98877 | -0.14648 | 12.7579 | -0.33875 | 122.2275 | 122.1405 | -0.93842 | -0.96588 | 0.018311 | -0.12817 | -121.7651 | 0.89722 | 0.082398 | 0.21057 | -121.962 | -0.07782 | -0.10528 | 0.20599 | 0.71411 | 0.52185 | 0.62714 | 0.11902 | 1.1169 | 0.92011 | 0.54474 | -123.0103 | 123.0881 | 123.0011 | 13.6185 | -122.9874
1340.6406 | 122.8683 | -0.84686 | 121.9116 | 0.79698 | 0.038075 | 0.0026089 | 0.36395 | -0.029916 | -0.016608 | -0.026399 | 0.46419 | -0.036818 | 0.045579 | 0.039191 | 0.0088381 | 0.074663 | 0.07782 | 0.10986 | -0.26093 | -0.73242 | 0.19684 | -0.8194 | -0.98419 | -0.068665 | 13.4537 | -0.21973 | 122.1909 | 122.0901 | -0.92926 | -0.95673 | 0.027466 | -0.13733 | -121.7148 | 0.95673 | 0.11444 | 0.25177 | -121.8338 | -0.082397 | -0.10986 | 0.27924 | 0.7782 | 0.62714 | 0.737 | 0.17853 | 1.0437 | 0.92468 | 0.58594 | -122.8958 | 123.0377 | 122.937 | 14.3005 | -122.8683
1341.6406 | 122.9507 | -0.82855 | 121.994 | 0.73594 | 0.014576 | 0.036789 | 0.36716 | -0.051278 | -0.048652 | -0.036012 | 0.2353 | -0.031478 | 0.026353 | 0.041327 | 0.01311 | 0.083208 | -0.013733 | 0.054932 | -0.28839 | -0.75989 | 0.15106 | -0.87433 | -1.0025 | -0.11444 | 12.5198 | -0.2243 | 122.2 | 122.1085 | -0.92926 | -0.93842 | -0.045777 | -0.17395 | -121.843 | 0.88348 | 0.068664 | 0.24261 | -122.0078 | -0.10071 | -0.10986 | 0.20599 | 0.71411 | 0.60425 | 0.71411 | 0.11444 | 0.97961 | 0.81482 | 0.54016 | -122.9965 | 123.0286 | 122.937 | 13.3484 | -122.9324
1342.6406 | 122.9141 | -0.83313 | 122.0078 | -0.13381 | 0.010304 | 0.0090179 | 0.36609 | -0.036325 | -0.030494 | -0.029603 | -0.14616 | -0.044295 | 0.045579 | 0.027442 | 0.020587 | 0.077868 | -0.12817 | 0.20142 | -0.16479 | -0.74158 | 0.19226 | -0.84686 | -0.99335 | -0.045776 | 13.2019 | -0.21057 | 122.2 | 122.1085 | -0.92926 | -0.92468 | -0.013733 | -0.16022 | -121.8155 | 1.0345 | 0.091553 | 0.25177 | -122.1359 | -0.09613 | -0.091553 | 0.19226 | 0.78735 | 0.62256 | 0.71411 | 0.10071 | 1.0254 | 0.70496 | 0.66834 | -123.0011 | 123.0331 | 122.9416 | 14.035 | -122.9324
1343.6406 | 122.9736 | -0.79193 | 122.0627 | 0.53758 | 0.035939 | 0.019699 | 0.39066 | -0.02778 | -0.0080629 | -0.030671 | 0.35738 | -0.028273 | 0.064805 | 0.02317 | 0.025928 | 0.067187 | 0.027466 | 0.018311 | -0.32501 | -0.737 | 0.22888 | -0.82398 | -0.95673 | -0.045776 | 12.3917 | -0.23804 | 122.287 | 122.1451 | -0.90637 | -0.92468 | -0.032044 | -0.16479 | -121.8338 | 0.81024 | 0.054931 | 0.21973 | -122.0352 | -0.11444 | -0.13275 | 0.2243 | 0.74616 | 0.55389 | 0.68665 | 0.082398 | 1.0208 | 0.8194 | 0.46692 | -123.0194 | 123.0789 | 122.937 | 13.1836 | -122.9874
1344.6406 | 122.8821 | -0.80566 | 122.0673 | 0.24766 | 0.017781 | 0.011154 | 0.36502 | -0.039529 | -0.040107 | -0.029603 | 0.22005 | -0.040022 | 0.043443 | 0.048804 | 0.022724 | 0.074663 | 0.018311 | 0.045776 | -0.27466 | -0.74616 | 0.19684 | -0.78735 | -0.94299 | -0.059509 | 12.2864 | -0.23346 | 122.2687 | 122.1588 | -0.89722 | -0.90637 | 0.01831 | -0.13733 | -121.8704 | 0.85144 | 0.059509 | 0.19684 | -122.049 | -0.091553 | -0.10071 | 0.20142 | 0.74616 | 0.57221 | 0.67291 | 0.091552 | 1.0025 | 0.82398 | 0.53101 | -123.0103 | 123.0743 | 122.9645 | 13.092 | -122.9736
1345.6406 | 122.9141 | -0.8194 | 121.9986 | 0.79698 | 0.041279 | 0.0036769 | 0.3757 | -0.023507 | -0.023017 | -0.029603 | 0.37263 | -0.026137 | 0.045579 | 0.038123 | 0.022724 | 0.069323 | 0.086975 | 0.10529 | -0.23804 | -0.75073 | 0.16937 | -0.82398 | -0.9613 | -0.032043 | 12.2864 | -0.21057 | 122.2137 | 122.1085 | -0.90179 | -0.92926 | -0.004578 | -0.14191 | -121.8292 | 0.92468 | 0.068665 | 0.21057 | -121.9116 | -0.082397 | -0.10986 | 0.21515 | 0.78735 | 0.60883 | 0.71869 | 0.10986 | 0.98877 | 0.90637 | 0.58136 | -122.9599 | 123.0331 | 122.9279 | 13.1058 | -122.9279
1346.6562 | 122.2916 | -0.84686 | 121.5042 | 0.095073 | 0.049824 | 0.0047449 | 0.38425 | -0.022439 | 0.0090271 | -0.025331 | -0.32927 | -0.032546 | 0.060533 | 0.033851 | 0.026996 | 0.047961 | 0.07782 | 0.036621 | -0.29755 | -0.75989 | 0.22888 | -0.85602 | -1.0117 | -0.082397 | 12.236 | -0.28839 | 122.2366 | 122.1451 | -0.94299 | -0.95673 | -0.009155 | -0.16479 | -121.2753 | 0.88348 | 0.086975 | 0.25177 | -121.4264 | -0.09613 | -0.10986 | 0.73242 | 0.76447 | 0.55847 | 0.66833 | 0.64087 | 1.0757 | 0.92468 | 0.54932 | -122.5159 | 123.0835 | 122.9919 | 13.0829 | -122.4609
1347.6406 | 122.9462 | -0.84686 | 122.0627 | -5.2608 | 0.01244 | -0.0091401 | 0.35861 | -0.038461 | -0.016608 | -0.030671 | -0.45134 | -0.037886 | 0.041307 | 0.050941 | 0.017383 | 0.074663 | -0.045776 | 0.16479 | -0.20599 | -0.74158 | 0.17853 | -0.84686 | -0.98419 | -0.064087 | 11.5448 | -0.21973 | 122.2321 | 122.1176 | -0.94757 | -0.95215 | 0 | -0.13733 | -121.8842 | 1.0117 | 0.10529 | 0.24261 | -122.1085 | -0.10071 | -0.10528 | 0.16937 | 0.78278 | 0.62714 | 0.73242 | 0.054932 | 1.0254 | 0.80109 | 0.64087 | -123.0469 | 123.0789 | 122.9645 | 12.3917 | -123.0148
1348.6406 | 122.9324 | -0.83313 | 122.0444 | 0.21714 | 0.01244 | 0.021835 | 0.37677 | -0.043802 | -0.034766 | -0.038148 | 0.021682 | -0.036818 | 0.044511 | 0.026374 | 0.015247 | 0.074663 | 0.022888 | 0.09613 | -0.24719 | -0.737 | 0.21515 | -0.83313 | -0.98419 | -0.054932 | 11.9522 | -0.21057 | 122.2183 | 122.1268 | -0.91095 | -0.93842 | 0 | -0.15106 | -121.8292 | 0.92926 | 0.09613 | 0.24719 | -122.0215 | -0.07782 | -0.10529 | 0.17395 | 0.7782 | 0.62256 | 0.72785 | 0.082397 | 1.0483 | 0.85602 | 0.58594 | -123.0286 | 123.0515 | 122.9599 | 12.7853 | -122.9828
1349.6406 | 122.9279 | -0.81024 | 122.0261 | 2.0024 | 0.0060322 | 0.01329 | 0.37036 | -0.042733 | -0.03263 | -0.030671 | 0.0064239 | -0.024001 | 0.03917 | 0.037055 | 0.010974 | 0.075732 | -0.004578 | 0.054932 | -0.27924 | -0.75073 | 0.16937 | -0.84228 | -0.99335 | -0.059509 | 10.9909 | -0.20142 | 122.2321 | 122.1359 | -0.91095 | -0.93384 | -0.032043 | -0.1831 | -121.8567 | 0.86517 | 0.05951 | 0.24262 | -122.0306 | -0.10071 | -0.1236 | 0.20599 | 0.75073 | 0.60883 | 0.73242 | 0.10986 | 0.97962 | 0.80566 | 0.53101 | -123.0194 | 123.0423 | 122.9462 | 11.8011 | -122.9599
1350.6406 | 122.85 | -0.85602 | 121.8063 | -0.30166 | 0.032734 | 0.01329 | 0.38318 | -0.032052 | 0.0015501 | -0.030671 | -0.39031 | -0.015456 | 0.062669 | 0.034919 | 0.015247 | 0.061846 | -0.022888 | 0.004578 | -0.32959 | -0.80109 | 0.24261 | -0.8606 | -0.99792 | -0.10986 | 10.7529 | -0.33875 | 122.2916 | 122.1542 | -0.9613 | -0.97961 | -0.004578 | -0.14191 | -121.5637 | 0.8606 | 0.054932 | 0.19684 | -121.8292 | -0.10529 | -0.1236 | 0.48523 | 0.74615 | 0.51727 | 0.64087 | 0.3479 | 1.0986 | 0.83313 | 0.52643 | -122.8043 | 123.1476 | 123.0103 | 11.6089 | -122.7859
1351.6406 | 122.4197 | -0.8606 | 122.0856 | 0.29344 | 0.055165 | -0.019821 | 0.39386 | -0.037393 | 0.017572 | -0.023195 | -0.0088351 | -0.030409 | 0.064805 | 0.044532 | 0.026996 | 0.063982 | -0.009155 | -0.004578 | -0.34332 | -0.78278 | 0.22888 | -0.85144 | -1.0025 | -0.10071 | 10.6567 | -0.36621 | 122.2595 | 122.168 | -0.94299 | -0.97046 | 0.009156 | -0.14191 | -121.8567 | 0.85602 | 0.07782 | 0.21973 | -122.0947 | -0.082397 | -0.10986 | 0.17395 | 0.75989 | 0.49439 | 0.60425 | 0.082398 | 1.0895 | 0.85144 | 0.51727 | -123.0881 | 123.1201 | 123.0286 | 11.5173 | -123.056
1352.6406 | 122.8455 | -0.85602 | 122.0718 | -0.22536 | 0.0049632 | 0.0079499 | 0.37357 | -0.032052 | -0.029426 | -0.031739 | -0.13091 | -0.036818 | 0.037034 | 0.046668 | 0.010974 | 0.073595 | -0.018311 | 0.050354 | -0.29297 | -0.75989 | 0.2243 | -0.85144 | -0.97961 | -0.10071 | 10.5515 | -0.3067 | 122.2824 | 122.1771 | -0.93842 | -0.94757 | 0.004578 | -0.1236 | -121.8475 | 0.90637 | 0.09613 | 0.21973 | -122.0901 | -0.082398 | -0.091553 | 0.21057 | 0.75531 | 0.54932 | 0.64087 | 0.10529 | 1.0803 | 0.83771 | 0.56305 | -123.0515 | 123.1384 | 123.0331 | 11.4075 | -123.0194
1353.6406 | 122.8912 | -0.83771 | 122.0993 | -0.24062 | 0.0049632 | 0.0079499 | 0.37036 | -0.037393 | -0.024085 | -0.036012 | -0.28349 | -0.024001 | 0.046647 | 0.033851 | 0.014179 | 0.078936 | 0 | 0.10986 | -0.25635 | -0.71869 | 0.21515 | -0.82398 | -0.97046 | -0.050354 | 10.9543 | -0.28839 | 122.2824 | 122.1771 | -0.92468 | -0.93842 | 0.013733 | -0.13275 | -121.8842 | 0.94757 | 0.11902 | 0.25177 | -122.0993 | -0.086975 | -0.10071 | 0.18311 | 0.78735 | 0.54932 | 0.65003 | 0.07782 | 1.0529 | 0.83771 | 0.58136 | -123.0698 | 123.1201 | 123.0148 | 11.792 | -123.0377
1354.6406 | 122.8638 | -0.8194 | 122.113 | -0.27114 | 0.018849 | 0.0079499 | 0.37784 | -0.030984 | -0.026221 | -0.03708 | -0.32927 | -0.030409 | 0.046647 | 0.029578 | 0.016315 | 0.05971 | 0.018311 | 0.10986 | -0.23804 | -0.6958 | 0.20599 | -0.80566 | -0.9613 | -0.059509 | 11.0687 | -0.25177 | 122.2961 | 122.1542 | -0.90179 | -0.9201 | 0.013733 | -0.14191 | -121.907 | 0.92926 | 0.1236 | 0.2655 | -122.0947 | -0.082397 | -0.10071 | 0.18311 | 0.75989 | 0.56763 | 0.66833 | 0.041199 | 1.0254 | 0.83771 | 0.58136 | -123.0743 | 123.1155 | 122.9736 | 11.8881 | -123.0331
1355.6406 | 122.8317 | -0.85144 | 122.0901 | -0.24062 | 0.033803 | 0.017563 | 0.37784 | -0.016031 | -0.014472 | -0.039216 | -0.45134 | -0.019728 | 0.031694 | 0.032783 | 0.023792 | 0.063982 | -0.022888 | 0.013733 | -0.33417 | -0.77362 | 0.2243 | -0.8606 | -0.97961 | -0.10071 | 10.2081 | -0.31128 | 122.2916 | 122.1359 | -0.93842 | -0.97504 | -0.009156 | -0.12817 | -121.8658 | 0.86517 | 0.077819 | 0.20599 | -122.113 | -0.086976 | -0.1236 | 0.20142 | 0.75073 | 0.54016 | 0.66376 | 0.045776 | 1.0757 | 0.82855 | 0.51727 | -123.0698 | 123.143 | 122.9874 | 11.0596 | -123.0652
1356.6406 | 122.9599 | -0.7782 | 122.0627 | 0.095073 | 0.027394 | 0.016495 | 0.38532 | -0.038461 | -0.010199 | -0.027467 | 0.34212 | -0.041091 | 0.060533 | 0.025306 | 0.022724 | 0.08214 | 0.064087 | 0.10986 | -0.23346 | -0.70038 | 0.17395 | -0.79193 | -0.92468 | 0.082397 | 10.3867 | -0.1831 | 122.2458 | 122.1497 | -0.87891 | -0.88806 | -0.013733 | -0.14649 | -121.8887 | 0.88806 | 0.07782 | 0.22431 | -121.9986 | -0.10071 | -0.10986 | 0.18311 | 0.86059 | 0.59509 | 0.70496 | 0.086975 | 0.95215 | 0.84228 | 0.54474 | -122.9874 | 123.024 | 122.9279 | 11.1649 | -122.9507
1357.6406 | 122.6303 | -0.81024 | 122.0627 | 0.14085 | 0.055165 | 0.0068819 | 0.39066 | -0.038461 | 0.013299 | -0.01999 | -0.039353 | -0.031478 | 0.059465 | 0.042396 | 0.029132 | 0.067187 | 0.054932 | 0.013733 | -0.32044 | -0.73242 | 0.21057 | -0.82398 | -0.9613 | -0.027466 | 10.1669 | -0.30212 | 122.3099 | 122.2183 | -0.91553 | -0.92926 | -0.013733 | -0.15106 | -121.8521 | 0.82398 | 0.07782 | 0.22888 | -122.0078 | -0.10528 | -0.11902 | 0.24719 | 0.78278 | 0.50812 | 0.62714 | 0.15564 | 1.0208 | 0.86517 | 0.48981 | -123.024 | 123.1201 | 123.0286 | 10.9772 | -122.9919
1358.6406 | 122.9141 | -0.81024 | 122.0901 | -0.19484 | 0.041279 | 0.0026089 | 0.38959 | -0.042733 | 0.0090271 | -0.018922 | 0.34212 | -0.014388 | 0.063737 | 0.038123 | 0.031268 | 0.081072 | -0.013733 | -0.018311 | -0.35248 | -0.74616 | 0.2243 | -0.81482 | -0.9613 | 0.14648 | 10.2493 | -0.25635 | 122.2916 | 122.1771 | -0.90637 | -0.89722 | -0.004577 | -0.15106 | -121.8658 | 0.79193 | 0.064087 | 0.21515 | -122.1039 | -0.09613 | -0.086975 | 0.20142 | 0.95673 | 0.55389 | 0.64087 | 0.086975 | 1.0345 | 0.79651 | 0.45776 | -123.0515 | 123.1018 | 122.9874 | 11.0596 | -122.9874
1359.6406 | 122.8317 | -0.81024 | 122.113 | 0.034038 | 0.041279 | -0.0048681 | 0.37677 | -0.03312 | 0.0079581 | -0.027467 | 0.0064239 | -0.020796 | 0.047715 | 0.026374 | 0.031268 | 0.075732 | 0.086975 | 0.26093 | -0.21515 | -0.62714 | 0.27466 | -0.75989 | -0.90179 | 0.59967 | 10.4141 | -0.27008 | 122.3236 | 122.2046 | -0.88348 | -0.90179 | 0.050354 | -0.091552 | -121.8384 | 1.0712 | 0.18311 | 0.27466 | -122.0261 | -0.073242 | -0.091552 | 0.21057 | 1.4099 | 0.54016 | 0.63171 | 0.091553 | 1.0849 | 0.89722 | 0.59509 | -123.0148 | 123.1338 | 123.0148 | 11.2244 | -123.0148
1360.6406 | 122.8683 | -0.81482 | 122.1039 | 0.29344 | 0.058369 | 0.0047449 | 0.36823 | -0.037393 | 0.0015501 | -0.028535 | 0.0064239 | -0.021865 | 0.049852 | 0.019965 | 0.028064 | 0.080004 | 0.013733 | 0.018311 | -0.32501 | -0.73242 | 0.20599 | -0.79651 | -0.9613 | 0.036621 | 10.817 | -0.3067 | 122.3328 | 122.2366 | -0.91095 | -0.92468 | 0.01831 | -0.14649 | -121.8979 | 0.83313 | 0.082397 | 0.22888 | -122.0901 | -0.096131 | -0.10986 | 0.22888 | 0.85144 | 0.50812 | 0.61798 | 0.13275 | 1.0208 | 0.82855 | 0.48981 | -123.0652 | 123.1476 | 123.0515 | 11.6318 | -123.0286
1361.6406 | 122.7859 | -0.79651 | 122.1268 | 0.52232 | 0.053029 | -0.0016631 | 0.37998 | -0.023507 | -0.0027229 | -0.012513 | 0.37263 | -0.031478 | 0.061601 | 0.02851 | 0.023792 | 0.0768 | -0.027466 | -0.050354 | -0.36621 | -0.74158 | 0.23346 | -0.80566 | -0.96588 | -0.050354 | 10.2859 | -0.31586 | 122.3373 | 122.2412 | -0.88806 | -0.90179 | -0.009155 | -0.16937 | -121.8933 | 0.74616 | 0.054932 | 0.2243 | -122.1542 | -0.091553 | -0.10528 | 0.21057 | 0.74616 | 0.48065 | 0.58594 | 0.11444 | 1.03 | 0.76904 | 0.4303 | -123.0927 | 123.1338 | 123.0377 | 11.0825 | -123.0286
1362.6406 | 122.9507 | -0.80109 | 122.0261 | -0.011739 | 0.022053 | 0.0090179 | 0.36395 | -0.034188 | -0.028357 | -0.039216 | 0.571 | -0.030409 | 0.05092 | 0.034919 | 0.021655 | 0.085345 | 0.013733 | 0.11444 | -0.25177 | -0.72784 | 0.19226 | -0.82398 | -0.95673 | -0.032043 | 9.4437 | -0.21057 | 122.2458 | 122.1313 | -0.92926 | -0.92926 | -0.022889 | -0.15564 | -121.8338 | 0.91553 | 0.073242 | 0.22888 | -122.0123 | -0.12817 | -0.12817 | 0.21973 | 0.76904 | 0.59051 | 0.71869 | 0.10529 | 0.99335 | 0.81482 | 0.54932 | -122.9828 | 123.0469 | 122.9324 | 10.2448 | -122.9553
1363.6406 | 122.8867 | -0.85602 | 122.0261 | 0.55284 | 0.06371 | -0.0080721 | 0.37784 | -0.036325 | -0.00058594 | -0.025331 | -1.1838 | -0.030409 | 0.065873 | 0.044532 | 0.026996 | 0.0768 | -0.004578 | -0.036621 | -0.26093 | -0.91095 | 0.24261 | -0.85144 | -0.99335 | -0.15564 | 10.2814 | -0.34332 | 122.287 | 122.168 | -0.9613 | -0.96588 | 0.004578 | -0.13733 | -121.7834 | 0.8194 | -0.054932 | 0.082397 | -122.0306 | -0.10529 | -0.10986 | 0.26093 | 0.70038 | 0.51269 | 0.62256 | 0.14191 | 1.0986 | 0.85144 | 0.59509 | -123.0194 | 123.143 | 123.024 | 11.1374 | -122.9919
1364.6406 | 122.9645 | -0.82855 | 122.0215 | 0.52232 | 0.0071002 | 0.0090179 | 0.37357 | -0.04487 | -0.029426 | -0.032808 | 0.58626 | -0.028273 | 0.051988 | 0.041327 | 0.020587 | 0.084276 | 0.041199 | 0.10071 | -0.2655 | -0.75989 | 0.19684 | -0.83771 | -0.97504 | -0.13733 | 10.0937 | -0.24261 | 122.2504 | 122.1405 | -0.93384 | -0.95215 | -0.009156 | -0.14649 | -121.8246 | 0.92926 | 0.068664 | 0.21515 | -121.9803 | -0.10529 | -0.1236 | 0.22888 | 0.69122 | 0.58594 | 0.70953 | 0.11902 | 1.0254 | 0.86975 | 0.56305 | -122.9965 | 123.0789 | 122.9691 | 10.9222 | -122.9736
1365.6406 | 122.937 | -0.79651 | 122.0627 | 0.44602 | 0.019917 | 0.0068819 | 0.37036 | -0.029916 | -0.035834 | -0.021058 | 0.43367 | -0.043227 | 0.047715 | 0.025306 | 0.016315 | 0.075732 | 0.050354 | 0.10529 | -0.23346 | -0.71411 | 0.18768 | -0.78735 | -0.92926 | -0.10529 | 9.7275 | -0.19226 | 122.2504 | 122.1725 | -0.89722 | -0.91095 | 0.009155 | -0.13275 | -121.875 | 0.9018 | 0.082398 | 0.21515 | -122.0123 | -0.10071 | -0.11444 | 0.18768 | 0.69122 | 0.60425 | 0.71869 | 0.10986 | 0.98419 | 0.84686 | 0.56305 | -122.9919 | 123.0469 | 122.9691 | 10.524 | -122.9736
1366.6406 | 123.0286 | -0.79651 | 122.0627 | 0.14085 | -0.0057178 | 0.015426 | 0.36502 | -0.040597 | -0.030494 | -0.036012 | 0.097976 | -0.053908 | 0.026353 | 0.025306 | 0.021655 | 0.077868 | 0.073242 | 0.11444 | -0.21973 | -0.68665 | 0.21057 | -0.80109 | -0.93842 | -0.1236 | 9.6954 | -0.16937 | 122.287 | 122.1771 | -0.87891 | -0.90179 | -0.004577 | -0.14191 | -121.8521 | 0.91095 | 0.10986 | 0.25177 | -121.9894 | -0.082397 | -0.10528 | 0.2243 | 0.67291 | 0.62714 | 0.73242 | 0.11444 | 1.0071 | 0.86975 | 0.57678 | -123.0011 | 123.0835 | 122.9736 | 10.4919 | -122.9645
1367.6406 | 122.9553 | -0.79651 | 122.0947 | 0.32395 | 0.0081682 | 0.018631 | 0.36716 | -0.03312 | -0.033698 | -0.038148 | -0.39031 | -0.030409 | 0.034898 | 0.026374 | 0.017383 | 0.069323 | 0.004578 | 0.059509 | -0.27008 | -0.83771 | 0.19226 | -0.82398 | -1.0071 | -0.1831 | 8.2077 | -0.21515 | 122.2549 | 122.1817 | -0.90637 | -0.9201 | -0.027466 | -0.21057 | -121.9025 | 0.85602 | -0.041199 | 0.16937 | -122.0901 | -0.10986 | -0.1236 | 0.16022 | 0.6134 | 0.58136 | 0.70496 | 0.086975 | 0.98877 | 0.80109 | 0.52643 | -123.1018 | 123.0515 | 122.9782 | 9.0042 | -123.0148
1368.6406 | 122.9691 | -0.80566 | 122.0627 | 0.32395 | -0.0035808 | 0.021835 | 0.3693 | -0.039529 | -0.025153 | -0.043489 | 0.067459 | -0.042159 | 0.041307 | 0.043464 | 0.019519 | 0.083208 | 0.041199 | 0.07782 | -0.25177 | -0.72784 | 0.21515 | -0.8194 | -0.94757 | -0.15106 | 7.7774 | -0.20142 | 122.2778 | 122.1771 | -0.90637 | -0.91095 | -0.013733 | -0.14191 | -121.8475 | 0.88348 | 0.07782 | 0.21973 | -122.0215 | -0.10071 | -0.10529 | 0.21515 | 0.6546 | 0.60425 | 0.70953 | 0.11444 | 1.0208 | 0.84686 | 0.55389 | -123.0103 | 123.0835 | 122.9828 | 8.5831 | -122.9736
1369.6406 | 122.9507 | -0.79193 | 122.113 | 0.41551 | 0.02419 | 0.00047294 | 0.37464 | -0.038461 | -0.023017 | -0.040284 | 0.20479 | -0.046431 | 0.03383 | 0.035987 | 0.017383 | 0.062914 | 0.032043 | 0.068665 | -0.27466 | -0.72327 | 0.21973 | -0.7782 | -0.9201 | -0.13275 | 8.0246 | -0.21515 | 122.287 | 122.168 | -0.85602 | -0.90179 | 0.013733 | -0.12817 | -121.8933 | 0.8606 | 0.068664 | 0.19684 | -122.081 | -0.064087 | -0.10986 | 0.17395 | 0.65918 | 0.57678 | 0.68664 | 0.054932 | 1.0117 | 0.82397 | 0.51727 | -123.0331 | 123.0789 | 122.9599 | 8.8165 | -123.0148
1370.6406 | 122.8683 | -0.81024 | 121.9299 | -0.22536 | 0.030598 | 0.0068819 | 0.38211 | -0.029916 | 0.0015501 | -0.032808 | -1.1838 | -0.032546 | 0.037034 | 0.035987 | 0.022724 | 0.066119 | 0.14191 | 0.27924 | -0.21057 | -0.79651 | 0.27466 | -0.78278 | -0.91553 | -0.30212 | 7.2006 | -0.28839 | 122.3511 | 122.2137 | -0.9201 | -0.9201 | 0.027466 | -0.10528 | -121.6553 | 1.0895 | 0.013733 | 0.11902 | -121.788 | -0.10986 | -0.10986 | 0.42114 | 0.50812 | 0.52185 | 0.63171 | 0.28381 | 1.0849 | 0.95215 | 0.59967 | -122.8455 | 123.1613 | 123.024 | 8.0109 | -122.85
1371.6406 | 123.0057 | -0.76904 | 122.1313 | 0.079814 | -0.0035808 | 0.012222 | 0.3725 | -0.028848 | -0.021949 | -0.038148 | 0.0064239 | -0.024001 | 0.024217 | 0.02851 | 0.015247 | 0.0768 | 0.045776 | 0.11902 | -0.2243 | -0.66376 | 0.21515 | -0.76446 | -0.90637 | -0.19684 | 7.576 | -0.12817 | 122.3007 | 122.1954 | -0.86517 | -0.87433 | 0.004578 | -0.13733 | -121.9162 | 0.88806 | 0.10529 | 0.24261 | -122.0856 | -0.09613 | -0.10529 | 0.16937 | 0.57221 | 0.64087 | 0.74616 | 0.064087 | 0.98419 | 0.81482 | 0.54474 | -123.0377 | 123.0698 | 122.9645 | 8.345 | -123.0057
1372.6406 | 122.8638 | -0.85144 | 122.1634 | -0.24062 | 0.017781 | 0.017563 | 0.39066 | -0.034188 | -0.0059269 | -0.043489 | -1.1075 | -0.026137 | 0.053056 | 0.050941 | 0.025928 | 0.069323 | 0.1236 | 0.29755 | -0.21515 | -0.81024 | 0.27924 | -0.78278 | -0.92926 | -0.29755 | 7.9651 | -0.28839 | 122.3785 | 122.2321 | -0.89264 | -0.91095 | 0.068664 | -0.07782 | -121.8842 | 1.149 | 0.041198 | 0.11902 | -122.0398 | -0.041199 | -0.05951 | 0.21515 | 0.55389 | 0.56305 | 0.62256 | 0.068665 | 1.1307 | 0.97504 | 0.63629 | -123.0927 | 123.23 | 123.0835 | 8.8165 | -123.0743
1373.6406 | 122.9736 | -0.76904 | 122.113 | -0.91201 | -0.00037681 | -0.0027321 | 0.37143 | -0.035257 | -0.028357 | -0.029603 | -0.35979 | -0.043227 | 0.038102 | 0.038123 | 0.018451 | 0.070391 | 0.032043 | 0.17395 | -0.1831 | -0.6546 | 0.1831 | -0.76446 | -0.92926 | -0.24719 | 7.7545 | -0.16479 | 122.3007 | 122.1863 | -0.86975 | -0.86975 | 0.004578 | -0.16022 | -121.9299 | 0.94299 | 0.11444 | 0.27466 | -122.081 | -0.10071 | -0.10071 | 0.18768 | 0.52185 | 0.60425 | 0.70496 | 0.073242 | 0.95215 | 0.80109 | 0.58594 | -123.0423 | 123.0698 | 122.9553 | 8.5236 | -122.9828
1374.6406 | 122.905 | -0.80109 | 122.1085 | -0.14907 | 0.037007 | 0.0026089 | 0.38425 | -0.036325 | 0.0090271 | -0.018922 | -0.4666 | -0.033614 | 0.054124 | 0.049872 | 0.029132 | 0.063982 | -0.004578 | 0.027466 | -0.31128 | -0.71869 | 0.23346 | -0.79651 | -0.95215 | -0.24719 | 7.0312 | -0.26093 | 122.3373 | 122.2046 | -0.90179 | -0.90179 | 0.004577 | -0.15106 | -121.875 | 0.82855 | 0.082397 | 0.23346 | -122.113 | -0.10071 | -0.10071 | 0.22888 | 0.55389 | 0.54016 | 0.64087 | 0.096131 | 1.0345 | 0.79651 | 0.48981 | -123.0606 | 123.1384 | 123.0057 | 7.8323 | -123.0103
1375.6406 | 122.9279 | -0.79193 | 122.1497 | -0.10329 | 0.02419 | 0.0026089 | 0.38532 | -0.036325 | -0.0016549 | -0.023195 | -0.22246 | -0.029341 | 0.064805 | 0.041327 | 0.031268 | 0.061846 | 0.013733 | 0.036621 | -0.27008 | -0.70496 | 0.2243 | -0.80566 | -0.94757 | -0.28381 | 7.0267 | -0.22888 | 122.3511 | 122.2366 | -0.88348 | -0.89264 | -0.013733 | -0.15564 | -121.9254 | 0.82855 | 0.086975 | 0.24262 | -122.1359 | -0.091553 | -0.10071 | 0.20142 | 0.50812 | 0.56305 | 0.66376 | 0.086975 | 1.0162 | 0.80566 | 0.52185 | -123.0972 | 123.143 | 123.0286 | 7.8186 | -123.0423
1376.6406 | 122.8867 | -0.79651 | 122.1313 | -0.27114 | 0.035939 | 0.0090179 | 0.38745 | -0.029916 | -0.011268 | -0.040284 | -0.78703 | -0.038954 | 0.057328 | 0.038123 | 0.025928 | 0.068255 | 0.19684 | 0.11444 | -0.32959 | -0.79651 | 0.27466 | -0.75989 | -0.90637 | -0.37537 | 5.484 | -0.27924 | 122.3923 | 122.2458 | -0.88806 | -0.9201 | 0.036621 | -0.10986 | -121.8567 | 0.91095 | 0 | 0.10986 | -121.9345 | -0.091553 | -0.1236 | 0.26093 | 0.42114 | 0.51727 | 0.64087 | 0.11444 | 1.0712 | 0.99335 | 0.46692 | -123.0377 | 123.1888 | 123.0423 | 6.2805 | -123.0515
1377.6406 | 122.9004 | -0.80109 | 122.1176 | -0.14907 | 0.043416 | -0.0027321 | 0.37998 | -0.036325 | -0.00058594 | -0.021058 | -0.16142 | -0.031478 | 0.074418 | 0.037055 | 0.021655 | 0.070391 | 0.009155 | 0.022888 | -0.28839 | -0.70953 | 0.23346 | -0.81024 | -0.95215 | -0.30212 | 5.5847 | -0.2243 | 122.3511 | 122.2504 | -0.87433 | -0.88806 | -0.009156 | -0.15106 | -121.8842 | 0.82397 | 0.091552 | 0.24261 | -122.1085 | -0.073243 | -0.086976 | 0.23346 | 0.49896 | 0.57678 | 0.66376 | 0.13275 | 1.0345 | 0.81024 | 0.51269 | -123.0698 | 123.1522 | 123.0515 | 6.3858 | -123.0057
1378.6406 | 122.8455 | -0.79651 | 122.1359 | -1.5834 | 0.043416 | 0.00047294 | 0.38425 | -0.041665 | 0.0026181 | -0.021058 | -0.0088351 | -0.027205 | 0.053056 | 0.035987 | 0.02486 | 0.073595 | 0.041199 | 0.064087 | -0.29297 | -0.70496 | 0.2655 | -0.75073 | -0.90637 | -0.31128 | 4.9026 | -0.26093 | 122.3694 | 122.2321 | -0.89722 | -0.90179 | 0.045777 | -0.10986 | -121.8704 | 0.8606 | 0.091553 | 0.20142 | -122.0947 | -0.10071 | -0.10528 | 0.23346 | 0.48523 | 0.53558 | 0.64087 | 0.096131 | 1.062 | 0.83771 | 0.50354 | -123.0423 | 123.1659 | 123.0286 | 5.6992 | -123.0377
1379.6406 | 122.9324 | -0.81482 | 122.113 | -0.072774 | 0.050892 | 0.012222 | 0.3725 | -0.024575 | -0.0059269 | -0.024263 | -0.48186 | -0.026137 | 0.045579 | 0.034919 | 0.032337 | 0.063982 | 0.013733 | 0.036621 | -0.29755 | -0.72327 | 0.23804 | -0.82398 | -0.97504 | -0.33875 | 5.0171 | -0.25177 | 122.3145 | 122.2137 | -0.90637 | -0.91553 | -0.009156 | -0.16022 | -121.875 | 0.85144 | 0.091552 | 0.25177 | -122.0993 | -0.091553 | -0.10071 | 0.20142 | 0.47607 | 0.56305 | 0.66376 | 0.10071 | 1.0529 | 0.82855 | 0.51727 | -123.0881 | 123.1293 | 123.0286 | 5.8319 | -123.0286
1380.6406 | 122.9279 | -0.82398 | 122.1222 | 0.15611 | 0.043416 | -0.015549 | 0.37036 | -0.023507 | 0.0015501 | -0.026399 | -0.054612 | -0.031478 | 0.060533 | 0.047736 | 0.021655 | 0.0768 | 0.027466 | 0.050354 | -0.28381 | -0.72784 | 0.27924 | -0.78735 | -0.92926 | -0.32959 | 6.5094 | -0.27924 | 122.3282 | 122.2458 | -0.92468 | -0.93384 | 0.036621 | -0.10528 | -121.843 | 0.87433 | 0.096131 | 0.20142 | -122.0947 | -0.10071 | -0.10986 | 0.20599 | 0.49439 | 0.54474 | 0.6546 | 0.1236 | 1.1032 | 0.85144 | 0.54016 | -123.0515 | 123.1522 | 123.0698 | 7.3334 | -123.056
1381.6406 | 122.905 | -0.75073 | 122.1451 | 0.079814 | 0.057301 | -0.0059361 | 0.38532 | -0.024575 | -0.0037909 | -0.018922 | -0.085129 | -0.022933 | 0.063737 | 0.042396 | 0.029132 | 0.070391 | 0.018311 | 0.064087 | -0.27466 | -0.70496 | 0.21973 | -0.79193 | -0.95215 | -0.09613 | 5.5298 | -0.18768 | 122.3969 | 122.319 | -0.84228 | -0.84228 | -0.041199 | -0.20142 | -121.9254 | 0.81482 | 0.045776 | 0.24719 | -122.1268 | -0.091553 | -0.091553 | 0.25177 | 0.6546 | 0.56305 | 0.6546 | 0.17395 | 0.97046 | 0.76904 | 0.47607 | -123.0972 | 123.1476 | 123.0698 | 6.2805 | -122.9874
1382.6406 | 123.0103 | -0.74158 | 122.1405 | 0.52232 | 0.020985 | 0.021835 | 0.3725 | -0.03312 | -0.013404 | -0.030671 | 0.4947 | -0.03575 | 0.03917 | 0.037055 | 0.021655 | 0.073595 | 0.054932 | 0.11444 | -0.21515 | -0.60883 | 0.1831 | -0.70953 | -0.85144 | -0.19684 | 4.7699 | -0.33417 | 122.287 | 122.2275 | -0.84686 | -0.84686 | 0.032043 | -0.10986 | -121.9574 | 0.85602 | 0.13275 | 0.24261 | -122.0856 | -0.10529 | -0.10529 | 0.14648 | 0.54474 | 0.40741 | 0.5127 | 0.086975 | 0.92468 | 0.79651 | 0.52643 | -122.9919 | 123.0286 | 122.9691 | 5.5115 | -122.9874
1383.6406 | 122.8912 | -0.74158 | 122.2046 | 0.41551 | 0.037007 | 0.014358 | 0.38639 | -0.03312 | 0.0058221 | -0.022126 | -1.2753 | -0.03575 | 0.066941 | 0.040259 | 0.020587 | 0.068255 | -0.018311 | -0.041199 | -0.37079 | -0.68207 | 0.22888 | -0.74158 | -0.88806 | -0.27008 | 5.0079 | -0.19684 | 122.4152 | 122.3419 | -0.81482 | -0.84686 | 0 | -0.14648 | -121.9757 | 0.70038 | 0.059509 | 0.20599 | -122.2229 | -0.073242 | -0.10529 | 0.21057 | 0.4715 | 0.54474 | 0.65003 | 0.13733 | 0.97046 | 0.72327 | 0.37079 | -123.0927 | 123.1567 | 123.0835 | 5.7495 | -123.0515
1384.6406 | 122.0215 | -0.7782 | 122.1863 | 0.41551 | 0.054097 | 0.00047294 | 0.3725 | -0.049142 | 0.0090271 | -0.026399 | 0.46419 | -0.022933 | 0.069078 | 0.026374 | 0.028064 | 0.081072 | -0.022888 | -0.045776 | -0.34332 | -0.70038 | 0.2243 | -0.75531 | -0.91095 | -0.29297 | 6.8436 | -0.24719 | 122.4106 | 122.3328 | -0.87891 | -0.88348 | 0.022888 | -0.13275 | -121.962 | 0.73242 | 0.07782 | 0.21057 | -122.2092 | -0.10071 | -0.10529 | 0.2243 | 0.48523 | 0.53101 | 0.63629 | 0.14648 | 1.0025 | 0.75531 | 0.43487 | -123.0972 | 123.1888 | 123.111 | 7.6218 | -123.0698
1385.6406 | 122.2046 | -0.75531 | 122.0123 | 0.2324 | 0.051961 | 0.0026089 | 0.38639 | -0.045938 | -0.0016549 | -0.030671 | 0.35738 | -0.014388 | 0.063737 | 0.030646 | 0.032337 | 0.072527 | -0.009155 | -0.059509 | -0.35706 | -0.69122 | 0.21973 | -0.76904 | -0.92468 | -0.33875 | 5.4062 | -0.28839 | 122.3969 | 122.3465 | -0.87891 | -0.87433 | -0.013733 | -0.16937 | -121.7926 | 0.6958 | 0.064087 | 0.23346 | -122.0215 | -0.1236 | -0.11902 | 0.38452 | 0.41657 | 0.46692 | 0.58594 | 0.33417 | 0.97504 | 0.74616 | 0.39825 | -122.937 | 123.1522 | 123.1018 | 6.1615 | -122.8867
1386.6406 | 122.9462 | -0.74616 | 122.1542 | 0.53758 | 0.034871 | 0.0047449 | 0.35221 | -0.029916 | -0.020881 | -0.034944 | 0.571 | -0.041091 | 0.062669 | 0.041327 | 0.015247 | 0.073595 | 0.059509 | 0.09613 | -0.21973 | -0.60883 | 0.1831 | -0.70038 | -0.83771 | -0.20142 | 5.0446 | -0.1831 | 122.3511 | 122.2183 | -0.83313 | -0.82855 | 0.045777 | -0.091553 | -121.9711 | 0.84228 | 0.13733 | 0.22888 | -122.0947 | -0.086975 | -0.082397 | 0.19684 | 0.54474 | 0.56305 | 0.64545 | 0.064087 | 0.92926 | 0.80566 | 0.52643 | -122.9919 | 123.0972 | 122.9645 | 5.7907 | -122.9828
1387.6406 | 123.0103 | -0.68665 | 122.1634 | 0.47654 | 0.014576 | 0.011154 | 0.38959 | -0.037393 | -0.027289 | -0.015718 | 0.18953 | -0.032546 | 0.055192 | 0.040259 | 0.017383 | 0.081072 | -0.16937 | 0.24719 | -0.14648 | -0.63629 | 0.14648 | -0.74158 | -0.87891 | -0.18768 | 4.8569 | -0.091553 | 122.3648 | 122.3236 | -0.80109 | -0.8194 | -0.054931 | -0.19226 | -122.0169 | 0.93384 | 0.050354 | 0.24261 | -122.3328 | -0.11444 | -0.13275 | 0.20142 | 0.49896 | 0.59509 | 0.72784 | 0.16022 | 0.83313 | 0.51727 | 0.54016 | -123.0423 | 123.0515 | 123.0103 | 5.5435 | -122.9828
1388.6406 | 122.9553 | -0.6958 | 122.2 | 0.90379 | 0.015645 | 0.0079499 | 0.3693 | -0.053415 | -0.031562 | -0.038148 | 0.46419 | -0.028273 | 0.051988 | 0.032783 | 0.014179 | 0.08214 | 0.064087 | 0.091553 | -0.2243 | -0.62256 | 0.19226 | -0.68207 | -0.85602 | -0.20142 | 4.3396 | -0.10529 | 122.3648 | 122.3007 | -0.79193 | -0.81482 | 0.013733 | -0.16022 | -122.0078 | 0.78735 | 0.073242 | 0.23346 | -122.1359 | -0.09613 | -0.11902 | 0.16479 | 0.49438 | 0.59052 | 0.70953 | 0.10071 | 0.88806 | 0.75989 | 0.4715 | -123.056 | 123.0606 | 122.9965 | 5.0354 | -123.0148
1389.6406 | 122.6761 | -0.77362 | 121.7789 | 0.50706 | 0.043416 | -0.0038001 | 0.38959 | -0.032052 | 0.0079581 | -0.03708 | 0.38789 | -0.030409 | 0.048783 | 0.0456 | 0.033405 | 0.070391 | 0.045776 | 0 | -0.32959 | -0.73242 | 0.20142 | -0.79651 | -0.91553 | -0.33875 | 4.7791 | -0.2243 | 122.3785 | 122.2687 | -0.8606 | -0.89264 | -0.022888 | -0.14191 | -121.5775 | 0.77362 | 0.041199 | 0.1831 | -121.7331 | -0.086975 | -0.11902 | 0.59967 | 0.43488 | 0.54932 | 0.66833 | 0.48981 | 0.97504 | 0.8194 | 0.44403 | -122.6944 | 123.1522 | 123.0423 | 5.5527 | -122.6715
1390.6406 | 122.9874 | -0.76446 | 122.1039 | 0.43077 | 0.00069119 | 0.0036769 | 0.36075 | -0.048074 | -0.03263 | -0.040284 | 0.082718 | -0.044295 | 0.048783 | 0.030646 | 0.018451 | 0.073595 | 0.032043 | 0.041199 | -0.2655 | -0.67749 | 0.21057 | -0.74158 | -0.89722 | -0.30212 | 4.7562 | -0.17395 | 122.3419 | 122.2824 | -0.84228 | -0.86975 | 0.022888 | -0.13275 | -121.8933 | 0.80566 | 0.086975 | 0.21973 | -122.0718 | -0.07782 | -0.10529 | 0.23804 | 0.46234 | 0.59051 | 0.6958 | 0.17853 | 0.97504 | 0.79651 | 0.49896 | -123.0011 | 123.1064 | 123.0469 | 5.5206 | -122.9736
1391.6406 | 123.0194 | -0.76446 | 121.9345 | 0.20188 | 0.017781 | 0.0026089 | 0.36395 | -0.047006 | -0.029426 | -0.044557 | 0.15901 | -0.049636 | 0.055192 | 0.032783 | 0.017383 | 0.074663 | 0.027466 | 0.045776 | -0.27924 | -0.69122 | 0.20599 | -0.76904 | -0.92468 | -0.34332 | 4.5868 | -0.20599 | 122.3557 | 122.2687 | -0.86975 | -0.89264 | -0.004578 | -0.16022 | -121.7285 | 0.81024 | 0.073242 | 0.23346 | -121.907 | -0.10529 | -0.12817 | 0.42114 | 0.42114 | 0.55847 | 0.68664 | 0.33417 | 0.97046 | 0.79193 | 0.48523 | -122.8592 | 123.1201 | 123.0331 | 5.3513 | -122.8271
1392.6406 | 123.0286 | -0.75531 | 121.8109 | 0.095073 | 0.00069119 | 0.014358 | 0.3757 | -0.053415 | -0.025153 | -0.042421 | 0.067459 | -0.041091 | 0.040239 | 0.040259 | 0.010974 | 0.068255 | 0.068665 | 0.086975 | -0.22888 | -0.66834 | 0.21057 | -0.76446 | -0.89264 | -0.27466 | 4.129 | -0.12817 | 122.3557 | 122.2458 | -0.84686 | -0.8606 | -0.009155 | -0.13733 | -121.6003 | 0.84229 | 0.086975 | 0.2243 | -121.7422 | -0.091553 | -0.10529 | 0.54474 | 0.48065 | 0.62714 | 0.73242 | 0.43488 | 0.96588 | 0.82398 | 0.52643 | -122.7036 | 123.111 | 123.0011 | 4.8843 | -122.6715
1393.6406 | 122.9736 | -0.7782 | 121.8796 | 0.52232 | 0.025258 | 0.0090179 | 0.37464 | -0.04487 | -0.014472 | -0.042421 | 0.32686 | -0.038954 | 0.058397 | 0.039191 | 0.022724 | 0.080004 | 0.064087 | 0.09613 | -0.24719 | -0.69122 | 0.20599 | -0.77362 | -0.89264 | -0.29297 | 3.8681 | -0.1831 | 122.3465 | 122.2321 | -0.85144 | -0.86517 | 0.004577 | -0.11444 | -121.6736 | 0.87433 | 0.086975 | 0.20142 | -121.8155 | -0.073242 | -0.086975 | 0.46692 | 0.48523 | 0.59509 | 0.68207 | 0.35248 | 0.98419 | 0.84228 | 0.53101 | -122.7722 | 123.1247 | 123.0103 | 4.6463 | -122.7448
1394.6406 | 122.5845 | -0.82855 | 121.3623 | -1.263 | 0.053029 | -0.0016631 | 0.38532 | -0.032052 | 0.00048206 | -0.025331 | -0.52763 | -0.031478 | 0.060533 | 0.035987 | 0.028064 | 0.051165 | 0.018311 | -0.013733 | -0.32959 | -0.72784 | 0.25635 | -0.78735 | -0.93842 | -0.31586 | 3.7445 | -0.27924 | 122.3785 | 122.2733 | -0.90179 | -0.9201 | 0.041198 | -0.10986 | -121.106 | 0.81482 | 0.10071 | 0.21057 | -121.344 | -0.073242 | -0.091553 | 1.0162 | 0.51269 | 0.54932 | 0.64087 | 0.91095 | 1.0849 | 0.84686 | 0.49896 | -122.3007 | 123.2071 | 123.1018 | 4.5731 | -122.2824
1395.6406 | 123.0331 | -0.79651 | 122.0398 | 0.24766 | -0.0078538 | 0.016495 | 0.35968 | -0.042733 | -0.033698 | -0.034944 | 0.22005 | -0.046431 | 0.053056 | 0.038123 | 0.016315 | 0.075732 | 0.013733 | 0.064087 | -0.27008 | -0.70038 | 0.21057 | -0.76904 | -0.91095 | -0.32044 | 3.7079 | -0.19684 | 122.3419 | 122.2458 | -0.86517 | -0.88806 | 0.027466 | -0.11444 | -121.8292 | 0.8606 | 0.096131 | 0.21057 | -122.0261 | -0.068664 | -0.091553 | 0.30212 | 0.47607 | 0.59967 | 0.69122 | 0.20599 | 1.0071 | 0.81024 | 0.52643 | -122.9507 | 123.1384 | 123.0423 | 4.5044 | -122.9279
1396.6406 | 122.9965 | -0.75989 | 122.1497 | 0.26292 | -0.0057178 | -0.0038001 | 0.36395 | -0.03312 | -0.020881 | -0.043489 | 0.66255 | -0.045363 | 0.049852 | 0.027442 | 0.021655 | 0.074663 | 0.018311 | 0.073242 | -0.4715 | -0.76904 | 0.1831 | -0.81024 | -0.9613 | -0.28381 | 3.5477 | -0.18768 | 122.3557 | 122.2458 | -0.8606 | -0.87433 | -0.050354 | -0.20142 | -121.9666 | 0.83313 | -0.009155 | 0.19226 | -122.1313 | -0.10071 | -0.11444 | 0.20599 | 0.47608 | 0.57221 | 0.68665 | 0.096131 | 0.94299 | 0.7782 | 0.28839 | -123.111 | 123.1155 | 123.0057 | 4.3076 | -123.024
1397.6406 | 122.9828 | -0.75531 | 121.9025 | -0.10329 | 0.00069119 | 0.0058129 | 0.37891 | -0.053415 | -0.021949 | -0.030671 | -0.23772 | -0.031478 | 0.047715 | 0.025306 | 0.020587 | 0.071459 | 0.082397 | 0.14648 | -0.17853 | -0.63171 | 0.19226 | -0.75531 | -0.88806 | -0.3067 | 3.7857 | -0.10071 | 122.3557 | 122.2275 | -0.85144 | -0.88806 | 0 | -0.13275 | -121.7102 | 0.90179 | 0.1236 | 0.25635 | -121.8201 | -0.09613 | -0.13275 | 0.45319 | 0.44861 | 0.6546 | 0.78735 | 0.32501 | 0.94757 | 0.83771 | 0.57678 | -122.7905 | 123.111 | 122.9828 | 4.541 | -122.7905
1398.6406 | 122.9507 | -0.737 | 122.0306 | -0.88149 | -0.0035808 | -0.013413 | 0.3757 | -0.038461 | -0.0048589 | -0.042421 | -0.40556 | -0.040022 | 0.060533 | 0.035987 | 0.018451 | 0.069323 | 0.018311 | 0.16022 | -0.21057 | -0.62714 | 0.18768 | -0.76904 | -0.89722 | -0.2243 | 3.6163 | -0.14648 | 122.3877 | 122.2595 | -0.84686 | -0.84228 | -0.032043 | -0.16022 | -121.843 | 0.89722 | 0.10986 | 0.27008 | -122.0123 | -0.10986 | -0.10528 | 0.35705 | 0.5127 | 0.59052 | 0.6958 | 0.22888 | 0.92468 | 0.75531 | 0.52643 | -122.9279 | 123.1247 | 122.9965 | 4.3533 | -122.8729
1399.6406 | 122.9141 | -0.77362 | 122.0673 | -0.22536 | 0.019917 | 0.0047449 | 0.37784 | -0.034188 | -0.011268 | -0.030671 | -0.52763 | -0.040022 | 0.048783 | 0.0456 | 0.022724 | 0.072527 | 0.013733 | 0.054932 | -0.29755 | -0.71411 | 0.25635 | -0.74158 | -0.91095 | -0.31586 | 3.8773 | -0.23346 | 122.4152 | 122.2595 | -0.87433 | -0.88348 | 0.032044 | -0.13733 | -121.8109 | 0.82855 | 0.05951 | 0.19684 | -122.0535 | -0.10071 | -0.10986 | 0.3479 | 0.45776 | 0.54016 | 0.65003 | 0.19226 | 1.03 | 0.78735 | 0.47608 | -122.9782 | 123.1888 | 123.0331 | 4.6509 | -122.9507
1400.6406 | 122.8134 | -0.78735 | 122.2046 | -0.24062 | 0.028462 | 0.015426 | 0.38211 | -0.029916 | -0.011268 | -0.027467 | -0.48186 | -0.027205 | 0.049852 | 0.029578 | 0.02486 | 0.066119 | -0.022888 | 0.018311 | -0.31586 | -0.74616 | 0.25177 | -0.83313 | -0.98419 | -0.36163 | 2.4811 | -0.3067 | 122.3648 | 122.2733 | -0.89722 | -0.92468 | -0.045776 | -0.19684 | -121.9528 | 0.80566 | 0.041199 | 0.23804 | -122.2275 | -0.10986 | -0.13733 | 0.16022 | 0.42572 | 0.48065 | 0.61798 | 0.068664 | 1.0391 | 0.76447 | 0.4715 | -123.1888 | 123.1522 | 123.0606 | 3.2684 | -123.1293
1401.6406 | 122.9645 | -0.78278 | 122.1725 | -0.13381 | 0.0060322 | 0.0058129 | 0.36395 | -0.02778 | -0.024085 | -0.018922 | -0.26824 | -0.03575 | 0.049852 | 0.02317 | 0.012042 | 0.072527 | 0.045776 | 0.12817 | -0.22888 | -0.66376 | 0.19226 | -0.78735 | -0.90637 | -0.33417 | 2.3987 | -0.20142 | 122.3419 | 122.2366 | -0.88348 | -0.90637 | -0.004578 | -0.1236 | -121.9803 | 0.91095 | 0.11902 | 0.24261 | -122.1268 | -0.10071 | -0.1236 | 0.16937 | 0.44861 | 0.58136 | 0.70496 | 0.064087 | 0.97504 | 0.82855 | 0.55389 | -123.0789 | 123.1247 | 123.0194 | 3.1815 | -123.0789
1402.6406 | 122.3877 | -0.79193 | 122.1634 | 0.18663 | 0.055165 | -0.0038001 | 0.38425 | -0.02778 | 0.0047541 | -0.018922 | -0.0088351 | -0.019728 | 0.054124 | 0.035987 | 0.037677 | 0.060778 | 0.022888 | 0.032043 | -0.33875 | -0.71411 | 0.18768 | -0.80109 | -0.9613 | -0.38452 | 2.4628 | -0.29297 | 122.3419 | 122.2275 | -0.91095 | -0.92468 | -0.009155 | -0.16937 | -121.9757 | 0.82397 | 0.07782 | 0.24719 | -122.1405 | -0.11902 | -0.13275 | 0.17853 | 0.40741 | 0.49896 | 0.63171 | 0.064087 | 0.97961 | 0.81482 | 0.45319 | -123.1247 | 123.1339 | 123.0194 | 3.2547 | -123.0881
1403.6406 | 122.8729 | -0.79651 | 122.1771 | -0.24062 | 0.020985 | 0.0090179 | 0.37464 | -0.039529 | -0.020881 | -0.036012 | -0.039353 | -0.015456 | 0.047715 | 0.039191 | 0.029132 | 0.06505 | 0.2243 | -0.16022 | -0.39368 | -0.6546 | 0.27008 | -0.74616 | -0.89264 | -0.35248 | 2.1835 | -0.24261 | 122.4197 | 122.3099 | -0.87433 | -0.91095 | 0.050354 | -0.09613 | -121.907 | 0.63629 | 0.14191 | 0.23804 | -121.9528 | -0.07782 | -0.11444 | 0.24262 | 0.44403 | 0.55389 | 0.66834 | 0.13275 | 1.0666 | 1.0208 | 0.40283 | -123.0698 | 123.2162 | 123.1064 | 2.98 | -123.0881
1404.6406 | 122.7493 | -0.78735 | 122.1909 | -0.30166 | 0.027394 | 0.0015409 | 0.3725 | -0.041665 | -0.016608 | -0.028535 | -0.45134 | -0.027205 | 0.044511 | 0.035987 | 0.017383 | 0.072527 | -0.036621 | 0.013733 | -0.32044 | -0.6958 | 0.23346 | -0.78278 | -0.95215 | -0.33417 | 2.1103 | -0.25177 | 122.438 | 122.2824 | -0.86975 | -0.89722 | 0.004578 | -0.16479 | -121.9574 | 0.80109 | 0.091553 | 0.25635 | -122.2275 | -0.082397 | -0.10986 | 0.24719 | 0.45319 | 0.53558 | 0.64545 | 0.091553 | 1.0208 | 0.75073 | 0.46692 | -123.143 | 123.2254 | 123.0698 | 2.8976 | -123.0881
1405.6406 | 122.8867 | -0.76904 | 122.1863 | -0.14907 | 0.030598 | 0.012222 | 0.3693 | -0.030984 | -0.0069949 | -0.022126 | -0.34453 | -0.031478 | 0.044511 | 0.038123 | 0.02486 | 0.072527 | -0.032043 | 0.013733 | -0.32044 | -0.69122 | 0.21973 | -0.78278 | -0.93384 | -0.33875 | 1.8448 | -0.2243 | 122.3969 | 122.2961 | -0.88806 | -0.90637 | -0.013733 | -0.16479 | -121.9666 | 0.78278 | 0.07782 | 0.24261 | -122.2183 | -0.11902 | -0.13733 | 0.21057 | 0.4303 | 0.54474 | 0.68207 | 0.10986 | 0.98877 | 0.737 | 0.44861 | -123.1201 | 123.1659 | 123.0652 | 2.6138 | -123.0927
1406.6406 | 122.9095 | -0.80109 | 122.1954 | 0.44602 | 0.037007 | 0.0090179 | 0.37677 | -0.028848 | 0.00048206 | -0.028535 | -3.3047 | -0.031478 | 0.05626 | 0.033851 | 0.019519 | 0.0768 | -0.045776 | -0.027466 | -0.37537 | -0.72327 | 0.23346 | -0.79651 | -0.93842 | -0.27924 | 1.6708 | -0.23804 | 122.3785 | 122.2641 | -0.88806 | -0.88806 | 0.004577 | -0.13733 | -121.962 | 0.77362 | 0.077819 | 0.21515 | -122.2412 | -0.086976 | -0.086976 | 0.1831 | 0.52185 | 0.56305 | 0.65003 | 0.068664 | 1.0345 | 0.75531 | 0.42572 | -123.1339 | 123.1796 | 123.0652 | 2.4719 | -123.0835
1407.6562 | 123.0423 | -0.75531 | 122.1497 | 0.034038 | 0.023121 | 0.025039 | 0.35755 | -0.052346 | -0.046515 | -0.034944 | -0.19194 | -0.048567 | 0.035966 | 0.043464 | 0.019519 | 0.080004 | 0.027466 | 0.16937 | -0.19684 | -0.64087 | 0.19684 | -0.74158 | -0.88806 | -0.17395 | 2.0508 | -0.10986 | 122.3511 | 122.2687 | -0.84228 | -0.8606 | 0.013733 | -0.13275 | -121.9528 | 0.92468 | 0.11444 | 0.24719 | -122.1222 | -0.086975 | -0.10529 | 0.20142 | 0.58136 | 0.64545 | 0.75073 | 0.11902 | 0.95215 | 0.78278 | 0.55847 | -123.0377 | 123.1064 | 123.024 | 2.8061 | -123.0103
1408.6562 | 122.9187 | -0.78278 | 122.1771 | -0.25588 | 0.020985 | 0.025039 | 0.36182 | -0.040597 | -0.013404 | -0.026399 | -0.31401 | -0.022933 | 0.049852 | 0.029578 | 0.016315 | 0.062914 | -0.032043 | 0.009155 | -0.33875 | -0.73242 | 0.25177 | -0.81024 | -0.95673 | -0.1831 | 1.6571 | -0.27924 | 122.4564 | 122.319 | -0.86975 | -0.87433 | -0.027466 | -0.17395 | -121.9254 | 0.79193 | 0.050354 | 0.2243 | -122.2092 | -0.086975 | -0.091553 | 0.27924 | 0.59967 | 0.50354 | 0.59509 | 0.14191 | 1.0345 | 0.75073 | 0.44403 | -123.1339 | 123.2391 | 123.1018 | 2.4399 | -123.0515
1409.6406 | 122.6807 | -0.82398 | 122.1222 | 0.32395 | 0.071187 | -0.00059506 | 0.37784 | -0.02778 | 0.0047541 | -0.016786 | -0.039353 | -0.016524 | 0.060533 | 0.047736 | 0.034473 | 0.06505 | 0 | 0.004578 | -0.35706 | -0.74616 | 0.20599 | -0.8194 | -0.94757 | -0.32501 | 1.7532 | -0.30212 | 122.3557 | 122.2366 | -0.92468 | -0.94757 | 0.004578 | -0.1236 | -121.9162 | 0.82855 | 0.07782 | 0.20142 | -122.1222 | -0.10071 | -0.1236 | 0.23346 | 0.49896 | 0.52185 | 0.64545 | 0.11444 | 1.03 | 0.82398 | 0.46692 | -123.0698 | 123.1796 | 123.0606 | 2.5772 | -123.0698
1410.6406 | 122.9462 | -0.78735 | 122.1863 | 0.46128 | 0.043416 | 0.011154 | 0.37357 | -0.05021 | -0.00058594 | -0.01999 | 0.20479 | -0.038954 | 0.07335 | 0.029578 | 0.038745 | 0.070391 | -0.036621 | -0.032043 | -0.38452 | -0.75531 | 0.22888 | -0.81482 | -0.96588 | -0.27008 | 1.5335 | -0.23346 | 122.4014 | 122.3007 | -0.87433 | -0.88806 | -0.027465 | -0.17853 | -121.9574 | 0.75531 | 0.032044 | 0.21057 | -122.2229 | -0.086975 | -0.10071 | 0.21515 | 0.51727 | 0.5539 | 0.6546 | 0.11444 | 1.0162 | 0.75073 | 0.40283 | -123.1522 | 123.1888 | 123.0881 | 2.3209 | -123.0743
1411.6406 | 122.8546 | -0.78735 | 122.168 | 0.36973 | 0.055165 | 0.0068819 | 0.36716 | -0.039529 | -0.00058594 | -0.025331 | 0.18953 | -0.03575 | 0.066941 | 0.043464 | 0.033405 | 0.072527 | -0.032043 | -0.054932 | -0.37537 | -0.74616 | 0.23346 | -0.80109 | -0.96588 | -0.33417 | 2.0645 | -0.28839 | 122.4014 | 122.3465 | -0.88806 | -0.88348 | -0.013732 | -0.17853 | -121.9345 | 0.73242 | 0.041199 | 0.21973 | -122.2 | -0.10071 | -0.09613 | 0.23346 | 0.45319 | 0.49896 | 0.59509 | 0.17853 | 1.0208 | 0.75531 | 0.41199 | -123.1338 | 123.1888 | 123.1339 | 2.8519 | -123.0515
1412.6406 | 123.0057 | -0.737 | 122.1863 | 0.44602 | 0.027394 | 0.017563 | 0.37784 | -0.038461 | -0.052924 | -0.025331 | 0.54048 | -0.040022 | 0.05092 | 0.040259 | 0.01311 | 0.086413 | 0.059509 | 0.10986 | -0.22888 | -0.66834 | 0.21057 | -0.73242 | -0.88348 | -0.23346 | 1.9363 | -0.13275 | 122.374 | 122.3099 | -0.82855 | -0.8606 | 0.004578 | -0.14648 | -121.9757 | 0.84686 | 0.068665 | 0.21515 | -122.1268 | -0.091552 | -0.1236 | 0.18768 | 0.50354 | 0.60425 | 0.72785 | 0.1236 | 0.94757 | 0.79651 | 0.50812 | -123.0698 | 123.111 | 123.0469 | 2.6733 | -123.0469
1413.6406 | 123.0103 | -0.73242 | 122.168 | 0.4918 | 0.039143 | -0.0038001 | 0.39707 | -0.039529 | -0.017676 | -0.026399 | 0.4947 | -0.030409 | 0.05626 | 0.042396 | 0.028064 | 0.067187 | 0.018311 | -0.004578 | -0.33875 | -0.68665 | 0.2243 | -0.77362 | -0.90637 | -0.28381 | 1.6525 | -0.17395 | 122.4106 | 122.3053 | -0.83313 | -0.84686 | -0.041199 | -0.17395 | -121.9437 | 0.72784 | 0.045776 | 0.21973 | -122.1497 | -0.10071 | -0.11444 | 0.24261 | 0.44861 | 0.55847 | 0.67291 | 0.13733 | 0.95673 | 0.75073 | 0.39368 | -123.0743 | 123.143 | 123.0377 | 2.3849 | -123.0148
1414.6406 | 122.9736 | -0.70038 | 122.2046 | 0.4918 | 0.022053 | 0.0047449 | 0.36823 | -0.047006 | -0.029426 | -0.039216 | 0.54048 | -0.032546 | 0.048783 | 0.038123 | 0.017383 | 0.081072 | 0.068665 | 0.09613 | -0.23346 | -0.63629 | 0.16937 | -0.71411 | -0.86975 | -0.23804 | 1.8631 | -0.10529 | 122.4197 | 122.3511 | -0.8194 | -0.82855 | -0.013733 | -0.16937 | -122.0352 | 0.79651 | 0.064086 | 0.23346 | -122.1359 | -0.11902 | -0.12817 | 0.21515 | 0.46234 | 0.59509 | 0.72327 | 0.14648 | 0.86975 | 0.76904 | 0.46692 | -123.0743 | 123.1201 | 123.0515 | 2.5635 | -123.0331
1415.6406 | 123.0057 | -0.71869 | 122.1542 | 0.56809 | 0.014576 | 0.0015409 | 0.36716 | -0.02778 | -0.021949 | -0.03708 | 0.571 | -0.038954 | 0.045579 | 0.039191 | 0.032337 | 0.072527 | 0.07782 | -0.21057 | -0.42114 | -0.62256 | 0.16479 | -0.78735 | -0.92468 | -0.25635 | 2.0187 | -0.11902 | 122.3831 | 122.3145 | -0.83313 | -0.82855 | -0.068665 | -0.20599 | -121.9894 | 0.50812 | 0.09613 | 0.30212 | -122.0764 | -0.11444 | -0.10986 | 0.22888 | 0.46234 | 0.59967 | 0.70953 | 0.16022 | 0.88348 | 0.79651 | 0.29755 | -123.0789 | 123.1018 | 123.0331 | 2.7374 | -122.9828
1416.6406 | 123.0469 | -0.72784 | 122.2092 | 0.20188 | -0.0046498 | 0.0047449 | 0.37143 | -0.055551 | -0.042243 | -0.03708 | 0.067459 | -0.038954 | 0.048783 | 0.038123 | 0.016315 | 0.075732 | 0.045776 | 0.07782 | -0.23804 | -0.63171 | 0.21515 | -0.72327 | -0.8606 | -0.26093 | 1.8402 | -0.086975 | 122.406 | 122.3328 | -0.81024 | -0.84228 | 0.004577 | -0.13275 | -121.994 | 0.80566 | 0.09613 | 0.22888 | -122.1634 | -0.082398 | -0.11444 | 0.19684 | 0.46692 | 0.64087 | 0.75531 | 0.1236 | 0.94299 | 0.77362 | 0.48981 | -123.0698 | 123.1339 | 123.0606 | 2.5681 | -123.0515
1417.6406 | 123.0057 | -0.72327 | 122.1954 | 0.29344 | 0.023121 | 0.010086 | 0.38532 | -0.040597 | -0.01554 | -0.042421 | 0.021682 | -0.038954 | 0.044511 | 0.021033 | 0.017383 | 0.078936 | -0.004578 | 0.036621 | -0.27008 | -0.66376 | 0.15106 | -0.77362 | -0.91095 | -0.27466 | 1.8631 | -0.1236 | 122.3969 | 122.3145 | -0.8194 | -0.82855 | -0.050354 | -0.18768 | -122.0444 | 0.75989 | 0.05951 | 0.24719 | -122.2 | -0.09613 | -0.10528 | 0.20142 | 0.44861 | 0.59967 | 0.70496 | 0.11902 | 0.87433 | 0.71869 | 0.45319 | -123.1064 | 123.1201 | 123.0377 | 2.5864 | -123.024
1418.6406 | 123.0057 | -0.75073 | 122.1542 | 0.50706 | 0.0092362 | -0.0048681 | 0.38211 | -0.051278 | -0.026221 | -0.036012 | 0.28108 | -0.03575 | 0.040239 | 0.031714 | 0.025928 | 0.075732 | 0.054932 | 0.068665 | -0.27008 | -0.66834 | 0.21057 | -0.74616 | -0.90637 | -0.29755 | 1.6479 | -0.17395 | 122.3831 | 122.2687 | -0.83771 | -0.87433 | 0.004577 | -0.15564 | -121.9437 | 0.8194 | 0.082397 | 0.23804 | -122.0993 | -0.086976 | -0.1236 | 0.22888 | 0.45319 | 0.57678 | 0.70038 | 0.11444 | 0.9613 | 0.80566 | 0.48065 | -123.0606 | 123.1338 | 123.0194 | 2.3987 | -123.0286
1419.6406 | 123.0057 | -0.75989 | 122.1542 | 0.2324 | 0.0017592 | -0.00059506 | 0.36609 | -0.039529 | -0.024085 | -0.036012 | 0.17427 | -0.046431 | 0.041307 | 0.029578 | 0.010974 | 0.075732 | 0.018311 | -0.20142 | -0.35706 | -0.76446 | 0.16479 | -0.82855 | -0.94757 | -0.31586 | 1.9226 | -0.17853 | 122.3694 | 122.2916 | -0.87433 | -0.87891 | -0.068664 | -0.18768 | -121.9894 | 0.55847 | -0.004577 | 0.18311 | -122.1359 | -0.11444 | -0.11902 | 0.21515 | 0.44403 | 0.58136 | 0.70038 | 0.13733 | 0.92468 | 0.7782 | 0.40283 | -123.1018 | 123.1293 | 123.0515 | 2.6825 | -123.0331
1420.6406 | 122.9919 | -0.81482 | 122.0764 | 0.26292 | -0.0025128 | 0.0079499 | 0.37891 | -0.039529 | -0.028357 | -0.044557 | 0.15901 | -0.028273 | 0.037034 | 0.032783 | 0.020587 | 0.070391 | 0.018311 | 0.07782 | -0.27924 | -0.71411 | 0.20599 | -0.79651 | -0.92926 | -0.32959 | 1.5701 | -0.19684 | 122.374 | 122.2412 | -0.89264 | -0.91095 | 0.01831 | -0.11444 | -121.8704 | 0.89264 | 0.10071 | 0.21515 | -122.0581 | -0.07782 | -0.096131 | 0.29755 | 0.48523 | 0.61798 | 0.71411 | 0.1648 | 1.0208 | 0.83313 | 0.53558 | -123.0057 | 123.1888 | 123.056 | 2.3849 | -122.9874
1421.6406 | 122.9965 | -0.80109 | 122.0901 | 0.38499 | 0.0071002 | 0.015426 | 0.40027 | -0.038461 | -0.025153 | -0.042421 | 0.22005 | -0.049636 | 0.051988 | 0.026374 | 0.021655 | 0.077868 | 0.045776 | 0.054932 | -0.29297 | -0.74616 | 0.21515 | -0.81024 | -0.9613 | -0.34332 | 1.767 | -0.24719 | 122.3145 | 122.2046 | -0.90179 | -0.93384 | -0.009156 | -0.16022 | -121.875 | 0.85602 | 0.054931 | 0.21515 | -122.0444 | -0.10071 | -0.13275 | 0.2243 | 0.45776 | 0.55389 | 0.68665 | 0.11444 | 1.0162 | 0.84686 | 0.50812 | -123.0515 | 123.1155 | 123.0057 | 2.5681 | -123.024
1422.6406 | 122.937 | -0.8606 | 121.8201 | -0.25588 | 0.026326 | 0.017563 | 0.37891 | -0.035257 | 0.014367 | -0.040284 | 3.5159 | -0.028273 | 0.043443 | 0.037055 | 0.033405 | 0.062914 | 0.009155 | 0 | -0.35248 | -0.78735 | 0.24261 | -0.85602 | -0.97961 | -0.36163 | 1.7487 | -0.33875 | 122.3831 | 122.2549 | -0.93842 | -0.95215 | 0.004578 | -0.11902 | -121.5775 | 0.8606 | 0.073242 | 0.19226 | -121.8109 | -0.07782 | -0.091552 | 0.56305 | 0.49896 | 0.52185 | 0.6134 | 0.43488 | 1.1032 | 0.86975 | 0.50812 | -122.7997 | 123.2437 | 123.1155 | 2.6093 | -122.7722
1423.6406 | 123.0148 | -0.86975 | 122.0856 | -0.17959 | -0.0099898 | 0.0079499 | 0.37036 | -0.030984 | -0.00058594 | -0.028535 | -0.75652 | -0.053908 | 0.038102 | 0.0456 | 0.017383 | 0.066119 | -0.11902 | 0.23346 | -0.21057 | -0.80109 | 0.17853 | -0.88806 | -1.0254 | -0.32044 | 1.9821 | -0.2655 | 122.2824 | 122.1634 | -0.97961 | -0.97046 | -0.018311 | -0.15564 | -121.907 | 1.1032 | 0.068665 | 0.2243 | -122.2046 | -0.10986 | -0.10071 | 0.19684 | 0.54932 | 0.60425 | 0.70496 | 0.07782 | 1.0483 | 0.75073 | 0.65918 | -123.111 | 123.1522 | 123.0331 | 2.8519 | -123.056
1424.6406 | 122.9187 | -0.89264 | 122.1085 | -0.22536 | 0.025258 | 0.014358 | 0.38959 | -0.045938 | -0.011268 | -0.031739 | -0.86333 | -0.038954 | 0.044511 | 0.025306 | 0.023792 | 0.056505 | -0.013733 | 0.022888 | -0.33417 | -0.83771 | 0.24261 | -0.90179 | -1.0391 | -0.46692 | 1.8311 | -0.40283 | 122.319 | 122.1542 | -1.0254 | -1.03 | -0.009155 | -0.14648 | -121.8658 | 0.91553 | 0.054931 | 0.20142 | -122.1222 | -0.13275 | -0.13733 | 0.21057 | 0.42572 | 0.48981 | 0.62714 | 0.045777 | 1.1353 | 0.87891 | 0.55847 | -123.1476 | 123.2117 | 123.0469 | 2.7237 | -123.1384
1425.6406 | 123.0743 | -0.78735 | 122.113 | -0.19484 | 0.028462 | 0.022903 | 0.36609 | -0.040597 | -0.031562 | -0.032808 | -0.28349 | -0.043227 | 0.054124 | 0.043464 | 0.012042 | 0.070391 | 0.068665 | 0.19684 | -0.19226 | -0.68207 | 0.19226 | -0.80566 | -0.92926 | -0.35248 | 2.0782 | -0.17853 | 122.3511 | 122.2 | -0.88348 | -0.89722 | -0.01831 | -0.14191 | -121.9208 | 0.98419 | 0.10529 | 0.24719 | -122.0444 | -0.09613 | -0.10986 | 0.23804 | 0.43488 | 0.60883 | 0.71869 | 0.086975 | 0.97962 | 0.85602 | 0.59509 | -123.0423 | 123.1384 | 122.9874 | 2.8656 | -123.0103
1426.6406 | 122.9141 | -0.76446 | 122.2504 | -0.25588 | 0.025258 | 0.011154 | 0.38745 | -0.03312 | -0.013404 | -0.034944 | -0.51238 | -0.027205 | 0.062669 | 0.033851 | 0.023792 | 0.060778 | -0.004578 | 0.050354 | -0.29755 | -0.70038 | 0.21973 | -0.75989 | -0.90637 | -0.3479 | 2.0828 | -0.2243 | 122.4609 | 122.3145 | -0.86517 | -0.87433 | 0.004577 | -0.14191 | -122.0306 | 0.81482 | 0.064087 | 0.20599 | -122.2549 | -0.10071 | -0.10986 | 0.21057 | 0.41656 | 0.54016 | 0.65003 | 0.064087 | 0.98419 | 0.75989 | 0.46692 | -123.1567 | 123.2254 | 123.0789 | 2.8473 | -123.1247
1427.6562 | 123.0103 | -0.71411 | 122.2137 | 0.50706 | 0.032734 | 0.026108 | 0.34793 | -0.036325 | -0.028357 | -0.046693 | 0.69307 | -0.033614 | 0.059465 | 0.029578 | 0.029132 | 0.075732 | 0.19226 | 0.068665 | -0.21973 | -0.59052 | 0.14191 | -0.75073 | -0.87433 | -0.2243 | 2.0142 | -0.10986 | 122.438 | 122.3007 | -0.79651 | -0.81024 | -0.036621 | -0.16022 | -122.0718 | 0.78278 | 0.1236 | 0.28381 | -122.0215 | -0.082398 | -0.096131 | 0.2243 | 0.48981 | 0.60425 | 0.70038 | 0.086975 | 0.85602 | 0.90637 | 0.49438 | -123.0881 | 123.1522 | 123.0148 | 2.7283 | -123.024
1428.6406 | 122.9279 | -0.7782 | 122.2366 | -0.25588 | 0.02419 | 0.0015409 | 0.38532 | -0.037393 | 0.0015501 | -0.028535 | -0.87859 | -0.017592 | 0.059465 | 0.030646 | 0.026996 | 0.074663 | 0.022888 | 0.35706 | -0.16479 | -0.73242 | 0.27924 | -0.74158 | -0.87891 | -0.32501 | 2.4216 | -0.24719 | 122.4564 | 122.3282 | -0.8606 | -0.87433 | 0.036621 | -0.10071 | -121.9574 | 1.1353 | 0.045776 | 0.14648 | -122.2137 | -0.082398 | -0.096131 | 0.21973 | 0.45319 | 0.53101 | 0.62714 | 0.091553 | 1.0574 | 0.80109 | 0.6134 | -123.1155 | 123.2346 | 123.1064 | 3.1998 | -123.111
1429.6406 | 122.9324 | -0.75073 | 122.2595 | -0.36269 | 0.013508 | -0.00059506 | 0.37677 | -0.035257 | -0.010199 | -0.029603 | -0.39031 | -0.022933 | 0.044511 | 0.0456 | 0.026996 | 0.074663 | 0.013733 | 0.07782 | -0.26093 | -0.63629 | 0.21973 | -0.74158 | -0.87433 | -0.33875 | 2.1103 | -0.19226 | 122.4655 | 122.3236 | -0.8194 | -0.8606 | 0.009155 | -0.1236 | -122.0398 | 0.82855 | 0.11444 | 0.23804 | -122.2458 | -0.068665 | -0.10986 | 0.20599 | 0.41199 | 0.55847 | 0.66834 | 0.064087 | 0.97046 | 0.76446 | 0.48981 | -123.1339 | 123.2162 | 123.0743 | 2.861 | -123.1201
1430.6406 | 122.7219 | -0.737 | 122.2778 | 0.064555 | 0.039143 | 0.0026089 | 0.38211 | -0.041665 | 0.010095 | -0.03708 | -0.26824 | -0.024001 | 0.058397 | 0.032783 | 0.034473 | 0.058642 | 0.059509 | 0.054932 | -0.27466 | -0.61798 | 0.2243 | -0.74616 | -0.87433 | -0.30212 | 1.9272 | -0.1831 | 122.4884 | 122.3373 | -0.83313 | -0.84228 | -0.009155 | -0.13733 | -122.0535 | 0.79193 | 0.11902 | 0.25635 | -122.2183 | -0.09613 | -0.10528 | 0.21057 | 0.43488 | 0.5539 | 0.65918 | 0.059509 | 0.9613 | 0.79651 | 0.46234 | -123.1522 | 123.2254 | 123.0743 | 2.6642 | -123.1201
1431.6406 | 122.9507 | -0.737 | 122.2778 | -0.25588 | 0.043416 | 0.017563 | 0.38745 | -0.047006 | 0.0047541 | -0.031739 | -0.42082 | -0.031478 | 0.05626 | 0.033851 | 0.025928 | 0.062914 | -0.027466 | 0.027466 | -0.3067 | -0.65002 | 0.20599 | -0.737 | -0.90637 | -0.31586 | 1.6571 | -0.19684 | 122.5113 | 122.3694 | -0.83313 | -0.82398 | 0 | -0.16937 | -122.0718 | 0.76447 | 0.086976 | 0.25635 | -122.3053 | -0.09613 | -0.086975 | 0.23346 | 0.42114 | 0.54016 | 0.62714 | 0.091553 | 0.94299 | 0.70953 | 0.4303 | -123.1842 | 123.2483 | 123.1064 | 2.3941 | -123.1018
1432.6406 | 123.0789 | -0.69122 | 122.2549 | 0.064555 | 0.025258 | 0.041061 | 0.37998 | -0.045938 | -0.042243 | -0.029603 | -0.22246 | -0.030409 | 0.037034 | 0.018897 | -0.0050469 | 0.08214 | 0.045776 | 0.18768 | -0.16479 | -0.59509 | 0.20599 | -0.68207 | -0.83771 | -0.16937 | 1.9638 | -0.041199 | 122.4289 | 122.3373 | -0.79193 | -0.80109 | 0.009155 | -0.14648 | -122.0489 | 0.87891 | 0.09613 | 0.24262 | -122.2092 | -0.10071 | -0.10986 | 0.17395 | 0.52185 | 0.65002 | 0.75989 | 0.082397 | 0.89722 | 0.737 | 0.52643 | -123.0927 | 123.1201 | 123.0286 | 2.655 | -123.056
1433.6406 | 122.9141 | -0.73242 | 122.2504 | -0.10329 | 0.045552 | 0.0047449 | 0.38745 | -0.026712 | 0.0036861 | -0.025331 | 0.021682 | -0.024001 | 0.063737 | 0.019965 | 0.025928 | 0.069323 | 0.041199 | 0.054932 | -0.27924 | -0.63171 | 0.22888 | -0.75531 | -0.90179 | -0.3067 | 1.7166 | -0.19226 | 122.4426 | 122.3373 | -0.84228 | -0.85144 | -0.022888 | -0.16937 | -122.0215 | 0.78735 | 0.10071 | 0.27008 | -122.2092 | -0.10986 | -0.11902 | 0.19226 | 0.42572 | 0.54016 | 0.65918 | 0.086975 | 0.9613 | 0.77362 | 0.45319 | -123.1522 | 123.175 | 123.0698 | 2.449 | -123.1018
1434.6406 | 122.9645 | -0.75989 | 122.2412 | 0.36973 | 0.049824 | -0.0027321 | 0.38104 | -0.038461 | 0.0015501 | -0.021058 | 0.35738 | -0.028273 | 0.055192 | 0.048804 | 0.025928 | 0.072527 | -0.013733 | -0.009155 | -0.33417 | -0.69122 | 0.24261 | -0.74616 | -0.88806 | -0.27924 | 1.7029 | -0.17395 | 122.4518 | 122.3236 | -0.83771 | -0.83771 | 0.013733 | -0.12817 | -121.9986 | 0.75073 | 0.068665 | 0.19684 | -122.2549 | -0.07782 | -0.07782 | 0.21057 | 0.48065 | 0.58594 | 0.66376 | 0.082397 | 1.0025 | 0.74616 | 0.42572 | -123.1293 | 123.2117 | 123.0835 | 2.4628 | -123.0789
1435.6406 | 122.9416 | -0.74616 | 122.2778 | 0.32395 | 0.06371 | 0.0036769 | 0.37891 | -0.037393 | 0.0026181 | -0.022126 | 0.26582 | -0.033614 | 0.058397 | 0.042396 | 0.020587 | 0.070391 | -0.022888 | -0.054932 | -0.35706 | -0.69122 | 0.24719 | -0.73242 | -0.89722 | -0.37537 | 1.6388 | -0.22888 | 122.4792 | 122.3831 | -0.83313 | -0.8606 | 0.013733 | -0.15106 | -122.0306 | 0.69122 | 0.054932 | 0.20599 | -122.3007 | -0.086975 | -0.11444 | 0.20142 | 0.37079 | 0.51727 | 0.63171 | 0.10529 | 0.99335 | 0.72327 | 0.3891 | -123.175 | 123.2254 | 123.1293 | 2.3849 | -123.1384
1436.6406 | 123.0606 | -0.70496 | 122.2229 | 0.64439 | 0.044484 | 0.0090179 | 0.38211 | -0.038461 | -0.010199 | -0.021058 | 0.40315 | -0.027205 | 0.062669 | 0.038123 | 0.021655 | 0.078936 | 0.054932 | 0.10529 | -0.26093 | -0.6134 | 0.19684 | -0.72327 | -0.87433 | -0.27008 | 2.1881 | -0.10986 | 122.4243 | 122.3145 | -0.78735 | -0.82855 | -0.018311 | -0.16937 | -122.0261 | 0.81024 | 0.091553 | 0.26093 | -122.168 | -0.082398 | -0.1236 | 0.20142 | 0.43488 | 0.59509 | 0.71869 | 0.091553 | 0.90179 | 0.75989 | 0.44403 | -123.0972 | 123.1293 | 123.0194 | 2.8931 | -123.0515
1437.6406 | 122.9507 | -0.74616 | 122.2549 | -0.27114 | 0.035939 | 0.01329 | 0.37891 | -0.034188 | -0.0091309 | -0.038148 | -0.31401 | -0.031478 | 0.047715 | 0.042396 | 0.032337 | 0.067187 | -0.013733 | 0 | -0.32044 | -0.66376 | 0.21515 | -0.75531 | -0.89722 | -0.33875 | 1.6251 | -0.17853 | 122.493 | 122.3694 | -0.82855 | -0.85602 | -0.009155 | -0.15106 | -122.0398 | 0.74616 | 0.082398 | 0.23346 | -122.2687 | -0.082397 | -0.10986 | 0.23804 | 0.40741 | 0.56763 | 0.67749 | 0.11444 | 0.9613 | 0.73242 | 0.42572 | -123.1522 | 123.2391 | 123.1155 | 2.3712 | -123.111
1438.6406 | 122.9828 | -0.74158 | 122.2366 | 0.43077 | 0.056233 | 0.0026089 | 0.37464 | -0.036325 | -0.01554 | -0.022126 | 0.40315 | -0.028273 | 0.079759 | 0.031714 | 0.0302 | 0.066119 | -0.018311 | 0.004578 | -0.34332 | -0.67749 | 0.22888 | -0.74616 | -0.88806 | -0.27924 | 1.5839 | -0.16937 | 122.4655 | 122.3511 | -0.82398 | -0.83313 | -0.004578 | -0.14648 | -122.0078 | 0.74616 | 0.064087 | 0.21057 | -122.2549 | -0.082398 | -0.091553 | 0.22888 | 0.46234 | 0.5722 | 0.66376 | 0.11444 | 0.97046 | 0.72327 | 0.39825 | -123.1247 | 123.2071 | 123.0927 | 2.3254 | -123.0698
1439.6406 | 123.0927 | -0.69122 | 122.2504 | 0.61387 | 0.059437 | 0.0026089 | 0.37464 | -0.036325 | -0.027289 | -0.025331 | 0.4947 | -0.028273 | 0.064805 | 0.030646 | 0.020587 | 0.078936 | 0.082397 | 0.082397 | -0.21973 | -0.59509 | 0.20599 | -0.70038 | -0.84228 | -0.17853 | 1.7853 | -0.07782 | 122.4243 | 122.3602 | -0.79651 | -0.80109 | -0.009155 | -0.15106 | -122.0444 | 0.77362 | 0.09613 | 0.24719 | -122.168 | -0.10529 | -0.10986 | 0.17395 | 0.5127 | 0.6134 | 0.72327 | 0.10986 | 0.89722 | 0.77362 | 0.4715 | -123.0927 | 123.1155 | 123.0515 | 2.4765 | -123.0515
1440.6406 | 123.0423 | -0.71869 | 122.2366 | 0.50706 | 0.040211 | -0.00059506 | 0.37357 | -0.037393 | -0.010199 | -0.026399 | 0.41841 | -0.031478 | 0.071214 | 0.039191 | 0.021655 | 0.072527 | 0.073242 | 0.054932 | -0.26093 | -0.59509 | 0.19684 | -0.71411 | -0.85602 | -0.24261 | 1.6296 | -0.086975 | 122.4335 | 122.3648 | -0.79193 | -0.81024 | 0.004578 | -0.13733 | -122.0398 | 0.77362 | 0.1236 | 0.26092 | -122.1634 | -0.073242 | -0.091553 | 0.19684 | 0.47607 | 0.63171 | 0.72327 | 0.12817 | 0.91553 | 0.79193 | 0.45776 | -123.0927 | 123.1522 | 123.0835 | 2.3483 | -123.0469
1441.6406 | 123.0515 | -0.6958 | 122.2183 | 0.56809 | 0.028462 | 0.0079499 | 0.37677 | -0.043802 | -0.010199 | -0.023195 | 0.46419 | -0.038954 | 0.049852 | 0.033851 | 0.026996 | 0.067187 | 0.091553 | 0.09613 | -0.23804 | -0.59052 | 0.20599 | -0.70496 | -0.8606 | -0.26093 | 1.5381 | -0.09613 | 122.438 | 122.3694 | -0.81024 | -0.79651 | -0.009155 | -0.1648 | -122.0123 | 0.79193 | 0.10529 | 0.27008 | -122.1268 | -0.11444 | -0.10071 | 0.21973 | 0.43488 | 0.59967 | 0.70038 | 0.15106 | 0.9018 | 0.78735 | 0.45776 | -123.0789 | 123.1339 | 123.0652 | 2.2339 | -123.0148
1442.6406 | 122.9645 | -0.70953 | 122.2504 | -0.31691 | 0.044484 | 0.0026089 | 0.36716 | -0.030984 | -0.0048589 | -0.041353 | -0.22246 | -0.026137 | 0.046647 | 0.046668 | 0.043018 | 0.05971 | 0.059509 | 0.022888 | -0.29297 | -0.64545 | 0.23346 | -0.73242 | -0.87891 | -0.25177 | 1.6067 | -0.16937 | 122.4792 | 122.4152 | -0.83313 | -0.85144 | -0.022888 | -0.16937 | -122.0169 | 0.73242 | 0.064087 | 0.23346 | -122.1909 | -0.1236 | -0.14191 | 0.22888 | 0.45776 | 0.54016 | 0.68207 | 0.16479 | 0.94299 | 0.76904 | 0.41657 | -123.1293 | 123.1888 | 123.1247 | 2.3163 | -123.1018
1443.6406 | 122.2366 | -0.64545 | 122.2824 | 0.52232 | 0.032734 | 0.019699 | 0.36823 | -0.039529 | -0.0080629 | -0.029603 | 0.73885 | -0.033614 | 0.05626 | 0.040259 | 0.020587 | 0.08214 | 0.07782 | 0.091553 | -0.23804 | -0.55847 | 0.17853 | -0.64087 | -0.80109 | 0.022888 | 4.541 | -0.045776 | 122.4564 | 122.3877 | -0.74616 | -0.75989 | 0.004578 | -0.15564 | -122.1039 | 0.737 | 0.086975 | 0.24261 | -122.2046 | -0.10071 | -0.11444 | 0.17395 | 0.66834 | 0.59967 | 0.71411 | 0.10528 | 0.82398 | 0.72327 | 0.40741 | -123.0835 | 123.1018 | 123.0331 | 5.1865 | -123.0423
1444.6406 | 122.9004 | -0.6546 | 122.1359 | 0.43077 | 0.019917 | 0.012222 | 0.37143 | -0.035257 | -0.036902 | -0.038148 | 0.50996 | -0.036818 | 0.049852 | 0.041327 | 0.01311 | 0.075732 | 0.027466 | 0.064087 | -0.23804 | -0.59509 | 0.21057 | -0.65918 | -0.81024 | 0.31586 | 2.1194 | -0.07782 | 122.5296 | 122.4014 | -0.75989 | -0.78735 | -0.004578 | -0.15564 | -121.9254 | 0.71869 | 0.059509 | 0.21515 | -122.1085 | -0.10529 | -0.13275 | 0.39368 | 0.97046 | 0.57678 | 0.70953 | 0.2655 | 0.86517 | 0.68207 | 0.41657 | -122.9462 | 123.1842 | 123.056 | 2.774 | -122.9233
1445.6406 | 122.4564 | -0.63629 | 122.1451 | 0.46128 | 0.028462 | 0.0090179 | 0.3757 | -0.047006 | -0.027289 | -0.03708 | 0.76936 | -0.040022 | 0.03917 | 0.043464 | 0.015247 | 0.070391 | 0.073242 | 0.10529 | -0.23346 | -0.55847 | 0.21057 | -0.62714 | -0.76904 | -0.041199 | 3.2455 | -0.054932 | 122.5342 | 122.4243 | -0.74158 | -0.74616 | 0.009156 | -0.13275 | -121.9345 | 0.74158 | 0.07782 | 0.21057 | -122.0718 | -0.10529 | -0.10986 | 0.3891 | 0.59509 | 0.58136 | 0.69122 | 0.27923 | 0.84686 | 0.70953 | 0.40283 | -122.9141 | 123.1705 | 123.0606 | 3.8818 | -122.8912
1446.6406 | 122.4335 | -0.63629 | 122.3648 | 0.034038 | 0.013508 | 0.010086 | 0.36609 | -0.040597 | -0.035834 | -0.043489 | 0.082718 | -0.044295 | 0.049852 | 0.042396 | 0.015247 | 0.073595 | 0.091553 | 0.14191 | -0.17853 | -0.52185 | 0.21515 | -0.62714 | -0.7782 | -0.091553 | 1.8951 | 0.009155 | 122.493 | 122.4152 | -0.75989 | -0.75989 | 0.009156 | -0.14191 | -122.1497 | 0.7782 | 0.11444 | 0.25635 | -122.2733 | -0.1236 | -0.1236 | 0.12817 | 0.54474 | 0.64545 | 0.76904 | 0.050354 | 0.85144 | 0.72784 | 0.45776 | -123.143 | 123.1293 | 123.0515 | 2.5314 | -123.1247
1447.6406 | 111.026 | -0.93842 | 98.1766 | 0.50706 | 0.043416 | -0.0070041 | 0.37036 | -0.040597 | 0.0026181 | -0.027467 | 0.3116 | -0.031478 | 0.047715 | 0.049872 | 0.026996 | 0.060778 | 0.004578 | -0.036621 | -0.36621 | -0.66376 | 0.24719 | -0.71411 | -0.86975 | -0.21057 | 2.4033 | -0.20599 | 122.5388 | 122.3923 | -0.81024 | -0.81024 | 0.2243 | 0.068665 | -97.9294 | 0.9018 | 0.27466 | 0.20599 | -98.172 | 0.12817 | 0.12817 | 24.3622 | 0.72785 | 0.73242 | 0.60425 | 24.2157 | 1.1856 | 0.94299 | 0.57221 | -99.0463 | 123.4772 | 123.3307 | 3.3417 | -98.9868
1448.6406 | 122.5296 | -0.74158 | 121.6461 | 0.049296 | -0.012126 | 0.012222 | 0.36182 | -0.034188 | -0.040107 | -0.029603 | 0.12849 | -0.046431 | 0.044511 | 0.032783 | 0.0056341 | 0.068255 | 0.018311 | 0.073242 | -0.24261 | -0.6546 | 0.1831 | -0.74158 | -0.90637 | -0.18768 | 2.2247 | -0.11902 | 122.4106 | 122.3236 | -0.83771 | -0.85144 | 0 | -0.16479 | -121.463 | 0.81482 | 0.086975 | 0.25177 | -121.6278 | -0.096131 | -0.10986 | 0.76447 | 0.55389 | 0.62256 | 0.73242 | 0.67749 | 0.92468 | 0.75989 | 0.49896 | -122.5525 | 123.1522 | 123.0652 | 2.9663 | -122.4976
1449.6406 | 122.5708 | -0.737 | 121.5775 | 0.21714 | 0.0071002 | 0.011154 | 0.37464 | -0.028848 | -0.033698 | -0.040284 | 0.61677 | -0.037886 | 0.032762 | 0.041327 | 0.017383 | 0.0768 | 0.004578 | 0.064087 | -0.2655 | -0.64087 | 0.20142 | -0.72327 | -0.87891 | -0.20599 | 2.2476 | -0.13733 | 122.4243 | 122.3282 | -0.85602 | -0.86517 | 0.013733 | -0.14191 | -121.376 | 0.80109 | 0.096131 | 0.23804 | -121.5729 | -0.11902 | -0.12817 | 0.84686 | 0.53101 | 0.59967 | 0.72784 | 0.75073 | 0.93842 | 0.74158 | 0.4715 | -122.4564 | 123.1613 | 123.0652 | 2.9846 | -122.4426
1450.6406 | 122.3328 | -0.6546 | 117.3111 | -0.19484 | 0.0060322 | 0.016495 | 0.37143 | -0.037393 | -0.029426 | -0.030671 | -0.29875 | -0.045363 | 0.03383 | 0.021033 | 0.029132 | 0.058642 | 0.068665 | 0.15106 | -0.19226 | -0.58136 | 0.21057 | -0.6958 | -0.83771 | -0.11902 | 1.9775 | -0.086975 | 122.4701 | 122.3511 | -0.80109 | -0.8194 | -0.041199 | -0.18311 | -117.1005 | 0.80566 | 0.073242 | 0.25635 | -117.2424 | -0.14648 | -0.1648 | 5.159 | 0.53558 | 0.56763 | 0.73242 | 5.04 | 0.86517 | 0.72327 | 0.46234 | -118.1488 | 123.1247 | 123.0057 | 2.6321 | -118.1305
1451.6406 | 122.3694 | -0.65002 | 121.2158 | -0.042256 | 0.01244 | 0.022903 | 0.37357 | -0.043802 | -0.011268 | -0.040284 | -0.11565 | -0.048567 | 0.026353 | 0.037055 | 0.020587 | 0.066119 | 0.082397 | 0.16022 | -0.17853 | -0.56763 | 0.20599 | -0.67749 | -0.84686 | -0.11902 | 2.0966 | -0.050354 | 122.4609 | 122.3373 | -0.79651 | -0.80109 | -0.027466 | -0.19684 | -121.0098 | 0.81024 | 0.082397 | 0.27924 | -121.1334 | -0.14648 | -0.15106 | 1.2451 | 0.53101 | 0.59967 | 0.75073 | 1.1215 | 0.85602 | 0.73242 | 0.4715 | -122.0627 | 123.111 | 122.9874 | 2.7466 | -122.0169
1452.6406 | 122.5204 | -0.70953 | 121.8246 | 0.43077 | 0.0071002 | -0.0027321 | 0.36609 | -0.037393 | -0.020881 | -0.031739 | 0.37263 | -0.049636 | 0.040239 | 0.018897 | 0.023792 | 0.070391 | 0.068665 | 0.11444 | -0.24261 | -0.60883 | 0.21515 | -0.72327 | -0.82855 | -0.17395 | 1.6571 | -0.1236 | 122.4701 | 122.3419 | -0.80109 | -0.81024 | -0.013733 | -0.11902 | -121.6095 | 0.82398 | 0.10071 | 0.21973 | -121.756 | -0.091552 | -0.10071 | 0.64545 | 0.53558 | 0.58594 | 0.68665 | 0.51727 | 0.92468 | 0.7782 | 0.46692 | -122.6532 | 123.1796 | 123.0515 | 2.3666 | -122.6349
1453.6406 | 122.2458 | -0.58594 | 112.0468 | -0.17959 | 0.0049632 | 0.0079499 | 0.36289 | -0.032052 | -0.0048589 | -0.01465 | -0.35979 | -0.043227 | 0.046647 | 0.02851 | 0.025928 | 0.05971 | -0.11444 | 0.20142 | -0.13275 | -0.60425 | 0.17853 | -0.68665 | -0.84686 | -0.1236 | 2.6138 | -0.068665 | 122.493 | 122.3648 | -0.78278 | -0.78278 | -0.10071 | -0.26093 | -111.8683 | 0.78735 | -0.018311 | 0.24262 | -112.1613 | -0.19684 | -0.19684 | 10.4462 | 0.46234 | 0.51727 | 0.71411 | 10.318 | 0.76447 | 0.4715 | 0.45319 | -112.8937 | 123.0789 | 122.9507 | 3.1998 | -112.8296
1454.6406 | 100.8041 | -0.86975 | 95.5811 | -0.22536 | 0.013508 | 0.011154 | 0.38639 | -0.032052 | -0.0059269 | -0.021058 | 3.3786 | -0.03575 | 0.046647 | 0.050941 | 0.036609 | 0.055437 | -0.004578 | 0 | -0.32044 | -0.63171 | 0.23804 | -0.70953 | -0.83771 | -0.19226 | 2.2842 | -0.17853 | 122.5845 | 122.4197 | -0.76446 | -0.78278 | 0.16022 | 0.032043 | -95.343 | 0.86975 | 0.23804 | 0.20599 | -95.5856 | 0.10529 | 0.086975 | 27.0035 | 0.67749 | 0.69122 | 0.60425 | 26.8387 | 1.1078 | 0.86517 | 0.54932 | -96.4188 | 123.4543 | 123.2895 | 3.154 | -96.3638
1455.6406 | 122.7951 | -106.3339 | 16.2964 | 0.88853 | 0.043416 | 0.073105 | 0.31055 | 0.074759 | -0.0037909 | -0.033876 | -0.61919 | 3.0789 | 0.057328 | 0.061622 | 2.9675 | 0.068255 | -0.009155 | -0.004578 | -26.2939 | -106.5537 | 0.20142 | -106.5765 | -106.5765 | -105.1025 | -2.0645 | 0.32044 | 16.0309 | 15.9622 | -106.4346 | -106.4255 | -0.24262 | -0.24262 | -16.095 | 106.3293 | -0.21973 | 0.022888 | -16.3055 | -0.10071 | -0.091553 | -0.2655 | 1.2314 | 106.6544 | 106.7459 | -0.33417 | 106.5353 | 106.3248 | 80.04 | -122.8729 | 122.3648 | 122.2961 | 104.2694 | -122.7219
1456.6406 | 122.731 | -98.1445 | 24.3851 | -0.24062 | 0.02419 | 0.067764 | 0.31696 | 0.079032 | -0.0080629 | -0.022126 | -0.78703 | 2.8984 | 0.051988 | 0.038123 | 2.7945 | 0.0768 | -0.10986 | 0.068665 | -23.2086 | -97.8195 | 0.19226 | -98.0392 | -98.0347 | -96.6431 | -8.2352 | 4.454 | 24.6277 | 24.4949 | -98.259 | -98.291 | 0.10528 | 0.10986 | -24.1928 | 98.2132 | 0.32501 | 0.21515 | -24.4949 | -0.11444 | -0.14648 | 0.24262 | 1.5015 | 102.5986 | 102.7451 | 0.10986 | 98.3368 | 98.0347 | 74.9359 | -122.4197 | 122.7722 | 122.6395 | 89.9094 | -122.6761
1457.6406 | 93.3517 | -69.3375 | 51.6083 | -0.25588 | 0.031666 | 0.046402 | 0.32443 | 0.029898 | 0.00048206 | -0.032808 | -0.69548 | 2.7478 | 0.044511 | 0.035987 | 2.7261 | 0.062914 | -0.045776 | 0.059509 | -14.0259 | -59.4543 | 0.19684 | -60.0586 | -59.761 | -58.0765 | 1.1856 | 37.9303 | 62.8235 | 61.7844 | -63.1531 | -65.9821 | 9.2789 | 9.5764 | -51.4114 | 69.397 | 9.8831 | 0.3067 | -51.6541 | 6.1844 | 3.3554 | 11.2152 | 11.261 | 107.2678 | 103.9124 | 10.1761 | 69.5343 | 69.2917 | 55.3116 | -111.3693 | 132.1609 | 131.1218 | 70.5231 | -117.5903
1458.6406 | 122.1497 | -73.3887 | 28.299 | -0.042256 | 0.10537 | 0.05281 | 0.28064 | 0.14419 | 0.048547 | -0.018922 | -0.57341 | 2.9678 | 0.032762 | 0.027442 | 2.8319 | 0.071459 | -0.65002 | 1.0666 | -22.6135 | -92.7109 | 0.15106 | -30.6519 | -18.9972 | -94.1116 | -3.6438 | 5.8182 | 27.3605 | 27.269 | -62.59 | -31.9107 | 42.7368 | 54.3915 | -28.1479 | 74.4553 | -19.3222 | -73.7137 | -28.949 | 10.7986 | 41.478 | -0.93842 | -20.723 | 79.2068 | 37.7289 | -1.03 | 73.5397 | 72.7386 | 50.7751 | -47.2961 | 100.7492 | 100.6577 | 69.7449 | -60.2097
1459.6406 | 122.5571 | -92.5369 | 24.2981 | -0.042256 | 0.16945 | 0.03038 | 0.31055 | 0.0801 | 0.0058221 | -0.016786 | -0.43608 | 2.8439 | 0.043443 | 0.030646 | 2.7347 | 0.084276 | -0.036621 | 0.32959 | -23.8586 | -88.4857 | 0.17853 | -80.9738 | -74.9176 | -97.4762 | -1.3367 | 0.74616 | 23.703 | 23.7305 | -84.343 | -79.7882 | 11.5631 | 17.6193 | -24.1196 | 92.8665 | 4.0512 | -13.5681 | -24.3347 | 8.194 | 12.7487 | -0.59509 | -4.9393 | 93.2831 | 80.5344 | -0.56763 | 92.7155 | 92.5003 | 68.6783 | -99.2157 | 116.2399 | 116.2674 | 91.2003 | -104.0863
1460.6406 | 122.699 | -90.4678 | 27.0218 | -0.7289 | 0.14382 | 0.038925 | 0.30734 | 0.079032 | 0.0036861 | -0.0082413 | 0.021682 | 2.7766 | 0.054124 | 0.026374 | 2.6311 | 0.072527 | -0.23804 | 0.65918 | -23.5016 | -108.3893 | 0.14191 | -71.2784 | -50.9949 | -94.6976 | -1.0941 | -0.15106 | 26.8707 | 26.9806 | -68.4906 | -61.4365 | 19.1895 | 39.473 | -26.8799 | 91.127 | -17.9214 | -57.3944 | -27.2598 | 21.9772 | 29.0314 | -0.15106 | -4.2297 | 90.3168 | 61.2854 | -0.041199 | 90.6097 | 90.2298 | 66.9662 | -78.0167 | 117.3386 | 117.4484 | 89.3738 | -88.4583
1461.6406 | 122.6166 | -93.1412 | 29.2236 | -0.026997 | 0.04662 | 0.053879 | 0.32443 | 0.068351 | -0.0016549 | -0.023195 | 0.082718 | 2.7221 | 0.069078 | 0.038123 | 2.63 | 0.0768 | 0.004578 | 0.07782 | -22.8973 | -93.7729 | 0.20599 | -92.8162 | -92.9718 | -92.0242 | -2.1606 | 0.009155 | 29.1046 | 29.0726 | -93.1458 | -93.2465 | 0.32501 | 0.16937 | -29.0176 | 93.219 | -0.63171 | -0.80109 | -29.2191 | -0.004578 | -0.10529 | -0.11902 | 1.1169 | 93.1503 | 93.2556 | -0.15106 | 93.3472 | 93.1458 | 70.2438 | -122.1954 | 122.2458 | 122.2137 | 90.9805 | -122.4701
1462.6406 | 122.6532 | -92.8574 | 29.4754 | 0.11033 | 0.047688 | 0.045334 | 0.32337 | 0.071555 | -0.00058594 | -0.036012 | -0.39031 | 2.6655 | 0.042375 | 0.030646 | 2.5745 | 0.071459 | 0.068665 | 0.027466 | -22.5998 | -92.4408 | 0.25177 | -93.2922 | -93.457 | -92.6743 | -2.298 | -0.17853 | 28.8757 | 29.0039 | -92.6331 | -92.3859 | -0.43488 | -0.59967 | -29.2236 | 92.8848 | 0.41656 | 1.0162 | -29.4067 | 0.2243 | 0.4715 | -0.59967 | 0.18311 | 92.6788 | 92.2073 | -0.4715 | 93.1091 | 92.926 | 70.2576 | -122.9324 | 121.7331 | 121.8613 | 90.5594 | -121.8613
1463.6406 | 122.2916 | -98.2727 | 24.028 | 0.034038 | 0.037007 | -0.041184 | 0.3757 | 0.079032 | 0.58367 | -0.01465 | -0.13091 | 3.3747 | 0.060533 | 0.042396 | 2.6984 | 0.062914 | -3.2181 | 0.013733 | -19.6838 | -1.6434 | 0.21973 | -97.7509 | -97.8928 | -96.1212 | -2.005 | -0.20142 | 24.3073 | 24.1837 | -98.1583 | -98.2315 | 0.52185 | 0.37994 | -23.8083 | 98.2864 | 96.6293 | 96.2494 | -27.2461 | 0.11444 | 0.041199 | 0.27924 | 2.1515 | 98.0713 | 98.0301 | 0.15564 | 98.4924 | 95.0546 | 78.5889 | -121.9208 | 122.58 | 122.4564 | 96.2677 | -122.2595
1464.6406 | 122.319 | -100.8636 | 21.5149 | 0.26292 | 0.034871 | 0.018631 | 0.37464 | 0.075827 | 0.61572 | -0.029603 | 0.15901 | 3.4816 | 0.064805 | 0.035987 | 2.7827 | 0.077868 | -3.4973 | -0.064087 | -19.9905 | -1.506 | 0.25177 | -101.3077 | -101.1566 | -99.2981 | -1.7349 | -0.21515 | 21.5195 | 21.492 | -100.8499 | -100.8957 | -0.44403 | -0.29297 | -21.2631 | 100.7996 | 99.3576 | 99.6506 | -25.0122 | 0.013732 | -0.032044 | 0.004577 | 1.5656 | 100.6485 | 100.6805 | -0.022889 | 101.1154 | 97.3663 | 80.8731 | -122.6715 | 122.3831 | 122.3557 | 99.1287 | -122.4106
1465.6406 | 122.4335 | -99.7192 | 22.6822 | 0.32395 | 0.033803 | -0.0048681 | 0.37891 | 0.072623 | 0.59008 | -0.018922 | 0.64729 | 3.442 | 0.061601 | 0.037055 | 2.7475 | 0.073595 | -3.4744 | -0.054932 | -19.0704 | -1.6525 | 0.21515 | -99.6872 | -99.7787 | -98.5977 | -1.3 | -0.24719 | 22.5677 | 22.5174 | -99.6231 | -99.646 | 0.032043 | -0.05951 | -22.467 | 99.6643 | 98.0667 | 98.1262 | -26.1566 | 0.09613 | 0.073242 | -0.11444 | 1.1215 | 99.472 | 99.3988 | -0.16479 | 99.9344 | 96.2448 | 80.6488 | -122.4609 | 122.287 | 122.2366 | 98.4192 | -122.3282
1466.6406 | 122.4472 | -103.9581 | 18.4296 | 1.682 | 0.041279 | 0.017563 | 0.37891 | 0.075827 | 0.61144 | -0.027467 | 0.7541 | 3.5745 | 0.063737 | 0.052009 | 2.8404 | 0.070391 | -3.6713 | -0.045776 | -19.7067 | -1.6159 | 0.23804 | -103.8895 | -104.0176 | -102.7908 | -1.3824 | -0.21973 | 18.2739 | 18.1824 | -103.8895 | -103.9261 | 0.068665 | -0.059509 | -18.1915 | 103.9124 | 102.3422 | 102.4017 | -22.1008 | 0.068665 | 0.032044 | -0.15564 | 1.1673 | 103.7384 | 103.7064 | -0.24719 | 104.1962 | 100.2869 | 84.2514 | -122.4472 | 122.2321 | 122.1405 | 102.5757 | -122.3557
1467.6406 | 122.4747 | -118.9178 | 3.447 | 0.47654 | 0.047688 | -0.0016631 | 0.37891 | 0.096122 | 0.71505 | -0.027467 | 0.70833 | 4.0861 | 0.069078 | 0.02851 | 3.2431 | 0.081072 | -4.2068 | -0.032043 | -23.3322 | -1.5656 | 0.2243 | -118.9499 | -119.0277 | -117.6636 | -1.6846 | -0.21515 | 3.1815 | 3.1448 | -118.8538 | -118.8812 | -0.032043 | -0.10986 | -3.2227 | 118.8858 | 117.3523 | 117.4622 | -7.6538 | 0.064087 | 0.036621 | -0.2655 | 1.2543 | 118.7027 | 118.6661 | -0.30212 | 119.1422 | 114.711 | 95.5856 | -122.4747 | 122.0993 | 122.0627 | 117.2333 | -122.3282
1468.6406 | 122.4976 | -118.9957 | 3.3096 | 0.58335 | 0.032734 | 0.011154 | 0.37891 | 0.099326 | 0.7033 | -0.027467 | 0.81514 | 4.1427 | 0.064805 | 0.041327 | 3.305 | 0.073595 | -4.1611 | 0.004578 | -22.9935 | -1.4236 | 0.2243 | -118.9774 | -119.0872 | -117.6361 | -1.5106 | -0.17395 | 3.0441 | 3.0121 | -118.9316 | -118.9453 | 0.018311 | -0.091552 | -3.0853 | 119.0002 | 117.572 | 117.6636 | -7.4707 | 0.064087 | 0.050355 | -0.2655 | 1.3596 | 118.8217 | 118.7714 | -0.29755 | 119.22 | 114.8346 | 96.0022 | -122.3969 | 122.0398 | 122.0078 | 117.485 | -122.2549
1469.6406 | 122.4838 | -119.101 | 3.1815 | 0.56809 | 0.033803 | 0.0058129 | 0.36823 | 0.1068 | 0.71398 | -0.039216 | 1.3187 | 4.1491 | 0.042375 | 0.030646 | 3.2997 | 0.063982 | -4.2938 | 0.045776 | -23.0118 | -1.3046 | 0.19226 | -119.0598 | -119.1788 | -117.8101 | -1.3916 | -0.1236 | 2.9114 | 2.8702 | -119.014 | -119.0369 | 0.041199 | -0.07782 | -2.9892 | 119.1467 | 117.7963 | 117.8741 | -7.4753 | 0.086975 | 0.064087 | -0.27008 | 1.2909 | 118.9774 | 118.9133 | -0.31128 | 119.2932 | 114.8071 | 96.0892 | -122.3602 | 122.0123 | 121.9711 | 117.7094 | -122.2183
1470.6406 | 122.4243 | -119.1238 | 3.1448 | 1.1479 | 0.034871 | 0.010086 | 0.37677 | 0.10039 | 0.70437 | -0.030671 | 0.93721 | 4.1363 | 0.037034 | 0.038123 | 3.3029 | 0.08214 | -4.2847 | 0.068665 | -22.9431 | -1.506 | 0.1831 | -119.0872 | -119.1971 | -117.8604 | -1.4191 | -0.11902 | 2.861 | 2.829 | -119.046 | -119.0781 | 0.036621 | -0.073243 | -2.9617 | 119.1925 | 117.6178 | 117.691 | -7.4295 | 0.077819 | 0.045776 | -0.28381 | 1.2634 | 119.0048 | 118.959 | -0.31586 | 119.3069 | 114.8392 | 96.1807 | -122.3419 | 121.9849 | 121.9528 | 117.7048 | -122.2229
1471.6406 | 122.4152 | -119.1147 | 3.1311 | 0.35447 | 0.010304 | 0.00047294 | 0.36716 | 0.089713 | 0.69369 | -0.031739 | 1.0288 | 4.1331 | 0.05092 | 0.050941 | 3.2944 | 0.085345 | -4.7424 | 0.091553 | -23.2498 | -1.6342 | 0.20599 | -119.046 | -119.1696 | -117.8604 | -1.3229 | -0.1236 | 2.8473 | 2.8107 | -119.0323 | -119.0506 | 0.068664 | -0.054932 | -2.9251 | 119.2062 | 117.4805 | 117.5354 | -7.8735 | 0.082397 | 0.064087 | -0.28381 | 1.2543 | 118.9911 | 118.927 | -0.32044 | 119.3207 | 114.3723 | 95.8649 | -122.3007 | 121.962 | 121.9254 | 117.7917 | -122.1817
1472.6406 | 122.438 | -119.0689 | 3.1677 | 0.58335 | 0.016713 | 0.0047449 | 0.37677 | 0.098258 | 0.69262 | -0.042421 | 0.55574 | 4.116 | 0.041307 | 0.037055 | 3.2826 | 0.078936 | -4.7607 | 0.050354 | -23.14 | -1.5518 | 0.19226 | -119.0506 | -119.1376 | -117.7826 | -1.2405 | -0.11902 | 2.8885 | 2.8427 | -119.0186 | -119.0094 | 0.018311 | -0.068664 | -2.9755 | 119.1193 | 117.5171 | 117.5858 | -7.9285 | 0.050354 | 0.05951 | -0.27924 | 1.2863 | 118.9499 | 118.8904 | -0.32501 | 119.2612 | 114.3082 | 95.929 | -122.3053 | 121.9574 | 121.9116 | 117.8284 | -122.1771
1473.6406 | 122.374 | -119.1193 | 3.0945 | 0.3087 | 0.0071002 | 0.0026089 | 0.36609 | 0.088645 | 0.69583 | -0.045625 | 0.55574 | 4.1384 | 0.046647 | 0.038123 | 3.2901 | 0.070391 | -4.8981 | 0.032043 | -22.966 | -1.4694 | 0.21973 | -119.0781 | -119.2062 | -117.9062 | -1.2222 | -0.16937 | 2.7557 | 2.7191 | -119.0918 | -119.0689 | 0.041199 | -0.086975 | -2.8748 | 119.1513 | 117.6498 | 117.7368 | -7.9926 | 0.027466 | 0.050354 | -0.33875 | 1.2131 | 118.9499 | 118.8995 | -0.37537 | 119.339 | 114.2212 | 96.1533 | -122.3007 | 121.875 | 121.8384 | 117.897 | -122.1634
1474.6406 | 122.3419 | -119.101 | 3.067 | -0.19484 | -0.0014448 | 0.0047449 | 0.36609 | 0.088645 | 0.69689 | -0.042421 | 0.2353 | 4.1374 | 0.034898 | 0.037055 | 3.2922 | 0.071459 | -4.8706 | 0.13275 | -22.6868 | -1.3458 | 0.19684 | -119.0781 | -119.1605 | -117.8421 | -1.4191 | -0.10986 | 2.8107 | 2.742 | -119.0872 | -119.0964 | 0.022888 | -0.059509 | -2.8702 | 119.2337 | 117.7551 | 117.8146 | -7.9376 | 0.013733 | 0.004577 | -0.25635 | 1.2589 | 118.9911 | 118.9865 | -0.32501 | 119.2978 | 114.2303 | 96.4142 | -122.2275 | 121.9116 | 121.843 | 117.6819 | -122.1634
1475.6406 | 122.4014 | -119.0552 | 3.1265 | -0.22536 | 0.0060322 | 0.0068819 | 0.36075 | 0.084372 | 0.68728 | -0.044557 | 0.2353 | 4.1192 | 0.05092 | 0.037055 | 3.2965 | 0.069323 | -4.985 | 0.15564 | -22.1237 | -1.4145 | 0.21057 | -119.0186 | -119.1147 | -117.8192 | -1.1948 | -0.10071 | 2.8336 | 2.7878 | -118.9728 | -119.0048 | 0.036621 | -0.059509 | -2.916 | 119.2108 | 117.6407 | 117.7002 | -8.1116 | 0.082398 | 0.050354 | -0.29297 | 1.236 | 118.9545 | 118.9041 | -0.33875 | 119.2657 | 114.0701 | 96.9315 | -122.2412 | 121.8887 | 121.843 | 117.8604 | -122.1313
1476.6406 | 122.3511 | -118.927 | 3.2272 | 1.4836 | -0.0035808 | 0.017563 | 0.38318 | 0.088645 | 0.67874 | -0.045625 | 0.34212 | 4.1192 | 0.058397 | 0.037055 | 3.2869 | 0.078936 | -5.1453 | 0.045776 | -22.0001 | -1.4786 | 0.16937 | -118.9178 | -119.0277 | -117.7689 | -1.2955 | -0.14191 | 2.9434 | 2.9205 | -118.8766 | -118.8904 | 0.009155 | -0.10071 | -3.0579 | 118.9728 | 117.4484 | 117.5491 | -8.3725 | 0.050354 | 0.036621 | -0.28381 | 1.1581 | 118.7851 | 118.7485 | -0.3067 | 119.0964 | 113.7817 | 96.9269 | -122.2549 | 121.8704 | 121.8475 | 117.6315 | -122.1176
1477.6406 | 122.3648 | -119.1147 | 3.035 | 0.17137 | 0.011372 | 0.0090179 | 0.36502 | 0.089713 | 0.69155 | -0.038148 | 0.29634 | 4.1331 | 0.03917 | 0.032783 | 3.289 | 0.077868 | -5.2689 | 0.10529 | -22.1603 | -1.5289 | 0.2243 | -119.1147 | -119.2017 | -117.9199 | -1.2543 | -0.10071 | 2.7328 | 2.6962 | -119.0643 | -119.0643 | 0 | -0.086975 | -2.8107 | 119.22 | 117.5858 | 117.6727 | -8.3038 | 0.050354 | 0.050354 | -0.30212 | 1.1948 | 119.014 | 118.9636 | -0.33874 | 119.339 | 113.8458 | 96.9543 | -122.2366 | 121.8475 | 121.8109 | 117.8604 | -122.0993
1478.6406 | 122.4289 | -119.2429 | 2.9251 | -0.2101 | 0.0028272 | 0.0047449 | 0.38425 | 0.092917 | 0.70223 | -0.030671 | 0.0522 | 4.1246 | 0.046647 | 0.021033 | 3.2869 | 0.068255 | -5.7404 | 0.14648 | -22.9431 | -1.3 | 0.1831 | -119.1788 | -119.252 | -117.9657 | -1.1261 | -0.1236 | 2.655 | 2.6047 | -119.1193 | -119.1238 | 0.064087 | -0.009155 | -2.742 | 119.3893 | 117.9428 | 117.952 | -8.6655 | 0.1236 | 0.11902 | -0.27008 | 1.2772 | 119.1193 | 119.0002 | -0.32044 | 119.426 | 113.5025 | 96.2997 | -122.1771 | 121.8979 | 121.8475 | 118.1168 | -122.049
1479.6406 | 122.3373 | -119.3481 | 2.7512 | 0.018779 | 0.0049632 | 0.022903 | 0.36609 | 0.090781 | 0.7033 | -0.038148 | -0.054612 | 4.1342 | 0.032762 | 0.02851 | 3.3008 | 0.068255 | -5.9235 | 0.19226 | -22.8333 | -1.4145 | 0.21515 | -119.3298 | -119.4214 | -118.103 | -1.2039 | -0.11444 | 2.4719 | 2.417 | -119.2841 | -119.2932 | 0.018311 | -0.073242 | -2.536 | 119.5404 | 117.9337 | 118.0069 | -8.6746 | 0.064087 | 0.054932 | -0.27924 | 1.2451 | 119.2337 | 119.1788 | -0.33417 | 119.5633 | 113.4247 | 96.5149 | -122.1725 | 121.8201 | 121.7651 | 118.1442 | -122.0444
1480.6406 | 122.2961 | -119.3298 | 2.8244 | -0.66787 | 0.0071002 | 0.019699 | 0.37143 | 0.087577 | 0.70437 | -0.031739 | -0.13091 | 4.1299 | 0.035966 | 0.032783 | 3.3072 | 0.06505 | -5.6488 | 0.14191 | -22.9248 | -1.4053 | 0.19226 | -119.3024 | -119.4122 | -118.103 | -1.3046 | -0.15106 | 2.5177 | 2.4536 | -119.2612 | -119.2841 | 0.027466 | -0.082397 | -2.6321 | 119.4717 | 117.9245 | 118.0069 | -8.4732 | 0.068665 | 0.045776 | -0.3067 | 1.2268 | 119.1788 | 119.133 | -0.37079 | 119.5221 | 113.681 | 96.405 | -122.2366 | 121.8475 | 121.7834 | 118.0252 | -122.1085
1481.6406 | 122.2275 | -119.339 | 2.8107 | -0.2101 | 0.023121 | 0.0047449 | 0.36716 | 0.084372 | 0.70544 | -0.031739 | -0.13091 | 4.1416 | 0.042375 | 0.030646 | 3.2965 | 0.067187 | -5.8273 | 0.10529 | -22.5403 | -1.1078 | 0.19684 | -119.2932 | -119.3893 | -118.071 | -1.4236 | -0.19684 | 2.5223 | 2.4811 | -119.2795 | -119.2932 | 0.045776 | -0.050354 | -2.6138 | 119.4443 | 118.2312 | 118.2816 | -8.638 | 0.059509 | 0.045776 | -0.28839 | 1.268 | 119.1422 | 119.0964 | -0.32959 | 119.5358 | 113.5117 | 96.7987 | -122.2 | 121.8613 | 121.8201 | 117.9153 | -122.1039
1482.6406 | 122.1542 | -119.3069 | 2.8748 | -0.2101 | 0.0071002 | 0.014358 | 0.37464 | 0.092917 | 0.72253 | -0.033876 | -1.0922 | 4.1416 | 0.034898 | 0.034919 | 3.2965 | 0.062914 | -5.7678 | 0.073242 | -22.6044 | -1.0071 | 0.22888 | -119.2566 | -119.3527 | -118.0344 | -1.7487 | -0.23346 | 2.5864 | 2.5085 | -119.2337 | -119.1971 | 0.050354 | -0.045776 | -2.6459 | 119.3802 | 118.2999 | 118.3456 | -8.6426 | 0.073242 | 0.10986 | -0.28839 | 1.2726 | 119.0735 | 118.9636 | -0.36621 | 119.5358 | 113.5391 | 96.7026 | -122.2275 | 121.8933 | 121.8155 | 117.5583 | -122.0718
1483.6406 | 122.1176 | -119.2703 | 2.9022 | -0.10329 | 0.010304 | 0.012222 | 0.38104 | 0.098258 | 0.70971 | -0.042421 | -0.28349 | 4.1395 | 0.047715 | 0.037055 | 3.2922 | 0.060778 | -5.8411 | 0.022888 | -22.4533 | -1.0803 | 0.23804 | -119.2429 | -119.3069 | -118.0847 | -1.7532 | -0.24719 | 2.6276 | 2.5681 | -119.1559 | -119.1834 | 0.027466 | -0.036621 | -2.6642 | 119.2932 | 118.19 | 118.2266 | -8.7433 | 0.11444 | 0.086975 | -0.27466 | 1.1856 | 119.0231 | 118.9362 | -0.33417 | 119.5084 | 113.4293 | 96.817 | -122.2092 | 121.8979 | 121.8384 | 117.5171 | -122.0856
1484.6406 | 122.1954 | -119.3527 | 2.7557 | -0.13381 | 0.039143 | 0.0047449 | 0.39173 | 0.096122 | 0.73748 | -0.029603 | -0.19194 | 4.1352 | 0.041307 | 0.049872 | 3.3082 | 0.068255 | -5.896 | 0.013733 | -22.467 | -1.1124 | 0.23346 | -119.3115 | -119.4031 | -118.1488 | -1.4282 | -0.24261 | 2.4857 | 2.4307 | -119.2841 | -119.2612 | 0.041199 | -0.050354 | -2.5223 | 119.3665 | 118.2404 | 118.2907 | -8.6517 | 0.068664 | 0.091553 | -0.27008 | 1.2039 | 119.1101 | 119.0186 | -0.32501 | 119.5862 | 113.4567 | 96.8857 | -122.1588 | 121.8384 | 121.7834 | 117.9245 | -122.0169
1485.6406 | 122.113 | -119.3573 | 2.7786 | 0.15611 | 0.034871 | 0.0058129 | 0.37784 | 0.098258 | 0.73214 | -0.021058 | 0.097976 | 4.1416 | 0.043443 | 0.02851 | 3.3104 | 0.068255 | -5.896 | 0.018311 | -22.9889 | -1.1169 | 0.21515 | -119.2886 | -119.3619 | -118.1717 | -1.4236 | -0.27924 | 2.4811 | 2.4445 | -119.2703 | -119.2612 | 0.068665 | -0.004577 | -2.5635 | 119.3756 | 118.2404 | 118.2449 | -8.6746 | 0.086975 | 0.096131 | -0.29755 | 1.1856 | 119.0781 | 118.9819 | -0.33417 | 119.5724 | 113.4613 | 96.3684 | -122.1405 | 121.8384 | 121.8018 | 117.9337 | -122.0398
1486.6406 | 122.1725 | -119.3161 | 2.7832 | -0.22536 | 0.047688 | 0.018631 | 0.37677 | 0.1036 | 0.71185 | -0.028535 | -0.17668 | 4.1395 | 0.049852 | 0.029578 | 3.2986 | 0.061846 | -6.1111 | 0 | -23.2681 | -1.1032 | 0.21973 | -119.3024 | -119.3527 | -118.1213 | -1.2589 | -0.2243 | 2.504 | 2.4582 | -119.2291 | -119.2245 | 0.013733 | -0.036621 | -2.5635 | 119.3161 | 118.2129 | 118.2495 | -8.8943 | 0.086975 | 0.091553 | -0.27924 | 1.1948 | 119.0918 | 119.0002 | -0.32501 | 119.5358 | 113.205 | 96.048 | -122.1359 | 121.8201 | 121.7743 | 118.0573 | -122.0078
1487.7031 | 122.0718 | -119.2841 | 2.8244 | -0.22536 | 0.032734 | 0.018631 | 0.3757 | 0.1036 | 0.69689 | -0.028535 | -0.87859 | 4.1427 | 0.043443 | 0.031714 | 3.2933 | 0.072527 | -6.0013 | 0.009155 | -22.9477 | -1.3733 | 0.2243 | -119.252 | -119.3344 | -118.1351 | -1.2222 | -0.23346 | 2.5681 | 2.5131 | -119.2154 | -119.2017 | 0.032044 | -0.050354 | -2.6001 | 119.2932 | 117.9108 | 117.9611 | -8.8257 | 0.068665 | 0.082398 | -0.25635 | 1.149 | 119.0506 | 118.9682 | -0.31128 | 119.5084 | 113.2828 | 96.3364 | -122.1588 | 121.8521 | 121.7972 | 118.0618 | -122.0261
1488.6406 | 122.1222 | -119.2612 | 2.8015 | -1.1104 | 0.058369 | -0.0091401 | 0.37357 | 0.086509 | 0.73107 | -0.021058 | 0.20479 | 4.1427 | 0.058397 | 0.031714 | 3.305 | 0.069323 | -5.8914 | 0.064087 | -22.9431 | -1.3641 | 0.2655 | -119.1971 | -119.2886 | -117.9428 | -1.1627 | -0.24261 | 2.536 | 2.4765 | -119.1605 | -119.1879 | 0.064086 | -0.027466 | -2.536 | 119.3253 | 117.897 | 117.9245 | -8.6929 | 0.10071 | 0.073242 | -0.2655 | 1.3184 | 119.0186 | 118.9453 | -0.32501 | 119.5267 | 113.3698 | 96.3181 | -122.0901 | 121.7972 | 121.7377 | 118.0984 | -121.9894
1489.6406 | 122.0673 | -119.0048 | 3.0762 | 0.27818 | 0.056233 | 0.0058129 | 0.38318 | 0.099326 | 0.72466 | -0.018922 | 0.17427 | 4.1299 | 0.062669 | 0.026374 | 3.2986 | 0.077868 | -5.9921 | -0.013733 | -23.0255 | -1.4099 | 0.21973 | -118.9499 | -119.046 | -117.8329 | -1.2543 | -0.27466 | 2.8061 | 2.7374 | -118.8812 | -118.927 | 0.054932 | -0.041199 | -2.8564 | 118.9911 | 117.5949 | 117.6361 | -9.0683 | 0.1236 | 0.07782 | -0.27008 | 1.1719 | 118.7302 | 118.6523 | -0.33875 | 119.2245 | 113.0127 | 95.9793 | -122.1222 | 121.8109 | 121.7422 | 117.7506 | -122.0032
1490.6406 | 122.0398 | -119.1971 | 2.8519 | 0.3087 | 0.035939 | -0.00059506 | 0.37677 | 0.096122 | 0.71932 | -0.023195 | 0.29634 | 4.1384 | 0.055192 | 0.025306 | 3.2944 | 0.081072 | -6.102 | -0.045776 | -22.728 | -1.6891 | 0.21515 | -119.1788 | -119.2474 | -118.0847 | -1.3092 | -0.28381 | 2.5681 | 2.5269 | -119.1284 | -119.1467 | 0.018311 | -0.050354 | -2.6367 | 119.1513 | 117.5079 | 117.5583 | -8.9539 | 0.068665 | 0.050354 | -0.28381 | 1.1124 | 118.9133 | 118.8629 | -0.32501 | 119.4122 | 113.0951 | 96.4691 | -122.0993 | 121.7651 | 121.7239 | 117.8879 | -121.9986
1491.6406 | 122.0352 | -119.2566 | 2.7695 | 0.29344 | 0.054097 | 0.010086 | 0.38959 | 0.088645 | 0.70864 | -0.017854 | 0.55574 | 4.1342 | 0.059465 | 0.034919 | 3.2986 | 0.081072 | -6.1386 | -0.064087 | -22.998 | -1.7441 | 0.23346 | -119.2062 | -119.3115 | -118.1076 | -1.1719 | -0.25177 | 2.5085 | 2.4719 | -119.1879 | -119.1925 | 0.050354 | -0.054931 | -2.536 | 119.1925 | 117.5125 | 117.5674 | -8.9081 | 0.068665 | 0.064087 | -0.26093 | 1.149 | 119.0048 | 118.9407 | -0.29755 | 119.4901 | 113.118 | 96.2585 | -122.081 | 121.7651 | 121.7285 | 118.0847 | -121.962
1492.6406 | 122.168 | -118.9178 | 3.0304 | 0.52232 | 0.030598 | 0.0036769 | 0.37036 | 0.10573 | 0.69155 | -0.032808 | 0.84566 | 4.1203 | 0.051988 | 0.039191 | 3.2847 | 0.080004 | -6.1798 | 0.068665 | -22.0917 | -1.6205 | 0.18768 | -118.8675 | -118.9774 | -117.7414 | -1.0162 | -0.12817 | 2.7466 | 2.6917 | -118.8538 | -118.8538 | 0.050354 | -0.059509 | -2.8427 | 118.9865 | 117.2974 | 117.3569 | -9.2102 | 0.064087 | 0.064087 | -0.28381 | 1.1765 | 118.7897 | 118.7256 | -0.33875 | 119.1055 | 112.738 | 96.8262 | -122.0078 | 121.6644 | 121.6095 | 117.9016 | -121.8842
1493.6406 | 122.0627 | -119.1147 | 2.829 | 1.1937 | 0.051961 | 0.014358 | 0.38318 | 0.087577 | 0.71398 | -0.029603 | 0.60152 | 4.1363 | 0.044511 | 0.032783 | 3.2922 | 0.070391 | -6.7062 | -0.050354 | -22.197 | -1.2405 | 0.24261 | -119.101 | -119.2154 | -117.9886 | -1.0849 | -0.23804 | 2.5681 | 2.5085 | -119.0735 | -119.0689 | 0.013733 | -0.10071 | -2.5864 | 119.0643 | 117.8741 | 117.9749 | -9.5352 | 0.041199 | 0.045776 | -0.26092 | 1.1261 | 118.8766 | 118.8309 | -0.32043 | 119.3573 | 112.4084 | 96.9177 | -122.0444 | 121.6827 | 121.6232 | 118.0298 | -121.8979
1494.6406 | 122.1634 | -119.0689 | 2.8336 | 0.36973 | 0.026326 | 0.00047294 | 0.36716 | 0.087577 | 0.70651 | -0.038148 | 0.89143 | 4.1278 | 0.034898 | 0.024238 | 3.2826 | 0.077868 | -6.395 | 0.054932 | -22.4396 | -1.2451 | 0.18768 | -119.0414 | -119.1467 | -117.8741 | -1.0254 | -0.1236 | 2.5543 | 2.5223 | -119.0048 | -119.0186 | 0.027466 | -0.07782 | -2.6459 | 119.1238 | 117.8238 | 117.9016 | -9.2285 | 0.064087 | 0.050354 | -0.27924 | 1.1948 | 118.9453 | 118.895 | -0.31128 | 119.2566 | 112.674 | 96.6293 | -121.9803 | 121.6232 | 121.5912 | 118.0435 | -121.8521
1495.6406 | 122.0673 | -119.1101 | 2.7603 | 0.61387 | 0.043416 | -0.012345 | 0.37464 | 0.098258 | 0.69689 | -0.03708 | 0.7541 | 4.116 | 0.044511 | 0.041327 | 3.2912 | 0.0768 | -6.4407 | 0.091553 | -22.1283 | -1.3138 | 0.17853 | -119.0689 | -119.1696 | -117.952 | -1.0025 | -0.35706 | 2.5131 | 2.4582 | -119.1422 | -119.1101 | 0.041198 | -0.05951 | -2.5818 | 119.2017 | 117.7963 | 117.8558 | -9.2011 | -0.032044 | 0 | -0.24719 | 1.1581 | 118.7531 | 118.7531 | -0.30212 | 119.2886 | 112.6694 | 96.9818 | -121.9299 | 121.6232 | 121.5683 | 118.1076 | -121.8704
1496.6406 | 122.0993 | -119.0002 | 2.861 | 0.56809 | 0.023121 | 0.0047449 | 0.36182 | 0.099326 | 0.69689 | -0.023195 | 0.50996 | 4.1117 | 0.045579 | 0.038123 | 3.2912 | 0.073595 | -6.6055 | 0.27008 | -22.1237 | -1.4145 | 0.15106 | -119.0414 | -119.1101 | -117.865 | -0.98877 | -0.10986 | 2.5681 | 2.5406 | -118.9819 | -118.9957 | -0.041199 | -0.10986 | -2.71 | 119.2703 | 117.5858 | 117.6956 | -9.4666 | 0.01831 | 0.004577 | -0.29297 | 1.1353 | 118.8904 | 118.8858 | -0.32043 | 119.1513 | 112.3947 | 96.8765 | -121.9711 | 121.5683 | 121.5408 | 118.0115 | -121.8567
1497.6406 | 122.1039 | -119.0506 | 2.8198 | 0.32395 | 0.016713 | 0.01329 | 0.36823 | 0.087577 | 0.69903 | -0.030671 | 0.81514 | 4.1203 | 0.054124 | 0.038123 | 3.2826 | 0.077868 | -6.2439 | 0.10986 | -22.3618 | -1.149 | 0.19226 | -119.0277 | -119.1284 | -117.9016 | -0.9613 | -0.11444 | 2.5543 | 2.5085 | -119.0186 | -118.9957 | 0.022888 | -0.07782 | -2.6276 | 119.1605 | 117.9016 | 117.9794 | -9.0637 | 0.032043 | 0.054931 | -0.2655 | 1.149 | 118.9362 | 118.8812 | -0.31128 | 119.2429 | 112.8067 | 96.6888 | -121.9482 | 121.6049 | 121.5591 | 118.0893 | -121.8155
1498.6406 | 122.049 | -119.22 | 2.7054 | 0.33921 | 0.0060322 | 0.0047449 | 0.35327 | 0.089713 | 0.69476 | -0.045625 | 0.55574 | 4.1117 | 0.057328 | 0.032783 | 3.289 | 0.070391 | -6.4819 | 0.059509 | -22.4167 | -1.4465 | 0.21057 | -119.1925 | -119.2795 | -118.0847 | -0.9613 | -0.15106 | 2.4124 | 2.3529 | -119.1559 | -119.1513 | 0.027466 | -0.059509 | -2.4948 | 119.2795 | 117.7734 | 117.8329 | -9.1873 | 0.064087 | 0.068665 | -0.29297 | 1.1353 | 119.0689 | 119.0002 | -0.35248 | 119.4305 | 112.738 | 96.8033 | -121.9849 | 121.6324 | 121.5729 | 118.2587 | -121.8567
1499.6406 | 122.0444 | -119.1284 | 2.7512 | 0.53758 | 0.0049632 | 0.011154 | 0.35327 | 0.087577 | 0.69583 | -0.03708 | 0.4947 | 4.1107 | 0.053056 | 0.046668 | 3.288 | 0.072527 | -6.1066 | 0.07782 | -21.7575 | -1.3824 | 0.21057 | -119.0918 | -119.1971 | -118.0161 | -0.92468 | -0.17853 | 2.4765 | 2.4307 | -119.0598 | -119.0826 | 0.036621 | -0.068665 | -2.5406 | 119.2062 | 117.746 | 117.8146 | -8.8577 | 0.068665 | 0.045776 | -0.27466 | 1.1124 | 118.9499 | 118.9041 | -0.32044 | 119.339 | 113.0219 | 97.3709 | -121.9482 | 121.6049 | 121.5591 | 118.2037 | -121.8338
1500.6406 | 122.0306 | -119.1879 | 2.6871 | 0.24766 | 0.0049632 | 0.018631 | 0.36716 | 0.081168 | 0.69048 | -0.043489 | 0.4947 | 4.1107 | 0.044511 | 0.031714 | 3.2869 | 0.070391 | -5.7541 | 0.073242 | -21.8124 | -1.3824 | 0.19684 | -119.133 | -119.2429 | -118.0527 | -0.98877 | -0.15564 | 2.4124 | 2.3621 | -119.1193 | -119.1422 | 0.054931 | -0.054932 | -2.4902 | 119.2612 | 117.8055 | 117.8604 | -8.4412 | 0.068664 | 0.045776 | -0.27466 | 1.1353 | 119.0323 | 118.9865 | -0.32501 | 119.3848 | 113.4338 | 97.3755 | -121.9299 | 121.6003 | 121.55 | 118.1992 | -121.8292
1501.6406 | 122.0444 | -119.1513 | 2.6917 | 0.15611 | -0.00037681 | 0.011154 | 0.37464 | 0.087577 | 0.68728 | -0.041353 | 0.26582 | 4.1149 | 0.044511 | 0.030646 | 3.2922 | 0.061846 | -6.015 | 0.086975 | -22.0596 | -1.4648 | 0.20599 | -119.1788 | -119.2703 | -118.0435 | -0.87891 | -0.11444 | 2.3987 | 2.3346 | -119.1147 | -119.133 | -0.027466 | -0.11902 | -2.4857 | 119.2383 | 117.6865 | 117.8055 | -8.7067 | 0.036621 | 0.01831 | -0.29297 | 1.1078 | 119.0369 | 119.0186 | -0.35705 | 119.3573 | 113.1363 | 97.0917 | -121.962 | 121.55 | 121.4859 | 118.2724 | -121.8246
1502.6406 | 122.0627 | -119.1788 | 2.6596 | 0.14085 | 0.014576 | 0.0047449 | 0.37357 | 0.091849 | 0.69155 | -0.042421 | 0.29634 | 4.1171 | 0.03917 | 0.029578 | 3.2805 | 0.069323 | -5.8823 | 0.10529 | -22.0871 | -1.4465 | 0.21973 | -119.1376 | -119.252 | -118.0161 | -0.97504 | -0.11444 | 2.3849 | 2.33 | -119.101 | -119.1193 | 0.041199 | -0.073242 | -2.4399 | 119.2841 | 117.7322 | 117.8055 | -8.5419 | 0.07782 | 0.059509 | -0.27466 | 1.1627 | 119.0643 | 119.0048 | -0.32959 | 119.3985 | 113.2965 | 97.0917 | -121.9116 | 121.5637 | 121.5088 | 118.2037 | -121.7789
1503.6406 | 122.0718 | -119.1971 | 2.623 | 0.20188 | -0.016399 | 0.011154 | 0.35861 | 0.084372 | 0.68835 | -0.036012 | 0.26582 | 4.1096 | 0.029557 | 0.025306 | 3.2869 | 0.072527 | -5.8594 | 0.13733 | -22.0367 | -1.4236 | 0.21057 | -119.1788 | -119.2703 | -118.0069 | -0.98877 | -0.09613 | 2.3483 | 2.298 | -119.1513 | -119.165 | 0.018311 | -0.073242 | -2.4124 | 119.3344 | 117.7734 | 117.8467 | -8.4824 | 0.045777 | 0.032044 | -0.27466 | 1.1902 | 119.101 | 119.0689 | -0.32501 | 119.4077 | 113.3377 | 97.1603 | -121.8933 | 121.5454 | 121.4951 | 118.2083 | -121.788
1504.6406 | 122.0581 | -119.1834 | 2.6276 | 0.12559 | -0.0025128 | 0.0058129 | 0.36823 | 0.092917 | 0.69262 | -0.042421 | 0.38789 | 4.1053 | 0.031694 | 0.015693 | 3.2837 | 0.063982 | -6.015 | 0.14191 | -22.0642 | -1.2863 | 0.21057 | -119.1696 | -119.2383 | -117.9886 | -0.90637 | -0.10071 | 2.3438 | 2.2842 | -119.1101 | -119.133 | 0.013733 | -0.054931 | -2.417 | 119.3253 | 117.897 | 117.952 | -8.6426 | 0.073243 | 0.050354 | -0.28381 | 1.1948 | 119.0826 | 119.0323 | -0.34332 | 119.3939 | 113.1683 | 97.1191 | -121.8658 | 121.5271 | 121.4676 | 118.277 | -121.7606
1505.6406 | 121.9894 | -119.2108 | 2.6276 | 3.3147 | 0.016713 | 0.019699 | 0.35114 | 0.083304 | 0.68835 | -0.033876 | 0.021682 | 4.1107 | 0.022081 | 0.015693 | 3.2815 | 0.058642 | -5.9235 | 0.16479 | -22.1146 | -1.4053 | 0.17853 | -119.1696 | -119.2566 | -118.071 | -0.89264 | -0.14648 | 2.3254 | 2.2797 | -119.1284 | -119.1559 | 0.041198 | -0.045777 | -2.449 | 119.3756 | 117.8055 | 117.8513 | -8.551 | 0.082397 | 0.054931 | -0.30212 | 1.1398 | 119.0643 | 119.0094 | -0.3479 | 119.3893 | 113.2874 | 97.0963 | -121.8842 | 121.5363 | 121.4905 | 118.3182 | -121.7834
1506.6406 | 122.0581 | -119.0643 | 2.7328 | -0.16433 | 0.0028272 | 0.0090179 | 0.36182 | 0.10253 | 0.69689 | -0.027467 | 0.021682 | 4.1171 | 0.029557 | 0.024238 | 3.2986 | 0.054369 | -4.5273 | 0.14648 | -22.2656 | -1.0437 | 0.20599 | -119.0414 | -119.1467 | -117.952 | -1.0117 | -0.18768 | 2.4307 | 2.3575 | -119.0323 | -118.9957 | 0.022888 | -0.082398 | -2.5269 | 119.2108 | 118.0206 | 118.103 | -7.2601 | 0.032043 | 0.068664 | -0.30212 | 1.1124 | 118.8766 | 118.808 | -0.37537 | 119.2703 | 114.537 | 96.7987 | -121.8796 | 121.4951 | 121.4218 | 118.0527 | -121.7285
1507.6406 | 122.0078 | -119.0231 | 2.7786 | -0.16433 | 0.01244 | 0.0036769 | 0.36075 | 0.09719 | 0.68408 | -0.045625 | 0.34212 | 4.1064 | 0.026353 | 0.031714 | 3.2869 | 0.067187 | -4.2938 | -0.17853 | -22.5174 | -1.0071 | 0.19684 | -118.9957 | -119.0781 | -117.8604 | -0.737 | -0.12817 | 2.504 | 2.4445 | -118.9407 | -118.9728 | 0.027465 | -0.054932 | -2.5818 | 118.8446 | 118.0161 | 118.071 | -7.0724 | 0.082397 | 0.050354 | -0.27466 | 1.1627 | 118.895 | 118.8446 | -0.33417 | 119.22 | 114.7293 | 96.5057 | -121.8567 | 121.5271 | 121.4676 | 118.2861 | -121.7514
1508.6406 | 121.8933 | -119.0689 | 2.7328 | 0.4918 | 0.047688 | -0.00059506 | 0.36395 | 0.095053 | 0.71078 | -0.032808 | 0.72359 | 4.1192 | 0.05092 | 0.042396 | 3.2954 | 0.066119 | -4.5044 | -0.032043 | -22.8333 | -1.1765 | 0.25635 | -119.0826 | -119.1559 | -117.9016 | -0.90179 | -0.24719 | 2.4765 | 2.3941 | -119.0323 | -119.0277 | -0.013733 | -0.086975 | -2.4765 | 119.0369 | 117.8925 | 117.9794 | -7.2372 | 0.036621 | 0.041199 | -0.25635 | 1.1673 | 118.8217 | 118.7805 | -0.33874 | 119.3253 | 114.5645 | 96.2357 | -121.8887 | 121.5454 | 121.463 | 118.1671 | -121.7606
1509.6406 | 121.8475 | -119.0231 | 2.8519 | -0.088033 | 0.019917 | 0.0058129 | 0.37677 | 0.093985 | 0.69689 | -0.031739 | -0.085129 | 4.1053 | 0.051988 | 0.033851 | 3.2783 | 0.071459 | -4.7699 | -0.013733 | -22.4167 | -1.4145 | 0.23804 | -118.9819 | -119.0872 | -117.8833 | -0.84228 | -0.23804 | 2.5497 | 2.504 | -118.9636 | -118.9362 | 0.041198 | -0.064087 | -2.6138 | 119.0094 | 117.6086 | 117.6727 | -7.6218 | 0.059509 | 0.086975 | -0.30212 | 1.1398 | 118.7851 | 118.6981 | -0.3479 | 119.2612 | 114.2532 | 96.6064 | -121.9391 | 121.5729 | 121.5271 | 118.1808 | -121.788
1510.6406 | 121.8704 | -118.9316 | 2.916 | -0.30166 | 0.023121 | 0.01329 | 0.37357 | 0.088645 | 0.70223 | -0.029603 | -0.29875 | 4.1128 | 0.03383 | 0.034919 | 3.2677 | 0.05971 | -4.953 | 0.009155 | -22.8607 | -1.4694 | 0.22888 | -118.9545 | -119.0414 | -117.8833 | -0.8606 | -0.25177 | 2.6047 | 2.536 | -118.9133 | -118.8858 | -0.022888 | -0.10986 | -2.6871 | 118.9407 | 117.4622 | 117.572 | -7.869 | 0.018311 | 0.045777 | -0.31128 | 1.0483 | 118.6798 | 118.634 | -0.37994 | 119.1605 | 113.9786 | 96.0709 | -121.9574 | 121.5363 | 121.4676 | 118.071 | -121.8018
1511.6406 | 121.8246 | -118.9636 | 2.8656 | -0.22536 | 0.040211 | 0.014358 | 0.37143 | 0.082236 | 0.69903 | -0.028535 | -1.611 | 4.1181 | 0.049852 | 0.041327 | 3.2719 | 0.066119 | -4.8386 | 0.013733 | -23.1033 | -1.5289 | 0.2243 | -118.9682 | -119.0689 | -117.9153 | -0.82398 | -0.2243 | 2.6093 | 2.5497 | -118.9041 | -118.9362 | -0.004578 | -0.10529 | -2.6413 | 118.9774 | 117.4347 | 117.54 | -7.7042 | 0.059509 | 0.027466 | -0.25635 | 1.0483 | 118.7393 | 118.7119 | -0.31586 | 119.1879 | 114.1251 | 95.8603 | -121.9345 | 121.5729 | 121.5134 | 118.1396 | -121.8018
1512.6406 | 121.8613 | -118.9728 | 2.8244 | -0.19484 | 0.041279 | 0.014358 | 0.37036 | 0.091849 | 0.7236 | -0.030671 | -0.17668 | 4.1117 | 0.046647 | 0.02851 | 3.2826 | 0.068255 | -4.8248 | 0.022888 | -22.7783 | -1.4008 | 0.22888 | -118.9728 | -119.0414 | -117.8467 | -0.83313 | -0.20599 | 2.536 | 2.4811 | -118.927 | -118.9133 | 0 | -0.068665 | -2.5955 | 118.9957 | 117.572 | 117.6407 | -7.6492 | 0.045776 | 0.059509 | -0.28839 | 1.1261 | 118.7668 | 118.7073 | -0.34332 | 119.2017 | 114.1479 | 96.1945 | -121.8658 | 121.5088 | 121.4539 | 118.1396 | -121.7377
1513.6406 | 121.9299 | -118.9819 | 2.7695 | -0.026997 | 0.035939 | -0.0091401 | 0.3693 | 0.092917 | 0.69903 | -0.031739 | 0.66255 | 4.1053 | 0.046647 | 0.040259 | 3.2794 | 0.072527 | -5.0766 | 0.10986 | -23.0072 | -1.5335 | 0.18768 | -118.9453 | -119.0414 | -117.8101 | -0.68665 | -0.1236 | 2.4765 | 2.4261 | -118.9041 | -118.8858 | 0.036622 | -0.059509 | -2.5818 | 119.0918 | 117.4484 | 117.5079 | -7.8461 | 0.07782 | 0.096131 | -0.29297 | 1.1719 | 118.8583 | 118.7622 | -0.34332 | 119.1696 | 113.9053 | 95.9747 | -121.8109 | 121.4584 | 121.4081 | 118.2953 | -121.6553
1514.6406 | 121.8613 | -119.1879 | 2.5955 | -0.072774 | 0.045552 | -0.00059506 | 0.37784 | 0.10573 | 0.70864 | -0.025331 | -0.14616 | 4.1149 | 0.046647 | 0.038123 | 3.2869 | 0.0768 | -5.1453 | 0 | -23.3185 | -1.4282 | 0.23346 | -119.1238 | -119.252 | -118.0801 | -0.82855 | -0.23346 | 2.3346 | 2.2797 | -119.0964 | -119.1284 | 0.064087 | -0.064087 | -2.3621 | 119.1879 | 117.7597 | 117.8238 | -7.7408 | 0.091552 | 0.059509 | -0.26092 | 1.1078 | 118.9545 | 118.895 | -0.31586 | 119.4214 | 114.0427 | 95.8694 | -121.8475 | 121.5225 | 121.4676 | 118.3594 | -121.7239
1515.6406 | 121.8384 | -118.9819 | 2.8198 | 0.049296 | 0.049824 | -0.0091401 | 0.37998 | 0.10146 | 0.71932 | -0.033876 | 0.097976 | 4.1192 | 0.05626 | 0.033851 | 3.2837 | 0.089617 | -5.2094 | 0.059509 | -23.4467 | -1.4374 | 0.2243 | -118.959 | -119.0689 | -117.5812 | -0.82855 | -0.15106 | 2.5497 | 2.5223 | -118.8858 | -118.9041 | 0.022889 | -0.086975 | -2.5955 | 119.0414 | 117.5446 | 117.6315 | -8.0292 | 0.096131 | 0.07782 | -0.27008 | 1.4008 | 118.8309 | 118.7531 | -0.29755 | 119.2062 | 113.7726 | 95.5353 | -121.8887 | 121.5317 | 121.5042 | 118.1534 | -121.7239
1516.6406 | 121.8292 | -119.0323 | 2.71 | 0.095073 | 0.054097 | 0.0015409 | 0.37143 | 0.089713 | 0.71398 | -0.028535 | 0.036941 | 4.1203 | 0.055192 | 0.029578 | 3.2933 | 0.070391 | -5.3513 | 0.027466 | -23.0804 | -0.99792 | 0.29297 | -118.9957 | -119.0781 | -117.9382 | -1.9638 | -0.21515 | 2.4582 | 2.3712 | -118.9911 | -118.959 | 0.036621 | -0.045776 | -2.417 | 119.0598 | 118.0344 | 118.0801 | -8.0612 | 0.041199 | 0.073243 | -0.25177 | 1.0941 | 118.8171 | 118.7439 | -0.33874 | 119.3253 | 113.681 | 95.9518 | -121.788 | 121.4905 | 121.4035 | 117.0685 | -121.669
1517.6406 | 121.7606 | -119.0598 | 2.7145 | 0.00352 | 0.053029 | -0.0027321 | 0.37784 | 0.093985 | 0.70544 | -0.011445 | 0.28108 | 4.1149 | 0.048783 | 0.025306 | 3.2869 | 0.062914 | -5.5252 | 0.027466 | -22.7737 | -1.1032 | 0.22888 | -119.0094 | -119.0918 | -117.9611 | -1.1032 | -0.25635 | 2.4307 | 2.3666 | -118.959 | -118.9865 | 0.050354 | -0.032044 | -2.4857 | 119.0872 | 117.9565 | 117.9886 | -8.2397 | 0.10071 | 0.073242 | -0.28381 | 1.0986 | 118.8034 | 118.7302 | -0.3479 | 119.2886 | 113.5345 | 96.286 | -121.8063 | 121.4905 | 121.4264 | 117.9565 | -121.701
1518.6406 | 121.8567 | -119.0002 | 2.7054 | 0.12559 | 0.011372 | 0.0047449 | 0.36289 | 0.082236 | 0.67233 | -0.025331 | 0.64729 | 4.1075 | 0.038102 | 0.025306 | 3.2794 | 0.085345 | -5.3513 | 0.10071 | -22.8607 | -1.4191 | 0.17853 | -118.9362 | -119.0323 | -117.8513 | -0.95215 | -0.10986 | 2.4261 | 2.3758 | -118.9545 | -118.8995 | 0.064087 | -0.032044 | -2.5269 | 119.101 | 117.5812 | 117.6132 | -8.0566 | 0.045776 | 0.10071 | -0.27924 | 1.149 | 118.8904 | 118.7897 | -0.32959 | 119.1788 | 113.649 | 96.1395 | -121.7377 | 121.4264 | 121.376 | 118.0481 | -121.6049
1519.6406 | 121.756 | -118.9865 | 2.7557 | 0.53758 | 0.04662 | 0.0068819 | 0.37998 | 0.089713 | 0.71398 | -0.016786 | 0.46419 | 4.1085 | 0.060533 | 0.029578 | 3.2805 | 0.080004 | -5.3284 | -0.041199 | -23.0942 | -1.6342 | 0.24261 | -118.9682 | -119.101 | -117.8604 | -0.87433 | -0.32044 | 2.4857 | 2.4353 | -118.9224 | -118.895 | 0.01831 | -0.11444 | -2.5131 | 118.9453 | 117.3523 | 117.4667 | -8.0841 | 0.064087 | 0.091553 | -0.27008 | 1.1261 | 118.6661 | 118.5745 | -0.32043 | 119.2291 | 113.6581 | 95.8923 | -121.8567 | 121.4722 | 121.4218 | 118.1122 | -121.6507
1520.6406 | 121.7697 | -118.959 | 2.7786 | 0.32395 | 0.035939 | -0.00059506 | 0.36823 | 0.088645 | 0.72146 | -0.022126 | 0.40315 | 4.1107 | 0.072282 | 0.039191 | 3.2869 | 0.077868 | -5.3009 | -0.050354 | -23.085 | -1.3641 | 0.24719 | -118.9407 | -119.0277 | -117.8513 | -1.0666 | -0.26093 | 2.5314 | 2.4582 | -118.9087 | -118.8721 | 0.01831 | -0.068665 | -2.5314 | 118.9087 | 117.5949 | 117.6636 | -8.0795 | 0.050354 | 0.086975 | -0.24719 | 1.1078 | 118.6981 | 118.6111 | -0.32043 | 119.2062 | 113.6581 | 95.874 | -121.8063 | 121.4905 | 121.4172 | 117.8925 | -121.6507
1521.6406 | 121.8567 | -118.7714 | 2.8839 | 0.61387 | 0.02953 | 0.012222 | 0.36289 | 0.091849 | 0.69903 | -0.022126 | 1.2729 | 4.1 | 0.05626 | 0.040259 | 3.2741 | 0.074663 | -5.072 | 0.059509 | -23.0301 | -1.0117 | 0.20599 | -118.7439 | -118.8583 | -117.6224 | -0.89264 | -0.13275 | 2.6001 | 2.5635 | -118.7393 | -118.6981 | 0.027466 | -0.086975 | -2.6779 | 118.8309 | 117.7597 | 117.8467 | -7.9559 | 0.032043 | 0.073242 | -0.28381 | 1.149 | 118.6386 | 118.5654 | -0.32043 | 118.9774 | 113.6993 | 95.7413 | -121.7422 | 121.3715 | 121.3348 | 117.8787 | -121.582
1522.6406 | 121.8018 | -118.9499 | 2.7283 | 0.55284 | 0.053029 | -0.0048681 | 0.38745 | 0.087577 | 0.69476 | -0.024263 | 0.7541 | 4.1139 | 0.051988 | 0.018897 | 3.2773 | 0.077868 | -5.1224 | -0.018311 | -23.0392 | -1.355 | 0.23804 | -118.9133 | -119.0094 | -117.8375 | -1.4191 | -0.16937 | 2.4719 | 2.4261 | -118.895 | -118.8721 | 0.036621 | -0.059509 | -2.4902 | 118.9316 | 117.5949 | 117.6544 | -7.8506 | 0.054932 | 0.07782 | -0.25635 | 1.1124 | 118.7805 | 118.7027 | -0.30212 | 119.1879 | 113.8275 | 95.9106 | -121.7377 | 121.4218 | 121.376 | 117.5308 | -121.6003
1523.6406 | 121.8521 | -119.014 | 2.6367 | -0.14907 | 0.014576 | 0.018631 | 0.36502 | 0.09719 | 0.65844 | -0.032808 | 0.3116 | 4.0957 | 0.038102 | 0.021033 | 3.2751 | 0.073595 | -5.0674 | 0.14191 | -22.879 | -1.0757 | 0.17853 | -118.9819 | -119.0964 | -117.9245 | -1.1215 | -0.11444 | 2.3392 | 2.3209 | -118.9774 | -118.9728 | 0.032043 | -0.082398 | -2.4582 | 119.1559 | 117.9382 | 118.0206 | -7.7042 | 0.036621 | 0.041199 | -0.29755 | 1.0895 | 118.8995 | 118.8583 | -0.31586 | 119.1925 | 113.9465 | 96.1349 | -121.7331 | 121.3531 | 121.3348 | 117.8925 | -121.6095
1524.6406 | 121.8658 | -118.9819 | 2.6367 | 0.32395 | 0.058369 | 0.0026089 | 0.35648 | 0.10039 | 0.70757 | -0.028535 | 0.7541 | 4.0989 | 0.026353 | 0.030646 | 3.2698 | 0.063982 | -4.8386 | 0.068665 | -23.3002 | -1.1398 | 0.19684 | -118.9774 | -119.0643 | -117.865 | -1.2177 | -0.13275 | 2.3575 | 2.298 | -118.9499 | -118.9453 | 0.004578 | -0.082397 | -2.4399 | 119.0506 | 117.8421 | 117.9245 | -7.4753 | 0.032044 | 0.036622 | -0.27924 | 1.1169 | 118.8492 | 118.8126 | -0.33874 | 119.1788 | 114.1434 | 95.6818 | -121.701 | 121.3394 | 121.2799 | 117.7643 | -121.582
1525.6406 | 121.8704 | -119.0414 | 2.5726 | 0.7512 | 0.040211 | -0.0048681 | 0.3757 | 0.08544 | 0.7033 | -0.031739 | 0.70833 | 4.1011 | 0.037034 | 0.026374 | 3.2794 | 0.078936 | -4.8111 | 0.10986 | -24.0646 | -1.3229 | 0.17853 | -118.9774 | -119.0781 | -117.8879 | -1.0574 | -0.11902 | 2.2934 | 2.2705 | -119.0414 | -119.0323 | 0.064087 | -0.036621 | -2.3941 | 119.1513 | 117.7185 | 117.7551 | -7.3837 | 0 | 0.009155 | -0.27924 | 1.1536 | 118.9224 | 118.9133 | -0.30212 | 119.22 | 114.2303 | 94.9768 | -121.6507 | 121.3348 | 121.312 | 117.984 | -121.6049
1526.6406 | 121.7926 | -119.046 | 2.6138 | 0.53758 | 0.026326 | 0.0068819 | 0.35968 | 0.082236 | 0.68408 | -0.041353 | 0.72359 | 4.1021 | 0.045579 | 0.037055 | 3.2741 | 0.067187 | -4.8798 | 0.10071 | -23.5977 | -1.2955 | 0.21057 | -118.9819 | -119.0598 | -117.8741 | -0.98419 | -0.13733 | 2.3209 | 2.2934 | -118.9682 | -118.9774 | 0.064087 | -0.013732 | -2.4033 | 119.1467 | 117.7505 | 117.7643 | -7.4936 | 0.07782 | 0.068665 | -0.29297 | 1.1719 | 118.9087 | 118.84 | -0.32043 | 119.2566 | 114.1663 | 95.4483 | -121.6736 | 121.3669 | 121.3394 | 118.0618 | -121.5912
1527.6406 | 121.756 | -118.9728 | 2.6505 | 0.12559 | 0.030598 | 0.0068819 | 0.36182 | 0.079032 | 0.69903 | -0.033876 | 0.63203 | 4.0947 | 0.054124 | 0.026374 | 3.2719 | 0.081072 | -4.8981 | 0.09613 | -23.4421 | -1.1261 | 0.19226 | -118.9819 | -119.0369 | -117.8238 | -0.96588 | -0.11902 | 2.3392 | 2.2888 | -118.9316 | -118.9407 | -0.009156 | -0.064087 | -2.4582 | 119.0689 | 117.8467 | 117.9108 | -7.5485 | 0.041198 | 0.032043 | -0.31128 | 1.149 | 118.8538 | 118.8217 | -0.36163 | 119.165 | 114.0747 | 95.5307 | -121.6873 | 121.312 | 121.2616 | 118.0069 | -121.5912
1528.6406 | 121.9391 | -118.9819 | 2.6505 | -0.088033 | 0.0028272 | 0.0058129 | 0.37143 | 0.090781 | 0.6798 | -0.028535 | 0.067459 | 4.0829 | 0.042375 | 0.015693 | 3.2666 | 0.074663 | -4.7928 | 0.14191 | -23.1537 | -1.5518 | 0.20142 | -118.9041 | -118.9957 | -117.7734 | -0.93842 | -0.10529 | 2.4124 | 2.3483 | -118.8995 | -118.9041 | 0.07782 | -0.013733 | -2.449 | 119.1238 | 117.4301 | 117.4438 | -7.4432 | 0.082398 | 0.07782 | -0.23804 | 1.2085 | 118.8766 | 118.7988 | -0.30212 | 119.1833 | 114.1891 | 95.8282 | -121.6461 | 121.3943 | 121.3303 | 118.0435 | -121.5546
1529.6875 | 121.6873 | -118.9499 | 2.7328 | -0.088033 | 0.010304 | 0.017563 | 0.37677 | 0.086509 | 0.70544 | -0.043489 | -0.22246 | 4.1011 | 0.045579 | 0.032783 | 3.2677 | 0.06505 | -5.0903 | 0.018311 | -23.2727 | -1.355 | 0.23346 | -118.927 | -119.014 | -117.8787 | -1.1169 | -0.24719 | 2.449 | 2.4078 | -118.9362 | -118.8858 | 0.022888 | -0.064087 | -2.4994 | 118.9682 | 117.5949 | 117.659 | -7.8232 | 0.013733 | 0.064087 | -0.28381 | 1.0712 | 118.7027 | 118.6386 | -0.32501 | 119.1833 | 113.8596 | 95.6772 | -121.7468 | 121.3989 | 121.3577 | 117.8329 | -121.6187
1530.6406 | 121.756 | -118.9865 | 2.6413 | 0.15611 | 0.011372 | -0.0027321 | 0.37143 | 0.074759 | 0.68408 | -0.030671 | 0.50996 | 4.085 | 0.032762 | 0.029578 | 3.2655 | 0.074663 | -5.04 | 0.064087 | -23.4833 | -1.0117 | 0.16479 | -118.9774 | -119.0552 | -117.865 | -1.0574 | -0.13275 | 2.3483 | 2.2888 | -118.9362 | -118.9178 | 0.009155 | -0.068665 | -2.4765 | 119.0506 | 117.9749 | 118.0435 | -7.6813 | 0.050354 | 0.068664 | -0.29297 | 1.1215 | 118.8538 | 118.7851 | -0.35248 | 119.1513 | 113.9465 | 95.5032 | -121.6965 | 121.3348 | 121.2753 | 117.9291 | -121.5591
1531.6406 | 121.7651 | -118.9682 | 2.6138 | 0.11033 | 0.0071002 | 0.017563 | 0.349 | 0.09719 | 0.68621 | -0.034944 | 0.34212 | 4.0979 | 0.024217 | 0.014625 | 3.2741 | 0.070391 | -5.0446 | 0.091553 | -23.7808 | -1.1261 | 0.20599 | -118.9636 | -119.0414 | -117.7826 | -1.0803 | -0.11902 | 2.3438 | 2.2797 | -118.9087 | -118.9362 | 0.004578 | -0.073242 | -2.4078 | 119.0598 | 117.8421 | 117.9153 | -7.6584 | 0.05951 | 0.032044 | -0.27008 | 1.1856 | 118.8492 | 118.8171 | -0.33417 | 119.1742 | 113.9236 | 95.1874 | -121.6553 | 121.312 | 121.2479 | 117.8879 | -121.55
1532.7656 | 121.669 | -119.046 | 2.623 | 0.36973 | 0.049824 | 0.00047294 | 0.38104 | 0.093985 | 0.73321 | -0.027467 | 0.41841 | 4.1149 | 0.058397 | 0.034919 | 3.2815 | 0.063982 | -4.9896 | -0.022888 | -23.7671 | -1.7349 | 0.22888 | -119.0048 | -119.0689 | -117.9016 | -1.0071 | -0.27924 | 2.3346 | 2.2797 | -118.9774 | -118.9682 | 0.041199 | -0.022888 | -2.3941 | 119.0231 | 117.3111 | 117.334 | -7.6126 | 0.068665 | 0.07782 | -0.28839 | 1.1444 | 118.7668 | 118.689 | -0.34332 | 119.2749 | 114.0564 | 95.2789 | -121.6919 | 121.3806 | 121.3257 | 118.0389 | -121.5912
1533.8594 | 121.6644 | -118.9362 | 2.6871 | 0.46128 | 0.02419 | -0.014481 | 0.36609 | 0.087577 | 0.70757 | -0.023195 | -4.2355 | 4.1609 | 0.03383 | 0.10862 | 3.2783 | 0.066119 | -5.2277 | -0.022888 | -24.0234 | -2.0828 | 0.22888 | -118.8995 | -118.9728 | 1.8723 | -0.93842 | -0.23346 | 2.4261 | 2.3666 | -118.8766 | -118.8904 | 0.036621 | -0.036621 | -2.4582 | 118.9133 | 116.8533 | 116.89 | -7.9147 | 0.059509 | 0.045776 | -0.26093 | 120.8084 | 118.7027 | 118.6569 | -0.32043 | 119.165 | 113.7085 | 94.9127 | -121.6599 | 121.3623 | 121.3028 | 117.9977 | -121.5775
1534.6406 | 121.7651 | -118.808 | 2.7649 | -0.10329 | 0.0038952 | 0.014358 | 0.3693 | 0.082236 | 0.66165 | -0.044557 | 0.067459 | 4.1587 | 0.03917 | 0.096869 | 3.2538 | 0.075732 | -5.1819 | 0.18768 | -23.6664 | -1.3229 | 0.20142 | -118.7759 | -118.8766 | 2.0279 | -0.75531 | -0.091553 | 2.4673 | 2.4124 | -118.7531 | -118.7164 | 0.032043 | -0.068665 | -2.5635 | 118.9957 | 117.485 | 117.5537 | -7.9468 | 0.054931 | 0.091552 | -0.29755 | 120.8359 | 118.7164 | 118.6249 | -0.35248 | 119.0094 | 113.6261 | 95.1416 | -121.6415 | 121.2753 | 121.2204 | 118.0527 | -121.4813
1535.6406 | 121.637 | -118.7485 | 2.8793 | -0.11855 | 0.039143 | 0.0090179 | 0.35968 | 0.098258 | 0.68514 | -0.033876 | -0.054612 | 4.1502 | 0.057328 | 0.086188 | 3.2634 | 0.068255 | -5.1407 | 0.013733 | -23.2864 | -1.3321 | 0.23804 | -118.6935 | -118.8034 | 2.0004 | -0.87891 | -0.2243 | 2.6093 | 2.5406 | -118.7393 | -118.6798 | 0.054932 | -0.054932 | -2.6413 | 118.7622 | 117.4164 | 117.4713 | -8.02 | 0.009155 | 0.068664 | -0.27008 | 120.7489 | 118.5242 | 118.4555 | -0.33874 | 118.9865 | 113.6078 | 95.462 | -121.6827 | 121.3577 | 121.2891 | 117.8696 | -121.5591
1536.6406 | 121.637 | -118.7347 | 2.8427 | -0.27114 | 0.010304 | 0.015426 | 0.37036 | 0.091849 | 0.68408 | -0.021058 | -0.13091 | 4.1609 | 0.032762 | 0.088325 | 3.2516 | 0.073595 | -5.0446 | 0.07782 | -23.2315 | -1.3092 | 0.21973 | -118.6981 | -118.8034 | 2.0233 | -0.82398 | -0.21057 | 2.5864 | 2.5314 | -118.6981 | -118.7119 | 0.036621 | -0.068665 | -2.623 | 118.8126 | 117.4255 | 117.4942 | -7.8873 | 0.036621 | 0.022888 | -0.25635 | 120.7581 | 118.5242 | 118.5013 | -0.31128 | 118.9545 | 113.6902 | 95.5032 | -121.6461 | 121.3211 | 121.2662 | 117.9108 | -121.5546
1537.6406 | 121.6232 | -118.7988 | 2.8152 | -0.19484 | 0.0092362 | 0.012222 | 0.36502 | 0.089713 | 0.70437 | -0.033876 | -0.0088351 | 4.1523 | 0.051988 | 0.091529 | 3.2634 | 0.073595 | -5.3055 | 0.086975 | -23.0026 | -1.1856 | 0.22888 | -118.7851 | -118.8721 | 1.9363 | -0.94299 | -0.24719 | 2.5223 | 2.4719 | -118.7622 | -118.7622 | 0.013733 | -0.073242 | -2.5864 | 118.8858 | 117.6132 | 117.6865 | -8.1207 | 0.036621 | 0.036621 | -0.29297 | 120.7352 | 118.5516 | 118.515 | -0.34332 | 119.0277 | 113.4933 | 95.7962 | -121.6873 | 121.3211 | 121.2708 | 117.8558 | -121.5775
1538.6406 | 121.6782 | -118.7668 | 2.861 | -0.25588 | 0.014576 | 0.0079499 | 0.36716 | 0.096122 | 0.69155 | -0.024263 | -0.10039 | 4.1502 | 0.040239 | 0.087256 | 3.2612 | 0.077868 | -5.1498 | 0.09613 | -23.5519 | -1.2177 | 0.21057 | -118.7256 | -118.7897 | 2.005 | -0.91553 | -0.20142 | 2.5681 | 2.5131 | -118.721 | -118.7027 | 0.041199 | -0.022888 | -2.6505 | 118.8629 | 117.5491 | 117.572 | -8.0109 | 0.045777 | 0.064087 | -0.29297 | 120.7718 | 118.5654 | 118.5013 | -0.3479 | 118.9774 | 113.6169 | 95.2148 | -121.6507 | 121.3348 | 121.2799 | 117.8513 | -121.5637
1539.6406 | 121.6049 | -118.5562 | 3.0441 | -0.22536 | 0.023121 | 0.0068819 | 0.36823 | 0.093985 | 0.69903 | -0.025331 | 3.4854 | 4.1513 | 0.054124 | 0.095801 | 3.2591 | 0.067187 | -5.1178 | -0.013733 | -24.1379 | -1.4053 | 0.24261 | -118.5059 | -118.5516 | 2.2385 | -0.86975 | -0.25635 | 2.8152 | 2.7603 | -118.4647 | -118.4921 | 0.050354 | 0.004577 | -2.8015 | 118.5425 | 117.1509 | 117.1463 | -8.1619 | 0.091552 | 0.064087 | -0.22888 | 120.7947 | 118.2999 | 118.2358 | -0.28381 | 118.7988 | 113.4384 | 94.4183 | -121.5958 | 121.3715 | 121.3165 | 117.6865 | -121.5363
1540.6406 | 121.6187 | -118.8583 | 2.7191 | -1.5224 | 0.050892 | -0.0016631 | 0.3725 | 0.082236 | 0.70971 | -0.027467 | -0.19194 | 4.1555 | 0.055192 | 0.084052 | 3.2655 | 0.062914 | -5.072 | 0.004578 | -24.0005 | -1.2314 | 0.26093 | -118.8583 | -118.9224 | 1.9089 | -0.87891 | -0.25177 | 2.4353 | 2.3758 | -118.8446 | -118.808 | 0 | -0.064087 | -2.4582 | 118.8629 | 117.627 | 117.691 | -7.7911 | 0.013733 | 0.050354 | -0.28381 | 120.7672 | 118.6066 | 118.5562 | -0.34332 | 119.1193 | 113.7863 | 94.8578 | -121.6415 | 121.2936 | 121.2341 | 117.9794 | -121.5271
1541.6406 | 121.6187 | -118.8263 | 2.7695 | -0.14907 | 0.040211 | 0.018631 | 0.3693 | 0.09719 | 0.7001 | -0.030671 | -0.11565 | 4.163 | 0.045579 | 0.097938 | 3.2634 | 0.057574 | -5.2505 | 0.004578 | -23.6847 | -1.0208 | 0.21973 | -118.7943 | -118.8812 | 1.9775 | -0.88806 | -0.2243 | 2.4857 | 2.4307 | -118.7622 | -118.7805 | 0.032044 | -0.054932 | -2.5497 | 118.8309 | 117.8055 | 117.8604 | -8.02 | 0.064087 | 0.045776 | -0.28381 | 120.8038 | 118.602 | 118.5562 | -0.33875 | 119.046 | 113.5757 | 95.1416 | -121.6507 | 121.312 | 121.257 | 117.9382 | -121.55
1542.6406 | 121.6507 | -118.7943 | 2.7557 | 0.018779 | 0.048756 | 0.0015409 | 0.38959 | 0.082236 | 0.71078 | -0.021058 | 0.11323 | 4.1609 | 0.049852 | 0.10435 | 3.2687 | 0.073595 | -5.0995 | 0.045776 | -23.6984 | -1.1719 | 0.22888 | -118.8354 | -118.9362 | 1.9501 | -1.1215 | -0.21515 | 2.4033 | 2.3529 | -118.7485 | -118.7027 | -0.041199 | -0.14191 | -2.5269 | 118.84 | 117.6224 | 117.7643 | -7.8552 | 0.045776 | 0.091552 | -0.35248 | 120.7443 | 118.5791 | 118.4875 | -0.40283 | 119.0231 | 113.6948 | 95.0958 | -121.6919 | 121.1975 | 121.1472 | 117.6727 | -121.4584
1543.6875 | 121.6187 | -118.959 | 2.623 | -0.11855 | 0.060505 | -0.0027321 | 0.38211 | 0.088645 | 0.70864 | -0.015718 | 0.0522 | 4.1662 | 0.025285 | 0.095801 | 3.2751 | 0.06505 | -5.3101 | 0.064087 | -23.7808 | -1.0208 | 0.22888 | -118.9087 | -118.9911 | 1.8768 | -1.181 | -0.20599 | 2.3438 | 2.3071 | -118.8446 | -118.84 | 0.050354 | -0.032044 | -2.3941 | 119.0231 | 117.9382 | 117.9703 | -7.933 | 0.11444 | 0.11902 | -0.27924 | 120.8359 | 118.7531 | 118.634 | -0.31586 | 119.1879 | 113.649 | 95.1782 | -121.6141 | 121.3028 | 121.2662 | 117.778 | -121.463
1544.6406 | 121.5912 | -118.9682 | 2.5818 | 0.26292 | 0.058369 | -0.00059506 | 0.35968 | 0.081168 | 0.70117 | -0.022126 | 0.18953 | 4.1598 | 0.049852 | 0.11716 | 3.2709 | 0.075732 | -5.5161 | 0.041199 | -23.6664 | -1.181 | 0.23346 | -118.9407 | -119.0186 | 1.8219 | -1.0712 | -0.25635 | 2.2888 | 2.2247 | -118.9133 | -118.8904 | 0.027466 | -0.050354 | -2.3483 | 119.0094 | 117.7872 | 117.8375 | -8.0978 | 0.054932 | 0.07782 | -0.29297 | 120.7901 | 118.7119 | 118.634 | -0.35706 | 119.2017 | 113.4521 | 95.3018 | -121.6003 | 121.257 | 121.1929 | 117.897 | -121.4722
1545.6406 | 121.5591 | -118.9133 | 2.6321 | 0.18663 | 0.032734 | 0.0015409 | 0.36609 | 0.093985 | 0.70971 | -0.022126 | 0.29634 | 4.1609 | 0.054124 | 0.10328 | 3.2687 | 0.078936 | -5.365 | 0.013733 | -23.1949 | -1.1444 | 0.21515 | -118.8904 | -118.9636 | 1.8539 | -1.1353 | -0.27008 | 2.3575 | 2.3163 | -118.84 | -118.8446 | 0.022888 | -0.050354 | -2.417 | 118.927 | 117.7689 | 117.8192 | -7.9971 | 0.073242 | 0.068665 | -0.27466 | 120.7672 | 118.6432 | 118.5745 | -0.31586 | 119.1284 | 113.5483 | 95.7184 | -121.5958 | 121.2708 | 121.2296 | 117.778 | -121.4767
1546.6406 | 121.5042 | -118.6432 | 2.8839 | 0.32395 | 0.064778 | -0.0016631 | 0.3693 | 0.10253 | 0.69903 | -0.022126 | 0.55574 | 4.1577 | 0.058397 | 0.099006 | 3.2655 | 0.080004 | -5.2689 | -0.050354 | -23.3688 | -1.0712 | 0.22888 | -118.6432 | -118.7485 | 2.0828 | -1.0208 | -0.25635 | 2.5909 | 2.5223 | -118.6203 | -118.5654 | 0 | -0.10529 | -2.655 | 118.5928 | 117.572 | 117.6773 | -8.1528 | 0.022888 | 0.077819 | -0.29297 | 120.726 | 118.3868 | 118.309 | -0.36163 | 118.8721 | 113.3743 | 95.2744 | -121.6324 | 121.2341 | 121.1655 | 117.6224 | -121.4493
1547.6406 | 121.5363 | -118.5928 | 2.9343 | 0.32395 | 0.064778 | -0.0027321 | 0.38318 | 0.092917 | 0.7001 | -0.024263 | 0.92195 | 4.163 | 0.060533 | 0.10007 | 3.2548 | 0.0768 | -5.2231 | -0.041199 | -23.8907 | -1.062 | 0.22888 | -118.5654 | -118.6523 | 2.1149 | -1.0437 | -0.27008 | 2.6733 | 2.6413 | -118.5379 | -118.5425 | 0.027465 | -0.05951 | -2.7054 | 118.5516 | 117.5308 | 117.5903 | -8.1573 | 0.054931 | 0.050354 | -0.26092 | 120.7077 | 118.3228 | 118.2724 | -0.29297 | 118.8217 | 113.3698 | 94.7021 | -121.5866 | 121.2662 | 121.2341 | 117.5491 | -121.4767
1548.6406 | 121.5134 | -118.5837 | 2.9572 | 0.12559 | 0.035939 | 0.0090179 | 0.3757 | 0.10146 | 0.69903 | -0.030671 | 0.52522 | 4.1534 | 0.069078 | 0.11396 | 3.2634 | 0.074663 | -5.2231 | -0.07782 | -23.9044 | -1.0162 | 0.24261 | -118.5471 | -118.6295 | 2.1561 | -1.0757 | -0.24719 | 2.6688 | 2.6413 | -118.5104 | -118.515 | 0.036621 | -0.045777 | -2.7145 | 118.5059 | 117.5674 | 117.6132 | -8.1802 | 0.073242 | 0.068664 | -0.28839 | 120.7397 | 118.3365 | 118.2678 | -0.31586 | 118.8263 | 113.3606 | 94.6793 | -121.5866 | 121.2524 | 121.225 | 117.5079 | -121.4722
1549.6406 | 121.6141 | -118.6523 | 2.8656 | 0.43077 | 0.038075 | -0.0027321 | 0.37357 | 0.095053 | 0.70223 | -0.025331 | 0.70833 | 4.1502 | 0.03917 | 0.095801 | 3.2591 | 0.069323 | -5.159 | -0.013733 | -23.7808 | -0.94757 | 0.2243 | -118.5883 | -118.6935 | 2.1194 | -0.9201 | -0.19684 | 2.5726 | 2.5085 | -118.6157 | -118.5654 | 0.064087 | -0.041198 | -2.6413 | 118.6386 | 117.7048 | 117.746 | -8.0246 | 0.036621 | 0.086975 | -0.29297 | 120.7718 | 118.4555 | 118.3685 | -0.35706 | 118.8766 | 113.4933 | 94.8715 | -121.5591 | 121.225 | 121.1609 | 117.7322 | -121.431
1550.6406 | 121.6187 | -118.602 | 2.8519 | 0.62913 | 0.044484 | -0.0048681 | 0.36395 | 0.090781 | 0.70117 | -0.036012 | 0.76936 | 4.147 | 0.066941 | 0.10435 | 3.2527 | 0.083208 | -5.0766 | 0.018311 | -24.0738 | -0.76446 | 0.20599 | -118.5699 | -118.6935 | 2.179 | -0.85144 | -0.14191 | 2.5543 | 2.5177 | -118.5745 | -118.5516 | 0.032044 | -0.091552 | -2.6459 | 118.6203 | 117.8375 | 117.9291 | -7.9285 | 0.027466 | 0.050354 | -0.29755 | 120.7809 | 118.4601 | 118.4097 | -0.33417 | 118.808 | 113.5254 | 94.5282 | -121.5454 | 121.1563 | 121.1197 | 117.7506 | -121.4035
1551.6406 | 121.6461 | -118.515 | 2.9343 | 0.61387 | 0.034871 | 0.0090179 | 0.38211 | 0.089713 | 0.6766 | -0.038148 | -2.7096 | 4.1427 | 0.044511 | 0.10328 | 3.2548 | 0.0768 | -4.8386 | 0.10529 | -24.2523 | -0.68207 | 0.18768 | -118.4875 | -118.6295 | 2.2842 | -0.88348 | -0.10071 | 2.623 | 2.5909 | -118.4326 | -118.4555 | 0.027466 | -0.11444 | -2.7466 | 118.6203 | 117.8329 | 117.9474 | -7.7728 | 0.082398 | 0.05951 | -0.31128 | 120.7993 | 118.4143 | 118.3548 | -0.34332 | 118.7027 | 113.6765 | 94.2627 | -121.5637 | 121.138 | 121.106 | 117.6315 | -121.3898
1552.6406 | 121.6415 | -118.5471 | 2.8702 | 0.26292 | 0.041279 | 0.0058129 | 0.38745 | 0.091849 | 0.7001 | -0.027467 | 0.72359 | 4.1374 | 0.057328 | 0.10328 | 3.2591 | 0.06505 | -4.8614 | 0.10529 | -24.0829 | -0.6958 | 0.1831 | -118.4967 | -118.6295 | 2.2385 | -0.74616 | -0.11444 | 2.5772 | 2.5635 | -118.5059 | -118.5013 | 0.050354 | -0.082398 | -2.6871 | 118.6523 | 117.8513 | 117.9337 | -7.7316 | 0.041199 | 0.045776 | -0.29297 | 120.7855 | 118.4326 | 118.3868 | -0.3067 | 118.7302 | 113.6856 | 94.4641 | -121.4996 | 121.1243 | 121.1105 | 117.8009 | -121.3715
1553.6406 | 121.5775 | -118.5928 | 2.8336 | 0.59861 | 0.035939 | 0.016495 | 0.3725 | 0.086509 | 0.68408 | -0.040284 | 0.81514 | 4.1427 | 0.044511 | 0.10221 | 3.2527 | 0.072527 | -4.9347 | 0.10529 | -24.0463 | -0.72327 | 0.19684 | -118.5562 | -118.6523 | 2.1698 | -0.79193 | -0.13275 | 2.5635 | 2.5177 | -118.5562 | -118.5242 | 0.036621 | -0.05951 | -2.6367 | 118.6981 | 117.8696 | 117.9291 | -7.7682 | 0.036621 | 0.068664 | -0.27008 | 120.7626 | 118.4601 | 118.3914 | -0.31586 | 118.7897 | 113.6581 | 94.5465 | -121.4859 | 121.1563 | 121.1105 | 117.8009 | -121.3577
1554.6406 | 121.582 | -118.3411 | 3.0716 | 0.55284 | 0.0081682 | 0.0090179 | 0.3693 | 0.089713 | 0.67874 | -0.040284 | 0.70833 | 4.1256 | 0.046647 | 0.091529 | 3.2463 | 0.072527 | -4.9393 | 0.073242 | -24.0829 | -0.72784 | 0.20142 | -118.3182 | -118.4326 | 2.3758 | -0.86517 | -0.15106 | 2.7969 | 2.742 | -118.3273 | -118.3044 | 0.022888 | -0.091553 | -2.8702 | 118.4143 | 117.6132 | 117.7048 | -8.0109 | 0.013732 | 0.036621 | -0.27466 | 120.7169 | 118.19 | 118.1534 | -0.32959 | 118.5425 | 113.4018 | 94.2581 | -121.5042 | 121.138 | 121.0831 | 117.4759 | -121.376
1555.6406 | 121.6141 | -118.6661 | 2.7466 | 0.29344 | 0.019917 | 0.0036769 | 0.37036 | 0.092917 | 0.68942 | -0.042421 | 0.63203 | 4.1384 | 0.049852 | 0.12037 | 3.2623 | 0.067187 | -4.9026 | 0.10529 | -24.2203 | -0.66834 | 0.20599 | -118.6615 | -118.7622 | 2.1011 | -0.77362 | -0.11444 | 2.4353 | 2.3987 | -118.6569 | -118.6249 | 0.004578 | -0.09613 | -2.5406 | 118.7714 | 117.9977 | 118.0939 | -7.6492 | 0.009156 | 0.041199 | -0.31128 | 120.7672 | 118.5516 | 118.5104 | -0.3479 | 118.8721 | 113.7634 | 94.4458 | -121.5088 | 121.1014 | 121.0648 | 117.8925 | -121.3715
1556.6406 | 121.5591 | -118.2953 | 3.1494 | 0.70542 | 0.0017592 | 0.01329 | 0.37464 | 0.073691 | 0.68621 | -0.034944 | 0.4947 | 4.116 | 0.026353 | 0.1161 | 3.2388 | 0.072527 | -4.8935 | 0.050354 | -24.3713 | -0.72784 | 0.21515 | -118.2907 | -118.3594 | 2.4307 | -0.87891 | -0.15106 | 2.8427 | 2.8015 | -118.2678 | -118.2632 | 0.004578 | -0.064087 | -2.9343 | 118.3456 | 117.5674 | 117.6315 | -8.0429 | 0.027466 | 0.032043 | -0.3067 | 120.726 | 118.1442 | 118.1122 | -0.3479 | 118.5104 | 113.4018 | 93.9239 | -121.5088 | 121.138 | 121.0968 | 117.4164 | -121.4127
1557.6406 | 121.6049 | -118.4052 | 3.0029 | 0.32395 | 0.0028272 | 0.0026089 | 0.37357 | 0.082236 | 0.67767 | -0.046693 | 0.40315 | 4.1235 | 0.042375 | 0.091529 | 3.2495 | 0.073595 | -5.278 | 0.050354 | -24.5132 | -0.62714 | 0.20599 | -118.3502 | -118.4189 | 2.1103 | -0.99335 | -0.20599 | 2.6962 | 2.655 | -118.364 | -118.3731 | 0.054931 | -0.013733 | -2.7969 | 118.4555 | 117.778 | 117.7917 | -8.2809 | 0.041198 | 0.032043 | -0.3067 | 120.5154 | 118.1992 | 118.1671 | -0.3479 | 118.6111 | 113.1271 | 93.8919 | -121.4218 | 121.1014 | 121.0602 | 117.4118 | -121.376
1558.6406 | 121.5912 | -118.6249 | 2.829 | 0.26292 | 0.0017592 | 0.0079499 | 0.3693 | 0.082236 | 0.6766 | -0.034944 | 0.29634 | 4.1363 | 0.049852 | 0.10007 | 3.2463 | 0.062914 | -5.3329 | -0.16479 | -23.9365 | -0.66376 | 0.13733 | -118.6066 | -118.721 | 2.1149 | -1.6754 | -0.13733 | 2.5131 | 2.4765 | -118.5883 | -118.5608 | 0.018311 | -0.09613 | -2.6917 | 118.4601 | 117.9611 | 118.0573 | -8.1619 | 0.036621 | 0.064087 | -0.31586 | 120.7397 | 118.4875 | 118.4235 | -0.35248 | 118.7622 | 113.2919 | 94.6884 | -121.55 | 121.138 | 121.1014 | 116.9495 | -121.3898
1559.6406 | 121.6232 | -118.5608 | 2.861 | 0.33921 | 0.0092362 | 0.0068819 | 0.37677 | 0.089713 | 0.68621 | -0.044557 | 0.28108 | 4.1278 | 0.032762 | 0.10648 | 3.2548 | 0.060778 | -5.0491 | 0.09613 | -23.6664 | -0.63171 | 0.20142 | -118.5562 | -118.6203 | 2.1927 | -0.38452 | -0.11902 | 2.5589 | 2.5223 | -118.4921 | -118.5196 | 0.004578 | -0.059509 | -2.6596 | 118.6569 | 117.9291 | 117.9886 | -7.9102 | 0.068665 | 0.041199 | -0.30212 | 120.7535 | 118.4418 | 118.4006 | -0.33874 | 118.7622 | 113.5117 | 94.8944 | -121.4813 | 121.1197 | 121.0831 | 118.1763 | -121.3806
1560.6875 | 121.5775 | -118.7302 | 2.6962 | 0.38499 | 0.022053 | -0.0027321 | 0.36075 | 0.092917 | 0.69796 | -0.03708 | 0.58626 | 4.1342 | 0.042375 | 0.097938 | 3.2612 | 0.066119 | -4.985 | 0.13275 | -23.703 | -0.64087 | 0.19226 | -118.6981 | -118.7668 | 2.037 | -0.44861 | -0.14191 | 2.3941 | 2.3438 | -118.6798 | -118.6523 | 0.032044 | -0.036621 | -2.504 | 118.8629 | 118.0893 | 118.1259 | -7.6813 | 0.050354 | 0.07782 | -0.30212 | 120.7672 | 118.5883 | 118.5104 | -0.35248 | 118.9224 | 113.7451 | 95.0272 | -121.463 | 121.1243 | 121.0739 | 118.2816 | -121.3486
1561.6406 | 121.6141 | -118.8034 | 2.5589 | 0.11033 | -0.0067858 | 0.0068819 | 0.36395 | 0.086509 | 0.6798 | -0.03708 | 0.14375 | 4.1395 | 0.038102 | 0.093665 | 3.2559 | 0.075732 | -4.9301 | 0.1236 | -23.7259 | -0.74616 | 0.21515 | -118.7714 | -118.8995 | 1.9547 | -0.44403 | -0.10529 | 2.298 | 2.2156 | -118.7714 | -118.7485 | 0.032044 | -0.09613 | -2.3438 | 118.927 | 118.0573 | 118.1534 | -7.489 | 0.032044 | 0.054932 | -0.26092 | 120.7581 | 118.6981 | 118.6432 | -0.34332 | 119.0186 | 113.8733 | 95.0775 | -121.4584 | 121.1014 | 121.019 | 118.3594 | -121.3074
1562.6406 | 121.6324 | -118.7759 | 2.6047 | 0.034038 | 0.025258 | 0.0058129 | 0.35434 | 0.082236 | 0.67767 | -0.034944 | 0.54048 | 4.1342 | 0.03383 | 0.097938 | 3.2634 | 0.052233 | -4.8798 | 0.16937 | -23.4238 | -0.94757 | 0.21973 | -118.7576 | -118.8721 | 2.0004 | -0.43488 | -0.091553 | 2.3254 | 2.2659 | -118.721 | -118.7073 | 0.018311 | -0.09613 | -2.3849 | 118.9453 | 117.8284 | 117.9245 | -7.4844 | 0.054932 | 0.068665 | -0.27924 | 120.7764 | 118.6844 | 118.6157 | -0.33874 | 118.9957 | 113.8962 | 95.3522 | -121.4767 | 121.1014 | 121.0419 | 118.3411 | -121.3119
1563.6406 | 121.5683 | -118.4189 | 2.9663 | -2.2853 | -0.0089218 | 0.010086 | 0.35648 | 0.090781 | 0.68194 | -0.027467 | -0.054612 | 4.1331 | 0.031694 | 0.1161 | 3.257 | 0.06505 | -4.9576 | 0.16022 | -22.4991 | -0.81482 | 0.1831 | -118.4372 | -118.5333 | 2.2751 | -0.50354 | -0.13733 | 2.6825 | 2.6184 | -118.4143 | -118.4052 | -0.018311 | -0.11444 | -2.7832 | 118.5791 | 117.6041 | 117.7185 | -7.9239 | 0.004577 | 0.013733 | -0.28381 | 120.694 | 118.2816 | 118.2678 | -0.3479 | 118.602 | 113.4613 | 95.9198 | -121.4996 | 121.1014 | 121.0373 | 117.9153 | -121.3715
1564.6406 | 121.5546 | -118.7302 | 2.6779 | -0.30166 | 0.0049632 | 0.011154 | 0.36609 | 0.087577 | 0.68835 | -0.038148 | -0.13091 | 4.1384 | 0.038102 | 0.092597 | 3.2527 | 0.06505 | -4.9576 | 0.14648 | -22.9477 | -1.1673 | 0.18768 | -118.7027 | -118.7759 | 2.0004 | -0.49896 | -0.16022 | 2.3804 | 2.3483 | -118.7302 | -118.6432 | 0.027466 | -0.045776 | -2.4902 | 118.8766 | 117.5629 | 117.6086 | -7.6355 | 0 | 0.086976 | -0.29755 | 120.7306 | 118.5699 | 118.483 | -0.32959 | 118.9178 | 113.7726 | 95.7825 | -121.4539 | 121.1105 | 121.0785 | 118.2312 | -121.3211
1565.6406 | 121.4951 | -118.5745 | 2.8564 | -0.25588 | 0.014576 | 0.014358 | 0.35541 | 0.083304 | 0.69155 | -0.024263 | -0.19194 | 4.1352 | 0.040239 | 0.094733 | 3.2591 | 0.069323 | -4.9438 | 0.11902 | -22.261 | -1.0849 | 0.20142 | -118.5471 | -118.6523 | 2.1103 | -0.48065 | -0.17395 | 2.5497 | 2.5085 | -118.5425 | -118.5562 | 0.027466 | -0.07782 | -2.655 | 118.6935 | 117.4896 | 117.5674 | -7.8003 | 0.032044 | 0.018311 | -0.3067 | 120.6848 | 118.4006 | 118.3823 | -0.3479 | 118.7759 | 113.6307 | 96.3135 | -121.5088 | 121.1243 | 121.0831 | 118.0939 | -121.4127
1566.6406 | 121.463 | -118.7759 | 2.6276 | -0.2101 | 0.0038952 | 0.01329 | 0.35648 | 0.086509 | 0.69689 | -0.034944 | -0.19194 | 4.1374 | 0.045579 | 0.10648 | 3.2591 | 0.062914 | -5.0262 | 0.091553 | -22.9523 | -1.2131 | 0.20599 | -118.7576 | -118.8446 | 1.8997 | -0.44403 | -0.16479 | 2.3849 | 2.3392 | -118.7485 | -118.7164 | 0.018311 | -0.068664 | -2.4216 | 118.8675 | 117.5629 | 117.6315 | -7.6538 | 0.027466 | 0.059509 | -0.24261 | 120.6757 | 118.6111 | 118.5516 | -0.28839 | 118.9819 | 113.7497 | 95.8237 | -121.4722 | 121.1609 | 121.1151 | 118.3319 | -121.344
1567.6406 | 121.4676 | -118.7027 | 2.7466 | -0.25588 | 0.033803 | 0.014358 | 0.36075 | 0.098258 | 0.69689 | -0.022126 | 1.1051 | 4.147 | 0.042375 | 0.090461 | 3.2548 | 0.066119 | -4.9667 | 0.19684 | -22.8012 | -0.74616 | 0.27466 | -118.6066 | -118.7256 | 1.9821 | -0.44861 | -0.21515 | 2.4765 | 2.417 | -118.634 | -118.6569 | 0.096131 | -0.022888 | -2.4719 | 118.8995 | 117.9565 | 117.9794 | -7.7133 | 0.068665 | 0.045777 | -0.27008 | 120.6848 | 118.4875 | 118.4418 | -0.32959 | 118.9774 | 113.736 | 95.9015 | -121.4722 | 121.1792 | 121.1197 | 118.2541 | -121.4035
1568.6406 | 121.4493 | -118.6478 | 2.7969 | -0.24062 | 0.037007 | 0.014358 | 0.35968 | 0.088645 | 0.69369 | -0.040284 | -0.2072 | 4.1363 | 0.03383 | 0.10862 | 3.2442 | 0.062914 | -4.9255 | 0.032043 | -23.5657 | -0.91553 | 0.25635 | -118.6249 | -118.7393 | 1.9958 | -0.44861 | -0.20142 | 2.5223 | 2.4719 | -118.5928 | -118.602 | 0.022888 | -0.091553 | -2.5406 | 118.6798 | 117.7322 | 117.8238 | -7.7225 | 0.054932 | 0.045776 | -0.27466 | 120.6436 | 118.4464 | 118.4006 | -0.32501 | 118.9041 | 113.7222 | 95.0821 | -121.5363 | 121.17 | 121.1197 | 118.1992 | -121.3989
1569.6406 | 121.5042 | -118.6981 | 2.7008 | -0.16433 | 0.02419 | -0.0038001 | 0.38532 | 0.089713 | 0.70544 | -0.033876 | -0.23772 | 4.1363 | 0.044511 | 0.10541 | 3.2623 | 0.067187 | -4.9622 | 0.009155 | -24.1608 | -1.2497 | 0.2243 | -118.6935 | -118.7943 | 1.9547 | -0.40741 | -0.19684 | 2.4399 | 2.3712 | -118.6707 | -118.6249 | 0.004578 | -0.09613 | -2.4765 | 118.7073 | 117.4484 | 117.5446 | -7.663 | 0.027466 | 0.073242 | -0.26093 | 120.6528 | 118.5013 | 118.428 | -0.32959 | 118.9224 | 113.736 | 94.5374 | -121.4951 | 121.138 | 121.0693 | 118.2907 | -121.3257
1570.6406 | 121.4767 | -118.6935 | 2.7466 | -0.11855 | 0.054097 | 0.0058129 | 0.3693 | 0.092917 | 0.71185 | -0.028535 | -0.17668 | 4.1406 | 0.042375 | 0.10541 | 3.2495 | 0.071459 | -4.9301 | 0.022888 | -24.7009 | -0.95673 | 0.21973 | -118.6661 | -118.7576 | 1.9958 | -0.41657 | -0.19684 | 2.4536 | 2.3895 | -118.6249 | -118.634 | 0.027465 | -0.064087 | -2.5269 | 118.7164 | 117.7368 | 117.8009 | -7.6767 | 0.068664 | 0.059509 | -0.29297 | 120.6894 | 118.4967 | 118.4372 | -0.35706 | 118.9133 | 113.7634 | 93.9926 | -121.5042 | 121.1472 | 121.0831 | 118.277 | -121.3806
1571.6406 | 121.463 | -118.6478 | 2.7466 | 0.20188 | 0.060505 | 0.0058129 | 0.37143 | 0.10573 | 0.70864 | -0.022126 | 0.20479 | 4.147 | 0.069078 | 0.089393 | 3.2623 | 0.060778 | -4.8935 | 0.018311 | -24.3851 | -1.4145 | 0.20142 | -118.6249 | -118.7256 | 2.0004 | -0.46692 | -0.20142 | 2.4719 | 2.4078 | -118.602 | -118.6203 | 0.022888 | -0.07782 | -2.5452 | 118.6661 | 117.2333 | 117.3111 | -7.6401 | 0.045776 | 0.027466 | -0.27466 | 120.6482 | 118.4464 | 118.4189 | -0.33875 | 118.8492 | 113.7543 | 94.2627 | -121.4722 | 121.1197 | 121.0556 | 118.1808 | -121.3669
1572.6406 | 121.4951 | -118.6478 | 2.742 | 0.095073 | 0.04662 | 0.0047449 | 0.37998 | 0.090781 | 0.69689 | -0.028535 | 0.067459 | 4.1449 | 0.057328 | 0.097938 | 3.2506 | 0.070391 | -4.7791 | 0.068665 | -23.8953 | -1.5289 | 0.23346 | -118.6432 | -118.7439 | 2.0325 | -0.37079 | -0.12817 | 2.449 | 2.4261 | -118.602 | -118.5974 | 0.004578 | -0.09613 | -2.5085 | 118.7164 | 117.1188 | 117.215 | -7.5211 | 0.045776 | 0.050354 | -0.29297 | 120.6802 | 118.5196 | 118.4692 | -0.31586 | 118.8812 | 113.8687 | 94.7525 | -121.4859 | 121.0968 | 121.0739 | 118.277 | -121.3394
1573.6406 | 121.5179 | -118.309 | 3.1036 | 0.00352 | 0.055165 | 0.0079499 | 0.36823 | 0.082236 | 0.7033 | -0.01999 | 0.17427 | 4.1224 | 0.051988 | 0.10007 | 3.2506 | 0.069323 | -4.7333 | 0.059509 | -23.8907 | -1.2589 | 0.22888 | -118.3411 | -118.428 | 2.3071 | -0.39825 | -0.14191 | 2.7466 | 2.6962 | -118.2312 | -118.19 | -0.032043 | -0.11902 | -2.8748 | 118.3685 | 117.0502 | 117.1692 | -7.8369 | 0.07782 | 0.11902 | -0.35706 | 120.6162 | 118.1671 | 118.0481 | -0.40741 | 118.5379 | 113.5757 | 94.4183 | -121.5317 | 121.0556 | 121.0052 | 117.9108 | -121.2936
1574.6406 | 121.4401 | -118.4052 | 3.0075 | 0.20188 | 0.066914 | 0.00047294 | 0.37998 | 0.084372 | 0.69155 | -0.029603 | 0.32686 | 4.1203 | 0.053056 | 0.10007 | 3.2474 | 0.073595 | -4.985 | -0.004578 | -24.4492 | -1.5839 | 0.21057 | -118.3823 | -118.5013 | 2.2247 | -0.48523 | -0.20599 | 2.7283 | 2.6642 | -118.3914 | -118.3685 | 0.022888 | -0.096131 | -2.7969 | 118.4006 | 116.8213 | 116.9174 | -7.9926 | 0.013733 | 0.036621 | -0.27924 | 120.6299 | 118.1992 | 118.1625 | -0.34332 | 118.6157 | 113.4201 | 93.956 | -121.5088 | 121.1334 | 121.0693 | 117.9199 | -121.376
1575.6406 | 121.4493 | -118.4143 | 2.9709 | 3.0248 | 0.075459 | 0.0058129 | 0.38639 | 0.096122 | 0.70117 | -0.028535 | 0.28108 | 4.1374 | 0.049852 | 0.07978 | 3.2484 | 0.061846 | -5.3467 | 0.064087 | -23.8083 | -1.4236 | 0.27466 | -118.3685 | -118.4692 | 2.2385 | -0.37079 | -0.10071 | 2.6825 | 2.6413 | -118.3731 | -118.3731 | 0.045777 | -0.054931 | -2.6962 | 118.4784 | 116.9907 | 117.0456 | -8.3176 | 0.041199 | 0.041199 | -0.28839 | 120.6528 | 118.3136 | 118.2724 | -0.32959 | 118.689 | 113.0676 | 94.606 | -121.4401 | 121.0968 | 121.0556 | 118.0435 | -121.344
1576.6406 | 121.376 | -118.4418 | 2.9755 | 0.24766 | 0.048756 | -0.00059506 | 0.38745 | 0.08544 | 0.69155 | -0.027467 | 0.54048 | 4.132 | 0.059465 | 0.10007 | 3.2378 | 0.073595 | -5.1498 | -0.064087 | -23.7808 | -1.268 | 0.21973 | -118.4052 | -118.5013 | 2.1652 | -0.56305 | -0.17853 | 2.7008 | 2.6733 | -118.4235 | -118.3823 | 0.036621 | -0.05951 | -2.7557 | 118.3777 | 117.1738 | 117.2333 | -8.1253 | 0.01831 | 0.059509 | -0.27466 | 120.607 | 118.2632 | 118.2037 | -0.30212 | 118.6615 | 113.2919 | 94.6609 | -121.4767 | 121.1426 | 121.1151 | 117.8787 | -121.3577
1577.6406 | 121.4493 | -118.4647 | 2.916 | 0.47654 | 0.050892 | 0.00047294 | 0.36609 | 0.083304 | 0.68514 | -0.045625 | 1.044 | 4.1256 | 0.044511 | 0.10755 | 3.2388 | 0.080004 | -5.0812 | -0.11444 | -23.6984 | -1.561 | 0.26093 | -118.4235 | -118.515 | 2.1561 | -0.50812 | -0.14191 | 2.6413 | 2.6047 | -118.4189 | -118.3868 | 0.041199 | -0.050354 | -2.655 | 118.3502 | 116.9037 | 116.954 | -7.9971 | 0.045777 | 0.07782 | -0.27466 | 120.6207 | 118.3228 | 118.2449 | -0.31128 | 118.7256 | 113.3835 | 94.7662 | -121.431 | 121.106 | 121.0693 | 117.9565 | -121.3028
1578.6406 | 121.3074 | -118.428 | 2.9297 | 0.35447 | 0.071187 | 0.0079499 | 0.37891 | 0.087577 | 0.68835 | -0.027467 | 0.61677 | 4.1363 | 0.066941 | 0.10648 | 3.2442 | 0.074663 | -5.3329 | -0.054932 | -24.2661 | -1.1673 | 0.23346 | -118.4738 | -118.5562 | 2.1332 | -0.54474 | -0.16022 | 2.6276 | 2.6001 | -118.4372 | -118.4052 | -0.045776 | -0.12817 | -2.6962 | 118.3731 | 117.2607 | 117.3889 | -8.2626 | -0.009155 | 0.022889 | -0.30212 | 120.5612 | 118.2678 | 118.2449 | -0.32959 | 118.6615 | 113.0951 | 94.162 | -121.4859 | 121.0556 | 121.0281 | 117.8833 | -121.3348
1579.6406 | 121.4539 | -118.396 | 2.948 | 0.50706 | 0.027394 | 0.0058129 | 0.36182 | 0.09719 | 0.69048 | -0.027467 | 0.69307 | 4.1342 | 0.051988 | 0.10114 | 3.2442 | 0.08214 | -5.1041 | -0.022888 | -24.44 | -0.95215 | 0.22888 | -118.3731 | -118.4967 | 2.2293 | -0.3891 | -0.07782 | 2.6733 | 2.6276 | -118.3731 | -118.3456 | 0.022888 | -0.10071 | -2.7191 | 118.3731 | 117.4438 | 117.5446 | -8.0521 | 0.022888 | 0.050354 | -0.27466 | 120.6253 | 118.3182 | 118.2678 | -0.32044 | 118.6249 | 113.2919 | 93.956 | -121.4447 | 121.0693 | 121.0236 | 118.0069 | -121.2936
1580.6406 | 121.4218 | -118.6386 | 2.7512 | 0.47654 | 0.06371 | -0.0038001 | 0.38852 | 0.083304 | 0.71078 | -0.0039683 | 0.12849 | 4.1363 | 0.049852 | 0.095801 | 3.2474 | 0.075732 | -5.8685 | 0.28839 | -24.5316 | -0.9201 | 0.23804 | -118.5837 | -118.6707 | 1.9913 | -0.45776 | -0.13275 | 2.4857 | 2.449 | -118.602 | -118.5699 | 0.054932 | -0.032043 | -2.5131 | 118.927 | 117.7185 | 117.7505 | -8.6197 | 0.036621 | 0.068665 | -0.2655 | 120.6299 | 118.5059 | 118.4372 | -0.30212 | 118.8766 | 112.7701 | 94.1071 | -121.4218 | 121.1243 | 121.0876 | 118.1808 | -121.3211
1581.6406 | 121.5271 | -118.5379 | 2.7695 | 0.61387 | 0.034871 | 0.0068819 | 0.37784 | 0.082236 | 0.68621 | -0.027467 | 0.7541 | 4.1256 | 0.047715 | 0.10328 | 3.2527 | 0.069323 | -5.3009 | 0.018311 | -24.3484 | -0.89264 | 0.20599 | -118.4967 | -118.6203 | 2.0966 | -0.32501 | -0.022888 | 2.4765 | 2.4445 | -118.5196 | -118.4921 | 0.041199 | -0.082397 | -2.5635 | 118.5562 | 117.6453 | 117.7277 | -8.0704 | 0.018311 | 0.045777 | -0.29297 | 120.6345 | 118.515 | 118.4692 | -0.32501 | 118.7439 | 113.237 | 94.1895 | -121.3898 | 121.0144 | 120.9824 | 118.2129 | -121.2616
1582.6406 | 121.4539 | -118.6157 | 2.7466 | 0.27818 | 0.02953 | 0.0026089 | 0.38318 | 0.086509 | 0.69476 | -0.031739 | 0.63203 | 4.1256 | 0.051988 | 0.093665 | 3.2495 | 0.068255 | -5.6442 | -0.050354 | -24.0784 | -0.85144 | 0.23346 | -118.5745 | -118.6707 | 2.0233 | -0.3891 | -0.091553 | 2.4673 | 2.4399 | -118.5562 | -118.5471 | 0.041199 | -0.054931 | -2.5131 | 118.5654 | 117.7643 | 117.8192 | -8.3908 | 0.05951 | 0.068665 | -0.27924 | 120.639 | 118.5242 | 118.4555 | -0.3067 | 118.8492 | 112.9715 | 94.5374 | -121.4172 | 121.0831 | 121.0556 | 118.2266 | -121.2936
1583.6406 | 121.5363 | -118.4235 | 2.861 | 0.35447 | 0.053029 | 0.00047294 | 0.36182 | 0.087577 | 0.68942 | -0.036012 | 0.89143 | 4.1235 | 0.053056 | 0.10114 | 3.242 | 0.072527 | -5.246 | 0.10529 | -24.5636 | -0.6958 | 0.19684 | -118.4235 | -118.5196 | 2.211 | -0.3067 | -0.027466 | 2.5635 | 2.536 | -118.4143 | -118.3731 | 0 | -0.09613 | -2.6642 | 118.5287 | 117.7277 | 117.8238 | -8.107 | 0.009155 | 0.050354 | -0.29755 | 120.6345 | 118.396 | 118.3456 | -0.32501 | 118.6203 | 113.1775 | 93.8599 | -121.3806 | 120.9869 | 120.9595 | 118.1168 | -121.2341
1584.6406 | 121.4767 | -118.4921 | 2.7786 | -3.0025 | 0.034871 | 0.012222 | 0.37677 | 0.086509 | 0.67874 | -0.038148 | 0.67781 | 4.1149 | 0.045579 | 0.11075 | 3.2431 | 0.067187 | -5.04 | 0.10986 | -24.115 | -1.062 | 0.17395 | -118.4875 | -118.5699 | 2.1423 | -0.36621 | -0.027466 | 2.4994 | 2.4719 | -118.4875 | -118.4509 | 0.004577 | -0.07782 | -2.6047 | 118.602 | 117.4301 | 117.5079 | -7.8186 | 0.004577 | 0.041198 | -0.27923 | 120.6345 | 118.4647 | 118.4235 | -0.3067 | 118.6661 | 113.4521 | 94.3771 | -121.3486 | 120.9915 | 120.9641 | 118.1259 | -121.2296
1585.6406 | 121.6141 | -118.4601 | 2.861 | 0.64439 | 0.031666 | 0.0015409 | 0.36502 | 0.077964 | 0.68408 | -0.031739 | 0.79988 | 4.1128 | 0.041307 | 0.092597 | 3.2399 | 0.072527 | -4.9118 | 0.086975 | -24.0143 | -1.0712 | 0.18768 | -118.3594 | -118.4509 | 2.2705 | -0.29755 | -0.022888 | 2.6321 | 2.5772 | -118.4326 | -118.4052 | 0.10071 | 0.009155 | -2.6733 | 118.5471 | 117.3889 | 117.3798 | -7.7728 | 0.027466 | 0.054932 | -0.22888 | 120.7306 | 118.4372 | 118.3823 | -0.28381 | 118.6478 | 113.5483 | 94.4458 | -121.312 | 121.0922 | 121.0373 | 118.1625 | -121.2662
1586.6406 | 121.4905 | -118.4052 | 2.8702 | 0.56809 | 0.04662 | 0.0058129 | 0.38104 | 0.089713 | 0.69369 | -0.036012 | 0.70833 | 4.1235 | 0.040239 | 0.089393 | 3.2388 | 0.071459 | -5.2185 | 0.091553 | -23.8541 | -1.0529 | 0.20142 | -118.3823 | -118.4784 | 2.2064 | -0.27466 | -0.004578 | 2.5497 | 2.504 | -118.3685 | -118.364 | 0.022888 | -0.073243 | -2.6688 | 118.4967 | 117.3523 | 117.4255 | -8.0887 | 0.036621 | 0.041198 | -0.32043 | 120.6116 | 118.4006 | 118.3594 | -0.36621 | 118.6066 | 113.1866 | 94.5511 | -121.3486 | 120.9549 | 120.9091 | 118.1305 | -121.2341
1587.6406 | 121.4539 | -118.3136 | 2.98 | 0.44602 | 0.015645 | 0.012222 | 0.36502 | 0.087577 | 0.67233 | -0.038148 | 0.72359 | 4.1192 | 0.044511 | 0.10969 | 3.2388 | 0.075732 | -5.1773 | 0.10529 | -24.0784 | -1.268 | 0.21057 | -118.2861 | -118.3502 | 2.3026 | -0.4303 | -0.009155 | 2.7237 | 2.6459 | -118.309 | -118.2404 | 0.027466 | -0.036621 | -2.7695 | 118.4189 | 117.0456 | 117.0822 | -8.1573 | 0.004578 | 0.073243 | -0.25635 | 120.6161 | 118.3044 | 118.2312 | -0.33417 | 118.5242 | 113.1363 | 94.2352 | -121.3303 | 121.0373 | 120.9595 | 117.8833 | -121.2204
1588.6406 | 121.463 | -118.2358 | 3.0624 | -2.5905 | 0.048756 | -0.0038001 | 0.36823 | 0.095053 | 0.67874 | -0.03708 | 0.58626 | 4.1107 | 0.028489 | 0.11716 | 3.2356 | 0.069323 | -5.0171 | 0.12817 | -23.7167 | -1.4374 | 0.17853 | -118.2083 | -118.2907 | 2.417 | -0.28839 | 0.022888 | 2.7512 | 2.7054 | -118.2266 | -118.2175 | 0.027466 | -0.054931 | -2.8839 | 118.364 | 116.7984 | 116.8533 | -8.0795 | 0.009155 | 0.018311 | -0.31128 | 120.6528 | 118.2587 | 118.2404 | -0.35706 | 118.4143 | 113.2187 | 94.519 | -121.3531 | 120.9869 | 120.9412 | 117.9474 | -121.2799
1589.6406 | 121.5042 | -118.2678 | 3.0075 | 0.15611 | 0.00069119 | -0.0027321 | 0.37998 | 0.089713 | 0.66165 | -0.039216 | 0.14375 | 4.0979 | 0.040239 | 0.087256 | 3.2367 | 0.05971 | -4.9072 | 0.15106 | -23.7991 | -1.1765 | 0.20599 | -118.2449 | -118.364 | 2.3529 | -0.2243 | 0.013733 | 2.6962 | 2.6733 | -118.2907 | -118.2404 | 0.022888 | -0.096131 | -2.8015 | 118.4189 | 117.0914 | 117.1875 | -7.9147 | -0.022888 | 0.027466 | -0.31128 | 120.6207 | 118.2816 | 118.2541 | -0.33417 | 118.4738 | 113.3606 | 94.4687 | -121.3715 | 120.9641 | 120.9412 | 118.0435 | -121.2479
1590.6406 | 121.4676 | -118.2999 | 3.0075 | 0.18663 | 0.0017592 | 0.016495 | 0.36075 | 0.0801 | 0.67339 | -0.053102 | 0.47945 | 4.1021 | 0.038102 | 0.096869 | 3.2324 | 0.06505 | -4.9484 | 0.050354 | -24.0143 | -1.0986 | 0.15106 | -118.2953 | -118.3777 | 2.3117 | -0.3067 | -0.022888 | 2.7283 | 2.6733 | -118.2861 | -118.2724 | 0.004578 | -0.07782 | -2.8564 | 118.3502 | 117.2012 | 117.2791 | -7.9559 | 0.013733 | 0.027466 | -0.27924 | 120.6116 | 118.277 | 118.2495 | -0.33417 | 118.4509 | 113.3514 | 94.2856 | -121.3852 | 121.0281 | 120.9732 | 117.9932 | -121.2799
1591.6406 | 121.4127 | -118.3228 | 2.9709 | 0.29344 | 0.0049632 | 0.0079499 | 0.35648 | 0.091849 | 0.67019 | -0.041353 | 0.38789 | 4.1075 | 0.025285 | 0.081916 | 3.242 | 0.06505 | -4.9713 | 0.054932 | -23.8998 | -0.70038 | 0.21515 | -118.2495 | -118.3365 | 2.3346 | -0.33875 | -0.041199 | 2.742 | 2.7008 | -118.3685 | -118.3594 | 0.073242 | -0.013733 | -2.7557 | 118.3777 | 117.6224 | 117.6361 | -7.9422 | -0.045776 | -0.036621 | -0.22888 | 120.6573 | 118.2816 | 118.3182 | -0.27008 | 118.5379 | 113.3514 | 94.4229 | -121.3074 | 121.0648 | 121.0236 | 117.984 | -121.3303
1592.6406 | 121.4676 | -118.2953 | 2.9663 | 0.3087 | 0.01244 | 0.0079499 | 0.36823 | 0.087577 | 0.68728 | -0.036012 | -1.7636 | 4.1032 | 0.037034 | 0.096869 | 3.2249 | 0.060778 | -4.9713 | 0.045776 | -23.5153 | -0.71869 | 0.21515 | -118.2495 | -118.4143 | 2.298 | -0.32959 | -0.059509 | 2.655 | 2.6138 | -118.3182 | -118.2816 | 0.045776 | -0.11902 | -2.7512 | 118.3411 | 117.5766 | 117.6956 | -7.9376 | -0.022888 | 0.013733 | -0.31128 | 120.5933 | 118.2358 | 118.222 | -0.35248 | 118.5104 | 113.324 | 94.78 | -121.3806 | 120.9503 | 120.9091 | 117.9657 | -121.2479
1593.6406 | 121.4722 | -118.3228 | 2.9892 | 0.15611 | 0.016713 | -0.0027321 | 0.38318 | 0.084372 | 0.67874 | -0.03708 | 0.28108 | 4.1085 | 0.049852 | 0.093665 | 3.2335 | 0.072527 | -5.0308 | 0.045776 | -23.3459 | -0.91553 | 0.16022 | -118.3365 | -118.428 | 2.3071 | -0.29755 | -0.013733 | 2.6825 | 2.6321 | -118.2953 | -118.277 | -0.013733 | -0.10529 | -2.829 | 118.3685 | 117.4072 | 117.5125 | -8.02 | 0.027466 | 0.045776 | -0.3067 | 120.6299 | 118.309 | 118.2632 | -0.35706 | 118.483 | 113.2919 | 94.9768 | -121.4172 | 121.0052 | 120.9549 | 118.0252 | -121.2662
1594.6406 | 121.4035 | -118.3502 | 2.9846 | 0.049296 | 0.051961 | -0.084976 | 0.36075 | 0.093985 | 0.72573 | -0.024263 | -0.0088351 | 4.1203 | 0.064805 | 0.10328 | 3.2228 | 0.057574 | -5.0034 | 0.086975 | -23.6206 | -0.737 | 0.27466 | -118.2907 | -118.4189 | 2.2842 | -0.3479 | -0.13733 | 2.6917 | 2.6321 | -118.3136 | -118.2724 | 0.05951 | -0.068664 | -2.71 | 118.4372 | 117.6132 | 117.6819 | -7.988 | 0.036621 | 0.07782 | -0.29297 | 120.6345 | 118.2129 | 118.1351 | -0.35248 | 118.6249 | 113.3469 | 94.7296 | -121.4035 | 121.0419 | 120.9824 | 118.0023 | -121.257
1595.6406 | 121.4447 | -118.3823 | 2.9205 | -0.19484 | 0.0028272 | 0.019699 | 0.36823 | 0.086509 | 0.64883 | -0.041353 | 0.29634 | 4.116 | 0.03383 | 0.11075 | 3.2367 | 0.070391 | -5.0171 | -0.17395 | -24.0967 | -0.88348 | 0.17395 | -118.3319 | -118.4601 | 2.2522 | -0.21057 | -0.009155 | 2.6184 | 2.5955 | -118.3319 | -118.3044 | 0.050354 | -0.07782 | -2.7466 | 118.2083 | 117.4988 | 117.5766 | -7.9376 | 0.050354 | 0.07782 | -0.30212 | 120.6345 | 118.3731 | 118.2953 | -0.32501 | 118.5562 | 113.3652 | 94.2856 | -121.3806 | 121.0007 | 120.9778 | 118.1717 | -121.225
1596.6406 | 121.5134 | -118.3777 | 2.8885 | 0.00352 | -0.012126 | 0.021835 | 0.36716 | 0.081168 | 0.67126 | -0.039216 | 0.18953 | 4.1171 | 0.041307 | 0.096869 | 3.2303 | 0.083208 | -5.2872 | 0.14191 | -23.8266 | -0.84228 | 0.21973 | -118.3502 | -118.4326 | 2.2934 | -0.22888 | 0.032043 | 2.6138 | 2.5681 | -118.3365 | -118.3228 | 0.027466 | -0.054931 | -2.6688 | 118.5196 | 117.5354 | 117.5903 | -8.1757 | 0.041199 | 0.054932 | -0.27466 | 120.6711 | 118.4097 | 118.3548 | -0.32043 | 118.5974 | 113.0905 | 94.5511 | -121.3211 | 120.9915 | 120.9457 | 118.1488 | -121.2112
1597.6406 | 121.4401 | -118.4097 | 2.8793 | -0.11855 | 0.01244 | 0.014358 | 0.38318 | 0.083304 | 0.68835 | -0.041353 | 0.021682 | 4.1117 | 0.032762 | 0.06269 | 3.2399 | 0.077868 | -5.1361 | 0.16937 | -24.0463 | -0.92926 | 0.19684 | -118.3594 | -118.4555 | 2.2156 | -0.3891 | 0.041199 | 2.5909 | 2.536 | -118.3594 | -118.3502 | 0.050354 | -0.045776 | -2.6825 | 118.5791 | 117.4805 | 117.5262 | -8.0154 | 0.050354 | 0.059509 | -0.28839 | 120.6253 | 118.4509 | 118.3914 | -0.34332 | 118.6066 | 113.2736 | 94.3634 | -121.3348 | 121.0007 | 120.9457 | 118.0206 | -121.2296
1598.6406 | 121.4447 | -118.3044 | 2.9617 | -0.16433 | 0.0081682 | 0.017563 | 0.36609 | 0.070487 | 0.64349 | -0.046693 | 0.63203 | 4.1096 | 0.028489 | 0.10007 | 3.2399 | 0.061846 | -4.9988 | -0.17853 | -24.3668 | -1.0803 | 0.18768 | -118.2907 | -118.3914 | 2.3071 | -0.2243 | 0.004578 | 2.6779 | 2.6093 | -118.2861 | -118.277 | 0.013733 | -0.086975 | -2.774 | 118.1259 | 117.2241 | 117.3111 | -7.9605 | 0.01831 | 0.027465 | -0.28381 | 120.6116 | 118.309 | 118.2816 | -0.35248 | 118.4921 | 113.3057 | 93.9377 | -121.3531 | 120.9824 | 120.9137 | 118.0801 | -121.2387
1599.6406 | 121.3577 | -118.3868 | 2.916 | 0.20188 | 0.043416 | -0.062546 | 0.39173 | 0.088645 | 0.71612 | -0.032808 | 0.021682 | 4.1203 | 0.060533 | 0.099006 | 3.2506 | 0.053301 | -5.3329 | 0.027466 | -23.8449 | -1.1444 | 0.21973 | -118.3502 | -118.4555 | 2.179 | -0.39825 | -0.17395 | 2.6459 | 2.5955 | -118.3548 | -118.364 | 0.036621 | -0.068664 | -2.6962 | 118.4143 | 117.2424 | 117.3111 | -8.2489 | 0.032044 | 0.022888 | -0.27008 | 120.5658 | 118.2129 | 118.19 | -0.32043 | 118.6066 | 113.0539 | 94.5419 | -121.3715 | 121.0327 | 120.9824 | 117.9886 | -121.2799
1600.6406 | 121.4081 | -118.3731 | 2.948 | -0.2101 | 0.018849 | 0.00047294 | 0.36075 | 0.089713 | 0.68621 | -0.025331 | -0.085129 | 4.1 | 0.046647 | 0.094733 | 3.2367 | 0.069323 | -5.191 | 0.13733 | -23.7122 | -0.95215 | 0.20599 | -118.3182 | -118.4189 | 2.2568 | -0.27924 | -0.036621 | 2.6596 | 2.6138 | -118.3456 | -118.2953 | 0.054932 | -0.045776 | -2.742 | 118.5104 | 117.421 | 117.4667 | -8.139 | 0.027466 | 0.07782 | -0.28839 | 120.6299 | 118.3365 | 118.2587 | -0.33417 | 118.5791 | 113.1821 | 94.6609 | -121.3669 | 121.0327 | 120.9869 | 118.0939 | -121.2433
1601.6406 | 121.344 | -118.3456 | 2.9846 | -0.65261 | 0.019917 | 0.014358 | 0.38532 | 0.079032 | 0.6798 | -0.040284 | -0.22246 | 4.1149 | 0.047715 | 0.095801 | 3.2345 | 0.068255 | -5.191 | 0.032043 | -23.8998 | -1.4923 | 0.25177 | -118.3365 | -118.4601 | 2.2293 | -0.37537 | -0.086975 | 2.7328 | 2.6642 | -118.3182 | -118.2816 | 0.009155 | -0.11444 | -2.7328 | 118.3777 | 116.8533 | 116.9678 | -8.1757 | 0.027466 | 0.064087 | -0.25177 | 120.575 | 118.2587 | 118.1946 | -0.32043 | 118.5974 | 113.1546 | 94.4458 | -121.4447 | 121.0785 | 121.0098 | 117.9703 | -121.2662
1602.6406 | 121.3486 | -118.4692 | 2.8793 | -0.27114 | 0.032734 | 0.0090179 | 0.36823 | 0.081168 | 0.68087 | -0.038148 | -0.039353 | 4.1246 | 0.045579 | 0.10328 | 3.2399 | 0.074663 | -5.2963 | 0.082397 | -24.1608 | -0.93384 | 0.20599 | -118.4097 | -118.5013 | 2.092 | -0.37537 | -0.11444 | 2.5955 | 2.536 | -118.4418 | -118.3823 | 0.059509 | -0.032044 | -2.6733 | 118.5516 | 117.5354 | 117.5674 | -8.1757 | 0.027466 | 0.086975 | -0.28381 | 120.5612 | 118.3548 | 118.2678 | -0.34332 | 118.6752 | 113.1729 | 94.3085 | -121.3806 | 121.0648 | 121.0052 | 118.0939 | -121.2616
1603.6406 | 121.3074 | -118.4967 | 2.8427 | -0.30166 | 0.018849 | 0.00047294 | 0.37357 | 0.081168 | 0.6798 | -0.040284 | -0.039353 | 4.1171 | 0.034898 | 0.11075 | 3.2388 | 0.071459 | -5.5664 | 0.036621 | -23.7946 | -1.0162 | 0.23804 | -118.4647 | -118.5287 | 2.0691 | -0.41657 | -0.09613 | 2.5635 | 2.5131 | -118.4601 | -118.428 | 0.032043 | -0.032044 | -2.6047 | 118.5333 | 117.4805 | 117.5125 | -8.4091 | 0.036621 | 0.068664 | -0.27924 | 120.5658 | 118.4006 | 118.3319 | -0.32959 | 118.7347 | 112.9303 | 94.7021 | -121.3715 | 121.0602 | 121.0098 | 118.0801 | -121.2708
1604.6406 | 121.431 | -118.3777 | 2.8473 | 0.62913 | 0.0060322 | 0.0015409 | 0.36823 | 0.092917 | 0.6798 | -0.027467 | 1.0745 | 4.1075 | 0.042375 | 0.097938 | 3.2527 | 0.081072 | -5.4108 | 0.12817 | -23.8174 | -1.0895 | 0.18768 | -118.4235 | -118.5242 | 2.1973 | -0.30212 | 0.013733 | 2.536 | 2.4857 | -118.3914 | -118.3594 | -0.045776 | -0.14648 | -2.6596 | 118.5059 | 117.2882 | 117.4347 | -8.2581 | -0.013732 | 0.018311 | -0.31128 | 120.575 | 118.3914 | 118.3731 | -0.36163 | 118.5654 | 112.9669 | 94.5602 | -121.3715 | 120.9137 | 120.8633 | 118.0756 | -121.2067
1605.6406 | 121.3715 | -118.4143 | 2.9205 | 0.44602 | 0.030598 | 0.031448 | 0.37357 | 0.087577 | 0.68942 | -0.032808 | -0.17668 | 4.1075 | 0.051988 | 0.094733 | 3.241 | 0.060778 | -5.4245 | -0.013733 | -24.1425 | -1.2268 | 0.24261 | -118.3777 | -118.4692 | 2.1469 | -0.35706 | -0.064087 | 2.6413 | 2.5955 | -118.3868 | -118.3502 | 0.036621 | -0.054931 | -2.6779 | 118.4006 | 117.1875 | 117.2424 | -8.345 | 0.027466 | 0.064087 | -0.27924 | 120.5612 | 118.3502 | 118.2861 | -0.32501 | 118.6569 | 112.9898 | 94.2719 | -121.3898 | 121.0556 | 121.0098 | 118.0573 | -121.2708
1606.6406 | 121.3623 | -118.2724 | 3.0533 | -0.10329 | 0.055165 | 0.010086 | 0.37784 | 0.08544 | 0.69262 | -0.028535 | -0.16142 | 4.1032 | 0.044511 | 0.092597 | 3.2367 | 0.058642 | -5.7358 | 0 | -24.3576 | -1.4374 | 0.23346 | -118.2358 | -118.364 | 2.2705 | -0.33875 | -0.082397 | 2.7786 | 2.7145 | -118.2495 | -118.2266 | 0.036621 | -0.091553 | -2.8198 | 118.2724 | 116.835 | 116.9266 | -8.7891 | 0.022888 | 0.045776 | -0.27466 | 120.5429 | 118.19 | 118.1442 | -0.33875 | 118.5059 | 112.5366 | 93.9148 | -121.4172 | 121.051 | 120.9869 | 117.9337 | -121.2799
1607.6406 | 121.3898 | -118.3136 | 2.9938 | -0.11855 | 0.037007 | 0.012222 | 0.37677 | 0.092917 | 0.68621 | -0.030671 | -0.22246 | 4.1043 | 0.051988 | 0.10435 | 3.2335 | 0.062914 | -5.452 | 0.009155 | -24.0967 | -1.2772 | 0.2243 | -118.277 | -118.4006 | 2.2476 | -0.32959 | -0.036621 | 2.7328 | 2.6962 | -118.2724 | -118.2358 | 0.036621 | -0.086975 | -2.7695 | 118.3228 | 117.0364 | 117.1234 | -8.4457 | 0.041199 | 0.07782 | -0.26093 | 120.5612 | 118.277 | 118.1992 | -0.29755 | 118.5379 | 112.8616 | 94.2169 | -121.3943 | 121.0464 | 121.0098 | 117.984 | -121.2296
1608.6406 | 121.3806 | -118.3731 | 2.9572 | 0.00352 | 0.059437 | -0.0080721 | 0.37784 | 0.099326 | 0.69155 | -0.030671 | 0.067459 | 4.1053 | 0.047715 | 0.10435 | 3.2431 | 0.069323 | -5.3101 | 0.064087 | -24.1013 | -0.8606 | 0.23804 | -118.3228 | -118.4509 | 2.2247 | -0.36621 | -0.059509 | 2.6596 | 2.623 | -118.309 | -118.3044 | 0.050354 | -0.07782 | -2.7191 | 118.4372 | 117.5125 | 117.5903 | -8.2672 | 0.064087 | 0.068665 | -0.29755 | 120.5978 | 118.3136 | 118.2449 | -0.33417 | 118.6111 | 113.063 | 94.2719 | -121.4081 | 121.0327 | 120.9961 | 118.0069 | -121.2616
1609.6406 | 121.4264 | -118.4738 | 2.7328 | 0.55284 | 0.033803 | 0.014358 | 0.35541 | 0.081168 | 0.67019 | -0.034944 | -0.57341 | 4.1085 | 0.05626 | 0.10007 | 3.2313 | 0.084276 | -5.2551 | -0.19226 | -24.6872 | -0.85602 | 0.15106 | -118.5333 | -118.6249 | 2.0966 | -0.2655 | 0.032043 | 2.4353 | 2.3941 | -118.4692 | -118.4372 | -0.059509 | -0.15106 | -2.5818 | 118.2816 | 117.6178 | 117.7689 | -7.988 | 0.004578 | 0.036621 | -0.29755 | 120.5704 | 118.5059 | 118.4692 | -0.33874 | 118.6249 | 113.2187 | 93.7866 | -121.3577 | 120.9091 | 120.8679 | 118.2083 | -121.17
1610.6406 | 121.3989 | -118.5791 | 2.7237 | -0.17959 | 0.062642 | 0.0015409 | 0.38532 | 0.096122 | 0.70651 | -0.031739 | -0.14616 | 4.1235 | 0.047715 | 0.10114 | 3.2378 | 0.067187 | -5.6946 | 0.022888 | -23.9594 | -1.3184 | 0.22888 | -118.5379 | -118.6661 | 1.9958 | -0.32501 | -0.050354 | 2.4582 | 2.4078 | -118.5379 | -118.5196 | 0.041199 | -0.086975 | -2.4948 | 118.602 | 117.2607 | 117.3477 | -8.4183 | 0.041199 | 0.05951 | -0.2655 | 120.575 | 118.5287 | 118.4692 | -0.31586 | 118.808 | 112.8845 | 94.6198 | -121.3898 | 121.0373 | 120.9869 | 118.2541 | -121.2433
1611.6406 | 121.3531 | -118.4692 | 2.8244 | 0.095073 | 0.041279 | 0.011154 | 0.3725 | 0.09719 | 0.69155 | -0.023195 | 0.22005 | 4.1235 | 0.054124 | 0.08512 | 3.2431 | 0.066119 | -5.5161 | -0.10529 | -23.2452 | -1.474 | 0.25177 | -118.3502 | -118.4967 | 2.0966 | -0.34332 | -0.064087 | 2.5543 | 2.504 | -118.4692 | -118.3914 | 0.11902 | -0.027466 | -2.5726 | 118.364 | 116.9952 | 117.0227 | -8.3405 | 0 | 0.07782 | -0.27008 | 120.5658 | 118.4052 | 118.3273 | -0.32044 | 118.721 | 112.9532 | 95.224 | -121.3211 | 121.0236 | 120.9732 | 118.1259 | -121.2158
1612.6406 | 121.3577 | -118.4967 | 2.8061 | 0.12559 | 0.051961 | -0.0048681 | 0.35755 | 0.088645 | 0.68514 | -0.030671 | 0.34212 | 4.1149 | 0.053056 | 0.10648 | 3.2378 | 0.074663 | -5.5252 | 0.068665 | -23.7076 | -1.767 | 0.29297 | -118.4143 | -118.5471 | 2.0737 | -0.4303 | -0.082397 | 2.5085 | 2.4994 | -118.483 | -118.4418 | 0.082397 | -0.050354 | -2.5131 | 118.5654 | 116.7297 | 116.7801 | -8.3313 | 0.013733 | 0.054932 | -0.29755 | 120.5704 | 118.4143 | 118.3594 | -0.3067 | 118.7897 | 112.9715 | 94.7891 | -121.3531 | 121.0052 | 120.9961 | 118.0664 | -121.2479
1613.6406 | 121.3257 | -118.5013 | 2.7969 | 0.079814 | 0.057301 | 0.0026089 | 0.38104 | 0.090781 | 0.69583 | -0.029603 | 0.18953 | 4.116 | 0.054124 | 0.096869 | 3.2506 | 0.067187 | -5.571 | 0.036621 | -23.4146 | -1.68 | 0.26093 | -118.4784 | -118.5883 | 2.0508 | -0.4303 | -0.059509 | 2.5177 | 2.4673 | -118.4647 | -118.4509 | 0.022888 | -0.086975 | -2.536 | 118.5379 | 116.8213 | 116.9083 | -8.3679 | 0.036621 | 0.050354 | -0.27924 | 120.5521 | 118.4418 | 118.3914 | -0.32959 | 118.7622 | 112.9303 | 95.0867 | -121.3852 | 121.019 | 120.9686 | 118.071 | -121.2479
1614.6406 | 121.312 | -118.4647 | 2.8702 | 0.21714 | 0.065846 | 0.0079499 | 0.38639 | 0.091849 | 0.7001 | -0.026399 | 0.3116 | 4.1171 | 0.053056 | 0.095801 | 3.241 | 0.075732 | -5.6396 | -0.059509 | -23.5382 | -1.9547 | 0.20599 | -118.4006 | -118.5242 | 2.0645 | -0.46234 | -0.073242 | 2.6001 | 2.5452 | -118.4052 | -118.4006 | 0.064087 | -0.059509 | -2.6642 | 118.4052 | 116.51 | 116.5695 | -8.5098 | 0.05951 | 0.064087 | -0.27008 | 120.5292 | 118.3914 | 118.3273 | -0.32501 | 118.6707 | 112.825 | 94.9265 | -121.3943 | 121.0648 | 121.0098 | 118.0023 | -121.2708
1615.6406 | 121.312 | -118.3868 | 2.9297 | 0.32395 | 0.041279 | 0.0036769 | 0.36716 | 0.10039 | 0.69689 | -0.031739 | 0.89143 | 4.1043 | 0.051988 | 0.10114 | 3.2442 | 0.060778 | -5.4337 | -0.027466 | -23.5199 | -1.1261 | 0.21057 | -118.3502 | -118.4509 | 2.1332 | -0.48523 | -0.1236 | 2.6505 | 2.6184 | -118.3502 | -118.2953 | 0.036621 | -0.064087 | -2.7191 | 118.3594 | 117.2607 | 117.3248 | -8.3633 | 0.036621 | 0.091553 | -0.27923 | 120.52 | 118.2632 | 118.1717 | -0.31128 | 118.5974 | 112.9532 | 94.8669 | -121.3806 | 121.0373 | 121.0052 | 117.9016 | -121.225
1616.6406 | 121.3074 | -118.2999 | 3.0121 | 0.15611 | 0.067982 | 0.0015409 | 0.38425 | 0.095053 | 0.68194 | -0.026399 | 0.40315 | 4.0989 | 0.065873 | 0.089393 | 3.2388 | 0.069323 | -5.452 | -0.013733 | -23.5245 | -1.4969 | 0.21515 | -118.2541 | -118.3594 | 2.243 | -0.4715 | -0.054932 | 2.7328 | 2.6825 | -118.2724 | -118.2495 | 0.045777 | -0.059509 | -2.7969 | 118.2861 | 116.803 | 116.8625 | -8.4641 | 0.027466 | 0.050354 | -0.27924 | 120.5429 | 118.2449 | 118.1946 | -0.32959 | 118.515 | 112.8479 | 94.7754 | -121.3715 | 121.0327 | 120.9824 | 117.8284 | -121.2616
1617.6406 | 121.2982 | -118.4052 | 2.916 | 0.59861 | 0.055165 | -0.0080721 | 0.40134 | 0.088645 | 0.68621 | -0.033876 | 0.50996 | 4.1181 | 0.064805 | 0.094733 | 3.241 | 0.081072 | -5.5435 | -0.068665 | -23.6847 | -1.1765 | 0.23346 | -118.364 | -118.4692 | 2.1194 | -0.61798 | -0.050354 | 2.6367 | 2.5864 | -118.3502 | -118.3228 | 0.041198 | -0.064087 | -2.6825 | 118.3365 | 117.2287 | 117.2928 | -8.4595 | 0.054931 | 0.082397 | -0.27924 | 120.5246 | 118.3548 | 118.2724 | -0.32959 | 118.6386 | 112.8616 | 94.7205 | -121.3852 | 121.0419 | 120.9915 | 117.7872 | -121.2387
1618.6406 | 121.312 | -118.2449 | 3.0487 | 0.32395 | 0.06905 | 0.0026089 | 0.396 | 0.090781 | 0.68728 | -0.038148 | 0.58626 | 4.1107 | 0.059465 | 0.10221 | 3.2356 | 0.066119 | -5.5481 | -0.07782 | -23.2178 | -1.9318 | 0.2243 | -118.1992 | -118.2861 | 2.2934 | -0.52185 | 0.009155 | 2.7924 | 2.7695 | -118.2083 | -118.1946 | 0.045776 | -0.041199 | -2.8244 | 118.1671 | 116.3132 | 116.3544 | -8.5968 | 0.036621 | 0.050354 | -0.25635 | 120.5383 | 118.2541 | 118.2037 | -0.27924 | 118.4692 | 112.6968 | 95.0272 | -121.3348 | 121.0373 | 121.0144 | 117.7231 | -121.2433
1619.6406 | 121.3211 | -118.4784 | 2.8702 | 0.3087 | 0.072255 | -0.0038001 | 0.36609 | 0.095053 | 0.68301 | -0.029603 | 0.571 | 4.1085 | 0.058397 | 0.096869 | 3.2463 | 0.066119 | -5.4199 | -0.045776 | -22.9935 | -1.9547 | 0.23804 | -118.3731 | -118.5242 | 2.0828 | -0.46692 | -0.027466 | 2.6001 | 2.5406 | -118.3823 | -118.3731 | 0.10529 | -0.045776 | -2.6321 | 118.4326 | 116.5237 | 116.5695 | -8.2901 | 0.096131 | 0.10529 | -0.27008 | 120.5612 | 118.4509 | 118.3456 | -0.32959 | 118.7164 | 113.0585 | 95.4849 | -121.3943 | 121.0785 | 121.019 | 118.0115 | -121.2433
1620.6406 | 121.225 | -118.3731 | 2.9022 | 0.40025 | 0.054097 | -0.0038001 | 0.36502 | 0.076896 | 0.68728 | -0.031739 | 0.63203 | 4.1064 | 0.055192 | 0.099006 | 3.241 | 0.069323 | -5.3741 | -0.041199 | -22.8378 | -1.4648 | 0.25177 | -118.3731 | -118.4784 | 2.1103 | -0.44861 | -0.036621 | 2.623 | 2.5818 | -118.396 | -118.3548 | 0 | -0.10529 | -2.6505 | 118.3319 | 116.9083 | 117.0135 | -8.2764 | -0.022888 | 0.018311 | -0.27924 | 120.4834 | 118.3365 | 118.3182 | -0.32044 | 118.6249 | 112.999 | 95.5353 | -121.3806 | 120.9961 | 120.9549 | 117.9245 | -121.257
1621.6406 | 121.344 | -118.3594 | 2.9114 | 0.7512 | 0.053029 | 0.011154 | 0.37357 | 0.090781 | 0.67446 | -0.038148 | 0.73885 | 4.1075 | 0.066941 | 0.092597 | 3.2292 | 0.072527 | -5.3696 | -0.018311 | -22.9019 | -1.5839 | 0.23346 | -118.2953 | -118.4189 | 2.1835 | -0.38452 | 0.032043 | 2.6184 | 2.5864 | -118.3319 | -118.2999 | 0.064087 | -0.059509 | -2.6779 | 118.3411 | 116.7755 | 116.835 | -8.2809 | 0.027466 | 0.059509 | -0.29297 | 120.5429 | 118.3914 | 118.3319 | -0.32501 | 118.5928 | 112.9898 | 95.4575 | -121.3303 | 120.9778 | 120.9457 | 117.9749 | -121.2112
1622.6406 | 121.3806 | -118.3914 | 2.8702 | 0.27818 | 0.054097 | 0.0036769 | 0.3725 | 0.084372 | 0.69476 | -0.039216 | 0.78462 | 4.0904 | 0.051988 | 0.11075 | 3.2388 | 0.085345 | -5.5847 | -0.027466 | -23.053 | -1.5518 | 0.21057 | -118.3594 | -118.4372 | 2.1698 | -0.41657 | 0.022888 | 2.5818 | 2.5406 | -118.364 | -118.3182 | 0.032043 | -0.045777 | -2.6596 | 118.364 | 116.8396 | 116.8854 | -8.4549 | 0.027465 | 0.073242 | -0.28839 | 120.5612 | 118.4143 | 118.3411 | -0.32959 | 118.602 | 112.8067 | 95.3384 | -121.3074 | 120.9732 | 120.932 | 117.9749 | -121.1884
1623.6406 | 121.3211 | -118.3914 | 2.9022 | 0.4918 | 0.051961 | 0.0026089 | 0.3757 | 0.084372 | 0.6766 | -0.03708 | -4.3576 | 4.1064 | 0.058397 | 0.10862 | 3.2356 | 0.078936 | -5.6076 | -0.041199 | -23.3231 | -1.8631 | 0.23346 | -118.3182 | -118.4006 | 2.1378 | -0.47607 | -0.045776 | 2.6459 | 2.6047 | -118.3456 | -118.3502 | 0.073242 | -0.009156 | -2.6688 | 118.3502 | 116.5283 | 116.5375 | -8.5098 | 0.045776 | 0.041198 | -0.25635 | 120.5292 | 118.3456 | 118.3044 | -0.29755 | 118.6249 | 112.7838 | 95.0684 | -121.3028 | 121.0373 | 120.9961 | 117.9153 | -121.2524
1624.6406 | 121.4218 | -118.2632 | 2.9617 | 0.56809 | 0.02953 | 0.0079499 | 0.37357 | 0.082236 | 0.68087 | -0.026399 | 0.79988 | 4.1021 | 0.040239 | 0.10648 | 3.2313 | 0.066119 | -5.6396 | 0 | -22.7005 | -2.0966 | 0.21973 | -118.2816 | -118.3182 | 2.298 | -0.39368 | 0.082397 | 2.6825 | 2.6505 | -118.2678 | -118.2083 | -0.01831 | -0.054931 | -2.742 | 118.2632 | 116.1667 | 116.2216 | -8.6014 | -0.004577 | 0.054932 | -0.27924 | 120.5612 | 118.3456 | 118.2907 | -0.31128 | 118.483 | 112.6236 | 95.5627 | -121.2799 | 120.9457 | 120.9137 | 117.8696 | -121.17
1625.6406 | 121.4218 | -118.2678 | 2.9388 | 0.55284 | 0.028462 | -0.010208 | 0.35755 | 0.092917 | 0.67874 | -0.038148 | 0.81514 | 4.0925 | 0.061601 | 0.11396 | 3.242 | 0.0768 | -5.7816 | 0.027466 | -22.7966 | -1.8036 | 0.21973 | -118.2632 | -118.3594 | 2.2705 | -0.32044 | 0.09613 | 2.655 | 2.6321 | -118.2632 | -118.2404 | 0.004577 | -0.091553 | -2.7191 | 118.2953 | 116.4642 | 116.5558 | -8.7204 | 0.004577 | 0.027466 | -0.28381 | 120.5383 | 118.364 | 118.3365 | -0.3067 | 118.4875 | 112.4863 | 95.4712 | -121.2982 | 120.9229 | 120.9 | 117.9474 | -121.1792
1626.6406 | 121.4355 | -118.2861 | 2.9114 | 0.59861 | 0.059437 | 0.0026089 | 0.3693 | 0.079032 | 0.65844 | -0.039216 | 0.73885 | 4.0904 | 0.049852 | 0.10541 | 3.2313 | 0.081072 | -5.7999 | 0.10071 | -22.9935 | -2.0691 | 0.16937 | -118.2129 | -118.3411 | 2.3346 | -0.58594 | -0.068665 | 2.6367 | 2.6047 | -118.3319 | -118.2632 | 0.073242 | -0.054931 | -2.742 | 118.3868 | 116.217 | 116.272 | -8.7112 | -0.045776 | 0.022888 | -0.27466 | 120.6207 | 118.2175 | 118.1946 | -0.3067 | 118.4555 | 112.4863 | 95.2927 | -121.2524 | 120.9229 | 120.8908 | 117.7002 | -121.1746
1627.6406 | 121.431 | -118.4326 | 2.7649 | 0.58335 | 0.042347 | 0.0047449 | 0.35968 | 0.091849 | 0.6798 | -0.036012 | 0.78462 | 4.1064 | 0.045579 | 0.10114 | 3.2345 | 0.070391 | -5.8228 | 0.064087 | -23.1125 | -1.5015 | 0.19226 | -118.4235 | -118.515 | 2.1332 | -0.37079 | 0.064087 | 2.5085 | 2.4582 | -118.4555 | -118.396 | 0.009155 | -0.082398 | -2.5726 | 118.4967 | 116.9312 | 117.0136 | -8.5876 | -0.022888 | 0.036621 | -0.25635 | 120.5658 | 118.4967 | 118.4601 | -0.3067 | 118.6249 | 112.6099 | 95.3201 | -121.2799 | 120.9412 | 120.8908 | 118.0618 | -121.1609
1628.6406 | 121.4172 | -118.428 | 2.7603 | 0.61387 | 0.038075 | 0.0015409 | 0.38104 | 0.08544 | 0.67126 | -0.029603 | -1.0312 | 4.0957 | 0.048783 | 0.10114 | 3.2271 | 0.067187 | -5.7266 | 0.10071 | -22.8058 | -1.7075 | 0.18768 | -118.4601 | -118.5562 | 2.124 | -0.32959 | 0.018311 | 2.4536 | 2.417 | -118.4235 | -118.3914 | -0.032043 | -0.12817 | -2.5726 | 118.5287 | 116.7206 | 116.8488 | -8.4869 | 0.004578 | 0.036622 | -0.3067 | 120.5521 | 118.4464 | 118.4097 | -0.34332 | 118.6157 | 112.7014 | 95.6223 | -121.3165 | 120.8817 | 120.845 | 118.0984 | -121.1517
1629.6406 | 121.431 | -118.4463 | 2.7695 | 0.55284 | 0.042347 | -0.0070041 | 0.36182 | 0.081168 | 0.66912 | -0.032808 | -0.52763 | 4.1064 | 0.05626 | 0.097938 | 3.2271 | 0.071459 | -5.6992 | 0.12817 | -23.5199 | -1.506 | 0.16022 | -118.4738 | -118.5516 | 2.1423 | -0.34332 | 0.054932 | 2.4857 | 2.4261 | -118.4418 | -118.396 | -0.027466 | -0.10529 | -2.6093 | 118.5745 | 116.9403 | 117.0456 | -8.4686 | 0.004578 | 0.050354 | -0.28381 | 120.5887 | 118.5013 | 118.4509 | -0.34332 | 118.6066 | 112.7472 | 94.9265 | -121.3211 | 120.932 | 120.8725 | 118.103 | -121.1655
1630.6406 | 121.431 | -118.3273 | 2.861 | 0.85801 | 0.032734 | -0.023026 | 0.36289 | 0.086509 | 0.68408 | -0.038148 | 0.69307 | 4.0936 | 0.041307 | 0.10435 | 3.2367 | 0.073595 | -5.8411 | 0.086975 | -23.1033 | -1.6113 | 0.19684 | -118.2953 | -118.4006 | 2.2522 | -0.32959 | 0.050354 | 2.5818 | 2.5314 | -118.3456 | -118.2632 | 0.032044 | -0.073242 | -2.6642 | 118.4143 | 116.716 | 116.7892 | -8.7021 | -0.01831 | 0.064087 | -0.27924 | 120.5795 | 118.3777 | 118.3136 | -0.32959 | 118.5242 | 112.4863 | 95.224 | -121.2616 | 120.9091 | 120.8588 | 117.9977 | -121.1243
1631.6875 | 121.4127 | -118.3182 | 2.8702 | 3.0705 | 0.04662 | -0.0016631 | 0.38425 | 0.081168 | 0.6798 | -0.041353 | 0.69307 | 4.0936 | 0.03383 | 0.10435 | 3.226 | 0.069323 | -5.6992 | 0.064087 | -23.1171 | -1.4969 | 0.15106 | -118.3273 | -118.4326 | 2.2385 | -0.37994 | 0.059509 | 2.5681 | 2.5452 | -118.3548 | -118.2953 | -0.009156 | -0.11444 | -2.7191 | 118.3823 | 116.8213 | 116.9357 | -8.5693 | -0.036621 | 0.022888 | -0.30212 | 120.5566 | 118.3777 | 118.3548 | -0.32501 | 118.4692 | 112.619 | 95.2011 | -121.3028 | 120.8862 | 120.8633 | 117.9382 | -121.1655
1632.6406 | 121.3943 | -118.4326 | 2.8107 | 0.47654 | 0.0092362 | 0.0090179 | 0.38104 | 0.076896 | 0.66271 | -0.036012 | 0.571 | 4.0925 | 0.057328 | 0.10328 | 3.2388 | 0.070391 | -5.8594 | 0.07782 | -22.9935 | -1.8082 | 0.21515 | -118.3685 | -118.483 | 2.124 | -0.37079 | 0.041199 | 2.5314 | 2.4811 | -118.3868 | -118.3456 | 0.064087 | -0.050354 | -2.5955 | 118.5104 | 116.6244 | 116.6748 | -8.67 | 0.045776 | 0.086975 | -0.27924 | 120.5566 | 118.4738 | 118.3868 | -0.32959 | 118.6478 | 112.5732 | 95.4391 | -121.2936 | 120.964 | 120.9137 | 118.0618 | -121.1563
1633.6406 | 121.3943 | -118.2037 | 2.9938 | 1.209 | 0.040211 | 0.010086 | 0.35861 | 0.092917 | 0.65951 | -0.042421 | 0.66255 | 4.0925 | 0.053056 | 0.099006 | 3.2335 | 0.072527 | -5.7129 | 0.10986 | -22.998 | -1.7349 | 0.16937 | -118.1717 | -118.2907 | 2.3621 | -0.36621 | 0.059509 | 2.7283 | 2.6505 | -118.1854 | -118.1534 | 0.032043 | -0.086975 | -2.8244 | 118.3136 | 116.4688 | 116.5558 | -8.7067 | 0.01831 | 0.050354 | -0.2655 | 120.5658 | 118.2632 | 118.2129 | -0.34332 | 118.3731 | 112.4908 | 95.2057 | -121.2845 | 120.932 | 120.8542 | 117.8375 | -121.1472
1634.6406 | 121.3989 | -118.3731 | 2.8336 | 0.91905 | 0.010304 | 0.011154 | 0.36075 | 0.082236 | 0.67553 | -0.028535 | 0.60152 | 4.0882 | 0.029557 | 0.10007 | 3.2196 | 0.06505 | -5.8777 | 0.10529 | -23.2819 | -1.9547 | 0.19226 | -118.3411 | -118.4235 | 2.2202 | -0.36163 | 0.036621 | 2.5772 | 2.504 | -118.3685 | -118.3319 | 0.032044 | -0.050354 | -2.6413 | 118.4784 | 116.4185 | 116.4688 | -8.7112 | 0.004578 | 0.041199 | -0.25635 | 120.5933 | 118.4097 | 118.3685 | -0.32959 | 118.5654 | 112.4954 | 95.0912 | -121.257 | 120.9503 | 120.8771 | 118.0115 | -121.1655
1635.6406 | 121.3806 | -118.4052 | 2.8152 | 0.44602 | 0.0017592 | -0.00059506 | 0.35861 | 0.089713 | 0.66485 | -0.043489 | 0.47945 | 4.0968 | 0.027421 | 0.097938 | 3.2292 | 0.063982 | -5.9601 | 0.09613 | -23.1445 | -1.6937 | 0.21057 | -118.4052 | -118.4784 | 2.124 | -0.36163 | -0.009155 | 2.5314 | 2.4765 | -118.396 | -118.3777 | 0 | -0.073243 | -2.6047 | 118.5013 | 116.7114 | 116.7847 | -8.7753 | 0.009155 | 0.027465 | -0.28381 | 120.5292 | 118.396 | 118.3685 | -0.33875 | 118.6157 | 112.4451 | 95.2606 | -121.2936 | 120.9366 | 120.8817 | 118.0435 | -121.1929
1636.6406 | 121.3852 | -118.3136 | 2.9297 | 0.52232 | 0.026326 | 0.016495 | 0.37357 | 0.077964 | 0.68087 | -0.038148 | 0.69307 | 4.0893 | 0.041307 | 0.091529 | 3.2239 | 0.068255 | -5.8685 | 0.11444 | -23.0255 | -1.2085 | 0.2243 | -118.2861 | -118.3685 | 2.2614 | -0.38452 | -0.013733 | 2.6413 | 2.5635 | -118.2953 | -118.2724 | 0.027466 | -0.054931 | -2.7054 | 118.428 | 117.1051 | 117.16 | -8.7982 | 0.018311 | 0.041199 | -0.28839 | 120.575 | 118.2999 | 118.2587 | -0.36621 | 118.5379 | 112.4451 | 95.2881 | -121.2982 | 120.9549 | 120.8771 | 117.9291 | -121.2021
1637.6875 | 121.4172 | -118.428 | 2.7557 | 0.62913 | 0.032734 | -0.0048681 | 0.37677 | 0.091849 | 0.68835 | -0.030671 | 0.52522 | 4.0914 | 0.048783 | 0.099006 | 3.2388 | 0.062914 | -5.9143 | 0.07782 | -23.0759 | -2.2705 | 0.19684 | -118.4052 | -118.5104 | 2.1561 | -0.36163 | 0.050354 | 2.4765 | 2.4078 | -118.4555 | -118.396 | 0.022889 | -0.082397 | -2.5589 | 118.5059 | 116.1575 | 116.2399 | -8.67 | -0.027465 | 0.032044 | -0.27924 | 120.5841 | 118.4784 | 118.4463 | -0.3479 | 118.6249 | 112.5137 | 95.3522 | -121.2662 | 120.9045 | 120.8359 | 118.0664 | -121.1517
1638.6406 | 121.3806 | -118.4875 | 2.7512 | 0.36973 | -0.0046498 | 0.014358 | 0.36182 | 0.096122 | 0.65524 | -0.043489 | 0.46419 | 4.0893 | 0.025285 | 0.10114 | 3.2313 | 0.0768 | -5.9372 | 0.07782 | -23.3826 | -2.0737 | 0.19226 | -118.428 | -118.5471 | 2.0508 | -0.39368 | 0.054932 | 2.4536 | 2.417 | -118.4738 | -118.4189 | 0.059509 | -0.059509 | -2.5589 | 118.5654 | 116.4139 | 116.4734 | -8.6884 | 0.013733 | 0.068665 | -0.29755 | 120.5383 | 118.5425 | 118.4738 | -0.33417 | 118.6798 | 112.5504 | 95.105 | -121.2982 | 120.9412 | 120.9045 | 118.0939 | -121.17
1639.6406 | 121.4127 | -118.4418 | 2.7237 | 0.11033 | 0.016713 | 0.0015409 | 0.37357 | 0.073691 | 0.6531 | -0.031739 | 0.15901 | 4.0872 | 0.038102 | 0.099006 | 3.2356 | 0.067187 | -5.864 | 0.13733 | -23.735 | -2.3529 | 0.2243 | -118.4143 | -118.515 | 2.1378 | -0.31586 | 0.14191 | 2.4811 | 2.4261 | -118.4235 | -118.4006 | 0.027465 | -0.073243 | -2.4994 | 118.5791 | 116.0889 | 116.1621 | -8.5876 | 0.01831 | 0.041198 | -0.24262 | 120.5795 | 118.5837 | 118.5425 | -0.29755 | 118.6661 | 112.5778 | 94.7067 | -121.2387 | 120.9229 | 120.8679 | 118.1259 | -121.1243
1640.6406 | 121.3074 | -118.5699 | 2.6459 | 0.26292 | 0.013508 | 0.0079499 | 0.3693 | 0.088645 | 0.66699 | -0.049897 | 0.38789 | 4.0968 | 0.03917 | 0.082984 | 3.2271 | 0.071459 | -6.3309 | 0.073242 | -23.465 | -1.7349 | 0.19684 | -118.4601 | -118.5883 | 2.037 | -0.40283 | -0.004578 | 2.4399 | 2.3987 | -118.5745 | -118.5745 | 0.10986 | -0.018311 | -2.449 | 118.6432 | 116.835 | 116.8533 | -8.9767 | -0.004578 | -0.004578 | -0.20599 | 120.607 | 118.5654 | 118.5699 | -0.24719 | 118.7668 | 112.2391 | 95.105 | -121.2341 | 121.0098 | 120.9686 | 118.1671 | -121.2204
1641.6406 | 121.3531 | -118.4921 | 2.7008 | 0.26292 | 0.016713 | 0.0068819 | 0.37784 | 0.093985 | 0.66592 | -0.043489 | 0.37263 | 4.0904 | 0.032762 | 0.10328 | 3.2303 | 0.070391 | -6.2302 | 0.054932 | -22.8424 | -1.7487 | 0.23804 | -118.4463 | -118.5562 | 1.9089 | -0.49896 | -0.022888 | 2.3941 | 2.3483 | -118.483 | -118.4601 | 0.045776 | -0.064087 | -2.4628 | 118.5471 | 116.7435 | 116.8076 | -8.931 | 0.009155 | 0.032043 | -0.3067 | 120.401 | 118.4692 | 118.4372 | -0.35248 | 118.7302 | 112.262 | 95.6497 | -121.257 | 120.8862 | 120.8405 | 117.9932 | -121.1609
1642.6406 | 121.4127 | -118.4052 | 2.8015 | 0.00352 | 0.013508 | 0.021835 | 0.36609 | 0.083304 | 0.66699 | -0.043489 | 0.18953 | 4.0914 | 0.044511 | 0.096869 | 3.2207 | 0.070391 | -6.1569 | 0.1236 | -23.1354 | -1.8173 | 0.23346 | -118.4052 | -118.4875 | 2.1835 | -0.31586 | 0.050354 | 2.5269 | 2.449 | -118.396 | -118.3685 | 0 | -0.082398 | -2.5681 | 118.5287 | 116.5878 | 116.6702 | -8.9584 | 0.009155 | 0.036621 | -0.27466 | 120.5887 | 118.4555 | 118.4189 | -0.35248 | 118.6386 | 112.2482 | 95.2698 | -121.2891 | 120.932 | 120.8542 | 118.0893 | -121.17
1643.6406 | 121.4127 | -118.4921 | 2.7512 | 0.15611 | 0.0028272 | 0.0047449 | 0.36395 | 0.075827 | 0.67233 | -0.030671 | 0.50996 | 4.0936 | 0.035966 | 0.10007 | 3.2271 | 0.06505 | -6.4453 | -0.064087 | -23.6481 | -1.7441 | 0.14648 | -118.515 | -118.602 | 2.0737 | -0.36621 | 0.086975 | 2.4399 | 2.3987 | -118.483 | -118.428 | -0.022889 | -0.10986 | -2.6047 | 118.428 | 116.748 | 116.8579 | -9.1965 | 0.009155 | 0.064086 | -0.31128 | 120.5658 | 118.5791 | 118.515 | -0.35248 | 118.6386 | 112.0468 | 94.8441 | -121.3531 | 120.932 | 120.8908 | 118.1259 | -121.1792
1644.6406 | 121.4218 | -118.2861 | 2.916 | 0.21714 | 0.011372 | 0.012222 | 0.38104 | 0.087577 | 0.66165 | -0.033876 | 0.26582 | 4.0925 | 0.038102 | 0.074439 | 3.2207 | 0.066119 | -6.0333 | 0.14191 | -23.3414 | -2.005 | 0.21973 | -118.2358 | -118.3868 | 2.3117 | -0.39368 | 0.16479 | 2.655 | 2.5864 | -118.2632 | -118.2495 | 0.050354 | -0.10071 | -2.6962 | 118.428 | 116.2811 | 116.3818 | -8.9493 | 0.022888 | 0.036621 | -0.26093 | 120.5978 | 118.4509 | 118.4143 | -0.32959 | 118.5059 | 112.2528 | 94.9448 | -121.3028 | 120.9412 | 120.8725 | 117.8925 | -121.1655
1645.6406 | 121.4218 | -118.4097 | 2.7649 | 0.064555 | 0.0092362 | 0.010086 | 0.36395 | 0.088645 | 0.65844 | -0.034944 | -0.22246 | 4.0818 | 0.032762 | 0.10328 | 3.2335 | 0.062914 | -6.1249 | 0.15564 | -23.4833 | -1.9226 | 0.21973 | -118.3731 | -118.5104 | 2.1835 | -0.31128 | 0.21057 | 2.4811 | 2.4307 | -118.4006 | -118.3823 | 0.036621 | -0.10071 | -2.5452 | 118.5654 | 116.4871 | 116.5878 | -8.8898 | 0.009155 | 0.027466 | -0.28381 | 120.5933 | 118.6203 | 118.5928 | -0.33417 | 118.6295 | 112.2849 | 94.9265 | -121.2753 | 120.8908 | 120.8405 | 118.0984 | -121.1472
1646.6406 | 121.431 | -118.428 | 2.7512 | -0.011739 | 0.0060322 | 0.010086 | 0.36823 | 0.074759 | 0.65737 | -0.027467 | 0.021682 | 4.0786 | 0.029557 | 0.094733 | 3.2324 | 0.067187 | -6.1478 | 0.19226 | -23.2635 | -1.8906 | 0.20599 | -118.4326 | -118.5059 | 2.1744 | -0.32044 | 0.18768 | 2.4719 | 2.4216 | -118.4509 | -118.3914 | -0.004577 | -0.077819 | -2.5452 | 118.6203 | 116.5375 | 116.6153 | -8.8989 | -0.022888 | 0.036622 | -0.27924 | 120.6024 | 118.6157 | 118.5791 | -0.32959 | 118.634 | 112.2803 | 95.1645 | -121.257 | 120.9 | 120.8496 | 118.1076 | -121.1426
1647.6406 | 121.4447 | -118.5104 | 2.6642 | -0.10329 | 0.013508 | 0.0015409 | 0.38211 | 0.083304 | 0.67874 | -0.029603 | 0.0064239 | 4.0914 | 0.041307 | 0.10648 | 3.2345 | 0.061846 | -6.189 | 0.19684 | -23.4467 | -1.9318 | 0.18768 | -118.5013 | -118.6249 | 2.0554 | -0.3479 | 0.11444 | 2.3895 | 2.33 | -118.5516 | -118.4875 | 0.009155 | -0.11444 | -2.4765 | 118.7073 | 116.5787 | 116.6931 | -8.8531 | -0.041199 | 0.022888 | -0.27466 | 120.5658 | 118.6249 | 118.602 | -0.33417 | 118.6981 | 112.3215 | 95.0638 | -121.2891 | 120.9 | 120.8405 | 118.1625 | -121.1517
1648.6406 | 121.4172 | -118.6111 | 2.6001 | -0.11855 | -0.0099898 | 0.0068819 | 0.37143 | 0.079032 | 0.66271 | -0.039216 | -0.054612 | 4.0936 | 0.043443 | 0.08512 | 3.2356 | 0.06505 | -6.1615 | 0.17853 | -23.2956 | -1.918 | 0.1831 | -118.5654 | -118.6707 | 1.9867 | -0.31586 | 0.09613 | 2.3071 | 2.2568 | -118.5745 | -118.5516 | 0.045776 | -0.059509 | -2.417 | 118.7897 | 116.6931 | 116.7526 | -8.7616 | 0.036621 | 0.059509 | -0.29297 | 120.5978 | 118.7073 | 118.6478 | -0.34332 | 118.7942 | 112.4496 | 95.3156 | -121.2708 | 120.9183 | 120.8679 | 118.2953 | -121.1517
1649.6875 | 121.431 | -118.5059 | 2.6733 | 0.00352 | 0.020985 | 0.017563 | 0.37143 | 0.074759 | 0.6563 | -0.036012 | 0.22005 | 4.0882 | 0.043443 | 0.084052 | 3.2388 | 0.071459 | -6.0516 | 0.14191 | -22.8882 | -1.3824 | 0.21515 | -118.4967 | -118.6066 | 2.0828 | -0.33417 | 0.19684 | 2.4216 | 2.3483 | -118.5013 | -118.4784 | 0.009155 | -0.10071 | -2.4582 | 118.6478 | 117.1234 | 117.2241 | -8.725 | 0.004577 | 0.027465 | -0.25177 | 120.5887 | 118.7027 | 118.6752 | -0.32501 | 118.721 | 112.4542 | 95.6177 | -121.2799 | 120.9274 | 120.8542 | 118.1717 | -121.1517
1650.6406 | 121.4355 | -118.4967 | 2.6733 | -0.22536 | 0.022053 | 0.0068819 | 0.37143 | 0.093985 | 0.66699 | -0.031739 | -0.085129 | 4.085 | 0.032762 | 0.078712 | 3.2164 | 0.06505 | -6.0013 | 0.16937 | -23.0072 | -1.6937 | 0.20599 | -118.4921 | -118.602 | 2.1103 | -0.65002 | 0.11444 | 2.3804 | 2.3529 | -118.5013 | -118.4555 | 0.004578 | -0.10529 | -2.4673 | 118.6661 | 116.803 | 116.9083 | -8.6746 | -0.004578 | 0.041199 | -0.29297 | 120.607 | 118.6111 | 118.5699 | -0.32044 | 118.7027 | 112.4954 | 95.4895 | -121.2753 | 120.8771 | 120.8496 | 117.8467 | -121.1288
1651.6406 | 121.4081 | -118.5242 | 2.6688 | -0.14907 | 0.020985 | 0.021835 | 0.36502 | 0.082236 | 0.66699 | -0.03708 | 5.286 | 4.0829 | 0.027421 | 0.089393 | 3.2474 | 0.063982 | -6.0471 | 0.15106 | -22.7829 | -1.4328 | 0.18768 | -118.5013 | -118.6707 | 2.0416 | -0.32044 | 0.13275 | 2.3758 | 2.3254 | -118.5196 | -118.4601 | 0.022888 | -0.14648 | -2.4811 | 118.6752 | 117.0914 | 117.2379 | -8.7158 | 0.004578 | 0.064087 | -0.29297 | 120.5658 | 118.6569 | 118.5928 | -0.34332 | 118.7119 | 112.4771 | 95.7413 | -121.3394 | 120.9 | 120.8496 | 118.2037 | -121.1288
1652.6406 | 121.3303 | -118.5974 | 2.6733 | -0.24062 | 0.030598 | 0.010086 | 0.37677 | 0.079032 | 0.67339 | -0.039216 | -0.2072 | 4.1 | 0.032762 | 0.090461 | 3.2303 | 0.060778 | -5.8136 | 0.10071 | -22.4396 | -1.5289 | 0.21973 | -118.5379 | -118.6523 | 1.9547 | -0.39825 | 0.059509 | 2.417 | 2.3666 | -118.5745 | -118.5196 | 0.059509 | -0.054932 | -2.4536 | 118.6981 | 117.0685 | 117.1234 | -8.4869 | 0.022888 | 0.07782 | -0.25635 | 120.5521 | 118.6569 | 118.5791 | -0.3067 | 118.8171 | 112.7838 | 96.1578 | -121.3257 | 121.0144 | 120.9641 | 118.1992 | -121.1929
1653.6406 | 121.2799 | -118.5562 | 2.6825 | -0.27114 | 0.013508 | 0.0015409 | 0.36609 | 0.08544 | 0.6766 | -0.038148 | -0.29875 | 4.0925 | 0.044511 | 0.092597 | 3.2249 | 0.060778 | -5.9326 | 0.09613 | -22.6547 | -1.6891 | 0.2243 | -118.5104 | -118.6203 | 1.9547 | -0.46234 | 0.022888 | 2.4033 | 2.3666 | -118.5471 | -118.5196 | 0.045776 | -0.064087 | -2.4582 | 118.6523 | 116.8671 | 116.9312 | -8.6151 | 0.009155 | 0.036621 | -0.27924 | 120.5109 | 118.5791 | 118.5425 | -0.31586 | 118.7805 | 112.6236 | 95.9015 | -121.3028 | 120.9595 | 120.9229 | 118.0939 | -121.2021
1654.6406 | 121.2708 | -118.5287 | 2.7328 | -0.27114 | 0.017781 | 0.0058129 | 0.36823 | 0.082236 | 0.67126 | -0.040284 | -0.024094 | 4.0904 | 0.040239 | 0.089393 | 3.2324 | 0.056505 | -5.7907 | 0.073242 | -22.6318 | -2.0691 | 0.21973 | -118.483 | -118.6157 | 1.9913 | -0.41657 | 0.032043 | 2.4445 | 2.3987 | -118.5333 | -118.4875 | 0.045777 | -0.086975 | -2.5131 | 118.602 | 116.4597 | 116.5466 | -8.5236 | -0.004577 | 0.041199 | -0.28839 | 120.52 | 118.5608 | 118.5196 | -0.33417 | 118.7485 | 112.738 | 95.8969 | -121.3486 | 120.9732 | 120.9274 | 118.1122 | -121.2204
1655.6406 | 121.2799 | -118.5791 | 2.6871 | -0.25588 | 0.0081682 | 0.0090179 | 0.3757 | 0.088645 | 0.67339 | -0.026399 | -0.19194 | 4.0936 | 0.031694 | 0.082984 | 3.2303 | 0.054369 | -5.7312 | 0.050354 | -22.6501 | -2.1194 | 0.22888 | -118.515 | -118.6066 | 1.9363 | -0.44861 | 0.19226 | 2.4445 | 2.3666 | -118.5837 | -118.5333 | 0.064087 | -0.027465 | -2.4582 | 118.6295 | 116.4597 | 116.4871 | -8.4183 | -0.004577 | 0.045777 | -0.24261 | 120.5154 | 118.7714 | 118.7256 | -0.32043 | 118.808 | 112.8479 | 95.929 | -121.2936 | 121.0236 | 120.9457 | 118.1305 | -121.2204
1656.6406 | 121.2982 | -118.6066 | 2.6642 | -0.25588 | 0.031666 | 0.01329 | 0.37464 | 0.091849 | 0.67233 | -0.041353 | -1.0922 | 4.0936 | 0.054124 | 0.095801 | 3.2335 | 0.062914 | -6.2119 | 0.022888 | -22.9477 | -2.2614 | 0.26093 | -118.515 | -118.5974 | 1.9272 | -0.46692 | 0.12817 | 2.4399 | 2.3621 | -118.602 | -118.5562 | 0.091552 | 0.009155 | -2.4033 | 118.6295 | 116.3452 | 116.3361 | -8.876 | 0.004577 | 0.050354 | -0.2243 | 120.5338 | 118.7347 | 118.6844 | -0.30212 | 118.8675 | 112.3947 | 95.6589 | -121.2616 | 121.0464 | 120.9686 | 118.1396 | -121.2204
1657.6406 | 121.2708 | -118.634 | 2.6321 | -0.31691 | 0.026326 | 0.011154 | 0.3725 | 0.08544 | 0.66592 | -0.040284 | -0.14616 | 4.0989 | 0.042375 | 0.10541 | 3.2345 | 0.073595 | -6.1295 | 0.027466 | -23.2498 | -1.68 | 0.25177 | -118.6157 | -118.721 | 1.8539 | -0.39368 | 0.10986 | 2.3712 | 2.3026 | -118.6432 | -118.5974 | 0.01831 | -0.086975 | -2.3804 | 118.6615 | 116.954 | 117.041 | -8.7616 | -0.009155 | 0.036621 | -0.26092 | 120.488 | 118.7439 | 118.7073 | -0.32959 | 118.8858 | 112.5046 | 95.3842 | -121.3531 | 121.0052 | 120.9366 | 118.2404 | -121.2296
1658.6406 | 121.2936 | -118.6707 | 2.6138 | -0.31691 | 0.027394 | 0.0026089 | 0.36395 | 0.073691 | 0.67874 | -0.034944 | -0.11565 | 4.0925 | 0.046647 | 0.095801 | 3.2356 | 0.067187 | -6.0287 | 0.022888 | -22.7737 | -1.6251 | 0.23804 | -118.6478 | -118.7714 | 1.8219 | -0.39825 | 0.07782 | 2.3163 | 2.2842 | -118.6386 | -118.6249 | 0.022888 | -0.10071 | -2.3758 | 118.6935 | 117.0456 | 117.1463 | -8.6426 | 0.032043 | 0.045776 | -0.29755 | 120.4926 | 118.7485 | 118.7027 | -0.32959 | 118.9087 | 112.6419 | 95.8969 | -121.3852 | 120.9869 | 120.9549 | 118.2724 | -121.2387
1659.6406 | 121.3074 | -118.4235 | 2.8885 | 3.1316 | 0.025258 | 0.015426 | 0.36609 | 0.081168 | 0.68194 | -0.041353 | -0.085129 | 4.1011 | 0.040239 | 0.097938 | 3.2463 | 0.057574 | -6.308 | -0.009155 | -22.8653 | -1.5427 | 0.27008 | -118.3731 | -118.5013 | 2.0966 | -0.4715 | 0.20142 | 2.5955 | 2.5497 | -118.3914 | -118.3594 | 0.050354 | -0.07782 | -2.6184 | 118.4143 | 116.8808 | 116.9586 | -9.1965 | 0.032044 | 0.064087 | -0.29297 | 120.52 | 118.6249 | 118.5608 | -0.33874 | 118.6935 | 112.1155 | 95.5582 | -121.3898 | 121.019 | 120.9732 | 117.952 | -121.2479
1660.6406 | 121.3028 | -118.5059 | 2.7786 | 1.209 | 0.039143 | 0.0068819 | 0.37143 | 0.09719 | 0.67874 | -0.033876 | -0.14616 | 4.0925 | 0.038102 | 0.10007 | 3.2399 | 0.070391 | -6.6467 | 0 | -22.5998 | -1.5656 | 0.24719 | -118.4692 | -118.5654 | 2.0096 | -0.41199 | 0.1831 | 2.4948 | 2.4399 | -118.4784 | -118.4647 | 0.036621 | -0.05951 | -2.5314 | 118.5059 | 116.9403 | 116.9998 | -9.4254 | 0.027465 | 0.041198 | -0.28381 | 120.5154 | 118.689 | 118.6478 | -0.33874 | 118.7531 | 111.8591 | 95.9061 | -121.344 | 121.0007 | 120.9457 | 118.0939 | -121.2433
1661.6406 | 121.3211 | -118.5928 | 2.6917 | 0.3087 | 0.04662 | 0.00047294 | 0.37036 | 0.091849 | 0.6766 | -0.033876 | -0.10039 | 4.1053 | 0.057328 | 0.08512 | 3.2324 | 0.068255 | -6.4545 | 0.004578 | -23.1262 | -1.6342 | 0.24261 | -118.5379 | -118.6661 | 1.9226 | -0.40741 | 0.20599 | 2.4124 | 2.3529 | -118.5608 | -118.5425 | 0.054931 | -0.073243 | -2.449 | 118.5974 | 116.9586 | 117.0319 | -9.1461 | 0.032043 | 0.050354 | -0.27923 | 120.5154 | 118.7988 | 118.7485 | -0.33875 | 118.8354 | 112.1384 | 95.4666 | -121.3577 | 121.0052 | 120.9457 | 118.1854 | -121.2341
1662.6406 | 121.2845 | -118.5883 | 2.7008 | -0.19484 | 0.049824 | 0.00047294 | 0.35968 | 0.065146 | 0.6766 | -0.040284 | -0.039353 | 4.0989 | 0.054124 | 0.11289 | 3.2378 | 0.066119 | -6.0837 | 0 | -22.8607 | -1.9135 | 0.22888 | -118.5333 | -118.6523 | 1.9363 | -0.44403 | 0.13275 | 2.417 | 2.3712 | -118.6066 | -118.515 | 0.054932 | -0.064087 | -2.4719 | 118.5883 | 116.6748 | 116.7389 | -8.7845 | -0.01831 | 0.073242 | -0.28381 | 120.5246 | 118.721 | 118.6478 | -0.32959 | 118.8171 | 112.5046 | 95.7275 | -121.3531 | 121.0052 | 120.9595 | 118.1442 | -121.2158
1663.6406 | 121.3074 | -118.4967 | 2.742 | -0.088033 | 0.04662 | -0.012345 | 0.37677 | 0.077964 | 0.68194 | -0.025331 | -0.085129 | 4.084 | 0.05626 | 0.091529 | 3.2345 | 0.066119 | -6.2622 | 0.032043 | -23.1628 | -2.3209 | 0.2243 | -118.5013 | -118.6111 | 2.0325 | -0.37079 | 0.21973 | 2.4536 | 2.417 | -118.4875 | -118.4692 | -0.004578 | -0.11444 | -2.5177 | 118.5287 | 116.1758 | 116.2903 | -9.0042 | 0.009155 | 0.027466 | -0.28839 | 120.5292 | 118.7164 | 118.689 | -0.32501 | 118.721 | 112.2345 | 95.3339 | -121.3531 | 120.9503 | 120.9137 | 118.1259 | -121.2112
1664.6406 | 121.3303 | -118.4052 | 2.8473 | -0.16433 | 0.042347 | -0.0048681 | 0.37677 | 0.090781 | 0.6798 | -0.026399 | 0.036941 | 4.0957 | 0.053056 | 0.10007 | 3.2345 | 0.062914 | -6.3675 | 0.059509 | -23.3093 | -2.3849 | 0.23804 | -118.364 | -118.4921 | 2.1194 | -0.37994 | 0.27466 | 2.5635 | 2.5497 | -118.4143 | -118.3365 | 0.041198 | -0.086975 | -2.6093 | 118.4647 | 116.0202 | 116.1072 | -9.2148 | -0.009156 | 0.068664 | -0.28381 | 120.5246 | 118.6798 | 118.6111 | -0.29755 | 118.6432 | 112.0377 | 95.0958 | -121.3394 | 120.9686 | 120.9549 | 118.0252 | -121.1838
1665.6406 | 121.3211 | -117.8696 | 3.4012 | -0.25588 | 0.053029 | -0.0059361 | 0.37891 | 0.087577 | 0.6798 | -0.021058 | -0.10039 | 4.0701 | 0.042375 | 0.095801 | 3.2185 | 0.070391 | -6.1935 | 0.009155 | -23.4146 | -1.8814 | 0.23346 | -117.8513 | -117.9657 | 2.6321 | -0.42572 | 0.31586 | 3.1219 | 3.067 | -117.8604 | -117.8284 | 0.018311 | -0.09613 | -3.1677 | 117.8787 | 115.9882 | 116.0843 | -9.5947 | 0.009155 | 0.041199 | -0.27924 | 120.5017 | 118.1854 | 118.1442 | -0.33417 | 118.103 | 111.676 | 94.455 | -121.3669 | 120.9915 | 120.9366 | 117.4438 | -121.2296
1666.6406 | 121.312 | -118.0664 | 3.1769 | -0.16433 | 0.051961 | -0.0016631 | 0.37891 | 0.090781 | 0.68087 | -0.022126 | 0.097976 | 4.0818 | 0.044511 | 0.093665 | 3.2249 | 0.066119 | -6.4316 | 0.050354 | -23.7076 | -2.2339 | 0.22888 | -118.0252 | -118.1488 | 2.4353 | -0.38452 | 0.31128 | 2.8931 | 2.8336 | -118.0618 | -118.0298 | 0.041198 | -0.082398 | -2.948 | 118.1168 | 115.8325 | 115.9149 | -9.6085 | 0.004577 | 0.036621 | -0.28381 | 120.5017 | 118.3777 | 118.3411 | -0.34332 | 118.2953 | 111.6348 | 94.3588 | -121.3257 | 120.9595 | 120.9 | 117.6819 | -121.2067
1667.6406 | 121.3165 | -118.103 | 3.1311 | 0.018779 | 0.055165 | 0.015426 | 0.3725 | 0.096122 | 0.66699 | -0.032808 | 0.036941 | 4.0882 | 0.051988 | 0.10328 | 3.2207 | 0.05971 | -6.7612 | 0.041199 | -23.7717 | -1.5381 | 0.2243 | -118.0618 | -118.1946 | 2.4353 | -0.39825 | 0.33417 | 2.8656 | 2.8381 | -118.0984 | -118.0481 | 0.041198 | -0.091553 | -2.9068 | 118.1442 | 116.5649 | 116.6565 | -9.8923 | 0.004577 | 0.054931 | -0.2655 | 120.5383 | 118.4372 | 118.3823 | -0.29297 | 118.3273 | 111.3419 | 94.3314 | -121.3257 | 120.9686 | 120.9412 | 117.7048 | -121.1792
1668.6406 | 121.312 | -118.2678 | 2.9617 | 0.12559 | 0.051961 | -0.0016631 | 0.36823 | 0.10253 | 0.68194 | -0.029603 | 0.17427 | 4.0893 | 0.044511 | 0.10221 | 3.2345 | 0.061846 | -6.9717 | 0.041199 | -23.6664 | -1.442 | 0.23804 | -118.2266 | -118.3594 | 2.2385 | -0.35706 | 0.31128 | 2.6917 | 2.6642 | -118.2632 | -118.2129 | 0.041198 | -0.091553 | -2.7237 | 118.309 | 116.8259 | 116.9174 | -9.9335 | 0.004577 | 0.054931 | -0.27008 | 120.5063 | 118.5791 | 118.5242 | -0.29755 | 118.5059 | 111.2961 | 94.6014 | -121.3211 | 120.9595 | 120.932 | 117.9108 | -121.1746
1669.6406 | 121.3394 | -118.0252 | 3.1769 | -0.026997 | 0.062642 | 0.0058129 | 0.38959 | 0.087577 | 0.67874 | -0.033876 | 0.15901 | 4.0904 | 0.034898 | 0.088325 | 3.2249 | 0.073595 | -6.9717 | 0.054932 | -23.3093 | -1.4603 | 0.2243 | -118.0984 | -118.2266 | 2.4124 | -0.40283 | 0.38452 | 2.8336 | 2.8244 | -118.1122 | -117.984 | -0.073242 | -0.20142 | -2.9526 | 118.0801 | 116.5649 | 116.7664 | -10.1486 | -0.086975 | 0.041199 | -0.34332 | 120.4376 | 118.4097 | 118.3685 | -0.35248 | 118.2495 | 111.0535 | 94.7159 | -121.4035 | 120.8588 | 120.8496 | 117.6224 | -121.1609
1670.6406 | 121.3028 | -118.2175 | 3.035 | 0.079814 | 0.054097 | 0.0047449 | 0.38211 | 0.081168 | 0.68194 | -0.034944 | 0.44893 | 4.085 | 0.046647 | 0.095801 | 3.2378 | 0.074663 | -6.6238 | 0.009155 | -23.172 | -1.5701 | 0.21515 | -118.1808 | -118.3136 | 2.298 | -0.45319 | 0.29297 | 2.7695 | 2.7374 | -118.1946 | -118.1808 | 0.036621 | -0.096131 | -2.8198 | 118.2266 | 116.6473 | 116.7435 | -9.6588 | 0.022888 | 0.036621 | -0.2655 | 120.5154 | 118.5104 | 118.4738 | -0.29755 | 118.4326 | 111.5936 | 95.0455 | -121.3486 | 120.9869 | 120.9549 | 117.7643 | -121.2158
1671.6406 | 121.3257 | -118.1351 | 3.1036 | -0.011739 | 0.062642 | 0.0079499 | 0.37891 | 0.081168 | 0.6766 | -0.032808 | 0.28108 | 4.0914 | 0.035966 | 0.091529 | 3.2281 | 0.061846 | -6.5964 | 0.032043 | -23.3002 | -1.7349 | 0.21515 | -118.1122 | -118.2404 | 2.417 | -0.4303 | 0.43488 | 2.861 | 2.8336 | -118.1351 | -118.103 | 0.022888 | -0.10529 | -2.8885 | 118.1671 | 116.4001 | 116.5054 | -9.7 | 0 | 0.032044 | -0.24262 | 120.5521 | 118.5699 | 118.5379 | -0.27008 | 118.3502 | 111.5387 | 94.8349 | -121.344 | 120.9961 | 120.9686 | 117.7048 | -121.2067
1672.6406 | 121.3165 | -100.3922 | 20.8099 | 0.064555 | 0.0081682 | -0.1042 | 0.25928 | 0.070487 | 0.58581 | -0.023195 | -1.7941 | 3.9366 | 0.10005 | 0.12678 | 3.2078 | 0.12807 | -5.3833 | 0.064087 | -19.4595 | -1.2772 | 0.54016 | -100.4562 | -100.4059 | 20.2835 | 0.14191 | 18.2419 | 20.6314 | 20.5627 | -100.5203 | -100.4196 | -0.064087 | -0.013733 | -20.2698 | 100.4562 | 99.115 | 99.1287 | -26.1932 | -0.12817 | -0.027466 | -0.17853 | 120.6757 | 118.634 | 118.6615 | -0.24719 | 100.9323 | 95.0088 | 80.9326 | -121.2158 | 121.0236 | 120.9549 | 100.5341 | -121.2296
1673.6406 | 121.2982 | -93.8828 | 27.3788 | 0.27818 | 0.018849 | -0.027298 | 0.31055 | 0.050193 | 0.54202 | -0.022126 | -0.40556 | 3.9067 | 0.096849 | 0.092597 | 3.226 | 0.080004 | -5.9143 | 0.018311 | -18.4021 | -1.4191 | 0.35248 | -93.8965 | -94.0063 | 26.7746 | -0.11444 | 24.8932 | 27.1545 | 27.0767 | -93.8965 | -93.8644 | -0.013733 | -0.1236 | -27.0264 | 93.9011 | 92.4637 | 92.5873 | -33.2932 | -0.013733 | 0.01831 | -0.2243 | 120.6573 | 118.7759 | 118.7576 | -0.30212 | 94.2352 | 87.9684 | 75.4807 | -121.3852 | 121.0373 | 120.9595 | 93.7683 | -121.2433
1674.6406 | 121.2936 | -96.1899 | 25.058 | 0.33921 | 0.022053 | -0.097794 | 0.31696 | 0.066214 | 0.54843 | -0.026399 | 0.067459 | 3.9323 | 0.041307 | 0.090461 | 3.2271 | 0.080004 | -6.221 | 0 | -18.8004 | -1.7944 | 0.21057 | -96.1945 | -96.3318 | 24.4263 | -0.1831 | 22.4991 | 24.8062 | 24.765 | -96.167 | -96.199 | -0.004578 | -0.14191 | -24.8474 | 96.1899 | 94.3954 | 94.5374 | -31.279 | 0.022888 | -0.009156 | -0.25177 | 120.6162 | 118.689 | 118.6981 | -0.29297 | 96.4005 | 89.9689 | 77.3895 | -121.3898 | 120.9961 | 120.9549 | 96.0068 | -121.257
1675.6406 | 121.2479 | -91.9922 | 29.2511 | 0.46128 | 0.035939 | 0.0036769 | 0.3693 | 0.055533 | 0.52065 | -0.031739 | 0.4947 | 3.9077 | 0.045579 | 0.10969 | 3.2164 | 0.0768 | -5.9463 | -0.027466 | -17.9306 | -1.6159 | 0.23804 | -91.951 | -92.0837 | 28.6377 | -0.15106 | 26.6602 | 29.0176 | 28.9993 | -91.9052 | -91.9556 | 0.041198 | -0.091553 | -29.0131 | 91.9647 | 90.3763 | 90.4678 | -35.1974 | 0.086975 | 0.036621 | -0.23346 | 120.6299 | 118.6523 | 118.6157 | -0.25177 | 92.2302 | 86.0458 | 74.0616 | -121.3348 | 121.0098 | 120.9915 | 91.8411 | -121.2067
1676.6406 | 121.3028 | -90.358 | 30.8533 | 0.50706 | 0.023121 | -0.0027321 | 0.37357 | 0.058738 | 0.51318 | -0.032808 | 5.7742 | 3.8874 | 0.055192 | 0.093665 | 3.2228 | 0.080004 | -5.9647 | -0.045776 | -17.9214 | -2.1973 | 0.23346 | -90.2985 | -90.4175 | 30.3131 | -0.004578 | 28.4271 | 30.6931 | 30.5878 | -90.3305 | -90.3213 | 0.059509 | -0.059509 | -30.6198 | 90.3122 | 88.1607 | 88.2202 | -36.8179 | 0.027466 | 0.036621 | -0.16022 | 120.6711 | 118.7851 | 118.7485 | -0.2655 | 90.5914 | 84.3933 | 72.4365 | -121.2708 | 121.051 | 120.9457 | 90.3534 | -121.1746
1677.6406 | 121.3165 | -97.5357 | 23.6664 | 0.47654 | 0.039143 | 0.0026089 | 0.36823 | 0.061942 | 0.54736 | -0.034944 | -0.16142 | 3.9579 | 0.058397 | 0.089393 | 3.2271 | 0.080004 | -6.1157 | -0.28381 | -19.78 | -1.9226 | 0.24261 | -97.5174 | -97.6181 | 23.0392 | -0.13275 | 21.1166 | 23.4238 | 23.3551 | -97.5082 | -97.5128 | 0.018311 | -0.082397 | -23.4238 | 97.2519 | 95.6131 | 95.6955 | -29.7821 | 0.027466 | 0.022889 | -0.24261 | 120.575 | 118.6523 | 118.6295 | -0.31128 | 97.7783 | 91.42 | 77.7557 | -121.2845 | 120.9595 | 120.8908 | 97.403 | -121.1792
1678.6406 | 121.3028 | -98.9868 | 22.2656 | 0.21714 | 0.019917 | -0.06041 | 0.33405 | 0.068351 | 0.55804 | -0.028535 | 0.58626 | 3.9515 | 0.060533 | 0.093665 | 3.2345 | 0.077868 | -6.1203 | -0.082397 | -19.8853 | -1.8494 | 0.24261 | -98.9365 | -99.0417 | 21.6019 | -0.16479 | 19.693 | 22.0367 | 21.9727 | -98.941 | -98.9548 | 0.050354 | -0.054932 | -22.023 | 98.9044 | 97.1375 | 97.1924 | -28.3859 | 0.045776 | 0.032043 | -0.22888 | 120.5887 | 118.6798 | 118.6478 | -0.29297 | 99.2294 | 92.8665 | 79.1016 | -121.3074 | 121.0236 | 120.9595 | 98.822 | -121.2204
1679.6406 | 121.3394 | -96.9131 | 24.2706 | -0.33217 | 0.045552 | -0.0080721 | 0.38532 | 0.059806 | 0.54629 | -0.036012 | 0.58626 | 3.928 | 0.05626 | 0.096869 | 3.226 | 0.063982 | -6.1386 | -0.050354 | -19.4046 | -2.3804 | 0.22888 | -96.8994 | -97.0093 | 23.671 | -0.1236 | 21.8582 | 24.0143 | 23.996 | -96.9131 | -96.9177 | 0.013733 | -0.09613 | -24.0417 | 96.8628 | 94.5328 | 94.6289 | -30.4092 | 0 | -0.004578 | -0.25635 | 120.5841 | 118.7714 | 118.7759 | -0.27466 | 97.142 | 90.7745 | 77.5085 | -121.2799 | 120.9274 | 120.9091 | 96.7896 | -121.1884
1680.6406 | 121.4081 | -116.3269 | 4.8157 | 0.56809 | 0.027394 | 0.00047294 | 0.3725 | 0.077964 | 0.65844 | -0.03708 | 0.58626 | 4.0562 | 0.034898 | 0.086188 | 3.2132 | 0.069323 | -6.9626 | 0.041199 | -23.1766 | -1.8951 | 0.19226 | -116.3315 | -116.4276 | 4.1885 | -0.10071 | 2.2293 | 4.5364 | 4.4952 | -116.3727 | -116.3544 | -0.004578 | -0.10071 | -4.6234 | 116.3681 | 114.4318 | 114.5325 | -11.7783 | -0.045777 | -0.027466 | -0.27924 | 120.5154 | 118.5562 | 118.5837 | -0.32043 | 116.5192 | 109.3643 | 93.1503 | -121.2433 | 120.8633 | 120.8221 | 116.2262 | -121.17
1681.6406 | 121.3577 | -116.4139 | 4.7928 | 0.55284 | 0.031666 | 0.014358 | 0.3725 | 0.081168 | 0.6563 | -0.034944 | 0.61677 | 4.0754 | 0.05092 | 0.086188 | 3.2271 | 0.068255 | -6.9351 | -0.013733 | -23.0072 | -1.6479 | 0.2243 | -116.4001 | -116.51 | 4.129 | -0.16937 | 2.2339 | 4.5319 | 4.5044 | -116.423 | -116.3681 | 0.013733 | -0.096131 | -4.5685 | 116.4001 | 114.7659 | 114.8621 | -11.7279 | -0.009156 | 0.045776 | -0.26093 | 120.5429 | 118.6478 | 118.602 | -0.28839 | 116.6382 | 109.4788 | 93.4067 | -121.3028 | 120.9457 | 120.9183 | 116.2445 | -121.1609
1682.6406 | 121.3898 | -116.4368 | 4.7379 | 0.58335 | 0.02419 | 0.014358 | 0.38211 | 0.071555 | 0.66271 | -0.039216 | 0.69307 | 4.0679 | 0.038102 | 0.11182 | 3.2185 | 0.069323 | -6.926 | 0.004578 | -23.1308 | -1.9318 | 0.21057 | -116.4322 | -116.5512 | 4.1016 | -0.14648 | 2.2293 | 4.4815 | 4.4495 | -116.4688 | -116.3864 | 0.004578 | -0.11444 | -4.5273 | 116.4413 | 114.505 | 114.6194 | -11.6638 | -0.032043 | 0.050354 | -0.25635 | 120.5383 | 118.6661 | 118.6157 | -0.28839 | 116.6473 | 109.5108 | 93.306 | -121.2891 | 120.9183 | 120.8862 | 116.2903 | -121.1243
1683.6406 | 121.4447 | -116.3315 | 4.8569 | 0.62913 | 0.020985 | -0.0016631 | 0.37036 | 0.087577 | 0.64883 | -0.039216 | 0.73885 | 4.0658 | 0.05626 | 0.10328 | 3.2239 | 0.073595 | -6.8848 | 0.09613 | -22.9797 | -1.8173 | 0.17853 | -116.2354 | -116.3452 | 4.1565 | -0.4303 | 2.4078 | 4.5731 | 4.5273 | -116.3589 | -116.304 | 0.09613 | -0.013733 | -4.6783 | 116.4276 | 114.5142 | 114.5279 | -11.7416 | -0.027466 | 0.027466 | -0.28381 | 120.488 | 118.7393 | 118.7119 | -0.32959 | 116.51 | 109.4467 | 93.3517 | -121.2021 | 120.9045 | 120.8588 | 115.9012 | -121.1609
1684.6875 | 121.257 | -116.4047 | 4.8935 | 0.29344 | -0.045238 | 0.088058 | 0.30414 | 0.082236 | 0.68087 | -0.041353 | 0.17427 | 4.0797 | 0.058397 | 0.10007 | 3.2249 | 0.068255 | -6.4957 | -0.045776 | -23.14 | -1.68 | 0.2243 | -116.3773 | -116.4459 | 4.097 | -0.29755 | 2.2156 | 4.6143 | 4.5639 | -116.4001 | -116.3544 | 0.027466 | -0.041199 | -4.6692 | 116.3589 | 114.7247 | 114.7659 | -11.3892 | 0.004578 | 0.050354 | -0.27924 | 120.5017 | 118.6203 | 118.5699 | -0.32959 | 116.629 | 109.9091 | 93.2648 | -121.3394 | 121.019 | 120.9686 | 116.1072 | -121.2479
1685.6406 | 121.2845 | -116.4871 | 4.7745 | -0.30166 | 0.028462 | 0.010086 | 0.36609 | 0.082236 | 0.63601 | -0.047761 | -4.205 | 4.0647 | 0.05092 | 0.10755 | 3.2036 | 0.067187 | -6.4636 | -0.004578 | -23.2361 | -1.9958 | 0.23804 | -116.4551 | -116.5695 | 4.0558 | -0.28839 | 2.2293 | 4.541 | 4.5136 | -116.4825 | -116.4276 | 0.032044 | -0.082397 | -4.5364 | 116.4825 | 114.4913 | 114.5737 | -11.2381 | 0.004578 | 0.05951 | -0.23346 | 120.5429 | 118.7164 | 118.6569 | -0.26092 | 116.7252 | 110.0235 | 93.251 | -121.344 | 121.0281 | 121.0007 | 116.1987 | -121.2021
1686.6406 | 121.376 | -116.3864 | 4.8477 | 0.47654 | 0.019917 | 0.0026089 | 0.35221 | 0.082236 | 0.63387 | -0.043489 | 0.46419 | 4.0647 | 0.051988 | 0.084052 | 3.211 | 0.080004 | -6.4087 | 0.064087 | -23.1857 | -1.7853 | 0.20599 | -116.2994 | -116.4093 | 4.1382 | -0.14648 | 2.3529 | 4.5364 | 4.4907 | -116.3727 | -116.3361 | 0.086976 | -0.022888 | -4.6417 | 116.4505 | 114.6011 | 114.624 | -11.2564 | 0.013733 | 0.050354 | -0.31128 | 120.5246 | 118.7393 | 118.689 | -0.35705 | 116.5924 | 109.9777 | 93.2007 | -121.257 | 120.9229 | 120.8771 | 116.2399 | -121.1838
1687.6406 | 121.3852 | -116.3269 | 4.8431 | 0.24766 | 0.014576 | 0.012222 | 0.36075 | 0.084372 | 0.6563 | -0.031739 | 0.63203 | 4.0626 | 0.044511 | 0.095801 | 3.2185 | 0.069323 | -6.0883 | 0.10986 | -23.2132 | -1.4648 | 0.19226 | -116.2949 | -116.4185 | 4.2206 | -0.11902 | 2.3666 | 4.5822 | 4.5136 | -116.3315 | -116.2903 | 0.032043 | -0.091553 | -4.6509 | 116.4368 | 114.8621 | 114.9536 | -10.9314 | -0.004578 | 0.036621 | -0.26093 | 120.5475 | 118.6935 | 118.6569 | -0.32959 | 116.5192 | 110.2386 | 93.1137 | -121.2616 | 120.9091 | 120.8405 | 116.2079 | -121.1334
1688.6406 | 121.3852 | -116.2628 | 4.9026 | 0.47654 | 0.020985 | 0.0068819 | 0.36823 | 0.0801 | 0.64776 | -0.040284 | 0.67781 | 4.0573 | 0.031694 | 0.097938 | 3.2143 | 0.075732 | -6.3492 | 0.091553 | -23.0804 | -1.6708 | 0.20599 | -116.1804 | -116.3269 | 4.2892 | -0.14648 | 2.4216 | 4.6417 | 4.6051 | -116.2582 | -116.217 | 0.082397 | -0.064087 | -4.6967 | 116.3544 | 114.592 | 114.6561 | -11.2518 | 0.004577 | 0.045776 | -0.26093 | 120.5521 | 118.6844 | 118.6386 | -0.29755 | 116.4688 | 109.9136 | 93.1824 | -121.2296 | 120.9045 | 120.8679 | 116.1163 | -121.1197
1689.6406 | 121.3806 | -116.3223 | 4.8889 | 0.58335 | -0.00037681 | 0.016495 | 0.3693 | 0.075827 | 0.64135 | -0.040284 | 0.52522 | 4.053 | 0.026353 | 0.10648 | 3.2143 | 0.072527 | -6.5094 | 0.10071 | -22.9156 | -1.6296 | 0.20142 | -116.272 | -116.3773 | 4.2389 | -0.14648 | 2.4033 | 4.6143 | 4.5685 | -116.3086 | -116.2766 | 0.050354 | -0.054931 | -4.6875 | 116.423 | 114.6927 | 114.7476 | -11.3983 | 0.013733 | 0.045777 | -0.27466 | 120.5612 | 118.7256 | 118.6798 | -0.32043 | 116.5237 | 109.8129 | 93.4067 | -121.2662 | 120.9366 | 120.8908 | 116.1758 | -121.1655
1690.6406 | 121.2799 | -116.3223 | 4.9484 | -0.2864 | -0.0067858 | 0.0026089 | 0.36609 | 0.08544 | 0.64776 | -0.027467 | -0.52763 | 4.0637 | 0.034898 | 0.10221 | 3.2175 | 0.058642 | -6.9534 | 0.018311 | -22.9385 | -1.9089 | 0.22888 | -116.3315 | -116.4551 | 4.184 | -0.19684 | 2.3438 | 4.6692 | 4.6097 | -116.3315 | -116.272 | -0.009155 | -0.13275 | -4.7195 | 116.3406 | 114.4135 | 114.5462 | -11.9019 | -0.009155 | 0.050354 | -0.27924 | 120.5063 | 118.6661 | 118.6157 | -0.33875 | 116.5512 | 109.3689 | 93.3838 | -121.4035 | 120.9915 | 120.932 | 116.1255 | -121.2204
1691.6406 | 121.3531 | -116.3361 | 4.9026 | 0.52232 | 0.013508 | 0.01329 | 0.36502 | 0.079032 | 0.64562 | -0.047761 | 0.571 | 4.0551 | 0.049852 | 0.10328 | 3.2121 | 0.073595 | -7.0084 | 0.09613 | -22.7646 | -1.5884 | 0.21515 | -116.2537 | -116.3635 | 4.2389 | -0.16022 | 2.4582 | 4.628 | 4.5731 | -116.2811 | -116.2491 | 0.082398 | -0.027465 | -4.6875 | 116.4322 | 114.7476 | 114.7751 | -11.911 | 0.054932 | 0.086976 | -0.27466 | 120.575 | 118.7943 | 118.7073 | -0.32959 | 116.5512 | 109.3277 | 93.5715 | -121.2662 | 120.9641 | 120.9091 | 116.1758 | -121.1517
1692.6406 | 121.344 | -116.3132 | 4.9026 | 0.44602 | 0.030598 | 0.012222 | 0.36716 | 0.072623 | 0.64776 | -0.03708 | 0.40315 | 4.0637 | 0.043443 | 0.097938 | 3.2217 | 0.071459 | -6.9305 | 0.073242 | -22.4167 | -1.8036 | 0.19684 | -116.2628 | -116.3589 | 4.2343 | -0.15564 | 2.4078 | 4.6234 | 4.5731 | -116.3086 | -116.272 | 0.050354 | -0.045777 | -4.7058 | 116.3864 | 114.5096 | 114.5554 | -11.8332 | 0.004577 | 0.041198 | -0.27924 | 120.5475 | 118.721 | 118.6798 | -0.32959 | 116.51 | 109.3826 | 93.8965 | -121.2616 | 120.9366 | 120.8862 | 116.1575 | -121.1746
1693.6406 | 121.3715 | -116.1438 | 5.0354 | 0.3087 | -0.0067858 | 0.017563 | 0.35541 | 0.08544 | 0.63708 | -0.044557 | 0.32686 | 4.0701 | 0.03383 | 0.093665 | 3.2271 | 0.074663 | -7.0908 | 0.064087 | -22.641 | -1.8036 | 0.20142 | -116.2308 | -116.3727 | 4.3304 | -0.12817 | 2.5223 | 4.7195 | 4.6463 | -116.2079 | -116.153 | -0.086975 | -0.22888 | -4.834 | 116.2079 | 114.3402 | 114.5691 | -12.1262 | -0.064087 | -0.009155 | -0.31586 | 120.4742 | 118.6661 | 118.6752 | -0.3891 | 116.3452 | 109.053 | 93.5028 | -121.4081 | 120.8633 | 120.7901 | 116.0156 | -121.1884
1694.6406 | 121.3623 | -116.4825 | 4.7424 | 0.20188 | -0.0067858 | 0.016495 | 0.36823 | 0.084372 | 0.63067 | -0.03708 | -0.0088351 | 4.0615 | 0.040239 | 0.10328 | 3.2078 | 0.073595 | -8.2901 | -0.14191 | -23.2269 | -2.4948 | 0.18768 | -116.51 | -116.6061 | 4.0695 | -0.12817 | 2.3071 | 4.4312 | 4.39 | -116.4917 | -116.4322 | -0.027466 | -0.1236 | -4.5547 | 116.3406 | 113.9877 | 114.1113 | -13.0325 | -0.009155 | 0.050354 | -0.31128 | 120.5521 | 118.7897 | 118.7393 | -0.35248 | 116.6702 | 108.1924 | 93.2556 | -121.3486 | 120.9137 | 120.8725 | 116.3544 | -121.1746
1695.6406 | 121.344 | -116.423 | 4.8248 | 1.0411 | -0.014263 | -0.02623 | 0.38959 | 0.077964 | 0.67874 | -0.027467 | -0.11565 | 4.0637 | 0.049852 | 0.091529 | 3.2014 | 0.044756 | -7.7042 | 0.041199 | -22.6273 | -2.0416 | 0.2243 | -116.3864 | -116.5146 | 4.1473 | -0.16022 | 2.3209 | 4.5593 | 4.5136 | -116.4001 | -116.3727 | 0.036621 | -0.091552 | -4.6005 | 116.4642 | 114.3814 | 114.473 | -12.529 | 0.022889 | 0.050354 | -0.2655 | 120.5704 | 118.7439 | 118.6935 | -0.31128 | 116.6473 | 108.7189 | 93.7958 | -121.3394 | 120.9824 | 120.9366 | 116.2628 | -121.1975
1696.6406 | 121.4035 | -115.773 | 5.397 | 0.24766 | 0.0049632 | 0.0068819 | 0.38425 | 0.071555 | 0.6296 | -0.028535 | 0.29634 | 4.0647 | 0.03383 | 0.097938 | 3.2153 | 0.075732 | -7.576 | 0.064087 | -22.5082 | -2.0187 | 0.15106 | -115.7776 | -115.892 | 4.747 | -0.10071 | 2.8839 | 5.1315 | 5.0858 | -115.8142 | -115.7593 | -0.004578 | -0.11902 | -5.246 | 115.8371 | 113.7543 | 113.8733 | -12.973 | -0.041199 | 0.013733 | -0.2655 | 120.52 | 118.6569 | 118.6432 | -0.31128 | 115.9241 | 108.197 | 93.2648 | -121.2891 | 120.9045 | 120.8588 | 115.6723 | -121.1563
1697.6406 | 121.4264 | -115.8783 | 5.2917 | 0.17137 | 0.00069119 | 0.019699 | 0.36182 | 0.077964 | 0.63601 | -0.040284 | 0.12849 | 4.0551 | 0.045579 | 0.090461 | 3.2228 | 0.073595 | -7.2006 | 0.14648 | -22.0139 | -1.7807 | 0.21973 | -115.8463 | -115.9836 | 4.7104 | -0.059509 | 2.916 | 5.0079 | 4.9576 | -115.9058 | -115.8829 | 0.032044 | -0.10529 | -5.072 | 116.0248 | 114.0976 | 114.2029 | -12.4924 | -0.027466 | -0.004578 | -0.28381 | 120.5887 | 118.7943 | 118.7988 | -0.33417 | 116.098 | 108.6777 | 93.8644 | -121.2753 | 120.8862 | 120.8359 | 115.8188 | -121.1746
1698.6406 | 121.4081 | -115.7135 | 5.5069 | -0.88149 | -0.015331 | 0.0079499 | 0.36182 | 0.079032 | 0.62853 | -0.030671 | 0.20479 | 4.0477 | 0.032762 | 0.084052 | 3.2132 | 0.072527 | -6.9672 | 0.050354 | -21.8353 | -1.799 | 0.16937 | -115.7043 | -115.8096 | 4.8477 | -0.09613 | 3.0441 | 5.2139 | 5.159 | -115.6906 | -115.6586 | 0.009155 | -0.09613 | -5.3375 | 115.7639 | 113.9145 | 114.0106 | -12.4741 | 0.022888 | 0.054932 | -0.29297 | 120.5612 | 118.7576 | 118.7027 | -0.3479 | 115.8829 | 108.7463 | 93.8782 | -121.3165 | 120.9274 | 120.8725 | 115.6174 | -121.1655
1699.6406 | 121.431 | -115.8096 | 5.3879 | 0.00352 | 0.00069119 | 0.0079499 | 0.37357 | 0.075827 | 0.63174 | -0.028535 | -0.0088351 | 4.0455 | 0.030626 | 0.10435 | 3.2132 | 0.062914 | -7.0816 | 0.15106 | -21.6614 | -1.8082 | 0.21515 | -115.7639 | -115.8691 | 4.7791 | -0.045776 | 2.8107 | 5.1178 | 5.0583 | -115.8005 | -115.773 | 0.045776 | -0.05951 | -5.1727 | 115.9607 | 114.0015 | 114.061 | -12.4695 | 0.009155 | 0.036621 | -0.27008 | 120.5887 | 118.6203 | 118.5837 | -0.32959 | 116.0248 | 108.728 | 94.1483 | -121.257 | 120.9274 | 120.8679 | 115.7639 | -121.1609
1700.6406 | 121.3348 | -115.9241 | 5.3192 | -0.2864 | 0.025258 | 0.0058129 | 0.37998 | 0.076896 | 0.65737 | -0.030671 | -0.34453 | 4.0594 | 0.053056 | 0.10114 | 3.2239 | 0.050097 | -6.8069 | 0.018311 | -21.7163 | -1.8448 | 0.21515 | -115.9103 | -116.0385 | 4.5822 | -0.16479 | 2.536 | 5.0583 | 4.9896 | -115.9424 | -115.9058 | 0.013733 | -0.11444 | -5.1041 | 115.9424 | 114.0793 | 114.1937 | -12.1262 | -0.018311 | 0.01831 | -0.26092 | 120.5063 | 118.4601 | 118.4418 | -0.32959 | 116.1392 | 109.1171 | 94.2078 | -121.3577 | 120.9824 | 120.9137 | 115.7593 | -121.225
1701.6406 | 121.4264 | -116.2216 | 4.9622 | 0.15611 | 0.0071002 | 0.01329 | 0.37891 | 0.075827 | 0.63387 | -0.031739 | 0.14375 | 4.0562 | 0.034898 | 0.096869 | 3.2228 | 0.073595 | -7.3013 | 0.14191 | -21.9131 | -1.8173 | 0.21515 | -116.1942 | -116.2994 | 4.3396 | -0.036621 | 2.5635 | 4.6555 | 4.6005 | -116.2399 | -116.2033 | 0.027466 | -0.077819 | -4.747 | 116.3635 | 114.4043 | 114.4821 | -12.2635 | -0.01831 | 0.018311 | -0.3067 | 120.5612 | 118.7851 | 118.7668 | -0.36163 | 116.4368 | 108.9203 | 94.3085 | -121.2616 | 120.8771 | 120.8221 | 116.185 | -121.1655
1702.6406 | 121.4127 | -116.1713 | 5.0262 | 0.12559 | 0.0060322 | 0.016495 | 0.37357 | 0.071555 | 0.63067 | -0.047761 | 0.097976 | 4.0519 | 0.042375 | 0.075507 | 3.2089 | 0.061846 | -7.2601 | 0.15106 | -21.6156 | -1.8082 | 0.21515 | -116.1484 | -116.2399 | 4.4083 | -0.036621 | 2.6047 | 4.7424 | 4.6783 | -116.153 | -116.1163 | 0.022889 | -0.068664 | -4.8111 | 116.3223 | 114.3631 | 114.4318 | -12.2864 | 0.018311 | 0.054932 | -0.28381 | 120.5795 | 118.7759 | 118.721 | -0.3479 | 116.3864 | 108.9111 | 94.5557 | -121.2662 | 120.9137 | 120.8496 | 116.1346 | -121.1426
1703.6406 | 121.4127 | -115.8783 | 5.3146 | 0.034038 | -0.0057178 | 0.020767 | 0.36716 | 0.079032 | 0.63708 | -0.042421 | 0.14375 | 4.0477 | 0.028489 | 0.096869 | 3.211 | 0.071459 | -7.0404 | 0.13733 | -21.8903 | -1.7532 | 0.21057 | -115.8279 | -115.8875 | 4.7424 | -0.045776 | 2.8748 | 5.0446 | 4.9667 | -115.8646 | -115.8417 | 0.050354 | -0.009155 | -5.1041 | 116.0156 | 114.1251 | 114.1342 | -12.355 | 0.013733 | 0.036621 | -0.27008 | 120.6207 | 118.7531 | 118.7164 | -0.3479 | 116.0889 | 108.8379 | 93.988 | -121.2021 | 120.9229 | 120.845 | 115.8325 | -121.1563
1704.6875 | 121.2845 | -115.7181 | 5.4657 | -0.10329 | -0.00037681 | 0.0090179 | 0.37464 | 0.086509 | 0.63387 | -0.036012 | 0.0064239 | 4.0541 | 0.027421 | 0.10328 | 3.211 | 0.066119 | -6.958 | 0.15106 | -21.7072 | -1.799 | 0.20142 | -115.6815 | -115.7822 | 4.8706 | -0.027466 | 3.0304 | 5.2002 | 5.1361 | -115.7364 | -115.654 | 0.036621 | -0.064087 | -5.2643 | 115.8691 | 113.9191 | 113.9832 | -12.4237 | -0.01831 | 0.064087 | -0.2655 | 120.5887 | 118.7485 | 118.6844 | -0.32959 | 115.9195 | 108.7601 | 94.0109 | -121.2479 | 120.9183 | 120.8542 | 115.6906 | -121.1197
1705.6406 | 121.2753 | -115.9287 | 5.3375 | 0.33921 | 0.032734 | -0.0091401 | 0.37357 | 0.076896 | 0.67126 | 0.0056447 | 0.26582 | 4.0605 | 0.035966 | 0.10969 | 3.2292 | 0.062914 | -7.196 | -0.018311 | -22.2244 | -2.1698 | 0.24261 | -115.9195 | -116.0248 | 4.5914 | -0.2243 | 2.5635 | 5.0491 | 4.9896 | -115.9332 | -115.8737 | 0.009155 | -0.09613 | -5.0949 | 115.9103 | 113.7589 | 113.855 | -12.5336 | -0.004578 | 0.054932 | -0.28839 | 120.52 | 118.4921 | 118.4372 | -0.3479 | 116.1713 | 108.7326 | 93.7042 | -121.3623 | 120.9778 | 120.9183 | 115.7043 | -121.2112
1706.6406 | 121.4355 | -115.8829 | 5.3009 | 0.11033 | -0.00037681 | 0.015426 | 0.36716 | 0.079032 | 0.63067 | -0.041353 | 0.17427 | 4.0477 | 0.030626 | 0.08512 | 3.2046 | 0.0768 | -7.1594 | 0.13275 | -22.0825 | -1.7441 | 0.21973 | -115.8417 | -115.9561 | 4.715 | -0.032043 | 2.861 | 5.04 | 4.985 | -115.8783 | -115.8325 | 0.041199 | -0.073242 | -5.0812 | 116.0156 | 114.1388 | 114.212 | -12.4603 | 0.004578 | 0.050354 | -0.26093 | 120.5978 | 118.7439 | 118.6935 | -0.31586 | 116.1026 | 108.7234 | 93.8004 | -121.257 | 120.9229 | 120.8679 | 115.8508 | -121.1334
1707.6406 | 121.4355 | -115.9332 | 5.3009 | -0.042256 | 0.013508 | 0.025039 | 0.36395 | 0.086509 | 0.63067 | -0.036012 | 0.0064239 | 4.0477 | 0.041307 | 0.093665 | 3.2132 | 0.073595 | -7.0175 | 0.15564 | -22.3022 | -2.0142 | 0.20142 | -115.8783 | -115.9744 | 4.6967 | -0.032043 | 2.8519 | 5.0034 | 4.9484 | -115.9058 | -115.8508 | 0.054932 | -0.041198 | -5.0995 | 116.0889 | 113.9191 | 113.9603 | -12.3184 | 0.027466 | 0.082398 | -0.29755 | 120.6299 | 118.7851 | 118.7027 | -0.35248 | 116.1346 | 108.9157 | 93.631 | -121.2753 | 120.9366 | 120.8817 | 115.9012 | -121.1517
1708.6406 | 121.2936 | -116.1713 | 5.0995 | -0.25588 | 0.016713 | 0.028244 | 0.37784 | 0.087577 | 0.6499 | -0.039216 | -0.0088351 | 4.0679 | 0.05092 | 0.10007 | 3.2046 | 0.060778 | -7.0175 | 0.059509 | -22.6044 | -2.3117 | 0.23346 | -116.098 | -116.2262 | 4.3488 | -0.15106 | 2.5314 | 4.834 | 4.7836 | -116.1758 | -116.1163 | 0.073243 | -0.054931 | -4.866 | 116.2308 | 113.8596 | 113.9145 | -12.117 | -0.004577 | 0.054932 | -0.2655 | 120.52 | 118.7027 | 118.6478 | -0.31586 | 116.4047 | 109.1537 | 93.5669 | -121.3257 | 121.0052 | 120.9549 | 116.0202 | -121.2158
1709.6406 | 121.3989 | -116.0934 | 5.1178 | -0.042256 | -0.012126 | 0.0079499 | 0.36823 | 0.081168 | 0.62747 | -0.039216 | -0.039353 | 4.0444 | 0.03917 | 0.093665 | 3.2175 | 0.062914 | -6.9855 | 0.15106 | -22.6135 | -1.9501 | 0.20599 | -116.0522 | -116.1667 | 4.5181 | -0.013733 | 2.6413 | 4.8706 | 4.8019 | -116.0843 | -116.0156 | 0.041199 | -0.073242 | -4.9118 | 116.2445 | 114.1434 | 114.2166 | -12.1033 | 0.009155 | 0.07782 | -0.24719 | 120.6116 | 118.7347 | 118.6569 | -0.31586 | 116.2994 | 109.108 | 93.4799 | -121.2845 | 120.9641 | 120.8954 | 116.0797 | -121.1334
1710.6406 | 121.4401 | -115.6036 | 5.5664 | -0.026997 | 0.00069119 | 0.015426 | 0.3725 | 0.077964 | 0.63708 | -0.045625 | -0.06987 | 4.0306 | 0.041307 | 0.092597 | 3.1982 | 0.066119 | -6.8893 | 0.19226 | -22.3251 | -1.8356 | 0.20142 | -115.5762 | -115.6769 | 4.9713 | -0.036621 | 2.8931 | 5.3192 | 5.2414 | -115.6128 | -115.5807 | 0.027466 | -0.073242 | -5.365 | 115.7959 | 113.768 | 113.8412 | -12.4557 | -0.009155 | 0.022888 | -0.24719 | 120.575 | 118.4967 | 118.4738 | -0.32501 | 115.8051 | 108.7143 | 93.2785 | -121.2433 | 120.9229 | 120.845 | 115.567 | -121.1472
1711.6406 | 121.376 | -115.892 | 5.3329 | -1.797 | 0.01244 | -0.0059361 | 0.37357 | 0.08544 | 0.63708 | -0.044557 | -0.085129 | 4.0423 | 0.044511 | 0.095801 | 3.2025 | 0.056505 | -6.8985 | 0.13275 | -22.4121 | -1.7441 | 0.20142 | -115.8554 | -115.9698 | 4.6829 | -0.059509 | 2.6779 | 5.0217 | 4.9713 | -115.9149 | -115.8371 | 0.036621 | -0.07782 | -5.1315 | 116.0248 | 114.1479 | 114.2258 | -12.2314 | -0.022888 | 0.054932 | -0.31128 | 120.575 | 118.5699 | 118.515 | -0.36163 | 116.0934 | 108.9935 | 93.4799 | -121.3028 | 120.9137 | 120.8633 | 115.8325 | -121.17
1712.6406 | 121.4035 | -115.8737 | 5.3055 | -0.30166 | -0.0067858 | 0.017563 | 0.37357 | 0.072623 | 0.62426 | -0.033876 | -0.024094 | 4.0455 | 0.031694 | 0.095801 | 3.2121 | 0.053301 | -6.8802 | 0.17853 | -22.4075 | -2.5085 | 0.19684 | -115.8279 | -115.9561 | 4.7058 | -0.041199 | 2.7832 | 5.0354 | 4.9805 | -115.9012 | -115.8554 | 0.045776 | -0.082398 | -5.1086 | 116.0522 | 113.3652 | 113.4476 | -12.1857 | -0.027466 | 0.01831 | -0.27008 | 120.5795 | 118.6569 | 118.6386 | -0.32501 | 116.0706 | 108.9935 | 93.4662 | -121.2616 | 120.9091 | 120.8542 | 115.8325 | -121.1609
1713.6406 | 121.4127 | -116.4001 | 4.7836 | -0.026997 | 0.015645 | 0.01329 | 0.35861 | 0.079032 | 0.63708 | -0.040284 | -0.0088351 | 4.0519 | 0.040239 | 0.088325 | 3.2121 | 0.062914 | -6.8756 | 0.16022 | -22.3846 | -2.211 | 0.21057 | -116.3589 | -116.4871 | 4.1885 | -0.036621 | 2.2934 | 4.509 | 4.4632 | -116.4047 | -116.391 | 0.041198 | -0.086976 | -4.5731 | 116.5604 | 114.1891 | 114.2761 | -11.6592 | -0.004578 | 0.009155 | -0.27466 | 120.5887 | 118.6935 | 118.6844 | -0.32043 | 116.6107 | 109.5245 | 94.0155 | -121.2708 | 120.9091 | 120.8633 | 116.3635 | -121.1746
1714.6406 | 121.3989 | -116.3086 | 4.921 | -0.24062 | 0.016713 | 0.026108 | 0.40775 | 0.082236 | 0.65737 | -0.027467 | -0.43608 | 4.0519 | 0.046647 | 0.086188 | 3.2057 | 0.060778 | -6.9672 | 0.15106 | -22.1832 | -1.9272 | 0.17853 | -116.2903 | -116.391 | 4.2847 | -0.045776 | 2.4765 | 4.6326 | 4.5639 | -116.304 | -116.2582 | 0.018311 | -0.082397 | -4.7424 | 116.4597 | 114.3814 | 114.4638 | -11.8881 | 0.004578 | 0.050354 | -0.28839 | 120.5933 | 118.7851 | 118.7347 | -0.35705 | 116.4871 | 109.3414 | 94.1254 | -121.3119 | 120.9412 | 120.8725 | 116.2628 | -121.1792
1715.6406 | 121.312 | -116.4459 | 4.7882 | -0.22536 | 0.035939 | 0.01329 | 0.36075 | 0.081168 | 0.64135 | -0.036012 | -0.19194 | 4.0477 | 0.05092 | 0.10648 | 3.2153 | 0.060778 | -6.8756 | 0.10071 | -22.3068 | -2.2842 | 0.23346 | -116.423 | -116.5283 | 4.097 | -0.11902 | 2.298 | 4.5044 | 4.4449 | -116.4459 | -116.423 | 0.022888 | -0.082397 | -4.5547 | 116.5466 | 114.1617 | 114.2441 | -11.6638 | 0 | 0.022888 | -0.28381 | 120.5429 | 118.7439 | 118.721 | -0.34332 | 116.6794 | 109.5703 | 94.1391 | -121.3165 | 120.9503 | 120.8908 | 116.3269 | -121.2112
1716.6406 | 121.4127 | -116.423 | 4.747 | -0.14907 | 0.0071002 | 0.0015409 | 0.36395 | 0.08544 | 0.63601 | -0.036012 | 2.814 | 4.0444 | 0.048783 | 0.11289 | 3.2089 | 0.069323 | -6.8069 | 0.13275 | -22.1832 | -2.2522 | 0.1831 | -116.4597 | -116.6107 | 4.1473 | -0.073242 | 2.2202 | 4.454 | 4.39 | -116.4139 | -116.3956 | -0.036621 | -0.18768 | -4.5639 | 116.5558 | 114.1708 | 114.3585 | -11.554 | 0.009156 | 0.027466 | -0.29297 | 120.5704 | 118.6432 | 118.6157 | -0.35705 | 116.6061 | 109.6161 | 94.2398 | -121.3577 | 120.8771 | 120.813 | 116.3498 | -121.1426
1717.6406 | 121.3531 | -116.4963 | 4.7516 | -0.11855 | 0.0092362 | 0.0079499 | 0.36182 | 0.077964 | 0.63174 | -0.03708 | -0.14616 | 4.0551 | 0.03917 | 0.094733 | 3.21 | 0.067187 | -6.8985 | 0.1236 | -22.1787 | -2.7283 | 0.21057 | -116.478 | -116.5833 | 4.0649 | -0.086975 | 2.1744 | 4.454 | 4.3991 | -116.5192 | -116.478 | 0.018311 | -0.086975 | -4.541 | 116.6199 | 113.768 | 113.855 | -11.6501 | -0.022888 | 0.018311 | -0.29755 | 120.5612 | 118.6707 | 118.6523 | -0.35248 | 116.7068 | 109.5978 | 94.3176 | -121.3348 | 120.9503 | 120.8954 | 116.4093 | -121.2296
1718.6406 | 121.4081 | -116.4322 | 4.7928 | 0.50706 | 0.022053 | 0.011154 | 0.37784 | 0.087577 | 0.63922 | -0.032808 | -0.10039 | 4.0391 | 0.049852 | 0.090461 | 3.2121 | 0.06505 | -6.9946 | 0.1236 | -21.817 | -2.3026 | 0.21973 | -116.3818 | -116.4917 | 4.1611 | -0.054932 | 2.1652 | 4.5181 | 4.4724 | -116.4322 | -116.3818 | 0.050354 | -0.059509 | -4.5731 | 116.5558 | 114.1296 | 114.1891 | -11.7874 | 0 | 0.050354 | -0.27466 | 120.5933 | 118.5974 | 118.5471 | -0.32044 | 116.6519 | 109.4376 | 94.6152 | -121.2845 | 120.9503 | 120.9045 | 116.3773 | -121.1746
1719.6406 | 121.4172 | -116.3589 | 4.8798 | -1.8581 | 0.025258 | -0.00059506 | 0.36502 | 0.071555 | 0.64028 | -0.031739 | -0.19194 | 4.037 | 0.031694 | 0.10007 | 3.21 | 0.054369 | -6.9946 | 0.17395 | -22.0963 | -2.3392 | 0.21515 | -116.3315 | -116.4368 | 4.2206 | -0.054932 | 2.2614 | 4.5914 | 4.5364 | -116.3498 | -116.3452 | 0.027466 | -0.07782 | -4.6646 | 116.5329 | 114.0198 | 114.0976 | -11.8744 | 0.009156 | 0.013733 | -0.28839 | 120.5795 | 118.6203 | 118.6066 | -0.34332 | 116.5741 | 109.3643 | 94.2627 | -121.3165 | 120.9503 | 120.8954 | 116.304 | -121.225
1720.6406 | 121.4127 | -116.4185 | 4.7607 | 0.064555 | 0.038075 | 0.012222 | 0.3725 | 0.067282 | 0.63601 | -0.040284 | -0.06987 | 4.0359 | 0.031694 | 0.10007 | 3.1993 | 0.075732 | -6.8939 | 0.17395 | -22.0047 | -2.2339 | 0.21515 | -116.4047 | -116.5283 | 4.1565 | -0.032043 | 2.1881 | 4.4678 | 4.4449 | -116.4505 | -116.391 | 0.013733 | -0.10986 | -4.5456 | 116.5924 | 114.1846 | 114.2944 | -11.6547 | -0.032043 | 0.027466 | -0.29297 | 120.575 | 118.6066 | 118.5791 | -0.31586 | 116.6336 | 109.5245 | 94.4138 | -121.2891 | 120.8862 | 120.8633 | 116.3864 | -121.1517
1721.6406 | 121.3074 | -116.0843 | 5.1956 | 0.00352 | 0.0028272 | 0.018631 | 0.3693 | 0.070487 | 0.64135 | -0.038148 | -0.25298 | 4.053 | 0.030626 | 0.097938 | 3.2143 | 0.055437 | -6.9534 | 0 | -22.2519 | -1.9821 | 0.24261 | -116.0385 | -116.1804 | 4.4495 | -0.16022 | 2.3987 | 4.8935 | 4.8752 | -116.0889 | -116.0156 | 0.045777 | -0.09613 | -4.953 | 116.0843 | 114.1022 | 114.1983 | -12.149 | -0.004577 | 0.068665 | -0.30212 | 120.5338 | 118.483 | 118.4143 | -0.32043 | 116.3269 | 109.1309 | 93.8324 | -121.376 | 120.9778 | 120.9595 | 115.9241 | -121.2112
1722.6406 | 121.4081 | -116.2903 | 4.953 | -0.13381 | 0.0081682 | 0.0068819 | 0.3757 | 0.082236 | 0.63387 | -0.03708 | -0.14616 | 4.037 | 0.047715 | 0.084052 | 3.211 | 0.060778 | -6.8527 | 0.11444 | -22.11 | -2.3849 | 0.21515 | -116.2537 | -116.3773 | 4.2664 | -0.068665 | 2.3346 | 4.6738 | 4.6143 | -116.2949 | -116.2582 | 0.036621 | -0.086975 | -4.7379 | 116.4047 | 113.9053 | 113.9923 | -11.8057 | -0.004578 | 0.032043 | -0.27924 | 120.5566 | 118.6249 | 118.5928 | -0.33874 | 116.5054 | 109.4376 | 94.1803 | -121.3303 | 120.9641 | 120.9045 | 116.2216 | -121.2112
1723.6406 | 121.3623 | -116.478 | 4.7058 | -0.11855 | 0.0081682 | 0.020767 | 0.37036 | 0.077964 | 0.63494 | -0.043489 | -0.024094 | 4.0412 | 0.037034 | 0.10007 | 3.2185 | 0.057574 | -6.9122 | 0.15106 | -22.0551 | -2.0096 | 0.21515 | -116.4551 | -116.5741 | 4.0329 | 0.16479 | 2.2659 | 4.4403 | 4.3762 | -116.5329 | -116.4597 | 0.022888 | -0.096131 | -4.4907 | 116.629 | 114.4684 | 114.5645 | -11.618 | -0.054932 | 0.01831 | -0.2655 | 120.5109 | 118.7439 | 118.7256 | -0.32959 | 116.6931 | 109.5657 | 94.4229 | -121.2799 | 120.9183 | 120.8542 | 116.6428 | -121.1655
1724.6406 | 121.3028 | -116.4322 | 4.8431 | -0.2864 | 0.018849 | 0.0058129 | 0.36502 | 0.074759 | 0.6563 | -0.033876 | -0.17668 | 4.0594 | 0.032762 | 0.10007 | 3.2228 | 0.067187 | -6.9672 | 0.068665 | -21.9269 | -1.9226 | 0.23804 | -116.391 | -116.4871 | 4.0924 | -0.14191 | 2.4078 | 4.5685 | 4.4952 | -116.4413 | -116.3773 | 0.041199 | -0.054932 | -4.6051 | 116.5009 | 114.5096 | 114.5645 | -11.8103 | -0.009155 | 0.054932 | -0.27466 | 120.5246 | 118.84 | 118.7851 | -0.3479 | 116.6702 | 109.465 | 94.5053 | -121.3303 | 121.0007 | 120.9274 | 116.2903 | -121.2204
1725.6406 | 121.3715 | -116.2262 | 5.0079 | -0.22536 | 0.033803 | 0.0058129 | 0.38104 | 0.069419 | 0.64028 | -0.03708 | -0.0088351 | 4.0551 | 0.030626 | 0.088325 | 3.2196 | 0.058642 | -7.2601 | 0.11444 | -22.142 | -1.9592 | 0.18768 | -116.1896 | -116.304 | 4.3625 | -0.041199 | 2.623 | 4.7195 | 4.6646 | -116.2125 | -116.1942 | 0.036621 | -0.07782 | -4.8203 | 116.3406 | 114.267 | 114.3448 | -12.2681 | 0.013733 | 0.032043 | -0.28839 | 120.5887 | 118.8492 | 118.8171 | -0.34332 | 116.4139 | 108.9661 | 94.0842 | -121.312 | 120.9457 | 120.8908 | 116.185 | -121.2021
1726.6406 | 121.4264 | -116.4001 | 4.8111 | 0.17137 | 0.0038952 | 0.026108 | 0.38639 | 0.074759 | 0.63387 | -0.046693 | 0.021682 | 4.0434 | 0.03917 | 0.087256 | 3.2036 | 0.072527 | -7.132 | 0.15564 | -22.0322 | -2.0416 | 0.21515 | -116.3635 | -116.4734 | 4.2023 | -0.022888 | 2.4261 | 4.5319 | 4.4586 | -116.3956 | -116.3544 | 0.036621 | -0.073243 | -4.5959 | 116.5558 | 114.3585 | 114.4318 | -11.9431 | 0.004577 | 0.045776 | -0.27924 | 120.6024 | 118.8263 | 118.7805 | -0.35248 | 116.6153 | 109.2682 | 94.368 | -121.2845 | 120.932 | 120.8588 | 116.3773 | -121.1655
1727.6406 | 121.3394 | -116.3269 | 4.8935 | -0.25588 | 0.0038952 | 0.015426 | 0.37464 | 0.083304 | 0.63815 | -0.036012 | -0.14616 | 4.0434 | 0.035966 | 0.10114 | 3.2153 | 0.062914 | -7.0724 | 0.09613 | -21.8079 | -2.0554 | 0.22888 | -116.2994 | -116.4093 | 4.2252 | -0.09613 | 2.3575 | 4.6417 | 4.5639 | -116.3681 | -116.2949 | 0.027466 | -0.082398 | -4.6646 | 116.423 | 114.2715 | 114.3539 | -11.9659 | -0.041199 | 0.032043 | -0.25177 | 120.5521 | 118.6844 | 118.6523 | -0.32959 | 116.5558 | 109.2545 | 94.519 | -121.3028 | 120.9686 | 120.8908 | 116.2308 | -121.1884
1728.6406 | 121.4539 | -116.0889 | 5.1178 | -0.19484 | 0.0081682 | 0.0068819 | 0.37036 | 0.074759 | 0.63815 | -0.033876 | 0.0522 | 4.0519 | 0.019944 | 0.089393 | 3.2324 | 0.054369 | -7.0999 | 0.15106 | -21.7484 | -1.9547 | 0.21515 | -116.0614 | -116.1621 | 4.4495 | 0.036621 | 2.6276 | 4.8111 | 4.7516 | -116.1118 | -116.0522 | 0.027466 | -0.073242 | -4.9026 | 116.2399 | 114.1342 | 114.2075 | -12.2177 | -0.022888 | 0.036621 | -0.3067 | 120.5383 | 118.7164 | 118.6798 | -0.36621 | 116.304 | 108.989 | 94.3405 | -121.2799 | 120.9 | 120.8405 | 116.1255 | -121.17
1729.6406 | 121.3623 | -116.1209 | 5.1086 | -0.30166 | 0.0017592 | 0.0079499 | 0.36609 | 0.069419 | 0.63494 | -0.029603 | -0.11565 | 4.037 | 0.018876 | 0.10862 | 3.21 | 0.070391 | -7.0404 | 0.12817 | -21.7072 | -2.6138 | 0.21057 | -116.1255 | -116.2125 | 4.4312 | -0.064087 | 2.6688 | 4.8157 | 4.7745 | -116.1392 | -116.0889 | -0.004577 | -0.091552 | -4.8981 | 116.2491 | 113.5071 | 113.5986 | -12.149 | -0.01831 | 0.032044 | -0.29297 | 120.5521 | 118.7897 | 118.7576 | -0.33417 | 116.3315 | 109.0805 | 94.4138 | -121.3211 | 120.9366 | 120.8954 | 116.0568 | -121.1975
1730.6406 | 121.4722 | -116.3361 | 4.8477 | -0.16433 | -0.013195 | 0.022903 | 0.3725 | 0.076896 | 0.63387 | -0.033876 | 0.021682 | 4.0444 | 0.026353 | 0.092597 | 3.211 | 0.070391 | -7.1091 | 0.14648 | -21.8628 | -2.1515 | 0.19684 | -116.304 | -116.3956 | 4.2572 | -0.027466 | 2.536 | 4.6005 | 4.5364 | -116.3727 | -116.3315 | 0.032044 | -0.059509 | -4.6509 | 116.4825 | 114.1846 | 114.2441 | -11.9568 | -0.036621 | 0.004578 | -0.24719 | 120.5933 | 118.8721 | 118.8675 | -0.31128 | 116.5329 | 109.227 | 94.4733 | -121.2433 | 120.9366 | 120.8725 | 116.3086 | -121.1792
1731.6406 | 121.3806 | -116.2857 | 4.9576 | -1.1714 | 0.0081682 | 0.0090179 | 0.36823 | 0.0801 | 0.64776 | -0.034944 | -0.13091 | 4.053 | 0.035966 | 0.089393 | 3.2132 | 0.066119 | -7.1777 | 0.13275 | -22.1695 | -1.9043 | 0.21057 | -116.2445 | -116.3544 | 4.3121 | -0.073242 | 2.5681 | 4.6783 | 4.6188 | -116.2949 | -116.2537 | 0.041199 | -0.068664 | -4.747 | 116.4185 | 114.3814 | 114.4501 | -12.1353 | -0.009155 | 0.032044 | -0.27924 | 120.5978 | 118.8538 | 118.8217 | -0.33875 | 116.4963 | 109.108 | 94.1162 | -121.312 | 120.9641 | 120.9045 | 116.2125 | -121.2112
1732.6406 | 121.3806 | -116.3544 | 4.866 | 0.46128 | 0.022053 | -0.0016631 | 0.36609 | 0.077964 | 0.63174 | -0.044557 | -0.024094 | 4.038 | 0.038102 | 0.092597 | 3.2068 | 0.06505 | -7.0724 | 0.11444 | -22.2015 | -2.211 | 0.21057 | -116.2994 | -116.4276 | 4.2252 | -0.050354 | 2.5085 | 4.5822 | 4.541 | -116.3727 | -116.304 | 0.054932 | -0.073242 | -4.6555 | 116.4688 | 114.1434 | 114.2166 | -11.9385 | -0.018311 | 0.050354 | -0.28381 | 120.5795 | 118.8629 | 118.8126 | -0.32501 | 116.5649 | 109.2819 | 94.1528 | -121.2936 | 120.9366 | 120.8954 | 116.304 | -121.17
1733.6406 | 121.4035 | -116.3406 | 4.8889 | 4.4133 | 0.0092362 | 0.01329 | 0.36716 | 0.089713 | 0.63174 | -0.033876 | 0.021682 | 4.0444 | 0.029557 | 0.08512 | 3.2153 | 0.058642 | -7.2281 | 0.11444 | -22.0184 | -2.1515 | 0.19684 | -116.2811 | -116.4001 | 4.2709 | -0.073242 | 2.5589 | 4.628 | 4.5685 | -116.3177 | -116.2949 | 0.059509 | -0.059509 | -4.6921 | 116.4551 | 114.1891 | 114.2487 | -12.117 | 0.022888 | 0.045776 | -0.26093 | 120.6116 | 118.8995 | 118.8538 | -0.32043 | 116.5375 | 109.1125 | 94.3222 | -121.2891 | 120.9686 | 120.9091 | 116.2674 | -121.1838
1734.6406 | 121.3806 | -116.3727 | 4.8523 | -3.445 | 0.015645 | -0.012345 | 0.37784 | 0.081168 | 0.64883 | -0.026399 | -0.26824 | 4.0391 | 0.032762 | 0.10114 | 3.2153 | 0.073595 | -7.2281 | 0.15564 | -21.9131 | -1.8677 | 0.17853 | -116.3544 | -116.4597 | 4.2114 | -0.064087 | 2.4445 | 4.5868 | 4.5181 | -116.3452 | -116.3132 | 0.018311 | -0.086975 | -4.6738 | 116.5283 | 114.505 | 114.592 | -12.0804 | 0.027466 | 0.05951 | -0.2655 | 120.5841 | 118.8171 | 118.7576 | -0.33417 | 116.5512 | 109.1446 | 94.4595 | -121.312 | 120.9595 | 120.8908 | 116.3086 | -121.1655
1735.6406 | 121.312 | -116.2766 | 5.0217 | -0.19484 | 0.016713 | 0.0090179 | 0.35968 | 0.072623 | 0.6531 | -0.041353 | -0.26824 | 4.0498 | 0.035966 | 0.11075 | 3.2217 | 0.077868 | -7.164 | 0.022888 | -22.0505 | -1.9089 | 0.23346 | -116.2582 | -116.3864 | 4.248 | -0.16022 | 2.4765 | 4.7195 | 4.6646 | -116.3086 | -116.2491 | 0.01831 | -0.10986 | -4.7882 | 116.2994 | 114.3677 | 114.4775 | -12.1857 | -0.032044 | 0.027466 | -0.30212 | 120.5246 | 118.7531 | 118.7256 | -0.35705 | 116.51 | 109.1125 | 94.2261 | -121.4081 | 120.9961 | 120.9412 | 116.1163 | -121.2708
1736.6406 | 121.4127 | -116.4688 | 4.7195 | -0.13381 | -0.0099898 | 0.018631 | 0.36823 | 0.086509 | 0.60504 | -0.038148 | 0.67781 | 4.0338 | 0.038102 | 0.081916 | 3.2078 | 0.06505 | -6.9168 | -0.12817 | -22.0413 | -2.0828 | 0.16479 | -116.4642 | -116.5649 | 4.1016 | -0.041199 | 2.3346 | 4.454 | 4.3854 | -116.4871 | -116.4413 | 0.004578 | -0.09613 | -4.5547 | 116.3406 | 114.386 | 114.4821 | -11.6364 | -0.018311 | 0.027466 | -0.2655 | 120.5704 | 118.8034 | 118.7759 | -0.33417 | 116.6336 | 109.552 | 94.4275 | -121.2845 | 120.9229 | 120.8542 | 116.4276 | -121.1609
1737.6406 | 121.3531 | -116.3589 | 4.9164 | -0.25588 | 0.013508 | 0.01329 | 0.37357 | 0.08544 | 0.63281 | -0.041353 | -0.10039 | 4.0391 | 0.025285 | 0.10435 | 3.2196 | 0.067187 | -7.1045 | 0.10986 | -22.2931 | -2.5406 | 0.2243 | -116.2811 | -116.4413 | 4.2023 | -0.10071 | 2.4445 | 4.6097 | 4.5639 | -116.3818 | -116.3223 | 0.07782 | -0.082397 | -4.6921 | 116.4688 | 113.8184 | 113.9008 | -12.0209 | -0.022888 | 0.036621 | -0.3067 | 120.5612 | 118.8034 | 118.7668 | -0.35248 | 116.5833 | 109.2545 | 94.0659 | -121.3577 | 120.9686 | 120.9229 | 116.2582 | -121.2387
1738.6875 | 121.4081 | -116.6611 | 4.5502 | 0.17137 | -0.0014448 | 0.0058129 | 0.37143 | 0.074759 | 0.6264 | -0.048829 | 0.26582 | 4.0348 | 0.038102 | 0.092597 | 3.2175 | 0.074663 | -7.0908 | 0.10529 | -21.9452 | -2.2659 | 0.23346 | -116.6199 | -116.7435 | 3.923 | -0.068665 | 2.3071 | 4.2847 | 4.2023 | -116.6611 | -116.6428 | 0.041199 | -0.082397 | -4.3167 | 116.7664 | 114.3951 | 114.4775 | -11.6409 | 0 | 0.018311 | -0.2655 | 120.5841 | 118.9682 | 118.9499 | -0.3479 | 116.8945 | 109.5703 | 94.7159 | -121.2936 | 120.9457 | 120.8633 | 116.5924 | -121.1929
1739.6406 | 121.4264 | -116.1392 | 5.0766 | -0.14907 | 0.0060322 | 0.0090179 | 0.37464 | 0.083304 | 0.6264 | -0.032808 | 5.1181 | 4.0423 | 0.03917 | 0.10007 | 3.2153 | 0.057574 | -6.958 | 0.16022 | -21.7255 | -2.5085 | 0.21057 | -116.098 | -116.2445 | 4.4632 | -0.022888 | 2.8061 | 4.7882 | 4.7333 | -116.1346 | -116.1255 | 0.041199 | -0.10529 | -4.866 | 116.2994 | 113.6307 | 113.736 | -12.0346 | 0.004577 | 0.013733 | -0.28839 | 120.6024 | 118.9453 | 118.9316 | -0.34332 | 116.3498 | 109.1812 | 94.4138 | -121.3211 | 120.9274 | 120.8725 | 116.1163 | -121.2021
1740.6406 | 121.4218 | -116.5421 | 4.6555 | -0.17959 | 0.0081682 | 0.020767 | 0.37464 | 0.071555 | 0.64028 | -0.033876 | 0.0522 | 4.0252 | 0.035966 | 0.10007 | 3.2132 | 0.060778 | -6.9672 | 0.16022 | -21.9818 | -2.5269 | 0.19684 | -116.5329 | -116.6336 | 4.0558 | -0.10071 | 2.3346 | 4.3579 | 4.2984 | -116.5787 | -116.5237 | 0.009155 | -0.091553 | -4.4586 | 116.7023 | 114.0152 | 114.1068 | -11.6226 | -0.036621 | 0.01831 | -0.29755 | 120.5978 | 118.8766 | 118.8583 | -0.35706 | 116.7389 | 109.5749 | 94.5602 | -121.2891 | 120.9 | 120.8405 | 116.4413 | -121.1792
1741.6406 | 121.3623 | -116.3177 | 4.921 | -0.2864 | 0.0092362 | 0.01329 | 0.37998 | 0.096122 | 0.63815 | -0.040284 | -0.13091 | 4.0434 | 0.03383 | 0.10648 | 3.21 | 0.061846 | -6.9534 | 0.14648 | -21.8536 | -2.0462 | 0.21057 | -116.2903 | -116.4185 | 4.2526 | -0.068665 | 2.5772 | 4.628 | 4.5868 | -116.3498 | -116.2949 | 0.027466 | -0.10071 | -4.7104 | 116.4642 | 114.2715 | 114.3723 | -11.8744 | -0.032043 | 0.022888 | -0.29297 | 120.5704 | 118.895 | 118.8721 | -0.33417 | 116.5283 | 109.3643 | 94.4641 | -121.3394 | 120.9457 | 120.9045 | 116.2491 | -121.2158
1742.6406 | 121.3852 | -116.3773 | 4.8431 | -0.65261 | -0.0067858 | 0.00047294 | 0.36609 | 0.08544 | 0.64669 | -0.034944 | -0.11565 | 4.0487 | 0.025285 | 0.10969 | 3.2175 | 0.057574 | -6.9214 | 0.15106 | -21.9406 | -1.8951 | 0.21057 | -116.3727 | -116.478 | 4.1885 | -0.059509 | 2.5314 | 4.5547 | 4.4952 | -116.4185 | -116.3589 | 0.004577 | -0.10071 | -4.6326 | 116.5283 | 114.4821 | 114.5828 | -11.7645 | -0.041199 | 0.01831 | -0.28839 | 120.5658 | 118.9087 | 118.8904 | -0.3479 | 116.5878 | 109.4559 | 94.4366 | -121.3211 | 120.932 | 120.8725 | 116.3177 | -121.2021
1743.6406 | 121.4172 | -116.4825 | 4.7287 | 3.0858 | 0.015645 | 0.023971 | 0.37891 | 0.075827 | 0.64349 | -0.038148 | 0.036941 | 4.0434 | 0.027421 | 0.089393 | 3.2164 | 0.06505 | -6.8665 | 0.10529 | -21.4416 | -2.0737 | 0.20599 | -116.4505 | -116.5558 | 4.0924 | -0.041199 | 2.449 | 4.4495 | 4.4083 | -116.5009 | -116.4597 | 0.032044 | -0.073242 | -4.5227 | 116.5878 | 114.4089 | 114.4821 | -11.5952 | -0.01831 | 0.022888 | -0.27924 | 120.575 | 118.9316 | 118.9087 | -0.32043 | 116.6885 | 109.6161 | 95.0409 | -121.2845 | 120.932 | 120.8908 | 116.4413 | -121.1884
1744.6406 | 121.4172 | -116.4139 | 4.8019 | -0.25588 | 0.0038952 | 0.0036769 | 0.37143 | 0.077964 | 0.6296 | -0.032808 | 0.35738 | 4.038 | 0.028489 | 0.096869 | 3.2025 | 0.058642 | -6.9763 | 0.13733 | -21.6339 | -2.1927 | 0.19684 | -116.3773 | -116.5146 | 4.184 | -0.054932 | 2.4857 | 4.509 | 4.4769 | -116.4368 | -116.3864 | 0.036621 | -0.10071 | -4.6051 | 116.5512 | 114.2212 | 114.3219 | -11.7783 | -0.022889 | 0.027465 | -0.29297 | 120.5978 | 118.8995 | 118.8721 | -0.32501 | 116.6107 | 109.4376 | 94.78 | -121.3165 | 120.9229 | 120.8908 | 116.3589 | -121.1884
1745.6406 | 121.4172 | -116.3864 | 4.8431 | -0.13381 | 0.0092362 | 0.011154 | 0.37143 | 0.086509 | 0.63494 | -0.036012 | 3.6533 | 4.0455 | 0.029557 | 0.10007 | 3.211 | 0.063982 | -6.8985 | 0.14648 | -22.0139 | -1.8539 | 0.19684 | -116.3635 | -116.4963 | 4.2297 | -0.073242 | 2.4902 | 4.5456 | 4.4907 | -116.391 | -116.3406 | 0.022889 | -0.10986 | -4.6463 | 116.5329 | 114.5325 | 114.6423 | -11.7416 | -0.004577 | 0.045777 | -0.29755 | 120.6162 | 118.8766 | 118.8309 | -0.35248 | 116.5833 | 109.4879 | 94.3726 | -121.3394 | 120.932 | 120.8771 | 116.3132 | -121.1838
1746.6406 | 121.4035 | -116.2354 | 4.9667 | -0.17959 | 0.0028272 | 0.011154 | 0.37357 | 0.076896 | 0.63174 | -0.040284 | -0.039353 | 4.0327 | 0.032762 | 0.080848 | 3.2132 | 0.062914 | -6.9992 | 0.15564 | -22.3068 | -2.1194 | 0.19226 | -116.153 | -116.2994 | 4.2297 | 0.20142 | 2.4857 | 4.7104 | 4.6188 | -116.2399 | -116.2033 | 0.082398 | -0.064086 | -4.7745 | 116.391 | 114.1159 | 114.18 | -11.9659 | -0.004577 | 0.032044 | -0.25635 | 120.4651 | 118.721 | 118.689 | -0.3479 | 116.4276 | 109.2361 | 93.9285 | -121.2662 | 120.9457 | 120.8542 | 116.4368 | -121.17
1747.6406 | 121.431 | -116.2491 | 4.9484 | 0.049296 | 0.015645 | 0.0036769 | 0.37036 | 0.072623 | 0.62853 | -0.033876 | -0.024094 | 4.0295 | 0.03917 | 0.084052 | 3.2121 | 0.05971 | -6.958 | 0.16479 | -22.1878 | -2.2705 | 0.20599 | -116.2445 | -116.3086 | 4.3625 | -0.018311 | 2.6367 | 4.6875 | 4.6234 | -116.2537 | -116.1896 | 0.004577 | -0.05951 | -4.7424 | 116.4139 | 113.9786 | 114.0381 | -11.9064 | -0.004578 | 0.059509 | -0.26093 | 120.6116 | 118.8858 | 118.8263 | -0.32501 | 116.4551 | 109.2911 | 94.0613 | -121.257 | 120.9366 | 120.8725 | 116.2308 | -121.138
1748.6406 | 121.4172 | -116.2491 | 4.953 | -0.27114 | 0.025258 | 0.037857 | 0.38211 | 0.072623 | 0.6499 | -0.043489 | -0.024094 | 4.0359 | 0.030626 | 0.086188 | 3.2068 | 0.05971 | -7.0129 | 0.07782 | -22.3251 | -2.5635 | 0.18768 | -116.2445 | -116.3727 | 4.3213 | -0.036621 | 2.6001 | 4.6692 | 4.6005 | -116.272 | -116.2354 | 0.004577 | -0.1236 | -4.7653 | 116.3269 | 113.6856 | 113.8092 | -11.9659 | -0.022889 | 0.013732 | -0.28381 | 120.5704 | 118.8492 | 118.8355 | -0.35248 | 116.4368 | 109.2361 | 93.9239 | -121.3257 | 120.9183 | 120.8496 | 116.2125 | -121.1884
1749.6406 | 121.4264 | -116.5375 | 4.6555 | -0.2101 | 0.013508 | 0.014358 | 0.36609 | 0.072623 | 0.64135 | -0.039216 | 3.3634 | 4.0412 | 0.030626 | 0.084052 | 3.2185 | 0.067187 | -6.9717 | 0.15106 | -22.3709 | -1.9867 | 0.20599 | -116.5604 | -116.7023 | 4.0466 | -0.073242 | 2.3392 | 4.3808 | 4.3076 | -116.5878 | -116.5283 | -0.022888 | -0.16479 | -4.4495 | 116.6885 | 114.5508 | 114.7156 | -11.6272 | -0.050354 | 0.009156 | -0.27466 | 120.5841 | 118.8766 | 118.8675 | -0.3479 | 116.7435 | 109.5657 | 94.1666 | -121.3577 | 120.9183 | 120.845 | 116.4642 | -121.1838
1750.6406 | 121.4355 | -116.6199 | 4.5822 | -0.22536 | 0.015645 | 0.0079499 | 0.37784 | 0.086509 | 0.63494 | -0.038148 | -0.10039 | 4.0327 | 0.045579 | 0.084052 | 3.1972 | 0.068255 | -6.9077 | 0.16022 | -22.4991 | -2.3804 | 0.20142 | -116.5878 | -116.6885 | 3.9963 | -0.068665 | 2.3575 | 4.3213 | 4.2435 | -116.6428 | -116.5924 | 0.032043 | -0.068665 | -4.3808 | 116.7801 | 114.2395 | 114.3082 | -11.4899 | -0.022888 | 0.027466 | -0.26092 | 120.6162 | 118.9774 | 118.9499 | -0.33874 | 116.8213 | 109.7122 | 94.1208 | -121.2708 | 120.9412 | 120.8633 | 116.5512 | -121.1746
1751.6406 | 121.4447 | -116.185 | 5.04 | -0.2864 | 0.0017592 | 0.014358 | 0.35755 | 0.072623 | 0.63067 | -0.043489 | -0.06987 | 4.0359 | 0.037034 | 0.081916 | 3.2068 | 0.066119 | -6.8573 | 0.1831 | -22.2977 | -2.3026 | 0.21057 | -116.1255 | -116.2582 | 4.4128 | -0.041199 | 2.6962 | 4.7653 | 4.6738 | -116.1942 | -116.1438 | 0.05951 | -0.073242 | -4.8294 | 116.3681 | 113.8824 | 113.9557 | -11.8973 | -0.009155 | 0.041199 | -0.27466 | 120.5978 | 118.8812 | 118.84 | -0.36621 | 116.3956 | 109.3277 | 93.8873 | -121.2982 | 120.9503 | 120.8588 | 116.1438 | -121.1838
1752.6406 | 121.431 | -116.2537 | 4.9484 | -0.22536 | 0.013508 | 0.0047449 | 0.36502 | 0.077964 | 0.6296 | -0.036012 | -0.75652 | 4.0316 | 0.034898 | 0.095801 | 3.2014 | 0.057574 | -7.1228 | 0.26093 | -22.0642 | -1.9455 | 0.19684 | -116.2354 | -116.3498 | 4.3442 | -0.054932 | 2.5955 | 4.6646 | 4.6371 | -116.2857 | -116.2445 | 0.01831 | -0.09613 | -4.7516 | 116.5146 | 114.3082 | 114.4043 | -12.0712 | -0.032044 | 0.009155 | -0.28381 | 120.5978 | 118.8492 | 118.84 | -0.31128 | 116.4505 | 109.1309 | 94.1895 | -121.2982 | 120.9183 | 120.8908 | 116.1987 | -121.1929
1753.6406 | 121.4813 | -116.1896 | 5.0171 | 0.12559 | -0.0057178 | 0.015426 | 0.37036 | 0.089713 | 0.64135 | -0.039216 | 0.37263 | 4.0348 | 0.028489 | 0.090461 | 3.2132 | 0.05971 | -6.839 | 0.16479 | -22.1191 | -2.0462 | 0.21057 | -116.1758 | -116.3086 | 4.4449 | -0.050354 | 2.6962 | 4.715 | 4.6509 | -116.2262 | -116.1758 | 0.013733 | -0.11902 | -4.8065 | 116.3544 | 114.1434 | 114.2624 | -11.8561 | -0.036621 | 0.013733 | -0.30212 | 120.6345 | 118.8858 | 118.8721 | -0.36621 | 116.4001 | 109.3506 | 94.0704 | -121.3257 | 120.9045 | 120.8405 | 116.1392 | -121.1929
1754.6406 | 121.4401 | -116.1438 | 5.0858 | 0.11033 | -0.0046498 | 0.010086 | 0.38104 | 0.08544 | 0.62319 | -0.046693 | 0.097976 | 4.0306 | 0.041307 | 0.087256 | 3.2004 | 0.071459 | -6.8344 | 0.14191 | -22.1603 | -1.8631 | 0.2243 | -116.0751 | -116.185 | 4.509 | -0.073242 | 2.7145 | 4.8203 | 4.7516 | -116.1163 | -116.0568 | 0.068665 | -0.041199 | -4.8614 | 116.2857 | 114.2807 | 114.3219 | -11.9202 | 0.027466 | 0.086975 | -0.2655 | 120.6528 | 118.8583 | 118.7714 | -0.33417 | 116.3681 | 109.3094 | 93.9835 | -121.2708 | 120.9641 | 120.8954 | 116.0706 | -121.1426
1755.6406 | 121.4264 | -116.2994 | 4.8935 | 0.17137 | 0.01244 | 0.0068819 | 0.37143 | 0.0801 | 0.63387 | -0.043489 | 0.067459 | 4.0498 | 0.042375 | 0.090461 | 3.2036 | 0.063982 | -6.8207 | 0.16937 | -22.6456 | -1.973 | 0.19684 | -116.2766 | -116.3956 | 4.3167 | -0.022888 | 2.6413 | 4.6051 | 4.5593 | -116.3132 | -116.2628 | 0.022888 | -0.096131 | -4.6967 | 116.4688 | 114.3265 | 114.4226 | -11.7142 | -0.013733 | 0.036621 | -0.28839 | 120.6161 | 118.9407 | 118.9041 | -0.33417 | 116.4963 | 109.4788 | 93.6539 | -121.2891 | 120.9045 | 120.8588 | 116.2766 | -121.1563
1756.6406 | 121.4493 | -116.2537 | 4.9759 | -0.10329 | -0.020671 | 0.0047449 | 0.3725 | 0.076896 | 0.62853 | -0.030671 | 0.3116 | 4.0391 | 0.059465 | 0.084052 | 3.2078 | 0.062914 | -6.8527 | 0.12817 | -22.8012 | -2.1469 | 0.2243 | -116.217 | -116.3361 | 4.3991 | -0.013733 | 2.7328 | 4.6829 | 4.6143 | -116.2766 | -116.2079 | 0.036621 | -0.082398 | -4.7516 | 116.3818 | 114.1068 | 114.1891 | -11.8286 | -0.022888 | 0.045776 | -0.29297 | 120.6528 | 118.9865 | 118.9407 | -0.36163 | 116.478 | 109.4009 | 93.4525 | -121.312 | 120.9366 | 120.8679 | 116.2399 | -121.1838
1757.6875 | 121.3806 | -116.3727 | 4.8843 | 0.53758 | 0.0028272 | 0.010086 | 0.36395 | 0.066214 | 0.64669 | -0.03708 | 0.54048 | 4.0455 | 0.048783 | 0.089393 | 3.2046 | 0.067187 | -6.8619 | 0.09613 | -22.7829 | -2.0508 | 0.21515 | -116.2857 | -116.4185 | 4.2572 | -0.13275 | 2.5269 | 4.6097 | 4.5593 | -116.3361 | -116.3177 | 0.086975 | -0.045776 | -4.6692 | 116.4688 | 114.3219 | 114.3677 | -11.7462 | 0.036621 | 0.054932 | -0.27466 | 120.6299 | 118.8995 | 118.8446 | -0.32501 | 116.5878 | 109.5108 | 93.5898 | -121.3028 | 120.9824 | 120.932 | 116.2399 | -121.2021
1758.6406 | 121.4264 | -116.4001 | 4.7974 | -0.17959 | 0.015645 | 0.034653 | 0.37143 | 0.082236 | 0.63387 | -0.032808 | -0.024094 | 4.0487 | 0.024217 | 0.087256 | 3.2014 | 0.055437 | -6.8436 | 0.15106 | -22.4396 | -1.8906 | 0.20599 | -116.3818 | -116.5054 | 4.1885 | -0.027466 | 2.504 | 4.5136 | 4.4266 | -116.4551 | -116.3727 | 0.01831 | -0.10529 | -4.5914 | 116.5512 | 114.5096 | 114.6149 | -11.6409 | -0.054932 | 0.027465 | -0.28381 | 120.5887 | 118.9041 | 118.8766 | -0.37079 | 116.6061 | 109.5566 | 93.9606 | -121.3028 | 120.9137 | 120.8267 | 116.3727 | -121.17
1759.6406 | 121.4355 | -116.2582 | 4.9622 | 0.064555 | 0.0038952 | 0.01329 | 0.37036 | 0.076896 | 0.63922 | -0.050966 | -0.054612 | 4.0306 | 0.037034 | 0.089393 | 3.2004 | 0.062914 | -6.8481 | 0.1831 | -22.6181 | -2.1423 | 0.23346 | -116.2125 | -116.3086 | 4.3671 | -0.036621 | 2.4902 | 4.6875 | 4.6417 | -116.272 | -116.2399 | 0.045777 | -0.050354 | -4.7287 | 116.4413 | 114.1159 | 114.1663 | -11.8103 | -0.013733 | 0.018311 | -0.27466 | 120.6253 | 118.7485 | 118.7302 | -0.32043 | 116.4917 | 109.4101 | 93.6401 | -121.2708 | 120.9457 | 120.9 | 116.2216 | -121.2021
1760.6406 | 121.3623 | -116.4505 | 4.747 | 0.3087 | 0.0049632 | 0.0090179 | 0.36289 | 0.076896 | 0.63174 | -0.044557 | 0.35738 | 4.0391 | 0.046647 | 0.092597 | 3.1993 | 0.071459 | -6.871 | 0.073242 | -22.9111 | -2.1011 | 0.20599 | -116.3681 | -116.51 | 4.1565 | -0.33417 | 2.179 | 4.5136 | 4.4312 | -116.51 | -116.4368 | 0.082397 | -0.05951 | -4.541 | 116.5237 | 114.3494 | 114.4089 | -11.618 | -0.05951 | 0.013732 | -0.23346 | 120.607 | 118.6295 | 118.6157 | -0.31586 | 116.6565 | 109.5795 | 93.5394 | -121.257 | 120.9641 | 120.8817 | 116.1163 | -121.1838
1761.6406 | 121.4172 | -97.6135 | 23.5794 | 0.84275 | -0.0078538 | 0.015426 | 0.36609 | 0.059806 | 0.52706 | -0.043489 | 0.35738 | 3.912 | 0.048783 | 0.094733 | 3.2004 | 0.069323 | -6.0242 | 0.073242 | -19.1437 | -2.5452 | 0.20142 | -98.0118 | -98.1308 | 22.998 | 0.004578 | 21.2311 | 23.172 | 23.1216 | -97.6868 | -97.6089 | -0.39826 | -0.51727 | -23.378 | 97.6868 | 95.0684 | 95.5856 | -29.6036 | -0.073243 | 0.004577 | -0.40741 | 120.6116 | 118.8446 | 118.84 | -0.45776 | 97.8149 | 91.5894 | 78.4698 | -121.7102 | 120.7855 | 120.7352 | 97.6181 | -121.1884
1762.6406 | 121.4584 | -97.2107 | 23.9868 | 0.12559 | -0.0067858 | 0.016495 | 0.37036 | 0.061942 | 0.53134 | -0.030671 | 0.22005 | 3.9099 | 0.035966 | 0.091529 | 3.1982 | 0.061846 | -5.9601 | 0.11444 | -18.782 | -2.3163 | 0.2243 | -97.2015 | -97.3068 | 23.497 | 0.041199 | 21.9315 | 23.7579 | 23.6572 | -97.1466 | -97.1329 | 0.009155 | -0.096131 | -23.7625 | 97.3251 | 94.8944 | 94.9905 | -29.9469 | 0.064087 | 0.077819 | -0.22888 | 120.7077 | 119.1422 | 119.0643 | -0.32959 | 97.435 | 91.2506 | 78.4287 | -121.2936 | 120.9686 | 120.8679 | 97.2519 | -121.1197
1763.6406 | 121.4355 | -116.6656 | 4.541 | -0.27114 | 0.014576 | 0.017563 | 0.37036 | 0.079032 | 0.62319 | -0.023195 | 0.38789 | 4.0412 | 0.038102 | 0.092597 | 3.21 | 0.052233 | -6.8298 | 0.041199 | -22.6318 | -2.536 | 0.19684 | -116.684 | -116.7755 | 3.923 | -0.064087 | 2.1469 | 4.2664 | 4.1931 | -116.716 | -116.6519 | -0.018311 | -0.10986 | -4.3442 | 116.7068 | 114.1296 | 114.2395 | -11.3709 | -0.050354 | 0.013732 | -0.27466 | 120.5887 | 118.8126 | 118.7988 | -0.3479 | 116.8625 | 109.8358 | 94.0338 | -121.3165 | 120.932 | 120.8588 | 116.6016 | -121.1929
1764.6406 | 121.4264 | -116.5741 | 4.6188 | 0.18663 | -0.0035808 | 0.0090179 | 0.36609 | 0.06301 | 0.62106 | -0.033876 | 0.036941 | 4.037 | 0.030626 | 0.087256 | 3.195 | 0.054369 | -6.8802 | 0.091553 | -22.4442 | -2.1469 | 0.22888 | -116.5695 | -116.716 | 4.0192 | -0.068665 | 2.2247 | 4.3533 | 4.2938 | -116.6199 | -116.5649 | 0.004578 | -0.14191 | -4.39 | 116.6656 | 114.4272 | 114.5691 | -11.499 | -0.045776 | 0.009156 | -0.2655 | 120.5933 | 118.7988 | 118.7897 | -0.32501 | 116.803 | 109.6939 | 94.1299 | -121.3348 | 120.9274 | 120.8679 | 116.5054 | -121.1838
1765.6406 | 121.4722 | -116.217 | 4.985 | -0.042256 | -0.0078538 | 0.0068819 | 0.36609 | 0.082236 | 0.62213 | -0.036012 | 0.14375 | 4.0263 | 0.03917 | 0.089393 | 3.2036 | 0.066119 | -6.8344 | 0.14191 | -22.4899 | -2.4033 | 0.21973 | -116.1987 | -116.3086 | 4.4403 | -0.091553 | 2.5955 | 4.7287 | 4.6417 | -116.2445 | -116.1758 | 0.018311 | -0.091553 | -4.7653 | 116.3589 | 113.8138 | 113.9053 | -11.8195 | -0.027466 | 0.041199 | -0.25635 | 120.6573 | 118.8126 | 118.7714 | -0.34332 | 116.4368 | 109.3826 | 93.7271 | -121.2936 | 120.9457 | 120.8588 | 116.1255 | -121.1609
1766.6406 | 121.4813 | -116.5009 | 4.7104 | 0.14085 | 0.02419 | 0.016495 | 0.36609 | 0.070487 | 0.63067 | -0.038148 | 0.036941 | 4.0316 | 0.044511 | 0.10114 | 3.1908 | 0.066119 | -6.8985 | 0.1236 | -22.4258 | -2.1927 | 0.21515 | -116.4917 | -116.6107 | 4.1428 | -0.068665 | 2.2614 | 4.4586 | 4.3945 | -116.5283 | -116.4505 | 0.009155 | -0.10986 | -4.4952 | 116.6245 | 114.3082 | 114.418 | -11.6089 | -0.027466 | 0.050354 | -0.25177 | 120.6436 | 118.7622 | 118.7119 | -0.31586 | 116.716 | 109.6024 | 94.075 | -121.3211 | 120.9595 | 120.8954 | 116.4322 | -121.1609
1767.6406 | 121.4355 | -115.773 | 5.4749 | 0.38499 | 0.0017592 | 0.012222 | 0.36289 | 0.071555 | 0.6264 | -0.03708 | 1.1051 | 4.021 | 0.041307 | 0.089393 | 3.2004 | 0.061846 | -6.8802 | 0.059509 | -22.1146 | -2.1332 | 0.21515 | -115.7181 | -115.8554 | 4.8203 | -0.16022 | 2.9297 | 5.1453 | 5.1132 | -115.773 | -115.7455 | 0.054931 | -0.082398 | -5.2597 | 115.8325 | 113.6398 | 113.7222 | -12.355 | 0 | 0.027466 | -0.32959 | 120.5933 | 118.7027 | 118.6752 | -0.36163 | 115.9882 | 108.8928 | 93.6584 | -121.3303 | 120.9183 | 120.8862 | 115.6128 | -121.2204
1768.6406 | 121.3989 | -115.9515 | 5.2597 | 0.21714 | -0.00037681 | 0.01329 | 0.36182 | 0.068351 | 0.62106 | -0.041353 | 0.40315 | 4.021 | 0.043443 | 0.081916 | 3.2046 | 0.070391 | -6.8619 | 0.07782 | -22.0276 | -2.4399 | 0.20142 | -115.8691 | -115.9607 | 4.6829 | -0.14648 | 2.7374 | 5.0446 | 4.9805 | -116.0385 | -115.9378 | 0.082397 | -0.009155 | -5.0583 | 116.0294 | 113.5117 | 113.5208 | -12.1216 | -0.086975 | 0.013733 | -0.21515 | 120.6345 | 118.689 | 118.6752 | -0.27924 | 116.153 | 109.0897 | 93.9239 | -121.2204 | 120.9961 | 120.932 | 115.8051 | -121.1975
1769.6406 | 121.3943 | -115.8005 | 5.397 | 0.62913 | 0.0028272 | 0.0068819 | 0.35648 | 0.077964 | 0.61999 | -0.052034 | 0.29634 | 4.0327 | 0.021012 | 0.091529 | 3.2014 | 0.063982 | -6.8939 | 0.064087 | -22.2702 | -1.9592 | 0.19226 | -115.8005 | -115.9012 | 4.7791 | -0.10071 | 3.0212 | 5.127 | 5.0674 | -115.8463 | -115.7684 | 0 | -0.10071 | -5.2048 | 115.8646 | 113.8412 | 113.942 | -12.291 | -0.045776 | 0.032043 | -0.27008 | 120.5795 | 118.8217 | 118.7897 | -0.32959 | 115.9927 | 108.9066 | 93.5303 | -121.2982 | 120.9274 | 120.8679 | 115.6998 | -121.1655
1770.6406 | 121.4127 | -116.0202 | 5.2094 | 0.26292 | 0.00069119 | 0.020767 | 0.37036 | 0.073691 | 0.63494 | -0.039216 | 0.43367 | 4.0231 | 0.021012 | 0.090461 | 3.1982 | 0.066119 | -7.196 | -0.045776 | -22.7097 | -2.1881 | 0.16937 | -116.0339 | -116.1575 | 4.5868 | -0.12817 | 2.7832 | 4.9393 | 4.8752 | -116.0202 | -115.979 | -0.013733 | -0.13733 | -5.04 | 115.9744 | 113.8321 | 113.9694 | -12.4054 | 0 | 0.041199 | -0.27008 | 120.607 | 118.8034 | 118.7622 | -0.33417 | 116.1896 | 108.8242 | 93.3105 | -121.3669 | 120.9595 | 120.8954 | 115.892 | -121.1884
1771.6875 | 121.3806 | -115.9149 | 5.3055 | 0.50706 | 0.026326 | 0.018631 | 0.37143 | 0.076896 | 0.63494 | -0.034944 | 0.35738 | 4.0348 | 0.032762 | 0.095801 | 3.1993 | 0.070391 | -6.8527 | 0.07782 | -22.7554 | -2.1057 | 0.20599 | -115.8829 | -116.0156 | 4.6921 | -0.14191 | 2.8519 | 5.0354 | 4.9667 | -115.9332 | -115.8875 | 0.032043 | -0.10071 | -5.0995 | 115.9927 | 113.8092 | 113.9099 | -12.1582 | -0.018311 | 0.027466 | -0.27008 | 120.607 | 118.7668 | 118.7393 | -0.33875 | 116.1209 | 109.0622 | 93.1595 | -121.3211 | 120.9503 | 120.8817 | 115.773 | -121.1929
1772.6406 | 121.431 | -115.9927 | 5.2139 | 0.14085 | 0.0081682 | 0.017563 | 0.37036 | 0.077964 | 0.62747 | -0.025331 | 0.14375 | 4.0295 | 0.024217 | 0.089393 | 3.1961 | 0.070391 | -6.9122 | 0.086975 | -22.673 | -2.0279 | 0.2243 | -115.9836 | -116.1301 | 4.5959 | -0.10071 | 2.742 | 4.9438 | 4.8569 | -116.0248 | -115.9927 | 0.009155 | -0.13733 | -4.9896 | 116.0797 | 113.9648 | 114.1022 | -12.1262 | -0.032043 | 0 | -0.27008 | 120.5887 | 118.7347 | 118.7347 | -0.35705 | 116.217 | 109.0805 | 93.3197 | -121.344 | 120.9366 | 120.8496 | 115.892 | -121.2067
1773.6406 | 121.3989 | -115.9698 | 5.2734 | 1.8498 | 0.0092362 | 0.019699 | 0.36182 | 0.084372 | 0.63281 | -0.040284 | 0.3116 | 4.0188 | 0.03383 | 0.093665 | 3.1972 | 0.068255 | -6.926 | 0.054932 | -22.6364 | -2.0599 | 0.19226 | -115.9332 | -116.0751 | 4.6509 | -0.1236 | 2.7786 | 4.9988 | 4.9301 | -115.9927 | -115.9515 | 0.036621 | -0.10529 | -5.0812 | 116.0248 | 113.9099 | 114.0152 | -12.1994 | -0.022888 | 0.018311 | -0.27466 | 120.6207 | 118.7485 | 118.7302 | -0.34332 | 116.1621 | 109.0439 | 93.3334 | -121.3486 | 120.9686 | 120.9 | 115.8463 | -121.225
1774.6406 | 121.3989 | -115.9973 | 5.2277 | 0.55284 | 0.0071002 | 0.028244 | 0.36823 | 0.095053 | 0.62853 | -0.039216 | 0.34212 | 4.0242 | 0.046647 | 0.088325 | 3.2004 | 0.061846 | -6.8939 | 0.073242 | -22.6456 | -2.0691 | 0.19226 | -115.9607 | -116.0614 | 4.5868 | -0.14191 | 2.7512 | 4.953 | 4.8935 | -116.0156 | -115.9882 | 0.036621 | -0.064087 | -5.0354 | 116.0706 | 113.9282 | 113.9923 | -12.1216 | -0.018311 | 0.009155 | -0.27466 | 120.5841 | 118.7485 | 118.7393 | -0.33417 | 116.1896 | 109.1034 | 93.3517 | -121.2891 | 120.9503 | 120.8908 | 115.8554 | -121.2158
1775.6406 | 121.4447 | -116.0889 | 5.1224 | 0.32395 | 0.00069119 | 0.0068819 | 0.35755 | 0.083304 | 0.63601 | -0.031739 | 0.28108 | 4.021 | 0.032762 | 0.076575 | 3.1897 | 0.069323 | -7.0267 | 0.068665 | -22.6273 | -2.0142 | 0.20142 | -116.0248 | -116.1392 | 4.2572 | -0.20599 | 2.6505 | 4.8386 | 4.7882 | -116.1209 | -116.066 | 0.064087 | -0.050354 | -4.921 | 116.1575 | 114.0747 | 114.1251 | -12.149 | -0.032044 | 0.022888 | -0.28381 | 120.3461 | 118.7393 | 118.7164 | -0.33417 | 116.2903 | 109.0622 | 93.4616 | -121.2616 | 120.9274 | 120.8771 | 115.8829 | -121.1884
1776.6406 | 121.4172 | -115.8966 | 5.3558 | 0.17137 | 0.010304 | 0.016495 | 0.36716 | 0.070487 | 0.6264 | -0.027467 | 0.35738 | 4.0274 | 0.034898 | 0.097938 | 3.1972 | 0.062914 | -7.3883 | 0.07782 | -22.5906 | -2.0187 | 0.21973 | -115.86 | -115.9653 | 4.6921 | -0.15564 | 2.8336 | 5.0674 | 4.9988 | -115.9149 | -115.8646 | 0.036621 | -0.068665 | -5.1361 | 115.9744 | 113.8779 | 113.9465 | -12.7441 | -0.018311 | 0.032043 | -0.28839 | 120.5887 | 118.7302 | 118.6981 | -0.35706 | 116.1163 | 108.5083 | 93.306 | -121.3211 | 120.9641 | 120.8954 | 115.741 | -121.2204
1777.6406 | 121.4127 | -115.8325 | 5.4245 | 0.2324 | 0.0071002 | 0.012222 | 0.36075 | 0.081168 | 0.62747 | -0.031739 | 0.22005 | 4.0306 | 0.043443 | 0.092597 | 3.1908 | 0.062914 | -7.4982 | -0.064087 | -22.3251 | -2.1423 | 0.15106 | -115.8417 | -115.9653 | 4.7745 | -0.14191 | 3.0029 | 5.1407 | 5.0858 | -115.8096 | -115.7913 | -0.009155 | -0.13275 | -5.2734 | 115.7684 | 113.6902 | 113.8229 | -12.9227 | 0.022889 | 0.041199 | -0.28381 | 120.607 | 118.8355 | 118.7943 | -0.33875 | 115.9836 | 108.3344 | 93.5074 | -121.3898 | 120.9732 | 120.9183 | 115.6906 | -121.2158
1778.6406 | 121.3852 | -115.6723 | 5.5389 | 0.52232 | 0.0081682 | 0.00047294 | 0.38425 | 0.075827 | 0.62853 | -0.036012 | 0.40315 | 4.022 | 0.037034 | 0.096869 | 3.2078 | 0.071459 | -7.2281 | 0.091553 | -22.7783 | -2.243 | 0.21973 | -115.6448 | -115.773 | 4.9026 | -0.15564 | 3.0258 | 5.2597 | 5.1956 | -115.7135 | -115.654 | 0.027466 | -0.10071 | -5.3192 | 115.7639 | 113.4293 | 113.53 | -12.767 | -0.041199 | 0.01831 | -0.27923 | 120.575 | 118.6981 | 118.6798 | -0.34332 | 115.892 | 108.4442 | 92.894 | -121.3119 | 120.932 | 120.8679 | 115.5167 | -121.1929
1779.6406 | 121.3943 | -115.9012 | 5.3558 | 0.38499 | 0.0028272 | 0.016495 | 0.37143 | 0.079032 | 0.63174 | -0.044557 | 0.37263 | 4.021 | 0.053056 | 0.10114 | 3.1972 | 0.058642 | -7.1411 | 0.059509 | -22.6913 | -2.1744 | 0.21057 | -115.8279 | -115.9561 | 4.7195 | -0.15564 | 2.8885 | 5.0858 | 5.0308 | -115.9103 | -115.8508 | 0.073242 | -0.054932 | -5.1453 | 115.9607 | 113.7268 | 113.7817 | -12.4969 | -0.009155 | 0.050354 | -0.27008 | 120.6207 | 118.7897 | 118.7393 | -0.32501 | 116.1118 | 108.7601 | 93.2098 | -121.312 | 120.9869 | 120.932 | 115.7455 | -121.2067
1780.6406 | 121.4172 | -116.2125 | 5.0491 | 0.47654 | 0.0049632 | 0.018631 | 0.35755 | 0.074759 | 0.63494 | -0.03708 | 0.32686 | 4.0338 | 0.040239 | 0.088325 | 3.2014 | 0.061846 | -7.1777 | 0.07782 | -22.9935 | -2.5497 | 0.21973 | -116.1804 | -116.2857 | 4.39 | -0.16022 | 2.6001 | 4.7791 | 4.6967 | -116.2216 | -116.1621 | 0.032043 | -0.073243 | -4.8294 | 116.2903 | 113.6627 | 113.736 | -12.2269 | -0.009156 | 0.050354 | -0.27008 | 120.6024 | 118.8126 | 118.7622 | -0.35248 | 116.4322 | 109.0347 | 93.219 | -121.3348 | 120.9915 | 120.9091 | 116.0522 | -121.2112
1781.6406 | 121.3715 | -116.3544 | 4.9438 | -0.16433 | 0.026326 | 0.0058129 | 0.36395 | 0.08544 | 0.66271 | -0.024263 | -0.23772 | 4.0338 | 0.028489 | 0.081916 | 3.211 | 0.052233 | -7.1411 | 0.018311 | -23.1445 | -2.3483 | 0.23346 | -116.3315 | -116.4368 | 4.2435 | -0.17395 | 2.4536 | 4.66 | 4.6051 | -116.3818 | -116.3223 | 0.022888 | -0.082398 | -4.7104 | 116.3727 | 114.006 | 114.0884 | -12.085 | -0.027466 | 0.032043 | -0.28381 | 120.5978 | 118.808 | 118.7759 | -0.33875 | 116.5878 | 109.2133 | 93.2098 | -121.3806 | 121.0144 | 120.9595 | 116.1804 | -121.2662
1782.6406 | 121.4493 | -116.1896 | 5.0674 | 0.43077 | 0.025258 | 0.020767 | 0.35861 | 0.083304 | 0.63174 | -0.038148 | 0.571 | 4.0338 | 0.03917 | 0.096869 | 3.1897 | 0.069323 | -7.1091 | 0.10986 | -23.0988 | -2.1881 | 0.21057 | -116.1301 | -116.2674 | 4.4266 | -0.14648 | 2.6047 | 4.7836 | 4.7058 | -116.1896 | -116.1438 | 0.059509 | -0.07782 | -4.8569 | 116.2994 | 114.0015 | 114.0793 | -12.1765 | 0 | 0.045776 | -0.28381 | 120.6162 | 118.7943 | 118.7485 | -0.36163 | 116.4001 | 109.0805 | 93.0908 | -121.3348 | 120.9732 | 120.8954 | 116.0431 | -121.2112
1783.6406 | 121.4035 | -116.1804 | 5.0217 | 0.47654 | 0.010304 | 0.0036769 | 0.37677 | 0.0801 | 0.62426 | -0.036012 | 0.64729 | 4.0359 | 0.034898 | 0.099006 | 3.2014 | 0.069323 | -7.0908 | 0.1236 | -22.8836 | -2.3529 | 0.20599 | -116.1575 | -116.272 | 4.4266 | -0.13733 | 2.5497 | 4.7287 | 4.6921 | -116.2125 | -116.185 | 0.022888 | -0.091553 | -4.8157 | 116.304 | 113.8275 | 113.9191 | -12.1124 | -0.032043 | -0.004578 | -0.29297 | 120.607 | 118.7302 | 118.7347 | -0.32959 | 116.3864 | 109.0897 | 93.2968 | -121.2936 | 120.9091 | 120.8725 | 116.0431 | -121.2067
1784.6406 | 121.4035 | -116.0889 | 5.1086 | 0.67491 | 0.023121 | 0.012222 | 0.36609 | 0.076896 | 0.63174 | -0.027467 | 0.63203 | 4.022 | 0.037034 | 0.088325 | 3.1993 | 0.061846 | -7.0175 | 0.1236 | -23.0072 | -1.9363 | 0.19684 | -116.0797 | -116.1804 | 4.5502 | -0.20599 | 2.6596 | 4.8614 | 4.7928 | -116.1301 | -116.066 | 0.009155 | -0.091553 | -4.9118 | 116.2125 | 114.1525 | 114.2441 | -12.1262 | -0.041199 | 0.022888 | -0.24719 | 120.639 | 118.7485 | 118.7256 | -0.31586 | 116.2857 | 109.0713 | 93.0817 | -121.2891 | 120.9503 | 120.8817 | 115.8829 | -121.1746
1785.6406 | 121.4218 | -116.185 | 5.0354 | 2.628 | 0.034871 | 0.017563 | 0.38104 | 0.086509 | 0.64456 | -0.032808 | 0.64729 | 4.0327 | 0.040239 | 0.10328 | 3.2078 | 0.05971 | -6.9763 | 0.091553 | -22.6456 | -1.918 | 0.16479 | -116.153 | -116.2674 | 4.454 | -0.21515 | 2.6642 | 4.7699 | 4.7104 | -116.2033 | -116.1484 | 0.032044 | -0.082397 | -4.8706 | 116.2766 | 114.267 | 114.3494 | -12.0117 | -0.01831 | 0.036622 | -0.2655 | 120.639 | 118.8492 | 118.8126 | -0.32501 | 116.3498 | 109.2087 | 93.5394 | -121.3028 | 120.9549 | 120.8954 | 115.9698 | -121.1838
1786.6406 | 121.2982 | -116.1942 | 5.1224 | -0.24062 | 0.015645 | 0.0068819 | 0.37464 | 0.079032 | 0.65417 | -0.033876 | -0.31401 | 4.0316 | 0.058397 | 0.10114 | 3.1918 | 0.058642 | -7.1182 | -0.009155 | -22.6639 | -2.1149 | 0.25635 | -116.1713 | -116.2994 | 4.4769 | 0.036621 | 2.4948 | 4.8706 | 4.7928 | -116.2262 | -116.1392 | 0.022888 | -0.10528 | -4.866 | 116.185 | 114.0793 | 114.1846 | -12.2406 | -0.032043 | 0.054932 | -0.25177 | 120.6711 | 118.689 | 118.634 | -0.32959 | 116.4505 | 109.0759 | 93.5303 | -121.4218 | 121.0648 | 120.9869 | 116.2308 | -121.2616
1787.6406 | 121.4767 | -116.2582 | 4.9576 | 0.55284 | 0.028462 | 0.0047449 | 0.36289 | 0.082236 | 0.64028 | -0.03708 | 0.571 | 4.0231 | 0.062669 | 0.11075 | 3.2303 | 0.067187 | -7.196 | 0.11444 | -22.9889 | -2.1194 | 0.19684 | -116.1987 | -116.3498 | 4.2938 | -0.027466 | 2.6505 | 4.6738 | 4.5914 | -116.304 | -116.2399 | 0.05951 | -0.091552 | -4.7607 | 116.3727 | 114.1388 | 114.2303 | -12.1536 | -0.045776 | 0.018311 | -0.28381 | 120.5521 | 118.9087 | 118.8904 | -0.36621 | 116.4551 | 109.0622 | 93.2693 | -121.3074 | 120.932 | 120.8496 | 116.2308 | -121.1975
1788.6406 | 121.4035 | -116.1346 | 5.0858 | 0.72068 | 0.019917 | 0.0026089 | 0.37464 | 0.076896 | 0.64028 | -0.027467 | 0.67781 | 4.0252 | 0.042375 | 0.091529 | 3.2121 | 0.068255 | -7.1091 | 0.11444 | -23.085 | -2.2568 | 0.19226 | -116.0156 | -116.1713 | 4.5776 | -0.21973 | 2.8152 | 4.8706 | 4.8065 | -116.1118 | -116.0339 | 0.11902 | -0.036621 | -4.8935 | 116.2491 | 113.8779 | 113.9145 | -12.1948 | 0.022889 | 0.10071 | -0.21515 | 120.7123 | 118.9499 | 118.8492 | -0.27923 | 116.3269 | 109.0256 | 93.0496 | -121.257 | 121.0052 | 120.9412 | 115.9149 | -121.1197
1789.6406 | 121.4264 | -116.1713 | 5.0491 | 0.52232 | 0.028462 | 0.0026089 | 0.36182 | 0.0801 | 0.64349 | -0.040284 | 0.43367 | 4.0252 | 0.034898 | 0.10114 | 3.211 | 0.067187 | -7.1503 | 0.19226 | -23.2956 | -2.2064 | 0.14648 | -116.1346 | -116.2537 | 4.4724 | -0.21515 | 2.7008 | 4.7745 | 4.7287 | -116.1987 | -116.1484 | 0.036621 | -0.082397 | -4.9026 | 116.3635 | 113.9648 | 114.0472 | -12.1994 | -0.027465 | 0.022889 | -0.27466 | 120.6436 | 118.8721 | 118.8492 | -0.32043 | 116.3177 | 109.021 | 92.8757 | -121.3028 | 120.9457 | 120.9 | 115.9561 | -121.1975
1790.6406 | 121.4539 | -116.2033 | 5.0171 | 0.59861 | 0.033803 | 0.0068819 | 0.36182 | 0.084372 | 0.64669 | -0.031739 | 2.0206 | 4.0348 | 0.05092 | 0.08512 | 3.2046 | 0.067187 | -6.958 | 0.1236 | -23.085 | -2.1927 | 0.19684 | -116.2354 | -116.3544 | 4.4083 | -0.17395 | 2.6825 | 4.6967 | 4.6692 | -116.2216 | -116.1987 | -0.032044 | -0.15106 | -4.8203 | 116.3269 | 114.0106 | 114.1617 | -11.9751 | -0.018311 | 0.004578 | -0.32043 | 120.6116 | 118.8858 | 118.8812 | -0.3479 | 116.4001 | 109.2453 | 93.1183 | -121.3715 | 120.9 | 120.8725 | 116.0294 | -121.2158
1791.7031 | 121.4172 | -116.2399 | 5.0079 | 0.32395 | 0.017781 | 0.026108 | 0.3693 | 0.073691 | 0.63281 | -0.043489 | 0.4947 | 4.0284 | 0.040239 | 0.10007 | 3.1929 | 0.067187 | -7.3334 | 0.068665 | -23.0438 | -2.3438 | 0.21057 | -116.2033 | -116.3315 | 4.335 | -0.23346 | 2.6093 | 4.7287 | 4.6692 | -116.2766 | -116.2262 | 0.036621 | -0.091553 | -4.7974 | 116.3086 | 113.8962 | 113.9877 | -12.3413 | -0.036621 | 0.013733 | -0.27924 | 120.575 | 118.8492 | 118.8354 | -0.33875 | 116.4505 | 108.9066 | 93.1961 | -121.3394 | 120.9686 | 120.9091 | 116.0065 | -121.2341
1792.6406 | 121.3715 | -116.0889 | 5.1407 | 0.7512 | 0.020985 | 0.0068819 | 0.36182 | 0.079032 | 0.64883 | -0.033876 | 0.55574 | 4.021 | 0.058397 | 0.10007 | 3.2057 | 0.058642 | -7.196 | 0.10986 | -23.0301 | -2.3758 | 0.19684 | -116.0202 | -116.1209 | 4.6097 | -0.19684 | 2.8793 | 4.9026 | 4.8203 | -116.0797 | -116.0294 | 0.068664 | -0.032044 | -4.9438 | 116.1987 | 113.7131 | 113.7451 | -12.3367 | 0.009155 | 0.059509 | -0.23804 | 120.6985 | 118.9682 | 118.9087 | -0.32043 | 116.2857 | 108.8928 | 93.0588 | -121.2616 | 120.9915 | 120.9091 | 115.892 | -121.17
1793.6406 | 121.4218 | -116.3681 | 4.8798 | 3.0248 | 0.028462 | 0.01329 | 0.36395 | 0.071555 | 0.63922 | -0.040284 | 0.76936 | 4.0274 | 0.047715 | 0.10328 | 3.2025 | 0.072527 | -7.2556 | 0.07782 | -22.9111 | -2.5269 | 0.14648 | -116.2949 | -116.4322 | 4.303 | -0.20142 | 2.5772 | 4.6005 | 4.5547 | -116.3635 | -116.3315 | 0.073242 | -0.064087 | -4.7333 | 116.4459 | 113.8412 | 113.9053 | -12.1353 | 0.004578 | 0.036621 | -0.27924 | 120.6711 | 118.9453 | 118.9087 | -0.32501 | 116.5146 | 109.1125 | 93.457 | -121.312 | 120.9686 | 120.9229 | 116.1667 | -121.2112
1794.6406 | 121.4447 | -116.4047 | 4.834 | 0.47654 | 0.034871 | 0.0047449 | 0.39707 | 0.0801 | 0.65417 | -0.044557 | 0.41841 | 4.0348 | 0.037034 | 0.11182 | 3.2068 | 0.05971 | -7.164 | 0.032043 | -22.9797 | -2.6413 | 0.21057 | -116.3773 | -116.51 | 4.248 | -0.20599 | 2.5223 | 4.5502 | 4.4952 | -116.4459 | -116.3589 | 0.027466 | -0.10529 | -4.6234 | 116.4368 | 113.7634 | 113.8687 | -11.998 | -0.041199 | 0.045776 | -0.28381 | 120.6528 | 118.927 | 118.8812 | -0.33875 | 116.6153 | 109.2407 | 93.425 | -121.344 | 120.9549 | 120.9 | 116.1987 | -121.1929
1795.6406 | 121.4584 | -116.3681 | 4.834 | 0.62913 | 0.045552 | 0.0036769 | 0.3757 | 0.088645 | 0.64883 | -0.03708 | 0.29634 | 4.0327 | 0.05092 | 0.10862 | 3.2046 | 0.073595 | -6.8802 | 0.082397 | -23.0438 | -2.2385 | 0.20599 | -116.3681 | -116.4963 | 4.2297 | -0.23346 | 2.4673 | 4.5731 | 4.4907 | -116.4505 | -116.3635 | 0 | -0.12817 | -4.628 | 116.4505 | 114.1296 | 114.2578 | -11.7142 | -0.082397 | 0.004578 | -0.26093 | 120.5978 | 118.8354 | 118.8309 | -0.34332 | 116.5741 | 109.4879 | 93.3243 | -121.3303 | 120.9412 | 120.8588 | 116.1346 | -121.1975
1796.6406 | 121.4676 | -116.3864 | 4.8248 | 0.034038 | 0.00069119 | 0.016495 | 0.35327 | 0.060874 | 0.62213 | -0.048829 | 0.036941 | 4.0231 | 0.030626 | 0.096869 | 3.195 | 0.062914 | -6.8985 | 0.17853 | -22.8378 | -2.3758 | 0.21515 | -116.3727 | -116.4642 | 4.2297 | -0.15106 | 2.4261 | 4.5319 | 4.5044 | -116.4597 | -116.3956 | 0.013733 | -0.077819 | -4.6097 | 116.5649 | 114.0106 | 114.0884 | -11.7233 | -0.073242 | -0.009155 | -0.29297 | 120.6162 | 118.8126 | 118.8217 | -0.32043 | 116.6016 | 109.4879 | 93.5486 | -121.2891 | 120.9183 | 120.8908 | 116.2354 | -121.2204
1797.6406 | 121.5637 | -116.3681 | 4.8706 | 0.64439 | 0.034871 | -0.0027321 | 0.36395 | 0.08544 | 0.64135 | -0.028535 | 0.69307 | 4.0274 | 0.040239 | 0.086188 | 3.2046 | 0.050097 | -6.7932 | 0.10071 | -23.0392 | -2.2842 | 0.19226 | -116.2857 | -116.4368 | 4.3213 | -0.17853 | 2.4994 | 4.6188 | 4.5547 | -116.3864 | -116.3223 | 0.082397 | -0.068665 | -4.6783 | 116.4688 | 114.0839 | 114.1525 | -11.6638 | -0.018311 | 0.045776 | -0.25177 | 120.6894 | 118.8675 | 118.8217 | -0.31586 | 116.5604 | 109.5749 | 93.3289 | -121.3074 | 120.9869 | 120.9229 | 116.1896 | -121.1929
1798.6406 | 121.4539 | -116.185 | 5.0354 | 0.26292 | 0.032734 | -0.0059361 | 0.36075 | 0.077964 | 0.65096 | -0.032808 | 0.52522 | 4.0231 | 0.03917 | 0.091529 | 3.194 | 0.066119 | -7.196 | 0.1236 | -22.9614 | -2.1011 | 0.20599 | -116.153 | -116.2811 | 4.4586 | -0.19226 | 2.6733 | 4.7562 | 4.715 | -116.2125 | -116.1301 | 0.032044 | -0.09613 | -4.8294 | 116.3086 | 114.0839 | 114.18 | -12.2314 | -0.027465 | 0.054932 | -0.27923 | 120.6436 | 118.8583 | 118.8034 | -0.32043 | 116.391 | 108.989 | 93.2236 | -121.3165 | 120.9412 | 120.9 | 115.9927 | -121.1655
1799.6406 | 121.463 | -116.3132 | 4.921 | 0.55284 | 0.032734 | -0.0080721 | 0.35755 | 0.068351 | 0.64242 | -0.029603 | 1.044 | 4.0252 | 0.042375 | 0.087256 | 3.2025 | 0.06505 | -7.4066 | 0.10986 | -22.8104 | -2.3483 | 0.16022 | -116.2903 | -116.4368 | 4.3442 | -0.20142 | 2.5818 | 4.6326 | 4.5959 | -116.3498 | -116.2811 | 0.022888 | -0.1236 | -4.7607 | 116.423 | 113.9648 | 114.0884 | -12.3276 | -0.036621 | 0.032043 | -0.28839 | 120.6573 | 118.895 | 118.8629 | -0.32501 | 116.4734 | 108.9066 | 93.5028 | -121.3577 | 120.9457 | 120.9091 | 116.1118 | -121.2021
1800.6406 | 121.4676 | -116.2262 | 5.0171 | 0.59861 | 0.026326 | 0.0026089 | 0.36823 | 0.077964 | 0.64883 | -0.030671 | 0.7541 | 4.0242 | 0.03917 | 0.092597 | 3.1993 | 0.068255 | -6.8436 | 0.10529 | -22.7417 | -2.774 | 0.19226 | -116.2628 | -116.3635 | 4.4174 | -0.16479 | 2.6779 | 4.7012 | 4.6692 | -116.2262 | -116.1804 | -0.036621 | -0.13733 | -4.8248 | 116.3315 | 113.4521 | 113.5895 | -11.8607 | 0 | 0.045776 | -0.31586 | 120.6436 | 118.9041 | 118.8583 | -0.3479 | 116.4185 | 109.3826 | 93.4845 | -121.3806 | 120.9274 | 120.8954 | 116.0614 | -121.1975
1801.6406 | 121.3715 | -116.4276 | 4.8752 | -0.24062 | 0.015645 | 0.011154 | 0.37143 | 0.082236 | 0.63067 | -0.039216 | -0.11565 | 4.0242 | 0.043443 | 0.08512 | 3.1929 | 0.06505 | -7.2006 | 0.073242 | -23.1079 | -2.2385 | 0.21973 | -116.3956 | -116.5329 | 4.1473 | -0.25177 | 2.4307 | 4.5868 | 4.5364 | -116.4871 | -116.4139 | 0.032043 | -0.10529 | -4.6555 | 116.5009 | 114.1891 | 114.2944 | -12.0758 | -0.05951 | 0.013733 | -0.28839 | 120.575 | 118.8583 | 118.8446 | -0.33874 | 116.6473 | 109.227 | 93.3197 | -121.4081 | 121.0144 | 120.9641 | 116.1758 | -121.2891
1802.6406 | 121.4218 | -116.5146 | 4.7012 | 0.59861 | 0.035939 | 0.00047294 | 0.3757 | 0.073691 | 0.66592 | -0.026399 | 0.55574 | 4.0263 | 0.055192 | 0.093665 | 3.2046 | 0.063982 | -6.9992 | 0.054932 | -22.8973 | -2.1652 | 0.2243 | -116.5146 | -116.6336 | 4.1016 | -0.21057 | 2.3209 | 4.4174 | 4.3671 | -116.5787 | -116.4825 | 0 | -0.11902 | -4.4769 | 116.5695 | 114.3494 | 114.4684 | -11.7004 | -0.064087 | 0.032043 | -0.28381 | 120.6161 | 118.8354 | 118.8034 | -0.33417 | 116.7389 | 109.5154 | 93.6172 | -121.3348 | 120.932 | 120.8817 | 116.304 | -121.1838
1803.6406 | 121.431 | -116.5237 | 4.7012 | -0.7289 | 0.02953 | 0.011154 | 0.35755 | 0.077964 | 0.63708 | -0.028535 | 0.63203 | 4.0359 | 0.031694 | 0.089393 | 3.1961 | 0.071459 | -6.958 | 0.11902 | -22.7646 | -1.9867 | 0.19684 | -116.4917 | -116.5924 | 4.1107 | -0.21057 | 2.3712 | 4.4266 | 4.39 | -116.5741 | -116.5237 | 0.032044 | -0.068664 | -4.5044 | 116.6428 | 114.537 | 114.6057 | -11.6592 | -0.050354 | 0 | -0.27466 | 120.6345 | 118.895 | 118.895 | -0.31128 | 116.7206 | 109.5657 | 93.7592 | -121.2936 | 120.9503 | 120.9137 | 116.3132 | -121.225
1804.6406 | 121.431 | -116.6519 | 4.5731 | -0.042256 | 0.038075 | -0.013413 | 0.36075 | 0.076896 | 0.65524 | -0.031739 | 0.60152 | 4.0274 | 0.044511 | 0.096869 | 3.21 | 0.071459 | -6.9672 | 0.11444 | -23.0209 | -2.4078 | 0.19226 | -116.629 | -116.748 | 3.9825 | -0.21057 | 2.243 | 4.2847 | 4.2526 | -116.7114 | -116.6473 | 0.022889 | -0.09613 | -4.3808 | 116.7664 | 114.2441 | 114.3402 | -11.5402 | -0.059509 | 0.004578 | -0.28839 | 120.6345 | 118.895 | 118.8904 | -0.32043 | 116.8442 | 109.6848 | 93.631 | -121.3211 | 120.9366 | 120.9045 | 116.4413 | -121.2204
1805.6406 | 121.4767 | -116.5237 | 4.6967 | 0.36973 | 0.048756 | 0.0068819 | 0.36075 | 0.082236 | 0.66165 | -0.027467 | 0.67781 | 4.0348 | 0.043443 | 0.091529 | 3.2089 | 0.068255 | -7.077 | 0.10529 | -22.7783 | -2.2934 | 0.2243 | -116.4413 | -116.6016 | 4.1061 | -0.21973 | 2.3666 | 4.4357 | 4.3716 | -116.5695 | -116.51 | 0.082398 | -0.077819 | -4.4724 | 116.629 | 114.2303 | 114.3082 | -11.7737 | -0.045776 | 0.013733 | -0.26092 | 120.6299 | 118.8904 | 118.8766 | -0.32501 | 116.748 | 109.4467 | 93.7454 | -121.2982 | 120.9595 | 120.8954 | 116.304 | -121.2067
1806.6406 | 121.4035 | -116.6748 | 4.6188 | 0.35447 | 0.010304 | 0.0090179 | 0.3757 | 0.071555 | 0.62533 | -0.044557 | 0.34212 | 4.022 | 0.03917 | 0.096869 | 3.1929 | 0.071459 | -7.1777 | 0.054932 | -22.6593 | -2.3621 | 0.21973 | -116.6061 | -116.7297 | 4.0146 | -0.27466 | 2.2797 | 4.4037 | 4.3304 | -116.6611 | -116.6107 | 0.068665 | -0.054931 | -4.3991 | 116.7297 | 114.3127 | 114.3677 | -11.7966 | 0.013733 | 0.064087 | -0.21515 | 120.6894 | 118.9545 | 118.8904 | -0.28839 | 116.8945 | 109.4971 | 94.0155 | -121.3486 | 121.0785 | 121.0052 | 116.4001 | -121.2296
1807.6406 | 121.4401 | -116.716 | 4.5273 | 0.55284 | 0.033803 | 0.0036769 | 0.37784 | 0.084372 | 0.65096 | -0.040284 | -1.7483 | 4.022 | 0.043443 | 0.091529 | 3.2089 | 0.066119 | -7.0679 | 0.10986 | -22.6181 | -2.1927 | 0.19684 | -116.7297 | -116.8579 | 3.9093 | -0.19684 | 2.2064 | 4.2297 | 4.1702 | -116.7389 | -116.6794 | -0.013733 | -0.14191 | -4.3304 | 116.8259 | 114.5233 | 114.6652 | -11.5952 | -0.022889 | 0.036621 | -0.29755 | 120.6253 | 118.9224 | 118.8858 | -0.35706 | 116.9128 | 109.6481 | 94.0979 | -121.3852 | 120.9457 | 120.8862 | 116.5192 | -121.2067
1808.6406 | 121.431 | -116.5741 | 4.6555 | 0.56809 | 0.033803 | 0.0068819 | 0.37464 | 0.082236 | 0.65951 | -0.025331 | 0.3116 | 4.038 | 0.044511 | 0.094733 | 3.2004 | 0.05971 | -7.0038 | 0.068665 | -22.6135 | -2.1057 | 0.21515 | -116.5375 | -116.6885 | 4.0878 | -0.27466 | 2.3438 | 4.39 | 4.3396 | -116.6061 | -116.5466 | 0.036621 | -0.11444 | -4.4403 | 116.6428 | 114.4684 | 114.5828 | -11.6592 | -0.032043 | 0.027466 | -0.2655 | 120.6619 | 118.9178 | 118.8904 | -0.31586 | 116.7892 | 109.5703 | 93.9606 | -121.344 | 120.9641 | 120.9137 | 116.2994 | -121.2021
1809.6406 | 121.4722 | -116.5329 | 4.7104 | 0.55284 | 0.031666 | -0.0038001 | 0.36823 | 0.084372 | 0.64669 | -0.029603 | 0.47945 | 4.0274 | 0.043443 | 0.088325 | 3.2036 | 0.066119 | -7.2144 | 0.045776 | -22.7921 | -2.3712 | 0.21973 | -116.5237 | -116.6428 | 4.1016 | -0.35706 | 2.3529 | 4.4083 | 4.3945 | -116.5833 | -116.4825 | 0.009155 | -0.10986 | -4.4907 | 116.5787 | 114.1617 | 114.2715 | -11.9247 | -0.050354 | 0.050354 | -0.30212 | 120.6345 | 118.8858 | 118.8354 | -0.31586 | 116.7526 | 109.3185 | 93.7408 | -121.3531 | 120.9412 | 120.9274 | 116.1758 | -121.1929
1810.6406 | 121.4264 | -116.5878 | 4.628 | 0.70542 | 0.034871 | -0.0048681 | 0.36395 | 0.088645 | 0.65417 | -0.032808 | 0.67781 | 4.0295 | 0.034898 | 0.096869 | 3.2089 | 0.063982 | -7.0999 | 0.10529 | -22.6364 | -2.6642 | 0.20142 | -116.4871 | -116.6336 | 4.0833 | -0.27924 | 2.3529 | 4.4083 | 4.3579 | -116.5787 | -116.5237 | 0.10071 | -0.045776 | -4.4266 | 116.6931 | 113.9236 | 113.9694 | -11.7279 | 0.009156 | 0.064087 | -0.21973 | 120.6711 | 118.9407 | 118.8766 | -0.27008 | 116.7892 | 109.4879 | 93.9514 | -121.2616 | 120.9961 | 120.9457 | 116.3086 | -121.1517
1811.6406 | 121.463 | -116.4642 | 4.7607 | 1.8651 | 0.044484 | 0.0026089 | 0.36823 | 0.071555 | 0.64456 | -0.031739 | 0.66255 | 4.0316 | 0.042375 | 0.091529 | 3.2057 | 0.058642 | -7.0496 | 0.09613 | -22.467 | -2.2705 | 0.20599 | -116.4185 | -116.5649 | 4.1611 | -0.27924 | 2.4353 | 4.4861 | 4.422 | -116.5146 | -116.4597 | 0.045776 | -0.10071 | -4.5547 | 116.5604 | 114.1937 | 114.2944 | -11.8103 | -0.050354 | 0.004577 | -0.27466 | 120.6253 | 118.8995 | 118.895 | -0.33874 | 116.6702 | 109.4147 | 93.9972 | -121.3257 | 120.9503 | 120.8862 | 116.185 | -121.2204
1812.6406 | 121.4722 | -101.6602 | 19.4595 | 0.56809 | 0.042347 | -0.013413 | 0.37036 | 0.064078 | 0.56658 | -0.041353 | 0.72359 | 3.9141 | 0.030626 | 0.095801 | 3.21 | 0.061846 | -6.4774 | 0.09613 | -19.8303 | -1.9409 | 0.19226 | -101.6785 | -101.7929 | 19.0018 | -0.13733 | 17.3447 | 19.2261 | 19.1391 | -101.7334 | -101.6922 | -0.018311 | -0.13275 | -19.2673 | 101.7563 | 99.7192 | 99.852 | -25.9369 | -0.073242 | -0.032044 | -0.23346 | 120.6619 | 119.0048 | 119.0369 | -0.32043 | 101.8524 | 95.1828 | 81.8298 | -121.2524 | 120.8862 | 120.7993 | 101.5228 | -121.1517
1813.6406 | 121.4676 | -116.3635 | 4.8294 | 0.62913 | 0.048756 | -0.0048681 | 0.35755 | 0.095053 | 0.65737 | -0.024263 | 0.34212 | 4.0306 | 0.040239 | 0.10435 | 3.2025 | 0.062914 | -7.2144 | 0.059509 | -22.8241 | -2.1698 | 0.24261 | -116.3773 | -116.478 | 4.2664 | -0.2655 | 2.5452 | 4.5776 | 4.5273 | -116.4642 | -116.3589 | -0.013733 | -0.11444 | -4.5868 | 116.423 | 114.1937 | 114.3082 | -12.0438 | -0.10071 | 0.004577 | -0.25177 | 120.6299 | 118.9087 | 118.9041 | -0.30212 | 116.6061 | 109.1492 | 93.5394 | -121.3074 | 120.9412 | 120.8908 | 116.098 | -121.1884
1814.6406 | 121.376 | -116.4001 | 4.8431 | 0.44602 | 0.032734 | -0.0027321 | 0.35221 | 0.083304 | 0.6499 | -0.032808 | 0.64729 | 4.0231 | 0.046647 | 0.099006 | 3.2025 | 0.071459 | -7.1365 | 0.10071 | -22.7646 | -2.0691 | 0.19684 | -116.2949 | -116.4093 | 4.3076 | -0.21057 | 2.5864 | 4.6417 | 4.5959 | -116.3635 | -116.3361 | 0.10529 | -0.009156 | -4.6463 | 116.5009 | 114.3311 | 114.3402 | -11.9797 | 0.036621 | 0.064086 | -0.20142 | 120.7077 | 118.9865 | 118.9224 | -0.24719 | 116.597 | 109.2636 | 93.6356 | -121.2524 | 121.0419 | 120.9961 | 116.1896 | -121.1792
1815.6406 | 121.4447 | -116.423 | 4.8431 | 0.56809 | 0.041279 | -0.0048681 | 0.36395 | 0.073691 | 0.66592 | -0.040284 | 0.60152 | 4.0306 | 0.046647 | 0.089393 | 3.2089 | 0.070391 | -7.1503 | 0.009155 | -22.76 | -2.4307 | 0.21515 | -116.3864 | -116.51 | 4.2114 | -0.28381 | 2.4902 | 4.5868 | 4.5227 | -116.4642 | -116.3818 | 0.036621 | -0.086975 | -4.628 | 116.4322 | 113.9923 | 114.0793 | -11.9934 | -0.041198 | 0.041199 | -0.25635 | 120.6345 | 118.9133 | 118.8721 | -0.32043 | 116.6382 | 109.2728 | 93.663 | -121.3531 | 121.0098 | 120.9457 | 116.1392 | -121.225
1816.6406 | 121.4081 | -116.4551 | 4.8111 | 0.50706 | 0.057301 | -0.0038001 | 0.37998 | 0.084372 | 0.64776 | -0.036012 | 0.63203 | 4.0402 | 0.047715 | 0.097938 | 3.2025 | 0.061846 | -7.1869 | -0.009155 | -22.8973 | -2.4353 | 0.22888 | -116.423 | -116.5329 | 4.1748 | -0.29297 | 2.4445 | 4.5593 | 4.5136 | -116.4734 | -116.4322 | 0.032043 | -0.07782 | -4.5822 | 116.4459 | 114.0198 | 114.0976 | -11.998 | -0.018311 | 0.022888 | -0.25177 | 120.6299 | 118.8995 | 118.8766 | -0.29755 | 116.684 | 109.2682 | 93.5577 | -121.344 | 121.0144 | 120.9686 | 116.1621 | -121.2433
1817.6406 | 121.4493 | -116.4825 | 4.7791 | 0.46128 | 0.018849 | 0.020767 | 0.36716 | 0.083304 | 0.62213 | -0.055238 | 0.63203 | 4.022 | 0.063737 | 0.095801 | 3.2004 | 0.067187 | -7.1594 | 0.1236 | -22.7188 | -2.504 | 0.21515 | -116.4185 | -116.5604 | 4.1473 | -0.24261 | 2.4628 | 4.509 | 4.454 | -116.5237 | -116.4734 | 0.064087 | -0.07782 | -4.5639 | 116.6061 | 113.9786 | 114.0564 | -11.9385 | -0.041199 | 0.009155 | -0.27008 | 120.6299 | 118.9453 | 118.9362 | -0.32501 | 116.6977 | 109.3231 | 93.7637 | -121.3394 | 120.9915 | 120.9366 | 116.2399 | -121.2524
1818.6406 | 121.4676 | -116.4047 | 4.8203 | 0.58335 | 0.043416 | -0.010208 | 0.37036 | 0.088645 | 0.6499 | -0.036012 | 0.38789 | 4.0188 | 0.044511 | 0.087256 | 3.2078 | 0.070391 | -7.1182 | 0.054932 | -22.6959 | -1.918 | 0.20599 | -116.3635 | -116.5329 | 4.2389 | -0.34332 | 2.504 | 4.5547 | 4.4998 | -116.4597 | -116.3635 | 0.041199 | -0.12817 | -4.6143 | 116.4597 | 114.4867 | 114.6149 | -11.9385 | -0.054932 | 0.041199 | -0.2655 | 120.6436 | 118.9087 | 118.8675 | -0.32043 | 116.6107 | 109.2865 | 93.7088 | -121.3531 | 120.9595 | 120.9045 | 116.0614 | -121.1838
1819.6406 | 121.4355 | -116.4413 | 4.8203 | 0.55284 | 0.048756 | -0.0048681 | 0.36823 | 0.070487 | 0.66271 | -0.036012 | 0.58626 | 4.0242 | 0.05626 | 0.088325 | 3.2089 | 0.06505 | -7.1182 | 0.013733 | -22.6181 | -1.973 | 0.21973 | -116.4047 | -116.5329 | 4.2114 | -0.27924 | 2.4811 | 4.5456 | 4.5044 | -116.4459 | -116.4276 | 0.036621 | -0.091553 | -4.6005 | 116.4551 | 114.4684 | 114.5599 | -11.9385 | -0.004578 | 0.013733 | -0.27466 | 120.6528 | 118.9224 | 118.9087 | -0.31586 | 116.6611 | 109.3231 | 93.8232 | -121.3531 | 120.9869 | 120.9457 | 116.1621 | -121.2479
1820.6406 | 121.463 | -116.4047 | 4.8294 | 0.56809 | 0.013508 | -0.0070041 | 0.36395 | 0.086509 | 0.62319 | -0.036012 | 0.70833 | 4.0145 | 0.048783 | 0.097938 | 3.1886 | 0.075732 | -7.1228 | 0.15564 | -22.4213 | -2.3895 | 0.13733 | -116.4001 | -116.4963 | 4.2206 | -0.28839 | 2.4948 | 4.5547 | 4.509 | -116.4505 | -116.4139 | 0.004578 | -0.091553 | -4.6921 | 116.5604 | 114.0152 | 114.1068 | -11.9522 | -0.045776 | -0.009155 | -0.27466 | 120.6253 | 118.8995 | 118.9087 | -0.32043 | 116.5421 | 109.2819 | 93.9835 | -121.3257 | 120.9595 | 120.9137 | 116.1163 | -121.2433
1821.6406 | 121.4447 | -116.3635 | 4.8889 | 0.55284 | 0.014576 | 0.00047294 | 0.3757 | 0.072623 | 0.64028 | -0.031739 | 1.0745 | 4.006 | 0.03383 | 0.088325 | 3.2078 | 0.062914 | -7.0221 | 0.10071 | -22.6089 | -2.5635 | 0.17853 | -116.4047 | -116.4963 | 4.2938 | -0.29755 | 2.5772 | 4.6188 | 4.5547 | -116.3635 | -116.3086 | -0.041199 | -0.13275 | -4.7104 | 116.4642 | 113.8 | 113.9328 | -11.911 | 0 | 0.054931 | -0.27008 | 120.6573 | 118.9407 | 118.8858 | -0.33417 | 116.5421 | 109.3414 | 93.7546 | -121.3852 | 120.9824 | 120.9183 | 116.066 | -121.1975
1822.6406 | 121.4081 | -116.4001 | 4.9026 | -0.2864 | 0.044484 | -0.0091401 | 0.37464 | 0.083304 | 0.66165 | -0.034944 | 0.41841 | 4.0306 | 0.063737 | 0.086188 | 3.2025 | 0.062914 | -7.1503 | -0.013733 | -22.998 | -2.6688 | 0.24261 | -116.3681 | -116.4871 | 4.216 | -0.37079 | 2.4628 | 4.6463 | 4.6051 | -116.4322 | -116.3635 | 0.032043 | -0.086976 | -4.66 | 116.3864 | 113.7314 | 113.8184 | -12.0529 | -0.032044 | 0.036621 | -0.25635 | 120.6161 | 118.8629 | 118.8263 | -0.29755 | 116.6428 | 109.2499 | 93.4021 | -121.3898 | 121.0464 | 121.0052 | 116.0294 | -121.2662
1823.6406 | 121.3898 | -116.3864 | 4.9072 | 0.3087 | 0.034871 | 0.0058129 | 0.36502 | 0.077964 | 0.65203 | -0.026399 | 0.50996 | 4.0316 | 0.048783 | 0.094733 | 3.2068 | 0.063982 | -7.2052 | 0.018311 | -22.7921 | -2.2614 | 0.24261 | -116.3498 | -116.4642 | 4.2023 | -0.37994 | 2.4536 | 4.6326 | 4.5959 | -116.4276 | -116.3635 | 0.036622 | -0.077819 | -4.6646 | 116.4047 | 114.1251 | 114.2029 | -12.1124 | -0.041198 | 0.022889 | -0.27466 | 120.5887 | 118.84 | 118.8171 | -0.31128 | 116.629 | 109.1812 | 93.5944 | -121.3715 | 121.019 | 120.9824 | 116.0065 | -121.2708
1824.6406 | 121.431 | -116.3086 | 4.9301 | 0.53758 | 0.040211 | -0.012345 | 0.38211 | 0.079032 | 0.65203 | -0.033876 | 0.60152 | 4.0295 | 0.060533 | 0.10755 | 3.2046 | 0.063982 | -7.1548 | 0.013733 | -22.7875 | -2.0874 | 0.20599 | -116.2903 | -116.4047 | 4.2984 | -0.31128 | 2.5543 | 4.6738 | 4.6234 | -116.3589 | -116.2994 | 0.018311 | -0.09613 | -4.7241 | 116.3223 | 114.2212 | 114.3173 | -12.085 | -0.050354 | 0.009156 | -0.25635 | 120.607 | 118.8629 | 118.8538 | -0.3067 | 116.5146 | 109.1537 | 93.5211 | -121.3348 | 120.9824 | 120.932 | 115.9973 | -121.2296
1825.6406 | 121.4172 | -115.5624 | 5.7404 | 0.52232 | 0.051961 | 0.0015409 | 0.35861 | 0.075827 | 0.64883 | -0.026399 | 0.66255 | 4.0242 | 0.05092 | 0.093665 | 3.1982 | 0.066119 | -7.0953 | 0.009155 | -22.522 | -2.0096 | 0.23804 | -115.48 | -115.6082 | 5.0858 | -0.34332 | 3.3325 | 5.4749 | 5.4245 | -115.535 | -115.5029 | 0.082397 | -0.045776 | -5.5023 | 115.5716 | 113.5529 | 113.5986 | -12.8357 | 0.027466 | 0.059509 | -0.2655 | 120.6482 | 118.895 | 118.8355 | -0.31586 | 115.8005 | 108.4671 | 93.0405 | -121.3486 | 121.0373 | 120.9869 | 115.2191 | -121.2433
1826.6406 | 121.3898 | -115.741 | 5.5435 | 0.46128 | 0.047688 | -0.0016631 | 0.36609 | 0.082236 | 0.64028 | -0.039216 | 0.63203 | 4.0284 | 0.049852 | 0.087256 | 3.2068 | 0.054369 | -7.1045 | -0.022888 | -22.5128 | -2.4948 | 0.23346 | -115.686 | -115.8279 | 4.8889 | -0.3479 | 3.1219 | 5.2917 | 5.2322 | -115.7593 | -115.7089 | 0.054932 | -0.086975 | -5.3101 | 115.7181 | 113.2462 | 113.3331 | -12.648 | -0.01831 | 0.032044 | -0.25177 | 120.6299 | 118.8629 | 118.8309 | -0.31128 | 115.9744 | 108.6365 | 93.2281 | -121.3715 | 121.0327 | 120.9732 | 115.3931 | -121.2524
1827.6406 | 121.4539 | -115.7501 | 5.4977 | 0.52232 | 0.054097 | 0.0058129 | 0.37143 | 0.073691 | 0.64028 | -0.03708 | 0.64729 | 4.0156 | 0.046647 | 0.095801 | 3.1993 | 0.074663 | -7.0633 | 0.050354 | -22.5677 | -2.1332 | 0.21057 | -115.7227 | -115.8371 | 4.9026 | -0.34332 | 3.0396 | 5.2368 | 5.191 | -115.7822 | -115.6998 | 0.027466 | -0.086975 | -5.2872 | 115.8005 | 113.6169 | 113.7039 | -12.561 | -0.032044 | 0.050354 | -0.26093 | 120.6528 | 118.7897 | 118.7393 | -0.3067 | 115.9607 | 108.6868 | 93.1824 | -121.3348 | 120.9869 | 120.9412 | 115.4068 | -121.1975
1828.6406 | 121.4539 | -115.9515 | 5.3238 | 0.61387 | 0.043416 | 0.0026089 | 0.37677 | 0.079032 | 0.64883 | -0.032808 | 0.64729 | 4.0252 | 0.045579 | 0.082984 | 3.1961 | 0.057574 | -7.045 | 0.009155 | -22.1603 | -2.2339 | 0.21515 | -115.892 | -116.0294 | 4.7058 | -0.29297 | 2.9205 | 5.072 | 5.0171 | -115.9744 | -115.9058 | 0.059509 | -0.07782 | -5.1086 | 115.9607 | 113.7177 | 113.7955 | -12.3688 | -0.022888 | 0.045776 | -0.25177 | 120.6573 | 118.8721 | 118.8263 | -0.3067 | 116.1667 | 108.9066 | 93.7912 | -121.3531 | 121.0236 | 120.9686 | 115.6586 | -121.2296
1829.6406 | 121.3715 | -115.8279 | 5.4977 | 0.53758 | 0.045552 | 0.0058129 | 0.38852 | 0.070487 | 0.65203 | -0.032808 | 2.0969 | 4.0188 | 0.046647 | 0.088325 | 3.2014 | 0.062914 | -7.0633 | -0.036621 | -22.2519 | -1.8356 | 0.25177 | -115.6769 | -115.8463 | 4.7653 | -0.3479 | 2.9205 | 5.246 | 5.2139 | -115.8325 | -115.773 | 0.15106 | -0.01831 | -5.246 | 115.7913 | 113.9923 | 114.0106 | -12.561 | -0.004578 | 0.054932 | -0.25177 | 120.5933 | 118.7485 | 118.6935 | -0.28381 | 116.0797 | 108.7646 | 93.576 | -121.344 | 121.0739 | 121.0419 | 115.48 | -121.2708
1830.6406 | 121.4081 | -115.8325 | 5.4428 | 0.4918 | 0.041279 | -0.0059361 | 0.37784 | 0.076896 | 0.64776 | -0.034944 | 0.63203 | 4.0167 | 0.048783 | 0.11075 | 3.2014 | 0.070391 | -7.045 | -0.004578 | -22.197 | -1.9089 | 0.23804 | -115.8325 | -115.9653 | 4.7607 | -0.33417 | 2.9388 | 5.159 | 5.1132 | -115.8783 | -115.8096 | 0 | -0.13275 | -5.2048 | 115.8279 | 113.9236 | 114.0564 | -12.4878 | -0.045776 | 0.022889 | -0.28381 | 120.5933 | 118.7714 | 118.7485 | -0.32959 | 116.0706 | 108.7875 | 93.6356 | -121.4081 | 120.9915 | 120.9457 | 115.4984 | -121.2524
1831.6875 | 121.3394 | -115.8188 | 5.484 | 0.14085 | 0.043416 | -0.042252 | 0.36502 | 0.076896 | 0.66165 | -0.045625 | 0.28108 | 4.0306 | 0.051988 | 0.091529 | 3.211 | 0.055437 | -7.0724 | -0.027466 | -22.7097 | -2.1194 | 0.21057 | -115.7867 | -115.9515 | 4.747 | -0.38452 | 2.9205 | 5.2231 | 5.1682 | -115.8646 | -115.8142 | 0.032044 | -0.13275 | -5.2734 | 115.7913 | 113.6993 | 113.8321 | -12.5565 | -0.045776 | 0.004578 | -0.26093 | 120.5658 | 118.7393 | 118.7347 | -0.31586 | 116.0294 | 108.7463 | 93.1091 | -121.4355 | 121.0419 | 120.9869 | 115.4343 | -121.2982
1832.6406 | 121.3715 | -115.8966 | 5.4108 | 0.55284 | 0.051961 | -0.010208 | 0.36182 | 0.084372 | 0.62747 | -0.021058 | 0.43367 | 4.0306 | 0.051988 | 0.094733 | 3.1961 | 0.071459 | -7.2281 | 0.064087 | -22.7371 | -2.092 | 0.25177 | -115.8875 | -115.9973 | 4.6875 | -0.37537 | 2.9068 | 5.1315 | 5.0858 | -115.9287 | -115.8737 | 0.009155 | -0.10071 | -5.159 | 115.9607 | 113.8046 | 113.9053 | -12.6389 | -0.032044 | 0.022888 | -0.27924 | 120.5841 | 118.8034 | 118.7805 | -0.32501 | 116.1484 | 108.6685 | 93.1595 | -121.4081 | 121.0281 | 120.9824 | 115.5212 | -121.2845
1833.6406 | 121.3623 | -116.1758 | 5.1361 | 0.50706 | 0.038075 | -0.0027321 | 0.37464 | 0.077964 | 0.64776 | -0.039216 | 0.76936 | 4.0252 | 0.045579 | 0.095801 | 3.1982 | 0.070391 | -7.0862 | -0.041199 | -23.0621 | -2.0599 | 0.26093 | -116.1118 | -116.2079 | 4.3808 | -0.33417 | 2.6321 | 4.8706 | 4.8386 | -116.1896 | -116.1209 | 0.064087 | -0.032044 | -4.8752 | 116.1346 | 114.1159 | 114.1479 | -12.2223 | -0.013733 | 0.054931 | -0.2655 | 120.5566 | 118.808 | 118.7531 | -0.29755 | 116.4368 | 109.0897 | 93.1137 | -121.344 | 121.0464 | 121.0144 | 115.8417 | -121.257
1834.6406 | 121.4218 | -116.3864 | 4.9072 | 0.61387 | 0.049824 | 0.0058129 | 0.37677 | 0.016013 | 0.64028 | -0.042421 | 0.63203 | 3.9601 | 0.05092 | 0.099006 | 3.2004 | 0.06505 | -115.2237 | -0.036621 | -35.2798 | -2.0737 | 0.23804 | -116.3773 | -116.478 | 4.2343 | -0.3479 | 2.504 | 4.6646 | 4.6097 | -116.4093 | -116.3223 | 0.009156 | -0.091552 | -4.6692 | 116.3498 | 114.3127 | 114.4043 | -120.1309 | -0.022888 | 0.064087 | -0.24261 | 120.6207 | 118.8904 | 118.8263 | -0.29755 | 116.6245 | 1.1627 | 81.1066 | -121.3852 | 121.051 | 120.9961 | 116.0385 | -121.2296
1835.6406 | 121.4676 | -116.4551 | 4.7928 | 0.67491 | 0.050892 | -0.0070041 | 0.36609 | 0.02349 | 0.64349 | -0.033876 | 0.40315 | 3.9569 | 0.051988 | 0.10862 | 3.1993 | 0.066119 | -115.361 | 0.013733 | -35.202 | -2.3346 | 0.2243 | -116.4551 | -116.5741 | 4.1565 | -0.21973 | 2.417 | 4.5181 | 4.5044 | -116.5009 | -116.423 | 0 | -0.11902 | -4.5685 | 116.4688 | 114.1205 | 114.2395 | -120.1538 | -0.045776 | 0.032043 | -0.27466 | 120.6116 | 118.8721 | 118.84 | -0.28839 | 116.6794 | 1.0941 | 81.2531 | -121.3669 | 120.9732 | 120.9595 | 116.2354 | -121.2158
1836.6406 | 121.3623 | -116.5237 | 4.8248 | 0.82749 | 0.038075 | -0.015549 | 0.3725 | 0.026694 | 0.6531 | -0.032808 | 0.4947 | 3.9547 | 0.051988 | 0.10007 | 3.1993 | 0.068255 | -114.9994 | -0.068665 | -35.1517 | -2.5177 | 0.24261 | -116.478 | -116.6382 | 4.0695 | -0.40741 | 2.3209 | 4.541 | 4.5044 | -116.5512 | -116.4963 | 0.045777 | -0.11444 | -4.5822 | 116.4551 | 114.006 | 114.1205 | -119.8242 | -0.027465 | 0.027466 | -0.28381 | 120.5933 | 118.8446 | 118.8171 | -0.32043 | 116.7664 | 1.5244 | 81.3721 | -121.463 | 121.0648 | 121.0281 | 116.1163 | -121.3211
1837.6406 | 121.3989 | -116.5466 | 4.7882 | 0.50706 | 0.079732 | -0.0016631 | 0.38211 | -0.0085541 | 0.65096 | -0.044557 | 2.2647 | 3.9611 | 0.037034 | 0.096869 | 3.2014 | 0.069323 | -115.1916 | -0.059509 | -35.1059 | -2.4582 | 0.24261 | -116.4322 | -116.5741 | 4.0741 | -0.36163 | 2.2934 | 4.5639 | 4.5181 | -116.5833 | -116.5009 | 0.11444 | -0.027466 | -4.5456 | 116.4871 | 114.0884 | 114.1159 | -119.9799 | -0.036621 | 0.045777 | -0.2243 | 120.6207 | 118.84 | 118.7943 | -0.27008 | 116.7892 | 1.355 | 81.4407 | -121.3623 | 121.1105 | 121.0648 | 116.185 | -121.2891
1838.6875 | 121.3623 | -116.4688 | 4.8843 | 0.2324 | 0.044484 | -0.042252 | 0.37891 | 0.0085359 | 0.65951 | -0.027467 | 0.20479 | 3.9665 | 0.060533 | 0.08512 | 3.1993 | 0.06505 | -115.3152 | 0.004578 | -34.9823 | -2.1469 | 0.21973 | -116.4322 | -116.5512 | 4.1611 | -0.36163 | 2.2842 | 4.5914 | 4.5547 | -116.4688 | -116.4185 | 0.036621 | -0.082397 | -4.6646 | 116.4734 | 114.3219 | 114.4043 | -120.1996 | 0 | 0.050354 | -0.29297 | 120.6299 | 118.7531 | 118.7027 | -0.32959 | 116.6885 | 1.1536 | 81.4865 | -121.4355 | 121.0602 | 121.0236 | 116.1072 | -121.3028
1839.6406 | 121.4676 | -116.6016 | 4.7379 | 0.52232 | 0.061574 | -0.0080721 | 0.38104 | 0.0063999 | 0.64135 | -0.032808 | 0.50996 | 3.9622 | 0.05092 | 0.10007 | 3.2068 | 0.080004 | -115.4114 | -0.050354 | -34.6802 | -2.0187 | 0.25177 | -116.597 | -116.7023 | 3.978 | -0.40741 | 2.1835 | 4.454 | 4.4266 | -116.6061 | -116.5237 | 0.004577 | -0.10071 | -4.4861 | 116.5512 | 114.5828 | 114.6835 | -120.1492 | -0.004578 | 0.077819 | -0.28381 | 120.5795 | 118.7851 | 118.7073 | -0.31128 | 116.8533 | 1.1902 | 81.9214 | -121.4401 | 121.0556 | 121.0281 | 116.1942 | -121.2616
1840.6406 | 121.3898 | -116.1575 | 5.1636 | 2.4144 | 0.044484 | 0.021835 | 0.37784 | 0.0042639 | 0.63067 | -0.048829 | 0.66255 | 3.9515 | 0.051988 | 0.099006 | 3.1961 | 0.057574 | -114.9582 | -0.036621 | -34.6207 | -2.6733 | 0.23804 | -116.1346 | -116.2354 | 4.454 | -0.36621 | 2.6642 | 4.8935 | 4.8706 | -116.1942 | -116.1163 | 0.022888 | -0.07782 | -4.9255 | 116.1209 | 113.4842 | 113.562 | -120.1218 | -0.036621 | 0.041199 | -0.27008 | 120.6116 | 118.8217 | 118.7805 | -0.29297 | 116.3956 | 1.1993 | 81.5369 | -121.3989 | 121.051 | 121.0281 | 115.7913 | -121.2799
1841.6875 | 121.4127 | -116.5695 | 4.7333 | -0.11855 | 0.066914 | -0.00059506 | 0.37143 | 0.020285 | 0.64242 | -0.033876 | -0.085129 | 3.9537 | 0.055192 | 0.080848 | 3.194 | 0.068255 | -115.4343 | -0.009155 | -34.6115 | -2.1835 | 0.23346 | -116.5878 | -116.6977 | 4.0009 | -0.33875 | 2.2842 | 4.4861 | 4.4586 | -116.597 | -116.5558 | -0.018311 | -0.12817 | -4.4998 | 116.5604 | 114.386 | 114.5142 | -120.1675 | -0.027466 | 0.013733 | -0.24719 | 120.5704 | 118.8538 | 118.84 | -0.27466 | 116.803 | 1.1353 | 81.958 | -121.431 | 121.0556 | 121.0281 | 116.2308 | -121.2891
1842.6406 | 121.3486 | -116.5558 | 4.7516 | 0.14085 | 0.042347 | -0.013413 | 0.37891 | 0.016013 | 0.64883 | -0.034944 | 0.571 | 3.9633 | 0.055192 | 0.08512 | 3.2057 | 0.075732 | -115.4663 | -0.082397 | -34.6802 | -2.5177 | 0.22888 | -116.5421 | -116.684 | 3.9825 | -0.41199 | 2.2522 | 4.4769 | 4.4312 | -116.6199 | -116.5512 | 0.013733 | -0.12817 | -4.5227 | 116.4734 | 114.0381 | 114.1663 | -120.2179 | -0.064087 | 0.004578 | -0.27466 | 120.5383 | 118.808 | 118.8034 | -0.32043 | 116.7847 | 1.0895 | 81.8756 | -121.4355 | 121.0327 | 120.9869 | 116.1438 | -121.3028
1843.6406 | 121.3257 | -116.684 | 4.6738 | 0.32395 | 0.060505 | -0.010208 | 0.3725 | 0.017081 | 0.65844 | -0.038148 | 0.70833 | 3.9729 | 0.062669 | 0.087256 | 3.2025 | 0.072527 | -115.1459 | -0.082397 | -34.639 | -1.9043 | 0.22888 | -116.6016 | -116.7389 | 3.8956 | -0.42114 | 2.1561 | 4.4037 | 4.3716 | -116.7343 | -116.6382 | 0.082398 | -0.054932 | -4.4449 | 116.6016 | 114.7797 | 114.8346 | -119.8196 | -0.050354 | 0.045776 | -0.27008 | 120.5795 | 118.84 | 118.7943 | -0.30212 | 116.9128 | 1.5381 | 82.045 | -121.4127 | 121.0876 | 121.0556 | 116.2628 | -121.312
1844.6406 | 121.3898 | -116.3773 | 4.9713 | 0.55284 | 0.04662 | 0.0015409 | 0.38852 | 0.010672 | 0.65524 | -0.033876 | 4.6298 | 3.9622 | 0.043443 | 0.092597 | 3.2004 | 0.072527 | -114.7202 | -0.054932 | -34.6207 | -2.298 | 0.26093 | -116.3361 | -116.4642 | 4.2068 | -0.29297 | 2.4811 | 4.715 | 4.6829 | -116.391 | -116.304 | 0.041198 | -0.086975 | -4.7104 | 116.3223 | 114.0793 | 114.1663 | -119.6915 | -0.013733 | 0.073242 | -0.25635 | 120.5841 | 118.8583 | 118.7851 | -0.28839 | 116.6382 | 1.6571 | 81.7566 | -121.4355 | 121.0922 | 121.0602 | 116.0843 | -121.2753
1845.6406 | 121.3394 | -116.4688 | 4.8798 | 0.53758 | 0.045552 | 0.010086 | 0.38425 | 0.0053319 | 0.64776 | -0.036012 | 0.571 | 3.9569 | 0.071214 | 0.091529 | 3.1929 | 0.087481 | -115.1688 | -0.054932 | -34.6115 | -2.6779 | 0.25177 | -116.4368 | -116.5741 | 4.1061 | -0.19226 | 2.4353 | 4.6188 | 4.5685 | -116.4871 | -116.4368 | 0.032043 | -0.10529 | -4.628 | 116.4139 | 113.7909 | 113.8962 | -120.0485 | -0.018311 | 0.032043 | -0.26093 | 120.575 | 118.9041 | 118.8721 | -0.31128 | 116.7206 | 1.3 | 81.8573 | -121.4539 | 121.0876 | 121.0373 | 116.2766 | -121.3165
1846.6406 | 121.2982 | -116.5329 | 4.8248 | 0.50706 | 0.053029 | 0.0015409 | 0.37998 | 0.02349 | 0.63922 | -0.046693 | 0.66255 | 3.9558 | 0.063737 | 0.090461 | 3.1908 | 0.066119 | -115.3976 | -0.073242 | -34.5108 | -2.2018 | 0.23804 | -116.5192 | -116.6473 | 4.0421 | -0.43488 | 2.3254 | 4.5273 | 4.5044 | -116.5421 | -116.4963 | 0.013733 | -0.11444 | -4.5868 | 116.4597 | 114.3311 | 114.4455 | -120.2225 | -0.009155 | 0.036621 | -0.29755 | 120.575 | 118.8583 | 118.8217 | -0.32043 | 116.7709 | 1.1353 | 82.0221 | -121.4722 | 121.0602 | 121.0373 | 116.098 | -121.3211
1847.6406 | 121.2753 | -116.423 | 4.8752 | 0.4918 | 0.037007 | -0.0080721 | 0.36716 | 0.014945 | 0.6499 | -0.046693 | 0.55574 | 3.9569 | 0.05092 | 0.089393 | 3.1929 | 0.053301 | -114.418 | -0.054932 | -34.021 | -2.0966 | 0.23346 | -116.4185 | -116.5787 | 4.1336 | -0.46692 | 2.2934 | 4.6097 | 4.5776 | -116.4963 | -116.4459 | 0.004578 | -0.15564 | -4.6417 | 116.3681 | 114.3265 | 114.4821 | -119.2932 | -0.073242 | -0.022888 | -0.2655 | 120.5566 | 118.7164 | 118.7393 | -0.29755 | 116.6565 | 2.005 | 82.402 | -121.4539 | 121.0327 | 121.0007 | 115.9561 | -121.3211
1848.6406 | 121.3943 | -116.5375 | 4.7607 | 1.4073 | 0.032734 | 0.0090179 | 0.36716 | 0.013877 | 0.63708 | -0.041353 | 0.63203 | 3.9558 | 0.051988 | 0.10969 | 3.194 | 0.060778 | -115.3564 | -0.036621 | -34.3094 | -2.0325 | 0.22888 | -116.5146 | -116.6336 | 4.0787 | -0.41657 | 2.2705 | 4.5181 | 4.4861 | -116.5604 | -116.4871 | 0.022889 | -0.09613 | -4.5319 | 116.5009 | 114.505 | 114.6011 | -120.1172 | -0.022888 | 0.050354 | -0.24261 | 120.6162 | 118.808 | 118.7576 | -0.27466 | 116.7664 | 1.181 | 82.2281 | -121.3943 | 121.0556 | 121.0236 | 116.1209 | -121.2479
1849.6406 | 121.4081 | -116.5329 | 4.7974 | -2.4837 | 0.032734 | 0.0079499 | 0.38211 | 0.02349 | 0.63067 | -0.026399 | 0.571 | 3.9547 | 0.055192 | 0.092597 | 3.1854 | 0.060778 | -115.0223 | 0 | -34.2819 | -2.092 | 0.25177 | -116.4734 | -116.6061 | 4.0833 | -0.42114 | 2.2842 | 4.5319 | 4.4998 | -116.5604 | -116.478 | 0.059509 | -0.073242 | -4.5456 | 116.5329 | 114.4409 | 114.5142 | -119.8196 | -0.027466 | 0.054932 | -0.2655 | 120.6162 | 118.8171 | 118.7622 | -0.29755 | 116.7847 | 1.5106 | 82.251 | -121.4035 | 121.0648 | 121.0327 | 116.1118 | -121.2753
1850.6406 | 121.3394 | -116.4963 | 4.8981 | 0.43077 | 0.050892 | 0.0068819 | 0.37998 | 0.018149 | 0.63708 | -0.03708 | 0.54048 | 3.9473 | 0.049852 | 0.087256 | 3.195 | 0.054369 | -115.1825 | -0.064087 | -34.0714 | -2.6642 | 0.2243 | -116.4093 | -116.5558 | 4.129 | -0.43488 | 2.3483 | 4.6143 | 4.5822 | -116.5054 | -116.4459 | 0.086975 | -0.059509 | -4.6738 | 116.4322 | 113.8321 | 113.8916 | -120.0806 | -0.009155 | 0.050354 | -0.28381 | 120.6253 | 118.8446 | 118.7943 | -0.31586 | 116.7206 | 1.3138 | 82.4249 | -121.4539 | 121.1105 | 121.0785 | 116.0614 | -121.344
1851.6406 | 121.4127 | -116.5375 | 4.7974 | 0.52232 | 0.064778 | 0.00047294 | 0.33939 | 0.0074679 | 0.64456 | -0.053102 | 0.98299 | 3.9601 | 0.053056 | 0.11396 | 3.1918 | 0.073595 | -115.004 | -0.16937 | -33.8196 | -2.1194 | 0.25177 | -116.51 | -116.6336 | 4.0421 | -0.40741 | 2.2751 | 4.5227 | 4.4952 | -116.5649 | -116.5329 | 0.027466 | -0.09613 | -4.5456 | 116.3681 | 114.418 | 114.5142 | -119.8013 | -0.027465 | 0.004578 | -0.27466 | 120.5795 | 118.8126 | 118.808 | -0.30212 | 116.7892 | 1.5335 | 82.7179 | -121.431 | 121.0602 | 121.0327 | 116.1301 | -121.3303
1852.6406 | 121.376 | -116.5833 | 4.7424 | 0.55284 | 0.040211 | 0.0015409 | 0.37677 | 0.016013 | 0.65417 | -0.0071733 | 1.0593 | 3.9601 | 0.057328 | 0.10648 | 3.1982 | 0.071459 | -114.6286 | 0.041199 | -33.5266 | -2.1561 | 0.24261 | -116.51 | -116.6519 | 4.0466 | -0.43488 | 2.2339 | 4.4952 | 4.4724 | -116.629 | -116.5375 | 0.073242 | -0.068665 | -4.4998 | 116.6245 | 114.4272 | 114.4958 | -119.371 | -0.045776 | 0.045776 | -0.24719 | 120.6299 | 118.8171 | 118.7714 | -0.27008 | 116.8259 | 1.9547 | 83.0566 | -121.3943 | 121.0785 | 121.0556 | 116.1484 | -121.2799
1853.6406 | 121.376 | -116.6565 | 4.6967 | 0.50706 | 0.051961 | 0.0026089 | 0.37891 | 0.016013 | 0.64349 | -0.032808 | 2.5241 | 3.9569 | 0.058397 | 0.10221 | 3.1908 | 0.070391 | -115.4984 | -0.050354 | -33.4808 | -2.655 | 0.25635 | -116.5329 | -116.7114 | 3.9734 | -0.44403 | 2.1835 | 4.4449 | 4.4128 | -116.6885 | -116.6016 | 0.1236 | -0.054932 | -4.4403 | 116.6061 | 114.0015 | 114.0564 | -120.195 | -0.032044 | 0.054932 | -0.25177 | 120.6299 | 118.84 | 118.7851 | -0.28381 | 116.9128 | 1.1581 | 83.1757 | -121.4081 | 121.1014 | 121.0693 | 116.2125 | -121.2982
1854.6406 | 121.431 | -116.5878 | 4.7424 | 0.55284 | 0.057301 | 0.0090179 | 0.37143 | 0.0085359 | 0.64242 | -0.028535 | 0.70833 | 3.9462 | 0.048783 | 0.097938 | 3.194 | 0.0768 | -115.2969 | -0.022888 | -33.0414 | -2.5955 | 0.23346 | -116.5604 | -116.6794 | 4.0512 | -0.39368 | 2.2842 | 4.4769 | 4.4449 | -116.6336 | -116.5421 | 0.027466 | -0.091552 | -4.509 | 116.5649 | 113.9923 | 114.0839 | -120.0394 | -0.045776 | 0.045777 | -0.2655 | 120.639 | 118.8721 | 118.8263 | -0.29755 | 116.8213 | 1.2909 | 83.5464 | -121.4218 | 121.0648 | 121.0327 | 116.1942 | -121.2845
1855.6406 | 121.4172 | -116.4963 | 4.8203 | 0.56809 | 0.027394 | 0.0047449 | 0.37784 | 0.024558 | 0.64242 | -0.036012 | 0.63203 | 3.9515 | 0.060533 | 0.094733 | 3.1961 | 0.061846 | -115.1825 | -0.036621 | -33.403 | -2.6779 | 0.22888 | -116.4551 | -116.5878 | 4.1519 | -0.40283 | 2.3712 | 4.5731 | 4.5273 | -116.5237 | -116.4505 | 0.041199 | -0.091553 | -4.5914 | 116.4597 | 113.8184 | 113.9099 | -120.0027 | -0.027466 | 0.045777 | -0.24719 | 120.6482 | 118.8675 | 118.8217 | -0.29297 | 116.7252 | 1.3138 | 83.0933 | -121.4081 | 121.0693 | 121.0236 | 116.0934 | -121.2708
1856.6406 | 121.3898 | -116.5192 | 4.8157 | 0.27818 | 0.037007 | -0.014481 | 0.36502 | 0.014945 | 0.6531 | -0.036012 | 0.43367 | 3.9611 | 0.058397 | 0.10435 | 3.1929 | 0.058642 | -114.7156 | -0.073242 | -33.2703 | -2.1011 | 0.2243 | -116.5283 | -116.6473 | 4.0237 | -0.45319 | 2.2888 | 4.4998 | 4.4815 | -116.5787 | -116.4917 | -0.009155 | -0.12817 | -4.5914 | 116.4459 | 114.418 | 114.5462 | -119.5312 | -0.059509 | 0.027466 | -0.31586 | 120.5429 | 118.808 | 118.7805 | -0.33417 | 116.7435 | 1.8036 | 83.2489 | -121.463 | 121.019 | 121.0007 | 116.066 | -121.3074
1857.6406 | 121.3669 | -116.629 | 4.7104 | 0.33921 | 0.044484 | 0.0058129 | 0.38425 | 0.018149 | 0.65737 | -0.03708 | 0.571 | 3.9558 | 0.046647 | 0.099006 | 3.1961 | 0.061846 | -115.4755 | -0.07782 | -33.4717 | -2.4765 | 0.24719 | -116.5833 | -116.7252 | 3.9642 | -0.43488 | 2.211 | 4.4495 | 4.4174 | -116.6748 | -116.6061 | 0.045776 | -0.096131 | -4.4632 | 116.5512 | 114.1525 | 114.2487 | -120.1859 | -0.045777 | 0.022888 | -0.26093 | 120.5933 | 118.84 | 118.8171 | -0.29297 | 116.8762 | 1.1536 | 83.1573 | -121.4355 | 121.0785 | 121.0464 | 116.1942 | -121.3165
1858.6406 | 121.3943 | -116.7389 | 4.6005 | 0.4918 | 0.041279 | -0.019821 | 0.35221 | 0.018149 | 0.62106 | -0.031739 | 0.70833 | 3.9515 | 0.049852 | 0.090461 | 3.1854 | 0.068255 | -115.4297 | 0 | -33.1146 | -2.1561 | 0.24719 | -116.6977 | -116.8121 | 3.8818 | -0.4303 | 2.1194 | 4.335 | 4.303 | -116.7801 | -116.7252 | 0.041199 | -0.073242 | -4.3533 | 116.7389 | 114.5828 | 114.6561 | -120.0302 | -0.041198 | 0.013733 | -0.2655 | 120.6207 | 118.8583 | 118.8446 | -0.29755 | 116.9861 | 1.3092 | 83.6243 | -121.4127 | 121.0739 | 121.0419 | 116.3086 | -121.3257
1859.6875 | 121.4081 | -116.8213 | 4.5136 | 0.15611 | 0.055165 | -0.046524 | 0.38104 | 0.012809 | 0.64776 | -0.028535 | 0.26582 | 3.9537 | 0.043443 | 0.097938 | 3.2014 | 0.05971 | -115.1596 | -0.013733 | -33.1467 | -2.5177 | 0.24261 | -116.7755 | -116.9037 | 3.7994 | -0.3891 | 2.0737 | 4.2892 | 4.2343 | -116.8579 | -116.7984 | 0.045776 | -0.082398 | -4.2709 | 116.8076 | 114.3036 | 114.386 | -119.6732 | -0.036621 | 0.022888 | -0.2243 | 120.6207 | 118.895 | 118.8721 | -0.27924 | 117.0639 | 1.6617 | 83.6746 | -121.4172 | 121.1105 | 121.0556 | 116.4322 | -121.312
1860.6406 | 121.3898 | -116.6428 | 4.7241 | 0.4918 | 0.076527 | 0.00047294 | 0.37891 | 0.0085359 | 0.64135 | -0.027467 | 0.47945 | 3.9537 | 0.07335 | 0.10114 | 3.1961 | 0.054369 | -115.2008 | -0.045776 | -33.1284 | -2.7054 | 0.23346 | -116.5695 | -116.7023 | 4.0741 | -0.47607 | 2.243 | 4.4724 | 4.4266 | -116.6702 | -116.6199 | 0.073242 | -0.05951 | -4.4907 | 116.597 | 113.9374 | 113.9969 | -119.9249 | -0.027466 | 0.022888 | -0.25177 | 120.7169 | 118.8858 | 118.8629 | -0.29755 | 116.8762 | 1.442 | 83.5144 | -121.4264 | 121.1151 | 121.0693 | 116.1667 | -121.344
1861.6406 | 121.4172 | -116.5695 | 4.8019 | 0.14085 | 0.038075 | -0.0059361 | 0.38959 | 0.014945 | 0.64776 | -0.029603 | 0.63203 | 3.943 | 0.053056 | 0.10221 | 3.1982 | 0.063982 | -115.2237 | -0.041199 | -33.0551 | -2.8107 | 0.22888 | -116.5283 | -116.6428 | 4.0604 | -0.40741 | 2.33 | 4.5044 | 4.4815 | -116.6107 | -116.5329 | 0.041199 | -0.073242 | -4.5731 | 116.5283 | 113.7588 | 113.8321 | -120.0256 | -0.041199 | 0.036621 | -0.29755 | 120.6299 | 118.8995 | 118.8629 | -0.32043 | 116.7984 | 1.3458 | 83.5144 | -121.4447 | 121.0739 | 121.051 | 116.1621 | -121.3348
1862.6406 | 121.4127 | -116.5146 | 4.8248 | -0.94253 | 0.018849 | -0.0059361 | 0.35968 | 0.018149 | 0.64242 | -0.031739 | 0.52522 | 3.9483 | 0.049852 | 0.10755 | 3.1908 | 0.072527 | -115.0085 | 0 | -32.6797 | -2.6459 | 0.25635 | -116.4642 | -116.6153 | 4.1153 | -0.41657 | 2.3575 | 4.5822 | 4.5364 | -116.5329 | -116.478 | 0.050354 | -0.10071 | -4.5685 | 116.5146 | 113.8687 | 113.9694 | -119.8334 | -0.018311 | 0.036621 | -0.24262 | 120.6299 | 118.8721 | 118.8354 | -0.28839 | 116.7709 | 1.506 | 83.8348 | -121.4401 | 121.0968 | 121.051 | 116.098 | -121.3028
1863.6406 | 121.3623 | -116.7847 | 4.5868 | 0.40025 | 0.056233 | -0.028366 | 0.37357 | 0.0063999 | 0.65737 | -0.030671 | 0.66255 | 3.9505 | 0.046647 | 0.097938 | 3.1886 | 0.063982 | -115.3976 | -0.10071 | -33.0048 | -2.0462 | 0.22888 | -116.7297 | -116.8533 | 3.7949 | -0.45319 | 2.092 | 4.335 | 4.2801 | -116.8076 | -116.7526 | 0.054932 | -0.068665 | -4.3579 | 116.684 | 114.7385 | 114.8071 | -119.9844 | -0.022888 | 0.032043 | -0.25177 | 120.5795 | 118.8766 | 118.8446 | -0.3067 | 117.0135 | 1.387 | 83.7799 | -121.4401 | 121.1197 | 121.0648 | 116.3315 | -121.3394
1864.6406 | 121.376 | -116.7984 | 4.5822 | 0.38499 | 0.041279 | -0.00059506 | 0.3725 | 0.026694 | 0.6499 | -0.029603 | 0.22005 | 3.9633 | 0.055192 | 0.088325 | 3.194 | 0.062914 | -115.2603 | -0.068665 | -32.5195 | -2.179 | 0.23346 | -116.7709 | -116.8808 | 3.8132 | -0.45776 | 2.0874 | 4.3167 | 4.2938 | -116.8121 | -116.7526 | 0.027466 | -0.082397 | -4.3488 | 116.7297 | 114.6194 | 114.7018 | -119.8425 | -0.013733 | 0.045776 | -0.2655 | 120.6116 | 118.8858 | 118.84 | -0.28839 | 117.0319 | 1.5381 | 84.2789 | -121.463 | 121.1151 | 121.0922 | 116.3406 | -121.3348
1865.6406 | 121.2753 | -116.4688 | 4.8614 | 0.38499 | 0.056233 | -0.0059361 | 0.3725 | 0.0042639 | 0.65096 | -0.041353 | 0.54048 | 3.9526 | 0.046647 | 0.10435 | 3.1929 | 0.056505 | -115.1321 | -0.054932 | -32.4142 | -2.504 | 0.24719 | -116.4871 | -116.5787 | 4.0924 | -0.43488 | 2.3895 | 4.6051 | 4.5319 | -116.5466 | -116.4505 | -0.018311 | -0.10986 | -4.6143 | 116.4139 | 113.9648 | 114.0747 | -119.9936 | -0.07782 | 0.018311 | -0.25635 | 120.5612 | 118.8583 | 118.84 | -0.32959 | 116.716 | 1.3367 | 84.0546 | -121.4401 | 121.0739 | 121.0007 | 116.0339 | -121.312
1866.6875 | 121.4676 | -116.629 | 4.6875 | 0.61387 | 0.047688 | -0.0016631 | 0.3725 | 0.012809 | 0.63815 | -0.038148 | 0.78462 | 3.9579 | 0.05626 | 0.099006 | 3.1875 | 0.068255 | -115.3793 | -0.004578 | -33.0185 | -2.3758 | 0.2243 | -116.6016 | -116.7206 | 4.0421 | -0.35706 | 2.3529 | 4.4266 | 4.3854 | -116.6565 | -116.5833 | 0.027466 | -0.091553 | -4.4632 | 116.6245 | 114.2532 | 114.3448 | -120.0668 | -0.027466 | 0.045776 | -0.26093 | 120.6711 | 118.9819 | 118.9362 | -0.30212 | 116.8533 | 1.2497 | 83.6105 | -121.4081 | 121.0556 | 121.0144 | 116.272 | -121.2708
1867.6406 | 121.3669 | -116.8625 | 4.4998 | 0.29344 | 0.058369 | -0.012345 | 0.38639 | 0.021354 | 0.64242 | -0.043489 | 0.3116 | 3.9515 | 0.058397 | 0.091529 | 3.1993 | 0.061846 | -115.6174 | -0.073242 | -32.9727 | -2.536 | 0.22888 | -116.8167 | -116.9403 | 3.7125 | -0.45319 | 2.0325 | 4.2389 | 4.1977 | -116.8991 | -116.8076 | 0.045777 | -0.07782 | -4.2709 | 116.7892 | 114.3265 | 114.4043 | -120.1172 | -0.036621 | 0.054932 | -0.26093 | 120.575 | 118.895 | 118.84 | -0.30212 | 117.0914 | 1.2451 | 83.8898 | -121.4401 | 121.1014 | 121.0602 | 116.4093 | -121.3074
1868.6406 | 121.3943 | -116.9174 | 4.4998 | 0.33921 | 0.041279 | 0.0047449 | 0.38104 | 0.014945 | 0.63922 | -0.036012 | 0.52522 | 3.9473 | 0.040239 | 0.096869 | 3.1865 | 0.070391 | -115.7272 | -0.064087 | -32.6202 | -2.7512 | 0.23804 | -116.8442 | -116.9861 | 3.7033 | -0.42114 | 1.973 | 4.1977 | 4.1794 | -116.8945 | -116.8442 | 0.073242 | -0.068665 | -4.2618 | 116.8533 | 114.1663 | 114.2349 | -120.2271 | 0.022888 | 0.073242 | -0.30212 | 120.6207 | 118.8904 | 118.8171 | -0.32043 | 117.1555 | 1.1902 | 84.2972 | -121.4859 | 121.1151 | 121.0968 | 116.4963 | -121.344
1869.6406 | 121.4355 | -116.9174 | 4.454 | -1.5224 | 0.060505 | 0.0015409 | 0.39066 | 0.027762 | 0.63601 | -0.031739 | 0.60152 | 3.9558 | 0.059465 | 0.096869 | 3.1886 | 0.067187 | -115.8005 | -0.068665 | -32.9361 | -2.7466 | 0.25177 | -116.8808 | -116.9998 | 3.717 | -0.43488 | 2.0554 | 4.184 | 4.1519 | -116.922 | -116.835 | 0.036621 | -0.082398 | -4.2023 | 116.8488 | 114.1708 | 114.2532 | -120.2545 | -0.004578 | 0.082397 | -0.27008 | 120.6345 | 118.9728 | 118.8904 | -0.30212 | 117.1692 | 1.1169 | 83.9813 | -121.4539 | 121.1014 | 121.0693 | 116.4825 | -121.2891
1870.6406 | 121.3669 | -116.8945 | 4.4861 | 0.24766 | 0.065846 | -0.037979 | 0.37464 | 0.019217 | 0.64776 | -0.042421 | 0.32686 | 3.9611 | 0.07335 | 0.092597 | 3.2057 | 0.049029 | -115.6082 | -0.018311 | -32.515 | -2.0554 | 0.23804 | -116.8396 | -116.9449 | 3.7399 | -0.41657 | 2.0645 | 4.2023 | 4.1702 | -116.8808 | -116.8625 | 0.054931 | -0.050354 | -4.248 | 116.8762 | 114.8392 | 114.8895 | -120.0943 | 0.013733 | 0.032043 | -0.28381 | 120.6345 | 118.959 | 118.927 | -0.31586 | 117.1326 | 1.2863 | 84.3796 | -121.431 | 121.0968 | 121.0648 | 116.478 | -121.3486
1871.6875 | 121.431 | -116.5192 | 4.8294 | 0.034038 | 0.053029 | 0.0015409 | 0.38639 | 0.02349 | 0.6499 | -0.03708 | 0.17427 | 3.9558 | 0.053056 | 0.10114 | 3.1865 | 0.069323 | -115.4297 | 0.027466 | -32.9132 | -1.9501 | 0.24719 | -116.5558 | -116.6794 | 4.0787 | -0.33875 | 2.3895 | 4.5136 | 4.4769 | -116.4963 | -116.4642 | -0.036621 | -0.16022 | -4.5822 | 116.5466 | 114.5691 | 114.7293 | -120.2591 | 0.022888 | 0.054932 | -0.31586 | 120.5978 | 118.9087 | 118.8538 | -0.35248 | 116.7664 | 1.0895 | 83.606 | -121.5088 | 121.0327 | 120.9961 | 116.1804 | -121.2936
1872.6406 | 121.3852 | -116.423 | 4.9255 | 0.2324 | 0.062642 | 0.00047294 | 0.36823 | 0.018149 | 0.65203 | -0.033876 | 0.35738 | 3.9526 | 0.065873 | 0.086188 | 3.1972 | 0.069323 | -115.274 | -0.041199 | -32.7667 | -1.9547 | 0.21515 | -116.4047 | -116.5237 | 4.1702 | -0.40283 | 2.5085 | 4.6646 | 4.6234 | -116.4734 | -116.4093 | 0.018311 | -0.10071 | -4.7104 | 116.3818 | 114.4684 | 114.5691 | -120.1996 | -0.050354 | 0.013733 | -0.26093 | 120.5933 | 118.9316 | 118.9178 | -0.30212 | 116.6382 | 1.149 | 83.6563 | -121.4493 | 121.0876 | 121.0464 | 116.0202 | -121.3348
1873.6406 | 121.3898 | -116.5146 | 4.8477 | 0.21714 | 0.060505 | -0.0016631 | 0.36823 | 0.020285 | 0.64028 | -0.043489 | 0.26582 | 3.959 | 0.046647 | 0.094733 | 3.1993 | 0.061846 | -115.0543 | -0.022888 | -32.4692 | -2.1332 | 0.21973 | -116.5054 | -116.597 | 4.097 | -0.42114 | 2.4261 | 4.5731 | 4.5547 | -116.5558 | -116.478 | 0.009155 | -0.082398 | -4.628 | 116.4917 | 114.3814 | 114.4638 | -119.902 | -0.041199 | 0.036621 | -0.27466 | 120.6116 | 118.9407 | 118.9041 | -0.29297 | 116.7343 | 1.4603 | 84.0454 | -121.4447 | 121.0876 | 121.0693 | 116.0934 | -121.3257
1874.6406 | 121.3943 | -116.4322 | 4.921 | 0.24766 | 0.055165 | 0.0026089 | 0.37998 | 0.0063999 | 0.65737 | -0.030671 | 0.35738 | 3.9579 | 0.040239 | 0.091529 | 3.1929 | 0.06505 | -115.0314 | -0.018311 | -32.1121 | -2.3392 | 0.21973 | -116.4139 | -116.51 | 4.1794 | -0.40283 | 2.4811 | 4.6783 | 4.6234 | -116.4917 | -116.3864 | 0.018311 | -0.07782 | -4.7012 | 116.4139 | 114.093 | 114.1708 | -119.9524 | -0.059509 | 0.045776 | -0.24261 | 120.6116 | 118.9133 | 118.8675 | -0.29755 | 116.6519 | 1.4008 | 84.3201 | -121.431 | 121.1105 | 121.0556 | 116.0294 | -121.3074
1875.6406 | 121.3486 | -116.3956 | 4.9622 | 0.3087 | 0.045552 | -0.0016631 | 0.36823 | 0.022422 | 0.63601 | -0.043489 | 0.64729 | 3.9515 | 0.051988 | 0.097938 | 3.1918 | 0.072527 | -115.2054 | -0.064087 | -32.2357 | -2.5955 | 0.21973 | -116.3498 | -116.5009 | 4.2023 | -0.46234 | 2.5177 | 4.7012 | 4.6692 | -116.4139 | -116.3681 | 0.045777 | -0.10529 | -4.7424 | 116.3315 | 113.8 | 113.9053 | -120.1675 | -0.01831 | 0.027466 | -0.26092 | 120.5978 | 118.9133 | 118.8858 | -0.29297 | 116.6153 | 1.1902 | 84.1599 | -121.463 | 121.0968 | 121.0648 | 115.9332 | -121.3303
1876.6406 | 121.3806 | -116.6611 | 4.7058 | 0.15611 | 0.04662 | 0.0058129 | 0.38532 | 0.014945 | 0.65417 | -0.036012 | 0.46419 | 3.943 | 0.057328 | 0.096869 | 3.1918 | 0.070391 | -115.4114 | -0.050354 | -32.4966 | -2.3895 | 0.21057 | -116.6245 | -116.7572 | 3.9505 | -0.43488 | 2.2614 | 4.4495 | 4.3991 | -116.6885 | -116.6199 | 0.036621 | -0.09613 | -4.4952 | 116.6107 | 114.2715 | 114.3677 | -120.1172 | -0.027466 | 0.041199 | -0.25635 | 120.6116 | 118.9224 | 118.8812 | -0.3067 | 116.8716 | 1.2497 | 84.1644 | -121.463 | 121.1105 | 121.0602 | 116.2262 | -121.3257
1877.6406 | 121.4081 | -116.6428 | 4.6692 | 0.12559 | 0.060505 | -0.0016631 | 0.36395 | 0.017081 | 0.63281 | -0.043489 | 0.38789 | 3.9419 | 0.069078 | 0.074439 | 3.1886 | 0.071459 | -115.5029 | 0.041199 | -32.222 | -2.0416 | 0.28839 | -116.5741 | -116.7068 | 3.9597 | -0.34332 | 2.298 | 4.422 | 4.3808 | -116.6794 | -116.5924 | 0.068664 | -0.064087 | -4.3808 | 116.684 | 114.6011 | 114.6652 | -120.1721 | -0.036621 | 0.050354 | -0.24719 | 120.6024 | 118.9407 | 118.8904 | -0.28839 | 116.9312 | 1.1398 | 84.4208 | -121.376 | 121.0648 | 121.0236 | 116.2994 | -121.2616
1878.6406 | 121.4081 | -116.9266 | 4.454 | 0.24766 | 0.062642 | -0.0038001 | 0.37357 | 0.012809 | 0.64776 | -0.034944 | 0.37263 | 3.9537 | 0.044511 | 0.099006 | 3.1961 | 0.067187 | -115.6128 | -0.036621 | -32.2174 | -2.243 | 0.2243 | -116.8625 | -116.9907 | 3.6942 | -0.39825 | 2.0233 | 4.1977 | 4.1428 | -116.9632 | -116.8808 | 0.064087 | -0.064087 | -4.2297 | 116.89 | 114.6835 | 114.7476 | -120.0668 | -0.036621 | 0.045777 | -0.25635 | 120.6207 | 118.9499 | 118.9041 | -0.31128 | 117.1509 | 1.3138 | 84.7092 | -121.4447 | 121.1243 | 121.0693 | 116.5283 | -121.3348
1879.6406 | 121.3989 | -117.0364 | 4.3442 | 0.14085 | 0.058369 | -0.0059361 | 0.37784 | 0.021354 | 0.64776 | -0.034944 | 0.37263 | 3.9526 | 0.058397 | 0.089393 | 3.195 | 0.071459 | -115.5853 | -0.027466 | -32.2128 | -2.3117 | 0.21973 | -116.9769 | -117.1188 | 3.5843 | -0.3891 | 1.9501 | 4.0695 | 4.0741 | -117.041 | -116.9952 | 0.059509 | -0.082397 | -4.1245 | 117.009 | 114.7247 | 114.8071 | -119.9295 | -0.004578 | 0.041199 | -0.27466 | 120.6207 | 118.9865 | 118.9453 | -0.27008 | 117.2562 | 1.4511 | 84.8236 | -121.463 | 121.106 | 121.1105 | 116.6473 | -121.3394
1880.6406 | 121.4081 | -116.9815 | 4.3762 | 0.50706 | 0.066914 | 0.0079499 | 0.37677 | 0.013877 | 0.63494 | -0.024263 | -0.16142 | 3.943 | 0.060533 | 0.10328 | 3.1801 | 0.069323 | -115.7684 | -0.054932 | -32.2678 | -2.7191 | 0.23346 | -116.9174 | -117.0914 | 3.6667 | -0.46234 | 1.9775 | 4.1153 | 4.0924 | -117.0364 | -116.954 | 0.064087 | -0.10986 | -4.1428 | 116.9266 | 114.2624 | 114.3723 | -120.1447 | -0.054932 | 0.027465 | -0.26093 | 120.6482 | 118.959 | 118.9316 | -0.28381 | 117.215 | 1.2131 | 84.7137 | -121.4676 | 121.0968 | 121.0739 | 116.5192 | -121.3303
1881.6875 | 121.3531 | -116.4551 | 4.8981 | 0.24766 | 0.090413 | -0.0038001 | 0.37036 | 0.020285 | 0.64562 | -0.039216 | 0.26582 | 3.9515 | 0.046647 | 0.093665 | 3.1972 | 0.058642 | -115.0818 | -0.059509 | -32.6157 | -2.6184 | 0.21973 | -116.423 | -116.5649 | 4.1199 | -0.44861 | 2.4307 | 4.6509 | 4.628 | -116.5146 | -116.423 | 0.032043 | -0.10986 | -4.6783 | 116.3956 | 113.8367 | 113.9465 | -119.9799 | -0.059509 | 0.032043 | -0.24719 | 120.575 | 118.8858 | 118.8538 | -0.27008 | 116.6748 | 1.3733 | 83.8394 | -121.463 | 121.106 | 121.0831 | 116.0065 | -121.3211
1882.6406 | 121.5088 | -116.4597 | 4.8386 | 0.049296 | -0.0025128 | 0.0026089 | 0.35861 | 0.0010589 | 0.5826 | -0.042421 | 0.41841 | 3.9312 | 0.03917 | 0.089393 | 3.1705 | 0.087481 | -115.0177 | 0.09613 | -32.5836 | -2.774 | 0.21973 | -116.423 | -116.5466 | 4.184 | -0.25177 | 2.5406 | 4.5731 | 4.5319 | -116.4734 | -116.423 | 0.036621 | -0.086975 | -4.6188 | 116.5558 | 113.6856 | 113.7726 | -119.8563 | -0.013733 | 0.036621 | -0.2655 | 120.6436 | 119.0002 | 118.9636 | -0.3067 | 116.6794 | 1.442 | 83.876 | -121.3852 | 121.0327 | 120.9915 | 116.2079 | -121.2616
1883.6406 | 121.3898 | -116.5192 | 4.8477 | 0.40025 | 0.047688 | -0.0027321 | 0.36716 | 0.0063999 | 0.65417 | -0.034944 | 0.26582 | 3.9494 | 0.054124 | 0.097938 | 3.2025 | 0.055437 | -114.5554 | -0.045776 | -32.2815 | -2.3071 | 0.21973 | -116.4688 | -116.5833 | 4.0924 | -0.44403 | 2.2797 | 4.6005 | 4.5364 | -116.5741 | -116.5009 | 0.050354 | -0.064087 | -4.628 | 116.4734 | 114.212 | 114.2761 | -119.4031 | -0.054932 | 0.018311 | -0.24719 | 120.6116 | 118.7988 | 118.7805 | -0.31128 | 116.7389 | 1.9638 | 84.2377 | -121.431 | 121.1197 | 121.0556 | 116.0751 | -121.3486
1884.6406 | 121.4264 | -116.4139 | 4.9164 | 0.064555 | 0.073323 | 0.011154 | 0.37998 | 0.017081 | 0.6563 | -0.043489 | 0.2353 | 3.9473 | 0.043443 | 0.094733 | 3.1993 | 0.063982 | -115.1047 | 0.11444 | -32.1945 | -2.4124 | 0.29297 | -116.3681 | -116.478 | 4.2114 | -0.35248 | 2.4353 | 4.6783 | 4.6326 | -116.4734 | -116.4185 | 0.045776 | -0.064087 | -4.6234 | 116.5283 | 114.0015 | 114.0656 | -120.0211 | -0.05951 | -0.004578 | -0.23804 | 120.6253 | 118.8492 | 118.8538 | -0.28381 | 116.7068 | 1.3092 | 84.2194 | -121.3943 | 121.0922 | 121.0464 | 116.0614 | -121.3348
1885.6406 | 121.3943 | -116.6977 | 4.6967 | 0.24766 | 0.057301 | 0.0015409 | 0.36075 | 0.010672 | 0.64456 | -0.026399 | 0.28108 | 3.9494 | 0.049852 | 0.10541 | 3.1875 | 0.061846 | -115.0543 | -0.013733 | -32.3776 | -2.4536 | 0.21973 | -116.6428 | -116.7709 | 3.9368 | -0.41657 | 2.1652 | 4.4266 | 4.3854 | -116.7252 | -116.6565 | 0.054932 | -0.073242 | -4.4769 | 116.684 | 114.2441 | 114.3173 | -119.751 | -0.027466 | 0.041199 | -0.27008 | 120.6345 | 118.8629 | 118.8217 | -0.31128 | 116.9174 | 1.6434 | 84.3201 | -121.4676 | 121.1243 | 121.0831 | 116.2811 | -121.3531
1886.6406 | 121.3852 | -116.7847 | 4.5959 | 0.24766 | 0.058369 | 0.0036769 | 0.3757 | 0.019217 | 0.64562 | -0.041353 | 0.20479 | 3.9473 | 0.062669 | 0.10114 | 3.1833 | 0.068255 | -115.5167 | -0.009155 | -32.2632 | -2.6459 | 0.2243 | -116.7343 | -116.8579 | 3.8544 | -0.39825 | 2.1057 | 4.3167 | 4.303 | -116.8259 | -116.7526 | 0.050354 | -0.073242 | -4.3716 | 116.7755 | 114.1388 | 114.212 | -120.1126 | -0.041199 | 0.032043 | -0.27924 | 120.639 | 118.8904 | 118.8583 | -0.29297 | 117.009 | 1.268 | 84.5215 | -121.4539 | 121.1014 | 121.0876 | 116.3864 | -121.3486
1887.6406 | 121.5454 | -116.4688 | 4.8111 | 0.12559 | 0.019917 | 0.015426 | 0.35007 | 0.0042639 | 0.58154 | -0.048829 | 0.34212 | 3.9312 | 0.03917 | 0.093665 | 3.1683 | 0.084276 | -114.9673 | 0.13733 | -32.254 | -2.3254 | 0.20142 | -116.4413 | -116.5558 | 4.1794 | 3.2913 | 2.5223 | 4.5502 | 4.5044 | -116.5146 | -116.4871 | 0.027466 | -0.086975 | -4.6097 | 116.6061 | 114.1434 | 114.2303 | -119.7784 | -0.045776 | -0.018311 | -0.26093 | 120.6482 | 118.9911 | 119.0094 | -0.3067 | 116.6702 | 1.5015 | 84.2148 | -121.3669 | 121.019 | 120.9732 | 119.7601 | -121.2982
1888.7031 | 121.3898 | -116.6565 | 4.7195 | -0.22536 | 0.023121 | 0.0058129 | 0.36182 | 0.018149 | 0.60717 | -0.044557 | 0.28108 | 3.9334 | 0.043443 | 0.080848 | 3.1801 | 0.058642 | -115.3702 | 0.036621 | -32.3822 | -2.7374 | 0.23346 | -116.5833 | -116.7114 | 3.978 | 3.6942 | 2.298 | 4.4586 | 4.4174 | -116.6931 | -116.6107 | 0.073242 | -0.054932 | -4.4861 | 116.6931 | 113.9191 | 113.974 | -120.0897 | -0.036621 | 0.045776 | -0.26092 | 120.6345 | 118.9545 | 118.9087 | -0.30212 | 116.89 | 1.2863 | 84.2743 | -121.431 | 121.1151 | 121.0739 | 120.3506 | -121.3303
1889.6406 | 121.3806 | -116.5924 | 4.8203 | 0.18663 | 0.057301 | 0.010086 | 0.37464 | 0.022422 | 0.66271 | -0.031739 | 0.17427 | 3.9344 | 0.05092 | 0.10648 | 3.1929 | 0.05971 | -115.2878 | -0.027466 | -32.1304 | -2.5452 | 0.21515 | -116.5329 | -116.6702 | 4.0192 | 3.7216 | 2.2888 | 4.5502 | 4.509 | -116.6382 | -116.5466 | 0.059509 | -0.07782 | -4.6051 | 116.5649 | 114.0472 | 114.1251 | -120.108 | -0.045777 | 0.045776 | -0.27008 | 120.6116 | 118.8812 | 118.8354 | -0.31128 | 116.8076 | 1.3046 | 84.462 | -121.4905 | 121.1426 | 121.1014 | 120.314 | -121.3669
1890.6406 | 121.3852 | -116.4871 | 4.8981 | 0.12559 | 0.059437 | 0.010086 | 0.39066 | 0.021354 | 0.65417 | -0.034944 | 0.18953 | 3.9451 | 0.057328 | 0.10114 | 3.1822 | 0.056505 | -115.1184 | 0.022888 | -32.254 | -2.1286 | 0.25635 | -116.4413 | -116.5741 | 4.1656 | 4.1107 | 2.4307 | 4.6051 | 4.5868 | -116.4963 | -116.4459 | 0.045777 | -0.086975 | -4.6417 | 116.51 | 114.3585 | 114.4455 | -120.0165 | -0.009155 | 0.041199 | -0.29297 | 120.6528 | 118.9178 | 118.8766 | -0.31128 | 116.7435 | 1.3687 | 84.2331 | -121.4722 | 121.0922 | 121.0739 | 120.5978 | -121.344
1891.6406 | 121.3989 | -116.6245 | 4.7882 | 0.55284 | 0.061574 | 0.01329 | 0.3757 | 0.01174 | 0.64135 | -0.036012 | 0.50996 | 3.943 | 0.058397 | 0.095801 | 3.1833 | 0.067187 | -115.3976 | -0.045776 | -32.3593 | -2.1103 | 0.25177 | -116.5649 | -116.684 | 4.0329 | 3.9368 | 2.3026 | 4.5136 | 4.4678 | -116.6061 | -116.5741 | 0.05951 | -0.059509 | -4.5364 | 116.5787 | 114.5142 | 114.5737 | -120.1859 | 0.018311 | 0.050354 | -0.27466 | 120.6573 | 118.927 | 118.8766 | -0.32043 | 116.8762 | 1.2268 | 84.2651 | -121.4722 | 121.138 | 121.0922 | 120.5612 | -121.3623
1892.6406 | 121.5363 | -116.4917 | 4.7928 | 0.62913 | 0.041279 | 0.0058129 | 0.35861 | 0.02349 | 0.63067 | -0.034944 | 0.67781 | 3.9398 | 0.061601 | 0.10648 | 3.1875 | 0.071459 | -115.4205 | 0.032043 | -32.3776 | -2.2476 | 0.21057 | -116.51 | -116.6061 | 4.1428 | -0.54474 | 2.4399 | 4.4998 | 4.4678 | -116.5512 | -116.4825 | -0.018311 | -0.11444 | -4.5822 | 116.5237 | 114.2441 | 114.3585 | -120.2133 | -0.059509 | 0.009155 | -0.29297 | 120.6345 | 118.9316 | 118.9224 | -0.32501 | 116.7023 | 1.0712 | 84.1141 | -121.3989 | 120.9915 | 120.9595 | 115.947 | -121.2753
1893.6406 | 121.3806 | -116.5604 | 4.8203 | 0.26292 | 0.056233 | -0.011276 | 0.38532 | 0.02349 | 0.65737 | -0.029603 | 0.25056 | 3.9408 | 0.05092 | 0.096869 | 3.1918 | 0.062914 | -115.3793 | -0.027466 | -32.2952 | -2.5818 | 0.21973 | -116.5146 | -116.6473 | 4.0787 | -0.56305 | 2.3483 | 4.5685 | 4.5181 | -116.597 | -116.5192 | 0.045777 | -0.086975 | -4.6005 | 116.5329 | 113.9786 | 114.0656 | -120.1996 | -0.036621 | 0.041199 | -0.25177 | 120.639 | 118.9087 | 118.8675 | -0.30212 | 116.7801 | 1.181 | 84.2651 | -121.4676 | 121.1288 | 121.0785 | 115.9973 | -121.3394
1894.6406 | 121.4218 | -116.7068 | 4.66 | 0.15611 | 0.051961 | 0.0015409 | 0.36182 | 0.010672 | 0.65203 | -0.029603 | 0.35738 | 3.9451 | 0.054124 | 0.091529 | 3.1811 | 0.05971 | -115.4892 | -0.013733 | -32.0618 | -2.4857 | 0.21515 | -116.6519 | -116.8121 | 3.9001 | -0.54016 | 2.1744 | 4.3854 | 4.3625 | -116.7709 | -116.6794 | 0.054931 | -0.10529 | -4.4449 | 116.6931 | 114.2212 | 114.3265 | -120.1492 | -0.064087 | 0.027466 | -0.27466 | 120.607 | 118.8812 | 118.8538 | -0.29755 | 116.922 | 1.2177 | 84.6451 | -121.4722 | 121.0922 | 121.0693 | 116.1667 | -121.3394
1895.6406 | 121.3852 | -116.6199 | 4.7791 | 0.2324 | 0.054097 | 0.0015409 | 0.37036 | 0.0063999 | 0.64456 | -0.044557 | 0.63203 | 3.9473 | 0.053056 | 0.097938 | 3.1908 | 0.06505 | -115.3839 | -0.10071 | -32.0206 | -2.7649 | 0.24261 | -116.5649 | -116.7068 | 4.0192 | -0.53558 | 2.2888 | 4.4998 | 4.4724 | -116.6245 | -116.5787 | 0.054932 | -0.086975 | -4.5364 | 116.5192 | 113.855 | 113.942 | -120.163 | -0.004578 | 0.041199 | -0.27924 | 120.639 | 118.9087 | 118.8675 | -0.3067 | 116.8625 | 1.236 | 84.5993 | -121.4859 | 121.1197 | 121.0922 | 116.0843 | -121.3577
1896.6406 | 121.3806 | -116.4459 | 4.9393 | 0.26292 | 0.067982 | -0.0048681 | 0.38211 | 0.0074679 | 0.64562 | -0.027467 | 0.58626 | 3.9473 | 0.065873 | 0.092597 | 3.1865 | 0.062914 | -115.2145 | -0.073242 | -31.9107 | -2.4902 | 0.23804 | -116.4047 | -116.5283 | 4.1611 | -0.57678 | 2.3712 | 4.6738 | 4.6509 | -116.5146 | -116.4047 | 0.041199 | -0.082397 | -4.7012 | 116.3727 | 113.9557 | 114.0381 | -120.1538 | -0.068664 | 0.041199 | -0.2655 | 120.607 | 118.8171 | 118.7759 | -0.28839 | 116.684 | 1.2314 | 84.5352 | -121.4676 | 121.1197 | 121.0968 | 115.8691 | -121.344
1897.6406 | 121.4676 | -116.2491 | 5.0583 | 0.41551 | 0.016713 | 0.0090179 | 0.33832 | 0.0096039 | 0.59222 | -0.042421 | 0.70833 | 3.9248 | 0.045579 | 0.092597 | 3.1737 | 0.071459 | -115.1596 | 0.050354 | -31.9473 | -2.7512 | 0.21973 | -116.2354 | -116.3589 | 4.3808 | -0.4715 | 2.623 | 4.7607 | 4.7562 | -116.2857 | -116.2354 | 0.013732 | -0.10986 | -4.8386 | 116.2994 | 113.4979 | 113.6078 | -120.2179 | -0.036622 | 0.013732 | -0.29755 | 120.6299 | 118.8721 | 118.8583 | -0.30212 | 116.4688 | 1.0895 | 84.3018 | -121.4172 | 121.0098 | 121.0052 | 115.7776 | -121.2936
1898.6875 | 121.4447 | -116.2811 | 5.072 | 0.049296 | 0.051961 | 0.0058129 | 0.38852 | 0.017081 | 0.64135 | -0.040284 | 0.11323 | 3.9302 | 0.049852 | 0.07978 | 3.1833 | 0.053301 | -115.0589 | 0.032043 | -31.9748 | -2.9297 | 0.25177 | -116.272 | -116.3864 | 4.3716 | -0.11444 | 2.5772 | 4.8019 | 4.7562 | -116.3544 | -116.2674 | 0.009155 | -0.10529 | -4.8203 | 116.3132 | 113.3514 | 113.4567 | -120.1309 | -0.073242 | 0.013733 | -0.27008 | 120.6528 | 118.8583 | 118.8446 | -0.31586 | 116.5329 | 1.2222 | 84.3063 | -121.4584 | 121.0831 | 121.0373 | 116.1667 | -121.3394
1899.6406 | 121.3852 | -116.3681 | 5.0537 | 0.20188 | 0.056233 | 0.010086 | 0.36395 | 0.012809 | 0.64562 | -0.041353 | 0.34212 | 3.9216 | 0.058397 | 0.10007 | 3.1811 | 0.062914 | -115.3244 | -0.041199 | -32.0572 | -2.7969 | 0.23346 | -116.3177 | -116.4368 | 4.2938 | 4.0604 | 2.4765 | 4.7516 | 4.7104 | -116.4093 | -116.2994 | 0.050354 | -0.068665 | -4.8203 | 116.3269 | 113.5712 | 113.6398 | -120.3781 | -0.041199 | 0.068665 | -0.30212 | 120.6619 | 118.8446 | 118.7759 | -0.34332 | 116.6016 | 1.0437 | 84.3109 | -121.4905 | 121.1197 | 121.0785 | 120.4285 | -121.3531
1900.6406 | 121.3898 | -116.5329 | 4.8706 | 0.27818 | 0.054097 | -0.013413 | 0.38318 | 0.017081 | 0.65203 | -0.034944 | 0.29634 | 3.9451 | 0.041307 | 0.094733 | 3.1865 | 0.05971 | -115.274 | -0.032043 | -31.4209 | -2.6505 | 0.2243 | -116.4734 | -116.629 | 4.097 | 4.01 | 2.298 | 4.5959 | 4.5456 | -116.5649 | -116.4825 | 0.059509 | -0.09613 | -4.6463 | 116.5009 | 113.8824 | 113.9786 | -120.1447 | -0.032043 | 0.050354 | -0.27466 | 120.6299 | 118.8309 | 118.7805 | -0.32501 | 116.7572 | 1.2589 | 85.112 | -121.4996 | 121.1288 | 121.0785 | 120.5429 | -121.3531
1901.6406 | 121.3989 | -116.5695 | 4.7836 | 0.20188 | 0.066914 | -0.0091401 | 0.3725 | 0.016013 | 0.64349 | -0.044557 | 0.34212 | 3.9366 | 0.048783 | 0.086188 | 3.1897 | 0.061846 | -115.0818 | -0.027466 | -31.4163 | -2.7191 | 0.23346 | -116.51 | -116.6656 | 4.0466 | -0.67291 | 2.3071 | 4.5456 | 4.4998 | -116.597 | -116.5512 | 0.059509 | -0.09613 | -4.5502 | 116.5421 | 113.8504 | 113.9465 | -119.8654 | -0.027466 | 0.018311 | -0.23804 | 120.6162 | 118.8766 | 118.8583 | -0.28381 | 116.803 | 1.4877 | 85.1532 | -121.4493 | 121.1151 | 121.0693 | 115.8966 | -121.3348
1902.6406 | 121.4859 | -116.3864 | 4.9805 | 0.32395 | 0.013508 | 0.01329 | 0.35434 | 0.0010589 | 0.59542 | -0.043489 | 0.55574 | 3.9205 | 0.019944 | 0.094733 | 3.1715 | 0.08214 | -115.0497 | 0.045776 | -32.0526 | -2.5772 | 0.19684 | -116.3223 | -116.4642 | 4.2892 | 4.1931 | 2.5681 | 4.6875 | 4.66 | -116.391 | -116.304 | 0.064087 | -0.077819 | -4.7836 | 116.4322 | 113.8092 | 113.887 | -120.0302 | -0.004577 | 0.082398 | -0.29297 | 120.6757 | 118.9545 | 118.8721 | -0.32044 | 116.5833 | 1.3367 | 84.3338 | -121.4447 | 121.0739 | 121.0464 | 120.5795 | -121.2845
1903.6406 | 121.376 | -116.304 | 5.0766 | 0.32395 | 0.067982 | 0.0036769 | 0.38425 | 0.013877 | 0.64456 | -0.033876 | 0.29634 | 3.9398 | 0.060533 | 0.10541 | 3.1875 | 0.056505 | -115.1505 | -0.045776 | -32.3181 | -2.6642 | 0.24719 | -116.2445 | -116.3818 | 4.3259 | 1.3916 | 2.5085 | 4.8248 | 4.7928 | -116.3315 | -116.272 | 0.059509 | -0.07782 | -4.8294 | 116.2582 | 113.6398 | 113.7177 | -120.2271 | -0.027466 | 0.032043 | -0.25177 | 120.6299 | 118.8126 | 118.7805 | -0.28381 | 116.5512 | 1.1536 | 83.9859 | -121.4584 | 121.1288 | 121.0968 | 117.6956 | -121.3486
1904.6406 | 121.4401 | -116.3361 | 5.0171 | 0.58335 | 0.039143 | 0.0036769 | 0.37143 | 0.010672 | 0.64562 | -0.031739 | 0.29634 | 3.9419 | 0.054124 | 0.10328 | 3.179 | 0.06505 | -115.2008 | 0.009155 | -31.8466 | -2.4902 | 0.26093 | -116.2811 | -116.4185 | 4.3167 | -0.50812 | 2.4628 | 4.747 | 4.7195 | -116.3635 | -116.2994 | 0.054932 | -0.082397 | -4.7562 | 116.3452 | 113.8458 | 113.9282 | -120.2179 | -0.027465 | 0.036622 | -0.27008 | 120.6528 | 118.7988 | 118.7622 | -0.29755 | 116.597 | 1.1353 | 84.4894 | -121.4355 | 121.0831 | 121.0556 | 115.8279 | -121.3165
1905.6406 | 121.4218 | -116.4093 | 4.9622 | 0.18663 | 0.06371 | -0.00059506 | 0.37998 | 0.0010589 | 0.64242 | -0.039216 | 0.34212 | 3.9398 | 0.044511 | 0.10435 | 3.1811 | 0.050097 | -115.2191 | 0.041199 | -32.2037 | -2.2156 | 0.29755 | -116.3223 | -116.4688 | 4.2618 | -0.44403 | 2.3392 | 4.6875 | 4.66 | -116.4505 | -116.3635 | 0.086975 | -0.059509 | -4.6646 | 116.4505 | 114.1937 | 114.2532 | -120.1813 | -0.041198 | 0.045777 | -0.27466 | 120.6711 | 118.7485 | 118.7027 | -0.30212 | 116.7068 | 1.1902 | 84.2056 | -121.431 | 121.0968 | 121.0693 | 115.9653 | -121.3257
1906.6406 | 121.4081 | -116.2674 | 5.1086 | 0.21714 | 0.06371 | -0.0070041 | 0.38532 | 0.021354 | 0.63601 | -0.03708 | 0.58626 | 3.9248 | 0.042375 | 0.10221 | 3.1726 | 0.058642 | -115.2283 | -0.059509 | -32.2449 | -2.948 | 0.23804 | -116.2445 | -116.3635 | 4.3442 | -0.58594 | 2.3438 | 4.8523 | 4.8019 | -116.2949 | -116.2445 | 0.022888 | -0.09613 | -4.8706 | 116.2079 | 113.3194 | 113.4155 | -120.3369 | -0.027466 | 0.022888 | -0.25635 | 120.6116 | 118.6111 | 118.5883 | -0.3067 | 116.5054 | 1.0391 | 84.0225 | -121.4722 | 121.1197 | 121.0693 | 115.6815 | -121.3531
1907.6406 | 121.5271 | -116.3361 | 5.0079 | 0.095073 | 0.033803 | 0.01329 | 0.36716 | 0.0074679 | 0.58901 | -0.031739 | 0.41841 | 3.9109 | 0.05626 | 0.091529 | 3.1512 | 0.075732 | -115.1459 | 0.13275 | -32.0206 | -2.6825 | 0.21057 | -116.2582 | -116.4093 | 4.39 | -0.35706 | 2.5406 | 4.715 | 4.6738 | -116.3498 | -116.2445 | 0.07782 | -0.073242 | -4.7974 | 116.4688 | 113.6536 | 113.7268 | -120.1538 | -0.013732 | 0.091553 | -0.29297 | 120.726 | 118.8766 | 118.7851 | -0.33417 | 116.5466 | 1.1902 | 84.3155 | -121.4172 | 121.051 | 121.0098 | 115.979 | -121.2524
1908.6406 | 121.3852 | -116.2033 | 5.1773 | 0.27818 | 0.051961 | -0.016617 | 0.3725 | 0.014945 | 0.64028 | -0.038148 | 0.28108 | 3.9173 | 0.049852 | 0.094733 | 3.1865 | 0.053301 | -114.8117 | -0.050354 | -31.9794 | -2.7649 | 0.21515 | -116.1667 | -116.3269 | 4.4312 | -0.49439 | 2.4124 | 4.9255 | 4.8752 | -116.2308 | -116.1575 | 0.036621 | -0.1236 | -4.9622 | 116.153 | 113.4384 | 113.562 | -119.989 | -0.027466 | 0.045776 | -0.25177 | 120.6345 | 118.6157 | 118.5699 | -0.30212 | 116.4185 | 1.3916 | 84.2239 | -121.5042 | 121.1288 | 121.0785 | 115.7089 | -121.3348
1909.6406 | 121.3806 | -116.2354 | 5.1361 | 0.33921 | 0.044484 | 0.0026089 | 0.37998 | 0.029898 | 0.64669 | -0.028535 | 0.26582 | 3.9227 | 0.048783 | 0.091529 | 3.1811 | 0.062914 | -114.9628 | -0.027466 | -31.7322 | -2.7557 | 0.2243 | -116.1896 | -116.3315 | 4.3762 | -0.47607 | 2.4124 | 4.866 | 4.8248 | -116.2949 | -116.2033 | 0.045777 | -0.09613 | -4.9118 | 116.2079 | 113.4796 | 113.5757 | -120.0989 | -0.059509 | 0.032044 | -0.27008 | 120.6116 | 118.6478 | 118.6157 | -0.31128 | 116.4597 | 1.2726 | 84.5032 | -121.4676 | 121.1014 | 121.0602 | 115.7593 | -121.3394
1910.6406 | 121.3989 | -116.2537 | 5.1132 | 0.2324 | 0.054097 | -0.0080721 | 0.35327 | 0.0021269 | 0.63708 | -0.040284 | 0.3116 | 3.9366 | 0.044511 | 0.10114 | 3.1865 | 0.062914 | -115.2237 | -0.009155 | -31.6818 | -2.3621 | 0.21057 | -116.2262 | -116.3498 | 4.3854 | -0.44861 | 2.3666 | 4.8569 | 4.8157 | -116.3086 | -116.2354 | 0.027466 | -0.09613 | -4.9026 | 116.2445 | 113.8916 | 113.9877 | -120.3369 | -0.054932 | 0.01831 | -0.25635 | 120.639 | 118.6203 | 118.602 | -0.29755 | 116.4642 | 1.03 | 84.5718 | -121.463 | 121.1105 | 121.0693 | 115.8051 | -121.3486
1911.6406 | 121.4447 | -116.1484 | 5.2643 | 0.079814 | 0.056233 | 0.00047294 | 0.38104 | 0.0085359 | 0.63601 | -0.034944 | 0.17427 | 3.9227 | 0.05626 | 0.093665 | 3.1833 | 0.054369 | -115.21 | 0.032043 | -31.3751 | -2.2247 | 0.23346 | -116.1346 | -116.2674 | 4.7699 | -0.94299 | 2.6047 | 4.985 | 4.9484 | -116.1484 | -116.0889 | 0.013732 | -0.11902 | -5.0308 | 116.1804 | 113.9236 | 114.0427 | -120.4742 | 0 | 0.059509 | -0.27924 | 120.9183 | 118.7531 | 118.6935 | -0.31586 | 116.3818 | 0.93841 | 84.7733 | -121.5317 | 121.1334 | 121.0968 | 115.2054 | -121.3531
1912.6875 | 121.4996 | -116.1804 | 5.127 | 0.59861 | 0.033803 | -0.0016631 | 0.35968 | 0.017081 | 0.62319 | -0.033876 | 1.1203 | 3.9248 | 0.05092 | 0.086188 | 3.1726 | 0.070391 | -115.0223 | 0.054932 | -31.5125 | -2.6276 | 0.18768 | -116.1667 | -116.2903 | 4.5273 | -1.68 | 2.4994 | 4.8569 | 4.7974 | -116.2308 | -116.1438 | 0.013733 | -0.10986 | -4.9393 | 116.2354 | 113.5529 | 113.6627 | -120.1492 | -0.050354 | 0.036621 | -0.27008 | 120.7077 | 118.6798 | 118.6432 | -0.32959 | 116.3681 | 1.1581 | 84.668 | -121.4172 | 121.0373 | 120.9778 | 114.5004 | -121.2708
1913.6406 | 121.4539 | -116.1484 | 5.2277 | 0.14085 | 0.047688 | -0.0059361 | 0.38639 | 0.018149 | 0.64135 | -0.040284 | 0.17427 | 3.9259 | 0.051988 | 0.094733 | 3.1822 | 0.06505 | -114.6835 | 0.10986 | -31.5582 | -2.7786 | 0.31128 | -116.0751 | -116.2125 | 4.5136 | -0.77362 | 2.4811 | 4.9347 | 4.9118 | -116.185 | -116.153 | 0.073242 | -0.064087 | -4.9164 | 116.2582 | 113.3698 | 113.4338 | -119.9112 | -0.036622 | -0.004578 | -0.29297 | 120.6619 | 118.6295 | 118.634 | -0.31586 | 116.4597 | 1.4648 | 84.5901 | -121.4401 | 121.0831 | 121.0602 | 115.3748 | -121.3806
1914.6406 | 121.4584 | -116.2674 | 5.0949 | 0.095073 | 0.06371 | 0.017563 | 0.36823 | 0.021354 | 0.63922 | -0.034944 | 2.4936 | 3.9131 | 0.055192 | 0.089393 | 3.1758 | 0.05971 | -114.8621 | 0.027466 | -31.8466 | -2.7145 | 0.21973 | -116.2308 | -116.3681 | 4.4037 | -0.3891 | 2.4582 | 4.8798 | 4.834 | -116.304 | -116.2445 | 0.036621 | -0.10071 | -4.8752 | 116.2949 | 113.5529 | 113.6536 | -119.957 | -0.036621 | 0.022888 | -0.21515 | 120.6711 | 118.7256 | 118.7027 | -0.26093 | 116.4871 | 1.4053 | 84.4208 | -121.463 | 121.1472 | 121.1014 | 115.8783 | -121.3394
1915.6406 | 121.4767 | -116.0065 | 5.365 | -0.011739 | 0.047688 | 0.0058129 | 0.3725 | 0.0085359 | 0.62853 | -0.028535 | 0.067459 | 3.9334 | 0.053056 | 0.093665 | 3.1811 | 0.06505 | -114.9033 | 0.041199 | -31.3522 | -2.4536 | 0.24261 | -116.0706 | -116.1896 | 4.5822 | -0.39825 | 2.6047 | 4.9896 | 4.9576 | -116.0843 | -115.9424 | -0.064087 | -0.18311 | -5.1224 | 116.0477 | 113.5529 | 113.736 | -120.2682 | -0.07782 | 0.064087 | -0.37537 | 120.5887 | 118.6111 | 118.5471 | -0.40741 | 116.2491 | 1.1032 | 84.6542 | -121.5546 | 120.9961 | 120.9641 | 115.6082 | -121.3074
1916.7031 | 121.431 | -116.4139 | 4.953 | -0.27114 | 0.028462 | 0.012222 | 0.36502 | -0.0032131 | 0.59863 | -0.045625 | 0.067459 | 3.9312 | 0.049852 | 0.086188 | 3.1598 | 0.06505 | -115.3061 | 0.073242 | -31.4987 | -2.3758 | 0.2243 | -116.4047 | -116.51 | 4.2023 | -0.39368 | 2.2888 | 4.6829 | 4.6509 | -116.4917 | -116.4139 | 0.009155 | -0.096131 | -4.7287 | 116.4871 | 114.0381 | 114.1342 | -120.2591 | -0.07782 | 0 | -0.27008 | 120.6161 | 118.7027 | 118.7027 | -0.30212 | 116.6382 | 1.1078 | 84.9152 | -121.463 | 121.0968 | 121.0648 | 116.0202 | -121.3669
1917.6406 | 121.4172 | -116.4368 | 4.921 | 0.12559 | 0.057301 | 0.0015409 | 0.38211 | 0.02883 | 0.65844 | -0.039216 | 0.082718 | 3.9302 | 0.043443 | 0.089393 | 3.179 | 0.066119 | -115.0681 | 0.068665 | -30.986 | -2.6367 | 0.25177 | -116.304 | -116.4459 | 4.2435 | -0.2655 | 2.243 | 4.6921 | 4.6371 | -116.4734 | -116.4139 | 0.13275 | -0.009155 | -4.6692 | 116.5054 | 113.8 | 113.8092 | -119.989 | -0.036621 | 0.022889 | -0.22888 | 120.6802 | 118.6798 | 118.6569 | -0.28381 | 116.6885 | 1.3687 | 85.4507 | -121.3669 | 121.1288 | 121.0739 | 116.1713 | -121.3348
1918.6406 | 121.4722 | -116.1942 | 5.2048 | -0.14907 | 0.049824 | 0.0058129 | 0.37784 | 0.017081 | 0.62426 | -0.040284 | -0.14616 | 3.9216 | 0.042375 | 0.093665 | 3.1737 | 0.066119 | -114.9307 | 0.022888 | -31.3889 | -2.6276 | 0.2243 | -116.1301 | -116.2766 | 4.4907 | -0.40741 | 2.4124 | 4.9438 | 4.8935 | -116.2033 | -116.1438 | 0.064087 | -0.082397 | -4.9805 | 116.217 | 113.5666 | 113.649 | -120.1355 | -0.009155 | 0.050354 | -0.26093 | 120.6848 | 118.6066 | 118.5562 | -0.31128 | 116.4185 | 1.2634 | 84.8053 | -121.4813 | 121.138 | 121.0876 | 115.7867 | -121.3486
1919.6406 | 121.4676 | -116.1301 | 5.2231 | 0.095073 | 0.058369 | 0.010086 | 0.37998 | 0.0096039 | 0.64135 | -0.031739 | 0.067459 | 3.9238 | 0.037034 | 0.10114 | 3.1747 | 0.060778 | -114.9353 | 0.050354 | -31.4621 | -2.5314 | 0.25177 | -116.1896 | -116.3269 | 4.4449 | -0.36621 | 2.3804 | 4.8843 | 4.8248 | -116.2537 | -116.1301 | -0.059509 | -0.19684 | -4.9713 | 116.1804 | 113.5986 | 113.7955 | -120.1584 | -0.1236 | 0 | -0.33875 | 120.575 | 118.5104 | 118.5104 | -0.39825 | 116.3818 | 1.1948 | 84.668 | -121.55 | 121.0144 | 120.9549 | 115.7639 | -121.3531
1920.6406 | 121.4584 | -116.4047 | 4.985 | -0.042256 | 0.051961 | 0.0068819 | 0.3725 | 0.030967 | 0.63174 | -0.040284 | 0.15901 | 3.9195 | 0.047715 | 0.086188 | 3.1758 | 0.057574 | -114.7842 | 0.064087 | -31.6269 | -2.5177 | 0.24719 | -116.3406 | -116.4597 | 4.2892 | -0.34332 | 2.298 | 4.7058 | 4.6783 | -116.4093 | -116.3452 | 0.064087 | -0.054932 | -4.7379 | 116.4688 | 113.887 | 113.942 | -119.7693 | -0.004578 | 0.059509 | -0.27923 | 120.694 | 118.7027 | 118.6432 | -0.3067 | 116.6519 | 1.6205 | 84.7778 | -121.4447 | 121.1105 | 121.0831 | 116.0614 | -121.3303
1921.6406 | 121.4493 | -116.2445 | 5.0995 | -0.11855 | 0.057301 | 0.0058129 | 0.38104 | 0.0085359 | 0.64028 | -0.031739 | 0.11323 | 3.9291 | 0.048783 | 0.080848 | 3.1683 | 0.061846 | -113.9374 | 0.050354 | -31.6315 | -2.33 | 0.25177 | -116.2491 | -116.3818 | 4.3762 | -0.37079 | 2.3483 | 4.834 | 4.7791 | -116.3315 | -116.2582 | -0.004577 | -0.13733 | -4.8477 | 116.2949 | 113.9145 | 114.0518 | -119.0369 | -0.086975 | -0.013733 | -0.2655 | 120.6207 | 118.5928 | 118.6066 | -0.32043 | 116.4963 | 2.3071 | 84.613 | -121.4813 | 121.0785 | 121.0236 | 115.8737 | -121.3577
1922.6406 | 121.4127 | -116.1392 | 5.2597 | 0.18663 | 0.065846 | 0.0036769 | 0.37357 | 0.02349 | 0.63281 | -0.038148 | 0.34212 | 3.9205 | 0.027421 | 0.10435 | 3.1865 | 0.068255 | -114.4318 | 0 | -31.0776 | -2.6047 | 0.21515 | -116.1026 | -116.2491 | 4.4861 | -0.64087 | 2.4628 | 4.9805 | 4.9255 | -116.1713 | -116.1118 | 0.036621 | -0.10986 | -5.0446 | 116.1392 | 113.5345 | 113.6444 | -119.6915 | -0.032044 | 0.027466 | -0.27924 | 120.6253 | 118.602 | 118.5745 | -0.33417 | 116.3544 | 1.7075 | 85.0616 | -121.5088 | 121.1197 | 121.0648 | 115.4984 | -121.3715
1923.6875 | 121.3806 | -116.1072 | 5.2231 | -0.026997 | 0.034871 | -0.0038001 | 0.38104 | 0.0096039 | 0.63067 | -0.036012 | 0.18953 | 3.9483 | 0.047715 | 0.084052 | 3.1694 | 0.06505 | -115.5624 | 0.045776 | -31.4941 | -2.449 | 0.23346 | -116.1438 | -116.304 | 4.4907 | -0.36163 | 2.4033 | 4.9301 | 4.8614 | -116.2216 | -116.1438 | -0.036621 | -0.19684 | -4.9896 | 116.153 | 113.6581 | 113.855 | -120.7855 | -0.11444 | -0.036621 | -0.29297 | 120.5978 | 118.5104 | 118.5471 | -0.36163 | 116.3406 | 0.54474 | 84.613 | -121.5271 | 121.0373 | 120.9686 | 115.7455 | -121.3669
1924.6406 | 121.4813 | -116.1804 | 5.2185 | -0.10329 | 0.053029 | -0.0016631 | 0.3757 | 0.013877 | 0.63815 | -0.036012 | 0.17427 | 3.9173 | 0.060533 | 0.10648 | 3.1641 | 0.056505 | -115.21 | 0.041199 | -30.9219 | -2.3392 | 0.2243 | -116.1392 | -116.272 | 4.509 | -0.43488 | 2.4399 | 4.953 | 4.8889 | -116.2033 | -116.153 | 0.041199 | -0.091553 | -4.9942 | 116.2216 | 113.8412 | 113.9328 | -120.4285 | -0.022888 | 0.027466 | -0.2655 | 120.6894 | 118.6203 | 118.5928 | -0.32959 | 116.4047 | 0.97046 | 85.2585 | -121.4905 | 121.1334 | 121.0693 | 115.7455 | -121.3715
1925.6406 | 121.4447 | -115.9882 | 5.4062 | -0.072774 | 0.048756 | 0.0058129 | 0.3757 | 0.010672 | 0.63067 | -0.043489 | -0.0088351 | 3.9227 | 0.051988 | 0.080848 | 3.1608 | 0.05971 | -115.0635 | -0.009155 | -30.6931 | -2.4902 | 0.23346 | -115.9927 | -116.1163 | 4.6463 | -0.53558 | 2.6276 | 5.1178 | 5.0766 | -116.0431 | -115.9698 | -0.004578 | -0.12817 | -5.1727 | 115.979 | 113.4979 | 113.6261 | -120.4697 | -0.054932 | 0.01831 | -0.28839 | 120.6345 | 118.6157 | 118.5974 | -0.32959 | 116.2216 | 0.92468 | 85.2951 | -121.5225 | 121.106 | 121.0648 | 115.4526 | -121.376
1926.6406 | 121.4493 | -116.1667 | 5.2597 | -0.82045 | 0.034871 | -0.0038001 | 0.38852 | 0.022422 | 0.6264 | -0.044557 | -0.054612 | 3.9173 | 0.047715 | 0.086188 | 3.1512 | 0.054369 | -113.7497 | -0.018311 | -30.4321 | -2.4078 | 0.24261 | -116.0889 | -116.2262 | 4.5044 | -0.43488 | 2.449 | 4.9988 | 4.953 | -116.1804 | -116.1026 | 0.07782 | -0.059509 | -5.0171 | 116.1484 | 113.7588 | 113.8184 | -119.0094 | -0.013733 | 0.064087 | -0.26093 | 120.6711 | 118.6157 | 118.5516 | -0.3067 | 116.4093 | 2.417 | 85.7346 | -121.4859 | 121.1655 | 121.1197 | 115.7318 | -121.3623
1927.6406 | 121.4401 | -116.1758 | 5.1956 | -0.22536 | 0.044484 | 0.0026089 | 0.36823 | 0.0085359 | 0.63174 | -0.043489 | -0.039353 | 3.9216 | 0.041307 | 0.097938 | 3.1598 | 0.054369 | -115.2008 | 0.004578 | -30.9174 | -2.6459 | 0.22888 | -116.1484 | -116.2811 | 4.4815 | -0.41199 | 2.4261 | 4.9347 | 4.9072 | -116.2491 | -116.1392 | 0.027466 | -0.10529 | -4.9667 | 116.1804 | 113.53 | 113.6353 | -120.3964 | -0.073242 | 0.036621 | -0.26093 | 120.6573 | 118.602 | 118.5654 | -0.28839 | 116.4047 | 0.97504 | 85.2585 | -121.4767 | 121.1105 | 121.0831 | 115.7639 | -121.3348
1928.6406 | 121.4676 | -116.098 | 5.3192 | -0.17959 | 0.038075 | 0.0047449 | 0.37784 | 0.019217 | 0.63067 | -0.034944 | -0.085129 | 3.9205 | 0.042375 | 0.093665 | 3.1683 | 0.054369 | -115.0818 | -0.022888 | -30.6885 | -2.3712 | 0.20599 | -116.0706 | -116.1713 | 4.5914 | -0.43488 | 2.5314 | 5.0491 | 5.0079 | -116.098 | -116.0385 | 0.027465 | -0.073243 | -5.1132 | 116.0751 | 113.7268 | 113.8 | -120.401 | 0 | 0.059509 | -0.27008 | 120.6894 | 118.6295 | 118.5699 | -0.31128 | 116.304 | 1.0162 | 85.4095 | -121.4905 | 121.1472 | 121.106 | 115.6631 | -121.3577
1929.6406 | 121.4493 | -116.1942 | 5.159 | -0.088033 | 0.06371 | 0.0068819 | 0.39279 | 0.017081 | 0.63281 | -0.041353 | 0.18953 | 3.9302 | 0.051988 | 0.084052 | 3.1705 | 0.058642 | -115.0818 | 0.050354 | -30.098 | -2.3026 | 0.23804 | -116.1713 | -116.304 | 4.4724 | -0.3891 | 2.4033 | 4.9164 | 4.8569 | -116.2582 | -116.1758 | 0.022888 | -0.10986 | -4.921 | 116.2445 | 113.8916 | 114.0015 | -120.2408 | -0.064087 | 0.018311 | -0.24262 | 120.6665 | 118.5974 | 118.5791 | -0.30212 | 116.4322 | 1.1124 | 86.0962 | -121.463 | 121.1105 | 121.051 | 115.8051 | -121.3348
1930.6406 | 121.4355 | -115.8508 | 5.5527 | 0.00352 | 0.059437 | 0.0079499 | 0.37784 | 0.070487 | 0.63601 | -0.033876 | 0.25056 | 3.9782 | 0.054124 | 0.094733 | 3.1705 | 0.073595 | -10.7437 | 0.050354 | -22.261 | -2.504 | 0.22888 | -115.8279 | -115.9515 | 5.0812 | -0.32959 | 2.7695 | 5.2872 | 5.246 | -115.8554 | -115.8051 | 0.022888 | -0.10071 | -5.3238 | 115.9012 | 113.3469 | 113.4476 | -16.2964 | -0.004578 | 0.045776 | -0.2655 | 120.932 | 118.6203 | 118.5745 | -0.3067 | 116.0797 | 105.1071 | 93.5898 | -121.5042 | 121.138 | 121.0968 | 115.5212 | -121.3577
1931.6875 | 121.4172 | -116.066 | 5.3375 | -0.17959 | 0.035939 | 0.011154 | 0.3757 | 0.064078 | 0.60824 | -0.047761 | 0.0064239 | 3.9675 | 0.055192 | 0.090461 | 3.1534 | 0.066119 | -10.4462 | 0 | -22.5128 | -2.3849 | 0.25177 | -116.0294 | -116.1804 | 4.5639 | -0.49896 | 2.4033 | 5.0903 | 5.0217 | -116.1118 | -116.0339 | 0.036621 | -0.11444 | -5.0858 | 116.066 | 113.681 | 113.7955 | -15.7837 | -0.045776 | 0.032043 | -0.24719 | 120.6299 | 118.4692 | 118.4372 | -0.31586 | 116.3177 | 105.6198 | 93.5532 | -121.5179 | 121.1563 | 121.0876 | 115.567 | -121.3715
1932.6406 | 121.4035 | -116.0431 | 5.3696 | -0.24062 | 0.043416 | 0.0079499 | 0.38104 | 0.074759 | 0.6296 | -0.040284 | -1.8551 | 3.9729 | 0.054124 | 0.080848 | 3.148 | 0.066119 | -8.4457 | -0.013733 | -22.2656 | -2.2476 | 0.28381 | -115.9058 | -116.0431 | 4.6097 | -0.46234 | 2.5177 | 5.1224 | 5.0812 | -116.0934 | -115.9607 | 0.13733 | 0 | -5.0858 | 116.0294 | 113.7955 | 113.7955 | -13.8153 | -0.050354 | 0.082398 | -0.24719 | 120.6528 | 118.5608 | 118.4784 | -0.28839 | 116.3269 | 107.5974 | 93.7775 | -121.4127 | 121.1655 | 121.1243 | 115.5808 | -121.3303
1933.6406 | 121.4401 | -116.2766 | 5.1041 | -0.13381 | 0.053029 | -0.0048681 | 0.37464 | 0.073691 | 0.64562 | -0.049897 | 0.082718 | 3.9836 | 0.055192 | 0.090461 | 3.163 | 0.054369 | -8.2993 | 0.032043 | -22.197 | -2.5681 | 0.23346 | -116.2582 | -116.3681 | 4.3808 | -0.67749 | 2.4124 | 4.8111 | 4.7791 | -116.3177 | -116.2628 | 0.01831 | -0.091553 | -4.8706 | 116.3086 | 113.7085 | 113.8 | -13.4033 | -0.041199 | 0.013733 | -0.29297 | 120.6573 | 118.689 | 118.6752 | -0.32501 | 116.51 | 107.9773 | 94.0796 | -121.4722 | 121.0876 | 121.0556 | 115.5991 | -121.3669
1934.6406 | 121.4493 | -116.3544 | 5.0583 | 1.1479 | 0.039143 | 0.014358 | 0.37998 | 0.088645 | 0.61572 | -0.046693 | -0.024094 | 3.9793 | 0.05626 | 0.095801 | 3.163 | 0.069323 | -8.2031 | -0.022888 | -22.3801 | -2.6596 | 0.2655 | -116.2903 | -116.4368 | 4.2984 | -0.48523 | 2.3758 | 4.7928 | 4.7516 | -116.4001 | -116.2994 | 0.064087 | -0.082398 | -4.7928 | 116.3315 | 113.6948 | 113.7772 | -13.2614 | -0.045776 | 0.054932 | -0.2655 | 120.6528 | 118.7302 | 118.6752 | -0.3067 | 116.6199 | 108.1512 | 93.9743 | -121.4951 | 121.1472 | 121.106 | 115.8691 | -121.3577
1935.6406 | 121.4539 | -116.3452 | 5.0491 | -0.16433 | 0.038075 | 0.0058129 | 0.37036 | 0.070487 | 0.62106 | -0.034944 | -0.039353 | 4.006 | 0.048783 | 0.10221 | 3.1715 | 0.069323 | -8.1253 | 0.009155 | -22.403 | -2.7374 | 0.2243 | -116.2949 | -116.4322 | 4.3076 | -0.42114 | 2.4582 | 4.7791 | 4.7241 | -116.3864 | -116.3086 | 0.050354 | -0.086975 | -4.8248 | 116.3544 | 113.6078 | 113.6948 | -13.1744 | -0.041199 | 0.036621 | -0.27008 | 120.6528 | 118.8034 | 118.7668 | -0.32501 | 116.5695 | 108.2199 | 93.9423 | -121.4813 | 121.1243 | 121.0693 | 115.9241 | -121.3577
1936.6406 | 121.4355 | -116.1072 | 5.2872 | -0.14907 | 0.051961 | 0.0036769 | 0.38639 | 0.0801 | 0.6296 | -0.03708 | -0.054612 | 3.9804 | 0.032762 | 0.087256 | 3.163 | 0.063982 | -8.0292 | -0.009155 | -22.3114 | -2.7695 | 0.22888 | -116.066 | -116.217 | 4.5319 | -0.37537 | 2.5726 | 4.9896 | 4.953 | -116.1438 | -116.0751 | 0.041199 | -0.10986 | -5.0583 | 116.098 | 113.3377 | 113.4476 | -13.3163 | -0.036621 | 0.032044 | -0.29755 | 120.639 | 118.6798 | 118.6478 | -0.33417 | 116.3361 | 108.078 | 93.7958 | -121.5042 | 121.0968 | 121.0602 | 115.7318 | -121.3623
1937.6406 | 121.4447 | -116.2949 | 5.1086 | -0.59157 | 0.033803 | 0.0015409 | 0.36182 | 0.071555 | 0.64456 | -0.040284 | -0.024094 | 3.9814 | 0.055192 | 0.092597 | 3.1673 | 0.051165 | -7.9605 | -0.009155 | -22.4716 | -2.7191 | 0.25635 | -116.2308 | -116.3681 | 4.3396 | 3.5522 | 2.449 | 4.8477 | 4.7928 | -116.3361 | -116.2628 | 0.064087 | -0.073242 | -4.8523 | 116.2857 | 113.5757 | 113.649 | -13.0692 | -0.041199 | 0.032044 | -0.26093 | 120.6345 | 118.7439 | 118.7119 | -0.31586 | 116.5512 | 108.3344 | 93.8232 | -121.4767 | 121.1426 | 121.0876 | 119.8471 | -121.3715
1938.6406 | 121.4355 | -116.2674 | 5.1453 | 0.50706 | 0.022053 | -0.0048681 | 0.36502 | 0.083304 | 0.62213 | -0.052034 | 0.036941 | 3.9857 | 0.045579 | 0.092597 | 3.1662 | 0.069323 | -7.9514 | 0.009155 | -22.7097 | -2.3621 | 0.25177 | -116.2033 | -116.3406 | 4.3671 | 3.8223 | 2.4948 | 4.8614 | 4.834 | -116.2903 | -116.1942 | 0.064087 | -0.073242 | -4.8935 | 116.2766 | 113.9053 | 113.9786 | -13.0966 | -0.022888 | 0.073242 | -0.28381 | 120.6345 | 118.7622 | 118.689 | -0.31128 | 116.5192 | 108.316 | 93.5577 | -121.4859 | 121.1288 | 121.1014 | 120.0897 | -121.3394
1939.6406 | 121.431 | -116.185 | 5.2231 | -0.2101 | 0.027394 | 0.0058129 | 0.38425 | 0.074759 | 0.61251 | -0.047761 | 0.63203 | 3.9782 | 0.043443 | 0.099006 | 3.1598 | 0.068255 | -7.9514 | -0.1831 | -22.522 | -2.2476 | 0.27924 | -116.0934 | -116.2079 | 4.4586 | 0.66834 | 2.5726 | 4.9713 | 4.9118 | -116.2125 | -116.1255 | 0.091553 | -0.022888 | -4.9438 | 116.0019 | 113.9374 | 113.9603 | -13.1744 | -0.027465 | 0.05951 | -0.25177 | 120.6436 | 118.7576 | 118.6981 | -0.31128 | 116.4642 | 108.2336 | 93.663 | -121.431 | 121.1563 | 121.0968 | 116.8533 | -121.3486
1940.6406 | 121.4172 | -116.5375 | 4.8889 | -0.2864 | 0.034871 | 0.015426 | 0.38852 | 0.074759 | 0.62319 | -0.047761 | -0.74126 | 3.9878 | 0.05626 | 0.093665 | 3.1683 | 0.068255 | -8.0429 | 0.004578 | -22.467 | -2.9022 | 0.2655 | -116.4871 | -116.6107 | 4.0878 | -1.0666 | 2.3071 | 4.628 | 4.5914 | -116.5787 | -116.4917 | 0.050354 | -0.073242 | -4.6234 | 116.5421 | 113.6353 | 113.7085 | -12.9318 | -0.041198 | 0.045777 | -0.26093 | 120.6253 | 118.8446 | 118.7988 | -0.29755 | 116.803 | 108.4946 | 94.0704 | -121.4996 | 121.1655 | 121.1288 | 115.4709 | -121.3806
1941.6875 | 121.582 | -116.5329 | 4.8065 | 0.034038 | 0.0060322 | 0.018631 | 0.36609 | 0.074759 | 0.59222 | -0.046693 | 0.22005 | 3.9622 | 0.043443 | 0.084052 | 3.1534 | 0.075732 | -7.7866 | 0.1831 | -22.1603 | -2.3392 | 0.21057 | -116.478 | -116.6061 | 4.184 | 2.179 | 2.4307 | 4.541 | 4.4861 | -116.5512 | -116.4734 | 0.054932 | -0.073242 | -4.5959 | 116.716 | 114.1937 | 114.267 | -12.5931 | -0.01831 | 0.059509 | -0.2655 | 120.7169 | 118.9636 | 118.9041 | -0.32043 | 116.7435 | 108.7463 | 94.3726 | -121.4127 | 121.0739 | 121.019 | 118.7119 | -121.2799
1942.6406 | 121.5317 | -116.1072 | 5.2917 | -0.2864 | 0.043416 | 0.0090179 | 0.3725 | 0.082236 | 0.6264 | -0.044557 | -0.11565 | 3.9761 | 0.047715 | 0.086188 | 3.1608 | 0.068255 | -7.7637 | -0.004578 | -22.3984 | -2.7191 | 0.24261 | -116.1301 | -116.2399 | 4.4769 | 3.8956 | 2.5543 | 5.0079 | 4.9255 | -116.1896 | -116.1438 | -0.022888 | -0.13275 | -5.0491 | 116.1026 | 113.3881 | 113.5208 | -13.0554 | -0.082397 | -0.036621 | -0.28381 | 120.5841 | 118.6615 | 118.6981 | -0.36621 | 116.3498 | 108.3435 | 93.7088 | -121.5317 | 121.1151 | 121.0327 | 120.0027 | -121.4355
1943.6406 | 121.4447 | -116.4505 | 4.9438 | -2.9719 | 0.032734 | 0.0015409 | 0.36395 | 0.075827 | 0.63922 | -0.043489 | -0.17668 | 3.99 | 0.049852 | 0.096869 | 3.1694 | 0.054369 | -7.7591 | 0.013733 | -22.7097 | -2.655 | 0.2655 | -116.4001 | -116.5466 | 4.1931 | -1.4328 | 2.3758 | 4.6829 | 4.6371 | -116.5054 | -116.4276 | 0.050354 | -0.096131 | -4.6783 | 116.4642 | 113.7955 | 113.8916 | -12.7029 | -0.054932 | 0.022888 | -0.26093 | 120.6436 | 118.8263 | 118.8034 | -0.3067 | 116.716 | 108.6914 | 93.7408 | -121.4905 | 121.1334 | 121.0876 | 115.0177 | -121.3715
1944.6406 | 121.4127 | -116.5558 | 4.8294 | -0.25588 | 0.028462 | 0.0047449 | 0.38852 | 0.077964 | 0.62853 | -0.055238 | -0.35979 | 3.9868 | 0.037034 | 0.094733 | 3.1662 | 0.060778 | -7.6675 | 0 | -22.7417 | -2.4673 | 0.29755 | -116.4642 | -116.6199 | 4.097 | -0.073242 | 2.2797 | 4.5822 | 4.5227 | -116.5878 | -116.51 | 0.091553 | -0.064087 | -4.5319 | 116.5558 | 114.0884 | 114.1525 | -12.4969 | -0.032044 | 0.045776 | -0.24719 | 120.6528 | 118.8354 | 118.7897 | -0.3067 | 116.8533 | 108.8882 | 93.8141 | -121.4493 | 121.138 | 121.0785 | 116.4825 | -121.3394
1945.6406 | 121.4676 | -116.3086 | 5.0858 | -0.17959 | 0.034871 | 0.0068819 | 0.37357 | 0.074759 | 0.64242 | -0.034944 | -0.14616 | 3.9825 | 0.045579 | 0.10007 | 3.1737 | 0.051165 | -7.7774 | 0.013733 | -22.5586 | -2.7512 | 0.24719 | -116.272 | -116.4047 | 4.3304 | -0.66834 | 2.5085 | 4.8157 | 4.7562 | -116.3818 | -116.2949 | 0.036621 | -0.09613 | -4.8386 | 116.3223 | 113.5574 | 113.6536 | -12.8632 | -0.073242 | 0.013733 | -0.27008 | 120.639 | 118.8171 | 118.8034 | -0.32959 | 116.5558 | 108.5312 | 93.75 | -121.4905 | 121.1243 | 121.0648 | 115.6403 | -121.3806
1946.6406 | 121.4355 | -116.217 | 5.1865 | -0.27114 | 0.038075 | 0.014358 | 0.37464 | 0.081168 | 0.61572 | -0.050966 | 0.097976 | 3.9697 | 0.048783 | 0.095801 | 3.1598 | 0.05971 | -7.6675 | 0.068665 | -22.641 | -2.623 | 0.22888 | -116.1713 | -116.2445 | 4.4266 | 3.0167 | 2.4673 | 4.9026 | 4.8523 | -116.2811 | -116.1667 | 0.045776 | -0.027466 | -4.9576 | 116.2857 | 113.5941 | 113.6215 | -12.854 | -0.064087 | 0.050354 | -0.28381 | 120.6436 | 118.6844 | 118.634 | -0.33417 | 116.4459 | 108.5495 | 93.576 | -121.431 | 121.1197 | 121.0693 | 119.2337 | -121.3531
1947.7031 | 121.5775 | -116.2491 | 5.0674 | 0.049296 | 0.011372 | 0.0036769 | 0.37998 | 0.074759 | 0.60183 | -0.053102 | 0.26582 | 3.9729 | 0.024217 | 0.092597 | 3.148 | 0.070391 | -7.5073 | 0.14648 | -22.2153 | -2.3392 | 0.23346 | -116.2125 | -116.3406 | 4.4586 | -0.064087 | 2.5909 | 4.7699 | 4.7379 | -116.3086 | -116.2399 | 0.036621 | -0.091553 | -4.834 | 116.3956 | 113.9099 | 114.0015 | -12.5748 | -0.05951 | 0.009155 | -0.29755 | 120.7077 | 118.84 | 118.8309 | -0.32959 | 116.4825 | 108.7418 | 94.0338 | -121.4081 | 121.019 | 120.9869 | 116.185 | -121.3074
1948.6406 | 121.3943 | -116.3727 | 5.0446 | -0.30166 | 0.010304 | 0.0090179 | 0.37677 | 0.077964 | 0.63174 | -0.05951 | -0.13091 | 3.9836 | 0.037034 | 0.084052 | 3.1587 | 0.057574 | -7.5302 | 0.009155 | -22.229 | -2.7695 | 0.25635 | -116.3086 | -116.4688 | 4.2709 | -0.44861 | 2.3392 | 4.7699 | 4.7333 | -116.423 | -116.3361 | 0.064087 | -0.09613 | -4.7882 | 116.3818 | 113.6032 | 113.6993 | -12.5748 | -0.050354 | 0.036621 | -0.27466 | 120.6436 | 118.7119 | 118.6752 | -0.31128 | 116.629 | 108.8425 | 94.1437 | -121.5134 | 121.1426 | 121.106 | 115.9241 | -121.3806
1949.6406 | 121.3989 | -116.2354 | 5.1544 | -0.19484 | 0.035939 | 0.027176 | 0.37998 | 0.079032 | 0.62533 | -0.050966 | -0.11565 | 3.9665 | 0.042375 | 0.094733 | 3.1608 | 0.061846 | -7.4753 | 0.032043 | -22.229 | -2.655 | 0.2243 | -116.1942 | -116.3315 | 4.3854 | -0.30212 | 2.4353 | 4.8889 | 4.8477 | -116.2811 | -116.2079 | 0.041199 | -0.09613 | -4.9301 | 116.2674 | 113.5803 | 113.6765 | -12.6297 | -0.045776 | 0.027466 | -0.2655 | 120.6207 | 118.6707 | 118.6432 | -0.3067 | 116.4597 | 108.7601 | 94.0063 | -121.4859 | 121.1243 | 121.0831 | 115.9332 | -121.3623
1950.6875 | 121.3898 | -116.2628 | 5.1132 | 0.20188 | 0.043416 | -0.0059361 | 0.36823 | 0.067282 | 0.64135 | -0.040284 | 0.22005 | 3.9889 | 0.051988 | 0.086188 | 3.1811 | 0.045824 | -7.4478 | 0.027466 | -21.9635 | -2.4673 | 0.2243 | -116.2262 | -116.3681 | 4.3716 | -0.33417 | 2.3163 | 4.8431 | 4.7745 | -116.3269 | -116.2445 | 0.036621 | -0.10529 | -4.8889 | 116.2903 | 113.7955 | 113.9008 | -12.561 | -0.064087 | 0.01831 | -0.27008 | 120.6345 | 118.5791 | 118.5608 | -0.33875 | 116.4871 | 108.815 | 94.2993 | -121.4813 | 121.106 | 121.0373 | 115.9287 | -121.3577
1951.6406 | 121.4355 | -116.1667 | 5.278 | -0.24062 | 0.035939 | 0.025039 | 0.3757 | 0.075827 | 0.61572 | -0.050966 | -0.11565 | 3.9772 | 0.053056 | 0.099006 | 3.1555 | 0.053301 | -7.5073 | 0 | -21.9177 | -2.4582 | 0.25635 | -116.1072 | -116.2354 | 4.6234 | -0.737 | 2.3987 | 5.0354 | 4.9667 | -116.1713 | -116.1118 | 0.059509 | -0.068665 | -5.0217 | 116.1667 | 113.7085 | 113.7772 | -12.7853 | -0.004578 | 0.054932 | -0.24261 | 120.7901 | 118.5654 | 118.5104 | -0.31128 | 116.423 | 108.6594 | 94.249 | -121.5134 | 121.2021 | 121.1334 | 115.4297 | -121.3898
1952.6406 | 121.4355 | -116.2216 | 5.159 | -0.25588 | 0.027394 | 0.011154 | 0.36075 | 0.075827 | 0.61678 | -0.045625 | -0.0088351 | 3.9675 | 0.046647 | 0.088325 | 3.1641 | 0.068255 | -7.4249 | 0.086975 | -21.0754 | -2.6367 | 0.23346 | -116.1942 | -116.304 | 4.4037 | -0.32959 | 2.4261 | 4.9164 | 4.8569 | -116.3086 | -116.185 | 0.027466 | -0.082397 | -4.9255 | 116.3086 | 113.5849 | 113.6673 | -12.5839 | -0.086975 | 0.036621 | -0.24262 | 120.6253 | 118.6478 | 118.6111 | -0.30212 | 116.4551 | 108.7967 | 95.1462 | -121.463 | 121.138 | 121.0785 | 115.892 | -121.344
1953.6406 | 121.4813 | -116.3956 | 5.0034 | -0.22536 | 0.027394 | 0.0058129 | 0.37036 | 0.084372 | 0.61465 | -0.044557 | -0.0088351 | 3.9772 | 0.040239 | 0.097938 | 3.1587 | 0.060778 | -7.3013 | 0.091553 | -21.0434 | -2.2934 | 0.21515 | -116.3315 | -116.4642 | 4.2755 | 0.054932 | 2.2888 | 4.7241 | 4.6646 | -116.4459 | -116.3727 | 0.064087 | -0.068664 | -4.7882 | 116.4871 | 114.1022 | 114.1708 | -12.3047 | -0.050354 | 0.022888 | -0.27924 | 120.6711 | 118.6844 | 118.6615 | -0.33875 | 116.6107 | 109.0942 | 95.3522 | -121.4676 | 121.1197 | 121.0602 | 116.4505 | -121.376
1954.6406 | 121.4539 | -116.5375 | 4.8706 | -0.19484 | 0.018849 | 0.012222 | 0.37891 | 0.082236 | 0.62106 | -0.042421 | -0.11565 | 3.9761 | 0.032762 | 0.096869 | 3.1673 | 0.056505 | -7.3746 | 0.022888 | -20.9518 | -2.5314 | 0.23804 | -116.5146 | -116.6336 | 4.1061 | -0.6546 | 2.1469 | 4.6005 | 4.5364 | -116.6107 | -116.51 | 0.022889 | -0.09613 | -4.6326 | 116.5604 | 114.006 | 114.1022 | -12.2452 | -0.073242 | 0.027466 | -0.27008 | 120.6436 | 118.6844 | 118.6569 | -0.33417 | 116.7755 | 109.1629 | 95.5856 | -121.5042 | 121.138 | 121.0739 | 115.8829 | -121.3806
1955.6406 | 121.4355 | -116.6061 | 4.8065 | -0.25588 | 0.030598 | 0.014358 | 0.3757 | 0.055533 | 0.62853 | -0.036012 | -0.11565 | 3.9686 | 0.044511 | 0.089393 | 3.1512 | 0.058642 | -7.3792 | 0.027466 | -21.4828 | -2.623 | 0.25177 | -116.5833 | -116.7023 | 4.0375 | -1.3229 | 2.1057 | 4.5364 | 4.4449 | -116.6565 | -116.5833 | 0.022888 | -0.096131 | -4.5547 | 116.6336 | 113.9832 | 114.0793 | -12.1857 | -0.050354 | 0.022888 | -0.27008 | 120.6436 | 118.7119 | 118.689 | -0.36163 | 116.8579 | 109.227 | 95.1233 | -121.5088 | 121.1426 | 121.051 | 115.2832 | -121.3898
1956.6406 | 121.4401 | -116.5192 | 4.8935 | -0.19484 | 0.031666 | 0.0090179 | 0.37036 | 0.086509 | 0.63494 | -0.042421 | -1.0922 | 3.9707 | 0.046647 | 0.095801 | 3.1651 | 0.05971 | -7.4295 | 0.013733 | -21.2906 | -2.4719 | 0.25177 | -116.3956 | -116.5283 | 4.1565 | -2.243 | 2.124 | 4.66 | 4.5914 | -116.5466 | -116.51 | 0.1236 | -0.009155 | -4.6417 | 116.5329 | 114.0472 | 114.0564 | -12.323 | -0.027466 | 0.009155 | -0.23346 | 120.6757 | 118.6432 | 118.634 | -0.30212 | 116.7709 | 109.0897 | 95.2286 | -121.4218 | 121.1792 | 121.1105 | 114.2761 | -121.4035
1957.6406 | 121.4355 | -116.2949 | 5.0995 | -0.2101 | 0.047688 | 0.0090179 | 0.3693 | 0.081168 | 0.62747 | -0.040284 | -2.3434 | 3.9611 | 0.044511 | 0.095801 | 3.1576 | 0.06505 | -7.3883 | 0.013733 | -21.4645 | -2.774 | 0.25177 | -116.2628 | -116.4322 | 4.3533 | -0.74616 | 2.298 | 4.8523 | 4.8065 | -116.3635 | -116.2766 | 0.032044 | -0.13733 | -4.8477 | 116.3086 | 113.5208 | 113.6581 | -12.4878 | -0.068664 | 0.018311 | -0.24719 | 120.6482 | 118.5928 | 118.5745 | -0.29297 | 116.5466 | 108.9066 | 94.8303 | -121.5317 | 121.1472 | 121.1014 | 115.5487 | -121.376
1958.6406 | 121.4401 | -116.2079 | 5.2139 | -0.2101 | 0.016713 | 0.020767 | 0.36395 | 0.073691 | 0.63067 | -0.047761 | -0.10039 | 3.9718 | 0.044511 | 0.10007 | 3.1448 | 0.057574 | -7.3059 | 0.009155 | -20.8328 | -2.3529 | 0.24261 | -116.1667 | -116.3086 | 4.541 | 0.2655 | 2.3483 | 4.9667 | 4.9118 | -116.2537 | -116.1484 | 0.041199 | -0.10071 | -4.9713 | 116.217 | 113.855 | 113.9557 | -12.5198 | -0.045776 | 0.05951 | -0.24719 | 120.7489 | 118.5562 | 118.4967 | -0.30212 | 116.4505 | 108.902 | 95.3751 | -121.5225 | 121.1746 | 121.1197 | 116.4734 | -121.3623
1959.6406 | 121.4035 | -116.2857 | 5.1086 | -0.25588 | 0.02953 | 0.0090179 | 0.36075 | 0.058738 | 0.6296 | -0.041353 | -0.039353 | 3.9601 | 0.042375 | 0.084052 | 3.1544 | 0.05971 | -7.3288 | 0.10071 | -20.7413 | -2.3254 | 0.23804 | -116.2033 | -116.3589 | 4.3671 | -1.149 | 2.3575 | 4.8203 | 4.7653 | -116.3406 | -116.2262 | 0.082398 | -0.073242 | -4.8706 | 116.3864 | 113.9603 | 114.0335 | -12.4374 | -0.054931 | 0.05951 | -0.28839 | 120.6528 | 118.6432 | 118.5837 | -0.34332 | 116.5237 | 108.9569 | 95.5444 | -121.4676 | 121.106 | 121.051 | 115.1367 | -121.3348
1960.6406 | 121.4035 | -116.5146 | 4.8889 | -0.30166 | 0.022053 | 0.0015409 | 0.37143 | 0.081168 | 0.63387 | -0.056306 | -0.23772 | 3.9793 | 0.041307 | 0.086188 | 3.1673 | 0.058642 | -7.3929 | -0.004578 | -20.7184 | -2.3987 | 0.25635 | -116.478 | -116.629 | 4.1199 | -1.0208 | 2.1286 | 4.6234 | 4.5593 | -116.6061 | -116.51 | 0.036621 | -0.11444 | -4.6326 | 116.51 | 114.1159 | 114.2303 | -12.2818 | -0.091553 | 0.004577 | -0.2655 | 120.6345 | 118.6432 | 118.6386 | -0.32959 | 116.7709 | 109.1217 | 95.7962 | -121.5179 | 121.138 | 121.0739 | 115.4938 | -121.3989
1961.6406 | 121.4401 | -116.597 | 4.8019 | -0.30166 | 0.019917 | 0.014358 | 0.36823 | 0.083304 | 0.62426 | -0.041353 | -0.13091 | 3.9665 | 0.047715 | 0.10328 | 3.1544 | 0.067187 | -7.608 | 0.032043 | -20.8832 | -2.6459 | 0.26093 | -116.5558 | -116.7068 | 4.0604 | -0.81482 | 2.1011 | 4.541 | 4.4952 | -116.629 | -116.5787 | 0.041199 | -0.10986 | -4.541 | 116.629 | 113.9511 | 114.061 | -12.41 | -0.032043 | 0.018311 | -0.26093 | 120.6573 | 118.6981 | 118.6798 | -0.3067 | 116.8579 | 108.989 | 95.7138 | -121.5088 | 121.138 | 121.0922 | 115.7822 | -121.3806
1962.6406 | 121.4172 | -116.6199 | 4.8065 | -0.16433 | 0.025258 | 0.021835 | 0.37891 | 0.077964 | 0.62213 | -0.036012 | -0.19194 | 3.9782 | 0.035966 | 0.092597 | 3.1619 | 0.057574 | -7.5485 | 0.032043 | -20.9564 | -2.3987 | 0.25177 | -116.6016 | -116.7252 | 4.0375 | -1.5015 | 2.0645 | 4.5319 | 4.4724 | -116.6702 | -116.6016 | 0.018311 | -0.10529 | -4.5547 | 116.6519 | 114.2212 | 114.3265 | -12.355 | -0.050354 | 0.018311 | -0.27466 | 120.6573 | 118.6844 | 118.6661 | -0.33417 | 116.8716 | 109.0713 | 95.6635 | -121.5317 | 121.1517 | 121.0922 | 115.1184 | -121.4081
1963.6406 | 121.4081 | -116.5009 | 4.8798 | -0.2864 | 0.043416 | 0.0026089 | 0.36182 | 0.077964 | 0.61892 | -0.049897 | -0.16142 | 3.9729 | 0.051988 | 0.10328 | 3.1502 | 0.063982 | -7.4661 | 0.036621 | -20.8237 | -2.2156 | 0.25635 | -116.4734 | -116.6245 | 4.1016 | -2.1973 | 2.1835 | 4.6005 | 4.5364 | -116.6153 | -116.4917 | 0.027465 | -0.1236 | -4.6234 | 116.5375 | 114.2853 | 114.4089 | -12.3459 | -0.11444 | 0.009155 | -0.27924 | 120.6024 | 118.6844 | 118.6752 | -0.34332 | 116.7572 | 109.0347 | 95.6772 | -121.5042 | 121.1014 | 121.0373 | 114.3036 | -121.3715
1964.6406 | 121.3852 | -116.0843 | 5.3284 | -0.24062 | 0.028462 | 0.0015409 | 0.36823 | 0.070487 | 0.63174 | -0.045625 | -0.19194 | 3.9793 | 0.043443 | 0.082984 | 3.1608 | 0.077868 | -7.489 | 0.018311 | -20.7047 | -2.449 | 0.26093 | -116.0706 | -116.2125 | 4.509 | -0.45776 | 2.4857 | 5.0903 | 5.0354 | -116.1301 | -116.066 | 0.013733 | -0.12817 | -5.0674 | 116.1026 | 113.6353 | 113.7634 | -12.8174 | -0.045776 | 0.018311 | -0.23804 | 120.5933 | 118.5699 | 118.5516 | -0.29297 | 116.3452 | 108.5953 | 95.3796 | -121.5408 | 121.1746 | 121.1197 | 115.6265 | -121.3943
1965.7031 | 121.5546 | -116.3956 | 5.0034 | 0.20188 | 0.028462 | 0.010086 | 0.37357 | 0.059806 | 0.61038 | -0.043489 | 0.50996 | 3.9611 | 0.047715 | 0.095801 | 3.148 | 0.068255 | -7.5256 | 0.07782 | -20.5948 | -2.3529 | 0.19226 | -116.2262 | -116.3406 | 4.4037 | -0.11902 | 2.3849 | 4.8065 | 4.747 | -116.3315 | -116.3361 | 0.16937 | 0.054932 | -4.8111 | 116.4734 | 114.0427 | 113.9877 | -12.529 | 0.064087 | 0.059509 | -0.19684 | 120.7993 | 118.7805 | 118.721 | -0.25635 | 116.5878 | 108.8699 | 95.8008 | -121.344 | 121.2021 | 121.1426 | 116.2766 | -121.3394
1966.6406 | 121.5363 | -116.4688 | 4.9393 | -0.19484 | 0.026326 | 0.010086 | 0.37784 | 0.075827 | 0.63708 | -0.039216 | -0.06987 | 3.9686 | 0.042375 | 0.087256 | 3.1576 | 0.051165 | -7.4661 | 0.009155 | -20.6726 | -2.3621 | 0.25177 | -116.51 | -116.6428 | 4.1153 | 2.5589 | 2.0645 | 4.6005 | 4.5456 | -116.5833 | -116.4825 | -0.041199 | -0.17395 | -4.6875 | 116.478 | 114.1068 | 114.2807 | -12.4054 | -0.11444 | -0.013733 | -0.33874 | 120.5841 | 118.5333 | 118.5471 | -0.39368 | 116.7206 | 109.0027 | 95.7962 | -121.582 | 121.0693 | 121.0144 | 119.0277 | -121.4218
1967.6406 | 121.4447 | -116.2949 | 5.1224 | -0.36269 | 0.023121 | 0.0079499 | 0.37036 | 0.066214 | 0.62319 | -0.045625 | -0.039353 | 3.9665 | 0.057328 | 0.089393 | 3.1555 | 0.058642 | -7.3608 | 0.10071 | -20.8694 | -2.0325 | 0.24261 | -116.2354 | -116.3498 | 4.3762 | -0.25635 | 2.3346 | 4.8431 | 4.7699 | -116.3406 | -116.2582 | 0.059509 | -0.054931 | -4.8798 | 116.3956 | 114.2624 | 114.3173 | -12.4832 | -0.045776 | 0.036621 | -0.27923 | 120.6711 | 118.6295 | 118.5928 | -0.35248 | 116.5375 | 108.934 | 95.4254 | -121.4722 | 121.138 | 121.0648 | 116.0385 | -121.3806
1968.6406 | 121.4264 | -115.7318 | 5.7449 | -0.31691 | 0.032734 | 0.010086 | 0.36716 | 0.083304 | 0.63281 | -0.046693 | -0.23772 | 3.9601 | 0.03917 | 0.097938 | 3.1598 | 0.052233 | -7.4432 | 0.009155 | -20.8786 | -2.1652 | 0.2655 | -115.6952 | -115.773 | 4.9072 | -1.0071 | 3.1403 | 5.5527 | 5.5161 | -115.6265 | -115.5945 | 0.036622 | -0.041198 | -5.4794 | 115.741 | 113.5666 | 113.6078 | -13.1882 | 0.10529 | 0.13733 | -0.19226 | 120.639 | 118.8721 | 118.7347 | -0.22888 | 115.9973 | 108.2886 | 94.8532 | -121.5179 | 121.2845 | 121.2479 | 114.7247 | -121.3394
1969.6406 | 121.4081 | -116.0751 | 5.2826 | -0.59157 | 0.01244 | 0.01329 | 0.3693 | 0.074759 | 0.6296 | -0.042421 | -0.23772 | 3.9675 | 0.03917 | 0.10221 | 3.1587 | 0.05971 | -7.4524 | 0.041199 | -20.8328 | -2.8519 | 0.24719 | -116.066 | -116.2079 | 4.5593 | -0.23804 | 2.5864 | 5.0262 | 5.0034 | -116.1484 | -116.0706 | 0.009155 | -0.13275 | -5.0354 | 116.1163 | 113.2233 | 113.356 | -12.735 | -0.073242 | 0.004577 | -0.25635 | 120.6345 | 118.6615 | 118.6569 | -0.27924 | 116.3223 | 108.6227 | 95.2423 | -121.4905 | 121.1014 | 121.0785 | 115.8371 | -121.3531
1970.6875 | 121.4859 | -116.2491 | 5.1132 | -0.16433 | 0.026326 | 0.020767 | 0.36395 | 0.081168 | 0.61572 | -0.045625 | -0.039353 | 3.959 | 0.043443 | 0.08512 | 3.1502 | 0.069323 | -7.3929 | 0.14648 | -20.7092 | -2.504 | 0.2243 | -116.2262 | -116.3635 | 4.4403 | 0.082397 | 2.4124 | 4.8431 | 4.7653 | -116.3361 | -116.2399 | 0.022888 | -0.11444 | -4.8889 | 116.3956 | 113.7451 | 113.8596 | -12.5061 | -0.086976 | 0.009155 | -0.27008 | 120.6894 | 118.6615 | 118.6523 | -0.3479 | 116.4734 | 108.8562 | 95.5399 | -121.4767 | 121.0922 | 121.0144 | 116.3315 | -121.3531
1971.6406 | 121.4264 | -116.1438 | 5.2872 | -0.2864 | 0.040211 | 0.0058129 | 0.3757 | 0.067282 | 0.63067 | -0.042421 | -0.085129 | 3.9633 | 0.034898 | 0.10114 | 3.1587 | 0.055437 | -7.4524 | 0.027466 | -20.7459 | -2.504 | 0.27466 | -116.1209 | -116.2582 | 4.6326 | -0.67749 | 2.3163 | 5.04 | 4.9942 | -116.1621 | -116.1255 | 0.022888 | -0.11444 | -5.0125 | 116.1713 | 113.6398 | 113.7543 | -12.7396 | -0.01831 | 0.018311 | -0.24719 | 120.7764 | 118.4601 | 118.4418 | -0.29297 | 116.4185 | 108.6914 | 95.3979 | -121.5454 | 121.1838 | 121.138 | 115.4663 | -121.4127
1972.6406 | 121.463 | -116.1072 | 5.2917 | -0.25588 | 0.038075 | -0.0016631 | 0.38211 | 0.077964 | 0.61892 | -0.042421 | -0.14616 | 3.9622 | 0.041307 | 0.10114 | 3.1512 | 0.061846 | -7.3975 | 0.022888 | -20.549 | -2.6596 | 0.26093 | -116.1346 | -116.2628 | 4.4861 | -0.50354 | 2.3849 | 4.9805 | 4.9255 | -116.1896 | -116.0522 | -0.027466 | -0.15564 | -5.0308 | 116.1301 | 113.4476 | 113.6032 | -12.6892 | -0.082397 | 0.054932 | -0.31128 | 120.5933 | 118.4921 | 118.4372 | -0.36621 | 116.3681 | 108.7097 | 95.5582 | -121.5546 | 121.0876 | 121.0327 | 115.6036 | -121.344
1973.6406 | 121.4401 | -116.0248 | 5.3879 | -0.24062 | 0.020985 | 0.01329 | 0.38959 | 0.072623 | 0.62213 | -0.034944 | -0.054612 | 3.9558 | 0.045579 | 0.097938 | 3.1491 | 0.054369 | -7.2968 | 0.10071 | -20.3064 | -2.6825 | 0.22888 | -115.9561 | -116.098 | 4.6463 | 1.1398 | 2.5543 | 5.1041 | 5.0629 | -116.0522 | -115.9927 | 0.068664 | -0.073242 | -5.159 | 116.1255 | 113.3423 | 113.4155 | -12.6846 | -0.027466 | 0.032043 | -0.28381 | 120.6711 | 118.5791 | 118.5471 | -0.32501 | 116.2537 | 108.728 | 95.7184 | -121.4859 | 121.1288 | 121.0876 | 117.1646 | -121.3806
1974.6406 | 121.4539 | -116.2262 | 5.1727 | -0.13381 | 0.018849 | 0.017563 | 0.36823 | 0.0801 | 0.61785 | -0.049897 | -0.13091 | 3.9558 | 0.05092 | 0.07978 | 3.1534 | 0.061846 | -7.2647 | 0.11902 | -20.2927 | -2.4582 | 0.24261 | -116.1438 | -116.2949 | 4.4724 | -0.53101 | 2.3392 | 4.8798 | 4.8431 | -116.2628 | -116.1896 | 0.082397 | -0.068665 | -4.9301 | 116.3452 | 113.768 | 113.8367 | -12.4374 | -0.036621 | 0.036621 | -0.29297 | 120.6985 | 118.5654 | 118.5287 | -0.32959 | 116.4688 | 108.9615 | 95.9335 | -121.4676 | 121.106 | 121.0693 | 115.6952 | -121.3623
1975.6875 | 121.4996 | -95.0638 | 25.9323 | -0.11855 | 0.032734 | 0.017563 | 0.37357 | 0.052329 | 0.49609 | -0.049897 | 0.097976 | 3.8052 | 0.05092 | 0.088325 | 3.148 | 0.053301 | -6.2531 | 0.15564 | -16.3696 | -2.0004 | 0.20599 | -95.0912 | -95.2332 | 25.676 | 0.045776 | 23.6801 | 25.8682 | 25.795 | -95.1233 | -95.1096 | -0.027466 | -0.16937 | -25.7263 | 95.2194 | 93.0634 | 93.2327 | -32.1854 | -0.059509 | -0.045776 | -0.064087 | 120.7397 | 118.7439 | 118.7897 | -0.13733 | 95.2698 | 88.8107 | 78.6942 | -121.1655 | 120.932 | 120.8588 | 95.1096 | -121.0419
1976.6406 | 121.4493 | -115.8279 | 5.5618 | -0.30166 | 0.013508 | 0.016495 | 0.37784 | 0.074759 | 0.6264 | -0.045625 | -0.14616 | 3.9611 | 0.029557 | 0.082984 | 3.1587 | 0.058642 | -7.695 | 0.054932 | -20.192 | -2.6642 | 0.2243 | -115.8188 | -115.9287 | 4.8248 | -0.32959 | 2.8656 | 5.2963 | 5.2322 | -115.9378 | -115.8234 | 0.009155 | -0.10071 | -5.3375 | 115.8829 | 113.1638 | 113.2645 | -13.2568 | -0.10986 | 0.004578 | -0.2655 | 120.6528 | 118.6935 | 118.689 | -0.32959 | 116.0522 | 108.1329 | 95.636 | -121.4905 | 121.1243 | 121.0602 | 115.4984 | -121.3852
1977.6875 | 121.4584 | -116.2399 | 5.1865 | -0.68313 | 0.040211 | 0.010086 | 0.3757 | 0.072623 | 0.63708 | -0.030671 | -0.31401 | 3.974 | 0.049852 | 0.080848 | 3.1705 | 0.054369 | -7.6218 | 0.027466 | -20.2927 | -2.7786 | 0.25635 | -116.1942 | -116.3406 | 4.4495 | -0.28381 | 2.5269 | 4.9072 | 4.8614 | -116.2811 | -116.2033 | 0.045776 | -0.10071 | -4.9301 | 116.2674 | 113.4613 | 113.562 | -12.8082 | -0.041199 | 0.036621 | -0.27923 | 120.6894 | 118.7668 | 118.7302 | -0.32501 | 116.4963 | 108.6182 | 95.9473 | -121.5271 | 121.1472 | 121.1014 | 115.9561 | -121.3898
1978.6406 | 121.4539 | -116.2628 | 5.1865 | -0.30166 | 0.031666 | 0.011154 | 0.38104 | 0.073691 | 0.63708 | -0.043489 | -0.17668 | 3.9697 | 0.040239 | 0.082984 | 3.1502 | 0.069323 | -7.5714 | 0.022888 | -20.3018 | -2.3575 | 0.25635 | -116.1896 | -116.3315 | 4.4403 | -0.5127 | 2.449 | 4.9164 | 4.866 | -116.2811 | -116.2033 | 0.073242 | -0.068665 | -4.9301 | 116.2857 | 113.9053 | 113.974 | -12.7579 | -0.018311 | 0.059509 | -0.27008 | 120.7031 | 118.7119 | 118.6523 | -0.32043 | 116.5192 | 108.6914 | 95.961 | -121.5179 | 121.1792 | 121.1288 | 115.7501 | -121.3898
1979.6406 | 121.431 | -116.1163 | 5.3192 | -0.13381 | 0.032734 | 0.011154 | 0.37677 | 0.081168 | 0.62106 | -0.043489 | -0.17668 | 3.9686 | 0.049852 | 0.08512 | 3.1502 | 0.06505 | -7.6035 | 0.022888 | -20.7962 | -2.3849 | 0.24261 | -116.0797 | -116.1942 | 4.5502 | 1.3916 | 2.5406 | 5.04 | 4.9988 | -116.153 | -116.066 | 0.036621 | -0.07782 | -5.0766 | 116.1392 | 113.7314 | 113.8092 | -12.9227 | -0.036621 | 0.050354 | -0.27924 | 120.6665 | 118.6569 | 118.6066 | -0.32043 | 116.3589 | 108.5129 | 95.3201 | -121.5134 | 121.1563 | 121.1151 | 117.5079 | -121.3852
1980.6406 | 121.5179 | -116.1484 | 5.2414 | -0.11855 | 0.020985 | 0.0090179 | 0.37677 | 0.0801 | 0.61038 | -0.047761 | -0.06987 | 3.9547 | 0.043443 | 0.087256 | 3.147 | 0.053301 | -7.4524 | 0.13733 | -20.7504 | -2.4811 | 0.23346 | -116.098 | -116.2445 | 4.5593 | 0.92926 | 2.536 | 4.953 | 4.9164 | -116.2079 | -116.1301 | 0.050354 | -0.096131 | -5.0079 | 116.2857 | 113.6673 | 113.7634 | -12.6938 | -0.05951 | 0.01831 | -0.28839 | 120.7077 | 118.6844 | 118.6661 | -0.32501 | 116.3818 | 108.696 | 95.3979 | -121.4859 | 121.1014 | 121.0648 | 117.0776 | -121.3715
1981.6875 | 121.4218 | -116.2354 | 5.2048 | -0.2864 | 0.022053 | 0.015426 | 0.36823 | 0.071555 | 0.61785 | -0.041353 | -0.085129 | 3.9611 | 0.047715 | 0.095801 | 3.1512 | 0.057574 | -7.5119 | 0.054932 | -20.8099 | -2.3987 | 0.2655 | -116.1713 | -116.3269 | 4.4586 | -0.37994 | 2.4078 | 4.9255 | 4.8523 | -116.2811 | -116.1987 | 0.064087 | -0.091552 | -4.9393 | 116.2903 | 113.8367 | 113.9282 | -12.7167 | -0.045776 | 0.036622 | -0.27924 | 120.694 | 118.6432 | 118.6066 | -0.35248 | 116.5009 | 108.7234 | 95.4254 | -121.5317 | 121.1609 | 121.0876 | 115.8554 | -121.4035
1982.6406 | 121.3211 | -116.1163 | 5.3284 | -0.2864 | 0.015645 | 0.0036769 | 0.36609 | 0.079032 | 0.62747 | -0.053102 | -0.14616 | 3.9601 | 0.05092 | 0.087256 | 3.1523 | 0.06505 | -7.3929 | 0.018311 | -20.6085 | -2.5131 | 0.2655 | -116.1392 | -116.272 | 4.5044 | -0.2655 | 2.4033 | 4.9713 | 4.9438 | -116.1713 | -116.0751 | -0.022888 | -0.15564 | -5.0629 | 116.1346 | 113.6032 | 113.7588 | -12.7213 | -0.054932 | 0.041199 | -0.35706 | 120.6207 | 118.5196 | 118.4784 | -0.38452 | 116.3818 | 108.7234 | 95.5078 | -121.6003 | 121.0876 | 121.0602 | 115.8508 | -121.4035
1983.6406 | 121.257 | -115.9836 | 5.3604 | 0.049296 | 0.079732 | 0.019699 | 0.37891 | 0.074759 | 0.64883 | -0.027467 | 0.2353 | 3.9718 | 0.048783 | 0.088325 | 3.1854 | 0.051165 | -7.3242 | 0.032043 | -20.7459 | -2.243 | 0.22888 | -116.0065 | -116.1301 | 4.6417 | -0.091553 | 2.5085 | 5.072 | 5.0171 | -116.0843 | -116.0339 | -0.022888 | -0.14648 | -5.1315 | 116.0156 | 113.7405 | 113.887 | -12.6846 | -0.10071 | -0.050354 | -0.28839 | 120.6253 | 118.4921 | 118.5425 | -0.34332 | 116.2125 | 108.6594 | 95.2377 | -121.4905 | 121.0556 | 121.0007 | 115.892 | -121.3943
1984.6406 | 121.4264 | -116.0522 | 5.4016 | -0.24062 | 0.026326 | 0.018631 | 0.37036 | 0.074759 | 0.61892 | -0.047761 | -0.054612 | 3.9718 | 0.034898 | 0.096869 | 3.147 | 0.061846 | -7.4387 | 0.027466 | -20.7092 | -2.4261 | 0.26093 | -116.0019 | -116.1301 | 4.6234 | -0.11902 | 2.5681 | 5.1041 | 5.0583 | -116.0889 | -115.9744 | 0.050354 | -0.07782 | -5.1407 | 116.0797 | 113.6261 | 113.7039 | -12.8403 | -0.036621 | 0.07782 | -0.29755 | 120.6757 | 118.6203 | 118.5425 | -0.34332 | 116.3132 | 108.6136 | 95.343 | -121.5317 | 121.1563 | 121.1105 | 115.9332 | -121.376
1985.6406 | 121.4447 | -116.0751 | 5.3696 | -0.25588 | 0.02953 | 0.0068819 | 0.36823 | 0.075827 | 0.62106 | -0.040284 | -0.085129 | 3.9633 | 0.046647 | 0.089393 | 3.1523 | 0.056505 | -7.4753 | 0.018311 | -20.5124 | -2.4765 | 0.23804 | -116.0294 | -116.1621 | 4.6097 | 0.09613 | 2.5269 | 5.0674 | 5.0217 | -116.1163 | -116.0431 | 0.045776 | -0.086975 | -5.1315 | 116.0934 | 113.5986 | 113.6856 | -12.8448 | -0.041199 | 0.032043 | -0.30212 | 120.6848 | 118.602 | 118.5699 | -0.3479 | 116.3132 | 108.5999 | 95.5627 | -121.5317 | 121.1426 | 121.0968 | 116.1713 | -121.4127
1986.6406 | 121.4493 | -115.979 | 5.4291 | -0.22536 | 0.026326 | 0.014358 | 0.36609 | 0.059806 | 0.62426 | -0.047761 | 0.021682 | 3.9601 | 0.044511 | 0.084052 | 3.1427 | 0.056505 | -7.5623 | 0.045776 | -20.7001 | -2.6779 | 0.2655 | -115.9195 | -116.0477 | 4.6738 | -0.064087 | 2.6413 | 5.159 | 5.1178 | -116.0385 | -115.9378 | 0.059509 | -0.068664 | -5.1636 | 116.0248 | 113.3011 | 113.3698 | -12.9913 | -0.059509 | 0.041199 | -0.27008 | 120.6528 | 118.6203 | 118.5791 | -0.31128 | 116.2445 | 108.4167 | 95.2789 | -121.4767 | 121.138 | 121.0968 | 115.9149 | -121.3669
1987.6406 | 121.4676 | -116.2354 | 5.2322 | -0.22536 | 0.022053 | 0.0036769 | 0.35755 | 0.060874 | 0.62106 | -0.039216 | -0.14616 | 3.9686 | 0.032762 | 0.089393 | 3.1555 | 0.057574 | -7.5348 | 0.086975 | -20.7413 | -2.4216 | 0.23346 | -116.1484 | -116.2354 | 4.4632 | 0.28839 | 2.5314 | 4.9301 | 4.8935 | -116.2445 | -116.1942 | 0.086976 | 0 | -4.9988 | 116.3223 | 113.8138 | 113.8138 | -12.767 | -0.009155 | 0.041199 | -0.30212 | 120.6985 | 118.7668 | 118.7256 | -0.33875 | 116.4688 | 108.7006 | 95.4941 | -121.4676 | 121.1655 | 121.1288 | 116.5237 | -121.4264
1988.6406 | 121.4035 | -116.3818 | 5.0446 | 0.47654 | 0.051961 | 0.0036769 | 0.396 | 0.086509 | 0.6499 | -0.034944 | 0.50996 | 3.974 | 0.061601 | 0.089393 | 3.1705 | 0.052233 | -7.5211 | -0.009155 | -21.0342 | -2.7695 | 0.25177 | -116.3361 | -116.51 | 4.2801 | -0.2655 | 2.3941 | 4.7653 | 4.6829 | -116.423 | -116.3635 | 0.045776 | -0.12817 | -4.7928 | 116.3727 | 113.6124 | 113.7405 | -12.5656 | -0.041199 | 0.018311 | -0.27924 | 120.6619 | 118.7759 | 118.7576 | -0.36163 | 116.6336 | 108.8608 | 95.3476 | -121.5546 | 121.1472 | 121.0648 | 116.1163 | -121.4081
1989.6406 | 121.4355 | -116.3727 | 5.0583 | -0.36269 | 0.02419 | 0.010086 | 0.3725 | 0.0801 | 0.60931 | -0.041353 | -0.024094 | 3.9782 | 0.047715 | 0.10114 | 3.1534 | 0.063982 | -7.5302 | 0.054932 | -21.0388 | -2.6001 | 0.24261 | -116.3132 | -116.423 | 4.3076 | -0.059509 | 2.5406 | 4.8203 | 4.7562 | -116.4139 | -116.3361 | 0.05951 | -0.050354 | -4.8157 | 116.4276 | 113.7726 | 113.8229 | -12.5885 | -0.041198 | 0.036621 | -0.23804 | 120.6802 | 118.9133 | 118.8766 | -0.30212 | 116.6153 | 108.8425 | 95.3339 | -121.4813 | 121.1929 | 121.1288 | 116.3132 | -121.3943
1990.6406 | 121.5088 | -116.3177 | 5.0583 | 2.155 | 0.0081682 | 0.021835 | 0.35114 | 0.068351 | 0.61144 | -0.044557 | 0.11323 | 3.9579 | 0.049852 | 0.082984 | 3.1555 | 0.058642 | -7.7545 | 0.15106 | -21.0159 | -1.8127 | 0.20599 | -116.2766 | -116.3956 | 4.3945 | -0.082397 | 2.5726 | 4.7653 | 4.7104 | -116.3818 | -116.2949 | 0.041199 | -0.07782 | -4.8523 | 116.4688 | 114.505 | 114.5828 | -12.8128 | -0.064087 | 0.022888 | -0.29297 | 120.7123 | 118.8904 | 118.8675 | -0.3479 | 116.5237 | 108.5632 | 95.3018 | -121.4539 | 121.0831 | 121.0281 | 116.2354 | -121.3531
1991.6406 | 121.4722 | -116.3498 | 5.0583 | -0.24062 | 0.031666 | 0.018631 | 0.36823 | 0.077964 | 0.61038 | -0.039216 | -0.054612 | 3.959 | 0.042375 | 0.082984 | 3.1608 | 0.050097 | -7.4249 | 0.10529 | -21.2585 | -1.8311 | 0.23346 | -116.3086 | -116.4688 | 4.3304 | -0.036621 | 2.4994 | 4.7607 | 4.7012 | -116.4093 | -116.3452 | 0.041198 | -0.11902 | -4.8248 | 116.4551 | 114.5187 | 114.6378 | -12.4832 | -0.05951 | 0.004577 | -0.29755 | 120.6802 | 118.8492 | 118.8446 | -0.35706 | 116.5833 | 108.9249 | 95.0912 | -121.5271 | 121.1105 | 121.051 | 116.3132 | -121.4035
1992.6406 | 121.4996 | -116.4642 | 4.9255 | -0.072774 | 0.0081682 | 0.0068819 | 0.36609 | 0.084372 | 0.6296 | -0.03708 | -0.054612 | 3.9579 | 0.03917 | 0.08512 | 3.163 | 0.058642 | -7.2739 | 0.13275 | -21.0846 | -2.0554 | 0.23346 | -116.4093 | -116.5787 | 4.2343 | 0.50812 | 2.4353 | 4.6463 | 4.5776 | -116.5329 | -116.4597 | 0.054931 | -0.11444 | -4.6921 | 116.597 | 114.4089 | 114.5233 | -12.1994 | -0.068665 | 0.004577 | -0.27924 | 120.6985 | 118.8995 | 118.895 | -0.3479 | 116.6977 | 109.1904 | 95.3796 | -121.5042 | 121.1105 | 121.0419 | 116.9724 | -121.3852
1993.6406 | 121.4539 | -116.3269 | 5.1178 | 0.2324 | 0.061574 | -0.087113 | 0.38211 | 0.076896 | 0.64883 | -0.034944 | 0.18953 | 3.9729 | 0.063737 | 0.084052 | 3.1726 | 0.058642 | -7.4387 | 0.032043 | -21.4005 | -2.2156 | 0.24719 | -116.2537 | -116.3818 | 4.3625 | 0.72327 | 2.4719 | 4.834 | 4.7607 | -116.3818 | -116.2949 | 0.073242 | -0.054932 | -4.8706 | 116.3589 | 114.1113 | 114.1663 | -12.5565 | -0.054932 | 0.032043 | -0.28381 | 120.6894 | 118.7988 | 118.7668 | -0.35706 | 116.5741 | 108.8882 | 94.9265 | -121.4996 | 121.1609 | 121.0876 | 117.0502 | -121.4127
1994.6406 | 121.5637 | -116.3452 | 5.0079 | 0.14085 | 0.0049632 | 0.0079499 | 0.36823 | 0.061942 | 0.61038 | -0.047761 | 0.036941 | 3.9654 | 0.044511 | 0.069098 | 3.1491 | 0.06505 | -7.2693 | 0.18768 | -21.2357 | -2.4902 | 0.21515 | -116.2949 | -116.4688 | 4.4083 | 1.0254 | 2.6321 | 4.7058 | 4.6692 | -116.3681 | -116.3132 | 0.050354 | -0.1236 | -4.7928 | 116.5329 | 113.855 | 113.9786 | -12.2772 | -0.022888 | 0.032044 | -0.30212 | 120.7535 | 118.9774 | 118.9453 | -0.33875 | 116.5604 | 109.0759 | 95.1096 | -121.4767 | 121.051 | 121.0144 | 117.3706 | -121.3211
1995.6406 | 121.5591 | -116.4871 | 4.866 | -0.17959 | 0.048756 | 0.017563 | 0.36823 | 0.077964 | 0.62213 | -0.034944 | -3.7167 | 3.9654 | 0.049852 | 0.087256 | 3.1619 | 0.05971 | -7.3288 | 0.16022 | -21.2906 | -2.3026 | 0.20599 | -116.4459 | -116.5787 | 4.2709 | 0.23346 | 2.5269 | 4.5547 | 4.509 | -116.5375 | -116.4505 | 0.041199 | -0.091552 | -4.66 | 116.6473 | 114.1846 | 114.2761 | -12.1948 | -0.050354 | 0.036622 | -0.31128 | 120.7581 | 119.014 | 118.9774 | -0.35706 | 116.6931 | 109.1583 | 95.1965 | -121.4447 | 121.0419 | 120.9961 | 116.7206 | -121.3165
1996.6406 | 121.4813 | -116.5466 | 4.8065 | -0.10329 | 0.028462 | 0.012222 | 0.3693 | 0.066214 | 0.61465 | -0.050966 | 0.0522 | 3.9654 | 0.038102 | 0.084052 | 3.1608 | 0.05971 | -7.338 | 0.14648 | -21.4279 | -2.1973 | 0.21057 | -116.4963 | -116.629 | 4.2114 | 0.36163 | 2.4536 | 4.5181 | 4.4998 | -116.6153 | -116.5466 | 0.050354 | -0.082397 | -4.5959 | 116.6931 | 114.3494 | 114.4318 | -12.1445 | -0.068664 | 0 | -0.28839 | 120.7581 | 119.0002 | 119.0002 | -0.3067 | 116.7572 | 109.2087 | 95.1187 | -121.4355 | 121.0648 | 121.0464 | 116.9083 | -121.3531
1997.6406 | 121.5866 | -116.2766 | 5.0674 | -0.2864 | 0.0038952 | 0.0079499 | 0.36823 | 0.066214 | 0.61785 | -0.040284 | 0.036941 | 3.9579 | 0.031694 | 0.093665 | 3.1576 | 0.051165 | -7.4707 | 0.16937 | -21.5515 | -2.1469 | 0.20599 | -116.2308 | -116.3544 | 4.4449 | 0.56305 | 2.6047 | 4.7836 | 4.7379 | -116.3406 | -116.2537 | 0.045776 | -0.07782 | -4.8614 | 116.4459 | 114.1296 | 114.2075 | -12.5381 | -0.064087 | 0.022888 | -0.28381 | 120.7214 | 118.8812 | 118.8583 | -0.32959 | 116.4825 | 108.8058 | 94.725 | -121.4218 | 121.0602 | 121.0144 | 116.8396 | -121.3211
1998.6562 | 121.463 | -116.1942 | 5.1544 | 0.61387 | 0.041279 | -0.014481 | 0.38425 | 0.077964 | 0.65524 | -0.039216 | 0.571 | 3.9569 | 0.05092 | 0.090461 | 3.1683 | 0.047961 | -7.5165 | 0.013733 | -21.6614 | -2.3254 | 0.24261 | -116.1942 | -116.3269 | 4.4907 | -0.032043 | 2.5772 | 4.9026 | 4.8019 | -116.2994 | -116.1804 | 0 | -0.13275 | -4.9118 | 116.2079 | 113.8687 | 114.0015 | -12.6709 | -0.10528 | 0.013733 | -0.25177 | 120.6848 | 118.7714 | 118.7576 | -0.35248 | 116.4368 | 108.6777 | 94.5328 | -121.4813 | 121.0968 | 120.9961 | 116.1621 | -121.3348
1999.6406 | 121.5454 | -116.217 | 5.1132 | -0.13381 | 0.020985 | 0.0015409 | 0.35114 | 0.074759 | 0.60397 | -0.042421 | 0.036941 | 3.9579 | 0.035966 | 0.11396 | 3.1224 | 0.074663 | -7.4066 | 0.15106 | -21.492 | -2.124 | 0.21515 | -116.1942 | -116.3223 | 4.5776 | -0.082397 | 2.6505 | 4.834 | 4.7699 | -116.272 | -116.217 | 0.022888 | -0.10529 | -4.8981 | 116.3681 | 114.093 | 114.1983 | -12.5198 | -0.054932 | 0 | -0.27924 | 120.7947 | 118.8675 | 118.8675 | -0.34332 | 116.4322 | 108.8104 | 94.725 | -121.4355 | 121.051 | 120.9869 | 116.1346 | -121.3303
2000.6406 | 121.5683 | -116.1621 | 5.191 | 0.12559 | -0.014263 | 0.017563 | 0.35541 | 0.073691 | 0.59863 | -0.038148 | 0.18953 | 3.9622 | 0.031694 | 0.086188 | 3.1544 | 0.063982 | -7.4524 | 0.16022 | -21.2585 | -2.5177 | 0.21515 | -116.1255 | -116.2491 | 4.6143 | 2.2522 | 2.7054 | 4.9164 | 4.8523 | -116.2033 | -116.1438 | 0.036621 | -0.086975 | -4.9759 | 116.3223 | 113.6444 | 113.7314 | -12.6434 | -0.041199 | 0.01831 | -0.27466 | 120.7764 | 118.8675 | 118.8492 | -0.33875 | 116.3773 | 108.7097 | 94.9036 | -121.4401 | 121.0785 | 121.0144 | 118.4143 | -121.3348
2001.6406 | 121.55 | -116.1301 | 5.2322 | -0.072774 | -0.0035808 | 0.016495 | 0.36075 | 0.070487 | 0.61465 | -0.056306 | 0.3116 | 3.9451 | 0.030626 | 0.084052 | 3.1534 | 0.066119 | -7.5485 | 0.12817 | -21.2357 | -2.5177 | 0.23804 | -116.1072 | -116.2537 | 4.6188 | 0.10986 | 2.6825 | 4.953 | 4.9026 | -116.185 | -116.1026 | 0.022888 | -0.1236 | -4.9942 | 116.2582 | 113.6124 | 113.736 | -12.7808 | -0.054932 | 0.027466 | -0.27924 | 120.7489 | 118.8126 | 118.7851 | -0.32959 | 116.3681 | 108.5815 | 94.8944 | -121.4859 | 121.0831 | 121.0327 | 116.2399 | -121.3348
2002.6406 | 121.6095 | -115.9927 | 5.3558 | -0.026997 | 0.0060322 | 0.0079499 | 0.36289 | 0.067282 | 0.61999 | -0.036012 | 0.082718 | 3.9526 | 0.030626 | 0.074439 | 3.147 | 0.062914 | -7.4615 | 0.16479 | -21.1395 | -2.1652 | 0.21057 | -115.9424 | -116.0843 | 4.7699 | 1.2085 | 2.7695 | 5.072 | 5.0308 | -116.0202 | -115.9927 | 0.050354 | -0.091553 | -5.1453 | 116.1575 | 113.8275 | 113.9191 | -12.8174 | -0.027466 | 0 | -0.28381 | 120.7626 | 118.7622 | 118.7622 | -0.32501 | 116.2033 | 108.5312 | 94.8532 | -121.4401 | 121.0648 | 121.0236 | 117.2012 | -121.3486
2003.6406 | 121.4996 | -116.3498 | 5.072 | -0.13381 | 0.035939 | 0.0015409 | 0.37143 | 0.0801 | 0.65096 | -0.032808 | -0.26824 | 3.9558 | 0.038102 | 0.08512 | 3.1619 | 0.043688 | -7.5531 | 0.013733 | -21.3455 | -2.6138 | 0.24719 | -116.3223 | -116.423 | 4.3716 | -0.16022 | 2.3438 | 4.7928 | 4.7195 | -116.391 | -116.3315 | 0.027465 | -0.073243 | -4.8248 | 116.3635 | 113.736 | 113.8092 | -12.6251 | -0.041199 | 0.01831 | -0.27923 | 120.7214 | 118.6935 | 118.6752 | -0.35248 | 116.597 | 108.7967 | 95.0043 | -121.4951 | 121.1426 | 121.0693 | 116.1896 | -121.4035
2004.6406 | 121.5683 | -116.2491 | 5.0903 | 0.079814 | -0.0046498 | 0.014358 | 0.36075 | 0.083304 | 0.60824 | -0.048829 | 0.28108 | 3.9473 | 0.031694 | 0.10541 | 3.1427 | 0.068255 | -7.4936 | 0.16937 | -21.4005 | -2.5955 | 0.22888 | -116.2079 | -116.3589 | 4.5136 | 0.073242 | 2.504 | 4.7836 | 4.7424 | -116.2994 | -116.2582 | 0.041198 | -0.10986 | -4.8615 | 116.4185 | 113.6536 | 113.7634 | -12.5839 | -0.050354 | -0.009156 | -0.3067 | 120.7626 | 118.7531 | 118.7622 | -0.3479 | 116.478 | 108.7555 | 94.8486 | -121.4493 | 121.0327 | 120.9915 | 116.3223 | -121.3486
2005.6406 | 121.6553 | -116.478 | 4.9026 | -0.088033 | 0.0071002 | 0.018631 | 0.36716 | 0.066214 | 0.61038 | -0.043489 | -0.024094 | 3.9537 | 0.049852 | 0.081916 | 3.1534 | 0.062914 | -7.4661 | 0.17853 | -21.4966 | -2.5269 | 0.20142 | -116.4093 | -116.5283 | 4.3076 | 0.091553 | 2.3209 | 4.6188 | 4.5731 | -116.4825 | -116.4276 | 0.068664 | -0.050354 | -4.7012 | 116.6565 | 113.9511 | 114.0015 | -12.3688 | -0.004578 | 0.050354 | -0.28381 | 120.7855 | 118.7988 | 118.7485 | -0.32959 | 116.6794 | 109.0118 | 94.9814 | -121.431 | 121.0968 | 121.051 | 116.5695 | -121.3303
2006.6406 | 121.5866 | -116.272 | 5.0674 | 0.12559 | 0.026326 | 0.016495 | 0.36395 | 0.071555 | 0.60931 | -0.046693 | 0.067459 | 3.944 | 0.038102 | 0.082984 | 3.1395 | 0.057574 | -7.4066 | 0.1831 | -21.5698 | -2.2522 | 0.20142 | -116.2582 | -116.3544 | 4.4724 | 0.045776 | 2.4216 | 4.8019 | 4.715 | -116.3498 | -116.272 | 0.013733 | -0.082397 | -4.866 | 116.4551 | 114.0198 | 114.1022 | -12.4741 | -0.077819 | 0 | -0.2655 | 120.7443 | 118.6935 | 118.6935 | -0.35248 | 116.4734 | 108.8654 | 94.7021 | -121.4218 | 121.0739 | 120.9869 | 116.3177 | -121.3394
2007.6406 | 121.5683 | -116.2766 | 5.072 | 0.14085 | 0.0092362 | 0.022903 | 0.34473 | 0.059806 | 0.61678 | -0.057374 | 0.22005 | 3.9515 | 0.040239 | 0.090461 | 3.1566 | 0.063982 | -7.4615 | 0.13733 | -21.7804 | -2.2247 | 0.2243 | -116.2491 | -116.3864 | 4.4678 | 0.013733 | 2.449 | 4.7928 | 4.7241 | -116.3361 | -116.2537 | 0.027466 | -0.10986 | -4.8477 | 116.4139 | 114.0518 | 114.1617 | -12.5336 | -0.05951 | 0.022888 | -0.27923 | 120.7443 | 118.7256 | 118.7027 | -0.3479 | 116.5009 | 108.815 | 94.4962 | -121.4584 | 121.0693 | 121.0007 | 116.2903 | -121.3257
2008.6406 | 121.4996 | -116.5146 | 4.866 | 0.17137 | 0.054097 | -0.011276 | 0.36182 | 0.071555 | 0.65203 | -0.036012 | -0.085129 | 3.9675 | 0.038102 | 0.094733 | 3.1726 | 0.051165 | -7.4295 | 0.082397 | -21.8491 | -2.2614 | 0.25635 | -116.5146 | -116.6748 | 4.2023 | 1.3321 | 2.1149 | 4.5776 | 4.5273 | -116.597 | -116.5237 | 0 | -0.16022 | -4.6097 | 116.597 | 114.2532 | 114.4135 | -12.2955 | -0.082398 | -0.009156 | -0.28839 | 120.7169 | 118.6295 | 118.6386 | -0.33875 | 116.7709 | 109.0851 | 94.6655 | -121.5408 | 121.0922 | 121.0419 | 117.8467 | -121.3898
2009.6875 | 121.5729 | -116.3864 | 4.9713 | 0.27818 | 0.014576 | 0.01329 | 0.3725 | 0.065146 | 0.60824 | -0.045625 | 0.29634 | 3.9483 | 0.034898 | 0.082984 | 3.1416 | 0.069323 | -7.4799 | 0.09613 | -21.9818 | -2.2705 | 0.23346 | -116.391 | -116.5054 | 4.3259 | -0.022888 | 2.3483 | 4.6646 | 4.6051 | -116.4825 | -116.3956 | -0.004577 | -0.11902 | -4.7379 | 116.4825 | 114.1159 | 114.2349 | -12.4512 | -0.09613 | -0.009155 | -0.3067 | 120.7123 | 118.7347 | 118.7439 | -0.36621 | 116.6199 | 108.9066 | 94.4046 | -121.4767 | 121.051 | 120.9915 | 116.3635 | -121.3669
2010.6406 | 121.637 | -116.2628 | 5.0583 | 0.15611 | 0.014576 | 0.00047294 | 0.37357 | 0.055533 | 0.6061 | -0.03708 | 0.28108 | 3.9601 | 0.034898 | 0.088325 | 3.1459 | 0.062914 | -7.4707 | 0.14648 | -21.7712 | -2.3621 | 0.2243 | -116.2582 | -116.3727 | 4.4998 | 3.3691 | 2.4261 | 4.8019 | 4.7058 | -116.3361 | -116.217 | 0.004577 | -0.10986 | -4.834 | 116.4093 | 113.9008 | 114.0106 | -12.529 | -0.073243 | 0.045776 | -0.25635 | 120.7626 | 118.689 | 118.6432 | -0.35248 | 116.4871 | 108.7921 | 94.4916 | -121.431 | 121.0648 | 120.9686 | 119.632 | -121.2753
2011.6406 | 121.6049 | -116.2125 | 5.1361 | 0.11033 | 0.0071002 | 0.026108 | 0.37036 | 0.064078 | 0.6061 | -0.045625 | 0.20479 | 3.9451 | 0.034898 | 0.086188 | 3.1491 | 0.057574 | -7.7454 | 0.13733 | -21.73 | -2.655 | 0.21973 | -116.1942 | -116.3132 | 4.5593 | 1.9363 | 2.536 | 4.8569 | 4.7882 | -116.2949 | -116.2033 | 0.01831 | -0.10071 | -4.9164 | 116.3498 | 113.5574 | 113.6581 | -12.8815 | -0.082398 | 0.009155 | -0.27923 | 120.7718 | 118.7485 | 118.7393 | -0.3479 | 116.4322 | 108.4671 | 94.4824 | -121.4493 | 121.0693 | 121.0007 | 118.1488 | -121.3394
2012.6406 | 121.5637 | -116.4413 | 4.8843 | -0.25588 | -0.0035808 | 0.012222 | 0.3757 | 0.071555 | 0.60183 | -0.044557 | 0.021682 | 3.9408 | 0.043443 | 0.082984 | 3.1598 | 0.053301 | -7.5577 | 0.19226 | -21.6934 | -2.5223 | 0.21515 | -116.391 | -116.5192 | 4.3259 | -0.10071 | 2.3254 | 4.6234 | 4.5776 | -116.5054 | -116.4001 | 0.050354 | -0.07782 | -4.6692 | 116.6336 | 113.9191 | 113.9969 | -12.442 | -0.064087 | 0.041199 | -0.26092 | 120.7672 | 118.7668 | 118.7256 | -0.3067 | 116.6565 | 108.8837 | 94.7479 | -121.4035 | 121.0648 | 121.019 | 116.3406 | -121.2845
2013.6406 | 121.5591 | -116.5054 | 4.8523 | 0.38499 | 0.019917 | 0.014358 | 0.36075 | 0.057669 | 0.61358 | -0.055238 | 0.067459 | 3.9558 | 0.028489 | 0.075507 | 3.163 | 0.058642 | -7.5119 | 0.19684 | -21.46 | -2.2934 | 0.21973 | -116.4551 | -116.6061 | 4.2435 | -0.086975 | 2.2705 | 4.5685 | 4.4724 | -116.5924 | -116.4688 | 0.050354 | -0.10071 | -4.6326 | 116.7023 | 114.212 | 114.3127 | -12.3642 | -0.086975 | 0.036621 | -0.28381 | 120.7489 | 118.7759 | 118.7393 | -0.37994 | 116.7252 | 108.9935 | 95.0455 | -121.4584 | 121.0739 | 120.9778 | 116.4185 | -121.3211
2014.6406 | 121.5637 | -116.3864 | 4.9713 | 0.17137 | 0.027394 | 0.0026089 | 0.36182 | 0.06301 | 0.60717 | -0.053102 | 0.18953 | 3.9376 | 0.026353 | 0.082984 | 3.1512 | 0.057574 | -7.5119 | 0.12817 | -21.4554 | -2.3804 | 0.22888 | -116.3269 | -116.4871 | 4.3488 | -0.068665 | 2.3849 | 4.6783 | 4.628 | -116.4551 | -116.3727 | 0.05951 | -0.10071 | -4.7424 | 116.5146 | 114.006 | 114.1068 | -12.4832 | -0.068664 | 0.013733 | -0.29297 | 120.7352 | 118.7714 | 118.7576 | -0.34332 | 116.6153 | 108.8745 | 94.931 | -121.4584 | 121.0648 | 121.0144 | 116.3177 | -121.344
2015.6406 | 121.5637 | -116.4642 | 4.9118 | 0.14085 | -0.011058 | 0.0047449 | 0.36716 | 0.067282 | 0.60931 | -0.049897 | 0.15901 | 3.943 | 0.01674 | 0.10541 | 3.1523 | 0.062914 | -7.5073 | 0.1236 | -21.6156 | -2.5543 | 0.23346 | -116.4047 | -116.5146 | 4.2892 | -0.004578 | 2.3758 | 4.6188 | 4.5593 | -116.4963 | -116.4597 | 0.059509 | -0.050354 | -4.6783 | 116.5878 | 113.9099 | 113.9603 | -12.4191 | -0.032044 | 0.004577 | -0.29297 | 120.7535 | 118.84 | 118.8354 | -0.35248 | 116.6977 | 108.9569 | 94.8486 | -121.4264 | 121.0831 | 121.0236 | 116.4597 | -121.3715
2016.6406 | 121.6278 | -116.6748 | 4.6921 | 0.064555 | 0.01244 | 0.0047449 | 0.36502 | 0.072623 | 0.60076 | -0.039216 | -0.31401 | 3.9483 | 0.040239 | 0.082984 | 3.1523 | 0.066119 | -7.4432 | 0.16479 | -21.5332 | -2.4033 | 0.23346 | -116.6336 | -116.7755 | 4.1199 | 0.068665 | 2.1835 | 4.3945 | 4.335 | -116.7343 | -116.6565 | 0.041199 | -0.10071 | -4.4586 | 116.8396 | 114.2715 | 114.3723 | -12.1353 | -0.059509 | 0.018311 | -0.29755 | 120.7947 | 118.8583 | 118.84 | -0.35706 | 116.9083 | 109.2316 | 95.1416 | -121.4676 | 121.0693 | 121.0098 | 116.7435 | -121.3486
2017.6406 | 121.5637 | -116.7664 | 4.5593 | 0.064555 | 0.014576 | 0.014358 | 0.38639 | 0.069419 | 0.60824 | -0.048829 | 0.28108 | 3.9494 | 0.043443 | 0.076575 | 3.1608 | 0.062914 | -7.4432 | 0.15564 | -21.2952 | -2.5452 | 0.23346 | -116.748 | -116.8671 | 3.9963 | 0.27924 | 2.092 | 4.2526 | 4.2252 | -116.835 | -116.7297 | 0.01831 | -0.10071 | -4.3259 | 116.922 | 114.2212 | 114.3219 | -12.0026 | -0.068665 | 0.036621 | -0.3067 | 120.7626 | 118.8583 | 118.8217 | -0.33417 | 116.9998 | 109.3231 | 95.4712 | -121.4264 | 121.019 | 120.9915 | 117.0456 | -121.2891
2018.6406 | 121.6003 | -116.5924 | 4.7745 | 0.064555 | 0.011372 | 0.021835 | 0.36609 | 0.077964 | 0.61465 | -0.048829 | 0.082718 | 3.9462 | 0.025285 | 0.090461 | 3.1502 | 0.063982 | -7.457 | 0.14191 | -21.0617 | -2.2797 | 0.23346 | -116.5421 | -116.6656 | 4.1931 | 0.21973 | 2.2888 | 4.4632 | 4.4128 | -116.6565 | -116.5787 | 0.050354 | -0.073242 | -4.541 | 116.7343 | 114.3127 | 114.386 | -12.2314 | -0.064087 | 0.013733 | -0.31128 | 120.7855 | 118.8812 | 118.8675 | -0.36163 | 116.8259 | 109.1354 | 95.5307 | -121.4401 | 121.0556 | 121.0052 | 116.8121 | -121.3531
2019.6406 | 121.5866 | -116.6565 | 4.6829 | -0.17959 | 0.014576 | 0.020767 | 0.36716 | 0.058738 | 0.61144 | -0.042421 | -0.054612 | 3.9558 | 0.029557 | 0.092597 | 3.1448 | 0.055437 | -7.5165 | 0.17853 | -21.3547 | -2.3575 | 0.21515 | -116.6473 | -116.7847 | 4.1107 | 0.65002 | 2.179 | 4.3945 | 4.3304 | -116.7252 | -116.684 | 0.009155 | -0.12817 | -4.4678 | 116.835 | 114.299 | 114.4272 | -12.1994 | -0.068665 | -0.027466 | -0.28839 | 120.7672 | 118.8354 | 118.8629 | -0.35248 | 116.8716 | 109.14 | 95.3018 | -121.4676 | 121.051 | 120.9869 | 117.3065 | -121.3669
2020.6406 | 121.6141 | -116.7206 | 4.6005 | 0.18663 | -0.014263 | 0.018631 | 0.38104 | 0.068351 | 0.61251 | -0.043489 | -0.085129 | 3.9515 | 0.027421 | 0.07978 | 3.1502 | 0.052233 | -7.5668 | 0.17395 | -21.5469 | -2.3895 | 0.21515 | -116.6885 | -116.8396 | 4.0329 | 0.054932 | 2.1606 | 4.3121 | 4.2618 | -116.8076 | -116.716 | 0.032043 | -0.11902 | -4.3854 | 116.8945 | 114.3311 | 114.4501 | -12.1674 | -0.086975 | 0.004578 | -0.28839 | 120.7535 | 118.8812 | 118.8766 | -0.33875 | 116.9357 | 109.1537 | 95.1736 | -121.4401 | 121.0327 | 120.9824 | 116.7755 | -121.3165
2021.6406 | 121.5683 | -116.803 | 4.541 | 0.17137 | 0.0081682 | 0.010086 | 0.35221 | 0.077964 | 0.61785 | -0.030671 | 0.18953 | 3.959 | 0.034898 | 0.07978 | 3.1427 | 0.061846 | -7.7454 | 0.10071 | -21.7804 | -2.3071 | 0.24261 | -116.7892 | -116.8991 | 3.9459 | -0.064087 | 2.092 | 4.2664 | 4.1977 | -116.9037 | -116.8076 | 0.013733 | -0.09613 | -4.2984 | 116.9037 | 114.4958 | 114.592 | -12.2864 | -0.10071 | -0.004577 | -0.27466 | 120.7489 | 118.895 | 118.8995 | -0.34332 | 117.0456 | 109.0576 | 95.0226 | -121.4401 | 121.0693 | 121.0007 | 116.7389 | -121.3486
2022.6406 | 121.5683 | -116.803 | 4.5639 | 0.47654 | 0.023121 | 0.0090179 | 0.37036 | 0.069419 | 0.61678 | -0.046693 | 0.25056 | 3.9473 | 0.040239 | 0.086188 | 3.1576 | 0.052233 | -7.6813 | 0.064087 | -21.73 | -2.33 | 0.19226 | -116.7755 | -116.89 | 3.9459 | 0.032043 | 2.0462 | 4.2938 | 4.2389 | -116.8671 | -116.7892 | 0.027466 | -0.086975 | -4.3716 | 116.8671 | 114.473 | 114.5599 | -12.2452 | -0.064086 | 0.013733 | -0.27008 | 120.7489 | 118.8492 | 118.8355 | -0.32501 | 116.9952 | 109.1217 | 95.0729 | -121.4539 | 121.0968 | 121.0419 | 116.835 | -121.3531
2023.6406 | 121.5683 | -116.4688 | 4.8889 | 0.12559 | -0.00037681 | 0.011154 | 0.35114 | 0.068351 | 0.60824 | -0.041353 | 0.17427 | 3.9408 | 0.028489 | 0.10114 | 3.1544 | 0.050097 | -7.6035 | 0.16022 | -21.7163 | -2.2568 | 0.2243 | -116.3956 | -116.5192 | 4.3167 | 0.059509 | 2.417 | 4.6188 | 4.5593 | -116.5054 | -116.4322 | 0.073242 | -0.050354 | -4.6646 | 116.629 | 114.212 | 114.2624 | -12.4924 | -0.036621 | 0.036621 | -0.27008 | 120.7855 | 118.8858 | 118.8492 | -0.32959 | 116.6931 | 108.8654 | 94.7525 | -121.4081 | 121.0876 | 121.0281 | 116.5283 | -121.3211
2024.6406 | 121.5637 | -116.7435 | 4.5868 | 0.18663 | 0.010304 | 0.01329 | 0.37357 | 0.0801 | 0.60183 | -0.042421 | 0.2353 | 3.9547 | 0.021012 | 0.074439 | 3.1448 | 0.056505 | -7.5989 | 0.11902 | -21.8033 | -2.1286 | 0.24719 | -116.7389 | -116.8762 | 3.9963 | 0.07782 | 2.1057 | 4.335 | 4.2526 | -116.8121 | -116.7526 | 0.004577 | -0.13275 | -4.3396 | 116.8625 | 114.6149 | 114.7476 | -12.1857 | -0.068665 | -0.009156 | -0.25177 | 120.7397 | 118.8492 | 118.8583 | -0.33417 | 116.9907 | 109.1446 | 94.9402 | -121.463 | 121.0785 | 120.9961 | 116.8213 | -121.3394
2025.6406 | 121.5591 | -116.803 | 4.5685 | 0.17137 | 0.0060322 | 0.014358 | 0.36289 | 0.071555 | 0.6061 | -0.042421 | 0.17427 | 3.9579 | 0.030626 | 0.08512 | 3.1448 | 0.053301 | -7.663 | 0.086975 | -21.8857 | -2.124 | 0.21515 | -116.7847 | -116.9037 | 3.9459 | -0.082397 | 2.1011 | 4.2847 | 4.2206 | -116.8808 | -116.7618 | 0.018311 | -0.10071 | -4.3533 | 116.89 | 114.679 | 114.7797 | -12.2314 | -0.077819 | 0.041199 | -0.28381 | 120.7489 | 118.9041 | 118.8629 | -0.3479 | 117.0181 | 109.14 | 94.9173 | -121.4722 | 121.0876 | 121.0236 | 116.7206 | -121.3303
2026.6406 | 121.5912 | -116.5512 | 4.7882 | 0.12559 | 0.010304 | 0.022903 | 0.35968 | 0.073691 | 0.62106 | -0.048829 | 0.15901 | 3.9601 | 0.043443 | 0.092597 | 3.1448 | 0.060778 | -7.5211 | 0.15106 | -21.6934 | -2.0325 | 0.23804 | -116.5009 | -116.6199 | 4.2435 | 0.19684 | 2.3712 | 4.5593 | 4.4586 | -116.5878 | -116.5329 | 0.050354 | -0.068665 | -4.5502 | 116.7023 | 114.5187 | 114.5874 | -12.3093 | -0.036622 | 0.01831 | -0.22888 | 120.7947 | 118.9224 | 118.9041 | -0.32959 | 116.7892 | 109.0302 | 94.8578 | -121.4081 | 121.1105 | 121.0098 | 116.748 | -121.3211
2027.6406 | 121.55 | -116.7618 | 4.5731 | 0.064555 | 0.01244 | 0.0058129 | 0.35114 | 0.074759 | 0.61251 | -0.036012 | 0.12849 | 3.9515 | 0.024217 | 0.08512 | 3.1491 | 0.056505 | -7.5531 | 0.13733 | -21.7621 | -2.0874 | 0.21973 | -116.7435 | -116.8945 | 3.9917 | 0.16479 | 2.1149 | 4.3076 | 4.2618 | -116.8579 | -116.7755 | 0.018311 | -0.13275 | -4.3533 | 116.8991 | 114.6744 | 114.8071 | -12.1262 | -0.09613 | -0.013733 | -0.2655 | 120.7535 | 118.8766 | 118.8904 | -0.31128 | 116.9815 | 109.2087 | 94.9997 | -121.4676 | 121.0693 | 121.0236 | 116.9266 | -121.3486
2028.6406 | 121.55 | -116.5924 | 4.7333 | 0.3087 | 0.0028272 | 0.018631 | 0.36716 | 0.073691 | 0.62319 | -0.046693 | 0.3116 | 3.9537 | 0.03383 | 0.06803 | 3.1587 | 0.06505 | -7.6172 | 0.068665 | -21.5469 | -2.2202 | 0.2243 | -116.5421 | -116.6977 | 4.1016 | 0.83313 | 2.2888 | 4.4312 | 4.3671 | -116.6748 | -116.5924 | 0.050354 | -0.10529 | -4.509 | 116.6611 | 114.3723 | 114.4775 | -12.3505 | -0.082398 | 0 | -0.30212 | 120.694 | 118.8812 | 118.8812 | -0.36621 | 116.8167 | 108.9752 | 95.0455 | -121.431 | 121.0236 | 120.9595 | 117.4255 | -121.3257
2029.6406 | 121.5637 | -116.5375 | 4.8523 | 0.079814 | 0.0049632 | 0.0090179 | 0.36609 | 0.079032 | 0.61358 | -0.03708 | 0.32686 | 3.9515 | 0.043443 | 0.08512 | 3.1566 | 0.066119 | -7.5989 | 0.10986 | -21.5195 | -2.3849 | 0.21057 | -116.478 | -116.6153 | 4.2389 | 0.022888 | 2.4216 | 4.5639 | 4.4998 | -116.5787 | -116.51 | 0.05951 | -0.077819 | -4.6417 | 116.6473 | 114.1525 | 114.2303 | -12.4512 | -0.041198 | 0.027466 | -0.28839 | 120.7764 | 118.959 | 118.9316 | -0.35248 | 116.748 | 108.9386 | 95.018 | -121.4676 | 121.1014 | 121.0373 | 116.5604 | -121.3623
2030.6406 | 121.5637 | -116.7709 | 4.5822 | 0.2324 | 0.016713 | 0.011154 | 0.36609 | 0.083304 | 0.6029 | -0.030671 | 0.50996 | 3.9579 | 0.034898 | 0.092597 | 3.1416 | 0.054369 | -7.6859 | 0.11444 | -21.6568 | -2.2751 | 0.15564 | -116.7572 | -116.9266 | 3.9597 | -0.009155 | 2.1011 | 4.3167 | 4.2526 | -116.8488 | -116.7755 | 0.013733 | -0.15564 | -4.4266 | 116.8854 | 114.4958 | 114.6515 | -12.2681 | -0.07782 | -0.004578 | -0.2655 | 120.7306 | 118.8721 | 118.8766 | -0.32959 | 116.9266 | 109.0851 | 95.1141 | -121.5088 | 121.0876 | 121.0236 | 116.7618 | -121.3577
2031.6406 | 121.5546 | -116.7297 | 4.6143 | 0.26292 | 0.011372 | 0.025039 | 0.37036 | 0.073691 | 0.61038 | -0.047761 | 0.34212 | 3.9408 | 0.03383 | 0.092597 | 3.1512 | 0.066119 | -7.6172 | 0.073242 | -21.8857 | -2.3026 | 0.21973 | -116.7114 | -116.8533 | 4.0009 | -0.082397 | 2.0737 | 4.2847 | 4.216 | -116.8488 | -116.7343 | 0.01831 | -0.1236 | -4.3945 | 116.803 | 114.4272 | 114.5508 | -12.2314 | -0.11902 | -0.004578 | -0.32959 | 120.7306 | 118.8034 | 118.808 | -0.39826 | 116.9495 | 109.1125 | 94.8441 | -121.4676 | 121.0144 | 120.9457 | 116.6473 | -121.3486
2032.6406 | 121.55 | -116.6931 | 4.6509 | 0.17137 | -0.0046498 | 0.014358 | 0.3693 | 0.071555 | 0.6061 | -0.048829 | 0.26582 | 3.9537 | 0.037034 | 0.082984 | 3.1459 | 0.066119 | -7.6172 | 0.086975 | -21.817 | -2.3209 | 0.23804 | -116.6748 | -116.8121 | 4.0421 | -0.11444 | 2.1378 | 4.3991 | 4.3167 | -116.7938 | -116.6748 | 0.01831 | -0.11902 | -4.4128 | 116.7801 | 114.3723 | 114.4913 | -12.2681 | -0.10071 | 0.01831 | -0.25177 | 120.7352 | 118.8309 | 118.8126 | -0.33417 | 116.9312 | 109.0759 | 94.8761 | -121.463 | 121.0922 | 121.0098 | 116.5787 | -121.3257
2033.6406 | 121.5454 | -116.3544 | 5.0262 | 0.27818 | -0.0025128 | 0.023971 | 0.36075 | 0.070487 | 0.61999 | -0.050966 | 0.17427 | 3.9505 | 0.037034 | 0.081916 | 3.1459 | 0.047961 | -7.5943 | 0.064087 | -21.4691 | -2.6321 | 0.15564 | -116.3956 | -116.5283 | 4.3808 | -0.009155 | 2.4628 | 4.7241 | 4.6829 | -116.4597 | -116.3635 | -0.041199 | -0.17395 | -4.8706 | 116.4185 | 113.7222 | 113.8962 | -12.6205 | -0.10529 | -0.009155 | -0.30212 | 120.7352 | 118.8171 | 118.8263 | -0.34332 | 116.51 | 108.7601 | 94.8853 | -121.5546 | 121.0785 | 121.0373 | 116.3452 | -121.3898
2034.6406 | 121.55 | -116.7435 | 4.6326 | 0.3087 | 0.020985 | 0.017563 | 0.36075 | 0.074759 | 0.60717 | -0.042421 | 0.32686 | 3.9366 | 0.022081 | 0.089393 | 3.1406 | 0.060778 | -7.8461 | 0.07782 | -21.3547 | -2.6138 | 0.23804 | -116.7068 | -116.8213 | 4.0283 | 0.027466 | 1.9821 | 4.3304 | 4.2572 | -116.7755 | -116.7068 | 0.036621 | -0.07782 | -4.3945 | 116.8213 | 114.1296 | 114.2075 | -12.4786 | -0.032044 | 0.036621 | -0.30212 | 120.7718 | 118.7256 | 118.689 | -0.37537 | 116.9815 | 108.8974 | 95.3888 | -121.4539 | 121.0739 | 121.0007 | 116.7709 | -121.3394
2035.6406 | 121.5088 | -116.5558 | 4.8111 | 0.4918 | 0.0017592 | 0.0047449 | 0.36502 | 0.06301 | 0.6296 | -0.044557 | 0.54048 | 3.9505 | 0.03383 | 0.087256 | 3.1491 | 0.058642 | -7.7545 | 0.10986 | -21.199 | -2.5543 | 0.2243 | -116.5283 | -116.6519 | 4.2023 | 0.13733 | 2.1286 | 4.5044 | 4.4861 | -116.6336 | -116.5375 | 0.027466 | -0.096131 | -4.5868 | 116.6656 | 114.0015 | 114.0976 | -12.5656 | -0.07782 | 0.01831 | -0.3067 | 120.7581 | 118.6844 | 118.6661 | -0.32501 | 116.7801 | 108.8013 | 95.3568 | -121.463 | 121.0602 | 121.0419 | 116.6931 | -121.3486
2036.6406 | 121.5225 | -116.6748 | 4.6921 | 0.18663 | 0.011372 | 0.011154 | 0.36823 | 0.065146 | 0.61465 | -0.053102 | 0.38789 | 3.9505 | 0.044511 | 0.087256 | 3.1406 | 0.054369 | -7.663 | 0.07782 | -21.0754 | -2.3712 | 0.22888 | -116.6611 | -116.8167 | 4.0054 | 0.11444 | 2.037 | 4.39 | 4.3167 | -116.7389 | -116.6565 | 0.013733 | -0.14191 | -4.4632 | 116.7526 | 114.3036 | 114.4455 | -12.355 | -0.064087 | 0.018311 | -0.30212 | 120.6802 | 118.7119 | 118.6935 | -0.37537 | 116.9037 | 109.0118 | 95.5994 | -121.5088 | 121.0648 | 120.9915 | 116.7892 | -121.3486
2037.6875 | 121.4676 | -116.8259 | 4.5502 | 3.925 | 0.030598 | 0.018631 | 0.36716 | 0.072623 | 0.63601 | -0.047761 | 0.55574 | 3.9601 | 0.037034 | 0.094733 | 3.163 | 0.057574 | -11.3937 | -0.027466 | -21.7072 | -2.4857 | 0.28381 | -116.8304 | -116.9449 | 3.8864 | -0.086975 | 1.8723 | 4.2984 | 4.2206 | -116.9266 | -116.8579 | -0.004577 | -0.11902 | -4.2664 | 116.7984 | 114.3402 | 114.4592 | -15.9439 | -0.10071 | -0.032043 | -0.25177 | 120.7123 | 118.6981 | 118.7302 | -0.32959 | 117.1097 | 105.4321 | 95.1187 | -121.4951 | 121.1243 | 121.0464 | 116.7389 | -121.4081
2038.6406 | 121.5363 | -116.6245 | 4.7516 | 0.44602 | 0.027394 | 0.0026089 | 0.36182 | 0.072623 | 0.61678 | -0.041353 | 0.58626 | 3.9526 | 0.030626 | 0.084052 | 3.1373 | 0.058642 | -10.9909 | 0.10529 | -21.5927 | -2.5681 | 0.21515 | -116.5833 | -116.684 | 4.1565 | -0.19684 | 2.1835 | 4.4724 | 4.4266 | -116.6473 | -116.6107 | 0.041199 | -0.059509 | -4.5364 | 116.7297 | 114.0564 | 114.1159 | -15.7425 | -0.022888 | 0.013733 | -0.27924 | 120.7809 | 118.808 | 118.7943 | -0.32501 | 116.8396 | 105.6335 | 95.0317 | -121.4355 | 121.0968 | 121.051 | 116.4276 | -121.3623
2039.6406 | 121.5317 | -116.6061 | 4.7699 | 0.44602 | 0.00069119 | 0.0026089 | 0.36823 | 0.075827 | 0.61465 | -0.042421 | 0.40315 | 3.9419 | 0.027421 | 0.10007 | 3.1406 | 0.058642 | -10.8627 | 0.07782 | -21.4325 | -2.33 | 0.21515 | -116.5833 | -116.7023 | 4.1107 | 1.1307 | 2.1332 | 4.4815 | 4.4128 | -116.6565 | -116.5833 | 0.022888 | -0.096131 | -4.5547 | 116.684 | 114.2761 | 114.3723 | -15.6326 | -0.050354 | 0.022888 | -0.28839 | 120.7169 | 118.7393 | 118.7164 | -0.35705 | 116.8213 | 105.7434 | 95.1736 | -121.4722 | 121.0876 | 121.019 | 117.7368 | -121.3531
2040.6406 | 121.5317 | -116.6245 | 4.7791 | 0.46128 | 0.0071002 | 0.012222 | 0.36182 | 0.060874 | 0.62106 | -0.046693 | 0.41841 | 3.9398 | 0.034898 | 0.10648 | 3.147 | 0.052233 | -10.3683 | 0.10529 | -21.6339 | -2.5909 | 0.23346 | -116.5375 | -116.7068 | 4.1245 | -0.086975 | 2.1011 | 4.4998 | 4.422 | -116.6656 | -116.6016 | 0.086975 | -0.082397 | -4.5456 | 116.7297 | 114.0335 | 114.1159 | -15.1474 | -0.041198 | 0.022889 | -0.27924 | 120.7489 | 118.7256 | 118.7027 | -0.35706 | 116.8579 | 106.2561 | 94.9905 | -121.4859 | 121.1243 | 121.0464 | 116.5375 | -121.3806
2041.6406 | 121.5775 | -116.6748 | 4.6646 | 0.53758 | 0.019917 | 0.014358 | 0.33725 | 0.066214 | 0.61999 | -0.045625 | 1.0745 | 3.9473 | 0.03917 | 0.087256 | 3.1491 | 0.051165 | -9.6634 | 0.045776 | -21.5836 | -2.4033 | 0.15564 | -116.6519 | -116.7664 | 4.1061 | 0.90179 | 2.0187 | 4.3945 | 4.3442 | -116.7297 | -116.6428 | 0.022888 | -0.091552 | -4.509 | 116.7206 | 114.2715 | 114.3631 | -14.328 | -0.054931 | 0.032044 | -0.27008 | 120.7809 | 118.6935 | 118.6615 | -0.32043 | 116.8304 | 107.0114 | 95.0912 | -121.431 | 121.0693 | 121.019 | 117.5766 | -121.3074
2042.6875 | 121.5637 | -116.6428 | 4.7287 | 0.53758 | 0.049824 | -0.00059506 | 0.36609 | 0.069419 | 0.62747 | -0.041353 | 0.54048 | 3.9462 | 0.046647 | 0.080848 | 3.1534 | 0.060778 | -9.6313 | 0.10986 | -21.5469 | -2.3895 | 0.20599 | -116.6107 | -116.7206 | 4.1336 | 0.054932 | 2.037 | 4.4678 | 4.39 | -116.716 | -116.629 | 0.032043 | -0.07782 | -4.5227 | 116.7526 | 114.2532 | 114.3311 | -14.36 | -0.073242 | 0.013733 | -0.26093 | 120.7764 | 118.6798 | 118.6661 | -0.33874 | 116.8488 | 107.0114 | 95.0958 | -121.4493 | 121.1105 | 121.0327 | 116.6977 | -121.3577
2043.6406 | 121.55 | -116.3315 | 5.0034 | -0.86623 | 0.019917 | 0.00047294 | 0.3757 | 0.079032 | 0.6296 | -0.040284 | 0.60152 | 3.9473 | 0.037034 | 0.08512 | 3.1555 | 0.062914 | -9.4803 | 0.12817 | -21.3547 | -2.2705 | 0.19226 | -116.3177 | -116.478 | 4.4266 | -0.050354 | 2.3117 | 4.715 | 4.6829 | -116.4093 | -116.3315 | 0.013733 | -0.14648 | -4.8111 | 116.4597 | 114.061 | 114.2075 | -14.4836 | -0.07782 | 0 | -0.28839 | 120.7581 | 118.6432 | 118.6432 | -0.32044 | 116.5237 | 106.8512 | 94.9768 | -121.4813 | 121.0464 | 121.0144 | 116.2811 | -121.3348
2044.6406 | 121.5363 | -116.4688 | 4.8889 | 0.55284 | 0.035939 | -0.0016631 | 0.35968 | 0.068351 | 0.64562 | -0.040284 | 0.067459 | 3.944 | 0.045579 | 0.10541 | 3.1363 | 0.060778 | -9.5993 | 0.23346 | -21.4188 | -2.2842 | 0.16022 | -116.4505 | -116.6016 | 4.3121 | 0.12817 | 2.1606 | 4.6051 | 4.5456 | -116.5604 | -116.4505 | 0.018311 | -0.13275 | -4.7287 | 116.7023 | 114.1846 | 114.3173 | -14.4882 | -0.091553 | 0.018311 | -0.28381 | 120.7809 | 118.6295 | 118.6111 | -0.34332 | 116.629 | 106.8695 | 95.05 | -121.4905 | 121.0739 | 121.0144 | 116.597 | -121.3394
2045.6406 | 121.5912 | -116.5833 | 4.7745 | 0.56809 | 0.037007 | -0.00059506 | 0.35434 | 0.071555 | 0.62533 | -0.038148 | 0.63203 | 3.9515 | 0.042375 | 0.097938 | 3.1373 | 0.051165 | -9.4254 | 0.1236 | -21.5881 | -2.2476 | 0.19684 | -116.5466 | -116.6885 | 4.2618 | 0.17395 | 2.1103 | 4.4632 | 4.4083 | -116.6611 | -116.5558 | 0.036621 | -0.10529 | -4.5776 | 116.7068 | 114.3356 | 114.4409 | -14.1998 | -0.07782 | 0.027466 | -0.31128 | 120.845 | 118.6935 | 118.6661 | -0.36621 | 116.7801 | 107.1579 | 94.9951 | -121.463 | 121.0464 | 120.9915 | 116.7572 | -121.3303
2046.6406 | 121.5546 | -116.4825 | 4.8523 | 0.26292 | 0.058369 | 0.012222 | 0.36289 | 0.082236 | 0.62106 | -0.048829 | 0.60152 | 3.9515 | 0.045579 | 0.094733 | 3.1459 | 0.057574 | -9.3933 | 0.10071 | -21.5607 | -2.5269 | 0.20599 | -116.423 | -116.5649 | 4.2938 | -0.018311 | 2.1698 | 4.5914 | 4.5227 | -116.5512 | -116.4642 | 0.059509 | -0.082397 | -4.6463 | 116.5833 | 113.9557 | 114.0381 | -14.2456 | -0.068664 | 0.018311 | -0.26092 | 120.7764 | 118.6523 | 118.634 | -0.32959 | 116.6885 | 107.0892 | 94.9219 | -121.4172 | 121.0739 | 121.0052 | 116.4642 | -121.3165
2047.6406 | 121.5912 | -116.5878 | 4.7607 | 0.62913 | 0.047688 | -0.0048681 | 0.37464 | 0.070487 | 0.62533 | -0.050966 | 0.73885 | 3.9515 | 0.045579 | 0.093665 | 3.1416 | 0.060778 | -9.1278 | -0.009155 | -21.7575 | -2.3438 | 0.16022 | -116.5833 | -116.7297 | 4.1611 | 0.6958 | 2.0599 | 4.4678 | 4.4357 | -116.6656 | -116.5649 | 0.004578 | -0.14191 | -4.6005 | 116.5787 | 114.2441 | 114.386 | -13.8885 | -0.077819 | 0.022889 | -0.29297 | 120.7489 | 118.6478 | 118.6249 | -0.32501 | 116.748 | 107.46 | 94.8303 | -121.4905 | 121.0556 | 121.0236 | 117.2836 | -121.3257
2048.6406 | 121.5775 | -116.5283 | 4.8248 | 0.55284 | 0.057301 | 0.00047294 | 0.37143 | 0.081168 | 0.63708 | -0.046693 | 1.4255 | 3.9398 | 0.046647 | 0.092597 | 3.1512 | 0.052233 | -9.256 | 0.073242 | -21.7026 | -2.4307 | 0.20599 | -116.51 | -116.6473 | 4.2343 | -0.054932 | 2.1378 | 4.5685 | 4.4952 | -116.6061 | -116.4825 | 0.01831 | -0.11902 | -4.6188 | 116.6016 | 114.0976 | 114.2166 | -14.0808 | -0.07782 | 0.045776 | -0.25635 | 120.7626 | 118.6661 | 118.6203 | -0.32959 | 116.7343 | 107.2723 | 94.8257 | -121.4722 | 121.0968 | 121.0236 | 116.4734 | -121.3074
2049.6406 | 121.5866 | -116.6428 | 4.6829 | 0.64439 | 0.033803 | 0.0015409 | 0.3725 | 0.075827 | 0.63281 | -0.034944 | 0.60152 | 3.9537 | 0.054124 | 0.089393 | 3.1566 | 0.056505 | -9.2285 | 0.045776 | -21.817 | -2.3666 | 0.2243 | -116.6565 | -116.7801 | 4.0833 | -0.082397 | 2.0691 | 4.3991 | 4.3716 | -116.7572 | -116.6428 | -0.013733 | -0.13733 | -4.4586 | 116.6885 | 114.2761 | 114.4135 | -13.9114 | -0.11444 | 0 | -0.28381 | 120.726 | 118.7119 | 118.7119 | -0.31128 | 116.8671 | 107.4142 | 94.8257 | -121.463 | 121.0419 | 121.0144 | 116.5604 | -121.3257
2050.6406 | 121.5729 | -116.7526 | 4.5776 | 1.7278 | 0.053029 | -0.00059506 | 0.35221 | 0.075827 | 0.63601 | -0.034944 | 0.63203 | 3.9473 | 0.045579 | 0.082984 | 3.1544 | 0.062914 | -9.1507 | 0.091553 | -21.7575 | -2.2568 | 0.21515 | -116.7389 | -116.8762 | 3.9963 | -0.022888 | 2.005 | 4.2938 | 4.2297 | -116.8762 | -116.7572 | 0.013733 | -0.1236 | -4.3625 | 116.8442 | 114.4958 | 114.6194 | -13.7283 | -0.1236 | -0.004577 | -0.28381 | 120.7489 | 118.7576 | 118.7622 | -0.3479 | 116.9678 | 107.6019 | 94.9951 | -121.4539 | 121.0464 | 120.9824 | 116.7297 | -121.3348
2051.6406 | 121.5866 | -116.5924 | 4.747 | 0.50706 | 0.053029 | 0.0090179 | 0.35114 | 0.081168 | 0.64349 | -0.033876 | 0.73885 | 3.9601 | 0.053056 | 0.095801 | 3.1523 | 0.069323 | -9.1095 | 0.11444 | -21.3547 | -2.2018 | 0.2243 | -116.5787 | -116.7068 | 4.1565 | -0.032043 | 2.1332 | 4.4632 | 4.422 | -116.7023 | -116.6061 | 0.013733 | -0.11444 | -4.5227 | 116.7068 | 114.3906 | 114.505 | -13.8565 | -0.10986 | -0.013733 | -0.28381 | 120.7489 | 118.7256 | 118.7393 | -0.32501 | 116.8167 | 107.4829 | 95.2377 | -121.4539 | 121.0556 | 121.0144 | 116.5604 | -121.3531
2052.6406 | 121.5866 | -116.7801 | 4.5593 | 0.67491 | 0.062642 | 0.0079499 | 0.36182 | 0.076896 | 0.64028 | -0.042421 | 0.28108 | 3.9526 | 0.045579 | 0.089393 | 3.1534 | 0.060778 | -9.1415 | 0.054932 | -21.4325 | -2.179 | 0.22888 | -116.7618 | -116.8945 | 3.9597 | 0.12817 | 2.0096 | 4.2984 | 4.2297 | -116.8579 | -116.7709 | 0.01831 | -0.11444 | -4.3304 | 116.835 | 114.6011 | 114.7156 | -13.7009 | -0.07782 | 0.009155 | -0.26093 | 120.7397 | 118.7897 | 118.7805 | -0.32959 | 117.009 | 107.6385 | 95.3476 | -121.4539 | 121.0785 | 121.0098 | 116.9083 | -121.3303
2053.6406 | 121.4996 | -116.9678 | 4.4128 | 0.69017 | 0.070118 | -0.0016631 | 0.36823 | 0.065146 | 0.6264 | -0.052034 | 0.70833 | 3.9473 | 0.047715 | 0.10648 | 3.1512 | 0.056505 | -9.0958 | 0.10986 | -21.4096 | -2.1973 | 0.21057 | -116.8533 | -116.9678 | 3.8956 | 0.009155 | 1.9089 | 4.184 | 4.1382 | -116.9769 | -116.9174 | 0.11444 | 0 | -4.2023 | 117.0776 | 114.7705 | 114.7705 | -13.5086 | -0.009156 | 0.050354 | -0.22888 | 120.8633 | 118.8766 | 118.8263 | -0.27466 | 117.1783 | 107.872 | 95.5582 | -121.3806 | 121.1517 | 121.106 | 116.9769 | -121.3303
2054.6406 | 121.5637 | -116.6977 | 4.6555 | 1.331 | 0.050892 | -0.0091401 | 0.3757 | 0.071555 | 0.64242 | -0.039216 | 0.60152 | 3.9505 | 0.057328 | 0.087256 | 3.1502 | 0.063982 | -9.082 | 0.10529 | -21.286 | -2.2568 | 0.20142 | -116.6702 | -116.7984 | 4.0787 | 0.16479 | 2.1103 | 4.3579 | 4.335 | -116.7755 | -116.7206 | 0.027466 | -0.10071 | -4.454 | 116.803 | 114.4409 | 114.5416 | -13.7375 | -0.07782 | -0.022888 | -0.29755 | 120.7764 | 118.808 | 118.8309 | -0.32043 | 116.8991 | 107.6157 | 95.4117 | -121.4539 | 121.0556 | 121.0327 | 116.8625 | -121.376
2055.6406 | 121.5408 | -116.6153 | 4.7699 | 0.47654 | 0.039143 | -0.0048681 | 0.36823 | 0.065146 | 0.64776 | -0.052034 | 0.61677 | 3.9579 | 0.049852 | 0.091529 | 3.1544 | 0.060778 | -9.1095 | -0.009155 | -21.3593 | -2.3758 | 0.23346 | -116.5924 | -116.748 | 4.1016 | -0.11902 | 2.124 | 4.4952 | 4.454 | -116.6885 | -116.597 | 0.022888 | -0.13275 | -4.5364 | 116.6061 | 114.2395 | 114.3723 | -13.8794 | -0.073243 | 0.01831 | -0.27466 | 120.7169 | 118.7393 | 118.721 | -0.31586 | 116.8488 | 107.5058 | 95.256 | -121.5179 | 121.1105 | 121.0693 | 116.4963 | -121.3669
2056.6406 | 121.4951 | -116.8396 | 4.5868 | 0.27818 | 0.056233 | 0.01329 | 0.36502 | 0.071555 | 0.63815 | -0.033876 | 0.64729 | 3.9526 | 0.045579 | 0.10007 | 3.1598 | 0.051165 | -9.0958 | -0.027466 | -21.405 | -2.417 | 0.22888 | -116.7618 | -116.9128 | 3.9139 | 0.050354 | 2.0187 | 4.335 | 4.2801 | -116.8945 | -116.803 | 0.07782 | -0.073242 | -4.3579 | 116.8121 | 114.4226 | 114.4959 | -13.6826 | -0.054931 | 0.036621 | -0.25177 | 120.7535 | 118.8583 | 118.8217 | -0.3067 | 117.0685 | 107.7438 | 95.4346 | -121.4996 | 121.1746 | 121.1197 | 116.89 | -121.3898
2057.6406 | 121.5683 | -116.9357 | 4.4174 | 0.56809 | 0.041279 | 0.0047449 | 0.37891 | 0.069419 | 0.62853 | -0.048829 | 0.64729 | 3.9547 | 0.045579 | 0.090461 | 3.1523 | 0.056505 | -9.0958 | 0.036621 | -21.4325 | -2.2522 | 0.21515 | -116.922 | -117.0639 | 3.8269 | -0.082397 | 1.8997 | 4.1382 | 4.0924 | -117.0273 | -116.9083 | 0.013733 | -0.12817 | -4.2023 | 116.9724 | 114.6835 | 114.8117 | -13.5132 | -0.091553 | 0.027466 | -0.27923 | 120.7626 | 118.8354 | 118.808 | -0.32501 | 117.1509 | 107.84 | 95.5032 | -121.4813 | 121.0739 | 121.0281 | 116.8533 | -121.3257
2058.6406 | 121.5591 | -116.9815 | 4.3991 | 0.56809 | 0.070118 | -0.0091401 | 0.37143 | 0.058738 | 0.64242 | -0.032808 | 0.60152 | 3.9633 | 0.034898 | 0.095801 | 3.1534 | 0.070391 | -9.0637 | 0.018311 | -21.4188 | -2.3529 | 0.23346 | -116.9495 | -117.0593 | 3.7811 | -0.09613 | 1.8631 | 4.1245 | 4.1061 | -117.0364 | -116.9495 | 0.032043 | -0.07782 | -4.1657 | 116.9998 | 114.6286 | 114.7064 | -13.4628 | -0.054932 | 0.032043 | -0.27466 | 120.7626 | 118.8446 | 118.8126 | -0.29297 | 117.215 | 107.9178 | 95.5627 | -121.4584 | 121.106 | 121.0876 | 116.8854 | -121.3486
2059.6406 | 121.5729 | -116.9495 | 4.3854 | 0.3087 | 0.055165 | -0.0027321 | 0.36075 | 0.071555 | 0.63281 | -0.036012 | 0.7541 | 3.9387 | 0.043443 | 0.096869 | 3.1416 | 0.06505 | -8.9722 | 0.068665 | -21.3867 | -2.1927 | 0.1831 | -116.9312 | -117.0593 | 3.8132 | -0.086975 | 1.9043 | 4.1153 | 4.0833 | -117.0502 | -116.9449 | 0.018311 | -0.10986 | -4.2023 | 117.0181 | 114.7568 | 114.8666 | -13.3575 | -0.10071 | 0.004578 | -0.27008 | 120.7626 | 118.8538 | 118.8492 | -0.30212 | 117.1326 | 107.9773 | 95.5627 | -121.4447 | 121.0648 | 121.0327 | 116.8625 | -121.3303
2060.6406 | 121.5591 | -116.89 | 4.4724 | 0.61387 | 0.055165 | -0.0027321 | 0.36182 | 0.076896 | 0.63174 | -0.034944 | 0.92195 | 3.9558 | 0.047715 | 0.10969 | 3.1598 | 0.067187 | -8.9859 | 0.086975 | -21.3913 | -2.1194 | 0.19684 | -116.8716 | -116.9678 | 3.8635 | -0.25177 | 2.0187 | 4.1931 | 4.1656 | -116.9632 | -116.8625 | 0.018311 | -0.077819 | -4.2755 | 116.9769 | 114.7705 | 114.8483 | -13.4583 | -0.073242 | 0.027466 | -0.27924 | 120.7535 | 118.9087 | 118.8812 | -0.3067 | 117.0868 | 107.9041 | 95.4987 | -121.4401 | 121.0831 | 121.0556 | 116.6382 | -121.3348
2061.6406 | 121.5866 | -116.6428 | 4.7379 | 0.59861 | 0.042347 | 0.0068819 | 0.36609 | 0.079032 | 0.63601 | -0.038148 | 0.40315 | 3.9462 | 0.047715 | 0.078712 | 3.1544 | 0.072527 | -8.9722 | 0.054932 | -21.4233 | -2.2705 | 0.21973 | -116.6336 | -116.7618 | 4.0833 | -0.14191 | 2.211 | 4.4449 | 4.39 | -116.7389 | -116.6153 | 0.009155 | -0.11902 | -4.5181 | 116.6977 | 114.3723 | 114.4913 | -13.71 | -0.096131 | 0.027466 | -0.29297 | 120.726 | 118.8538 | 118.8263 | -0.3479 | 116.8625 | 107.6706 | 95.2194 | -121.4996 | 121.0876 | 121.0327 | 116.5009 | -121.3531
2062.6406 | 121.4951 | -116.7755 | 4.6417 | 5.6798 | 0.062642 | 0.012222 | 0.38745 | 0.073691 | 0.63601 | -0.038148 | 0.66255 | 3.9483 | 0.05092 | 0.073371 | 3.163 | 0.067187 | -8.931 | -0.073242 | -21.5515 | -2.1973 | 0.24719 | -116.7526 | -116.8854 | 3.923 | -0.21057 | 1.9501 | 4.3579 | 4.3304 | -116.8533 | -116.7618 | 0.022888 | -0.10986 | -4.3945 | 116.7023 | 114.5782 | 114.6881 | -13.5727 | -0.07782 | 0.013733 | -0.28381 | 120.6985 | 118.7256 | 118.7119 | -0.31128 | 117.0227 | 107.8445 | 95.224 | -121.5271 | 121.1334 | 121.106 | 116.5649 | -121.4035
2063.6406 | 121.4676 | -116.8762 | 4.5959 | 0.52232 | 0.06905 | 0.0036769 | 0.36609 | 0.065146 | 0.63174 | -0.040284 | -1.611 | 3.9462 | 0.051988 | 0.097938 | 3.1502 | 0.062914 | -9.0454 | 0.16479 | -21.5652 | -2.4399 | 0.25177 | -116.7892 | -116.9266 | 3.8727 | -0.17395 | 1.8265 | 4.3167 | 4.2847 | -116.9174 | -116.8533 | 0.086975 | -0.050354 | -4.3442 | 117.041 | 114.4363 | 114.4867 | -13.6414 | -0.041198 | 0.022888 | -0.27924 | 120.7489 | 118.7027 | 118.6798 | -0.31128 | 117.128 | 107.8308 | 95.311 | -121.5225 | 121.1929 | 121.1609 | 116.7023 | -121.4493
2064.6406 | 121.5775 | -116.8121 | 4.5776 | 0.4918 | 0.045552 | -0.0038001 | 0.35434 | 0.077964 | 0.63494 | -0.034944 | 0.66255 | 3.9569 | 0.060533 | 0.095801 | 3.1459 | 0.070391 | -8.9813 | -0.013733 | -21.2219 | -2.2751 | 0.25177 | -116.7664 | -116.9266 | 3.9093 | -1.3092 | 1.8768 | 4.3304 | 4.2892 | -116.8808 | -116.7847 | 0.045777 | -0.11444 | -4.3259 | 116.7984 | 114.537 | 114.6515 | -13.559 | -0.068664 | 0.027466 | -0.24719 | 120.7214 | 118.689 | 118.6615 | -0.28839 | 117.0639 | 107.8308 | 95.5902 | -121.5042 | 121.1426 | 121.1014 | 115.5029 | -121.3623
2065.6406 | 121.4905 | -116.8304 | 4.5914 | 1.4073 | 0.043416 | -0.0016631 | 0.3693 | 0.065146 | 0.6296 | -0.034944 | 0.61677 | 3.9483 | 0.05626 | 0.088325 | 3.1502 | 0.067187 | -8.9539 | -0.036621 | -21.5195 | -2.2522 | 0.26093 | -116.7664 | -116.9083 | 3.9047 | 0.1236 | 1.9043 | 4.335 | 4.2755 | -116.9128 | -116.7984 | 0.064087 | -0.07782 | -4.3304 | 116.7938 | 114.5782 | 114.6561 | -13.5452 | -0.082398 | 0.032043 | -0.25635 | 120.7352 | 118.7347 | 118.7027 | -0.31586 | 117.0914 | 107.8766 | 95.311 | -121.4996 | 121.1655 | 121.106 | 116.954 | -121.3898
2066.6406 | 121.5317 | -116.7297 | 4.6371 | 0.53758 | 0.043416 | -0.0048681 | 0.36395 | 0.070487 | 0.62213 | -0.043489 | 0.66255 | 3.9473 | 0.05092 | 0.10114 | 3.147 | 0.061846 | -8.9447 | 0.018311 | -21.6019 | -2.2659 | 0.2243 | -116.7114 | -116.8213 | 4.01 | 0.10529 | 1.9821 | 4.3854 | 4.335 | -116.835 | -116.7343 | 0.01831 | -0.091553 | -4.4128 | 116.748 | 114.4638 | 114.5554 | -13.5818 | -0.10529 | -0.004578 | -0.25177 | 120.7397 | 118.7119 | 118.7164 | -0.30212 | 116.954 | 107.785 | 95.1279 | -121.4584 | 121.1151 | 121.0648 | 116.835 | -121.3715
2067.6406 | 121.5729 | -116.9083 | 4.4632 | 0.61387 | 0.050892 | -0.0016631 | 0.3725 | 0.069419 | 0.62213 | -0.030671 | 0.66255 | 3.9494 | 0.048783 | 0.093665 | 3.147 | 0.063982 | -8.9493 | -0.013733 | -21.7255 | -2.3209 | 0.22888 | -116.8808 | -117.041 | 3.8177 | 0.14648 | 1.8356 | 4.216 | 4.1565 | -116.9632 | -116.89 | 0.027466 | -0.13275 | -4.2343 | 116.8945 | 114.5874 | 114.7202 | -13.4125 | -0.054932 | 0.01831 | -0.24719 | 120.726 | 118.7439 | 118.7256 | -0.3067 | 117.1371 | 107.959 | 95.1828 | -121.5042 | 121.1243 | 121.0648 | 117.0547 | -121.3531
2068.6406 | 121.5225 | -116.9815 | 4.422 | 0.35447 | 0.057301 | 0.0079499 | 0.35114 | 0.067282 | 0.64349 | -0.036012 | 0.63203 | 3.959 | 0.05092 | 0.094733 | 3.1491 | 0.069323 | -8.931 | -0.018311 | -21.8124 | -2.3071 | 0.24719 | -116.9357 | -117.0547 | 3.7445 | -0.17395 | 1.7761 | 4.1656 | 4.1153 | -117.0319 | -116.9586 | 0.045776 | -0.073243 | -4.1748 | 116.9632 | 114.6744 | 114.7476 | -13.353 | -0.050354 | 0.022888 | -0.25635 | 120.726 | 118.7576 | 118.7347 | -0.3067 | 117.2287 | 108.0505 | 95.1691 | -121.4767 | 121.1472 | 121.0968 | 116.8076 | -121.3806
2069.6406 | 121.4401 | -117.0319 | 4.3991 | 0.32395 | 0.054097 | 0.0026089 | 0.3693 | 0.071555 | 0.64562 | -0.039216 | 0.3116 | 3.9601 | 0.051988 | 0.093665 | 3.1534 | 0.053301 | -8.9172 | -0.032043 | -21.7346 | -2.5726 | 0.24261 | -116.9815 | -117.1555 | 3.6301 | -0.20142 | 1.6479 | 4.1245 | 4.0695 | -117.1051 | -117.0319 | 0.050354 | -0.1236 | -4.1565 | 116.9998 | 114.4592 | 114.5828 | -13.3163 | -0.073243 | 0 | -0.27466 | 120.6619 | 118.6798 | 118.6798 | -0.32959 | 117.2745 | 108.1146 | 95.2972 | -121.5546 | 121.1563 | 121.1014 | 116.8304 | -121.431
2070.6406 | 121.4767 | -117.0181 | 4.4403 | 0.21714 | 0.064778 | -0.0070041 | 0.37143 | 0.067282 | 0.63708 | -0.043489 | 0.47945 | 3.9697 | 0.057328 | 0.090461 | 3.1502 | 0.061846 | -8.9813 | -0.07782 | -21.7484 | -2.4399 | 0.24719 | -116.9724 | -117.1051 | 3.6758 | -0.1831 | 1.6479 | 4.1748 | 4.1153 | -117.0639 | -116.9861 | 0.045776 | -0.086976 | -4.1931 | 116.9403 | 114.5782 | 114.6652 | -13.4216 | -0.045777 | 0.032043 | -0.2655 | 120.694 | 118.6661 | 118.634 | -0.32501 | 117.2653 | 108.0368 | 95.2698 | -121.5454 | 121.1929 | 121.1334 | 116.835 | -121.4264
2071.6406 | 121.4355 | -116.6565 | 4.7882 | 0.32395 | 0.06905 | -0.0038001 | 0.3693 | 0.064078 | 0.63708 | -0.033876 | 0.47945 | 3.9494 | 0.049852 | 0.082984 | 3.1534 | 0.072527 | -8.9447 | -0.032043 | -21.8765 | -2.5909 | 0.2243 | -116.597 | -116.7526 | 4.0283 | -0.20142 | 1.9867 | 4.5273 | 4.509 | -116.7206 | -116.6382 | 0.059509 | -0.096131 | -4.5639 | 116.6245 | 114.0656 | 114.1617 | -13.7329 | -0.064087 | 0.01831 | -0.26093 | 120.6848 | 118.6432 | 118.6249 | -0.27924 | 116.8808 | 107.7118 | 94.78 | -121.5408 | 121.1838 | 121.1655 | 116.4551 | -121.4264
2072.6406 | 121.4767 | -117.009 | 4.4495 | 0.27818 | 0.070118 | -0.0070041 | 0.38639 | 0.075827 | 0.64028 | -0.040284 | 0.34212 | 3.9526 | 0.044511 | 0.090461 | 3.1512 | 0.058642 | -8.9493 | -0.032043 | -22.0688 | -2.5085 | 0.23346 | -116.9357 | -117.1005 | 3.653 | -0.1831 | 1.7944 | 4.1428 | 4.1199 | -117.1097 | -116.9907 | 0.073242 | -0.091553 | -4.216 | 116.9769 | 114.5004 | 114.592 | -13.3987 | -0.10071 | 0.01831 | -0.3067 | 120.6619 | 118.8034 | 118.7851 | -0.32959 | 117.2424 | 108.0597 | 94.9402 | -121.55 | 121.1517 | 121.1288 | 116.8259 | -121.4401
2073.6406 | 121.4539 | -117.1463 | 4.3304 | 0.26292 | 0.059437 | -0.011276 | 0.36716 | 0.068351 | 0.63601 | -0.030671 | 0.52522 | 3.9558 | 0.05092 | 0.08512 | 3.1459 | 0.066119 | -8.9447 | -0.073242 | -21.9818 | -2.3804 | 0.24719 | -117.0364 | -117.1967 | 3.5843 | -0.21973 | 1.7395 | 4.0695 | 4.0237 | -117.1783 | -117.1005 | 0.10986 | -0.050354 | -4.0833 | 117.0731 | 114.7659 | 114.8163 | -13.2751 | -0.032044 | 0.045776 | -0.26093 | 120.7306 | 118.8858 | 118.84 | -0.3067 | 117.3935 | 108.2016 | 95.1645 | -121.5271 | 121.2158 | 121.17 | 116.9266 | -121.431
2074.6406 | 121.4355 | -116.8945 | 4.5959 | 0.29344 | 0.074391 | -0.011276 | 0.38211 | 0.060874 | 0.63922 | -0.03708 | 0.11323 | 3.9611 | 0.054124 | 0.092597 | 3.1523 | 0.066119 | -8.9401 | -0.036621 | -21.8399 | -2.6001 | 0.25635 | -116.8121 | -116.954 | 3.7994 | -0.21973 | 2.0233 | 4.3167 | 4.2984 | -116.9266 | -116.835 | 0.082397 | -0.05951 | -4.3396 | 116.8579 | 114.2944 | 114.3539 | -13.5361 | -0.032044 | 0.059509 | -0.27924 | 120.694 | 118.9178 | 118.8583 | -0.29755 | 117.1509 | 107.9544 | 95.0546 | -121.55 | 121.2112 | 121.1929 | 116.6748 | -121.431
2075.6406 | 121.4539 | -116.9266 | 4.509 | 0.095073 | 0.060505 | -0.0080721 | 0.38104 | 0.068351 | 0.63174 | -0.034944 | 0.38789 | 3.9558 | 0.066941 | 0.10328 | 3.1576 | 0.054369 | -9.0134 | -0.050354 | -22.0047 | -2.3621 | 0.21973 | -116.8716 | -117.0273 | 3.7491 | -0.37994 | 1.8494 | 4.2389 | 4.216 | -117.0227 | -116.9083 | 0.054932 | -0.10071 | -4.2892 | 116.8762 | 114.5645 | 114.6652 | -13.5223 | -0.09613 | 0.018311 | -0.27008 | 120.6757 | 118.7759 | 118.7576 | -0.29297 | 117.1463 | 107.9132 | 94.9219 | -121.5363 | 121.1655 | 121.1426 | 116.5466 | -121.4172
2076.6406 | 121.4813 | -116.8945 | 4.5181 | 0.095073 | 0.053029 | -0.00059506 | 0.3693 | 0.070487 | 0.62747 | -0.050966 | 0.34212 | 3.9505 | 0.059465 | 0.095801 | 3.1544 | 0.056505 | -8.9905 | 0.30212 | -21.8857 | -2.2842 | 0.28381 | -116.7847 | -116.9312 | 3.8132 | -0.30212 | 1.886 | 4.2709 | 4.2389 | -116.9724 | -116.8762 | 0.10986 | -0.036621 | -4.2343 | 117.1967 | 114.6103 | 114.6469 | -13.5086 | -0.07782 | 0.01831 | -0.24719 | 120.7077 | 118.7805 | 118.7622 | -0.27923 | 117.1783 | 107.9041 | 95.0088 | -121.4493 | 121.1655 | 121.1334 | 116.5924 | -121.3943
2077.6406 | 121.4584 | -116.9449 | 4.5227 | 0.049296 | 0.077595 | 0.0047449 | 0.38104 | 0.070487 | 0.63708 | -0.040284 | 0.37263 | 3.9622 | 0.047715 | 0.084052 | 3.1651 | 0.052233 | -8.9264 | 0.004578 | -21.7758 | -2.4078 | 0.21973 | -116.8671 | -117.0319 | 3.7765 | -0.26093 | 1.8631 | 4.2435 | 4.1977 | -117.0273 | -116.9037 | 0.07782 | -0.086975 | -4.303 | 116.9495 | 114.537 | 114.624 | -13.4491 | -0.082398 | 0.041198 | -0.27924 | 120.7214 | 118.808 | 118.7668 | -0.32501 | 117.1646 | 108.0185 | 95.1691 | -121.5546 | 121.1884 | 121.1426 | 116.684 | -121.4264
2078.6406 | 121.5134 | -116.9861 | 4.4861 | -0.75942 | 0.060505 | 0.0036769 | 0.36289 | 0.068351 | 0.63922 | -0.042421 | 0.25056 | 3.9494 | 0.051988 | 0.091529 | 3.1448 | 0.052233 | -8.8669 | 0.041199 | -21.8719 | -2.3163 | 0.27924 | -116.9174 | -117.0456 | 3.7674 | -0.21057 | 1.799 | 4.1977 | 4.1702 | -117.041 | -116.9449 | 0.068665 | -0.059509 | -4.2068 | 117.0273 | 114.6698 | 114.7293 | -13.353 | -0.054932 | 0.041199 | -0.28839 | 120.7535 | 118.7851 | 118.7439 | -0.31586 | 117.2653 | 108.1192 | 95.1141 | -121.5317 | 121.1838 | 121.1563 | 116.7755 | -121.431
2079.6406 | 121.5088 | -116.922 | 4.5227 | 0.20188 | 0.085072 | -0.00059506 | 0.36716 | 0.059806 | 0.63387 | -0.041353 | 0.3116 | 3.9686 | 0.051988 | 0.092597 | 3.132 | 0.073595 | -9.0225 | 0.009155 | -21.8719 | -2.3392 | 0.2243 | -116.9266 | -117.0135 | 3.7445 | -0.3067 | 1.799 | 4.2526 | 4.2114 | -116.9952 | -116.9083 | -0.004578 | -0.091553 | -4.2984 | 116.9312 | 114.5828 | 114.6744 | -13.5452 | -0.073242 | 0.013733 | -0.27008 | 120.6665 | 118.721 | 118.7073 | -0.31128 | 117.1463 | 107.8995 | 95.05 | -121.5363 | 121.1746 | 121.1334 | 116.6153 | -121.431
2080.6406 | 121.4905 | -116.9357 | 4.5273 | -0.11855 | 0.062642 | -0.00059506 | 0.38104 | 0.069419 | 0.63815 | -0.045625 | 0.38789 | 3.9537 | 0.066941 | 0.092597 | 3.1448 | 0.057574 | -8.9676 | 0.004578 | -21.7255 | -2.3026 | 0.23346 | -116.8671 | -117.0044 | 3.772 | -0.11444 | 1.8356 | 4.2618 | 4.216 | -117.009 | -116.8854 | 0.068665 | -0.068665 | -4.2938 | 116.9403 | 114.6332 | 114.7018 | -13.4949 | -0.073242 | 0.050354 | -0.2655 | 120.7077 | 118.7714 | 118.721 | -0.31128 | 117.1692 | 107.9681 | 95.2103 | -121.5317 | 121.1975 | 121.1517 | 116.8213 | -121.4127
2081.6406 | 121.4905 | -117.0135 | 4.4312 | 0.15611 | 0.06905 | -0.018753 | 0.38852 | 0.073691 | 0.64242 | -0.040284 | 0.18953 | 3.9526 | 0.042375 | 0.10114 | 3.1502 | 0.06505 | -8.9539 | 0.045776 | -21.698 | -2.2568 | 0.30212 | -116.9266 | -117.0502 | 3.7125 | -0.10071 | 1.799 | 4.1565 | 4.1336 | -117.0456 | -116.9678 | 0.086975 | -0.036621 | -4.129 | 117.0593 | 114.7568 | 114.7934 | -13.385 | -0.032043 | 0.045777 | -0.27466 | 120.726 | 118.8126 | 118.7668 | -0.29755 | 117.3157 | 108.0597 | 95.3156 | -121.4813 | 121.17 | 121.1472 | 116.9128 | -121.3989
2082.6406 | 121.4951 | -117.0593 | 4.4037 | 0.18663 | 0.081868 | -0.00059506 | 0.38532 | 0.071555 | 0.64135 | -0.038148 | 0.3116 | 3.9473 | 0.057328 | 0.10114 | 3.147 | 0.057574 | -8.9859 | -0.004578 | -21.8857 | -2.2934 | 0.22888 | -116.9724 | -117.128 | 3.653 | -0.07782 | 1.7761 | 4.1428 | 4.0924 | -117.128 | -117.0181 | 0.086975 | -0.068665 | -4.1748 | 117.0547 | 114.7659 | 114.8346 | -13.3896 | -0.068665 | 0.041199 | -0.26093 | 120.7123 | 118.8354 | 118.7943 | -0.31128 | 117.2882 | 108.0734 | 95.1736 | -121.5317 | 121.2021 | 121.1517 | 116.9815 | -121.4218
2083.6406 | 121.5546 | -116.7572 | 4.6875 | 0.049296 | 0.040211 | 0.0047449 | 0.37464 | 0.075827 | 0.63708 | -0.045625 | 0.15901 | 3.9483 | 0.051988 | 0.08512 | 3.1406 | 0.066119 | -8.9355 | 0.059509 | -21.7667 | -2.6276 | 0.21973 | -116.7892 | -116.9357 | 3.9001 | 0.091553 | 2.0874 | 4.335 | 4.3259 | -116.8442 | -116.6977 | -0.032044 | -0.17853 | -4.4678 | 116.8167 | 114.1296 | 114.3082 | -13.623 | -0.086975 | 0.059509 | -0.35248 | 120.6573 | 118.8446 | 118.7851 | -0.36163 | 116.9769 | 107.8217 | 94.9905 | -121.6232 | 121.0922 | 121.0831 | 116.8488 | -121.3852
2084.6406 | 121.4996 | -116.8808 | 4.5364 | 0.064555 | 0.075459 | 0.010086 | 0.35434 | 0.067282 | 0.62426 | -0.042421 | 0.2353 | 3.9547 | 0.053056 | 0.087256 | 3.1523 | 0.05971 | -8.9722 | 0.059509 | -21.7804 | -2.3438 | 0.30212 | -116.7709 | -116.9312 | 3.8406 | -0.027466 | 2.0325 | 4.2938 | 4.2526 | -116.9357 | -116.8671 | 0.10986 | -0.050354 | -4.2343 | 116.9403 | 114.537 | 114.5874 | -13.5086 | -0.054932 | 0.013733 | -0.24262 | 120.7214 | 118.9133 | 118.8995 | -0.28381 | 117.1829 | 107.9086 | 95.1004 | -121.4676 | 121.1746 | 121.1334 | 116.8533 | -121.4035
2085.6406 | 121.5088 | -116.954 | 4.4678 | 0.064555 | 0.051961 | 0.0026089 | 0.36502 | 0.065146 | 0.63601 | -0.036012 | 0.28108 | 3.9526 | 0.053056 | 0.088325 | 3.1373 | 0.063982 | -8.8852 | 0.050354 | -21.8811 | -2.3849 | 0.24261 | -116.9083 | -117.0639 | 3.7262 | 0.17853 | 1.8539 | 4.2526 | 4.2206 | -117.041 | -116.9403 | 0.045777 | -0.10986 | -4.2252 | 117.0044 | 114.5691 | 114.679 | -13.353 | -0.086975 | 0.013733 | -0.21515 | 120.6802 | 118.808 | 118.7943 | -0.24719 | 117.1967 | 108.0688 | 95.0729 | -121.5317 | 121.2067 | 121.1746 | 117.1326 | -121.4081
2086.6406 | 121.4996 | -116.8716 | 4.6143 | 0.064555 | 0.056233 | -0.0027321 | 0.38104 | 0.074759 | 0.6264 | -0.038148 | 0.26582 | 3.9494 | 0.03383 | 0.08512 | 3.147 | 0.057574 | -8.9081 | 0.036621 | -22.0596 | -2.5223 | 0.24261 | -116.8167 | -116.9678 | 3.8727 | 0.15106 | 1.8723 | 4.303 | 4.2572 | -116.9266 | -116.8533 | 0.054932 | -0.09613 | -4.3716 | 116.9083 | 114.3494 | 114.4455 | -13.5223 | -0.054932 | 0.01831 | -0.31128 | 120.7443 | 118.7439 | 118.7256 | -0.35706 | 117.1143 | 107.9636 | 94.812 | -121.582 | 121.1746 | 121.1288 | 117.0227 | -121.4676
2087.6406 | 121.4813 | -116.8259 | 4.6234 | 0.064555 | 0.057301 | -0.015549 | 0.36716 | 0.066214 | 0.63387 | -0.038148 | 0.12849 | 3.9505 | 0.048783 | 0.086188 | 3.1448 | 0.061846 | -8.8852 | -0.022888 | -21.6934 | -2.2751 | 0.2655 | -116.6656 | -116.835 | 3.9139 | 0.58594 | 1.9135 | 4.3625 | 4.3396 | -116.8762 | -116.7938 | 0.16022 | -0.009155 | -4.3579 | 116.803 | 114.5508 | 114.5599 | -13.5086 | -0.050354 | 0.032044 | -0.26093 | 120.7397 | 118.7393 | 118.7073 | -0.28381 | 117.0914 | 107.9407 | 95.1324 | -121.4584 | 121.1884 | 121.1655 | 117.4118 | -121.4172
2088.6406 | 121.5088 | -116.8579 | 4.6051 | 0.049296 | 0.062642 | -0.0048681 | 0.36609 | 0.081168 | 0.6296 | -0.043489 | 0.29634 | 3.944 | 0.041307 | 0.091529 | 3.147 | 0.056505 | -8.876 | 0.036621 | -21.8353 | -2.3438 | 0.25177 | -116.8488 | -116.9861 | 3.8361 | 0.55847 | 2.0233 | 4.2938 | 4.2847 | -116.8762 | -116.835 | 0.009155 | -0.12817 | -4.3533 | 116.8945 | 114.5142 | 114.6423 | -13.4811 | -0.018311 | 0.022888 | -0.31128 | 120.694 | 118.8812 | 118.8583 | -0.32043 | 117.1097 | 107.9819 | 95.0226 | -121.5912 | 121.1517 | 121.1426 | 117.4164 | -121.4401
2089.6875 | 121.5042 | -116.8076 | 4.6417 | -0.11855 | 0.049824 | 0.014358 | 0.36289 | 0.070487 | 0.61892 | -0.044557 | -0.06987 | 3.9419 | 0.049852 | 0.095801 | 3.1406 | 0.063982 | -8.931 | -0.013733 | -21.6934 | -2.298 | 0.23346 | -116.7343 | -116.8716 | 3.9139 | 0 | 1.9958 | 4.3808 | 4.3488 | -116.8579 | -116.7618 | 0.073242 | -0.064087 | -4.4083 | 116.7938 | 114.5096 | 114.5737 | -13.5727 | -0.050354 | 0.045776 | -0.26093 | 120.7214 | 118.8034 | 118.7576 | -0.29297 | 117.041 | 107.8766 | 95.1141 | -121.5134 | 121.1884 | 121.1563 | 116.8076 | -121.4035
2090.6406 | 121.5225 | -116.8671 | 4.5914 | -0.072774 | 0.044484 | 0.017563 | 0.3725 | 0.071555 | 0.61465 | -0.048829 | 0.021682 | 3.943 | 0.051988 | 0.086188 | 3.1416 | 0.06505 | -8.9905 | -0.004578 | -21.6797 | -2.3987 | 0.24261 | -116.8076 | -116.9632 | 3.8177 | 0.21057 | 1.9684 | 4.3213 | 4.2801 | -116.9449 | -116.8488 | 0.059509 | -0.096131 | -4.3488 | 116.8625 | 114.4684 | 114.5645 | -13.5818 | -0.07782 | 0.01831 | -0.27008 | 120.6848 | 118.8354 | 118.8171 | -0.31128 | 117.1097 | 107.8766 | 95.1874 | -121.5546 | 121.1884 | 121.1472 | 117.0776 | -121.4401
2091.6406 | 121.5179 | -116.8762 | 4.5776 | -0.10329 | 0.045552 | 0.017563 | 0.36075 | 0.089713 | 0.62747 | -0.040284 | 0.0522 | 3.9483 | 0.047715 | 0.086188 | 3.1373 | 0.060778 | -8.9264 | 0.004578 | -21.4828 | -2.4078 | 0.21057 | -116.8213 | -116.9724 | 3.8589 | -0.13275 | 1.973 | 4.303 | 4.2526 | -116.9586 | -116.8167 | 0.054932 | -0.09613 | -4.3671 | 116.8808 | 114.4684 | 114.5645 | -13.504 | -0.082397 | 0.05951 | -0.27466 | 120.7352 | 118.8492 | 118.7897 | -0.32501 | 117.0868 | 107.9498 | 95.3934 | -121.55 | 121.1792 | 121.1288 | 116.7435 | -121.3943
2092.6406 | 121.5363 | -116.7755 | 4.6921 | -0.17959 | 0.037007 | 0.0047449 | 0.36182 | 0.081168 | 0.63174 | -0.047761 | -0.06987 | 3.944 | 0.060533 | 0.10114 | 3.147 | 0.056505 | -8.9264 | -0.009155 | -21.5424 | -2.2751 | 0.23804 | -116.7206 | -116.8625 | 3.9322 | 0.72784 | 2.0645 | 4.4083 | 4.3762 | -116.8442 | -116.7755 | 0.054932 | -0.086975 | -4.454 | 116.7664 | 114.5004 | 114.5874 | -13.6185 | -0.068664 | 0 | -0.28381 | 120.7077 | 118.84 | 118.84 | -0.31586 | 117.0136 | 107.8491 | 95.2332 | -121.5546 | 121.1838 | 121.1517 | 117.5034 | -121.4676
2093.6406 | 121.4584 | -116.9724 | 4.4815 | 0.2324 | 0.038075 | 0.0026089 | 0.37357 | 0.066214 | 0.62747 | -0.042421 | 0.036941 | 3.9376 | 0.041307 | 0.090461 | 3.132 | 0.053301 | -8.9722 | -0.009155 | -21.5195 | -2.3987 | 0.25177 | -116.9266 | -117.0593 | 3.6987 | -0.068665 | 1.8402 | 4.2068 | 4.1519 | -117.0639 | -116.9449 | 0.045776 | -0.086975 | -4.2297 | 116.9632 | 114.5737 | 114.6606 | -13.4537 | -0.091553 | 0.027466 | -0.27466 | 120.6711 | 118.8126 | 118.7851 | -0.32959 | 117.2241 | 108.0002 | 95.4529 | -121.5408 | 121.1792 | 121.1243 | 116.9037 | -121.4264
2094.6406 | 121.5317 | -116.9907 | 4.454 | -0.088033 | 0.051961 | 0.00047294 | 0.36823 | 0.066214 | 0.62426 | -0.043489 | 0.036941 | 3.9419 | 0.05626 | 0.095801 | 3.1406 | 0.054369 | -8.9127 | -0.004578 | -21.6476 | -2.2797 | 0.23346 | -116.9449 | -117.1005 | 3.7216 | 0.14648 | 1.9043 | 4.1656 | 4.1382 | -117.0593 | -116.9632 | 0.045777 | -0.10986 | -4.2206 | 116.9861 | 114.711 | 114.8209 | -13.3667 | -0.068664 | 0.027466 | -0.28839 | 120.7123 | 118.895 | 118.8675 | -0.31586 | 117.2241 | 108.078 | 95.343 | -121.5546 | 121.1563 | 121.1288 | 117.1371 | -121.4172
2095.6406 | 121.5088 | -116.6428 | 4.7928 | -0.27114 | 0.047688 | 0.0068819 | 0.36823 | 0.065146 | 0.6296 | -0.031739 | -0.11565 | 3.9302 | 0.048783 | 0.090461 | 3.1406 | 0.066119 | -8.9264 | -0.009155 | -21.6614 | -2.5497 | 0.24261 | -116.6061 | -116.7618 | 4.0466 | 0.78278 | 2.0828 | 4.5136 | 4.4769 | -116.7526 | -116.6245 | 0.036621 | -0.11902 | -4.5502 | 116.6336 | 114.093 | 114.212 | -13.7192 | -0.10986 | 0.01831 | -0.27924 | 120.6894 | 118.7256 | 118.7073 | -0.31586 | 116.8854 | 107.7164 | 94.9814 | -121.5546 | 121.1563 | 121.1197 | 117.4255 | -121.4172
2096.6406 | 121.3806 | -116.9357 | 4.5364 | -0.25588 | 0.031666 | 0.0047449 | 0.38532 | 0.072623 | 0.60931 | -0.05417 | 0.0064239 | 3.9344 | 0.051988 | 0.093665 | 3.1331 | 0.058642 | -9.0088 | -0.009155 | -21.6293 | -2.4353 | 0.26093 | -116.9312 | -117.1188 | 3.685 | 0.41199 | 1.7624 | 4.2206 | 4.1794 | -117.0227 | -116.8991 | 0.004578 | -0.1831 | -4.2755 | 116.9266 | 114.5004 | 114.6835 | -13.5452 | -0.086975 | 0.036621 | -0.31586 | 120.6207 | 118.6981 | 118.6615 | -0.35706 | 117.1967 | 107.9269 | 95.3064 | -121.6553 | 121.1563 | 121.1151 | 117.3477 | -121.4355
2097.6406 | 121.4584 | -117.009 | 4.4769 | -0.92727 | 0.023121 | 0.017563 | 0.36823 | 0.068351 | 0.61465 | -0.03708 | -0.0088351 | 3.9366 | 0.037034 | 0.081916 | 3.1395 | 0.061846 | -9.0179 | 0 | -21.7438 | -2.2797 | 0.24719 | -116.9632 | -117.1188 | 3.6758 | 0.46234 | 1.7578 | 4.2114 | 4.1519 | -117.0868 | -116.9495 | 0.045776 | -0.10986 | -4.2297 | 117.009 | 114.7293 | 114.8392 | -13.4949 | -0.07782 | 0.059509 | -0.2655 | 120.6848 | 118.7668 | 118.7073 | -0.32501 | 117.2562 | 107.991 | 95.2652 | -121.5958 | 121.2204 | 121.1609 | 117.4713 | -121.4264
2098.6406 | 121.4767 | -116.9815 | 4.4861 | -0.30166 | 0.062642 | 0.014358 | 0.3725 | 0.060874 | 0.62106 | -0.050966 | 1.3339 | 3.944 | 0.037034 | 0.088325 | 3.1341 | 0.063982 | -8.9813 | -0.013733 | -21.8719 | -2.2614 | 0.25177 | -116.8945 | -117.0227 | 3.7216 | -0.23804 | 1.8906 | 4.2297 | 4.184 | -117.0547 | -116.9632 | 0.086975 | -0.041199 | -4.2343 | 116.9678 | 114.7202 | 114.7614 | -13.4674 | -0.073243 | 0.01831 | -0.25635 | 120.7031 | 118.8721 | 118.8538 | -0.30212 | 117.2333 | 108.0002 | 95.1096 | -121.5088 | 121.2112 | 121.1655 | 116.7435 | -121.4493
2099.6406 | 121.463 | -116.7938 | 4.6097 | 0.52232 | 0.066914 | -0.0027321 | 0.37143 | 0.071555 | 0.64028 | -0.040284 | 0.17427 | 3.9419 | 0.051988 | 0.087256 | 3.1427 | 0.055437 | -8.7982 | -0.14191 | -21.9589 | -2.1881 | 0.27924 | -116.7572 | -116.9083 | 3.8818 | 0.23346 | 1.8768 | 4.3625 | 4.3442 | -116.8716 | -116.7892 | 0.036621 | -0.11444 | -4.3304 | 116.6519 | 114.6057 | 114.7202 | -13.4079 | -0.07782 | 0.004577 | -0.24719 | 120.6757 | 118.6707 | 118.6661 | -0.2655 | 117.0731 | 107.9956 | 94.8349 | -121.5179 | 121.1563 | 121.138 | 117.0273 | -121.3989
2100.6406 | 121.4813 | -116.748 | 4.7104 | -2.9109 | 0.039143 | -0.010208 | 0.35648 | 0.083304 | 0.63174 | -0.036012 | -0.06987 | 3.9344 | 0.049852 | 0.095801 | 3.1352 | 0.061846 | -8.9676 | 0.009155 | -21.8536 | -2.2476 | 0.28381 | -116.7252 | -116.8533 | 3.923 | 0.1236 | 1.9684 | 4.4266 | 4.4083 | -116.8076 | -116.7068 | 0.022888 | -0.10529 | -4.4266 | 116.7572 | 114.5004 | 114.6057 | -13.678 | -0.059509 | 0.041199 | -0.28381 | 120.6711 | 118.7164 | 118.6752 | -0.30212 | 117.0319 | 107.7805 | 94.8944 | -121.5637 | 121.1746 | 121.1563 | 116.8716 | -121.4172
2101.6406 | 121.4722 | -116.9998 | 4.4815 | -0.22536 | 0.053029 | 0.0079499 | 0.38959 | 0.066214 | 0.61785 | -0.044557 | 0.097976 | 3.9537 | 0.034898 | 0.088325 | 3.1363 | 0.063982 | -8.9996 | 0 | -22.0551 | -2.1103 | 0.27924 | -116.8716 | -117.009 | 3.7079 | 0.22888 | 1.7853 | 4.2435 | 4.184 | -117.0502 | -116.9815 | 0.12817 | -0.009155 | -4.2023 | 116.9998 | 114.8895 | 114.8987 | -13.4811 | -0.050354 | 0.018311 | -0.23804 | 120.7077 | 118.7851 | 118.7668 | -0.29755 | 117.2791 | 108.0002 | 94.9448 | -121.4905 | 121.2433 | 121.1838 | 117.2287 | -121.463
2102.6406 | 121.5088 | -116.7847 | 4.7241 | -0.27114 | 0.041279 | 0.015426 | 0.3757 | 0.08544 | 0.62747 | -0.040284 | -0.054612 | 3.9398 | 0.034898 | 0.086188 | 3.1363 | 0.053301 | -9.0271 | -0.004578 | -21.9223 | -2.2934 | 0.26093 | -116.7435 | -116.8671 | 4.0466 | -0.013733 | 1.9684 | 4.4678 | 4.4083 | -116.8121 | -116.7389 | 0.041199 | -0.082397 | -4.4632 | 116.7801 | 114.4913 | 114.5737 | -13.7512 | -0.027466 | 0.045776 | -0.25635 | 120.8313 | 118.7531 | 118.7073 | -0.31586 | 117.0456 | 107.7576 | 94.8624 | -121.5912 | 121.2524 | 121.1929 | 116.7709 | -121.463
2103.6406 | 121.5088 | -116.803 | 4.66 | -0.25588 | 0.02953 | 0.015426 | 0.37143 | 0.061942 | 0.6061 | -0.052034 | 0.021682 | 3.9302 | 0.035966 | 0.10755 | 3.1363 | 0.058642 | -8.9722 | 0.09613 | -21.8033 | -2.211 | 0.23346 | -116.7343 | -116.8671 | 3.9322 | 0.16022 | 2.0874 | 4.3854 | 4.3396 | -116.8625 | -116.7755 | 0.068665 | -0.064086 | -4.4266 | 116.8991 | 114.592 | 114.6561 | -13.6322 | -0.059509 | 0.027466 | -0.27466 | 120.7352 | 118.8904 | 118.8629 | -0.32043 | 117.0364 | 107.8308 | 94.9997 | -121.5271 | 121.1884 | 121.1426 | 116.9632 | -121.4355
2104.6406 | 121.4813 | -116.9769 | 4.4998 | 0.20188 | 0.044484 | -0.0070041 | 0.38745 | 0.076896 | 0.64456 | -0.038148 | 0.3116 | 3.9419 | 0.047715 | 0.10328 | 3.1491 | 0.05971 | -9.0363 | -0.022888 | -22.2656 | -2.3575 | 0.24261 | -116.8945 | -117.0639 | 3.7216 | -0.004578 | 1.7853 | 4.2297 | 4.1794 | -117.0135 | -116.9312 | 0.082398 | -0.086975 | -4.2572 | 116.954 | 114.6194 | 114.7064 | -13.5361 | -0.036621 | 0.045777 | -0.27008 | 120.6985 | 118.7622 | 118.7164 | -0.32043 | 117.2195 | 107.9407 | 94.7113 | -121.5637 | 121.2067 | 121.1563 | 116.9724 | -121.431
2105.6406 | 121.4767 | -116.8625 | 4.6005 | -0.25588 | 0.013508 | 0.023971 | 0.35968 | 0.070487 | 0.60397 | -0.044557 | 0.11323 | 3.9419 | 0.038102 | 0.099006 | 3.1192 | 0.061846 | -9.0683 | 0.073242 | -22.2382 | -2.2568 | 0.23346 | -116.8213 | -116.9678 | 3.8406 | -0.13733 | 1.7761 | 4.3213 | 4.2664 | -116.9403 | -116.8304 | 0.041199 | -0.10528 | -4.3671 | 116.9357 | 114.6057 | 114.711 | -13.6688 | -0.07782 | 0.032044 | -0.27924 | 120.7031 | 118.6386 | 118.6066 | -0.33417 | 117.0959 | 107.7942 | 94.6243 | -121.5683 | 121.1838 | 121.1288 | 116.7252 | -121.431
2106.6406 | 121.4905 | -116.8121 | 4.6234 | -0.24062 | 0.015645 | 0.026108 | 0.36182 | 0.074759 | 0.60931 | -0.052034 | -0.0088351 | 3.9323 | 0.025285 | 0.080848 | 3.1384 | 0.063982 | -9.0225 | 0.086975 | -22.4213 | -2.2385 | 0.22888 | -116.7664 | -116.89 | 3.9047 | 0.059509 | 1.8036 | 4.3671 | 4.303 | -116.89 | -116.7938 | 0.045777 | -0.07782 | -4.3945 | 116.8991 | 114.5737 | 114.6515 | -13.6459 | -0.07782 | 0.018311 | -0.25635 | 120.7169 | 118.6157 | 118.5974 | -0.32043 | 117.041 | 107.7896 | 94.3909 | -121.5134 | 121.1792 | 121.1151 | 116.8716 | -121.4172
2107.6406 | 121.4859 | -116.6611 | 4.7928 | -0.2864 | 0.014576 | 0.0026089 | 0.36075 | 0.06301 | 0.61251 | -0.055238 | -0.95488 | 3.9291 | 0.042375 | 0.090461 | 3.1267 | 0.060778 | -9.0317 | 0.018311 | -22.3389 | -2.3529 | 0.24261 | -116.6107 | -116.7297 | 4.0512 | -0.18768 | 1.9867 | 4.5364 | 4.4998 | -116.716 | -116.629 | 0.050354 | -0.068664 | -4.5502 | 116.6794 | 114.3082 | 114.3768 | -13.8245 | -0.054931 | 0.032044 | -0.25635 | 120.7123 | 118.6478 | 118.6157 | -0.29297 | 116.9037 | 107.6294 | 94.3222 | -121.5225 | 121.1975 | 121.1609 | 116.4734 | -121.4218
2108.6406 | 121.5225 | -116.6702 | 4.7974 | -0.27114 | 0.011372 | 0.016495 | 0.3693 | 0.072623 | 0.60504 | -0.048829 | -0.06987 | 3.9195 | 0.028489 | 0.10755 | 3.1299 | 0.05971 | -8.9996 | 0.086975 | -22.0871 | -2.2842 | 0.2243 | -116.6107 | -116.7435 | 4.0604 | 3.0579 | 1.9547 | 4.5319 | 4.4724 | -116.7389 | -116.6656 | 0.059509 | -0.073242 | -4.5731 | 116.7572 | 114.386 | 114.4592 | -13.797 | -0.068665 | 0.004578 | -0.2655 | 120.7306 | 118.6249 | 118.6203 | -0.32501 | 116.8945 | 107.6706 | 94.5831 | -121.5408 | 121.2021 | 121.1426 | 119.7281 | -121.463
2109.6406 | 121.5179 | -116.5512 | 4.8752 | 0.41551 | 0.067982 | -0.00059506 | 0.37464 | 0.070487 | 0.63281 | -0.045625 | 0.571 | 3.9387 | 0.057328 | 0.08512 | 3.1352 | 0.052233 | -9.0454 | -0.009155 | -22.0047 | -2.2568 | 0.26093 | -116.5009 | -116.6473 | 4.2068 | -0.19226 | 2.0508 | 4.6326 | 4.5547 | -116.6153 | -116.5283 | 0.050354 | -0.096131 | -4.6143 | 116.5421 | 114.2944 | 114.3906 | -13.9206 | -0.064087 | 0.022888 | -0.24261 | 120.7581 | 118.602 | 118.5791 | -0.32043 | 116.8121 | 107.5058 | 94.5465 | -121.5225 | 121.1838 | 121.106 | 116.3589 | -121.4035
2110.6406 | 121.6232 | -116.7206 | 4.6692 | 0.034038 | 0.0049632 | 0.0079499 | 0.36609 | 0.068351 | 0.61251 | -0.043489 | 0.0522 | 3.9323 | 0.028489 | 0.094733 | 3.1245 | 0.061846 | -8.9767 | 0.14648 | -21.9406 | -2.0828 | 0.21057 | -116.6656 | -116.8259 | 4.0466 | 0.16022 | 1.9318 | 4.39 | 4.3442 | -116.7938 | -116.7068 | 0.054932 | -0.10529 | -4.4586 | 116.8671 | 114.6378 | 114.743 | -13.6459 | -0.073242 | 0.013733 | -0.27923 | 120.7672 | 118.6523 | 118.6386 | -0.32501 | 116.9312 | 107.7438 | 94.78 | -121.4951 | 121.1105 | 121.0648 | 116.8808 | -121.376
2111.6406 | 121.6232 | -116.7435 | 4.6051 | 0.00352 | 0.00069119 | 0.01329 | 0.37036 | 0.067282 | 0.59649 | -0.045625 | 0.15901 | 3.9195 | 0.015672 | 0.096869 | 3.1256 | 0.06505 | -8.9951 | 0.20142 | -21.5927 | -2.1378 | 0.22888 | -116.7297 | -116.8625 | 4.0192 | -0.073242 | 1.9226 | 4.3488 | 4.2847 | -116.8213 | -116.748 | 0.013733 | -0.11902 | -4.3762 | 116.9449 | 114.6057 | 114.7247 | -13.6002 | -0.07782 | -0.004578 | -0.25635 | 120.7626 | 118.6661 | 118.6707 | -0.32043 | 116.9724 | 107.7484 | 95.1508 | -121.4676 | 121.0922 | 121.0281 | 116.6702 | -121.3531
2112.6406 | 121.5271 | -116.6016 | 4.8065 | -0.026997 | 0.011372 | 0.011154 | 0.34473 | 0.069419 | 0.60504 | -0.047761 | 0.082718 | 3.9216 | 0.037034 | 0.094733 | 3.1384 | 0.053301 | -8.9859 | 0.13733 | -21.524 | -2.0142 | 0.2243 | -116.5283 | -116.6611 | 4.2023 | 0.17395 | 2.1469 | 4.5456 | 4.4815 | -116.6473 | -116.6153 | 0.073242 | -0.05951 | -4.5822 | 116.7389 | 114.5874 | 114.6469 | -13.7924 | -0.045777 | -0.013733 | -0.26093 | 120.8038 | 118.7485 | 118.7622 | -0.32501 | 116.8259 | 107.6157 | 95.0775 | -121.4676 | 121.1472 | 121.0831 | 116.7755 | -121.4218
2113.6406 | 121.6232 | -116.8533 | 4.5319 | 0.079814 | 0.01244 | 0.0015409 | 0.36716 | 0.061942 | 0.61572 | -0.050966 | 0.14375 | 3.9238 | 0.032762 | 0.094733 | 3.1224 | 0.058642 | -8.9905 | 0.19684 | -21.6385 | -2.1149 | 0.23804 | -116.8167 | -116.9724 | 3.9368 | 0.43488 | 1.9135 | 4.2618 | 4.184 | -116.9403 | -116.8488 | 0.036622 | -0.11902 | -4.2938 | 117.0502 | 114.7385 | 114.8575 | -13.5223 | -0.086975 | 0.004578 | -0.27008 | 120.7901 | 118.7668 | 118.7622 | -0.3479 | 117.0914 | 107.8629 | 95.2148 | -121.5042 | 121.1151 | 121.0373 | 117.2882 | -121.3806
2114.7031 | 121.5866 | -116.5878 | 4.7928 | 0.14085 | 0.043416 | 0.0047449 | 0.38745 | 0.070487 | 0.62533 | -0.050966 | 0.50996 | 3.9526 | 0.05626 | 0.086188 | 3.1256 | 0.060778 | -8.9676 | 0.1236 | -21.6843 | -2.179 | 0.20599 | -116.5558 | -116.7023 | 4.1885 | 0.9201 | 2.0645 | 4.4998 | 4.454 | -116.684 | -116.5649 | 0.032044 | -0.11444 | -4.5868 | 116.7114 | 114.4089 | 114.5233 | -13.7604 | -0.09613 | 0.022889 | -0.29297 | 120.7764 | 118.6523 | 118.6295 | -0.33875 | 116.7938 | 107.6202 | 94.9036 | -121.4951 | 121.0876 | 121.0419 | 117.5079 | -121.3577
2115.6406 | 121.6003 | -116.6016 | 4.7607 | 0.35447 | 0.0060322 | 0.010086 | 0.38639 | 0.064078 | 0.61572 | -0.048829 | 0.097976 | 3.9195 | 0.030626 | 0.090461 | 3.1288 | 0.062914 | -8.9355 | 0.17395 | -21.5378 | -2.2018 | 0.20599 | -116.5695 | -116.716 | 4.1702 | 0.068665 | 2.0874 | 4.4769 | 4.4495 | -116.6885 | -116.6016 | 0.032043 | -0.11444 | -4.5547 | 116.7755 | 114.3997 | 114.5142 | -13.6963 | -0.086976 | 0 | -0.28381 | 120.7718 | 118.689 | 118.689 | -0.31128 | 116.8076 | 107.666 | 95.0638 | -121.4767 | 121.0785 | 121.051 | 116.6702 | -121.3623
2116.6406 | 121.582 | -116.6748 | 4.7241 | 0.079814 | 0.014576 | 0.0068819 | 0.35648 | 0.065146 | 0.61038 | -0.050966 | 0.37263 | 3.9259 | 0.044511 | 0.089393 | 3.1171 | 0.055437 | -8.9951 | 0.10071 | -21.6705 | -2.1332 | 0.23346 | -116.6656 | -116.8167 | 4.097 | 0.013733 | 2.0782 | 4.4266 | 4.3854 | -116.7618 | -116.6656 | 0.009156 | -0.14191 | -4.4907 | 116.7755 | 114.5416 | 114.6835 | -13.7192 | -0.086975 | 0.009156 | -0.29755 | 120.7718 | 118.7531 | 118.7439 | -0.33875 | 116.9083 | 107.6797 | 95.0043 | -121.5408 | 121.1014 | 121.0602 | 116.6885 | -121.3898
2117.6406 | 121.5591 | -116.7572 | 4.6371 | 0.38499 | -0.0014448 | 0.0047449 | 0.38318 | 0.06301 | 0.60824 | -0.044557 | 0.37263 | 3.9227 | 0.023149 | 0.096869 | 3.1331 | 0.073595 | -8.9951 | 0.086975 | -21.8033 | -2.1973 | 0.21973 | -116.748 | -116.8854 | 3.9825 | 0.31128 | 1.9913 | 4.3533 | 4.303 | -116.8579 | -116.7618 | 0.009155 | -0.12817 | -4.4174 | 116.8442 | 114.5599 | 114.6881 | -13.6322 | -0.10071 | -0.004578 | -0.28381 | 120.7397 | 118.7485 | 118.7531 | -0.33417 | 116.9769 | 107.7621 | 94.9539 | -121.5225 | 121.1105 | 121.0602 | 117.0685 | -121.3989
2118.6406 | 121.5775 | -116.8533 | 4.5547 | 0.27818 | -0.0035808 | 0.0090179 | 0.37784 | 0.060874 | 0.61038 | -0.047761 | 0.61677 | 3.9173 | 0.031694 | 0.087256 | 3.1245 | 0.057574 | -9.0363 | 0.054932 | -21.7804 | -2.1881 | 0.2243 | -116.8076 | -116.9266 | 3.9139 | -0.19684 | 1.8814 | 4.2252 | 4.1931 | -116.8991 | -116.8716 | 0.045777 | -0.073242 | -4.3304 | 116.9083 | 114.6652 | 114.7385 | -13.591 | -0.045776 | -0.01831 | -0.32959 | 120.7672 | 118.7347 | 118.7531 | -0.36163 | 117.0776 | 107.8171 | 95.0729 | -121.4813 | 121.0785 | 121.0464 | 116.6565 | -121.4264
2119.6406 | 121.4951 | -116.8808 | 4.5822 | -0.31691 | 0.037007 | -0.0016631 | 0.38104 | 0.073691 | 0.64135 | -0.041353 | 3.1345 | 3.9462 | 0.055192 | 0.091529 | 3.1384 | 0.031939 | -9.0729 | 0.009155 | -21.785 | -2.2568 | 0.25635 | -116.835 | -116.922 | 3.8589 | -0.21057 | 1.7853 | 4.3488 | 4.2847 | -116.9632 | -116.8808 | 0.045776 | -0.041199 | -4.3259 | 116.89 | 114.624 | 114.6652 | -13.6551 | -0.082398 | 0 | -0.23346 | 120.7397 | 118.6661 | 118.6661 | -0.29755 | 117.1371 | 107.8079 | 95.0958 | -121.5042 | 121.2296 | 121.1655 | 116.6702 | -121.463
2120.6406 | 121.5775 | -116.7984 | 4.628 | 0.32395 | 0.027394 | 0.0047449 | 0.35434 | 0.059806 | 0.61572 | -0.038148 | 0.52522 | 3.9334 | 0.03383 | 0.08512 | 3.1331 | 0.060778 | -9.0912 | 0.10071 | -21.7163 | -2.1881 | 0.22888 | -116.748 | -116.8671 | 3.9642 | 0.20599 | 1.9547 | 4.3442 | 4.2938 | -116.8716 | -116.7618 | 0.050354 | -0.068664 | -4.3991 | 116.8991 | 114.6103 | 114.679 | -13.7192 | -0.073242 | 0.036621 | -0.28381 | 120.7626 | 118.7531 | 118.7164 | -0.33417 | 117.0273 | 107.7072 | 95.0821 | -121.4951 | 121.1426 | 121.0922 | 117.0044 | -121.3898
2121.6406 | 121.5637 | -116.7297 | 4.6646 | 0.32395 | 0.019917 | 0.0058129 | 0.34793 | 0.06301 | 0.60183 | -0.042421 | 0.40315 | 3.9334 | 0.032762 | 0.095801 | 3.1309 | 0.05971 | -9.1736 | 0.064087 | -21.7346 | -2.2568 | 0.2243 | -116.6336 | -116.7938 | 3.7857 | 0.93842 | 2.0325 | 4.3762 | 4.2938 | -116.8167 | -116.7023 | 0.09613 | -0.064087 | -4.4403 | 116.7938 | 114.473 | 114.537 | -13.8382 | -0.086975 | 0.027465 | -0.28839 | 120.5154 | 118.7622 | 118.7347 | -0.37079 | 116.954 | 107.5562 | 94.9951 | -121.4584 | 121.106 | 121.0236 | 117.6682 | -121.3669
2122.6406 | 121.5683 | -116.684 | 4.7287 | 0.29344 | 0.023121 | 0.0068819 | 0.36182 | 0.059806 | 0.61572 | -0.050966 | 0.54048 | 3.9291 | 0.037034 | 0.089393 | 3.1331 | 0.060778 | -9.1232 | 0.073242 | -22.1146 | -2.2156 | 0.23346 | -116.6336 | -116.7709 | 4.0741 | 0.3067 | 2.1515 | 4.4357 | 4.3808 | -116.7435 | -116.6656 | 0.050354 | -0.086975 | -4.4952 | 116.7572 | 114.4684 | 114.5554 | -13.8519 | -0.059509 | 0.018311 | -0.29297 | 120.7581 | 118.8354 | 118.8171 | -0.3479 | 116.9174 | 107.5607 | 94.5694 | -121.4996 | 121.1197 | 121.0648 | 116.9907 | -121.3943
2123.6406 | 121.6141 | -116.8625 | 4.5502 | 0.21714 | 0.02419 | 0.01329 | 0.36075 | 0.073691 | 0.61038 | -0.052034 | 0.34212 | 3.9366 | 0.041307 | 0.10114 | 3.1277 | 0.054369 | -9.1278 | 0.064087 | -22.2565 | -2.1378 | 0.22888 | -116.8076 | -116.9312 | 3.9322 | 0.94299 | 1.9775 | 4.2252 | 4.1794 | -116.954 | -116.8442 | 0.054932 | -0.068664 | -4.3213 | 116.9266 | 114.7247 | 114.7934 | -13.678 | -0.091553 | 0.018311 | -0.32501 | 120.7947 | 118.84 | 118.8217 | -0.37079 | 117.0914 | 107.7347 | 94.606 | -121.4813 | 121.0876 | 121.0419 | 117.8055 | -121.3943
2124.6406 | 121.5134 | -116.716 | 4.7241 | -0.13381 | 0.023121 | -0.0027321 | 0.38532 | 0.074759 | 0.64883 | -0.044557 | -0.22246 | 3.9312 | 0.05092 | 0.089393 | 3.147 | 0.04262 | -9.1003 | 0.009155 | -22.4945 | -2.2842 | 0.24719 | -116.6931 | -116.8396 | 4.0237 | 1.0117 | 2.0187 | 4.4678 | 4.3945 | -116.8121 | -116.7252 | 0.022888 | -0.1236 | -4.4769 | 116.7252 | 114.4318 | 114.5554 | -13.8245 | -0.096131 | -0.009156 | -0.25635 | 120.7397 | 118.7347 | 118.7439 | -0.32959 | 116.9632 | 107.6157 | 94.2215 | -121.5637 | 121.1838 | 121.1105 | 117.7277 | -121.4493
2125.6406 | 121.5637 | -116.6519 | 4.7424 | 0.35447 | 0.025258 | 0.0047449 | 0.35434 | 0.060874 | 0.61999 | -0.046693 | 0.64729 | 3.9248 | 0.043443 | 0.095801 | 3.1267 | 0.062914 | -9.082 | 0.13275 | -22.6135 | -2.211 | 0.2243 | -116.6107 | -116.7389 | 4.1382 | 0.96588 | 2.092 | 4.4586 | 4.3991 | -116.7343 | -116.6428 | 0.041199 | -0.086975 | -4.5181 | 116.7847 | 114.4409 | 114.5279 | -13.8245 | -0.082397 | 0.009156 | -0.28381 | 120.7901 | 118.7439 | 118.7347 | -0.34332 | 116.8762 | 107.5699 | 94.0384 | -121.4813 | 121.1105 | 121.051 | 117.6178 | -121.3852
2126.6406 | 121.5546 | -116.8716 | 4.5227 | 0.46128 | 0.01244 | -0.00059506 | 0.37464 | 0.070487 | 0.61144 | -0.041353 | 0.55574 | 3.9291 | 0.047715 | 0.095801 | 3.1288 | 0.062914 | -9.1003 | 0.10529 | -22.7005 | -2.3209 | 0.21515 | -116.8213 | -116.9586 | 3.9093 | 1.2405 | 1.9226 | 4.2572 | 4.2023 | -116.9495 | -116.8671 | 0.050354 | -0.086975 | -4.3076 | 116.9769 | 114.5508 | 114.6378 | -13.623 | -0.07782 | 0.004578 | -0.2655 | 120.7809 | 118.7943 | 118.7897 | -0.32043 | 117.0868 | 107.7713 | 94.1711 | -121.4813 | 121.1288 | 121.0739 | 118.1122 | -121.3898
2127.6406 | 121.5454 | -116.9174 | 4.5319 | 0.52232 | 0.027394 | -0.0048681 | 0.34259 | 0.064078 | 0.62533 | -0.052034 | 0.66255 | 3.9248 | 0.042375 | 0.089393 | 3.1235 | 0.058642 | -9.0454 | 0.11444 | -22.6364 | -2.211 | 0.2243 | -116.8442 | -116.9632 | 3.9185 | 1.2314 | 1.8997 | 4.2252 | 4.1656 | -116.9449 | -116.8579 | 0.073242 | -0.045777 | -4.3076 | 117.0319 | 114.7064 | 114.7522 | -13.5773 | -0.027466 | 0.059509 | -0.3067 | 120.8359 | 118.8171 | 118.7576 | -0.36621 | 117.1417 | 107.872 | 94.281 | -121.4951 | 121.1426 | 121.0831 | 118.1488 | -121.3898
2128.6406 | 121.5958 | -116.9907 | 4.4128 | 0.53758 | 0.023121 | 0.0090179 | 0.37357 | 0.0801 | 0.60824 | -0.047761 | 0.60152 | 3.9291 | 0.034898 | 0.087256 | 3.1352 | 0.061846 | -9.0454 | 0.091553 | -22.4533 | -2.1469 | 0.2243 | -116.9174 | -117.0776 | 3.7994 | 1.2268 | 1.8494 | 4.1473 | 4.1016 | -117.0593 | -116.922 | 0.073243 | -0.086975 | -4.1885 | 117.0822 | 114.8438 | 114.9307 | -13.4583 | -0.068664 | 0.068665 | -0.2655 | 120.7901 | 118.84 | 118.7714 | -0.31128 | 117.215 | 107.9453 | 94.5374 | -121.4905 | 121.138 | 121.0922 | 118.2175 | -121.3348
2129.6406 | 121.582 | -116.9128 | 4.4998 | 0.2324 | 0.016713 | 0.022903 | 0.35648 | 0.066214 | 0.61465 | -0.041353 | 0.25056 | 3.9323 | 0.040239 | 0.081916 | 3.1299 | 0.067187 | -9.0225 | 0.045776 | -22.4945 | -2.3849 | 0.1831 | -116.89 | -117.0181 | 3.8864 | 0.94299 | 1.9409 | 4.2389 | 4.184 | -116.9724 | -116.8854 | 0.022888 | -0.10529 | -4.3167 | 116.9586 | 114.5279 | 114.6332 | -13.5223 | -0.059509 | 0.027466 | -0.26093 | 120.7993 | 118.8538 | 118.8263 | -0.31586 | 117.0959 | 107.8903 | 94.4183 | -121.5179 | 121.1517 | 121.0968 | 117.8558 | -121.3852
2130.6406 | 121.5775 | -116.8533 | 4.5319 | 0.079814 | 0.041279 | 0.0036769 | 0.35968 | 0.073691 | 0.61892 | -0.03708 | 0.67781 | 3.9366 | 0.035966 | 0.076575 | 3.1395 | 0.057574 | -8.9905 | 0.11902 | -22.5128 | -2.1515 | 0.21515 | -116.803 | -116.9998 | 3.9505 | 0.71869 | 1.9409 | 4.2618 | 4.1794 | -116.9586 | -116.8671 | 0.050354 | -0.14648 | -4.3167 | 116.9724 | 114.7018 | 114.8483 | -13.5223 | -0.10528 | -0.013732 | -0.27008 | 120.8038 | 118.7943 | 118.808 | -0.35248 | 117.0685 | 107.8629 | 94.3405 | -121.5317 | 121.1151 | 121.0327 | 117.572 | -121.3989
2131.6406 | 121.5866 | -116.8442 | 4.5136 | 0.2324 | 0.045552 | 0.012222 | 0.36502 | 0.070487 | 0.64135 | -0.034944 | 0.67781 | 3.9483 | 0.061601 | 0.089393 | 3.1352 | 0.057574 | -8.9584 | 0.09613 | -22.3434 | -2.0691 | 0.20599 | -116.8488 | -116.9495 | 3.9413 | 0.42114 | 1.9958 | 4.2206 | 4.184 | -116.9449 | -116.835 | -0.004578 | -0.10529 | -4.3076 | 116.9403 | 114.7751 | 114.8804 | -13.472 | -0.10071 | 0.009155 | -0.29297 | 120.7855 | 118.84 | 118.8309 | -0.32959 | 117.0502 | 107.8857 | 94.5007 | -121.463 | 121.0648 | 121.0281 | 117.2653 | -121.3486
2132.6406 | 121.6003 | -116.9632 | 4.4174 | 0.64439 | 0.040211 | 0.0026089 | 0.36182 | 0.083304 | 0.62747 | -0.032808 | 0.60152 | 3.9312 | 0.045579 | 0.089393 | 3.148 | 0.038348 | -8.9813 | 0.1236 | -22.4625 | -2.0828 | 0.2243 | -116.9128 | -117.0456 | 3.8223 | 0.52185 | 1.8723 | 4.1061 | 4.0512 | -117.0639 | -116.954 | 0.050354 | -0.082397 | -4.1931 | 117.0868 | 114.8804 | 114.9628 | -13.3987 | -0.10071 | 0.009155 | -0.31128 | 120.7855 | 118.8354 | 118.8263 | -0.36621 | 117.1875 | 107.9819 | 94.5007 | -121.463 | 121.0693 | 121.0144 | 117.485 | -121.3715
2133.6406 | 121.5958 | -116.7297 | 4.6875 | 0.7512 | 0.037007 | 0.00047294 | 0.3725 | 0.070487 | 0.63815 | -0.036012 | 0.61677 | 3.9291 | 0.047715 | 0.095801 | 3.1384 | 0.061846 | -8.9722 | 0.11444 | -22.4213 | -2.1103 | 0.19226 | -116.6656 | -116.8488 | 4.1016 | 0.14648 | 2.0828 | 4.3854 | 4.3396 | -116.8076 | -116.6885 | 0.064087 | -0.11902 | -4.4952 | 116.8442 | 114.6194 | 114.7385 | -13.6597 | -0.07782 | 0.041198 | -0.30212 | 120.8313 | 118.8126 | 118.7714 | -0.3479 | 116.922 | 107.7576 | 94.3085 | -121.5363 | 121.1151 | 121.0693 | 116.8762 | -121.376
2134.6406 | 121.6324 | -116.8442 | 4.5502 | 0.4918 | 0.044484 | 0.0036769 | 0.37036 | 0.061942 | 0.63494 | -0.030671 | 0.47945 | 3.9387 | 0.047715 | 0.089393 | 3.1299 | 0.054369 | -8.9813 | 0.059509 | -22.4121 | -2.0416 | 0.21515 | -116.8121 | -116.9266 | 3.9734 | 0.59052 | 1.8768 | 4.248 | 4.2252 | -116.9312 | -116.803 | 0.032043 | -0.082398 | -4.335 | 116.9037 | 114.8026 | 114.8849 | -13.5315 | -0.086975 | 0.041198 | -0.30212 | 120.8176 | 118.721 | 118.6798 | -0.32501 | 117.0593 | 107.8629 | 94.4321 | -121.4767 | 121.0922 | 121.0693 | 117.4347 | -121.3531
2135.6406 | 121.6507 | -116.9586 | 4.4083 | 0.53758 | 0.035939 | -0.0016631 | 0.37357 | 0.077964 | 0.63601 | -0.048829 | 0.67781 | 3.9398 | 0.043443 | 0.07978 | 3.1288 | 0.049029 | -9.0042 | 0.10529 | -22.0047 | -2.0325 | 0.21057 | -116.8854 | -117.0227 | 3.7949 | 0.83313 | 1.7899 | 4.1428 | 4.0924 | -117.0776 | -116.9632 | 0.073242 | -0.064087 | -4.1977 | 117.0639 | 114.9261 | 114.9902 | -13.4125 | -0.11902 | -0.004578 | -0.2655 | 120.7535 | 118.7485 | 118.7531 | -0.31586 | 117.1692 | 107.9544 | 94.9539 | -121.431 | 121.1014 | 121.051 | 117.7917 | -121.3715
2136.6406 | 121.6232 | -116.803 | 4.5822 | 0.29344 | 0.056233 | 0.00047294 | 0.3693 | 0.073691 | 0.63387 | -0.028535 | 0.66255 | 3.9323 | 0.048783 | 0.08512 | 3.1341 | 0.060778 | -8.9859 | 0.10071 | -22.0779 | -2.1561 | 0.20142 | -116.7664 | -116.922 | 4.0054 | 1.1032 | 1.8402 | 4.3076 | 4.2526 | -116.89 | -116.8259 | 0.036622 | -0.11902 | -4.3808 | 116.9037 | 114.6469 | 114.7659 | -13.5681 | -0.086975 | -0.022888 | -0.27466 | 120.8084 | 118.6432 | 118.6661 | -0.32959 | 117.0044 | 107.8171 | 94.725 | -121.5042 | 121.1105 | 121.0556 | 117.9062 | -121.4081
2137.6406 | 121.6187 | -116.7343 | 4.6326 | 0.58335 | 0.070118 | -0.00059506 | 0.36716 | 0.060874 | 0.6296 | -0.031739 | 0.571 | 3.9323 | 0.044511 | 0.088325 | 3.1352 | 0.058642 | -8.9813 | 0.086975 | -22.1741 | -2.179 | 0.20599 | -116.6977 | -116.8854 | 4.0604 | 0.90179 | 2.0142 | 4.3396 | 4.3121 | -116.8533 | -116.716 | 0.036621 | -0.15106 | -4.4266 | 116.8213 | 114.5554 | 114.7064 | -13.6139 | -0.11902 | 0.018311 | -0.29297 | 120.7947 | 118.7485 | 118.7302 | -0.32043 | 116.9403 | 107.753 | 94.5602 | -121.5179 | 121.0739 | 121.0464 | 117.6361 | -121.3486
2139 | 121.6095 | -116.8808 | 4.5044 | 0.12559 | 0.0017592 | 0.020767 | 0.35327 | 0.069419 | 0.58581 | -0.043489 | 0.3116 | 3.9163 | 0.040239 | 0.095801 | 3.1288 | 0.069323 | -9.0408 | 0.10529 | -22.1146 | -2.4811 | 0.24261 | -116.835 | -116.9998 | 3.9093 | 0 | 1.9272 | 4.2297 | 4.1885 | -116.9174 | -116.8213 | 0.045776 | -0.11902 | -4.2618 | 116.9861 | 114.3997 | 114.5187 | -13.5452 | -0.036621 | 0.059509 | -0.27466 | 120.7901 | 118.808 | 118.7485 | -0.31586 | 117.1234 | 107.84 | 94.7662 | -121.5042 | 121.1105 | 121.0693 | 116.8808 | -121.3257
2139.6406 | 121.582 | -116.9357 | 4.4678 | 0.56809 | 0.054097 | 0.0036769 | 0.3693 | 0.074759 | 0.63922 | -0.044557 | 0.571 | 3.9238 | 0.03383 | 0.07978 | 3.1384 | 0.051165 | -9.0317 | 0.027466 | -22.1054 | -2.1927 | 0.24261 | -116.9037 | -117.0639 | 3.8589 | -0.082397 | 1.8448 | 4.2068 | 4.1336 | -117.0547 | -116.9174 | 0.032043 | -0.12817 | -4.2252 | 116.9632 | 114.743 | 114.8712 | -13.4994 | -0.11902 | 0.018311 | -0.26093 | 120.7947 | 118.7805 | 118.7622 | -0.33417 | 117.1783 | 107.9041 | 94.8303 | -121.5317 | 121.1426 | 121.0693 | 116.8533 | -121.3852
2140.6406 | 121.6187 | -116.9998 | 4.4357 | 0.17137 | 0.0092362 | -0.00059506 | 0.36823 | 0.061942 | 0.60717 | -0.042421 | 0.35738 | 3.9248 | 0.024217 | 0.089393 | 3.1277 | 0.070391 | -9.1049 | 0.091553 | -22.3068 | -2.1881 | 0.21515 | -116.922 | -117.0593 | 3.7903 | 0.009155 | 1.8906 | 4.1702 | 4.1107 | -117.0685 | -116.9815 | 0.07782 | -0.059509 | -4.2206 | 117.0914 | 114.8117 | 114.8712 | -13.5406 | -0.068664 | 0.018311 | -0.2655 | 120.7901 | 118.8904 | 118.8721 | -0.32501 | 117.215 | 107.8949 | 94.693 | -121.4951 | 121.17 | 121.1105 | 117.009 | -121.4172
2141.6406 | 121.6415 | -117.0227 | 4.3533 | 0.55284 | 0.058369 | -0.0048681 | 0.38959 | 0.06301 | 0.63494 | -0.038148 | 1.2576 | 3.9398 | 0.040239 | 0.074439 | 3.1502 | 0.049029 | -9.0317 | 0.09613 | -22.5632 | -2.0874 | 0.21973 | -117.0227 | -117.1783 | 3.7628 | 0.72327 | 1.8723 | 4.0695 | 4.0054 | -117.128 | -117.0319 | 0 | -0.15564 | -4.1336 | 117.1188 | 114.9353 | 115.0909 | -13.385 | -0.10529 | -0.009155 | -0.28381 | 120.7855 | 118.895 | 118.9041 | -0.3479 | 117.2424 | 107.991 | 94.4595 | -121.5317 | 121.0922 | 121.0281 | 117.746 | -121.3852
2142.6406 | 121.6049 | -117.0593 | 4.3442 | 0.61387 | 0.043416 | 0.00047294 | 0.37464 | 0.074759 | 0.63601 | -0.041353 | 0.61677 | 3.9291 | 0.048783 | 0.089393 | 3.1427 | 0.050097 | -9.0729 | 0.054932 | -22.6822 | -2.2064 | 0.21973 | -117.0364 | -117.1829 | 3.7354 | 1.1765 | 1.8311 | 4.0558 | 3.9963 | -117.1509 | -117.0547 | 0.022888 | -0.1236 | -4.1245 | 117.1143 | 114.8529 | 114.9765 | -13.4171 | -0.091553 | 0.004577 | -0.28839 | 120.7947 | 118.8904 | 118.8858 | -0.3479 | 117.2791 | 107.9864 | 94.3771 | -121.5271 | 121.1151 | 121.0556 | 118.2358 | -121.3989
2143.6562 | 121.5408 | -117.0776 | 4.335 | -0.16433 | 0.023121 | 0.0058129 | 0.37464 | 0.060874 | 0.60076 | -0.045625 | 0.0522 | 3.9248 | 0.05092 | 0.090461 | 3.1277 | 0.061846 | -9.082 | 0.14191 | -22.6456 | -2.124 | 0.22888 | -116.9998 | -117.128 | 3.7582 | 0.56763 | 1.918 | 4.0649 | 4.0283 | -117.1143 | -117.0776 | 0.07782 | -0.050354 | -4.1061 | 117.2195 | 114.9536 | 115.004 | -13.4171 | -0.036621 | 0 | -0.27008 | 120.8359 | 118.9957 | 118.9957 | -0.3067 | 117.3065 | 107.9956 | 94.4321 | -121.463 | 121.1426 | 121.106 | 117.6453 | -121.4127
2144.6406 | 121.4905 | -116.7526 | 4.7241 | 0.53758 | 0.073323 | 0.0047449 | 0.36075 | 0.065146 | 0.64776 | -0.040284 | 2.0969 | 3.9473 | 0.057328 | 0.094733 | 3.1438 | 0.049029 | -9.1232 | -0.027466 | -22.7005 | -2.1744 | 0.2655 | -116.6473 | -116.7755 | 3.9917 | 0.89722 | 2.0828 | 4.4724 | 4.422 | -116.8076 | -116.7068 | 0.10529 | -0.022888 | -4.4586 | 116.7252 | 114.5782 | 114.6011 | -13.8474 | -0.054931 | 0.045777 | -0.25177 | 120.7443 | 118.8354 | 118.7897 | -0.30212 | 117.0181 | 107.6294 | 94.0521 | -121.4996 | 121.225 | 121.1746 | 117.6498 | -121.431
2145.6406 | 121.4905 | -116.922 | 4.5547 | 0.4918 | 0.045552 | -0.0038001 | 0.37357 | 0.074759 | 0.63387 | -0.031739 | 0.43367 | 3.9355 | 0.057328 | 0.1161 | 3.1459 | 0.052233 | -9.1507 | -0.045776 | -22.673 | -2.2568 | 0.25177 | -116.8762 | -117.0227 | 3.7216 | 0.67291 | 1.8082 | 4.2892 | 4.2343 | -116.9861 | -116.922 | 0.045776 | -0.10071 | -4.303 | 116.8762 | 114.6652 | 114.7659 | -13.7054 | -0.064087 | 0 | -0.2655 | 120.6436 | 118.7302 | 118.7302 | -0.32043 | 117.1738 | 107.7713 | 94.249 | -121.5775 | 121.2112 | 121.1563 | 117.5949 | -121.4767
2146.6406 | 121.5363 | -116.922 | 4.4998 | 0.034038 | 0.055165 | -0.013413 | 0.37143 | 0.048056 | 0.62533 | -0.033876 | 0.54048 | 3.9334 | 0.038102 | 0.10007 | 3.1459 | 0.066119 | -9.1736 | -0.013733 | -22.5311 | -2.1652 | 0.23346 | -116.89 | -117.041 | 3.8361 | 1.6663 | 1.8631 | 4.2526 | 4.1977 | -117.0135 | -116.9083 | 0.032043 | -0.11902 | -4.2664 | 116.9083 | 114.7568 | 114.8758 | -13.6734 | -0.091553 | 0.013733 | -0.24719 | 120.7581 | 118.7851 | 118.7714 | -0.30212 | 117.1555 | 107.7484 | 94.3909 | -121.5408 | 121.1746 | 121.1197 | 118.5883 | -121.4081
2147.6875 | 121.5317 | -116.9495 | 4.4724 | -0.17959 | 0.060505 | -0.0038001 | 0.38104 | 0.068351 | 0.63601 | -0.031739 | -0.13091 | 3.9398 | 0.041307 | 0.076575 | 3.1341 | 0.054369 | -9.137 | 0.009155 | -22.4167 | -2.1652 | 0.23804 | -116.9449 | -117.1188 | 3.772 | 0.36621 | 1.8311 | 4.2252 | 4.1565 | -117.0502 | -116.9632 | 0.004578 | -0.16937 | -4.2343 | 116.9586 | 114.7842 | 114.9536 | -13.6093 | -0.10071 | -0.013733 | -0.24719 | 120.7214 | 118.7805 | 118.7943 | -0.31586 | 117.1875 | 107.8125 | 94.5328 | -121.5912 | 121.1746 | 121.106 | 117.3157 | -121.4355
2148.6406 | 121.5866 | -116.9037 | 4.5227 | 0.55284 | 0.061574 | 0.012222 | 0.3693 | 0.068351 | 0.6296 | -0.03708 | 0.63203 | 3.9312 | 0.046647 | 0.097938 | 3.1309 | 0.061846 | -9.1049 | 0.009155 | -22.2107 | -2.0599 | 0.25635 | -116.8991 | -117.0273 | 3.8452 | 0.40741 | 1.8585 | 4.2297 | 4.1931 | -116.9952 | -116.8991 | 0.004578 | -0.1236 | -4.2664 | 116.9128 | 114.8438 | 114.9673 | -13.6276 | -0.091552 | 0.004578 | -0.29297 | 120.7489 | 118.7622 | 118.7576 | -0.32959 | 117.16 | 107.7988 | 94.693 | -121.55 | 121.1334 | 121.0968 | 117.3111 | -121.4218
2149.6406 | 121.6141 | -116.8213 | 4.6005 | 0.61387 | 0.056233 | -0.011276 | 0.33939 | 0.060874 | 0.59222 | -0.045625 | 0.93721 | 3.9216 | 0.032762 | 0.088325 | 3.1235 | 0.068255 | -9.0408 | 0.11902 | -21.817 | -2.1378 | 0.15106 | -116.7618 | -116.8945 | 3.9963 | 0.55847 | 1.886 | 4.335 | 4.2801 | -116.8854 | -116.7984 | 0.059509 | -0.073242 | -4.4495 | 116.9403 | 114.6835 | 114.7568 | -13.6414 | -0.064087 | 0.022888 | -0.2655 | 120.8176 | 118.7073 | 118.6844 | -0.32043 | 116.9724 | 107.7805 | 95.0043 | -121.4951 | 121.1563 | 121.1014 | 117.3798 | -121.3989
2150.6406 | 121.5363 | -116.803 | 4.6371 | 0.46128 | 0.06905 | -0.013413 | 0.36075 | 0.068351 | 0.62747 | -0.047761 | 0.64729 | 3.9216 | 0.040239 | 0.091529 | 3.1309 | 0.06505 | -9.0912 | -0.013733 | -21.9498 | -2.179 | 0.23346 | -116.7572 | -116.9174 | 3.9734 | -0.004578 | 1.8082 | 4.3488 | 4.3213 | -116.8671 | -116.7847 | 0.045777 | -0.11444 | -4.4037 | 116.7892 | 114.624 | 114.7385 | -13.7283 | -0.064086 | 0.018311 | -0.28839 | 120.7764 | 118.6111 | 118.5928 | -0.31586 | 117.0364 | 107.7118 | 94.8532 | -121.5546 | 121.1517 | 121.1243 | 116.7984 | -121.4218
2151.6406 | 121.5271 | -116.8304 | 4.628 | 0.41551 | 0.047688 | -0.0091401 | 0.37357 | 0.068351 | 0.63601 | -0.036012 | 0.52522 | 3.9312 | 0.043443 | 0.08512 | 3.1427 | 0.054369 | -9.1049 | -0.045776 | -22.4945 | -2.4902 | 0.2655 | -116.8076 | -116.9357 | 3.8773 | -0.14648 | 1.6617 | 4.3625 | 4.3167 | -116.9174 | -116.8213 | 0.022888 | -0.10529 | -4.3625 | 116.7847 | 114.3402 | 114.4455 | -13.7329 | -0.086975 | 0.009155 | -0.2655 | 120.7077 | 118.4921 | 118.483 | -0.31128 | 117.0959 | 107.7255 | 94.3359 | -121.5637 | 121.1929 | 121.1472 | 116.684 | -121.4493
2152.6406 | 121.5363 | -116.9952 | 4.4632 | 0.17137 | 0.04662 | -0.0016631 | 0.3725 | 0.053397 | 0.63708 | -0.038148 | 0.61677 | 3.9344 | 0.046647 | 0.10114 | 3.1384 | 0.063982 | -9.1003 | -0.050354 | -22.3892 | -2.1927 | 0.26093 | -116.9449 | -117.0776 | 3.772 | -0.054932 | 1.7578 | 4.1656 | 4.1336 | -117.0639 | -116.9724 | 0.050354 | -0.082398 | -4.2023 | 116.9449 | 114.8026 | 114.8849 | -13.5635 | -0.068665 | 0.022888 | -0.29755 | 120.7672 | 118.7531 | 118.7302 | -0.32959 | 117.2562 | 107.8949 | 94.606 | -121.5408 | 121.1609 | 121.1288 | 116.9403 | -121.4355
2153.6406 | 121.5363 | -117.041 | 4.3991 | 6.107 | 0.065846 | 0.022903 | 0.3725 | 0.064078 | 0.63708 | -0.052034 | 0.7541 | 3.9387 | 0.054124 | 0.095801 | 3.1427 | 0.075732 | -9.0408 | -0.050354 | -22.3343 | -2.2705 | 0.25177 | -116.9998 | -117.1326 | 3.7079 | -0.20142 | 1.8127 | 4.1611 | 4.1016 | -117.1326 | -117.0319 | 0.041199 | -0.091552 | -4.1473 | 116.9907 | 114.7705 | 114.8621 | -13.4399 | -0.091552 | 0.009156 | -0.23804 | 120.7489 | 118.8538 | 118.8446 | -0.29755 | 117.2928 | 108.0002 | 94.7067 | -121.5317 | 121.2021 | 121.1426 | 116.8396 | -121.431
2154.6406 | 121.5912 | -116.8808 | 4.5364 | 0.56809 | 0.059437 | -0.0027321 | 0.36823 | 0.070487 | 0.62747 | -0.036012 | 0.66255 | 3.927 | 0.05092 | 0.096869 | 3.1331 | 0.060778 | -9.1095 | 0.009155 | -22.2931 | -2.1835 | 0.21515 | -116.8396 | -116.9998 | 3.9047 | 0.17853 | 1.8402 | 4.2343 | 4.216 | -116.9586 | -116.8625 | 0.041198 | -0.11902 | -4.3213 | 116.89 | 114.6973 | 114.8163 | -13.6459 | -0.07782 | 0.01831 | -0.30212 | 120.7855 | 118.721 | 118.7027 | -0.32044 | 117.0959 | 107.7713 | 94.5877 | -121.5363 | 121.1151 | 121.0968 | 117.0593 | -121.3989
2155.6562 | 121.6232 | -116.8945 | 4.5319 | -0.072774 | 0.039143 | 0.031448 | 0.38425 | 0.068351 | 0.59222 | -0.052034 | 0.14375 | 3.9227 | 0.028489 | 0.08512 | 3.116 | 0.0768 | -9.0225 | 0.17395 | -22.1054 | -2.3712 | 0.21515 | -116.8213 | -116.9815 | 3.8956 | 0.53101 | 1.9135 | 4.2389 | 4.1885 | -116.9769 | -116.8854 | 0.073242 | -0.086975 | -4.3167 | 117.0685 | 114.5233 | 114.6103 | -13.5544 | -0.082398 | 0.009155 | -0.29297 | 120.7901 | 118.808 | 118.7988 | -0.34332 | 117.1097 | 107.872 | 94.7891 | -121.5134 | 121.1334 | 121.0831 | 117.4255 | -121.4172
2156.6406 | 121.637 | -116.8167 | 4.5593 | 0.47654 | 0.043416 | 0.010086 | 0.35007 | 0.066214 | 0.61785 | -0.042421 | 0.50996 | 3.9205 | 0.063737 | 0.092597 | 3.1309 | 0.055437 | -8.9859 | 0.013733 | -22.3297 | -2.1194 | 0.21057 | -116.7801 | -116.9174 | 3.9505 | 0.63629 | 1.8494 | 4.2892 | 4.2343 | -116.9128 | -116.8396 | 0.036621 | -0.10071 | -4.3488 | 116.8304 | 114.6973 | 114.798 | -13.5452 | -0.096131 | -0.022889 | -0.27008 | 120.7672 | 118.6661 | 118.689 | -0.32501 | 117.0273 | 107.8308 | 94.487 | -121.4767 | 121.106 | 121.051 | 117.453 | -121.3989
2157.7031 | 121.6278 | -116.803 | 4.5822 | 0.27818 | 0.055165 | -0.011276 | 0.37143 | 0.082236 | 0.63067 | -0.033876 | 0.69307 | 3.9141 | 0.059465 | 0.10007 | 3.1288 | 0.058642 | -8.9722 | 0.11444 | -22.2382 | -2.2385 | 0.21515 | -116.7664 | -116.9083 | 4.0192 | 0.5722 | 1.8585 | 4.303 | 4.2664 | -116.8762 | -116.8076 | 0.036622 | -0.10529 | -4.3671 | 116.9174 | 114.5645 | 114.6698 | -13.5544 | -0.073242 | -0.004577 | -0.27923 | 120.8221 | 118.6615 | 118.6661 | -0.31586 | 117.0181 | 107.8308 | 94.5648 | -121.4905 | 121.106 | 121.0693 | 117.3752 | -121.3898
2158.6562 | 121.5958 | -116.835 | 4.5593 | 0.58335 | 0.040211 | 0.0068819 | 0.36289 | 0.06301 | 0.61465 | -0.042421 | 1.1813 | 3.9131 | 0.041307 | 0.092597 | 3.1256 | 0.056505 | -9.2056 | -0.045776 | -22.0184 | -2.0691 | 0.16937 | -116.8121 | -116.9495 | 3.978 | 1.2222 | 1.8448 | 4.2664 | 4.2343 | -116.9312 | -116.8304 | 0.022888 | -0.11444 | -4.39 | 116.7892 | 114.7659 | 114.8804 | -13.765 | -0.09613 | 0.004578 | -0.29297 | 120.813 | 118.6798 | 118.6752 | -0.32501 | 117.0044 | 107.6294 | 94.8166 | -121.5088 | 121.1014 | 121.0693 | 118.0573 | -121.3898
2159.6406 | 121.4951 | -116.89 | 4.5914 | 0.44602 | 0.049824 | -0.0080721 | 0.36609 | 0.068351 | 0.63601 | -0.043489 | 0.41841 | 3.9184 | 0.054124 | 0.090461 | 3.1309 | 0.053301 | -9.0637 | -0.059509 | -22.2702 | -2.3758 | 0.25177 | -116.8121 | -116.9678 | 3.8589 | 0.054932 | 1.6663 | 4.335 | 4.2709 | -116.9815 | -116.8625 | 0.07782 | -0.077819 | -4.3396 | 116.8304 | 114.5142 | 114.592 | -13.6551 | -0.091552 | 0.027466 | -0.25635 | 120.7489 | 118.5562 | 118.5287 | -0.32044 | 117.1417 | 107.8262 | 94.6198 | -121.5591 | 121.225 | 121.1609 | 116.9449 | -121.4539
2160.6875 | 121.5866 | -116.8945 | 4.5593 | -0.11855 | 0.040211 | -0.0038001 | 0.36823 | 0.072623 | 0.59756 | -0.048829 | -0.0088351 | 3.9152 | 0.03917 | 0.092597 | 3.1074 | 0.056505 | -8.9996 | 0.12817 | -22.0642 | -2.0416 | 0.21973 | -116.8076 | -116.9678 | 3.9322 | 2.5314 | 1.8494 | 4.2755 | 4.2252 | -116.9769 | -116.8945 | 0.086975 | -0.073242 | -4.3396 | 117.0227 | 114.8529 | 114.9261 | -13.559 | -0.082398 | 0 | -0.28381 | 120.8267 | 118.7439 | 118.7439 | -0.33417 | 117.1143 | 107.8949 | 94.8303 | -121.5271 | 121.17 | 121.1197 | 119.426 | -121.4539
2161.6406 | 121.4584 | -116.8762 | 4.6234 | 0.36973 | 0.049824 | 0.0036769 | 0.3693 | 0.060874 | 0.63601 | -0.030671 | 0.46419 | 3.9152 | 0.049852 | 0.089393 | 3.132 | 0.054369 | -9.0637 | -0.059509 | -22.1375 | -2.1606 | 0.26093 | -116.8304 | -116.9815 | 3.8773 | 1.593 | 1.6571 | 4.3533 | 4.2984 | -116.9907 | -116.8625 | 0.045777 | -0.10528 | -4.3625 | 116.8167 | 114.7156 | 114.8209 | -13.6871 | -0.11444 | 0.013733 | -0.27008 | 120.7535 | 118.5333 | 118.5196 | -0.32501 | 117.1371 | 107.8125 | 94.7388 | -121.6049 | 121.2296 | 121.1746 | 118.4692 | -121.4859
2162.6406 | 121.6324 | -116.89 | 4.5181 | 1.0869 | 0.054097 | -0.00059506 | 0.37677 | 0.086509 | 0.63387 | -0.056306 | 0.70833 | 3.9131 | 0.03917 | 0.093665 | 3.1245 | 0.062914 | -9.0088 | 0.10529 | -21.9269 | -2.2842 | 0.1831 | -116.8533 | -116.9815 | 3.9093 | 0.4303 | 1.7715 | 4.2252 | 4.1885 | -116.9632 | -116.8716 | 0.036621 | -0.091552 | -4.335 | 116.9952 | 114.6057 | 114.6973 | -13.5269 | -0.073242 | 0.018311 | -0.29297 | 120.7993 | 118.6615 | 118.6432 | -0.32959 | 117.0731 | 107.8812 | 94.9631 | -121.4996 | 121.1151 | 121.0785 | 117.3203 | -121.3898
2163.6406 | 121.5454 | -117.0044 | 4.422 | 0.53758 | 0.057301 | -0.0048681 | 0.36182 | 0.061942 | 0.62319 | -0.055238 | 0.58626 | 3.9291 | 0.060533 | 0.091529 | 3.1341 | 0.069323 | -9.0683 | -0.013733 | -22.2153 | -2.1744 | 0.23346 | -116.9769 | -117.1097 | 3.7491 | 0.70496 | 1.7075 | 4.1565 | 4.1245 | -117.0868 | -116.9815 | 0.027466 | -0.10528 | -4.1885 | 116.9907 | 114.83 | 114.9353 | -13.4903 | -0.082397 | 0.022889 | -0.2655 | 120.7535 | 118.7119 | 118.689 | -0.29755 | 117.2379 | 107.9361 | 94.7891 | -121.5317 | 121.1609 | 121.1288 | 117.7094 | -121.4035
2164.6406 | 121.5683 | -117.1051 | 4.3671 | 0.47654 | 0.053029 | -0.010208 | 0.35861 | 0.0801 | 0.63387 | -0.041353 | 0.571 | 3.9302 | 0.061601 | 0.075507 | 3.1309 | 0.060778 | -9.0729 | -0.045776 | -22.2565 | -2.243 | 0.2655 | -117.0593 | -117.1967 | 3.7949 | -1.062 | 1.7532 | 4.1016 | 4.0787 | -117.1783 | -117.0685 | 0.045777 | -0.091552 | -4.1016 | 117.0593 | 114.8621 | 114.9536 | -13.4399 | -0.073242 | 0.036622 | -0.2655 | 120.9 | 118.8583 | 118.8217 | -0.28839 | 117.3706 | 108.0322 | 94.8486 | -121.5637 | 121.2067 | 121.1838 | 116.0431 | -121.4355
2165.6406 | 121.6141 | -116.8533 | 4.541 | 0.52232 | 0.041279 | -0.0016631 | 0.37677 | 0.072623 | 0.61999 | -0.047761 | 0.47945 | 3.9195 | 0.048783 | 0.090461 | 3.1256 | 0.066119 | -9.0179 | 0.064087 | -22.0551 | -2.0279 | 0.2243 | -116.8213 | -116.9998 | 3.9139 | 0.045776 | 1.7349 | 4.2618 | 4.2206 | -116.9495 | -116.89 | 0.032044 | -0.14648 | -4.3167 | 116.9174 | 114.8254 | 114.9719 | -13.559 | -0.09613 | -0.036621 | -0.27924 | 120.7672 | 118.5883 | 118.6249 | -0.32043 | 117.0776 | 107.8354 | 94.7983 | -121.5408 | 121.1151 | 121.0739 | 116.8991 | -121.431
2166.6406 | 121.4767 | -117.0547 | 4.4449 | 0.55284 | 0.054097 | -0.0027321 | 0.36609 | 0.061942 | 0.63922 | -0.034944 | 0.46419 | 3.9344 | 0.065873 | 0.10114 | 3.1277 | 0.063982 | -9.0729 | -0.054932 | -22.2794 | -2.1194 | 0.26093 | -116.9861 | -117.1692 | 3.6713 | 0.022888 | 1.6342 | 4.1702 | 4.1016 | -117.1371 | -117.0502 | 0.068665 | -0.11444 | -4.184 | 116.9998 | 114.9353 | 115.0497 | -13.5178 | -0.082397 | 0.004578 | -0.27466 | 120.726 | 118.689 | 118.6844 | -0.34332 | 117.3157 | 107.9819 | 94.7754 | -121.6141 | 121.225 | 121.1563 | 117.0776 | -121.4951
2167.6406 | 121.6278 | -116.9128 | 4.4907 | 0.52232 | 0.048756 | -0.010208 | 0.38211 | 0.065146 | 0.62106 | -0.038148 | 0.73885 | 3.9205 | 0.051988 | 0.092597 | 3.1277 | 0.061846 | -9.0134 | 0.018311 | -22.348 | -2.1057 | 0.2243 | -116.8625 | -117.0319 | 3.8635 | 0.21515 | 1.7303 | 4.2068 | 4.1931 | -117.0273 | -116.89 | 0.050354 | -0.11902 | -4.2664 | 116.9312 | 114.8071 | 114.9261 | -13.504 | -0.11444 | 0.022888 | -0.28381 | 120.7764 | 118.6432 | 118.6203 | -0.29755 | 117.1371 | 107.8995 | 94.5648 | -121.5225 | 121.1197 | 121.106 | 117.128 | -121.3806
2168.6406 | 121.5317 | -117.1326 | 4.3396 | 0.46128 | 0.048756 | 0.010086 | 0.38104 | 0.049125 | 0.62747 | -0.040284 | -1.1075 | 3.9216 | 0.042375 | 0.10114 | 3.1235 | 0.055437 | -9.05 | -0.15106 | -22.3663 | -2.1378 | 0.27008 | -117.0456 | -117.2012 | 3.6118 | 0.018311 | 1.6617 | 4.0878 | 4.0329 | -117.2058 | -117.1188 | 0.086975 | -0.068665 | -4.0695 | 116.9815 | 114.9948 | 115.0635 | -13.3896 | -0.073243 | 0.013733 | -0.25177 | 120.7443 | 118.7943 | 118.7805 | -0.3067 | 117.4026 | 108.0826 | 94.7662 | -121.5408 | 121.2204 | 121.1655 | 117.1509 | -121.4584
2169.6406 | 121.5591 | -116.9998 | 4.454 | 0.52232 | 0.057301 | 0.0047449 | 0.36609 | 0.065146 | 0.62106 | -0.03708 | 0.72359 | 3.9227 | 0.057328 | 0.097938 | 3.1224 | 0.063982 | -9.0134 | -0.009155 | -22.4213 | -2.1515 | 0.25635 | -116.9449 | -117.0685 | 3.7811 | 0.54016 | 1.68 | 4.1748 | 4.1336 | -117.0868 | -116.9769 | 0.054932 | -0.068664 | -4.1977 | 116.9907 | 114.8483 | 114.917 | -13.4674 | -0.086975 | 0.022888 | -0.27924 | 120.7809 | 118.6798 | 118.6569 | -0.32043 | 117.2562 | 107.9864 | 94.5786 | -121.5225 | 121.1746 | 121.1334 | 117.54 | -121.431
2170.6406 | 121.5546 | -117.0044 | 4.4449 | 0.24766 | 0.062642 | 0.0026089 | 0.35861 | 0.067282 | 0.61999 | -0.032808 | 0.64729 | 3.9152 | 0.046647 | 0.093665 | 3.1341 | 0.062914 | -9.0134 | -0.009155 | -22.4716 | -2.1423 | 0.24719 | -116.954 | -117.0914 | 3.772 | 1.5335 | 1.6891 | 4.184 | 4.1245 | -117.0868 | -116.9678 | 0.050354 | -0.086975 | -4.1977 | 116.9952 | 114.8621 | 114.949 | -13.4583 | -0.082397 | 0.036622 | -0.26093 | 120.7764 | 118.6935 | 118.6569 | -0.32043 | 117.2516 | 107.991 | 94.5328 | -121.5363 | 121.1884 | 121.1288 | 118.5379 | -121.4127
2171.6406 | 121.6049 | -116.8854 | 4.4952 | 0.56809 | 0.066914 | -0.00059506 | 0.35968 | 0.082236 | 0.61572 | -0.057374 | 0.73885 | 3.9109 | 0.043443 | 0.086188 | 3.1128 | 0.071459 | -8.9447 | 0.09613 | -22.3618 | -2.124 | 0.19226 | -116.8121 | -116.954 | 3.804 | 0.63171 | 1.8814 | 4.2114 | 4.1611 | -116.9815 | -116.89 | 0.073242 | -0.068665 | -4.303 | 116.9815 | 114.7614 | 114.83 | -13.4399 | -0.09613 | -0.004578 | -0.28381 | 120.6894 | 118.7668 | 118.7714 | -0.33417 | 117.0776 | 107.9407 | 94.5236 | -121.4493 | 121.0968 | 121.0464 | 117.5171 | -121.3852
2172.6406 | 121.4905 | -116.9998 | 4.4769 | 0.41551 | 0.059437 | -0.010208 | 0.37998 | 0.075827 | 0.63494 | -0.044557 | 0.44893 | 3.9216 | 0.055192 | 0.097938 | 3.1299 | 0.058642 | -9.05 | -0.07782 | -22.435 | -2.3666 | 0.25635 | -116.954 | -117.0731 | 3.7262 | -0.24261 | 1.6479 | 4.2068 | 4.1702 | -117.1005 | -116.9952 | 0.045776 | -0.073242 | -4.2206 | 116.922 | 114.6332 | 114.7064 | -13.5269 | -0.10071 | 0.004578 | -0.27008 | 120.726 | 118.6478 | 118.6432 | -0.3067 | 117.2562 | 107.9498 | 94.5648 | -121.55 | 121.2067 | 121.17 | 116.7572 | -121.4722
2173.6875 | 121.5591 | -111.8134 | 9.7 | -0.13381 | 0.043416 | 0.0015409 | 0.37036 | 0.064078 | 0.58901 | -0.041353 | -0.25298 | 3.8928 | 0.042375 | 0.092597 | 3.0893 | 0.091753 | -8.8715 | -0.009155 | -21.2357 | -2.1561 | 0.23346 | -111.8179 | -111.9186 | 8.9767 | -0.050354 | 5.5984 | 9.3933 | 9.3658 | -111.8866 | -111.7905 | -0.004578 | -0.10529 | -9.4666 | 111.8042 | 109.6573 | 109.7626 | -18.5715 | -0.073243 | 0.022888 | -0.3067 | 120.7901 | 117.4118 | 117.3889 | -0.33417 | 112.0468 | 102.9419 | 90.5777 | -121.6187 | 121.2067 | 121.1792 | 111.763 | -121.4905
2174.6406 | 121.5775 | -113.9832 | 7.5073 | 0.4918 | 0.042347 | -0.0038001 | 0.3693 | 0.066214 | 0.60824 | -0.031739 | 0.58626 | 3.9216 | 0.057328 | 0.088325 | 3.1 | 0.10243 | -8.9447 | -0.027466 | -21.6339 | -2.1423 | 0.23804 | -113.9053 | -114.0335 | 6.8802 | -0.018311 | 3.8086 | 7.2693 | 7.2098 | -113.9923 | -113.8962 | 0.07782 | -0.050354 | -7.2693 | 113.9557 | 111.8408 | 111.8912 | -16.452 | -0.009156 | 0.086975 | -0.23804 | 120.8633 | 117.7917 | 117.7048 | -0.29755 | 114.2212 | 105.0385 | 92.3492 | -121.5408 | 121.2524 | 121.1929 | 113.9648 | -121.4035
2175.6406 | 121.4355 | -114.5416 | 6.9992 | 0.4918 | 0.050892 | -0.0070041 | 0.36823 | 0.067282 | 0.60824 | -0.040284 | 0.47945 | 3.9291 | 0.05092 | 0.094733 | 3.1096 | 0.098162 | -9.0317 | -0.059509 | -21.8399 | -2.2156 | 0.26093 | -114.4638 | -114.6194 | 6.2347 | 0.14191 | 3.3234 | 6.7062 | 6.6742 | -114.5462 | -114.4455 | 0.07782 | -0.07782 | -6.7383 | 114.4821 | 112.326 | 112.4039 | -16.0309 | -0.004578 | 0.09613 | -0.29297 | 120.7764 | 117.865 | 117.7689 | -0.32501 | 114.8026 | 105.5099 | 92.7017 | -121.6187 | 121.2479 | 121.2158 | 114.6835 | -121.4447
2176.6406 | 121.5317 | -114.7156 | 6.7566 | 1.8041 | 0.058369 | 0.0026089 | 0.36289 | 0.067282 | 0.61251 | -0.03708 | 0.61677 | 3.9227 | 0.066941 | 0.099006 | 3.0978 | 0.1035 | -9.0729 | -0.032043 | -21.8033 | -2.179 | 0.25635 | -114.6652 | -114.8392 | 6.0654 | -0.045776 | 3.2364 | 6.5002 | 6.4362 | -114.7797 | -114.6927 | 0.050354 | -0.1236 | -6.5002 | 114.6835 | 112.5366 | 112.6602 | -15.8295 | -0.064087 | 0.022888 | -0.25635 | 120.7809 | 117.952 | 117.9291 | -0.32044 | 114.9719 | 105.6427 | 92.9123 | -121.5958 | 121.2158 | 121.1517 | 114.6698 | -121.4493
2177.6406 | 121.5363 | -114.9353 | 6.5506 | 0.52232 | 0.059437 | -0.021958 | 0.36289 | 0.069419 | 0.61251 | -0.031739 | 0.34212 | 3.9323 | 0.061601 | 0.088325 | 3.1032 | 0.094958 | -9.1782 | 0.09613 | -21.8399 | -2.2568 | 0.27466 | -114.8895 | -114.9902 | 5.8548 | 2.829 | 3.035 | 6.2668 | 6.2622 | -115.004 | -114.8987 | 0.045777 | -0.054931 | -6.2759 | 115.0314 | 112.6785 | 112.7335 | -15.7288 | -0.068664 | 0.036621 | -0.28381 | 120.7901 | 117.9703 | 117.9337 | -0.28839 | 115.21 | 105.7571 | 93.0954 | -121.5408 | 121.2021 | 121.1975 | 117.7643 | -121.4493
2178.7031 | 121.4951 | -115.0406 | 6.4407 | -0.24062 | 0.06371 | 0.0079499 | 0.3725 | 0.058738 | 0.6029 | -0.042421 | -2.1908 | 3.9248 | 0.048783 | 0.08512 | 3.0946 | 0.096026 | -9.082 | -0.018311 | -21.8491 | -2.4445 | 0.25177 | -114.9811 | -115.1138 | 5.7404 | 0.51727 | 2.9846 | 6.2439 | 6.1661 | -115.1047 | -115.0085 | 0.059509 | -0.073243 | -6.189 | 115.0223 | 112.5961 | 112.6694 | -15.5228 | -0.064087 | 0.032043 | -0.19684 | 120.7809 | 118.0252 | 117.9932 | -0.27466 | 115.2924 | 105.9586 | 93.1915 | -121.5546 | 121.2845 | 121.2067 | 115.5579 | -121.4493
2179.6406 | 121.5179 | -115.1505 | 6.3904 | 0.27818 | 0.062642 | 0.0015409 | 0.37784 | 0.066214 | 0.62213 | -0.039216 | 0.28108 | 3.9334 | 0.05092 | 0.10435 | 3.1096 | 0.084276 | -9.0912 | -0.050354 | -21.6934 | -2.6138 | 0.23346 | -115.0635 | -115.2145 | 5.5847 | -0.064087 | 2.861 | 6.0883 | 6.0608 | -115.2054 | -115.1093 | 0.086975 | -0.064087 | -6.1569 | 115.1001 | 112.5366 | 112.6007 | -15.4816 | -0.054931 | 0.041199 | -0.30212 | 120.7352 | 118.0115 | 117.9703 | -0.32959 | 115.3839 | 106.0593 | 93.457 | -121.6049 | 121.2387 | 121.2112 | 115.0864 | -121.4996
2180.6406 | 121.5363 | -115.1825 | 6.2805 | -0.33217 | 0.033803 | -0.0059361 | 0.36823 | 0.066214 | 0.61358 | -0.053102 | 0.67781 | 3.9227 | 0.040239 | 0.092597 | 3.1106 | 0.098162 | -9.0912 | -0.018311 | -21.5057 | -2.504 | 0.2655 | -115.1413 | -115.2786 | 5.5893 | -0.041199 | 2.8931 | 6.0059 | 5.9738 | -115.2603 | -115.1321 | 0.041199 | -0.09613 | -6.015 | 115.1642 | 112.6785 | 112.7747 | -15.3717 | -0.07782 | 0.050354 | -0.27466 | 120.7718 | 118.0756 | 118.0252 | -0.3067 | 115.448 | 106.0913 | 93.6768 | -121.5591 | 121.1884 | 121.1563 | 115.1413 | -121.4127
2181.6406 | 121.5408 | -115.1779 | 6.2851 | 0.38499 | 0.057301 | 0.0047449 | 0.36289 | 0.068351 | 0.60824 | -0.03708 | 0.46419 | 3.9398 | 0.05092 | 0.093665 | 3.1106 | 0.08214 | -9.0958 | -0.086975 | -21.3181 | -2.6413 | 0.25177 | -115.1505 | -115.2878 | 5.5481 | -0.07782 | 2.8381 | 6.0242 | 5.9784 | -115.2832 | -115.1916 | 0.027465 | -0.10986 | -6.0333 | 115.0909 | 112.5366 | 112.6465 | -15.3809 | -0.10529 | -0.013733 | -0.26093 | 120.726 | 118.0161 | 118.0298 | -0.3067 | 115.4297 | 106.0822 | 93.8599 | -121.5729 | 121.2021 | 121.1563 | 115.1001 | -121.4767
2182.6406 | 121.5363 | -115.274 | 6.189 | 0.53758 | 0.053029 | -0.010208 | 0.37036 | 0.056601 | 0.63708 | -0.046693 | -0.039353 | 3.9376 | 0.053056 | 0.084052 | 3.1106 | 0.092821 | -9.137 | 0.013733 | -21.4783 | -2.3941 | 0.27924 | -115.2557 | -115.3839 | 5.4749 | -0.064087 | 2.8381 | 5.928 | 5.896 | -115.3702 | -115.2374 | 0.018311 | -0.10986 | -5.9097 | 115.2878 | 112.8799 | 112.9898 | -15.3259 | -0.09613 | 0.036621 | -0.26092 | 120.7489 | 118.1122 | 118.0756 | -0.29297 | 115.5533 | 106.1371 | 93.7958 | -121.5729 | 121.2021 | 121.17 | 115.21 | -121.4264
2183.6406 | 121.5729 | -115.2786 | 6.1752 | 0.44602 | 0.064778 | 0.01329 | 0.37998 | 0.068351 | 0.60824 | -0.03708 | 0.81514 | 3.9408 | 0.066941 | 0.096869 | 3.1117 | 0.090685 | -9.1415 | -0.027466 | -21.2082 | -2.2842 | 0.24261 | -115.2328 | -115.3793 | 5.4886 | -0.009155 | 2.8656 | 5.9006 | 5.8594 | -115.361 | -115.2512 | 0.045776 | -0.10071 | -5.9326 | 115.2512 | 112.9944 | 113.0951 | -15.3168 | -0.082398 | 0.027465 | -0.27466 | 120.7672 | 118.1442 | 118.1168 | -0.31586 | 115.5212 | 106.1371 | 94.0704 | -121.5546 | 121.1792 | 121.138 | 115.2695 | -121.4264
2184.6406 | 121.5637 | -115.2557 | 6.2119 | 0.53758 | 0.074391 | -0.0016631 | 0.3757 | 0.067282 | 0.61038 | -0.03708 | 0.61677 | 3.9227 | 0.046647 | 0.084052 | 3.1171 | 0.10671 | -9.1553 | -0.009155 | -21.2311 | -2.2659 | 0.23346 | -115.21 | -115.361 | 5.5206 | -0.009155 | 2.8336 | 5.9418 | 5.896 | -115.3381 | -115.2374 | 0.045776 | -0.10529 | -5.9784 | 115.2466 | 112.9898 | 113.0951 | -15.3671 | -0.082398 | 0.01831 | -0.27008 | 120.7764 | 118.0893 | 118.071 | -0.31586 | 115.4892 | 106.1005 | 94.0247 | -121.5729 | 121.1975 | 121.1517 | 115.2466 | -121.4493
2185.6406 | 121.4905 | -115.2512 | 6.2439 | -0.24062 | 0.020985 | 0.012222 | 0.36823 | 0.074759 | 0.59008 | -0.052034 | -0.19194 | 3.9205 | 0.037034 | 0.10862 | 3.0914 | 0.098162 | -9.1507 | 0.022888 | -21.199 | -2.2614 | 0.27008 | -115.1916 | -115.3244 | 5.4794 | 0.19684 | 2.7832 | 5.983 | 5.9235 | -115.3564 | -115.2374 | 0.05951 | -0.073242 | -5.9738 | 115.274 | 112.9898 | 113.063 | -15.3946 | -0.10528 | 0.013733 | -0.26093 | 120.7306 | 118.0344 | 118.0206 | -0.32043 | 115.5212 | 106.1005 | 94.0521 | -121.5683 | 121.2341 | 121.1746 | 115.448 | -121.4813
2186.6406 | 121.5271 | -115.3336 | 6.134 | 0.53758 | 0.079732 | 0.0047449 | 0.36609 | 0.058738 | 0.60824 | -0.057374 | 0.99824 | 3.9387 | 0.05092 | 0.093665 | 3.1053 | 0.091753 | -8.8806 | -0.15106 | -21.2952 | -2.3712 | 0.2655 | -115.274 | -115.4068 | 5.4382 | 0.17395 | 2.7466 | 5.8823 | 5.8411 | -115.4205 | -115.3107 | 0.059509 | -0.073242 | -5.8685 | 115.1825 | 112.9623 | 113.0356 | -15.0146 | -0.086975 | 0.022888 | -0.25177 | 120.7718 | 118.0801 | 118.0573 | -0.29297 | 115.5991 | 106.4529 | 94.0384 | -121.5408 | 121.2158 | 121.1746 | 115.5075 | -121.4447
2187.6719 | 121.6187 | -115.3702 | 6.0516 | 0.33921 | 0.055165 | 0.0047449 | 0.39066 | 0.059806 | 0.58474 | -0.052034 | 0.571 | 3.9238 | 0.057328 | 0.093665 | 3.0968 | 0.09389 | -9.1049 | 0.050354 | -21.3364 | -2.2705 | 0.21515 | -115.3244 | -115.4343 | 5.3925 | 0.28839 | 2.8198 | 5.8044 | 5.7632 | -115.4617 | -115.3656 | 0.045776 | -0.064087 | -5.8365 | 115.4205 | 113.0997 | 113.1638 | -15.1566 | -0.091553 | 0.004577 | -0.24719 | 120.7626 | 118.19 | 118.1854 | -0.28839 | 115.5853 | 106.2653 | 94.0338 | -121.4859 | 121.1746 | 121.1334 | 115.6586 | -121.4172
2188.6406 | 121.4996 | -115.5167 | 6.0013 | 0.26292 | 0.062642 | -0.016617 | 0.37784 | 0.066214 | 0.63067 | -0.045625 | 0.3116 | 3.9366 | 0.038102 | 0.08512 | 3.1138 | 0.083208 | -9.1095 | -0.027466 | -21.5561 | -2.3438 | 0.24719 | -115.4434 | -115.5945 | 5.2277 | 0.22888 | 2.6596 | 5.7129 | 5.6534 | -115.5899 | -115.4984 | 0.073243 | -0.077819 | -5.7541 | 115.4892 | 113.1729 | 113.2507 | -15.1108 | -0.073242 | 0.018311 | -0.28839 | 120.7443 | 118.1763 | 118.158 | -0.3479 | 115.7639 | 106.4072 | 93.9606 | -121.5958 | 121.2296 | 121.17 | 115.7455 | -121.4996
2189.6406 | 121.5317 | -115.5487 | 5.9326 | 0.52232 | 0.075459 | 0.0068819 | 0.3757 | 0.050193 | 0.60931 | -0.063783 | 1.1051 | 3.9408 | 0.065873 | 0.082984 | 3.1171 | 0.096026 | -8.9264 | -0.1236 | -21.5607 | -2.298 | 0.27466 | -115.4755 | -115.6448 | 5.2414 | 0.32501 | 2.6733 | 5.69 | 5.6213 | -115.6219 | -115.5029 | 0.073242 | -0.09613 | -5.658 | 115.4251 | 113.2507 | 113.3469 | -14.859 | -0.073242 | 0.045776 | -0.24261 | 120.7901 | 118.222 | 118.1763 | -0.31128 | 115.8234 | 106.6223 | 93.988 | -121.5775 | 121.2387 | 121.17 | 115.8737 | -121.4355
2190.6562 | 121.5134 | -115.5899 | 5.9052 | -0.25588 | 0.019917 | 0.00047294 | 0.35648 | 0.066214 | 0.59435 | -0.061647 | 0.067459 | 3.9238 | 0.05092 | 0.07978 | 3.0914 | 0.097094 | -9.1141 | 0.068665 | -21.4279 | -2.4582 | 0.2655 | -115.5029 | -115.6769 | 5.1636 | 0.045776 | 2.7237 | 5.6259 | 5.5847 | -115.6906 | -115.5716 | 0.086975 | -0.086975 | -5.6396 | 115.6586 | 113.1317 | 113.2187 | -15.0192 | -0.10071 | 0.018311 | -0.27923 | 120.7535 | 118.3136 | 118.2953 | -0.32043 | 115.8554 | 106.4758 | 94.162 | -121.582 | 121.2158 | 121.1746 | 115.6357 | -121.4767
2191.6406 | 121.4951 | -115.5991 | 5.9189 | 0.26292 | 0.053029 | -0.0016631 | 0.39066 | 0.066214 | 0.62747 | -0.046693 | 0.15901 | 3.9312 | 0.045579 | 0.096869 | 3.1085 | 0.084276 | -9.0912 | -0.004578 | -21.3821 | -2.5772 | 0.2243 | -115.5441 | -115.6723 | 5.159 | 0.49896 | 2.6093 | 5.5984 | 5.5664 | -115.6815 | -115.5991 | 0.054932 | -0.073242 | -5.6946 | 115.5945 | 113.0219 | 113.0951 | -15.0101 | -0.082398 | 0 | -0.32043 | 120.7581 | 118.2083 | 118.2083 | -0.35248 | 115.8234 | 106.5079 | 94.2169 | -121.5912 | 121.1975 | 121.1655 | 116.098 | -121.5179
2192.6406 | 121.5637 | -115.5075 | 5.9921 | 0.034038 | 0.056233 | -0.0059361 | 0.37143 | 0.074759 | 0.61572 | -0.033876 | 0.11323 | 3.9312 | 0.044511 | 0.11396 | 3.1181 | 0.088549 | -8.9813 | 0.054932 | -21.3272 | -2.2659 | 0.2655 | -115.4434 | -115.6036 | 5.3101 | 0.21057 | 2.6642 | 5.7587 | 5.7175 | -115.5624 | -115.4938 | 0.064087 | -0.096131 | -5.7266 | 115.5624 | 113.2416 | 113.3377 | -14.9734 | -0.054932 | 0.013733 | -0.23346 | 120.8176 | 118.1717 | 118.158 | -0.27466 | 115.773 | 106.5262 | 94.1803 | -121.5958 | 121.2662 | 121.225 | 115.7181 | -121.4859
2193.6406 | 121.5775 | -115.4205 | 6.0516 | 0.064555 | 0.064778 | -0.0091401 | 0.3725 | 0.070487 | 0.60824 | -0.052034 | 0.14375 | 3.9302 | 0.055192 | 0.087256 | 3.101 | 0.091753 | -8.9951 | 0.064087 | -21.3821 | -2.3895 | 0.23346 | -115.3564 | -115.5075 | 5.3833 | 0.71411 | 2.6459 | 5.8044 | 5.7449 | -115.4892 | -115.4114 | 0.064087 | -0.086975 | -5.8182 | 115.4846 | 113.031 | 113.118 | -15.0467 | -0.068665 | 0.009155 | -0.24719 | 120.8038 | 118.0664 | 118.0573 | -0.3067 | 115.654 | 106.4255 | 94.0384 | -121.5591 | 121.225 | 121.1655 | 116.1346 | -121.463
2194.6406 | 121.5408 | -115.3793 | 6.0745 | 0.095073 | 0.048756 | -0.010208 | 0.35861 | 0.068351 | 0.62213 | -0.033876 | 0.17427 | 3.9355 | 0.046647 | 0.080848 | 3.1053 | 0.091753 | -9.0271 | 0.050354 | -21.405 | -2.3392 | 0.23804 | -115.2924 | -115.361 | 5.397 | 0.88348 | 2.6596 | 5.8273 | 5.7816 | -115.4617 | -115.3839 | 0.086975 | 0.01831 | -5.8365 | 115.4297 | 113.0402 | 113.0219 | -15.1016 | -0.082398 | -0.004578 | -0.24719 | 120.7764 | 118.0389 | 118.0435 | -0.29297 | 115.6174 | 106.3522 | 93.9743 | -121.4355 | 121.2067 | 121.1609 | 116.2628 | -121.4584
2195.6406 | 121.5591 | -115.4388 | 6.0242 | 0.4918 | 0.04662 | -0.012345 | 0.36502 | 0.070487 | 0.60717 | -0.03708 | 0.64729 | 3.9248 | 0.045579 | 0.087256 | 3.0978 | 0.09389 | -9.0683 | -0.009155 | -21.4874 | -2.2797 | 0.25177 | -115.3839 | -115.5212 | 5.3329 | 0.10986 | 2.6505 | 5.7358 | 5.6946 | -115.5396 | -115.4205 | 0.054932 | -0.082397 | -5.7724 | 115.4297 | 113.1592 | 113.2416 | -15.0925 | -0.10071 | 0.018311 | -0.28839 | 120.7718 | 118.0893 | 118.071 | -0.32959 | 115.6906 | 106.3705 | 93.9514 | -121.5454 | 121.1746 | 121.1334 | 115.5487 | -121.4447
2196.6406 | 121.5729 | -115.3976 | 6.0791 | -0.10329 | 0.059437 | 0.0068819 | 0.37036 | 0.071555 | 0.61785 | -0.03708 | 0.082718 | 3.927 | 0.048783 | 0.086188 | 3.1032 | 0.091753 | -8.9859 | 0.036621 | -21.405 | -2.2202 | 0.23346 | -115.3427 | -115.4755 | 5.3925 | 0.46692 | 2.6367 | 5.809 | 5.7907 | -115.4617 | -115.3702 | 0.054932 | -0.07782 | -5.8456 | 115.4343 | 113.1775 | 113.2553 | -15.065 | -0.064087 | 0.027466 | -0.27008 | 120.7901 | 118.0344 | 118.0069 | -0.28839 | 115.6311 | 106.4117 | 93.9926 | -121.5546 | 121.2067 | 121.1884 | 115.8646 | -121.4493
2197.6406 | 121.5729 | -115.361 | 6.1295 | -0.088033 | 0.050892 | -0.0080721 | 0.38104 | 0.065146 | 0.61358 | -0.042421 | 0.0064239 | 3.9152 | 0.05092 | 0.10435 | 3.1 | 0.092821 | -9.0271 | 0.022888 | -21.5561 | -2.417 | 0.23804 | -115.3152 | -115.4846 | 5.4108 | 0.10071 | 2.6367 | 5.8502 | 5.7953 | -115.4755 | -115.3336 | 0.045776 | -0.1236 | -5.8914 | 115.3839 | 112.944 | 113.0676 | -15.1566 | -0.11444 | 0.027466 | -0.27924 | 120.7718 | 117.9977 | 117.9703 | -0.33417 | 115.5991 | 106.3339 | 93.8049 | -121.6141 | 121.2112 | 121.1563 | 115.4617 | -121.463
2198.6406 | 121.582 | -115.6448 | 5.8594 | -0.026997 | 0.062642 | 0.0047449 | 0.36395 | 0.064078 | 0.61358 | -0.027467 | -0.16142 | 3.928 | 0.045579 | 0.080848 | 3.1085 | 0.092821 | -9.05 | 0.018311 | -21.7346 | -2.4811 | 0.24719 | -115.5624 | -115.7227 | 5.1407 | 0.34332 | 2.6184 | 5.6122 | 5.5527 | -115.7089 | -115.6311 | 0.082397 | -0.07782 | -5.6122 | 115.6631 | 113.1638 | 113.2416 | -14.9094 | -0.064087 | 0.013732 | -0.24719 | 120.7855 | 118.2632 | 118.2495 | -0.3067 | 115.892 | 106.5948 | 93.9102 | -121.582 | 121.257 | 121.1975 | 115.9882 | -121.4905
2199.6719 | 121.6003 | -115.6631 | 5.7999 | 0.47654 | 0.039143 | 0.00047294 | 0.35861 | 0.072623 | 0.57192 | -0.048829 | 0.64729 | 3.927 | 0.049852 | 0.092597 | 3.1053 | 0.10243 | -9.0408 | 0.073242 | -21.7392 | -2.3575 | 0.21973 | -115.6036 | -115.7318 | 5.0995 | 0.068665 | 2.6779 | 5.5115 | 5.4611 | -115.7181 | -115.6174 | 0.059509 | -0.068665 | -5.5801 | 115.7364 | 113.3057 | 113.3743 | -14.8407 | -0.054932 | 0.045776 | -0.28839 | 120.7626 | 118.3411 | 118.2953 | -0.33874 | 115.8829 | 106.6223 | 93.9239 | -121.5317 | 121.1746 | 121.1243 | 115.7318 | -121.4172
2200.6406 | 121.5271 | -115.5991 | 5.9052 | 0.53758 | 0.06905 | 0.018631 | 0.36823 | 0.071555 | 0.61999 | -0.050966 | 0.50996 | 3.9462 | 0.054124 | 0.082984 | 3.0968 | 0.094958 | -9.0271 | -0.045776 | -21.9177 | -2.5818 | 0.26093 | -115.567 | -115.6906 | 5.1498 | 2.0691 | 2.4857 | 5.6076 | 5.5573 | -115.6723 | -115.5762 | 0.032043 | -0.091553 | -5.6442 | 115.5533 | 113.0173 | 113.1088 | -14.9323 | -0.073242 | 0.022888 | -0.29755 | 120.7489 | 118.0847 | 118.0618 | -0.3479 | 115.86 | 106.572 | 93.6813 | -121.5958 | 121.2067 | 121.1563 | 117.6682 | -121.4813
2201.6406 | 121.5088 | -115.5716 | 5.9372 | -0.27114 | 0.055165 | 0.0047449 | 0.37677 | 0.064078 | 0.61144 | -0.048829 | -0.06987 | 3.9355 | 0.026353 | 0.071235 | 3.0882 | 0.096026 | -9.0637 | -0.009155 | -21.9589 | -2.6917 | 0.26093 | -115.5396 | -115.6631 | 5.1727 | -0.11444 | 2.5955 | 5.7129 | 5.6534 | -115.6357 | -115.5579 | 0.032043 | -0.091553 | -5.6763 | 115.5624 | 112.8799 | 112.9715 | -15.0009 | -0.064087 | 0.013733 | -0.2243 | 120.7443 | 118.1671 | 118.1534 | -0.28381 | 115.8325 | 106.5079 | 93.6127 | -121.6003 | 121.2845 | 121.225 | 115.4572 | -121.4951
2202.6406 | 121.5408 | -115.5807 | 5.9143 | 1.1327 | 0.041279 | 0.0090179 | 0.36075 | 0.069419 | 0.59649 | -0.046693 | -0.0088351 | 3.9238 | 0.057328 | 0.087256 | 3.0968 | 0.084276 | -9.1278 | 0.013733 | -21.8491 | -2.5772 | 0.27466 | -115.5304 | -115.654 | 5.1773 | -0.045776 | 2.5406 | 5.6671 | 5.6213 | -115.6448 | -115.5624 | 0.050354 | -0.073242 | -5.6396 | 115.5945 | 113.0035 | 113.0768 | -15.0421 | -0.064086 | 0.018311 | -0.24719 | 120.7581 | 118.1213 | 118.103 | -0.29297 | 115.8554 | 106.4529 | 93.7317 | -121.5683 | 121.2479 | 121.2021 | 115.535 | -121.4767
2203.6406 | 121.5042 | -115.5762 | 5.9326 | -0.24062 | 0.033803 | 0.0090179 | 0.36502 | 0.070487 | 0.60931 | -0.049897 | -1.0922 | 3.9302 | 0.05092 | 0.08512 | 3.0946 | 0.092821 | -9.0637 | 0 | -21.904 | -2.5131 | 0.2655 | -115.4572 | -115.6036 | 5.1956 | -0.086975 | 2.5497 | 5.6992 | 5.6351 | -115.6357 | -115.5533 | 0.11902 | -0.027466 | -5.6671 | 115.5762 | 113.063 | 113.0905 | -14.9963 | -0.059509 | 0.022888 | -0.23346 | 120.7718 | 118.1259 | 118.103 | -0.29755 | 115.8417 | 106.5125 | 93.6722 | -121.5363 | 121.2753 | 121.2112 | 115.4892 | -121.4859
2204.6406 | 121.4218 | -115.4892 | 6.0013 | -0.33217 | 0.02953 | 0.019699 | 0.37891 | 0.06301 | 0.60183 | -0.057374 | -0.024094 | 3.9163 | 0.045579 | 0.086188 | 3.1085 | 0.091753 | -9.0683 | -0.009155 | -21.8079 | -2.4994 | 0.2655 | -115.5075 | -115.6448 | 5.1727 | -0.064087 | 2.5406 | 5.6763 | 5.6259 | -115.6265 | -115.48 | -0.01831 | -0.15564 | -5.7358 | 115.48 | 112.9898 | 113.1454 | -15.0696 | -0.13733 | 0.009155 | -0.32501 | 120.6619 | 118.0298 | 118.0206 | -0.37537 | 115.7547 | 106.4209 | 93.6813 | -121.6461 | 121.1655 | 121.1151 | 115.4251 | -121.4813
2205.6406 | 121.5775 | -115.5304 | 5.9601 | 0.38499 | 0.059437 | -0.00059506 | 0.38211 | 0.068351 | 0.6296 | -0.044557 | 0.46419 | 3.9259 | 0.054124 | 0.091529 | 3.1032 | 0.089617 | -9.1049 | -0.036621 | -21.8033 | -2.3666 | 0.2655 | -115.4984 | -115.6265 | 5.2094 | -0.10071 | 2.5131 | 5.6808 | 5.6351 | -115.5762 | -115.48 | 0.032044 | -0.09613 | -5.6946 | 115.4938 | 113.1638 | 113.2599 | -15.065 | -0.045776 | 0.050354 | -0.27924 | 120.7397 | 118.0435 | 117.9932 | -0.32501 | 115.7959 | 106.4255 | 93.7271 | -121.5866 | 121.2112 | 121.1655 | 115.4297 | -121.4401
2206.6406 | 121.6049 | -115.5075 | 5.9189 | -0.69838 | 0.030598 | -0.00059506 | 0.35755 | 0.06301 | 0.58688 | -0.040284 | 0.036941 | 3.927 | 0.041307 | 0.096869 | 3.0925 | 0.092821 | -8.9951 | 0.10529 | -21.6888 | -2.3163 | 0.21515 | -115.4846 | -115.6311 | 5.2643 | 0.045776 | 2.6459 | 5.6351 | 5.603 | -115.5991 | -115.535 | 0.022888 | -0.1236 | -5.7037 | 115.6128 | 113.1912 | 113.3148 | -14.9139 | -0.091553 | -0.027466 | -0.28381 | 120.7718 | 118.1534 | 118.1808 | -0.31586 | 115.7227 | 106.5125 | 93.8187 | -121.55 | 121.1426 | 121.1105 | 115.5533 | -121.4539
2207.6406 | 121.5546 | -115.5533 | 5.9097 | -0.24062 | 0.017781 | 0.012222 | 0.36075 | 0.065146 | 0.59115 | -0.061647 | -0.054612 | 3.9195 | 0.034898 | 0.081916 | 3.0957 | 0.091753 | -8.9951 | 0.082397 | -21.6248 | -2.3849 | 0.23346 | -115.4892 | -115.654 | 5.2048 | -0.022888 | 2.5543 | 5.6717 | 5.6076 | -115.6448 | -115.5441 | 0.064087 | -0.10071 | -5.6763 | 115.6357 | 113.1683 | 113.269 | -14.9048 | -0.091552 | 0.009156 | -0.23804 | 120.7581 | 118.1076 | 118.0984 | -0.30212 | 115.7867 | 106.5582 | 93.9285 | -121.5637 | 121.225 | 121.1609 | 115.5304 | -121.4539
2208.6406 | 121.4905 | -115.5533 | 5.9418 | -0.25588 | 0.025258 | 0.010086 | 0.36609 | 0.060874 | 0.6061 | -0.053102 | -1.2601 | 3.9312 | 0.060533 | 0.082984 | 3.1042 | 0.085345 | -9.0775 | 0.009155 | -21.6888 | -2.3987 | 0.27466 | -115.4297 | -115.5853 | 5.2002 | -0.086975 | 2.5269 | 5.7037 | 5.6396 | -115.6494 | -115.5579 | 0.1236 | -0.032043 | -5.6671 | 115.5624 | 113.1546 | 113.1866 | -15.0192 | -0.09613 | -0.004577 | -0.23804 | 120.7535 | 118.0801 | 118.0847 | -0.30212 | 115.8279 | 106.4758 | 93.8644 | -121.5271 | 121.257 | 121.1929 | 115.4663 | -121.4996
2209.6406 | 121.6232 | -115.5441 | 5.9097 | -2.3006 | 0.017781 | -0.0070041 | 0.36182 | 0.057669 | 0.59756 | -0.046693 | -0.0088351 | 3.9173 | 0.044511 | 0.10435 | 3.0904 | 0.092821 | -9.0317 | 0.13275 | -21.5607 | -2.3346 | 0.20599 | -115.4617 | -115.6128 | 5.2597 | 0.059509 | 2.6138 | 5.6259 | 5.5939 | -115.6128 | -115.5212 | 0.082397 | -0.068665 | -5.7037 | 115.6769 | 113.2095 | 113.2782 | -14.9414 | -0.068665 | 0.022888 | -0.28381 | 120.8038 | 118.158 | 118.1351 | -0.31586 | 115.7501 | 106.5125 | 93.9835 | -121.5225 | 121.17 | 121.138 | 115.6036 | -121.431
2210.6406 | 121.4951 | -115.448 | 5.9875 | 0.049296 | 0.056233 | 0.00047294 | 0.38104 | 0.059806 | 0.6296 | -0.053102 | 0.067459 | 3.9227 | 0.045579 | 0.086188 | 3.1085 | 0.075732 | -8.9996 | 0.064087 | -21.5607 | -2.3254 | 0.24261 | -115.5212 | -115.6586 | 5.2551 | -0.07782 | 2.4994 | 5.6351 | 5.603 | -115.6448 | -115.535 | -0.073242 | -0.21057 | -5.7449 | 115.5121 | 113.1226 | 113.3331 | -14.9872 | -0.19684 | -0.086975 | -0.35248 | 120.7031 | 117.9474 | 118.0344 | -0.38452 | 115.6906 | 106.4484 | 93.8873 | -121.6461 | 121.0831 | 121.051 | 115.3702 | -121.5225
2211.6406 | 121.5363 | -115.5762 | 5.928 | -0.2864 | 0.017781 | 0.0058129 | 0.38318 | 0.061942 | 0.6029 | -0.044557 | -0.16142 | 3.9141 | 0.047715 | 0.090461 | 3.1074 | 0.096026 | -9.0958 | 0.050354 | -21.579 | -2.3895 | 0.24719 | -115.5167 | -115.654 | 5.1819 | -0.07782 | 2.4811 | 5.6717 | 5.6259 | -115.6815 | -115.5487 | 0.059509 | -0.07782 | -5.6808 | 115.6265 | 113.1866 | 113.2645 | -15.0238 | -0.10529 | 0.027466 | -0.25635 | 120.7581 | 118.0573 | 118.0298 | -0.30212 | 115.8234 | 106.4804 | 93.9972 | -121.582 | 121.2479 | 121.2021 | 115.4984 | -121.4767
2212.6406 | 121.6232 | -115.5991 | 5.8456 | 2.0177 | 0.048756 | 0.0079499 | 0.37677 | 0.056601 | 0.59008 | -0.061647 | 0.12849 | 3.9099 | 0.032762 | 0.092597 | 3.0925 | 0.098162 | -9.0134 | 0.13275 | -21.524 | -2.33 | 0.19684 | -115.5441 | -115.6952 | 5.1819 | 0.018311 | 2.5818 | 5.5527 | 5.5161 | -115.6952 | -115.5991 | 0.054932 | -0.09613 | -5.6488 | 115.7318 | 113.269 | 113.3652 | -14.859 | -0.09613 | 0 | -0.29297 | 120.7809 | 118.1808 | 118.1808 | -0.32959 | 115.7959 | 106.5857 | 94.075 | -121.5408 | 121.1517 | 121.1151 | 115.6174 | -121.4447
2213.6406 | 121.637 | -115.5945 | 5.8182 | 0.14085 | -0.00037681 | 0.0026089 | 0.35007 | 0.069419 | 0.58688 | -0.047761 | -0.024094 | 3.9067 | 0.026353 | 0.084052 | 3.0936 | 0.091753 | -9.0134 | 0.18768 | -21.4783 | -2.4307 | 0.20599 | -115.5716 | -115.686 | 5.2139 | 0.009155 | 2.6093 | 5.5298 | 5.4794 | -115.6723 | -115.6036 | 0.022888 | -0.091553 | -5.6122 | 115.7822 | 113.1638 | 113.2553 | -14.8315 | -0.07782 | -0.009156 | -0.28839 | 120.8084 | 118.2037 | 118.2129 | -0.33875 | 115.8005 | 106.5811 | 94.1162 | -121.5042 | 121.1243 | 121.0739 | 115.6036 | -121.4218
2214.6875 | 121.5225 | -115.6082 | 5.8594 | 0.50706 | 0.066914 | -0.027298 | 0.35648 | 0.067282 | 0.61251 | -0.046693 | 0.50996 | 3.9312 | 0.066941 | 0.087256 | 3.101 | 0.087481 | -9.1232 | 0.09613 | -21.6888 | -2.3575 | 0.26093 | -115.5579 | -115.7089 | 5.1727 | -0.10986 | 2.449 | 5.6076 | 5.5573 | -115.6998 | -115.6036 | 0.050354 | -0.10071 | -5.5984 | 115.7043 | 113.2507 | 113.3514 | -14.9826 | -0.091553 | 0.004577 | -0.25177 | 120.7809 | 118.0573 | 118.0527 | -0.30212 | 115.8691 | 106.485 | 93.9194 | -121.5683 | 121.2158 | 121.1655 | 115.4984 | -121.463
2215.6406 | 121.5775 | -115.6128 | 5.7724 | -0.19484 | 0.0060322 | 0.012222 | 0.37143 | 0.073691 | 0.58474 | -0.050966 | -0.054612 | 3.9131 | 0.047715 | 0.080848 | 3.0946 | 0.091753 | -9.0363 | 0.16022 | -21.6843 | -2.2751 | 0.2243 | -115.5807 | -115.7043 | 5.1819 | 0.15564 | 2.5772 | 5.5206 | 5.4657 | -115.7089 | -115.6265 | 0.032043 | -0.091553 | -5.5481 | 115.773 | 113.3377 | 113.4293 | -14.8087 | -0.09613 | -0.013733 | -0.25177 | 120.7947 | 118.19 | 118.2037 | -0.3067 | 115.8371 | 106.5765 | 93.9285 | -121.4767 | 121.1334 | 121.0785 | 115.7684 | -121.3989
2216.6406 | 121.6278 | -115.6174 | 5.8273 | -2.1632 | 0.022053 | 0.011154 | 0.36075 | 0.061942 | 0.6029 | -0.057374 | -0.10039 | 3.9205 | 0.034898 | 0.080848 | 3.0893 | 0.089617 | -9.0958 | 0.16937 | -21.7667 | -2.3575 | 0.21057 | -115.567 | -115.7135 | 5.1773 | 0.032043 | 2.5818 | 5.5481 | 5.5206 | -115.7272 | -115.5991 | 0.050354 | -0.09613 | -5.6168 | 115.7867 | 113.2599 | 113.356 | -14.9231 | -0.10986 | 0.018311 | -0.27924 | 120.7947 | 118.1992 | 118.1808 | -0.3067 | 115.8279 | 106.5216 | 93.8507 | -121.5408 | 121.1655 | 121.138 | 115.6494 | -121.4264
2217.6406 | 121.6141 | -115.6357 | 5.7999 | -0.19484 | 0.015645 | 0.012222 | 0.36823 | 0.067282 | 0.58474 | -0.03708 | 0.29634 | 3.9099 | 0.054124 | 0.087256 | 3.0893 | 0.094958 | -9.2102 | 0.17853 | -21.698 | -2.3529 | 0.2243 | -115.6128 | -115.7593 | 5.1773 | 0.009155 | 2.5681 | 5.5206 | 5.4565 | -115.7364 | -115.6357 | 0.022888 | -0.1236 | -5.5756 | 115.8142 | 113.2828 | 113.4064 | -15.0101 | -0.10071 | 0 | -0.27924 | 120.813 | 118.2037 | 118.2037 | -0.34332 | 115.86 | 106.4255 | 93.9377 | -121.5591 | 121.1563 | 121.0922 | 115.6448 | -121.4355
2218.6406 | 121.5134 | -115.6815 | 5.809 | 0.034038 | 0.027394 | -0.0038001 | 0.37036 | 0.061942 | 0.61999 | -0.053102 | -0.25298 | 3.912 | 0.044511 | 0.092597 | 3.0925 | 0.086413 | -9.1324 | 0.032043 | -21.8124 | -2.3666 | 0.26093 | -115.6174 | -115.773 | 5.0812 | -0.091553 | 2.449 | 5.5435 | 5.4794 | -115.7913 | -115.6998 | 0.064087 | -0.091552 | -5.5481 | 115.7135 | 113.3148 | 113.4064 | -14.9414 | -0.10986 | -0.01831 | -0.2655 | 120.7626 | 118.1305 | 118.1488 | -0.32959 | 115.9424 | 106.5491 | 93.869 | -121.582 | 121.225 | 121.1609 | 115.5899 | -121.5088
2219.6406 | 121.6415 | -115.7043 | 5.6992 | -0.17959 | 0.016713 | 0.014358 | 0.36395 | 0.073691 | 0.59649 | -0.055238 | 0.0522 | 3.9131 | 0.03917 | 0.08512 | 3.0989 | 0.067187 | -9.0729 | 0.16022 | -21.5332 | -2.3849 | 0.21973 | -115.6723 | -115.8096 | 5.1132 | -0.2243 | 2.4994 | 5.4153 | 5.3696 | -115.8142 | -115.7318 | 0.032044 | -0.10528 | -5.4794 | 115.8646 | 113.3194 | 113.4247 | -14.772 | -0.10986 | -0.027466 | -0.28381 | 120.8176 | 118.2037 | 118.2312 | -0.32959 | 115.9241 | 106.6315 | 94.1711 | -121.5088 | 121.1197 | 121.0739 | 115.48 | -121.431
2220.6406 | 121.7331 | -115.6265 | 5.7999 | 0.00352 | 0.0092362 | 0.019699 | 0.36075 | 0.067282 | 0.59649 | -0.049897 | 0.0522 | 3.9163 | 0.046647 | 0.078712 | 3.0882 | 0.084276 | -9.0591 | 0.16937 | -21.2952 | -2.2247 | 0.22888 | -115.5624 | -115.7227 | 5.2277 | 0 | 2.5955 | 5.5481 | 5.5069 | -115.6631 | -115.5945 | 0.064087 | -0.09613 | -5.571 | 115.7959 | 113.4018 | 113.4979 | -14.859 | -0.036621 | 0.032044 | -0.25177 | 120.8542 | 118.222 | 118.19 | -0.29297 | 115.8554 | 106.5674 | 94.3314 | -121.5225 | 121.1746 | 121.1334 | 115.6265 | -121.3943
2221.6406 | 121.6599 | -115.567 | 5.864 | 0.049296 | 0.022053 | 0.011154 | 0.37891 | 0.049125 | 0.59008 | -0.048829 | 0.0522 | 3.9088 | 0.041307 | 0.082984 | 3.0957 | 0.09389 | -9.082 | 0.18768 | -21.3684 | -2.3163 | 0.2243 | -115.5258 | -115.6357 | 5.2734 | -0.036621 | 2.5864 | 5.5756 | 5.5115 | -115.654 | -115.5167 | 0.041199 | -0.068664 | -5.6396 | 115.7547 | 113.2507 | 113.3194 | -14.946 | -0.086975 | 0.050354 | -0.28839 | 120.8405 | 118.1534 | 118.103 | -0.35248 | 115.7913 | 106.485 | 94.1986 | -121.4996 | 121.1426 | 121.0785 | 115.5304 | -121.3806
2222.6406 | 121.5454 | -115.6265 | 5.8273 | -0.24062 | 0.031666 | 0.01329 | 0.36823 | 0.067282 | 0.61572 | -0.055238 | -0.14616 | 3.9259 | 0.035966 | 0.073371 | 3.101 | 0.070391 | -9.1507 | 0.11902 | -21.4279 | -2.3712 | 0.23346 | -115.567 | -115.7455 | 5.1636 | -0.086975 | 2.4902 | 5.5893 | 5.5115 | -115.7272 | -115.6357 | 0.059509 | -0.11902 | -5.5939 | 115.7455 | 113.2553 | 113.3743 | -14.978 | -0.10071 | -0.009155 | -0.23804 | 120.7901 | 118.1168 | 118.1259 | -0.31586 | 115.86 | 106.4758 | 94.1986 | -121.5729 | 121.2158 | 121.138 | 115.5396 | -121.463
2223.6406 | 121.6141 | -115.567 | 5.864 | -0.057515 | 0.0081682 | 0.0068819 | 0.3725 | 0.056601 | 0.59863 | -0.049897 | -4.556 | 3.9152 | 0.041307 | 0.095801 | 3.0893 | 0.091753 | -9.1461 | 0.17395 | -21.5424 | -2.4216 | 0.21973 | -115.5075 | -115.6906 | 5.3009 | -0.14648 | 2.5955 | 5.5756 | 5.5206 | -115.6952 | -115.5487 | 0.05951 | -0.1236 | -5.6442 | 115.741 | 113.1454 | 113.269 | -15.0101 | -0.12817 | 0.018311 | -0.28839 | 120.8679 | 118.1625 | 118.1442 | -0.34332 | 115.7867 | 106.4209 | 94.0247 | -121.5546 | 121.1426 | 121.0876 | 115.4205 | -121.4127
2224.6406 | 121.582 | -115.5441 | 5.8365 | -0.11855 | -0.0057178 | 0.022903 | 0.36182 | 0.070487 | 0.60824 | -0.060579 | -0.0088351 | 3.9099 | 0.027421 | 0.075507 | 3.0839 | 0.085345 | -9.1553 | 0.17395 | -21.5378 | -2.3758 | 0.20599 | -115.5258 | -115.6815 | 5.1132 | 0.27008 | 2.4857 | 5.5756 | 5.5069 | -115.654 | -115.5807 | 0.01831 | -0.13733 | -5.6305 | 115.7181 | 113.1683 | 113.3057 | -14.9918 | -0.10986 | -0.036622 | -0.26093 | 120.6573 | 118.0298 | 118.0664 | -0.32959 | 115.7501 | 106.3889 | 94.0063 | -121.5179 | 121.1197 | 121.051 | 115.8142 | -121.4172
2225.6562 | 121.6187 | -115.6219 | 5.809 | 0.59861 | 0.043416 | 0.011154 | 0.37784 | 0.070487 | 0.6264 | -0.040284 | 0.50996 | 3.9248 | 0.045579 | 0.10114 | 3.1096 | 0.090685 | -9.2468 | 0.036621 | -21.6293 | -2.4078 | 0.22888 | -115.5624 | -115.741 | 5.1956 | -0.07782 | 2.5131 | 5.5481 | 5.4886 | -115.7089 | -115.6036 | 0.059509 | -0.11902 | -5.5801 | 115.6586 | 113.2141 | 113.3331 | -15.0558 | -0.086975 | 0.01831 | -0.26093 | 120.8176 | 118.1351 | 118.1168 | -0.32044 | 115.8508 | 106.3751 | 93.9926 | -121.55 | 121.17 | 121.1105 | 115.5441 | -121.4127
2226.6406 | 121.6232 | -115.6082 | 5.7861 | -1.8733 | 0.01244 | 0.0026089 | 0.349 | 0.068351 | 0.60183 | -0.038148 | -0.085129 | 3.9152 | 0.03383 | 0.090461 | 3.0936 | 0.080004 | -9.2422 | 0.17853 | -21.4279 | -2.3621 | 0.20599 | -115.5624 | -115.7181 | 5.2139 | -0.013733 | 2.5589 | 5.5435 | 5.4977 | -115.7181 | -115.6128 | 0.045776 | -0.10986 | -5.5801 | 115.7867 | 113.2462 | 113.356 | -15.0284 | -0.10986 | -0.004578 | -0.24262 | 120.8221 | 118.1671 | 118.1717 | -0.28839 | 115.8142 | 106.366 | 94.1803 | -121.5042 | 121.1517 | 121.106 | 115.5945 | -121.3989
2227.6406 | 121.6919 | -115.6494 | 5.7495 | -0.026997 | 0.016713 | 0.0090179 | 0.37143 | 0.064078 | 0.59863 | -0.046693 | 0.0064239 | 3.9195 | 0.03383 | 0.088325 | 3.0839 | 0.096026 | -9.2194 | 0.1831 | -21.492 | -2.33 | 0.2243 | -115.6174 | -115.7684 | 5.1682 | 0.045776 | 2.5818 | 5.4749 | 5.4199 | -115.741 | -115.6769 | 0.032043 | -0.11902 | -5.5252 | 115.8325 | 113.3194 | 113.4384 | -14.9689 | -0.091553 | -0.027466 | -0.27466 | 120.8176 | 118.2312 | 118.2587 | -0.32959 | 115.8737 | 106.4301 | 94.1574 | -121.5179 | 121.1243 | 121.0693 | 115.6952 | -121.4264
2228.6406 | 121.6644 | -115.6723 | 5.7449 | -0.042256 | 0.010304 | 0.016495 | 0.36716 | 0.071555 | 0.60397 | -0.045625 | 0.20479 | 3.9131 | 0.035966 | 0.084052 | 3.1 | 0.098162 | -9.1919 | 0.17395 | -21.4462 | -2.5223 | 0.24261 | -115.6631 | -115.7959 | 5.1636 | 0.022888 | 2.5864 | 5.4749 | 5.4199 | -115.7684 | -115.6815 | 0.009155 | -0.1236 | -5.5023 | 115.8463 | 113.15 | 113.2736 | -14.9368 | -0.096131 | -0.009156 | -0.27008 | 120.8359 | 118.2587 | 118.2678 | -0.32501 | 115.9149 | 106.4804 | 94.2261 | -121.5408 | 121.1472 | 121.0922 | 115.6952 | -121.4264
2229.6406 | 121.6507 | -115.6403 | 5.7678 | 0.049296 | 0.0092362 | 0.0068819 | 0.36289 | 0.057669 | 0.60183 | -0.043489 | 0.15901 | 3.9067 | 0.034898 | 0.092597 | 3.0904 | 0.084276 | -9.2285 | 0.16937 | -21.4737 | -2.4857 | 0.23346 | -115.6128 | -115.7547 | 5.1865 | -0.68665 | 2.5589 | 5.5206 | 5.452 | -115.7501 | -115.6494 | 0.027466 | -0.11444 | -5.5344 | 115.8096 | 113.1546 | 113.269 | -14.9963 | -0.10986 | -0.009155 | -0.24719 | 120.8267 | 118.1992 | 118.2083 | -0.31586 | 115.8737 | 106.4117 | 94.1666 | -121.5225 | 121.1609 | 121.0922 | 114.9536 | -121.4172
2230.6406 | 121.6324 | -115.654 | 5.7953 | 0.81224 | 0.0028272 | 0.0015409 | 0.37143 | 0.064078 | 0.59863 | -0.039216 | -0.06987 | 3.9173 | 0.023149 | 0.094733 | 3.0925 | 0.078936 | -9.2697 | 0.16937 | -21.4233 | -2.3712 | 0.22888 | -115.6219 | -115.773 | 5.1773 | -0.054932 | 2.5085 | 5.5206 | 5.4428 | -115.7547 | -115.6219 | 0.032044 | -0.11902 | -5.5664 | 115.8234 | 113.2828 | 113.4018 | -15.065 | -0.10071 | 0.032044 | -0.27466 | 120.8313 | 118.1625 | 118.1305 | -0.35248 | 115.8829 | 106.3843 | 94.2307 | -121.5683 | 121.1746 | 121.0968 | 115.5991 | -121.4172
2231.6406 | 121.6324 | -115.6677 | 5.7724 | -0.14907 | 0.016713 | 0.014358 | 0.37357 | 0.055533 | 0.57833 | -0.049897 | 0.89143 | 3.9088 | 0.038102 | 0.089393 | 3.101 | 0.083208 | -9.0683 | -0.09613 | -21.6019 | -2.4811 | 0.21515 | -115.6357 | -115.7684 | 5.1682 | -0.16937 | 2.5177 | 5.5115 | 5.4337 | -115.7593 | -115.6723 | 0.032044 | -0.10071 | -5.5573 | 115.5716 | 113.1866 | 113.2874 | -14.8407 | -0.091552 | -0.004577 | -0.26093 | 120.8359 | 118.1854 | 118.19 | -0.33875 | 115.8829 | 106.5994 | 94.0659 | -121.5408 | 121.1792 | 121.1014 | 115.4984 | -121.4447
2232.6406 | 121.6827 | -115.6723 | 5.7632 | -0.057515 | 0.037007 | 0.014358 | 0.35541 | 0.054465 | 0.60076 | -0.052034 | -0.054612 | 3.9024 | 0.027421 | 0.086188 | 3.0989 | 0.08214 | -9.2514 | 0.18768 | -21.6339 | -2.3849 | 0.23346 | -115.6403 | -115.7639 | 5.191 | -1.5152 | 2.5635 | 5.4749 | 5.4199 | -115.7501 | -115.6586 | 0.032043 | -0.091553 | -5.5298 | 115.86 | 113.2874 | 113.3789 | -15.0146 | -0.07782 | 0.013733 | -0.28839 | 120.8633 | 118.2358 | 118.222 | -0.34332 | 115.9058 | 106.4209 | 94.0384 | -121.5271 | 121.1472 | 121.0922 | 114.1571 | -121.4218
2233.6406 | 121.6507 | -115.6494 | 5.7632 | 0.00352 | 0.0092362 | 0.0090179 | 0.37036 | 0.066214 | 0.59222 | -0.049897 | 0.17427 | 3.9109 | 0.041307 | 0.095801 | 3.0882 | 0.089617 | -9.3201 | 0.16479 | -21.4096 | -2.449 | 0.21973 | -115.6357 | -115.7547 | 5.191 | -0.19226 | 2.5589 | 5.4932 | 5.4199 | -115.7501 | -115.6815 | 0.013733 | -0.10529 | -5.5435 | 115.8142 | 113.2004 | 113.3057 | -15.0833 | -0.10071 | -0.032044 | -0.27008 | 120.8405 | 118.2083 | 118.2404 | -0.34332 | 115.8691 | 106.3293 | 94.2398 | -121.5179 | 121.1426 | 121.0693 | 115.4572 | -121.4447
2234.6406 | 121.637 | -115.6815 | 5.7587 | -0.011739 | 0.0092362 | 0.021835 | 0.37143 | 0.060874 | 0.59969 | -0.053102 | 0.2353 | 3.9067 | 0.038102 | 0.074439 | 3.0861 | 0.069323 | -9.3704 | 0.13733 | -21.3226 | -2.3438 | 0.24719 | -115.6311 | -115.7593 | 5.2002 | -0.36621 | 2.5589 | 5.5161 | 5.4291 | -115.7455 | -115.6815 | 0.050354 | -0.077819 | -5.5115 | 115.8188 | 113.3377 | 113.4155 | -15.1291 | -0.064086 | 0 | -0.24261 | 120.8817 | 118.2404 | 118.2404 | -0.32959 | 115.9287 | 106.311 | 94.3588 | -121.5179 | 121.1975 | 121.1105 | 115.3152 | -121.4401
2235.6406 | 121.637 | -115.6631 | 5.7678 | 0.095073 | -0.0025128 | 0.017563 | 0.35541 | 0.068351 | 0.60504 | -0.046693 | 0.18953 | 3.9099 | 0.018876 | 0.074439 | 3.0882 | 0.087481 | -9.4711 | 0.13733 | -21.1487 | -2.1149 | 0.22888 | -115.6403 | -115.7501 | 5.1682 | -0.17395 | 2.536 | 5.4977 | 5.4291 | -115.7547 | -115.6723 | 0.022888 | -0.086975 | -5.5389 | 115.8005 | 113.5483 | 113.6353 | -15.239 | -0.091553 | -0.009155 | -0.27008 | 120.8313 | 118.1992 | 118.2083 | -0.33874 | 115.892 | 106.192 | 94.5145 | -121.5179 | 121.1609 | 121.0922 | 115.4892 | -121.4401
2236.6406 | 121.6507 | -115.6082 | 5.777 | 0.14085 | 0.0060322 | 0.016495 | 0.37036 | 0.055533 | 0.60397 | -0.043489 | 0.41841 | 3.9131 | 0.031694 | 0.080848 | 3.0968 | 0.092821 | -9.5856 | 0.1236 | -21.2814 | -2.0233 | 0.25635 | -115.6036 | -115.7593 | 5.1956 | -0.07782 | 2.5589 | 5.5298 | 5.4703 | -115.7089 | -115.6265 | 0.004577 | -0.15106 | -5.5206 | 115.7318 | 113.5849 | 113.736 | -15.3625 | -0.10071 | -0.018311 | -0.24719 | 120.8038 | 118.1671 | 118.1854 | -0.3067 | 115.8646 | 106.0226 | 94.3268 | -121.5363 | 121.138 | 121.0785 | 115.5304 | -121.4035
2237.6406 | 121.6599 | -115.6631 | 5.7495 | -0.057515 | 0.01244 | 0.014358 | 0.36075 | 0.071555 | 0.59222 | -0.046693 | -0.039353 | 3.9163 | 0.029557 | 0.078712 | 3.0829 | 0.08214 | -9.5993 | 0.15564 | -21.1945 | -2.1194 | 0.24719 | -115.6219 | -115.773 | 5.2002 | -0.28839 | 2.5543 | 5.4749 | 5.4153 | -115.7593 | -115.6219 | 0.041199 | -0.10986 | -5.5023 | 115.8188 | 113.5437 | 113.6536 | -15.3488 | -0.09613 | 0.041199 | -0.27466 | 120.8633 | 118.2175 | 118.1763 | -0.33417 | 115.9103 | 106.0638 | 94.4687 | -121.5225 | 121.138 | 121.0785 | 115.3748 | -121.3715
2238.6406 | 121.637 | -115.7318 | 5.6808 | 0.15611 | 0.0038952 | 0.014358 | 0.36395 | 0.054465 | 0.59863 | -0.050966 | 0.15901 | 3.912 | 0.030626 | 0.076575 | 3.0946 | 0.089617 | -9.7916 | 0.15106 | -21.2677 | -2.3666 | 0.23804 | -115.6952 | -115.8463 | 5.1178 | -0.84228 | 2.5406 | 5.4062 | 5.3604 | -115.8096 | -115.7272 | 0.036622 | -0.11444 | -5.4428 | 115.8829 | 113.3652 | 113.4796 | -15.4724 | -0.077819 | 0.004578 | -0.27466 | 120.8496 | 118.2724 | 118.2678 | -0.32043 | 115.9698 | 105.9402 | 94.4641 | -121.5271 | 121.138 | 121.0922 | 114.8895 | -121.4081
2239.6406 | 121.6461 | -115.741 | 5.6992 | 0.21714 | 0.043416 | -0.00059506 | 0.37998 | 0.069419 | 0.60397 | -0.042421 | 0.021682 | 3.9152 | 0.040239 | 0.07978 | 3.1021 | 0.085345 | -11.3846 | 0.10986 | -21.2997 | -2.33 | 0.2243 | -115.7043 | -115.8371 | 5.0949 | -0.050354 | 2.5085 | 5.4382 | 5.3787 | -115.8325 | -115.7181 | 0.036621 | -0.09613 | -5.4749 | 115.8508 | 113.4109 | 113.5071 | -17.0837 | -0.091553 | 0.022888 | -0.26093 | 120.8359 | 118.2495 | 118.2266 | -0.32043 | 115.9653 | 104.3564 | 94.4412 | -121.5363 | 121.1792 | 121.1197 | 115.6906 | -121.4172
2240.6406 | 121.6553 | -115.773 | 5.6351 | 0.20188 | 0.0028272 | -0.00059506 | 0.36182 | 0.055533 | 0.59756 | -0.046693 | 0.25056 | 3.9056 | 0.043443 | 0.086188 | 3.0989 | 0.086413 | -11.5082 | 0.12817 | -21.3318 | -2.3575 | 0.24261 | -115.7455 | -115.9058 | 5.0674 | -0.41199 | 2.5269 | 5.3558 | 5.3238 | -115.8829 | -115.7776 | 0.027466 | -0.13275 | -5.3925 | 115.9012 | 113.4155 | 113.5483 | -17.1433 | -0.10986 | -0.004578 | -0.27924 | 120.8405 | 118.2999 | 118.3044 | -0.31128 | 116.0156 | 104.2648 | 94.4412 | -121.5408 | 121.1288 | 121.0968 | 115.361 | -121.4127
2241.6406 | 121.6644 | -115.7593 | 5.6534 | 0.18663 | 0.00069119 | 0.016495 | 0.35861 | 0.057669 | 0.59649 | -0.044557 | 0.3116 | 3.9141 | 0.041307 | 0.10007 | 3.0936 | 0.090685 | -11.3388 | 0.086975 | -21.405 | -2.4582 | 0.21515 | -115.741 | -115.8737 | 5.0491 | -0.40741 | 2.5406 | 5.4062 | 5.3192 | -115.8508 | -115.741 | 0.01831 | -0.11444 | -5.4382 | 115.8463 | 113.3011 | 113.4155 | -16.9922 | -0.091553 | 0.01831 | -0.24719 | 120.8084 | 118.2999 | 118.2816 | -0.33417 | 115.9744 | 104.4205 | 94.3542 | -121.5271 | 121.1655 | 121.0785 | 115.3519 | -121.3943
2242.6406 | 121.6461 | -115.8051 | 5.5984 | 0.034038 | 0.014576 | 0.0090179 | 0.36716 | 0.051261 | 0.60397 | -0.048829 | 0.097976 | 3.9141 | 0.044511 | 0.097938 | 3.0904 | 0.087481 | -11.2747 | 0.16937 | -21.4462 | -2.2888 | 0.24261 | -115.7501 | -115.9103 | 5.0629 | -1.9089 | 2.5452 | 5.3329 | 5.2643 | -115.9149 | -115.8096 | 0.054932 | -0.10528 | -5.3558 | 115.9744 | 113.5162 | 113.6215 | -16.8732 | -0.10986 | -0.004577 | -0.2655 | 120.8679 | 118.3502 | 118.3548 | -0.33417 | 116.0477 | 104.5303 | 94.3588 | -121.5088 | 121.138 | 121.0693 | 113.8962 | -121.4081
2243.6406 | 121.6507 | -115.8325 | 5.6396 | -0.65261 | 0.028462 | 0.0068819 | 0.37464 | 0.055533 | 0.59008 | -0.041353 | 0.3116 | 3.9141 | 0.03383 | 0.07978 | 3.0936 | 0.087481 | -11.1191 | 0.086975 | -21.5607 | -2.0462 | 0.20142 | -115.8051 | -115.9378 | 5.0079 | -2.4399 | 2.5223 | 5.3467 | 5.2963 | -115.9149 | -115.8096 | 0.027466 | -0.10528 | -5.4382 | 115.9195 | 113.7863 | 113.8916 | -16.7587 | -0.082397 | 0.022889 | -0.29297 | 120.8405 | 118.3548 | 118.3319 | -0.34332 | 116.0339 | 104.7134 | 94.2719 | -121.5775 | 121.1792 | 121.1288 | 113.3926 | -121.4493
2244.6406 | 121.6507 | -115.7822 | 5.6213 | 0.095073 | -0.00037681 | 0.0047449 | 0.36395 | 0.054465 | 0.60183 | -0.039216 | 0.14375 | 3.9141 | 0.026353 | 0.078712 | 3.0871 | 0.088549 | -10.7758 | 0.14191 | -21.4233 | -2.1515 | 0.23804 | -115.7593 | -115.9149 | 5.0583 | -1.2817 | 2.5406 | 5.3604 | 5.3055 | -115.8966 | -115.8005 | 0.022889 | -0.13275 | -5.3833 | 115.9241 | 113.6307 | 113.7634 | -16.3971 | -0.11444 | -0.01831 | -0.26092 | 120.8405 | 118.3228 | 118.3411 | -0.31586 | 116.0202 | 105.0064 | 94.3588 | -121.5363 | 121.1426 | 121.0876 | 114.5004 | -121.4218
2245.6406 | 121.6827 | -115.9287 | 5.4932 | 0.14085 | 0.022053 | 0.0036769 | 0.36395 | 0.065146 | 0.59863 | -0.057374 | 0.18953 | 3.9067 | 0.040239 | 0.084052 | 3.0914 | 0.08214 | -10.6018 | 0.13275 | -21.4416 | -2.2476 | 0.24719 | -115.8737 | -116.0614 | 4.9438 | -5.0903 | 2.5406 | 5.2597 | 5.1865 | -115.9882 | -115.9195 | 0.054932 | -0.13275 | -5.246 | 116.0614 | 113.681 | 113.8138 | -16.095 | -0.059509 | 0.009155 | -0.23346 | 120.8725 | 118.4692 | 118.4601 | -0.3067 | 116.1758 | 105.3268 | 94.487 | -121.5546 | 121.1884 | 121.1151 | 110.8383 | -121.4127
2246.6406 | 121.6415 | -115.9241 | 5.484 | -0.10329 | 0.019917 | 0.018631 | 0.36075 | 0.070487 | 0.6029 | -0.046693 | 0.0064239 | 3.9184 | 0.030626 | 0.081916 | 3.0882 | 0.081072 | -10.4782 | 0.18768 | -21.405 | -2.2385 | 0.21973 | -115.8875 | -116.0339 | 4.921 | -2.7328 | 2.5131 | 5.2368 | 5.159 | -116.0294 | -115.9424 | 0.036621 | -0.10986 | -5.2643 | 116.1118 | 113.6856 | 113.7955 | -15.9622 | -0.10529 | -0.018311 | -0.24719 | 120.845 | 118.4372 | 118.4555 | -0.32501 | 116.1438 | 105.4459 | 94.519 | -121.5179 | 121.1609 | 121.0831 | 113.1912 | -121.4264
2247.6406 | 121.637 | -115.8463 | 5.5756 | 0.20188 | -0.0025128 | 0.0015409 | 0.35541 | 0.055533 | 0.59649 | -0.047761 | 0.22005 | 3.9163 | 0.032762 | 0.080848 | 3.0946 | 0.087481 | -10.4599 | 0.12817 | -21.3959 | -2.179 | 0.24261 | -115.8188 | -115.9882 | 4.9988 | -3.804 | 2.5223 | 5.3101 | 5.246 | -115.9332 | -115.8508 | 0.027465 | -0.14191 | -5.3329 | 115.9744 | 113.6673 | 113.8092 | -16.0355 | -0.086976 | -0.004578 | -0.2655 | 120.845 | 118.3685 | 118.3731 | -0.32959 | 116.0889 | 105.3864 | 94.4504 | -121.5637 | 121.1563 | 121.0922 | 112.0422 | -121.4264
2248.6406 | 121.6415 | -115.8005 | 5.6305 | 0.095073 | 0.020985 | 0.0068819 | 0.35541 | 0.052329 | 0.59329 | -0.042421 | 0.2353 | 3.912 | 0.047715 | 0.081916 | 3.0914 | 0.090685 | -10.3821 | 0.11444 | -21.2173 | -2.2156 | 0.23346 | -115.773 | -115.9103 | 5.0446 | -6.1111 | 2.4994 | 5.3696 | 5.3055 | -115.8783 | -115.7822 | 0.027466 | -0.10986 | -5.397 | 115.9149 | 113.5849 | 113.6948 | -16.0126 | -0.07782 | 0.01831 | -0.26093 | 120.845 | 118.2999 | 118.2816 | -0.32501 | 116.0339 | 105.4184 | 94.5831 | -121.5408 | 121.17 | 121.106 | 109.6893 | -121.4127
2249.6719 | 121.4996 | -115.8508 | 5.6351 | 0.29344 | 0.062642 | -0.00059506 | 0.36289 | 0.065146 | 0.63067 | -0.031739 | 0.25056 | 3.9312 | 0.05092 | 0.10648 | 3.116 | 0.075732 | -10.405 | -0.022888 | -21.5698 | -2.1744 | 0.25177 | -115.8508 | -115.9836 | 4.9072 | -6.6559 | 2.3209 | 5.3558 | 5.3009 | -115.9607 | -115.8554 | 0 | -0.13275 | -5.3833 | 115.8279 | 113.6765 | 113.8092 | -16.04 | -0.10986 | -0.004578 | -0.27924 | 120.7581 | 118.1717 | 118.1763 | -0.33417 | 116.1026 | 105.4459 | 94.281 | -121.6187 | 121.2067 | 121.1517 | 109.1949 | -121.4905
2250.6406 | 121.6324 | -115.7959 | 5.6168 | -0.2101 | 0.010304 | 0.011154 | 0.36075 | 0.071555 | 0.59435 | -0.038148 | -1.8857 | 3.9099 | 0.055192 | 0.081916 | 3.0775 | 0.086413 | -10.2585 | 0.15564 | -21.4142 | -2.0233 | 0.20599 | -115.8279 | -115.9744 | 5.0491 | -18.187 | 2.4994 | 5.3375 | 5.2872 | -115.9195 | -115.7684 | -0.032044 | -0.17853 | -5.4108 | 115.9515 | 113.7726 | 113.9511 | -15.8752 | -0.1236 | 0.027465 | -0.27924 | 120.845 | 118.2953 | 118.2678 | -0.32959 | 116.0019 | 105.5374 | 94.3817 | -121.5912 | 121.1334 | 121.0831 | 97.6089 | -121.3852
2251.6406 | 121.6141 | -115.8142 | 5.6168 | -0.16433 | 0.02419 | -0.00059506 | 0.35968 | 0.083304 | 0.60076 | -0.052034 | 4.2178 | 3.9056 | 0.029557 | 0.10114 | 3.101 | 0.08214 | -10.2493 | 0.15106 | -21.4142 | -2.0096 | 0.2243 | -115.7913 | -115.9698 | 5.0308 | -2.0279 | 2.4902 | 5.3238 | 5.2643 | -115.9149 | -115.8188 | 0.022888 | -0.15564 | -5.3925 | 115.9653 | 113.8046 | 113.9603 | -15.8661 | -0.10071 | -0.004578 | -0.29297 | 120.845 | 118.3044 | 118.309 | -0.35248 | 116.0385 | 105.5649 | 94.4 | -121.5866 | 121.138 | 121.0785 | 113.7863 | -121.4355
2252.6406 | 121.6736 | -115.8783 | 5.5435 | -0.14907 | 0.013508 | 0.01329 | 0.37143 | 0.060874 | 0.60183 | -0.049897 | 0.37263 | 3.9238 | 0.038102 | 0.082984 | 3.1 | 0.10137 | -10.2676 | 0.15564 | -21.405 | -1.9318 | 0.24719 | -115.8371 | -115.9882 | 4.9988 | -3.1082 | 2.5314 | 5.2689 | 5.2185 | -115.9973 | -115.8875 | 0.041199 | -0.10986 | -5.2963 | 116.0339 | 113.9465 | 114.0564 | -15.8112 | -0.11902 | -0.009155 | -0.27466 | 120.8771 | 118.4097 | 118.4189 | -0.32501 | 116.1255 | 105.6107 | 94.4733 | -121.5317 | 121.1472 | 121.0968 | 112.7701 | -121.431
2253.6406 | 121.6461 | -115.7639 | 5.6396 | -0.16433 | 0.019917 | -0.0070041 | 0.36182 | 0.058738 | 0.6061 | -0.052034 | -0.054612 | 3.9109 | 0.03917 | 0.095801 | 3.0968 | 0.090685 | -10.2448 | 0.16022 | -21.3547 | -2.0737 | 0.2243 | -115.7776 | -115.892 | 5.0949 | -2.5955 | 2.4719 | 5.3558 | 5.3101 | -115.9195 | -115.7959 | -0.013733 | -0.12817 | -5.4153 | 115.9241 | 113.6902 | 113.8184 | -15.8844 | -0.15564 | -0.032043 | -0.28381 | 120.8588 | 118.2358 | 118.2678 | -0.32959 | 115.9882 | 105.5191 | 94.4092 | -121.5317 | 121.1197 | 121.0739 | 113.1683 | -121.4355
2254.6406 | 121.6736 | -115.7547 | 5.6534 | 0.11033 | 0.0028272 | 0.0079499 | 0.35114 | 0.056601 | 0.58901 | -0.045625 | -0.11565 | 3.9173 | 0.021012 | 0.088325 | 3.1021 | 0.090685 | -10.2676 | 0.16479 | -21.2631 | -2.0554 | 0.24261 | -115.7227 | -115.8829 | 5.0995 | -2.3163 | 2.536 | 5.3787 | 5.3284 | -115.86 | -115.7639 | 0.032044 | -0.12817 | -5.4108 | 115.9195 | 113.6993 | 113.8275 | -15.921 | -0.10528 | -0.009155 | -0.27466 | 120.8542 | 118.2907 | 118.2999 | -0.32501 | 115.9973 | 105.4871 | 94.4916 | -121.5363 | 121.1334 | 121.0831 | 113.4384 | -121.4172
2255.6406 | 121.6553 | -116.0019 | 5.4108 | -0.14907 | -0.00037681 | 0.011154 | 0.36289 | 0.064078 | 0.59969 | -0.040284 | -0.039353 | 3.9056 | 0.035966 | 0.078712 | 3.0946 | 0.096026 | -10.3088 | 0.14648 | -21.405 | -1.9638 | 0.2243 | -115.9744 | -116.1026 | 4.747 | -2.3163 | 2.2934 | 5.1498 | 5.0674 | -116.1392 | -116.0156 | 0.027466 | -0.10071 | -5.1865 | 116.1484 | 114.0381 | 114.1388 | -15.7196 | -0.13733 | -0.013733 | -0.26093 | 120.7489 | 118.2953 | 118.309 | -0.34332 | 116.2262 | 105.6931 | 94.5969 | -121.5134 | 121.1517 | 121.0693 | 113.6856 | -121.4264
2256.6719 | 121.4859 | -116.0614 | 5.4337 | 0.3087 | 0.032734 | -0.020889 | 0.38318 | 0.058738 | 0.64562 | -0.033876 | 0.37263 | 3.9387 | 0.03383 | 0.084052 | 3.1128 | 0.08214 | -10.4141 | -0.004578 | -21.7392 | -2.0554 | 0.24719 | -116.0385 | -116.185 | 4.7287 | -1.7487 | 2.3254 | 5.1727 | 5.0858 | -116.1621 | -116.0614 | 0.022888 | -0.1236 | -5.1865 | 116.0568 | 114.006 | 114.1296 | -15.8478 | -0.10071 | 0 | -0.26093 | 120.7901 | 118.3868 | 118.3868 | -0.3479 | 116.3086 | 105.6473 | 94.3222 | -121.6187 | 121.2341 | 121.1472 | 114.3127 | -121.4951
2257.6406 | 121.669 | -115.9973 | 5.4474 | 0.12559 | 0.013508 | 0.011154 | 0.36075 | 0.057669 | 0.59435 | -0.042421 | 0.2353 | 3.9184 | 0.03917 | 0.096869 | 3.0914 | 0.1003 | -10.4004 | 0.15564 | -21.579 | -1.9318 | 0.24261 | -115.9424 | -116.0614 | 4.8614 | -1.6342 | 2.4994 | 5.1727 | 5.1178 | -116.066 | -116.0019 | 0.054931 | -0.064087 | -5.2048 | 116.153 | 114.0656 | 114.1296 | -15.8478 | -0.068665 | -0.004578 | -0.27466 | 120.8588 | 118.4967 | 118.5013 | -0.32959 | 116.2399 | 105.5969 | 94.4183 | -121.5088 | 121.17 | 121.1151 | 114.3631 | -121.4493
2258.6406 | 121.6599 | -115.86 | 5.5527 | -0.11855 | 0.019917 | 0.0015409 | 0.36289 | 0.064078 | 0.59115 | -0.049897 | 0.0522 | 3.9045 | 0.03383 | 0.095801 | 3.0871 | 0.089617 | -10.3134 | 0.19226 | -21.7346 | -1.8997 | 0.2243 | -115.8188 | -115.9653 | 4.985 | -8.7067 | 2.4948 | 5.3009 | 5.2414 | -115.9607 | -115.8646 | 0.041198 | -0.10529 | -5.3284 | 116.0522 | 113.9603 | 114.0656 | -15.8661 | -0.10071 | -0.004578 | -0.25177 | 120.845 | 118.3548 | 118.3594 | -0.31128 | 116.0843 | 105.5466 | 94.1254 | -121.5179 | 121.1609 | 121.1014 | 107.1533 | -121.4172
2259.6406 | 121.6599 | -115.8554 | 5.5847 | -0.14907 | 0.0092362 | 0.023971 | 0.36609 | 0.070487 | 0.60824 | -0.041353 | -0.4666 | 3.9152 | 0.032762 | 0.087256 | 3.0925 | 0.087481 | -10.4462 | 0.29755 | -21.9131 | -2.0828 | 0.21973 | -115.86 | -116.0019 | 4.9622 | -1.9638 | 2.4719 | 5.3055 | 5.2368 | -115.9744 | -115.86 | -0.004577 | -0.14648 | -5.365 | 116.153 | 113.7726 | 113.9191 | -16.0309 | -0.11902 | -0.004577 | -0.27924 | 120.8176 | 118.3273 | 118.3319 | -0.3479 | 116.0751 | 105.4092 | 93.9423 | -121.5866 | 121.1609 | 121.0922 | 113.8916 | -121.4447
2260.6406 | 121.55 | -115.8051 | 5.6442 | -0.11855 | 0.016713 | 0.011154 | 0.35541 | 0.057669 | 0.61144 | -0.049897 | -0.13091 | 3.9152 | 0.030626 | 0.095801 | 3.0968 | 0.085345 | -10.1349 | 0.10986 | -21.6843 | -2.0599 | 0.23804 | -115.8051 | -115.9241 | 4.9713 | -3.4332 | 2.4216 | 5.3604 | 5.2963 | -115.9515 | -115.8463 | 0 | -0.11902 | -5.4062 | 115.9149 | 113.7451 | 113.8641 | -15.7791 | -0.14648 | -0.041198 | -0.28381 | 120.7764 | 118.2266 | 118.2678 | -0.3479 | 116.0431 | 105.6702 | 94.1208 | -121.5683 | 121.1655 | 121.1014 | 112.3718 | -121.4905
2261.6406 | 121.6599 | -120.8038 | 0.58594 | -0.11855 | 0.0081682 | 0.021835 | 0.36716 | -0.052346 | -0.020881 | 0.028075 | 0.11323 | 3.238 | 0.034898 | 0.087256 | 3.1427 | 0.091753 | 0.059509 | 0.14648 | 0.032043 | 0.10071 | 0.24261 | -0.10986 | -0.2655 | 0.1236 | -2.1469 | -0.082397 | 0.37994 | 0.33875 | -120.932 | -120.8725 | 120.694 | 120.5383 | -0.34332 | 120.9503 | 120.9045 | 0.36621 | -0.52643 | -0.12817 | -0.068665 | -0.20599 | 120.9274 | 120.7214 | 120.7901 | -0.24719 | 121.0464 | 120.8633 | 120.8359 | -0.85144 | 121.1838 | 121.1426 | 118.6569 | -121.4584
2262.6406 | 121.6736 | -120.8862 | 0.59052 | 0.034038 | 0.017781 | 0.025039 | 0.36502 | -0.068368 | -0.024085 | 0.023803 | 0.20479 | 3.2487 | 0.025285 | 0.091529 | 3.1491 | 0.090685 | 0.064087 | 0.13733 | 0.013733 | 0.07782 | 0.24719 | -0.10071 | -0.28381 | 0.1236 | -105.368 | -0.09613 | 0.39825 | 0.34332 | -120.9961 | -120.8679 | 120.7855 | 120.6024 | -0.34332 | 121.0236 | 120.9641 | 0.36163 | -0.52643 | -0.10986 | 0.01831 | -0.19226 | 121.0098 | 120.7901 | 120.7718 | -0.24719 | 121.1334 | 120.9503 | 120.9 | -0.87433 | 121.2845 | 121.2296 | 15.5182 | -121.4584
2263.6406 | 121.6644 | -120.9366 | 0.59967 | -0.19484 | 0.01244 | 0.0058129 | 0.3693 | -0.058755 | -0.020881 | 0.033416 | 0.64729 | 3.2508 | 0.043443 | 0.087256 | 3.1576 | 0.084276 | -0.045776 | 0.3891 | 0.12817 | 0.018311 | 0.22888 | -0.13733 | -0.30212 | 0.10071 | -72.6608 | -0.13275 | 0.3891 | 0.32959 | -121.0007 | -120.9137 | 120.7993 | 120.6345 | -0.37079 | 121.3257 | 120.9549 | 0.32044 | -0.64545 | -0.064087 | 0.022888 | -0.21057 | 121.0373 | 120.8038 | 120.7809 | -0.27008 | 121.1655 | 120.8908 | 121.0648 | -0.90179 | 121.3257 | 121.2662 | 48.2758 | -121.5134
2264.6406 | 121.7102 | -120.9229 | 0.59509 | -0.11855 | 0.019917 | 0.011154 | 0.34686 | -0.057687 | -0.01554 | 0.037688 | -0.23772 | 3.2466 | 0.01674 | 0.084052 | 3.1384 | 0.080004 | 0.064087 | 0.15564 | 0.036621 | 0.09613 | 0.21973 | -0.12817 | -0.28839 | 0.10071 | -109.5062 | -0.16022 | 0.36163 | 0.31586 | -121.0281 | -120.9091 | 120.7947 | 120.6345 | -0.37537 | 121.0785 | 121.019 | 0.38452 | -0.53101 | -0.10528 | 0.013733 | -0.23346 | 121.0236 | 120.7626 | 120.7489 | -0.27924 | 121.1426 | 120.9869 | 120.9595 | -0.88348 | 121.2845 | 121.2387 | 11.4166 | -121.5042
2265.6406 | 121.7148 | -120.9183 | 0.59967 | 0.034038 | 0.011372 | 0.012222 | 0.36823 | -0.072641 | -0.027289 | 0.031279 | 0.0522 | 3.2583 | 0.034898 | 0.072303 | 3.1576 | 0.085345 | 0.07782 | 0.15106 | 0.009155 | 0.091553 | 0.23346 | -0.11444 | -0.26093 | 0.11444 | -1.5747 | -0.09613 | 0.39825 | 0.32501 | -121.0098 | -120.9137 | 120.8038 | 120.6573 | -0.36621 | 121.0693 | 121.0098 | 0.35248 | -0.52185 | -0.091553 | 0.004578 | -0.20142 | 121.0327 | 120.8221 | 120.8176 | -0.27466 | 121.1517 | 120.9961 | 120.9274 | -0.86059 | 121.3165 | 121.2433 | 119.3436 | -121.5134
2266.6406 | 121.7102 | -120.9229 | 0.60883 | -0.16433 | 0.011372 | 0.012222 | 0.349 | -0.0673 | -0.046515 | 0.037688 | 0.50996 | 3.2508 | 0.019944 | 0.092597 | 3.1662 | 0.080004 | 0.23804 | -0.1236 | -0.045776 | 0.11902 | 0.21515 | -0.12817 | -0.27924 | 0.082397 | -4.0466 | -0.11902 | 0.3891 | 0.33417 | -121.0327 | -120.9503 | 120.7947 | 120.6436 | -0.39368 | 120.7993 | 121.0419 | 0.39825 | -0.37079 | -0.10986 | -0.027465 | -0.21973 | 121.0052 | 120.8038 | 120.8313 | -0.27466 | 121.138 | 121.1609 | 120.8771 | -0.88806 | 121.312 | 121.257 | 116.8762 | -121.5591
2267.6406 | 121.7468 | -120.9412 | 0.59052 | -0.011739 | -0.0046498 | 0.0036769 | 0.36716 | -0.051278 | -0.026221 | 0.038756 | -0.11565 | 3.2444 | 0.026353 | 0.07978 | 3.1555 | 0.094958 | 0.07782 | 0.17395 | 0.027466 | 0.091553 | 0.25635 | -0.086975 | -0.25635 | 0.14191 | -3.6758 | -0.07782 | 0.38452 | 0.33417 | -121.0419 | -120.932 | 120.8542 | 120.6848 | -0.33417 | 121.1151 | 121.0327 | 0.3479 | -0.5127 | -0.10071 | 0.009155 | -0.20599 | 121.0831 | 120.8633 | 120.8542 | -0.25635 | 121.1975 | 121.019 | 120.9686 | -0.84686 | 121.3257 | 121.2753 | 117.2653 | -121.5225
2268.6406 | 121.6919 | -120.9366 | 0.6134 | 0.24766 | 0.016713 | 0.025039 | 0.3458 | -0.065164 | -0.019813 | 0.047301 | 0.15901 | 3.2562 | 0.024217 | 0.07978 | 3.1544 | 0.086413 | 0.032043 | 0.064087 | -0.036621 | 0.032043 | 0.16479 | -0.16479 | -0.31586 | 0.068665 | -110.0922 | -0.14191 | 0.40741 | 0.34332 | -121.0236 | -120.9412 | 120.7718 | 120.6207 | -0.44861 | 121.0007 | 120.9686 | 0.3479 | -0.58136 | -0.086976 | -0.004578 | -0.20599 | 121.0052 | 120.7947 | 120.7993 | -0.27008 | 121.1014 | 120.9686 | 120.9 | -0.92926 | 121.344 | 121.2799 | 10.8444 | -121.5546
2269.6406 | 121.701 | -120.9412 | 0.59509 | 0.32395 | 0.0081682 | 0.017563 | 0.35755 | -0.057687 | -0.023017 | 0.043029 | 0.082718 | 3.2466 | 0.043443 | 0.078712 | 3.1587 | 0.080004 | 0.013733 | 0.068665 | -0.050354 | 0.050354 | 0.23804 | -0.14191 | -0.29297 | 0.068665 | -111.5295 | -0.16022 | 0.32959 | 0.30212 | -121.0464 | -120.9503 | 120.7993 | 120.6482 | -0.35706 | 121.0098 | 120.9915 | 0.34332 | -0.58136 | -0.10529 | -0.009155 | -0.2655 | 121.0098 | 120.7809 | 120.7901 | -0.29297 | 121.1792 | 120.9549 | 120.8908 | -0.88806 | 121.2708 | 121.2433 | 9.4116 | -121.5454
2270.6406 | 121.7056 | -120.9229 | 0.62256 | 0.20188 | 0.01244 | 0.020767 | 0.37357 | -0.059823 | -0.023017 | 0.050505 | 0.021682 | 3.2466 | 0.029557 | 0.080848 | 3.1641 | 0.091753 | 0.054932 | 0.10071 | -0.022888 | 0.068665 | 0.21515 | -0.12817 | -0.29755 | 0.09613 | -0.20599 | -0.10986 | 0.39368 | 0.33875 | -121.0556 | -120.9274 | 120.7947 | 120.6253 | -0.40741 | 121.0236 | 120.9915 | 0.36621 | -0.56763 | -0.13275 | -0.004577 | -0.22888 | 121.019 | 120.813 | 120.8176 | -0.28381 | 121.138 | 120.9778 | 120.9 | -0.9201 | 121.3165 | 121.2616 | 120.7169 | -121.55
2271.6406 | 121.7377 | -120.9503 | 0.59967 | -0.057515 | 0.028462 | 0.0047449 | 0.35114 | -0.063028 | -0.020881 | 0.038756 | -0.11565 | 3.2444 | 0.019944 | 0.092597 | 3.148 | 0.09389 | 0.07782 | 0.1236 | -0.013733 | 0.082397 | 0.24261 | -0.091553 | -0.25635 | 0.1236 | -0.1236 | -0.091553 | 0.39825 | 0.36163 | -121.0327 | -120.9274 | 120.8588 | 120.694 | -0.35706 | 121.0739 | 121.0327 | 0.33875 | -0.52185 | -0.082398 | 0.022888 | -0.20142 | 121.0739 | 120.8588 | 120.8359 | -0.23804 | 121.1929 | 121.0281 | 120.9366 | -0.85602 | 121.3486 | 121.3119 | 120.8267 | -121.5271
2272.6406 | 121.7285 | -120.932 | 0.62256 | 0.3087 | -0.0067858 | 0.014358 | 0.3725 | -0.063028 | -0.024085 | 0.025939 | -0.024094 | 3.237 | 0.032762 | 0.089393 | 3.1608 | 0.087481 | 0.045776 | 0.09613 | -0.018311 | 0.073242 | 0.23804 | -0.091553 | -0.2655 | 0.09613 | -0.11444 | -0.10986 | 0.39825 | 0.34332 | -121.0373 | -120.932 | 120.8405 | 120.6665 | -0.38452 | 121.0281 | 121.0052 | 0.33874 | -0.57678 | -0.10528 | 0 | -0.2243 | 121.0281 | 120.8221 | 120.8221 | -0.27924 | 121.17 | 120.9778 | 120.9137 | -0.88806 | 121.3303 | 121.2753 | 120.8176 | -121.5546
2273.6406 | 121.701 | -120.9457 | 0.60883 | 0.29344 | 0.0081682 | 0.00047294 | 0.37677 | -0.065164 | -0.020881 | 0.052642 | 0.25056 | 3.2551 | 0.019944 | 0.094733 | 3.1502 | 0.084276 | 0.022888 | 0.07782 | -0.045776 | 0.050354 | 0.21973 | -0.086975 | -0.2655 | 0.054932 | -0.79651 | -0.17395 | 0.39825 | 0.32959 | -121.0602 | -120.9366 | 120.8588 | 120.6802 | -0.3891 | 121.0236 | 120.9961 | 0.31586 | -0.58594 | -0.11444 | 0.009156 | -0.21057 | 121.0007 | 120.7718 | 120.7626 | -0.27924 | 121.1655 | 120.9686 | 120.9 | -0.87433 | 121.344 | 121.2753 | 120.1492 | -121.5454
2274.6406 | 121.6827 | -120.9549 | 0.6134 | 0.44602 | 0.032734 | -0.00059506 | 0.36289 | -0.064096 | -0.0080629 | 0.04196 | 0.15901 | 3.2594 | 0.03917 | 0.092597 | 3.1576 | 0.088549 | 0.036621 | 0.09613 | -0.050354 | 0.059509 | 0.22888 | -0.10529 | -0.26093 | 0.059509 | -0.11444 | -0.16022 | 0.37537 | 0.32501 | -121.0464 | -120.9457 | 120.8496 | 120.694 | -0.38452 | 121.051 | 121.0144 | 0.32043 | -0.57678 | -0.091553 | 0.009155 | -0.23804 | 121.0144 | 120.7947 | 120.7855 | -0.28839 | 121.1838 | 120.9915 | 120.9045 | -0.87433 | 121.3303 | 121.2799 | 120.8405 | -121.5591
2275.7031 | 121.6873 | -120.9686 | 0.54474 | 0.38499 | 0.018849 | 0.0036769 | 0.38104 | -0.060891 | -0.017676 | 0.038756 | 0.11323 | 3.254 | 0.03383 | 0.07978 | 3.1555 | 0.1003 | 0.009155 | 0.082397 | -0.050354 | 0.054932 | 0.23804 | -0.10071 | -0.27466 | -0.23804 | -0.10529 | -0.25635 | 0.3479 | 0.28381 | -121.1334 | -120.9961 | 120.8679 | 120.694 | -0.3067 | 121.051 | 121.0236 | 0.32959 | -0.53558 | -0.16479 | -0.027466 | -0.19684 | 120.7306 | 120.7123 | 120.7397 | -0.26093 | 121.2067 | 120.9778 | 120.9183 | -0.8194 | 121.3165 | 121.2524 | 120.8633 | -121.5408
2276.6406 | 121.7056 | -120.9641 | 0.60883 | -0.22536 | 0.0060322 | 0.017563 | 0.34366 | -0.064096 | -0.039039 | 0.048369 | -0.22246 | 3.2551 | 0.0081946 | 0.072303 | 3.1608 | 0.092821 | 0.07782 | 0.14648 | 0.022888 | 0.10071 | 0.20599 | -0.12817 | -0.29297 | 0.09613 | -0.022888 | -0.14648 | 0.39368 | 0.33875 | -121.0785 | -120.932 | 120.8359 | 120.6711 | -0.40283 | 121.1105 | 121.0648 | 0.39368 | -0.53101 | -0.11444 | 0.032043 | -0.21515 | 121.0602 | 120.8176 | 120.7855 | -0.27008 | 121.17 | 121.0419 | 120.9869 | -0.90179 | 121.3577 | 121.3028 | 120.9412 | -121.5408
2277.6406 | 121.7148 | -121.0098 | 0.55389 | 0.21714 | 0.018849 | 0.014358 | 0.37357 | -0.069436 | -0.014472 | 0.05371 | 0.067459 | 3.2508 | 0.05092 | 0.078712 | 3.1459 | 0.089617 | 0.009155 | 0.10071 | -0.054932 | 0.045776 | 0.2243 | -0.11902 | -0.2655 | -0.07782 | -0.42572 | -0.29297 | 0.37994 | 0.27924 | -121.1334 | -121.0144 | 120.8908 | 120.7443 | -0.32959 | 121.1105 | 121.0556 | 0.31128 | -0.54474 | -0.1236 | -0.004577 | -0.17395 | 120.932 | 120.7169 | 120.7214 | -0.27466 | 121.2341 | 121.019 | 120.9549 | -0.8194 | 121.3898 | 121.2891 | 120.5841 | -121.5683
2278.6406 | 121.6507 | -121.0007 | 0.6134 | 0.079814 | 0.056233 | -0.0070041 | 0.36075 | -0.049142 | 0.017572 | 0.063323 | 0.60152 | 3.2701 | 0.049852 | 0.095801 | 3.1779 | 0.087481 | 0.07782 | 0.086975 | -0.073242 | 0.12817 | 0.25635 | -0.13733 | -0.25635 | 0.059509 | -0.23804 | -0.24261 | 0.45319 | 0.36621 | -121.1014 | -120.9869 | 120.8633 | 120.7443 | -0.35706 | 121.0876 | 121.1288 | 0.38452 | -0.53558 | -0.10071 | 0.013733 | -0.16022 | 121.0602 | 120.7581 | 120.7443 | -0.24719 | 121.257 | 121.0785 | 120.9274 | -0.86975 | 121.4539 | 121.3669 | 120.7626 | -121.6003
2279.6406 | 121.6919 | -120.9869 | 0.59052 | 0.43077 | 0.014576 | 0.01329 | 0.36823 | -0.073709 | -0.017676 | 0.038756 | 0.20479 | 3.2615 | 0.037034 | 0.088325 | 3.1448 | 0.1035 | 0.027466 | 0.068665 | -0.059509 | 0.036621 | 0.24261 | -0.10071 | -0.28839 | 0.059509 | -2.3849 | -0.16479 | 0.40741 | 0.31586 | -121.0464 | -120.9366 | 120.8862 | 120.6985 | -0.3479 | 121.0556 | 121.0236 | 0.32501 | -0.56305 | -0.05951 | 0.050354 | -0.18311 | 121.0464 | 120.8221 | 120.7718 | -0.27466 | 121.2296 | 121.0144 | 120.9274 | -0.87891 | 121.3943 | 121.3028 | 118.602 | -121.5271
2280.6719 | 121.6278 | -121.0052 | 0.63629 | -0.24062 | 0.035939 | 0.0047449 | 0.36289 | -0.060891 | -0.0059269 | 0.048369 | -0.17668 | 3.2615 | 0.041307 | 0.096869 | 3.1512 | 0.08214 | 0.018311 | 0.07782 | -0.050354 | 0.032043 | 0.25177 | -0.14191 | -0.31128 | -0.004578 | -0.31586 | -0.24261 | 0.42114 | 0.37537 | -121.106 | -120.9915 | 120.8633 | 120.694 | -0.38452 | 121.0831 | 121.0373 | 0.34332 | -0.61798 | -0.10071 | 0.013733 | -0.21515 | 121.0007 | 120.7626 | 120.7489 | -0.26093 | 121.257 | 121.0236 | 120.9549 | -0.94757 | 121.4264 | 121.3806 | 120.6894 | -121.6278
2281.6406 | 121.6141 | -121.019 | 0.62714 | -0.22536 | 0.028462 | 0.00047294 | 0.36609 | -0.055551 | -0.011268 | 0.049437 | -0.2072 | 3.2594 | 0.034898 | 0.093665 | 3.1587 | 0.094958 | 0.027466 | 0.059509 | -0.045776 | 0.032043 | 0.25635 | -0.14191 | -0.29297 | 0 | -2.8198 | -0.26093 | 0.42572 | 0.35706 | -121.1014 | -120.9961 | 120.8771 | 120.726 | -0.37079 | 121.0785 | 121.051 | 0.32501 | -0.59967 | -0.082397 | 0.022888 | -0.20142 | 121.019 | 120.7581 | 120.7352 | -0.27008 | 121.2753 | 121.0464 | 120.9732 | -0.9201 | 121.4447 | 121.376 | 118.1992 | -121.6232
2282.6406 | 121.7056 | -121.0098 | 0.59509 | 0.18663 | 0.035939 | 0.016495 | 0.3725 | -0.069436 | -0.040107 | 0.039824 | 2.4478 | 3.2519 | 0.032762 | 0.073371 | 3.1534 | 0.090685 | 0.013733 | 0.082397 | -0.054932 | 0.059509 | 0.24261 | -0.11902 | -0.27466 | 0.050354 | -1.0757 | -0.16479 | 0.34332 | 0.28839 | -121.0785 | -120.9961 | 120.8908 | 120.7352 | -0.35248 | 121.0922 | 121.0693 | 0.33417 | -0.58136 | -0.068664 | 0.013733 | -0.25177 | 121.0602 | 120.845 | 120.8313 | -0.3067 | 121.2524 | 121.0236 | 120.9549 | -0.86975 | 121.3531 | 121.2982 | 119.9341 | -121.5912
2283.6406 | 121.7377 | -120.9641 | 0.58594 | -2.9872 | 0.026326 | -0.0048681 | 0.36823 | -0.059823 | -0.0027229 | 0.052642 | 0.25056 | 3.2455 | 0.023149 | 0.084052 | 3.1587 | 0.086413 | 0.045776 | 0.14191 | -0.013733 | 0.064087 | 0.17853 | -0.1236 | -0.27466 | 0.10986 | -3.479 | -0.1236 | 0.36163 | 0.33875 | -121.0602 | -120.9686 | 120.8405 | 120.6894 | -0.40741 | 121.106 | 121.0281 | 0.33875 | -0.54016 | -0.096131 | -0.004578 | -0.2243 | 121.0739 | 120.8405 | 120.845 | -0.24719 | 121.1426 | 121.0098 | 120.9503 | -0.86059 | 121.3257 | 121.3028 | 117.485 | -121.5546
2284.6406 | 121.701 | -120.9732 | 0.60883 | 0.43077 | 0.034871 | 0.012222 | 0.38532 | -0.058755 | -0.0091309 | 0.044097 | 0.35738 | 3.2487 | 0.028489 | 0.071235 | 3.1534 | 0.083208 | 0.091553 | 0.11902 | -0.018311 | 0.068665 | 0.22888 | -0.10986 | -0.25635 | 0.082397 | -4.2984 | -0.14648 | 0.39825 | 0.33417 | -121.0602 | -120.9641 | 120.8633 | 120.7169 | -0.37994 | 121.0922 | 121.0419 | 0.32501 | -0.51727 | -0.086975 | 0.009156 | -0.21057 | 121.0556 | 120.8267 | 120.8176 | -0.27466 | 121.2021 | 121.0648 | 120.9549 | -0.86517 | 121.3715 | 121.3074 | 116.6748 | -121.5729
2285.6406 | 121.7651 | -120.9595 | 0.60883 | -0.16433 | 0.016713 | 0.015426 | 0.35861 | -0.057687 | -0.013404 | 0.0067127 | -0.17668 | 3.254 | 0.044511 | 0.082984 | 3.1523 | 0.094958 | 0.22888 | -0.14648 | -0.10986 | 0.082397 | 0.21515 | -0.14648 | -0.28381 | 0.082397 | -1.3 | -0.12817 | 0.37994 | 0.34332 | -121.0785 | -120.9595 | 120.813 | 120.6757 | -0.39368 | 120.813 | 121.0419 | 0.36621 | -0.37994 | -0.11902 | 0 | -0.22888 | 121.0419 | 120.8313 | 120.8313 | -0.2655 | 121.1746 | 121.1884 | 120.8496 | -0.89264 | 121.3394 | 121.3028 | 119.6594 | -121.5683
2286.6406 | 121.6919 | -120.9869 | 0.61798 | -0.011739 | 0.020985 | 0.010086 | 0.36609 | -0.053415 | -0.012336 | 0.03662 | -0.34453 | 3.2498 | 0.03383 | 0.06803 | 3.1619 | 0.078936 | 0.07782 | 0.13275 | 0.009155 | 0.086975 | 0.21057 | -0.10071 | -0.29297 | 0.050354 | -1.1169 | -0.15564 | 0.3891 | 0.34332 | -121.106 | -120.9961 | 120.8862 | 120.694 | -0.40741 | 121.1197 | 121.0739 | 0.37994 | -0.54016 | -0.11902 | -0.009156 | -0.22888 | 121.0373 | 120.8313 | 120.8405 | -0.27466 | 121.1975 | 121.0648 | 120.9961 | -0.91095 | 121.376 | 121.3303 | 119.87 | -121.6141
2287.6406 | 121.701 | -120.9915 | 0.59967 | 0.41551 | 0.056233 | 0.012222 | 0.36395 | -0.057687 | -0.020881 | 0.038756 | 0.34212 | 3.2562 | 0.014604 | 0.089393 | 3.1491 | 0.091753 | 0.073242 | 0.12817 | -0.022888 | 0.068665 | 0.21973 | -0.10071 | -0.26093 | 0.10071 | -107.8354 | -0.16022 | 0.39368 | 0.32959 | -121.0785 | -120.9915 | 120.8908 | 120.7306 | -0.37994 | 121.1197 | 121.0602 | 0.32959 | -0.52643 | -0.086975 | 0 | -0.20599 | 121.0922 | 120.8313 | 120.8313 | -0.27008 | 121.2112 | 121.0648 | 120.9686 | -0.86059 | 121.3852 | 121.3211 | 13.1561 | -121.5912
2288.6406 | 121.7331 | -120.9595 | 0.59967 | 0.44602 | 0.028462 | 0.017563 | 0.35541 | -0.063028 | -0.014472 | 0.047301 | 0.38789 | 3.2519 | 0.034898 | 0.084052 | 3.1598 | 0.089617 | 0.086975 | 0.11902 | -0.013733 | 0.07782 | 0.22888 | -0.10529 | -0.26093 | 0.10529 | -0.48523 | -0.12817 | 0.37994 | 0.33417 | -121.0693 | -120.9824 | 120.8542 | 120.6985 | -0.37079 | 121.0785 | 121.0373 | 0.33875 | -0.5127 | -0.10986 | -0.022888 | -0.21973 | 121.0648 | 120.8313 | 120.8542 | -0.2655 | 121.1884 | 121.0464 | 120.9457 | -0.86059 | 121.3394 | 121.2936 | 120.4742 | -121.582
2289.6406 | 121.7056 | -120.9915 | 0.60883 | 0.52232 | 0.020985 | -0.0059361 | 0.38318 | -0.051278 | -0.0048589 | 0.03662 | 0.26582 | 3.2583 | 0.03917 | 0.075507 | 3.1406 | 0.090685 | 0.073242 | 0.10071 | -0.041199 | 0.054932 | 0.23804 | -0.11444 | -0.24261 | 0.082397 | -0.61798 | -0.16479 | 0.40741 | 0.34332 | -121.0739 | -120.9824 | 120.8771 | 120.7489 | -0.37079 | 121.0922 | 121.0464 | 0.29755 | -0.53558 | -0.082398 | 0.009155 | -0.20142 | 121.0739 | 120.8267 | 120.8176 | -0.2655 | 121.2296 | 121.0648 | 120.9503 | -0.85144 | 121.3989 | 121.3348 | 120.3735 | -121.5912
2290.6406 | 121.7422 | -120.9824 | 0.59509 | 0.61387 | 0.042347 | -0.0059361 | 0.37891 | -0.071573 | 0.0047541 | 0.043029 | 0.14375 | 3.2583 | 0.041307 | 0.084052 | 3.163 | 0.087481 | 0.10071 | 0.068665 | -0.059509 | 0.064087 | 0.22888 | -0.1236 | -0.28839 | 0.1236 | -1.9363 | -0.15564 | 0.36621 | 0.32044 | -121.0831 | -120.9457 | 120.8588 | 120.694 | -0.36621 | 121.051 | 121.0464 | 0.35248 | -0.49438 | -0.10071 | 0.036621 | -0.22888 | 121.106 | 120.8267 | 120.7901 | -0.27466 | 121.2112 | 121.0831 | 120.9229 | -0.88348 | 121.3486 | 121.3028 | 119.046 | -121.5408
2291.6719 | 121.7834 | -120.9686 | 0.60883 | 0.095073 | 0.019917 | 0.011154 | 0.35114 | -0.071573 | -0.029426 | 0.039824 | -0.37505 | 3.254 | 0.03383 | 0.089393 | 3.1395 | 0.098162 | 0.073242 | 0.18768 | 0.045776 | 0.07782 | 0.21973 | -0.10529 | -0.25635 | 0.10071 | -1.0345 | -0.11444 | 0.38452 | 0.32501 | -121.0648 | -120.9732 | 120.8633 | 120.7123 | -0.3891 | 121.1563 | 121.0464 | 0.33417 | -0.53558 | -0.09613 | -0.004578 | -0.2243 | 121.0693 | 120.8542 | 120.8588 | -0.28381 | 121.1884 | 121.0419 | 121.0144 | -0.86517 | 121.3531 | 121.2936 | 119.9341 | -121.582
2292.6406 | 121.7514 | -121.0007 | 0.59967 | 3.2384 | 0.061574 | 0.016495 | 0.37036 | -0.070504 | -0.013404 | 0.051574 | 0.44893 | 3.2594 | 0.038102 | 0.086188 | 3.1587 | 0.094958 | 0.16479 | 0.07782 | -0.004578 | 0.082397 | 0.17395 | -0.13733 | -0.28839 | 0.10986 | -5.9006 | -0.14648 | 0.39368 | 0.33875 | -121.0831 | -120.9869 | 120.8633 | 120.7123 | -0.42572 | 121.0785 | 121.0831 | 0.37079 | -0.43488 | -0.082398 | 0.013733 | -0.20599 | 121.1105 | 120.8542 | 120.8405 | -0.26093 | 121.1746 | 121.1655 | 120.9961 | -0.88806 | 121.3943 | 121.3394 | 115.1001 | -121.5866
2293.6406 | 121.7514 | -120.9915 | 0.59967 | 0.61387 | 0.06371 | 0.0036769 | 0.38318 | -0.058755 | 0.0058221 | 0.038756 | 0.40315 | 3.2626 | 0.042375 | 0.086188 | 3.1694 | 0.083208 | 0.10071 | 0.091553 | -0.054932 | 0.07782 | 0.22888 | -0.11902 | -0.25635 | 0.11444 | -6.2256 | -0.14648 | 0.37537 | 0.31586 | -121.0739 | -120.9869 | 120.8725 | 120.7352 | -0.37079 | 121.0831 | 121.0693 | 0.33417 | -0.49896 | -0.082398 | 0.004578 | -0.2243 | 121.106 | 120.845 | 120.8405 | -0.28381 | 121.2204 | 121.0922 | 120.9366 | -0.85602 | 121.3669 | 121.3074 | 114.7659 | -121.5866
2294.6406 | 121.669 | -121.0464 | 0.62256 | -3.4907 | 0.058369 | -0.00059506 | 0.37143 | -0.071573 | 0.0090271 | 0.061187 | 0.021682 | 3.2572 | 0.05092 | 0.086188 | 3.1673 | 0.077868 | -0.022888 | 0.022888 | -0.14191 | -0.013733 | 0.25177 | -0.14191 | -0.28839 | 0.022888 | -5.6122 | -0.24719 | 0.40283 | 0.33875 | -121.1334 | -121.0236 | 120.9045 | 120.7581 | -0.37079 | 121.0693 | 121.0327 | 0.27466 | -0.64545 | -0.086975 | 0.022888 | -0.21973 | 121.0693 | 120.7993 | 120.7764 | -0.28381 | 121.2982 | 121.0236 | 120.9045 | -0.91095 | 121.4493 | 121.3852 | 115.4343 | -121.6461
2295.6406 | 121.6919 | -121.0373 | 0.59967 | 0.58335 | 0.045552 | -0.0027321 | 0.35861 | -0.063028 | 0.0090271 | 0.054778 | 0.35738 | 3.2551 | 0.042375 | 0.088325 | 3.1715 | 0.084276 | 0.027466 | 0.009155 | -0.12817 | 0.004578 | 0.25177 | -0.13275 | -0.27466 | 0.045776 | -0.94757 | -0.21057 | 0.39368 | 0.32959 | -121.1197 | -121.0098 | 120.9045 | 120.7626 | -0.3479 | 121.0464 | 121.0419 | 0.27924 | -0.5722 | -0.082398 | 0.027465 | -0.20599 | 121.0831 | 120.8267 | 120.7993 | -0.27008 | 121.2891 | 121.0648 | 120.9091 | -0.87433 | 121.431 | 121.3669 | 120.0897 | -121.6095
2296.7031 | 121.7697 | -120.9961 | 0.60883 | 0.14085 | 0.050892 | 0.014358 | 0.36609 | -0.068368 | -0.039039 | 0.051574 | 0.067459 | 3.2423 | 0.042375 | 0.073371 | 3.1438 | 0.09923 | 0.045776 | 0.082397 | -0.004578 | 0.07782 | 0.24261 | -0.09613 | -0.26093 | 0.086975 | -116.0568 | -0.11444 | 0.38452 | 0.34332 | -121.0739 | -120.9869 | 120.9 | 120.7352 | -0.36621 | 121.0785 | 121.0739 | 0.33875 | -0.56305 | -0.07782 | 0.009156 | -0.2243 | 121.0831 | 120.8817 | 120.8725 | -0.2655 | 121.2387 | 121.0419 | 120.9915 | -0.86975 | 121.3806 | 121.3394 | 4.9393 | -121.5958
2297.6406 | 121.6232 | -121.051 | 0.61798 | 0.27818 | 0.070118 | -0.0016631 | 0.38211 | -0.051278 | 0.010095 | 0.060118 | 0.32686 | 3.2647 | 0.05092 | 0.082984 | 3.1747 | 0.083208 | 0.041199 | -0.059509 | -0.17395 | 0.009155 | 0.24719 | -0.14648 | -0.31128 | -0.013733 | -116.1575 | -0.2655 | 0.40741 | 0.37079 | -121.1609 | -121.0236 | 120.9045 | 120.7397 | -0.37079 | 120.9915 | 121.0602 | 0.32043 | -0.57678 | -0.10986 | 0.027465 | -0.21057 | 121.0373 | 120.7855 | 120.7581 | -0.24719 | 121.2982 | 121.0922 | 120.8771 | -0.92926 | 121.4584 | 121.4218 | 4.8935 | -121.6415
2298.6406 | 121.6873 | -121.051 | 0.64545 | 0.47654 | 0.073323 | 0.0026089 | 0.3725 | -0.052346 | 0.0015501 | 0.062255 | 0.2353 | 3.2679 | 0.038102 | 0.10435 | 3.1608 | 0.088549 | 0.022888 | -0.036621 | -0.16022 | -0.004578 | 0.27008 | -0.13733 | -0.29297 | 0.16022 | -117.6682 | -0.15564 | 0.4303 | 0.37994 | -121.1288 | -120.9778 | 120.9137 | 120.7581 | -0.37537 | 121.0144 | 121.0464 | 0.28839 | -0.62256 | -0.07782 | 0.073242 | -0.21515 | 121.2112 | 120.8954 | 120.8221 | -0.2655 | 121.3211 | 121.0739 | 120.8908 | -0.93842 | 121.4813 | 121.431 | 3.3829 | -121.6232
2299.6406 | 121.6736 | -121.019 | 0.6134 | 0.55284 | 0.092549 | -0.0080721 | 0.39493 | -0.055551 | 0.00048206 | 0.050505 | 0.20479 | 3.2637 | 0.040239 | 0.095801 | 3.1641 | 0.087481 | 0.018311 | -0.036621 | -0.17853 | 0 | 0.27008 | -0.1236 | -0.27924 | -0.004578 | -117.7094 | -0.24261 | 0.41199 | 0.37079 | -121.1243 | -121.019 | 120.8954 | 120.7397 | -0.34332 | 120.9824 | 121.019 | 0.27924 | -0.59509 | -0.10529 | 0 | -0.20142 | 121.0144 | 120.7764 | 120.7764 | -0.24261 | 121.2891 | 121.0373 | 120.8405 | -0.89264 | 121.431 | 121.3898 | 3.3096 | -121.6324
2300.6875 | 121.7789 | -120.9778 | 0.61798 | 0.15611 | 0.014576 | 0.026108 | 0.34793 | -0.066232 | -0.045447 | 0.037688 | 0.15901 | 3.2487 | 0.012468 | 0.086188 | 3.1427 | 0.1035 | 0.041199 | 0.10071 | -0.022888 | 0.082397 | 0.23346 | -0.10071 | -0.27466 | 0.07782 | -3.0762 | -0.091553 | 0.40741 | 0.34332 | -121.0785 | -120.9778 | 120.8771 | 120.7031 | -0.38452 | 121.0785 | 121.0602 | 0.35706 | -0.57678 | -0.10071 | 0 | -0.21057 | 121.0556 | 120.8862 | 120.8862 | -0.27466 | 121.2112 | 121.019 | 120.9549 | -0.89264 | 121.3852 | 121.3211 | 117.9016 | -121.5958
2301.6406 | 121.6415 | -121.0693 | 0.6134 | 0.29344 | 0.085072 | 0.0036769 | 0.36716 | -0.047006 | 0.0090271 | 0.048369 | 0.021682 | 3.2562 | 0.03917 | 0.084052 | 3.1651 | 0.083208 | 0.018311 | -0.009155 | -0.12817 | 0.004578 | 0.25177 | -0.16479 | -0.31586 | -0.027466 | -2.449 | -0.27466 | 0.39368 | 0.34332 | -121.1792 | -121.0236 | 120.9045 | 120.7535 | -0.36163 | 121.0602 | 121.0739 | 0.32044 | -0.59509 | -0.10986 | 0.045776 | -0.21973 | 121.0419 | 120.7947 | 120.7489 | -0.27008 | 121.3211 | 121.0876 | 120.9412 | -0.92926 | 121.463 | 121.4127 | 118.6203 | -121.637
2302.6406 | 121.6736 | -121.0419 | 0.59967 | 0.12559 | 0.057301 | 0.0068819 | 0.36502 | -0.066232 | 0.013299 | 0.044097 | -0.06987 | 3.2722 | 0.058397 | 0.082984 | 3.1566 | 0.078936 | 0.013733 | 0.004578 | -0.11902 | 0.018311 | 0.23804 | -0.13275 | -0.31128 | -0.022888 | -1.5472 | -0.27466 | 0.40283 | 0.34332 | -121.1563 | -121.0602 | 120.9091 | 120.7306 | -0.36163 | 121.0464 | 121.0602 | 0.32959 | -0.58594 | -0.11444 | -0.018311 | -0.19684 | 121.019 | 120.7672 | 120.7855 | -0.25635 | 121.2799 | 121.0556 | 120.9229 | -0.91095 | 121.4447 | 121.3852 | 119.4946 | -121.6599
2303.6406 | 121.6461 | -121.0464 | 0.62256 | 0.17137 | 0.073323 | -0.0038001 | 0.36502 | -0.069436 | 0.012231 | 0.05371 | 0.0522 | 3.2637 | 0.047715 | 0.089393 | 3.1651 | 0.098162 | -0.027466 | -0.027466 | -0.14648 | 0 | 0.24719 | -0.16937 | -0.30212 | -0.045776 | -1.7624 | -0.28381 | 0.41657 | 0.36621 | -121.17 | -121.0373 | 120.8771 | 120.7443 | -0.37537 | 121.019 | 121.0464 | 0.30212 | -0.65002 | -0.1236 | 0.009156 | -0.20599 | 121.0007 | 120.7626 | 120.7535 | -0.25635 | 121.2936 | 121.019 | 120.9 | -0.92468 | 121.463 | 121.4127 | 119.2841 | -121.6599
2304.6406 | 121.6461 | -121.051 | 0.62256 | 0.049296 | 0.056233 | -0.0048681 | 0.37784 | -0.059823 | 0.0068901 | 0.051574 | 0.26582 | 3.2615 | 0.049852 | 0.094733 | 3.163 | 0.085345 | -0.045776 | -0.045776 | -0.17395 | 0 | 0.24261 | -0.1236 | -0.31586 | -0.032043 | -2.6321 | -0.2655 | 0.42114 | 0.36163 | -121.1563 | -121.0327 | 120.9274 | 120.7352 | -0.37994 | 121.0052 | 121.051 | 0.31586 | -0.66834 | -0.10529 | 0.01831 | -0.20142 | 121.019 | 120.7855 | 120.7672 | -0.26093 | 121.2936 | 121.0052 | 120.8771 | -0.93842 | 121.4722 | 121.4127 | 118.4189 | -121.6553
2305.6406 | 121.7834 | -121.0007 | 0.62256 | -0.43899 | 0.011372 | 0.03038 | 0.36395 | -0.065164 | -0.056128 | 0.035552 | 0.35738 | 3.2444 | 0.021012 | 0.090461 | 3.1459 | 0.098162 | -0.027466 | 0.059509 | -0.027466 | 0.064087 | 0.20142 | -0.11902 | -0.28381 | 0.027466 | -1.0483 | -0.11902 | 0.39825 | 0.33875 | -121.106 | -120.9961 | 120.8817 | 120.7169 | -0.42114 | 121.0602 | 121.0648 | 0.3479 | -0.65002 | -0.10529 | 0.004577 | -0.2243 | 121.0281 | 120.8817 | 120.8771 | -0.28381 | 121.2021 | 120.9732 | 120.9732 | -0.90637 | 121.3989 | 121.3394 | 119.9524 | -121.6187
2306.6406 | 121.6553 | -121.0739 | 0.63171 | 0.26292 | 0.067982 | -0.0091401 | 0.37998 | -0.0673 | 0.0036861 | 0.045165 | 0.18953 | 3.2551 | 0.038102 | 0.094733 | 3.1705 | 0.081072 | 0.013733 | -0.027466 | -0.15106 | -0.009155 | 0.23346 | -0.12817 | -0.32044 | -0.050354 | -2.5955 | -0.28381 | 0.41199 | 0.3479 | -121.1426 | -121.0785 | 120.9457 | 120.7535 | -0.39826 | 121.0464 | 121.0648 | 0.31128 | -0.61798 | -0.068664 | -0.004577 | -0.21973 | 121.0236 | 120.7901 | 120.7947 | -0.28381 | 121.3074 | 121.0876 | 120.9229 | -0.95215 | 121.4859 | 121.4218 | 118.4784 | -121.7102
2307.6406 | 121.6599 | -121.051 | 0.6134 | 0.17137 | 0.066914 | -0.0027321 | 0.36823 | -0.056619 | 0.014367 | 0.050505 | -0.0088351 | 3.2551 | 0.048783 | 0.08512 | 3.1534 | 0.0768 | 0.022888 | 0.009155 | -0.11444 | 0 | 0.23804 | -0.13733 | -0.31586 | -0.036621 | -1.1124 | -0.2655 | 0.40283 | 0.35248 | -121.1655 | -121.0556 | 120.9137 | 120.7352 | -0.37537 | 121.0602 | 121.051 | 0.31586 | -0.59052 | -0.11444 | -0.004578 | -0.21057 | 121.0144 | 120.7855 | 120.7901 | -0.26093 | 121.2891 | 121.0739 | 120.9366 | -0.92926 | 121.4539 | 121.4035 | 119.9387 | -121.669
2308.6875 | 121.6553 | -121.0098 | 0.66834 | -0.33217 | 0.054097 | 0.0015409 | 0.36823 | -0.060891 | -0.030494 | 0.050505 | -0.32927 | 3.2572 | 0.040239 | 0.084052 | 3.1438 | 0.091753 | -0.032043 | 0.009155 | -0.09613 | 0.013733 | 0.2655 | -0.13275 | -0.30212 | -0.009155 | -3.6072 | -0.19226 | 0.46234 | 0.42572 | -121.0968 | -121.0327 | 120.8771 | 120.7077 | -0.40283 | 121.019 | 121.0236 | 0.31586 | -0.70038 | -0.086975 | -0.022888 | -0.20599 | 121.0007 | 120.8176 | 120.8405 | -0.24262 | 121.2753 | 120.9778 | 120.9137 | -0.97046 | 121.4722 | 121.4355 | 117.4026 | -121.701
2309.6406 | 121.701 | -121.0648 | 0.62714 | -0.2864 | 0.064778 | -0.0091401 | 0.37784 | -0.054483 | 0.0036861 | 0.052642 | -0.054612 | 3.2669 | 0.045579 | 0.072303 | 3.1512 | 0.077868 | 0.050354 | 0.027466 | -0.068665 | 0.036621 | 0.26093 | -0.14191 | -0.29755 | 0.013733 | -4.1061 | -0.2243 | 0.41199 | 0.37079 | -121.1517 | -121.0327 | 120.9229 | 120.7672 | -0.36621 | 121.0922 | 121.1014 | 0.33417 | -0.57678 | -0.086975 | 0.032043 | -0.21515 | 121.0785 | 120.8405 | 120.8084 | -0.25635 | 121.3257 | 121.1151 | 120.9961 | -0.92468 | 121.4767 | 121.4355 | 116.9586 | -121.6599
2310.6719 | 121.7651 | -121.0007 | 0.59052 | -0.51528 | 0.031666 | 0.010086 | 0.35755 | -0.070504 | -0.026221 | 0.03662 | 0.47945 | 3.2508 | 0.028489 | 0.080848 | 3.1448 | 0.09923 | 0.036621 | 0.10986 | -0.009155 | 0.068665 | 0.20142 | -0.10986 | -0.25177 | 0.07782 | -3.3142 | -0.1236 | 0.38452 | 0.33875 | -121.0922 | -121.0007 | 120.8908 | 120.7489 | -0.3891 | 121.1105 | 121.0693 | 0.32044 | -0.55389 | -0.091553 | 0 | -0.20599 | 121.0785 | 120.8771 | 120.8771 | -0.25177 | 121.2021 | 121.0373 | 120.9915 | -0.84228 | 121.3852 | 121.3394 | 117.6865 | -121.5912
2311.6406 | 121.6919 | -121.0098 | 0.66834 | 0.11033 | 0.057301 | -0.0070041 | 0.36716 | -0.059823 | 0.0058221 | 0.038756 | -0.17668 | 3.2444 | 0.054124 | 0.088325 | 3.1576 | 0.10671 | 0.054932 | 0.064087 | -0.073242 | 0.041199 | 0.23346 | -0.12817 | -0.29297 | 0.24719 | -6.4774 | -0.17395 | 0.46234 | 0.41657 | -121.1014 | -121.0236 | 120.8817 | 120.7169 | -0.43488 | 121.0739 | 121.051 | 0.33417 | -0.6134 | -0.091552 | -0.013733 | -0.20599 | 121.257 | 120.8359 | 120.8496 | -0.25177 | 121.2433 | 121.0648 | 120.9366 | -0.9613 | 121.4722 | 121.4264 | 114.5325 | -121.6919
2312.6406 | 121.6553 | -121.051 | 0.63171 | 0.2324 | 0.062642 | -0.0038001 | 0.36502 | -0.072641 | 0.015435 | 0.045165 | -0.039353 | 3.269 | 0.055192 | 0.091529 | 3.1448 | 0.086413 | -0.013733 | -0.018311 | -0.15106 | -0.009155 | 0.22888 | -0.15106 | -0.31128 | -0.064087 | -4.5273 | -0.27466 | 0.39825 | 0.37079 | -121.1517 | -121.0648 | 120.9 | 120.7397 | -0.40283 | 121.0327 | 121.0419 | 0.30212 | -0.64545 | -0.10071 | -0.013733 | -0.23346 | 120.9869 | 120.7764 | 120.7901 | -0.26093 | 121.2799 | 121.0373 | 120.9 | -0.94299 | 121.4493 | 121.4218 | 116.5237 | -121.6965
2313.6406 | 121.669 | -121.0693 | 0.60883 | 0.21714 | 0.061574 | -0.011276 | 0.37784 | -0.073709 | 0.0079581 | 0.057982 | 0.067459 | 3.253 | 0.055192 | 0.093665 | 3.1651 | 0.078936 | -0.004578 | 0.004578 | -0.10986 | 0.004578 | 0.24719 | -0.15564 | -0.32501 | -0.045776 | -3.2684 | -0.28381 | 0.39368 | 0.36163 | -121.1838 | -121.0602 | 120.9137 | 120.7443 | -0.36163 | 121.0739 | 121.0739 | 0.32959 | -0.6134 | -0.11444 | 0.009155 | -0.21515 | 121.0236 | 120.7855 | 120.7764 | -0.24719 | 121.3165 | 121.0648 | 120.9595 | -0.93384 | 121.463 | 121.431 | 117.8009 | -121.669
2314.6562 | 121.7514 | -121.0236 | 0.60425 | 0.47654 | 0.044484 | -0.0027321 | 0.36609 | -0.064096 | -0.035834 | 0.04196 | 0.55574 | 3.2487 | 0.047715 | 0.078712 | 3.1373 | 0.10243 | 0.032043 | 0.10529 | -0.032043 | 0.07782 | 0.21973 | -0.091553 | -0.25177 | 0.064087 | -3.5477 | -0.15106 | 0.40283 | 0.35706 | -121.1151 | -120.9961 | 120.932 | 120.7718 | -0.38452 | 121.1288 | 121.1014 | 0.32959 | -0.5722 | -0.091552 | 0.027466 | -0.20142 | 121.0876 | 120.8725 | 120.845 | -0.24719 | 121.2433 | 121.0556 | 120.9915 | -0.85602 | 121.4264 | 121.3806 | 117.4759 | -121.6003
2315.6406 | 121.6553 | -121.0602 | 0.63171 | 0.36973 | 0.059437 | 0.0015409 | 0.37784 | -0.066232 | 0.0090271 | 0.051574 | 0.18953 | 3.2508 | 0.059465 | 0.090461 | 3.1544 | 0.081072 | -0.027466 | -0.036621 | -0.16937 | 0.009155 | 0.2655 | -0.13275 | -0.29755 | -0.041199 | -3.9871 | -0.27924 | 0.41657 | 0.37079 | -121.1975 | -121.0373 | 120.9274 | 120.7626 | -0.36621 | 121.0236 | 121.0693 | 0.3067 | -0.65918 | -0.13733 | 0.022889 | -0.21515 | 121.019 | 120.7809 | 120.7581 | -0.26093 | 121.3257 | 121.0327 | 120.8908 | -0.92926 | 121.4767 | 121.431 | 117.0731 | -121.669
2316.6562 | 121.7789 | -121.0144 | 0.56305 | 0.59861 | 0.054097 | 0.010086 | 0.37464 | -0.063028 | -0.023017 | 0.039824 | 3.1955 | 3.253 | 0.047715 | 0.090461 | 3.1523 | 0.083208 | 0.064087 | 0.10529 | -0.041199 | 0.082397 | 0.21515 | -0.086975 | -0.26093 | 0.032043 | -2.2476 | -0.16022 | 0.36163 | 0.31128 | -121.106 | -120.9961 | 120.9274 | 120.7535 | -0.3479 | 121.1197 | 121.0968 | 0.34332 | -0.49896 | -0.091553 | 0.01831 | -0.20142 | 121.0464 | 120.8542 | 120.8359 | -0.25177 | 121.2296 | 121.0785 | 120.9732 | -0.82397 | 121.376 | 121.3257 | 118.7668 | -121.5591
2317.6406 | 121.7102 | -121.0693 | 0.61798 | 0.034038 | 0.043416 | -0.0080721 | 0.36502 | -0.0673 | 0.0015501 | 0.049437 | -0.2072 | 3.2583 | 0.030626 | 0.096869 | 3.1566 | 0.087481 | 0.059509 | 0.041199 | -0.082397 | 0.041199 | 0.27466 | -0.12817 | -0.29755 | 0.032043 | -3.1815 | -0.22888 | 0.41199 | 0.37537 | -121.1288 | -121.0464 | 120.9412 | 120.7718 | -0.34332 | 121.1105 | 121.1105 | 0.33874 | -0.55847 | -0.059509 | 0.022888 | -0.20599 | 121.1014 | 120.8405 | 120.8176 | -0.24262 | 121.344 | 121.1288 | 120.9869 | -0.91553 | 121.4813 | 121.4447 | 117.8879 | -121.6644
2318.6406 | 121.7102 | -121.0327 | 0.61798 | -0.2101 | 0.038075 | 0.014358 | 0.36823 | -0.059823 | 0.00048206 | 0.038756 | -0.2072 | 3.2626 | 0.044511 | 0.090461 | 3.1576 | 0.089617 | 0.032043 | 0.036621 | -0.068665 | 0.041199 | 0.25177 | -0.14648 | -0.29297 | 0 | -5.5252 | -0.21973 | 0.41199 | 0.37537 | -121.1472 | -121.0236 | 120.8862 | 120.7397 | -0.36621 | 121.0693 | 121.0739 | 0.33417 | -0.58594 | -0.11444 | 0.009155 | -0.20599 | 121.0327 | 120.813 | 120.8038 | -0.24262 | 121.2845 | 121.0648 | 120.9641 | -0.91095 | 121.4447 | 121.4081 | 115.5075 | -121.6415
2319.6406 | 121.6827 | -121.0648 | 0.63171 | -0.17959 | 0.038075 | 0.0058129 | 0.3757 | -0.055551 | -0.0091309 | 0.043029 | 0.81514 | 3.254 | 0.062669 | 0.094733 | 3.148 | 0.090685 | -0.041199 | 0.27008 | 0.091553 | 0.086975 | 0.29297 | -0.1236 | -0.26093 | -0.032043 | -2.6871 | -0.25635 | 0.4303 | 0.3891 | -121.1746 | -121.0602 | 120.9412 | 120.8038 | -0.33875 | 121.3348 | 121.1517 | 0.3479 | -0.67291 | -0.10986 | 0.004577 | -0.20142 | 121.0327 | 120.8084 | 120.8038 | -0.24262 | 121.3577 | 121.0236 | 121.1563 | -0.89264 | 121.4951 | 121.4539 | 118.3777 | -121.6919
2320.6406 | 121.6461 | -121.0785 | 0.62256 | 0.26292 | 0.065846 | 0.011154 | 0.37036 | -0.056619 | -0.0016549 | 0.049437 | 0.29634 | 3.2519 | 0.048783 | 0.091529 | 3.1502 | 0.091753 | -0.041199 | -0.041199 | -0.15564 | 0.004578 | 0.25177 | -0.14191 | -0.31586 | -0.032043 | -2.6184 | -0.2655 | 0.41657 | 0.37079 | -121.1746 | -121.051 | 120.9366 | 120.7626 | -0.37079 | 121.0373 | 121.0831 | 0.32044 | -0.66376 | -0.096131 | 0.027466 | -0.20599 | 121.0464 | 120.813 | 120.7855 | -0.25177 | 121.3303 | 121.0373 | 120.9229 | -0.93842 | 121.4951 | 121.4493 | 118.4601 | -121.6736
2321.6406 | 121.7194 | -121.0602 | 0.61798 | 0.064555 | 0.065846 | 0.0026089 | 0.38318 | -0.063028 | -0.012336 | 0.044097 | -0.29875 | 3.2551 | 0.054124 | 0.092597 | 3.148 | 0.081072 | -0.022888 | 0.009155 | -0.086975 | 0.022888 | 0.24719 | -0.14191 | -0.29297 | -0.022888 | -5.571 | -0.23804 | 0.40283 | 0.35706 | -121.1472 | -121.0373 | 120.9183 | 120.7672 | -0.37079 | 121.0693 | 121.0831 | 0.31586 | -0.64087 | -0.086975 | 0.022889 | -0.21515 | 121.0373 | 120.8221 | 120.7993 | -0.26093 | 121.3074 | 121.0373 | 120.9732 | -0.91095 | 121.463 | 121.4172 | 115.4892 | -121.6553
2322.6406 | 121.6965 | -121.0739 | 0.64087 | -0.22536 | 0.02953 | 0.0047449 | 0.36502 | -0.057687 | -0.034766 | 0.033416 | -0.29875 | 3.2572 | 0.048783 | 0.091529 | 3.1341 | 0.091753 | -0.009155 | 0.086975 | -0.041199 | 0.050354 | 0.25177 | -0.11444 | -0.28381 | -0.022888 | -3.0258 | -0.21057 | 0.41657 | 0.37994 | -121.1884 | -121.0373 | 120.9595 | 120.7901 | -0.3891 | 121.1609 | 121.1243 | 0.33417 | -0.65002 | -0.11444 | 0.036622 | -0.2243 | 121.051 | 120.8633 | 120.8267 | -0.26093 | 121.3257 | 121.0648 | 121.0327 | -0.92468 | 121.4905 | 121.4539 | 118.0481 | -121.6782
2323.6406 | 121.7789 | -121.0281 | 0.62256 | -0.45424 | 0.030598 | 0.0058129 | 0.36182 | -0.068368 | -0.024085 | 0.037688 | -0.23772 | 3.2466 | 0.021012 | 0.093665 | 3.1459 | 0.083208 | 0.018311 | 0.14191 | -0.004578 | 0.091553 | 0.23804 | -0.11444 | -0.25635 | 0.004578 | -0.59052 | -0.16937 | 0.39825 | 0.37079 | -121.1334 | -121.0236 | 120.9137 | 120.7718 | -0.38452 | 121.17 | 121.1197 | 0.3479 | -0.60425 | -0.10529 | 0.004577 | -0.2243 | 121.0327 | 120.8588 | 120.8542 | -0.25177 | 121.2662 | 121.0464 | 121.0236 | -0.87891 | 121.4264 | 121.3989 | 120.4376 | -121.6461
2324.6406 | 121.6919 | -121.0785 | 0.61798 | -0.43899 | 0.016713 | 0.010086 | 0.36182 | -0.063028 | -0.017676 | 0.033416 | -0.37505 | 3.2466 | 0.037034 | 0.087256 | 3.1491 | 0.081072 | -0.036621 | -0.009155 | -0.086975 | -0.009155 | 0.26093 | -0.15106 | -0.29755 | -0.045776 | -2.2339 | -0.22888 | 0.42114 | 0.37537 | -121.1929 | -121.0327 | 120.9274 | 120.7809 | -0.35706 | 121.0693 | 121.0693 | 0.28839 | -0.6546 | -0.11444 | 0.045776 | -0.19684 | 121.0327 | 120.8496 | 120.8038 | -0.24262 | 121.3394 | 121.0419 | 120.9915 | -0.91553 | 121.4996 | 121.4539 | 118.8446 | -121.6507
2325.6406 | 121.6782 | -121.0648 | 0.6134 | 0.11033 | 0.055165 | -0.040116 | 0.38959 | -0.061959 | 0.0079581 | 0.047301 | 0.25056 | 3.2583 | 0.053056 | 0.096869 | 3.1416 | 0.078936 | -0.022888 | -0.068665 | -0.1831 | 0.004578 | 0.27466 | -0.14648 | -0.29755 | -0.018311 | -1.0254 | -0.27924 | 0.42572 | 0.37994 | -121.1792 | -121.0648 | 120.9183 | 120.7672 | -0.33875 | 120.9961 | 121.0693 | 0.30212 | -0.63629 | -0.11444 | 0 | -0.18768 | 121.0464 | 120.7855 | 120.7855 | -0.23346 | 121.3394 | 121.0419 | 120.8817 | -0.91095 | 121.4905 | 121.4447 | 120.0394 | -121.6782
2326.6406 | 121.7239 | -121.0236 | 0.60425 | -0.25588 | 0.00069119 | 0.0090179 | 0.36075 | -0.065164 | -0.021949 | 0.045165 | -0.32927 | 3.2391 | 0.034898 | 0.093665 | 3.1427 | 0.097094 | 0.032043 | 0.10071 | -0.013733 | 0.086975 | 0.24261 | -0.11902 | -0.2655 | 0.018311 | -1.8585 | -0.17853 | 0.39825 | 0.33875 | -121.1426 | -121.0144 | 120.9045 | 120.7581 | -0.36163 | 121.1243 | 121.1105 | 0.35248 | -0.5722 | -0.11902 | 0.009156 | -0.20599 | 121.0419 | 120.845 | 120.8359 | -0.2655 | 121.2662 | 121.0556 | 121.0098 | -0.86975 | 121.4218 | 121.3623 | 119.165 | -121.6187
2327.6406 | 121.6873 | -121.0693 | 0.62714 | -0.33217 | 0.015645 | 0.023971 | 0.36823 | -0.069436 | -0.026221 | 0.030211 | -0.17668 | 3.2444 | 0.040239 | 0.086188 | 3.1534 | 0.086413 | 0.004578 | 0.082397 | -0.059509 | 0.045776 | 0.25635 | -0.1236 | -0.28839 | -0.041199 | -1.4465 | -0.23346 | 0.41657 | 0.36621 | -121.1746 | -121.051 | 120.9457 | 120.7809 | -0.37079 | 121.1517 | 121.1151 | 0.33417 | -0.62256 | -0.10529 | 0.018311 | -0.21057 | 121.0281 | 120.8359 | 120.8176 | -0.26093 | 121.3257 | 121.0739 | 121.0098 | -0.91553 | 121.4859 | 121.4355 | 119.6228 | -121.6782
2328.6875 | 121.756 | -121.0144 | 0.59967 | 0.064555 | 0.032734 | 0.011154 | 0.3693 | -0.071573 | -0.018744 | 0.035552 | 0.41841 | 3.2476 | 0.048783 | 0.089393 | 3.1438 | 0.088549 | 0.059509 | 0.10071 | -0.036621 | 0.068665 | 0.21057 | -0.086975 | -0.26093 | 0.068665 | -1.3458 | -0.15106 | 0.38452 | 0.36163 | -121.1014 | -121.0007 | 120.9274 | 120.7535 | -0.3891 | 121.1151 | 121.0831 | 0.32959 | -0.54016 | -0.086975 | 0.013733 | -0.21515 | 121.0831 | 120.8633 | 120.8496 | -0.23804 | 121.225 | 121.0739 | 120.9778 | -0.86059 | 121.3989 | 121.376 | 119.6686 | -121.6003
2329.6406 | 121.6873 | -121.051 | 0.63171 | -0.2101 | 0.015645 | 0.010086 | 0.35968 | -0.051278 | -0.018744 | 0.027007 | -0.37505 | 3.2412 | 0.03917 | 0.081916 | 3.1459 | 0.098162 | 0.018311 | 0.091553 | -0.050354 | 0.054932 | 0.25177 | -0.1236 | -0.2655 | -0.018311 | -1.7807 | -0.25177 | 0.41199 | 0.37537 | -121.1563 | -121.0464 | 120.9274 | 120.7855 | -0.37994 | 121.1426 | 121.106 | 0.32043 | -0.6134 | -0.10529 | 0.004577 | -0.21973 | 121.0327 | 120.7993 | 120.7947 | -0.25635 | 121.3028 | 121.0693 | 121.0007 | -0.89722 | 121.463 | 121.4264 | 119.2703 | -121.6782
2330.6406 | 121.8201 | -121.0464 | 0.57678 | -0.16433 | 0.027394 | 0.0047449 | 0.37143 | -0.066232 | -0.027289 | 0.03662 | -0.23772 | 3.2391 | 0.034898 | 0.080848 | 3.132 | 0.078936 | 0.059509 | 0.15106 | 0.032043 | 0.07782 | 0.24261 | -0.10529 | -0.2655 | 0.073242 | -3.0167 | -0.073242 | 0.3891 | 0.32959 | -121.1426 | -121.0556 | 120.9412 | 120.7809 | -0.33417 | 121.1975 | 121.1243 | 0.34332 | -0.51727 | -0.09613 | -0.009155 | -0.18768 | 121.1197 | 120.9732 | 120.9824 | -0.24719 | 121.2891 | 121.106 | 121.0785 | -0.84228 | 121.4355 | 121.376 | 118.0298 | -121.6324
2331.6406 | 121.7514 | -121.0373 | 0.59052 | 0.17137 | 0.0092362 | 0.00047294 | 0.35327 | -0.0673 | -0.018744 | 0.039824 | 0.28108 | 3.2295 | 0.045579 | 0.094733 | 3.1416 | 0.083208 | 0.009155 | 0.068665 | -0.054932 | 0.064087 | 0.22888 | -0.10529 | -0.30212 | 0.018311 | -3.2547 | -0.16937 | 0.34332 | 0.29755 | -121.1472 | -121.0602 | 120.932 | 120.7352 | -0.36163 | 121.106 | 121.1014 | 0.36621 | -0.58136 | -0.10986 | -0.022889 | -0.24719 | 121.0556 | 120.8679 | 120.8908 | -0.29297 | 121.2662 | 121.0464 | 120.9824 | -0.89264 | 121.3806 | 121.3348 | 117.7826 | -121.6507
2332.6406 | 121.8475 | -121.0144 | 0.58594 | 0.049296 | -0.0099898 | 0.0047449 | 0.36289 | -0.063028 | -0.01554 | 0.03662 | -0.43608 | 3.237 | 0.019944 | 0.08512 | 3.1373 | 0.092821 | 0.082397 | 0.15564 | 0.009155 | 0.09613 | 0.22888 | -0.09613 | -0.24261 | 0.12817 | -6.1935 | -0.09613 | 0.38452 | 0.33417 | -121.1243 | -121.0098 | 120.9183 | 120.7718 | -0.35706 | 121.17 | 121.1105 | 0.33874 | -0.50354 | -0.10986 | 0.004577 | -0.20142 | 121.1426 | 120.9183 | 120.9137 | -0.25177 | 121.2433 | 121.0968 | 121.0236 | -0.82855 | 121.3989 | 121.3486 | 114.8209 | -121.5958
2333.6406 | 121.8063 | -121.0373 | 0.62256 | -0.25588 | 0.0017592 | 0.0068819 | 0.36716 | -0.055551 | -0.020881 | 0.034484 | -0.23772 | 3.2466 | 0.045579 | 0.073371 | 3.1438 | 0.072527 | 0.10986 | 0.16022 | 0.027466 | 0.10529 | 0.23804 | -0.09613 | -0.24261 | 0.073242 | -4.3213 | -0.13275 | 0.3891 | 0.33875 | -121.1334 | -121.0098 | 120.9412 | 120.7947 | -0.38452 | 121.1975 | 121.1426 | 0.3479 | -0.5127 | -0.096131 | 0.027465 | -0.23346 | 121.1105 | 120.9045 | 120.8771 | -0.28381 | 121.2753 | 121.1472 | 121.0648 | -0.86517 | 121.4264 | 121.376 | 116.716 | -121.6324
2334.6875 | 121.7239 | -121.0464 | 0.62714 | -0.088033 | 0.039143 | -0.0070041 | 0.37036 | -0.069436 | 0.012231 | 0.050505 | -0.66496 | 3.2562 | 0.034898 | 0.093665 | 3.1651 | 0.074663 | 0.09613 | 0.032043 | -0.086975 | 0.036621 | 0.27008 | -0.14648 | -0.30212 | 0.041199 | -10.8398 | -0.24719 | 0.41657 | 0.36163 | -121.1655 | -121.0556 | 120.9 | 120.7443 | -0.35706 | 121.0785 | 121.0831 | 0.33875 | -0.53101 | -0.11902 | -0.009155 | -0.21057 | 121.0876 | 120.7993 | 120.8084 | -0.2655 | 121.3165 | 121.1426 | 120.9595 | -0.92926 | 121.463 | 121.4081 | 110.2066 | -121.6827
2335.6406 | 121.8201 | -121.0236 | 0.59967 | 0.095073 | 0.013508 | 0.015426 | 0.3693 | -0.064096 | -0.030494 | 0.03662 | -0.054612 | 3.2476 | 0.022081 | 0.08512 | 3.1309 | 0.089617 | 0.059509 | 0.1236 | -0.009155 | 0.073242 | 0.24719 | -0.10071 | -0.24261 | 0.10071 | -6.2576 | -0.10986 | 0.39368 | 0.3479 | -121.1105 | -121.0281 | 120.9229 | 120.7809 | -0.35248 | 121.1472 | 121.0968 | 0.31586 | -0.54016 | -0.086975 | -0.004577 | -0.20599 | 121.1243 | 120.9137 | 120.9183 | -0.25177 | 121.2708 | 121.0831 | 121.0144 | -0.84229 | 121.4172 | 121.3715 | 114.7659 | -121.6278
2336.6406 | 121.8063 | -121.0464 | 0.60883 | 0.35447 | 0.018849 | 0.0079499 | 0.35861 | -0.065164 | -0.023017 | 0.04196 | 0.021682 | 3.2455 | 0.035966 | 0.092597 | 3.1416 | 0.089617 | 0.013733 | 0.091553 | -0.018311 | 0.082397 | 0.21973 | -0.13275 | -0.27466 | 0.064087 | -4.1794 | -0.12817 | 0.39368 | 0.35248 | -121.1426 | -121.019 | 120.9137 | 120.7718 | -0.3891 | 121.138 | 121.1288 | 0.35706 | -0.59509 | -0.09613 | 0.027466 | -0.21515 | 121.1105 | 120.9183 | 120.8908 | -0.25635 | 121.2662 | 121.0602 | 121.0281 | -0.88348 | 121.4401 | 121.3989 | 116.8671 | -121.6278
2337.6875 | 121.6782 | -121.0648 | 0.59509 | 0.3087 | 0.048756 | 0.0079499 | 0.37357 | -0.071573 | 0.020776 | 0.050505 | -0.085129 | 3.2658 | 0.034898 | 0.087256 | 3.1662 | 0.084276 | 0.018311 | -0.013733 | -0.16479 | -0.018311 | 0.2655 | -0.13733 | -0.3067 | -0.036621 | -2.0782 | -0.29755 | 0.41657 | 0.36621 | -121.1746 | -121.0693 | 120.9274 | 120.7581 | -0.32959 | 121.051 | 121.0464 | 0.28839 | -0.57678 | -0.10986 | -0.004578 | -0.17853 | 121.0281 | 120.7672 | 120.7718 | -0.22888 | 121.3303 | 121.0831 | 120.9 | -0.90179 | 121.4813 | 121.431 | 118.9865 | -121.6644
2338.6406 | 121.8109 | -121.1609 | 0.54474 | 0.35447 | 0.028462 | 0.0036769 | 0.36823 | -0.053415 | -0.021949 | 0.04196 | 0.14375 | 3.2391 | 0.037034 | 0.072303 | 3.132 | 0.10884 | -0.009155 | 0.073242 | -0.068665 | 0.036621 | 0.25177 | -0.10529 | -0.2655 | 0.032043 | -2.417 | -0.16022 | 0.3891 | 0.35248 | -121.1288 | -121.0556 | 121.0556 | 120.8954 | -0.29297 | 121.2341 | 121.1975 | 0.30212 | -0.55389 | 0.032044 | 0.10529 | -0.15564 | 121.1929 | 121.0007 | 120.8954 | -0.19226 | 121.4127 | 121.1517 | 121.0922 | -0.81024 | 121.55 | 121.5134 | 118.7439 | -121.6003
2339.6562 | 121.701 | -121.0876 | 0.62714 | -0.19484 | 0.037007 | 0.0068819 | 0.38745 | -0.066232 | -0.0048589 | 0.055846 | -0.06987 | 3.2487 | 0.042375 | 0.092597 | 3.1491 | 0.085345 | 0.064087 | -0.027466 | -0.10071 | 0.027466 | 0.30212 | -0.091553 | -0.25177 | -0.027466 | -1.9272 | -0.26093 | 0.42572 | 0.35248 | -121.1792 | -121.0602 | 120.9961 | 120.8359 | -0.32501 | 121.0602 | 121.1151 | 0.27924 | -0.56305 | -0.091553 | 0.027465 | -0.20142 | 121.0602 | 120.8267 | 120.7993 | -0.27466 | 121.3898 | 121.1517 | 120.9869 | -0.87891 | 121.5134 | 121.4401 | 119.1605 | -121.6873
2340.6406 | 121.7926 | -121.1105 | 0.54474 | 0.27818 | 0.028462 | 0.0047449 | 0.35861 | -0.0673 | -0.03797 | 0.038756 | 0.12849 | 3.2423 | 0.027421 | 0.086188 | 3.1352 | 0.086413 | 0.009155 | 0.068665 | -0.073242 | 0.045776 | 0.23804 | -0.10529 | -0.27466 | 0.041199 | -2.5818 | -0.16479 | 0.3891 | 0.31586 | -121.2524 | -121.106 | 121.0052 | 120.8359 | -0.3067 | 121.1792 | 121.1563 | 0.32043 | -0.53558 | -0.14191 | 0.004578 | -0.15564 | 121.1517 | 120.9457 | 120.9412 | -0.22888 | 121.3486 | 121.1197 | 121.0373 | -0.8194 | 121.4996 | 121.4264 | 118.5287 | -121.6507
2341.6406 | 121.7606 | -121.0327 | 0.60425 | 0.33921 | 0.016713 | 0.017563 | 0.36395 | -0.065164 | -0.025153 | 0.034484 | 0.18953 | 3.2476 | 0.025285 | 0.074439 | 3.1459 | 0.089617 | 0.018311 | 0.091553 | -0.073242 | 0.045776 | 0.25177 | -0.10529 | -0.27924 | 0.045776 | -4.3533 | -0.15564 | 0.39368 | 0.35248 | -121.1563 | -121.0236 | 120.9274 | 120.7535 | -0.35248 | 121.1243 | 121.0785 | 0.32501 | -0.58594 | -0.1236 | 0.009155 | -0.21057 | 121.0785 | 120.8771 | 120.8679 | -0.25177 | 121.2845 | 121.051 | 120.9595 | -0.88348 | 121.4264 | 121.3852 | 116.6794 | -121.6278
2342.6875 | 121.6827 | -121.0419 | 0.62714 | 0.29344 | 0.067982 | 0.0036769 | 0.3725 | -0.058755 | 0.019708 | 0.051574 | 0.036941 | 3.2551 | 0.043443 | 0.093665 | 3.1491 | 0.070391 | 0.022888 | -0.045776 | -0.16022 | -0.009155 | 0.24261 | -0.13275 | -0.32044 | -0.032043 | -3.1403 | -0.30212 | 0.42572 | 0.33875 | -121.17 | -121.0648 | 120.9091 | 120.7214 | -0.38452 | 120.9961 | 121.0327 | 0.31128 | -0.60425 | -0.12817 | -0.022888 | -0.20142 | 121.0098 | 120.7397 | 120.7626 | -0.28839 | 121.2845 | 121.0648 | 120.8817 | -0.94757 | 121.4676 | 121.3806 | 117.9016 | -121.6919
2343.6406 | 121.8063 | -121.0281 | 0.59967 | 0.93431 | 0.047688 | -0.012345 | 0.3725 | -0.049142 | -0.00058594 | 0.051574 | 0.52522 | 3.2498 | 0.037034 | 0.081916 | 3.1523 | 0.097094 | 0.10529 | 0.10986 | -0.050354 | 0.086975 | 0.2243 | -0.091553 | -0.25635 | 0.10071 | -3.392 | -0.12817 | 0.36163 | 0.31128 | -121.1334 | -121.019 | 120.9366 | 120.7718 | -0.37537 | 121.138 | 121.1151 | 0.34332 | -0.49438 | -0.10529 | 0.009155 | -0.23804 | 121.1288 | 120.9 | 120.8908 | -0.28839 | 121.2524 | 121.1334 | 120.9778 | -0.85602 | 121.3898 | 121.3394 | 117.6361 | -121.6187
2344.6406 | 121.7514 | -121.0281 | 0.60425 | 0.55284 | 0.040211 | 0.011154 | 0.36395 | -0.066232 | -0.021949 | 0.047301 | 0.44893 | 3.2444 | 0.034898 | 0.087256 | 3.148 | 0.098162 | 0.07782 | 0.10071 | -0.064087 | 0.07782 | 0.21515 | -0.086975 | -0.24719 | 0.07782 | -2.5085 | -0.14648 | 0.39825 | 0.35706 | -121.1151 | -121.0007 | 120.9412 | 120.7809 | -0.3891 | 121.1288 | 121.106 | 0.32501 | -0.52643 | -0.086975 | 0.027466 | -0.20599 | 121.106 | 120.8817 | 120.8542 | -0.24719 | 121.2433 | 121.106 | 120.9641 | -0.85144 | 121.4264 | 121.3852 | 118.5196 | -121.6049
2345.6719 | 121.7926 | -121.0602 | 0.59509 | -0.2101 | 0.038075 | 0.016495 | 0.35648 | -0.066232 | -0.031562 | 0.033416 | -3.3047 | 3.2455 | 0.040239 | 0.092597 | 3.1384 | 0.091753 | 0.082397 | 0.13275 | -0.009155 | 0.09613 | 0.2243 | -0.091553 | -0.27466 | 0.10986 | -4.3167 | -0.11902 | 0.37537 | 0.33417 | -121.1426 | -121.0144 | 120.9686 | 120.7855 | -0.37079 | 121.1929 | 121.1563 | 0.37079 | -0.5127 | -0.082397 | 0.045777 | -0.21973 | 121.17 | 120.9412 | 120.8954 | -0.26093 | 121.2845 | 121.1426 | 121.051 | -0.86975 | 121.4355 | 121.3943 | 116.7435 | -121.6095
2346.6406 | 121.7422 | -121.0419 | 0.6134 | 0.46128 | 0.027394 | -0.010208 | 0.35968 | -0.072641 | -0.013404 | 0.035552 | 0.37263 | 3.2391 | 0.038102 | 0.086188 | 3.1459 | 0.09389 | 0.082397 | 0.082397 | -0.07782 | 0.059509 | 0.2243 | -0.086975 | -0.22888 | 0.068665 | -83.8531 | -0.1831 | 0.37994 | 0.34332 | -121.1197 | -121.0281 | 120.9549 | 120.813 | -0.3891 | 121.1243 | 121.1014 | 0.28839 | -0.53101 | -0.07782 | 0.013733 | -0.23346 | 121.1105 | 120.8588 | 120.845 | -0.27008 | 121.2662 | 121.1243 | 120.9641 | -0.84229 | 121.4218 | 121.3852 | 37.1887 | -121.6415
2347.6406 | 121.8246 | -121.0327 | 0.59509 | 0.4918 | 0.055165 | -0.0059361 | 0.37357 | -0.061959 | 0.0047541 | 0.04196 | 0.52522 | 3.2338 | 0.055192 | 0.07978 | 3.1544 | 0.078936 | 0.10986 | 0.073242 | -0.064087 | 0.045776 | 0.23346 | -0.11444 | -0.2655 | 0.10986 | -108.5312 | -0.15106 | 0.37537 | 0.31586 | -121.1472 | -121.0236 | 120.9183 | 120.7672 | -0.36163 | 121.106 | 121.0785 | 0.31128 | -0.48523 | -0.11444 | 0.009155 | -0.21973 | 121.1426 | 120.8817 | 120.8725 | -0.27924 | 121.2662 | 121.1426 | 120.9686 | -0.8606 | 121.4081 | 121.3486 | 12.5015 | -121.6187
2348.6406 | 121.8109 | -121.0876 | 0.56763 | 0.55284 | 0.038075 | 0.0026089 | 0.36182 | -0.068368 | 0.0036861 | 0.043029 | 0.46419 | 3.2487 | 0.031694 | 0.096869 | 3.147 | 0.080004 | 0.11902 | 0.10529 | -0.054932 | 0.07782 | 0.21515 | -0.091553 | -0.2655 | 0.091553 | -0.94757 | -0.12817 | 0.36621 | 0.33417 | -121.138 | -121.0327 | 120.9961 | 120.8221 | -0.35248 | 121.1929 | 121.1655 | 0.34332 | -0.44861 | -0.050354 | 0.054931 | -0.20142 | 121.1792 | 120.9595 | 120.9045 | -0.23346 | 121.3028 | 121.2067 | 121.0327 | -0.83313 | 121.4539 | 121.4218 | 120.1401 | -121.6003
2349.6406 | 121.7743 | -121.0327 | 0.59052 | 0.62913 | 0.059437 | 0.0026089 | 0.36075 | -0.058755 | -0.013404 | 0.04196 | 0.8304 | 3.2402 | 0.042375 | 0.092597 | 3.1416 | 0.091753 | 0.036621 | -0.12817 | -0.15564 | 0.10986 | 0.1831 | -0.1236 | -0.29755 | 0.09613 | -0.97046 | -0.14648 | 0.35706 | 0.31128 | -121.1288 | -121.0281 | 120.9091 | 120.7352 | -0.40741 | 120.9045 | 121.1426 | 0.40741 | -0.55389 | -0.09613 | 0.004578 | -0.23346 | 121.1288 | 120.8862 | 120.8817 | -0.27924 | 121.2158 | 121.0693 | 120.8771 | -0.88806 | 121.3898 | 121.344 | 120.0623 | -121.6187
2350.6406 | 121.8109 | -121.0464 | 0.58594 | 0.55284 | 0.056233 | 0.00047294 | 0.36289 | -0.054483 | 0.0090271 | 0.043029 | 0.18953 | 3.2423 | 0.042375 | 0.095801 | 3.1523 | 0.077868 | 0.10986 | 0.027466 | -0.09613 | 0.086975 | 0.23804 | -0.10071 | -0.25635 | 0.09613 | -1.7715 | -0.13733 | 0.37079 | 0.33417 | -121.1472 | -121.0098 | 120.9457 | 120.7901 | -0.3479 | 121.0739 | 121.1334 | 0.34332 | -0.47607 | -0.10071 | 0.036621 | -0.21515 | 121.1426 | 120.9091 | 120.8725 | -0.25177 | 121.2845 | 121.1563 | 120.9503 | -0.84229 | 121.4172 | 121.3806 | 119.2749 | -121.5958
2351.6875 | 121.9025 | -121.0831 | 0.58136 | -0.057515 | 0.041279 | -0.0080721 | 0.3757 | -0.071573 | -0.026221 | 0.043029 | -0.19194 | 3.2412 | 0.029557 | 0.075507 | 3.1373 | 0.086413 | 0.07782 | 0.13733 | 0 | 0.086975 | 0.23804 | -0.09613 | -0.25177 | 0.07782 | -2.0096 | -0.1236 | 0.36621 | 0.31586 | -121.138 | -121.0281 | 120.9869 | 120.8313 | -0.34332 | 121.2204 | 121.17 | 0.33874 | -0.50354 | -0.054931 | 0.054932 | -0.21515 | 121.1609 | 120.9595 | 120.9045 | -0.2655 | 121.3211 | 121.1609 | 121.0831 | -0.83313 | 121.4493 | 121.3989 | 119.0735 | -121.6095
2352.6406 | 121.7651 | -121.051 | 0.58136 | 0.56809 | 0.040211 | 0.0015409 | 0.38745 | -0.052346 | 0.0036861 | 0.045165 | 0.34212 | 3.254 | 0.037034 | 0.088325 | 3.163 | 0.078936 | 0.045776 | 0.036621 | -0.14191 | 0.027466 | 0.25177 | -0.1236 | -0.27924 | 0.064087 | -1.1948 | -0.1831 | 0.37537 | 0.35706 | -121.17 | -121.0373 | 120.9274 | 120.7718 | -0.32959 | 121.0876 | 121.0785 | 0.3067 | -0.53558 | -0.11902 | 0.013733 | -0.20599 | 121.1151 | 120.8679 | 120.8542 | -0.2243 | 121.3028 | 121.0968 | 120.9091 | -0.8606 | 121.4264 | 121.4081 | 119.8563 | -121.6187
2353.6406 | 121.7834 | -121.0419 | 0.54932 | 0.59861 | 0.047688 | -0.0016631 | 0.37784 | -0.053415 | -0.0069949 | 0.047301 | 0.44893 | 3.2423 | 0.037034 | 0.078712 | 3.1608 | 0.084276 | 0.10071 | 0.10986 | -0.068665 | 0.086975 | 0.21973 | -0.086975 | -0.24719 | -0.009155 | -1.9684 | -0.10529 | 0.35248 | 0.27924 | -121.1609 | -121.0602 | 120.9549 | 120.7947 | -0.32959 | 121.1517 | 121.1288 | 0.33417 | -0.44861 | -0.11902 | -0.018311 | -0.19684 | 121.0327 | 120.9366 | 120.9549 | -0.27008 | 121.2616 | 121.1426 | 120.9732 | -0.79651 | 121.3943 | 121.3211 | 119.0735 | -121.6095
2354.6406 | 121.8155 | -121.0373 | 0.60425 | 0.50706 | 0.049824 | 0.00047294 | 0.37784 | -0.05021 | 0.00048206 | 0.043029 | 0.40315 | 3.2402 | 0.040239 | 0.080848 | 3.1459 | 0.083208 | 0.10986 | 0.1236 | -0.059509 | 0.086975 | 0.21057 | -0.07782 | -0.24719 | 0.10986 | -2.1881 | -0.14191 | 0.37994 | 0.32501 | -121.138 | -121.0236 | 120.9595 | 120.7901 | -0.39368 | 121.1609 | 121.1243 | 0.33417 | -0.49439 | -0.10071 | 0.013732 | -0.2243 | 121.1472 | 120.8954 | 120.8817 | -0.27924 | 121.2479 | 121.1472 | 120.9778 | -0.85144 | 121.4172 | 121.3623 | 118.8492 | -121.6278
2355.6562 | 121.8246 | -121.0556 | 0.60883 | -0.026997 | 0.037007 | 0.0090179 | 0.37998 | -0.063028 | -0.024085 | 0.034484 | -0.2072 | 3.2423 | 0.022081 | 0.075507 | 3.1373 | 0.090685 | 0.11902 | 0.15106 | 0.022888 | 0.10071 | 0.21973 | -0.086975 | -0.2655 | 0.086975 | -1.5884 | -0.10986 | 0.37079 | 0.32959 | -121.1517 | -121.0144 | 120.9686 | 120.7901 | -0.3891 | 121.2067 | 121.1563 | 0.36621 | -0.48981 | -0.09613 | 0.041199 | -0.23804 | 121.1426 | 120.9457 | 120.9045 | -0.27924 | 121.2753 | 121.1746 | 121.0785 | -0.87433 | 121.4264 | 121.3852 | 119.4672 | -121.6232
2356.6406 | 121.8109 | -121.0236 | 0.58594 | 0.67491 | 0.035939 | -0.0048681 | 0.37784 | -0.056619 | 0.0026181 | 0.04196 | -0.085129 | 3.2498 | 0.031694 | 0.086188 | 3.1576 | 0.081072 | 0.10529 | 0.086975 | -0.086975 | 0.073242 | 0.23346 | -0.10529 | -0.25635 | 0.10071 | -4.4266 | -0.13733 | 0.36621 | 0.3067 | -121.1426 | -121.0419 | 120.9183 | 120.7672 | -0.35248 | 121.1105 | 121.0968 | 0.32959 | -0.48065 | -0.11902 | -0.01831 | -0.21973 | 121.1243 | 120.8862 | 120.9045 | -0.27924 | 121.257 | 121.1288 | 120.9366 | -0.84229 | 121.3898 | 121.3303 | 116.597 | -121.6278
2357.6406 | 121.701 | -121.0831 | 0.60425 | 0.4918 | 0.048756 | -0.00059506 | 0.37143 | -0.064096 | 0.012231 | 0.047301 | -1.5652 | 3.253 | 0.034898 | 0.095801 | 3.1598 | 0.090685 | 0.032043 | -0.013733 | -0.11902 | -0.054932 | 0.26093 | -0.10529 | -0.25635 | 0.022888 | -2.7969 | -0.23804 | 0.42114 | 0.3479 | -121.1746 | -121.0464 | 120.9778 | 120.8267 | -0.34332 | 121.0693 | 121.0281 | 0.20142 | -0.5722 | -0.091553 | 0.036621 | -0.18311 | 121.106 | 120.845 | 120.8084 | -0.25635 | 121.344 | 121.1151 | 120.9641 | -0.8606 | 121.5042 | 121.431 | 118.2861 | -121.6507
2358.6406 | 121.6644 | -121.0785 | 0.6134 | 0.4918 | 0.047688 | 0.0036769 | 0.35861 | -0.061959 | 0.013299 | 0.046233 | 0.28108 | 3.2412 | 0.047715 | 0.090461 | 3.1587 | 0.0768 | 0.018311 | -0.050354 | -0.19226 | 0 | 0.2655 | -0.12817 | -0.28839 | -0.009155 | -2.3209 | -0.28381 | 0.41657 | 0.37994 | -121.1517 | -121.0556 | 120.9503 | 120.7901 | -0.3479 | 121.0281 | 121.0785 | 0.28839 | -0.59509 | -0.073242 | 0.022888 | -0.19684 | 121.0693 | 120.7947 | 120.7718 | -0.23346 | 121.344 | 121.0968 | 120.8862 | -0.90179 | 121.4951 | 121.4584 | 118.7576 | -121.669
2359.6406 | 121.7331 | -121.0968 | 0.58594 | 0.46128 | 0.060505 | -0.013413 | 0.37998 | -0.072641 | -0.0037909 | 0.061187 | 0.18953 | 3.2455 | 0.043443 | 0.078712 | 3.1395 | 0.085345 | -0.032043 | 0.032043 | -0.19226 | -0.004578 | 0.27924 | -0.11902 | -0.25635 | 0.013733 | -4.2618 | -0.23804 | 0.40283 | 0.3479 | -121.2021 | -121.0922 | 120.9778 | 120.8405 | -0.3067 | 121.1288 | 121.0922 | 0.25177 | -0.61798 | -0.10529 | 0.004578 | -0.18311 | 121.1105 | 120.8588 | 120.8542 | -0.23804 | 121.376 | 121.0648 | 120.9045 | -0.84229 | 121.4996 | 121.4447 | 116.835 | -121.6782
2360.6875 | 121.8246 | -121.0464 | 0.60883 | 0.15611 | 0.027394 | 0.0090179 | 0.37357 | -0.057687 | -0.046515 | 0.04196 | 0.0522 | 3.2263 | 0.034898 | 0.086188 | 3.1277 | 0.097094 | 0.054932 | 0.12817 | -0.022888 | 0.07782 | 0.2655 | -0.091553 | -0.23346 | 0.10071 | -14.8682 | -0.07782 | 0.39825 | 0.32959 | -121.1288 | -121.019 | 120.9549 | 120.813 | -0.34332 | 121.1746 | 121.1243 | 0.31128 | -0.55389 | -0.082397 | 0.027466 | -0.21057 | 121.1472 | 120.9686 | 120.9412 | -0.27924 | 121.312 | 121.1014 | 121.0236 | -0.84228 | 121.4447 | 121.376 | 106.1783 | -121.6278
2361.6406 | 121.669 | -121.0739 | 0.61798 | 0.55284 | 0.060505 | 0.0026089 | 0.38104 | -0.063028 | 0.0068901 | 0.05371 | 0.22005 | 3.2455 | 0.051988 | 0.087256 | 3.1491 | 0.080004 | 0.018311 | -0.050354 | -0.20599 | 0.009155 | 0.27008 | -0.11444 | -0.28839 | -0.013733 | -10.3043 | -0.27008 | 0.40741 | 0.36163 | -121.1838 | -121.0739 | 120.9595 | 120.7855 | -0.3479 | 121.0236 | 121.0831 | 0.29755 | -0.59967 | -0.10986 | 0 | -0.21057 | 121.0602 | 120.8038 | 120.8038 | -0.25635 | 121.344 | 121.0922 | 120.8679 | -0.90637 | 121.4813 | 121.4355 | 110.7697 | -121.6919
2362.6875 | 121.7239 | -121.0648 | 0.63171 | -0.34743 | 0.022053 | 0.022903 | 0.37464 | -0.068368 | -0.025153 | 0.044097 | -0.28349 | 3.2402 | 0.032762 | 0.090461 | 3.1309 | 0.09389 | 0.045776 | 0.09613 | -0.045776 | 0.073242 | 0.22888 | -0.09613 | -0.2655 | 0.022888 | -6.1295 | -0.16937 | 0.39368 | 0.36163 | -121.1563 | -121.051 | 120.9686 | 120.7993 | -0.40283 | 121.1609 | 121.138 | 0.33874 | -0.58594 | -0.091553 | 0.013733 | -0.23804 | 121.0876 | 120.8954 | 120.8817 | -0.27008 | 121.2936 | 121.1105 | 121.019 | -0.89722 | 121.4584 | 121.4264 | 114.9353 | -121.6827
2363.6406 | 121.7422 | -121.1014 | 0.63629 | 0.44602 | 0.064778 | -0.0059361 | 0.3725 | -0.066232 | 0.015435 | 0.05371 | 0.22005 | 3.2412 | 0.046647 | 0.091529 | 3.1502 | 0.1035 | 0.022888 | -0.027466 | -0.21515 | 0.018311 | 0.25177 | -0.13733 | -0.29297 | 0.13733 | -7.8506 | -0.10986 | 0.42114 | 0.37994 | -121.1655 | -121.051 | 120.9641 | 120.8084 | -0.38452 | 121.0739 | 121.1197 | 0.31128 | -0.6134 | -0.064087 | 0.050354 | -0.21515 | 121.2387 | 120.9915 | 120.9412 | -0.25635 | 121.3531 | 121.1243 | 120.8862 | -0.92926 | 121.5225 | 121.4813 | 113.2507 | -121.6873
2364.6562 | 121.7834 | -121.0373 | 0.59967 | 0.29344 | 0.044484 | 0.011154 | 0.38425 | -0.066232 | -0.030494 | 0.044097 | 0.29634 | 3.2305 | 0.041307 | 0.080848 | 3.1267 | 0.096026 | 0.009155 | 0.041199 | -0.091553 | 0.041199 | 0.21973 | -0.10986 | -0.25177 | 0.022888 | -6.6559 | -0.14648 | 0.39825 | 0.33417 | -121.17 | -121.0831 | 120.9274 | 120.7855 | -0.37994 | 121.0785 | 121.0785 | 0.29297 | -0.59052 | -0.13275 | -0.045777 | -0.20142 | 121.0602 | 120.8908 | 120.9366 | -0.2655 | 121.257 | 121.0464 | 120.9457 | -0.85144 | 121.4355 | 121.3715 | 114.3814 | -121.6827
2365.6406 | 121.6736 | -121.0922 | 0.62256 | 0.20188 | 0.076527 | 0.00047294 | 0.37784 | -0.066232 | 0.01864 | 0.051574 | 0.067459 | 3.2466 | 0.05092 | 0.097938 | 3.1587 | 0.081072 | 0 | -0.068665 | -0.22888 | -0.013733 | 0.26093 | -0.13275 | -0.30212 | -0.009155 | -7.782 | -0.28381 | 0.42114 | 0.37079 | -121.2067 | -121.0968 | 120.9595 | 120.7901 | -0.36163 | 121.0236 | 121.0785 | 0.28839 | -0.62256 | -0.11444 | -0.004578 | -0.20142 | 121.0831 | 120.8084 | 120.813 | -0.25177 | 121.3531 | 121.0922 | 120.8633 | -0.92468 | 121.5134 | 121.463 | 113.3102 | -121.7194
2366.6406 | 121.7606 | -121.0739 | 0.60425 | 0.11033 | 0.040211 | 0.0015409 | 0.36075 | -0.063028 | 0.0068901 | 0.052642 | -0.13091 | 3.2466 | 0.053056 | 0.084052 | 3.1438 | 0.077868 | 0.073242 | 0.041199 | -0.10986 | 0.050354 | 0.2655 | -0.13275 | -0.29755 | 0.050354 | -5.4886 | -0.21973 | 0.40283 | 0.36163 | -121.1838 | -121.0739 | 120.9412 | 120.7764 | -0.33875 | 121.1151 | 121.1243 | 0.3479 | -0.53101 | -0.10986 | 0 | -0.20142 | 121.1243 | 120.8542 | 120.8542 | -0.24262 | 121.3394 | 121.1472 | 120.9641 | -0.90179 | 121.4767 | 121.4355 | 115.5853 | -121.6782
2367.6406 | 121.7789 | -121.0419 | 0.59967 | 0.41551 | 0.031666 | 0.0079499 | 0.35861 | -0.066232 | -0.034766 | 0.043029 | 0.50996 | 3.2305 | 0.03383 | 0.07978 | 3.1331 | 0.11312 | 0.009155 | 0.091553 | -0.11444 | 0.054932 | 0.23346 | -0.073242 | -0.24261 | 0.032043 | -6.0883 | -0.16022 | 0.37994 | 0.33875 | -121.1792 | -121.0373 | 120.9686 | 120.7993 | -0.36621 | 121.1334 | 121.0968 | 0.29755 | -0.59052 | -0.13733 | 0.004578 | -0.21973 | 121.0739 | 120.8817 | 120.8771 | -0.26093 | 121.2753 | 121.051 | 120.9274 | -0.84229 | 121.4218 | 121.3806 | 114.9536 | -121.637
2368.6406 | 121.7926 | -121.051 | 0.57678 | 0.3087 | 0.010304 | 0.012222 | 0.35114 | -0.063028 | -0.024085 | 0.03662 | 0.32686 | 3.2263 | 0.032762 | 0.074439 | 3.1373 | 0.091753 | 0.013733 | 0.050354 | -0.11444 | 0.050354 | 0.23804 | -0.10529 | -0.2655 | 0.018311 | -10.6613 | -0.15564 | 0.39825 | 0.34332 | -121.17 | -121.0648 | 120.9457 | 120.7855 | -0.33875 | 121.1014 | 121.1014 | 0.31586 | -0.56305 | -0.11902 | -0.013733 | -0.17853 | 121.0693 | 120.8954 | 120.9091 | -0.23346 | 121.2891 | 121.0648 | 120.9366 | -0.84228 | 121.4493 | 121.3943 | 110.3897 | -121.6415
2369.6406 | 121.7194 | -121.106 | 0.59509 | 0.20188 | 0.04662 | 0.0090179 | 0.37464 | -0.0673 | 0.019708 | 0.049437 | -0.11565 | 3.2466 | 0.038102 | 0.095801 | 3.1587 | 0.080004 | 0.1236 | 0.082397 | -0.17395 | 0.036621 | 0.30212 | -0.050354 | -0.24719 | -0.004578 | -9.082 | -0.25635 | 0.41199 | 0.36163 | -121.1655 | -121.0968 | 121.0556 | 120.8588 | -0.29297 | 121.1884 | 121.1426 | 0.28381 | -0.4715 | -0.059509 | 0.009155 | -0.18311 | 121.1014 | 120.8496 | 120.8405 | -0.23346 | 121.4081 | 121.2296 | 120.932 | -0.84228 | 121.5179 | 121.4676 | 112.0239 | -121.6919
2370.6406 | 121.7194 | -121.0831 | 0.6134 | 0.52232 | 0.054097 | -0.0080721 | 0.3757 | -0.070504 | 0.0015501 | 0.057982 | 1.5781 | 3.2551 | 0.044511 | 0.080848 | 3.1491 | 0.091753 | -0.004578 | -0.013733 | -0.19226 | 0.022888 | 0.26093 | -0.13275 | -0.27466 | -0.027466 | -8.9493 | -0.26093 | 0.43488 | 0.37079 | -121.2021 | -121.0739 | 120.9503 | 120.8084 | -0.35248 | 121.0693 | 121.106 | 0.29755 | -0.61798 | -0.11902 | 0.009155 | -0.17853 | 121.0556 | 120.8221 | 120.813 | -0.24261 | 121.344 | 121.0785 | 120.8908 | -0.88806 | 121.5179 | 121.4539 | 112.1338 | -121.6873
2371.6562 | 121.7834 | -121.0556 | 0.59967 | -0.59157 | 0.034871 | 0.0015409 | 0.36182 | -0.068368 | -0.021949 | 0.040892 | 0.47945 | 3.2412 | 0.03917 | 0.071235 | 3.1363 | 0.09389 | 0.050354 | 0.11444 | -0.091553 | 0.068665 | 0.19684 | -0.07782 | -0.27008 | 0.082397 | -116.7343 | -0.13733 | 0.3891 | 0.35706 | -121.1655 | -121.0281 | 120.9778 | 120.7855 | -0.40283 | 121.17 | 121.1243 | 0.33875 | -0.54932 | -0.10986 | 0.027466 | -0.21057 | 121.138 | 120.9183 | 120.8908 | -0.24261 | 121.2524 | 121.106 | 120.9641 | -0.86975 | 121.4447 | 121.4127 | 4.3213 | -121.6278
2372.6406 | 121.7239 | -121.0968 | 0.59509 | 0.62913 | 0.048756 | 0.016495 | 0.35327 | -0.05021 | -0.0080629 | 0.046233 | 0.38789 | 3.2402 | 0.060533 | 0.088325 | 3.1502 | 0.084276 | 0.027466 | 0.054932 | -0.1831 | 0.013733 | 0.2655 | -0.11902 | -0.27924 | 0.036621 | -116.8716 | -0.23346 | 0.39368 | 0.36163 | -121.1929 | -121.0739 | 120.9778 | 120.8176 | -0.32959 | 121.1517 | 121.1105 | 0.29297 | -0.56763 | -0.09613 | 0.022888 | -0.20142 | 121.1334 | 120.8633 | 120.8405 | -0.23346 | 121.3623 | 121.1243 | 120.9137 | -0.87433 | 121.4905 | 121.4584 | 4.2252 | -121.669
2373.6406 | 121.7285 | -121.0327 | 0.66834 | 0.049296 | 0.061574 | -0.0059361 | 0.37891 | -0.060891 | 0.0079581 | 0.04196 | -0.14616 | 3.2434 | 0.060533 | 0.094733 | 3.1544 | 0.068255 | 0.073242 | 0.050354 | -0.13733 | 0.022888 | 0.24719 | -0.12817 | -0.28381 | 0.022888 | -0.54932 | -0.21973 | 0.41657 | 0.37079 | -121.0876 | -121.0052 | 120.9045 | 120.7489 | -0.42114 | 121.0831 | 121.0556 | 0.3067 | -0.59509 | -0.054931 | 0.027466 | -0.25177 | 121.0556 | 120.813 | 120.7855 | -0.29755 | 121.2799 | 121.106 | 120.8954 | -0.95215 | 121.4493 | 121.4035 | 120.4834 | -121.6736
2374.6406 | 121.7606 | -121.0876 | 0.60883 | 0.049296 | 0.050892 | -0.0080721 | 0.37357 | -0.056619 | -0.0069949 | 0.051574 | -0.19194 | 3.254 | 0.05626 | 0.097938 | 3.1459 | 0.087481 | 0.036621 | 0.068665 | -0.11902 | 0.032043 | 0.24719 | -0.11902 | -0.28839 | 0.022888 | -1.2039 | -0.22888 | 0.40741 | 0.36621 | -121.1929 | -121.0693 | 120.9686 | 120.7993 | -0.36163 | 121.1563 | 121.1197 | 0.32043 | -0.5722 | -0.10529 | 0.01831 | -0.20142 | 121.1105 | 120.8588 | 120.8405 | -0.24261 | 121.3348 | 121.1243 | 120.9686 | -0.89722 | 121.4951 | 121.4539 | 119.8837 | -121.6782
2375.6406 | 121.7194 | -121.1105 | 0.64087 | 0.12559 | 0.078663 | 0.0026089 | 0.37357 | -0.0673 | -0.0016549 | 0.040892 | 0.3116 | 3.2466 | 0.053056 | 0.095801 | 3.1491 | 0.091753 | -0.050354 | -0.068665 | -0.2243 | -0.018311 | 0.26093 | -0.12817 | -0.28839 | -0.022888 | -1.3046 | -0.26093 | 0.41199 | 0.3479 | -121.2021 | -121.0785 | 120.9824 | 120.8221 | -0.37994 | 121.0419 | 121.0922 | 0.27008 | -0.69122 | -0.091552 | 0.032044 | -0.22888 | 121.0876 | 120.8496 | 120.8176 | -0.29297 | 121.3715 | 121.0602 | 120.8862 | -0.92926 | 121.5225 | 121.4584 | 119.8059 | -121.7194
2376.6406 | 121.8109 | -121.051 | 0.64087 | 0.049296 | 0.064778 | -0.0016631 | 0.37998 | -0.053415 | -0.00058594 | 0.048369 | -0.039353 | 3.2412 | 0.044511 | 0.088325 | 3.1459 | 0.084276 | 0.050354 | 0.054932 | -0.13733 | 0.041199 | 0.2655 | -0.1236 | -0.28839 | 0.018311 | -1.0895 | -0.23804 | 0.39825 | 0.35248 | -121.2067 | -121.0831 | 120.9274 | 120.7626 | -0.37537 | 121.106 | 121.0922 | 0.32959 | -0.59052 | -0.15564 | -0.032044 | -0.24262 | 121.0693 | 120.813 | 120.845 | -0.28839 | 121.3165 | 121.1014 | 120.9137 | -0.92926 | 121.4493 | 121.4035 | 119.9615 | -121.7239
2377.6406 | 121.6919 | -121.0968 | 0.61798 | 0.47654 | 0.078663 | -0.0059361 | 0.3757 | -0.063028 | -0.0037909 | 0.03662 | 0.29634 | 3.2402 | 0.055192 | 0.084052 | 3.1299 | 0.085345 | -0.027466 | -0.018311 | -0.20599 | 0.009155 | 0.2655 | -0.12817 | -0.30212 | -0.022888 | -1.4465 | -0.2655 | 0.40741 | 0.37537 | -121.2296 | -121.0693 | 120.9686 | 120.7947 | -0.35248 | 121.0785 | 121.106 | 0.31128 | -0.64545 | -0.13275 | 0.027466 | -0.21057 | 121.0739 | 120.8313 | 120.8038 | -0.24262 | 121.3623 | 121.0693 | 120.8908 | -0.9201 | 121.5042 | 121.4722 | 119.6503 | -121.6873
2378.6406 | 121.7377 | -121.0739 | 0.60425 | 0.85801 | 0.056233 | 0.016495 | 0.38104 | -0.064096 | -0.014472 | 0.050505 | -0.29875 | 3.2423 | 0.040239 | 0.08512 | 3.1384 | 0.090685 | -0.032043 | 0 | -0.16479 | 0.018311 | 0.27466 | -0.12817 | -0.29755 | -0.032043 | -1.7075 | -0.23346 | 0.40741 | 0.36621 | -121.1975 | -121.0922 | 120.9457 | 120.7764 | -0.32959 | 121.0739 | 121.0922 | 0.31586 | -0.63629 | -0.1236 | -0.01831 | -0.19684 | 121.0419 | 120.8405 | 120.8588 | -0.23804 | 121.3486 | 121.0419 | 120.9091 | -0.90179 | 121.4813 | 121.4401 | 119.3665 | -121.6965
2379.6406 | 121.756 | -121.0831 | 0.6134 | -0.2101 | 0.058369 | -0.0027321 | 0.37357 | -0.064096 | -0.0080629 | 0.049437 | -0.26824 | 3.2434 | 0.048783 | 0.10007 | 3.1427 | 0.09389 | 0 | 0.027466 | -0.15564 | 0.045776 | 0.23346 | -0.14648 | -0.31586 | 0 | -4.1061 | -0.20142 | 0.39825 | 0.36621 | -121.2067 | -121.0785 | 120.9366 | 120.7672 | -0.37994 | 121.1105 | 121.1288 | 0.36163 | -0.6134 | -0.1236 | 0.004578 | -0.21515 | 121.0831 | 120.8817 | 120.8771 | -0.24719 | 121.3165 | 121.0831 | 120.9274 | -0.92926 | 121.4813 | 121.4493 | 116.9769 | -121.6919
2380.6406 | 121.6873 | -121.0876 | 0.61798 | 0.47654 | 0.070118 | 0.00047294 | 0.38104 | -0.063028 | -0.00058594 | 0.046233 | 0.37263 | 3.2412 | 0.051988 | 0.076575 | 3.1416 | 0.091753 | -0.036621 | -0.036621 | -0.23804 | 0.018311 | 0.27466 | -0.1236 | -0.30212 | -0.032043 | -0.96588 | -0.26093 | 0.41657 | 0.37079 | -121.2067 | -121.1243 | 120.9641 | 120.7855 | -0.34332 | 121.051 | 121.106 | 0.32044 | -0.6546 | -0.11902 | -0.036622 | -0.20142 | 121.0556 | 120.8267 | 120.8633 | -0.24719 | 121.3623 | 121.051 | 120.8496 | -0.9201 | 121.5042 | 121.4584 | 120.1218 | -121.7422
2381.6406 | 121.8338 | -121.0648 | 0.58136 | 0.65965 | 0.049824 | 0.0015409 | 0.36289 | -0.064096 | -0.021949 | 0.04196 | 0.50996 | 3.2338 | 0.03917 | 0.087256 | 3.1309 | 0.098162 | 0.045776 | 0.10986 | -0.091553 | 0.091553 | 0.21515 | -0.086975 | -0.24261 | 0.07782 | -1.5656 | -0.1236 | 0.36621 | 0.32044 | -121.1563 | -121.0648 | 120.9778 | 120.8221 | -0.36621 | 121.1746 | 121.1563 | 0.33417 | -0.53558 | -0.091553 | 0 | -0.21515 | 121.1426 | 120.9412 | 120.9412 | -0.26092 | 121.2799 | 121.1105 | 120.9732 | -0.82398 | 121.431 | 121.3852 | 119.4992 | -121.6461
2382.6406 | 121.8338 | -121.0556 | 0.59509 | 0.24766 | 0.059437 | 0.0047449 | 0.3725 | -0.070504 | -0.012336 | 0.048369 | 0.55574 | 3.237 | 0.035966 | 0.074439 | 3.147 | 0.091753 | 0.073242 | 0.086975 | -0.11902 | 0.10529 | 0.21515 | -0.068665 | -0.25177 | 0.059509 | -1.8173 | -0.14191 | 0.36163 | 0.32959 | -121.17 | -121.051 | 120.9869 | 120.8038 | -0.37994 | 121.1426 | 121.1609 | 0.35706 | -0.52185 | -0.11444 | 0.004578 | -0.23346 | 121.1151 | 120.9137 | 120.9091 | -0.2655 | 121.2708 | 121.1288 | 120.9366 | -0.84686 | 121.4172 | 121.3852 | 119.2383 | -121.6461
2383.6406 | 121.7331 | -121.0785 | 0.59509 | -0.11855 | 0.043416 | -0.00059506 | 0.37677 | -0.072641 | -0.0069949 | 0.04196 | -0.35979 | 3.2434 | 0.03383 | 0.081916 | 3.1438 | 0.078936 | -0.018311 | 0.009155 | -0.17853 | 0.022888 | 0.24261 | -0.13275 | -0.3067 | -0.013733 | -1.3138 | -0.23346 | 0.39825 | 0.35248 | -121.2021 | -121.106 | 120.9457 | 120.7718 | -0.35248 | 121.0876 | 121.1014 | 0.32959 | -0.6134 | -0.1236 | -0.027466 | -0.19684 | 121.0648 | 120.845 | 120.8725 | -0.24261 | 121.3211 | 121.0602 | 120.9 | -0.90179 | 121.4767 | 121.431 | 119.7647 | -121.7011
2384.6406 | 121.7377 | -121.1105 | 0.60883 | 0.064555 | 0.064778 | 0.011154 | 0.38104 | -0.053415 | -0.0037909 | 0.050505 | -0.35979 | 3.2434 | 0.054124 | 0.086188 | 3.1416 | 0.087481 | -0.022888 | 0.009155 | -0.19226 | 0.018311 | 0.2655 | -0.12817 | -0.30212 | -0.022888 | -0.50812 | -0.22888 | 0.40283 | 0.36163 | -121.2112 | -121.106 | 120.9824 | 120.8084 | -0.34332 | 121.1197 | 121.1288 | 0.32044 | -0.63171 | -0.10071 | 0.004578 | -0.20599 | 121.0876 | 120.8817 | 120.8771 | -0.24719 | 121.376 | 121.0876 | 120.9183 | -0.91095 | 121.5134 | 121.4722 | 120.6024 | -121.7148
2385.6875 | 121.8521 | -121.0281 | 0.58594 | 0.034038 | 0.039143 | 0.01329 | 0.38639 | -0.060891 | -0.04972 | 0.03662 | 0.18953 | 3.2338 | 0.05626 | 0.084052 | 3.1128 | 0.092821 | 0.045776 | 0.15564 | -0.036621 | 0.10986 | 0.24719 | -0.07782 | -0.22888 | 0.082397 | -116.5329 | -0.09613 | 0.37537 | 0.34332 | -121.1792 | -121.0693 | 120.9503 | 120.7993 | -0.33875 | 121.1838 | 121.138 | 0.33875 | -0.54016 | -0.15106 | -0.041199 | -0.21057 | 121.1105 | 120.932 | 120.9732 | -0.24261 | 121.2753 | 121.0739 | 120.9915 | -0.81482 | 121.4035 | 121.3715 | 4.4952 | -121.6553
2386.6406 | 121.7377 | -121.0968 | 0.60883 | -0.2101 | 0.06371 | 0.022903 | 0.3725 | -0.072641 | -0.011268 | 0.04196 | -0.77178 | 3.2402 | 0.047715 | 0.077643 | 3.1341 | 0.0768 | -0.009155 | 0.23346 | -0.041199 | 0.013733 | 0.27008 | -0.091553 | -0.25177 | -0.032043 | -6.9855 | -0.24719 | 0.43488 | 0.37994 | -121.2067 | -121.106 | 121.0052 | 120.845 | -0.33874 | 121.3303 | 121.1105 | 0.2655 | -0.61798 | -0.10986 | -0.009155 | -0.17395 | 121.0648 | 120.8496 | 120.8588 | -0.22888 | 121.3669 | 121.0876 | 121.0556 | -0.8606 | 121.5317 | 121.4767 | 114.1113 | -121.7148
2387.6562 | 121.8384 | -121.0693 | 0.59052 | 0.56809 | 0.051961 | -0.0038001 | 0.38852 | -0.053415 | 0.0026181 | 0.048369 | 0.35738 | 3.2305 | 0.047715 | 0.07978 | 3.1459 | 0.091753 | 0.004578 | 0.054932 | -0.14191 | 0.045776 | 0.23346 | -0.10071 | -0.28381 | 0.091553 | -2.2797 | -0.16479 | 0.37537 | 0.32959 | -121.1975 | -121.0739 | 120.9686 | 120.7855 | -0.35706 | 121.1243 | 121.1151 | 0.32959 | -0.58594 | -0.12817 | -0.004578 | -0.21515 | 121.1609 | 120.9045 | 120.9091 | -0.26093 | 121.3028 | 121.0739 | 120.9274 | -0.87433 | 121.4447 | 121.3989 | 118.7897 | -121.6644
2388.6406 | 121.7102 | -121.1151 | 0.64087 | 0.034038 | 0.02419 | 0.0079499 | 0.36716 | -0.057687 | -0.031562 | 0.034484 | -0.35979 | 3.2338 | 0.035966 | 0.096869 | 3.1288 | 0.086413 | -0.059509 | 0.036621 | -0.13275 | -0.004578 | 0.2655 | -0.1236 | -0.30212 | -0.041199 | -2.0828 | -0.24719 | 0.4303 | 0.3891 | -121.1929 | -121.0922 | 120.9915 | 120.813 | -0.37537 | 121.1517 | 121.1105 | 0.29755 | -0.70038 | -0.07782 | 0.022888 | -0.21057 | 121.0739 | 120.8679 | 120.845 | -0.25177 | 121.3806 | 121.0556 | 120.9824 | -0.94299 | 121.5454 | 121.5042 | 119.0323 | -121.7331
2389.6406 | 121.7148 | -121.1151 | 0.64545 | -0.2864 | 0.023121 | 0.0015409 | 0.37143 | -0.070504 | -0.014472 | 0.037688 | -0.2072 | 3.2466 | 0.026353 | 0.071235 | 3.1288 | 0.094958 | -0.027466 | 0.027466 | -0.16022 | 0 | 0.25177 | -0.11902 | -0.29297 | -0.041199 | -3.3142 | -0.25177 | 0.42572 | 0.37537 | -121.2341 | -121.1014 | 120.9961 | 120.8221 | -0.39368 | 121.1426 | 121.1151 | 0.29297 | -0.67291 | -0.11902 | 0.013733 | -0.21973 | 121.0739 | 120.8633 | 120.8496 | -0.27008 | 121.3669 | 121.0876 | 120.9549 | -0.93842 | 121.5408 | 121.4905 | 117.8009 | -121.7468
2390.6406 | 121.6873 | -121.019 | 0.6546 | 0.034038 | 0.054097 | -0.00059506 | 0.38639 | -0.054483 | 0.013299 | 0.033416 | -0.14616 | 3.2434 | 0.064805 | 0.089393 | 3.1502 | 0.075732 | 0.045776 | 0.045776 | -0.15564 | 0.041199 | 0.24719 | -0.1236 | -0.27924 | 0.013733 | -19.2398 | -0.24719 | 0.39825 | 0.35706 | -121.2067 | -121.0968 | 120.8954 | 120.7397 | -0.40741 | 121.0648 | 121.0602 | 0.32043 | -0.60883 | -0.18768 | -0.07782 | -0.25635 | 121.0327 | 120.7718 | 120.8496 | -0.29755 | 121.2662 | 121.0648 | 120.8633 | -0.93384 | 121.4172 | 121.376 | 101.7792 | -121.7514
2391.6406 | 121.7606 | -121.106 | 0.60883 | -0.22536 | 0.042347 | 0.0090179 | 0.3725 | -0.057687 | -0.011268 | 0.046233 | 0.43367 | 3.2391 | 0.05626 | 0.092597 | 3.1373 | 0.08214 | -0.036621 | 0.18768 | -0.013733 | 0.09613 | 0.28839 | -0.09613 | -0.26093 | -0.022888 | -105.0385 | -0.25635 | 0.4303 | 0.3891 | -121.2204 | -121.0968 | 121.0098 | 120.845 | -0.32043 | 121.2936 | 121.2021 | 0.35706 | -0.64545 | -0.11444 | 0.009155 | -0.17853 | 121.0831 | 120.8496 | 120.8405 | -0.21973 | 121.3943 | 121.0693 | 121.0922 | -0.86975 | 121.5363 | 121.4951 | 16.0675 | -121.7056
2392.6406 | 121.7468 | -121.0968 | 0.63171 | -0.56106 | 0.033803 | 0.010086 | 0.35541 | -0.070504 | -0.026221 | 0.038756 | -0.28349 | 3.2359 | 0.024217 | 0.082984 | 3.1309 | 0.098162 | 0.013733 | 0.11902 | -0.086975 | 0.07782 | 0.23346 | -0.10071 | -0.27008 | -0.009155 | -3.6026 | -0.19684 | 0.40741 | 0.3479 | -121.2021 | -121.0648 | 120.9961 | 120.8267 | -0.39826 | 121.2158 | 121.1746 | 0.3479 | -0.61798 | -0.10529 | 0.032044 | -0.2243 | 121.0876 | 120.9 | 120.8679 | -0.28381 | 121.3303 | 121.1105 | 121.0098 | -0.9018 | 121.5042 | 121.4447 | 117.4942 | -121.6965
2393.6719 | 121.7056 | -121.0876 | 0.62256 | 0.50706 | 0.067982 | -0.013413 | 0.38425 | -0.065164 | -0.00058594 | 0.052642 | 0.25056 | 3.2444 | 0.048783 | 0.10114 | 3.1384 | 0.0768 | 0 | -0.032043 | -0.2243 | -0.004578 | 0.27008 | -0.10986 | -0.27008 | -0.027466 | -9.1599 | -0.28839 | 0.41199 | 0.36163 | -121.1838 | -121.1014 | 120.9778 | 120.8176 | -0.35248 | 121.0556 | 121.0831 | 0.2655 | -0.62256 | -0.096131 | -0.013733 | -0.21057 | 121.0602 | 120.7993 | 120.813 | -0.26093 | 121.3577 | 121.0876 | 120.8633 | -0.89264 | 121.4996 | 121.4493 | 111.9278 | -121.7239
2394.6406 | 121.701 | -121.1151 | 0.61798 | -0.25588 | 0.028462 | 0.020767 | 0.37891 | -0.059823 | -0.028357 | 0.037688 | -0.35979 | 3.2338 | 0.042375 | 0.084052 | 3.1384 | 0.083208 | -0.041199 | 0 | -0.16479 | 0.013733 | 0.27008 | -0.13733 | -0.29297 | -0.041199 | -1.0895 | -0.25635 | 0.41657 | 0.37994 | -121.2067 | -121.106 | 120.9778 | 120.8221 | -0.3479 | 121.1151 | 121.1288 | 0.3067 | -0.65918 | -0.091553 | 0.009155 | -0.20142 | 121.0739 | 120.8588 | 120.8496 | -0.23804 | 121.3852 | 121.0739 | 120.9503 | -0.91095 | 121.5317 | 121.4951 | 120.0256 | -121.7239
2395.6562 | 121.756 | -121.0831 | 0.59967 | 0.52232 | 0.060505 | -0.0027321 | 0.37464 | -0.059823 | -0.017676 | 0.040892 | 0.55574 | 3.2423 | 0.053056 | 0.097938 | 3.1331 | 0.084276 | 0.17395 | -0.082397 | -0.23346 | 0.041199 | 0.27466 | -0.10071 | -0.25635 | 0.018311 | -0.98419 | -0.21973 | 0.41199 | 0.33875 | -121.1929 | -121.0648 | 120.9824 | 120.8267 | -0.32501 | 121.0007 | 121.1243 | 0.29755 | -0.42572 | -0.10986 | 0.018311 | -0.18768 | 121.1014 | 120.8633 | 120.845 | -0.26093 | 121.3577 | 121.257 | 120.8496 | -0.85602 | 121.4951 | 121.4218 | 120.0989 | -121.6644
2396.6406 | 121.7468 | -121.0831 | 0.62714 | -0.19484 | 0.037007 | 0.0026089 | 0.36075 | -0.063028 | -0.021949 | 0.039824 | -0.26824 | 3.2284 | 0.037034 | 0.088325 | 3.1331 | 0.086413 | -0.009155 | 0.10986 | -0.091553 | 0.07782 | 0.21973 | -0.11902 | -0.28381 | -0.009155 | -0.80109 | -0.20142 | 0.39825 | 0.36621 | -121.2021 | -121.0922 | 120.9641 | 120.7993 | -0.40741 | 121.1929 | 121.1609 | 0.36163 | -0.63629 | -0.11902 | -0.009155 | -0.22888 | 121.0739 | 120.8817 | 120.8908 | -0.26093 | 121.3028 | 121.0739 | 120.9915 | -0.91095 | 121.4813 | 121.4493 | 120.282 | -121.7194
2397.6406 | 121.7102 | -121.106 | 0.62714 | -0.13381 | 0.040211 | 0.012222 | 0.37357 | -0.0673 | -0.019813 | 0.037688 | -0.22246 | 3.2498 | 0.043443 | 0.082984 | 3.1256 | 0.078936 | 0 | -0.004578 | -0.1831 | 0.009155 | 0.27008 | -0.14648 | -0.30212 | -0.045776 | -1.8768 | -0.24719 | 0.43488 | 0.3891 | -121.1929 | -121.1334 | 120.9595 | 120.8038 | -0.35706 | 121.1014 | 121.1151 | 0.31128 | -0.62714 | -0.086975 | -0.027466 | -0.19226 | 121.0602 | 120.8588 | 120.8862 | -0.23804 | 121.376 | 121.106 | 120.9229 | -0.92926 | 121.5408 | 121.4951 | 119.2291 | -121.7606
2398.6719 | 121.701 | -121.0922 | 0.61798 | 0.43077 | 0.053029 | -0.0038001 | 0.36823 | -0.068368 | 0.0036861 | 0.040892 | 0.28108 | 3.2466 | 0.049852 | 0.099006 | 3.147 | 0.083208 | -0.036621 | -0.054932 | -0.28839 | 0 | 0.27924 | -0.11902 | -0.29755 | -0.027466 | -111.9598 | -0.29297 | 0.40741 | 0.3479 | -121.1975 | -121.1014 | 120.9732 | 120.7947 | -0.33875 | 121.0373 | 121.0922 | 0.29755 | -0.6546 | -0.10529 | -0.009155 | -0.21057 | 121.0648 | 120.7993 | 120.8084 | -0.27008 | 121.3715 | 121.0556 | 120.8038 | -0.91553 | 121.4996 | 121.4401 | 9.1324 | -121.7194
2399.6406 | 121.8018 | -121.0739 | 0.60425 | -0.10329 | 0.0060322 | 0.015426 | 0.35968 | -0.05021 | -0.043311 | 0.047301 | -0.23772 | 3.2348 | 0.03383 | 0.07978 | 3.1267 | 0.087481 | 0.036621 | 0.12817 | -0.082397 | 0.07782 | 0.22888 | -0.086975 | -0.24261 | 0.045776 | -116.0431 | -0.16479 | 0.37994 | 0.32959 | -121.2158 | -121.0739 | 120.9869 | 120.8313 | -0.37537 | 121.2021 | 121.1517 | 0.32044 | -0.56763 | -0.14191 | 0 | -0.2243 | 121.1197 | 120.9091 | 120.9091 | -0.27466 | 121.3028 | 121.1105 | 120.9915 | -0.84686 | 121.4539 | 121.4035 | 5.0308 | -121.6782
2400.6406 | 121.6965 | -121.0556 | 0.64545 | -0.17959 | 0.032734 | 0.0036769 | 0.37036 | -0.074777 | -0.0069949 | 0.04196 | -0.42082 | 3.2402 | 0.037034 | 0.091529 | 3.132 | 0.078936 | -0.032043 | 0.004578 | -0.19226 | 0.027466 | 0.27008 | -0.12817 | -0.29297 | -0.036621 | -104.1367 | -0.25635 | 0.42114 | 0.37994 | -121.2112 | -121.0831 | 120.9274 | 120.7626 | -0.37537 | 121.0602 | 121.0831 | 0.32043 | -0.67749 | -0.15564 | -0.027466 | -0.2243 | 121.019 | 120.7993 | 120.8267 | -0.2655 | 121.3257 | 121.0236 | 120.8633 | -0.93842 | 121.4767 | 121.4355 | 16.9189 | -121.7285
2401.6406 | 121.7422 | -121.106 | 0.62714 | -0.14907 | 0.032734 | 0.0068819 | 0.36716 | -0.071573 | -0.025153 | 0.045165 | -1.5805 | 3.2327 | 0.048783 | 0.091529 | 3.1267 | 0.078936 | -0.013733 | 0.041199 | -0.16022 | 0.027466 | 0.2655 | -0.1236 | -0.28381 | -0.041199 | -1.1032 | -0.23804 | 0.42114 | 0.37079 | -121.2341 | -121.0785 | 120.9824 | 120.8221 | -0.36163 | 121.1472 | 121.1334 | 0.31128 | -0.64087 | -0.12817 | 0.027466 | -0.20599 | 121.0648 | 120.8679 | 120.8405 | -0.25635 | 121.3715 | 121.0922 | 120.9457 | -0.91095 | 121.5271 | 121.4767 | 120.0027 | -121.7056
2402.6719 | 121.6873 | -121.0968 | 0.62256 | 0.27818 | 0.053029 | -0.0038001 | 0.36716 | -0.059823 | 0.0068901 | 0.04196 | -0.0088351 | 3.2455 | 0.046647 | 0.082984 | 3.147 | 0.077868 | -0.036621 | -0.050354 | -0.21973 | 0 | 0.2655 | -0.13733 | -0.3067 | -0.050354 | -0.85144 | -0.29755 | 0.42572 | 0.36621 | -121.225 | -121.0968 | 120.9595 | 120.7901 | -0.35706 | 121.0464 | 121.0968 | 0.3067 | -0.65918 | -0.12817 | 0 | -0.19684 | 121.0464 | 120.7993 | 120.7993 | -0.25635 | 121.3623 | 121.0602 | 120.8771 | -0.92926 | 121.5225 | 121.463 | 120.2454 | -121.7194
2403.6406 | 121.7285 | -121.1243 | 0.60883 | -0.27114 | 0.035939 | 0.0026089 | 0.3757 | -0.061959 | -0.012336 | 0.037688 | -0.34453 | 3.2391 | 0.037034 | 0.080848 | 3.1341 | 0.091753 | -0.032043 | 0.009155 | -0.21057 | 0.018311 | 0.2655 | -0.1236 | -0.27008 | -0.036621 | -4.1061 | -0.24261 | 0.41657 | 0.35706 | -121.225 | -121.0831 | 121.0007 | 120.8542 | -0.34332 | 121.1334 | 121.1426 | 0.28839 | -0.64087 | -0.10071 | 0.041199 | -0.19226 | 121.0876 | 120.8817 | 120.8405 | -0.25177 | 121.3898 | 121.0922 | 120.9137 | -0.87891 | 121.5408 | 121.4813 | 117.0181 | -121.6919
2404.6719 | 121.7239 | -121.1288 | 0.6134 | 0.36973 | 0.04662 | -0.0091401 | 0.36716 | -0.061959 | -0.0037909 | 0.060118 | 0.082718 | 3.2338 | 0.037034 | 0.10969 | 3.1352 | 0.08214 | 0.018311 | -0.073242 | -0.20142 | 0.091553 | 0.28381 | -0.10071 | -0.24719 | -0.027466 | -10.4965 | -0.28381 | 0.43945 | 0.36621 | -121.2112 | -121.1243 | 121.0281 | 120.8817 | -0.32959 | 121.0556 | 121.2204 | 0.33874 | -0.59509 | -0.082398 | 0.004577 | -0.17395 | 121.1014 | 120.845 | 120.8405 | -0.24719 | 121.4127 | 121.1472 | 120.9274 | -0.86059 | 121.5683 | 121.4951 | 110.6323 | -121.7377
2405.6406 | 121.7285 | -121.0968 | 0.63171 | -0.16433 | 0.037007 | -0.00059506 | 0.37998 | -0.055551 | -0.016608 | 0.038756 | -0.42082 | 3.2423 | 0.032762 | 0.093665 | 3.1277 | 0.083208 | -0.032043 | 0.009155 | -0.20599 | 0.018311 | 0.26093 | -0.10986 | -0.29297 | -0.041199 | -9.3521 | -0.22888 | 0.41199 | 0.36163 | -121.1884 | -121.1105 | 120.9869 | 120.8038 | -0.37079 | 121.106 | 121.1151 | 0.31128 | -0.66376 | -0.091552 | -0.013733 | -0.21973 | 121.0556 | 120.8679 | 120.8817 | -0.27008 | 121.3577 | 121.0648 | 120.8908 | -0.92468 | 121.5088 | 121.4584 | 111.7447 | -121.7422
2406.6562 | 121.7514 | -121.0968 | 0.6134 | 0.29344 | 0.058369 | -0.0070041 | 0.37036 | -0.056619 | 0.015435 | 0.054778 | 0.67781 | 3.2434 | 0.049852 | 0.088325 | 3.1384 | 0.089617 | 0 | 0.022888 | -0.25635 | 0.018311 | 0.26093 | -0.1236 | -0.25635 | -0.018311 | -5.2597 | -0.27466 | 0.4303 | 0.37994 | -121.2112 | -121.1197 | 120.9732 | 120.8405 | -0.35248 | 121.1197 | 121.1151 | 0.27466 | -0.6134 | -0.11444 | -0.022888 | -0.18311 | 121.0785 | 120.8221 | 120.845 | -0.23346 | 121.3577 | 121.0968 | 120.8405 | -0.86975 | 121.5271 | 121.4767 | 115.8371 | -121.7331
2407.6406 | 121.875 | -121.0785 | 0.62714 | 0.12559 | 0.014576 | 0.018631 | 0.37143 | -0.071573 | -0.050788 | 0.034484 | 0.17427 | 3.2252 | 0.014604 | 0.084052 | 3.1171 | 0.10243 | 0.032043 | 0.09613 | -0.13733 | 0.086975 | 0.21057 | -0.1236 | -0.26093 | 0.091553 | -3.2181 | -0.082397 | 0.39368 | 0.36163 | -121.1655 | -121.0327 | 120.9549 | 120.8176 | -0.41657 | 121.1746 | 121.1655 | 0.3479 | -0.59509 | -0.086975 | 0.045776 | -0.23346 | 121.17 | 120.9961 | 120.9503 | -0.2655 | 121.2891 | 121.1105 | 120.9412 | -0.88806 | 121.4722 | 121.4401 | 117.8604 | -121.6599
2408.6406 | 121.8155 | -121.0602 | 0.59509 | -0.24062 | 0.031666 | 0.016495 | 0.36716 | -0.065164 | -0.031562 | 0.034484 | -0.2072 | 3.2295 | 0.028489 | 0.095801 | 3.1267 | 0.089617 | 0.036621 | 0.13733 | -0.12817 | 0.082397 | 0.21515 | -0.082397 | -0.27008 | 0.045776 | -101.2848 | -0.13733 | 0.39368 | 0.32959 | -121.1746 | -121.051 | 120.9778 | 120.7901 | -0.37994 | 121.1975 | 121.1426 | 0.35248 | -0.55847 | -0.11444 | 0.009156 | -0.20142 | 121.106 | 120.9229 | 120.9137 | -0.2655 | 121.2753 | 121.0968 | 120.932 | -0.86517 | 121.4539 | 121.3898 | 19.7754 | -121.6461
2409.6406 | 121.8475 | -121.0556 | 0.58136 | 0.15611 | 0.0071002 | 0.00047294 | 0.36289 | -0.064096 | -0.036902 | 0.034484 | 0.12849 | 3.2391 | 0.03917 | 0.094733 | 3.1181 | 0.08214 | 0.059509 | 0.12817 | -0.1236 | 0.09613 | 0.23804 | -0.086975 | -0.23804 | 0.1236 | -8.812 | -0.07782 | 0.40283 | 0.32959 | -121.1746 | -121.0602 | 120.9686 | 120.8176 | -0.34332 | 121.1838 | 121.1517 | 0.33417 | -0.52185 | -0.11902 | -0.004578 | -0.17853 | 121.1792 | 120.9778 | 120.9824 | -0.25177 | 121.2936 | 121.1151 | 120.932 | -0.8194 | 121.4584 | 121.3852 | 112.2437 | -121.6415
2410.6562 | 121.7285 | -121.0785 | 0.60425 | 0.20188 | 0.042347 | 0.0026089 | 0.3757 | -0.058755 | 0.010095 | 0.049437 | -0.054612 | 3.2572 | 0.048783 | 0.093665 | 3.147 | 0.072527 | 0.050354 | 0.032043 | -0.21515 | 0.041199 | 0.25635 | -0.11444 | -0.27008 | 0.004578 | -6.2347 | -0.26093 | 0.41199 | 0.37079 | -121.2112 | -121.0968 | 120.9641 | 120.8084 | -0.3479 | 121.1105 | 121.1197 | 0.31128 | -0.55389 | -0.13275 | -0.018311 | -0.19226 | 121.0831 | 120.8176 | 120.8359 | -0.23346 | 121.3348 | 121.1288 | 120.8633 | -0.87433 | 121.4905 | 121.4493 | 114.8438 | -121.701
2411.6406 | 121.7834 | -121.0922 | 0.6134 | -0.24062 | 0.02953 | 0.0036769 | 0.3725 | -0.063028 | -0.013404 | 0.038756 | -0.29875 | 3.238 | 0.063737 | 0.07978 | 3.1277 | 0.087481 | 0.022888 | 0.10071 | -0.17395 | 0.064087 | 0.21973 | -0.10529 | -0.26093 | -0.009155 | -113.53 | -0.25177 | 0.40283 | 0.34332 | -121.1975 | -121.0739 | 120.9869 | 120.8313 | -0.39368 | 121.1929 | 121.1563 | 0.32501 | -0.59052 | -0.10529 | 0.01831 | -0.21057 | 121.0831 | 120.8405 | 120.8221 | -0.27008 | 121.312 | 121.1151 | 120.9183 | -0.87433 | 121.4951 | 121.4355 | 7.5623 | -121.6873
2412.6406 | 121.788 | -121.0876 | 0.59967 | 0.43077 | 0.0071002 | 0.0068819 | 0.36609 | -0.069436 | -0.041175 | 0.038756 | 0.26582 | 3.2316 | 0.035966 | 0.093665 | 3.1277 | 0.086413 | -0.009155 | 0.073242 | -0.25635 | 0.045776 | 0.22888 | -0.11902 | -0.24719 | 0.013733 | -115.6448 | -0.16022 | 0.37994 | 0.33875 | -121.1746 | -121.051 | 120.9686 | 120.8405 | -0.37079 | 121.1609 | 121.1334 | 0.29297 | -0.60883 | -0.086976 | 0.036621 | -0.21973 | 121.1014 | 120.9274 | 120.8908 | -0.26093 | 121.3165 | 121.0785 | 120.8313 | -0.84686 | 121.4676 | 121.4264 | 5.4428 | -121.6507
2413.7031 | 121.7789 | -121.0693 | 0.61798 | 0.50706 | 0.031666 | -0.0038001 | 0.35327 | -0.059823 | 0.016503 | 0.043029 | 0.32686 | 3.2391 | 0.047715 | 0.094733 | 3.1416 | 0.081072 | 0.022888 | 0.018311 | -0.33417 | 0.013733 | 0.26093 | -0.12817 | -0.27008 | 0.027466 | -117.4896 | -0.2243 | 0.39825 | 0.3479 | -121.1975 | -121.0602 | 120.9412 | 120.7993 | -0.35706 | 121.0876 | 121.0831 | 0.28381 | -0.59509 | -0.12817 | 0.009155 | -0.21973 | 121.0968 | 120.845 | 120.8359 | -0.27008 | 121.3303 | 121.0922 | 120.7352 | -0.88806 | 121.4676 | 121.4172 | 3.5797 | -121.6782
2414.6406 | 121.8704 | -121.0602 | 0.59967 | 0.15611 | 0.030598 | 0.00047294 | 0.35541 | -0.071573 | -0.042243 | 0.031279 | 0.036941 | 3.2252 | 0.037034 | 0.090461 | 3.1245 | 0.086413 | 0.013733 | 0.059509 | -0.19226 | 0.073242 | 0.23346 | -0.10529 | -0.25635 | 0.10529 | -110.5865 | -0.10529 | 0.38452 | 0.3479 | -121.1655 | -121.0693 | 120.9549 | 120.8038 | -0.36621 | 121.1197 | 121.1334 | 0.32959 | -0.58594 | -0.10528 | -0.009155 | -0.21515 | 121.1655 | 120.9549 | 120.9641 | -0.25177 | 121.2936 | 121.0739 | 120.8679 | -0.85602 | 121.4447 | 121.4081 | 10.4736 | -121.669
2415.6562 | 121.7789 | -121.0785 | 0.6134 | 0.095073 | 0.056233 | -0.0016631 | 0.38852 | -0.054483 | 0.026116 | 0.045165 | -0.22246 | 3.2391 | 0.042375 | 0.084052 | 3.1448 | 0.075732 | 0.059509 | 0.064087 | -0.27466 | 0.050354 | 0.27924 | -0.1236 | -0.28381 | 0.027466 | -107.4692 | -0.25177 | 0.41657 | 0.34332 | -121.2021 | -121.0876 | 120.9549 | 120.7947 | -0.33417 | 121.1426 | 121.1288 | 0.33417 | -0.55389 | -0.1236 | -0.009155 | -0.19684 | 121.106 | 120.8267 | 120.8359 | -0.27008 | 121.3577 | 121.138 | 120.8038 | -0.89722 | 121.4951 | 121.4218 | 13.6093 | -121.701
2416.6406 | 121.788 | -121.0785 | 0.6134 | 0.26292 | 0.0017592 | 0.014358 | 0.36823 | -0.068368 | -0.03263 | 0.043029 | 0.22005 | 3.2295 | 0.030626 | 0.084052 | 3.1245 | 0.090685 | 0 | 0.059509 | -0.24719 | 0.050354 | 0.21973 | -0.11902 | -0.25177 | 0.018311 | -109.7672 | -0.15106 | 0.37994 | 0.3479 | -121.1746 | -121.0693 | 120.9595 | 120.8267 | -0.39368 | 121.138 | 121.1288 | 0.30212 | -0.6134 | -0.096131 | 0.009155 | -0.23346 | 121.0968 | 120.9274 | 120.9183 | -0.2655 | 121.2982 | 121.0785 | 120.8313 | -0.86517 | 121.4584 | 121.4264 | 11.3113 | -121.6827
2417.6406 | 121.8246 | -121.051 | 0.59967 | 0.14085 | 0.018849 | -0.0016631 | 0.35648 | -0.070504 | -0.027289 | 0.028075 | 0.11323 | 3.2338 | 0.049852 | 0.07978 | 3.1224 | 0.091753 | 0.004578 | 0.064087 | -0.28839 | 0.064087 | 0.22888 | -0.086975 | -0.24719 | 0.032043 | -111.9324 | -0.12817 | 0.40741 | 0.3479 | -121.2021 | -121.0693 | 120.9641 | 120.8038 | -0.37079 | 121.1151 | 121.1151 | 0.31128 | -0.59509 | -0.15106 | -0.018311 | -0.19226 | 121.0831 | 120.9229 | 120.9412 | -0.25177 | 121.2799 | 121.0556 | 120.7626 | -0.84686 | 121.4584 | 121.3989 | 9.1187 | -121.669
2418.6406 | 121.8475 | -121.0693 | 0.59967 | 0.018779 | 0.020985 | 0.00047294 | 0.36502 | -0.068368 | -0.01554 | 0.028075 | -0.0088351 | 3.2338 | 0.023149 | 0.080848 | 3.1395 | 0.098162 | 0.054932 | 0.09613 | -0.20142 | 0.068665 | 0.23804 | -0.11444 | -0.24719 | 0.068665 | -113.5117 | -0.10986 | 0.37537 | 0.33417 | -121.1655 | -121.0556 | 120.9549 | 120.8221 | -0.36163 | 121.1655 | 121.138 | 0.31586 | -0.54474 | -0.09613 | 0.013733 | -0.2243 | 121.138 | 120.9595 | 120.9457 | -0.2655 | 121.3074 | 121.1243 | 120.8679 | -0.84686 | 121.4447 | 121.4035 | 7.5577 | -121.6553
2419.6562 | 121.7743 | -121.0876 | 0.62714 | -0.17959 | 0.038075 | -0.00059506 | 0.36075 | -0.058755 | 0.012231 | 0.039824 | -0.42082 | 3.238 | 0.043443 | 0.081916 | 3.1406 | 0.070391 | 0.022888 | 0.013733 | -0.28839 | 0.022888 | 0.28839 | -0.13275 | -0.29755 | -0.013733 | -5.7358 | -0.23804 | 0.41199 | 0.37079 | -121.2204 | -121.1151 | 120.9549 | 120.7901 | -0.33875 | 121.1014 | 121.1105 | 0.32043 | -0.60425 | -0.13275 | -0.027466 | -0.21515 | 121.0739 | 120.8496 | 120.8771 | -0.25635 | 121.376 | 121.1105 | 120.7993 | -0.92468 | 121.4996 | 121.4584 | 115.3519 | -121.7422
2420.6406 | 121.8338 | -121.0556 | 0.58594 | 0.11033 | 0.023121 | 0.0068819 | 0.36502 | -0.058755 | -0.028357 | 0.031279 | 0.021682 | 3.2338 | 0.032762 | 0.087256 | 3.1224 | 0.086413 | 0.050354 | 0.10529 | -0.21515 | 0.068665 | 0.23804 | -0.082397 | -0.26093 | 0.10529 | -23.2773 | -0.11902 | 0.3891 | 0.33875 | -121.1792 | -121.0556 | 120.9732 | 120.7947 | -0.3479 | 121.1609 | 121.1243 | 0.32959 | -0.53558 | -0.1236 | 0 | -0.19684 | 121.1609 | 120.9366 | 120.9366 | -0.24719 | 121.2936 | 121.106 | 120.8405 | -0.84686 | 121.4447 | 121.3943 | 97.7783 | -121.6415
2421.6562 | 121.7606 | -121.0739 | 0.61798 | -0.13381 | 0.040211 | -0.0016631 | 0.37143 | -0.060891 | 0.0026181 | 0.044097 | -0.45134 | 3.2316 | 0.038102 | 0.080848 | 3.1341 | 0.073595 | 0.022888 | 0.004578 | -0.36163 | 0.027466 | 0.25635 | -0.14191 | -0.29755 | 0.009155 | -97.3938 | -0.23346 | 0.42114 | 0.36163 | -121.2387 | -121.0968 | 120.932 | 120.7764 | -0.36163 | 121.0785 | 121.1014 | 0.32501 | -0.59509 | -0.16479 | -0.022888 | -0.19684 | 121.0831 | 120.8405 | 120.8633 | -0.25635 | 121.3303 | 121.0968 | 120.7123 | -0.91553 | 121.4951 | 121.4355 | 23.6801 | -121.7148
2422.6406 | 121.7972 | -121.0693 | 0.60425 | 0.29344 | 0.02419 | 0.0047449 | 0.35541 | -0.075845 | -0.030494 | 0.039824 | 0.25056 | 3.2327 | 0.024217 | 0.087256 | 3.1203 | 0.087481 | 0.004578 | 0.068665 | -0.24261 | 0.045776 | 0.23804 | -0.10529 | -0.27008 | 0.018311 | -9.1873 | -0.16479 | 0.39825 | 0.32959 | -121.1838 | -121.0922 | 120.9641 | 120.7993 | -0.36621 | 121.138 | 121.1151 | 0.31586 | -0.59967 | -0.11444 | -0.022888 | -0.20599 | 121.0876 | 120.9045 | 120.9274 | -0.27466 | 121.3074 | 121.0739 | 120.8267 | -0.87433 | 121.4676 | 121.3989 | 111.882 | -121.6965
2423.6562 | 121.7102 | -121.0785 | 0.62256 | -0.25588 | 0.037007 | 0.010086 | 0.36716 | -0.068368 | 0.0036861 | 0.040892 | -0.42082 | 3.2423 | 0.051988 | 0.082984 | 3.1288 | 0.074663 | 0.013733 | 0.018311 | -0.27466 | 0.009155 | 0.25635 | -0.14191 | -0.3067 | -0.027466 | -35.4218 | -0.26093 | 0.42114 | 0.36621 | -121.225 | -121.1151 | 120.9366 | 120.7718 | -0.36621 | 121.0968 | 121.0876 | 0.31586 | -0.60883 | -0.14648 | -0.036621 | -0.20142 | 121.051 | 120.8176 | 120.8542 | -0.25635 | 121.3348 | 121.0922 | 120.8038 | -0.92926 | 121.4996 | 121.4447 | 85.6567 | -121.7377
2424.6406 | 121.7926 | -121.0739 | 0.58594 | 0.50706 | 0.047688 | 0.0036769 | 0.36502 | -0.080117 | -0.029426 | 0.045165 | 0.43367 | 3.2359 | 0.042375 | 0.077643 | 3.1213 | 0.098162 | 0.045776 | 0.086975 | -0.34332 | 0.027466 | 0.23804 | -0.07782 | -0.26093 | 0.050354 | -105.5649 | -0.1831 | 0.39368 | 0.34332 | -121.1884 | -121.0968 | 120.9961 | 120.813 | -0.3479 | 121.1609 | 121.1014 | 0.28839 | -0.54016 | -0.11444 | -0.022888 | -0.19226 | 121.1243 | 120.8908 | 120.9137 | -0.24261 | 121.312 | 121.1197 | 120.7306 | -0.84686 | 121.4676 | 121.4172 | 15.509 | -121.6827
2425.6875 | 121.7285 | -121.106 | 0.62714 | -0.27114 | 0.044484 | 0.0079499 | 0.36182 | -0.070504 | -0.012336 | 0.04196 | -0.51238 | 3.2391 | 0.029557 | 0.070167 | 3.1384 | 0.073595 | -0.009155 | 0.004578 | -0.26093 | 0.009155 | 0.2655 | -0.12817 | -0.29755 | -0.022888 | -7.8094 | -0.25177 | 0.42572 | 0.39368 | -121.2433 | -121.1105 | 120.9778 | 120.8084 | -0.36163 | 121.1105 | 121.1151 | 0.3067 | -0.63629 | -0.13733 | -0.004578 | -0.20142 | 121.0831 | 120.8542 | 120.8588 | -0.23346 | 121.3715 | 121.0968 | 120.845 | -0.92468 | 121.5317 | 121.4996 | 113.2965 | -121.7377
2426.6406 | 121.7972 | -121.0602 | 0.60883 | 0.44602 | 0.025258 | -0.00059506 | 0.37677 | -0.063028 | -0.024085 | 0.04196 | 0.3116 | 3.2284 | 0.053056 | 0.090461 | 3.116 | 0.078936 | 0.027466 | 0.073242 | -0.24719 | 0.064087 | 0.23804 | -0.09613 | -0.25177 | 0.050354 | -9.7916 | -0.15106 | 0.39368 | 0.33875 | -121.1884 | -121.0693 | 120.9641 | 120.8084 | -0.37079 | 121.1334 | 121.1243 | 0.31586 | -0.58136 | -0.12817 | -0.009155 | -0.21515 | 121.1105 | 120.9091 | 120.9183 | -0.27008 | 121.2982 | 121.0876 | 120.813 | -0.8606 | 121.4539 | 121.3989 | 111.2686 | -121.6782
2427.6406 | 121.8018 | -121.0876 | 0.57678 | 0.53758 | 0.028462 | 0.012222 | 0.36609 | -0.0673 | -0.017676 | 0.048369 | 0.3116 | 3.2252 | 0.037034 | 0.086188 | 3.1331 | 0.090685 | 0.050354 | 0.082397 | -0.31586 | 0.059509 | 0.2243 | -0.09613 | -0.24261 | 0.064087 | -43.4052 | -0.16937 | 0.38452 | 0.36163 | -121.1975 | -121.0876 | 120.9915 | 120.845 | -0.35248 | 121.17 | 121.1472 | 0.30212 | -0.52643 | -0.10986 | 0 | -0.19226 | 121.1517 | 120.9183 | 120.9183 | -0.21515 | 121.312 | 121.138 | 120.7718 | -0.8194 | 121.4722 | 121.4493 | 77.6825 | -121.6644
2428.6406 | 121.7422 | -121.0876 | 0.62714 | -0.19484 | 0.062642 | 0.028244 | 0.36609 | -0.063028 | 0.0068901 | 0.039824 | -0.45134 | 3.2241 | 0.040239 | 0.084052 | 3.1406 | 0.081072 | 0.022888 | -0.004578 | -0.35248 | 0.018311 | 0.2655 | -0.12817 | -0.28381 | -0.004578 | -14.3692 | -0.25177 | 0.41657 | 0.37079 | -121.2112 | -121.1243 | 120.9595 | 120.8038 | -0.36163 | 121.0831 | 121.106 | 0.30212 | -0.60425 | -0.1236 | -0.036622 | -0.21057 | 121.0831 | 120.8359 | 120.8725 | -0.25635 | 121.3531 | 121.1105 | 120.7352 | -0.91095 | 121.5042 | 121.4584 | 106.7184 | -121.7514
2429.6562 | 121.7239 | -121.1197 | 0.61798 | -0.24062 | 0.041279 | 0.0079499 | 0.37143 | -0.064096 | -0.017676 | 0.043029 | -0.28349 | 3.2327 | 0.051988 | 0.082984 | 3.1341 | 0.091753 | -0.018311 | 0.032043 | -0.24719 | 0.027466 | 0.2655 | -0.12817 | -0.27008 | -0.009155 | -50.5875 | -0.24261 | 0.41657 | 0.37537 | -121.2387 | -121.1151 | 120.9915 | 120.8496 | -0.35248 | 121.1517 | 121.1472 | 0.29755 | -0.63629 | -0.11902 | 0.004578 | -0.20142 | 121.1105 | 120.8771 | 120.8725 | -0.24262 | 121.3852 | 121.1014 | 120.8725 | -0.88806 | 121.5363 | 121.4951 | 70.5322 | -121.7331
2430.6406 | 121.7972 | -121.0922 | 0.60425 | 0.4918 | 0.039143 | 0.011154 | 0.35434 | -0.0673 | -0.030494 | 0.039824 | 0.2353 | 3.222 | 0.037034 | 0.088325 | 3.1256 | 0.098162 | 0 | 0.073242 | -0.32501 | 0.027466 | 0.25177 | -0.10071 | -0.27008 | 0.050354 | -17.9581 | -0.15106 | 0.37537 | 0.32501 | -121.1838 | -121.0831 | 120.9915 | 120.8221 | -0.35248 | 121.1655 | 121.1197 | 0.29755 | -0.60425 | -0.091553 | 0.009155 | -0.22888 | 121.1426 | 120.9412 | 120.932 | -0.27924 | 121.344 | 121.0922 | 120.7672 | -0.87433 | 121.4676 | 121.4172 | 103.1342 | -121.6873
2431.6406 | 121.843 | -121.0464 | 0.59509 | 0.53758 | 0.047688 | 0.0026089 | 0.37036 | -0.054483 | 0.0090271 | 0.045165 | 0.38789 | 3.2295 | 0.037034 | 0.096869 | 3.1427 | 0.078936 | 0.09613 | 0.11902 | -0.28839 | 0.068665 | 0.21515 | -0.073242 | -0.25177 | 0.10986 | -22.554 | -0.14191 | 0.37537 | 0.32501 | -121.1792 | -121.0464 | 120.9732 | 120.7947 | -0.37994 | 121.1655 | 121.1151 | 0.32044 | -0.49896 | -0.13275 | 0 | -0.21973 | 121.1563 | 120.9045 | 120.9045 | -0.27008 | 121.2616 | 121.1426 | 120.7581 | -0.84686 | 121.4218 | 121.3715 | 98.4924 | -121.6415
2432.6719 | 121.8567 | -121.0739 | 0.60425 | -0.22536 | 0.037007 | 0.0047449 | 0.37891 | -0.071573 | -0.026221 | 0.03662 | -0.23772 | 3.2295 | 0.041307 | 0.071235 | 3.1256 | 0.088549 | 0.068665 | 0.14191 | -0.23346 | 0.073242 | 0.23804 | -0.091553 | -0.24261 | 0.068665 | -24.3301 | -0.11902 | 0.37079 | 0.34332 | -121.1792 | -121.0693 | 120.9824 | 120.8313 | -0.36621 | 121.2158 | 121.1472 | 0.31586 | -0.53558 | -0.10528 | 0.004578 | -0.23346 | 121.1426 | 120.9549 | 120.9503 | -0.26093 | 121.312 | 121.1426 | 120.8405 | -0.84686 | 121.4447 | 121.4172 | 96.7438 | -121.6736
2433.6406 | 121.8109 | -121.0739 | 0.59509 | 0.65965 | 0.058369 | -0.00059506 | 0.36182 | -0.053415 | 0.0047541 | 0.04196 | 0.29634 | 3.2444 | 0.03383 | 0.093665 | 3.1363 | 0.078936 | 0.045776 | 0.009155 | -0.38452 | 0.022888 | 0.25635 | -0.11902 | -0.27466 | 0.059509 | -23.6343 | -0.19684 | 0.3891 | 0.33417 | -121.2204 | -121.0831 | 120.9549 | 120.7993 | -0.33874 | 121.0831 | 121.0968 | 0.29755 | -0.54932 | -0.14648 | -0.009155 | -0.20599 | 121.1334 | 120.8771 | 120.8862 | -0.26093 | 121.3303 | 121.1197 | 120.6894 | -0.86975 | 121.463 | 121.4081 | 97.4396 | -121.6782
2434.6406 | 121.8658 | -121.0464 | 0.58136 | 0.53758 | 0.051961 | 0.00047294 | 0.36823 | -0.057687 | 0.0015501 | 0.052642 | 0.70833 | 3.2476 | 0.042375 | 0.088325 | 3.132 | 0.078936 | 0.086975 | 0.082397 | -0.32501 | 0.054932 | 0.2243 | -0.09613 | -0.26093 | 0.10529 | -22.7783 | -0.14648 | 0.38452 | 0.33875 | -121.1838 | -121.0785 | 120.9503 | 120.7855 | -0.35706 | 121.1288 | 121.1014 | 0.31586 | -0.49438 | -0.13733 | -0.032043 | -0.19684 | 121.1517 | 120.9 | 120.932 | -0.24261 | 121.2708 | 121.1334 | 120.7214 | -0.84228 | 121.431 | 121.3852 | 98.2681 | -121.6599
2435.6406 | 121.8658 | -121.0556 | 0.59967 | -0.042256 | 0.027394 | 0.0090179 | 0.36609 | -0.075845 | -0.034766 | 0.034484 | 0.021682 | 3.2305 | 0.032762 | 0.096869 | 3.1203 | 0.094958 | 0.064087 | 0.14648 | -0.23346 | 0.09613 | 0.23346 | -0.09613 | -0.25635 | 0.10071 | -23.4055 | -0.091553 | 0.3891 | 0.33875 | -121.1838 | -121.0693 | 120.9595 | 120.7993 | -0.36621 | 121.2021 | 121.1517 | 0.35248 | -0.53558 | -0.12817 | -0.013733 | -0.21057 | 121.1563 | 120.9641 | 120.9778 | -0.26093 | 121.2891 | 121.1197 | 120.8221 | -0.85602 | 121.4447 | 121.3943 | 97.6501 | -121.669
2436.6406 | 121.7972 | -121.0831 | 0.59509 | 0.47654 | 0.034871 | 0.011154 | 0.3693 | -0.069436 | -0.023017 | 0.034484 | 0.52522 | 3.2241 | 0.045579 | 0.086188 | 3.1213 | 0.091753 | 0.054932 | 0.09613 | -0.31128 | 0.050354 | 0.22888 | -0.09613 | -0.24261 | 0.059509 | -23.1537 | -0.15564 | 0.3891 | 0.32959 | -121.2112 | -121.0648 | 120.9869 | 120.8405 | -0.36621 | 121.1792 | 121.1334 | 0.29297 | -0.54016 | -0.12817 | 0.018311 | -0.20599 | 121.1426 | 120.9274 | 120.9091 | -0.2655 | 121.312 | 121.138 | 120.7718 | -0.83771 | 121.4722 | 121.4127 | 97.9294 | -121.6599
2437.6406 | 121.843 | -121.0876 | 0.58594 | 0.53758 | 0.056233 | -0.012345 | 0.36609 | -0.066232 | 0.0090271 | 0.052642 | 0.89143 | 3.237 | 0.040239 | 0.087256 | 3.1427 | 0.080004 | 0.091553 | 0.086975 | -0.32501 | 0.068665 | 0.24261 | -0.091553 | -0.2655 | 0.10986 | -22.8928 | -0.15564 | 0.3891 | 0.32044 | -121.2067 | -121.0602 | 120.9961 | 120.8221 | -0.34332 | 121.1746 | 121.1563 | 0.33417 | -0.49438 | -0.11902 | 0.027465 | -0.19684 | 121.1975 | 120.932 | 120.9045 | -0.2655 | 121.3303 | 121.1792 | 120.7626 | -0.85144 | 121.4767 | 121.4081 | 98.1949 | -121.6461
2438.6406 | 121.843 | -121.0648 | 0.6134 | 0.55284 | 0.070118 | 0.01329 | 0.3725 | -0.0673 | 0.0036861 | 0.040892 | 0.38789 | 3.3032 | 0.053056 | 0.17591 | 3.1309 | 0.077868 | 0.054932 | 0.041199 | -0.25177 | 0.041199 | 0.25635 | -0.10529 | -0.2655 | 0.082397 | -21.8582 | -0.16937 | 0.3891 | 0.34332 | -121.1426 | -121.051 | 120.9595 | 120.7993 | -0.35706 | 121.106 | 121.106 | 0.3067 | -0.55847 | -0.07782 | 0.013733 | -0.2243 | 121.1472 | 120.8954 | 120.8817 | -0.27008 | 121.3211 | 121.1197 | 120.813 | -0.87891 | 121.4539 | 121.4081 | 99.2065 | -121.6644
2439.6875 | 121.8979 | -121.0464 | 0.59509 | -0.22536 | 0.040211 | 0.01329 | 0.35648 | -0.071573 | -0.021949 | 0.046233 | -0.16142 | 3.269 | 0.042375 | 0.1161 | 3.1224 | 0.072527 | 0.082397 | 0.16479 | -0.16937 | 0.10071 | 0.22888 | -0.09613 | -0.23346 | 0.041199 | -20.9885 | -0.10529 | 0.39368 | 0.33875 | -121.1746 | -121.0831 | 120.9503 | 120.813 | -0.36621 | 121.2112 | 121.1472 | 0.33417 | -0.5127 | -0.12817 | -0.036621 | -0.20142 | 121.0876 | 120.9412 | 120.9778 | -0.25635 | 121.2753 | 121.1288 | 120.8771 | -0.82855 | 121.4401 | 121.3852 | 100.058 | -121.6782
2440.6406 | 121.8384 | -121.0602 | 0.58136 | 0.62913 | 0.048756 | 0.0036769 | 0.36609 | -0.064096 | -0.0037909 | 0.038756 | 0.92195 | 3.2711 | 0.041307 | 0.12037 | 3.1459 | 0.081072 | 0.091553 | 0.09613 | -0.22888 | 0.073242 | 0.24261 | -0.082397 | -0.25635 | 0.07782 | -14.2548 | -0.14191 | 0.37537 | 0.32501 | -121.1517 | -121.0556 | 120.9778 | 120.8038 | -0.33874 | 121.1563 | 121.1334 | 0.32959 | -0.48981 | -0.091552 | 0.004578 | -0.20599 | 121.138 | 120.9183 | 120.9137 | -0.25635 | 121.3028 | 121.1517 | 120.8313 | -0.83771 | 121.4355 | 121.3852 | 106.8054 | -121.637
2441.6406 | 121.701 | -121.0968 | 0.62714 | 0.50706 | 0.065846 | 0.011154 | 0.37464 | -0.074777 | -0.00058594 | 0.046233 | 0.20479 | 3.2637 | 0.038102 | 0.10755 | 3.1416 | 0.0768 | 0.018311 | -0.027466 | -0.31586 | 0.022888 | 0.2655 | -0.11444 | -0.29755 | 0 | -15.5869 | -0.27466 | 0.41657 | 0.36621 | -121.2158 | -121.1197 | 120.9824 | 120.7993 | -0.36163 | 121.0693 | 121.1197 | 0.32043 | -0.60883 | -0.11902 | -0.022888 | -0.21057 | 121.0968 | 120.8221 | 120.845 | -0.26093 | 121.3623 | 121.1151 | 120.7809 | -0.92468 | 121.5134 | 121.463 | 105.5099 | -121.7468
2442.6406 | 121.756 | -121.1105 | 0.61798 | 0.52232 | 0.064778 | 0.0026089 | 0.36395 | -0.073709 | 0.0026181 | 0.049437 | 0.28108 | 3.2348 | 0.045579 | 0.089393 | 3.1406 | 0.085345 | -0.004578 | -0.004578 | -0.27924 | 0.004578 | 0.25635 | -0.13275 | -0.28381 | 0 | -16.5298 | -0.24719 | 0.41657 | 0.33875 | -121.2296 | -121.0876 | 120.9778 | 120.8267 | -0.36163 | 121.106 | 121.1151 | 0.28839 | -0.62256 | -0.11902 | 0.022889 | -0.20142 | 121.1105 | 120.8633 | 120.8405 | -0.27924 | 121.3669 | 121.106 | 120.8313 | -0.90179 | 121.5271 | 121.4493 | 104.5807 | -121.7056
2443.6562 | 121.8567 | -121.0693 | 0.59509 | -0.072774 | 0.032734 | 0.0015409 | 0.36823 | -0.080117 | -0.040107 | 0.039824 | -0.14616 | 3.2263 | 0.026353 | 0.081916 | 3.1203 | 0.094958 | 0.064087 | 0.17853 | -0.032043 | 0.09613 | 0.25177 | -0.10071 | -0.24719 | 0.086975 | -16.8045 | -0.11444 | 0.3891 | 0.33417 | -121.1746 | -121.0556 | 120.9686 | 120.8221 | -0.34332 | 121.2479 | 121.1655 | 0.34332 | -0.53101 | -0.10529 | 0.013733 | -0.20599 | 121.1563 | 120.9549 | 120.9412 | -0.26093 | 121.3211 | 121.1334 | 121.0373 | -0.84228 | 121.4584 | 121.4035 | 104.2648 | -121.6507
2444.6406 | 121.843 | -121.0602 | 0.59509 | 0.56809 | 0.050892 | -0.0038001 | 0.36289 | -0.053415 | -0.0059269 | 0.043029 | 0.87617 | 3.2316 | 0.035966 | 0.087256 | 3.1406 | 0.081072 | 0.086975 | 0.091553 | -0.15106 | 0.082397 | 0.23804 | -0.086975 | -0.24261 | 0.064087 | -32.1808 | -0.15106 | 0.37994 | 0.32959 | -121.1975 | -121.0602 | 120.9732 | 120.8176 | -0.35706 | 121.1517 | 121.1426 | 0.32501 | -0.50812 | -0.13733 | 0 | -0.21515 | 121.1243 | 120.9091 | 120.9091 | -0.2655 | 121.2982 | 121.1472 | 120.9091 | -0.83771 | 121.4401 | 121.3898 | 88.8794 | -121.6553
2445.6406 | 121.8384 | -121.0831 | 0.58136 | 0.65965 | 0.073323 | 0.0026089 | 0.35968 | -0.057687 | -0.0037909 | 0.047301 | 0.0522 | 3.2444 | 0.057328 | 0.096869 | 3.1459 | 0.087481 | 0.059509 | 0.068665 | -0.16479 | 0.068665 | 0.24719 | -0.091553 | -0.26093 | 0.050354 | -33.2245 | -0.14648 | 0.39368 | 0.32959 | -121.1838 | -121.0464 | 120.9915 | 120.8221 | -0.33417 | 121.1517 | 121.1517 | 0.32959 | -0.52185 | -0.10071 | 0.036621 | -0.18768 | 121.1334 | 120.9366 | 120.9 | -0.25177 | 121.3303 | 121.1426 | 120.9183 | -0.84228 | 121.4767 | 121.4127 | 87.8586 | -121.6278
2446.6719 | 121.8338 | -121.0739 | 0.59967 | 0.14085 | 0.040211 | 0.0047449 | 0.38104 | -0.072641 | -0.036902 | 0.040892 | -0.024094 | 3.2263 | 0.032762 | 0.080848 | 3.1213 | 0.085345 | 0.018311 | 0.086975 | -0.1236 | 0.07782 | 0.23804 | -0.11444 | -0.24261 | 0.064087 | -31.4346 | -0.12817 | 0.39825 | 0.3479 | -121.1472 | -121.0785 | 120.9595 | 120.8313 | -0.36163 | 121.1609 | 121.1517 | 0.32044 | -0.58136 | -0.073242 | -0.004577 | -0.20142 | 121.138 | 120.9457 | 120.9503 | -0.25177 | 121.312 | 121.0922 | 120.9503 | -0.84229 | 121.4722 | 121.4218 | 89.6393 | -121.6782
2447.6406 | 121.8018 | -121.1105 | 0.60883 | 0.61387 | 0.065846 | 0.00047294 | 0.3693 | -0.060891 | -0.00058594 | 0.046233 | 0.46419 | 3.2391 | 0.05092 | 0.081916 | 3.1341 | 0.078936 | 0.050354 | 0.018311 | -0.21057 | 0.018311 | 0.26093 | -0.10986 | -0.29297 | 0.045776 | -30.2536 | -0.20599 | 0.39825 | 0.33875 | -121.2204 | -121.0831 | 121.0007 | 120.8176 | -0.3479 | 121.1288 | 121.1288 | 0.31128 | -0.55847 | -0.10986 | 0.027466 | -0.21057 | 121.1563 | 120.9045 | 120.8771 | -0.27008 | 121.3715 | 121.1609 | 120.9 | -0.90179 | 121.5088 | 121.4493 | 90.8569 | -121.6919
2448.6406 | 121.7239 | -121.1243 | 0.63629 | 0.44602 | 0.054097 | 0.0036769 | 0.3725 | -0.065164 | -0.00058594 | 0.03662 | 0.28108 | 3.2626 | 0.048783 | 0.10114 | 3.1299 | 0.081072 | 0.032043 | -0.036621 | -0.24719 | 0.004578 | 0.28381 | -0.13275 | -0.27466 | 0 | -33.0002 | -0.27466 | 0.41657 | 0.37537 | -121.2067 | -121.1014 | 120.9915 | 120.8496 | -0.35248 | 121.0876 | 121.1288 | 0.27924 | -0.60425 | -0.082397 | 0.022889 | -0.21973 | 121.1243 | 120.8496 | 120.8267 | -0.26093 | 121.4081 | 121.1563 | 120.8771 | -0.91095 | 121.5408 | 121.4996 | 88.1241 | -121.7377
2449.6406 | 121.7377 | -121.0922 | 0.65002 | 0.43077 | 0.070118 | 0.0036769 | 0.3693 | -0.065164 | -0.00058594 | 0.054778 | 0.28108 | 3.2348 | 0.049852 | 0.11075 | 3.1395 | 0.085345 | -0.018311 | -0.032043 | -0.24719 | 0.009155 | 0.26093 | -0.1236 | -0.29755 | -0.018311 | -32.634 | -0.25635 | 0.42572 | 0.35248 | -121.2158 | -121.1197 | 120.9686 | 120.7947 | -0.3891 | 121.0602 | 121.1014 | 0.3067 | -0.66834 | -0.1236 | -0.027466 | -0.2243 | 121.0739 | 120.8359 | 120.8633 | -0.29755 | 121.3531 | 121.0739 | 120.845 | -0.94757 | 121.5179 | 121.4447 | 88.4583 | -121.7697
2450.6406 | 121.7468 | -121.1151 | 0.6134 | 0.53758 | 0.064778 | -0.0048681 | 0.36823 | -0.059823 | -0.0037909 | 0.047301 | 0.34212 | 3.3096 | 0.037034 | 0.14814 | 3.1213 | 0.089617 | -0.013733 | -0.009155 | -0.32501 | 0.004578 | 0.25635 | -0.11902 | -0.27924 | 0.013733 | -35.5133 | -0.24719 | 0.42572 | 0.36163 | -121.225 | -121.0876 | 120.9961 | 120.8359 | -0.35706 | 121.106 | 121.1197 | 0.28381 | -0.62714 | -0.10986 | 0.027466 | -0.18768 | 121.1288 | 120.8679 | 120.8405 | -0.25177 | 121.3715 | 121.1014 | 120.7901 | -0.89264 | 121.5408 | 121.4767 | 85.6018 | -121.701
2451.6406 | 121.6965 | -121.1288 | 0.64087 | 0.3087 | 0.076527 | -0.0016631 | 0.37464 | -0.059823 | -0.0059269 | 0.057982 | 0.38789 | 3.2957 | 0.066941 | 0.14814 | 3.147 | 0.08214 | -0.009155 | -0.036621 | -0.25635 | 0.009155 | 0.2655 | -0.09613 | -0.28839 | -0.068665 | -29.7409 | -0.27924 | 0.42114 | 0.3891 | -121.1792 | -121.1014 | 121.0327 | 120.8405 | -0.37537 | 121.0922 | 121.138 | 0.29755 | -0.65002 | -0.050354 | 0.027466 | -0.21973 | 121.0602 | 120.8496 | 120.8221 | -0.25177 | 121.3943 | 121.1197 | 120.8725 | -0.92926 | 121.55 | 121.5179 | 91.3879 | -121.7422
2452.6406 | 121.7834 | -121.106 | 0.60883 | 0.52232 | 0.076527 | -0.00059506 | 0.37357 | -0.058755 | -0.012336 | 0.039824 | 0.43367 | 3.237 | 0.059465 | 0.087256 | 3.1288 | 0.091753 | 0 | -0.004578 | -0.23804 | 0.009155 | 0.2655 | -0.11902 | -0.27008 | 0.018311 | -25.7263 | -0.20142 | 0.40283 | 0.36163 | -121.1838 | -121.0876 | 120.9869 | 120.8359 | -0.34332 | 121.1014 | 121.1151 | 0.27924 | -0.60883 | -0.07782 | 0.018311 | -0.20599 | 121.1243 | 120.9045 | 120.8862 | -0.24719 | 121.3715 | 121.106 | 120.8679 | -0.87891 | 121.5088 | 121.4676 | 95.3796 | -121.6965
2453.6406 | 121.8567 | -121.0876 | 0.60425 | 0.14085 | 0.027394 | 0.015426 | 0.36609 | -0.058755 | -0.059333 | 0.03662 | 0.0522 | 3.2263 | 0.038102 | 0.076575 | 3.1106 | 0.09389 | -0.009155 | 0.10529 | -0.059509 | 0.07782 | 0.23346 | -0.086975 | -0.25177 | 0.054932 | -28.4729 | -0.10071 | 0.39825 | 0.3479 | -121.1975 | -121.0648 | 121.0007 | 120.8359 | -0.37079 | 121.1929 | 121.1655 | 0.32959 | -0.6134 | -0.10986 | 0.022888 | -0.20599 | 121.1426 | 120.9869 | 120.9641 | -0.25635 | 121.3211 | 121.0785 | 121.0281 | -0.85602 | 121.4859 | 121.4355 | 92.6147 | -121.669
2454.6719 | 121.8109 | -121.0831 | 0.60883 | 0.33921 | 0.044484 | 0.012222 | 0.36395 | -0.082254 | -0.029426 | 0.037688 | 0.3116 | 3.2316 | 0.053056 | 0.084052 | 3.1203 | 0.097094 | -0.009155 | 0.068665 | -0.12817 | 0.036621 | 0.24261 | -0.086975 | -0.26093 | -0.009155 | -27.2278 | -0.14191 | 0.38452 | 0.32959 | -121.225 | -121.0968 | 120.9961 | 120.8221 | -0.36621 | 121.1517 | 121.1197 | 0.29755 | -0.61798 | -0.14191 | -0.013733 | -0.2243 | 121.0739 | 120.9412 | 120.9549 | -0.27924 | 121.3257 | 121.0739 | 120.9549 | -0.86975 | 121.4676 | 121.4127 | 93.8553 | -121.7056
2455.6406 | 121.788 | -121.0785 | 0.61798 | 0.62913 | 0.065846 | -0.0016631 | 0.36609 | -0.065164 | 0.0015501 | 0.043029 | 0.44893 | 3.2327 | 0.043443 | 0.087256 | 3.1406 | 0.08214 | 0.041199 | 0 | -0.23804 | 0.009155 | 0.27466 | -0.11902 | -0.27008 | -1.8723 | -20.7825 | -0.21515 | 0.41657 | 0.34332 | -121.2158 | -121.1014 | 120.9595 | 120.8084 | -0.34332 | 121.0785 | 121.0876 | 0.27924 | -0.57678 | -0.13733 | -0.022888 | -0.20142 | 119.2062 | 120.8633 | 120.8862 | -0.27466 | 121.3531 | 121.1197 | 120.8405 | -0.88806 | 121.4951 | 121.4218 | 100.296 | -121.7194
2456.6875 | 121.907 | -121.6232 | 0.13275 | 0.21714 | 0.023121 | 0.011154 | 0.37891 | -0.071573 | -0.034766 | 0.025939 | 0.17427 | -0.016524 | -0.033461 | -0.075097 | -0.0039789 | 0.10884 | 0.018311 | 0.073242 | -0.009155 | 0.064087 | 0.24719 | -0.11902 | -0.25635 | 0.064087 | 0.086975 | 0.068665 | 0.18768 | 0.12817 | -0.3067 | -0.25177 | 121.5042 | 121.3669 | 0.11444 | 121.6965 | 121.6873 | 0.32044 | -0.11444 | 121.3165 | 121.3715 | 0.054932 | 121.6873 | 121.6919 | 0.32044 | -0.004577 | 121.8704 | 121.6415 | 121.6141 | -0.3891 | 121.8109 | 121.7514 | 121.7102 | -0.38452
2457.6406 | 121.8933 | -121.7468 | 0.16479 | 0.26292 | 0.071187 | -0.00059506 | 0.37357 | -0.069436 | 0.022912 | 0.038756 | -0.0088351 | 0.00056556 | -0.03453 | -0.061212 | 0.028064 | 0.086413 | 0.045776 | 0 | -0.10071 | 0.022888 | 0.27008 | -0.1236 | -0.25635 | 0 | -0.013733 | -0.082397 | 0.20142 | 0.16022 | -0.28381 | -0.27924 | 121.6232 | 121.4905 | 0.10529 | 121.7468 | 121.7697 | 0.27924 | -0.11902 | 121.463 | 121.4676 | 0.036621 | 121.7468 | 121.6644 | 0.19684 | -0.004578 | 122.0169 | 121.7926 | 121.6461 | -0.42114 | 121.9482 | 121.907 | 121.7331 | -0.44403
2458.6406 | 122.0535 | -121.7468 | 0.12817 | 0.53758 | 0.051961 | 0.00047294 | 0.36823 | -0.061959 | -0.0069949 | 0.052642 | 0.32686 | -0.0026384 | -0.024916 | -0.060143 | 0.010974 | 0.10778 | 0.082397 | 0.064087 | -0.059509 | 0.050354 | 0.2243 | -0.091553 | -0.2655 | 0.09613 | 0.064087 | 0.064087 | 0.1831 | 0.1236 | -0.23346 | -0.22888 | 121.6553 | 121.4813 | 0.09613 | 121.8109 | 121.7972 | 0.31586 | -0.045777 | 121.5134 | 121.5179 | 0.054931 | 121.843 | 121.8109 | 0.29297 | -0.004578 | 121.9711 | 121.8292 | 121.6873 | -0.39368 | 121.9299 | 121.8704 | 121.8109 | -0.35706
2459.6406 | 121.9482 | -121.8201 | 0.16479 | 0.27818 | 0.067982 | -0.0016631 | 0.38745 | -0.052346 | 0.0068901 | 0.043029 | 0.082718 | 0.0080426 | -0.027053 | -0.069756 | 0.035541 | 0.1035 | 0.032043 | 0 | -0.10986 | 0.013733 | 0.25635 | -0.11902 | -0.28381 | -0.022888 | -0.018311 | -0.091553 | 0.21057 | 0.16022 | -0.28381 | -0.28381 | 121.701 | 121.5363 | 0.091553 | 121.8201 | 121.8338 | 0.29755 | -0.13275 | 121.5363 | 121.5363 | 0.045776 | 121.7972 | 121.7285 | 0.19226 | -0.004578 | 122.0764 | 121.8521 | 121.7102 | -0.44861 | 122.0306 | 121.9803 | 121.8018 | -0.44861
2460.6406 | 121.9849 | -121.8521 | 0.14191 | 0.46128 | 0.062642 | 0.011154 | 0.36395 | -0.056619 | -0.00058594 | 0.043029 | 0.34212 | 0.00056556 | -0.029189 | -0.054803 | 0.015247 | 0.10564 | 0.009155 | -0.022888 | -0.13733 | 0.009155 | 0.27008 | -0.11902 | -0.28381 | -0.013733 | -0.022888 | -0.045776 | 0.2243 | 0.16479 | -0.25177 | -0.28839 | 121.7331 | 121.5683 | 0.12817 | 121.8292 | 121.8613 | 0.29297 | -0.13275 | 121.6003 | 121.5637 | 0.082397 | 121.8384 | 121.8063 | 0.24262 | 0.022888 | 122.1222 | 121.8613 | 121.7148 | -0.42572 | 122.0764 | 122.0169 | 121.8292 | -0.4303
2461.6406 | 122.0032 | -121.8292 | 0.15564 | 0.15611 | 0.060505 | 0.0026089 | 0.36609 | -0.064096 | -0.00058594 | 0.046233 | 0.036941 | -0.0026384 | -0.021712 | -0.052667 | 0.02486 | 0.10884 | 0.059509 | 0.027466 | -0.09613 | 0.027466 | 0.26093 | -0.11444 | -0.2655 | -0.004578 | 0.013733 | -0.068665 | 0.20599 | 0.16479 | -0.26093 | -0.27466 | 121.7148 | 121.5637 | 0.10529 | 121.8567 | 121.8567 | 0.29297 | -0.096131 | 121.5683 | 121.5546 | 0.050354 | 121.8246 | 121.7606 | 0.20599 | 0.009155 | 122.0901 | 121.8887 | 121.7331 | -0.42114 | 122.0352 | 121.994 | 121.843 | -0.4303
2462.6406 | 122.0078 | -121.8567 | 0.16937 | 0.27818 | 0.054097 | 0.00047294 | 0.3725 | -0.063028 | 0.00048206 | 0.052642 | 0.11323 | 0.0059056 | -0.0078274 | -0.059075 | 0.02486 | 0.11632 | 0.009155 | 0.004578 | -0.11444 | 0.018311 | 0.25177 | -0.11902 | -0.2655 | -0.036621 | -0.013733 | -0.073242 | 0.2243 | 0.17395 | -0.25635 | -0.28381 | 121.7377 | 121.5912 | 0.082397 | 121.8613 | 121.875 | 0.28381 | -0.16022 | 121.6003 | 121.5729 | 0.054931 | 121.8201 | 121.7834 | 0.21057 | 0.004577 | 122.1085 | 121.8658 | 121.7422 | -0.43488 | 122.081 | 122.0306 | 121.843 | -0.45319
2463.6562 | 122.0947 | -121.8613 | 0.13733 | 0.36973 | 0.028462 | 0.0047449 | 0.36182 | -0.0673 | -0.046515 | 0.047301 | 0.38789 | -0.0047754 | -0.036666 | -0.052667 | 0.0034971 | 0.1238 | -0.009155 | 0.07782 | -0.036621 | 0.036621 | 0.22888 | -0.068665 | -0.24261 | 0.032043 | 0.064087 | 0.045776 | 0.19226 | 0.14648 | -0.23346 | -0.25635 | 121.7926 | 121.6187 | 0.091553 | 121.9391 | 121.8979 | 0.27924 | -0.14648 | 121.6278 | 121.6049 | 0.054932 | 121.8933 | 121.907 | 0.30212 | 0.009155 | 122.0901 | 121.8521 | 121.8246 | -0.37994 | 122.0535 | 122.0078 | 121.9254 | -0.39368
2464.6406 | 122.0627 | -121.8887 | 0.14191 | -0.10329 | 0.051961 | 0.020767 | 0.37677 | -0.052346 | 0.0090271 | 0.040892 | -0.2072 | 0.0048376 | -0.024916 | -0.053735 | 0.0067021 | 0.09923 | 0.068665 | 0.050354 | -0.054932 | 0.045776 | 0.22888 | -0.1236 | -0.29297 | 0.027466 | 0.045776 | -0.027466 | 0.2243 | 0.15106 | -0.25635 | -0.26093 | 121.7651 | 121.5958 | 0.086975 | 121.9391 | 121.9345 | 0.33874 | -0.073242 | 121.6324 | 121.6278 | 0.082397 | 121.9162 | 121.8613 | 0.23346 | 0.009155 | 122.1176 | 121.9574 | 121.8338 | -0.43488 | 122.113 | 122.0398 | 121.9345 | -0.40283
2465.6406 | 122.0901 | -121.8979 | 0.16022 | -0.10329 | 0.06371 | 0.010086 | 0.35968 | -0.061959 | 0.0058221 | 0.04196 | -0.19194 | 0.0080426 | -0.037734 | -0.066552 | 0.0099061 | 0.10564 | 0.054932 | 0.054932 | -0.041199 | 0.064087 | 0.25635 | -0.10986 | -0.28381 | 0.013733 | 0.045776 | -0.050354 | 0.22888 | 0.15564 | -0.2655 | -0.2655 | 121.788 | 121.6141 | 0.096131 | 121.9528 | 121.962 | 0.3479 | -0.10528 | 121.6324 | 121.6324 | 0.068665 | 121.9116 | 121.8475 | 0.21515 | -0.004577 | 122.1542 | 121.9528 | 121.8567 | -0.44403 | 122.1268 | 122.0535 | 121.9437 | -0.42572
2466.6406 | 122.1085 | -121.9116 | 0.16022 | -0.22536 | 0.050892 | 0.0026089 | 0.36609 | -0.063028 | -0.014472 | 0.039824 | -0.17668 | 0.0037696 | -0.02278 | -0.061212 | 0.021655 | 0.10778 | 0.027466 | 0.013733 | -0.050354 | 0.054932 | 0.2655 | -0.13275 | -0.27924 | 0 | 0.041199 | -0.018311 | 0.21515 | 0.16937 | -0.25635 | -0.28381 | 121.7789 | 121.6324 | 0.10529 | 121.9254 | 121.9666 | 0.33417 | -0.13275 | 121.6553 | 121.6278 | 0.054932 | 121.9116 | 121.8933 | 0.2655 | 0.009156 | 122.1771 | 121.9391 | 121.8613 | -0.43945 | 122.1268 | 122.081 | 121.9528 | -0.44403
2467.6406 | 122.0856 | -121.9254 | 0.16937 | -0.22536 | 0.040211 | 0.016495 | 0.36395 | -0.064096 | -0.026221 | 0.044097 | -0.29875 | -0.00050244 | -0.03987 | -0.06228 | 0.0099061 | 0.11846 | -0.045776 | -0.004578 | -0.082397 | 0.009155 | 0.27008 | -0.12817 | -0.31128 | -0.041199 | -0.009155 | -0.054932 | 0.23804 | 0.17395 | -0.25635 | -0.27924 | 121.7972 | 121.6141 | 0.10071 | 121.9208 | 121.9345 | 0.32043 | -0.21515 | 121.669 | 121.6461 | 0.068664 | 121.8842 | 121.8704 | 0.2243 | 0.004577 | 122.1954 | 121.8796 | 121.843 | -0.48065 | 122.1634 | 122.0993 | 121.9162 | -0.44861
2468.6719 | 122.2046 | -121.9208 | 0.11902 | 0.41551 | 0.058369 | -0.0027321 | 0.37677 | -0.066232 | -0.01554 | 0.044097 | 0.571 | -0.0058434 | -0.019576 | -0.064416 | 0.0056341 | 0.11739 | 0.064087 | 0.11444 | -0.027466 | 0.10071 | 0.21057 | -0.07782 | -0.23346 | 0.059509 | 0.09613 | 0.068665 | 0.17853 | 0.10986 | -0.21515 | -0.25177 | 121.843 | 121.6873 | 0.091552 | 122.0352 | 122.0215 | 0.33417 | -0.054932 | 121.7056 | 121.669 | 0.059509 | 121.9803 | 121.9894 | 0.32044 | -0.009156 | 122.1313 | 121.9849 | 121.8933 | -0.35248 | 122.0993 | 122.0306 | 122.0169 | -0.37079
2469.6406 | 122.1497 | -121.9208 | 0.16022 | -0.11855 | 0.044484 | 0.0068819 | 0.37464 | -0.070504 | -0.018744 | 0.056914 | -0.28349 | 0.00056556 | -0.042006 | -0.06228 | 0.0088381 | 0.10137 | 0.022888 | 0.041199 | -0.059509 | 0.059509 | 0.2655 | -0.12817 | -0.29297 | 0.013733 | 0.045776 | -0.022888 | 0.22888 | 0.16022 | -0.24719 | -0.27924 | 121.7926 | 121.6278 | 0.10529 | 121.962 | 121.9803 | 0.35248 | -0.13733 | 121.6736 | 121.6415 | 0.068665 | 121.9345 | 121.8979 | 0.25635 | 0 | 122.1863 | 121.9437 | 121.8613 | -0.45319 | 122.1497 | 122.081 | 121.9666 | -0.43945
2470.6406 | 122.1405 | -121.9666 | 0.17395 | -0.10329 | 0.048756 | -0.0038001 | 0.36823 | -0.074777 | -0.0080629 | 0.029143 | -0.26824 | 0.0037696 | -0.03453 | -0.06762 | 0.019519 | 0.10671 | -0.009155 | 0.004578 | -0.07782 | 0.022888 | 0.24719 | -0.12817 | -0.28839 | -0.013733 | 0.041199 | -0.027466 | 0.22888 | 0.16479 | -0.26093 | -0.27466 | 121.8384 | 121.6782 | 0.073242 | 121.9711 | 121.9894 | 0.31128 | -0.1831 | 121.7056 | 121.6919 | 0.054932 | 121.9528 | 121.9391 | 0.24719 | -0.009155 | 122.2137 | 121.9574 | 121.8887 | -0.46234 | 122.1954 | 122.1313 | 122.0078 | -0.44861
2471.6719 | 122.2595 | -121.9437 | 0.13733 | 0.53758 | 0.041279 | 0.0015409 | 0.36823 | -0.063028 | -0.024085 | 0.046233 | 0.52522 | -0.00050244 | -0.031325 | -0.061212 | 0.012042 | 0.10884 | 0.050354 | 0.10071 | -0.004578 | 0.09613 | 0.21057 | -0.086975 | -0.24261 | 0.073242 | 0.091553 | 0.064087 | 0.1831 | 0.11444 | -0.22888 | -0.22888 | 121.8567 | 121.701 | 0.073242 | 122.0444 | 122.0398 | 0.33874 | -0.086975 | 121.7148 | 121.7148 | 0.045776 | 122.0169 | 122.0078 | 0.29297 | -0.022888 | 122.1542 | 121.994 | 121.9391 | -0.37994 | 122.1268 | 122.0581 | 122.0352 | -0.36621
2472.6406 | 122.1313 | -122.0078 | 0.15106 | -0.25588 | 0.044484 | 0.0047449 | 0.37464 | -0.047006 | -0.0080629 | 0.031279 | -0.28349 | -0.0047754 | -0.031325 | -0.069756 | 0.0099061 | 0.10243 | -0.032043 | -0.009155 | -0.068665 | 0.009155 | 0.27008 | -0.10986 | -0.27924 | -0.041199 | 0.004578 | -0.050354 | 0.23804 | 0.16479 | -0.24719 | -0.29297 | 121.8979 | 121.7285 | 0.11902 | 121.9986 | 122.0169 | 0.28839 | -0.18311 | 121.7606 | 121.7148 | 0.086975 | 121.9666 | 121.9574 | 0.24261 | 0.013733 | 122.2778 | 121.9757 | 121.9391 | -0.4303 | 122.2458 | 122.1725 | 122.0123 | -0.44403
2473.6406 | 122.287 | -121.9528 | 0.1236 | 0.61387 | 0.056233 | 0.0026089 | 0.36289 | -0.0673 | -0.012336 | 0.04196 | 0.54048 | 0.00056556 | -0.020644 | -0.049462 | 0.019519 | 0.12059 | 0.068665 | 0.11444 | -0.013733 | 0.09613 | 0.21057 | -0.082397 | -0.23804 | 0.086975 | 0.086975 | 0.064087 | 0.17395 | 0.1236 | -0.21973 | -0.23346 | 121.8704 | 121.7148 | 0.086975 | 122.0673 | 122.049 | 0.33417 | -0.054931 | 121.7331 | 121.7194 | 0.050354 | 122.0398 | 122.0169 | 0.29755 | 0 | 122.1634 | 122.0215 | 121.9391 | -0.36163 | 122.1268 | 122.0764 | 122.0398 | -0.35706
2474.6406 | 122.2046 | -121.9849 | 0.16022 | -0.14907 | 0.054097 | 0.0036769 | 0.37998 | -0.058755 | 0.0079581 | 0.040892 | -0.25298 | 0.010179 | -0.032393 | -0.071893 | 0.015247 | 0.089617 | 0.018311 | 0.022888 | -0.045776 | 0.041199 | 0.26093 | -0.1236 | -0.28839 | -0.018311 | 0.059509 | -0.022888 | 0.22888 | 0.15106 | -0.24719 | -0.2655 | 121.8613 | 121.6965 | 0.10071 | 122.0078 | 122.0261 | 0.32959 | -0.14191 | 121.7377 | 121.7194 | 0.068665 | 121.9666 | 121.962 | 0.24261 | -0.009155 | 122.2458 | 122.0032 | 121.9391 | -0.44861 | 122.2137 | 122.1359 | 122.0444 | -0.42572
2475.6406 | 122.2092 | -121.9986 | 0.15564 | -0.088033 | 0.049824 | -0.0038001 | 0.37677 | -0.060891 | -0.0059269 | 0.047301 | -0.39031 | 0.0059056 | -0.032393 | -0.052667 | 0.0056341 | 0.11418 | -0.032043 | 0.013733 | -0.045776 | 0.018311 | 0.27008 | -0.12817 | -0.28839 | -0.022888 | 0.032043 | -0.036621 | 0.2243 | 0.14648 | -0.2655 | -0.27466 | 121.8704 | 121.7102 | 0.11444 | 122.0123 | 122.0169 | 0.3067 | -0.18768 | 121.7331 | 121.7239 | 0.068664 | 121.9757 | 121.962 | 0.23804 | -0.009156 | 122.2687 | 121.9666 | 121.9528 | -0.44403 | 122.2229 | 122.1451 | 122.0306 | -0.4303
2476.6406 | 122.1817 | -122.0535 | 0.17395 | -0.27114 | 0.037007 | 0.0058129 | 0.37143 | -0.076913 | -0.023017 | 0.028075 | -0.34453 | -0.00050244 | -0.036666 | -0.056939 | 0.0067021 | 0.11632 | -0.041199 | 0.027466 | -0.064087 | 0.004578 | 0.27924 | -0.12817 | -0.29755 | -0.050354 | 0.009155 | -0.059509 | 0.24719 | 0.17853 | -0.26093 | -0.28839 | 121.9254 | 121.756 | 0.10529 | 122.081 | 122.0581 | 0.30212 | -0.21515 | 121.7926 | 121.7651 | 0.073242 | 122.0032 | 121.994 | 0.22888 | 0.004578 | 122.3328 | 122.0123 | 121.9894 | -0.4715 | 122.3007 | 122.2321 | 122.0627 | -0.46234
2477.6406 | 122.1954 | -122.049 | 0.16479 | -0.2864 | 0.045552 | 0.0036769 | 0.38639 | -0.0673 | -0.024085 | 0.038756 | -0.25298 | -0.0090474 | -0.032393 | -0.059075 | 0.0045661 | 0.11418 | -0.032043 | 0.045776 | -0.041199 | 0.013733 | 0.2655 | -0.13275 | -0.27924 | -0.036621 | 0.004578 | -0.045776 | 0.2243 | 0.17395 | -0.27008 | -0.27466 | 121.9162 | 121.7697 | 0.10071 | 122.0947 | 122.0627 | 0.29297 | -0.19684 | 121.7789 | 121.7743 | 0.059509 | 122.0123 | 122.0032 | 0.22888 | 0.009155 | 122.3145 | 122.0169 | 122.0078 | -0.44403 | 122.2733 | 122.2229 | 122.0535 | -0.43945
2478.6406 | 122.2321 | -122.0444 | 0.17853 | -0.2864 | 0.038075 | 0.0079499 | 0.35327 | -0.070504 | -0.026221 | 0.03662 | -0.26824 | -0.0069114 | -0.033461 | -0.054803 | -0.0050469 | 0.10457 | 0.009155 | 0.086975 | 0 | 0.068665 | 0.25177 | -0.11902 | -0.28839 | -0.027466 | 0.045776 | -0.022888 | 0.2243 | 0.15564 | -0.23804 | -0.27008 | 121.9254 | 121.756 | 0.073242 | 122.1313 | 122.113 | 0.35706 | -0.16937 | 121.8063 | 121.7743 | 0.045776 | 122.0169 | 122.0215 | 0.24719 | -0.022888 | 122.2961 | 122.0535 | 122.0444 | -0.46692 | 122.2687 | 122.2 | 122.0901 | -0.44861
2479.6875 | 122.2183 | -122.0627 | 0.15564 | 0.41551 | 0.035939 | 0.0015409 | 0.36182 | -0.055551 | -0.00058594 | 0.045165 | 0.15901 | 0.010179 | -0.045211 | -0.053735 | 0.0088381 | 0.10564 | -0.009155 | -0.036621 | -0.1236 | 0.009155 | 0.2655 | -0.1236 | -0.27924 | -0.022888 | -0.041199 | -0.073242 | 0.21973 | 0.16479 | -0.26093 | -0.28839 | 121.9391 | 121.7834 | 0.10986 | 122.0261 | 122.0718 | 0.28839 | -0.16479 | 121.8018 | 121.7743 | 0.064087 | 122.0398 | 121.9894 | 0.21515 | 0.009155 | 122.3282 | 122.0535 | 121.9391 | -0.43488 | 122.2824 | 122.2275 | 122.0215 | -0.44403
2480.6406 | 122.2046 | -122.0764 | 0.16022 | -0.33217 | 0.026326 | 0.0090179 | 0.37143 | -0.058755 | -0.020881 | 0.04196 | -0.35979 | -0.0090474 | -0.046279 | -0.052667 | 0.0077701 | 0.1035 | -0.036621 | 0.004578 | -0.059509 | -0.009155 | 0.27924 | -0.11902 | -0.29755 | -0.059509 | 0.004578 | -0.064087 | 0.22888 | 0.16937 | -0.27008 | -0.27466 | 121.9574 | 121.7789 | 0.11902 | 122.081 | 122.0673 | 0.28839 | -0.19684 | 121.8063 | 121.8018 | 0.068665 | 122.0169 | 122.0123 | 0.21057 | 0.009156 | 122.3557 | 122.0398 | 122.0169 | -0.45776 | 122.3053 | 122.2458 | 122.081 | -0.43488
2481.6875 | 122.3145 | -122.0673 | 0.14191 | 0.20188 | 0.023121 | 0.0026089 | 0.36182 | -0.073709 | -0.029426 | 0.04196 | 0.20479 | -0.01332 | -0.031325 | -0.054803 | -0.00077485 | 0.11952 | -0.036621 | 0.07782 | -0.022888 | 0.045776 | 0.23804 | -0.082397 | -0.23346 | 0.009155 | 0.045776 | 0.041199 | 0.18768 | 0.13275 | -0.23346 | -0.24719 | 121.9849 | 121.8338 | 0.09613 | 122.1451 | 122.113 | 0.27924 | -0.17853 | 121.8338 | 121.8201 | 0.045776 | 122.0764 | 122.1085 | 0.28839 | -0.009156 | 122.3053 | 122.0306 | 122.0444 | -0.37537 | 122.2549 | 122.2 | 122.113 | -0.3891
2482.6406 | 122.374 | -122.0306 | 0.13275 | 0.064555 | 0.0049632 | 0.0068819 | 0.36502 | -0.066232 | -0.030494 | 0.033416 | -0.10039 | -0.0079794 | -0.036666 | -0.06228 | -0.00077485 | 0.11205 | 0.064087 | 0.16022 | 0.054932 | 0.086975 | 0.23346 | -0.086975 | -0.25177 | 0.082397 | 0.14648 | 0.082397 | 0.19226 | 0.11902 | -0.21515 | -0.25635 | 121.9437 | 121.7789 | 0.10071 | 122.1909 | 122.1176 | 0.33874 | -0.068664 | 121.8155 | 121.7743 | 0.05951 | 122.113 | 122.113 | 0.33875 | -0.013732 | 122.2641 | 122.0947 | 122.0856 | -0.38452 | 122.2229 | 122.1497 | 122.1771 | -0.3891
2483.6719 | 122.2641 | -122.0901 | 0.15106 | 0.12559 | 0.055165 | -0.015549 | 0.36289 | -0.047006 | 0.012231 | 0.037688 | -0.17668 | 0.0059056 | -0.03987 | -0.063348 | 0.017383 | 0.096026 | 0.073242 | 0.064087 | -0.054932 | 0.036621 | 0.27924 | -0.10986 | -0.27924 | 0.018311 | 0.027466 | -0.054932 | 0.21057 | 0.14648 | -0.24719 | -0.27008 | 121.9803 | 121.8109 | 0.12817 | 122.1542 | 122.1268 | 0.31586 | -0.07782 | 121.843 | 121.8201 | 0.059509 | 122.1085 | 122.0352 | 0.21515 | -0.004578 | 122.3694 | 122.1634 | 122.0352 | -0.4303 | 122.3007 | 122.2366 | 122.1176 | -0.42114
2484.6406 | 122.4014 | -122.0627 | 0.12817 | 0.034038 | 0.0092362 | 0.011154 | 0.36289 | -0.074777 | -0.03797 | 0.04196 | -0.16142 | -0.011183 | -0.044143 | -0.063348 | 0.0067021 | 0.11846 | 0.050354 | 0.16022 | 0.045776 | 0.082397 | 0.24261 | -0.082397 | -0.24261 | 0.11444 | 0.16022 | 0.082397 | 0.1831 | 0.11444 | -0.20599 | -0.23804 | 121.9803 | 121.8201 | 0.11444 | 122.2229 | 122.1451 | 0.32501 | -0.07782 | 121.8567 | 121.8246 | 0.054931 | 122.1771 | 122.1451 | 0.32043 | -0.013733 | 122.3053 | 122.113 | 122.1085 | -0.37079 | 122.2458 | 122.1771 | 122.2229 | -0.36621
2485.6406 | 122.3328 | -122.0901 | 0.14648 | -0.16433 | 0.01244 | 0.0090179 | 0.35434 | -0.066232 | -0.016608 | 0.032347 | -0.29875 | 0.0016336 | -0.037734 | -0.061212 | -0.0039789 | 0.10991 | 0.045776 | 0.13275 | 0.064087 | 0.086975 | 0.23346 | -0.082397 | -0.25177 | 0.041199 | 0.11444 | 0.032043 | 0.19226 | 0.13733 | -0.22888 | -0.24261 | 122.0078 | 121.8384 | 0.086975 | 122.2229 | 122.1771 | 0.33874 | -0.10071 | 121.8613 | 121.8475 | 0.045777 | 122.1313 | 122.1222 | 0.27466 | -0.009155 | 122.3236 | 122.1359 | 122.1542 | -0.39825 | 122.2824 | 122.2275 | 122.2046 | -0.3891
2486.6406 | 122.3877 | -122.0673 | 0.13733 | 0.11033 | -0.0014448 | 0.015426 | 0.37036 | -0.066232 | -0.035834 | 0.03662 | -0.024094 | -0.014388 | -0.049483 | -0.06228 | -0.00077485 | 0.10243 | 0.032043 | 0.086975 | 0.013733 | 0.082397 | 0.23804 | -0.10071 | -0.23804 | 0.064087 | 0.09613 | 0.064087 | 0.20142 | 0.1236 | -0.20599 | -0.23346 | 121.9666 | 121.8292 | 0.10071 | 122.1542 | 122.1497 | 0.32043 | -0.10529 | 121.8613 | 121.8338 | 0.064087 | 122.1313 | 122.1313 | 0.29755 | -0.013733 | 122.3053 | 122.0993 | 122.081 | -0.37537 | 122.2687 | 122.1909 | 122.1634 | -0.37079
2487.6406 | 122.4014 | -122.0856 | 0.12817 | -0.19484 | 0.011372 | 0.022903 | 0.35434 | -0.068368 | -0.025153 | 0.017394 | -0.28349 | -0.0090474 | -0.043074 | -0.063348 | -0.0018429 | 0.10884 | 0.068665 | 0.16479 | 0.050354 | 0.10071 | 0.23346 | -0.091553 | -0.23346 | 0.10071 | 0.15106 | 0.073242 | 0.18768 | 0.12817 | -0.2243 | -0.23804 | 121.994 | 121.8521 | 0.10528 | 122.2504 | 122.1863 | 0.33417 | -0.059509 | 121.8613 | 121.8475 | 0.059509 | 122.1863 | 122.1588 | 0.31128 | 0 | 122.319 | 122.1542 | 122.1359 | -0.36163 | 122.2733 | 122.2137 | 122.2366 | -0.36621
2488.6406 | 122.374 | -122.1176 | 0.13275 | 0.33921 | 0.017781 | 0.0015409 | 0.35968 | -0.066232 | -0.023017 | 0.04196 | 0.067459 | -0.014388 | -0.037734 | -0.066552 | 0.0045661 | 0.11205 | 0.004578 | 0.086975 | -0.027466 | 0.050354 | 0.23346 | -0.086975 | -0.24261 | 0.013733 | 0.041199 | 0.036621 | 0.20599 | 0.14191 | -0.21973 | -0.24719 | 122.0306 | 121.875 | 0.10071 | 122.2046 | 122.168 | 0.29297 | -0.12817 | 121.8979 | 121.8704 | 0.073243 | 122.1313 | 122.1542 | 0.28381 | 0.009156 | 122.3511 | 122.1222 | 122.0901 | -0.37537 | 122.3236 | 122.2595 | 122.1588 | -0.37994
2489.6719 | 122.3099 | -122.1405 | 0.16937 | -0.2101 | 0.027394 | 0.014358 | 0.37891 | -0.065164 | 0.020776 | 0.045165 | -0.37505 | 0.00056556 | -0.046279 | -0.063348 | 0.018451 | 0.096026 | 0.027466 | 0.013733 | -0.059509 | 0.022888 | 0.27924 | -0.1236 | -0.28381 | -0.018311 | -0.004578 | -0.050354 | 0.22888 | 0.16937 | -0.24261 | -0.28381 | 122.0169 | 121.8567 | 0.10986 | 122.1542 | 122.1634 | 0.3067 | -0.14191 | 121.8979 | 121.8567 | 0.059509 | 122.1222 | 122.0901 | 0.23346 | 0 | 122.4197 | 122.168 | 122.081 | -0.45319 | 122.3694 | 122.3099 | 122.1359 | -0.45319
2490.6406 | 122.3877 | -122.1039 | 0.15106 | 0.3087 | 0.0092362 | -0.00059506 | 0.35968 | -0.074777 | -0.021949 | 0.033416 | 0.18953 | -0.0090474 | -0.037734 | -0.061212 | -0.0018429 | 0.11098 | 0.009155 | 0.07782 | -0.013733 | 0.054932 | 0.23346 | -0.10071 | -0.23346 | 0.032043 | 0.050354 | 0.036621 | 0.19226 | 0.1236 | -0.21057 | -0.24261 | 122.0032 | 121.8704 | 0.082397 | 122.1817 | 122.1588 | 0.28839 | -0.14191 | 121.8933 | 121.8613 | 0.041199 | 122.1359 | 122.1405 | 0.27924 | -0.027466 | 122.3373 | 122.113 | 122.0901 | -0.38452 | 122.2961 | 122.2275 | 122.1542 | -0.39368
2491.6562 | 122.3419 | -122.1405 | 0.17395 | -0.10329 | 0.043416 | -0.0027321 | 0.37036 | -0.069436 | 0.010095 | 0.043029 | -0.37505 | 0.011247 | -0.03987 | -0.065484 | 0.012042 | 0.085345 | 0.041199 | 0.064087 | -0.032043 | 0.045776 | 0.26093 | -0.10529 | -0.27924 | 0.032043 | 0.045776 | -0.032043 | 0.2243 | 0.16022 | -0.23804 | -0.28381 | 122.0352 | 121.8613 | 0.086975 | 122.2046 | 122.1863 | 0.32501 | -0.13275 | 121.9025 | 121.8567 | 0.050354 | 122.1725 | 122.1085 | 0.25177 | -0.013733 | 122.4014 | 122.1817 | 122.1085 | -0.45319 | 122.3648 | 122.3007 | 122.1863 | -0.45776
2492.6406 | 122.3831 | -122.1359 | 0.13275 | 0.29344 | 0.028462 | 0.0026089 | 0.37357 | -0.068368 | -0.035834 | 0.044097 | 0.20479 | -0.0069114 | -0.037734 | -0.070825 | -0.00077485 | 0.11205 | -0.013733 | 0.07782 | -0.018311 | 0.050354 | 0.24719 | -0.10071 | -0.25177 | 0.022888 | 0.068665 | 0.032043 | 0.19684 | 0.12817 | -0.21057 | -0.24261 | 122.0352 | 121.8842 | 0.11444 | 122.2137 | 122.1863 | 0.30212 | -0.14648 | 121.9254 | 121.8933 | 0.064087 | 122.1588 | 122.168 | 0.27466 | -0.004577 | 122.3831 | 122.1222 | 122.1176 | -0.38452 | 122.3328 | 122.2641 | 122.2046 | -0.37537
2493.6406 | 122.3877 | -122.1405 | 0.11902 | 0.36973 | 0.032734 | 0.01329 | 0.37784 | -0.075845 | -0.019813 | 0.043029 | 0.18953 | -0.015456 | -0.037734 | -0.076165 | 0.00029315 | 0.11632 | 0.009155 | 0.082397 | -0.004578 | 0.045776 | 0.2243 | -0.086975 | -0.25635 | 0.032043 | 0.027466 | 0.027466 | 0.21973 | 0.13733 | -0.2243 | -0.24261 | 122.0535 | 121.8842 | 0.10529 | 122.2229 | 122.1863 | 0.30212 | -0.10986 | 121.9162 | 121.8979 | 0.10071 | 122.1725 | 122.168 | 0.27008 | 0.01831 | 122.3648 | 122.1497 | 122.1359 | -0.37537 | 122.3602 | 122.2778 | 122.168 | -0.36163
2494.6406 | 122.3969 | -122.1588 | 0.14648 | 0.46128 | 0.038075 | 0.00047294 | 0.36609 | -0.072641 | -0.024085 | 0.037688 | 0.32686 | -0.014388 | -0.030257 | -0.071893 | 0.012042 | 0.11312 | 0.018311 | 0.09613 | -0.036621 | 0.032043 | 0.21973 | -0.082397 | -0.26093 | 0.045776 | 0.032043 | 0.018311 | 0.18768 | 0.11902 | -0.21057 | -0.24261 | 122.0764 | 121.8979 | 0.073243 | 122.2549 | 122.1909 | 0.29297 | -0.12817 | 121.9482 | 121.9162 | 0.041199 | 122.2046 | 122.1771 | 0.26093 | -0.027465 | 122.3785 | 122.1771 | 122.1222 | -0.40741 | 122.3465 | 122.2778 | 122.1909 | -0.3891
2495.6406 | 122.4426 | -122.1588 | 0.14648 | 0.18663 | 0.01244 | 0.0047449 | 0.37464 | -0.077981 | -0.024085 | 0.045165 | 0.0522 | -0.010115 | -0.043074 | -0.056939 | 0.0024291 | 0.11205 | 0.009155 | 0.073242 | 0 | 0.054932 | 0.25177 | -0.09613 | -0.26093 | 0.059509 | 0.054932 | 0.064087 | 0.19684 | 0.13275 | -0.21057 | -0.24261 | 122.0627 | 121.8979 | 0.10529 | 122.2321 | 122.2137 | 0.31586 | -0.13733 | 121.9482 | 121.9162 | 0.050354 | 122.2183 | 122.2229 | 0.3067 | -0.013733 | 122.4106 | 122.168 | 122.1588 | -0.40741 | 122.3557 | 122.2916 | 122.2137 | -0.3891
2496.6406 | 122.4655 | -122.1588 | 0.10986 | 0.47654 | 0.054097 | -0.0048681 | 0.36182 | -0.068368 | 0.00048206 | 0.047301 | 0.40315 | -0.0069114 | -0.032393 | -0.06762 | 0.023792 | 0.10991 | 0.086975 | 0.14191 | -0.009155 | 0.10071 | 0.22888 | -0.086975 | -0.24261 | 0.10986 | 0.073242 | 0.059509 | 0.16937 | 0.12817 | -0.19684 | -0.23346 | 122.0718 | 121.9162 | 0.11902 | 122.3007 | 122.2595 | 0.34332 | -0.022888 | 121.962 | 121.9254 | 0.05951 | 122.2687 | 122.2183 | 0.29297 | 0.018311 | 122.3877 | 122.2458 | 122.1497 | -0.35248 | 122.3282 | 122.287 | 122.2321 | -0.34332
2497.6406 | 122.4701 | -122.168 | 0.13733 | 0.58335 | 0.038075 | 0.0090179 | 0.36395 | -0.055551 | -0.0037909 | 0.049437 | 0.43367 | -0.0015704 | -0.051619 | -0.069756 | 0.012042 | 0.094958 | 0.091553 | 0.1236 | 0.009155 | 0.086975 | 0.2243 | -0.086975 | -0.24261 | 0.11444 | 0.086975 | 0.064087 | 0.19684 | 0.10986 | -0.20599 | -0.21973 | 122.081 | 121.9254 | 0.086975 | 122.2916 | 122.2549 | 0.32959 | -0.045776 | 121.962 | 121.9482 | 0.059509 | 122.2824 | 122.2321 | 0.28381 | -0.027466 | 122.3923 | 122.2595 | 122.1771 | -0.37994 | 122.3648 | 122.2778 | 122.2549 | -0.35706
2498.6406 | 122.4747 | -122.1451 | 0.11444 | 0.70542 | 0.038075 | -0.0027321 | 0.36075 | -0.04487 | 0.0058221 | 0.048369 | 0.40315 | -0.015456 | -0.035598 | -0.056939 | 0.017383 | 0.098162 | 0.11902 | 0.11444 | 0.013733 | 0.10529 | 0.23804 | -0.07782 | -0.22888 | 0.10529 | 0.07782 | 0.041199 | 0.16937 | 0.10986 | -0.21057 | -0.22888 | 122.0673 | 121.9162 | 0.1236 | 122.2595 | 122.2504 | 0.33417 | 0.004578 | 121.9345 | 121.9162 | 0.054932 | 122.2504 | 122.1863 | 0.27008 | -0.004578 | 122.3831 | 122.2641 | 122.1588 | -0.34332 | 122.3145 | 122.2549 | 122.2229 | -0.34332
2499.6406 | 122.4747 | -122.1497 | 0.15564 | 0.53758 | 0.041279 | 0.0015409 | 0.35968 | -0.070504 | 0.0026181 | 0.057982 | 0.34212 | -0.010115 | -0.020644 | -0.077233 | 0.02486 | 0.094958 | 0.086975 | 0.11902 | -0.004578 | 0.082397 | 0.23346 | -0.091553 | -0.24719 | 0.11902 | 0.07782 | 0.050354 | 0.17395 | 0.11444 | -0.21515 | -0.23804 | 122.0581 | 121.9025 | 0.077819 | 122.2687 | 122.2321 | 0.32959 | -0.068665 | 121.9345 | 121.9116 | 0.01831 | 122.2687 | 122.2 | 0.28839 | -0.041199 | 122.3831 | 122.2366 | 122.1451 | -0.40283 | 122.3236 | 122.2641 | 122.2275 | -0.39368
2500.6406 | 122.4792 | -122.1588 | 0.11902 | 0.46128 | 0.070118 | 0.0058129 | 0.36395 | -0.069436 | 0.0026181 | 0.043029 | 0.32686 | 0.0027016 | -0.030257 | -0.059075 | 0.021655 | 0.11418 | 0.041199 | 0.054932 | -0.045776 | 0.050354 | 0.24261 | -0.10071 | -0.24719 | 0.10071 | 0.059509 | 0.032043 | 0.20142 | 0.11902 | -0.20142 | -0.24719 | 122.0581 | 121.9116 | 0.1236 | 122.2137 | 122.2092 | 0.29755 | -0.07782 | 121.9574 | 121.9116 | 0.082397 | 122.2595 | 122.1909 | 0.27924 | 0 | 122.4014 | 122.2 | 122.113 | -0.36621 | 122.3602 | 122.2778 | 122.2183 | -0.36621
2501.6406 | 122.4701 | -122.1909 | 0.15564 | 0.55284 | 0.04662 | 0.0047449 | 0.36716 | -0.056619 | 0.00048206 | 0.046233 | 0.41841 | -0.0058434 | -0.020644 | -0.063348 | 0.015247 | 0.11418 | 0.022888 | 0.018311 | -0.073242 | 0.013733 | 0.27008 | -0.10529 | -0.2655 | 0.050354 | 0.004578 | -0.013733 | 0.21057 | 0.14648 | -0.21057 | -0.24261 | 122.0856 | 121.9254 | 0.11444 | 122.2092 | 122.2046 | 0.27924 | -0.13275 | 121.9803 | 121.9482 | 0.054931 | 122.2412 | 122.1771 | 0.22888 | -0.009156 | 122.4609 | 122.2137 | 122.1176 | -0.42114 | 122.4014 | 122.3373 | 122.1954 | -0.39826
2502.6719 | 122.5388 | -122.2 | 0.13275 | 0.049296 | 0.048756 | 0.0047449 | 0.36182 | -0.069436 | -0.035834 | 0.025939 | -0.054612 | -0.0047754 | -0.033461 | -0.07937 | -0.0082519 | 0.10457 | 0.09613 | 0.14191 | 0.068665 | 0.11444 | 0.23804 | -0.086975 | -0.25177 | 0.073242 | 0.17395 | 0.086975 | 0.19684 | 0.12817 | -0.20599 | -0.20599 | 122.113 | 121.9482 | 0.10529 | 122.3419 | 122.3145 | 0.36621 | -0.036621 | 121.994 | 121.994 | 0.064087 | 122.2733 | 122.287 | 0.29297 | -0.004577 | 122.438 | 122.2961 | 122.2687 | -0.38452 | 122.3969 | 122.3282 | 122.374 | -0.33875
2503.6406 | 122.3831 | -122.2321 | 0.16937 | 0.41551 | 0.06371 | -0.00059506 | 0.38104 | -0.073709 | 0.0090271 | 0.05371 | 0.26582 | 0.0037696 | -0.01744 | -0.065484 | 0.014179 | 0.10671 | 0.022888 | -0.050354 | -0.11444 | 0.004578 | 0.27466 | -0.11444 | -0.28381 | 0.004578 | -0.013733 | -0.073242 | 0.22888 | 0.16022 | -0.24719 | -0.27924 | 122.1176 | 121.9482 | 0.10529 | 122.1817 | 122.2366 | 0.28839 | -0.14649 | 121.9849 | 121.9528 | 0.059509 | 122.2366 | 122.1588 | 0.20599 | -0.009156 | 122.5067 | 122.2549 | 122.1176 | -0.45319 | 122.4609 | 122.3923 | 122.2183 | -0.44861
2504.6406 | 122.438 | -122.2458 | 0.16022 | 0.4918 | 0.058369 | 0.0026089 | 0.36823 | -0.058755 | -0.0037909 | 0.055846 | 0.41841 | 0.010179 | -0.027053 | -0.052667 | 0.018451 | 0.10457 | 0.018311 | -0.018311 | -0.10986 | 0 | 0.27924 | -0.11444 | -0.27924 | 0.041199 | 0.004578 | -0.027466 | 0.20599 | 0.14648 | -0.22888 | -0.24719 | 122.1313 | 121.9666 | 0.11902 | 122.2275 | 122.2458 | 0.27924 | -0.14191 | 122.0169 | 121.9986 | 0.045777 | 122.287 | 122.2183 | 0.21973 | -0.013733 | 122.525 | 122.2641 | 122.1359 | -0.43945 | 122.4518 | 122.3923 | 122.2504 | -0.40741
2505.6406 | 122.4106 | -122.2504 | 0.13275 | 0.50706 | 0.060505 | -0.0038001 | 0.3693 | -0.070504 | -0.0016549 | 0.057982 | 0.26582 | 0.0048376 | -0.029189 | -0.053735 | 0.022724 | 0.10778 | 0.018311 | -0.013733 | -0.1236 | 0 | 0.27466 | -0.1236 | -0.28381 | -0.004578 | -0.004578 | -0.054932 | 0.22888 | 0.14648 | -0.25635 | -0.25635 | 122.1268 | 121.9666 | 0.14191 | 122.2366 | 122.2504 | 0.28381 | -0.11444 | 121.994 | 121.994 | 0.096131 | 122.2458 | 122.1954 | 0.20142 | 0.013733 | 122.525 | 122.2687 | 122.1268 | -0.41656 | 122.4792 | 122.3969 | 122.2458 | -0.3891
2506.6562 | 122.5708 | -122.2321 | 0.13275 | 0.049296 | 0.020985 | 0.0036769 | 0.3725 | -0.070504 | -0.042243 | 0.034484 | -0.054612 | -0.0079794 | -0.036666 | -0.059075 | -0.0061159 | 0.12166 | 0.045776 | 0.15106 | 0.068665 | 0.07782 | 0.23804 | -0.091553 | -0.22888 | 0.07782 | 0.16022 | 0.082397 | 0.17395 | 0.12817 | -0.20599 | -0.22888 | 122.1405 | 122.0032 | 0.10529 | 122.3831 | 122.3099 | 0.3067 | -0.086975 | 122.0261 | 122.0032 | 0.041199 | 122.3099 | 122.3145 | 0.31128 | -0.004577 | 122.4701 | 122.2778 | 122.3007 | -0.36163 | 122.406 | 122.3602 | 122.3923 | -0.36163
2507.6406 | 122.406 | -122.2733 | 0.16479 | 0.20188 | 0.062642 | 0.0026089 | 0.36502 | -0.063028 | 0.01864 | 0.055846 | 0.28108 | -0.0058434 | -0.028121 | -0.065484 | 0.0302 | 0.1035 | 0 | -0.068665 | -0.14648 | -0.004578 | 0.26093 | -0.10986 | -0.27924 | -0.018311 | -0.022888 | -0.082397 | 0.21515 | 0.16479 | -0.23346 | -0.26093 | 122.1634 | 121.994 | 0.09613 | 122.2046 | 122.2687 | 0.27466 | -0.16479 | 122.0398 | 122.0123 | 0.050354 | 122.2549 | 122.1909 | 0.17853 | 0 | 122.5342 | 122.2733 | 122.1268 | -0.44403 | 122.4884 | 122.438 | 122.2504 | -0.42572
2508.6406 | 122.4838 | -122.2687 | 0.13733 | 0.69017 | 0.057301 | 0.0090179 | 0.37464 | -0.066232 | -0.0016549 | 0.046233 | 0.37263 | -0.0015704 | -0.030257 | -0.06762 | 0.018451 | 0.11846 | 0.032043 | 0.009155 | -0.082397 | 0.027466 | 0.27008 | -0.10986 | -0.25177 | 0.054932 | 0.027466 | -0.009155 | 0.20599 | 0.13733 | -0.23346 | -0.24719 | 122.1588 | 122.0169 | 0.13275 | 122.2778 | 122.2961 | 0.27924 | -0.10529 | 122.0352 | 122.0215 | 0.068665 | 122.3236 | 122.2595 | 0.23804 | 0 | 122.5388 | 122.3007 | 122.1863 | -0.3891 | 122.4747 | 122.406 | 122.2961 | -0.38452
2509.6406 | 122.4655 | -122.2733 | 0.13733 | 0.47654 | 0.079732 | -0.00059506 | 0.36395 | -0.068368 | -0.0091309 | 0.052642 | 0.43367 | 0.010179 | -0.024916 | -0.066552 | 0.022724 | 0.11632 | 0.009155 | -0.022888 | -0.10071 | 0.004578 | 0.27466 | -0.11902 | -0.26093 | 0.013733 | 0.004578 | -0.032043 | 0.20142 | 0.16022 | -0.23804 | -0.2243 | 122.1542 | 122.0123 | 0.13733 | 122.2504 | 122.2778 | 0.2655 | -0.12817 | 122.0352 | 122.0489 | 0.064087 | 122.287 | 122.2412 | 0.19226 | 0.022888 | 122.5479 | 122.2824 | 122.1725 | -0.39825 | 122.4747 | 122.4335 | 122.2778 | -0.36163
2510.6406 | 122.4197 | -122.2916 | 0.16937 | 0.33921 | 0.064778 | -0.014481 | 0.37464 | -0.060891 | 0.0090271 | 0.048369 | -0.10039 | 0.0080426 | -0.01744 | -0.064416 | 0.025928 | 0.097094 | 0.045776 | 0.004578 | -0.064087 | 0.027466 | 0.25635 | -0.10986 | -0.27466 | 0 | 0.004578 | -0.054932 | 0.22888 | 0.14648 | -0.23346 | -0.25635 | 122.1817 | 122.0169 | 0.086975 | 122.2961 | 122.319 | 0.30212 | -0.1236 | 122.0581 | 122.0352 | 0.059509 | 122.2916 | 122.2366 | 0.20142 | -0.022889 | 122.5479 | 122.3373 | 122.2275 | -0.44403 | 122.5204 | 122.438 | 122.2961 | -0.42572
2511.6406 | 122.4152 | -122.2733 | 0.16479 | 0.26292 | 0.084004 | -0.00059506 | 0.37677 | -0.066232 | 0.0036861 | 0.054778 | 0.15901 | 0.016588 | -0.03987 | -0.06762 | 0.019519 | 0.10457 | 0.013733 | -0.013733 | -0.086975 | 0.022888 | 0.25177 | -0.10071 | -0.28839 | -0.032043 | -0.013733 | -0.07782 | 0.21515 | 0.16479 | -0.24261 | -0.27466 | 122.1725 | 121.9849 | 0.086975 | 122.2595 | 122.2961 | 0.31128 | -0.15106 | 122.0306 | 121.9986 | 0.050354 | 122.2412 | 122.1954 | 0.19684 | 0 | 122.525 | 122.287 | 122.1863 | -0.45319 | 122.4884 | 122.438 | 122.2595 | -0.43945
2512.6406 | 122.4243 | -122.2733 | 0.17853 | 0.32395 | 0.077595 | 0.0068819 | 0.38104 | -0.055551 | -0.00058594 | 0.045165 | 0.0064239 | -0.0037074 | -0.027053 | -0.058007 | 0.026996 | 0.10991 | 0.009155 | 0.013733 | -0.07782 | 0.027466 | 0.27008 | -0.11902 | -0.2655 | -0.027466 | 0.004578 | -0.086975 | 0.23804 | 0.15564 | -0.24719 | -0.27924 | 122.1542 | 122.0078 | 0.091553 | 122.287 | 122.3007 | 0.29297 | -0.16937 | 122.0261 | 121.994 | 0.059509 | 122.2458 | 122.1863 | 0.19226 | -0.022888 | 122.5433 | 122.2824 | 122.1954 | -0.44403 | 122.5113 | 122.4289 | 122.2778 | -0.45776
2513.6875 | 122.5525 | -122.2961 | 0.1236 | 0.17137 | 0.030598 | 0.0058129 | 0.3725 | -0.068368 | -0.051856 | 0.033416 | 0.2353 | -0.011183 | -0.025985 | -0.066552 | -0.0093199 | 0.12059 | -0.027466 | 0.050354 | -0.013733 | 0.041199 | 0.25177 | -0.086975 | -0.27466 | 0.018311 | 0.091553 | 0.068665 | 0.18768 | 0.1236 | -0.2243 | -0.23804 | 122.2092 | 122.0215 | 0.12817 | 122.3465 | 122.3373 | 0.31586 | -0.15106 | 122.0718 | 122.0581 | 0.064087 | 122.3145 | 122.3648 | 0.3067 | 0 | 122.5479 | 122.2687 | 122.2824 | -0.39825 | 122.4838 | 122.4197 | 122.3877 | -0.36163
2514.6406 | 122.4701 | -122.3053 | 0.16479 | 0.14085 | 0.070118 | -0.00059506 | 0.37891 | -0.068368 | 0.0090271 | 0.040892 | -0.10039 | 0.0037696 | -0.03987 | -0.063348 | 0.023792 | 0.096026 | 0.054932 | 0.045776 | -0.041199 | 0.018311 | 0.26093 | -0.09613 | -0.27466 | 0.004578 | 0.009155 | -0.059509 | 0.22888 | 0.16479 | -0.24261 | -0.25635 | 122.2092 | 122.0306 | 0.09613 | 122.3511 | 122.3236 | 0.29297 | -0.10986 | 122.0627 | 122.0489 | 0.064087 | 122.3099 | 122.2458 | 0.19684 | 0 | 122.5662 | 122.3602 | 122.2641 | -0.43945 | 122.5342 | 122.4701 | 122.3145 | -0.42114
2515.6406 | 122.4655 | -122.3099 | 0.14648 | 0.11033 | 0.048756 | 0.0068819 | 0.3725 | -0.065164 | -0.0037909 | 0.04196 | -0.039353 | 0.010179 | -0.038802 | -0.048394 | 0.016315 | 0.098162 | 0.073242 | 0.050354 | -0.036621 | 0.045776 | 0.26093 | -0.11444 | -0.27008 | 0.004578 | 0.027466 | -0.036621 | 0.21973 | 0.15564 | -0.23804 | -0.25177 | 122.1954 | 122.0398 | 0.11444 | 122.3602 | 122.3557 | 0.31586 | -0.073242 | 122.0718 | 122.0581 | 0.073243 | 122.3145 | 122.2733 | 0.21515 | 0.009156 | 122.5708 | 122.3831 | 122.2733 | -0.41657 | 122.5296 | 122.4655 | 122.3373 | -0.39825
2516.6406 | 122.4792 | -122.3053 | 0.16479 | 0.11033 | 0.064778 | -0.0059361 | 0.36289 | -0.063028 | 0.0036861 | 0.052642 | 0.11323 | 0.0027016 | -0.025985 | -0.063348 | 0.016315 | 0.10564 | 0.032043 | 0.018311 | -0.064087 | 0.032043 | 0.26093 | -0.10071 | -0.25635 | -0.022888 | 0.013733 | -0.054932 | 0.2243 | 0.16479 | -0.21057 | -0.25177 | 122.2046 | 122.0489 | 0.09613 | 122.3236 | 122.3373 | 0.28839 | -0.13275 | 122.0947 | 122.0535 | 0.059509 | 122.2824 | 122.2504 | 0.19684 | 0 | 122.5662 | 122.3373 | 122.2412 | -0.42114 | 122.5296 | 122.4701 | 122.319 | -0.41656
2517.6406 | 122.5021 | -122.3282 | 0.16022 | 0.064555 | 0.057301 | -0.00059506 | 0.36395 | -0.056619 | -0.0069949 | 0.052642 | -0.22246 | 0.0016336 | -0.024916 | -0.054803 | 0.015247 | 0.11525 | 0.022888 | 0.059509 | -0.018311 | 0.045776 | 0.27008 | -0.12817 | -0.27008 | 0.004578 | 0.050354 | -0.022888 | 0.21057 | 0.16479 | -0.23804 | -0.25177 | 122.2 | 122.0581 | 0.10986 | 122.3877 | 122.374 | 0.31586 | -0.13733 | 122.0901 | 122.0764 | 0.050354 | 122.3328 | 122.3053 | 0.22888 | 0.004578 | 122.5983 | 122.3511 | 122.3099 | -0.4303 | 122.5388 | 122.493 | 122.3785 | -0.41199
2518.6406 | 122.493 | -122.3373 | 0.16022 | 0.27818 | 0.078663 | -0.0080721 | 0.37036 | -0.070504 | 0.0036861 | 0.045165 | 0.0522 | -0.00050244 | -0.021712 | -0.076165 | 0.014179 | 0.11312 | -0.004578 | 0.004578 | -0.064087 | 0.022888 | 0.2655 | -0.1236 | -0.2655 | -0.045776 | 0.009155 | -0.064087 | 0.20599 | 0.17853 | -0.21973 | -0.25635 | 122.2137 | 122.0718 | 0.10529 | 122.3419 | 122.3602 | 0.28839 | -0.16479 | 122.1176 | 122.081 | 0.045777 | 122.2916 | 122.2733 | 0.19226 | 0.018311 | 122.6028 | 122.3328 | 122.2733 | -0.42572 | 122.5433 | 122.5159 | 122.3465 | -0.41657
2519.6406 | 122.5067 | -122.3511 | 0.15564 | 0.018779 | 0.075459 | 0.0047449 | 0.37143 | -0.064096 | -0.0059269 | 0.050505 | -0.14616 | -0.0015704 | -0.030257 | -0.077233 | 0.016315 | 0.10457 | 0.032043 | 0.054932 | -0.009155 | 0.041199 | 0.27924 | -0.086975 | -0.29297 | 0 | 0.050354 | -0.032043 | 0.21515 | 0.16022 | -0.23346 | -0.25177 | 122.2641 | 122.0581 | 0.1236 | 122.406 | 122.3923 | 0.33417 | -0.1236 | 122.1176 | 122.0993 | 0.059509 | 122.3511 | 122.319 | 0.21973 | 0.004577 | 122.6303 | 122.3831 | 122.3419 | -0.44861 | 122.5662 | 122.5113 | 122.4014 | -0.40741
2520.6406 | 122.525 | -122.3053 | 0.15564 | 0.049296 | 0.087208 | -0.0070041 | 0.38852 | -0.069436 | -0.0059269 | 0.040892 | -0.06987 | 0.0091106 | -0.025985 | -0.065484 | 0.015247 | 0.1003 | 0.022888 | 0.045776 | -0.027466 | 0.036621 | 0.27008 | -0.10986 | -0.27008 | 0.022888 | 0.045776 | -0.027466 | 0.21057 | 0.16479 | -0.23346 | -0.2655 | 122.1954 | 122.0352 | 0.11444 | 122.3511 | 122.3419 | 0.3067 | -0.13275 | 122.0718 | 122.0398 | 0.054931 | 122.3282 | 122.2778 | 0.23804 | 0.009155 | 122.5754 | 122.3282 | 122.2778 | -0.42572 | 122.5159 | 122.4701 | 122.3511 | -0.42114
2521.6406 | 122.493 | -122.3465 | 0.15106 | 0.15611 | 0.061574 | 0.015426 | 0.38532 | -0.064096 | -0.0027229 | 0.052642 | 0.12849 | -0.0037074 | -0.024916 | -0.075097 | 0.016315 | 0.10671 | 0 | 0.022888 | -0.068665 | 0.045776 | 0.27008 | -0.091553 | -0.28839 | -0.050354 | 0 | -0.068665 | 0.2243 | 0.17853 | -0.23804 | -0.25177 | 122.2549 | 122.0581 | 0.11902 | 122.3694 | 122.3923 | 0.33417 | -0.15106 | 122.1085 | 122.0947 | 0.073242 | 122.2961 | 122.2778 | 0.1831 | 0.027466 | 122.6166 | 122.3465 | 122.2778 | -0.43945 | 122.5708 | 122.525 | 122.3465 | -0.40283
2522.6406 | 122.5479 | -122.3419 | 0.16937 | -0.2101 | 0.048756 | 0.00047294 | 0.38852 | -0.054483 | -0.012336 | 0.051574 | -0.32927 | 0.00056556 | -0.028121 | -0.060143 | 0.0067021 | 0.11846 | -0.018311 | 0.036621 | -0.027466 | 0.045776 | 0.2655 | -0.13275 | -0.29297 | -0.018311 | 0.068665 | -0.027466 | 0.2243 | 0.16479 | -0.24261 | -0.27466 | 122.2092 | 122.049 | 0.09613 | 122.3785 | 122.3877 | 0.33874 | -0.18768 | 122.0993 | 122.0673 | 0.054931 | 122.3236 | 122.3145 | 0.24719 | -0.004578 | 122.6074 | 122.3236 | 122.3145 | -0.46234 | 122.5662 | 122.5067 | 122.4106 | -0.44403
2523.6406 | 122.5571 | -122.3557 | 0.13733 | -0.14907 | 0.042347 | -0.0016631 | 0.37464 | -0.052346 | -0.010199 | 0.031279 | -0.22246 | -0.0026384 | -0.03987 | -0.051599 | 0.0099061 | 0.11525 | -0.027466 | 0 | -0.054932 | 0.022888 | 0.27466 | -0.10986 | -0.29297 | -0.036621 | 0.050354 | -0.013733 | 0.23346 | 0.16022 | -0.22888 | -0.25177 | 122.2458 | 122.0627 | 0.13733 | 122.3557 | 122.3785 | 0.31586 | -0.16479 | 122.1268 | 122.1039 | 0.09613 | 122.319 | 122.3419 | 0.23804 | 0.022888 | 122.6303 | 122.3282 | 122.3007 | -0.4303 | 122.5891 | 122.5159 | 122.406 | -0.3891
2524.6406 | 122.4976 | -122.3602 | 0.16937 | 0.3087 | 0.081868 | -0.0016631 | 0.36395 | -0.066232 | 0.0026181 | 0.03662 | -0.0088351 | 0.0048376 | -0.016372 | -0.051599 | 0.025928 | 0.10671 | 0 | 0.009155 | -0.073242 | 0.036621 | 0.25177 | -0.10986 | -0.27008 | -0.041199 | -0.009155 | -0.068665 | 0.23346 | 0.17853 | -0.24261 | -0.26093 | 122.2504 | 122.0901 | 0.082397 | 122.3694 | 122.3969 | 0.3067 | -0.16937 | 122.1176 | 122.0993 | 0.064086 | 122.319 | 122.2916 | 0.19226 | 0.009155 | 122.612 | 122.3602 | 122.287 | -0.43945 | 122.5937 | 122.5388 | 122.3511 | -0.4303
2525.6406 | 122.5433 | -122.3557 | 0.16022 | 0.14085 | 0.056233 | 0.0047449 | 0.35861 | -0.058755 | -0.0037909 | 0.039824 | -0.10039 | 0.0059056 | -0.015303 | -0.055871 | 0.0099061 | 0.10991 | 0.027466 | 0.050354 | -0.050354 | 0.050354 | 0.2655 | -0.10529 | -0.27008 | 0.009155 | 0.032043 | -0.045776 | 0.19684 | 0.14191 | -0.23804 | -0.26093 | 122.2504 | 122.0856 | 0.10529 | 122.406 | 122.406 | 0.32044 | -0.13275 | 122.1176 | 122.0947 | 0.036621 | 122.3648 | 122.3099 | 0.21515 | -0.01831 | 122.6212 | 122.3831 | 122.3053 | -0.4303 | 122.5525 | 122.4976 | 122.3877 | -0.42114
2526.6406 | 122.5662 | -122.3602 | 0.16022 | -0.17959 | 0.057301 | 0.0047449 | 0.37143 | -0.075845 | -0.013404 | 0.046233 | -0.29875 | -0.0058434 | -0.038802 | -0.056939 | 0.012042 | 0.10457 | -0.036621 | 0.013733 | -0.073242 | 0.036621 | 0.27008 | -0.12817 | -0.27924 | -0.032043 | 0.022888 | -0.032043 | 0.21057 | 0.16479 | -0.24719 | -0.25177 | 122.2321 | 122.081 | 0.10986 | 122.374 | 122.3969 | 0.31586 | -0.19684 | 122.113 | 122.1085 | 0.050354 | 122.3282 | 122.3282 | 0.21973 | 0.004578 | 122.6303 | 122.3236 | 122.287 | -0.43945 | 122.5708 | 122.525 | 122.3831 | -0.41199
2527.6406 | 122.5525 | -122.3465 | 0.15564 | 0.079814 | 0.050892 | -0.0016631 | 0.3725 | -0.065164 | 0.0026181 | 0.039824 | 0.0064239 | 0.0080426 | -0.038802 | -0.070825 | 0.019519 | 0.10884 | 0.032043 | 0.050354 | -0.036621 | 0.045776 | 0.2655 | -0.10986 | -0.2655 | -0.009155 | 0.036621 | -0.036621 | 0.21515 | 0.15106 | -0.22888 | -0.25177 | 122.2366 | 122.081 | 0.10986 | 122.3969 | 122.3923 | 0.31128 | -0.1236 | 122.1176 | 122.0947 | 0.059509 | 122.3373 | 122.3099 | 0.21515 | -0.004578 | 122.612 | 122.3785 | 122.3099 | -0.42114 | 122.5616 | 122.4976 | 122.3831 | -0.40741
2528.6406 | 122.5113 | -122.3969 | 0.17395 | -0.042256 | 0.033803 | 0.0047449 | 0.37891 | -0.070504 | -0.034766 | 0.022734 | -0.39031 | -0.0026384 | -0.033461 | -0.071893 | -0.0029109 | 0.12166 | -0.054932 | 0.022888 | -0.073242 | 0.004578 | 0.25177 | -0.12817 | -0.27924 | -0.064087 | 0.009155 | -0.041199 | 0.2243 | 0.17395 | -0.24719 | -0.27466 | 122.2687 | 122.1176 | 0.07782 | 122.4197 | 122.4014 | 0.28381 | -0.22888 | 122.1497 | 122.1222 | 0.050354 | 122.3328 | 122.3557 | 0.23346 | 0 | 122.6486 | 122.3419 | 122.3236 | -0.45319 | 122.6212 | 122.5708 | 122.406 | -0.44861
2529.6406 | 122.525 | -122.3831 | 0.16022 | -0.30166 | 0.049824 | 0.011154 | 0.36823 | -0.071573 | -0.021949 | 0.039824 | -0.32927 | -0.0026384 | -0.027053 | -0.058007 | 0.0024291 | 0.10457 | -0.050354 | -0.013733 | -0.073242 | 0.009155 | 0.27008 | -0.13275 | -0.29297 | -0.041199 | 0 | -0.054932 | 0.2655 | 0.17853 | -0.25177 | -0.26093 | 122.2504 | 122.0901 | 0.10986 | 122.3694 | 122.3923 | 0.30212 | -0.21057 | 122.1313 | 122.1222 | 0.10529 | 122.3419 | 122.3282 | 0.20599 | 0.018311 | 122.6532 | 122.3328 | 122.3099 | -0.45319 | 122.6486 | 122.5616 | 122.3831 | -0.42114
2530.6406 | 122.5891 | -122.3785 | 0.16937 | -0.16433 | 0.060505 | 0.0068819 | 0.37036 | -0.068368 | -0.0091309 | 0.032347 | -0.23772 | 0.0027016 | -0.033461 | -0.054803 | 0.0077701 | 0.10243 | 0.022888 | 0.050354 | -0.027466 | 0.045776 | 0.27008 | -0.10529 | -0.27466 | -0.004578 | 0.045776 | -0.041199 | 0.21057 | 0.15564 | -0.24719 | -0.26093 | 122.2733 | 122.1039 | 0.10071 | 122.4289 | 122.4243 | 0.32043 | -0.14649 | 122.1313 | 122.1176 | 0.041198 | 122.374 | 122.3373 | 0.21973 | -0.013733 | 122.6486 | 122.4014 | 122.3511 | -0.44403 | 122.5891 | 122.5342 | 122.4243 | -0.4303
2531.6406 | 122.5662 | -122.4152 | 0.16479 | -0.27114 | 0.050892 | 0.017563 | 0.36395 | -0.058755 | -0.023017 | 0.030211 | -0.34453 | -0.0026384 | -0.03987 | -0.064416 | 0.0034971 | 0.11952 | -0.045776 | -0.004578 | -0.082397 | 0 | 0.27466 | -0.11902 | -0.28381 | -0.064087 | 0.004578 | -0.064087 | 0.22888 | 0.17395 | -0.24719 | -0.27466 | 122.2961 | 122.1313 | 0.10986 | 122.4106 | 122.4152 | 0.28381 | -0.21057 | 122.168 | 122.1405 | 0.064087 | 122.3511 | 122.3511 | 0.21057 | 0.009155 | 122.6898 | 122.3694 | 122.3328 | -0.44861 | 122.644 | 122.5891 | 122.4197 | -0.43945
2532.6406 | 122.5571 | -122.406 | 0.19226 | -0.30166 | 0.042347 | 0.019699 | 0.38852 | -0.066232 | -0.031562 | 0.033416 | -0.28349 | -0.012251 | -0.031325 | -0.068688 | 0.0034971 | 0.11312 | -0.054932 | 0 | -0.091553 | 0.004578 | 0.27924 | -0.10529 | -0.28839 | -0.059509 | 0.004578 | -0.073242 | 0.22888 | 0.16937 | -0.23804 | -0.25177 | 122.3007 | 122.1176 | 0.086975 | 122.406 | 122.4106 | 0.29297 | -0.24719 | 122.168 | 122.1542 | 0.036621 | 122.3465 | 122.3328 | 0.17853 | -0.022888 | 122.6852 | 122.3511 | 122.3145 | -0.48065 | 122.6349 | 122.5754 | 122.4106 | -0.44403
2533.6406 | 122.5937 | -122.406 | 0.16022 | -0.16433 | 0.048756 | -0.0027321 | 0.36075 | -0.066232 | -0.011268 | 0.044097 | -0.32927 | -0.00050244 | -0.038802 | -0.065484 | 0.02486 | 0.10564 | 0.013733 | 0.059509 | -0.07782 | 0.045776 | 0.27008 | -0.10986 | -0.28381 | -0.004578 | 0.045776 | -0.032043 | 0.19684 | 0.1831 | -0.21973 | -0.25177 | 122.2961 | 122.1222 | 0.10986 | 122.4655 | 122.4518 | 0.32959 | -0.14648 | 122.1863 | 122.1542 | 0.036621 | 122.4014 | 122.374 | 0.21973 | 0.022888 | 122.6761 | 122.4197 | 122.3282 | -0.44403 | 122.6028 | 122.5891 | 122.4518 | -0.41199
2534.6406 | 122.5479 | -122.4106 | 0.16479 | -0.19484 | 0.042347 | 0.0058129 | 0.36823 | -0.071573 | -0.025153 | 0.032347 | -0.35979 | -0.0015704 | -0.036666 | -0.058007 | -0.0039789 | 0.11952 | -0.045776 | 0.013733 | -0.091553 | 0.013733 | 0.24719 | -0.11444 | -0.27008 | -0.059509 | -0.009155 | -0.050354 | 0.21973 | 0.16479 | -0.23804 | -0.27008 | 122.2961 | 122.1405 | 0.082397 | 122.4243 | 122.4243 | 0.28381 | -0.21057 | 122.1725 | 122.1405 | 0.054932 | 122.3511 | 122.3602 | 0.21973 | 0 | 122.6578 | 122.3648 | 122.319 | -0.43488 | 122.6303 | 122.5754 | 122.4014 | -0.43488
2535.6406 | 122.5525 | -122.4243 | 0.1831 | -0.36269 | 0.042347 | 0.0047449 | 0.36823 | -0.0673 | -0.014472 | 0.034484 | -0.32927 | 0.0016336 | -0.029189 | -0.060143 | 0.0056341 | 0.11632 | -0.036621 | 0 | -0.09613 | 0.004578 | 0.2655 | -0.11902 | -0.29755 | -0.064087 | -0.018311 | -0.054932 | 0.24719 | 0.16022 | -0.24261 | -0.2655 | 122.3053 | 122.1268 | 0.082398 | 122.4243 | 122.4289 | 0.30212 | -0.21973 | 122.1817 | 122.1588 | 0.064087 | 122.3602 | 122.3694 | 0.21057 | -0.022888 | 122.6898 | 122.3877 | 122.3282 | -0.48065 | 122.6715 | 122.5845 | 122.406 | -0.44861
2536.6406 | 122.5937 | -122.4197 | 0.15564 | -0.25588 | 0.023121 | 0.0079499 | 0.37143 | -0.065164 | -0.029426 | 0.038756 | -0.2072 | -0.0069114 | -0.028121 | -0.056939 | -0.0018429 | 0.10778 | 0.004578 | 0.10071 | -0.027466 | 0.064087 | 0.23804 | -0.10071 | -0.27008 | -0.004578 | 0.059509 | 0 | 0.2243 | 0.17395 | -0.21515 | -0.25177 | 122.319 | 122.1497 | 0.082397 | 122.5204 | 122.4838 | 0.33417 | -0.15106 | 122.2046 | 122.168 | 0.068664 | 122.4152 | 122.4197 | 0.25177 | 0.01831 | 122.6578 | 122.4243 | 122.3923 | -0.42572 | 122.644 | 122.5937 | 122.4792 | -0.40741
2537.6562 | 122.6532 | -122.3877 | 0.13275 | 0.59861 | 0.047688 | 0.0068819 | 0.36823 | -0.069436 | 0.014367 | 0.044097 | 0.41841 | -0.011183 | -0.016372 | -0.056939 | 0.01311 | 0.11952 | 0.009155 | 0.027466 | -0.086975 | 0.032043 | 0.25177 | -0.1236 | -0.27008 | 0.045776 | 0.045776 | -0.004578 | 0.18768 | 0.14648 | -0.21515 | -0.2243 | 122.2641 | 122.1176 | 0.11902 | 122.4152 | 122.4197 | 0.30212 | -0.1236 | 122.1725 | 122.1634 | 0.054932 | 122.4335 | 122.3831 | 0.21973 | 0.013733 | 122.6395 | 122.3969 | 122.3007 | -0.40283 | 122.5754 | 122.5342 | 122.4335 | -0.35706
2538.6406 | 122.58 | -122.4564 | 0.16479 | -0.19484 | 0.02953 | -0.00059506 | 0.36823 | -0.0673 | -0.026221 | 0.029143 | -0.26824 | -0.012251 | -0.038802 | -0.083642 | -0.00077485 | 0.11205 | -0.018311 | 0.091553 | -0.027466 | 0.050354 | 0.27008 | -0.1236 | -0.2655 | -0.022888 | 0.050354 | -0.041199 | 0.24261 | 0.14191 | -0.2243 | -0.27924 | 122.3328 | 122.1909 | 0.10529 | 122.5479 | 122.5067 | 0.31586 | -0.18311 | 122.2321 | 122.1771 | 0.07782 | 122.4335 | 122.4152 | 0.23804 | -0.022888 | 122.7264 | 122.438 | 122.4289 | -0.4303 | 122.699 | 122.5983 | 122.5067 | -0.44403
2539.6406 | 122.5571 | -122.4564 | 0.16479 | 0.24766 | 0.064778 | -0.040116 | 0.36823 | -0.074777 | 0.0079581 | 0.04196 | -0.11565 | -0.0026384 | -0.030257 | -0.059075 | 0.015247 | 0.10457 | 0.004578 | 0.009155 | -0.09613 | 0.013733 | 0.27466 | -0.082397 | -0.27466 | -0.032043 | 0 | -0.10071 | 0.21057 | 0.16937 | -0.23804 | -0.27466 | 122.374 | 122.1817 | 0.10986 | 122.4655 | 122.4701 | 0.28839 | -0.16022 | 122.2183 | 122.1817 | 0.045776 | 122.4243 | 122.3557 | 0.17395 | 0.004578 | 122.731 | 122.4609 | 122.3602 | -0.43945 | 122.6669 | 122.6257 | 122.4564 | -0.43945
2540.6719 | 122.5708 | -122.4472 | 0.1831 | 0.15611 | 0.048756 | -0.0059361 | 0.36823 | -0.0673 | 0.0068901 | 0.04196 | 0.17427 | -0.0026384 | -0.037734 | -0.071893 | 0.020587 | 0.10671 | -0.045776 | -0.045776 | -0.1236 | -0.009155 | 0.2655 | -0.11444 | -0.25635 | -0.041199 | -0.036621 | -0.086975 | 0.22888 | 0.17395 | -0.21973 | -0.26093 | 122.3328 | 122.1909 | 0.082398 | 122.4014 | 122.438 | 0.24719 | -0.22888 | 122.2275 | 122.1863 | 0.045777 | 122.406 | 122.3602 | 0.17395 | -0.009155 | 122.7127 | 122.4014 | 122.3236 | -0.43945 | 122.6761 | 122.6212 | 122.4106 | -0.44403
2541.6406 | 122.612 | -122.438 | 0.15106 | -0.27114 | 0.0081682 | 0.0026089 | 0.3693 | -0.059823 | -0.031562 | 0.038756 | -0.25298 | -0.01332 | -0.031325 | -0.053735 | -0.00077485 | 0.1035 | -0.009155 | 0.09613 | -0.032043 | 0.059509 | 0.25635 | -0.09613 | -0.27924 | -0.036621 | 0.050354 | -0.018311 | 0.22888 | 0.13275 | -0.23804 | -0.24261 | 122.3419 | 122.1588 | 0.10529 | 122.5342 | 122.4976 | 0.33874 | -0.16022 | 122.2 | 122.1954 | 0.07782 | 122.4014 | 122.4197 | 0.2243 | -0.018311 | 122.6944 | 122.4289 | 122.406 | -0.4303 | 122.6669 | 122.5708 | 122.4884 | -0.39368
2542.6875 | 122.7173 | -122.4197 | 0.1236 | 0.59861 | 0.031666 | 0.00047294 | 0.35327 | -0.066232 | -0.013404 | 0.047301 | 0.47945 | -0.014388 | -0.024916 | -0.06228 | 0.010974 | 0.11739 | 0.050354 | 0.12817 | 0.009155 | 0.07782 | 0.23346 | -0.082397 | -0.23804 | 0.07782 | 0.10071 | 0.059509 | 0.16937 | 0.1236 | -0.19226 | -0.22888 | 122.3373 | 122.1817 | 0.10986 | 122.5479 | 122.4976 | 0.31586 | -0.073242 | 122.2275 | 122.1909 | 0.045777 | 122.4976 | 122.4792 | 0.28839 | 0 | 122.6532 | 122.4701 | 122.4289 | -0.36163 | 122.5891 | 122.5433 | 122.5204 | -0.35248
2543.6406 | 122.6212 | -122.4564 | 0.15106 | -0.24062 | 0.034871 | -0.0027321 | 0.36502 | -0.063028 | -0.023017 | 0.032347 | -0.39031 | -0.01866 | -0.031325 | -0.06762 | 0.0045661 | 0.11525 | -0.013733 | 0.073242 | -0.045776 | 0.045776 | 0.24719 | -0.10529 | -0.27466 | -0.022888 | 0.027466 | -0.036621 | 0.22888 | 0.17395 | -0.23804 | -0.27466 | 122.3511 | 122.1817 | 0.09613 | 122.5296 | 122.5021 | 0.32043 | -0.16479 | 122.2183 | 122.1817 | 0.07782 | 122.4335 | 122.4197 | 0.23804 | 0.022888 | 122.7036 | 122.4426 | 122.4106 | -0.42572 | 122.6852 | 122.6303 | 122.4838 | -0.42572
2544.6406 | 122.5845 | -122.4518 | 0.16937 | 0.29344 | 0.072255 | -0.052933 | 0.38852 | -0.077981 | 0.0079581 | 0.046233 | -0.06987 | 0.0016336 | -0.01744 | -0.076165 | 0.035541 | 0.096026 | -0.004578 | -0.004578 | -0.11902 | 0.022888 | 0.27466 | -0.11902 | -0.29755 | -0.036621 | -0.032043 | -0.11444 | 0.21515 | 0.16022 | -0.23346 | -0.24719 | 122.3328 | 122.1542 | 0.10529 | 122.4472 | 122.4747 | 0.32043 | -0.17395 | 122.2183 | 122.2046 | 0.045776 | 122.4152 | 122.3373 | 0.13275 | -0.009156 | 122.7264 | 122.4472 | 122.3328 | -0.46692 | 122.6669 | 122.612 | 122.4197 | -0.41656
2545.6406 | 122.7173 | -122.4152 | 0.13733 | -0.13381 | 0.016713 | 0.010086 | 0.35968 | -0.065164 | -0.043311 | 0.034484 | -0.16142 | -0.01332 | -0.045211 | -0.063348 | -0.0039789 | 0.10564 | 0.041199 | 0.15564 | 0.036621 | 0.086975 | 0.24261 | -0.09613 | -0.23804 | 0.068665 | 0.14648 | 0.073242 | 0.19226 | 0.13733 | -0.20599 | -0.21973 | 122.319 | 122.1771 | 0.10529 | 122.5708 | 122.5021 | 0.32501 | -0.09613 | 122.2092 | 122.1954 | 0.054932 | 122.4838 | 122.4884 | 0.29297 | 0 | 122.6578 | 122.4564 | 122.4518 | -0.37537 | 122.6074 | 122.5525 | 122.5616 | -0.35706
2546.6406 | 122.7493 | -122.4197 | 0.14191 | 0.00352 | 0.0017592 | 0.026108 | 0.35221 | -0.073709 | -0.046515 | 0.034484 | -0.039353 | -0.015456 | -0.043074 | -0.064416 | -0.0061159 | 0.09923 | 0.032043 | 0.18768 | 0.050354 | 0.10071 | 0.24261 | -0.086975 | -0.23804 | 0.073242 | 0.14648 | 0.07782 | 0.19226 | 0.13733 | -0.20142 | -0.23804 | 122.3328 | 122.1817 | 0.10071 | 122.6074 | 122.5204 | 0.33875 | -0.10986 | 122.2183 | 122.1817 | 0.050354 | 122.493 | 122.4976 | 0.31586 | -0.004578 | 122.6624 | 122.4518 | 122.4701 | -0.37994 | 122.612 | 122.5571 | 122.5662 | -0.37994
2547.6406 | 122.6852 | -122.4518 | 0.13275 | -0.16433 | 0.0060322 | 0.0036769 | 0.36395 | -0.063028 | -0.018744 | 0.035552 | -0.42082 | -0.010115 | -0.042006 | -0.075097 | 0.010974 | 0.10457 | 0.032043 | 0.14648 | 0.013733 | 0.07782 | 0.23804 | -0.082397 | -0.25635 | 0.027466 | 0.086975 | 0.018311 | 0.21515 | 0.13733 | -0.21057 | -0.23346 | 122.3694 | 122.1954 | 0.10529 | 122.5983 | 122.5296 | 0.33417 | -0.10071 | 122.2412 | 122.2183 | 0.082398 | 122.4792 | 122.4701 | 0.25177 | 0.004578 | 122.6898 | 122.4838 | 122.4655 | -0.3891 | 122.6669 | 122.5891 | 122.5388 | -0.36621
2548.6406 | 122.7356 | -122.4518 | 0.14648 | 0.095073 | 0.0028272 | 0.011154 | 0.35648 | -0.0673 | -0.034766 | 0.030211 | 0.0522 | -0.0047754 | -0.048415 | -0.059075 | 0.0024291 | 0.11098 | 0.036621 | 0.10986 | 0.004578 | 0.082397 | 0.23804 | -0.073242 | -0.2243 | 0.064087 | 0.10071 | 0.064087 | 0.20142 | 0.12817 | -0.19684 | -0.23804 | 122.3785 | 122.2275 | 0.091553 | 122.5616 | 122.5342 | 0.3067 | -0.10986 | 122.2549 | 122.2137 | 0.054932 | 122.5159 | 122.5159 | 0.30212 | -0.01831 | 122.6898 | 122.4884 | 122.4564 | -0.37079 | 122.6532 | 122.58 | 122.5525 | -0.38452
2549.6719 | 122.6715 | -122.4655 | 0.14648 | 0.064555 | 0.037007 | 0.0068819 | 0.3725 | -0.066232 | 0.01864 | 0.047301 | -0.35979 | 0.0037696 | -0.018508 | -0.06762 | 0.020587 | 0.088549 | 0.073242 | 0.068665 | -0.068665 | 0.050354 | 0.27924 | -0.10986 | -0.27924 | 0.032043 | 0.027466 | -0.045776 | 0.21057 | 0.16022 | -0.21515 | -0.25177 | 122.3557 | 122.1863 | 0.13275 | 122.5342 | 122.5159 | 0.32959 | -0.073242 | 122.2504 | 122.2137 | 0.064087 | 122.4976 | 122.4197 | 0.20599 | 0.013733 | 122.7448 | 122.5388 | 122.3969 | -0.42572 | 122.6761 | 122.6257 | 122.493 | -0.39825
2550.6406 | 122.7036 | -122.4564 | 0.14648 | 0.26292 | 0.013508 | 0.012222 | 0.36823 | -0.070504 | -0.036902 | 0.031279 | 0.15901 | -0.010115 | -0.043074 | -0.068688 | 0.0024291 | 0.10991 | -0.009155 | 0.082397 | -0.022888 | 0.054932 | 0.24261 | -0.10529 | -0.25177 | 0.041199 | 0.082397 | 0.036621 | 0.19226 | 0.11902 | -0.19226 | -0.2243 | 122.3511 | 122.2046 | 0.096131 | 122.5388 | 122.5113 | 0.3067 | -0.15564 | 122.2641 | 122.2321 | 0.045777 | 122.4976 | 122.493 | 0.26093 | -0.027465 | 122.699 | 122.4472 | 122.4335 | -0.39825 | 122.6486 | 122.5754 | 122.5388 | -0.37079
2551.6875 | 122.6486 | -122.4426 | 0.14648 | 0.24766 | 0.059437 | 0.0058129 | 0.3757 | -0.072641 | 0.0058221 | 0.030211 | 0.17427 | -0.00050244 | -0.024916 | -0.054803 | 0.029132 | 0.088549 | -0.018311 | -0.027466 | -0.1236 | 0 | 0.26093 | -0.11902 | -0.27008 | -0.013733 | -0.041199 | -0.07782 | 0.21057 | 0.16479 | -0.24719 | -0.24261 | 122.3236 | 122.1725 | 0.11444 | 122.4152 | 122.4426 | 0.27008 | -0.16479 | 122.1954 | 122.2 | 0.064087 | 122.4289 | 122.3648 | 0.16479 | 0.018311 | 122.7036 | 122.4243 | 122.319 | -0.41657 | 122.6532 | 122.6074 | 122.4014 | -0.3891
2552.6406 | 122.7264 | -122.4335 | 0.1236 | 0.18663 | 0.0038952 | -0.0038001 | 0.37143 | -0.069436 | -0.03797 | 0.043029 | 0.18953 | -0.01332 | -0.043074 | -0.053735 | 0.0013611 | 0.12059 | -0.018311 | 0.073242 | -0.013733 | 0.059509 | 0.23346 | -0.082397 | -0.24261 | 0.022888 | 0.068665 | 0.045776 | 0.17853 | 0.14191 | -0.21515 | -0.23346 | 122.3511 | 122.1909 | 0.10986 | 122.5067 | 122.493 | 0.30212 | -0.14191 | 122.2183 | 122.2 | 0.054932 | 122.4564 | 122.4792 | 0.27924 | 0.018311 | 122.6669 | 122.4152 | 122.4197 | -0.36621 | 122.612 | 122.5754 | 122.5021 | -0.35706
2553.6406 | 122.7264 | -122.4518 | 0.13275 | 0.35447 | 0.017781 | 0.015426 | 0.36609 | -0.075845 | -0.020881 | 0.029143 | 0.25056 | -0.0090474 | -0.049483 | -0.075097 | 0.0034971 | 0.11098 | 0.004578 | 0.073242 | -0.027466 | 0.050354 | 0.23346 | -0.068665 | -0.25635 | 0.018311 | 0.045776 | 0.032043 | 0.20599 | 0.13275 | -0.20599 | -0.23346 | 122.3831 | 122.1954 | 0.10071 | 122.525 | 122.5021 | 0.3067 | -0.12817 | 122.2458 | 122.2183 | 0.073243 | 122.4701 | 122.4838 | 0.2655 | 0 | 122.6852 | 122.4564 | 122.4243 | -0.3891 | 122.6578 | 122.5845 | 122.4976 | -0.36621
2554.6406 | 122.6532 | -122.493 | 0.16022 | -0.25588 | 0.027394 | 0.014358 | 0.3757 | -0.063028 | -0.010199 | 0.035552 | -0.35979 | -0.0026384 | -0.035598 | -0.06762 | 0.0088381 | 0.10457 | 0.022888 | 0.10071 | -0.027466 | 0.050354 | 0.24719 | -0.10986 | -0.27008 | -0.009155 | 0.041199 | -0.036621 | 0.19684 | 0.15106 | -0.21973 | -0.25177 | 122.3831 | 122.2229 | 0.086975 | 122.5937 | 122.5433 | 0.32044 | -0.13733 | 122.2733 | 122.2412 | 0.036621 | 122.4838 | 122.4564 | 0.21515 | -0.009155 | 122.7402 | 122.5159 | 122.4655 | -0.4303 | 122.6898 | 122.644 | 122.5342 | -0.41199
2555.6406 | 122.7722 | -122.4564 | 0.1236 | 0.17137 | 0.041279 | 0.028244 | 0.36182 | -0.073709 | -0.029426 | 0.031279 | 0.11323 | -0.0015704 | -0.03987 | -0.081506 | 0.014179 | 0.10884 | 0.009155 | 0.10071 | -0.013733 | 0.073242 | 0.26093 | -0.07782 | -0.25635 | 0.064087 | 0.091553 | 0.068665 | 0.1831 | 0.1236 | -0.17853 | -0.24261 | 122.3785 | 122.2 | 0.13733 | 122.5571 | 122.5296 | 0.32959 | -0.11444 | 122.2778 | 122.2137 | 0.059509 | 122.5204 | 122.525 | 0.31128 | 0 | 122.7173 | 122.4655 | 122.4426 | -0.37994 | 122.6395 | 122.58 | 122.5479 | -0.36621
2556.6406 | 122.7859 | -122.4426 | 0.11444 | 0.58335 | 0.051961 | -0.0016631 | 0.35968 | -0.058755 | -0.0037909 | 0.037688 | 0.40315 | -0.00050244 | -0.032393 | -0.06762 | 0.021655 | 0.10243 | 0.11444 | 0.11902 | 0.018311 | 0.10986 | 0.2243 | -0.068665 | -0.24261 | 0.10529 | 0.09613 | 0.045776 | 0.19684 | 0.12817 | -0.1831 | -0.21515 | 122.374 | 122.2 | 0.10986 | 122.5616 | 122.5525 | 0.35248 | 0 | 122.2595 | 122.2275 | 0.082397 | 122.5479 | 122.4884 | 0.26093 | 0.013733 | 122.6669 | 122.5571 | 122.4609 | -0.35706 | 122.6395 | 122.5708 | 122.5388 | -0.32959
2557.6406 | 122.7448 | -122.4564 | 0.1236 | 0.61387 | 0.04662 | 0.016495 | 0.36502 | -0.058755 | -0.0059269 | 0.047301 | 0.37263 | 0.0037696 | -0.029189 | -0.068688 | 0.0034971 | 0.11205 | 0.091553 | 0.1236 | 0.018311 | 0.086975 | 0.20599 | -0.086975 | -0.23804 | 0.10529 | 0.091553 | 0.059509 | 0.19226 | 0.10986 | -0.18768 | -0.20142 | 122.3694 | 122.2183 | 0.082398 | 122.58 | 122.5433 | 0.32501 | -0.032043 | 122.2687 | 122.2549 | 0.068665 | 122.5616 | 122.5159 | 0.26093 | -0.013733 | 122.6624 | 122.5479 | 122.4747 | -0.36163 | 122.6486 | 122.5662 | 122.5479 | -0.32501
2558.6406 | 122.7356 | -122.4701 | 0.11902 | 0.56809 | 0.04662 | 0.0026089 | 0.36716 | -0.061959 | -0.011268 | 0.050505 | 0.46419 | -0.0058434 | -0.023848 | -0.051599 | 0.0088381 | 0.10564 | 0.07782 | 0.1236 | 0.013733 | 0.07782 | 0.20599 | -0.073242 | -0.24719 | 0.10071 | 0.09613 | 0.050354 | 0.17853 | 0.1236 | -0.20142 | -0.21515 | 122.3969 | 122.2229 | 0.086975 | 122.5937 | 122.5479 | 0.32501 | -0.041199 | 122.2687 | 122.2549 | 0.059509 | 122.5708 | 122.5204 | 0.2655 | 0.004577 | 122.6761 | 122.5479 | 122.4838 | -0.36621 | 122.6486 | 122.5937 | 122.5662 | -0.33417
2559.6406 | 122.6486 | -122.5113 | 0.16479 | -0.2101 | 0.030598 | 0.0068819 | 0.38104 | -0.064096 | 0.0026181 | 0.044097 | -0.48186 | 0.00056556 | -0.031325 | -0.065484 | 0.016315 | 0.10457 | -0.013733 | -0.004578 | -0.10529 | 0.004578 | 0.27924 | -0.1236 | -0.27466 | -0.009155 | -0.004578 | -0.064087 | 0.23346 | 0.15106 | -0.23804 | -0.27466 | 122.3877 | 122.2366 | 0.11444 | 122.5067 | 122.5159 | 0.27924 | -0.17853 | 122.2733 | 122.2366 | 0.068664 | 122.5021 | 122.4472 | 0.21057 | -0.013733 | 122.7905 | 122.4976 | 122.406 | -0.43945 | 122.7448 | 122.6624 | 122.5067 | -0.43945
2560.6406 | 122.7768 | -122.4655 | 0.10986 | 0.65965 | 0.035939 | -0.00059506 | 0.35861 | -0.064096 | -0.010199 | 0.05371 | 0.38789 | -0.011183 | -0.033461 | -0.075097 | 0.019519 | 0.11098 | 0.09613 | 0.13275 | 0.013733 | 0.09613 | 0.23346 | -0.07782 | -0.23804 | 0.10529 | 0.10071 | 0.054932 | 0.18768 | 0.10529 | -0.20142 | -0.21057 | 122.3877 | 122.2275 | 0.1236 | 122.5983 | 122.5616 | 0.33417 | -0.013733 | 122.2641 | 122.2549 | 0.07782 | 122.5708 | 122.5204 | 0.2655 | -0.004577 | 122.699 | 122.5616 | 122.4792 | -0.3479 | 122.6532 | 122.5708 | 122.5662 | -0.32043
2561.6406 | 122.7722 | -122.4747 | 0.13733 | 0.59861 | 0.048756 | -0.010208 | 0.37357 | -0.063028 | -0.018744 | 0.047301 | 0.46419 | 0.0016336 | -0.048415 | -0.061212 | 0.010974 | 0.1003 | 0.07782 | 0.12817 | 0.027466 | 0.10071 | 0.24261 | -0.07782 | -0.22888 | 0.091553 | 0.10071 | 0.059509 | 0.17853 | 0.13733 | -0.19684 | -0.21515 | 122.3969 | 122.2458 | 0.10529 | 122.6028 | 122.5754 | 0.32959 | -0.059509 | 122.2778 | 122.2595 | 0.041199 | 122.5662 | 122.5342 | 0.27466 | 0 | 122.7173 | 122.5525 | 122.5021 | -0.36621 | 122.6532 | 122.612 | 122.5754 | -0.35248
2562.6406 | 122.7905 | -122.4747 | 0.13275 | 1.1937 | 0.064778 | 0.016495 | 0.36182 | -0.055551 | -0.00058594 | 0.046233 | 0.40315 | 0.0027016 | -0.035598 | -0.071893 | 0.014179 | 0.11312 | 0.086975 | 0.11444 | 0.004578 | 0.10071 | 0.23346 | -0.068665 | -0.23804 | 0.10529 | 0.10986 | 0.059509 | 0.17853 | 0.11444 | -0.20599 | -0.20599 | 122.406 | 122.2366 | 0.10071 | 122.5891 | 122.5754 | 0.33875 | -0.045776 | 122.2687 | 122.2687 | 0.045777 | 122.58 | 122.5342 | 0.2655 | -0.01831 | 122.7081 | 122.5616 | 122.4792 | -0.37079 | 122.6532 | 122.5891 | 122.5845 | -0.33875
2563.6406 | 122.7951 | -122.4884 | 0.12817 | 0.64439 | 0.051961 | -0.0059361 | 0.36075 | -0.071573 | 0.0015501 | 0.049437 | 0.32686 | 0.0027016 | -0.032393 | -0.055871 | 0.022724 | 0.09389 | 0.059509 | 0.054932 | -0.018311 | 0.068665 | 0.26093 | -0.07782 | -0.24261 | 0.068665 | 0.091553 | 0.027466 | 0.17853 | 0.13275 | -0.20142 | -0.21973 | 122.4106 | 122.2458 | 0.13275 | 122.5433 | 122.5571 | 0.31128 | -0.068665 | 122.287 | 122.2687 | 0.050354 | 122.5571 | 122.5159 | 0.24719 | 0.004577 | 122.7493 | 122.5479 | 122.4701 | -0.37079 | 122.6669 | 122.6212 | 122.58 | -0.3479
2564.6406 | 122.7402 | -122.5159 | 0.14648 | 0.36973 | 0.030598 | -0.00059506 | 0.37677 | -0.077981 | -0.03263 | 0.046233 | 0.26582 | -0.0026384 | -0.030257 | -0.071893 | 0.00029315 | 0.10778 | -0.004578 | 0.068665 | -0.013733 | 0.064087 | 0.23804 | -0.082397 | -0.23804 | 0.045776 | 0.059509 | 0.032043 | 0.19684 | 0.13275 | -0.19684 | -0.23346 | 122.4335 | 122.2778 | 0.091553 | 122.5845 | 122.58 | 0.30212 | -0.15106 | 122.319 | 122.2824 | 0.050354 | 122.5616 | 122.5479 | 0.2655 | -0.013733 | 122.7539 | 122.5113 | 122.5021 | -0.38452 | 122.7127 | 122.6486 | 122.5754 | -0.37994
2565.6719 | 122.7631 | -122.5113 | 0.14191 | -0.14907 | 0.032734 | 0.0068819 | 0.36395 | -0.051278 | -0.020881 | 0.037688 | -0.26824 | -0.01332 | -0.044143 | -0.068688 | 0.0034971 | 0.10137 | 0.073242 | 0.14648 | 0.036621 | 0.091553 | 0.22888 | -0.082397 | -0.23346 | 0.059509 | 0.14648 | 0.045776 | 0.17395 | 0.13275 | -0.19684 | -0.21973 | 122.4289 | 122.2778 | 0.086975 | 122.6578 | 122.6028 | 0.32501 | -0.068665 | 122.3145 | 122.2916 | 0.032043 | 122.5708 | 122.5571 | 0.2655 | -0.009156 | 122.7402 | 122.5845 | 122.5479 | -0.37537 | 122.6852 | 122.644 | 122.6578 | -0.36163
2566.6406 | 122.7356 | -122.5159 | 0.15564 | 0.46128 | 0.064778 | -0.019821 | 0.35327 | -0.066232 | 0.0026181 | 0.037688 | 0.25056 | 0.0048376 | -0.027053 | -0.052667 | 0.015247 | 0.10243 | 0.041199 | -0.004578 | -0.10529 | 0.013733 | 0.2655 | -0.11444 | -0.27008 | 0.041199 | 0.018311 | -0.036621 | 0.20599 | 0.14191 | -0.21057 | -0.22888 | 122.4014 | 122.2458 | 0.10986 | 122.5113 | 122.5296 | 0.28381 | -0.11444 | 122.3053 | 122.287 | 0.050354 | 122.5571 | 122.4792 | 0.19226 | -0.013733 | 122.7814 | 122.5571 | 122.4106 | -0.42572 | 122.7219 | 122.6578 | 122.5342 | -0.38452
2567.6406 | 122.7127 | -122.5159 | 0.16479 | 0.44602 | 0.066914 | -0.012345 | 0.38318 | -0.068368 | 0.0047541 | 0.048369 | 0.29634 | 0.0069746 | -0.036666 | -0.058007 | 0.016315 | 0.10671 | 0.036621 | -0.018311 | -0.10986 | 0.009155 | 0.2655 | -0.11902 | -0.27008 | 0.013733 | -0.018311 | -0.054932 | 0.22888 | 0.15564 | -0.21973 | -0.22888 | 122.3969 | 122.2458 | 0.10071 | 122.4976 | 122.525 | 0.27924 | -0.12817 | 122.2961 | 122.287 | 0.064087 | 122.5296 | 122.4609 | 0.17395 | -0.009155 | 122.7814 | 122.5525 | 122.406 | -0.43488 | 122.7448 | 122.6715 | 122.4976 | -0.39368
2568.6406 | 122.699 | -122.5479 | 0.14648 | 0.4918 | 0.057301 | -0.0038001 | 0.36182 | -0.0673 | 0.0068901 | 0.049437 | 0.20479 | 0.0027016 | -0.028121 | -0.055871 | 0.026996 | 0.10564 | -0.018311 | 0 | -0.10529 | 0.018311 | 0.28839 | -0.11444 | -0.27466 | -0.022888 | -0.032043 | -0.07782 | 0.21973 | 0.14191 | -0.21973 | -0.25177 | 122.4335 | 122.2733 | 0.14191 | 122.5479 | 122.5662 | 0.29297 | -0.16479 | 122.3282 | 122.2961 | 0.073243 | 122.525 | 122.4701 | 0.17395 | -0.004577 | 122.8363 | 122.5296 | 122.4426 | -0.42114 | 122.7676 | 122.6898 | 122.5159 | -0.39825
2569.6562 | 122.7768 | -122.525 | 0.14191 | 0.20188 | 0.020985 | 0.011154 | 0.37784 | -0.075845 | -0.047584 | 0.044097 | 0.12849 | -0.0058434 | -0.029189 | -0.069756 | -0.0018429 | 0.11525 | -0.013733 | 0.059509 | -0.013733 | 0.059509 | 0.23346 | -0.09613 | -0.25177 | 0.022888 | 0.086975 | 0.054932 | 0.19684 | 0.13275 | -0.17395 | -0.2243 | 122.4289 | 122.2733 | 0.091552 | 122.5845 | 122.5845 | 0.31128 | -0.15564 | 122.3511 | 122.3007 | 0.054931 | 122.5479 | 122.58 | 0.27924 | -0.009156 | 122.7585 | 122.5113 | 122.5113 | -0.39368 | 122.7219 | 122.6578 | 122.612 | -0.36621
2570.6406 | 122.7264 | -122.5525 | 0.15564 | 0.079814 | 0.057301 | -0.0048681 | 0.37998 | -0.063028 | 0.015435 | 0.04196 | -0.11565 | 0.017656 | -0.03987 | -0.06762 | 0.020587 | 0.10671 | 0.086975 | 0.054932 | -0.082397 | 0.036621 | 0.26093 | -0.10529 | -0.26093 | 0.009155 | 0.041199 | -0.054932 | 0.21057 | 0.16022 | -0.22888 | -0.24261 | 122.4472 | 122.2916 | 0.10529 | 122.6074 | 122.5891 | 0.29755 | -0.068665 | 122.3236 | 122.3099 | 0.054931 | 122.5616 | 122.4976 | 0.18768 | 0.004577 | 122.8134 | 122.6395 | 122.4701 | -0.41657 | 122.7631 | 122.7127 | 122.5937 | -0.39826
2571.6406 | 122.7127 | -122.5525 | 0.16022 | 0.049296 | 0.071187 | 0.0026089 | 0.3725 | -0.070504 | -0.0059269 | 0.03662 | -0.11565 | 0.0080426 | -0.028121 | -0.055871 | 0.021655 | 0.10243 | 0.064087 | 0.054932 | -0.059509 | 0.050354 | 0.27466 | -0.10529 | -0.26093 | 0.045776 | 0.036621 | -0.036621 | 0.21515 | 0.15106 | -0.22888 | -0.24719 | 122.4472 | 122.2916 | 0.11444 | 122.6074 | 122.6028 | 0.31128 | -0.09613 | 122.3236 | 122.3053 | 0.054932 | 122.5983 | 122.5159 | 0.21057 | -0.009155 | 122.8271 | 122.6166 | 122.493 | -0.42114 | 122.7676 | 122.7036 | 122.5891 | -0.40741
2572.6406 | 122.7264 | -122.5616 | 0.15564 | 0.12559 | 0.053029 | -0.0080721 | 0.3725 | -0.064096 | 0.0068901 | 0.043029 | -0.054612 | -0.00050244 | -0.02278 | -0.074029 | 0.017383 | 0.10671 | 0.054932 | 0.050354 | -0.073242 | 0.041199 | 0.25177 | -0.11902 | -0.27466 | 0.004578 | 0.036621 | -0.036621 | 0.23804 | 0.14191 | -0.2243 | -0.25177 | 122.4426 | 122.287 | 0.09613 | 122.612 | 122.6028 | 0.31586 | -0.10071 | 122.3373 | 122.3099 | 0.082397 | 122.5662 | 122.525 | 0.21515 | -0.013733 | 122.8134 | 122.6166 | 122.4884 | -0.4303 | 122.7997 | 122.7036 | 122.5983 | -0.40741
2573.6406 | 122.7631 | -122.5708 | 0.15564 | 0.064555 | 0.071187 | 0.0047449 | 0.37143 | -0.068368 | -0.0016549 | 0.04196 | -0.085129 | 0.0037696 | -0.038802 | -0.053735 | 0.01311 | 0.11739 | 0.059509 | 0.059509 | -0.068665 | 0.054932 | 0.25635 | -0.09613 | -0.27466 | 0.027466 | 0.045776 | -0.018311 | 0.21973 | 0.15106 | -0.21973 | -0.22888 | 122.4747 | 122.2961 | 0.10071 | 122.6303 | 122.6257 | 0.32959 | -0.096131 | 122.3511 | 122.3419 | 0.064087 | 122.5983 | 122.5525 | 0.21057 | -0.004578 | 122.8271 | 122.6303 | 122.5021 | -0.4303 | 122.7905 | 122.7219 | 122.6166 | -0.38452
2574.6406 | 122.7631 | -122.5296 | 0.14648 | -0.10329 | 0.059437 | 0.0047449 | 0.36716 | -0.058755 | -0.0069949 | 0.051574 | -0.11565 | 0.0059056 | -0.03453 | -0.056939 | 0.020587 | 0.11312 | 0.041199 | 0.050354 | -0.054932 | 0.059509 | 0.27924 | -0.13275 | -0.27466 | 0.018311 | 0.073242 | -0.027466 | 0.23346 | 0.16022 | -0.21973 | -0.22888 | 122.3969 | 122.2549 | 0.13275 | 122.58 | 122.5891 | 0.33417 | -0.10529 | 122.3099 | 122.3007 | 0.086975 | 122.5479 | 122.5021 | 0.20142 | 0.013733 | 122.8088 | 122.5708 | 122.4747 | -0.42114 | 122.7631 | 122.6898 | 122.6028 | -0.37537
2575.7031 | 122.8546 | -122.5433 | 0.13733 | 0.62913 | 0.059437 | -0.0027321 | 0.36182 | -0.055551 | -0.026221 | 0.038756 | 0.571 | -0.016524 | -0.040938 | -0.082574 | 0.0013611 | 0.11632 | 0.041199 | 0.11444 | 0.022888 | 0.082397 | 0.24261 | -0.082397 | -0.23346 | 0.059509 | 0.10529 | 0.054932 | 0.16937 | 0.1236 | -0.20599 | -0.2243 | 122.4609 | 122.3099 | 0.10529 | 122.6578 | 122.6257 | 0.31586 | -0.09613 | 122.3373 | 122.319 | 0.032044 | 122.6028 | 122.5983 | 0.27924 | -0.013733 | 122.7859 | 122.5845 | 122.5662 | -0.37079 | 122.7127 | 122.6669 | 122.6486 | -0.36163
2576.6406 | 122.7448 | -122.5708 | 0.15106 | -0.088033 | 0.06371 | -0.0059361 | 0.3725 | -0.051278 | 0.0036861 | 0.049437 | -0.23772 | -0.0069114 | -0.038802 | -0.06228 | 0.017383 | 0.1003 | 0.027466 | 0.036621 | -0.07782 | 0.045776 | 0.28381 | -0.11902 | -0.28839 | 0.004578 | 0.073242 | -0.041199 | 0.2243 | 0.15106 | -0.23346 | -0.25635 | 122.4518 | 122.2824 | 0.13275 | 122.6074 | 122.6166 | 0.33417 | -0.1236 | 122.3373 | 122.3145 | 0.073242 | 122.5754 | 122.5296 | 0.21515 | 0 | 122.8546 | 122.5983 | 122.493 | -0.43945 | 122.7951 | 122.7219 | 122.644 | -0.40741
2577.6406 | 122.7264 | -122.5937 | 0.15564 | -0.22536 | 0.039143 | -0.0016631 | 0.3757 | -0.068368 | -0.020881 | 0.028075 | -0.29875 | 0.0037696 | -0.030257 | -0.064416 | 0.0024291 | 0.10991 | -0.045776 | -0.004578 | -0.11444 | 0.009155 | 0.28381 | -0.12817 | -0.27924 | -0.045776 | 0.022888 | -0.059509 | 0.25635 | 0.17395 | -0.25177 | -0.22888 | 122.4655 | 122.3145 | 0.12817 | 122.5891 | 122.6028 | 0.28839 | -0.20142 | 122.3419 | 122.3648 | 0.10071 | 122.5479 | 122.5342 | 0.16937 | 0.01831 | 122.8775 | 122.5479 | 122.4792 | -0.43488 | 122.85 | 122.7676 | 122.6166 | -0.38452
2578.6406 | 122.7722 | -122.5891 | 0.15106 | -0.13381 | 0.064778 | -0.016617 | 0.37143 | -0.071573 | -0.012336 | 0.055846 | -0.0088351 | 0.0037696 | -0.03453 | -0.061212 | 0.019519 | 0.1003 | 0.032043 | 0.050354 | -0.068665 | 0.050354 | 0.27008 | -0.11444 | -0.25635 | 0.009155 | 0.059509 | -0.027466 | 0.21515 | 0.16022 | -0.2243 | -0.25177 | 122.4747 | 122.3328 | 0.11902 | 122.6395 | 122.6395 | 0.3067 | -0.11902 | 122.3648 | 122.3373 | 0.064087 | 122.5983 | 122.5616 | 0.2243 | 0.009155 | 122.8592 | 122.6212 | 122.5204 | -0.40741 | 122.8043 | 122.7493 | 122.6486 | -0.40283
2579.6406 | 122.7814 | -122.5571 | 0.14648 | 0.095073 | 0.04662 | 0.014358 | 0.35755 | -0.066232 | -0.0016549 | 0.043029 | -0.10039 | 0.0037696 | -0.024916 | -0.061212 | 0.018451 | 0.10243 | 0.027466 | 0.054932 | -0.064087 | 0.045776 | 0.2655 | -0.10986 | -0.28381 | 0.009155 | 0.050354 | -0.027466 | 0.22888 | 0.14648 | -0.23346 | -0.24261 | 122.4472 | 122.2733 | 0.11902 | 122.612 | 122.6028 | 0.32959 | -0.11902 | 122.3236 | 122.3145 | 0.082398 | 122.5662 | 122.5296 | 0.21515 | 0 | 122.8226 | 122.5845 | 122.493 | -0.4303 | 122.7859 | 122.7036 | 122.6074 | -0.3891
2580.6406 | 122.7402 | -122.5983 | 0.16937 | -0.33217 | 0.026326 | 0.012222 | 0.37464 | -0.066232 | -0.029426 | 0.03662 | -0.40556 | -0.012251 | -0.035598 | -0.066552 | 0.00029315 | 0.11525 | -0.082397 | 0.018311 | -0.10529 | -0.009155 | 0.27466 | -0.13733 | -0.28381 | -0.054932 | 0.009155 | -0.045776 | 0.24261 | 0.15564 | -0.23804 | -0.25635 | 122.4609 | 122.3145 | 0.10529 | 122.6166 | 122.5891 | 0.27466 | -0.25177 | 122.3602 | 122.3419 | 0.073242 | 122.5433 | 122.5525 | 0.21057 | -0.013733 | 122.8729 | 122.5159 | 122.493 | -0.45319 | 122.8409 | 122.7539 | 122.6074 | -0.42572
2581.6406 | 122.7402 | -122.6028 | 0.16479 | -0.30166 | 0.026326 | -0.00059506 | 0.38639 | -0.061959 | -0.018744 | 0.035552 | 0.15901 | 0.00056556 | -0.03987 | -0.064416 | -0.0018429 | 0.11098 | -0.041199 | 0.013733 | -0.064087 | 0.027466 | 0.25635 | -0.11444 | -0.27466 | -0.064087 | 0.032043 | -0.050354 | 0.21973 | 0.17395 | -0.25177 | -0.2655 | 122.4884 | 122.3282 | 0.091553 | 122.6166 | 122.6303 | 0.30212 | -0.20599 | 122.3511 | 122.3373 | 0.054932 | 122.5388 | 122.5525 | 0.21515 | 0.009155 | 122.8592 | 122.5616 | 122.5388 | -0.43945 | 122.8226 | 122.7768 | 122.6349 | -0.4303
2582.6406 | 122.7264 | -122.5891 | 0.16479 | -0.19484 | 0.028462 | 0.0058129 | 0.37464 | -0.059823 | -0.027289 | 0.03662 | -0.39031 | -0.012251 | -0.040938 | -0.058007 | 0.0088381 | 0.10991 | -0.050354 | 0.018311 | -0.10529 | -0.013733 | 0.28381 | -0.14648 | -0.28839 | -0.068665 | 0 | -0.041199 | 0.22888 | 0.16937 | -0.24261 | -0.25635 | 122.4426 | 122.3007 | 0.11902 | 122.6074 | 122.5754 | 0.27466 | -0.21515 | 122.3465 | 122.3328 | 0.064087 | 122.5204 | 122.5479 | 0.21515 | 0.004578 | 122.8729 | 122.5388 | 122.4838 | -0.45319 | 122.818 | 122.7585 | 122.5891 | -0.42114
2583.6406 | 122.7997 | -122.5616 | 0.16022 | -0.10329 | 0.038075 | 0.015426 | 0.3725 | -0.0673 | -0.024085 | 0.039824 | -0.26824 | -0.0090474 | -0.040938 | -0.069756 | 0.0024291 | 0.10778 | 0.032043 | 0.11444 | 0.013733 | 0.068665 | 0.23346 | -0.091553 | -0.24719 | 0.013733 | 0.091553 | 0.032043 | 0.2243 | 0.14648 | -0.19226 | -0.24719 | 122.4701 | 122.3145 | 0.073242 | 122.6761 | 122.6303 | 0.31586 | -0.12817 | 122.3694 | 122.3145 | 0.064087 | 122.5754 | 122.5937 | 0.27924 | -0.013733 | 122.7951 | 122.5937 | 122.5754 | -0.40741 | 122.7859 | 122.7081 | 122.6532 | -0.40741
2584.6406 | 122.7768 | -122.612 | 0.15106 | -0.22536 | 0.018849 | 0.0090179 | 0.35968 | -0.073709 | -0.026221 | 0.030211 | -0.37505 | -0.019728 | -0.040938 | -0.069756 | 0.0013611 | 0.10671 | 0.013733 | 0.10071 | -0.045776 | 0.064087 | 0.26093 | -0.11902 | -0.25635 | -0.022888 | 0.032043 | -0.018311 | 0.2243 | 0.15106 | -0.22888 | -0.25177 | 122.493 | 122.3557 | 0.10986 | 122.7127 | 122.6761 | 0.32044 | -0.13733 | 122.3831 | 122.3602 | 0.073242 | 122.5891 | 122.5937 | 0.23346 | 0 | 122.8729 | 122.6257 | 122.5662 | -0.40741 | 122.8363 | 122.7631 | 122.644 | -0.40283
2585.6406 | 122.8043 | -122.5388 | 0.14191 | -0.19484 | 0.015645 | 0.015426 | 0.37036 | -0.063028 | -0.013404 | 0.037688 | -0.29875 | -0.019728 | -0.061232 | -0.056939 | -0.0039789 | 0.098162 | 0.050354 | 0.11444 | 0.009155 | 0.091553 | 0.24261 | -0.082397 | -0.25635 | 0.027466 | 0.10071 | 0.022888 | 0.19684 | 0.14191 | -0.19684 | -0.21515 | 122.4564 | 122.2824 | 0.10071 | 122.6532 | 122.6303 | 0.3479 | -0.091553 | 122.3419 | 122.3236 | 0.054931 | 122.5662 | 122.5616 | 0.23804 | 0 | 122.7814 | 122.5891 | 122.5479 | -0.39826 | 122.7356 | 122.6807 | 122.6395 | -0.35706
2586.6406 | 122.8455 | -122.5891 | 0.14648 | -0.13381 | 0.017781 | 0.0090179 | 0.36716 | -0.065164 | -0.017676 | 0.034484 | -0.32927 | -0.025069 | -0.051619 | -0.06762 | 0.010974 | 0.10991 | 0.059509 | 0.14191 | 0.018311 | 0.091553 | 0.25177 | -0.07782 | -0.25177 | 0.050354 | 0.10986 | 0.041199 | 0.17853 | 0.13275 | -0.19226 | -0.2243 | 122.5113 | 122.3373 | 0.10529 | 122.731 | 122.6807 | 0.34332 | -0.086975 | 122.3969 | 122.3648 | 0.032044 | 122.6395 | 122.6303 | 0.2655 | -0.013733 | 122.8409 | 122.6486 | 122.6074 | -0.39825 | 122.7676 | 122.7219 | 122.699 | -0.37079
2587.6406 | 122.7448 | -122.6212 | 0.14191 | 0.52232 | 0.065846 | -0.00059506 | 0.36823 | -0.073709 | 0.010095 | 0.04196 | 0.20479 | 0.0027016 | -0.020644 | -0.070825 | 0.026996 | 0.1035 | -0.009155 | -0.022888 | -0.11902 | 0.009155 | 0.27008 | -0.11444 | -0.27466 | -0.004578 | -0.064087 | -0.082397 | 0.2243 | 0.15106 | -0.25177 | -0.24261 | 122.5067 | 122.3465 | 0.12817 | 122.5983 | 122.6303 | 0.28381 | -0.15106 | 122.3694 | 122.3785 | 0.082397 | 122.6166 | 122.5388 | 0.16022 | 0.009155 | 122.8912 | 122.612 | 122.5021 | -0.41657 | 122.8455 | 122.7722 | 122.5571 | -0.38452
2588.6406 | 122.8958 | -122.5754 | 0.12817 | -0.71364 | 0.027394 | 0.012222 | 0.3693 | -0.065164 | -0.025153 | 0.027007 | -0.14616 | -0.012251 | -0.055892 | -0.069756 | -0.0018429 | 0.11525 | 0.064087 | 0.18768 | 0.045776 | 0.09613 | 0.25177 | -0.086975 | -0.27466 | 0.054932 | 0.13275 | 0.068665 | 0.17395 | 0.1236 | -0.18768 | -0.22888 | 122.4884 | 122.3007 | 0.1236 | 122.7631 | 122.6715 | 0.37079 | -0.064087 | 122.3877 | 122.3465 | 0.045776 | 122.6303 | 122.644 | 0.29755 | -0.004578 | 122.8271 | 122.6395 | 122.6212 | -0.40283 | 122.7493 | 122.699 | 122.7081 | -0.35706
2589.6719 | 122.7722 | -122.5983 | 0.14648 | 0.064555 | 0.045552 | -0.014481 | 0.35861 | -0.071573 | 0.014367 | 0.044097 | -0.11565 | 0.00056556 | -0.027053 | -0.061212 | 0.021655 | 0.09923 | 0.064087 | 0.068665 | -0.07782 | 0.027466 | 0.27466 | -0.11444 | -0.27466 | 0.018311 | -0.004578 | -0.054932 | 0.2243 | 0.15564 | -0.21057 | -0.23804 | 122.4838 | 122.3236 | 0.12817 | 122.6669 | 122.6257 | 0.30212 | -0.082397 | 122.3877 | 122.3602 | 0.07782 | 122.6166 | 122.5433 | 0.1831 | 0.009156 | 122.8729 | 122.6624 | 122.5204 | -0.42114 | 122.8226 | 122.7539 | 122.5937 | -0.38452
2590.6406 | 122.8409 | -122.5662 | 0.14191 | -0.19484 | 0.017781 | 0.0015409 | 0.3693 | -0.059823 | -0.029426 | 0.044097 | -0.16142 | -0.016524 | -0.036666 | -0.058007 | 0.010974 | 0.1035 | 0.032043 | 0.16479 | 0.022888 | 0.09613 | 0.22888 | -0.10071 | -0.25177 | 0.045776 | 0.1236 | 0.041199 | 0.19684 | 0.13275 | -0.20142 | -0.21515 | 122.4655 | 122.3145 | 0.086975 | 122.731 | 122.6624 | 0.3479 | -0.10986 | 122.3648 | 122.3511 | 0.054931 | 122.612 | 122.6074 | 0.25635 | -0.009156 | 122.7951 | 122.5983 | 122.5891 | -0.39368 | 122.7631 | 122.699 | 122.6898 | -0.35706
2591.6875 | 122.8043 | -122.5983 | 0.15564 | 0.079814 | 0.051961 | 0.0079499 | 0.35434 | -0.070504 | 0.010095 | 0.048369 | -0.19194 | 0.0016336 | -0.03453 | -0.054803 | 0.022724 | 0.1035 | 0.064087 | 0.064087 | -0.064087 | 0.041199 | 0.2655 | -0.10986 | -0.27008 | 0.022888 | 0.027466 | -0.036621 | 0.21057 | 0.15106 | -0.2243 | -0.24261 | 122.4884 | 122.3282 | 0.10986 | 122.6624 | 122.6395 | 0.31128 | -0.091553 | 122.374 | 122.3557 | 0.054931 | 122.6212 | 122.5616 | 0.20599 | -0.004578 | 122.8638 | 122.6624 | 122.5342 | -0.42572 | 122.8088 | 122.7493 | 122.6257 | -0.39826
2592.6406 | 122.8546 | -122.5616 | 0.14648 | 0.29344 | 0.0028272 | 0.0015409 | 0.37677 | -0.076913 | -0.039039 | 0.035552 | 0.14375 | -0.010115 | -0.046279 | -0.055871 | -0.0071839 | 0.11846 | -0.027466 | 0.068665 | -0.013733 | 0.054932 | 0.24261 | -0.10986 | -0.24261 | 0.032043 | 0.073242 | 0.054932 | 0.17853 | 0.13733 | -0.19226 | -0.21515 | 122.4518 | 122.319 | 0.096131 | 122.6303 | 122.6166 | 0.29755 | -0.17395 | 122.3694 | 122.3465 | 0.032044 | 122.5937 | 122.6166 | 0.27008 | -0.009155 | 122.8043 | 122.5342 | 122.5479 | -0.3891 | 122.7402 | 122.699 | 122.6349 | -0.36163
2593.6406 | 122.8592 | -122.5891 | 0.14191 | 0.11033 | 0.023121 | 0.012222 | 0.36289 | -0.059823 | -0.040107 | 0.037688 | 0.082718 | -0.014388 | -0.032393 | -0.053735 | -0.0061159 | 0.12166 | 0.004578 | 0.082397 | 0.004578 | 0.059509 | 0.23804 | -0.091553 | -0.23804 | 0.050354 | 0.086975 | 0.064087 | 0.19226 | 0.13275 | -0.19226 | -0.21515 | 122.4976 | 122.3511 | 0.09613 | 122.6715 | 122.6486 | 0.29755 | -0.13733 | 122.3969 | 122.374 | 0.050354 | 122.6395 | 122.6532 | 0.27924 | -0.009156 | 122.8271 | 122.5937 | 122.5937 | -0.37994 | 122.7814 | 122.7219 | 122.6761 | -0.35706
2594.6406 | 122.8821 | -122.58 | 0.13275 | 0.18663 | 0.022053 | 0.0068819 | 0.36289 | -0.071573 | -0.024085 | 0.031279 | 0.097976 | -0.01332 | -0.032393 | -0.065484 | 0.00029315 | 0.1035 | -0.004578 | 0.086975 | -0.022888 | 0.050354 | 0.24719 | -0.086975 | -0.24261 | 0.045776 | 0.07782 | 0.054932 | 0.18768 | 0.12817 | -0.20142 | -0.21515 | 122.493 | 122.3373 | 0.11444 | 122.6669 | 122.6303 | 0.29297 | -0.13733 | 122.3785 | 122.3648 | 0.054932 | 122.6257 | 122.6349 | 0.27008 | -0.004577 | 122.8271 | 122.5754 | 122.5571 | -0.37537 | 122.7676 | 122.7081 | 122.6578 | -0.3479
2595.6406 | 122.8546 | -122.58 | 0.15106 | 0.33921 | 0.010304 | 0.010086 | 0.35968 | -0.075845 | -0.010199 | 0.01953 | 0.14375 | -0.011183 | -0.036666 | -0.064416 | -0.0050469 | 0.09923 | -0.004578 | 0.064087 | -0.018311 | 0.054932 | 0.23804 | -0.1236 | -0.24719 | 0.027466 | 0.054932 | 0.022888 | 0.19684 | 0.12817 | -0.20142 | -0.22888 | 122.4564 | 122.3328 | 0.086975 | 122.644 | 122.6349 | 0.30212 | -0.15564 | 122.3785 | 122.3511 | 0.045776 | 122.6074 | 122.6028 | 0.25177 | -0.022888 | 122.818 | 122.5754 | 122.5616 | -0.39825 | 122.7768 | 122.7081 | 122.6349 | -0.37994
2596.6562 | 122.8134 | -122.5983 | 0.16022 | -0.11855 | 0.044484 | 0.00047294 | 0.37357 | -0.065164 | 0.010095 | 0.040892 | -0.32927 | 0.0048376 | -0.035598 | -0.059075 | 0.034473 | 0.091753 | 0.036621 | 0.064087 | -0.068665 | 0.064087 | 0.27924 | -0.11902 | -0.27924 | 0.013733 | 0.022888 | -0.032043 | 0.21973 | 0.15564 | -0.22888 | -0.24719 | 122.4792 | 122.319 | 0.11902 | 122.6624 | 122.6624 | 0.34332 | -0.1236 | 122.3694 | 122.3511 | 0.05951 | 122.612 | 122.5662 | 0.21515 | -0.004577 | 122.8775 | 122.6349 | 122.5296 | -0.43945 | 122.818 | 122.7539 | 122.6212 | -0.40741
2597.6406 | 122.8729 | -122.5845 | 0.14191 | 0.44602 | 0.038075 | 0.0047449 | 0.37464 | -0.079049 | -0.023017 | 0.039824 | 0.571 | -0.011183 | -0.040938 | -0.064416 | 0.0077701 | 0.11525 | 0.032043 | 0.068665 | -0.022888 | 0.054932 | 0.22888 | -0.082397 | -0.25177 | 0.036621 | 0.050354 | 0.022888 | 0.18768 | 0.14191 | -0.19226 | -0.21515 | 122.5021 | 122.3328 | 0.086975 | 122.6532 | 122.6395 | 0.3067 | -0.10986 | 122.3923 | 122.3694 | 0.045776 | 122.6212 | 122.6074 | 0.23804 | 0 | 122.8134 | 122.6166 | 122.5616 | -0.39368 | 122.7722 | 122.7264 | 122.6349 | -0.35706
2598.6406 | 122.8409 | -122.5891 | 0.12817 | 0.33921 | 0.017781 | -0.0091401 | 0.36075 | -0.068368 | -0.017676 | 0.031279 | 0.32686 | -0.014388 | -0.038802 | -0.059075 | 0.0077701 | 0.10457 | 0.009155 | 0.07782 | -0.022888 | 0.050354 | 0.23346 | -0.07782 | -0.25635 | 0.032043 | 0.059509 | 0.027466 | 0.19684 | 0.14191 | -0.19226 | -0.2243 | 122.5113 | 122.3328 | 0.10528 | 122.6669 | 122.6395 | 0.3067 | -0.11902 | 122.3969 | 122.3648 | 0.068664 | 122.6212 | 122.6166 | 0.25177 | 0.013733 | 122.8226 | 122.5983 | 122.5662 | -0.38452 | 122.7859 | 122.731 | 122.6486 | -0.35248
2599.6406 | 122.8638 | -122.5891 | 0.13733 | 0.44602 | 0.031666 | 0.0036769 | 0.35861 | -0.080117 | -0.030494 | 0.035552 | 0.37263 | -0.016524 | -0.045211 | -0.056939 | -0.0061159 | 0.09923 | 0.027466 | 0.086975 | -0.013733 | 0.036621 | 0.26093 | -0.082397 | -0.24261 | 0.041199 | 0.059509 | 0.027466 | 0.1831 | 0.13275 | -0.19684 | -0.21973 | 122.5067 | 122.3465 | 0.1236 | 122.6761 | 122.6257 | 0.27924 | -0.10986 | 122.3923 | 122.3694 | 0.045776 | 122.6303 | 122.6166 | 0.24719 | -0.004578 | 122.85 | 122.6166 | 122.5754 | -0.37994 | 122.7722 | 122.7219 | 122.6486 | -0.35706
2600.6562 | 122.8271 | -122.6212 | 0.14648 | -0.2101 | 0.045552 | -0.00059506 | 0.37143 | -0.074777 | 0.0068901 | 0.033416 | -0.45134 | -0.0058434 | -0.045211 | -0.052667 | 0.020587 | 0.090685 | 0.013733 | 0.009155 | -0.10529 | 0.022888 | 0.27008 | -0.13275 | -0.27466 | -0.009155 | 0.027466 | -0.068665 | 0.22888 | 0.15564 | -0.22888 | -0.25177 | 122.4884 | 122.3465 | 0.1236 | 122.6303 | 122.644 | 0.29755 | -0.13275 | 122.3923 | 122.3694 | 0.082398 | 122.612 | 122.5525 | 0.1831 | 0.009156 | 122.8912 | 122.6349 | 122.5159 | -0.42114 | 122.85 | 122.7768 | 122.6486 | -0.39825
2601.6406 | 122.8592 | -122.6257 | 0.1236 | 0.50706 | 0.02953 | 0.00047294 | 0.37357 | -0.059823 | -0.01554 | 0.050505 | 0.40315 | -0.0090474 | -0.024916 | -0.07937 | 0.015247 | 0.11418 | 0.068665 | 0.10986 | 0.004578 | 0.073242 | 0.22888 | -0.059509 | -0.23804 | 0.068665 | 0.07782 | 0.036621 | 0.18768 | 0.10986 | -0.17853 | -0.21057 | 122.5662 | 122.3877 | 0.10529 | 122.7356 | 122.699 | 0.31128 | -0.054931 | 122.4472 | 122.4152 | 0.064087 | 122.6944 | 122.6624 | 0.24719 | -0.013733 | 122.8546 | 122.6944 | 122.6303 | -0.36163 | 122.8134 | 122.7356 | 122.7036 | -0.33417
2602.6406 | 122.8867 | -122.6212 | 0.14648 | 0.27818 | 0.015645 | -0.0027321 | 0.35221 | -0.068368 | -0.019813 | 0.034484 | 0.17427 | -0.010115 | -0.037734 | -0.065484 | -0.0061159 | 0.10137 | 0.013733 | 0.064087 | -0.018311 | 0.050354 | 0.25177 | -0.10071 | -0.24261 | 0.041199 | 0.068665 | 0.036621 | 0.20142 | 0.13733 | -0.19226 | -0.21973 | 122.5204 | 122.3785 | 0.10529 | 122.6852 | 122.6715 | 0.29297 | -0.13275 | 122.4289 | 122.4014 | 0.054932 | 122.6624 | 122.6578 | 0.25635 | -0.009155 | 122.8729 | 122.6349 | 122.6028 | -0.3891 | 122.8226 | 122.7585 | 122.6898 | -0.36621
2603.6406 | 122.8867 | -122.6532 | 0.13275 | 0.33921 | 0.030598 | -0.00059506 | 0.35968 | -0.080117 | -0.026221 | 0.025939 | 0.15901 | -0.011183 | -0.053756 | -0.059075 | 0.0034971 | 0.10671 | 0.022888 | 0.059509 | -0.022888 | 0.050354 | 0.23804 | -0.10529 | -0.25635 | 0.032043 | 0.045776 | 0.027466 | 0.20599 | 0.14648 | -0.1831 | -0.21057 | 122.5479 | 122.3969 | 0.10529 | 122.7127 | 122.7036 | 0.3067 | -0.10986 | 122.4701 | 122.4426 | 0.073243 | 122.6852 | 122.6807 | 0.23804 | 0.013733 | 122.8912 | 122.6761 | 122.6303 | -0.3891 | 122.8592 | 122.7997 | 122.699 | -0.34332
2604.6406 | 122.8867 | -122.6303 | 0.12817 | 0.2324 | 0.034871 | 0.014358 | 0.36502 | -0.073709 | -0.018744 | 0.039824 | 0.082718 | -0.016524 | -0.025985 | -0.059075 | 0.010974 | 0.10243 | 0.009155 | 0.059509 | -0.027466 | 0.036621 | 0.25635 | -0.086975 | -0.24261 | 0.050354 | 0.073242 | 0.045776 | 0.19226 | 0.13275 | -0.19226 | -0.21057 | 122.5433 | 122.3877 | 0.12817 | 122.6898 | 122.6669 | 0.27924 | -0.11902 | 122.438 | 122.4197 | 0.064087 | 122.6807 | 122.6761 | 0.25635 | 0.004577 | 122.8867 | 122.6395 | 122.6028 | -0.37079 | 122.8226 | 122.7631 | 122.7036 | -0.33875
2605.6406 | 122.9279 | -122.6166 | 0.13733 | 0.43077 | 0.042347 | -0.0080721 | 0.35221 | -0.069436 | 0.0047541 | 0.045165 | 0.32686 | -0.011183 | -0.03987 | -0.052667 | 0.020587 | 0.09923 | 0.10071 | 0.11902 | 0.013733 | 0.09613 | 0.22888 | -0.086975 | -0.25635 | 0.10529 | 0.091553 | 0.054932 | 0.1831 | 0.14191 | -0.19226 | -0.21057 | 122.5296 | 122.3602 | 0.091553 | 122.7356 | 122.7127 | 0.35248 | -0.036621 | 122.4243 | 122.406 | 0.045776 | 122.7219 | 122.6715 | 0.2655 | 0.004578 | 122.8455 | 122.7173 | 122.6303 | -0.39368 | 122.7997 | 122.7585 | 122.7081 | -0.3479
2606.6406 | 122.9187 | -122.5845 | 0.1236 | 0.61387 | 0.054097 | 0.0047449 | 0.35434 | -0.058755 | -0.0037909 | 0.045165 | 0.44893 | -0.012251 | -0.038802 | -0.075097 | 0.025928 | 0.09923 | 0.11444 | 0.1236 | 0.022888 | 0.091553 | 0.24261 | -0.064087 | -0.2243 | 0.1236 | 0.09613 | 0.054932 | 0.16479 | 0.11902 | -0.19684 | -0.20599 | 122.5204 | 122.3602 | 0.11902 | 122.7081 | 122.6761 | 0.31586 | -0.009155 | 122.3877 | 122.3785 | 0.041199 | 122.7081 | 122.6395 | 0.26093 | -0.004577 | 122.8271 | 122.699 | 122.6074 | -0.3479 | 122.7493 | 122.7036 | 122.6807 | -0.32959
2607.6406 | 122.9324 | -122.6074 | 0.14191 | 0.2324 | 0.064778 | 0.0058129 | 0.36289 | -0.060891 | -0.010199 | 0.05371 | 0.40315 | -0.00050244 | -0.03987 | -0.06762 | 0.017383 | 0.11098 | 0.10071 | 0.13733 | 0.009155 | 0.082397 | 0.23346 | -0.068665 | -0.23346 | 0.11444 | 0.10071 | 0.050354 | 0.19226 | 0.1236 | -0.18768 | -0.21515 | 122.5388 | 122.374 | 0.091552 | 122.7448 | 122.6898 | 0.31586 | -0.041199 | 122.4197 | 122.3923 | 0.050354 | 122.7219 | 122.6578 | 0.2655 | -0.018311 | 122.8409 | 122.7081 | 122.6166 | -0.37537 | 122.7997 | 122.731 | 122.7081 | -0.35706
2608.6406 | 122.937 | -122.5937 | 0.11902 | 0.58335 | 0.061574 | 0.011154 | 0.3725 | -0.071573 | -0.0048589 | 0.047301 | 0.38789 | -0.0090474 | -0.03453 | -0.06762 | 0.023792 | 0.10564 | 0.086975 | 0.12817 | 0.022888 | 0.07782 | 0.23346 | -0.064087 | -0.2243 | 0.11444 | 0.10529 | 0.054932 | 0.17395 | 0.11902 | -0.17853 | -0.21057 | 122.5296 | 122.3694 | 0.11444 | 122.7219 | 122.6715 | 0.30212 | -0.032044 | 122.4152 | 122.3831 | 0.054931 | 122.7081 | 122.6486 | 0.2655 | 0 | 122.8271 | 122.6807 | 122.6166 | -0.34332 | 122.7676 | 122.7127 | 122.699 | -0.32959
2609.6406 | 122.8867 | -122.6486 | 0.13275 | 0.56809 | 0.055165 | -0.0027321 | 0.37784 | -0.064096 | 0.013299 | 0.04196 | 0.26582 | 0.0027016 | -0.032393 | -0.055871 | 0.017383 | 0.10243 | 0.068665 | 0.045776 | -0.054932 | 0.045776 | 0.26093 | -0.09613 | -0.2655 | 0.10071 | 0.082397 | 0.022888 | 0.19226 | 0.13733 | -0.18768 | -0.21973 | 122.5525 | 122.3831 | 0.12817 | 122.6944 | 122.6944 | 0.31128 | -0.064086 | 122.4609 | 122.4289 | 0.05951 | 122.7493 | 122.6715 | 0.24261 | 0.004578 | 122.9095 | 122.7173 | 122.5937 | -0.39825 | 122.8409 | 122.7859 | 122.731 | -0.35248
2610.6562 | 122.9187 | -122.6303 | 0.15106 | -0.2101 | 0.037007 | 0.014358 | 0.37998 | -0.066232 | -0.031562 | 0.040892 | -0.29875 | -0.0058434 | -0.051619 | -0.049462 | 0.0013611 | 0.10671 | 0.073242 | 0.13733 | 0.032043 | 0.086975 | 0.23804 | -0.10071 | -0.26093 | 0.064087 | 0.15564 | 0.054932 | 0.17853 | 0.10986 | -0.19226 | -0.21515 | 122.5296 | 122.3694 | 0.086975 | 122.7676 | 122.7173 | 0.3479 | -0.07782 | 122.438 | 122.4152 | 0.027466 | 122.6944 | 122.6852 | 0.27008 | -0.041199 | 122.8683 | 122.7036 | 122.6624 | -0.41199 | 122.8088 | 122.7402 | 122.7859 | -0.36621
2611.6406 | 122.85 | -122.6624 | 0.13275 | 0.44602 | 0.065846 | 0.0079499 | 0.3693 | -0.071573 | 0.010095 | 0.037688 | 0.15901 | 0.0080426 | -0.013167 | -0.065484 | 0.032337 | 0.09923 | 0.041199 | -0.013733 | -0.09613 | 0.009155 | 0.27008 | -0.11902 | -0.27924 | 0.018311 | -0.009155 | -0.045776 | 0.21973 | 0.16022 | -0.21515 | -0.24261 | 122.5433 | 122.3831 | 0.13733 | 122.6486 | 122.6715 | 0.28839 | -0.091552 | 122.4472 | 122.4197 | 0.086976 | 122.6807 | 122.6166 | 0.19684 | 0.027466 | 122.9324 | 122.7036 | 122.5662 | -0.41199 | 122.8821 | 122.8226 | 122.6532 | -0.37537
2612.6875 | 122.9462 | -122.644 | 0.13733 | 0.034038 | 0.035939 | 0.015426 | 0.3725 | -0.075845 | -0.035834 | 0.029143 | -0.22246 | -0.015456 | -0.035598 | -0.070825 | 0.0077701 | 0.11312 | 0.091553 | 0.16937 | 0.054932 | 0.10986 | 0.23804 | -0.082397 | -0.25635 | 0.073242 | 0.16479 | 0.082397 | 0.19684 | 0.14191 | -0.19226 | -0.21057 | 122.5616 | 122.3877 | 0.10071 | 122.8134 | 122.7539 | 0.36621 | -0.045776 | 122.4518 | 122.4335 | 0.059509 | 122.7173 | 122.7264 | 0.29297 | 0.004578 | 122.8821 | 122.7356 | 122.699 | -0.39368 | 122.8409 | 122.7859 | 122.8088 | -0.3479
2613.6406 | 122.9462 | -122.6349 | 0.1236 | 0.56809 | 0.042347 | 0.012222 | 0.37143 | -0.060891 | -0.00058594 | 0.03662 | 1.0745 | 0.0016336 | -0.042006 | -0.068688 | 0.0302 | 0.10671 | 0.091553 | 0.068665 | 0.013733 | 0.091553 | 0.25635 | -0.10529 | -0.26093 | 0.09613 | 0.10071 | 0.054932 | 0.19226 | 0.11902 | -0.17395 | -0.21515 | 122.5296 | 122.374 | 0.13275 | 122.7036 | 122.7264 | 0.35248 | -0.032043 | 122.4609 | 122.4197 | 0.068665 | 122.731 | 122.6898 | 0.27008 | -0.004577 | 122.8912 | 122.7264 | 122.6486 | -0.38452 | 122.8271 | 122.7539 | 122.7356 | -0.33875
2614.6875 | 122.8363 | -122.7081 | 0.17853 | -0.19484 | 0.048756 | 0.0090179 | 0.36609 | -0.060891 | -0.011268 | 0.035552 | -0.52763 | 0.00056556 | -0.027053 | -0.066552 | 0.016315 | 0.09923 | 0.027466 | -0.004578 | -0.091553 | 0 | 0.26093 | -0.10986 | -0.29297 | -0.041199 | 0.032043 | -0.036621 | 0.21973 | 0.17395 | -0.24719 | -0.26093 | 122.5983 | 122.4152 | 0.082397 | 122.7036 | 122.7081 | 0.29297 | -0.15106 | 122.4609 | 122.4472 | 0.041199 | 122.6669 | 122.6715 | 0.2243 | -0.004578 | 122.9691 | 122.7356 | 122.6166 | -0.4715 | 122.9279 | 122.8821 | 122.7402 | -0.43945
2615.6406 | 122.8455 | -122.6624 | 0.15564 | 0.61387 | 0.061574 | -0.0048681 | 0.36823 | -0.064096 | -0.0016549 | 0.039824 | 0.22005 | 0.0059056 | -0.035598 | -0.058007 | 0.014179 | 0.10564 | 0.036621 | -0.036621 | -0.086975 | 0.009155 | 0.27924 | -0.10986 | -0.29755 | -0.009155 | -0.022888 | -0.064087 | 0.23804 | 0.16479 | -0.21973 | -0.25635 | 122.5525 | 122.3648 | 0.1236 | 122.6257 | 122.6715 | 0.3067 | -0.11902 | 122.4426 | 122.406 | 0.082397 | 122.6532 | 122.5983 | 0.19226 | 0.009155 | 122.9416 | 122.699 | 122.5754 | -0.45319 | 122.9004 | 122.8271 | 122.6395 | -0.41199
2616.6406 | 122.8409 | -122.6944 | 0.15106 | 0.81224 | 0.076527 | -0.0016631 | 0.35648 | -0.061959 | 0.00048206 | 0.043029 | 0.17427 | 0.0069746 | -0.024916 | -0.064416 | 0.020587 | 0.10137 | 0 | -0.045776 | -0.1236 | -0.009155 | 0.27924 | -0.11902 | -0.27924 | -0.009155 | -0.032043 | -0.059509 | 0.21973 | 0.16479 | -0.22888 | -0.25177 | 122.5754 | 122.4152 | 0.12817 | 122.6486 | 122.6852 | 0.27008 | -0.15106 | 122.4655 | 122.4426 | 0.068665 | 122.6852 | 122.6349 | 0.19226 | 0.013733 | 122.9736 | 122.6944 | 122.5708 | -0.4303 | 122.9141 | 122.8592 | 122.6624 | -0.40283
2617.6406 | 122.7997 | -122.6898 | 0.15564 | 0.32395 | 0.075459 | -0.0016631 | 0.37891 | -0.049142 | 0.0036861 | 0.043029 | 0.54048 | 0.0048376 | -0.042006 | -0.063348 | 0.026996 | 0.10778 | 0.004578 | -0.032043 | -0.091553 | 0.013733 | 0.2655 | -0.11444 | -0.28839 | -0.041199 | -0.032043 | -0.11444 | 0.22888 | 0.16479 | -0.21973 | -0.23346 | 122.5754 | 122.4014 | 0.10986 | 122.6578 | 122.7036 | 0.30212 | -0.15106 | 122.4701 | 122.4564 | 0.073242 | 122.6486 | 122.5754 | 0.11902 | 0.009155 | 122.9553 | 122.6944 | 122.5983 | -0.44403 | 122.9187 | 122.8546 | 122.6578 | -0.3891
2618.6406 | 122.8683 | -122.6715 | 0.14648 | 0.53758 | 0.061574 | -0.0016631 | 0.3693 | -0.068368 | 0.0068901 | 0.047301 | 0.35738 | 0.0016336 | -0.030257 | -0.06762 | 0.014179 | 0.11312 | 0.004578 | 0.009155 | -0.082397 | 0 | 0.2655 | -0.10986 | -0.26093 | 0.009155 | 0.009155 | -0.032043 | 0.22888 | 0.14648 | -0.21973 | -0.2243 | 122.5616 | 122.4106 | 0.11902 | 122.6807 | 122.6715 | 0.26093 | -0.14191 | 122.4518 | 122.4472 | 0.082398 | 122.6807 | 122.6395 | 0.19226 | 0 | 122.937 | 122.6761 | 122.5891 | -0.40741 | 122.9004 | 122.818 | 122.6807 | -0.37079
2619.6406 | 122.8592 | -122.7036 | 0.16022 | 0.55284 | 0.054097 | -0.0038001 | 0.36182 | -0.070504 | -0.0059269 | 0.055846 | 0.26582 | -0.0058434 | -0.019576 | -0.056939 | 0.0099061 | 0.10991 | 0.004578 | -0.036621 | -0.091553 | 0.004578 | 0.27466 | -0.10071 | -0.28839 | -0.027466 | -0.013733 | -0.050354 | 0.24261 | 0.17853 | -0.22888 | -0.24719 | 122.6028 | 122.4152 | 0.11444 | 122.6669 | 122.7081 | 0.29297 | -0.15564 | 122.4747 | 122.4564 | 0.082398 | 122.6761 | 122.6532 | 0.19684 | 0.018311 | 122.9782 | 122.7081 | 122.612 | -0.44861 | 122.9462 | 122.8821 | 122.6898 | -0.40741
2620.6406 | 122.8363 | -122.7127 | 0.15564 | 0.50706 | 0.0808 | -0.0070041 | 0.36823 | -0.072641 | 0.0015501 | 0.043029 | 0.26582 | 0.0048376 | -0.012099 | -0.072961 | 0.020587 | 0.10564 | -0.032043 | -0.018311 | -0.10986 | 0.027466 | 0.27924 | -0.09613 | -0.27466 | -0.041199 | -0.032043 | -0.082397 | 0.23804 | 0.16937 | -0.21973 | -0.2655 | 122.6166 | 122.4381 | 0.1236 | 122.6944 | 122.7402 | 0.30212 | -0.18768 | 122.493 | 122.4472 | 0.082397 | 122.6715 | 122.6303 | 0.18311 | 0.013733 | 122.9919 | 122.6807 | 122.6028 | -0.4303 | 122.9507 | 122.8821 | 122.6807 | -0.42114
2621.6406 | 122.8455 | -122.7081 | 0.18768 | 0.11033 | 0.064778 | 0.0068819 | 0.38211 | -0.061959 | 0.00048206 | 0.043029 | 0.0064239 | 0.0091106 | -0.027053 | -0.066552 | 0.018451 | 0.10991 | 0.018311 | 0.022888 | -0.09613 | 0.022888 | 0.26093 | -0.10529 | -0.27924 | -0.018311 | 0.013733 | -0.064087 | 0.2243 | 0.16479 | -0.21057 | -0.23346 | 122.6028 | 122.4289 | 0.073242 | 122.731 | 122.731 | 0.30212 | -0.16937 | 122.4976 | 122.4747 | 0.036621 | 122.6898 | 122.644 | 0.16937 | -0.022888 | 122.9691 | 122.7264 | 122.612 | -0.46692 | 122.9324 | 122.8729 | 122.7219 | -0.42114
2622.6875 | 122.9599 | -122.699 | 0.16022 | 0.17137 | 0.053029 | 0.017563 | 0.35114 | -0.071573 | -0.052924 | 0.030211 | 0.35738 | -0.015456 | -0.035598 | -0.069756 | 0.0013611 | 0.11739 | -0.054932 | 0.054932 | -0.009155 | 0.059509 | 0.23804 | -0.086975 | -0.24719 | 0.013733 | 0.07782 | 0.064087 | 0.20142 | 0.15564 | -0.21057 | -0.21057 | 122.612 | 122.4518 | 0.07782 | 122.7539 | 122.7585 | 0.3067 | -0.21515 | 122.4884 | 122.4884 | 0.041199 | 122.7127 | 122.7631 | 0.27466 | -0.004577 | 122.937 | 122.644 | 122.6898 | -0.40741 | 122.9004 | 122.8546 | 122.7768 | -0.37079
2623.6406 | 122.8546 | -122.7081 | 0.15564 | 0.21714 | 0.065846 | 0.014358 | 0.35221 | -0.059823 | 0.0068901 | 0.040892 | 0.0522 | -0.00050244 | -0.035598 | -0.058007 | 0.031268 | 0.10137 | 0.022888 | 0.013733 | -0.09613 | 0.036621 | 0.27008 | -0.10529 | -0.25635 | -0.027466 | 0 | -0.073242 | 0.21515 | 0.16479 | -0.22888 | -0.25177 | 122.6028 | 122.4518 | 0.11444 | 122.7219 | 122.7448 | 0.29297 | -0.13275 | 122.4792 | 122.4564 | 0.059509 | 122.6807 | 122.6349 | 0.17853 | 0.009155 | 122.9782 | 122.731 | 122.612 | -0.41199 | 122.9233 | 122.8729 | 122.7081 | -0.40741
2624.6719 | 122.9324 | -122.6898 | 0.12817 | 0.50706 | 0.051961 | 0.0068819 | 0.35114 | -0.066232 | -0.020881 | 0.046233 | 0.50996 | -0.011183 | -0.029189 | -0.065484 | -0.0039789 | 0.11632 | 0.045776 | 0.09613 | 0.004578 | 0.064087 | 0.23346 | -0.086975 | -0.24261 | 0.045776 | 0.082397 | 0.054932 | 0.1831 | 0.12817 | -0.20142 | -0.23346 | 122.6028 | 122.4472 | 0.10528 | 122.7859 | 122.7539 | 0.3067 | -0.082398 | 122.4884 | 122.4564 | 0.054931 | 122.7356 | 122.7448 | 0.28839 | 0 | 122.9233 | 122.7356 | 122.6944 | -0.37079 | 122.8729 | 122.818 | 122.7722 | -0.36163
2625.6406 | 122.8912 | -122.7173 | 0.14648 | -0.10329 | 0.053029 | 0.0015409 | 0.35861 | -0.066232 | -0.0080629 | 0.043029 | -0.14616 | -0.0047754 | -0.032393 | -0.069756 | 0.012042 | 0.10457 | 0.041199 | 0.054932 | -0.059509 | 0.045776 | 0.27466 | -0.10986 | -0.27466 | 0.009155 | 0.045776 | -0.018311 | 0.21515 | 0.16022 | -0.23346 | -0.22888 | 122.6074 | 122.4426 | 0.12817 | 122.7722 | 122.7631 | 0.32043 | -0.10529 | 122.4838 | 122.4884 | 0.068665 | 122.7264 | 122.699 | 0.21057 | 0.013733 | 122.9919 | 122.7585 | 122.6578 | -0.42114 | 122.9324 | 122.8775 | 122.7631 | -0.37537
2626.6406 | 122.905 | -122.6898 | 0.15564 | -0.17959 | 0.058369 | 0.0047449 | 0.35968 | -0.043802 | -0.0027229 | 0.039824 | -0.37505 | -0.00050244 | -0.023848 | -0.060143 | 0.01311 | 0.10778 | 0.009155 | 0.009155 | -0.091553 | 0.027466 | 0.27924 | -0.1236 | -0.27924 | -0.009155 | 0.045776 | -0.022888 | 0.22888 | 0.17395 | -0.21515 | -0.24261 | 122.5662 | 122.4106 | 0.1236 | 122.699 | 122.7173 | 0.3067 | -0.14649 | 122.4747 | 122.4472 | 0.073242 | 122.6807 | 122.6669 | 0.21973 | 0.01831 | 122.9691 | 122.699 | 122.5983 | -0.43488 | 122.9187 | 122.8638 | 122.7356 | -0.39826
2627.6406 | 122.8958 | -122.7081 | 0.15106 | -0.14907 | 0.062642 | -0.0038001 | 0.35861 | -0.061959 | -0.0048589 | 0.049437 | -0.28349 | 0.0016336 | -0.03987 | -0.065484 | 0.022724 | 0.10457 | 0.004578 | 0.032043 | -0.068665 | 0.045776 | 0.2655 | -0.10986 | -0.27008 | 0 | 0.022888 | -0.022888 | 0.2243 | 0.16937 | -0.21057 | -0.23346 | 122.5983 | 122.438 | 0.11444 | 122.7402 | 122.7539 | 0.31586 | -0.14648 | 122.4976 | 122.4747 | 0.073242 | 122.7081 | 122.6852 | 0.21057 | 0.018311 | 122.9736 | 122.7127 | 122.6395 | -0.42114 | 122.9324 | 122.8775 | 122.731 | -0.38452
2628.6406 | 122.9141 | -122.7081 | 0.15564 | -0.011739 | 0.048756 | 0.017563 | 0.3725 | -0.064096 | -0.0059269 | 0.054778 | -0.25298 | 0.0080426 | -0.029189 | -0.074029 | 0.012042 | 0.10884 | 0.009155 | 0.091553 | -0.050354 | 0.054932 | 0.27008 | -0.10986 | -0.27466 | 0.018311 | 0.064087 | -0.032043 | 0.21515 | 0.15106 | -0.2243 | -0.24719 | 122.5983 | 122.4335 | 0.11444 | 122.7997 | 122.7631 | 0.32959 | -0.14649 | 122.4838 | 122.4609 | 0.059509 | 122.7264 | 122.6761 | 0.21515 | -0.004578 | 122.9782 | 122.7173 | 122.6578 | -0.4303 | 122.9233 | 122.8592 | 122.7722 | -0.40283
2629.6406 | 122.9095 | -122.6944 | 0.15106 | -0.057515 | 0.077595 | -0.015549 | 0.37036 | -0.070504 | -0.0037909 | 0.046233 | -0.14616 | 0.0059056 | -0.031325 | -0.058007 | 0.018451 | 0.1003 | 0.022888 | 0.059509 | -0.064087 | 0.041199 | 0.26093 | -0.09613 | -0.2655 | 0.013733 | 0.045776 | -0.041199 | 0.24261 | 0.16022 | -0.21057 | -0.22888 | 122.5983 | 122.4289 | 0.10986 | 122.7539 | 122.7356 | 0.3067 | -0.12817 | 122.4838 | 122.4655 | 0.091553 | 122.7081 | 122.6532 | 0.18768 | 0.009155 | 122.9553 | 122.7173 | 122.6303 | -0.41656 | 122.937 | 122.8546 | 122.7402 | -0.37994
2630.6406 | 122.8958 | -122.699 | 0.16479 | -0.11855 | 0.044484 | -0.0091401 | 0.37143 | -0.072641 | -0.0048589 | 0.046233 | -0.35979 | -0.0026384 | -0.031325 | -0.058007 | 0.014179 | 0.089617 | 0 | 0.059509 | -0.064087 | 0.059509 | 0.27924 | -0.091553 | -0.28381 | -0.009155 | 0.059509 | -0.022888 | 0.22888 | 0.15564 | -0.22888 | -0.21515 | 122.6074 | 122.4152 | 0.11444 | 122.7585 | 122.7585 | 0.34332 | -0.16479 | 122.4701 | 122.4838 | 0.064087 | 122.6898 | 122.6761 | 0.19226 | -0.009155 | 122.9782 | 122.699 | 122.6349 | -0.44861 | 122.9279 | 122.8546 | 122.7585 | -0.37994
2631.6406 | 122.9095 | -122.731 | 0.16022 | -0.22536 | 0.050892 | 0.0079499 | 0.36289 | -0.054483 | -0.0080629 | 0.033416 | -0.26824 | 0.0016336 | -0.033461 | -0.068688 | 0.021655 | 0.11632 | -0.032043 | 0.018311 | -0.091553 | 0.027466 | 0.26093 | -0.1236 | -0.28839 | -0.013733 | 0.041199 | -0.009155 | 0.22888 | 0.15564 | -0.22888 | -0.25177 | 122.6074 | 122.4426 | 0.10071 | 122.7493 | 122.7585 | 0.31586 | -0.19226 | 122.5021 | 122.4792 | 0.068665 | 122.7173 | 122.7219 | 0.24261 | -0.004577 | 122.9919 | 122.699 | 122.6395 | -0.44861 | 122.9599 | 122.8867 | 122.7722 | -0.41199
2632.6406 | 122.8546 | -122.7081 | 0.14191 | -0.17959 | 0.034871 | 0.020767 | 0.36395 | -0.069436 | -0.040107 | 0.043029 | -0.26824 | -0.0090474 | -0.035598 | -0.066552 | 0.0034971 | 0.11205 | -0.022888 | 0.10529 | -0.045776 | 0.045776 | 0.26093 | -0.10529 | -0.26093 | -0.041199 | 0.045776 | -0.022888 | 0.21515 | 0.14648 | -0.2243 | -0.24719 | 122.6028 | 122.4472 | 0.11902 | 122.8134 | 122.7539 | 0.3067 | -0.16479 | 122.4838 | 122.4609 | 0.073242 | 122.6669 | 122.6852 | 0.2243 | 0.004577 | 122.9691 | 122.6852 | 122.6624 | -0.40283 | 122.9233 | 122.8546 | 122.7539 | -0.3891
2633.6406 | 122.9599 | -122.7264 | 0.13733 | -0.10329 | 0.014576 | 0.0079499 | 0.37143 | -0.068368 | -0.028357 | 0.028075 | -0.23772 | -0.015456 | -0.023848 | -0.070825 | -0.0071839 | 0.10778 | 0.013733 | 0.12817 | 0.009155 | 0.091553 | 0.24261 | -0.073242 | -0.25177 | 0.013733 | 0.091553 | 0.027466 | 0.20142 | 0.14648 | -0.20142 | -0.22888 | 122.6532 | 122.4747 | 0.10529 | 122.8546 | 122.818 | 0.34332 | -0.1236 | 122.525 | 122.4976 | 0.064087 | 122.7402 | 122.7539 | 0.25635 | 0.009155 | 122.9691 | 122.7402 | 122.7356 | -0.3891 | 122.9279 | 122.8729 | 122.818 | -0.36621
2634.6406 | 122.905 | -122.7356 | 0.15564 | -0.24062 | 0.026326 | 0.020767 | 0.3693 | -0.070504 | -0.021949 | 0.022734 | -0.28349 | -0.011183 | -0.023848 | -0.066552 | 0.0099061 | 0.10243 | 0.009155 | 0.10529 | -0.018311 | 0.045776 | 0.25635 | -0.09613 | -0.25635 | -0.022888 | 0.045776 | 0.009155 | 0.21973 | 0.14648 | -0.21057 | -0.25177 | 122.6395 | 122.4792 | 0.10071 | 122.8409 | 122.7814 | 0.30212 | -0.14649 | 122.525 | 122.4838 | 0.064087 | 122.7127 | 122.7448 | 0.26093 | -0.009156 | 122.9919 | 122.7448 | 122.7173 | -0.41199 | 122.9553 | 122.8821 | 122.7814 | -0.40741
2635.6406 | 122.8958 | -122.7402 | 0.16479 | 0.2324 | 0.058369 | 0.00047294 | 0.37998 | -0.070504 | 0.014367 | 0.039824 | 0.021682 | 0.0059056 | -0.029189 | -0.065484 | 0.012042 | 0.098162 | 0.041199 | 0.013733 | -0.09613 | 0.022888 | 0.2655 | -0.091553 | -0.27466 | -0.022888 | -0.013733 | -0.082397 | 0.2243 | 0.17395 | -0.21057 | -0.24261 | 122.6486 | 122.4655 | 0.10071 | 122.7539 | 122.7631 | 0.29755 | -0.1236 | 122.5296 | 122.4976 | 0.059509 | 122.7173 | 122.6578 | 0.16022 | 0.009155 | 123.0057 | 122.7814 | 122.644 | -0.43945 | 122.9645 | 122.9141 | 122.7264 | -0.40741
2636.6406 | 122.9004 | -122.7173 | 0.16937 | 0.47654 | 0.031666 | 0.0079499 | 0.37464 | -0.063028 | 0.0036861 | 0.050505 | 0.29634 | 0.0069746 | -0.021712 | -0.055871 | 0.028064 | 0.10884 | 0 | -0.032043 | -0.1236 | -0.004578 | 0.27466 | -0.10986 | -0.27466 | -0.027466 | -0.041199 | -0.068665 | 0.21515 | 0.17853 | -0.21973 | -0.23804 | 122.6074 | 122.4426 | 0.10529 | 122.6852 | 122.7127 | 0.27008 | -0.16937 | 122.4976 | 122.4792 | 0.045776 | 122.6898 | 122.6486 | 0.16937 | 0.009155 | 122.9919 | 122.7173 | 122.5937 | -0.44403 | 122.9324 | 122.8958 | 122.6761 | -0.40741
2637.6406 | 123.0103 | -122.6944 | 0.15106 | -0.10329 | 0.0060322 | 0.012222 | 0.36289 | -0.074777 | -0.051856 | 0.045165 | -0.085129 | -0.0069114 | -0.043074 | -0.064416 | -0.010388 | 0.10778 | 0.059509 | 0.17395 | 0.045776 | 0.10986 | 0.24261 | -0.07782 | -0.27008 | 0.054932 | 0.14648 | 0.086975 | 0.18768 | 0.14191 | -0.18768 | -0.21515 | 122.6166 | 122.4243 | 0.091553 | 122.8683 | 122.8043 | 0.37994 | -0.091553 | 122.5067 | 122.4792 | 0.036621 | 122.7493 | 122.7814 | 0.30212 | -0.009155 | 122.937 | 122.7539 | 122.7402 | -0.42114 | 122.8821 | 122.8363 | 122.8409 | -0.36621
2638.6406 | 123.0103 | -122.6944 | 0.1236 | 0.034038 | 0.0092362 | 0.016495 | 0.35541 | -0.063028 | -0.041175 | 0.020598 | 0.082718 | -0.017592 | -0.043074 | -0.063348 | -0.014661 | 0.11205 | 0.036621 | 0.14648 | 0.013733 | 0.082397 | 0.22888 | -0.09613 | -0.24719 | 0.073242 | 0.16022 | 0.10986 | 0.19226 | 0.12817 | -0.19226 | -0.20142 | 122.5983 | 122.4472 | 0.10529 | 122.8409 | 122.7768 | 0.32959 | -0.086975 | 122.5021 | 122.493 | 0.068665 | 122.7676 | 122.8043 | 0.31128 | 0.004578 | 122.9233 | 122.731 | 122.7081 | -0.37079 | 122.8867 | 122.8226 | 122.8546 | -0.32501
2639.6406 | 122.9919 | -122.7036 | 0.13733 | 0.049296 | 0.01244 | 0.017563 | 0.35648 | -0.066232 | -0.040107 | 0.030211 | 0.15901 | -0.0069114 | -0.031325 | -0.074029 | 0.0013611 | 0.10884 | 0.054932 | 0.091553 | 0.013733 | 0.064087 | 0.25177 | -0.082397 | -0.25177 | 0.07782 | 0.091553 | 0.073242 | 0.19684 | 0.11902 | -0.1831 | -0.21057 | 122.6212 | 122.4518 | 0.11444 | 122.7951 | 122.7676 | 0.31586 | -0.082397 | 122.5204 | 122.493 | 0.059509 | 122.7814 | 122.7768 | 0.28381 | -0.01831 | 122.9553 | 122.7585 | 122.7173 | -0.3891 | 122.9004 | 122.8226 | 122.7951 | -0.3479
2640.6562 | 122.8867 | -122.7356 | 0.16937 | 0.15611 | 0.061574 | -0.093521 | 0.38104 | -0.064096 | 0.027185 | 0.039824 | 0.036941 | 0.0048376 | -0.012099 | -0.051599 | 0.025928 | 0.083208 | 0.050354 | 0.041199 | -0.073242 | 0.032043 | 0.27008 | -0.10071 | -0.26093 | 0.009155 | -0.009155 | -0.07782 | 0.21057 | 0.16022 | -0.22888 | -0.24719 | 122.6349 | 122.4747 | 0.10071 | 122.7768 | 122.7676 | 0.29297 | -0.11902 | 122.5067 | 122.4884 | 0.041198 | 122.7448 | 122.6578 | 0.16937 | -0.009156 | 123.0057 | 122.7859 | 122.6624 | -0.4303 | 122.9462 | 122.8958 | 122.7264 | -0.41656
2641.6406 | 122.9782 | -122.7402 | 0.14191 | 0.15611 | 0.0060322 | 0.01329 | 0.36823 | -0.073709 | -0.039039 | 0.020598 | 0.082718 | -0.026137 | -0.045211 | -0.060143 | 0.0067021 | 0.12059 | 0.004578 | 0.10529 | -0.004578 | 0.054932 | 0.23804 | -0.086975 | -0.25177 | 0.059509 | 0.09613 | 0.064087 | 0.20142 | 0.12817 | -0.19684 | -0.21515 | 122.6532 | 122.4884 | 0.09613 | 122.8455 | 122.7951 | 0.3067 | -0.13733 | 122.5433 | 122.525 | 0.059509 | 122.7997 | 122.8043 | 0.27924 | -0.013733 | 122.9782 | 122.7448 | 122.7356 | -0.39368 | 122.9416 | 122.8683 | 122.8363 | -0.35706
2642.6406 | 123.0148 | -122.6807 | 0.1236 | 0.21714 | -0.0067858 | 0.020767 | 0.36502 | -0.073709 | -0.029426 | 0.018462 | -0.22246 | -0.019728 | -0.043074 | -0.061212 | -0.00077485 | 0.10991 | 0.086975 | 0.16937 | 0.050354 | 0.10986 | 0.24719 | -0.086975 | -0.24261 | 0.082397 | 0.14648 | 0.068665 | 0.19684 | 0.13275 | -0.18768 | -0.20599 | 122.5937 | 122.438 | 0.1236 | 122.85 | 122.7905 | 0.35248 | -0.036621 | 122.493 | 122.4747 | 0.073242 | 122.7631 | 122.7493 | 0.27466 | 0.009155 | 122.9279 | 122.7676 | 122.731 | -0.36621 | 122.8775 | 122.8134 | 122.8271 | -0.32959
2643.6406 | 123.0423 | -122.6898 | 0.13275 | -0.011739 | 0.018849 | 0.0079499 | 0.36502 | -0.056619 | -0.03263 | 0.028075 | 0.11323 | -0.0058434 | -0.053756 | -0.063348 | -0.012524 | 0.10778 | 0.064087 | 0.15106 | 0.018311 | 0.068665 | 0.23346 | -0.073242 | -0.24719 | 0.11444 | 0.09613 | 0.11444 | 0.18768 | 0.12817 | -0.17395 | -0.21057 | 122.6166 | 122.4426 | 0.10071 | 122.8409 | 122.7585 | 0.31586 | -0.068664 | 122.5159 | 122.4792 | 0.054932 | 122.8043 | 122.8043 | 0.32501 | -0.004577 | 122.9233 | 122.7539 | 122.7081 | -0.37994 | 122.8775 | 122.818 | 122.7859 | -0.34332
2644.6875 | 122.9462 | -122.6944 | 0.16022 | 0.55284 | 0.041279 | 0.0058129 | 0.3725 | -0.076913 | 0.019708 | 0.049437 | 0.25056 | -0.0015704 | -0.016372 | -0.053735 | 0.025928 | 0.092821 | 0.022888 | 0.018311 | -0.086975 | 0.018311 | 0.27466 | -0.09613 | -0.25177 | 0.032043 | 0.009155 | -0.027466 | 0.21057 | 0.14191 | -0.20142 | -0.24719 | 122.5983 | 122.4426 | 0.11444 | 122.7127 | 122.7127 | 0.27008 | -0.13733 | 122.493 | 122.4472 | 0.050354 | 122.7264 | 122.6669 | 0.21973 | -0.01831 | 122.9691 | 122.7173 | 122.6074 | -0.41199 | 122.905 | 122.8363 | 122.7036 | -0.40741
2645.6406 | 122.8821 | -122.7722 | 0.16937 | -0.27114 | 0.053029 | -0.011276 | 0.36716 | -0.076913 | -0.010199 | 0.04196 | -0.43608 | -0.0069114 | -0.025985 | -0.063348 | 0.0088381 | 0.10564 | -0.018311 | 0 | -0.10529 | 0.004578 | 0.27924 | -0.10986 | -0.29297 | -0.022888 | 0.004578 | -0.068665 | 0.23804 | 0.17395 | -0.2243 | -0.25177 | 122.6624 | 122.4792 | 0.10986 | 122.7722 | 122.7768 | 0.29755 | -0.18768 | 122.5479 | 122.5204 | 0.068664 | 122.7493 | 122.7036 | 0.1831 | 0.004577 | 123.0515 | 122.7539 | 122.6669 | -0.46234 | 123.0103 | 122.9462 | 122.7768 | -0.42114
2646.6406 | 122.9828 | -122.731 | 0.11444 | 0.52232 | 0.041279 | 0.0026089 | 0.3458 | -0.048074 | -0.01554 | 0.040892 | 0.44893 | 0.0037696 | -0.048415 | -0.060143 | 0.0088381 | 0.10564 | 0.045776 | 0.1236 | 0.022888 | 0.073242 | 0.23346 | -0.073242 | -0.22888 | 0.082397 | 0.10529 | 0.045776 | 0.16937 | 0.12817 | -0.18768 | -0.21515 | 122.6578 | 122.5021 | 0.11902 | 122.8546 | 122.8043 | 0.30212 | -0.068665 | 122.5433 | 122.5159 | 0.054932 | 122.8134 | 122.7768 | 0.26093 | 0.013733 | 122.9645 | 122.7768 | 122.7539 | -0.34332 | 122.9004 | 122.8592 | 122.8363 | -0.32959
2647.6719 | 122.9462 | -122.7356 | 0.14648 | -0.13381 | 0.065846 | -0.00059506 | 0.3725 | -0.051278 | 0.0090271 | 0.034484 | -0.48186 | 0.0048376 | -0.03453 | -0.069756 | 0.02486 | 0.10564 | 0.022888 | 0.027466 | -0.10071 | 0.036621 | 0.28381 | -0.11902 | -0.28839 | -0.004578 | 0.059509 | -0.032043 | 0.2243 | 0.17853 | -0.21057 | -0.22888 | 122.6166 | 122.4472 | 0.13733 | 122.7631 | 122.7722 | 0.32501 | -0.1236 | 122.525 | 122.5067 | 0.07782 | 122.731 | 122.7036 | 0.19684 | 0.032044 | 123.0194 | 122.7585 | 122.6349 | -0.43488 | 122.9599 | 122.9141 | 122.7951 | -0.37537
2648.6406 | 122.9828 | -122.7173 | 0.10986 | 0.4918 | 0.043416 | 0.014358 | 0.35861 | -0.064096 | -0.010199 | 0.043029 | 0.41841 | -0.01866 | -0.044143 | -0.058007 | 0.0024291 | 0.11098 | 0.068665 | 0.11902 | 0.022888 | 0.073242 | 0.21973 | -0.07782 | -0.23346 | 0.086975 | 0.091553 | 0.050354 | 0.18768 | 0.14648 | -0.1831 | -0.20142 | 122.6395 | 122.4838 | 0.10986 | 122.8363 | 122.7905 | 0.3067 | -0.041198 | 122.5342 | 122.5159 | 0.07782 | 122.8043 | 122.7676 | 0.25177 | 0.036621 | 122.937 | 122.7859 | 122.7402 | -0.34332 | 122.905 | 122.8638 | 122.8088 | -0.31128
2649.6406 | 123.0331 | -122.7081 | 0.11902 | 0.59861 | 0.049824 | -0.0016631 | 0.35541 | -0.060891 | -0.013404 | 0.050505 | 0.40315 | -0.011183 | -0.030257 | -0.06762 | 0.0067021 | 0.10457 | 0.082397 | 0.11902 | 0.013733 | 0.082397 | 0.2243 | -0.10529 | -0.22888 | 0.082397 | 0.10071 | 0.064087 | 0.17395 | 0.12817 | -0.19226 | -0.20142 | 122.6028 | 122.4792 | 0.10529 | 122.8271 | 122.7905 | 0.31128 | -0.036622 | 122.5159 | 122.5067 | 0.054931 | 122.7905 | 122.7722 | 0.2655 | 0.009155 | 122.9324 | 122.7905 | 122.7219 | -0.3479 | 122.8821 | 122.8363 | 122.8088 | -0.32044
2650.6562 | 122.9004 | -122.7402 | 0.17395 | -0.2864 | 0.033803 | 0.0068819 | 0.36716 | -0.054483 | -0.020881 | 0.047301 | -0.63445 | -0.0047754 | -0.029189 | -0.06762 | 0.0034971 | 0.1035 | -0.004578 | 0.018311 | -0.086975 | 0.022888 | 0.2655 | -0.12817 | -0.29755 | -0.022888 | -0.004578 | -0.054932 | 0.22888 | 0.16937 | -0.22888 | -0.23346 | 122.612 | 122.4426 | 0.091553 | 122.7585 | 122.7631 | 0.32043 | -0.17853 | 122.5113 | 122.5067 | 0.054932 | 122.7173 | 122.6852 | 0.17853 | -0.004577 | 123.0057 | 122.7356 | 122.6532 | -0.4715 | 122.9691 | 122.9095 | 122.7356 | -0.40741
2651.6406 | 123.0423 | -122.7081 | 0.14191 | 0.29344 | 0.054097 | 0.0068819 | 0.37143 | -0.070504 | -0.0037909 | 0.031279 | 0.29634 | 0.0027016 | -0.032393 | -0.070825 | 0.0077701 | 0.09923 | 0.10986 | 0.10071 | -0.018311 | 0.073242 | 0.22888 | -0.082397 | -0.24719 | 0.091553 | 0.10071 | 0.054932 | 0.1831 | 0.11902 | -0.1831 | -0.19684 | 122.6257 | 122.4609 | 0.086975 | 122.8088 | 122.7814 | 0.32043 | -0.032044 | 122.525 | 122.5113 | 0.041198 | 122.7997 | 122.7631 | 0.25177 | -0.022888 | 122.937 | 122.818 | 122.6898 | -0.3891 | 122.8912 | 122.8271 | 122.8088 | -0.33875
2652.6406 | 122.9462 | -122.7722 | 0.14648 | 0.56809 | 0.074391 | -0.010208 | 0.36609 | -0.064096 | 0.012231 | 0.04196 | 0.3116 | 0.0016336 | -0.043074 | -0.060143 | 0.026996 | 0.098162 | 0.032043 | -0.009155 | -0.10529 | 0.009155 | 0.28381 | -0.09613 | -0.28839 | 0.022888 | -0.018311 | -0.059509 | 0.21973 | 0.16479 | -0.21973 | -0.2243 | 122.6761 | 122.4838 | 0.13733 | 122.7631 | 122.7814 | 0.29755 | -0.11444 | 122.5525 | 122.5479 | 0.073243 | 122.7951 | 122.7127 | 0.16479 | 0.018311 | 123.056 | 122.8043 | 122.6669 | -0.43488 | 122.9919 | 122.937 | 122.7539 | -0.37079
2653.6562 | 123.0057 | -122.7402 | 0.13733 | -0.17959 | 0.054097 | -0.00059506 | 0.38211 | -0.061959 | -0.026221 | 0.04196 | -0.29875 | -0.01332 | -0.043074 | -0.083642 | 0.0056341 | 0.10564 | 0.064087 | 0.1236 | 0.027466 | 0.09613 | 0.24719 | -0.082397 | -0.24261 | 0.045776 | 0.12817 | 0.050354 | 0.18768 | 0.13733 | -0.20142 | -0.21973 | 122.6578 | 122.4976 | 0.10986 | 122.8638 | 122.8363 | 0.33874 | -0.073242 | 122.5388 | 122.5204 | 0.050354 | 122.7859 | 122.7905 | 0.27008 | 0 | 122.9874 | 122.8043 | 122.7676 | -0.37994 | 122.9279 | 122.8775 | 122.8683 | -0.35706
2654.6406 | 123.0194 | -122.7173 | 0.14191 | 0.56809 | 0.044484 | -0.0080721 | 0.36075 | -0.0673 | 0.0058221 | 0.037688 | 0.12849 | -0.0026384 | -0.037734 | -0.059075 | 0.015247 | 0.1035 | 0.064087 | 0.054932 | -0.036621 | 0.045776 | 0.24719 | -0.09613 | -0.24261 | 0.091553 | 0.027466 | 0.009155 | 0.19684 | 0.14191 | -0.19684 | -0.19684 | 122.6212 | 122.4747 | 0.10528 | 122.7722 | 122.7631 | 0.28839 | -0.07782 | 122.5204 | 122.5204 | 0.054931 | 122.8088 | 122.7264 | 0.20599 | 0 | 122.9645 | 122.7814 | 122.6807 | -0.38452 | 122.9141 | 122.8592 | 122.7448 | -0.33875
2655.6406 | 122.9874 | -122.7402 | 0.15564 | -0.24062 | 0.032734 | 0.0058129 | 0.34366 | -0.077981 | -0.019813 | 0.03662 | -0.42082 | -0.0090474 | -0.047347 | -0.072961 | 0.014179 | 0.10564 | 0.059509 | 0.11444 | 0.004578 | 0.091553 | 0.23804 | -0.09613 | -0.25635 | 0.022888 | 0.1236 | 0.045776 | 0.17853 | 0.14191 | -0.19226 | -0.23804 | 122.644 | 122.4838 | 0.082397 | 122.8546 | 122.8317 | 0.3479 | -0.096131 | 122.5479 | 122.5021 | 0.022888 | 122.7631 | 122.7859 | 0.28381 | -0.013733 | 122.9782 | 122.7997 | 122.7448 | -0.41199 | 122.9187 | 122.8821 | 122.8638 | -0.39368
2656.6406 | 122.9599 | -122.7402 | 0.15106 | 0.59861 | 0.066914 | -0.0070041 | 0.36075 | -0.075845 | 0.0079581 | 0.049437 | 0.20479 | 0.011247 | -0.016372 | -0.066552 | 0.010974 | 0.10457 | 0.018311 | 0.004578 | -0.10071 | 0.013733 | 0.28839 | -0.11902 | -0.28381 | 0.013733 | -0.022888 | -0.041199 | 0.2243 | 0.15564 | -0.21515 | -0.26093 | 122.6212 | 122.4564 | 0.13733 | 122.7448 | 122.7539 | 0.29755 | -0.13275 | 122.525 | 122.4792 | 0.073242 | 122.7539 | 122.699 | 0.21973 | 0.004578 | 123.0286 | 122.7585 | 122.6395 | -0.43488 | 122.9645 | 122.8958 | 122.7173 | -0.41199
2657.6406 | 122.9324 | -122.7539 | 0.16479 | 0.40025 | 0.097889 | 0.0026089 | 0.38532 | -0.064096 | 0.0036861 | 0.05371 | 0.26582 | 0.0016336 | -0.036666 | -0.058007 | 0.022724 | 0.11098 | -0.009155 | 0 | -0.11444 | 0.009155 | 0.2655 | -0.1236 | -0.27466 | -0.018311 | -0.027466 | -0.064087 | 0.21973 | 0.17395 | -0.21973 | -0.25635 | 122.6303 | 122.4792 | 0.10071 | 122.7539 | 122.7631 | 0.28381 | -0.17395 | 122.5342 | 122.4976 | 0.054932 | 122.7356 | 122.6898 | 0.19226 | 0.009155 | 123.0194 | 122.7448 | 122.6395 | -0.43945 | 122.9736 | 122.9279 | 122.7264 | -0.42114
2658.6406 | 122.9233 | -122.7905 | 0.16022 | 0.53758 | 0.081868 | 0.018631 | 0.36823 | -0.061959 | 0.0090271 | 0.056914 | 0.2353 | 0.0048376 | -0.021712 | -0.053735 | 0.018451 | 0.10884 | -0.032043 | -0.045776 | -0.13733 | -0.009155 | 0.28381 | -0.10529 | -0.28839 | -0.009155 | -0.041199 | -0.082397 | 0.21973 | 0.16022 | -0.21515 | -0.24261 | 122.6852 | 122.5021 | 0.1236 | 122.7448 | 122.7814 | 0.27924 | -0.19226 | 122.5754 | 122.5479 | 0.05951 | 122.7814 | 122.7081 | 0.16022 | 0 | 123.0743 | 122.7585 | 122.6532 | -0.44861 | 123.0103 | 122.9507 | 122.7493 | -0.40283
2659.6562 | 123.0515 | -122.7539 | 0.12817 | 0.079814 | 0.034871 | -0.0038001 | 0.37036 | -0.075845 | -0.03797 | 0.045165 | 0.15901 | -0.01332 | -0.02278 | -0.064416 | -0.0029109 | 0.1238 | 0.022888 | 0.09613 | 0.013733 | 0.082397 | 0.23346 | -0.10071 | -0.23346 | 0.054932 | 0.1236 | 0.07782 | 0.21057 | 0.13275 | -0.16937 | -0.21515 | 122.6532 | 122.5204 | 0.10528 | 122.85 | 122.8363 | 0.31586 | -0.10529 | 122.5845 | 122.5388 | 0.082397 | 122.8088 | 122.8317 | 0.29297 | 0.004577 | 122.9874 | 122.7768 | 122.7676 | -0.36163 | 122.9645 | 122.8867 | 122.8775 | -0.34332
2660.6406 | 123.0194 | -122.7493 | 0.13275 | 0.50706 | 0.047688 | 0.011154 | 0.37143 | -0.052346 | -0.017676 | 0.025939 | 0.43367 | -0.01332 | -0.024916 | -0.068688 | 0.010974 | 0.11205 | 0.059509 | 0.10986 | 0.027466 | 0.073242 | 0.23804 | -0.064087 | -0.21973 | 0.068665 | 0.09613 | 0.068665 | 0.17853 | 0.13733 | -0.18768 | -0.21973 | 122.6852 | 122.5296 | 0.10529 | 122.8592 | 122.8226 | 0.29297 | -0.073242 | 122.5616 | 122.5296 | 0.045777 | 122.818 | 122.818 | 0.28839 | 0.004578 | 122.9874 | 122.8088 | 122.7768 | -0.35248 | 122.9279 | 122.8867 | 122.8455 | -0.35248
2661.6406 | 122.9141 | -122.8088 | 0.16022 | 0.27818 | 0.065846 | -0.013413 | 0.36609 | -0.066232 | 0.016503 | 0.039824 | 0.25056 | 0.0091106 | -0.0024864 | -0.055871 | 0.022724 | 0.098162 | 0.013733 | -0.013733 | -0.11444 | 0.009155 | 0.27008 | -0.11444 | -0.26093 | -0.036621 | -0.064087 | -0.11444 | 0.2243 | 0.17395 | -0.23346 | -0.24719 | 122.6944 | 122.5479 | 0.10986 | 122.7951 | 122.818 | 0.27008 | -0.14648 | 122.5754 | 122.5616 | 0.064087 | 122.7722 | 122.6944 | 0.13275 | 0.013733 | 123.0789 | 122.8226 | 122.6944 | -0.42114 | 123.0331 | 122.9828 | 122.7448 | -0.40741
2662.6406 | 122.9279 | -122.818 | 0.16479 | 0.20188 | 0.065846 | -0.00059506 | 0.37143 | -0.063028 | 0.013299 | 0.03662 | 0.0064239 | -0.0015704 | -0.013167 | -0.071893 | 0.036609 | 0.098162 | 0.004578 | 0.032043 | -0.09613 | 0.032043 | 0.27466 | -0.086975 | -0.27924 | -0.013733 | 0 | -0.07782 | 0.21515 | 0.15106 | -0.21515 | -0.24261 | 122.731 | 122.5388 | 0.10986 | 122.85 | 122.85 | 0.31128 | -0.16022 | 122.6028 | 122.5754 | 0.050354 | 122.8043 | 122.7402 | 0.16479 | -0.013733 | 123.0927 | 122.8226 | 122.7219 | -0.44403 | 123.0331 | 122.9691 | 122.818 | -0.40741
2663.6406 | 122.9187 | -122.7951 | 0.16937 | 0.41551 | 0.075459 | 0.00047294 | 0.38318 | -0.064096 | 0.0058221 | 0.040892 | -0.024094 | 0.0059056 | -0.01744 | -0.04519 | 0.017383 | 0.1035 | -0.009155 | -0.004578 | -0.12817 | 0.009155 | 0.27466 | -0.10986 | -0.27008 | -0.054932 | -0.032043 | -0.10529 | 0.21515 | 0.17395 | -0.21973 | -0.25177 | 122.6852 | 122.525 | 0.10529 | 122.7905 | 122.8043 | 0.27924 | -0.17853 | 122.5754 | 122.5433 | 0.045776 | 122.7402 | 122.6898 | 0.14648 | 0.004577 | 123.0698 | 122.7859 | 122.6669 | -0.43945 | 123.0103 | 122.9691 | 122.7631 | -0.42114
2664.6406 | 122.9691 | -122.7859 | 0.13733 | 0.079814 | 0.074391 | -0.010208 | 0.36609 | -0.064096 | -0.0037909 | 0.051574 | -0.06987 | -0.0015704 | -0.023848 | -0.06228 | 0.018451 | 0.10564 | 0.027466 | 0.07782 | -0.073242 | 0.041199 | 0.27924 | -0.10529 | -0.2655 | 0.009155 | 0.036621 | -0.041199 | 0.21057 | 0.14648 | -0.21515 | -0.23346 | 122.6807 | 122.5204 | 0.14191 | 122.8638 | 122.8271 | 0.3067 | -0.10986 | 122.5708 | 122.5525 | 0.073242 | 122.7951 | 122.7448 | 0.19226 | 0.009155 | 123.0652 | 122.8134 | 122.7127 | -0.40283 | 122.9965 | 122.9324 | 122.8226 | -0.37079
2665.6406 | 122.9782 | -122.7951 | 0.16022 | -0.026997 | 0.06371 | -0.0016631 | 0.36609 | -0.066232 | 0.0058221 | 0.045165 | -0.0088351 | -0.0037074 | -0.029189 | -0.055871 | 0.0088381 | 0.10778 | 0.036621 | 0.064087 | -0.07782 | 0.045776 | 0.28381 | -0.10529 | -0.26093 | 0.009155 | 0.064087 | -0.036621 | 0.21057 | 0.16479 | -0.2243 | -0.23346 | 122.6898 | 122.5342 | 0.1236 | 122.8592 | 122.8409 | 0.3067 | -0.1236 | 122.5708 | 122.5616 | 0.050354 | 122.8043 | 122.7585 | 0.19684 | 0.004578 | 123.0789 | 122.8317 | 122.7173 | -0.42114 | 123.0057 | 122.9599 | 122.8592 | -0.39368
2666.6406 | 122.9828 | -122.7997 | 0.15564 | -0.11855 | 0.060505 | 0.0015409 | 0.38104 | -0.057687 | -0.0027229 | 0.052642 | -0.14616 | 0.0048376 | -0.016372 | -0.066552 | 0.017383 | 0.10137 | 0.022888 | 0.054932 | -0.073242 | 0.045776 | 0.27466 | -0.09613 | -0.28381 | 0.018311 | 0.059509 | -0.036621 | 0.21973 | 0.15564 | -0.2243 | -0.24719 | 122.7036 | 122.5159 | 0.11902 | 122.8546 | 122.8455 | 0.32959 | -0.13275 | 122.5754 | 122.5525 | 0.064087 | 122.818 | 122.7631 | 0.21057 | 0 | 123.0743 | 122.8226 | 122.7264 | -0.43945 | 123.0194 | 122.9553 | 122.8592 | -0.40283
2667.6406 | 122.9507 | -122.8088 | 0.16937 | 0.15611 | 0.073323 | -0.0038001 | 0.36823 | -0.071573 | 0.00048206 | 0.037688 | -0.0088351 | 0.0069746 | -0.028121 | -0.072961 | 0.020587 | 0.10137 | 0.022888 | 0.054932 | -0.082397 | 0.036621 | 0.27008 | -0.11444 | -0.2655 | -0.018311 | 0.018311 | -0.045776 | 0.23346 | 0.15564 | -0.21515 | -0.22888 | 122.6944 | 122.5433 | 0.10071 | 122.8638 | 122.8455 | 0.30212 | -0.14649 | 122.5937 | 122.58 | 0.064086 | 122.7905 | 122.7631 | 0.18311 | -0.013733 | 123.0789 | 122.8317 | 122.7264 | -0.43488 | 123.0423 | 122.9645 | 122.8271 | -0.39826
2668.6406 | 122.9874 | -122.8043 | 0.14648 | -0.10329 | 0.057301 | 0.0058129 | 0.37677 | -0.064096 | -0.0016549 | 0.039824 | 0.021682 | -0.0058434 | -0.024916 | -0.078301 | 0.0077701 | 0.10778 | 0.009155 | 0.054932 | -0.073242 | 0.050354 | 0.26093 | -0.10986 | -0.27924 | -0.009155 | 0.041199 | -0.032043 | 0.21515 | 0.15564 | -0.2243 | -0.23804 | 122.6944 | 122.525 | 0.11444 | 122.8592 | 122.8546 | 0.32959 | -0.13733 | 122.58 | 122.5662 | 0.068665 | 122.7951 | 122.7722 | 0.20599 | 0.009156 | 123.0652 | 122.8134 | 122.731 | -0.42572 | 123.0194 | 122.9599 | 122.8455 | -0.38452
2669.6406 | 122.9828 | -122.7814 | 0.16937 | -0.19484 | 0.057301 | 0.0058129 | 0.3725 | -0.071573 | -0.016608 | 0.047301 | -0.28349 | -0.0026384 | -0.018508 | -0.055871 | 0.015247 | 0.1035 | -0.027466 | 0.004578 | -0.10071 | 0.022888 | 0.27008 | -0.11902 | -0.28381 | -0.022888 | 0.041199 | -0.018311 | 0.2243 | 0.17395 | -0.22888 | -0.24261 | 122.6624 | 122.4976 | 0.10071 | 122.7859 | 122.8043 | 0.3067 | -0.19684 | 122.5525 | 122.5388 | 0.054931 | 122.7585 | 122.7631 | 0.2243 | 0.004577 | 123.0515 | 122.7539 | 122.6807 | -0.45319 | 123.0057 | 122.9553 | 122.8226 | -0.41199
2670.6406 | 122.9919 | -122.818 | 0.15106 | -0.026997 | 0.039143 | -0.016617 | 0.36075 | -0.070504 | -0.0059269 | 0.049437 | -0.14616 | -0.0026384 | -0.02278 | -0.066552 | 0.014179 | 0.10671 | 0.013733 | 0.082397 | -0.073242 | 0.050354 | 0.27008 | -0.10529 | -0.24261 | 0.004578 | 0.050354 | -0.041199 | 0.22888 | 0.16022 | -0.21973 | -0.23346 | 122.7127 | 122.5754 | 0.11902 | 122.9004 | 122.8683 | 0.29297 | -0.13733 | 122.5983 | 122.5845 | 0.07782 | 122.8226 | 122.7768 | 0.19226 | 0.009155 | 123.0881 | 122.8317 | 122.7448 | -0.39368 | 123.0469 | 122.9782 | 122.8683 | -0.38452
2671.6406 | 122.9691 | -122.8226 | 0.16937 | -0.27114 | 0.076527 | 0.020767 | 0.36609 | -0.053415 | -0.023017 | 0.039824 | -0.14616 | 0.0027016 | -0.028121 | -0.061212 | 0.0067021 | 0.10137 | -0.059509 | 0 | -0.09613 | 0.009155 | 0.28839 | -0.1236 | -0.28381 | -0.059509 | -0.004578 | -0.045776 | 0.24719 | 0.1831 | -0.24261 | -0.24719 | 122.699 | 122.5388 | 0.11902 | 122.8226 | 122.8317 | 0.29297 | -0.22888 | 122.58 | 122.5754 | 0.077819 | 122.7631 | 122.7768 | 0.20142 | 0.013732 | 123.111 | 122.7631 | 122.7264 | -0.45319 | 123.0698 | 123.0057 | 122.818 | -0.41656
2672.6406 | 123.0011 | -122.8088 | 0.16022 | -0.16433 | 0.026326 | 0.020767 | 0.38425 | -0.060891 | -0.029426 | 0.029143 | -0.17668 | -0.011183 | -0.035598 | -0.063348 | -0.013592 | 0.11952 | -0.004578 | 0.11902 | -0.013733 | 0.073242 | 0.25177 | -0.07782 | -0.23804 | -0.013733 | 0.091553 | 0.009155 | 0.19684 | 0.16937 | -0.21973 | -0.23346 | 122.731 | 122.5708 | 0.091553 | 122.9279 | 122.8821 | 0.31128 | -0.16479 | 122.5891 | 122.5754 | 0.036621 | 122.7951 | 122.818 | 0.24261 | 0.009156 | 123.0606 | 122.8043 | 122.7951 | -0.39825 | 123.0057 | 122.9782 | 122.9004 | -0.39368
2673.6406 | 122.9599 | -122.7905 | 0.15564 | -0.27114 | 0.019917 | 0.0068819 | 0.37143 | -0.055551 | -0.020881 | 0.020598 | -0.37505 | -0.010115 | -0.035598 | -0.066552 | 0.0024291 | 0.11418 | -0.013733 | 0.086975 | -0.041199 | 0.045776 | 0.2655 | -0.11444 | -0.2655 | -0.032043 | 0.027466 | -0.032043 | 0.22888 | 0.16022 | -0.21515 | -0.23804 | 122.6761 | 122.525 | 0.10986 | 122.8775 | 122.8363 | 0.31128 | -0.16937 | 122.5754 | 122.5525 | 0.073242 | 122.7585 | 122.7585 | 0.20599 | 0.004577 | 123.056 | 122.7768 | 122.7493 | -0.42114 | 123.0194 | 122.9507 | 122.818 | -0.39368
2674.6406 | 123.0698 | -122.7539 | 0.11444 | 0.59861 | 0.050892 | -0.012345 | 0.36075 | -0.064096 | -0.0048589 | 0.025939 | -0.13091 | -0.0079794 | -0.030257 | -0.063348 | 0.0099061 | 0.10137 | 0.032043 | 0.11444 | -0.018311 | 0.064087 | 0.24719 | -0.091553 | -0.22888 | 0.068665 | 0.07782 | 0.068665 | 0.19226 | 0.11902 | -0.20142 | -0.21057 | 122.6624 | 122.525 | 0.13275 | 122.8683 | 122.818 | 0.29297 | -0.082398 | 122.5525 | 122.5433 | 0.07782 | 122.8226 | 122.8226 | 0.27924 | 0.004578 | 123.0011 | 122.7859 | 122.7356 | -0.34332 | 122.9462 | 122.8729 | 122.8317 | -0.32501
2675.6406 | 122.9828 | -122.7997 | 0.16022 | -0.30166 | 0.017781 | 0.015426 | 0.38318 | -0.064096 | -0.023017 | 0.035552 | -0.31401 | -0.01332 | -0.038802 | -0.074029 | 0.0034971 | 0.10671 | 0.013733 | 0.10071 | -0.036621 | 0.064087 | 0.25177 | -0.086975 | -0.2655 | -0.045776 | 0.054932 | -0.022888 | 0.21515 | 0.16937 | -0.21515 | -0.24719 | 122.7127 | 122.5342 | 0.091553 | 122.9004 | 122.8638 | 0.32959 | -0.14648 | 122.5845 | 122.5525 | 0.054932 | 122.7539 | 122.7768 | 0.2243 | 0.009156 | 123.0515 | 122.8134 | 122.7631 | -0.42572 | 123.0148 | 122.9691 | 122.8546 | -0.40741
2676.6406 | 122.9599 | -122.8134 | 0.16479 | -0.24062 | 0.018849 | 0.0090179 | 0.3725 | -0.068368 | -0.010199 | 0.037688 | -0.35979 | -0.010115 | -0.024916 | -0.049462 | 0.0045661 | 0.096026 | -0.018311 | -0.009155 | -0.10986 | -0.004578 | 0.28839 | -0.11902 | -0.28381 | -0.041199 | -0.013733 | -0.068665 | 0.23804 | 0.16479 | -0.22888 | -0.24719 | 122.6944 | 122.5296 | 0.1236 | 122.8043 | 122.8088 | 0.27923 | -0.18311 | 122.5845 | 122.5662 | 0.073242 | 122.7722 | 122.7448 | 0.17853 | 0 | 123.1018 | 122.7951 | 122.7036 | -0.44861 | 123.0515 | 122.9782 | 122.7997 | -0.41199
2677.6406 | 122.9599 | -122.818 | 0.16937 | 0.018779 | 0.030598 | 0.014358 | 0.37143 | -0.061959 | -0.024085 | 0.037688 | -0.39031 | -0.0015704 | -0.03453 | -0.063348 | 0.010974 | 0.1003 | -0.013733 | -0.004578 | -0.10529 | 0 | 0.27008 | -0.1236 | -0.27466 | -0.050354 | -0.004578 | -0.059509 | 0.2243 | 0.1831 | -0.22888 | -0.25635 | 122.6944 | 122.5433 | 0.10071 | 122.8134 | 122.818 | 0.27466 | -0.18311 | 122.5891 | 122.5616 | 0.054931 | 122.7676 | 122.7585 | 0.19684 | 0.013732 | 123.0881 | 122.8043 | 122.7127 | -0.44403 | 123.0423 | 123.0011 | 122.8134 | -0.42572
2678.6406 | 122.9507 | -122.8043 | 0.14648 | -0.2864 | 0.038075 | 0.022903 | 0.36609 | -0.066232 | -0.019813 | 0.032347 | 0.067459 | -0.0026384 | -0.032393 | -0.058007 | 0.00029315 | 0.10884 | 0.004578 | 0.050354 | -0.064087 | 0.018311 | 0.26093 | -0.10071 | -0.25177 | -0.050354 | 0.10529 | -0.068665 | 0.2243 | 0.15564 | -0.21057 | -0.24261 | 122.7036 | 122.5525 | 0.11444 | 122.8546 | 122.8226 | 0.27008 | -0.14191 | 122.5937 | 122.5616 | 0.07782 | 122.7539 | 122.7356 | 0.17395 | 0.009156 | 123.0652 | 122.8088 | 122.7402 | -0.39825 | 123.0286 | 122.9599 | 122.9095 | -0.3891
2679.6406 | 123.0103 | -122.7951 | 0.16937 | -0.19484 | 0.048756 | 0.015426 | 0.35968 | -0.066232 | -0.024085 | 0.03662 | -0.29875 | -0.010115 | -0.030257 | -0.064416 | 0.0045661 | 0.09923 | 0.027466 | 0.1236 | -0.013733 | 0.068665 | 0.24261 | -0.09613 | -0.24261 | 0.004578 | 0.07782 | 0.004578 | 0.2243 | 0.15106 | -0.21515 | -0.23804 | 122.699 | 122.5525 | 0.073242 | 122.9187 | 122.8638 | 0.31128 | -0.14191 | 122.58 | 122.5571 | 0.054931 | 122.7997 | 122.7997 | 0.24261 | -0.018311 | 123.0377 | 122.8226 | 122.7814 | -0.41199 | 123.0194 | 122.9462 | 122.8729 | -0.40741
2680.6406 | 123.0835 | -122.8134 | 0.14191 | -0.011739 | 0.01244 | 0.0079499 | 0.36289 | -0.073709 | -0.034766 | 0.030211 | 0.0064239 | -0.014388 | -0.03987 | -0.063348 | -0.0039789 | 0.11312 | 0.018311 | 0.12817 | 0.018311 | 0.073242 | 0.24261 | -0.07782 | -0.24719 | 0.07782 | 0.10529 | 0.086975 | 0.20142 | 0.13275 | -0.18768 | -0.21515 | 122.7356 | 122.5662 | 0.10071 | 122.9416 | 122.8867 | 0.32043 | -0.1236 | 122.6257 | 122.5983 | 0.059509 | 122.8912 | 122.9004 | 0.30212 | -0.009156 | 123.056 | 122.8317 | 122.8317 | -0.3891 | 123.0148 | 122.9462 | 122.9187 | -0.35706
2681.6406 | 123.111 | -122.7722 | 0.12817 | 0.095073 | 0.0017592 | 0.0090179 | 0.3693 | -0.073709 | -0.029426 | 0.033416 | -0.48186 | -0.012251 | -0.03987 | -0.065484 | 0.0056341 | 0.11205 | 0.068665 | 0.14191 | 0.013733 | 0.068665 | 0.22888 | -0.064087 | -0.23346 | 0.086975 | 0.13733 | 0.10071 | 0.19684 | 0.13733 | -0.19226 | -0.21057 | 122.7081 | 122.5388 | 0.10071 | 122.9141 | 122.8409 | 0.30212 | -0.059509 | 122.58 | 122.5616 | 0.068664 | 122.8592 | 122.8729 | 0.31128 | 0.009155 | 123.0011 | 122.8409 | 122.7859 | -0.36163 | 122.9691 | 122.9095 | 122.9095 | -0.33875
2682.6406 | 123.0835 | -122.7814 | 0.13733 | 0.018779 | 0.032734 | 0.0079499 | 0.36289 | -0.060891 | -0.013404 | 0.023803 | 0.0522 | -0.0079794 | -0.043074 | -0.071893 | -0.0071839 | 0.10137 | 0.064087 | 0.11444 | 0.018311 | 0.064087 | 0.24719 | -0.086975 | -0.23804 | 0.073242 | 0.11902 | 0.07782 | 0.1831 | 0.13733 | -0.17853 | -0.21057 | 122.6944 | 122.5433 | 0.10986 | 122.8958 | 122.8455 | 0.30212 | -0.073242 | 122.6028 | 122.5708 | 0.045776 | 122.8546 | 122.8592 | 0.28839 | 0 | 123.0286 | 122.8455 | 122.7997 | -0.37537 | 122.9645 | 122.9187 | 122.9004 | -0.3479
2683.6406 | 123.0789 | -122.7814 | 0.1236 | -0.24062 | 0.04662 | 0.016495 | 0.35221 | -0.069436 | -0.028357 | 0.035552 | -0.22246 | -0.012251 | -0.042006 | -0.076165 | -0.00077485 | 0.10243 | 0.068665 | 0.14648 | 0.027466 | 0.086975 | 0.24719 | -0.073242 | -0.2243 | 0.073242 | 0.14191 | 0.050354 | 0.1831 | 0.11902 | -0.18768 | -0.20599 | 122.7081 | 122.5571 | 0.1236 | 122.9279 | 122.8683 | 0.31128 | -0.054931 | 122.5937 | 122.5754 | 0.059509 | 122.8546 | 122.8317 | 0.25635 | -0.004577 | 123.0286 | 122.85 | 122.8088 | -0.3479 | 122.9645 | 122.9004 | 122.9233 | -0.32959
2684.6406 | 123.0698 | -122.7676 | 0.1236 | 0.17137 | 0.035939 | 0.010086 | 0.36716 | -0.058755 | -0.017676 | 0.027007 | 0.082718 | -0.0079794 | -0.035598 | -0.06762 | 0.0045661 | 0.11098 | 0.027466 | 0.064087 | -0.018311 | 0.054932 | 0.2655 | -0.086975 | -0.23804 | 0.059509 | 0.064087 | 0.050354 | 0.19226 | 0.13733 | -0.17853 | -0.21057 | 122.6807 | 122.5296 | 0.14191 | 122.8317 | 122.8226 | 0.29297 | -0.09613 | 122.5891 | 122.5571 | 0.068665 | 122.8271 | 122.818 | 0.26093 | 0.013733 | 123.0331 | 122.7951 | 122.7493 | -0.36163 | 122.9599 | 122.905 | 122.8317 | -0.33417
2685.6406 | 123.0515 | -122.7951 | 0.13275 | 0.26292 | -0.0014448 | 0.012222 | 0.3725 | -0.072641 | -0.014472 | 0.038756 | 0.12849 | -0.01866 | -0.046279 | -0.066552 | 0.015247 | 0.11312 | 0.032043 | 0.082397 | -0.009155 | 0.050354 | 0.23804 | -0.07782 | -0.2655 | 0.032043 | 0.050354 | 0.045776 | 0.21057 | 0.14191 | -0.19684 | -0.21515 | 122.7173 | 122.5296 | 0.10529 | 122.8775 | 122.8455 | 0.31586 | -0.10071 | 122.5983 | 122.58 | 0.07782 | 122.8271 | 122.8409 | 0.26093 | 0.009156 | 123.0331 | 122.8271 | 122.7859 | -0.39825 | 123.0057 | 122.937 | 122.8455 | -0.3479
2686.7031 | 122.9599 | -122.8317 | 0.14648 | 0.18663 | 0.049824 | -0.0070041 | 0.36716 | -0.074777 | 0.014367 | 0.048369 | -0.024094 | 0.0059056 | -0.020644 | -0.059075 | 0.02486 | 0.081072 | 0.013733 | -0.036621 | -0.10529 | 0.004578 | 0.26093 | -0.11444 | -0.26093 | 0.004578 | -0.045776 | -0.091553 | 0.22888 | 0.14648 | -0.21515 | -0.2243 | 122.7173 | 122.5708 | 0.11444 | 122.7951 | 122.8363 | 0.2655 | -0.13275 | 122.6166 | 122.6074 | 0.082398 | 122.8363 | 122.7402 | 0.13275 | 0 | 123.0927 | 122.8455 | 122.7264 | -0.40741 | 123.0606 | 122.9782 | 122.7859 | -0.37079
2687.6406 | 123.0606 | -122.7905 | 0.14191 | 0.43077 | 0.026326 | 0.010086 | 0.36182 | -0.091867 | -0.027289 | 0.055846 | 0.17427 | -0.015456 | -0.047347 | -0.066552 | 0.0045661 | 0.11098 | 0.009155 | 0.082397 | 0 | 0.050354 | 0.24261 | -0.07782 | -0.25177 | 0.054932 | 0.068665 | 0.032043 | 0.20599 | 0.1236 | -0.18768 | -0.21057 | 122.7127 | 122.5388 | 0.10071 | 122.8729 | 122.8409 | 0.30212 | -0.13275 | 122.6028 | 122.58 | 0.064087 | 122.8455 | 122.8226 | 0.24261 | -0.018311 | 123.0331 | 122.7997 | 122.7905 | -0.39368 | 122.9965 | 122.9141 | 122.8592 | -0.35248
2688.6406 | 123.1293 | -122.7631 | 0.12817 | 0.00352 | -0.0035808 | 0.015426 | 0.36609 | -0.070504 | -0.030494 | 0.038756 | -0.039353 | -0.0026384 | -0.045211 | -0.059075 | 0.00029315 | 0.10778 | 0.054932 | 0.13733 | 0.018311 | 0.07782 | 0.25177 | -0.068665 | -0.21973 | 0.086975 | 0.10529 | 0.091553 | 0.19226 | 0.11902 | -0.1831 | -0.20599 | 122.6944 | 122.5433 | 0.1236 | 122.9004 | 122.8409 | 0.29755 | -0.073242 | 122.58 | 122.5571 | 0.064087 | 122.85 | 122.8546 | 0.29755 | -0.009155 | 123.0148 | 122.818 | 122.7814 | -0.3479 | 122.9553 | 122.8821 | 122.8683 | -0.33417
2689.6406 | 123.0652 | -122.7951 | 0.13275 | 0.14085 | 0.023121 | 0.0036769 | 0.37036 | -0.068368 | -0.028357 | 0.046233 | 0.15901 | -0.010115 | -0.065505 | -0.06228 | 0.0088381 | 0.11525 | 0.009155 | 0.045776 | -0.004578 | 0.059509 | 0.24261 | -0.07782 | -0.24261 | 0.041199 | 0.064087 | 0.041199 | 0.20142 | 0.1236 | -0.20599 | -0.19684 | 122.7173 | 122.5525 | 0.10986 | 122.8409 | 122.8546 | 0.30212 | -0.1236 | 122.5891 | 122.5983 | 0.068665 | 122.8363 | 122.8363 | 0.23804 | -0.009155 | 123.0377 | 122.8043 | 122.7905 | -0.37537 | 122.9965 | 122.9187 | 122.8592 | -0.32959
2690.6406 | 123.0652 | -122.7951 | 0.14191 | 0.24766 | 0.028462 | 0.014358 | 0.3693 | -0.0673 | -0.017676 | 0.035552 | 0.11323 | -0.015456 | -0.052687 | -0.063348 | 0.01311 | 0.09389 | 0.022888 | 0.068665 | -0.018311 | 0.050354 | 0.25177 | -0.086975 | -0.24719 | 0.041199 | 0.045776 | 0.032043 | 0.19684 | 0.14191 | -0.18768 | -0.21973 | 122.7081 | 122.5479 | 0.10986 | 122.8638 | 122.8455 | 0.29755 | -0.11902 | 122.6074 | 122.5754 | 0.054931 | 122.8363 | 122.8271 | 0.25177 | 0 | 123.0469 | 122.818 | 122.7768 | -0.3891 | 122.9919 | 122.937 | 122.8409 | -0.36163
2691.6406 | 123.0652 | -122.7997 | 0.13275 | 0.52232 | 0.017781 | 0.0090179 | 0.35755 | -0.08439 | -0.01554 | 0.031279 | 0.26582 | -0.01866 | -0.018508 | -0.061212 | 0.0077701 | 0.10564 | 0.068665 | 0.11444 | 0.009155 | 0.07782 | 0.22888 | -0.073242 | -0.23804 | 0.07782 | 0.050354 | 0.018311 | 0.19684 | 0.12817 | -0.19684 | -0.21973 | 122.7264 | 122.5616 | 0.096131 | 122.9141 | 122.8775 | 0.31586 | -0.064086 | 122.6028 | 122.58 | 0.064087 | 122.8775 | 122.818 | 0.23804 | -0.004577 | 123.0286 | 122.8683 | 122.8088 | -0.37079 | 122.9965 | 122.9279 | 122.85 | -0.35248
2692.6406 | 123.056 | -122.7859 | 0.12817 | 0.41551 | 0.039143 | 0.011154 | 0.35541 | -0.065164 | -0.0048589 | 0.043029 | 0.35738 | 0.0016336 | -0.045211 | -0.06228 | 0.018451 | 0.10884 | 0.086975 | 0.11444 | 0.032043 | 0.082397 | 0.23804 | -0.068665 | -0.25177 | 0.086975 | 0.073242 | 0.041199 | 0.1831 | 0.1236 | -0.16937 | -0.19684 | 122.7173 | 122.5342 | 0.10986 | 122.9004 | 122.8683 | 0.33417 | -0.041199 | 122.6166 | 122.5891 | 0.054931 | 122.8729 | 122.8271 | 0.23804 | -0.004578 | 123.024 | 122.8729 | 122.818 | -0.37994 | 122.9691 | 122.9095 | 122.8592 | -0.32501
2693.6406 | 123.0743 | -122.8088 | 0.12817 | 0.41551 | 0.023121 | 0.0079499 | 0.3693 | -0.070504 | -0.017676 | 0.039824 | 0.32686 | -0.0069114 | -0.037734 | -0.068688 | 0.016315 | 0.11312 | 0.045776 | 0.11444 | 0.018311 | 0.054932 | 0.24719 | -0.068665 | -0.22888 | 0.064087 | 0.064087 | 0.018311 | 0.18768 | 0.13275 | -0.1831 | -0.21973 | 122.7402 | 122.58 | 0.11902 | 122.9233 | 122.8638 | 0.28381 | -0.082398 | 122.6257 | 122.5891 | 0.059509 | 122.8729 | 122.8271 | 0.23804 | 0.004577 | 123.056 | 122.8546 | 122.8271 | -0.35706 | 122.9965 | 122.9416 | 122.8729 | -0.3479
2694.6406 | 123.0972 | -122.7905 | 0.13275 | 0.59861 | 0.038075 | -0.00059506 | 0.37464 | -0.057687 | 0.0068901 | 0.045165 | 0.32686 | -0.0047754 | -0.032393 | -0.064416 | 0.026996 | 0.098162 | 0.07782 | 0.15106 | 0.027466 | 0.07782 | 0.23346 | -0.059509 | -0.22888 | 0.11902 | 0.10529 | 0.054932 | 0.19226 | 0.10986 | -0.16937 | -0.20599 | 122.731 | 122.5616 | 0.10071 | 122.9416 | 122.8683 | 0.3067 | -0.054931 | 122.6212 | 122.5845 | 0.05951 | 122.9095 | 122.8455 | 0.26093 | -0.022888 | 123.024 | 122.8683 | 122.818 | -0.36163 | 122.9828 | 122.9004 | 122.8958 | -0.33875
2695.6406 | 123.0515 | -122.818 | 0.14191 | 0.47654 | 0.037007 | -0.012345 | 0.35755 | -0.065164 | -0.0091309 | 0.038756 | 0.38789 | -0.0015704 | -0.032393 | -0.074029 | 0.0099061 | 0.1003 | 0.027466 | 0.09613 | 0 | 0.036621 | 0.25177 | -0.07782 | -0.22888 | 0.068665 | 0.050354 | 0.013733 | 0.19684 | 0.14191 | -0.1831 | -0.21515 | 122.7402 | 122.5891 | 0.10986 | 122.9141 | 122.8546 | 0.2655 | -0.11444 | 122.6349 | 122.6028 | 0.054931 | 122.8867 | 122.8317 | 0.22888 | 0 | 123.0698 | 122.8455 | 122.818 | -0.37079 | 123.0148 | 122.9599 | 122.8683 | -0.35706
2696.6406 | 123.1018 | -122.7905 | 0.13275 | 0.53758 | 0.045552 | 0.0047449 | 0.35648 | -0.063028 | 0.0047541 | 0.04196 | 0.37263 | -0.0047754 | -0.040938 | -0.051599 | 0.028064 | 0.097094 | 0.09613 | 0.1236 | 0.036621 | 0.073242 | 0.23804 | -0.082397 | -0.23804 | 0.11902 | 0.082397 | 0.059509 | 0.19226 | 0.1236 | -0.1831 | -0.20142 | 122.7081 | 122.5525 | 0.10529 | 122.9141 | 122.8638 | 0.31128 | -0.036621 | 122.6074 | 122.5891 | 0.05951 | 122.9095 | 122.85 | 0.26093 | -0.009155 | 123.0286 | 122.8867 | 122.8271 | -0.37079 | 122.9828 | 122.9141 | 122.8729 | -0.33417
2697.6406 | 123.0789 | -122.8134 | 0.14648 | 0.50706 | 0.049824 | 0.0090179 | 0.35968 | -0.057687 | -0.012336 | 0.045165 | 0.38789 | -0.0037074 | -0.023848 | -0.058007 | 0.0088381 | 0.10991 | 0.073242 | 0.10071 | 0.027466 | 0.086975 | 0.23804 | -0.073242 | -0.22888 | 0.091553 | 0.091553 | 0.045776 | 0.20599 | 0.12817 | -0.18768 | -0.21057 | 122.7402 | 122.5845 | 0.091553 | 122.9141 | 122.9004 | 0.31586 | -0.073242 | 122.6257 | 122.6028 | 0.05951 | 122.905 | 122.8592 | 0.25635 | -0.01831 | 123.0515 | 122.8867 | 122.8409 | -0.37537 | 123.0194 | 122.9416 | 122.905 | -0.35706
2698.6406 | 123.0972 | -122.8088 | 0.12817 | 0.4918 | 0.058369 | 0.00047294 | 0.37036 | -0.048074 | -0.0037909 | 0.035552 | 0.38789 | 0.0037696 | -0.028121 | -0.058007 | 0.019519 | 0.10884 | 0.091553 | 0.10986 | 0.018311 | 0.073242 | 0.22888 | -0.068665 | -0.2243 | 0.11444 | 0.082397 | 0.054932 | 0.19684 | 0.10986 | -0.19684 | -0.20599 | 122.7402 | 122.5845 | 0.10071 | 122.9187 | 122.8821 | 0.29755 | -0.036621 | 122.612 | 122.6028 | 0.068664 | 122.9233 | 122.8638 | 0.26093 | -0.018311 | 123.0377 | 122.9004 | 122.8271 | -0.35248 | 123.0057 | 122.9187 | 122.8912 | -0.33417
2699.6406 | 123.1293 | -122.8088 | 0.13275 | 0.62913 | 0.066914 | -0.0080721 | 0.35861 | -0.066232 | 0.0058221 | 0.035552 | 0.34212 | 0.00056556 | -0.03987 | -0.06228 | 0.020587 | 0.098162 | 0.091553 | 0.10529 | -0.004578 | 0.07782 | 0.22888 | -0.068665 | -0.22888 | 0.10529 | 0.10529 | 0.041199 | 0.16937 | 0.11902 | -0.1831 | -0.1831 | 122.7402 | 122.58 | 0.096131 | 122.9141 | 122.8867 | 0.3067 | -0.041198 | 122.6257 | 122.6257 | 0.036622 | 122.9141 | 122.85 | 0.2243 | -0.013732 | 123.0377 | 122.9004 | 122.8043 | -0.36163 | 122.9782 | 122.9279 | 122.9141 | -0.31586
2700.6406 | 123.1018 | -122.8088 | 0.11902 | 0.56809 | 0.043416 | -0.0038001 | 0.3757 | -0.068368 | 0.0079581 | 0.052642 | 0.082718 | -0.0047754 | -0.038802 | -0.06228 | 0.022724 | 0.1035 | 0.064087 | 0.054932 | -0.018311 | 0.068665 | 0.25177 | -0.091553 | -0.24719 | 0.10986 | 0.082397 | 0.041199 | 0.20599 | 0.13275 | -0.17853 | -0.20142 | 122.7173 | 122.5616 | 0.13275 | 122.8638 | 122.8775 | 0.31586 | -0.054932 | 122.6303 | 122.6074 | 0.086975 | 122.9187 | 122.85 | 0.24262 | 0.013732 | 123.0606 | 122.8729 | 122.7905 | -0.36621 | 123.0148 | 122.9416 | 122.8912 | -0.32044
2701.6406 | 123.0881 | -122.8088 | 0.14191 | 0.58335 | 0.0808 | 0.00047294 | 0.36182 | -0.071573 | 0.010095 | 0.046233 | 0.3116 | 0.0080426 | -0.027053 | -0.063348 | 0.010974 | 0.10243 | 0.036621 | 0.041199 | -0.054932 | 0.036621 | 0.25635 | -0.086975 | -0.24261 | 0.073242 | 0.068665 | 0.018311 | 0.17853 | 0.14191 | -0.18768 | -0.21973 | 122.7219 | 122.5662 | 0.11444 | 122.85 | 122.8455 | 0.27924 | -0.10529 | 122.6212 | 122.5891 | 0.036621 | 122.8821 | 122.8271 | 0.23804 | 0 | 123.0652 | 122.8455 | 122.7539 | -0.38452 | 122.9874 | 122.9507 | 122.8775 | -0.36163
2702.6875 | 123.0286 | -122.8546 | 0.16479 | -0.27114 | 0.04662 | 0.021835 | 0.35968 | -0.061959 | -0.019813 | 0.043029 | -0.32927 | 0.0091106 | -0.024916 | -0.066552 | 0.0034971 | 0.10243 | 0.032043 | 0.086975 | -0.018311 | 0.050354 | 0.2655 | -0.09613 | -0.25635 | 0.018311 | 0.068665 | -0.013733 | 0.21973 | 0.16022 | -0.19684 | -0.23804 | 122.7585 | 122.5983 | 0.10071 | 122.9416 | 122.905 | 0.3067 | -0.13275 | 122.6578 | 122.6166 | 0.054932 | 122.8729 | 122.8409 | 0.2243 | -0.004578 | 123.1201 | 122.8867 | 122.8363 | -0.42114 | 123.0743 | 123.0148 | 122.9233 | -0.40283
2703.6406 | 123.111 | -122.8271 | 0.14191 | 0.50706 | 0.049824 | 0.0047449 | 0.36502 | -0.064096 | 0.0026181 | 0.047301 | 0.2353 | -0.0058434 | -0.047347 | -0.053735 | 0.021655 | 0.10564 | 0.073242 | 0.064087 | -0.027466 | 0.050354 | 0.27008 | -0.073242 | -0.23346 | 0.073242 | 0.1236 | 0.041199 | 0.17853 | 0.12817 | -0.17395 | -0.21057 | 122.7539 | 122.5937 | 0.12817 | 122.8912 | 122.8775 | 0.28381 | -0.068665 | 122.6532 | 122.6166 | 0.036621 | 122.9004 | 122.8683 | 0.25177 | -0.013733 | 123.0972 | 122.9004 | 122.7997 | -0.37537 | 123.0057 | 122.9553 | 122.9507 | -0.35248
2704.7031 | 123.0606 | -122.8363 | 0.16479 | 0.049296 | 0.051961 | -0.0016631 | 0.3725 | -0.065164 | 0.020776 | 0.039824 | -0.23772 | 0.0059056 | -0.011031 | -0.06228 | 0.017383 | 0.09923 | 0.064087 | 0.054932 | -0.059509 | 0.045776 | 0.28381 | -0.086975 | -0.26093 | 0.032043 | 0.050354 | -0.032043 | 0.23346 | 0.16937 | -0.20142 | -0.23804 | 122.7493 | 122.5754 | 0.11902 | 122.8912 | 122.8821 | 0.3067 | -0.10071 | 122.6349 | 122.5983 | 0.068664 | 122.8683 | 122.8043 | 0.20599 | 0.004578 | 123.1201 | 122.9004 | 122.7768 | -0.42572 | 123.0698 | 123.0057 | 122.8867 | -0.40283
2705.6406 | 123.0972 | -122.818 | 0.12817 | 0.56809 | 0.072255 | -0.0016631 | 0.36182 | -0.070504 | -0.0059269 | 0.04196 | 0.40315 | -0.0047754 | -0.024916 | -0.065484 | 0.014179 | 0.11632 | 0.082397 | 0.091553 | -0.004578 | 0.054932 | 0.23804 | -0.082397 | -0.24719 | 0.091553 | 0.10529 | 0.064087 | 0.16022 | 0.1236 | -0.18768 | -0.19684 | 122.7356 | 122.5708 | 0.10986 | 122.9095 | 122.8729 | 0.30212 | -0.045777 | 122.6303 | 122.6212 | 0.032043 | 122.9095 | 122.8821 | 0.26093 | -0.004578 | 123.056 | 122.9004 | 122.8134 | -0.37537 | 122.9782 | 122.9416 | 122.9233 | -0.32501
2706.6406 | 123.111 | -122.818 | 0.13275 | 0.46128 | 0.057301 | -0.0048681 | 0.3693 | -0.056619 | -0.0037909 | 0.03662 | 0.34212 | 0.00056556 | -0.03453 | -0.069756 | 0.021655 | 0.10991 | 0.045776 | 0.050354 | -0.032043 | 0.036621 | 0.26093 | -0.07782 | -0.24261 | 0.082397 | 0.091553 | 0.045776 | 0.20599 | 0.11902 | -0.17395 | -0.20599 | 122.7402 | 122.5754 | 0.12817 | 122.8683 | 122.8546 | 0.27924 | -0.086975 | 122.644 | 122.612 | 0.073243 | 122.9004 | 122.8638 | 0.25177 | -0.013732 | 123.0789 | 122.8638 | 122.7859 | -0.37537 | 123.024 | 122.937 | 122.9095 | -0.33875
2707.6406 | 123.0103 | -122.8592 | 0.15564 | 0.58335 | 0.06371 | 0.0036769 | 0.37464 | -0.057687 | -0.0027229 | 0.045165 | 0.25056 | -0.0015704 | -0.024916 | -0.061212 | 0.020587 | 0.10564 | 0.004578 | -0.032043 | -0.10529 | 0.004578 | 0.28381 | -0.11444 | -0.2655 | -0.013733 | -0.009155 | -0.064087 | 0.21973 | 0.16937 | -0.2243 | -0.22888 | 122.7448 | 122.5937 | 0.12817 | 122.8271 | 122.8638 | 0.27008 | -0.15106 | 122.6349 | 122.6303 | 0.064087 | 122.8455 | 122.7951 | 0.16479 | 0.013733 | 123.143 | 122.8638 | 122.7539 | -0.42114 | 123.0789 | 123.0286 | 122.85 | -0.38452
2708.6406 | 123.0194 | -122.8592 | 0.14648 | 0.40025 | 0.071187 | 0.0047449 | 0.37036 | -0.0673 | 0.012231 | 0.038756 | 0.2353 | 0.011247 | -0.021712 | -0.066552 | 0.02486 | 0.094958 | 0 | -0.032043 | -0.10071 | 0.009155 | 0.29755 | -0.11444 | -0.2655 | -0.022888 | -0.022888 | -0.07782 | 0.23346 | 0.16479 | -0.21973 | -0.24261 | 122.7448 | 122.5937 | 0.15106 | 122.8271 | 122.8683 | 0.27466 | -0.14648 | 122.6395 | 122.6166 | 0.086975 | 122.8363 | 122.7814 | 0.16479 | 0.018311 | 123.1567 | 122.8592 | 122.7585 | -0.41199 | 123.0927 | 123.024 | 122.8363 | -0.3891
2709.6406 | 123.0377 | -122.8683 | 0.15564 | 0.52232 | 0.085072 | 0.00047294 | 0.38104 | -0.068368 | 0.0036861 | 0.049437 | 0.29634 | 0.0037696 | -0.02278 | -0.068688 | 0.022724 | 0.10991 | -0.022888 | -0.022888 | -0.09613 | 0 | 0.27466 | -0.10071 | -0.2655 | -0.004578 | -0.018311 | -0.050354 | 0.21515 | 0.15564 | -0.2243 | -0.24261 | 122.7676 | 122.6028 | 0.11902 | 122.8455 | 122.8683 | 0.2655 | -0.17853 | 122.644 | 122.6257 | 0.059509 | 122.8638 | 122.818 | 0.19226 | 0 | 123.143 | 122.8455 | 122.7722 | -0.42114 | 123.0835 | 123.024 | 122.85 | -0.39826
2710.6406 | 123.0194 | -122.8821 | 0.16022 | 0.4918 | 0.070118 | 0.00047294 | 0.3693 | -0.063028 | 0.00048206 | 0.047301 | 0.3116 | 0.0080426 | -0.019576 | -0.054803 | 0.016315 | 0.10991 | -0.004578 | -0.022888 | -0.11444 | 0.027466 | 0.27466 | -0.091553 | -0.26093 | -0.013733 | -0.022888 | -0.054932 | 0.22888 | 0.16022 | -0.21515 | -0.23804 | 122.7905 | 122.6212 | 0.11444 | 122.8592 | 122.9095 | 0.28839 | -0.16479 | 122.6669 | 122.644 | 0.068665 | 122.8683 | 122.8271 | 0.1831 | 0 | 123.1567 | 122.8775 | 122.7676 | -0.42114 | 123.111 | 123.0423 | 122.8592 | -0.39825
2711.6406 | 123.0103 | -122.8729 | 0.16022 | 0.36973 | 0.076527 | -0.0038001 | 0.37464 | -0.063028 | -0.0069949 | 0.035552 | 0.29634 | 0.0091106 | -0.01744 | -0.063348 | 0.017383 | 0.11525 | -0.032043 | -0.041199 | -0.12817 | 0.004578 | 0.27924 | -0.11902 | -0.25635 | -0.022888 | -0.036621 | -0.068665 | 0.2243 | 0.16937 | -0.21057 | -0.24261 | 122.7539 | 122.6166 | 0.11902 | 122.8317 | 122.8775 | 0.26093 | -0.19226 | 122.6624 | 122.6303 | 0.064087 | 122.85 | 122.8043 | 0.17395 | 0.009156 | 123.1522 | 122.8409 | 122.7448 | -0.41657 | 123.0972 | 123.0423 | 122.8363 | -0.40283
2712.6406 | 123.0927 | -122.8592 | 0.13275 | 0.47654 | 0.070118 | -0.0016631 | 0.36395 | -0.058755 | -0.0059269 | 0.037688 | 0.46419 | -0.00050244 | -0.020644 | -0.066552 | 0.012042 | 0.11098 | 0.013733 | 0.004578 | -0.068665 | 0.013733 | 0.26093 | -0.10071 | -0.2655 | 0.018311 | 0.041199 | -0.018311 | 0.21515 | 0.15106 | -0.21057 | -0.21057 | 122.7585 | 122.5937 | 0.12817 | 122.8638 | 122.8729 | 0.27924 | -0.11902 | 122.6486 | 122.6486 | 0.082398 | 122.8775 | 122.8409 | 0.19226 | 0.018311 | 123.1201 | 122.8729 | 122.7905 | -0.39825 | 123.0743 | 123.0103 | 122.9004 | -0.34332
2713.6406 | 123.024 | -122.8729 | 0.16937 | 0.43077 | 0.064778 | 0.00047294 | 0.35755 | -0.070504 | 0.00048206 | 0.044097 | 0.32686 | 0.0069746 | -0.038802 | -0.068688 | 0.016315 | 0.11098 | -0.032043 | -0.022888 | -0.10071 | 0.004578 | 0.28381 | -0.10986 | -0.27466 | -0.050354 | -0.027466 | -0.064087 | 0.21973 | 0.16937 | -0.2243 | -0.25177 | 122.7631 | 122.5983 | 0.11444 | 122.85 | 122.8775 | 0.27924 | -0.20142 | 122.6486 | 122.6212 | 0.050354 | 122.8226 | 122.8088 | 0.18768 | 0 | 123.1567 | 122.8409 | 122.7722 | -0.44403 | 123.0927 | 123.0423 | 122.8455 | -0.42114
2714.6406 | 123.0286 | -122.8729 | 0.16022 | 0.50706 | 0.067982 | -0.012345 | 0.3757 | -0.069436 | -0.0069949 | 0.034484 | 0.37263 | 0.00056556 | -0.035598 | -0.061212 | 0.018451 | 0.10778 | -0.022888 | -0.009155 | -0.086975 | 0.004578 | 0.27466 | -0.10071 | -0.27924 | -0.018311 | -0.022888 | -0.036621 | 0.21515 | 0.16479 | -0.21057 | -0.23804 | 122.7722 | 122.5937 | 0.11444 | 122.8638 | 122.8775 | 0.28381 | -0.1831 | 122.6624 | 122.6349 | 0.054932 | 122.8546 | 122.8363 | 0.20142 | 0.004578 | 123.1476 | 122.85 | 122.7859 | -0.43945 | 123.0881 | 123.0377 | 122.85 | -0.39825
2715.6406 | 123.0331 | -122.8867 | 0.14648 | 0.15611 | 0.062642 | 0.0026089 | 0.35861 | -0.060891 | -0.0027229 | 0.04196 | 0.036941 | 0.0069746 | -0.038802 | -0.059075 | 0.012042 | 0.10457 | 0.018311 | 0.059509 | -0.059509 | 0.050354 | 0.27008 | -0.11444 | -0.26093 | -0.004578 | 0.009155 | -0.050354 | 0.21973 | 0.15564 | -0.21515 | -0.24719 | 122.7722 | 122.6257 | 0.1236 | 122.9462 | 122.937 | 0.31128 | -0.12817 | 122.6715 | 122.6395 | 0.073243 | 122.8821 | 122.8363 | 0.19684 | 0.009156 | 123.1567 | 122.905 | 122.8271 | -0.40741 | 123.1064 | 123.0423 | 122.8958 | -0.39368
2716.6562 | 123.1384 | -122.8638 | 0.13275 | 0.26292 | 0.044484 | 0.01329 | 0.37357 | -0.076913 | -0.048652 | 0.037688 | 0.34212 | -0.011183 | -0.033461 | -0.085778 | -0.0071839 | 0.12273 | -0.041199 | 0.054932 | 0.009155 | 0.059509 | 0.25635 | -0.091553 | -0.25635 | 0.027466 | 0.086975 | 0.07782 | 0.21057 | 0.15564 | -0.17395 | -0.20599 | 122.7722 | 122.6074 | 0.1236 | 122.9187 | 122.9233 | 0.31586 | -0.17395 | 122.6898 | 122.6578 | 0.07782 | 122.8912 | 122.9416 | 0.28381 | 0.022889 | 123.1201 | 122.8226 | 122.8729 | -0.3891 | 123.0743 | 123.0194 | 122.9507 | -0.33875
2717.6406 | 123.0423 | -122.8821 | 0.15564 | 0.18663 | 0.061574 | 0.012222 | 0.37464 | -0.059823 | 0.0047541 | 0.048369 | 0.021682 | 0.00056556 | -0.02278 | -0.068688 | 0.02486 | 0.1003 | 0.059509 | 0.041199 | -0.073242 | 0.050354 | 0.27008 | -0.11444 | -0.25177 | -0.013733 | 0.004578 | -0.07782 | 0.22888 | 0.16479 | -0.2243 | -0.23804 | 122.7676 | 122.6303 | 0.11444 | 122.9233 | 122.9324 | 0.30212 | -0.096131 | 122.6578 | 122.644 | 0.073242 | 122.8683 | 122.8043 | 0.16022 | 0.009155 | 123.1522 | 122.9416 | 122.8088 | -0.40741 | 123.111 | 123.0469 | 122.8867 | -0.39368
2718.6406 | 123.0148 | -122.9004 | 0.16022 | 0.11033 | 0.056233 | -0.012345 | 0.35861 | -0.071573 | 0.0058221 | 0.044097 | 0.18953 | -0.00050244 | -0.029189 | -0.069756 | 0.015247 | 0.10778 | -0.036621 | -0.036621 | -0.12817 | 0.004578 | 0.27466 | -0.11444 | -0.2655 | -0.027466 | -0.022888 | -0.082397 | 0.23346 | 0.16479 | -0.21973 | -0.23346 | 122.7859 | 122.6349 | 0.11444 | 122.8638 | 122.905 | 0.27008 | -0.19684 | 122.6807 | 122.6669 | 0.073242 | 122.8729 | 122.818 | 0.15106 | 0.004578 | 123.175 | 122.8638 | 122.7722 | -0.42572 | 123.1338 | 123.0652 | 122.8775 | -0.39368
2719.6406 | 123.056 | -122.8592 | 0.14648 | 0.14085 | 0.079732 | 0.0047449 | 0.38745 | -0.052346 | 0.0015501 | 0.045165 | -0.11565 | 0.0048376 | -0.025985 | -0.06228 | 0.019519 | 0.10671 | 0.054932 | 0.050354 | -0.064087 | 0.059509 | 0.25635 | -0.10071 | -0.24719 | 0.013733 | 0.059509 | -0.032043 | 0.2243 | 0.16022 | -0.21973 | -0.23804 | 122.7585 | 122.612 | 0.10986 | 122.9095 | 122.9187 | 0.3067 | -0.091552 | 122.6395 | 122.6212 | 0.07782 | 122.8729 | 122.8271 | 0.20599 | 0.013733 | 123.1155 | 122.9141 | 122.7951 | -0.39368 | 123.0835 | 123.0194 | 122.9187 | -0.38452
2720.6406 | 123.0652 | -122.8912 | 0.16479 | -0.2101 | 0.050892 | 0.0036769 | 0.36823 | -0.072641 | -0.013404 | 0.044097 | -0.29875 | 0.0016336 | -0.042006 | -0.068688 | 0.010974 | 0.10884 | -0.009155 | -0.004578 | -0.091553 | 0.027466 | 0.2655 | -0.11444 | -0.27924 | -0.013733 | 0.054932 | -0.022888 | 0.21973 | 0.15564 | -0.21057 | -0.24719 | 122.7768 | 122.612 | 0.10071 | 122.8867 | 122.9187 | 0.3067 | -0.17395 | 122.6807 | 122.644 | 0.054932 | 122.8775 | 122.8683 | 0.2243 | -0.009155 | 123.1567 | 122.8821 | 122.7997 | -0.44403 | 123.111 | 123.0469 | 122.9462 | -0.41199
2721.6406 | 123.0377 | -122.9095 | 0.17395 | 0.21714 | 0.0808 | 0.0079499 | 0.3693 | -0.0673 | 0.0015501 | 0.045165 | 0.12849 | 0.0016336 | -0.023848 | -0.056939 | 0.0088381 | 0.1003 | 0.027466 | 0.013733 | -0.091553 | 0.022888 | 0.26093 | -0.10986 | -0.27466 | -0.036621 | 0.004578 | -0.068665 | 0.20599 | 0.15564 | -0.21973 | -0.23804 | 122.7997 | 122.6349 | 0.086975 | 122.9233 | 122.9324 | 0.29755 | -0.14648 | 122.6898 | 122.6715 | 0.032044 | 122.8729 | 122.8409 | 0.16937 | -0.01831 | 123.1705 | 122.937 | 122.818 | -0.44861 | 123.1155 | 123.0652 | 122.9141 | -0.41199
2722.6406 | 123.0743 | -122.8729 | 0.14648 | 0.034038 | 0.066914 | 0.014358 | 0.37891 | -0.070504 | 0.00048206 | 0.03662 | -0.17668 | 0.0091106 | -0.015303 | -0.064416 | 0.017383 | 0.098162 | 0.018311 | 0.045776 | -0.054932 | 0.059509 | 0.2655 | -0.11444 | -0.27466 | 0.013733 | 0.050354 | -0.036621 | 0.21057 | 0.17395 | -0.21057 | -0.21973 | 122.7585 | 122.5983 | 0.11902 | 122.9187 | 122.9324 | 0.33417 | -0.12817 | 122.6624 | 122.6532 | 0.064087 | 122.8867 | 122.8363 | 0.18311 | 0.027466 | 123.1384 | 122.8912 | 122.818 | -0.42114 | 123.0835 | 123.0469 | 122.9233 | -0.36621
2723.6406 | 123.0515 | -122.8592 | 0.15564 | 0.12559 | 0.06371 | -0.0048681 | 0.35968 | -0.064096 | 0.0026181 | 0.039824 | 0.0064239 | 0.0016336 | -0.027053 | -0.066552 | 0.015247 | 0.11312 | 0.036621 | 0.036621 | -0.068665 | 0.041199 | 0.25635 | -0.09613 | -0.25177 | 0.004578 | 0.036621 | -0.045776 | 0.21515 | 0.16022 | -0.21057 | -0.22888 | 122.7631 | 122.6074 | 0.10071 | 122.8958 | 122.9004 | 0.29297 | -0.11902 | 122.6486 | 122.6303 | 0.059509 | 122.8638 | 122.8134 | 0.18311 | 0.004577 | 123.1155 | 122.8958 | 122.7905 | -0.40741 | 123.0743 | 123.0194 | 122.8958 | -0.38452
2724.6406 | 123.0927 | -122.905 | 0.16022 | -0.17959 | 0.06905 | 0.0026089 | 0.36609 | -0.08439 | -0.00058594 | 0.051574 | -0.16142 | -0.0079794 | -0.028121 | -0.076165 | 0.010974 | 0.11312 | 0.022888 | 0.041199 | -0.054932 | 0.050354 | 0.29297 | -0.10529 | -0.25635 | -0.009155 | 0.032043 | -0.022888 | 0.21973 | 0.15564 | -0.19684 | -0.2243 | 122.7997 | 122.6486 | 0.13275 | 122.9462 | 122.9553 | 0.3067 | -0.13733 | 122.7081 | 122.6807 | 0.05951 | 122.8958 | 122.8821 | 0.20142 | -0.004577 | 123.1979 | 122.9279 | 122.85 | -0.41657 | 123.1247 | 123.0606 | 122.937 | -0.38452
2725.6406 | 123.0743 | -122.8912 | 0.16937 | -0.22536 | 0.050892 | -0.0038001 | 0.36182 | -0.077981 | -0.0091309 | 0.037688 | -0.25298 | -0.0015704 | -0.033461 | -0.06228 | 0.010974 | 0.11418 | -0.027466 | 0.022888 | -0.086975 | 0.018311 | 0.27466 | -0.12817 | -0.28381 | -0.036621 | 0.050354 | -0.018311 | 0.21057 | 0.16937 | -0.22888 | -0.24719 | 122.7631 | 122.6074 | 0.10529 | 122.9141 | 122.9095 | 0.30212 | -0.19684 | 122.6624 | 122.644 | 0.041198 | 122.8546 | 122.8729 | 0.22888 | 0 | 123.1659 | 122.8638 | 122.8043 | -0.45319 | 123.1018 | 123.0606 | 122.9416 | -0.41656
2726.6406 | 123.0652 | -122.8821 | 0.17395 | -0.14907 | 0.050892 | 0.0015409 | 0.36395 | -0.063028 | -0.0091309 | 0.029143 | -0.29875 | -0.0090474 | -0.03987 | -0.059075 | 0.015247 | 0.10243 | -0.027466 | 0.009155 | -0.082397 | 0.032043 | 0.27008 | -0.1236 | -0.27466 | -0.054932 | 0.022888 | -0.050354 | 0.23804 | 0.15564 | -0.21973 | -0.23346 | 122.7585 | 122.6074 | 0.096131 | 122.8912 | 122.9141 | 0.3067 | -0.20142 | 122.6624 | 122.6486 | 0.064087 | 122.8271 | 122.8317 | 0.1831 | -0.01831 | 123.1522 | 122.8546 | 122.7997 | -0.44861 | 123.1201 | 123.0377 | 122.905 | -0.40741
2727.6406 | 123.0423 | -122.9141 | 0.15564 | -0.2864 | 0.039143 | 0.017563 | 0.36289 | -0.081186 | -0.033698 | 0.032347 | -0.31401 | -0.0015704 | -0.021712 | -0.085778 | -0.011456 | 0.10991 | -0.068665 | 0.004578 | -0.086975 | 0.009155 | 0.27466 | -0.10071 | -0.27924 | -0.059509 | 0.022888 | -0.050354 | 0.23804 | 0.16479 | -0.22888 | -0.24261 | 122.8134 | 122.6349 | 0.11902 | 122.9187 | 122.9233 | 0.28839 | -0.22431 | 122.6852 | 122.6715 | 0.082397 | 122.8546 | 122.8638 | 0.19226 | 0.009155 | 123.1888 | 122.8455 | 122.8271 | -0.43488 | 123.1522 | 123.0789 | 122.937 | -0.39826
2728.6406 | 123.0469 | -122.8958 | 0.1831 | -0.2864 | 0.043416 | 0.0068819 | 0.3725 | -0.066232 | -0.013404 | 0.03662 | -0.34453 | -0.012251 | -0.036666 | -0.068688 | 0.01311 | 0.09923 | -0.045776 | -0.004578 | -0.086975 | 0.004578 | 0.28839 | -0.11902 | -0.27466 | -0.054932 | 0.004578 | -0.059509 | 0.24719 | 0.1831 | -0.24261 | -0.24719 | 122.7768 | 122.6212 | 0.10529 | 122.8912 | 122.9004 | 0.27924 | -0.22888 | 122.6532 | 122.6486 | 0.064087 | 122.8409 | 122.8363 | 0.18768 | 0 | 123.1842 | 122.85 | 122.8088 | -0.45776 | 123.143 | 123.0789 | 122.9004 | -0.4303
2729.6406 | 123.0469 | -122.937 | 0.16479 | -0.24062 | 0.047688 | 0.0058129 | 0.37464 | -0.069436 | -0.0059269 | 0.032347 | -0.29875 | -0.0015704 | -0.029189 | -0.063348 | 0.0077701 | 0.10778 | -0.027466 | -0.013733 | -0.10071 | 0.009155 | 0.28381 | -0.10529 | -0.28381 | -0.064087 | 0.004578 | -0.050354 | 0.23346 | 0.16937 | -0.21515 | -0.25635 | 122.8317 | 122.6532 | 0.11902 | 122.9233 | 122.9462 | 0.29297 | -0.19226 | 122.7219 | 122.6807 | 0.068664 | 122.8729 | 122.8867 | 0.20599 | 0.004578 | 123.2208 | 122.9095 | 122.8363 | -0.44861 | 123.1705 | 123.1064 | 122.9416 | -0.42114
2730.6406 | 123.0789 | -122.9004 | 0.19226 | -0.16433 | 0.041279 | 0.0079499 | 0.35968 | -0.066232 | -0.013404 | 0.033416 | -0.28349 | 0.0027016 | -0.024916 | -0.071893 | 0.0077701 | 0.1035 | -0.018311 | 0.009155 | -0.073242 | 0.027466 | 0.27008 | -0.10529 | -0.27008 | -0.036621 | 0.009155 | -0.036621 | 0.24719 | 0.17395 | -0.2243 | -0.24261 | 122.7951 | 122.6303 | 0.07782 | 122.9095 | 122.9279 | 0.29755 | -0.21057 | 122.6761 | 122.6578 | 0.054931 | 122.8638 | 122.8638 | 0.20599 | -0.018311 | 123.1705 | 122.8821 | 122.8271 | -0.46234 | 123.1476 | 123.0743 | 122.9095 | -0.43488
2731.6406 | 123.0331 | -122.9095 | 0.17395 | 0.40025 | 0.084004 | -0.0059361 | 0.37998 | -0.059823 | 0.0036861 | 0.044097 | -0.10039 | -0.010115 | -0.019576 | -0.066552 | 0.016315 | 0.10457 | -0.013733 | 0.009155 | -0.10071 | 0.022888 | 0.2655 | -0.11444 | -0.25635 | -0.059509 | -0.059509 | -0.10529 | 0.2243 | 0.16022 | -0.21057 | -0.23804 | 122.7951 | 122.6532 | 0.091553 | 122.9187 | 122.9324 | 0.27924 | -0.18768 | 122.699 | 122.6715 | 0.050354 | 122.85 | 122.8043 | 0.13275 | -0.013733 | 123.175 | 122.8958 | 122.8088 | -0.4303 | 123.1339 | 123.0698 | 122.85 | -0.41199
2732.6406 | 123.0423 | -122.9324 | 0.16937 | -0.33217 | 0.040211 | 0.0079499 | 0.3693 | -0.071573 | -0.028357 | 0.03662 | -0.39031 | -0.0047754 | -0.024916 | -0.05053 | 0.0067021 | 0.11312 | -0.050354 | 0 | -0.10529 | -0.004578 | 0.28839 | -0.1236 | -0.28381 | -0.050354 | 0.004578 | -0.054932 | 0.24719 | 0.17853 | -0.21057 | -0.23804 | 122.8088 | 122.6486 | 0.11902 | 122.9324 | 122.9279 | 0.27923 | -0.21973 | 122.7219 | 122.6944 | 0.077819 | 122.8821 | 122.8775 | 0.1831 | 0.009155 | 123.2208 | 122.8821 | 122.8271 | -0.45319 | 123.1796 | 123.111 | 122.937 | -0.40741
2733.6406 | 123.0377 | -122.9004 | 0.15564 | -0.24062 | 0.049824 | 0.010086 | 0.37357 | -0.063028 | -0.027289 | 0.038756 | -0.32927 | -0.01332 | -0.047347 | -0.053735 | 0.012042 | 0.10564 | -0.054932 | -0.004578 | -0.086975 | 0 | 0.27924 | -0.11902 | -0.28381 | -0.059509 | 0 | -0.054932 | 0.25177 | 0.1831 | -0.21057 | -0.23804 | 122.7814 | 122.6166 | 0.1236 | 122.8958 | 122.9004 | 0.28381 | -0.21057 | 122.6898 | 122.6624 | 0.09613 | 122.8409 | 122.8455 | 0.1831 | 0.027465 | 123.1796 | 122.8455 | 122.8134 | -0.43945 | 123.1522 | 123.0835 | 122.9004 | -0.39368
2734.6406 | 123.0515 | -122.9004 | 0.1831 | -0.30166 | 0.02953 | 0.0047449 | 0.3693 | -0.055551 | -0.011268 | 0.030211 | -0.31401 | -0.0047754 | -0.043074 | -0.075097 | 0.0056341 | 0.10457 | -0.041199 | 0.018311 | -0.10071 | 0 | 0.28381 | -0.11902 | -0.27466 | -0.059509 | -0.004578 | -0.068665 | 0.24719 | 0.17853 | -0.22888 | -0.24719 | 122.7814 | 122.6257 | 0.10071 | 122.9187 | 122.9004 | 0.27466 | -0.2243 | 122.6715 | 122.6532 | 0.064087 | 122.8409 | 122.8317 | 0.17853 | -0.004577 | 123.1842 | 122.8592 | 122.7997 | -0.45776 | 123.1476 | 123.0789 | 122.8958 | -0.4303
2735.6406 | 123.1613 | -122.8638 | 0.14648 | -0.2101 | 0.022053 | 0.0047449 | 0.37677 | -0.075845 | -0.030494 | 0.037688 | -0.2072 | -0.012251 | -0.045211 | -0.071893 | -0.00077485 | 0.10564 | 0.018311 | 0.15564 | 0.050354 | 0.086975 | 0.23804 | -0.07782 | -0.24261 | 0.032043 | 0.13275 | 0.059509 | 0.19684 | 0.13733 | -0.1831 | -0.20599 | 122.7859 | 122.6212 | 0.091553 | 123.0194 | 122.9507 | 0.32959 | -0.12817 | 122.6807 | 122.6578 | 0.050354 | 122.8958 | 122.9233 | 0.2655 | -0.009155 | 123.1018 | 122.8821 | 122.9141 | -0.3891 | 123.0606 | 123.0011 | 122.9965 | -0.35248
2736.7031 | 123.1659 | -122.8912 | 0.1236 | 0.2324 | 0.028462 | 0.014358 | 0.3757 | -0.074777 | -0.031562 | 0.029143 | 0.11323 | -0.016524 | -0.028121 | -0.06228 | -0.00077485 | 0.11952 | -0.022888 | 0.10529 | 0.009155 | 0.059509 | 0.25635 | -0.086975 | -0.23804 | 0.027466 | 0.09613 | 0.059509 | 0.1831 | 0.13733 | -0.1831 | -0.21515 | 122.8043 | 122.6532 | 0.13275 | 122.9965 | 122.9507 | 0.29755 | -0.14648 | 122.7081 | 122.6761 | 0.059509 | 122.9187 | 122.9507 | 0.27466 | 0.013733 | 123.1476 | 122.8683 | 122.9004 | -0.36163 | 123.0743 | 123.0286 | 122.9874 | -0.33875
2737.6406 | 123.1476 | -122.8729 | 0.13733 | -0.22536 | 0.014576 | 0.0068819 | 0.35541 | -0.075845 | -0.028357 | 0.020598 | -0.22246 | -0.0069114 | -0.044143 | -0.065484 | -0.00077485 | 0.10137 | 0.045776 | 0.14648 | 0.036621 | 0.09613 | 0.22888 | -0.073242 | -0.24261 | 0.054932 | 0.11902 | 0.054932 | 0.20599 | 0.13275 | -0.16937 | -0.19226 | 122.7997 | 122.6303 | 0.091553 | 123.0194 | 122.9691 | 0.33874 | -0.091553 | 122.7036 | 122.6807 | 0.068665 | 122.9279 | 122.9279 | 0.24719 | -0.004578 | 123.1018 | 122.9187 | 122.9095 | -0.37994 | 123.0789 | 123.0057 | 122.9919 | -0.32959
2738.6406 | 123.1888 | -122.8821 | 0.1236 | -0.14907 | 0.017781 | 0.014358 | 0.35541 | -0.080117 | -0.028357 | 0.018462 | -0.23772 | -0.01332 | -0.031325 | -0.066552 | -0.0029109 | 0.096026 | 0.059509 | 0.15106 | 0.027466 | 0.086975 | 0.24261 | -0.068665 | -0.24261 | 0.059509 | 0.13733 | 0.059509 | 0.20142 | 0.10986 | -0.16937 | -0.18768 | 122.8134 | 122.6395 | 0.11902 | 123.0331 | 122.9691 | 0.32959 | -0.064087 | 122.7127 | 122.6944 | 0.07782 | 122.9416 | 122.9416 | 0.24719 | -0.013733 | 123.1247 | 122.9416 | 122.9095 | -0.36621 | 123.0835 | 122.9919 | 123.0194 | -0.31128
2739.6406 | 123.0743 | -122.9095 | 0.16022 | -0.24062 | 0.020985 | 0.0058129 | 0.36182 | -0.082254 | -0.027289 | 0.032347 | -0.42082 | -0.0037074 | -0.038802 | -0.070825 | 0.0099061 | 0.10564 | 0.036621 | 0.10986 | -0.018311 | 0.068665 | 0.26093 | -0.09613 | -0.26093 | -0.013733 | 0.050354 | -0.032043 | 0.21057 | 0.16022 | -0.21973 | -0.23346 | 122.8134 | 122.6486 | 0.10071 | 123.0194 | 122.9782 | 0.32959 | -0.1236 | 122.6898 | 122.6761 | 0.050354 | 122.8958 | 122.8775 | 0.20142 | 0 | 123.1705 | 122.9462 | 122.8912 | -0.42114 | 123.1201 | 123.0698 | 122.9599 | -0.39368
2740.6875 | 123.056 | -122.8821 | 0.14648 | 0.14085 | 0.060505 | 0.0047449 | 0.37464 | -0.072641 | 0.013299 | 0.045165 | -0.10039 | 0.0080426 | -0.033461 | -0.056939 | 0.026996 | 0.086413 | 0.054932 | 0.054932 | -0.073242 | 0.018311 | 0.27466 | -0.09613 | -0.27008 | 0.009155 | -0.009155 | -0.086975 | 0.2243 | 0.16022 | -0.21515 | -0.24719 | 122.7859 | 122.612 | 0.12817 | 122.937 | 122.9004 | 0.28839 | -0.091552 | 122.6669 | 122.6349 | 0.07782 | 122.8912 | 122.7951 | 0.16022 | 0.013733 | 123.1567 | 122.937 | 122.8088 | -0.41657 | 123.1064 | 123.0423 | 122.8729 | -0.39368
2741.6406 | 123.0835 | -122.9095 | 0.1831 | -0.17959 | 0.048756 | 0.0079499 | 0.37891 | -0.066232 | -0.0016549 | 0.033416 | -0.28349 | 0.00056556 | -0.028121 | -0.054803 | 0.0088381 | 0.10671 | -0.018311 | 0.018311 | -0.082397 | 0.027466 | 0.28381 | -0.10529 | -0.30212 | -0.027466 | 0.022888 | -0.064087 | 0.24719 | 0.15564 | -0.20599 | -0.23346 | 122.8043 | 122.6074 | 0.10071 | 122.9279 | 122.937 | 0.32959 | -0.20142 | 122.7036 | 122.6761 | 0.064087 | 122.8821 | 122.8455 | 0.16937 | -0.027465 | 123.1934 | 122.8912 | 122.8271 | -0.48523 | 123.1567 | 123.0652 | 122.9324 | -0.41656
2742.6406 | 123.1567 | -122.8775 | 0.13275 | 0.18663 | 0.010304 | -0.0027321 | 0.34473 | -0.072641 | -0.029426 | 0.044097 | 0.18953 | -0.01332 | -0.037734 | -0.054803 | -0.0039789 | 0.12273 | -0.018311 | 0.07782 | -0.004578 | 0.041199 | 0.2655 | -0.086975 | -0.25177 | 0.041199 | 0.068665 | 0.064087 | 0.20599 | 0.13733 | -0.1831 | -0.21057 | 122.7905 | 122.6257 | 0.13275 | 122.9553 | 122.9187 | 0.29297 | -0.15106 | 122.6944 | 122.6669 | 0.073243 | 122.9187 | 122.9416 | 0.27466 | 0.004578 | 123.143 | 122.8592 | 122.8729 | -0.38452 | 123.0835 | 123.0148 | 122.9462 | -0.34332
2743.6562 | 123.0698 | -122.8912 | 0.14648 | 0.11033 | 0.055165 | 0.0090179 | 0.36395 | -0.065164 | 0.014367 | 0.032347 | -0.17668 | 0.0037696 | -0.029189 | -0.061212 | 0.019519 | 0.09923 | 0.068665 | 0.09613 | -0.064087 | 0.050354 | 0.26093 | -0.10071 | -0.27924 | 0.027466 | 0.022888 | -0.050354 | 0.21515 | 0.13275 | -0.21057 | -0.23346 | 122.7905 | 122.612 | 0.11444 | 122.9874 | 122.9416 | 0.32959 | -0.077819 | 122.6807 | 122.6578 | 0.068665 | 122.9187 | 122.8409 | 0.1831 | -0.013733 | 123.1522 | 122.9599 | 122.8271 | -0.42572 | 123.1064 | 123.024 | 122.9141 | -0.37994
2744.6406 | 123.1934 | -122.8729 | 0.15106 | 0.034038 | 0.01244 | 0.012222 | 0.35434 | -0.0673 | -0.030494 | 0.04196 | 0.0064239 | -0.0047754 | -0.043074 | -0.065484 | -0.010388 | 0.11525 | 0.022888 | 0.12817 | 0.027466 | 0.068665 | 0.25635 | -0.086975 | -0.22888 | 0.07782 | 0.12817 | 0.07782 | 0.19684 | 0.13275 | -0.17395 | -0.19226 | 122.7859 | 122.644 | 0.10529 | 123.0011 | 122.9416 | 0.29755 | -0.12817 | 122.699 | 122.6807 | 0.045776 | 122.9507 | 122.9507 | 0.27008 | -0.018311 | 123.1293 | 122.8958 | 122.9004 | -0.37994 | 123.0698 | 123.0057 | 123.0011 | -0.34332
2745.6562 | 123.111 | -122.8912 | 0.15106 | 0.064555 | 0.049824 | 0.016495 | 0.3757 | -0.063028 | 0.0058221 | 0.048369 | -0.31401 | -0.00050244 | -0.032393 | -0.063348 | 0.023792 | 0.092821 | 0.050354 | 0.059509 | -0.059509 | 0.050354 | 0.27466 | -0.10986 | -0.27924 | 0.022888 | 0.036621 | -0.041199 | 0.20599 | 0.15564 | -0.20142 | -0.22888 | 122.7814 | 122.612 | 0.1236 | 122.9507 | 122.9416 | 0.32959 | -0.10071 | 122.6898 | 122.6624 | 0.054932 | 122.9141 | 122.85 | 0.18768 | 0.004578 | 123.1659 | 122.9416 | 122.8317 | -0.4303 | 123.0972 | 123.0469 | 122.9279 | -0.37994
2746.6406 | 123.0423 | -122.9507 | 0.16022 | -0.30166 | 0.033803 | -0.0027321 | 0.38318 | -0.075845 | -0.017676 | 0.040892 | -0.35979 | -0.0037074 | -0.040938 | -0.064416 | -0.0061159 | 0.10884 | -0.018311 | 0.009155 | -0.09613 | 0.013733 | 0.29297 | -0.10986 | -0.27466 | -0.064087 | 0.013733 | -0.073242 | 0.22888 | 0.16937 | -0.21515 | -0.24261 | 122.8409 | 122.6761 | 0.13275 | 122.9599 | 122.9645 | 0.28839 | -0.17853 | 122.7356 | 122.7081 | 0.068665 | 122.8867 | 122.8775 | 0.16937 | 0.009156 | 123.2437 | 122.9324 | 122.8546 | -0.43488 | 123.1796 | 123.1201 | 122.9645 | -0.40283
2747.6406 | 123.1705 | -122.8821 | 0.14191 | 0.18663 | 0.0081682 | 0.0079499 | 0.36395 | -0.077981 | -0.030494 | 0.028075 | 0.036941 | -0.014388 | -0.03453 | -0.075097 | 0.0024291 | 0.11632 | -0.009155 | 0.086975 | 0.004578 | 0.050354 | 0.25635 | -0.073242 | -0.26093 | 0.036621 | 0.091553 | 0.059509 | 0.19684 | 0.15106 | -0.1831 | -0.2243 | 122.8088 | 122.6212 | 0.11444 | 122.9691 | 122.9324 | 0.31128 | -0.15106 | 122.699 | 122.6578 | 0.054931 | 122.9187 | 122.9416 | 0.28381 | 0.009155 | 123.1384 | 122.8729 | 122.8867 | -0.40283 | 123.0789 | 123.0331 | 122.9736 | -0.36621
2748.6406 | 123.1522 | -122.8821 | 0.12817 | 0.4918 | 0.056233 | 0.01329 | 0.35968 | -0.071573 | -0.020881 | 0.034484 | 0.50996 | -0.0090474 | -0.040938 | -0.064416 | 0.014179 | 0.10243 | 0.059509 | 0.11444 | 0.022888 | 0.064087 | 0.23346 | -0.073242 | -0.21973 | 0.073242 | 0.054932 | 0.050354 | 0.19684 | 0.11444 | -0.19226 | -0.20142 | 122.8088 | 122.6624 | 0.10528 | 122.9965 | 122.9462 | 0.28381 | -0.068665 | 122.6898 | 122.6807 | 0.068664 | 122.9553 | 122.9324 | 0.25177 | -0.013733 | 123.1155 | 122.9416 | 122.905 | -0.3479 | 123.0789 | 122.9965 | 122.937 | -0.32959
2749.6406 | 123.1705 | -122.9095 | 0.14648 | 0.18663 | 0.034871 | 0.0068819 | 0.37143 | -0.066232 | -0.030494 | 0.023803 | 0.11323 | -0.010115 | -0.044143 | -0.061212 | -0.0018429 | 0.10671 | 0.018311 | 0.073242 | -0.004578 | 0.064087 | 0.2655 | -0.07782 | -0.23804 | 0.027466 | 0.10071 | 0.068665 | 0.1831 | 0.13733 | -0.19226 | -0.21057 | 122.8317 | 122.6715 | 0.11902 | 122.9828 | 122.9736 | 0.30212 | -0.12817 | 122.7173 | 122.699 | 0.036621 | 122.937 | 122.9782 | 0.27924 | -0.009155 | 123.175 | 122.9279 | 122.905 | -0.38452 | 123.0927 | 123.0469 | 123.0103 | -0.35706
2750.6406 | 123.1384 | -122.8867 | 0.15564 | 0.36973 | 0.018849 | 0.0079499 | 0.37891 | -0.072641 | -0.017676 | 0.022734 | 0.22005 | -0.0069114 | -0.037734 | -0.061212 | 0.0024291 | 0.1035 | 0.041199 | 0.068665 | -0.009155 | 0.036621 | 0.25635 | -0.068665 | -0.23346 | 0.036621 | 0.050354 | 0.032043 | 0.1831 | 0.13733 | -0.19226 | -0.21057 | 122.818 | 122.6532 | 0.10071 | 122.9553 | 122.9233 | 0.27008 | -0.11444 | 122.6944 | 122.6761 | 0.027465 | 122.9233 | 122.9187 | 0.24261 | -0.018311 | 123.143 | 122.9279 | 122.8775 | -0.3891 | 123.0698 | 123.024 | 122.937 | -0.36621
2751.6406 | 123.0698 | -122.9095 | 0.19684 | -0.22536 | 0.053029 | 0.0047449 | 0.38639 | -0.060891 | 0.0036861 | 0.035552 | -0.4666 | -0.00050244 | -0.038802 | -0.053735 | 0.023792 | 0.087481 | 0.018311 | 0 | -0.10071 | 0.018311 | 0.27466 | -0.13275 | -0.28381 | -0.013733 | -0.009155 | -0.059509 | 0.23346 | 0.16479 | -0.21973 | -0.24261 | 122.7768 | 122.6257 | 0.07782 | 122.9095 | 122.9279 | 0.30212 | -0.17853 | 122.6898 | 122.6669 | 0.036621 | 122.8958 | 122.85 | 0.18311 | -0.032043 | 123.1842 | 122.9279 | 122.8088 | -0.48065 | 123.143 | 123.0743 | 122.9004 | -0.43945
2752.6406 | 123.1567 | -122.8821 | 0.14191 | 0.50706 | 0.056233 | 0.01329 | 0.37143 | -0.075845 | -0.01554 | 0.034484 | 0.43367 | -0.012251 | -0.042006 | -0.071893 | 0.0067021 | 0.11098 | 0.068665 | 0.14191 | 0.018311 | 0.07782 | 0.23346 | -0.059509 | -0.24719 | 0.086975 | 0.091553 | 0.041199 | 0.17395 | 0.12817 | -0.1831 | -0.21057 | 122.8226 | 122.6349 | 0.091552 | 123.024 | 122.9599 | 0.32501 | -0.073242 | 122.699 | 122.6715 | 0.032043 | 122.9691 | 122.9233 | 0.25177 | -0.013733 | 123.1155 | 122.9507 | 122.9004 | -0.3891 | 123.056 | 123.0103 | 122.9736 | -0.35248
2753.6875 | 123.0698 | -122.9187 | 0.15564 | 0.21714 | 0.051961 | -0.0048681 | 0.37143 | -0.065164 | 0.020776 | 0.047301 | 0.11323 | 0.0037696 | -0.016372 | -0.06228 | 0.021655 | 0.098162 | 0.004578 | -0.013733 | -0.11444 | -0.009155 | 0.29297 | -0.09613 | -0.27924 | -0.018311 | -0.022888 | -0.091553 | 0.23346 | 0.16479 | -0.20599 | -0.2243 | 122.8226 | 122.6395 | 0.13733 | 122.905 | 122.9095 | 0.27008 | -0.15106 | 122.7127 | 122.6944 | 0.077819 | 122.9004 | 122.8271 | 0.13275 | 0.009155 | 123.2117 | 122.9233 | 122.8043 | -0.43488 | 123.1522 | 123.0835 | 122.8958 | -0.37994
2754.6406 | 123.1888 | -122.8912 | 0.14191 | 0.65965 | 0.056233 | -0.0059361 | 0.35968 | -0.065164 | -0.0059269 | 0.044097 | 0.43367 | -0.0037074 | -0.029189 | -0.059075 | 0.019519 | 0.10457 | 0.07782 | 0.13275 | 0.032043 | 0.091553 | 0.23346 | -0.068665 | -0.21057 | 0.10071 | 0.10529 | 0.064087 | 0.1831 | 0.11444 | -0.1831 | -0.21973 | 122.8226 | 122.6807 | 0.091552 | 123.024 | 122.9828 | 0.30212 | -0.064087 | 122.7081 | 122.6715 | 0.041198 | 122.9919 | 122.9553 | 0.28381 | -0.027466 | 123.1247 | 122.9691 | 122.9233 | -0.35248 | 123.0743 | 123.0057 | 122.9965 | -0.36163
2755.6719 | 123.2025 | -122.8958 | 0.13275 | -0.088033 | 0.038075 | 0.010086 | 0.37784 | -0.0673 | -0.029426 | 0.029143 | -0.22246 | -0.0047754 | -0.050551 | -0.074029 | 0.0056341 | 0.10884 | 0.07782 | 0.15106 | 0.032043 | 0.091553 | 0.22888 | -0.07782 | -0.2243 | 0.068665 | 0.15106 | 0.082397 | 0.1831 | 0.13733 | -0.16937 | -0.21515 | 122.818 | 122.6715 | 0.096131 | 123.0469 | 122.9874 | 0.31586 | -0.054931 | 122.7264 | 122.6807 | 0.050354 | 122.9645 | 122.9782 | 0.29755 | 0.004578 | 123.1247 | 122.9736 | 122.9279 | -0.35706 | 123.0789 | 123.0331 | 123.0469 | -0.3479
2756.6406 | 123.0972 | -122.9141 | 0.15564 | 0.40025 | 0.051961 | 0.0068819 | 0.3693 | -0.066232 | 0.00048206 | 0.033416 | 0.25056 | 0.0027016 | -0.031325 | -0.061212 | 0.016315 | 0.10671 | 0.036621 | -0.009155 | -0.10986 | 0 | 0.27466 | -0.09613 | -0.2655 | 0.013733 | 0 | -0.050354 | 0.21057 | 0.16022 | -0.21515 | -0.2243 | 122.818 | 122.6486 | 0.11902 | 122.905 | 122.9141 | 0.2655 | -0.11902 | 122.699 | 122.6898 | 0.054931 | 122.9279 | 122.8638 | 0.17395 | 0.004577 | 123.1888 | 122.9507 | 122.8043 | -0.42114 | 123.1247 | 123.0743 | 122.9141 | -0.37994
2757.6406 | 123.1705 | -122.9004 | 0.13275 | 0.59861 | 0.038075 | -0.00059506 | 0.35541 | -0.074777 | -0.018744 | 0.031279 | 0.47945 | -0.0090474 | -0.036666 | -0.065484 | 0.0067021 | 0.1035 | 0.07782 | 0.11444 | 0.018311 | 0.091553 | 0.2243 | -0.091553 | -0.20599 | 0.10529 | 0.09613 | 0.050354 | 0.18768 | 0.13275 | -0.1831 | -0.20142 | 122.8088 | 122.6944 | 0.091553 | 123.0148 | 122.9919 | 0.29755 | -0.054931 | 122.7173 | 122.699 | 0.054932 | 123.0057 | 122.9507 | 0.25177 | 0 | 123.1247 | 122.9782 | 122.9187 | -0.33875 | 123.0881 | 123.0331 | 122.9965 | -0.33417
2758.6406 | 123.1796 | -122.905 | 0.13275 | 0.58335 | 0.062642 | -0.0016631 | 0.3725 | -0.066232 | 0.0090271 | 0.039824 | 0.32686 | -0.00050244 | -0.016372 | -0.070825 | 0.016315 | 0.10137 | 0.064087 | 0.050354 | -0.036621 | 0.054932 | 0.24719 | -0.082397 | -0.25177 | 0.073242 | 0.07782 | 0.036621 | 0.19226 | 0.13733 | -0.16022 | -0.19684 | 122.8226 | 122.6532 | 0.11444 | 122.9553 | 122.9599 | 0.3067 | -0.068664 | 122.7448 | 122.7081 | 0.05951 | 122.9782 | 122.9416 | 0.23346 | 0.004578 | 123.1522 | 122.9691 | 122.8683 | -0.38452 | 123.0972 | 123.0423 | 122.9828 | -0.32959
2759.6406 | 123.1613 | -122.9141 | 0.13733 | 0.47654 | 0.066914 | 0.0047449 | 0.36289 | -0.069436 | -0.0059269 | 0.04196 | 0.38789 | 0.012315 | -0.0088954 | -0.058007 | 0.014179 | 0.11632 | 0.027466 | 0.004578 | -0.073242 | 0.018311 | 0.2655 | -0.10071 | -0.23346 | 0.022888 | 0.018311 | -0.022888 | 0.21515 | 0.14648 | -0.19684 | -0.23346 | 122.8134 | 122.6807 | 0.12817 | 122.9187 | 122.9324 | 0.25177 | -0.10986 | 122.7173 | 122.6807 | 0.07782 | 122.937 | 122.8912 | 0.21057 | 0.009155 | 123.1796 | 122.9416 | 122.8409 | -0.37079 | 123.1293 | 123.0606 | 122.9324 | -0.37079
2760.6406 | 123.1934 | -122.8867 | 0.12817 | 0.4918 | 0.060505 | 0.0026089 | 0.37036 | -0.076913 | 0.0026181 | 0.044097 | 0.41841 | -0.0026384 | -0.033461 | -0.071893 | 0.017383 | 0.10564 | 0.064087 | 0.036621 | -0.041199 | 0.059509 | 0.26093 | -0.082397 | -0.2655 | 0.07782 | 0.041199 | 0.045776 | 0.19226 | 0.14191 | -0.17395 | -0.18768 | 122.8043 | 122.6212 | 0.13275 | 122.9233 | 122.9462 | 0.32501 | -0.064087 | 122.7127 | 122.699 | 0.064087 | 122.9645 | 122.9324 | 0.23346 | 0.013733 | 123.1476 | 122.9507 | 122.8455 | -0.39368 | 123.0789 | 123.0286 | 122.9279 | -0.31586
2761.6406 | 123.0927 | -122.9507 | 0.16479 | 0.53758 | 0.067982 | 0.0036769 | 0.349 | -0.0673 | 0.0036861 | 0.044097 | 0.3116 | 0.0027016 | -0.013167 | -0.055871 | 0.012042 | 0.11846 | 0.009155 | -0.036621 | -0.10529 | 0.009155 | 0.30212 | -0.09613 | -0.28839 | -0.022888 | -0.036621 | -0.064087 | 0.20599 | 0.16022 | -0.20142 | -0.24719 | 122.8546 | 122.6624 | 0.13733 | 122.9141 | 122.9599 | 0.29755 | -0.15564 | 122.7493 | 122.7036 | 0.041199 | 122.9279 | 122.8867 | 0.1831 | -0.004578 | 123.2529 | 122.9599 | 122.8455 | -0.45319 | 123.1567 | 123.111 | 122.9141 | -0.41199
2762.6406 | 123.0698 | -122.9462 | 0.13733 | 0.35447 | 0.056233 | -0.0091401 | 0.36716 | -0.064096 | 0.0068901 | 0.045165 | 0.18953 | 0.0027016 | -0.018508 | -0.076165 | 0.01311 | 0.097094 | 0.018311 | 0 | -0.09613 | 0.027466 | 0.27466 | -0.11444 | -0.27466 | -0.022888 | 0 | -0.086975 | 0.23804 | 0.16937 | -0.21973 | -0.24261 | 122.8317 | 122.6715 | 0.13733 | 122.9462 | 122.9736 | 0.30212 | -0.11902 | 122.7264 | 122.7036 | 0.10071 | 122.9233 | 122.8592 | 0.15564 | 0.032044 | 123.2208 | 122.9645 | 122.85 | -0.41199 | 123.1842 | 123.1155 | 122.9462 | -0.37994
2763.6875 | 123.1018 | -122.9462 | 0.16937 | -0.24062 | 0.048756 | 0.0026089 | 0.37784 | -0.075845 | -0.018744 | 0.043029 | -0.35979 | -0.0015704 | -0.0035544 | -0.078301 | 0.0099061 | 0.1035 | -0.027466 | 0.004578 | -0.091553 | 0.009155 | 0.28381 | -0.12817 | -0.28381 | -0.041199 | 0.013733 | -0.059509 | 0.24261 | 0.18768 | -0.23346 | -0.25177 | 122.818 | 122.6624 | 0.11444 | 122.9507 | 122.9553 | 0.29297 | -0.19684 | 122.7127 | 122.6944 | 0.073242 | 122.905 | 122.8867 | 0.19226 | 0.01831 | 123.23 | 122.9187 | 122.8546 | -0.45319 | 123.1888 | 123.1339 | 122.9599 | -0.42114
2764.6406 | 123.0927 | -122.9462 | 0.15564 | 0.58335 | 0.059437 | 0.0015409 | 0.3757 | -0.074777 | -0.0016549 | 0.047301 | 0.25056 | 0.0027016 | -0.02278 | -0.060143 | 0.017383 | 0.10137 | 0 | -0.027466 | -0.10529 | 0.009155 | 0.27466 | -0.10529 | -0.26093 | -0.041199 | -0.036621 | -0.082397 | 0.2243 | 0.16937 | -0.21515 | -0.23346 | 122.8409 | 122.6852 | 0.11902 | 122.9187 | 122.9553 | 0.27008 | -0.15564 | 122.731 | 122.7127 | 0.068664 | 122.905 | 122.8638 | 0.15106 | 0.013733 | 123.2208 | 122.9462 | 122.8409 | -0.41657 | 123.1705 | 123.1155 | 122.9095 | -0.3891
2765.6406 | 123.1064 | -122.9507 | 0.16022 | 0.47654 | 0.055165 | -0.0048681 | 0.36609 | -0.069436 | 0.010095 | 0.040892 | 0.38789 | 0.0091106 | -0.037734 | -0.060143 | 0.018451 | 0.11098 | -0.009155 | -0.022888 | -0.10071 | 0.004578 | 0.31128 | -0.1236 | -0.27466 | -0.027466 | -0.022888 | -0.054932 | 0.21973 | 0.15564 | -0.22888 | -0.23346 | 122.8271 | 122.6761 | 0.15106 | 122.9279 | 122.9553 | 0.27924 | -0.16937 | 122.7219 | 122.7173 | 0.05951 | 122.9233 | 122.8958 | 0.17853 | -0.004577 | 123.262 | 122.9416 | 122.85 | -0.43488 | 123.1705 | 123.1064 | 122.9279 | -0.39368
2766.6406 | 123.0743 | -122.9599 | 0.17395 | 0.20188 | 0.087208 | -0.00059506 | 0.36609 | -0.069436 | -0.0016549 | 0.049437 | 0.097976 | 0.0069746 | -0.023848 | -0.066552 | 0.020587 | 0.10564 | -0.004578 | -0.018311 | -0.091553 | 0.022888 | 0.27466 | -0.11444 | -0.28381 | -0.054932 | -0.022888 | -0.082397 | 0.23804 | 0.15564 | -0.21973 | -0.24261 | 122.8455 | 122.6761 | 0.10071 | 122.9416 | 122.9828 | 0.3067 | -0.17853 | 122.7402 | 122.7173 | 0.064087 | 122.905 | 122.8775 | 0.16022 | -0.01831 | 123.2346 | 122.9553 | 122.8683 | -0.45776 | 123.1979 | 123.1155 | 122.937 | -0.41656
2767.6719 | 123.1567 | -122.9324 | 0.13275 | 0.50706 | 0.044484 | 0.01329 | 0.35968 | -0.068368 | -0.03797 | 0.033416 | 0.54048 | -0.0058434 | -0.019576 | -0.081506 | -0.0050469 | 0.10884 | 0.004578 | 0.091553 | -0.004578 | 0.050354 | 0.21973 | -0.086975 | -0.23804 | 0.032043 | 0.064087 | 0.045776 | 0.20142 | 0.14648 | -0.17853 | -0.2243 | 122.8455 | 122.6944 | 0.086976 | 123.024 | 122.9828 | 0.28839 | -0.12817 | 122.7539 | 122.7081 | 0.068665 | 122.9645 | 122.9782 | 0.27008 | 0.013733 | 123.1522 | 122.937 | 122.9279 | -0.37079 | 123.1338 | 123.0789 | 122.9965 | -0.35706
2768.6406 | 123.111 | -122.9324 | 0.15564 | 0.049296 | 0.088276 | 0.0047449 | 0.36395 | -0.075845 | 0.010095 | 0.046233 | 0.021682 | 0.0016336 | -0.031325 | -0.06228 | 0.02486 | 0.09923 | 0.041199 | 0.068665 | -0.073242 | 0.045776 | 0.25177 | -0.10529 | -0.26093 | -0.004578 | 0.018311 | -0.050354 | 0.20599 | 0.13733 | -0.21515 | -0.24261 | 122.8271 | 122.6715 | 0.09613 | 123.0011 | 122.9782 | 0.3067 | -0.11444 | 122.7173 | 122.6898 | 0.050354 | 122.9279 | 122.8821 | 0.19226 | -0.018311 | 123.1842 | 122.9736 | 122.8592 | -0.41657 | 123.1384 | 123.0698 | 122.9507 | -0.39826
2769.6406 | 123.0972 | -122.9553 | 0.17395 | 0.26292 | 0.074391 | -0.0091401 | 0.37036 | -0.068368 | -0.0059269 | 0.030211 | 0.0522 | 0.0059056 | -0.027053 | -0.06228 | 0.017383 | 0.10243 | -0.004578 | 0.027466 | -0.082397 | 0.032043 | 0.27924 | -0.10529 | -0.28839 | -0.022888 | 0 | -0.050354 | 0.23804 | 0.16937 | -0.2243 | -0.24719 | 122.85 | 122.6669 | 0.10529 | 122.9828 | 122.9874 | 0.32043 | -0.17853 | 122.731 | 122.7081 | 0.064087 | 122.9324 | 122.905 | 0.19684 | -0.004577 | 123.2346 | 122.9507 | 122.8729 | -0.46234 | 123.1934 | 123.1247 | 122.9553 | -0.42114
2770.6406 | 123.1247 | -122.937 | 0.15564 | 0.049296 | 0.072255 | -0.0027321 | 0.36075 | -0.074777 | -0.0037909 | 0.048369 | -0.23772 | -0.011183 | -0.0099634 | -0.064416 | 0.019519 | 0.09389 | 0.009155 | 0.059509 | -0.059509 | 0.050354 | 0.25635 | -0.09613 | -0.25177 | 0.013733 | 0.050354 | -0.036621 | 0.22888 | 0.16022 | -0.20142 | -0.23804 | 122.8409 | 122.6852 | 0.10071 | 122.9965 | 122.9874 | 0.30212 | -0.14649 | 122.7356 | 122.699 | 0.073242 | 122.9507 | 122.9004 | 0.20142 | 0.004577 | 123.1934 | 122.9462 | 122.8775 | -0.40741 | 123.1659 | 123.0972 | 122.9874 | -0.39368
2771.6406 | 123.1247 | -122.937 | 0.15106 | 0.12559 | 0.060505 | 0.012222 | 0.3725 | -0.065164 | -0.0048589 | 0.047301 | -0.039353 | 0.0016336 | -0.0056904 | -0.069756 | 0.019519 | 0.10671 | 0.022888 | 0.045776 | -0.059509 | 0.045776 | 0.2655 | -0.11444 | -0.28381 | 0.004578 | 0.036621 | -0.045776 | 0.21973 | 0.15564 | -0.21057 | -0.23346 | 122.8226 | 122.6532 | 0.11444 | 122.9828 | 122.9828 | 0.32959 | -0.12817 | 122.7264 | 122.7036 | 0.068665 | 122.9416 | 122.8912 | 0.18768 | 0.004578 | 123.2025 | 122.9599 | 122.8775 | -0.43488 | 123.1567 | 123.0927 | 122.9736 | -0.38452
2772.6406 | 123.1155 | -122.9324 | 0.16022 | 0.18663 | 0.074391 | 0.0079499 | 0.37998 | -0.070504 | 0.0026181 | 0.040892 | 0.067459 | -0.00050244 | -0.029189 | -0.070825 | 0.021655 | 0.11525 | 0.032043 | 0.032043 | -0.082397 | 0.045776 | 0.28381 | -0.086975 | -0.25177 | -0.032043 | 0.009155 | -0.054932 | 0.21973 | 0.16022 | -0.20142 | -0.23346 | 122.8455 | 122.6807 | 0.1236 | 122.9645 | 122.9782 | 0.29755 | -0.12817 | 122.731 | 122.699 | 0.05951 | 122.9004 | 122.8775 | 0.17853 | 0 | 123.2162 | 122.9645 | 122.85 | -0.41199 | 123.1522 | 123.0927 | 122.9416 | -0.39368
2773.6562 | 123.1979 | -122.937 | 0.13733 | 0.53758 | 0.064778 | 0.0015409 | 0.37357 | -0.077981 | -0.033698 | 0.030211 | 0.47945 | -0.0079794 | -0.03987 | -0.056939 | -0.0082519 | 0.11312 | 0.054932 | 0.09613 | 0.027466 | 0.082397 | 0.23804 | -0.07782 | -0.2243 | 0.050354 | 0.086975 | 0.054932 | 0.19684 | 0.12817 | -0.16937 | -0.21057 | 122.8592 | 122.7127 | 0.10071 | 123.0331 | 123.0194 | 0.3067 | -0.082397 | 122.7676 | 122.7264 | 0.059509 | 122.9874 | 122.9919 | 0.2655 | -0.009155 | 123.175 | 122.9919 | 122.9645 | -0.36163 | 123.1338 | 123.0652 | 123.024 | -0.3479
2774.6406 | 123.1384 | -122.9645 | 0.14191 | -0.026997 | 0.0808 | -0.0016631 | 0.37677 | -0.074777 | 0.0015501 | 0.039824 | -0.2072 | -0.0015704 | -0.025985 | -0.068688 | 0.019519 | 0.098162 | 0.036621 | 0.07782 | -0.059509 | 0.050354 | 0.27924 | -0.10529 | -0.2655 | 0.004578 | 0.032043 | -0.036621 | 0.20599 | 0.15106 | -0.21515 | -0.23346 | 122.8592 | 122.699 | 0.13733 | 123.0423 | 123.0148 | 0.31586 | -0.10529 | 122.7493 | 122.731 | 0.064087 | 122.9691 | 122.9279 | 0.19684 | 0.009155 | 123.2437 | 123.0011 | 122.905 | -0.40741 | 123.1705 | 123.1155 | 122.9965 | -0.37537
2775.7031 | 123.2208 | -122.9095 | 0.1236 | 0.61387 | 0.047688 | 0.01329 | 0.37143 | -0.059823 | -0.010199 | 0.043029 | 0.47945 | -0.0026384 | -0.02278 | -0.060143 | 0.0067021 | 0.11632 | 0.018311 | 0.045776 | -0.027466 | 0.045776 | 0.25635 | -0.091553 | -0.24261 | 0.059509 | 0.009155 | 0.068665 | 0.1831 | 0.12817 | -0.17853 | -0.21057 | 122.818 | 122.6669 | 0.13275 | 122.9553 | 122.9553 | 0.28839 | -0.10528 | 122.731 | 122.699 | 0.059509 | 122.9691 | 122.9782 | 0.27924 | 0.004578 | 123.1659 | 122.9279 | 122.8821 | -0.36621 | 123.0927 | 123.0377 | 122.9187 | -0.33417
2776.6406 | 123.0972 | -122.9416 | 0.16937 | -0.27114 | 0.041279 | 0.016495 | 0.3725 | -0.064096 | -0.018744 | 0.037688 | -0.35979 | -0.0069114 | -0.019576 | -0.064416 | 0.0024291 | 0.10884 | -0.054932 | 0.018311 | -0.10529 | 0.004578 | 0.29297 | -0.12817 | -0.28381 | -0.068665 | 0 | -0.059509 | 0.24719 | 0.19226 | -0.24261 | -0.23346 | 122.8134 | 122.6578 | 0.1236 | 122.9599 | 122.9462 | 0.28839 | -0.22431 | 122.699 | 122.7081 | 0.077819 | 122.8729 | 122.8821 | 0.17395 | 0.022888 | 123.2346 | 122.8867 | 122.8363 | -0.45319 | 123.1888 | 123.1338 | 122.9416 | -0.40283
2777.6406 | 123.111 | -122.9691 | 0.16479 | -0.22536 | 0.050892 | 0.0015409 | 0.37357 | -0.073709 | -0.0091309 | 0.035552 | -0.26824 | -0.0058434 | -0.036666 | -0.066552 | 0.0099061 | 0.1035 | -0.059509 | 0.013733 | -0.10986 | 0.018311 | 0.27924 | -0.11902 | -0.27466 | -0.064087 | 0 | -0.064087 | 0.23804 | 0.16937 | -0.21515 | -0.24261 | 122.85 | 122.6944 | 0.11444 | 122.9828 | 122.9874 | 0.29297 | -0.2243 | 122.7539 | 122.7264 | 0.073242 | 122.905 | 122.905 | 0.17853 | 0.004578 | 123.2483 | 122.9095 | 122.8592 | -0.43945 | 123.2071 | 123.1384 | 122.9691 | -0.40741
2778.6562 | 123.2391 | -122.9233 | 0.13733 | 0.58335 | 0.041279 | 0.010086 | 0.37357 | -0.058755 | -0.0027229 | 0.032347 | 0.46419 | -0.0026384 | -0.020644 | -0.051599 | 0.014179 | 0.10457 | 0.045776 | 0.09613 | -0.009155 | 0.064087 | 0.25177 | -0.068665 | -0.23346 | 0.059509 | 0.091553 | 0.045776 | 0.17853 | 0.10529 | -0.19684 | -0.19226 | 122.8546 | 122.6898 | 0.11444 | 123.0194 | 122.9874 | 0.29755 | -0.091553 | 122.7264 | 122.731 | 0.041199 | 122.9828 | 122.9691 | 0.23804 | -0.032043 | 123.175 | 122.9691 | 122.9141 | -0.37079 | 123.1018 | 123.0286 | 123.0148 | -0.32959
2779.6406 | 123.1155 | -122.9553 | 0.15564 | -0.24062 | 0.045552 | 0.0090179 | 0.37143 | -0.077981 | -0.0069949 | 0.033416 | -0.29875 | -0.0015704 | -0.036666 | -0.070825 | 0.014179 | 0.1035 | -0.036621 | 0.009155 | -0.091553 | 0.004578 | 0.28839 | -0.1236 | -0.27008 | -0.064087 | -0.004578 | -0.045776 | 0.23804 | 0.16479 | -0.23346 | -0.25177 | 122.8317 | 122.6852 | 0.13275 | 122.9645 | 122.9599 | 0.27466 | -0.19226 | 122.7219 | 122.7036 | 0.082397 | 122.8912 | 122.9095 | 0.20599 | 0.009155 | 123.2437 | 122.9187 | 122.8638 | -0.42572 | 123.1934 | 123.1201 | 122.9507 | -0.40741
2780.6562 | 123.1705 | -122.9324 | 0.14648 | 0.52232 | 0.064778 | 0.0068819 | 0.36716 | -0.073709 | -0.0080629 | 0.04196 | 0.38789 | -0.0069114 | -0.032393 | -0.06228 | 0.019519 | 0.10991 | -0.004578 | 0.032043 | -0.082397 | 0.022888 | 0.27924 | -0.10071 | -0.27466 | 0.009155 | 0.009155 | -0.009155 | 0.20142 | 0.15564 | -0.19226 | -0.21515 | 122.8317 | 122.6578 | 0.13275 | 122.9645 | 122.9553 | 0.29755 | -0.15106 | 122.7402 | 122.7173 | 0.054932 | 122.9416 | 122.9233 | 0.20599 | 0.009156 | 123.2117 | 122.9279 | 122.85 | -0.42114 | 123.1338 | 123.0881 | 122.9416 | -0.36163
2781.6406 | 123.1247 | -122.9553 | 0.15564 | -0.17959 | 0.073323 | 0.00047294 | 0.3693 | -0.073709 | -0.012336 | 0.035552 | -0.29875 | -0.0047754 | -0.03453 | -0.06762 | 0.012042 | 0.11312 | -0.027466 | 0.022888 | -0.07782 | 0.018311 | 0.29297 | -0.10529 | -0.26093 | -0.050354 | 0 | -0.059509 | 0.23804 | 0.17395 | -0.22888 | -0.24261 | 122.85 | 122.6944 | 0.13733 | 122.9782 | 122.9736 | 0.27924 | -0.18311 | 122.7264 | 122.7127 | 0.082397 | 122.905 | 122.8958 | 0.18311 | 0.01831 | 123.2483 | 122.9279 | 122.8775 | -0.41657 | 123.1934 | 123.1293 | 122.9553 | -0.39826
2782.6406 | 123.1155 | -122.9599 | 0.18768 | -0.25588 | 0.030598 | 0.0090179 | 0.36182 | -0.070504 | -0.023017 | 0.028075 | -0.35979 | -0.01332 | -0.038802 | -0.063348 | -0.0071839 | 0.10991 | -0.036621 | 0.045776 | -0.073242 | 0.018311 | 0.27008 | -0.10529 | -0.27924 | -0.054932 | 0 | -0.054932 | 0.23346 | 0.15564 | -0.2243 | -0.24719 | 122.8546 | 122.6807 | 0.082398 | 123.0057 | 122.9782 | 0.29755 | -0.2243 | 122.7356 | 122.7127 | 0.045776 | 122.905 | 122.905 | 0.19226 | -0.032043 | 123.23 | 122.9233 | 122.8867 | -0.46692 | 123.1934 | 123.1155 | 122.9599 | -0.43488
2783.7031 | 123.0743 | -122.9416 | 0.14191 | 0.3087 | 0.073323 | -0.0059361 | 0.37357 | -0.064096 | 0.011163 | 0.03662 | 0.15901 | 0.00056556 | -0.027053 | -0.066552 | 0.015247 | 0.096026 | -0.032043 | -0.004578 | -0.10071 | 0.013733 | 0.28381 | -0.11902 | -0.27466 | -0.054932 | -0.064087 | -0.10529 | 0.24261 | 0.16479 | -0.21057 | -0.24261 | 122.8226 | 122.6669 | 0.14191 | 122.937 | 122.9553 | 0.28839 | -0.17395 | 122.731 | 122.699 | 0.10071 | 122.8867 | 122.8363 | 0.13733 | 0.022888 | 123.2254 | 122.9095 | 122.8409 | -0.41657 | 123.1842 | 123.1064 | 122.8775 | -0.38452
2784.6406 | 123.1064 | -122.9736 | 0.17395 | -0.22536 | 0.050892 | 0.014358 | 0.3693 | -0.08439 | -0.025153 | 0.040892 | -0.29875 | -0.0058434 | -0.038802 | -0.074029 | 0.0045661 | 0.10884 | -0.045776 | 0.027466 | -0.082397 | 0.004578 | 0.28381 | -0.12817 | -0.29755 | -0.050354 | 0.004578 | -0.054932 | 0.24261 | 0.16937 | -0.21057 | -0.25635 | 122.8455 | 122.6761 | 0.10986 | 123.0011 | 122.9782 | 0.30212 | -0.21973 | 122.7631 | 122.7173 | 0.068665 | 122.9233 | 122.9187 | 0.20142 | -0.004577 | 123.2574 | 122.9279 | 122.8912 | -0.4715 | 123.2162 | 123.143 | 122.9782 | -0.4303
2785.6406 | 123.1064 | -122.9736 | 0.16937 | -0.22536 | 0.035939 | 0.01329 | 0.37998 | -0.075845 | -0.045447 | 0.03662 | -0.28349 | -0.011183 | -0.036666 | -0.068688 | 0.0056341 | 0.10457 | -0.022888 | 0.054932 | -0.054932 | 0.032043 | 0.27008 | -0.09613 | -0.25635 | -0.054932 | 0.022888 | -0.045776 | 0.21515 | 0.17395 | -0.21515 | -0.2655 | 122.8775 | 122.7173 | 0.10071 | 123.0286 | 123.0057 | 0.28839 | -0.19226 | 122.7585 | 122.7081 | 0.045776 | 122.9187 | 122.9279 | 0.21973 | 0.004577 | 123.2437 | 122.9507 | 122.9187 | -0.42572 | 123.1888 | 123.1476 | 122.9965 | -0.43488
2786.6406 | 123.143 | -122.9645 | 0.15564 | -0.25588 | 0.022053 | 0.017563 | 0.37143 | -0.058755 | -0.020881 | 0.023803 | -0.23772 | -0.0069114 | -0.033461 | -0.059075 | 0.0067021 | 0.10243 | 0.009155 | 0.10529 | -0.018311 | 0.064087 | 0.27008 | -0.091553 | -0.2655 | -0.009155 | 0.068665 | -0.018311 | 0.21057 | 0.16022 | -0.21057 | -0.2243 | 122.8729 | 122.699 | 0.11444 | 123.0698 | 123.0286 | 0.32959 | -0.14649 | 122.7539 | 122.7402 | 0.054931 | 122.9553 | 122.9462 | 0.20599 | 0.004577 | 123.2346 | 122.9736 | 122.9462 | -0.42114 | 123.175 | 123.1247 | 123.0331 | -0.37994
2787.6719 | 123.111 | -122.9736 | 0.16022 | 0.44602 | 0.044484 | 0.0068819 | 0.3757 | -0.071573 | 0.0047541 | 0.03662 | 0.26582 | 0.0080426 | -0.014235 | -0.063348 | 0.023792 | 0.10564 | -0.022888 | -0.027466 | -0.10986 | -0.004578 | 0.27466 | -0.09613 | -0.26093 | -0.027466 | -0.041199 | -0.091553 | 0.21057 | 0.16022 | -0.21057 | -0.24261 | 122.8775 | 122.7127 | 0.11444 | 122.9462 | 122.9691 | 0.25635 | -0.1831 | 122.7631 | 122.731 | 0.050354 | 122.9462 | 122.8821 | 0.15106 | 0 | 123.2483 | 122.9507 | 122.8638 | -0.42114 | 123.1842 | 123.1339 | 122.9324 | -0.40283
2788.6406 | 123.2208 | -122.937 | 0.12817 | -0.17959 | 0.0092362 | 0.019699 | 0.36289 | -0.0673 | -0.030494 | 0.028075 | -0.22246 | -0.01866 | -0.052687 | -0.064416 | 0.00029315 | 0.11632 | 0.018311 | 0.13733 | 0.013733 | 0.082397 | 0.23346 | -0.073242 | -0.25635 | 0.036621 | 0.12817 | 0.054932 | 0.19684 | 0.14191 | -0.1831 | -0.20142 | 122.8638 | 122.6807 | 0.10528 | 123.0743 | 123.0194 | 0.33875 | -0.10986 | 122.7539 | 122.7356 | 0.068664 | 122.9736 | 122.9919 | 0.25635 | 0.013733 | 123.1705 | 122.9553 | 122.9507 | -0.38452 | 123.1338 | 123.0789 | 123.0652 | -0.32959
2789.6406 | 123.1613 | -122.9645 | 0.16937 | -0.30166 | 0.020985 | -0.0016631 | 0.36395 | -0.060891 | -0.017676 | 0.034484 | -0.35979 | -0.0079794 | -0.055892 | -0.074029 | 0.0099061 | 0.10884 | -0.013733 | 0.11444 | -0.009155 | 0.073242 | 0.24719 | -0.086975 | -0.25635 | -0.013733 | 0.050354 | -0.004578 | 0.21057 | 0.14191 | -0.20142 | -0.2243 | 122.8775 | 122.7081 | 0.077819 | 123.0789 | 123.0377 | 0.32959 | -0.18311 | 122.7631 | 122.7402 | 0.041198 | 122.9507 | 122.9599 | 0.21973 | -0.027466 | 123.2117 | 122.9507 | 122.9553 | -0.42572 | 123.175 | 123.1064 | 123.0148 | -0.39368
2790.6406 | 123.2529 | -122.905 | 0.13733 | 0.11033 | 0.0092362 | 0.016495 | 0.36823 | -0.0673 | -0.035834 | 0.032347 | 0.15901 | -0.01866 | -0.048415 | -0.072961 | -0.0050469 | 0.10243 | 0.032043 | 0.13275 | 0.013733 | 0.082397 | 0.25177 | -0.068665 | -0.24719 | 0.10071 | 0.1236 | 0.091553 | 0.21057 | 0.13733 | -0.17395 | -0.19684 | 122.8363 | 122.6578 | 0.11444 | 123.0377 | 122.9874 | 0.32959 | -0.10529 | 122.731 | 122.7081 | 0.073242 | 123.0057 | 122.9965 | 0.28839 | 0 | 123.1567 | 122.937 | 122.9187 | -0.38452 | 123.1155 | 123.0423 | 123.0286 | -0.33417
2791.6406 | 123.1293 | -122.9736 | 0.17395 | 0.32395 | 0.050892 | -0.0027321 | 0.35327 | -0.058755 | 0.0047541 | 0.037688 | 0.097976 | -0.0026384 | -0.021712 | -0.055871 | 0.022724 | 0.097094 | -0.009155 | -0.054932 | -0.10986 | -0.018311 | 0.28381 | -0.10071 | -0.25635 | -0.018311 | -0.041199 | -0.10071 | 0.23346 | 0.17395 | -0.2243 | -0.23346 | 122.8729 | 122.7173 | 0.10986 | 122.9187 | 122.9553 | 0.23804 | -0.1831 | 122.7493 | 122.7402 | 0.059509 | 122.9553 | 122.8729 | 0.13275 | 0 | 123.2574 | 122.9645 | 122.8638 | -0.4303 | 123.2071 | 123.1476 | 122.9324 | -0.40741
2792.6406 | 123.2346 | -122.9004 | 0.13733 | -0.19484 | 0.016713 | 0.014358 | 0.35861 | -0.074777 | -0.043311 | 0.032347 | -0.29875 | -0.015456 | -0.024916 | -0.068688 | 0.0067021 | 0.10137 | 0.050354 | 0.14191 | 0.032043 | 0.07782 | 0.26093 | -0.091553 | -0.25177 | 0.064087 | 0.13275 | 0.041199 | 0.17395 | 0.13733 | -0.16937 | -0.20599 | 122.8088 | 122.6486 | 0.1236 | 123.0423 | 122.9782 | 0.32959 | -0.086975 | 122.731 | 122.6944 | 0.036621 | 122.9645 | 122.9416 | 0.24719 | 0 | 123.1613 | 122.9507 | 122.9324 | -0.3891 | 123.0743 | 123.0377 | 123.0331 | -0.34332
2793.6562 | 123.1384 | -122.9782 | 0.16479 | 0.3087 | 0.057301 | -0.0070041 | 0.36716 | -0.0673 | 0.014367 | 0.043029 | -0.23772 | 0.00056556 | -0.032393 | -0.06228 | 0.01311 | 0.096026 | 0.013733 | 0.032043 | -0.091553 | 0.041199 | 0.27924 | -0.10529 | -0.27008 | -0.018311 | 0 | -0.082397 | 0.23804 | 0.15564 | -0.21057 | -0.22888 | 122.8729 | 122.7081 | 0.11444 | 123.0103 | 123.0194 | 0.31128 | -0.15106 | 122.7676 | 122.7493 | 0.073242 | 122.9599 | 122.8958 | 0.14649 | -0.009155 | 123.2574 | 122.9919 | 122.8867 | -0.43488 | 123.2162 | 123.1339 | 122.9782 | -0.39368
2794.6406 | 123.2346 | -122.9416 | 0.13275 | -0.11855 | 0.0049632 | 0.0068819 | 0.35648 | -0.083322 | -0.045447 | 0.034484 | -0.2072 | -0.014388 | -0.050551 | -0.075097 | 0.0067021 | 0.10991 | 0.027466 | 0.15564 | 0.022888 | 0.073242 | 0.25177 | -0.07782 | -0.23346 | 0.064087 | 0.14648 | 0.064087 | 0.20142 | 0.13733 | -0.1831 | -0.21057 | 122.8638 | 122.7081 | 0.11902 | 123.0972 | 123.0148 | 0.3067 | -0.10529 | 122.7585 | 122.731 | 0.068665 | 123.0057 | 123.0057 | 0.27466 | 0.004578 | 123.1934 | 122.9691 | 122.9645 | -0.36621 | 123.143 | 123.0789 | 123.0881 | -0.34332
2795.6406 | 123.2483 | -122.9233 | 0.1236 | 0.034038 | 0.038075 | 0.0090179 | 0.35648 | -0.079049 | -0.029426 | 0.034484 | -0.2072 | -0.014388 | -0.044143 | -0.049462 | 0.0099061 | 0.10243 | 0.068665 | 0.19226 | 0.064087 | 0.10071 | 0.25177 | -0.091553 | -0.23346 | 0.050354 | 0.15564 | 0.086975 | 0.1831 | 0.13733 | -0.17853 | -0.21057 | 122.8317 | 122.6898 | 0.12817 | 123.1155 | 123.024 | 0.33417 | -0.054931 | 122.7448 | 122.7127 | 0.059509 | 122.9736 | 123.0103 | 0.29755 | 0.013733 | 123.175 | 122.9919 | 122.9874 | -0.35706 | 123.1064 | 123.0606 | 123.0789 | -0.33417

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.4333 | 25.4501 | 25.8459 | 26.0561
0.5667 | 25.4461 | 25.8429 | 26.0541
1.5667 | 25.4528 | 25.8226 | 26.0526
2.5667 | 25.5597 | 25.8308 | 26.0477
3.5667 | 26.1768 | 25.8293 | 26.0476
4.5667 | 27.4934 | 25.8386 | 26.0505
5.5667 | 29.5209 | 25.8311 | 26.0499
6.5667 | 32.1233 | 25.8318 | 26.047
7.5667 | 35.1996 | 25.8342 | 26.0485
8.5667 | 38.7186 | 25.8323 | 26.0515
9.5667 | 42.5772 | 25.8452 | 26.0564
10.5667 | 46.7136 | 25.8493 | 26.0579
11.5667 | 51.1154 | 25.8538 | 26.0659
12.5667 | 55.7416 | 25.8638 | 26.0837
13.5667 | 60.5441 | 25.8751 | 26.1038
14.5667 | 65.4968 | 25.8932 | 26.1134
15.5667 | 70.6204 | 25.9224 | 26.1445
16.5667 | 75.911 | 25.9405 | 26.1644
17.5667 | 81.2754 | 25.9786 | 26.2077
18.5667 | 86.7759 | 26.0181 | 26.2458
19.5667 | 92.3604 | 26.0526 | 26.2935
20.5667 | 98.1108 | 26.0949 | 26.3485
21.5667 | 103.8936 | 26.1556 | 26.4097
22.5667 | 109.6842 | 26.2197 | 26.4663
23.5667 | 115.5465 | 26.2846 | 26.5413
24.5667 | 121.4552 | 26.3647 | 26.6212
25.5667 | 127.398 | 26.4405 | 26.7141
26.5667 | 133.3521 | 26.5429 | 26.8118
27.5667 | 139.4433 | 26.6435 | 26.9221
28.5667 | 145.5071 | 26.7436 | 27.0396
29.5667 | 151.5139 | 26.8564 | 27.1696
30.5667 | 157.5734 | 26.998 | 27.3119
31.5667 | 163.6049 | 27.1209 | 27.4616
32.5667 | 169.5453 | 27.26 | 27.6363
33.5667 | 175.5217 | 27.4152 | 27.7995
34.5667 | 181.463 | 27.5909 | 27.9902
35.5667 | 187.4175 | 27.7569 | 28.1948
36.5667 | 193.3429 | 27.9409 | 28.4157
37.5667 | 199.271 | 28.1371 | 28.6412
38.5667 | 205.0881 | 28.3471 | 28.8797
39.5667 | 211.0033 | 28.5643 | 29.1377
40.5667 | 216.861 | 28.8017 | 29.3972
41.5667 | 222.7158 | 29.0454 | 29.6706
42.5667 | 228.5977 | 29.3039 | 29.9699
43.5667 | 234.4156 | 29.5815 | 30.2682
44.5667 | 240.1778 | 29.8648 | 30.5874
45.5667 | 245.9061 | 30.1587 | 30.9368
46.5667 | 251.724 | 30.4685 | 31.2896
47.5667 | 257.6237 | 30.7939 | 31.6489
48.5667 | 263.525 | 31.1524 | 32.0361
49.5667 | 269.3649 | 31.5016 | 32.4302
50.5667 | 275.0498 | 31.8718 | 32.8477
51.5667 | 280.7426 | 32.2556 | 33.2766
52.5667 | 286.3931 | 32.6508 | 33.7235
53.5667 | 291.9888 | 33.0484 | 34.1887
54.5667 | 297.2651 | 33.4628 | 34.6593
55.5667 | 302.0678 | 33.9061 | 35.1579
56.5667 | 306.4805 | 34.3418 | 35.6589
57.5667 | 310.6151 | 34.7986 | 36.1808
58.5667 | 314.5136 | 35.2821 | 36.7249
59.5667 | 318.2022 | 35.7673 | 37.272
60.5667 | 321.7143 | 36.2643 | 37.8341
61.5667 | 324.8742 | 36.764 | 38.4011
62.5667 | 327.942 | 37.2832 | 38.9776
63.5667 | 330.573 | 37.8195 | 39.5603
64.5667 | 332.8781 | 38.3562 | 40.1707
65.5667 | 334.9369 | 38.8963 | 40.7917
66.5667 | 336.495 | 39.4605 | 41.407
67.5667 | 337.6019 | 40.019 | 42.0383
68.5667 | 338.6072 | 40.5983 | 42.6727
69.5667 | 339.5495 | 41.1715 | 43.313
70.5667 | 340.2527 | 41.75 | 43.9665
71.5667 | 340.6924 | 42.3308 | 44.6113
72.5667 | 340.9754 | 42.9197 | 45.2483
73.5667 | 341.1824 | 43.5016 | 45.8871
74.5667 | 341.4064 | 44.0998 | 46.5279
75.5667 | 341.4383 | 44.6993 | 47.1722
76.5667 | 341.2746 | 45.294 | 47.8195
77.5667 | 341.1486 | 45.8899 | 48.4639
78.5667 | 340.8934 | 46.494 | 49.1111
79.5667 | 340.6659 | 47.105 | 49.7492
80.5667 | 340.2979 | 47.7012 | 50.4033
81.5667 | 339.8333 | 48.3071 | 51.0384
82.5667 | 339.5133 | 48.9171 | 51.6734
83.5667 | 339.2052 | 49.5161 | 52.3127
84.5667 | 338.7535 | 50.138 | 52.9418
85.5667 | 338.4932 | 50.7301 | 53.568
86.5667 | 338.124 | 51.3216 | 54.192
87.5667 | 337.702 | 51.9285 | 54.8122
88.5667 | 337.3858 | 52.5165 | 55.4321
89.5667 | 336.9524 | 53.111 | 56.0464
90.5667 | 336.507 | 53.7101 | 56.6649
91.5667 | 336.0989 | 54.2823 | 57.2705
92.5667 | 335.643 | 54.8654 | 57.8822
93.5667 | 335.0727 | 55.4473 | 58.4824
94.5667 | 334.6152 | 56.0187 | 59.0879
95.5667 | 334.1703 | 56.5925 | 59.6959
96.5667 | 333.6405 | 57.1483 | 60.294
97.5667 | 333.0416 | 57.7141 | 60.8837
98.5667 | 332.4461 | 58.2764 | 61.4726
99.5667 | 331.9173 | 58.8377 | 62.0534
100.5667 | 331.5206 | 59.4038 | 62.6358
101.5667 | 330.9366 | 59.945 | 63.2102
102.5667 | 330.27 | 60.4877 | 63.7855
103.5667 | 329.7407 | 61.0197 | 64.339
104.5667 | 329.2218 | 61.5499 | 64.8894
105.5667 | 328.7358 | 62.0701 | 65.4431
106.5667 | 328.2764 | 62.6047 | 65.9852
107.5667 | 327.7076 | 63.109 | 66.5197
108.5667 | 327.172 | 63.6236 | 67.0495
109.5667 | 326.6992 | 64.1094 | 67.5783
110.5667 | 326.2395 | 64.6112 | 68.0978
111.5667 | 325.7513 | 65.0979 | 68.6181
112.5667 | 325.3468 | 65.5943 | 69.1331
113.5667 | 324.7727 | 66.0796 | 69.6402
114.5667 | 324.2723 | 66.5579 | 70.1484
115.5667 | 323.7348 | 67.0385 | 70.6497
116.5667 | 323.3363 | 67.5143 | 71.147
117.5667 | 323.0233 | 67.9755 | 71.6383
118.5667 | 322.77 | 68.4338 | 72.1188
119.5667 | 322.6125 | 68.9157 | 72.6099
120.5667 | 322.4461 | 69.3786 | 73.0924
121.5667 | 322.282 | 69.8328 | 73.5719
122.5667 | 322.1549 | 70.2898 | 74.049
123.5667 | 322.2573 | 70.7362 | 74.515
124.5667 | 322.3351 | 71.1885 | 74.9879
125.5667 | 322.3831 | 71.6336 | 75.4556
126.5667 | 322.604 | 72.0734 | 75.9236
127.5667 | 322.865 | 72.5239 | 76.3846
128.5667 | 323.0397 | 72.9598 | 76.8418
129.5667 | 323.3098 | 73.4059 | 77.3018
130.5667 | 323.6338 | 73.8355 | 77.7621
131.5667 | 324.0884 | 74.2692 | 78.2266
132.5667 | 324.5224 | 74.7062 | 78.6834
133.5667 | 324.8341 | 75.1358 | 79.1381
134.5667 | 325.244 | 75.5764 | 79.5974
135.5667 | 325.7305 | 76.0091 | 80.0479
136.5667 | 326.2455 | 76.4375 | 80.5033
137.5667 | 326.5978 | 76.8717 | 80.9489
138.5667 | 327.0076 | 77.2963 | 81.4136
139.5667 | 327.4491 | 77.7367 | 81.8623
140.5667 | 328.0291 | 78.17 | 82.3192
141.5667 | 328.4375 | 78.6087 | 82.773
142.5667 | 328.8633 | 79.0476 | 83.2276
143.5667 | 329.2301 | 79.4726 | 83.6783
144.5667 | 329.6867 | 79.9107 | 84.135
145.5667 | 330.1578 | 80.3435 | 84.5988
146.5667 | 330.5694 | 80.7826 | 85.0587
147.5667 | 330.9371 | 81.2161 | 85.5227
148.5667 | 331.3079 | 81.661 | 85.9801
149.5667 | 331.5598 | 82.093 | 86.4433
150.5667 | 331.7497 | 82.5324 | 86.9013
151.5667 | 332.0031 | 82.9724 | 87.3691
152.5667 | 332.2587 | 83.4045 | 87.8322
153.5667 | 332.4252 | 83.8488 | 88.2963
154.5667 | 332.518 | 84.2738 | 88.754
155.5667 | 332.6091 | 84.7257 | 89.2044
156.5667 | 332.744 | 85.1537 | 89.6615
157.5667 | 332.8239 | 85.5872 | 90.1141
158.5667 | 332.9776 | 86.0219 | 90.5619
159.5667 | 333.1063 | 86.4436 | 91.0039
160.5667 | 333.0961 | 86.8856 | 91.4531
161.5667 | 333.068 | 87.305 | 91.9004
162.5667 | 333.1168 | 87.7479 | 92.3442
163.5667 | 333.132 | 88.1764 | 92.7898
164.5667 | 333.0878 | 88.5932 | 93.2311
165.5667 | 333.0685 | 89.0318 | 93.6763
166.5667 | 333.0888 | 89.4567 | 94.1146
167.5667 | 333.0754 | 89.8737 | 94.5504
168.5667 | 332.9726 | 90.2942 | 94.9911
169.5667 | 332.7934 | 90.7242 | 95.423
170.5667 | 332.6409 | 91.144 | 95.8659
171.5667 | 332.572 | 91.5597 | 96.2976
172.5667 | 332.6166 | 91.9706 | 96.7299
173.5667 | 332.5251 | 92.3908 | 97.1764
174.5667 | 332.3901 | 92.7986 | 97.6021
175.5667 | 332.3318 | 93.2098 | 98.0313
176.5667 | 332.2623 | 93.6277 | 98.456
177.5667 | 332.2678 | 94.0241 | 98.8866
178.5667 | 332.3211 | 94.4371 | 99.305
179.5667 | 332.3195 | 94.8294 | 99.7291
180.5667 | 332.3113 | 95.2385 | 100.1529
181.5667 | 332.2716 | 95.6366 | 100.5688
182.5667 | 332.1818 | 96.0404 | 100.9885
183.5667 | 332.2541 | 96.4349 | 101.4023
184.5667 | 332.1678 | 96.8369 | 101.8247
185.5667 | 332.1735 | 97.2448 | 102.2289
186.5667 | 332.1483 | 97.6358 | 102.6438
187.5667 | 332.0489 | 98.0306 | 103.0532
188.5667 | 331.9153 | 98.4141 | 103.4629
189.5667 | 331.9509 | 98.7919 | 103.8696
190.5667 | 331.9497 | 99.1825 | 104.2796
191.5667 | 331.9406 | 99.5613 | 104.6807
192.5667 | 331.894 | 99.949 | 105.0852
193.5667 | 331.8677 | 100.3203 | 105.4777
194.5667 | 331.8556 | 100.7079 | 105.8829
195.5667 | 331.7855 | 101.0722 | 106.2744
196.5667 | 331.6942 | 101.451 | 106.6799
197.5667 | 331.7874 | 101.8266 | 107.0848
198.5667 | 331.8024 | 102.198 | 107.4774
199.5667 | 331.9096 | 102.568 | 107.8607
200.5667 | 331.9187 | 102.9427 | 108.259
201.5667 | 331.9193 | 103.3163 | 108.6436
202.5667 | 331.913 | 103.6838 | 109.0298
203.5667 | 331.879 | 104.0471 | 109.4102
204.5667 | 331.955 | 104.4102 | 109.8001
205.5667 | 332.0226 | 104.7838 | 110.1781
206.5667 | 332.0377 | 105.145 | 110.5633
207.5667 | 332.0591 | 105.5095 | 110.9501
208.5667 | 332.1081 | 105.871 | 111.3245
209.5667 | 332.181 | 106.2376 | 111.6975
210.5667 | 332.2814 | 106.599 | 112.0752
211.5667 | 332.3229 | 106.9562 | 112.4518
212.5667 | 332.2739 | 107.312 | 112.8264
213.5667 | 332.3211 | 107.6672 | 113.1992
214.5667 | 332.3254 | 107.9944 | 113.5654
215.5667 | 332.2473 | 108.3353 | 113.9401
216.5667 | 332.234 | 108.6771 | 114.2993
217.5667 | 332.2518 | 109.0192 | 114.6688
218.5667 | 332.2667 | 109.366 | 115.0386
219.5667 | 332.2865 | 109.7188 | 115.3986
220.5667 | 332.3233 | 110.061 | 115.7578
221.5667 | 332.372 | 110.4058 | 116.134
222.5667 | 332.4591 | 110.7557 | 116.4983
223.5667 | 332.4704 | 111.1074 | 116.854
224.5667 | 332.3811 | 111.437 | 117.2129
225.5667 | 332.3868 | 111.788 | 117.5665
226.5667 | 332.5716 | 112.1296 | 117.9177
227.5667 | 332.5238 | 112.465 | 118.277
228.5667 | 332.5127 | 112.8108 | 118.6219
229.5667 | 332.5921 | 113.1341 | 118.9727
230.5667 | 332.672 | 113.4715 | 119.3127
231.5667 | 332.7026 | 113.804 | 119.6673
232.5667 | 332.6204 | 114.1311 | 120.008
233.5667 | 332.5602 | 114.4598 | 120.3574
234.5667 | 332.5107 | 114.7828 | 120.6967
235.5667 | 332.418 | 115.1099 | 121.0292
236.5667 | 332.3022 | 115.4379 | 121.372
237.5667 | 332.2692 | 115.7548 | 121.7048
238.5667 | 332.3276 | 116.0746 | 122.0379
239.5667 | 332.3106 | 116.3978 | 122.3755
240.5667 | 332.2696 | 116.7194 | 122.7083
241.5667 | 332.1786 | 117.0328 | 123.0296
242.5667 | 332.0599 | 117.3511 | 123.3516
243.5667 | 332.0605 | 117.6494 | 123.6765
244.5667 | 332.081 | 117.9627 | 124.0062
245.5667 | 332.1586 | 118.2757 | 124.3287
246.5667 | 332.1149 | 118.5764 | 124.6405
247.5667 | 332.0176 | 118.8905 | 124.9626
248.5667 | 331.9828 | 119.196 | 125.2746
249.5667 | 332.006 | 119.4847 | 125.6021
250.5667 | 332.0304 | 119.8035 | 125.9147
251.5667 | 331.8765 | 120.0907 | 126.224
252.5667 | 331.7354 | 120.3894 | 126.53
253.5667 | 331.6522 | 120.6823 | 126.8332
254.5667 | 331.6382 | 120.9847 | 127.1258
255.5667 | 331.5881 | 121.2566 | 127.424
256.5667 | 331.4868 | 121.5599 | 127.7168
257.5667 | 331.2951 | 121.8131 | 128.0055
258.5667 | 331.2605 | 122.0945 | 128.3008
259.5667 | 331.1483 | 122.3765 | 128.585
260.5667 | 331.0132 | 122.6528 | 128.8651
261.5667 | 330.9592 | 122.9456 | 129.1447
262.5667 | 330.843 | 123.2158 | 129.4241
263.5667 | 330.8297 | 123.5004 | 129.6962
264.5667 | 330.8799 | 123.7849 | 129.9748
265.5667 | 330.8946 | 124.056 | 130.2521
266.5667 | 330.8095 | 124.3333 | 130.5257
267.5667 | 330.7919 | 124.6197 | 130.7963
268.5667 | 330.6772 | 124.9084 | 131.0726
269.5667 | 330.6367 | 125.1836 | 131.35
270.5667 | 330.6732 | 125.4518 | 131.6365
271.5667 | 330.7612 | 125.7327 | 131.9189
272.5667 | 330.7922 | 126.0171 | 132.2041
273.5667 | 330.7861 | 126.2943 | 132.4959
274.5667 | 330.7497 | 126.5735 | 132.7879
275.5667 | 330.6361 | 126.8526 | 133.0781
276.5667 | 330.7145 | 127.1293 | 133.3697
277.5667 | 330.7828 | 127.4128 | 133.674
278.5667 | 330.917 | 127.6865 | 133.9778
279.5667 | 330.9917 | 127.9655 | 134.2794
280.5667 | 330.941 | 128.2552 | 134.5923
281.5667 | 330.9801 | 128.5428 | 134.9098
282.5667 | 331.0076 | 128.8309 | 135.2267
283.5667 | 330.9467 | 129.1259 | 135.5393
284.5667 | 330.9939 | 129.4112 | 135.855
285.5667 | 331.0206 | 129.7021 | 136.1821
286.5667 | 331.0575 | 130.0067 | 136.5097
287.5667 | 331.0637 | 130.3038 | 136.8352
288.5667 | 331.1003 | 130.5995 | 137.1606
289.5667 | 331.1752 | 130.9105 | 137.487
290.5667 | 331.2353 | 131.2098 | 137.8222
291.5667 | 331.3215 | 131.5229 | 138.1593
292.5667 | 331.3785 | 131.8383 | 138.4926
293.5667 | 331.3397 | 132.1489 | 138.8375
294.5667 | 331.2614 | 132.4649 | 139.1669
295.5667 | 331.1987 | 132.7777 | 139.5084
296.5667 | 331.25 | 133.0988 | 139.8437
297.5667 | 331.1909 | 133.4273 | 140.1791
298.5667 | 331.283 | 133.74 | 140.5174
299.5667 | 331.2937 | 134.0656 | 140.8621
300.5667 | 331.2471 | 134.3878 | 141.2008
301.5667 | 331.2571 | 134.7186 | 141.5491
302.5667 | 331.325 | 135.0502 | 141.8888
303.5667 | 331.4632 | 135.3842 | 142.2349
304.5667 | 331.4778 | 135.7143 | 142.5813
305.5667 | 331.4454 | 136.0546 | 142.9229
306.5667 | 331.5627 | 136.3786 | 143.2724
307.5667 | 331.5979 | 136.7201 | 143.615
308.5667 | 331.5946 | 137.0434 | 143.9606
309.5667 | 331.5352 | 137.3783 | 144.3065
310.5667 | 331.3974 | 137.7049 | 144.6467
311.5667 | 331.3703 | 138.0384 | 145.0078
312.5667 | 331.4044 | 138.3777 | 145.3417
313.5667 | 331.4103 | 138.7047 | 145.6802
314.5667 | 331.3575 | 139.0286 | 146.0282
315.5667 | 331.2685 | 139.3619 | 146.3769
316.5667 | 331.1918 | 139.692 | 146.7138
317.5667 | 331.2374 | 140.007 | 147.0577
318.5667 | 331.2937 | 140.3316 | 147.3972
319.5667 | 331.3766 | 140.6613 | 147.7378
320.5667 | 331.3376 | 140.9897 | 148.0758
321.5667 | 331.2407 | 141.3072 | 148.4156
322.5667 | 331.1595 | 141.6269 | 148.7463
323.5667 | 331.0827 | 141.9518 | 149.0842
324.5667 | 330.945 | 142.2723 | 149.4185
325.5667 | 330.8142 | 142.5793 | 149.7581
326.5667 | 330.8571 | 142.9107 | 150.0875
327.5667 | 330.7476 | 143.2208 | 150.4212
328.5667 | 330.572 | 143.5375 | 150.7512
329.5667 | 330.6343 | 143.8575 | 151.0802
330.5667 | 330.6492 | 144.1678 | 151.4106
331.5667 | 330.5494 | 144.4833 | 151.733
332.5667 | 330.5126 | 144.8013 | 152.0679
333.5667 | 330.4365 | 145.1088 | 152.3987
334.5667 | 330.4085 | 145.4284 | 152.7215
335.5667 | 330.3137 | 145.7349 | 153.0502
336.5667 | 330.2455 | 146.0436 | 153.372
337.5667 | 330.2179 | 146.3553 | 153.6996
338.5667 | 330.1153 | 146.6559 | 154.0242
339.5667 | 329.9942 | 146.9705 | 154.3431
340.5667 | 329.9326 | 147.2726 | 154.6841
341.5667 | 329.8566 | 147.5837 | 155.0113
342.5667 | 329.7804 | 147.8881 | 155.326
343.5667 | 329.6816 | 148.1983 | 155.6504
344.5667 | 329.6057 | 148.4967 | 155.9718
345.5667 | 329.5949 | 148.8008 | 156.2946
346.5667 | 329.5951 | 149.0959 | 156.6082
347.5667 | 329.6996 | 149.4049 | 156.929
348.5667 | 329.63 | 149.7035 | 157.2489
349.5667 | 329.6585 | 149.9961 | 157.563
350.5667 | 329.6416 | 150.3032 | 157.881
351.5667 | 329.5634 | 150.5962 | 158.2007
352.5667 | 329.5378 | 150.8952 | 158.5161
353.5667 | 329.6214 | 151.1838 | 158.825
354.5667 | 329.8033 | 151.4842 | 159.1426
355.5667 | 329.8292 | 151.7826 | 159.4469
356.5667 | 329.9056 | 152.0701 | 159.7677
357.5667 | 329.9474 | 152.3672 | 160.078
358.5667 | 329.991 | 152.6704 | 160.3966
359.5667 | 330.0972 | 152.9618 | 160.7082
360.6135 | 330.0837 | 153.2698 | 161.0387
361.5667 | 330.1389 | 153.5549 | 161.3382
362.5667 | 330.2207 | 153.8399 | 161.6444
363.5667 | 330.2101 | 154.1292 | 161.9589
364.5667 | 330.2313 | 154.4251 | 162.2652
365.5667 | 330.2752 | 154.7245 | 162.5774
366.5667 | 330.3403 | 155.0197 | 162.8853
367.5667 | 330.4843 | 155.3179 | 163.1903
368.5667 | 330.6392 | 155.5983 | 163.5007
369.5667 | 330.7867 | 155.8898 | 163.8164
370.5667 | 330.8187 | 156.1864 | 164.1204
371.5667 | 330.7541 | 156.4643 | 164.4414
372.5667 | 330.7778 | 156.7637 | 164.752
373.5667 | 330.7626 | 157.049 | 165.0589
374.5667 | 330.7427 | 157.3357 | 165.3701
375.5667 | 330.7538 | 157.6179 | 165.6712
376.5667 | 330.7327 | 157.9061 | 165.9839
377.5667 | 330.7355 | 158.2005 | 166.2871
378.5667 | 330.6778 | 158.4822 | 166.594
379.5667 | 330.6018 | 158.7649 | 166.9071
380.5667 | 330.5704 | 159.0534 | 167.2046
381.5667 | 330.4648 | 159.3322 | 167.5088
382.5667 | 330.544 | 159.6172 | 167.8147
383.5667 | 330.5675 | 159.9101 | 168.1128
384.5667 | 330.5766 | 160.18 | 168.4195
385.5667 | 330.5271 | 160.4675 | 168.7227
386.5667 | 330.4777 | 160.7488 | 169.0276
387.5667 | 330.4498 | 161.0248 | 169.3238
388.5667 | 330.4311 | 161.305 | 169.6303
389.5667 | 330.4137 | 161.5857 | 169.9278
390.5667 | 330.4366 | 161.8594 | 170.2331
391.5667 | 330.4653 | 162.1384 | 170.5332
392.5667 | 330.44 | 162.419 | 170.8279
393.5667 | 330.4113 | 162.6863 | 171.1179
394.5667 | 330.3356 | 162.9655 | 171.4196
395.5667 | 330.3772 | 163.2372 | 171.7188
396.5667 | 330.2845 | 163.5113 | 172.0179
397.5667 | 330.1942 | 163.789 | 172.3052
398.5667 | 330.1463 | 164.0594 | 172.5993
399.5667 | 330.0561 | 164.3461 | 172.898
400.5667 | 329.9995 | 164.6065 | 173.1944
401.5667 | 329.9899 | 164.8866 | 173.4829
402.5667 | 329.8814 | 165.1608 | 173.7831
403.5667 | 329.8873 | 165.4312 | 174.0916
404.5667 | 329.8432 | 165.696 | 174.3805
405.5667 | 329.7714 | 165.9709 | 174.6747
406.5667 | 329.7745 | 166.239 | 174.9734
407.5667 | 329.7638 | 166.5081 | 175.2646
408.5667 | 329.7507 | 166.7725 | 175.5536
409.5667 | 329.8522 | 167.0407 | 175.8389
410.5667 | 329.8976 | 167.2978 | 176.1338
411.5667 | 329.8184 | 167.5681 | 176.4194
412.5667 | 329.8478 | 167.8386 | 176.7091
413.5667 | 329.9891 | 168.0968 | 176.9863
414.5667 | 330.0691 | 168.3561 | 177.2687
415.5667 | 330.0494 | 168.6071 | 177.5537
416.5667 | 330.0521 | 168.8801 | 177.8359
417.5667 | 330.1022 | 169.133 | 178.124
418.5667 | 330.0854 | 169.4034 | 178.3966
419.5667 | 330.1719 | 169.6632 | 178.6783
420.5667 | 330.2151 | 169.9136 | 178.9627
421.5667 | 330.2033 | 170.1671 | 179.2344
422.5667 | 330.2832 | 170.422 | 179.5116
423.5667 | 330.3243 | 170.6929 | 179.7824
424.5667 | 330.2157 | 170.9535 | 180.0564
425.5667 | 330.2154 | 171.2035 | 180.327
426.5667 | 330.2047 | 171.467 | 180.5994
427.5667 | 330.2204 | 171.7302 | 180.8708
428.5667 | 330.2032 | 171.9777 | 181.1314
429.5667 | 330.1844 | 172.2434 | 181.397
430.5667 | 330.0951 | 172.4989 | 181.6682
431.5667 | 330.0362 | 172.76 | 181.932
432.5667 | 330.0212 | 173.0072 | 182.1909
433.5667 | 330.0213 | 173.2701 | 182.4531
434.5667 | 329.9858 | 173.5207 | 182.7211
435.5667 | 329.8681 | 173.786 | 182.9803
436.5667 | 329.8446 | 174.0457 | 183.2487
437.5667 | 329.8409 | 174.3073 | 183.5036
438.5667 | 329.7747 | 174.5556 | 183.7638
439.5667 | 329.7847 | 174.8185 | 184.0258
440.5667 | 329.7772 | 175.0654 | 184.2824
441.5667 | 329.583 | 175.3186 | 184.533
442.5667 | 329.5208 | 175.5585 | 184.7919
443.5667 | 329.4602 | 175.8219 | 185.0359
444.5667 | 329.4265 | 176.0644 | 185.2793
445.5667 | 329.3569 | 176.3176 | 185.5334
446.5667 | 329.3181 | 176.5659 | 185.7765
447.5667 | 329.2762 | 176.808 | 186.0217
448.5667 | 329.1562 | 177.0572 | 186.261
449.5667 | 329.1586 | 177.3041 | 186.5011
450.5667 | 329.0767 | 177.5526 | 186.7471
451.5667 | 329.0654 | 177.7971 | 186.9831
452.5667 | 329.13 | 178.0375 | 187.2267
453.5667 | 329.1775 | 178.2867 | 187.4632
454.5667 | 329.2185 | 178.5296 | 187.699
455.5667 | 329.2024 | 178.7761 | 187.9356
456.5667 | 329.2105 | 179.0276 | 188.1762
457.5667 | 329.2066 | 179.2541 | 188.4133
458.5667 | 329.3209 | 179.5119 | 188.6439
459.5667 | 329.4171 | 179.7401 | 188.8808
460.5667 | 329.4819 | 179.9784 | 189.1139
461.5667 | 329.5285 | 180.2251 | 189.3471
462.5667 | 329.5881 | 180.4666 | 189.5807
463.5667 | 329.5728 | 180.7117 | 189.8109
464.5667 | 329.4973 | 180.9573 | 190.0419
465.5667 | 329.4728 | 181.191 | 190.2742
466.5667 | 329.5052 | 181.4242 | 190.5043
467.5667 | 329.4558 | 181.666 | 190.7366
468.5667 | 329.4063 | 181.9082 | 190.9547
469.5667 | 329.2981 | 182.1348 | 191.1916
470.5667 | 329.3167 | 182.3783 | 191.4079
471.5667 | 329.273 | 182.6114 | 191.6446
472.5667 | 329.187 | 182.8493 | 191.867
473.5667 | 329.1867 | 183.0825 | 192.0863
474.5667 | 329.162 | 183.3146 | 192.3062
475.5667 | 329.1907 | 183.5439 | 192.5407
476.5667 | 329.3398 | 183.7919 | 192.7758
477.5667 | 329.3537 | 184.0427 | 192.9921
478.5667 | 329.3532 | 184.2745 | 193.2175
479.5667 | 329.3799 | 184.5048 | 193.4368
480.5667 | 329.4617 | 184.7385 | 193.674
481.5667 | 329.541 | 184.9712 | 193.9018
482.5667 | 329.4538 | 185.2 | 194.1256
483.5667 | 329.4576 | 185.4276 | 194.3483
484.5667 | 329.5537 | 185.67 | 194.5699
485.5667 | 329.5114 | 185.8928 | 194.7872
486.5667 | 329.5154 | 186.1262 | 195.0162
487.5667 | 329.6125 | 186.3535 | 195.2381
488.5667 | 329.6412 | 186.594 | 195.4616
489.5667 | 329.6259 | 186.8331 | 195.6815
490.5667 | 329.6751 | 187.042 | 195.908
491.5667 | 329.5736 | 187.2929 | 196.1312
492.5667 | 329.568 | 187.5205 | 196.3598
493.5667 | 329.7198 | 187.746 | 196.5807
494.5667 | 329.8364 | 187.9781 | 196.8089
495.5667 | 329.8064 | 188.2106 | 197.0279
496.5667 | 329.8218 | 188.4364 | 197.2463
497.5667 | 329.8667 | 188.6695 | 197.474
498.5667 | 330.0089 | 188.8928 | 197.7008
499.5667 | 330.0394 | 189.1261 | 197.9168
500.5667 | 329.9269 | 189.3579 | 198.1434
501.5667 | 329.8871 | 189.5782 | 198.3574
502.5667 | 329.9111 | 189.8065 | 198.5805
503.5667 | 329.9168 | 190.0365 | 198.7963
504.5667 | 329.8953 | 190.2618 | 199.0169
505.5667 | 329.8581 | 190.4948 | 199.2361
506.5667 | 329.8289 | 190.7212 | 199.4502
507.5667 | 329.8144 | 190.9516 | 199.6761
508.5667 | 329.8881 | 191.1744 | 199.8952
509.5667 | 329.8934 | 191.4015 | 200.1175
510.5667 | 329.7992 | 191.612 | 200.3365
511.5667 | 329.6881 | 191.8517 | 200.5492
512.5667 | 329.7836 | 192.0779 | 200.7665
513.5667 | 329.9066 | 192.295 | 200.9886
514.5667 | 329.936 | 192.5229 | 201.2041
515.5667 | 329.8561 | 192.7441 | 201.4246
516.5667 | 329.8679 | 192.9687 | 201.6338
517.5667 | 329.9539 | 193.1893 | 201.8572
518.5667 | 329.9936 | 193.4054 | 202.0664
519.5667 | 329.9847 | 193.6427 | 202.2913
520.5667 | 329.971 | 193.8634 | 202.5059
521.5667 | 329.8825 | 194.0925 | 202.7199
522.5667 | 329.8317 | 194.3065 | 202.9306
523.5667 | 329.7455 | 194.524 | 203.1557
524.5667 | 329.7735 | 194.7496 | 203.3737
525.5667 | 329.7064 | 194.9688 | 203.5932
526.5667 | 329.5969 | 195.183 | 203.8102
527.5667 | 329.5146 | 195.3988 | 204.015
528.5667 | 329.3891 | 195.6074 | 204.2305
529.5667 | 329.4312 | 195.8325 | 204.4458
530.5667 | 329.3238 | 196.0452 | 204.6682
531.5667 | 329.2803 | 196.2589 | 204.8765
532.5667 | 329.3759 | 196.4729 | 205.0835
533.5667 | 329.4299 | 196.6787 | 205.296
534.5667 | 329.4564 | 196.9028 | 205.5091
535.5667 | 329.5023 | 197.1119 | 205.715
536.5667 | 329.4743 | 197.3302 | 205.9282
537.5667 | 329.3075 | 197.5428 | 206.1327
538.5667 | 329.1935 | 197.749 | 206.3313
539.5667 | 329.0015 | 197.962 | 206.5412
540.5667 | 328.9217 | 198.1696 | 206.7481
541.5667 | 328.8966 | 198.3871 | 206.9525
542.5667 | 328.8108 | 198.587 | 207.1636
543.5667 | 328.7002 | 198.8108 | 207.3597
544.5667 | 328.7128 | 199.018 | 207.5708
545.5667 | 328.7005 | 199.2277 | 207.7697
546.5667 | 328.7055 | 199.4507 | 207.9824
547.5667 | 328.7515 | 199.6512 | 208.1769
548.5667 | 328.7004 | 199.8595 | 208.3808
549.5667 | 328.5964 | 200.0679 | 208.5818
550.5667 | 328.5735 | 200.2848 | 208.7827
551.5667 | 328.506 | 200.4861 | 208.9786
552.5667 | 328.445 | 200.701 | 209.1727
553.5667 | 328.4753 | 200.9056 | 209.3654
554.5667 | 328.4671 | 201.1313 | 209.559
555.5667 | 328.4159 | 201.3292 | 209.7459
556.5667 | 328.362 | 201.5432 | 209.9429
557.5667 | 328.3534 | 201.7513 | 210.1331
558.5667 | 328.3787 | 201.9724 | 210.3248
559.5667 | 328.4657 | 202.1803 | 210.5098
560.5667 | 328.5797 | 202.3907 | 210.695
561.5667 | 328.7389 | 202.5985 | 210.8824
562.5667 | 328.8158 | 202.813 | 211.0764
563.5667 | 328.8433 | 203.0214 | 211.2683
564.5667 | 328.8297 | 203.2314 | 211.4655
565.5667 | 328.8025 | 203.4579 | 211.6629
566.5667 | 328.8635 | 203.6733 | 211.8584
567.5667 | 328.9109 | 203.8717 | 212.047
568.5667 | 329.0522 | 204.0878 | 212.2436
569.5667 | 329.0639 | 204.2943 | 212.4398
570.5667 | 329.1072 | 204.5012 | 212.6423
571.5667 | 329.11 | 204.7099 | 212.8499
572.5667 | 329.1345 | 204.9191 | 213.0513
573.5667 | 329.2349 | 205.1196 | 213.2702
574.5667 | 329.2175 | 205.3227 | 213.4772
575.5667 | 329.2135 | 205.5411 | 213.6745
576.5667 | 329.1855 | 205.7371 | 213.884
577.5667 | 329.221 | 205.9478 | 214.0908
578.5667 | 329.2419 | 206.143 | 214.2958
579.5667 | 329.313 | 206.3411 | 214.4951
580.5667 | 329.4384 | 206.5407 | 214.7062
581.5667 | 329.6139 | 206.7334 | 214.9018
582.5667 | 329.6733 | 206.9294 | 215.1092
583.5667 | 329.6079 | 207.1317 | 215.3118
584.5667 | 329.6106 | 207.3362 | 215.5211
585.5667 | 329.6536 | 207.5137 | 215.7147
586.5667 | 329.664 | 207.72 | 215.9177
587.5667 | 329.6691 | 207.9163 | 216.1106
588.5667 | 329.7763 | 208.1049 | 216.2955
589.5667 | 329.7602 | 208.2959 | 216.4849
590.5667 | 329.8158 | 208.492 | 216.6858
591.5667 | 329.8015 | 208.6895 | 216.8715
592.5667 | 329.7696 | 208.8644 | 217.0555
593.5667 | 329.7457 | 209.0691 | 217.2385
594.5667 | 329.7292 | 209.2609 | 217.4268
595.5667 | 329.8088 | 209.4482 | 217.6082
596.5667 | 329.8773 | 209.6378 | 217.7872
597.5667 | 329.9101 | 209.8375 | 217.9537
598.5667 | 329.8391 | 210.0233 | 218.1163
599.5667 | 329.8653 | 210.2066 | 218.2856
600.5667 | 329.8998 | 210.3899 | 218.4551
601.5667 | 329.9402 | 210.5905 | 218.6248
602.5667 | 329.8784 | 210.7818 | 218.7943
603.5667 | 329.802 | 210.9675 | 218.9656
604.5667 | 329.7649 | 211.162 | 219.1319
605.5667 | 329.7333 | 211.3476 | 219.3055
606.5667 | 329.6058 | 211.5357 | 219.4678
607.5667 | 329.4331 | 211.7397 | 219.6336
608.5667 | 329.3026 | 211.9247 | 219.7976
609.5667 | 329.1789 | 212.1103 | 219.9711
610.5667 | 329.0378 | 212.2967 | 220.1379
611.5667 | 329.054 | 212.4937 | 220.2977
612.5667 | 329.1357 | 212.6826 | 220.4665
613.5667 | 329.0972 | 212.8692 | 220.6298
614.5667 | 329.1212 | 213.0532 | 220.7926
615.5667 | 329.1101 | 213.249 | 220.9631
616.5667 | 329.0743 | 213.4233 | 221.131
617.5667 | 329.0673 | 213.628 | 221.2867
618.5667 | 329.0905 | 213.8116 | 221.4554
619.5667 | 329.0246 | 214.003 | 221.6227
620.5667 | 328.9872 | 214.1726 | 221.7743
621.5667 | 328.8703 | 214.3567 | 221.9388
622.5667 | 328.9413 | 214.5521 | 222.1034
623.5667 | 328.982 | 214.7415 | 222.2623
624.5667 | 328.9418 | 214.9164 | 222.4231
625.5667 | 328.7921 | 215.1043 | 222.5771
626.5667 | 328.6591 | 215.2915 | 222.7366
627.5667 | 328.5999 | 215.4846 | 222.9002
628.5667 | 328.5384 | 215.652 | 223.0619
629.5667 | 328.4763 | 215.8298 | 223.2258
630.5667 | 328.5377 | 216.0178 | 223.38
631.5667 | 328.5476 | 216.2056 | 223.5375
632.5667 | 328.6187 | 216.389 | 223.696
633.5667 | 328.5974 | 216.5548 | 223.861
634.5667 | 328.6141 | 216.7352 | 224.005
635.5667 | 328.6426 | 216.9121 | 224.1703
636.5667 | 328.6636 | 217.0965 | 224.3193
637.5667 | 328.7144 | 217.2672 | 224.484
638.5667 | 328.7459 | 217.4364 | 224.6368
639.5667 | 328.6785 | 217.6167 | 224.793
640.5667 | 328.7269 | 217.7949 | 224.9562
641.5667 | 328.6125 | 217.9728 | 225.1142
642.5667 | 328.5293 | 218.1364 | 225.2756
643.5667 | 328.5526 | 218.3035 | 225.4338
644.5667 | 328.5357 | 218.4754 | 225.5911
645.5667 | 328.6243 | 218.6549 | 225.7365
646.5667 | 328.6631 | 218.8229 | 225.8954
647.5667 | 328.7334 | 218.9934 | 226.0548
648.5667 | 328.7445 | 219.1618 | 226.1999
649.5667 | 328.8235 | 219.3277 | 226.3591
650.5667 | 328.8593 | 219.483 | 226.5121
651.5667 | 328.7975 | 219.6524 | 226.6692
652.5667 | 328.8556 | 219.8312 | 226.8245
653.5667 | 328.7955 | 219.989 | 226.9748
654.5667 | 328.7414 | 220.1548 | 227.1333
655.5667 | 328.694 | 220.3202 | 227.2826
656.5667 | 328.581 | 220.4787 | 227.4485
657.5667 | 328.5481 | 220.6502 | 227.6085
658.5667 | 328.6066 | 220.8147 | 227.7693
659.5667 | 328.5898 | 220.9766 | 227.9247
660.5667 | 328.5631 | 221.1307 | 228.0798
661.5667 | 328.5599 | 221.2908 | 228.241
662.5667 | 328.5226 | 221.4616 | 228.4014
663.5667 | 328.5505 | 221.6211 | 228.5575
664.5667 | 328.5298 | 221.7665 | 228.713
665.5667 | 328.5182 | 221.9346 | 228.8721
666.5667 | 328.5577 | 222.0945 | 229.0236
667.5667 | 328.6141 | 222.2475 | 229.1821
668.5667 | 328.6645 | 222.4039 | 229.3375
669.5667 | 328.7806 | 222.5682 | 229.4853
670.5667 | 328.8089 | 222.7224 | 229.6373
671.5667 | 328.8137 | 222.8958 | 229.7847
672.5667 | 328.9273 | 223.0453 | 229.9322
673.5667 | 328.9364 | 223.2051 | 230.0734
674.5667 | 328.9394 | 223.353 | 230.2247
675.5667 | 328.9375 | 223.5056 | 230.372
676.5667 | 329.0229 | 223.6574 | 230.5192
677.5667 | 329.1256 | 223.8214 | 230.667
678.5667 | 329.1298 | 223.9722 | 230.8221
679.5667 | 329.1184 | 224.136 | 230.9702
680.5667 | 329.1164 | 224.2799 | 231.121
681.5667 | 329.1665 | 224.4358 | 231.2622
682.5667 | 329.2146 | 224.5831 | 231.412
683.5667 | 329.234 | 224.7422 | 231.5617
684.5667 | 329.2278 | 224.8858 | 231.7038
685.5667 | 329.2178 | 225.0395 | 231.8519
686.5667 | 329.1309 | 225.1774 | 232.0054
687.5667 | 329.0601 | 225.34 | 232.1718
688.5667 | 329.037 | 225.4867 | 232.3212
689.5667 | 329.0908 | 225.6266 | 232.4752
690.5667 | 329.0858 | 225.7847 | 232.6209
691.5667 | 329.0115 | 225.9318 | 232.7756
692.5667 | 328.9851 | 226.0729 | 232.9459
693.5667 | 329.0471 | 226.2325 | 233.0865
694.5667 | 329.0699 | 226.37 | 233.2217
695.5667 | 328.9898 | 226.5222 | 233.3353
696.5667 | 328.8867 | 226.6734 | 233.4651
697.5667 | 328.7543 | 226.8127 | 233.5833
698.5667 | 328.7357 | 226.9591 | 233.7064
699.5667 | 328.8161 | 227.1087 | 233.8273
700.5667 | 328.9068 | 227.2498 | 233.947
701.5667 | 328.8956 | 227.3886 | 234.0598
702.5667 | 328.9527 | 227.5443 | 234.1747
703.5667 | 329.016 | 227.6817 | 234.2964
704.5667 | 328.9559 | 227.8133 | 234.4037
705.5667 | 329.0051 | 227.9669 | 234.5136
706.5667 | 329.1192 | 228.1112 | 234.6333
707.5667 | 329.1697 | 228.253 | 234.738
708.5667 | 329.1834 | 228.3949 | 234.8521
709.5667 | 329.1805 | 228.533 | 234.9642
710.5667 | 329.1844 | 228.685 | 235.0686
711.5667 | 329.2455 | 228.812 | 235.1759
712.5667 | 329.2684 | 228.9678 | 235.2801
713.5667 | 329.3198 | 229.1072 | 235.3885
714.5667 | 329.2801 | 229.2513 | 235.5007
715.5667 | 329.1474 | 229.3905 | 235.6146
716.5667 | 329.1642 | 229.5255 | 235.7219
717.5667 | 329.296 | 229.6686 | 235.8361
718.5667 | 329.3767 | 229.8094 | 235.9586
719.5667 | 329.4064 | 229.948 | 236.0734
720.5667 | 329.4659 | 230.0954 | 236.1991
721.5667 | 329.5152 | 230.2302 | 236.3271
722.5667 | 329.5059 | 230.3758 | 236.4492
723.5667 | 329.4707 | 230.508 | 236.5766
724.5667 | 329.4224 | 230.6441 | 236.7075
725.5667 | 329.3785 | 230.792 | 236.8323
726.5667 | 329.2927 | 230.9284 | 236.9791
727.5667 | 329.2819 | 231.0712 | 237.1237
728.5667 | 329.2197 | 231.2014 | 237.2572
729.5667 | 329.1376 | 231.3467 | 237.3837
730.5667 | 329.121 | 231.4881 | 237.5038
731.5667 | 329.0862 | 231.6255 | 237.6194
732.5667 | 329.0752 | 231.7532 | 237.7464
733.5667 | 329.0009 | 231.8898 | 237.8699
734.5667 | 328.931 | 232.0248 | 237.9832
735.5667 | 328.7831 | 232.1567 | 238.0895
736.5667 | 328.6994 | 232.2959 | 238.206
737.5667 | 328.6297 | 232.4315 | 238.327
738.5667 | 328.5328 | 232.5762 | 238.4279
739.5667 | 328.4947 | 232.7131 | 238.5405
740.5667 | 328.4448 | 232.85 | 238.6448
741.5667 | 328.3526 | 232.9747 | 238.748
742.5667 | 328.3535 | 233.1163 | 238.85
743.5667 | 328.4191 | 233.2503 | 238.9528
744.5667 | 328.3546 | 233.3743 | 239.0506
745.5667 | 328.2864 | 233.5093 | 239.1561
746.5667 | 328.2579 | 233.6268 | 239.2563
747.5667 | 328.1722 | 233.7641 | 239.3682
748.5667 | 328.1042 | 233.8993 | 239.4705
749.5667 | 328.1348 | 234.0398 | 239.5698
750.5667 | 328.1053 | 234.1792 | 239.6732
751.5667 | 328.1203 | 234.3046 | 239.7728
752.5667 | 328.1342 | 234.4393 | 239.8824
753.5667 | 328.1275 | 234.5726 | 239.9827
754.5667 | 328.1329 | 234.7067 | 240.08
755.5667 | 328.0895 | 234.831 | 240.1878
756.5667 | 328.1032 | 234.9623 | 240.2842
757.5667 | 328.1533 | 235.0962 | 240.3815
758.5667 | 328.1388 | 235.2245 | 240.4851
759.5667 | 328.1406 | 235.3484 | 240.5908
760.5667 | 328.1885 | 235.4901 | 240.6887
761.5667 | 328.2374 | 235.6139 | 240.7889
762.5667 | 328.2922 | 235.7397 | 240.8996
763.5667 | 328.3949 | 235.8709 | 241.0079
764.5667 | 328.4683 | 235.9948 | 241.1172
765.5667 | 328.5355 | 236.1162 | 241.2138
766.5667 | 328.5896 | 236.2454 | 241.3155
767.5667 | 328.6164 | 236.3711 | 241.4141
768.5667 | 328.6495 | 236.5029 | 241.5106
769.5667 | 328.7895 | 236.6222 | 241.613
770.5667 | 328.8106 | 236.7585 | 241.7123
771.5667 | 328.8727 | 236.8904 | 241.8121
772.5667 | 328.987 | 237.0072 | 241.9127
773.5667 | 329.1573 | 237.1409 | 242.0108
774.5667 | 329.3118 | 237.2757 | 242.1072
775.5667 | 329.407 | 237.4063 | 242.2096
776.5667 | 329.4049 | 237.5236 | 242.3119
777.5667 | 329.3509 | 237.6433 | 242.4043
778.5667 | 329.2456 | 237.7772 | 242.4909
779.5667 | 329.2438 | 237.9092 | 242.5836
780.5667 | 329.3265 | 238.0418 | 242.6886
781.5667 | 329.2831 | 238.1592 | 242.7722
782.5667 | 329.2169 | 238.2787 | 242.8698
783.5667 | 329.117 | 238.4057 | 242.9625
784.5667 | 328.9822 | 238.5328 | 243.0542
785.5667 | 328.7789 | 238.6461 | 243.1455
786.5667 | 328.7152 | 238.7671 | 243.2392
787.5667 | 328.711 | 238.8876 | 243.3329
788.5667 | 328.6928 | 239.015 | 243.4224
789.5667 | 328.66 | 239.1235 | 243.502
790.5667 | 328.7362 | 239.2452 | 243.5918
791.5667 | 328.7161 | 239.3595 | 243.6695
792.5667 | 328.7616 | 239.4824 | 243.7578
793.5667 | 328.6984 | 239.6026 | 243.8481
794.5667 | 328.662 | 239.7097 | 243.9419
795.5667 | 328.5031 | 239.8212 | 244.026
796.5667 | 328.4385 | 239.9455 | 244.1143
797.5667 | 328.4503 | 240.0496 | 244.2065
798.5667 | 328.3656 | 240.1683 | 244.2928
799.5667 | 328.2403 | 240.2853 | 244.3799
800.5667 | 328.2077 | 240.3923 | 244.466
801.5667 | 328.2044 | 240.5121 | 244.564
802.5667 | 328.162 | 240.6281 | 244.6571
803.5667 | 328.0836 | 240.7304 | 244.742
804.5667 | 328.1339 | 240.8551 | 244.8372
805.5667 | 328.1457 | 240.9637 | 244.9272
806.5667 | 328.0217 | 241.079 | 245.0134
807.5667 | 327.99 | 241.1773 | 245.1087
808.5667 | 327.9756 | 241.2989 | 245.1977
809.5667 | 327.9526 | 241.4053 | 245.2949
810.5667 | 328.0068 | 241.5139 | 245.3814
811.5667 | 328.0262 | 241.6288 | 245.4829
812.5667 | 327.9759 | 241.7374 | 245.5752
813.5667 | 327.9212 | 241.8418 | 245.6749
814.5667 | 327.7767 | 241.9514 | 245.7627
815.5667 | 327.7376 | 242.0545 | 245.8568
816.5667 | 327.6647 | 242.161 | 245.9337
817.5667 | 327.6012 | 242.2785 | 246.0302
818.5667 | 327.6401 | 242.3798 | 246.1156
819.5667 | 327.7024 | 242.4759 | 246.1916
820.5667 | 327.6437 | 242.5818 | 246.2876
821.5667 | 327.5579 | 242.6847 | 246.3727
822.5667 | 327.4071 | 242.789 | 246.4575
823.5667 | 327.3899 | 242.8834 | 246.5493
824.5667 | 327.2476 | 242.9868 | 246.634
825.5667 | 327.1439 | 243.0833 | 246.7318
826.5667 | 327.1282 | 243.1719 | 246.8266
827.5667 | 327.0317 | 243.2769 | 246.9174
828.5667 | 327.1288 | 243.3663 | 247.0151
829.5667 | 327.2286 | 243.4737 | 247.1104
830.5667 | 327.2079 | 243.5664 | 247.2107
831.5667 | 327.2215 | 243.6684 | 247.3001
832.5667 | 327.1108 | 243.7556 | 247.4081
833.5667 | 327.0861 | 243.8539 | 247.5055
834.5667 | 327.0894 | 243.9529 | 247.6102
835.5667 | 327.0978 | 244.0499 | 247.7184
836.5667 | 327.0054 | 244.1418 | 247.8203
837.5667 | 327.0069 | 244.2295 | 247.9191
838.5667 | 327.0364 | 244.334 | 248.0192
839.5667 | 327.0013 | 244.4243 | 248.1267
840.5667 | 326.9201 | 244.5199 | 248.2215
841.5667 | 326.8974 | 244.6097 | 248.3252
842.5667 | 326.8999 | 244.7051 | 248.4316
843.5667 | 326.9699 | 244.8018 | 248.538
844.5667 | 327.0249 | 244.8872 | 248.6436
845.5667 | 327.0793 | 244.9749 | 248.7441
846.5667 | 327.1088 | 245.0529 | 248.8497
847.5667 | 327.2001 | 245.1555 | 248.9416
848.5667 | 327.329 | 245.2374 | 249.0475
849.5667 | 327.2943 | 245.3305 | 249.1449
850.5667 | 327.4022 | 245.4137 | 249.2388
851.5667 | 327.4339 | 245.4989 | 249.3434
852.5667 | 327.5816 | 245.6004 | 249.4384
853.5667 | 327.6669 | 245.6868 | 249.538
854.5667 | 327.7814 | 245.768 | 249.6298
855.5667 | 327.9044 | 245.8617 | 249.741
856.5667 | 328.0644 | 245.9485 | 249.8448
857.5667 | 328.1305 | 246.035 | 249.9504
858.5667 | 328.1807 | 246.125 | 250.0581
859.5667 | 328.2302 | 246.2132 | 250.1638
860.5667 | 328.4034 | 246.3068 | 250.2736
861.5667 | 328.4412 | 246.3889 | 250.3802
862.5667 | 328.4129 | 246.4663 | 250.4838
863.5667 | 328.408 | 246.5563 | 250.5917
864.5667 | 328.472 | 246.6471 | 250.6893
865.5667 | 328.4699 | 246.7228 | 250.7877
866.5667 | 328.5682 | 246.8091 | 250.8867
867.5667 | 328.6191 | 246.8948 | 250.9868
868.5667 | 328.672 | 246.975 | 251.0836
869.5667 | 328.621 | 247.0617 | 251.1719
870.5667 | 328.573 | 247.1586 | 251.2661
871.5667 | 328.5592 | 247.2326 | 251.3609
872.5667 | 328.5321 | 247.327 | 251.4532
873.5667 | 328.5679 | 247.4219 | 251.5555
874.5667 | 328.6368 | 247.4975 | 251.6523
875.5667 | 328.6055 | 247.5872 | 251.75
876.5667 | 328.6346 | 247.6764 | 251.8459
877.5667 | 328.6122 | 247.7631 | 251.9521
878.5667 | 328.5894 | 247.8447 | 252.0432
879.5667 | 328.6159 | 247.9381 | 252.1331
880.5667 | 328.6042 | 248.0246 | 252.2216
881.5667 | 328.6712 | 248.1208 | 252.3137
882.5667 | 328.7042 | 248.2114 | 252.3977
883.5667 | 328.7805 | 248.2934 | 252.4872
884.5667 | 328.9189 | 248.3819 | 252.5683
885.5667 | 328.9162 | 248.4878 | 252.6508
886.5667 | 328.8199 | 248.5803 | 252.7387
887.5667 | 328.7507 | 248.6667 | 252.8163
888.5667 | 328.6468 | 248.7689 | 252.9047
889.5667 | 328.7033 | 248.8571 | 252.9892
890.5667 | 328.758 | 248.9451 | 253.0719
891.5667 | 328.8075 | 249.0327 | 253.1575
892.5667 | 328.7303 | 249.1221 | 253.2458
893.5667 | 328.6628 | 249.2058 | 253.333
894.5667 | 328.7415 | 249.2913 | 253.4126
895.5667 | 328.7499 | 249.3799 | 253.5052
896.5667 | 328.7868 | 249.4536 | 253.5879
897.5667 | 328.7762 | 249.5325 | 253.678
898.5667 | 328.7994 | 249.625 | 253.7642
899.5667 | 328.8667 | 249.7004 | 253.8531
900.5667 | 328.943 | 249.7842 | 253.9412
901.5667 | 329.0592 | 249.8623 | 254.0302
902.5667 | 329.1435 | 249.9279 | 254.1261
903.5667 | 329.21 | 250.0127 | 254.2287
904.5667 | 329.3354 | 250.0938 | 254.3395
905.5667 | 329.3072 | 250.1707 | 254.4363
906.5667 | 329.319 | 250.2503 | 254.5336
907.5667 | 329.4092 | 250.3258 | 254.6381
908.5667 | 329.4527 | 250.4015 | 254.746
909.5667 | 329.5389 | 250.4851 | 254.846
910.5667 | 329.4974 | 250.5574 | 254.9468
911.5667 | 329.4211 | 250.6467 | 255.048
912.5667 | 329.3983 | 250.7246 | 255.1536
913.5667 | 329.3931 | 250.8094 | 255.2593
914.5667 | 329.3773 | 250.8831 | 255.3631
915.5667 | 329.3113 | 250.9692 | 255.4669
916.5667 | 329.2627 | 251.038 | 255.5721
917.5667 | 329.3855 | 251.1252 | 255.6855
918.5667 | 329.4387 | 251.1971 | 255.7898
919.5667 | 329.4604 | 251.2922 | 255.9018
920.5667 | 329.526 | 251.3662 | 256.0163
921.5667 | 329.5923 | 251.4436 | 256.1292
922.5667 | 329.6464 | 251.5281 | 256.2385
923.5667 | 329.652 | 251.6044 | 256.3631
924.5667 | 329.7344 | 251.6904 | 256.4854
925.5667 | 329.7918 | 251.7573 | 256.6056
926.5667 | 329.673 | 251.8456 | 256.728
927.5667 | 329.4701 | 251.9268 | 256.8635
928.5667 | 329.4061 | 251.9984 | 256.9842
929.5667 | 329.3622 | 252.0692 | 257.1138
930.5667 | 329.3037 | 252.1493 | 257.2407
931.5667 | 329.2212 | 252.2204 | 257.3701
932.5667 | 329.1231 | 252.2851 | 257.5041
933.5667 | 329.1657 | 252.3599 | 257.6323
934.5667 | 329.1701 | 252.4232 | 257.7637
935.5667 | 329.1265 | 252.5014 | 257.9019
936.5667 | 329.078 | 252.561 | 258.0314
937.5667 | 329.1178 | 252.6144 | 258.1606
938.5667 | 329.1262 | 252.6878 | 258.2909
939.5667 | 329.0956 | 252.7545 | 258.4121
940.5667 | 329.0892 | 252.829 | 258.547
941.5667 | 329.0905 | 252.8923 | 258.6681
942.5667 | 329.1246 | 252.9613 | 258.7907
943.5667 | 329.0637 | 253.0245 | 258.9169
944.5667 | 329.0835 | 253.0916 | 259.0307
945.5667 | 329.0837 | 253.1665 | 259.1599
946.5667 | 329.0734 | 253.2381 | 259.2837
947.5667 | 328.9499 | 253.3047 | 259.3943
948.5667 | 328.9677 | 253.3799 | 259.5059
949.5667 | 329.0101 | 253.4504 | 259.623
950.5667 | 329.0384 | 253.5047 | 259.7332
951.5667 | 329.0446 | 253.5745 | 259.8526
952.5667 | 328.9745 | 253.6615 | 259.9649
953.5667 | 328.9651 | 253.7196 | 260.0781
954.5667 | 329.0086 | 253.7944 | 260.1931
955.5667 | 329.0572 | 253.8637 | 260.2964
956.5667 | 329.0932 | 253.9337 | 260.4101
957.5667 | 329.1054 | 253.9989 | 260.5137
958.5667 | 329.1113 | 254.0671 | 260.6251
959.5667 | 329.1061 | 254.144 | 260.7443
960.5823 | 329.1067 | 254.2097 | 260.8416
961.5667 | 329.1154 | 254.281 | 260.9538
962.5667 | 329.0322 | 254.3612 | 261.0575
963.5667 | 328.9487 | 254.4257 | 261.159
964.5667 | 328.8662 | 254.4998 | 261.265
965.5667 | 328.8418 | 254.5779 | 261.3715
966.5667 | 328.8867 | 254.653 | 261.476
967.5667 | 328.8285 | 254.7222 | 261.5937
968.5667 | 328.7465 | 254.793 | 261.6951
969.5667 | 328.6555 | 254.8713 | 261.7963
970.5667 | 328.5722 | 254.9509 | 261.8907
971.5667 | 328.5106 | 255.0155 | 261.9886
972.5667 | 328.4625 | 255.0833 | 262.0855
973.5667 | 328.3789 | 255.1671 | 262.1807
974.5667 | 328.3623 | 255.2504 | 262.2717
975.5667 | 328.4241 | 255.3205 | 262.3669
976.5667 | 328.3519 | 255.4041 | 262.4629
977.5667 | 328.2856 | 255.49 | 262.5558
978.5667 | 328.1344 | 255.5735 | 262.6367
979.5667 | 328.1633 | 255.6498 | 262.7187
980.5667 | 328.2479 | 255.7253 | 262.8033
981.5667 | 328.2349 | 255.8125 | 262.8855
982.5667 | 328.1755 | 255.8931 | 262.9657
983.5667 | 328.1485 | 255.9602 | 263.048
984.5667 | 328.0049 | 256.0536 | 263.1257
985.5667 | 328.0299 | 256.137 | 263.2067
986.5667 | 328.0487 | 256.2032 | 263.2757
987.5667 | 328.116 | 256.2861 | 263.3509
988.5667 | 328.0738 | 256.3647 | 263.424
989.5667 | 328.0061 | 256.4456 | 263.5021
990.5667 | 327.9801 | 256.5265 | 263.5834
991.5667 | 327.8861 | 256.6044 | 263.6552
992.5667 | 328.0202 | 256.6848 | 263.7361
993.5667 | 328.1215 | 256.7654 | 263.8128
994.5667 | 328.1965 | 256.8485 | 263.8819
995.5667 | 328.2194 | 256.9288 | 263.9576
996.5667 | 328.2603 | 257.0034 | 264.038
997.5667 | 328.3391 | 257.0743 | 264.1147
998.5667 | 328.4758 | 257.1538 | 264.1879
999.5667 | 328.5135 | 257.2276 | 264.2638
1000.5667 | 328.5081 | 257.2948 | 264.3385
1001.5667 | 328.5737 | 257.3607 | 264.4099
1002.5667 | 328.6891 | 257.4375 | 264.4832
1003.5667 | 328.6496 | 257.5037 | 264.5587
1004.5667 | 328.7023 | 257.5815 | 264.6356
1005.5667 | 328.8386 | 257.6546 | 264.7073
1006.5667 | 328.8452 | 257.7375 | 264.7751
1007.5667 | 328.797 | 257.8071 | 264.8379
1008.5667 | 328.785 | 257.897 | 264.91
1009.5667 | 328.8573 | 257.9812 | 264.9767
1010.5667 | 328.8844 | 258.0594 | 265.0342
1011.5667 | 328.8708 | 258.1312 | 265.1068
1012.5667 | 328.8483 | 258.2251 | 265.171
1013.5667 | 328.7841 | 258.3154 | 265.2396
1014.5667 | 328.7671 | 258.3888 | 265.2989
1015.5667 | 328.7783 | 258.4665 | 265.3561
1016.5667 | 328.8235 | 258.5557 | 265.4173
1017.5667 | 328.8533 | 258.6232 | 265.4648
1018.5667 | 328.9066 | 258.7077 | 265.5194
1019.5667 | 328.8841 | 258.8029 | 265.5572
1020.5667 | 328.7973 | 258.8868 | 265.6057
1021.5667 | 328.7306 | 258.9681 | 265.6512
1022.5667 | 328.6595 | 259.0539 | 265.6911
1023.5667 | 328.5962 | 259.1466 | 265.7483
1024.5667 | 328.4871 | 259.2466 | 265.7898
1025.5667 | 328.4256 | 259.3289 | 265.8334
1026.5667 | 328.4049 | 259.4287 | 265.8715
1027.5667 | 328.3937 | 259.5146 | 265.908
1028.5667 | 328.3222 | 259.6134 | 265.9467
1029.5667 | 328.2274 | 259.7152 | 265.988
1030.5667 | 328.1702 | 259.8008 | 266.0192
1031.5667 | 328.0472 | 259.8863 | 266.057
1032.5667 | 327.9516 | 259.9692 | 266.0876
1033.5667 | 327.9055 | 260.0616 | 266.1313
1034.5667 | 327.8448 | 260.1295 | 266.1719
1035.5667 | 327.7598 | 260.2046 | 266.2174
1036.5667 | 327.7706 | 260.2883 | 266.2602
1037.5667 | 327.7172 | 260.3632 | 266.3058
1038.5667 | 327.6933 | 260.4398 | 266.3414
1039.5667 | 327.5633 | 260.5249 | 266.3934
1040.5667 | 327.5351 | 260.6041 | 266.4361
1041.5667 | 327.5318 | 260.6961 | 266.4825
1042.5667 | 327.5008 | 260.7692 | 266.5396
1043.5667 | 327.4755 | 260.8519 | 266.5871
1044.5667 | 327.3959 | 260.9197 | 266.6373
1045.5667 | 327.2658 | 260.977 | 266.6837
1046.5667 | 327.2005 | 261.0608 | 266.7457
1047.5667 | 327.1747 | 261.1321 | 266.8217
1048.5667 | 327.1311 | 261.2014 | 266.8944
1049.5667 | 327.0492 | 261.2602 | 266.9565
1050.5667 | 327.0216 | 261.3404 | 267.0021
1051.5667 | 327.0127 | 261.3942 | 267.052
1052.5667 | 327.095 | 261.4778 | 267.1045
1053.5667 | 327.186 | 261.5702 | 267.1569
1054.5667 | 327.2153 | 261.6283 | 267.2055
1055.5667 | 327.2627 | 261.715 | 267.2545
1056.5667 | 327.3887 | 261.7692 | 267.3072
1057.5667 | 327.508 | 261.8574 | 267.3677
1058.5667 | 327.6162 | 261.9297 | 267.4226
1059.5667 | 327.7075 | 261.9867 | 267.4641
1060.5667 | 327.742 | 262.0484 | 267.5061
1061.5667 | 327.8214 | 262.1194 | 267.5595
1062.5667 | 327.8668 | 262.1771 | 267.6052
1063.5667 | 328.0275 | 262.2507 | 267.6395
1064.5667 | 328.1556 | 262.3072 | 267.6792
1065.5667 | 328.3283 | 262.381 | 267.7342
1066.5667 | 328.4103 | 262.4485 | 267.7738
1067.5667 | 328.4481 | 262.5076 | 267.8211
1068.5667 | 328.4426 | 262.5638 | 267.8642
1069.5667 | 328.4591 | 262.6249 | 267.9089
1070.5667 | 328.6161 | 262.6692 | 267.935
1071.5667 | 328.7655 | 262.6682 | 267.9442
1072.5667 | 328.8007 | 262.7112 | 267.9815
1073.5667 | 328.783 | 262.7705 | 268.0301
1074.5667 | 328.79 | 262.8057 | 268.0667
1075.5667 | 328.9124 | 262.854 | 268.1044
1076.5667 | 328.9776 | 262.9081 | 268.1417
1077.5667 | 328.9525 | 262.9564 | 268.1775
1078.5667 | 329.0128 | 263.0096 | 268.2166
1079.5667 | 329.1521 | 263.0652 | 268.2648
1080.5667 | 329.2252 | 263.1208 | 268.3034
1081.5667 | 329.3328 | 263.1837 | 268.3464
1082.5667 | 329.3577 | 263.2439 | 268.3999
1083.5667 | 329.2978 | 263.3193 | 268.4675
1084.5667 | 329.3376 | 263.3951 | 268.5122
1085.5667 | 329.3557 | 263.4669 | 268.5704
1086.5667 | 329.4045 | 263.5358 | 268.6274
1087.5667 | 329.5669 | 263.6186 | 268.6721
1088.5667 | 329.6868 | 263.6909 | 268.7155
1089.5667 | 329.7557 | 263.7691 | 268.7777
1090.5667 | 329.7397 | 263.9334 | 268.8665
1091.5667 | 329.7413 | 264.0007 | 268.9276
1092.5667 | 329.6594 | 264.0343 | 268.9665
1093.5667 | 329.5398 | 264.1037 | 269.0171
1094.5667 | 329.4747 | 264.1739 | 269.0737
1095.5667 | 329.4316 | 264.2638 | 269.1129
1096.5667 | 329.3245 | 264.3514 | 269.1764
1097.5667 | 329.1653 | 264.4375 | 269.2214
1098.5667 | 329.0603 | 264.5285 | 269.2734
1099.5667 | 328.8729 | 264.6096 | 269.3282
1100.5667 | 328.8264 | 264.7028 | 269.3752
1101.5667 | 328.7592 | 264.7885 | 269.4271
1102.5667 | 328.6972 | 264.8725 | 269.4787
1103.5667 | 328.6273 | 264.9517 | 269.5197
1104.5667 | 328.5074 | 265.0317 | 269.5762
1105.5667 | 328.3998 | 265.0924 | 269.6331
1106.5667 | 328.3032 | 265.1817 | 269.6885
1107.5667 | 328.2539 | 265.2515 | 269.7437
1108.5667 | 328.2146 | 265.3115 | 269.795
1109.5667 | 328.1454 | 265.3609 | 269.8446
1110.5667 | 328.1419 | 265.4373 | 269.8987
1111.5667 | 328.096 | 265.4994 | 269.9375
1112.5667 | 327.9605 | 265.5769 | 270.0195
1113.5667 | 327.8419 | 265.6513 | 270.0607
1114.5667 | 327.7703 | 265.7157 | 270.1121
1115.5667 | 327.78 | 265.7769 | 270.1632
1116.5667 | 327.6734 | 265.8362 | 270.2035
1117.5667 | 327.5969 | 265.9108 | 270.2403
1118.5667 | 327.4947 | 265.9941 | 270.288
1119.5667 | 327.4973 | 266.0526 | 270.3286
1120.5667 | 327.565 | 266.0962 | 270.3558
1121.5667 | 327.6453 | 266.1593 | 270.393
1122.5667 | 327.6815 | 266.2233 | 270.4336
1123.5667 | 327.5862 | 266.3677 | 270.4301
1124.5667 | 327.7597 | 266.4183 | 270.5753
1125.5667 | 327.7342 | 266.4688 | 270.6183
1126.5667 | 327.7266 | 266.5108 | 270.6574
1127.5667 | 327.7215 | 266.5507 | 270.6954
1128.5667 | 327.7853 | 266.6144 | 270.7369
1129.5667 | 327.8534 | 266.6747 | 270.7799
1130.5667 | 327.926 | 266.722 | 270.8215
1131.5667 | 328.0073 | 266.7759 | 270.8539
1132.5667 | 328.0333 | 266.8309 | 270.8907
1133.5667 | 328.1524 | 266.8794 | 270.9327
1134.5667 | 328.1787 | 266.9152 | 270.9707
1135.5667 | 328.1639 | 266.9537 | 271.0089
1136.5667 | 328.1478 | 266.9989 | 271.0498
1137.5667 | 328.2022 | 267.0406 | 271.0925
1138.5667 | 328.2657 | 267.071 | 271.1368
1139.5667 | 328.3519 | 267.1033 | 271.1755
1140.5667 | 328.3971 | 267.1293 | 271.217
1141.5667 | 328.5072 | 267.1542 | 271.2528
1142.5667 | 328.4481 | 267.1925 | 271.2859
1143.5667 | 328.4399 | 267.2223 | 271.3201
1144.5667 | 328.5539 | 267.2459 | 271.3546
1145.5667 | 328.6192 | 267.2725 | 271.3912
1146.5667 | 328.6489 | 267.2982 | 271.4333
1147.5667 | 328.7793 | 267.3177 | 271.4774
1148.5667 | 328.8616 | 267.3397 | 271.5224
1149.5667 | 328.8761 | 267.367 | 271.5652
1150.5667 | 328.77 | 267.3862 | 271.6049
1151.5667 | 328.7172 | 267.4313 | 271.6449
1152.5667 | 328.6531 | 267.474 | 271.6886
1153.5667 | 328.6351 | 267.511 | 271.7327
1154.5667 | 328.5966 | 267.5652 | 271.7731
1155.5667 | 328.6825 | 267.6142 | 271.8155
1156.5667 | 328.6917 | 267.6524 | 271.8495
1157.5667 | 328.7406 | 267.6924 | 271.8877
1158.5667 | 328.7107 | 267.739 | 271.9273
1159.5667 | 328.646 | 267.793 | 271.9701
1160.5667 | 328.4594 | 267.8429 | 272.0129
1161.5667 | 328.2986 | 267.8914 | 272.0434
1162.5667 | 328.2899 | 267.9373 | 272.0867
1163.5667 | 328.1489 | 267.9873 | 272.123
1164.5667 | 328.0597 | 268.03 | 272.1591
1165.5667 | 328.0815 | 268.0787 | 272.1954
1166.5667 | 327.9871 | 268.1148 | 272.2353
1167.5667 | 327.933 | 268.1601 | 272.2726
1168.5667 | 327.903 | 268.2134 | 272.308
1169.5667 | 327.8813 | 268.2537 | 272.3411
1170.5667 | 327.7942 | 268.3028 | 272.3812
1171.5667 | 327.834 | 268.3557 | 272.4145
1172.5667 | 327.8037 | 268.4184 | 272.4562
1173.5667 | 327.7455 | 268.4629 | 272.4927
1174.5667 | 327.7302 | 268.5167 | 272.5339
1175.5667 | 327.7519 | 268.5681 | 272.5666
1176.5667 | 327.7773 | 268.6293 | 272.6141
1177.5667 | 327.6985 | 268.6816 | 272.6512
1178.5667 | 327.7056 | 268.739 | 272.6968
1179.5667 | 327.7704 | 268.7858 | 272.7375
1180.5667 | 327.7558 | 268.8308 | 272.7824
1181.5667 | 327.7 | 268.8967 | 272.8176
1182.5667 | 327.6505 | 268.9561 | 272.8618
1183.5667 | 327.6778 | 269.0155 | 272.8937
1184.5667 | 327.6915 | 269.0557 | 272.9308
1185.5667 | 327.6725 | 269.1213 | 272.9655
1186.5667 | 327.7289 | 269.1776 | 273.0005
1187.5667 | 327.674 | 269.2256 | 273.0284
1188.5667 | 327.5943 | 269.26 | 273.0649
1189.5667 | 327.5881 | 269.2934 | 273.0915
1190.5667 | 327.6178 | 269.3192 | 273.124
1191.5667 | 327.6157 | 269.3527 | 273.1452
1192.5667 | 327.5779 | 269.3869 | 273.1651
1193.5667 | 327.5512 | 269.4152 | 273.1764
1194.5667 | 327.5641 | 269.4284 | 273.2007
1195.5667 | 327.5444 | 269.4569 | 273.2069
1196.5667 | 327.5717 | 269.4726 | 273.2281
1197.5667 | 327.5472 | 269.4881 | 273.2516
1198.5667 | 327.5503 | 269.5055 | 273.2784
1199.5667 | 327.4944 | 269.5283 | 273.3015
1200.5667 | 327.5849 | 269.5418 | 273.3289
1201.5667 | 327.5999 | 269.5496 | 273.3627
1202.5667 | 327.6342 | 269.5606 | 273.3897
1203.5667 | 327.5877 | 269.5644 | 273.4114
1204.5667 | 327.5844 | 269.5785 | 273.4472
1205.5667 | 327.6716 | 269.5996 | 273.4704
1206.5667 | 327.6481 | 269.6191 | 273.5008
1207.5667 | 327.6121 | 269.6298 | 273.5354
1208.5667 | 327.6376 | 269.6357 | 273.5626
1209.5667 | 327.6261 | 269.6433 | 273.5896
1210.5667 | 327.6563 | 269.6569 | 273.6112
1211.5667 | 327.6491 | 269.6548 | 273.6254
1212.5667 | 327.627 | 269.6684 | 273.6475
1213.5667 | 327.6213 | 269.6601 | 273.6742
1214.5667 | 327.5925 | 269.6717 | 273.7054
1215.5667 | 327.5706 | 269.6781 | 273.7325
1216.5667 | 327.5189 | 269.667 | 273.7616
1217.5667 | 327.5062 | 269.6689 | 273.7833
1218.5667 | 327.5541 | 269.6641 | 273.8117
1219.5667 | 327.6085 | 269.6619 | 273.839
1220.5667 | 327.685 | 269.6637 | 273.8596
1221.5667 | 327.692 | 269.6719 | 273.882
1222.5667 | 327.7415 | 269.6681 | 273.9004
1223.5667 | 327.7601 | 269.6796 | 273.9249
1224.5667 | 327.7506 | 269.6925 | 273.9394
1225.5667 | 327.7726 | 269.7042 | 273.9613
1226.5667 | 327.7989 | 269.721 | 273.9702
1227.5667 | 327.8084 | 269.7324 | 273.9976
1228.5667 | 327.8003 | 269.7523 | 274.0272
1229.5667 | 327.808 | 269.7584 | 274.0424
1230.5667 | 327.8086 | 269.7866 | 274.0787
1231.5667 | 327.8341 | 269.7987 | 274.1126
1232.5667 | 327.9035 | 269.817 | 274.1456
1233.5667 | 327.8182 | 269.8251 | 274.1804
1234.5667 | 327.7161 | 269.8493 | 274.2076
1235.5667 | 327.6696 | 269.8762 | 274.2412
1236.5667 | 327.6469 | 269.8979 | 274.2715
1237.5667 | 327.6087 | 269.9241 | 274.302
1238.5667 | 327.6194 | 269.9434 | 274.3336
1239.5667 | 327.6255 | 269.9671 | 274.3686
1240.5667 | 327.5807 | 269.9905 | 274.3976
1241.5667 | 327.5454 | 270.0171 | 274.4229
1242.5667 | 327.589 | 270.0348 | 274.4529
1243.5667 | 327.6623 | 270.0492 | 274.4735
1244.5667 | 327.6611 | 270.0625 | 274.4878
1245.5667 | 327.7345 | 270.0693 | 274.519
1246.5667 | 327.8287 | 270.0858 | 274.5268
1247.5667 | 327.8437 | 270.1019 | 274.5566
1248.5667 | 327.8519 | 270.1036 | 274.5708
1249.5667 | 327.8746 | 270.1071 | 274.5945
1250.5667 | 327.8451 | 270.1231 | 274.6089
1251.5667 | 327.8197 | 270.1207 | 274.6369
1252.5667 | 327.9035 | 270.1348 | 274.6586
1253.5667 | 327.842 | 270.1294 | 274.6882
1254.5667 | 327.7528 | 270.1346 | 274.71
1255.5667 | 327.7183 | 270.14 | 274.7297
1256.5667 | 327.7557 | 270.1464 | 274.7496
1257.5667 | 327.7344 | 270.154 | 274.7732
1258.5667 | 327.8035 | 270.1521 | 274.785
1259.5667 | 327.7481 | 270.1585 | 274.8023
1260.5667 | 327.7172 | 270.1534 | 274.8202
1261.5667 | 327.6474 | 270.1685 | 274.8392
1262.5667 | 327.5905 | 270.1654 | 274.8607
1263.5667 | 327.5057 | 270.174 | 274.8925
1264.5667 | 327.4384 | 270.1731 | 274.9132
1265.5667 | 327.4384 | 270.1837 | 274.9354
1266.5667 | 327.4906 | 270.2077 | 274.9605
1267.5667 | 327.4642 | 270.2205 | 274.9879
1268.5667 | 327.3918 | 270.2271 | 275.0031
1269.5667 | 327.4227 | 270.2311 | 275.0243
1270.5667 | 327.383 | 270.2307 | 275.0533
1271.5667 | 327.3829 | 270.2409 | 275.0798
1272.5667 | 327.4198 | 270.2363 | 275.116
1273.5667 | 327.5149 | 270.2409 | 275.1403
1274.5667 | 327.5695 | 270.251 | 275.165
1275.5667 | 327.6509 | 270.2495 | 275.1933
1276.5667 | 327.6655 | 270.2488 | 275.2146
1277.5667 | 327.5619 | 270.2506 | 275.241
1278.5667 | 327.514 | 270.259 | 275.2651
1279.5667 | 327.5571 | 270.2576 | 275.2851
1280.5667 | 327.4669 | 270.2623 | 275.3095
1281.5667 | 327.4703 | 270.2532 | 275.3336
1282.5667 | 327.4115 | 270.2643 | 275.3556
1283.5667 | 327.3594 | 270.2645 | 275.3814
1284.5667 | 327.3724 | 270.2702 | 275.3917
1285.5667 | 327.4327 | 270.2802 | 275.4019
1286.5667 | 327.5183 | 270.2811 | 275.4213
1287.5667 | 327.5444 | 270.279 | 275.4373
1288.5667 | 327.5587 | 270.2711 | 275.4569
1289.5667 | 327.5575 | 270.281 | 275.4816
1290.5667 | 327.5465 | 270.274 | 275.5004
1291.5667 | 327.5862 | 270.2779 | 275.5268
1292.5667 | 327.4905 | 270.2895 | 275.556
1293.5667 | 327.4975 | 270.2885 | 275.5793
1294.5667 | 327.4978 | 270.291 | 275.599
1295.5667 | 327.4484 | 270.2953 | 275.6238
1296.5667 | 327.449 | 270.2906 | 275.6381
1297.5667 | 327.4982 | 270.2933 | 275.6468
1298.5667 | 327.421 | 270.2959 | 275.6526
1299.5667 | 327.4318 | 270.3062 | 275.6684
1300.5667 | 327.5079 | 270.3106 | 275.6903
1301.5667 | 327.4975 | 270.31 | 275.7057
1302.5667 | 327.4922 | 270.3081 | 275.7261
1303.5667 | 327.5666 | 270.3128 | 275.7491
1304.5667 | 327.6503 | 270.307 | 275.7695
1305.5667 | 327.7535 | 270.3165 | 275.7925
1306.5667 | 327.7987 | 270.3179 | 275.8066
1307.5667 | 327.7147 | 270.3234 | 275.8112
1308.5667 | 327.6338 | 270.3201 | 275.8286
1309.5667 | 327.5108 | 270.327 | 275.8334
1310.5667 | 327.484 | 270.3209 | 275.8542
1311.5667 | 327.4701 | 270.336 | 275.8572
1312.5667 | 327.5214 | 270.3343 | 275.8627
1313.5667 | 327.5418 | 270.3467 | 275.8811
1314.5667 | 327.6384 | 270.3533 | 275.8877
1315.5667 | 327.6575 | 270.3586 | 275.8957
1316.5667 | 327.6383 | 270.3635 | 275.9106
1317.5667 | 327.6457 | 270.3572 | 275.9222
1318.5667 | 327.6654 | 270.373 | 275.9342
1319.5667 | 327.5854 | 270.3854 | 275.961
1320.5667 | 327.5365 | 270.3905 | 275.9814
1321.5667 | 327.5925 | 270.4 | 276.0034
1322.5667 | 327.6548 | 270.4129 | 276.0128
1323.5667 | 327.6883 | 270.435 | 276.0332
1324.5667 | 327.7154 | 270.4413 | 276.0483
1325.5667 | 327.7392 | 270.4599 | 276.053
1326.5667 | 327.8135 | 270.4678 | 276.0801
1327.5667 | 327.8123 | 270.486 | 276.096
1328.5667 | 327.7874 | 270.5058 | 276.1157
1329.5667 | 327.7859 | 270.5111 | 276.1277
1330.5667 | 327.7272 | 270.5271 | 276.1485
1331.5667 | 327.7939 | 270.536 | 276.1614
1332.5667 | 327.8472 | 270.5455 | 276.172
1333.5667 | 327.8204 | 270.5388 | 276.1916
1334.5667 | 327.8597 | 270.5587 | 276.2026
1335.5667 | 327.7613 | 270.5596 | 276.216
1336.5667 | 327.851 | 270.5628 | 276.228
1337.5667 | 327.9092 | 270.5739 | 276.2449
1338.5667 | 327.9541 | 270.5708 | 276.2625
1339.5667 | 327.9655 | 270.5845 | 276.2805
1340.5667 | 327.9557 | 270.5936 | 276.3
1341.5667 | 327.9701 | 270.6063 | 276.3181
1342.5667 | 327.9915 | 270.6104 | 276.3326
1343.5667 | 327.9749 | 270.6174 | 276.3505
1344.5667 | 327.9749 | 270.6157 | 276.3602
1345.5667 | 327.9384 | 270.6331 | 276.3775
1346.5667 | 327.8946 | 270.6503 | 276.3952
1347.5667 | 327.8657 | 270.6507 | 276.4048
1348.5667 | 327.8471 | 270.6744 | 276.4271
1349.5667 | 327.8176 | 270.683 | 276.4496
1350.5667 | 327.8238 | 270.6803 | 276.4601
1351.5667 | 327.8057 | 270.686 | 276.4657
1352.5667 | 327.8171 | 270.7009 | 276.4788
1353.5667 | 327.8856 | 270.7108 | 276.4824
1354.5667 | 328.0211 | 270.7278 | 276.4956
1355.5667 | 328.0677 | 270.7276 | 276.5092
1356.5667 | 328.1302 | 270.7335 | 276.5252
1357.5667 | 328.1753 | 270.7489 | 276.5383
1358.5667 | 328.2097 | 270.7506 | 276.5604
1359.5667 | 328.2044 | 270.763 | 276.5776
1360.5667 | 328.2323 | 270.7726 | 276.5983
1361.5667 | 328.3196 | 270.7987 | 276.6103
1362.5667 | 328.4311 | 270.8189 | 276.6316
1363.5667 | 328.4328 | 270.8362 | 276.6423
1364.5667 | 328.5064 | 270.856 | 276.6654
1365.5667 | 328.4899 | 270.8799 | 276.6857
1366.5667 | 328.5568 | 270.9136 | 276.6927
1367.5667 | 328.6734 | 270.9418 | 276.6969
1368.5667 | 328.6444 | 270.9596 | 276.6949
1369.5667 | 328.6665 | 270.9842 | 276.7051
1370.5667 | 328.6598 | 271.0177 | 276.7214
1371.5667 | 328.642 | 271.0384 | 276.733
1372.5667 | 328.5849 | 271.0525 | 276.7556
1373.5667 | 328.6056 | 271.084 | 276.7801
1374.5667 | 328.5462 | 271.1093 | 276.8
1375.5667 | 328.4959 | 271.1367 | 276.8231
1376.5667 | 328.4798 | 271.1545 | 276.8393
1377.5667 | 328.4924 | 271.1719 | 276.8595
1378.5667 | 328.3751 | 271.1943 | 276.8974
1379.5667 | 328.3654 | 271.2085 | 276.9148
1380.5667 | 328.3388 | 271.2281 | 276.9306
1381.5667 | 328.286 | 271.2433 | 276.9528
1382.5667 | 328.2089 | 271.2606 | 276.9693
1383.5667 | 328.2058 | 271.283 | 276.9891
1384.5667 | 328.2229 | 271.2964 | 277.0039
1385.5667 | 328.2168 | 271.3263 | 277.0277
1386.5667 | 328.1633 | 271.3275 | 277.049
1387.5667 | 328.1068 | 271.3571 | 277.0728
1388.5667 | 328.0233 | 271.3574 | 277.0967
1389.5667 | 327.936 | 271.3929 | 277.121
1390.5667 | 327.9933 | 271.3966 | 277.1419
1391.5667 | 327.9881 | 271.4112 | 277.1608
1392.5667 | 328.0607 | 271.4272 | 277.1863
1393.5667 | 328.0589 | 271.4362 | 277.2022
1394.5667 | 328.0196 | 271.4537 | 277.2204
1395.5667 | 328.1445 | 271.4633 | 277.2369
1396.5667 | 328.21 | 271.481 | 277.2616
1397.5667 | 328.1966 | 271.497 | 277.2689
1398.5667 | 328.2113 | 271.5073 | 277.2899
1399.5667 | 328.1726 | 271.5164 | 277.306
1400.5667 | 328.2062 | 271.5149 | 277.3188
1401.5667 | 328.2428 | 271.5093 | 277.3392
1402.5667 | 328.15 | 271.5126 | 277.3529
1403.5667 | 328.0841 | 271.4961 | 277.3775
1404.5667 | 328.1178 | 271.4999 | 277.3972
1405.5667 | 328.1265 | 271.4951 | 277.4057
1406.5667 | 328.2127 | 271.4995 | 277.4219
1407.5667 | 328.2026 | 271.4908 | 277.4399
1408.5667 | 328.1194 | 271.4956 | 277.46
1409.5667 | 328.1403 | 271.4956 | 277.4802
1410.5667 | 328.1017 | 271.4998 | 277.499
1411.5667 | 328.108 | 271.5012 | 277.5102
1412.5667 | 328.1104 | 271.5087 | 277.5311
1413.5667 | 328.0953 | 271.5226 | 277.5438
1414.5667 | 328.156 | 271.5377 | 277.5552
1415.5667 | 328.1826 | 271.5629 | 277.5638
1416.5667 | 328.1648 | 271.5848 | 277.5819
1417.5667 | 328.1556 | 271.6049 | 277.5939
1418.5667 | 328.192 | 271.6093 | 277.6096
1419.5667 | 328.202 | 271.6258 | 277.628
1420.5667 | 328.179 | 271.632 | 277.6489
1421.5667 | 328.1981 | 271.6481 | 277.671
1422.5667 | 328.1123 | 271.6662 | 277.7012
1423.5667 | 328.1326 | 271.6809 | 277.7253
1424.5667 | 328.075 | 271.6767 | 277.7466
1425.5667 | 328.0349 | 271.6844 | 277.7633
1426.5667 | 328.0076 | 271.6949 | 277.7674
1427.5667 | 327.9092 | 271.7062 | 277.784
1428.5667 | 327.9534 | 271.703 | 277.791
1429.5667 | 327.9553 | 271.7119 | 277.798
1430.5667 | 327.8475 | 271.7237 | 277.8026
1431.5667 | 327.8309 | 271.7298 | 277.8298
1432.5667 | 327.7485 | 271.7338 | 277.8451
1433.5667 | 327.6701 | 271.7379 | 277.8559
1434.5667 | 327.6522 | 271.7639 | 277.8779
1435.5667 | 327.6819 | 271.7769 | 277.8997
1436.5667 | 327.6518 | 271.7899 | 277.9116
1437.5667 | 327.6286 | 271.7427 | 277.8334
1438.5667 | 327.6519 | 271.7695 | 277.851
1439.5667 | 327.6073 | 271.77 | 277.898
1440.5667 | 327.5549 | 271.7914 | 277.9135
1441.5667 | 327.3865 | 271.7895 | 277.9149
1442.5667 | 327.5399 | 271.8063 | 277.9364
1443.5667 | 327.5373 | 271.808 | 277.9493
1444.5667 | 327.6156 | 271.829 | 277.9623
1445.5667 | 327.5907 | 271.8393 | 277.997
1446.5667 | 327.651 | 271.853 | 277.9993
1447.5667 | 327.6196 | 271.8603 | 278.0084
1448.5667 | 327.62 | 271.8683 | 278.0131
1449.5667 | 327.6239 | 271.8858 | 278.0243
1450.5667 | 327.7177 | 271.8944 | 278.0244
1451.5667 | 327.7821 | 271.9007 | 278.0323
1452.5667 | 327.8526 | 271.9157 | 278.0435
1453.5667 | 327.8837 | 271.921 | 278.0587
1454.5667 | 328.0042 | 271.9302 | 278.0598
1455.5667 | 328.0186 | 271.9444 | 278.0763
1456.5667 | 328.1078 | 271.9505 | 278.0965
1457.5667 | 328.1055 | 271.9681 | 278.1148
1458.5667 | 328.1158 | 271.9642 | 278.1329
1459.5667 | 328.1187 | 271.9854 | 278.151
1460.5667 | 328.1317 | 271.9982 | 278.1643
1461.5667 | 328.1677 | 271.9922 | 278.1736
1462.5667 | 328.2874 | 271.9946 | 278.1862
1463.5667 | 328.4079 | 271.9979 | 278.2096
1464.5667 | 328.3636 | 272.0095 | 278.2213
1465.5667 | 328.2909 | 272.0199 | 278.2436
1466.5667 | 328.2714 | 272.0235 | 278.2674
1467.5667 | 328.215 | 272.034 | 278.2963
1468.5667 | 328.2455 | 272.0599 | 278.3107
1469.5667 | 328.2555 | 272.0552 | 278.3244
1470.5667 | 328.2623 | 272.0712 | 278.3372
1471.5667 | 328.2562 | 272.089 | 278.3536
1472.5667 | 328.3129 | 272.1097 | 278.3643
1473.5667 | 328.2814 | 272.1175 | 278.3854
1474.5667 | 328.2314 | 272.1242 | 278.3909
1475.5667 | 328.2106 | 272.149 | 278.3922
1476.5667 | 328.2305 | 272.1718 | 278.4017
1477.5667 | 328.1707 | 272.1887 | 278.4077
1478.5667 | 328.1494 | 272.2089 | 278.4158
1479.5667 | 328.1454 | 272.2301 | 278.4288
1480.5667 | 328.1171 | 272.2398 | 278.4317
1481.5667 | 328.0213 | 272.2396 | 278.4374
1482.5667 | 327.9579 | 272.2521 | 278.4363
1483.5667 | 327.9852 | 272.2706 | 278.431
1484.5667 | 328.0532 | 272.2804 | 278.4393
1485.5667 | 328.0331 | 272.2956 | 278.4429
1486.5667 | 328.0613 | 272.2942 | 278.452
1487.5667 | 328.1154 | 272.3044 | 278.4626
1488.5667 | 328.0873 | 272.3119 | 278.4736
1489.5667 | 328.1829 | 272.3129 | 278.4846
1490.5667 | 328.2388 | 272.3101 | 278.4859
1491.5667 | 328.3142 | 272.3021 | 278.4898
1492.5667 | 328.2693 | 272.3114 | 278.5013
1493.5667 | 328.3257 | 272.3141 | 278.501
1494.5667 | 328.4144 | 272.3329 | 278.5211
1495.5667 | 328.3579 | 272.3329 | 278.5159
1496.5667 | 328.2426 | 272.3336 | 278.5346
1497.5667 | 328.2259 | 272.3541 | 278.549
1498.5667 | 328.2401 | 272.3636 | 278.5613
1499.5667 | 328.1665 | 272.3801 | 278.5692
1500.5667 | 328.1518 | 272.3857 | 278.5708
1501.5667 | 328.0304 | 272.4166 | 278.5879
1502.5667 | 328.0458 | 272.4252 | 278.6037
1503.5667 | 328.0004 | 272.4245 | 278.6133
1504.5667 | 328.009 | 272.4518 | 278.6245
1505.5667 | 327.9849 | 272.4797 | 278.6328
1506.5667 | 327.9814 | 272.4899 | 278.6458
1507.5667 | 327.9804 | 272.5117 | 278.6545
1508.5667 | 327.9304 | 272.5355 | 278.6609
1509.5667 | 327.9535 | 272.5395 | 278.6696
1510.5667 | 327.9681 | 272.5664 | 278.68
1511.5667 | 327.9536 | 272.5721 | 278.691
1512.5667 | 327.958 | 272.5775 | 278.6947
1513.5667 | 327.9198 | 272.5914 | 278.706
1514.5667 | 327.8929 | 272.595 | 278.7219
1515.5667 | 327.9644 | 272.6052 | 278.7243
1516.5667 | 327.9576 | 272.6492 | 278.7419
1517.5667 | 327.8732 | 272.6599 | 278.7503
1518.5667 | 327.9209 | 272.6722 | 278.7516
1519.5667 | 327.9351 | 272.6921 | 278.7596
1520.5667 | 327.9035 | 272.6963 | 278.7581
1521.5667 | 327.8086 | 272.7148 | 278.7606
1522.5667 | 327.7677 | 272.7275 | 278.7683
1523.5667 | 327.6878 | 272.7361 | 278.7781
1524.5667 | 327.7006 | 272.7545 | 278.7878
1525.5667 | 327.7371 | 272.756 | 278.8033
1526.5667 | 327.627 | 272.772 | 278.8123
1527.5667 | 327.5743 | 272.8066 | 278.8255
1528.5667 | 327.4918 | 272.8299 | 278.836
1529.5667 | 327.4064 | 272.8533 | 278.845
1530.5667 | 327.3787 | 272.8902 | 278.8569
1531.5667 | 327.3608 | 272.9046 | 278.8677
1532.5667 | 327.2648 | 272.9577 | 278.8741
1533.5667 | 327.2755 | 272.9744 | 278.8675
1534.5667 | 327.3179 | 273.0037 | 278.8687
1535.5667 | 327.2716 | 273.0052 | 278.8709
1536.5667 | 327.2112 | 273.0159 | 278.8728
1537.5667 | 327.1808 | 273.0438 | 278.8865
1538.5667 | 327.1629 | 273.0572 | 278.8864
1539.5667 | 327.1318 | 273.0508 | 278.8841
1540.5667 | 327.1282 | 273.0479 | 278.8922
1541.5667 | 327.0637 | 273.0427 | 278.8988
1542.5667 | 327.0535 | 273.0463 | 278.9089
1543.5667 | 327.0487 | 273.0615 | 278.9083
1544.5667 | 327.0571 | 273.0788 | 278.9216
1545.5667 | 327.0104 | 273.1052 | 278.9364
1546.5667 | 327.0381 | 273.1131 | 278.9463
1547.5667 | 326.993 | 273.1336 | 278.9598
1548.5667 | 326.9585 | 273.1738 | 278.9719
1549.5667 | 326.9906 | 273.1768 | 278.9759
1550.5667 | 327.0222 | 273.1908 | 278.988
1551.5667 | 327.0171 | 273.209 | 278.9987
1552.5667 | 327.1086 | 273.2086 | 279.0113
1553.5667 | 327.1742 | 273.2233 | 279.0234
1554.5667 | 327.1136 | 273.2316 | 279.0426
1555.5667 | 327.1089 | 273.2406 | 279.0559
1556.5667 | 327.088 | 273.2551 | 279.0644
1557.5667 | 327.0985 | 273.237 | 279.076
1558.5667 | 327.0428 | 273.2525 | 279.0986
1559.5667 | 327.0322 | 273.2673 | 279.1088
1560.5667 | 327.0508 | 273.2559 | 279.1169
1561.5667 | 327.0467 | 273.2626 | 279.1291
1562.5667 | 327.0994 | 273.2718 | 279.1429
1563.5667 | 327.1107 | 273.2819 | 279.1628
1564.5667 | 327.1271 | 273.2816 | 279.1733
1565.5667 | 327.0725 | 273.2897 | 279.1798
1566.5667 | 327.2017 | 273.2982 | 279.1945
1567.5667 | 327.2842 | 273.3098 | 279.1975
1568.5667 | 327.4562 | 273.3493 | 279.2105
1569.5667 | 327.5546 | 273.3544 | 279.2163
1570.5667 | 327.6057 | 273.3717 | 279.2195
1571.5667 | 327.5902 | 273.3733 | 279.2266
1572.5667 | 327.5774 | 273.3727 | 279.2336
1573.5667 | 327.5613 | 273.3751 | 279.2518
1574.5667 | 327.4935 | 273.3787 | 279.2512
1575.5667 | 327.4708 | 273.3583 | 279.2596
1576.5667 | 327.3974 | 273.3745 | 279.2679
1577.5667 | 327.3565 | 273.3855 | 279.2793
1578.5667 | 327.2773 | 273.3906 | 279.2844
1579.5667 | 327.3088 | 273.3955 | 279.2953
1580.5667 | 327.4335 | 273.4064 | 279.3138
1581.5667 | 327.4847 | 273.4213 | 279.3338
1582.5667 | 327.4841 | 273.4233 | 279.3499
1583.5667 | 327.4978 | 273.4148 | 279.3658
1584.5667 | 327.4863 | 273.3987 | 279.3794
1585.5667 | 327.5696 | 273.4256 | 279.3982
1586.5667 | 327.6519 | 273.4393 | 279.402
1587.5667 | 327.7062 | 273.4533 | 279.4244
1588.5667 | 327.7281 | 273.4612 | 279.4239
1589.5667 | 327.756 | 273.4477 | 279.4308
1590.5667 | 327.8538 | 273.4725 | 279.4314
1591.5667 | 327.9205 | 273.4809 | 279.4426
1592.5667 | 327.9404 | 273.4914 | 279.4575
1593.5667 | 327.9548 | 273.5108 | 279.4674
1594.5667 | 327.9584 | 273.5283 | 279.4777
1595.5667 | 327.9718 | 273.5427 | 279.4823
1596.5667 | 328.0194 | 273.5624 | 279.4901
1597.5667 | 328.1111 | 273.5885 | 279.4995
1598.5667 | 328.0467 | 273.6024 | 279.5001
1599.5667 | 328.0429 | 273.5938 | 279.517
1600.5667 | 328.1105 | 273.6015 | 279.5275
1601.5667 | 328.0344 | 273.6101 | 279.5412
1602.5667 | 328.009 | 273.6007 | 279.5511
1603.5667 | 328.0157 | 273.6084 | 279.5638
1604.5667 | 328.0379 | 273.6161 | 279.5745
1605.5667 | 328.0741 | 273.6148 | 279.592
1606.5667 | 327.9702 | 273.6234 | 279.6055
1607.5667 | 327.8945 | 273.6125 | 279.6268
1608.5667 | 327.893 | 273.6174 | 279.628
1609.5667 | 327.7643 | 273.6156 | 279.6433
1610.5667 | 327.6989 | 273.6302 | 279.6446
1611.5667 | 327.6614 | 273.6388 | 279.6574
1612.5667 | 327.6312 | 273.6569 | 279.6664
1613.5667 | 327.5801 | 273.6723 | 279.6739
1614.5667 | 327.5178 | 273.6675 | 279.6826
1615.5667 | 327.5674 | 273.6553 | 279.6841
1616.5667 | 327.5807 | 273.6896 | 279.697
1617.5667 | 327.6587 | 273.7015 | 279.7065
1618.5667 | 327.6555 | 273.6979 | 279.7201
1619.5667 | 327.6973 | 273.718 | 279.7271
1620.5667 | 327.7631 | 273.7536 | 279.7379
1621.5667 | 327.7759 | 273.7688 | 279.7463
1622.5667 | 327.803 | 273.7852 | 279.7594
1623.5667 | 327.8106 | 273.8121 | 279.7615
1624.5667 | 327.7153 | 273.8285 | 279.7735
1625.5667 | 327.6209 | 273.827 | 279.7837
1626.5667 | 327.6889 | 273.8347 | 279.7894
1627.5667 | 327.7174 | 273.8276 | 279.7966
1628.5667 | 327.6917 | 273.8316 | 279.8032
1629.5667 | 327.6834 | 273.8474 | 279.8071
1630.5667 | 327.6568 | 273.853 | 279.8155
1631.5667 | 327.6157 | 273.8489 | 279.8239
1632.5667 | 327.5962 | 273.8583 | 279.8264
1633.5667 | 327.4257 | 273.8797 | 279.8468
1634.5667 | 327.4196 | 273.8834 | 279.8503
1635.5667 | 327.4397 | 273.8971 | 279.856
1636.5667 | 327.4198 | 273.918 | 279.8669
1637.5667 | 327.3449 | 273.9242 | 279.8722
1638.5667 | 327.2989 | 273.9315 | 279.8746
1639.5667 | 327.3522 | 273.937 | 279.887
1640.5667 | 327.3337 | 273.9376 | 279.8832
1641.5667 | 327.3877 | 273.9148 | 279.8982
1642.5667 | 327.4852 | 273.9559 | 279.9073
1643.5667 | 327.5673 | 273.9831 | 279.9207
1644.5667 | 327.537 | 273.9736 | 279.9229
1645.5667 | 327.5432 | 273.9822 | 279.935
1646.5667 | 327.6122 | 274.0036 | 279.9386
1647.5667 | 327.7207 | 274.0208 | 279.9441
1648.5667 | 327.8899 | 274.0465 | 279.9502
1649.5667 | 327.9011 | 274.0516 | 279.964
1650.5667 | 327.9582 | 274.05 | 279.9711
1651.5667 | 328.0084 | 274.0411 | 279.9777
1652.5667 | 328.1123 | 274.0492 | 279.989
1653.5667 | 328.19 | 274.0668 | 280.0024
1654.5667 | 328.235 | 274.0868 | 280.0089
1655.5667 | 328.1742 | 274.0769 | 280.0254
1656.5667 | 328.1781 | 274.0796 | 280.0321
1657.5667 | 328.1913 | 274.0957 | 280.0368
1658.5667 | 328.1888 | 274.094 | 280.0446
1659.5667 | 328.2411 | 274.1293 | 280.0546
1660.5667 | 328.3386 | 274.1492 | 280.0599
1661.5667 | 328.3365 | 274.1836 | 280.0708
1662.5667 | 328.2614 | 274.1968 | 280.0754
1663.5667 | 328.1381 | 274.2205 | 280.0819
1664.5667 | 328.0709 | 274.2507 | 280.0962
1665.5667 | 328.0562 | 274.2893 | 280.1137
1666.5667 | 328.0602 | 274.2999 | 280.1322
1667.5667 | 328.1071 | 274.3221 | 280.1476
1668.5667 | 328.0744 | 274.3378 | 280.1639
1669.5667 | 328.0259 | 274.3511 | 280.1812
1670.5667 | 328.0122 | 274.3647 | 280.1959
1671.5667 | 328.0628 | 274.3747 | 280.2174
1672.5667 | 328.0617 | 274.4076 | 280.2275
1673.5667 | 328.0627 | 274.432 | 280.2475
1674.5667 | 328.0045 | 274.421 | 280.2661
1675.5667 | 327.9091 | 274.4406 | 280.2885
1676.5667 | 327.8612 | 274.4716 | 280.2979
1677.5667 | 327.8725 | 274.4704 | 280.3184
1678.5667 | 327.8588 | 274.4864 | 280.3407
1679.5667 | 327.7882 | 274.4982 | 280.3602
1680.5667 | 327.7659 | 274.5624 | 280.3802
1681.5667 | 327.8766 | 274.6015 | 280.4041
1682.5667 | 327.9271 | 274.6119 | 280.4219
1683.5667 | 327.8734 | 274.6245 | 280.4422
1684.5667 | 327.8139 | 274.6467 | 280.461
1685.5667 | 327.7286 | 274.6537 | 280.4766
1686.5667 | 327.6912 | 274.6619 | 280.489
1687.5667 | 327.7059 | 274.6692 | 280.5159
1688.5667 | 327.664 | 274.657 | 280.5306
1689.5667 | 327.5006 | 274.6674 | 280.5433
1690.5667 | 327.4054 | 274.6735 | 280.5578
1691.5667 | 327.3684 | 274.6415 | 280.5811
1692.5667 | 327.376 | 274.6405 | 280.589
1693.5667 | 327.4081 | 274.6492 | 280.6055
1694.5667 | 327.2705 | 274.6487 | 280.6275
1695.5667 | 327.2018 | 274.6732 | 280.6409
1696.5667 | 327.187 | 274.6652 | 280.6555
1697.5667 | 327.2158 | 274.6749 | 280.674
1698.5667 | 327.3273 | 274.7062 | 280.6913
1699.5667 | 327.3816 | 274.7367 | 280.7108
1700.5667 | 327.3572 | 274.7407 | 280.7406
1701.5667 | 327.3212 | 274.7445 | 280.7576
1702.5667 | 327.2984 | 274.7582 | 280.775
1703.5667 | 327.3178 | 274.78 | 280.7937
1704.5667 | 327.4425 | 274.7923 | 280.8166
1705.5667 | 327.5793 | 274.8091 | 280.8317
1706.5667 | 327.6392 | 274.8212 | 280.8413
1707.5667 | 327.687 | 274.8125 | 280.8465
1708.5667 | 327.8051 | 274.8264 | 280.8592
1709.5667 | 327.8781 | 274.8446 | 280.8551
1710.5667 | 327.9157 | 274.884 | 280.8583
1711.5667 | 327.9404 | 274.853 | 280.8616
1712.5667 | 327.9353 | 274.8559 | 280.8715
1713.5667 | 327.9924 | 274.8551 | 280.8737
1714.5667 | 328.0376 | 274.8695 | 280.8774
1715.5667 | 327.9244 | 274.8377 | 280.8879
1716.5667 | 327.9164 | 274.8349 | 280.8947
1717.5667 | 327.9629 | 274.843 | 280.8938
1718.5667 | 327.959 | 274.8441 | 280.9049
1719.5667 | 327.9292 | 274.8449 | 280.9117
1720.5667 | 327.9707 | 274.869 | 280.9228
1721.5667 | 328.022 | 274.8782 | 280.9331
1722.5667 | 328.0921 | 274.8816 | 280.9449
1723.5667 | 328.1061 | 274.8868 | 280.9572
1724.5667 | 328.1044 | 274.8771 | 280.9709
1725.5667 | 328.1154 | 274.92 | 280.9836
1726.5667 | 328.1278 | 274.9499 | 280.9977
1727.5667 | 328.1482 | 274.9655 | 281.0176
1728.5667 | 328.1854 | 274.979 | 281.02
1729.5667 | 328.3031 | 275.0061 | 281.0357
1730.5667 | 328.4042 | 275.0496 | 281.0504
1731.5667 | 328.4929 | 275.0899 | 281.0637
1732.5667 | 328.5538 | 275.1011 | 281.0823
1733.5667 | 328.4452 | 275.12 | 281.1059
1734.5667 | 328.4007 | 275.1131 | 281.1227
1735.5667 | 328.3966 | 275.106 | 281.1391
1736.5667 | 328.3444 | 275.1195 | 281.1512
1737.5667 | 328.3902 | 275.1123 | 281.1706
1738.5667 | 328.3817 | 275.1138 | 281.1883
1739.5667 | 328.2804 | 275.1037 | 281.207
1740.5667 | 328.2497 | 275.1051 | 281.228
1741.5667 | 328.1919 | 275.1037 | 281.2479
1742.5667 | 328.0974 | 275.1157 | 281.2747
1743.5667 | 328.0397 | 275.1274 | 281.2959
1744.5667 | 328.0702 | 275.122 | 281.3074
1745.5667 | 328.1397 | 275.1372 | 281.3379
1746.5667 | 328.1258 | 275.1458 | 281.356
1747.5667 | 328.1847 | 275.1588 | 281.3765
1748.5667 | 328.1583 | 275.1577 | 281.403
1749.5667 | 328.1479 | 275.1586 | 281.4219
1750.5667 | 328.1377 | 275.1502 | 281.4492
1751.5667 | 328.0737 | 275.1567 | 281.4675
1752.5667 | 328.0904 | 275.1817 | 281.4881
1753.5667 | 327.9924 | 275.1972 | 281.5051
1754.5667 | 327.8222 | 275.2113 | 281.5303
1755.5667 | 327.7261 | 275.2223 | 281.5492
1756.5667 | 327.8004 | 275.2269 | 281.5593
1757.5667 | 327.8652 | 275.2317 | 281.5755
1758.5667 | 327.839 | 275.2393 | 281.5932
1759.5667 | 327.8506 | 275.2618 | 281.6067
1760.5667 | 327.8742 | 275.3006 | 281.6298
1761.5667 | 327.8733 | 275.2965 | 281.6531
1762.5667 | 327.8181 | 275.2912 | 281.6663
1763.5667 | 327.7933 | 275.3157 | 281.6801
1764.5667 | 327.927 | 275.3107 | 281.6927
1765.5667 | 327.9923 | 275.3266 | 281.7065
1766.5667 | 327.9809 | 275.343 | 281.7361
1767.5667 | 327.9825 | 275.3327 | 281.7503
1768.5667 | 328.0171 | 275.3488 | 281.7693
1769.5667 | 327.9948 | 275.3666 | 281.7791
1770.5667 | 328.0694 | 275.3736 | 281.788
1771.5667 | 328.1506 | 275.3751 | 281.8034
1772.5667 | 328.225 | 275.3966 | 281.8115
1773.5667 | 328.2208 | 275.3966 | 281.8209
1774.5667 | 328.1535 | 275.3918 | 281.8215
1775.5667 | 328.0898 | 275.4031 | 281.8344
1776.5667 | 328.0868 | 275.401 | 281.8404
1777.5667 | 327.9407 | 275.4131 | 281.8566
1778.5667 | 327.9977 | 275.4508 | 281.8665
1779.5667 | 328.0522 | 275.4835 | 281.8766
1780.5667 | 327.9986 | 275.4729 | 281.889
1781.5667 | 327.9936 | 275.4904 | 281.8989
1782.5667 | 327.9958 | 275.5176 | 281.9139
1783.5667 | 328.0644 | 275.4837 | 281.9217
1784.5667 | 328.136 | 275.4831 | 281.9383
1785.5667 | 328.2363 | 275.4962 | 281.9433
1786.5667 | 328.3268 | 275.513 | 281.9573
1787.5667 | 328.2349 | 275.5301 | 281.9666
1788.5667 | 328.2278 | 275.5459 | 281.9794
1789.5667 | 328.2909 | 275.5561 | 281.9834
1790.5667 | 328.226 | 275.5879 | 282.004
1791.5667 | 328.1605 | 275.5923 | 282.0118
1792.5667 | 328.1601 | 275.5946 | 282.0215
1793.5667 | 328.2164 | 275.6259 | 282.036
1794.5667 | 328.2511 | 275.6233 | 282.0478
1795.5667 | 328.2349 | 275.6415 | 282.0568
1796.5667 | 328.1911 | 275.6566 | 282.0681
1797.5667 | 328.1068 | 275.6862 | 282.0863
1798.5667 | 328.0476 | 275.6984 | 282.0978
1799.5667 | 327.9664 | 275.721 | 282.1067
1800.5667 | 328.0282 | 275.7287 | 282.1252
1801.5667 | 328.115 | 275.7546 | 282.1337
1802.5667 | 328.1752 | 275.7975 | 282.1563
1803.5667 | 328.1483 | 275.8229 | 282.184
1804.5667 | 328.1136 | 275.8202 | 282.2012
1805.5667 | 328.0737 | 275.7951 | 282.2345
1806.5667 | 328.1457 | 275.8297 | 282.2566
1807.5667 | 328.075 | 275.8428 | 282.2904
1808.5667 | 327.868 | 275.8727 | 282.3219
1809.5667 | 327.8015 | 275.931 | 282.3395
1810.5667 | 327.7989 | 275.9824 | 282.384
1811.5667 | 327.7016 | 276.0406 | 282.4079
1812.5667 | 327.7382 | 276.0965 | 282.4244
1813.5667 | 327.6639 | 276.1844 | 282.4532
1814.5667 | 327.6166 | 276.2278 | 282.4736
1815.5667 | 327.5857 | 276.229 | 282.4875
1816.5667 | 327.5881 | 276.2629 | 282.504
1817.5667 | 327.6415 | 276.292 | 282.5108
1818.5667 | 327.6958 | 276.3093 | 282.5243
1819.5667 | 327.7318 | 276.3362 | 282.5494
1820.5667 | 327.7017 | 276.336 | 282.5698
1821.5667 | 327.6815 | 276.3735 | 282.5921
1822.5667 | 327.6537 | 276.3745 | 282.6121
1823.5667 | 327.5463 | 276.3776 | 282.6344
1824.5667 | 327.537 | 276.3543 | 282.6551
1825.5667 | 327.5568 | 276.3586 | 282.6883
1826.5667 | 327.5743 | 276.3808 | 282.7
1827.5667 | 327.4973 | 276.4057 | 282.7268
1828.5667 | 327.4885 | 276.4373 | 282.7402
1829.5667 | 327.5342 | 276.4662 | 282.7503
1830.5667 | 327.5841 | 276.4998 | 282.7603
1831.5667 | 327.5798 | 276.5114 | 282.7684
1832.5667 | 327.6047 | 276.5023 | 282.7804
1833.5667 | 327.5896 | 276.4926 | 282.7933
1834.5667 | 327.5727 | 276.5029 | 282.8036
1835.5667 | 327.5401 | 276.4787 | 282.8133
1836.5667 | 327.5906 | 276.4628 | 282.8159
1837.5667 | 327.6566 | 276.4615 | 282.8239
1838.5667 | 327.6975 | 276.5089 | 282.8284
1839.5667 | 327.6728 | 276.5349 | 282.8374
1840.5667 | 327.6563 | 276.5621 | 282.8391
1841.5667 | 327.694 | 276.5907 | 282.8343
1842.5667 | 327.7247 | 276.6251 | 282.8383
1843.5667 | 327.7659 | 276.6393 | 282.8432
1844.5667 | 327.7911 | 276.6506 | 282.8371
1845.5667 | 327.9043 | 276.6608 | 282.8307
1846.5667 | 327.9741 | 276.6688 | 282.8312
1847.5667 | 328.0215 | 276.6746 | 282.8279
1848.5667 | 328.1668 | 276.6877 | 282.8258
1849.5667 | 328.3933 | 276.6823 | 282.8333
1850.5667 | 328.5425 | 276.7249 | 282.8286
1851.5667 | 328.6272 | 276.7707 | 282.8259
1852.5667 | 328.7361 | 276.8063 | 282.8342
1853.5667 | 328.8407 | 276.8296 | 282.8437
1854.5667 | 328.9744 | 276.808 | 282.8475
1855.5667 | 328.9988 | 276.8007 | 282.8663
1856.5667 | 329.042 | 276.7658 | 282.8713
1857.5667 | 329.1248 | 276.7339 | 282.8845
1858.5667 | 329.2175 | 276.723 | 282.8996
1859.5667 | 329.151 | 276.7068 | 282.9122
1860.5667 | 329.133 | 276.7003 | 282.9269
1861.5667 | 329.1001 | 276.7032 | 282.9356
1862.5667 | 328.992 | 276.6811 | 282.9598
1863.5667 | 328.9744 | 276.6984 | 282.9751
1864.5667 | 329.0161 | 276.7129 | 282.9907
1865.5667 | 329.0024 | 276.7386 | 283.0029
1866.5667 | 328.8693 | 276.7591 | 283.0153
1867.5667 | 328.777 | 276.7612 | 283.034
1868.5667 | 328.7703 | 276.776 | 283.0545
1869.5667 | 328.848 | 276.7893 | 283.0695
1870.5667 | 328.9387 | 276.8193 | 283.0908
1871.5667 | 329.0502 | 276.8059 | 283.1084
1872.5667 | 329.075 | 276.8107 | 283.1329
1873.5667 | 329.0726 | 276.8182 | 283.1474
1874.5667 | 329.0607 | 276.844 | 283.1666
1875.5667 | 329.0878 | 276.8467 | 283.1839
1876.5667 | 329.1877 | 276.8515 | 283.2027
1877.5667 | 329.2452 | 276.8449 | 283.2123
1878.5667 | 329.2966 | 276.8491 | 283.2254
1879.5667 | 329.2395 | 276.8847 | 283.2402
1880.5667 | 329.0979 | 276.9166 | 283.2513
1881.5667 | 328.9719 | 276.9726 | 283.2783
1882.5667 | 328.956 | 277.0103 | 283.2851
1883.5667 | 328.919 | 277.0661 | 283.3032
1884.5667 | 328.846 | 277.0627 | 283.3124
1885.5667 | 328.8192 | 277.1112 | 283.3233
1886.5667 | 328.7782 | 277.129 | 283.338
1887.5667 | 328.7279 | 277.1225 | 283.3503
1888.5667 | 328.6403 | 277.1313 | 283.362
1889.5667 | 328.5237 | 277.1371 | 283.374
1890.5667 | 328.4443 | 277.1193 | 283.392
1891.5667 | 328.38 | 277.1179 | 283.4107
1892.5667 | 328.3839 | 277.1078 | 283.4291
1893.5667 | 328.3861 | 277.1089 | 283.447
1894.5667 | 328.3282 | 277.108 | 283.4624
1895.5667 | 328.2361 | 277.1104 | 283.4692
1896.5667 | 328.2107 | 277.108 | 283.4876
1897.5667 | 328.2485 | 277.1043 | 283.501
1898.5667 | 328.1743 | 277.0642 | 283.5098
1899.5667 | 328.1186 | 277.0467 | 283.5224
1900.5667 | 328.0781 | 277.0231 | 283.5424
1901.5667 | 328.0899 | 277.0158 | 283.5446
1902.5667 | 328.0933 | 277.0036 | 283.5544
1903.5667 | 328.1324 | 276.9763 | 283.5651
1904.5667 | 328.1533 | 276.9584 | 283.5776
1905.5667 | 328.1404 | 276.9513 | 283.5816
1906.5667 | 328.1984 | 276.9354 | 283.5907
1907.5667 | 328.2451 | 276.9076 | 283.5909
1908.5667 | 328.3099 | 276.9006 | 283.5951
1909.5667 | 328.3523 | 276.8834 | 283.5962
1910.5667 | 328.3504 | 276.8991 | 283.595
1911.5667 | 328.3047 | 276.9103 | 283.5983
1912.5667 | 328.3365 | 276.9453 | 283.5959
1913.5667 | 328.4279 | 276.9679 | 283.5861
1914.5667 | 328.4618 | 277.0067 | 283.5772
1915.5667 | 328.4086 | 277.028 | 283.5692
1916.5667 | 328.4113 | 277.0268 | 283.5669
1917.5667 | 328.4255 | 277.0008 | 283.5629
1918.5667 | 328.4233 | 276.9666 | 283.5691
1919.5667 | 328.4189 | 276.9557 | 283.5735
1920.5667 | 328.5195 | 276.9495 | 283.5721
1921.5667 | 328.5353 | 276.9906 | 283.5735
1922.5667 | 328.5825 | 277.0352 | 283.5859
1923.5667 | 328.6315 | 277.0873 | 283.5907
1924.5667 | 328.6959 | 277.1441 | 283.5925
1925.5667 | 328.694 | 277.1959 | 283.6005
1926.5667 | 328.7927 | 277.2171 | 283.6077
1927.5667 | 328.874 | 277.2287 | 283.6187
1928.5667 | 328.8546 | 277.2232 | 283.6275
1929.5667 | 328.8891 | 277.2262 | 283.636
1930.5667 | 328.9447 | 277.2406 | 283.6411
1931.5667 | 328.9645 | 277.2633 | 283.6557
1932.5667 | 328.9219 | 277.2757 | 283.6639
1933.5667 | 328.9381 | 277.2966 | 283.6757
1934.5667 | 328.9222 | 277.2986 | 283.6851
1935.5667 | 328.8792 | 277.2812 | 283.695
1936.5667 | 328.7953 | 277.2716 | 283.7042
1937.5667 | 328.7814 | 277.229 | 283.7166
1938.5667 | 328.8399 | 277.1575 | 283.7308
1939.5667 | 328.8798 | 277.0975 | 283.7485
1940.5667 | 328.8524 | 277.0474 | 283.7612
1941.5667 | 328.8197 | 277.0659 | 283.7737
1942.5667 | 328.8566 | 277.1276 | 283.7815
1943.5667 | 328.9914 | 277.1837 | 283.7986
1944.5667 | 329.0683 | 277.2491 | 283.8025
1945.5667 | 329.0979 | 277.275 | 283.8129
1946.5667 | 329.1221 | 277.2815 | 283.8265
1947.5667 | 329.1434 | 277.29 | 283.8306
1948.5667 | 329.153 | 277.289 | 283.8492
1949.5667 | 329 | 277.2651 | 283.8629
1950.5667 | 328.9044 | 277.2258 | 283.8783
1951.5667 | 328.8771 | 277.1958 | 283.8912
1952.5667 | 328.8701 | 277.1875 | 283.9113
1953.5667 | 328.8804 | 277.1804 | 283.9325
1954.5667 | 328.8829 | 277.2275 | 283.948
1955.5667 | 328.8376 | 277.2561 | 283.9677
1956.5667 | 328.7812 | 277.3073 | 283.9913
1957.5667 | 328.908 | 277.3765 | 284.0037
1958.5667 | 328.7203 | 277.3948 | 284.0182
1959.5667 | 328.7369 | 277.3774 | 284.039
1960.5667 | 328.7156 | 277.3601 | 284.0567
1961.5667 | 328.5939 | 277.3226 | 284.0736
1962.5667 | 328.4818 | 277.3036 | 284.0914
1963.5667 | 328.3349 | 277.2603 | 284.11
1964.5667 | 328.2834 | 277.2527 | 284.1218
1965.5667 | 328.1894 | 277.2484 | 284.1409
1966.5667 | 328.1659 | 277.2387 | 284.157
1967.5667 | 327.9786 | 277.231 | 284.1601
1968.5667 | 327.8364 | 277.2548 | 284.1843
1969.5667 | 327.7659 | 277.2412 | 284.1994
1970.5667 | 327.7167 | 277.2788 | 284.2117
1971.5667 | 327.7019 | 277.3609 | 284.2176
1972.5667 | 327.6882 | 277.4682 | 284.2307
1973.5667 | 327.636 | 277.5661 | 284.2364
1974.5667 | 327.6236 | 277.6524 | 284.2516
1975.5667 | 327.611 | 277.7089 | 284.2619
1976.5667 | 327.612 | 277.7845 | 284.2781
1977.5667 | 327.5436 | 277.8207 | 284.2853
1978.5667 | 327.5455 | 277.798 | 284.2964
1979.5667 | 327.6033 | 277.7723 | 284.3018
1980.5667 | 327.5961 | 277.7499 | 284.3088
1981.5667 | 327.6552 | 277.7549 | 284.3198
1982.5667 | 327.5607 | 277.7531 | 284.3241
1983.5667 | 327.4794 | 277.717 | 284.3347
1984.5667 | 327.4216 | 277.683 | 284.333
1985.5667 | 327.4192 | 277.651 | 284.3425
1986.5667 | 327.4913 | 277.6318 | 284.3543
1987.5667 | 327.4735 | 277.6184 | 284.3613
1988.5667 | 327.4412 | 277.6298 | 284.3667
1989.5667 | 327.2864 | 277.6548 | 284.3809
1990.5667 | 327.2388 | 277.6879 | 284.3827
1991.5667 | 327.2146 | 277.7006 | 284.3898
1992.5667 | 327.1546 | 277.7002 | 284.4003
1993.5667 | 327.0952 | 277.714 | 284.4028
1994.5667 | 327.0458 | 277.7299 | 284.4122
1995.5667 | 327.1359 | 277.7581 | 284.4116
1996.5667 | 327.1871 | 277.7991 | 284.4202
1997.5667 | 327.2937 | 277.8383 | 284.4275
1998.5667 | 327.3422 | 277.8795 | 284.433
1999.5667 | 327.3932 | 277.9161 | 284.4369
2000.5667 | 327.3926 | 277.9369 | 284.4355
2001.5667 | 327.4648 | 277.9461 | 284.4453
2002.5667 | 327.4773 | 277.9419 | 284.4505
2003.5667 | 327.458 | 277.9747 | 284.4498
2004.5667 | 327.452 | 278.033 | 284.4622
2005.5667 | 327.4584 | 278.079 | 284.4658
2006.5667 | 327.4718 | 278.0877 | 284.4631
2007.5667 | 327.4877 | 278.0599 | 284.4671
2008.5667 | 327.4419 | 278.0396 | 284.4658
2009.5667 | 327.4615 | 278.0312 | 284.471
2010.5667 | 327.4143 | 278.049 | 284.4631
2011.5667 | 327.4279 | 278.0769 | 284.4586
2012.5667 | 327.4152 | 278.1279 | 284.4547
2013.5667 | 327.4316 | 278.1783 | 284.4451
2014.5667 | 327.4487 | 278.2351 | 284.4416
2015.5667 | 327.5131 | 278.2689 | 284.4415
2016.5667 | 327.5337 | 278.3035 | 284.4361
2017.5667 | 327.5634 | 278.3226 | 284.4443
2018.5667 | 327.5119 | 278.3645 | 284.4352
2019.5667 | 327.5532 | 278.3925 | 284.443
2020.5667 | 327.5961 | 278.3926 | 284.4292
2021.5667 | 327.6891 | 278.3901 | 284.439
2022.5667 | 327.7773 | 278.3502 | 284.4362
2023.5667 | 327.782 | 278.3146 | 284.4328
2024.5667 | 327.8132 | 278.2574 | 284.4449
2025.5667 | 327.882 | 278.2032 | 284.4458
2026.5667 | 327.8335 | 278.1562 | 284.4464
2027.5667 | 327.8674 | 278.1127 | 284.4547
2028.5667 | 327.8565 | 278.0642 | 284.4519
2029.5667 | 327.7923 | 278.0017 | 284.4523
2030.5667 | 327.7902 | 277.9423 | 284.4575
2031.5667 | 327.7736 | 277.8982 | 284.4605
2032.5667 | 327.8182 | 277.8731 | 284.4581
2033.5667 | 327.849 | 277.8397 | 284.4652
2034.5667 | 327.9246 | 277.808 | 284.4688
2035.5667 | 327.9916 | 277.806 | 284.4688
2036.5667 | 328.0925 | 277.8359 | 284.4783
2037.5667 | 328.1207 | 277.9255 | 284.4796
2038.5667 | 328.2388 | 278.0234 | 284.4811
2039.5667 | 328.3654 | 278.1093 | 284.4782
2040.5667 | 328.4193 | 278.1722 | 284.4804
2041.5667 | 328.4358 | 278.2125 | 284.4833
2042.5667 | 328.4932 | 278.2506 | 284.4851
2043.5667 | 328.5766 | 278.2857 | 284.4955
2044.5667 | 328.6189 | 278.2833 | 284.5008
2045.5667 | 328.637 | 278.2693 | 284.5012
2046.5667 | 328.7972 | 278.2272 | 284.5031
2047.5667 | 328.875 | 278.194 | 284.5074
2048.5667 | 328.9049 | 278.136 | 284.5132
2049.5667 | 328.9882 | 278.0509 | 284.5173
2050.5667 | 328.9912 | 277.9814 | 284.5206
2051.5667 | 328.9511 | 277.9214 | 284.5264
2052.5667 | 328.9575 | 277.8938 | 284.5227
2053.5667 | 328.9656 | 277.8873 | 284.5303
2054.5667 | 329.013 | 277.8978 | 284.5338
2055.5667 | 329.0736 | 277.893 | 284.5421
2056.5667 | 329.13 | 277.8966 | 284.5551
2057.5667 | 329.1334 | 277.9007 | 284.5587
2058.5667 | 329.1305 | 277.8997 | 284.5655
2059.5667 | 329.1304 | 277.8952 | 284.5847
2060.5667 | 329.1509 | 277.8902 | 284.6012
2061.5667 | 329.0425 | 277.892 | 284.6101
2062.5667 | 328.931 | 277.901 | 284.6203
2063.5667 | 328.941 | 277.9044 | 284.6314
2064.5667 | 328.9862 | 277.9301 | 284.6375
2065.5667 | 328.9669 | 277.9624 | 284.6429
2066.5667 | 329.0106 | 278.019 | 284.6493
2067.5667 | 328.9918 | 278.0627 | 284.6584
2068.5667 | 328.9237 | 278.1061 | 284.6632
2069.5667 | 328.9547 | 278.1506 | 284.6711
2070.5667 | 328.9536 | 278.1544 | 284.6847
2071.5667 | 328.8522 | 278.1256 | 284.6908
2072.5667 | 328.8404 | 278.0705 | 284.7029
2073.5667 | 328.8347 | 278.0389 | 284.7199
2074.5667 | 328.7531 | 278.0046 | 284.7366
2075.5667 | 328.5892 | 277.9573 | 284.7514
2076.5667 | 328.4505 | 277.9207 | 284.7634
2077.5667 | 328.4482 | 277.8726 | 284.764
2078.5667 | 328.5012 | 277.846 | 284.7763
2079.5667 | 328.5288 | 277.8303 | 284.7903
2080.5667 | 328.4147 | 277.8157 | 284.7975
2081.5667 | 328.2 | 277.7748 | 284.8042
2082.5667 | 328.1068 | 277.7791 | 284.8188
2083.5667 | 328.0939 | 277.8164 | 284.8259
2084.5667 | 328.094 | 277.882 | 284.828
2085.5667 | 328.1274 | 277.9553 | 284.8338
2086.5667 | 328.1767 | 278.0235 | 284.8375
2087.5667 | 328.136 | 278.0773 | 284.8512
2088.5667 | 328.124 | 278.1462 | 284.8565
2089.5667 | 328.1474 | 278.213 | 284.8714
2090.5667 | 328.0382 | 278.2965 | 284.8784
2091.5667 | 328.0174 | 278.3745 | 284.8816
2092.5667 | 327.9327 | 278.423 | 284.8885
2093.5667 | 327.9544 | 278.4651 | 284.8938
2094.5667 | 328.0005 | 278.4981 | 284.9006
2095.5667 | 327.9776 | 278.5198 | 284.9069
2096.5667 | 327.9062 | 278.5619 | 284.9172
2097.5667 | 327.7994 | 278.5746 | 284.9214
2098.5667 | 327.7361 | 278.5812 | 284.931
2099.5667 | 327.6743 | 278.6018 | 284.9335
2100.5667 | 327.6264 | 278.6205 | 284.9477
2101.5667 | 327.6247 | 278.616 | 284.9541
2102.5667 | 327.6234 | 278.6042 | 284.9597
2103.5667 | 327.6827 | 278.5876 | 284.9692
2104.5667 | 327.7211 | 278.6016 | 284.9805
2105.5667 | 327.7857 | 278.6038 | 284.9868
2106.5667 | 327.7897 | 278.5834 | 284.9947
2107.5667 | 327.7464 | 278.5405 | 285.0064
2108.5667 | 327.6511 | 278.5042 | 285.0135
2109.5667 | 327.6455 | 278.4749 | 285.0229
2110.5667 | 327.582 | 278.4636 | 285.0261
2111.5667 | 327.5598 | 278.4899 | 285.0309
2112.5667 | 327.5791 | 278.5217 | 285.0439
2113.5667 | 327.4446 | 278.491 | 285.0435
2114.5667 | 327.3998 | 278.4537 | 285.0486
2115.5667 | 327.4002 | 278.4137 | 285.0499
2116.5667 | 327.2234 | 278.3952 | 285.0543
2117.5667 | 327.1964 | 278.3773 | 285.0512
2118.5667 | 327.2967 | 278.3619 | 285.0491
2119.5667 | 327.2828 | 278.3418 | 285.0461
2120.5667 | 327.2871 | 278.3394 | 285.0493
2121.5667 | 327.2523 | 278.3299 | 285.053
2122.5667 | 327.2543 | 278.333 | 285.0568
2123.5667 | 327.3881 | 278.3416 | 285.0677
2124.5667 | 327.4689 | 278.3687 | 285.0732
2125.5667 | 327.559 | 278.3965 | 285.0774
2126.5667 | 327.5615 | 278.3983 | 285.0854
2127.5667 | 327.5187 | 278.3953 | 285.0907
2128.5667 | 327.5302 | 278.387 | 285.1134
2129.5667 | 327.5639 | 278.385 | 285.1197
2130.5667 | 327.6044 | 278.3797 | 285.1382
2131.5667 | 327.6691 | 278.3816 | 285.1629
2132.5667 | 327.6778 | 278.3672 | 285.1864
2133.5667 | 327.6866 | 278.355 | 285.2034
2134.5667 | 327.677 | 278.344 | 285.2259
2135.5667 | 327.6609 | 278.324 | 285.2524
2136.5667 | 327.654 | 278.3052 | 285.2746
2137.5667 | 327.5534 | 278.2912 | 285.306
2138.5667 | 327.5011 | 278.2782 | 285.3203
2139.5667 | 327.5282 | 278.2619 | 285.3477
2140.5667 | 327.5874 | 278.2645 | 285.3722
2141.5667 | 327.6289 | 278.3013 | 285.3847
2142.5667 | 327.6404 | 278.336 | 285.3855
2143.5667 | 327.6393 | 278.354 | 285.4045
2144.5667 | 327.6333 | 278.3998 | 285.4189
2145.5667 | 327.682 | 278.5064 | 285.4307
2146.5667 | 327.601 | 278.5955 | 285.4435
2147.5667 | 327.5634 | 278.6657 | 285.4574
2148.5667 | 327.6029 | 278.6852 | 285.4587
2149.5667 | 327.5217 | 278.6864 | 285.4706
2150.5667 | 327.4501 | 278.6876 | 285.4782
2151.5667 | 327.3933 | 278.7227 | 285.4811
2152.5667 | 327.41 | 278.7513 | 285.4886
2153.5667 | 327.421 | 278.7798 | 285.4965
2154.5667 | 327.4823 | 278.796 | 285.4958
2155.5667 | 327.4721 | 278.8386 | 285.5073
2156.5667 | 327.4745 | 278.811 | 285.4953
2157.5667 | 327.5086 | 278.8307 | 285.4987
2158.5667 | 327.44 | 278.831 | 285.5032
2159.5667 | 327.4262 | 278.8237 | 285.5049
2160.5667 | 327.4207 | 278.8324 | 285.5062
2161.5667 | 327.3792 | 278.8271 | 285.5085
2162.5667 | 327.3378 | 278.8409 | 285.5174
2163.5667 | 327.4507 | 278.8695 | 285.5221
2164.5667 | 327.5215 | 278.8824 | 285.5294
2165.5667 | 327.557 | 278.8783 | 285.5457
2166.5667 | 327.544 | 278.8847 | 285.5457
2167.5667 | 327.5245 | 278.8842 | 285.5553
2168.5667 | 327.5011 | 278.8924 | 285.5489
2169.5667 | 327.4759 | 278.8912 | 285.5463
2170.5667 | 327.434 | 278.8543 | 285.5477
2171.5667 | 327.467 | 278.8436 | 285.5509
2172.5667 | 327.464 | 278.8554 | 285.5538
2173.5667 | 327.419 | 278.8709 | 285.5571
2174.5667 | 327.4607 | 278.8279 | 285.5658
2175.5667 | 327.5656 | 278.8418 | 285.5606
2176.5667 | 327.5913 | 278.8233 | 285.5734
2177.5667 | 327.6659 | 278.7873 | 285.5809
2178.5667 | 327.6394 | 278.7692 | 285.5923
2179.5667 | 327.6229 | 278.8103 | 285.606
2180.5667 | 327.6955 | 278.8081 | 285.6232
2181.5667 | 327.7069 | 278.7731 | 285.6336
2182.5667 | 327.8284 | 278.7616 | 285.6459
2183.5667 | 327.8431 | 278.7272 | 285.6521
2184.5667 | 327.8357 | 278.677 | 285.6588
2185.5667 | 327.8519 | 278.6466 | 285.6746
2186.5667 | 327.8294 | 278.6173 | 285.6765
2187.5667 | 327.8134 | 278.6234 | 285.688
2188.5667 | 327.8001 | 278.6271 | 285.6895
2189.5667 | 327.7235 | 278.575 | 285.6922
2190.5667 | 327.7443 | 278.5321 | 285.6845
2191.5667 | 327.6865 | 278.5226 | 285.68
2192.5667 | 327.7958 | 278.4909 | 285.6688
2193.5667 | 327.8376 | 278.4769 | 285.6661
2194.5667 | 327.8633 | 278.505 | 285.6579
2195.5667 | 327.7516 | 278.529 | 285.6485
2196.5667 | 327.6738 | 278.529 | 285.6474
2197.5667 | 327.7519 | 278.491 | 285.6437
2198.5667 | 327.741 | 278.4769 | 285.6304
2199.5667 | 327.811 | 278.4783 | 285.6361
2200.5667 | 327.8523 | 278.4614 | 285.6244
2201.5667 | 327.9121 | 278.4742 | 285.6145
2202.5667 | 327.9181 | 278.471 | 285.6182
2203.5667 | 327.8896 | 278.4471 | 285.6221
2204.5667 | 327.9224 | 278.4127 | 285.6335
2205.5667 | 328.0389 | 278.3945 | 285.6373
2206.5667 | 328.0512 | 278.3858 | 285.6401
2207.5667 | 328.0229 | 278.3322 | 285.6425
2208.5667 | 328.0681 | 278.3399 | 285.6379
2209.5667 | 328.0719 | 278.3686 | 285.6289
2210.5667 | 328.0911 | 278.3985 | 285.6319
2211.5667 | 328.1527 | 278.4158 | 285.6279
2212.5667 | 328.1759 | 278.4231 | 285.6213
2213.5667 | 328.188 | 278.4281 | 285.6269
2214.5667 | 328.2547 | 278.4136 | 285.6366
2215.5667 | 328.3427 | 278.3859 | 285.6337
2216.5667 | 328.3942 | 278.3796 | 285.6348
2217.5667 | 328.3658 | 278.4103 | 285.6388
2218.5667 | 328.4138 | 278.4914 | 285.6421
2219.5667 | 328.4833 | 278.6063 | 285.6448
2220.5667 | 328.5121 | 278.7105 | 285.6412
2221.5667 | 328.6576 | 278.8107 | 285.6462
2222.5667 | 328.7731 | 278.889 | 285.6396
2223.5667 | 328.7263 | 278.9305 | 285.6507
2224.5667 | 328.7551 | 278.9677 | 285.646
2225.5667 | 328.6814 | 278.9996 | 285.6644
2226.5667 | 328.7383 | 279.0283 | 285.6684
2227.5667 | 328.8416 | 279.0583 | 285.6714
2228.5667 | 328.7749 | 279.0783 | 285.678
2229.5667 | 328.7811 | 279.069 | 285.6825
2230.5667 | 328.7262 | 279.0623 | 285.692
2231.5667 | 328.7597 | 279.088 | 285.7038
2232.5667 | 328.6885 | 279.1374 | 285.711
2233.5667 | 328.6875 | 279.1743 | 285.7201
2234.5667 | 328.7411 | 279.2305 | 285.7257
2235.5667 | 328.8491 | 279.2923 | 285.7317
2236.5667 | 328.9166 | 279.3469 | 285.7412
2237.5667 | 328.8396 | 279.3849 | 285.7557
2238.5667 | 328.8184 | 279.376 | 285.7665
2239.5667 | 328.7919 | 279.372 | 285.7704
2240.5667 | 328.8536 | 279.3312 | 285.775
2241.5667 | 328.9045 | 279.3023 | 285.7782
2242.5667 | 328.861 | 279.2706 | 285.7861
2243.5667 | 328.8105 | 279.2561 | 285.8346
2244.5667 | 328.8546 | 279.2192 | 285.8479
2245.5667 | 328.8335 | 279.155 | 285.8648
2246.5667 | 328.7358 | 279.1257 | 285.8725
2247.5667 | 328.684 | 279.1366 | 285.8841
2248.5667 | 328.704 | 279.1249 | 285.8944
2249.5667 | 328.7418 | 279.1331 | 285.9078
2250.5667 | 328.745 | 279.1167 | 285.9146
2251.5667 | 328.7166 | 279.1254 | 285.9224
2252.5667 | 328.6462 | 279.126 | 285.9399
2253.5667 | 328.6459 | 279.1335 | 285.9556
2254.5667 | 328.5265 | 279.167 | 285.9667
2255.5667 | 328.439 | 279.201 | 285.9853
2256.5667 | 328.3512 | 279.2063 | 285.9968
2257.5667 | 328.2802 | 279.2071 | 286.0022
2258.5667 | 328.2077 | 279.2038 | 286.0209
2259.5667 | 328.1902 | 279.1917 | 286.0331
2260.5667 | 328.1003 | 279.1366 | 286.044
2261.5667 | 328.1435 | 279.1192 | 286.0387
2262.5667 | 328.132 | 279.1427 | 286.0367
2263.5667 | 328.0683 | 279.1779 | 286.0209
2264.5667 | 328.1075 | 279.2377 | 286.0163
2265.5667 | 328.1384 | 279.2907 | 286.0094
2266.5667 | 328.1874 | 279.3029 | 286.0052
2267.5667 | 328.1552 | 279.2706 | 286.0029
2268.5667 | 328.1664 | 279.2323 | 286.017
2269.5667 | 328.0598 | 279.1905 | 286.0249
2270.5667 | 328.0399 | 279.1904 | 286.0281
2271.5667 | 328.018 | 279.1866 | 286.032
2272.5667 | 328.0565 | 279.1899 | 286.0361
2273.5667 | 328.1896 | 279.1956 | 286.0544
2274.5667 | 328.1902 | 279.2224 | 286.0596
2275.5667 | 328.2141 | 279.1946 | 286.0698
2276.5667 | 328.281 | 279.1774 | 286.0909
2277.5667 | 328.3729 | 279.1522 | 286.0982
2278.5667 | 328.4188 | 279.1404 | 286.1129
2279.5667 | 328.4502 | 279.1151 | 286.1261
2280.5667 | 328.4605 | 279.1145 | 286.1488
2281.5667 | 328.4575 | 279.0941 | 286.1729
2282.5667 | 328.5015 | 279.0646 | 286.1947
2283.5667 | 328.576 | 279.0476 | 286.2139
2284.5667 | 328.6445 | 279.0292 | 286.2368
2285.5667 | 328.7058 | 279.021 | 286.259
2286.5667 | 328.7361 | 278.9921 | 286.2773
2287.5667 | 328.8513 | 279.0214 | 286.2915
2288.5667 | 328.9163 | 279.1 | 286.3103
2289.5667 | 328.9768 | 279.206 | 286.3437
2290.5667 | 328.9759 | 279.3079 | 286.3667
2291.5667 | 329.003 | 279.3965 | 286.3983
2292.5667 | 329.1032 | 279.4568 | 286.4272
2293.5667 | 329.2249 | 279.5035 | 286.4553
2294.5667 | 329.2979 | 279.5256 | 286.491
2295.5667 | 329.2947 | 279.5375 | 286.5335
2296.5667 | 329.3584 | 279.5248 | 286.5912
2297.5667 | 329.3918 | 279.5078 | 286.6457
2298.5667 | 329.4846 | 279.4808 | 286.7072
2299.5667 | 329.5515 | 279.4558 | 286.7673
2300.5667 | 329.6013 | 279.4352 | 286.835
2301.5667 | 329.586 | 279.4162 | 286.89
2302.5667 | 329.5934 | 279.3969 | 286.9481
2303.5667 | 329.6055 | 279.3696 | 286.9958
2304.5667 | 329.5767 | 279.3455 | 287.051
2305.5667 | 329.5822 | 279.3556 | 287.1061
2306.5667 | 329.5501 | 279.3756 | 287.1705
2307.5667 | 329.5582 | 279.3989 | 287.2385
2308.5667 | 329.5392 | 279.4215 | 287.3031
2309.5667 | 329.5177 | 279.4533 | 287.372
2310.5667 | 329.4819 | 279.4968 | 287.4454
2311.5667 | 329.5157 | 279.5401 | 287.5251
2312.5667 | 329.4892 | 279.5667 | 287.6072
2313.5667 | 329.4024 | 279.6019 | 287.7006
2314.5667 | 329.3884 | 279.6508 | 287.7898
2315.5667 | 329.3839 | 279.683 | 287.8838
2316.5667 | 329.2379 | 279.7519 | 287.9783
2317.5667 | 329.0858 | 279.8212 | 288.0811
2318.5667 | 328.9374 | 279.9031 | 288.1808
2319.5667 | 328.8528 | 279.9819 | 288.2941
2320.5667 | 328.7516 | 280.0739 | 288.404
2321.5667 | 328.7195 | 280.1881 | 288.5301
2322.5667 | 328.6088 | 280.282 | 288.6635
2323.5667 | 328.496 | 280.4706 | 288.8016
2324.5667 | 328.3451 | 280.6001 | 288.9289
2325.5667 | 328.3549 | 280.7406 | 289.0676
2326.5667 | 328.2435 | 280.9212 | 289.2352
2327.5667 | 328.185 | 281.0876 | 289.3957
2328.5667 | 328.1329 | 281.2272 | 289.5594
2329.5667 | 328.0985 | 281.4073 | 289.7556
2330.5667 | 328.013 | 281.5383 | 289.9594
2331.5667 | 327.9871 | 281.7121 | 290.1929
2332.5667 | 327.9108 | 281.8882 | 290.435
2333.5667 | 327.8911 | 282.0788 | 290.6792
2334.5667 | 327.8103 | 282.2428 | 290.9486
2335.5667 | 327.7893 | 282.4318 | 291.2291
2336.5667 | 327.7376 | 282.6157 | 291.5285
2337.5667 | 327.6064 | 282.8205 | 291.8521
2338.5667 | 327.4852 | 283.0014 | 292.1877
2339.5667 | 327.3268 | 283.217 | 292.5564
2340.5667 | 327.1535 | 283.4512 | 292.9702
2341.5667 | 327.0945 | 283.6885 | 293.4257
2342.5667 | 326.9833 | 283.9699 | 293.939
2343.5667 | 326.9409 | 284.3084 | 294.5142
2344.5667 | 326.9109 | 284.6489 | 295.145
2345.5667 | 326.8534 | 285.0954 | 295.8438
2346.5667 | 326.7764 | 285.8756 | 296.6035
2347.5667 | 326.7597 | 289.2517 | 297.4159
2348.5667 | 326.6028 | 293.4834 | 298.2899
2349.5667 | 326.5009 | 297.9176 | 299.2542
2350.5667 | 326.4135 | 303.9224 | 300.3687
2351.6604 | 326.388 | 313.0497 | 301.8751
2352.5823 | 326.3361 | 317.9259 | 303.4605
2353.5823 | 326.322 | 322.3566 | 305.5788
2354.5979 | 326.2716 | 326.8905 | 308.1391
2355.5667 | 326.2428 | 330.4791 | 311.1287
2356.5667 | 326.2359 | 335.4429 | 314.5308
2357.5667 | 326.3225 | 341.4191 | 318.1273
2358.5667 | 326.2589 | 346.8498 | 321.7257
2359.5667 | 326.244 | 351.006 | 325.1293
2360.5667 | 326.3252 | 355.3783 | 328.5014
2361.5667 | 326.2682 | 360.7809 | 332.0291
2362.5667 | 326.1532 | 365.0052 | 335.5686
2363.5667 | 326.0381 | 368.7519 | 339.0186
2364.5667 | 326.0596 | 374.8361 | 342.6859
2365.5667 | 326.0801 | 380.3197 | 346.1499
2366.5667 | 326.0123 | 384.6003 | 349.5833
2367.5667 | 326.0032 | 389.2986 | 353.2384
2368.5667 | 326.0418 | 394.3673 | 357.0841
2369.5667 | 325.959 | 399.912 | 360.7767
2370.5667 | 325.8918 | 404.8994 | 364.3785
2371.5667 | 325.9083 | 410.8529 | 367.979
2372.5667 | 325.9318 | 415.521 | 371.7421
2373.5667 | 325.8732 | 420.4751 | 375.2771
2374.5667 | 325.8425 | 427.4123 | 379.4506
2375.5667 | 325.7512 | 430.98 | 382.8178
2376.5667 | 325.7149 | 434.9418 | 386.3881
2377.5667 | 325.7182 | 437.9568 | 389.7106
2378.5667 | 325.7054 | 442.5527 | 393.1565
2379.5667 | 325.5918 | 446.4514 | 396.4976
2380.5667 | 325.547 | 450.5906 | 399.6664
2381.5667 | 325.5095 | 454.0525 | 403.1801
2382.5667 | 325.4226 | 455.3204 | 406.7844
2383.5667 | 325.3385 | 457.4582 | 409.8696
2384.5667 | 325.3016 | 460.0606 | 412.6173
2385.5667 | 325.1817 | 462.2561 | 414.8266
2386.5667 | 325.0683 | 466.8252 | 416.9714
2387.5667 | 324.9895 | 467.8232 | 419.6966
2388.5667 | 324.9181 | 469.8096 | 422.0664
2389.5667 | 324.8578 | 476.346 | 424.8664
2390.5667 | 324.8105 | 480.112 | 427.6133
2391.5667 | 324.7347 | 480.6375 | 430.2614
2392.5667 | 324.7012 | 482.2873 | 432.2815
2393.5667 | 324.5687 | 482.9274 | 434.5814
2394.5667 | 324.4459 | 485.1944 | 436.5333
2395.5667 | 324.4235 | 486.2382 | 438.5896
2396.5667 | 324.3315 | 487.7911 | 440.4531
2397.5667 | 324.2965 | 488.5071 | 443.1139
2398.5667 | 324.2636 | 489.0125 | 445.6802
2399.5667 | 324.3102 | 491.7997 | 447.725
2400.5667 | 324.3068 | 492.8352 | 449.7331
2401.5667 | 324.2941 | 494.9695 | 451.577
2402.5667 | 324.2318 | 495.2931 | 453.7776
2403.5667 | 324.2855 | 497.0751 | 455.5754
2404.5667 | 324.3216 | 500.0121 | 458.035
2405.5667 | 324.2546 | 501.8723 | 459.8458
2406.5667 | 324.3509 | 501.9223 | 461.8019
2407.5667 | 324.4236 | 505.1039 | 463.9519
2408.5667 | 324.5164 | 506.1564 | 465.4802
2409.5667 | 324.6685 | 504.8467 | 467.0376
2410.5667 | 324.754 | 510.3042 | 468.0352
2411.5667 | 324.8493 | 510.5833 | 469.2253
2412.5667 | 324.9189 | 510.1775 | 470.7679
2413.5667 | 325.0337 | 510.7711 | 472.3021
2414.5667 | 325.3243 | 511.6131 | 473.9218
2415.5667 | 325.7276 | 512.8477 | 475.0782
2416.5667 | 326.0692 | 511.4276 | 476.7835
2417.5667 | 326.3603 | 511.8008 | 478.1839
2418.5667 | 326.7128 | 514.0189 | 479.681
2419.5667 | 327.1253 | 512.836 | 481.3508
2420.5667 | 327.366 | 511.2022 | 482.818
2421.5667 | 327.6172 | 510.593 | 484.2908
2422.5667 | 327.8327 | 507.6755 | 485.1631
2423.5667 | 328.0964 | 511.5097 | 485.5968
2424.5667 | 328.3215 | 512.7747 | 487.23
2425.5667 | 328.2669 | 509.3512 | 488.1797
2426.5667 | 328.323 | 506.254 | 489.1869
2427.5667 | 328.2489 | 507.1397 | 490.0326
2428.5667 | 328.1099 | 504.1982 | 490.8865
2429.5667 | 328.0456 | 506.3119 | 491.7619
2430.5667 | 327.8672 | 508.6314 | 492.7496
2431.5667 | 327.7069 | 510.4164 | 493.7668
2432.5667 | 327.6635 | 511.7203 | 494.3573
2433.5667 | 327.6544 | 512.1077 | 494.532
2434.5667 | 327.8519 | 511.4189 | 495.8042
2435.5667 | 328.1875 | 513.6182 | 496.626
2436.5667 | 328.2027 | 515.0712 | 497.5843
2437.5667 | 328.2703 | 513.8335 | 498.2303
2438.5667 | 328.4434 | 515.2126 | 498.9123
2439.5667 | 328.6008 | 512.8334 | 499.1966
2440.5667 | 328.6292 | 513.2374 | 499.5106
2441.5667 | 328.7382 | 511.1837 | 499.9517
2442.5667 | 328.9156 | 504.4681 | 499.8341
2443.5667 | 328.8826 | 506.718 | 499.3858
2444.5667 | 328.869 | 512.3717 | 499.5071
2445.5667 | 328.8542 | 509.606 | 500.0144
2446.5667 | 328.6761 | 510.0753 | 500.1817
2447.5667 | 328.614 | 513.6873 | 500.1293
2448.5667 | 328.7521 | 513.3732 | 500.3956
2449.5667 | 328.82 | 520.1386 | 501.2794
2450.5667 | 328.8999 | 524.2708 | 502.0532
2451.5667 | 329.1353 | 524.5992 | 502.9658
2452.5667 | 329.3017 | 527.6938 | 503.7579
2453.5667 | 329.4657 | 529.3085 | 504.5772
2454.5667 | 329.4086 | 529.569 | 505.3101
2455.5667 | 329.2291 | 531.6625 | 505.9936
2456.5667 | 329.1554 | 533.9764 | 506.8341
2457.5667 | 329.3449 | 529.2021 | 507.762
2458.5667 | 329.5639 | 527.9906 | 507.9453
2459.5667 | 329.425 | 529.7473 | 508.2332
2460.5667 | 329.421 | 530.8373 | 508.7241
2461.5667 | 329.3657 | 533.3402 | 509.3864
2462.5667 | 329.2675 | 535.6467 | 510.1646
2463.5667 | 329.4886 | 535.7552 | 511.0784
2464.5667 | 329.662 | 537.5707 | 512.2263
2465.5667 | 329.6174 | 536.8093 | 513.3362
2466.5667 | 329.6607 | 538.5807 | 514.3227
2467.5667 | 329.9713 | 541.5919 | 515.2474
2468.5667 | 330.1962 | 543.2377 | 516.1709
2469.5667 | 330.3083 | 543.1725 | 517.2262
2470.5667 | 330.3165 | 547.5914 | 518.3006
2471.5667 | 330.4377 | 549.7851 | 519.4551
2472.5667 | 330.4453 | 550.5744 | 520.4718
2473.5667 | 330.4265 | 553.6492 | 521.3713
2474.5667 | 330.5114 | 553.8379 | 522.2438
2475.5667 | 330.4803 | 553.6643 | 522.9549
2476.5667 | 330.5587 | 554.9151 | 523.7271
2477.5667 | 330.6158 | 558.5257 | 524.4401
2478.5667 | 330.6945 | 560.7669 | 525.0556
2479.5667 | 330.6703 | 561.1622 | 525.9177
2480.5667 | 330.6286 | 565.9271 | 526.9049
2481.5667 | 330.5814 | 567.5084 | 527.8384
2482.5667 | 330.6209 | 569.989 | 528.7911
2483.5667 | 330.5828 | 568.0002 | 529.769
2484.5667 | 330.4821 | 571.5044 | 530.847
2485.5667 | 330.4579 | 571.0128 | 532.1202
2486.5667 | 330.3601 | 575.3641 | 533.5084
2487.5667 | 330.2473 | 579.7234 | 534.851
2488.5667 | 330.168 | 579.2721 | 536.0824
2489.5667 | 329.9003 | 583.4211 | 537.2463
2490.5667 | 329.8186 | 587.3994 | 538.3421
2491.5667 | 329.8081 | 586.0721 | 539.3397
2492.5667 | 329.714 | 581.7002 | 540.4291
2493.5667 | 329.6357 | 582.9624 | 541.5095
2494.5667 | 329.6817 | 583.7202 | 542.7309
2495.5667 | 329.6209 | 585.073 | 544.0061
2496.5667 | 329.5651 | 587.5612 | 545.387
2497.5667 | 329.5091 | 592.4591 | 546.8919
2498.5667 | 329.4292 | 593.7649 | 548.5291
2499.5667 | 329.2471 | 594.5619 | 550.2033
2500.5667 | 329.0514 | 595.4717 | 551.834
2501.5667 | 328.8793 | 597.7037 | 553.3459
2502.5667 | 328.689 | 600.2982 | 554.7953
2503.5667 | 328.4811 | 605.4091 | 556.2905
2504.5667 | 328.4042 | 607.5366 | 557.829
2505.5667 | 328.2946 | 610.3762 | 559.4246
2506.5667 | 328.2299 | 617.0336 | 560.9878
2507.5667 | 328.162 | 616.1157 | 562.3599
2508.5667 | 328.0461 | 615.7554 | 563.8365
2509.5667 | 327.9775 | 616.6759 | 565.3016
2510.5667 | 327.9038 | 612.7344 | 566.5507
2511.5667 | 327.8282 | 604.7638 | 567.7179
2512.5667 | 327.7456 | 594.8173 | 568.9381
2513.5667 | 327.6976 | 586.5499 | 570.2471
2514.5667 | 327.6934 | 580.4209 | 571.6397
2515.5667 | 327.6534 | 573.858 | 573.1797
2516.5667 | 327.5849 | 569.792 | 574.6277
2517.5667 | 327.4829 | 564.1874 | 575.7398
2518.5667 | 327.4173 | 559.4477 | 576.5179
2519.5667 | 327.2975 | 555.5584 | 577.233
2520.5667 | 327.1997 | 552.2546 | 578.1841
2521.5667 | 327.1112 | 548.7579 | 579.1289
2522.5667 | 326.9854 | 545.512 | 579.8616
2523.5667 | 326.9461 | 542.794 | 580.2077
2524.5667 | 326.8764 | 539.5798 | 580.2672
2525.5667 | 326.7651 | 537.2007 | 580.1569
2526.5667 | 326.6028 | 534.6502 | 579.8948
2527.5667 | 326.4671 | 533.1564 | 579.5596
2528.5667 | 326.2743 | 530.6598 | 579.2693
2529.5667 | 326.1176 | 527.407 | 579.0475
2530.5667 | 325.9518 | 526.6093 | 578.952
2531.5667 | 325.8116 | 525.2142 | 578.7863
2532.5667 | 325.6634 | 523.685 | 578.6934
2533.5667 | 325.5762 | 522.9868 | 578.3285
2534.5667 | 325.4688 | 522.1024 | 577.8862
2535.5667 | 325.3745 | 521.1122 | 577.4412
2536.5667 | 325.23 | 519.2772 | 576.9621
2537.5667 | 325.0344 | 518.219 | 576.6786
2538.5667 | 324.8992 | 517.0431 | 576.4008
2539.5667 | 324.7716 | 516.013 | 576.1072
2540.5667 | 324.7311 | 515.762 | 576.1374
2541.5667 | 324.6116 | 514.8263 | 576.202
2542.5667 | 324.4561 | 513.8776 | 576.1685
2543.5667 | 324.3693 | 512.9339 | 576.1213
2544.5667 | 324.2765 | 511.9171 | 575.8693
2545.5667 | 324.1716 | 511.8557 | 575.5466
2546.5667 | 324.106 | 511.7035 | 575.2917
2547.5667 | 324.0346 | 510.6004 | 574.9061
2548.5667 | 323.9807 | 509.9654 | 574.9162
2549.5667 | 323.8645 | 509.4761 | 574.9138
2550.5667 | 323.75 | 509.5509 | 574.388
2551.5667 | 323.5948 | 509.1059 | 573.4682
2552.5667 | 323.428 | 508.3518 | 573.0222
2553.5667 | 323.3242 | 508.0034 | 572.5619
2554.5667 | 323.2034 | 507.9201 | 572.1803
2555.5667 | 323.0904 | 507.3002 | 571.9284
2556.5667 | 322.9581 | 506.9242 | 571.6965
2557.5667 | 322.7987 | 506.3938 | 571.0089
2558.5667 | 322.6458 | 506.0733 | 570.2208
2559.5667 | 322.4619 | 505.8987 | 569.0358
2560.5667 | 322.3221 | 505.2902 | 568.4673
2561.5667 | 322.2261 | 504.7416 | 567.7335
2562.5667 | 322.0787 | 504.6557 | 567.2974
2563.5667 | 321.93 | 504.0257 | 567.2429
2564.5667 | 321.8403 | 502.572 | 567.7429
2565.5667 | 321.7075 | 501.7725 | 568.2302
2566.5667 | 321.6472 | 500.7933 | 568.8881
2567.5667 | 321.5547 | 499.8034 | 569.855
2568.5667 | 321.4469 | 499.6826 | 570.6862
2569.5667 | 321.4434 | 500.145 | 571.9058
2570.5667 | 321.4796 | 500.7552 | 572.6159
2571.5667 | 321.5941 | 500.6462 | 573.0858
2572.5667 | 321.5737 | 501.1795 | 573.4616
2573.5667 | 321.5161 | 501.0275 | 574.1254
2574.5667 | 321.4362 | 499.9736 | 575.2003
2575.5667 | 321.452 | 499.8591 | 575.8545
2576.5667 | 321.3741 | 499.2934 | 576.7887
2577.5667 | 321.3213 | 499.1127 | 577.2687
2578.5667 | 321.3535 | 498.3776 | 577.7526
2579.5667 | 321.2976 | 499.0578 | 577.8886
2580.5667 | 321.1722 | 499.9849 | 577.4494
2581.5667 | 321.1358 | 499.5234 | 576.8735
2582.5667 | 321.1153 | 499.8241 | 576.2754
2583.5667 | 321.0588 | 499.4406 | 575.6038
2584.5667 | 320.9198 | 499.6729 | 575.8445
2585.5667 | 320.816 | 499.3809 | 575.6754
2586.5667 | 320.6722 | 498.8059 | 575.6523
2587.5667 | 320.5007 | 499.5977 | 575.0802
2588.5667 | 320.3699 | 500.0505 | 575.182
2589.5667 | 320.2678 | 499.3513 | 574.8437
2590.5667 | 320.1709 | 499.4058 | 574.3406
2591.5667 | 319.9578 | 498.8818 | 574.1723
2592.5667 | 319.8011 | 497.7164 | 573.9371
2593.5667 | 319.7202 | 497.6773 | 573.7478
2594.5667 | 319.6289 | 497.602 | 573.6844
2595.5667 | 319.5411 | 496.9361 | 573.6197
2596.5667 | 319.4951 | 496.5301 | 573.5565
2597.5667 | 319.362 | 497.4712 | 573.3018
2598.5667 | 319.2333 | 498.7176 | 572.7561
2599.5667 | 319.0752 | 497.3543 | 572.7333
2600.5667 | 318.8914 | 498.4191 | 572.7537
2601.5667 | 318.7899 | 498.8372 | 572.4859
2602.5667 | 318.7704 | 498.1999 | 572.2506
2603.5667 | 318.7017 | 497.881 | 572.0517
2604.5667 | 318.6271 | 497.8844 | 571.6011
2605.5667 | 318.4855 | 497.2775 | 571.1556
2606.5667 | 318.4147 | 496.7615 | 570.962
2607.5667 | 318.3 | 496.7949 | 570.6948
2608.5667 | 318.1826 | 496.794 | 570.4467
2609.5667 | 318.0563 | 496.6999 | 569.7802
2610.5667 | 317.9024 | 496.7558 | 569.6842
2611.5667 | 317.7726 | 497.5858 | 569.2945
2612.5667 | 317.6732 | 497.3755 | 568.6405
2613.5667 | 317.5836 | 498.3475 | 568.0094
2614.5667 | 317.4638 | 499.0583 | 567.5188
2615.5667 | 317.3555 | 499.7899 | 567.0698
2616.5667 | 317.2365 | 499.8843 | 566.3915
2617.5667 | 317.1 | 501.0762 | 565.6584
2618.5667 | 316.9846 | 502.2203 | 565.0262
2619.5667 | 316.8354 | 501.8991 | 564.2783
2620.5667 | 316.713 | 502.7379 | 563.6784
2621.5667 | 316.6176 | 502.8526 | 562.4155
2622.5667 | 316.4857 | 502.5086 | 561.5169
2623.5667 | 316.3687 | 501.8918 | 560.1845
2624.5667 | 316.219 | 502.0649 | 559.6139
2625.5667 | 316.079 | 502.5251 | 558.8155
2626.5667 | 315.965 | 503.4702 | 558.2281
2627.5667 | 315.8208 | 503.5373 | 557.6424
2628.5667 | 315.6762 | 503.485 | 556.8934
2629.5667 | 315.5577 | 503.1204 | 556.2629
2630.5667 | 315.3077 | 503.754 | 555.9515
2631.5667 | 315.1267 | 503.747 | 555.8449
2632.5667 | 314.9698 | 503.348 | 555.4151
2633.5667 | 314.8224 | 503.5697 | 554.7784
2634.5667 | 314.6596 | 503.4392 | 554.854
2635.5667 | 314.4994 | 503.4243 | 554.1948
2636.5667 | 314.3902 | 503.3473 | 553.8465
2637.5667 | 314.2442 | 504.5384 | 553.7165
2638.5667 | 314.029 | 503.6507 | 553.4409
2639.5667 | 313.7749 | 503.9411 | 553.0963
2640.5667 | 313.5273 | 504.667 | 552.7344
2641.5667 | 313.2701 | 504.4517 | 552.3322
2642.5667 | 313.0853 | 504.2955 | 551.7298
2643.5667 | 312.9093 | 504.1819 | 551.3053
2644.5667 | 312.6961 | 503.644 | 551.1221
2645.5667 | 312.5077 | 503.7097 | 550.7277
2646.5667 | 312.2669 | 504.0485 | 550.4717
2647.5667 | 312.0132 | 503.5686 | 549.8631
2648.5667 | 311.8179 | 503.7573 | 549.5567
2649.5667 | 311.6377 | 503.3873 | 548.9688
2650.5667 | 311.4347 | 502.8128 | 548.5414
2651.5667 | 311.2247 | 502.2037 | 548.309
2652.5667 | 311.039 | 502.4937 | 548.107
2653.5667 | 310.8907 | 502.4575 | 548.063
2654.5667 | 310.7055 | 502.0194 | 547.7435
2655.5667 | 310.4942 | 501.9372 | 547.6719
2656.5667 | 310.3214 | 501.2041 | 547.5458
2657.5667 | 310.1438 | 500.6718 | 547.2654
2658.5667 | 309.9513 | 500.521 | 546.8175
2659.5667 | 309.7237 | 500.513 | 547.0443
2660.5667 | 309.4978 | 500.2398 | 546.729
2661.5667 | 309.2229 | 500.7113 | 546.4672
2662.5667 | 308.9276 | 501.0053 | 546.3442
2663.5667 | 308.6887 | 500.76 | 546.2027
2664.5667 | 308.4638 | 500.2147 | 546.0335
2665.5667 | 308.2555 | 499.8278 | 545.5993
2666.5667 | 308.0758 | 500.0292 | 545.1547
2667.5667 | 307.8823 | 500.2666 | 544.6631
2668.5667 | 307.6716 | 499.4491 | 544.5394
2669.5667 | 307.4752 | 498.3702 | 544.256
2670.5667 | 307.2412 | 497.9114 | 544.4376
2671.5667 | 307.058 | 498.2662 | 543.8272
2672.5667 | 306.8879 | 497.5379 | 543.2244
2673.5667 | 306.7156 | 497.3755 | 543.0558
2674.5667 | 306.5233 | 496.6567 | 542.754
2675.5667 | 306.2613 | 496.0856 | 542.6299
2676.5667 | 305.9793 | 496.3851 | 542.7836
2677.5667 | 305.7462 | 495.6664 | 542.5149
2678.5667 | 305.5017 | 495.446 | 542.7702
2679.5667 | 305.2836 | 495.4715 | 542.4797
2680.5667 | 305.0737 | 494.1265 | 542.6013
2681.5667 | 304.8768 | 493.2503 | 542.5405
2682.5667 | 304.6532 | 493.0407 | 542.4264
2683.5667 | 304.4387 | 492.9979 | 542.4586
2684.5667 | 304.2055 | 492.274 | 542.5276
2685.5667 | 303.8859 | 491.4699 | 542.6823
2686.5667 | 303.5875 | 490.9608 | 542.8559
2687.5667 | 303.3269 | 490.7127 | 542.7841
2688.5667 | 303.0452 | 490.279 | 542.9168
2689.5667 | 302.818 | 489.7887 | 542.7247
2690.5667 | 302.5265 | 488.8304 | 542.6608
2691.5667 | 302.2996 | 487.7599 | 542.6759
2692.5667 | 302.0815 | 487.1684 | 542.6539
2693.5667 | 301.8726 | 487.137 | 542.3229
2694.5667 | 301.6159 | 486.8304 | 542.2663
2695.5667 | 301.3782 | 485.1714 | 542.329
2696.5667 | 301.1709 | 484.3457 | 542.174
2697.5667 | 300.9768 | 484.3688 | 542.0856
2698.5667 | 300.7911 | 483.3027 | 541.9872
2699.5667 | 300.6021 | 482.8807 | 541.4588
2700.5667 | 300.3958 | 482.8341 | 541.1916
2701.5667 | 300.2093 | 482.8968 | 540.941
2702.5667 | 300.0334 | 481.5375 | 540.4795
2703.5667 | 299.8623 | 480.1828 | 540.4139
2704.5667 | 299.6553 | 480.4136 | 540.1681
2705.5667 | 299.4324 | 479.6283 | 539.77
2706.5667 | 299.2091 | 478.4326 | 539.6288
2707.5667 | 299.0064 | 478.2364 | 539.0729
2708.5667 | 298.7931 | 477.4154 | 538.4995
2709.5667 | 298.5263 | 475.648 | 537.8594
2710.5667 | 298.2891 | 475.2456 | 537.4496
2711.5667 | 298.0972 | 475.3292 | 536.8151
2712.5667 | 297.9318 | 474.7362 | 536.0775
2713.5667 | 297.7306 | 474.0836 | 535.4862
2714.5667 | 297.5406 | 473.9029 | 534.8704
2715.5667 | 297.3602 | 473.2569 | 534.2835
2716.5667 | 297.1258 | 473.139 | 533.6666
2717.5667 | 296.8787 | 472.5711 | 533.072
2718.5667 | 296.6728 | 471.0591 | 532.5744
2719.5667 | 296.4976 | 470.9466 | 532.1321
2720.5667 | 296.3378 | 470.4434 | 531.6683
2721.5667 | 296.1311 | 470.3233 | 531.2584
2722.5667 | 295.9379 | 469.9906 | 530.7383
2723.5667 | 295.7762 | 469.6215 | 530.224
2724.5667 | 295.5929 | 469.3695 | 529.6255
2725.5667 | 295.3732 | 468.3576 | 529.1439
2726.5667 | 295.1246 | 467.5502 | 528.896
2727.5667 | 294.856 | 465.9144 | 528.3636
2728.5667 | 294.5984 | 464.7627 | 527.7474
2729.5667 | 294.3632 | 463.7729 | 527.2478
2730.5667 | 294.1513 | 463.1103 | 526.9364
2731.5667 | 293.9466 | 462.1211 | 526.4267
2732.5667 | 293.6701 | 461.819 | 525.9726
2733.5667 | 293.4567 | 461.0235 | 525.6478
2734.5667 | 293.2829 | 460.3187 | 525.3037
2735.5667 | 293.0571 | 460.6842 | 524.8844
2736.5667 | 292.8128 | 460.8526 | 524.5828
2737.5667 | 292.5859 | 460.9988 | 524.2151
2738.5667 | 292.3574 | 460.8507 | 523.8276
2739.5667 | 292.1611 | 460.0646 | 523.4593
2740.5667 | 291.9478 | 459.3647 | 523.1415
2741.5667 | 291.725 | 458.576 | 522.7655
2742.5667 | 291.4673 | 457.5636 | 522.4229
2743.5667 | 291.2259 | 457.4792 | 522.069
2744.5667 | 291.014 | 457.6814 | 521.7514
2745.5667 | 290.7755 | 457.2148 | 521.3364
2746.5667 | 290.5813 | 456.593 | 520.8973
2747.5667 | 290.3535 | 455.9028 | 520.4305
2748.5667 | 290.1596 | 454.9161 | 520.0184
2749.5667 | 289.9153 | 454.0601 | 519.4754
2750.5667 | 289.674 | 453.8066 | 519.1428
2751.5667 | 289.478 | 453.2777 | 518.9637
2752.5667 | 289.262 | 452.8249 | 518.5376
2753.5667 | 289.0493 | 452.924 | 518.208
2754.5667 | 288.8329 | 452.059 | 517.6643
2755.5667 | 288.62 | 452.537 | 517.2555
2756.5667 | 288.4291 | 451.8045 | 516.8755
2757.5667 | 288.142 | 450.7118 | 516.3291
2758.5667 | 287.9118 | 450.2239 | 515.8258
2759.5667 | 287.6946 | 449.93 | 515.3179
2760.5667 | 287.4602 | 449.9188 | 514.8822
2761.5667 | 287.2146 | 449.1069 | 514.6602
2762.5667 | 286.9871 | 448.1507 | 514.0267
2763.5667 | 286.7541 | 447.2059 | 513.4983
2764.5667 | 286.5147 | 447.1198 | 512.9775
2765.5667 | 286.2688 | 446.5687 | 512.6856
2766.5667 | 286.0595 | 445.4628 | 512.3563
2767.5667 | 285.8696 | 444.8672 | 511.8452
2768.5667 | 285.6363 | 444.5394 | 511.3247
2769.5667 | 285.4246 | 444.1773 | 511.0426
2770.5667 | 285.2219 | 443.8569 | 510.5956
2771.5667 | 284.9963 | 442.9513 | 510.0089
2772.5667 | 284.7752 | 442.9496 | 509.4155
2773.5667 | 284.5525 | 442.8585 | 508.8731
2774.5667 | 284.3235 | 441.9971 | 508.3167
2775.5667 | 284.111 | 441.984 | 507.7787
2776.5667 | 283.9122 | 441.3131 | 507.3183
2777.5667 | 283.689 | 440.9863 | 506.8554
2778.5667 | 283.4996 | 440.5777 | 506.2255
2779.5667 | 283.3084 | 440.9384 | 505.7427
2780.5667 | 283.0996 | 440.1508 | 505.2689
2781.5667 | 282.8995 | 439.5811 | 504.8114
2782.5667 | 282.6735 | 438.4382 | 504.1585
2783.5667 | 282.4419 | 438.3253 | 503.5515
2784.5667 | 282.2222 | 438.1114 | 503.1325
2785.5667 | 281.9971 | 438.4243 | 502.6985
2786.5667 | 281.7363 | 437.9464 | 502.2117
2787.5667 | 281.4735 | 437.4794 | 501.5861
2788.5667 | 281.2759 | 437.4116 | 501.0206
2789.5667 | 281.1099 | 437.3066 | 500.3121
2790.5667 | 280.8672 | 436.3649 | 499.7427
2791.5667 | 280.5786 | 435.6306 | 499.0836
2792.5667 | 280.3207 | 435.3369 | 498.3593
2793.5667 | 280.1119 | 435.5865 | 497.6505
2794.5667 | 279.9102 | 435.1608 | 496.987
2795.5667 | 279.6642 | 434.3045 | 496.2731